## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-13
Test Date: | 2006-11-28
Ignition Time Relative to Thermal Data: | 239 | s
Ignition Time Relative to Electrical Data: | 239 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Plots for XLPE cables at F and G

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Random Fill Tray, Location A |  |  |  |  | Location A | Random Fill Tray, Location C |  |  |  |  | Location C | Location E: Conduit with 3-cable bundle |  |  | Location F - 6-cable bundle 13-2 |  |  |  | Location F | Location G - 6-cable bundle 13-2 |  |  |  | Location G | Slug Calorimeters
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC1 Cable Center Row Center | TC2 Above Cable Mass | TC3 Below Cable mass | TC4 Cable Center Row Left | TC5 Cable Center Row Right | Tray Rung | TC1 Cable Center Row Center | TC2 Above Cable Mass | TC3 Below Cable mass | TC4 Cable Center Row Left | TC5 Cable Center Row Right | Tray Rung | Cable Temp | Air Inside Conduit | Conduit Temp | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Slug Calorimeter Above Location F | Slug Calorimeter Above Location G
0 | -239 | -5.9 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 3.4 | 221.2 | 7.5 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.8 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
1 | -238 | -5.8 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 3.2 | 225.2 | 8.2 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
2 | -237 | -6 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 2.8 | 208 | 9.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
3 | -236 | -6 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 3.1 | 223.4 | 11.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
4 | -235 | -6.1 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.6 | 3.1 | 258.9 | 10.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
5 | -234 | -6.3 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.9 | 12.4 | 10.4 | 21.7 | 9.6 | 3.4 | 234.3 | 10.1 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.8 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
6 | -233 | -6.2 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.8 | 12.4 | 10.3 | 21.7 | 9.7 | 2.7 | 230.9 | 10.3 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
7 | -232 | -6.3 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.8 | 12.4 | 10.3 | 21.7 | 9.7 | 2.5 | 229.1 | 10.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
8 | -231 | -6.3 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.8 | 12.4 | 10.3 | 21.7 | 9.7 | 3.1 | 263.1 | 9.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
9 | -230 | -6.4 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.8 | 12.4 | 10.3 | 21.7 | 9.7 | 3.7 | 243 | 10.8 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
10 | -229 | -6.5 | 0 | 0 | 11.4 | 11.5 | 11.6 | 11.8 | 12.4 | 10.3 | 21.7 | 9.7 | 3.5 | 248.2 | 10.4 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
11 | -228 | -6.3 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.4 | 10.3 | 21.7 | 9.7 | 3.3 | 249.2 | 11.1 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
12 | -227 | -6.4 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.4 | 10.3 | 21.7 | 9.7 | 3.9 | 237.3 | 11.9 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
13 | -226 | -6.4 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.8 | 245.5 | 11.1 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
14 | -225 | -6.2 | 0 | 0 | 11.4 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 3.9 | 248 | 9.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
15 | -224 | -6.3 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 3.9 | 226.9 | 11.2 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
16 | -223 | -6.3 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.9 | 244.1 | 12.1 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
17 | -222 | -6.3 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.9 | 248 | 11.8 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
18 | -221 | -6.4 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 3.1 | 255.9 | 9.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
19 | -220 | -6.5 | 0 | 0 | 11.4 | 11.4 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 3.1 | 227.2 | 7.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
20 | -219 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.9 | 12.3 | 10.3 | 21.6 | 9.7 | 2.7 | 207.9 | 7.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
21 | -218 | -6.6 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.6 | 2.5 | 228 | 8.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
22 | -217 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.6 | 2.3 | 236 | 7.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
23 | -216 | -6.3 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.1 | 215.7 | 7.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
24 | -215 | -6.6 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.2 | 223.1 | 9.4 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
25 | -214 | -6.4 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.5 | 222.7 | 9.3 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
26 | -213 | -6.3 | 0 | 0 | 11.3 | 11.5 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.8 | 239.5 | 9.4 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
27 | -212 | -5.9 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 3.3 | 206.6 | 9.8 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
28 | -211 | -5.7 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.9 | 230 | 9.2 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
29 | -210 | -5.9 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.3 | 250.2 | 8.3 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
30 | -209 | -6.1 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.3 | 227.5 | 7.2 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
31 | -208 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.5 | 245.9 | 7.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
32 | -207 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.2 | 234.5 | 8.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
33 | -206 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.2 | 238 | 9.2 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
34 | -205 | -6 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 1.9 | 229.3 | 11 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
35 | -204 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.3 | 228 | 10.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
36 | -203 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.5 | 220.7 | 10.3 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
37 | -202 | -6.4 | 0 | 0 | 11.1 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.8 | 203.9 | 10.4 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
38 | -201 | -5.5 | 0 | 0 | 11.1 | 11.5 | 11.7 | 11.9 | 12.3 | 10.5 | 21.7 | 9.6 | 2.5 | 222.8 | 10.2 | 10.7 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
39 | -200 | -6 | 0 | 0 | 11.1 | 11.5 | 11.7 | 11.9 | 12.3 | 10.5 | 21.7 | 9.7 | 2.3 | 212.7 | 10.2 | 10.7 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
40 | -199 | -6.8 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.2 | 203.7 | 10.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
41 | -198 | -6.7 | 0 | 0 | 11.1 | 11.5 | 11.7 | 11.9 | 12.3 | 10.5 | 21.7 | 9.7 | 1.8 | 211.3 | 11.4 | 10.7 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
42 | -197 | -6.6 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 3 | 215.7 | 13.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
43 | -196 | -6.7 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 3.6 | 213.2 | 16.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
44 | -195 | -6.6 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 3.5 | 212.6 | 19.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
45 | -194 | -6.6 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 2.7 | 226.6 | 18 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
46 | -193 | -6.5 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 2.8 | 219.9 | 15.4 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
47 | -192 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.6 | 218.9 | 15.8 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
48 | -191 | -5.6 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.6 | 4 | 217.3 | 14.3 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
49 | -190 | -5.7 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.3 | 204.9 | 10.5 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.8 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
50 | -189 | -5.9 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.6 | 3.7 | 239.2 | 7.3 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
51 | -188 | -6.1 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.4 | 10.4 | 21.6 | 9.6 | 4.2 | 224.2 | 7.8 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
52 | -187 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.4 | 10.4 | 21.6 | 9.7 | 4.5 | 215.2 | 12.7 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
53 | -186 | -6.1 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 3.4 | 216.6 | 13.8 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
54 | -185 | -6.2 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.9 | 208.9 | 12.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
55 | -184 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.2 | 214 | 10 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
56 | -183 | -6.3 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 1.9 | 215.4 | 11.6 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
57 | -182 | -6.4 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 1.7 | 229.4 | 10.8 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
58 | -181 | -6.5 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 1.9 | 207.6 | 11.2 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
59 | -180 | -6.5 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.4 | 233.9 | 9.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
60 | -179 | -6.7 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.6 | 2.7 | 210.5 | 9.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
61 | -178 | -6.7 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.6 | 2.8 | 222.3 | 9.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
62 | -177 | -6.6 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 3 | 219.7 | 8.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
63 | -176 | -6.7 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.6 | 3.6 | 224 | 8.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
64 | -175 | -6.4 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 3.6 | 211.5 | 8.4 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
65 | -174 | -6.1 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.6 | 3.1 | 223 | 7.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
66 | -173 | -6.2 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.3 | 21.7 | 9.6 | 2.5 | 221 | 8.5 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
67 | -172 | -6.4 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.4 | 219.5 | 9.7 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
68 | -171 | -6.2 | 0 | 0 | 11.3 | 11.5 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 2.9 | 216.4 | 10.3 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
69 | -170 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 3.2 | 205.8 | 10.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
70 | -169 | -6.6 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 3.1 | 206.2 | 10.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
71 | -168 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.7 | 216.4 | 9.8 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
72 | -167 | -5.5 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.8 | 217.4 | 9.3 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
73 | -166 | -5.7 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.4 | 234.2 | 8.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
74 | -165 | -6 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.4 | 220.7 | 7.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
75 | -164 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.8 | 200.6 | 9.8 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
76 | -163 | -6.2 | 0 | 0 | 11.1 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.9 | 208.1 | 11 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
77 | -162 | -6.3 | 0 | 0 | 11.1 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.8 | 200.5 | 11.2 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
78 | -161 | -6.5 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.1 | 214.2 | 11.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
79 | -160 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.2 | 201.7 | 13.4 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
80 | -159 | -6 | 0 | 0 | 11.1 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.2 | 207 | 15.6 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
81 | -158 | -6 | 0 | 0 | 11.2 | 11.5 | 11.8 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.8 | 211.6 | 14.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
82 | -157 | -6.1 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.7 | 208.3 | 13 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
83 | -156 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.4 | 205.6 | 13 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
84 | -155 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.2 | 212.1 | 12.4 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
85 | -154 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.2 | 212.4 | 11.9 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
86 | -153 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.1 | 211.8 | 9.5 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
87 | -152 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 4.4 | 214.9 | 10.3 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
88 | -151 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 4.2 | 208.4 | 9.1 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
89 | -150 | -6.6 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 3.4 | 211.5 | 7.7 | 10.6 | 10.2 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
90 | -149 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.9 | 270.7 | 6.1 | 10.6 | 10.2 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
91 | -148 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.5 | 287.9 | 5.2 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
92 | -147 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.5 | 250.5 | 8.2 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
93 | -146 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3 | 231.8 | 11.2 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
94 | -145 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 1.9 | 237.2 | 11.6 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
95 | -144 | -6 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.2 | 250.8 | 11.4 | 10.6 | 10.1 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
96 | -143 | -6.1 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.4 | 225.3 | 11 | 10.6 | 10.1 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
97 | -142 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.3 | 253.7 | 11.1 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
98 | -141 | -6 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.9 | 239.6 | 9.2 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
99 | -140 | -6.1 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.2 | 226.8 | 8.5 | 10.6 | 10.1 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
100 | -139 | -6 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.4 | 258.4 | 10.1 | 10.6 | 10.1 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
101 | -138 | -6 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.6 | 244.7 | 11.3 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
102 | -137 | -6.2 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.5 | 240.5 | 13.6 | 10.6 | 10.1 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
103 | -136 | -6.5 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 3.2 | 227 | 12.3 | 10.6 | 10.1 | 10.2 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
104 | -135 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 3.1 | 243.5 | 11.6 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
105 | -134 | -5.9 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 3.4 | 242.3 | 11.8 | 10.6 | 10.1 | 10.2 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
106 | -133 | -5.9 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 3.3 | 233.6 | 12.3 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
107 | -132 | -5.9 | 0 | 0 | 11.2 | 11.5 | 11.6 | 11.9 | 12.3 | 10.1 | 21.7 | 9.7 | 3.3 | 244.8 | 12.3 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
108 | -131 | -5.9 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.1 | 21.7 | 9.7 | 4.3 | 236.7 | 13.9 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
109 | -130 | -5.8 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 4.3 | 232.2 | 13.2 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
110 | -129 | -6 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.9 | 237 | 12.8 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
111 | -128 | -6.5 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 3.1 | 248.1 | 12.9 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
112 | -127 | -6.7 | 0 | 0 | 11.1 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.7 | 236.5 | 11.7 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
113 | -126 | -6.3 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.5 | 201.7 | 10.3 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
114 | -125 | -5.9 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.8 | 254 | 8.6 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
115 | -124 | -6.2 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 3.4 | 218.2 | 9.9 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
116 | -123 | -6.3 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.9 | 218.3 | 13.6 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
117 | -122 | -6.1 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.8 | 217.2 | 15.6 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
118 | -121 | -6.1 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.5 | 211.1 | 16 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
119 | -120 | -6 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.2 | 21.7 | 9.7 | 2.6 | 225.5 | 13.5 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
120 | -119 | -6 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 1.9 | 231.5 | 10.2 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
121 | -118 | -6.3 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 2.2 | 219.6 | 7.4 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
122 | -117 | -6.4 | 0 | 0 | 10.9 | 11.5 | 11.6 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 3 | 211.3 | 6.6 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
123 | -116 | -6.3 | 0 | 0 | 10.9 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 3.5 | 222.2 | 7.1 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
124 | -115 | -6.1 | 0 | 0 | 10.9 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 3.3 | 225.2 | 8.3 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
125 | -114 | -6.2 | 0 | 0 | 10.9 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 4.2 | 207.8 | 8.1 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
126 | -113 | -6.4 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 3.7 | 226.5 | 7.6 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
127 | -112 | -6.3 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.4 | 10.3 | 21.7 | 9.7 | 4 | 245.7 | 7.3 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
128 | -111 | -6.4 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.4 | 10.2 | 21.7 | 9.7 | 2.9 | 234.9 | 7.8 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
129 | -110 | -6.5 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.4 | 10.2 | 21.7 | 9.7 | 3.5 | 246.1 | 7.9 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
130 | -109 | -6.5 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.4 | 10.2 | 21.7 | 9.7 | 3.8 | 238.6 | 7.8 | 10.6 | 10.1 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
131 | -108 | -6.4 | 0 | 0 | 11 | 11.5 | 11.6 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.3 | 213.3 | 8.4 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
132 | -107 | -6.3 | 0 | 0 | 11 | 11.5 | 11.6 | 11.9 | 12.4 | 10.2 | 21.7 | 9.7 | 3.2 | 224.7 | 11 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
133 | -106 | -6.3 | 0 | 0 | 11 | 11.5 | 11.6 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 2.7 | 219.7 | 14 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
134 | -105 | -6.3 | 0 | 0 | 11 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.3 | 246.4 | 11.9 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
135 | -104 | -5.8 | 0 | 0 | 11 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.7 | 228.8 | 11.8 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
136 | -103 | -5.8 | 0 | 0 | 11 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.8 | 254.8 | 11.5 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
137 | -102 | -6 | 0 | 0 | 11 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.7 | 249.8 | 12.6 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
138 | -101 | -6.1 | 0 | 0 | 11.1 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.4 | 230.5 | 13.1 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
139 | -100 | -6.2 | 0 | 0 | 11 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.8 | 246.5 | 13.1 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
140 | -99 | -6.3 | 0 | 0 | 11 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 5 | 247.6 | 13.3 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
141 | -98 | -6.5 | 0 | 0 | 11.1 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.5 | 236.3 | 12.8 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
142 | -97 | -6.6 | 0 | 0 | 11.1 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.6 | 231 | 11.5 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
143 | -96 | -6.7 | 0 | 0 | 11.1 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.5 | 205.7 | 11.8 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
144 | -95 | -6.6 | 0 | 0 | 11.1 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.3 | 213.1 | 14.2 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
145 | -94 | -6.4 | 0 | 0 | 11.1 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 5.6 | 236.7 | 13 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
146 | -93 | -6.1 | 0 | 0 | 11.1 | 11.4 | 11.8 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.6 | 218.3 | 14.7 | 10.6 | 10.2 | 10.4 | 11.3 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
147 | -92 | -6 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 3.3 | 216.4 | 17.6 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.2 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
148 | -91 | -6.2 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 3.4 | 223.3 | 16.8 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
149 | -90 | -6.3 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.3 | 21.6 | 9.7 | 5.4 | 219.1 | 13.8 | 10.6 | 10.2 | 10.3 | 11.3 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
150 | -89 | -6.3 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.3 | 21.6 | 9.7 | 5.2 | 212.8 | 16.1 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
151 | -88 | -6.3 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.3 | 21.6 | 9.7 | 5.1 | 217 | 16.8 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
152 | -87 | -6.3 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.3 | 21.6 | 9.7 | 4.5 | 218 | 16.9 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
153 | -86 | -6.4 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 4.8 | 229.6 | 16.2 | 10.6 | 10.2 | 10.3 | 11.2 | 10.6 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
154 | -85 | -6.4 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 4.4 | 219 | 15.8 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
155 | -84 | -6.3 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.4 | 10.2 | 21.7 | 9.6 | 5.7 | 251.9 | 14.3 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
156 | -83 | -6.2 | 0 | 0 | 11.2 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 7.2 | 197.7 | 8.7 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
157 | -82 | -6.1 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 8.1 | 209.6 | 13 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
158 | -81 | -6.4 | 0 | 0 | 11.2 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 5.8 | 223.9 | 18 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
159 | -80 | -6.3 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 5.6 | 222.2 | 22.3 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
160 | -79 | -6.5 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.4 | 217.1 | 22.6 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
161 | -78 | -6.6 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 4.1 | 208.4 | 18.6 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
162 | -77 | -6.7 | 0 | 0 | 11.2 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 4.5 | 218.4 | 18.5 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
163 | -76 | -6.3 | 0 | 0 | 11.2 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.1 | 212.9 | 21 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5 | 9.9 | 10.3
164 | -75 | -6.5 | 0 | 0 | 11.2 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 4.1 | 207.1 | 20 | 10.6 | 10.1 | 10.4 | 11.2 | 10.6 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
165 | -74 | -6.5 | 0 | 0 | 11.2 | 11.4 | 11.7 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 3.8 | 209.2 | 17 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
166 | -73 | -5.8 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 5.3 | 210.3 | 14.6 | 10.6 | 10.1 | 10.4 | 11.2 | 10.6 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
167 | -72 | -5.4 | 0 | 0 | 11.2 | 11.4 | 11.6 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 5 | 212 | 12 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
168 | -71 | -5.8 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.4 | 10.2 | 21.7 | 9.7 | 4.4 | 220.4 | 12.9 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
169 | -70 | -6.2 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 3.5 | 239.9 | 12.5 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
170 | -69 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.4 | 10.2 | 21.6 | 9.7 | 2.8 | 220.8 | 12.2 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
171 | -68 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.3 | 10.2 | 21.6 | 9.7 | 2.6 | 214.8 | 15 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
172 | -67 | -6.4 | 0 | 0 | 11.3 | 11.3 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.6 | 209.1 | 19.5 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
173 | -66 | -6.4 | 0 | 0 | 11.3 | 11.3 | 11.6 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2.6 | 202.9 | 19.2 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
174 | -65 | -6.3 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 1.6 | 209.1 | 17.4 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
175 | -64 | -6.1 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 1.5 | 208.2 | 16.5 | 10.6 | 10.1 | 10.4 | 11.2 | 10.6 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.8 | 12.6 | 9.5 | 9.9 | 10.3
176 | -63 | -6.1 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 1.3 | 210.6 | 15.2 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
177 | -62 | -6.1 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.2 | 21.6 | 9.7 | 1.4 | 214.4 | 14.2 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
178 | -61 | -6.1 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 1.6 | 210.5 | 13.5 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
179 | -60 | -5.9 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.2 | 21.7 | 9.7 | 2 | 207 | 13.1 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
180 | -59 | -6.2 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.2 | 21.6 | 9.7 | 2.3 | 207.1 | 12.2 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
181 | -58 | -6.2 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.3 | 21.6 | 9.7 | 2.5 | 204 | 11.8 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
182 | -57 | -6.4 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.3 | 21.6 | 9.7 | 2.1 | 202 | 10.7 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
183 | -56 | -6.6 | 0 | 0 | 11.3 | 11.3 | 11.7 | 11.8 | 12.3 | 10.3 | 21.6 | 9.7 | 1.9 | 205.9 | 11.7 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
184 | -55 | -6.8 | 0 | 0 | 11.3 | 11.3 | 11.8 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.3 | 206.7 | 13.3 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
185 | -54 | -6.8 | 0 | 0 | 11.3 | 11.3 | 11.8 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.1 | 206 | 12.4 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
186 | -53 | -6.8 | 0 | 0 | 11.3 | 11.3 | 11.8 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 1.5 | 191 | 12.2 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5 | 9.9 | 10.3
187 | -52 | -6.8 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.3 | 21.6 | 9.7 | 2 | 191.2 | 11.6 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
188 | -51 | -6.8 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.8 | 12.3 | 10.3 | 21.6 | 9.7 | 2.7 | 191.3 | 11 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
189 | -50 | -6.8 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.3 | 21.6 | 9.7 | 3.1 | 202.8 | 9.5 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
190 | -49 | -6.6 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.3 | 21.6 | 9.7 | 2.7 | 203.3 | 10.5 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
191 | -48 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.6 | 9.7 | 3.1 | 189.3 | 12.3 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
192 | -47 | -6.3 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.7 | 2.8 | 222.9 | 11.1 | 10.6 | 10.1 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
193 | -46 | -6.5 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.7 | 2.5 | 228 | 10.8 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
194 | -45 | -6.6 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.5 | 217.6 | 9.2 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
195 | -44 | -6.5 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.3 | 210.3 | 8.3 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
196 | -43 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 2.9 | 230.3 | 7.7 | 10.6 | 10.1 | 10.3 | 11.2 | 10.6 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
197 | -42 | -6.4 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.3 | 214.7 | 8.7 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
198 | -41 | -6.4 | 0 | 0 | 11.2 | 11.6 | 11.7 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.5 | 224.7 | 9.8 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 11 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
199 | -40 | -6.5 | 0 | 0 | 11.2 | 11.6 | 11.7 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.1 | 230.6 | 11.6 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
200 | -39 | -6.4 | 0 | 0 | 11.2 | 11.6 | 11.7 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 4.8 | 209.3 | 13.9 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
201 | -38 | -6.3 | 0 | 0 | 11.2 | 11.6 | 11.7 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 4 | 215.2 | 16.8 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
202 | -37 | -6 | 0 | 0 | 11.2 | 11.6 | 11.7 | 11.9 | 12.3 | 10.5 | 21.6 | 9.7 | 4.5 | 210.7 | 16.9 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
203 | -36 | -5.9 | 0 | 0 | 11.2 | 11.6 | 11.7 | 11.9 | 12.3 | 10.5 | 21.6 | 9.7 | 4.4 | 192.1 | 15.3 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
204 | -35 | -6.1 | 0 | 0 | 11.2 | 11.6 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 3.9 | 210.4 | 19.5 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
205 | -34 | -6.3 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 3.8 | 206.5 | 20.4 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
206 | -33 | -4 | 0 | 0 | 11.2 | 11.5 | 11.7 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.7 | 208.9 | 20.1 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
207 | -32 | -6.9 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.3 | 207.7 | 19.7 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
208 | -31 | -6.9 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.3 | 213 | 18.8 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
209 | -30 | -6.9 | 0 | 0 | 11.3 | 11.5 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.7 | 3.4 | 214.9 | 16.4 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
210 | -29 | -6.8 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.9 | 12.3 | 10.4 | 21.6 | 9.7 | 3.7 | 204.5 | 17.9 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
211 | -28 | -5.1 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.3 | 10.4 | 21.7 | 9.7 | 3.5 | 205.4 | 17.7 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
212 | -27 | -3.9 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.9 | 12.3 | 10.4 | 21.7 | 9.6 | 3.5 | 200.8 | 17 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
213 | -26 | -2.9 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.3 | 10.4 | 21.7 | 9.7 | 3.1 | 204.2 | 18.7 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
214 | -25 | -1.4 | 0 | 0 | 11.3 | 11.4 | 11.6 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2.3 | 219.3 | 14.7 | 10.6 | 10.1 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
215 | -24 | 0.1 | 0.04 | 0.046758 | 11.4 | 11.4 | 11.6 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2 | 208.7 | 15.5 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
216 | -23 | -0.6 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.7 | 2.7 | 206.5 | 16.4 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
217 | -22 | -2.8 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 3.8 | 204.5 | 18.8 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
218 | -21 | -5.2 | 0 | 0 | 11.4 | 11.4 | 11.6 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 3.3 | 198 | 19.4 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.6 | 9.5 | 9.9 | 10.3
219 | -20 | -5.9 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2.9 | 200.5 | 18.5 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
220 | -19 | -6.2 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 3.3 | 202.1 | 17.1 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
221 | -18 | -6.4 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.5 | 21.7 | 9.6 | 3.4 | 209.7 | 18.2 | 10.6 | 10.2 | 10.3 | 11.2 | 10.6 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
222 | -17 | -6.4 | 0 | 0 | 11.4 | 11.4 | 11.7 | 11.8 | 12.3 | 10.5 | 21.7 | 9.6 | 3.1 | 212.6 | 16.1 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
223 | -16 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.5 | 21.7 | 9.6 | 3.2 | 191.9 | 16.5 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
224 | -15 | -6.6 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 3.1 | 197.7 | 17.5 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
225 | -14 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 3.6 | 194.8 | 15.9 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
226 | -13 | -6.6 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2.9 | 208.6 | 16.1 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
227 | -12 | -6.7 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2.4 | 210 | 16.1 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
228 | -11 | -6.5 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2.4 | 194.3 | 15 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
229 | -10 | -6.6 | 0 | 0 | 11.3 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 3 | 197.8 | 12.3 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.1 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
230 | -9 | -6.7 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 3.7 | 213.9 | 11.8 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
231 | -8 | -6.8 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2.9 | 197.6 | 13.1 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.8 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
232 | -7 | -6.8 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2.3 | 201.5 | 13.5 | 10.6 | 10.2 | 10.3 | 11.2 | 10.6 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
233 | -6 | -6.8 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 2 | 205.1 | 14.3 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
234 | -5 | -6.9 | 0 | 0 | 11.2 | 11.4 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 1.8 | 200.7 | 14.8 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
235 | -4 | -6.9 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.6 | 1.8 | 203.9 | 14.4 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
236 | -3 | -6.9 | 0 | 0 | 11.3 | 11.4 | 11.7 | 11.8 | 12.3 | 10.4 | 21.7 | 9.7 | 1.9 | 191.6 | 13.4 | 10.6 | 10.2 | 10.3 | 11.2 | 10.7 | 12.4 | 11.2 | 11.3 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
237 | -2 | -6.9 | 0 | 0 | 11.3 | 11.5 | 11.8 | 11.8 | 12.3 | 10.4 | 21.7 | 9.7 | 2.3 | 203.5 | 14.1 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
238 | -1 | -5.3 | 0 | 0 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.7 | 196.7 | 17.3 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
239 | 0 | 179.1 | 71.64 | 83.743 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.6 | 192.7 | 17.8 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
240 | 1 | 344.7 | 137.88 | 161.1738 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.8 | 185.7 | 16.1 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.4 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
241 | 2 | 368.8 | 147.52 | 172.4424 | 11.3 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 3.1 | 197.4 | 16.8 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.5 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
242 | 3 | 338.1 | 135.24 | 158.0878 | 11.4 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 3.2 | 203.7 | 16.7 | 10.6 | 10.2 | 10.4 | 11.2 | 10.7 | 12.5 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
243 | 4 | 313 | 125.2 | 146.3516 | 11.4 | 11.5 | 11.7 | 11.8 | 12.3 | 10.3 | 21.7 | 9.7 | 2.7 | 206.8 | 17.7 | 10.6 | 10.2 | 10.7 | 11.2 | 10.7 | 12.5 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.8 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
244 | 5 | 298.4 | 119.36 | 139.525 | 11.4 | 11.5 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 3 | 224.8 | 16.7 | 10.6 | 10.5 | 14.2 | 11.2 | 10.7 | 12.9 | 11.2 | 11.4 | 10.9 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
245 | 6 | 295 | 118 | 137.9352 | 11.4 | 11.5 | 11.8 | 11.9 | 12.3 | 10.3 | 21.7 | 9.7 | 3.1 | 223.8 | 13.7 | 10.6 | 12 | 24.7 | 11.2 | 10.7 | 13.7 | 11.2 | 11.4 | 11.2 | 11.7 | 11.7 | 13.9 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.5 | 9.9 | 10.3
246 | 7 | 293.8 | 117.52 | 137.3741 | 11.4 | 11.5 | 11.9 | 12 | 12.3 | 10.3 | 21.7 | 9.7 | 2.6 | 214.8 | 12.6 | 10.6 | 14.2 | 49.1 | 11.2 | 10.7 | 15.5 | 11.2 | 11.7 | 12.9 | 11.7 | 11.7 | 14.2 | 12.8 | 12.9 | 13.8 | 12.6 | 11.9 | 12.2 | 12.7 | 13.5 | 12.7 | 12.6 | 12 | 12.5 | 9.6 | 9.9 | 10.3
247 | 8 | 285.4 | 114.16 | 133.4465 | 11.4 | 11.5 | 12 | 12.2 | 12.3 | 10.3 | 21.7 | 9.7 | 2.8 | 206.4 | 14.5 | 10.7 | 17.6 | 74 | 11.2 | 10.7 | 18.5 | 11.2 | 13.5 | 16.5 | 11.7 | 11.7 | 15 | 12.8 | 12.9 | 13.9 | 12.6 | 11.9 | 12.8 | 12.7 | 13.6 | 12.8 | 12.6 | 12.1 | 12.5 | 9.6 | 9.9 | 10.3
248 | 9 | 280.6 | 112.24 | 131.2021 | 11.4 | 11.5 | 12.2 | 12.4 | 13.8 | 10.3 | 21.7 | 9.7 | 2.7 | 207.2 | 14.6 | 10.9 | 22.2 | 96.7 | 11.2 | 10.7 | 22.1 | 11.2 | 16.5 | 21.5 | 11.7 | 11.7 | 16.2 | 12.8 | 12.9 | 13.9 | 12.6 | 12.9 | 15.1 | 12.8 | 14.6 | 12.8 | 12.6 | 12.2 | 12.5 | 9.7 | 9.9 | 10.3
249 | 10 | 277.6 | 111.04 | 129.7994 | 11.5 | 11.6 | 12.3 | 12.6 | 17.9 | 10.4 | 21.7 | 9.7 | 2.5 | 199.2 | 14.4 | 11.3 | 27 | 125.8 | 11.2 | 10.8 | 27.2 | 11.2 | 19.8 | 26.5 | 11.7 | 11.7 | 17.2 | 12.8 | 12.9 | 13.9 | 12.6 | 14.5 | 18.6 | 13.3 | 15.9 | 12.8 | 12.7 | 12.3 | 12.6 | 9.8 | 9.9 | 10.3
250 | 11 | 275.6 | 110.24 | 128.8642 | 12.1 | 11.8 | 12.6 | 13 | 23.2 | 10.4 | 21.7 | 9.6 | 3 | 209.9 | 13.7 | 12 | 33.9 | 152.9 | 11.2 | 10.8 | 34.9 | 11.2 | 23.6 | 31.6 | 11.7 | 11.7 | 18.2 | 12.8 | 12.9 | 13.9 | 12.6 | 16.9 | 22.8 | 13.9 | 17.3 | 12.8 | 12.8 | 12.4 | 12.6 | 9.8 | 9.9 | 10.3
251 | 12 | 275.6 | 110.24 | 128.8642 | 12.7 | 12.5 | 13 | 13.4 | 28.2 | 10.4 | 21.7 | 9.7 | 2.4 | 215.1 | 12.3 | 12.8 | 40.9 | 183.6 | 11.2 | 11 | 42 | 11.2 | 27 | 36.4 | 11.7 | 11.7 | 19.1 | 12.8 | 12.9 | 13.9 | 12.6 | 18.9 | 25.8 | 14.3 | 18 | 12.8 | 13 | 12.5 | 12.6 | 9.9 | 10 | 10.3
252 | 13 | 275.1 | 110.04 | 128.6304 | 13.4 | 13.2 | 13.5 | 13.8 | 32.5 | 10.5 | 21.7 | 9.6 | 2.6 | 196.5 | 9.8 | 13.9 | 47.5 | 212.2 | 11.2 | 11.1 | 49.9 | 11.2 | 33.4 | 47.3 | 11.7 | 11.7 | 21.2 | 12.8 | 12.9 | 13.9 | 12.6 | 21.5 | 30.5 | 15.1 | 19.6 | 12.9 | 13.1 | 12.7 | 12.6 | 10 | 10 | 10.3
253 | 14 | 275.6 | 110.24 | 128.8642 | 13.7 | 14 | 14.2 | 14.6 | 38.3 | 10.6 | 21.7 | 9.7 | 2.8 | 209 | 9.5 | 15.3 | 54.6 | 249.2 | 11.2 | 11.3 | 57.6 | 11.2 | 37.9 | 53 | 11.7 | 11.7 | 22.6 | 12.8 | 12.9 | 13.9 | 12.7 | 24.2 | 34 | 15.4 | 20.9 | 12.9 | 13.5 | 12.9 | 12.6 | 10.1 | 10 | 10.3
254 | 15 | 275.5 | 110.2 | 128.8175 | 14 | 15 | 15.1 | 15.4 | 41.9 | 10.6 | 21.7 | 9.7 | 3.7 | 200.5 | 9.7 | 17 | 61.1 | 275.1 | 11.2 | 11.5 | 65.1 | 11.3 | 42.4 | 58.9 | 11.7 | 11.7 | 24.2 | 12.8 | 12.9 | 13.9 | 12.7 | 26.9 | 37.3 | 15.9 | 21.3 | 13 | 14.1 | 13.3 | 12.7 | 10.3 | 10.1 | 10.3
255 | 16 | 275.4 | 110.16 | 128.7707 | 14.6 | 15.8 | 16.1 | 16.4 | 46.1 | 10.7 | 21.7 | 9.7 | 4.5 | 203.2 | 11.4 | 18.9 | 67 | 293.5 | 11.3 | 11.7 | 72.8 | 11.3 | 46.3 | 63.2 | 11.7 | 11.7 | 25.1 | 12.8 | 12.9 | 13.9 | 12.8 | 29.3 | 41.7 | 16.2 | 21.9 | 13.1 | 14.8 | 13.9 | 12.7 | 10.4 | 10.1 | 10.3
256 | 17 | 276.2 | 110.48 | 129.1448 | 15.3 | 16.6 | 17.2 | 17.4 | 50.9 | 10.7 | 21.7 | 9.7 | 4.2 | 200.5 | 13.9 | 21 | 75.6 | 338.8 | 11.3 | 12 | 80.7 | 11.4 | 51.9 | 68.8 | 11.7 | 11.7 | 27.1 | 12.8 | 12.9 | 14 | 12.8 | 32 | 46.9 | 16.8 | 23.6 | 13.1 | 15.8 | 14.5 | 12.7 | 10.5 | 10.2 | 10.4
257 | 18 | 277.5 | 111 | 129.7526 | 16.3 | 18.1 | 18.4 | 18.5 | 57.3 | 10.7 | 21.6 | 9.7 | 2.9 | 207.1 | 14.7 | 23.3 | 82.7 | 362.3 | 11.3 | 12.4 | 88 | 11.4 | 57.3 | 80.3 | 11.7 | 11.8 | 28.9 | 12.8 | 12.9 | 14 | 12.9 | 34.9 | 52.6 | 17.6 | 25.1 | 13.2 | 16.8 | 15.4 | 12.8 | 10.6 | 10.2 | 10.4
258 | 19 | 279.6 | 111.84 | 130.7345 | 17.2 | 19.6 | 19.8 | 19.6 | 62.9 | 10.8 | 21.7 | 9.7 | 3.3 | 231.4 | 12.8 | 25.8 | 92.4 | 383.3 | 11.3 | 12.8 | 96.9 | 11.5 | 61.4 | 85.4 | 11.7 | 11.8 | 30.1 | 12.8 | 12.9 | 14.1 | 13 | 38.1 | 56.2 | 17.8 | 26.2 | 13.3 | 17.8 | 16.5 | 12.8 | 10.7 | 10.3 | 10.4
259 | 20 | 280.1 | 112.04 | 130.9683 | 18.3 | 20.5 | 21.5 | 20.8 | 66 | 10.8 | 21.7 | 9.7 | 4.6 | 219.3 | 10.2 | 28.4 | 103.9 | 416.3 | 11.3 | 13.3 | 105.4 | 11.6 | 66.2 | 91.6 | 11.7 | 11.8 | 32.6 | 12.8 | 12.9 | 14.1 | 13.1 | 40.7 | 58.2 | 17.7 | 26.6 | 13.4 | 19.1 | 17.4 | 12.9 | 10.9 | 10.3 | 10.5
260 | 21 | 280 | 112 | 130.9215 | 19.8 | 21.5 | 23.1 | 22.1 | 70.5 | 10.9 | 21.7 | 9.7 | 3.7 | 232.7 | 9.3 | 31.1 | 110.9 | 445.4 | 11.4 | 13.8 | 113.1 | 11.7 | 71.3 | 98.6 | 11.7 | 11.8 | 35.3 | 12.8 | 12.9 | 14.2 | 13.2 | 44.2 | 62.8 | 18.6 | 27.9 | 13.5 | 20.5 | 18.4 | 12.9 | 11 | 10.4 | 10.5
261 | 22 | 281.6 | 112.64 | 131.6697 | 21.4 | 22.8 | 24.8 | 23.5 | 75.7 | 10.9 | 21.7 | 9.8 | 2.2 | 233.3 | 8.3 | 33.8 | 123.5 | 484.1 | 11.4 | 14.5 | 120.4 | 11.8 | 75.5 | 105.1 | 11.7 | 11.9 | 37.5 | 12.8 | 12.9 | 14.2 | 13.4 | 47.4 | 66.7 | 19.2 | 29.4 | 13.5 | 21.8 | 19.6 | 13 | 11.2 | 10.4 | 10.5
262 | 23 | 282.2 | 112.88 | 131.9502 | 23.2 | 24.6 | 26.4 | 25 | 79.5 | 11 | 21.7 | 9.8 | 3.1 | 256.7 | 8.9 | 36.5 | 136.4 | 500 | 11.4 | 15.1 | 129.1 | 11.9 | 80 | 112.4 | 11.7 | 11.9 | 40 | 12.8 | 12.9 | 14.2 | 13.5 | 50.5 | 71.4 | 19.7 | 30.6 | 13.6 | 23.3 | 20.4 | 13 | 11.5 | 10.5 | 10.6
263 | 24 | 282.8 | 113.12 | 132.2308 | 24.9 | 26.5 | 28 | 26.5 | 84 | 11 | 21.7 | 9.8 | 2.9 | 222.6 | 9 | 39 | 144.8 | 512.2 | 11.5 | 15.8 | 138.2 | 12.1 | 85.9 | 122.8 | 11.7 | 11.9 | 42.5 | 12.8 | 12.9 | 14.3 | 13.7 | 54 | 76 | 20.7 | 31.6 | 13.7 | 25.2 | 21.6 | 13.1 | 11.7 | 10.6 | 10.6
264 | 25 | 282.3 | 112.92 | 131.997 | 26.3 | 28.6 | 29.9 | 27.8 | 88.1 | 11 | 21.7 | 9.9 | 3 | 238.2 | 8.5 | 41.3 | 151.5 | 532.7 | 11.6 | 16.6 | 146.5 | 12.2 | 89.7 | 125 | 11.7 | 12 | 43.9 | 12.8 | 12.9 | 14.3 | 13.8 | 57.4 | 78.7 | 21 | 31.8 | 13.8 | 26.6 | 22.8 | 13.2 | 11.9 | 10.6 | 10.7
265 | 26 | 283.7 | 113.48 | 132.6516 | 28.1 | 31 | 31.5 | 29.3 | 90.5 | 11.1 | 21.7 | 9.9 | 3.5 | 243.4 | 10.3 | 43.4 | 164.6 | 544.1 | 11.6 | 17.4 | 155.8 | 12.4 | 92.4 | 126.7 | 11.7 | 12 | 46 | 12.8 | 12.9 | 14.4 | 14 | 60.3 | 81.4 | 21.5 | 32 | 13.9 | 28.1 | 24 | 13.3 | 12 | 10.7 | 10.7
266 | 27 | 283.8 | 113.52 | 132.6983 | 29.8 | 32.6 | 33.3 | 30.8 | 94.4 | 11.1 | 21.7 | 9.9 | 3.1 | 242.3 | 11.9 | 45.3 | 173.5 | 571 | 11.7 | 18.2 | 165.9 | 12.6 | 94.4 | 130.1 | 11.7 | 12.1 | 46.7 | 12.8 | 12.9 | 14.5 | 14.2 | 62.7 | 81.8 | 21.1 | 32.6 | 14 | 29.6 | 25.5 | 13.4 | 12.2 | 10.7 | 10.8
267 | 28 | 283.6 | 113.44 | 132.6048 | 31.5 | 34.1 | 35.1 | 32.4 | 98.5 | 11.1 | 21.7 | 10 | 2.8 | 230 | 11.1 | 47 | 182.3 | 583.9 | 11.8 | 19.1 | 174.5 | 12.8 | 97.5 | 139.9 | 11.7 | 12.1 | 48.8 | 12.8 | 12.9 | 14.6 | 14.3 | 65.2 | 86.7 | 22.2 | 33.5 | 14.1 | 31.4 | 26.8 | 13.4 | 12.3 | 10.8 | 10.8
268 | 29 | 283.4 | 113.36 | 132.5113 | 32.8 | 35.7 | 37.1 | 34 | 105.1 | 11.1 | 21.7 | 10.1 | 2.8 | 232.8 | 10.8 | 48.5 | 188.1 | 585.4 | 11.9 | 20 | 184 | 13 | 99.5 | 143.1 | 11.8 | 12.2 | 49.4 | 12.8 | 12.9 | 14.7 | 14.5 | 67.9 | 89 | 22.2 | 34.8 | 14.1 | 33.6 | 28.1 | 13.6 | 12.5 | 10.9 | 10.9
269 | 30 | 285.2 | 114.08 | 133.3529 | 34.3 | 38 | 39.2 | 35.6 | 108 | 11.1 | 21.7 | 10.3 | 2.7 | 227 | 10.6 | 49.8 | 198.6 | 589.6 | 11.9 | 20.9 | 193.3 | 13.2 | 100.7 | 143.4 | 11.8 | 12.2 | 50.4 | 12.8 | 12.9 | 14.7 | 14.7 | 70.4 | 91 | 22 | 35.7 | 14.2 | 35.5 | 29.4 | 13.7 | 12.8 | 10.9 | 11
270 | 31 | 285.3 | 114.12 | 133.3997 | 35.8 | 40.5 | 41.4 | 37.2 | 110 | 11.1 | 21.7 | 10.4 | 2.9 | 230.2 | 8.9 | 51 | 204.7 | 594.7 | 12 | 21.9 | 201.5 | 13.4 | 103 | 149.3 | 11.8 | 12.3 | 52.4 | 12.8 | 12.9 | 14.8 | 14.9 | 72.2 | 91.9 | 21.6 | 35.9 | 14.3 | 36.8 | 30.6 | 13.7 | 13.1 | 11 | 11
271 | 32 | 285.1 | 114.04 | 133.3062 | 37.3 | 42.1 | 43.5 | 38.8 | 112.2 | 11.2 | 21.6 | 10.6 | 2.7 | 241.3 | 7.7 | 52.1 | 209.4 | 606.6 | 12.2 | 22.8 | 209.5 | 13.6 | 104.9 | 151.1 | 11.8 | 12.3 | 53.9 | 12.8 | 12.9 | 14.8 | 15.1 | 74.6 | 95.1 | 22.1 | 36.5 | 14.4 | 38.2 | 32 | 13.8 | 13.3 | 11.1 | 11.1
272 | 33 | 284.6 | 113.84 | 133.0724 | 38.8 | 43.7 | 45.4 | 40.5 | 114.8 | 11.2 | 21.6 | 10.9 | 2.5 | 250.9 | 7.6 | 53 | 214.7 | 611.4 | 12.3 | 23.8 | 216.3 | 13.8 | 107.3 | 154 | 11.8 | 12.4 | 54.9 | 12.8 | 12.9 | 14.9 | 15.3 | 77.2 | 97.1 | 22.3 | 37.4 | 14.4 | 39.5 | 33.8 | 13.8 | 13.6 | 11.2 | 11.2
273 | 34 | 286.9 | 114.76 | 134.1478 | 40.4 | 45.8 | 47.1 | 42.2 | 116.4 | 11.2 | 21.6 | 11.2 | 2.6 | 233.8 | 8.2 | 53.8 | 216.8 | 625.2 | 12.4 | 24.7 | 223.1 | 14.1 | 110.8 | 157.7 | 11.8 | 12.5 | 56.4 | 12.8 | 12.9 | 14.9 | 15.5 | 79.2 | 99.6 | 22 | 38.5 | 14.5 | 41 | 35.1 | 14 | 13.8 | 11.2 | 11.2
274 | 35 | 288.1 | 115.24 | 134.7089 | 42.1 | 48.4 | 48.8 | 43.8 | 117.4 | 11.2 | 21.6 | 11.5 | 2.9 | 233.8 | 8.4 | 54.5 | 218.7 | 620 | 12.5 | 25.6 | 229.5 | 14.3 | 113.9 | 161.8 | 11.8 | 12.5 | 57.3 | 12.8 | 12.9 | 15.1 | 15.7 | 81.3 | 102.4 | 22 | 39.5 | 14.6 | 42.8 | 36.3 | 14.1 | 14 | 11.3 | 11.3
275 | 36 | 288.4 | 115.36 | 134.8492 | 43.9 | 50.9 | 50.4 | 45.3 | 118.5 | 11.3 | 21.6 | 11.7 | 2.7 | 258.7 | 7.8 | 55.2 | 219.2 | 626.7 | 12.7 | 26.6 | 236.2 | 14.6 | 117.1 | 165 | 11.9 | 12.6 | 58.8 | 12.8 | 12.9 | 15.2 | 15.9 | 83.1 | 104 | 22.1 | 40.4 | 14.7 | 44.3 | 37.8 | 14.2 | 14.2 | 11.4 | 11.4
276 | 37 | 288.1 | 115.24 | 134.7089 | 45.9 | 53.2 | 51.9 | 46.8 | 119 | 11.3 | 21.6 | 12 | 2.8 | 246.9 | 8.3 | 55.8 | 221.2 | 632.8 | 12.8 | 27.5 | 243.3 | 14.8 | 120 | 168.9 | 11.9 | 12.6 | 60.2 | 12.8 | 12.9 | 15.2 | 16 | 84.8 | 105.5 | 22.2 | 41.1 | 14.8 | 46 | 39 | 14.3 | 14.4 | 11.5 | 11.4
277 | 38 | 287.6 | 115.04 | 134.4751 | 47.8 | 55.9 | 53.3 | 48.2 | 119.6 | 11.4 | 21.6 | 12.3 | 2.6 | 232.2 | 9.1 | 56.3 | 228.5 | 631.1 | 13 | 28.4 | 252.3 | 15.1 | 122.7 | 172.2 | 11.9 | 12.7 | 61.3 | 12.8 | 12.9 | 15.2 | 16.2 | 86.8 | 106.5 | 22 | 42 | 14.8 | 47.6 | 40.3 | 14.5 | 14.5 | 11.6 | 11.5
278 | 39 | 287.6 | 115.04 | 134.4751 | 49.5 | 57.9 | 54.6 | 49.7 | 120 | 11.4 | 21.6 | 12.5 | 2.2 | 239.2 | 9.6 | 56.7 | 230.8 | 625.2 | 13.1 | 29.4 | 261.9 | 15.3 | 129.3 | 177.9 | 11.9 | 12.7 | 65 | 12.8 | 12.9 | 15.3 | 16.4 | 89 | 108.6 | 22 | 43.5 | 14.9 | 49.4 | 41.7 | 14.6 | 14.8 | 11.7 | 11.6
279 | 40 | 289.6 | 115.84 | 135.4103 | 51.3 | 59.8 | 55.9 | 51.2 | 121.8 | 11.4 | 21.6 | 12.7 | 2.3 | 234 | 9.6 | 57.2 | 232.8 | 634.2 | 13.3 | 30.4 | 270.6 | 15.6 | 132.2 | 180.8 | 11.9 | 12.8 | 66.4 | 12.8 | 12.9 | 15.5 | 16.6 | 91.4 | 110.3 | 22.3 | 44.7 | 15 | 50.6 | 43.7 | 14.6 | 15.1 | 11.8 | 11.6
280 | 41 | 289.8 | 115.92 | 135.5038 | 53 | 62.1 | 57.3 | 52.6 | 122.5 | 11.5 | 21.6 | 13 | 2.3 | 251.8 | 9.1 | 57.5 | 233.5 | 642.5 | 13.5 | 31.4 | 277.8 | 15.9 | 135.9 | 184.3 | 12 | 12.9 | 67.4 | 12.8 | 12.9 | 15.5 | 16.7 | 93.2 | 112.7 | 22.6 | 44.8 | 15.1 | 52 | 45 | 14.7 | 15.2 | 11.9 | 11.7
281 | 42 | 289.5 | 115.8 | 135.3635 | 54.2 | 63.7 | 58.6 | 54 | 124.2 | 11.5 | 21.6 | 13.2 | 2.1 | 223.6 | 8.2 | 57.9 | 236.4 | 657.9 | 13.6 | 32.4 | 287.5 | 16.2 | 138 | 185.9 | 12 | 12.9 | 69.1 | 12.8 | 13 | 15.5 | 16.9 | 95.3 | 114.3 | 22.4 | 45.4 | 15.2 | 53.6 | 46.8 | 14.8 | 15.4 | 12 | 11.8
282 | 43 | 289.1 | 115.64 | 135.1765 | 55.6 | 65.6 | 59.7 | 55.3 | 127.3 | 11.6 | 21.6 | 13.4 | 2.9 | 239.4 | 6.9 | 58.2 | 236.6 | 663.1 | 13.8 | 33.5 | 296.6 | 16.5 | 144.1 | 191.5 | 12 | 13 | 72.4 | 12.8 | 13 | 15.6 | 17.1 | 98.2 | 118.4 | 23.3 | 46.9 | 15.3 | 55.1 | 48.6 | 14.9 | 15.7 | 12.1 | 11.9
283 | 44 | 288.8 | 115.52 | 135.0362 | 56.9 | 66.9 | 60.8 | 56.8 | 129.5 | 11.7 | 21.6 | 13.7 | 3.1 | 251.9 | 6.5 | 58.4 | 236.5 | 673.8 | 14 | 34.5 | 304.1 | 16.8 | 147.7 | 195.4 | 12 | 13.1 | 74 | 12.8 | 13 | 15.7 | 17.3 | 100.9 | 120.7 | 23.7 | 47.4 | 15.3 | 56.5 | 50.2 | 15 | 16 | 12.2 | 12
284 | 45 | 290 | 116 | 135.5973 | 58.2 | 67.7 | 61.9 | 58.2 | 129.4 | 11.8 | 21.6 | 13.9 | 3.2 | 233.9 | 7.9 | 58.7 | 237.5 | 670.8 | 14.2 | 35.6 | 310.8 | 17.2 | 151.3 | 202.6 | 12.1 | 13.1 | 76.1 | 12.8 | 13 | 15.8 | 17.4 | 103.1 | 122.4 | 24 | 48.6 | 15.4 | 57.7 | 51.9 | 15.1 | 16.2 | 12.3 | 12
285 | 46 | 291.7 | 116.68 | 136.3922 | 59.5 | 69 | 63.2 | 59.5 | 130.2 | 11.9 | 21.6 | 14.2 | 3.1 | 237.2 | 8.7 | 58.9 | 236.6 | 664.1 | 14.4 | 36.6 | 315.8 | 17.5 | 152.8 | 202 | 12.1 | 13.2 | 77 | 12.8 | 13 | 15.9 | 17.6 | 104.9 | 124.9 | 24.3 | 49.1 | 15.5 | 58.9 | 53.4 | 15.2 | 16.5 | 12.4 | 12.1
286 | 47 | 291.5 | 116.6 | 136.2987 | 60.6 | 71 | 64.4 | 60.8 | 131.9 | 12 | 21.6 | 14.4 | 2.6 | 233.7 | 9.3 | 59.1 | 233.8 | 652.3 | 14.6 | 37.6 | 320.7 | 17.9 | 153.8 | 202.5 | 12.1 | 13.3 | 77.9 | 12.8 | 13 | 15.9 | 17.8 | 107.2 | 127 | 24.4 | 49.6 | 15.6 | 60.4 | 54.6 | 15.5 | 16.7 | 12.5 | 12.2
287 | 48 | 290.7 | 116.28 | 135.9246 | 61.8 | 73.3 | 65.7 | 62.2 | 133.8 | 12.1 | 21.6 | 14.6 | 2.9 | 228.1 | 8.5 | 59.2 | 234.1 | 647.4 | 14.8 | 38.6 | 326.1 | 18.3 | 153.9 | 205 | 12.1 | 13.4 | 78.5 | 12.8 | 13 | 15.9 | 18 | 108.7 | 127.7 | 24.5 | 50.3 | 15.7 | 62 | 56.1 | 15.6 | 17 | 12.6 | 12.3
288 | 49 | 290.7 | 116.28 | 135.9246 | 62.8 | 74.8 | 67 | 63.3 | 135.9 | 12.1 | 21.6 | 14.8 | 3 | 237.9 | 7.2 | 59.3 | 231.5 | 646.7 | 15 | 39.5 | 332.7 | 18.7 | 153.9 | 206.7 | 12.2 | 13.5 | 79.4 | 12.8 | 13 | 16 | 18.2 | 110 | 128.4 | 24.4 | 50.9 | 15.8 | 63.6 | 57 | 15.7 | 17.4 | 12.7 | 12.4
289 | 50 | 290.2 | 116.08 | 135.6908 | 63.7 | 75.7 | 68.5 | 64.5 | 136.9 | 12.2 | 21.6 | 15 | 3.6 | 224.2 | 7.6 | 59.4 | 229.6 | 653.8 | 15.2 | 40.4 | 337.5 | 19.1 | 154.6 | 208.8 | 12.2 | 13.5 | 80.7 | 12.8 | 13 | 16.1 | 18.4 | 111.5 | 129.9 | 24.1 | 51.5 | 15.9 | 65.2 | 58.2 | 15.6 | 17.8 | 12.8 | 12.5
290 | 51 | 290 | 116 | 135.5973 | 64.6 | 77.2 | 70.3 | 65.6 | 138.9 | 12.2 | 21.6 | 15.3 | 4.2 | 221.8 | 7.5 | 59.4 | 228.1 | 650.1 | 15.4 | 41.3 | 341.5 | 19.5 | 153.8 | 208.9 | 12.2 | 13.6 | 81.1 | 12.8 | 13.1 | 16.2 | 18.7 | 112.1 | 130.7 | 23.8 | 51.4 | 15.9 | 66.2 | 59.4 | 15.7 | 18 | 12.9 | 12.5
291 | 52 | 290.9 | 116.36 | 136.0181 | 65.8 | 78.5 | 71.7 | 66.6 | 139.5 | 12.2 | 21.6 | 15.5 | 4.1 | 219.7 | 8.9 | 59.5 | 227.5 | 630.9 | 15.6 | 42.2 | 345.3 | 19.9 | 152.1 | 206.7 | 12.2 | 13.7 | 81.4 | 12.8 | 13.1 | 16.4 | 18.9 | 113.2 | 131 | 23.8 | 51.5 | 16 | 67.1 | 60.3 | 15.8 | 18.2 | 13.1 | 12.6
292 | 53 | 292.8 | 117.12 | 136.9065 | 66.9 | 79.5 | 73.2 | 67.4 | 138.7 | 12.2 | 21.6 | 15.7 | 3.9 | 219.9 | 10.6 | 59.5 | 228 | 631.3 | 15.8 | 43.1 | 348.5 | 20.2 | 150.1 | 205.1 | 12.3 | 13.8 | 81.7 | 12.8 | 13.1 | 16.6 | 19.1 | 113.2 | 129.8 | 23.2 | 51.1 | 16.1 | 68.3 | 61.4 | 15.8 | 18.4 | 13.2 | 12.7
293 | 54 | 293 | 117.2 | 137 | 68 | 80.7 | 75 | 68 | 136.3 | 12.2 | 21.6 | 16 | 4.1 | 227.5 | 11.7 | 59.4 | 238.2 | 644 | 16 | 43.9 | 353.5 | 20.6 | 149.5 | 206.5 | 12.3 | 13.9 | 82.7 | 12.8 | 13.1 | 16.6 | 19.3 | 112.9 | 128.7 | 22.6 | 50.5 | 16.1 | 69.6 | 62.4 | 15.8 | 18.7 | 13.3 | 12.8
294 | 55 | 293.4 | 117.36 | 137.1871 | 69.2 | 81.7 | 76.7 | 68.9 | 136.5 | 12.3 | 21.6 | 16.2 | 4.4 | 213 | 11.9 | 59.4 | 249.2 | 655.4 | 16.2 | 44.8 | 360.5 | 21 | 149.7 | 206.3 | 12.3 | 13.9 | 84 | 12.8 | 13.1 | 16.6 | 19.4 | 113.8 | 131.3 | 23 | 51.4 | 16.2 | 71 | 63.7 | 15.9 | 19 | 13.3 | 12.9
295 | 56 | 293.6 | 117.44 | 137.2806 | 70.2 | 82.8 | 78.3 | 69.9 | 138.2 | 12.3 | 21.6 | 16.4 | 4.4 | 227.3 | 10.5 | 59.4 | 249.2 | 652 | 16.4 | 45.6 | 365.6 | 21.4 | 148.8 | 202.9 | 12.4 | 14 | 84.3 | 12.8 | 13.1 | 16.7 | 19.6 | 114.9 | 133.1 | 22.9 | 52 | 16.3 | 72.4 | 64.8 | 16 | 19.2 | 13.4 | 13
296 | 57 | 293.3 | 117.32 | 137.1403 | 71.2 | 84.2 | 79.7 | 70.9 | 138.7 | 12.3 | 21.6 | 16.6 | 4.5 | 233.5 | 9.8 | 59.3 | 247.5 | 646 | 16.7 | 46.5 | 370.5 | 21.8 | 147.7 | 199.2 | 12.4 | 14.1 | 84.7 | 12.8 | 13.2 | 16.8 | 19.7 | 115.6 | 133.2 | 22.7 | 52.6 | 16.3 | 73.6 | 65.7 | 16.1 | 19.5 | 13.5 | 13.1
297 | 58 | 292.8 | 117.12 | 136.9065 | 72.2 | 85.2 | 80.9 | 71.9 | 138.5 | 12.4 | 21.6 | 16.9 | 3 | 232 | 9.5 | 59.2 | 245.1 | 648.9 | 16.9 | 47.3 | 376.9 | 22.2 | 148.3 | 201.9 | 12.4 | 14.2 | 86 | 12.8 | 13.2 | 16.9 | 19.9 | 116.3 | 134.4 | 22.8 | 52.4 | 16.4 | 74.9 | 66.6 | 16.2 | 19.8 | 13.6 | 13.2
298 | 59 | 292.8 | 117.12 | 136.9065 | 73.4 | 86.4 | 82.5 | 72.8 | 140.8 | 12.4 | 21.6 | 17 | 2.6 | 279.8 | 8.1 | 59.2 | 243 | 633.4 | 17.2 | 48.2 | 382.4 | 22.6 | 147.7 | 200.2 | 12.5 | 14.2 | 86.6 | 12.8 | 13.2 | 16.9 | 20 | 117.6 | 136.6 | 23.3 | 52.9 | 16.5 | 76 | 67.8 | 16.2 | 20.2 | 13.7 | 13.3
299 | 60 | 291.6 | 116.64 | 136.3454 | 74.4 | 87.5 | 83.9 | 73.7 | 140.6 | 12.4 | 21.6 | 17.2 | 1.8 | 227.5 | 7.7 | 59.1 | 243.1 | 637.1 | 17.5 | 49.1 | 387.5 | 23 | 146.9 | 198.3 | 12.5 | 14.3 | 87.1 | 12.8 | 13.2 | 17.1 | 20.2 | 117.7 | 136 | 22.9 | 53.5 | 16.6 | 76.9 | 69.6 | 16.4 | 20.4 | 13.8 | 13.3
300 | 61 | 292.8 | 117.12 | 136.9065 | 75 | 88.5 | 85 | 74.4 | 139.9 | 12.5 | 21.6 | 17.3 | 1.3 | 233.9 | 7.9 | 59 | 244.7 | 656.6 | 17.8 | 50 | 393.7 | 23.4 | 147.4 | 198.5 | 12.5 | 14.4 | 88.6 | 12.8 | 13.3 | 17.2 | 20.4 | 118 | 135.8 | 22.6 | 54.1 | 16.6 | 78.1 | 70.8 | 16.5 | 20.7 | 13.9 | 13.4
301 | 62 | 293.1 | 117.24 | 137.0468 | 75.6 | 89.9 | 86.3 | 74.9 | 140.3 | 12.6 | 21.6 | 17.5 | 1.7 | 213.2 | 8.2 | 58.9 | 245.6 | 660.3 | 18 | 51 | 397.5 | 23.8 | 148.8 | 201.1 | 12.6 | 14.4 | 90.7 | 12.8 | 13.3 | 17.4 | 20.5 | 118.7 | 136.5 | 22.8 | 55.1 | 16.7 | 79 | 71.5 | 16.7 | 21 | 14 | 13.6
302 | 63 | 292.1 | 116.84 | 136.5792 | 76.2 | 91.1 | 87.4 | 75.5 | 140.5 | 12.6 | 21.6 | 17.7 | 2.6 | 204.3 | 11.2 | 58.8 | 244.5 | 665.7 | 18.3 | 52 | 400.4 | 24.2 | 150.2 | 202.7 | 12.6 | 14.5 | 92.9 | 12.8 | 13.3 | 17.3 | 20.6 | 119.4 | 138.3 | 22.8 | 56.2 | 16.8 | 80.3 | 72.5 | 16.7 | 21.2 | 14.1 | 13.7
303 | 64 | 293.8 | 117.52 | 137.3741 | 76.9 | 91.9 | 88.9 | 76.1 | 141.4 | 12.6 | 21.6 | 17.9 | 2.3 | 194.2 | 10.9 | 58.7 | 245.8 | 661.1 | 18.6 | 53 | 404.5 | 24.6 | 153.2 | 207.5 | 12.6 | 14.6 | 95.8 | 12.8 | 13.3 | 17.4 | 20.8 | 120.6 | 140.3 | 23 | 57.1 | 16.8 | 81 | 73.4 | 16.8 | 21.4 | 14.2 | 13.8
304 | 65 | 293.2 | 117.28 | 137.0936 | 77.9 | 92.9 | 90.1 | 76.8 | 143 | 12.6 | 21.6 | 18.2 | 2.6 | 187.8 | 9.6 | 58.6 | 246.2 | 673.5 | 18.9 | 54 | 408.8 | 25 | 155.4 | 210.7 | 12.7 | 14.6 | 100 | 12.8 | 13.4 | 17.6 | 20.9 | 123 | 142.3 | 23.1 | 58.9 | 16.9 | 81.9 | 74.3 | 16.9 | 21.7 | 14.3 | 13.9
305 | 66 | 292.5 | 117 | 136.7663 | 78.6 | 93.7 | 90.8 | 77.4 | 143.7 | 12.6 | 21.6 | 18.4 | 3.1 | 189.6 | 9.5 | 58.4 | 248.3 | 691.1 | 19.2 | 55.1 | 414 | 25.4 | 159.2 | 218.6 | 12.7 | 14.7 | 102.8 | 12.8 | 13.4 | 17.7 | 21.1 | 124.5 | 144.2 | 23.4 | 60.2 | 17 | 82.6 | 75.3 | 17 | 22 | 14.4 | 14
306 | 67 | 294.8 | 117.92 | 137.8417 | 79.3 | 94 | 91.3 | 78.1 | 145.8 | 12.6 | 21.6 | 18.6 | 4 | 208.4 | 9.4 | 58.3 | 250.3 | 691.6 | 19.5 | 56.3 | 421.2 | 25.8 | 163.8 | 223.2 | 12.7 | 14.8 | 103.9 | 12.8 | 13.4 | 17.7 | 21.2 | 126.6 | 146.8 | 24.2 | 62.3 | 17.1 | 83.8 | 75.9 | 17.1 | 22.4 | 14.6 | 14.1
307 | 68 | 292.7 | 117.08 | 136.8598 | 79.7 | 95.4 | 91.7 | 78.9 | 148.1 | 12.7 | 21.6 | 18.8 | 6.9 | 196.1 | 15.1 | 58.2 | 251.2 | 689.9 | 19.8 | 57.7 | 427.8 | 26.2 | 167 | 224.3 | 12.8 | 14.8 | 105.4 | 12.8 | 13.4 | 17.8 | 21.4 | 128.9 | 149.6 | 24.9 | 63.8 | 17.1 | 85 | 76.4 | 17.1 | 22.4 | 14.7 | 14.2
308 | 69 | 294.2 | 117.68 | 137.5611 | 80.3 | 96.7 | 92.1 | 79.4 | 150.2 | 12.6 | 21.6 | 19 | 6.7 | 201.6 | 17.2 | 58.1 | 250.8 | 689.2 | 20.1 | 59.2 | 433.7 | 26.7 | 166.4 | 221.7 | 12.8 | 14.9 | 105.1 | 12.8 | 13.5 | 17.9 | 21.5 | 130.6 | 151 | 24.6 | 64.3 | 17.2 | 86.1 | 77 | 17.2 | 22.6 | 14.8 | 14.3
309 | 70 | 295.2 | 118.08 | 138.0287 | 81 | 97.5 | 92.8 | 79.9 | 149.4 | 12.6 | 21.6 | 19.2 | 5.8 | 204.9 | 19.9 | 58 | 247.2 | 681.5 | 20.5 | 60.8 | 437.4 | 27.1 | 165.7 | 219.6 | 12.8 | 15 | 105.9 | 12.8 | 13.5 | 18 | 21.7 | 130.9 | 150 | 24 | 63.6 | 17.3 | 86.9 | 77.4 | 17.2 | 23 | 15 | 14.4
310 | 71 | 295.1 | 118.04 | 137.982 | 81.9 | 98.2 | 93.6 | 80.4 | 148.3 | 12.6 | 21.6 | 19.4 | 5.3 | 222.7 | 22.5 | 57.9 | 245.2 | 678.8 | 20.8 | 62.4 | 442.1 | 27.5 | 166.5 | 220.3 | 12.9 | 15.1 | 107.9 | 12.8 | 13.5 | 18.1 | 21.9 | 131 | 149 | 23.5 | 63.3 | 17.4 | 87.5 | 78.1 | 17.4 | 23.4 | 15.1 | 14.5
311 | 72 | 294.6 | 117.84 | 137.7482 | 83.1 | 99 | 94.2 | 80.9 | 148.3 | 12.6 | 21.6 | 19.5 | 5.8 | 228.5 | 23.7 | 57.8 | 245.2 | 684.6 | 21.1 | 64.1 | 447 | 28 | 169.4 | 224.4 | 12.9 | 15.2 | 109.8 | 12.8 | 13.5 | 18.2 | 22.1 | 131.9 | 150.7 | 23.9 | 64.3 | 17.5 | 88.4 | 78.7 | 17.5 | 23.7 | 15.2 | 14.6
312 | 73 | 295.4 | 118.16 | 138.1222 | 84 | 99.9 | 94.6 | 81.4 | 150.3 | 12.6 | 21.6 | 19.7 | 5.1 | 221.6 | 20.6 | 57.7 | 247.1 | 680.4 | 21.5 | 66 | 453.2 | 28.5 | 172.8 | 229.3 | 13 | 15.3 | 112.2 | 12.8 | 13.5 | 18.2 | 22.2 | 133.4 | 152.1 | 24.4 | 65.8 | 17.5 | 89.4 | 79.5 | 17.6 | 23.9 | 15.3 | 14.7
313 | 74 | 294.7 | 117.88 | 137.7949 | 84.8 | 100.8 | 95.2 | 82 | 151.6 | 12.6 | 21.6 | 19.8 | 5.1 | 207 | 18.4 | 57.6 | 246.3 | 692.1 | 21.8 | 68 | 457.7 | 28.9 | 174.9 | 230.3 | 13 | 15.4 | 114.3 | 12.9 | 13.6 | 18.4 | 22.4 | 134.8 | 153.6 | 25.1 | 66.8 | 17.6 | 90.2 | 80.8 | 17.7 | 24.2 | 15.4 | 14.8
314 | 75 | 294.3 | 117.72 | 137.6079 | 85.4 | 101.2 | 95.7 | 82.7 | 153.1 | 12.7 | 21.6 | 19.9 | 3.8 | 247.4 | 13 | 57.5 | 242.8 | 692.9 | 22.2 | 70 | 461.4 | 29.4 | 175.6 | 231.9 | 13 | 15.5 | 115.1 | 12.9 | 13.6 | 18.5 | 22.6 | 136.3 | 154.7 | 25.1 | 67.3 | 17.7 | 91.2 | 81.5 | 17.8 | 24.5 | 15.6 | 14.9
315 | 76 | 294.3 | 117.72 | 137.6079 | 86.1 | 101.2 | 96.2 | 83.3 | 154.1 | 12.7 | 21.6 | 20.1 | 3.7 | 238.3 | 10.9 | 57.4 | 241.8 | 700.9 | 22.5 | 72 | 465.2 | 29.9 | 176.1 | 230.3 | 13.1 | 15.5 | 116.5 | 12.9 | 13.6 | 18.6 | 22.8 | 137.6 | 155 | 25.2 | 67 | 17.8 | 91.9 | 82.3 | 17.9 | 24.7 | 15.7 | 15
316 | 77 | 294 | 117.6 | 137.4676 | 87 | 101.7 | 96.7 | 83.9 | 155.5 | 12.7 | 21.6 | 20.2 | 4.7 | 244.4 | 10.8 | 57.3 | 241.2 | 689.3 | 22.9 | 74.1 | 469 | 30.3 | 176.9 | 229.5 | 13.1 | 15.6 | 117.3 | 12.9 | 13.7 | 18.6 | 22.9 | 139.3 | 157.6 | 25.6 | 67.5 | 17.8 | 92.4 | 83.3 | 18 | 25 | 15.8 | 15.1
317 | 78 | 294.2 | 117.68 | 137.5611 | 87.9 | 102.6 | 97.2 | 84.6 | 157 | 12.7 | 21.6 | 20.3 | 5.2 | 239.8 | 13.4 | 57.2 | 242 | 671.1 | 23.2 | 76.1 | 474.1 | 30.8 | 176.8 | 229.5 | 13.2 | 15.7 | 117.4 | 12.9 | 13.7 | 18.8 | 23.1 | 140 | 157.7 | 25.4 | 67.6 | 17.9 | 93.2 | 83.8 | 18.3 | 25.3 | 15.9 | 15.2
318 | 79 | 294.3 | 117.72 | 137.6079 | 88.1 | 102.8 | 97.8 | 85.2 | 156.8 | 12.8 | 21.6 | 20.5 | 3.7 | 248.6 | 12.9 | 57.2 | 241.6 | 669.2 | 23.6 | 78.1 | 479.5 | 31.3 | 178.1 | 232.1 | 13.2 | 15.8 | 119 | 12.9 | 13.7 | 18.8 | 23.3 | 140.7 | 157.9 | 25.4 | 67.7 | 18 | 94 | 84.2 | 18.5 | 25.5 | 16.1 | 15.3
319 | 80 | 294.2 | 117.68 | 137.5611 | 89.1 | 102.7 | 98.4 | 85.7 | 156.6 | 12.8 | 21.6 | 20.6 | 5 | 234.8 | 14.1 | 57.1 | 240.9 | 666.8 | 24 | 80 | 486.3 | 31.8 | 178.6 | 233.6 | 13.2 | 15.9 | 120.4 | 12.9 | 13.8 | 18.9 | 23.5 | 141.4 | 158.3 | 25.4 | 69 | 18.1 | 95.9 | 84.6 | 18.6 | 25.7 | 16.2 | 15.4
320 | 81 | 295.3 | 118.12 | 138.0755 | 90.5 | 103.3 | 99 | 86.1 | 156.9 | 12.8 | 21.6 | 20.8 | 5.4 | 238.5 | 13.9 | 57.1 | 238.5 | 654.8 | 24.4 | 81.8 | 491.5 | 32.3 | 177.7 | 231 | 13.3 | 16 | 121.3 | 12.9 | 13.8 | 19 | 23.7 | 142 | 157.7 | 25.1 | 69 | 18.2 | 96.4 | 85.5 | 18.7 | 26 | 16.3 | 15.6
321 | 82 | 295.5 | 118.2 | 138.169 | 91 | 103.6 | 99.5 | 86.6 | 156 | 12.8 | 21.6 | 20.9 | 5.6 | 242.3 | 13.3 | 57.1 | 235.8 | 636.2 | 24.7 | 83.6 | 495.8 | 32.8 | 175.3 | 226.4 | 13.3 | 16.1 | 121.3 | 12.9 | 13.8 | 19 | 23.9 | 142.1 | 156.7 | 24.9 | 68.6 | 18.2 | 97 | 86.7 | 18.8 | 26.3 | 16.4 | 15.7
322 | 83 | 296 | 118.4 | 138.4028 | 91.5 | 103.9 | 100.1 | 87 | 154.9 | 12.9 | 21.6 | 21.1 | 5.8 | 240.7 | 11.7 | 57 | 232.8 | 631.4 | 25.1 | 85.4 | 499.7 | 33.3 | 173.9 | 224 | 13.4 | 16.2 | 121.6 | 12.9 | 13.9 | 19.1 | 24.1 | 142.4 | 156.2 | 24.9 | 68.5 | 18.3 | 97.6 | 87.2 | 19 | 26.6 | 16.5 | 15.8
323 | 84 | 295.9 | 118.36 | 138.356 | 92.3 | 104.4 | 100.8 | 87.4 | 154.2 | 12.9 | 21.6 | 21.2 | 6.1 | 230 | 11.4 | 57 | 231.8 | 638.8 | 25.5 | 87.1 | 503.3 | 33.8 | 172.6 | 221.6 | 13.4 | 16.3 | 122.3 | 12.9 | 13.9 | 19.3 | 24.3 | 142.4 | 155.4 | 25 | 68.6 | 18.4 | 98.1 | 87.4 | 19 | 26.9 | 16.6 | 15.9
324 | 85 | 295.4 | 118.16 | 138.1222 | 92.9 | 104.7 | 101.4 | 87.9 | 153.6 | 12.9 | 21.5 | 21.3 | 5.4 | 227.7 | 13.2 | 57 | 230.4 | 646.9 | 25.9 | 88.7 | 507.2 | 34.3 | 173.4 | 225.9 | 13.5 | 16.4 | 123.7 | 12.9 | 13.9 | 19.4 | 24.5 | 142.2 | 154.9 | 24.9 | 68.6 | 18.4 | 98.6 | 87.9 | 19.1 | 27.1 | 16.7 | 16
325 | 86 | 292 | 116.8 | 136.5325 | 93.3 | 105 | 102 | 88.3 | 153.1 | 13 | 21.5 | 21.4 | 4.1 | 228.2 | 14.1 | 57 | 230.8 | 640.9 | 26.3 | 90.3 | 510.1 | 34.8 | 173.8 | 225.5 | 13.5 | 16.5 | 124.5 | 12.9 | 14 | 19.6 | 24.6 | 142.3 | 154.4 | 24.7 | 69.2 | 18.5 | 98.7 | 88.5 | 19.1 | 27.5 | 16.8 | 16.1
326 | 87 | 294.1 | 117.64 | 137.5144 | 93.4 | 105.2 | 102.4 | 88.7 | 151.9 | 13 | 21.5 | 21.5 | 4 | 218.4 | 16.4 | 57 | 231 | 636.8 | 26.7 | 91.9 | 513.6 | 35.2 | 176.6 | 226.9 | 13.6 | 16.6 | 128 | 12.9 | 14 | 19.6 | 24.8 | 142.5 | 154 | 24.5 | 70.2 | 18.6 | 99 | 89.1 | 19.1 | 27.7 | 16.9 | 16.2
327 | 88 | 294.1 | 117.64 | 137.5144 | 93.7 | 105.9 | 102.8 | 88.9 | 151.5 | 13.1 | 21.5 | 21.7 | 3.4 | 238.4 | 14.5 | 57 | 230.6 | 633.4 | 27.1 | 93.5 | 517.5 | 35.7 | 181.4 | 233.1 | 13.6 | 16.7 | 131.6 | 12.9 | 14 | 19.6 | 25 | 143.1 | 155.5 | 24.6 | 72.7 | 18.7 | 99.5 | 90.1 | 19.2 | 28 | 17.1 | 16.3
328 | 89 | 295.3 | 118.12 | 138.0755 | 94.1 | 106.7 | 103.1 | 89.3 | 152.6 | 13.1 | 21.5 | 21.7 | 3.4 | 233.9 | 11.4 | 57.1 | 229.8 | 631 | 27.5 | 95.2 | 521.1 | 36.2 | 185.3 | 238.8 | 13.7 | 16.8 | 134.6 | 12.9 | 14.1 | 19.8 | 25.1 | 144.5 | 157.1 | 25.1 | 74.3 | 18.7 | 100 | 90.6 | 19.4 | 28.1 | 17.2 | 16.4
329 | 90 | 294.9 | 117.96 | 137.8884 | 94.6 | 107.9 | 103.2 | 89.8 | 153.4 | 13.1 | 21.5 | 21.8 | 3.3 | 218.8 | 12.8 | 57.1 | 228.7 | 634.1 | 27.9 | 96.8 | 525.2 | 36.7 | 188.1 | 240.3 | 13.7 | 16.9 | 136.8 | 12.9 | 14.1 | 19.8 | 25.3 | 145.8 | 158.7 | 25.9 | 75.2 | 18.8 | 100.5 | 91 | 19.5 | 28.4 | 17.3 | 16.5
330 | 91 | 292.4 | 116.96 | 136.7195 | 95.1 | 108.3 | 103.3 | 90.2 | 154.2 | 13.1 | 21.5 | 21.9 | 4.7 | 228.5 | 11.6 | 57.2 | 229.9 | 639.4 | 28.3 | 98.4 | 527.9 | 37.2 | 188.1 | 241.3 | 13.8 | 17 | 136.6 | 12.9 | 14.2 | 19.9 | 25.4 | 146.5 | 159.6 | 26.1 | 75.5 | 18.9 | 101.2 | 91.1 | 19.5 | 28.8 | 17.5 | 16.6
331 | 92 | 292.5 | 117 | 136.7663 | 95.8 | 108.3 | 103.4 | 90.6 | 154.5 | 13.2 | 21.5 | 22 | 3.9 | 227.3 | 10.9 | 57.3 | 228.1 | 632 | 28.7 | 99.9 | 531.2 | 37.7 | 187.8 | 240.7 | 13.8 | 17.1 | 137 | 12.9 | 14.2 | 20 | 25.6 | 146.8 | 160.1 | 25.9 | 75.4 | 19 | 101.8 | 91.8 | 19.6 | 29.1 | 17.6 | 16.7
332 | 93 | 294 | 117.6 | 137.4676 | 96.1 | 108.6 | 103.6 | 90.9 | 154.7 | 13.1 | 21.5 | 22.1 | 2.9 | 240.9 | 10.7 | 57.4 | 224.6 | 626.4 | 29.1 | 101.4 | 533.6 | 38.2 | 186.5 | 238.2 | 13.9 | 17.2 | 136.8 | 13 | 14.2 | 20.1 | 25.8 | 147.1 | 162.1 | 26.2 | 75.9 | 19.1 | 102.2 | 92.4 | 19.8 | 29.3 | 17.7 | 16.9
333 | 94 | 295.2 | 118.08 | 138.0287 | 96.6 | 108.7 | 104.1 | 91.1 | 154 | 13.1 | 21.5 | 22.3 | 2.6 | 247.4 | 9.6 | 57.4 | 222 | 634.7 | 29.5 | 102.8 | 537.1 | 38.7 | 187.1 | 239.3 | 13.9 | 17.3 | 138 | 13 | 14.3 | 20.2 | 26 | 147.1 | 161.5 | 26 | 76.2 | 19.2 | 102.7 | 92.8 | 19.9 | 29.5 | 17.8 | 17
334 | 95 | 294.2 | 117.68 | 137.5611 | 96.9 | 108.8 | 104.6 | 91.2 | 155.2 | 13.2 | 21.5 | 22.4 | 2.3 | 224.3 | 9.5 | 57.5 | 220.1 | 631.2 | 29.9 | 104 | 540.3 | 39.2 | 186.3 | 237.4 | 14 | 17.4 | 138.5 | 13 | 14.3 | 20.3 | 26.1 | 148.2 | 162.6 | 26.5 | 76.8 | 19.3 | 103.2 | 93.5 | 20 | 29.8 | 17.9 | 17.1
335 | 96 | 293.4 | 117.36 | 137.1871 | 97.5 | 109 | 105 | 91.4 | 156.3 | 13.2 | 21.5 | 22.5 | 3.2 | 219.5 | 10.9 | 57.6 | 220.8 | 635.7 | 30.3 | 105.2 | 542.4 | 39.7 | 186.4 | 238 | 14.1 | 17.5 | 139 | 13 | 14.3 | 20.3 | 26.3 | 148.5 | 162.2 | 26.4 | 76.9 | 19.3 | 103.5 | 94 | 20.1 | 30 | 18 | 17.2
336 | 97 | 294.2 | 117.68 | 137.5611 | 98.4 | 109 | 105.5 | 91.9 | 157.2 | 13.2 | 21.5 | 22.6 | 3.7 | 237.7 | 9.7 | 57.8 | 220.6 | 644.7 | 30.7 | 106.3 | 544.6 | 40.2 | 185.6 | 237.4 | 14.1 | 17.6 | 139.1 | 13 | 14.4 | 20.5 | 26.5 | 148.4 | 162.3 | 26.1 | 77 | 19.4 | 104.1 | 95 | 20.1 | 30.2 | 18.2 | 17.3
337 | 98 | 295.2 | 118.08 | 138.0287 | 98.5 | 108.9 | 105.9 | 92.4 | 156.9 | 13.3 | 21.5 | 22.7 | 3.3 | 223.3 | 8.5 | 57.9 | 221.4 | 646.4 | 31.1 | 107.4 | 547.5 | 40.8 | 184.8 | 236.3 | 14.2 | 17.7 | 139.5 | 13 | 14.4 | 20.6 | 26.7 | 148.1 | 162.4 | 26 | 76.9 | 19.5 | 104.6 | 95.6 | 20.2 | 30.5 | 18.3 | 17.4
338 | 99 | 293.5 | 117.4 | 137.2338 | 98.6 | 109 | 106.2 | 92.8 | 157.6 | 13.3 | 21.5 | 22.8 | 3.5 | 229.6 | 10.8 | 58 | 222.2 | 646.1 | 31.6 | 108.4 | 549.4 | 41.3 | 183.9 | 235.4 | 14.2 | 17.8 | 140 | 13 | 14.5 | 20.6 | 26.9 | 148.4 | 162.4 | 26.4 | 77.1 | 19.6 | 105.1 | 96 | 20.5 | 30.8 | 18.4 | 17.5
339 | 100 | 295.1 | 118.04 | 137.982 | 98.4 | 109.3 | 106.6 | 93.1 | 157.7 | 13.4 | 21.5 | 22.9 | 3.3 | 250.3 | 10 | 58.2 | 221.6 | 646.7 | 32 | 109.3 | 550.7 | 41.8 | 183.6 | 238 | 14.3 | 17.9 | 140.4 | 13 | 14.5 | 20.8 | 27.1 | 148.2 | 161.4 | 26.1 | 76.8 | 19.7 | 105.6 | 96.2 | 20.6 | 31.1 | 18.5 | 17.6
340 | 101 | 294.9 | 117.96 | 137.8884 | 98.4 | 109.4 | 107 | 93.3 | 158 | 13.4 | 21.5 | 23 | 3.6 | 220.7 | 10.6 | 58.3 | 221.5 | 643.2 | 32.4 | 110.3 | 553.7 | 42.3 | 184 | 237.9 | 14.4 | 18 | 141.2 | 13 | 14.6 | 20.9 | 27.3 | 148.1 | 161.7 | 25.9 | 77.4 | 19.7 | 106 | 96.4 | 20.8 | 31.4 | 18.6 | 17.7
341 | 102 | 294 | 117.6 | 137.4676 | 98.5 | 109.4 | 107.6 | 93.2 | 158.7 | 13.4 | 21.5 | 23.1 | 3.7 | 216 | 11.9 | 58.5 | 221.4 | 644.7 | 32.8 | 111.2 | 557.6 | 42.8 | 185.2 | 238.7 | 14.4 | 18 | 142.2 | 13 | 14.6 | 20.9 | 27.4 | 148.3 | 161.6 | 26.2 | 77.9 | 19.8 | 106.2 | 96.7 | 20.9 | 31.7 | 18.7 | 17.9
342 | 103 | 293.5 | 117.4 | 137.2338 | 98.6 | 109.4 | 108.2 | 93.2 | 159.8 | 13.4 | 21.5 | 23.2 | 3.2 | 221.5 | 12.7 | 58.6 | 222 | 651.5 | 33.3 | 112.1 | 561.9 | 43.3 | 185.5 | 237.8 | 14.5 | 18.1 | 143 | 13 | 14.7 | 21.1 | 27.6 | 148.8 | 162.7 | 26.4 | 78.8 | 19.9 | 106.6 | 96.8 | 20.9 | 32 | 18.8 | 18
343 | 104 | 294.1 | 117.64 | 137.5144 | 98.9 | 109.4 | 108.6 | 93.3 | 160.3 | 13.4 | 21.5 | 23.2 | 3.4 | 229.3 | 11.3 | 58.8 | 223 | 653 | 33.7 | 112.9 | 564.6 | 43.8 | 186.6 | 239.8 | 14.5 | 18.2 | 143.9 | 13 | 14.7 | 21.1 | 27.8 | 148.9 | 163.4 | 26.7 | 79.6 | 19.9 | 107.1 | 97 | 20.9 | 32.2 | 18.9 | 18.1
344 | 105 | 294.3 | 117.72 | 137.6079 | 99.2 | 109.5 | 109.1 | 93.3 | 160.9 | 13.4 | 21.5 | 23.3 | 3.5 | 217.3 | 12.7 | 58.9 | 223.1 | 652 | 34.2 | 113.9 | 567.7 | 44.3 | 188.6 | 242 | 14.6 | 18.3 | 145.2 | 13 | 14.8 | 21.3 | 28 | 149.1 | 163.6 | 26.8 | 80.5 | 20 | 107.4 | 97.2 | 20.9 | 32.5 | 19 | 18.2
345 | 106 | 296 | 118.4 | 138.4028 | 99.5 | 109.5 | 109.7 | 93.5 | 160.9 | 13.4 | 21.5 | 23.4 | 3.5 | 227.2 | 13.7 | 59.1 | 222.7 | 659.1 | 34.6 | 114.8 | 570.8 | 44.8 | 189.4 | 242.1 | 14.7 | 18.4 | 146.1 | 13 | 14.8 | 21.5 | 28.1 | 149.6 | 163.8 | 26.7 | 81.2 | 20.1 | 107.9 | 97.6 | 21.1 | 32.8 | 19.1 | 18.3
346 | 107 | 296.8 | 118.72 | 138.7768 | 99.9 | 109.8 | 109.9 | 93.8 | 162 | 13.4 | 21.5 | 23.5 | 3 | 217.9 | 12.8 | 59.3 | 223 | 659.2 | 35 | 115.7 | 572.2 | 45.3 | 189.4 | 240.9 | 14.7 | 18.5 | 146.8 | 13.1 | 14.8 | 21.5 | 28.3 | 150.2 | 164.7 | 26.9 | 82 | 20.1 | 108.2 | 98 | 21.1 | 33.2 | 19.3 | 18.4
347 | 108 | 295.5 | 118.2 | 138.169 | 100.2 | 110.5 | 110.2 | 94 | 164.4 | 13.4 | 21.5 | 23.6 | 2.7 | 212.9 | 15.4 | 59.4 | 223.9 | 654.6 | 35.5 | 116.7 | 573.4 | 45.8 | 189.4 | 239.9 | 14.8 | 18.6 | 146.9 | 13.1 | 14.9 | 21.6 | 28.5 | 151.1 | 170.1 | 27.4 | 83.3 | 20.2 | 108.7 | 98 | 21.2 | 33.5 | 19.4 | 18.5
348 | 109 | 295.8 | 118.32 | 138.3093 | 100.1 | 110.5 | 110.5 | 94.2 | 165.9 | 13.4 | 21.5 | 23.7 | 2.9 | 217.6 | 16.4 | 59.6 | 223.7 | 656.5 | 35.9 | 117.6 | 575.1 | 46.3 | 188.7 | 238.6 | 14.8 | 18.7 | 147.2 | 13.1 | 14.9 | 21.7 | 28.7 | 151.3 | 168.9 | 27.1 | 83.5 | 20.3 | 109.1 | 98.8 | 21.3 | 33.6 | 19.5 | 18.6
349 | 110 | 295.7 | 118.28 | 138.2625 | 100.1 | 110.5 | 110.9 | 94.3 | 166.4 | 13.4 | 21.5 | 23.8 | 2.8 | 214.1 | 14.5 | 59.7 | 222.9 | 649.9 | 36.4 | 118.5 | 576.6 | 46.8 | 190.5 | 244.9 | 14.9 | 18.8 | 148.2 | 13.1 | 15 | 21.8 | 28.9 | 151.9 | 168.8 | 27.3 | 83.5 | 20.3 | 109.5 | 99.4 | 21.4 | 33.8 | 19.6 | 18.7
350 | 111 | 295.6 | 118.24 | 138.2157 | 100.4 | 110.6 | 111.3 | 94.5 | 165.9 | 13.4 | 21.5 | 23.9 | 2.7 | 183.8 | 11 | 59.9 | 222.3 | 650 | 36.9 | 119.3 | 578.9 | 47.3 | 190 | 242.2 | 15 | 18.9 | 148.6 | 13.1 | 15 | 21.8 | 29.1 | 151.9 | 168.4 | 27 | 83.7 | 20.4 | 109.7 | 100.1 | 21.6 | 34 | 19.8 | 18.8
351 | 112 | 296 | 118.4 | 138.4028 | 100.9 | 111.1 | 111.5 | 94.5 | 164.8 | 13.4 | 21.5 | 24 | 2.7 | 225.7 | 10.6 | 60 | 222.5 | 654.4 | 37.4 | 120 | 582 | 47.8 | 189.9 | 243.5 | 15 | 18.9 | 149.6 | 13.1 | 15.1 | 21.9 | 29.3 | 152.1 | 167.6 | 26.7 | 84.1 | 20.5 | 109.8 | 100.8 | 21.6 | 34.2 | 19.9 | 18.9
352 | 113 | 295.6 | 118.24 | 138.2157 | 101.7 | 111.5 | 111.5 | 94.7 | 164.9 | 13.4 | 21.5 | 24 | 3.1 | 208.6 | 13.5 | 60.1 | 221.5 | 656.6 | 37.8 | 120.7 | 585.3 | 48.3 | 189.9 | 243 | 15.1 | 19 | 151 | 13.1 | 15.1 | 22 | 29.5 | 152.8 | 167.9 | 27.3 | 84.9 | 20.6 | 110.2 | 101 | 21.8 | 34.4 | 20 | 19
353 | 114 | 295.6 | 118.24 | 138.2157 | 102.1 | 112.3 | 111.4 | 95 | 166.2 | 13.4 | 21.5 | 24.1 | 2.6 | 201.3 | 14 | 60.2 | 220.1 | 658.9 | 38.3 | 121.3 | 588.3 | 48.7 | 189.4 | 242.8 | 15.1 | 19.1 | 151.9 | 13.1 | 15.2 | 22.2 | 29.7 | 154 | 168.4 | 28 | 85.6 | 20.6 | 110.7 | 101.1 | 21.9 | 34.4 | 20.1 | 19.1
354 | 115 | 295.7 | 118.28 | 138.2625 | 102.1 | 112.7 | 111.4 | 95.4 | 166.9 | 13.4 | 21.5 | 24.2 | 2.4 | 207.6 | 14.1 | 60.4 | 220.3 | 671.6 | 38.8 | 121.9 | 590.8 | 49.2 | 189.5 | 243.3 | 15.2 | 19.2 | 153.2 | 13.1 | 15.2 | 22.3 | 29.8 | 155.1 | 169.3 | 28.2 | 86.5 | 20.7 | 111.1 | 101.2 | 21.9 | 34.6 | 20.3 | 19.2
355 | 116 | 295.7 | 118.28 | 138.2625 | 101.8 | 112.8 | 111.6 | 95.9 | 169.4 | 13.4 | 21.5 | 24.3 | 2.9 | 209.9 | 13.8 | 60.5 | 219.3 | 667.1 | 39.3 | 122.5 | 593.3 | 49.7 | 188.7 | 241.6 | 15.3 | 19.3 | 153.6 | 13.1 | 15.3 | 22.4 | 30 | 155.1 | 170.2 | 28.5 | 87.1 | 20.8 | 111.5 | 101.4 | 21.9 | 34.9 | 20.4 | 19.3
356 | 117 | 295.8 | 118.32 | 138.3093 | 101.6 | 113.4 | 111.9 | 96 | 169 | 13.4 | 21.5 | 24.4 | 3.3 | 212 | 13.5 | 60.6 | 219 | 668.8 | 39.8 | 123 | 598.1 | 50.2 | 188 | 241.5 | 15.3 | 19.4 | 154.5 | 13.1 | 15.3 | 22.4 | 30.2 | 154.8 | 169.2 | 28.1 | 87 | 20.9 | 111.7 | 101.7 | 22 | 35 | 20.5 | 19.4
357 | 118 | 295.2 | 118.08 | 138.0287 | 101.8 | 113.8 | 112.1 | 96.1 | 167.7 | 13.4 | 21.5 | 24.5 | 3.4 | 213.8 | 13.2 | 60.7 | 219.3 | 679.4 | 40.3 | 123.6 | 601.4 | 50.6 | 188 | 242.1 | 15.4 | 19.5 | 155.2 | 13.1 | 15.4 | 22.5 | 30.4 | 154.8 | 168.9 | 28 | 86.9 | 20.9 | 111.8 | 102.3 | 22.2 | 35.2 | 20.6 | 19.6
358 | 119 | 294.8 | 117.92 | 137.8417 | 101.7 | 114.5 | 112.4 | 96.3 | 169.2 | 13.4 | 21.5 | 24.6 | 3.3 | 212.4 | 12.5 | 60.8 | 220.7 | 696.7 | 40.8 | 124.1 | 606.5 | 51.1 | 189.1 | 243 | 15.5 | 19.6 | 155.4 | 13.2 | 15.4 | 22.6 | 30.6 | 155.6 | 170.8 | 28.7 | 87.8 | 21 | 112.3 | 102.6 | 22.3 | 35.5 | 20.8 | 19.7
359 | 120 | 294.9 | 117.96 | 137.8884 | 101.7 | 115.4 | 112.7 | 96.4 | 171.7 | 13.4 | 21.5 | 24.6 | 3.2 | 201.2 | 11.4 | 61 | 223.7 | 710.2 | 41.3 | 124.6 | 610.2 | 51.6 | 190.9 | 246 | 15.5 | 19.7 | 156.1 | 13.2 | 15.5 | 22.6 | 30.8 | 156.3 | 172.2 | 28.8 | 88.5 | 21.1 | 112.9 | 102.7 | 22.4 | 35.8 | 20.9 | 19.8
360 | 121 | 296.6 | 118.64 | 138.6833 | 101.8 | 115.6 | 113.1 | 96.7 | 174.5 | 13.4 | 21.5 | 24.7 | 3.1 | 203.7 | 9.9 | 61.1 | 225.8 | 717.5 | 41.9 | 125 | 612.2 | 52.1 | 190.5 | 247.3 | 15.6 | 19.7 | 156.6 | 13.2 | 15.5 | 22.9 | 31 | 157 | 172.9 | 29.2 | 88.9 | 21.1 | 113.2 | 102.7 | 22.4 | 35.8 | 21 | 19.9
361 | 122 | 296.1 | 118.44 | 138.4495 | 102.2 | 115.6 | 113.8 | 97 | 176 | 13.5 | 21.5 | 24.8 | 3 | 209.4 | 8.7 | 61.2 | 226.6 | 706.3 | 42.4 | 125.5 | 612.9 | 52.6 | 189.8 | 248.3 | 15.7 | 19.8 | 157.2 | 13.2 | 15.6 | 23 | 31.2 | 157.7 | 173.4 | 29.6 | 90 | 21.2 | 113.5 | 102.8 | 22.6 | 35.9 | 21.1 | 20
362 | 123 | 296 | 118.4 | 138.4028 | 102.3 | 115.6 | 114.4 | 97.2 | 174.4 | 13.5 | 21.5 | 24.9 | 3.4 | 211 | 8.7 | 61.4 | 226 | 703.5 | 42.9 | 125.9 | 615.1 | 53 | 189.6 | 247.2 | 15.7 | 19.9 | 157.3 | 13.2 | 15.6 | 23.1 | 31.4 | 157.6 | 173.2 | 29.7 | 89.5 | 21.3 | 113.7 | 102.8 | 22.8 | 36.1 | 21.3 | 20.1
363 | 124 | 296.1 | 118.44 | 138.4495 | 102.3 | 115.9 | 114.7 | 97.4 | 173.3 | 13.5 | 21.5 | 24.9 | 3.7 | 215.7 | 9 | 61.6 | 226.9 | 696.5 | 43.5 | 126.3 | 617.3 | 53.5 | 188.2 | 245.3 | 15.8 | 20 | 157.4 | 13.2 | 15.7 | 23.3 | 31.7 | 157.6 | 172.9 | 29.5 | 89.5 | 21.3 | 113.8 | 103.2 | 22.9 | 36.5 | 21.4 | 20.2
364 | 125 | 296.2 | 118.48 | 138.4963 | 102.5 | 116 | 115 | 97.7 | 171.6 | 13.6 | 21.5 | 25 | 3.2 | 214.5 | 8.8 | 61.8 | 226.1 | 677.1 | 44 | 126.7 | 620.2 | 54 | 187.8 | 242.6 | 15.9 | 20.1 | 158.1 | 13.2 | 15.7 | 23.3 | 31.9 | 157.5 | 172.2 | 29.3 | 89.6 | 21.4 | 114 | 103.2 | 23.1 | 36.7 | 21.5 | 20.3
365 | 126 | 296.3 | 118.52 | 138.5431 | 102.7 | 116.9 | 115.4 | 98 | 170.5 | 13.6 | 21.5 | 25 | 3.3 | 211.5 | 9.1 | 62 | 225.3 | 667.5 | 44.6 | 127.1 | 623.2 | 54.4 | 187.7 | 242 | 15.9 | 20.2 | 158.6 | 13.2 | 15.8 | 23.3 | 32.1 | 157.4 | 171.2 | 29.1 | 89.5 | 21.4 | 114.2 | 103.2 | 23.2 | 36.9 | 21.6 | 20.5
366 | 127 | 295.7 | 118.28 | 138.2625 | 102.9 | 117.7 | 115.9 | 98.2 | 169.9 | 13.7 | 21.4 | 25.1 | 3.8 | 211.3 | 9.6 | 62.2 | 224.8 | 671.8 | 45.1 | 127.6 | 624.3 | 54.9 | 186.7 | 239.4 | 16 | 20.3 | 159 | 13.2 | 15.9 | 23.5 | 32.3 | 157.6 | 170.6 | 29 | 89.9 | 21.5 | 114.5 | 103.6 | 23.2 | 37 | 21.7 | 20.5
367 | 128 | 294 | 117.6 | 137.4676 | 103.2 | 118.2 | 116.2 | 98.4 | 169.2 | 13.8 | 21.5 | 25.2 | 4.2 | 238.7 | 7.2 | 62.4 | 223.9 | 685.5 | 45.7 | 128 | 623.6 | 55.3 | 185.5 | 238 | 16.1 | 20.3 | 159.2 | 13.2 | 15.9 | 23.8 | 32.5 | 157.2 | 169.8 | 28.8 | 90.3 | 21.6 | 114.4 | 104.1 | 23.3 | 37.1 | 21.8 | 20.7
368 | 129 | 294.9 | 117.96 | 137.8884 | 103.4 | 118.2 | 116.7 | 98.4 | 168.9 | 14 | 21.4 | 25.3 | 3.6 | 200.7 | 6.9 | 62.6 | 225.1 | 694.2 | 46.2 | 128.4 | 623.5 | 55.8 | 185.3 | 240.2 | 16.1 | 20.4 | 159.4 | 13.2 | 16 | 23.9 | 32.7 | 157 | 169.8 | 28.9 | 90.3 | 21.6 | 114.5 | 104.3 | 23.3 | 37.3 | 21.9 | 20.8
369 | 130 | 295.6 | 118.24 | 138.2157 | 103.4 | 118.1 | 117.2 | 98.4 | 169.6 | 14 | 21.4 | 25.4 | 3.4 | 204.2 | 9.1 | 62.8 | 226.8 | 694.4 | 46.8 | 128.8 | 624.4 | 56.3 | 185.3 | 239.5 | 16.2 | 20.5 | 160.2 | 13.2 | 16 | 24 | 32.9 | 157.1 | 171.4 | 29.4 | 90.8 | 21.7 | 114.8 | 104.7 | 23.4 | 37.6 | 22.1 | 20.9
370 | 131 | 295.8 | 118.32 | 138.3093 | 103.4 | 118.4 | 117.6 | 98.6 | 172.9 | 14.1 | 21.4 | 25.5 | 3.2 | 209.5 | 11 | 63.1 | 226.2 | 686.5 | 47.4 | 129.1 | 625.9 | 56.7 | 185 | 238.8 | 16.3 | 20.6 | 160.5 | 13.3 | 16.1 | 24 | 33.1 | 157.7 | 172 | 29.6 | 91.7 | 21.8 | 115 | 105 | 23.4 | 37.8 | 22.2 | 21
371 | 132 | 296 | 118.4 | 138.4028 | 103.5 | 118.4 | 118 | 98.9 | 173 | 14.1 | 21.4 | 25.6 | 1.9 | 211.7 | 10.8 | 63.3 | 225.8 | 689.1 | 47.9 | 129.5 | 626.1 | 57.2 | 184.4 | 238.2 | 16.3 | 20.7 | 160.9 | 13.3 | 16.1 | 24 | 33.3 | 157.2 | 172.1 | 29.2 | 92.1 | 21.8 | 115.3 | 105.2 | 23.5 | 38 | 22.3 | 21.1
372 | 133 | 295 | 118 | 137.9352 | 103.6 | 118.5 | 119 | 99.2 | 172.9 | 14.1 | 21.4 | 25.7 | 2.1 | 205.3 | 10.7 | 63.5 | 224.5 | 688.1 | 48.5 | 129.8 | 625.5 | 57.6 | 184.1 | 236.5 | 16.4 | 20.8 | 161 | 13.3 | 16.2 | 24.1 | 33.5 | 157.2 | 173.8 | 29.3 | 92.8 | 21.9 | 115.5 | 105.4 | 23.6 | 38.2 | 22.4 | 21.2
373 | 134 | 294.8 | 117.92 | 137.8417 | 103.4 | 118.6 | 119.5 | 99.2 | 171.1 | 14.1 | 21.4 | 25.8 | 2.2 | 208.5 | 10.8 | 63.7 | 223.3 | 699 | 49.1 | 130.1 | 625.8 | 58 | 182.4 | 233.9 | 16.5 | 20.8 | 161.1 | 13.3 | 16.3 | 24.3 | 33.7 | 156.2 | 171.7 | 28.9 | 92.6 | 22 | 115.6 | 105.5 | 23.6 | 38.4 | 22.5 | 21.3
374 | 135 | 295.7 | 118.28 | 138.2625 | 103.3 | 118.6 | 119.9 | 99.3 | 168.8 | 14.2 | 21.4 | 25.9 | 3.2 | 228.3 | 10.1 | 63.9 | 224 | 685.1 | 49.7 | 130.4 | 627.2 | 58.5 | 182.4 | 235.3 | 16.5 | 20.9 | 161.8 | 13.3 | 16.3 | 24.4 | 33.9 | 156 | 171.2 | 28.7 | 92.8 | 22 | 115.5 | 106.1 | 23.6 | 38.6 | 22.6 | 21.5
375 | 136 | 296 | 118.4 | 138.4028 | 103.6 | 119.1 | 120 | 99.2 | 168.1 | 14.2 | 21.4 | 26 | 2.9 | 227.4 | 7.7 | 64.1 | 224.4 | 677.3 | 50.3 | 130.7 | 629.9 | 58.9 | 183.2 | 235.5 | 16.6 | 21 | 162.7 | 13.3 | 16.4 | 24.4 | 34.1 | 156.2 | 171 | 28.7 | 93.7 | 22.1 | 115.4 | 106.9 | 23.8 | 38.8 | 22.8 | 21.6
376 | 137 | 296.4 | 118.56 | 138.5898 | 104.1 | 119.2 | 119.7 | 99.2 | 168 | 14.2 | 21.4 | 26.1 | 2.4 | 217.8 | 6 | 64.3 | 223.7 | 679.3 | 50.9 | 130.9 | 632.9 | 59.4 | 185.1 | 238 | 16.7 | 21.1 | 164.4 | 13.3 | 16.4 | 24.6 | 34.3 | 157 | 172 | 29.1 | 94.5 | 22.2 | 115.6 | 107 | 23.9 | 39 | 22.9 | 21.7
377 | 138 | 296 | 118.4 | 138.4028 | 104.5 | 119.6 | 119.7 | 99.3 | 169.6 | 14.3 | 21.4 | 26.2 | 2.3 | 204.3 | 6.8 | 64.5 | 223.4 | 676.6 | 51.5 | 131.2 | 634.2 | 59.8 | 185.6 | 238.3 | 16.8 | 21.2 | 165.2 | 13.3 | 16.5 | 24.6 | 34.5 | 157.7 | 172.4 | 29.3 | 95.5 | 22.3 | 115.6 | 106.7 | 24.1 | 39.3 | 23 | 21.8
378 | 139 | 295.8 | 118.32 | 138.3093 | 104.9 | 119.6 | 119.7 | 99.5 | 170.4 | 14.3 | 21.4 | 26.3 | 2.5 | 187.7 | 9.3 | 64.8 | 223.5 | 684.8 | 52.1 | 131.4 | 636.8 | 60.2 | 186.7 | 240.8 | 16.8 | 21.3 | 165.8 | 13.4 | 16.5 | 24.7 | 34.7 | 158.2 | 172.6 | 29.6 | 95.7 | 22.3 | 115.8 | 106.6 | 24.2 | 39.4 | 23.1 | 21.9
379 | 140 | 295.4 | 118.16 | 138.1222 | 105.6 | 119.5 | 119.8 | 99.8 | 170.5 | 14.3 | 21.4 | 26.5 | 2.4 | 175.4 | 8 | 65 | 223.7 | 678.7 | 52.7 | 131.6 | 637 | 60.7 | 186.2 | 241.5 | 16.9 | 21.3 | 166.1 | 13.4 | 16.6 | 24.8 | 34.8 | 158.2 | 172 | 29.6 | 96 | 22.4 | 116.1 | 107.3 | 24.2 | 39.6 | 23.3 | 22
380 | 141 | 295.7 | 118.28 | 138.2625 | 105.9 | 119.2 | 119.5 | 99.9 | 168.7 | 14.4 | 21.4 | 26.6 | 2.4 | 197.3 | 6.6 | 65.2 | 224.1 | 680.1 | 53.3 | 131.7 | 638 | 61.1 | 185.8 | 240.9 | 17 | 21.4 | 166.6 | 13.4 | 16.7 | 24.9 | 35 | 157.5 | 170.4 | 29.2 | 95.7 | 22.5 | 116.4 | 107.4 | 24.3 | 39.7 | 23.4 | 22.1
381 | 142 | 296.1 | 118.44 | 138.4495 | 105.8 | 118.9 | 119.3 | 100.1 | 166.9 | 14.4 | 21.4 | 26.7 | 2.5 | 194.4 | 8.8 | 65.4 | 224.1 | 689.2 | 53.9 | 131.8 | 639.1 | 61.6 | 186 | 239.5 | 17.1 | 21.5 | 167.9 | 13.4 | 16.7 | 25.1 | 35.2 | 157.7 | 169.6 | 29.1 | 95.6 | 22.6 | 116.8 | 107.6 | 24.4 | 39.9 | 23.5 | 22.2
382 | 143 | 296.3 | 118.52 | 138.5431 | 106.1 | 118.8 | 119.2 | 100.3 | 166.1 | 14.5 | 21.4 | 26.8 | 2.7 | 192.3 | 11.6 | 65.6 | 225.2 | 697.1 | 54.5 | 131.9 | 641.1 | 62 | 187.4 | 241.7 | 17.1 | 21.6 | 168.8 | 13.4 | 16.8 | 25.2 | 35.4 | 157.8 | 170.4 | 29.1 | 96.2 | 22.7 | 117.2 | 108.2 | 24.5 | 40.1 | 23.6 | 22.3
383 | 144 | 296.5 | 118.6 | 138.6366 | 106.9 | 119.8 | 119.1 | 100.5 | 167.2 | 14.5 | 21.4 | 26.9 | 2.7 | 188.7 | 11.3 | 65.8 | 224.5 | 682.6 | 55.1 | 132 | 641.8 | 62.4 | 188.2 | 240.6 | 17.2 | 21.7 | 170 | 13.4 | 16.9 | 25.2 | 35.6 | 159 | 171.6 | 29.3 | 97.3 | 22.7 | 117.9 | 108.9 | 24.6 | 40.3 | 23.7 | 22.5
384 | 145 | 295.7 | 118.28 | 138.2625 | 107.5 | 120 | 118.7 | 100.9 | 167.9 | 14.6 | 21.4 | 27.1 | 2.9 | 191.4 | 10.8 | 66 | 225 | 677.9 | 55.7 | 132.1 | 641.9 | 62.9 | 187.8 | 241.5 | 17.3 | 21.8 | 170.7 | 13.4 | 16.9 | 25.3 | 35.8 | 159.6 | 171.8 | 29.2 | 97.7 | 22.8 | 118.3 | 109.3 | 24.8 | 40.5 | 23.8 | 22.6
385 | 146 | 296 | 118.4 | 138.4028 | 109 | 120.2 | 118.7 | 101.3 | 167.7 | 14.6 | 21.4 | 27.2 | 2.8 | 196.1 | 9.7 | 66.2 | 224.6 | 682 | 56.3 | 132.2 | 641.8 | 63.3 | 186.9 | 238.9 | 17.4 | 21.9 | 170.8 | 13.4 | 17 | 25.4 | 36 | 159.9 | 171.8 | 29.5 | 98 | 22.9 | 118.7 | 109.4 | 24.9 | 40.7 | 24 | 22.7
386 | 147 | 295.1 | 118.04 | 137.982 | 110 | 119.9 | 118.7 | 101.7 | 167.1 | 14.7 | 21.4 | 27.3 | 3 | 207.1 | 8 | 66.4 | 224.9 | 672.4 | 56.9 | 132.3 | 641 | 63.7 | 185.2 | 234.6 | 17.4 | 22 | 170.5 | 13.4 | 17.1 | 25.5 | 36.1 | 159.7 | 170.8 | 29.2 | 97.8 | 23 | 119.2 | 109.9 | 25 | 41 | 24.1 | 22.8
387 | 148 | 294.7 | 117.88 | 137.7949 | 110.3 | 119.8 | 118.8 | 102.1 | 166.5 | 14.7 | 21.4 | 27.3 | 2.7 | 232.9 | 6.3 | 66.5 | 224.9 | 680.2 | 57.5 | 132.4 | 640.3 | 64.2 | 184.4 | 233.6 | 17.5 | 22.1 | 170.5 | 13.5 | 17.1 | 25.6 | 36.3 | 159.1 | 169.2 | 28.8 | 97.2 | 23.1 | 119.2 | 110.1 | 25.2 | 41.3 | 24.2 | 23
388 | 149 | 295.9 | 118.36 | 138.356 | 110.1 | 119.7 | 119.2 | 102.5 | 165.3 | 14.7 | 21.4 | 27.4 | 3.1 | 230 | 5.6 | 66.7 | 225.5 | 683.2 | 58.1 | 132.5 | 641.1 | 64.6 | 183.8 | 233 | 17.6 | 22.2 | 170.7 | 13.5 | 17.2 | 25.9 | 36.5 | 158.6 | 168 | 28.8 | 97 | 23.2 | 119.4 | 110.1 | 25.3 | 41.4 | 24.4 | 23.1
389 | 150 | 296.1 | 118.44 | 138.4495 | 109.8 | 119.8 | 119.6 | 102.7 | 165.3 | 14.8 | 21.4 | 27.5 | 4 | 236 | 5.8 | 66.8 | 225.8 | 676.5 | 58.7 | 132.5 | 641.2 | 65 | 184 | 235.4 | 17.6 | 22.3 | 171.6 | 13.5 | 17.2 | 25.9 | 36.7 | 158.3 | 168.4 | 29.3 | 97.7 | 23.2 | 119.5 | 110.2 | 25.3 | 41.5 | 24.5 | 23.2
390 | 151 | 296.2 | 118.48 | 138.4963 | 109.6 | 119.7 | 119.5 | 102.8 | 166.4 | 14.8 | 21.4 | 27.6 | 3.7 | 192.5 | 6.6 | 66.9 | 224.3 | 664.4 | 59.3 | 132.6 | 642 | 65.4 | 183.6 | 234.2 | 17.7 | 22.3 | 172.2 | 13.5 | 17.3 | 25.9 | 36.8 | 158.5 | 168.4 | 29.5 | 98 | 23.3 | 119.4 | 110.8 | 25.4 | 41.8 | 24.6 | 23.3
391 | 152 | 295.8 | 118.32 | 138.3093 | 110 | 119.7 | 119.2 | 103 | 166.5 | 14.8 | 21.4 | 27.8 | 3.6 | 228.5 | 7.4 | 67 | 224.2 | 669.7 | 59.8 | 132.7 | 642.9 | 65.8 | 185.1 | 237.2 | 17.8 | 22.4 | 173.9 | 13.5 | 17.4 | 26 | 37 | 158.8 | 167.7 | 29.4 | 98.3 | 23.4 | 119.5 | 111.2 | 25.6 | 42 | 24.7 | 23.4
392 | 153 | 296.6 | 118.64 | 138.6833 | 110.5 | 119.8 | 118.9 | 103 | 166.5 | 14.9 | 21.4 | 27.8 | 3.5 | 228.1 | 7.2 | 67.2 | 225.4 | 685.1 | 60.4 | 132.7 | 644.7 | 66.3 | 187.9 | 243.3 | 17.9 | 22.5 | 176.4 | 13.5 | 17.4 | 26.3 | 37.2 | 160 | 168.9 | 29.9 | 100.8 | 23.5 | 119.4 | 111.5 | 25.6 | 42.2 | 24.8 | 23.5
393 | 154 | 294.9 | 117.96 | 137.8884 | 110.9 | 120.5 | 119 | 103 | 167.5 | 14.9 | 21.4 | 27.9 | 3.1 | 216.8 | 8.6 | 67.3 | 226.3 | 683.1 | 61 | 132.8 | 645.3 | 66.7 | 189.6 | 246.8 | 18 | 22.6 | 177.1 | 13.5 | 17.5 | 26.4 | 37.3 | 160.6 | 169.5 | 29.8 | 101.8 | 23.6 | 119.3 | 111.9 | 25.8 | 42.4 | 24.9 | 23.7
394 | 155 | 295.8 | 118.32 | 138.3093 | 110.9 | 120.9 | 119 | 103.1 | 168.2 | 14.9 | 21.4 | 28 | 2.6 | 210.8 | 8.1 | 67.4 | 227.5 | 689.9 | 61.6 | 132.8 | 646 | 67.1 | 189.9 | 246.7 | 18 | 22.7 | 176.6 | 13.5 | 17.6 | 26.3 | 37.5 | 161 | 169.8 | 29.9 | 101.9 | 23.6 | 119.6 | 111.9 | 25.9 | 42.6 | 25 | 23.8
395 | 156 | 295 | 118 | 137.9352 | 110.6 | 121.3 | 118.9 | 103.1 | 168 | 14.9 | 21.4 | 28.1 | 3.2 | 217.9 | 7.2 | 67.5 | 229.8 | 691.3 | 62.2 | 132.9 | 647.5 | 67.5 | 192.3 | 252 | 18.1 | 22.8 | 177.4 | 13.6 | 17.6 | 26.4 | 37.7 | 161.4 | 171.2 | 30 | 102.4 | 23.7 | 120.6 | 111.9 | 25.9 | 42.7 | 25.2 | 23.9
396 | 157 | 296.5 | 118.6 | 138.6366 | 110.5 | 122 | 118.9 | 103.2 | 168.7 | 15 | 21.4 | 28.2 | 3 | 238.4 | 6.2 | 67.6 | 229.5 | 680.4 | 62.8 | 132.9 | 648.5 | 67.9 | 193.2 | 250.2 | 18.2 | 22.9 | 178.1 | 13.6 | 17.7 | 26.6 | 37.9 | 162.1 | 172.8 | 30.4 | 103.3 | 23.8 | 120.9 | 111.8 | 26 | 42.8 | 25.3 | 24
397 | 158 | 294.1 | 117.64 | 137.5144 | 110.7 | 122.6 | 118.8 | 103.2 | 169.9 | 15 | 21.4 | 28.3 | 2.9 | 247 | 5.3 | 67.7 | 228.2 | 679.1 | 63.3 | 133 | 649.5 | 68.4 | 193 | 249.4 | 18.2 | 23 | 178.1 | 13.6 | 17.8 | 26.7 | 38 | 162.4 | 173.8 | 30.6 | 103.8 | 23.9 | 120.9 | 111.7 | 26.1 | 43 | 25.4 | 24.1
398 | 159 | 295.6 | 118.24 | 138.2157 | 110.9 | 122.6 | 118.7 | 103.2 | 171.2 | 15 | 21.4 | 28.4 | 3.1 | 247.1 | 5 | 67.9 | 227.2 | 681.5 | 63.9 | 133 | 650.2 | 68.8 | 192.2 | 249 | 18.3 | 23.1 | 178.1 | 13.6 | 17.8 | 26.8 | 38.2 | 162.2 | 173.6 | 30.6 | 104 | 24 | 121.1 | 111.5 | 26.2 | 43.1 | 25.6 | 24.2
399 | 160 | 295.6 | 118.24 | 138.2157 | 110.8 | 122.7 | 118.4 | 103.3 | 171.2 | 15.1 | 21.4 | 28.5 | 3.3 | 247.8 | 5.5 | 68 | 226.9 | 678.4 | 64.5 | 133.1 | 651.5 | 69.2 | 191.7 | 247.1 | 18.4 | 23.2 | 178.9 | 13.6 | 17.9 | 26.9 | 38.4 | 162.1 | 173.6 | 30.6 | 104 | 24.1 | 121.4 | 111.4 | 26.4 | 43.4 | 25.7 | 24.3
400 | 161 | 295.2 | 118.08 | 138.0287 | 110.4 | 122.3 | 118.7 | 103.5 | 172.4 | 15.1 | 21.4 | 28.6 | 3.4 | 196.6 | 5.7 | 68.1 | 225.8 | 666 | 65 | 133.2 | 652.4 | 69.6 | 191.8 | 247.3 | 18.5 | 23.3 | 179.5 | 13.6 | 17.9 | 26.9 | 38.6 | 162.7 | 173.7 | 30.6 | 103.9 | 24.1 | 121.4 | 112 | 26.5 | 43.6 | 25.8 | 24.5
401 | 162 | 295.6 | 118.24 | 138.2157 | 110.7 | 122 | 118.9 | 103.7 | 172.6 | 15.1 | 21.4 | 28.7 | 4.2 | 235.1 | 5.4 | 68.2 | 225.6 | 657.8 | 65.6 | 133.3 | 653 | 70 | 193.1 | 247.3 | 18.5 | 23.4 | 180.6 | 13.6 | 18 | 27 | 38.7 | 163 | 174.9 | 31 | 104 | 24.2 | 121.3 | 112.3 | 26.6 | 43.8 | 26 | 24.6
402 | 163 | 295.5 | 118.2 | 138.169 | 110.9 | 122 | 119 | 103.9 | 173.8 | 15.1 | 21.4 | 28.8 | 4 | 224.8 | 6.5 | 68.3 | 225.2 | 657.2 | 66.2 | 133.4 | 652.6 | 70.5 | 192 | 244.4 | 18.6 | 23.5 | 180.9 | 13.7 | 18 | 27.1 | 38.9 | 163.6 | 175.5 | 31.4 | 104.2 | 24.3 | 121.4 | 112.1 | 26.6 | 44 | 26.1 | 24.7
403 | 164 | 294.7 | 117.88 | 137.7949 | 111.3 | 121.9 | 118.9 | 104 | 173.6 | 15.1 | 21.3 | 28.8 | 3.2 | 203.1 | 6.9 | 68.4 | 225.1 | 685.3 | 66.7 | 133.5 | 652.7 | 70.8 | 191.6 | 244.4 | 18.7 | 23.6 | 181.4 | 13.7 | 18.1 | 27.2 | 39.1 | 163.5 | 176.1 | 31.6 | 104 | 24.4 | 121.5 | 112.5 | 26.7 | 44.1 | 26.2 | 24.8
404 | 165 | 294.7 | 117.88 | 137.7949 | 111.7 | 121.6 | 119.1 | 103.8 | 173.9 | 15.2 | 21.3 | 28.9 | 3.1 | 209 | 9.7 | 68.6 | 226.8 | 691.5 | 67.3 | 133.7 | 653 | 71.3 | 192.9 | 247.8 | 18.8 | 23.7 | 182.2 | 13.7 | 18.2 | 27.4 | 39.3 | 163.8 | 177 | 31.9 | 104.5 | 24.5 | 121.5 | 113.1 | 26.7 | 44.3 | 26.3 | 24.9
405 | 166 | 295 | 118 | 137.9352 | 111.6 | 121.3 | 119.7 | 103.6 | 175.5 | 15.2 | 21.3 | 29 | 4 | 223.5 | 11.5 | 68.7 | 226.7 | 701.3 | 67.8 | 133.9 | 653 | 71.7 | 192.7 | 246.8 | 18.8 | 23.8 | 182.8 | 13.7 | 18.2 | 27.5 | 39.5 | 164.1 | 177.1 | 31.7 | 106.1 | 24.6 | 121.4 | 113.5 | 26.8 | 44.4 | 26.5 | 25
406 | 167 | 295.1 | 118.04 | 137.982 | 111.4 | 121.3 | 120.2 | 103.4 | 176.1 | 15.3 | 21.3 | 29.1 | 4.6 | 223.7 | 9.5 | 68.9 | 226.9 | 694.7 | 68.4 | 134 | 652.4 | 72.1 | 192.3 | 244.7 | 18.9 | 23.9 | 183.2 | 13.7 | 18.3 | 27.5 | 39.7 | 164 | 177.3 | 31.9 | 106.1 | 24.6 | 121.5 | 113.3 | 26.8 | 44.5 | 26.6 | 25.2
407 | 168 | 294.9 | 117.96 | 137.8884 | 111.1 | 121.4 | 120.8 | 103.4 | 177.6 | 15.3 | 21.3 | 29.2 | 4.7 | 229.4 | 7.3 | 69 | 225.9 | 683.4 | 68.9 | 134.1 | 652.1 | 72.5 | 191.4 | 247.2 | 19 | 24 | 184.3 | 13.7 | 18.4 | 27.7 | 39.9 | 164.2 | 178.4 | 32.1 | 106.6 | 24.7 | 121.6 | 113.2 | 26.8 | 44.7 | 26.7 | 25.3
408 | 169 | 293.4 | 117.36 | 137.1871 | 110.7 | 121.1 | 121.4 | 103.6 | 177.4 | 15.3 | 21.3 | 29.3 | 4.1 | 210 | 6.5 | 69.1 | 225.6 | 679.9 | 69.5 | 134.3 | 652.7 | 72.9 | 190.9 | 247 | 19.1 | 24.1 | 185 | 13.7 | 18.4 | 27.8 | 40 | 163.5 | 177.5 | 32 | 106.5 | 24.8 | 121.7 | 113.3 | 27 | 44.8 | 26.9 | 25.4
409 | 170 | 292.8 | 117.12 | 136.9065 | 110.3 | 120.8 | 121.9 | 103.8 | 176.8 | 15.4 | 21.3 | 29.4 | 3.8 | 247 | 6.1 | 69.3 | 225.5 | 672.7 | 70.1 | 134.4 | 651.7 | 73.3 | 191.3 | 249.5 | 19.2 | 24.2 | 185.4 | 13.8 | 18.5 | 27.9 | 40.2 | 163.4 | 178.7 | 32.4 | 106.9 | 24.9 | 121.8 | 113.3 | 27 | 45 | 27 | 25.5
410 | 171 | 293.7 | 117.48 | 137.3274 | 110.1 | 121 | 122.1 | 103.9 | 177.4 | 15.4 | 21.3 | 29.4 | 3.8 | 210.4 | 7.3 | 69.4 | 224.7 | 668.6 | 70.6 | 134.5 | 651.1 | 73.7 | 190.9 | 248 | 19.2 | 24.3 | 185.2 | 13.8 | 18.5 | 28.1 | 40.4 | 163.4 | 178.8 | 32.4 | 106.9 | 25 | 121.9 | 113.6 | 27.1 | 45.1 | 27.1 | 25.6
411 | 172 | 293.1 | 117.24 | 137.0468 | 110.2 | 122.1 | 122.2 | 104 | 176.6 | 15.5 | 21.3 | 29.5 | 4.3 | 254.7 | 8 | 69.6 | 223.7 | 672.6 | 71.2 | 134.7 | 652.9 | 74.1 | 190.7 | 249.3 | 19.3 | 24.4 | 185.6 | 13.8 | 18.6 | 28.2 | 40.6 | 162.7 | 178.1 | 32.2 | 106.9 | 25 | 121.9 | 113.9 | 27.2 | 45.2 | 27.2 | 25.7
412 | 173 | 294.4 | 117.76 | 137.6547 | 110.3 | 122.4 | 122.8 | 104.1 | 177.1 | 15.5 | 21.3 | 29.6 | 4.5 | 240.1 | 8.6 | 69.7 | 223.5 | 671 | 71.8 | 134.8 | 653.8 | 74.5 | 190.4 | 251.8 | 19.4 | 24.5 | 186.4 | 13.8 | 18.7 | 28.2 | 40.8 | 162.9 | 179.7 | 32.6 | 107.2 | 25.1 | 121.9 | 114.4 | 27.2 | 45.3 | 27.3 | 25.8
413 | 174 | 291.8 | 116.72 | 136.439 | 110.5 | 122.4 | 122.9 | 103.9 | 178.5 | 15.5 | 21.3 | 29.7 | 4.8 | 217.3 | 9.5 | 69.9 | 222.4 | 667.2 | 72.3 | 134.8 | 653.6 | 74.9 | 190.2 | 255.8 | 19.5 | 24.6 | 186.7 | 13.8 | 18.8 | 28.4 | 41 | 163.3 | 180.2 | 32.7 | 108.3 | 25.2 | 121.9 | 115 | 27.4 | 45.6 | 27.5 | 25.9
414 | 175 | 294.6 | 117.84 | 137.7482 | 110.7 | 122.9 | 122.9 | 103.5 | 179.5 | 15.5 | 21.3 | 29.8 | 4.9 | 227.2 | 12 | 70 | 222.5 | 686.9 | 72.9 | 134.9 | 653.7 | 75.3 | 191 | 255.6 | 19.6 | 24.7 | 187.2 | 13.8 | 18.8 | 28.5 | 41.2 | 162.8 | 178.7 | 32.6 | 108.7 | 25.3 | 122 | 115.5 | 27.5 | 45.8 | 27.6 | 26
415 | 176 | 293.7 | 117.48 | 137.3274 | 110.3 | 124.3 | 123.3 | 103.1 | 178.5 | 15.5 | 21.3 | 29.8 | 3.4 | 216 | 14.9 | 70.1 | 224.1 | 685.3 | 73.4 | 135 | 654.5 | 75.7 | 191.7 | 255.8 | 19.7 | 24.8 | 187.8 | 13.9 | 18.9 | 28.6 | 41.4 | 162.7 | 181.2 | 32.6 | 109 | 25.4 | 122.2 | 115.6 | 27.6 | 45.8 | 27.7 | 26.2
416 | 177 | 293.1 | 117.24 | 137.0468 | 109.9 | 125.2 | 123.6 | 102.7 | 179.2 | 15.5 | 21.3 | 29.9 | 2.6 | 218.6 | 13.1 | 70.3 | 224.6 | 686.9 | 73.9 | 135 | 655.1 | 76.1 | 192 | 259.1 | 19.7 | 24.9 | 188.7 | 13.9 | 18.9 | 28.7 | 41.6 | 162.6 | 181.5 | 33 | 109.6 | 25.4 | 122.2 | 115.4 | 27.5 | 45.9 | 27.8 | 26.3
417 | 178 | 295.1 | 118.04 | 137.982 | 109.8 | 125.7 | 123.9 | 102.5 | 178.9 | 15.5 | 21.3 | 29.9 | 2.8 | 252.9 | 9.3 | 70.5 | 224.3 | 685.4 | 74.5 | 135 | 655.1 | 76.5 | 191.7 | 258 | 19.8 | 25 | 189 | 13.9 | 19 | 28.8 | 41.8 | 162.5 | 181.4 | 33 | 109.6 | 25.5 | 122.1 | 115.1 | 27.6 | 46.1 | 28 | 26.4
418 | 179 | 292.2 | 116.88 | 136.626 | 109.9 | 125.8 | 124.2 | 102.5 | 178.7 | 15.5 | 21.3 | 30 | 3.3 | 240.4 | 11 | 70.6 | 224.7 | 675 | 75 | 135 | 655.3 | 76.8 | 193.2 | 261 | 19.9 | 25.1 | 188.9 | 13.9 | 19.1 | 28.9 | 42 | 162.3 | 182.1 | 33 | 109.9 | 25.6 | 122.2 | 114.9 | 27.6 | 46.2 | 28.1 | 26.5
419 | 180 | 295 | 118 | 137.9352 | 109.8 | 125.5 | 124.9 | 102.4 | 179.9 | 15.6 | 21.3 | 30.1 | 4.5 | 238.3 | 13.7 | 70.7 | 224.4 | 665.2 | 75.6 | 135 | 655 | 77.2 | 193.6 | 258.2 | 20 | 25.2 | 189.2 | 13.9 | 19.1 | 29.1 | 42.2 | 162.4 | 182.1 | 33.1 | 110.8 | 25.7 | 122.4 | 115.3 | 27.7 | 46.4 | 28.2 | 26.6
420 | 181 | 295 | 118 | 137.9352 | 109.8 | 125.5 | 125.4 | 102.4 | 180.1 | 15.6 | 21.3 | 30.2 | 4.3 | 245.2 | 13.7 | 70.9 | 224 | 667.7 | 76.1 | 135 | 655.3 | 77.6 | 192.2 | 255.2 | 20.1 | 25.3 | 189.1 | 13.9 | 19.2 | 29.1 | 42.4 | 162.1 | 180.7 | 32.8 | 110.7 | 25.8 | 122.6 | 115.9 | 27.8 | 46.5 | 28.3 | 26.7
421 | 182 | 293.1 | 117.24 | 137.0468 | 110 | 126.1 | 125.9 | 102.5 | 177.5 | 15.7 | 21.3 | 30.3 | 3.7 | 245.1 | 13.6 | 71 | 223.9 | 675.1 | 76.7 | 135 | 656 | 78 | 192.6 | 257.7 | 20.2 | 25.4 | 190.9 | 13.9 | 19.2 | 29.2 | 42.6 | 161.2 | 180 | 32.7 | 110.5 | 25.8 | 122.6 | 116.1 | 27.9 | 46.6 | 28.4 | 26.8
422 | 183 | 295.3 | 118.12 | 138.0755 | 110.1 | 126.6 | 126.2 | 102.5 | 177.5 | 15.7 | 21.3 | 30.3 | 3.1 | 244.1 | 13 | 71.2 | 223.8 | 678.6 | 77.2 | 135 | 656.8 | 78.4 | 192.9 | 258.9 | 20.3 | 25.5 | 191.5 | 14 | 19.3 | 29.4 | 42.8 | 161.4 | 180.6 | 33.2 | 111.3 | 25.9 | 122.6 | 115.8 | 28 | 46.7 | 28.6 | 26.9
423 | 184 | 295 | 118 | 137.9352 | 110 | 126.9 | 126.5 | 102.3 | 177.7 | 15.8 | 21.3 | 30.4 | 3.8 | 255.4 | 12.1 | 71.3 | 224.7 | 674.6 | 77.7 | 135 | 657.9 | 78.7 | 194.9 | 268.2 | 20.3 | 25.6 | 193.6 | 14 | 19.4 | 29.6 | 43 | 161.7 | 181.5 | 33.4 | 111.5 | 26 | 122.7 | 115.4 | 28 | 46.8 | 28.7 | 27
424 | 185 | 295 | 118 | 137.9352 | 110.5 | 127.2 | 126.7 | 102.1 | 180.2 | 15.8 | 21.3 | 30.4 | 3 | 229.3 | 10.8 | 71.4 | 223.8 | 674.5 | 78.3 | 135 | 657.3 | 79.1 | 193.9 | 265.6 | 20.4 | 25.7 | 194.2 | 14 | 19.4 | 29.7 | 43.1 | 162.7 | 182.2 | 33.7 | 112.9 | 26 | 122.9 | 115.1 | 28.1 | 46.9 | 28.8 | 27.1
425 | 186 | 295.4 | 118.16 | 138.1222 | 111.1 | 127 | 126.8 | 101.9 | 181.2 | 15.8 | 21.3 | 30.5 | 3.4 | 222.7 | 9.5 | 71.6 | 223.2 | 679.4 | 78.8 | 135 | 657.3 | 79.5 | 192.7 | 262.7 | 20.5 | 25.8 | 194 | 14 | 19.5 | 29.9 | 43.3 | 163.1 | 181.8 | 33.6 | 113.3 | 26.1 | 122.8 | 115.1 | 28.2 | 47.1 | 28.9 | 27.2
426 | 187 | 293.2 | 117.28 | 137.0936 | 111.3 | 126.6 | 126.8 | 101.9 | 180.6 | 15.8 | 21.3 | 30.6 | 3.2 | 229.5 | 8.8 | 71.7 | 223 | 680.1 | 79.4 | 135.1 | 656.4 | 79.8 | 190.6 | 262.8 | 20.6 | 25.9 | 193.6 | 14 | 19.6 | 30 | 43.6 | 163.3 | 181.4 | 33.8 | 113.5 | 26.2 | 122.9 | 114.9 | 28.3 | 47.2 | 29.1 | 27.3
427 | 188 | 295 | 118 | 137.9352 | 111.3 | 126.1 | 126.5 | 101.8 | 181.1 | 15.8 | 21.3 | 30.7 | 3.4 | 229.8 | 7.9 | 71.8 | 222.8 | 690.1 | 79.9 | 135.1 | 654.9 | 80.2 | 189.3 | 259.9 | 20.7 | 26 | 193.4 | 14 | 19.7 | 30.1 | 43.7 | 164 | 182.1 | 33.8 | 113.9 | 26.2 | 123 | 114.7 | 28.4 | 47.3 | 29.2 | 27.4
428 | 189 | 294.2 | 117.68 | 137.5611 | 111.3 | 126 | 126.4 | 101.9 | 181.6 | 15.9 | 21.3 | 30.8 | 3.8 | 225.2 | 7.9 | 71.9 | 223.6 | 695.2 | 80.5 | 135.1 | 653.7 | 80.6 | 190 | 265.6 | 20.8 | 26.1 | 194.2 | 14 | 19.8 | 30.2 | 43.9 | 164 | 183.9 | 34 | 114.7 | 26.3 | 123.2 | 114.6 | 28.5 | 47.4 | 29.3 | 27.5
429 | 190 | 294.3 | 117.72 | 137.6079 | 111.4 | 126.3 | 126.6 | 102.2 | 182.8 | 16 | 21.3 | 30.8 | 4.3 | 241.7 | 8 | 72.1 | 224.3 | 698.3 | 81 | 135.1 | 652.6 | 80.9 | 192.5 | 270.8 | 20.9 | 26.1 | 194.5 | 14.1 | 19.8 | 30.3 | 44.1 | 164 | 184.2 | 34.1 | 115.2 | 26.4 | 123.2 | 114.6 | 28.6 | 47.5 | 29.4 | 27.6
430 | 191 | 294.5 | 117.8 | 137.7014 | 111.6 | 126.2 | 126.9 | 102.4 | 183.3 | 16 | 21.3 | 30.9 | 5.2 | 211.3 | 11.3 | 72.2 | 225.9 | 707.7 | 81.6 | 135.1 | 651.8 | 81.3 | 193 | 269.9 | 21 | 26.2 | 194.5 | 14.1 | 19.9 | 30.3 | 44.3 | 164.2 | 184.4 | 34 | 115.4 | 26.5 | 123.5 | 114.6 | 28.6 | 47.5 | 29.6 | 27.7
431 | 192 | 295.4 | 118.16 | 138.1222 | 111.6 | 126.4 | 127.2 | 102.5 | 183.1 | 16.1 | 21.3 | 30.9 | 5.5 | 217.3 | 12.8 | 72.3 | 225.5 | 703.4 | 82.1 | 135.2 | 651.1 | 81.6 | 191.9 | 265.7 | 21.1 | 26.3 | 193.9 | 14.1 | 20 | 30.3 | 44.5 | 163.9 | 183.7 | 34.3 | 115.3 | 26.5 | 123.7 | 114.6 | 28.7 | 47.6 | 29.7 | 27.8
432 | 193 | 294.1 | 117.64 | 137.5144 | 111.3 | 126.2 | 127.1 | 102.6 | 181.4 | 16.1 | 21.3 | 31 | 4.7 | 213.4 | 12 | 72.4 | 225.6 | 701.9 | 82.7 | 135.2 | 650.5 | 82 | 192.1 | 272.5 | 21.2 | 26.4 | 196.1 | 14.1 | 20.1 | 30.4 | 44.7 | 163.6 | 182.7 | 34 | 115 | 26.6 | 124 | 115.2 | 28.8 | 47.7 | 29.8 | 27.9
433 | 194 | 294.8 | 117.92 | 137.8417 | 111 | 126 | 127.1 | 102.8 | 180.2 | 16.1 | 21.3 | 31 | 4.4 | 214.6 | 14.1 | 72.6 | 225.6 | 707.3 | 83.3 | 135.2 | 650.5 | 82.4 | 192 | 269.3 | 21.2 | 26.5 | 196.3 | 14.1 | 20.1 | 30.6 | 44.9 | 163.2 | 181.6 | 34 | 114.6 | 26.7 | 124.1 | 115.4 | 28.9 | 47.8 | 29.9 | 28
434 | 195 | 295.2 | 118.08 | 138.0287 | 111 | 125.9 | 127.2 | 102.9 | 178.9 | 16.2 | 21.3 | 31.1 | 4.5 | 223.1 | 15.4 | 72.7 | 226.2 | 698.6 | 83.8 | 135.2 | 649.8 | 82.7 | 193 | 268.4 | 21.3 | 26.6 | 196.5 | 14.2 | 20.2 | 30.7 | 45.1 | 163.2 | 182.1 | 34.4 | 114.7 | 26.8 | 124.1 | 115.5 | 29 | 47.9 | 30 | 28.1
435 | 196 | 294.3 | 117.72 | 137.6079 | 110.9 | 126.1 | 127.2 | 102.8 | 179.1 | 16.2 | 21.3 | 31.2 | 4.5 | 216.1 | 14.4 | 72.8 | 224.8 | 708.2 | 84.4 | 135.3 | 648.4 | 83 | 192.6 | 264.4 | 21.4 | 26.7 | 196.1 | 14.2 | 20.3 | 30.8 | 45.3 | 163.8 | 181.2 | 34.6 | 115.2 | 26.9 | 123.9 | 115.6 | 29.1 | 48 | 30.2 | 28.2
436 | 197 | 295.7 | 118.28 | 138.2625 | 110.9 | 126.2 | 127 | 102.5 | 177.6 | 16.2 | 21.3 | 31.2 | 3.5 | 218.6 | 15.1 | 72.9 | 224 | 708 | 84.9 | 135.3 | 647 | 83.4 | 191.7 | 262.2 | 21.5 | 26.8 | 196.1 | 14.2 | 20.3 | 31.1 | 45.4 | 163.6 | 180.4 | 34.4 | 115.1 | 26.9 | 123.8 | 115.5 | 29.2 | 48 | 30.3 | 28.3
437 | 198 | 294.5 | 117.8 | 137.7014 | 110.6 | 126.2 | 127 | 102.1 | 177 | 16.3 | 21.3 | 31.2 | 3.3 | 216.7 | 14.6 | 73.1 | 225.2 | 701.4 | 85.5 | 135.4 | 646.8 | 83.7 | 192.1 | 262.9 | 21.6 | 26.9 | 196.4 | 14.2 | 20.4 | 31.1 | 45.6 | 163.5 | 180.2 | 34.1 | 115.7 | 27 | 123.8 | 115.4 | 29.2 | 48.2 | 30.4 | 28.4
438 | 199 | 294.6 | 117.84 | 137.7482 | 110.3 | 126.2 | 126.9 | 101.8 | 178.3 | 16.3 | 21.3 | 31.3 | 3.7 | 223.6 | 15.1 | 73.2 | 227 | 710.4 | 86 | 135.4 | 646.6 | 84.1 | 193 | 263.1 | 21.7 | 27 | 197.4 | 14.2 | 20.5 | 31.1 | 45.8 | 164.5 | 181.6 | 34.4 | 117.3 | 27.1 | 123.7 | 115.3 | 29.3 | 48.2 | 30.5 | 28.5
439 | 200 | 294.8 | 117.92 | 137.8417 | 109.8 | 125.9 | 126.9 | 101.9 | 180.6 | 16.3 | 21.2 | 31.3 | 4.1 | 218.8 | 14.3 | 73.3 | 228.9 | 719.1 | 86.6 | 135.5 | 645.8 | 84.4 | 193.7 | 264 | 21.8 | 27.1 | 197.1 | 14.2 | 20.6 | 31.2 | 46 | 164.4 | 182.1 | 34.5 | 117.9 | 27.2 | 123.7 | 115.1 | 29.3 | 48.4 | 30.6 | 28.6
440 | 201 | 295.2 | 118.08 | 138.0287 | 109.7 | 125.6 | 126.9 | 102.1 | 182.5 | 16.3 | 21.3 | 31.4 | 4.7 | 215.9 | 13.8 | 73.5 | 230.2 | 709.4 | 87.1 | 135.6 | 646.1 | 84.8 | 196.5 | 269.8 | 21.9 | 27.2 | 199.1 | 14.3 | 20.6 | 31.4 | 46.2 | 165.4 | 184.8 | 35.3 | 119 | 27.2 | 123.7 | 114.8 | 29.5 | 48.5 | 30.8 | 28.7
441 | 202 | 294.1 | 117.64 | 137.5144 | 109.8 | 125.3 | 127.1 | 102.2 | 184.2 | 16.4 | 21.3 | 31.4 | 4.5 | 212.4 | 13.9 | 73.6 | 230.6 | 714.8 | 87.7 | 135.6 | 645.9 | 85.1 | 196.2 | 269.4 | 22 | 27.3 | 199.3 | 14.3 | 20.7 | 31.4 | 46.3 | 165.6 | 184 | 35.3 | 119 | 27.3 | 123.6 | 114.9 | 29.7 | 48.6 | 30.9 | 28.8
442 | 203 | 295.6 | 118.24 | 138.2157 | 110.1 | 125 | 127.1 | 102.2 | 183.1 | 16.4 | 21.3 | 31.5 | 4.5 | 219.8 | 13.6 | 73.8 | 231.4 | 720.4 | 88.2 | 135.7 | 645.4 | 85.4 | 197.2 | 270.9 | 22.1 | 27.3 | 199.4 | 14.3 | 20.8 | 31.5 | 46.5 | 165.3 | 184 | 35.5 | 118.9 | 27.4 | 123.7 | 115.2 | 29.7 | 48.7 | 31 | 28.9
443 | 204 | 295.8 | 118.32 | 138.3093 | 110.2 | 124.9 | 127.2 | 102.4 | 183.7 | 16.4 | 21.3 | 31.5 | 5.5 | 200.6 | 11.2 | 73.9 | 232.2 | 721.5 | 88.8 | 135.8 | 645.4 | 85.8 | 200 | 273.9 | 22.2 | 27.4 | 200.5 | 14.3 | 20.8 | 31.6 | 46.7 | 165.8 | 185.6 | 35.9 | 119.8 | 27.5 | 123.8 | 115.3 | 29.8 | 49 | 31.2 | 29
444 | 205 | 295.6 | 118.24 | 138.2157 | 110.2 | 124.8 | 127.3 | 102.6 | 185 | 16.4 | 21.2 | 31.6 | 6.1 | 221.6 | 8.5 | 74 | 231.8 | 728.4 | 89.4 | 135.9 | 645.5 | 86.1 | 200 | 271.9 | 22.3 | 27.5 | 200.7 | 14.3 | 20.9 | 31.7 | 46.9 | 166.4 | 185 | 35.7 | 120.6 | 27.6 | 123.7 | 115.3 | 29.9 | 49.1 | 31.3 | 29.1
445 | 206 | 295.8 | 118.32 | 138.3093 | 110.2 | 124.8 | 127.5 | 103 | 183.7 | 16.5 | 21.2 | 31.6 | 4.5 | 232.4 | 8.9 | 74.2 | 232.4 | 732 | 89.9 | 136 | 645.5 | 86.4 | 200.4 | 270.1 | 22.4 | 27.6 | 201.1 | 14.4 | 20.9 | 31.8 | 47.1 | 166.2 | 184.6 | 35.5 | 120.5 | 27.6 | 123.8 | 115.2 | 30 | 49.3 | 31.4 | 29.2
446 | 207 | 294.4 | 117.76 | 137.6547 | 110.5 | 125.3 | 127.2 | 103.3 | 183.3 | 16.5 | 21.2 | 31.7 | 5.4 | 223.2 | 9.8 | 74.3 | 233.5 | 721.5 | 90.5 | 136.1 | 645.2 | 86.8 | 199.9 | 266.9 | 22.5 | 27.7 | 201 | 14.4 | 21 | 31.9 | 47.3 | 166.5 | 184.7 | 35.5 | 120.4 | 27.7 | 123.8 | 115.1 | 30.1 | 49.3 | 31.6 | 29.2
447 | 208 | 294.6 | 117.84 | 137.7482 | 111.2 | 125.3 | 127.2 | 103.6 | 184 | 16.5 | 21.2 | 31.7 | 5 | 227.5 | 8.8 | 74.4 | 233.8 | 701.8 | 91.1 | 136.2 | 646.3 | 87.1 | 200 | 267 | 22.5 | 27.8 | 201.8 | 14.4 | 21.1 | 32.1 | 47.5 | 167 | 185.5 | 35.9 | 120.8 | 27.8 | 123.8 | 115.1 | 30.4 | 49.4 | 31.7 | 29.3
448 | 209 | 295.6 | 118.24 | 138.2157 | 111.6 | 125.3 | 127.1 | 103.8 | 184.7 | 16.6 | 21.2 | 31.8 | 4.4 | 227.8 | 9.7 | 74.6 | 233 | 707.7 | 91.6 | 136.4 | 648 | 87.4 | 199.5 | 265.1 | 22.6 | 27.9 | 202.2 | 14.4 | 21.1 | 32.2 | 47.7 | 167.2 | 184.1 | 35.8 | 120.5 | 27.9 | 123.7 | 115.1 | 30.5 | 49.5 | 31.8 | 29.4
449 | 210 | 294.2 | 117.68 | 137.5611 | 111.5 | 126.1 | 126.8 | 104 | 184.3 | 16.6 | 21.2 | 31.8 | 5.6 | 226 | 10.6 | 74.7 | 233.7 | 708.3 | 92.2 | 136.5 | 649.1 | 87.8 | 201.5 | 265.1 | 22.7 | 28 | 203.3 | 14.4 | 21.2 | 32.3 | 47.8 | 167.5 | 185 | 36 | 120.8 | 28 | 123.7 | 115 | 30.6 | 49.6 | 31.9 | 29.5
450 | 211 | 295.4 | 118.16 | 138.1222 | 111.4 | 126.4 | 126.6 | 104.2 | 186.2 | 16.6 | 21.2 | 31.9 | 6.5 | 226.7 | 10.8 | 74.8 | 233.9 | 709.5 | 92.7 | 136.7 | 649.9 | 88.1 | 201.5 | 265.9 | 22.8 | 28.1 | 203.3 | 14.5 | 21.3 | 32.3 | 48 | 168 | 184.6 | 36 | 121.5 | 28 | 123.8 | 114.9 | 30.6 | 49.7 | 32.1 | 29.6
451 | 212 | 295.1 | 118.04 | 137.982 | 111.7 | 126.8 | 126.6 | 104.1 | 185.7 | 16.7 | 21.2 | 32 | 4.8 | 225.3 | 10.4 | 75 | 232.3 | 705.8 | 93.3 | 136.9 | 650.9 | 88.4 | 202.4 | 266.3 | 22.9 | 28.2 | 203.9 | 14.5 | 21.3 | 32.5 | 48.2 | 167.6 | 184.8 | 35.9 | 121.8 | 28.1 | 123.8 | 115.1 | 30.7 | 49.8 | 32.2 | 29.7
452 | 213 | 293.9 | 117.56 | 137.4209 | 112 | 126.6 | 126.5 | 103.7 | 186.2 | 16.7 | 21.2 | 32 | 3.3 | 232.7 | 9.9 | 75.1 | 231.8 | 688.1 | 93.8 | 137 | 652.7 | 88.7 | 201.5 | 263.6 | 23 | 28.3 | 203.7 | 14.5 | 21.4 | 32.6 | 48.4 | 168 | 185.1 | 36.1 | 122.3 | 28.2 | 123.8 | 115.2 | 30.8 | 50 | 32.3 | 29.8
453 | 214 | 295.7 | 118.28 | 138.2625 | 111.7 | 126.4 | 126.6 | 103.8 | 185.1 | 16.7 | 21.2 | 32 | 2.2 | 247.8 | 10.3 | 75.2 | 231.2 | 675.9 | 94.4 | 137.2 | 653.6 | 89.1 | 201.8 | 264.8 | 23.1 | 28.4 | 204 | 14.5 | 21.5 | 32.6 | 48.6 | 168 | 186.4 | 36.2 | 122.5 | 28.3 | 123.9 | 115.1 | 30.9 | 50.1 | 32.5 | 29.9
454 | 215 | 294.4 | 117.76 | 137.6547 | 111.8 | 126.2 | 126.8 | 104 | 184.6 | 16.8 | 21.2 | 32.1 | 2.1 | 250.7 | 14.3 | 75.4 | 230.7 | 676.5 | 94.9 | 137.4 | 654.2 | 89.4 | 202.7 | 264 | 23.2 | 28.5 | 205 | 14.5 | 21.5 | 32.8 | 48.8 | 168 | 185.6 | 36.2 | 123.1 | 28.4 | 124.6 | 114.9 | 31.1 | 50.2 | 32.6 | 30
455 | 216 | 293.8 | 117.52 | 137.3741 | 112.3 | 126.9 | 126.3 | 104.1 | 182.9 | 16.8 | 21.2 | 32.2 | 2.2 | 246.4 | 14.3 | 75.5 | 231 | 674 | 95.5 | 137.6 | 655.7 | 89.7 | 204 | 269.6 | 23.3 | 28.6 | 206.2 | 14.5 | 21.6 | 32.9 | 49 | 167.4 | 184.7 | 36 | 123.2 | 28.5 | 125 | 115.3 | 31.1 | 50.4 | 32.7 | 30.1
456 | 217 | 294.6 | 117.84 | 137.7482 | 112.3 | 127 | 126 | 104.4 | 182.9 | 16.8 | 21.2 | 32.2 | 2.8 | 250.8 | 13.9 | 75.7 | 231.4 | 676.6 | 96 | 137.7 | 657.4 | 90.1 | 205.3 | 270.3 | 23.4 | 28.7 | 207.2 | 14.6 | 21.7 | 33 | 49.1 | 168.1 | 186.2 | 36.5 | 124.2 | 28.5 | 125.2 | 115.9 | 31.3 | 50.5 | 32.8 | 30.2
457 | 218 | 294.7 | 117.88 | 137.7949 | 112.3 | 127 | 126 | 104.6 | 183.5 | 16.8 | 21.2 | 32.3 | 3.3 | 233.8 | 11.7 | 75.8 | 233.3 | 686.7 | 96.5 | 137.9 | 658.6 | 90.4 | 206 | 270.9 | 23.4 | 28.8 | 207.6 | 14.6 | 21.8 | 33.1 | 49.3 | 168.6 | 186.1 | 36.7 | 124.9 | 28.6 | 125.1 | 116.5 | 31.4 | 50.7 | 33 | 30.3
458 | 219 | 295.3 | 118.12 | 138.0755 | 112.6 | 127.2 | 126 | 104.7 | 186.1 | 16.9 | 21.2 | 32.4 | 3.4 | 245.2 | 9.8 | 76 | 234.4 | 694.2 | 97.1 | 138 | 658.1 | 90.7 | 207.1 | 275.1 | 23.5 | 28.9 | 208.9 | 14.6 | 21.8 | 33.2 | 49.5 | 169.6 | 187.1 | 37 | 125.7 | 28.7 | 125.2 | 116.2 | 31.5 | 51 | 33.1 | 30.4
459 | 220 | 295.1 | 118.04 | 137.982 | 112.8 | 126.9 | 126.3 | 105 | 187 | 16.9 | 21.2 | 32.5 | 3.4 | 238 | 10.7 | 76.1 | 235.1 | 702 | 97.6 | 138.2 | 657.3 | 91 | 208.6 | 279.3 | 23.6 | 29 | 209.4 | 14.6 | 21.9 | 33.3 | 49.7 | 169.5 | 187.6 | 37.3 | 126 | 28.8 | 125.4 | 116.1 | 31.6 | 51.1 | 33.3 | 30.5
460 | 221 | 294.3 | 117.72 | 137.6079 | 112.8 | 127.4 | 126.6 | 105.3 | 189.6 | 17 | 21.2 | 32.6 | 3.7 | 264.9 | 12.5 | 76.3 | 236.3 | 698.9 | 98.1 | 138.4 | 657.3 | 91.4 | 209 | 279.1 | 23.7 | 29.1 | 209.7 | 14.6 | 22 | 33.4 | 49.8 | 171.8 | 189.5 | 38.6 | 127.5 | 28.9 | 125.7 | 116.2 | 31.7 | 51.3 | 33.4 | 30.7
461 | 222 | 295 | 118 | 137.9352 | 112.7 | 127.7 | 126.9 | 105.6 | 190.6 | 17 | 21.2 | 32.7 | 4 | 266.9 | 8.4 | 76.5 | 236.4 | 724.4 | 98.7 | 138.5 | 658.5 | 91.7 | 209.8 | 281.1 | 23.8 | 29.2 | 209.3 | 14.7 | 22.1 | 33.5 | 50 | 171.8 | 189.7 | 38.4 | 127.6 | 29 | 125.7 | 116.7 | 31.8 | 51.4 | 33.5 | 30.7
462 | 223 | 295.2 | 118.08 | 138.0287 | 112.5 | 127.6 | 127.3 | 105.9 | 189.7 | 17.1 | 21.2 | 32.8 | 3.9 | 254.7 | 7.5 | 76.6 | 237.5 | 730.6 | 99.2 | 138.6 | 659.1 | 92 | 210.1 | 281.2 | 23.9 | 29.3 | 209.5 | 14.7 | 22.1 | 33.5 | 50.2 | 171.8 | 190.3 | 38.4 | 127.9 | 29.1 | 125.7 | 117.2 | 31.9 | 51.6 | 33.7 | 30.9
463 | 224 | 294.4 | 117.76 | 137.6547 | 112.5 | 127 | 127.3 | 106.2 | 189.7 | 17.2 | 21.2 | 32.9 | 4.1 | 237.3 | 8.4 | 76.8 | 238 | 732.6 | 99.7 | 138.8 | 658.3 | 92.4 | 212.5 | 285.7 | 24 | 29.4 | 210.3 | 14.7 | 22.2 | 33.7 | 50.4 | 171.9 | 190.3 | 38.2 | 128.2 | 29.1 | 125.7 | 117.2 | 31.9 | 51.7 | 33.8 | 31
464 | 225 | 293.6 | 117.44 | 137.2806 | 112.3 | 126.9 | 127.3 | 106.4 | 189.2 | 17.2 | 21.2 | 32.9 | 4.5 | 249.3 | 10.7 | 76.9 | 239.1 | 716.4 | 100.2 | 138.9 | 658.2 | 92.7 | 212.8 | 285.6 | 24.1 | 29.5 | 210.6 | 14.7 | 22.3 | 33.8 | 50.6 | 172.3 | 190.8 | 38.4 | 128.6 | 29.2 | 125.8 | 117.2 | 31.9 | 51.9 | 34 | 31
465 | 226 | 294.2 | 117.68 | 137.5611 | 112.2 | 126.5 | 127.5 | 106.6 | 187.9 | 17.2 | 21.2 | 33 | 3.7 | 244.7 | 14.4 | 77.1 | 238.6 | 707.6 | 100.8 | 139 | 657.5 | 93 | 212.3 | 282.6 | 24.2 | 29.7 | 210.2 | 14.7 | 22.3 | 33.9 | 50.8 | 172.2 | 189.7 | 38.2 | 128.9 | 29.3 | 126.1 | 117.3 | 32 | 52 | 34.1 | 31.1
466 | 227 | 295.1 | 118.04 | 137.982 | 112.3 | 126.5 | 127.7 | 106.6 | 185.8 | 17.3 | 21.2 | 33.1 | 3.3 | 244 | 15.9 | 77.3 | 236 | 710.5 | 101.3 | 139.2 | 658.3 | 93.4 | 211.4 | 282.3 | 24.3 | 29.7 | 210.9 | 14.8 | 22.4 | 33.9 | 51 | 171.9 | 188.8 | 38.4 | 128.6 | 29.4 | 126.1 | 117.7 | 32.2 | 52.1 | 34.3 | 31.3
467 | 228 | 294.3 | 117.72 | 137.6079 | 112.5 | 126.7 | 128 | 106.8 | 186.2 | 17.3 | 21.2 | 33.1 | 3.1 | 237.5 | 15.5 | 77.4 | 235 | 707.7 | 101.8 | 139.3 | 658 | 93.7 | 209.3 | 283.1 | 24.4 | 29.9 | 211.1 | 14.8 | 22.4 | 34 | 51.2 | 172 | 188 | 38.8 | 129.2 | 29.4 | 126.2 | 117.6 | 32.3 | 52.2 | 34.4 | 31.3
468 | 229 | 294.1 | 117.64 | 137.5144 | 112.6 | 127 | 128.3 | 107 | 185.3 | 17.4 | 21.2 | 33.1 | 3.2 | 236.3 | 14.1 | 77.6 | 233.8 | 695.2 | 102.3 | 139.4 | 657.9 | 94 | 208.4 | 282.6 | 24.5 | 30 | 211.1 | 14.8 | 22.5 | 34.2 | 51.4 | 171.3 | 186.6 | 38.5 | 129 | 29.5 | 126.5 | 117.5 | 32.6 | 52.3 | 34.6 | 31.4
469 | 230 | 294.9 | 117.96 | 137.8884 | 112.8 | 127 | 128.4 | 107.3 | 183.6 | 17.4 | 21.2 | 33.1 | 2.5 | 239.9 | 11.6 | 77.8 | 233.5 | 701.9 | 102.8 | 139.5 | 658.1 | 94.3 | 206.9 | 278.8 | 24.6 | 30.1 | 210.7 | 14.8 | 22.6 | 34.4 | 51.6 | 171 | 186.4 | 38.3 | 129 | 29.6 | 126.7 | 117.7 | 32.6 | 52.4 | 34.7 | 31.5
470 | 231 | 295 | 118 | 137.9352 | 113.2 | 127.2 | 128.6 | 107.7 | 182.3 | 17.4 | 21.2 | 33.1 | 3.5 | 233.9 | 12.9 | 77.9 | 235.4 | 709.4 | 103.4 | 139.6 | 658 | 94.7 | 207.4 | 279.4 | 24.7 | 30.2 | 211.4 | 14.8 | 22.7 | 34.5 | 51.8 | 170.7 | 186.5 | 38.2 | 129.1 | 29.7 | 126.6 | 118.2 | 32.7 | 52.5 | 34.8 | 31.6
471 | 232 | 295.2 | 118.08 | 138.0287 | 113.5 | 127.7 | 128.8 | 108 | 182.5 | 17.5 | 21.2 | 33.2 | 5 | 239.9 | 14 | 78.1 | 234 | 721.1 | 103.9 | 139.8 | 657.2 | 95 | 206.2 | 275.1 | 24.8 | 30.3 | 211.1 | 14.9 | 22.8 | 34.6 | 52 | 170.5 | 186.8 | 38.2 | 129.5 | 29.8 | 126.6 | 118.4 | 32.8 | 52.6 | 34.9 | 31.7
472 | 233 | 294.4 | 117.76 | 137.6547 | 113.5 | 128.4 | 128.9 | 108.4 | 183.3 | 17.6 | 21.2 | 33.3 | 4.4 | 252.1 | 14.3 | 78.3 | 234.8 | 739.8 | 104.4 | 139.9 | 658.7 | 95.3 | 206.6 | 274.5 | 24.9 | 30.4 | 211.2 | 14.9 | 22.8 | 34.7 | 52.2 | 170.5 | 187.7 | 38.4 | 129.6 | 29.9 | 126.7 | 118.7 | 32.9 | 52.7 | 35.1 | 31.8
473 | 234 | 294.5 | 117.8 | 137.7014 | 113.6 | 128.5 | 129.2 | 108.5 | 185.3 | 17.6 | 21.2 | 33.3 | 4.8 | 246.9 | 13.2 | 78.5 | 236.8 | 739.1 | 104.9 | 140 | 659.9 | 95.6 | 207.4 | 275 | 25 | 30.5 | 212.1 | 14.9 | 22.9 | 34.8 | 52.4 | 171.1 | 189.6 | 38.6 | 130.4 | 30 | 126.7 | 119 | 33 | 52.9 | 35.2 | 31.9
474 | 235 | 295.4 | 118.16 | 138.1222 | 113.5 | 128.2 | 129.4 | 108.5 | 187 | 17.7 | 21.2 | 33.4 | 4.3 | 241.3 | 12.8 | 78.7 | 236.8 | 739.1 | 105.4 | 140.1 | 659.4 | 96 | 206.3 | 274 | 25.1 | 30.6 | 211.8 | 14.9 | 23 | 34.8 | 52.5 | 171.3 | 189.9 | 38.9 | 131.1 | 30 | 126.7 | 118.9 | 33.1 | 53.1 | 35.4 | 32
475 | 236 | 295.3 | 118.12 | 138.0755 | 113.5 | 127.9 | 129.6 | 108.6 | 186.6 | 17.7 | 21.2 | 33.4 | 3.3 | 238.1 | 14.3 | 78.8 | 238.6 | 747.2 | 105.9 | 140.3 | 658.5 | 96.3 | 207.6 | 280.2 | 25.2 | 30.7 | 211.9 | 15 | 23.1 | 34.9 | 52.7 | 171.1 | 190.4 | 39.2 | 130.9 | 30.1 | 126.8 | 118.7 | 33.2 | 53.2 | 35.5 | 32.1
476 | 237 | 295.5 | 118.2 | 138.169 | 113.3 | 128 | 129.6 | 108.9 | 190.5 | 17.8 | 21.2 | 33.4 | 3.5 | 259.9 | 16.2 | 79 | 239.1 | 733 | 106.4 | 140.4 | 658.6 | 96.6 | 212.4 | 293.1 | 25.3 | 30.8 | 214.2 | 15 | 23.1 | 35.1 | 52.9 | 171.9 | 191.8 | 39.7 | 132.1 | 30.2 | 126.8 | 118.9 | 33.3 | 53.4 | 35.6 | 32.2
477 | 238 | 295.1 | 118.04 | 137.982 | 113.2 | 128 | 129.6 | 109.2 | 192.7 | 17.8 | 21.2 | 33.5 | 3 | 251.5 | 16.8 | 79.2 | 240.3 | 716.8 | 106.9 | 140.5 | 657.6 | 96.9 | 213.4 | 293.3 | 25.4 | 31 | 214.5 | 15 | 23.2 | 35.2 | 53.1 | 172.5 | 193.6 | 39.9 | 133.2 | 30.3 | 127 | 119.3 | 33.4 | 53.6 | 35.8 | 32.3
478 | 239 | 294.4 | 117.76 | 137.6547 | 113.4 | 128.7 | 129.7 | 109.2 | 193.8 | 17.9 | 21.2 | 33.6 | 3.3 | 249.3 | 14.1 | 79.4 | 241 | 710.6 | 107.4 | 140.6 | 656.8 | 97.2 | 214.7 | 296.1 | 25.5 | 31.1 | 214.7 | 15 | 23.3 | 35.3 | 53.2 | 173.4 | 195.4 | 40.1 | 133.9 | 30.3 | 127.1 | 119.7 | 33.5 | 53.7 | 35.9 | 32.4
479 | 240 | 295.2 | 118.08 | 138.0287 | 113.6 | 130.2 | 130.1 | 109.3 | 194.9 | 17.9 | 21.2 | 33.6 | 4.3 | 245.3 | 15 | 79.6 | 241.1 | 709.6 | 107.9 | 140.8 | 656.6 | 97.5 | 216.1 | 298.7 | 25.6 | 31.2 | 215.4 | 15 | 23.3 | 35.5 | 53.4 | 174 | 196 | 40.4 | 134.4 | 30.4 | 127.2 | 119.8 | 33.6 | 53.8 | 36 | 32.5
480 | 241 | 296.4 | 118.56 | 138.5898 | 114.2 | 131.3 | 130.5 | 109.2 | 196.2 | 17.9 | 21.2 | 33.7 | 4.1 | 249.7 | 15.9 | 79.8 | 239.5 | 711 | 108.4 | 140.9 | 657.2 | 97.9 | 216.2 | 296.5 | 25.7 | 31.3 | 216 | 15.1 | 23.4 | 35.6 | 53.6 | 174.5 | 196.4 | 40.6 | 135.5 | 30.5 | 127.3 | 119.9 | 33.8 | 53.8 | 36.2 | 32.6
481 | 242 | 297 | 118.8 | 138.8704 | 114.5 | 132.3 | 130.6 | 108.9 | 196.3 | 18 | 21.2 | 33.8 | 3.7 | 257.8 | 16.8 | 79.9 | 240 | 714.3 | 108.9 | 141 | 659.8 | 98.2 | 216.4 | 295.7 | 25.8 | 31.4 | 216.6 | 15.1 | 23.5 | 35.6 | 53.8 | 174.7 | 194.9 | 40.2 | 135.1 | 30.6 | 127.5 | 119.7 | 33.9 | 53.9 | 36.4 | 32.7
482 | 243 | 296.3 | 118.52 | 138.5431 | 114.7 | 132.7 | 130.8 | 108.8 | 195.8 | 18 | 21.2 | 33.8 | 3.5 | 253.8 | 17.4 | 80.1 | 240.4 | 712.1 | 109.4 | 141.1 | 661.7 | 98.5 | 217.8 | 296.5 | 25.9 | 31.5 | 217.8 | 15.1 | 23.5 | 35.7 | 54 | 175.3 | 196.2 | 40.2 | 135.8 | 30.7 | 127.9 | 119.7 | 34.1 | 54 | 36.5 | 32.8
483 | 244 | 296.8 | 118.72 | 138.7768 | 114.6 | 133.2 | 130.9 | 108.9 | 197.7 | 18 | 21.2 | 33.9 | 3.7 | 248.8 | 16.4 | 80.3 | 240.4 | 713.6 | 109.9 | 141.2 | 661.6 | 98.8 | 218.2 | 296.9 | 25.9 | 31.6 | 218.5 | 15.1 | 23.6 | 35.9 | 54.2 | 176 | 196 | 40.4 | 135.8 | 30.7 | 128.2 | 119.5 | 34.2 | 54.1 | 36.6 | 32.9
484 | 245 | 295.9 | 118.36 | 138.356 | 114.5 | 133.6 | 131.1 | 109 | 197.7 | 18 | 21.2 | 33.9 | 4.2 | 247.5 | 15 | 80.5 | 240.8 | 707.5 | 110.3 | 141.3 | 661.3 | 99.1 | 217.6 | 297.8 | 26 | 31.7 | 218.8 | 15.1 | 23.7 | 36 | 54.4 | 176.1 | 197.9 | 40.6 | 135.9 | 30.8 | 128.3 | 119.4 | 34.3 | 54.3 | 36.8 | 33
485 | 246 | 296.5 | 118.6 | 138.6366 | 114.7 | 133.6 | 131.3 | 109.1 | 199.4 | 18.1 | 21.2 | 34 | 4.1 | 243 | 14.8 | 80.7 | 241.3 | 714.3 | 110.8 | 141.4 | 661.4 | 99.4 | 219.3 | 303.3 | 26.1 | 31.8 | 219.8 | 15.2 | 23.8 | 36.1 | 54.6 | 178.2 | 203 | 41.6 | 136.7 | 30.9 | 128.3 | 119.2 | 34.3 | 54.4 | 36.9 | 33.1
486 | 247 | 296.2 | 118.48 | 138.4963 | 114.5 | 133.3 | 131.1 | 109.1 | 203.9 | 18.1 | 21.2 | 34.1 | 3.6 | 252.3 | 13.7 | 80.9 | 242 | 712.5 | 111.3 | 141.5 | 660.7 | 99.7 | 220.8 | 310.9 | 26.2 | 31.9 | 221.4 | 15.2 | 23.8 | 36.2 | 54.8 | 180.2 | 204 | 42.1 | 137.6 | 31 | 128.3 | 119.1 | 34.3 | 54.5 | 37 | 33.2
487 | 248 | 295.8 | 118.32 | 138.3093 | 114.2 | 132.8 | 131.3 | 109.3 | 205.1 | 18.1 | 21.2 | 34.2 | 4.3 | 235.7 | 14.6 | 81.1 | 241.7 | 699 | 111.8 | 141.6 | 659.3 | 100.1 | 219.9 | 305.2 | 26.3 | 32.1 | 221.5 | 15.2 | 23.9 | 36.3 | 54.9 | 180.8 | 205.4 | 42.4 | 138 | 31.1 | 128.4 | 119 | 34.4 | 54.6 | 37.2 | 33.3
488 | 249 | 296.5 | 118.6 | 138.6366 | 113.9 | 132.5 | 131.7 | 109.4 | 206.8 | 18.1 | 21.2 | 34.2 | 4.2 | 243.2 | 14.1 | 81.3 | 241.2 | 712.2 | 112.3 | 141.7 | 658.1 | 100.4 | 218.7 | 301.9 | 26.5 | 32.2 | 221.1 | 15.2 | 24 | 36.5 | 55.2 | 181.1 | 205.2 | 42.3 | 138.1 | 31.1 | 128.5 | 119 | 34.5 | 54.6 | 37.3 | 33.3
489 | 250 | 296 | 118.4 | 138.4028 | 114.1 | 131.9 | 132.3 | 109.6 | 205.1 | 18.1 | 21.2 | 34.2 | 3.7 | 244.1 | 14.6 | 81.6 | 242 | 716.7 | 112.8 | 141.8 | 657.6 | 100.7 | 221.1 | 304.9 | 26.6 | 32.3 | 222.6 | 15.3 | 24.1 | 36.6 | 55.4 | 180.4 | 204.8 | 42 | 137.7 | 31.2 | 128.7 | 119.1 | 34.5 | 54.8 | 37.4 | 33.4
490 | 251 | 295.3 | 118.12 | 138.0755 | 114 | 131.3 | 133 | 110.1 | 204.4 | 18.1 | 21.2 | 34.3 | 4.3 | 241 | 13.6 | 81.8 | 241.6 | 718.3 | 113.3 | 141.9 | 656.7 | 101.1 | 221.4 | 303.8 | 26.7 | 32.4 | 222.7 | 15.3 | 24.2 | 36.7 | 55.6 | 180.6 | 206 | 42.5 | 138.3 | 31.3 | 129 | 119.5 | 34.7 | 54.8 | 37.6 | 33.5
491 | 252 | 295 | 118 | 137.9352 | 114.2 | 131.3 | 133.4 | 110.2 | 204.8 | 18.1 | 21.2 | 34.3 | 3.5 | 260.3 | 11.4 | 82 | 242.5 | 725.2 | 113.8 | 142 | 656.7 | 101.4 | 219.9 | 302.1 | 26.8 | 32.5 | 222 | 15.3 | 24.3 | 36.9 | 55.8 | 180.8 | 205.5 | 42.7 | 138.7 | 31.4 | 129.2 | 119.8 | 34.8 | 55 | 37.7 | 33.6
492 | 253 | 295.6 | 118.24 | 138.2157 | 114.5 | 131.6 | 133.6 | 110.2 | 204.5 | 18.2 | 21.2 | 34.3 | 3.5 | 228.9 | 10.6 | 82.2 | 243.6 | 710.4 | 114.3 | 142.1 | 655.8 | 101.7 | 219.9 | 301.8 | 26.8 | 32.6 | 222.2 | 15.3 | 24.4 | 36.9 | 56 | 181.1 | 206.3 | 42.6 | 139.4 | 31.5 | 129.5 | 119.9 | 34.9 | 55.1 | 37.8 | 33.7
493 | 254 | 296.2 | 118.48 | 138.4963 | 114.8 | 131.5 | 134 | 110.4 | 204.1 | 18.2 | 21.2 | 34.3 | 3.1 | 250 | 9.1 | 82.4 | 242.7 | 700.5 | 114.8 | 142.2 | 654.1 | 102.1 | 218.6 | 296.7 | 27 | 32.8 | 222 | 15.4 | 24.5 | 37.1 | 56.2 | 180.6 | 205.7 | 42.5 | 139.5 | 31.6 | 129.7 | 119.9 | 34.9 | 55.2 | 37.9 | 33.8
494 | 255 | 296.5 | 118.6 | 138.6366 | 115.3 | 131.4 | 134.3 | 110.7 | 202.7 | 18.2 | 21.2 | 34.4 | 3.3 | 233.2 | 8.8 | 82.6 | 241 | 689.8 | 115.3 | 142.3 | 652.3 | 102.4 | 216.9 | 293 | 27.1 | 32.9 | 221.7 | 15.4 | 24.6 | 37.2 | 56.4 | 179.8 | 204.3 | 42.4 | 139.5 | 31.7 | 129.8 | 120.6 | 35 | 55.3 | 38.1 | 33.9
495 | 256 | 293.7 | 117.48 | 137.3274 | 116 | 132.4 | 134.5 | 110.9 | 199.9 | 18.3 | 21.2 | 34.5 | 2.9 | 237.3 | 11.1 | 82.8 | 240 | 710.1 | 115.8 | 142.4 | 650.8 | 102.8 | 215.6 | 289.8 | 27.2 | 33 | 221.3 | 15.4 | 24.6 | 37.2 | 56.6 | 178.5 | 201.5 | 42.1 | 139 | 31.7 | 129.9 | 121.2 | 35.1 | 55.4 | 38.2 | 34
496 | 257 | 296.1 | 118.44 | 138.4495 | 116.5 | 132.9 | 134.6 | 111.2 | 196.2 | 18.3 | 21.2 | 34.5 | 2.5 | 226.5 | 11.6 | 83 | 239.8 | 724.3 | 116.3 | 142.5 | 651.5 | 103.1 | 215 | 289.2 | 27.3 | 33.1 | 221.2 | 15.4 | 24.7 | 37.3 | 56.8 | 177.7 | 200.4 | 41.9 | 138.5 | 31.8 | 129.9 | 121.4 | 35.2 | 55.4 | 38.3 | 34.1
497 | 258 | 295.7 | 118.28 | 138.2625 | 116.5 | 132.8 | 134.8 | 111.5 | 195.8 | 18.4 | 21.2 | 34.5 | 2.5 | 234.5 | 11 | 83.2 | 241.1 | 718.3 | 116.8 | 142.5 | 652.4 | 103.4 | 216.1 | 293.1 | 27.4 | 33.2 | 222 | 15.4 | 24.8 | 37.5 | 57.1 | 178.1 | 199.7 | 41.8 | 139.8 | 31.9 | 130.1 | 121.4 | 35.3 | 55.6 | 38.4 | 34.2
498 | 259 | 297.3 | 118.92 | 139.0106 | 116.7 | 132.5 | 135.1 | 111.9 | 195.7 | 18.5 | 21.2 | 34.5 | 2.6 | 213.4 | 9.1 | 83.4 | 244 | 728.3 | 117.4 | 142.7 | 653.1 | 103.8 | 217.3 | 294.1 | 27.5 | 33.3 | 222.9 | 15.5 | 24.9 | 37.6 | 57.2 | 179.2 | 200.7 | 41.8 | 140.7 | 32 | 130.3 | 121.4 | 35.4 | 55.8 | 38.5 | 34.3
499 | 260 | 295.4 | 118.16 | 138.1222 | 117.1 | 133.3 | 135.3 | 112.3 | 196.9 | 18.6 | 21.2 | 34.5 | 2.5 | 218 | 7.9 | 83.6 | 247 | 712.7 | 117.9 | 142.8 | 653.3 | 104.2 | 218.2 | 292.7 | 27.6 | 33.4 | 223.6 | 15.5 | 25 | 37.8 | 57.4 | 180.3 | 201.9 | 41.9 | 141.4 | 32.1 | 130.5 | 121.8 | 35.6 | 55.9 | 38.7 | 34.4
500 | 261 | 294 | 117.6 | 137.4676 | 117.6 | 134.7 | 135.3 | 112.6 | 196.3 | 18.7 | 21.2 | 34.5 | 2.4 | 216.1 | 8.9 | 83.8 | 248.1 | 702.8 | 118.4 | 142.9 | 653 | 104.5 | 217.5 | 289.7 | 27.7 | 33.5 | 224 | 15.5 | 25.1 | 37.8 | 57.6 | 180.9 | 201.3 | 41.9 | 142.2 | 32.1 | 130.6 | 122.2 | 35.7 | 56.1 | 38.8 | 34.5
501 | 262 | 294.2 | 117.68 | 137.5611 | 117.8 | 135.2 | 135.2 | 112.7 | 195.1 | 18.7 | 21.2 | 34.5 | 1.9 | 221 | 10 | 84 | 247.7 | 701.6 | 118.9 | 143 | 652.8 | 104.9 | 217.7 | 291.4 | 27.8 | 33.7 | 224.7 | 15.5 | 25.2 | 37.9 | 57.8 | 181.5 | 201.4 | 42.1 | 142.4 | 32.2 | 130.9 | 122.1 | 35.8 | 56.3 | 39 | 34.6
502 | 263 | 294.1 | 117.64 | 137.5144 | 118.7 | 135 | 134.9 | 112.9 | 196.1 | 18.8 | 21.2 | 34.5 | 1.9 | 198.4 | 9.3 | 84.2 | 247.8 | 710.2 | 119.5 | 143.2 | 651.9 | 105.2 | 221.6 | 302.7 | 27.9 | 33.8 | 226.7 | 15.6 | 25.3 | 38 | 58 | 182 | 201.9 | 42.6 | 142.7 | 32.3 | 131.2 | 122.3 | 35.9 | 56.4 | 39.1 | 34.7
503 | 264 | 294 | 117.6 | 137.4676 | 119.5 | 135.2 | 134.7 | 113.1 | 196.5 | 18.8 | 21.2 | 34.6 | 2.2 | 194.2 | 9.1 | 84.4 | 247.2 | 711.9 | 120 | 143.4 | 651.1 | 105.6 | 224.4 | 306.4 | 28 | 33.9 | 227.1 | 15.6 | 25.4 | 38.2 | 58.1 | 182.3 | 203 | 43 | 143.7 | 32.4 | 131.6 | 122.9 | 35.9 | 56.5 | 39.3 | 34.8
504 | 265 | 294.2 | 117.68 | 137.5611 | 119.5 | 135.7 | 134.6 | 113.2 | 197.7 | 18.9 | 21.2 | 34.6 | 2.6 | 184.6 | 10 | 84.6 | 246.7 | 725.3 | 120.5 | 143.6 | 651.7 | 105.9 | 226.5 | 307.2 | 28.1 | 34 | 227.7 | 15.6 | 25.4 | 38.2 | 58.3 | 183.1 | 203.7 | 43.2 | 144.8 | 32.5 | 131.7 | 123.1 | 36 | 56.7 | 39.4 | 34.9
505 | 266 | 294.3 | 117.72 | 137.6079 | 119.2 | 136.7 | 134.8 | 113.5 | 198.5 | 18.9 | 21.2 | 34.7 | 2.2 | 189.3 | 11.9 | 84.8 | 246.9 | 720.9 | 121 | 143.8 | 652.1 | 106.3 | 227.8 | 304 | 28.2 | 34.1 | 226.9 | 15.6 | 25.5 | 38.4 | 58.5 | 183.4 | 203.9 | 43.2 | 144.8 | 32.6 | 131.7 | 123.2 | 36.1 | 56.8 | 39.6 | 35
506 | 267 | 294.2 | 117.68 | 137.5611 | 119 | 137 | 134.9 | 113.6 | 199.6 | 18.9 | 21.2 | 34.7 | 2.3 | 184.1 | 11.2 | 85 | 245.2 | 721.2 | 121.5 | 144 | 651.9 | 106.7 | 230.3 | 311.1 | 28.3 | 34.2 | 228.4 | 15.7 | 25.6 | 38.4 | 58.7 | 183.8 | 203.9 | 43.2 | 145.3 | 32.7 | 131.7 | 123 | 36.2 | 56.9 | 39.7 | 35.1
507 | 268 | 294.3 | 117.72 | 137.6079 | 119.2 | 137 | 134.8 | 113.6 | 201.4 | 19 | 21.2 | 34.8 | 2.7 | 189.9 | 10.8 | 85.3 | 243.8 | 711.9 | 122.1 | 144.3 | 650.7 | 107 | 229.8 | 308.5 | 28.4 | 34.4 | 228.5 | 15.7 | 25.7 | 38.5 | 58.9 | 184.7 | 204.8 | 43.5 | 146.8 | 32.8 | 131.6 | 122.9 | 36.3 | 57 | 39.9 | 35.2
508 | 269 | 294.5 | 117.8 | 137.7014 | 119.4 | 136.6 | 134.6 | 113.6 | 199.7 | 19 | 21.2 | 34.8 | 2.9 | 184.1 | 11 | 85.5 | 243.6 | 718.5 | 122.6 | 144.5 | 649.6 | 107.4 | 227.4 | 304.4 | 28.5 | 34.5 | 227.6 | 15.7 | 25.8 | 38.6 | 59.1 | 183.7 | 203.1 | 43.2 | 146.1 | 32.9 | 131.8 | 123.3 | 36.4 | 57.1 | 40.1 | 35.3
509 | 270 | 293.6 | 117.44 | 137.2806 | 119.3 | 136.3 | 134.9 | 113.6 | 200.1 | 19 | 21.2 | 34.9 | 3 | 189.3 | 11.5 | 85.7 | 245.1 | 733.1 | 123.1 | 144.7 | 649.4 | 107.8 | 226.7 | 304.6 | 28.6 | 34.6 | 227.7 | 15.7 | 25.9 | 38.8 | 59.2 | 183.4 | 206 | 43.9 | 146.8 | 32.9 | 131.9 | 123.5 | 36.5 | 57.1 | 40.2 | 35.4
510 | 271 | 296 | 118.4 | 138.4028 | 119.2 | 135.7 | 135.1 | 113.6 | 201.2 | 19 | 21.2 | 35 | 3.1 | 229.5 | 9.1 | 85.9 | 245.3 | 735.3 | 123.6 | 144.9 | 649 | 108.1 | 227.1 | 309.6 | 28.7 | 34.7 | 228.3 | 15.8 | 26 | 39 | 59.4 | 182.6 | 204.6 | 43.9 | 146.7 | 33 | 132.1 | 123.3 | 36.6 | 57.2 | 40.3 | 35.5
511 | 272 | 295.6 | 118.24 | 138.2157 | 119.3 | 135.2 | 135.1 | 113.6 | 200.2 | 19.1 | 21.1 | 35 | 2.4 | 206 | 9.1 | 86.1 | 244.6 | 724.2 | 124.1 | 145.2 | 647.6 | 108.5 | 225.2 | 304.1 | 28.8 | 34.8 | 228.1 | 15.8 | 26 | 39 | 59.6 | 182.5 | 204.3 | 43.9 | 146.9 | 33.1 | 132.2 | 123.2 | 36.7 | 57.3 | 40.5 | 35.6
512 | 273 | 295.8 | 118.32 | 138.3093 | 119.3 | 135 | 135.3 | 113.8 | 198.7 | 19.1 | 21.1 | 35 | 2.4 | 213 | 10.2 | 86.3 | 245.3 | 723.4 | 124.6 | 145.4 | 646.1 | 108.8 | 224.7 | 303.9 | 28.9 | 35 | 228.7 | 15.8 | 26.1 | 39.2 | 59.8 | 181.4 | 203.5 | 43.9 | 146.6 | 33.2 | 132 | 123.1 | 36.9 | 57.4 | 40.6 | 35.7
513 | 274 | 295.4 | 118.16 | 138.1222 | 119.2 | 134.8 | 135.7 | 114 | 200.1 | 19.1 | 21.1 | 35.1 | 2.4 | 218.3 | 10.2 | 86.5 | 244.6 | 716.8 | 125.1 | 145.6 | 644.7 | 109.1 | 225.5 | 304.4 | 29 | 35.1 | 229.4 | 15.8 | 26.2 | 39.3 | 60 | 181.6 | 204.4 | 44.2 | 147.3 | 33.3 | 132 | 123.3 | 37 | 57.4 | 40.7 | 35.8
514 | 275 | 295.8 | 118.32 | 138.3093 | 118.8 | 134.5 | 135.9 | 114.2 | 200 | 19.1 | 21.1 | 35.1 | 2.6 | 216.8 | 9.6 | 86.7 | 243.7 | 710.5 | 125.6 | 145.8 | 644.6 | 109.5 | 224.6 | 303.5 | 29.1 | 35.2 | 230.8 | 15.9 | 26.3 | 39.4 | 60.2 | 180.7 | 202.8 | 44 | 147.2 | 33.4 | 132.1 | 123.4 | 37 | 57.6 | 40.8 | 35.9
515 | 276 | 296 | 118.4 | 138.4028 | 118.9 | 134.5 | 136.6 | 114.2 | 199.3 | 19.1 | 21.1 | 35.2 | 2.7 | 218.8 | 9.4 | 86.9 | 245.7 | 703.6 | 126.1 | 146 | 644.8 | 109.8 | 226.3 | 309.4 | 29.3 | 35.3 | 233 | 15.9 | 26.4 | 39.5 | 60.3 | 181 | 204.4 | 44.3 | 148 | 33.4 | 132.1 | 123.6 | 37.2 | 57.7 | 41 | 36
516 | 277 | 294.6 | 117.84 | 137.7482 | 119.5 | 134.4 | 137.2 | 114.3 | 203.1 | 19.2 | 21.1 | 35.3 | 3.2 | 242.5 | 8 | 87.2 | 245.2 | 703.8 | 126.5 | 146.2 | 644.4 | 110.1 | 228.1 | 310.9 | 29.4 | 35.4 | 234.8 | 15.9 | 26.5 | 39.6 | 60.5 | 182.4 | 206.4 | 44.9 | 149.2 | 33.5 | 132.1 | 123.9 | 37.2 | 57.8 | 41.1 | 36.1
517 | 278 | 291.6 | 116.64 | 136.3454 | 119.8 | 134.3 | 137.7 | 114.5 | 203.6 | 19.2 | 21.1 | 35.3 | 3.5 | 270.4 | 7.6 | 87.4 | 244.9 | 702.5 | 127 | 146.4 | 643.9 | 110.4 | 227.1 | 307.5 | 29.5 | 35.5 | 233.9 | 15.9 | 26.6 | 39.8 | 60.7 | 182.6 | 205.9 | 44.8 | 149.2 | 33.6 | 132 | 123.9 | 37.3 | 58 | 41.2 | 36.1
518 | 279 | 293.6 | 117.44 | 137.2806 | 119.9 | 134.4 | 138.2 | 114.6 | 202.1 | 19.2 | 21.1 | 35.4 | 3.5 | 241.8 | 8.4 | 87.6 | 245.6 | 694.9 | 127.5 | 146.7 | 643.3 | 110.7 | 226.4 | 304.6 | 29.6 | 35.7 | 233.6 | 16 | 26.6 | 39.9 | 60.9 | 182.5 | 204.3 | 44.6 | 148.9 | 33.7 | 132 | 123.8 | 37.5 | 58 | 41.4 | 36.2
519 | 280 | 292.9 | 117.16 | 136.9533 | 119.9 | 134.5 | 138.6 | 114.7 | 200.5 | 19.3 | 21.1 | 35.4 | 3.3 | 243.7 | 8.9 | 87.9 | 246 | 691.1 | 128 | 146.9 | 642.8 | 111 | 225.8 | 303.3 | 29.7 | 35.8 | 233.8 | 16 | 26.7 | 40 | 61.1 | 182.3 | 203.9 | 44.7 | 148.4 | 33.7 | 132.1 | 123.8 | 37.7 | 58.1 | 41.5 | 36.3
520 | 281 | 294.4 | 117.76 | 137.6547 | 119.6 | 135.4 | 139.1 | 114.7 | 200.2 | 19.4 | 21.1 | 35.5 | 3.4 | 251.1 | 8 | 88.1 | 248.1 | 690.8 | 128.5 | 147.1 | 641.9 | 111.2 | 226.8 | 305 | 29.8 | 35.9 | 235 | 16 | 26.8 | 40.1 | 61.3 | 182.7 | 204.2 | 45.1 | 148.4 | 33.8 | 132.4 | 123.8 | 37.8 | 58.2 | 41.6 | 36.4
521 | 282 | 295.4 | 118.16 | 138.1222 | 120 | 136.3 | 139.3 | 114.8 | 200.1 | 19.4 | 21.1 | 35.5 | 3 | 252.3 | 7.9 | 88.4 | 247.9 | 683 | 129 | 147.3 | 641.9 | 111.4 | 226.3 | 300.1 | 29.9 | 36 | 234.5 | 16 | 26.9 | 40.2 | 61.5 | 182.8 | 204 | 45.2 | 148.8 | 33.9 | 132.5 | 123.8 | 37.9 | 58.4 | 41.8 | 36.5
522 | 283 | 295 | 118 | 137.9352 | 120.7 | 136.2 | 139.3 | 115.2 | 198.4 | 19.4 | 21.1 | 35.6 | 3.3 | 250.9 | 8.3 | 88.7 | 246.4 | 682.1 | 129.4 | 147.6 | 641.8 | 111.7 | 224.3 | 295.2 | 30 | 36.1 | 233.9 | 16.1 | 27 | 40.4 | 61.6 | 182.4 | 203 | 44.8 | 148.6 | 34 | 132.7 | 123.9 | 38 | 58.4 | 41.9 | 36.6
523 | 284 | 295.1 | 118.04 | 137.982 | 121.1 | 135.8 | 139.4 | 115.5 | 197.1 | 19.5 | 21.1 | 35.7 | 3 | 248.2 | 8.6 | 89 | 245.4 | 685.4 | 129.9 | 147.8 | 640.8 | 111.9 | 222.7 | 295.8 | 30.1 | 36.3 | 234.3 | 16.1 | 27 | 40.5 | 61.8 | 182.2 | 202 | 44.8 | 148.3 | 34.1 | 132.7 | 124.1 | 38.1 | 58.5 | 42 | 36.7
524 | 285 | 294.9 | 117.96 | 137.8884 | 121.3 | 135.6 | 139.5 | 115.6 | 197.2 | 19.5 | 21.1 | 35.8 | 2.8 | 259.4 | 7.7 | 89.3 | 246 | 680.9 | 130.4 | 148.1 | 639.8 | 112.1 | 224.3 | 303.2 | 30.3 | 36.4 | 236.4 | 16.1 | 27.1 | 40.7 | 62 | 182.3 | 203 | 45.2 | 148.6 | 34.1 | 132.7 | 124.8 | 38.2 | 58.6 | 42.2 | 36.8
525 | 286 | 295.5 | 118.2 | 138.169 | 121.5 | 135.5 | 139.5 | 115.8 | 198.6 | 19.5 | 21.1 | 35.8 | 2.4 | 259.7 | 7.4 | 89.5 | 245 | 681.9 | 130.9 | 148.3 | 638.5 | 112.4 | 223.6 | 300.5 | 30.4 | 36.5 | 235.7 | 16.2 | 27.2 | 40.7 | 62.2 | 182.1 | 202.7 | 45.3 | 149.2 | 34.2 | 132.9 | 124.9 | 38.3 | 58.8 | 42.3 | 36.9
526 | 287 | 295.2 | 118.08 | 138.0287 | 122 | 136.1 | 139.6 | 115.8 | 199 | 19.5 | 21.1 | 35.8 | 2.3 | 249.2 | 8.3 | 89.8 | 243.1 | 695.7 | 131.3 | 148.6 | 637.3 | 112.6 | 224.3 | 303.4 | 30.5 | 36.6 | 236.2 | 16.2 | 27.3 | 41 | 62.4 | 182.3 | 203.7 | 45.3 | 150.1 | 34.3 | 133.3 | 125.2 | 38.4 | 58.9 | 42.4 | 37
527 | 288 | 295.3 | 118.12 | 138.0755 | 122 | 136.1 | 140 | 115.8 | 199.8 | 19.6 | 21.1 | 35.8 | 2.6 | 235.2 | 9.4 | 90.1 | 243.1 | 696 | 131.8 | 148.9 | 636.9 | 112.9 | 224.6 | 304.7 | 30.6 | 36.7 | 235.9 | 16.2 | 27.3 | 41.1 | 62.5 | 182.1 | 203.5 | 45.6 | 150.3 | 34.4 | 133.6 | 125.1 | 38.5 | 59.1 | 42.6 | 37.1
528 | 289 | 294.9 | 117.96 | 137.8884 | 122.1 | 136.2 | 140.2 | 116.1 | 199.8 | 19.6 | 21.1 | 35.9 | 2.5 | 228.6 | 9.3 | 90.4 | 243.2 | 684.8 | 132.3 | 149.1 | 636.1 | 113.2 | 223.6 | 300.6 | 30.7 | 36.9 | 235.1 | 16.2 | 27.4 | 41.2 | 62.7 | 181.9 | 202.8 | 45.5 | 150.3 | 34.5 | 133.8 | 124.9 | 38.6 | 59.3 | 42.7 | 37.2
529 | 290 | 294.6 | 117.84 | 137.7482 | 122 | 136.1 | 140.5 | 116.4 | 199.5 | 19.6 | 21.1 | 35.9 | 2.3 | 242.3 | 9.8 | 90.6 | 241.5 | 689.7 | 132.7 | 149.4 | 634.1 | 113.5 | 223.2 | 300.4 | 30.8 | 37 | 235.5 | 16.3 | 27.5 | 41.3 | 62.9 | 181.5 | 204.4 | 45.8 | 151 | 34.5 | 133.9 | 124.7 | 38.7 | 59.4 | 42.8 | 37.3
530 | 291 | 294.2 | 117.68 | 137.5611 | 122.4 | 136.4 | 141 | 116.7 | 198.2 | 19.6 | 21.1 | 35.9 | 2.6 | 243.6 | 10.5 | 90.9 | 238.9 | 700.5 | 133.2 | 149.6 | 633.3 | 113.7 | 221.7 | 296.9 | 30.9 | 37.1 | 234.6 | 16.3 | 27.5 | 41.4 | 63 | 180.5 | 202.3 | 45.5 | 150.9 | 34.6 | 133.8 | 124.9 | 38.7 | 59.6 | 43 | 37.4
531 | 292 | 294.2 | 117.68 | 137.5611 | 122.8 | 136.6 | 141.5 | 116.9 | 197.7 | 19.6 | 21.1 | 36 | 3.1 | 233.8 | 11.2 | 91.2 | 237.8 | 707.7 | 133.7 | 149.9 | 633.7 | 114.1 | 222.7 | 298.9 | 31 | 37.2 | 234.3 | 16.3 | 27.6 | 41.5 | 63.2 | 180.9 | 205.3 | 46 | 150.7 | 34.7 | 134.1 | 125.3 | 38.9 | 59.7 | 43.1 | 37.5
532 | 293 | 294.2 | 117.68 | 137.5611 | 122.9 | 136.5 | 141.7 | 117.2 | 199.1 | 19.7 | 21.1 | 36.1 | 3.4 | 232.4 | 10.2 | 91.4 | 239.2 | 712.1 | 134.1 | 150.2 | 634.5 | 114.4 | 221.9 | 294.4 | 31.1 | 37.3 | 233.7 | 16.3 | 27.7 | 41.5 | 63.4 | 181.5 | 204.8 | 46.2 | 151 | 34.8 | 134.5 | 125.7 | 38.9 | 59.9 | 43.2 | 37.6
533 | 294 | 294.5 | 117.8 | 137.7014 | 122.6 | 136.7 | 141.8 | 117.4 | 199.5 | 19.7 | 21.1 | 36.1 | 3.4 | 205.9 | 8.1 | 91.6 | 240.5 | 714 | 134.6 | 150.4 | 635.2 | 114.7 | 222.5 | 298 | 31.3 | 37.5 | 233.8 | 16.4 | 27.8 | 41.8 | 63.6 | 181.9 | 204.7 | 46.3 | 151.4 | 34.9 | 134.9 | 126.1 | 39 | 60.1 | 43.4 | 37.7
534 | 295 | 293.9 | 117.56 | 137.4209 | 122.3 | 137.2 | 141.8 | 117.6 | 200.4 | 19.7 | 21.1 | 36.2 | 3.4 | 243.2 | 6.8 | 91.9 | 242.1 | 697.4 | 135.1 | 150.7 | 635.4 | 115 | 222.9 | 298.1 | 31.4 | 37.6 | 233.9 | 16.4 | 27.9 | 41.8 | 63.7 | 182.2 | 205.3 | 46.3 | 151.6 | 35 | 135.2 | 126.4 | 39.1 | 60.3 | 43.5 | 37.8
535 | 296 | 294.8 | 117.92 | 137.8417 | 122.3 | 137.5 | 141.8 | 117.7 | 200.6 | 19.8 | 21.1 | 36.2 | 2.8 | 244.3 | 7.5 | 92.1 | 244.6 | 703.5 | 135.5 | 151 | 635.1 | 115.3 | 223.8 | 301 | 31.5 | 37.7 | 234.3 | 16.4 | 28 | 42 | 63.9 | 182.1 | 205.1 | 46.1 | 151.8 | 35 | 135.3 | 126.7 | 39.1 | 60.4 | 43.6 | 37.9
536 | 297 | 296.1 | 118.44 | 138.4495 | 122.8 | 137.8 | 142.1 | 117.5 | 201.2 | 19.8 | 21.1 | 36.3 | 2.8 | 250.1 | 7.9 | 92.3 | 245.4 | 701.4 | 136 | 151.2 | 635.5 | 115.6 | 224.7 | 302.5 | 31.6 | 37.8 | 235.7 | 16.5 | 28 | 42 | 64.1 | 182.4 | 205.2 | 46.4 | 152.4 | 35.1 | 135.4 | 126.7 | 39.2 | 60.6 | 43.8 | 38
537 | 298 | 296.2 | 118.48 | 138.4963 | 123 | 137.6 | 142.1 | 117.2 | 202.2 | 19.8 | 21.1 | 36.3 | 3.2 | 254.1 | 8.3 | 92.6 | 246.3 | 706.3 | 136.4 | 151.5 | 635.2 | 115.9 | 223.5 | 298.1 | 31.7 | 37.9 | 235.6 | 16.5 | 28.1 | 42 | 64.3 | 182.6 | 204.8 | 46.4 | 152.5 | 35.2 | 135.4 | 126.5 | 39.3 | 60.7 | 44 | 38.1
538 | 299 | 293.5 | 117.4 | 137.2338 | 123.1 | 137.8 | 141.9 | 117.1 | 202.2 | 19.9 | 21.1 | 36.4 | 4.1 | 253.3 | 8.5 | 92.8 | 247.4 | 705.5 | 136.9 | 151.8 | 635.3 | 116.2 | 223.2 | 295.8 | 31.8 | 38.1 | 235.5 | 16.5 | 28.2 | 42.2 | 64.4 | 183.2 | 206.3 | 46.8 | 152.7 | 35.3 | 135.5 | 126.4 | 39.4 | 60.8 | 44.1 | 38.2
539 | 300 | 293.6 | 117.44 | 137.2806 | 123.4 | 137.8 | 141.4 | 117.1 | 202.2 | 19.9 | 21.1 | 36.5 | 4 | 247.2 | 9.8 | 93 | 248 | 701.2 | 137.3 | 152.1 | 636.3 | 116.5 | 221.6 | 292.3 | 31.9 | 38.2 | 235.7 | 16.5 | 28.2 | 42.3 | 64.6 | 183.6 | 205.7 | 46.9 | 152.4 | 35.4 | 135.7 | 126.3 | 39.6 | 60.9 | 44.2 | 38.3
540 | 301 | 293.2 | 117.28 | 137.0936 | 123.1 | 138.1 | 141.3 | 117.3 | 201.6 | 19.9 | 21.1 | 36.6 | 3.3 | 220.7 | 9.8 | 93.2 | 252.9 | 695.2 | 137.7 | 152.4 | 638.1 | 116.8 | 224.9 | 300.5 | 32.1 | 38.3 | 238.1 | 16.6 | 28.3 | 42.5 | 64.8 | 183.7 | 205.3 | 47 | 152.3 | 35.4 | 136 | 126.3 | 39.7 | 61 | 44.4 | 38.4
541 | 302 | 293.7 | 117.48 | 137.3274 | 123.2 | 138.2 | 141.2 | 117.6 | 201.1 | 20 | 21.1 | 36.6 | 2.8 | 244.4 | 10.7 | 93.4 | 256.2 | 687.1 | 138.1 | 152.7 | 639.2 | 117.1 | 227.6 | 303.9 | 32.2 | 38.4 | 238.9 | 16.6 | 28.4 | 42.6 | 64.9 | 184.4 | 205.4 | 47 | 153.2 | 35.5 | 136 | 126.3 | 39.8 | 61.1 | 44.5 | 38.5
542 | 303 | 295.4 | 118.16 | 138.1222 | 123.3 | 138.6 | 141.1 | 117.9 | 200.9 | 20 | 21.1 | 36.7 | 3.4 | 242.7 | 13.1 | 93.6 | 259.1 | 692.1 | 138.6 | 153 | 641.9 | 117.4 | 230.1 | 305.2 | 32.3 | 38.5 | 240.3 | 16.6 | 28.4 | 42.7 | 65.1 | 185.3 | 205.7 | 47.1 | 154.1 | 35.6 | 136.1 | 126.3 | 39.9 | 61.3 | 44.6 | 38.6
543 | 304 | 292.1 | 116.84 | 136.5792 | 123.5 | 139.2 | 140.6 | 118.2 | 201.5 | 20.1 | 21.1 | 36.8 | 3 | 233.4 | 11.9 | 93.8 | 259 | 692.7 | 139 | 153.3 | 643.8 | 117.7 | 230.8 | 306.8 | 32.4 | 38.7 | 240.5 | 16.6 | 28.5 | 42.8 | 65.3 | 186.2 | 206.1 | 47.3 | 154.6 | 35.7 | 136.1 | 126.5 | 39.9 | 61.3 | 44.8 | 38.7
544 | 305 | 291.7 | 116.68 | 136.3922 | 124.3 | 139 | 140.3 | 118.3 | 202 | 20.1 | 21.1 | 36.8 | 2.9 | 261.5 | 11.2 | 94 | 258.9 | 678.6 | 139.4 | 153.7 | 644.1 | 117.9 | 231.1 | 307.3 | 32.5 | 38.8 | 240.7 | 16.7 | 28.6 | 43 | 65.5 | 186.5 | 206.3 | 47.8 | 155.4 | 35.8 | 136.2 | 126.5 | 40 | 61.4 | 44.9 | 38.8
545 | 306 | 290.8 | 116.32 | 135.9714 | 124.7 | 138.9 | 140.1 | 118.5 | 202 | 20.2 | 21.1 | 36.8 | 2.5 | 254.5 | 12.1 | 94.2 | 258.5 | 681.9 | 139.8 | 154 | 643.4 | 118.2 | 229.7 | 305.9 | 32.6 | 38.9 | 240.7 | 16.7 | 28.7 | 43 | 65.6 | 186.7 | 206 | 48 | 155.1 | 35.9 | 136.3 | 126.6 | 40.2 | 61.5 | 45.1 | 38.9
546 | 307 | 291 | 116.4 | 136.0649 | 124.6 | 138.6 | 140 | 118.6 | 202.9 | 20.2 | 21.1 | 36.9 | 3.2 | 245 | 11.7 | 94.4 | 259.3 | 678.5 | 140.3 | 154.4 | 642.5 | 118.5 | 228.9 | 306.9 | 32.8 | 39.1 | 241.5 | 16.7 | 28.8 | 43.1 | 65.8 | 186.7 | 206.5 | 48.2 | 155 | 36 | 136.3 | 126.6 | 40.3 | 61.7 | 45.2 | 39
547 | 308 | 291.6 | 116.64 | 136.3454 | 124.4 | 138.6 | 140.3 | 118.5 | 201.9 | 20.2 | 21.1 | 36.9 | 3.3 | 249.5 | 11.7 | 94.6 | 260 | 686.5 | 140.7 | 154.7 | 642.3 | 118.8 | 229.4 | 305.6 | 32.9 | 39.2 | 241.9 | 16.8 | 28.9 | 43.3 | 66 | 186.1 | 205.2 | 47.9 | 154.7 | 36.1 | 136.4 | 126.8 | 40.3 | 61.9 | 45.4 | 39.1
548 | 309 | 291.8 | 116.72 | 136.439 | 123.9 | 139 | 140.4 | 118.3 | 202.1 | 20.2 | 21.1 | 36.9 | 3.2 | 242.1 | 11.3 | 94.8 | 262.7 | 701.9 | 141.1 | 155 | 643.3 | 119 | 230.4 | 307.2 | 33 | 39.3 | 243.3 | 16.8 | 29 | 43.4 | 66.2 | 186.7 | 206.5 | 48.1 | 155 | 36.2 | 136.6 | 127.2 | 40.4 | 62.1 | 45.5 | 39.2
549 | 310 | 291.3 | 116.52 | 136.2052 | 123.5 | 139.1 | 140.4 | 118.5 | 203.6 | 20.3 | 21.1 | 37 | 3.1 | 248.1 | 10.8 | 95 | 263.5 | 688.2 | 141.5 | 155.3 | 643.4 | 119.3 | 231.3 | 309.1 | 33.1 | 39.4 | 243.7 | 16.8 | 29.1 | 43.5 | 66.4 | 187 | 207 | 48.3 | 155.3 | 36.2 | 136.7 | 127.4 | 40.5 | 62.2 | 45.6 | 39.3
550 | 311 | 292.3 | 116.92 | 136.6727 | 123.6 | 139.1 | 140.5 | 118.7 | 203.3 | 20.4 | 21.1 | 37 | 3.3 | 242.8 | 9.3 | 95.2 | 263.3 | 687.9 | 141.9 | 155.7 | 641.9 | 119.6 | 231.3 | 310 | 33.2 | 39.6 | 243.2 | 16.9 | 29.2 | 43.5 | 66.5 | 187.1 | 207.2 | 48.6 | 155.4 | 36.3 | 136.6 | 127.3 | 40.6 | 62.2 | 45.8 | 39.4
551 | 312 | 293.7 | 117.48 | 137.3274 | 123.8 | 138.8 | 140.8 | 119 | 203.8 | 20.4 | 21.1 | 37.1 | 3.5 | 244.2 | 8.7 | 95.4 | 262 | 691.5 | 142.3 | 156 | 640.5 | 119.9 | 229 | 307.2 | 33.3 | 39.7 | 242.7 | 16.9 | 29.3 | 43.7 | 66.7 | 187.5 | 208.3 | 49.2 | 156.2 | 36.4 | 136.7 | 127.2 | 40.7 | 62.3 | 45.9 | 39.5
552 | 313 | 297 | 118.8 | 138.8704 | 124.1 | 138.4 | 141.3 | 119 | 204.3 | 20.4 | 21.1 | 37.1 | 3.3 | 255.6 | 8.3 | 95.5 | 260 | 697.2 | 142.7 | 156.3 | 639.3 | 120.1 | 228.5 | 305.5 | 33.5 | 39.8 | 242.6 | 16.9 | 29.4 | 43.9 | 66.9 | 187.1 | 208.7 | 49 | 156.6 | 36.5 | 136.7 | 127.3 | 40.8 | 62.4 | 46.1 | 39.6
553 | 314 | 309.3 | 123.72 | 144.6216 | 124.5 | 139.3 | 141.8 | 118.9 | 205.6 | 20.4 | 21.1 | 37.1 | 3 | 243.1 | 6.5 | 95.7 | 258.5 | 721.8 | 143.1 | 156.7 | 639.4 | 120.4 | 227.5 | 303.6 | 33.6 | 39.9 | 242 | 17 | 29.5 | 43.9 | 67.1 | 187.3 | 208.2 | 49.2 | 157 | 36.6 | 136.6 | 127.6 | 40.8 | 62.4 | 46.2 | 39.6
554 | 315 | 331.8 | 132.72 | 155.142 | 124.4 | 139.6 | 141.9 | 118.8 | 206.1 | 20.5 | 21.1 | 37.2 | 3.3 | 203.7 | 5.4 | 95.9 | 258.9 | 736.2 | 143.5 | 157 | 641 | 120.7 | 227.9 | 304.4 | 33.7 | 40.1 | 242 | 17 | 29.6 | 44 | 67.3 | 187.6 | 208.4 | 49.5 | 157.2 | 36.7 | 136.7 | 127.7 | 40.9 | 62.5 | 46.3 | 39.7
555 | 316 | 346.7 | 138.68 | 162.1089 | 123.9 | 139.9 | 141.6 | 118.8 | 206.5 | 20.5 | 21.1 | 37.2 | 2.5 | 220.9 | 5.6 | 96.1 | 261.6 | 751.4 | 144 | 157.3 | 643.3 | 120.9 | 229.5 | 306 | 33.8 | 40.2 | 243.2 | 17 | 29.6 | 44.1 | 67.4 | 188.2 | 208.4 | 49.5 | 157.7 | 36.7 | 136.8 | 127.9 | 41 | 62.6 | 46.4 | 39.8
556 | 317 | 353.1 | 141.24 | 165.1014 | 124 | 140.5 | 141.3 | 118.8 | 207.5 | 20.5 | 21.1 | 37.3 | 1.9 | 239.5 | 5.6 | 96.4 | 266.1 | 755.1 | 144.4 | 157.6 | 645.4 | 121.2 | 232 | 310.7 | 33.9 | 40.3 | 245.4 | 17.1 | 29.7 | 44.3 | 67.6 | 189.4 | 210.9 | 49.8 | 158 | 36.8 | 136.8 | 128.3 | 41.1 | 62.7 | 46.6 | 39.9
557 | 318 | 354.8 | 141.92 | 165.8963 | 124.1 | 140.5 | 141.5 | 119.1 | 210.5 | 20.6 | 21.1 | 37.3 | 2.1 | 214.5 | 5.5 | 96.6 | 270.5 | 746.2 | 144.8 | 157.9 | 646.6 | 121.5 | 233.3 | 312.9 | 34.1 | 40.4 | 245.9 | 17.1 | 29.8 | 44.5 | 67.8 | 190.5 | 212.2 | 49.8 | 159.1 | 36.9 | 136.9 | 128.6 | 41.2 | 62.8 | 46.7 | 40
558 | 319 | 357.3 | 142.92 | 167.0652 | 124.7 | 140.6 | 141.8 | 119.2 | 214.5 | 20.6 | 21.1 | 37.4 | 2.9 | 242.5 | 4.9 | 96.8 | 270.6 | 741.6 | 145.2 | 158.3 | 647.3 | 121.8 | 235.8 | 317.8 | 34.2 | 40.6 | 246.2 | 17.1 | 29.8 | 44.5 | 68 | 193.1 | 223.1 | 50.4 | 161.2 | 37 | 137.1 | 128.4 | 41.3 | 62.9 | 46.9 | 40.1
559 | 320 | 358.5 | 143.4 | 167.6263 | 125.2 | 141.3 | 142.5 | 119.4 | 219.2 | 20.6 | 21.1 | 37.5 | 3.4 | 269.2 | 4.3 | 97 | 270.1 | 735.7 | 145.6 | 158.6 | 647.7 | 122.1 | 236.2 | 319.5 | 34.3 | 40.7 | 247.6 | 17.1 | 29.9 | 44.8 | 68.2 | 193.9 | 225.4 | 50.3 | 163.2 | 37.1 | 137.3 | 128.4 | 41.5 | 63 | 47.1 | 40.2
560 | 321 | 358.7 | 143.48 | 167.7199 | 125.7 | 141.5 | 143.4 | 119.7 | 219.3 | 20.6 | 21.1 | 37.5 | 4.1 | 231.9 | 4.3 | 97.3 | 268.7 | 742 | 146 | 158.9 | 647.8 | 122.3 | 235.3 | 318.6 | 34.4 | 40.8 | 248 | 17.2 | 30 | 44.9 | 68.4 | 194 | 226.6 | 50.8 | 162.6 | 37.2 | 137.4 | 128.4 | 41.7 | 63.1 | 47.2 | 40.3
561 | 322 | 359.4 | 143.76 | 168.0472 | 126.3 | 141.5 | 143.9 | 119.8 | 219.7 | 20.7 | 21.1 | 37.6 | 3.6 | 213.6 | 4.8 | 97.5 | 269.4 | 740.5 | 146.5 | 159.3 | 649 | 122.7 | 235.4 | 320.3 | 34.5 | 40.9 | 249.6 | 17.2 | 30.1 | 44.9 | 68.6 | 194.5 | 227.1 | 51.2 | 162.6 | 37.3 | 138 | 128.6 | 41.8 | 63.2 | 47.4 | 40.4
562 | 323 | 359.1 | 143.64 | 167.9069 | 127 | 141.2 | 144.4 | 120.3 | 221.3 | 20.7 | 21.1 | 37.7 | 2.6 | 235.9 | 5.4 | 97.7 | 272.2 | 745.3 | 146.9 | 159.6 | 651.1 | 123 | 236 | 322.1 | 34.6 | 41.1 | 249.8 | 17.2 | 30.1 | 45.2 | 68.8 | 195.8 | 229.5 | 51.5 | 162.9 | 37.3 | 138.4 | 128.9 | 41.9 | 63.3 | 47.5 | 40.5
563 | 324 | 359.3 | 143.72 | 168.0004 | 127.7 | 141.6 | 145.3 | 121 | 223 | 20.7 | 21.1 | 37.7 | 2.9 | 238 | 5.4 | 97.9 | 274.7 | 748 | 147.3 | 159.9 | 653.9 | 123.3 | 236.7 | 324.8 | 34.8 | 41.2 | 250.7 | 17.3 | 30.2 | 45.3 | 69 | 196.7 | 228.7 | 51.4 | 163 | 37.4 | 138.7 | 129 | 42.1 | 63.5 | 47.7 | 40.6
564 | 325 | 361.4 | 144.56 | 168.9823 | 128.3 | 142.1 | 146.2 | 121.9 | 222.3 | 20.8 | 21.1 | 37.8 | 3.2 | 229.8 | 6.2 | 98.1 | 275 | 753.4 | 147.7 | 160.2 | 655.8 | 123.7 | 235.7 | 319.4 | 34.9 | 41.3 | 251 | 17.3 | 30.3 | 45.5 | 69.2 | 197.5 | 228.1 | 51.3 | 162.7 | 37.5 | 139.1 | 129.3 | 42.2 | 63.7 | 47.8 | 40.7
565 | 326 | 360.7 | 144.28 | 168.655 | 128.9 | 143 | 146.9 | 122.4 | 221.4 | 20.8 | 21.1 | 37.9 | 3.9 | 219.4 | 7 | 98.3 | 278.9 | 763.3 | 148.1 | 160.5 | 657.1 | 124 | 236.3 | 323.2 | 35 | 41.5 | 252.2 | 17.3 | 30.4 | 45.5 | 69.3 | 198.1 | 227.1 | 51.3 | 163 | 37.6 | 139.7 | 129.9 | 42.4 | 63.8 | 48 | 40.8
566 | 327 | 361.6 | 144.64 | 169.0758 | 129.4 | 143.6 | 147.6 | 122.9 | 221.9 | 20.8 | 21.1 | 38.1 | 4.2 | 231.7 | 6.4 | 98.5 | 282.8 | 760 | 148.5 | 160.9 | 657.8 | 124.4 | 237.6 | 325 | 35.1 | 41.6 | 253.9 | 17.4 | 30.5 | 45.7 | 69.6 | 198.8 | 228 | 51.4 | 163.4 | 37.7 | 140.2 | 130.8 | 42.6 | 64 | 48.1 | 40.9
567 | 328 | 363.3 | 145.32 | 169.8707 | 130.1 | 145.1 | 147.9 | 123.4 | 223.5 | 20.9 | 21 | 38.2 | 3.9 | 214.8 | 7.4 | 98.7 | 284.2 | 753 | 149 | 161.2 | 658 | 124.8 | 238.9 | 328.3 | 35.2 | 41.7 | 256.2 | 17.4 | 30.6 | 45.9 | 69.8 | 199.4 | 230.4 | 51.6 | 163.8 | 37.9 | 140.8 | 131.5 | 42.7 | 64.3 | 48.3 | 41
568 | 329 | 364.3 | 145.72 | 170.3383 | 130.4 | 146.1 | 148.1 | 123.6 | 224.6 | 20.9 | 21 | 38.3 | 4.5 | 215.3 | 8.9 | 98.9 | 284.5 | 752.4 | 149.4 | 161.6 | 658.1 | 125.2 | 238.5 | 326.4 | 35.3 | 41.8 | 255.6 | 17.4 | 30.7 | 46 | 69.9 | 200 | 230.4 | 51.7 | 164.2 | 38 | 141.3 | 131.8 | 42.8 | 64.5 | 48.5 | 41.2
569 | 330 | 365 | 146 | 170.6656 | 130.6 | 147.1 | 148.9 | 123.6 | 224.2 | 20.9 | 21 | 38.4 | 3.8 | 239.1 | 9 | 99.1 | 290 | 753.1 | 149.8 | 162 | 658.9 | 125.6 | 242.1 | 335.5 | 35.5 | 42 | 257.6 | 17.5 | 30.8 | 46.1 | 70.1 | 200.3 | 232.6 | 51.9 | 164.3 | 38.1 | 141.6 | 132.7 | 42.9 | 64.8 | 48.6 | 41.3
570 | 331 | 365.9 | 146.36 | 171.0864 | 130.8 | 148.3 | 149.6 | 123.8 | 226 | 20.9 | 21 | 38.5 | 3.6 | 212.5 | 8.2 | 99.3 | 294.6 | 757.8 | 150.3 | 162.3 | 660.1 | 126.1 | 245.9 | 340.9 | 35.6 | 42.1 | 260.2 | 17.5 | 30.9 | 46.2 | 70.3 | 201.9 | 234.4 | 52.2 | 165.6 | 38.2 | 142 | 133.2 | 43 | 65 | 48.8 | 41.4
571 | 332 | 367.2 | 146.88 | 171.6943 | 131.1 | 149.9 | 150.4 | 124.2 | 227.7 | 21 | 21 | 38.6 | 3.2 | 224 | 7.9 | 99.6 | 305.3 | 763.8 | 150.7 | 162.7 | 661.9 | 126.5 | 250 | 348 | 35.7 | 42.2 | 263.7 | 17.5 | 31 | 46.4 | 70.5 | 203.6 | 237 | 52.5 | 166.3 | 38.3 | 142.2 | 133.5 | 43.1 | 65.1 | 48.9 | 41.5
572 | 333 | 368.5 | 147.4 | 172.3021 | 131.3 | 150.7 | 150.8 | 124.8 | 235 | 21.1 | 21 | 38.7 | 3.2 | 214.1 | 8 | 99.8 | 316.5 | 765.1 | 151.1 | 163 | 663.7 | 126.9 | 255.8 | 361 | 35.8 | 42.3 | 265.3 | 17.6 | 31.1 | 46.6 | 70.7 | 207.1 | 242.5 | 53.2 | 168.7 | 38.4 | 142.6 | 133.8 | 43.4 | 65.3 | 49.1 | 41.6
573 | 334 | 368.2 | 147.28 | 172.1618 | 131.8 | 150.8 | 151.4 | 125.3 | 239.5 | 21.1 | 21 | 38.9 | 3.7 | 219.4 | 9.3 | 100 | 318.4 | 760.4 | 151.5 | 163.4 | 665.1 | 127.4 | 259.4 | 370.7 | 35.9 | 42.5 | 267.4 | 17.6 | 31.2 | 46.7 | 70.9 | 209.5 | 245.6 | 53.4 | 170.1 | 38.5 | 143.3 | 134.2 | 43.5 | 65.4 | 49.3 | 41.7
574 | 335 | 369.6 | 147.84 | 172.8164 | 132.6 | 151.3 | 151.9 | 125.9 | 242.6 | 21.2 | 21 | 39 | 3.7 | 245.8 | 8.2 | 100.2 | 316.5 | 750.8 | 151.9 | 163.7 | 665.3 | 127.8 | 262.7 | 374.6 | 36.1 | 42.6 | 267.9 | 17.6 | 31.3 | 46.9 | 71.1 | 211 | 248.7 | 53.5 | 171.1 | 38.6 | 143.8 | 134.7 | 43.8 | 65.6 | 49.5 | 41.8
575 | 336 | 371.1 | 148.44 | 173.5178 | 133.2 | 151.6 | 152.5 | 126.4 | 247.6 | 21.2 | 21 | 39.2 | 2.9 | 239.4 | 8.4 | 100.5 | 315.6 | 746.3 | 152.4 | 164.1 | 664.2 | 128.3 | 267.7 | 382.8 | 36.2 | 42.7 | 268.8 | 17.7 | 31.4 | 47.1 | 71.3 | 213 | 253.2 | 53.9 | 172.8 | 38.7 | 144.3 | 135.4 | 43.8 | 65.8 | 49.7 | 41.9
576 | 337 | 371.1 | 148.44 | 173.5178 | 133.8 | 151.7 | 153.1 | 127 | 251.9 | 21.3 | 21 | 39.3 | 3.1 | 239.8 | 9.7 | 100.7 | 315.3 | 754.1 | 152.8 | 164.4 | 664.9 | 128.7 | 274.1 | 391.5 | 36.3 | 42.9 | 271.3 | 17.7 | 31.5 | 47.3 | 71.6 | 214.6 | 256.7 | 54.2 | 173.9 | 38.8 | 144.8 | 135.6 | 44 | 66 | 49.9 | 42
577 | 338 | 372.1 | 148.84 | 173.9854 | 134.2 | 151.9 | 153.7 | 127.6 | 255 | 21.3 | 21 | 39.4 | 3.6 | 229.1 | 9.1 | 100.9 | 317.1 | 765.4 | 153.2 | 164.8 | 666.2 | 129.2 | 280.7 | 409.6 | 36.5 | 43 | 275.4 | 17.7 | 31.6 | 47.4 | 71.8 | 217.3 | 259.6 | 54.7 | 175.5 | 38.9 | 145.4 | 135.7 | 44.1 | 66.2 | 50.1 | 42.2
578 | 339 | 372.1 | 148.84 | 173.9854 | 134.7 | 152.6 | 154.4 | 128.4 | 260.6 | 21.3 | 21 | 39.5 | 3.6 | 217.1 | 7.6 | 101.2 | 315.2 | 765.7 | 153.6 | 165.2 | 667.4 | 129.7 | 283.9 | 412.7 | 36.6 | 43.1 | 276.2 | 17.8 | 31.7 | 47.6 | 72 | 219.8 | 268.4 | 55.6 | 177.3 | 39 | 146.1 | 136.1 | 44.2 | 66.4 | 50.3 | 42.3
579 | 340 | 371.6 | 148.64 | 173.7516 | 135.4 | 153.6 | 155.3 | 128.9 | 268 | 21.4 | 21 | 39.6 | 3.8 | 211.8 | 8.2 | 101.4 | 313.1 | 779.1 | 154 | 165.5 | 669 | 130.1 | 287.1 | 418.5 | 36.7 | 43.3 | 277 | 17.8 | 31.8 | 47.9 | 72.2 | 221.8 | 270.8 | 55.9 | 179.6 | 39.1 | 146.7 | 137.1 | 44.4 | 66.6 | 50.5 | 42.4
580 | 341 | 372.9 | 149.16 | 174.3594 | 136.7 | 153.9 | 156.6 | 129.6 | 268.8 | 21.4 | 21 | 39.8 | 3.5 | 211.4 | 10.5 | 101.6 | 315.5 | 791.1 | 154.4 | 165.9 | 671.5 | 130.6 | 289.2 | 424.4 | 36.9 | 43.4 | 278.1 | 17.8 | 31.8 | 48 | 72.4 | 222.7 | 270.9 | 55.8 | 180.1 | 39.2 | 147.4 | 137.5 | 44.5 | 66.9 | 50.7 | 42.5
581 | 342 | 375 | 150 | 175.3414 | 137.1 | 154.2 | 157.6 | 130.3 | 271.3 | 21.4 | 21 | 39.9 | 3.2 | 219.6 | 10.8 | 101.9 | 319 | 798.4 | 154.8 | 166.3 | 674.3 | 131.1 | 294.3 | 438.1 | 37 | 43.6 | 281.5 | 17.9 | 31.9 | 48.2 | 72.7 | 225.3 | 276.7 | 56.1 | 180.6 | 39.3 | 148.2 | 137.9 | 44.7 | 67 | 51 | 42.6
582 | 343 | 374.9 | 149.96 | 175.2946 | 137.6 | 154.5 | 158.2 | 131 | 275.6 | 21.5 | 21 | 40 | 3.3 | 211.3 | 10.6 | 102.1 | 324.4 | 798.5 | 155.2 | 166.7 | 676.3 | 131.6 | 297.3 | 442.1 | 37.2 | 43.7 | 284.4 | 17.9 | 32 | 48.2 | 72.9 | 227.8 | 278.1 | 56.2 | 181.9 | 39.4 | 149 | 138.6 | 44.8 | 67.3 | 51.2 | 42.8
583 | 344 | 373.9 | 149.56 | 174.827 | 138.3 | 155.3 | 158.9 | 132.1 | 275.7 | 21.5 | 21 | 40.1 | 2.9 | 215.5 | 10.1 | 102.3 | 333.8 | 789.5 | 155.6 | 167 | 678 | 132.1 | 300.2 | 444.6 | 37.3 | 43.8 | 287.9 | 17.9 | 32.1 | 48.4 | 73.2 | 230.4 | 279.5 | 56.4 | 182.4 | 39.5 | 149.6 | 139.5 | 45 | 67.5 | 51.4 | 42.9
584 | 345 | 375 | 150 | 175.3414 | 139.1 | 157.5 | 159.2 | 133.1 | 274.2 | 21.6 | 21 | 40.2 | 3.2 | 225.5 | 9.5 | 102.6 | 339.2 | 791.3 | 156 | 167.4 | 679.5 | 132.6 | 303.2 | 452.2 | 37.4 | 44 | 291.7 | 18 | 32.2 | 48.7 | 73.4 | 232.6 | 279 | 56.6 | 183.2 | 39.6 | 150.3 | 140.1 | 45.3 | 67.7 | 51.7 | 43
585 | 346 | 377.2 | 150.88 | 176.37 | 139.9 | 158.4 | 159.4 | 134 | 271 | 21.7 | 21 | 40.4 | 4.1 | 216.9 | 8.8 | 102.8 | 342.4 | 779.9 | 156.4 | 167.8 | 681.9 | 133.1 | 303.9 | 449.3 | 37.6 | 44.1 | 293.5 | 18 | 32.3 | 48.7 | 73.6 | 233.5 | 278.8 | 56.7 | 183.4 | 39.8 | 152.2 | 141.3 | 45.5 | 68 | 51.9 | 43.2
586 | 347 | 377 | 150.8 | 176.2765 | 141.1 | 158.6 | 159.6 | 135 | 268.3 | 21.7 | 21 | 40.5 | 4.2 | 213.4 | 9.2 | 103.1 | 343.2 | 784.3 | 156.8 | 168.1 | 684.8 | 133.6 | 302.9 | 442 | 37.7 | 44.3 | 293.4 | 18 | 32.4 | 48.9 | 73.9 | 233.9 | 277.4 | 56.7 | 183.3 | 39.9 | 153.2 | 142.4 | 45.8 | 68.3 | 52.2 | 43.4
587 | 348 | 377 | 150.8 | 176.2765 | 142.8 | 160.1 | 159.9 | 136.1 | 264.7 | 21.8 | 21 | 40.6 | 4.5 | 211 | 9.4 | 103.3 | 343.9 | 783.1 | 157.2 | 168.4 | 686.1 | 134.2 | 302.6 | 436.2 | 37.9 | 44.4 | 293.5 | 18.1 | 32.4 | 49 | 74.1 | 234.1 | 276.5 | 57.1 | 182.8 | 40 | 154.2 | 142.5 | 46 | 68.4 | 52.4 | 43.5
588 | 349 | 377.7 | 151.08 | 176.6038 | 143.7 | 161.5 | 160.1 | 136.9 | 264.2 | 21.9 | 21 | 40.7 | 4.5 | 195.6 | 9.8 | 103.6 | 345.6 | 797.1 | 157.6 | 168.8 | 687.2 | 134.7 | 302.7 | 439.5 | 38 | 44.6 | 295.1 | 18.1 | 32.5 | 49.1 | 74.4 | 234.7 | 276.4 | 57.2 | 183 | 40.2 | 155.2 | 142.9 | 46.3 | 68.6 | 52.6 | 43.7
589 | 350 | 377.2 | 150.88 | 176.37 | 144.9 | 162 | 160.2 | 137.7 | 267 | 21.9 | 21 | 40.8 | 4.5 | 193.6 | 10.7 | 103.8 | 353.3 | 796 | 157.9 | 169.2 | 688 | 135.2 | 306.2 | 445.8 | 38.2 | 44.7 | 298.1 | 18.1 | 32.6 | 49.2 | 74.7 | 236.6 | 278.7 | 57.7 | 184.3 | 40.3 | 156.2 | 143.6 | 46.6 | 68.9 | 52.8 | 43.8
590 | 351 | 378.8 | 151.52 | 177.1181 | 145.6 | 162.3 | 160.2 | 138.4 | 266.5 | 22 | 21 | 40.9 | 4 | 206.5 | 9.6 | 104.1 | 356.8 | 794.9 | 158.3 | 169.6 | 688.5 | 135.8 | 306.4 | 450.2 | 38.3 | 44.9 | 300.7 | 18.2 | 32.7 | 49.3 | 74.9 | 238.6 | 278.4 | 57.6 | 186 | 40.4 | 156.6 | 144.8 | 46.6 | 69.2 | 53.1 | 43.9
591 | 352 | 380.1 | 152.04 | 177.726 | 146 | 163.4 | 160.2 | 139 | 264.8 | 22 | 21 | 41 | 3.1 | 231.3 | 7.1 | 104.3 | 358.5 | 797.4 | 158.7 | 170 | 689.9 | 136.3 | 307.7 | 459 | 38.5 | 45.1 | 304.1 | 18.2 | 32.8 | 49.5 | 75.1 | 239.6 | 278.5 | 57.7 | 187.2 | 40.6 | 156.9 | 146.1 | 46.8 | 69.5 | 53.3 | 44.1
592 | 353 | 379.6 | 151.84 | 177.4922 | 146.1 | 163.7 | 160.1 | 139.8 | 266.3 | 22 | 21 | 41.1 | 2.8 | 201.9 | 6.1 | 104.6 | 358.7 | 790.2 | 159.1 | 170.4 | 691.5 | 136.9 | 308.5 | 458.7 | 38.6 | 45.2 | 306.5 | 18.2 | 32.9 | 49.7 | 75.4 | 241.4 | 280.3 | 58 | 188.2 | 40.7 | 157.5 | 147.1 | 46.9 | 69.6 | 53.6 | 44.2
593 | 354 | 378.3 | 151.32 | 176.8844 | 146.6 | 165.4 | 160 | 140.5 | 268.4 | 22 | 21 | 41.2 | 3.1 | 200.1 | 5.8 | 104.9 | 360.6 | 792 | 159.4 | 170.7 | 692.2 | 137.5 | 308.8 | 456.4 | 38.8 | 45.4 | 307.7 | 18.3 | 33 | 49.9 | 75.6 | 243.5 | 282.6 | 58.2 | 189.5 | 40.9 | 158 | 147.4 | 47 | 69.9 | 53.8 | 44.4
594 | 355 | 378.3 | 151.32 | 176.8844 | 147.2 | 167.4 | 160.5 | 140.9 | 270.3 | 22 | 21 | 41.3 | 3.6 | 212.6 | 6.2 | 105.2 | 361.3 | 790.2 | 159.8 | 171.1 | 691.8 | 138 | 306.9 | 452.3 | 38.9 | 45.5 | 307.1 | 18.3 | 33.1 | 50.1 | 75.9 | 243.2 | 280.4 | 57.9 | 190.2 | 41 | 158.6 | 147.4 | 47.2 | 70.2 | 54.1 | 44.5
595 | 356 | 380.7 | 152.28 | 178.0065 | 147.2 | 167.8 | 161.2 | 141.4 | 269.1 | 22.1 | 21 | 41.3 | 3.8 | 211.3 | 6.2 | 105.5 | 360.3 | 789.7 | 160.2 | 171.5 | 692.4 | 138.6 | 308.4 | 455.2 | 39.1 | 45.7 | 308.1 | 18.3 | 33.2 | 50.2 | 76.1 | 243.7 | 281.2 | 58.2 | 189.7 | 41.1 | 159.2 | 147.7 | 47.4 | 70.4 | 54.3 | 44.7
596 | 357 | 381.1 | 152.44 | 178.1936 | 147.4 | 167.2 | 162.1 | 141.5 | 270.8 | 22.1 | 21 | 41.4 | 4.3 | 206.8 | 10.9 | 105.8 | 361.4 | 790.9 | 160.6 | 171.9 | 693.2 | 139.2 | 311.7 | 463.8 | 39.2 | 45.9 | 310.8 | 18.4 | 33.3 | 50.4 | 76.4 | 246.4 | 285.2 | 59.3 | 190.8 | 41.3 | 160 | 148.2 | 47.5 | 70.7 | 54.5 | 44.8
597 | 358 | 380.7 | 152.28 | 178.0065 | 148 | 167.1 | 162.6 | 141.8 | 275.2 | 22.1 | 21 | 41.5 | 4.9 | 196.3 | 15.9 | 106 | 362.4 | 786.6 | 161 | 172.3 | 694 | 139.8 | 314 | 469.9 | 39.4 | 46 | 314.1 | 18.4 | 33.5 | 50.7 | 76.6 | 248.1 | 286.5 | 59.6 | 191.9 | 41.4 | 160.3 | 148.8 | 47.6 | 70.9 | 54.7 | 44.9
598 | 359 | 380.4 | 152.16 | 177.8663 | 148.4 | 166.8 | 163.3 | 142.4 | 275.4 | 22.1 | 21 | 41.6 | 4 | 197.8 | 17.1 | 106.4 | 362.6 | 767.4 | 161.3 | 172.7 | 694 | 140.4 | 313.1 | 467 | 39.5 | 46.2 | 315.4 | 18.5 | 33.6 | 50.8 | 76.9 | 248.5 | 285.4 | 59.7 | 191.7 | 41.5 | 160.7 | 148.7 | 47.7 | 71 | 55 | 45.1
599 | 360 | 381.1 | 152.44 | 178.1936 | 149.3 | 166.3 | 164 | 142.7 | 274.3 | 22.1 | 21 | 41.8 | 3.7 | 209.7 | 16.7 | 106.6 | 363.5 | 766.7 | 161.7 | 173.2 | 693.7 | 141 | 315 | 469.1 | 39.7 | 46.4 | 317.2 | 18.5 | 33.7 | 51 | 77.1 | 248.6 | 285.9 | 60 | 191.5 | 41.6 | 161 | 148.8 | 47.8 | 71.2 | 55.2 | 45.2
600 | 361 | 381.5 | 152.6 | 178.3806 | 149.7 | 166.4 | 164.7 | 143 | 277.2 | 22.1 | 21 | 41.9 | 3.7 | 209.7 | 15.7 | 106.9 | 362.5 | 764.1 | 162.1 | 173.7 | 694.1 | 141.6 | 314.7 | 465 | 39.8 | 46.5 | 317.1 | 18.5 | 33.8 | 51.3 | 77.4 | 249.4 | 286.7 | 60.2 | 193 | 41.8 | 161.6 | 149.1 | 47.9 | 71.3 | 55.4 | 45.3
601 | 362 | 380.3 | 152.12 | 177.8195 | 150.2 | 166.2 | 165.3 | 143.6 | 275.1 | 22.1 | 21 | 42 | 3.4 | 209.5 | 16.5 | 107.2 | 360.3 | 756.1 | 162.5 | 174.1 | 695.5 | 142.2 | 311.9 | 456.3 | 40 | 46.7 | 316.6 | 18.6 | 33.9 | 51.3 | 77.6 | 249 | 285.1 | 60.1 | 193 | 41.9 | 162.3 | 149.6 | 47.9 | 71.4 | 55.6 | 45.5
602 | 363 | 378.9 | 151.56 | 177.1649 | 150.6 | 166 | 165.8 | 144.5 | 272.2 | 22.2 | 21 | 42.2 | 3.2 | 214.2 | 16.3 | 107.6 | 364.9 | 755.4 | 162.9 | 174.6 | 697.5 | 142.8 | 310.9 | 453.6 | 40.1 | 46.9 | 316.6 | 18.6 | 34 | 51.5 | 77.9 | 248.3 | 282.7 | 59.9 | 192.5 | 42 | 162.8 | 150.6 | 48.1 | 71.6 | 55.8 | 45.6
603 | 364 | 380.5 | 152.2 | 177.913 | 150.8 | 165.9 | 166.1 | 144.8 | 269.6 | 22.2 | 21 | 42.3 | 2.9 | 212.6 | 16.1 | 107.9 | 371.6 | 772 | 163.4 | 175.2 | 699.5 | 143.5 | 311.7 | 460.9 | 40.3 | 47 | 320 | 18.7 | 34.1 | 51.6 | 78.1 | 248.2 | 283.8 | 60.2 | 192.8 | 42.1 | 163.3 | 151.6 | 48.2 | 71.9 | 56 | 45.7
604 | 365 | 381.3 | 152.52 | 178.2871 | 150.9 | 165.8 | 166.4 | 145.2 | 273.4 | 22.3 | 21 | 42.4 | 3.3 | 213.4 | 14.7 | 108.2 | 370 | 772.7 | 163.8 | 175.7 | 701.5 | 144.1 | 314.2 | 467.3 | 40.4 | 47.2 | 322.5 | 18.7 | 34.2 | 51.8 | 78.4 | 249.9 | 286 | 61 | 195.2 | 42.2 | 163.8 | 151.7 | 48.3 | 72.2 | 56.2 | 45.9
605 | 366 | 380.1 | 152.04 | 177.726 | 151.3 | 165.9 | 166.7 | 145.6 | 273.5 | 22.3 | 21 | 42.5 | 3 | 196.8 | 14.4 | 108.5 | 367.9 | 764 | 164.2 | 176.4 | 702.5 | 144.7 | 310.2 | 454.8 | 40.6 | 47.4 | 320.7 | 18.7 | 34.4 | 52 | 78.6 | 248.8 | 282.2 | 60.7 | 194.9 | 42.3 | 164.2 | 152.4 | 48.4 | 72.3 | 56.4 | 46
606 | 367 | 381.5 | 152.6 | 178.3806 | 151.6 | 166.1 | 167 | 146 | 270.5 | 22.4 | 21 | 42.5 | 3 | 194.9 | 12 | 108.8 | 366.8 | 769.2 | 164.6 | 177.1 | 705 | 145.4 | 308.4 | 449.9 | 40.7 | 47.5 | 321.1 | 18.8 | 34.5 | 52.2 | 78.9 | 247.9 | 282 | 60.8 | 194.4 | 42.4 | 164.7 | 152.8 | 48.5 | 72.6 | 56.6 | 46.2
607 | 368 | 381.2 | 152.48 | 178.2403 | 151.5 | 165.9 | 167.5 | 146.2 | 272.7 | 22.5 | 21 | 42.6 | 3.6 | 187.5 | 12.3 | 109.1 | 368.2 | 782 | 165 | 177.8 | 707.5 | 146 | 310.5 | 456.2 | 40.8 | 47.7 | 323.4 | 18.8 | 34.7 | 52.4 | 79.1 | 249.4 | 283.7 | 61.2 | 195.2 | 42.5 | 165.4 | 153.2 | 48.6 | 72.7 | 56.8 | 46.3
608 | 369 | 382 | 152.8 | 178.6144 | 151 | 165.3 | 167.9 | 146.5 | 274 | 22.5 | 21 | 42.7 | 3.5 | 195 | 13.5 | 109.5 | 370.2 | 786.1 | 165.4 | 178.3 | 709.7 | 146.7 | 314.4 | 465.2 | 41 | 47.9 | 327.2 | 18.9 | 34.8 | 52.5 | 79.4 | 250.6 | 286.1 | 61.8 | 196 | 42.6 | 166 | 153.9 | 48.8 | 73.1 | 57 | 46.5
609 | 370 | 381.6 | 152.64 | 178.4274 | 151.4 | 164.9 | 168.3 | 146.5 | 274.6 | 22.5 | 21 | 42.8 | 3.1 | 164.4 | 10.5 | 109.8 | 370.2 | 776.5 | 165.7 | 178.8 | 710.1 | 147.3 | 314.1 | 464 | 41.1 | 48.1 | 327.1 | 18.9 | 34.9 | 52.6 | 79.6 | 251.5 | 285.5 | 62.3 | 196.8 | 42.7 | 166.4 | 154.3 | 48.9 | 73.2 | 57.2 | 46.6
610 | 371 | 378.7 | 151.48 | 177.0714 | 152.3 | 165 | 168.8 | 146.6 | 274.6 | 22.5 | 21 | 42.8 | 3.1 | 174.7 | 8.2 | 110.2 | 370.3 | 785.1 | 166.1 | 179.5 | 711 | 148 | 312.7 | 457.2 | 41.3 | 48.2 | 327.3 | 18.9 | 35 | 52.8 | 79.9 | 251.1 | 284.8 | 62.3 | 197 | 42.8 | 166.5 | 154.9 | 49 | 73.4 | 57.4 | 46.8
611 | 372 | 378.9 | 151.56 | 177.1649 | 152.3 | 165.5 | 168.8 | 146.9 | 274.1 | 22.5 | 20.9 | 42.9 | 3.1 | 184.4 | 9.1 | 110.5 | 370.4 | 797.8 | 166.5 | 180.5 | 713.4 | 148.6 | 313.5 | 458.3 | 41.4 | 48.4 | 328.1 | 19 | 35.1 | 53 | 80.1 | 251 | 284.8 | 62.4 | 197 | 43 | 166.9 | 155.5 | 49.2 | 73.6 | 57.7 | 46.9
612 | 373 | 382.1 | 152.84 | 178.6612 | 151.9 | 166.1 | 169 | 147.2 | 273.2 | 22.6 | 20.9 | 43 | 2.7 | 161.8 | 11.9 | 110.8 | 371.5 | 801 | 166.8 | 181.4 | 715.7 | 149.3 | 313.5 | 457.3 | 41.6 | 48.6 | 328.7 | 19 | 35.2 | 53.1 | 80.4 | 251.3 | 286.9 | 62.7 | 197.9 | 43.1 | 167.3 | 155.9 | 49.3 | 73.8 | 57.9 | 47.1
613 | 374 | 381 | 152.4 | 178.1468 | 152 | 166.4 | 169.1 | 147.3 | 275.9 | 22.6 | 20.9 | 43.1 | 2.9 | 209.5 | 9 | 111.2 | 371.1 | 791.2 | 167.1 | 182.4 | 717.9 | 149.9 | 313.5 | 464.3 | 41.7 | 48.7 | 330 | 19.1 | 35.3 | 53.2 | 80.6 | 252.5 | 288.2 | 63 | 199.5 | 43.2 | 167.5 | 156.5 | 49.3 | 74 | 58.1 | 47.2
614 | 375 | 380.5 | 152.2 | 177.913 | 151.9 | 166.4 | 169.4 | 147.6 | 275.7 | 22.6 | 20.9 | 43.2 | 3.2 | 216.6 | 9.1 | 111.5 | 370.6 | 792.4 | 167.3 | 183 | 719.7 | 150.6 | 315.8 | 471.3 | 41.9 | 48.9 | 332.2 | 19.1 | 35.4 | 53.5 | 80.9 | 252.6 | 288.8 | 64.3 | 200 | 43.3 | 167.6 | 157.1 | 49.4 | 74.2 | 58.3 | 47.4
615 | 376 | 381.6 | 152.64 | 178.4274 | 152.3 | 166.2 | 169.7 | 147.9 | 275.6 | 22.7 | 20.9 | 43.3 | 2.9 | 194.8 | 12 | 111.9 | 369.7 | 806.6 | 167.5 | 183.9 | 721.5 | 151.2 | 315.8 | 467.3 | 42 | 49.1 | 332.6 | 19.1 | 35.5 | 53.6 | 81.1 | 253.2 | 289.2 | 66.6 | 200.7 | 43.4 | 167.8 | 157.4 | 49.5 | 74.4 | 58.5 | 47.5
616 | 377 | 382 | 152.8 | 178.6144 | 152.3 | 167 | 169.9 | 148.3 | 277.9 | 22.7 | 20.9 | 43.4 | 3.3 | 185.2 | 12.7 | 112.2 | 369.3 | 811.2 | 167.7 | 185 | 723.4 | 151.9 | 317.5 | 467.9 | 42.2 | 49.3 | 334 | 19.2 | 35.6 | 53.7 | 81.4 | 254.8 | 291.3 | 69.5 | 202.1 | 43.5 | 168.1 | 158.1 | 49.6 | 74.5 | 58.7 | 47.7
617 | 378 | 381.6 | 152.64 | 178.4274 | 152.3 | 166.9 | 170.5 | 148 | 281.4 | 22.8 | 20.9 | 43.5 | 3.4 | 203.2 | 10.7 | 112.6 | 368.2 | 805.7 | 167.9 | 186 | 724.9 | 152.6 | 318.1 | 469.8 | 42.3 | 49.4 | 335.4 | 19.2 | 35.6 | 53.8 | 81.7 | 256 | 294.3 | 71.1 | 203.6 | 43.6 | 168.3 | 158.6 | 49.8 | 74.7 | 58.9 | 47.8
618 | 379 | 381.6 | 152.64 | 178.4274 | 152.6 | 167.2 | 171.2 | 148.2 | 284.5 | 22.8 | 20.9 | 43.5 | 3.2 | 213.4 | 8.7 | 112.9 | 367.8 | 801.3 | 168.1 | 187.2 | 725.8 | 153.3 | 318.3 | 469.6 | 42.5 | 49.6 | 337.3 | 19.3 | 35.7 | 54.3 | 81.9 | 256.8 | 296.5 | 72.1 | 205 | 43.7 | 168.4 | 158.5 | 49.9 | 75 | 59.1 | 48
619 | 380 | 381.2 | 152.48 | 178.2403 | 153.1 | 167.5 | 171.7 | 148.5 | 285.1 | 22.9 | 20.9 | 43.6 | 3.4 | 190.5 | 10.5 | 113.3 | 365.6 | 796.4 | 168.3 | 188.3 | 725.8 | 153.9 | 316.4 | 466.4 | 42.6 | 49.8 | 338.8 | 19.3 | 35.8 | 54.5 | 82.2 | 257.5 | 296.8 | 72.7 | 206.3 | 43.8 | 168.7 | 158.9 | 50 | 75.2 | 59.4 | 48.1
620 | 381 | 380.7 | 152.28 | 178.0065 | 153.4 | 167.6 | 172.5 | 148.6 | 284.4 | 23 | 20.9 | 43.6 | 3.4 | 200.8 | 12.3 | 113.6 | 365.2 | 783.6 | 168.4 | 189.1 | 725.5 | 154.6 | 315.8 | 461.5 | 42.8 | 49.9 | 338.9 | 19.3 | 35.9 | 54.6 | 82.5 | 257.5 | 297.7 | 73.2 | 206.3 | 43.9 | 169.1 | 159.6 | 50.2 | 75.4 | 59.6 | 48.2
621 | 382 | 377.6 | 151.04 | 176.5571 | 154 | 168.5 | 173.6 | 148.9 | 283.5 | 23.1 | 20.9 | 43.7 | 3.1 | 195.3 | 12 | 113.9 | 365.6 | 772.5 | 168.6 | 189.8 | 724.7 | 155.2 | 313.1 | 453.5 | 42.9 | 50.1 | 338.6 | 19.4 | 36 | 54.7 | 82.8 | 256.8 | 296 | 73.1 | 205.7 | 44 | 169.7 | 159.6 | 50.4 | 75.6 | 59.8 | 48.4
622 | 383 | 379.3 | 151.72 | 177.3519 | 155.1 | 169.6 | 174.4 | 149.1 | 282.2 | 23.1 | 20.9 | 43.7 | 2.9 | 186.6 | 11.4 | 114.3 | 365.8 | 769.9 | 168.7 | 190.2 | 724 | 155.9 | 311.4 | 449.7 | 43.1 | 50.3 | 339.3 | 19.4 | 36.1 | 55.2 | 83.1 | 257 | 300.1 | 74.8 | 205.8 | 44.1 | 170.8 | 160.1 | 50.5 | 75.7 | 60 | 48.5
623 | 384 | 379.8 | 151.92 | 177.5857 | 156.2 | 170.5 | 175.3 | 149.4 | 282.4 | 23.1 | 20.9 | 43.8 | 3.9 | 191.9 | 12.2 | 114.5 | 367.5 | 766.3 | 168.9 | 190.9 | 723.3 | 156.6 | 311.3 | 450.9 | 43.2 | 50.4 | 340.5 | 19.5 | 36.2 | 55.4 | 83.5 | 256.6 | 300.3 | 75.6 | 206.9 | 44.2 | 171.3 | 160.7 | 50.5 | 76 | 60.2 | 48.7
624 | 385 | 381.2 | 152.48 | 178.2403 | 156.1 | 170.7 | 176.5 | 149.8 | 283.6 | 23.1 | 20.9 | 43.9 | 3.8 | 195.5 | 14.8 | 114.9 | 370.4 | 760.1 | 169 | 191.6 | 722.9 | 157.2 | 312.8 | 459.9 | 43.4 | 50.6 | 344.2 | 19.5 | 36.3 | 55.4 | 83.8 | 256.1 | 302.8 | 76.6 | 207.8 | 44.3 | 171.6 | 161.2 | 50.7 | 76.3 | 60.4 | 48.8
625 | 386 | 381.3 | 152.52 | 178.2871 | 155.9 | 170.8 | 177.3 | 150.4 | 282.9 | 23.1 | 20.9 | 44 | 3.5 | 201.7 | 13.7 | 115.2 | 368.5 | 767.3 | 169.2 | 192.1 | 723.1 | 157.9 | 314.1 | 458.6 | 43.6 | 50.8 | 345.5 | 19.6 | 36.4 | 55.5 | 84.1 | 256.1 | 301.9 | 77 | 208.2 | 44.4 | 172 | 161.9 | 50.8 | 76.5 | 60.6 | 49
626 | 387 | 379.3 | 151.72 | 177.3519 | 156.8 | 171 | 177.6 | 150.8 | 285.8 | 23.1 | 20.9 | 44.1 | 3.7 | 187.4 | 16.8 | 115.4 | 368.9 | 774.6 | 169.4 | 192.6 | 723.1 | 158.6 | 314.5 | 460.9 | 43.7 | 51 | 346.9 | 19.6 | 36.6 | 55.8 | 84.4 | 257 | 304.3 | 79.4 | 209.3 | 44.5 | 172.2 | 162.5 | 50.9 | 76.7 | 60.8 | 49.1
627 | 388 | 380.3 | 152.12 | 177.8195 | 157.1 | 172 | 177.5 | 151.2 | 288.3 | 23.1 | 20.9 | 44.2 | 4 | 184.1 | 18.5 | 115.7 | 368.5 | 772.8 | 169.6 | 193.1 | 723.6 | 159.2 | 315.5 | 476 | 43.9 | 51.1 | 349.9 | 19.6 | 36.7 | 56.1 | 84.8 | 258.1 | 306.1 | 80.1 | 209.9 | 44.7 | 172.8 | 162.4 | 51 | 76.9 | 61 | 49.3
628 | 389 | 381.7 | 152.68 | 178.4741 | 157.5 | 171.8 | 177.8 | 151.5 | 290.1 | 23.1 | 20.9 | 44.3 | 4.5 | 183.1 | 17.7 | 116 | 370.9 | 778.5 | 169.8 | 193.7 | 724.4 | 159.9 | 315.1 | 471 | 44 | 51.3 | 351 | 19.7 | 36.9 | 56.3 | 85.1 | 258.5 | 304.7 | 80 | 209.8 | 44.8 | 173.2 | 162.8 | 51.1 | 77.2 | 61.2 | 49.4
629 | 390 | 381.9 | 152.76 | 178.5676 | 158 | 171.9 | 178.1 | 151.2 | 287.7 | 23.2 | 20.9 | 44.5 | 3.9 | 191.2 | 18.6 | 116.3 | 372 | 786.5 | 170 | 194.2 | 725.5 | 160.6 | 314.4 | 468 | 44.2 | 51.5 | 352.1 | 19.7 | 37 | 56.4 | 85.5 | 258.8 | 304.1 | 81 | 209.5 | 44.9 | 173.4 | 162.8 | 51.2 | 77.3 | 61.5 | 49.5
630 | 391 | 382.2 | 152.88 | 178.7079 | 158.5 | 172.2 | 178.3 | 151.1 | 288.9 | 23.2 | 20.9 | 44.5 | 3.6 | 193.1 | 18.8 | 116.6 | 372.2 | 784.8 | 170.3 | 194.5 | 726.1 | 161.2 | 313.7 | 468.3 | 44.4 | 51.6 | 353.3 | 19.8 | 37.1 | 56.6 | 85.8 | 260 | 306.9 | 82.3 | 210.1 | 45 | 173.5 | 163.4 | 51.4 | 77.5 | 61.7 | 49.7
631 | 392 | 381.6 | 152.64 | 178.4274 | 159.1 | 172.9 | 178.6 | 151.1 | 288.6 | 23.2 | 20.9 | 44.6 | 3.7 | 200.5 | 17.6 | 116.9 | 369.9 | 785.1 | 170.6 | 194.9 | 726.7 | 161.9 | 311.5 | 460.7 | 44.5 | 51.8 | 352.4 | 19.8 | 37.2 | 56.8 | 86.2 | 260 | 304.5 | 82.3 | 210.1 | 45.1 | 173.4 | 163.8 | 51.5 | 77.6 | 61.9 | 49.8
632 | 393 | 381.9 | 152.76 | 178.5676 | 159.5 | 173.4 | 178.7 | 151 | 284.8 | 23.3 | 20.9 | 44.7 | 3.5 | 201.6 | 14.5 | 117.1 | 369.4 | 791.2 | 170.9 | 195.2 | 727.4 | 162.5 | 310.2 | 461.1 | 44.7 | 52 | 352.9 | 19.9 | 37.3 | 56.9 | 86.5 | 259.3 | 304 | 81.7 | 209.8 | 45.3 | 173.6 | 163.8 | 51.6 | 77.8 | 62.1 | 49.9
633 | 394 | 382.3 | 152.92 | 178.7547 | 159.6 | 172.9 | 178.8 | 151.3 | 285.9 | 23.4 | 20.9 | 44.8 | 3.5 | 215.6 | 13.1 | 117.4 | 372.2 | 796.9 | 171.1 | 196 | 727.5 | 163.2 | 312 | 468.2 | 44.8 | 52.2 | 355.7 | 19.9 | 37.4 | 57.1 | 86.8 | 260.3 | 307 | 83.2 | 211.1 | 45.4 | 173.9 | 163.8 | 51.9 | 77.9 | 62.3 | 50.1
634 | 395 | 382.1 | 152.84 | 178.6612 | 159.5 | 172.7 | 178.9 | 151.2 | 287.1 | 23.5 | 20.9 | 44.9 | 3.6 | 196.8 | 13.7 | 117.7 | 370.4 | 791.2 | 171.4 | 196.4 | 727.9 | 163.8 | 311.4 | 463.8 | 45 | 52.3 | 358.1 | 20 | 37.6 | 57.3 | 87.2 | 261.6 | 306.4 | 84.6 | 212 | 45.5 | 174.2 | 163.8 | 52.1 | 78 | 62.5 | 50.2
635 | 396 | 382.9 | 153.16 | 179.0352 | 159.7 | 172.9 | 178.8 | 151.4 | 285.2 | 23.5 | 20.9 | 45 | 3.9 | 187.4 | 13.9 | 118 | 368.7 | 779.8 | 171.7 | 197 | 729.8 | 164.4 | 309.8 | 453.5 | 45.2 | 52.5 | 356.8 | 20 | 37.7 | 57.3 | 87.5 | 261.4 | 303.6 | 84.6 | 211.6 | 45.6 | 174.2 | 164 | 52.2 | 78.1 | 62.7 | 50.4
636 | 397 | 382.7 | 153.08 | 178.9417 | 159.9 | 173.1 | 179.1 | 151.7 | 281.4 | 23.5 | 20.9 | 45.1 | 3.5 | 184.9 | 13.3 | 118.3 | 368.2 | 770.6 | 171.9 | 197.2 | 731.3 | 165.1 | 308.6 | 447.2 | 45.3 | 52.7 | 356.7 | 20.1 | 37.9 | 57.5 | 87.9 | 260.3 | 302.6 | 85.4 | 211.1 | 45.7 | 174.2 | 164.5 | 52.3 | 78.3 | 63 | 50.5
637 | 398 | 380.7 | 152.28 | 178.0065 | 160.2 | 172.6 | 179.2 | 152 | 283.2 | 23.5 | 20.9 | 45.2 | 3.8 | 201.4 | 13.5 | 118.6 | 367.4 | 779.1 | 172.2 | 197.3 | 731.3 | 165.7 | 308 | 450.4 | 45.5 | 52.9 | 357.3 | 20.1 | 38 | 57.6 | 88.2 | 260.9 | 308.2 | 87.3 | 213 | 45.9 | 174.5 | 164.5 | 52.5 | 78.5 | 63.2 | 50.7
638 | 399 | 380.9 | 152.36 | 178.1001 | 160.5 | 171.9 | 179.8 | 152.3 | 287.9 | 23.5 | 20.9 | 45.3 | 4.5 | 195.7 | 13.2 | 118.8 | 367.7 | 774.9 | 172.5 | 197.6 | 730.4 | 166.3 | 310.4 | 465.2 | 45.7 | 53 | 359.9 | 20.2 | 38.2 | 57.9 | 88.6 | 261.2 | 308.4 | 88.6 | 215.5 | 46 | 174.6 | 164.6 | 52.6 | 78.7 | 63.4 | 50.8
639 | 400 | 381.2 | 152.48 | 178.2403 | 160.3 | 171.5 | 180.4 | 152.6 | 286.7 | 23.6 | 20.9 | 45.4 | 3.7 | 181.9 | 12.1 | 119.1 | 371.3 | 772.4 | 172.8 | 197.9 | 729.5 | 166.9 | 310.8 | 472 | 45.8 | 53.2 | 363.2 | 20.2 | 38.3 | 58.1 | 88.9 | 261.5 | 306.8 | 88 | 215.5 | 46.1 | 174.6 | 164.6 | 52.8 | 78.8 | 63.6 | 51
640 | 401 | 381.5 | 152.6 | 178.3806 | 160.5 | 171.7 | 181 | 152.9 | 287.9 | 23.7 | 20.9 | 45.5 | 3.9 | 207.7 | 11 | 119.4 | 374 | 772.7 | 173.1 | 198.4 | 729.3 | 167.5 | 315.6 | 491 | 46 | 53.4 | 367.7 | 20.2 | 38.4 | 58.3 | 89.2 | 261.9 | 312.5 | 88.9 | 216.8 | 46.2 | 174.7 | 164.4 | 53 | 78.9 | 63.8 | 51.1
641 | 402 | 382.6 | 153.04 | 178.8949 | 161.1 | 172.3 | 181.1 | 153.1 | 295.1 | 23.8 | 20.9 | 45.6 | 4.1 | 208.4 | 12.1 | 119.7 | 373.2 | 750.8 | 173.5 | 198.7 | 728.7 | 168.1 | 317.6 | 488.6 | 46.2 | 53.6 | 368 | 20.3 | 38.6 | 58.6 | 89.6 | 265.2 | 318.1 | 91.2 | 219.2 | 46.3 | 175.2 | 164.4 | 53.2 | 79.1 | 64.1 | 51.2
642 | 403 | 382.7 | 153.08 | 178.9417 | 161.6 | 173.1 | 181.2 | 153.3 | 298.9 | 23.9 | 20.9 | 45.7 | 4.4 | 208.6 | 12.7 | 120 | 382.7 | 741.5 | 173.9 | 199 | 728.6 | 168.7 | 319.4 | 490.2 | 46.3 | 53.7 | 369 | 20.4 | 38.7 | 58.9 | 89.9 | 266.2 | 318.9 | 92 | 220 | 46.4 | 175.2 | 165 | 53.4 | 79.3 | 64.3 | 51.4
643 | 404 | 382.3 | 152.92 | 178.7547 | 162.2 | 174.2 | 181.6 | 153.7 | 298.1 | 24 | 20.9 | 45.7 | 4.3 | 192.4 | 13.8 | 120.3 | 385.1 | 754.4 | 174.3 | 199.5 | 728.9 | 169.3 | 321.1 | 495.1 | 46.5 | 53.9 | 371.3 | 20.4 | 38.9 | 59.3 | 90.3 | 266.9 | 320.1 | 92.4 | 219.7 | 46.5 | 175.6 | 164.8 | 53.5 | 79.5 | 64.5 | 51.5
644 | 405 | 381.6 | 152.64 | 178.4274 | 162.7 | 175.3 | 182.2 | 153.9 | 297.6 | 24.1 | 20.9 | 45.8 | 4.8 | 202.9 | 13.6 | 120.5 | 384.1 | 757.4 | 174.6 | 199.9 | 728.4 | 169.9 | 322.6 | 500.6 | 46.6 | 54.1 | 373.9 | 20.5 | 39 | 59.3 | 90.6 | 268.1 | 319.5 | 93.4 | 219.8 | 46.7 | 175.9 | 164.9 | 53.6 | 79.6 | 64.8 | 51.7
645 | 406 | 381.7 | 152.68 | 178.4741 | 163.2 | 176.1 | 183 | 154.3 | 295.2 | 24.2 | 20.9 | 46 | 4.3 | 193.3 | 12.5 | 120.8 | 386.3 | 755 | 175 | 200.2 | 727.3 | 170.5 | 324.1 | 504.9 | 46.8 | 54.3 | 375.2 | 20.5 | 39.2 | 59.5 | 90.9 | 267.4 | 317.6 | 92.5 | 220.3 | 46.8 | 176.2 | 165.1 | 53.7 | 79.7 | 65 | 51.8
646 | 407 | 382.8 | 153.12 | 178.9885 | 163.6 | 176.1 | 184.2 | 154.8 | 295.2 | 24.2 | 20.9 | 46.1 | 4 | 197.7 | 11.9 | 121.1 | 387.6 | 757.8 | 175.4 | 200.6 | 727 | 171.2 | 324.8 | 507.6 | 47 | 54.5 | 376.3 | 20.6 | 39.3 | 59.6 | 91.3 | 267.6 | 317.9 | 93 | 220.3 | 46.9 | 176.6 | 166 | 53.9 | 79.9 | 65.2 | 52
647 | 408 | 381.8 | 152.72 | 178.5209 | 163.8 | 175.8 | 185.1 | 155 | 296.7 | 24.3 | 20.9 | 46.1 | 4.6 | 199.7 | 12.8 | 121.4 | 388.2 | 761.9 | 175.7 | 200.9 | 726.5 | 171.7 | 326.2 | 514.1 | 47.1 | 54.6 | 378 | 20.6 | 39.4 | 59.8 | 91.6 | 267.7 | 318.2 | 93.1 | 220.7 | 47 | 177.1 | 166.9 | 54.1 | 80.1 | 65.4 | 52.1
648 | 409 | 381.5 | 152.6 | 178.3806 | 164 | 176.3 | 185.9 | 155.7 | 297.8 | 24.4 | 20.9 | 46.2 | 5 | 206 | 11.7 | 121.7 | 386.3 | 767.4 | 176 | 201.2 | 726.6 | 172.4 | 324.6 | 503.7 | 47.3 | 54.8 | 377.1 | 20.7 | 39.5 | 60.1 | 91.9 | 268.6 | 319.3 | 94 | 221.4 | 47.1 | 177.4 | 166.8 | 54.2 | 80.5 | 65.7 | 52.3
649 | 410 | 382.8 | 153.12 | 178.9885 | 164.1 | 177.2 | 186.5 | 156.3 | 296.6 | 24.5 | 20.9 | 46.3 | 5.4 | 204.9 | 9.6 | 122 | 382 | 762 | 176.3 | 201.6 | 726.2 | 173 | 322.2 | 492.2 | 47.5 | 55 | 375.4 | 20.7 | 39.7 | 60.4 | 92.3 | 267.6 | 316.8 | 93.5 | 220.9 | 47.3 | 177.6 | 167 | 54.2 | 80.6 | 65.9 | 52.4
650 | 411 | 381.6 | 152.64 | 178.4274 | 163.9 | 176.9 | 186.7 | 156.7 | 294.8 | 24.5 | 20.9 | 46.3 | 5.2 | 221.6 | 8.9 | 122.2 | 382.6 | 758.9 | 176.6 | 201.8 | 726.3 | 173.6 | 320.2 | 484.6 | 47.6 | 55.2 | 375.8 | 20.8 | 39.8 | 60.4 | 92.6 | 267.1 | 315.9 | 92.5 | 220.6 | 47.4 | 178.2 | 167 | 54.3 | 80.7 | 66.1 | 52.6
651 | 412 | 381.3 | 152.52 | 178.2871 | 164.3 | 177.7 | 187.1 | 157 | 292 | 24.5 | 20.9 | 46.4 | 5.2 | 232.5 | 8.9 | 122.5 | 382.6 | 756.3 | 176.9 | 202 | 726.5 | 174.2 | 320.4 | 482.2 | 47.8 | 55.4 | 378 | 20.8 | 40 | 60.6 | 93 | 267 | 314.7 | 92.7 | 221 | 47.5 | 178.7 | 167 | 54.6 | 80.9 | 66.4 | 52.7
652 | 413 | 381.2 | 152.48 | 178.2403 | 164.5 | 178.6 | 187.5 | 157.2 | 294.8 | 24.5 | 20.9 | 46.4 | 5.2 | 207.7 | 8.6 | 122.8 | 384.1 | 763.4 | 177.1 | 202.2 | 727.1 | 174.8 | 320.9 | 484.4 | 48 | 55.6 | 378.9 | 20.9 | 40.1 | 60.8 | 93.3 | 268.5 | 316.4 | 94.1 | 221 | 47.6 | 179.2 | 167 | 54.7 | 81.2 | 66.6 | 52.9
653 | 414 | 381.5 | 152.6 | 178.3806 | 164.9 | 178.8 | 187.6 | 157.5 | 296 | 24.5 | 20.9 | 46.5 | 4.7 | 215 | 8.5 | 123.1 | 382.7 | 772.4 | 177.4 | 202.5 | 727.5 | 175.4 | 322.3 | 489.3 | 48.1 | 55.7 | 379.7 | 20.9 | 40.2 | 61 | 93.6 | 269.8 | 318.6 | 94.3 | 222.2 | 47.8 | 179.5 | 167.2 | 55 | 81.3 | 66.8 | 53
654 | 415 | 381 | 152.4 | 178.1468 | 165 | 180.3 | 187.9 | 157.7 | 296.4 | 24.4 | 20.9 | 46.6 | 4.1 | 190.3 | 8.4 | 123.4 | 381 | 795.6 | 177.8 | 202.8 | 728.4 | 176 | 322.4 | 490.2 | 48.3 | 55.9 | 380.4 | 21 | 40.3 | 61.2 | 94 | 270.4 | 319 | 94.4 | 223.2 | 47.9 | 179.6 | 168 | 55.2 | 81.7 | 67.1 | 53.2
655 | 416 | 382.7 | 153.08 | 178.9417 | 165.1 | 181.6 | 187.6 | 157.9 | 293.7 | 24.4 | 20.9 | 46.7 | 4.7 | 224.2 | 7.6 | 123.7 | 381.2 | 810.5 | 178.1 | 203.2 | 730.4 | 176.6 | 322.9 | 488.9 | 48.5 | 56.1 | 380.9 | 21 | 40.3 | 61.4 | 94.3 | 269.7 | 317.6 | 93.9 | 223.3 | 48 | 180.3 | 168.4 | 55.4 | 81.9 | 67.4 | 53.3
656 | 417 | 382.3 | 152.92 | 178.7547 | 164.9 | 181.5 | 187.4 | 158.1 | 293.7 | 24.4 | 20.9 | 46.8 | 4.9 | 208.5 | 11.8 | 124 | 381.2 | 813 | 178.4 | 203.7 | 732.2 | 177.2 | 324.4 | 498.4 | 48.6 | 56.3 | 383.9 | 21.1 | 40.4 | 61.5 | 94.6 | 271.2 | 317 | 94.5 | 224.4 | 48.2 | 180.7 | 168.5 | 55.8 | 82.1 | 67.6 | 53.5
657 | 418 | 381.6 | 152.64 | 178.4274 | 165.1 | 182.2 | 187.6 | 158.4 | 294.1 | 24.4 | 20.8 | 46.9 | 4.3 | 209.5 | 15.7 | 124.3 | 381.1 | 799.3 | 178.8 | 204.1 | 732.7 | 177.8 | 323 | 491.4 | 48.8 | 56.5 | 384 | 21.1 | 40.6 | 61.6 | 94.9 | 273.9 | 317.3 | 94.8 | 225.6 | 48.3 | 180.8 | 169.1 | 56 | 82.3 | 67.9 | 53.6
658 | 419 | 381.6 | 152.64 | 178.4274 | 165.5 | 185.4 | 187.7 | 158.9 | 293.7 | 24.5 | 20.8 | 47 | 4.5 | 205.7 | 19 | 124.6 | 380.5 | 794.8 | 179.1 | 204.4 | 733.3 | 178.3 | 320.5 | 482.8 | 49 | 56.7 | 383.1 | 21.2 | 40.6 | 61.8 | 95.3 | 274 | 316.7 | 94.8 | 226.3 | 48.4 | 181 | 168.9 | 56.2 | 82.6 | 68.2 | 53.8
659 | 420 | 381.1 | 152.44 | 178.1936 | 165.4 | 186.2 | 187.1 | 159.5 | 292.7 | 24.5 | 20.8 | 47.1 | 4.4 | 208.4 | 17.6 | 124.9 | 384 | 804.8 | 179.4 | 205 | 734.2 | 178.9 | 319.2 | 478.4 | 49.1 | 56.9 | 383.3 | 21.3 | 40.7 | 62 | 95.6 | 274.9 | 317.5 | 95 | 226.6 | 48.6 | 181.4 | 169 | 56.4 | 82.8 | 68.5 | 54
660 | 421 | 381.4 | 152.56 | 178.3339 | 165.5 | 185.8 | 186.6 | 159.6 | 294.4 | 24.6 | 20.8 | 47.2 | 5.1 | 211.3 | 14.9 | 125.2 | 384.4 | 807.8 | 179.7 | 205.4 | 734.5 | 179.5 | 319.5 | 478.1 | 49.3 | 57.1 | 384.8 | 21.3 | 40.8 | 62.1 | 95.9 | 275.8 | 320.4 | 95.8 | 227.2 | 48.7 | 181.4 | 169.4 | 56.6 | 83.1 | 68.7 | 54.1
661 | 422 | 381.5 | 152.6 | 178.3806 | 165.7 | 185.5 | 186.4 | 159.4 | 296.4 | 24.6 | 20.8 | 47.3 | 4.9 | 212 | 11 | 125.5 | 383.5 | 797.8 | 180.1 | 205.6 | 734.4 | 180 | 318.9 | 472.1 | 49.5 | 57.3 | 384.3 | 21.4 | 41 | 62.4 | 96.3 | 276.3 | 321.7 | 96.7 | 227.7 | 48.9 | 181.6 | 169.5 | 56.8 | 83.2 | 69 | 54.2
662 | 423 | 380.9 | 152.36 | 178.1001 | 166 | 184.9 | 186.6 | 159.3 | 297.2 | 24.7 | 20.8 | 47.4 | 4.6 | 198.5 | 11.4 | 125.7 | 382.7 | 801.2 | 180.4 | 206.1 | 734.7 | 180.6 | 317.6 | 467 | 49.6 | 57.5 | 383.6 | 21.4 | 41.1 | 62.3 | 96.6 | 276.1 | 320.2 | 97.1 | 227.8 | 49 | 181.7 | 169.4 | 57.1 | 83.4 | 69.2 | 54.4
663 | 424 | 380.1 | 152.04 | 177.726 | 166.5 | 184.3 | 186.6 | 159 | 295.2 | 24.8 | 20.8 | 47.5 | 4.9 | 206.9 | 11.2 | 126.1 | 380.2 | 800.6 | 180.8 | 206.8 | 734.7 | 181.1 | 316.3 | 460.7 | 49.8 | 57.7 | 382.9 | 21.5 | 41.3 | 62.6 | 96.9 | 275.9 | 319.3 | 97.6 | 228.7 | 49.1 | 181.9 | 169.4 | 57.2 | 83.6 | 69.4 | 54.5
664 | 425 | 381.8 | 152.72 | 178.5209 | 166.5 | 183.9 | 186.4 | 159 | 293.8 | 24.8 | 20.8 | 47.6 | 5.3 | 207.1 | 11.9 | 126.4 | 379.9 | 811.7 | 181.1 | 207.3 | 735.2 | 181.7 | 315.9 | 464 | 50 | 57.9 | 382.8 | 21.5 | 41.4 | 63 | 97.2 | 276.2 | 320 | 99.1 | 231.7 | 49.3 | 181.9 | 169.5 | 57.2 | 83.9 | 69.7 | 54.7
665 | 426 | 378.7 | 151.48 | 177.0714 | 166.3 | 184.7 | 186.3 | 159.4 | 296.4 | 24.8 | 20.8 | 47.6 | 5.5 | 212.6 | 12 | 126.7 | 380.5 | 818.7 | 181.5 | 208 | 736.1 | 182.2 | 317.8 | 469.8 | 50.1 | 58 | 384 | 21.6 | 41.5 | 63.1 | 97.5 | 277 | 319.7 | 100.5 | 233.4 | 49.4 | 182 | 169.4 | 57.4 | 84.1 | 69.9 | 54.8
666 | 427 | 383.1 | 153.24 | 179.1287 | 165.9 | 185 | 186.3 | 159.4 | 299.8 | 24.8 | 20.8 | 47.7 | 5.3 | 203.6 | 12.8 | 127 | 376.1 | 817.9 | 181.8 | 208.7 | 736.5 | 182.8 | 318.8 | 483.3 | 50.3 | 58.2 | 386.1 | 21.7 | 41.6 | 63.4 | 97.9 | 278.2 | 326.2 | 101.3 | 234 | 49.5 | 182.1 | 169.5 | 57.5 | 84.2 | 70.2 | 55
667 | 428 | 380.5 | 152.2 | 177.913 | 165.1 | 184.6 | 186.1 | 159.3 | 303.8 | 24.9 | 20.8 | 47.7 | 5 | 215.6 | 12.8 | 127.4 | 374.6 | 813.2 | 182.1 | 209.2 | 736.6 | 183.3 | 319.1 | 487.4 | 50.5 | 58.4 | 387.1 | 21.7 | 41.7 | 63.6 | 98.2 | 278.1 | 328.4 | 100.4 | 234.5 | 49.7 | 182.3 | 169.9 | 57.6 | 84.4 | 70.5 | 55.1
668 | 429 | 379 | 151.6 | 177.2117 | 164.8 | 184.8 | 186.2 | 159.3 | 307.2 | 24.9 | 20.8 | 47.7 | 4.9 | 214.7 | 10.9 | 127.7 | 370.3 | 813.8 | 182.4 | 209.9 | 735.7 | 183.9 | 319.6 | 493.4 | 50.7 | 58.6 | 387.7 | 21.8 | 41.8 | 63.8 | 98.5 | 279.3 | 336.3 | 101.2 | 235.8 | 49.8 | 182.5 | 170.1 | 57.7 | 84.6 | 70.7 | 55.3
669 | 430 | 380.4 | 152.16 | 177.8663 | 164.8 | 185.1 | 187.1 | 159 | 306.3 | 24.9 | 20.8 | 47.8 | 5.3 | 205.1 | 12 | 128.1 | 369 | 815.9 | 182.7 | 210.4 | 735.9 | 184.4 | 318.8 | 497.3 | 50.8 | 58.8 | 389.3 | 21.8 | 41.9 | 64 | 98.8 | 279.1 | 333.4 | 102.4 | 235 | 49.9 | 182.4 | 170.5 | 57.8 | 84.6 | 70.9 | 55.4
670 | 431 | 380.9 | 152.36 | 178.1001 | 164.6 | 186.2 | 187.2 | 159 | 302.3 | 24.9 | 20.8 | 47.9 | 5.2 | 207 | 12.8 | 128.5 | 370.1 | 807.8 | 183 | 211 | 736.1 | 185 | 318.8 | 498.9 | 51 | 59 | 389.3 | 21.9 | 42 | 64 | 99.2 | 278.7 | 331.6 | 101.7 | 234.4 | 50.1 | 182.2 | 170.6 | 57.9 | 84.8 | 71.2 | 55.5
671 | 432 | 382 | 152.8 | 178.6144 | 164.8 | 187.5 | 186.5 | 159.1 | 301.9 | 25 | 20.8 | 47.9 | 5.3 | 208.5 | 14.3 | 128.9 | 371.1 | 806.7 | 183.3 | 211.6 | 736.5 | 185.5 | 319.9 | 497.8 | 51.2 | 59.2 | 389.6 | 21.9 | 42.1 | 64.2 | 99.5 | 279.3 | 331.9 | 101.8 | 234.9 | 50.2 | 182.2 | 170.3 | 57.9 | 84.9 | 71.5 | 55.7
672 | 433 | 381.6 | 152.64 | 178.4274 | 164.9 | 187.5 | 186.4 | 159.2 | 302.6 | 25 | 20.8 | 48 | 5.1 | 206.6 | 15 | 129.3 | 379.5 | 802.1 | 183.6 | 212.2 | 736.9 | 186.1 | 320.5 | 495.9 | 51.3 | 59.4 | 390.3 | 22 | 42.2 | 64.6 | 99.8 | 279.3 | 332.3 | 102.2 | 236.1 | 50.3 | 182.2 | 170.4 | 58 | 85.1 | 71.7 | 55.8
673 | 434 | 380.7 | 152.28 | 178.0065 | 165 | 187.5 | 186.8 | 159.2 | 302 | 25.1 | 20.8 | 48.1 | 4.7 | 204.9 | 13.5 | 129.7 | 386.7 | 795 | 183.8 | 212.7 | 738.1 | 186.6 | 319.7 | 499.3 | 51.5 | 59.6 | 391.6 | 22.1 | 42.4 | 64.7 | 100.2 | 278.9 | 330.8 | 101.9 | 236.2 | 50.4 | 182 | 170.4 | 58.2 | 85.2 | 72 | 56
674 | 435 | 382 | 152.8 | 178.6144 | 165.6 | 187.6 | 187 | 159.4 | 303 | 25.2 | 20.8 | 48.1 | 4.1 | 221.3 | 10.4 | 130.1 | 386.8 | 799.5 | 184.1 | 213.3 | 739.1 | 187.2 | 319.3 | 497.7 | 51.7 | 59.8 | 390.9 | 22.1 | 42.5 | 64.9 | 100.5 | 279.5 | 330 | 102.8 | 236.6 | 50.6 | 182.2 | 170.5 | 58.3 | 85.4 | 72.3 | 56.1
675 | 436 | 381.8 | 152.72 | 178.5209 | 165.6 | 187.9 | 186.8 | 159.5 | 302.3 | 25.3 | 20.8 | 48.2 | 4.1 | 210.5 | 11.7 | 130.6 | 388.1 | 809 | 184.4 | 213.8 | 739.6 | 187.7 | 319.4 | 504.2 | 51.8 | 60 | 392.3 | 22.2 | 42.7 | 65 | 100.8 | 279.8 | 328.2 | 101.5 | 237.1 | 50.7 | 182.4 | 170.4 | 58.5 | 85.8 | 72.5 | 56.2
676 | 437 | 381 | 152.4 | 178.1468 | 165.8 | 187.5 | 186.6 | 159.8 | 302.5 | 25.4 | 20.8 | 48.2 | 4.7 | 211.3 | 12.8 | 131 | 384.5 | 811.2 | 184.8 | 214.5 | 739.8 | 188.3 | 320.6 | 504.6 | 52 | 60.2 | 393.6 | 22.2 | 42.9 | 65.2 | 101.2 | 281 | 328 | 101.9 | 238.2 | 50.8 | 182.5 | 170.7 | 58.7 | 86 | 72.8 | 56.4
677 | 438 | 380.5 | 152.2 | 177.913 | 166.5 | 188.6 | 186.6 | 160.1 | 302.8 | 25.4 | 20.8 | 48.3 | 4.1 | 209.2 | 12.8 | 131.5 | 379.4 | 818.5 | 185.1 | 215.2 | 740.2 | 188.8 | 321.2 | 499.5 | 52.2 | 60.4 | 392.7 | 22.3 | 43 | 65.4 | 101.5 | 281.7 | 329 | 101.7 | 239.7 | 50.9 | 182.8 | 170.9 | 58.9 | 86.2 | 73.1 | 56.5
678 | 439 | 381.4 | 152.56 | 178.3339 | 167.6 | 189.5 | 186.7 | 160.4 | 304.6 | 25.5 | 20.8 | 48.2 | 3.4 | 207.9 | 11.4 | 132 | 384.6 | 814.9 | 185.4 | 215.7 | 740.5 | 189.4 | 319.7 | 495.1 | 52.3 | 60.6 | 392.4 | 22.4 | 43.2 | 65.6 | 101.8 | 282.9 | 330.1 | 103.3 | 240.8 | 51.1 | 183 | 171 | 59 | 86.4 | 73.3 | 56.7
679 | 440 | 381.4 | 152.56 | 178.3339 | 167.7 | 189.1 | 186.7 | 160.4 | 303.6 | 25.5 | 20.8 | 48.2 | 3.4 | 193.2 | 11.2 | 132.4 | 381.8 | 812.9 | 185.8 | 216.3 | 739.9 | 189.9 | 319.9 | 505.8 | 52.5 | 60.8 | 394.4 | 22.4 | 43.3 | 65.9 | 102.2 | 283.1 | 333.1 | 103.2 | 241.3 | 51.2 | 183.1 | 171.4 | 59.2 | 86.5 | 73.6 | 56.8
680 | 441 | 381.9 | 152.76 | 178.5676 | 167.7 | 188.7 | 186.6 | 160.6 | 305.4 | 25.5 | 20.8 | 48.2 | 3.7 | 189.7 | 9.5 | 132.9 | 379.4 | 804.1 | 186.1 | 216.9 | 739.7 | 190.5 | 320 | 515.1 | 52.7 | 61 | 397.1 | 22.5 | 43.5 | 66.1 | 102.5 | 284.3 | 334 | 103.5 | 242.5 | 51.3 | 183.3 | 171.6 | 59.2 | 86.8 | 73.9 | 57
681 | 442 | 381.6 | 152.64 | 178.4274 | 167.4 | 188.6 | 186.8 | 160.5 | 304.3 | 25.5 | 20.8 | 48.3 | 3.8 | 208.5 | 8.4 | 133.4 | 379.2 | 801.5 | 186.5 | 217.4 | 740.6 | 191.1 | 321.1 | 515.5 | 52.9 | 61.2 | 398.4 | 22.6 | 43.7 | 66.1 | 102.8 | 284.2 | 331.3 | 103.6 | 242.4 | 51.5 | 183.4 | 172.2 | 59.3 | 86.8 | 74.2 | 57.1
682 | 443 | 381.6 | 152.64 | 178.4274 | 166.9 | 189.2 | 187.2 | 160.5 | 301.5 | 25.6 | 20.8 | 48.3 | 4.1 | 204.1 | 15.1 | 133.9 | 381.2 | 799.4 | 186.9 | 218 | 741.7 | 191.6 | 321.4 | 514.1 | 53 | 61.4 | 400.3 | 22.6 | 43.9 | 66.3 | 103.2 | 284.2 | 330.1 | 103.3 | 242.4 | 51.6 | 183.5 | 172.3 | 59.5 | 86.9 | 74.4 | 57.3
683 | 444 | 384.5 | 153.8 | 179.7833 | 166.6 | 190.7 | 187.2 | 160.8 | 300.8 | 25.7 | 20.8 | 48.4 | 3.7 | 190.3 | 16.9 | 134.4 | 381.4 | 793.5 | 187.3 | 218.5 | 742.5 | 192.2 | 321 | 512.1 | 53.2 | 61.6 | 400.7 | 22.7 | 44 | 66.5 | 103.5 | 284 | 328.3 | 103.6 | 242.7 | 51.7 | 183.6 | 172.4 | 59.6 | 87.3 | 74.7 | 57.4
684 | 445 | 385.8 | 154.32 | 180.3912 | 167.2 | 191.4 | 187.1 | 161.1 | 300.1 | 25.8 | 20.8 | 48.4 | 3.7 | 191.1 | 16.8 | 134.9 | 385.3 | 800.8 | 187.7 | 219 | 743.6 | 192.8 | 321.4 | 518.4 | 53.4 | 61.8 | 402.6 | 22.7 | 44.1 | 66.7 | 103.8 | 284 | 328.5 | 104.9 | 243.6 | 51.8 | 183.8 | 172.5 | 59.7 | 87.5 | 75 | 57.5
685 | 446 | 385.1 | 154.04 | 180.0639 | 167.7 | 190.9 | 187.4 | 161.3 | 305.7 | 25.9 | 20.8 | 48.5 | 4.1 | 185.5 | 16.4 | 135.4 | 387.5 | 788.1 | 188.1 | 219.6 | 744 | 193.3 | 323.5 | 522.4 | 53.5 | 62 | 406.4 | 22.8 | 44.3 | 67 | 104.1 | 286.3 | 331.5 | 107.1 | 244.2 | 52 | 184.1 | 173.5 | 59.8 | 87.6 | 75.3 | 57.7
686 | 447 | 383.1 | 153.24 | 179.1287 | 167.4 | 190.8 | 188 | 161.5 | 308.3 | 26 | 20.8 | 48.6 | 3.8 | 195.3 | 15.2 | 135.9 | 385.5 | 778.6 | 188.5 | 220 | 743.2 | 193.9 | 322.3 | 516.1 | 53.7 | 62.2 | 406.1 | 22.9 | 44.4 | 67.2 | 104.5 | 287.1 | 331.1 | 107.6 | 244.6 | 52.1 | 184.3 | 174.5 | 60 | 87.8 | 75.5 | 57.8
687 | 448 | 382.8 | 153.12 | 178.9885 | 166.9 | 190.9 | 188.4 | 161.8 | 306.1 | 26 | 20.8 | 48.6 | 4 | 205.3 | 14.7 | 136.4 | 383.2 | 788.7 | 188.9 | 220.5 | 742.4 | 194.4 | 321 | 509.4 | 53.9 | 62.4 | 405.2 | 22.9 | 44.5 | 67.3 | 104.8 | 286.8 | 328.7 | 106.9 | 244 | 52.2 | 184.6 | 175.1 | 60.1 | 88.1 | 75.8 | 58
688 | 449 | 383.1 | 153.24 | 179.1287 | 167.2 | 191 | 188.7 | 162.3 | 308.8 | 26.1 | 20.8 | 48.6 | 4.5 | 203.7 | 13.4 | 136.9 | 384.1 | 790.1 | 189.3 | 221 | 741.8 | 195 | 320.2 | 508.9 | 54.1 | 62.6 | 405.2 | 23 | 44.6 | 67.5 | 105.1 | 289 | 328.8 | 107.8 | 245.6 | 52.4 | 184.8 | 175.2 | 60.2 | 88.4 | 76.1 | 58.1
689 | 450 | 381.7 | 152.68 | 178.4741 | 167.5 | 191.7 | 188.8 | 162.5 | 308.7 | 26.2 | 20.8 | 48.7 | 4.5 | 210.6 | 12.6 | 137.5 | 387.1 | 787.6 | 189.8 | 221.4 | 741.7 | 195.5 | 319.9 | 504.9 | 54.2 | 62.8 | 405.2 | 23.1 | 44.7 | 67.7 | 105.5 | 289.9 | 329.5 | 106.9 | 247.4 | 52.5 | 184.9 | 175.1 | 60.4 | 88.6 | 76.4 | 58.3
690 | 451 | 381.8 | 152.72 | 178.5209 | 168.3 | 191.9 | 189.1 | 162.7 | 308.8 | 26.2 | 20.8 | 48.8 | 4.2 | 219.5 | 11.8 | 138 | 384.6 | 777.5 | 190.2 | 221.9 | 741.9 | 196.1 | 318.8 | 503.7 | 54.4 | 63 | 405.1 | 23.2 | 44.8 | 68.1 | 105.8 | 290.1 | 330.3 | 106.8 | 247.7 | 52.6 | 184.9 | 175.4 | 60.6 | 88.7 | 76.6 | 58.4
691 | 452 | 382.3 | 152.92 | 178.7547 | 169.1 | 191.5 | 189.7 | 162.7 | 307.8 | 26.3 | 20.8 | 48.9 | 4.2 | 213.3 | 10.5 | 138.6 | 384.4 | 777.5 | 190.6 | 221.8 | 741.7 | 196.6 | 318.2 | 502.9 | 54.6 | 63.2 | 404.6 | 23.2 | 44.9 | 68.4 | 106.1 | 289.1 | 328.5 | 105.8 | 247.7 | 52.7 | 184.9 | 175.8 | 60.8 | 89.1 | 76.9 | 58.6
692 | 453 | 382.3 | 152.92 | 178.7547 | 169.4 | 190.7 | 190.4 | 163 | 307.3 | 26.3 | 20.8 | 49 | 4.3 | 219.1 | 10.9 | 139.2 | 381.6 | 786.9 | 191 | 221.5 | 741.5 | 197.2 | 318.5 | 506.1 | 54.8 | 63.4 | 405.9 | 23.3 | 45.1 | 68.5 | 106.5 | 288.8 | 327.6 | 106.6 | 247.6 | 52.8 | 185.2 | 175.8 | 60.9 | 89.4 | 77.2 | 58.7
693 | 454 | 383.3 | 153.32 | 179.2222 | 169.4 | 190.2 | 190.9 | 163.4 | 306.6 | 26.4 | 20.8 | 49 | 5.2 | 218 | 10.6 | 139.8 | 379.3 | 790.8 | 191.5 | 222.2 | 741.5 | 197.7 | 320.6 | 520.1 | 54.9 | 63.6 | 408.6 | 23.4 | 45.2 | 68.8 | 106.8 | 288.6 | 327.4 | 107.2 | 247.6 | 53 | 185.5 | 175.9 | 61.1 | 89.6 | 77.5 | 58.9
694 | 455 | 384.9 | 153.96 | 179.9704 | 169.9 | 190.5 | 190.9 | 163.5 | 307.2 | 26.4 | 20.8 | 49.1 | 5.2 | 221.1 | 9.6 | 140.4 | 377.5 | 795.6 | 191.9 | 222.8 | 740.9 | 198.2 | 322.2 | 525.7 | 55.1 | 63.8 | 410.7 | 23.4 | 45.4 | 69 | 107.1 | 288 | 331.3 | 106.8 | 247.8 | 53.1 | 185.9 | 176 | 61.3 | 89.7 | 77.8 | 59
695 | 456 | 385.5 | 154.2 | 180.2509 | 170.4 | 190.9 | 191.2 | 163.7 | 307.3 | 26.4 | 20.8 | 49.2 | 5.4 | 230.5 | 7.6 | 141 | 379 | 793 | 192.3 | 223.4 | 740.3 | 198.8 | 321.2 | 533.3 | 55.3 | 64 | 411 | 23.5 | 45.5 | 69.2 | 107.5 | 287.5 | 330.2 | 106.3 | 248.2 | 53.2 | 186.4 | 175.9 | 61.4 | 90.1 | 78 | 59.2
696 | 457 | 385.3 | 154.12 | 180.1574 | 170.1 | 190.9 | 191.8 | 164.1 | 306.8 | 26.5 | 20.7 | 49.3 | 4.3 | 205.5 | 7.4 | 141.6 | 383.6 | 793.4 | 192.8 | 224 | 740.3 | 199.3 | 319.6 | 524.3 | 55.5 | 64.2 | 410.1 | 23.6 | 45.7 | 69.2 | 107.8 | 288.2 | 329.4 | 106.3 | 249.5 | 53.3 | 186.7 | 177 | 61.6 | 90.4 | 78.2 | 59.3
697 | 458 | 383.6 | 153.44 | 179.3625 | 170 | 191.4 | 192 | 164.6 | 304.8 | 26.5 | 20.7 | 49.4 | 3.8 | 195.2 | 9.9 | 142.2 | 389.3 | 790.7 | 193.3 | 224.6 | 740 | 199.8 | 318 | 515.7 | 55.6 | 64.4 | 409 | 23.6 | 45.8 | 69.4 | 108.1 | 288 | 327.2 | 106 | 249.7 | 53.4 | 187.1 | 177.5 | 61.8 | 90.7 | 78.5 | 59.5
698 | 459 | 383.4 | 153.36 | 179.269 | 170.5 | 191.9 | 192.2 | 164.8 | 303.1 | 26.6 | 20.7 | 49.5 | 3.6 | 217.4 | 12 | 142.7 | 386.4 | 787.7 | 193.8 | 225.2 | 739.2 | 200.4 | 317.8 | 506.5 | 55.8 | 64.6 | 407.5 | 23.7 | 46 | 69.6 | 108.5 | 287.3 | 326.2 | 106.4 | 250.1 | 53.6 | 187.4 | 177.4 | 62 | 90.9 | 78.8 | 59.7
699 | 460 | 384.3 | 153.72 | 179.6898 | 170.8 | 192 | 192.5 | 164.8 | 302 | 26.6 | 20.7 | 49.6 | 3.8 | 220.7 | 10.7 | 143.3 | 386.9 | 791.1 | 194.2 | 225.8 | 738.8 | 200.9 | 316.3 | 507.8 | 56 | 64.8 | 407.4 | 23.8 | 46.2 | 69.9 | 108.8 | 286.2 | 324.6 | 106.5 | 250.3 | 53.7 | 187.6 | 177.7 | 62.1 | 91.1 | 79.1 | 59.8
700 | 461 | 384.3 | 153.72 | 179.6898 | 170.6 | 191.9 | 192.9 | 164.8 | 299.8 | 26.7 | 20.7 | 49.7 | 4.1 | 204 | 8.1 | 143.9 | 390.3 | 800.4 | 194.7 | 226.5 | 739.1 | 201.4 | 315.4 | 507.9 | 56.2 | 65 | 408.1 | 23.8 | 46.3 | 70 | 109.2 | 286.3 | 324.4 | 106.6 | 250.4 | 53.8 | 188 | 178.2 | 62.4 | 91.3 | 79.4 | 60
701 | 462 | 383.4 | 153.36 | 179.269 | 171 | 192.6 | 192.5 | 164.8 | 299.4 | 26.7 | 20.7 | 49.8 | 4.1 | 255 | 7.3 | 144.5 | 391.7 | 794.5 | 195.2 | 227.2 | 739.4 | 201.9 | 315.8 | 509.8 | 56.3 | 65.2 | 408.5 | 23.9 | 46.4 | 70.1 | 109.5 | 288 | 324.5 | 106.7 | 251.5 | 53.9 | 188.2 | 178.7 | 62.5 | 91.6 | 79.7 | 60.1
702 | 463 | 382.1 | 152.84 | 178.6612 | 171.4 | 194.8 | 191.8 | 164.8 | 300.3 | 26.7 | 20.7 | 49.9 | 4.3 | 206.9 | 9.3 | 145 | 394.5 | 802.3 | 195.6 | 228 | 740 | 202.5 | 316.6 | 512.2 | 56.5 | 65.4 | 408.7 | 24 | 46.5 | 70.3 | 109.8 | 288.2 | 329.3 | 107.9 | 252.8 | 54.1 | 188.4 | 178.4 | 62.6 | 91.8 | 80 | 60.3
703 | 464 | 384.5 | 153.8 | 179.7833 | 171.6 | 196.4 | 191.7 | 165 | 302.3 | 26.8 | 20.7 | 50 | 4.9 | 205.7 | 11.9 | 145.6 | 403.3 | 807.9 | 196.1 | 229 | 740.5 | 203 | 315.3 | 508.7 | 56.7 | 65.7 | 408.9 | 24.1 | 46.6 | 70.4 | 110.2 | 289.3 | 329.4 | 107.9 | 254.4 | 54.2 | 189 | 178.1 | 62.6 | 92 | 80.2 | 60.5
704 | 465 | 383.2 | 153.28 | 179.1755 | 171.7 | 197 | 191.2 | 165.2 | 303.8 | 26.8 | 20.7 | 50.1 | 5 | 205 | 11.8 | 146.2 | 402 | 812.5 | 196.6 | 229.8 | 740.5 | 203.5 | 314.1 | 511.1 | 56.9 | 65.9 | 408.5 | 24.1 | 46.7 | 70.8 | 110.5 | 288.4 | 330.6 | 108.4 | 255 | 54.4 | 189.5 | 178.6 | 62.7 | 92.1 | 80.5 | 60.6
705 | 466 | 379.8 | 151.92 | 177.5857 | 171.8 | 196.7 | 190.9 | 165.5 | 309.6 | 26.8 | 20.7 | 50.2 | 4.8 | 190.7 | 11.5 | 146.8 | 397.4 | 802 | 197.1 | 230.4 | 739.6 | 204 | 313.7 | 506.5 | 57 | 66.1 | 407.6 | 24.2 | 46.8 | 71 | 110.8 | 289.4 | 333.4 | 109.4 | 256.9 | 54.5 | 189.9 | 179.3 | 62.9 | 92.2 | 80.8 | 60.8
706 | 467 | 381.8 | 152.72 | 178.5209 | 172.2 | 196.6 | 191 | 165.5 | 309.4 | 26.8 | 20.7 | 50.3 | 4.5 | 199.3 | 10.9 | 147.3 | 394.4 | 813 | 197.5 | 231 | 739.3 | 204.5 | 312.8 | 500.2 | 57.2 | 66.3 | 406.1 | 24.3 | 46.9 | 71.3 | 111.2 | 287.4 | 329.4 | 108.1 | 256.8 | 54.6 | 189.9 | 179.3 | 63 | 92.4 | 81.1 | 60.9
707 | 468 | 382.4 | 152.96 | 178.8014 | 172.7 | 196.1 | 191.5 | 165.9 | 308.5 | 26.8 | 20.7 | 50.4 | 4.7 | 224.6 | 9.2 | 147.9 | 392.6 | 820.5 | 197.8 | 231.6 | 740 | 205 | 313.1 | 512.9 | 57.4 | 66.5 | 408.4 | 24.4 | 47 | 71.5 | 111.5 | 286.7 | 330.9 | 108.9 | 256.6 | 54.8 | 190 | 179.1 | 63.1 | 92.6 | 81.4 | 61.1
708 | 469 | 383.1 | 153.24 | 179.1287 | 172.4 | 195.2 | 191.8 | 166.1 | 311.5 | 26.8 | 20.7 | 50.5 | 4.7 | 213.4 | 9 | 148.5 | 391.8 | 820.4 | 198.1 | 231.9 | 740.6 | 205.5 | 316.7 | 528.6 | 57.6 | 66.7 | 412.6 | 24.4 | 47.2 | 71.8 | 111.8 | 287.6 | 336.1 | 110.1 | 257.3 | 54.9 | 190.4 | 179.4 | 63.2 | 92.6 | 81.7 | 61.2
709 | 470 | 381.3 | 152.52 | 178.2871 | 172.3 | 194.4 | 192 | 166.1 | 315.7 | 26.8 | 20.7 | 50.7 | 4.5 | 199.4 | 12 | 149.1 | 392.2 | 815.4 | 198.4 | 232.4 | 740.5 | 206 | 320.6 | 533.1 | 57.8 | 66.9 | 415.3 | 24.5 | 47.3 | 71.9 | 112.2 | 289.5 | 338.7 | 112 | 258.1 | 55 | 190.8 | 179.2 | 63.2 | 92.7 | 82 | 61.4
710 | 471 | 383.9 | 153.56 | 179.5028 | 172.7 | 193.9 | 192.1 | 166.2 | 318.7 | 26.8 | 20.7 | 50.8 | 4.5 | 216.9 | 12.9 | 149.7 | 395.1 | 816.8 | 198.7 | 233 | 740.2 | 206.5 | 324.2 | 542 | 57.9 | 67.1 | 417.9 | 24.6 | 47.4 | 72 | 112.5 | 290.5 | 340.2 | 111.8 | 259 | 55.1 | 190.6 | 179.5 | 63.5 | 93 | 82.3 | 61.6
711 | 472 | 381.1 | 152.44 | 178.1936 | 172.9 | 193.6 | 192.3 | 166 | 320.9 | 26.8 | 20.7 | 50.9 | 4.5 | 215.5 | 14.8 | 150.3 | 398.3 | 809.5 | 199 | 233.6 | 740.5 | 207 | 326.7 | 545 | 58.1 | 67.3 | 420.8 | 24.7 | 47.6 | 72 | 112.8 | 292 | 340.8 | 112.2 | 259.9 | 55.2 | 190.7 | 179.6 | 63.7 | 93 | 82.5 | 61.7
712 | 473 | 379 | 151.6 | 177.2117 | 173.1 | 193.2 | 192.3 | 165.9 | 320.2 | 26.8 | 20.7 | 50.9 | 4.1 | 196.5 | 13.6 | 150.9 | 398 | 808.7 | 199.3 | 234.1 | 740.5 | 207.5 | 326.3 | 541.7 | 58.3 | 67.5 | 420.3 | 24.7 | 47.7 | 72.2 | 113.2 | 293.6 | 339.7 | 113.6 | 259.6 | 55.3 | 190.9 | 179.6 | 63.8 | 93.3 | 82.8 | 61.9
713 | 474 | 377.5 | 151 | 176.5103 | 173.3 | 194 | 192.4 | 165.7 | 317.9 | 26.9 | 20.7 | 51 | 3.6 | 180.6 | 11.6 | 151.6 | 397.8 | 824.5 | 199.7 | 234.6 | 740.6 | 208 | 327.6 | 544.7 | 58.5 | 67.7 | 421.9 | 24.8 | 47.8 | 72.4 | 113.5 | 293.3 | 339.5 | 113.5 | 258.8 | 55.5 | 191 | 179.8 | 63.9 | 93.5 | 83.1 | 62
714 | 475 | 379.8 | 151.92 | 177.5857 | 173.4 | 195.5 | 192.1 | 165.3 | 318 | 27 | 20.7 | 51 | 4 | 198.4 | 16.2 | 152.2 | 398 | 816.6 | 200 | 235.1 | 741 | 208.5 | 329.1 | 540.2 | 58.7 | 68 | 421.2 | 24.9 | 47.9 | 72.7 | 113.9 | 293.6 | 339.4 | 114 | 259.7 | 55.6 | 191.7 | 180.1 | 64.1 | 93.6 | 83.4 | 62.2
715 | 476 | 380.6 | 152.24 | 177.9598 | 173.1 | 196.2 | 191.7 | 165.1 | 317.4 | 26.9 | 20.7 | 51 | 4.4 | 194.8 | 13.8 | 152.9 | 396.5 | 802.3 | 200.4 | 235.5 | 740.6 | 209 | 327.7 | 532.2 | 58.9 | 68.2 | 419 | 24.9 | 48 | 73 | 114.3 | 293.5 | 339.1 | 112.6 | 260.9 | 55.7 | 192.4 | 179.8 | 64.3 | 93.7 | 83.7 | 62.4
716 | 477 | 380.4 | 152.16 | 177.8663 | 172.9 | 196.3 | 191.9 | 165.2 | 320 | 26.9 | 20.7 | 51 | 4.1 | 206.7 | 15 | 153.5 | 396.5 | 791.9 | 200.7 | 235.9 | 740.1 | 209.5 | 329.7 | 547 | 59.1 | 68.4 | 420.3 | 25 | 48.2 | 73.4 | 114.6 | 294.2 | 342.6 | 112.3 | 262 | 55.9 | 192.5 | 179.9 | 64.3 | 93.8 | 83.9 | 62.5
717 | 478 | 379.2 | 151.68 | 177.3052 | 172.8 | 196 | 192.7 | 165.5 | 323.9 | 26.9 | 20.7 | 51 | 3.8 | 192.4 | 15.7 | 154.2 | 400 | 789.8 | 201.1 | 236.2 | 740.6 | 210 | 332.4 | 550 | 59.2 | 68.6 | 424.6 | 25.1 | 48.3 | 73.4 | 115 | 295.5 | 344.1 | 114.9 | 262.5 | 56 | 192.4 | 180.4 | 64.4 | 94.1 | 84.2 | 62.7
718 | 479 | 381.3 | 152.52 | 178.2871 | 172.9 | 195.6 | 193 | 165.8 | 324 | 26.9 | 20.7 | 51.1 | 3.9 | 192.6 | 14 | 154.8 | 403.4 | 779.7 | 201.5 | 236.6 | 740.8 | 210.5 | 331.9 | 542.4 | 59.4 | 68.8 | 424.9 | 25.2 | 48.4 | 73.6 | 115.3 | 295.7 | 345.2 | 115 | 263 | 56.1 | 192.2 | 180.3 | 64.6 | 94.3 | 84.5 | 62.8
719 | 480 | 384 | 153.6 | 179.5496 | 172.8 | 196.3 | 192.5 | 166.2 | 319.9 | 26.9 | 20.7 | 51.1 | 3.7 | 189 | 10.4 | 155.5 | 409.7 | 773 | 201.9 | 236.8 | 740.9 | 211 | 331.5 | 539 | 59.6 | 69 | 425.8 | 25.3 | 48.6 | 73.7 | 115.7 | 294.9 | 342.2 | 114.5 | 262.5 | 56.2 | 192.3 | 180.7 | 64.7 | 94.5 | 84.8 | 63
720 | 481 | 384.3 | 153.72 | 179.6898 | 173.2 | 197.9 | 192.9 | 166.5 | 318.8 | 27 | 20.7 | 51.2 | 3.5 | 204.1 | 9.6 | 156.1 | 413.7 | 764.9 | 202.4 | 237.1 | 741.7 | 211.5 | 332.5 | 540.4 | 59.8 | 69.2 | 427.1 | 25.3 | 48.8 | 73.9 | 116.1 | 295.1 | 341.6 | 116.2 | 262.2 | 56.3 | 192.8 | 181.3 | 64.9 | 94.6 | 85 | 63.1
721 | 482 | 382.9 | 153.16 | 179.0352 | 173.8 | 199.1 | 193.2 | 166.8 | 318.6 | 27 | 20.7 | 51.2 | 4.3 | 190.8 | 11.1 | 156.7 | 415.3 | 753.5 | 202.8 | 237.3 | 742.2 | 212 | 336.4 | 550.7 | 60 | 69.4 | 432.8 | 25.4 | 48.9 | 74.1 | 116.4 | 295.2 | 341.8 | 117.4 | 261.2 | 56.5 | 193.1 | 182.1 | 65 | 94.8 | 85.3 | 63.3
722 | 483 | 382.5 | 153 | 178.8482 | 174.2 | 198.3 | 193.4 | 167.2 | 319.4 | 27.1 | 20.7 | 51.3 | 4.1 | 200.5 | 10.6 | 157.3 | 418.6 | 743.1 | 203.3 | 237.7 | 742.1 | 212.5 | 339.2 | 553.4 | 60.2 | 69.7 | 437.2 | 25.5 | 49.1 | 74.4 | 116.8 | 295.8 | 342.9 | 119 | 261.7 | 56.6 | 193.5 | 182.5 | 65.3 | 95.1 | 85.6 | 63.5
723 | 484 | 379.5 | 151.8 | 177.4455 | 174.5 | 197.4 | 193.3 | 167.5 | 318.2 | 27.1 | 20.7 | 51.4 | 4.1 | 198 | 8.5 | 157.9 | 421.9 | 738.4 | 203.7 | 238 | 742.3 | 213 | 340.1 | 553.6 | 60.4 | 69.9 | 437.4 | 25.6 | 49.2 | 74.5 | 117.2 | 295.7 | 340.6 | 117.9 | 261 | 56.7 | 193.7 | 183.1 | 65.5 | 95.3 | 85.8 | 63.6
724 | 485 | 381.5 | 152.6 | 178.3806 | 174.9 | 196.8 | 193.4 | 168 | 315.7 | 27.1 | 20.7 | 51.5 | 3.6 | 198.3 | 9.2 | 158.5 | 420.8 | 729.1 | 204.1 | 238.4 | 741.8 | 213.6 | 341 | 550.1 | 60.6 | 70.1 | 438.1 | 25.6 | 49.4 | 74.6 | 117.6 | 295.4 | 341.7 | 118.7 | 260.6 | 56.8 | 193.9 | 183.3 | 65.7 | 95.4 | 86 | 63.8
725 | 486 | 381.1 | 152.44 | 178.1936 | 176.1 | 196.8 | 193.6 | 168.8 | 317.5 | 27.2 | 20.7 | 51.6 | 3.6 | 200.7 | 11.9 | 159.1 | 426.6 | 731.3 | 204.6 | 238.7 | 742 | 214.1 | 341.7 | 551.4 | 60.8 | 70.3 | 440.8 | 25.7 | 49.5 | 74.7 | 117.9 | 296.2 | 341.5 | 120.3 | 260.9 | 57 | 194 | 183.5 | 65.9 | 95.7 | 86.3 | 63.9
726 | 487 | 381.8 | 152.72 | 178.5209 | 177 | 197.1 | 193.7 | 168.9 | 317.5 | 27.3 | 20.7 | 51.6 | 4.4 | 197 | 12.3 | 159.8 | 429.7 | 732.5 | 205 | 239 | 742.5 | 214.6 | 340.7 | 546.6 | 60.9 | 70.5 | 440 | 25.8 | 49.8 | 74.9 | 118.3 | 296.1 | 339.2 | 120.1 | 260.7 | 57.1 | 194 | 183.7 | 66.2 | 95.9 | 86.5 | 64.1
727 | 488 | 380.3 | 152.12 | 177.8195 | 177.1 | 197.4 | 193.9 | 168.8 | 315.9 | 27.3 | 20.7 | 51.7 | 4.7 | 188.3 | 11.7 | 160.5 | 434.2 | 731.6 | 205.4 | 239.4 | 742.4 | 215.1 | 340.8 | 544 | 61.1 | 70.7 | 439.3 | 25.9 | 50 | 75.1 | 118.7 | 296.6 | 338.8 | 119.6 | 261.6 | 57.2 | 194 | 183.7 | 66.5 | 96.1 | 86.7 | 64.2
728 | 489 | 381.5 | 152.6 | 178.3806 | 177.3 | 197.3 | 193.6 | 169 | 315.9 | 27.4 | 20.7 | 51.8 | 5 | 186 | 12.4 | 161.2 | 434.2 | 739.6 | 205.9 | 239.8 | 742.5 | 215.6 | 338.9 | 533.5 | 61.3 | 70.9 | 438.4 | 26 | 50.2 | 75.3 | 119.1 | 296.5 | 336.2 | 119.1 | 262.4 | 57.4 | 194.1 | 183.6 | 66.7 | 96.3 | 87 | 64.4
729 | 490 | 383.7 | 153.48 | 179.4093 | 178.5 | 197.2 | 193.5 | 169 | 313.5 | 27.4 | 20.7 | 51.8 | 4.7 | 172.4 | 10.3 | 162 | 435.7 | 723.2 | 206.3 | 240.2 | 742.8 | 216.1 | 337.9 | 529.1 | 61.5 | 71.1 | 440 | 26 | 50.3 | 75.5 | 119.5 | 296.1 | 335.3 | 120.5 | 261.8 | 57.5 | 194.1 | 183.1 | 67 | 96.4 | 87.3 | 64.5
730 | 491 | 383.2 | 153.28 | 179.1755 | 179.5 | 196.5 | 193.6 | 169.1 | 313 | 27.4 | 20.7 | 52 | 4.8 | 187.1 | 8.3 | 162.9 | 431 | 716.9 | 206.7 | 240.6 | 742.2 | 216.6 | 335.9 | 522.2 | 61.7 | 71.4 | 439.8 | 26.1 | 50.4 | 75.7 | 119.9 | 296.1 | 334.5 | 121.9 | 261.8 | 57.6 | 194.1 | 182.9 | 67 | 96.6 | 87.5 | 64.7
731 | 492 | 382.3 | 152.92 | 178.7547 | 179.8 | 196 | 193.5 | 168.8 | 311.1 | 27.5 | 20.7 | 52.1 | 5.8 | 204.8 | 11 | 163.7 | 430.2 | 726.6 | 207.2 | 241 | 741.6 | 217.2 | 335 | 516.6 | 61.9 | 71.6 | 439.8 | 26.2 | 50.5 | 75.8 | 120.2 | 295 | 332.6 | 121.2 | 262 | 57.8 | 194.3 | 183 | 67.2 | 96.9 | 87.7 | 64.9
732 | 493 | 382.8 | 153.12 | 178.9885 | 180.6 | 195 | 193.7 | 168.9 | 310.3 | 27.6 | 20.7 | 52.2 | 5.5 | 198.4 | 14.4 | 164.6 | 429 | 727.2 | 207.6 | 241.5 | 741.5 | 217.7 | 334.6 | 511.2 | 62.1 | 71.8 | 440.5 | 26.3 | 50.7 | 75.9 | 120.6 | 295.1 | 334.7 | 122.1 | 262.8 | 57.9 | 194.7 | 183 | 67.5 | 97 | 88 | 65
733 | 494 | 382 | 152.8 | 178.6144 | 181.5 | 194.1 | 193.7 | 169.3 | 311.9 | 27.7 | 20.7 | 52.2 | 4.8 | 197.9 | 14.4 | 165.4 | 428.4 | 728.9 | 208 | 241.9 | 741.3 | 218.2 | 335.1 | 511.1 | 62.3 | 72 | 442 | 26.4 | 50.9 | 76.1 | 121 | 294.8 | 335.6 | 121.8 | 263.4 | 58 | 195.4 | 183.2 | 67.7 | 97.2 | 88.2 | 65.2
734 | 495 | 382.2 | 152.88 | 178.7079 | 181.9 | 194.1 | 194 | 169.8 | 313.2 | 27.8 | 20.7 | 52.3 | 4.3 | 232.5 | 11.3 | 166.3 | 426 | 730.3 | 208.4 | 242.3 | 741.1 | 218.7 | 337.8 | 516.9 | 62.5 | 72.2 | 444 | 26.5 | 51 | 76.4 | 121.4 | 294.7 | 338 | 122.4 | 263.5 | 58.2 | 195.2 | 183.7 | 67.8 | 97.5 | 88.4 | 65.4
735 | 496 | 382 | 152.8 | 178.6144 | 181.8 | 193.4 | 194.4 | 170.3 | 313.4 | 27.8 | 20.7 | 52.4 | 4.7 | 292.8 | 6.4 | 167.2 | 436.3 | 740.1 | 208.8 | 242.7 | 740.5 | 219.2 | 336.6 | 513.1 | 62.7 | 72.4 | 444.2 | 26.5 | 51.2 | 76.5 | 121.8 | 294.4 | 337.6 | 122.7 | 263 | 58.3 | 195.3 | 183.5 | 67.9 | 97.6 | 88.7 | 65.6
736 | 497 | 383.3 | 153.32 | 179.2222 | 181.9 | 194.3 | 194.9 | 170.7 | 313.5 | 27.9 | 20.7 | 52.5 | 4.4 | 248.9 | 3.8 | 168.1 | 449.3 | 755.4 | 209.2 | 243.2 | 740.8 | 219.7 | 335.6 | 508.5 | 62.9 | 72.7 | 444.4 | 26.6 | 51.4 | 76.9 | 122.2 | 294 | 337 | 123.6 | 262.8 | 58.5 | 195.5 | 183.8 | 68 | 97.9 | 88.9 | 65.7
737 | 498 | 382.4 | 152.96 | 178.8014 | 182.2 | 195.6 | 194.9 | 170.9 | 313.1 | 28 | 20.7 | 52.5 | 3.6 | 189.9 | 6.4 | 168.9 | 461.7 | 766.1 | 209.6 | 243.7 | 741.9 | 220.2 | 336.5 | 503.2 | 63.1 | 72.9 | 444.4 | 26.7 | 51.5 | 77 | 122.6 | 294 | 337.3 | 122.2 | 263.2 | 58.6 | 195.4 | 184.2 | 68.1 | 98.1 | 89.2 | 65.9
738 | 499 | 382.1 | 152.84 | 178.6612 | 182.2 | 197.4 | 195.1 | 171 | 312.3 | 28 | 20.7 | 52.6 | 3.8 | 215.3 | 7.8 | 169.8 | 456.4 | 781.3 | 210 | 244.2 | 742.6 | 220.7 | 337 | 501.6 | 63.2 | 73.1 | 444.2 | 26.8 | 51.7 | 77 | 123 | 293.6 | 334.2 | 121.2 | 263.1 | 58.7 | 195.3 | 184.3 | 68.3 | 98.4 | 89.4 | 66
739 | 500 | 381.2 | 152.48 | 178.2403 | 182.3 | 199 | 195.2 | 171.3 | 311.3 | 28.1 | 20.7 | 52.6 | 4.3 | 183.9 | 6.3 | 170.6 | 455.2 | 778.4 | 210.3 | 244.8 | 742.8 | 221.2 | 335.8 | 497.1 | 63.4 | 73.3 | 442.8 | 26.9 | 51.8 | 77.2 | 123.4 | 293.6 | 334 | 119.8 | 263.7 | 58.8 | 195.2 | 184.7 | 68.5 | 98.6 | 89.7 | 66.2
740 | 501 | 380.4 | 152.16 | 177.8663 | 182.5 | 199.4 | 194.8 | 171.8 | 311.1 | 28.2 | 20.7 | 52.7 | 4.6 | 235 | 5.3 | 171.4 | 459 | 785.5 | 210.7 | 245.3 | 743.6 | 221.7 | 335.8 | 496.9 | 63.6 | 73.5 | 442.9 | 27 | 52 | 77.3 | 123.8 | 293.6 | 335.5 | 121.1 | 265 | 59 | 195.3 | 184.8 | 68.7 | 98.8 | 89.9 | 66.3
741 | 502 | 382.2 | 152.88 | 178.7079 | 182.4 | 200.5 | 194.3 | 172 | 312 | 28.3 | 20.7 | 52.8 | 5.2 | 214.4 | 6.7 | 172.2 | 469.7 | 795.9 | 211 | 245.9 | 745 | 222.2 | 338.3 | 501.5 | 63.8 | 73.7 | 443.9 | 27.1 | 52.1 | 77.5 | 124.2 | 294.9 | 336.9 | 121.3 | 266.4 | 59.1 | 195.4 | 185 | 68.9 | 99.2 | 90.2 | 66.5
742 | 503 | 381.4 | 152.56 | 178.3339 | 181.7 | 202.4 | 193.7 | 172.2 | 311.8 | 28.3 | 20.7 | 52.9 | 4.1 | 222.5 | 8.2 | 172.9 | 461.1 | 793.4 | 211.4 | 246.5 | 745.4 | 222.6 | 337.4 | 495.8 | 64 | 74 | 442 | 27.1 | 52.3 | 77.6 | 124.6 | 295.9 | 336.1 | 121.7 | 266.8 | 59.3 | 195.3 | 185 | 68.9 | 99.3 | 90.5 | 66.7
743 | 504 | 381 | 152.4 | 178.1468 | 181.4 | 202.5 | 193.3 | 172.3 | 311.2 | 28.4 | 20.7 | 52.9 | 3.8 | 212.6 | 8.8 | 173.6 | 452.9 | 806.2 | 211.7 | 247 | 745.8 | 223.1 | 334.9 | 488.1 | 64.2 | 74.2 | 439.7 | 27.2 | 52.4 | 77.9 | 125 | 295.4 | 334.1 | 121.8 | 267.3 | 59.4 | 195.3 | 184.8 | 68.9 | 99.5 | 90.9 | 66.8
744 | 505 | 383.1 | 153.24 | 179.1287 | 180.9 | 203.9 | 192.8 | 172.1 | 311.2 | 28.4 | 20.7 | 53.1 | 3.8 | 244.5 | 7.6 | 174.2 | 449.8 | 801.4 | 212.1 | 247.5 | 746.2 | 223.6 | 333 | 485.8 | 64.4 | 74.4 | 438.7 | 27.3 | 52.6 | 78.1 | 125.5 | 294.1 | 334.3 | 121.6 | 267.7 | 59.6 | 195.7 | 184.6 | 69.1 | 99.7 | 91.2 | 67
745 | 506 | 381.8 | 152.72 | 178.5209 | 180.1 | 203.3 | 192.9 | 172.1 | 311.6 | 28.4 | 20.7 | 53.1 | 3.7 | 243.8 | 6.3 | 174.8 | 444.8 | 793.9 | 212.4 | 248 | 746.2 | 224.1 | 333.2 | 485.2 | 64.6 | 74.6 | 438.3 | 27.4 | 52.7 | 78.2 | 125.9 | 293.7 | 337 | 122.7 | 267.4 | 59.7 | 195.5 | 184.8 | 69.2 | 99.8 | 91.4 | 67.1
746 | 507 | 382 | 152.8 | 178.6144 | 179.5 | 201.8 | 193.2 | 171.8 | 313.4 | 28.5 | 20.6 | 53.1 | 3.7 | 241.2 | 6.5 | 175.3 | 439.6 | 790.2 | 212.8 | 248.4 | 746.9 | 224.6 | 333.9 | 488 | 64.8 | 74.8 | 438.6 | 27.5 | 52.9 | 78.4 | 126.3 | 293.1 | 337.8 | 124.7 | 267.6 | 59.8 | 195.5 | 184.5 | 69.3 | 99.8 | 91.7 | 67.3
747 | 508 | 382.2 | 152.88 | 178.7079 | 179.1 | 200 | 193.5 | 171.1 | 312.9 | 28.5 | 20.6 | 53.2 | 4.5 | 233.1 | 6.3 | 175.8 | 434.7 | 777.9 | 213.1 | 248.8 | 747.9 | 225 | 335.3 | 494.9 | 65 | 75 | 441 | 27.6 | 53 | 78.7 | 126.7 | 292.6 | 338.1 | 126.3 | 267.1 | 60 | 195.7 | 184.1 | 69.5 | 100 | 91.9 | 67.4
748 | 509 | 382.2 | 152.88 | 178.7079 | 179 | 198.5 | 193.7 | 170.5 | 315.1 | 28.6 | 20.6 | 53.2 | 4.2 | 222.3 | 6.2 | 176.3 | 440.7 | 781.5 | 213.4 | 249.2 | 748.4 | 225.5 | 337.9 | 502.2 | 65.2 | 75.3 | 443.4 | 27.7 | 53.1 | 78.8 | 127.1 | 293.7 | 339.6 | 127.4 | 267.9 | 60.1 | 196.6 | 184.3 | 69.8 | 100.2 | 92.2 | 67.6
749 | 510 | 382.7 | 153.08 | 178.9417 | 179.4 | 197.7 | 193.9 | 170.6 | 315.7 | 28.6 | 20.6 | 53.3 | 4.2 | 209.7 | 7 | 176.7 | 437.4 | 774.2 | 213.8 | 249.6 | 749.1 | 226 | 338.9 | 505.5 | 65.4 | 75.5 | 444.1 | 27.7 | 53.2 | 78.9 | 127.5 | 293.2 | 337.1 | 127 | 267.9 | 60.2 | 197.6 | 184.6 | 70 | 100.4 | 92.4 | 67.7
750 | 511 | 384.6 | 153.84 | 179.8301 | 179.9 | 196.9 | 194 | 170.7 | 316 | 28.6 | 20.6 | 53.4 | 4.9 | 216.6 | 8.6 | 177.2 | 436.9 | 768.6 | 214.1 | 250 | 750.1 | 226.4 | 339.8 | 510.6 | 65.5 | 75.7 | 445.4 | 27.8 | 53.3 | 79 | 128 | 293.4 | 338.8 | 128.2 | 267.7 | 60.4 | 197.6 | 184.7 | 70.2 | 100.7 | 92.7 | 68
751 | 512 | 384.6 | 153.84 | 179.8301 | 180.3 | 195.8 | 193.9 | 171.2 | 317.8 | 28.6 | 20.6 | 53.4 | 4.9 | 224.3 | 9 | 177.6 | 441.2 | 770.6 | 214.4 | 250.4 | 750.7 | 226.9 | 342.4 | 514.1 | 65.7 | 75.9 | 445.6 | 27.9 | 53.5 | 79.3 | 128.4 | 294.3 | 338.2 | 128 | 268.6 | 60.5 | 197.6 | 184.7 | 70.2 | 100.9 | 92.9 | 68.1
752 | 513 | 382.8 | 153.12 | 178.9885 | 180.4 | 195.3 | 193.8 | 171.7 | 318.1 | 28.6 | 20.6 | 53.4 | 4.4 | 199.5 | 11.1 | 178 | 444.6 | 758.8 | 214.7 | 250.8 | 751.9 | 227.4 | 341.4 | 507.4 | 65.9 | 76.1 | 445.1 | 28 | 53.6 | 79.4 | 128.8 | 294.4 | 339 | 129 | 269.2 | 60.6 | 197.3 | 185.3 | 70.3 | 101 | 93.2 | 68.3
753 | 514 | 382.2 | 152.88 | 178.7079 | 180.1 | 196 | 194.1 | 172 | 319.4 | 28.7 | 20.6 | 53.4 | 5 | 206.4 | 13 | 178.4 | 442.5 | 755.3 | 215 | 251.2 | 752.7 | 227.8 | 341.9 | 510.5 | 66.1 | 76.4 | 446.5 | 28.1 | 53.7 | 79.5 | 129.2 | 295.1 | 339.9 | 131.3 | 269.5 | 60.8 | 197.2 | 185.2 | 70.5 | 101.2 | 93.4 | 68.4
754 | 515 | 382.1 | 152.84 | 178.6612 | 180.4 | 196.6 | 194.5 | 171.5 | 320.2 | 28.8 | 20.6 | 53.4 | 4.7 | 204.5 | 14.4 | 178.7 | 439.7 | 762 | 215.3 | 251.6 | 753.3 | 228.3 | 342.1 | 508 | 66.3 | 76.6 | 446.8 | 28.2 | 53.8 | 79.7 | 129.6 | 295.5 | 338.1 | 131.1 | 269.1 | 60.9 | 197 | 185.3 | 70.6 | 101.4 | 93.7 | 68.6
755 | 516 | 382.2 | 152.88 | 178.7079 | 181.2 | 195.7 | 194.2 | 171.5 | 320 | 28.8 | 20.6 | 53.5 | 4.5 | 209.2 | 16.4 | 179.1 | 439.1 | 762.6 | 215.7 | 251.9 | 753.9 | 228.7 | 343.8 | 517.1 | 66.5 | 76.8 | 448.5 | 28.3 | 53.9 | 80 | 130.1 | 296.3 | 341.5 | 131.3 | 269.6 | 61 | 197.1 | 185.3 | 70.8 | 101.7 | 93.9 | 68.8
756 | 517 | 383.2 | 153.28 | 179.1755 | 181.8 | 195.6 | 194 | 171.9 | 324.1 | 28.9 | 20.6 | 53.5 | 4.4 | 209.2 | 16.3 | 179.4 | 439.8 | 771.8 | 216 | 252.2 | 754.6 | 229.2 | 345.3 | 528 | 66.7 | 77 | 450.1 | 28.4 | 54 | 80.2 | 130.5 | 297.9 | 347.9 | 132.5 | 273.2 | 61.2 | 197.4 | 185.2 | 70.9 | 101.9 | 94.2 | 68.9
757 | 518 | 382.8 | 153.12 | 178.9885 | 182 | 197.7 | 194.3 | 172.2 | 324.2 | 29 | 20.6 | 53.6 | 5.4 | 205.9 | 15.2 | 179.8 | 442.8 | 761.1 | 216.3 | 252.5 | 755.1 | 229.7 | 346.3 | 534.7 | 66.9 | 77.2 | 450.6 | 28.4 | 54.1 | 80.3 | 130.9 | 298.7 | 348.2 | 131.6 | 273.9 | 61.3 | 197.6 | 185.2 | 71.1 | 102.2 | 94.5 | 69.1
758 | 519 | 382.8 | 153.12 | 178.9885 | 182.7 | 199.1 | 194.6 | 172.7 | 324.5 | 29 | 20.6 | 53.7 | 4.8 | 211.7 | 15.3 | 180.1 | 450.7 | 775 | 216.6 | 252.8 | 755 | 230.1 | 349.2 | 541.7 | 67.1 | 77.5 | 451.5 | 28.5 | 54.3 | 80.4 | 131.4 | 299.1 | 349 | 132.2 | 274.1 | 61.4 | 197.6 | 185.7 | 71.2 | 102.4 | 94.8 | 69.2
759 | 520 | 382.9 | 153.16 | 179.0352 | 183.5 | 201.2 | 194.6 | 172.7 | 325.5 | 29 | 20.6 | 53.7 | 5 | 206 | 14.4 | 180.5 | 461.7 | 788.2 | 216.9 | 253 | 755 | 230.6 | 349.5 | 542.4 | 67.3 | 77.7 | 451.5 | 28.6 | 54.4 | 80.5 | 131.8 | 300.2 | 354.3 | 133.4 | 274.9 | 61.6 | 198.1 | 185.8 | 71.3 | 102.8 | 95 | 69.4
760 | 521 | 381.9 | 152.76 | 178.5676 | 183.8 | 201.6 | 194.5 | 173.2 | 324.9 | 29.1 | 20.6 | 53.8 | 5.3 | 220 | 14.2 | 180.8 | 460.6 | 797.2 | 217.1 | 253.4 | 755.6 | 231 | 350.2 | 536.4 | 67.4 | 77.9 | 450.8 | 28.7 | 54.5 | 80.7 | 132.2 | 300.3 | 351.6 | 131.9 | 275.2 | 61.7 | 198.5 | 185.8 | 71.5 | 103 | 95.3 | 69.6
761 | 522 | 382.5 | 153 | 178.8482 | 183.6 | 201.7 | 194.5 | 173.7 | 321.9 | 29.2 | 20.6 | 53.8 | 5.9 | 199.4 | 12 | 181.2 | 475.3 | 791.8 | 217.4 | 253.8 | 756.1 | 231.5 | 350.7 | 539.6 | 67.6 | 78.2 | 451 | 28.8 | 54.6 | 81 | 132.7 | 300.4 | 351.1 | 130 | 275.5 | 61.8 | 198.8 | 186.4 | 71.7 | 103.2 | 95.6 | 69.7
762 | 523 | 383.3 | 153.32 | 179.2222 | 183.7 | 204.5 | 194.9 | 173.4 | 323.8 | 29.2 | 20.6 | 53.9 | 5.3 | 211 | 11.1 | 181.6 | 477.4 | 777.9 | 217.7 | 254.2 | 755.8 | 232 | 350.4 | 537.6 | 67.8 | 78.4 | 451.4 | 28.9 | 54.7 | 81.3 | 133.1 | 301.9 | 352.4 | 131.2 | 276.5 | 62 | 198.7 | 186.3 | 71.7 | 103.4 | 95.9 | 69.9
763 | 524 | 382.9 | 153.16 | 179.0352 | 183.9 | 205.2 | 194.8 | 173.4 | 323 | 29.3 | 20.6 | 53.9 | 4.7 | 211.7 | 9.3 | 182 | 475.5 | 762.4 | 217.9 | 254.6 | 755.2 | 232.4 | 351 | 537.3 | 68 | 78.6 | 454.2 | 29 | 54.8 | 81.4 | 133.5 | 300.3 | 349.1 | 131.6 | 276.1 | 62.1 | 198.8 | 186.1 | 71.9 | 103.6 | 96.2 | 70.1
764 | 525 | 383.3 | 153.32 | 179.2222 | 183.6 | 204.3 | 194.8 | 173.5 | 323.4 | 29.3 | 20.6 | 54 | 4.2 | 218.4 | 9.5 | 182.5 | 476.7 | 753.6 | 218.2 | 254.8 | 754.6 | 232.9 | 351.7 | 538.9 | 68.2 | 78.9 | 456.1 | 29.1 | 54.9 | 81.5 | 134 | 301.4 | 352.3 | 133.6 | 276.2 | 62.2 | 199 | 186.2 | 72 | 103.7 | 96.5 | 70.2
765 | 526 | 383.4 | 153.36 | 179.269 | 183.6 | 204.4 | 194.7 | 173.7 | 326.4 | 29.4 | 20.6 | 54 | 4.4 | 240 | 7.9 | 183 | 488.6 | 737.9 | 218.5 | 255.1 | 755.3 | 233.4 | 352.7 | 539 | 68.4 | 79.1 | 456.8 | 29.2 | 55 | 81.7 | 134.4 | 302.3 | 351.4 | 134.4 | 276 | 62.3 | 199 | 186.6 | 72.1 | 103.8 | 96.8 | 70.4
766 | 527 | 384.3 | 153.72 | 179.6898 | 183.7 | 204.5 | 194.4 | 173.8 | 325.4 | 29.4 | 20.6 | 54 | 5.1 | 222.8 | 10.4 | 183.6 | 482.1 | 728.5 | 218.8 | 255.6 | 756.4 | 233.8 | 352.1 | 536.5 | 68.6 | 79.3 | 458 | 29.3 | 55.1 | 81.9 | 134.9 | 302.1 | 349.7 | 134.9 | 275.6 | 62.5 | 199 | 187.1 | 72.2 | 103.9 | 97 | 70.6
767 | 528 | 383.4 | 153.36 | 179.269 | 183.9 | 204.3 | 194.4 | 174 | 326.6 | 29.4 | 20.6 | 54.1 | 4.5 | 218 | 16.1 | 184.1 | 475.4 | 716.7 | 219.1 | 255.9 | 756.8 | 234.3 | 353.5 | 536.4 | 68.8 | 79.6 | 460.3 | 29.4 | 55.3 | 82 | 135.3 | 302.4 | 353.3 | 136 | 275.7 | 62.6 | 198.9 | 187.1 | 72.3 | 104.1 | 97.3 | 70.7
768 | 529 | 383 | 153.2 | 179.082 | 184.5 | 203.3 | 194.5 | 173.8 | 325.7 | 29.3 | 20.6 | 54.1 | 5.4 | 216.8 | 16.5 | 184.8 | 468.8 | 698.6 | 219.4 | 256.2 | 756.5 | 234.8 | 352.5 | 526.4 | 69 | 79.8 | 459.6 | 29.4 | 55.5 | 82.1 | 135.8 | 303 | 351.6 | 137.4 | 275.2 | 62.7 | 198.9 | 187.1 | 72.4 | 104.3 | 97.5 | 70.8
769 | 530 | 383.7 | 153.48 | 179.4093 | 185 | 202.5 | 194.7 | 174 | 323.6 | 29.3 | 20.6 | 54.1 | 5.4 | 219.3 | 17.3 | 185.4 | 460.5 | 669.7 | 219.7 | 256.5 | 755.2 | 235.2 | 349.6 | 517.1 | 69.2 | 80 | 458.4 | 29.5 | 55.6 | 82.3 | 136.2 | 302.2 | 345.1 | 137.6 | 274.2 | 62.8 | 198.9 | 186.9 | 72.5 | 104.6 | 97.7 | 71
770 | 531 | 383.4 | 153.36 | 179.269 | 186.2 | 201.5 | 194.7 | 174.5 | 317.6 | 29.2 | 20.6 | 54.1 | 5.1 | 217.4 | 17.5 | 186.1 | 457.1 | 663.9 | 220.1 | 256.8 | 754.4 | 235.7 | 347.4 | 511.6 | 69.4 | 80.3 | 458.2 | 29.6 | 55.8 | 82.6 | 136.7 | 299.9 | 339.8 | 136.4 | 272.6 | 63 | 199.2 | 186.6 | 72.7 | 104.7 | 97.9 | 71.2
771 | 532 | 384.2 | 153.68 | 179.6431 | 186.7 | 200.5 | 194.5 | 174.7 | 315.6 | 29.1 | 20.6 | 54.1 | 5.3 | 210.1 | 16.9 | 186.8 | 448.8 | 677.4 | 220.4 | 257 | 753.6 | 236.1 | 346.6 | 512 | 69.6 | 80.5 | 458.8 | 29.7 | 55.9 | 82.7 | 137.1 | 299.9 | 341.9 | 136.5 | 273.9 | 63.1 | 199.8 | 186.5 | 73 | 104.9 | 98.1 | 71.3
772 | 533 | 383.2 | 153.28 | 179.1755 | 187.2 | 200.6 | 195.1 | 175.1 | 312.6 | 29.1 | 20.6 | 54.2 | 5.2 | 213.3 | 16.4 | 187.5 | 449.3 | 689.7 | 220.7 | 257.3 | 753.1 | 236.6 | 345.1 | 511 | 69.8 | 80.8 | 460.4 | 29.8 | 56 | 82.8 | 137.5 | 299 | 338 | 135.7 | 273.8 | 63.2 | 200.2 | 186.7 | 73.2 | 105.1 | 98.3 | 71.5
773 | 534 | 383.2 | 153.28 | 179.1755 | 188.4 | 201.1 | 195.7 | 175.4 | 311.5 | 29.1 | 20.6 | 54.3 | 4.5 | 207 | 15.6 | 188.3 | 443.3 | 697.4 | 221 | 257.6 | 753.3 | 237.1 | 343.4 | 508.8 | 70 | 81 | 460.2 | 29.9 | 56.2 | 82.9 | 138 | 298.7 | 337.6 | 135.2 | 273.6 | 63.4 | 200.4 | 187.4 | 73.3 | 105.3 | 98.5 | 71.7
774 | 535 | 382.8 | 153.12 | 178.9885 | 189.6 | 201.9 | 196.2 | 175.8 | 313.8 | 29.2 | 20.6 | 54.4 | 5.8 | 207.9 | 15.7 | 189 | 445 | 719.6 | 221.3 | 258 | 752.5 | 237.5 | 343.2 | 513.1 | 70.2 | 81.2 | 462 | 30 | 56.3 | 83.1 | 138.4 | 299.5 | 337.3 | 136 | 274.1 | 63.5 | 200.4 | 188 | 73.4 | 105.5 | 98.8 | 71.9
775 | 536 | 382.5 | 153 | 178.8482 | 190 | 201.9 | 196.5 | 176.3 | 314.6 | 29.2 | 20.6 | 54.4 | 5.7 | 206.5 | 14.7 | 189.7 | 450 | 717.3 | 221.7 | 258.4 | 751.7 | 238 | 346.4 | 525.2 | 70.4 | 81.5 | 465.7 | 30.1 | 56.5 | 83.4 | 138.9 | 299.1 | 335.5 | 136.3 | 274.3 | 63.6 | 200.8 | 188 | 73.6 | 105.6 | 99.1 | 72.1
776 | 537 | 383 | 153.2 | 179.082 | 190.2 | 201.2 | 196.7 | 176.5 | 314.7 | 29.3 | 20.6 | 54.6 | 5.5 | 210.8 | 15.9 | 190.5 | 446.9 | 715.7 | 222 | 258.7 | 750.4 | 238.4 | 348.9 | 533.5 | 70.6 | 81.7 | 466.9 | 30.2 | 56.6 | 83.6 | 139.3 | 299.6 | 335.6 | 137 | 274.6 | 63.8 | 201.2 | 188.6 | 73.8 | 105.8 | 99.3 | 72.2
777 | 538 | 383 | 153.2 | 179.082 | 190.7 | 202.1 | 197.1 | 176.3 | 313.8 | 29.4 | 20.6 | 54.7 | 6.1 | 213.3 | 17.1 | 191.2 | 446 | 725.6 | 222.3 | 259.1 | 749.4 | 238.9 | 353.3 | 543.7 | 70.8 | 81.9 | 469.8 | 30.3 | 56.7 | 83.8 | 139.7 | 299.8 | 336.6 | 137.4 | 274.7 | 63.9 | 201.5 | 189.1 | 74 | 106.1 | 99.6 | 72.4
778 | 539 | 383.6 | 153.44 | 179.3625 | 191.2 | 203.6 | 197.5 | 176.5 | 315.6 | 29.4 | 20.6 | 54.8 | 5.6 | 212.9 | 17.3 | 192 | 445.5 | 740.2 | 222.7 | 259.7 | 748.8 | 239.3 | 354.4 | 546.4 | 71 | 82.2 | 470 | 30.4 | 56.9 | 84 | 140.2 | 300.4 | 336.8 | 137.2 | 275.2 | 64 | 201.8 | 189.3 | 74.1 | 106.2 | 99.8 | 72.6
779 | 540 | 383.4 | 153.36 | 179.269 | 190.9 | 204.1 | 197.9 | 176.6 | 317.4 | 29.4 | 20.6 | 54.9 | 5.5 | 223.8 | 17.6 | 192.7 | 449.8 | 746 | 223 | 260.2 | 748.6 | 239.8 | 357 | 555.4 | 71.2 | 82.4 | 471.5 | 30.5 | 57 | 84.2 | 140.6 | 301 | 341.1 | 138.1 | 276.5 | 64.2 | 202 | 189.2 | 74.2 | 106.4 | 100 | 72.7
780 | 541 | 382.8 | 153.12 | 178.9885 | 190.6 | 203.7 | 198.6 | 176.5 | 321.8 | 29.4 | 20.6 | 55 | 6.1 | 228.2 | 13.2 | 193.5 | 449.2 | 747.8 | 223.3 | 260.7 | 748.1 | 240.2 | 358.7 | 555.3 | 71.4 | 82.6 | 471.5 | 30.6 | 57.2 | 84.4 | 141 | 301.5 | 345.1 | 139.7 | 278.8 | 64.3 | 201.9 | 189.8 | 74.2 | 106.7 | 100.3 | 72.9
781 | 542 | 381.1 | 152.44 | 178.1936 | 190.3 | 203.2 | 199.3 | 176.5 | 326 | 29.5 | 20.6 | 55.1 | 5.6 | 227.1 | 12.4 | 194.3 | 458.5 | 759.1 | 223.6 | 261.2 | 748.8 | 240.7 | 359.7 | 553 | 71.6 | 82.9 | 471.6 | 30.7 | 57.3 | 84.5 | 141.5 | 303 | 347.4 | 140.3 | 279.2 | 64.4 | 201.7 | 190.7 | 74.4 | 107 | 100.5 | 73.1
782 | 543 | 382.3 | 152.92 | 178.7547 | 189.6 | 202.9 | 200.2 | 176.3 | 326.2 | 29.5 | 20.6 | 55.3 | 4.2 | 240.5 | 10.3 | 195 | 460.9 | 758.4 | 223.9 | 261.7 | 750.4 | 241.1 | 359.9 | 548.2 | 71.8 | 83.1 | 471.3 | 30.8 | 57.5 | 84.8 | 141.9 | 303.7 | 346.2 | 139.3 | 278.8 | 64.5 | 201.7 | 191.2 | 74.5 | 107.2 | 100.8 | 73.2
783 | 544 | 383.9 | 153.56 | 179.5028 | 188.9 | 202.4 | 200.4 | 176.5 | 326.6 | 29.5 | 20.6 | 55.3 | 3.7 | 208.6 | 9.4 | 195.8 | 463.5 | 764 | 224.2 | 262.2 | 752.3 | 241.5 | 361.6 | 547.5 | 72 | 83.3 | 472.3 | 30.8 | 57.6 | 84.8 | 142.3 | 304.2 | 344.7 | 139.7 | 278.8 | 64.7 | 201.7 | 191 | 74.7 | 107.4 | 101.1 | 73.4
784 | 545 | 381.7 | 152.68 | 178.4741 | 188.9 | 202.3 | 200.2 | 176.6 | 328.6 | 29.6 | 20.6 | 55.3 | 4.5 | 241.1 | 9.3 | 196.5 | 461.7 | 759.6 | 224.5 | 262.7 | 754 | 242 | 362.2 | 546.5 | 72.2 | 83.6 | 474.4 | 30.9 | 57.7 | 85 | 142.8 | 306.8 | 348.3 | 142.1 | 278.7 | 64.8 | 201.7 | 190.7 | 74.8 | 107.7 | 101.4 | 73.5
785 | 546 | 381.6 | 152.64 | 178.4274 | 189.5 | 201.8 | 200.5 | 176.5 | 330 | 29.6 | 20.6 | 55.3 | 4.1 | 233.2 | 8.1 | 197.2 | 458.7 | 751.7 | 224.8 | 263.2 | 754.5 | 242.4 | 361.3 | 538.7 | 72.4 | 83.8 | 474.3 | 31 | 57.8 | 85.2 | 143.2 | 307.4 | 350.8 | 142.4 | 278.9 | 64.9 | 201.9 | 190.5 | 75 | 107.9 | 101.6 | 73.7
786 | 547 | 382.1 | 152.84 | 178.6612 | 189.6 | 201.8 | 200.7 | 176.6 | 331.2 | 29.7 | 20.6 | 55.2 | 3.8 | 253.1 | 9.2 | 197.9 | 451.3 | 749.5 | 225.2 | 263.6 | 753.8 | 242.8 | 358.6 | 527.8 | 72.6 | 84 | 472.8 | 31.1 | 57.9 | 85.4 | 143.6 | 308 | 351.5 | 142.3 | 279 | 65.1 | 202.6 | 190.5 | 75.2 | 108 | 101.9 | 73.8
787 | 548 | 382.4 | 152.96 | 178.8014 | 189.1 | 201.4 | 200.9 | 177.1 | 325.4 | 29.7 | 20.6 | 55.2 | 4.7 | 238.3 | 12.9 | 198.6 | 452.1 | 740.3 | 225.5 | 263.8 | 753.1 | 243.3 | 356.1 | 520.5 | 72.8 | 84.3 | 472.6 | 31.2 | 58 | 85.7 | 144.1 | 305.4 | 346.2 | 140.9 | 277.5 | 65.2 | 203 | 190.6 | 75.4 | 108.3 | 102.1 | 74
788 | 549 | 382.5 | 153 | 178.8482 | 188.2 | 201.3 | 201.3 | 177.6 | 320.2 | 29.7 | 20.6 | 55.2 | 5 | 252.7 | 15.5 | 199.2 | 457 | 744.1 | 225.7 | 264.3 | 754.4 | 243.7 | 353.4 | 510.3 | 73 | 84.5 | 471.9 | 31.3 | 58.2 | 85.9 | 144.5 | 303.6 | 341.4 | 140.3 | 276.2 | 65.3 | 203.1 | 190.8 | 75.7 | 108.5 | 102.3 | 74.2
789 | 550 | 382.6 | 153.04 | 178.8949 | 187.6 | 200.8 | 202 | 177.8 | 317 | 29.8 | 20.6 | 55.3 | 5 | 256.8 | 14.8 | 199.9 | 454.8 | 740.2 | 226.1 | 264.9 | 755.3 | 244.2 | 351.1 | 504.5 | 73.2 | 84.8 | 471.7 | 31.4 | 58.4 | 86 | 144.9 | 302.3 | 338.1 | 140.1 | 275.6 | 65.5 | 203 | 190.7 | 75.8 | 108.6 | 102.5 | 74.3
790 | 551 | 382.7 | 153.08 | 178.9417 | 187.6 | 200.8 | 201.9 | 178.5 | 315 | 29.8 | 20.6 | 55.3 | 4.9 | 257.1 | 12.5 | 200.5 | 449.1 | 731.3 | 226.4 | 265.4 | 756.4 | 244.6 | 350.3 | 498.8 | 73.4 | 85 | 472.4 | 31.5 | 58.5 | 86 | 145.4 | 301.1 | 335.8 | 140.1 | 275.7 | 65.6 | 202.8 | 190.6 | 76.2 | 108.7 | 102.7 | 74.5
791 | 552 | 381.1 | 152.44 | 178.1936 | 189 | 201.1 | 201.6 | 178.8 | 313.6 | 29.8 | 20.6 | 55.4 | 4.9 | 248.8 | 10.1 | 201.1 | 443.9 | 736.8 | 226.7 | 265.8 | 757.6 | 245.1 | 348.1 | 492.6 | 73.6 | 85.3 | 471.2 | 31.6 | 58.7 | 86.2 | 145.8 | 300.7 | 335.2 | 141.6 | 276.1 | 65.7 | 203.3 | 190.9 | 76.3 | 108.9 | 102.9 | 74.7
792 | 553 | 381.2 | 152.48 | 178.2403 | 190.3 | 200.9 | 201.7 | 179.2 | 314.5 | 29.9 | 20.6 | 55.4 | 4.5 | 227.3 | 8.9 | 201.7 | 441.8 | 742.7 | 226.9 | 266.1 | 758.8 | 245.5 | 347.3 | 494.9 | 73.8 | 85.5 | 471.5 | 31.7 | 58.8 | 86.5 | 146.2 | 300.1 | 335.9 | 142.4 | 276.4 | 65.9 | 203.4 | 191.2 | 76.5 | 109.1 | 103.1 | 74.8
793 | 554 | 381.1 | 152.44 | 178.1936 | 190.1 | 199.9 | 201.5 | 179.8 | 314.3 | 29.9 | 20.6 | 55.4 | 4.2 | 251.7 | 7.8 | 202.3 | 439.6 | 762.1 | 227.3 | 266.4 | 759.1 | 245.9 | 346.6 | 498.6 | 74 | 85.8 | 471.8 | 31.8 | 59 | 86.6 | 146.6 | 299.2 | 334.2 | 142.7 | 275.8 | 66 | 203.3 | 191.5 | 76.6 | 109.4 | 103.3 | 75
794 | 555 | 381.8 | 152.72 | 178.5209 | 190.1 | 199 | 201.5 | 180.4 | 315.6 | 30 | 20.6 | 55.5 | 4.6 | 233.1 | 8.6 | 202.9 | 437.5 | 757.7 | 227.6 | 266.7 | 759.3 | 246.4 | 346 | 500.5 | 74.2 | 86.1 | 473.3 | 31.9 | 59.1 | 86.8 | 147 | 299.7 | 335.4 | 143.8 | 275.8 | 66.1 | 203.3 | 191.7 | 76.7 | 109.6 | 103.6 | 75.1
795 | 556 | 384 | 153.6 | 179.5496 | 189.8 | 199 | 201.5 | 180.7 | 315.6 | 30 | 20.6 | 55.6 | 4.3 | 273.2 | 7.6 | 203.4 | 439.9 | 759.4 | 227.9 | 267 | 759.5 | 246.8 | 345.2 | 499.5 | 74.5 | 86.3 | 473 | 32 | 59.3 | 87 | 147.5 | 299 | 334.5 | 142.8 | 275.8 | 66.3 | 203.3 | 191.9 | 76.8 | 109.8 | 103.8 | 75.3
796 | 557 | 383.7 | 153.48 | 179.4093 | 189.6 | 198.9 | 201.7 | 180.7 | 315.2 | 30.1 | 20.6 | 55.6 | 3.8 | 248.2 | 8.9 | 204 | 444 | 757.8 | 228.2 | 267.4 | 760.5 | 247.2 | 344.7 | 501.8 | 74.7 | 86.6 | 474.3 | 32.1 | 59.4 | 87.2 | 147.9 | 298.9 | 334.6 | 142.1 | 276.8 | 66.4 | 203.2 | 191.9 | 77 | 110.2 | 104 | 75.4
797 | 558 | 381.5 | 152.6 | 178.3806 | 188.9 | 200.9 | 202.2 | 180.7 | 314.7 | 30.1 | 20.6 | 55.6 | 4.1 | 249.2 | 11.8 | 204.5 | 456.7 | 776.3 | 228.5 | 267.8 | 761.5 | 247.6 | 344.6 | 501.3 | 74.9 | 86.8 | 475.6 | 32.2 | 59.5 | 87.2 | 148.3 | 299.5 | 334.7 | 142 | 277.9 | 66.5 | 203.1 | 192 | 77.2 | 110.5 | 104.2 | 75.6
798 | 559 | 381.6 | 152.64 | 178.4274 | 188.3 | 203 | 202.2 | 180.5 | 316.4 | 30.1 | 20.6 | 55.7 | 6.3 | 273 | 10.6 | 205 | 471.6 | 789 | 228.8 | 268.2 | 762.9 | 248.1 | 346.4 | 512.2 | 75.1 | 87.1 | 476.8 | 32.3 | 59.6 | 87.3 | 148.7 | 300.7 | 336.7 | 142.7 | 279 | 66.7 | 203.1 | 191.7 | 77.4 | 110.7 | 104.5 | 75.8
799 | 560 | 381.5 | 152.6 | 178.3806 | 188.1 | 204.7 | 202.2 | 180.5 | 319.9 | 30.2 | 20.5 | 55.8 | 6.3 | 258.9 | 10.5 | 205.5 | 477.8 | 793.4 | 229.1 | 268.6 | 764.1 | 248.5 | 348.5 | 517.6 | 75.3 | 87.4 | 478.1 | 32.4 | 59.8 | 87.5 | 149.1 | 302.6 | 340.8 | 144.6 | 281 | 66.8 | 203.2 | 191.6 | 77.6 | 110.7 | 104.8 | 75.9
800 | 561 | 381.7 | 152.68 | 178.4741 | 188.1 | 205.9 | 202.5 | 180.4 | 321.7 | 30.2 | 20.5 | 55.9 | 4.6 | 256.4 | 16.3 | 206 | 475.6 | 783.1 | 229.4 | 268.8 | 764.2 | 248.9 | 349.1 | 522.9 | 75.5 | 87.6 | 478.8 | 32.5 | 59.9 | 87.7 | 149.5 | 303.3 | 340.3 | 144.7 | 281.5 | 66.9 | 203.3 | 191.5 | 77.8 | 111 | 105.1 | 76.1
801 | 562 | 382.6 | 153.04 | 178.8949 | 188.1 | 205.7 | 202.8 | 180.4 | 319.6 | 30.2 | 20.5 | 55.9 | 4.4 | 243.7 | 16.4 | 206.5 | 477.6 | 781.8 | 229.7 | 269.1 | 764.1 | 249.3 | 348.7 | 520.7 | 75.7 | 87.9 | 479 | 32.6 | 60 | 87.8 | 149.9 | 302.8 | 338.6 | 144.7 | 280.2 | 67.1 | 203.4 | 191.3 | 77.9 | 111.2 | 105.4 | 76.3
802 | 563 | 382.1 | 152.84 | 178.6612 | 188.2 | 205 | 202.8 | 180.6 | 319.9 | 30.2 | 20.5 | 55.9 | 5.1 | 253.8 | 15.5 | 207 | 483.5 | 770.2 | 230 | 269.3 | 764.2 | 249.7 | 347.2 | 524.6 | 75.9 | 88.2 | 479 | 32.7 | 60.2 | 88.1 | 150.4 | 302.9 | 339.4 | 145.7 | 279.9 | 67.2 | 203.8 | 191.4 | 78.1 | 111.4 | 105.7 | 76.4
803 | 564 | 383.7 | 153.48 | 179.4093 | 188.1 | 204 | 202.8 | 180.9 | 319.8 | 30.2 | 20.5 | 56 | 4.6 | 244 | 14.6 | 207.5 | 485.6 | 769.2 | 230.3 | 269.6 | 764.8 | 250.2 | 347.8 | 532.2 | 76.1 | 88.4 | 481 | 32.8 | 60.3 | 88.2 | 150.8 | 302.7 | 340.9 | 145.5 | 279.9 | 67.3 | 204 | 191.5 | 78.2 | 111.6 | 105.9 | 76.6
804 | 565 | 382.9 | 153.16 | 179.0352 | 188.3 | 202.9 | 203.8 | 180.9 | 323.1 | 30.2 | 20.5 | 56 | 5.2 | 249 | 12.8 | 208 | 483.9 | 761 | 230.6 | 270 | 765.3 | 250.6 | 349.4 | 537.9 | 76.3 | 88.7 | 482.7 | 32.9 | 60.4 | 88.4 | 151.2 | 303.7 | 341.8 | 146.7 | 280.2 | 67.5 | 204.1 | 191.9 | 78.2 | 111.8 | 106.1 | 76.8
805 | 566 | 381.1 | 152.44 | 178.1936 | 188.8 | 202 | 203.7 | 181.1 | 325.9 | 30.2 | 20.5 | 56 | 5.9 | 260.8 | 12.1 | 208.5 | 479.4 | 757.8 | 231 | 270.3 | 766.4 | 251 | 351.5 | 535.2 | 76.6 | 89 | 484.3 | 33 | 60.5 | 88.7 | 151.6 | 304.4 | 342.2 | 147.4 | 280.1 | 67.6 | 204.3 | 192.5 | 78.3 | 111.9 | 106.3 | 76.9
806 | 567 | 381.6 | 152.64 | 178.4274 | 189.2 | 201.8 | 203.5 | 181.3 | 324.7 | 30.3 | 20.5 | 56 | 4.8 | 260.6 | 11.9 | 209 | 474.7 | 764.7 | 231.2 | 270.7 | 768.2 | 251.4 | 352.3 | 528.4 | 76.8 | 89.3 | 484.3 | 33.1 | 60.6 | 88.7 | 152 | 304.9 | 341.3 | 147 | 280.1 | 67.7 | 204.4 | 193.5 | 78.4 | 112.3 | 106.6 | 77.1
807 | 568 | 381.2 | 152.48 | 178.2403 | 189.5 | 201.7 | 203.2 | 181.8 | 323.6 | 30.3 | 20.5 | 56 | 4 | 245.1 | 13.2 | 209.4 | 467.6 | 778.4 | 231.6 | 271.1 | 768.9 | 251.9 | 352.6 | 521 | 77 | 89.5 | 483.3 | 33.2 | 60.8 | 88.8 | 152.4 | 304.6 | 340.4 | 147.3 | 280.3 | 67.8 | 204.7 | 194 | 78.5 | 112.5 | 106.8 | 77.3
808 | 569 | 381.6 | 152.64 | 178.4274 | 189.5 | 200.8 | 203.6 | 182.2 | 321.6 | 30.3 | 20.5 | 56 | 4.5 | 256.1 | 14.6 | 209.9 | 473.7 | 782.8 | 231.9 | 271.4 | 769.4 | 252.3 | 351.4 | 519.1 | 77.2 | 89.8 | 483.4 | 33.3 | 60.9 | 89 | 152.8 | 304 | 337.6 | 147.6 | 280.2 | 68 | 205.2 | 194 | 78.6 | 112.7 | 107.1 | 77.4
809 | 570 | 378.6 | 151.44 | 177.0246 | 189.4 | 200.7 | 204.1 | 182.5 | 318.9 | 30.3 | 20.5 | 56 | 3.7 | 258.6 | 14.7 | 210.4 | 477.6 | 778 | 232.2 | 271.7 | 769.8 | 252.7 | 350.3 | 515.3 | 77.4 | 90.1 | 482.5 | 33.4 | 61.1 | 89.2 | 153.2 | 303.1 | 336 | 147.1 | 279.6 | 68.1 | 205.7 | 194.6 | 78.7 | 113 | 107.3 | 77.6
810 | 571 | 379.1 | 151.64 | 177.2584 | 189.4 | 200.9 | 204.2 | 183.1 | 319.7 | 30.3 | 20.5 | 56 | 4.2 | 270.1 | 13.9 | 210.9 | 472.4 | 763.3 | 232.5 | 272 | 768.9 | 253.2 | 350.5 | 520.9 | 77.6 | 90.4 | 483.7 | 33.5 | 61.2 | 89.5 | 153.6 | 302.5 | 340.2 | 149.2 | 279.7 | 68.2 | 206.1 | 194.7 | 78.9 | 113.3 | 107.6 | 77.8
811 | 572 | 379.6 | 151.84 | 177.4922 | 190 | 200.7 | 204.6 | 183.2 | 321.1 | 30.3 | 20.5 | 56.1 | 4.9 | 260.7 | 13.3 | 211.3 | 474.7 | 764 | 232.8 | 272.3 | 768.6 | 253.6 | 350.2 | 523.1 | 77.8 | 90.7 | 484.3 | 33.6 | 61.3 | 89.7 | 154 | 302.5 | 337.8 | 149.3 | 279.1 | 68.3 | 206.2 | 195.1 | 79.1 | 113.6 | 107.8 | 78
812 | 573 | 380.4 | 152.16 | 177.8663 | 190.4 | 200.6 | 204.9 | 183.2 | 320.5 | 30.4 | 20.5 | 56.1 | 5.1 | 257.9 | 14.8 | 211.8 | 479.5 | 762.1 | 233.1 | 272.7 | 769.2 | 254.1 | 351.2 | 526 | 78 | 90.9 | 485.3 | 33.7 | 61.5 | 89.9 | 154.4 | 302.6 | 337.1 | 148.7 | 279.3 | 68.5 | 206.4 | 195.1 | 79.2 | 113.8 | 108 | 78.2
813 | 574 | 382.2 | 152.88 | 178.7079 | 190 | 200.5 | 205.6 | 183.4 | 322.2 | 30.4 | 20.5 | 56.1 | 4.6 | 252.2 | 14.3 | 212.2 | 480.8 | 761.9 | 233.4 | 273 | 769.8 | 254.5 | 353.1 | 529.8 | 78.2 | 91.2 | 485.9 | 33.8 | 61.6 | 90 | 154.9 | 302.9 | 339 | 149.1 | 279.9 | 68.6 | 206.4 | 195.4 | 79.3 | 114 | 108.2 | 78.4
814 | 575 | 382.3 | 152.92 | 178.7547 | 189.6 | 200.4 | 205.4 | 183.5 | 324.7 | 30.4 | 20.5 | 56.2 | 5.2 | 247.9 | 13.5 | 212.7 | 481.4 | 770.7 | 233.7 | 273.4 | 770.9 | 255 | 353.6 | 540.9 | 78.4 | 91.4 | 486.4 | 33.9 | 61.7 | 90.2 | 155.3 | 303 | 338.2 | 149 | 280.6 | 68.7 | 206.6 | 195.7 | 79.5 | 114.3 | 108.5 | 78.5
815 | 576 | 381.3 | 152.52 | 178.2871 | 189.7 | 200.4 | 205.5 | 183.3 | 323.5 | 30.5 | 20.5 | 56.2 | 4.5 | 241.5 | 13.2 | 213.2 | 482.2 | 772 | 234.1 | 273.7 | 771.8 | 255.5 | 355.5 | 542 | 78.7 | 91.7 | 487.6 | 34 | 61.9 | 90.4 | 155.7 | 302.8 | 337.6 | 148.9 | 281.1 | 68.8 | 206.4 | 196.3 | 79.6 | 114.7 | 108.7 | 78.7
816 | 577 | 380.6 | 152.24 | 177.9598 | 191 | 200.6 | 205.9 | 183.4 | 321.8 | 30.5 | 20.5 | 56.2 | 5.2 | 265.1 | 12.7 | 213.6 | 479.9 | 764.4 | 234.4 | 273.9 | 771.9 | 255.9 | 357.1 | 538.2 | 78.9 | 91.9 | 488.8 | 34.1 | 62 | 90.5 | 156 | 303.5 | 337.4 | 149.7 | 281.7 | 68.9 | 206.5 | 197 | 79.8 | 115 | 108.9 | 78.9
817 | 578 | 381.2 | 152.48 | 178.2403 | 191.9 | 201.2 | 205.9 | 183.8 | 320 | 30.5 | 20.5 | 56.2 | 4.9 | 257.2 | 12.1 | 214.1 | 483.8 | 758.3 | 234.7 | 274.2 | 772.6 | 256.4 | 356.3 | 529.6 | 79.1 | 92.2 | 488.1 | 34.2 | 62.2 | 90.7 | 156.4 | 303.7 | 334.8 | 149.4 | 281.1 | 69.1 | 206.6 | 197.1 | 79.9 | 115.2 | 109.2 | 79
818 | 579 | 383.6 | 153.44 | 179.3625 | 192.9 | 203 | 205.8 | 184.1 | 316.8 | 30.5 | 20.5 | 56.3 | 4.7 | 254.4 | 11.9 | 214.5 | 478.9 | 756.5 | 235 | 274.5 | 773.5 | 256.8 | 355 | 523.7 | 79.3 | 92.5 | 487.8 | 34.3 | 62.3 | 90.8 | 156.8 | 302.5 | 331.7 | 149.1 | 280.1 | 69.2 | 206.8 | 197.4 | 80.1 | 115.5 | 109.4 | 79.2
819 | 580 | 383.7 | 153.48 | 179.4093 | 193.6 | 203.7 | 205.9 | 184.7 | 314.7 | 30.6 | 20.5 | 56.3 | 4.9 | 251 | 12.7 | 215 | 471.7 | 768.9 | 235.4 | 274.8 | 774 | 257.3 | 353 | 513.9 | 79.5 | 92.7 | 486.4 | 34.4 | 62.4 | 91 | 157.2 | 301.7 | 330.7 | 149.2 | 279.8 | 69.4 | 206.8 | 197.3 | 80.3 | 115.7 | 109.7 | 79.4
820 | 581 | 380.7 | 152.28 | 178.0065 | 194.4 | 203.5 | 206.1 | 185.2 | 314 | 30.6 | 20.5 | 56.4 | 4.4 | 244.6 | 12.3 | 215.5 | 473.5 | 778.1 | 235.7 | 275.2 | 774.5 | 257.7 | 351.6 | 510.4 | 79.7 | 93 | 485.6 | 34.5 | 62.5 | 91.2 | 157.6 | 301 | 331.4 | 150.1 | 279.7 | 69.5 | 206.8 | 197.3 | 80.5 | 115.9 | 109.9 | 79.5
821 | 582 | 378.8 | 151.52 | 177.1181 | 195.1 | 203 | 206.2 | 185.3 | 315.5 | 30.6 | 20.5 | 56.5 | 5.1 | 243.2 | 10.6 | 216 | 469.6 | 774.9 | 236 | 275.5 | 775.2 | 258.2 | 351.8 | 508.6 | 79.9 | 93.2 | 486.1 | 34.6 | 62.7 | 91.4 | 158 | 301 | 330.7 | 151.1 | 280 | 69.7 | 206.8 | 197.6 | 80.7 | 116.1 | 110.1 | 79.7
822 | 583 | 381.7 | 152.68 | 178.4741 | 195.4 | 203.6 | 206.2 | 185.2 | 314.6 | 30.6 | 20.5 | 56.5 | 5.6 | 253.4 | 8.8 | 216.4 | 468.8 | 779.2 | 236.3 | 275.6 | 775.6 | 258.7 | 352.6 | 511.7 | 80.2 | 93.5 | 487.2 | 34.7 | 62.8 | 91.5 | 158.4 | 301.7 | 329.5 | 151 | 279.7 | 69.8 | 206.8 | 198.4 | 80.8 | 116.4 | 110.3 | 79.9
823 | 584 | 380.8 | 152.32 | 178.0533 | 195.8 | 204.1 | 206 | 185.5 | 317 | 30.7 | 20.5 | 56.6 | 4.5 | 232.7 | 8.4 | 216.9 | 469.8 | 777.9 | 236.7 | 275.8 | 775.7 | 259.1 | 353.7 | 517.6 | 80.4 | 93.7 | 488.2 | 34.8 | 62.9 | 91.7 | 158.8 | 302.3 | 330 | 151.7 | 280.1 | 69.9 | 206.6 | 198.8 | 80.9 | 116.6 | 110.6 | 80
824 | 585 | 381.7 | 152.68 | 178.4741 | 196.2 | 204.2 | 206.1 | 185.4 | 318.5 | 30.7 | 20.5 | 56.6 | 3.9 | 233.8 | 8.9 | 217.4 | 471.5 | 778.5 | 237 | 275.9 | 775.3 | 259.6 | 352.8 | 524.4 | 80.6 | 94 | 489 | 34.9 | 63.1 | 92 | 159.1 | 303 | 334.1 | 152.2 | 281 | 70.1 | 206.8 | 198.4 | 81 | 116.9 | 110.8 | 80.2
825 | 586 | 381 | 152.4 | 178.1468 | 196.2 | 204 | 206.6 | 185.2 | 320.4 | 30.8 | 20.5 | 56.6 | 3.9 | 236.3 | 8.8 | 217.8 | 472.6 | 768.2 | 237.4 | 276.1 | 775.2 | 260 | 354.3 | 526.8 | 80.8 | 94.2 | 490.5 | 35 | 63.2 | 92.2 | 159.5 | 302.9 | 336.8 | 153.3 | 281.8 | 70.2 | 207.2 | 198.2 | 81.1 | 117.2 | 111 | 80.4
826 | 587 | 380.7 | 152.28 | 178.0065 | 195.9 | 203.9 | 207.1 | 185.3 | 322.9 | 30.8 | 20.5 | 56.7 | 4.2 | 229.5 | 10.1 | 218.3 | 473.8 | 777.2 | 237.7 | 276.2 | 775.1 | 260.5 | 354.5 | 531.2 | 81 | 94.5 | 490.6 | 35.1 | 63.3 | 92.4 | 159.9 | 304 | 341.1 | 152.9 | 282.4 | 70.4 | 207.5 | 197.8 | 81.1 | 117.4 | 111.3 | 80.6
827 | 588 | 382.3 | 152.92 | 178.7547 | 195.9 | 204.1 | 207.8 | 185.7 | 324.9 | 30.9 | 20.5 | 56.8 | 4.5 | 233.8 | 11 | 218.7 | 474 | 766.7 | 238 | 276.5 | 775.9 | 260.9 | 354.1 | 533.4 | 81.2 | 94.7 | 491.6 | 35.2 | 63.4 | 92.6 | 160.3 | 304.4 | 341.7 | 153.3 | 283.2 | 70.5 | 207.6 | 197.5 | 81.4 | 117.6 | 111.6 | 80.7
828 | 589 | 385.7 | 154.28 | 180.3444 | 195.8 | 203.9 | 208.6 | 186 | 324.2 | 30.8 | 20.5 | 56.8 | 3.5 | 242.8 | 11.7 | 219.2 | 474.2 | 788.7 | 238.3 | 276.8 | 776.6 | 261.4 | 355 | 530.9 | 81.4 | 95 | 492.1 | 35.3 | 63.6 | 92.8 | 160.7 | 304.9 | 341.6 | 154 | 283.6 | 70.6 | 207.8 | 198.3 | 81.5 | 117.8 | 111.8 | 80.9
829 | 590 | 385.6 | 154.24 | 180.2977 | 195.8 | 203.4 | 208.7 | 186.3 | 324.8 | 30.8 | 20.5 | 56.9 | 3.7 | 245.1 | 12.1 | 219.6 | 478.3 | 794.7 | 238.6 | 277 | 777.3 | 261.8 | 356.4 | 529.9 | 81.7 | 95.2 | 492.4 | 35.4 | 63.7 | 92.8 | 161 | 306.4 | 342.7 | 154.6 | 284 | 70.8 | 208.1 | 199 | 81.6 | 118.1 | 112.1 | 81.1
830 | 591 | 383.7 | 153.48 | 179.4093 | 195.6 | 203 | 208.7 | 186.5 | 324.8 | 30.8 | 20.5 | 56.9 | 3.9 | 234.2 | 11.7 | 220 | 479 | 794.3 | 239 | 277.3 | 778.4 | 262.3 | 357.5 | 526.5 | 81.9 | 95.4 | 491.9 | 35.5 | 63.9 | 92.9 | 161.4 | 307.5 | 343.4 | 154.8 | 285 | 70.9 | 208.3 | 199.2 | 81.8 | 118.3 | 112.3 | 81.3
831 | 592 | 382.4 | 152.96 | 178.8014 | 195.5 | 204.2 | 208.6 | 186.4 | 324.3 | 30.9 | 20.5 | 57.1 | 4.2 | 231.8 | 10.8 | 220.5 | 479.5 | 782.1 | 239.3 | 277.5 | 779.1 | 262.7 | 357.7 | 524.8 | 82.1 | 95.7 | 492.5 | 35.6 | 64 | 93.2 | 161.8 | 308.3 | 342.6 | 154.1 | 285.2 | 71.1 | 208.6 | 198.9 | 82 | 118.6 | 112.6 | 81.5
832 | 593 | 381.2 | 152.48 | 178.2403 | 196.5 | 206.8 | 208.2 | 186.4 | 322.9 | 30.9 | 20.5 | 57.2 | 3.7 | 235.5 | 10.5 | 220.9 | 480.3 | 780.6 | 239.7 | 277.8 | 779.6 | 263.2 | 359.8 | 528.5 | 82.3 | 95.9 | 493.7 | 35.7 | 64.2 | 93.2 | 162.2 | 309.1 | 343 | 153.8 | 285 | 71.2 | 208.8 | 198.8 | 82.3 | 118.9 | 112.9 | 81.7
833 | 594 | 381.6 | 152.64 | 178.4274 | 197.1 | 208.3 | 208.2 | 186.8 | 323.2 | 30.9 | 20.5 | 57.2 | 4.1 | 228.9 | 10 | 221.4 | 484.8 | 788.4 | 240 | 278.1 | 780.1 | 263.6 | 361.6 | 534.3 | 82.5 | 96.2 | 494.5 | 35.8 | 64.3 | 93.5 | 162.6 | 309.2 | 342.9 | 154.4 | 285.4 | 71.4 | 209 | 198.5 | 82.5 | 119.1 | 113.2 | 81.8
834 | 595 | 383.3 | 153.32 | 179.2222 | 197.1 | 208 | 207.6 | 187.1 | 325 | 30.9 | 20.5 | 57.3 | 4.2 | 239.4 | 9.2 | 221.8 | 486.8 | 782.2 | 240.4 | 278.5 | 780.9 | 264.1 | 362.6 | 536 | 82.7 | 96.4 | 494.9 | 35.9 | 64.4 | 93.8 | 163 | 310.5 | 344.5 | 154.9 | 286.1 | 71.5 | 209.5 | 198.5 | 82.7 | 119.3 | 113.5 | 82
835 | 596 | 384 | 153.6 | 179.5496 | 196.8 | 208.2 | 207.4 | 187.4 | 325.9 | 31 | 20.5 | 57.4 | 3.3 | 235.6 | 11.4 | 222.3 | 489.6 | 784.7 | 240.7 | 278.7 | 780.6 | 264.5 | 362.3 | 530.4 | 83 | 96.7 | 493.6 | 36 | 64.6 | 93.8 | 163.3 | 311.2 | 342.5 | 154 | 286.1 | 71.7 | 209.9 | 198.6 | 82.9 | 119.6 | 113.8 | 82.2
836 | 597 | 383.3 | 153.32 | 179.2222 | 196.6 | 211.9 | 207.1 | 187.7 | 324.2 | 31 | 20.5 | 57.4 | 3 | 245.3 | 12.1 | 222.8 | 491.8 | 787.9 | 241 | 279.1 | 780.9 | 265 | 363.1 | 532.7 | 83.2 | 96.9 | 493.2 | 36.1 | 64.7 | 94.1 | 163.7 | 311.2 | 340.4 | 152.8 | 285.7 | 71.8 | 210.1 | 199 | 83 | 119.9 | 114.1 | 82.4
837 | 598 | 382.4 | 152.96 | 178.8014 | 196.4 | 213.6 | 206.2 | 188.5 | 322.6 | 31 | 20.5 | 57.5 | 3.3 | 242 | 12.8 | 223.2 | 494.1 | 774.8 | 241.4 | 279.3 | 780.2 | 265.4 | 363.5 | 534.2 | 83.4 | 97.1 | 495 | 36.2 | 64.8 | 94.2 | 164.1 | 311.4 | 339.3 | 153.5 | 286.3 | 72 | 210.5 | 199.4 | 83.2 | 120.1 | 114.4 | 82.6
838 | 599 | 380.3 | 152.12 | 177.8195 | 196.6 | 213.7 | 205.7 | 188.8 | 320.5 | 31.1 | 20.5 | 57.5 | 2.8 | 219.1 | 12.2 | 223.7 | 500.5 | 761.3 | 241.7 | 279.6 | 778.7 | 265.9 | 362.7 | 529.6 | 83.6 | 97.4 | 494.9 | 36.3 | 65 | 94.4 | 164.5 | 310.8 | 338.4 | 153.2 | 285.9 | 72.1 | 210.5 | 199.5 | 83.4 | 120.2 | 114.7 | 82.8
839 | 600 | 382.8 | 153.12 | 178.9885 | 196.6 | 212.8 | 206.3 | 188.8 | 320.7 | 31.1 | 20.5 | 57.6 | 3.7 | 238 | 10.2 | 224.1 | 504.2 | 763 | 242.1 | 279.9 | 777.2 | 266.4 | 363.1 | 529.3 | 83.9 | 97.6 | 494.5 | 36.4 | 65.1 | 94.7 | 164.9 | 310.3 | 337.6 | 153.3 | 285.8 | 72.3 | 210.5 | 199.9 | 83.5 | 120.4 | 114.9 | 82.9
840 | 601 | 380.6 | 152.24 | 177.9598 | 196.5 | 211.6 | 206.8 | 188.6 | 318.9 | 31.1 | 20.5 | 57.6 | 3.9 | 208.9 | 9.2 | 224.6 | 509.3 | 756 | 242.5 | 280.2 | 776.1 | 266.8 | 360.9 | 526.6 | 84.1 | 97.8 | 494.4 | 36.5 | 65.2 | 94.8 | 165.2 | 309.3 | 336.8 | 154.1 | 285.2 | 72.4 | 210.4 | 199.9 | 83.7 | 120.7 | 115.2 | 83.1
841 | 602 | 378.6 | 151.44 | 177.0246 | 196.3 | 211.1 | 207 | 188.5 | 317.8 | 31.1 | 20.5 | 57.7 | 4.6 | 241.9 | 8.1 | 225 | 508.6 | 750.2 | 242.8 | 280.5 | 774.6 | 267.3 | 358.7 | 520.6 | 84.3 | 98.1 | 494.1 | 36.6 | 65.3 | 95 | 165.6 | 309 | 337.5 | 155.9 | 284.8 | 72.6 | 210.2 | 199.7 | 83.8 | 120.8 | 115.4 | 83.3
842 | 603 | 379 | 151.6 | 177.2117 | 195.8 | 210.8 | 207.5 | 188.7 | 318 | 31.2 | 20.5 | 57.7 | 4.5 | 234.1 | 7.1 | 225.4 | 512 | 755.8 | 243.1 | 280.9 | 773.8 | 267.7 | 358.7 | 531.8 | 84.5 | 98.3 | 496 | 36.7 | 65.5 | 95.3 | 166 | 307.2 | 338.2 | 155.9 | 284.8 | 72.7 | 210.3 | 199.3 | 83.9 | 121 | 115.6 | 83.5
843 | 604 | 378.3 | 151.32 | 176.8844 | 195.8 | 210.7 | 208.2 | 188.8 | 322.2 | 31.2 | 20.4 | 57.8 | 4.4 | 235.7 | 6.4 | 225.9 | 518.5 | 768.1 | 243.5 | 281.3 | 773.8 | 268.2 | 359.9 | 535.6 | 84.7 | 98.5 | 498.3 | 36.8 | 65.6 | 95.6 | 166.3 | 307 | 342.3 | 157.5 | 285.8 | 72.8 | 210.5 | 199.1 | 84 | 121 | 115.8 | 83.6
844 | 605 | 378.7 | 151.48 | 177.0714 | 196.4 | 210 | 208.7 | 188.9 | 325.6 | 31.2 | 20.5 | 57.9 | 4.4 | 226 | 6.4 | 226.3 | 518.7 | 764.2 | 243.8 | 281.6 | 774.8 | 268.7 | 359.4 | 535.6 | 85 | 98.8 | 499.5 | 36.9 | 65.7 | 95.6 | 166.7 | 307.9 | 342.9 | 158.7 | 286 | 72.9 | 211 | 199.2 | 84.1 | 121 | 116 | 83.8
845 | 606 | 379.9 | 151.96 | 177.6325 | 196.1 | 209.4 | 208.6 | 189 | 327.1 | 31.3 | 20.4 | 58 | 4.4 | 235.3 | 6.3 | 226.8 | 515.7 | 757.2 | 244.2 | 282 | 775.4 | 269.1 | 359.4 | 531 | 85.2 | 99 | 500.6 | 37 | 65.9 | 95.8 | 167.1 | 308.5 | 343.3 | 158.7 | 285.9 | 73.1 | 211.1 | 200.2 | 84.2 | 121.2 | 116.2 | 84
846 | 607 | 380.8 | 152.32 | 178.0533 | 196.6 | 208.6 | 208.5 | 189.3 | 327 | 31.3 | 20.4 | 58.1 | 4.1 | 240.8 | 5.8 | 227.2 | 513.4 | 759.7 | 244.5 | 282.3 | 775 | 269.6 | 358.4 | 528 | 85.4 | 99.2 | 499.9 | 37.1 | 66 | 95.9 | 167.4 | 308.2 | 343.6 | 158.9 | 285.5 | 73.2 | 211.2 | 200.6 | 84.4 | 121.4 | 116.5 | 84.2
847 | 608 | 380.4 | 152.16 | 177.8663 | 197.9 | 207.5 | 208.4 | 189.3 | 326.9 | 31.4 | 20.4 | 58.1 | 4.3 | 243.1 | 6.2 | 227.6 | 512.1 | 745.6 | 244.9 | 282.6 | 775.2 | 270 | 356.7 | 525 | 85.6 | 99.5 | 500.2 | 37.2 | 66.1 | 96.2 | 167.8 | 307.3 | 342.1 | 158.6 | 285.4 | 73.3 | 211.3 | 200.6 | 84.6 | 121.6 | 116.7 | 84.4
848 | 609 | 380.9 | 152.36 | 178.1001 | 199.4 | 206.9 | 209.1 | 189.2 | 325.7 | 31.4 | 20.4 | 58.2 | 4 | 226.8 | 6.3 | 228 | 511.8 | 736.8 | 245.2 | 282.9 | 775.2 | 270.5 | 355.2 | 523.8 | 85.9 | 99.7 | 500.2 | 37.3 | 66.3 | 96.4 | 168.2 | 307.2 | 340.9 | 159.5 | 285.5 | 73.4 | 211.4 | 200.9 | 84.7 | 121.8 | 116.9 | 84.5
849 | 610 | 383.6 | 153.44 | 179.3625 | 200.5 | 206.7 | 209.4 | 189.1 | 325.1 | 31.4 | 20.4 | 58.3 | 3.3 | 237.6 | 5.9 | 228.5 | 512.3 | 730.2 | 245.6 | 283.2 | 774.4 | 270.9 | 355.7 | 528.2 | 86.1 | 99.9 | 500.8 | 37.4 | 66.4 | 96.5 | 168.6 | 307.2 | 342.9 | 159.3 | 285.4 | 73.5 | 211.3 | 200.8 | 84.9 | 122 | 117.1 | 84.7
850 | 611 | 383.6 | 153.44 | 179.3625 | 200.7 | 207.1 | 210 | 189 | 326.9 | 31.4 | 20.4 | 58.3 | 3.8 | 244.4 | 6.7 | 228.9 | 513.7 | 729.1 | 245.9 | 283.5 | 773.7 | 271.4 | 354.2 | 528.3 | 86.3 | 100.2 | 501.2 | 37.5 | 66.6 | 96.6 | 168.9 | 307.9 | 344.5 | 160.7 | 286.3 | 73.7 | 211.6 | 200.8 | 85 | 122.2 | 117.4 | 84.9
851 | 612 | 381.3 | 152.52 | 178.2871 | 200.2 | 207 | 210.5 | 189.1 | 325.4 | 31.5 | 20.4 | 58.4 | 4.3 | 241.3 | 7.8 | 229.3 | 511 | 727.6 | 246.3 | 283.9 | 773.4 | 271.8 | 353.3 | 527.2 | 86.5 | 100.4 | 500.7 | 37.6 | 66.7 | 96.9 | 169.3 | 307.3 | 348.1 | 160.5 | 286.3 | 73.8 | 211.6 | 200.4 | 85.1 | 122.4 | 117.6 | 85.1
852 | 613 | 380.7 | 152.28 | 178.0065 | 199.6 | 206.7 | 210.8 | 189.2 | 325 | 31.5 | 20.4 | 58.5 | 4.4 | 220.3 | 8 | 229.7 | 505.8 | 730.9 | 246.5 | 284.2 | 772.8 | 272.2 | 351.8 | 520.2 | 86.8 | 100.6 | 500 | 37.7 | 66.8 | 97.1 | 169.7 | 307.2 | 346.1 | 161.4 | 286.5 | 73.9 | 211.8 | 200.1 | 85.3 | 122.6 | 117.8 | 85.2
853 | 614 | 381.7 | 152.68 | 178.4741 | 199.5 | 206.6 | 211.2 | 189.5 | 322.5 | 31.5 | 20.4 | 58.6 | 4 | 210.8 | 8 | 230.2 | 501.8 | 729.4 | 246.9 | 284.4 | 772 | 272.7 | 349.7 | 512 | 87 | 100.9 | 498.5 | 37.9 | 67 | 97.2 | 170.1 | 305.9 | 343.5 | 162.5 | 286 | 74 | 211.9 | 200 | 85.5 | 122.7 | 118.1 | 85.4
854 | 615 | 381.4 | 152.56 | 178.3339 | 199.4 | 205.9 | 211.6 | 189.9 | 319.6 | 31.6 | 20.4 | 58.7 | 4.2 | 195 | 8 | 230.6 | 496.2 | 734.9 | 247.2 | 284.8 | 772 | 273.1 | 348.3 | 511.7 | 87.2 | 101.1 | 498.1 | 38 | 67.1 | 97.5 | 170.4 | 303.9 | 339.5 | 161.6 | 285.2 | 74.1 | 212.2 | 199.8 | 85.7 | 122.8 | 118.3 | 85.6
855 | 616 | 382.1 | 152.84 | 178.6612 | 199.3 | 205.3 | 212.1 | 190 | 319.2 | 31.6 | 20.4 | 58.8 | 4.8 | 222.9 | 8 | 231 | 493.6 | 740.9 | 247.5 | 285.1 | 771.5 | 273.5 | 348.4 | 511.5 | 87.4 | 101.4 | 498.6 | 38.1 | 67.2 | 97.5 | 170.8 | 303 | 338.7 | 161.5 | 284.8 | 74.3 | 212.2 | 199.8 | 85.8 | 123 | 118.5 | 85.8
856 | 617 | 382 | 152.8 | 178.6144 | 201.2 | 205.3 | 212.1 | 190.2 | 321.5 | 31.7 | 20.4 | 58.9 | 5.1 | 238.1 | 7.2 | 231.4 | 493.1 | 745.2 | 247.9 | 285.5 | 771.7 | 274 | 351.9 | 523.4 | 87.7 | 101.6 | 500.7 | 38.2 | 67.4 | 97.8 | 171.2 | 303.5 | 341.2 | 163.2 | 284.8 | 74.4 | 212.1 | 199.8 | 85.9 | 123.4 | 118.7 | 85.9
857 | 618 | 382.1 | 152.84 | 178.6612 | 201.9 | 205.4 | 211.5 | 190.4 | 324.7 | 31.7 | 20.4 | 58.9 | 4.8 | 250.4 | 6.6 | 231.8 | 491.6 | 754.9 | 248.2 | 285.8 | 772.5 | 274.4 | 355.4 | 537 | 87.9 | 101.8 | 503.4 | 38.3 | 67.5 | 98 | 171.6 | 304.5 | 344 | 163.9 | 285.6 | 74.5 | 211.8 | 200.2 | 86 | 123.6 | 118.9 | 86.1
858 | 619 | 380.8 | 152.32 | 178.0533 | 201.9 | 204.9 | 211.6 | 190.7 | 327.7 | 31.8 | 20.4 | 59 | 4.8 | 228.7 | 6.2 | 232.3 | 490.3 | 767.5 | 248.5 | 286.1 | 772.8 | 274.9 | 357.7 | 545.6 | 88.1 | 102.1 | 506 | 38.4 | 67.7 | 98.1 | 172 | 305.4 | 345.3 | 165.4 | 286 | 74.6 | 211.8 | 200.9 | 86.1 | 123.8 | 119.1 | 86.3
859 | 620 | 382.1 | 152.84 | 178.6612 | 203.2 | 204.6 | 212.3 | 190.9 | 330.3 | 31.8 | 20.4 | 59.1 | 4.6 | 228.3 | 6.1 | 232.7 | 490.9 | 775.3 | 248.9 | 286.4 | 772.1 | 275.3 | 358.5 | 547.1 | 88.3 | 102.3 | 506.8 | 38.5 | 67.8 | 98.3 | 172.3 | 306.8 | 346.7 | 166.5 | 286.3 | 74.7 | 211.8 | 201.3 | 86.1 | 124 | 119.3 | 86.4
860 | 621 | 382.3 | 152.92 | 178.7547 | 205.2 | 204.7 | 212.9 | 190.9 | 333.3 | 31.8 | 20.4 | 59.1 | 4.5 | 221.5 | 6.6 | 233.1 | 494.8 | 776.1 | 249.3 | 286.8 | 772 | 275.7 | 363.5 | 560.4 | 88.6 | 102.6 | 509.6 | 38.6 | 68 | 98.6 | 172.7 | 309 | 351.1 | 167.2 | 287 | 74.8 | 211.9 | 201 | 86.2 | 124.2 | 119.5 | 86.6
861 | 622 | 381.7 | 152.68 | 178.4741 | 205.7 | 205.2 | 213.2 | 191.2 | 336.5 | 31.8 | 20.4 | 59.2 | 3.7 | 207.7 | 5.7 | 233.5 | 496.6 | 782.9 | 249.6 | 287.1 | 772.1 | 276.2 | 365.4 | 563.3 | 88.8 | 102.8 | 511.7 | 38.7 | 68.1 | 98.7 | 173.1 | 309.8 | 351.1 | 167.6 | 287.2 | 75 | 212.5 | 200.7 | 86.3 | 124.5 | 119.8 | 86.8
862 | 623 | 381.8 | 152.72 | 178.5209 | 205.4 | 205.6 | 213.8 | 191.3 | 335.5 | 31.7 | 20.4 | 59.2 | 3.4 | 248.6 | 5 | 233.9 | 498.8 | 798.6 | 249.9 | 287.5 | 772 | 276.6 | 366.4 | 569.3 | 89 | 103.1 | 513.5 | 38.8 | 68.3 | 99 | 173.5 | 309.7 | 350.9 | 167 | 287.3 | 75.1 | 212.8 | 201.4 | 86.4 | 124.6 | 120 | 87
863 | 624 | 381.9 | 152.76 | 178.5676 | 205.7 | 205.8 | 214.1 | 191.4 | 336.9 | 31.7 | 20.4 | 59.3 | 4 | 248.2 | 4.7 | 234.3 | 498.4 | 785.6 | 250.3 | 287.8 | 772 | 277 | 366.2 | 565.3 | 89.2 | 103.3 | 515 | 38.9 | 68.4 | 99.2 | 173.9 | 310.5 | 352.9 | 168.1 | 287.8 | 75.2 | 213 | 202.3 | 86.5 | 124.8 | 120.2 | 87.2
864 | 625 | 381.8 | 152.72 | 178.5209 | 205.4 | 206 | 214.4 | 191.5 | 337.4 | 31.7 | 20.4 | 59.4 | 3.9 | 230.9 | 4.6 | 234.7 | 496 | 773.7 | 250.6 | 288.2 | 772.3 | 277.4 | 365.4 | 552.8 | 89.4 | 103.6 | 514.6 | 39 | 68.5 | 99.4 | 174.2 | 311 | 351.2 | 168.5 | 287.2 | 75.3 | 213.3 | 202.9 | 86.6 | 125.2 | 120.5 | 87.3
865 | 626 | 382 | 152.8 | 178.6144 | 204.5 | 206.4 | 214.7 | 191.6 | 335.8 | 31.8 | 20.4 | 59.4 | 3.9 | 216.3 | 4.3 | 235.1 | 493.5 | 780.4 | 250.9 | 288.5 | 772.8 | 277.8 | 366.8 | 548.6 | 89.7 | 103.8 | 514.8 | 39.1 | 68.7 | 99.6 | 174.6 | 311.4 | 349.9 | 169.2 | 286.9 | 75.4 | 213.3 | 202.9 | 86.8 | 125.4 | 120.7 | 87.5
866 | 627 | 383 | 153.2 | 179.082 | 204.2 | 207.2 | 215.2 | 191.8 | 333.2 | 31.8 | 20.4 | 59.5 | 3.8 | 209.4 | 4.4 | 235.5 | 495.5 | 783.8 | 251.2 | 288.9 | 774.1 | 278.3 | 368.3 | 551.5 | 89.9 | 104.1 | 515.3 | 39.2 | 68.8 | 99.7 | 175 | 311.7 | 347.8 | 168.3 | 287.2 | 75.5 | 213.4 | 203.2 | 87 | 125.6 | 120.9 | 87.7
867 | 628 | 383.9 | 153.56 | 179.5028 | 204.8 | 208.7 | 215 | 192.3 | 332 | 31.9 | 20.4 | 59.6 | 3.4 | 224.3 | 4.4 | 235.9 | 500 | 782.3 | 251.6 | 289.3 | 775.1 | 278.7 | 368.6 | 548.9 | 90.1 | 104.3 | 515.9 | 39.3 | 69 | 99.8 | 175.4 | 313.1 | 349.4 | 168.6 | 288 | 75.7 | 213.3 | 203.3 | 87.2 | 125.9 | 121.2 | 87.9
868 | 629 | 383.5 | 153.4 | 179.3158 | 205.7 | 210.7 | 214.5 | 192.8 | 332.9 | 31.9 | 20.4 | 59.6 | 3.4 | 258.2 | 4 | 236.3 | 502.8 | 782.4 | 251.9 | 289.5 | 775.5 | 279.1 | 370.1 | 547.8 | 90.4 | 104.6 | 516.3 | 39.4 | 69.1 | 100.1 | 175.8 | 313.9 | 349.6 | 168.2 | 288.8 | 75.8 | 213.7 | 203.1 | 87.5 | 126.1 | 121.4 | 88.1
869 | 630 | 381.2 | 152.48 | 178.2403 | 207.1 | 212.4 | 214.4 | 193.2 | 331.3 | 32 | 20.4 | 59.7 | 3.5 | 216.8 | 4.3 | 236.7 | 502.8 | 777.2 | 252.2 | 289.9 | 776 | 279.5 | 369.3 | 540.9 | 90.6 | 104.8 | 516.2 | 39.5 | 69.3 | 100 | 176.2 | 314.4 | 346.4 | 168.6 | 288.6 | 76 | 214.1 | 203.2 | 87.8 | 126.2 | 121.7 | 88.3
870 | 631 | 380.3 | 152.12 | 177.8195 | 207.8 | 216.7 | 214 | 193.4 | 329.4 | 32.1 | 20.4 | 59.7 | 3.5 | 196.6 | 5.6 | 237.1 | 500 | 782.2 | 252.5 | 290.2 | 775.9 | 279.9 | 368.5 | 538.9 | 90.8 | 105.1 | 516.3 | 39.6 | 69.4 | 100.1 | 176.6 | 314.4 | 345 | 169 | 288.1 | 76.1 | 214.3 | 203.1 | 88.1 | 126.4 | 121.9 | 88.4
871 | 632 | 383.2 | 153.28 | 179.1755 | 208 | 218.4 | 213.6 | 193.4 | 329.8 | 32.1 | 20.4 | 59.8 | 3.5 | 212.8 | 6 | 237.5 | 503.7 | 777 | 252.9 | 290.6 | 777 | 280.3 | 372 | 550 | 91 | 105.3 | 518.6 | 39.7 | 69.5 | 100.3 | 176.9 | 315.3 | 346.3 | 170.5 | 288.5 | 76.3 | 214.2 | 203.9 | 88.3 | 126.7 | 122.2 | 88.6
872 | 633 | 383 | 153.2 | 179.082 | 208.1 | 220.2 | 213.2 | 193.6 | 329.7 | 32.2 | 20.4 | 59.8 | 4.1 | 211.8 | 7.6 | 237.9 | 508.6 | 772 | 253.2 | 291 | 777.5 | 280.7 | 374 | 560.7 | 91.2 | 105.6 | 521.8 | 39.8 | 69.7 | 100.4 | 177.3 | 315.8 | 345.4 | 171.2 | 289.1 | 76.4 | 214.3 | 204.1 | 88.5 | 127 | 122.4 | 88.8
873 | 634 | 383.3 | 153.32 | 179.2222 | 208.2 | 222.2 | 212.5 | 193.4 | 328.2 | 32.2 | 20.4 | 59.8 | 4.9 | 204 | 8.8 | 238.3 | 513.6 | 766.3 | 253.5 | 291.4 | 778 | 281.1 | 374.7 | 556.9 | 91.5 | 105.8 | 521.9 | 40 | 69.8 | 100.5 | 177.7 | 315.7 | 342.4 | 170.7 | 289.2 | 76.6 | 214.2 | 204.2 | 88.7 | 127.1 | 122.6 | 88.9
874 | 635 | 383 | 153.2 | 179.082 | 208.2 | 221.7 | 211.9 | 193.2 | 324.8 | 32.3 | 20.4 | 59.8 | 5.4 | 223.2 | 8.7 | 238.7 | 522.9 | 781.4 | 253.8 | 291.9 | 778.4 | 281.5 | 375.2 | 556.9 | 91.7 | 106.1 | 522.2 | 40.1 | 69.9 | 100.7 | 178.1 | 315.1 | 340.6 | 170.2 | 288.8 | 76.7 | 214.4 | 204.2 | 89 | 127.4 | 122.9 | 89.1
875 | 636 | 383.1 | 153.24 | 179.1287 | 208 | 220.4 | 211.8 | 193.6 | 325.9 | 32.3 | 20.4 | 59.8 | 5.3 | 199.6 | 8.9 | 239 | 527.7 | 777.9 | 254.2 | 292.3 | 777.5 | 281.9 | 377.2 | 555.1 | 91.9 | 106.4 | 522.2 | 40.2 | 70.1 | 100.9 | 178.5 | 316 | 341.7 | 170.4 | 289.4 | 76.9 | 214 | 204.3 | 89.2 | 127.8 | 123.1 | 89.3
876 | 637 | 381.8 | 152.72 | 178.5209 | 208.1 | 221.1 | 211.9 | 193.7 | 325.2 | 32.4 | 20.4 | 59.9 | 4.8 | 201.1 | 8.9 | 239.5 | 532.7 | 781.9 | 254.5 | 292.7 | 777 | 282.4 | 377.9 | 556.2 | 92.1 | 106.6 | 522.4 | 40.3 | 70.2 | 101.1 | 178.9 | 315.9 | 341 | 169.9 | 289.4 | 77.1 | 214.9 | 204.6 | 89.3 | 128.2 | 123.4 | 89.5
877 | 638 | 382.2 | 152.88 | 178.7079 | 208.2 | 223.2 | 211.8 | 193.9 | 325.2 | 32.5 | 20.4 | 59.9 | 4.6 | 208.5 | 9.5 | 239.9 | 536.6 | 771.9 | 254.8 | 293.2 | 777.9 | 282.8 | 378.3 | 560.7 | 92.4 | 106.9 | 523.8 | 40.4 | 70.3 | 101.3 | 179.3 | 316.1 | 345.3 | 171.7 | 290 | 77.2 | 216.1 | 204.8 | 89.7 | 128.3 | 123.7 | 89.7
878 | 639 | 379.7 | 151.88 | 177.539 | 208.7 | 225.1 | 211.8 | 194.2 | 327.5 | 32.5 | 20.4 | 60 | 3.8 | 210.2 | 9.7 | 240.3 | 539.7 | 766.3 | 255.1 | 293.6 | 778.1 | 283.3 | 376.8 | 558.4 | 92.6 | 107.1 | 524 | 40.5 | 70.5 | 101.7 | 179.7 | 316.7 | 349 | 172.6 | 291 | 77.4 | 215.9 | 204.7 | 89.8 | 128.5 | 123.9 | 89.9
879 | 640 | 381.2 | 152.48 | 178.2403 | 209.6 | 225.1 | 211.6 | 194.6 | 330.6 | 32.6 | 20.4 | 60.1 | 3.2 | 213.4 | 9.7 | 240.7 | 546.5 | 766.6 | 255.4 | 294.1 | 777.6 | 283.7 | 377.2 | 561.7 | 92.8 | 107.4 | 525.9 | 40.6 | 70.6 | 101.8 | 180.1 | 318.3 | 351.9 | 173.1 | 291.3 | 77.6 | 217.1 | 204.9 | 90 | 128.8 | 124.2 | 90.1
880 | 641 | 380.4 | 152.16 | 177.8663 | 210.5 | 223.3 | 211.4 | 194.4 | 334.6 | 32.6 | 20.4 | 60.2 | 3.1 | 222.7 | 8.7 | 241.1 | 551.6 | 744.7 | 255.7 | 294.5 | 778 | 284.2 | 375.8 | 561.9 | 93.1 | 107.7 | 526.4 | 40.7 | 70.7 | 102.1 | 180.5 | 318.7 | 351.1 | 173 | 291.6 | 77.8 | 218.3 | 205.5 | 90.1 | 129.2 | 124.4 | 90.3
881 | 642 | 382.9 | 153.16 | 179.0352 | 210.7 | 222.1 | 211.8 | 193.9 | 333.4 | 32.5 | 20.4 | 60.2 | 3.3 | 209.6 | 9 | 241.5 | 548.6 | 722.3 | 256 | 294.9 | 777.7 | 284.6 | 372.6 | 550.6 | 93.3 | 107.9 | 524.4 | 40.8 | 70.9 | 102.1 | 180.8 | 317.7 | 348.5 | 173.6 | 290.5 | 78 | 218.1 | 205.7 | 90.2 | 129.4 | 124.7 | 90.5
882 | 643 | 380.7 | 152.28 | 178.0065 | 211.5 | 221.5 | 212.1 | 193.9 | 329.9 | 32.5 | 20.4 | 60.2 | 3.5 | 223.9 | 9.6 | 241.9 | 551.7 | 717.3 | 256.2 | 295.3 | 776.3 | 285.1 | 370.4 | 543.5 | 93.5 | 108.2 | 523.9 | 40.9 | 71 | 102.3 | 181.2 | 315.8 | 344.3 | 172.1 | 289.1 | 78.1 | 218.5 | 205.6 | 90.3 | 129.4 | 124.9 | 90.7
883 | 644 | 381.9 | 152.76 | 178.5676 | 212.1 | 220.3 | 212.5 | 193.8 | 327.2 | 32.6 | 20.4 | 60.3 | 3.9 | 199.4 | 9.1 | 242.2 | 551.3 | 714.3 | 256.5 | 295.7 | 775.3 | 285.5 | 370.8 | 542.5 | 93.8 | 108.5 | 525.5 | 41 | 71.1 | 102.5 | 181.6 | 314.8 | 343.2 | 172.2 | 288.9 | 78.3 | 218.5 | 205.5 | 90.4 | 129.7 | 125.1 | 90.9
884 | 645 | 382 | 152.8 | 178.6144 | 212 | 218.9 | 213.3 | 193.5 | 328 | 32.6 | 20.4 | 60.3 | 3.9 | 207.6 | 8.7 | 242.6 | 551.7 | 718.6 | 256.8 | 296.1 | 774.1 | 285.9 | 371.8 | 547.3 | 94 | 108.8 | 526.6 | 41.1 | 71.3 | 102.7 | 182 | 313.7 | 341.8 | 172.8 | 288.5 | 78.4 | 218.4 | 205.6 | 90.6 | 130 | 125.3 | 91.1
885 | 646 | 381.1 | 152.44 | 178.1936 | 211.6 | 217.8 | 214.1 | 193.4 | 329.2 | 32.7 | 20.4 | 60.4 | 3.4 | 196.7 | 8.7 | 243 | 551.8 | 736.9 | 257.1 | 296.6 | 773.9 | 286.3 | 371.8 | 547.6 | 94.2 | 109 | 527.7 | 41.3 | 71.4 | 102.9 | 182.4 | 313.7 | 343.5 | 173.8 | 288.8 | 78.5 | 218.2 | 205.5 | 90.7 | 130.1 | 125.5 | 91.2
886 | 647 | 382.3 | 152.92 | 178.7547 | 211.4 | 216.6 | 214.7 | 193.8 | 331.2 | 32.7 | 20.4 | 60.4 | 3.3 | 195.5 | 7.2 | 243.4 | 554.2 | 744.5 | 257.4 | 297 | 773.6 | 286.7 | 375.8 | 563.3 | 94.5 | 109.3 | 530.2 | 41.4 | 71.6 | 103.2 | 182.8 | 313.8 | 347.2 | 174.6 | 289.6 | 78.7 | 218.2 | 205.7 | 90.9 | 130.2 | 125.7 | 91.4
887 | 648 | 383.8 | 153.52 | 179.456 | 211.9 | 215.9 | 215.2 | 194.1 | 335.6 | 32.7 | 20.4 | 60.5 | 3.6 | 176.1 | 5.8 | 243.7 | 563.3 | 749.9 | 257.6 | 297.5 | 773.1 | 287.1 | 377.5 | 567.6 | 94.7 | 109.6 | 532.1 | 41.5 | 71.7 | 103.4 | 183.2 | 315.1 | 350.8 | 175.6 | 290.4 | 78.8 | 218.2 | 205.8 | 90.9 | 130.4 | 125.9 | 91.6
888 | 649 | 382.1 | 152.84 | 178.6612 | 211.6 | 216.3 | 215.7 | 194.5 | 337.9 | 32.7 | 20.4 | 60.6 | 3.4 | 206.8 | 6.2 | 244.1 | 566.4 | 742.2 | 257.9 | 298.1 | 773.2 | 287.5 | 379.2 | 574.9 | 95 | 109.8 | 535.7 | 41.6 | 71.8 | 103.6 | 183.6 | 315.6 | 352.1 | 176.1 | 290.4 | 78.9 | 218.4 | 206.4 | 91 | 130.6 | 126.1 | 91.7
889 | 650 | 381.2 | 152.48 | 178.2403 | 211.1 | 216.5 | 216.6 | 194.6 | 336.9 | 32.7 | 20.4 | 60.6 | 3.6 | 169.8 | 6.1 | 244.4 | 565.6 | 740 | 258.2 | 298.6 | 772.9 | 287.9 | 381.8 | 576.2 | 95.2 | 110.1 | 537.4 | 41.7 | 72 | 103.9 | 184 | 315.7 | 353.5 | 176.1 | 290.5 | 79.1 | 218.5 | 206.7 | 91.2 | 130.7 | 126.4 | 91.9
890 | 651 | 380.4 | 152.16 | 177.8663 | 210.7 | 216.4 | 217.4 | 194.7 | 339.7 | 32.7 | 20.4 | 60.7 | 3.5 | 189 | 5.6 | 244.8 | 561.3 | 731 | 258.4 | 299.1 | 771.8 | 288.3 | 383.5 | 571.3 | 95.4 | 110.4 | 538.9 | 41.8 | 72.2 | 104.2 | 184.3 | 317.7 | 353.8 | 176.2 | 291.8 | 79.2 | 218.7 | 206.8 | 91.3 | 131 | 126.6 | 92.1
891 | 652 | 380.5 | 152.2 | 177.913 | 210.1 | 217.4 | 218.7 | 194.8 | 338.1 | 32.7 | 20.4 | 60.8 | 3.7 | 207.8 | 5.8 | 245.1 | 557.4 | 720.8 | 258.7 | 299.7 | 770.9 | 288.8 | 382.3 | 564.7 | 95.6 | 110.7 | 537.6 | 41.9 | 72.3 | 104.2 | 184.7 | 316.3 | 349.5 | 175.5 | 291 | 79.3 | 218.9 | 206.5 | 91.5 | 131.1 | 126.8 | 92.2
892 | 653 | 382.2 | 152.88 | 178.7079 | 210.4 | 218.4 | 219.2 | 194.9 | 333.5 | 32.7 | 20.4 | 60.9 | 3.5 | 204.8 | 5.9 | 245.4 | 557.6 | 725.3 | 258.9 | 300.2 | 770.9 | 289.2 | 380.7 | 556.8 | 95.9 | 110.9 | 535.6 | 42 | 72.4 | 104.2 | 185.1 | 315 | 348.6 | 176.3 | 290 | 79.5 | 219.4 | 206.5 | 91.7 | 131.2 | 127.1 | 92.4
893 | 654 | 382.4 | 152.96 | 178.8014 | 211.7 | 218.1 | 219.3 | 195.3 | 333.2 | 32.7 | 20.4 | 60.9 | 3.7 | 257.9 | 5.5 | 245.7 | 552.6 | 744.4 | 259.2 | 300.8 | 771 | 289.6 | 382 | 561.7 | 96.1 | 111.2 | 536.9 | 42.1 | 72.6 | 104.6 | 185.5 | 314.6 | 348.9 | 175.9 | 290.4 | 79.6 | 219.8 | 206.7 | 91.8 | 131.4 | 127.3 | 92.6
894 | 655 | 383.1 | 153.24 | 179.1287 | 211.2 | 217.9 | 219.7 | 195.6 | 335.4 | 32.7 | 20.4 | 60.9 | 3.5 | 204.2 | 5.8 | 246 | 549.8 | 760.3 | 259.4 | 301.4 | 771.4 | 290 | 384.2 | 565.9 | 96.3 | 111.5 | 538.1 | 42.2 | 72.7 | 104.8 | 185.8 | 315.8 | 351.1 | 176 | 291.6 | 79.7 | 219.9 | 207.3 | 91.9 | 131.5 | 127.5 | 92.8
895 | 656 | 379.4 | 151.76 | 177.3987 | 210.3 | 218.1 | 219.9 | 195.9 | 335.7 | 32.8 | 20.4 | 61 | 3.7 | 195.9 | 7.1 | 246.4 | 544.1 | 769.1 | 259.8 | 301.8 | 772.7 | 290.4 | 384 | 558.3 | 96.6 | 111.8 | 537.2 | 42.3 | 72.9 | 105 | 186.2 | 316.6 | 349.1 | 175.8 | 291.8 | 79.9 | 219.8 | 207.8 | 92 | 131.8 | 127.7 | 93
896 | 657 | 380.8 | 152.32 | 178.0533 | 210.3 | 218.9 | 220.1 | 196.2 | 334.4 | 32.8 | 20.4 | 61 | 4.2 | 199.2 | 6.7 | 246.7 | 542.9 | 773.6 | 260 | 302.4 | 774.4 | 290.8 | 384.3 | 566.9 | 96.8 | 112.1 | 538.9 | 42.5 | 73 | 105.1 | 186.6 | 317 | 347.3 | 175.3 | 292.3 | 80 | 220 | 208.1 | 92.2 | 132.1 | 127.9 | 93.2
897 | 658 | 381.4 | 152.56 | 178.3339 | 211.5 | 218.7 | 219.9 | 196.2 | 332.9 | 32.9 | 20.4 | 61.1 | 4 | 186.1 | 5.7 | 246.9 | 541.8 | 776.3 | 260.3 | 303 | 775.5 | 291.2 | 384.4 | 572.1 | 97 | 112.3 | 540.7 | 42.6 | 73.1 | 105.3 | 186.9 | 317.1 | 345.9 | 175.3 | 292.7 | 80.1 | 220.1 | 208.3 | 92.4 | 132.3 | 128.2 | 93.4
898 | 659 | 380.5 | 152.2 | 177.913 | 212.5 | 218.8 | 219.5 | 196.4 | 330.9 | 32.9 | 20.4 | 61.1 | 4 | 214.7 | 5.3 | 247.2 | 539.1 | 782.2 | 260.6 | 303.6 | 775.7 | 291.6 | 385.6 | 574.5 | 97.3 | 112.6 | 541.6 | 42.7 | 73.2 | 105.4 | 187.3 | 316.8 | 344.5 | 176 | 292.9 | 80.2 | 220.2 | 208.1 | 92.6 | 132.6 | 128.5 | 93.5
899 | 660 | 380.9 | 152.36 | 178.1001 | 213.3 | 219.1 | 219.2 | 197 | 330.4 | 33 | 20.3 | 61.2 | 3.9 | 203.3 | 5.3 | 247.6 | 536.5 | 787 | 261 | 304 | 774.8 | 292 | 386.6 | 578.9 | 97.5 | 112.9 | 541.9 | 42.8 | 73.3 | 105.6 | 187.6 | 317.6 | 344.2 | 176.4 | 293.4 | 80.4 | 220.6 | 208.9 | 92.7 | 132.8 | 128.7 | 93.7
900 | 661 | 381.9 | 152.76 | 178.5676 | 214.5 | 219.6 | 218.9 | 197.8 | 330.6 | 33 | 20.3 | 61.2 | 3.7 | 206.1 | 5.8 | 247.8 | 532.8 | 786 | 261.2 | 304.6 | 773.9 | 292.4 | 386.7 | 574.7 | 97.7 | 113.2 | 541 | 42.9 | 73.5 | 105.7 | 188 | 317.7 | 343.6 | 176.5 | 293.4 | 80.5 | 221.1 | 209.5 | 92.9 | 133.1 | 129 | 93.9
901 | 662 | 381.3 | 152.52 | 178.2871 | 215.1 | 220.5 | 217.9 | 197.9 | 330.6 | 33 | 20.3 | 61.2 | 3.5 | 219.1 | 7.3 | 248.1 | 530.3 | 792 | 261.5 | 305.2 | 775.1 | 292.8 | 386 | 578.9 | 98 | 113.4 | 541.4 | 43 | 73.6 | 105.8 | 188.4 | 317.8 | 343.9 | 176.9 | 293.6 | 80.7 | 221.1 | 209.7 | 93 | 133.2 | 129.2 | 94.1
902 | 663 | 385.5 | 154.2 | 180.2509 | 215 | 221.6 | 217.5 | 197.7 | 331.9 | 33 | 20.3 | 61.2 | 4.1 | 193.8 | 7.9 | 248.4 | 521.2 | 787.8 | 261.9 | 305.8 | 776.2 | 293.2 | 385.3 | 574.1 | 98.2 | 113.7 | 542.4 | 43.1 | 73.8 | 106.1 | 188.7 | 319.1 | 345.3 | 177.8 | 294 | 80.8 | 221.1 | 209.9 | 93.1 | 133.4 | 129.5 | 94.3
903 | 664 | 386.3 | 154.52 | 180.625 | 214.5 | 221.9 | 217.8 | 197.8 | 333.5 | 33.1 | 20.3 | 61.3 | 4.4 | 202.8 | 8.5 | 248.8 | 516.4 | 784 | 262.2 | 306.3 | 776.7 | 293.5 | 384.7 | 568.4 | 98.4 | 114 | 543 | 43.2 | 73.9 | 106.5 | 189.1 | 318.7 | 344.6 | 178.5 | 294.2 | 81 | 220.9 | 210.1 | 93.4 | 133.6 | 129.8 | 94.5
904 | 665 | 399.5 | 159.8 | 186.797 | 214.5 | 221.2 | 218 | 197.8 | 331.7 | 33.2 | 20.3 | 61.4 | 4.5 | 194.2 | 9 | 249.1 | 512.3 | 784.9 | 262.5 | 306.9 | 778.1 | 293.9 | 384.6 | 565 | 98.7 | 114.2 | 543 | 43.3 | 74.1 | 106.5 | 189.4 | 318.3 | 342.4 | 179.3 | 293.3 | 81.1 | 220.7 | 210 | 93.5 | 133.9 | 130 | 94.7
905 | 666 | 425.4 | 170.16 | 198.9072 | 214.1 | 220.7 | 218.5 | 197.7 | 330.3 | 33.3 | 20.3 | 61.5 | 4.2 | 196.8 | 8.9 | 249.4 | 509.9 | 787 | 262.8 | 307.4 | 779.2 | 294.3 | 385.1 | 570.3 | 98.9 | 114.5 | 543.1 | 43.4 | 74.2 | 106.6 | 189.8 | 317.6 | 341.4 | 180.1 | 293 | 81.2 | 220.7 | 210.1 | 93.6 | 134.1 | 130.3 | 94.8
906 | 667 | 442.6 | 177.04 | 206.9496 | 213.4 | 220.2 | 218.7 | 197.7 | 329.3 | 33.4 | 20.3 | 61.5 | 4.4 | 211.5 | 8.1 | 249.7 | 503.3 | 788.7 | 263.1 | 308 | 780.8 | 294.6 | 384.1 | 563.9 | 99.1 | 114.8 | 542.4 | 43.6 | 74.3 | 106.8 | 190.1 | 317.6 | 342.9 | 179.8 | 293.5 | 81.4 | 221 | 209.9 | 93.6 | 134.4 | 130.5 | 95
907 | 668 | 449.6 | 179.84 | 210.2226 | 212.8 | 219.3 | 218.6 | 197.8 | 331.8 | 33.5 | 20.3 | 61.6 | 4 | 209.5 | 8.4 | 250 | 503.4 | 795.1 | 263.4 | 308.7 | 782.1 | 295 | 384.9 | 576.3 | 99.4 | 115 | 544.8 | 43.7 | 74.5 | 107 | 190.5 | 318.7 | 351.2 | 182.5 | 294.7 | 81.5 | 221.1 | 210.4 | 93.7 | 134.5 | 130.7 | 95.2
908 | 669 | 451.7 | 180.68 | 211.2045 | 212.7 | 218.7 | 218.8 | 197.7 | 336.4 | 33.6 | 20.3 | 61.6 | 3.6 | 230.7 | 8.3 | 250.3 | 502.4 | 793.9 | 263.7 | 309.3 | 783 | 295.3 | 386 | 583.5 | 99.6 | 115.3 | 547.1 | 43.8 | 74.6 | 107.3 | 190.8 | 320.3 | 353.3 | 183.2 | 295.9 | 81.6 | 220.9 | 210.8 | 93.9 | 134.8 | 131 | 95.4
909 | 670 | 452.6 | 181.04 | 211.6253 | 212.7 | 218.2 | 218.7 | 198 | 338.9 | 33.7 | 20.3 | 61.6 | 3.6 | 219.1 | 8 | 250.5 | 499.3 | 781.1 | 264 | 309.7 | 783.3 | 295.7 | 385.3 | 578.5 | 99.8 | 115.5 | 547.1 | 43.9 | 74.8 | 107.6 | 191.2 | 321.2 | 354 | 183.9 | 296 | 81.7 | 221 | 210.9 | 94.1 | 135 | 131.2 | 95.6
910 | 671 | 452.5 | 181 | 211.5786 | 212.6 | 218.1 | 218.9 | 198.4 | 339.9 | 33.8 | 20.3 | 61.7 | 3.9 | 229.2 | 7.8 | 250.8 | 499.5 | 776.7 | 264.4 | 310.2 | 783.2 | 296 | 386.3 | 579.3 | 100.1 | 115.8 | 547.9 | 44 | 74.9 | 107.8 | 191.6 | 322.2 | 354.3 | 184.5 | 296.2 | 81.9 | 221.3 | 211.4 | 94.3 | 135.2 | 131.4 | 95.8
911 | 672 | 450.7 | 180.28 | 210.7369 | 213.1 | 218 | 219.6 | 198.5 | 342.5 | 33.8 | 20.3 | 61.7 | 3.8 | 214.2 | 7.1 | 251 | 497.7 | 803.7 | 264.6 | 310.7 | 783.6 | 296.4 | 387.9 | 583.5 | 100.3 | 116.1 | 549.7 | 44.1 | 75.1 | 108.1 | 191.9 | 322.9 | 356.2 | 184.1 | 296.6 | 82 | 221.8 | 211.3 | 94.4 | 135.4 | 131.7 | 96
912 | 673 | 452.6 | 181.04 | 211.6253 | 213.4 | 218.4 | 220.5 | 199 | 341.2 | 33.8 | 20.3 | 61.8 | 3.7 | 223.6 | 7.3 | 251.3 | 502.3 | 815.1 | 265 | 311.4 | 784 | 296.7 | 390.8 | 597.7 | 100.5 | 116.3 | 551.4 | 44.2 | 75.2 | 108.4 | 192.3 | 323.2 | 357.7 | 184.5 | 296.9 | 82.1 | 222.3 | 211.3 | 94.5 | 135.7 | 131.9 | 96.2
913 | 674 | 456.8 | 182.72 | 213.5892 | 213.7 | 218.7 | 221.2 | 199.6 | 344.1 | 33.9 | 20.3 | 61.8 | 4 | 202.2 | 9.8 | 251.6 | 506.3 | 816.6 | 265.3 | 311.9 | 784 | 297.1 | 394.3 | 604.1 | 100.8 | 116.6 | 554.4 | 44.3 | 75.3 | 108.7 | 192.6 | 325.9 | 362.8 | 185.4 | 298 | 82.3 | 223 | 211.6 | 94.6 | 135.9 | 132.1 | 96.3
914 | 675 | 457.4 | 182.96 | 213.8697 | 214.2 | 218.2 | 221.7 | 200.3 | 345.2 | 34 | 20.3 | 62 | 4.2 | 198.5 | 11.8 | 251.8 | 506.3 | 813.5 | 265.6 | 312.5 | 784.5 | 297.4 | 395.3 | 604.7 | 101 | 116.9 | 555.9 | 44.5 | 75.5 | 109 | 193 | 326.7 | 362.8 | 185.8 | 298.7 | 82.4 | 223.4 | 211.8 | 94.8 | 136.1 | 132.4 | 96.6
915 | 676 | 457.9 | 183.16 | 214.1035 | 213.8 | 217.9 | 222.4 | 201 | 348 | 34 | 20.3 | 62.1 | 4.1 | 200 | 12.1 | 252 | 504.8 | 799.8 | 265.9 | 313 | 785.9 | 297.8 | 396.5 | 596.7 | 101.2 | 117.1 | 556.4 | 44.6 | 75.6 | 109 | 193.3 | 328.1 | 363.9 | 186.6 | 299.2 | 82.5 | 224.6 | 211.9 | 95 | 136.4 | 132.6 | 96.8
916 | 677 | 457.2 | 182.88 | 213.7762 | 213.2 | 217.8 | 222.4 | 201.5 | 349 | 34.1 | 20.3 | 62.2 | 4.6 | 203 | 11.7 | 252.3 | 499.9 | 786.1 | 266.1 | 313.4 | 786.2 | 298.1 | 396.5 | 591 | 101.5 | 117.4 | 556.1 | 44.7 | 75.8 | 109.2 | 193.7 | 329.1 | 361.9 | 186.8 | 299 | 82.7 | 225.2 | 212.5 | 95.2 | 136.8 | 132.9 | 97
917 | 678 | 456.3 | 182.52 | 213.3554 | 213.7 | 217.8 | 222.8 | 202 | 347.7 | 34.2 | 20.3 | 62.3 | 4.3 | 215.4 | 10.2 | 252.5 | 500 | 785.5 | 266.4 | 313.8 | 786.5 | 298.4 | 396.7 | 583.7 | 101.7 | 117.7 | 555.8 | 44.8 | 75.9 | 109.5 | 194.1 | 328.9 | 362 | 187.6 | 298.6 | 82.8 | 225.3 | 212.5 | 95.4 | 136.9 | 133.2 | 97.2
918 | 679 | 457.1 | 182.84 | 213.7294 | 214.8 | 218 | 223.4 | 202.6 | 347.3 | 34.3 | 20.3 | 62.4 | 3.7 | 203.1 | 10.5 | 252.7 | 501 | 787.1 | 266.7 | 314.3 | 786.9 | 298.8 | 398.1 | 583.9 | 102 | 118 | 557.7 | 44.9 | 76.1 | 109.6 | 194.4 | 329.8 | 361.6 | 188.2 | 298.9 | 82.9 | 225.5 | 213.3 | 95.6 | 137.1 | 133.4 | 97.4
919 | 680 | 458.5 | 183.4 | 214.384 | 216.9 | 219.3 | 224.1 | 203.1 | 348.3 | 34.3 | 20.3 | 62.4 | 3.6 | 214.8 | 10.3 | 252.9 | 499.9 | 782.6 | 267 | 314.7 | 788.2 | 299.1 | 399 | 584.2 | 102.2 | 118.2 | 559 | 45 | 76.2 | 109.8 | 194.8 | 331.3 | 361.8 | 188.9 | 299.8 | 83.1 | 225.8 | 213.9 | 95.9 | 137.6 | 133.7 | 97.6
920 | 681 | 457.6 | 183.04 | 213.9632 | 219.2 | 220 | 224.5 | 203.9 | 345.9 | 34.4 | 20.3 | 62.4 | 3.5 | 209.3 | 9.6 | 253.1 | 498.5 | 793.8 | 267.4 | 315.3 | 789.6 | 299.5 | 398.9 | 588.7 | 102.5 | 118.5 | 560.2 | 45.1 | 76.4 | 109.8 | 195.2 | 331 | 359.4 | 188 | 299.8 | 83.2 | 226.1 | 213.8 | 96.1 | 137.9 | 134 | 97.8
921 | 682 | 460.5 | 184.2 | 215.3192 | 221.2 | 220.4 | 224.8 | 204.7 | 343.8 | 34.5 | 20.3 | 62.5 | 4.3 | 213 | 10.8 | 253.3 | 503.4 | 798.5 | 267.8 | 315.9 | 790.3 | 299.8 | 399.4 | 584.9 | 102.7 | 118.8 | 560.7 | 45.2 | 76.5 | 110 | 195.5 | 331 | 357.7 | 187.4 | 299.9 | 83.4 | 226.8 | 213.9 | 96.4 | 138.2 | 134.2 | 98
922 | 683 | 459.7 | 183.88 | 214.9451 | 222.9 | 221.5 | 224.8 | 205.5 | 343.5 | 34.5 | 20.3 | 62.5 | 4.5 | 207 | 12 | 253.3 | 507.3 | 816.2 | 268.1 | 316.5 | 791.8 | 300.2 | 402 | 597.3 | 103 | 119.1 | 563.2 | 45.3 | 76.6 | 110.2 | 195.9 | 331.6 | 360 | 187.7 | 300.7 | 83.5 | 227.5 | 214.9 | 96.8 | 138.5 | 134.5 | 98.2
923 | 684 | 459 | 183.6 | 214.6178 | 222.9 | 223 | 224.4 | 206.9 | 347.8 | 34.6 | 20.3 | 62.6 | 4 | 215.3 | 11.3 | 253.5 | 521.1 | 809.4 | 268.5 | 317.1 | 793 | 300.6 | 405 | 614.2 | 103.2 | 119.4 | 567.4 | 45.5 | 76.8 | 110.5 | 196.2 | 334.1 | 363.7 | 189.7 | 302.6 | 83.7 | 227.7 | 215.7 | 97 | 138.7 | 134.8 | 98.4
924 | 685 | 461.1 | 184.44 | 215.5997 | 223.5 | 223.9 | 224.4 | 208 | 352 | 34.6 | 20.3 | 62.7 | 3.4 | 210.4 | 10.7 | 253.6 | 531.6 | 812.6 | 268.8 | 317.4 | 793.3 | 301 | 409.1 | 626.6 | 103.5 | 119.6 | 570.3 | 45.6 | 77 | 110.8 | 196.6 | 336.1 | 367.8 | 190 | 304 | 83.9 | 227.9 | 216.1 | 97.1 | 139 | 135.1 | 98.6
925 | 686 | 462.9 | 185.16 | 216.4414 | 224.2 | 224.2 | 224.8 | 208.3 | 353.8 | 34.6 | 20.3 | 62.9 | 3.8 | 212.3 | 10.7 | 253.7 | 537.7 | 804.2 | 269.2 | 318 | 793.8 | 301.3 | 413.9 | 625.7 | 103.7 | 119.9 | 573.3 | 45.7 | 77.1 | 111.1 | 197 | 338 | 367 | 189.7 | 304.8 | 84.1 | 228.1 | 217 | 97.4 | 139.3 | 135.4 | 98.8
926 | 687 | 463.9 | 185.56 | 216.9089 | 224.9 | 224.4 | 225.3 | 208.7 | 354 | 34.7 | 20.3 | 63 | 4.1 | 206.5 | 11.3 | 253.8 | 541.3 | 808.8 | 269.5 | 318.6 | 793.9 | 301.7 | 416.2 | 627.4 | 104 | 120.2 | 574.4 | 45.8 | 77.3 | 111.1 | 197.3 | 338.7 | 366.3 | 189.9 | 305 | 84.2 | 228.5 | 217.8 | 97.7 | 139.8 | 135.7 | 99
927 | 688 | 464.8 | 185.92 | 217.3298 | 224.5 | 224.3 | 225.3 | 209.1 | 353.4 | 34.7 | 20.3 | 63.1 | 4 | 212.6 | 10.9 | 254 | 540.7 | 798.5 | 269.9 | 318.9 | 795 | 302.1 | 419 | 627.7 | 104.2 | 120.5 | 575.8 | 45.9 | 77.4 | 111.2 | 197.7 | 339.3 | 367.5 | 191.6 | 305 | 84.4 | 228.9 | 217.8 | 98 | 140 | 136 | 99.2
928 | 689 | 465.1 | 186.04 | 217.47 | 226 | 224.7 | 225.3 | 209.4 | 355 | 34.8 | 20.3 | 63.2 | 3.4 | 204.8 | 12.3 | 254.1 | 540.4 | 789.9 | 270.3 | 319.4 | 796.5 | 302.5 | 420.2 | 625.7 | 104.5 | 120.7 | 576.3 | 46 | 77.6 | 111.4 | 198 | 341.8 | 368.9 | 191.2 | 305.6 | 84.6 | 229.7 | 218.1 | 98.2 | 140.3 | 136.3 | 99.5
929 | 690 | 466.5 | 186.6 | 218.1246 | 229 | 224.8 | 225 | 209.9 | 356.3 | 34.9 | 20.3 | 63.4 | 4.1 | 211.4 | 12.8 | 254.2 | 544.8 | 793 | 270.6 | 319.7 | 797.4 | 302.9 | 420.9 | 619.6 | 104.7 | 121 | 577.8 | 46.1 | 77.8 | 111.8 | 198.4 | 344 | 370.6 | 190.6 | 306.1 | 84.8 | 229.9 | 219.1 | 98.3 | 140.7 | 136.7 | 99.7
930 | 691 | 467.5 | 187 | 218.5922 | 230.3 | 226.8 | 224.7 | 210.5 | 356.3 | 34.9 | 20.3 | 63.5 | 4 | 209.8 | 12 | 254.3 | 544.7 | 797.6 | 270.9 | 320.2 | 798.5 | 303.3 | 421.3 | 615.7 | 105 | 121.3 | 578.1 | 46.2 | 77.9 | 112 | 198.8 | 345 | 369.9 | 191.2 | 307 | 85 | 230.5 | 220 | 98.6 | 141.1 | 137 | 99.9
931 | 692 | 468.3 | 187.32 | 218.9663 | 230.4 | 227.7 | 225.1 | 211.1 | 356 | 35 | 20.3 | 63.6 | 3.6 | 203.7 | 11.7 | 254.5 | 544.1 | 804 | 271.4 | 320.7 | 800.5 | 303.7 | 422.4 | 623.7 | 105.3 | 121.5 | 580.6 | 46.3 | 78 | 112.1 | 199.1 | 345.4 | 369.3 | 191.4 | 307.2 | 85.2 | 230.9 | 221.2 | 98.8 | 141.5 | 137.3 | 100.1
932 | 693 | 466.3 | 186.52 | 218.0311 | 230.6 | 227 | 225.3 | 211.4 | 355.8 | 35.1 | 20.3 | 63.7 | 4 | 204 | 10.6 | 254.6 | 544.4 | 800.3 | 271.7 | 321.3 | 802.3 | 304.1 | 422.8 | 623.5 | 105.5 | 121.8 | 582.5 | 46.5 | 78.2 | 112.3 | 199.5 | 346.1 | 368.5 | 191.7 | 306.8 | 85.4 | 231.4 | 221.4 | 99 | 141.9 | 137.6 | 100.4
933 | 694 | 465.1 | 186.04 | 217.47 | 232.5 | 227 | 225.7 | 211.6 | 355.6 | 35.2 | 20.2 | 63.7 | 5 | 205.2 | 10.5 | 254.7 | 542.3 | 803.3 | 272 | 322 | 803.4 | 304.5 | 423.8 | 626.6 | 105.8 | 122.1 | 584.8 | 46.6 | 78.3 | 112.6 | 199.8 | 346.2 | 367.3 | 191.8 | 306.4 | 85.6 | 231.7 | 221.9 | 99.1 | 142.1 | 137.9 | 100.6
934 | 695 | 466.3 | 186.52 | 218.0311 | 234.2 | 227.9 | 226.1 | 212.4 | 355.6 | 35.3 | 20.2 | 63.8 | 5.6 | 220.4 | 10 | 254.8 | 539.5 | 799.4 | 272.4 | 322.6 | 804.3 | 304.9 | 423.7 | 630.3 | 106.1 | 122.4 | 586 | 46.7 | 78.5 | 112.7 | 200.2 | 345.7 | 365.7 | 192.2 | 306.4 | 85.8 | 232 | 222.1 | 99.2 | 142.4 | 138.2 | 100.8
935 | 696 | 467.3 | 186.92 | 218.4987 | 235.6 | 228 | 226.1 | 213 | 355.6 | 35.3 | 20.2 | 63.9 | 4.6 | 203.2 | 10.8 | 255 | 536.5 | 804.7 | 272.8 | 323 | 805.2 | 305.3 | 421.9 | 622.9 | 106.4 | 122.6 | 585.7 | 46.8 | 78.6 | 112.9 | 200.5 | 345.7 | 363.3 | 191.5 | 306 | 85.9 | 233.8 | 222.1 | 99.4 | 142.6 | 138.4 | 101.1
936 | 697 | 468.5 | 187.4 | 219.0598 | 237.5 | 228.8 | 226.5 | 213.6 | 355.3 | 35.4 | 20.2 | 64 | 4.4 | 208.6 | 12.2 | 255.1 | 534.7 | 814.8 | 273.2 | 323.7 | 806.4 | 305.7 | 421.6 | 619.2 | 106.6 | 122.9 | 586.2 | 46.9 | 78.8 | 113.1 | 200.9 | 346.4 | 364.1 | 191.7 | 306.9 | 86.1 | 234 | 222.3 | 99.6 | 142.9 | 138.7 | 101.3
937 | 698 | 468.7 | 187.48 | 219.1533 | 238.7 | 229.2 | 227.3 | 214.5 | 355.6 | 35.5 | 20.2 | 64.2 | 4.8 | 224.5 | 11.6 | 255.1 | 535.2 | 824.8 | 273.5 | 324.3 | 806.8 | 306.1 | 421.5 | 615.5 | 106.9 | 123.2 | 586.4 | 47 | 78.9 | 113.2 | 201.2 | 347.1 | 364.3 | 192.7 | 308.6 | 86.3 | 234 | 223.1 | 99.9 | 143.1 | 139 | 101.5
938 | 699 | 468.9 | 187.56 | 219.2468 | 238.6 | 228.5 | 227.8 | 215.2 | 355.5 | 35.5 | 20.2 | 64.3 | 4.8 | 224 | 11.2 | 255.2 | 533.2 | 819.4 | 273.8 | 324.6 | 807.1 | 306.5 | 422.7 | 611.4 | 107.2 | 123.5 | 588.3 | 47.1 | 79.1 | 113.4 | 201.6 | 347.2 | 363.8 | 192.6 | 308.5 | 86.5 | 234.1 | 223.3 | 100.2 | 143.3 | 139.3 | 101.7
939 | 700 | 469.1 | 187.64 | 219.3403 | 238.2 | 228.7 | 227.9 | 215.5 | 355.5 | 35.5 | 20.2 | 64.5 | 4.9 | 209.9 | 13.1 | 255.2 | 531.6 | 820.1 | 274.1 | 325.4 | 808 | 306.9 | 423.8 | 615 | 107.5 | 123.7 | 590.1 | 47.2 | 79.2 | 113.6 | 201.9 | 347.6 | 363.5 | 192.5 | 308.4 | 86.7 | 234.4 | 223.5 | 100.4 | 143.5 | 139.6 | 101.9
940 | 701 | 469.6 | 187.84 | 219.5741 | 238.3 | 229.8 | 228 | 216.2 | 356.5 | 35.5 | 20.2 | 64.6 | 5.9 | 227.4 | 12.4 | 255.1 | 532.1 | 830.3 | 274.5 | 326 | 808.4 | 307.3 | 423.8 | 622 | 107.8 | 124 | 592 | 47.4 | 79.4 | 113.7 | 202.3 | 348.6 | 364 | 193.2 | 308.6 | 86.9 | 234.9 | 223.8 | 100.7 | 143.8 | 139.8 | 102.1
941 | 702 | 470.5 | 188.2 | 219.995 | 238.4 | 229.8 | 228.5 | 216.8 | 359.2 | 35.5 | 20.2 | 64.7 | 4.9 | 209.1 | 11.8 | 255 | 535.3 | 842.4 | 274.8 | 326.5 | 809 | 307.7 | 425.4 | 626.7 | 108 | 124.3 | 594.4 | 47.5 | 79.4 | 114.1 | 202.6 | 349.7 | 367.5 | 193.3 | 309 | 87.1 | 235 | 223.6 | 101 | 144 | 140.1 | 102.4
942 | 703 | 470 | 188 | 219.7612 | 238.7 | 231 | 229 | 217 | 361.5 | 35.5 | 20.2 | 64.8 | 4.3 | 221 | 11.9 | 255.1 | 546 | 841.9 | 275.3 | 327.1 | 808.7 | 308.1 | 428.2 | 637.5 | 108.3 | 124.6 | 596.6 | 47.6 | 79.5 | 114.6 | 203 | 351.5 | 376.3 | 193.9 | 312.2 | 87.3 | 235.3 | 223.6 | 101.2 | 144.2 | 140.4 | 102.6
943 | 704 | 472.1 | 188.84 | 220.7431 | 238.9 | 233.8 | 229.7 | 216.7 | 368.4 | 35.6 | 20.2 | 64.9 | 4.3 | 234.3 | 10.4 | 255.1 | 551.1 | 841.9 | 275.6 | 327.6 | 806.9 | 308.6 | 431.4 | 644.5 | 108.6 | 124.9 | 598.6 | 47.7 | 79.7 | 115 | 203.4 | 354.3 | 385.3 | 195 | 315.5 | 87.5 | 235.6 | 223.6 | 101.6 | 144.5 | 140.7 | 102.8
944 | 705 | 467.6 | 187.04 | 218.639 | 238.6 | 235.3 | 231.7 | 216.5 | 370.6 | 35.7 | 20.2 | 65 | 4.2 | 230.1 | 9.5 | 255 | 548.2 | 846.3 | 275.8 | 328.1 | 806.4 | 309.1 | 433.1 | 648.1 | 108.9 | 125.1 | 600.4 | 47.8 | 79.9 | 115.3 | 203.7 | 354.2 | 386.8 | 195.3 | 315.2 | 87.6 | 236.1 | 223.4 | 101.7 | 144.6 | 141.1 | 103
945 | 706 | 471.2 | 188.48 | 220.3223 | 237.9 | 234.9 | 233 | 216.6 | 371.5 | 35.8 | 20.2 | 65.1 | 4.3 | 230.4 | 10.7 | 255 | 549.9 | 854.6 | 276.1 | 328.9 | 806.6 | 309.6 | 435.6 | 651.2 | 109.2 | 125.4 | 602.6 | 47.9 | 80 | 115.4 | 204.1 | 356 | 390.2 | 196.5 | 315.1 | 87.8 | 236.4 | 223.8 | 101.9 | 144.8 | 141.5 | 103.2
946 | 707 | 470.6 | 188.24 | 220.0417 | 236.6 | 234.3 | 233.2 | 216.7 | 372.5 | 35.9 | 20.2 | 65.1 | 4.4 | 222.8 | 11.1 | 255.1 | 555.1 | 851.3 | 276.5 | 329.5 | 807.2 | 310.1 | 438 | 651.9 | 109.5 | 125.7 | 605.3 | 48 | 80.1 | 115.5 | 204.5 | 357.9 | 394.1 | 196.1 | 316.4 | 88 | 236.6 | 224.1 | 102.2 | 145 | 141.8 | 103.4
947 | 708 | 470.8 | 188.32 | 220.1352 | 235.5 | 235.1 | 233.1 | 216.7 | 375 | 36 | 20.2 | 65.1 | 5 | 210.6 | 12.7 | 255.1 | 557.6 | 845 | 276.8 | 330.1 | 808.2 | 310.6 | 441.8 | 659.8 | 109.8 | 126 | 609 | 48.2 | 80.3 | 115.7 | 204.8 | 360.9 | 397.7 | 196.8 | 318.6 | 88.2 | 236.7 | 224.3 | 102.4 | 145.4 | 142.1 | 103.6
948 | 709 | 470.5 | 188.2 | 219.995 | 234.3 | 234.9 | 233.2 | 216.7 | 375.4 | 36 | 20.2 | 65.2 | 4.6 | 218.9 | 12.1 | 255.2 | 562.4 | 830.4 | 277 | 330.8 | 809.9 | 311.1 | 444 | 660.3 | 110.1 | 126.3 | 611.8 | 48.3 | 80.5 | 116 | 205.2 | 361.9 | 398.7 | 197.3 | 319.4 | 88.3 | 236.9 | 224.6 | 102.6 | 145.6 | 142.4 | 103.8
949 | 710 | 471.7 | 188.68 | 220.556 | 233.8 | 234.3 | 233.1 | 217.1 | 377.9 | 36.1 | 20.2 | 65.3 | 4.8 | 222.7 | 11.7 | 255.3 | 563.1 | 831.7 | 277.4 | 331.2 | 811.1 | 311.6 | 444.9 | 658.5 | 110.4 | 126.6 | 612.4 | 48.4 | 80.7 | 116.1 | 205.6 | 363.5 | 403.3 | 198.4 | 320.1 | 88.5 | 237.4 | 224.9 | 102.7 | 145.8 | 142.7 | 104
950 | 711 | 471.7 | 188.68 | 220.556 | 233.7 | 234.1 | 233.7 | 217.3 | 380.9 | 36.2 | 20.2 | 65.4 | 4.3 | 208.7 | 10.2 | 255.6 | 563.5 | 837.6 | 277.8 | 332 | 810.8 | 312 | 446.7 | 667.4 | 110.7 | 126.9 | 615.4 | 48.5 | 80.8 | 116.6 | 206 | 364.2 | 404.7 | 199.3 | 320.2 | 88.7 | 237.6 | 225.5 | 102.8 | 146.1 | 143 | 104.2
951 | 712 | 471.6 | 188.64 | 220.5093 | 233.4 | 233.5 | 234.4 | 217.5 | 381.9 | 36.3 | 20.2 | 65.4 | 4.2 | 252.2 | 7.9 | 256 | 565.9 | 847.1 | 278 | 332.5 | 809.5 | 312.5 | 447.8 | 672.2 | 111 | 127.2 | 616.1 | 48.6 | 80.9 | 117.1 | 206.4 | 364.1 | 406.9 | 199.4 | 319.6 | 88.8 | 238.2 | 225.9 | 102.9 | 146.5 | 143.4 | 104.5
952 | 713 | 471.8 | 188.72 | 220.6028 | 232.9 | 232.5 | 235.1 | 218.1 | 382.8 | 36.3 | 20.2 | 65.4 | 4.3 | 229.6 | 6.8 | 256.8 | 568.6 | 844.7 | 278.5 | 333.2 | 809.2 | 313.1 | 448.4 | 675.1 | 111.3 | 127.6 | 617.4 | 48.7 | 81 | 117.3 | 206.8 | 364 | 407 | 199.5 | 319.7 | 89 | 239.1 | 225.9 | 103.2 | 146.8 | 143.7 | 104.7
953 | 714 | 471.4 | 188.56 | 220.4158 | 231.9 | 231.8 | 235.7 | 218.4 | 381.7 | 36.4 | 20.2 | 65.4 | 4 | 230.1 | 7.1 | 257.5 | 574.7 | 833.8 | 278.9 | 333.7 | 809.6 | 313.7 | 449.5 | 668.8 | 111.6 | 127.9 | 617.5 | 48.8 | 81.2 | 117.4 | 207.2 | 363.4 | 407.4 | 199.1 | 320.1 | 89.2 | 239.4 | 226.6 | 103.3 | 147.2 | 144 | 104.9
954 | 715 | 472.1 | 188.84 | 220.7431 | 230.9 | 231.9 | 236 | 218.7 | 382.9 | 36.5 | 20.2 | 65.4 | 4.5 | 214 | 6.5 | 258.2 | 576.1 | 831.6 | 279.3 | 334.4 | 810.1 | 314.2 | 451.5 | 671.4 | 111.9 | 128.2 | 619 | 49 | 81.4 | 117.7 | 207.6 | 365.2 | 410.4 | 200.4 | 321.4 | 89.3 | 239.7 | 226.6 | 103.5 | 147.4 | 144.3 | 105.2
955 | 716 | 472 | 188.8 | 220.6963 | 230.1 | 232.5 | 236.1 | 219 | 387 | 36.5 | 20.2 | 65.5 | 4.7 | 263.4 | 5.6 | 258.7 | 579.2 | 841.4 | 279.6 | 334.8 | 811.1 | 314.8 | 452.9 | 677.4 | 112.3 | 128.5 | 620.6 | 49.1 | 81.5 | 118.1 | 208 | 367.2 | 413 | 201.1 | 322.8 | 89.5 | 240.4 | 226.4 | 103.6 | 147.7 | 144.6 | 105.4
956 | 717 | 472.2 | 188.88 | 220.7898 | 229.7 | 232.8 | 236 | 219.2 | 388.9 | 36.6 | 20.2 | 65.5 | 4.5 | 212 | 4.7 | 259.1 | 581.4 | 836.9 | 279.8 | 335.4 | 812.2 | 315.3 | 454.5 | 678.5 | 112.6 | 128.8 | 622.2 | 49.2 | 81.7 | 118.4 | 208.4 | 369.2 | 420.7 | 202.4 | 325.7 | 89.6 | 240.8 | 226.5 | 103.9 | 148 | 144.9 | 105.6
957 | 718 | 472.1 | 188.84 | 220.7431 | 229.3 | 233.6 | 235.9 | 219.2 | 394.5 | 36.6 | 20.2 | 65.6 | 4.3 | 203.1 | 4 | 259.7 | 578.6 | 832.2 | 280.1 | 336.1 | 813 | 315.9 | 455.1 | 678.5 | 112.9 | 129.1 | 623.1 | 49.3 | 81.8 | 118.8 | 208.8 | 372 | 425.1 | 203.2 | 327.8 | 89.8 | 240.9 | 226.8 | 103.9 | 148.2 | 145.3 | 105.9
958 | 719 | 471.5 | 188.6 | 220.4625 | 229 | 233.7 | 236.4 | 219.5 | 396.7 | 36.7 | 20.2 | 65.6 | 4 | 255.7 | 4 | 260.3 | 578.9 | 825.5 | 280.6 | 336.5 | 813.1 | 316.4 | 452.8 | 673.9 | 113.3 | 129.5 | 624.2 | 49.4 | 81.9 | 119 | 209.2 | 372.7 | 423.6 | 203.2 | 326.9 | 89.9 | 241 | 227 | 104 | 148.5 | 145.6 | 106.1
959 | 720 | 468.8 | 187.52 | 219.2001 | 228.5 | 233.8 | 237 | 219.6 | 393.1 | 36.7 | 20.2 | 65.7 | 4.4 | 226.2 | 4.8 | 260.8 | 592.2 | 826.1 | 281 | 337 | 813.3 | 317 | 455.2 | 676.5 | 113.6 | 129.8 | 626 | 49.5 | 82.1 | 119 | 209.6 | 372.5 | 420.5 | 203.1 | 326.9 | 90 | 241.3 | 226.9 | 104.3 | 148.8 | 145.9 | 106.3
960 | 721 | 473 | 189.2 | 221.1639 | 228.6 | 234 | 237.6 | 219.8 | 390.8 | 36.7 | 20.2 | 65.7 | 4.7 | 203.1 | 6.5 | 261.1 | 594.5 | 826.4 | 281.2 | 337.7 | 814.4 | 317.6 | 457.7 | 677.1 | 113.9 | 130.1 | 627.3 | 49.6 | 82.3 | 119.1 | 210 | 373.3 | 421.5 | 203.7 | 328 | 90.2 | 243.5 | 227.4 | 104.5 | 149.2 | 146.2 | 106.5
961 | 722 | 469.8 | 187.92 | 219.6677 | 230 | 234.9 | 237.6 | 220.2 | 391.1 | 36.8 | 20.2 | 65.8 | 4.5 | 222.8 | 6.8 | 261.6 | 591.9 | 833.8 | 281.6 | 338.4 | 815.1 | 318.2 | 459.1 | 682.4 | 114.3 | 130.4 | 629.5 | 49.7 | 82.4 | 119.5 | 210.4 | 374.9 | 422.8 | 204.4 | 329.1 | 90.3 | 244.5 | 228.4 | 104.7 | 149.5 | 146.6 | 106.8
962 | 723 | 468 | 187.2 | 218.826 | 230.9 | 235.6 | 237.3 | 220.9 | 393.2 | 36.9 | 20.2 | 65.8 | 3.8 | 231.5 | 6.6 | 262 | 592.7 | 836.2 | 282 | 339.3 | 814.6 | 318.7 | 459.3 | 679.6 | 114.6 | 130.8 | 631 | 49.8 | 82.6 | 119.8 | 210.8 | 376.4 | 428.7 | 205 | 330.1 | 90.5 | 244.5 | 228.7 | 104.9 | 149.7 | 146.9 | 107.1
963 | 724 | 468.3 | 187.32 | 218.9663 | 231 | 235.9 | 237.4 | 221.6 | 399 | 37 | 20.2 | 65.9 | 4.6 | 224.5 | 6.6 | 262.5 | 593.3 | 836.8 | 282.4 | 339.8 | 814.6 | 319.3 | 460.3 | 685.3 | 114.9 | 131.1 | 632.6 | 50 | 82.8 | 120.1 | 211.2 | 379 | 436.7 | 206 | 331.3 | 90.6 | 244.7 | 229.3 | 105.1 | 150.1 | 147.2 | 107.3
964 | 725 | 469.2 | 187.68 | 219.3871 | 230.6 | 236.5 | 237.7 | 221.6 | 402.9 | 37 | 20.2 | 65.9 | 4.5 | 250.2 | 7.3 | 262.8 | 603.7 | 826.3 | 282.8 | 340.6 | 814.5 | 319.9 | 462.1 | 690.1 | 115.3 | 131.4 | 634.9 | 50.1 | 83 | 120.3 | 211.6 | 381.2 | 439.8 | 206.4 | 334.4 | 90.8 | 244.9 | 229.2 | 105.2 | 150.5 | 147.5 | 107.5
965 | 726 | 468.8 | 187.52 | 219.2001 | 230.2 | 237.2 | 237.8 | 221.4 | 401.6 | 37.1 | 20.2 | 65.9 | 4 | 252.1 | 7.3 | 263.1 | 604.2 | 835.1 | 283.1 | 341.2 | 815.9 | 320.5 | 462.3 | 687.8 | 115.6 | 131.8 | 636.8 | 50.2 | 83.1 | 120.4 | 212 | 381.9 | 437.9 | 206.6 | 335.2 | 90.9 | 245 | 229.4 | 105.3 | 150.8 | 147.9 | 107.8
966 | 727 | 468.4 | 187.36 | 219.013 | 230.6 | 237.8 | 237.8 | 221.6 | 400.8 | 37.2 | 20.2 | 66 | 3.8 | 246.6 | 7.6 | 263.4 | 601.7 | 841.1 | 283.4 | 341.9 | 817.4 | 321.1 | 461.7 | 686 | 116 | 132.1 | 638.4 | 50.3 | 83.2 | 120.7 | 212.4 | 382.7 | 436.6 | 206.7 | 335.7 | 91.1 | 246 | 229.5 | 105.5 | 151 | 148.2 | 108
967 | 728 | 468.7 | 187.48 | 219.1533 | 231.8 | 237.3 | 237.8 | 222.3 | 398.5 | 37.3 | 20.2 | 66.1 | 3.7 | 245 | 8.1 | 263.8 | 598.3 | 842.9 | 283.9 | 342.6 | 818.5 | 321.7 | 462 | 685.4 | 116.3 | 132.5 | 638.7 | 50.4 | 83.3 | 121 | 212.7 | 382.1 | 433.7 | 206.9 | 335.4 | 91.2 | 246.4 | 230.1 | 105.7 | 151.3 | 148.6 | 108.2
968 | 729 | 470.5 | 188.2 | 219.995 | 232 | 238.1 | 237.9 | 223 | 396.6 | 37.3 | 20.2 | 66.2 | 3.8 | 227.7 | 9.1 | 264.2 | 597.7 | 839.2 | 284.4 | 343.4 | 818.5 | 322.3 | 463 | 688.7 | 116.6 | 132.8 | 639.4 | 50.5 | 83.5 | 121.2 | 213.1 | 382.9 | 437.7 | 207.6 | 335.8 | 91.4 | 246.8 | 230.2 | 106 | 151.6 | 148.9 | 108.5
969 | 730 | 472.1 | 188.84 | 220.7431 | 232.7 | 239.6 | 238 | 223.2 | 398.3 | 37.4 | 20.2 | 66.2 | 4 | 224.2 | 9.2 | 264.7 | 596.1 | 826.2 | 284.9 | 343.8 | 817.9 | 322.9 | 463 | 690.4 | 117 | 133.2 | 641 | 50.6 | 83.7 | 121.5 | 213.5 | 383.7 | 438.8 | 207.7 | 337 | 91.5 | 247.2 | 230.3 | 106.2 | 151.9 | 149.3 | 108.8
970 | 731 | 473.1 | 189.24 | 221.2107 | 232.3 | 239 | 238.2 | 223.3 | 401 | 37.4 | 20.2 | 66.3 | 4 | 212.7 | 7.6 | 265 | 600.6 | 832.7 | 285.2 | 344.5 | 817.2 | 323.5 | 462.4 | 694.1 | 117.3 | 133.5 | 643 | 50.7 | 83.9 | 121.9 | 213.9 | 384.1 | 441.3 | 208.6 | 337.8 | 91.7 | 246.9 | 230.2 | 106.4 | 152.1 | 149.6 | 109
971 | 732 | 473.7 | 189.48 | 221.4912 | 232.1 | 238.2 | 238.5 | 223 | 406.7 | 37.4 | 20.2 | 66.4 | 4.8 | 237.9 | 6.9 | 265.3 | 600.5 | 832.7 | 285.5 | 345.2 | 816.6 | 324.1 | 462.8 | 696.3 | 117.7 | 133.9 | 643.6 | 50.9 | 84 | 122.3 | 214.3 | 386.5 | 445.9 | 209.2 | 338.8 | 91.8 | 246.7 | 230.6 | 106.5 | 152.2 | 150 | 109.2
972 | 733 | 473.3 | 189.32 | 221.3042 | 231.7 | 238.3 | 238.7 | 222.9 | 414.5 | 37.5 | 20.2 | 66.5 | 4.9 | 227.6 | 7.6 | 265.9 | 613.4 | 813.5 | 286.1 | 346 | 815.5 | 324.7 | 463 | 704.1 | 118 | 134.2 | 644.7 | 51 | 84.3 | 122.7 | 214.7 | 389.3 | 455 | 210 | 341.3 | 92 | 246.7 | 230.4 | 106.5 | 152.4 | 150.3 | 109.4
973 | 734 | 472.5 | 189 | 220.9301 | 231.4 | 238.4 | 239.8 | 223.1 | 424.9 | 37.5 | 20.2 | 66.6 | 5 | 193.3 | 8.8 | 266.2 | 615.2 | 815.8 | 286.4 | 346.4 | 814 | 325.3 | 463.5 | 704.4 | 118.3 | 134.6 | 645.4 | 51.1 | 84.4 | 123.2 | 215.1 | 391 | 466.3 | 210.9 | 343.4 | 92.1 | 246.8 | 230.4 | 106.6 | 152.7 | 150.7 | 109.6
974 | 735 | 470.8 | 188.32 | 220.1352 | 231.6 | 238.4 | 240.9 | 223.1 | 432.1 | 37.6 | 20.2 | 66.6 | 5.4 | 207.6 | 8 | 266.6 | 621 | 823.5 | 286.9 | 347.1 | 813.1 | 326 | 466.2 | 706.4 | 118.7 | 135 | 647.8 | 51.2 | 84.6 | 123.5 | 215.5 | 393 | 472.5 | 212.1 | 345 | 92.2 | 247 | 230.4 | 106.8 | 153.1 | 151 | 109.9
975 | 736 | 471.2 | 188.48 | 220.3223 | 232 | 238.3 | 241.6 | 223.1 | 431.8 | 37.6 | 20.2 | 66.7 | 5.4 | 241.6 | 7.4 | 267 | 618.6 | 834.4 | 287.4 | 347.9 | 812 | 326.6 | 466.7 | 701.6 | 119 | 135.3 | 647.3 | 51.3 | 84.7 | 123.9 | 215.9 | 393.2 | 471.7 | 211.7 | 345.4 | 92.3 | 247.5 | 230.4 | 107 | 153.2 | 151.4 | 110.1
976 | 737 | 470.6 | 188.24 | 220.0417 | 232.3 | 239.5 | 242.5 | 223.4 | 431 | 37.7 | 20.2 | 66.7 | 5 | 255.7 | 7.3 | 267.4 | 625.5 | 836.7 | 287.7 | 348.6 | 812 | 327.2 | 468.4 | 707.8 | 119.4 | 135.7 | 648.5 | 51.4 | 84.9 | 124.1 | 216.3 | 394.1 | 473.7 | 212 | 346.6 | 92.5 | 247.9 | 230.7 | 107.1 | 153.4 | 151.7 | 110.3
977 | 738 | 472.2 | 188.88 | 220.7898 | 232.3 | 240 | 243.6 | 223.6 | 428.9 | 37.8 | 20.2 | 66.8 | 6.1 | 245 | 7.6 | 267.7 | 632.3 | 844 | 288 | 349.3 | 812.5 | 327.8 | 469.3 | 708.5 | 119.7 | 136.1 | 649.9 | 51.5 | 85 | 124.3 | 216.7 | 394.9 | 471.7 | 212.2 | 346.7 | 92.6 | 248.2 | 230.9 | 107.3 | 153.7 | 152 | 110.6
978 | 739 | 473 | 189.2 | 221.1639 | 231.9 | 239.5 | 244.3 | 223.8 | 425.9 | 37.8 | 20.1 | 66.9 | 5.8 | 263.8 | 7.7 | 268 | 634.9 | 849.9 | 288.3 | 349.9 | 812.8 | 328.5 | 471.8 | 714.7 | 120 | 136.4 | 650.6 | 51.6 | 85.3 | 124.5 | 217.2 | 394.9 | 469.6 | 212.4 | 346.7 | 92.7 | 248.4 | 231.1 | 107.5 | 154.1 | 152.4 | 110.8
979 | 740 | 470.9 | 188.36 | 220.182 | 231.7 | 239.7 | 244.5 | 223.8 | 425.1 | 37.8 | 20.1 | 67 | 5.6 | 267.3 | 6.9 | 268.5 | 635.7 | 852.4 | 288.8 | 350.7 | 812.7 | 329.1 | 473.3 | 719.9 | 120.4 | 136.8 | 653.4 | 51.7 | 85.6 | 124.7 | 217.6 | 396.7 | 471.1 | 213 | 348.8 | 92.9 | 248.6 | 231.2 | 107.6 | 154.3 | 152.7 | 111
980 | 741 | 471.4 | 188.56 | 220.4158 | 232.2 | 240.2 | 244.3 | 224.1 | 425.2 | 37.9 | 20.1 | 67.1 | 6.2 | 246.3 | 6.9 | 268.9 | 633.4 | 834.4 | 289.3 | 351 | 812.6 | 329.8 | 476 | 714.3 | 120.7 | 137.2 | 653.8 | 51.9 | 85.8 | 125 | 218 | 397.8 | 471.5 | 213.1 | 350.8 | 93 | 249 | 231.9 | 107.7 | 154.6 | 153.1 | 111.3
981 | 742 | 472.5 | 189 | 220.9301 | 233 | 241.1 | 244.3 | 224.1 | 422.6 | 37.9 | 20.1 | 67.2 | 6.1 | 229.4 | 7.4 | 269.5 | 628.6 | 828.4 | 289.8 | 351.6 | 811 | 330.4 | 475.9 | 703.2 | 121 | 137.5 | 654.8 | 52 | 86.1 | 125.2 | 218.4 | 398.5 | 467.8 | 213.1 | 351.8 | 93.1 | 249.2 | 232.5 | 107.9 | 154.8 | 153.5 | 111.5
982 | 743 | 472.7 | 189.08 | 221.0236 | 233.4 | 241.5 | 244.2 | 224.2 | 419.5 | 38 | 20.1 | 67.4 | 6.4 | 225 | 8.3 | 270.1 | 626.9 | 818.4 | 290.2 | 352.2 | 809.7 | 331.1 | 476 | 705.1 | 121.4 | 137.9 | 655.3 | 52.1 | 86.3 | 125.6 | 218.9 | 399.4 | 466.3 | 213 | 351.7 | 93.3 | 249.4 | 233.4 | 108.1 | 155 | 153.9 | 111.8
983 | 744 | 472.1 | 188.84 | 220.7431 | 234.1 | 241.8 | 244.4 | 224.3 | 422.5 | 38 | 20.1 | 67.5 | 5.1 | 250.2 | 9.2 | 270.6 | 630 | 817.5 | 290.4 | 352.8 | 809.6 | 331.8 | 476 | 707.1 | 121.7 | 138.3 | 658.4 | 52.2 | 86.5 | 126 | 219.3 | 402 | 468.3 | 213.6 | 353.5 | 93.4 | 249.7 | 234.1 | 108.2 | 155.3 | 154.2 | 112
984 | 745 | 472.1 | 188.84 | 220.7431 | 234.5 | 242.9 | 244.5 | 224.7 | 422.6 | 38 | 20.1 | 67.6 | 4.1 | 239.5 | 11.8 | 271.2 | 628.5 | 814.8 | 290.8 | 353.5 | 809.5 | 332.4 | 477 | 708.9 | 122 | 138.7 | 659.7 | 52.3 | 86.7 | 126.3 | 219.7 | 403 | 470.2 | 214.1 | 355.2 | 93.5 | 249.9 | 234.5 | 108.3 | 155.6 | 154.6 | 112.3
985 | 746 | 472.2 | 188.88 | 220.7898 | 234.4 | 243.2 | 244.5 | 224.6 | 420.3 | 38 | 20.1 | 67.7 | 4 | 246.7 | 12.4 | 271.7 | 626.1 | 822.7 | 291.2 | 354 | 810.2 | 333.1 | 476.3 | 710.7 | 122.4 | 139.1 | 659.5 | 52.4 | 86.9 | 126.5 | 220.1 | 401.8 | 466.8 | 213.6 | 354.2 | 93.7 | 249.9 | 234.7 | 108.5 | 155.9 | 155 | 112.5
986 | 747 | 472.8 | 189.12 | 221.0704 | 233.7 | 242.8 | 244.5 | 224.5 | 418.8 | 38.1 | 20.1 | 67.8 | 3.9 | 249.9 | 12.5 | 272.1 | 623.5 | 817.1 | 291.6 | 354.7 | 810 | 333.7 | 474 | 712.6 | 122.7 | 139.5 | 661.4 | 52.5 | 87.1 | 126.6 | 220.5 | 401.9 | 465.6 | 213.5 | 354.2 | 93.8 | 250.3 | 234.9 | 108.6 | 156.3 | 155.3 | 112.7
987 | 748 | 472 | 188.8 | 220.6963 | 233.2 | 241.8 | 244.5 | 224.3 | 417.4 | 38.1 | 20.1 | 67.8 | 4.5 | 244.2 | 13.4 | 272.6 | 615.7 | 800.4 | 292.2 | 355.2 | 811 | 334.4 | 474.1 | 699.2 | 123.1 | 139.9 | 663.2 | 52.6 | 87.3 | 126.9 | 220.9 | 401.9 | 463.1 | 213.3 | 354.3 | 93.9 | 250.5 | 235.2 | 108.8 | 156.5 | 155.7 | 113
988 | 749 | 472.1 | 188.84 | 220.7431 | 233.6 | 241.5 | 244.4 | 224.2 | 419.1 | 38.1 | 20.1 | 67.9 | 5.5 | 264.9 | 12.1 | 272.9 | 614.5 | 796.2 | 292.4 | 355.6 | 810.9 | 335.1 | 477.8 | 697.3 | 123.4 | 140.2 | 663.8 | 52.8 | 87.3 | 127.4 | 221.3 | 404 | 471.9 | 213.7 | 356.4 | 94.1 | 250.6 | 235.1 | 109.1 | 156.8 | 156 | 113.2
989 | 750 | 471.6 | 188.64 | 220.5093 | 234.5 | 241.6 | 244.6 | 224.1 | 422.9 | 38.2 | 20.1 | 68 | 5.8 | 259.5 | 10 | 273.2 | 610.8 | 796 | 292.7 | 356.3 | 810.3 | 335.7 | 476.2 | 694.3 | 123.8 | 140.6 | 665 | 52.9 | 87.3 | 127.6 | 221.7 | 405.8 | 475.8 | 214.5 | 357.1 | 94.2 | 250.8 | 235.9 | 109.2 | 157.1 | 156.3 | 113.4
990 | 751 | 472.5 | 189 | 220.9301 | 235.4 | 241 | 245.1 | 224 | 429.5 | 38.2 | 20.1 | 68.2 | 6 | 263.2 | 7.9 | 273.5 | 607.7 | 786.7 | 293 | 356.9 | 809.5 | 336.4 | 474.3 | 696.4 | 124.1 | 141 | 665 | 53 | 87.4 | 128 | 222.1 | 407.9 | 479.6 | 215 | 358 | 94.4 | 251.1 | 236.2 | 109.5 | 157.4 | 156.6 | 113.6
991 | 752 | 474.3 | 189.72 | 221.7717 | 236.2 | 240.4 | 245.6 | 224.3 | 426.8 | 38.3 | 20.1 | 68.3 | 5.5 | 217.2 | 7.5 | 273.9 | 610.3 | 794.4 | 293.4 | 357.3 | 808.6 | 337.1 | 473.3 | 705.1 | 124.5 | 141.4 | 667.8 | 53.1 | 87.6 | 128.1 | 222.5 | 406.1 | 473.9 | 215.1 | 357.2 | 94.5 | 251.5 | 236.1 | 109.7 | 157.7 | 157 | 113.9
992 | 753 | 472.5 | 189 | 220.9301 | 237.1 | 240.1 | 246.8 | 224.7 | 423.4 | 38.3 | 20.1 | 68.3 | 4.6 | 209.1 | 10.7 | 274.3 | 610.5 | 800 | 293.8 | 357.9 | 808.6 | 337.8 | 472.8 | 705.2 | 124.8 | 141.8 | 670 | 53.2 | 87.7 | 128.4 | 222.8 | 405.3 | 475.3 | 215.5 | 357.3 | 94.6 | 251.7 | 236.1 | 109.9 | 158 | 157.3 | 114.1
993 | 754 | 472.1 | 188.84 | 220.7431 | 237.6 | 240.7 | 247.7 | 225.2 | 425.5 | 38.4 | 20.1 | 68.3 | 4.7 | 211 | 12.4 | 274.6 | 610.5 | 810.4 | 294.2 | 358.4 | 808.5 | 338.5 | 471.8 | 709.4 | 125.2 | 142.3 | 673 | 53.4 | 87.8 | 128.8 | 223.3 | 405.8 | 472.7 | 215.8 | 357.6 | 94.8 | 252 | 236.4 | 110.1 | 158.3 | 157.6 | 114.4
994 | 755 | 472.7 | 189.08 | 221.0236 | 237.9 | 241.3 | 248.1 | 225.8 | 422.8 | 38.4 | 20.1 | 68.3 | 5.2 | 207.5 | 13.7 | 275 | 610.6 | 817.6 | 294.6 | 359 | 809 | 339.2 | 471.2 | 707.3 | 125.6 | 142.6 | 673.8 | 53.5 | 88 | 129 | 223.7 | 405.8 | 468.5 | 216.1 | 357.9 | 94.9 | 252.1 | 236.2 | 110.3 | 158.6 | 157.9 | 114.6
995 | 756 | 472.9 | 189.16 | 221.1171 | 238 | 242.4 | 248.8 | 226.1 | 420.4 | 38.5 | 20.1 | 68.3 | 6.2 | 201.1 | 15.5 | 275.4 | 610.9 | 812 | 294.9 | 359.8 | 810.3 | 339.9 | 471.3 | 709.7 | 125.9 | 143.1 | 675.2 | 53.6 | 88.2 | 129.1 | 224.1 | 405.6 | 462.1 | 216 | 358.1 | 95.1 | 252.2 | 236.4 | 110.5 | 158.9 | 158.3 | 114.8
996 | 757 | 473.5 | 189.4 | 221.3977 | 238.2 | 242.7 | 249.2 | 226.4 | 416.9 | 38.5 | 20.1 | 68.3 | 6.4 | 195.1 | 13.9 | 275.8 | 609.7 | 818.1 | 295.2 | 360.4 | 811.6 | 340.6 | 470.8 | 707.1 | 126.3 | 143.5 | 676.2 | 53.7 | 88.3 | 129.3 | 224.5 | 404.1 | 458.3 | 216 | 357.7 | 95.2 | 252.3 | 236.6 | 110.6 | 159.3 | 158.6 | 115.1
997 | 758 | 473.3 | 189.32 | 221.3042 | 238.3 | 243.5 | 248.4 | 226.5 | 415.4 | 38.5 | 20.1 | 68.4 | 5.6 | 207.1 | 15.7 | 276.1 | 606.9 | 824.1 | 295.6 | 360.8 | 812.5 | 341.3 | 468.9 | 706.6 | 126.6 | 143.9 | 677.5 | 53.8 | 88.5 | 129.7 | 224.8 | 404.3 | 458 | 216.7 | 359.1 | 95.3 | 252.6 | 237 | 110.8 | 159.6 | 159 | 115.3
998 | 759 | 473.2 | 189.28 | 221.2574 | 238.3 | 243.4 | 247.7 | 226.6 | 412.7 | 38.6 | 20.1 | 68.4 | 5.3 | 195.6 | 17.7 | 276.6 | 610.5 | 816.8 | 296 | 361.4 | 813.3 | 342.1 | 467.8 | 703.9 | 127 | 144.3 | 678.5 | 53.9 | 88.7 | 129.9 | 225.2 | 403.3 | 453.1 | 216.7 | 358.8 | 95.5 | 254 | 237.8 | 111 | 159.8 | 159.3 | 115.5
999 | 760 | 473.4 | 189.36 | 221.3509 | 238.4 | 243 | 247.8 | 227.3 | 409.3 | 38.6 | 20.1 | 68.4 | 5 | 180.6 | 15.9 | 276.9 | 604.6 | 814 | 296.3 | 362 | 813.7 | 342.8 | 467 | 704.1 | 127.3 | 144.7 | 679.8 | 54 | 89 | 130.3 | 225.6 | 401.9 | 450.8 | 216.7 | 358.5 | 95.6 | 254 | 238.2 | 111.1 | 160.2 | 159.7 | 115.8
1000 | 761 | 472.6 | 189.04 | 220.9769 | 238.9 | 242.7 | 248.4 | 227.8 | 412.2 | 38.6 | 20.1 | 68.5 | 4.9 | 226.9 | 10.7 | 277.3 | 604.3 | 808.2 | 296.8 | 362.3 | 813.3 | 343.5 | 466.2 | 700.8 | 127.7 | 145.1 | 679.6 | 54.2 | 89.2 | 130.9 | 226 | 403.1 | 454.7 | 217.5 | 358.8 | 95.8 | 254.2 | 238.3 | 111.3 | 160.5 | 160 | 116.1
1001 | 762 | 472.9 | 189.16 | 221.1171 | 239.4 | 242.7 | 249 | 228.2 | 417.5 | 38.7 | 20.1 | 68.7 | 4.4 | 209.1 | 10.9 | 277.7 | 604.5 | 798.3 | 297.1 | 362.9 | 812.4 | 344.2 | 465.5 | 704.6 | 128.1 | 145.5 | 678.7 | 54.3 | 89.5 | 131.5 | 226.4 | 405 | 459.9 | 217.9 | 360.5 | 95.9 | 254.5 | 238.6 | 111.5 | 160.6 | 160.3 | 116.3
1002 | 763 | 473.2 | 189.28 | 221.2574 | 239.4 | 242.4 | 250.4 | 228.5 | 422.1 | 38.7 | 20.1 | 68.8 | 4.2 | 212.6 | 13.8 | 278.1 | 600.3 | 789.9 | 297.4 | 363.4 | 811.7 | 344.9 | 466.1 | 704.7 | 128.4 | 145.9 | 682.8 | 54.4 | 89.7 | 131.7 | 226.7 | 406.5 | 465.3 | 218.8 | 362.8 | 96.1 | 254.7 | 239.3 | 111.7 | 160.8 | 160.6 | 116.6
1003 | 764 | 472.4 | 188.96 | 220.8834 | 239.2 | 241.8 | 251.6 | 228.7 | 424.7 | 38.7 | 20.1 | 68.9 | 4.2 | 192.4 | 16.3 | 278.4 | 598.9 | 788.6 | 297.7 | 363.8 | 811.5 | 345.6 | 466.6 | 704.2 | 128.8 | 146.3 | 680 | 54.5 | 90 | 131.9 | 227.1 | 406.6 | 466.6 | 219 | 363.8 | 96.2 | 254.7 | 239.6 | 111.8 | 161.1 | 160.9 | 116.8
1004 | 765 | 471.6 | 188.64 | 220.5093 | 239.2 | 241.7 | 251.7 | 229.1 | 424.5 | 38.7 | 20.1 | 69 | 5 | 198.2 | 13.7 | 278.8 | 600.7 | 788.8 | 298.1 | 364.3 | 811.6 | 346.4 | 467 | 713.8 | 129.1 | 146.7 | 685.3 | 54.6 | 90.1 | 132.1 | 227.4 | 406.5 | 464.4 | 219.7 | 363 | 96.3 | 254.6 | 239.5 | 111.8 | 161.4 | 161.2 | 117
1005 | 766 | 472.3 | 188.92 | 220.8366 | 239.6 | 241.7 | 251.9 | 229.5 | 425.6 | 38.6 | 20.1 | 69.1 | 4.9 | 199.2 | 13.5 | 279.2 | 597.5 | 789.3 | 298.5 | 364.7 | 811.6 | 347.1 | 469.5 | 714.2 | 129.4 | 147.1 | 686.8 | 54.7 | 90.4 | 132.5 | 227.8 | 408.2 | 467.8 | 220.3 | 365.1 | 96.5 | 254.9 | 239 | 112 | 161.6 | 161.5 | 117.3
1006 | 767 | 471.9 | 188.76 | 220.6496 | 239.8 | 241.6 | 252.5 | 229.6 | 427.1 | 38.6 | 20 | 69.1 | 5.8 | 201 | 14.5 | 279.6 | 598.3 | 797.9 | 299 | 365.1 | 810.7 | 347.8 | 467.7 | 710.3 | 129.8 | 147.5 | 685.6 | 54.8 | 90.6 | 132.9 | 228.1 | 409.2 | 465.7 | 220.6 | 366.1 | 96.6 | 255 | 238.6 | 112.2 | 161.8 | 161.8 | 117.5
1007 | 768 | 472.9 | 189.16 | 221.1171 | 240 | 241.6 | 253.2 | 229.8 | 427.1 | 38.6 | 20 | 69.1 | 5.9 | 202.8 | 14.8 | 280 | 597.5 | 803.8 | 299.4 | 365.7 | 809.8 | 348.5 | 467.7 | 714.2 | 130.1 | 147.9 | 684.6 | 54.9 | 90.7 | 133.2 | 228.4 | 409.5 | 468.5 | 220.9 | 365.9 | 96.8 | 255 | 238.3 | 112.4 | 162.1 | 162.1 | 117.7
1008 | 769 | 472.8 | 189.12 | 221.0704 | 240 | 241.3 | 254.4 | 230.1 | 433 | 38.6 | 20 | 69.1 | 5.7 | 207 | 14.3 | 280.4 | 596.9 | 806.4 | 299.8 | 366.1 | 808.7 | 349.3 | 468.1 | 722.8 | 130.5 | 148.4 | 685.1 | 55.1 | 90.9 | 133.8 | 228.8 | 410.9 | 472.8 | 221.4 | 367.7 | 96.9 | 255.1 | 238.1 | 112.6 | 162.3 | 162.5 | 118
1009 | 770 | 472.6 | 189.04 | 220.9769 | 240.4 | 242.9 | 255.3 | 230.1 | 437.1 | 38.6 | 20 | 69.2 | 5.2 | 216.6 | 15.5 | 280.7 | 598.2 | 799.2 | 300.1 | 366.4 | 808 | 350 | 468.8 | 723.4 | 130.8 | 148.8 | 689.1 | 55.2 | 91.2 | 134.2 | 229.1 | 410.8 | 473.1 | 221.7 | 369.2 | 97 | 255.3 | 238 | 112.8 | 162.5 | 162.8 | 118.2
1010 | 771 | 472.2 | 188.88 | 220.7898 | 241.4 | 244 | 256 | 230.2 | 438 | 38.7 | 20 | 69.3 | 5.4 | 212.6 | 19 | 281.1 | 599.8 | 779.2 | 300.6 | 366.8 | 806.4 | 350.8 | 467 | 722.7 | 131.1 | 149.2 | 686.1 | 55.3 | 91.4 | 134.5 | 229.4 | 411.2 | 475 | 222.1 | 370.3 | 97.2 | 255.4 | 237.8 | 113 | 162.6 | 163.2 | 118.4
1011 | 772 | 472.4 | 188.96 | 220.8834 | 241.6 | 244 | 256.9 | 230.6 | 442.6 | 38.8 | 20 | 69.3 | 6.2 | 205.4 | 20.6 | 281.5 | 600.1 | 770.7 | 301.1 | 367.3 | 803 | 351.5 | 467.7 | 723.9 | 131.5 | 149.6 | 690 | 55.4 | 91.6 | 135.1 | 229.7 | 413.6 | 476.8 | 222.7 | 372.1 | 97.3 | 255.4 | 238.2 | 113.1 | 162.8 | 163.5 | 118.7
1012 | 773 | 473.8 | 189.52 | 221.538 | 241.9 | 245.1 | 257.5 | 230.7 | 444.9 | 38.8 | 20 | 69.4 | 5.9 | 197.6 | 20.2 | 281.8 | 597.6 | 774.4 | 301.4 | 367.9 | 800.1 | 352.2 | 467.1 | 728.8 | 131.8 | 150 | 688.6 | 55.5 | 91.9 | 135.6 | 230 | 414.3 | 478.3 | 222.9 | 373.1 | 97.4 | 255.5 | 238.8 | 113.3 | 163.1 | 163.8 | 118.9
1013 | 774 | 475.4 | 190.16 | 222.2861 | 242.1 | 246.4 | 259 | 230.7 | 442.3 | 38.9 | 20 | 69.5 | 5.7 | 207.8 | 18.1 | 282.1 | 597.3 | 782.5 | 301.7 | 368.5 | 798.7 | 353 | 465.8 | 723.8 | 132.1 | 150.4 | 691.3 | 55.7 | 92.2 | 135.7 | 230.3 | 413.2 | 473 | 222.9 | 372.2 | 97.5 | 255.5 | 239.8 | 113.5 | 163.2 | 164.2 | 119.2
1014 | 775 | 475.1 | 190.04 | 222.1458 | 241.6 | 247.2 | 259.8 | 230.9 | 437.5 | 39 | 20 | 69.6 | 4.7 | 200.4 | 17.6 | 282.4 | 599.3 | 795.2 | 302 | 368.8 | 797.5 | 353.7 | 464.3 | 719.9 | 132.5 | 150.8 | 688.7 | 55.8 | 92.4 | 136 | 230.5 | 411.2 | 469.2 | 222.9 | 371.4 | 97.7 | 255.7 | 239.7 | 113.6 | 163.5 | 164.5 | 119.5
1015 | 776 | 473.5 | 189.4 | 221.3977 | 241.3 | 248 | 259.8 | 231.4 | 436 | 39 | 20 | 69.7 | 5.5 | 212.6 | 14.5 | 282.8 | 599.7 | 805.6 | 302.4 | 369.3 | 796.2 | 354.5 | 463.5 | 724 | 132.8 | 151.3 | 687 | 55.9 | 92.6 | 136.4 | 230.8 | 411.8 | 473.9 | 223.6 | 372.7 | 97.8 | 255.8 | 240.5 | 113.9 | 163.7 | 164.8 | 119.7
1016 | 777 | 473.2 | 189.28 | 221.2574 | 241.6 | 247.8 | 260.3 | 231.9 | 439.4 | 39 | 20 | 69.9 | 5.2 | 193.4 | 13.8 | 283.1 | 603.6 | 786.9 | 302.7 | 369.9 | 794.7 | 355.2 | 463.4 | 727.9 | 133.1 | 151.7 | 692 | 56 | 92.8 | 137 | 231.1 | 413.9 | 476.2 | 224.5 | 374.6 | 97.9 | 255.8 | 240.9 | 114 | 163.9 | 165.2 | 120
1017 | 778 | 472.4 | 188.96 | 220.8834 | 241.8 | 247.6 | 260.8 | 232.1 | 444.8 | 39 | 20 | 70 | 4.9 | 207.7 | 16.6 | 283.4 | 604.9 | 757.8 | 302.9 | 370.1 | 792.5 | 356 | 462.1 | 720 | 133.5 | 152.1 | 688.7 | 56.1 | 93.1 | 137.6 | 231.3 | 415.5 | 476.4 | 224.9 | 375 | 98.1 | 256.2 | 240.8 | 114.1 | 164 | 165.6 | 120.2
1018 | 779 | 472.2 | 188.88 | 220.7898 | 241.9 | 247.9 | 261.6 | 232.1 | 440.3 | 39 | 20 | 70 | 4.6 | 203.6 | 18.9 | 283.7 | 621.9 | 765.8 | 303.2 | 370.4 | 790.8 | 356.7 | 459.6 | 709.3 | 133.8 | 152.5 | 685.8 | 56.3 | 93.3 | 137.8 | 231.6 | 412.8 | 470.9 | 224.7 | 372.9 | 98.2 | 256.6 | 240.9 | 114.3 | 164.2 | 165.9 | 120.5
1019 | 780 | 472.7 | 189.08 | 221.0236 | 242.2 | 249.5 | 262.5 | 232.3 | 435.7 | 39 | 20 | 70 | 6.2 | 204.2 | 19.6 | 284.1 | 632 | 780.7 | 303.5 | 371.1 | 790.4 | 357.5 | 460.8 | 712.8 | 134.1 | 152.9 | 687.6 | 56.4 | 93.5 | 138.1 | 231.9 | 410.9 | 471.9 | 224.8 | 372.5 | 98.3 | 256.9 | 241.2 | 114.5 | 164.5 | 166.3 | 120.7
1020 | 781 | 472.6 | 189.04 | 220.9769 | 243 | 249.6 | 262.9 | 233 | 436.1 | 39 | 20 | 70 | 6.3 | 205.5 | 19.3 | 284.4 | 625.6 | 778.4 | 303.9 | 371.6 | 790.2 | 358.2 | 460.7 | 716.6 | 134.4 | 153.4 | 684.1 | 56.5 | 93.7 | 138.5 | 232.1 | 411.2 | 472 | 225 | 373.8 | 98.4 | 257.5 | 242 | 114.6 | 164.9 | 166.6 | 121
1021 | 782 | 474 | 189.6 | 221.6315 | 243.1 | 249.4 | 262.9 | 233.8 | 440.9 | 39.1 | 20 | 70.1 | 6.7 | 205.1 | 17.5 | 284.7 | 625.2 | 763.4 | 304.2 | 371.9 | 789.4 | 359 | 459.7 | 720.9 | 134.8 | 153.8 | 687.6 | 56.6 | 93.9 | 138.8 | 232.3 | 412.7 | 473 | 225.5 | 374.9 | 98.6 | 257.8 | 243.2 | 114.8 | 165.2 | 166.9 | 121.2
1022 | 783 | 472.9 | 189.16 | 221.1171 | 243.6 | 248.8 | 263.1 | 234.4 | 442.3 | 39.1 | 20 | 70.1 | 6 | 206.6 | 17.1 | 285 | 631.1 | 754.4 | 304.5 | 372.5 | 788.4 | 359.7 | 459.5 | 716.8 | 135.1 | 154.2 | 689.3 | 56.8 | 94.1 | 139 | 232.6 | 414.1 | 479 | 225.9 | 376.3 | 98.7 | 258 | 243.8 | 115 | 165.5 | 167.3 | 121.5
1023 | 784 | 471.6 | 188.64 | 220.5093 | 244.5 | 248.4 | 263.2 | 234.3 | 447.1 | 39.1 | 20 | 70.1 | 4.5 | 212.2 | 17.2 | 285.2 | 630.5 | 754.9 | 304.7 | 373.1 | 788.2 | 360.5 | 459.7 | 715.1 | 135.4 | 154.6 | 689.3 | 56.9 | 94.3 | 139.2 | 232.8 | 418 | 479.2 | 226.4 | 377.8 | 98.9 | 258.1 | 243.5 | 115.2 | 165.8 | 167.7 | 121.7
1024 | 785 | 471 | 188.4 | 220.2287 | 245.5 | 248.5 | 263.2 | 234 | 444.7 | 39.1 | 20 | 70.2 | 4.6 | 205.2 | 15.7 | 285.5 | 638.8 | 756.2 | 305.1 | 373.4 | 789 | 361.2 | 459.2 | 719.9 | 135.8 | 155.1 | 684.6 | 57 | 94.5 | 139.4 | 233 | 417.7 | 474.4 | 226.4 | 377.5 | 99 | 258.5 | 243.7 | 115.5 | 166.2 | 168 | 122
1025 | 786 | 472.6 | 189.04 | 220.9769 | 246.7 | 248.5 | 263.2 | 233.9 | 443.7 | 39.2 | 20 | 70.2 | 4.9 | 203 | 14.6 | 285.9 | 637 | 759.2 | 305.6 | 374 | 789 | 362 | 459.1 | 723.2 | 136.1 | 155.5 | 688.3 | 57.2 | 94.7 | 139.9 | 233.2 | 417.1 | 476.1 | 226.8 | 379.1 | 99.2 | 259.2 | 243.9 | 115.7 | 166.4 | 168.4 | 122.3
1026 | 787 | 472.6 | 189.04 | 220.9769 | 247.1 | 248.9 | 263.5 | 233.9 | 441.7 | 39.3 | 20 | 70.3 | 4.9 | 217.6 | 13.1 | 286.1 | 636.5 | 772.7 | 306 | 374.6 | 790 | 362.7 | 457.7 | 726.1 | 136.4 | 155.9 | 690.8 | 57.3 | 94.8 | 140.1 | 233.4 | 416.7 | 475.1 | 226.8 | 379.4 | 99.3 | 259.6 | 243.6 | 115.9 | 166.4 | 168.7 | 122.5
1027 | 788 | 472.3 | 188.92 | 220.8366 | 248.1 | 249 | 263.3 | 234.5 | 440.3 | 39.4 | 20 | 70.4 | 5.2 | 215 | 12.2 | 286.4 | 629 | 773.4 | 306.4 | 375.3 | 791.4 | 363.5 | 456.9 | 714.8 | 136.7 | 156.3 | 693.2 | 57.5 | 94.9 | 140.2 | 233.6 | 416.5 | 474.3 | 227.2 | 379.7 | 99.4 | 259.7 | 243.7 | 116.1 | 166.6 | 169.1 | 122.8
1028 | 789 | 472.9 | 189.16 | 221.1171 | 249.2 | 249.1 | 263.4 | 235.1 | 437.9 | 39.4 | 20 | 70.5 | 5.2 | 219.4 | 11.6 | 286.7 | 636 | 782.5 | 306.8 | 375.6 | 792.3 | 364.2 | 455.8 | 709.5 | 137.1 | 156.8 | 688.5 | 57.6 | 95 | 140.6 | 233.8 | 415.6 | 472.2 | 227.1 | 379.2 | 99.6 | 260.2 | 244.5 | 116.2 | 167 | 169.4 | 123
1029 | 790 | 473.1 | 189.24 | 221.2107 | 250.3 | 250.6 | 263.7 | 235.7 | 438.7 | 39.5 | 20 | 70.5 | 4.6 | 212 | 12.8 | 286.9 | 633.7 | 771.5 | 307.2 | 376.3 | 792.8 | 364.9 | 456.1 | 717.3 | 137.4 | 157.2 | 692.8 | 57.7 | 95.2 | 141.2 | 234 | 416.5 | 473.4 | 227.3 | 380.5 | 99.8 | 260.5 | 245 | 116.4 | 167.3 | 169.8 | 123.3
1030 | 791 | 472.7 | 189.08 | 221.0236 | 251 | 251.3 | 263.9 | 236 | 442.3 | 39.5 | 20 | 70.6 | 4.8 | 207 | 12.2 | 287.2 | 640.9 | 758 | 307.6 | 376.7 | 792 | 365.7 | 455.4 | 716 | 137.7 | 157.6 | 693.2 | 57.9 | 95.4 | 141.6 | 234.2 | 417.1 | 472.2 | 227.4 | 380.5 | 99.9 | 260.8 | 244.9 | 116.5 | 167.5 | 170.2 | 123.5
1031 | 792 | 472.4 | 188.96 | 220.8834 | 251.5 | 251.8 | 264.1 | 236.3 | 440.6 | 39.5 | 20 | 70.7 | 4.4 | 210.6 | 12.6 | 287.5 | 641.1 | 766.5 | 308 | 377 | 791.5 | 366.4 | 455.6 | 720 | 138.1 | 158.1 | 692 | 58 | 95.7 | 142 | 234.4 | 416.2 | 470.9 | 227.4 | 379.4 | 100.1 | 261 | 245.1 | 116.6 | 167.8 | 170.5 | 123.8
1032 | 793 | 471.3 | 188.52 | 220.369 | 251.8 | 251.7 | 264.9 | 236.7 | 440.9 | 39.5 | 20 | 70.8 | 4.4 | 215.7 | 11.6 | 287.8 | 648.2 | 773.9 | 308.4 | 377.6 | 791.6 | 367.1 | 456.4 | 723.5 | 138.4 | 158.5 | 693 | 58.1 | 95.9 | 142.2 | 234.6 | 416.3 | 471.3 | 227.4 | 380.3 | 100.2 | 261.2 | 245.9 | 116.8 | 168.1 | 170.8 | 124
1033 | 794 | 470.8 | 188.32 | 220.1352 | 252 | 252 | 265.4 | 236.9 | 442.2 | 39.6 | 20 | 70.9 | 5.2 | 219 | 10 | 288.1 | 639.6 | 771.6 | 308.8 | 378.4 | 792.1 | 367.9 | 456.2 | 719.4 | 138.7 | 158.9 | 695.1 | 58.3 | 96.2 | 142.6 | 234.9 | 417.1 | 471.2 | 227.4 | 381.4 | 100.4 | 261.6 | 246.6 | 117 | 168.3 | 171.1 | 124.3
1034 | 795 | 470.4 | 188.16 | 219.9482 | 252.2 | 252 | 265.1 | 237.1 | 439.7 | 39.6 | 20 | 71.1 | 6.2 | 217.1 | 10.1 | 288.3 | 642.6 | 766.5 | 309.1 | 378.7 | 793.3 | 368.6 | 456.3 | 709.7 | 139.1 | 159.4 | 696.6 | 58.4 | 96.4 | 142.8 | 235.1 | 415.4 | 465 | 227.3 | 379.8 | 100.6 | 261.7 | 247.1 | 117.3 | 168.6 | 171.5 | 124.5
1035 | 796 | 471.8 | 188.72 | 220.6028 | 252.4 | 251.6 | 265 | 237.6 | 436.1 | 39.6 | 20 | 71.2 | 5.3 | 228.4 | 11.4 | 288.5 | 644.7 | 768.4 | 309.4 | 379.1 | 793.5 | 369.3 | 459.3 | 708.3 | 139.4 | 159.8 | 691.6 | 58.6 | 96.7 | 143 | 235.3 | 414.9 | 464.6 | 227.4 | 379.4 | 100.7 | 261.8 | 246.6 | 117.5 | 168.9 | 171.8 | 124.8
1036 | 797 | 471.3 | 188.52 | 220.369 | 253 | 251.3 | 265.4 | 237.9 | 438.2 | 39.6 | 20 | 71.4 | 4.7 | 241 | 10.9 | 288.8 | 651.2 | 782 | 309.7 | 379.9 | 792.9 | 370 | 459.8 | 713.9 | 139.7 | 160.3 | 692.5 | 58.7 | 97 | 143.5 | 235.6 | 418 | 465.7 | 227.5 | 380.5 | 100.9 | 262 | 246.4 | 117.7 | 169.2 | 172.1 | 125
1037 | 798 | 470.7 | 188.28 | 220.0885 | 253.4 | 251 | 265.6 | 237.8 | 442.1 | 39.7 | 20 | 71.4 | 4.6 | 203.2 | 9.5 | 289 | 646.9 | 800.4 | 310 | 380.4 | 793.1 | 370.7 | 460.2 | 718 | 140.1 | 160.7 | 693.3 | 58.8 | 97.2 | 143.8 | 235.8 | 419.3 | 470.4 | 227.9 | 382.3 | 101 | 262 | 246.3 | 117.8 | 169.6 | 172.4 | 125.3
1038 | 799 | 472.5 | 189 | 220.9301 | 253.7 | 251.4 | 266 | 237.3 | 446.6 | 39.7 | 20 | 71.4 | 4.1 | 252.7 | 9 | 289.3 | 649.3 | 809.7 | 310.4 | 381.3 | 794.4 | 371.4 | 461.6 | 723.3 | 140.4 | 161.2 | 694.8 | 59 | 97.5 | 143.9 | 236 | 421.7 | 479 | 228.4 | 384.1 | 101.2 | 262.1 | 246.3 | 118 | 169.9 | 172.7 | 125.5
1039 | 800 | 472.5 | 189 | 220.9301 | 253.8 | 253.4 | 266 | 236.9 | 448.7 | 39.8 | 19.9 | 71.5 | 4.4 | 242.8 | 8.5 | 289.5 | 644.3 | 797.9 | 310.7 | 381.7 | 795.8 | 372.1 | 463 | 723.9 | 140.7 | 161.6 | 694.6 | 59.1 | 97.7 | 144.1 | 236.3 | 422.4 | 478.7 | 228.9 | 384.3 | 101.3 | 262.3 | 246.6 | 118.3 | 170.3 | 173.1 | 125.7
1040 | 801 | 472.7 | 189.08 | 221.0236 | 253.8 | 254.5 | 265.7 | 236.7 | 447.2 | 39.8 | 19.9 | 71.5 | 3.5 | 242.4 | 8 | 289.8 | 636.6 | 785.3 | 311.1 | 382.2 | 797.2 | 372.8 | 462.8 | 725.3 | 141.1 | 162.1 | 693.1 | 59.2 | 97.9 | 144.4 | 236.5 | 423.1 | 477.6 | 229.4 | 384.2 | 101.5 | 262.9 | 247 | 118.5 | 170.5 | 173.5 | 126
1041 | 802 | 472.3 | 188.92 | 220.8366 | 253.7 | 254.7 | 265.1 | 236.7 | 447.7 | 39.9 | 19.9 | 71.5 | 3.7 | 246.1 | 7.7 | 290 | 640.2 | 786.1 | 311.5 | 382.6 | 797.4 | 373.5 | 462.1 | 728.6 | 141.4 | 162.6 | 696 | 59.4 | 98 | 144.9 | 236.8 | 424.5 | 480.1 | 230.3 | 384.9 | 101.7 | 263.1 | 247.8 | 118.7 | 170.8 | 173.9 | 126.3
1042 | 803 | 472.1 | 188.84 | 220.7431 | 254.1 | 254.8 | 265.5 | 236.7 | 447.1 | 40 | 19.9 | 71.5 | 4.8 | 238.8 | 8.3 | 290.2 | 644.2 | 797.2 | 311.8 | 383.4 | 798 | 374.2 | 462.9 | 732.3 | 141.7 | 163.1 | 698.4 | 59.5 | 98.2 | 145.1 | 237.2 | 424.6 | 478.5 | 230.9 | 385.4 | 101.8 | 263.1 | 247.7 | 118.9 | 171.1 | 174.2 | 126.5
1043 | 804 | 473.3 | 189.32 | 221.3042 | 254.1 | 254.8 | 266.3 | 236.9 | 442.9 | 40 | 19.9 | 71.5 | 4.8 | 204.3 | 10.4 | 290.4 | 642 | 800.1 | 312.1 | 384.2 | 799.3 | 374.8 | 463.7 | 733.1 | 142 | 163.5 | 701.6 | 59.7 | 98.3 | 145.1 | 237.7 | 423.7 | 476.8 | 231.4 | 385.2 | 102 | 263.2 | 247.8 | 119.1 | 171.4 | 174.6 | 126.8
1044 | 805 | 474.4 | 189.76 | 221.8185 | 253.7 | 254.2 | 266.1 | 237 | 439.1 | 40.1 | 19.9 | 71.6 | 4.2 | 233.7 | 10.9 | 290.6 | 640.9 | 805.5 | 312.4 | 384.7 | 799.8 | 375.6 | 464.4 | 730.1 | 142.4 | 164 | 699.1 | 59.8 | 98.5 | 145.2 | 238.1 | 422.1 | 473 | 231.7 | 385.1 | 102.1 | 263.3 | 247.6 | 119.4 | 171.7 | 174.9 | 127
1045 | 806 | 472.8 | 189.12 | 221.0704 | 253.1 | 254.6 | 265.4 | 237.3 | 433.5 | 40 | 19.9 | 71.6 | 4.4 | 226.6 | 11.3 | 290.8 | 638.5 | 813.3 | 312.8 | 384.9 | 800.6 | 376.2 | 466.5 | 728 | 142.7 | 164.5 | 700.8 | 59.9 | 98.7 | 145.5 | 238.5 | 419.9 | 469.2 | 231.9 | 386.1 | 102.3 | 263.6 | 248 | 119.7 | 172 | 175.3 | 127.3
1046 | 807 | 472.5 | 189 | 220.9301 | 253.6 | 256.6 | 264.7 | 237.4 | 431.5 | 40.1 | 19.9 | 71.6 | 4.8 | 234.4 | 10 | 291 | 636.7 | 808.7 | 313.2 | 385.7 | 800.8 | 376.9 | 468.2 | 726.5 | 143 | 165 | 701.1 | 60.1 | 99 | 145.6 | 238.9 | 419.6 | 470.5 | 232.3 | 386.4 | 102.5 | 263.7 | 249 | 119.9 | 172.3 | 175.7 | 127.5
1047 | 808 | 472.5 | 189 | 220.9301 | 255.1 | 257.5 | 263.8 | 237.9 | 431.3 | 40.1 | 19.9 | 71.7 | 4.9 | 245.8 | 7.9 | 291.2 | 635.9 | 812.5 | 313.6 | 386.3 | 800.5 | 377.5 | 470.5 | 727.5 | 143.4 | 165.5 | 702.1 | 60.2 | 99.3 | 145.9 | 239.2 | 419.7 | 470.6 | 232.5 | 387.7 | 102.6 | 264.1 | 249.8 | 120.2 | 172.6 | 176 | 127.8
1048 | 809 | 472.4 | 188.96 | 220.8834 | 256 | 259.6 | 262.5 | 238.1 | 431.2 | 40.1 | 19.9 | 71.8 | 5.1 | 217.3 | 7.7 | 291.4 | 637.4 | 819.9 | 314.1 | 386.7 | 800.1 | 378.2 | 471.1 | 725.9 | 143.7 | 166 | 698 | 60.4 | 99.5 | 146.1 | 239.6 | 418.9 | 469.3 | 232.8 | 387.7 | 102.8 | 264.5 | 250.5 | 120.3 | 172.9 | 176.4 | 128
1049 | 810 | 472 | 188.8 | 220.6963 | 256.3 | 261.4 | 260.9 | 238.6 | 428.4 | 40.2 | 19.9 | 71.9 | 4.5 | 245.5 | 9 | 291.7 | 638.6 | 826.7 | 314.6 | 387.2 | 800.1 | 378.8 | 472.2 | 725 | 144.1 | 166.5 | 697.4 | 60.5 | 99.8 | 146.4 | 240 | 418 | 468.2 | 233.3 | 388.4 | 103 | 264.3 | 250.9 | 120.5 | 173.2 | 176.9 | 128.3
1050 | 811 | 472.7 | 189.08 | 221.0236 | 255.5 | 262 | 260.8 | 238.6 | 428 | 40.2 | 19.9 | 71.9 | 5.1 | 241.1 | 9.4 | 291.8 | 635.2 | 829.7 | 314.9 | 387.8 | 800.1 | 379.4 | 473.9 | 725.5 | 144.4 | 167 | 695.5 | 60.7 | 100 | 146.6 | 240.4 | 418.2 | 469.9 | 233.6 | 389.4 | 103.2 | 264.2 | 251.1 | 120.6 | 173.6 | 177.3 | 128.6
1051 | 812 | 473.8 | 189.52 | 221.538 | 254.3 | 263.5 | 260.3 | 238.7 | 428.3 | 40.3 | 19.9 | 72 | 4.7 | 248.3 | 10.9 | 292 | 635.1 | 816.4 | 315.3 | 388.2 | 800.2 | 380.1 | 476.4 | 722.6 | 144.8 | 167.4 | 697.8 | 60.8 | 100.3 | 146.8 | 240.8 | 419.4 | 470 | 234.1 | 391.1 | 103.3 | 264.3 | 250.8 | 120.9 | 173.8 | 177.7 | 128.8
1052 | 813 | 474.8 | 189.92 | 222.0055 | 254 | 263.8 | 259.8 | 238.8 | 428.8 | 40.3 | 19.9 | 72.1 | 5.1 | 251.6 | 11.4 | 292.2 | 639.3 | 822 | 315.8 | 388.7 | 799.4 | 380.7 | 478.7 | 732.3 | 145.1 | 167.9 | 695.2 | 61 | 100.5 | 147 | 241.2 | 421.9 | 474.6 | 234.6 | 393.9 | 103.5 | 264.5 | 251.3 | 121 | 174 | 178.1 | 129.1
1053 | 814 | 474.1 | 189.64 | 221.6782 | 253.9 | 263.4 | 258.8 | 238.5 | 432.4 | 40.4 | 19.9 | 72.2 | 6.6 | 237 | 10.4 | 292.4 | 642 | 831.6 | 316.1 | 389.6 | 798.6 | 381.3 | 480.4 | 739.6 | 145.4 | 168.4 | 694.9 | 61.1 | 100.7 | 147.4 | 241.6 | 423.7 | 481 | 235.3 | 396.4 | 103.7 | 264.5 | 251.4 | 121.2 | 174.3 | 178.6 | 129.3
1054 | 815 | 473.8 | 189.52 | 221.538 | 253 | 262.8 | 257.8 | 238.2 | 439.3 | 40.4 | 19.9 | 72.3 | 8 | 247.5 | 10.8 | 292.6 | 644 | 835.1 | 316.5 | 389.6 | 798.5 | 381.9 | 482.7 | 736.6 | 145.8 | 168.9 | 694.9 | 61.3 | 100.9 | 147.8 | 241.9 | 427.7 | 492.3 | 236.4 | 400.4 | 103.9 | 264.7 | 251.5 | 121.3 | 174.5 | 179 | 129.6
1055 | 816 | 473.2 | 189.28 | 221.2574 | 252.1 | 261.9 | 257.7 | 237.8 | 449.5 | 40.5 | 19.9 | 72.3 | 6 | 243.8 | 11.6 | 292.8 | 639.4 | 837.4 | 317 | 390.2 | 798.9 | 382.5 | 484.5 | 742.5 | 146.1 | 169.3 | 693.2 | 61.4 | 101 | 148.1 | 242.3 | 431.6 | 499.8 | 237.3 | 404.6 | 104.1 | 264.8 | 251.3 | 121.5 | 174.8 | 179.5 | 129.8
1056 | 817 | 473.1 | 189.24 | 221.2107 | 251.6 | 261.7 | 257.4 | 237.2 | 456.2 | 40.5 | 19.9 | 72.3 | 4.5 | 236.1 | 11.9 | 293.1 | 642.2 | 827.5 | 317.4 | 390.7 | 799.5 | 383.1 | 487.3 | 751.9 | 146.5 | 169.8 | 696.8 | 61.6 | 101.1 | 148.3 | 242.7 | 436.8 | 511.3 | 238.2 | 408.3 | 104.2 | 264.7 | 251.1 | 121.6 | 175.2 | 180 | 130
1057 | 818 | 474.3 | 189.72 | 221.7717 | 251.7 | 260.5 | 257.7 | 237.1 | 457.1 | 40.6 | 19.9 | 72.2 | 3.8 | 221.8 | 10.3 | 293.2 | 644.7 | 808.8 | 317.7 | 391 | 800.8 | 383.8 | 486.9 | 753.1 | 146.8 | 170.2 | 697 | 61.7 | 101.3 | 148.5 | 243.1 | 437.9 | 511 | 239 | 407.6 | 104.4 | 264.9 | 251.2 | 121.8 | 175.3 | 180.5 | 130.3
1058 | 819 | 473.5 | 189.4 | 221.3977 | 251.6 | 259.1 | 257.5 | 237.3 | 455 | 40.6 | 19.9 | 72.3 | 4.7 | 235 | 8.5 | 293.4 | 640.5 | 804.2 | 318.1 | 391.8 | 802.5 | 384.4 | 488.1 | 744.3 | 147.2 | 170.7 | 697 | 61.9 | 101.6 | 148.6 | 243.4 | 437.5 | 509.5 | 239.3 | 406.2 | 104.6 | 265.3 | 251.5 | 122 | 175.5 | 181 | 130.5
1059 | 820 | 474.6 | 189.84 | 221.912 | 252 | 258.3 | 257.4 | 237.7 | 454 | 40.7 | 19.9 | 72.4 | 5 | 235.5 | 8.3 | 293.6 | 651.8 | 786.1 | 318.5 | 392.2 | 802.8 | 384.9 | 490.8 | 736.2 | 147.6 | 171.2 | 698.8 | 62 | 101.7 | 149 | 243.8 | 438.3 | 508.8 | 240 | 406.1 | 104.7 | 265.4 | 251.5 | 122.2 | 175.7 | 181.4 | 130.8
1060 | 821 | 473.7 | 189.48 | 221.4912 | 253.1 | 257.5 | 258 | 237.7 | 455.8 | 40.8 | 19.9 | 72.5 | 5.8 | 237.1 | 9 | 293.8 | 650.6 | 769.6 | 319 | 392.4 | 801.8 | 385.5 | 497 | 725.9 | 147.9 | 171.6 | 694.8 | 62.2 | 101.9 | 149.8 | 244.1 | 438.8 | 511.6 | 240.4 | 405.9 | 104.9 | 265.7 | 252.1 | 122.4 | 175.9 | 181.8 | 131
1061 | 822 | 474 | 189.6 | 221.6315 | 254.1 | 257 | 258.5 | 237.7 | 460.2 | 40.8 | 19.9 | 72.6 | 5 | 242 | 8.1 | 294.1 | 661.8 | 762.3 | 319.4 | 392.7 | 800.3 | 386 | 502.2 | 717.5 | 148.3 | 172 | 692.2 | 62.3 | 102.1 | 150 | 244.5 | 439.9 | 515 | 240.8 | 406.8 | 105.1 | 265.9 | 252.8 | 122.6 | 176.2 | 182.2 | 131.3
1062 | 823 | 474.2 | 189.68 | 221.725 | 254.5 | 256.6 | 259.5 | 237.6 | 463.3 | 40.8 | 19.9 | 72.7 | 4.3 | 242.7 | 8 | 294.2 | 664.9 | 752.2 | 319.6 | 393.2 | 799.6 | 386.6 | 503.8 | 720.1 | 148.7 | 172.5 | 692.1 | 62.5 | 102.3 | 150.1 | 244.8 | 440.9 | 514.6 | 241 | 406 | 105.2 | 266 | 253 | 122.7 | 176.5 | 182.6 | 131.5
1063 | 824 | 473.3 | 189.32 | 221.3042 | 255.2 | 256.3 | 259.7 | 237.5 | 461.6 | 40.9 | 19.9 | 72.8 | 4.9 | 227.7 | 8.3 | 294.5 | 667.1 | 727.8 | 320 | 393.5 | 799.2 | 387.1 | 504.8 | 708.4 | 149 | 172.9 | 692.4 | 62.6 | 102.5 | 150.5 | 245.2 | 440.6 | 512.6 | 241.2 | 406.2 | 105.4 | 266.1 | 252.9 | 122.9 | 176.6 | 183 | 131.8
1064 | 825 | 473.5 | 189.4 | 221.3977 | 256 | 256.4 | 260.2 | 237.8 | 459.2 | 40.9 | 19.9 | 72.9 | 6.1 | 253.2 | 8.6 | 294.6 | 668.5 | 728.9 | 320.1 | 394.1 | 799.9 | 387.7 | 508.4 | 695.4 | 149.4 | 173.4 | 691.9 | 62.7 | 102.7 | 150.5 | 245.5 | 440.4 | 510.3 | 241.4 | 404.9 | 105.5 | 266.3 | 252.5 | 123.1 | 176.9 | 183.3 | 132
1065 | 826 | 473 | 189.2 | 221.1639 | 257.2 | 256.1 | 260.9 | 238.2 | 454.2 | 41 | 19.8 | 73.1 | 7.1 | 262.1 | 8.2 | 294.7 | 665.1 | 725.9 | 320.3 | 394.8 | 800.9 | 388.3 | 513.8 | 686.8 | 149.8 | 173.8 | 686.5 | 62.9 | 102.8 | 150.6 | 245.9 | 438.6 | 504.8 | 241.5 | 405.7 | 105.7 | 267.2 | 252.3 | 123.3 | 177.2 | 183.7 | 132.2
1066 | 827 | 473.2 | 189.28 | 221.2574 | 260.1 | 255.4 | 261.1 | 238.6 | 448 | 41 | 19.8 | 73.2 | 6.2 | 234.9 | 6.7 | 295 | 663.8 | 743.1 | 320.8 | 394.9 | 801.1 | 388.8 | 510 | 685.4 | 150.2 | 174.2 | 683.7 | 63 | 103 | 150.8 | 246.3 | 435.6 | 495.8 | 241.6 | 404.1 | 105.8 | 269 | 252.3 | 123.5 | 177.6 | 184 | 132.5
1067 | 828 | 472.9 | 189.16 | 221.1171 | 263.3 | 254.4 | 261 | 239.1 | 441.5 | 41 | 19.8 | 73.3 | 6.7 | 233.5 | 7 | 295.2 | 662.8 | 741.7 | 321.2 | 395.3 | 801.5 | 389.4 | 507.7 | 689.2 | 150.6 | 174.7 | 684.9 | 63.2 | 103.1 | 151.2 | 246.6 | 432.1 | 495.9 | 241.6 | 402.3 | 106 | 269.1 | 252.7 | 123.6 | 177.8 | 184.3 | 132.8
1068 | 829 | 474.4 | 189.76 | 221.8185 | 265.1 | 253.9 | 261.4 | 240.1 | 444.2 | 41 | 19.8 | 73.5 | 5.5 | 248.7 | 8 | 295.4 | 661.9 | 744.3 | 321.5 | 396 | 801.2 | 389.9 | 504.5 | 690.6 | 151 | 175.1 | 685.1 | 63.3 | 103.3 | 151.5 | 247 | 432.2 | 499 | 241.8 | 404.2 | 106.2 | 269.5 | 252.7 | 123.8 | 178 | 184.6 | 133.1
1069 | 830 | 473.7 | 189.48 | 221.4912 | 264.9 | 253.8 | 262.3 | 241.1 | 442.5 | 41 | 19.8 | 73.6 | 6.2 | 236.6 | 9 | 295.5 | 661.5 | 767.9 | 321.8 | 396.4 | 800.9 | 390.5 | 503.7 | 694.3 | 151.4 | 175.5 | 687 | 63.4 | 103.4 | 151.9 | 247.4 | 429.3 | 494.9 | 241.9 | 402.6 | 106.3 | 269.2 | 252.7 | 124 | 178.2 | 185 | 133.3
1070 | 831 | 473.7 | 189.48 | 221.4912 | 264.5 | 253.6 | 262.9 | 241.4 | 440.4 | 41.1 | 19.8 | 73.7 | 5.8 | 255.1 | 10.2 | 295.7 | 657.6 | 787.8 | 322.1 | 396.5 | 800.8 | 391.2 | 504 | 698.8 | 151.8 | 176 | 687.5 | 63.6 | 103.6 | 152.1 | 247.7 | 428.7 | 492.7 | 242 | 403.1 | 106.5 | 268.8 | 253.4 | 124.1 | 178.5 | 185.3 | 133.6
1071 | 832 | 473.6 | 189.44 | 221.4444 | 263.9 | 253.6 | 263.9 | 241 | 441.8 | 41.1 | 19.8 | 73.8 | 5.3 | 244.3 | 10.6 | 295.9 | 656.8 | 799.9 | 322.4 | 397.1 | 800.7 | 391.8 | 504.6 | 703.8 | 152.2 | 176.4 | 688.4 | 63.7 | 103.8 | 152.2 | 248.1 | 430.1 | 496.6 | 242.3 | 405.5 | 106.6 | 268.8 | 254 | 124.3 | 178.7 | 185.6 | 133.8
1072 | 833 | 473.9 | 189.56 | 221.5847 | 263.4 | 253.9 | 264.1 | 240.8 | 443.9 | 41 | 19.8 | 73.9 | 5.6 | 248.3 | 10.7 | 296.2 | 650.8 | 797.6 | 322.8 | 397.3 | 800.4 | 392.4 | 505.1 | 702.1 | 152.6 | 176.8 | 690 | 63.8 | 104 | 152.6 | 248.4 | 431.1 | 496.2 | 242.6 | 406.3 | 106.8 | 268.7 | 253.7 | 124.4 | 178.8 | 186 | 134
1073 | 834 | 474.1 | 189.64 | 221.6782 | 263.4 | 254.3 | 264.1 | 240.8 | 446.9 | 41 | 19.8 | 73.9 | 5.4 | 232.3 | 11.5 | 296.3 | 649.4 | 770.7 | 323.1 | 398.1 | 799.5 | 393 | 504.4 | 704.5 | 153 | 177.3 | 687.9 | 63.9 | 104.2 | 153.5 | 248.8 | 430.9 | 497 | 242.8 | 406.2 | 106.9 | 268.8 | 253.4 | 124.4 | 179 | 186.3 | 134.3
1074 | 835 | 473.5 | 189.4 | 221.3977 | 263.4 | 255 | 264.9 | 240.6 | 453.5 | 41 | 19.8 | 74 | 5.6 | 245.8 | 12.5 | 296.5 | 658.5 | 768.4 | 323.4 | 398.4 | 798 | 393.6 | 503.9 | 701.8 | 153.4 | 177.7 | 684.2 | 64.1 | 104.3 | 154.1 | 249.1 | 434.8 | 501.5 | 243.1 | 407.7 | 107.1 | 268.9 | 253.5 | 124.6 | 179.1 | 186.7 | 134.5
1075 | 836 | 473.3 | 189.32 | 221.3042 | 262.8 | 255.8 | 265.8 | 240.5 | 454.6 | 41 | 19.8 | 74 | 5.4 | 244.6 | 14.1 | 296.7 | 655.2 | 753 | 323.8 | 398.9 | 796.6 | 394.2 | 503.2 | 702.2 | 153.8 | 178.1 | 684.7 | 64.2 | 104.6 | 154.4 | 249.5 | 434.4 | 495.7 | 243.3 | 406.6 | 107.2 | 269.2 | 253.6 | 124.7 | 179.3 | 187.1 | 134.8
1076 | 837 | 473.5 | 189.4 | 221.3977 | 262.5 | 255.5 | 266.6 | 241 | 452.4 | 41.1 | 19.8 | 74.1 | 5.4 | 229.9 | 13.3 | 296.9 | 652.4 | 743.7 | 324.2 | 399.1 | 795 | 394.8 | 502.3 | 700.8 | 154.2 | 178.5 | 685.5 | 64.3 | 104.8 | 154.6 | 249.9 | 432.6 | 492.5 | 243.4 | 405 | 107.4 | 269.7 | 253.1 | 124.8 | 179.4 | 187.4 | 135
1077 | 838 | 473.7 | 189.48 | 221.4912 | 262.2 | 255.1 | 268.2 | 241.1 | 450.6 | 41.1 | 19.8 | 74.1 | 5.8 | 238.7 | 13.8 | 297.1 | 651.5 | 740.6 | 324.5 | 399.1 | 793.6 | 395.4 | 502.9 | 708.7 | 154.6 | 179 | 684.1 | 64.4 | 105 | 155 | 250.2 | 431.6 | 494.3 | 243.6 | 405.6 | 107.5 | 269.7 | 252.8 | 124.9 | 179.6 | 187.7 | 135.2
1078 | 839 | 473.9 | 189.56 | 221.5847 | 262.6 | 255.3 | 269.3 | 241.7 | 452.8 | 41.2 | 19.8 | 74.2 | 5.6 | 230 | 12.6 | 297.3 | 651.7 | 744 | 324.9 | 399.5 | 792.9 | 395.9 | 503.1 | 707.8 | 155 | 179.4 | 684.9 | 64.5 | 105.2 | 155.4 | 250.6 | 432.4 | 497.6 | 243.9 | 406.6 | 107.7 | 269.9 | 252.7 | 125.1 | 179.8 | 188 | 135.5
1079 | 840 | 472.7 | 189.08 | 221.0236 | 262.4 | 255.7 | 270.6 | 242.3 | 461.6 | 41.2 | 19.8 | 74.2 | 5.6 | 228.7 | 11.2 | 297.6 | 653.1 | 744.2 | 325.3 | 399.8 | 791.5 | 396.5 | 506.5 | 711.8 | 155.4 | 179.9 | 683.7 | 64.6 | 105.5 | 155.8 | 251 | 437.3 | 505.8 | 244.5 | 410 | 107.8 | 270.2 | 252.7 | 125.3 | 180 | 188.3 | 135.7
1080 | 841 | 473.3 | 189.32 | 221.3042 | 261.8 | 255.5 | 271.6 | 242.5 | 467.3 | 41.3 | 19.8 | 74.2 | 6.2 | 218.4 | 11.4 | 297.8 | 658.4 | 740.8 | 325.7 | 400.2 | 789.6 | 397.1 | 505.6 | 708.7 | 155.8 | 180.3 | 685.8 | 64.7 | 105.7 | 156.1 | 251.4 | 438.7 | 504 | 244.9 | 409.4 | 107.9 | 270.6 | 253.1 | 125.5 | 180.3 | 188.6 | 136
1081 | 842 | 473.9 | 189.56 | 221.5847 | 261.2 | 255.4 | 272.8 | 242.8 | 465.9 | 41.3 | 19.8 | 74.2 | 6.9 | 220.5 | 13.2 | 298 | 657.4 | 764 | 326.1 | 400.6 | 788.2 | 397.7 | 504.4 | 713 | 156.2 | 180.7 | 682.6 | 64.9 | 105.9 | 156.3 | 251.7 | 438 | 507.3 | 245.2 | 408.7 | 108 | 270.5 | 254 | 125.7 | 180.5 | 189 | 136.3
1082 | 843 | 473.8 | 189.52 | 221.538 | 260.2 | 257.2 | 273.7 | 242.9 | 464.5 | 41.4 | 19.8 | 74.2 | 7.6 | 271.6 | 12.9 | 298.1 | 654 | 780.4 | 326.5 | 400.8 | 787.9 | 398.3 | 503.1 | 712 | 156.6 | 181.2 | 683.5 | 65 | 106.2 | 156.5 | 252 | 437.6 | 507 | 245.4 | 408.6 | 108.2 | 270.5 | 253.9 | 125.9 | 180.8 | 189.3 | 136.5
1083 | 844 | 473.6 | 189.44 | 221.4444 | 259 | 258.4 | 273.7 | 243 | 459.2 | 41.4 | 19.8 | 74.3 | 7.5 | 246.2 | 10.8 | 298.3 | 653.8 | 792.9 | 327.1 | 401.2 | 788.7 | 399 | 502.3 | 711.4 | 157 | 181.6 | 684.5 | 65.1 | 106.5 | 156.8 | 252.4 | 435.2 | 501.8 | 245.7 | 408.3 | 108.3 | 270.7 | 253.9 | 126.1 | 181 | 189.7 | 136.8
1084 | 845 | 473.3 | 189.32 | 221.3042 | 259 | 259.5 | 273.5 | 243 | 459.2 | 41.4 | 19.8 | 74.2 | 5.6 | 246.7 | 11.3 | 298.5 | 648.9 | 788.9 | 327.6 | 401.6 | 789.5 | 399.6 | 501.9 | 716.6 | 157.4 | 182.1 | 682.1 | 65.2 | 106.8 | 157.4 | 252.7 | 435.5 | 505.6 | 246.1 | 409.2 | 108.4 | 271.2 | 254.1 | 126.3 | 181.2 | 190 | 137
1085 | 846 | 473 | 189.2 | 221.1639 | 258.9 | 260.8 | 273.8 | 243 | 462.3 | 41.4 | 19.8 | 74.2 | 4.5 | 221.8 | 10.4 | 298.7 | 644.5 | 777.2 | 328.2 | 401.8 | 789.5 | 400.2 | 501.5 | 716.8 | 157.8 | 182.5 | 682.3 | 65.3 | 106.9 | 157.7 | 253.1 | 436.7 | 509.5 | 246.4 | 410.4 | 108.6 | 270.9 | 254.8 | 126.6 | 181.6 | 190.4 | 137.3
1086 | 847 | 473.3 | 189.32 | 221.3042 | 259.3 | 261 | 273.7 | 243 | 461.1 | 41.5 | 19.8 | 74.2 | 5 | 253.4 | 9.3 | 298.9 | 641.3 | 765.8 | 328.9 | 401.8 | 789.9 | 400.8 | 500.6 | 713.3 | 158.2 | 183 | 683.9 | 65.4 | 107.1 | 157.8 | 253.5 | 436.3 | 506.6 | 246.7 | 410.6 | 108.7 | 270.6 | 254.8 | 126.7 | 181.7 | 190.7 | 137.6
1087 | 848 | 473.8 | 189.52 | 221.538 | 259.2 | 260.7 | 273.4 | 242.6 | 456 | 41.5 | 19.8 | 74.3 | 5.9 | 222.9 | 10 | 299.1 | 636.2 | 751.1 | 329.4 | 402.1 | 792.3 | 401.5 | 498.9 | 701.4 | 158.6 | 183.5 | 680.9 | 65.5 | 107.4 | 157.8 | 253.9 | 434.9 | 498.6 | 246.8 | 409.3 | 108.8 | 270.4 | 254.7 | 127.1 | 181.8 | 191 | 137.8
1088 | 849 | 473 | 189.2 | 221.1639 | 258.9 | 260.5 | 272.8 | 242.4 | 449.8 | 41.6 | 19.8 | 74.3 | 6.9 | 216.9 | 10.2 | 299.2 | 641 | 732.7 | 329.9 | 402.1 | 794.2 | 402.1 | 496 | 697.4 | 159 | 183.9 | 681.2 | 65.6 | 107.6 | 157.9 | 254.3 | 433.1 | 491.8 | 246.8 | 408.2 | 109 | 270.5 | 254.8 | 127.3 | 182.1 | 191.4 | 138
1089 | 850 | 473.7 | 189.48 | 221.4912 | 260.3 | 261.2 | 271.5 | 242.3 | 443.8 | 41.6 | 19.8 | 74.4 | 7.2 | 237.7 | 8.2 | 299.4 | 658.9 | 725.5 | 330.5 | 402.1 | 794.4 | 402.7 | 493.2 | 684.1 | 159.4 | 184.4 | 679.5 | 65.8 | 107.8 | 158.1 | 254.7 | 430.8 | 484.6 | 246.8 | 407.1 | 109.1 | 271.3 | 255 | 127.4 | 182.5 | 191.7 | 138.3
1090 | 851 | 472.8 | 189.12 | 221.0704 | 262.3 | 261.4 | 270.2 | 242.6 | 440.2 | 41.7 | 19.8 | 74.3 | 6.6 | 228.5 | 7.5 | 299.7 | 653.1 | 728.2 | 331.2 | 402.4 | 793.7 | 403.4 | 493.4 | 676.2 | 159.8 | 184.9 | 677.7 | 65.9 | 108 | 158.3 | 255.1 | 431.1 | 477.9 | 246.8 | 407 | 109.2 | 271.9 | 255.6 | 127.7 | 182.9 | 192 | 138.5
1091 | 852 | 473 | 189.2 | 221.1639 | 263.8 | 262.9 | 269.1 | 243.7 | 436.5 | 41.7 | 19.8 | 74.3 | 6.1 | 247 | 7.5 | 299.9 | 651.7 | 747.5 | 331.8 | 402.9 | 793.1 | 404 | 493.1 | 669.2 | 160.3 | 185.3 | 675.3 | 66 | 108.2 | 158.4 | 255.5 | 429.8 | 472.1 | 246.9 | 406.6 | 109.4 | 272.4 | 256.4 | 128 | 183.4 | 192.4 | 138.8
1092 | 853 | 473.3 | 189.32 | 221.3042 | 264.5 | 262.9 | 268.1 | 244.7 | 432.6 | 41.8 | 19.8 | 74.3 | 5.1 | 218.8 | 8.1 | 300.1 | 649.7 | 769.2 | 332.4 | 403.3 | 793 | 404.6 | 493.5 | 671.9 | 160.7 | 185.8 | 673.6 | 66.1 | 108.4 | 158.4 | 256 | 428.2 | 466.7 | 247.1 | 406.1 | 109.6 | 273.3 | 257 | 128.4 | 183.7 | 192.8 | 139.1
1093 | 854 | 473.6 | 189.44 | 221.4444 | 263.8 | 262.4 | 266.7 | 245.6 | 430.7 | 41.8 | 19.8 | 74.4 | 4.8 | 214.5 | 8.4 | 300.4 | 651.2 | 779.8 | 333 | 403.7 | 792.4 | 405.2 | 493.3 | 676.3 | 161.1 | 186.3 | 673 | 66.2 | 108.6 | 158.6 | 256.4 | 428.1 | 465.2 | 247.2 | 406.6 | 109.7 | 274.1 | 257.7 | 128.7 | 184 | 193.1 | 139.3
1094 | 855 | 473.6 | 189.44 | 221.4444 | 263.3 | 262.8 | 265.6 | 246.2 | 434 | 41.9 | 19.8 | 74.5 | 6 | 212.9 | 8.3 | 300.6 | 643.3 | 775.8 | 333.6 | 404 | 792.6 | 405.8 | 493.2 | 665.8 | 161.5 | 186.7 | 672.9 | 66.4 | 108.8 | 158.7 | 256.7 | 431.4 | 464.2 | 247.3 | 408.3 | 109.9 | 274.7 | 258 | 129.1 | 184.3 | 193.5 | 139.6
1095 | 856 | 473.1 | 189.24 | 221.2107 | 265.1 | 264.8 | 265.1 | 246.8 | 434.2 | 41.9 | 19.8 | 74.6 | 6.7 | 205.9 | 9.8 | 300.8 | 644.5 | 788 | 334.2 | 404.4 | 793.6 | 406.4 | 491.4 | 659.9 | 161.9 | 187.2 | 669.4 | 66.5 | 109 | 158.9 | 257.1 | 430.8 | 461.8 | 247.3 | 407.8 | 110.1 | 275.2 | 258.4 | 129.4 | 184.6 | 193.8 | 139.9
1096 | 857 | 473 | 189.2 | 221.1639 | 267.5 | 267.2 | 264.7 | 246.8 | 432 | 41.9 | 19.8 | 74.5 | 6.1 | 226.5 | 10.6 | 301 | 651.5 | 806.7 | 334.9 | 404.8 | 794.4 | 407 | 491 | 661.2 | 162.3 | 187.7 | 669.9 | 66.6 | 109.2 | 159.2 | 257.4 | 429.7 | 463.2 | 247.4 | 408.1 | 110.3 | 275.4 | 258.9 | 129.6 | 185.1 | 194.2 | 140.2
1097 | 858 | 472 | 188.8 | 220.6963 | 268.8 | 270.5 | 264.6 | 246.8 | 430.3 | 42 | 19.8 | 74.5 | 6.4 | 239.4 | 9.9 | 301.3 | 648.6 | 811.4 | 335.5 | 405.1 | 795.9 | 407.6 | 491.6 | 659 | 162.7 | 188.1 | 668.6 | 66.7 | 109.4 | 159.3 | 257.8 | 428.5 | 465.1 | 247.5 | 408.6 | 110.5 | 275.1 | 259.4 | 129.7 | 185.4 | 194.6 | 140.4
1098 | 859 | 472.8 | 189.12 | 221.0704 | 269.2 | 273.5 | 264.5 | 246.9 | 430.1 | 42 | 19.8 | 74.6 | 7 | 251.9 | 11.3 | 301.5 | 644.3 | 811.1 | 336.1 | 405.6 | 796.5 | 408.3 | 491.4 | 657.3 | 163.1 | 188.6 | 668.1 | 66.8 | 109.7 | 159.6 | 258.2 | 427.7 | 464.4 | 247.6 | 409 | 110.7 | 274.9 | 259.6 | 129.9 | 185.7 | 195 | 140.7
1099 | 860 | 473.7 | 189.48 | 221.4912 | 269.5 | 276.7 | 263.8 | 246.4 | 428.4 | 42 | 19.8 | 74.7 | 7.3 | 246.2 | 11.1 | 301.7 | 636.2 | 798.1 | 336.8 | 405.7 | 796.4 | 408.9 | 491 | 654.8 | 163.5 | 189 | 669.9 | 66.9 | 109.9 | 159.7 | 258.6 | 427.9 | 460.3 | 247.7 | 410.2 | 110.9 | 274.6 | 260.1 | 130.2 | 186.2 | 195.4 | 140.9
1100 | 861 | 473.5 | 189.4 | 221.3977 | 268.7 | 279 | 262.7 | 245.9 | 424.6 | 42.1 | 19.8 | 74.8 | 6.8 | 258.1 | 10.8 | 302 | 641.6 | 795.5 | 337.4 | 405.6 | 796.1 | 409.5 | 489.9 | 654.2 | 163.9 | 189.5 | 669.2 | 67 | 110.1 | 159.8 | 258.9 | 426.2 | 456.2 | 247.8 | 408.7 | 111.1 | 274.7 | 260.2 | 130.5 | 186.6 | 195.8 | 141.2
1101 | 862 | 472.5 | 189 | 220.9301 | 267.4 | 277.7 | 261.9 | 246.2 | 422.4 | 42.1 | 19.8 | 74.8 | 7.2 | 249 | 11 | 302.2 | 648.5 | 793.6 | 338 | 405.9 | 795.8 | 410 | 489.3 | 660 | 164.3 | 190 | 669.4 | 67.1 | 110.3 | 159.9 | 259.3 | 425.1 | 454.3 | 248.1 | 407.8 | 111.3 | 274.8 | 260 | 130.7 | 186.9 | 196.1 | 141.4
1102 | 863 | 473.3 | 189.32 | 221.3042 | 266.8 | 275.5 | 261.4 | 247 | 422.6 | 42.1 | 19.8 | 74.9 | 7.1 | 243.5 | 11.2 | 302.4 | 663.7 | 799.4 | 338.6 | 406.5 | 796.3 | 410.6 | 488.7 | 659 | 164.8 | 190.4 | 668 | 67.2 | 110.5 | 160 | 259.7 | 424.9 | 454.3 | 248.3 | 407.7 | 111.5 | 274.9 | 259.9 | 131 | 187.3 | 196.4 | 141.7
1103 | 864 | 473 | 189.2 | 221.1639 | 266.4 | 275.2 | 260.8 | 247.3 | 423.7 | 42.1 | 19.7 | 74.9 | 7.9 | 250.4 | 12.5 | 302.7 | 666.7 | 795.7 | 339.1 | 406.9 | 796.9 | 411.2 | 489 | 658.3 | 165.2 | 190.9 | 668 | 67.3 | 110.7 | 160.2 | 260 | 425.1 | 453.8 | 248.7 | 408.7 | 111.7 | 275.4 | 260.1 | 131.2 | 187.6 | 196.8 | 142
1104 | 865 | 473.1 | 189.24 | 221.2107 | 266 | 274.8 | 260.2 | 247.5 | 423 | 42.2 | 19.7 | 74.9 | 7.5 | 244.9 | 15 | 302.9 | 662.1 | 803.4 | 339.6 | 407.1 | 797 | 411.8 | 491.1 | 659.9 | 165.6 | 191.3 | 668 | 67.4 | 111 | 160.4 | 260.4 | 425.3 | 455.1 | 249.1 | 409 | 111.9 | 275.9 | 260.4 | 131.5 | 187.9 | 197.1 | 142.2
1105 | 866 | 473.4 | 189.36 | 221.3509 | 265.3 | 273 | 259.6 | 247.8 | 423 | 42.2 | 19.8 | 75 | 6.8 | 247.5 | 16.3 | 303.1 | 656.8 | 813.9 | 340.2 | 407.4 | 797.1 | 412.5 | 492.8 | 660.5 | 166 | 191.7 | 666.3 | 67.5 | 111.2 | 160.5 | 260.8 | 424.9 | 453 | 249.4 | 408.8 | 112.1 | 276.3 | 260.4 | 131.7 | 188.1 | 197.5 | 142.5
1106 | 867 | 472.7 | 189.08 | 221.0236 | 265.5 | 271.4 | 259.5 | 247.8 | 427.1 | 42.3 | 19.8 | 75.2 | 7 | 251 | 16.2 | 303.4 | 654.3 | 817.8 | 340.8 | 407.8 | 797.3 | 413.1 | 495.2 | 666.8 | 166.4 | 192.2 | 665.7 | 67.6 | 111.4 | 160.7 | 261.1 | 426.6 | 457.9 | 249.8 | 410.3 | 112.3 | 276.2 | 260.5 | 132 | 188.4 | 197.8 | 142.7
1107 | 868 | 472.5 | 189 | 220.9301 | 265.9 | 272.1 | 259.1 | 248 | 430 | 42.4 | 19.7 | 75.3 | 5.8 | 243.6 | 12.7 | 303.6 | 652.9 | 819.8 | 341.5 | 408.2 | 797.3 | 413.7 | 495.5 | 668.5 | 166.9 | 192.6 | 667.7 | 67.7 | 111.6 | 160.9 | 261.5 | 427.7 | 458.8 | 250.2 | 411.3 | 112.5 | 276.1 | 260.7 | 132.2 | 188.6 | 198.2 | 143
1108 | 869 | 473.9 | 189.56 | 221.5847 | 267.1 | 273.6 | 258.5 | 247.7 | 429.9 | 42.4 | 19.7 | 75.5 | 5.6 | 261.8 | 12.4 | 303.9 | 653.9 | 823.7 | 342.2 | 408.3 | 797.6 | 414.4 | 496.1 | 672.5 | 167.3 | 193.1 | 666.3 | 67.8 | 111.9 | 161.1 | 261.8 | 428.8 | 461.9 | 250.7 | 412.2 | 112.7 | 276 | 260.7 | 132.3 | 188.9 | 198.7 | 143.2
1109 | 870 | 474.3 | 189.72 | 221.7717 | 268.5 | 275.6 | 258 | 247.4 | 434.1 | 42.4 | 19.7 | 75.6 | 5.1 | 239.1 | 12.2 | 304.1 | 653.3 | 841 | 342.9 | 408.7 | 798.4 | 415 | 497 | 681.4 | 167.7 | 193.5 | 667.7 | 67.9 | 112.2 | 161.4 | 262.2 | 431.1 | 470 | 251.2 | 414.2 | 112.9 | 275.7 | 260.8 | 132.5 | 189.1 | 199.1 | 143.5
1110 | 871 | 474.4 | 189.76 | 221.8185 | 268.7 | 277.1 | 258 | 246.6 | 434.8 | 42.4 | 19.7 | 75.7 | 7.3 | 223.7 | 10.7 | 304.4 | 649.9 | 837.9 | 343.6 | 408.8 | 799.5 | 415.6 | 497.3 | 689.1 | 168.1 | 193.9 | 669.6 | 68 | 112.4 | 161.6 | 262.5 | 430.8 | 468.8 | 251.6 | 414.6 | 113.1 | 275.1 | 261 | 132.7 | 189.5 | 199.5 | 143.7
1111 | 872 | 473.1 | 189.24 | 221.2107 | 268.8 | 279 | 257.9 | 246.3 | 430.9 | 42.4 | 19.7 | 75.8 | 6.8 | 193.8 | 10 | 304.7 | 649.8 | 835.6 | 344.2 | 409.4 | 799.5 | 416.3 | 497.6 | 684.8 | 168.5 | 194.4 | 668.9 | 68.1 | 112.6 | 161.7 | 262.9 | 428.6 | 464.6 | 251.9 | 413.8 | 113.3 | 274.7 | 261.1 | 132.8 | 189.8 | 199.9 | 143.9
1112 | 873 | 473.2 | 189.28 | 221.2574 | 268.6 | 278.1 | 257.7 | 246.6 | 428.2 | 42.4 | 19.7 | 75.9 | 6.8 | 200.3 | 7.1 | 304.9 | 646.8 | 840.9 | 344.6 | 409.5 | 800 | 417 | 498.4 | 686.2 | 168.9 | 194.8 | 668.6 | 68.2 | 112.7 | 161.8 | 263.2 | 427.7 | 464.2 | 252.3 | 414.2 | 113.5 | 274.6 | 261.6 | 133 | 190 | 200.3 | 144.2
1113 | 874 | 473.5 | 189.4 | 221.3977 | 268.1 | 277.3 | 257.1 | 247 | 428.4 | 42.4 | 19.7 | 75.9 | 7.5 | 251.3 | 6.8 | 305.1 | 645.1 | 841.7 | 345.2 | 409.7 | 801.8 | 417.6 | 499.6 | 686.3 | 169.4 | 195.2 | 668 | 68.3 | 112.9 | 162.1 | 263.6 | 427.4 | 467.7 | 252.9 | 415.5 | 113.7 | 274.5 | 261.9 | 133.2 | 190.1 | 200.7 | 144.4
1114 | 875 | 473.8 | 189.52 | 221.538 | 267.4 | 277.1 | 257.1 | 247 | 436.9 | 42.4 | 19.7 | 76 | 7.2 | 256.9 | 8.5 | 305.4 | 644.3 | 831.2 | 345.6 | 409.9 | 803 | 418.2 | 501.2 | 690.9 | 169.8 | 195.6 | 667.8 | 68.4 | 113.1 | 162.6 | 263.9 | 430.8 | 478.9 | 253.8 | 418.3 | 113.9 | 274.4 | 261.4 | 133.3 | 190.3 | 201.1 | 144.6
1115 | 876 | 474.2 | 189.68 | 221.725 | 266.3 | 276.6 | 257.2 | 246.5 | 443 | 42.5 | 19.7 | 76.1 | 6.7 | 242.7 | 13 | 305.6 | 645.7 | 821.2 | 346 | 409.9 | 802.9 | 418.9 | 502.8 | 696.2 | 170.2 | 196 | 667.9 | 68.5 | 113.3 | 163 | 264.2 | 432 | 484.6 | 254.2 | 418.5 | 114 | 274.1 | 261.2 | 133.4 | 190.3 | 201.5 | 144.9
1116 | 877 | 473.2 | 189.28 | 221.2574 | 264.7 | 274.7 | 257.3 | 245.6 | 446.9 | 42.5 | 19.7 | 76.2 | 5.2 | 254.2 | 13.1 | 305.8 | 642.7 | 812 | 346.3 | 410 | 803 | 419.5 | 503.8 | 695.8 | 170.6 | 196.4 | 669.3 | 68.7 | 113.5 | 163.2 | 264.6 | 434 | 488.5 | 254.7 | 419.4 | 114.2 | 273.8 | 261.5 | 133.5 | 190.5 | 202 | 145.1
1117 | 878 | 473.8 | 189.52 | 221.538 | 263.6 | 272.7 | 257.9 | 244.8 | 446.5 | 42.5 | 19.7 | 76.2 | 4.7 | 244.9 | 14.5 | 306.1 | 639.7 | 802.4 | 346.6 | 410.1 | 803.5 | 420.2 | 504.4 | 694.1 | 171 | 196.9 | 668.8 | 68.8 | 113.8 | 163.5 | 264.9 | 433 | 486.6 | 255 | 417.7 | 114.4 | 273.5 | 261.3 | 133.7 | 190.7 | 202.3 | 145.3
1118 | 879 | 474.1 | 189.64 | 221.6782 | 263 | 270.8 | 258.8 | 244.7 | 447.9 | 42.6 | 19.7 | 76.3 | 4.6 | 225.4 | 13.8 | 306.3 | 647.7 | 808.3 | 346.9 | 410.6 | 803.7 | 420.8 | 504.5 | 696.9 | 171.4 | 197.3 | 669.7 | 68.9 | 114.1 | 163.8 | 265.2 | 432.5 | 485.9 | 255.3 | 417.2 | 114.5 | 274 | 260.9 | 133.8 | 190.9 | 202.7 | 145.5
1119 | 880 | 474.1 | 189.64 | 221.6782 | 262.7 | 269.7 | 259.8 | 244.5 | 450.5 | 42.6 | 19.7 | 76.3 | 4.6 | 209.1 | 13.3 | 306.6 | 653.3 | 814.6 | 347.5 | 410.8 | 804.2 | 421.5 | 505.7 | 707.4 | 171.8 | 197.7 | 672.6 | 69 | 114.2 | 164 | 265.6 | 434.1 | 494.9 | 255.7 | 418.1 | 114.6 | 274.3 | 261.3 | 133.9 | 191.1 | 203 | 145.8
1120 | 881 | 473.5 | 189.4 | 221.3977 | 262.1 | 268.3 | 260.7 | 244.4 | 461.7 | 42.6 | 19.7 | 76.4 | 4.6 | 218 | 11.5 | 306.8 | 657.7 | 811.8 | 348 | 410.5 | 804.2 | 422.1 | 506.6 | 713.2 | 172.2 | 198.1 | 674.9 | 69.1 | 114.4 | 164.4 | 265.9 | 437.2 | 501.5 | 256.3 | 420.2 | 114.8 | 274.5 | 261.7 | 134.1 | 191.3 | 203.3 | 146.1
1121 | 882 | 473 | 189.2 | 221.1639 | 261.6 | 267 | 261.1 | 244.6 | 463.8 | 42.6 | 19.7 | 76.5 | 4.1 | 228.9 | 9.3 | 307.1 | 660.6 | 822.7 | 348.6 | 410.9 | 803.8 | 422.8 | 507.6 | 708.7 | 172.6 | 198.5 | 674 | 69.2 | 114.6 | 164.6 | 266.2 | 438.3 | 501.3 | 256.9 | 420.7 | 114.9 | 274.8 | 262.2 | 134.2 | 191.5 | 203.7 | 146.3
1122 | 883 | 473.6 | 189.44 | 221.4444 | 261.2 | 266.2 | 261.7 | 244.8 | 463.6 | 42.6 | 19.7 | 76.5 | 3.9 | 222.4 | 8.3 | 307.4 | 658.2 | 833.1 | 349.1 | 410.8 | 803.3 | 423.5 | 509.2 | 712.3 | 173 | 198.9 | 671.6 | 69.3 | 114.8 | 165 | 266.6 | 440.1 | 506.5 | 257.4 | 421.1 | 115.1 | 274.9 | 262.7 | 134.4 | 191.8 | 204 | 146.5
1123 | 884 | 473.6 | 189.44 | 221.4444 | 260.9 | 266.2 | 262.3 | 245 | 466.7 | 42.7 | 19.7 | 76.6 | 4.6 | 240.3 | 7.5 | 307.7 | 657.9 | 837.5 | 349.9 | 411.3 | 802.6 | 424.2 | 510.3 | 716.5 | 173.4 | 199.3 | 672.9 | 69.4 | 114.9 | 165.2 | 266.9 | 443.3 | 511.3 | 257.8 | 422.6 | 115.2 | 275 | 263 | 134.5 | 192.1 | 204.4 | 146.8
1124 | 885 | 472.6 | 189.04 | 220.9769 | 260.4 | 266.1 | 262.2 | 244.9 | 463.3 | 42.7 | 19.7 | 76.8 | 5.6 | 197.6 | 7.8 | 308 | 660.1 | 833.8 | 350.4 | 411.7 | 802.8 | 424.9 | 510.4 | 713.5 | 173.8 | 199.7 | 672.6 | 69.6 | 115.1 | 165.2 | 267.3 | 443.2 | 506.8 | 258.2 | 422.9 | 115.3 | 275.3 | 263 | 134.7 | 192.5 | 204.8 | 147
1125 | 886 | 471.7 | 188.68 | 220.556 | 259.9 | 266 | 262.3 | 245.2 | 459.6 | 42.7 | 19.7 | 77 | 5.9 | 218.1 | 8.9 | 308.3 | 658.7 | 843.3 | 350.8 | 412.1 | 802.9 | 425.7 | 511.5 | 707.6 | 174.2 | 200.1 | 673.1 | 69.7 | 115.4 | 165.4 | 267.6 | 443.3 | 503 | 258.5 | 423.9 | 115.5 | 275.7 | 262.9 | 134.9 | 192.7 | 205.2 | 147.3
1126 | 887 | 473.2 | 189.28 | 221.2574 | 260.4 | 266.3 | 262.3 | 245.6 | 455.2 | 42.7 | 19.7 | 77 | 5.6 | 232.6 | 8.4 | 308.5 | 661.8 | 839.1 | 351.4 | 412.3 | 802.8 | 426.4 | 513.5 | 710.3 | 174.6 | 200.5 | 671.3 | 69.8 | 115.6 | 165.5 | 267.9 | 442.1 | 499.3 | 258.8 | 423.3 | 115.6 | 277.2 | 262.9 | 135.2 | 193 | 205.6 | 147.5
1127 | 888 | 473 | 189.2 | 221.1639 | 261.7 | 268 | 262.4 | 246 | 453.5 | 42.7 | 19.7 | 77.1 | 5.1 | 239 | 9 | 308.8 | 659.8 | 847.6 | 351.9 | 412.5 | 803.6 | 427.1 | 514.8 | 707.6 | 175 | 201 | 671.2 | 69.9 | 115.8 | 165.7 | 268.3 | 442.4 | 497.6 | 259.2 | 424.5 | 115.7 | 277.7 | 263.3 | 135.4 | 193.3 | 206 | 147.8
1128 | 889 | 471.9 | 188.76 | 220.6496 | 262.9 | 270 | 261.9 | 246.4 | 452.3 | 42.7 | 19.7 | 77.1 | 5.6 | 217.3 | 10.8 | 309.1 | 655.9 | 853 | 352.3 | 412.5 | 804.4 | 427.9 | 516.4 | 710.1 | 175.4 | 201.4 | 671.3 | 70 | 116 | 165.9 | 268.6 | 442.5 | 498.3 | 259.6 | 425.2 | 115.9 | 277.7 | 263.2 | 135.6 | 193.7 | 206.4 | 148.1
1129 | 890 | 474.2 | 189.68 | 221.725 | 263 | 270.3 | 261.6 | 246.6 | 457.7 | 42.7 | 19.7 | 77.2 | 6.3 | 246 | 11 | 309.3 | 655.1 | 855.7 | 352.8 | 412.6 | 804.9 | 428.6 | 517.2 | 719.3 | 175.8 | 201.8 | 671 | 70.1 | 116.2 | 166.4 | 269 | 445.9 | 507.8 | 260.1 | 427.6 | 116 | 277.8 | 263.2 | 135.8 | 193.9 | 206.9 | 148.3
1130 | 891 | 475.8 | 190.32 | 222.4731 | 262.6 | 271 | 261.8 | 246.7 | 461.1 | 42.7 | 19.7 | 77.2 | 5.5 | 224.8 | 10.6 | 309.6 | 652.1 | 851.4 | 353.4 | 412.4 | 804.4 | 429.4 | 518.7 | 723.7 | 176.1 | 202.2 | 672.9 | 70.2 | 116.4 | 166.6 | 269.3 | 446 | 509.7 | 260.6 | 429.3 | 116.2 | 277.7 | 262.8 | 136 | 194.1 | 207.3 | 148.6
1131 | 892 | 473.9 | 189.56 | 221.5847 | 261.9 | 271.2 | 262.3 | 246.7 | 468.7 | 42.8 | 19.7 | 77.4 | 5.4 | 244.8 | 11.1 | 309.9 | 648.8 | 826.6 | 353.9 | 412.3 | 804.3 | 430.1 | 522.6 | 729.1 | 176.5 | 202.6 | 671.9 | 70.3 | 116.6 | 167.2 | 269.7 | 449.3 | 519.5 | 261.3 | 432.6 | 116.4 | 277.5 | 262.5 | 136.2 | 194.4 | 207.8 | 148.8
1132 | 893 | 472.9 | 189.16 | 221.1171 | 261.5 | 271.1 | 262.8 | 247.3 | 475.2 | 42.8 | 19.7 | 77.4 | 7.7 | 234.6 | 9.3 | 310.2 | 653.7 | 795.3 | 354.3 | 412.5 | 804.6 | 430.8 | 524.5 | 727.6 | 176.9 | 203 | 675.6 | 70.4 | 116.9 | 167.5 | 270 | 450.7 | 522.4 | 261.7 | 432.7 | 116.5 | 277.8 | 262.5 | 136.4 | 194.5 | 208.2 | 149
1133 | 894 | 473.4 | 189.36 | 221.3509 | 261.8 | 270.2 | 263.2 | 247.5 | 472.8 | 42.9 | 19.7 | 77.6 | 8.1 | 220.5 | 7.7 | 310.5 | 656.4 | 775.6 | 354.7 | 412.8 | 803.5 | 431.5 | 526.4 | 722.5 | 177.3 | 203.4 | 674.5 | 70.5 | 117.1 | 167.8 | 270.4 | 449.9 | 518.9 | 262 | 431.4 | 116.7 | 278.3 | 262.9 | 136.5 | 194.6 | 208.7 | 149.3
1134 | 895 | 474.2 | 189.68 | 221.725 | 262.3 | 270 | 264.3 | 247.3 | 471.6 | 42.9 | 19.7 | 77.7 | 8.1 | 213.5 | 8.4 | 310.8 | 667.4 | 773.5 | 355.1 | 413.1 | 803.1 | 432.1 | 530.2 | 714.6 | 177.7 | 203.8 | 675.9 | 70.6 | 117.3 | 168 | 270.7 | 451.7 | 521.6 | 262.3 | 434 | 116.8 | 278.7 | 263.1 | 136.7 | 194.9 | 209 | 149.5
1135 | 896 | 474.4 | 189.76 | 221.8185 | 262.7 | 270.1 | 265.2 | 247.9 | 471.8 | 42.9 | 19.7 | 77.7 | 6.7 | 224.6 | 14.4 | 311.1 | 672 | 782.5 | 355.5 | 413.3 | 803.5 | 432.8 | 534.6 | 711.3 | 178 | 204.2 | 673.7 | 70.7 | 117.5 | 168.2 | 271.1 | 453.4 | 525.6 | 262.7 | 435.7 | 116.9 | 278.7 | 263.4 | 136.8 | 195.1 | 209.4 | 149.8
1136 | 897 | 472.7 | 189.08 | 221.0236 | 263.6 | 269.6 | 266.1 | 248.3 | 477.3 | 43 | 19.7 | 77.7 | 8.2 | 210 | 16.4 | 311.4 | 674.9 | 778.7 | 355.8 | 413.3 | 803.3 | 433.5 | 538.7 | 713.3 | 178.4 | 204.6 | 677.1 | 70.8 | 117.7 | 168.8 | 271.4 | 456.9 | 536.6 | 263.2 | 438.5 | 117.1 | 278.8 | 263.9 | 137 | 195.3 | 209.7 | 150
1137 | 898 | 474.5 | 189.8 | 221.8653 | 264.9 | 268.9 | 266.5 | 248.7 | 482.3 | 43 | 19.7 | 77.9 | 8.2 | 235.8 | 19.7 | 311.7 | 676.1 | 784.9 | 356.1 | 413.4 | 802.6 | 434.1 | 540.7 | 702.7 | 178.8 | 205.1 | 676.7 | 70.9 | 118 | 169.2 | 271.7 | 456.9 | 538.3 | 263.6 | 436.5 | 117.2 | 279.3 | 263.8 | 137.2 | 195.6 | 210.1 | 150.3
1138 | 899 | 473.4 | 189.36 | 221.3509 | 265.6 | 268.8 | 267.7 | 249 | 486.4 | 43.1 | 19.7 | 78 | 7.6 | 214.1 | 17.1 | 312 | 670 | 783.4 | 356.5 | 413.5 | 801.8 | 434.9 | 541.4 | 696.6 | 179.1 | 205.5 | 674.9 | 71 | 118.2 | 169.8 | 272.1 | 457.4 | 540.3 | 264.1 | 435.3 | 117.3 | 279.8 | 264.3 | 137.4 | 195.9 | 210.5 | 150.6
1139 | 900 | 474 | 189.6 | 221.6315 | 265.7 | 268.8 | 269 | 249.4 | 487.5 | 43.1 | 19.6 | 77.9 | 6.9 | 227.8 | 13.4 | 312.5 | 668.3 | 771.6 | 356.7 | 413.9 | 800.8 | 435.6 | 542.3 | 695.7 | 179.5 | 205.9 | 674.2 | 71.1 | 118.4 | 169.9 | 272.4 | 457.3 | 539.7 | 264.3 | 434.9 | 117.4 | 280.5 | 264.8 | 137.6 | 196.2 | 210.8 | 150.9
1140 | 901 | 473.8 | 189.52 | 221.538 | 266.2 | 268.6 | 270.4 | 249.8 | 487.5 | 43.1 | 19.6 | 77.9 | 6.1 | 232 | 12 | 312.8 | 672.3 | 769.1 | 356.8 | 414 | 799.8 | 436.2 | 543.6 | 695 | 179.9 | 206.3 | 674.7 | 71.2 | 118.6 | 170.3 | 272.7 | 457.8 | 535.6 | 264.5 | 434 | 117.6 | 280.8 | 265.2 | 137.7 | 196.4 | 211.2 | 151.1
1141 | 902 | 473.3 | 189.32 | 221.3042 | 266.9 | 268.5 | 271.5 | 250.2 | 485.1 | 43.2 | 19.7 | 77.9 | 5.5 | 215.8 | 16.9 | 313.1 | 672.8 | 779.8 | 357 | 414.2 | 798.2 | 436.9 | 543.3 | 696 | 180.2 | 206.7 | 675.1 | 71.3 | 118.8 | 170.5 | 273.1 | 455.7 | 528.3 | 264.7 | 432.8 | 117.7 | 280.9 | 265.4 | 137.9 | 196.7 | 211.5 | 151.4
1142 | 903 | 473 | 189.2 | 221.1639 | 267.5 | 268.4 | 272.7 | 250.7 | 481.6 | 43.2 | 19.6 | 77.9 | 6.2 | 225.9 | 16.2 | 313.4 | 667.5 | 767.3 | 357.2 | 414.3 | 797.7 | 437.6 | 545.5 | 695.1 | 180.6 | 207.1 | 674.7 | 71.4 | 119 | 171.1 | 273.4 | 453.4 | 522.5 | 264.9 | 431.8 | 117.8 | 281.2 | 265 | 138.2 | 196.8 | 211.8 | 151.6
1143 | 904 | 473.3 | 189.32 | 221.3042 | 267.7 | 268 | 273.4 | 250.9 | 481.4 | 43.2 | 19.6 | 78 | 6.3 | 219.4 | 12.8 | 313.7 | 664.3 | 773.5 | 357.2 | 414.4 | 798 | 438.3 | 549.2 | 697.3 | 181 | 207.5 | 674.9 | 71.5 | 119.3 | 171.3 | 273.7 | 453.4 | 522.4 | 265.1 | 432.3 | 117.9 | 281.3 | 265.6 | 138.4 | 197 | 212.1 | 151.9
1144 | 905 | 473.7 | 189.48 | 221.4912 | 268 | 267.4 | 274.6 | 251.1 | 484.6 | 43.2 | 19.6 | 78.1 | 5.6 | 222.2 | 12.6 | 314 | 662.9 | 776.8 | 357.4 | 414.4 | 797.3 | 439 | 549 | 703 | 181.3 | 208 | 675 | 71.6 | 119.5 | 171.6 | 274.1 | 455.6 | 526.8 | 265.6 | 434.5 | 118.1 | 281.1 | 265.9 | 138.7 | 197.2 | 212.4 | 152.2
1145 | 906 | 473.2 | 189.28 | 221.2574 | 267.9 | 267.2 | 275 | 251.3 | 487.7 | 43.2 | 19.6 | 78.3 | 5.5 | 217.3 | 15.7 | 314.2 | 662.5 | 767.6 | 357.6 | 414.7 | 797.7 | 439.8 | 548.3 | 705.6 | 181.7 | 208.4 | 676.3 | 71.7 | 119.7 | 171.9 | 274.4 | 457.5 | 530.1 | 265.9 | 437.5 | 118.2 | 281.3 | 265.5 | 139 | 197.3 | 212.7 | 152.4
1146 | 907 | 472.6 | 189.04 | 220.9769 | 267.9 | 267.4 | 275.6 | 251.5 | 486.4 | 43.3 | 19.6 | 78.4 | 5.5 | 219.6 | 16.7 | 314.5 | 664.3 | 755.1 | 357.7 | 414.7 | 798.7 | 440.5 | 546.1 | 706.2 | 182.1 | 208.8 | 676.9 | 71.8 | 120 | 172.2 | 274.7 | 457.5 | 529.6 | 266.2 | 437.2 | 118.3 | 281.3 | 265.3 | 139.2 | 197.4 | 213.1 | 152.7
1147 | 908 | 473.6 | 189.44 | 221.4444 | 268.2 | 267 | 276.2 | 251.4 | 479.2 | 43.3 | 19.6 | 78.4 | 6.2 | 248.1 | 12.5 | 314.7 | 665.8 | 746.8 | 357.9 | 414.8 | 799.4 | 441.2 | 544.9 | 697.6 | 182.4 | 209.2 | 675.9 | 71.9 | 120.2 | 172.3 | 275.1 | 453.7 | 521.5 | 266.3 | 434.4 | 118.4 | 281.3 | 265.8 | 139.4 | 197.7 | 213.5 | 152.9
1148 | 909 | 473.5 | 189.4 | 221.3977 | 269 | 266.2 | 276.3 | 251.4 | 474.7 | 43.3 | 19.6 | 78.3 | 6.9 | 213.3 | 9.7 | 315.1 | 664.6 | 738.8 | 358.3 | 414.6 | 798 | 441.9 | 548.4 | 688.7 | 182.8 | 209.7 | 672.8 | 72 | 120.4 | 172.8 | 275.4 | 451.4 | 520.4 | 266.6 | 433.9 | 118.6 | 281.4 | 266 | 139.6 | 197.9 | 213.8 | 153.2
1149 | 910 | 473.3 | 189.32 | 221.3042 | 269.2 | 266 | 276.5 | 251.6 | 472.6 | 43.3 | 19.6 | 78.3 | 6.3 | 217.4 | 8.8 | 315.4 | 665.2 | 750.8 | 358.6 | 415 | 797.6 | 442.6 | 552 | 687.9 | 183.2 | 210.1 | 671.6 | 72.2 | 120.7 | 173 | 275.8 | 449.6 | 515.7 | 266.8 | 433.4 | 118.7 | 281.5 | 265.7 | 139.8 | 198.1 | 214.1 | 153.4
1150 | 911 | 472.8 | 189.12 | 221.0704 | 268.6 | 265.9 | 276.2 | 251.9 | 468.6 | 43.3 | 19.6 | 78.3 | 6.2 | 215.2 | 8.8 | 315.7 | 669.5 | 765.9 | 358.9 | 415.2 | 797.6 | 443.3 | 550.7 | 695.6 | 183.5 | 210.5 | 672.2 | 72.3 | 120.9 | 173.1 | 276.1 | 448.2 | 514.5 | 267.2 | 432.4 | 118.8 | 281.3 | 265.8 | 140 | 198.3 | 214.4 | 153.6
1151 | 912 | 472.7 | 189.08 | 221.0236 | 267.6 | 265.8 | 276.5 | 252.3 | 471.2 | 43.3 | 19.6 | 78.3 | 6.1 | 213.7 | 9.4 | 316 | 665.1 | 755.4 | 359.1 | 415.3 | 798.2 | 444 | 551.5 | 701.8 | 183.9 | 210.9 | 673 | 72.4 | 121.1 | 173.7 | 276.5 | 450.1 | 523.4 | 267.7 | 435.6 | 118.9 | 281 | 265.3 | 140.2 | 198.5 | 214.7 | 153.9
1152 | 913 | 473.4 | 189.36 | 221.3509 | 267.1 | 266 | 276.9 | 252.2 | 475.7 | 43.3 | 19.6 | 78.4 | 7.1 | 235.7 | 9.7 | 316.3 | 664.3 | 745.3 | 359.3 | 415 | 798.8 | 444.8 | 550.6 | 703.4 | 184.3 | 211.4 | 675 | 72.5 | 121.3 | 174 | 276.8 | 451.7 | 523.1 | 268.3 | 437.4 | 119.1 | 281.1 | 264.8 | 140.4 | 198.6 | 215 | 154.1
1153 | 914 | 472.6 | 189.04 | 220.9769 | 267.1 | 266.5 | 277.6 | 252.3 | 474.1 | 43.3 | 19.6 | 78.4 | 6.9 | 248 | 10.4 | 316.6 | 668.9 | 727.8 | 359.5 | 415.2 | 799.5 | 445.6 | 551 | 699.5 | 184.6 | 211.8 | 675.4 | 72.6 | 121.5 | 174.3 | 277.2 | 450.5 | 518.9 | 268.4 | 436 | 119.2 | 281.2 | 264.8 | 140.6 | 198.8 | 215.4 | 154.4
1154 | 915 | 473.3 | 189.32 | 221.3042 | 267.4 | 267.2 | 277.7 | 252.5 | 468.6 | 43.3 | 19.6 | 78.5 | 7.5 | 205.3 | 9.2 | 316.9 | 673.6 | 727.1 | 359.5 | 415.3 | 798.7 | 446.4 | 551.3 | 700.3 | 185 | 212.2 | 675.7 | 72.7 | 121.8 | 174.5 | 277.5 | 448.4 | 516.6 | 268.7 | 435.8 | 119.3 | 281.4 | 264.5 | 140.9 | 198.9 | 215.7 | 154.6
1155 | 916 | 474 | 189.6 | 221.6315 | 267.8 | 267.4 | 277.3 | 252.7 | 465.2 | 43.3 | 19.6 | 78.5 | 6 | 200.9 | 8.2 | 317.2 | 677.3 | 741.6 | 359.7 | 415.3 | 799.9 | 447.4 | 551.5 | 702.6 | 185.3 | 212.6 | 676.2 | 72.8 | 122 | 174.7 | 277.8 | 445.6 | 511.9 | 269.1 | 434.7 | 119.4 | 282 | 264.3 | 141.3 | 199.1 | 216 | 154.9
1156 | 917 | 472.8 | 189.12 | 221.0704 | 267.9 | 267.1 | 277.8 | 252.8 | 462.2 | 43.4 | 19.6 | 78.5 | 5.9 | 218.8 | 9.5 | 317.6 | 670.6 | 752.2 | 359.9 | 415.2 | 800.9 | 448.6 | 551.7 | 697.6 | 185.7 | 213.1 | 676.4 | 72.9 | 122.3 | 174.9 | 278.2 | 443.3 | 508.7 | 269.3 | 433.8 | 119.6 | 282 | 264 | 141.4 | 199.3 | 216.2 | 155.1
1157 | 918 | 473.5 | 189.4 | 221.3977 | 268.1 | 266.9 | 277.9 | 253.2 | 463.2 | 43.4 | 19.6 | 78.5 | 5.7 | 232.2 | 10.7 | 317.9 | 669.2 | 752.9 | 360.1 | 415.2 | 802.3 | 450.4 | 551.2 | 697.5 | 186.1 | 213.5 | 676.1 | 73 | 122.5 | 175.3 | 278.5 | 443.7 | 509.3 | 269.5 | 433.5 | 119.7 | 282.2 | 264 | 141.6 | 199.5 | 216.5 | 155.4
1158 | 919 | 474.2 | 189.68 | 221.725 | 268.5 | 266.4 | 277.8 | 253.3 | 463.6 | 43.5 | 19.6 | 78.5 | 6.5 | 240 | 11.1 | 318.2 | 668.7 | 757.2 | 360.3 | 415.4 | 804 | 452.7 | 550.2 | 696.1 | 186.4 | 213.9 | 676.7 | 73.2 | 122.7 | 175.5 | 278.8 | 443.6 | 503.1 | 269.7 | 433.1 | 119.8 | 282.8 | 264.6 | 141.8 | 199.6 | 216.8 | 155.6
1159 | 920 | 474.2 | 189.68 | 221.725 | 268.5 | 266 | 277.7 | 253.3 | 458.3 | 43.5 | 19.6 | 78.6 | 5.9 | 220.3 | 12.3 | 318.5 | 665 | 754.4 | 360.6 | 415.4 | 805.7 | 454.7 | 549.4 | 693.8 | 186.7 | 214.3 | 676.6 | 73.3 | 123 | 175.6 | 279.2 | 441.5 | 495.2 | 269.8 | 431.8 | 119.9 | 282.8 | 265.1 | 142.1 | 199.9 | 217.1 | 155.8
1160 | 921 | 474.2 | 189.68 | 221.725 | 269.1 | 265.7 | 277.2 | 253.6 | 453.4 | 43.5 | 19.6 | 78.6 | 5.6 | 213.5 | 12.7 | 318.8 | 669.9 | 749.8 | 360.9 | 415.7 | 807.2 | 456.3 | 549.8 | 687.7 | 187.1 | 214.8 | 676.9 | 73.4 | 123.2 | 175.5 | 279.5 | 440.4 | 489.1 | 270 | 431.5 | 120.1 | 282.9 | 265.4 | 142.2 | 200.2 | 217.4 | 156.1
1161 | 922 | 473.4 | 189.36 | 221.3509 | 271.1 | 265.6 | 276.4 | 253.8 | 449.6 | 43.5 | 19.6 | 78.6 | 6.1 | 223.7 | 10.7 | 319.1 | 671.4 | 763 | 361.1 | 415.8 | 808.5 | 457.6 | 549.5 | 687.9 | 187.4 | 215.2 | 676 | 73.5 | 123.4 | 175.6 | 279.8 | 439.6 | 484.7 | 270.1 | 431.5 | 120.2 | 282.9 | 265.8 | 142.5 | 200.4 | 217.7 | 156.3
1162 | 923 | 472.8 | 189.12 | 221.0704 | 272.6 | 267 | 275.8 | 253.9 | 448.8 | 43.6 | 19.6 | 78.6 | 7.4 | 224.4 | 9.1 | 319.4 | 667.5 | 776.3 | 361.4 | 415.9 | 808.6 | 458.6 | 549.5 | 683.1 | 187.8 | 215.6 | 676.3 | 73.7 | 123.6 | 176 | 280.1 | 440.6 | 480 | 270.2 | 432.4 | 120.3 | 283.2 | 266.1 | 142.8 | 200.8 | 218.1 | 156.6
1163 | 924 | 473.6 | 189.44 | 221.4444 | 273.3 | 268.4 | 274.8 | 254.1 | 444.8 | 43.6 | 19.6 | 78.6 | 7.5 | 222.5 | 8.2 | 319.8 | 668.4 | 773 | 361.7 | 416.1 | 807.7 | 459.5 | 548.1 | 684.5 | 188.1 | 216.1 | 675.6 | 73.8 | 123.8 | 176.1 | 280.5 | 439.1 | 472.9 | 270.2 | 431.3 | 120.5 | 284.1 | 266.8 | 143.2 | 201.2 | 218.5 | 156.8
1164 | 925 | 473.4 | 189.36 | 221.3509 | 273 | 268.7 | 273.2 | 254.9 | 441 | 43.6 | 19.6 | 78.7 | 7.2 | 222.2 | 8.1 | 320.1 | 669.7 | 772.1 | 362 | 416.3 | 806.8 | 460.3 | 550.3 | 681.4 | 188.5 | 216.5 | 674.7 | 73.9 | 123.9 | 176.1 | 280.8 | 438.4 | 472.7 | 270.5 | 431.6 | 120.6 | 284.7 | 267.7 | 143.5 | 201.6 | 218.8 | 157.1
1165 | 926 | 473.6 | 189.44 | 221.4444 | 272.4 | 268.9 | 272.1 | 255.5 | 442.3 | 43.6 | 19.6 | 78.7 | 7.7 | 238.8 | 8.6 | 320.7 | 671.3 | 783 | 362.5 | 416.5 | 807.4 | 461 | 551.9 | 686.1 | 188.8 | 216.9 | 674.7 | 74.1 | 124.1 | 176.4 | 281.1 | 440 | 479 | 270.8 | 433 | 120.8 | 285.1 | 268.4 | 143.9 | 201.8 | 219.1 | 157.4
1166 | 927 | 473.7 | 189.48 | 221.4912 | 272.9 | 268.5 | 271.8 | 255.8 | 444.2 | 43.7 | 19.5 | 78.7 | 5.4 | 236.1 | 11.3 | 321.1 | 677.4 | 788.9 | 362.9 | 416.7 | 807.4 | 461.6 | 553 | 687.7 | 189.1 | 217.4 | 676.1 | 74.2 | 124.3 | 176.7 | 281.3 | 440.5 | 476.9 | 271.1 | 432.6 | 120.9 | 285.8 | 268.5 | 144.5 | 202.1 | 219.5 | 157.6
1167 | 928 | 472.8 | 189.12 | 221.0704 | 275.7 | 270.9 | 271.5 | 255.9 | 443.6 | 43.7 | 19.5 | 78.8 | 6.5 | 234.5 | 10.9 | 321.5 | 676.4 | 782 | 363.2 | 417 | 806.4 | 462.1 | 551 | 691.7 | 189.5 | 217.8 | 676.1 | 74.3 | 124.5 | 177.1 | 281.6 | 440.4 | 475.6 | 271.2 | 431.9 | 121.1 | 286.5 | 268.4 | 144.5 | 202.4 | 219.8 | 157.9
1168 | 929 | 472.3 | 188.92 | 220.8366 | 277 | 275 | 271.5 | 256.1 | 441.4 | 43.7 | 19.5 | 78.9 | 5 | 218.2 | 10.4 | 321.8 | 673.6 | 780 | 363.5 | 417.1 | 805.7 | 462.5 | 548.5 | 692.1 | 189.8 | 218.2 | 676.8 | 74.4 | 124.7 | 177.1 | 282 | 438.6 | 471.4 | 271.4 | 430.9 | 121.3 | 285.5 | 269.1 | 144.7 | 202.5 | 220.2 | 158.2
1169 | 930 | 473.6 | 189.44 | 221.4444 | 277.4 | 275.5 | 271.2 | 256.2 | 439.8 | 43.7 | 19.5 | 79.1 | 5.5 | 237.4 | 9 | 322 | 669.8 | 782.2 | 363.7 | 417.2 | 806.3 | 463 | 550.1 | 693.9 | 190.1 | 218.7 | 676.7 | 74.5 | 124.9 | 177.2 | 282.3 | 438.6 | 470.2 | 271.6 | 430.6 | 121.4 | 285.3 | 268.8 | 145 | 202.8 | 220.5 | 158.4
1170 | 931 | 475.8 | 190.32 | 222.4731 | 277.4 | 274.1 | 270.9 | 256 | 441 | 43.8 | 19.5 | 79.2 | 6 | 213.5 | 10.7 | 322.5 | 671.5 | 783.9 | 364 | 417.4 | 805.8 | 463.4 | 552.6 | 684.3 | 190.4 | 219.1 | 677.7 | 74.6 | 125.1 | 177.5 | 282.6 | 440.1 | 471.2 | 271.9 | 432.3 | 121.6 | 285.5 | 269.3 | 145.3 | 203 | 220.9 | 158.7
1171 | 932 | 475.5 | 190.2 | 222.3328 | 278 | 273.6 | 270.3 | 256.2 | 442.4 | 43.8 | 19.5 | 79.3 | 5.6 | 207.1 | 13.1 | 322.8 | 670.6 | 772.2 | 364.2 | 417.6 | 805 | 463.8 | 555.2 | 674.4 | 190.7 | 219.5 | 677.1 | 74.7 | 125.4 | 177.6 | 282.9 | 442 | 475.7 | 272.1 | 435.1 | 121.8 | 286.2 | 270.1 | 145.7 | 203.4 | 221.3 | 159
1172 | 933 | 472.8 | 189.12 | 221.0704 | 278.2 | 273.7 | 269.9 | 257.1 | 442.8 | 43.8 | 19.5 | 79.4 | 6.3 | 190.2 | 14.7 | 323.1 | 671.1 | 762.4 | 364.4 | 417.8 | 803.6 | 463.9 | 559 | 668.8 | 191 | 220 | 673.7 | 74.8 | 125.6 | 177.7 | 283.3 | 444.3 | 475.7 | 272.2 | 437.1 | 121.9 | 287.1 | 270.7 | 146.2 | 203.8 | 221.6 | 159.2
1173 | 934 | 472.8 | 189.12 | 221.0704 | 277.8 | 273 | 270.1 | 258.1 | 444.4 | 43.9 | 19.5 | 79.5 | 5.8 | 229.4 | 14.7 | 323.4 | 676.1 | 766.7 | 364.6 | 418 | 803.7 | 464.2 | 563.2 | 671.2 | 191.4 | 220.4 | 673.8 | 74.9 | 125.8 | 177.9 | 283.6 | 449 | 485.1 | 272.4 | 441.2 | 122.1 | 287.6 | 271 | 146.6 | 204.2 | 222 | 159.5
1174 | 935 | 473.3 | 189.32 | 221.3042 | 276.9 | 272.7 | 270.2 | 259.3 | 448 | 43.9 | 19.5 | 79.6 | 6.5 | 209.4 | 13.7 | 323.6 | 676.6 | 785.9 | 364.8 | 418.2 | 804.3 | 464.4 | 563.7 | 667.4 | 191.6 | 220.9 | 675 | 75 | 126 | 178.1 | 283.9 | 451.7 | 489.2 | 272.6 | 441.7 | 122.3 | 287.6 | 271.5 | 146.9 | 204.5 | 222.3 | 159.8
1175 | 936 | 472.9 | 189.16 | 221.1171 | 277.4 | 273.1 | 270.8 | 259.7 | 447.1 | 43.9 | 19.6 | 79.7 | 5.9 | 211.4 | 12.8 | 324.1 | 674.1 | 793.8 | 365.1 | 418.5 | 804.5 | 464.9 | 561.3 | 669 | 191.9 | 221.3 | 672.9 | 75.1 | 126.2 | 178.3 | 284.3 | 450.9 | 486.8 | 273 | 439.3 | 122.5 | 287.7 | 272.3 | 147.2 | 204.7 | 222.7 | 160.1
1176 | 937 | 473.9 | 189.56 | 221.5847 | 278.3 | 274.5 | 271.2 | 259.6 | 449.9 | 43.9 | 19.6 | 79.8 | 6.5 | 214 | 12.1 | 324.3 | 672.6 | 803.5 | 365.4 | 418.6 | 804.6 | 465.4 | 559.3 | 678.7 | 192.2 | 221.8 | 672.7 | 75.2 | 126.4 | 178.7 | 284.6 | 451.9 | 495.8 | 273.3 | 440 | 122.7 | 287.4 | 272.4 | 147.5 | 204.9 | 223.1 | 160.3
1177 | 938 | 474 | 189.6 | 221.6315 | 279.3 | 279.8 | 271.2 | 259.5 | 455.9 | 43.9 | 19.5 | 79.9 | 5.4 | 221 | 13.6 | 324.7 | 672.4 | 811.4 | 365.6 | 418.7 | 805.7 | 465.9 | 556.9 | 689.8 | 192.5 | 222.2 | 673.6 | 75.3 | 126.6 | 178.8 | 285 | 453.8 | 502 | 273.8 | 441.8 | 122.9 | 287 | 272 | 147.7 | 205.1 | 223.5 | 160.6
1178 | 939 | 474.4 | 189.76 | 221.8185 | 279 | 283.1 | 271.4 | 259.1 | 458.7 | 44 | 19.5 | 79.9 | 5.2 | 238.6 | 12.5 | 325.1 | 676.2 | 809.2 | 365.9 | 418.9 | 806.5 | 466.4 | 552.8 | 691.7 | 192.8 | 222.6 | 674.6 | 75.4 | 126.9 | 179 | 285.3 | 455.2 | 499.4 | 274.1 | 442.5 | 123 | 286.7 | 271.6 | 147.9 | 205.3 | 223.9 | 160.8
1179 | 940 | 473.3 | 189.32 | 221.3042 | 278.9 | 282.5 | 271.8 | 258.5 | 457.5 | 44 | 19.5 | 79.9 | 5.4 | 240.4 | 10.9 | 325.5 | 680.1 | 800.4 | 366.1 | 419.1 | 806.8 | 466.8 | 550.2 | 688.4 | 193.1 | 223.1 | 675.1 | 75.5 | 127.1 | 179.2 | 285.6 | 454.8 | 496.7 | 274.3 | 441.8 | 123.2 | 286.6 | 271.7 | 148.1 | 205.6 | 224.4 | 161
1180 | 941 | 472.8 | 189.12 | 221.0704 | 280.6 | 284.4 | 271.5 | 258.3 | 455 | 44.1 | 19.5 | 79.9 | 5.3 | 208.8 | 10.2 | 325.9 | 694.8 | 813.7 | 366.4 | 419.3 | 806.3 | 467.2 | 548 | 689.2 | 193.4 | 223.5 | 674.5 | 75.6 | 127.3 | 179.4 | 286 | 453.8 | 498.7 | 274.6 | 441.3 | 123.4 | 286.5 | 271.7 | 148.3 | 205.7 | 224.8 | 161.3
1181 | 942 | 471.1 | 188.44 | 220.2755 | 281.2 | 287.6 | 271.1 | 258.2 | 455.5 | 44.2 | 19.5 | 80 | 5 | 226.8 | 9 | 326.1 | 692.8 | 815.9 | 366.5 | 419.6 | 806.3 | 467.7 | 544.8 | 695.2 | 193.7 | 224 | 674.8 | 75.7 | 127.5 | 179.7 | 286.3 | 454.4 | 498.8 | 274.8 | 442.1 | 123.5 | 286.8 | 271.7 | 148.4 | 205.8 | 225.2 | 161.6
1182 | 943 | 473.7 | 189.48 | 221.4912 | 280.4 | 289.7 | 270.9 | 258.2 | 457.4 | 44.2 | 19.5 | 80.1 | 5.3 | 213.8 | 8.6 | 326.5 | 686 | 820.9 | 366.8 | 419.7 | 805.9 | 468.3 | 541.7 | 697.3 | 194 | 224.4 | 675.4 | 75.7 | 127.7 | 179.9 | 286.6 | 454.9 | 500.6 | 275.2 | 442.1 | 123.7 | 287.9 | 271.5 | 148.6 | 205.9 | 225.6 | 161.8
1183 | 944 | 473.6 | 189.44 | 221.4444 | 279 | 288.5 | 270.5 | 258.4 | 458.8 | 44.2 | 19.5 | 80.2 | 4.8 | 234.4 | 7.5 | 326.9 | 680.7 | 826.2 | 367.2 | 419.7 | 806.2 | 468.9 | 538.9 | 706.4 | 194.3 | 224.9 | 675.8 | 75.8 | 128 | 180.1 | 287 | 455.7 | 503.8 | 275.6 | 442.3 | 123.8 | 288.5 | 271.9 | 148.7 | 206.1 | 225.9 | 162.1
1184 | 945 | 472.3 | 188.92 | 220.8366 | 277.9 | 286.8 | 270.2 | 258 | 462.8 | 44.3 | 19.5 | 80.2 | 5.1 | 256.1 | 7.8 | 327.2 | 679.4 | 826.9 | 367.5 | 420 | 805.9 | 469.4 | 536.9 | 714.7 | 194.6 | 225.3 | 676.6 | 75.9 | 128.2 | 180.3 | 287.4 | 458 | 514.7 | 276 | 444.9 | 124 | 288.8 | 272.5 | 148.9 | 206.3 | 226.3 | 162.4
1185 | 946 | 473.1 | 189.24 | 221.2107 | 278.2 | 285.7 | 270.2 | 257.6 | 470.5 | 44.3 | 19.5 | 80.2 | 4.7 | 252.7 | 9.3 | 327.5 | 671.7 | 820.7 | 367.7 | 419.9 | 805.2 | 469.9 | 535.2 | 710.8 | 194.8 | 225.8 | 676.6 | 76 | 128.3 | 180.7 | 287.7 | 460.9 | 524.7 | 276.7 | 446.8 | 124.1 | 288.8 | 272.6 | 149.1 | 206.5 | 226.7 | 162.7
1186 | 947 | 473 | 189.2 | 221.1639 | 277.7 | 284.7 | 270.4 | 257.3 | 471.9 | 44.4 | 19.5 | 80.3 | 4.7 | 255.1 | 9.8 | 327.8 | 669.8 | 804.2 | 367.8 | 419.9 | 804.8 | 470.3 | 534.4 | 703.5 | 195.1 | 226.3 | 676.6 | 76.1 | 128.5 | 181 | 288 | 460.2 | 523.8 | 277.1 | 445.6 | 124.2 | 288.6 | 272.5 | 149.4 | 206.6 | 227.1 | 163
1187 | 948 | 473 | 189.2 | 221.1639 | 277.1 | 282.7 | 271 | 257.1 | 474.8 | 44.4 | 19.5 | 80.4 | 5.6 | 237.9 | 9.7 | 328.2 | 669 | 789.3 | 368 | 420 | 803.9 | 470.8 | 543.3 | 699.5 | 195.4 | 226.8 | 675.1 | 76.2 | 128.7 | 181.5 | 288.4 | 461.5 | 531.4 | 277.6 | 445.5 | 124.3 | 288.5 | 271.8 | 149.5 | 206.7 | 227.4 | 163.2
1188 | 949 | 473.1 | 189.24 | 221.2107 | 276.9 | 281.3 | 271.6 | 257 | 481 | 44.4 | 19.5 | 80.5 | 5.6 | 252.9 | 10.6 | 328.7 | 666.2 | 763.6 | 368.4 | 420.1 | 802.3 | 471.3 | 546.8 | 694.5 | 195.7 | 227.2 | 674.2 | 76.3 | 128.9 | 181.8 | 288.8 | 464.1 | 531.5 | 278.1 | 446.7 | 124.5 | 288.4 | 271 | 149.7 | 206.8 | 227.7 | 163.4
1189 | 950 | 472.3 | 188.92 | 220.8366 | 276.2 | 280.1 | 272 | 257.1 | 482.2 | 44.5 | 19.5 | 80.6 | 5.5 | 248.2 | 11.7 | 329.1 | 663.5 | 749.6 | 368.7 | 420.1 | 799.5 | 472.3 | 548.6 | 686.7 | 196 | 227.7 | 673.2 | 76.4 | 129.1 | 182.1 | 289.1 | 464.6 | 537.1 | 278.6 | 448 | 124.6 | 288.6 | 270.8 | 149.8 | 207 | 228.1 | 163.7
1190 | 951 | 473.2 | 189.28 | 221.2574 | 276.1 | 278.9 | 272.5 | 257.2 | 488.9 | 44.5 | 19.5 | 80.7 | 5.7 | 245.5 | 10.7 | 329.3 | 658.3 | 733.7 | 368.8 | 420.1 | 796.4 | 473.4 | 552.7 | 675.1 | 196.3 | 228.2 | 671.1 | 76.5 | 129.3 | 182.9 | 289.5 | 469.2 | 556.2 | 279.1 | 451.4 | 124.6 | 288.9 | 270.6 | 150.1 | 207.2 | 228.4 | 163.9
1191 | 952 | 474 | 189.6 | 221.6315 | 276 | 277.9 | 274.2 | 257.4 | 496 | 44.5 | 19.5 | 80.8 | 5.6 | 266.7 | 9.8 | 329.6 | 665.3 | 750.1 | 369 | 420.2 | 794.1 | 474.3 | 555.4 | 674.3 | 196.6 | 228.6 | 670.7 | 76.6 | 129.6 | 183.4 | 289.9 | 470.4 | 560.9 | 279.6 | 452.2 | 124.7 | 289.6 | 270.6 | 150.3 | 207.3 | 228.8 | 164.2
1192 | 953 | 473.9 | 189.56 | 221.5847 | 276.1 | 277.2 | 276.2 | 258 | 495.6 | 44.6 | 19.5 | 80.9 | 5.5 | 244.7 | 9.3 | 330 | 663.3 | 753.9 | 369.3 | 420 | 794.3 | 475.2 | 554.3 | 683.4 | 196.8 | 229.1 | 671.5 | 76.7 | 129.8 | 183.4 | 290.3 | 470 | 556.5 | 280 | 450.6 | 124.8 | 290.1 | 270.9 | 150.7 | 207.5 | 229.1 | 164.5
1193 | 954 | 473.8 | 189.52 | 221.538 | 275.3 | 276.9 | 277.9 | 258.7 | 492.2 | 44.6 | 19.5 | 80.9 | 5.6 | 254.5 | 9 | 330.3 | 664 | 756 | 369.5 | 420.1 | 796.2 | 476.1 | 551.3 | 686.4 | 197.1 | 229.5 | 673.3 | 76.8 | 130 | 183.4 | 290.6 | 468.6 | 549.7 | 280.5 | 448.8 | 124.9 | 290.5 | 271.2 | 151 | 207.7 | 229.5 | 164.7
1194 | 955 | 472.5 | 189 | 220.9301 | 274.6 | 276.6 | 278.7 | 259 | 489.3 | 44.7 | 19.5 | 80.9 | 6.3 | 246 | 9.2 | 330.6 | 660.6 | 752.7 | 369.8 | 420.2 | 797.5 | 476.9 | 552.3 | 686.5 | 197.4 | 230 | 673.2 | 76.9 | 130.3 | 183.7 | 291 | 467.6 | 544.2 | 280.9 | 447.7 | 125 | 290.9 | 271.9 | 151.2 | 208.1 | 229.8 | 165
1195 | 956 | 473.2 | 189.28 | 221.2574 | 274.3 | 276.5 | 278.9 | 258.9 | 484.6 | 44.7 | 19.5 | 81 | 6.6 | 244.1 | 8.7 | 330.9 | 659.8 | 754.7 | 370.1 | 420.3 | 797.7 | 477.7 | 552.7 | 689.1 | 197.7 | 230.4 | 673.2 | 77 | 130.5 | 183.9 | 291.4 | 464.8 | 535.6 | 281.2 | 446.4 | 125.1 | 291.1 | 272 | 151.4 | 208.4 | 230.1 | 165.3
1196 | 957 | 474.3 | 189.72 | 221.7717 | 274.3 | 276.7 | 279.3 | 259 | 477.9 | 44.7 | 19.5 | 81.1 | 6 | 233.6 | 8.5 | 331.3 | 664.6 | 749.6 | 370.3 | 420.5 | 799.1 | 478.4 | 553.5 | 688.7 | 197.9 | 230.8 | 674.6 | 77 | 130.7 | 183.9 | 291.8 | 463.4 | 527.1 | 281.4 | 445.9 | 125.1 | 291.3 | 272.6 | 151.5 | 208.8 | 230.4 | 165.5
1197 | 958 | 473.8 | 189.52 | 221.538 | 275.5 | 276 | 278.9 | 259.1 | 472.5 | 44.8 | 19.5 | 81.2 | 5.8 | 247.6 | 8.5 | 331.7 | 674 | 760.3 | 370.6 | 420.7 | 799.9 | 479 | 553.7 | 681.5 | 198.2 | 231.3 | 673.5 | 77.1 | 130.9 | 184.1 | 292.2 | 461.1 | 517.7 | 281.7 | 444.4 | 125.2 | 291.6 | 273.3 | 151.8 | 209.1 | 230.6 | 165.8
1198 | 959 | 472 | 188.8 | 220.6963 | 277.5 | 276.4 | 278.5 | 259.2 | 467 | 44.8 | 19.5 | 81.2 | 4.9 | 217.3 | 7.6 | 332.1 | 673.8 | 773.9 | 371.1 | 421 | 800.5 | 479.7 | 553.7 | 678.1 | 198.5 | 231.7 | 672.3 | 77.2 | 131.1 | 184.2 | 292.6 | 458.9 | 510.4 | 282 | 443.3 | 125.3 | 291.9 | 273.4 | 152.1 | 209.3 | 231 | 166.1
1199 | 960 | 471.4 | 188.56 | 220.4158 | 278.6 | 278.3 | 277.6 | 259.4 | 463.8 | 44.9 | 19.5 | 81.2 | 5.3 | 215.2 | 8 | 332.7 | 673.7 | 770.8 | 371.6 | 421.3 | 801.7 | 480.4 | 553.2 | 683.5 | 198.8 | 232.1 | 672.6 | 77.3 | 131.3 | 184.3 | 293 | 458.2 | 507.3 | 282.4 | 444.2 | 125.4 | 292.1 | 273.7 | 152.5 | 209.6 | 231.3 | 166.3
1200 | 961 | 471.5 | 188.6 | 220.4625 | 279.1 | 280.1 | 276.8 | 259.2 | 460.9 | 44.9 | 19.5 | 81.2 | 5.3 | 252.7 | 7.5 | 333.1 | 678.3 | 767.6 | 372 | 421.5 | 802.1 | 481 | 550.6 | 682.8 | 199 | 232.5 | 673.2 | 77.4 | 131.5 | 184.5 | 293.4 | 458.8 | 503.4 | 282.7 | 445.8 | 125.5 | 292.7 | 274.6 | 152.9 | 209.9 | 231.6 | 166.6
1201 | 962 | 472.6 | 189.04 | 220.9769 | 278.7 | 279.8 | 275.8 | 259.7 | 457.3 | 45 | 19.5 | 81.2 | 5.9 | 218 | 7.4 | 333.4 | 682.6 | 780.7 | 372.3 | 421.7 | 802.7 | 481.8 | 547.8 | 679 | 199.3 | 232.9 | 673.1 | 77.5 | 131.8 | 184.8 | 293.8 | 458.3 | 497.2 | 283 | 446.3 | 125.6 | 292.9 | 275.2 | 153.3 | 210.2 | 232 | 166.8
1202 | 963 | 471.4 | 188.56 | 220.4158 | 279.4 | 278.8 | 274.9 | 260.1 | 454.8 | 45 | 19.5 | 81.3 | 6.6 | 232 | 8.7 | 333.9 | 682.1 | 776.6 | 372.8 | 422 | 802.5 | 482.6 | 545.6 | 675.3 | 199.6 | 233.3 | 672.3 | 77.6 | 132 | 184.8 | 294.3 | 457.1 | 493 | 283.4 | 444.9 | 125.7 | 292.9 | 275.3 | 153.6 | 210.5 | 232.4 | 167.1
1203 | 964 | 473.3 | 189.32 | 221.3042 | 280.3 | 277.9 | 274.7 | 260.5 | 454 | 45.1 | 19.5 | 81.3 | 5.9 | 229 | 10.4 | 334.3 | 678.3 | 778.1 | 373.2 | 422.3 | 802.1 | 483.3 | 545.3 | 672.2 | 199.9 | 233.7 | 673 | 77.7 | 132.2 | 185 | 294.7 | 457.2 | 489.3 | 283.6 | 445.9 | 125.9 | 293.5 | 275.3 | 154.1 | 210.7 | 232.7 | 167.4
1204 | 965 | 471.7 | 188.68 | 220.556 | 279.5 | 276.5 | 274.2 | 260.9 | 453.9 | 45.2 | 19.5 | 81.3 | 5.5 | 204.6 | 10.7 | 334.6 | 683.2 | 786.5 | 373.6 | 422.6 | 802.3 | 484 | 546.6 | 674.9 | 200.1 | 234 | 672.7 | 77.8 | 132.4 | 185.2 | 295.1 | 458.3 | 490.8 | 284 | 446.6 | 126 | 293.7 | 276 | 154.4 | 211 | 233 | 167.7
1205 | 966 | 472.3 | 188.92 | 220.8366 | 278.9 | 275.8 | 273.7 | 261.1 | 454.8 | 45.2 | 19.5 | 81.3 | 5.5 | 205.9 | 8.5 | 334.9 | 687.6 | 786.6 | 373.9 | 422.8 | 802.4 | 484.7 | 544.6 | 674 | 200.4 | 234.3 | 673.3 | 77.9 | 132.6 | 185.4 | 295.6 | 460.7 | 488.1 | 284.2 | 446.7 | 126.1 | 294 | 276.8 | 154.6 | 211.3 | 233.4 | 167.9
1206 | 967 | 473.2 | 189.28 | 221.2574 | 278.7 | 276.8 | 273.8 | 261.6 | 453 | 45.2 | 19.5 | 81.3 | 4.9 | 241.6 | 6.8 | 335.3 | 690.2 | 788.5 | 374.2 | 423 | 802.4 | 485.3 | 543.3 | 672.7 | 200.7 | 234.7 | 674.3 | 77.9 | 132.8 | 185.6 | 296 | 461.1 | 487.3 | 284.6 | 446.7 | 126.3 | 294.3 | 276.9 | 154.9 | 211.7 | 233.8 | 168.2
1207 | 968 | 474.8 | 189.92 | 222.0055 | 278.3 | 277.5 | 273.6 | 261.7 | 453.5 | 45.3 | 19.4 | 81.3 | 4.6 | 215.6 | 6.4 | 335.8 | 692.8 | 789.2 | 374.6 | 423.2 | 802.7 | 485.9 | 543.5 | 673.9 | 200.9 | 235 | 675.8 | 78 | 133 | 185.7 | 296.4 | 460.9 | 489.3 | 284.9 | 446.2 | 126.4 | 294.2 | 276.8 | 155.2 | 211.9 | 234.1 | 168.5
1208 | 969 | 474.2 | 189.68 | 221.725 | 278.1 | 277.1 | 273.5 | 261.7 | 452.3 | 45.3 | 19.4 | 81.2 | 5.3 | 201.1 | 6.5 | 336.1 | 697.9 | 800.2 | 375 | 423.4 | 803.5 | 486.5 | 542.6 | 675 | 201.2 | 235.3 | 677.1 | 78.1 | 133.2 | 185.9 | 296.8 | 459.1 | 487.5 | 285.3 | 445 | 126.6 | 294 | 276.4 | 155.4 | 212 | 234.5 | 168.7
1209 | 970 | 472.5 | 189 | 220.9301 | 279 | 276.7 | 273.4 | 261.4 | 451.1 | 45.4 | 19.4 | 81.1 | 6.3 | 225.2 | 6 | 336.4 | 694.1 | 803.9 | 375.2 | 423.6 | 805.7 | 487.1 | 540.5 | 681.1 | 201.5 | 235.7 | 676.9 | 78.2 | 133.4 | 186.2 | 297.3 | 457.8 | 490.2 | 285.6 | 444.9 | 126.7 | 293.3 | 276 | 155.5 | 212.2 | 234.8 | 169
1210 | 971 | 471.9 | 188.76 | 220.6496 | 278.7 | 279.1 | 273.8 | 260.8 | 451.9 | 45.4 | 19.4 | 81.2 | 7 | 213.1 | 6.9 | 336.8 | 696.1 | 795.7 | 375.5 | 423.8 | 807.3 | 487.6 | 540.3 | 682.4 | 201.8 | 236 | 676.6 | 78.3 | 133.6 | 186.4 | 297.7 | 457.3 | 491.4 | 286 | 445 | 126.9 | 292.8 | 275.8 | 155.6 | 212.4 | 235.2 | 169.2
1211 | 972 | 472.5 | 189 | 220.9301 | 277.7 | 280.9 | 274.3 | 260.3 | 452.1 | 45.5 | 19.4 | 81.2 | 7.4 | 213.6 | 11.3 | 336.9 | 703.1 | 790 | 375.7 | 424 | 808.6 | 488.2 | 539.8 | 687.7 | 202 | 236.4 | 679.1 | 78.4 | 133.7 | 186.6 | 298.1 | 458.2 | 493 | 286.4 | 445.6 | 127 | 292.2 | 275.9 | 155.7 | 212.7 | 235.5 | 169.4
1212 | 973 | 472.6 | 189.04 | 220.9769 | 277 | 280.1 | 274 | 260.4 | 453.4 | 45.5 | 19.4 | 81.4 | 7 | 207.5 | 13.7 | 337.4 | 702.5 | 785.6 | 376.1 | 424.2 | 809.7 | 488.8 | 538.8 | 685 | 202.3 | 236.7 | 681.1 | 78.5 | 133.9 | 186.8 | 298.4 | 459 | 491.8 | 286.7 | 445.8 | 127.1 | 292 | 275.8 | 156 | 213 | 235.9 | 169.7
1213 | 974 | 472.9 | 189.16 | 221.1171 | 277.4 | 278.8 | 273 | 260.6 | 454.3 | 45.5 | 19.4 | 81.4 | 6.1 | 228.4 | 12.4 | 337.8 | 701.9 | 784.1 | 376.4 | 424.4 | 811.1 | 489.2 | 537.6 | 686.2 | 202.6 | 237 | 680 | 78.6 | 134.1 | 186.9 | 298.8 | 459.5 | 491.4 | 286.9 | 446.3 | 127.3 | 292.1 | 276.1 | 156.3 | 213.1 | 236.2 | 169.9
1214 | 975 | 474.2 | 189.68 | 221.725 | 277.8 | 278.2 | 273.6 | 261.4 | 453.6 | 45.7 | 19.4 | 81.5 | 6.4 | 206.9 | 13 | 338.1 | 695.9 | 768.1 | 376.6 | 424.6 | 812.5 | 489.7 | 536.7 | 686 | 202.9 | 237.3 | 680.9 | 78.6 | 134.3 | 187 | 299.2 | 460.6 | 490.9 | 287.2 | 446.9 | 127.3 | 292.5 | 277 | 156.5 | 213.3 | 236.4 | 170
1215 | 976 | 472 | 188.8 | 220.6963 | 279 | 277.1 | 272.2 | 261.5 | 454.4 | 45.6 | 19.4 | 81.6 | 7.5 | 219 | 13 | 338.3 | 692.7 | 756 | 376.8 | 424.8 | 812.7 | 490.1 | 535.7 | 685 | 203.1 | 237.7 | 680.8 | 78.8 | 134.5 | 187.2 | 299.6 | 464.2 | 486.5 | 287.3 | 449.6 | 127.5 | 293.6 | 278.2 | 157 | 213.8 | 236.9 | 170.4
1216 | 977 | 475.1 | 190.04 | 222.1458 | 278.9 | 276.6 | 271.1 | 262 | 453.5 | 45.6 | 19.4 | 81.7 | 6.7 | 234 | 13.1 | 338.3 | 690 | 764.2 | 377.2 | 425 | 812.2 | 490.6 | 534.5 | 686.5 | 203.4 | 238 | 680.6 | 78.8 | 134.7 | 187.4 | 300.1 | 465.2 | 485.9 | 287.5 | 448.6 | 127.6 | 294.4 | 279.1 | 157.4 | 214.4 | 237.3 | 170.7
1217 | 978 | 473.6 | 189.44 | 221.4444 | 278.4 | 276.1 | 270.7 | 262.3 | 452.2 | 45.6 | 19.4 | 81.7 | 6.5 | 225.9 | 14.4 | 338.8 | 695.1 | 779.7 | 377.6 | 425.2 | 811.3 | 491.1 | 533 | 695.9 | 203.7 | 238.3 | 680.1 | 78.9 | 134.9 | 187.6 | 300.5 | 464.5 | 484.6 | 287.8 | 448.1 | 127.8 | 294.8 | 279.3 | 157.8 | 214.6 | 237.6 | 171
1218 | 979 | 471.6 | 188.64 | 220.5093 | 278.1 | 277.5 | 270.8 | 262.6 | 454.1 | 45.7 | 19.4 | 81.8 | 6.2 | 224.9 | 12.5 | 339.3 | 695.4 | 790.5 | 378 | 425.4 | 811.3 | 491.5 | 533.3 | 697.3 | 204 | 238.7 | 681.1 | 79 | 135.1 | 187.9 | 301 | 465.3 | 490.6 | 288.2 | 449.1 | 127.9 | 295.2 | 279.5 | 158.2 | 214.8 | 238 | 171.2
1219 | 980 | 472.3 | 188.92 | 220.8366 | 277.9 | 279 | 271 | 263.1 | 456.2 | 45.7 | 19.4 | 81.7 | 4.7 | 244 | 11.2 | 339.7 | 697 | 792.3 | 378.4 | 425.6 | 811.4 | 491.9 | 533.5 | 691.8 | 204.2 | 239 | 679.8 | 79.1 | 135.3 | 188 | 301.4 | 466.2 | 493.3 | 288.6 | 450 | 128 | 295.2 | 279.7 | 158.4 | 215.1 | 238.3 | 171.5
1220 | 981 | 472.4 | 188.96 | 220.8834 | 278.6 | 280.4 | 271.1 | 263.4 | 456.2 | 45.8 | 19.4 | 81.8 | 4.4 | 250.9 | 12.1 | 340 | 696 | 785.6 | 378.8 | 425.8 | 811.6 | 492.4 | 535.7 | 687.4 | 204.5 | 239.3 | 679.6 | 79.2 | 135.4 | 188.1 | 301.8 | 465.3 | 492.9 | 288.9 | 448.7 | 128.2 | 295.3 | 279.5 | 158.7 | 215.3 | 238.7 | 171.8
1221 | 982 | 473.4 | 189.36 | 221.3509 | 280.9 | 282.5 | 271.2 | 263.3 | 456.2 | 45.8 | 19.4 | 81.9 | 5.6 | 240.9 | 11.3 | 340.5 | 697.6 | 793.7 | 379.1 | 426 | 812.2 | 492.8 | 535.1 | 689 | 204.8 | 239.6 | 679.9 | 79.3 | 135.6 | 188.5 | 302.3 | 464 | 492.3 | 289.2 | 447.7 | 128.3 | 295.2 | 279.8 | 158.9 | 215.5 | 239.1 | 172
1222 | 983 | 474.2 | 189.68 | 221.725 | 281.9 | 284.2 | 271.7 | 263.1 | 456.8 | 45.8 | 19.4 | 82 | 5.8 | 225.5 | 9 | 340.7 | 693 | 800.7 | 379.3 | 426.2 | 813.2 | 493.1 | 535.3 | 694 | 205.1 | 239.9 | 680.4 | 79.4 | 135.8 | 188.6 | 302.7 | 463.9 | 495.1 | 289.6 | 448.3 | 128.4 | 294.8 | 280.1 | 159.1 | 215.7 | 239.4 | 172.3
1223 | 984 | 471.9 | 188.76 | 220.6496 | 281.2 | 286.5 | 271.9 | 262.6 | 458.7 | 45.8 | 19.4 | 82.1 | 5.5 | 221.7 | 9 | 341.2 | 689.8 | 802.6 | 379.6 | 426.5 | 814.9 | 493.5 | 536.9 | 697.1 | 205.3 | 240.2 | 681.4 | 79.5 | 136 | 188.9 | 303.2 | 463.9 | 497.4 | 290.2 | 448.7 | 128.6 | 294.6 | 279.7 | 159.2 | 215.9 | 239.8 | 172.5
1224 | 985 | 471.3 | 188.52 | 220.369 | 280.8 | 288.9 | 271.5 | 261.6 | 462.5 | 45.9 | 19.4 | 82.2 | 5 | 235.8 | 10 | 341.7 | 687.5 | 805.9 | 379.9 | 426.8 | 815.5 | 493.9 | 536.3 | 698 | 205.6 | 240.6 | 681.4 | 79.6 | 136.2 | 189 | 303.6 | 464.8 | 497.5 | 290.5 | 448.7 | 128.7 | 294.5 | 279.3 | 159.4 | 216 | 240.2 | 172.7
1225 | 986 | 470.7 | 188.28 | 220.0885 | 280.4 | 290.6 | 271.3 | 261.5 | 466.1 | 46 | 19.4 | 82.3 | 5.2 | 236.3 | 10 | 342.1 | 686.6 | 809.4 | 380.3 | 427.1 | 815.7 | 494.2 | 536.9 | 700.4 | 205.9 | 240.9 | 681.9 | 79.7 | 136.4 | 189.3 | 304.1 | 467 | 502.7 | 291.1 | 449.8 | 128.8 | 294.7 | 279.1 | 159.5 | 216 | 240.6 | 172.9
1226 | 987 | 471.5 | 188.6 | 220.4625 | 280.1 | 290.8 | 270.7 | 261.3 | 471.7 | 45.9 | 19.4 | 82.4 | 5.3 | 257.2 | 10 | 342.4 | 690.4 | 815.1 | 380.5 | 427.4 | 815.8 | 494.6 | 537.3 | 710.3 | 206.2 | 241.2 | 683.1 | 79.8 | 136.7 | 189.6 | 304.6 | 469.8 | 511.8 | 291.7 | 452.7 | 128.9 | 295.1 | 279.1 | 159.7 | 216.2 | 241 | 173.2
1227 | 988 | 471.9 | 188.76 | 220.6496 | 279.2 | 290.2 | 270.2 | 261.1 | 480.9 | 45.9 | 19.4 | 82.5 | 5.5 | 258.5 | 11.8 | 342.6 | 690.9 | 818.8 | 380.8 | 427.7 | 815.7 | 495.1 | 538.8 | 713 | 206.5 | 241.6 | 684.4 | 79.9 | 136.9 | 189.9 | 305.1 | 474.1 | 522.6 | 292.4 | 455 | 129 | 295.3 | 279.4 | 159.9 | 216.5 | 241.4 | 173.5
1228 | 989 | 471.9 | 188.76 | 220.6496 | 278.5 | 288.7 | 269.9 | 261.3 | 486.3 | 45.9 | 19.4 | 82.6 | 5.9 | 248.8 | 11.7 | 343.1 | 693.1 | 826.2 | 381.2 | 428.1 | 815.4 | 495.5 | 538.1 | 717.4 | 206.8 | 241.9 | 684.2 | 80 | 137 | 190.2 | 305.6 | 475.1 | 522.8 | 292.8 | 455 | 129.1 | 295.8 | 279.7 | 160.1 | 216.7 | 241.8 | 173.7
1229 | 990 | 472.1 | 188.84 | 220.7431 | 278 | 287.7 | 270.4 | 261.3 | 483.7 | 45.9 | 19.4 | 82.8 | 6.1 | 242.2 | 9.4 | 343.6 | 698.1 | 830.3 | 381.6 | 428.5 | 815.9 | 496 | 537.4 | 715.7 | 207 | 242.2 | 684 | 80.1 | 137.2 | 190.2 | 306.1 | 475.3 | 521.1 | 293.3 | 454.3 | 129.2 | 296.3 | 280.1 | 160.4 | 216.9 | 242.2 | 174
1230 | 991 | 472.2 | 188.88 | 220.7898 | 277.4 | 290.1 | 270.5 | 260.9 | 482.1 | 46 | 19.4 | 83 | 6.3 | 225.9 | 7.7 | 343.8 | 703.2 | 821.1 | 381.9 | 428.8 | 816.4 | 496.6 | 535.5 | 716.5 | 207.3 | 242.6 | 684.4 | 80.1 | 137.4 | 190.5 | 306.6 | 475.8 | 522.8 | 293.7 | 455.6 | 129.3 | 296.3 | 280.1 | 160.6 | 217.2 | 242.6 | 174.3
1231 | 992 | 472.1 | 188.84 | 220.7431 | 277.8 | 293.5 | 270.3 | 261.1 | 478.9 | 46 | 19.4 | 83.1 | 5.9 | 207.3 | 7 | 343.8 | 705 | 827.4 | 382.2 | 429.1 | 816.7 | 497.1 | 534.6 | 707.7 | 207.6 | 243 | 683.1 | 80.2 | 137.7 | 190.6 | 307 | 473.5 | 519.1 | 294.2 | 454 | 129.4 | 297 | 279.7 | 160.8 | 217.3 | 243.1 | 174.5
1232 | 993 | 471.2 | 188.48 | 220.3223 | 278 | 293.9 | 270.3 | 261.2 | 473.8 | 46 | 19.4 | 83.2 | 5.8 | 232.7 | 7.2 | 344.3 | 698.9 | 828.6 | 382.6 | 429.4 | 816.6 | 497.7 | 533.6 | 712.4 | 207.9 | 243.3 | 682.5 | 80.3 | 137.9 | 190.8 | 307.5 | 471.6 | 516.8 | 294.6 | 453.5 | 129.5 | 297.2 | 279.5 | 161 | 217.4 | 243.4 | 174.8
1233 | 994 | 472.8 | 189.12 | 221.0704 | 277.4 | 294.3 | 270.4 | 261.2 | 470.3 | 46 | 19.4 | 83.3 | 5.2 | 247.6 | 7.2 | 344.9 | 694.9 | 826.4 | 383 | 429.7 | 816.4 | 498.3 | 532.1 | 714.4 | 208.2 | 243.7 | 683.2 | 80.4 | 138.1 | 191.1 | 308 | 470.4 | 513.4 | 295 | 453.3 | 129.6 | 297.4 | 279.4 | 161.2 | 217.6 | 243.8 | 175.1
1234 | 995 | 473 | 189.2 | 221.1639 | 276.8 | 293 | 270.5 | 261.3 | 470.1 | 46 | 19.4 | 83.4 | 5.5 | 238.7 | 8.4 | 345.3 | 697.4 | 815.5 | 383.3 | 430 | 816.8 | 498.9 | 533.3 | 706 | 208.5 | 244 | 682.7 | 80.5 | 138.3 | 191.5 | 308.5 | 470.4 | 514.7 | 295.4 | 453.9 | 129.7 | 297.7 | 279.5 | 161.4 | 217.8 | 244.2 | 175.3
1235 | 996 | 471.9 | 188.76 | 220.6496 | 277.1 | 292.5 | 271 | 261.4 | 471.8 | 46.1 | 19.4 | 83.5 | 4.8 | 238.6 | 8.8 | 345.5 | 705.8 | 830.3 | 383.5 | 430.2 | 817.6 | 499.5 | 533.5 | 709.4 | 208.8 | 244.4 | 682.8 | 80.6 | 138.5 | 191.6 | 309 | 469.6 | 517.9 | 296 | 453.8 | 129.8 | 297.6 | 279.8 | 161.7 | 218 | 244.5 | 175.6
1236 | 997 | 472.3 | 188.92 | 220.8366 | 277.9 | 290.3 | 271.7 | 261.2 | 474.6 | 46.2 | 19.4 | 83.5 | 5.1 | 245.7 | 9.4 | 345.6 | 708.6 | 826.3 | 384.1 | 430.4 | 817.5 | 500.1 | 535.6 | 706 | 209 | 244.8 | 682.6 | 80.6 | 138.7 | 191.7 | 309.4 | 470.4 | 519.8 | 296.4 | 455.4 | 129.9 | 297.3 | 279.9 | 161.9 | 218.1 | 244.9 | 175.8
1237 | 998 | 470.1 | 188.04 | 219.8079 | 278.6 | 288.8 | 271.6 | 261.4 | 471 | 46.3 | 19.4 | 83.5 | 5.3 | 242.9 | 8.2 | 345.8 | 714.2 | 820.9 | 384.3 | 430.7 | 817.3 | 500.5 | 534.6 | 705.3 | 209.3 | 245.2 | 682.3 | 80.7 | 138.9 | 191.8 | 309.9 | 469.2 | 514 | 296.8 | 454.1 | 130 | 297.1 | 279.8 | 162 | 218.3 | 245.3 | 176
1238 | 999 | 471.3 | 188.52 | 220.369 | 279.5 | 288.5 | 271.7 | 261.7 | 466.5 | 46.4 | 19.4 | 83.5 | 5.3 | 232.3 | 7.1 | 346.2 | 717.7 | 828.1 | 384.6 | 430.9 | 818.1 | 501.1 | 533.3 | 704.1 | 209.6 | 245.7 | 681.2 | 80.8 | 139.1 | 191.9 | 310.4 | 467.1 | 509.1 | 297.2 | 452.6 | 130.1 | 297.1 | 279.9 | 162.2 | 218.5 | 245.7 | 176.3
1239 | 1000 | 472.9 | 189.16 | 221.1171 | 280.4 | 288.3 | 271.4 | 261.9 | 466.1 | 46.4 | 19.4 | 83.5 | 5.2 | 225.1 | 6.7 | 346.5 | 711.5 | 823.9 | 384.9 | 431.1 | 819.6 | 501.8 | 533.4 | 705.9 | 209.9 | 246.2 | 682.2 | 80.9 | 139.3 | 192 | 310.9 | 467.1 | 509.7 | 297.7 | 452.8 | 130.2 | 297.3 | 279.6 | 162.5 | 218.8 | 246 | 176.5
1240 | 1001 | 471.7 | 188.68 | 220.556 | 281.9 | 290.7 | 271.3 | 262.3 | 465.5 | 46.4 | 19.4 | 83.5 | 5.1 | 216.8 | 9.5 | 346.9 | 711 | 820.4 | 385.1 | 431.3 | 821.1 | 502.5 | 533 | 705.7 | 210.2 | 246.7 | 683.5 | 81 | 139.5 | 192.4 | 311.3 | 467.1 | 508.1 | 297.9 | 453.6 | 130.3 | 297.3 | 279.4 | 162.9 | 218.9 | 246.3 | 176.8
1241 | 1002 | 472.5 | 189 | 220.9301 | 283.5 | 289.6 | 270.9 | 262.1 | 463.9 | 46.5 | 19.4 | 83.6 | 4.7 | 222.7 | 10.3 | 347.3 | 712.9 | 824.5 | 385.4 | 431.5 | 822.2 | 503.2 | 531.8 | 708.9 | 210.4 | 247.2 | 683.9 | 81 | 139.7 | 192.7 | 311.8 | 466.4 | 508.4 | 298.3 | 454.2 | 130.5 | 296.8 | 279.4 | 163.2 | 219 | 246.7 | 177
1242 | 1003 | 471 | 188.4 | 220.2287 | 284.5 | 287.9 | 270.3 | 261.4 | 463.6 | 46.5 | 19.4 | 83.6 | 5.3 | 207.8 | 9.9 | 347.6 | 707.1 | 816.8 | 385.6 | 431.7 | 823.2 | 503.9 | 530.2 | 715.5 | 210.7 | 247.7 | 685.8 | 81.1 | 139.9 | 192.9 | 312.2 | 466.5 | 507.5 | 298.6 | 454.8 | 130.6 | 296.5 | 279.9 | 163.4 | 219.2 | 247 | 177.3
1243 | 1004 | 469.4 | 187.76 | 219.4806 | 284.7 | 286.4 | 270.5 | 261.3 | 464.3 | 46.6 | 19.4 | 83.6 | 5.1 | 207.1 | 10.3 | 348 | 705.9 | 818 | 386 | 431.9 | 823.5 | 504.7 | 530.2 | 717.5 | 211 | 248.2 | 687.2 | 81.2 | 140.1 | 193 | 312.7 | 468.4 | 509 | 299 | 455.6 | 130.7 | 296.5 | 279.7 | 163.7 | 219.4 | 247.4 | 177.5
1244 | 1005 | 472.4 | 188.96 | 220.8834 | 284.7 | 285.6 | 271 | 261 | 465.1 | 46.6 | 19.4 | 83.6 | 5 | 211.1 | 9.2 | 348.4 | 707.6 | 816.8 | 386.5 | 432.1 | 822.7 | 505.4 | 529.9 | 712 | 211.3 | 248.6 | 686.1 | 81.3 | 140.3 | 193.1 | 313.1 | 468.3 | 507.1 | 299.3 | 455.1 | 130.8 | 296.2 | 279.7 | 164 | 219.6 | 247.8 | 177.7
1245 | 1006 | 471.5 | 188.6 | 220.4625 | 284.1 | 284.8 | 271.1 | 260.7 | 464.2 | 46.7 | 19.3 | 83.7 | 5.4 | 250.5 | 6.9 | 348.7 | 702.1 | 831 | 386.8 | 432.3 | 822.4 | 506.2 | 529.3 | 713.2 | 211.6 | 249.1 | 685 | 81.3 | 140.5 | 193.4 | 313.6 | 466.6 | 507.4 | 299.9 | 454.8 | 130.9 | 296.2 | 279.7 | 164.2 | 219.7 | 248.1 | 178
1246 | 1007 | 471.9 | 188.76 | 220.6496 | 282.3 | 284 | 271.8 | 261 | 466.7 | 46.8 | 19.3 | 83.6 | 4.8 | 237.8 | 6.1 | 349.1 | 697.3 | 834.9 | 387.2 | 432.5 | 822.2 | 507 | 529.4 | 721.4 | 211.9 | 249.6 | 686.3 | 81.4 | 140.6 | 193.8 | 314 | 467.1 | 508.9 | 300.4 | 455.4 | 131 | 296.2 | 279.4 | 164.2 | 219.9 | 248.4 | 178.2
1247 | 1008 | 472.1 | 188.84 | 220.7431 | 281.7 | 282.7 | 272.3 | 260.6 | 470 | 46.8 | 19.3 | 83.7 | 4.5 | 222.1 | 6.4 | 349.6 | 693.5 | 830.6 | 387.8 | 432.7 | 822.3 | 507.8 | 529.5 | 721.8 | 212.2 | 250.1 | 686.8 | 81.5 | 140.8 | 194.2 | 314.5 | 468.2 | 515.1 | 301 | 457.1 | 131.2 | 296.3 | 279.2 | 164.4 | 220.1 | 248.8 | 178.5
1248 | 1009 | 472.4 | 188.96 | 220.8834 | 280.6 | 281.3 | 272.6 | 260.5 | 475 | 46.9 | 19.3 | 83.8 | 4.7 | 221.2 | 9.4 | 349.9 | 700.1 | 837.6 | 388.1 | 432.8 | 821.9 | 508.6 | 530.1 | 724.3 | 212.5 | 250.5 | 688 | 81.6 | 141 | 194.6 | 315 | 468.3 | 521.1 | 301.6 | 458.2 | 131.3 | 296.2 | 279.4 | 164.5 | 220.1 | 249.2 | 178.7
1249 | 1010 | 471.5 | 188.6 | 220.4625 | 279.6 | 280.9 | 272.7 | 260.3 | 483 | 46.9 | 19.3 | 84 | 5.3 | 214.9 | 12.5 | 350.3 | 700.1 | 833.2 | 388.4 | 433 | 820.8 | 509.4 | 531.4 | 723.5 | 212.8 | 251 | 687.5 | 81.6 | 141.2 | 195 | 315.4 | 471.8 | 537.2 | 302.4 | 461.8 | 131.4 | 296.3 | 279.5 | 164.7 | 220.2 | 249.5 | 179
1250 | 1011 | 472.1 | 188.84 | 220.7431 | 279.5 | 280.3 | 273.5 | 260.2 | 490.2 | 47 | 19.3 | 84 | 5.2 | 216.5 | 12.5 | 350.8 | 701.7 | 822.9 | 388.9 | 433.1 | 818.9 | 510.2 | 531.8 | 720.5 | 213.1 | 251.4 | 686 | 81.7 | 141.3 | 195.3 | 315.9 | 474.2 | 545.2 | 303.2 | 463.6 | 131.5 | 296.2 | 279.8 | 164.8 | 220.3 | 249.9 | 179.2
1251 | 1012 | 472.6 | 189.04 | 220.9769 | 279.1 | 280.6 | 274.4 | 260.4 | 490.4 | 47 | 19.3 | 84 | 5.3 | 220.2 | 11.7 | 351.1 | 707.7 | 822.8 | 389.3 | 433.2 | 817 | 511 | 531 | 724.8 | 213.4 | 251.8 | 685.6 | 81.8 | 141.5 | 195.5 | 316.4 | 473.8 | 544.7 | 303.6 | 462.9 | 131.6 | 296.4 | 279.3 | 165 | 220.5 | 250.3 | 179.4
1252 | 1013 | 472.6 | 189.04 | 220.9769 | 278.2 | 280.3 | 275.8 | 260.5 | 489 | 47 | 19.3 | 84.2 | 4.3 | 211.9 | 10.6 | 351.5 | 706.7 | 828.7 | 389.8 | 433.4 | 815.5 | 511.8 | 530.2 | 725.6 | 213.7 | 252.2 | 685.7 | 81.9 | 141.7 | 195.6 | 316.9 | 474.6 | 545.9 | 304.2 | 463.5 | 131.7 | 296.4 | 279 | 165.3 | 220.7 | 250.7 | 179.7
1253 | 1014 | 472.4 | 188.96 | 220.8834 | 278.1 | 280.5 | 277 | 260.7 | 492.1 | 47 | 19.3 | 84.3 | 4.5 | 255.4 | 9.3 | 351.9 | 706.4 | 827.2 | 390.2 | 433.7 | 814.1 | 512.7 | 530.8 | 726.2 | 214 | 252.7 | 685.3 | 81.9 | 141.9 | 196.1 | 317.4 | 475.6 | 543.5 | 304.7 | 463.3 | 131.8 | 296.4 | 279.4 | 165.5 | 220.9 | 251.1 | 179.9
1254 | 1015 | 472.8 | 189.12 | 221.0704 | 278.1 | 281.6 | 277.4 | 260.8 | 493.4 | 47.1 | 19.3 | 84.4 | 5 | 244.7 | 8 | 352.4 | 709.4 | 826.8 | 390.8 | 433.9 | 813 | 513.5 | 532.5 | 730.7 | 214.2 | 253.1 | 685.1 | 82 | 142.1 | 196.4 | 317.9 | 476.7 | 549 | 305.3 | 463.7 | 132 | 296.4 | 279.5 | 165.6 | 221.1 | 251.5 | 180.1
1255 | 1016 | 472.5 | 189 | 220.9301 | 277.9 | 282 | 278.3 | 260.9 | 494.3 | 47.2 | 19.3 | 84.4 | 4.9 | 233.4 | 7.2 | 352.7 | 715.9 | 831.4 | 391.1 | 434.1 | 812.6 | 514.3 | 533.2 | 727.6 | 214.5 | 253.5 | 684.4 | 82.1 | 142.2 | 196.6 | 318.4 | 477.5 | 548.4 | 305.8 | 464.1 | 132.1 | 296.5 | 279.5 | 165.8 | 221.4 | 251.9 | 180.4
1256 | 1017 | 474.3 | 189.72 | 221.7717 | 277.5 | 281.7 | 279 | 261.2 | 492 | 47.3 | 19.3 | 84.5 | 4.5 | 244.8 | 8.9 | 352.9 | 720.6 | 829.7 | 391.4 | 434.3 | 812.1 | 515.2 | 532.9 | 732.3 | 214.8 | 253.9 | 685.1 | 82.2 | 142.4 | 196.8 | 318.9 | 477 | 543.1 | 306.4 | 463.4 | 132.2 | 296.3 | 279.6 | 166 | 221.6 | 252.1 | 180.6
1257 | 1018 | 476.6 | 190.64 | 222.8472 | 277.5 | 281.6 | 279.1 | 261.3 | 491 | 47.4 | 19.3 | 84.5 | 4.2 | 226.4 | 9.2 | 353.2 | 717 | 831.6 | 391.5 | 434.6 | 812 | 516 | 532.6 | 731.5 | 215.1 | 254.4 | 684.5 | 82.3 | 142.6 | 197 | 319.3 | 476.5 | 543.3 | 306.8 | 463.5 | 132.3 | 296.2 | 279.2 | 166.2 | 221.7 | 252.6 | 180.8
1258 | 1019 | 476.5 | 190.6 | 222.8004 | 277.2 | 281.6 | 279.3 | 261.3 | 493.1 | 47.4 | 19.3 | 84.6 | 4.4 | 243.4 | 9 | 353.5 | 714.7 | 833.8 | 391.9 | 434.9 | 811.4 | 516.9 | 533.5 | 731.5 | 215.4 | 254.8 | 685.3 | 82.4 | 142.8 | 197.2 | 319.8 | 478.1 | 545.8 | 307.3 | 465 | 132.4 | 296.5 | 279.4 | 166.4 | 221.9 | 252.9 | 181
1259 | 1020 | 476.4 | 190.56 | 222.7537 | 276.9 | 281.6 | 279.6 | 261.6 | 490.5 | 47.5 | 19.3 | 84.7 | 4 | 262.5 | 9 | 353.8 | 713.9 | 825.4 | 392.4 | 435.2 | 810.8 | 517.8 | 533.3 | 728.4 | 215.7 | 255.2 | 685.4 | 82.4 | 143 | 197.2 | 320.3 | 477.5 | 538.3 | 307.6 | 465.5 | 132.6 | 296.7 | 279.7 | 166.8 | 222.1 | 253.3 | 181.3
1260 | 1021 | 475.5 | 190.2 | 222.3328 | 278.1 | 282.7 | 279.2 | 261.9 | 485.3 | 47.5 | 19.3 | 84.9 | 4.9 | 265.8 | 8.4 | 354.1 | 713.2 | 827 | 392.8 | 435.5 | 810.9 | 518.7 | 532.7 | 719.4 | 216 | 255.6 | 683.9 | 82.5 | 143.2 | 197.4 | 320.8 | 476.3 | 534.3 | 308 | 464.2 | 132.7 | 296.9 | 280 | 167 | 222.3 | 253.7 | 181.5
1261 | 1022 | 474.6 | 189.84 | 221.912 | 279.3 | 286.6 | 278.2 | 262.1 | 484.3 | 47.5 | 19.3 | 85 | 5.2 | 254 | 7.6 | 354.4 | 706.9 | 827.6 | 393.1 | 435.7 | 811.4 | 519.7 | 533.3 | 711.5 | 216.3 | 256.1 | 683.5 | 82.6 | 143.4 | 197.6 | 321.3 | 475.2 | 532.4 | 308.5 | 464.1 | 132.8 | 297 | 280 | 167.3 | 222.5 | 254.1 | 181.8
1262 | 1023 | 474.4 | 189.76 | 221.8185 | 279.7 | 288.1 | 277.1 | 262.1 | 482.7 | 47.6 | 19.3 | 85.1 | 5.8 | 246.3 | 7.4 | 354.6 | 715.9 | 807.3 | 393.4 | 436 | 811.9 | 520.6 | 533.1 | 704.7 | 216.6 | 256.5 | 683.3 | 82.7 | 143.5 | 197.8 | 321.8 | 474.5 | 527.7 | 308.8 | 463.8 | 133 | 297.2 | 280.6 | 167.5 | 222.7 | 254.5 | 182
1263 | 1024 | 473.5 | 189.4 | 221.3977 | 279.5 | 287.7 | 276.5 | 262.2 | 477.4 | 47.6 | 19.3 | 85.1 | 5.5 | 243.4 | 6.6 | 354.8 | 718.9 | 798.9 | 393.7 | 436.3 | 813.2 | 521.5 | 534.6 | 694 | 216.9 | 256.9 | 683.5 | 82.8 | 143.7 | 197.8 | 322.3 | 472.2 | 524.7 | 308.9 | 462.3 | 133.1 | 297.7 | 281.4 | 167.7 | 223.1 | 254.8 | 182.3
1264 | 1025 | 471.7 | 188.68 | 220.556 | 279.8 | 286.7 | 276.4 | 261.9 | 471.4 | 47.6 | 19.3 | 85.1 | 5.5 | 228.5 | 5.9 | 354.9 | 720.1 | 776.5 | 394 | 436.6 | 813.1 | 522.5 | 540.7 | 682.7 | 217.2 | 257.4 | 682.5 | 82.9 | 144 | 198 | 322.8 | 471.1 | 525.9 | 309 | 464.2 | 133.3 | 298.2 | 281.9 | 168 | 223.5 | 255.2 | 182.5
1265 | 1026 | 473.6 | 189.44 | 221.4444 | 282.3 | 286 | 275.9 | 262.1 | 469.4 | 47.7 | 19.3 | 85.2 | 5.2 | 206.8 | 4.9 | 355.1 | 720.6 | 772.9 | 394.2 | 436.8 | 812.4 | 523.4 | 552.7 | 672.2 | 217.5 | 257.8 | 680.9 | 83 | 144.2 | 198.3 | 323.3 | 471.3 | 527.6 | 309.2 | 467 | 133.4 | 299.3 | 282.7 | 168.4 | 223.8 | 255.5 | 182.8
1266 | 1027 | 474 | 189.6 | 221.6315 | 283.7 | 284.3 | 275.4 | 262.7 | 467.5 | 47.7 | 19.3 | 85.2 | 5 | 237.4 | 5 | 355.2 | 715.7 | 762.4 | 394.3 | 437.2 | 812.3 | 524.5 | 557 | 670.4 | 217.8 | 258.3 | 680.1 | 83.1 | 144.4 | 198.4 | 323.8 | 470.9 | 521.6 | 309.6 | 466.7 | 133.6 | 299.6 | 283.3 | 168.7 | 224 | 255.9 | 183.1
1267 | 1028 | 474 | 189.6 | 221.6315 | 283.5 | 283.2 | 274.8 | 263.4 | 465.2 | 47.6 | 19.3 | 85.2 | 4 | 256.8 | 5.5 | 355.3 | 716.5 | 772.3 | 394.5 | 437.4 | 812.3 | 525.6 | 556.1 | 683.5 | 218.1 | 258.8 | 680.8 | 83.2 | 144.6 | 198.6 | 324.3 | 471 | 530.1 | 310.1 | 467.7 | 133.7 | 300 | 283.2 | 168.9 | 224 | 256.2 | 183.4
1268 | 1029 | 474 | 189.6 | 221.6315 | 283.8 | 283.3 | 274.8 | 263.6 | 471 | 47.6 | 19.3 | 85.2 | 4 | 233.4 | 6.7 | 355.6 | 706.6 | 768.6 | 394.9 | 437.8 | 812.1 | 526.7 | 555.7 | 689.2 | 218.4 | 259.2 | 681.7 | 83.3 | 144.8 | 199.1 | 324.7 | 474 | 540.5 | 310.9 | 471.1 | 133.9 | 300.1 | 283 | 169.1 | 224.1 | 256.5 | 183.7
1269 | 1030 | 474.3 | 189.72 | 221.7717 | 285.3 | 283.1 | 275.5 | 263.7 | 477.2 | 47.6 | 19.3 | 85.2 | 4.9 | 233.8 | 9.6 | 355.8 | 699.3 | 771.6 | 395.2 | 438.1 | 811.9 | 527.7 | 559.3 | 691.1 | 218.7 | 259.7 | 682.1 | 83.4 | 145 | 199.6 | 325.2 | 474.6 | 543.9 | 311.5 | 471.9 | 134.1 | 300 | 282.8 | 169.3 | 224.2 | 256.9 | 183.9
1270 | 1031 | 473.7 | 189.48 | 221.4912 | 285.5 | 283 | 276.1 | 263.3 | 480.2 | 47.6 | 19.3 | 85.2 | 5.4 | 237.8 | 9.5 | 355.8 | 699.2 | 777 | 395.3 | 438.3 | 812.6 | 528.8 | 562.3 | 701.4 | 218.9 | 260.1 | 683.3 | 83.5 | 145.1 | 199.6 | 325.8 | 476.4 | 548.2 | 312.2 | 473.1 | 134.2 | 299.9 | 282.9 | 169.5 | 224.4 | 257.3 | 184.1
1271 | 1032 | 473.9 | 189.56 | 221.5847 | 286.1 | 282.4 | 276.6 | 262.9 | 484.6 | 47.7 | 19.3 | 85.2 | 4.7 | 244.7 | 8.8 | 356 | 699.5 | 777.2 | 395.6 | 438.5 | 813.9 | 529.9 | 560.5 | 710.8 | 219.2 | 260.6 | 685.4 | 83.6 | 145.3 | 199.8 | 326.2 | 479.4 | 550.1 | 312.8 | 472.8 | 134.4 | 299.5 | 283.3 | 169.6 | 224.6 | 257.7 | 184.4
1272 | 1033 | 473.8 | 189.52 | 221.538 | 286.1 | 281.9 | 276.1 | 263.1 | 487 | 47.7 | 19.3 | 85.3 | 4.6 | 233.8 | 8.4 | 356.1 | 707.7 | 780.6 | 395.8 | 438.8 | 814.9 | 531.1 | 561.7 | 712.2 | 219.5 | 261 | 686.9 | 83.6 | 145.5 | 200 | 326.7 | 481.1 | 547 | 313.3 | 471.8 | 134.6 | 299.2 | 282.8 | 169.8 | 224.8 | 258.1 | 184.6
1273 | 1034 | 473.6 | 189.44 | 221.4444 | 285.9 | 281.9 | 275.6 | 262.9 | 487 | 47.8 | 19.3 | 85.3 | 5.5 | 246.7 | 7.6 | 356.3 | 708.5 | 790.8 | 396.2 | 439 | 815.9 | 532.2 | 564.8 | 713.9 | 219.8 | 261.4 | 687.7 | 83.7 | 145.7 | 200.2 | 327.2 | 482.2 | 550.6 | 314 | 473.2 | 134.7 | 299.1 | 282.6 | 170 | 225 | 258.4 | 184.8
1274 | 1035 | 473.3 | 189.32 | 221.3042 | 285.3 | 282.1 | 275.6 | 262.8 | 487.2 | 47.9 | 19.3 | 85.3 | 5.5 | 249.9 | 7.7 | 356.4 | 716.5 | 797.4 | 396.5 | 439.2 | 815.9 | 533.2 | 564.9 | 709.2 | 220.1 | 261.9 | 688.2 | 83.8 | 145.9 | 200.4 | 327.7 | 484.5 | 546.2 | 314.3 | 474.1 | 134.9 | 299.5 | 283.1 | 170.3 | 225.3 | 258.8 | 185
1275 | 1036 | 474.7 | 189.88 | 221.9588 | 286.2 | 281.7 | 276.2 | 263.1 | 485 | 48 | 19.2 | 85.3 | 5.9 | 262.6 | 7.6 | 356.7 | 713.2 | 792.2 | 397 | 439.5 | 815.1 | 534.3 | 565.4 | 705.3 | 220.4 | 262.3 | 687.9 | 83.9 | 146.1 | 200.4 | 328.2 | 484.8 | 540.6 | 314.7 | 473.5 | 135.1 | 300.5 | 283.7 | 170.7 | 225.7 | 259.2 | 185.3
1276 | 1037 | 475.7 | 190.28 | 222.4264 | 286 | 281.2 | 276 | 264.1 | 482.6 | 48 | 19.2 | 85.4 | 5.9 | 261.3 | 8.7 | 357 | 709 | 793.2 | 397.4 | 439.7 | 814.4 | 535.4 | 563.4 | 703.3 | 220.7 | 262.7 | 688 | 84 | 146.3 | 200.5 | 328.7 | 484.3 | 535.2 | 315 | 472.6 | 135.2 | 301.4 | 284.2 | 171 | 225.9 | 259.6 | 185.6
1277 | 1038 | 476.9 | 190.76 | 222.9874 | 285.3 | 281.9 | 275.4 | 265 | 481.3 | 48.1 | 19.2 | 85.4 | 6 | 242.2 | 9.5 | 357.2 | 705 | 798.8 | 397.7 | 440 | 814.6 | 536.5 | 562.6 | 702.3 | 221 | 263.1 | 686.6 | 84.1 | 146.5 | 200.8 | 329.2 | 486.5 | 534.8 | 315.4 | 474.3 | 135.4 | 302.1 | 284.9 | 171.5 | 226.2 | 260 | 185.9
1278 | 1039 | 475.4 | 190.16 | 222.2861 | 285 | 282.6 | 275.3 | 265.6 | 481.3 | 48.1 | 19.2 | 85.4 | 6.6 | 255.7 | 9.4 | 357.5 | 703.8 | 802.5 | 398.2 | 440.2 | 814.3 | 537.5 | 562.2 | 706.3 | 221.3 | 263.6 | 687.2 | 84.1 | 146.6 | 201 | 329.7 | 487.5 | 536.8 | 315.9 | 476.4 | 135.6 | 302.7 | 285.5 | 171.8 | 226.4 | 260.4 | 186.2
1279 | 1040 | 474.2 | 189.68 | 221.725 | 284.9 | 282.8 | 275.1 | 266.1 | 481.7 | 48.1 | 19.2 | 85.5 | 6.1 | 235.9 | 9 | 357.7 | 699.4 | 800.6 | 398.6 | 440.5 | 813.4 | 538.6 | 560.6 | 712 | 221.6 | 264 | 687.2 | 84.2 | 146.8 | 201.1 | 330.2 | 488.2 | 543.3 | 316.5 | 477.2 | 135.7 | 303 | 285.8 | 172.1 | 226.6 | 260.8 | 186.4
1280 | 1041 | 473.3 | 189.32 | 221.3042 | 285.4 | 285.4 | 274.9 | 266.2 | 483.4 | 48.1 | 19.2 | 85.6 | 6 | 248.5 | 9.3 | 358 | 703.1 | 803.9 | 399.1 | 440.7 | 812.9 | 539.7 | 559 | 710 | 221.9 | 264.5 | 687.9 | 84.3 | 147 | 201.3 | 330.7 | 489.1 | 540.7 | 316.9 | 477.7 | 135.9 | 302.8 | 286.3 | 172.3 | 226.8 | 261.2 | 186.7
1281 | 1042 | 472.3 | 188.92 | 220.8366 | 285.8 | 289.1 | 274.6 | 266 | 484.3 | 48.1 | 19.2 | 85.6 | 6.4 | 236.8 | 10.5 | 358 | 702.1 | 815.5 | 399.3 | 441 | 812.9 | 540.8 | 559.2 | 706.7 | 222.2 | 265 | 687.1 | 84.4 | 147.2 | 201.6 | 331.2 | 489.9 | 540.4 | 317.5 | 478.2 | 136.1 | 302.2 | 286.4 | 172.4 | 227 | 261.6 | 186.9
1282 | 1043 | 474.8 | 189.92 | 222.0055 | 286.9 | 290.7 | 275.1 | 265.8 | 483.3 | 48.2 | 19.2 | 85.8 | 5.9 | 259.3 | 9.2 | 358.1 | 698.9 | 814.8 | 399.7 | 441.2 | 813.1 | 541.9 | 558.8 | 708.5 | 222.5 | 265.4 | 687.9 | 84.5 | 147.3 | 201.9 | 331.7 | 488.9 | 536.3 | 317.9 | 477.3 | 136.3 | 302 | 286.3 | 172.6 | 227.3 | 262 | 187.1
1283 | 1044 | 474.6 | 189.84 | 221.912 | 287.5 | 292.5 | 275.7 | 265.4 | 481.7 | 48.2 | 19.2 | 86 | 5.9 | 226 | 7.6 | 358.1 | 696.8 | 815.5 | 399.9 | 441.4 | 813.2 | 543.1 | 558.8 | 717.2 | 222.8 | 265.9 | 688.8 | 84.5 | 147.4 | 202.4 | 332.2 | 487.4 | 539.8 | 318.6 | 475.9 | 136.5 | 302 | 286 | 172.8 | 227.3 | 262.4 | 187.3
1284 | 1045 | 474.4 | 189.76 | 221.8185 | 287.2 | 295.2 | 276.7 | 265.2 | 487.7 | 48.2 | 19.2 | 86.1 | 6.1 | 252.3 | 7.2 | 358.3 | 696.3 | 807.8 | 400.4 | 441.6 | 812.4 | 544.2 | 561.9 | 724.8 | 223.1 | 266.3 | 689.8 | 84.6 | 147.6 | 202.9 | 332.6 | 490.2 | 555.1 | 319.7 | 478.1 | 136.6 | 301.9 | 285.7 | 173 | 227.4 | 262.8 | 187.6
1285 | 1046 | 473 | 189.2 | 221.1639 | 287 | 294.7 | 278.4 | 265.3 | 499.2 | 48.2 | 19.2 | 86.2 | 6.2 | 228.1 | 8.6 | 358.6 | 702.7 | 815.5 | 401 | 441.8 | 810.8 | 545.3 | 567.1 | 724.1 | 223.4 | 266.8 | 689.5 | 84.7 | 147.8 | 203.4 | 333.1 | 493.6 | 572.8 | 320.5 | 483.5 | 136.8 | 302 | 285.5 | 173.2 | 227.5 | 263.2 | 187.8
1286 | 1047 | 473.9 | 189.56 | 221.5847 | 286.7 | 293.5 | 278.9 | 265.1 | 505.7 | 48.3 | 19.2 | 86.3 | 6.1 | 241.8 | 8.6 | 358.7 | 719.6 | 830.5 | 401.4 | 442 | 811 | 546.4 | 572.6 | 727.8 | 223.7 | 267.3 | 689.1 | 84.8 | 148 | 203.4 | 333.6 | 496.7 | 587.7 | 321.4 | 487.1 | 137 | 302 | 285.2 | 173.4 | 227.6 | 263.6 | 188
1287 | 1048 | 472.7 | 189.08 | 221.0236 | 286.1 | 293.4 | 279.6 | 265.2 | 507.7 | 48.4 | 19.2 | 86.4 | 5.3 | 234.3 | 7 | 358.9 | 710.5 | 835.2 | 401.9 | 442.2 | 811.5 | 547.6 | 571.9 | 727.9 | 224 | 267.8 | 689 | 84.8 | 148.1 | 203.6 | 334.1 | 499.6 | 590.7 | 322.3 | 487.9 | 137.2 | 302.1 | 284.9 | 173.5 | 227.7 | 264.1 | 188.3
1288 | 1049 | 472.4 | 188.96 | 220.8834 | 284.2 | 294 | 280.6 | 265.7 | 512.4 | 48.6 | 19.2 | 86.4 | 5.7 | 259.6 | 7.9 | 359.1 | 705.9 | 829.9 | 402.3 | 442.5 | 811.6 | 548.7 | 571.1 | 726.5 | 224.3 | 268.3 | 688 | 84.9 | 148.3 | 204.3 | 334.6 | 501.4 | 599 | 323.3 | 489.2 | 137.3 | 302.4 | 285.1 | 173.6 | 227.8 | 264.3 | 188.4
1289 | 1050 | 472.8 | 189.12 | 221.0704 | 284.5 | 293.1 | 280.6 | 265.4 | 515.8 | 48.6 | 19.2 | 86.5 | 4.8 | 244.6 | 10.4 | 359.1 | 705.4 | 827.5 | 402.7 | 442.7 | 812 | 549.8 | 570.4 | 724.6 | 224.6 | 268.8 | 688.5 | 85 | 148.5 | 204.6 | 335.1 | 500.4 | 599.6 | 323.9 | 488.3 | 137.5 | 302.8 | 285.1 | 173.9 | 227.9 | 264.9 | 188.8
1290 | 1051 | 472.9 | 189.16 | 221.1171 | 284.2 | 291.8 | 281.6 | 265.4 | 521.4 | 48.6 | 19.2 | 86.5 | 4 | 243.7 | 11.9 | 359.2 | 704.8 | 820.7 | 403 | 443 | 812.9 | 550.9 | 571.9 | 726.8 | 224.9 | 269.3 | 689.4 | 85.1 | 148.7 | 204.6 | 335.6 | 505.1 | 609 | 324.9 | 490 | 137.7 | 303.2 | 285 | 174.1 | 228.2 | 265.3 | 189
1291 | 1052 | 473.3 | 189.32 | 221.3042 | 284.2 | 290.8 | 282.4 | 265.7 | 525.7 | 48.7 | 19.2 | 86.5 | 4.7 | 243.9 | 12.9 | 359.3 | 702.6 | 819.3 | 403.4 | 443.3 | 813.2 | 551.9 | 573.5 | 724.5 | 225.2 | 269.7 | 689.5 | 85.1 | 148.9 | 204.9 | 336.1 | 508.8 | 618.4 | 325.8 | 493.5 | 137.8 | 303.4 | 285 | 174.4 | 228.3 | 265.7 | 189.3
1292 | 1053 | 473.1 | 189.24 | 221.2107 | 284.9 | 290.5 | 282.9 | 265.9 | 530.1 | 48.7 | 19.2 | 86.5 | 5.6 | 263.1 | 12.9 | 359.5 | 710.1 | 806.8 | 403.9 | 443.7 | 812.7 | 553.1 | 575 | 724.5 | 225.5 | 270.3 | 690.6 | 85.2 | 149 | 205.2 | 336.7 | 512.4 | 623.5 | 326.9 | 494.6 | 138 | 303.9 | 285 | 174.6 | 228.6 | 266.2 | 189.5
1293 | 1054 | 473.7 | 189.48 | 221.4912 | 285.2 | 290.6 | 283.7 | 266.6 | 529 | 48.7 | 19.2 | 86.5 | 6 | 263.3 | 15.3 | 359.8 | 707.6 | 797.5 | 404.5 | 444.1 | 811.9 | 554.1 | 575.1 | 719.4 | 225.9 | 270.8 | 691 | 85.3 | 149.2 | 205.3 | 337.3 | 511.8 | 618.5 | 327.5 | 494.8 | 138.1 | 304.2 | 285.5 | 174.7 | 228.8 | 266.7 | 189.8
1294 | 1055 | 472.5 | 189 | 220.9301 | 285.5 | 293 | 284 | 266.9 | 527.2 | 48.8 | 19.2 | 86.5 | 5.6 | 254.8 | 16.4 | 360.2 | 705.5 | 796.6 | 405.1 | 444.6 | 811.3 | 555.2 | 575.8 | 712.6 | 226.2 | 271.3 | 690.8 | 85.4 | 149.4 | 205.4 | 337.9 | 515.2 | 622.9 | 328.2 | 496.7 | 138.3 | 304.8 | 286.2 | 175 | 229.1 | 267.1 | 190
1295 | 1056 | 473.3 | 189.32 | 221.3042 | 287.4 | 295.1 | 284.1 | 267.3 | 524.1 | 48.8 | 19.2 | 86.6 | 5.6 | 262.3 | 13.9 | 360.3 | 702.2 | 798.4 | 405.4 | 444.9 | 811.2 | 556.3 | 576.6 | 709.8 | 226.6 | 271.8 | 689.9 | 85.5 | 149.6 | 205.5 | 338.4 | 516.6 | 614.6 | 329 | 496.5 | 138.5 | 305.5 | 287 | 175.3 | 229.4 | 267.6 | 190.3
1296 | 1057 | 473.1 | 189.24 | 221.2107 | 288.4 | 297.1 | 284.1 | 267.8 | 521.6 | 48.9 | 19.2 | 86.8 | 5.2 | 260.3 | 13.3 | 360.3 | 702.9 | 798.1 | 405.7 | 445.1 | 810.8 | 557.4 | 576.8 | 705.8 | 226.9 | 272.3 | 689.5 | 85.5 | 149.8 | 205.7 | 339.1 | 515.8 | 604.7 | 329.7 | 494.6 | 138.6 | 306.9 | 287.5 | 175.5 | 229.7 | 268.1 | 190.6
1297 | 1058 | 473 | 189.2 | 221.1639 | 289.4 | 297 | 284 | 268.2 | 516.3 | 49 | 19.2 | 87 | 6.5 | 255.1 | 16.2 | 360.3 | 703.9 | 790.8 | 405.9 | 445.4 | 811.2 | 558.5 | 577.1 | 703.8 | 227.2 | 272.8 | 689.6 | 85.6 | 150 | 205.9 | 339.6 | 514.7 | 593.3 | 330.4 | 493.5 | 138.8 | 307.3 | 288.3 | 175.9 | 230 | 268.5 | 190.8
1298 | 1059 | 472.3 | 188.92 | 220.8366 | 289.9 | 296.5 | 283.7 | 268.3 | 508.2 | 49.1 | 19.2 | 87.1 | 7 | 264.2 | 18.3 | 360.4 | 709.4 | 800 | 406.2 | 445.5 | 811.3 | 559.6 | 574.9 | 698.8 | 227.5 | 273.4 | 688.8 | 85.7 | 150.2 | 206 | 340.2 | 510.7 | 578.4 | 330.9 | 490.9 | 138.9 | 307.5 | 288.6 | 176.1 | 230.3 | 268.9 | 191.1
1299 | 1060 | 471.6 | 188.64 | 220.5093 | 289.7 | 295.3 | 282.9 | 268.4 | 501.2 | 49.2 | 19.2 | 87.2 | 7.5 | 250.9 | 18.7 | 360.5 | 709.9 | 804.8 | 406.6 | 445.7 | 811.2 | 560.7 | 574.5 | 700.2 | 227.9 | 273.8 | 688.5 | 85.8 | 150.4 | 206.2 | 340.8 | 509 | 575.7 | 331.5 | 491.4 | 139.1 | 307.5 | 289.1 | 176.4 | 230.7 | 269.2 | 191.4
1300 | 1061 | 472.4 | 188.96 | 220.8834 | 289.4 | 295.5 | 282.3 | 268.4 | 500.6 | 49.2 | 19.2 | 87.3 | 6.6 | 241.1 | 18.5 | 360.6 | 714.9 | 795.1 | 407 | 446.1 | 810.4 | 561.7 | 574.1 | 696.7 | 228.2 | 274.3 | 688.6 | 85.9 | 150.6 | 206.4 | 341.3 | 511.7 | 575 | 332.2 | 493.7 | 139.3 | 307.7 | 289.4 | 176.8 | 231 | 269.6 | 191.6
1301 | 1062 | 473 | 189.2 | 221.1639 | 288.7 | 295.3 | 282.1 | 268.6 | 500.6 | 49.3 | 19.2 | 87.4 | 6.5 | 247.1 | 15.2 | 360.7 | 712.8 | 788.7 | 407.5 | 446.3 | 808.7 | 562.8 | 572.4 | 685.8 | 228.5 | 274.8 | 687.3 | 86 | 150.8 | 206.5 | 341.8 | 514.7 | 568.3 | 332.7 | 494.9 | 139.5 | 308.1 | 290.1 | 177.2 | 231.3 | 270 | 191.8
1302 | 1063 | 472.2 | 188.88 | 220.7898 | 288.5 | 295.1 | 281.7 | 269.1 | 501.4 | 49.3 | 19.2 | 87.5 | 7.1 | 251.2 | 13.6 | 360.7 | 720.9 | 793.1 | 407.8 | 446.5 | 808.3 | 563.9 | 573.1 | 683.1 | 228.8 | 275.3 | 687.1 | 86.1 | 151 | 206.7 | 342.4 | 518.1 | 585 | 333.6 | 497.4 | 139.7 | 308 | 290.4 | 177.6 | 231.7 | 270.5 | 192.1
1303 | 1064 | 473 | 189.2 | 221.1639 | 287.9 | 295.1 | 281.4 | 269.5 | 505.1 | 49.3 | 19.2 | 87.6 | 6.1 | 268.7 | 11 | 360.9 | 729.1 | 794.9 | 408.3 | 446.7 | 808.7 | 565.1 | 578.8 | 682.5 | 229.1 | 275.8 | 687.1 | 86.1 | 151.1 | 207 | 342.9 | 520.6 | 585.4 | 334.4 | 500.6 | 139.9 | 308.1 | 290.9 | 177.8 | 231.8 | 271 | 192.3
1304 | 1065 | 471.8 | 188.72 | 220.6028 | 287.6 | 295.6 | 281.6 | 269.9 | 507 | 49.3 | 19.2 | 87.7 | 5.4 | 250.8 | 9.6 | 361 | 724.3 | 798.4 | 408.6 | 446.9 | 809.5 | 566.1 | 578.1 | 690.1 | 229.4 | 276.3 | 686.7 | 86.2 | 151.3 | 207.3 | 343.5 | 520.3 | 587.8 | 335.3 | 500.2 | 140 | 307.9 | 291.6 | 178.2 | 232 | 271.5 | 192.6
1305 | 1066 | 472.2 | 188.88 | 220.7898 | 288.8 | 296 | 281.6 | 270.5 | 506.1 | 49.3 | 19.2 | 87.7 | 4.9 | 242.7 | 9.7 | 361.1 | 729.3 | 793.6 | 409 | 447.2 | 808.9 | 567.2 | 575.6 | 694.5 | 229.8 | 276.7 | 686.9 | 86.3 | 151.5 | 207.5 | 344 | 519.7 | 581.4 | 336.1 | 499.1 | 140.2 | 307.8 | 291.9 | 178.4 | 232.3 | 271.9 | 192.8
1306 | 1067 | 472.9 | 189.16 | 221.1171 | 289.2 | 297.1 | 282.1 | 270.5 | 503.5 | 49.3 | 19.2 | 87.7 | 4.8 | 234.8 | 8.7 | 361.3 | 731.8 | 797.4 | 409.5 | 447.5 | 808 | 568.2 | 573.4 | 692 | 230.1 | 277.1 | 684.9 | 86.4 | 151.6 | 207.6 | 344.5 | 517.7 | 575.9 | 336.8 | 498.3 | 140.4 | 308 | 291.7 | 178.8 | 232.4 | 272.4 | 193.1
1307 | 1068 | 472 | 188.8 | 220.6963 | 289.3 | 298.6 | 282.5 | 270 | 503.7 | 49.3 | 19.2 | 87.7 | 5.5 | 229 | 8.1 | 361.4 | 733.5 | 800.4 | 409.8 | 447.4 | 808.1 | 569.2 | 572.3 | 696.7 | 230.5 | 277.5 | 684.3 | 86.5 | 151.8 | 208 | 345 | 515.9 | 577.2 | 337.6 | 499 | 140.6 | 307.7 | 291.7 | 179 | 232.6 | 272.8 | 193.3
1308 | 1069 | 471.7 | 188.68 | 220.556 | 289.8 | 300.1 | 282.5 | 269.8 | 505.7 | 49.4 | 19.2 | 87.7 | 5.2 | 241.7 | 8.6 | 361.4 | 727.3 | 813.5 | 409.9 | 447.3 | 809 | 570.3 | 570.1 | 704.8 | 230.8 | 277.8 | 685.2 | 86.6 | 152 | 208.3 | 345.6 | 515.5 | 584.8 | 338.9 | 501 | 140.9 | 307.6 | 291.6 | 179.1 | 232.7 | 273.2 | 193.5
1309 | 1070 | 472.8 | 189.12 | 221.0704 | 289.1 | 300.8 | 283 | 269.4 | 508.9 | 49.4 | 19.2 | 87.8 | 4.6 | 247.4 | 8.9 | 361.5 | 718.4 | 818.5 | 410.1 | 447.6 | 809.8 | 571.3 | 567.9 | 707.9 | 231.2 | 278.2 | 685.7 | 86.6 | 152.2 | 208.5 | 346.2 | 516.7 | 586.2 | 339.9 | 502.6 | 141 | 307.5 | 291.1 | 179.3 | 232.8 | 273.6 | 193.7
1310 | 1071 | 472.2 | 188.88 | 220.7898 | 289 | 301.3 | 282.8 | 268.6 | 506.4 | 49.5 | 19.2 | 87.8 | 5.4 | 237.7 | 9 | 361.7 | 711.4 | 824.6 | 410.5 | 448 | 809.4 | 572.3 | 565.8 | 714.3 | 231.5 | 278.6 | 686.5 | 86.7 | 152.4 | 208.7 | 346.7 | 514.4 | 582 | 340.8 | 501.1 | 141.2 | 307.4 | 290.8 | 179.4 | 233 | 274.1 | 194
1311 | 1072 | 472 | 188.8 | 220.6963 | 289.1 | 301.4 | 283.3 | 268.5 | 507.6 | 49.6 | 19.2 | 87.9 | 5.1 | 247.6 | 9.4 | 361.9 | 710.8 | 828.5 | 410.8 | 448.3 | 809.4 | 573.3 | 566.4 | 718.6 | 231.9 | 279.1 | 687.5 | 86.8 | 152.6 | 209.2 | 347.3 | 515.2 | 593.2 | 341.9 | 504 | 141.4 | 307.3 | 290.8 | 179.5 | 233.1 | 274.5 | 194.2
1312 | 1073 | 472.4 | 188.96 | 220.8834 | 288.9 | 302 | 284.3 | 268.4 | 518 | 49.6 | 19.2 | 87.9 | 4.9 | 252.5 | 9.9 | 362 | 708.4 | 825 | 411 | 448.5 | 809.5 | 574.2 | 567.8 | 719.6 | 232.2 | 279.5 | 687.3 | 86.9 | 152.8 | 209.8 | 348 | 518.8 | 605.6 | 343.3 | 507.8 | 141.6 | 308.6 | 290.8 | 179.8 | 233.2 | 274.9 | 194.4
1313 | 1074 | 472.1 | 188.84 | 220.7431 | 288.5 | 300.9 | 284.7 | 268.3 | 526.9 | 49.7 | 19.1 | 87.9 | 5.1 | 242.6 | 10 | 362.1 | 704.6 | 817.3 | 411.2 | 448.9 | 809.5 | 575.2 | 571.6 | 723.1 | 232.5 | 279.9 | 688 | 87 | 153 | 210 | 348.6 | 522.5 | 616.7 | 345 | 512.5 | 141.8 | 308.4 | 290.9 | 179.9 | 233.3 | 275.4 | 194.7
1314 | 1075 | 471.7 | 188.68 | 220.556 | 288.3 | 299.5 | 284.7 | 268.5 | 533.6 | 49.7 | 19.2 | 88 | 5.2 | 257 | 9.4 | 362.2 | 700.8 | 803.3 | 411.4 | 449.3 | 809.7 | 576.2 | 574.8 | 721.8 | 232.9 | 280.3 | 688.7 | 87.1 | 153.2 | 210.4 | 349.2 | 524.3 | 629.3 | 346.6 | 514.9 | 142 | 308.5 | 290.7 | 180 | 233.4 | 275.9 | 194.9
1315 | 1076 | 472.4 | 188.96 | 220.8834 | 288.8 | 298.4 | 285.5 | 268.5 | 540 | 49.7 | 19.1 | 88 | 5.5 | 253.7 | 10.2 | 362.2 | 697.6 | 795.8 | 411.5 | 449.6 | 810.5 | 577.2 | 577.2 | 718.9 | 233.2 | 280.7 | 689.2 | 87.2 | 153.4 | 210.8 | 349.9 | 527.1 | 639.6 | 348.4 | 517.7 | 142.2 | 308.8 | 290.7 | 180.3 | 233.6 | 276.4 | 195.2
1316 | 1077 | 472.6 | 189.04 | 220.9769 | 289.2 | 297.8 | 286.4 | 268.3 | 542.7 | 49.7 | 19.1 | 88.1 | 6.1 | 248.4 | 8.8 | 362.3 | 701.3 | 788.9 | 411.7 | 450 | 811.8 | 578.2 | 581.1 | 723.6 | 233.5 | 281.2 | 690.2 | 87.2 | 153.6 | 210.9 | 350.5 | 532.9 | 641.1 | 349.6 | 521.3 | 142.3 | 309.2 | 290.7 | 180.5 | 233.7 | 276.8 | 195.4
1317 | 1078 | 472.7 | 189.08 | 221.0236 | 289.3 | 298.2 | 286.6 | 268.4 | 544.6 | 49.8 | 19.1 | 88.1 | 5.8 | 261.5 | 9.5 | 362.5 | 707.8 | 787 | 411.9 | 450.2 | 812.2 | 579.2 | 582.1 | 723.5 | 233.8 | 281.6 | 691.3 | 87.3 | 153.7 | 211 | 351.2 | 536.6 | 635.7 | 350.6 | 524.3 | 142.5 | 309.7 | 291.1 | 180.8 | 233.8 | 277.3 | 195.6
1318 | 1079 | 472.7 | 189.08 | 221.0236 | 289.3 | 298.2 | 287.2 | 268.8 | 544.1 | 49.8 | 19.1 | 88.1 | 5.5 | 260.2 | 9.7 | 362.5 | 711.1 | 787.7 | 412.1 | 450.3 | 812.1 | 580.2 | 583 | 723.4 | 234.1 | 282.1 | 692.5 | 87.4 | 153.9 | 211.4 | 351.9 | 537.3 | 633 | 351.9 | 522.8 | 142.7 | 310 | 291.5 | 181 | 234 | 277.8 | 195.9
1319 | 1080 | 472.8 | 189.12 | 221.0704 | 289 | 297.2 | 287.6 | 269.2 | 543.2 | 49.8 | 19.1 | 88 | 5.6 | 241.7 | 9 | 362.5 | 709.1 | 786.6 | 412.1 | 450.8 | 812.7 | 581.2 | 585 | 723.2 | 234.5 | 282.6 | 694.3 | 87.5 | 154.1 | 211.7 | 352.6 | 539.6 | 634.5 | 353.4 | 524 | 142.9 | 310.4 | 291.6 | 181.3 | 234.3 | 278.3 | 196.1
1320 | 1081 | 472.3 | 188.92 | 220.8366 | 289.1 | 297.6 | 288.1 | 269.5 | 542.9 | 49.9 | 19.1 | 88 | 5.3 | 256.3 | 9.6 | 362.6 | 707.5 | 786.4 | 412.4 | 451.3 | 813.6 | 582.3 | 585.5 | 725.6 | 234.8 | 283 | 695.9 | 87.6 | 154.3 | 211.9 | 353.2 | 543.8 | 636.1 | 354.7 | 527.1 | 143 | 310.8 | 292.2 | 181.6 | 234.5 | 278.7 | 196.4
1321 | 1082 | 473.9 | 189.56 | 221.5847 | 288.8 | 298.2 | 288.1 | 269.9 | 538.8 | 49.9 | 19.1 | 88.1 | 5.4 | 253.2 | 10.8 | 362.7 | 706.6 | 785.1 | 412.5 | 451.6 | 814.2 | 583.3 | 584.1 | 729 | 235.1 | 283.5 | 697.1 | 87.7 | 154.5 | 212 | 353.9 | 543.4 | 627.4 | 355.5 | 527.2 | 143.2 | 311 | 292.6 | 181.9 | 234.8 | 279.3 | 196.6
1322 | 1083 | 475.1 | 190.04 | 222.1458 | 289.6 | 297.8 | 288.3 | 270.6 | 532.3 | 50 | 19.1 | 88.1 | 5 | 242.1 | 10.3 | 362.7 | 703.8 | 779.7 | 412.6 | 451.9 | 814.4 | 584.4 | 581.8 | 723.9 | 235.4 | 284 | 698.4 | 87.8 | 154.7 | 212.1 | 354.6 | 540.1 | 614.1 | 356.1 | 523.5 | 143.4 | 311.5 | 293.2 | 182.1 | 235.1 | 279.8 | 196.9
1323 | 1084 | 473.5 | 189.4 | 221.3977 | 292.4 | 297.3 | 288.3 | 271.5 | 524.4 | 50 | 19.1 | 88.1 | 5.3 | 240.8 | 10.3 | 362.9 | 709 | 781.5 | 412.8 | 452.1 | 814.7 | 585.3 | 581.3 | 718.3 | 235.7 | 284.6 | 698.9 | 87.9 | 154.9 | 212.3 | 355.3 | 536.2 | 601.6 | 356.6 | 521.5 | 143.6 | 311.7 | 293.3 | 182.4 | 235.4 | 280.2 | 197.1
1324 | 1085 | 473.6 | 189.44 | 221.4444 | 294.9 | 296.9 | 288.3 | 272 | 518.6 | 50 | 19.1 | 88.1 | 5.4 | 244.9 | 12.3 | 363.1 | 713.2 | 785.8 | 413.2 | 452.3 | 814.8 | 586.3 | 580.7 | 714.4 | 236 | 285.1 | 698.5 | 87.9 | 155.1 | 212.5 | 355.9 | 533.4 | 595.4 | 357.2 | 520.1 | 143.8 | 313.5 | 293.4 | 182.7 | 235.6 | 280.6 | 197.4
1325 | 1086 | 472.4 | 188.96 | 220.8834 | 295.2 | 296.2 | 288.4 | 272.2 | 517.5 | 50 | 19.1 | 88.1 | 5.9 | 245.3 | 12.7 | 363.1 | 710.8 | 772.8 | 413.2 | 452.2 | 814.6 | 587.2 | 580.7 | 712.8 | 236.4 | 285.6 | 697.3 | 88 | 155.2 | 212.6 | 356.6 | 534.2 | 594.8 | 358.1 | 520.8 | 143.9 | 314.4 | 293.8 | 183.1 | 236 | 281 | 197.7
1326 | 1087 | 472.5 | 189 | 220.9301 | 295.3 | 295.6 | 287.7 | 272.9 | 516.3 | 50.1 | 19.1 | 88.2 | 6.2 | 252.3 | 12 | 363.2 | 716.7 | 762 | 413.2 | 452.6 | 814.1 | 588.1 | 581.9 | 706.9 | 236.7 | 286.1 | 696.3 | 88.1 | 155.3 | 212.8 | 357.2 | 534.8 | 590.1 | 358.9 | 520.5 | 144.1 | 315 | 294 | 183.5 | 236.3 | 281.4 | 198
1327 | 1088 | 472.2 | 188.88 | 220.7898 | 295.6 | 295.1 | 287.6 | 273.8 | 513.2 | 50.1 | 19.1 | 88.3 | 5.9 | 246.9 | 11.2 | 363.3 | 710.5 | 767.8 | 413.3 | 452.3 | 814.5 | 589.1 | 589.5 | 704.7 | 237.1 | 286.6 | 694.6 | 88.2 | 155.5 | 212.9 | 357.9 | 534.7 | 586.1 | 359.4 | 522.1 | 144.3 | 315.6 | 294.5 | 183.8 | 236.6 | 281.8 | 198.3
1328 | 1089 | 472.2 | 188.88 | 220.7898 | 296.4 | 294 | 287.8 | 274.8 | 510.7 | 50.1 | 19.1 | 88.4 | 6.1 | 249.9 | 10.9 | 363.3 | 709.6 | 778.1 | 413.4 | 452.3 | 814.6 | 590.1 | 593.3 | 705.5 | 237.5 | 287.1 | 694.7 | 88.3 | 155.7 | 213.3 | 358.5 | 535.3 | 591.4 | 360.3 | 525.7 | 144.5 | 315.8 | 295 | 184.2 | 236.8 | 282.3 | 198.5
1329 | 1090 | 473.6 | 189.44 | 221.4444 | 296.5 | 293.5 | 288 | 275.4 | 516.6 | 50.1 | 19.1 | 88.4 | 6.3 | 263.9 | 13.1 | 363.4 | 712.1 | 776.7 | 413.4 | 452.3 | 815.3 | 591.1 | 595 | 708.1 | 237.9 | 287.7 | 695.8 | 88.4 | 155.9 | 213.5 | 359.2 | 537.7 | 604.5 | 361.7 | 529.3 | 144.7 | 315.3 | 295 | 184.5 | 236.9 | 282.7 | 198.8
1330 | 1091 | 474.4 | 189.76 | 221.8185 | 296.7 | 293.9 | 288 | 275.5 | 519.9 | 50.1 | 19.1 | 88.5 | 5.7 | 248.1 | 13.7 | 363.6 | 712 | 785 | 413.6 | 452 | 815.3 | 592.1 | 594.6 | 709.8 | 238.2 | 288.3 | 696.7 | 88.5 | 156 | 213.8 | 359.9 | 537.7 | 611.4 | 362.9 | 530.2 | 144.9 | 314.9 | 294.8 | 184.7 | 237 | 283.1 | 199
1331 | 1092 | 472.9 | 189.16 | 221.1171 | 299 | 294.1 | 288 | 275.6 | 520.1 | 50.1 | 19.1 | 88.6 | 5.4 | 248.3 | 13.6 | 363.8 | 711.5 | 796 | 413.9 | 452.1 | 815.8 | 593 | 593.1 | 714.4 | 238.6 | 289 | 697.7 | 88.5 | 156.2 | 213.9 | 360.5 | 538.1 | 609.3 | 364.2 | 530 | 145.1 | 314.6 | 294.8 | 185 | 237.1 | 283.6 | 199.3
1332 | 1093 | 472.9 | 189.16 | 221.1171 | 299.9 | 293.7 | 288.4 | 275.5 | 518.7 | 50.2 | 19.1 | 88.8 | 5.6 | 245.8 | 14.3 | 363.9 | 709.8 | 792.5 | 414 | 452.2 | 817.3 | 594 | 590.8 | 712.1 | 238.9 | 289.7 | 698.2 | 88.6 | 156.3 | 214.2 | 361.2 | 537.2 | 600.4 | 365 | 526.8 | 145.3 | 314.2 | 295 | 185.2 | 237.3 | 284 | 199.5
1333 | 1094 | 471.3 | 188.52 | 220.369 | 299.7 | 293.3 | 288.8 | 275.3 | 515.2 | 50.3 | 19.1 | 88.9 | 6.5 | 242.5 | 13.3 | 364.2 | 709.1 | 795.7 | 414.4 | 451.8 | 818.1 | 594.9 | 588.1 | 707.9 | 239.3 | 290.3 | 698 | 88.7 | 156.5 | 214.4 | 361.8 | 533.9 | 594.1 | 365.9 | 524.2 | 145.4 | 313.7 | 295.4 | 185.3 | 237.4 | 284.4 | 199.7
1334 | 1095 | 473.6 | 189.44 | 221.4444 | 300.3 | 292.7 | 289 | 275.4 | 519 | 50.3 | 19.1 | 89 | 7 | 236.2 | 12.3 | 364.4 | 717.6 | 797.1 | 414.6 | 451.7 | 818.2 | 595.8 | 588 | 710.4 | 239.6 | 290.8 | 698.2 | 88.8 | 156.7 | 214.8 | 362.5 | 534.3 | 604.6 | 367.2 | 527.3 | 145.5 | 313.2 | 295.4 | 185.4 | 237.5 | 284.8 | 200
1335 | 1096 | 473 | 189.2 | 221.1639 | 300.6 | 292.7 | 289.2 | 275.6 | 523.4 | 50.4 | 19.1 | 89.1 | 6.1 | 238.2 | 10.3 | 364.4 | 713.7 | 799.8 | 414.7 | 451.5 | 818.7 | 596.8 | 585.4 | 713.4 | 240 | 291.5 | 698.7 | 88.9 | 156.9 | 215.1 | 363.1 | 532.7 | 601.6 | 368.3 | 527.2 | 145.6 | 312.8 | 294.8 | 185.5 | 237.5 | 285.2 | 200.2
1336 | 1097 | 472.4 | 188.96 | 220.8834 | 300.1 | 293.1 | 289.2 | 275.5 | 527 | 50.4 | 19.1 | 89.3 | 7 | 248.9 | 8.6 | 364.6 | 708.8 | 794.3 | 415 | 451.1 | 819.6 | 597.7 | 587.1 | 717.3 | 240.3 | 292.2 | 700.3 | 89 | 157 | 215.7 | 363.8 | 532.5 | 600.4 | 369.1 | 527.8 | 145.8 | 312.5 | 294.5 | 185.6 | 237.5 | 285.6 | 200.4
1337 | 1098 | 471.5 | 188.6 | 220.4625 | 299.8 | 293.1 | 289.5 | 274.7 | 528.1 | 50.4 | 19.1 | 89.4 | 6.5 | 232.9 | 7.9 | 364.9 | 713.7 | 785.7 | 415.4 | 451.3 | 818.9 | 598.6 | 585.1 | 712.3 | 240.7 | 292.8 | 701.3 | 89.1 | 157.2 | 215.6 | 364.5 | 531.6 | 592.6 | 369.6 | 525.6 | 145.9 | 312.3 | 294.7 | 185.7 | 237.7 | 286 | 200.6
1338 | 1099 | 472.4 | 188.96 | 220.8834 | 301.2 | 292.6 | 290.1 | 274.5 | 523.1 | 50.5 | 19.1 | 89.5 | 6.6 | 221.1 | 8.3 | 364.9 | 717.2 | 786 | 415.4 | 451.6 | 817.9 | 599.4 | 587.4 | 711.4 | 241.1 | 293.5 | 700.5 | 89.2 | 157.3 | 215.6 | 365.1 | 531.2 | 596.2 | 370.2 | 526.6 | 146.1 | 312.5 | 295.1 | 185.9 | 237.9 | 286.4 | 200.9
1339 | 1100 | 473.2 | 189.28 | 221.2574 | 303.2 | 292.7 | 289.5 | 274.8 | 524.5 | 50.5 | 19.1 | 89.5 | 5.9 | 214.8 | 6.9 | 365.1 | 715.6 | 784.1 | 415.7 | 451.5 | 817.4 | 600.3 | 598.7 | 701.5 | 241.5 | 294.1 | 700 | 89.3 | 157.5 | 215.8 | 365.8 | 535 | 598.2 | 371.1 | 532.3 | 146.2 | 313.5 | 295.4 | 186.4 | 238.2 | 286.8 | 201.1
1340 | 1101 | 473 | 189.2 | 221.1639 | 303.4 | 293.3 | 288.6 | 275.3 | 525 | 50.5 | 19.1 | 89.5 | 6.2 | 258.6 | 5.3 | 365.3 | 711.2 | 779.9 | 415.9 | 451.2 | 817.1 | 601.2 | 611.7 | 694.9 | 241.8 | 294.7 | 699.3 | 89.4 | 157.6 | 216.1 | 366.5 | 538.7 | 600.5 | 371.8 | 535.3 | 146.4 | 314.5 | 295.8 | 186.8 | 238.5 | 287.3 | 201.4
1341 | 1102 | 471.6 | 188.64 | 220.5093 | 303 | 293.9 | 287.7 | 275.9 | 523.9 | 50.6 | 19.1 | 89.6 | 6.3 | 275.1 | 4.7 | 365.3 | 708.5 | 785.6 | 416 | 451.5 | 817.1 | 602.1 | 615.2 | 693.9 | 242.2 | 295.2 | 698.9 | 89.5 | 157.8 | 216.2 | 367.1 | 539.2 | 600.7 | 372.7 | 535.8 | 146.6 | 315.2 | 296.6 | 187.1 | 238.8 | 287.8 | 201.7
1342 | 1103 | 473.6 | 189.44 | 221.4444 | 303.4 | 294.6 | 287.6 | 276.3 | 520 | 50.7 | 19.1 | 89.7 | 5.9 | 221.9 | 4.5 | 365.4 | 709.2 | 792.7 | 416.2 | 451.9 | 817.5 | 602.9 | 613.6 | 692.7 | 242.5 | 295.8 | 698 | 89.6 | 158 | 216.4 | 367.7 | 538.3 | 595.2 | 373.4 | 533.7 | 146.8 | 315.3 | 296.9 | 187.3 | 238.9 | 288.2 | 201.9
1343 | 1104 | 472.9 | 189.16 | 221.1171 | 304.4 | 294.5 | 287.6 | 276.7 | 518.4 | 50.7 | 19.1 | 89.8 | 5.3 | 204.4 | 4.7 | 365.6 | 705.4 | 787.3 | 416.4 | 451.9 | 817.7 | 603.8 | 609.8 | 696.8 | 242.9 | 296.4 | 697.8 | 89.7 | 158.3 | 216.5 | 368.4 | 538.6 | 598.6 | 374.4 | 533.4 | 146.9 | 315.3 | 297.3 | 187.5 | 239.1 | 288.7 | 202.2
1344 | 1105 | 472.6 | 189.04 | 220.9769 | 304 | 294.1 | 287.8 | 276.9 | 518.9 | 50.8 | 19.1 | 89.9 | 5.7 | 224.1 | 5.5 | 365.8 | 705.6 | 779.8 | 416.6 | 451.5 | 816.7 | 604.6 | 610 | 698.3 | 243.2 | 297.1 | 698.8 | 89.8 | 158.5 | 216.9 | 369 | 539.5 | 597.4 | 375.3 | 533.2 | 147.1 | 315.3 | 297.9 | 187.8 | 239.5 | 289.1 | 202.4
1345 | 1106 | 472.5 | 189 | 220.9301 | 303.7 | 294.9 | 287.8 | 277.4 | 517.9 | 50.9 | 19.1 | 90 | 5.7 | 244.2 | 7.4 | 366.1 | 714.4 | 772.8 | 416.9 | 451.7 | 815.5 | 605.4 | 606 | 698.2 | 243.6 | 297.7 | 699.2 | 89.9 | 158.6 | 217.1 | 369.7 | 536 | 594.4 | 375.7 | 531 | 147.3 | 315.3 | 297.6 | 188.1 | 239.6 | 289.4 | 202.6
1346 | 1107 | 471.9 | 188.76 | 220.6496 | 305.3 | 297.1 | 287.8 | 277.6 | 518.1 | 50.9 | 19.1 | 90 | 6.5 | 206.9 | 7.3 | 366.2 | 710.4 | 762.8 | 416.9 | 452 | 815.9 | 606.3 | 602.1 | 693.5 | 243.9 | 298.4 | 699.9 | 90 | 158.8 | 217.2 | 370.3 | 533.2 | 588.3 | 376 | 529.3 | 147.5 | 315.3 | 297.4 | 188.3 | 239.8 | 289.9 | 202.9
1347 | 1108 | 473.2 | 189.28 | 221.2574 | 305.9 | 298.3 | 288 | 277.6 | 513.9 | 50.9 | 19.1 | 90 | 7.1 | 221.8 | 7.8 | 366.2 | 706.9 | 763.9 | 416.9 | 451.6 | 817.3 | 607.1 | 600.6 | 688.9 | 244.3 | 299 | 700.4 | 90.1 | 159 | 217.3 | 370.9 | 529.6 | 584.5 | 376.6 | 530.6 | 147.7 | 315.4 | 297.3 | 188.6 | 240 | 290.3 | 203.1
1348 | 1109 | 472.8 | 189.12 | 221.0704 | 307 | 297.6 | 287.9 | 277.6 | 512.3 | 50.9 | 19.1 | 90.1 | 6.1 | 215.6 | 10 | 366.3 | 715.2 | 765 | 416.9 | 451.9 | 817.7 | 608 | 601.7 | 689 | 244.6 | 299.8 | 700.7 | 90.2 | 159.2 | 217.7 | 371.6 | 529.2 | 589.3 | 377.6 | 532.7 | 147.9 | 316 | 297.4 | 188.8 | 240.2 | 290.7 | 203.4
1349 | 1110 | 473 | 189.2 | 221.1639 | 308.8 | 296.7 | 287.6 | 278.2 | 513.1 | 50.8 | 19 | 90.2 | 6.1 | 243.9 | 8.5 | 366.5 | 726.6 | 758.1 | 417 | 452.1 | 817.5 | 608.8 | 600.6 | 687.9 | 245 | 300.6 | 702.1 | 90.3 | 159.4 | 218 | 372.2 | 527.5 | 589.4 | 378.4 | 531.8 | 148 | 316.5 | 297.3 | 189 | 240.4 | 291.1 | 203.6
1350 | 1111 | 473.3 | 189.32 | 221.3042 | 309.8 | 296.7 | 287.6 | 278.6 | 511.2 | 50.8 | 19 | 90.3 | 5.9 | 213.5 | 6.7 | 366.7 | 727.8 | 741 | 417 | 451.6 | 816.9 | 609.6 | 598.6 | 683.1 | 245.3 | 301.3 | 701.8 | 90.4 | 159.6 | 218 | 372.8 | 527 | 576.5 | 378.6 | 530.6 | 148.2 | 317.1 | 297.6 | 189.4 | 240.7 | 291.5 | 203.9
1351 | 1112 | 473.9 | 189.56 | 221.5847 | 310.7 | 298.8 | 287 | 279.2 | 507.1 | 50.8 | 19 | 90.5 | 5.8 | 222 | 5.9 | 366.7 | 730.1 | 729.6 | 416.9 | 451.9 | 816.1 | 610.4 | 598.8 | 681.3 | 245.6 | 302 | 701 | 90.5 | 159.8 | 218.3 | 373.4 | 527.9 | 568.1 | 379 | 531.2 | 148.4 | 317.9 | 298.3 | 189.8 | 241.1 | 291.9 | 204.2
1352 | 1113 | 472.1 | 188.84 | 220.7431 | 310.2 | 298.8 | 286 | 280.3 | 506.6 | 50.8 | 19 | 90.5 | 5.1 | 221 | 5.6 | 366.9 | 722.1 | 731.5 | 417 | 452.1 | 815.5 | 611.1 | 594 | 673.9 | 246 | 302.6 | 700.1 | 90.6 | 160 | 218.4 | 374 | 527.8 | 569.2 | 379.7 | 532.8 | 148.6 | 318.4 | 299 | 190.1 | 241.4 | 292.3 | 204.5
1353 | 1114 | 474.2 | 189.68 | 221.725 | 309.5 | 298 | 285.5 | 280.9 | 513.6 | 50.8 | 19 | 90.6 | 5.2 | 252.1 | 5.4 | 367 | 725.2 | 740.7 | 417 | 451.7 | 816.7 | 612 | 597.1 | 673.6 | 246.3 | 303.3 | 699.8 | 90.7 | 160.2 | 218.6 | 374.6 | 531.3 | 571.5 | 380.6 | 535.3 | 148.8 | 319 | 299.9 | 190.4 | 241.6 | 292.7 | 204.7
1354 | 1115 | 474.6 | 189.84 | 221.912 | 310.3 | 297.1 | 285.8 | 281.4 | 514.7 | 50.8 | 19 | 90.7 | 5.9 | 242.8 | 6.1 | 367 | 719.3 | 744.8 | 416.8 | 452.1 | 817.9 | 612.8 | 599.8 | 671.6 | 246.6 | 303.9 | 699.8 | 90.8 | 160.3 | 218.9 | 375.3 | 531.8 | 578.8 | 381.3 | 536.3 | 149 | 319.4 | 300.4 | 190.6 | 241.8 | 293.1 | 205
1355 | 1116 | 474 | 189.6 | 221.6315 | 311.2 | 296.2 | 286 | 281.8 | 512.8 | 50.8 | 19 | 90.7 | 5.8 | 214.2 | 7.4 | 367 | 713.9 | 754.6 | 416.7 | 452.5 | 818.5 | 613.6 | 598.3 | 672 | 247 | 304.5 | 699.3 | 90.8 | 160.5 | 219 | 376 | 531.4 | 583.9 | 382.2 | 536.1 | 149.2 | 319.5 | 300.9 | 190.8 | 242.1 | 293.5 | 205.2
1356 | 1117 | 471 | 188.4 | 220.2287 | 311.7 | 295.5 | 286.4 | 281.9 | 511.3 | 50.8 | 19 | 90.9 | 5.7 | 216.9 | 8.8 | 367.1 | 709.2 | 760.3 | 416.8 | 452.3 | 817.8 | 614.3 | 597.3 | 672.1 | 247.3 | 304.9 | 699.4 | 90.9 | 160.6 | 219.3 | 376.6 | 529.7 | 573.7 | 382.7 | 531.9 | 149.4 | 319.4 | 301.1 | 191.1 | 242.3 | 293.9 | 205.5
1357 | 1118 | 471.9 | 188.76 | 220.6496 | 312.6 | 295.2 | 287.1 | 281.6 | 509.9 | 50.8 | 19 | 91 | 6.4 | 218.5 | 10.4 | 367.4 | 719.2 | 770.6 | 417 | 452.5 | 817 | 615.1 | 598.2 | 676.4 | 247.6 | 305 | 701 | 91 | 160.8 | 219.5 | 377.2 | 528.1 | 569.3 | 383.4 | 528.9 | 149.6 | 319.3 | 301.2 | 191.3 | 242.4 | 294.3 | 205.7
1358 | 1119 | 473.1 | 189.24 | 221.2107 | 313.6 | 295.1 | 287.5 | 281.8 | 509.8 | 50.8 | 19 | 91 | 5.4 | 221.9 | 10.5 | 367.6 | 721.3 | 773.1 | 417 | 452.9 | 816.7 | 615.8 | 603.5 | 678.9 | 247.9 | 304.7 | 701.3 | 91.1 | 160.9 | 219.8 | 377.9 | 527.8 | 572.9 | 384.3 | 529.3 | 149.8 | 319.2 | 301.6 | 191.4 | 242.6 | 294.6 | 206
1359 | 1120 | 471.4 | 188.56 | 220.4158 | 315.1 | 297.3 | 287.7 | 281.8 | 511.1 | 50.7 | 19 | 91.1 | 5.3 | 222.8 | 9.9 | 367.7 | 722.9 | 777.2 | 416.9 | 453 | 817.4 | 616.6 | 607.1 | 681.2 | 248.2 | 304.5 | 701.3 | 91.2 | 161.2 | 220 | 378.5 | 529.2 | 574.6 | 385.3 | 529.8 | 150 | 319.4 | 302.1 | 191.6 | 242.8 | 295 | 206.2
1360 | 1121 | 473.4 | 189.36 | 221.3509 | 316.6 | 299.7 | 287.7 | 281.9 | 511.3 | 50.7 | 19 | 91.1 | 6.1 | 222.3 | 9.2 | 367.7 | 722 | 771.3 | 416.7 | 452.6 | 818 | 617.3 | 605.5 | 673.1 | 248.6 | 304.5 | 700.6 | 91.3 | 161.4 | 220.1 | 379.1 | 529.1 | 571.8 | 385.9 | 529.7 | 150.2 | 319.3 | 302.4 | 191.9 | 243 | 295.4 | 206.4
1361 | 1122 | 472.9 | 189.16 | 221.1171 | 316.4 | 300.3 | 287.6 | 281.8 | 515 | 50.7 | 19 | 91.2 | 7.1 | 229.8 | 8.2 | 367.8 | 723.9 | 776.1 | 416.6 | 452.9 | 819 | 618.1 | 606.2 | 677.5 | 248.9 | 304.6 | 701 | 91.4 | 161.5 | 220.3 | 379.8 | 534.1 | 585.8 | 387 | 535.6 | 150.4 | 320.2 | 303 | 192.2 | 243.2 | 295.8 | 206.7
1362 | 1123 | 473.1 | 189.24 | 221.2107 | 316.2 | 299 | 288 | 281.7 | 521.1 | 50.8 | 19 | 91.3 | 7.3 | 211.3 | 8.1 | 368.1 | 723.8 | 778.1 | 416.8 | 453.2 | 820.1 | 618.8 | 609.3 | 692.1 | 249.2 | 304.7 | 702.3 | 91.5 | 161.7 | 220.6 | 380.4 | 537.6 | 593.7 | 388.2 | 539.5 | 150.6 | 321.2 | 302.9 | 192.4 | 243.2 | 296.3 | 207
1363 | 1124 | 473.2 | 189.28 | 221.2574 | 316.4 | 299.2 | 288.6 | 281.4 | 524.4 | 50.8 | 19 | 91.4 | 7.4 | 216.1 | 9.5 | 368.4 | 727.8 | 785 | 416.8 | 452.9 | 821.1 | 619.6 | 607.9 | 697.7 | 249.5 | 304.9 | 703.7 | 91.6 | 161.8 | 220.8 | 381 | 539.5 | 590.6 | 388.8 | 536.8 | 150.8 | 321 | 303.5 | 192.7 | 243.5 | 296.8 | 207.2
1364 | 1125 | 473.2 | 189.28 | 221.2574 | 316.2 | 301.9 | 289.2 | 281 | 522.5 | 50.8 | 19 | 91.6 | 6.4 | 219.5 | 9.9 | 368.6 | 719.5 | 789.4 | 416.8 | 453 | 821 | 620.3 | 607.7 | 696.2 | 249.8 | 305.1 | 703.4 | 91.7 | 162 | 220.9 | 381.6 | 538.9 | 585.2 | 389.3 | 534.8 | 151 | 321.4 | 303.3 | 193.1 | 243.9 | 297.2 | 207.5
1365 | 1126 | 473.9 | 189.56 | 221.5847 | 315.7 | 301 | 289.3 | 281 | 528.7 | 50.9 | 19 | 91.7 | 5.6 | 224.2 | 9.8 | 368.7 | 722.8 | 791.3 | 416.7 | 453.3 | 820.9 | 620.9 | 607.7 | 694.1 | 250.1 | 305.3 | 704.7 | 91.8 | 162.1 | 221 | 382.3 | 542.6 | 585.7 | 390 | 533.4 | 151.2 | 321.9 | 303.5 | 193.4 | 244.1 | 297.6 | 207.7
1366 | 1127 | 470.6 | 188.24 | 220.0417 | 314.2 | 299.9 | 289.3 | 281.6 | 531.1 | 50.9 | 19 | 91.8 | 6.3 | 232.7 | 8 | 368.8 | 719.5 | 799.4 | 416.6 | 453.8 | 821.1 | 621.5 | 605.6 | 692.2 | 250.4 | 305.6 | 704.8 | 91.9 | 162.4 | 221.4 | 382.9 | 543.5 | 596.6 | 390.8 | 533.5 | 151.4 | 322.1 | 303.4 | 193.7 | 244.2 | 298.1 | 208
1367 | 1128 | 472.1 | 188.84 | 220.7431 | 313.4 | 299.8 | 289.5 | 282.3 | 531.5 | 50.9 | 19 | 91.8 | 6.4 | 208.4 | 7.4 | 368.9 | 722.3 | 803 | 416.6 | 453.7 | 821.3 | 622.2 | 605.9 | 693.1 | 250.7 | 305.9 | 705.1 | 91.9 | 162.5 | 221.8 | 383.6 | 548.4 | 606.9 | 391.6 | 538 | 151.6 | 322.2 | 303.4 | 193.9 | 244.5 | 298.5 | 208.2
1368 | 1129 | 471.7 | 188.68 | 220.556 | 314.9 | 301.5 | 290.3 | 282.3 | 531.9 | 51 | 19 | 91.9 | 6.3 | 210.5 | 8.5 | 369.1 | 724.4 | 800.9 | 416.7 | 453.7 | 821.2 | 622.9 | 607.3 | 698.9 | 251 | 306.3 | 705.4 | 92 | 162.7 | 221.9 | 384.2 | 549.6 | 609.4 | 392.5 | 540.5 | 151.8 | 322.6 | 303.5 | 194.2 | 244.7 | 299 | 208.5
1369 | 1130 | 471.8 | 188.72 | 220.6028 | 316.1 | 301 | 290.7 | 282.4 | 533.7 | 51 | 19 | 91.8 | 6.1 | 215.1 | 7.7 | 369.5 | 719.5 | 796.4 | 416.9 | 454.1 | 821.1 | 623.6 | 606.4 | 704 | 251.3 | 306.8 | 705.9 | 92.1 | 162.8 | 222.1 | 384.8 | 550 | 603.3 | 393.2 | 537 | 152 | 322.4 | 304.1 | 194.4 | 245 | 299.5 | 208.8
1370 | 1131 | 471.8 | 188.72 | 220.6028 | 316.7 | 300.7 | 290.9 | 282.6 | 533.3 | 51 | 19 | 91.7 | 6.4 | 248.5 | 8.7 | 369.5 | 718.7 | 803.4 | 416.7 | 454 | 821 | 624.3 | 605.4 | 705.9 | 251.6 | 307.3 | 706.2 | 92.2 | 163 | 222.5 | 385.4 | 548.6 | 603.7 | 393.9 | 537 | 152.2 | 322.5 | 304.3 | 194.7 | 245.3 | 299.9 | 209
1371 | 1132 | 472.1 | 188.84 | 220.7431 | 318.9 | 303.6 | 290.7 | 282.3 | 532 | 51.1 | 19 | 91.7 | 5.2 | 249.2 | 11.6 | 369.9 | 716.1 | 797.6 | 417 | 453.9 | 820.5 | 624.9 | 608.1 | 701.9 | 251.9 | 307.9 | 705.6 | 92.3 | 163.1 | 222.7 | 386 | 548.5 | 607.2 | 394.9 | 540.3 | 152.5 | 322.5 | 304.8 | 195 | 245.6 | 300.3 | 209.3
1372 | 1133 | 472.9 | 189.16 | 221.1171 | 320.7 | 306.2 | 290.9 | 282.3 | 531.1 | 51.1 | 19 | 91.7 | 5.8 | 238.3 | 12.4 | 370 | 717.8 | 791.8 | 416.8 | 454.3 | 820 | 625.5 | 606.4 | 697.9 | 252.2 | 308.4 | 704.8 | 92.4 | 163.3 | 222.8 | 386.6 | 549.4 | 605.2 | 395.7 | 540.3 | 152.7 | 322.4 | 305.3 | 195.2 | 245.9 | 300.7 | 209.6
1373 | 1134 | 473 | 189.2 | 221.1639 | 321.1 | 305.2 | 291.1 | 282.4 | 535.9 | 51.1 | 19 | 91.7 | 6.6 | 222.8 | 11.5 | 370.1 | 724.4 | 794.6 | 416.7 | 454.6 | 819.6 | 626.1 | 607.2 | 690.7 | 252.5 | 308.9 | 704 | 92.5 | 163.5 | 223.2 | 387.2 | 550.9 | 615.2 | 396.7 | 539.5 | 152.9 | 322.5 | 305.6 | 195.4 | 246.1 | 301.2 | 209.8
1374 | 1135 | 472.1 | 188.84 | 220.7431 | 320.5 | 304.9 | 290.8 | 282.7 | 548.5 | 51.1 | 19 | 91.8 | 6.3 | 217.1 | 9.5 | 370.5 | 726 | 797.8 | 417 | 453.9 | 819.6 | 626.8 | 608.5 | 690.7 | 252.8 | 309.5 | 703.5 | 92.6 | 163.6 | 223.8 | 387.8 | 554.3 | 626.4 | 398 | 544.1 | 153.1 | 322.6 | 306.4 | 195.6 | 246.4 | 301.6 | 210.1
1375 | 1136 | 472.9 | 189.16 | 221.1171 | 319.8 | 306.3 | 290.8 | 282.9 | 549.3 | 51.1 | 19 | 91.9 | 5.5 | 238.6 | 8.7 | 370.6 | 726.6 | 794.8 | 417 | 453.8 | 819.6 | 627.4 | 606.2 | 694.7 | 253.2 | 310.2 | 703 | 92.7 | 163.8 | 224 | 388.4 | 554.2 | 628.1 | 399.1 | 542.7 | 153.3 | 322.2 | 306.4 | 195.7 | 246.6 | 302.1 | 210.3
1376 | 1137 | 470.3 | 188.12 | 219.9014 | 318.5 | 308 | 291.3 | 283 | 548.6 | 51.2 | 19 | 92 | 6.3 | 245.6 | 9.7 | 371 | 728 | 796.7 | 417.2 | 454.2 | 819.7 | 628.1 | 609.5 | 699.1 | 253.5 | 310.8 | 703.8 | 92.8 | 164 | 224 | 389 | 554.7 | 627.7 | 399.7 | 542.5 | 153.5 | 322.1 | 306.6 | 195.9 | 246.7 | 302.5 | 210.6
1377 | 1138 | 471.7 | 188.68 | 220.556 | 317.3 | 310.7 | 291.7 | 282.8 | 548.8 | 51.2 | 18.9 | 92.2 | 5.5 | 232 | 11.1 | 371.2 | 722.4 | 798.7 | 417.2 | 454.1 | 819.7 | 628.8 | 605.7 | 700.6 | 253.8 | 311.7 | 705 | 92.9 | 164.2 | 224.1 | 389.6 | 555.5 | 623.9 | 400.6 | 541.4 | 153.7 | 322.2 | 306.9 | 196.1 | 246.8 | 303 | 210.8
1378 | 1139 | 470.4 | 188.16 | 219.9482 | 317.8 | 311 | 291.3 | 282.7 | 544.2 | 51.2 | 18.9 | 92.4 | 5.5 | 214.8 | 11.4 | 371.5 | 722.3 | 798 | 417.4 | 454.5 | 819.4 | 629.4 | 602.7 | 698.6 | 254.1 | 312.5 | 705 | 93 | 164.4 | 224.3 | 390.3 | 555.2 | 620.1 | 401.3 | 539.4 | 154 | 322.6 | 307.5 | 196.4 | 247.2 | 303.4 | 211
1379 | 1140 | 471.4 | 188.56 | 220.4158 | 318.5 | 310.1 | 290.6 | 282.8 | 546.6 | 51.3 | 19 | 92.5 | 5.8 | 218.3 | 9.7 | 371.8 | 728.7 | 798.2 | 417.6 | 454.9 | 818.6 | 630 | 601.8 | 698.3 | 254.5 | 313.2 | 704.8 | 93.1 | 164.6 | 224.5 | 390.9 | 560.5 | 626.8 | 402.6 | 542 | 154.2 | 322.9 | 308.1 | 196.7 | 247.6 | 303.8 | 211.3
1380 | 1141 | 470.9 | 188.36 | 220.182 | 317.9 | 309.1 | 290 | 283.8 | 549 | 51.4 | 19 | 92.7 | 5.5 | 222.5 | 8.6 | 372.1 | 728.1 | 794.6 | 417.8 | 455 | 818.7 | 630.6 | 598.9 | 698.8 | 254.8 | 314 | 705.5 | 93.2 | 164.8 | 224.7 | 391.5 | 562.8 | 630.1 | 404.1 | 543.6 | 154.4 | 322.8 | 307.7 | 196.9 | 247.7 | 304.3 | 211.6
1381 | 1142 | 468.8 | 187.52 | 219.2001 | 318.8 | 307.6 | 290.1 | 284.4 | 547.1 | 51.5 | 18.9 | 92.7 | 5.6 | 228.3 | 8.9 | 372.2 | 726.2 | 799.5 | 417.8 | 455.3 | 819.2 | 631.3 | 596.6 | 699.3 | 255.2 | 314.8 | 705.9 | 93.3 | 165 | 224.9 | 392.2 | 560.5 | 628.5 | 405.2 | 541.9 | 154.6 | 323.1 | 307.4 | 197 | 247.9 | 304.7 | 211.8
1382 | 1143 | 468.9 | 187.56 | 219.2468 | 320.5 | 307.8 | 290.3 | 284.5 | 544.1 | 51.5 | 18.9 | 92.7 | 5.2 | 233.7 | 8.1 | 372.4 | 721.3 | 799.1 | 417.9 | 455.3 | 819 | 631.8 | 596.1 | 692.1 | 255.5 | 315.4 | 705.1 | 93.4 | 165.2 | 225 | 392.8 | 561 | 623.7 | 406 | 542.2 | 154.9 | 323.2 | 307.6 | 197.2 | 248.1 | 305.1 | 212.1
1383 | 1144 | 469 | 187.6 | 219.2936 | 319.9 | 309 | 290.4 | 284.8 | 543.2 | 51.5 | 18.9 | 92.8 | 5.8 | 267.6 | 7.3 | 372.6 | 718.2 | 795.7 | 418.1 | 454.8 | 818.7 | 632.3 | 593.9 | 689.2 | 255.8 | 316.2 | 704.4 | 93.5 | 165.4 | 225.3 | 393.5 | 563.3 | 617.2 | 406.8 | 541.3 | 155.1 | 323.7 | 307.7 | 197.5 | 248.4 | 305.5 | 212.3
1384 | 1145 | 468.5 | 187.4 | 219.0598 | 318.1 | 308.1 | 291 | 284.8 | 543.1 | 51.5 | 18.9 | 92.8 | 6 | 195 | 5.6 | 372.8 | 715.6 | 796 | 418.2 | 455.3 | 818.1 | 632.9 | 594.7 | 689.1 | 256.2 | 317.1 | 704.5 | 93.6 | 165.6 | 225.4 | 394.1 | 565.3 | 615 | 407.8 | 542 | 155.3 | 324.3 | 308.1 | 197.8 | 248.6 | 305.9 | 212.6
1385 | 1146 | 468.3 | 187.32 | 218.9663 | 316.7 | 307.7 | 291 | 284.8 | 543.7 | 51.6 | 18.9 | 93 | 5.9 | 218.4 | 4.8 | 372.9 | 717.7 | 799.2 | 418.2 | 455.7 | 817.7 | 633.4 | 592.8 | 696.1 | 256.5 | 318 | 704.9 | 93.6 | 165.7 | 225.7 | 394.8 | 566.2 | 614.8 | 408.8 | 542.4 | 155.6 | 324.8 | 308 | 198.2 | 248.8 | 306.4 | 212.8
1386 | 1147 | 470.7 | 188.28 | 220.0885 | 315.7 | 307.3 | 290.8 | 285.3 | 544.4 | 51.6 | 18.9 | 93 | 6.3 | 266.2 | 5.4 | 373.1 | 727.8 | 798.1 | 418.4 | 455.9 | 817.7 | 634 | 590.5 | 696.3 | 256.8 | 318.8 | 703.9 | 93.7 | 165.9 | 226 | 395.4 | 566.6 | 611.8 | 409.5 | 542.4 | 155.8 | 325.3 | 307.8 | 198.6 | 249.1 | 306.8 | 213.1
1387 | 1148 | 472.3 | 188.92 | 220.8366 | 315 | 307.3 | 290.9 | 285.7 | 545.7 | 51.6 | 18.9 | 93.1 | 7.2 | 220.7 | 7.1 | 373.4 | 728.9 | 800.2 | 418.6 | 455.5 | 817.7 | 634.5 | 590.3 | 697.4 | 257.1 | 319.8 | 703.5 | 93.8 | 166.1 | 226.2 | 396.1 | 568.1 | 615.6 | 410.4 | 543.9 | 156 | 325.6 | 307.9 | 198.9 | 249.3 | 307.2 | 213.4
1388 | 1149 | 471.8 | 188.72 | 220.6028 | 314.8 | 307.9 | 291 | 285.7 | 547.7 | 51.7 | 18.9 | 93 | 7.1 | 234.2 | 7.8 | 373.6 | 727.6 | 798.2 | 418.7 | 456 | 818.1 | 635.1 | 591.3 | 695.2 | 257.4 | 320.7 | 703.6 | 93.9 | 166.3 | 226.4 | 396.8 | 571.5 | 609.2 | 411.2 | 542.9 | 156.3 | 326.3 | 307.9 | 199 | 249.4 | 307.7 | 213.6
1389 | 1150 | 471.4 | 188.56 | 220.4158 | 314 | 308.5 | 291.1 | 285.9 | 552.8 | 51.7 | 18.9 | 93 | 6.5 | 233.4 | 6.6 | 373.8 | 721.6 | 801.4 | 418.9 | 456 | 818.1 | 635.6 | 591.6 | 701.3 | 257.7 | 321.7 | 704.3 | 94 | 166.4 | 226.7 | 397.5 | 576.6 | 610.9 | 412.2 | 542.7 | 156.5 | 326.4 | 308.7 | 199.2 | 249.5 | 308.1 | 213.9
1390 | 1151 | 472.4 | 188.96 | 220.8834 | 312.9 | 308.4 | 291 | 286 | 556.6 | 51.7 | 18.9 | 93 | 5.2 | 215.5 | 5.7 | 374.1 | 717.9 | 811.4 | 419.1 | 456.4 | 818.3 | 636.2 | 592.6 | 708.9 | 258 | 322.6 | 704.6 | 94.1 | 166.6 | 227.1 | 398.3 | 577.5 | 613.6 | 413 | 545 | 156.8 | 325.9 | 309 | 199.5 | 249.8 | 308.5 | 214.2
1391 | 1152 | 472.6 | 189.04 | 220.9769 | 312.4 | 309.4 | 291.9 | 285.6 | 559 | 51.8 | 18.9 | 93 | 4.2 | 234.6 | 7.7 | 374.3 | 714 | 810.4 | 419.3 | 456.4 | 818.1 | 636.7 | 592.8 | 712.3 | 258.3 | 323.5 | 705.4 | 94.2 | 166.8 | 227.4 | 399.2 | 581.5 | 620.3 | 414.1 | 547.8 | 157 | 325.7 | 308.7 | 199.7 | 250 | 309 | 214.4
1392 | 1153 | 469.5 | 187.8 | 219.5274 | 312.5 | 309.9 | 292.8 | 284.7 | 560.3 | 51.8 | 18.9 | 93 | 5.2 | 237.5 | 9 | 374.6 | 713.7 | 807.6 | 419.6 | 456.8 | 817.9 | 637.2 | 592.6 | 712.2 | 258.6 | 324.5 | 704.9 | 94.3 | 167 | 227.6 | 400 | 581.2 | 623.5 | 415.1 | 547.5 | 157.2 | 325.8 | 308.2 | 199.8 | 250.1 | 309.5 | 214.6
1393 | 1154 | 471.6 | 188.64 | 220.5093 | 313.2 | 311.4 | 293.3 | 284.6 | 558.9 | 51.9 | 18.9 | 93.1 | 5.9 | 234.4 | 8.5 | 374.8 | 708 | 806.3 | 419.6 | 456.9 | 818.3 | 637.7 | 592.1 | 710.5 | 258.9 | 325.6 | 705.2 | 94.4 | 167.2 | 227.7 | 400.6 | 579.4 | 621.3 | 415.9 | 547.1 | 157.5 | 326 | 308 | 200 | 250.2 | 309.9 | 214.8
1394 | 1155 | 471.4 | 188.56 | 220.4158 | 313.6 | 312.7 | 293.8 | 284.5 | 555.7 | 51.9 | 18.9 | 93.1 | 5.4 | 236.6 | 8.4 | 375 | 709.2 | 811.1 | 419.8 | 457 | 818.8 | 638.2 | 591.8 | 715.9 | 259.3 | 326.6 | 705.7 | 94.5 | 167.4 | 228 | 401.2 | 576.5 | 622.1 | 416.9 | 547.4 | 157.7 | 327.1 | 307.8 | 200.2 | 250.3 | 310.4 | 215.1
1395 | 1156 | 471.3 | 188.52 | 220.369 | 314.5 | 313.9 | 293.8 | 284.6 | 555.2 | 51.9 | 18.9 | 93.1 | 7.9 | 259.9 | 8.5 | 375.2 | 708.9 | 801.1 | 420 | 457.4 | 818 | 638.8 | 592.8 | 720.8 | 259.6 | 327.6 | 706.2 | 94.6 | 167.6 | 228.2 | 401.8 | 578.2 | 621 | 417.6 | 548.8 | 158 | 328.1 | 308 | 200.5 | 250.6 | 310.9 | 215.3
1396 | 1157 | 473.6 | 189.44 | 221.4444 | 314.4 | 315.7 | 293.6 | 284.3 | 555.6 | 52 | 18.9 | 93.2 | 7.9 | 223.8 | 8.4 | 375.4 | 713.3 | 789.2 | 420.2 | 457.5 | 816.7 | 639.3 | 594.8 | 710.6 | 259.9 | 328.8 | 704.7 | 94.7 | 167.7 | 228.4 | 402.5 | 582.8 | 612.8 | 418.3 | 549.5 | 158.2 | 329.4 | 308.7 | 201 | 250.9 | 311.4 | 215.6
1397 | 1158 | 475.1 | 190.04 | 222.1458 | 313.9 | 315.2 | 293.7 | 284.7 | 552.3 | 52 | 18.9 | 93.3 | 7.7 | 235.6 | 8.7 | 375.7 | 725 | 792.9 | 420.6 | 457.6 | 816.5 | 639.8 | 595.6 | 703.5 | 260.2 | 330 | 703.5 | 94.8 | 167.9 | 228.6 | 403.1 | 582.4 | 613.2 | 419 | 550.8 | 158.5 | 330.7 | 309.1 | 201.4 | 251.1 | 311.9 | 215.9
1398 | 1159 | 475.8 | 190.32 | 222.4731 | 313.7 | 314.7 | 293.3 | 286 | 550.3 | 52.1 | 18.9 | 93.2 | 5.9 | 254.2 | 9 | 375.9 | 727.1 | 803.6 | 420.8 | 457.8 | 816.1 | 640.4 | 594.6 | 700.3 | 260.5 | 331.3 | 702.6 | 94.9 | 168.1 | 228.7 | 403.8 | 581.2 | 613.2 | 420.1 | 551.2 | 158.7 | 331.5 | 309.2 | 201.8 | 251.4 | 312.5 | 216.2
1399 | 1160 | 474.3 | 189.72 | 221.7717 | 312.8 | 314.2 | 293.4 | 286.8 | 553.1 | 52.1 | 18.9 | 93.2 | 5.7 | 242.4 | 9.4 | 376.1 | 734.8 | 814.1 | 421.1 | 457.7 | 815.7 | 641 | 594.2 | 697.8 | 260.8 | 332.5 | 702.5 | 95 | 168.3 | 229 | 404.5 | 584 | 621.1 | 421.5 | 554.5 | 159 | 332.6 | 309.5 | 202.2 | 251.6 | 313 | 216.5
1400 | 1161 | 472.9 | 189.16 | 221.1171 | 312.6 | 314.1 | 293.8 | 286.8 | 554.9 | 52.1 | 18.9 | 93.3 | 5.5 | 246 | 12.1 | 376.4 | 734.9 | 812 | 421.5 | 458.2 | 815.9 | 641.6 | 592.3 | 700.3 | 261.2 | 333.7 | 702.1 | 95.1 | 168.4 | 229.4 | 405.1 | 585.9 | 621.1 | 422.3 | 553.1 | 159.2 | 333 | 309.5 | 202.5 | 251.6 | 313.5 | 216.8
1401 | 1162 | 474.4 | 189.76 | 221.8185 | 312.7 | 313.9 | 294 | 287.2 | 562.6 | 52.1 | 18.9 | 93.3 | 6.3 | 232.3 | 13.3 | 376.7 | 726.3 | 811.3 | 421.6 | 458.3 | 816.8 | 642.2 | 591.3 | 708.2 | 261.5 | 335 | 703.6 | 95.2 | 168.6 | 229.8 | 405.8 | 590.6 | 626.3 | 423 | 552.8 | 159.5 | 333 | 309.3 | 202.9 | 251.7 | 314.1 | 217.1
1402 | 1163 | 475.3 | 190.12 | 222.2393 | 312 | 313.4 | 294.9 | 286.8 | 563.7 | 52.1 | 18.9 | 93.3 | 6.6 | 239.9 | 13.4 | 376.8 | 726 | 802.1 | 421.7 | 458.2 | 817.8 | 642.7 | 590.3 | 711.7 | 261.9 | 336.2 | 705.1 | 95.3 | 168.8 | 229.9 | 406.4 | 587.1 | 619.1 | 423.7 | 550.4 | 159.8 | 333.1 | 309 | 203.1 | 251.9 | 314.6 | 217.3
1403 | 1164 | 473.2 | 189.28 | 221.2574 | 311.8 | 312.9 | 295.4 | 286.4 | 561.1 | 52.2 | 18.9 | 93.4 | 6.4 | 263.4 | 13.1 | 377 | 719.4 | 800.2 | 422 | 458.7 | 818.4 | 643.2 | 588.1 | 713.1 | 262.2 | 337.5 | 705.9 | 95.5 | 169 | 230.2 | 407 | 582.8 | 618.5 | 424.6 | 547.7 | 160 | 332.8 | 308.4 | 203.2 | 252 | 315 | 217.6
1404 | 1165 | 472.9 | 189.16 | 221.1171 | 311.5 | 312.7 | 295.4 | 286.8 | 563.8 | 52.3 | 18.9 | 93.3 | 7 | 246.9 | 11.6 | 377.2 | 718 | 801.9 | 422.4 | 458.5 | 818.7 | 643.7 | 585.7 | 712.3 | 262.5 | 338.8 | 705.9 | 95.6 | 169.2 | 230.5 | 407.6 | 582.5 | 617.1 | 425.5 | 548.1 | 160.3 | 332.8 | 308.2 | 203.4 | 252.1 | 315.4 | 217.8
1405 | 1166 | 473.4 | 189.36 | 221.3509 | 312.5 | 312.4 | 295.1 | 286.6 | 562.2 | 52.4 | 18.9 | 93.4 | 6.8 | 249.2 | 9.6 | 377.5 | 716.4 | 801.5 | 422.7 | 458.8 | 818.2 | 644.1 | 584.6 | 712.8 | 262.8 | 340 | 706.2 | 95.7 | 169.4 | 230.6 | 408.3 | 584.5 | 610.5 | 426.1 | 549.2 | 160.6 | 333.4 | 308.9 | 203.7 | 252.3 | 315.9 | 218.1
1406 | 1167 | 473.3 | 189.32 | 221.3042 | 313.5 | 312.5 | 295.1 | 286.3 | 561.6 | 52.5 | 18.9 | 93.4 | 6.1 | 270.2 | 6.6 | 377.6 | 716.8 | 792 | 423 | 459 | 818 | 644.5 | 584.4 | 707.5 | 263.1 | 341.3 | 706.5 | 95.8 | 169.6 | 230.9 | 409.1 | 593.4 | 610.1 | 426.7 | 549.9 | 160.8 | 333.9 | 310 | 204.1 | 252.8 | 316.3 | 218.3
1407 | 1168 | 472.7 | 189.08 | 221.0236 | 312.9 | 312 | 295 | 287.2 | 565.7 | 52.5 | 18.9 | 93.4 | 4.9 | 226.8 | 7.4 | 377.8 | 719.8 | 787.3 | 423.3 | 459.2 | 818.5 | 644.9 | 585.6 | 700.2 | 263.4 | 342.6 | 705.4 | 95.9 | 169.8 | 231 | 409.8 | 595.4 | 621 | 427.7 | 554.5 | 161.1 | 334.2 | 310.3 | 204.4 | 253.1 | 316.9 | 218.6
1408 | 1169 | 471.6 | 188.64 | 220.5093 | 312.8 | 311.9 | 294.6 | 287.9 | 563.8 | 52.6 | 18.9 | 93.4 | 5.8 | 247.1 | 9.5 | 378 | 720.9 | 788 | 423.6 | 459.3 | 819.1 | 645.4 | 584.5 | 703.7 | 263.7 | 345.1 | 705 | 96 | 170 | 231.1 | 410.5 | 594.7 | 618.3 | 428.6 | 555.2 | 161.3 | 334.4 | 310.7 | 204.8 | 253.3 | 317.4 | 218.9
1409 | 1170 | 473 | 189.2 | 221.1639 | 312 | 311.9 | 294 | 288.6 | 565.7 | 52.6 | 18.9 | 93.5 | 5.8 | 243.5 | 9.7 | 378.1 | 723.5 | 788.4 | 423.9 | 459.5 | 820.2 | 645.9 | 583.5 | 709.8 | 264.1 | 348.6 | 705.8 | 96.1 | 170.2 | 231.3 | 411.2 | 595.2 | 622.9 | 429.9 | 554 | 161.6 | 334.1 | 310.4 | 205.1 | 253.3 | 317.9 | 219.2
1410 | 1171 | 472.7 | 189.08 | 221.0236 | 312 | 312.3 | 293.9 | 289.4 | 564.1 | 52.6 | 18.9 | 93.6 | 5.6 | 233.3 | 12 | 378.3 | 723.5 | 787.8 | 424.2 | 459.3 | 821.5 | 646.4 | 582.4 | 713.7 | 264.4 | 350.7 | 708 | 96.2 | 170.4 | 231.6 | 411.7 | 592.6 | 617.1 | 430.5 | 553.1 | 161.9 | 334.1 | 310.5 | 205.5 | 253.5 | 318.4 | 219.4
1411 | 1172 | 472.9 | 189.16 | 221.1171 | 312.2 | 313.4 | 293.9 | 289 | 558.9 | 52.6 | 18.8 | 93.6 | 5.2 | 232.3 | 12 | 378.5 | 721.8 | 788.5 | 424.5 | 459.7 | 821 | 646.9 | 582.9 | 710.8 | 264.7 | 352 | 708.5 | 96.3 | 170.6 | 231.7 | 412.3 | 588.6 | 606.2 | 430.9 | 550.2 | 162.1 | 334.3 | 310.3 | 205.9 | 253.6 | 318.8 | 219.7
1412.1 | 1173.1 | 472.5 | 189 | 220.9301 | 312.5 | 313.9 | 294.3 | 288.8 | 553.5 | 52.7 | 18.8 | 93.6 | 5.6 | 244.5 | 10.1 | 378.7 | 724.3 | 793.4 | 424.9 | 459.8 | 820.4 | 647.4 | 582.1 | 708.1 | 265.1 | 353.9 | 707.4 | 96.4 | 170.7 | 232 | 412.9 | 585.2 | 600.5 | 431.4 | 550.5 | 162.4 | 334.2 | 310 | 206.2 | 253.7 | 319.2 | 219.9
1413.1 | 1174.1 | 472.6 | 189.04 | 220.9769 | 312.6 | 313.1 | 295 | 288.9 | 553.5 | 52.7 | 18.8 | 93.7 | 6.3 | 212.3 | 8.3 | 379 | 722.1 | 792.9 | 425.4 | 460.3 | 820.3 | 647.9 | 581.3 | 708.2 | 265.4 | 355.7 | 707.8 | 96.5 | 170.9 | 232.3 | 413.5 | 583.7 | 606.2 | 432.3 | 551.3 | 162.7 | 333.6 | 310.2 | 206.5 | 253.9 | 319.6 | 220.2
1414.1 | 1175.1 | 474.7 | 189.88 | 221.9588 | 313.2 | 313.5 | 294.8 | 288.3 | 553.8 | 52.8 | 18.8 | 93.7 | 6.7 | 228.7 | 8.2 | 379.2 | 719.3 | 795 | 425.8 | 460.2 | 819.9 | 648.5 | 580.3 | 707.2 | 265.8 | 357.1 | 708.7 | 96.6 | 171.1 | 232.3 | 414.2 | 584.9 | 602.3 | 432.8 | 551.8 | 163 | 333.2 | 311.1 | 206.9 | 254.1 | 320 | 220.4
1415.1 | 1176.1 | 475.8 | 190.32 | 222.4731 | 314 | 314.2 | 295 | 287.7 | 552 | 52.8 | 18.8 | 93.9 | 6.3 | 209.3 | 10.9 | 379.4 | 717.9 | 798.8 | 426.2 | 460.2 | 820 | 649 | 580.2 | 713.6 | 266.1 | 358.6 | 709.6 | 96.7 | 171.3 | 232.6 | 414.8 | 583.7 | 604.7 | 433.6 | 551.7 | 163.3 | 333.2 | 311 | 207.3 | 254.2 | 320.5 | 220.7
1416.1 | 1177.1 | 473.8 | 189.52 | 221.538 | 314.3 | 314.3 | 294.8 | 288.2 | 554.8 | 52.9 | 18.8 | 93.9 | 6.7 | 209 | 12.7 | 379.4 | 718.1 | 795.9 | 426.4 | 460.3 | 819.8 | 649.5 | 583.2 | 713.2 | 266.5 | 360.5 | 709.7 | 96.8 | 171.4 | 233 | 415.4 | 586.9 | 608.1 | 434.4 | 553.5 | 163.6 | 333.7 | 311 | 207.9 | 254.3 | 320.9 | 220.9
1417.1 | 1178.1 | 472.5 | 189 | 220.9301 | 314.6 | 314.1 | 294.9 | 288.7 | 554.3 | 52.9 | 18.8 | 93.9 | 5.6 | 210.2 | 13.4 | 379.5 | 715.5 | 794.4 | 426.7 | 460.5 | 819.6 | 650 | 583.7 | 709.7 | 266.9 | 361.6 | 709.1 | 96.9 | 171.6 | 233.1 | 416.1 | 588.1 | 605.4 | 435 | 553.7 | 163.9 | 334.4 | 311.1 | 208.4 | 254.6 | 321.4 | 221.2
1418.1 | 1179.1 | 472.1 | 188.84 | 220.7431 | 314.2 | 313.1 | 294.9 | 288.6 | 556.7 | 52.9 | 18.8 | 93.9 | 4.5 | 218.6 | 12.3 | 379.6 | 715.9 | 800 | 427 | 460.6 | 820 | 650.5 | 584.9 | 709.5 | 267.2 | 362.7 | 708.9 | 97 | 171.8 | 233.4 | 416.8 | 590.8 | 616.5 | 436.4 | 557.7 | 164.2 | 334.9 | 311.2 | 208.8 | 254.8 | 321.9 | 221.4
1419.1 | 1180.1 | 472.5 | 189 | 220.9301 | 314.6 | 312.1 | 294.5 | 288.2 | 560.2 | 53 | 18.8 | 93.9 | 5.1 | 216.6 | 12 | 379.8 | 714.4 | 809 | 427.5 | 460.8 | 820.4 | 651 | 583.6 | 718.7 | 267.6 | 364 | 709 | 97.1 | 172 | 233.6 | 417.4 | 590.2 | 618.8 | 437.8 | 558.9 | 164.5 | 334.7 | 311.6 | 209.1 | 254.9 | 322.5 | 221.7
1420.1 | 1181.1 | 473.6 | 189.44 | 221.4444 | 315.8 | 312.2 | 294.5 | 287.7 | 562.1 | 53 | 18.8 | 93.8 | 5.3 | 221.3 | 12.1 | 380 | 716.7 | 809.9 | 428.1 | 461.3 | 819.5 | 651.6 | 582.3 | 728.1 | 267.9 | 364.7 | 709.3 | 97.2 | 172.2 | 234 | 418.1 | 588.2 | 620.8 | 439 | 558.5 | 164.8 | 334.4 | 312.1 | 209.3 | 255 | 323 | 221.9
1421.1 | 1182.1 | 473 | 189.2 | 221.1639 | 315.8 | 312.2 | 295.1 | 287.4 | 565.6 | 53.1 | 18.8 | 93.7 | 5.7 | 233.9 | 10.8 | 380.3 | 718.4 | 812 | 428.6 | 461.7 | 819.3 | 652 | 581 | 727.4 | 268.2 | 365.7 | 708.1 | 97.4 | 172.4 | 234.2 | 418.9 | 587.9 | 625.8 | 440.2 | 559.6 | 165.1 | 334.2 | 312.4 | 209.5 | 255.1 | 323.4 | 222.1
1422.1 | 1183.1 | 474.2 | 189.68 | 221.725 | 315.5 | 314.4 | 296.2 | 287.3 | 567.3 | 53.1 | 18.8 | 93.7 | 5.7 | 215.7 | 9.3 | 380.6 | 724.6 | 802.8 | 429 | 461.8 | 818.8 | 652.5 | 580.4 | 728 | 268.6 | 366.9 | 708.3 | 97.5 | 172.6 | 234.3 | 419.7 | 588 | 625.8 | 441.1 | 561 | 165.4 | 334.6 | 312.2 | 209.8 | 255.2 | 323.9 | 222.4
1423.1 | 1184.1 | 473.4 | 189.36 | 221.3509 | 316.3 | 319 | 297 | 287.4 | 566.9 | 53.2 | 18.8 | 93.6 | 5.2 | 207.9 | 11.7 | 380.7 | 726.7 | 806.9 | 429.4 | 462.1 | 818.3 | 652.9 | 579.3 | 729.1 | 268.9 | 368.5 | 707.9 | 97.6 | 172.9 | 234.5 | 420.5 | 585.7 | 619.2 | 442 | 559.4 | 165.7 | 334.7 | 312.4 | 210.1 | 255.5 | 324.2 | 222.6
1424.1 | 1185.1 | 473.4 | 189.36 | 221.3509 | 316.7 | 319.2 | 297.2 | 287.9 | 565.4 | 53.2 | 18.8 | 93.6 | 4.9 | 210.1 | 12.5 | 381 | 729.8 | 814.8 | 430 | 462.3 | 818.1 | 653.3 | 578.2 | 730.9 | 269.2 | 369.7 | 707.1 | 97.7 | 173 | 234.9 | 421.2 | 583.4 | 617.7 | 442.8 | 557.7 | 166 | 334.5 | 312.5 | 210.3 | 255.6 | 324.5 | 222.9
1425.1 | 1186.1 | 474.2 | 189.68 | 221.725 | 316.5 | 318.4 | 297.2 | 288.4 | 568.7 | 53.1 | 18.8 | 93.6 | 5.6 | 217.5 | 11.5 | 381.2 | 730.6 | 814.7 | 430.5 | 462.2 | 817.3 | 653.7 | 579.7 | 730.1 | 269.5 | 371.3 | 705.8 | 97.8 | 173.3 | 235.4 | 421.9 | 580.6 | 625.4 | 444.3 | 558.7 | 166.3 | 335 | 313.1 | 210.5 | 255.7 | 324.8 | 223.1
1426.1 | 1187.1 | 470.2 | 188.08 | 219.8547 | 316.1 | 317.4 | 298 | 288.3 | 575.3 | 53.1 | 18.8 | 93.6 | 5.5 | 214.3 | 10.1 | 381.3 | 725.4 | 823.6 | 430.7 | 462.6 | 817.1 | 654 | 582.4 | 735.8 | 269.8 | 372.6 | 706.3 | 97.9 | 173.4 | 236 | 422.7 | 582.2 | 633.2 | 445.9 | 563.6 | 166.6 | 335.2 | 312.6 | 210.8 | 255.7 | 325.2 | 223.4
1427.1 | 1188.1 | 469.8 | 187.92 | 219.6677 | 315.8 | 317.1 | 299.7 | 288.1 | 577.1 | 53.1 | 18.8 | 93.7 | 4.9 | 215.8 | 9.9 | 381.4 | 726 | 826.2 | 431.1 | 462.8 | 817.7 | 654.5 | 583 | 742.6 | 270 | 373.6 | 707.7 | 98 | 173.7 | 236.2 | 423.5 | 582 | 633.3 | 446.9 | 563 | 166.8 | 335.2 | 312.8 | 211 | 255.8 | 325.7 | 223.6
1428.1 | 1189.1 | 470.7 | 188.28 | 220.0885 | 315.5 | 316.9 | 300.4 | 288.4 | 577.8 | 53.2 | 18.8 | 93.8 | 4.5 | 209.8 | 11.5 | 381.5 | 727.6 | 824 | 431.4 | 463.1 | 817.7 | 654.9 | 581.8 | 747.3 | 270.2 | 375.9 | 708.6 | 98.1 | 173.9 | 236.2 | 424.4 | 582 | 629.1 | 447.5 | 561.6 | 167.1 | 335.4 | 312.8 | 211.2 | 255.9 | 326.2 | 223.9
1429.1 | 1190.1 | 472.2 | 188.88 | 220.7898 | 314.6 | 317.2 | 300.5 | 288.5 | 576.1 | 53.1 | 18.8 | 93.9 | 4.8 | 204.8 | 12.5 | 381.6 | 721.9 | 825 | 431.8 | 463.5 | 817.9 | 655.3 | 579.4 | 747.1 | 270.3 | 376.5 | 709.4 | 98.2 | 174 | 236.4 | 425.3 | 581.1 | 623.4 | 448 | 560 | 167.4 | 335.9 | 312.8 | 211.4 | 256 | 326.7 | 224.2
1430.1 | 1191.1 | 473 | 189.2 | 221.1639 | 314.8 | 317.7 | 299.6 | 288.7 | 574.5 | 53.1 | 18.8 | 94 | 4.9 | 232.6 | 13 | 381.8 | 718.2 | 822.8 | 432.2 | 463.6 | 818.2 | 655.7 | 577.6 | 742.5 | 270.5 | 377.4 | 709.8 | 98.3 | 174.2 | 236.6 | 426.2 | 578.3 | 616.3 | 448.3 | 558.1 | 167.6 | 337 | 312.9 | 211.7 | 256.2 | 327.1 | 224.4
1431.1 | 1192.1 | 472.1 | 188.84 | 220.7431 | 315.8 | 319.2 | 298.9 | 288.7 | 571.5 | 53.1 | 18.8 | 94 | 5.7 | 234.8 | 11.1 | 381.9 | 714.4 | 807.8 | 432.6 | 463.7 | 819.5 | 656.1 | 576.5 | 739.7 | 270.7 | 377.9 | 710.8 | 98.5 | 174.4 | 236.7 | 427.1 | 575.2 | 608 | 449.1 | 556.4 | 167.9 | 337.2 | 312.5 | 211.9 | 256.5 | 327.6 | 224.7
1432.1 | 1193.1 | 470.4 | 188.16 | 219.9482 | 317.4 | 320.6 | 298.7 | 288.9 | 566.6 | 53.2 | 18.8 | 94 | 5.9 | 240.2 | 8.1 | 382.1 | 716 | 799.4 | 433.2 | 464.1 | 819.9 | 656.5 | 576.2 | 731.2 | 270.9 | 378.6 | 711.4 | 98.6 | 174.6 | 237 | 428 | 574 | 600.1 | 449.2 | 554.4 | 168.2 | 337.5 | 312.6 | 212.2 | 256.7 | 328 | 224.9
1433.1 | 1194.1 | 470.1 | 188.04 | 219.8079 | 319.3 | 320.3 | 298.7 | 289.3 | 564 | 53.3 | 18.8 | 94 | 5.6 | 238.6 | 6.7 | 382.3 | 717.6 | 791 | 433.6 | 464.2 | 819.7 | 656.9 | 576.4 | 722.5 | 271.1 | 379.4 | 711.7 | 98.7 | 174.7 | 237.2 | 429 | 573.7 | 589.8 | 449.3 | 554.9 | 168.4 | 338.2 | 313.5 | 212.7 | 257 | 328.4 | 225.2
1434.1 | 1195.1 | 472.2 | 188.88 | 220.7898 | 320.2 | 319 | 298.8 | 289.4 | 567.2 | 53.4 | 18.8 | 94 | 5.6 | 235 | 6.4 | 382.4 | 717.1 | 786.5 | 434.2 | 464.4 | 819.2 | 657.4 | 576.5 | 720.6 | 271.3 | 380.2 | 711.6 | 98.8 | 174.9 | 237.4 | 430 | 576.4 | 590.9 | 450.4 | 559.1 | 168.7 | 339.1 | 314.3 | 213.1 | 257.2 | 328.8 | 225.4
1435.1 | 1196.1 | 471.1 | 188.44 | 220.2755 | 320.4 | 317.8 | 298.9 | 290.1 | 565.7 | 53.5 | 18.8 | 94 | 5.8 | 233.1 | 5.8 | 382.7 | 717.3 | 782.8 | 434.8 | 464.7 | 817.2 | 657.8 | 576.6 | 716.1 | 271.6 | 381.1 | 711.9 | 98.9 | 175.1 | 237.5 | 431 | 575.6 | 587.7 | 450.8 | 557.7 | 169 | 339.1 | 315.2 | 213.5 | 257.5 | 329.2 | 225.7
1436.1 | 1197.1 | 471.8 | 188.72 | 220.6028 | 320.9 | 318 | 299.5 | 291 | 566.4 | 53.6 | 18.8 | 94 | 6.2 | 204.7 | 5.2 | 382.9 | 718.7 | 781.3 | 435.5 | 465.1 | 815.3 | 658.3 | 577.3 | 711.6 | 271.9 | 381.9 | 712.7 | 99 | 175.2 | 237.8 | 432 | 576.9 | 589.9 | 451.6 | 557.6 | 169.2 | 339.5 | 315.6 | 214 | 257.8 | 329.7 | 226
1437.1 | 1198.1 | 471.4 | 188.56 | 220.4158 | 320.6 | 318 | 299.8 | 291.9 | 566.9 | 53.7 | 18.8 | 94 | 6.2 | 224.3 | 5 | 383.1 | 716.5 | 779.8 | 436 | 465.4 | 815.4 | 658.7 | 577.2 | 709.5 | 272.3 | 382.7 | 712.5 | 99.1 | 175.3 | 238.1 | 432.8 | 578.2 | 591 | 452.2 | 557.5 | 169.5 | 339.8 | 316.5 | 214.5 | 258 | 330.1 | 226.2
1438.1 | 1199.1 | 471.4 | 188.56 | 220.4158 | 320.7 | 318.5 | 300.3 | 292.8 | 566.5 | 53.8 | 18.8 | 94.1 | 5.7 | 197.8 | 6.5 | 383.3 | 719.7 | 774.7 | 436.5 | 465.5 | 816.8 | 659.2 | 577.4 | 712.5 | 272.5 | 383.4 | 713.3 | 99.2 | 175.6 | 238.3 | 433.5 | 579 | 596.7 | 452.9 | 557.4 | 169.8 | 340.2 | 316.7 | 214.9 | 258.1 | 330.5 | 226.5
1439.1 | 1200.1 | 472.7 | 189.08 | 221.0236 | 321.9 | 318.4 | 300.8 | 293.3 | 565.4 | 53.8 | 18.8 | 94.2 | 5.4 | 218.6 | 5.7 | 383.4 | 717.6 | 777.7 | 436.7 | 465.7 | 818.3 | 659.7 | 576.9 | 717.3 | 272.8 | 384 | 714.4 | 99.3 | 175.7 | 238.5 | 434.2 | 578.2 | 592.6 | 453.3 | 557.5 | 170.1 | 340.1 | 317.3 | 215.2 | 258.3 | 330.9 | 226.7
1440.1 | 1201.1 | 473.7 | 189.48 | 221.4912 | 323 | 317.8 | 301.4 | 293.5 | 564.2 | 53.9 | 18.8 | 94.3 | 6.1 | 271.1 | 4.6 | 383.5 | 719.3 | 783.8 | 437.1 | 466 | 818.7 | 660.1 | 575.4 | 719.5 | 273.2 | 384.7 | 715.1 | 99.5 | 175.9 | 238.7 | 434.7 | 576.5 | 587.6 | 453.5 | 556.4 | 170.4 | 340 | 318 | 215.4 | 258.4 | 331.4 | 227
1441.1 | 1202.1 | 475 | 190 | 222.0991 | 324.3 | 317.7 | 302 | 293.7 | 566.9 | 54 | 18.8 | 94.3 | 6 | 234.5 | 5.5 | 383.7 | 719 | 776.6 | 437.6 | 466.2 | 818.6 | 660.6 | 575.6 | 715.3 | 273.5 | 385.6 | 715.2 | 99.6 | 176.1 | 239.1 | 435.5 | 580.2 | 589.4 | 454 | 560.1 | 170.7 | 340.2 | 318.7 | 215.9 | 258.7 | 331.8 | 227.3
1442.1 | 1203.1 | 474.1 | 189.64 | 221.6782 | 324.9 | 318.4 | 301.8 | 294.1 | 567.4 | 54.1 | 18.8 | 94.3 | 5 | 250.6 | 6.9 | 383.8 | 720.2 | 777.8 | 437.9 | 466.5 | 818.6 | 661.1 | 574.8 | 714.9 | 273.8 | 386.3 | 715.9 | 99.7 | 176.3 | 239.2 | 436.3 | 581.7 | 586.1 | 454.5 | 561.2 | 171 | 340.3 | 318.8 | 216.3 | 259 | 332.3 | 227.5
1443.1 | 1204.1 | 472.9 | 189.16 | 221.1171 | 324.8 | 318.5 | 301.2 | 294.4 | 567.1 | 54.1 | 18.7 | 94.4 | 4.8 | 234.1 | 7.7 | 383.9 | 716.9 | 786.2 | 438.2 | 467 | 818.7 | 661.5 | 574.7 | 718 | 274.2 | 387 | 716.1 | 99.8 | 176.5 | 239.6 | 436.9 | 581.2 | 591 | 455.5 | 560.8 | 171.4 | 340.2 | 319.2 | 216.6 | 259.2 | 332.7 | 227.8
1444.1 | 1205.1 | 472.5 | 189 | 220.9301 | 325 | 319 | 301 | 294.3 | 570.5 | 54.1 | 18.7 | 94.4 | 5.4 | 220.2 | 7 | 384.2 | 712.6 | 789.4 | 438.7 | 467.3 | 818.3 | 661.9 | 576 | 719.9 | 274.5 | 387.9 | 715.6 | 99.9 | 176.7 | 240 | 437.5 | 579.7 | 600.4 | 456.7 | 561.3 | 171.7 | 339.9 | 319.4 | 216.7 | 259.3 | 333.1 | 228.1
1445.1 | 1206.1 | 471.7 | 188.68 | 220.556 | 325 | 321.5 | 301.6 | 293.8 | 573.7 | 54.2 | 18.7 | 94.5 | 6.3 | 228.5 | 7.2 | 384.7 | 712 | 787.6 | 439.2 | 467.6 | 817.9 | 662.3 | 578.4 | 721.3 | 274.8 | 388.9 | 715.9 | 100 | 176.9 | 240.2 | 438.3 | 583 | 605.4 | 457 | 563.2 | 172 | 339.9 | 319.4 | 216.9 | 259.5 | 333.6 | 228.3
1446.1 | 1207.1 | 472 | 188.8 | 220.6963 | 325.6 | 324.5 | 302.2 | 293 | 573.8 | 54.2 | 18.7 | 94.5 | 6 | 254.5 | 7 | 385 | 713.2 | 780.7 | 439.6 | 467.9 | 816.7 | 662.7 | 579 | 724 | 274.9 | 389.7 | 716.1 | 100.1 | 177.2 | 240.3 | 438.9 | 583 | 607.7 | 457.7 | 562.7 | 172.3 | 339.9 | 319.3 | 217.2 | 259.9 | 334 | 228.6
1447.1 | 1208.1 | 473.2 | 189.28 | 221.2574 | 325 | 324 | 301.9 | 292.9 | 572.4 | 54.3 | 18.7 | 94.5 | 5.3 | 277.3 | 6.6 | 385.2 | 712.1 | 782.2 | 439.9 | 468.2 | 816 | 663.1 | 579.4 | 730.2 | 275.2 | 390.3 | 716.6 | 100.2 | 177.4 | 240.4 | 439.7 | 584.3 | 613.9 | 458.9 | 563.5 | 172.6 | 339.7 | 319.6 | 217.5 | 260 | 334.5 | 228.9
1448.1 | 1209.1 | 473 | 189.2 | 221.1639 | 325.1 | 324.3 | 301.9 | 293.1 | 575.2 | 54.4 | 18.7 | 94.6 | 6.5 | 258.3 | 6.9 | 385.5 | 710.4 | 789.9 | 440.2 | 468.3 | 815.5 | 663.6 | 582 | 736.9 | 275.4 | 391.2 | 718 | 100.3 | 177.5 | 240.7 | 440.6 | 585.1 | 618.1 | 460.7 | 565.4 | 172.9 | 339.4 | 320.4 | 217.7 | 260.3 | 335 | 229.1
1449.1 | 1210.1 | 471.6 | 188.64 | 220.5093 | 325.4 | 325.2 | 301.9 | 292.8 | 576.3 | 54.4 | 18.7 | 94.7 | 5.9 | 269.2 | 7.9 | 385.8 | 706.9 | 772.4 | 440.6 | 468.6 | 814.9 | 664 | 582.4 | 732.4 | 275.6 | 392.1 | 717.8 | 100.5 | 177.7 | 241.2 | 441.1 | 584.4 | 622.2 | 462.1 | 563.2 | 173.2 | 339.6 | 320.1 | 218 | 260.2 | 335.5 | 229.3
1450.1 | 1211.1 | 471.8 | 188.72 | 220.6028 | 325.5 | 324.4 | 301.6 | 292.2 | 579.4 | 54.5 | 18.7 | 94.8 | 6.2 | 255 | 9.3 | 385.8 | 705 | 770.6 | 440.8 | 468.8 | 814.4 | 664.4 | 588.1 | 731.6 | 275.7 | 393.1 | 717.3 | 100.6 | 177.9 | 241.6 | 441.7 | 582.7 | 626.4 | 463.2 | 561.1 | 173.6 | 339.2 | 319.5 | 218.1 | 260.2 | 335.9 | 229.5
1451.1 | 1212.1 | 471.7 | 188.68 | 220.556 | 326.3 | 322.9 | 302.5 | 291.8 | 582.3 | 54.5 | 18.7 | 94.9 | 6.3 | 260.1 | 10 | 386.1 | 709.3 | 775.1 | 441.1 | 469.1 | 814.8 | 664.9 | 596.6 | 726.8 | 276 | 393.9 | 717.3 | 100.7 | 178.1 | 241.7 | 442.7 | 587.2 | 626.2 | 464.3 | 561.4 | 173.8 | 338.9 | 319.1 | 218.3 | 260.4 | 336.3 | 229.8
1452.1 | 1213.1 | 472.1 | 188.84 | 220.7431 | 326.4 | 321.5 | 303.5 | 292 | 580.7 | 54.4 | 18.7 | 95.1 | 4.6 | 262.6 | 10.3 | 386.1 | 718.8 | 779.5 | 441.2 | 469.5 | 814.4 | 665.5 | 596.5 | 721.7 | 276.2 | 394.8 | 717.1 | 100.8 | 178.3 | 241.7 | 443.4 | 583.9 | 628.6 | 464.2 | 563.1 | 174.1 | 338.9 | 319.2 | 218.5 | 260.7 | 336.8 | 230
1453.1 | 1214.1 | 472.4 | 188.96 | 220.8834 | 327.3 | 320.3 | 303.9 | 292.4 | 573.8 | 54.4 | 18.7 | 95.2 | 4.7 | 246.9 | 9.7 | 386.2 | 713.9 | 762 | 441.4 | 469.9 | 813.6 | 665.9 | 595 | 712.6 | 276.4 | 395.6 | 716.1 | 100.9 | 178.5 | 241.8 | 443.9 | 581 | 620.6 | 463.9 | 560.4 | 174.4 | 339.5 | 319.4 | 218.9 | 260.8 | 337.2 | 230.3
1454.1 | 1215.1 | 471.7 | 188.68 | 220.556 | 326.9 | 321 | 303.3 | 292.9 | 579.8 | 54.4 | 18.7 | 95.3 | 5.5 | 234.3 | 8 | 386.2 | 716.3 | 743.2 | 441.5 | 470.3 | 812.7 | 666.4 | 595.6 | 701 | 276.6 | 396.4 | 716.1 | 101 | 178.7 | 242.2 | 444.4 | 585.2 | 620.2 | 463.7 | 562.7 | 174.7 | 341 | 319.9 | 219.3 | 261.1 | 337.6 | 230.6
1455.1 | 1216.1 | 472.9 | 189.16 | 221.1171 | 327.6 | 322.2 | 303 | 293.9 | 580.6 | 54.4 | 18.7 | 95.6 | 6.6 | 221.4 | 8.4 | 386.3 | 717.9 | 731.1 | 441.7 | 470.7 | 812.7 | 666.8 | 595.3 | 696.4 | 276.7 | 397.3 | 717 | 101.1 | 179 | 242.4 | 444.9 | 583.9 | 617.9 | 463.7 | 561.5 | 174.9 | 341.5 | 320.3 | 219.7 | 261.2 | 338.1 | 230.9
1456.1 | 1217.1 | 472.9 | 189.16 | 221.1171 | 327.7 | 321.9 | 302.7 | 294 | 594.3 | 54.4 | 18.7 | 95.8 | 7 | 220.5 | 7.5 | 386.5 | 718.4 | 731.8 | 441.8 | 471.1 | 811.8 | 667.2 | 593.2 | 696.9 | 276.9 | 398.3 | 717.8 | 101.3 | 179.2 | 242.6 | 445.6 | 588.2 | 624.8 | 464.6 | 565 | 175.2 | 342.1 | 321 | 220.2 | 261.5 | 338.5 | 231.1
1457.1 | 1218.1 | 471.7 | 188.68 | 220.556 | 328.3 | 320.9 | 302.9 | 293.9 | 608.7 | 54.5 | 18.7 | 96 | 7.2 | 216.9 | 6.1 | 386.6 | 719.1 | 740 | 442 | 471.6 | 811.7 | 667.6 | 596.8 | 701 | 277 | 399.2 | 718.1 | 101.4 | 179.3 | 243 | 446.3 | 593.5 | 634.3 | 465.9 | 568.2 | 175.5 | 342.8 | 321.5 | 220.6 | 261.7 | 339 | 231.4
1458.1 | 1219.1 | 471.7 | 188.68 | 220.556 | 329.1 | 320.1 | 303.1 | 294 | 611.3 | 54.5 | 18.7 | 96.2 | 5.9 | 276.2 | 5.6 | 386.8 | 720.4 | 746.9 | 442.4 | 471.9 | 811.9 | 668.1 | 598.3 | 705.4 | 277.2 | 400.2 | 718 | 101.5 | 179.5 | 243.2 | 447 | 593.8 | 630.1 | 466.3 | 568.2 | 175.7 | 343 | 321.5 | 220.9 | 261.8 | 339.5 | 231.7
1459.1 | 1220.1 | 471.5 | 188.6 | 220.4625 | 329.8 | 320.9 | 303.7 | 293.8 | 610 | 54.5 | 18.7 | 96.3 | 6.7 | 247.4 | 7 | 386.9 | 721.2 | 757.5 | 442.7 | 472.2 | 812.8 | 668.5 | 596.7 | 709.5 | 277.4 | 401.2 | 717.4 | 101.6 | 179.7 | 243.3 | 447.5 | 590.8 | 626.7 | 466.7 | 565.1 | 176 | 342.9 | 321.2 | 221.2 | 262 | 340 | 231.9
1460.1 | 1221.1 | 472.5 | 189 | 220.9301 | 331.2 | 320.4 | 304.3 | 293.8 | 607.6 | 54.6 | 18.7 | 96.4 | 5.6 | 234.6 | 9.8 | 387 | 719.4 | 756.3 | 442.8 | 472.7 | 813.1 | 668.9 | 595.3 | 709.5 | 277.5 | 402.2 | 717.5 | 101.7 | 179.9 | 243.6 | 448.1 | 587.9 | 621.5 | 467.2 | 563.2 | 176.3 | 342.8 | 320.8 | 221.5 | 262 | 340.5 | 232.2
1461.1 | 1222.1 | 473.2 | 189.28 | 221.2574 | 332.8 | 320.1 | 304.3 | 293.8 | 604.2 | 54.6 | 18.7 | 96.4 | 4.9 | 225.5 | 10.4 | 387.1 | 717.3 | 763.7 | 443 | 473.3 | 813.5 | 669.3 | 593 | 707.9 | 277.6 | 402.9 | 716.8 | 101.9 | 180.1 | 243.8 | 448.6 | 585.8 | 617.6 | 467.4 | 562.7 | 176.6 | 342.9 | 320.5 | 221.9 | 262.1 | 340.9 | 232.4
1462.1 | 1223.1 | 473.2 | 189.28 | 221.2574 | 333.9 | 319.8 | 304 | 293.7 | 603.2 | 54.7 | 18.7 | 96.3 | 4.9 | 221.6 | 8.6 | 387.3 | 719.7 | 765.4 | 443.3 | 473.7 | 814.9 | 669.7 | 593 | 714.8 | 277.9 | 403.7 | 718.6 | 102 | 180.4 | 244.1 | 449.1 | 585.8 | 618.4 | 467.4 | 563.4 | 176.9 | 342.9 | 320.4 | 222.1 | 262.3 | 341.4 | 232.7
1463.1 | 1224.1 | 473.4 | 189.36 | 221.3509 | 334.4 | 319.8 | 304 | 293.7 | 602.3 | 54.7 | 18.7 | 96.3 | 5.4 | 246.8 | 9.6 | 387.3 | 716.8 | 757.4 | 443.5 | 474 | 815.9 | 670 | 592.3 | 709.5 | 278.1 | 404.3 | 720.2 | 102.1 | 180.6 | 244.2 | 449.7 | 584.7 | 615.4 | 467.2 | 562.6 | 177.2 | 342.7 | 320.4 | 222.3 | 262.6 | 341.9 | 232.9
1464.1 | 1225.1 | 471.4 | 188.56 | 220.4158 | 334.8 | 319.1 | 304.1 | 293.4 | 608.4 | 54.7 | 18.7 | 96.3 | 5.7 | 243.1 | 10.9 | 387.5 | 720.7 | 764 | 443.9 | 474.2 | 816.2 | 670.5 | 591.6 | 708.1 | 278.3 | 405 | 721.8 | 102.2 | 180.8 | 244.5 | 450.6 | 589.5 | 619.7 | 467.8 | 566 | 177.5 | 342.7 | 320.6 | 222.6 | 262.7 | 342.4 | 233.2
1465.1 | 1226.1 | 472.3 | 188.92 | 220.8366 | 334.8 | 318.2 | 304 | 293.5 | 611.7 | 54.7 | 18.7 | 96.3 | 6.1 | 231.9 | 10.6 | 387.8 | 722.3 | 772 | 444.3 | 474.4 | 816.3 | 670.8 | 590.4 | 708.9 | 278.5 | 405.8 | 721.1 | 102.4 | 181 | 244.9 | 451.1 | 588.7 | 616.6 | 467.8 | 565.9 | 177.8 | 342.7 | 320.4 | 222.9 | 262.9 | 342.9 | 233.4
1466.1 | 1227.1 | 471.9 | 188.76 | 220.6496 | 337.1 | 319.6 | 304.7 | 293.9 | 615.7 | 54.7 | 18.7 | 96.3 | 5.8 | 231.8 | 9 | 388.2 | 722.6 | 782.3 | 444.7 | 474.7 | 816.6 | 671.2 | 590.1 | 711.4 | 278.6 | 406.5 | 720.6 | 102.5 | 181.1 | 245.1 | 451.5 | 588.1 | 623.6 | 468.1 | 566.3 | 178.1 | 342.6 | 320.2 | 223 | 263 | 343.4 | 233.6
1467.1 | 1228.1 | 470.4 | 188.16 | 219.9482 | 337.2 | 324.9 | 305.7 | 293.9 | 619.9 | 54.7 | 18.7 | 96.3 | 5.3 | 238.4 | 8.3 | 388.2 | 719.8 | 786.1 | 444.9 | 475 | 817 | 671.5 | 590.3 | 714.5 | 278.7 | 407.1 | 719.4 | 102.6 | 181.3 | 245.5 | 452 | 588.2 | 633.8 | 469.1 | 568.1 | 178.4 | 342.4 | 319.7 | 223.1 | 263 | 343.9 | 233.9
1468.1 | 1229.1 | 471.6 | 188.64 | 220.5093 | 336.8 | 327.5 | 306.3 | 293.4 | 621.1 | 54.7 | 18.7 | 96.4 | 6.2 | 251.1 | 8.3 | 388.6 | 720.9 | 789.4 | 445.3 | 475.3 | 816.8 | 671.8 | 591.3 | 717.5 | 278.8 | 407.8 | 719 | 102.7 | 181.4 | 245.9 | 452.3 | 587.7 | 631.4 | 468.5 | 567.2 | 178.6 | 342.1 | 319.4 | 223.3 | 263.1 | 344.4 | 234.1
1469.1 | 1230.1 | 472.2 | 188.88 | 220.7898 | 336.3 | 327 | 307.4 | 292.7 | 623.3 | 54.7 | 18.7 | 96.6 | 6.1 | 244.9 | 7.6 | 388.9 | 717.7 | 790.1 | 445.6 | 475.7 | 816.5 | 672.2 | 593.7 | 721.3 | 278.9 | 408.4 | 719 | 102.9 | 181.6 | 246.2 | 453 | 588.8 | 638.8 | 468.6 | 567.5 | 178.9 | 342.1 | 319.3 | 223.4 | 263.1 | 344.8 | 234.3
1470.1 | 1231.1 | 472.1 | 188.84 | 220.7431 | 335.2 | 326 | 308.1 | 292.6 | 628.1 | 54.7 | 18.7 | 96.7 | 5.4 | 256.9 | 6.7 | 389.3 | 722.1 | 789.1 | 446 | 476 | 816.1 | 672.5 | 599.7 | 723.9 | 279.1 | 409.1 | 719.2 | 103 | 181.8 | 246.3 | 453.6 | 591.1 | 637.9 | 468.8 | 569.6 | 179.2 | 342 | 319 | 223.6 | 263.2 | 345.2 | 234.6
1471.1 | 1232.1 | 472.6 | 189.04 | 220.9769 | 335 | 326.2 | 308.3 | 292.7 | 628.2 | 54.7 | 18.7 | 96.7 | 6 | 245.3 | 6.3 | 389.6 | 720 | 792.5 | 446.4 | 476.2 | 815.8 | 672.7 | 600 | 725.4 | 279.2 | 409.7 | 718.2 | 103.1 | 182 | 246.5 | 454.1 | 588.8 | 637.4 | 469 | 568.1 | 179.4 | 342.1 | 319.1 | 223.7 | 263.3 | 345.7 | 234.8
1472.1 | 1233.1 | 471.7 | 188.68 | 220.556 | 335.3 | 327.5 | 308.2 | 292.6 | 626.2 | 54.7 | 18.7 | 96.8 | 5.9 | 209.6 | 6.3 | 389.8 | 726.7 | 792.5 | 446.7 | 476.6 | 815.5 | 673 | 599.7 | 725 | 279.4 | 410.4 | 716.9 | 103.2 | 182.2 | 246.7 | 454.8 | 588.9 | 639 | 469.7 | 568.9 | 179.7 | 342.4 | 320 | 224 | 263.5 | 346.1 | 235
1473.1 | 1234.1 | 471.1 | 188.44 | 220.2755 | 334.9 | 330.6 | 308.2 | 292.3 | 617.8 | 54.7 | 18.7 | 96.8 | 6.5 | 230.1 | 6.4 | 390.1 | 723.1 | 790 | 447 | 476.8 | 814.5 | 673.4 | 598.4 | 725.7 | 279.5 | 411.1 | 717.1 | 103.4 | 182.4 | 246.9 | 455.4 | 586.7 | 633.8 | 470 | 567.9 | 179.9 | 342.7 | 320.3 | 224.3 | 263.6 | 346.6 | 235.2
1474.1 | 1235.1 | 472 | 188.8 | 220.6963 | 334.7 | 332.7 | 307.5 | 292.5 | 612 | 54.7 | 18.7 | 96.9 | 7 | 250.9 | 5.8 | 390.5 | 721 | 786.2 | 447.3 | 477 | 813.3 | 673.7 | 598 | 724.4 | 279.5 | 411.7 | 717.5 | 103.5 | 182.7 | 247.2 | 456.1 | 588.3 | 638.9 | 470.4 | 569.8 | 180.1 | 343.2 | 320.5 | 224.7 | 263.8 | 347.1 | 235.5
1475.1 | 1236.1 | 471 | 188.4 | 220.2287 | 333.8 | 332.2 | 307.2 | 293.3 | 606.7 | 54.7 | 18.7 | 97.1 | 6.8 | 232.7 | 5.6 | 390.5 | 721.3 | 794.8 | 447.5 | 477.3 | 812.8 | 674 | 599.7 | 728.8 | 279.6 | 412.4 | 716.9 | 103.6 | 182.9 | 247.4 | 456.7 | 587.1 | 639.4 | 470.6 | 571.2 | 180.4 | 343.4 | 320.9 | 224.8 | 264 | 347.6 | 235.7
1476.1 | 1237.1 | 471.4 | 188.56 | 220.4158 | 333.4 | 332.1 | 306.7 | 293.3 | 600.4 | 54.7 | 18.7 | 97.2 | 6.3 | 252.9 | 6.1 | 390.7 | 720.3 | 801.8 | 447.9 | 477.6 | 812.3 | 674.3 | 599.8 | 728.5 | 279.7 | 413.1 | 715.6 | 103.8 | 183.1 | 247.9 | 457.1 | 586.1 | 642.8 | 471 | 572.4 | 180.6 | 343.6 | 320.7 | 225 | 264.1 | 348.1 | 236
1477.1 | 1238.1 | 471.2 | 188.48 | 220.3223 | 333.8 | 334.2 | 305.8 | 293 | 598.3 | 54.7 | 18.6 | 97.3 | 5.8 | 246.4 | 5.5 | 390.8 | 716.9 | 806.9 | 448.1 | 478 | 811.9 | 674.6 | 599.9 | 730.7 | 279.7 | 413.8 | 714.2 | 103.9 | 183.4 | 248.4 | 457.5 | 585.2 | 647.9 | 471.1 | 572.3 | 180.9 | 343.5 | 320.8 | 225.1 | 264.1 | 348.6 | 236.3
1478.1 | 1239.1 | 472.5 | 189 | 220.9301 | 333 | 333.4 | 305.4 | 293.3 | 600.7 | 54.7 | 18.6 | 97.5 | 5 | 248.3 | 6.4 | 390.9 | 714.7 | 807.5 | 448.2 | 478.3 | 812.2 | 674.9 | 600.8 | 738.5 | 279.8 | 414.5 | 714.9 | 104 | 183.6 | 248.7 | 458.2 | 587 | 659.4 | 471.5 | 575.9 | 181.1 | 343.2 | 320.1 | 225.2 | 264.3 | 349.1 | 236.5
1479.1 | 1240.1 | 472.7 | 189.08 | 221.0236 | 331.6 | 331.5 | 305.6 | 292.8 | 599.1 | 54.8 | 18.6 | 97.6 | 5.7 | 248.7 | 9.1 | 391 | 714.5 | 814.9 | 448.4 | 478.6 | 812.3 | 675.2 | 600.8 | 742.7 | 279.9 | 415.1 | 715.4 | 104.2 | 183.9 | 248.8 | 458.7 | 585.6 | 656.6 | 471.4 | 575.1 | 181.4 | 343 | 319.7 | 225.2 | 264.3 | 349.6 | 236.7
1480.1 | 1241.1 | 472.6 | 189.04 | 220.9769 | 330.7 | 330.5 | 305.9 | 292.3 | 593.1 | 54.8 | 18.6 | 97.7 | 5.5 | 257.1 | 10.8 | 391.2 | 713 | 816.5 | 448.8 | 478.9 | 812.3 | 675.6 | 598.8 | 746.5 | 280 | 415.7 | 715.7 | 104.3 | 184.1 | 249 | 459.3 | 582.9 | 649.5 | 471.3 | 572.7 | 181.6 | 342.8 | 319.5 | 225.4 | 264.4 | 350.1 | 236.9
1481.1 | 1242.1 | 470.9 | 188.36 | 220.182 | 330.5 | 331.5 | 305.9 | 292 | 588.3 | 54.8 | 18.6 | 97.8 | 5.2 | 271.6 | 10.4 | 391.5 | 714.3 | 814.9 | 449.1 | 479.2 | 811.8 | 675.8 | 597 | 745.7 | 280.1 | 416.2 | 716.3 | 104.4 | 184.3 | 249.2 | 459.9 | 582.9 | 644 | 471.6 | 571.9 | 181.8 | 342.8 | 318.8 | 225.6 | 264.4 | 350.6 | 237.1
1482.1 | 1243.1 | 471.4 | 188.56 | 220.4158 | 330.4 | 333 | 305.9 | 291.8 | 587.5 | 54.9 | 18.6 | 97.7 | 5.3 | 245.5 | 10 | 391.6 | 717.1 | 808.1 | 449.2 | 479.5 | 812.2 | 676.1 | 597.3 | 747.1 | 280.2 | 416.7 | 716.3 | 104.6 | 184.6 | 249.5 | 460.6 | 587.1 | 648.7 | 471.8 | 573.6 | 182.1 | 342.8 | 318.3 | 225.9 | 264.4 | 351 | 237.4
1483.1 | 1244.1 | 468.7 | 187.48 | 219.1533 | 330.3 | 335.9 | 306.2 | 291.6 | 590.4 | 54.9 | 18.6 | 97.8 | 5.2 | 258.2 | 10.4 | 391.8 | 717.9 | 791 | 449.5 | 479.8 | 813.1 | 676.3 | 597.2 | 740.1 | 280.3 | 417.2 | 716.2 | 104.7 | 184.8 | 249.8 | 461.1 | 588.2 | 654.6 | 471.8 | 574.1 | 182.3 | 342.9 | 318 | 226 | 264.6 | 351.4 | 237.6
1484.1 | 1245.1 | 471 | 188.4 | 220.2287 | 329.7 | 335.3 | 306.8 | 291.3 | 592 | 54.9 | 18.6 | 97.8 | 5.6 | 246.9 | 9 | 391.8 | 722.2 | 791.6 | 449.6 | 480 | 814.1 | 676.7 | 601.2 | 743 | 280.4 | 417.6 | 717.9 | 104.9 | 185 | 250.2 | 461.8 | 587.5 | 658.3 | 471.9 | 574.4 | 182.5 | 342.9 | 318 | 226.2 | 264.8 | 351.8 | 237.8
1485.1 | 1246.1 | 470.2 | 188.08 | 219.8547 | 329.9 | 333.5 | 307.1 | 291.3 | 592.4 | 54.9 | 18.6 | 97.8 | 5.1 | 258.9 | 7.4 | 392.1 | 722.5 | 800.6 | 449.9 | 480.2 | 814.5 | 677 | 603.1 | 752.1 | 280.6 | 418 | 719 | 105 | 185.2 | 250.9 | 462.4 | 587 | 662.9 | 471.8 | 577.9 | 182.7 | 342.6 | 318.1 | 226.4 | 265 | 352.3 | 238
1486.1 | 1247.1 | 470.9 | 188.36 | 220.182 | 330.1 | 332.6 | 307.5 | 291 | 593 | 54.9 | 18.6 | 97.7 | 5.2 | 259.7 | 7.8 | 392.3 | 718.2 | 796.1 | 450.2 | 480.5 | 814.5 | 677.2 | 602.7 | 756.1 | 280.7 | 418.3 | 719.7 | 105.1 | 185.4 | 251 | 462.9 | 585.8 | 667.5 | 472.1 | 579.4 | 183 | 342.7 | 317.8 | 226.6 | 265 | 352.8 | 238.3
1487.1 | 1248.1 | 473 | 189.2 | 221.1639 | 328.9 | 331.8 | 308 | 291.2 | 594 | 55 | 18.6 | 97.7 | 5.1 | 256.3 | 7.5 | 392.3 | 715.2 | 790.9 | 450.3 | 480.8 | 815.1 | 677.4 | 601.2 | 755.7 | 280.8 | 418.6 | 720 | 105.3 | 185.6 | 251.2 | 463.5 | 585.5 | 667.7 | 472.5 | 578.4 | 183.2 | 342.9 | 317.6 | 226.9 | 265 | 353.3 | 238.5
1488.1 | 1249.1 | 474.2 | 189.68 | 221.725 | 328.5 | 330.6 | 308.5 | 291.2 | 599.2 | 55 | 18.6 | 97.6 | 5.6 | 243.5 | 7.4 | 392.4 | 715.5 | 781 | 450.5 | 481 | 815.2 | 677.6 | 601.7 | 753 | 281 | 419 | 720.3 | 105.4 | 185.8 | 251.7 | 464.1 | 587.5 | 675.5 | 472.8 | 581 | 183.4 | 342.8 | 317.9 | 227 | 265 | 353.7 | 238.7
1489.1 | 1250.1 | 474.1 | 189.64 | 221.6782 | 327.6 | 329.2 | 309.3 | 291.3 | 599.2 | 55 | 18.6 | 97.6 | 6.1 | 261.6 | 8.2 | 392.7 | 709.1 | 773.9 | 450.9 | 481.2 | 816 | 677.8 | 603.9 | 747.8 | 281.2 | 419.3 | 719.7 | 105.6 | 186 | 252 | 464.5 | 588 | 676.9 | 472.5 | 585 | 183.6 | 342.8 | 317.9 | 227.3 | 265.1 | 354.2 | 239
1490.1 | 1251.1 | 474.1 | 189.64 | 221.6782 | 327.1 | 328.2 | 309.9 | 291.3 | 599.4 | 55.1 | 18.6 | 97.7 | 6.5 | 249.8 | 9 | 392.8 | 706.1 | 768.1 | 451.1 | 481.4 | 817 | 678.1 | 605.7 | 751.7 | 281.3 | 419.8 | 720.6 | 105.7 | 186.3 | 252.1 | 465.2 | 590.1 | 672.1 | 473.1 | 583.5 | 183.9 | 343.2 | 317.7 | 227.7 | 265.1 | 354.6 | 239.2
1491.1 | 1252.1 | 468.8 | 187.52 | 219.2001 | 327.3 | 327.6 | 309.9 | 291.4 | 601.1 | 55.1 | 18.6 | 97.8 | 6.6 | 254.8 | 9 | 393 | 709 | 768.1 | 451.4 | 481.6 | 817.7 | 678.3 | 606.3 | 748.9 | 281.5 | 420.4 | 721.2 | 105.9 | 186.5 | 252.3 | 465.9 | 591.8 | 674.5 | 473.8 | 584.7 | 184.1 | 343.6 | 317.3 | 228 | 265.2 | 355 | 239.4
1492.1 | 1253.1 | 470.7 | 188.28 | 220.0885 | 327.3 | 327 | 310.2 | 291.8 | 604.2 | 55.1 | 18.6 | 98 | 6.8 | 261.9 | 9.9 | 393.1 | 712.3 | 773.1 | 451.6 | 481.8 | 817.6 | 678.6 | 608.4 | 751.6 | 281.7 | 421.1 | 722.4 | 106 | 186.7 | 252.8 | 466.4 | 593.8 | 678.4 | 473.8 | 583.8 | 184.3 | 344 | 317.1 | 228.3 | 265.4 | 355.5 | 239.7
1493.1 | 1254.1 | 471.5 | 188.6 | 220.4625 | 327.1 | 326.2 | 310.7 | 292.2 | 606.8 | 55.2 | 18.6 | 98.1 | 7.2 | 253.6 | 12.3 | 393.2 | 716 | 769.9 | 451.7 | 482 | 817.5 | 678.9 | 610.2 | 749.6 | 281.8 | 421.8 | 723.8 | 106.2 | 187 | 252.9 | 467.1 | 599.8 | 673.4 | 474.1 | 582.7 | 184.5 | 344.6 | 317.1 | 228.7 | 265.5 | 356 | 239.9
1494.1 | 1255.1 | 471.6 | 188.64 | 220.5093 | 327.2 | 326.3 | 311 | 292.3 | 605.4 | 55.3 | 18.6 | 98.2 | 6.7 | 259.6 | 12.7 | 393.5 | 723.2 | 776.6 | 452.2 | 482.2 | 817 | 679.2 | 608.7 | 742.3 | 282 | 422.5 | 723.9 | 106.4 | 187.2 | 253 | 467.8 | 601.1 | 670.8 | 474.7 | 584 | 184.7 | 345.2 | 317.8 | 229 | 265.7 | 356.5 | 240.2
1495.1 | 1256.1 | 473 | 189.2 | 221.1639 | 328.2 | 325.9 | 310.6 | 292.9 | 599 | 55.4 | 18.6 | 98.3 | 7 | 248.3 | 12.3 | 393.8 | 720.3 | 779 | 452.5 | 482.5 | 817.1 | 679.5 | 605.3 | 743 | 282.2 | 423.2 | 725 | 106.5 | 187.5 | 253.3 | 468.2 | 599.4 | 661.3 | 475.1 | 582.5 | 184.9 | 345.9 | 317.9 | 229.4 | 265.9 | 357 | 240.5
1496.1 | 1257.1 | 472.7 | 189.08 | 221.0236 | 329.4 | 325.4 | 310 | 293.5 | 595 | 55.4 | 18.6 | 98.4 | 6.7 | 251.9 | 11.7 | 394 | 717.2 | 772.2 | 452.9 | 482.7 | 817.1 | 679.7 | 603.6 | 740.5 | 282.4 | 423.9 | 723.9 | 106.7 | 187.8 | 253.6 | 468.9 | 600 | 656.6 | 475.6 | 583 | 185.1 | 346.4 | 318.7 | 229.7 | 266.2 | 357.6 | 240.7
1497.1 | 1258.1 | 474.8 | 189.92 | 222.0055 | 330 | 325.7 | 309.7 | 294 | 594.3 | 55.5 | 18.6 | 98.5 | 6.3 | 238.3 | 11.1 | 394.2 | 713.7 | 764.8 | 453.1 | 482.9 | 815.7 | 680 | 601.2 | 730.5 | 282.6 | 424.5 | 723.7 | 106.8 | 188 | 253.7 | 469.2 | 599.9 | 648.2 | 475.7 | 582.6 | 185.4 | 347 | 319.3 | 230.1 | 266.4 | 358.1 | 241
1498.1 | 1259.1 | 474.3 | 189.72 | 221.7717 | 330.3 | 325.6 | 309.9 | 294.5 | 589.5 | 55.6 | 18.6 | 98.5 | 5.8 | 241.7 | 11.4 | 394.4 | 715 | 772.7 | 453.4 | 483.1 | 815.1 | 680.3 | 599.9 | 726.3 | 282.8 | 425.2 | 723.7 | 107 | 188.2 | 253.8 | 469.6 | 597.8 | 636 | 476.2 | 578.6 | 185.6 | 347.8 | 319.8 | 230.5 | 266.6 | 358.6 | 241.3
1499.1 | 1260.1 | 472.9 | 189.16 | 221.1171 | 330.7 | 325.1 | 310.1 | 294.9 | 583.1 | 55.7 | 18.6 | 98.7 | 5.3 | 233.7 | 12.4 | 394.6 | 712.3 | 773.6 | 453.7 | 483.3 | 814.4 | 680.6 | 599.7 | 720.6 | 283 | 425.9 | 722.9 | 107.1 | 188.4 | 254.1 | 470.1 | 597.6 | 634.2 | 476.6 | 579.3 | 185.9 | 348.5 | 320.8 | 230.9 | 267 | 359.1 | 241.6
1500.1 | 1261.1 | 472.5 | 189 | 220.9301 | 330.5 | 325 | 310.3 | 295.8 | 590 | 55.7 | 18.6 | 98.8 | 5.6 | 243.7 | 13.7 | 394.8 | 709.2 | 773.9 | 454 | 483.5 | 814.4 | 680.9 | 600.3 | 717.1 | 283.1 | 426.7 | 722.5 | 107.3 | 188.6 | 254.4 | 470.8 | 607.3 | 644 | 477.4 | 584 | 186.2 | 349.2 | 321.4 | 231.2 | 267.2 | 359.6 | 241.8
1501.1 | 1262.1 | 473 | 189.2 | 221.1639 | 330.9 | 325.5 | 310.3 | 296.7 | 592.8 | 55.7 | 18.6 | 98.9 | 5.9 | 251 | 12.2 | 395 | 709.4 | 773.1 | 454.3 | 483.7 | 814.1 | 681.2 | 598.6 | 718.7 | 283.3 | 427.5 | 722.2 | 107.5 | 188.9 | 254.6 | 471.2 | 606.4 | 639.8 | 478.3 | 581.7 | 186.5 | 349.1 | 322.1 | 231.6 | 267.5 | 360.1 | 242.1
1502.1 | 1263.1 | 473 | 189.2 | 221.1639 | 331.4 | 325.7 | 310.6 | 297.1 | 591.5 | 55.8 | 18.5 | 98.9 | 5.2 | 251.6 | 13.3 | 395.1 | 710.9 | 760.1 | 454.5 | 483.9 | 813.5 | 681.4 | 597.8 | 717.5 | 283.5 | 428.3 | 722.7 | 107.6 | 189.1 | 254.9 | 471.8 | 606.2 | 637.7 | 479.1 | 580.2 | 186.8 | 349.2 | 322.7 | 231.8 | 267.7 | 360.6 | 242.3
1503.1 | 1264.1 | 473.7 | 189.48 | 221.4912 | 333.1 | 325.5 | 310.7 | 297.5 | 590 | 55.8 | 18.5 | 99 | 5.5 | 231 | 13.1 | 395.2 | 722.1 | 762.9 | 454.7 | 484.2 | 813.2 | 681.6 | 598.3 | 714.3 | 283.7 | 429 | 722.6 | 107.8 | 189.4 | 255.2 | 472.2 | 604.7 | 642.1 | 479.5 | 581.5 | 187.1 | 349.7 | 323.6 | 232.2 | 267.9 | 361.1 | 242.6
1504.1 | 1265.1 | 471.6 | 188.64 | 220.5093 | 335.6 | 325.6 | 311.1 | 298.3 | 591.5 | 55.9 | 18.5 | 99.2 | 6.3 | 226.6 | 11.3 | 395.5 | 721.8 | 765.6 | 455 | 484.4 | 813.8 | 681.9 | 599 | 718 | 283.9 | 429.8 | 723.5 | 107.9 | 189.6 | 255.4 | 472.7 | 604 | 654.6 | 480.2 | 582.5 | 187.4 | 349.8 | 324 | 232.5 | 268 | 361.6 | 242.8
1505.1 | 1266.1 | 472.1 | 188.84 | 220.7431 | 338.9 | 325.9 | 311 | 298.8 | 590 | 55.9 | 18.5 | 99.4 | 7.4 | 234.8 | 9.6 | 395.7 | 719 | 770.7 | 455.2 | 484.6 | 814.5 | 682.2 | 600.3 | 721.4 | 284.1 | 430.6 | 724.3 | 108.1 | 189.9 | 255.7 | 473.1 | 600.6 | 652.6 | 480.6 | 581.5 | 187.8 | 350 | 325.8 | 232.8 | 268.4 | 362.2 | 243.1
1506.1 | 1267.1 | 472 | 188.8 | 220.6963 | 342 | 327.4 | 311.1 | 298.6 | 586.1 | 56 | 18.5 | 99.4 | 6.8 | 228.3 | 8.9 | 396 | 720.7 | 769.9 | 455.5 | 484.8 | 814.8 | 682.5 | 599.9 | 723.8 | 284.3 | 431.4 | 724.5 | 108.3 | 190.2 | 255.9 | 473.2 | 598.1 | 642.9 | 480.5 | 579.3 | 188.1 | 350.2 | 325.9 | 233.1 | 268.7 | 362.7 | 243.4
1507.1 | 1268.1 | 471.3 | 188.52 | 220.369 | 344.1 | 328.2 | 311.8 | 299 | 581.2 | 56 | 18.5 | 99.5 | 7.1 | 197.5 | 7.8 | 396 | 723.1 | 757 | 455.6 | 485 | 814.1 | 682.7 | 599.4 | 717.7 | 284.5 | 432.2 | 725 | 108.4 | 190.4 | 256 | 473.3 | 595.4 | 630.2 | 480.3 | 576.6 | 188.4 | 350.1 | 326.2 | 233.4 | 269.1 | 363.1 | 243.7
1508.1 | 1269.1 | 472.7 | 189.08 | 221.0236 | 344.1 | 327.7 | 312.1 | 299.4 | 592 | 56.1 | 18.5 | 99.6 | 6.8 | 249.9 | 7 | 396.2 | 720.5 | 751.8 | 455.8 | 485.3 | 813 | 682.9 | 600.5 | 716.1 | 284.7 | 433 | 725.9 | 108.6 | 190.6 | 256.3 | 473.9 | 599.8 | 629 | 480.7 | 575.9 | 188.8 | 350.6 | 326.5 | 233.7 | 269.3 | 363.5 | 243.9
1509.1 | 1270.1 | 472.7 | 189.08 | 221.0236 | 343.7 | 327.2 | 311.9 | 299.6 | 603.6 | 56.1 | 18.5 | 99.5 | 6.1 | 229.6 | 7.1 | 396.6 | 716.7 | 757.2 | 456.2 | 485.5 | 812.8 | 683.2 | 602.1 | 723.7 | 284.9 | 433.7 | 727 | 108.8 | 190.9 | 256.6 | 474.7 | 604.6 | 631.9 | 481.7 | 577.3 | 189.1 | 350.9 | 327.2 | 234 | 269.5 | 363.9 | 244.2
1510.1 | 1271.1 | 472.9 | 189.16 | 221.1171 | 344.5 | 326.3 | 312.6 | 300 | 599.3 | 56.2 | 18.5 | 99.4 | 6.1 | 236.5 | 6.6 | 396.7 | 715.6 | 759.4 | 456.3 | 485.7 | 812.1 | 683.5 | 602.8 | 715.9 | 285.1 | 434.5 | 727.1 | 109 | 191.1 | 256.7 | 475.1 | 602 | 624.3 | 482.1 | 577.8 | 189.4 | 351.2 | 327 | 234.3 | 269.7 | 364.5 | 244.5
1511.1 | 1272.1 | 473.2 | 189.28 | 221.2574 | 344.8 | 325.6 | 313.3 | 300.3 | 594.4 | 56.2 | 18.5 | 99.3 | 6.9 | 233.5 | 7.8 | 396.7 | 714.5 | 752.3 | 456.2 | 485.9 | 811.9 | 683.8 | 602 | 718.2 | 285.3 | 435.2 | 727.2 | 109.1 | 191.3 | 256.9 | 475.4 | 601.8 | 624.8 | 482.3 | 577.6 | 189.7 | 351.6 | 327.5 | 234.6 | 269.9 | 365 | 244.7
1512.1 | 1273.1 | 471.7 | 188.68 | 220.556 | 344.4 | 325.9 | 313.5 | 300.5 | 595.9 | 56.2 | 18.5 | 99.3 | 6.5 | 225.5 | 6.8 | 396.8 | 712.5 | 747.5 | 456.1 | 486.2 | 812 | 684.1 | 602.7 | 718.7 | 285.5 | 435.9 | 726.9 | 109.3 | 191.5 | 257.2 | 476 | 603.7 | 623.1 | 482.5 | 577.8 | 190.1 | 352.5 | 328.2 | 235.2 | 270.2 | 365.5 | 245
1513.1 | 1274.1 | 472.4 | 188.96 | 220.8834 | 343.4 | 326 | 313.6 | 301.1 | 596.5 | 56.3 | 18.5 | 99.3 | 6.3 | 200.8 | 6.4 | 397.1 | 713.4 | 747.2 | 456.4 | 486.4 | 811.6 | 684.3 | 604.3 | 714 | 285.6 | 436.7 | 726.7 | 109.5 | 191.8 | 257.5 | 476.5 | 604.1 | 633.5 | 483.1 | 580.4 | 190.4 | 353.1 | 328.5 | 235.5 | 270.4 | 365.9 | 245.3
1514.1 | 1275.1 | 472.4 | 188.96 | 220.8834 | 343 | 325.6 | 314.3 | 302.1 | 599.8 | 56.3 | 18.5 | 99.4 | 5.9 | 221.3 | 5.3 | 397.4 | 720.3 | 748.9 | 456.6 | 486.6 | 810.8 | 684.6 | 604.4 | 711.8 | 285.9 | 437.5 | 726.1 | 109.6 | 192 | 257.8 | 477.1 | 607 | 631.7 | 483.9 | 580.8 | 190.7 | 353.8 | 329.7 | 235.9 | 270.8 | 366.4 | 245.6
1515.1 | 1276.1 | 472.8 | 189.12 | 221.0704 | 343.6 | 325.1 | 314.6 | 302.6 | 600.3 | 56.4 | 18.5 | 99.4 | 6.5 | 266.4 | 5.4 | 397.5 | 723.7 | 750.5 | 456.7 | 486.9 | 810.4 | 684.8 | 606.3 | 708 | 286 | 438.3 | 725.2 | 109.8 | 192.3 | 258 | 477.8 | 609.5 | 632.6 | 484.6 | 580.1 | 191.1 | 354.8 | 331.1 | 236.3 | 271 | 367 | 245.9
1516.1 | 1277.1 | 472.2 | 188.88 | 220.7898 | 344.7 | 324.4 | 314.9 | 303.3 | 601.7 | 56.4 | 18.5 | 99.5 | 6.8 | 217.3 | 5.9 | 397.7 | 722.6 | 751 | 456.7 | 487.1 | 810.5 | 685.1 | 608.7 | 709.8 | 286.2 | 439.2 | 725.3 | 110 | 192.5 | 258.3 | 478.3 | 609.8 | 637.9 | 485.4 | 580.1 | 191.4 | 354.8 | 331.4 | 236.5 | 271.1 | 367.5 | 246.2
1517.1 | 1278.1 | 472.9 | 189.16 | 221.1171 | 345.6 | 324.3 | 315.2 | 303.8 | 606.7 | 56.4 | 18.5 | 99.6 | 6.4 | 224 | 6.1 | 397.8 | 718.5 | 756 | 457 | 487.3 | 810.4 | 685.3 | 609.2 | 705.4 | 286.4 | 440 | 725.5 | 110.1 | 192.7 | 258.4 | 479 | 610.9 | 644.2 | 485.9 | 580.7 | 191.8 | 355 | 331.9 | 236.8 | 271.3 | 368 | 246.4
1518.1 | 1279.1 | 473.8 | 189.52 | 221.538 | 346 | 325 | 315.5 | 304 | 610.5 | 56.4 | 18.5 | 99.7 | 6.1 | 227.8 | 8.2 | 398 | 714.3 | 755.7 | 457.1 | 487.6 | 810.5 | 685.6 | 610.7 | 699.8 | 286.6 | 440.9 | 725.2 | 110.3 | 192.9 | 258.7 | 479.8 | 614.7 | 654.2 | 486.5 | 585 | 192.2 | 356 | 333 | 237.3 | 271.6 | 368.5 | 246.7
1519.1 | 1280.1 | 473.7 | 189.48 | 221.4912 | 346.2 | 325 | 316.2 | 304.9 | 608.8 | 56.4 | 18.5 | 99.8 | 4.9 | 240.6 | 10.6 | 398.1 | 715.1 | 763.9 | 457.2 | 487.9 | 811.2 | 686 | 610.6 | 701.4 | 286.8 | 441.7 | 724.6 | 110.5 | 193.2 | 259.1 | 480.1 | 612.9 | 658.9 | 486.8 | 587 | 192.5 | 356.6 | 332.8 | 237.8 | 271.8 | 369 | 247
1520.1 | 1281.1 | 473.3 | 189.32 | 221.3042 | 347 | 326.8 | 317 | 305.4 | 608 | 56.4 | 18.5 | 99.8 | 5.4 | 222.5 | 11.1 | 398.2 | 717 | 759.8 | 457.3 | 488.1 | 812.4 | 686.4 | 610.4 | 709.5 | 287 | 442.6 | 725.5 | 110.7 | 193.4 | 259.3 | 480.4 | 612 | 658 | 486.8 | 587.5 | 192.9 | 356.6 | 333.6 | 238 | 271.8 | 369.6 | 247.3
1521.1 | 1282.1 | 472.6 | 189.04 | 220.9769 | 350.1 | 330.2 | 317.6 | 305.1 | 609.7 | 56.4 | 18.5 | 99.8 | 5.6 | 258.5 | 9.5 | 398.3 | 721 | 762.6 | 457.4 | 488.4 | 813.9 | 686.6 | 610.2 | 712.2 | 287.1 | 443.5 | 726.5 | 110.8 | 193.7 | 259.5 | 481.2 | 611 | 671.5 | 487.8 | 588.4 | 193.2 | 356.8 | 334.3 | 238.3 | 272 | 370.1 | 247.6
1522.1 | 1283.1 | 472.4 | 188.96 | 220.8834 | 351.1 | 330.1 | 317.8 | 305.1 | 612.9 | 56.5 | 18.5 | 99.7 | 5.3 | 250.2 | 8.9 | 398.4 | 718 | 760.1 | 457.4 | 488.6 | 815.1 | 687.1 | 609.6 | 716.8 | 287.3 | 444.3 | 727.2 | 111 | 193.9 | 259.7 | 481.9 | 613.2 | 684.2 | 488.3 | 591.4 | 193.5 | 357 | 334.5 | 238.4 | 272.1 | 370.7 | 247.9
1523.1 | 1284.1 | 472.5 | 189 | 220.9301 | 350.9 | 329.3 | 318 | 305.6 | 613.3 | 56.5 | 18.5 | 99.6 | 5.7 | 244.8 | 7.7 | 398.5 | 713 | 750.4 | 457.3 | 488.8 | 816.1 | 687.5 | 606.8 | 720.7 | 287.5 | 445.1 | 727.8 | 111.2 | 194.1 | 260 | 482.1 | 610.8 | 681 | 488 | 589.3 | 193.9 | 356.8 | 334.2 | 238.6 | 272.2 | 371.2 | 248.1
1524.1 | 1285.1 | 473.7 | 189.48 | 221.4912 | 352.9 | 328.5 | 318.3 | 305.7 | 613.3 | 56.5 | 18.5 | 99.7 | 6.1 | 230.4 | 6.8 | 398.7 | 715.9 | 741.4 | 457.5 | 489.1 | 815.8 | 687.8 | 605.5 | 718.2 | 287.7 | 445.9 | 726.8 | 111.4 | 194.4 | 260.2 | 482.6 | 611.5 | 680.8 | 488.4 | 588.9 | 194.2 | 356.6 | 334.1 | 238.8 | 272.4 | 371.7 | 248.4
1525.1 | 1286.1 | 474 | 189.6 | 221.6315 | 356 | 328 | 319 | 305.3 | 615.8 | 56.5 | 18.5 | 99.6 | 5.4 | 235.7 | 6.7 | 399 | 718.2 | 749.1 | 457.6 | 489.3 | 815.8 | 688.2 | 602.8 | 719.8 | 287.9 | 446.7 | 726.7 | 111.5 | 194.6 | 260.6 | 483 | 613.5 | 685 | 488.5 | 588.2 | 194.5 | 356.6 | 334.4 | 238.9 | 272.6 | 372.2 | 248.6
1526.1 | 1287.1 | 473.5 | 189.4 | 221.3977 | 356.1 | 328.4 | 319.3 | 305.5 | 615.1 | 56.6 | 18.5 | 99.7 | 5.5 | 217.1 | 6.9 | 399.2 | 716.7 | 758.2 | 457.8 | 489.6 | 816.5 | 688.5 | 604.5 | 726.4 | 288.1 | 447.6 | 726.7 | 111.7 | 194.8 | 260.9 | 483.7 | 613.6 | 685.9 | 489.2 | 588.6 | 194.7 | 356.2 | 335 | 239 | 272.9 | 372.7 | 248.9
1527.1 | 1288.1 | 472.6 | 189.04 | 220.9769 | 358.3 | 328.6 | 319.8 | 305.6 | 612.5 | 56.6 | 18.5 | 99.7 | 5.9 | 268.3 | 6 | 399.4 | 714.7 | 763.3 | 457.7 | 489.9 | 816.4 | 688.9 | 606.9 | 730.4 | 288.3 | 448.6 | 727 | 111.9 | 195.1 | 261.1 | 484.3 | 613.1 | 676 | 489.3 | 588.5 | 195 | 356.7 | 335.2 | 239.3 | 273.2 | 373.2 | 249.1
1528.1 | 1289.1 | 472.5 | 189 | 220.9301 | 358.1 | 328.8 | 320 | 305.5 | 611 | 56.6 | 18.5 | 99.8 | 5.6 | 209.7 | 4.8 | 399.5 | 714.2 | 759.5 | 457.8 | 490.2 | 815.1 | 689.2 | 609.3 | 722.9 | 288.5 | 449.6 | 726.4 | 112.1 | 195.3 | 261.4 | 485 | 615.3 | 679.4 | 489.2 | 590.4 | 195.3 | 357.3 | 335.7 | 239.6 | 273.5 | 373.8 | 249.4
1529.1 | 1290.1 | 470.6 | 188.24 | 220.0417 | 355.8 | 328.5 | 320 | 305.9 | 609.7 | 56.6 | 18.5 | 99.9 | 6.2 | 208.7 | 6 | 399.7 | 714.8 | 759.1 | 458.1 | 490.5 | 814.6 | 689.6 | 611.3 | 719.5 | 288.7 | 450.6 | 726 | 112.2 | 195.6 | 261.6 | 485.7 | 619.1 | 679.9 | 489.2 | 591.8 | 195.5 | 357.7 | 336.4 | 240 | 273.8 | 374.3 | 249.7
1530.1 | 1291.1 | 470.4 | 188.16 | 219.9482 | 354.3 | 328.4 | 320.4 | 306.3 | 613.6 | 56.7 | 18.5 | 100 | 5.5 | 213.2 | 7.1 | 400 | 712.4 | 765 | 458.5 | 490.8 | 814.8 | 690 | 611.3 | 716.5 | 288.9 | 451.5 | 725.6 | 112.4 | 195.8 | 261.8 | 485.9 | 621 | 678.3 | 488.7 | 591.6 | 195.8 | 358 | 336.4 | 240.3 | 273.9 | 374.9 | 250
1531.1 | 1292.1 | 470.9 | 188.36 | 220.182 | 355.7 | 328.2 | 320.6 | 306.9 | 614.5 | 56.7 | 18.5 | 100 | 5.2 | 215.8 | 9.3 | 400.3 | 711.4 | 766.1 | 458.6 | 491 | 815 | 690.3 | 613.2 | 716.3 | 289.1 | 452.5 | 725.7 | 112.6 | 196.1 | 262.1 | 486.3 | 620.2 | 679.7 | 489 | 592.3 | 196.1 | 358.4 | 336.5 | 240.6 | 274.1 | 375.5 | 250.2
1532.1 | 1293.1 | 471.8 | 188.72 | 220.6028 | 357.7 | 327.9 | 321 | 306.9 | 617.3 | 56.7 | 18.5 | 100.1 | 5.3 | 220.6 | 12 | 400.3 | 710.1 | 770.8 | 458.7 | 491.3 | 815.3 | 690.6 | 614.3 | 717.9 | 289.3 | 453.4 | 725.5 | 112.8 | 196.4 | 262.5 | 487 | 618.7 | 683.8 | 489.7 | 593.5 | 196.4 | 359.2 | 336.3 | 241 | 274.1 | 376 | 250.5
1533.1 | 1294.1 | 472.4 | 188.96 | 220.8834 | 359.7 | 328 | 321.1 | 306.7 | 614.2 | 56.7 | 18.5 | 100.2 | 5.4 | 208.9 | 12.2 | 400.5 | 710.8 | 765.3 | 458.8 | 491.6 | 814.9 | 691 | 613.2 | 718 | 289.5 | 454.3 | 725 | 113 | 196.6 | 262.7 | 487.7 | 616.5 | 680.5 | 490.1 | 594.5 | 196.8 | 359.5 | 336.1 | 241.3 | 274.3 | 376.5 | 250.8
1534.1 | 1295.1 | 474.1 | 189.64 | 221.6782 | 361.2 | 327.9 | 321.5 | 306.7 | 612.4 | 56.7 | 18.5 | 100.3 | 5.3 | 218.7 | 10.8 | 400.7 | 706.9 | 760.2 | 459 | 491.9 | 815.2 | 691.2 | 613.6 | 721.1 | 289.7 | 455.2 | 725.4 | 113.1 | 196.9 | 262.8 | 488.3 | 617.4 | 676.3 | 490.4 | 593.6 | 197 | 359.7 | 336.4 | 241.7 | 274.5 | 377 | 251.1
1535.1 | 1296.1 | 469.9 | 187.96 | 219.7144 | 361.1 | 327.8 | 321.8 | 306.8 | 618.8 | 56.8 | 18.5 | 100.3 | 5.6 | 183.7 | 8.4 | 400.9 | 706.2 | 749.6 | 459.3 | 492.2 | 815.7 | 691.4 | 612.9 | 718.9 | 289.9 | 456.1 | 725.4 | 113.3 | 197.1 | 263.1 | 488.8 | 623.6 | 676.3 | 490.2 | 592.5 | 197.4 | 360 | 337.5 | 241.9 | 275 | 377.5 | 251.4
1536.1 | 1297.1 | 470.4 | 188.16 | 219.9482 | 360.3 | 327.8 | 321.6 | 307.6 | 624.5 | 56.8 | 18.4 | 100.3 | 5.7 | 238.6 | 6.4 | 401 | 711.8 | 755.8 | 459.2 | 492.4 | 816 | 691.7 | 616.3 | 717.9 | 290.2 | 457 | 725.8 | 113.5 | 197.3 | 263.4 | 489.6 | 625.9 | 680.1 | 490.9 | 595.2 | 197.7 | 360.7 | 338 | 242.2 | 275.2 | 378 | 251.7
1537.1 | 1298.1 | 471.7 | 188.68 | 220.556 | 361.5 | 327.6 | 322 | 308.3 | 619.9 | 56.8 | 18.4 | 100.4 | 5.6 | 207.1 | 6.5 | 401.5 | 714.9 | 754.9 | 459.6 | 492.7 | 815 | 692 | 618.3 | 715.9 | 290.4 | 457.8 | 726.3 | 113.7 | 197.5 | 263.7 | 490 | 626.1 | 676.4 | 490.7 | 594.6 | 198 | 361.4 | 338.5 | 242.5 | 275.5 | 378.5 | 252
1538.1 | 1299.1 | 471.2 | 188.48 | 220.3223 | 363.1 | 327.6 | 322.1 | 308.9 | 620.6 | 56.9 | 18.4 | 100.5 | 6.2 | 216.4 | 7.6 | 401.7 | 713.6 | 761.8 | 459.7 | 493 | 814.6 | 692.5 | 618.8 | 718.9 | 290.6 | 458.6 | 725.7 | 113.9 | 197.7 | 263.9 | 490.3 | 625.7 | 682.3 | 490.5 | 596.3 | 198.3 | 361.6 | 339.4 | 242.7 | 275.7 | 379 | 252.3
1539.1 | 1300.1 | 472.9 | 189.16 | 221.1171 | 364.1 | 329.1 | 322.5 | 309.5 | 621.3 | 56.9 | 18.4 | 100.5 | 5.8 | 202.9 | 10 | 402 | 712.9 | 765.9 | 459.9 | 493.3 | 815.6 | 692.8 | 619.2 | 719.3 | 290.8 | 459.5 | 725.1 | 114 | 197.9 | 264.1 | 490.9 | 624.3 | 686.5 | 491 | 599.6 | 198.7 | 361.8 | 340.1 | 242.9 | 276 | 379.6 | 252.6
1540.1 | 1301.1 | 475.6 | 190.24 | 222.3796 | 364.3 | 330.5 | 323.2 | 309.8 | 620.2 | 56.9 | 18.4 | 100.6 | 5.6 | 209.8 | 10.9 | 402.1 | 713.2 | 765.3 | 460 | 493.6 | 816.6 | 693.1 | 619.2 | 720.1 | 291 | 460.3 | 725.1 | 114.2 | 198.1 | 264.5 | 491 | 623.3 | 684.7 | 490.6 | 601.1 | 199 | 362.1 | 340 | 243.2 | 276 | 380.1 | 252.9
1541.1 | 1302.1 | 476.8 | 190.72 | 222.9407 | 364.6 | 330.7 | 323.9 | 309.5 | 614.5 | 56.9 | 18.4 | 100.6 | 4.7 | 215.2 | 10.1 | 402.4 | 714.8 | 758 | 460.2 | 493.9 | 816.4 | 693.5 | 616.9 | 714 | 291.2 | 461.1 | 724.2 | 114.4 | 198.3 | 264.7 | 491.2 | 622.2 | 686.3 | 490.4 | 599.8 | 199.4 | 362 | 339.6 | 243.4 | 276.2 | 380.7 | 253.1
1542.1 | 1303.1 | 473.7 | 189.48 | 221.4912 | 367.4 | 331.6 | 324 | 309.7 | 612.3 | 56.9 | 18.4 | 100.7 | 5.3 | 222.3 | 8.7 | 402.6 | 721.9 | 753.6 | 460.3 | 494.2 | 815.9 | 693.7 | 617.1 | 709 | 291.5 | 461.8 | 724.2 | 114.6 | 198.5 | 264.9 | 491.8 | 621.5 | 682.4 | 490.7 | 599.2 | 199.7 | 362.7 | 340 | 243.7 | 276.6 | 381.2 | 253.4
1543.1 | 1304.1 | 472.3 | 188.92 | 220.8366 | 366.9 | 332.3 | 324 | 310.3 | 607.4 | 57 | 18.4 | 100.8 | 6.8 | 248.5 | 7.5 | 402.8 | 729.7 | 746 | 460.5 | 494.5 | 816.6 | 694.1 | 618.7 | 704.3 | 291.7 | 462.6 | 723.6 | 114.7 | 198.7 | 265.2 | 492.5 | 620.3 | 675.2 | 491.2 | 598 | 200 | 363 | 340.1 | 244 | 276.7 | 381.8 | 253.7
1544.1 | 1305.1 | 473.3 | 189.32 | 221.3042 | 366.6 | 332.3 | 323.5 | 310.8 | 609.8 | 57 | 18.4 | 100.9 | 6.7 | 241 | 7.2 | 403 | 725.8 | 747.7 | 460.6 | 494.8 | 817.9 | 694.5 | 619 | 708.4 | 291.9 | 463.3 | 723.5 | 114.9 | 198.9 | 265.5 | 493.1 | 623.3 | 683.9 | 491.5 | 599.4 | 200.4 | 363.1 | 340.4 | 244.1 | 276.9 | 382.3 | 254
1545.1 | 1306.1 | 472 | 188.8 | 220.6963 | 368.2 | 332.1 | 324.1 | 311 | 615.1 | 57 | 18.4 | 101.1 | 6.5 | 233.6 | 8.2 | 403.2 | 719.3 | 746.5 | 460.7 | 495.1 | 819.3 | 694.9 | 618.9 | 710.8 | 292.2 | 463.9 | 724.1 | 115.1 | 199.1 | 265.8 | 493.4 | 622.5 | 680.2 | 491.5 | 599.6 | 200.7 | 363.2 | 340 | 244.2 | 277.1 | 382.8 | 254.2
1546.1 | 1307.1 | 472.5 | 189 | 220.9301 | 369.3 | 332.3 | 324.8 | 310.9 | 613.4 | 57.1 | 18.4 | 101.3 | 7.2 | 229.5 | 8.8 | 403.5 | 721.2 | 744.8 | 460.9 | 495.5 | 819.5 | 695.2 | 617.1 | 708.4 | 292.4 | 464.6 | 723.6 | 115.3 | 199.2 | 266.1 | 493.8 | 619.5 | 685.9 | 491.3 | 598.1 | 201 | 363.5 | 339.9 | 244.4 | 277.2 | 383.4 | 254.5
1547.1 | 1308.1 | 473.4 | 189.36 | 221.3509 | 370.3 | 332.1 | 325 | 310.8 | 610.8 | 57.1 | 18.4 | 101.5 | 6.9 | 228.2 | 8.9 | 403.7 | 725 | 737 | 461 | 495.8 | 818.2 | 695.5 | 619 | 706.7 | 292.6 | 465.2 | 723.5 | 115.5 | 199.4 | 266.3 | 494 | 617.3 | 673 | 491.1 | 596.1 | 201.3 | 364.3 | 340.1 | 244.8 | 277.5 | 383.9 | 254.8
1548.1 | 1309.1 | 473.3 | 189.32 | 221.3042 | 370.9 | 332.7 | 324.9 | 311.6 | 615.9 | 57.1 | 18.4 | 101.7 | 6.3 | 240.9 | 7.3 | 403.8 | 722.5 | 735 | 461.1 | 496.2 | 816.3 | 695.8 | 620.8 | 700.9 | 292.8 | 465.9 | 723 | 115.7 | 199.6 | 266.6 | 494.5 | 621.7 | 672.8 | 490.8 | 597.9 | 201.7 | 365.1 | 340.4 | 245.3 | 277.7 | 384.4 | 255.1
1549.1 | 1310.1 | 471.9 | 188.76 | 220.6496 | 369.9 | 333.3 | 325.1 | 312.4 | 629.6 | 57.2 | 18.4 | 101.7 | 5 | 242.6 | 7.2 | 403.9 | 727 | 741.1 | 461.1 | 496.5 | 816.6 | 696 | 620.5 | 699.9 | 293.1 | 466.5 | 722.6 | 115.8 | 199.8 | 266.8 | 495.3 | 628.3 | 682.5 | 490.9 | 601.5 | 202 | 365.5 | 340.3 | 245.5 | 277.8 | 384.9 | 255.4
1550.1 | 1311.1 | 471.4 | 188.56 | 220.4158 | 369.4 | 333.7 | 326.1 | 313 | 630.5 | 57.2 | 18.4 | 101.8 | 5.2 | 248.7 | 8.8 | 404.1 | 724.6 | 737.5 | 461.2 | 496.8 | 816.9 | 696.3 | 620 | 703.7 | 293.3 | 467.1 | 722.4 | 116 | 199.9 | 267.1 | 496 | 627.1 | 686.5 | 491 | 602.1 | 202.3 | 365.6 | 340.4 | 245.6 | 278.1 | 385.4 | 255.7
1551.1 | 1312.1 | 472.8 | 189.12 | 221.0704 | 369 | 334.4 | 326.4 | 312.8 | 626.9 | 57.3 | 18.4 | 101.8 | 6.7 | 249 | 9.7 | 404.4 | 720.7 | 738.3 | 461.4 | 497.1 | 817.2 | 696.7 | 618.4 | 706.8 | 293.5 | 467.7 | 723.1 | 116.2 | 200 | 267.3 | 496.8 | 627.9 | 685.5 | 491.9 | 600.7 | 202.7 | 366.2 | 340.2 | 245.9 | 278.3 | 386 | 256
1552.1 | 1313.1 | 472.1 | 188.84 | 220.7431 | 369.4 | 335.1 | 326.7 | 312.9 | 625.7 | 57.3 | 18.4 | 102 | 6.6 | 229.4 | 10.2 | 404.6 | 715.4 | 735 | 461.4 | 497.5 | 817.7 | 697 | 618.9 | 709.2 | 293.7 | 468.2 | 723.1 | 116.4 | 200.2 | 267.7 | 497.6 | 629.3 | 691.3 | 492.7 | 600.9 | 203 | 366.1 | 339.9 | 246.1 | 278.3 | 386.6 | 256.3
1553.1 | 1314.1 | 472.4 | 188.96 | 220.8834 | 371.2 | 335.7 | 327.6 | 312.9 | 623.7 | 57.3 | 18.4 | 102.1 | 5.6 | 240.1 | 9.4 | 404.8 | 713.9 | 727 | 461.5 | 497.8 | 818 | 697.3 | 619.6 | 698.3 | 294 | 468.7 | 721.1 | 116.6 | 200.4 | 268 | 497.7 | 627.6 | 684.7 | 492.2 | 600.7 | 203.3 | 366 | 339.4 | 246.3 | 278.4 | 387.1 | 256.6
1554.1 | 1315.1 | 471.1 | 188.44 | 220.2755 | 374 | 335.5 | 328.3 | 312.2 | 629.5 | 57.3 | 18.4 | 102.4 | 4.8 | 228.1 | 9.1 | 404.9 | 710 | 720.7 | 461.6 | 498.2 | 818.5 | 697.6 | 619.4 | 692.3 | 294.2 | 469.2 | 719.4 | 116.7 | 200.6 | 268.3 | 498.2 | 625.9 | 675.5 | 492.2 | 598.5 | 203.6 | 366.1 | 339.3 | 246.4 | 278.5 | 387.6 | 256.8
1555.1 | 1316.1 | 472.5 | 189 | 220.9301 | 378 | 335.1 | 329 | 312.1 | 633.9 | 57.3 | 18.4 | 102.5 | 4.8 | 249.5 | 9.5 | 405.1 | 705.1 | 724.6 | 461.6 | 498.5 | 817.9 | 697.9 | 620.8 | 690.1 | 294.5 | 469.8 | 718.2 | 116.9 | 200.8 | 268.6 | 498.6 | 629.3 | 671.4 | 492 | 597.8 | 203.9 | 366.4 | 339.7 | 246.6 | 278.8 | 388.1 | 257.1
1556.1 | 1317.1 | 470.8 | 188.32 | 220.1352 | 379 | 335.1 | 329.4 | 312.7 | 635.9 | 57.4 | 18.4 | 102.7 | 5.5 | 235.9 | 8.4 | 405.4 | 704.2 | 735.6 | 461.7 | 498.9 | 817.9 | 698.3 | 621.9 | 694.2 | 294.8 | 470.4 | 718.6 | 117.1 | 201.1 | 269 | 499.5 | 629.1 | 673.2 | 492 | 600.8 | 204.2 | 366.6 | 339.9 | 246.8 | 279 | 388.6 | 257.4
1557.1 | 1318.1 | 470.7 | 188.28 | 220.0885 | 378.8 | 335.1 | 329 | 312.8 | 637.3 | 57.4 | 18.4 | 102.9 | 6 | 220.2 | 7.5 | 405.6 | 702.4 | 746.6 | 461.6 | 499.3 | 817.2 | 698.6 | 621.8 | 698.9 | 295 | 471 | 719.3 | 117.3 | 201.3 | 269.1 | 500.1 | 635.4 | 675.1 | 492.1 | 601.6 | 204.5 | 367 | 340.6 | 247 | 279.3 | 389.1 | 257.6
1558.1 | 1319.1 | 473.4 | 189.36 | 221.3509 | 379.6 | 335.2 | 328.5 | 313.2 | 639.3 | 57.4 | 18.4 | 103 | 5.9 | 264.8 | 6.2 | 406.1 | 701.8 | 755.2 | 461.8 | 499.7 | 815.9 | 698.9 | 621.4 | 706 | 295.3 | 471.7 | 720.5 | 117.5 | 201.6 | 269.4 | 501 | 636.7 | 673.5 | 492.9 | 600.8 | 204.8 | 367.4 | 341.1 | 247.2 | 279.7 | 389.7 | 257.9
1559.1 | 1320.1 | 470.3 | 188.12 | 219.9014 | 378.3 | 335.7 | 328.6 | 313.6 | 634.6 | 57.5 | 18.4 | 103.1 | 6.5 | 256.4 | 4.8 | 406.2 | 703.5 | 757 | 461.8 | 500.1 | 814.9 | 699.2 | 624.7 | 705.1 | 295.5 | 472.3 | 720.8 | 117.6 | 201.8 | 269.7 | 501.5 | 635.2 | 677.7 | 493.1 | 601.7 | 205.2 | 367.5 | 341.9 | 247.5 | 280 | 390.2 | 258.2
1560.1 | 1321.1 | 470.3 | 188.12 | 219.9014 | 378.1 | 336.1 | 329 | 314 | 628.2 | 57.5 | 18.4 | 103.2 | 6.5 | 239.3 | 5.8 | 406.5 | 709.9 | 758.4 | 462.1 | 500.3 | 813.9 | 699.6 | 626.7 | 703.9 | 295.7 | 472.9 | 720.7 | 117.8 | 202 | 269.9 | 502.2 | 632.3 | 673.4 | 493.1 | 600.2 | 205.5 | 367.6 | 342 | 247.7 | 280.1 | 390.7 | 258.5
1561.1 | 1322.1 | 469.3 | 187.72 | 219.4339 | 377.8 | 336.6 | 329.5 | 314.1 | 624.9 | 57.6 | 18.3 | 103.3 | 6.1 | 228.6 | 6.2 | 406.8 | 709.8 | 750.4 | 462.3 | 500.7 | 812.8 | 699.9 | 626.4 | 701.5 | 296 | 473.6 | 720.3 | 118 | 202.2 | 270.2 | 502.7 | 632.6 | 668.8 | 493.4 | 600 | 205.9 | 367.9 | 342 | 247.9 | 280.1 | 391.2 | 258.7
1562.1 | 1323.1 | 470.6 | 188.24 | 220.0417 | 377.9 | 336.6 | 329.7 | 313.8 | 634.3 | 57.6 | 18.3 | 103.4 | 5.7 | 247.9 | 6 | 407 | 707.6 | 748.9 | 462.5 | 501.1 | 812.4 | 700.2 | 631.3 | 695.8 | 296.2 | 474.2 | 718.8 | 118.2 | 202.4 | 270.5 | 503.1 | 639.2 | 669.1 | 493.7 | 599.1 | 206.2 | 368.2 | 341.9 | 248.2 | 280.2 | 391.7 | 259.1
1563.1 | 1324.1 | 470.8 | 188.32 | 220.1352 | 377.7 | 336.7 | 330.4 | 313.7 | 636.3 | 57.6 | 18.3 | 103.6 | 5.8 | 243.5 | 7.6 | 407.1 | 709.5 | 735.6 | 462.5 | 501.5 | 812.8 | 700.6 | 635.5 | 690.5 | 296.5 | 474.8 | 718.1 | 118.4 | 202.7 | 270.8 | 503.8 | 641.8 | 672.3 | 494.1 | 599.5 | 206.6 | 368.4 | 341.8 | 248.3 | 280.4 | 392.3 | 259.4
1564.1 | 1325.1 | 469.2 | 187.68 | 219.3871 | 378.7 | 337.1 | 331 | 313.9 | 638.7 | 57.7 | 18.3 | 103.7 | 5.9 | 248.1 | 8.6 | 407.3 | 710.5 | 727 | 462.7 | 501.9 | 812.9 | 700.8 | 635.2 | 687.1 | 296.8 | 475.4 | 718 | 118.6 | 202.9 | 271.1 | 505.4 | 645.8 | 677.4 | 495.2 | 600.1 | 207 | 368.9 | 341.7 | 248.6 | 280.6 | 392.9 | 259.7
1565.1 | 1326.1 | 469.2 | 187.68 | 219.3871 | 378.6 | 337.5 | 331.3 | 314 | 637.7 | 57.7 | 18.3 | 103.8 | 5.4 | 256.1 | 9.3 | 407.6 | 706.6 | 722 | 463 | 502.3 | 812.9 | 701.1 | 633.4 | 684.6 | 297 | 476 | 718.8 | 118.8 | 203.1 | 271.3 | 505.9 | 645.1 | 675.4 | 495.6 | 602.7 | 207.4 | 369.2 | 341.6 | 248.9 | 280.7 | 393.5 | 260
1566.1 | 1327.1 | 471.6 | 188.64 | 220.5093 | 378.7 | 337.9 | 332.1 | 314.2 | 630 | 57.8 | 18.3 | 104 | 5.5 | 252.9 | 9.8 | 407.7 | 708 | 725.9 | 463.1 | 502.8 | 812.8 | 701.4 | 632.2 | 681.1 | 297.3 | 476.5 | 717.9 | 118.9 | 203.3 | 271.6 | 506.1 | 640.7 | 669.2 | 495.8 | 600.3 | 207.8 | 369.5 | 342.6 | 249.2 | 280.9 | 394.2 | 260.3
1567.1 | 1328.1 | 471.1 | 188.44 | 220.2755 | 380.8 | 338 | 332.8 | 314.4 | 626.9 | 57.8 | 18.3 | 104.1 | 5.5 | 247 | 10.4 | 407.9 | 706.5 | 728.5 | 463.2 | 503.2 | 812.9 | 701.8 | 632.2 | 682.9 | 297.5 | 477.1 | 717.8 | 119.1 | 203.6 | 272 | 506.8 | 640.1 | 664.8 | 496.2 | 598.9 | 208.2 | 370.2 | 343.9 | 249.5 | 281.3 | 394.7 | 260.6
1568.1 | 1329.1 | 470.3 | 188.12 | 219.9014 | 380.1 | 337.7 | 333.5 | 314.7 | 629.6 | 57.9 | 18.3 | 104.1 | 5 | 252.9 | 9.6 | 408.1 | 708.1 | 726.8 | 463.3 | 503.6 | 811.8 | 702.3 | 633.8 | 683.9 | 297.8 | 477.7 | 717.3 | 119.3 | 203.8 | 272.3 | 507.8 | 641.3 | 664 | 496.9 | 600.4 | 208.6 | 371 | 344.6 | 250 | 281.5 | 395.1 | 260.9
1569.1 | 1330.1 | 471.5 | 188.6 | 220.4625 | 378.2 | 337.5 | 333.9 | 315.3 | 635.8 | 58 | 18.3 | 104.2 | 4.9 | 257.9 | 8.8 | 408.3 | 718.3 | 726.9 | 463.4 | 504 | 810.6 | 702.6 | 638.6 | 683.1 | 298.1 | 478.3 | 716.8 | 119.5 | 204.1 | 272.5 | 508.8 | 643.9 | 666.4 | 497.7 | 604.3 | 209.1 | 371.9 | 344.9 | 250.5 | 281.7 | 395.7 | 261.2
1570.1 | 1331.1 | 471.6 | 188.64 | 220.5093 | 376.8 | 337.1 | 334.3 | 316 | 629.9 | 58 | 18.3 | 104.3 | 5.1 | 259.2 | 8.5 | 408.5 | 726.2 | 740.5 | 463.5 | 504.5 | 810.5 | 702.9 | 640.9 | 676.3 | 298.3 | 478.8 | 715.7 | 119.7 | 204.3 | 272.7 | 510.2 | 645.2 | 662.9 | 499.2 | 604.7 | 209.5 | 372.7 | 346.1 | 251 | 281.9 | 396.3 | 261.5
1571.1 | 1332.1 | 470.4 | 188.16 | 219.9482 | 376.6 | 337.5 | 334.9 | 316.7 | 644.4 | 58 | 18.3 | 104.5 | 5.5 | 250.9 | 9.1 | 408.7 | 723.9 | 749.7 | 463.6 | 504.9 | 810.4 | 703.2 | 640.9 | 680.1 | 298.6 | 479.4 | 715.1 | 119.9 | 204.5 | 272.9 | 511.6 | 653.3 | 665.7 | 500.7 | 603.6 | 210 | 373.3 | 347.4 | 251.3 | 282.2 | 396.9 | 261.8
1572.1 | 1333.1 | 470.6 | 188.24 | 220.0417 | 375.4 | 337.9 | 335.1 | 317.1 | 652.6 | 58.1 | 18.3 | 104.7 | 5.9 | 260.2 | 9.5 | 408.9 | 720.8 | 757.2 | 463.7 | 505.4 | 810.9 | 703.4 | 638.3 | 690.8 | 298.8 | 479.9 | 715.4 | 120.1 | 204.8 | 273.3 | 512.3 | 654.1 | 674.8 | 501.3 | 607.2 | 210.5 | 373.7 | 347 | 251.6 | 282.4 | 397.6 | 262.1
1573.1 | 1334.1 | 470.1 | 188.04 | 219.8079 | 374.7 | 339.7 | 334.9 | 317.1 | 647.7 | 58.1 | 18.3 | 104.8 | 5.9 | 254.9 | 10.1 | 409.1 | 723.6 | 755.9 | 463.9 | 505.9 | 810.6 | 703.8 | 635.1 | 696.9 | 299.1 | 480.4 | 715.6 | 120.3 | 205 | 273.6 | 512.7 | 652.4 | 679.1 | 501.7 | 607 | 211 | 373.7 | 347 | 251.8 | 282.5 | 398.3 | 262.4
1574.1 | 1335.1 | 471.5 | 188.6 | 220.4625 | 375.8 | 341.1 | 334.9 | 316.7 | 643.9 | 58.1 | 18.3 | 105 | 6.1 | 253.5 | 11 | 409.6 | 719.8 | 756 | 464.1 | 506.4 | 809.2 | 704.1 | 634 | 694.7 | 299.3 | 480.9 | 714.7 | 120.5 | 205.2 | 273.9 | 513.6 | 652.4 | 684.6 | 502.2 | 608 | 211.4 | 374.7 | 347.9 | 252.2 | 282.9 | 398.8 | 262.7
1575.1 | 1336.1 | 471.6 | 188.64 | 220.5093 | 375.2 | 341.9 | 335 | 317 | 645.8 | 58.2 | 18.3 | 105 | 5.7 | 246.5 | 10.6 | 410 | 716 | 755.1 | 464.3 | 506.9 | 807.8 | 704.4 | 634.1 | 694.7 | 299.6 | 481.3 | 713.3 | 120.7 | 205.4 | 274.1 | 514.6 | 654.2 | 691.1 | 503.2 | 611.2 | 211.9 | 376 | 348.5 | 252.6 | 283.1 | 399.4 | 263
1576.1 | 1337.1 | 472.1 | 188.84 | 220.7431 | 374 | 342.1 | 335.2 | 317.8 | 643.2 | 58.2 | 18.3 | 105.1 | 5.3 | 261.1 | 9.8 | 410.4 | 717.5 | 761.9 | 464.5 | 507.4 | 807.2 | 704.7 | 635.6 | 693.4 | 299.8 | 481.9 | 712.8 | 120.9 | 205.6 | 274.4 | 515.6 | 654.1 | 697.3 | 503.9 | 612.7 | 212.4 | 377 | 348.9 | 253 | 283.5 | 400 | 263.4
1577.1 | 1338.1 | 472.1 | 188.84 | 220.7431 | 374.4 | 342.4 | 335.3 | 318.3 | 644.3 | 58.2 | 18.3 | 105.2 | 4.9 | 283.6 | 9 | 410.7 | 718.7 | 759.6 | 464.8 | 507.9 | 806.6 | 705 | 636.8 | 694.6 | 300 | 482.3 | 712.8 | 121.1 | 205.9 | 274.7 | 516.4 | 654.2 | 705.4 | 504.9 | 615.2 | 212.9 | 377.3 | 349.4 | 253.3 | 283.8 | 400.6 | 263.7
1578.1 | 1339.1 | 471 | 188.4 | 220.2287 | 376.4 | 342.5 | 335.8 | 319 | 642.1 | 58.2 | 18.3 | 105.4 | 5 | 252.4 | 9 | 410.9 | 718.1 | 757.3 | 464.8 | 508.4 | 806.3 | 705.4 | 636.4 | 693.8 | 300.2 | 482.7 | 712.1 | 121.2 | 206.2 | 275 | 517.5 | 654.1 | 713.2 | 505.5 | 615.6 | 213.4 | 378.2 | 350.5 | 253.7 | 284.2 | 401.2 | 264
1579.1 | 1340.1 | 472 | 188.8 | 220.6963 | 377.2 | 342.5 | 336.6 | 319.5 | 637.6 | 58.2 | 18.3 | 105.5 | 4.8 | 240.6 | 9.3 | 411.1 | 718.8 | 766.4 | 464.9 | 508.9 | 805.9 | 705.7 | 636.8 | 695.6 | 300.4 | 483.2 | 712.4 | 121.4 | 206.4 | 275.3 | 518.8 | 653.3 | 715.4 | 505.8 | 618.3 | 213.9 | 378.5 | 351.3 | 253.9 | 284.6 | 401.9 | 264.4
1580.1 | 1341.1 | 472 | 188.8 | 220.6963 | 378.6 | 343.6 | 337.2 | 319.7 | 635.4 | 58.2 | 18.3 | 105.6 | 5.3 | 232.3 | 9.8 | 411.3 | 717.3 | 772.5 | 465 | 509.4 | 806.1 | 705.9 | 636 | 700.2 | 300.7 | 483.6 | 712.3 | 121.6 | 206.7 | 275.6 | 519.2 | 651 | 715.9 | 505.5 | 619.7 | 214.4 | 378.5 | 351.2 | 254.1 | 284.7 | 402.5 | 264.7
1581.1 | 1342.1 | 471.6 | 188.64 | 220.5093 | 379.1 | 344.5 | 337.7 | 319.9 | 634.2 | 58.2 | 18.3 | 105.6 | 5.4 | 221.5 | 10.5 | 411.5 | 714.1 | 779.5 | 465.2 | 510 | 806.4 | 706.2 | 636.4 | 695.8 | 300.9 | 484.1 | 711.6 | 121.8 | 207 | 275.9 | 519.6 | 649 | 709.9 | 505.4 | 616.6 | 214.9 | 378.7 | 351.2 | 254.4 | 284.8 | 403.2 | 265
1582.1 | 1343.1 | 472.7 | 189.08 | 221.0236 | 378.7 | 344.8 | 338 | 320.3 | 632 | 58.2 | 18.3 | 105.6 | 5.1 | 260.5 | 9.8 | 411.7 | 713.8 | 781.3 | 465.2 | 510.5 | 806.5 | 706.5 | 635.9 | 697.6 | 301.1 | 484.5 | 710.7 | 122 | 207.2 | 276.1 | 520.6 | 648.2 | 714.9 | 505.6 | 616 | 215.3 | 378.6 | 351.2 | 254.6 | 285.1 | 403.8 | 265.3
1583.1 | 1344.1 | 474.2 | 189.68 | 221.725 | 378.7 | 344.4 | 338.4 | 320.7 | 635 | 58.3 | 18.3 | 105.6 | 5.2 | 260.8 | 9 | 412 | 713.8 | 785.9 | 465.4 | 511 | 807.3 | 706.7 | 635.8 | 703.2 | 301.3 | 484.9 | 710.2 | 122.2 | 207.5 | 276.8 | 521.3 | 648.9 | 718 | 505.9 | 618.6 | 215.7 | 378.3 | 351.5 | 254.7 | 285.4 | 404.4 | 265.7
1584.1 | 1345.1 | 473.7 | 189.48 | 221.4912 | 378.4 | 345.8 | 338.6 | 321.2 | 637.5 | 58.4 | 18.3 | 105.7 | 5.5 | 265 | 8.3 | 412.2 | 715 | 785.5 | 465.5 | 511.5 | 807.9 | 706.9 | 636.1 | 711.9 | 301.6 | 485.3 | 710.3 | 122.4 | 207.8 | 277.2 | 521.7 | 647.8 | 724 | 505.7 | 620.4 | 216 | 378 | 351.3 | 254.8 | 285.4 | 405.1 | 266
1585.1 | 1346.1 | 473.6 | 189.44 | 221.4444 | 377.6 | 347.8 | 338.7 | 321 | 637.4 | 58.5 | 18.3 | 105.8 | 5.4 | 263.7 | 9.1 | 412.2 | 713.3 | 785.9 | 465.5 | 512 | 808.3 | 707.2 | 636.7 | 721.7 | 301.8 | 485.7 | 712.3 | 122.6 | 208 | 277.3 | 522.3 | 644 | 716.5 | 506 | 619 | 216.3 | 377.7 | 350.7 | 255 | 285.6 | 405.6 | 266.2
1586.1 | 1347.1 | 472.9 | 189.16 | 221.1171 | 378.2 | 346.9 | 339.5 | 321 | 637.9 | 58.6 | 18.3 | 105.9 | 5.5 | 270.9 | 8.7 | 412.5 | 711.6 | 788.3 | 465.7 | 512.5 | 808.6 | 707.5 | 637 | 729 | 302 | 486 | 713.3 | 122.8 | 208.3 | 277.7 | 523.2 | 642.9 | 718.8 | 506.1 | 617 | 216.6 | 377.4 | 350.4 | 255.1 | 285.7 | 406.2 | 266.5
1587.1 | 1348.1 | 472.6 | 189.04 | 220.9769 | 379.2 | 346.6 | 339.7 | 320.4 | 642.3 | 58.6 | 18.3 | 106 | 4.9 | 255.7 | 8.4 | 412.8 | 714.3 | 788.4 | 465.9 | 513.1 | 808.6 | 707.7 | 636.8 | 734.1 | 302.2 | 486.5 | 714.5 | 123 | 208.6 | 278.2 | 524 | 642 | 715.5 | 506.5 | 617.4 | 216.8 | 377.8 | 349.9 | 255.3 | 285.8 | 406.8 | 266.8
1588.1 | 1349.1 | 471.7 | 188.68 | 220.556 | 379.7 | 346.5 | 340.3 | 320.5 | 640.7 | 58.7 | 18.3 | 106.2 | 5.6 | 257.4 | 7.6 | 413 | 714.5 | 780.6 | 465.9 | 513.6 | 808.8 | 708 | 635.1 | 736.2 | 302.4 | 486.9 | 715 | 123.2 | 208.9 | 278.5 | 525 | 645.3 | 713.6 | 507.2 | 617.2 | 217.1 | 378.3 | 349.7 | 255.5 | 285.9 | 407.4 | 267.1
1589.1 | 1350.1 | 472.3 | 188.92 | 220.8366 | 380.6 | 346.6 | 340.7 | 320.6 | 643.2 | 58.7 | 18.3 | 106.3 | 5.7 | 239.2 | 7.2 | 413.2 | 719.2 | 778.1 | 466.1 | 514.1 | 810 | 708.3 | 634.8 | 734.3 | 302.6 | 487.2 | 715.1 | 123.4 | 209.2 | 278.9 | 526 | 645.3 | 718.4 | 507.7 | 618.4 | 217.3 | 378.9 | 349.6 | 255.7 | 286 | 408 | 267.5
1590.1 | 1351.1 | 474.2 | 189.68 | 221.725 | 379.9 | 346.6 | 340.5 | 320.7 | 641.2 | 58.7 | 18.3 | 106.4 | 6.1 | 239.4 | 7.7 | 413.4 | 716.8 | 775.3 | 466.2 | 514.5 | 810.5 | 708.7 | 635.8 | 732 | 302.8 | 487.6 | 714.5 | 123.6 | 209.5 | 279.3 | 526.6 | 641.9 | 714 | 508.1 | 616.3 | 217.6 | 379.1 | 349.5 | 255.9 | 286 | 408.5 | 267.8
1591.1 | 1352.1 | 473.8 | 189.52 | 221.538 | 378.6 | 346 | 340.7 | 320.8 | 640 | 58.7 | 18.2 | 106.5 | 6.6 | 246.2 | 7.6 | 413.5 | 714.8 | 776.3 | 466.2 | 515 | 810.8 | 709 | 638 | 734.6 | 303.1 | 487.9 | 714.9 | 123.8 | 209.8 | 279.9 | 527.4 | 639.6 | 710.6 | 508.3 | 615.3 | 217.8 | 379.3 | 349.4 | 256.1 | 286 | 409.1 | 268.1
1592.1 | 1353.1 | 474.9 | 189.96 | 222.0523 | 378 | 346.5 | 341.5 | 320.8 | 643.1 | 58.7 | 18.2 | 106.7 | 5.2 | 216.5 | 6.3 | 413.7 | 712.7 | 783.7 | 466.3 | 515.5 | 810.7 | 709.4 | 640 | 736 | 303.3 | 488.1 | 715.1 | 124 | 210.1 | 280.2 | 528.4 | 641.8 | 713.7 | 508.7 | 618.3 | 218 | 379.7 | 349.5 | 256.3 | 286.1 | 409.6 | 268.4
1593.1 | 1354.1 | 476.1 | 190.44 | 222.6134 | 378.1 | 347.4 | 342.2 | 321.2 | 642.2 | 58.7 | 18.2 | 106.7 | 5.5 | 206.9 | 5.6 | 414 | 712.2 | 785.4 | 466.4 | 516.1 | 810.6 | 709.8 | 640.8 | 734.8 | 303.6 | 488.4 | 715.2 | 124.2 | 210.4 | 280.5 | 529.3 | 639.8 | 712 | 509.1 | 619 | 218.3 | 380.2 | 349.6 | 256.5 | 286.3 | 410.3 | 268.7
1594.1 | 1355.1 | 473.2 | 189.28 | 221.2574 | 377.9 | 348.5 | 342.4 | 321.4 | 643.5 | 58.8 | 18.2 | 106.8 | 5.4 | 212.8 | 8.6 | 414.3 | 716 | 786.7 | 466.5 | 516.6 | 809.5 | 710.1 | 641.3 | 733.1 | 303.9 | 488.8 | 714.9 | 124.4 | 210.7 | 280.9 | 530.4 | 641.1 | 718.2 | 509.3 | 620.1 | 218.6 | 380.9 | 349.7 | 256.8 | 286.5 | 410.8 | 269
1595.1 | 1356.1 | 473.1 | 189.24 | 221.2107 | 378.8 | 349.7 | 343.2 | 321.3 | 644.9 | 58.8 | 18.2 | 106.8 | 6.2 | 202.7 | 13.3 | 414.5 | 720.4 | 794.6 | 466.6 | 517.1 | 808.9 | 710.4 | 641.1 | 729.7 | 304.1 | 489 | 713.2 | 124.6 | 211 | 281.2 | 531.6 | 642.5 | 722.1 | 510 | 622.7 | 218.9 | 381.3 | 349.5 | 257 | 286.7 | 411.4 | 269.3
1596.1 | 1357.1 | 472.3 | 188.92 | 220.8366 | 379.6 | 351.1 | 343.3 | 321.2 | 646.1 | 58.9 | 18.2 | 106.9 | 6.6 | 203 | 13.3 | 414.8 | 722.3 | 798.1 | 466.7 | 517.6 | 808.9 | 710.7 | 640.5 | 731.9 | 304.4 | 489.2 | 712.6 | 124.8 | 211.2 | 281.5 | 532.6 | 643.1 | 724.8 | 510.6 | 625.3 | 219.3 | 381.1 | 349.7 | 257.2 | 286.9 | 412 | 269.6
1597.1 | 1358.1 | 473.5 | 189.4 | 221.3977 | 380.5 | 351.5 | 343.3 | 321.4 | 645.6 | 59 | 18.2 | 107 | 6.3 | 212.1 | 12.6 | 415 | 724.5 | 799.5 | 466.9 | 518.2 | 808.6 | 711 | 639.3 | 736.8 | 304.6 | 489.4 | 713.1 | 125 | 211.5 | 281.6 | 532.9 | 642.5 | 724 | 510.6 | 625.6 | 219.6 | 381 | 350.6 | 257.4 | 287.2 | 412.6 | 269.9
1598.1 | 1359.1 | 473.9 | 189.56 | 221.5847 | 380.7 | 352.5 | 342.5 | 321.5 | 642.5 | 59 | 18.2 | 107.1 | 7 | 211.6 | 11.7 | 415.3 | 723.7 | 800 | 467.1 | 518.8 | 808.8 | 711.3 | 641 | 733.4 | 304.9 | 489.6 | 712.6 | 125.2 | 211.9 | 282.1 | 533.9 | 642.1 | 727.4 | 510.7 | 627.5 | 220 | 381.1 | 351.4 | 257.5 | 287.5 | 413.2 | 270.2
1599.1 | 1360.1 | 472.6 | 189.04 | 220.9769 | 381.1 | 353.6 | 342.2 | 321.6 | 640.9 | 59 | 18.2 | 107.2 | 7.3 | 203.4 | 12.1 | 415.6 | 719.2 | 797.1 | 467.3 | 519.3 | 808.7 | 711.6 | 641.2 | 731.8 | 305.2 | 489.6 | 711.8 | 125.4 | 212.2 | 282.5 | 534.8 | 641 | 732 | 510.7 | 629.4 | 220.4 | 381.1 | 351.7 | 257.7 | 287.8 | 413.8 | 270.5
1600.1 | 1361.1 | 473.9 | 189.56 | 221.5847 | 381.5 | 354.1 | 341.6 | 321.5 | 641.9 | 59.1 | 18.2 | 107.3 | 6.6 | 205.1 | 11.2 | 415.9 | 715.1 | 798.6 | 467.5 | 519.8 | 808.8 | 711.8 | 641.5 | 731.5 | 305.4 | 489.7 | 711.2 | 125.6 | 212.5 | 283.2 | 535.8 | 639.3 | 733 | 511.5 | 630 | 220.8 | 381.3 | 351.8 | 257.7 | 288.2 | 414.4 | 270.8
1601.1 | 1362.1 | 473.5 | 189.4 | 221.3977 | 382.9 | 353.5 | 342 | 320.9 | 644.6 | 59.1 | 18.2 | 107.4 | 6.2 | 211.8 | 11.5 | 416.1 | 712.9 | 800.4 | 467.6 | 520.4 | 809.4 | 712.2 | 642.9 | 731.2 | 305.6 | 489.9 | 711 | 125.8 | 212.7 | 283.5 | 536.5 | 637.4 | 729.7 | 511.8 | 627.7 | 221.1 | 381.4 | 351.6 | 257.8 | 288.3 | 415 | 271.1
1602.1 | 1363.1 | 473.6 | 189.44 | 221.4444 | 383.7 | 352.6 | 342.9 | 320.8 | 647.3 | 59.1 | 18.2 | 107.4 | 6.6 | 212.2 | 11.5 | 416.5 | 714.9 | 801.9 | 467.9 | 520.9 | 809.5 | 712.7 | 643.1 | 731.7 | 305.9 | 490 | 711.2 | 126 | 213 | 283.8 | 537.3 | 637.8 | 733 | 512.1 | 626.9 | 221.5 | 381.7 | 350.9 | 258 | 288.3 | 415.6 | 271.4
1603.1 | 1364.1 | 473.5 | 189.4 | 221.3977 | 383.8 | 351.6 | 343.9 | 320.8 | 648.6 | 59.3 | 18.2 | 107.4 | 6.4 | 204.9 | 10.8 | 416.7 | 711.7 | 798.1 | 468.1 | 521.4 | 809.6 | 713.2 | 644.3 | 733.7 | 306 | 490.3 | 710.5 | 126.2 | 213.3 | 284.4 | 538.3 | 637.5 | 731.4 | 512.5 | 625.1 | 221.9 | 381.6 | 350.4 | 258.2 | 288.3 | 416.2 | 271.7
1604.1 | 1365.1 | 472.2 | 188.88 | 220.7898 | 384.2 | 351.5 | 344.7 | 320.9 | 649.1 | 59.3 | 18.2 | 107.4 | 6.6 | 203.8 | 9.8 | 417.1 | 714.4 | 801.4 | 468.3 | 521.9 | 809.3 | 713.6 | 644.5 | 738 | 306.2 | 490.6 | 710.7 | 126.4 | 213.6 | 284.9 | 539.1 | 637.5 | 733.9 | 512.6 | 625.7 | 222.2 | 381.7 | 350.7 | 258.3 | 288.4 | 416.7 | 272
1605.1 | 1366.1 | 471.6 | 188.64 | 220.5093 | 385.6 | 351.1 | 345.2 | 320.7 | 649 | 59.4 | 18.2 | 107.4 | 6.2 | 225.7 | 8.5 | 417.3 | 718.4 | 799 | 468.5 | 522.5 | 809 | 713.9 | 644.7 | 743.2 | 306.4 | 490.9 | 711.5 | 126.6 | 213.9 | 285.1 | 539.9 | 637 | 730 | 512.5 | 625.7 | 222.6 | 381.7 | 350 | 258.5 | 288.6 | 417.3 | 272.3
1606.1 | 1367.1 | 473.9 | 189.56 | 221.5847 | 386.8 | 350.7 | 344.8 | 320.6 | 649.2 | 59.5 | 18.2 | 107.3 | 5.6 | 204.3 | 7.5 | 417.7 | 717.8 | 781.1 | 468.8 | 523 | 809 | 714.2 | 644.6 | 742.3 | 306.5 | 491.1 | 712.3 | 126.8 | 214.2 | 285.6 | 540.4 | 638.3 | 729.5 | 512.4 | 625.8 | 223 | 381.7 | 349.8 | 258.6 | 288.7 | 417.7 | 272.6
1607.1 | 1368.1 | 469.8 | 187.92 | 219.6677 | 389.1 | 350.3 | 345.7 | 321.1 | 650.3 | 59.6 | 18.2 | 107.3 | 5.4 | 201.9 | 5.4 | 418 | 723 | 777.8 | 468.9 | 523.5 | 807.9 | 714.5 | 646.9 | 734.5 | 306.7 | 491.2 | 711.6 | 127 | 214.5 | 286.6 | 541.3 | 639.3 | 730.3 | 512.3 | 627.3 | 223.4 | 382.2 | 350.1 | 258.8 | 288.7 | 418.3 | 272.9
1608.1 | 1369.1 | 472.3 | 188.92 | 220.8366 | 390.1 | 350.5 | 347 | 321.6 | 650.8 | 59.7 | 18.2 | 107.3 | 5.3 | 227 | 5 | 418.3 | 725.6 | 779.9 | 469.1 | 524 | 807.8 | 714.9 | 649.2 | 737.9 | 306.9 | 491.3 | 712.7 | 127.2 | 214.7 | 287.1 | 542.4 | 638.2 | 730.5 | 512.7 | 625.9 | 223.7 | 382.7 | 350.3 | 259 | 288.9 | 418.8 | 273.2
1609.1 | 1370.1 | 472.5 | 189 | 220.9301 | 391.7 | 350.7 | 348 | 322.2 | 650.5 | 59.7 | 18.2 | 107.2 | 5.1 | 204.4 | 6.7 | 418.5 | 725.6 | 776.5 | 469.3 | 524.4 | 807.5 | 715.4 | 649 | 740.2 | 307.1 | 491.5 | 714.6 | 127.4 | 215 | 287.1 | 542.9 | 637.3 | 726.8 | 513.1 | 624.8 | 224.1 | 383.2 | 350.5 | 259.2 | 289.1 | 419.4 | 273.5
1610.1 | 1371.1 | 472.4 | 188.96 | 220.8834 | 393.5 | 351.2 | 348.8 | 322.7 | 652.2 | 59.9 | 18.2 | 107.2 | 4.8 | 213.3 | 8 | 418.7 | 722.5 | 776.1 | 469.5 | 524.9 | 806.9 | 715.8 | 648.1 | 740.9 | 307.3 | 491.4 | 715.6 | 127.6 | 215.4 | 287.7 | 543.9 | 635.8 | 727.7 | 513.5 | 622.7 | 224.5 | 383.3 | 350.7 | 259.3 | 289.2 | 420 | 273.9
1611.1 | 1372.1 | 472.6 | 189.04 | 220.9769 | 395.2 | 351.5 | 349.3 | 322.9 | 651.1 | 59.9 | 18.2 | 107.2 | 5.4 | 214.7 | 7.5 | 419 | 721.2 | 770.4 | 469.7 | 525.3 | 807.6 | 716.2 | 648.4 | 739.8 | 307.5 | 491.4 | 714.6 | 127.8 | 215.7 | 288.1 | 544.5 | 635.8 | 725 | 513.7 | 625 | 224.9 | 383.3 | 351.1 | 259.4 | 289.3 | 420.5 | 274.2
1612.1 | 1373.1 | 472.3 | 188.92 | 220.8366 | 395.2 | 352.5 | 349.8 | 323 | 648.5 | 60 | 18.2 | 107.1 | 5.8 | 236.3 | 6.5 | 419.3 | 719.7 | 769 | 469.8 | 525.8 | 808.5 | 716.5 | 647.6 | 744.3 | 307.7 | 491.5 | 716.4 | 128 | 216 | 288.3 | 545.2 | 633.8 | 719 | 513.9 | 625 | 225.3 | 383 | 351.7 | 259.5 | 289.5 | 421.1 | 274.5
1613.1 | 1374.1 | 472.2 | 188.88 | 220.7898 | 395.9 | 352.7 | 350.3 | 323 | 646.8 | 60.1 | 18.2 | 107.1 | 5.4 | 242.6 | 6.8 | 419.5 | 723.1 | 772.5 | 469.9 | 526.3 | 808.6 | 716.8 | 648.1 | 735.6 | 307.9 | 491.2 | 717.2 | 128.2 | 216.2 | 288.3 | 546.7 | 632.6 | 719.5 | 514.2 | 624.7 | 225.7 | 382.8 | 351.4 | 259.7 | 289.9 | 421.5 | 274.8
1614.1 | 1375.1 | 472.6 | 189.04 | 220.9769 | 397.2 | 354.8 | 350.4 | 323.3 | 642.4 | 60.2 | 18.2 | 107.1 | 6.3 | 233 | 7.6 | 419.6 | 725.8 | 778.6 | 470.1 | 526.8 | 807.7 | 717.1 | 647.8 | 730.5 | 308.1 | 491.2 | 716.8 | 128.4 | 216.6 | 288.5 | 547.2 | 630.4 | 712.3 | 514.2 | 624.3 | 226.2 | 382.9 | 351.9 | 259.9 | 290.1 | 422 | 275.1
1615.1 | 1376.1 | 472.8 | 189.12 | 221.0704 | 399.1 | 356.1 | 350.5 | 323.8 | 641.3 | 60.2 | 18.2 | 107 | 5.6 | 220.5 | 8.1 | 420 | 723.9 | 772.3 | 470.3 | 527.3 | 807.1 | 717.3 | 647.5 | 727.2 | 308.2 | 491.1 | 716.4 | 128.7 | 216.9 | 288.7 | 548.3 | 632.4 | 711.4 | 514.9 | 624.6 | 226.7 | 383.5 | 352.8 | 260.1 | 290.4 | 422.5 | 275.4
1616.1 | 1377.1 | 472.6 | 189.04 | 220.9769 | 402.1 | 356.2 | 350.3 | 324.5 | 640.9 | 60.2 | 18.1 | 106.9 | 5.6 | 241.3 | 7.1 | 420.2 | 723 | 764.2 | 470.5 | 527.8 | 807.3 | 717.6 | 646.5 | 720.5 | 308.4 | 491.1 | 716.3 | 128.9 | 217.2 | 288.9 | 549.7 | 633.4 | 711.4 | 515.6 | 626.3 | 227.2 | 384 | 353.7 | 260.3 | 290.7 | 423.1 | 275.7
1617.1 | 1378.1 | 473.3 | 189.32 | 221.3042 | 403 | 355.6 | 349.5 | 325.6 | 646.6 | 60.2 | 18.1 | 106.8 | 5.7 | 251.7 | 7.1 | 420.4 | 721.6 | 762.6 | 470.6 | 528.3 | 807.4 | 717.9 | 649.1 | 721.8 | 308.6 | 491 | 716.6 | 129.1 | 217.4 | 289.2 | 551.2 | 635.3 | 718.7 | 516.5 | 629.2 | 227.8 | 384.4 | 353.9 | 260.5 | 291.1 | 423.7 | 276
1618.1 | 1379.1 | 471.5 | 188.6 | 220.4625 | 403.1 | 355.4 | 349.5 | 326.4 | 645 | 60.2 | 18.1 | 106.7 | 5.9 | 237.5 | 7.3 | 420.5 | 725.9 | 760.6 | 470.6 | 528.7 | 807.2 | 718.1 | 648.8 | 720.2 | 308.8 | 490.9 | 715.2 | 129.3 | 217.7 | 289.5 | 552.2 | 635 | 708.8 | 517.2 | 626.4 | 228.5 | 384.8 | 354.4 | 260.7 | 291.4 | 424.3 | 276.3
1619.1 | 1380.1 | 472.3 | 188.92 | 220.8366 | 404.2 | 354.9 | 349.6 | 326.9 | 642.9 | 60.3 | 18.1 | 106.7 | 6.4 | 256.1 | 8.9 | 420.6 | 724.6 | 758.9 | 470.7 | 529.2 | 807.8 | 718.4 | 649 | 720.9 | 309 | 490.8 | 714.8 | 129.5 | 217.9 | 289.8 | 553.3 | 635.7 | 707 | 517.6 | 627 | 229.1 | 384.8 | 355.2 | 260.9 | 291.7 | 424.8 | 276.7
1620.1 | 1381.1 | 471.4 | 188.56 | 220.4158 | 405.4 | 354 | 350.1 | 327.4 | 638.6 | 60.4 | 18.1 | 106.7 | 5.8 | 248.6 | 11.9 | 420.8 | 721.2 | 747.9 | 470.9 | 529.8 | 807 | 718.8 | 649.3 | 713.1 | 309.3 | 490.7 | 713.6 | 129.7 | 218.2 | 290.1 | 554.4 | 635.4 | 696 | 518.7 | 626.6 | 229.8 | 385.6 | 356.3 | 261.1 | 292 | 425.4 | 277
1621.1 | 1382.1 | 472.8 | 189.12 | 221.0704 | 406.5 | 353.8 | 350.1 | 328.1 | 634.6 | 60.5 | 18.1 | 106.7 | 5.9 | 247.8 | 12.8 | 421.1 | 719.7 | 744.2 | 471.1 | 530.2 | 805.9 | 719.2 | 651 | 713.6 | 309.4 | 490.6 | 712.5 | 129.9 | 218.4 | 290.2 | 555.2 | 634.8 | 690.6 | 520.3 | 624.9 | 230.4 | 386.3 | 357 | 261.4 | 292.3 | 425.9 | 277.3
1622.1 | 1383.1 | 472.7 | 189.08 | 221.0236 | 409.7 | 353.7 | 350.8 | 329.2 | 633.7 | 60.5 | 18.1 | 106.7 | 5.8 | 247.6 | 11.8 | 421.3 | 720.4 | 750.4 | 471.3 | 530.8 | 806.4 | 719.5 | 652.1 | 711.6 | 309.5 | 490.3 | 712.5 | 130.1 | 218.6 | 290.5 | 555.9 | 636.3 | 691.9 | 521.1 | 626.4 | 231 | 386.5 | 357.1 | 261.5 | 292.5 | 426.4 | 277.7
1623.1 | 1384.1 | 472 | 188.8 | 220.6963 | 410.2 | 353.7 | 351.5 | 329.9 | 638.9 | 60.5 | 18.1 | 106.7 | 5.9 | 255.7 | 10 | 421.5 | 719.6 | 756.9 | 471.5 | 531.3 | 807.1 | 719.7 | 650.8 | 715.8 | 309.6 | 489.7 | 713.3 | 130.3 | 218.9 | 291 | 556.5 | 637.8 | 701.5 | 521.5 | 628.7 | 231.7 | 386.4 | 356.8 | 261.6 | 292.6 | 426.9 | 278
1624.1 | 1385.1 | 472.1 | 188.84 | 220.7431 | 409.5 | 354.3 | 351.4 | 329.7 | 637.7 | 60.5 | 18.1 | 106.7 | 6.3 | 250.4 | 8.1 | 421.7 | 717.7 | 754 | 471.7 | 531.8 | 807.2 | 719.9 | 648.9 | 714.6 | 309.8 | 489.7 | 713.6 | 130.5 | 219.1 | 291.5 | 557 | 634.1 | 702.8 | 521.7 | 627.8 | 232.2 | 386 | 356.1 | 261.6 | 292.7 | 427.5 | 278.3
1625.1 | 1386.1 | 472.5 | 189 | 220.9301 | 409.5 | 354.1 | 352.1 | 328.8 | 642.5 | 60.5 | 18.1 | 106.7 | 6.2 | 215.5 | 6.4 | 422 | 714.8 | 748.5 | 471.9 | 532.3 | 807 | 720.2 | 649 | 706.9 | 309.9 | 489.8 | 712.5 | 130.7 | 219.3 | 291.8 | 557.5 | 634.7 | 694.4 | 522 | 623.8 | 232.7 | 385.9 | 355.2 | 261.7 | 292.8 | 428 | 278.6
1626.1 | 1387.1 | 472.3 | 188.92 | 220.8366 | 408.4 | 353.4 | 352.5 | 328.4 | 641.5 | 60.5 | 18.1 | 106.9 | 5.9 | 267.2 | 6.5 | 422.1 | 718.4 | 753.7 | 472 | 532.8 | 807.3 | 720.4 | 650.9 | 708.5 | 310.1 | 489.3 | 712.8 | 130.9 | 219.6 | 292.1 | 557.9 | 634.7 | 685.7 | 522.6 | 621.4 | 233.2 | 385.7 | 354.6 | 261.7 | 293 | 428.5 | 278.9
1627.1 | 1388.1 | 471.6 | 188.64 | 220.5093 | 409.5 | 354.1 | 352.4 | 328.8 | 638.7 | 60.6 | 18.1 | 107 | 5.9 | 233.9 | 6.9 | 422.5 | 718.1 | 749.8 | 472.3 | 533.3 | 807.4 | 720.8 | 654.2 | 704.5 | 310.3 | 489.1 | 712 | 131.1 | 219.9 | 292.2 | 559.2 | 635.5 | 688.1 | 523.2 | 621.7 | 233.6 | 385.7 | 355 | 261.9 | 293.3 | 429.3 | 279.2
1628.1 | 1389.1 | 471.3 | 188.52 | 220.369 | 409.6 | 355.4 | 352 | 329.3 | 638.5 | 60.7 | 18.1 | 107.1 | 5.9 | 235.3 | 6.9 | 423 | 717.5 | 750 | 472.6 | 533.7 | 805.8 | 721.2 | 655.1 | 696.6 | 310.5 | 489.2 | 711.3 | 131.3 | 220.1 | 292.4 | 560.2 | 636.6 | 680.5 | 523.9 | 620.6 | 234.1 | 386.6 | 355.7 | 262.1 | 293.6 | 430 | 279.5
1629.1 | 1390.1 | 469 | 187.6 | 219.2936 | 408.9 | 356.2 | 351.2 | 330.3 | 634.7 | 60.8 | 18.1 | 107.1 | 4.8 | 247.3 | 6.8 | 423.3 | 721.2 | 757.3 | 472.8 | 534.2 | 806.3 | 721.7 | 656.2 | 696.7 | 310.7 | 489 | 711.5 | 131.5 | 220.4 | 292.7 | 561 | 635.9 | 678.2 | 524.3 | 619.5 | 234.7 | 387.4 | 356.6 | 262.3 | 294.1 | 430.5 | 279.9
1630.1 | 1391.1 | 471.6 | 188.64 | 220.5093 | 409.6 | 356.9 | 351.1 | 331 | 628.2 | 60.8 | 18.1 | 107.2 | 5.2 | 219.8 | 9.2 | 423.6 | 720.7 | 768.9 | 473.1 | 534.7 | 807.3 | 722 | 655.1 | 696.9 | 310.9 | 488.9 | 710.9 | 131.7 | 220.6 | 292.9 | 561.2 | 634 | 679 | 524.7 | 620.3 | 235.2 | 387.4 | 357.1 | 262.4 | 294.4 | 431 | 280.2
1631.1 | 1392.1 | 471.1 | 188.44 | 220.2755 | 411.4 | 357.4 | 351.6 | 330.8 | 629.4 | 60.8 | 18.1 | 107.3 | 5.3 | 219.1 | 9.3 | 423.7 | 717.8 | 774.5 | 473.2 | 535.2 | 807.9 | 722.4 | 654.8 | 700.9 | 311.2 | 488.4 | 711.2 | 131.9 | 220.9 | 293.2 | 561.7 | 634.2 | 682.4 | 524.7 | 621.7 | 235.8 | 387.1 | 358.3 | 262.5 | 294.5 | 431.5 | 280.5
1632.1 | 1393.1 | 469.8 | 187.92 | 219.6677 | 412.5 | 358.1 | 351.8 | 330 | 630 | 60.8 | 18.1 | 107.5 | 5.2 | 240.7 | 8.7 | 423.9 | 715.9 | 776.1 | 473.5 | 535.7 | 808.5 | 722.8 | 653.2 | 702.4 | 311.3 | 487.9 | 711 | 132.1 | 221.2 | 293.4 | 562.1 | 633.2 | 683 | 525 | 623 | 236.4 | 386.8 | 358.4 | 262.5 | 294.7 | 431.9 | 280.8
1633.1 | 1394.1 | 471.9 | 188.76 | 220.6496 | 412 | 359.9 | 351.6 | 329.8 | 631.6 | 60.8 | 18.1 | 107.5 | 6.4 | 227.9 | 9 | 424 | 717 | 777.7 | 473.6 | 536.2 | 809.2 | 723.3 | 652.4 | 702.7 | 311.5 | 487.6 | 711.1 | 132.3 | 221.5 | 293.8 | 563.2 | 632.5 | 693.6 | 525.8 | 625.1 | 236.9 | 386.8 | 358.4 | 262.7 | 294.9 | 432.4 | 281.1
1634.1 | 1395.1 | 469 | 187.6 | 219.2936 | 413.2 | 361.1 | 351.8 | 330.2 | 630.3 | 60.7 | 18.1 | 107.6 | 6 | 212.6 | 8.8 | 424.3 | 715.8 | 782.6 | 473.9 | 536.8 | 809 | 723.7 | 651 | 705.6 | 311.8 | 487.5 | 710.9 | 132.5 | 221.8 | 294 | 563.2 | 630.4 | 696 | 525.9 | 626.5 | 237.4 | 386.6 | 358.3 | 262.7 | 295 | 432.9 | 281.4
1635.1 | 1396.1 | 470.9 | 188.36 | 220.182 | 415 | 362.1 | 351.8 | 330.2 | 631.8 | 60.7 | 18.1 | 107.6 | 6.1 | 225.5 | 10 | 424.6 | 714.1 | 783.4 | 474.1 | 537.3 | 807.9 | 724.1 | 650.4 | 712 | 312 | 487.4 | 711.8 | 132.7 | 222.1 | 294.5 | 562.9 | 629.2 | 695.3 | 525.8 | 625.2 | 237.9 | 386.2 | 358.2 | 262.7 | 295.1 | 433.4 | 281.7
1636.1 | 1397.1 | 470.2 | 188.08 | 219.8547 | 417.7 | 361.4 | 352.3 | 330 | 635 | 60.7 | 18.1 | 107.5 | 5.7 | 211.5 | 10.5 | 424.7 | 713.9 | 781.5 | 474.1 | 537.8 | 807.3 | 724.3 | 649.8 | 711.7 | 312.2 | 487.2 | 711.5 | 132.9 | 222.4 | 295.1 | 562.9 | 628.1 | 697.8 | 525.9 | 623.7 | 238.2 | 385.9 | 358.2 | 262.7 | 295.2 | 433.9 | 282
1637.1 | 1398.1 | 471.9 | 188.76 | 220.6496 | 418 | 360 | 353.1 | 330.2 | 637.4 | 60.8 | 18.1 | 107.5 | 6.7 | 216.2 | 10.2 | 424.9 | 718 | 781.7 | 474.3 | 538.2 | 807.7 | 724.6 | 649.5 | 707.8 | 312.5 | 487.2 | 711.1 | 133.1 | 222.7 | 295.4 | 563.8 | 629.2 | 697.5 | 526.2 | 621.7 | 238.6 | 385.8 | 357.6 | 262.8 | 295.4 | 434.3 | 282.3
1638.1 | 1399.1 | 470.2 | 188.08 | 219.8547 | 418.2 | 359.2 | 353.4 | 330.3 | 639.9 | 60.9 | 18.1 | 107.5 | 7.4 | 218 | 10.2 | 425.1 | 719.3 | 779.6 | 474.5 | 538.7 | 808 | 724.9 | 650.7 | 708.2 | 312.6 | 486.8 | 710.5 | 133.3 | 223 | 295.9 | 564.4 | 629.2 | 700.3 | 526.6 | 621.8 | 238.9 | 385.6 | 357.3 | 262.9 | 295.4 | 434.8 | 282.6
1639.1 | 1400.1 | 470.6 | 188.24 | 220.0417 | 420.7 | 358.4 | 353.7 | 330.5 | 642.3 | 60.9 | 18.1 | 107.6 | 7.6 | 216.8 | 8.6 | 425.2 | 723.3 | 766.7 | 474.6 | 539.2 | 808.1 | 725.2 | 649.5 | 701.5 | 312.7 | 486.8 | 709.5 | 133.5 | 223.2 | 296.1 | 565.8 | 629.4 | 702.3 | 527.6 | 621.5 | 239.1 | 385.8 | 357.4 | 263 | 295.4 | 435.3 | 282.9
1640.1 | 1401.1 | 472 | 188.8 | 220.6963 | 424.2 | 357.8 | 354.6 | 330.6 | 641.3 | 60.9 | 18.1 | 107.7 | 6.5 | 244.3 | 7.8 | 425.3 | 722.7 | 759.3 | 474.7 | 539.6 | 807.6 | 725.5 | 648.8 | 693.5 | 312.9 | 486.7 | 708.1 | 133.7 | 223.5 | 296.6 | 567.2 | 628.4 | 696 | 528.8 | 619.6 | 239.3 | 386.2 | 357.3 | 263.1 | 295.5 | 435.8 | 283.2
1641.1 | 1402.1 | 472.2 | 188.88 | 220.7898 | 424.3 | 357.6 | 355.7 | 330.9 | 635.3 | 61 | 18.1 | 107.8 | 6.1 | 250.2 | 7.4 | 425.6 | 727.2 | 746.3 | 474.9 | 540.1 | 807.9 | 725.8 | 648.9 | 696.5 | 313.1 | 486.7 | 708.1 | 133.9 | 223.8 | 296.7 | 568.3 | 627 | 683.6 | 530.4 | 617.8 | 239.5 | 386.3 | 357.2 | 263.2 | 295.7 | 436.2 | 283.5
1642.1 | 1403.1 | 471.8 | 188.72 | 220.6028 | 424.3 | 357.6 | 356.2 | 331 | 633.8 | 61 | 18.1 | 107.9 | 5.9 | 212.3 | 6.2 | 425.8 | 730.3 | 743.9 | 475 | 540.6 | 808.6 | 726.2 | 650.1 | 698.4 | 313.3 | 486.8 | 709.3 | 134.1 | 224.1 | 297 | 569.4 | 626.9 | 677.1 | 531.6 | 616.9 | 239.7 | 386.4 | 357.2 | 263.3 | 295.9 | 436.6 | 283.8
1643.1 | 1404.1 | 471.6 | 188.64 | 220.5093 | 424.5 | 357.3 | 356.2 | 331.2 | 631 | 61 | 18.1 | 108 | 5.9 | 243 | 6.2 | 425.9 | 726.6 | 739.5 | 475.1 | 541 | 809.3 | 726.4 | 649.2 | 701.3 | 313.4 | 486.4 | 710.7 | 134.3 | 224.4 | 297.2 | 569.5 | 624.8 | 672.2 | 532.2 | 615.5 | 239.9 | 386.6 | 357.1 | 263.4 | 295.9 | 437 | 284.1
1644.1 | 1405.1 | 472.5 | 189 | 220.9301 | 423.7 | 357.2 | 356.6 | 331.3 | 629.4 | 61.1 | 18.1 | 108 | 5.5 | 239.1 | 6.4 | 426.2 | 722.8 | 737.2 | 475.4 | 541.4 | 808.8 | 726.6 | 647.5 | 693.4 | 313.6 | 486.4 | 709.6 | 134.5 | 224.7 | 297.9 | 570.5 | 623.9 | 669 | 533.2 | 613.9 | 240.1 | 387.1 | 357.6 | 263.5 | 296 | 437.4 | 284.4
1645.1 | 1406.1 | 471.3 | 188.52 | 220.369 | 423.5 | 356.3 | 357.5 | 331 | 632.2 | 61.1 | 18.1 | 108 | 6.6 | 170.3 | 4.6 | 426.3 | 727.4 | 739.2 | 475.5 | 541.9 | 809.4 | 726.9 | 646.9 | 692.2 | 313.8 | 486.4 | 709.3 | 134.8 | 224.9 | 298.2 | 570.5 | 626.2 | 665.5 | 533.8 | 613.8 | 240.3 | 387.4 | 357.9 | 263.7 | 296.2 | 437.8 | 284.8
1646.1 | 1407.1 | 472.8 | 189.12 | 221.0704 | 425.8 | 356 | 357.9 | 331.3 | 631.8 | 61.1 | 18.1 | 108.1 | 7 | 241.8 | 3.2 | 426.5 | 727.6 | 743.4 | 475.6 | 542.3 | 810.5 | 727.1 | 648.6 | 692.7 | 313.9 | 485.6 | 710.1 | 135 | 225.2 | 298.1 | 571.4 | 623.8 | 658.6 | 534.6 | 612.8 | 240.4 | 387.4 | 358.3 | 263.8 | 296.5 | 438.1 | 285.1
1647.1 | 1408.1 | 473.2 | 189.28 | 221.2574 | 426.9 | 356.3 | 357.9 | 331.5 | 626.9 | 61.1 | 18 | 108.1 | 7.8 | 236.3 | 3.5 | 426.6 | 730.8 | 736.2 | 475.7 | 542.8 | 811.6 | 727.4 | 650.3 | 691 | 314 | 485.5 | 710.6 | 135.2 | 225.5 | 298.2 | 570.8 | 621.5 | 656.4 | 534.2 | 611.7 | 240.6 | 387.2 | 358.4 | 264 | 296.7 | 438.5 | 285.4
1648.1 | 1409.1 | 472 | 188.8 | 220.6963 | 427.9 | 356.7 | 357.7 | 331.6 | 624.8 | 61.1 | 18 | 108.2 | 7.6 | 215 | 6.2 | 426.9 | 729.1 | 743.5 | 476 | 543.2 | 812.4 | 727.8 | 651 | 693.6 | 314.1 | 485.6 | 710.7 | 135.4 | 225.7 | 298.5 | 570.6 | 619.9 | 653.9 | 534.3 | 611.7 | 240.9 | 387.1 | 358.8 | 264.1 | 296.9 | 438.9 | 285.7
1649.1 | 1410.1 | 473 | 189.2 | 221.1639 | 428.1 | 357.3 | 357.6 | 331.5 | 626.3 | 61.2 | 18 | 108.3 | 7.1 | 247.8 | 7.2 | 427.3 | 725.5 | 751.5 | 476.3 | 543.7 | 812.1 | 727.9 | 651.3 | 693.3 | 314.4 | 485.6 | 710.1 | 135.6 | 226 | 298.9 | 570.6 | 619.9 | 655 | 533.6 | 612.7 | 241.2 | 387 | 359.4 | 264.3 | 297.3 | 439.3 | 286
1650.1 | 1411.1 | 472.5 | 189 | 220.9301 | 427.6 | 358.6 | 357.7 | 331.6 | 632.1 | 61.2 | 18 | 108.4 | 7 | 224.9 | 6.6 | 427.4 | 729 | 753.9 | 476.4 | 544.1 | 811.5 | 728.1 | 651 | 690.4 | 314.8 | 485.6 | 709.9 | 135.7 | 226.3 | 299.2 | 571.9 | 623.7 | 664.6 | 533.6 | 616.2 | 241.4 | 387.5 | 360.2 | 264.6 | 297.6 | 439.8 | 286.3
1651.1 | 1412.1 | 473.5 | 189.4 | 221.3977 | 426.3 | 359.4 | 357.2 | 332.4 | 634.8 | 61.2 | 18 | 108.4 | 6.6 | 215 | 6 | 427.7 | 730.7 | 754.2 | 476.6 | 544.6 | 811.9 | 728.4 | 650.3 | 692.9 | 315.1 | 485.9 | 709.7 | 136 | 226.5 | 299.3 | 573.2 | 625.4 | 666.7 | 534.3 | 616.1 | 241.7 | 387.6 | 360.5 | 264.7 | 297.8 | 440.3 | 286.6
1652.1 | 1413.1 | 472.8 | 189.12 | 221.0704 | 426.9 | 359 | 356.9 | 333.2 | 631.4 | 61.3 | 18 | 108.6 | 6.1 | 219.1 | 6.9 | 427.8 | 733.3 | 757.3 | 476.8 | 545.1 | 812.3 | 728.6 | 650.7 | 694.2 | 315.4 | 486.1 | 710.2 | 136.2 | 226.8 | 299.6 | 573.2 | 624 | 667.4 | 534.6 | 615.2 | 242.1 | 387.6 | 360.6 | 264.9 | 297.9 | 440.8 | 286.9
1653.1 | 1414.1 | 472.8 | 189.12 | 221.0704 | 429.7 | 358.1 | 356.9 | 333.1 | 627.7 | 61.3 | 18 | 108.7 | 6.1 | 205.6 | 9.3 | 428 | 731.2 | 757.6 | 477 | 545.5 | 812.3 | 728.8 | 650.1 | 693 | 315.8 | 485.7 | 710.2 | 136.4 | 227 | 299.8 | 572.1 | 623 | 664.7 | 533.9 | 615.1 | 242.4 | 387.5 | 360.9 | 265.1 | 298.2 | 441.3 | 287.2
1654.1 | 1415.1 | 471.4 | 188.56 | 220.4158 | 432.3 | 357.9 | 357.3 | 333 | 624.9 | 61.3 | 18 | 108.7 | 6.1 | 239.4 | 10 | 428.4 | 727.9 | 765.5 | 477.3 | 546 | 812 | 729 | 649.9 | 695 | 316.1 | 485.8 | 710.2 | 136.6 | 227.2 | 300 | 572.4 | 622.8 | 665.6 | 533.5 | 614.6 | 242.7 | 387.4 | 361 | 265.3 | 298.5 | 441.7 | 287.5
1655.1 | 1416.1 | 472 | 188.8 | 220.6963 | 433.9 | 358.5 | 357.4 | 333.2 | 624.7 | 61.3 | 18 | 108.7 | 7 | 213.4 | 8.8 | 428.6 | 727.1 | 771 | 477.4 | 546.5 | 811.3 | 729.1 | 650.2 | 703.3 | 316.2 | 485.4 | 711.2 | 136.8 | 227.5 | 300.3 | 573.5 | 625.8 | 669.6 | 534.2 | 617.1 | 243.1 | 387.2 | 361.5 | 265.4 | 298.8 | 442.2 | 287.8
1656.1 | 1417.1 | 473.9 | 189.56 | 221.5847 | 435.7 | 359 | 357.2 | 333.3 | 621.8 | 61.3 | 18 | 108.8 | 7.3 | 213 | 10.6 | 428.8 | 728.3 | 777.5 | 477.6 | 547 | 810.7 | 729.2 | 649.7 | 703.7 | 316.3 | 485.6 | 710.7 | 137 | 227.8 | 300.5 | 574.7 | 624.1 | 672.5 | 534.9 | 616.4 | 243.5 | 387 | 362 | 265.6 | 299.2 | 442.6 | 288.1
1657.1 | 1418.1 | 475.1 | 190.04 | 222.1458 | 439.1 | 359.9 | 357.1 | 333.1 | 622.4 | 61.4 | 18 | 108.8 | 7.3 | 202.8 | 11.3 | 429 | 728.7 | 776.6 | 477.8 | 547.5 | 810.2 | 729.3 | 651 | 703.2 | 316.5 | 485.5 | 710 | 137.2 | 228 | 300.9 | 575.3 | 623.7 | 674.8 | 535.5 | 616.2 | 243.9 | 386.7 | 362 | 265.7 | 299.3 | 443.1 | 288.4
1658.1 | 1419.1 | 474.2 | 189.68 | 221.725 | 443.3 | 359.6 | 357.2 | 332.9 | 622.8 | 61.4 | 18 | 108.9 | 7.6 | 211.9 | 12.2 | 429.2 | 725 | 778.6 | 478 | 548 | 810.6 | 729.4 | 650.3 | 699.3 | 316.6 | 485.4 | 709.1 | 137.4 | 228.3 | 301.2 | 575.5 | 623 | 671.6 | 536.4 | 615 | 244.4 | 386.2 | 362 | 265.8 | 299.5 | 443.6 | 288.7
1659.1 | 1420.1 | 472.7 | 189.08 | 221.0236 | 445.1 | 360.9 | 357.1 | 333 | 621.9 | 61.4 | 18 | 109.1 | 6.2 | 215 | 15.1 | 429.6 | 726.3 | 776.5 | 478.3 | 548.5 | 810.4 | 729.7 | 649.8 | 700.6 | 316.8 | 485.5 | 710 | 137.6 | 228.6 | 301.4 | 575.9 | 620.8 | 672.4 | 537 | 615.1 | 244.7 | 385.8 | 362.1 | 266 | 299.6 | 444 | 288.9
1660.1 | 1421.1 | 473.6 | 189.44 | 221.4444 | 446.6 | 361.8 | 356.7 | 333.2 | 619.9 | 61.5 | 18 | 109.3 | 5.6 | 223.6 | 14 | 429.9 | 726.1 | 771.2 | 478.6 | 549 | 810.3 | 730 | 650.6 | 700.4 | 317.1 | 485.5 | 710 | 137.8 | 228.9 | 301.7 | 576.1 | 618.5 | 673.7 | 537.2 | 614.2 | 245.1 | 385.3 | 362.3 | 266.1 | 299.7 | 444.3 | 289.2
1661.1 | 1422.1 | 473.8 | 189.52 | 221.538 | 449.7 | 364.6 | 356.8 | 333.5 | 623 | 61.4 | 18 | 109.5 | 6.3 | 220 | 13.6 | 430 | 724.7 | 768.5 | 478.7 | 549.4 | 810.2 | 730.3 | 652.2 | 698.8 | 317.3 | 485.2 | 709.7 | 138 | 229.2 | 302 | 576.6 | 619.5 | 677.1 | 537.3 | 614.9 | 245.4 | 385.2 | 362.4 | 266.2 | 299.9 | 444.7 | 289.5
1662.1 | 1423.1 | 470.9 | 188.36 | 220.182 | 450.2 | 366.3 | 357 | 333.4 | 623.7 | 61.5 | 18 | 109.5 | 7 | 215.9 | 13 | 430.3 | 726.7 | 768.6 | 478.9 | 549.9 | 810.1 | 730.4 | 652.4 | 702.9 | 317.5 | 485.6 | 710.1 | 138.2 | 229.4 | 302.3 | 578 | 619.3 | 676.8 | 538.1 | 614.9 | 245.7 | 385.5 | 362.7 | 266.3 | 300.3 | 445 | 289.8
1663.1 | 1424.1 | 473.2 | 189.28 | 221.2574 | 450.5 | 367.3 | 357.2 | 333.1 | 622.8 | 61.5 | 18 | 109.5 | 5.9 | 216.3 | 11.6 | 430.6 | 725.3 | 773.6 | 479.2 | 550.3 | 810.4 | 730.6 | 652.9 | 706.4 | 317.7 | 485.7 | 710.5 | 138.4 | 229.7 | 302.4 | 578.4 | 619.9 | 676.1 | 538.5 | 613.5 | 246 | 385.5 | 362.6 | 266.5 | 300.4 | 445.5 | 290.1
1664.1 | 1425.1 | 473.3 | 189.32 | 221.3042 | 453.7 | 367.2 | 357 | 333.3 | 621.1 | 61.6 | 18 | 109.6 | 5.4 | 194.5 | 10.4 | 430.9 | 725.5 | 771.6 | 479.5 | 550.8 | 810.3 | 730.9 | 653.2 | 706.9 | 317.9 | 485.2 | 710.6 | 138.6 | 230 | 302.6 | 578.9 | 619.9 | 674.8 | 538.7 | 613.8 | 246.3 | 385.4 | 362.3 | 266.7 | 300.7 | 445.9 | 290.4
1665.1 | 1426.1 | 473.1 | 189.24 | 221.2107 | 458.4 | 366.4 | 356.7 | 333.8 | 623.3 | 61.6 | 18 | 109.7 | 5.1 | 218.8 | 9.1 | 431 | 726.8 | 779.4 | 479.6 | 551.3 | 810.5 | 731.1 | 651.7 | 709.3 | 318.1 | 485.6 | 710.7 | 138.8 | 230.2 | 302.9 | 579.6 | 619.4 | 678 | 539.5 | 614.3 | 246.6 | 385.3 | 362.1 | 266.9 | 300.9 | 446.3 | 290.7
1666.1 | 1427.1 | 473.7 | 189.48 | 221.4912 | 463.5 | 365.4 | 356.8 | 334.1 | 624.8 | 61.8 | 18 | 110 | 5.5 | 233.3 | 8.3 | 431.2 | 728 | 777.3 | 479.8 | 551.8 | 811 | 731.3 | 651.8 | 710.5 | 318.3 | 485.5 | 711.1 | 139 | 230.5 | 303.4 | 580.4 | 619.5 | 677 | 540.1 | 614 | 247 | 385.2 | 362.1 | 267 | 301.1 | 446.7 | 291
1667.1 | 1428.1 | 472.3 | 188.92 | 220.8366 | 467.8 | 367 | 356.9 | 334.1 | 626.3 | 61.8 | 18 | 110.1 | 6.4 | 218.3 | 9.9 | 431.4 | 731.7 | 778 | 480 | 552.2 | 811.7 | 731.6 | 652.1 | 708.5 | 318.4 | 485.5 | 711.4 | 139.2 | 230.8 | 303.5 | 580.1 | 619.3 | 673 | 540.5 | 613.6 | 247.3 | 384.9 | 361.5 | 267.2 | 301.3 | 447.1 | 291.3
1668.1 | 1429.1 | 473.3 | 189.32 | 221.3042 | 471.5 | 367.6 | 357.7 | 333.5 | 625.7 | 61.9 | 18 | 110.3 | 6.7 | 225.7 | 10.4 | 431.6 | 733.9 | 781.2 | 480.2 | 552.7 | 812.1 | 731.8 | 651.8 | 706.8 | 318.6 | 485 | 711.6 | 139.4 | 231 | 303.7 | 580.5 | 619.5 | 676.9 | 541.1 | 614.6 | 247.7 | 385.1 | 361.6 | 267.4 | 301.4 | 447.5 | 291.6
1669.1 | 1430.1 | 474.3 | 189.72 | 221.7717 | 469.7 | 367.9 | 358 | 333.6 | 624 | 61.9 | 18 | 110.5 | 6.6 | 208.7 | 10.2 | 431.9 | 735.4 | 775.5 | 480.4 | 553.2 | 812.2 | 732.1 | 651.6 | 702.9 | 318.8 | 485.1 | 711.4 | 139.6 | 231.3 | 304 | 580.9 | 619.1 | 674.8 | 541.4 | 614.6 | 248.1 | 385.5 | 361.9 | 267.6 | 301.6 | 447.9 | 291.9
1670.1 | 1431.1 | 474.4 | 189.76 | 221.8185 | 471 | 367.6 | 358.1 | 333.9 | 625 | 61.9 | 18 | 110.7 | 6.3 | 193.3 | 7.9 | 432.1 | 736.6 | 769.4 | 480.6 | 553.7 | 811.2 | 732.5 | 651.1 | 701.6 | 319 | 484.9 | 711.1 | 139.8 | 231.5 | 304.2 | 581.8 | 619.3 | 674.7 | 542.1 | 614.1 | 248.5 | 385.9 | 362.5 | 267.8 | 301.8 | 448.3 | 292.2
1671.1 | 1432.1 | 473.7 | 189.48 | 221.4912 | 469.3 | 366.7 | 357.9 | 334.3 | 622.3 | 61.9 | 17.9 | 110.7 | 6.3 | 201.4 | 8.2 | 432.2 | 736.6 | 770.5 | 480.7 | 554.1 | 811.3 | 732.9 | 650.6 | 699.5 | 319.1 | 485 | 711.6 | 140 | 231.8 | 304.3 | 583.7 | 619.1 | 677.8 | 543.4 | 613.7 | 248.9 | 386.4 | 363 | 268.1 | 302.1 | 448.8 | 292.5
1672.1 | 1433.1 | 471.8 | 188.72 | 220.6028 | 466.9 | 365.6 | 358.1 | 334.6 | 623.4 | 62 | 17.9 | 110.7 | 6.6 | 205.9 | 11.4 | 432.2 | 736.7 | 765.8 | 480.8 | 554.6 | 811.4 | 733.2 | 651.2 | 699.9 | 319.3 | 485 | 711.6 | 140.2 | 232 | 304.7 | 584.9 | 621.2 | 683.4 | 544.7 | 614.7 | 249.4 | 387 | 363.5 | 268.3 | 302.4 | 449.2 | 292.8
1673.1 | 1434.1 | 471.8 | 188.72 | 220.6028 | 466.8 | 365.1 | 358.1 | 335 | 623.7 | 62 | 17.9 | 110.8 | 6.3 | 212.2 | 12.3 | 432.4 | 735.7 | 755 | 481 | 555.1 | 810.5 | 733.5 | 652.5 | 697.4 | 319.4 | 484.9 | 711.4 | 140.4 | 232.3 | 304.9 | 585.5 | 622 | 677 | 545.8 | 614.6 | 249.8 | 388 | 364.6 | 268.6 | 302.7 | 449.7 | 293.1
1674.1 | 1435.1 | 471.6 | 188.64 | 220.5093 | 465.1 | 364.3 | 358.3 | 335.5 | 620.6 | 62.1 | 17.9 | 111 | 5.7 | 219.1 | 11 | 432.5 | 736.1 | 746.6 | 481.1 | 555.6 | 809.7 | 733.6 | 653.2 | 691.8 | 319.6 | 484.9 | 710.2 | 140.7 | 232.6 | 305.1 | 586.3 | 623 | 670.2 | 547.1 | 612.3 | 250.4 | 388.6 | 365.9 | 269 | 303.1 | 450.1 | 293.4
1675.1 | 1436.1 | 471.6 | 188.64 | 220.5093 | 463.4 | 363.9 | 358.6 | 336.8 | 619.4 | 62.2 | 17.9 | 111 | 5.9 | 213 | 11.5 | 432.7 | 731.8 | 740 | 481.4 | 556.1 | 808.6 | 733.8 | 653 | 683.7 | 319.8 | 484.5 | 708.4 | 140.8 | 232.8 | 305.3 | 586.8 | 624.4 | 669.9 | 548.1 | 612.5 | 250.9 | 389.3 | 366.3 | 269.3 | 303.4 | 450.6 | 293.8
1676.1 | 1437.1 | 471.6 | 188.64 | 220.5093 | 464 | 364.2 | 358.9 | 337.5 | 618.4 | 62.2 | 17.9 | 111 | 6.9 | 211.8 | 12.3 | 432.8 | 729.5 | 734.6 | 481.5 | 556.5 | 808.1 | 734.2 | 654.8 | 680.7 | 320 | 484.6 | 707 | 141.1 | 233.1 | 305.5 | 587.2 | 624.2 | 669.3 | 549.1 | 613.3 | 251.6 | 390 | 366.8 | 269.6 | 303.8 | 451.1 | 294.1
1677.1 | 1438.1 | 471.6 | 188.64 | 220.5093 | 464.6 | 366.1 | 358.9 | 337.9 | 618.2 | 62.2 | 17.9 | 111 | 6.9 | 207.7 | 12.3 | 432.9 | 729.2 | 736.1 | 481.6 | 557 | 807.2 | 734.4 | 655.2 | 679.5 | 320.1 | 484.3 | 705.9 | 141.3 | 233.3 | 305.8 | 588.2 | 624.9 | 671.4 | 550.4 | 615.7 | 252.2 | 391 | 367.7 | 269.9 | 304.1 | 451.7 | 294.4
1678.1 | 1439.1 | 473.1 | 189.24 | 221.2107 | 466.4 | 366.8 | 358.9 | 338.6 | 621.2 | 62.2 | 17.9 | 111 | 6.2 | 209.7 | 12.6 | 433 | 725.4 | 748.5 | 481.7 | 557.5 | 806.8 | 734.7 | 654.7 | 685.1 | 320.3 | 484.2 | 706.5 | 141.5 | 233.6 | 306.1 | 589.1 | 627.7 | 677.9 | 551.7 | 620.5 | 252.9 | 392.1 | 368.4 | 270.2 | 304.3 | 452.2 | 294.8
1679.1 | 1440.1 | 473.3 | 189.32 | 221.3042 | 467.3 | 366 | 359.3 | 339.4 | 621.5 | 62.3 | 17.9 | 111 | 6.5 | 213.3 | 13.1 | 433.1 | 724.5 | 755.9 | 481.9 | 558 | 807.3 | 734.8 | 654.4 | 687.1 | 320.5 | 484.3 | 706.3 | 141.7 | 233.8 | 306.3 | 589.4 | 628.9 | 677.7 | 552.6 | 619.4 | 253.6 | 392.5 | 369.3 | 270.4 | 304.6 | 452.8 | 295.2
1680.1 | 1441.1 | 473.2 | 189.28 | 221.2574 | 473.3 | 365.1 | 359.4 | 339.3 | 620.9 | 62.3 | 17.9 | 110.9 | 7 | 206.6 | 14.3 | 433.3 | 722.4 | 755.6 | 482.1 | 558.6 | 808.1 | 735.1 | 654.7 | 691.5 | 320.7 | 484.5 | 707 | 141.9 | 234.1 | 306.6 | 589.6 | 628.8 | 676.2 | 553.3 | 616.5 | 254.3 | 392.6 | 369.9 | 270.6 | 305 | 453.2 | 295.5
1681.1 | 1442.1 | 471.8 | 188.72 | 220.6028 | 476.3 | 364.6 | 359.6 | 339.2 | 620 | 62.4 | 17.9 | 110.9 | 6.9 | 204.6 | 14.2 | 433.4 | 724.6 | 764.9 | 482.3 | 559.1 | 808.2 | 735.1 | 654.4 | 695.5 | 320.9 | 484.3 | 707.8 | 142.1 | 234.4 | 306.8 | 590.9 | 627.7 | 684 | 554.2 | 617.3 | 255 | 393.1 | 370 | 270.8 | 305.2 | 453.7 | 295.9
1682.1 | 1443.1 | 471.4 | 188.56 | 220.4158 | 474.8 | 363.9 | 359.7 | 339.2 | 621.1 | 62.5 | 17.9 | 111 | 5.9 | 205.1 | 14 | 433.5 | 727.7 | 772 | 482.4 | 559.6 | 809.5 | 735.2 | 654.3 | 702.6 | 321 | 484.2 | 708.2 | 142.3 | 234.7 | 307.1 | 591 | 626 | 680.6 | 555.4 | 616.1 | 255.5 | 393.4 | 369.7 | 270.9 | 305.4 | 454.1 | 296.2
1683.1 | 1444.1 | 470.6 | 188.24 | 220.0417 | 474.8 | 363 | 360.1 | 339.1 | 625.7 | 62.5 | 17.9 | 111 | 5.4 | 206.5 | 13.3 | 433.8 | 730.1 | 777 | 482.7 | 560.1 | 811.4 | 735.3 | 654.3 | 707.9 | 321.1 | 484.2 | 709.7 | 142.5 | 235 | 307.4 | 590.9 | 626.3 | 682.4 | 556.1 | 616.6 | 255.9 | 393.1 | 369.5 | 271.1 | 305.5 | 454.5 | 296.5
1684.1 | 1445.1 | 472.8 | 189.12 | 221.0704 | 473.1 | 363.3 | 361 | 338.8 | 627 | 62.6 | 17.9 | 111 | 5.7 | 203.8 | 13.8 | 434 | 730.2 | 775.4 | 482.9 | 560.6 | 812.4 | 735.5 | 652.8 | 708.8 | 321.2 | 484 | 710.9 | 142.7 | 235.2 | 307.8 | 591.5 | 626.2 | 683 | 556.9 | 616.3 | 256.3 | 392.7 | 369.6 | 271.2 | 305.5 | 454.9 | 296.8
1685.1 | 1446.1 | 471 | 188.4 | 220.2287 | 470.3 | 364.1 | 361.1 | 338.7 | 627.2 | 62.7 | 17.9 | 111 | 6.2 | 230.5 | 13.5 | 434.1 | 726.6 | 778.3 | 483.1 | 561.1 | 812.4 | 735.6 | 650.2 | 714 | 321.1 | 483.5 | 712.2 | 142.9 | 235.5 | 308 | 591.6 | 627 | 683.4 | 557.2 | 616.7 | 256.6 | 392.7 | 369.6 | 271.4 | 305.7 | 455.3 | 297.1
1686.1 | 1447.1 | 471.5 | 188.6 | 220.4625 | 469.8 | 364.1 | 360.8 | 338.5 | 626.2 | 62.8 | 17.9 | 111 | 6.7 | 232.9 | 13.2 | 434.2 | 727 | 784.6 | 483.3 | 561.7 | 812.7 | 735.6 | 648.8 | 717.3 | 321.2 | 483.5 | 712.9 | 143.1 | 235.8 | 308.1 | 591.2 | 626.9 | 686.6 | 557.2 | 618.4 | 256.8 | 392.7 | 369.5 | 271.6 | 305.9 | 455.7 | 297.3
1687.1 | 1448.1 | 470.6 | 188.24 | 220.0417 | 471 | 366.1 | 360.6 | 337.8 | 626.2 | 62.8 | 17.9 | 111.1 | 6.5 | 211.3 | 11.8 | 434.5 | 728.9 | 785.1 | 483.5 | 562.3 | 812.3 | 735.5 | 648 | 717.1 | 321.5 | 483.5 | 712.7 | 143.3 | 236 | 308.4 | 591.1 | 626.1 | 690 | 557.4 | 620.1 | 257.1 | 392.6 | 369.5 | 271.8 | 306.1 | 456.1 | 297.6
1688.1 | 1449.1 | 469.6 | 187.84 | 219.5741 | 472.8 | 367.4 | 360.1 | 337.7 | 624.2 | 62.8 | 17.9 | 111 | 5.8 | 208.4 | 11.7 | 434.8 | 731.3 | 782.2 | 483.8 | 562.8 | 811.6 | 735.5 | 646.9 | 715.4 | 321.7 | 483.6 | 712.7 | 143.5 | 236.3 | 308.6 | 590.9 | 625.1 | 691.2 | 557.4 | 619.2 | 257.4 | 392.8 | 369.7 | 272 | 306.3 | 456.6 | 297.9
1689.1 | 1450.1 | 470 | 188 | 219.7612 | 476.7 | 367.1 | 359.9 | 338 | 623.9 | 62.9 | 17.9 | 111 | 5.5 | 218.3 | 9.9 | 435.1 | 732.8 | 777.1 | 484 | 563.3 | 811.5 | 735.5 | 646.4 | 717.2 | 322 | 483.6 | 713.9 | 143.7 | 236.6 | 308.8 | 591.1 | 624.5 | 691.1 | 557.3 | 618.3 | 257.6 | 393 | 369.4 | 272.2 | 306.5 | 457 | 298.2
1690.1 | 1451.1 | 470.8 | 188.32 | 220.1352 | 478.1 | 367.3 | 360.3 | 338.8 | 620.5 | 62.9 | 17.9 | 111 | 6.1 | 224.6 | 9 | 435.3 | 737 | 777.7 | 484.3 | 563.8 | 811.3 | 735.4 | 646.7 | 712.3 | 322.2 | 483.5 | 713.1 | 143.9 | 236.9 | 309 | 592.3 | 622.5 | 688 | 557.9 | 617.9 | 257.9 | 393.1 | 369 | 272.4 | 306.8 | 457.4 | 298.6
1691.1 | 1452.1 | 472 | 188.8 | 220.6963 | 477.1 | 367.2 | 359.8 | 339.3 | 618.5 | 63 | 17.9 | 111 | 6.1 | 238.7 | 7.8 | 435.5 | 739.3 | 768.6 | 484.5 | 564.4 | 810.9 | 735.4 | 647.8 | 711.1 | 322.4 | 483.4 | 713.1 | 144.2 | 237.2 | 309.3 | 593.7 | 621.1 | 692.3 | 558.4 | 618 | 258.2 | 393.2 | 368.8 | 272.6 | 307.1 | 457.8 | 298.9
1692.1 | 1453.1 | 470.5 | 188.2 | 219.995 | 478.5 | 366.6 | 359.8 | 339.5 | 618.8 | 63.1 | 17.9 | 110.9 | 6.2 | 209 | 7.3 | 435.7 | 738.3 | 763.3 | 484.7 | 564.9 | 810.2 | 735.6 | 649.5 | 708.1 | 322.5 | 483.5 | 712.4 | 144.4 | 237.5 | 309.5 | 594.1 | 621.6 | 690.8 | 559 | 618.1 | 258.4 | 393.9 | 369.5 | 272.9 | 307.5 | 458.2 | 299.2
1693.1 | 1454.1 | 471.1 | 188.44 | 220.2755 | 477.1 | 366.5 | 360.2 | 339.3 | 617.3 | 63.2 | 17.9 | 110.9 | 6.2 | 241.7 | 7.1 | 435.7 | 742.9 | 766.6 | 484.9 | 565.4 | 810.8 | 735.8 | 650.1 | 703.4 | 322.7 | 483.5 | 711.9 | 144.6 | 237.8 | 309.7 | 594.5 | 620 | 687.9 | 559.7 | 619.2 | 258.7 | 394.1 | 369.6 | 273.1 | 307.6 | 458.6 | 299.5
1694.1 | 1455.1 | 472.2 | 188.88 | 220.7898 | 475.8 | 366.4 | 360.3 | 339.3 | 614.9 | 63.2 | 17.9 | 111 | 6.8 | 240.5 | 7.8 | 435.9 | 741.6 | 772.5 | 485.1 | 566 | 811.6 | 736 | 650.7 | 705.4 | 322.9 | 483.5 | 711.9 | 144.8 | 238 | 310 | 595.7 | 619.2 | 686.6 | 560.6 | 618.6 | 259 | 394.1 | 369.6 | 273.3 | 307.8 | 459 | 299.8
1695.1 | 1456.1 | 470.1 | 188.04 | 219.8079 | 476.9 | 367.4 | 360.7 | 339.1 | 616 | 63.3 | 17.8 | 111.1 | 6.1 | 220.1 | 8.1 | 436.1 | 739.8 | 777.1 | 485.3 | 566.5 | 812.1 | 736.3 | 651.9 | 705.8 | 323.1 | 483.5 | 712.3 | 145 | 238.3 | 310.3 | 595.7 | 619.3 | 686.9 | 560.9 | 620.2 | 259.4 | 394.3 | 369.6 | 273.5 | 307.9 | 459.4 | 300.1
1696.1 | 1457.1 | 472.6 | 189.04 | 220.9769 | 476.6 | 368.9 | 361.2 | 338.6 | 618.1 | 63.4 | 17.8 | 111.2 | 6.2 | 231.3 | 7.7 | 436.4 | 735.5 | 781 | 485.6 | 567 | 812.5 | 736.5 | 650.5 | 707.4 | 323.2 | 483.3 | 712.2 | 145.2 | 238.6 | 310.5 | 595.3 | 618.5 | 688.5 | 561.2 | 619.2 | 259.6 | 394.8 | 369.4 | 273.6 | 308 | 459.9 | 300.4
1697.1 | 1458.1 | 472 | 188.8 | 220.6963 | 481 | 371.3 | 361.6 | 338.6 | 621.1 | 63.5 | 17.8 | 111.2 | 6.6 | 240.8 | 9.4 | 436.6 | 734.7 | 778 | 485.8 | 567.5 | 813 | 736.6 | 651.5 | 704.7 | 323.4 | 483.3 | 712.2 | 145.4 | 238.8 | 310.7 | 595.7 | 621 | 695 | 561.3 | 620.2 | 259.9 | 394.8 | 369.5 | 273.8 | 308.3 | 460.2 | 300.7
1698.1 | 1459.1 | 471.5 | 188.6 | 220.4625 | 484.1 | 373.9 | 361.4 | 339.2 | 620.4 | 63.6 | 17.8 | 111.3 | 7 | 242.8 | 12.4 | 436.8 | 733.1 | 776.5 | 486.1 | 568 | 812.8 | 736.8 | 652.2 | 704.7 | 323.5 | 483.4 | 712.6 | 145.6 | 239.1 | 311 | 596.6 | 620 | 695 | 561.8 | 621.8 | 260.1 | 394.8 | 369.7 | 274.1 | 308.5 | 460.6 | 301
1699.1 | 1460.1 | 472.1 | 188.84 | 220.7431 | 485.1 | 374.6 | 361 | 339.6 | 620 | 63.7 | 17.8 | 111.4 | 8.4 | 242.1 | 12.6 | 437.1 | 730.6 | 772.5 | 486.3 | 568.5 | 812.1 | 737.1 | 652.8 | 706.6 | 323.7 | 483.4 | 712.7 | 145.9 | 239.3 | 311.2 | 596.9 | 620.1 | 694.9 | 562.2 | 622.5 | 260.3 | 394.6 | 370.5 | 274.2 | 308.9 | 461.1 | 301.3
1700.1 | 1461.1 | 472.6 | 189.04 | 220.9769 | 482.5 | 373.9 | 361.3 | 340.4 | 621.9 | 63.8 | 17.8 | 111.6 | 7.4 | 260.2 | 13 | 437.2 | 729.4 | 764.7 | 486.5 | 569.1 | 812.4 | 737.2 | 654.4 | 708.7 | 323.8 | 483.4 | 711.5 | 146.1 | 239.6 | 311.4 | 597.9 | 622.4 | 695.4 | 562.9 | 623.5 | 260.6 | 394.6 | 371.2 | 274.4 | 309.3 | 461.5 | 301.6
1701.1 | 1462.1 | 472.7 | 189.08 | 221.0236 | 481.3 | 373.1 | 361.8 | 340.7 | 625 | 63.8 | 17.8 | 111.8 | 7.2 | 241.8 | 13.6 | 437.2 | 726.7 | 765.8 | 486.6 | 569.6 | 813.1 | 737.2 | 655.6 | 713.5 | 323.9 | 483.3 | 712.2 | 146.3 | 239.8 | 311.8 | 598.3 | 623.5 | 701.3 | 563.7 | 626 | 260.9 | 394.8 | 370.8 | 274.6 | 309.3 | 461.9 | 302
1702.1 | 1463.1 | 472.1 | 188.84 | 220.7431 | 481.7 | 371.9 | 361.7 | 340.3 | 624.6 | 63.8 | 17.8 | 111.9 | 6.3 | 244 | 15.3 | 437.6 | 728.8 | 768.7 | 487 | 570.1 | 813.7 | 737.2 | 654.7 | 712.5 | 324 | 483.2 | 712.7 | 146.5 | 240 | 312 | 598.3 | 621.8 | 696.2 | 564.3 | 624.9 | 261.1 | 394.5 | 370.4 | 274.7 | 309.5 | 462.4 | 302.3
1703.1 | 1464.1 | 471.6 | 188.64 | 220.5093 | 482 | 371.9 | 361.7 | 339.7 | 624.8 | 63.7 | 17.8 | 112.1 | 5.2 | 241.6 | 15.5 | 437.8 | 732.3 | 771.9 | 487.3 | 570.7 | 814.4 | 737.2 | 654.4 | 713.8 | 324.2 | 482.9 | 713.5 | 146.7 | 240.3 | 312.1 | 598.5 | 622.5 | 693.8 | 564.7 | 623 | 261.3 | 394.3 | 370.2 | 274.9 | 309.6 | 462.7 | 302.5
1704.1 | 1465.1 | 472.4 | 188.96 | 220.8834 | 480.3 | 371.9 | 361.9 | 339.9 | 625.5 | 63.8 | 17.8 | 112.2 | 5.3 | 237.2 | 16.1 | 438 | 733 | 773 | 487.6 | 571.2 | 814.1 | 737.3 | 654.9 | 716.2 | 324.2 | 482.8 | 714.5 | 146.9 | 240.5 | 312.4 | 599.2 | 623.4 | 694.7 | 565.2 | 623.7 | 261.6 | 394.3 | 370.5 | 275.1 | 309.9 | 463.2 | 302.8
1705.1 | 1466.1 | 472.6 | 189.04 | 220.9769 | 478 | 372.2 | 362 | 340.3 | 626.4 | 63.9 | 17.8 | 112.3 | 6.5 | 241.3 | 14.8 | 438.3 | 733.2 | 760.9 | 487.8 | 571.8 | 814.2 | 737.3 | 654.5 | 715.1 | 324.3 | 482.9 | 714.8 | 147.1 | 240.7 | 312.6 | 599.4 | 624.5 | 693.1 | 565.8 | 623 | 261.8 | 394.6 | 370.3 | 275.3 | 310 | 463.7 | 303.1
1706.1 | 1467.1 | 472.7 | 189.08 | 221.0236 | 476.2 | 371.8 | 362 | 340.3 | 629 | 64 | 17.8 | 112.4 | 7.7 | 240.2 | 12.7 | 438.6 | 733.6 | 755.3 | 488.1 | 572.4 | 815.5 | 737.2 | 653.1 | 709.3 | 324.5 | 483 | 714.8 | 147.3 | 241 | 313 | 599.1 | 628.2 | 691 | 566 | 621.2 | 262 | 394.7 | 369.4 | 275.4 | 310.2 | 464.2 | 303.4
1707.1 | 1468.1 | 472.9 | 189.16 | 221.1171 | 478.5 | 371 | 362.3 | 340.2 | 638.3 | 64 | 17.8 | 112.5 | 6.9 | 258.7 | 11.2 | 438.7 | 735 | 748.4 | 488.3 | 572.9 | 815.3 | 737.4 | 653.7 | 703 | 324.7 | 482.9 | 713.8 | 147.5 | 241.2 | 313.2 | 599.7 | 632.1 | 681 | 566.6 | 618.8 | 262.2 | 394.9 | 370.2 | 275.7 | 310.6 | 464.7 | 303.7
1708.1 | 1469.1 | 472.2 | 188.88 | 220.7898 | 477.5 | 370.3 | 362.6 | 340.5 | 634 | 64.1 | 17.8 | 112.6 | 7.5 | 238.4 | 11.6 | 439.3 | 736.4 | 747.3 | 488.6 | 573.4 | 813 | 737.3 | 655.3 | 699.4 | 324.8 | 482.7 | 711.9 | 147.8 | 241.5 | 313.4 | 601.6 | 631.2 | 682 | 567.8 | 620.9 | 262.4 | 395.4 | 371.3 | 276 | 311 | 465.4 | 304
1709.1 | 1470.1 | 472.5 | 189 | 220.9301 | 478.6 | 369.8 | 362.9 | 341.5 | 634.9 | 64.1 | 17.8 | 112.8 | 9 | 250 | 13.6 | 439.4 | 737 | 753 | 488.9 | 574 | 812.5 | 737.3 | 655.9 | 695.5 | 324.9 | 482.5 | 710.9 | 148 | 241.7 | 313.7 | 602.3 | 633.3 | 687.5 | 568.6 | 623.4 | 262.7 | 396.1 | 372 | 276.3 | 311.2 | 465.9 | 304.3
1710.1 | 1471.1 | 470.9 | 188.36 | 220.182 | 478.2 | 370.4 | 363.5 | 342.7 | 640.1 | 64.1 | 17.8 | 112.9 | 8.3 | 240.3 | 14.9 | 439.8 | 735.6 | 758.6 | 489.2 | 574.5 | 812.9 | 737.5 | 657.4 | 696.2 | 324.9 | 482.1 | 710 | 148.2 | 242 | 313.8 | 602.4 | 633.1 | 699.2 | 569 | 627.4 | 263 | 396.5 | 372.4 | 276.5 | 311.5 | 466.4 | 304.6
1711.1 | 1472.1 | 468 | 187.2 | 218.826 | 479.7 | 371.3 | 364.2 | 343 | 644.8 | 64.1 | 17.8 | 113 | 8.8 | 243.9 | 14.9 | 440 | 735.4 | 763.4 | 489.4 | 575 | 813.2 | 737.5 | 656.4 | 696 | 325 | 482.2 | 709.8 | 148.4 | 242.2 | 314.2 | 602.9 | 632.8 | 701.6 | 569.5 | 628.4 | 263.3 | 396.8 | 372.6 | 276.6 | 311.6 | 466.8 | 304.9
1712.1 | 1473.1 | 471.5 | 188.6 | 220.4625 | 480.8 | 371.1 | 363.7 | 342.9 | 643.7 | 64.1 | 17.8 | 113.1 | 7.8 | 242.6 | 14.9 | 440.2 | 735.8 | 760.8 | 489.7 | 575.6 | 813.1 | 737.5 | 655.7 | 694.5 | 325.1 | 481.9 | 709.6 | 148.6 | 242.5 | 314.4 | 604.2 | 634 | 701.6 | 570.6 | 627.7 | 263.7 | 397 | 372.5 | 276.9 | 311.8 | 467.3 | 305.2
1713.1 | 1474.1 | 473.7 | 189.48 | 221.4912 | 482.3 | 370.9 | 362.9 | 342.7 | 643.4 | 64.1 | 17.8 | 113.2 | 7.3 | 247.4 | 13.8 | 440.4 | 735.9 | 750.9 | 490 | 576.1 | 813.1 | 737.5 | 656.6 | 695.7 | 325.2 | 481.4 | 710.3 | 148.8 | 242.7 | 314.5 | 605.3 | 634.4 | 697.7 | 572.1 | 627.4 | 264 | 397.3 | 372.4 | 277.1 | 312 | 467.6 | 305.5
1714.1 | 1475.1 | 475.1 | 190.04 | 222.1458 | 481 | 371.8 | 362.7 | 342.6 | 639.1 | 64.1 | 17.8 | 113.3 | 7.1 | 237.4 | 13.9 | 440.6 | 733.9 | 749.7 | 490.2 | 576.6 | 813.2 | 737.5 | 656.7 | 699.7 | 325.3 | 481.1 | 711 | 149 | 243 | 314.8 | 605.4 | 632.4 | 697.2 | 572.9 | 626.9 | 264.3 | 397.9 | 372.7 | 277.3 | 312.1 | 468 | 305.8
1715.1 | 1476.1 | 495.8 | 198.32 | 231.8247 | 482.1 | 372.5 | 362.8 | 342.6 | 635.3 | 64.1 | 17.8 | 113.2 | 8 | 239.7 | 12.6 | 440.5 | 730.8 | 747.9 | 490.3 | 577.2 | 814.5 | 737.4 | 656.5 | 702.1 | 325.4 | 481.2 | 711.2 | 149.2 | 243.2 | 315 | 605.5 | 631.5 | 698.8 | 573.6 | 626.8 | 264.6 | 398.1 | 372.9 | 277.5 | 312.2 | 468.4 | 306.1
1716.1 | 1477.1 | 514.1 | 205.64 | 240.3813 | 483.6 | 372.8 | 363 | 343.1 | 631.8 | 64.2 | 17.8 | 113.2 | 9.2 | 232.4 | 11.9 | 440.5 | 728.8 | 745.3 | 490.4 | 577.8 | 815.6 | 737.5 | 655.6 | 705.3 | 325.6 | 481 | 712.6 | 149.4 | 243.5 | 315.2 | 605.4 | 630.3 | 700.7 | 573.8 | 625.2 | 264.9 | 398.3 | 373.1 | 277.7 | 312.3 | 468.8 | 306.5
1717.1 | 1478.1 | 525.8 | 210.32 | 245.852 | 485.1 | 372.5 | 362.9 | 343.1 | 630.2 | 64.2 | 17.8 | 113.2 | 9.3 | 243.7 | 10.9 | 440.7 | 727.5 | 745.6 | 490.7 | 578.3 | 816.5 | 737.7 | 653.5 | 710.7 | 325.7 | 480.6 | 714.4 | 149.6 | 243.8 | 315.4 | 605.7 | 628.7 | 699.5 | 574.2 | 626 | 265.1 | 398.3 | 373.7 | 278 | 312.6 | 469.2 | 306.7
1718.1 | 1479.1 | 532.2 | 212.88 | 248.8445 | 484.8 | 371.6 | 363.1 | 343.5 | 626.9 | 64.2 | 17.8 | 113.2 | 7.6 | 246.6 | 13.3 | 441 | 728 | 753.1 | 490.9 | 578.9 | 817 | 737.9 | 653.1 | 712.9 | 325.8 | 480.6 | 714.3 | 149.9 | 244 | 315.8 | 606.9 | 628.5 | 697.8 | 575 | 627.1 | 265.4 | 398.5 | 374.2 | 278.2 | 312.9 | 469.6 | 307
1719.1 | 1480.1 | 536.2 | 214.48 | 250.7148 | 482.3 | 371 | 363.3 | 343.9 | 626.7 | 64.3 | 17.8 | 113 | 7.9 | 237.2 | 13.3 | 440.9 | 731.9 | 762.6 | 491 | 579.4 | 817.4 | 737.8 | 652.5 | 717.9 | 325.9 | 480.7 | 714.8 | 150.1 | 244.3 | 316.2 | 606.5 | 628.2 | 697.6 | 575.3 | 627.8 | 265.7 | 398.5 | 373.9 | 278.4 | 313 | 470 | 307.3
1720.1 | 1481.1 | 538.7 | 215.48 | 251.8837 | 481.7 | 371 | 364 | 343.8 | 630.6 | 64.3 | 17.8 | 113 | 8.3 | 250.5 | 14.3 | 441 | 729.6 | 767.5 | 491.1 | 580 | 817.2 | 737.8 | 653.5 | 720.1 | 325.9 | 480.7 | 715.1 | 150.3 | 244.6 | 316.7 | 606.1 | 630.3 | 696.3 | 575.6 | 629 | 266 | 398.5 | 373.7 | 278.6 | 313.1 | 470.4 | 307.6
1721.1 | 1482.1 | 543.3 | 217.32 | 254.0346 | 484 | 371.7 | 364.6 | 343.7 | 635.6 | 64.3 | 17.8 | 113.1 | 7.6 | 236 | 12.9 | 441.1 | 725.9 | 770.2 | 491.3 | 580.5 | 817.3 | 737.8 | 654.7 | 724.1 | 326.1 | 480.9 | 715.5 | 150.5 | 244.8 | 317.2 | 606.1 | 630.6 | 696.4 | 576 | 629.3 | 266.2 | 398.3 | 373.9 | 278.8 | 313.2 | 470.8 | 307.9
1722.1 | 1483.1 | 545.3 | 218.12 | 254.9697 | 484.9 | 371.8 | 364.7 | 343.6 | 637.9 | 64.3 | 17.8 | 113.2 | 7.7 | 242 | 12.7 | 441.5 | 724.2 | 770.2 | 491.5 | 581 | 818 | 737.9 | 654.9 | 729.2 | 326.3 | 480.9 | 717.5 | 150.7 | 245.1 | 317.3 | 606.6 | 630.9 | 695.8 | 576.5 | 629.3 | 266.4 | 398.3 | 374.2 | 279.1 | 313.4 | 471.2 | 308.1
1723.1 | 1484.1 | 545.9 | 218.36 | 255.2503 | 486.1 | 372.7 | 364.8 | 343.8 | 634 | 64.3 | 17.8 | 113.4 | 7.7 | 257.5 | 11.9 | 441.9 | 724.7 | 767.1 | 491.9 | 581.6 | 818.8 | 738 | 654.7 | 731.3 | 326.5 | 480.8 | 718.5 | 150.9 | 245.4 | 317.3 | 606.4 | 629.8 | 689.5 | 576.2 | 627.4 | 266.6 | 398.4 | 374.8 | 279.3 | 313.6 | 471.6 | 308.4
1724.1 | 1485.1 | 545.4 | 218.16 | 255.0165 | 487.9 | 376.8 | 364.9 | 344.3 | 625.8 | 64.3 | 17.8 | 113.5 | 7.2 | 246.7 | 11.5 | 442.3 | 727.8 | 764.6 | 492.2 | 582.1 | 818.6 | 737.9 | 655 | 723 | 326.6 | 480.8 | 718.2 | 151.1 | 245.7 | 317.5 | 605.7 | 627.4 | 681.9 | 575.5 | 624.3 | 266.8 | 398.6 | 375.1 | 279.6 | 314 | 472 | 308.7
1725.1 | 1486.1 | 545.7 | 218.28 | 255.1567 | 493 | 377.8 | 365.3 | 344.9 | 621.1 | 64.3 | 17.8 | 113.7 | 6.6 | 261.3 | 13.7 | 442.4 | 731.5 | 762.4 | 492.4 | 582.6 | 819 | 737.8 | 655.5 | 720.1 | 326.8 | 481 | 718 | 151.3 | 246 | 317.7 | 605.6 | 626.2 | 679.7 | 574.9 | 623.3 | 267.1 | 399 | 375.4 | 279.9 | 314.2 | 472.3 | 309
1726.1 | 1487.1 | 546.4 | 218.56 | 255.484 | 495.8 | 378.2 | 365.6 | 345.5 | 618.5 | 64.4 | 17.8 | 114 | 6.7 | 273.5 | 13 | 442.6 | 730.9 | 752.4 | 492.6 | 583.1 | 819.1 | 737.7 | 655.2 | 711.9 | 326.8 | 481.1 | 717.4 | 151.5 | 246.3 | 317.9 | 605 | 626.9 | 671.8 | 573.8 | 625 | 267.3 | 399.8 | 376.2 | 280.3 | 314.5 | 472.8 | 309.3
1727.1 | 1488.1 | 546.4 | 218.56 | 255.484 | 498.1 | 378.1 | 365.6 | 346.2 | 618.2 | 64.4 | 17.8 | 114.4 | 6 | 248.4 | 13.1 | 442.6 | 733.2 | 745.7 | 492.8 | 583.7 | 819.9 | 737.8 | 654.4 | 707.1 | 326.9 | 481.1 | 716.6 | 151.7 | 246.5 | 318.2 | 605.3 | 625.4 | 665.8 | 573.3 | 622.5 | 267.6 | 400.5 | 376.7 | 280.6 | 314.8 | 473.3 | 309.6
1728.1 | 1489.1 | 547.4 | 218.96 | 255.9516 | 500.6 | 377 | 366.1 | 347.2 | 618.4 | 64.4 | 17.8 | 114.5 | 5.9 | 253.2 | 13.7 | 442.9 | 730.1 | 736 | 493.1 | 584.2 | 820.2 | 737.9 | 653.9 | 703.4 | 327 | 481.2 | 716.3 | 152 | 246.7 | 318.4 | 606.1 | 623.8 | 658.4 | 573.1 | 621.2 | 267.9 | 401.4 | 377.7 | 281 | 315.2 | 473.7 | 310
1729.1 | 1490.1 | 547.8 | 219.12 | 256.1387 | 502.2 | 376.9 | 367 | 348.1 | 618.2 | 64.3 | 17.8 | 114.6 | 5.5 | 250.2 | 14.3 | 442.9 | 731.9 | 730.6 | 493.2 | 584.7 | 820.2 | 737.9 | 652 | 694 | 327.1 | 481.1 | 715.1 | 152.2 | 247 | 318.6 | 606.6 | 625.7 | 654.8 | 573.2 | 618.7 | 268.3 | 401.9 | 378.7 | 281.3 | 315.7 | 474.1 | 310.3
1730.1 | 1491.1 | 547.4 | 218.96 | 255.9516 | 505.8 | 376.6 | 367.7 | 348.7 | 619.4 | 64.3 | 17.8 | 114.9 | 5.6 | 249.3 | 16.2 | 442.8 | 735.4 | 735 | 493.3 | 585.2 | 821.5 | 737.8 | 651.9 | 695.6 | 327.2 | 481.1 | 715 | 152.4 | 247.2 | 318.8 | 606.9 | 625 | 652.9 | 573.8 | 618.9 | 268.7 | 402.2 | 379.1 | 281.6 | 316 | 474.4 | 310.7
1731.1 | 1492.1 | 548.4 | 219.36 | 256.4192 | 505.1 | 376.1 | 368.7 | 348.6 | 617 | 64.3 | 17.8 | 115.2 | 6.8 | 242.9 | 15.5 | 442.8 | 735.1 | 746 | 493.4 | 585.7 | 821.9 | 737.8 | 654.4 | 699.5 | 327.3 | 481 | 715.6 | 152.6 | 247.4 | 319.1 | 607.1 | 624.1 | 644.6 | 574.2 | 617.1 | 269.1 | 402.4 | 379.3 | 281.9 | 316.2 | 474.8 | 311
1732.1 | 1493.1 | 548.8 | 219.52 | 256.6062 | 505 | 376.4 | 369.4 | 348.8 | 616.8 | 64.3 | 17.7 | 115.4 | 7.9 | 234.4 | 13.8 | 443 | 736.6 | 749.1 | 493.6 | 586.2 | 821.5 | 738 | 655.7 | 705.6 | 327.4 | 481 | 716.7 | 152.8 | 247.7 | 319.4 | 607.9 | 623.4 | 641.6 | 574.7 | 616.8 | 269.6 | 402.7 | 379.4 | 282.3 | 316.4 | 475.2 | 311.3
1733.1 | 1494.1 | 549.9 | 219.96 | 257.1206 | 503.3 | 376.8 | 370.1 | 348.6 | 616.8 | 64.3 | 17.7 | 115.6 | 7.4 | 246.8 | 12.8 | 443.2 | 740.5 | 750.9 | 493.8 | 586.7 | 820.2 | 738.2 | 656.8 | 707.5 | 327.5 | 480.9 | 717.1 | 153.1 | 247.9 | 319.6 | 608.8 | 623.4 | 638.9 | 575.1 | 617.8 | 270 | 403.4 | 380.1 | 282.8 | 316.9 | 475.6 | 311.6
1734.1 | 1495.1 | 551.9 | 220.76 | 258.0557 | 505.8 | 376.2 | 370.1 | 348.9 | 617.7 | 64.3 | 17.7 | 115.9 | 7.5 | 252.4 | 11.9 | 443.5 | 742 | 753.8 | 494.1 | 587.2 | 819.6 | 738.2 | 658 | 705.4 | 327.6 | 480.8 | 717.5 | 153.3 | 248.2 | 319.8 | 609.5 | 623.3 | 650.9 | 575.7 | 618.8 | 270.5 | 404 | 381.5 | 283.2 | 317.3 | 476 | 311.9
1735.1 | 1496.1 | 553 | 221.2 | 258.5701 | 505.1 | 375.5 | 370.3 | 349.3 | 622.9 | 64.4 | 17.7 | 116.1 | 6.8 | 246.5 | 11.7 | 443.5 | 739.2 | 761.6 | 494.3 | 587.7 | 820.1 | 738.3 | 659 | 713.8 | 327.8 | 480.7 | 718 | 153.5 | 248.4 | 320.1 | 610.2 | 624.5 | 667.4 | 576.5 | 620.5 | 271 | 404.4 | 382.3 | 283.6 | 317.7 | 476.4 | 312.2
1736.1 | 1497.1 | 554.3 | 221.72 | 259.1779 | 504.4 | 375.5 | 370.5 | 349.4 | 625.3 | 64.4 | 17.7 | 116.3 | 6.5 | 260.2 | 11.8 | 443.5 | 736.3 | 767.1 | 494.4 | 588.2 | 821.2 | 738.2 | 661.5 | 718 | 328 | 480.7 | 719.2 | 153.7 | 248.7 | 320.4 | 611.4 | 625 | 672.2 | 577.7 | 621.7 | 271.5 | 404.6 | 382.4 | 283.9 | 317.9 | 476.7 | 312.6
1737.1 | 1498.1 | 554.2 | 221.68 | 259.1311 | 503.5 | 376 | 370.6 | 349.5 | 624.8 | 64.4 | 17.7 | 116.3 | 7.1 | 258.5 | 12.2 | 443.6 | 733.8 | 766.2 | 494.6 | 588.8 | 821.9 | 738.2 | 660.7 | 725.8 | 328.1 | 480.5 | 720.7 | 154 | 249 | 320.6 | 611.3 | 623.5 | 676.8 | 578.3 | 622.6 | 271.9 | 404.7 | 382.5 | 284.2 | 318.1 | 477.1 | 312.9
1738.1 | 1499.1 | 553.8 | 221.52 | 258.9441 | 503 | 376.2 | 371.1 | 349.5 | 623.2 | 64.4 | 17.7 | 116.4 | 6.7 | 254.1 | 13.5 | 443.7 | 735.1 | 768.4 | 494.8 | 589.3 | 822.3 | 738.2 | 660.3 | 727.1 | 328.2 | 480.3 | 722.1 | 154.2 | 249.2 | 320.9 | 611.2 | 623.2 | 672.9 | 578.7 | 622.5 | 272.3 | 405 | 382.6 | 284.5 | 318.5 | 477.5 | 313.2
1739.1 | 1500.1 | 554 | 221.6 | 259.0376 | 503.6 | 376.8 | 371.3 | 349.5 | 622.4 | 64.5 | 17.7 | 116.5 | 6.7 | 264.3 | 12.1 | 443.6 | 734.4 | 767.9 | 494.9 | 589.9 | 823.1 | 738.2 | 659.9 | 731.8 | 328.4 | 480.3 | 722.5 | 154.4 | 249.5 | 321.1 | 611.7 | 623 | 677 | 579.4 | 624.3 | 272.8 | 405.5 | 382.6 | 284.8 | 318.6 | 477.9 | 313.5
1740.1 | 1501.1 | 555.4 | 222.16 | 259.6922 | 505.4 | 376.8 | 371.7 | 349.7 | 619.5 | 64.6 | 17.7 | 116.7 | 8 | 263.4 | 10.2 | 443.7 | 735.7 | 769 | 495 | 590.5 | 823.6 | 738.2 | 660 | 731.7 | 328.6 | 480.1 | 722.7 | 154.6 | 249.8 | 321.3 | 612.4 | 621.6 | 672.5 | 580.2 | 623.5 | 273.2 | 406.2 | 383.1 | 285.2 | 318.9 | 478.3 | 313.8
1741.1 | 1502.1 | 557.1 | 222.84 | 260.4871 | 507.3 | 376.6 | 371.9 | 349.8 | 621.1 | 64.7 | 17.7 | 116.8 | 7.3 | 260.9 | 8.9 | 443.8 | 735.3 | 773.2 | 495.3 | 591.1 | 824.7 | 738.2 | 660.3 | 740.4 | 328.7 | 479.9 | 724.4 | 154.8 | 250.1 | 321.7 | 612.3 | 622.7 | 679.4 | 580.5 | 625 | 273.6 | 406.4 | 383.1 | 285.4 | 319.2 | 478.7 | 314.1
1742.1 | 1503.1 | 557.5 | 223 | 260.6742 | 509.8 | 376.7 | 371.6 | 349.8 | 622.7 | 64.7 | 17.7 | 116.9 | 7.4 | 244.1 | 9.3 | 444 | 734.5 | 774.4 | 495.5 | 591.7 | 825.9 | 738.4 | 659.7 | 744.2 | 328.9 | 479.8 | 726.6 | 155.1 | 250.4 | 322.1 | 611.7 | 622.8 | 677.6 | 580.7 | 625.6 | 274 | 406.4 | 382.9 | 285.7 | 319.3 | 479.2 | 314.4
1743.1 | 1504.1 | 557.9 | 223.16 | 260.8612 | 513.9 | 378.7 | 371.8 | 349.3 | 621.5 | 64.7 | 17.7 | 117 | 7.4 | 254.3 | 10 | 444 | 735.9 | 773.1 | 495.7 | 592.2 | 826.5 | 738.4 | 659.4 | 747.1 | 329 | 479.7 | 727.6 | 155.3 | 250.7 | 322.5 | 611.9 | 621.5 | 678.7 | 581 | 626.4 | 274.4 | 406.4 | 383 | 285.9 | 319.5 | 479.5 | 314.7
1744.1 | 1505.1 | 559.2 | 223.68 | 261.469 | 515.7 | 379.2 | 372.3 | 349 | 621.2 | 64.7 | 17.7 | 117 | 6.8 | 252.7 | 11.6 | 444.2 | 736.7 | 766.3 | 496 | 592.8 | 827 | 738.6 | 660.4 | 747 | 329.1 | 479.7 | 728.1 | 155.5 | 251 | 323 | 612.5 | 619.1 | 681 | 581.7 | 624.7 | 274.7 | 406.2 | 383.1 | 286.1 | 319.7 | 479.9 | 315
1745.1 | 1506.1 | 559.9 | 223.96 | 261.7963 | 520.7 | 379 | 373.5 | 349.5 | 625.8 | 64.7 | 17.7 | 117.1 | 7.1 | 252.7 | 11.6 | 444.7 | 741.6 | 765.4 | 496.4 | 593.3 | 827.2 | 738.6 | 659.8 | 742.1 | 329.2 | 479.7 | 729.3 | 155.7 | 251.3 | 323.8 | 613.2 | 620.1 | 679 | 582.4 | 622.6 | 275 | 406.6 | 382.8 | 286.4 | 319.7 | 480.2 | 315.3
1746.1 | 1507.1 | 561.7 | 224.68 | 262.638 | 522.9 | 378.7 | 374.7 | 349.7 | 630.5 | 64.7 | 17.7 | 117.1 | 6.7 | 247.3 | 9.9 | 444.8 | 742 | 760.5 | 496.7 | 593.8 | 826.2 | 738.4 | 662.9 | 732.2 | 329.3 | 479.7 | 729.7 | 156 | 251.5 | 324.5 | 613.7 | 621.4 | 684.6 | 583.1 | 622.4 | 275.2 | 406.7 | 382.6 | 286.6 | 319.8 | 480.5 | 315.6
1747.1 | 1508.1 | 561.1 | 224.44 | 262.3574 | 524.4 | 378.2 | 375.5 | 349.8 | 636.2 | 64.8 | 17.7 | 117.2 | 7.2 | 255.7 | 10.7 | 445 | 746.6 | 766.1 | 496.9 | 594.3 | 825.7 | 738.4 | 665.8 | 728.7 | 329.4 | 479.3 | 729.2 | 156.2 | 251.8 | 324.9 | 613.9 | 623.5 | 682.6 | 583.9 | 622.3 | 275.4 | 407.1 | 382 | 286.9 | 319.9 | 480.9 | 315.9
1748.1 | 1509.1 | 560.5 | 224.2 | 262.0769 | 526.8 | 378 | 376.4 | 350.3 | 641.4 | 64.9 | 17.7 | 117.2 | 6.9 | 259.9 | 11.5 | 444.9 | 746.9 | 767.6 | 497.1 | 594.8 | 825.2 | 738.3 | 668.6 | 732.6 | 329.6 | 478.7 | 730 | 156.4 | 252.1 | 325.2 | 613.9 | 625.5 | 683.7 | 584.3 | 623.2 | 275.5 | 407.7 | 381.8 | 287.3 | 320.1 | 481.4 | 316.2
1749.1 | 1510.1 | 559.7 | 223.88 | 261.7028 | 545.2 | 379.5 | 377.3 | 350.5 | 644.4 | 65 | 17.7 | 117.2 | 7.2 | 259.8 | 11.8 | 445 | 747.1 | 769.7 | 497.3 | 595.4 | 824.9 | 738.2 | 668.8 | 734.8 | 329.7 | 478.7 | 730.7 | 156.6 | 252.4 | 325.8 | 613.8 | 626.1 | 686.7 | 584.5 | 624.6 | 275.7 | 408.3 | 382.1 | 287.6 | 320.3 | 481.8 | 316.6
1750.1 | 1511.1 | 560.9 | 224.36 | 262.2639 | 546.1 | 380.5 | 378.1 | 351 | 647.5 | 65 | 17.7 | 117.3 | 6.9 | 237.3 | 11 | 445.3 | 744.1 | 769.6 | 497.6 | 595.9 | 824.3 | 738.4 | 669.7 | 727.9 | 329.8 | 478.9 | 729 | 156.9 | 252.8 | 326.5 | 614.2 | 628.5 | 694 | 584.7 | 626.9 | 275.8 | 408.5 | 382.2 | 287.8 | 320.5 | 482.3 | 316.9
1751.1 | 1512.1 | 561.5 | 224.6 | 262.5445 | 540.2 | 381 | 379.3 | 351.4 | 649.7 | 65 | 17.7 | 117.5 | 6.6 | 241.7 | 10.2 | 445.3 | 741.1 | 766.7 | 497.9 | 596.4 | 823.1 | 738.5 | 671.3 | 724.2 | 329.9 | 478.8 | 727.3 | 157.1 | 253 | 327 | 614.8 | 629 | 697 | 585.7 | 627.5 | 275.9 | 408.8 | 382.2 | 288.1 | 320.5 | 482.7 | 317.2
1752.1 | 1513.1 | 561.2 | 224.48 | 262.4042 | 533.1 | 381.3 | 380.8 | 352 | 652.9 | 65.1 | 17.7 | 117.7 | 6 | 244.3 | 9.9 | 445.4 | 741.9 | 767.1 | 498.1 | 596.9 | 821.8 | 738.6 | 672.4 | 723 | 330.1 | 478.8 | 726.7 | 157.3 | 253.4 | 327.4 | 615.5 | 631.2 | 699.6 | 586.7 | 628.2 | 275.9 | 409.2 | 382 | 288.4 | 320.7 | 483.1 | 317.6
1753.1 | 1514.1 | 562 | 224.8 | 262.7782 | 529.4 | 381.5 | 381.3 | 352.6 | 649.4 | 65.1 | 17.7 | 117.7 | 6.6 | 245.8 | 9.8 | 445.4 | 740.9 | 776.4 | 498.4 | 597.5 | 821 | 738.6 | 671.9 | 727.6 | 330.2 | 478.8 | 728.1 | 157.6 | 253.7 | 327.2 | 615.5 | 629.7 | 698.8 | 587 | 627.7 | 276 | 409.4 | 382.1 | 288.7 | 321 | 483.5 | 317.9
1754.1 | 1515.1 | 561.4 | 224.56 | 262.4977 | 530.3 | 381.9 | 380.8 | 353 | 645.7 | 65.1 | 17.7 | 117.7 | 8.1 | 239.4 | 10.8 | 445.7 | 740 | 779.2 | 498.7 | 598 | 820.3 | 738.6 | 671.5 | 727.8 | 330.3 | 479 | 728.7 | 157.8 | 254 | 327.3 | 615.5 | 631.7 | 695.6 | 586.9 | 627.4 | 276.2 | 409.9 | 382.6 | 289.1 | 321.3 | 483.9 | 318.2
1755.1 | 1516.1 | 563.1 | 225.24 | 263.2926 | 525.6 | 383.3 | 380.1 | 353.3 | 643.6 | 65 | 17.7 | 117.8 | 6.8 | 244.4 | 13 | 445.9 | 738.6 | 779.1 | 499 | 598.6 | 819.9 | 738.8 | 672.2 | 731.6 | 330.4 | 479.1 | 729.2 | 158.1 | 254.4 | 327.7 | 615.3 | 632.8 | 698.4 | 586.6 | 628.3 | 276.3 | 410.5 | 383.5 | 289.5 | 321.7 | 484.3 | 318.5
1756.1 | 1517.1 | 562 | 224.8 | 262.7782 | 521.3 | 383.5 | 379.6 | 353.7 | 639.5 | 65.1 | 17.7 | 118 | 6 | 242.4 | 14 | 446 | 739.1 | 783.6 | 499.3 | 599.2 | 819.8 | 738.9 | 672.2 | 734.2 | 330.5 | 478.8 | 729.8 | 158.3 | 254.7 | 327.9 | 615 | 631.7 | 691.7 | 586.1 | 627.9 | 276.6 | 411.1 | 384.2 | 289.8 | 322.1 | 484.8 | 318.8
1757.1 | 1518.1 | 564.6 | 225.84 | 263.9939 | 519.8 | 384.8 | 379.9 | 353.7 | 639.4 | 65.1 | 17.7 | 118.2 | 5.7 | 234.5 | 12.2 | 446.2 | 741.4 | 784.3 | 499.6 | 599.8 | 820.4 | 738.9 | 672.4 | 740.7 | 330.7 | 478.8 | 731.3 | 158.5 | 255.1 | 328.3 | 615 | 630.8 | 693.5 | 585.7 | 629.5 | 276.8 | 411.3 | 385.3 | 290.1 | 322.4 | 485.1 | 319.1
1758.1 | 1519.1 | 565.3 | 226.12 | 264.3213 | 518.4 | 385.9 | 380.3 | 353.9 | 636.3 | 65.2 | 17.7 | 118.3 | 6 | 235.2 | 12.6 | 446.1 | 741.4 | 783 | 499.8 | 600.4 | 820.7 | 738.9 | 671.3 | 750.1 | 330.8 | 478.8 | 733.5 | 158.8 | 255.4 | 328.5 | 615 | 629.3 | 691.4 | 585.3 | 630 | 277.1 | 411.3 | 385.9 | 290.5 | 322.8 | 485.5 | 319.5
1759.1 | 1520.1 | 564.4 | 225.76 | 263.9004 | 517.9 | 386.9 | 380.8 | 354.5 | 635 | 65.2 | 17.7 | 118.4 | 5.8 | 241.3 | 12.7 | 446.2 | 741.3 | 785 | 500.1 | 601 | 820.8 | 739 | 670.6 | 751.9 | 330.9 | 478.8 | 734.5 | 159 | 255.6 | 328.8 | 615.7 | 629.3 | 696.2 | 585.4 | 630.4 | 277.4 | 411 | 386.2 | 290.7 | 323 | 485.9 | 319.8
1760.1 | 1521.1 | 564.4 | 225.76 | 263.9004 | 518.4 | 387.8 | 381.1 | 355.1 | 635.3 | 65.2 | 17.7 | 118.5 | 5.3 | 245.4 | 12 | 446.2 | 741.1 | 785.1 | 500.2 | 601.6 | 821.4 | 739.1 | 669.5 | 755.2 | 331.1 | 478.9 | 736.1 | 159.3 | 255.9 | 329.2 | 616.2 | 628.6 | 701.9 | 585.3 | 630.5 | 277.7 | 410.8 | 386.2 | 291 | 323.3 | 486.3 | 320.1
1761.1 | 1522.1 | 564.7 | 225.88 | 264.0407 | 520 | 390.6 | 381.7 | 355.4 | 636 | 65.2 | 17.7 | 118.6 | 6.5 | 234 | 11.3 | 446.3 | 738.7 | 785.3 | 500.5 | 602.3 | 822 | 739 | 669 | 758.6 | 331.2 | 479 | 736.6 | 159.5 | 256.3 | 329.4 | 616.1 | 629.1 | 708.4 | 585.3 | 631.5 | 277.9 | 410.7 | 385.8 | 291.3 | 323.5 | 486.7 | 320.4
1762.1 | 1523.1 | 566.7 | 226.68 | 264.9759 | 521.3 | 392.9 | 381.5 | 355.4 | 637.5 | 65.2 | 17.6 | 118.7 | 6.4 | 200.1 | 8.6 | 446.5 | 740.2 | 783.5 | 500.9 | 602.9 | 822.2 | 738.9 | 668.6 | 762.9 | 331.4 | 479 | 737.6 | 159.8 | 256.6 | 329.8 | 616.1 | 629.7 | 709.5 | 585.4 | 633 | 278.1 | 410.6 | 386.1 | 291.6 | 323.8 | 487.1 | 320.7
1763.1 | 1524.1 | 566.8 | 226.72 | 265.0226 | 521 | 392.9 | 381.3 | 355.4 | 635.4 | 65.2 | 17.6 | 118.7 | 6.5 | 241.3 | 8.5 | 446.7 | 739 | 784.1 | 501.2 | 603.6 | 822 | 738.9 | 668.8 | 769 | 331.5 | 478.6 | 739.4 | 160 | 256.9 | 330 | 616.4 | 629.3 | 704.2 | 585.7 | 632.5 | 278.4 | 410.7 | 385.9 | 292 | 324 | 487.5 | 320.9
1764.1 | 1525.1 | 567.5 | 227 | 265.3499 | 519.6 | 394.3 | 380.9 | 355.5 | 634.6 | 65.2 | 17.6 | 118.6 | 6.1 | 221.5 | 8.8 | 446.6 | 738.6 | 786.2 | 501.4 | 604.2 | 821.9 | 739 | 668.5 | 774.6 | 331.7 | 478.4 | 740.4 | 160.3 | 257.1 | 330.4 | 616.5 | 628.7 | 709.4 | 585.7 | 635 | 278.6 | 411.2 | 385.8 | 292.4 | 324.3 | 487.9 | 321.2
1765.1 | 1526.1 | 564.1 | 225.64 | 263.7602 | 517.9 | 395.6 | 380.9 | 355.6 | 634.8 | 65.3 | 17.6 | 118.6 | 5.8 | 230.5 | 8.1 | 446.6 | 738.1 | 785.4 | 501.6 | 604.8 | 823 | 739 | 668 | 777.8 | 331.8 | 478.2 | 741.5 | 160.5 | 257.4 | 330.6 | 616.4 | 628.7 | 709.8 | 585.6 | 637.4 | 278.8 | 411.5 | 386.3 | 292.7 | 324.5 | 488.3 | 321.5
1766.1 | 1527.1 | 563.7 | 225.48 | 263.5731 | 521.2 | 396.9 | 380.9 | 356.2 | 632.6 | 65.3 | 17.6 | 118.5 | 6.9 | 220.5 | 9.2 | 446.7 | 737.8 | 786.6 | 501.8 | 605.5 | 823.8 | 739.1 | 666.9 | 780.1 | 332 | 478 | 742.7 | 160.8 | 257.7 | 331.1 | 616.7 | 629.3 | 710.4 | 585.6 | 638 | 279.1 | 411.8 | 386.4 | 293 | 324.8 | 488.7 | 321.9
1767.1 | 1528.1 | 565.2 | 226.08 | 264.2745 | 522.8 | 396.8 | 380.9 | 356.6 | 633.3 | 65.2 | 17.6 | 118.6 | 6.8 | 216.1 | 10.9 | 446.7 | 737.1 | 788.3 | 502.1 | 606.1 | 824 | 739.1 | 666.2 | 784.2 | 332.1 | 478.4 | 743.6 | 161.1 | 258 | 331.4 | 616.5 | 630.2 | 711.8 | 585.5 | 639.8 | 279.3 | 412.1 | 386.4 | 293.4 | 325 | 489.1 | 322.2
1768.1 | 1529.1 | 564.8 | 225.92 | 264.0875 | 522 | 399.4 | 381.2 | 356.9 | 634.6 | 65.2 | 17.6 | 118.6 | 7.2 | 207.3 | 11.6 | 446.9 | 738 | 783.2 | 502.4 | 606.8 | 823.6 | 739.1 | 665.9 | 780 | 332.2 | 478.7 | 745 | 161.3 | 258.3 | 331.6 | 617.2 | 631.2 | 711.7 | 585.9 | 640.4 | 279.6 | 412.5 | 386.8 | 293.9 | 325.3 | 489.6 | 322.5
1769.1 | 1530.1 | 565.7 | 226.28 | 264.5083 | 525.7 | 401.2 | 381.2 | 357 | 635.3 | 65.2 | 17.6 | 118.6 | 6.8 | 201.8 | 11.6 | 446.9 | 739.6 | 779.7 | 502.7 | 607.4 | 823.7 | 739.1 | 667.1 | 776.7 | 332.4 | 478.6 | 745.3 | 161.6 | 258.6 | 331.9 | 617.7 | 631.9 | 711.3 | 586.2 | 641.9 | 279.9 | 413.2 | 387.1 | 294.4 | 325.7 | 490.1 | 322.7
1770.1 | 1531.1 | 564.5 | 225.8 | 263.9472 | 528.1 | 400 | 381.5 | 357.3 | 635.4 | 65.2 | 17.6 | 118.6 | 7.3 | 218.9 | 9 | 446.9 | 738.9 | 779 | 503 | 608.1 | 824.9 | 739.1 | 667.3 | 771.4 | 332.5 | 478.8 | 744.6 | 161.8 | 258.9 | 332.2 | 618.2 | 632.2 | 712 | 586.6 | 643.1 | 280.2 | 413.9 | 387.5 | 294.8 | 326 | 490.6 | 323
1771.1 | 1532.1 | 565.7 | 226.28 | 264.5083 | 526.9 | 399 | 381.8 | 357.8 | 636.3 | 65.2 | 17.6 | 118.7 | 7.3 | 259.4 | 8 | 446.8 | 738.4 | 774.3 | 503.1 | 608.7 | 826.1 | 739.1 | 667.7 | 773.8 | 332.7 | 478.5 | 745.5 | 162.1 | 259.2 | 332.6 | 618.3 | 632.6 | 717.2 | 586.9 | 645.3 | 280.5 | 414.4 | 388.1 | 295.2 | 326.2 | 491.1 | 323.3
1772.1 | 1533.1 | 566.2 | 226.48 | 264.7421 | 527.3 | 398.8 | 382 | 358.7 | 635.4 | 65.2 | 17.6 | 118.6 | 7.4 | 243.5 | 6.3 | 446.9 | 739.8 | 774.8 | 503.4 | 609.4 | 827.2 | 739.1 | 667.2 | 775.7 | 332.9 | 477.7 | 747.1 | 162.3 | 259.5 | 332.9 | 618.6 | 633 | 718.5 | 587.4 | 645.7 | 280.8 | 414.7 | 388.7 | 295.6 | 326.6 | 491.5 | 323.5
1773.1 | 1534.1 | 565.4 | 226.16 | 264.368 | 529.1 | 399.1 | 382 | 359.5 | 635 | 65.3 | 17.6 | 118.6 | 7.9 | 200.1 | 6.8 | 446.9 | 740.1 | 778.4 | 503.6 | 610 | 828.1 | 739.2 | 665.7 | 781 | 333 | 478.2 | 748.2 | 162.6 | 259.8 | 333.3 | 619.1 | 633.2 | 719.2 | 588 | 645.8 | 281.2 | 415.3 | 389 | 296 | 327 | 492 | 323.7
1774.1 | 1535.1 | 565.1 | 226.04 | 264.2277 | 530.5 | 398.6 | 382.3 | 360 | 633.1 | 65.4 | 17.6 | 118.6 | 7.5 | 242.6 | 7.3 | 446.9 | 742.2 | 781.8 | 503.9 | 610.8 | 827.7 | 739.2 | 665.4 | 779.5 | 333.2 | 478.3 | 748.8 | 162.9 | 260.1 | 333.5 | 618.9 | 631.7 | 714.9 | 588.2 | 645.5 | 281.5 | 416.1 | 389.4 | 296.5 | 327.4 | 492.5 | 323.9
1775.1 | 1536.1 | 567.2 | 226.88 | 265.2096 | 527.8 | 398.6 | 382.6 | 360.5 | 632.3 | 65.5 | 17.6 | 118.6 | 7 | 256.2 | 7.4 | 447.1 | 743 | 784.5 | 504.3 | 611.5 | 827.3 | 739.4 | 664.9 | 773.5 | 333.3 | 478.2 | 748.1 | 163.1 | 260.4 | 333.8 | 618.7 | 632.1 | 718.2 | 587.9 | 646.4 | 281.8 | 416.3 | 389.5 | 296.9 | 327.8 | 493 | 324.1
1776.1 | 1537.1 | 567.5 | 227 | 265.3499 | 528.5 | 401.6 | 383.2 | 361 | 633.6 | 65.6 | 17.6 | 118.6 | 7.2 | 248.9 | 8.8 | 447.3 | 745.3 | 789.3 | 504.6 | 612.2 | 827.1 | 739.5 | 664.5 | 773.2 | 333.5 | 478.5 | 748.1 | 163.4 | 260.7 | 334.1 | 618.8 | 632.4 | 718.6 | 587.8 | 647.4 | 282.1 | 416.4 | 389.7 | 297.3 | 328.1 | 493.4 | 324.4
1777.1 | 1538.1 | 568.3 | 227.32 | 265.724 | 528 | 404.8 | 383.2 | 361 | 633.3 | 65.7 | 17.6 | 118.7 | 7.6 | 245.2 | 12 | 447.5 | 744.7 | 786.5 | 505 | 612.9 | 827.1 | 739.4 | 664.7 | 773.8 | 333.7 | 479 | 747.9 | 163.6 | 261 | 334.4 | 618.6 | 632.8 | 716 | 587.5 | 647.7 | 282.4 | 416.6 | 390.1 | 297.7 | 328.3 | 493.8 | 324.7
1778.1 | 1539.1 | 564.9 | 225.96 | 264.1342 | 527.6 | 406 | 383.3 | 361.4 | 632.3 | 65.7 | 17.6 | 118.7 | 6.6 | 230.8 | 11.7 | 447.6 | 745.7 | 784.2 | 505.3 | 613.7 | 827 | 739.4 | 666.7 | 768.3 | 333.8 | 479.2 | 747.2 | 163.9 | 261.4 | 334.8 | 618.3 | 632.6 | 713 | 587.1 | 648.5 | 282.8 | 417.1 | 390.8 | 298.2 | 328.6 | 494.3 | 325
1779.1 | 1540.1 | 563.7 | 225.48 | 263.5731 | 529.8 | 405.6 | 383.4 | 362.3 | 630.5 | 65.8 | 17.6 | 118.8 | 6.6 | 242.6 | 12.5 | 447.8 | 747 | 780.5 | 505.7 | 614.4 | 827.2 | 739.5 | 668.2 | 761.9 | 334 | 479.4 | 746.2 | 164.2 | 261.7 | 335 | 618.4 | 631.7 | 710.8 | 586.9 | 648.1 | 283.1 | 417.5 | 391.3 | 298.6 | 328.9 | 494.7 | 325.3
1780.1 | 1541.1 | 563.7 | 225.48 | 263.5731 | 530.3 | 405.7 | 383.2 | 363 | 629 | 65.9 | 17.6 | 118.9 | 7.2 | 260 | 13.6 | 447.8 | 746.8 | 780.6 | 506 | 615 | 828.1 | 739.5 | 668.7 | 757.3 | 334.1 | 479.1 | 746 | 164.4 | 262 | 335.4 | 617.9 | 629.6 | 710.9 | 586.3 | 647 | 283.4 | 418.3 | 391.6 | 299.1 | 329.3 | 495.2 | 325.7
1781.1 | 1542.1 | 564 | 225.6 | 263.7134 | 531.3 | 407 | 383.8 | 363.4 | 632 | 66 | 17.6 | 118.9 | 6.7 | 237.1 | 11.7 | 448.2 | 746.9 | 777.7 | 506.4 | 615.7 | 828.5 | 739.5 | 671.1 | 754.4 | 334.3 | 479.2 | 745.4 | 164.7 | 262.3 | 335.7 | 618.4 | 632 | 719 | 586.1 | 647 | 283.7 | 418.9 | 392.1 | 299.5 | 329.6 | 495.6 | 326
1782.1 | 1543.1 | 564.2 | 225.68 | 263.8069 | 530.3 | 406.9 | 384.2 | 363.4 | 634 | 66.1 | 17.6 | 119 | 5.9 | 259.1 | 8.2 | 448.1 | 746.7 | 781.2 | 506.6 | 616.4 | 828.4 | 739.7 | 672.1 | 754.4 | 334.4 | 479.4 | 745.7 | 165 | 262.6 | 335.9 | 618.7 | 632.5 | 720.9 | 586.1 | 646.8 | 284 | 419.5 | 393.2 | 300 | 330 | 496 | 326.3
1783.1 | 1544.1 | 565.2 | 226.08 | 264.2745 | 531.5 | 406.9 | 384.2 | 363.9 | 632.5 | 66.2 | 17.6 | 119.2 | 5.7 | 261.4 | 7 | 448.4 | 747 | 785.4 | 506.9 | 617.1 | 827.8 | 740 | 671.2 | 753.3 | 334.6 | 479.5 | 746.3 | 165.2 | 263 | 336.1 | 619.4 | 631.4 | 719.8 | 586.3 | 647.1 | 284.3 | 420.4 | 393.8 | 300.5 | 330.3 | 496.4 | 326.6
1784.1 | 1545.1 | 565.7 | 226.28 | 264.5083 | 530.2 | 406 | 384.2 | 364.2 | 632.5 | 66.2 | 17.6 | 119.4 | 5.7 | 240.2 | 8.8 | 448.4 | 745.9 | 779.9 | 507.2 | 617.8 | 827 | 740.2 | 671.8 | 751.4 | 334.8 | 479.6 | 746.5 | 165.5 | 263.3 | 336.3 | 619.9 | 631.3 | 722.4 | 586.6 | 646.7 | 284.6 | 421.2 | 394.3 | 301 | 330.7 | 496.8 | 326.9
1785.1 | 1546.1 | 565.7 | 226.28 | 264.5083 | 529.3 | 405.9 | 384.2 | 364.3 | 633.4 | 66.4 | 17.6 | 119.7 | 5.2 | 193.4 | 7.5 | 448.6 | 746.8 | 770.1 | 507.5 | 618.4 | 825.6 | 740.4 | 672.3 | 745.8 | 335 | 479.9 | 746 | 165.8 | 263.6 | 336.7 | 620.7 | 632.5 | 723.1 | 587.5 | 646.6 | 284.9 | 422.3 | 395.3 | 301.8 | 331.2 | 497.2 | 327.3
1786.1 | 1547.1 | 566.1 | 226.44 | 264.6953 | 532.4 | 405.4 | 384.2 | 365.3 | 632.9 | 66.5 | 17.6 | 119.8 | 5.7 | 205.8 | 8.7 | 448.8 | 747 | 762 | 507.7 | 619.1 | 826.6 | 740.5 | 673.1 | 741.3 | 335.1 | 480.3 | 745.7 | 166 | 263.9 | 337.1 | 622 | 634.7 | 716.2 | 589 | 645.5 | 285.3 | 423.2 | 396.1 | 302.3 | 331.6 | 497.6 | 327.6
1787.1 | 1548.1 | 567.5 | 227 | 265.3499 | 532.9 | 404.6 | 384.9 | 366.2 | 634.4 | 66.7 | 17.6 | 119.9 | 6.2 | 201.2 | 10 | 448.9 | 747.8 | 754.1 | 508 | 619.8 | 827.7 | 740.5 | 673.3 | 734.7 | 335.3 | 480.7 | 745.2 | 166.3 | 264.2 | 337.2 | 622.7 | 634.5 | 715.1 | 590.1 | 645.3 | 285.6 | 423.9 | 397.4 | 302.8 | 332 | 498 | 328
1788.1 | 1549.1 | 567.4 | 226.96 | 265.3032 | 533.7 | 404.7 | 385.6 | 366.9 | 634.9 | 66.8 | 17.5 | 120 | 6 | 200.5 | 9.8 | 449 | 747.3 | 746.8 | 508.1 | 620.5 | 827.5 | 740.6 | 673.4 | 730.8 | 335.4 | 481.1 | 744.9 | 166.6 | 264.5 | 337.5 | 623.6 | 635.6 | 706.9 | 591.2 | 643.1 | 286.1 | 424.6 | 399.5 | 303.4 | 332.7 | 498.4 | 328.4
1789.1 | 1550.1 | 567.9 | 227.16 | 265.537 | 537.8 | 403.9 | 386 | 367.6 | 636.3 | 66.9 | 17.5 | 120 | 5.9 | 202 | 9.3 | 449.1 | 748.4 | 745.3 | 508.4 | 621.1 | 827.2 | 740.7 | 673.5 | 727.7 | 335.6 | 481.2 | 744.9 | 166.9 | 264.8 | 337.9 | 624.9 | 635.8 | 702.3 | 592.5 | 642.8 | 286.7 | 425.2 | 401.1 | 304 | 333.3 | 498.8 | 328.8
1790.1 | 1551.1 | 568 | 227.2 | 265.5837 | 538.7 | 402.7 | 386.7 | 367.8 | 634 | 66.9 | 17.5 | 120.1 | 5.8 | 216.5 | 7.9 | 449.1 | 751 | 750 | 508.6 | 621.8 | 827.6 | 740.8 | 673.9 | 732 | 335.8 | 481.4 | 745.3 | 167.2 | 265 | 338.2 | 625.3 | 634.5 | 700.1 | 593.7 | 642.3 | 287.3 | 426 | 402.2 | 304.5 | 333.6 | 499.2 | 329.1
1791.1 | 1552.1 | 565.9 | 226.36 | 264.6018 | 539 | 401.2 | 387.1 | 367.7 | 632.4 | 67 | 17.5 | 120.2 | 6.5 | 204.7 | 6.9 | 449.1 | 751 | 755.5 | 508.9 | 622.5 | 828.3 | 740.7 | 673.7 | 739 | 336 | 481.2 | 746.9 | 167.4 | 265.3 | 338.4 | 624.7 | 633.7 | 704.5 | 594.2 | 642.8 | 287.9 | 426.5 | 403.6 | 305 | 334 | 499.7 | 329.5
1792.1 | 1553.1 | 565.5 | 226.2 | 264.4148 | 544.2 | 399.9 | 387.5 | 367.5 | 631.8 | 67.1 | 17.5 | 120.5 | 6.1 | 197 | 6.6 | 449.2 | 747.9 | 759.5 | 509.1 | 623.2 | 828.5 | 740.9 | 671.8 | 743.2 | 336.1 | 481.2 | 747 | 167.7 | 265.6 | 338.8 | 624.4 | 632.7 | 704.3 | 594.5 | 642.8 | 288.5 | 426.7 | 403.7 | 305.3 | 334.3 | 500.1 | 329.8
1793.1 | 1554.1 | 565.7 | 226.28 | 264.5083 | 551.7 | 399.5 | 387.5 | 367 | 634.5 | 67.2 | 17.5 | 120.9 | 6.3 | 155.8 | 5.8 | 449.2 | 745.8 | 761.8 | 509.4 | 624 | 828.7 | 740.9 | 670.2 | 747.2 | 336.3 | 481.5 | 748.1 | 168 | 265.9 | 339.1 | 624.2 | 634.2 | 708.8 | 594.7 | 644.2 | 288.9 | 426.9 | 403.6 | 305.7 | 334.6 | 500.3 | 330.1
1794.1 | 1555.1 | 566.9 | 226.76 | 265.0694 | 555.5 | 399.4 | 387.3 | 366.3 | 637.7 | 67.2 | 17.5 | 121.2 | 7.3 | 169.3 | 3.4 | 449.2 | 744.9 | 760.1 | 509.6 | 624.7 | 829 | 741 | 670.9 | 751.3 | 336.4 | 481.8 | 749.1 | 168.3 | 266.2 | 339.4 | 624.1 | 634.6 | 713.7 | 594.9 | 647.4 | 289.3 | 427.1 | 403.6 | 306.1 | 334.8 | 500.7 | 330.4
1795.1 | 1556.1 | 565.3 | 226.12 | 264.3213 | 556.9 | 398.7 | 387.5 | 366.3 | 638.1 | 67.3 | 17.5 | 121.4 | 7.8 | 209.1 | 4.4 | 449.1 | 745.3 | 762.6 | 509.8 | 625.4 | 829.7 | 741.3 | 670.5 | 754.1 | 336.6 | 482.2 | 750.5 | 168.5 | 266.5 | 339.8 | 623.8 | 635.5 | 717 | 594.9 | 649.2 | 289.7 | 427.3 | 403.4 | 306.6 | 335.1 | 501.1 | 330.8
1796.1 | 1557.1 | 565.4 | 226.16 | 264.368 | 560 | 397.2 | 388.2 | 366.7 | 637.5 | 67.4 | 17.5 | 121.4 | 7.5 | 212 | 4.4 | 449.1 | 746 | 760.4 | 510 | 626.1 | 830.5 | 741.3 | 670.4 | 753.7 | 336.8 | 482.5 | 751 | 168.8 | 266.8 | 340 | 623.7 | 635.1 | 717.1 | 594.7 | 648.3 | 289.9 | 427.4 | 403.3 | 307.1 | 335.4 | 501.5 | 331.1
1797.1 | 1558.1 | 565.4 | 226.16 | 264.368 | 561.8 | 396.7 | 388.6 | 367.1 | 633.7 | 67.4 | 17.5 | 121.5 | 7 | 229 | 4.1 | 449 | 744.3 | 756.5 | 510.3 | 626.8 | 831.2 | 741.4 | 671.3 | 755.8 | 337 | 482.5 | 752.2 | 169.1 | 267.1 | 340.3 | 623 | 634.1 | 706.8 | 594.1 | 645.4 | 290.1 | 427.6 | 403.2 | 307.5 | 335.7 | 501.9 | 331.4
1798.1 | 1559.1 | 566.8 | 226.72 | 265.0226 | 564.5 | 397.1 | 389.1 | 367.5 | 633.1 | 67.5 | 17.5 | 121.5 | 6.8 | 200.1 | 3.8 | 449.1 | 742.7 | 760.4 | 510.5 | 627.5 | 831.7 | 741.4 | 672.6 | 766.2 | 337.2 | 482.6 | 753.4 | 169.4 | 267.5 | 340.6 | 623.3 | 634.1 | 712.5 | 593.8 | 645.7 | 290.3 | 427.9 | 402.9 | 308 | 336 | 502.3 | 331.8
1799.1 | 1560.1 | 565.5 | 226.2 | 264.4148 | 566 | 397.9 | 389.8 | 367.8 | 634.8 | 67.5 | 17.5 | 121.6 | 6.6 | 230.1 | 3.7 | 449.2 | 742.7 | 757.4 | 510.7 | 628.2 | 832.1 | 741.5 | 673.1 | 770.9 | 337.4 | 482.8 | 754.7 | 169.7 | 267.8 | 340.9 | 623.5 | 632.9 | 712.8 | 593.8 | 646.3 | 290.5 | 428 | 402.5 | 308.4 | 336.3 | 502.7 | 332.1
1800.1 | 1561.1 | 566 | 226.4 | 264.6486 | 562.5 | 398.1 | 390.1 | 368.3 | 631.7 | 67.6 | 17.5 | 121.7 | 6.8 | 249.7 | 4.1 | 449.1 | 742.3 | 756.6 | 510.8 | 628.9 | 833 | 741.5 | 673.2 | 770 | 337.5 | 483.1 | 755.4 | 170 | 268.1 | 341.2 | 623.3 | 630.7 | 715.9 | 593.8 | 647.4 | 290.7 | 427.9 | 401.7 | 308.8 | 336.5 | 503 | 332.4
1801.1 | 1562.1 | 566 | 226.4 | 264.6486 | 570.8 | 397.8 | 390.9 | 368.8 | 630 | 67.6 | 17.5 | 121.9 | 6.3 | 252.1 | 4.2 | 449.1 | 743.5 | 759.8 | 511.1 | 629.6 | 833.1 | 741.6 | 672.9 | 773.6 | 337.7 | 483.5 | 757.7 | 170.2 | 268.5 | 341.6 | 623.2 | 629.1 | 714.9 | 593.8 | 647.2 | 290.9 | 427.8 | 401.1 | 309.1 | 336.8 | 503.3 | 332.8
1802.1 | 1563.1 | 566.7 | 226.68 | 264.9759 | 578.2 | 398.2 | 391.6 | 369.2 | 631.9 | 67.7 | 17.5 | 122.1 | 6.4 | 248.6 | 5.3 | 449.2 | 743 | 760.5 | 511.3 | 630.3 | 833.4 | 741.6 | 674.4 | 775.6 | 337.9 | 483.8 | 758.1 | 170.5 | 268.8 | 342.1 | 623.4 | 629.3 | 717.1 | 594 | 647.7 | 291.1 | 427.6 | 401.2 | 309.5 | 337.1 | 503.7 | 333.1
1803.1 | 1564.1 | 567.1 | 226.84 | 265.1629 | 576.1 | 399.4 | 392.3 | 369.2 | 637 | 67.7 | 17.5 | 122.1 | 6.7 | 239.2 | 7.1 | 449.1 | 743.7 | 760.7 | 511.5 | 631 | 833.7 | 741.7 | 675.1 | 775.7 | 338.1 | 484.1 | 759.4 | 170.8 | 269.2 | 342.7 | 624 | 631.4 | 716.5 | 594.4 | 648.4 | 291.3 | 427.4 | 401.1 | 309.8 | 337.2 | 504 | 333.4
1804.1 | 1565.1 | 567.4 | 226.96 | 265.3032 | 576 | 401 | 393.9 | 369.2 | 639.6 | 67.7 | 17.5 | 122.1 | 6.4 | 247.4 | 9.2 | 449.1 | 744.9 | 761.2 | 511.7 | 631.6 | 833.7 | 741.7 | 676.4 | 774.9 | 338.2 | 484.7 | 759.8 | 171.1 | 269.5 | 343 | 624.2 | 632.5 | 712.7 | 594.7 | 647.5 | 291.4 | 427.1 | 401.1 | 310.2 | 337.5 | 504.3 | 333.8
1805.1 | 1566.1 | 567.1 | 226.84 | 265.1629 | 578.2 | 401.3 | 394.3 | 369.2 | 638.8 | 67.7 | 17.5 | 122 | 6.7 | 227.7 | 9.5 | 449.2 | 745.6 | 756.4 | 512 | 632.3 | 833.5 | 741.6 | 677.1 | 777.2 | 338.4 | 485.3 | 760.3 | 171.4 | 269.8 | 343.1 | 624.7 | 632.9 | 716 | 594.9 | 649 | 291.6 | 427.6 | 401.8 | 310.7 | 338 | 504.7 | 334.1
1806.1 | 1567.1 | 567 | 226.8 | 265.1161 | 575.8 | 402.3 | 394.8 | 369.9 | 637.7 | 67.7 | 17.5 | 122.1 | 6.5 | 251.3 | 9.4 | 449.6 | 743.4 | 746.8 | 512.4 | 633 | 832.7 | 741.7 | 676.4 | 771.3 | 338.6 | 485.9 | 760.1 | 171.7 | 270.2 | 343.3 | 625.7 | 633.5 | 716.8 | 595.7 | 651.7 | 291.8 | 428.5 | 402.4 | 311.4 | 338.4 | 505.1 | 334.4
1807.1 | 1568.1 | 567 | 226.8 | 265.1161 | 572.3 | 402.3 | 394.8 | 371 | 638.1 | 67.8 | 17.5 | 122.1 | 7.1 | 237.5 | 9.1 | 449.6 | 742.1 | 751.6 | 512.7 | 633.7 | 831.9 | 741.6 | 677.3 | 764.1 | 338.8 | 486.5 | 759.1 | 172 | 270.5 | 343.6 | 626.7 | 636.5 | 720 | 596.4 | 653.1 | 292.1 | 429.3 | 403.5 | 311.9 | 338.9 | 505.5 | 334.8
1808.1 | 1569.1 | 566.7 | 226.68 | 264.9759 | 571.9 | 401.2 | 395 | 371.9 | 640.8 | 67.9 | 17.5 | 122.2 | 6.6 | 227.9 | 8.4 | 449.5 | 740.9 | 751 | 512.8 | 634.3 | 832.4 | 741.5 | 678.7 | 763.6 | 339 | 487 | 758.6 | 172.2 | 270.9 | 343.9 | 627.2 | 636.5 | 724 | 597 | 654.2 | 292.5 | 429.6 | 404 | 312.3 | 339.3 | 506.1 | 335.2
1809.1 | 1570.1 | 567 | 226.8 | 265.1161 | 576.9 | 401 | 394.9 | 371.9 | 638.3 | 67.9 | 17.5 | 122.3 | 6.4 | 236.3 | 8.6 | 449.3 | 743.7 | 752.2 | 513 | 635 | 833 | 741.5 | 677.5 | 769.6 | 339.2 | 487.4 | 759.4 | 172.5 | 271.2 | 344.2 | 627.4 | 634.5 | 720.9 | 597.7 | 654.1 | 292.8 | 429.9 | 404.3 | 312.8 | 339.5 | 506.6 | 335.5
1810.1 | 1571.1 | 567.3 | 226.92 | 265.2564 | 581.2 | 401.8 | 395 | 371.7 | 638.7 | 68 | 17.5 | 122.5 | 5.6 | 233.1 | 8.8 | 449.3 | 742.2 | 751 | 513.2 | 635.6 | 833.3 | 741.6 | 676.8 | 766.4 | 339.3 | 487.9 | 759.3 | 172.8 | 271.5 | 344.5 | 627.4 | 634.1 | 720.5 | 598.1 | 652.8 | 293.2 | 430.1 | 404.4 | 313.2 | 339.7 | 507 | 335.8
1811.1 | 1572.1 | 565.2 | 226.08 | 264.2745 | 586.5 | 402.9 | 395.1 | 371.7 | 638.7 | 68 | 17.5 | 122.6 | 5.7 | 231.2 | 8.7 | 449.4 | 742.1 | 746.8 | 513.4 | 636.3 | 833.5 | 741.6 | 676.2 | 764 | 339.5 | 488.3 | 759.3 | 173.1 | 271.9 | 344.7 | 627.7 | 635.2 | 715.9 | 598.5 | 651.1 | 293.5 | 430.9 | 405.2 | 313.9 | 340.1 | 507.3 | 336.1
1812.1 | 1573.1 | 566 | 226.4 | 264.6486 | 587.5 | 402.6 | 394.8 | 372 | 639.5 | 68 | 17.5 | 122.7 | 5.8 | 226.4 | 8.1 | 449.6 | 742.7 | 744.6 | 513.6 | 637 | 832.9 | 741.8 | 677.6 | 755.9 | 339.7 | 488.7 | 758.1 | 173.4 | 272.2 | 345.1 | 628.5 | 638.2 | 717 | 599.4 | 652.3 | 293.9 | 431.8 | 406.1 | 314.7 | 340.5 | 507.7 | 336.5
1813.1 | 1574.1 | 567.2 | 226.88 | 265.2096 | 586.4 | 401.6 | 394.7 | 372.7 | 643.9 | 68 | 17.5 | 122.9 | 5.9 | 217.7 | 7.7 | 449.7 | 742.4 | 749.6 | 514 | 637.7 | 832.5 | 742.1 | 678.5 | 751.6 | 339.8 | 489.1 | 756.5 | 173.7 | 272.6 | 345.6 | 629.4 | 640.9 | 718.6 | 600.5 | 655.4 | 294.3 | 432.9 | 406.9 | 315.4 | 340.9 | 508.2 | 336.8
1814.1 | 1575.1 | 566.6 | 226.64 | 264.9291 | 588.5 | 401.5 | 394.4 | 373.1 | 645.7 | 68 | 17.4 | 123.1 | 6.6 | 221.5 | 7.8 | 449.6 | 742.2 | 751.6 | 514.1 | 638.4 | 832.3 | 742.3 | 677 | 758.7 | 340 | 489.5 | 757.1 | 174 | 272.9 | 345.8 | 629.2 | 639.9 | 719.1 | 601.1 | 657.6 | 294.7 | 433.4 | 407.3 | 315.9 | 341.1 | 508.8 | 337.3
1815.1 | 1576.1 | 566 | 226.4 | 264.6486 | 593.8 | 402.4 | 394.6 | 373.2 | 643.9 | 68 | 17.4 | 123.1 | 7 | 203.1 | 8.8 | 449.6 | 741.9 | 760.1 | 514.3 | 639.1 | 832.3 | 742.4 | 676.9 | 767.4 | 340.2 | 490 | 758.2 | 174.3 | 273.2 | 346.3 | 628.9 | 639.5 | 720.4 | 601.1 | 656.7 | 295.1 | 433.8 | 407.8 | 316.5 | 341.4 | 509.2 | 337.7
1816.1 | 1577.1 | 566.4 | 226.56 | 264.8356 | 595.3 | 404.2 | 395.2 | 373.6 | 645.9 | 68 | 17.4 | 123.2 | 7 | 214.8 | 9.5 | 449.9 | 741.1 | 759.1 | 514.7 | 639.7 | 831.9 | 742.6 | 676.9 | 767.8 | 340.4 | 490.4 | 758.7 | 174.6 | 273.5 | 346.6 | 630 | 641.2 | 727.2 | 601.7 | 659.5 | 295.5 | 434.8 | 408.7 | 317.2 | 341.9 | 509.6 | 338
1817.1 | 1578.1 | 566.3 | 226.52 | 264.7888 | 596.8 | 405.4 | 394.8 | 374.4 | 645.3 | 68 | 17.4 | 123.2 | 6.7 | 222.3 | 11.9 | 450 | 741.9 | 753.4 | 515 | 640.4 | 832 | 742.8 | 676.1 | 768.2 | 340.6 | 490.9 | 759.4 | 174.9 | 273.9 | 346.8 | 630.8 | 640.2 | 730.5 | 602.5 | 660.4 | 295.9 | 435.5 | 409 | 317.6 | 342.1 | 510 | 338.4
1818.1 | 1579.1 | 566.6 | 226.64 | 264.9291 | 595.1 | 404.9 | 394.9 | 375.1 | 644.1 | 68 | 17.4 | 123.2 | 5.8 | 218.8 | 12.7 | 449.9 | 742.6 | 751 | 515.1 | 641 | 832.2 | 742.7 | 677.6 | 768.6 | 340.7 | 491.3 | 760.2 | 175.2 | 274.2 | 347.2 | 630.8 | 639.2 | 732.5 | 602.9 | 661.4 | 296.2 | 435.6 | 409 | 317.9 | 342.4 | 510.4 | 338.8
1819.1 | 1580.1 | 565.7 | 226.28 | 264.5083 | 604.8 | 404.2 | 395.7 | 375 | 643.1 | 68.1 | 17.4 | 123.2 | 6.4 | 210.5 | 12.3 | 449.9 | 742.8 | 756.2 | 515.4 | 641.7 | 832.6 | 742.7 | 677.7 | 767.1 | 340.9 | 491.8 | 760.7 | 175.5 | 274.5 | 347.7 | 630.2 | 639 | 731.8 | 603 | 660.4 | 296.5 | 435.6 | 408.8 | 318.2 | 342.7 | 510.8 | 339.1
1820.1 | 1581.1 | 566 | 226.4 | 264.6486 | 603.9 | 407.4 | 396.6 | 374.9 | 640.9 | 68.1 | 17.4 | 123.2 | 6.1 | 219.4 | 11.3 | 450 | 744.5 | 758.7 | 515.6 | 642.3 | 832.7 | 742.7 | 677.6 | 767.5 | 341.1 | 492.2 | 762.1 | 175.8 | 274.8 | 347.9 | 629.5 | 637.2 | 726.8 | 602.7 | 658.7 | 296.8 | 435.7 | 408.8 | 318.6 | 343 | 511.2 | 339.5
1821.1 | 1582.1 | 566 | 226.4 | 264.6486 | 602.3 | 410.7 | 397.8 | 375.3 | 641.9 | 68.2 | 17.4 | 123.1 | 5.9 | 249.9 | 10.9 | 450 | 743.7 | 765.3 | 515.8 | 643 | 832.2 | 742.9 | 679.3 | 769.8 | 341.2 | 492.7 | 761.9 | 176.1 | 275.1 | 348.7 | 629.7 | 638.7 | 725.9 | 602.6 | 658.5 | 297 | 435.7 | 408.6 | 318.9 | 343.3 | 511.6 | 339.8
1822.1 | 1583.1 | 566.8 | 226.72 | 265.0226 | 602.3 | 414.3 | 398.8 | 375.7 | 646.7 | 68.3 | 17.4 | 122.9 | 6 | 238.6 | 12.3 | 450.2 | 746 | 762.7 | 516.1 | 643.6 | 831.8 | 743.1 | 679.3 | 769.2 | 341.4 | 493.2 | 762.5 | 176.4 | 275.4 | 348.9 | 630.2 | 639.6 | 721.7 | 602.9 | 657.1 | 297.1 | 436.1 | 408.6 | 319.3 | 343.6 | 511.9 | 340.1
1823.1 | 1584.1 | 566.9 | 226.76 | 265.0694 | 604.8 | 415.3 | 399.6 | 376 | 645.8 | 68.4 | 17.4 | 122.8 | 7.2 | 229.2 | 11.6 | 450.3 | 748.6 | 755.5 | 516.4 | 644.3 | 831.7 | 743 | 680.3 | 767.2 | 341.6 | 493.8 | 763.2 | 176.8 | 275.7 | 348.9 | 630.8 | 640.2 | 717 | 603 | 656 | 297.3 | 437 | 408.8 | 320 | 344.1 | 512.4 | 340.5
1824.1 | 1585.1 | 566.5 | 226.6 | 264.8823 | 609.8 | 414.9 | 399.2 | 376.6 | 645.5 | 68.5 | 17.4 | 122.9 | 7 | 221 | 8.9 | 450.3 | 751.2 | 756.5 | 516.6 | 644.9 | 831.6 | 743.1 | 682.8 | 757.5 | 341.8 | 494.3 | 762.3 | 177.1 | 276.1 | 349.3 | 631.3 | 640.3 | 713.2 | 603.3 | 655.6 | 297.6 | 437.6 | 409.1 | 320.6 | 344.4 | 512.8 | 340.9
1825.1 | 1586.1 | 565.7 | 226.28 | 264.5083 | 611 | 413.6 | 399.4 | 377.3 | 646.8 | 68.6 | 17.4 | 123.2 | 8.4 | 242.1 | 8.9 | 450.5 | 754.6 | 752.5 | 516.9 | 645.5 | 830.7 | 743.2 | 684.1 | 751.8 | 341.9 | 494.8 | 760.7 | 177.4 | 276.4 | 349.6 | 631.9 | 641.4 | 719.2 | 603.7 | 658 | 297.8 | 438.4 | 409.5 | 321.3 | 344.8 | 513.3 | 341.3
1826.1 | 1587.1 | 565.9 | 226.36 | 264.6018 | 608.9 | 414.3 | 399.9 | 378.1 | 648.4 | 68.8 | 17.4 | 123.4 | 7.6 | 244.1 | 9.5 | 450.6 | 753.7 | 744.5 | 517.1 | 646.2 | 830 | 743.3 | 683.3 | 752.7 | 342.1 | 495.3 | 759.7 | 177.7 | 276.8 | 349.9 | 633.1 | 643.2 | 719 | 604.4 | 660 | 298.2 | 440.1 | 410.5 | 322.2 | 345.4 | 513.9 | 341.7
1827.1 | 1588.1 | 566.6 | 226.64 | 264.9291 | 610 | 413.7 | 400.7 | 379 | 646.3 | 69 | 17.4 | 123.5 | 7.1 | 248.3 | 8.9 | 450.5 | 752.4 | 741 | 517.3 | 646.8 | 830.9 | 743.2 | 682.4 | 749.2 | 342.3 | 495.8 | 759.5 | 178 | 277.1 | 350.5 | 633.4 | 641.9 | 721.6 | 605 | 660 | 298.7 | 441.1 | 410.5 | 322.7 | 345.7 | 514.4 | 342.2
1828.1 | 1589.1 | 566.9 | 226.76 | 265.0694 | 609.5 | 412.6 | 401.3 | 379.2 | 641.6 | 69 | 17.4 | 123.6 | 7.3 | 245.4 | 9.1 | 450.4 | 751.4 | 746.6 | 517.5 | 647.4 | 832.2 | 743.1 | 683 | 742.9 | 342.5 | 496.4 | 758.8 | 178.3 | 277.4 | 350.9 | 632.5 | 638.6 | 717.7 | 604.7 | 658.7 | 299.1 | 441.1 | 410.9 | 323.2 | 346.1 | 514.8 | 342.6
1829.1 | 1590.1 | 568.1 | 227.24 | 265.6305 | 607.6 | 413.5 | 402.3 | 378.9 | 636.8 | 69.1 | 17.4 | 123.7 | 7.1 | 244.2 | 8.9 | 450.3 | 752.2 | 746.3 | 517.6 | 648 | 833.5 | 742.9 | 685.3 | 739.5 | 342.7 | 497 | 758.8 | 178.6 | 277.7 | 351 | 632.1 | 635.7 | 710 | 604.4 | 656.1 | 299.5 | 441.5 | 412.1 | 323.8 | 346.6 | 515.2 | 343
1830.1 | 1591.1 | 567.3 | 226.92 | 265.2564 | 608.2 | 415.7 | 402.9 | 379.3 | 637.8 | 69.2 | 17.4 | 123.9 | 7 | 249.7 | 8.5 | 450.3 | 753.1 | 744.6 | 517.7 | 648.6 | 834.3 | 743 | 686.7 | 741.2 | 342.8 | 497.6 | 759.1 | 178.9 | 278 | 351.2 | 633.3 | 637.1 | 716 | 604.7 | 656.6 | 300 | 442.4 | 413 | 324.4 | 346.9 | 515.5 | 343.4
1831.1 | 1592.1 | 566.8 | 226.72 | 265.0226 | 606.2 | 416.3 | 403 | 380.4 | 643.9 | 69.2 | 17.4 | 124.2 | 7.3 | 218.2 | 8.9 | 450.5 | 750.7 | 741.1 | 518.1 | 649.3 | 834.6 | 743 | 686.3 | 733.2 | 343 | 498.2 | 758.1 | 179.2 | 278.4 | 351.5 | 633.7 | 639.1 | 716.5 | 605 | 658.9 | 300.4 | 443.3 | 413.6 | 325 | 347.3 | 515.9 | 343.8
1832.1 | 1593.1 | 566.8 | 226.72 | 265.0226 | 606.4 | 416.4 | 403.2 | 381.5 | 642.9 | 69.3 | 17.4 | 124.2 | 7.5 | 238.2 | 10.4 | 450.4 | 747.8 | 727.8 | 518.3 | 649.9 | 832.8 | 743 | 686.1 | 722.7 | 343.2 | 498.9 | 756 | 179.6 | 278.7 | 351.8 | 634 | 640.1 | 705.6 | 605.6 | 657.1 | 300.9 | 444.4 | 415.1 | 325.7 | 348 | 516.3 | 344.2
1833.1 | 1594.1 | 566.9 | 226.76 | 265.0694 | 612.5 | 415.5 | 403.9 | 382.4 | 645 | 69.4 | 17.4 | 124.4 | 6.8 | 233.7 | 10.5 | 450.5 | 747.4 | 726.3 | 518.5 | 650.4 | 831.2 | 742.9 | 687.3 | 718.8 | 343.4 | 499.5 | 754.3 | 179.9 | 279 | 352.1 | 634.6 | 647.7 | 701.2 | 606.1 | 656 | 301.4 | 445.7 | 416.5 | 326.6 | 348.6 | 516.6 | 344.6
1834.1 | 1595.1 | 566.8 | 226.72 | 265.0226 | 614.4 | 415.3 | 404.6 | 384.1 | 650.4 | 69.4 | 17.4 | 124.6 | 7.4 | 254.1 | 10.5 | 450.7 | 746.6 | 732.4 | 518.8 | 651.1 | 831.5 | 742.9 | 688.9 | 721.2 | 343.6 | 500.1 | 755 | 180.2 | 279.3 | 352.6 | 635.2 | 649.6 | 711.2 | 606.9 | 658.3 | 301.9 | 446.7 | 417.4 | 327.2 | 349 | 517.1 | 345.1
1835.1 | 1596.1 | 566.5 | 226.6 | 264.8823 | 612.9 | 414.1 | 404.8 | 385 | 648.4 | 69.5 | 17.3 | 124.6 | 7.5 | 237.8 | 11.3 | 450.8 | 744.7 | 722.3 | 519 | 651.7 | 831.6 | 742.7 | 688.9 | 718.9 | 343.8 | 500.9 | 754.7 | 180.5 | 279.7 | 352.8 | 635.5 | 648.8 | 711.9 | 607.6 | 661.7 | 302.4 | 447.6 | 418 | 327.8 | 349.4 | 517.5 | 345.5
1836.1 | 1597.1 | 567 | 226.8 | 265.1161 | 615 | 413.1 | 405.4 | 385.1 | 648.9 | 69.5 | 17.3 | 124.6 | 6.6 | 241.7 | 10.5 | 450.8 | 747.2 | 708.9 | 519.2 | 652.3 | 828.9 | 742.7 | 691 | 713.6 | 344 | 501.7 | 753.6 | 180.8 | 280 | 353.3 | 636 | 649.7 | 709.1 | 608.2 | 663 | 302.9 | 448.6 | 419 | 328.5 | 349.9 | 518 | 345.9
1837.1 | 1598.1 | 566.8 | 226.72 | 265.0226 | 615 | 413.4 | 405.8 | 385.6 | 647.9 | 69.5 | 17.3 | 124.7 | 6.5 | 244.6 | 9.6 | 450.9 | 749.3 | 706.6 | 519.4 | 652.8 | 825.9 | 742.6 | 693.4 | 706.1 | 344.2 | 502.4 | 752.5 | 181.2 | 280.3 | 353.6 | 635.7 | 649.3 | 701.5 | 608.4 | 661.9 | 303.3 | 449.9 | 420.3 | 329.4 | 350.5 | 518.4 | 346.3
1838.1 | 1599.1 | 566.2 | 226.48 | 264.7421 | 615.1 | 413.9 | 406.6 | 386.8 | 647.1 | 69.6 | 17.3 | 124.7 | 6.8 | 251 | 10 | 451 | 752 | 714.2 | 519.6 | 653.4 | 824.8 | 742.5 | 700.9 | 707.4 | 344.4 | 503.3 | 752.2 | 181.5 | 280.6 | 353.8 | 636.1 | 649.7 | 705.5 | 608.7 | 660.3 | 303.8 | 451.7 | 420.9 | 330.1 | 351 | 518.7 | 346.8
1839.1 | 1600.1 | 568.1 | 227.24 | 265.6305 | 615.6 | 413.9 | 407.4 | 387.2 | 648.8 | 69.6 | 17.3 | 124.7 | 5.9 | 238.8 | 10.5 | 451.2 | 750.8 | 721.1 | 519.9 | 654 | 825.2 | 742.4 | 700.5 | 711.8 | 344.6 | 504.1 | 752 | 181.8 | 280.9 | 354.3 | 636.3 | 648.3 | 706.1 | 609.1 | 659.2 | 304.3 | 452.4 | 420.8 | 330.5 | 351.2 | 519.1 | 347.2
1840.1 | 1601.1 | 566.6 | 226.64 | 264.9291 | 619.6 | 415.4 | 408.1 | 386.8 | 647.6 | 69.7 | 17.3 | 124.9 | 6.2 | 220.7 | 10.6 | 451.1 | 751.5 | 725.3 | 520 | 654.6 | 825.3 | 742.3 | 697.8 | 714.3 | 344.8 | 505 | 753.1 | 182.1 | 281.2 | 354.3 | 636.5 | 647 | 707.9 | 609.4 | 657.6 | 304.7 | 452.7 | 421.3 | 331 | 351.6 | 519.5 | 347.7
1841.1 | 1602.1 | 567.1 | 226.84 | 265.1629 | 625.3 | 415.9 | 408 | 386.8 | 649.5 | 69.8 | 17.3 | 125.1 | 6.2 | 233.2 | 9.5 | 451.4 | 750 | 722.1 | 520.3 | 655.2 | 824.8 | 742.3 | 697 | 714.1 | 345.1 | 505.9 | 753.1 | 182.4 | 281.5 | 354.6 | 637.5 | 647.3 | 710.7 | 609.9 | 658.3 | 305.1 | 452.9 | 422.1 | 331.6 | 352.1 | 519.8 | 348.1
1842.1 | 1603.1 | 567.3 | 226.92 | 265.2564 | 625.1 | 415.5 | 409 | 387.1 | 650.2 | 69.9 | 17.3 | 125.5 | 5.8 | 228.6 | 9 | 451.4 | 747.9 | 725 | 520.5 | 655.8 | 825 | 742.4 | 695 | 717.8 | 345.3 | 506.9 | 753.1 | 182.8 | 281.9 | 354.9 | 638.2 | 647.1 | 713.8 | 610.6 | 659.4 | 305.6 | 453.4 | 422.7 | 332.3 | 352.7 | 520.2 | 348.5
1843.1 | 1604.1 | 567.3 | 226.92 | 265.2564 | 626.4 | 414.6 | 409.8 | 387.1 | 650.3 | 69.9 | 17.3 | 125.6 | 6.5 | 233.8 | 8.7 | 451.2 | 747.8 | 723.9 | 520.5 | 656.4 | 826.3 | 742.5 | 693.8 | 727.1 | 345.5 | 507.9 | 754.6 | 183.1 | 282.2 | 355.2 | 638.8 | 646.4 | 720.4 | 611.5 | 662.4 | 306 | 453.6 | 422.7 | 332.8 | 353 | 520.6 | 348.9
1844.1 | 1605.1 | 567.4 | 226.96 | 265.3032 | 627.8 | 414.3 | 410.2 | 387.6 | 648.5 | 69.9 | 17.3 | 125.8 | 7.1 | 229.4 | 7.8 | 451.2 | 746.3 | 724.7 | 520.7 | 657 | 827.2 | 742.6 | 691.2 | 734.2 | 345.7 | 509 | 756.5 | 183.4 | 282.5 | 355.5 | 638.5 | 644.7 | 721.5 | 612.2 | 663.4 | 306.5 | 453.9 | 422.8 | 333.3 | 353.3 | 521 | 349.3
1845.1 | 1606.1 | 567.6 | 227.04 | 265.3967 | 628.5 | 414.7 | 410.5 | 387.2 | 647.8 | 70 | 17.3 | 125.9 | 6.5 | 230.7 | 7.8 | 451.4 | 747.5 | 726.1 | 520.9 | 657.6 | 827.3 | 742.8 | 690.7 | 744.7 | 345.9 | 510 | 759 | 183.7 | 282.8 | 355.8 | 638.5 | 643.2 | 723.9 | 612.7 | 663.7 | 306.8 | 453.9 | 422.6 | 333.7 | 353.6 | 521.3 | 349.7
1846.1 | 1607.1 | 567.3 | 226.92 | 265.2564 | 631.6 | 413.9 | 410.6 | 387.2 | 646.2 | 70 | 17.3 | 126 | 5.9 | 251 | 8.1 | 451.4 | 746.9 | 732.9 | 521.1 | 658.3 | 827.2 | 743 | 689.6 | 750.1 | 346.2 | 511.1 | 760.4 | 184 | 283.1 | 356.2 | 638.9 | 640.8 | 725 | 613.3 | 662.7 | 307.1 | 453.7 | 422.4 | 334.1 | 353.9 | 521.7 | 350.1
1847.1 | 1608.1 | 567.1 | 226.84 | 265.1629 | 636.4 | 413.4 | 411.1 | 387.6 | 643.4 | 70.1 | 17.3 | 126.1 | 6.2 | 223.1 | 6.6 | 451.3 | 745.4 | 745 | 521.2 | 658.9 | 827 | 743.1 | 690.3 | 754.9 | 346.4 | 512.1 | 761.9 | 184.4 | 283.4 | 356.6 | 638.4 | 640.5 | 728.1 | 613.2 | 665.4 | 307.4 | 453.9 | 422.2 | 334.6 | 354.2 | 522 | 350.5
1848.1 | 1609.1 | 566.9 | 226.76 | 265.0694 | 646.7 | 413.3 | 411.3 | 387.6 | 642.2 | 70.2 | 17.3 | 126.1 | 6.6 | 201 | 4.6 | 451.2 | 744.9 | 745.5 | 521.3 | 659.6 | 828 | 743.2 | 689.1 | 758.7 | 346.6 | 513.2 | 761.5 | 184.7 | 283.7 | 357 | 637.9 | 639.3 | 726.3 | 613.1 | 666.3 | 307.7 | 453.9 | 421.8 | 335 | 354.4 | 522.4 | 350.9
1849.1 | 1610.1 | 567 | 226.8 | 265.1161 | 658.6 | 414.6 | 411.8 | 387.8 | 641.6 | 70.2 | 17.3 | 126.3 | 7.1 | 234.3 | 4.1 | 451.4 | 743.9 | 742.1 | 521.5 | 660.1 | 828.7 | 743.2 | 688.2 | 761.3 | 346.9 | 514.3 | 762.7 | 185 | 284 | 357.4 | 637.7 | 638.8 | 728 | 612.8 | 666.5 | 307.9 | 453.7 | 421.7 | 335.5 | 354.7 | 522.7 | 351.3
1850.1 | 1611.1 | 567 | 226.8 | 265.1161 | 661.3 | 417.1 | 412.6 | 388.2 | 641 | 70.2 | 17.3 | 126.4 | 7.7 | 217.7 | 4.8 | 451.3 | 744.3 | 740.3 | 521.6 | 660.7 | 829.5 | 743.3 | 687.7 | 762.2 | 347.1 | 515.4 | 763.4 | 185.4 | 284.4 | 357.6 | 637.6 | 637.7 | 726.5 | 612.6 | 664.4 | 308.1 | 453.2 | 421.3 | 335.7 | 354.9 | 523.1 | 351.6
1851.1 | 1612.1 | 565.8 | 226.32 | 264.555 | 662.7 | 418.5 | 413.2 | 388.1 | 641.9 | 70.2 | 17.3 | 126.6 | 7.2 | 240.6 | 5.7 | 451.2 | 744.6 | 739.7 | 521.7 | 661.3 | 829.6 | 743.4 | 688.8 | 765.3 | 347.3 | 516.4 | 763.6 | 185.7 | 284.7 | 358.1 | 637.9 | 637.2 | 726 | 612.7 | 664 | 308.2 | 452.5 | 420.8 | 336 | 355.1 | 523.4 | 352
1852.1 | 1613.1 | 567.3 | 226.92 | 265.2564 | 653.3 | 421.6 | 413.7 | 387.6 | 643.2 | 70.3 | 17.3 | 126.8 | 6.5 | 256.4 | 6.2 | 451.1 | 744 | 746.8 | 521.8 | 661.9 | 829.4 | 743.4 | 688 | 770.7 | 347.6 | 517.5 | 764.6 | 186 | 285 | 358.4 | 637.9 | 637.4 | 725.7 | 612.8 | 662.7 | 308.3 | 452.1 | 420.4 | 336.2 | 355.4 | 523.7 | 352.3
1853.1 | 1614.1 | 567.7 | 227.08 | 265.4434 | 648.7 | 422.6 | 413.8 | 387.1 | 643.6 | 70.3 | 17.3 | 126.9 | 6.6 | 257.3 | 6.7 | 451.2 | 742 | 748.5 | 522 | 662.5 | 829.3 | 743.3 | 687.5 | 771.8 | 347.8 | 518.7 | 766.2 | 186.3 | 285.4 | 358.8 | 638.6 | 637.4 | 728.1 | 613.3 | 663.9 | 308.4 | 452.1 | 420.1 | 336.6 | 355.6 | 524 | 352.7
1854.1 | 1615.1 | 567.4 | 226.96 | 265.3032 | 649 | 422.6 | 413.4 | 386.9 | 640.5 | 70.4 | 17.3 | 127 | 7.1 | 249.8 | 7.5 | 451.3 | 742.4 | 741.5 | 522.2 | 663 | 829.7 | 743.3 | 686.9 | 774.1 | 348 | 519.8 | 767.3 | 186.7 | 285.7 | 359 | 638.4 | 636.2 | 722.8 | 613.3 | 663.2 | 308.6 | 452.5 | 419.9 | 337.1 | 355.9 | 524.3 | 353
1855.1 | 1616.1 | 566.1 | 226.44 | 264.6953 | 644.4 | 425.3 | 413 | 387.1 | 640.2 | 70.4 | 17.3 | 127 | 7.6 | 253 | 8.5 | 451.4 | 741.3 | 737.6 | 522.3 | 663.6 | 829.1 | 743.5 | 687 | 769.2 | 348.3 | 520.9 | 767.4 | 187 | 286 | 359.2 | 638.5 | 636.6 | 728.9 | 613.2 | 664.9 | 308.8 | 453.3 | 420.2 | 337.9 | 356.3 | 524.6 | 353.4
1856.1 | 1617.1 | 565.9 | 226.36 | 264.6018 | 642.5 | 425.5 | 412.6 | 388.2 | 640.9 | 70.4 | 17.3 | 127 | 7.2 | 272.8 | 7.5 | 451.5 | 744.2 | 734.4 | 522.4 | 664.1 | 829 | 743.5 | 686.9 | 765 | 348.5 | 522 | 767 | 187.3 | 286.3 | 359.4 | 638.9 | 636.9 | 723.9 | 613.3 | 666.9 | 309.1 | 454.5 | 420.7 | 338.7 | 356.8 | 525 | 353.8
1857.1 | 1618.1 | 566.6 | 226.64 | 264.9291 | 646 | 424.3 | 412.3 | 389.6 | 642 | 70.5 | 17.3 | 127.1 | 6.4 | 260.8 | 7.8 | 451.6 | 746.8 | 732.4 | 522.6 | 664.6 | 829.4 | 743.4 | 688.9 | 758.8 | 348.7 | 523.1 | 766.4 | 187.6 | 286.6 | 359.7 | 640.1 | 638 | 725.6 | 614 | 666.8 | 309.4 | 455 | 421.3 | 339.3 | 357.2 | 525.4 | 354.3
1858.1 | 1619.1 | 568 | 227.2 | 265.5837 | 649.4 | 422.9 | 412.4 | 390 | 647.5 | 70.6 | 17.3 | 127.2 | 6.6 | 251.8 | 8.2 | 451.6 | 745.3 | 733.8 | 522.7 | 665.2 | 829.4 | 743.6 | 690.9 | 755.9 | 349 | 524.2 | 765.5 | 188 | 287 | 360 | 641.1 | 639.5 | 731.3 | 614.8 | 666.8 | 309.8 | 455.3 | 421.7 | 339.8 | 357.6 | 525.7 | 354.7
1859.1 | 1620.1 | 566.2 | 226.48 | 264.7421 | 649 | 421.9 | 412.4 | 389.6 | 650.1 | 70.6 | 17.3 | 127.4 | 6 | 238.4 | 7.5 | 451.7 | 742.5 | 731.6 | 522.9 | 665.8 | 830 | 743.6 | 691.5 | 761.8 | 349.2 | 525.3 | 766.4 | 188.3 | 287.3 | 360.3 | 642 | 639.4 | 738.1 | 615.7 | 667.6 | 310.1 | 455.2 | 421.8 | 340.1 | 357.8 | 526.1 | 355.1
1860.1 | 1621.1 | 566 | 226.4 | 264.6486 | 649 | 421.1 | 412.3 | 389.3 | 648.5 | 70.7 | 17.2 | 127.7 | 6.4 | 217.5 | 8 | 451.6 | 739.1 | 733.7 | 523 | 666.3 | 830.8 | 743.5 | 689.7 | 760.9 | 349.5 | 526.5 | 767.9 | 188.6 | 287.6 | 360.7 | 642 | 638.4 | 733.2 | 616.5 | 667 | 310.5 | 455.1 | 422 | 340.5 | 358.1 | 526.5 | 355.4
1861.1 | 1622.1 | 565.7 | 226.28 | 264.5083 | 655 | 420.1 | 412.4 | 389.3 | 646 | 70.8 | 17.2 | 127.9 | 8.1 | 212.5 | 8.5 | 451.9 | 740.5 | 738.9 | 523.2 | 666.9 | 831.1 | 743.5 | 688.7 | 758.1 | 349.7 | 527.6 | 768.3 | 188.9 | 287.9 | 361.1 | 641.4 | 638.1 | 724.8 | 616.6 | 663.5 | 310.8 | 455.5 | 422.4 | 341 | 358.4 | 526.8 | 355.8
1862.1 | 1623.1 | 565.3 | 226.12 | 264.3213 | 654.2 | 421 | 413.1 | 389.5 | 644.2 | 70.9 | 17.2 | 128 | 7.8 | 215.8 | 8.2 | 452.1 | 740.4 | 739.4 | 523.5 | 667.4 | 830.7 | 743.5 | 688.5 | 756.1 | 350 | 528.7 | 768.2 | 189.3 | 288.2 | 361.2 | 641.3 | 637.3 | 718.8 | 616.6 | 661.7 | 311 | 455.8 | 422.3 | 341.5 | 358.7 | 527.1 | 356.2
1863.1 | 1624.1 | 566.3 | 226.52 | 264.7888 | 657.7 | 422.2 | 413.7 | 390.2 | 644.3 | 71 | 17.2 | 127.9 | 6.5 | 219.4 | 7.9 | 452.4 | 739.9 | 734.1 | 523.7 | 668 | 830 | 743.3 | 689.9 | 757.4 | 350.2 | 529.8 | 768.6 | 189.6 | 288.6 | 361.5 | 641.8 | 637.5 | 717.7 | 616.5 | 661 | 311.3 | 456.1 | 422.6 | 342.1 | 359.1 | 527.3 | 356.6
1864.1 | 1625.1 | 565.4 | 226.16 | 264.368 | 657.4 | 423.2 | 413.9 | 390.4 | 646.6 | 71.1 | 17.2 | 127.9 | 6.6 | 252.9 | 7.2 | 452.7 | 738.4 | 742.5 | 523.9 | 668.6 | 829.7 | 743.3 | 690.1 | 756.3 | 350.5 | 530.9 | 767.9 | 189.9 | 288.9 | 361.8 | 642.4 | 638.7 | 720.4 | 616.8 | 663 | 311.6 | 456.6 | 422.8 | 342.6 | 359.5 | 527.7 | 356.9
1865.1 | 1626.1 | 565.9 | 226.36 | 264.6018 | 654.2 | 422.1 | 414.7 | 390.2 | 645.5 | 71.1 | 17.2 | 128 | 6.3 | 223.4 | 6.9 | 452.6 | 740.4 | 746.2 | 524 | 669.1 | 829.4 | 743.5 | 689.3 | 757.5 | 350.7 | 532 | 767.9 | 190.2 | 289.2 | 362 | 643 | 639 | 717.8 | 617.3 | 662.8 | 311.9 | 457.3 | 423.6 | 343.3 | 360.1 | 528 | 357.3
1866.1 | 1627.1 | 566.2 | 226.48 | 264.7421 | 652.8 | 421.6 | 414.9 | 390.3 | 644.2 | 71.2 | 17.2 | 128.1 | 6 | 223.4 | 6.5 | 452.8 | 739.1 | 741.1 | 524.2 | 669.6 | 829.2 | 743.5 | 689.5 | 754.6 | 351 | 533.1 | 766.9 | 190.6 | 289.5 | 362.4 | 644.1 | 640.8 | 721 | 618 | 663.5 | 312.3 | 458.1 | 424.7 | 344 | 360.5 | 528.4 | 357.7
1867.1 | 1628.1 | 565.9 | 226.36 | 264.6018 | 648.7 | 421.6 | 413.9 | 391 | 645.8 | 71.3 | 17.2 | 128.2 | 7.2 | 261.8 | 7.6 | 452.9 | 740 | 733.6 | 524.4 | 670.2 | 829.4 | 743.5 | 689.4 | 748.7 | 351.2 | 534.2 | 765.8 | 190.9 | 289.8 | 362.6 | 646.1 | 643.1 | 717 | 619.3 | 663.5 | 312.7 | 459 | 425.2 | 344.7 | 361 | 528.8 | 358.1
1868.1 | 1629.1 | 565.8 | 226.32 | 264.555 | 646.2 | 421.2 | 413.9 | 391.7 | 646.7 | 71.4 | 17.2 | 128.3 | 7.5 | 227.9 | 7.7 | 452.9 | 740.2 | 721.7 | 524.5 | 670.7 | 829.3 | 743.4 | 689.9 | 747 | 351.5 | 535.3 | 765.5 | 191.2 | 290.1 | 363.1 | 646.9 | 644.6 | 717.1 | 620.4 | 664.5 | 313.2 | 460 | 426.1 | 345.5 | 361.4 | 529.3 | 358.6
1869.1 | 1630.1 | 565.5 | 226.2 | 264.4148 | 648.6 | 421 | 413.6 | 392.1 | 648.3 | 71.5 | 17.2 | 128.3 | 7 | 212.6 | 11 | 452.8 | 743.1 | 717.7 | 524.6 | 671.2 | 829.6 | 743.2 | 690.8 | 743.9 | 351.8 | 536.3 | 764.4 | 191.6 | 290.4 | 363.3 | 648 | 644.7 | 718.7 | 621.8 | 665.6 | 313.8 | 461.1 | 427.4 | 346.3 | 361.8 | 529.9 | 359
1870.1 | 1631.1 | 565.3 | 226.12 | 264.3213 | 657.7 | 420.3 | 413 | 393 | 649.3 | 71.5 | 17.2 | 128.4 | 6.9 | 228.6 | 11.7 | 452.9 | 744.2 | 715.3 | 524.7 | 671.7 | 829.4 | 743.2 | 691.8 | 738.9 | 352 | 537.4 | 763.5 | 191.9 | 290.7 | 363.7 | 649.1 | 646.6 | 717.9 | 623.4 | 667.6 | 314.4 | 462.2 | 429 | 347 | 362.3 | 530.4 | 359.5
1871.1 | 1632.1 | 565.3 | 226.12 | 264.3213 | 653.9 | 419 | 412.9 | 393.3 | 646.9 | 71.5 | 17.2 | 128.4 | 10.6 | 218.4 | 13.6 | 452.9 | 744.3 | 722.4 | 524.9 | 672.2 | 829.1 | 743.3 | 691.4 | 742.5 | 352.3 | 538.4 | 763.7 | 192.2 | 291.1 | 363.8 | 649.8 | 645.3 | 713.4 | 624.9 | 666.9 | 315.1 | 463.2 | 429.9 | 347.5 | 362.8 | 530.9 | 359.9
1872.1 | 1633.1 | 566.4 | 226.56 | 264.8356 | 652.1 | 417.2 | 413 | 393.8 | 646.3 | 71.5 | 17.2 | 128.5 | 10.4 | 205.6 | 13.9 | 452.9 | 742.9 | 728.2 | 524.9 | 672.8 | 829.9 | 743.2 | 690.2 | 748.3 | 352.5 | 539.4 | 764.1 | 192.5 | 291.4 | 364.1 | 649.8 | 643.7 | 711.2 | 626 | 663.9 | 315.7 | 463.6 | 429.5 | 347.9 | 363.1 | 531.3 | 360.4
1873.1 | 1634.1 | 566.9 | 226.76 | 265.0694 | 658.7 | 415.8 | 413.1 | 393.5 | 646.4 | 71.6 | 17.2 | 128.7 | 8.7 | 206.2 | 14.2 | 452.8 | 742 | 731.4 | 525 | 673.3 | 831.1 | 743.3 | 689.9 | 752.1 | 352.8 | 540.4 | 765.6 | 192.9 | 291.7 | 364.7 | 648.5 | 643.3 | 710.6 | 626 | 663.1 | 316.2 | 463.6 | 429.2 | 348.3 | 363.3 | 531.6 | 360.8
1874.1 | 1635.1 | 565.9 | 226.36 | 264.6018 | 659.3 | 416.5 | 413.5 | 393.3 | 644.7 | 71.6 | 17.2 | 128.8 | 8.3 | 225.8 | 11.4 | 452.9 | 742.4 | 731.9 | 525.1 | 673.8 | 831.8 | 743.3 | 689 | 752.8 | 353.1 | 541.4 | 766.4 | 193.2 | 292 | 364.8 | 647.8 | 642 | 713.7 | 625.6 | 664 | 316.6 | 463.7 | 429.2 | 348.8 | 363.6 | 532 | 361.2
1875.1 | 1636.1 | 566.3 | 226.52 | 264.7888 | 660.5 | 417.5 | 414.4 | 393.9 | 643.6 | 71.6 | 17.2 | 129 | 9.1 | 235.5 | 8.8 | 453 | 743.9 | 725.6 | 525.3 | 674.3 | 832.1 | 743 | 688 | 748.7 | 353.3 | 542.4 | 766.2 | 193.5 | 292.3 | 365 | 648.3 | 641.7 | 720.5 | 625.5 | 666.2 | 316.9 | 463.9 | 429.2 | 349.2 | 363.9 | 532.3 | 361.5
1876.1 | 1637.1 | 567.1 | 226.84 | 265.1629 | 660.7 | 417.1 | 414.9 | 394.3 | 643.6 | 71.7 | 17.2 | 129 | 8.3 | 218.7 | 8.1 | 453 | 744.9 | 726.9 | 525.4 | 674.8 | 832.6 | 743 | 687.8 | 748 | 353.6 | 543.4 | 766.3 | 193.8 | 292.7 | 365.4 | 648.9 | 641.1 | 717.5 | 625.9 | 666.9 | 317.3 | 463.8 | 429.2 | 349.7 | 364.2 | 532.6 | 361.9
1877.1 | 1638.1 | 567.2 | 226.88 | 265.2096 | 655 | 416.4 | 415.3 | 394.2 | 644.6 | 71.7 | 17.2 | 129 | 7.6 | 234.5 | 9 | 453 | 744.7 | 733.9 | 525.5 | 675.4 | 832.5 | 743 | 687.7 | 752.2 | 353.8 | 544.4 | 766.5 | 194.2 | 293 | 365.7 | 649.1 | 640.5 | 719 | 626.1 | 666.5 | 317.6 | 464 | 429.1 | 350.2 | 364.5 | 532.9 | 362.3
1878.1 | 1639.1 | 567 | 226.8 | 265.1161 | 653.2 | 416.2 | 415.3 | 393.9 | 646.1 | 71.8 | 17.2 | 129 | 7.7 | 246.3 | 13.1 | 453.1 | 742.9 | 735.2 | 525.6 | 676 | 832.8 | 743 | 689.1 | 756.7 | 354.1 | 545.4 | 767.1 | 194.5 | 293.3 | 366 | 649 | 640.9 | 724.2 | 626.2 | 666.8 | 317.9 | 464.1 | 428.7 | 350.6 | 364.8 | 533.3 | 362.7
1879.1 | 1640.1 | 566.7 | 226.68 | 264.9759 | 667.9 | 416.5 | 415.4 | 394.1 | 645.4 | 71.9 | 17.2 | 129.1 | 7.9 | 237.4 | 16.7 | 453.2 | 741.7 | 738.8 | 525.7 | 676.5 | 832.3 | 743.1 | 690.4 | 763.9 | 354.3 | 546.4 | 768.8 | 194.8 | 293.6 | 366.4 | 649.1 | 641.3 | 726.1 | 626.3 | 668.1 | 318.2 | 464.2 | 428.9 | 351.1 | 365.2 | 533.6 | 363
1880.1 | 1641.1 | 566.9 | 226.76 | 265.0694 | 681.6 | 417.2 | 415.4 | 395.1 | 646.9 | 71.9 | 17.2 | 129.1 | 6.4 | 248.2 | 16 | 453.5 | 743.4 | 738 | 525.9 | 677 | 831.2 | 743.1 | 690.3 | 755.5 | 354.6 | 547.3 | 768.1 | 195.1 | 293.9 | 366.7 | 649.7 | 644.3 | 723.8 | 626.6 | 668 | 318.5 | 464.9 | 429.6 | 351.8 | 365.8 | 534 | 363.4
1881.1 | 1642.1 | 566.5 | 226.6 | 264.8823 | 684.8 | 417.8 | 415.9 | 396.5 | 649.8 | 71.9 | 17.2 | 129.2 | 6.4 | 249.1 | 14.4 | 453.6 | 742.3 | 736.6 | 526 | 677.5 | 831.1 | 743.4 | 691.3 | 750.4 | 354.8 | 548.3 | 767.4 | 195.5 | 294.2 | 367 | 650.4 | 645.2 | 722.3 | 627.2 | 668.7 | 318.8 | 465.6 | 429.7 | 352.3 | 366.1 | 534.4 | 363.8
1882.1 | 1643.1 | 567.4 | 226.96 | 265.3032 | 676.6 | 417.5 | 416.2 | 397.5 | 648.5 | 71.9 | 17.1 | 129.2 | 6.7 | 237.2 | 12.6 | 453.7 | 743.4 | 744.6 | 526.2 | 678 | 831.5 | 743.5 | 690.8 | 747.4 | 355.1 | 549.2 | 766.9 | 195.8 | 294.5 | 367.2 | 650.4 | 644.2 | 719.3 | 627.3 | 665.8 | 319.2 | 465.9 | 429.7 | 352.7 | 366.4 | 534.9 | 364.2
1883.1 | 1644.1 | 567.5 | 227 | 265.3499 | 669.1 | 417 | 416.8 | 397.2 | 650.7 | 72 | 17.1 | 129.2 | 6.3 | 235.8 | 10.6 | 453.9 | 743.5 | 738.6 | 526.3 | 678.4 | 830.9 | 743.4 | 690.9 | 746.4 | 355.4 | 550.2 | 766.9 | 196.2 | 294.7 | 367.5 | 650.7 | 644.9 | 722.6 | 627.5 | 666.7 | 319.5 | 466.5 | 430.3 | 353.3 | 366.8 | 535.2 | 364.6
1884.1 | 1645.1 | 567.8 | 227.12 | 265.4902 | 667.5 | 418.4 | 417 | 397.6 | 653.3 | 72 | 17.1 | 129.3 | 5.8 | 236.6 | 10.9 | 454.2 | 744 | 734.9 | 526.5 | 678.9 | 828.2 | 743.5 | 691.2 | 739.6 | 355.6 | 551.1 | 765.8 | 196.5 | 295 | 367.8 | 650.9 | 647.1 | 720 | 627.6 | 666.9 | 319.9 | 467.5 | 431 | 354.1 | 367.3 | 535.6 | 365.1
1885.1 | 1646.1 | 568.5 | 227.4 | 265.8175 | 660.5 | 418.4 | 417.2 | 398.5 | 653.3 | 72 | 17.1 | 129.4 | 6.6 | 258.4 | 9.2 | 454.4 | 743.9 | 731.8 | 526.6 | 679.3 | 826.7 | 743.5 | 693.8 | 736.6 | 355.9 | 552.1 | 765.7 | 196.8 | 295.3 | 368.1 | 652 | 648 | 714.4 | 628.1 | 665.8 | 320.4 | 468.9 | 432.1 | 355 | 367.8 | 536 | 365.5
1886.1 | 1647.1 | 567.4 | 226.96 | 265.3032 | 661.2 | 419 | 417.4 | 399.5 | 653.8 | 72.2 | 17.1 | 129.3 | 6.8 | 246.2 | 7.1 | 454.8 | 742.5 | 734.9 | 526.9 | 679.8 | 826.6 | 743.6 | 694.4 | 735.3 | 356.2 | 553 | 765.4 | 197.1 | 295.6 | 368.3 | 653.1 | 647.7 | 712.1 | 628.7 | 664.5 | 320.8 | 469.7 | 432.5 | 355.5 | 368.2 | 536.3 | 366
1887.1 | 1648.1 | 567.5 | 227 | 265.3499 | 661.9 | 419.5 | 417.6 | 400.2 | 656 | 72.3 | 17.1 | 129.3 | 7.3 | 252.8 | 8.9 | 455.3 | 742.6 | 732.3 | 527.2 | 680.3 | 826.6 | 743.7 | 695.4 | 736.3 | 356.4 | 553.9 | 766.1 | 197.5 | 295.9 | 368.7 | 653.8 | 648.6 | 720.4 | 629.3 | 664.8 | 321.3 | 471.2 | 433.2 | 356.1 | 368.6 | 536.7 | 366.5
1888.1 | 1649.1 | 565.3 | 226.12 | 264.3213 | 667.6 | 420.1 | 418.1 | 400.7 | 656.9 | 72.4 | 17.1 | 129.4 | 7.8 | 232.4 | 11.5 | 455.6 | 742.3 | 739.1 | 527.4 | 680.8 | 826.1 | 743.8 | 695.4 | 733.5 | 356.7 | 554.8 | 766.2 | 197.8 | 296.2 | 368.9 | 654.6 | 649 | 719.6 | 630.1 | 666.1 | 321.7 | 472.3 | 434.2 | 356.7 | 369.1 | 537.1 | 367
1889.1 | 1650.1 | 566 | 226.4 | 264.6486 | 671.1 | 421.5 | 417.5 | 400.2 | 654.8 | 72.5 | 17.1 | 129.6 | 6.5 | 202.8 | 11.2 | 455.6 | 740.8 | 739.7 | 527.5 | 681.3 | 826.3 | 743.9 | 695.6 | 736 | 357 | 555.7 | 765.8 | 198.1 | 296.5 | 369.2 | 654.9 | 648.4 | 714.3 | 630.7 | 666.9 | 322.2 | 473.1 | 434.9 | 357.3 | 369.6 | 537.5 | 367.5
1890.1 | 1651.1 | 567.8 | 227.12 | 265.4902 | 671.1 | 422.4 | 417.2 | 399.7 | 656.6 | 72.6 | 17.1 | 129.6 | 7 | 212 | 9.7 | 455.5 | 739.8 | 738.5 | 527.6 | 681.8 | 825.8 | 743.9 | 696.2 | 738.7 | 357.2 | 556.6 | 766.4 | 198.5 | 296.8 | 369.5 | 654.6 | 650 | 723.2 | 630.9 | 669.3 | 322.6 | 474.2 | 435.2 | 357.8 | 370.1 | 537.9 | 367.9
1891.1 | 1652.1 | 565.1 | 226.04 | 264.2277 | 664.8 | 422.1 | 417.2 | 399.3 | 657.4 | 72.6 | 17.1 | 129.6 | 7.8 | 214.1 | 8.2 | 455.7 | 738.3 | 741.2 | 527.8 | 682.2 | 825.4 | 743.9 | 696.3 | 739.8 | 357.5 | 557.6 | 766.4 | 198.8 | 297.1 | 369.8 | 654.3 | 649.3 | 723.1 | 631.1 | 670.3 | 323.1 | 474.9 | 435.8 | 358.4 | 370.4 | 538.3 | 368.4
1892.1 | 1653.1 | 564.9 | 225.96 | 264.1342 | 656.2 | 421.9 | 417.9 | 399.7 | 656 | 72.7 | 17.1 | 129.7 | 7.1 | 220.6 | 8.2 | 455.8 | 737.2 | 743.7 | 527.9 | 682.7 | 826.5 | 743.9 | 696.4 | 744.2 | 357.8 | 558.5 | 766.5 | 199.1 | 297.4 | 370.1 | 654.5 | 649 | 717.8 | 631.5 | 667.3 | 323.5 | 475.8 | 435.9 | 358.9 | 370.6 | 538.7 | 368.8
1893.1 | 1654.1 | 565 | 226 | 264.181 | 660.6 | 422.2 | 418.5 | 400.1 | 651.8 | 72.7 | 17.1 | 129.8 | 7.1 | 215.9 | 8.2 | 456 | 737.5 | 747.5 | 528.1 | 683.2 | 827.7 | 743.9 | 698 | 746.1 | 358 | 559.4 | 766 | 199.5 | 297.7 | 370.4 | 654 | 647.2 | 714.5 | 631.3 | 665.1 | 323.8 | 476.6 | 435.8 | 359.3 | 370.9 | 539.2 | 369.2
1894.1 | 1655.1 | 565.5 | 226.2 | 264.4148 | 671.1 | 423.4 | 418.9 | 400.3 | 646.3 | 72.8 | 17.1 | 129.9 | 6.6 | 200.1 | 8.7 | 455.9 | 737.3 | 751.5 | 528.2 | 683.8 | 827.6 | 743.9 | 697.2 | 747.6 | 358.3 | 560.2 | 766.2 | 199.8 | 298 | 370.6 | 653.6 | 644.4 | 713.4 | 631 | 664.9 | 324 | 476.5 | 435.6 | 359.6 | 371.2 | 539.5 | 369.6
1895.1 | 1656.1 | 566.6 | 226.64 | 264.9291 | 669.1 | 425.7 | 419.1 | 399.9 | 644.4 | 72.8 | 17.1 | 130 | 6.5 | 215.1 | 8.5 | 455.9 | 735.8 | 747.8 | 528.3 | 684.3 | 827.2 | 744.1 | 697 | 747.5 | 358.6 | 561.1 | 765.4 | 200.1 | 298.3 | 370.9 | 653.8 | 643.9 | 714.9 | 630.8 | 667.4 | 324.1 | 476.7 | 435.5 | 360.1 | 371.6 | 539.8 | 370
1896.1 | 1657.1 | 568 | 227.2 | 265.5837 | 667 | 427.2 | 419 | 399.5 | 647.7 | 72.9 | 17.1 | 130 | 6.7 | 218.7 | 8.5 | 456 | 737.4 | 740.2 | 528.4 | 684.7 | 828.3 | 744.2 | 695.3 | 746.1 | 358.8 | 561.9 | 765.7 | 200.4 | 298.6 | 371 | 654 | 644.1 | 715.9 | 630.8 | 670.6 | 324.4 | 476.7 | 435.2 | 360.5 | 372 | 540.1 | 370.5
1897.1 | 1658.1 | 567.9 | 227.16 | 265.537 | 661.4 | 427.3 | 418.8 | 399.1 | 645.8 | 72.9 | 17.1 | 130 | 7.4 | 193.1 | 9.1 | 456.1 | 739.6 | 741 | 528.5 | 685.1 | 828.9 | 744.1 | 694.9 | 744.6 | 359.1 | 562.8 | 766.1 | 200.8 | 298.9 | 371.3 | 654.8 | 643.1 | 714.2 | 630.9 | 669.1 | 324.6 | 476.5 | 435 | 360.8 | 372.3 | 540.5 | 370.9
1898.1 | 1659.1 | 567.1 | 226.84 | 265.1629 | 659.1 | 426.7 | 418.7 | 398.7 | 644.8 | 73 | 17.1 | 130.1 | 7.1 | 215.9 | 9.4 | 456.1 | 740.9 | 736.5 | 528.6 | 685.6 | 829.2 | 744.2 | 695.1 | 746.6 | 359.4 | 563.6 | 766.5 | 201.1 | 299.2 | 371.7 | 655.1 | 642.3 | 718.9 | 630.9 | 668.9 | 324.9 | 476.8 | 434.6 | 361.2 | 372.7 | 540.8 | 371.3
1899.1 | 1660.1 | 567.3 | 226.92 | 265.2564 | 658.6 | 427.1 | 418.8 | 398.7 | 644.3 | 73.1 | 17.1 | 130.1 | 6.4 | 192.6 | 10 | 456.1 | 741.9 | 734.6 | 528.8 | 686.1 | 829.9 | 744.2 | 693.5 | 747 | 359.6 | 564.5 | 767.1 | 201.4 | 299.5 | 371.8 | 655.2 | 642 | 719.5 | 630.9 | 668.6 | 325.2 | 476.7 | 434.4 | 361.5 | 372.9 | 541.1 | 371.7
1900.1 | 1661.1 | 564.2 | 225.68 | 263.8069 | 662.4 | 428 | 419.4 | 398.6 | 644.6 | 73.2 | 17.1 | 130.3 | 6 | 205.9 | 10.3 | 456.2 | 741.7 | 738.1 | 528.9 | 686.7 | 830.1 | 744.2 | 692.9 | 756.9 | 359.9 | 565.3 | 768.4 | 201.7 | 299.8 | 372.2 | 655.6 | 642.1 | 722.9 | 631 | 669.5 | 325.5 | 476.6 | 434 | 361.9 | 373.1 | 541.4 | 372.1
1901.1 | 1662.1 | 566.1 | 226.44 | 264.6953 | 661.1 | 427.1 | 419.2 | 398.5 | 645.9 | 73.3 | 17.1 | 130.4 | 5.7 | 194.1 | 11.4 | 456.3 | 740 | 739.3 | 529 | 687.1 | 830.2 | 744.2 | 692.1 | 759.8 | 360.2 | 566.2 | 768.5 | 202.1 | 300 | 372.6 | 655.3 | 641.3 | 722.2 | 631 | 669.7 | 325.8 | 476.2 | 433.7 | 362.2 | 373.3 | 541.8 | 372.4
1902.1 | 1663.1 | 566 | 226.4 | 264.6486 | 664.4 | 427.4 | 419.5 | 398.4 | 645.6 | 73.4 | 17.1 | 130.5 | 7 | 201.6 | 12.2 | 456.4 | 740.1 | 745 | 529.2 | 687.7 | 830.1 | 744.1 | 691.7 | 763.3 | 360.5 | 567 | 769.1 | 202.4 | 300.3 | 372.8 | 654.5 | 640.2 | 720.2 | 630.4 | 669.2 | 326 | 475.9 | 433.4 | 362.4 | 373.6 | 542.1 | 372.8
1903.1 | 1664.1 | 566 | 226.4 | 264.6486 | 666.3 | 429.9 | 419.7 | 398.2 | 646.1 | 73.4 | 17.1 | 130.6 | 7.6 | 208.6 | 10.1 | 456.6 | 740.4 | 752.9 | 529.4 | 688.2 | 829.9 | 744.2 | 691.7 | 766.7 | 360.7 | 567.9 | 769.9 | 202.7 | 300.6 | 373.1 | 654.4 | 641 | 719.4 | 630.2 | 668.1 | 326.2 | 475.6 | 433.2 | 362.8 | 373.9 | 542.4 | 373.2
1904.1 | 1665.1 | 566 | 226.4 | 264.6486 | 666.4 | 431 | 420 | 398.7 | 646.5 | 73.5 | 17.1 | 130.8 | 9.3 | 221.6 | 8.6 | 456.7 | 740.7 | 756.5 | 529.5 | 688.6 | 829.8 | 744.4 | 691.3 | 770.3 | 361 | 568.7 | 770.7 | 203 | 300.9 | 373.4 | 654.8 | 640.8 | 720.8 | 630 | 668.4 | 326.4 | 475.5 | 432.7 | 363.3 | 374 | 542.7 | 373.6
1905.1 | 1666.1 | 566.3 | 226.52 | 264.7888 | 659.4 | 430.9 | 420.7 | 399.3 | 645.5 | 73.5 | 17.1 | 131 | 9.6 | 200.1 | 7.6 | 456.9 | 740 | 754.4 | 529.7 | 689.1 | 830.4 | 744.3 | 690.7 | 772.1 | 361.3 | 569.5 | 771.5 | 203.4 | 301.2 | 373.8 | 654.6 | 640.2 | 717.3 | 629.5 | 669.2 | 326.6 | 475.4 | 432 | 363.6 | 374.2 | 543 | 374
1906.1 | 1667.1 | 565.7 | 226.28 | 264.5083 | 651.6 | 433.7 | 421.5 | 399.2 | 647.1 | 73.6 | 17.1 | 131.3 | 8.6 | 222.4 | 6.7 | 456.9 | 739.7 | 754.4 | 529.8 | 689.5 | 831.1 | 744.4 | 689.6 | 773.6 | 361.6 | 570.4 | 771.8 | 203.7 | 301.4 | 374.2 | 654.2 | 640.8 | 718.1 | 628.9 | 670.1 | 326.7 | 475.4 | 431.4 | 363.9 | 374.4 | 543.3 | 374.4
1907.1 | 1668.1 | 566 | 226.4 | 264.6486 | 647.2 | 435.8 | 421.7 | 399.1 | 649.2 | 73.6 | 17.1 | 131.5 | 8.2 | 247 | 6.7 | 456.9 | 739.2 | 757.7 | 529.9 | 690 | 831.6 | 744.2 | 689 | 775.7 | 361.8 | 571.2 | 772.2 | 204 | 301.7 | 374.4 | 654.2 | 640.8 | 717.3 | 628.7 | 670.5 | 326.8 | 475.5 | 431 | 364.3 | 374.6 | 543.5 | 374.8
1908.1 | 1669.1 | 566.7 | 226.68 | 264.9759 | 645.6 | 437.4 | 422.1 | 399.4 | 648.3 | 73.6 | 17 | 131.6 | 8.2 | 254.6 | 6.6 | 457.4 | 737.9 | 757.3 | 530.1 | 690.4 | 832.4 | 744.1 | 688.9 | 772.7 | 362.1 | 572 | 771.9 | 204.4 | 302 | 374.8 | 654.1 | 639.6 | 719.6 | 628.3 | 671.1 | 326.9 | 475.1 | 430.4 | 364.5 | 374.6 | 543.8 | 375.1
1909.1 | 1670.1 | 566.9 | 226.76 | 265.0694 | 645.4 | 438.3 | 423.2 | 399.5 | 646.2 | 73.6 | 17 | 131.7 | 8.8 | 224.7 | 7.3 | 457.6 | 737.7 | 751.9 | 530.3 | 690.8 | 833.2 | 744.1 | 689.9 | 765.4 | 362.4 | 572.8 | 771.1 | 204.7 | 302.3 | 375.2 | 654 | 638.5 | 719.2 | 628.1 | 670.9 | 326.9 | 474.7 | 429.7 | 364.7 | 374.7 | 544.1 | 375.5
1910.1 | 1671.1 | 566.1 | 226.44 | 264.6953 | 648.9 | 438.4 | 423.7 | 399.4 | 648.2 | 73.7 | 17 | 131.9 | 9.8 | 232.1 | 6.8 | 457.6 | 736.4 | 751.1 | 530.5 | 691.2 | 833.4 | 744 | 691.9 | 764 | 362.7 | 573.6 | 771 | 205 | 302.6 | 375.4 | 654.4 | 639.5 | 720.2 | 628.1 | 670 | 326.9 | 474.1 | 429.3 | 364.9 | 374.9 | 544.3 | 375.9
1911.1 | 1672.1 | 565.6 | 226.24 | 264.4615 | 656.6 | 438 | 423.2 | 399.4 | 649 | 73.7 | 17 | 132.1 | 9.1 | 221.9 | 7.6 | 457.7 | 736.1 | 760.9 | 530.6 | 691.6 | 832.9 | 743.9 | 695.5 | 764.6 | 362.9 | 574.4 | 771.1 | 205.3 | 302.9 | 375.7 | 654.8 | 639.5 | 715.2 | 628.4 | 668.6 | 326.9 | 473.8 | 429.2 | 365.2 | 375.2 | 544.5 | 376.2
1912.1 | 1673.1 | 566 | 226.4 | 264.6486 | 659.8 | 439.3 | 422.5 | 399.4 | 646.5 | 73.7 | 17 | 132.3 | 8.2 | 219.9 | 7.6 | 457.8 | 735.6 | 766.1 | 530.8 | 692.1 | 832.3 | 743.9 | 695.8 | 768 | 363.3 | 575.2 | 771.4 | 205.7 | 303.2 | 376.1 | 655.3 | 638.3 | 719 | 628.6 | 669.1 | 327 | 473.4 | 429.1 | 365.5 | 375.4 | 544.8 | 376.6
1913.1 | 1674.1 | 566.3 | 226.52 | 264.7888 | 654.6 | 440.1 | 422.3 | 399.3 | 647 | 73.8 | 17 | 132.4 | 7.1 | 191.4 | 8.5 | 457.9 | 735.4 | 772.8 | 531 | 692.5 | 832.1 | 744 | 694.8 | 770 | 363.7 | 576 | 772 | 206 | 303.5 | 376.3 | 655.5 | 637.9 | 722.9 | 628.8 | 670.9 | 327.2 | 472.7 | 428.9 | 365.9 | 375.7 | 545.1 | 376.9
1914.1 | 1675.1 | 566.9 | 226.76 | 265.0694 | 656.2 | 440 | 422.2 | 399.4 | 645.6 | 73.9 | 17 | 132.6 | 6.4 | 198 | 9.7 | 458.1 | 734.1 | 774 | 531.2 | 692.9 | 832.5 | 744.1 | 694 | 769.2 | 364 | 576.8 | 771.5 | 206.3 | 303.8 | 376.5 | 655.2 | 636.4 | 719.8 | 628.8 | 671.2 | 327.3 | 472.5 | 429 | 366.1 | 376 | 545.4 | 377.3
1915.1 | 1676.1 | 566.4 | 226.56 | 264.8356 | 654.6 | 438.3 | 422.3 | 399 | 641 | 73.9 | 17 | 132.7 | 7.2 | 204 | 13.3 | 458 | 733.8 | 768.9 | 531.3 | 693.4 | 832.7 | 744.3 | 691.7 | 768.6 | 364.4 | 577.5 | 771.1 | 206.7 | 304.1 | 376.7 | 655 | 635.3 | 714.2 | 628.7 | 669.7 | 327.5 | 472.4 | 429 | 366.5 | 376.2 | 545.6 | 377.6
1916.1 | 1677.1 | 567.1 | 226.84 | 265.1629 | 652.3 | 437.5 | 422.6 | 398.2 | 640.2 | 74 | 17 | 133 | 7.3 | 213.3 | 13.4 | 458 | 733.7 | 772.3 | 531.5 | 693.9 | 832.8 | 744.3 | 691.1 | 773.8 | 364.7 | 578.3 | 772.2 | 207 | 304.4 | 377.3 | 655.4 | 635.3 | 718.3 | 628.7 | 671.7 | 327.7 | 471.8 | 428.8 | 366.7 | 376.3 | 545.9 | 378
1917.1 | 1678.1 | 566.1 | 226.44 | 264.6953 | 655.2 | 437.4 | 422.8 | 397.5 | 642.1 | 74 | 17 | 133.2 | 7.3 | 207.8 | 11.1 | 458.3 | 733.1 | 769.8 | 531.8 | 694.2 | 833.3 | 744.3 | 691 | 772.5 | 365 | 579.1 | 773.2 | 207.3 | 304.7 | 377.6 | 655.2 | 636.3 | 716.2 | 628.6 | 672.7 | 327.8 | 471.5 | 428.6 | 367 | 376.6 | 546.2 | 378.3
1918.1 | 1679.1 | 565.9 | 226.36 | 264.6018 | 654.7 | 441.7 | 423.5 | 397.4 | 640.6 | 74.1 | 17 | 133.3 | 7.4 | 214 | 11.4 | 458.7 | 731.9 | 763.4 | 532.1 | 694.6 | 834.1 | 744.1 | 689 | 768 | 365.4 | 579.8 | 773.1 | 207.6 | 305 | 377.5 | 655 | 635.2 | 712.7 | 628.3 | 672.7 | 328 | 471.4 | 428.8 | 367.3 | 377 | 546.5 | 378.6
1919.1 | 1680.1 | 565.8 | 226.32 | 264.555 | 656.1 | 443.5 | 423.7 | 397.9 | 639.9 | 74.2 | 17 | 133.4 | 7.7 | 207.4 | 13.3 | 458.8 | 732.5 | 765 | 532.2 | 695 | 834 | 744 | 688.6 | 765.1 | 365.7 | 580.6 | 772.7 | 208 | 305.3 | 377.7 | 655.3 | 634.9 | 713.6 | 628.1 | 671.7 | 328.2 | 471.6 | 428.9 | 367.8 | 377.1 | 546.7 | 378.9
1920.1 | 1681.1 | 565.8 | 226.32 | 264.555 | 656.7 | 442.1 | 422.7 | 398.1 | 641.7 | 74.3 | 17 | 133.5 | 7.4 | 209.2 | 16.3 | 459.1 | 733.1 | 761.7 | 532.4 | 695.4 | 832.9 | 743.9 | 691.5 | 761.6 | 366 | 581.4 | 773 | 208.3 | 305.6 | 377.9 | 655.8 | 635.9 | 717.9 | 628.3 | 672.8 | 328.4 | 471.9 | 429.4 | 368.3 | 377.4 | 547 | 379.3
1921.1 | 1682.1 | 566.5 | 226.6 | 264.8823 | 662.9 | 441.1 | 422.1 | 398.8 | 641.5 | 74.4 | 17 | 133.5 | 6.2 | 213.5 | 14.6 | 459 | 733.3 | 758.8 | 532.5 | 695.7 | 832.9 | 743.9 | 694.7 | 760.4 | 366.4 | 582.1 | 773.5 | 208.6 | 305.9 | 378.2 | 655.8 | 635.9 | 720.8 | 628.3 | 674.1 | 328.7 | 472.3 | 429.2 | 368.8 | 377.6 | 547.3 | 379.7
1922.1 | 1683.1 | 566.7 | 226.68 | 264.9759 | 666.4 | 440.8 | 421.3 | 399.2 | 638.7 | 74.4 | 17 | 133.5 | 6.3 | 236.9 | 11.6 | 459 | 733.9 | 757.8 | 532.7 | 696.2 | 833.3 | 743.9 | 694.5 | 758.6 | 366.7 | 582.9 | 773.2 | 209 | 306.2 | 378.4 | 655.6 | 634.7 | 716.4 | 628.3 | 671.7 | 329 | 472.9 | 429.3 | 369.2 | 377.8 | 547.6 | 380
1923.1 | 1684.1 | 566 | 226.4 | 264.6486 | 664.8 | 440.8 | 420.5 | 399.2 | 636 | 74.5 | 17 | 133.5 | 6.7 | 210 | 13.2 | 459 | 733.9 | 759.7 | 532.8 | 696.6 | 833.4 | 743.8 | 693.6 | 759.5 | 367.1 | 583.6 | 773.8 | 209.3 | 306.5 | 378.8 | 655.5 | 633.9 | 714.1 | 628.1 | 670.6 | 329.3 | 473.1 | 429.6 | 369.5 | 378.3 | 547.8 | 380.4
1924.1 | 1685.1 | 565.2 | 226.08 | 264.2745 | 662.9 | 441.1 | 420.4 | 399.2 | 635.8 | 74.5 | 17 | 133.6 | 6.5 | 214.6 | 14.5 | 458.9 | 734.5 | 757.6 | 533 | 697 | 833.9 | 743.8 | 692.8 | 762.7 | 367.4 | 584.4 | 774.2 | 209.6 | 306.7 | 379.1 | 656 | 633.9 | 715.2 | 628.1 | 670.3 | 329.5 | 473.2 | 429.8 | 369.9 | 378.5 | 548.1 | 380.8
1925.1 | 1686.1 | 567.6 | 227.04 | 265.3967 | 658.5 | 439.3 | 420.3 | 399.6 | 638.9 | 74.6 | 17 | 133.7 | 7 | 221.5 | 14.3 | 458.8 | 734.4 | 753.7 | 533.1 | 697.4 | 833.3 | 743.7 | 692.8 | 759.2 | 367.8 | 585.1 | 773.4 | 210 | 307.1 | 379.4 | 656.8 | 636.2 | 715.6 | 628.5 | 672.3 | 329.9 | 473.7 | 430.6 | 370.4 | 378.9 | 548.4 | 381.1
1926.1 | 1687.1 | 568.2 | 227.28 | 265.6772 | 652.2 | 437.2 | 420.6 | 400.7 | 640.7 | 74.8 | 17 | 133.7 | 7.2 | 195.6 | 14.3 | 458.9 | 735.4 | 748.3 | 533.2 | 697.7 | 831.7 | 743.7 | 695.7 | 756.8 | 368.1 | 585.9 | 772.8 | 210.3 | 307.4 | 379.6 | 658.2 | 638.4 | 712 | 629.4 | 671.9 | 330.2 | 474.8 | 431.2 | 371 | 379.3 | 548.7 | 381.5
1927.1 | 1688.1 | 566.7 | 226.68 | 264.9759 | 647.3 | 436.1 | 421.2 | 401.9 | 640.6 | 74.9 | 17 | 133.8 | 7.9 | 201.3 | 13.4 | 459 | 735.2 | 739.1 | 533.3 | 698.1 | 830.7 | 743.7 | 702.5 | 752.4 | 368.5 | 586.6 | 772.5 | 210.6 | 307.7 | 379.8 | 659.1 | 638.6 | 707.1 | 630.2 | 670.2 | 330.6 | 475.6 | 431.7 | 371.5 | 379.6 | 549 | 381.9
1928.1 | 1689.1 | 566.2 | 226.48 | 264.7421 | 638.5 | 436.5 | 421.1 | 403.2 | 639.3 | 75 | 17 | 133.8 | 7.6 | 202.5 | 13.6 | 459.1 | 735.1 | 730.6 | 533.5 | 698.4 | 830 | 743.7 | 705.3 | 742.7 | 368.8 | 587.3 | 770.5 | 210.9 | 308 | 380.1 | 660.3 | 639.8 | 700.8 | 631.4 | 668.3 | 331.1 | 476.8 | 432.1 | 372.1 | 380 | 549.4 | 382.3
1929.1 | 1690.1 | 566.9 | 226.76 | 265.0694 | 628.5 | 436.1 | 421 | 403.8 | 642.2 | 75.1 | 17 | 133.8 | 5.2 | 208.3 | 16.8 | 459.2 | 734.4 | 728.1 | 533.6 | 698.7 | 830 | 743.5 | 705 | 737.1 | 369.2 | 588.1 | 770.2 | 211.3 | 308.3 | 380.4 | 661.2 | 640.1 | 704.6 | 632.6 | 668.5 | 331.6 | 478.3 | 432.9 | 372.7 | 380.2 | 549.7 | 382.8
1930.1 | 1691.1 | 566.7 | 226.68 | 264.9759 | 624.8 | 435.5 | 420.6 | 404.4 | 642.3 | 75.1 | 17 | 133.7 | 6.2 | 201.5 | 16.1 | 459.1 | 734.2 | 732.7 | 533.7 | 699.2 | 830.9 | 743.2 | 706.8 | 738.4 | 369.5 | 588.8 | 771 | 211.6 | 308.6 | 380.6 | 661.9 | 639.2 | 706.9 | 633.8 | 671 | 331.9 | 479.1 | 433.9 | 373.2 | 380.5 | 550 | 383.2
1931.1 | 1692.1 | 566.5 | 226.6 | 264.8823 | 626.6 | 433.8 | 420.4 | 404.5 | 640.4 | 75.2 | 16.9 | 133.6 | 7.4 | 205.3 | 15.7 | 459.2 | 733.5 | 733.2 | 533.8 | 699.5 | 832.4 | 743 | 704.7 | 741.7 | 369.9 | 589.5 | 771 | 211.9 | 308.9 | 380.9 | 661.8 | 639.4 | 711.6 | 634.4 | 671.9 | 332.3 | 479.2 | 434.1 | 373.5 | 380.8 | 550.2 | 383.6
1932.1 | 1693.1 | 567.5 | 227 | 265.3499 | 635.2 | 432.4 | 420.2 | 404.2 | 638.9 | 75.2 | 16.9 | 133.6 | 6.2 | 201 | 15.7 | 459.3 | 732.3 | 731.5 | 534 | 699.8 | 833.1 | 742.9 | 702.8 | 737 | 370.2 | 590.2 | 770.2 | 212.3 | 309.2 | 381.4 | 660.9 | 638.3 | 714 | 634.4 | 670.2 | 332.6 | 478.9 | 433.7 | 373.7 | 380.9 | 550.5 | 384
1933.1 | 1694.1 | 567.4 | 226.96 | 265.3032 | 642.1 | 431.7 | 420.7 | 403.6 | 637.6 | 75.2 | 16.9 | 133.5 | 6.5 | 190.4 | 12.3 | 459.3 | 731.8 | 731.4 | 534 | 700.2 | 832.8 | 742.6 | 701.7 | 730.9 | 370.6 | 591 | 769.8 | 212.6 | 309.5 | 381.5 | 660.5 | 636.4 | 705.1 | 634.5 | 666.1 | 332.8 | 478.6 | 433 | 373.9 | 381 | 550.7 | 384.3
1934.1 | 1695.1 | 567.2 | 226.88 | 265.2096 | 639.2 | 431.7 | 421.1 | 402.9 | 637.4 | 75.3 | 16.9 | 133.5 | 6.4 | 212.2 | 10.7 | 459.3 | 733 | 732.4 | 534.1 | 700.5 | 833.3 | 742.4 | 700.9 | 733.7 | 371 | 591.7 | 770.4 | 212.9 | 309.8 | 381.6 | 661.5 | 636.3 | 693.4 | 635.1 | 664.1 | 332.9 | 478.9 | 433.3 | 374.4 | 381.3 | 550.9 | 384.6
1935.1 | 1696.1 | 564.7 | 225.88 | 264.0407 | 635.7 | 431 | 421.3 | 402.9 | 634.8 | 75.4 | 16.9 | 133.5 | 7.4 | 201.2 | 14.4 | 459.2 | 733.3 | 733.1 | 534.2 | 700.9 | 833.6 | 742.4 | 701 | 740.4 | 371.3 | 592.4 | 770.5 | 213.3 | 310.1 | 381.8 | 662.8 | 636.3 | 693.9 | 635.9 | 665.8 | 333.1 | 478.9 | 433.1 | 374.7 | 381.5 | 551.2 | 385
1936.1 | 1697.1 | 564.4 | 225.76 | 263.9004 | 634.2 | 429.7 | 421.6 | 403 | 636.9 | 75.4 | 16.9 | 133.6 | 7.3 | 207.1 | 18.1 | 459.2 | 731.6 | 736.8 | 534.3 | 701.3 | 834.4 | 742.5 | 700.4 | 747.1 | 371.7 | 593.2 | 771.2 | 213.6 | 310.4 | 382.1 | 662.6 | 635.7 | 697 | 636.3 | 667.3 | 333.3 | 478.5 | 432.9 | 374.9 | 381.7 | 551.6 | 385.4
1937.1 | 1698.1 | 566.2 | 226.48 | 264.7421 | 633.7 | 429.6 | 421.8 | 403.2 | 639.7 | 75.5 | 16.9 | 133.7 | 7.3 | 204.3 | 19.8 | 459.4 | 731.6 | 740.5 | 534.5 | 701.6 | 835.1 | 742.5 | 699.4 | 748.4 | 372 | 594 | 771.6 | 213.9 | 310.7 | 382.6 | 662.2 | 634.7 | 698.5 | 636.4 | 666.5 | 333.4 | 478.3 | 433.1 | 375.1 | 381.9 | 551.7 | 385.7
1938.1 | 1699.1 | 565.8 | 226.32 | 264.555 | 632.6 | 432.7 | 422.1 | 403 | 636.5 | 75.5 | 16.9 | 133.8 | 7.3 | 207.5 | 19.1 | 459.5 | 731.6 | 742.7 | 534.6 | 702 | 835.5 | 742.5 | 699.5 | 744.6 | 372.4 | 594.7 | 771.2 | 214.3 | 311.1 | 382.7 | 662.4 | 633.2 | 696.2 | 636.6 | 666.2 | 333.6 | 478.6 | 433.8 | 375.4 | 382.3 | 551.9 | 386
1939.1 | 1700.1 | 563.6 | 225.44 | 263.5264 | 631.7 | 434.1 | 422.6 | 403.4 | 634.8 | 75.5 | 16.9 | 134 | 8.4 | 204.3 | 18.5 | 459.4 | 730 | 739.6 | 534.8 | 702.3 | 835.4 | 742.6 | 702.2 | 744 | 372.7 | 595.5 | 770.3 | 214.6 | 311.4 | 383.2 | 663.9 | 633.7 | 699.8 | 637.6 | 666.1 | 333.9 | 478 | 433.9 | 375.6 | 382.4 | 552.2 | 386.4
1940.1 | 1701.1 | 564 | 225.6 | 263.7134 | 630.1 | 434.4 | 423.7 | 403 | 641.8 | 75.5 | 16.9 | 134.2 | 8.1 | 203.3 | 18.2 | 459.4 | 729.2 | 739.7 | 534.8 | 702.7 | 835.6 | 742.5 | 700.4 | 749.7 | 373.1 | 596.2 | 770.3 | 214.9 | 311.7 | 384 | 663.8 | 635.7 | 701.2 | 638.3 | 666.4 | 334.1 | 477.7 | 433.3 | 375.7 | 382.4 | 552.4 | 386.7
1941.1 | 1702.1 | 565.5 | 226.2 | 264.4148 | 634 | 433.3 | 426.2 | 402.1 | 644.6 | 75.5 | 16.9 | 134.4 | 7.9 | 212.2 | 16.2 | 459.4 | 729.9 | 747.3 | 534.9 | 703.1 | 835.9 | 742.4 | 698.9 | 755.4 | 373.5 | 597 | 771.6 | 215.3 | 312 | 384.2 | 664.3 | 636.4 | 700.5 | 638.9 | 665.2 | 334.2 | 477.9 | 433 | 376 | 382.6 | 552.6 | 387
1942.1 | 1703.1 | 566.3 | 226.52 | 264.7888 | 632.2 | 432.4 | 427.4 | 401.8 | 647.5 | 75.6 | 16.9 | 134.7 | 7.7 | 208.6 | 14.3 | 459.8 | 729.3 | 746.7 | 535.2 | 703.4 | 836.3 | 742.3 | 701.6 | 752.1 | 373.9 | 597.8 | 771.6 | 215.6 | 312.3 | 384.3 | 664.3 | 636.8 | 701.5 | 639.1 | 665.2 | 334.3 | 478.1 | 433.1 | 376.4 | 382.9 | 552.8 | 387.3
1943.1 | 1704.1 | 567.7 | 227.08 | 265.4434 | 636.3 | 433.8 | 427.1 | 402.2 | 645 | 75.7 | 16.9 | 134.9 | 9.3 | 204.9 | 13.6 | 459.9 | 728.1 | 747.2 | 535.3 | 703.7 | 836.5 | 742.3 | 700.4 | 747.4 | 374.3 | 598.5 | 771.1 | 215.9 | 312.6 | 384.4 | 664.4 | 634.9 | 697.5 | 639 | 663.8 | 334.5 | 478.4 | 433.6 | 376.7 | 383.1 | 553 | 387.7
1944.1 | 1705.1 | 565.2 | 226.08 | 264.2745 | 634.5 | 436.7 | 425.9 | 403 | 639.4 | 75.7 | 16.9 | 135 | 9.9 | 247.7 | 11.2 | 460.1 | 728.1 | 744.4 | 535.5 | 704 | 836.6 | 742.2 | 699.3 | 747.2 | 374.7 | 599.3 | 771.2 | 216.3 | 312.9 | 384.5 | 665 | 633.4 | 695.5 | 639 | 663.5 | 334.6 | 478.6 | 433.8 | 377 | 383.4 | 553.2 | 388
1945.1 | 1706.1 | 565.3 | 226.12 | 264.3213 | 633.1 | 439.7 | 425 | 403.4 | 638.4 | 75.8 | 16.9 | 135 | 9.2 | 255.9 | 9.2 | 460.1 | 729.2 | 749 | 535.7 | 704.4 | 836.4 | 742.2 | 698.3 | 749.3 | 375.1 | 600 | 771.4 | 216.6 | 313.2 | 384.8 | 665.9 | 633.4 | 702.8 | 639.6 | 666.2 | 334.9 | 478.9 | 433.8 | 377.4 | 383.7 | 553.4 | 388.4
1946.1 | 1707.1 | 565.9 | 226.36 | 264.6018 | 632.6 | 439.1 | 424.3 | 403.4 | 641.4 | 75.9 | 16.9 | 135.2 | 9.2 | 230.4 | 7.8 | 460.2 | 729.4 | 753.7 | 535.8 | 704.8 | 835.9 | 742.4 | 696.5 | 758 | 375.5 | 600.8 | 772 | 216.9 | 313.4 | 385 | 666.3 | 634.3 | 704.6 | 640.1 | 668.3 | 335.1 | 479.3 | 433.6 | 377.8 | 384 | 553.6 | 388.8
1947.1 | 1708.1 | 565.7 | 226.28 | 264.5083 | 643.2 | 438.7 | 423.8 | 403.1 | 644.1 | 75.9 | 16.9 | 135.5 | 8.3 | 235 | 8.7 | 460.1 | 729.4 | 755.5 | 535.9 | 705.2 | 835.4 | 742.8 | 694.8 | 762.8 | 375.9 | 601.5 | 772.6 | 217.3 | 313.7 | 385.4 | 666.1 | 634.9 | 711.1 | 640.5 | 670.6 | 335.4 | 479.8 | 433.3 | 378.1 | 384.2 | 553.9 | 389.1
1948.1 | 1709.1 | 566.8 | 226.72 | 265.0226 | 650.2 | 437.6 | 424.4 | 402.6 | 643.2 | 76 | 16.9 | 135.7 | 8.7 | 215.5 | 9.7 | 460.2 | 729.2 | 760.4 | 535.9 | 705.6 | 835 | 743 | 693.3 | 766.3 | 376.3 | 602.2 | 773 | 217.6 | 314 | 385.6 | 666 | 634.5 | 713.9 | 640.9 | 672.4 | 335.6 | 480.1 | 433.4 | 378.4 | 384.3 | 554.2 | 389.5
1949.1 | 1710.1 | 566.5 | 226.6 | 264.8823 | 648.4 | 437.4 | 424.8 | 402.5 | 644.3 | 76 | 16.9 | 135.9 | 8.5 | 239.6 | 8.9 | 460.4 | 729.1 | 763 | 536.1 | 706.1 | 834.3 | 743.2 | 692.2 | 771.3 | 376.6 | 603 | 773.1 | 217.9 | 314.4 | 385.9 | 665.7 | 634.9 | 714.9 | 641 | 673.8 | 335.9 | 480 | 433.9 | 378.6 | 384.6 | 554.4 | 389.8
1950.1 | 1711.1 | 566.6 | 226.64 | 264.9291 | 648.3 | 439.3 | 425 | 402.2 | 644.3 | 76 | 16.9 | 136 | 8.2 | 208.3 | 12.2 | 460.6 | 728.6 | 767.3 | 536.4 | 706.5 | 834 | 743.4 | 691.7 | 778 | 377 | 603.7 | 773.9 | 218.3 | 314.7 | 386.1 | 665.9 | 634.2 | 718.4 | 641.3 | 675.6 | 336.1 | 480.7 | 434.3 | 379 | 384.8 | 554.7 | 390.1
1951.1 | 1712.1 | 565.7 | 226.28 | 264.5083 | 648.4 | 439.6 | 424.7 | 402.1 | 643.2 | 76 | 16.9 | 136.1 | 8.3 | 236.2 | 12 | 460.9 | 729.2 | 765.3 | 536.6 | 706.8 | 833.2 | 743.7 | 692 | 783.4 | 377.4 | 604.4 | 775.1 | 218.6 | 315 | 386.4 | 666.2 | 634.4 | 718.1 | 641.6 | 675.8 | 336.4 | 481.2 | 434.7 | 379.5 | 385.1 | 555 | 390.4
1952.1 | 1713.1 | 566.8 | 226.72 | 265.0226 | 648.5 | 439.1 | 424.5 | 402.4 | 644.1 | 76.1 | 16.9 | 136.1 | 9.4 | 247.2 | 10.9 | 461 | 728.5 | 758.4 | 536.8 | 707.1 | 832.2 | 744.1 | 691.4 | 777 | 377.7 | 605.1 | 774.5 | 218.9 | 315.3 | 386.7 | 666.3 | 635.8 | 716.4 | 641.9 | 674.1 | 336.7 | 481.6 | 435.1 | 379.8 | 385.4 | 555.3 | 390.8
1953.1 | 1714.1 | 565.3 | 226.12 | 264.3213 | 641 | 437.9 | 424.9 | 402.9 | 643.2 | 76.2 | 16.9 | 136.2 | 7.2 | 216.6 | 12.4 | 460.9 | 728.6 | 751.3 | 537 | 707.4 | 831.2 | 744.2 | 691.3 | 764.8 | 378.1 | 605.7 | 772.7 | 219.3 | 315.6 | 386.8 | 666.4 | 636.3 | 714.5 | 642 | 671.8 | 337.1 | 482.5 | 435.8 | 380.2 | 385.9 | 555.5 | 391.1
1954.1 | 1715.1 | 565 | 226 | 264.181 | 637 | 436.7 | 424.5 | 403.1 | 641.5 | 76.3 | 16.9 | 136.4 | 8.1 | 219 | 14.2 | 461.3 | 728 | 748.4 | 537.2 | 707.8 | 831.2 | 744.5 | 692.9 | 753.5 | 378.4 | 606.4 | 771 | 219.6 | 315.9 | 387.1 | 667.3 | 636.7 | 707.9 | 642.5 | 671.3 | 337.5 | 483 | 436.6 | 380.7 | 386.3 | 555.8 | 391.5
1955.1 | 1716.1 | 564.9 | 225.96 | 264.1342 | 634.2 | 436 | 424.2 | 403.7 | 639.2 | 76.3 | 16.8 | 136.5 | 7.5 | 215.6 | 10.5 | 461.4 | 728.1 | 750.5 | 537.3 | 708.3 | 831.7 | 744.9 | 693.6 | 751.5 | 378.8 | 607.1 | 770.6 | 219.9 | 316.1 | 387.4 | 668.9 | 636.3 | 705.7 | 643.5 | 673 | 338.1 | 483.6 | 436.8 | 381 | 386.6 | 556.2 | 391.9
1956.1 | 1717.1 | 565.9 | 226.36 | 264.6018 | 627.3 | 434.9 | 424.5 | 404.1 | 638.6 | 76.4 | 16.8 | 136.5 | 7.7 | 210.8 | 11.6 | 461.6 | 728.4 | 757.8 | 537.4 | 708.7 | 832.8 | 745.2 | 692.8 | 756.6 | 379.1 | 607.7 | 770.7 | 220.3 | 316.3 | 387.5 | 669.2 | 635.9 | 708.2 | 644 | 674.8 | 338.6 | 484.1 | 436.8 | 381.3 | 386.8 | 556.6 | 392.3
1957.1 | 1718.1 | 565.7 | 226.28 | 264.5083 | 627 | 433.7 | 424.8 | 403.9 | 638.4 | 76.4 | 16.8 | 136.6 | 8.2 | 211.7 | 13.7 | 461.7 | 727.6 | 763 | 537.6 | 709 | 833.1 | 745.5 | 691.9 | 766.9 | 379.5 | 608.4 | 772 | 220.6 | 316.6 | 387.9 | 668.7 | 634.2 | 712.5 | 643.9 | 675.8 | 339.1 | 484.1 | 437 | 381.6 | 387 | 556.9 | 392.6
1958.1 | 1719.1 | 565.9 | 226.36 | 264.6018 | 630.7 | 434.9 | 424.8 | 403.9 | 634.9 | 76.4 | 16.8 | 136.8 | 8.3 | 203.2 | 15.7 | 461.7 | 726.6 | 765.2 | 537.8 | 709.4 | 833.1 | 745.7 | 692.5 | 772.2 | 379.8 | 609 | 773.4 | 220.9 | 316.8 | 388.2 | 668.1 | 632.5 | 710.8 | 643.5 | 675 | 339.4 | 484.2 | 437.5 | 381.9 | 387.3 | 557.1 | 393
1959.1 | 1720.1 | 565.6 | 226.24 | 264.4615 | 627.9 | 435.8 | 425.2 | 404 | 635.8 | 76.5 | 16.8 | 136.7 | 7.6 | 208.8 | 17.2 | 461.7 | 726.4 | 756.6 | 538 | 709.8 | 833.6 | 745.9 | 692.3 | 767.5 | 380.1 | 609.7 | 773 | 221.3 | 317.1 | 388.3 | 668.4 | 633.1 | 712.1 | 643.6 | 675.3 | 339.8 | 485.1 | 438 | 382.4 | 387.5 | 557.4 | 393.3
1960.1 | 1721.1 | 566.1 | 226.44 | 264.6953 | 625.3 | 436.5 | 425.6 | 404.1 | 635.3 | 76.5 | 16.8 | 136.7 | 8.6 | 206.2 | 17.5 | 461.9 | 726 | 750.5 | 538.2 | 710.1 | 834.2 | 746 | 694.2 | 767.3 | 380.5 | 610.3 | 773.6 | 221.6 | 317.3 | 388.7 | 669 | 631.9 | 716.9 | 643.7 | 676.2 | 340 | 485.7 | 438.2 | 382.8 | 387.7 | 557.6 | 393.7
1961.1 | 1722.1 | 565.6 | 226.24 | 264.4615 | 622.3 | 435.9 | 425.9 | 404.2 | 632.8 | 76.6 | 16.8 | 136.7 | 8.6 | 212.8 | 16 | 462 | 726.9 | 748.8 | 538.3 | 710.4 | 834 | 746.2 | 695.2 | 768.1 | 380.8 | 611 | 775.1 | 221.9 | 317.6 | 388.9 | 668.8 | 630.1 | 718.5 | 643.5 | 677.2 | 340.2 | 485.8 | 438.2 | 383 | 387.9 | 557.9 | 394
1962.1 | 1723.1 | 566.1 | 226.44 | 264.6953 | 617.7 | 437.1 | 426.8 | 404.5 | 633.9 | 76.6 | 16.8 | 136.7 | 7.1 | 192.5 | 17.6 | 462.2 | 727.9 | 751.6 | 538.6 | 710.8 | 834.2 | 746.5 | 696.8 | 768.7 | 381.2 | 611.6 | 775.8 | 222.2 | 317.8 | 389.2 | 668.8 | 629.3 | 716.3 | 643.2 | 676.7 | 340.3 | 485.7 | 438.7 | 383.4 | 388.3 | 558.1 | 394.4
1963.1 | 1724.1 | 565 | 226 | 264.181 | 616.8 | 438.1 | 427.2 | 405.1 | 637.2 | 76.6 | 16.8 | 136.6 | 6.4 | 203.7 | 18 | 462.2 | 727.9 | 749.7 | 538.7 | 711.2 | 834.1 | 746.6 | 695.9 | 769.7 | 381.5 | 612.3 | 776.2 | 222.6 | 318 | 389.3 | 669.3 | 630.9 | 718.7 | 643.6 | 677.1 | 340.5 | 486.4 | 438.8 | 383.9 | 388.6 | 558.3 | 394.7
1964.1 | 1725.1 | 565.4 | 226.16 | 264.368 | 613.1 | 437.7 | 427.4 | 406.7 | 638.3 | 76.6 | 16.8 | 136.5 | 6.7 | 220.1 | 14.6 | 462.2 | 728.4 | 743.6 | 538.8 | 711.5 | 834.4 | 746.8 | 694.8 | 765.5 | 381.8 | 612.9 | 775.8 | 222.9 | 318.2 | 389.5 | 669.8 | 631.5 | 716.7 | 644.1 | 676.9 | 340.8 | 486.7 | 438.7 | 384.3 | 388.8 | 558.6 | 395.1
1965.1 | 1726.1 | 565.9 | 226.36 | 264.6018 | 621.3 | 437.6 | 427.2 | 407.4 | 638.5 | 76.6 | 16.8 | 136.4 | 6 | 224.4 | 11.1 | 462.3 | 728.6 | 746.5 | 539 | 711.8 | 834.1 | 747 | 695.2 | 760.1 | 382.2 | 613.5 | 774.6 | 223.2 | 318.4 | 389.8 | 670.2 | 632.7 | 718.7 | 644.5 | 678.4 | 341.1 | 487.3 | 438.9 | 384.8 | 389.2 | 558.9 | 395.5
1966.1 | 1727.1 | 564 | 225.6 | 263.7134 | 627.1 | 438.6 | 427.1 | 407.3 | 642.7 | 76.6 | 16.8 | 136.3 | 6.5 | 209.7 | 11.8 | 462.3 | 728.3 | 745.2 | 539.1 | 712.2 | 834.6 | 747.3 | 695 | 759.7 | 382.5 | 614.2 | 773.7 | 223.6 | 318.6 | 390 | 670.4 | 634.8 | 723.2 | 644.9 | 681.4 | 341.3 | 487.6 | 439.2 | 385.3 | 389.5 | 559.2 | 395.9
1967.1 | 1728.1 | 564.7 | 225.88 | 264.0407 | 630.7 | 437.7 | 427.2 | 408.1 | 645.7 | 76.6 | 16.8 | 136 | 6.1 | 203.3 | 14.2 | 462.3 | 727 | 738.5 | 539.3 | 712.6 | 834.4 | 747.5 | 694.7 | 758.7 | 382.8 | 614.8 | 773.2 | 223.9 | 318.8 | 390.4 | 671.1 | 636.5 | 727.8 | 645.4 | 681.5 | 341.6 | 487.6 | 439.4 | 385.7 | 389.7 | 559.5 | 396.2
1968.1 | 1729.1 | 566.2 | 226.48 | 264.7421 | 633.3 | 437.5 | 426.9 | 408.5 | 645.2 | 76.6 | 16.8 | 135.9 | 6 | 260.2 | 12.4 | 462.4 | 726.4 | 736.2 | 539.4 | 712.9 | 833.4 | 747.6 | 696.3 | 750.8 | 383.2 | 615.5 | 771.3 | 224.2 | 319 | 390.5 | 671.8 | 637.8 | 727 | 646.3 | 681.5 | 341.9 | 488.2 | 439.5 | 386.1 | 390 | 559.8 | 396.6
1969.1 | 1730.1 | 565.8 | 226.32 | 264.555 | 633.6 | 436.9 | 426.7 | 408.5 | 647.6 | 76.8 | 16.8 | 135.8 | 6.7 | 247.8 | 9 | 462.5 | 725.9 | 736.2 | 539.5 | 713.2 | 833.4 | 747.7 | 703 | 749.6 | 383.5 | 616.1 | 771.3 | 224.6 | 319.2 | 390.8 | 672.6 | 639 | 734.1 | 647 | 682.1 | 342.1 | 489.3 | 439.3 | 386.6 | 390.1 | 560.1 | 397
1970.1 | 1731.1 | 567.1 | 226.84 | 265.1629 | 630.7 | 436.5 | 426.9 | 408.3 | 649.4 | 76.8 | 16.8 | 135.8 | 7.2 | 215.5 | 7.8 | 462.3 | 725.9 | 742 | 539.5 | 713.6 | 833.1 | 747.8 | 704.3 | 756.2 | 383.9 | 616.7 | 771.7 | 224.9 | 319.4 | 391.1 | 672.6 | 639.2 | 734.9 | 647.4 | 682.8 | 342.3 | 489.8 | 439.6 | 387 | 390.3 | 560.4 | 397.3
1971.1 | 1732.1 | 567.2 | 226.88 | 265.2096 | 633.6 | 437.6 | 427 | 408.6 | 647.5 | 76.9 | 16.8 | 135.9 | 7 | 202.1 | 7.7 | 462.3 | 725.3 | 741.9 | 539.7 | 714 | 832.9 | 747.9 | 702.4 | 760.8 | 384.2 | 617.4 | 772 | 225.2 | 319.6 | 391.3 | 672.2 | 639 | 733.7 | 647.3 | 682.8 | 342.5 | 490.2 | 439.8 | 387.4 | 390.6 | 560.7 | 397.7
1972.1 | 1733.1 | 567.8 | 227.12 | 265.4902 | 637.3 | 437.8 | 426.6 | 409.1 | 650.9 | 76.9 | 16.8 | 135.9 | 7.7 | 227.7 | 7 | 462.4 | 724.5 | 738.1 | 539.8 | 714.3 | 833.3 | 748.1 | 702 | 758 | 384.5 | 618 | 772.5 | 225.6 | 319.8 | 391.6 | 672.1 | 640.9 | 736.8 | 647.3 | 683.6 | 342.7 | 490.6 | 440 | 387.9 | 390.8 | 561 | 398.1
1973.1 | 1734.1 | 566.4 | 226.56 | 264.8356 | 634.4 | 436.8 | 426.7 | 409.3 | 652.6 | 76.9 | 16.8 | 135.8 | 7.3 | 201 | 6.8 | 462.7 | 724.4 | 733.1 | 540 | 714.6 | 833.2 | 748.3 | 702 | 757.8 | 384.9 | 618.7 | 771.8 | 225.9 | 320 | 391.8 | 672.4 | 641.8 | 739 | 647.4 | 684.6 | 342.9 | 491.2 | 440.5 | 388.4 | 391.2 | 561.2 | 398.4
1974.1 | 1735.1 | 566.9 | 226.76 | 265.0694 | 636.2 | 435.5 | 426.7 | 410.4 | 650.6 | 76.8 | 16.8 | 135.8 | 6.9 | 212 | 8.9 | 462.6 | 725 | 730.6 | 540.1 | 715 | 833.9 | 748.4 | 701 | 757.3 | 385.2 | 619.3 | 771.6 | 226.2 | 320.2 | 392.1 | 672.8 | 640.9 | 741 | 647.7 | 684.4 | 343.1 | 491.2 | 440.9 | 388.6 | 391.4 | 561.5 | 398.8
1975.1 | 1736.1 | 566.2 | 226.48 | 264.7421 | 636.4 | 434.4 | 427.3 | 410.7 | 650 | 76.8 | 16.8 | 135.8 | 7.6 | 195.6 | 10.4 | 462.6 | 725.1 | 733.4 | 540.2 | 715.4 | 834.4 | 748.5 | 702.1 | 758.3 | 385.5 | 620 | 772 | 226.5 | 320.4 | 392.3 | 672.8 | 640.2 | 739.8 | 648 | 682 | 343.4 | 491.4 | 440.8 | 388.9 | 391.5 | 561.8 | 399.2
1976.1 | 1737.1 | 565.2 | 226.08 | 264.2745 | 640.5 | 434.3 | 428.3 | 410.6 | 646.3 | 76.7 | 16.8 | 135.9 | 7.6 | 206.9 | 10.4 | 462.6 | 724.8 | 736.2 | 540.3 | 715.7 | 834.7 | 748.7 | 701.1 | 760.2 | 385.8 | 620.6 | 772.7 | 226.9 | 320.7 | 392.8 | 672.5 | 637.7 | 732.1 | 647.6 | 679 | 343.5 | 491.8 | 441.1 | 389.2 | 391.7 | 562 | 399.5
1977.1 | 1738.1 | 565.3 | 226.12 | 264.3213 | 640.8 | 435.2 | 428.8 | 410.1 | 644.1 | 76.7 | 16.8 | 136.1 | 7.1 | 220.1 | 10 | 462.6 | 724.7 | 737.7 | 540.4 | 716 | 834.9 | 748.7 | 701.6 | 764.2 | 386.1 | 621.2 | 773.4 | 227.2 | 321 | 393 | 672.3 | 635.6 | 730.3 | 647.2 | 677.1 | 343.6 | 491.4 | 441.1 | 389.4 | 391.8 | 562.1 | 399.8
1978.1 | 1739.1 | 565.3 | 226.12 | 264.3213 | 641.2 | 437.1 | 430.1 | 409.8 | 643.5 | 76.7 | 16.8 | 136.2 | 7.4 | 203.9 | 11 | 462.6 | 724.9 | 739.2 | 540.4 | 716.4 | 835 | 748.7 | 702.1 | 765.4 | 386.5 | 621.9 | 774.1 | 227.5 | 321.3 | 393.2 | 672.8 | 634.8 | 725.9 | 647.5 | 676.4 | 343.7 | 490.7 | 441 | 389.6 | 392 | 562.2 | 400.1
1979.1 | 1740.1 | 565.8 | 226.32 | 264.555 | 643.2 | 437.6 | 430.3 | 409.8 | 643 | 76.6 | 16.8 | 136.4 | 7.5 | 205.4 | 12.8 | 462.5 | 725.4 | 740.4 | 540.5 | 716.7 | 834.4 | 748.8 | 702.7 | 763.3 | 386.8 | 622.5 | 775.4 | 227.8 | 321.6 | 393.5 | 673.1 | 634.4 | 720 | 647.5 | 675.2 | 343.8 | 490.3 | 440.7 | 389.8 | 392.1 | 562.4 | 400.4
1980.1 | 1741.1 | 565.8 | 226.32 | 264.555 | 643.2 | 439.4 | 430.7 | 409.6 | 640.7 | 76.6 | 16.8 | 136.6 | 7.6 | 208.6 | 14.8 | 462.6 | 726.7 | 741 | 540.6 | 717.1 | 833.5 | 749 | 701.1 | 767.8 | 387.1 | 623.2 | 777 | 228.2 | 321.9 | 393.6 | 673.6 | 633.8 | 717.3 | 647.4 | 674.4 | 343.9 | 490.5 | 440.8 | 390.2 | 392.3 | 562.5 | 400.8
1981.1 | 1742.1 | 565.1 | 226.04 | 264.2277 | 641.5 | 442.2 | 430.8 | 409.9 | 641 | 76.6 | 16.8 | 136.6 | 9.1 | 222.6 | 12.7 | 462.5 | 726.1 | 739.6 | 540.8 | 717.4 | 833.3 | 749.2 | 700.2 | 769.2 | 387.4 | 623.8 | 777.4 | 228.5 | 322.3 | 394 | 674.4 | 634.3 | 714.4 | 647.9 | 676.3 | 344 | 490.8 | 441 | 390.6 | 392.6 | 562.7 | 401.1
1982.1 | 1743.1 | 564.1 | 225.64 | 263.7602 | 635.9 | 442.8 | 430.8 | 410.1 | 640.6 | 76.5 | 16.8 | 136.7 | 9.5 | 240.3 | 9.8 | 462.5 | 726.3 | 742.9 | 540.9 | 717.8 | 833.8 | 749.4 | 699.8 | 766.9 | 387.7 | 624.4 | 777.1 | 228.8 | 322.6 | 394.2 | 675.3 | 635.6 | 713.3 | 648.6 | 678 | 344.2 | 491 | 440.9 | 391.1 | 392.9 | 563 | 401.5
1983.1 | 1744.1 | 564.6 | 225.84 | 263.9939 | 639.6 | 442.6 | 431 | 410.3 | 640.4 | 76.6 | 16.8 | 136.8 | 8.2 | 207.6 | 10.4 | 462.5 | 726.1 | 743 | 541 | 718.1 | 833.8 | 749.5 | 698.8 | 768.2 | 388 | 625 | 776.3 | 229.1 | 322.9 | 394.6 | 675 | 635.2 | 714.5 | 649 | 679.2 | 344.3 | 491 | 440.6 | 391.4 | 393.1 | 563.2 | 401.8
1984.1 | 1745.1 | 564.2 | 225.68 | 263.8069 | 648.1 | 443.2 | 431.7 | 410.5 | 641.8 | 76.6 | 16.8 | 137 | 8.8 | 210.5 | 14.5 | 462.7 | 724.5 | 741.3 | 541.1 | 718.4 | 834.2 | 749.5 | 697.8 | 770.7 | 388.3 | 625.7 | 776.1 | 229.5 | 323.3 | 395 | 674.8 | 635.4 | 717.7 | 649.2 | 679.9 | 344.4 | 490.4 | 440.3 | 391.5 | 393.2 | 563.5 | 402.1
1985.1 | 1746.1 | 564.7 | 225.88 | 264.0407 | 645.1 | 444.8 | 432 | 410.3 | 648.2 | 76.6 | 16.7 | 137.2 | 10.5 | 223.6 | 15 | 462.7 | 723.9 | 746.2 | 541.2 | 718.7 | 834.1 | 749.7 | 699 | 776.4 | 388.6 | 626.3 | 777 | 229.8 | 323.6 | 395.5 | 675.1 | 638.5 | 723.2 | 649.8 | 681.4 | 344.5 | 489.5 | 440.1 | 391.7 | 393.4 | 563.7 | 402.5
1986.1 | 1747.1 | 565.8 | 226.32 | 264.555 | 644.3 | 445 | 432.4 | 409.7 | 650.3 | 76.6 | 16.7 | 137.2 | 9.2 | 222.2 | 12.9 | 462.7 | 722.6 | 745.3 | 541.4 | 719 | 834.3 | 749.7 | 698.5 | 775.1 | 388.9 | 626.9 | 776.9 | 230.1 | 323.9 | 395.5 | 675.3 | 639.4 | 723.2 | 650 | 681.3 | 344.5 | 488.8 | 440.3 | 391.9 | 393.6 | 563.9 | 402.8
1987.1 | 1748.1 | 565.4 | 226.16 | 264.368 | 646.8 | 447.2 | 432.1 | 409.8 | 649.2 | 76.6 | 16.7 | 137.2 | 8.3 | 202.7 | 11.9 | 462.9 | 721.7 | 744.8 | 541.6 | 719.2 | 834.9 | 750 | 698.2 | 774.3 | 389.2 | 627.5 | 776.7 | 230.4 | 324.2 | 395.6 | 675.3 | 639.1 | 724.9 | 650.2 | 682.7 | 344.6 | 488.7 | 440.2 | 392.3 | 393.7 | 564.1 | 403.1
1988.1 | 1749.1 | 565.7 | 226.28 | 264.5083 | 644.1 | 449.7 | 431.3 | 410.3 | 646.8 | 76.8 | 16.7 | 137.2 | 7.4 | 216.8 | 8.3 | 463 | 722 | 745.9 | 541.7 | 719.5 | 835.4 | 750.1 | 701.8 | 774.4 | 389.6 | 628.1 | 777.1 | 230.8 | 324.5 | 396 | 675.6 | 637.7 | 727.1 | 650.4 | 683.6 | 344.7 | 488.6 | 439.9 | 392.6 | 393.8 | 564.3 | 403.4
1989.1 | 1750.1 | 565.5 | 226.2 | 264.4148 | 642 | 448.6 | 430.9 | 410.6 | 645.8 | 76.9 | 16.7 | 137.2 | 7.7 | 213.5 | 9 | 462.9 | 721.7 | 743.5 | 541.8 | 719.8 | 835.9 | 750.3 | 702 | 771.1 | 389.9 | 628.7 | 776.9 | 231.1 | 324.8 | 396.4 | 675.2 | 637.1 | 725.9 | 650.2 | 682.7 | 344.7 | 488.2 | 439.5 | 392.8 | 394 | 564.5 | 403.7
1990.1 | 1751.1 | 567.1 | 226.84 | 265.1629 | 645.3 | 447.1 | 430.6 | 410.4 | 646.3 | 77 | 16.7 | 137.3 | 8.6 | 196 | 11.9 | 462.8 | 721.8 | 741.7 | 541.9 | 720.2 | 836.1 | 750.5 | 701.6 | 772.6 | 390.2 | 629.3 | 777.7 | 231.4 | 325.2 | 396.6 | 675.2 | 636.8 | 722.1 | 650.1 | 680.8 | 344.7 | 487.8 | 439.1 | 393.1 | 394.2 | 564.7 | 404.1
1991.1 | 1752.1 | 568.5 | 227.4 | 265.8175 | 652.2 | 447.5 | 430.2 | 410.3 | 649.3 | 77.1 | 16.7 | 137.6 | 9.5 | 214.8 | 10 | 462.8 | 721.5 | 733.3 | 542.1 | 720.4 | 835.8 | 750.7 | 702 | 766.9 | 390.6 | 629.9 | 777.5 | 231.8 | 325.5 | 396.8 | 675.3 | 637.5 | 716.2 | 649.9 | 679.4 | 344.8 | 488.2 | 439.6 | 393.5 | 394.6 | 564.9 | 404.4
1992.1 | 1753.1 | 568.5 | 227.4 | 265.8175 | 650.4 | 450.2 | 430.3 | 410.7 | 648.2 | 77.2 | 16.7 | 137.7 | 8.5 | 193 | 10.1 | 463.2 | 720.9 | 721.8 | 542.3 | 720.7 | 834.8 | 750.7 | 704.6 | 759.7 | 390.8 | 630.4 | 775.9 | 232.1 | 325.9 | 396.9 | 676.2 | 638.8 | 710.4 | 650.2 | 678.9 | 345 | 489.2 | 440.6 | 394.1 | 395 | 565.1 | 404.7
1993.1 | 1754.1 | 566.2 | 226.48 | 264.7421 | 648.5 | 450.4 | 430.6 | 412.1 | 650 | 77.2 | 16.7 | 137.7 | 7.4 | 193.8 | 15.3 | 463.1 | 721.1 | 710.5 | 542.4 | 720.9 | 832.9 | 750.7 | 707.7 | 749.9 | 391.1 | 631 | 774.3 | 232.4 | 326.3 | 397.3 | 677.1 | 641.5 | 705 | 650.9 | 679.5 | 345.5 | 490.7 | 441.7 | 394.9 | 395.6 | 565.4 | 405.1
1994.1 | 1755.1 | 566 | 226.4 | 264.6486 | 644.4 | 451 | 431 | 413.2 | 648.2 | 77.2 | 16.7 | 137.6 | 7 | 203.7 | 20.8 | 462.8 | 721.2 | 708.6 | 542.5 | 721.2 | 832.7 | 750.8 | 710.2 | 743.1 | 391.4 | 631.6 | 772.5 | 232.7 | 326.6 | 397.5 | 678.1 | 641.9 | 699.3 | 651.8 | 678.8 | 346 | 491.5 | 442.7 | 395.3 | 395.9 | 565.7 | 405.5
1995.1 | 1756.1 | 566.5 | 226.6 | 264.8823 | 638.3 | 449.7 | 431.3 | 413.9 | 647.5 | 77.3 | 16.7 | 137.7 | 7.7 | 221.5 | 17.8 | 462.6 | 720.5 | 711 | 542.6 | 721.5 | 833 | 750.8 | 708.9 | 747.6 | 391.7 | 632.2 | 771.7 | 233.1 | 327 | 397.7 | 678.9 | 642.1 | 705.5 | 652.7 | 679.7 | 346.5 | 491.8 | 443.6 | 395.7 | 396.2 | 566 | 405.9
1996.1 | 1757.1 | 567.2 | 226.88 | 265.2096 | 631 | 449 | 431.2 | 414 | 649.9 | 77.3 | 16.7 | 137.8 | 7.5 | 209.7 | 13.9 | 462.6 | 720.8 | 721.4 | 542.7 | 721.8 | 833.2 | 750.8 | 707 | 756.2 | 392.1 | 632.8 | 772.7 | 233.4 | 327.2 | 397.9 | 679.5 | 642.1 | 710.8 | 653.8 | 682.3 | 347 | 493.1 | 445.7 | 396.1 | 396.5 | 566.3 | 406.2
1997.1 | 1758.1 | 567.3 | 226.92 | 265.2564 | 626.6 | 448.9 | 431.1 | 413.6 | 648.9 | 77.4 | 16.7 | 137.8 | 7.5 | 215.9 | 11.4 | 462.6 | 720.7 | 720.9 | 542.7 | 722.1 | 833.9 | 750.8 | 704.8 | 757.2 | 392.3 | 633.4 | 772.8 | 233.7 | 327.5 | 398.1 | 679.9 | 640.4 | 712.3 | 654.7 | 680.8 | 347.5 | 493.8 | 446.8 | 396.3 | 396.8 | 566.5 | 406.6
1998.1 | 1759.1 | 566.8 | 226.72 | 265.0226 | 630.6 | 447.2 | 431.2 | 413.3 | 647.3 | 77.4 | 16.7 | 137.8 | 6.3 | 182.1 | 9.1 | 462.6 | 720.4 | 717.3 | 542.9 | 722.4 | 835.4 | 750.9 | 704.2 | 751.9 | 392.6 | 634 | 773.1 | 234.1 | 327.7 | 398.5 | 680.1 | 638.1 | 711.3 | 655.1 | 677.9 | 347.9 | 493.8 | 446.8 | 396.6 | 397 | 566.7 | 406.9
1999.1 | 1760.1 | 566 | 226.4 | 264.6486 | 632.9 | 448.3 | 431.9 | 413.2 | 643.6 | 77.5 | 16.7 | 137.8 | 5.9 | 201.9 | 12.6 | 462.6 | 719.8 | 713.8 | 542.9 | 722.6 | 835.8 | 751 | 705 | 744.5 | 392.9 | 634.6 | 772 | 234.4 | 327.9 | 398.7 | 680 | 635.3 | 707.3 | 655.1 | 675.5 | 348.1 | 493.3 | 446.3 | 396.8 | 397.3 | 566.8 | 407.2
2000.1 | 1761.1 | 569.4 | 227.76 | 266.2383 | 638.6 | 448.6 | 433.2 | 413.2 | 641.5 | 77.7 | 16.7 | 137.8 | 6.1 | 200.2 | 18 | 462.4 | 719.6 | 718.9 | 543.1 | 722.8 | 836.5 | 751 | 705.4 | 744.1 | 393.2 | 635.2 | 772 | 234.7 | 328.1 | 398.9 | 679.6 | 634.9 | 705.5 | 655.1 | 674.4 | 348.3 | 492.6 | 445.9 | 397 | 397.5 | 567 | 407.5
2001.1 | 1762.1 | 568.3 | 227.32 | 265.724 | 635 | 447.1 | 434 | 413 | 642.1 | 77.8 | 16.7 | 137.8 | 6 | 202.6 | 18.8 | 462.1 | 720.4 | 717.8 | 543.2 | 723.1 | 836.3 | 750.9 | 704.8 | 752.3 | 393.5 | 635.8 | 774.2 | 235.1 | 328.2 | 399.1 | 679.7 | 635.8 | 705.4 | 655.2 | 674.8 | 348.4 | 492.3 | 445.7 | 397.2 | 397.8 | 567.1 | 407.8
2002.1 | 1763.1 | 566.8 | 226.72 | 265.0226 | 630.1 | 447.1 | 433.7 | 412.9 | 642.4 | 77.8 | 16.7 | 137.9 | 6.6 | 196.6 | 18.9 | 462 | 721 | 723.4 | 543.3 | 723.5 | 835.7 | 751 | 706.5 | 757.8 | 393.8 | 636.4 | 774.9 | 235.4 | 328.4 | 399.5 | 680.9 | 637.8 | 706.1 | 655.9 | 677.1 | 348.6 | 492.9 | 445.7 | 397.7 | 398.1 | 567.3 | 408.1
2003.1 | 1764.1 | 567.7 | 227.08 | 265.4434 | 624.8 | 446.4 | 433.4 | 413.5 | 645.8 | 77.9 | 16.7 | 137.8 | 7 | 186.7 | 21.5 | 461.8 | 720.7 | 725.2 | 543.4 | 723.9 | 835.5 | 751.2 | 706.1 | 760.5 | 394 | 637 | 775.1 | 235.7 | 328.6 | 399.8 | 682.1 | 640 | 711.9 | 656.9 | 680.2 | 348.7 | 493.9 | 445.5 | 398.2 | 398.2 | 567.5 | 408.4
2004.1 | 1765.1 | 566.8 | 226.72 | 265.0226 | 619.6 | 446.6 | 433.8 | 413.9 | 646.8 | 78 | 16.7 | 137.7 | 6.4 | 192.4 | 21.1 | 461.9 | 719.9 | 722.6 | 543.5 | 724.1 | 836.3 | 751.3 | 703.7 | 760.1 | 394.3 | 637.6 | 775 | 236.1 | 328.8 | 400.1 | 681.8 | 639.8 | 710.4 | 657.3 | 681.2 | 348.9 | 494.8 | 444.8 | 398.6 | 398.3 | 567.8 | 408.8
2005.1 | 1766.1 | 565.7 | 226.28 | 264.5083 | 620 | 448.7 | 433.8 | 414 | 647.1 | 78 | 16.7 | 137.6 | 6.2 | 195.2 | 19.1 | 461.8 | 719.6 | 723.9 | 543.6 | 724.3 | 836.4 | 751.3 | 704 | 761 | 394.6 | 638.1 | 775 | 236.4 | 328.9 | 400.4 | 681.1 | 639.3 | 712.1 | 657.3 | 680.3 | 348.9 | 494.6 | 444.4 | 398.9 | 398.4 | 568.1 | 409.1
2006.1 | 1767.1 | 566.5 | 226.6 | 264.8823 | 621.4 | 448.4 | 434.8 | 413.8 | 648.2 | 78.1 | 16.7 | 137.5 | 5.8 | 188.9 | 19.8 | 462 | 719.8 | 728.4 | 543.8 | 724.6 | 836.3 | 751.3 | 703.8 | 759.8 | 394.9 | 638.7 | 775.6 | 236.8 | 329.1 | 400.6 | 681.2 | 640.1 | 711.2 | 657.3 | 676.6 | 348.9 | 494 | 444.4 | 399.1 | 398.7 | 568.3 | 409.4
2007.1 | 1768.1 | 566.1 | 226.44 | 264.6953 | 626.6 | 448 | 435.2 | 413.7 | 648.6 | 78.2 | 16.7 | 137.4 | 6.6 | 195.2 | 20.4 | 461.7 | 720.6 | 729.2 | 543.9 | 724.9 | 836.5 | 751.3 | 702.8 | 761 | 395.3 | 639.3 | 775.7 | 237.1 | 329.3 | 400.8 | 681.4 | 639.5 | 707.9 | 657.1 | 674.9 | 348.9 | 493.4 | 444.2 | 399.4 | 398.8 | 568.4 | 409.7
2008.1 | 1769.1 | 566.4 | 226.56 | 264.8356 | 624.3 | 450.7 | 434.9 | 413.8 | 644.1 | 78.2 | 16.7 | 137.4 | 8.1 | 185.6 | 18.1 | 461.4 | 720.4 | 726.1 | 544 | 725.2 | 836.8 | 751.3 | 701.3 | 755.9 | 395.5 | 639.8 | 774.8 | 237.4 | 329.5 | 401 | 681.2 | 637.5 | 706 | 656.7 | 673.4 | 348.8 | 493 | 443.8 | 399.6 | 398.9 | 568.5 | 410
2009.1 | 1770.1 | 566.3 | 226.52 | 264.7888 | 619.7 | 452.3 | 435.3 | 414.1 | 641.4 | 78.3 | 16.7 | 137.5 | 7.8 | 186.8 | 16.3 | 461.3 | 720.8 | 729.1 | 544.1 | 725.5 | 836.9 | 751.4 | 701.5 | 757.6 | 395.9 | 640.3 | 775.4 | 237.7 | 329.8 | 401.1 | 680.9 | 637.2 | 706.3 | 656.2 | 674.7 | 348.8 | 493.1 | 443.9 | 400 | 399.1 | 568.7 | 410.3
2010.1 | 1771.1 | 566.2 | 226.48 | 264.7421 | 614.1 | 453.2 | 435.2 | 414.3 | 640.9 | 78.4 | 16.7 | 137.6 | 7.1 | 181.2 | 17.9 | 461.3 | 721 | 729.5 | 544.1 | 725.7 | 836.1 | 751.6 | 701.3 | 760.4 | 396.2 | 640.9 | 776.1 | 238.1 | 330 | 401.4 | 681.3 | 636.7 | 710.6 | 656.2 | 677.4 | 348.8 | 493.9 | 444.1 | 400.5 | 399.4 | 568.9 | 410.6
2011.1 | 1772.1 | 566.1 | 226.44 | 264.6953 | 611.4 | 453.5 | 434.9 | 414.6 | 642.1 | 78.4 | 16.7 | 137.8 | 7.4 | 177 | 16.4 | 461.4 | 720.9 | 724 | 544.2 | 726.1 | 835.6 | 751.9 | 700.8 | 759.7 | 396.5 | 641.4 | 775.8 | 238.4 | 330.3 | 401.6 | 681.2 | 637.7 | 710.4 | 656.1 | 677.7 | 349 | 494.7 | 444.5 | 400.9 | 399.7 | 569.2 | 411
2012.1 | 1773.1 | 566.8 | 226.72 | 265.0226 | 609.7 | 452.3 | 434.4 | 415 | 642.4 | 78.5 | 16.7 | 137.9 | 6.6 | 174.7 | 15.3 | 461.7 | 720 | 726.9 | 544.3 | 726.4 | 835.6 | 752.2 | 700.1 | 758.1 | 396.8 | 642 | 776.1 | 238.8 | 330.5 | 401.8 | 681.5 | 638.2 | 709.6 | 656.2 | 678.6 | 349.2 | 495.2 | 444.6 | 401.3 | 399.9 | 569.4 | 411.3
2013.1 | 1774.1 | 565 | 226 | 264.181 | 614.5 | 452.6 | 434.8 | 414.9 | 642.9 | 78.7 | 16.7 | 138 | 6.7 | 171.6 | 16.1 | 461.6 | 719.9 | 726 | 544.4 | 726.7 | 836 | 752.6 | 700.3 | 760 | 397.1 | 642.5 | 776.4 | 239.1 | 330.8 | 402.1 | 681.9 | 638.9 | 713 | 656.3 | 680 | 349.4 | 495.8 | 444.6 | 401.7 | 400 | 569.6 | 411.7
2014.1 | 1775.1 | 565 | 226 | 264.181 | 619.7 | 453.7 | 434.3 | 414.6 | 641.9 | 78.8 | 16.7 | 138.2 | 7.4 | 192.4 | 13.1 | 461.7 | 720.3 | 724.7 | 544.6 | 727 | 836.3 | 752.9 | 702.5 | 764 | 397.4 | 643 | 777.3 | 239.4 | 331.1 | 402.4 | 681.8 | 638 | 711.2 | 656.2 | 678.2 | 349.6 | 495.8 | 444.3 | 402 | 400.2 | 569.9 | 412
2015.1 | 1776.1 | 565.6 | 226.24 | 264.4615 | 622.7 | 453.7 | 434.4 | 414.4 | 639.9 | 78.8 | 16.6 | 138.4 | 7.6 | 209.7 | 9.7 | 461.6 | 719.9 | 723.8 | 544.7 | 727.3 | 836.5 | 753.2 | 704.5 | 760.2 | 397.6 | 643.5 | 777.8 | 239.7 | 331.3 | 402.6 | 682 | 636.3 | 713.2 | 656.4 | 678 | 349.8 | 495 | 444.4 | 402.3 | 400.4 | 570 | 412.3
2016.1 | 1777.1 | 566.7 | 226.68 | 264.9759 | 627.3 | 454.1 | 435.5 | 414.6 | 639.1 | 78.8 | 16.6 | 138.5 | 7.9 | 208.9 | 8.8 | 461.4 | 719.9 | 716.4 | 544.8 | 727.4 | 836.1 | 753.4 | 707.7 | 754.5 | 397.9 | 644 | 777 | 240.1 | 331.6 | 403.1 | 682.2 | 635.3 | 713.4 | 656.6 | 677.6 | 349.9 | 494.5 | 444.1 | 402.6 | 400.4 | 570.2 | 412.6
2017.1 | 1778.1 | 566.3 | 226.52 | 264.7888 | 628.7 | 453.6 | 436.6 | 415.1 | 643 | 78.7 | 16.6 | 138.6 | 8.9 | 166.4 | 7.6 | 461.4 | 718.7 | 716 | 544.9 | 727.7 | 835.1 | 753.5 | 706.8 | 748.2 | 398.3 | 644.5 | 775.8 | 240.4 | 331.8 | 403.6 | 682.4 | 637.3 | 711.6 | 657 | 675.4 | 349.8 | 494.7 | 443.7 | 402.9 | 400.3 | 570.3 | 413
2018.1 | 1779.1 | 565.5 | 226.2 | 264.4148 | 633.6 | 453.4 | 438.8 | 415.2 | 646.6 | 78.7 | 16.6 | 138.6 | 8.9 | 179.2 | 8.8 | 461.6 | 718.2 | 719.2 | 545 | 727.9 | 834.1 | 753.3 | 706.9 | 753.9 | 398.6 | 645 | 777.4 | 240.7 | 332 | 403.7 | 683 | 640.1 | 711.9 | 657.5 | 675.6 | 349.8 | 495 | 443.6 | 403.2 | 400.5 | 570.5 | 413.3
2019.1 | 1780.1 | 565.5 | 226.2 | 264.4148 | 633.7 | 452.5 | 439.4 | 416.1 | 648.2 | 78.8 | 16.6 | 138.7 | 9 | 170.3 | 13.9 | 461.9 | 718.1 | 717.9 | 545.2 | 728.1 | 834.2 | 753.4 | 705.6 | 756.3 | 399 | 645.6 | 778.4 | 241.1 | 332.2 | 403.8 | 683.4 | 640.8 | 708.1 | 658.1 | 674.6 | 349.8 | 495.2 | 443.7 | 403.6 | 400.7 | 570.6 | 413.6
2020.1 | 1781.1 | 566.3 | 226.52 | 264.7888 | 634.4 | 452.4 | 439.6 | 417.2 | 644.8 | 78.9 | 16.6 | 138.7 | 8.6 | 219.8 | 10.7 | 462.1 | 718.1 | 716.9 | 545.5 | 728.3 | 834.4 | 753.5 | 703.3 | 758.9 | 399.4 | 646.1 | 779.5 | 241.4 | 332.4 | 404 | 683.3 | 638.1 | 702.6 | 658 | 672.5 | 349.8 | 495.2 | 443.6 | 404 | 400.8 | 570.8 | 414
2021.1 | 1782.1 | 566.9 | 226.76 | 265.0694 | 631.4 | 454.4 | 440.2 | 417.9 | 644.8 | 78.9 | 16.6 | 138.7 | 8.4 | 192.9 | 11.8 | 462.4 | 718 | 721.9 | 545.6 | 728.5 | 834 | 753.5 | 702.8 | 760.3 | 399.6 | 646.7 | 779.4 | 241.7 | 332.6 | 404.3 | 682.9 | 637.2 | 702.4 | 657.6 | 673.6 | 349.9 | 495.5 | 443.3 | 404.4 | 400.9 | 571 | 414.3
2022.1 | 1783.1 | 566.5 | 226.6 | 264.8823 | 633.6 | 457.3 | 440.5 | 418.4 | 645.3 | 78.9 | 16.6 | 138.8 | 8.8 | 155.3 | 10.3 | 462.7 | 718 | 725.4 | 545.8 | 728.9 | 833.6 | 753.6 | 703.5 | 758.1 | 399.9 | 647.3 | 779.2 | 242 | 332.8 | 404.8 | 682.4 | 636.7 | 701.8 | 657.2 | 672.5 | 349.9 | 495.5 | 443.1 | 404.7 | 401 | 571.1 | 414.6
2023.1 | 1784.1 | 566.5 | 226.6 | 264.8823 | 632.5 | 457.1 | 440.8 | 418.8 | 645.2 | 78.9 | 16.6 | 139 | 8.4 | 209.5 | 12.4 | 462.6 | 719.2 | 734 | 545.9 | 729.3 | 831.8 | 753.7 | 705.1 | 758.6 | 400.3 | 647.8 | 779.5 | 242.4 | 333.1 | 404.8 | 682.7 | 637 | 703.3 | 657 | 674.3 | 350 | 495.6 | 443.8 | 405.1 | 401.3 | 571.2 | 414.9
2024.1 | 1785.1 | 565.5 | 226.2 | 264.4148 | 631.6 | 458.4 | 440.2 | 419.6 | 646.8 | 79 | 16.6 | 139.2 | 8.8 | 195.1 | 15.3 | 462.6 | 719.8 | 738.5 | 546 | 729.7 | 830.1 | 754 | 704.6 | 758.8 | 400.7 | 648.2 | 778.6 | 242.7 | 333.3 | 405.1 | 683.2 | 639.2 | 705.5 | 657.3 | 678.8 | 350.2 | 496.2 | 444.3 | 405.6 | 401.5 | 571.4 | 415.2
2025.1 | 1786.1 | 565.3 | 226.12 | 264.3213 | 623.8 | 460.5 | 439.5 | 420.4 | 648.8 | 79.1 | 16.6 | 139.3 | 8.9 | 207.1 | 14.5 | 462.6 | 720.4 | 746 | 546 | 730.1 | 828.6 | 754.2 | 704.5 | 759.3 | 400.9 | 648.7 | 778 | 243 | 333.5 | 405.3 | 683.7 | 640.4 | 709.7 | 657.9 | 681.1 | 350.5 | 498 | 444.8 | 406.1 | 401.7 | 571.7 | 415.6
2026.1 | 1787.1 | 566.2 | 226.48 | 264.7421 | 619.5 | 461.1 | 439.5 | 421.2 | 649.3 | 79.1 | 16.6 | 139.3 | 8.3 | 220.7 | 13.2 | 462.8 | 720.9 | 748.2 | 546.1 | 730.4 | 829 | 754.3 | 703.3 | 766.8 | 401.1 | 649.2 | 779.1 | 243.4 | 333.7 | 405.5 | 683.9 | 640.8 | 711.6 | 658.6 | 680.6 | 350.8 | 498.7 | 444.8 | 406.5 | 401.9 | 572.1 | 415.9
2027.1 | 1788.1 | 566 | 226.4 | 264.6486 | 618 | 459.9 | 438.9 | 421.4 | 649.5 | 79.1 | 16.6 | 139.3 | 7.5 | 227.8 | 11.5 | 463 | 720.4 | 748 | 546.3 | 730.7 | 829.1 | 754.6 | 702.3 | 773 | 401.2 | 649.8 | 780 | 243.7 | 334 | 405.9 | 684 | 640.6 | 717.1 | 658.8 | 682.5 | 351.1 | 499 | 444.7 | 406.8 | 402 | 572.4 | 416.3
2028.1 | 1789.1 | 566.1 | 226.44 | 264.6953 | 618.6 | 458.9 | 438.1 | 420.8 | 650.2 | 79 | 16.6 | 139.3 | 7.5 | 192.8 | 11.5 | 463.1 | 720.3 | 753.3 | 546.4 | 731 | 828.9 | 754.9 | 701.2 | 777.9 | 401.4 | 650.3 | 781 | 244 | 334.2 | 406.3 | 683.6 | 640.3 | 715.6 | 658.9 | 682.1 | 351.3 | 498.9 | 444.7 | 407.1 | 402.1 | 572.6 | 416.6
2029.1 | 1790.1 | 566 | 226.4 | 264.6486 | 619.1 | 458.5 | 438.9 | 420.2 | 650.6 | 79 | 16.6 | 139.2 | 7.9 | 190.9 | 10.4 | 463.2 | 720.1 | 756.8 | 546.6 | 731.2 | 828.7 | 755.3 | 700.6 | 782.3 | 401.6 | 650.8 | 781.1 | 244.3 | 334.4 | 406.5 | 683.5 | 638.8 | 717.1 | 658.8 | 682.5 | 351.4 | 498.2 | 444.5 | 407.3 | 402.2 | 572.8 | 416.9
2030.1 | 1791.1 | 566 | 226.4 | 264.6486 | 617.8 | 462.6 | 439.7 | 419.9 | 648.4 | 78.9 | 16.6 | 139.2 | 7.6 | 218.1 | 11.8 | 463.7 | 720.3 | 756.5 | 546.8 | 731.5 | 828.6 | 755.6 | 700.3 | 784 | 401.9 | 651.3 | 781.8 | 244.7 | 334.6 | 406.8 | 683.5 | 637.6 | 718.1 | 658.7 | 682.6 | 351.5 | 497.7 | 444.3 | 407.5 | 402.3 | 572.9 | 417.2
2031.1 | 1792.1 | 565.6 | 226.24 | 264.4615 | 618.4 | 463.9 | 439.9 | 419.8 | 645.5 | 78.9 | 16.6 | 139.1 | 7.7 | 210.4 | 11.2 | 464.4 | 720.2 | 754.7 | 547.1 | 731.7 | 828.7 | 755.9 | 699.7 | 782.8 | 402.3 | 651.8 | 782.1 | 245 | 334.8 | 406.8 | 683.6 | 636.9 | 719.1 | 658.7 | 682.5 | 351.6 | 497.3 | 444.3 | 407.7 | 402.5 | 573.1 | 417.5
2032.1 | 1793.1 | 565.6 | 226.24 | 264.4615 | 619.3 | 467.6 | 439.4 | 419.9 | 645 | 78.9 | 16.6 | 139.1 | 8 | 206 | 9.8 | 464.5 | 719.7 | 755 | 547.3 | 731.9 | 828.9 | 756.1 | 698.8 | 779.1 | 402.6 | 652.2 | 782.2 | 245.3 | 335 | 406.9 | 683.9 | 637 | 720.2 | 659 | 682.2 | 351.8 | 497.9 | 444.4 | 408 | 402.6 | 573.3 | 417.7
2033.1 | 1794.1 | 566.8 | 226.72 | 265.0226 | 620.3 | 467.7 | 438.6 | 419.8 | 642.4 | 79 | 16.6 | 139.1 | 7.2 | 227.9 | 8.5 | 464.5 | 719.6 | 758 | 547.4 | 732.2 | 828.5 | 756.2 | 698.6 | 782.2 | 403 | 652.7 | 782.8 | 245.7 | 335.3 | 407.1 | 684.5 | 636.2 | 718.7 | 659.5 | 682 | 352 | 497.4 | 444.6 | 408.4 | 402.8 | 573.5 | 418
2034.1 | 1795.1 | 566.8 | 226.72 | 265.0226 | 620.7 | 467.9 | 438.1 | 419.7 | 641.9 | 79.1 | 16.6 | 139.1 | 6.9 | 226.6 | 9.4 | 464.6 | 719.2 | 761.5 | 547.5 | 732.6 | 828.3 | 756.3 | 698.6 | 784.7 | 403.3 | 653.2 | 783.1 | 246 | 335.5 | 407.4 | 684.2 | 636.3 | 716.5 | 659.4 | 680.5 | 352.1 | 497.2 | 444.6 | 408.6 | 403 | 573.7 | 418.3
2035.1 | 1796.1 | 566.6 | 226.64 | 264.9291 | 621.7 | 469.1 | 437.8 | 419.6 | 640.5 | 79.2 | 16.6 | 139.3 | 8.1 | 213.4 | 10.7 | 464.9 | 718.7 | 761.1 | 547.7 | 732.9 | 828.2 | 756.5 | 698.1 | 784.5 | 403.5 | 653.6 | 783.4 | 246.3 | 335.8 | 407.6 | 683.7 | 635.8 | 713.4 | 658.9 | 679.4 | 352.2 | 497.2 | 444.5 | 408.9 | 403.1 | 573.9 | 418.6
2036.1 | 1797.1 | 566.8 | 226.72 | 265.0226 | 621.4 | 472.7 | 437.7 | 418.9 | 639.1 | 79.2 | 16.6 | 139.4 | 9 | 211.7 | 11.5 | 464.9 | 718.4 | 760.9 | 547.8 | 733.2 | 828.2 | 756.6 | 697.8 | 780.4 | 403.8 | 654.1 | 782.8 | 246.7 | 336.1 | 407.9 | 683.3 | 634.6 | 712.5 | 658.4 | 679.5 | 352.3 | 497.1 | 444.5 | 409.2 | 403.2 | 574.1 | 418.9
2037.1 | 1798.1 | 566 | 226.4 | 264.6486 | 619.2 | 471.3 | 437.6 | 418.7 | 637.5 | 79.3 | 16.6 | 139.5 | 8.5 | 217.4 | 11.8 | 465 | 717.6 | 761.3 | 548 | 733.3 | 828.9 | 756.8 | 698.6 | 782.1 | 404.1 | 654.5 | 783.7 | 247 | 336.4 | 408.1 | 683.2 | 634.5 | 713.6 | 657.9 | 680.6 | 352.4 | 497.1 | 444.8 | 409.5 | 403.4 | 574.3 | 419.2
2038.1 | 1799.1 | 566.9 | 226.76 | 265.0694 | 615.3 | 468.7 | 437.2 | 419.1 | 638.2 | 79.3 | 16.6 | 139.7 | 7.6 | 228.2 | 9.3 | 465.1 | 717.3 | 759 | 548.1 | 733.5 | 829.1 | 757 | 698.2 | 779.3 | 404.4 | 654.9 | 783.4 | 247.3 | 336.7 | 408.2 | 683.6 | 635.9 | 711 | 658 | 681 | 352.5 | 497.6 | 445.1 | 409.8 | 403.6 | 574.5 | 419.5
2039.1 | 1800.1 | 567.1 | 226.84 | 265.1629 | 615.6 | 466.6 | 437.5 | 419.3 | 641.4 | 79.2 | 16.5 | 139.8 | 7.3 | 193.7 | 8.7 | 465 | 717.4 | 754.1 | 548.2 | 733.9 | 829.3 | 757.2 | 697.5 | 781.3 | 404.9 | 655.3 | 783.2 | 247.7 | 336.9 | 408.4 | 684.6 | 637.2 | 713.6 | 658.4 | 683.7 | 352.7 | 497.9 | 445.6 | 410.2 | 403.8 | 574.8 | 419.9
2040.1 | 1801.1 | 566.9 | 226.76 | 265.0694 | 615.9 | 464.5 | 437.2 | 419.6 | 641.3 | 79.2 | 16.6 | 139.7 | 7.7 | 245.4 | 7.9 | 465.1 | 717.1 | 750.8 | 548.4 | 734.2 | 829.7 | 757.3 | 697.4 | 782.9 | 405.2 | 655.7 | 784 | 248 | 337.2 | 408.7 | 684.6 | 637.1 | 711.2 | 658.6 | 684.7 | 352.9 | 498 | 445.8 | 410.6 | 404 | 575.1 | 420.2
2041.1 | 1802.1 | 566.1 | 226.44 | 264.6953 | 614.9 | 464.9 | 436.4 | 419.9 | 640.1 | 79.2 | 16.5 | 139.8 | 7.8 | 213.4 | 9 | 465.2 | 716.8 | 745.7 | 548.5 | 734.4 | 830 | 757.3 | 696.8 | 775.5 | 405.4 | 656.1 | 783 | 248.4 | 337.4 | 408.8 | 684.9 | 637 | 713.2 | 659.1 | 685.1 | 353.1 | 498.4 | 446.1 | 411 | 404.3 | 575.3 | 420.5
2042.1 | 1803.1 | 566.2 | 226.48 | 264.7421 | 613.7 | 464.9 | 436.3 | 419.7 | 642.2 | 79.1 | 16.5 | 139.8 | 7.2 | 217.5 | 11.3 | 465.2 | 717.1 | 742.8 | 548.6 | 734.7 | 829.6 | 757.5 | 699.9 | 773.2 | 405.6 | 656.4 | 782.9 | 248.7 | 337.7 | 409 | 685.7 | 638.4 | 716.5 | 659.8 | 686.5 | 353.3 | 499.2 | 446.6 | 411.5 | 404.6 | 575.6 | 420.8
2043.1 | 1804.1 | 566.4 | 226.56 | 264.8356 | 610.4 | 464.8 | 436.7 | 419.8 | 643.3 | 79.2 | 16.5 | 139.7 | 6.3 | 208.2 | 10.7 | 465.2 | 716.9 | 736.6 | 548.7 | 735 | 829.2 | 757.7 | 700.4 | 774.5 | 405.9 | 656.9 | 782.7 | 249.1 | 337.9 | 409.4 | 686.4 | 639.1 | 716.8 | 660.4 | 685.8 | 353.6 | 500 | 447.1 | 411.9 | 404.8 | 575.9 | 421.2
2044.1 | 1805.1 | 567.4 | 226.96 | 265.3032 | 608.8 | 464.6 | 436.9 | 420 | 643.7 | 79.2 | 16.5 | 139.7 | 6.1 | 230.1 | 7.7 | 465.2 | 716.9 | 732.9 | 548.8 | 735.2 | 828.9 | 757.8 | 701.3 | 778.8 | 406.2 | 657.3 | 783.6 | 249.4 | 338.1 | 409.7 | 686.8 | 639.1 | 713 | 661 | 684.2 | 353.9 | 500.3 | 447.7 | 412.4 | 405 | 576.2 | 421.5
2045.1 | 1806.1 | 566.1 | 226.44 | 264.6953 | 609.1 | 464 | 437.6 | 420 | 643.4 | 79.3 | 16.5 | 139.7 | 6.1 | 207.3 | 6.1 | 465.2 | 717 | 730 | 548.8 | 735.4 | 829.3 | 758 | 701 | 773.1 | 406.5 | 657.7 | 783.1 | 249.7 | 338.4 | 409.9 | 686.9 | 639.3 | 708.7 | 661.4 | 681.8 | 354.2 | 500.8 | 448.3 | 412.8 | 405.3 | 576.4 | 421.8
2046.1 | 1807.1 | 566.8 | 226.72 | 265.0226 | 603.3 | 463.4 | 438.2 | 420.7 | 643.8 | 79.4 | 16.5 | 139.6 | 7.1 | 194.6 | 5.8 | 465.3 | 716.6 | 726.1 | 548.9 | 735.7 | 829.2 | 758.1 | 701 | 771.4 | 407.1 | 658.1 | 782.2 | 250.1 | 338.6 | 410.1 | 687.9 | 639.1 | 716.2 | 662.4 | 683.9 | 354.5 | 501.4 | 448.4 | 413.2 | 405.5 | 576.6 | 422.1
2047.1 | 1808.1 | 567 | 226.8 | 265.1161 | 604.2 | 463.2 | 437.8 | 421.7 | 643 | 79.4 | 16.5 | 139.6 | 7.4 | 232.6 | 5 | 465.4 | 716.3 | 724.3 | 549 | 735.8 | 829.4 | 758.2 | 701.5 | 772.1 | 407.2 | 658.5 | 782.7 | 250.4 | 338.9 | 410.3 | 688.1 | 637.7 | 720.7 | 663 | 686.5 | 354.8 | 501.3 | 448.5 | 413.4 | 405.7 | 576.9 | 422.4
2048.1 | 1809.1 | 565.7 | 226.28 | 264.5083 | 604.4 | 462.1 | 437.4 | 421.8 | 642.8 | 79.4 | 16.5 | 139.7 | 7.5 | 254.7 | 5.5 | 465.5 | 716.2 | 724 | 549.2 | 736 | 828.7 | 758.2 | 701.1 | 772.1 | 407.7 | 659 | 782.8 | 250.8 | 339.2 | 410.7 | 687.7 | 637 | 725.1 | 663.2 | 687.5 | 355 | 501.3 | 448.1 | 413.7 | 405.7 | 577.1 | 422.8
2049.1 | 1810.1 | 568.2 | 227.28 | 265.6772 | 603.3 | 461.6 | 438.7 | 421.1 | 644.5 | 79.3 | 16.5 | 139.7 | 7.1 | 245.3 | 6.9 | 465.5 | 715.3 | 728.9 | 549.3 | 736.2 | 828.2 | 758.5 | 702.1 | 772.5 | 408 | 659.4 | 783.1 | 251.1 | 339.4 | 411.1 | 687.7 | 638.1 | 729.9 | 663.6 | 689 | 355.1 | 501.2 | 447.5 | 413.9 | 405.7 | 577.3 | 423
2050.1 | 1811.1 | 566.8 | 226.72 | 265.0226 | 606.6 | 461.3 | 439.7 | 420.5 | 650.5 | 79.3 | 16.5 | 139.7 | 6.6 | 249.3 | 7.5 | 465.7 | 714.7 | 732.7 | 549.4 | 736.4 | 827.5 | 758.8 | 703.3 | 775.8 | 408.2 | 659.8 | 782.7 | 251.4 | 339.7 | 411.6 | 687.5 | 640.5 | 729.2 | 663.9 | 688.7 | 355.1 | 500.9 | 447.4 | 414.2 | 405.8 | 577.4 | 423.3
2051.1 | 1812.1 | 565.3 | 226.12 | 264.3213 | 609 | 462.7 | 440.2 | 420.3 | 654 | 79.3 | 16.5 | 139.8 | 6.8 | 237.6 | 7.5 | 465.9 | 713.9 | 729.4 | 549.6 | 736.4 | 827.3 | 758.9 | 702.6 | 773.9 | 408.5 | 660.2 | 782.4 | 251.8 | 339.9 | 411.9 | 687.3 | 643.3 | 729.5 | 664 | 687.2 | 355.1 | 500.6 | 447 | 414.5 | 405.9 | 577.7 | 423.6
2052.1 | 1813.1 | 566.3 | 226.52 | 264.7888 | 605.7 | 463.9 | 440.7 | 419.9 | 657.6 | 79.3 | 16.5 | 139.8 | 6.9 | 230.2 | 7.4 | 466 | 713.3 | 728.6 | 549.7 | 736.7 | 826.8 | 759 | 702.5 | 770.8 | 408.8 | 660.7 | 782.8 | 252.1 | 340.1 | 412.1 | 687.2 | 645.6 | 731.8 | 664 | 686.5 | 355.1 | 500.3 | 446.5 | 414.8 | 406 | 577.9 | 423.9
2053.1 | 1814.1 | 566 | 226.4 | 264.6486 | 605.1 | 462.4 | 441 | 420.2 | 658.2 | 79.3 | 16.5 | 139.9 | 6.8 | 257.1 | 9.3 | 466.3 | 712.7 | 731.3 | 549.9 | 736.9 | 826.4 | 759.1 | 703.8 | 763.4 | 409.1 | 661.1 | 782.6 | 252.4 | 340.4 | 412.6 | 687.7 | 646.5 | 732.1 | 664.5 | 686.3 | 355.1 | 500 | 446.1 | 415.1 | 406 | 578.1 | 424.2
2054.1 | 1815.1 | 566.4 | 226.56 | 264.8356 | 602.7 | 461.2 | 441.6 | 420.6 | 660.3 | 79.4 | 16.5 | 140 | 5.8 | 266 | 10.3 | 466.6 | 712.5 | 739.7 | 550 | 737.1 | 826.3 | 759.2 | 706.5 | 766.4 | 409.7 | 661.5 | 782.9 | 252.7 | 340.7 | 412.8 | 688.1 | 647.9 | 729.8 | 664.9 | 686.2 | 355.1 | 499.8 | 446 | 415.4 | 406.2 | 578.3 | 424.5
2055.1 | 1816.1 | 566.8 | 226.72 | 265.0226 | 603 | 462.6 | 442.6 | 420.9 | 662.5 | 79.4 | 16.5 | 140.1 | 7.7 | 246.4 | 9.4 | 467.1 | 711.6 | 744.7 | 550.2 | 737.2 | 826.2 | 759.5 | 706.5 | 768.5 | 409.9 | 661.9 | 782.7 | 253 | 341 | 413.4 | 687.8 | 648.5 | 731.4 | 665 | 686.8 | 355.1 | 499.4 | 445.5 | 415.7 | 406.1 | 578.5 | 424.8
2056.1 | 1817.1 | 567.1 | 226.84 | 265.1629 | 601.2 | 466.4 | 444.1 | 421.2 | 664.8 | 79.6 | 16.5 | 140.3 | 8.2 | 279.4 | 8.5 | 467.3 | 711.3 | 748 | 550.4 | 737.5 | 826.3 | 759.7 | 706.6 | 769.5 | 410.1 | 662.4 | 781.7 | 253.3 | 341.2 | 413.7 | 687.8 | 649.8 | 730.8 | 665.1 | 686.6 | 355.1 | 499.6 | 445.1 | 416 | 406.1 | 578.8 | 425
2057.1 | 1818.1 | 564.1 | 225.64 | 263.7602 | 599.6 | 468 | 445.1 | 421.1 | 665.8 | 79.7 | 16.5 | 140.4 | 8.2 | 247 | 8 | 467.6 | 710.8 | 744 | 550.5 | 737.7 | 826.8 | 759.9 | 707.7 | 770.7 | 410.5 | 662.8 | 782.3 | 253.6 | 341.4 | 413.8 | 688.4 | 650.9 | 728.5 | 665.3 | 687.6 | 355 | 499.4 | 445.2 | 416.2 | 406.3 | 579.1 | 425.4
2058.1 | 1819.1 | 565 | 226 | 264.181 | 600.9 | 470.9 | 445.7 | 421.6 | 662.1 | 79.9 | 16.5 | 140.5 | 8.3 | 242.3 | 7.2 | 467.9 | 711.6 | 743.5 | 550.7 | 737.9 | 827.2 | 760.1 | 707.8 | 767.7 | 410.8 | 663.3 | 782.6 | 253.9 | 341.7 | 413.9 | 689.4 | 649.9 | 730 | 665.6 | 688.8 | 355.1 | 499.8 | 445.3 | 416.5 | 406.6 | 579.3 | 425.7
2059.1 | 1820.1 | 564.7 | 225.88 | 264.0407 | 601.1 | 472.1 | 445.6 | 422.1 | 656.7 | 79.9 | 16.5 | 140.8 | 7.8 | 238.3 | 7.1 | 468 | 711.7 | 742.5 | 550.7 | 738.2 | 827.6 | 760.5 | 708.3 | 764.7 | 411 | 663.7 | 782 | 254.2 | 341.9 | 414 | 689.4 | 647.5 | 729.8 | 665.7 | 688.6 | 355.2 | 500.2 | 445.3 | 416.9 | 406.7 | 579.6 | 426
2060.1 | 1821.1 | 565 | 226 | 264.181 | 600.3 | 470.8 | 444.9 | 422 | 652 | 80.1 | 16.5 | 140.9 | 8.2 | 271.3 | 7.6 | 468.1 | 711.6 | 745 | 550.8 | 738.4 | 827.5 | 760.6 | 706.6 | 767.7 | 411.4 | 664.1 | 781.6 | 254.4 | 342.2 | 414.3 | 689 | 645 | 730.6 | 665.5 | 687.4 | 355.2 | 500 | 445.1 | 417.2 | 406.8 | 579.8 | 426.3
2061.1 | 1822.1 | 565.9 | 226.36 | 264.6018 | 600.2 | 471.2 | 444.6 | 421.6 | 654.6 | 80.2 | 16.5 | 141 | 7.8 | 238.1 | 8.4 | 468.6 | 712 | 748.2 | 551 | 738.6 | 827.6 | 760.7 | 706.3 | 773.5 | 411.7 | 664.5 | 782.8 | 254.7 | 342.4 | 414.8 | 689 | 646.3 | 733.9 | 665.6 | 689.3 | 355.3 | 499.7 | 445.3 | 417.4 | 407 | 580 | 426.5
2062.1 | 1823.1 | 564.2 | 225.68 | 263.8069 | 599.8 | 472.5 | 444.7 | 420.2 | 654.8 | 80.3 | 16.5 | 141.1 | 7.3 | 256.1 | 9 | 468.9 | 713.5 | 747.9 | 551.1 | 738.7 | 827.7 | 761 | 706.3 | 774.2 | 412 | 664.9 | 783.2 | 255 | 342.6 | 415 | 688.9 | 645.5 | 733.8 | 665.4 | 689 | 355.5 | 499.4 | 445.5 | 417.7 | 407.2 | 580.2 | 426.8
2063.1 | 1824.1 | 566.9 | 226.76 | 265.0694 | 599.7 | 474.4 | 443.8 | 420.5 | 653.8 | 80.5 | 16.5 | 141.2 | 7.2 | 248.4 | 10.5 | 469.2 | 714.1 | 746.4 | 551.3 | 739 | 828.2 | 761 | 705.8 | 775.1 | 412.3 | 665.3 | 784 | 255.2 | 342.8 | 415.2 | 688.8 | 644.8 | 733.7 | 665.1 | 689.5 | 355.7 | 499.5 | 446.8 | 418.1 | 407.4 | 580.4 | 427.1
2064.1 | 1825.1 | 563.7 | 225.48 | 263.5731 | 601.9 | 475.5 | 443 | 421.2 | 653.3 | 80.6 | 16.5 | 141.2 | 7.6 | 269.8 | 8.8 | 469.9 | 713.7 | 748.8 | 551.6 | 739.1 | 828.5 | 761.1 | 704.9 | 770.2 | 412.7 | 665.7 | 783.1 | 255.5 | 343.1 | 415.3 | 689 | 645.4 | 732.9 | 665.1 | 689.8 | 356 | 500 | 447.3 | 418.4 | 407.6 | 580.6 | 427.4
2065.1 | 1826.1 | 562 | 224.8 | 262.7782 | 605.6 | 476 | 442.9 | 421.5 | 655.3 | 80.7 | 16.5 | 141.3 | 8.1 | 240.7 | 8.6 | 470.4 | 714 | 753.4 | 551.8 | 739.4 | 828.2 | 761.3 | 705.9 | 767.8 | 412.7 | 666 | 782.1 | 255.8 | 343.3 | 415.5 | 689.4 | 646.4 | 734.9 | 665.3 | 690.6 | 356.3 | 500.1 | 447.6 | 418.8 | 407.8 | 580.8 | 427.6
2066.1 | 1827.1 | 564.6 | 225.84 | 263.9939 | 608.1 | 474.8 | 442.9 | 421.8 | 656.2 | 80.8 | 16.5 | 141.4 | 7.1 | 233.2 | 8.8 | 470.6 | 714.8 | 755.7 | 551.9 | 739.8 | 827.7 | 761.5 | 706.4 | 769.3 | 413.2 | 666.4 | 781.6 | 256 | 343.5 | 415.6 | 689.8 | 646.4 | 734 | 665.7 | 691.3 | 356.7 | 500.1 | 448 | 419.1 | 408.1 | 581.1 | 428
2067.1 | 1828.1 | 565.6 | 226.24 | 264.4615 | 610 | 473.2 | 442.6 | 422.2 | 654.7 | 80.8 | 16.5 | 141.5 | 6.3 | 236 | 7.1 | 471.1 | 714.5 | 754.9 | 552.1 | 739.9 | 827.8 | 761.5 | 705.4 | 768.7 | 413.7 | 666.8 | 781.7 | 256.3 | 343.7 | 415.9 | 689.9 | 645.2 | 730.4 | 666.2 | 690.5 | 357 | 499.9 | 447.9 | 419.4 | 408.2 | 581.3 | 428.3
2068.1 | 1829.1 | 565 | 226 | 264.181 | 615.4 | 473.8 | 443.1 | 422.1 | 650.2 | 80.9 | 16.5 | 141.7 | 6.9 | 245.9 | 7.4 | 471.7 | 714.6 | 754.6 | 552.3 | 740.2 | 828.6 | 761.7 | 705.4 | 770.4 | 413.9 | 667.1 | 781.6 | 256.5 | 343.8 | 416.3 | 689.6 | 642.8 | 729.6 | 666.3 | 689.4 | 357.3 | 500 | 447.7 | 419.6 | 408.3 | 581.5 | 428.5
2069.1 | 1830.1 | 563.7 | 225.48 | 263.5731 | 610.7 | 474.9 | 443.9 | 421.7 | 650.7 | 80.9 | 16.4 | 141.8 | 7.2 | 247.5 | 8.9 | 471.8 | 714 | 753.7 | 552.5 | 740.3 | 829.1 | 761.8 | 705.9 | 768.8 | 414.2 | 667.5 | 781.5 | 256.8 | 344 | 416.9 | 689.2 | 642.5 | 729.9 | 666.2 | 690.1 | 357.5 | 500.4 | 447.6 | 419.8 | 408.3 | 581.7 | 428.8
2070.1 | 1831.1 | 565 | 226 | 264.181 | 606.3 | 474.1 | 444.7 | 421.8 | 652.8 | 81 | 16.4 | 141.9 | 6.9 | 217.5 | 8.2 | 471.9 | 714.4 | 750.9 | 552.6 | 740.5 | 829.4 | 762.1 | 705.5 | 770.3 | 414.3 | 667.9 | 781.6 | 257 | 344.3 | 417.2 | 689.3 | 642 | 731.1 | 666.2 | 690.3 | 357.6 | 500.7 | 448.4 | 420.1 | 408.5 | 581.9 | 429.1
2071.1 | 1832.1 | 565 | 226 | 264.181 | 606.4 | 472.7 | 445.2 | 421.7 | 653.5 | 81.1 | 16.4 | 142 | 7.5 | 197.5 | 6.2 | 472.1 | 714.4 | 750 | 552.7 | 740.7 | 829.5 | 762.4 | 705.2 | 770.3 | 414.6 | 668.2 | 781.2 | 257.2 | 344.6 | 417.3 | 689.3 | 642.3 | 730.2 | 666.1 | 690.5 | 357.8 | 500.3 | 449.1 | 420.4 | 408.7 | 582.2 | 429.4
2072.1 | 1833.1 | 566.4 | 226.56 | 264.8356 | 608 | 471.7 | 445.5 | 421.6 | 651 | 81.1 | 16.4 | 142.2 | 8.2 | 244.1 | 5.2 | 472.4 | 714.5 | 747.5 | 552.8 | 740.9 | 830 | 762.7 | 704.3 | 773.5 | 415 | 668.5 | 782.2 | 257.5 | 344.8 | 417.5 | 689.2 | 641 | 729.7 | 665.7 | 690.2 | 358 | 500.1 | 449.8 | 420.6 | 408.9 | 582.5 | 429.6
2073.1 | 1834.1 | 564.6 | 225.84 | 263.9939 | 609.8 | 471.6 | 446.2 | 422 | 647.3 | 81.1 | 16.4 | 142.2 | 8.2 | 235.6 | 6.2 | 472.5 | 714.9 | 747.4 | 552.9 | 741.1 | 830.5 | 762.9 | 703.8 | 776.6 | 415.3 | 668.8 | 783.1 | 257.7 | 345 | 417.8 | 688.7 | 640 | 723.7 | 665.1 | 690.4 | 358.2 | 500.4 | 449.9 | 421 | 409.2 | 582.7 | 429.9
2074.1 | 1835.1 | 565 | 226 | 264.181 | 608.2 | 472.3 | 445.8 | 422.6 | 643.9 | 81.1 | 16.4 | 142 | 7.1 | 216.7 | 5.4 | 472.7 | 715.2 | 746.7 | 553.1 | 741.4 | 831.7 | 763.1 | 703.2 | 778.4 | 415.8 | 669.1 | 783.7 | 257.9 | 345.3 | 417.9 | 688.9 | 639.2 | 721.8 | 664.9 | 689.9 | 358.5 | 500.4 | 450.1 | 421.3 | 409.4 | 583 | 430.2
2075.1 | 1836.1 | 565.9 | 226.36 | 264.6018 | 611.8 | 473.9 | 445.5 | 422.9 | 641.3 | 81.1 | 16.4 | 142 | 6 | 245.1 | 5.2 | 473 | 715.6 | 743.8 | 553.2 | 741.7 | 832 | 763.3 | 702.8 | 781.1 | 415.9 | 669.4 | 783.9 | 258.2 | 345.5 | 418.1 | 689.6 | 637.9 | 722.3 | 665 | 692 | 358.8 | 500.1 | 450.5 | 421.7 | 409.7 | 583.2 | 430.4
2076.1 | 1837.1 | 565.8 | 226.32 | 264.555 | 610.8 | 475.7 | 446.3 | 422.9 | 639.6 | 81.1 | 16.4 | 141.9 | 5.9 | 235.6 | 6.4 | 473.3 | 715.2 | 744.8 | 553.4 | 741.8 | 832 | 763.4 | 702.7 | 781.5 | 416.5 | 669.7 | 784.3 | 258.4 | 345.7 | 418.4 | 689.4 | 637 | 721.7 | 664.8 | 692.2 | 359.1 | 500.3 | 450.7 | 422.1 | 409.8 | 583.5 | 430.7
2077.1 | 1838.1 | 565.4 | 226.16 | 264.368 | 606.8 | 475.7 | 446.7 | 423.5 | 641.6 | 81.2 | 16.4 | 141.9 | 6.1 | 227.6 | 5.8 | 473.9 | 715.1 | 742.3 | 553.7 | 741.9 | 832 | 763.6 | 702.7 | 780.1 | 416.6 | 670 | 783.7 | 258.6 | 346 | 418.6 | 689.6 | 638 | 723.8 | 664.8 | 693.1 | 359.3 | 501.1 | 451.1 | 422.6 | 410.1 | 583.7 | 431
2078.1 | 1839.1 | 565.9 | 226.36 | 264.6018 | 603.5 | 476 | 446.1 | 423.7 | 641.2 | 81.3 | 16.4 | 142.1 | 6.9 | 216.4 | 5.1 | 474.2 | 714 | 737.4 | 553.9 | 742.1 | 832.7 | 763.7 | 702.2 | 772.9 | 416.7 | 670.3 | 782.5 | 258.8 | 346.2 | 418.8 | 689.1 | 636.5 | 717.2 | 664.6 | 691.7 | 359.6 | 501.9 | 451.4 | 422.9 | 410.3 | 584 | 431.3
2079.1 | 1840.1 | 567 | 226.8 | 265.1161 | 603.4 | 476.1 | 445.6 | 424.4 | 635.9 | 81.4 | 16.4 | 142.1 | 6.9 | 248.3 | 5.4 | 474.1 | 713.5 | 730.9 | 554 | 742.3 | 834.3 | 763.5 | 702.1 | 768.7 | 417.1 | 670.5 | 781.5 | 259.1 | 346.5 | 419 | 688.5 | 633.5 | 713.7 | 664.1 | 689.5 | 359.8 | 502.7 | 451.6 | 423.3 | 410.5 | 584.3 | 431.6
2080.1 | 1841.1 | 567.4 | 226.96 | 265.3032 | 602.7 | 477.4 | 445.9 | 424.8 | 632.5 | 81.4 | 16.4 | 142.2 | 6.7 | 251 | 5.3 | 474.2 | 713.7 | 728.2 | 554.1 | 742.3 | 834.2 | 763.4 | 703 | 772 | 417.1 | 670.8 | 781.4 | 259.3 | 346.8 | 419.2 | 688 | 631.4 | 712.5 | 663.3 | 687.1 | 360 | 502.7 | 452 | 423.5 | 410.7 | 584.4 | 431.8
2081.1 | 1842.1 | 566.9 | 226.76 | 265.0694 | 604.5 | 480.4 | 445.4 | 425 | 632.8 | 81.5 | 16.4 | 142.2 | 6.6 | 242.8 | 5.6 | 474.5 | 713.4 | 727.7 | 554.3 | 742.4 | 833 | 763.4 | 703.4 | 771 | 417.4 | 671.2 | 780.6 | 259.5 | 347.1 | 419.3 | 688.2 | 631.8 | 714.3 | 663.1 | 687.8 | 360.2 | 502.1 | 452.6 | 423.7 | 411.1 | 584.6 | 432.1
2082.1 | 1843.1 | 565.5 | 226.2 | 264.4148 | 599.9 | 482 | 444.6 | 425.3 | 635.1 | 81.6 | 16.4 | 142.3 | 6.4 | 262.5 | 5.8 | 474.9 | 713.7 | 729.4 | 554.5 | 742.5 | 832.5 | 763.6 | 704.1 | 766.9 | 417.8 | 671.5 | 779.5 | 259.7 | 347.4 | 419.5 | 689.5 | 634 | 710.9 | 663.9 | 687.6 | 360.5 | 502.7 | 453.4 | 424.1 | 411.5 | 584.8 | 432.4
2083.1 | 1844.1 | 567.4 | 226.96 | 265.3032 | 596 | 480.4 | 444.9 | 426.1 | 637.4 | 81.6 | 16.4 | 142.5 | 7.1 | 231.1 | 5.8 | 475.3 | 713.7 | 731.5 | 554.7 | 742.7 | 832.5 | 763.7 | 704.3 | 761.9 | 418 | 671.8 | 779.3 | 259.9 | 347.7 | 419.8 | 690.4 | 635.5 | 710.1 | 664.5 | 689.5 | 360.9 | 503.1 | 454 | 424.5 | 411.7 | 585.1 | 432.7
2084.1 | 1845.1 | 567 | 226.8 | 265.1161 | 597.5 | 481.6 | 445.3 | 426.6 | 639.3 | 81.7 | 16.4 | 142.6 | 7.7 | 222.2 | 5.7 | 475.7 | 714.5 | 729.7 | 554.9 | 742.9 | 832 | 763.8 | 704.5 | 760.6 | 418.3 | 672.2 | 779.8 | 260.1 | 348.1 | 419.9 | 690.7 | 636.6 | 708.1 | 665.2 | 691 | 361.3 | 503.9 | 454.6 | 424.9 | 412.1 | 585.4 | 433
2085.1 | 1846.1 | 567.2 | 226.88 | 265.2096 | 596.5 | 481.7 | 444.7 | 426.7 | 639 | 81.8 | 16.4 | 142.7 | 7.8 | 237.7 | 7 | 475.7 | 714.9 | 727.7 | 555.1 | 743.1 | 832.2 | 763.9 | 704.8 | 759.6 | 418.5 | 672.5 | 779.3 | 260.4 | 348.4 | 420.1 | 690.9 | 635.9 | 708.5 | 665.9 | 690.9 | 361.7 | 504.7 | 455.2 | 425.4 | 412.3 | 585.8 | 433.3
2086.1 | 1847.1 | 566.2 | 226.48 | 264.7421 | 595.8 | 479.2 | 444 | 426.4 | 635.6 | 82 | 16.4 | 142.8 | 8.1 | 234.9 | 7.2 | 475.9 | 714.4 | 728.7 | 555.2 | 743.3 | 832.7 | 764 | 705 | 756.1 | 419 | 672.8 | 778.8 | 260.6 | 348.9 | 420.4 | 691.5 | 634.3 | 707.1 | 667 | 688.2 | 362 | 504.7 | 455.7 | 425.7 | 412.5 | 586 | 433.6
2087.1 | 1848.1 | 565.8 | 226.32 | 264.555 | 595.7 | 477.1 | 443.6 | 426.4 | 637.3 | 82.2 | 16.4 | 142.9 | 7.6 | 253.6 | 7.7 | 476.2 | 714.4 | 733 | 555.4 | 743.4 | 833.6 | 764.1 | 705.4 | 756.9 | 419.1 | 673.1 | 779.1 | 260.8 | 349.4 | 420.7 | 692 | 634.6 | 710.5 | 667.5 | 691 | 362.3 | 504.5 | 456.6 | 426.2 | 412.8 | 586.3 | 433.9
2088.1 | 1849.1 | 565.8 | 226.32 | 264.555 | 599.9 | 474.9 | 443.9 | 426.7 | 641.2 | 82.3 | 16.4 | 143 | 7.3 | 237.3 | 8.9 | 476.4 | 714.5 | 733.9 | 555.6 | 743.6 | 833.6 | 764.3 | 706 | 755.5 | 419.2 | 673.4 | 778.3 | 261.1 | 349.8 | 420.8 | 692 | 636.8 | 715 | 667.9 | 692.4 | 362.6 | 504.5 | 457.4 | 426.6 | 413 | 586.5 | 434.2
2089.1 | 1850.1 | 566.3 | 226.52 | 264.7888 | 599.7 | 473.1 | 444.3 | 426.9 | 642.7 | 82.3 | 16.4 | 143 | 7.2 | 248.5 | 7.7 | 476.4 | 715.1 | 733.6 | 555.7 | 743.8 | 833.8 | 764.3 | 704.9 | 756.4 | 419.6 | 673.8 | 778.6 | 261.3 | 350.2 | 420.9 | 691.7 | 636.9 | 714.7 | 668 | 691.7 | 362.9 | 504.7 | 457.7 | 427 | 413.2 | 586.8 | 434.5
2090.1 | 1851.1 | 566.7 | 226.68 | 264.9759 | 600.4 | 472.6 | 443.5 | 427.4 | 641.3 | 82.3 | 16.4 | 143.1 | 7 | 235.5 | 6.9 | 476.3 | 715 | 731.8 | 555.7 | 743.9 | 835 | 764.5 | 705.5 | 756.1 | 419.8 | 674.2 | 779.1 | 261.5 | 350.5 | 421.3 | 691.5 | 636.4 | 716.7 | 667.9 | 691.9 | 363.2 | 504.7 | 458.2 | 427.4 | 413.4 | 587 | 434.8
2091.1 | 1852.1 | 566.2 | 226.48 | 264.7421 | 600.3 | 472.5 | 443.3 | 427.1 | 639 | 82.3 | 16.4 | 143.2 | 7.1 | 246 | 8.1 | 476.4 | 715.6 | 730.1 | 555.8 | 744 | 835.9 | 764.7 | 706.1 | 753 | 420.3 | 674.5 | 778.9 | 261.7 | 350.8 | 421.5 | 691 | 634.8 | 715.1 | 667.7 | 689.8 | 363.4 | 504.4 | 458.7 | 427.7 | 413.8 | 587.3 | 435.1
2092.1 | 1853.1 | 568.7 | 227.48 | 265.911 | 601.3 | 472.5 | 444.2 | 426.9 | 639.4 | 82.4 | 16.4 | 143.4 | 7.7 | 234.2 | 9.2 | 476.6 | 716 | 730.4 | 556 | 744.1 | 836.2 | 764.8 | 706.5 | 750.8 | 420.4 | 674.9 | 780 | 261.9 | 351.1 | 421.7 | 692.2 | 635.8 | 714.7 | 668.4 | 689.8 | 363.7 | 504.9 | 459.3 | 428.2 | 414.1 | 587.5 | 435.4
2093.1 | 1854.1 | 569.6 | 227.84 | 266.3318 | 599.7 | 474.1 | 444.6 | 427 | 644.1 | 82.4 | 16.4 | 143.4 | 8.5 | 230.6 | 8.5 | 476.6 | 715.7 | 728.9 | 556.1 | 744.3 | 836.5 | 764.8 | 707.2 | 748.7 | 420.7 | 675.4 | 779.1 | 262.1 | 351.3 | 422 | 692.9 | 637.8 | 713.4 | 669.3 | 690.5 | 364 | 506 | 459.7 | 428.8 | 414.4 | 587.8 | 435.7
2094.1 | 1855.1 | 567.8 | 227.12 | 265.4902 | 602.1 | 474.3 | 444.1 | 428.1 | 645.6 | 82.4 | 16.4 | 143.4 | 7.7 | 246.8 | 7.8 | 476.7 | 715.4 | 732.6 | 556.2 | 744.5 | 836.9 | 765 | 707.6 | 749.1 | 420.8 | 675.8 | 779.3 | 262.3 | 351.6 | 422.2 | 693.3 | 638.2 | 714.7 | 670 | 690.9 | 364.3 | 506.7 | 460 | 429.2 | 414.6 | 588.1 | 436.1
2095.1 | 1856.1 | 567.2 | 226.88 | 265.2096 | 603.2 | 474.5 | 443.7 | 429.1 | 645.3 | 82.3 | 16.3 | 143.4 | 8 | 241.7 | 7 | 476.8 | 716.4 | 740.2 | 556.3 | 744.7 | 837 | 765.1 | 707.6 | 751.5 | 421.6 | 676.2 | 779.4 | 262.5 | 351.8 | 422.3 | 693.7 | 638.5 | 722.4 | 670.7 | 692.6 | 364.6 | 506.8 | 460.2 | 429.6 | 414.8 | 588.4 | 436.4
2096.1 | 1857.1 | 567.9 | 227.16 | 265.537 | 605.7 | 475.8 | 444.4 | 429 | 645.1 | 82.3 | 16.3 | 143.7 | 8.7 | 226.2 | 6.5 | 477 | 716.7 | 741.2 | 556.4 | 744.8 | 837.8 | 765.2 | 706.7 | 757 | 421.4 | 676.7 | 779.8 | 262.7 | 352 | 422.7 | 693.3 | 637.9 | 725.4 | 670.9 | 693 | 364.9 | 506.3 | 459.8 | 429.8 | 414.9 | 588.6 | 436.7
2097.1 | 1858.1 | 566.9 | 226.76 | 265.0694 | 606.3 | 477.3 | 444.6 | 428.4 | 643.2 | 82.3 | 16.3 | 143.8 | 8.7 | 211.9 | 5.9 | 477.2 | 717.1 | 739.3 | 556.5 | 745 | 838.1 | 765.3 | 706.1 | 759.9 | 421.5 | 677.1 | 780.6 | 262.9 | 352.3 | 423 | 692.8 | 636.3 | 725.3 | 670.7 | 692 | 365.1 | 506.3 | 459.6 | 430.1 | 414.9 | 588.8 | 436.9
2098.1 | 1859.1 | 567 | 226.8 | 265.1161 | 605 | 477.4 | 446.2 | 428 | 641.2 | 82.4 | 16.3 | 143.9 | 8.2 | 222.6 | 5.1 | 477.4 | 717.4 | 739.9 | 556.7 | 745.2 | 838.8 | 765.3 | 705.8 | 763.3 | 422 | 677.5 | 781.4 | 263.1 | 352.4 | 423.2 | 692.7 | 636.1 | 721.5 | 670.4 | 691.1 | 365.2 | 506.4 | 459.5 | 430.4 | 415.1 | 589 | 437.2
2099.1 | 1860.1 | 567 | 226.8 | 265.1161 | 604.8 | 479.6 | 446.3 | 427.9 | 640 | 82.5 | 16.3 | 144 | 8.4 | 258.6 | 6 | 477.6 | 716.7 | 741.5 | 556.8 | 745.3 | 839.4 | 765.4 | 705.4 | 767 | 422.3 | 677.9 | 782.2 | 263.3 | 352.6 | 423.5 | 692.9 | 635.1 | 724.7 | 670.6 | 691.9 | 365.4 | 506.9 | 459.5 | 430.9 | 415.2 | 589.2 | 437.5
2100.1 | 1861.1 | 567.3 | 226.92 | 265.2564 | 602.1 | 482.1 | 446.3 | 428.2 | 640.7 | 82.5 | 16.3 | 144.1 | 8.4 | 232.5 | 7 | 477.8 | 716.1 | 744.8 | 557 | 745.4 | 839.6 | 765.6 | 705 | 767.2 | 422.2 | 678.3 | 781.7 | 263.5 | 352.8 | 424 | 692.7 | 635.6 | 726.3 | 670.6 | 692.7 | 365.6 | 507.1 | 459.1 | 431.3 | 415.2 | 589.4 | 437.8
2101.1 | 1862.1 | 567.6 | 227.04 | 265.3967 | 600.5 | 484.9 | 446.3 | 428.5 | 646.1 | 82.6 | 16.3 | 144.2 | 7.6 | 258.6 | 7.9 | 478.2 | 715 | 745.4 | 557.2 | 745.5 | 838.7 | 765.9 | 705.2 | 764 | 422.5 | 678.7 | 780.7 | 263.7 | 353.1 | 424.7 | 693.1 | 638.7 | 729.7 | 671.1 | 691.7 | 365.6 | 506.4 | 458.8 | 431.6 | 415.3 | 589.6 | 438
2102.1 | 1863.1 | 566.7 | 226.68 | 264.9759 | 598.8 | 485.8 | 445.7 | 428.1 | 651.8 | 82.6 | 16.3 | 144.3 | 7.2 | 223.4 | 8.8 | 478.4 | 714.2 | 744.4 | 557.4 | 745.7 | 838.4 | 766.1 | 706.3 | 764.1 | 422.9 | 679.2 | 780.1 | 263.9 | 353.3 | 425 | 693 | 641.4 | 729.9 | 671.3 | 692.9 | 365.7 | 506 | 458.6 | 432 | 415.4 | 589.8 | 438.3
2103.1 | 1864.1 | 566.7 | 226.68 | 264.9759 | 599.1 | 484.5 | 445.8 | 427.5 | 652.5 | 82.7 | 16.3 | 144.6 | 8.4 | 243.1 | 10.1 | 478.6 | 714.1 | 746.1 | 557.6 | 745.9 | 837.8 | 766.2 | 707.3 | 763.4 | 423 | 679.6 | 779.9 | 264.1 | 353.4 | 425.1 | 693 | 641 | 723.6 | 671.1 | 690.6 | 365.8 | 506 | 458.8 | 432.3 | 415.6 | 590 | 438.6
2104.1 | 1865.1 | 566.7 | 226.68 | 264.9759 | 596.7 | 485.2 | 446.1 | 427.9 | 652 | 82.7 | 16.3 | 144.9 | 10.4 | 236 | 9.3 | 478.8 | 714.1 | 744.1 | 557.8 | 746 | 837.3 | 766.4 | 708.7 | 759 | 423.4 | 680 | 779 | 264.3 | 353.6 | 425 | 693.8 | 642 | 722.9 | 671.4 | 693.5 | 366 | 506.6 | 459.8 | 433 | 416.1 | 590.2 | 438.9
2105.1 | 1866.1 | 566.8 | 226.72 | 265.0226 | 597.5 | 486.9 | 445.3 | 428.8 | 652.9 | 82.8 | 16.3 | 145 | 9.8 | 175.6 | 8.5 | 479.1 | 713.7 | 743.1 | 558 | 746.1 | 837.9 | 766.6 | 708.6 | 754.7 | 423.6 | 680.4 | 778.1 | 264.5 | 353.8 | 425.2 | 694.8 | 642.5 | 726.2 | 672.4 | 694.3 | 366.3 | 508.2 | 460.5 | 433.6 | 416.4 | 590.4 | 439.2
2106.1 | 1867.1 | 568.1 | 227.24 | 265.6305 | 598.2 | 488 | 443.5 | 429.4 | 652.8 | 82.8 | 16.3 | 145.1 | 9.4 | 253.4 | 5.9 | 479.6 | 713.1 | 738.2 | 558.2 | 746.2 | 837.9 | 766.6 | 708.2 | 746.9 | 423.8 | 680.7 | 777.1 | 264.7 | 354 | 425.3 | 695.4 | 642.8 | 726 | 673.1 | 693.5 | 366.7 | 508.5 | 460.6 | 434 | 416.6 | 590.7 | 439.5
2107.1 | 1868.1 | 566.5 | 226.6 | 264.8823 | 598.2 | 487.3 | 443.1 | 429.8 | 651 | 82.8 | 16.3 | 145.1 | 7.6 | 236.1 | 6.3 | 480 | 713.9 | 740.8 | 558.5 | 746.4 | 837 | 766.7 | 708.1 | 744.5 | 424 | 681.1 | 776.5 | 264.9 | 354.2 | 425.4 | 696 | 643.2 | 721.4 | 674.1 | 692.9 | 367 | 510.1 | 460.9 | 434.6 | 417 | 590.9 | 439.8
2108.1 | 1869.1 | 568 | 227.2 | 265.5837 | 595.7 | 486.4 | 442.4 | 429.4 | 650.3 | 82.9 | 16.3 | 145.2 | 8.2 | 250 | 9.3 | 480.4 | 715.1 | 741.8 | 558.7 | 746.5 | 836.1 | 766.7 | 709.1 | 740.1 | 424.2 | 681.5 | 774.4 | 265.1 | 354.4 | 425.7 | 696.7 | 644.5 | 720.1 | 674.8 | 691.4 | 367.4 | 511.3 | 461.4 | 435.2 | 417.3 | 591.2 | 440.1
2109.1 | 1870.1 | 566.6 | 226.64 | 264.9291 | 598.9 | 489.5 | 441.1 | 430.5 | 650.9 | 82.9 | 16.3 | 145.2 | 7.7 | 231.2 | 9 | 480.4 | 716.3 | 744.1 | 558.9 | 746.7 | 836.5 | 766.7 | 708.6 | 742.9 | 424.8 | 681.9 | 775 | 265.1 | 354.6 | 425.9 | 697.1 | 644.9 | 719.1 | 675.6 | 693 | 367.9 | 512.7 | 461.8 | 435.9 | 417.6 | 591.5 | 440.5
2110.1 | 1871.1 | 566.6 | 226.64 | 264.9291 | 599.8 | 496.5 | 441 | 431.5 | 651.3 | 82.9 | 16.3 | 145.2 | 8.2 | 229.6 | 8.4 | 480.3 | 716.8 | 743.7 | 559 | 746.9 | 837.6 | 766.7 | 708.2 | 748.2 | 425.3 | 682.3 | 775.8 | 265.1 | 354.8 | 426.2 | 697.3 | 644.9 | 715.6 | 675.9 | 693.6 | 368.3 | 513.6 | 464 | 436.4 | 418.1 | 591.9 | 440.8
2111.1 | 1872.1 | 567.7 | 227.08 | 265.4434 | 599.9 | 501.7 | 441.1 | 431.4 | 649.2 | 82.9 | 16.3 | 145.2 | 8.6 | 254.8 | 8.4 | 480.4 | 716.7 | 739.2 | 559.1 | 747 | 837.5 | 766.9 | 708 | 746.4 | 425.3 | 682.6 | 775.7 | 265.2 | 355 | 426.3 | 697.2 | 643.7 | 713.6 | 675.9 | 693.4 | 368.7 | 514.1 | 465.8 | 436.9 | 418.9 | 592.2 | 441.1
2112.1 | 1873.1 | 566 | 226.4 | 264.6486 | 597.8 | 501.2 | 440.4 | 431.1 | 647.2 | 82.9 | 16.3 | 145.3 | 9.1 | 233.3 | 9.5 | 480.7 | 717.1 | 734.1 | 559.3 | 747.1 | 836.2 | 767.2 | 708.2 | 740 | 425.4 | 682.9 | 774.5 | 265.4 | 355.1 | 426.5 | 697.4 | 644.4 | 713.2 | 676.2 | 694.3 | 369.2 | 514.7 | 468 | 437.6 | 419.8 | 592.5 | 441.4
2113.1 | 1874.1 | 567.8 | 227.12 | 265.4902 | 593.8 | 500 | 438.3 | 432.1 | 645.6 | 82.9 | 16.3 | 145.4 | 9.4 | 208.3 | 8 | 480.8 | 716.9 | 729.1 | 559.5 | 747.3 | 835.8 | 767.3 | 708.3 | 737.6 | 425.7 | 683.2 | 773.3 | 265.7 | 355.3 | 426.6 | 697.8 | 644.1 | 706.9 | 676.8 | 693.1 | 369.8 | 516.3 | 469.3 | 438.2 | 420.1 | 592.7 | 441.8
2114.1 | 1875.1 | 568.3 | 227.32 | 265.724 | 591.5 | 497.9 | 438.7 | 432.8 | 646.6 | 82.9 | 16.3 | 145.4 | 9 | 230 | 6.6 | 480.9 | 716.9 | 725.2 | 559.6 | 747.4 | 836.7 | 767.3 | 708.1 | 738.7 | 426 | 683.5 | 773.8 | 266.2 | 355.5 | 427.1 | 698 | 644.3 | 710.4 | 677 | 693.4 | 370.4 | 516.7 | 469.5 | 438.6 | 420.3 | 593 | 442.1
2115.1 | 1876.1 | 567.2 | 226.88 | 265.2096 | 590.9 | 497 | 439.8 | 433.1 | 645.9 | 83 | 16.3 | 145.4 | 8.1 | 234.3 | 7.1 | 481 | 716.2 | 724 | 559.7 | 747.5 | 837.3 | 767.2 | 708.5 | 739.1 | 426.7 | 683.7 | 774 | 266.4 | 355.8 | 427.3 | 697.5 | 642.9 | 711.2 | 676.9 | 693.4 | 370.9 | 516.3 | 469.1 | 438.9 | 420.4 | 593.2 | 442.4
2116.1 | 1877.1 | 565.4 | 226.16 | 264.368 | 590.6 | 496.3 | 439 | 432.3 | 642.3 | 83 | 16.3 | 145.3 | 8.1 | 212.2 | 7.7 | 481.2 | 716 | 723.1 | 559.9 | 747.7 | 837.8 | 767.2 | 708.9 | 737.4 | 426.8 | 684.1 | 773.8 | 266.6 | 355.9 | 427.5 | 697 | 640.9 | 712.3 | 676.4 | 692 | 371.3 | 515.8 | 468.5 | 439.3 | 420.5 | 593.4 | 442.7
2117.1 | 1878.1 | 565.6 | 226.24 | 264.4615 | 587.9 | 497.1 | 437.9 | 431.1 | 642.6 | 83 | 16.3 | 145.2 | 8.4 | 207.1 | 8.1 | 481.6 | 715.9 | 726.3 | 560.1 | 747.9 | 837.7 | 767.4 | 709.4 | 741.6 | 426.9 | 684.4 | 775 | 266.6 | 356.1 | 427.8 | 696.6 | 641.3 | 710.3 | 675.7 | 691.8 | 371.5 | 516.5 | 468.1 | 439.9 | 420.6 | 593.6 | 443
2118.1 | 1879.1 | 565.6 | 226.24 | 264.4615 | 584.4 | 499.9 | 437.3 | 430.7 | 642.4 | 83 | 16.3 | 145.3 | 8.6 | 226.2 | 8.9 | 481.6 | 715 | 730.9 | 560.3 | 748.1 | 838.1 | 767.5 | 709.6 | 745.1 | 427.2 | 684.7 | 775.5 | 266.5 | 356.3 | 427.8 | 696.5 | 640.9 | 713.3 | 675.4 | 693.8 | 371.7 | 517.3 | 468 | 440.5 | 420.8 | 593.8 | 443.2
2119.1 | 1880.1 | 566.9 | 226.76 | 265.0694 | 581.5 | 504.3 | 437 | 431.2 | 641.1 | 83.1 | 16.3 | 145.2 | 9 | 208.5 | 9.7 | 481.7 | 714.4 | 730.9 | 560.4 | 748.1 | 838.3 | 767.7 | 709.2 | 744.6 | 427.3 | 684.9 | 774.7 | 267 | 356.5 | 428 | 696.5 | 640.5 | 713.8 | 675.4 | 695.3 | 371.9 | 517.4 | 468.9 | 441 | 421.2 | 594.1 | 443.5
2120.1 | 1881.1 | 567.4 | 226.96 | 265.3032 | 579 | 506 | 436.8 | 432.3 | 641 | 83.1 | 16.3 | 145.4 | 8.9 | 228.9 | 9 | 482 | 714.4 | 728.8 | 560.6 | 748.1 | 838 | 767.8 | 709.3 | 742.3 | 427.7 | 685.2 | 774.8 | 267.1 | 356.7 | 428.3 | 696.9 | 639.9 | 713.4 | 675.5 | 695.6 | 372.3 | 517.9 | 471.4 | 441.6 | 421.9 | 594.4 | 443.8
2121.1 | 1882.1 | 567.7 | 227.08 | 265.4434 | 574.9 | 510.6 | 436.9 | 432.7 | 640.3 | 83.2 | 16.3 | 145.7 | 7.2 | 234 | 8 | 482.2 | 714.2 | 730.1 | 560.8 | 748.3 | 838.1 | 767.8 | 708.8 | 741.9 | 427.9 | 685.4 | 774.8 | 267.7 | 356.8 | 428.3 | 697.5 | 639.2 | 714.3 | 675.9 | 695 | 372.6 | 517.7 | 471.6 | 441.9 | 422.2 | 594.6 | 444.1
2122.1 | 1883.1 | 566.4 | 226.56 | 264.8356 | 571.8 | 508.7 | 437.4 | 432.6 | 641.8 | 83.2 | 16.3 | 145.9 | 6.7 | 211.7 | 8.1 | 482.3 | 713.1 | 732.2 | 560.9 | 748.4 | 838.6 | 767.8 | 708.8 | 740.1 | 428.3 | 685.6 | 774.3 | 267.3 | 357 | 428.7 | 697.5 | 638.8 | 717.9 | 676 | 695.9 | 373 | 516.9 | 471.1 | 442.2 | 422.2 | 594.8 | 444.4
2123.1 | 1884.1 | 566.8 | 226.72 | 265.0226 | 571.6 | 506.8 | 437.8 | 432.5 | 641.3 | 83.3 | 16.3 | 146 | 8 | 242.7 | 9 | 482.3 | 712.9 | 738.7 | 561 | 748.6 | 838.6 | 767.7 | 708.7 | 740.3 | 428.8 | 686 | 773.7 | 267.5 | 357.2 | 429.1 | 696.9 | 637.5 | 716.6 | 675.6 | 694.9 | 373.2 | 515.7 | 470.5 | 442.3 | 422.3 | 595 | 444.7
2124.1 | 1885.1 | 566.7 | 226.68 | 264.9759 | 571.3 | 508.6 | 438.1 | 432 | 639.7 | 83.3 | 16.3 | 146.1 | 8.4 | 231.6 | 8 | 482.5 | 712.8 | 733.1 | 561.1 | 748.6 | 839.1 | 767.5 | 708.5 | 740.7 | 429 | 686.2 | 773.2 | 267.8 | 357.4 | 429.3 | 696.7 | 636 | 716.5 | 675 | 695.1 | 373.4 | 514.4 | 470.1 | 442.4 | 422.4 | 595.2 | 444.9
2125.1 | 1886.1 | 567.1 | 226.84 | 265.1629 | 569.5 | 511.8 | 438.3 | 431.6 | 639.2 | 83.3 | 16.3 | 146.2 | 8.1 | 249.9 | 8.1 | 483 | 711.5 | 729.8 | 561.4 | 748.6 | 838.9 | 767.5 | 708.1 | 734.8 | 429.4 | 686.5 | 772.3 | 268.3 | 357.6 | 429.6 | 696.2 | 635.1 | 716 | 674.4 | 694.5 | 373.5 | 513.8 | 469.8 | 442.6 | 422.5 | 595.3 | 445.2
2126.1 | 1887.1 | 567.2 | 226.88 | 265.2096 | 569.3 | 511.4 | 438.3 | 430.3 | 639.2 | 83.2 | 16.3 | 146.2 | 7.2 | 252.3 | 9.5 | 482.9 | 711.3 | 728.6 | 561.5 | 748.9 | 838.8 | 767.2 | 708.1 | 734.6 | 429.6 | 686.8 | 771.6 | 268.4 | 357.8 | 429.6 | 696 | 634.6 | 711 | 674.2 | 691 | 373.6 | 513.4 | 469.9 | 442.8 | 422.6 | 595.5 | 445.5
2127.1 | 1888.1 | 567.2 | 226.88 | 265.2096 | 568.5 | 508.5 | 439.3 | 429.4 | 640.9 | 83.1 | 16.2 | 146.4 | 7.9 | 229.5 | 8.6 | 483.1 | 710.9 | 727.3 | 561.6 | 748.9 | 839 | 767 | 710 | 729.3 | 429.9 | 687.1 | 771.1 | 268.7 | 358 | 429.8 | 696.4 | 633.5 | 710.8 | 674.5 | 689.6 | 373.6 | 513.7 | 469.6 | 443.2 | 422.7 | 595.6 | 445.7
2128.1 | 1889.1 | 566.8 | 226.72 | 265.0226 | 569.1 | 510 | 439.1 | 429.7 | 641.5 | 83.1 | 16.2 | 146.6 | 9 | 223.9 | 9.3 | 483.3 | 711.2 | 728.8 | 561.8 | 749 | 839.4 | 766.8 | 711.8 | 729.5 | 430.1 | 687.4 | 770.9 | 269 | 358.2 | 430 | 697 | 632.8 | 706.1 | 674.9 | 689.2 | 373.7 | 513 | 469.4 | 443.5 | 422.9 | 595.7 | 446
2129.1 | 1890.1 | 567.5 | 227 | 265.3499 | 568.8 | 509.8 | 437.8 | 430.1 | 638.2 | 83 | 16.2 | 146.8 | 8.2 | 220 | 11.7 | 483.4 | 711.4 | 736.2 | 561.9 | 749.1 | 839.4 | 766.7 | 711.1 | 733 | 430.4 | 687.8 | 770.5 | 269.1 | 358.4 | 430.2 | 696.9 | 632.1 | 705.6 | 674.6 | 688.9 | 373.8 | 512.8 | 469.5 | 443.8 | 423.1 | 595.9 | 446.2
2130.1 | 1891.1 | 566.5 | 226.6 | 264.8823 | 568.3 | 519.3 | 437.5 | 429.9 | 642.1 | 83 | 16.2 | 147.1 | 7.9 | 207.1 | 11.5 | 483.4 | 712.7 | 736.1 | 562.1 | 749.2 | 839 | 766.7 | 710.4 | 741 | 430.7 | 688.1 | 771.6 | 269 | 358.6 | 430.5 | 697 | 634.3 | 710.2 | 674.9 | 692.7 | 373.9 | 513.2 | 469.3 | 444.2 | 423.3 | 596.1 | 446.5
2131.1 | 1892.1 | 566.2 | 226.48 | 264.7421 | 568.2 | 524.9 | 438 | 429.3 | 646.4 | 83.1 | 16.2 | 147.2 | 7.4 | 208.8 | 13.8 | 483.7 | 713.1 | 734.4 | 562.2 | 749.2 | 839.2 | 766.7 | 708.4 | 742.9 | 430.8 | 688.4 | 772.4 | 268.9 | 358.8 | 430.6 | 697 | 635.5 | 713.3 | 675.2 | 693.7 | 374.1 | 513.5 | 469.1 | 444.6 | 423.5 | 596.4 | 446.8
2132.1 | 1893.1 | 566.6 | 226.64 | 264.9291 | 566.5 | 526.6 | 437.4 | 429.9 | 646.7 | 83.2 | 16.2 | 147.4 | 6.6 | 203 | 16.2 | 484 | 713.5 | 730.6 | 562.4 | 749.3 | 839.6 | 767 | 708.2 | 741.8 | 431.1 | 688.7 | 772.3 | 269.6 | 359 | 430.9 | 697.3 | 636.2 | 715 | 675.5 | 693.9 | 374.2 | 513.6 | 469.5 | 445 | 423.7 | 596.7 | 447.1
2133.1 | 1894.1 | 567.5 | 227 | 265.3499 | 564.7 | 527.1 | 436.6 | 430.8 | 646.6 | 83.3 | 16.2 | 147.6 | 6.2 | 205 | 15.4 | 484 | 713.5 | 725.7 | 562.6 | 749.4 | 839.8 | 767 | 708.6 | 741 | 431.5 | 689.1 | 772.1 | 269.8 | 359.1 | 431.1 | 697.3 | 636.4 | 711.5 | 675.5 | 691.2 | 374.3 | 514 | 470.2 | 445.5 | 423.9 | 596.9 | 447.5
2134.1 | 1895.1 | 567 | 226.8 | 265.1161 | 565.4 | 533.5 | 437.3 | 430.6 | 645.4 | 83.4 | 16.2 | 148 | 7.2 | 210.7 | 14.2 | 484.1 | 713.3 | 721.8 | 562.7 | 749.5 | 839.9 | 767.2 | 709.1 | 740.3 | 431.9 | 689.4 | 772.7 | 270 | 359.3 | 431.3 | 697.8 | 636.9 | 708.9 | 676 | 690.8 | 374.5 | 514.4 | 470.9 | 445.9 | 424.2 | 597.2 | 447.8
2135.1 | 1896.1 | 567.1 | 226.84 | 265.1629 | 565.2 | 536.4 | 437.5 | 430.4 | 646.7 | 83.4 | 16.2 | 148.1 | 7.8 | 206.2 | 14 | 484.1 | 713.5 | 719.2 | 562.8 | 749.6 | 839.8 | 767.2 | 709 | 741.5 | 432.1 | 689.7 | 772.5 | 270.2 | 359.4 | 431.6 | 698.7 | 637.7 | 707.6 | 677 | 690.8 | 374.8 | 514.8 | 471.3 | 446.3 | 424.5 | 597.4 | 448.1
2136.1 | 1897.1 | 565.9 | 226.36 | 264.6018 | 563.3 | 532.9 | 437.1 | 431 | 644.2 | 83.4 | 16.2 | 148.2 | 8.9 | 205.9 | 14.5 | 484.2 | 713.8 | 716.7 | 562.9 | 749.7 | 839.8 | 767.2 | 709.1 | 735.7 | 432.6 | 690.1 | 771.3 | 270.3 | 359.6 | 431.9 | 699.3 | 637.2 | 702.9 | 677.8 | 690.9 | 375.2 | 514.5 | 471.3 | 446.4 | 424.8 | 597.7 | 448.4
2137.1 | 1898.1 | 565.3 | 226.12 | 264.3213 | 561.4 | 532.3 | 436.7 | 431.5 | 642.1 | 83.5 | 16.2 | 148.2 | 7.5 | 207.9 | 16.5 | 484.3 | 713 | 713.8 | 563 | 749.7 | 840.3 | 767.2 | 709.2 | 735.8 | 432.6 | 690.3 | 771.7 | 270.5 | 359.8 | 432 | 699.3 | 635.8 | 705.5 | 678.1 | 690.1 | 375.5 | 513.7 | 471 | 446.5 | 424.9 | 597.9 | 448.7
2138.1 | 1899.1 | 566.9 | 226.76 | 265.0694 | 560.4 | 538.7 | 436.5 | 431 | 639.9 | 83.5 | 16.2 | 148.1 | 7.2 | 207 | 18.7 | 484.6 | 713.9 | 717 | 563.2 | 749.9 | 840.1 | 767.2 | 708.7 | 738 | 432.8 | 690.6 | 771.8 | 270.8 | 360 | 432.1 | 699.5 | 635.3 | 703.7 | 678.3 | 689.7 | 375.8 | 513.2 | 471 | 446.8 | 425.1 | 598.2 | 448.9
2139.1 | 1900.1 | 565.8 | 226.32 | 264.555 | 560.5 | 535.3 | 436 | 430.4 | 641.2 | 83.6 | 16.2 | 148 | 6.5 | 221.3 | 17.5 | 485 | 714 | 718.8 | 563.5 | 750 | 839.2 | 767.4 | 709.3 | 733.5 | 433.1 | 690.9 | 770.5 | 270.8 | 360.2 | 432.4 | 700.3 | 636.9 | 705.6 | 679.1 | 690.7 | 376.1 | 513.4 | 471.1 | 447.4 | 425.4 | 598.4 | 449.1
2140.1 | 1901.1 | 566.1 | 226.44 | 264.6953 | 559.9 | 532.2 | 434.6 | 431.3 | 651.1 | 83.8 | 16.2 | 148 | 7.7 | 199.6 | 16.9 | 485.3 | 713.9 | 720.7 | 563.7 | 750 | 838.2 | 767.4 | 709.3 | 732.9 | 433.6 | 691.2 | 769.7 | 271.2 | 360.5 | 432.6 | 701 | 641 | 710.7 | 679.9 | 694.1 | 376.4 | 514.5 | 471.1 | 448.1 | 425.6 | 598.7 | 449.4
2141.1 | 1902.1 | 565.4 | 226.16 | 264.368 | 560.4 | 537.8 | 433.7 | 432.9 | 656.3 | 83.9 | 16.2 | 148.1 | 7.7 | 197.7 | 15.4 | 485.5 | 714.9 | 728.2 | 563.9 | 750.3 | 837.3 | 767.5 | 709.4 | 741.2 | 434.2 | 691.5 | 771.1 | 271.1 | 360.8 | 432.8 | 701.3 | 643.3 | 714.7 | 680.4 | 695.6 | 376.8 | 515.3 | 470.8 | 448.5 | 425.7 | 599.1 | 449.7
2142.1 | 1903.1 | 565.7 | 226.28 | 264.5083 | 561 | 557.9 | 433.7 | 433.6 | 655.7 | 84 | 16.2 | 148 | 7.6 | 189.4 | 15.3 | 485.7 | 715.6 | 732.9 | 564.1 | 750.5 | 837.1 | 767.4 | 708.3 | 744.1 | 434.6 | 691.8 | 771.4 | 271.5 | 361 | 433 | 700.9 | 642.5 | 713.8 | 680.8 | 694.5 | 377.1 | 515.4 | 470.8 | 448.7 | 425.9 | 599.4 | 450.1
2143.1 | 1904.1 | 564.7 | 225.88 | 264.0407 | 563.6 | 570.2 | 434 | 433.6 | 651.8 | 84.1 | 16.2 | 147.8 | 6.9 | 182.9 | 13.1 | 486 | 716.2 | 737.2 | 564.3 | 750.6 | 837.3 | 767.6 | 707.6 | 745.6 | 434.7 | 692 | 771.7 | 271.7 | 361.1 | 433.5 | 700.4 | 641 | 712.5 | 680.7 | 692.8 | 377.4 | 515.2 | 471.2 | 448.6 | 426 | 599.6 | 450.3
2144.1 | 1905.1 | 566.4 | 226.56 | 264.8356 | 563.3 | 577.3 | 434.9 | 433.4 | 654.1 | 84.1 | 16.2 | 147.6 | 6.7 | 207.6 | 13.3 | 485.9 | 716.6 | 743 | 564.4 | 750.8 | 837.9 | 767.6 | 707.4 | 753.1 | 435.1 | 692.2 | 773 | 272 | 361.4 | 433.8 | 700.3 | 642.9 | 716.6 | 681 | 694.1 | 377.7 | 515.3 | 472.2 | 448.6 | 426.4 | 599.8 | 450.6
2145.1 | 1906.1 | 566.4 | 226.56 | 264.8356 | 563.6 | 580.4 | 435.9 | 433.6 | 657.3 | 84 | 16.2 | 147.6 | 7.5 | 203.7 | 14.7 | 486.1 | 717.1 | 745.1 | 564.6 | 750.9 | 838.3 | 767.8 | 707.4 | 759.2 | 435.4 | 692.4 | 773.5 | 272.3 | 361.6 | 434 | 700.2 | 643.7 | 717.6 | 680.9 | 695.9 | 378 | 515.2 | 472.9 | 448.6 | 426.8 | 600 | 450.8
2146.1 | 1907.1 | 566.5 | 226.6 | 264.8823 | 562.7 | 576.2 | 436.8 | 433.6 | 657.4 | 84 | 16.2 | 147.7 | 7.7 | 212.9 | 18 | 486.2 | 717.3 | 748.2 | 564.7 | 751 | 838.7 | 767.7 | 706.5 | 758.2 | 435.8 | 692.7 | 773.9 | 272.5 | 361.8 | 434.3 | 699.8 | 643.1 | 717.3 | 680.6 | 695.3 | 378.3 | 515.1 | 473.1 | 448.6 | 427.2 | 600.2 | 451.1
2147.1 | 1908.1 | 565.5 | 226.2 | 264.4148 | 562.9 | 570.3 | 436.7 | 433.1 | 655.3 | 84.1 | 16.2 | 148 | 8.2 | 202.7 | 22 | 486.4 | 717 | 746.5 | 564.8 | 751 | 839.5 | 767.7 | 705.9 | 755.1 | 436 | 692.9 | 773.7 | 272.7 | 362 | 434.6 | 699.5 | 642.2 | 717.2 | 680.4 | 694.7 | 378.5 | 514.9 | 472.9 | 448.7 | 427.3 | 600.4 | 451.3
2148.1 | 1909.1 | 565.5 | 226.2 | 264.4148 | 561.7 | 562.9 | 436.3 | 432.7 | 652.1 | 84.2 | 16.2 | 148.1 | 7.5 | 194.1 | 20 | 486.6 | 716.7 | 742.4 | 565 | 751.3 | 839.8 | 767.6 | 705.6 | 751.9 | 436.6 | 693.1 | 773.1 | 272.9 | 362.2 | 434.7 | 699.4 | 641 | 715.5 | 679.8 | 694.5 | 378.8 | 514.9 | 472.7 | 448.7 | 427.5 | 600.6 | 451.6
2149.1 | 1910.1 | 565.9 | 226.36 | 264.6018 | 561.5 | 559.9 | 435.6 | 433.2 | 649 | 84.3 | 16.2 | 148.3 | 7.6 | 197.3 | 15.8 | 486.7 | 717 | 739.7 | 565.1 | 751.4 | 840.6 | 767.6 | 705.4 | 752.5 | 436.8 | 693.2 | 773.1 | 273.1 | 362.3 | 434.8 | 699.1 | 640.1 | 714.8 | 679.2 | 694.4 | 379 | 516.4 | 472.4 | 448.7 | 427.5 | 600.8 | 451.8
2150.1 | 1911.1 | 565.3 | 226.12 | 264.3213 | 561.5 | 562.9 | 435 | 432.7 | 645.2 | 84.4 | 16.2 | 148.5 | 8.4 | 200.1 | 13.8 | 486.9 | 716.8 | 737.3 | 565.3 | 751.3 | 841.4 | 767.5 | 705.2 | 747.4 | 437.2 | 693.3 | 772.2 | 273.3 | 362.5 | 435.2 | 698.7 | 637.9 | 715.3 | 678.7 | 693.5 | 379.1 | 516.1 | 472.1 | 448.6 | 427.5 | 601 | 452.1
2151.1 | 1912.1 | 565.1 | 226.04 | 264.2277 | 560.8 | 564.9 | 435.4 | 432.7 | 644.9 | 84.4 | 16.2 | 148.7 | 7.6 | 211.9 | 14.9 | 487.1 | 716.1 | 735.1 | 565.5 | 751.3 | 841.6 | 767.4 | 705.7 | 743.5 | 437.2 | 693.5 | 771.6 | 273.5 | 362.8 | 435.7 | 698.5 | 637.7 | 718 | 678.3 | 694.4 | 379.2 | 515.7 | 471.6 | 448.6 | 427.6 | 601.2 | 452.3
2152.1 | 1913.1 | 565.9 | 226.36 | 264.6018 | 559.1 | 565.7 | 436.9 | 432.6 | 648.5 | 84.4 | 16.2 | 148.7 | 8 | 220.2 | 13 | 487.4 | 715.6 | 732.2 | 565.7 | 751.4 | 841.5 | 767.3 | 707.4 | 742.1 | 437.5 | 693.7 | 771.5 | 273.7 | 363 | 435.9 | 698.4 | 639.8 | 716.6 | 678.4 | 697 | 379.1 | 515.4 | 470.9 | 448.6 | 427.6 | 601.3 | 452.6
2153.1 | 1914.1 | 566.9 | 226.76 | 265.0694 | 557.8 | 573.9 | 437.8 | 431.6 | 648.6 | 84.4 | 16.2 | 148.5 | 8.4 | 187.7 | 11.6 | 487.5 | 715.4 | 727.8 | 565.8 | 751.5 | 840.2 | 767.2 | 706.8 | 740.2 | 437.8 | 693.8 | 772 | 273.9 | 363.2 | 435.9 | 698.2 | 640 | 715.3 | 678 | 695.6 | 379.1 | 514.8 | 470.2 | 448.6 | 427.7 | 601.6 | 452.8
2154.1 | 1915.1 | 567.6 | 227.04 | 265.3967 | 556.3 | 568.3 | 437.5 | 431.3 | 648.1 | 84.4 | 16.2 | 148.4 | 9.1 | 210.5 | 9.3 | 487.5 | 715.8 | 727.6 | 565.9 | 751.7 | 839.5 | 767.1 | 706.1 | 744.9 | 438.2 | 693.9 | 773.2 | 274.2 | 363.4 | 436.1 | 698.3 | 640.1 | 716.6 | 678 | 696.3 | 379.1 | 514 | 469.7 | 448.5 | 428 | 601.8 | 453.1
2155.1 | 1916.1 | 567 | 226.8 | 265.1161 | 555.7 | 568 | 437.5 | 431.7 | 647.2 | 84.4 | 16.1 | 148.2 | 8.9 | 213.3 | 10 | 487.6 | 715.2 | 727.8 | 566.1 | 751.8 | 839.8 | 767.2 | 705.9 | 745.9 | 438.5 | 694.1 | 773.4 | 274.4 | 363.6 | 436.4 | 698.1 | 639.4 | 715.8 | 677.8 | 696 | 379.2 | 513.4 | 469.8 | 448.3 | 428.2 | 602 | 453.3
2156.1 | 1917.1 | 567.9 | 227.16 | 265.537 | 555.8 | 574.1 | 438.7 | 432.2 | 645.2 | 84.3 | 16.1 | 148 | 8.3 | 242.7 | 7.4 | 487.9 | 715.4 | 728.1 | 566.3 | 751.9 | 839.8 | 766.9 | 706 | 742.1 | 438.6 | 694.2 | 773.2 | 274.5 | 363.7 | 436.7 | 698.1 | 639.2 | 713.9 | 677.6 | 696.1 | 379.3 | 513.9 | 469.7 | 448.3 | 428.3 | 602.2 | 453.6
2157.1 | 1918.1 | 567.1 | 226.84 | 265.1629 | 555.5 | 578.9 | 439.8 | 432.6 | 645.6 | 84.2 | 16.1 | 148 | 8.8 | 192.7 | 8.9 | 488 | 715.9 | 728.5 | 566.4 | 752.1 | 839.5 | 766.9 | 706.6 | 743.6 | 438.9 | 694.4 | 772.6 | 274.5 | 363.8 | 436.9 | 698.1 | 638.9 | 713.7 | 677.5 | 696.8 | 379.5 | 514.2 | 470 | 448.4 | 428.5 | 602.5 | 453.9
2158.1 | 1919.1 | 566.1 | 226.44 | 264.6953 | 554.4 | 581.4 | 439.7 | 433.4 | 645.6 | 84.2 | 16.1 | 147.9 | 8.6 | 195.3 | 13 | 488.1 | 716.5 | 728.7 | 566.5 | 752.3 | 838.7 | 766.7 | 706.1 | 742.3 | 439.1 | 694.6 | 772.5 | 274.9 | 364.2 | 437 | 698.1 | 638.9 | 714.6 | 677.6 | 697.2 | 379.7 | 514.4 | 470.8 | 448.3 | 428.8 | 602.8 | 454.1
2159.1 | 1920.1 | 566.8 | 226.72 | 265.0226 | 553.8 | 580.6 | 439.4 | 433.6 | 646.4 | 84.3 | 16.1 | 147.9 | 8.5 | 197.5 | 14.1 | 488.2 | 717.4 | 733.2 | 566.7 | 752.5 | 838.1 | 766.4 | 706.5 | 743.5 | 439.5 | 694.7 | 772.7 | 275.2 | 364.4 | 437.2 | 698.8 | 639.8 | 718.4 | 678.4 | 699.2 | 380 | 515.3 | 471.4 | 448.4 | 429 | 603.1 | 454.4
2160.1 | 1921.1 | 567.2 | 226.88 | 265.2096 | 554.3 | 592.4 | 438.9 | 434.7 | 650.3 | 84.3 | 16.1 | 147.8 | 8.4 | 183.4 | 16.2 | 488.5 | 717 | 735.9 | 566.9 | 752.6 | 838.2 | 766.3 | 706.6 | 749.3 | 439.7 | 694.8 | 773.2 | 275.3 | 364.7 | 437.7 | 699.2 | 640.8 | 723.1 | 679 | 701.5 | 380.3 | 515.6 | 471.3 | 448.2 | 429.1 | 603.4 | 454.8
2161.1 | 1922.1 | 567.6 | 227.04 | 265.3967 | 554.2 | 598.1 | 440.4 | 435.6 | 653 | 84.3 | 16.1 | 147.9 | 8.5 | 206.1 | 13.6 | 488.9 | 717.3 | 741.1 | 567.1 | 752.8 | 837.9 | 766.2 | 706.8 | 749.3 | 439.9 | 694.9 | 773.3 | 275.7 | 365.1 | 438.1 | 699.4 | 643.6 | 723.8 | 679.6 | 701.4 | 380.5 | 515.5 | 471.1 | 448 | 429.1 | 603.6 | 455.1
2162.1 | 1923.1 | 567.1 | 226.84 | 265.1629 | 554 | 600.2 | 441.8 | 435.5 | 655.7 | 84.3 | 16.1 | 148 | 8.9 | 197.6 | 15.4 | 489 | 718.4 | 742.4 | 567.3 | 752.9 | 837.5 | 765.9 | 706.5 | 754.5 | 440.3 | 695 | 774.9 | 275.9 | 365.4 | 438.2 | 699.4 | 645.3 | 722.5 | 679.8 | 700.7 | 380.8 | 515.3 | 471.4 | 447.9 | 429.4 | 603.8 | 455.3
2163.1 | 1924.1 | 565.2 | 226.08 | 264.2745 | 553.6 | 605.5 | 440.4 | 434.5 | 656.1 | 84.2 | 16.1 | 148.2 | 8.8 | 197.5 | 15 | 489.3 | 719 | 743.9 | 567.5 | 753.1 | 837.6 | 766 | 706.2 | 756.1 | 440.5 | 695.1 | 775.1 | 276.1 | 365.7 | 438.2 | 699.7 | 645.9 | 720.9 | 680.3 | 699.5 | 381.2 | 515.9 | 472.2 | 448.3 | 429.7 | 604 | 455.6
2164.1 | 1925.1 | 566.3 | 226.52 | 264.7888 | 552.2 | 605.6 | 439.2 | 434.8 | 656.5 | 84.2 | 16.1 | 148.2 | 7.9 | 207.1 | 15.4 | 489.5 | 720.7 | 741.4 | 567.7 | 753.2 | 837.4 | 765.7 | 705.8 | 755.7 | 440.8 | 695.2 | 774.5 | 276.2 | 365.8 | 438.4 | 700.6 | 646.7 | 720.8 | 681.4 | 699.9 | 381.6 | 517.9 | 473.3 | 448.8 | 430 | 604.3 | 455.9
2165.1 | 1926.1 | 567.4 | 226.96 | 265.3032 | 552.1 | 613.4 | 439.1 | 436.6 | 659.3 | 84.1 | 16.1 | 148.1 | 7.1 | 223.8 | 11.8 | 489.6 | 721.3 | 735.7 | 567.8 | 753.3 | 837 | 765.2 | 704.9 | 752.6 | 441.1 | 695.3 | 774.6 | 276.4 | 366.1 | 438.6 | 701.6 | 649.3 | 720.5 | 682.5 | 702.1 | 382.1 | 520.3 | 474.3 | 449.5 | 430.3 | 604.6 | 456.2
2166.1 | 1927.1 | 566.4 | 226.56 | 264.8356 | 551.9 | 620.7 | 438.5 | 437.5 | 662.8 | 84.1 | 16.1 | 148.1 | 7.1 | 207.9 | 11.4 | 489.7 | 721.4 | 731.1 | 567.9 | 753.3 | 837.4 | 764.4 | 704.3 | 751.6 | 441.4 | 695.4 | 774.8 | 276.1 | 366.4 | 438.8 | 701.6 | 650.3 | 718.9 | 682.9 | 703.1 | 382.5 | 521.5 | 474.7 | 450 | 430.7 | 604.9 | 456.6
2167.1 | 1928.1 | 566.4 | 226.56 | 264.8356 | 551.6 | 619.8 | 438.3 | 437.9 | 663.7 | 84.2 | 16.1 | 148.1 | 7.4 | 232.2 | 10.6 | 490 | 721.2 | 727.2 | 568.1 | 753.4 | 837.7 | 764 | 704.1 | 751.7 | 441.8 | 695.4 | 776 | 275.9 | 366.6 | 439 | 701.3 | 650.1 | 718.4 | 682.8 | 702.7 | 383 | 522.4 | 475 | 450.4 | 431 | 605.2 | 456.9
2168.1 | 1929.1 | 566.8 | 226.72 | 265.0226 | 551.7 | 616.2 | 439 | 438.3 | 661.4 | 84.4 | 16.1 | 148 | 7.6 | 220.8 | 10 | 490.1 | 720.1 | 722.2 | 568.2 | 753.4 | 838.4 | 763.3 | 704.2 | 748.2 | 442.2 | 695.5 | 775 | 276 | 366.9 | 439.2 | 700.9 | 648.8 | 716.9 | 682.6 | 701.2 | 383.4 | 522.2 | 474.5 | 450.6 | 431 | 605.5 | 457.2
2169.1 | 1930.1 | 566.3 | 226.52 | 264.7888 | 552.7 | 616.5 | 438.6 | 438.5 | 657.6 | 84.5 | 16.1 | 148 | 8 | 207.9 | 15.4 | 490.3 | 719.4 | 722.9 | 568.4 | 753.5 | 838.8 | 762.8 | 704.4 | 746.2 | 442.5 | 695.6 | 774.6 | 276 | 367.2 | 439.4 | 700.6 | 647.3 | 718.1 | 682.3 | 700.7 | 383.7 | 521.3 | 473.9 | 450.6 | 431.1 | 605.7 | 457.5
2170.1 | 1931.1 | 567.2 | 226.88 | 265.2096 | 553.3 | 611.6 | 438.3 | 437.3 | 654.1 | 84.6 | 16.1 | 147.9 | 8.6 | 205.4 | 16.8 | 490.3 | 718.5 | 723.8 | 568.5 | 753.6 | 838.9 | 762.3 | 704.3 | 749.2 | 443 | 695.6 | 775.3 | 276.2 | 367.4 | 439.6 | 701 | 645.6 | 720.5 | 682.3 | 701.1 | 383.8 | 520.2 | 473.7 | 450.7 | 431.2 | 605.9 | 457.7
2171.1 | 1932.1 | 566.7 | 226.68 | 264.9759 | 552.6 | 611.9 | 438.7 | 436.2 | 651.9 | 84.7 | 16.1 | 148 | 8 | 203.3 | 16.8 | 490.4 | 717.1 | 721 | 568.6 | 753.6 | 839.4 | 762 | 703.8 | 743.8 | 443.3 | 695.6 | 775.5 | 276.7 | 367.6 | 439.8 | 700.8 | 645 | 715.9 | 682.2 | 700.2 | 384.1 | 519.9 | 473.6 | 451 | 431.5 | 606.1 | 458
2172.1 | 1933.1 | 566.1 | 226.44 | 264.6953 | 552 | 615 | 439.1 | 436.1 | 649.8 | 84.7 | 16.1 | 148.1 | 7.5 | 212 | 16.9 | 490.6 | 716.5 | 720.5 | 568.8 | 753.5 | 839.9 | 761.8 | 703.9 | 738.2 | 443.8 | 695.6 | 773.9 | 276.6 | 367.8 | 439.9 | 700.8 | 644.6 | 713.6 | 682.3 | 699.6 | 384.3 | 520.3 | 473.7 | 451.5 | 431.7 | 606.3 | 458.2
2173.1 | 1934.1 | 566.6 | 226.64 | 264.9291 | 551 | 624.3 | 438.3 | 437.2 | 649.5 | 84.7 | 16.1 | 148.2 | 7.8 | 209 | 16.3 | 490.7 | 716.3 | 716.3 | 568.9 | 753.7 | 839.9 | 761.7 | 705.1 | 734.7 | 444.1 | 695.8 | 772.4 | 276.8 | 368.1 | 440.1 | 701 | 644.4 | 712.7 | 682.7 | 698.3 | 384.4 | 519.8 | 473.6 | 451.8 | 431.8 | 606.5 | 458.5
2174.1 | 1935.1 | 567.2 | 226.88 | 265.2096 | 551.7 | 624.1 | 437.7 | 437.2 | 647.2 | 84.7 | 16.1 | 148.3 | 7.5 | 217.5 | 14.1 | 490.8 | 716 | 718.8 | 569 | 753.8 | 839.3 | 761.5 | 705.8 | 736.8 | 444.3 | 696 | 772.5 | 277 | 368.6 | 440.3 | 701.1 | 643.4 | 709.2 | 682.6 | 696.6 | 384.5 | 519 | 473.1 | 451.9 | 431.9 | 606.8 | 458.7
2175.1 | 1936.1 | 567.1 | 226.84 | 265.1629 | 552 | 617.8 | 437.8 | 437.1 | 647.1 | 84.8 | 16.1 | 148.5 | 7.9 | 239.5 | 9.9 | 491 | 716.8 | 721.7 | 569.2 | 754 | 838.8 | 761.6 | 705.5 | 745.1 | 444.8 | 696.1 | 774.3 | 276.8 | 369 | 440.7 | 701.2 | 642.9 | 710.5 | 682.7 | 695.6 | 384.7 | 518.2 | 472.6 | 452.2 | 432 | 607 | 459
2176.1 | 1937.1 | 567.4 | 226.96 | 265.3032 | 551.1 | 620.8 | 437.9 | 437.6 | 649 | 84.8 | 16.1 | 148.7 | 7.1 | 194.2 | 7.9 | 491.1 | 717.1 | 728.2 | 569.4 | 754.1 | 838.3 | 761.4 | 705.2 | 749.1 | 445.2 | 696.2 | 775.7 | 276.9 | 369.5 | 440.9 | 701.2 | 642.4 | 712.9 | 682.6 | 698.2 | 384.9 | 517.5 | 472.2 | 452.5 | 432 | 607.4 | 459.2
2177.1 | 1938.1 | 567 | 226.8 | 265.1161 | 551.7 | 620.9 | 438.2 | 438 | 648.1 | 84.8 | 16.1 | 148.7 | 6.6 | 191.1 | 5.7 | 491.3 | 716.6 | 728.6 | 569.5 | 754.3 | 838.4 | 761.7 | 704.5 | 750.2 | 445.7 | 696.4 | 775.9 | 277.3 | 369.9 | 441 | 700.7 | 641.4 | 712.9 | 682.1 | 698.7 | 385 | 517 | 471.9 | 452.9 | 432.1 | 607.7 | 459.5
2178.1 | 1939.1 | 568.4 | 227.36 | 265.7707 | 553 | 621.6 | 437.9 | 438 | 647.1 | 84.8 | 16.1 | 148.7 | 5.5 | 199.7 | 8.2 | 491.5 | 716 | 727.2 | 569.7 | 754.4 | 838.5 | 761.7 | 704.1 | 751.2 | 446.1 | 696.4 | 775.5 | 277.8 | 370.4 | 441.2 | 700.6 | 641 | 716 | 682 | 699.1 | 385.2 | 516.5 | 472.3 | 453.4 | 432.2 | 607.9 | 459.7
2179.1 | 1940.1 | 567.3 | 226.92 | 265.2564 | 553.3 | 624.9 | 437.6 | 437.9 | 648.9 | 84.8 | 16.1 | 148.7 | 7.2 | 215.2 | 11 | 491.6 | 716.7 | 731.2 | 569.8 | 754.5 | 838.1 | 761.6 | 704.9 | 753.8 | 446.7 | 696.5 | 776.4 | 277.9 | 370.8 | 441.5 | 701.1 | 642.2 | 718.2 | 682.5 | 701 | 385.5 | 516.4 | 474.3 | 453.9 | 433.1 | 608.1 | 460
2180.1 | 1941.1 | 567.3 | 226.92 | 265.2564 | 553.3 | 624 | 436.7 | 438.1 | 652.3 | 84.8 | 16.1 | 148.7 | 8.1 | 191.5 | 14.7 | 491.8 | 718.4 | 734.6 | 569.9 | 754.7 | 837.8 | 761.4 | 705.1 | 755.6 | 447.3 | 696.6 | 776.8 | 277.5 | 371.2 | 441.7 | 701.4 | 643.4 | 721.5 | 682.9 | 703.5 | 386 | 516.5 | 475.4 | 454.4 | 433.6 | 608.3 | 460.2
2181.1 | 1942.1 | 567.7 | 227.08 | 265.4434 | 552.3 | 631.9 | 436.8 | 438.3 | 652.5 | 84.8 | 16.1 | 148.8 | 8.1 | 195.3 | 14.4 | 492 | 718.7 | 733.7 | 570.1 | 754.7 | 837.5 | 761.2 | 704.6 | 749.4 | 447.8 | 696.8 | 775.4 | 277.7 | 371.7 | 441.8 | 701.4 | 643.5 | 716.9 | 683.3 | 702.6 | 386.6 | 516.9 | 475.9 | 455.1 | 433.8 | 608.5 | 460.5
2182.1 | 1943.1 | 566.6 | 226.64 | 264.9291 | 550.8 | 629.1 | 437.4 | 437.7 | 653.1 | 84.8 | 16.1 | 149.2 | 7.6 | 202.1 | 14.8 | 492.5 | 718.8 | 726.9 | 570.3 | 754.8 | 836.2 | 761.2 | 705.1 | 745.4 | 448.1 | 696.9 | 774.9 | 277.8 | 372.1 | 442.1 | 702 | 645 | 710.1 | 684.2 | 702.9 | 387.1 | 519.1 | 476.9 | 456.2 | 434.1 | 608.8 | 460.8
2183.1 | 1944.1 | 566.5 | 226.6 | 264.8823 | 549.9 | 630.1 | 437.7 | 437.7 | 653 | 84.7 | 16.1 | 149.5 | 7.2 | 191.6 | 17.7 | 493 | 719 | 723.2 | 570.5 | 754.7 | 834.8 | 761 | 706.2 | 734 | 448.4 | 696.8 | 772.5 | 278 | 372.5 | 442.4 | 702.7 | 647.3 | 700.9 | 684.7 | 702.5 | 387.7 | 522.2 | 478 | 458.1 | 434.4 | 609.1 | 461.1
2184.1 | 1945.1 | 565.2 | 226.08 | 264.2745 | 549 | 635.7 | 438.1 | 439.9 | 652.5 | 84.7 | 16.1 | 149.6 | 8 | 216.9 | 17.6 | 493.4 | 718.3 | 727.5 | 570.7 | 754.7 | 835.1 | 760.6 | 707.8 | 732.8 | 448.7 | 696.9 | 772 | 278.2 | 372.9 | 442.7 | 702.9 | 647.1 | 704.1 | 684.7 | 703.1 | 388.3 | 524.3 | 479.2 | 459.5 | 434.6 | 609.5 | 461.5
2185.1 | 1946.1 | 565.5 | 226.2 | 264.4148 | 551.1 | 634.2 | 438.8 | 441.8 | 656.6 | 84.6 | 16 | 149.8 | 7.4 | 209.7 | 17.9 | 493.5 | 716.6 | 727.4 | 570.9 | 754.9 | 835.7 | 759.8 | 707.4 | 732.9 | 449.2 | 697 | 771.9 | 278.5 | 373.1 | 442.7 | 702.9 | 647.1 | 706.2 | 684.8 | 704.8 | 388.8 | 524.5 | 480.4 | 460.2 | 434.8 | 609.9 | 461.9
2186.1 | 1947.1 | 566.4 | 226.56 | 264.8356 | 552.5 | 637.5 | 438.6 | 442.4 | 655.5 | 84.5 | 16 | 149.9 | 7.5 | 209.1 | 18.9 | 493.5 | 715.8 | 726.8 | 571 | 754.9 | 836.1 | 759.4 | 707.4 | 733.6 | 449.4 | 697.1 | 772 | 278.6 | 373.3 | 442.9 | 702.9 | 647 | 704.7 | 684.8 | 704 | 389.3 | 525.1 | 480.6 | 460.6 | 435 | 610.2 | 462.2
2187.1 | 1948.1 | 566.2 | 226.48 | 264.7421 | 554.9 | 641.5 | 438.1 | 441.5 | 654.4 | 84.5 | 16 | 150 | 7.3 | 209.1 | 18.6 | 493.5 | 715.6 | 722 | 571.1 | 755 | 836.2 | 759.1 | 707 | 734.6 | 449.7 | 697.1 | 772 | 278.9 | 373.5 | 443.2 | 703.1 | 646.5 | 704.7 | 685.2 | 703.7 | 389.8 | 525.1 | 480.5 | 461.2 | 435.2 | 610.4 | 462.4
2188.1 | 1949.1 | 566.9 | 226.76 | 265.0694 | 555.5 | 645.9 | 439.1 | 441.4 | 654.1 | 84.5 | 16 | 150.1 | 7.1 | 214.8 | 16.9 | 493.6 | 715.8 | 719.8 | 571.2 | 755.1 | 836.2 | 758.6 | 706.9 | 735.9 | 449.8 | 697.2 | 772.3 | 279.2 | 373.7 | 443.3 | 703.4 | 645.5 | 706 | 685.6 | 702.2 | 390.2 | 525.3 | 480.2 | 462 | 435.3 | 610.8 | 462.7
2189.1 | 1950.1 | 566.3 | 226.52 | 264.7888 | 556.8 | 646.1 | 439 | 441.5 | 652.1 | 84.5 | 16 | 150.2 | 8.6 | 216.1 | 14.9 | 493.9 | 715.8 | 716.5 | 571.3 | 755.1 | 835.4 | 758 | 706.7 | 739 | 450 | 697.1 | 773.4 | 279 | 374 | 443.6 | 702.9 | 644 | 705.6 | 685.2 | 700.7 | 390.5 | 526 | 479.7 | 462.6 | 435.4 | 611 | 463
2190.1 | 1951.1 | 566.4 | 226.56 | 264.8356 | 558.1 | 646.5 | 438.7 | 440.6 | 648.8 | 84.5 | 16 | 150.2 | 9.5 | 208.7 | 12.4 | 494.1 | 715.8 | 712.2 | 571.5 | 755.1 | 834.9 | 757.8 | 706.3 | 741.5 | 450.6 | 697.1 | 774 | 279.2 | 374.5 | 443.9 | 702.3 | 643 | 705.1 | 684.4 | 699.8 | 390.6 | 525.7 | 479.6 | 463.3 | 435.5 | 611.2 | 463.3
2191.1 | 1952.1 | 566.1 | 226.44 | 264.6953 | 557.3 | 645.5 | 439.7 | 439.8 | 646.4 | 84.6 | 16 | 150.4 | 10.2 | 195 | 13.2 | 494.3 | 713.8 | 705.9 | 571.6 | 755 | 835.4 | 757.3 | 706.1 | 733.4 | 451.2 | 697.1 | 772.2 | 279.4 | 374.9 | 444.1 | 701.7 | 641.4 | 704.1 | 684 | 698.7 | 390.9 | 526.1 | 479.6 | 464.1 | 435.6 | 611.5 | 463.5
2192.1 | 1953.1 | 566.7 | 226.68 | 264.9759 | 559.4 | 652.6 | 441.4 | 440.4 | 641.6 | 84.5 | 16 | 150.4 | 9.9 | 210.3 | 11.7 | 494.8 | 712.3 | 701 | 571.9 | 754.9 | 835.6 | 757.1 | 707.2 | 720.4 | 450.9 | 697.1 | 769.1 | 279.5 | 375.2 | 444.1 | 701.2 | 638.7 | 696.8 | 683.4 | 694.5 | 391 | 526.7 | 479.4 | 464.8 | 435.7 | 611.7 | 463.8
2193.1 | 1954.1 | 564.3 | 225.72 | 263.8537 | 558.9 | 654 | 443.2 | 440.2 | 637.1 | 84.4 | 16 | 150.4 | 9.5 | 230.1 | 10.2 | 495.1 | 710.7 | 697.8 | 572.1 | 754.9 | 835.5 | 756.6 | 709.2 | 715.2 | 450.8 | 697.1 | 767.5 | 279.7 | 375.6 | 444.3 | 701.1 | 636 | 692.7 | 682.8 | 691.5 | 391 | 526 | 478.3 | 465.1 | 435.6 | 611.9 | 464.1
2194.1 | 1955.1 | 565 | 226 | 264.181 | 559.4 | 656.4 | 442.4 | 439.2 | 634.3 | 84.4 | 16 | 150.5 | 8.9 | 250.8 | 7.8 | 495.1 | 709.8 | 699.2 | 572.2 | 754.9 | 835.2 | 756.2 | 709.7 | 712.6 | 451.1 | 697.1 | 767.2 | 279.8 | 376 | 444.5 | 700.6 | 632.9 | 688.6 | 681.8 | 690.1 | 391.1 | 524.8 | 477.5 | 465.5 | 435.8 | 612.1 | 464.3
2195.1 | 1956.1 | 564.2 | 225.68 | 263.8069 | 560.9 | 648.9 | 442 | 439.6 | 630.2 | 84.3 | 16 | 150.5 | 8.7 | 250.6 | 7.3 | 495.1 | 709.1 | 701.9 | 572.3 | 755 | 834.7 | 755.9 | 709.2 | 710.2 | 451.2 | 697.1 | 767 | 280 | 376.3 | 444.6 | 699.9 | 630 | 687.6 | 680.6 | 689.9 | 391.2 | 524.9 | 477.3 | 466.5 | 436 | 612.2 | 464.5
2196.1 | 1957.1 | 563.4 | 225.36 | 263.4329 | 560.7 | 657.5 | 441.5 | 440.2 | 626.9 | 84.3 | 16 | 150.4 | 7.6 | 237.3 | 7.8 | 495.4 | 708.6 | 704.9 | 572.4 | 755 | 834.5 | 755.8 | 709.2 | 714.5 | 451.1 | 697.3 | 767.7 | 280.1 | 376.7 | 444.8 | 699.5 | 627.9 | 687 | 679.7 | 690.7 | 391.3 | 525.5 | 476.8 | 467.2 | 436.2 | 612.3 | 464.8
2197.1 | 1958.1 | 564.4 | 225.76 | 263.9004 | 560.9 | 661.8 | 441.7 | 439.9 | 623.8 | 84.5 | 16 | 150.3 | 7.8 | 212.8 | 10.9 | 495.5 | 707.5 | 710.8 | 572.5 | 755.1 | 834.6 | 756 | 708.1 | 718.9 | 450.8 | 697.5 | 768 | 280.3 | 377.1 | 445 | 699.1 | 626.4 | 688.8 | 679 | 692.2 | 391.4 | 526.1 | 476.7 | 467.7 | 436.3 | 612.4 | 465.1
2198.1 | 1959.1 | 565.4 | 226.16 | 264.368 | 561.1 | 674.2 | 441.5 | 439.9 | 623.3 | 84.6 | 16 | 150.4 | 8.6 | 228.2 | 12.3 | 495.7 | 707.2 | 716.8 | 572.7 | 755.1 | 835 | 756.1 | 708.2 | 725.3 | 450.7 | 697.7 | 769.6 | 280.4 | 377.4 | 445.3 | 698.8 | 626.6 | 694.2 | 678.6 | 695.9 | 391.6 | 526 | 476.7 | 468.4 | 436.6 | 612.5 | 465.3
2199.1 | 1960.1 | 566.7 | 226.68 | 264.9759 | 560 | 678.5 | 440.6 | 440.2 | 627.5 | 84.8 | 16 | 150.5 | 8.6 | 235 | 11.1 | 496 | 707.1 | 719.2 | 572.8 | 755.2 | 834.9 | 756.5 | 707.8 | 725.1 | 451.1 | 697.9 | 768.9 | 280.6 | 377.8 | 445.5 | 698.9 | 628.5 | 696.4 | 678.7 | 698.5 | 391.8 | 526.5 | 476.7 | 469.3 | 436.8 | 612.8 | 465.6
2200.1 | 1961.1 | 564.9 | 225.96 | 264.1342 | 558.5 | 676.7 | 441.3 | 440.8 | 629.8 | 85 | 16 | 150.4 | 7.2 | 236 | 9.9 | 496.1 | 707.1 | 723.7 | 572.9 | 755.4 | 835 | 756.5 | 707.2 | 726.8 | 451.1 | 698 | 769.2 | 280.7 | 378.1 | 445.5 | 699 | 629.6 | 690.8 | 679 | 698.3 | 392.1 | 529.4 | 476.6 | 470.2 | 436.8 | 613 | 466
2201.1 | 1962.1 | 565.4 | 226.16 | 264.368 | 557.3 | 684.7 | 441.8 | 441.4 | 631.5 | 85.2 | 16 | 150.5 | 8 | 245.6 | 8.7 | 496.2 | 707.4 | 726.8 | 573.1 | 755.5 | 834.8 | 756.6 | 707 | 735 | 451.2 | 698.1 | 770.3 | 280.9 | 378.4 | 445.8 | 699.4 | 629.7 | 695.7 | 679.4 | 699.5 | 392.2 | 530.3 | 476.4 | 470.7 | 436.8 | 613.3 | 466.3
2202.1 | 1963.1 | 565 | 226 | 264.181 | 556.7 | 688.7 | 440.8 | 441 | 635.3 | 85.3 | 16 | 150.7 | 8.3 | 206.1 | 6.4 | 496.5 | 708.4 | 728.3 | 573.2 | 755.6 | 834.3 | 756.6 | 706.5 | 739.4 | 451.3 | 698.2 | 771.7 | 281.1 | 378.8 | 446 | 699.5 | 630.4 | 697.2 | 679.6 | 699.6 | 392.4 | 529.3 | 476.4 | 470.9 | 436.9 | 613.5 | 466.6
2203.1 | 1964.1 | 565.6 | 226.24 | 264.4615 | 556.5 | 682.2 | 440.2 | 440.8 | 636.4 | 85.4 | 16 | 151 | 10 | 229.2 | 6.1 | 496.8 | 708.1 | 727.5 | 573.3 | 755.7 | 833.1 | 756.8 | 706.7 | 743.5 | 451.3 | 698.3 | 772.8 | 281.2 | 379 | 446.3 | 699.2 | 630.3 | 698.8 | 679.4 | 698.4 | 392.5 | 528.9 | 476.8 | 471.3 | 437 | 613.7 | 466.8
2204.1 | 1965.1 | 568.1 | 227.24 | 265.6305 | 555.6 | 673.3 | 441.5 | 441.5 | 636.8 | 85.5 | 16 | 151.2 | 10.2 | 240.5 | 6.8 | 497 | 709.1 | 728.5 | 573.5 | 755.9 | 832.6 | 757 | 706.4 | 749.2 | 451.5 | 698.4 | 773.7 | 281.2 | 379.2 | 446.5 | 699.2 | 631.4 | 697.7 | 679.2 | 699.5 | 392.7 | 530.5 | 477.3 | 472 | 437.2 | 613.9 | 467.1
2205.1 | 1966.1 | 568.5 | 227.4 | 265.8175 | 553.3 | 668.7 | 443.3 | 442.4 | 639.2 | 85.4 | 16 | 151.4 | 8.8 | 239 | 6.9 | 497.1 | 710 | 722.8 | 573.6 | 756 | 832 | 757.2 | 706.3 | 747.7 | 451.3 | 698.5 | 773.5 | 281.4 | 379.6 | 446.6 | 699.7 | 633.8 | 694.7 | 680 | 699.3 | 393.1 | 533.6 | 478.4 | 473 | 437.4 | 614.2 | 467.5
2206.1 | 1967.1 | 568.2 | 227.28 | 265.6772 | 552.1 | 676.6 | 443.5 | 443.7 | 641.5 | 85.4 | 16 | 151.4 | 7.9 | 241.6 | 9.1 | 497.3 | 709.4 | 716.8 | 573.7 | 756.1 | 831.9 | 757.5 | 705.8 | 747.4 | 451.4 | 698.7 | 773 | 281.6 | 379.9 | 446.8 | 700.6 | 635.2 | 695.7 | 681.2 | 697.9 | 393.5 | 534 | 479.3 | 473.7 | 437.7 | 614.5 | 467.8
2207.1 | 1968.1 | 568.6 | 227.44 | 265.8643 | 553.1 | 678.2 | 442.5 | 444.2 | 643.9 | 85.6 | 16 | 151.3 | 7.5 | 239.3 | 13.5 | 497.5 | 709.1 | 716.1 | 573.8 | 756.1 | 832.4 | 757.9 | 705.5 | 749.3 | 451.1 | 698.8 | 774.4 | 281.8 | 380.1 | 447 | 700.9 | 636.4 | 698.9 | 681.7 | 698.6 | 394 | 533.3 | 479.7 | 474 | 437.9 | 614.8 | 468.2
2208.1 | 1969.1 | 566.6 | 226.64 | 264.9291 | 553.9 | 680.1 | 442.4 | 444 | 645.9 | 85.6 | 16 | 151.3 | 7.6 | 244.1 | 15.9 | 497.6 | 709.9 | 716.7 | 573.8 | 756.2 | 832.3 | 758.2 | 705.8 | 750.3 | 451.2 | 698.8 | 774.8 | 282 | 380.4 | 447.3 | 700.7 | 638.2 | 697.1 | 681.6 | 698.5 | 394.3 | 532.6 | 480.2 | 474.1 | 438 | 615.1 | 468.4
2209.1 | 1970.1 | 566.8 | 226.72 | 265.0226 | 554.6 | 685.9 | 444.1 | 444.3 | 646.6 | 85.6 | 16 | 151.1 | 8.4 | 215.4 | 12.3 | 497.8 | 709.7 | 711.3 | 573.9 | 756.2 | 831.6 | 758.6 | 706.3 | 740.9 | 451.1 | 698.8 | 772.5 | 282.4 | 380.7 | 447.5 | 700.7 | 639.9 | 692.5 | 682 | 698.4 | 394.7 | 533.1 | 481.5 | 474.9 | 438.4 | 615.4 | 468.7
2210.1 | 1971.1 | 567.4 | 226.96 | 265.3032 | 554 | 679.9 | 445 | 445.5 | 645.9 | 85.7 | 16 | 151.2 | 8.1 | 216.8 | 8.8 | 498.1 | 709.7 | 711.5 | 574.1 | 756.1 | 831.4 | 758.5 | 706.6 | 732.1 | 451 | 698.8 | 770.8 | 282.8 | 381 | 447.8 | 700.9 | 641.5 | 686.2 | 682.4 | 695.9 | 395.2 | 534.9 | 483.7 | 475.9 | 438.8 | 615.7 | 469.1
2211.1 | 1972.1 | 566.7 | 226.68 | 264.9759 | 552.4 | 687.9 | 445.6 | 447 | 646 | 85.8 | 16 | 151.3 | 7.8 | 219.8 | 10.2 | 498.4 | 710.5 | 713.8 | 574.2 | 756.2 | 831.3 | 758.7 | 707 | 736.3 | 451.1 | 698.9 | 772.2 | 283.1 | 381.4 | 448.1 | 701.2 | 641.5 | 690.6 | 682.7 | 695.6 | 395.9 | 535 | 484.5 | 476.3 | 439 | 616 | 469.4
2212.1 | 1973.1 | 567.4 | 226.96 | 265.3032 | 552 | 687.2 | 445.5 | 447.2 | 646.6 | 85.9 | 16 | 151.3 | 7 | 205 | 12.5 | 498.6 | 710.2 | 716.6 | 574.4 | 756.4 | 831.5 | 758.8 | 705.9 | 738.5 | 451.2 | 698.9 | 772.4 | 283.3 | 381.7 | 448.1 | 701.1 | 641.7 | 692.8 | 682.9 | 697.4 | 396.4 | 534.8 | 485.1 | 476.4 | 439.2 | 616.3 | 469.7
2213.1 | 1974.1 | 567.2 | 226.88 | 265.2096 | 553.9 | 687.9 | 445 | 447.7 | 648 | 86 | 16 | 151.5 | 7.4 | 218.4 | 12.8 | 498.7 | 710.4 | 719 | 574.5 | 756.6 | 832 | 758.9 | 705.3 | 740.3 | 451.2 | 699 | 772.4 | 283.3 | 381.9 | 448.3 | 701.4 | 641.8 | 695.9 | 683.6 | 699.9 | 396.8 | 535 | 486.2 | 476.4 | 439.5 | 616.7 | 470
2214.1 | 1975.1 | 566.8 | 226.72 | 265.0226 | 554.2 | 688.5 | 446.2 | 448.4 | 647.9 | 86.1 | 16 | 151.5 | 6.7 | 218.1 | 12.1 | 498.8 | 710.5 | 722.8 | 574.5 | 756.6 | 831.9 | 758.8 | 704.9 | 740.9 | 451.2 | 699 | 773 | 283.7 | 382.2 | 448.4 | 701.7 | 640.9 | 697.3 | 684.1 | 700.9 | 397.3 | 535.4 | 485.9 | 476.4 | 439.7 | 616.9 | 470.3
2215.1 | 1976.1 | 565.8 | 226.32 | 264.555 | 554.3 | 696.6 | 446.9 | 448.8 | 644.8 | 86.2 | 16 | 151.4 | 8.2 | 221 | 11.5 | 498.9 | 710.2 | 719.6 | 574.6 | 756.7 | 831.6 | 759.2 | 704.7 | 739.8 | 451.2 | 699.1 | 773.2 | 283.8 | 382.5 | 448.7 | 701.6 | 639.8 | 702.3 | 684 | 700.9 | 397.7 | 534.6 | 485.6 | 476.3 | 439.7 | 617.1 | 470.6
2216.1 | 1977.1 | 566.7 | 226.68 | 264.9759 | 554.1 | 694 | 446.8 | 448.3 | 644.1 | 86.2 | 15.9 | 151.4 | 7.5 | 243.8 | 9.4 | 499.1 | 710 | 716.8 | 574.6 | 756.7 | 831.7 | 759.3 | 705.2 | 736.6 | 451.2 | 699.2 | 772.9 | 284.1 | 382.8 | 448.9 | 701.2 | 638.9 | 702.5 | 684.1 | 700.3 | 398 | 534 | 485.8 | 476.5 | 439.8 | 617.2 | 470.9
2217.1 | 1978.1 | 567.3 | 226.92 | 265.2564 | 554.6 | 680.4 | 445.4 | 448.2 | 641.2 | 86.2 | 15.9 | 151.3 | 7 | 229.8 | 11.4 | 499.3 | 711 | 716.2 | 574.8 | 756.9 | 831.4 | 759.4 | 705.1 | 737.3 | 451.3 | 699 | 773.1 | 284.4 | 383.1 | 449 | 700.9 | 637.7 | 700.6 | 684.1 | 697.1 | 398.2 | 534.2 | 486.3 | 476.6 | 440.3 | 617.3 | 471.1
2218.1 | 1979.1 | 566.6 | 226.64 | 264.9291 | 553.6 | 681.5 | 444.9 | 447.8 | 643.2 | 86.2 | 15.9 | 151 | 6.2 | 208.1 | 13.3 | 499.5 | 711.6 | 718.7 | 574.9 | 757 | 831.2 | 759.5 | 704.2 | 739.3 | 451.1 | 699.1 | 773.9 | 284.4 | 383.4 | 449.2 | 701.1 | 638.9 | 703.5 | 684.5 | 697.6 | 398.6 | 534.7 | 487 | 476.9 | 440.9 | 617.5 | 471.4
2219.1 | 1980.1 | 567.8 | 227.12 | 265.4902 | 554.2 | 678.8 | 445.3 | 446.7 | 646 | 86.2 | 15.9 | 150.9 | 6.6 | 203 | 15.9 | 499.7 | 711 | 718.3 | 574.9 | 757 | 831.9 | 759.3 | 703.3 | 742.6 | 451.3 | 699.1 | 774.7 | 284.6 | 383.7 | 449.3 | 701.2 | 639.5 | 704.6 | 684.8 | 698 | 399 | 536.5 | 487.1 | 477 | 441 | 617.7 | 471.7
2220.1 | 1981.1 | 568.8 | 227.52 | 265.9578 | 554.2 | 684.1 | 444.7 | 445.8 | 646 | 86.2 | 15.9 | 150.9 | 7.1 | 202.9 | 15.1 | 499.9 | 710.3 | 718.3 | 575 | 756.9 | 832.3 | 759.1 | 703.1 | 745 | 451.2 | 699.2 | 776 | 284.9 | 384 | 449.6 | 701.2 | 639.2 | 708.6 | 684.7 | 699.6 | 399.3 | 535.5 | 488 | 477 | 441.3 | 617.9 | 472
2221.1 | 1982.1 | 569.7 | 227.88 | 266.3786 | 553.8 | 687 | 444.8 | 444.8 | 643.4 | 86.2 | 15.9 | 151 | 6.2 | 198 | 14.2 | 500 | 710.3 | 718.7 | 575 | 757 | 832.3 | 759.5 | 702.6 | 741.4 | 451.1 | 699.1 | 776.2 | 285 | 384.3 | 449.7 | 701.1 | 637.9 | 707 | 684.3 | 697.9 | 399.6 | 535.6 | 488.7 | 477.1 | 441.9 | 618 | 472.2
2222.1 | 1983.1 | 568.2 | 227.28 | 265.6772 | 553.3 | 680.8 | 444.8 | 444.3 | 643.5 | 86.2 | 15.9 | 151.2 | 6.1 | 201.8 | 15.1 | 500.3 | 709.9 | 719.2 | 575.2 | 757 | 832.4 | 759.7 | 703.2 | 736.2 | 451.2 | 699.3 | 774.9 | 285.1 | 384.6 | 449.9 | 701.4 | 638.6 | 705 | 684.1 | 697.8 | 400 | 536.9 | 489.6 | 477.4 | 442 | 618.2 | 472.5
2223.1 | 1984.1 | 567.4 | 226.96 | 265.3032 | 552.9 | 681.4 | 444.7 | 445.2 | 644.6 | 86.1 | 15.9 | 151.4 | 6.4 | 187.9 | 14.1 | 500.5 | 710.1 | 721.6 | 575.3 | 757 | 832.2 | 759.9 | 703.2 | 735.9 | 451.2 | 699.5 | 773.8 | 285.2 | 384.9 | 450.1 | 701.2 | 639.3 | 704.2 | 683.7 | 697.8 | 400.5 | 536.5 | 489.5 | 477.2 | 442.2 | 618.5 | 472.8
2224.1 | 1985.1 | 567.2 | 226.88 | 265.2096 | 555.1 | 677.7 | 443.8 | 446.3 | 646.9 | 86.1 | 15.9 | 151.6 | 6.9 | 228.4 | 11.4 | 500.7 | 710.8 | 719.3 | 575.4 | 757.2 | 832.3 | 759.7 | 703.4 | 737.2 | 451.4 | 699.5 | 774.2 | 285.3 | 385.1 | 450.2 | 701 | 640.5 | 702 | 683.4 | 699.1 | 400.9 | 535.8 | 489.8 | 477.2 | 442.4 | 618.8 | 473.1
2225.1 | 1986.1 | 568.6 | 227.44 | 265.8643 | 555.1 | 669.9 | 443.5 | 447.8 | 645.7 | 86 | 15.9 | 151.8 | 8.1 | 210.3 | 7.9 | 501 | 711 | 714.9 | 575.5 | 757.1 | 833.1 | 759.7 | 704.2 | 733.2 | 451.3 | 699.4 | 773.9 | 285.5 | 385.5 | 450.4 | 701 | 640.5 | 697.6 | 683.6 | 696.8 | 401.3 | 535.1 | 490.5 | 477.3 | 442.8 | 619.1 | 473.4
2226.1 | 1987.1 | 566.8 | 226.72 | 265.0226 | 554.7 | 672.8 | 443.7 | 450.1 | 643.5 | 86 | 15.9 | 152 | 8.1 | 186.1 | 8 | 501.2 | 711.2 | 716.5 | 575.4 | 757.2 | 833.2 | 759.7 | 704 | 734.2 | 451.5 | 699.5 | 773.9 | 285.6 | 385.7 | 450.5 | 700.9 | 639 | 697.4 | 683.5 | 695.1 | 401.7 | 535.2 | 490.6 | 477.3 | 442.9 | 619.3 | 473.7
2227.1 | 1988.1 | 565.2 | 226.08 | 264.2745 | 555.1 | 672.6 | 443.6 | 450.5 | 642.8 | 86 | 15.9 | 152.1 | 8 | 179.5 | 8.2 | 501.4 | 711.7 | 716.7 | 575.5 | 757.3 | 833.4 | 759.9 | 703.9 | 735.5 | 451.4 | 699.5 | 774.2 | 285.6 | 386 | 450.7 | 701.3 | 639.3 | 696.2 | 683.3 | 696.9 | 402 | 535.7 | 490.7 | 477.4 | 443.2 | 619.5 | 474
2228.1 | 1989.1 | 566.9 | 226.76 | 265.0694 | 554.5 | 678.1 | 443 | 449.8 | 645.1 | 86.1 | 15.9 | 152.2 | 8.6 | 201.1 | 7.8 | 501.8 | 711 | 715.9 | 575.8 | 757.2 | 833.9 | 760 | 703.7 | 731.3 | 451.4 | 699.5 | 773.2 | 285.8 | 386.3 | 450.9 | 701.8 | 640.5 | 693.1 | 683.7 | 696.9 | 402.3 | 535.6 | 490.5 | 477.7 | 443.5 | 619.8 | 474.3
2229.1 | 1990.1 | 568.2 | 227.28 | 265.6772 | 554.2 | 679.3 | 442.4 | 449.2 | 644.8 | 86 | 15.9 | 152.2 | 7.9 | 210.3 | 10.2 | 502 | 710.1 | 715.4 | 575.9 | 757.2 | 834.5 | 760 | 703.9 | 727.4 | 451.3 | 699.7 | 772.6 | 286.2 | 386.5 | 451.1 | 701.8 | 640 | 691.6 | 684 | 695.2 | 402.5 | 536.8 | 489.6 | 478.2 | 443.6 | 620 | 474.6
2230.1 | 1991.1 | 567.8 | 227.12 | 265.4902 | 554.6 | 665.9 | 442.2 | 448.9 | 643.2 | 86 | 15.9 | 152.1 | 6.8 | 212.3 | 10.2 | 502.2 | 709.4 | 716.1 | 576 | 757.2 | 834.8 | 760.2 | 704.1 | 727.2 | 451.6 | 699.6 | 772.5 | 286.4 | 386.8 | 451.3 | 701.6 | 638.4 | 692.7 | 683.4 | 693.6 | 402.6 | 537.8 | 488.7 | 478.5 | 443.6 | 620.3 | 474.9
2231.1 | 1992.1 | 567.5 | 227 | 265.3499 | 553.1 | 652.9 | 442.5 | 448.4 | 640.4 | 86 | 15.9 | 152.1 | 7 | 207 | 10.4 | 502.4 | 709.7 | 714.7 | 576 | 757.2 | 835.3 | 760 | 703.9 | 726.5 | 451.6 | 699.8 | 771.9 | 286.7 | 387 | 451.6 | 701.1 | 636.2 | 688.7 | 682.5 | 690.2 | 402.6 | 537 | 489.3 | 478.6 | 443.8 | 620.4 | 475.2
2232.1 | 1993.1 | 566.9 | 226.76 | 265.0694 | 551.9 | 649.7 | 444 | 448.4 | 638.6 | 86.1 | 15.9 | 152.1 | 7.5 | 226.5 | 9.4 | 502.6 | 710.1 | 713.7 | 576.2 | 757.1 | 836 | 759.9 | 703.5 | 726 | 451.4 | 699.9 | 771.8 | 286.9 | 387.2 | 451.7 | 700.9 | 635.3 | 684.9 | 682.3 | 689.9 | 402.7 | 538.5 | 489.6 | 478.7 | 444.1 | 620.5 | 475.4
2233.1 | 1994.1 | 565.8 | 226.32 | 264.555 | 552.3 | 644.6 | 443.8 | 448.4 | 637.3 | 86.1 | 15.9 | 152.1 | 7.5 | 198.4 | 9.3 | 502.8 | 710.1 | 716.4 | 576.2 | 757.2 | 836.2 | 760 | 702.6 | 724.6 | 451.3 | 699.8 | 770.9 | 287.4 | 387.5 | 451.8 | 700.7 | 634.5 | 680.8 | 682 | 689.5 | 402.9 | 539.8 | 489.3 | 479 | 444.3 | 620.6 | 475.7
2234.1 | 1995.1 | 565.8 | 226.32 | 264.555 | 551.6 | 636.7 | 445 | 448.7 | 639.3 | 86.2 | 15.9 | 152.2 | 9 | 211.9 | 11.8 | 503 | 709.7 | 715.9 | 576.1 | 757.3 | 836.5 | 760.2 | 702.8 | 727.2 | 451.4 | 699.9 | 771 | 287.7 | 387.7 | 451.9 | 700.6 | 634.7 | 681.5 | 681.7 | 689.3 | 403 | 539.5 | 489 | 479 | 444.3 | 620.7 | 476
2235.1 | 1996.1 | 565.9 | 226.36 | 264.6018 | 551.6 | 629 | 445.1 | 448.6 | 639.8 | 86.2 | 15.9 | 152.5 | 9.2 | 208.5 | 13.5 | 503.6 | 709.3 | 707.6 | 576.4 | 757.1 | 834.8 | 760.5 | 702.9 | 723.2 | 451.3 | 699.8 | 770 | 287.9 | 387.9 | 452.1 | 701.1 | 635.9 | 681 | 682.1 | 690.1 | 403.2 | 540.2 | 490.3 | 479.6 | 444.8 | 620.8 | 476.3
2236.1 | 1997.1 | 566 | 226.4 | 264.6486 | 551.4 | 617.7 | 444 | 450.9 | 644.6 | 86.2 | 15.9 | 152.6 | 8.5 | 209.4 | 13 | 504.3 | 709.2 | 706.4 | 576.5 | 757 | 832.4 | 760.3 | 703.3 | 711.6 | 451.1 | 699.7 | 767.1 | 288.1 | 388.2 | 452.2 | 701.4 | 638.5 | 678 | 682.2 | 689.1 | 403.6 | 542.8 | 491.7 | 480.5 | 445.4 | 620.9 | 476.6
2237.1 | 1998.1 | 566.2 | 226.48 | 264.7421 | 549.9 | 617.8 | 443.7 | 453.6 | 645.3 | 86.2 | 15.9 | 152.7 | 7.8 | 219.2 | 14 | 504.8 | 708.3 | 713.3 | 576.3 | 757 | 832.3 | 760.2 | 704.1 | 708 | 451.1 | 700 | 765.9 | 288.3 | 388.5 | 452.3 | 701.4 | 638.8 | 677.8 | 682.5 | 687.6 | 404.4 | 542.7 | 491.1 | 480.4 | 445.5 | 621.1 | 477
2238.1 | 1999.1 | 565.6 | 226.24 | 264.4615 | 548.4 | 632.2 | 444.2 | 455.4 | 645.1 | 86.2 | 15.9 | 152.8 | 8.6 | 211 | 18.6 | 504.9 | 708.3 | 712.5 | 576.3 | 756.9 | 832.8 | 760 | 704.2 | 710.5 | 451.1 | 700 | 766.7 | 288.5 | 388.7 | 452.6 | 701.7 | 638.2 | 682.5 | 682.6 | 689.8 | 405.1 | 540.5 | 494.3 | 480 | 446.4 | 621.3 | 477.2
2239.1 | 2000.1 | 567.4 | 226.96 | 265.3032 | 547.6 | 638 | 444.1 | 454.9 | 643.2 | 86.2 | 15.9 | 152.9 | 7.9 | 225.1 | 17.8 | 505.1 | 708.5 | 711.2 | 576.3 | 757 | 833.5 | 760 | 705.7 | 711.9 | 451.1 | 700.1 | 767.5 | 288.6 | 389 | 452.8 | 701.7 | 637.1 | 685.7 | 682.2 | 691 | 405.5 | 539.1 | 499.5 | 479.7 | 447.6 | 621.5 | 477.4
2240.1 | 2001.1 | 568.8 | 227.52 | 265.9578 | 548.4 | 646.6 | 443.8 | 454.9 | 640.9 | 86.2 | 15.9 | 152.7 | 9 | 235 | 12.4 | 505.3 | 707.9 | 705.4 | 576.4 | 757.1 | 834.2 | 760.4 | 705.6 | 708.6 | 451.1 | 700.3 | 767.1 | 288.8 | 389.2 | 452.9 | 701.4 | 636.4 | 682.9 | 681.8 | 688.7 | 405.9 | 538.9 | 502.4 | 479.8 | 448.2 | 621.7 | 477.6
2241.1 | 2002.1 | 567.5 | 227 | 265.3499 | 548.9 | 647.5 | 444 | 455.9 | 638.5 | 86.3 | 15.9 | 152.5 | 9 | 204.3 | 12.2 | 505.5 | 707.2 | 699.5 | 576.5 | 756.9 | 834.8 | 760.3 | 705.3 | 704.7 | 451.4 | 700.4 | 767 | 288.7 | 389.5 | 453.2 | 701.3 | 635.1 | 679.7 | 681.6 | 686.6 | 406.3 | 538.8 | 503.9 | 479.8 | 448.8 | 622 | 477.9
2242.1 | 2003.1 | 566.9 | 226.76 | 265.0694 | 550 | 648.6 | 443.3 | 456.4 | 639.6 | 86.3 | 15.9 | 152.5 | 8.2 | 203.6 | 14 | 505.8 | 706.9 | 697.5 | 576.5 | 756.9 | 834.6 | 760.3 | 705.7 | 698.6 | 451.3 | 700.4 | 765.9 | 289.1 | 389.7 | 453.4 | 701.8 | 635.9 | 682.1 | 681.8 | 688.7 | 406.8 | 538.9 | 503.9 | 479.9 | 448.9 | 622.5 | 478.2
2243.1 | 2004.1 | 566.4 | 226.56 | 264.8356 | 549.6 | 652.7 | 444 | 458.3 | 640.4 | 86.4 | 15.9 | 152.4 | 7.4 | 203.6 | 14.3 | 506.1 | 707.4 | 699.4 | 576.6 | 756.8 | 834.8 | 760.3 | 705.3 | 695.9 | 451.2 | 700.7 | 764.5 | 289.3 | 389.9 | 453.4 | 702.1 | 636.3 | 677.9 | 682.4 | 688.9 | 407.2 | 538.8 | 502.9 | 480.2 | 448.9 | 622.7 | 478.5
2244.1 | 2005.1 | 567.6 | 227.04 | 265.3967 | 548.5 | 651.9 | 443.9 | 459.6 | 638.5 | 86.3 | 15.8 | 152.3 | 7.4 | 203.7 | 15.8 | 506.4 | 706.1 | 700.6 | 576.7 | 756.7 | 835 | 760.4 | 704.4 | 694 | 451.3 | 700.8 | 763.5 | 289.6 | 390.2 | 453.5 | 702.2 | 635 | 675.8 | 682.7 | 687.5 | 407.6 | 537.5 | 500.7 | 480 | 448.9 | 622.9 | 478.8
2245.1 | 2006.1 | 567.3 | 226.92 | 265.2564 | 547.8 | 653.9 | 444.5 | 459.8 | 636.9 | 86.4 | 15.8 | 152.2 | 7.2 | 217.6 | 16 | 506.6 | 705.8 | 706.9 | 576.8 | 756.7 | 834.8 | 760.3 | 703.9 | 697 | 451.7 | 701 | 764.2 | 289.9 | 390.4 | 453.7 | 702.6 | 633.8 | 680.1 | 683.1 | 686.9 | 407.8 | 535.8 | 498.8 | 479.9 | 448.8 | 623.1 | 479.1
2246.1 | 2007.1 | 566.9 | 226.76 | 265.0694 | 547.5 | 664.7 | 445.5 | 459.8 | 635.3 | 86.5 | 15.8 | 152.1 | 7.5 | 217.2 | 14.8 | 506.8 | 706.4 | 708 | 576.9 | 756.8 | 834.6 | 760.1 | 703.4 | 705.9 | 451.4 | 701.2 | 765.5 | 290.1 | 390.7 | 454 | 702.5 | 632.8 | 681.9 | 682.9 | 687.6 | 407.8 | 534.3 | 496.9 | 479.7 | 448.8 | 623.3 | 479.2
2247.1 | 2008.1 | 566.9 | 226.76 | 265.0694 | 548.6 | 662.4 | 445 | 458.1 | 635.6 | 86.6 | 15.8 | 152.1 | 7.7 | 214.2 | 14.8 | 507 | 706.2 | 708 | 576.9 | 756.8 | 834.6 | 760.3 | 702.6 | 707.4 | 451.5 | 701.3 | 765.2 | 290.3 | 391 | 454 | 702.2 | 632.3 | 687 | 682.3 | 689.4 | 407.8 | 533.5 | 495.8 | 479.8 | 448.9 | 623.5 | 479.5
2248.1 | 2009.1 | 567.1 | 226.84 | 265.1629 | 547.2 | 655.3 | 446.4 | 457.5 | 636.7 | 86.6 | 15.8 | 151.9 | 7.4 | 206.9 | 14.4 | 507.2 | 705.7 | 705.9 | 577 | 756.8 | 834.6 | 760.3 | 701.6 | 706.5 | 451.7 | 701.2 | 764.6 | 290.4 | 391.3 | 454.1 | 702 | 633.5 | 687.1 | 682.2 | 690.7 | 407.9 | 533.6 | 496.2 | 480.1 | 449.1 | 623.7 | 479.7
2249.1 | 2010.1 | 567.2 | 226.88 | 265.2096 | 544.7 | 654 | 447.9 | 458 | 638.1 | 86.7 | 15.8 | 152 | 7.1 | 194.4 | 15.6 | 507.5 | 704.6 | 701.6 | 577.3 | 756.8 | 834.6 | 760.5 | 702 | 704.5 | 451.6 | 701.3 | 763.9 | 290.8 | 391.7 | 454.3 | 702.1 | 634.3 | 687.8 | 682.7 | 689.4 | 408.1 | 534.6 | 497.2 | 480.3 | 449.2 | 623.7 | 479.9
2250.1 | 2011.1 | 566.6 | 226.64 | 264.9291 | 544.9 | 649.7 | 446.1 | 459 | 641.2 | 86.8 | 15.8 | 152 | 6.7 | 221.4 | 13.4 | 507.7 | 703.4 | 699.7 | 577.3 | 756.8 | 834.4 | 760.6 | 703.1 | 702.1 | 451.8 | 701.6 | 763.6 | 290.7 | 391.9 | 454.6 | 702.4 | 636.6 | 683.3 | 682.8 | 689.4 | 408.5 | 534.9 | 499.2 | 480.6 | 450.1 | 623.9 | 480.2
2251.1 | 2012.1 | 566.3 | 226.52 | 264.7888 | 545.3 | 641 | 443.9 | 459.8 | 644.7 | 86.9 | 15.8 | 152.1 | 6 | 203 | 11.1 | 508.1 | 703.9 | 702.8 | 577.3 | 756.9 | 833.9 | 760.4 | 703.3 | 700.4 | 451.8 | 701.9 | 762.7 | 291.1 | 392.2 | 454.9 | 702.6 | 638.8 | 680.1 | 682.8 | 689.5 | 409 | 535.1 | 499.5 | 480.7 | 450.6 | 624.2 | 480.5
2252.1 | 2013.1 | 566.5 | 226.6 | 264.8823 | 543.6 | 643.8 | 444 | 461.4 | 643.4 | 87.1 | 15.8 | 152.1 | 6.2 | 213.2 | 13.3 | 508.3 | 703.8 | 708.8 | 577.4 | 756.9 | 834.1 | 760.4 | 702.7 | 701.7 | 452.1 | 702 | 762.5 | 291.5 | 392.5 | 454.9 | 702.6 | 638.5 | 681.8 | 682.9 | 689.3 | 409.4 | 533.7 | 498.6 | 480.5 | 450.7 | 624.4 | 480.8
2253.1 | 2014.1 | 566.2 | 226.48 | 264.7421 | 544.7 | 649.9 | 444.2 | 461.2 | 643.5 | 87.3 | 15.8 | 152.2 | 7.5 | 215.2 | 13.1 | 508.6 | 703.6 | 714.9 | 577.5 | 756.8 | 834.5 | 760.3 | 701.7 | 703.5 | 452.4 | 702.2 | 762.4 | 291.8 | 392.8 | 455 | 702.6 | 638.9 | 682.9 | 683.3 | 691.3 | 409.7 | 533.3 | 498.2 | 480.8 | 450.8 | 624.6 | 481
2254.1 | 2015.1 | 565.4 | 226.16 | 264.368 | 545.3 | 654.4 | 444.5 | 460.5 | 648.2 | 87.4 | 15.8 | 152.1 | 8.1 | 209.8 | 14.2 | 508.9 | 703.5 | 717.1 | 577.7 | 756.9 | 834.6 | 760.4 | 701.8 | 706.5 | 452.7 | 702.2 | 762.1 | 292 | 392.9 | 455.1 | 702.7 | 640.1 | 686.5 | 683.3 | 693.4 | 409.9 | 534 | 496.8 | 480.9 | 450.7 | 624.8 | 481.2
2255.1 | 2016.1 | 566 | 226.4 | 264.6486 | 545 | 653.8 | 445.5 | 459.5 | 648.5 | 87.5 | 15.8 | 152.3 | 8.3 | 204.7 | 14.5 | 509.2 | 704.3 | 721.6 | 577.8 | 756.9 | 834.1 | 760.2 | 702.3 | 709.8 | 453 | 702.2 | 762.6 | 292.2 | 393.2 | 455.2 | 702.5 | 640.7 | 684.3 | 683.2 | 692.4 | 410.1 | 533.7 | 495.2 | 481 | 450.7 | 625 | 481.5
2256.1 | 2017.1 | 566.7 | 226.68 | 264.9759 | 544.5 | 650.5 | 446.3 | 459.5 | 647.8 | 87.6 | 15.8 | 152.4 | 6.7 | 206.7 | 14.9 | 509.6 | 705.3 | 719.8 | 577.9 | 756.9 | 834.1 | 760.1 | 701.7 | 712.2 | 453.4 | 702.3 | 763.3 | 292.4 | 393.5 | 455.3 | 702.4 | 641.2 | 684.1 | 683.1 | 692.4 | 410.3 | 533.9 | 496.4 | 481.4 | 450.9 | 625.2 | 481.8
2257.1 | 2018.1 | 567.2 | 226.88 | 265.2096 | 544.4 | 649 | 446.7 | 459.3 | 649.9 | 87.7 | 15.8 | 152.6 | 7.3 | 210.2 | 15.3 | 510.3 | 704.9 | 718.9 | 578.1 | 756.8 | 834.2 | 760.1 | 701.2 | 710.4 | 453.7 | 702.3 | 762.4 | 292.7 | 393.8 | 455.5 | 702.7 | 644 | 683.3 | 683.8 | 694 | 410.7 | 537 | 499.4 | 482.6 | 451.7 | 625.4 | 482.1
2258.1 | 2019.1 | 567.2 | 226.88 | 265.2096 | 545.3 | 638.2 | 446.8 | 460.2 | 653.3 | 87.8 | 15.8 | 152.8 | 7.3 | 215.4 | 16.7 | 510.4 | 705.4 | 716.8 | 578.2 | 756.8 | 834.1 | 760.2 | 701.3 | 705.5 | 454.1 | 702.3 | 761 | 292.8 | 394.2 | 455.7 | 702.9 | 646.3 | 684.6 | 684.4 | 693.4 | 411.6 | 544.1 | 501.1 | 484.6 | 452.6 | 625.7 | 482.6
2259.1 | 2020.1 | 566.9 | 226.76 | 265.0694 | 544.4 | 633.2 | 447.3 | 463.3 | 655.1 | 87.9 | 15.8 | 152.9 | 6.9 | 223.5 | 14.5 | 510.6 | 705.4 | 715.7 | 578.3 | 756.8 | 835.1 | 760.1 | 701.5 | 704.2 | 454.4 | 702.4 | 760.6 | 293 | 394.4 | 455.8 | 703 | 646.3 | 685.1 | 684.6 | 692.1 | 412.4 | 545.3 | 501.1 | 484.8 | 452.8 | 625.9 | 483.2
2260.1 | 2021.1 | 567.4 | 226.96 | 265.3032 | 545.2 | 626.8 | 449.4 | 465.1 | 651.1 | 88 | 15.8 | 153 | 8.1 | 201 | 13.7 | 510.8 | 705.1 | 711.6 | 578.4 | 756.6 | 836.3 | 760.1 | 700.8 | 702.2 | 454.9 | 702.4 | 759.5 | 293.1 | 394.7 | 456.1 | 702.6 | 643.8 | 684.7 | 684.3 | 688.7 | 413 | 544 | 501 | 484.7 | 453 | 626.1 | 483.6
2261.1 | 2022.1 | 565.6 | 226.24 | 264.4615 | 549.1 | 629.3 | 450.5 | 464.9 | 647.4 | 88 | 15.8 | 153.2 | 8.6 | 207.4 | 14.3 | 511.2 | 705.5 | 709.2 | 578.6 | 756.4 | 836.6 | 759.9 | 700.9 | 699.1 | 455.8 | 702.4 | 758.7 | 293.3 | 395 | 456.4 | 702.7 | 642.3 | 687.8 | 684.5 | 687.9 | 413.3 | 546.2 | 502 | 485.8 | 453.3 | 626.2 | 483.9
2262.1 | 2023.1 | 565.1 | 226.04 | 264.2277 | 554.6 | 630.2 | 449.6 | 464.3 | 645.5 | 88.1 | 15.8 | 153.3 | 8.1 | 206 | 13.3 | 511.6 | 705 | 704.4 | 578.7 | 756.3 | 836.6 | 759.8 | 701.5 | 697.8 | 456.3 | 702.5 | 758.6 | 293.6 | 395.3 | 456.6 | 702.6 | 640.8 | 684.4 | 684.6 | 685.4 | 413.6 | 556 | 502.4 | 487.3 | 453.6 | 626.4 | 484.2
2263.1 | 2024.1 | 566.4 | 226.56 | 264.8356 | 558 | 631.4 | 448.5 | 464.8 | 642.7 | 88 | 15.8 | 153.4 | 7.3 | 208.3 | 12.1 | 512 | 704.1 | 706.6 | 579 | 756.2 | 836 | 759.3 | 701.6 | 694.4 | 456.8 | 702.5 | 758.6 | 293.8 | 395.6 | 456.6 | 702.5 | 639.5 | 678.4 | 684.5 | 682.8 | 413.8 | 559.6 | 501.7 | 487.9 | 453.8 | 626.7 | 484.7
2264.1 | 2025.1 | 566.8 | 226.72 | 265.0226 | 556.7 | 634.7 | 448.8 | 466 | 640.6 | 88 | 15.8 | 153.3 | 5.5 | 207.7 | 13.9 | 512.4 | 702.2 | 701.7 | 579.1 | 756.1 | 835.9 | 759 | 701.5 | 691.6 | 457.4 | 702.5 | 757.3 | 294.1 | 395.8 | 456.8 | 702.5 | 638.4 | 676.4 | 684.3 | 682.2 | 413.8 | 560.8 | 500.2 | 488 | 453.7 | 627 | 485.1
2265.1 | 2026.1 | 566.9 | 226.76 | 265.0694 | 559.4 | 640.4 | 448.4 | 467.9 | 637.4 | 87.9 | 15.8 | 153.2 | 5.5 | 209.1 | 17.3 | 512.8 | 701.2 | 702.4 | 579.2 | 755.9 | 836.1 | 758.9 | 701.5 | 687.8 | 458 | 702.4 | 755.7 | 294.3 | 396.1 | 456.9 | 702.2 | 636.6 | 672.5 | 683.7 | 679.8 | 413.9 | 558.7 | 498.4 | 487.7 | 453.6 | 627.3 | 485.5
2266.1 | 2027.1 | 566.2 | 226.48 | 264.7421 | 561.5 | 641.1 | 448.1 | 468.3 | 633.3 | 87.9 | 15.8 | 153.1 | 7 | 212.2 | 16.2 | 513.1 | 701 | 710 | 579.5 | 756 | 835.5 | 758.8 | 702.2 | 693.8 | 458.6 | 702.6 | 755.7 | 294.4 | 396.4 | 457 | 701.9 | 634.2 | 669.4 | 683.1 | 678.5 | 413.9 | 556.2 | 496.7 | 487.4 | 453.6 | 627.6 | 485.7
2267.1 | 2028.1 | 566.7 | 226.68 | 264.9759 | 559.4 | 631.3 | 446.8 | 467.1 | 632.7 | 87.8 | 15.8 | 153 | 8.1 | 214.9 | 13 | 513.4 | 702.4 | 715.2 | 579.7 | 756.2 | 834.7 | 758.4 | 702.5 | 699.9 | 459.6 | 702.6 | 756.6 | 294.5 | 396.6 | 457.3 | 702 | 633.7 | 671.7 | 683.1 | 682 | 413.7 | 553.6 | 495.4 | 487.4 | 453.7 | 627.9 | 486
2268.1 | 2029.1 | 568.5 | 227.4 | 265.8175 | 557.6 | 628.1 | 446.2 | 467.9 | 634 | 87.8 | 15.8 | 152.8 | 8.2 | 204.7 | 9.8 | 513.5 | 703.6 | 720.3 | 579.8 | 756.3 | 833.9 | 758 | 701.9 | 706.9 | 460.2 | 702.6 | 757.8 | 294.6 | 396.9 | 457.5 | 702 | 634.3 | 670.8 | 683.1 | 683.9 | 413.5 | 553.5 | 494.4 | 487.7 | 453.8 | 628.1 | 486.3
2269.1 | 2030.1 | 569.1 | 227.64 | 266.098 | 559.3 | 646.2 | 445 | 469 | 635 | 87.8 | 15.8 | 152.6 | 8.4 | 187.8 | 7.4 | 513.7 | 704.5 | 721.4 | 579.9 | 756.3 | 834.3 | 757.6 | 700.8 | 718.4 | 460.7 | 702.6 | 760.6 | 294.8 | 397.1 | 457.6 | 701.8 | 634.3 | 669.5 | 682.3 | 683.8 | 413.5 | 554.3 | 493.3 | 488 | 453.8 | 628.2 | 486.7
2270.1 | 2031.1 | 567.6 | 227.04 | 265.3967 | 559.6 | 646.4 | 443.9 | 469.2 | 633.9 | 87.9 | 15.8 | 152.5 | 8.2 | 211.9 | 9.9 | 513.9 | 704.4 | 722.8 | 580 | 756.3 | 834.4 | 757.6 | 699.8 | 721.5 | 461.4 | 702.5 | 761.3 | 295 | 397.4 | 457.6 | 701.5 | 634.5 | 669 | 681.9 | 682.3 | 413.5 | 554 | 492.5 | 487.8 | 453.8 | 628.2 | 487
2271.1 | 2032.1 | 567.2 | 226.88 | 265.2096 | 557.7 | 655.5 | 443.3 | 469.4 | 635.8 | 88 | 15.8 | 152.3 | 7.6 | 210.4 | 16.5 | 514.1 | 704.1 | 725.1 | 580 | 756.3 | 834.3 | 757.5 | 699.9 | 722.3 | 462.1 | 702.3 | 761.1 | 295.3 | 397.7 | 457.8 | 701.4 | 635.6 | 674.7 | 681.7 | 684.9 | 413.5 | 552.5 | 492.4 | 487.4 | 453.9 | 628.3 | 487.3
2272.1 | 2033.1 | 566.3 | 226.52 | 264.7888 | 556.4 | 658.4 | 442.9 | 468 | 640.8 | 88.2 | 15.8 | 152.3 | 7.7 | 205.9 | 16.9 | 514.3 | 704 | 724.6 | 580.1 | 756.4 | 834.1 | 757.6 | 700 | 723.4 | 462.7 | 702.2 | 761.1 | 295.4 | 398 | 458.2 | 701.4 | 637.4 | 680.3 | 681.5 | 687.3 | 413.6 | 550.5 | 491.9 | 487.1 | 454 | 628.4 | 487.6
2273.1 | 2034.1 | 567.5 | 227 | 265.3499 | 555.7 | 665.8 | 443.9 | 466.5 | 645.8 | 88.2 | 15.8 | 152.1 | 8 | 206.7 | 15.5 | 514.7 | 703.4 | 726.7 | 580.3 | 756.3 | 833.7 | 757.3 | 699.6 | 724 | 463.1 | 702.1 | 760.9 | 295.6 | 398.2 | 458.7 | 701.2 | 639 | 682.4 | 681.8 | 688 | 413.5 | 548.4 | 490.9 | 486.8 | 453.9 | 628.5 | 487.8
2274.1 | 2035.1 | 567.9 | 227.16 | 265.537 | 555.1 | 662.1 | 445.8 | 464.5 | 648.1 | 88.1 | 15.8 | 152 | 7.5 | 206.1 | 17 | 514.8 | 703 | 727 | 580.3 | 756.4 | 833.3 | 757.4 | 699.4 | 728.7 | 463.8 | 702.2 | 761.9 | 295.9 | 398.6 | 458.7 | 701.1 | 639 | 683.4 | 682.1 | 686.8 | 413.4 | 546.6 | 490 | 486.6 | 453.9 | 628.6 | 488
2275.1 | 2036.1 | 567.5 | 227 | 265.3499 | 554.7 | 654.6 | 446.9 | 462.4 | 646.3 | 88 | 15.8 | 152 | 7.5 | 209.6 | 20 | 514.9 | 702.8 | 727.4 | 580.3 | 756.3 | 833.4 | 757 | 698.9 | 729.2 | 464.2 | 702 | 762.3 | 296.3 | 398.8 | 458.7 | 700.9 | 638.7 | 681.7 | 681.7 | 685.2 | 413.5 | 547 | 490.3 | 486.8 | 454 | 628.7 | 488.3
2276.1 | 2037.1 | 567.2 | 226.88 | 265.2096 | 555.6 | 660.8 | 447.2 | 462.6 | 643.1 | 87.9 | 15.8 | 152.2 | 7.9 | 205.3 | 25.2 | 515.2 | 702.1 | 725.4 | 580.4 | 756.3 | 833.2 | 757.2 | 698.3 | 726.4 | 464.7 | 702.2 | 762.6 | 296.6 | 399.1 | 458.8 | 700.6 | 637.5 | 685.5 | 681.2 | 683.9 | 413.5 | 548.2 | 491.5 | 486.9 | 454.2 | 628.8 | 488.6
2277.1 | 2038.1 | 567.4 | 226.96 | 265.3032 | 557.5 | 661.7 | 447.9 | 463.2 | 640.3 | 88 | 15.8 | 152.4 | 10.1 | 209.4 | 23.1 | 515.6 | 701 | 722.2 | 580.7 | 756.1 | 833.3 | 757.2 | 698.2 | 723.5 | 465.2 | 702.1 | 762.7 | 296.9 | 399.4 | 459.1 | 700.4 | 635.6 | 687.6 | 680.7 | 684.1 | 413.5 | 547 | 491.6 | 487 | 454.2 | 628.8 | 488.9
2278.1 | 2039.1 | 567.7 | 227.08 | 265.4434 | 558 | 648.4 | 448.1 | 462 | 637.9 | 88 | 15.8 | 152.5 | 10.2 | 204.6 | 22.7 | 515.8 | 699.8 | 719.6 | 580.8 | 756.1 | 833.4 | 756.9 | 698.4 | 719.5 | 465.7 | 701.9 | 761.2 | 297 | 399.7 | 459.5 | 700.2 | 634.5 | 690.3 | 680 | 684.2 | 413.6 | 546 | 490.4 | 486.8 | 454.1 | 628.8 | 489.2
2279.1 | 2040.1 | 566.7 | 226.68 | 264.9759 | 557.5 | 644.1 | 448.2 | 460.7 | 636.9 | 88.1 | 15.8 | 152.8 | 12 | 215.3 | 21 | 516 | 699.2 | 720 | 581 | 755.9 | 834 | 756.6 | 698.6 | 713.8 | 466.3 | 701.9 | 760.7 | 297.1 | 400 | 459.6 | 700 | 633.6 | 689.5 | 680 | 684.5 | 413.6 | 545.2 | 489.8 | 486.5 | 454 | 628.9 | 489.4
2280.1 | 2041.1 | 283.3 | 113.32 | 132.4646 | 556.7 | 641 | 448.5 | 460 | 634.6 | 88.2 | 15.8 | 152.9 | 11.2 | 226.4 | 17.8 | 516.4 | 698.9 | 724.5 | 581.1 | 756 | 834.5 | 756.3 | 698.9 | 715.3 | 466.6 | 701.9 | 760.7 | 297.5 | 400.3 | 459.6 | 699.8 | 632.3 | 687.1 | 679.8 | 683.2 | 413.6 | 544.6 | 490 | 486.4 | 454.1 | 628.9 | 489.7
2281.1 | 2042.1 | -6.8 | 0 | 0 | 555.6 | 645.3 | 449.5 | 458.9 | 632.4 | 88.3 | 15.7 | 153.1 | 11.3 | 220.3 | 17.7 | 516.8 | 698.4 | 723.3 | 581.2 | 755.8 | 834.7 | 755.8 | 697.7 | 718 | 466.9 | 701.9 | 760.7 | 297.9 | 400.6 | 459.6 | 699.4 | 630.9 | 685.3 | 679.3 | 682.4 | 413.5 | 545.3 | 489.5 | 486.2 | 454.1 | 629.1 | 490
2282.1 | 2043.1 | -6.8 | 0 | 0 | 553.5 | 649.9 | 448.8 | 457.6 | 628.2 | 88.3 | 15.7 | 153.2 | 11 | 222.1 | 16.9 | 517.2 | 697.3 | 713.3 | 581.5 | 755.5 | 833.2 | 755.6 | 695.3 | 704 | 467.1 | 701.9 | 756.6 | 298.3 | 400.9 | 459.4 | 698.7 | 628.6 | 677.6 | 678.4 | 678.4 | 413.4 | 544.5 | 488.7 | 485.8 | 453.9 | 629.1 | 490.2
2283.1 | 2044.1 | -6.8 | 0 | 0 | 550.9 | 645.8 | 447 | 456.7 | 620.6 | 88.3 | 15.7 | 153.3 | 8.6 | 232.2 | 16.2 | 517.2 | 697.2 | 699 | 581.7 | 755.3 | 826.3 | 755.2 | 694.1 | 687.5 | 467.5 | 701.5 | 751.7 | 298.7 | 401.1 | 459.2 | 697.8 | 625.5 | 668.2 | 677.5 | 674 | 413.1 | 543 | 486.8 | 485.4 | 453.5 | 629 | 490.4
2284.1 | 2045.1 | -6.8 | 0 | 0 | 546.1 | 631.9 | 444.8 | 454.4 | 615.1 | 88.3 | 15.7 | 153.2 | 8.4 | 231.7 | 14.1 | 517.2 | 697.2 | 687.1 | 581.7 | 755.1 | 818 | 754.1 | 693.5 | 672.5 | 467.5 | 700.9 | 747.2 | 299.1 | 401.4 | 459.2 | 697.2 | 622.5 | 659.7 | 676.9 | 669.8 | 412.8 | 540.5 | 483.8 | 484.5 | 453 | 628.9 | 490.6
2285.1 | 2046.1 | -6.8 | 0 | 0 | 541.7 | 619.7 | 442.4 | 451.1 | 611.1 | 88.2 | 15.7 | 153.1 | 8.3 | 232.3 | 11.1 | 517.3 | 697.1 | 676.3 | 581.8 | 754.8 | 810.2 | 753.6 | 691.2 | 657.7 | 467.8 | 700.8 | 742.6 | 299.3 | 401.7 | 459.1 | 696.7 | 620 | 654 | 676.3 | 667.9 | 412.5 | 538.6 | 480.8 | 483.8 | 452.4 | 628.8 | 490.8
2286.1 | 2047.1 | -6.8 | 0 | 0 | 539.4 | 614.1 | 440 | 447.8 | 610.6 | 88.2 | 15.7 | 152.6 | 7.5 | 233 | 9.2 | 517.4 | 697.1 | 666.5 | 581.8 | 754.5 | 802.5 | 753.1 | 688.6 | 644.5 | 467.8 | 700.5 | 738.1 | 299.7 | 401.9 | 459 | 696.1 | 618.8 | 647 | 676 | 665.1 | 412 | 537.9 | 477.6 | 483.5 | 451.8 | 628.8 | 491
2287.1 | 2048.1 | -6.8 | 0 | 0 | 536.1 | 611.2 | 437.2 | 444.5 | 608.6 | 88.1 | 15.7 | 151.9 | 6.9 | 246.5 | 9.6 | 517.4 | 697.6 | 657.4 | 581.9 | 754.2 | 795 | 752.3 | 685.8 | 633.6 | 467.9 | 700.2 | 734.2 | 299.9 | 402.1 | 459 | 695.8 | 617.7 | 638.7 | 675.9 | 660.8 | 411.5 | 537.4 | 474.1 | 483.1 | 451.2 | 628.8 | 491.2
2288.1 | 2049.1 | -6.8 | 0 | 0 | 534.1 | 610.9 | 434.5 | 441.8 | 605.2 | 88 | 15.7 | 151.2 | 7.3 | 242.2 | 11 | 517.5 | 698.1 | 649.5 | 581.8 | 753.9 | 788.1 | 751.5 | 683 | 623.9 | 468.3 | 700.1 | 730 | 300.2 | 402.3 | 458.9 | 695.2 | 616.1 | 630.7 | 675.4 | 656.8 | 410.9 | 536.6 | 470.7 | 482.8 | 450.6 | 628.7 | 491.4
2289.1 | 2050.1 | -6.8 | 0 | 0 | 531.4 | 608.3 | 432 | 439 | 605.1 | 87.9 | 15.7 | 150.3 | 7.3 | 220.7 | 12.1 | 517.6 | 698.7 | 641.6 | 581.8 | 753.5 | 781.6 | 750.5 | 680.3 | 613.4 | 468.7 | 699.8 | 726.2 | 301.1 | 402.5 | 458.9 | 694.8 | 617.2 | 625 | 675.5 | 654.1 | 410.3 | 536.5 | 467.8 | 482.5 | 450 | 628.7 | 491.6
2290.1 | 2051.1 | -6.8 | 0 | 0 | 529.8 | 606.8 | 430.8 | 436.4 | 605.2 | 87.8 | 15.7 | 149.4 | 6.6 | 247.4 | 11.2 | 517.7 | 698.5 | 634.9 | 581.8 | 753.2 | 775.7 | 749.6 | 677.6 | 604 | 469.3 | 699.6 | 722.9 | 301.4 | 402.7 | 458.9 | 694.4 | 616.5 | 620.8 | 674.9 | 652.4 | 409.5 | 535.3 | 465 | 482 | 449.4 | 628.7 | 491.8
2291.1 | 2052.1 | -6.8 | 0 | 0 | 528 | 601.8 | 429.2 | 433.9 | 604.7 | 87.7 | 15.7 | 148.3 | 7.4 | 208.3 | 10.4 | 517.8 | 698.3 | 628.1 | 581.8 | 752.8 | 769.6 | 748.8 | 674 | 596.4 | 469.7 | 699.2 | 719.6 | 301.5 | 402.8 | 458.8 | 693.8 | 615 | 618.1 | 674.5 | 650.7 | 408.7 | 533 | 462.8 | 481.6 | 448.9 | 628.8 | 491.9
2292.1 | 2053.1 | -6.8 | 0 | 0 | 525.4 | 603.5 | 428.7 | 431.3 | 604.6 | 87.6 | 15.7 | 147.3 | 6.9 | 262.8 | 11.3 | 517.9 | 698.1 | 621.9 | 581.8 | 752.4 | 763.8 | 748 | 670.6 | 588.5 | 470 | 699.1 | 715.8 | 301.7 | 403 | 458.7 | 693.3 | 614.3 | 614.1 | 674 | 649.4 | 407.9 | 530.8 | 460 | 481.2 | 448.4 | 628.8 | 492
2293.1 | 2054.1 | -6.8 | 0 | 0 | 523.9 | 602.3 | 429.1 | 429 | 601.4 | 87.4 | 15.7 | 146.3 | 6.8 | 241.5 | 10.2 | 518 | 698.7 | 615.8 | 581.8 | 752 | 758.6 | 747.2 | 668.6 | 581.3 | 470.5 | 698.8 | 712.8 | 301.6 | 403.2 | 458.6 | 692.7 | 612.3 | 610.7 | 673.1 | 648.2 | 407.3 | 529.4 | 457.8 | 481 | 447.8 | 628.8 | 492.2
2294.1 | 2055.1 | -6.8 | 0 | 0 | 521.5 | 597.5 | 428.8 | 426.7 | 598.4 | 87.3 | 15.7 | 145.2 | 5.8 | 218.2 | 12.3 | 518.2 | 699.2 | 610.3 | 581.9 | 751.6 | 753.9 | 746.3 | 666.4 | 574.8 | 471.1 | 698.5 | 709.6 | 301.8 | 403.4 | 458.6 | 692 | 610.1 | 605.8 | 672.2 | 646.9 | 406.5 | 528 | 455.7 | 480.5 | 447.3 | 628.7 | 492.3
2295.1 | 2056.1 | -6.8 | 0 | 0 | 518.6 | 598.9 | 428.5 | 424.7 | 595.2 | 87.1 | 15.7 | 144.3 | 6.7 | 201.5 | 16.7 | 518.3 | 698.2 | 604.4 | 582 | 751.3 | 749.3 | 745.4 | 664.2 | 567.7 | 471.6 | 698.1 | 705.7 | 302.1 | 403.6 | 458.5 | 691.3 | 607.7 | 602.3 | 671.3 | 645.3 | 405.7 | 526 | 453.4 | 480 | 446.8 | 628.6 | 492.4
2296.1 | 2057.1 | -6.8 | 0 | 0 | 518 | 595.7 | 427.9 | 423.2 | 592.2 | 87 | 15.7 | 143.3 | 6.9 | 210 | 15.8 | 518.3 | 697.7 | 599.9 | 582 | 750.9 | 745 | 744.3 | 662 | 563.7 | 471.9 | 697.8 | 702.5 | 302.3 | 403.8 | 458.4 | 690.5 | 605.3 | 598.7 | 670.2 | 643.9 | 405 | 523.8 | 451.3 | 479.5 | 446.2 | 628.5 | 492.6
2297.1 | 2058.1 | -6.8 | 0 | 0 | 516.5 | 591.6 | 426.8 | 421.6 | 590.6 | 86.8 | 15.7 | 142.5 | 6.3 | 205.2 | 13 | 518.4 | 697.4 | 595.9 | 582 | 750.5 | 740.9 | 743.5 | 660.3 | 560.4 | 472.5 | 697.3 | 699.1 | 302.3 | 404 | 458.4 | 689.6 | 603.3 | 596.4 | 669.5 | 642.4 | 404.3 | 522.4 | 449.4 | 479.1 | 445.7 | 628.4 | 492.6
2298.1 | 2059.1 | -6.8 | 0 | 0 | 515.9 | 589.7 | 425.9 | 419.9 | 590.2 | 86.7 | 15.7 | 141.7 | 6.1 | 223.5 | 10.3 | 518.5 | 696.7 | 591.5 | 582 | 750 | 737.3 | 742 | 658.7 | 554.8 | 472.7 | 696.9 | 695.7 | 302.4 | 404.2 | 458.4 | 688.9 | 602.4 | 597.4 | 668.9 | 641.2 | 403.6 | 521 | 447.5 | 478.8 | 445.2 | 628.5 | 492.7
2299.1 | 2060.1 | -6.8 | 0 | 0 | 513.9 | 587.5 | 425.7 | 418.2 | 590.1 | 86.5 | 15.7 | 140.9 | 6.3 | 251.2 | 6.7 | 518.7 | 697.1 | 587 | 582.1 | 749.6 | 734 | 740.9 | 656.9 | 550.4 | 473.4 | 696.6 | 693 | 302.4 | 404.3 | 458.3 | 688.1 | 601.8 | 593.3 | 667.9 | 638.8 | 403 | 520.6 | 445.7 | 478.6 | 444.7 | 628.5 | 492.8
2300.1 | 2061.1 | -6.8 | 0 | 0 | 512.7 | 585.7 | 425 | 416.6 | 588.5 | 86.4 | 15.7 | 140.3 | 5.8 | 199.9 | 4.5 | 518.8 | 696.6 | 583 | 582.1 | 749.2 | 730.9 | 740.4 | 655.7 | 547.2 | 474.3 | 696.2 | 689.9 | 302.3 | 404.5 | 458.2 | 687.3 | 600.7 | 589 | 666.8 | 636.5 | 402.3 | 520.8 | 444.2 | 478.3 | 444.2 | 628.4 | 492.9
2301.1 | 2062.1 | -6.8 | 0 | 0 | 511.5 | 582.5 | 424.6 | 415.6 | 584.9 | 86.3 | 15.7 | 139.7 | 6.9 | 269.9 | 3.6 | 519 | 696 | 578.9 | 582.1 | 748.7 | 728.3 | 739.5 | 653.9 | 545.3 | 474.8 | 695.7 | 686.6 | 302.4 | 404.6 | 458.1 | 686.4 | 598.9 | 585.1 | 665.5 | 634.3 | 401.7 | 520.6 | 442.7 | 478 | 443.7 | 628.4 | 493
2302.1 | 2063.1 | -6.8 | 0 | 0 | 508.5 | 583.8 | 424.1 | 415 | 581.6 | 86.2 | 15.7 | 139.1 | 6 | 217.7 | 6.6 | 519.2 | 695.9 | 575.1 | 582.1 | 748.3 | 725.7 | 739 | 651.6 | 543.9 | 475.5 | 695 | 683.9 | 302.6 | 404.8 | 458 | 685.6 | 596.4 | 584.1 | 664.5 | 634.3 | 401.1 | 520.3 | 440.9 | 477.8 | 443.3 | 628.4 | 493.1
2303.1 | 2064.1 | -6.8 | 0 | 0 | 507.1 | 586.1 | 423.2 | 414.2 | 581 | 86.1 | 15.7 | 138.5 | 5.8 | 217.6 | 10.9 | 519.3 | 695.1 | 571.9 | 582.2 | 747.9 | 722.8 | 738.3 | 650.3 | 540.7 | 476.4 | 694.4 | 681.6 | 302.6 | 405 | 457.8 | 684.6 | 595.5 | 581.8 | 663.5 | 633.9 | 400.5 | 519.7 | 439.5 | 477.7 | 442.7 | 628.3 | 493.2
2304.1 | 2065.1 | -6.8 | 0 | 0 | 505.7 | 580.9 | 422.3 | 413.4 | 579.4 | 85.9 | 15.7 | 137.9 | 6.6 | 210.1 | 12.7 | 519.4 | 695.1 | 569.2 | 582.1 | 747.5 | 719.8 | 737.7 | 649.1 | 539 | 477.1 | 693.9 | 679.3 | 302.1 | 405.1 | 457.7 | 684 | 593.6 | 580 | 663.2 | 632.9 | 400 | 518.5 | 438.4 | 478.1 | 442.2 | 628.2 | 493.3
2305.1 | 2066.1 | -6.8 | 0 | 0 | 504.4 | 578.4 | 421.5 | 412.6 | 577.3 | 85.8 | 15.7 | 137.3 | 5.8 | 221.5 | 12.7 | 519.4 | 696.2 | 566.3 | 582 | 747 | 716.5 | 736.8 | 646.8 | 537.8 | 478.2 | 693.4 | 676.7 | 302.2 | 405.2 | 457.6 | 683.6 | 592 | 578.3 | 662.8 | 631.8 | 399.5 | 517.7 | 437.3 | 478.1 | 441.8 | 628.1 | 493.5
2306.1 | 2067.1 | -6.7 | 0 | 0 | 504.6 | 583.9 | 421.3 | 411.6 | 576.3 | 85.7 | 15.7 | 136.8 | 4.9 | 205.2 | 12.6 | 519.4 | 696.7 | 562.9 | 582.1 | 746.5 | 713.3 | 735.6 | 645.5 | 533.9 | 478.9 | 692.9 | 674.2 | 302 | 405.4 | 457.6 | 683 | 591.6 | 576.7 | 661.9 | 629.8 | 399 | 517.2 | 436.1 | 477.8 | 441.2 | 628 | 493.6
2307.1 | 2068.1 | -6.8 | 0 | 0 | 504 | 583.3 | 421.4 | 410.7 | 575.2 | 85.6 | 15.7 | 136.5 | 5 | 212.6 | 12.9 | 519.5 | 695.4 | 559.6 | 582 | 746.1 | 710.4 | 734.5 | 643.9 | 530.2 | 479.3 | 692.4 | 671.8 | 302.1 | 405.5 | 457.5 | 682.3 | 590.9 | 574.1 | 661 | 627.4 | 398.5 | 516.7 | 434.9 | 477.1 | 440.7 | 627.9 | 493.7
2308.1 | 2069.1 | -6.8 | 0 | 0 | 503.3 | 584 | 421.3 | 410.1 | 573.4 | 85.5 | 15.7 | 136.2 | 5.2 | 208.2 | 11 | 519.5 | 694.3 | 556.9 | 582 | 745.5 | 707.4 | 733.6 | 642.9 | 527 | 479.8 | 691.9 | 669.6 | 302.1 | 405.5 | 457.3 | 681.7 | 589.6 | 573.7 | 660.3 | 625.3 | 398 | 516.9 | 433.6 | 476.8 | 440.2 | 627.9 | 493.8
2309.1 | 2070.1 | -6.8 | 0 | 0 | 503 | 586.8 | 421.1 | 409.2 | 573 | 85.4 | 15.7 | 135.8 | 5.3 | 204.9 | 11.1 | 519.6 | 692.8 | 554.5 | 581.9 | 745.1 | 704 | 732.6 | 642.2 | 524.2 | 480.2 | 691.4 | 666.7 | 302.2 | 405.4 | 457.3 | 681 | 589.1 | 573.1 | 659.5 | 623.8 | 397.5 | 516.2 | 432.5 | 476.6 | 439.7 | 627.9 | 493.9
2310.1 | 2071.1 | -6.8 | 0 | 0 | 503.9 | 585.1 | 420.5 | 408.6 | 572.5 | 85.3 | 15.7 | 135.5 | 5.8 | 216.9 | 12.7 | 519.6 | 691.4 | 552.1 | 581.8 | 744.7 | 700.7 | 731.5 | 641.7 | 521.9 | 479.4 | 690.9 | 664 | 302.2 | 405.4 | 457.3 | 680.2 | 587.8 | 571.7 | 658.7 | 622.9 | 397 | 515.4 | 431.6 | 476 | 439.3 | 627.7 | 494
2311.1 | 2072.1 | -6.8 | 0 | 0 | 504.4 | 580.7 | 420.3 | 408 | 571.6 | 85.1 | 15.7 | 135.3 | 6.1 | 211 | 14.1 | 519.7 | 690.5 | 549.9 | 581.6 | 744.3 | 697.6 | 730.4 | 641.1 | 521.3 | 479.3 | 690.3 | 661.8 | 302.4 | 405.5 | 457 | 679.4 | 586.4 | 569.7 | 658.2 | 621.2 | 396.5 | 515.1 | 430.8 | 475.5 | 438.9 | 627.5 | 494
2312.1 | 2073.1 | -6.7 | 0 | 0 | 505.5 | 580.8 | 419.9 | 407.8 | 570 | 85 | 15.7 | 135.2 | 6.2 | 213.3 | 13.7 | 519.7 | 690 | 548.1 | 581.4 | 743.9 | 694.4 | 729.2 | 640.2 | 519.8 | 479.8 | 689.7 | 659.8 | 302.4 | 405.6 | 456.9 | 678.6 | 585.5 | 568.7 | 657.8 | 619.9 | 396 | 514.2 | 430.3 | 475 | 438.4 | 627.3 | 494.1
2313.1 | 2074.1 | -6.8 | 0 | 0 | 505.3 | 586.3 | 419.6 | 407.2 | 569.3 | 84.8 | 15.7 | 135 | 6.3 | 215.5 | 11.8 | 519.7 | 690 | 546.3 | 581.1 | 743.6 | 691.1 | 727.8 | 639.7 | 519.1 | 480.6 | 689.1 | 658.5 | 302.4 | 405.6 | 456.8 | 678 | 584.9 | 567 | 657.4 | 619 | 395.5 | 513.3 | 429.7 | 474.6 | 438 | 627.1 | 494.2
2314.1 | 2075.1 | -6.7 | 0 | 0 | 505.9 | 584.5 | 420 | 406.1 | 568.5 | 84.6 | 15.7 | 134.7 | 6.4 | 234.6 | 9.6 | 519.8 | 689.7 | 544.4 | 580.9 | 743.1 | 687.5 | 726.8 | 639.7 | 517.8 | 480.8 | 688.5 | 656.9 | 302.5 | 405.6 | 456.6 | 677.4 | 584.2 | 565.1 | 657.1 | 618.5 | 395.1 | 512.4 | 428.9 | 473.8 | 437.6 | 627 | 494.2
2315.1 | 2076.1 | -6.8 | 0 | 0 | 506.1 | 585 | 419.9 | 405.7 | 566.7 | 84.4 | 15.7 | 134.4 | 5.9 | 223.7 | 8.9 | 519.8 | 689.6 | 543 | 580.7 | 742.6 | 684 | 725.5 | 639.8 | 518.8 | 481 | 687.9 | 655.1 | 302.5 | 405.7 | 456.5 | 676.7 | 582.8 | 562.6 | 656.7 | 617.1 | 394.6 | 511.9 | 428.1 | 473.4 | 437.2 | 626.9 | 494.3
2316.1 | 2077.1 | -6.7 | 0 | 0 | 505.5 | 581.8 | 419.2 | 405 | 565.7 | 84.3 | 15.7 | 134.2 | 5.6 | 200.7 | 10.4 | 519.9 | 691.1 | 540.8 | 580.5 | 742.1 | 680.6 | 724.5 | 640.7 | 517.9 | 481.4 | 687.3 | 653.3 | 302.4 | 405.8 | 456.4 | 675.8 | 581.5 | 560.9 | 656 | 616.3 | 394.2 | 511 | 427.8 | 472.7 | 436.7 | 626.9 | 494.3
2317.1 | 2078.1 | -6.8 | 0 | 0 | 503.4 | 577.2 | 418.5 | 404.3 | 564.4 | 84.1 | 15.7 | 134.1 | 6 | 186.5 | 11.1 | 519.9 | 690.9 | 538.7 | 580.3 | 741.6 | 677.2 | 724 | 641.3 | 515.9 | 481.5 | 686.7 | 651 | 302.5 | 405.9 | 456.2 | 675 | 579.9 | 559.3 | 655.4 | 614.8 | 393.8 | 509.8 | 427.5 | 472.1 | 436.3 | 626.7 | 494.4
2318.1 | 2079.1 | -6.7 | 0 | 0 | 501.9 | 571.5 | 418.3 | 404.1 | 562.1 | 83.9 | 15.7 | 133.7 | 6 | 197 | 9.2 | 520 | 691.4 | 535.8 | 580.2 | 741.1 | 673.9 | 723 | 640.9 | 516.3 | 481.4 | 686.2 | 649.9 | 302.5 | 406 | 456.1 | 674.2 | 578.1 | 557.7 | 654.9 | 613.2 | 393.4 | 508.2 | 427.1 | 471.6 | 435.9 | 626.6 | 494.4
2319.1 | 2080.1 | -6.7 | 0 | 0 | 500.5 | 568.4 | 418.5 | 403.8 | 560.2 | 83.8 | 15.7 | 133.3 | 4.9 | 208.6 | 9.6 | 520 | 691.1 | 533.3 | 580.1 | 740.7 | 670.5 | 722 | 640 | 514.6 | 480.9 | 685.6 | 648.7 | 302.4 | 406.2 | 455.9 | 673.7 | 577.1 | 557 | 654.8 | 612.2 | 393 | 506.7 | 426.8 | 471.2 | 435.4 | 626.5 | 494.5
2320.1 | 2081.1 | -6.7 | 0 | 0 | 499.3 | 567.2 | 417.9 | 402.8 | 560.4 | 83.6 | 15.7 | 132.9 | 5.4 | 190.9 | 9.9 | 520.1 | 691.5 | 531.2 | 579.9 | 740.1 | 667 | 721 | 638.5 | 515.2 | 480.7 | 685.1 | 647.7 | 302.5 | 406.4 | 455.8 | 673.1 | 576.3 | 556 | 654.3 | 611.3 | 392.6 | 505.4 | 426.4 | 471 | 435 | 626.3 | 494.5
2321.1 | 2082.1 | -6.7 | 0 | 0 | 498.3 | 570.6 | 417.5 | 401.9 | 559.9 | 83.4 | 15.7 | 132.6 | 6 | 199.8 | 11.2 | 520.1 | 692 | 529.2 | 579.7 | 739.7 | 663.7 | 720.4 | 637.3 | 517.7 | 480.5 | 684.4 | 646.3 | 302.3 | 406.5 | 455.6 | 672.5 | 575.2 | 555.5 | 653.7 | 610 | 392.2 | 504.4 | 425.9 | 470.9 | 434.5 | 626 | 494.6
2322.1 | 2083.1 | -6.7 | 0 | 0 | 497.8 | 572.4 | 418.1 | 401.9 | 559.3 | 83.2 | 15.7 | 132.3 | 5.5 | 192.9 | 10.1 | 520.2 | 692 | 527.4 | 579.6 | 739.2 | 660.7 | 719.6 | 636.9 | 519 | 481 | 683.7 | 645 | 302.4 | 406.6 | 455.5 | 671.8 | 574.3 | 554.6 | 653.6 | 608.4 | 391.8 | 503.4 | 425.5 | 470.7 | 434.1 | 625.8 | 494.6
2323.1 | 2084.1 | -6.7 | 0 | 0 | 497.4 | 569.3 | 417.9 | 402.1 | 557.8 | 83 | 15.7 | 131.8 | 4.6 | 197 | 9.8 | 520.3 | 693.2 | 525.5 | 579.5 | 738.8 | 657.7 | 718.9 | 636.6 | 520.7 | 481.8 | 682.9 | 643.7 | 302.5 | 406.7 | 455.4 | 671.4 | 572.7 | 553.7 | 653.6 | 607.5 | 391.4 | 502.4 | 425 | 470.4 | 433.7 | 625.6 | 494.7
2324.1 | 2085.1 | -6.7 | 0 | 0 | 497.2 | 568.5 | 417.1 | 402.6 | 556.2 | 82.8 | 15.7 | 131.3 | 4.6 | 193.2 | 9.5 | 520.3 | 693.1 | 523.7 | 579.3 | 738.3 | 654.9 | 718.1 | 636.3 | 521.9 | 482.3 | 682.3 | 642.3 | 302.5 | 406.8 | 455.2 | 670.9 | 571.1 | 552.2 | 653.2 | 606.4 | 391.1 | 501.3 | 424.4 | 470.4 | 433.3 | 625.4 | 494.7
2325.1 | 2086.1 | -6.7 | 0 | 0 | 497.6 | 569.7 | 417 | 403 | 554.9 | 82.6 | 15.7 | 130.9 | 5 | 193.5 | 8 | 520.4 | 692.4 | 522.2 | 579.2 | 737.8 | 652.7 | 717.2 | 636.1 | 522 | 482.3 | 681.5 | 641 | 302.6 | 406.9 | 455 | 670.5 | 569.7 | 552.1 | 653.2 | 606 | 390.8 | 500.2 | 423.7 | 470 | 432.9 | 625.2 | 494.8
2326.1 | 2087.1 | -6.7 | 0 | 0 | 498.3 | 567.5 | 416.5 | 402.4 | 553.4 | 82.5 | 15.7 | 130.4 | 4.9 | 222 | 6.6 | 520.5 | 692.2 | 520.4 | 578.9 | 737.2 | 650.8 | 716.3 | 635.8 | 520.1 | 482.4 | 680.8 | 639.3 | 302.7 | 407 | 454.9 | 669.3 | 568.7 | 551.3 | 655 | 604.7 | 390.4 | 499.1 | 423 | 469.7 | 432.4 | 625.1 | 494.8
2327.1 | 2088.1 | -6.7 | 0 | 0 | 498.7 | 564.4 | 415.9 | 401.8 | 548.5 | 82.3 | 15.7 | 130 | 5.1 | 180 | 5.9 | 520.6 | 691.1 | 518.6 | 578.6 | 736.7 | 649.4 | 715.3 | 634.8 | 519.4 | 482.7 | 680.2 | 637 | 302.7 | 407.1 | 454.8 | 664.2 | 566.5 | 551.8 | 657.9 | 603.5 | 390.1 | 497.8 | 422.5 | 469.5 | 432 | 624.9 | 494.9
2328.1 | 2089.1 | -6.7 | 0 | 0 | 501.4 | 561 | 415.3 | 401.7 | 542.6 | 82.1 | 15.7 | 129.5 | 4.8 | 210.4 | 7.9 | 520.6 | 690.6 | 516.7 | 578.3 | 736.3 | 648.2 | 714.8 | 632.1 | 522.3 | 483.1 | 679.7 | 636 | 302.6 | 407.1 | 454.6 | 657.4 | 563.7 | 551.1 | 662.8 | 602.3 | 389.8 | 496.5 | 422 | 469.3 | 431.6 | 624.7 | 494.9
2329.1 | 2090.1 | -6.7 | 0 | 0 | 502.6 | 567.4 | 414.3 | 401.2 | 538.3 | 81.9 | 15.7 | 129 | 5.1 | 203.5 | 9.7 | 520.7 | 690.2 | 515.1 | 578.1 | 735.8 | 647.1 | 714 | 629.7 | 521.7 | 483.6 | 679.1 | 634.5 | 302.5 | 407.3 | 454.4 | 656.7 | 562.1 | 551 | 667.7 | 600.2 | 389.5 | 495.7 | 421.6 | 469.3 | 431.2 | 624.3 | 494.9
2330.1 | 2091.1 | -6.7 | 0 | 0 | 502.8 | 578 | 412.8 | 400.6 | 533.4 | 81.7 | 15.7 | 128.6 | 5 | 186 | 10.7 | 520.8 | 689.1 | 513.9 | 577.9 | 735.4 | 645.7 | 712.9 | 627.8 | 521.6 | 484.7 | 678.8 | 633.4 | 302.8 | 407.2 | 454.3 | 651.1 | 559.5 | 549.8 | 669.7 | 598.4 | 389.2 | 494.8 | 421.2 | 469 | 430.8 | 624 | 495
2331.1 | 2092.1 | -6.7 | 0 | 0 | 503.1 | 585.5 | 410.9 | 400.2 | 525.1 | 81.5 | 15.7 | 128.1 | 5 | 193.1 | 10.8 | 520.8 | 689.2 | 512.5 | 577.6 | 734.9 | 643.8 | 712.8 | 623.1 | 520.1 | 485.5 | 678.8 | 632.5 | 303.1 | 407.4 | 454.3 | 625.9 | 551 | 539.2 | 647.1 | 596.4 | 388.9 | 493.7 | 421.1 | 468.7 | 430.4 | 623.6 | 494.9
2332.1 | 2093.1 | -6.7 | 0 | 0 | 504.1 | 596.2 | 409.8 | 399.8 | 502.6 | 81.3 | 15.7 | 127.8 | 5 | 202.1 | 10 | 520.9 | 689.3 | 510.8 | 577.3 | 734.5 | 641.6 | 712.3 | 615.3 | 520.2 | 486.3 | 678.8 | 631.1 | 303.2 | 407.2 | 454 | 586.9 | 529.8 | 523.7 | 619.6 | 593.1 | 388.6 | 492.8 | 421 | 468.3 | 430 | 623.2 | 495
2333.1 | 2094.1 | -6.7 | 0 | 0 | 502 | 601.9 | 408.6 | 399.3 | 496.1 | 81.1 | 15.7 | 127.5 | 5.1 | 217.4 | 9.5 | 521 | 688.4 | 509.4 | 577 | 733.9 | 639.2 | 711.1 | 612.3 | 519.2 | 487.2 | 678.2 | 629.4 | 303.1 | 407.1 | 453.7 | 599.3 | 524.9 | 521.2 | 622.4 | 590.9 | 388.3 | 491.5 | 420.8 | 467.6 | 429.6 | 622.8 | 495
2334.1 | 2095.1 | -6.7 | 0 | 0 | 500.4 | 604.7 | 407.2 | 398.6 | 482.6 | 80.9 | 15.7 | 127.1 | 5.2 | 212.9 | 10.7 | 521 | 687.5 | 508.3 | 576.7 | 733.4 | 636.7 | 710.4 | 608.6 | 517.6 | 487.6 | 677.6 | 627.5 | 304.6 | 407 | 453.4 | 602.7 | 510 | 511.5 | 605.2 | 589.3 | 388 | 490.1 | 420.3 | 466.7 | 429.3 | 622.3 | 494.9
2335.1 | 2096.1 | -6.7 | 0 | 0 | 498.6 | 599.4 | 405.6 | 397.6 | 444.3 | 80.7 | 15.7 | 126.9 | 5.3 | 208.3 | 10.2 | 521.1 | 686 | 507.2 | 576.5 | 732.9 | 634.1 | 709.5 | 601.1 | 515.2 | 488 | 676.6 | 626 | 307.8 | 407.1 | 453 | 599.6 | 481.2 | 497.2 | 577.1 | 586.2 | 387.8 | 488.3 | 419.7 | 466.1 | 429 | 621.8 | 494.8
2336.1 | 2097.1 | -6.7 | 0 | 0 | 496.7 | 604.2 | 403.8 | 396.4 | 419.3 | 80.6 | 15.7 | 126.7 | 5.6 | 204.9 | 10 | 521.1 | 686.1 | 505.6 | 576.2 | 732.3 | 631.5 | 708.1 | 593.8 | 513.6 | 487.9 | 674.6 | 624.2 | 308.6 | 406.9 | 452.7 | 578.4 | 452.5 | 484.6 | 555.9 | 582.7 | 387.5 | 486.9 | 419.4 | 465.4 | 428.6 | 621.3 | 494.8
2337.1 | 2098.1 | -6.7 | 0 | 0 | 494.2 | 608 | 401.6 | 394.9 | 410.7 | 80.5 | 15.7 | 126.5 | 5.5 | 200.1 | 11 | 521.2 | 685.4 | 504.4 | 576 | 731.7 | 628.6 | 706.6 | 584.2 | 512.6 | 488.1 | 671.7 | 622.6 | 307.2 | 406.6 | 452.4 | 550.4 | 435.2 | 479 | 547.6 | 579 | 387.1 | 485.3 | 418.8 | 464.8 | 428.2 | 620.7 | 494.7
2338.1 | 2099.1 | -6.7 | 0 | 0 | 491.5 | 610 | 399.3 | 393.1 | 400.1 | 80.4 | 15.7 | 126.4 | 5.6 | 202.5 | 11.7 | 521.3 | 683.9 | 503.3 | 575.9 | 731.2 | 625.8 | 704.8 | 572.6 | 510.1 | 489.1 | 669.2 | 620.9 | 306.5 | 406.3 | 452.1 | 558.7 | 421.8 | 473.4 | 536.5 | 575.1 | 386.8 | 483.7 | 417.9 | 464.2 | 427.7 | 620.1 | 494.6
2339.1 | 2100.1 | -6.7 | 0 | 0 | 489.8 | 604.6 | 397 | 391.7 | 389.6 | 80.3 | 15.7 | 126.4 | 5 | 205.8 | 11.2 | 521.3 | 683.4 | 501.7 | 575.8 | 730.8 | 622.7 | 702.8 | 563.7 | 505.5 | 489.9 | 665.2 | 619.2 | 306.3 | 406 | 451.6 | 566.7 | 412.6 | 469 | 527.8 | 570.1 | 386.5 | 482.3 | 416.9 | 463.8 | 427.2 | 619.6 | 494.5
2340.1 | 2101.1 | -6.7 | 0 | 0 | 488.4 | 590.3 | 395.8 | 390.5 | 379.4 | 80.2 | 15.7 | 126.3 | 4.7 | 213.9 | 9.8 | 521.4 | 681.8 | 500.2 | 575.5 | 730.2 | 620 | 700.2 | 555.3 | 503.3 | 490.6 | 661.2 | 618 | 305.1 | 405.7 | 451.3 | 572.7 | 405.5 | 464.4 | 520.6 | 565.3 | 386.2 | 481.4 | 416 | 463.5 | 426.8 | 619 | 494.5
2341.1 | 2102.1 | -6.7 | 0 | 0 | 487.1 | 581.6 | 394.8 | 389.5 | 369.1 | 80.2 | 15.7 | 126.1 | 5.6 | 205.1 | 10.5 | 521.4 | 680 | 499 | 575.1 | 729.7 | 617.4 | 696.9 | 545.2 | 503 | 490.8 | 658.4 | 616.9 | 303.4 | 405.4 | 451.1 | 578.4 | 403.5 | 456.2 | 511.8 | 560.1 | 385.8 | 480.4 | 415.2 | 463 | 426.3 | 618.5 | 494.4
2342.1 | 2103.1 | -6.7 | 0 | 0 | 486.2 | 583.5 | 393.4 | 388.5 | 358.5 | 80.1 | 15.7 | 126 | 5.5 | 221 | 9.9 | 521.5 | 679.8 | 497.8 | 574.8 | 729.1 | 615 | 693.9 | 536.2 | 501.6 | 490.9 | 656.2 | 615.2 | 303 | 405.3 | 450.8 | 580.2 | 402.6 | 448.2 | 506.7 | 549.5 | 385.5 | 479.3 | 414.3 | 462.7 | 425.9 | 617.9 | 494.4
2343.1 | 2104.1 | -6.7 | 0 | 0 | 485.6 | 586.2 | 391.6 | 387.5 | 350.1 | 80 | 15.7 | 125.9 | 5.1 | 234.8 | 8 | 521.5 | 678.1 | 496.6 | 574.4 | 728.6 | 612.5 | 690.9 | 518.3 | 500.8 | 490.7 | 653.2 | 613.3 | 303.2 | 405.1 | 450.5 | 580.3 | 403.3 | 440.5 | 502.1 | 529.9 | 385.2 | 478 | 413.3 | 462.3 | 425.4 | 617.2 | 494.3
2344.1 | 2105.1 | -6.7 | 0 | 0 | 485.8 | 582.1 | 389.6 | 386.4 | 345.7 | 79.8 | 15.7 | 125.7 | 5.3 | 240.3 | 6.9 | 521.6 | 677.2 | 495.1 | 574.1 | 728 | 609.8 | 687.1 | 499.5 | 500 | 491.1 | 646.4 | 611.7 | 303.1 | 404.9 | 450.2 | 578.7 | 403.6 | 433.4 | 497.9 | 501 | 384.8 | 476.9 | 412.6 | 462.1 | 425.1 | 616.6 | 494.2
2345.1 | 2106.1 | -6.7 | 0 | 0 | 485.5 | 575.5 | 387.6 | 384.9 | 341.3 | 79.6 | 15.7 | 125.4 | 5.1 | 228.7 | 6.2 | 521.6 | 676.1 | 493.5 | 573.8 | 727.3 | 607.3 | 683.6 | 483.3 | 497.8 | 490.9 | 635.9 | 609.8 | 303.2 | 404.7 | 449.9 | 575.3 | 401.2 | 424.5 | 493 | 469 | 384.5 | 475.6 | 411.7 | 461.8 | 424.7 | 615.9 | 494.1
2346.1 | 2107.1 | -6.7 | 0 | 0 | 484.7 | 584.7 | 385.6 | 383.3 | 336.1 | 79.4 | 15.7 | 125.2 | 5.1 | 212.9 | 8.2 | 521.7 | 674.6 | 492.1 | 573.4 | 726.1 | 604.8 | 680.2 | 467.2 | 495.9 | 491.1 | 628.3 | 607.8 | 303.3 | 404.6 | 449.6 | 570.5 | 399.8 | 417.8 | 487.6 | 436.9 | 384.1 | 474.7 | 410.9 | 461.5 | 424.3 | 615.3 | 494
2347.1 | 2108.1 | -6.7 | 0 | 0 | 484.8 | 586 | 383.8 | 381.9 | 333 | 79.3 | 15.7 | 125 | 5.6 | 206.2 | 10.1 | 521.8 | 673.9 | 490.8 | 573 | 725.1 | 602.1 | 676.9 | 453.9 | 493.2 | 490.7 | 619.8 | 605.9 | 303.2 | 404.4 | 449.4 | 565.4 | 397.6 | 411.2 | 480.4 | 402.7 | 383.8 | 473.3 | 410.2 | 461.2 | 423.9 | 614.6 | 493.9
2348.1 | 2109.1 | -6.7 | 0 | 0 | 484.5 | 584.5 | 382.2 | 380.8 | 329.5 | 79.1 | 15.7 | 124.8 | 5.2 | 218 | 10.2 | 521.9 | 673.1 | 489.5 | 572.5 | 719.4 | 599.2 | 673.4 | 443.6 | 489.9 | 490.5 | 611 | 603.5 | 303 | 404.1 | 449.1 | 559.2 | 395.1 | 404.4 | 471.9 | 286.3 | 383.4 | 471.9 | 409.5 | 460.9 | 423.5 | 614 | 493.7
2349.1 | 2110.1 | -6.7 | 0 | 0 | 484.1 | 585 | 380.8 | 380.1 | 330.5 | 78.9 | 15.7 | 124.6 | 4.7 | 249 | 8.9 | 522 | 672 | 488.2 | 572 | 716.1 | 596.6 | 670 | 431.4 | 485.4 | 489.6 | 601.1 | 601.3 | 302.9 | 403.8 | 448.8 | 551.2 | 393.4 | 397.8 | 460.1 | 107.5 | 383.1 | 470.7 | 408.9 | 460.6 | 423.1 | 613.2 | 493.6
2350.1 | 2111.1 | -6.7 | 0 | 0 | 483.3 | 596.5 | 379.6 | 379.3 | 333 | 78.7 | 15.7 | 124.2 | 5 | 228.4 | 7.9 | 522.1 | 670.6 | 487.1 | 571.5 | 712.3 | 594 | 666.2 | 422.1 | 482.7 | 488 | 591.2 | 598.7 | 303.1 | 403.7 | 448.5 | 538.6 | 391.5 | 391.9 | 441.5 | 96.5 | 382.8 | 469.8 | 408.4 | 460.4 | 422.7 | 612.5 | 493.4
2351.1 | 2112.1 | -6.7 | 0 | 0 | 482.4 | 605.2 | 378.6 | 378.3 | 334 | 78.6 | 15.7 | 123.9 | 4.8 | 214.9 | 8.2 | 522.1 | 668.1 | 486 | 571.1 | 703.2 | 591.5 | 662.9 | 414.9 | 478.6 | 485.9 | 580.7 | 596.6 | 303 | 403.3 | 448.2 | 488.8 | 390.5 | 387.5 | 413 | 96.2 | 382.5 | 468.7 | 407.6 | 460.1 | 422.3 | 611.9 | 493.2
2352.1 | 2113.1 | -6.7 | 0 | 0 | 481.1 | 600 | 377.4 | 377.3 | 335.6 | 78.6 | 15.7 | 123.6 | 5.4 | 237 | 9 | 522.1 | 666.5 | 484.8 | 570.7 | 692.4 | 589.1 | 659.6 | 403.8 | 476.4 | 482.6 | 569.6 | 594.5 | 303 | 403.3 | 448 | 175 | 389.4 | 382 | 392 | 96.1 | 382.3 | 467.5 | 406.5 | 459.8 | 421.9 | 611.2 | 493.1
2353.1 | 2114.1 | -6.7 | 0 | 0 | 480.1 | 593.9 | 376.3 | 376.3 | 337.4 | 78.5 | 15.7 | 123.6 | 6 | 235.5 | 10.7 | 522.2 | 665.7 | 483.4 | 570.3 | 684.8 | 586.5 | 656.6 | 398.2 | 473.8 | 477.9 | 558.8 | 592.5 | 303.3 | 403 | 447.7 | 125.5 | 388.4 | 375 | 374.4 | 94.7 | 382 | 466.1 | 405.4 | 459.4 | 421.5 | 610.6 | 493
2354.1 | 2115.1 | -6.7 | 0 | 0 | 479.2 | 593.8 | 375.4 | 375.3 | 338 | 78.4 | 15.7 | 123.6 | 5.3 | 236.5 | 12.8 | 522.3 | 664.9 | 481.8 | 569.9 | 680.6 | 584.2 | 653.8 | 389.3 | 470.4 | 475.3 | 547.6 | 590.8 | 303.1 | 402.5 | 447.4 | 124 | 387.5 | 367 | 361.2 | 93.6 | 381.7 | 464.8 | 404.5 | 459 | 421.1 | 609.9 | 492.8
2355.1 | 2116.1 | -6.7 | 0 | 0 | 477.8 | 590 | 374.3 | 374.4 | 337.6 | 78.3 | 15.7 | 123.4 | 5.1 | 220.7 | 12.9 | 522.3 | 664.2 | 480.4 | 569.6 | 678.2 | 581.6 | 651.2 | 382 | 469.1 | 472.1 | 534.4 | 588.7 | 302.9 | 402.3 | 447.1 | 123.3 | 386.4 | 211.3 | 348.5 | 93.5 | 381.5 | 464.3 | 404 | 458.5 | 420.7 | 609.1 | 492.6
2356.1 | 2117.1 | -6.7 | 0 | 0 | 476.5 | 590.7 | 373.1 | 373.4 | 338 | 78.2 | 15.7 | 123.2 | 5.1 | 209.1 | 12.9 | 522.4 | 663 | 479 | 569.2 | 676.2 | 579.1 | 648.8 | 373.4 | 466.6 | 469 | 519.2 | 586.9 | 302.9 | 402.2 | 446.9 | 120.7 | 385.5 | 150.4 | 335.8 | 93 | 381.2 | 463.6 | 403.4 | 458 | 420.4 | 608.5 | 492.5
2357.1 | 2118.1 | -6.8 | 0 | 0 | 475.5 | 587.7 | 372 | 372.5 | 338.8 | 78 | 15.7 | 123 | 5.1 | 211.1 | 13.6 | 522.6 | 662.8 | 477.6 | 568.8 | 672.8 | 576.5 | 646.3 | 360.7 | 462.4 | 467.5 | 503.9 | 585 | 302.8 | 402.1 | 446.6 | 119.4 | 384.1 | 147.2 | 321.1 | 93 | 381 | 462.6 | 402.8 | 457.5 | 420 | 607.8 | 492.3
2358.1 | 2119.1 | -6.7 | 0 | 0 | 474.5 | 590.6 | 370.9 | 371.7 | 339.8 | 77.9 | 15.7 | 122.7 | 5.5 | 212.6 | 12.1 | 522.8 | 661.6 | 476.1 | 568.3 | 667.2 | 574.1 | 643.7 | 347.9 | 460 | 465.5 | 487.4 | 582.7 | 302.9 | 402 | 446.3 | 118.2 | 382.9 | 144.6 | 305.5 | 91.7 | 380.8 | 462.2 | 402.1 | 457.1 | 419.5 | 607.1 | 492.2
2359.1 | 2120.1 | -6.7 | 0 | 0 | 473.4 | 598.7 | 369.9 | 371 | 340.7 | 77.8 | 15.7 | 122.5 | 4.7 | 222.7 | 11.2 | 523.1 | 659.6 | 474.7 | 567.9 | 660.5 | 571.8 | 641 | 339.3 | 456.2 | 462.3 | 472.2 | 579.9 | 303 | 401.8 | 446 | 118.4 | 382.3 | 143.7 | 294.1 | 89.9 | 380.6 | 462 | 401.5 | 456.7 | 419.1 | 606.5 | 492
2360.1 | 2121.1 | -6.7 | 0 | 0 | 472.2 | 605.7 | 368.9 | 370.2 | 340.7 | 77.7 | 15.7 | 122.3 | 5 | 243.6 | 11 | 523.5 | 655 | 473.5 | 567.5 | 654.4 | 569.5 | 637.4 | 331.1 | 453.9 | 459.1 | 462 | 577.3 | 303.1 | 401.6 | 445.7 | 115.2 | 381.1 | 140.2 | 283.5 | 87.6 | 380.3 | 461.5 | 401.3 | 456.2 | 418.8 | 605.8 | 491.9
2361.1 | 2122.1 | -6.7 | 0 | 0 | 470.9 | 608.1 | 367.9 | 369.4 | 340.6 | 77.6 | 15.7 | 122 | 4.5 | 248.5 | 9.3 | 523.7 | 652.3 | 472.2 | 567.1 | 648.7 | 567.4 | 632.7 | 324.3 | 450.5 | 455.5 | 453.2 | 574.7 | 303.1 | 401.4 | 445.5 | 112.8 | 380.5 | 136.7 | 273 | 86.9 | 380.1 | 461 | 400.8 | 455.7 | 418.5 | 605.2 | 491.8
2362.1 | 2123.1 | -6.7 | 0 | 0 | 469.4 | 605.2 | 366.9 | 368.5 | 341.2 | 77.4 | 15.7 | 121.7 | 4.9 | 238.3 | 7.8 | 523.9 | 650.5 | 470.7 | 566.7 | 642.7 | 565.4 | 629 | 319 | 447 | 452.5 | 443.5 | 571.7 | 303.1 | 401.1 | 445.1 | 110.6 | 379.5 | 135.1 | 259.9 | 86.2 | 379.8 | 460.6 | 400.2 | 455.2 | 418.1 | 604.6 | 491.6
2363.1 | 2124.1 | -6.7 | 0 | 0 | 468.1 | 599.5 | 366 | 367.5 | 342.4 | 77.1 | 15.7 | 121.6 | 5 | 232.1 | 9.2 | 524 | 649.4 | 469.5 | 566.2 | 637.6 | 563.2 | 625.9 | 313.2 | 443.4 | 448.5 | 433.1 | 568.9 | 303.1 | 400.9 | 444.8 | 109.7 | 375.9 | 133.4 | 251.3 | 84.8 | 379.6 | 460.2 | 399.3 | 454.7 | 417.7 | 604 | 491.4
2364.1 | 2125.1 | -6.8 | 0 | 0 | 468.1 | 592.5 | 365.2 | 366.5 | 343.2 | 76.9 | 15.7 | 121.5 | 5 | 253.8 | 10.1 | 524 | 648.3 | 468.3 | 565.7 | 632.4 | 561 | 622.2 | 304.8 | 438.6 | 443 | 423 | 566.2 | 303.1 | 400.7 | 444.5 | 108.1 | 369.4 | 130.5 | 244.4 | 84.7 | 379.3 | 459.5 | 398.6 | 454.2 | 417.3 | 603.3 | 491.2
2365.1 | 2126.1 | -6.7 | 0 | 0 | 468 | 589.1 | 364.3 | 365.6 | 343.6 | 76.6 | 15.7 | 121.3 | 4.5 | 239.8 | 10.2 | 524 | 646.9 | 467.4 | 565.2 | 626.5 | 559 | 618.1 | 287 | 432.7 | 430.9 | 411.6 | 563.3 | 303.1 | 400.7 | 444.2 | 106.2 | 365.3 | 127.8 | 237.5 | 83.8 | 379 | 458.8 | 397.9 | 453.9 | 416.9 | 602.7 | 491.1
2366.1 | 2127.1 | -6.7 | 0 | 0 | 467 | 584 | 363.5 | 364.8 | 344.3 | 76.4 | 15.7 | 121 | 5.2 | 245.7 | 9.5 | 523.9 | 644.8 | 466.2 | 564.8 | 619.9 | 556.9 | 614 | 276.4 | 427.1 | 387.1 | 401.9 | 559.1 | 303.4 | 400.8 | 443.9 | 106 | 362.9 | 126 | 229.8 | 82.7 | 378.8 | 458.1 | 397.3 | 453.5 | 416.4 | 602.1 | 490.9
2367.1 | 2128.1 | -6.8 | 0 | 0 | 466.3 | 570.2 | 362.9 | 364 | 344.9 | 76.2 | 15.7 | 120.7 | 5.2 | 240.8 | 8 | 523.8 | 643.5 | 465.4 | 564.3 | 612.7 | 554.9 | 610.4 | 271.7 | 421.8 | 358.8 | 393.3 | 535.8 | 303.5 | 400.7 | 443.6 | 104.7 | 361.1 | 124.5 | 223.1 | 82.1 | 378.5 | 457.2 | 396.4 | 453.2 | 416 | 601.4 | 490.8
2368.1 | 2129.1 | -6.7 | 0 | 0 | 465.7 | 560.9 | 362.6 | 363.3 | 345.2 | 76.1 | 15.7 | 120.3 | 5.4 | 251.1 | 7.2 | 523.1 | 641.3 | 463.9 | 563.8 | 604.1 | 552.8 | 607 | 266.9 | 418.1 | 337.5 | 384.4 | 552.4 | 303.6 | 400.6 | 443.4 | 104.4 | 360.3 | 123.1 | 217.5 | 81.2 | 378.2 | 456.6 | 395.3 | 452.8 | 415.5 | 600.8 | 490.6
2369.1 | 2130.1 | -6.7 | 0 | 0 | 464 | 554 | 362.5 | 362.6 | 344.1 | 76 | 15.7 | 120.1 | 5.5 | 237.9 | 6.6 | 522.1 | 640.9 | 462.1 | 563.4 | 593.7 | 550.9 | 604.4 | 264.4 | 415.3 | 307.5 | 375.5 | 558.8 | 303.5 | 400.4 | 443.1 | 104.6 | 359.3 | 121.6 | 212 | 80.2 | 377.9 | 456 | 394.3 | 452.4 | 415 | 600.2 | 490.4
2370.1 | 2131.1 | -6.7 | 0 | 0 | 462.7 | 549.9 | 362.4 | 361.9 | 343.4 | 75.9 | 15.7 | 119.8 | 5.4 | 236.4 | 6.8 | 520.6 | 641 | 460.3 | 562.9 | 581.9 | 549.1 | 602 | 258.9 | 412.2 | 293.8 | 366.8 | 555.7 | 303.3 | 399.9 | 442.8 | 103.4 | 358.3 | 120.4 | 206.3 | 80 | 377.5 | 455.4 | 393.3 | 452.1 | 414.6 | 599.7 | 490.2
2371.1 | 2132.1 | -6.7 | 0 | 0 | 461.9 | 546.9 | 362 | 361.1 | 343.5 | 75.8 | 15.7 | 119.5 | 5.6 | 222 | 6.5 | 518.7 | 640 | 457.3 | 562.4 | 569 | 547.1 | 599.9 | 250.6 | 408.9 | 279.3 | 358.1 | 552.3 | 303.1 | 399.1 | 442.5 | 102.3 | 358 | 119.5 | 201.1 | 79.5 | 377.2 | 455.4 | 392.5 | 451.7 | 414.1 | 599.1 | 490
2372.1 | 2133.1 | -6.8 | 0 | 0 | 461.6 | 548.7 | 361.4 | 360.3 | 343.4 | 75.7 | 15.7 | 119.2 | 5.2 | 201.5 | 7.8 | 516.6 | 639.1 | 450.8 | 561.9 | 555.7 | 545.1 | 597.1 | 247.7 | 405.1 | 273.3 | 349.1 | 549.6 | 303.1 | 398.7 | 442.2 | 101.3 | 358.7 | 117.8 | 195.8 | 78.8 | 376.9 | 455.3 | 391.5 | 451.3 | 413.6 | 598.5 | 489.9
2373.1 | 2134.1 | -6.8 | 0 | 0 | 460.7 | 551.8 | 361.1 | 359.4 | 344 | 75.7 | 15.7 | 118.9 | 5.4 | 206.6 | 10.8 | 514 | 637.7 | 447 | 561.4 | 542 | 543 | 594.5 | 244.5 | 399.5 | 261.9 | 340.5 | 546.3 | 302.9 | 398.5 | 441.9 | 100 | 359.7 | 116.3 | 191.1 | 78.3 | 376.6 | 454.6 | 390.4 | 451.1 | 413.2 | 597.9 | 489.7
2374.1 | 2135.1 | -6.7 | 0 | 0 | 459.5 | 546.4 | 360.9 | 358.5 | 344.6 | 75.6 | 15.7 | 118.7 | 5.3 | 212.2 | 11.7 | 511 | 635.9 | 443.2 | 560.8 | 527.6 | 540.8 | 591.8 | 235.8 | 394.3 | 250.8 | 331.5 | 544 | 302.9 | 398.3 | 441.7 | 98.9 | 360.4 | 114.5 | 186.2 | 77.7 | 376.3 | 454 | 389.3 | 450.8 | 412.7 | 597.3 | 489.5
2375.1 | 2136.1 | -6.7 | 0 | 0 | 458.7 | 542.7 | 360.7 | 357.7 | 344.7 | 75.5 | 15.7 | 118.4 | 6.1 | 215.1 | 10.9 | 508.1 | 634.6 | 437.5 | 560.3 | 513 | 538.7 | 588 | 229.1 | 390.5 | 251.3 | 322.5 | 541.1 | 302.9 | 398.1 | 441.4 | 98.1 | 360.6 | 113 | 181.1 | 75.5 | 376 | 453.6 | 388.2 | 450.5 | 412.2 | 596.7 | 489.4
2376.1 | 2137.1 | -6.8 | 0 | 0 | 457.3 | 542.3 | 360.5 | 356.8 | 345 | 75.5 | 15.7 | 118.3 | 5.8 | 205.5 | 9.6 | 505.3 | 633.2 | 432.5 | 559.9 | 498.5 | 536.7 | 584.7 | 225.2 | 387.2 | 254.6 | 313.3 | 532.7 | 302.9 | 397.9 | 441.1 | 97.3 | 361.1 | 110.9 | 176.3 | 73.8 | 375.7 | 453.1 | 387.1 | 450 | 411.8 | 596.1 | 489.2
2377.1 | 2138.1 | -6.7 | 0 | 0 | 456.3 | 543 | 360.2 | 356.1 | 344.9 | 75.4 | 15.7 | 118 | 6.2 | 219.3 | 8.7 | 502.5 | 631.8 | 428 | 559.4 | 484.6 | 534.9 | 581.7 | 223.3 | 383.9 | 257.7 | 304.7 | 515.4 | 303.1 | 397.5 | 440.8 | 96.5 | 361.3 | 109.4 | 171 | 73 | 375.4 | 452.7 | 386 | 449.4 | 411.3 | 595.5 | 489
2378.1 | 2139.1 | -6.7 | 0 | 0 | 456.1 | 548.6 | 359.9 | 355.3 | 344.9 | 75.3 | 15.7 | 117.7 | 5.8 | 236.8 | 7 | 499.8 | 628.2 | 423.4 | 558.9 | 471.4 | 533 | 577.8 | 221 | 379.6 | 255.6 | 295.6 | 467.6 | 303 | 397.3 | 440.5 | 96.1 | 361.9 | 109 | 166.2 | 72.8 | 375.1 | 452.1 | 384.9 | 448.9 | 410.8 | 594.9 | 488.9
2379.1 | 2140.1 | -6.7 | 0 | 0 | 455.9 | 550.7 | 360 | 354.7 | 344.7 | 75.3 | 15.7 | 117.5 | 5.6 | 266.9 | 6.1 | 496.9 | 625.5 | 417.4 | 558.3 | 459 | 531 | 573.3 | 218.9 | 376.5 | 255 | 204.2 | 368.3 | 303 | 397.2 | 440.2 | 95.4 | 361.9 | 106.4 | 161.2 | 71.7 | 374.8 | 451.6 | 383.9 | 448.4 | 410.3 | 594.2 | 488.7
2380.1 | 2141.1 | -6.7 | 0 | 0 | 454.5 | 548.6 | 359.9 | 354.1 | 344.8 | 75.2 | 15.7 | 117.2 | 7.1 | 263.2 | 6.3 | 493.9 | 624.6 | 407.6 | 557.8 | 447.2 | 528.9 | 569.1 | 217.4 | 374.4 | 254.9 | 138 | 153.8 | 303.4 | 396.9 | 439.9 | 94.7 | 362 | 105 | 156.6 | 70.6 | 374.5 | 451.2 | 382.9 | 447.9 | 409.8 | 593.6 | 488.5
2381.1 | 2142.1 | -6.7 | 0 | 0 | 453.1 | 542.5 | 359.8 | 353.5 | 345.1 | 75.1 | 15.7 | 117 | 6.7 | 244.5 | 6.1 | 491.1 | 623.2 | 392.4 | 557.2 | 434.6 | 526.7 | 565.4 | 216.1 | 372.6 | 253.5 | 137.1 | 101.4 | 303.3 | 396.6 | 439.6 | 94.2 | 362.5 | 103.2 | 152.8 | 69 | 374.2 | 450.8 | 382 | 447.4 | 409.4 | 592.9 | 488.3
2382.1 | 2143.1 | -6.7 | 0 | 0 | 452.5 | 540.4 | 359.7 | 352.9 | 344.8 | 75.1 | 15.7 | 116.8 | 6.2 | 237.8 | 6.9 | 488.2 | 619.8 | 379.9 | 556.7 | 423.9 | 524.8 | 561.4 | 214.9 | 368.4 | 248.7 | 137.4 | 98.9 | 303.6 | 396.6 | 439.3 | 93.8 | 362.8 | 102.7 | 149.6 | 68.3 | 373.8 | 450.4 | 381.3 | 447 | 408.9 | 592.3 | 488.1
2383.1 | 2144.1 | -6.7 | 0 | 0 | 452 | 534.9 | 359.7 | 352.2 | 344.9 | 75 | 15.7 | 116.6 | 7 | 234.2 | 7.8 | 485.5 | 616.5 | 370.8 | 556.1 | 413.7 | 522.8 | 557.4 | 212.6 | 366.6 | 246.9 | 136.9 | 97.5 | 303.7 | 396 | 439 | 93 | 362.6 | 101.7 | 146.3 | 68.3 | 373.5 | 450 | 380.4 | 446.5 | 408.4 | 591.7 | 487.9
2384.1 | 2145.1 | -6.7 | 0 | 0 | 451.9 | 531.3 | 359.4 | 351.7 | 344.5 | 74.8 | 15.7 | 116.5 | 6.5 | 250.6 | 8.2 | 482.7 | 612.6 | 363.3 | 555.6 | 403.8 | 520.8 | 553.5 | 211.6 | 364.4 | 243.2 | 135.8 | 96.9 | 304.1 | 395.3 | 438.7 | 92.4 | 362.3 | 100.8 | 143.6 | 67.6 | 373.2 | 449.6 | 379.5 | 446.1 | 407.9 | 591.1 | 487.8
2385.1 | 2146.1 | -6.7 | 0 | 0 | 451.9 | 530.9 | 359.3 | 351.1 | 344.4 | 74.7 | 15.7 | 116.2 | 5.7 | 236.8 | 9.1 | 480 | 610.8 | 354.1 | 555 | 393.2 | 518.8 | 549.4 | 211 | 362 | 237.9 | 134.9 | 95.5 | 304.4 | 395.3 | 438.4 | 91.7 | 362.1 | 99.3 | 136.3 | 67.5 | 372.9 | 449.1 | 378.6 | 445.7 | 407.4 | 590.5 | 487.6
2386.1 | 2147.1 | -6.7 | 0 | 0 | 452 | 527.7 | 359 | 350.7 | 344.7 | 74.5 | 15.7 | 116 | 6 | 248.3 | 8.4 | 477.3 | 607.8 | 350 | 554.5 | 383 | 516.9 | 544.9 | 208.8 | 359.6 | 233.1 | 134.7 | 94.7 | 304.5 | 395.3 | 438.1 | 91.3 | 362.2 | 98.5 | 130.4 | 68.4 | 372.6 | 448.6 | 377.8 | 445.3 | 406.9 | 589.8 | 487.4
2387.1 | 2148.1 | -6.7 | 0 | 0 | 451.6 | 524.6 | 358.6 | 350.1 | 343.8 | 74.3 | 15.7 | 115.9 | 6.1 | 245 | 9 | 474.6 | 604.4 | 347.2 | 554 | 374.3 | 515.4 | 541.7 | 207.7 | 357.7 | 229.4 | 134.2 | 94.4 | 304.3 | 395.3 | 437.8 | 90.7 | 361.6 | 98.8 | 129.6 | 69.3 | 372.3 | 448.4 | 377.3 | 444.9 | 406.4 | 589.2 | 487.2
2388.1 | 2149.1 | -6.7 | 0 | 0 | 451.1 | 523.3 | 358.2 | 349.6 | 342.5 | 74.1 | 15.7 | 115.6 | 5.6 | 250.2 | 8.9 | 471.9 | 600.8 | 344.5 | 553.5 | 365.8 | 513.5 | 537.4 | 205.3 | 354.1 | 224.5 | 133.8 | 94.6 | 304.2 | 395.3 | 437.5 | 90.1 | 361.4 | 97.1 | 127.7 | 68.7 | 372 | 447.8 | 377 | 444.5 | 406 | 588.6 | 487.1
2389.1 | 2150.1 | -6.7 | 0 | 0 | 450.7 | 524.8 | 357.7 | 349.1 | 341.4 | 73.9 | 15.7 | 115.4 | 5.4 | 251.9 | 10 | 469.2 | 598.1 | 340.6 | 553 | 358 | 511.6 | 533.1 | 203.2 | 352.4 | 219.1 | 133.2 | 94.3 | 304.3 | 395.1 | 437.2 | 89.4 | 360.5 | 94 | 124.8 | 67.8 | 371.6 | 447 | 376.3 | 444.2 | 405.6 | 588 | 486.9
2390.1 | 2151.1 | -6.7 | 0 | 0 | 449.9 | 524.9 | 357.4 | 348.6 | 340.5 | 73.7 | 15.7 | 115.2 | 6 | 239.6 | 10.1 | 466.6 | 592.1 | 336.2 | 552.5 | 350.7 | 509.9 | 529.2 | 202.9 | 350.7 | 215.2 | 132.8 | 93.8 | 304.6 | 394.7 | 436.9 | 88.9 | 360 | 92.7 | 123.8 | 67.8 | 371.3 | 446.6 | 375.5 | 443.9 | 405.1 | 587.4 | 486.7
2391.1 | 2152.1 | -6.7 | 0 | 0 | 448.2 | 525.5 | 356.7 | 348.1 | 338.7 | 73.6 | 15.7 | 115 | 5.6 | 229.6 | 9.2 | 464.1 | 586.3 | 332.2 | 551.9 | 343.1 | 508.1 | 525.2 | 201.8 | 346.8 | 211.3 | 132.8 | 92.7 | 304.5 | 394.5 | 436.6 | 88.3 | 359.8 | 92.1 | 122.6 | 67.5 | 371 | 446.1 | 374.6 | 443.5 | 404.7 | 586.7 | 486.5
2392.1 | 2153.1 | -6.7 | 0 | 0 | 446 | 528.2 | 356 | 347.6 | 336.8 | 73.5 | 15.7 | 114.8 | 5.5 | 251.2 | 7.9 | 461.6 | 584.2 | 328.7 | 551.4 | 335.6 | 506.5 | 520.5 | 200.4 | 343.2 | 206.6 | 132.4 | 93.3 | 304.2 | 394.4 | 436.3 | 87.8 | 357.3 | 92 | 121.2 | 67.4 | 370.7 | 445.8 | 373.7 | 443.2 | 404.2 | 586.1 | 486.3
2393.1 | 2154.1 | -6.7 | 0 | 0 | 444.7 | 530.3 | 355.1 | 347.2 | 335.3 | 73.5 | 15.7 | 114.6 | 5.9 | 269.8 | 7.6 | 459.2 | 579.3 | 325.6 | 550.8 | 328.2 | 505 | 515.9 | 198.4 | 339.8 | 201.7 | 132.4 | 93.1 | 304.6 | 394.5 | 435.9 | 87.4 | 353.9 | 90.4 | 119.6 | 67.4 | 370.4 | 445.7 | 372.7 | 442.9 | 403.7 | 585.4 | 486.1
2394.1 | 2155.1 | -6.7 | 0 | 0 | 444.5 | 530.9 | 354.4 | 346.8 | 333.3 | 73.4 | 15.7 | 114.5 | 6.1 | 250.6 | 7.5 | 456.8 | 573.3 | 322 | 550.2 | 321.1 | 503.6 | 511.5 | 198 | 337 | 198.2 | 131.7 | 93.1 | 304.8 | 393.3 | 435.7 | 86.6 | 352.9 | 89.4 | 118.2 | 66.3 | 370.2 | 445.7 | 371.9 | 442.5 | 403.3 | 584.7 | 485.9
2395.1 | 2156.1 | -6.7 | 0 | 0 | 443.9 | 527.6 | 353.7 | 346.3 | 330.9 | 73.3 | 15.7 | 114.2 | 6.1 | 239.7 | 8.6 | 454.4 | 566.8 | 318.6 | 549.5 | 288 | 502 | 506.8 | 197 | 333.9 | 194.8 | 131.4 | 93 | 305.1 | 392.7 | 435.4 | 85.9 | 352.9 | 88.6 | 117 | 64.7 | 369.9 | 445.4 | 371.1 | 442.2 | 402.9 | 584.1 | 485.7
2396.1 | 2157.1 | -6.7 | 0 | 0 | 443.7 | 529.3 | 353.1 | 345.7 | 329.1 | 73.2 | 15.7 | 114 | 5.8 | 251.7 | 8.6 | 452 | 559.9 | 315.8 | 548.8 | 268.6 | 500.4 | 502.5 | 195.2 | 330.7 | 191.6 | 131.1 | 93.4 | 305.3 | 392.6 | 435.1 | 85.5 | 352.8 | 88.7 | 115.7 | 63.5 | 369.6 | 444.9 | 370.3 | 441.8 | 402.4 | 583.4 | 485.5
2397.1 | 2158.1 | -6.7 | 0 | 0 | 442.7 | 526.3 | 352.5 | 345.3 | 328.8 | 73.1 | 15.7 | 113.9 | 5.3 | 251.4 | 9 | 449.8 | 555.8 | 313 | 548.1 | 273.9 | 498.7 | 498.3 | 194.2 | 328 | 189.3 | 130.5 | 93.2 | 305.9 | 392.6 | 434.8 | 85.3 | 352.3 | 86.5 | 114.2 | 61.8 | 369.3 | 444.4 | 369.4 | 441.6 | 402 | 582.7 | 485.3
2398.1 | 2159.1 | -6.7 | 0 | 0 | 441.7 | 523.5 | 351.8 | 344.8 | 326.6 | 73 | 15.7 | 113.9 | 5.2 | 243.5 | 11.6 | 447.5 | 552.1 | 309.5 | 547.3 | 272.6 | 497 | 493.8 | 193.1 | 325.5 | 188.4 | 129.9 | 92.9 | 305.6 | 392.4 | 434.5 | 84.9 | 351.9 | 85.5 | 112.6 | 61.1 | 369 | 443.9 | 368.5 | 441.2 | 401.5 | 582 | 485.1
2399.1 | 2160.1 | -6.7 | 0 | 0 | 441.4 | 521.4 | 351.2 | 344.3 | 325.6 | 72.9 | 15.7 | 113.8 | 5.2 | 237.5 | 13.4 | 445.2 | 547.1 | 305.7 | 546.6 | 268.9 | 495.2 | 490.2 | 191.3 | 290.5 | 185.5 | 129.5 | 92.7 | 308.9 | 392.6 | 434.1 | 84.3 | 351.4 | 83.3 | 111.1 | 60.6 | 368.7 | 443.4 | 367.6 | 440.9 | 401.1 | 581.4 | 485
2400.1 | 2161.1 | -6.7 | 0 | 0 | 441.2 | 519.7 | 350.6 | 343.5 | 325 | 72.8 | 15.7 | 113.8 | 5.2 | 265.9 | 11.1 | 443 | 537.2 | 302.4 | 545.7 | 263.6 | 493.8 | 486 | 189.7 | 176.4 | 185.2 | 128.3 | 91.9 | 311.4 | 392.8 | 433.8 | 83.2 | 350.8 | 82.5 | 109.8 | 60.1 | 368.4 | 442.7 | 366.7 | 440.6 | 400.6 | 580.7 | 484.8
2401.1 | 2162.1 | -6.7 | 0 | 0 | 440.2 | 517.9 | 350.1 | 342.9 | 325.6 | 72.6 | 15.7 | 113.7 | 6.6 | 257.6 | 9.7 | 440.8 | 527.5 | 300.1 | 544.7 | 256.8 | 492.2 | 482 | 188 | 171.7 | 182.3 | 127.5 | 91.7 | 319.7 | 393.3 | 433.5 | 83.1 | 349.7 | 82.1 | 109 | 59.4 | 368.1 | 442.2 | 366 | 440.3 | 400.2 | 580 | 484.6
2402.1 | 2163.1 | -6.7 | 0 | 0 | 439.4 | 521.1 | 349.5 | 342.4 | 325.7 | 72.5 | 15.7 | 113.6 | 6 | 261.6 | 10.4 | 438.7 | 518.7 | 298 | 543.5 | 248.3 | 490.4 | 477.9 | 185.8 | 168.4 | 178.9 | 126.1 | 90.7 | 320.7 | 392.9 | 433.2 | 82.6 | 348.9 | 80.9 | 107.9 | 59.1 | 367.8 | 441.9 | 365.7 | 440 | 399.7 | 579.4 | 484.4
2403.1 | 2164.1 | -6.7 | 0 | 0 | 438.1 | 520.4 | 348.7 | 341.9 | 325.2 | 72.3 | 15.7 | 113.4 | 6 | 248.7 | 11.5 | 436.7 | 509 | 295.5 | 542.2 | 238.6 | 488.6 | 473.5 | 185 | 166.6 | 176.5 | 124.8 | 90.3 | 320.5 | 392.2 | 432.9 | 82.1 | 348.3 | 79.7 | 106.8 | 58.2 | 367.5 | 441.8 | 365.1 | 439.7 | 399.3 | 578.7 | 484.2
2404.1 | 2165.1 | -6.7 | 0 | 0 | 437.3 | 520 | 348.2 | 341.5 | 324.8 | 72.2 | 15.7 | 113.2 | 5.4 | 237.1 | 13 | 434.7 | 498.7 | 294.2 | 540.5 | 225.9 | 487.1 | 469.2 | 185.4 | 165 | 175.7 | 123.5 | 90 | 318.4 | 391.6 | 432.6 | 81.8 | 347.5 | 79.1 | 106.1 | 58.6 | 367.2 | 440.7 | 364.3 | 439.4 | 398.8 | 578.1 | 484
2405.1 | 2166.1 | -6.7 | 0 | 0 | 436.7 | 515.5 | 347.6 | 341.1 | 324.7 | 72 | 15.7 | 113.1 | 6.4 | 247.6 | 12.9 | 432.7 | 485.3 | 291.7 | 538.6 | 209.4 | 485.1 | 465.1 | 183.9 | 162.5 | 173.3 | 122.2 | 89.5 | 312.9 | 390.9 | 432.3 | 81.3 | 346.7 | 78.2 | 106 | 58.8 | 366.9 | 439.5 | 363.5 | 439.1 | 398.4 | 577.4 | 483.8
2406.1 | 2167.1 | -6.7 | 0 | 0 | 436.2 | 510.1 | 346.9 | 340.5 | 324.6 | 71.9 | 15.7 | 113 | 6.9 | 265.1 | 11.8 | 430.7 | 477.2 | 287.5 | 536.5 | 193.6 | 483.1 | 461.4 | 183.4 | 159.9 | 173.2 | 121 | 89.9 | 314.4 | 390.7 | 432 | 81 | 346.1 | 77.5 | 105.7 | 59 | 366.6 | 438.2 | 362.6 | 438.8 | 397.9 | 576.7 | 483.5
2407.1 | 2168.1 | -6.7 | 0 | 0 | 435.2 | 504.9 | 346.3 | 339.9 | 324.3 | 71.7 | 15.7 | 112.7 | 6.4 | 228.5 | 8.9 | 428.7 | 474.4 | 283.7 | 534.2 | 181.9 | 481.1 | 457 | 182 | 158 | 171.2 | 119.6 | 89.8 | 316.2 | 390.7 | 431.7 | 80.7 | 345.4 | 76.6 | 105.2 | 59.1 | 366.3 | 437.2 | 361.7 | 438.5 | 397.4 | 576.1 | 483.3
2408.1 | 2169.1 | -6.7 | 0 | 0 | 434.4 | 503.2 | 345.7 | 339.3 | 324.6 | 71.5 | 15.7 | 112.5 | 5.4 | 257.7 | 6.6 | 426 | 470.9 | 280.5 | 531.8 | 175.3 | 479.2 | 452.8 | 181.2 | 158.8 | 171.1 | 118.3 | 89.2 | 318.5 | 391 | 431.4 | 80.5 | 344.4 | 75.5 | 104.5 | 59.9 | 366 | 436.6 | 360.8 | 438.2 | 397 | 575.4 | 483.1
2409.1 | 2170.1 | -6.7 | 0 | 0 | 434.1 | 503.2 | 345 | 338.8 | 325.2 | 71.3 | 15.7 | 112.4 | 5.3 | 240.1 | 7.2 | 423.9 | 471.8 | 277.7 | 529.1 | 170.9 | 477.5 | 448.7 | 180.2 | 157.9 | 168.5 | 117.3 | 88.9 | 320 | 391.3 | 431.1 | 80 | 343.6 | 75.6 | 103.4 | 59.5 | 365.7 | 436.1 | 359.9 | 437.8 | 396.6 | 574.7 | 482.9
2410.1 | 2171.1 | -6.7 | 0 | 0 | 433.8 | 496.3 | 344.3 | 338.3 | 325.1 | 71.1 | 15.7 | 112.3 | 6.9 | 233.3 | 9.2 | 421.9 | 472.2 | 276.2 | 526.2 | 167.4 | 475.7 | 444.6 | 178.5 | 158.2 | 166.3 | 116.4 | 88.4 | 320.6 | 391 | 430.8 | 79.7 | 342.6 | 74.5 | 103.2 | 59.3 | 365.4 | 435.2 | 359 | 437.4 | 396.1 | 574 | 482.6
2411.1 | 2172.1 | -6.7 | 0 | 0 | 432.7 | 492 | 343.7 | 337.7 | 324.5 | 70.9 | 15.7 | 112.1 | 7.1 | 204.1 | 10.7 | 420 | 470.3 | 273.9 | 523 | 164.6 | 473.6 | 440.7 | 178.2 | 158.6 | 164.7 | 115.4 | 88.5 | 321.5 | 390.6 | 430.5 | 79.4 | 341.8 | 73 | 103.1 | 59.4 | 365.1 | 434.5 | 358.3 | 437.1 | 395.6 | 573.4 | 482.4
2412.1 | 2173.1 | -6.7 | 0 | 0 | 432.2 | 487 | 343.1 | 337 | 324.1 | 70.7 | 15.7 | 112 | 5 | 204.7 | 16.8 | 418 | 465.3 | 276.2 | 519.5 | 161.9 | 471.6 | 437.1 | 176.6 | 157.7 | 164 | 114.4 | 89.1 | 321.6 | 390.5 | 430.2 | 79.1 | 341.2 | 72.2 | 102.3 | 60.2 | 364.8 | 433.9 | 357.5 | 436.8 | 395.2 | 572.7 | 482.2
2413.1 | 2174.1 | -6.7 | 0 | 0 | 431.8 | 482.9 | 342.5 | 336.2 | 323.2 | 70.6 | 15.7 | 111.9 | 5.1 | 212.2 | 17.9 | 415.4 | 460.6 | 272.4 | 515.6 | 158.9 | 469.8 | 433.6 | 175.6 | 156.9 | 162.8 | 113.7 | 89 | 322 | 390.2 | 429.9 | 78.7 | 340.5 | 71.8 | 102.1 | 60.5 | 364.5 | 433.3 | 356.6 | 436.5 | 394.7 | 572.1 | 482
2414.1 | 2175.1 | -6.7 | 0 | 0 | 431 | 477.8 | 342 | 335.5 | 321.6 | 70.4 | 15.7 | 111.7 | 5.3 | 216.8 | 15.4 | 412.5 | 458.2 | 267.6 | 510.9 | 155.7 | 468.1 | 429.8 | 174.5 | 156.2 | 161.6 | 112.7 | 88.9 | 322.4 | 390 | 429.6 | 78.4 | 339.9 | 71 | 101.6 | 60.1 | 364.3 | 433 | 355.8 | 436.1 | 394.3 | 571.4 | 481.7
2415.1 | 2176.1 | -6.7 | 0 | 0 | 430.1 | 478.1 | 341.4 | 334.8 | 321.2 | 70.3 | 15.7 | 111.4 | 6 | 202.6 | 16.1 | 410.1 | 456 | 263.8 | 505.2 | 153.4 | 466.5 | 426 | 174.3 | 155.1 | 161.2 | 111.9 | 88.4 | 323.1 | 389.9 | 429.3 | 78.2 | 339 | 69.9 | 100.9 | 60.5 | 364 | 432.7 | 355 | 435.7 | 393.8 | 570.8 | 481.5
2416.1 | 2177.1 | -6.6 | 0 | 0 | 429.3 | 481 | 340.8 | 334.1 | 321.3 | 70.2 | 15.7 | 111 | 7.1 | 215.5 | 14.3 | 407.2 | 452.1 | 260 | 497.8 | 151 | 464.9 | 422.3 | 173.7 | 152.8 | 157.8 | 111.1 | 88.7 | 322.5 | 389.7 | 429 | 77.8 | 338.4 | 69 | 100.7 | 61 | 363.7 | 432.2 | 354.3 | 435.3 | 393.4 | 570.1 | 481.2
2417.1 | 2178.1 | -6.6 | 0 | 0 | 428.7 | 477.8 | 340.2 | 333.6 | 319.8 | 70.1 | 15.7 | 110.8 | 7.2 | 207.7 | 15.2 | 404.2 | 446.6 | 255.8 | 488.5 | 148.7 | 463.4 | 418.4 | 172.9 | 153.3 | 156 | 110.4 | 88.7 | 322.1 | 389.4 | 428.7 | 77.5 | 337.8 | 68.3 | 100.6 | 61.2 | 363.4 | 431.1 | 353.6 | 434.8 | 393 | 569.5 | 481
2418.1 | 2179.1 | -6.7 | 0 | 0 | 427.5 | 479.8 | 339.7 | 333.2 | 318.4 | 70 | 15.7 | 110.5 | 7.3 | 210.5 | 19.9 | 400.8 | 443.1 | 251.7 | 476.5 | 146.8 | 461.6 | 414.5 | 172.8 | 153.3 | 153.8 | 109.5 | 88.7 | 322.7 | 388.7 | 428.4 | 77.2 | 337.3 | 67.6 | 100.4 | 61.5 | 363.1 | 429.6 | 352.8 | 434.4 | 392.5 | 568.8 | 480.8
2419.1 | 2180.1 | -6.7 | 0 | 0 | 426.1 | 480.6 | 338.9 | 332.4 | 317.7 | 69.9 | 15.7 | 110.3 | 6.2 | 216.8 | 20.2 | 397.3 | 439.5 | 247.1 | 461.5 | 144.7 | 459.4 | 410.2 | 171.4 | 151.9 | 153.7 | 108.8 | 88.2 | 323.2 | 388.6 | 428.1 | 77.1 | 336.7 | 66.8 | 100.4 | 61.6 | 362.8 | 428.5 | 352.1 | 434.1 | 392.1 | 568.2 | 480.5
2420.1 | 2181.1 | -6.7 | 0 | 0 | 425.8 | 485.5 | 338.2 | 331.6 | 317.8 | 69.7 | 15.7 | 110.2 | 5.8 | 205.5 | 18.4 | 392.1 | 433.9 | 242.5 | 443.5 | 141.8 | 457.6 | 406.8 | 170.4 | 150.6 | 154.7 | 108.3 | 87.6 | 323.4 | 388.4 | 427.8 | 76.9 | 336 | 67.1 | 100.1 | 61 | 362.6 | 427.8 | 351.4 | 433.8 | 391.6 | 567.5 | 480.3
2421.1 | 2182.1 | -6.7 | 0 | 0 | 425.5 | 489 | 337.5 | 330.9 | 316.5 | 69.4 | 15.7 | 110 | 6 | 217.4 | 17 | 387.2 | 432.3 | 237.8 | 422.5 | 138.7 | 455.8 | 402.6 | 169.8 | 149.8 | 152.7 | 107.6 | 86.9 | 323.2 | 388.4 | 427.4 | 76.8 | 335.3 | 67.3 | 99.5 | 60.7 | 362.3 | 427.5 | 350.7 | 433.4 | 391.2 | 566.9 | 480
2422.1 | 2183.1 | -6.7 | 0 | 0 | 425.4 | 486 | 336.8 | 330.4 | 314.7 | 69.2 | 15.7 | 109.8 | 6.6 | 210.1 | 17.9 | 383.6 | 430.2 | 232.3 | 400.3 | 136 | 453.7 | 398.3 | 169.4 | 148.8 | 150.8 | 107 | 86.7 | 323.1 | 388.3 | 427.1 | 76.4 | 334.2 | 66.6 | 99 | 59.6 | 362.1 | 427.3 | 350.2 | 433.1 | 390.7 | 566.2 | 479.8
2423.1 | 2184.1 | -6.7 | 0 | 0 | 423.9 | 488.6 | 336.2 | 330 | 314.5 | 69 | 15.7 | 109.6 | 6.6 | 205 | 16.3 | 379.1 | 427 | 227.2 | 377.5 | 134 | 451.5 | 394.8 | 168 | 148.1 | 149.6 | 106.4 | 86.3 | 323.3 | 388.1 | 426.8 | 76.3 | 333.1 | 65.8 | 98.7 | 59 | 361.8 | 427 | 349.6 | 432.7 | 390.3 | 565.6 | 479.5
2424.1 | 2185.1 | -6.7 | 0 | 0 | 423 | 488.5 | 335.6 | 329.7 | 314.1 | 68.8 | 15.7 | 109.4 | 7 | 210.4 | 17.3 | 374.9 | 422.3 | 222 | 354.5 | 131.8 | 449.1 | 391.2 | 167.4 | 149.1 | 150 | 105.4 | 85.8 | 323.2 | 387.9 | 426.5 | 76.3 | 331.7 | 64.7 | 98.7 | 59.1 | 361.5 | 426.8 | 348.9 | 432.3 | 389.9 | 564.9 | 479.3
2425.1 | 2186.1 | -6.7 | 0 | 0 | 422.3 | 486 | 335 | 329.3 | 313.4 | 68.7 | 15.7 | 109.2 | 7 | 210.3 | 19.4 | 370.9 | 419.2 | 216.4 | 330.1 | 129.7 | 446.7 | 387.6 | 165.7 | 146.6 | 148.7 | 104.8 | 85.5 | 322.7 | 387.2 | 426.2 | 76.1 | 331 | 64.5 | 98.7 | 58.5 | 361.3 | 426.7 | 348.1 | 432 | 389.4 | 564.3 | 479
2426.1 | 2187.1 | -6.7 | 0 | 0 | 421.7 | 485.7 | 334.4 | 328.8 | 312.4 | 68.6 | 15.7 | 109.1 | 6.8 | 212.1 | 17.6 | 367.4 | 415.9 | 210.1 | 302.4 | 127.8 | 444.2 | 384.2 | 164.7 | 145.8 | 148.1 | 104.3 | 85.3 | 322.9 | 386.8 | 425.9 | 75.8 | 330.5 | 63.8 | 98.3 | 56.9 | 361 | 426.5 | 347.4 | 431.6 | 389 | 563.7 | 478.8
2427.1 | 2188.1 | -6.7 | 0 | 0 | 420.7 | 480.5 | 333.7 | 328.1 | 311.1 | 68.5 | 15.7 | 108.9 | 6.9 | 229.7 | 15.1 | 364.3 | 409.5 | 203.8 | 249.6 | 126 | 441.6 | 380.1 | 164.3 | 145 | 147.7 | 103.5 | 86.1 | 323.1 | 386.6 | 425.6 | 75.5 | 329.8 | 63.3 | 98.1 | 55.5 | 360.7 | 426.1 | 346.8 | 431.2 | 388.5 | 563 | 478.6
2428.1 | 2189.1 | -6.7 | 0 | 0 | 420.1 | 476.8 | 333.1 | 327.5 | 311.2 | 68.4 | 15.7 | 108.6 | 7.1 | 216.4 | 15.2 | 361.7 | 407 | 197.6 | 126.5 | 123.7 | 438.5 | 376.4 | 163.4 | 144.6 | 146.1 | 103 | 86.1 | 322.3 | 386.3 | 425.3 | 75.1 | 328.9 | 62.2 | 97.7 | 54.8 | 360.4 | 425.6 | 346.2 | 430.8 | 388.1 | 562.4 | 478.3
2429.1 | 2190.1 | -6.7 | 0 | 0 | 419.1 | 473.5 | 332.5 | 326.9 | 311.7 | 68.3 | 15.7 | 108.3 | 6.8 | 221.6 | 17 | 359.4 | 405.3 | 192 | 120.9 | 122.1 | 435.2 | 372.3 | 162.5 | 144.3 | 145.7 | 102.4 | 86 | 321.1 | 386.1 | 425.1 | 75.3 | 328.2 | 62.4 | 97.3 | 54.5 | 360.2 | 424.9 | 345.5 | 430.4 | 387.7 | 561.8 | 478.1
2430.1 | 2191.1 | -6.7 | 0 | 0 | 417.9 | 470 | 331.9 | 326.3 | 311.7 | 68.2 | 15.7 | 108.1 | 7 | 214 | 17.4 | 357.3 | 401 | 186.5 | 120.1 | 121.2 | 431.4 | 368.6 | 162.8 | 144.4 | 146.8 | 101.7 | 85.9 | 320 | 385.6 | 424.7 | 75 | 327.5 | 62.4 | 96.5 | 54.7 | 359.9 | 424.4 | 345 | 430.1 | 387.3 | 561.1 | 477.8
2431.1 | 2192.1 | -6.7 | 0 | 0 | 417.7 | 467.1 | 331.3 | 325.7 | 311 | 68.1 | 15.7 | 107.9 | 6.1 | 221.9 | 13.7 | 355.4 | 397.2 | 182.2 | 119.5 | 119.8 | 427.1 | 365 | 163.2 | 142.8 | 146.1 | 101.3 | 85.4 | 318.8 | 385.2 | 424.4 | 74.5 | 326.6 | 61.7 | 95.9 | 56.1 | 359.6 | 424.2 | 344.4 | 429.9 | 386.8 | 560.5 | 477.6
2432.1 | 2193.1 | -6.7 | 0 | 0 | 418.1 | 467.6 | 330.9 | 325.2 | 311.1 | 68 | 15.7 | 107.7 | 5.8 | 215.7 | 10.2 | 353.2 | 395 | 177.8 | 119.1 | 118.2 | 422.1 | 361.4 | 162.1 | 142.1 | 145.1 | 100.4 | 85.5 | 318.3 | 385 | 424.1 | 74.4 | 326.4 | 60.9 | 95.7 | 56.3 | 359.3 | 423.8 | 343.9 | 429.7 | 386.4 | 559.9 | 477.3
2433.1 | 2194.1 | -6.8 | 0 | 0 | 417.6 | 468.5 | 330.6 | 324.8 | 310.2 | 67.9 | 15.7 | 107.5 | 6.3 | 221 | 8.5 | 350.8 | 389 | 173 | 118.8 | 116.5 | 416.7 | 356.9 | 161.4 | 141.1 | 143.4 | 100 | 86 | 311.9 | 384.1 | 423.8 | 74.2 | 326 | 61.1 | 95.6 | 55.9 | 359.1 | 423.5 | 343.3 | 429.4 | 386 | 559.2 | 477.1
2434.1 | 2195.1 | -6.7 | 0 | 0 | 416.3 | 467.8 | 330.5 | 324.4 | 309.9 | 67.8 | 15.7 | 107.4 | 7.7 | 211.9 | 9.1 | 348.4 | 384.6 | 168 | 118.4 | 114.7 | 411 | 352.7 | 161.3 | 140.9 | 142.3 | 99.4 | 86 | 305.3 | 383.1 | 423.5 | 74.2 | 325.5 | 60.1 | 95.7 | 55.6 | 358.8 | 423.2 | 342.7 | 429.2 | 385.6 | 558.6 | 476.8
2435.1 | 2196.1 | -6.7 | 0 | 0 | 416 | 466.4 | 330.2 | 323.9 | 309.6 | 67.6 | 15.7 | 107.2 | 7.6 | 210.3 | 9.5 | 346 | 380.2 | 163.3 | 118.1 | 113.4 | 404.6 | 349.3 | 160.5 | 139.5 | 143.6 | 98.7 | 85.7 | 304.2 | 382.5 | 423.2 | 74.2 | 325.3 | 60.1 | 95.6 | 55.6 | 358.6 | 422.8 | 342 | 429 | 385.2 | 558 | 476.6
2436.1 | 2197.1 | -6.7 | 0 | 0 | 415.9 | 467.5 | 329.8 | 323.4 | 309.2 | 67.5 | 15.7 | 107 | 6.8 | 210.7 | 9.4 | 343.8 | 372.1 | 160 | 117.8 | 112.2 | 397.7 | 344.9 | 160.5 | 139.1 | 143.2 | 98.1 | 85.2 | 304.2 | 382.2 | 422.9 | 74.1 | 324.8 | 61 | 95.3 | 56 | 358.3 | 422.3 | 341.5 | 428.7 | 384.8 | 557.4 | 476.3
2437.1 | 2198.1 | -6.7 | 0 | 0 | 415.8 | 463.2 | 329.5 | 323 | 308.6 | 67.3 | 15.8 | 106.8 | 6.6 | 218.3 | 8.1 | 341.6 | 366.3 | 156.3 | 117.5 | 110.4 | 390.4 | 341.2 | 159.6 | 139.1 | 141.6 | 97.5 | 85.4 | 304.2 | 382 | 422.7 | 73.9 | 323.4 | 60.8 | 94.9 | 56.1 | 358 | 421.2 | 340.9 | 428.5 | 384.4 | 556.7 | 476.1
2438.1 | 2199.1 | -6.7 | 0 | 0 | 415.3 | 461.2 | 329.2 | 322.4 | 308.4 | 67.1 | 15.7 | 106.5 | 6.8 | 261.1 | 6.3 | 339.4 | 360 | 152.3 | 117.1 | 108.7 | 382.5 | 336.9 | 158.8 | 138.9 | 140.6 | 96.9 | 85.8 | 304.1 | 381.9 | 422.4 | 73.5 | 323.1 | 60.2 | 94.4 | 56.5 | 357.8 | 420 | 340.4 | 428.3 | 383.9 | 556.1 | 475.9
2439.1 | 2200.1 | -6.7 | 0 | 0 | 414.1 | 458.1 | 329 | 321.9 | 308.7 | 66.7 | 15.7 | 106.2 | 6.8 | 200.7 | 6.8 | 337 | 354.7 | 148.8 | 116.8 | 107.3 | 374.1 | 333 | 158.8 | 139 | 140.9 | 96.2 | 85.7 | 304 | 381.9 | 422.1 | 73.4 | 322.8 | 59 | 94.2 | 57.2 | 357.5 | 419.2 | 339.9 | 428.2 | 383.5 | 555.5 | 475.6
2440.1 | 2201.1 | -6.7 | 0 | 0 | 413.3 | 461.6 | 328.8 | 321.4 | 308.9 | 66.5 | 15.7 | 106.1 | 6.9 | 212.6 | 6.8 | 334.6 | 349 | 145.8 | 116.5 | 105.9 | 365.3 | 329.1 | 158.9 | 138.7 | 140.2 | 95.7 | 85.4 | 303.8 | 381.6 | 421.7 | 73.3 | 322.5 | 58.8 | 93.9 | 57.1 | 357.3 | 419 | 339.4 | 428.1 | 383.1 | 554.9 | 475.3
2441.1 | 2202.1 | -6.7 | 0 | 0 | 412.8 | 460.6 | 328.3 | 320.9 | 307.8 | 66.3 | 15.7 | 106 | 7.1 | 233.1 | 8.1 | 332.4 | 343.7 | 142.7 | 116.2 | 104.7 | 355.9 | 324.9 | 157.5 | 138.3 | 139 | 95.2 | 85 | 303 | 381.4 | 421.4 | 72.9 | 322 | 58.2 | 93.6 | 56.6 | 357 | 418.1 | 338.9 | 427.9 | 382.7 | 554.2 | 475.1
2442.1 | 2203.1 | -6.7 | 0 | 0 | 411.8 | 456.5 | 328 | 320.5 | 305.7 | 66.2 | 15.8 | 105.9 | 5.9 | 201.4 | 10.9 | 330.2 | 338.4 | 139.7 | 115.8 | 103.3 | 346.2 | 318.8 | 157.4 | 138.8 | 139.6 | 94.3 | 84.9 | 302.8 | 381 | 421.1 | 72.8 | 321.1 | 58.3 | 93.2 | 56.5 | 356.8 | 417.8 | 338.8 | 427.8 | 382.3 | 553.6 | 474.8
2443.1 | 2204.1 | -6.6 | 0 | 0 | 410.7 | 455.3 | 327.8 | 320.1 | 305.1 | 66.2 | 15.7 | 105.9 | 5.6 | 263.5 | 9.4 | 328 | 332.9 | 136.7 | 115.5 | 102 | 336.2 | 314.5 | 157.6 | 137.8 | 138.9 | 93.9 | 84.4 | 302.1 | 380.5 | 420.8 | 72.8 | 320.3 | 58.5 | 93 | 56.7 | 356.5 | 417.7 | 339 | 427.7 | 381.9 | 553 | 474.6
2444.1 | 2205.1 | -6.6 | 0 | 0 | 409.8 | 454.3 | 327.3 | 319.7 | 305.6 | 66.2 | 15.8 | 105.9 | 5.4 | 218.6 | 6.5 | 325.9 | 326.7 | 133.5 | 115.2 | 100.7 | 324.6 | 308.5 | 157 | 137.5 | 138.4 | 93.4 | 84.1 | 299.3 | 380.2 | 420.5 | 72.6 | 319.4 | 57.6 | 92.8 | 57.7 | 356.2 | 417.4 | 338.7 | 427.6 | 381.4 | 552.3 | 474.3
2445.1 | 2206.1 | -6.7 | 0 | 0 | 409.7 | 449.6 | 326.7 | 319.3 | 306.3 | 66.1 | 15.7 | 105.7 | 5.7 | 218.4 | 8 | 323.7 | 320.7 | 131.1 | 114.8 | 99.5 | 309.8 | 300.7 | 155.8 | 137.3 | 138.2 | 92.9 | 84 | 299.4 | 379.8 | 420.2 | 72.5 | 318.7 | 57.1 | 92.8 | 57.6 | 356 | 416.9 | 338.4 | 427.5 | 381 | 551.7 | 474.1
2446.1 | 2207.1 | -6.6 | 0 | 0 | 409.4 | 442.6 | 326.2 | 318.8 | 306.3 | 66 | 15.7 | 105.5 | 6.9 | 215.8 | 12.1 | 321.6 | 316.1 | 127.6 | 114.3 | 98.4 | 291.7 | 291.2 | 154.3 | 136.8 | 137.2 | 92.3 | 83.4 | 298.9 | 379.4 | 419.9 | 72.2 | 317.9 | 56.8 | 93 | 57.4 | 355.7 | 416.6 | 337.9 | 427.4 | 380.6 | 551.1 | 473.8
2447.1 | 2208.1 | -6.5 | 0 | 0 | 409 | 436.2 | 325.6 | 318.2 | 305.2 | 65.9 | 15.8 | 105.2 | 5.9 | 212.1 | 12.9 | 319.3 | 312 | 125.1 | 113.9 | 97.7 | 273.8 | 279.2 | 153.4 | 136 | 136.8 | 91.8 | 83.4 | 297.4 | 379.3 | 419.6 | 72.3 | 317.4 | 56.9 | 92.6 | 57.6 | 355.5 | 415.9 | 337.3 | 427.3 | 380.2 | 550.5 | 473.6
2448.1 | 2209.1 | -6.5 | 0 | 0 | 408.2 | 432.1 | 325.1 | 317.7 | 305.6 | 65.8 | 15.8 | 105 | 5.7 | 222.8 | 11.4 | 317.1 | 305.3 | 122.5 | 113.5 | 96.4 | 254.8 | 264 | 152.7 | 135.4 | 136.3 | 91.2 | 83.8 | 297 | 378.8 | 419.3 | 72.2 | 316.7 | 56.1 | 92.4 | 57.5 | 355.2 | 415.9 | 336.8 | 427.2 | 379.8 | 549.9 | 473.3
2449.1 | 2210.1 | -6.4 | 0 | 0 | 407.2 | 431 | 324.5 | 317.2 | 305.4 | 65.7 | 15.8 | 104.8 | 5.9 | 223.7 | 9.1 | 314.9 | 300.7 | 118.9 | 113.2 | 95.3 | 236.2 | 246.3 | 152.3 | 135 | 135.3 | 90.7 | 84.5 | 297.1 | 378.1 | 419 | 72.1 | 316.4 | 55.4 | 92 | 57.4 | 355 | 415.7 | 336.2 | 427.1 | 379.5 | 549.3 | 473.1
2450.1 | 2211.1 | -6.3 | 0 | 0 | 406 | 427.9 | 324 | 316.8 | 305 | 65.5 | 15.8 | 104.6 | 5.6 | 224.2 | 9.4 | 312.6 | 297.8 | 116.1 | 112.7 | 94.4 | 217.5 | 227.8 | 152 | 135.6 | 135.2 | 90.1 | 84.5 | 296.8 | 378 | 418.7 | 71.8 | 316.4 | 55.5 | 91.5 | 56.8 | 354.8 | 415.6 | 335.6 | 426.9 | 379 | 548.7 | 472.8
2451.1 | 2212.1 | -6.1 | 0 | 0 | 405.1 | 424 | 323.6 | 316.3 | 305.2 | 65.4 | 15.8 | 104.5 | 5.3 | 195.8 | 11 | 310.4 | 295.3 | 113.6 | 112.3 | 93.1 | 199.1 | 205.9 | 151.1 | 134.9 | 133.8 | 89.5 | 84.6 | 295.9 | 378 | 418.4 | 71.5 | 316.3 | 55.7 | 91.2 | 56.6 | 354.5 | 415.6 | 335 | 426.8 | 378.6 | 548.1 | 472.6
2452.1 | 2213.1 | -6.3 | 0 | 0 | 404.9 | 419.8 | 323.1 | 315.8 | 305.7 | 65.3 | 15.8 | 104.3 | 5.5 | 212.9 | 12.2 | 308.2 | 291.2 | 110.9 | 111.9 | 91.8 | 181.2 | 180.9 | 151.1 | 134.1 | 133 | 88.8 | 84.7 | 296.2 | 378 | 418.1 | 71.4 | 316 | 55.4 | 90.9 | 56.7 | 354.3 | 415.3 | 334.4 | 426.7 | 378.2 | 547.5 | 472.3
2453.1 | 2214.1 | -6.4 | 0 | 0 | 405 | 417.7 | 322.5 | 315.4 | 305.3 | 65.2 | 15.8 | 104.1 | 5.6 | 203.9 | 13.5 | 306 | 288.8 | 108.2 | 111.5 | 90.6 | 163.7 | 163.7 | 150.9 | 133.6 | 132.2 | 88.3 | 84.5 | 295.9 | 377.8 | 417.8 | 71.3 | 315.2 | 55.1 | 90 | 56.4 | 354 | 414.2 | 333.8 | 426.5 | 377.8 | 546.9 | 472.1
2454.1 | 2215.1 | -6.6 | 0 | 0 | 404.6 | 416.4 | 322.1 | 315 | 304.6 | 65.2 | 15.8 | 104 | 6.5 | 206.1 | 13.5 | 303.8 | 282.9 | 106.2 | 111.1 | 89.4 | 147.6 | 154.5 | 150.4 | 133.3 | 131.1 | 87.8 | 84.9 | 296.4 | 377.4 | 417.5 | 71.1 | 313 | 54.5 | 89.6 | 56.4 | 353.8 | 413 | 333 | 426.4 | 377.4 | 546.3 | 471.8
2455.1 | 2216.1 | -6.6 | 0 | 0 | 403.9 | 413.7 | 321.7 | 314.6 | 304.5 | 65.1 | 15.8 | 103.8 | 6.7 | 201.1 | 13.5 | 301.7 | 278 | 104.4 | 110.8 | 87.9 | 136.1 | 149.8 | 150 | 132.3 | 130 | 87.4 | 84.5 | 296 | 377.2 | 417.2 | 71.2 | 310.9 | 55.1 | 89.8 | 56.7 | 353.5 | 412.2 | 332.4 | 426.2 | 377 | 545.7 | 471.6
2456.1 | 2217.1 | -6.5 | 0 | 0 | 403.1 | 412.5 | 321.3 | 314.2 | 304 | 65 | 15.8 | 103.5 | 7.1 | 200.4 | 15.9 | 299.5 | 271.7 | 102.9 | 110.4 | 86.7 | 126.9 | 147.9 | 149.4 | 131.5 | 129 | 86.9 | 84.6 | 296.1 | 377 | 416.9 | 71.2 | 309.2 | 55.3 | 89.9 | 56.9 | 353.3 | 411 | 331.8 | 426 | 376.6 | 545 | 471.3
2457.1 | 2218.1 | -6.6 | 0 | 0 | 402.3 | 411.2 | 320.7 | 313.8 | 302.3 | 64.9 | 15.8 | 103.4 | 6.2 | 205 | 17.7 | 297.4 | 267.7 | 101.4 | 110.1 | 85.9 | 119.7 | 146.4 | 148.3 | 131.4 | 128.5 | 86.3 | 84.1 | 296.5 | 376.8 | 416.6 | 70.9 | 308 | 54.5 | 89.4 | 57.5 | 353 | 410.4 | 331.2 | 425.8 | 376.2 | 544.4 | 471
2458.1 | 2219.1 | -6.6 | 0 | 0 | 401.5 | 411.3 | 320.1 | 313.4 | 301.5 | 64.9 | 15.8 | 103.2 | 6 | 206.9 | 18.7 | 295.3 | 263.3 | 100 | 109.8 | 85.1 | 113.7 | 145.4 | 147.8 | 132.2 | 128 | 85.7 | 84 | 296.5 | 376.5 | 416.3 | 70.6 | 307.1 | 54.2 | 89 | 57.6 | 352.7 | 410.1 | 330.7 | 425.7 | 375.9 | 543.8 | 470.8
2459.1 | 2220.1 | -6.7 | 0 | 0 | 400.9 | 411.8 | 319.6 | 312.9 | 300.9 | 64.8 | 15.8 | 102.9 | 6 | 208.6 | 17.9 | 293.3 | 260.8 | 98.1 | 109.4 | 84.4 | 108.8 | 144.4 | 147.6 | 131.5 | 126.6 | 85.1 | 83.5 | 296 | 376 | 416 | 70.5 | 306 | 53.9 | 88.9 | 57.4 | 352.5 | 409.9 | 330.2 | 425.6 | 375.5 | 543.2 | 470.5
2460.1 | 2221.1 | -6.7 | 0 | 0 | 400.3 | 410.1 | 319.3 | 312.4 | 300.3 | 64.7 | 15.8 | 102.6 | 6.2 | 227.3 | 15.5 | 291.2 | 256.4 | 96.5 | 109 | 83.6 | 105 | 144.4 | 146.6 | 131 | 124.3 | 84.5 | 83.2 | 295.7 | 376 | 415.8 | 70.5 | 305.4 | 52.9 | 88.8 | 57.7 | 352.2 | 409.5 | 329.7 | 425.5 | 375.1 | 542.6 | 470.3
2461.1 | 2222.1 | -6.7 | 0 | 0 | 399.1 | 408.5 | 319.2 | 311.8 | 300.8 | 64.6 | 15.8 | 102.4 | 5.8 | 215.2 | 13.5 | 289.1 | 251.7 | 95 | 108.5 | 82.8 | 102.2 | 144.6 | 146.7 | 131.5 | 122.1 | 84.1 | 82.7 | 295.7 | 375.7 | 415.5 | 70.3 | 305.2 | 53.4 | 88.5 | 58.6 | 351.9 | 408.7 | 329.2 | 425.4 | 374.7 | 542 | 470
2462.1 | 2223.1 | -6.7 | 0 | 0 | 398 | 408.3 | 318.8 | 311.4 | 299.2 | 64.6 | 15.8 | 102.2 | 6.1 | 216.1 | 14.3 | 287.1 | 244.8 | 94 | 108.3 | 82.1 | 100 | 145.1 | 146.6 | 131 | 120.3 | 83.7 | 81.7 | 296.2 | 375.7 | 415.2 | 70.2 | 304.6 | 53.9 | 88.4 | 58.6 | 351.7 | 408.9 | 328.8 | 425.3 | 374.3 | 541.4 | 469.8
2463.1 | 2224.1 | -6.7 | 0 | 0 | 397.3 | 407.3 | 318.3 | 311.1 | 297.3 | 64.5 | 15.8 | 102 | 5.9 | 210.7 | 16 | 285.1 | 239.6 | 92.9 | 107.6 | 81.4 | 98.8 | 144.7 | 146 | 130.4 | 119.3 | 83.3 | 81 | 296.4 | 375.1 | 414.9 | 70 | 304 | 53.7 | 88.3 | 58.3 | 351.4 | 408.5 | 328.4 | 425.2 | 373.9 | 540.8 | 469.5
2464.1 | 2225.1 | -6.7 | 0 | 0 | 396.9 | 405.3 | 318.1 | 310.8 | 295.4 | 64.4 | 15.8 | 101.8 | 5.6 | 196.1 | 15.6 | 283.1 | 235.8 | 92 | 106.7 | 80.6 | 97.7 | 144.4 | 145.6 | 130 | 119.2 | 82.7 | 80.7 | 296.5 | 374.7 | 414.6 | 69.9 | 303.5 | 53.2 | 88.1 | 58.5 | 351.2 | 408.3 | 327.8 | 425.2 | 373.5 | 540.3 | 469.3
2465.1 | 2226.1 | -6.7 | 0 | 0 | 396.4 | 402.4 | 317.8 | 310.4 | 294.6 | 64.2 | 15.8 | 101.7 | 5.5 | 195.7 | 14.9 | 281.1 | 232.3 | 90.9 | 106.2 | 79.9 | 96.9 | 144.1 | 145.6 | 129.1 | 118.9 | 82 | 80.4 | 297.2 | 373.6 | 414.3 | 69.8 | 303.1 | 53.5 | 88 | 58.4 | 350.9 | 408.3 | 327.3 | 425.1 | 373.2 | 539.7 | 469
2466.1 | 2227.1 | -6.6 | 0 | 0 | 396 | 399.7 | 317.3 | 310.1 | 294.8 | 64 | 15.8 | 101.6 | 7.5 | 210.5 | 15 | 279 | 227.6 | 90 | 105.4 | 79.2 | 96.3 | 143.8 | 145.2 | 128.7 | 118.1 | 81.4 | 80.2 | 296.8 | 372.9 | 414 | 69.8 | 303.2 | 53.4 | 88 | 57.9 | 350.7 | 407.7 | 326.7 | 425 | 372.8 | 539.1 | 468.8
2467.1 | 2228.1 | -6.2 | 0 | 0 | 395.4 | 396.8 | 316.9 | 309.6 | 295 | 63.8 | 15.8 | 101.5 | 7.7 | 217.1 | 14.7 | 277.1 | 222.6 | 89 | 104.7 | 78.4 | 96 | 143.7 | 144.8 | 128.2 | 117.3 | 80.9 | 79.6 | 296.7 | 372.8 | 413.7 | 69.6 | 303.8 | 53.8 | 87.7 | 57.9 | 350.4 | 406.5 | 326.3 | 424.9 | 372.4 | 538.5 | 468.5
2468.1 | 2229.1 | -6.4 | 0 | 0 | 394.4 | 395.5 | 316.5 | 309.2 | 294.3 | 63.7 | 15.8 | 101.4 | 6.6 | 202.6 | 14.7 | 275.1 | 217.8 | 88 | 104.1 | 77.6 | 95.7 | 143.3 | 143.8 | 127.8 | 116.5 | 80.5 | 79.3 | 296.8 | 372.5 | 413.4 | 69.3 | 304.4 | 53.6 | 87.4 | 58.8 | 350.2 | 405.5 | 325.9 | 424.8 | 372 | 538 | 468.3
2469.1 | 2230.1 | -6.7 | 0 | 0 | 394.1 | 395.3 | 316.1 | 308.9 | 293.6 | 63.6 | 15.8 | 101.2 | 6.6 | 217.6 | 14.2 | 273.1 | 213.8 | 86.6 | 103.6 | 77.1 | 95.6 | 142.4 | 143 | 127.9 | 116.6 | 80.1 | 78.7 | 297 | 371.9 | 413.1 | 69.2 | 304.8 | 52.7 | 87.1 | 58.5 | 349.9 | 404.9 | 325.6 | 424.6 | 371.6 | 537.4 | 468
2470.1 | 2231.1 | -6.7 | 0 | 0 | 394.4 | 393.6 | 315.4 | 308.6 | 294.2 | 63.5 | 15.8 | 101.1 | 6 | 213.1 | 17.3 | 271.2 | 209.9 | 84.3 | 102.9 | 76.6 | 95.2 | 141.7 | 142.9 | 127.3 | 116.3 | 79.6 | 78.2 | 296.8 | 371.2 | 412.8 | 69.2 | 304.9 | 53 | 86.9 | 58 | 349.7 | 404.1 | 325.1 | 424.4 | 371.2 | 536.8 | 467.7
2471.1 | 2232.1 | -6.7 | 0 | 0 | 394.2 | 391.1 | 315.2 | 308.5 | 292.4 | 63.4 | 15.8 | 101 | 6.3 | 215.3 | 18.8 | 269.3 | 206.9 | 82.7 | 102.3 | 76.1 | 94.6 | 140.9 | 142.3 | 126.7 | 116 | 78.9 | 78.1 | 296.3 | 370.7 | 412.5 | 69.2 | 305 | 52.9 | 86.8 | 57.4 | 349.5 | 403.1 | 324.7 | 424.2 | 370.8 | 536.2 | 467.5
2472.1 | 2233.1 | -6.7 | 0 | 0 | 393.7 | 390 | 315.1 | 308.2 | 290.6 | 63.3 | 15.8 | 100.8 | 6.4 | 223.7 | 18.6 | 267.3 | 203.6 | 81.2 | 101.6 | 75.6 | 94.4 | 141.3 | 141.7 | 125.8 | 115.2 | 78.3 | 77.8 | 296.7 | 370.3 | 412.2 | 68.9 | 305.2 | 52.1 | 86.7 | 57.2 | 349.2 | 401.7 | 324.3 | 423.9 | 370.4 | 535.7 | 467.2
2473.1 | 2234.1 | -6.7 | 0 | 0 | 392.9 | 388.3 | 314.5 | 308 | 289.5 | 63.2 | 15.8 | 100.7 | 5.9 | 214.2 | 17.4 | 265.4 | 198.3 | 80.2 | 101.7 | 75.1 | 94.3 | 140.8 | 140.4 | 125.2 | 114.6 | 78.1 | 77.4 | 296.2 | 369.8 | 411.9 | 68.8 | 305 | 51.7 | 86.4 | 56.8 | 349 | 400.7 | 323.9 | 423.6 | 370 | 535.1 | 467
2474.1 | 2235.1 | -6.5 | 0 | 0 | 392.2 | 386.1 | 314 | 307.8 | 289.3 | 63.1 | 15.8 | 100.5 | 5.4 | 208.3 | 18.1 | 263.5 | 193.7 | 78.9 | 102.4 | 74.6 | 94.2 | 139.7 | 139.8 | 124.8 | 114.1 | 77.3 | 76.8 | 296.3 | 369 | 411.7 | 68.7 | 304.6 | 51 | 86.4 | 56.8 | 348.8 | 400.1 | 323.6 | 423.3 | 369.6 | 534.5 | 466.7
2475.1 | 2236.1 | -6.5 | 0 | 0 | 391.7 | 384.3 | 313.5 | 307.6 | 288.3 | 63 | 15.8 | 100.3 | 6.3 | 201.5 | 19.1 | 261.6 | 190.2 | 77.8 | 102.3 | 74.1 | 94.3 | 139.4 | 139.7 | 124.7 | 113.5 | 76.7 | 76.6 | 296.2 | 368.9 | 411.3 | 68.7 | 304.4 | 50.8 | 86.1 | 57.1 | 348.5 | 398.8 | 323.3 | 423 | 369.3 | 533.9 | 466.5
2476.1 | 2237.1 | -6.3 | 0 | 0 | 390.9 | 381.8 | 313 | 307.3 | 286.3 | 62.8 | 15.8 | 100.1 | 5.7 | 202.1 | 18 | 259.7 | 186.7 | 76.9 | 101.7 | 73.6 | 94.3 | 139 | 139.7 | 124.4 | 113.3 | 76.2 | 76.4 | 295.8 | 368.6 | 411.1 | 68.7 | 304.2 | 50.1 | 85.9 | 56.7 | 348.3 | 398.5 | 322.9 | 422.8 | 368.9 | 533.3 | 466.2
2477.1 | 2238.1 | -6.2 | 0 | 0 | 390.6 | 380.3 | 312.6 | 307 | 284.7 | 62.6 | 15.9 | 100 | 5.2 | 204.4 | 17.4 | 257.8 | 183.1 | 76.4 | 101.5 | 73.3 | 93.8 | 138.9 | 139.6 | 123.7 | 113 | 75.7 | 76.5 | 295.8 | 368.2 | 410.8 | 68.6 | 304.1 | 50.2 | 85.6 | 56.2 | 348 | 397.7 | 322.6 | 422.5 | 368.5 | 532.7 | 466
2478.1 | 2239.1 | -6.2 | 0 | 0 | 390.3 | 379 | 312.1 | 306.6 | 284 | 62.4 | 15.9 | 100 | 4.9 | 204.7 | 16.5 | 256 | 180.3 | 75.5 | 101.2 | 72.8 | 93.2 | 138.5 | 138.9 | 122.7 | 112.5 | 75.3 | 76.1 | 295.1 | 368 | 410.5 | 68.4 | 303.9 | 51.1 | 85.2 | 56.4 | 347.8 | 397 | 322.2 | 422.3 | 368.1 | 532.2 | 465.7
2479.1 | 2240.1 | -6.3 | 0 | 0 | 389.9 | 378.9 | 311.7 | 306.4 | 282.9 | 62.3 | 15.9 | 100 | 4.9 | 203.6 | 15.7 | 254.1 | 176.6 | 75.1 | 100.8 | 72.3 | 92.3 | 138.1 | 138.2 | 121.4 | 111.8 | 75 | 76 | 294.7 | 367.6 | 410.2 | 68.2 | 303.8 | 50.4 | 84.8 | 56.4 | 347.5 | 397 | 321.9 | 422.1 | 367.8 | 531.6 | 465.5
2480.1 | 2241.1 | -6.2 | 0 | 0 | 389.2 | 378.2 | 311.3 | 306.1 | 281.4 | 62.2 | 15.9 | 99.9 | 4.5 | 200.7 | 15 | 252.4 | 172.6 | 74.5 | 100.6 | 71.9 | 91.7 | 138 | 137.4 | 121.2 | 111.5 | 74.5 | 76.1 | 294.2 | 366.8 | 409.9 | 68.1 | 303.5 | 49.6 | 84.3 | 55.6 | 347.3 | 396.1 | 321.6 | 421.8 | 367.4 | 531 | 465.2
2481.1 | 2242.1 | -6 | 0 | 0 | 388.4 | 377.3 | 310.8 | 305.9 | 279.3 | 62.1 | 15.9 | 99.8 | 4.6 | 206.8 | 14.7 | 250.5 | 169.7 | 74.3 | 100.1 | 71.6 | 91.8 | 137.6 | 136.6 | 121.1 | 110.8 | 74 | 76.3 | 294 | 366.4 | 409.6 | 68 | 303.2 | 49.3 | 84 | 55.1 | 347.1 | 395.7 | 321.2 | 421.6 | 367 | 530.5 | 464.9
2482.1 | 2243.1 | -5.9 | 0 | 0 | 388.5 | 375.9 | 310.5 | 305.6 | 278.1 | 62 | 15.9 | 99.6 | 5.4 | 201.9 | 13.9 | 248.7 | 167.6 | 73.9 | 99.5 | 71.3 | 91.9 | 137.1 | 136.4 | 120.1 | 111 | 73.4 | 76.3 | 293.9 | 366.1 | 409.4 | 67.9 | 303 | 49.8 | 83.6 | 55.2 | 346.8 | 396.2 | 320.9 | 421.4 | 366.7 | 529.9 | 464.7
2483.1 | 2244.1 | -5.8 | 0 | 0 | 388.4 | 374.6 | 310.2 | 305.2 | 276.6 | 61.9 | 15.9 | 99.5 | 5.2 | 204.2 | 13 | 246.9 | 164.5 | 73.3 | 98.8 | 71 | 91.7 | 136.2 | 136.2 | 119.3 | 110.5 | 72.9 | 76 | 294.1 | 365.9 | 409 | 67.7 | 301.1 | 50.3 | 83.6 | 55.2 | 346.6 | 396.2 | 320.6 | 421.2 | 366.3 | 529.3 | 464.4
2484.1 | 2245.1 | -5.8 | 0 | 0 | 387.8 | 374.7 | 309.8 | 304.9 | 274 | 61.8 | 15.9 | 99.4 | 4.9 | 198.4 | 12.5 | 245.2 | 162.1 | 72.9 | 98.2 | 70.8 | 91.7 | 136.6 | 135.2 | 119.2 | 109.9 | 72.3 | 76 | 294.5 | 365.9 | 408.8 | 67.4 | 298.8 | 50.1 | 83.2 | 55.3 | 346.3 | 396.5 | 320.2 | 420.9 | 366 | 528.8 | 464.2
2485.1 | 2246.1 | -5.8 | 0 | 0 | 387.4 | 375.9 | 309.4 | 304.6 | 272.7 | 61.7 | 15.9 | 99.2 | 5 | 204.5 | 12 | 243.4 | 160 | 72.4 | 97.6 | 70.5 | 91.4 | 136.6 | 135.6 | 118.6 | 109.6 | 71.8 | 75.6 | 294.2 | 365.6 | 408.5 | 67.2 | 297.1 | 49.4 | 83 | 55.7 | 346.1 | 396.9 | 319.9 | 420.7 | 365.6 | 528.2 | 463.9
2486.1 | 2247.1 | -6 | 0 | 0 | 387.2 | 375.2 | 309 | 304.3 | 271.8 | 61.5 | 15.9 | 99 | 5.2 | 205.4 | 12 | 241.7 | 156.5 | 71.6 | 96.9 | 70.3 | 91.5 | 136.4 | 135.8 | 118 | 109 | 71.4 | 75.2 | 293.4 | 364.8 | 408.2 | 67.2 | 295.6 | 49.2 | 82.9 | 56.1 | 345.8 | 397 | 319.6 | 420.5 | 365.2 | 527.6 | 463.7
2487.1 | 2248.1 | -6 | 0 | 0 | 386.7 | 373.1 | 308.7 | 304.1 | 269.6 | 61.4 | 15.9 | 98.9 | 5.5 | 215.6 | 11 | 239.9 | 154.2 | 71.1 | 96.3 | 70.1 | 91.3 | 136.5 | 135.3 | 116.7 | 108 | 70.9 | 75.1 | 292.9 | 364.1 | 407.9 | 67.2 | 294.4 | 48.9 | 82.7 | 55.8 | 345.6 | 396.6 | 319.3 | 420.4 | 364.9 | 527.1 | 463.4
2488.1 | 2249.1 | -6.1 | 0 | 0 | 386.3 | 371.3 | 308.4 | 303.7 | 268 | 61.3 | 15.9 | 98.7 | 5.5 | 231.9 | 8.2 | 238.2 | 150.9 | 70.6 | 95.7 | 69.9 | 91.1 | 136.4 | 135.3 | 116.2 | 107.3 | 70.5 | 75 | 293.3 | 363.9 | 407.6 | 67.1 | 293.7 | 48.8 | 83 | 56.3 | 345.3 | 396 | 318.9 | 420.2 | 364.5 | 526.5 | 463.2
2489.1 | 2250.1 | -6.1 | 0 | 0 | 385.7 | 369.4 | 308.1 | 303.4 | 267.4 | 61.3 | 15.9 | 98.5 | 5.6 | 219.7 | 6.5 | 236.5 | 147.6 | 70.2 | 95.2 | 69.7 | 90.9 | 135.2 | 134.4 | 116 | 106.7 | 70 | 75.2 | 293.3 | 363.8 | 407.3 | 66.9 | 293.1 | 48.6 | 82.9 | 55.9 | 345.1 | 395.4 | 318.6 | 420 | 364.2 | 525.9 | 462.9
2490.1 | 2251.1 | -6.2 | 0 | 0 | 385.3 | 367.7 | 307.6 | 303 | 268.1 | 61.1 | 15.9 | 98.3 | 5.4 | 224.5 | 6.2 | 234.8 | 145 | 69.5 | 94.6 | 69.6 | 91.2 | 134.7 | 133.7 | 116 | 106.5 | 69.6 | 75 | 292.9 | 363.6 | 407 | 66.8 | 292.6 | 48.4 | 82.8 | 55.5 | 344.8 | 395.4 | 318.2 | 419.8 | 363.8 | 525.4 | 462.6
2491.1 | 2252.1 | -6.2 | 0 | 0 | 384.8 | 366.6 | 307.1 | 302.6 | 268.4 | 60.9 | 15.9 | 98.2 | 5.4 | 204.6 | 7.4 | 233.2 | 143.6 | 68.8 | 93.9 | 69.4 | 90.7 | 134.1 | 133.3 | 115.7 | 106.7 | 69 | 74.8 | 292.1 | 363.4 | 406.7 | 66.7 | 292.2 | 48.2 | 82.8 | 54.9 | 344.6 | 395.1 | 317.9 | 419.7 | 363.5 | 524.8 | 462.4
2492.1 | 2253.1 | -6.1 | 0 | 0 | 384.1 | 366.2 | 306.8 | 302.2 | 268.2 | 60.7 | 15.9 | 98 | 5 | 221.1 | 7.1 | 231.6 | 141.5 | 68 | 93.3 | 69.1 | 90.5 | 133.8 | 133.2 | 115.7 | 106.6 | 68.6 | 74.6 | 292.2 | 362.9 | 406.4 | 66.5 | 291.9 | 47.9 | 82.6 | 54.9 | 344.3 | 393.9 | 317.5 | 419.5 | 363.1 | 524.2 | 462.1
2493.1 | 2254.1 | -5.8 | 0 | 0 | 383.4 | 366 | 306.5 | 301.8 | 266.5 | 60.5 | 15.9 | 97.9 | 5.1 | 219.4 | 7.4 | 230 | 139.7 | 67.1 | 92.8 | 68.9 | 90.7 | 133.9 | 132.7 | 115.5 | 106.5 | 68.2 | 74.6 | 292 | 362.8 | 406.1 | 66.2 | 292.5 | 47.8 | 82.4 | 55 | 344.1 | 393.2 | 317.1 | 419.3 | 362.8 | 523.7 | 461.9
2494.1 | 2255.1 | -5.8 | 0 | 0 | 383.1 | 365.2 | 306.1 | 301.3 | 266.4 | 60.4 | 15.9 | 97.8 | 5.8 | 232.8 | 8 | 228.4 | 137.4 | 66.3 | 92.2 | 68.7 | 90.5 | 133.4 | 132.1 | 115.3 | 105.9 | 67.8 | 74.6 | 291.7 | 362.1 | 405.9 | 66.3 | 293.1 | 47.6 | 82.3 | 55.6 | 343.8 | 392.9 | 316.8 | 419.1 | 362.4 | 523.1 | 461.6
2495.1 | 2256.1 | -5.8 | 0 | 0 | 382 | 363.9 | 305.6 | 300.9 | 267.5 | 60.2 | 15.9 | 97.6 | 6.7 | 268.7 | 6.4 | 226.8 | 134.7 | 65.5 | 91.7 | 68.5 | 90.2 | 133 | 131.8 | 115.4 | 105.9 | 67.4 | 74.3 | 291.5 | 362.2 | 405.6 | 66.3 | 293 | 48.5 | 82.2 | 55.4 | 343.6 | 391.9 | 316.3 | 418.9 | 362.1 | 522.5 | 461.4
2496.1 | 2257.1 | -5.8 | 0 | 0 | 381.3 | 362.4 | 305.1 | 300.6 | 267.5 | 60 | 15.9 | 97.5 | 7.1 | 230.5 | 5.4 | 225.3 | 131.5 | 64.9 | 91.3 | 68.3 | 89.8 | 132.7 | 131.7 | 115 | 105.5 | 67 | 74 | 291.5 | 362.3 | 405.3 | 66.3 | 289.5 | 47.9 | 82 | 54.8 | 343.3 | 390.7 | 315.9 | 418.7 | 361.7 | 522 | 461.1
2497.1 | 2258.1 | -6.2 | 0 | 0 | 380.8 | 361.4 | 304.7 | 300.3 | 265.4 | 59.9 | 15.9 | 97.3 | 5.9 | 192.5 | 4.8 | 223.8 | 128.2 | 64.3 | 90.8 | 68.2 | 89.6 | 132.3 | 131 | 114.1 | 104.6 | 66.7 | 73.9 | 291.5 | 362.2 | 405 | 66.1 | 287.2 | 48.1 | 81.8 | 54.7 | 343.1 | 390 | 315.5 | 418.6 | 361.3 | 521.4 | 460.9
2498.1 | 2259.1 | -6.3 | 0 | 0 | 380.6 | 360.6 | 304.3 | 299.9 | 262.9 | 59.7 | 15.9 | 97.1 | 5 | 225 | 4 | 222.3 | 125.7 | 63.6 | 90.4 | 68 | 89.5 | 131.5 | 130.3 | 114 | 104.3 | 66.3 | 73.8 | 291.6 | 361.7 | 404.8 | 66.1 | 286.1 | 47.9 | 81.8 | 54 | 342.8 | 389.3 | 315.1 | 418.4 | 361 | 520.9 | 460.6
2499.1 | 2260.1 | -6.5 | 0 | 0 | 380.5 | 359.2 | 303.9 | 299.6 | 262.6 | 59.6 | 15.9 | 97 | 6 | 206.8 | 3.8 | 220.8 | 123.6 | 63.2 | 89.9 | 67.9 | 89.5 | 130.8 | 130 | 113.8 | 103.9 | 66 | 73.8 | 291.6 | 360.8 | 404.5 | 66.2 | 285.1 | 47.7 | 81.6 | 53.5 | 342.5 | 388 | 314.7 | 418.3 | 360.6 | 520.3 | 460.4
2500.1 | 2261.1 | -6.4 | 0 | 0 | 380.6 | 357.4 | 303.5 | 299.3 | 261.9 | 59.5 | 15.9 | 97 | 6.2 | 246.4 | 6.8 | 219.3 | 121.4 | 63.1 | 89.5 | 67.8 | 89.7 | 130.4 | 129.7 | 113.6 | 103.4 | 65.6 | 73.7 | 291.1 | 360.8 | 404.2 | 66.3 | 285.9 | 48.1 | 81.6 | 53.4 | 342.3 | 387.4 | 314.2 | 418.2 | 360.3 | 519.8 | 460.1
2501.1 | 2262.1 | -6.3 | 0 | 0 | 379.9 | 356 | 303.1 | 298.9 | 261.9 | 59.4 | 16 | 96.9 | 5.1 | 227.3 | 8.6 | 217.9 | 120.3 | 62.6 | 89.1 | 67.6 | 90.1 | 129.5 | 129.1 | 113.8 | 103.5 | 65.4 | 73.7 | 290.5 | 360.6 | 403.9 | 66.2 | 286.3 | 48.4 | 81.3 | 53.1 | 342 | 387.1 | 313.8 | 418 | 359.9 | 519.2 | 459.9
2502.1 | 2263.1 | -6.3 | 0 | 0 | 379.4 | 354.7 | 302.8 | 298.5 | 261.7 | 59.3 | 16 | 96.8 | 5.4 | 236.3 | 9.5 | 216.4 | 118.7 | 62.3 | 88.6 | 67.5 | 91 | 129.2 | 127 | 113.8 | 103.2 | 65.1 | 73.5 | 289.7 | 360.3 | 403.7 | 66.1 | 287 | 49.3 | 81 | 53.4 | 341.8 | 386.6 | 313.3 | 417.9 | 359.5 | 518.7 | 459.6
2503.1 | 2264.1 | -6.2 | 0 | 0 | 379.2 | 354 | 302.4 | 298 | 261.2 | 59.2 | 16 | 96.7 | 6.4 | 247.4 | 11.6 | 215 | 116.2 | 67.5 | 88.2 | 67.4 | 90.8 | 128.1 | 126.9 | 113.6 | 103.3 | 64.8 | 73.2 | 289.7 | 359.9 | 403.4 | 66.2 | 287.6 | 50.1 | 81.2 | 52.9 | 341.6 | 385.6 | 312.8 | 417.8 | 359.2 | 518.1 | 459.4
2504.1 | 2265.1 | -6 | 0 | 0 | 378.8 | 353.4 | 302.1 | 297.5 | 259.8 | 59.1 | 16 | 96.6 | 6.4 | 244.9 | 13.2 | 213.6 | 113.9 | 72.5 | 87.8 | 67.3 | 90.7 | 127.9 | 126.7 | 113.7 | 103.2 | 64.6 | 72.8 | 289.4 | 359.5 | 403.1 | 66.1 | 288.1 | 51.7 | 81.1 | 52.9 | 341.3 | 385.7 | 312.4 | 417.7 | 358.8 | 517.6 | 459.1
2505.1 | 2266.1 | -6.2 | 0 | 0 | 378.5 | 352.7 | 301.8 | 297.2 | 259.2 | 58.9 | 16 | 96.5 | 6.2 | 252 | 16.1 | 212.2 | 112.8 | 69.7 | 87.4 | 67.1 | 90.1 | 126.9 | 126.6 | 113.7 | 102.6 | 64.4 | 72.6 | 288.7 | 359.3 | 402.8 | 66 | 288.3 | 50.3 | 81.3 | 52.8 | 341.1 | 386.6 | 312.1 | 417.5 | 358.5 | 517.1 | 458.9
2506.1 | 2267.1 | -6.1 | 0 | 0 | 377.7 | 351.9 | 301.4 | 296.8 | 256.4 | 58.8 | 16 | 96.3 | 7.1 | 250.6 | 16.8 | 210.9 | 110.2 | 67.3 | 86.9 | 67 | 89.1 | 126.5 | 126.4 | 114.4 | 102 | 64.1 | 72.4 | 288.3 | 359.3 | 402.6 | 65.9 | 288.8 | 49.2 | 81.4 | 53.4 | 340.8 | 387 | 311.7 | 417.4 | 358.1 | 516.5 | 458.6
2507.1 | 2268.1 | -6 | 0 | 0 | 377.2 | 351.2 | 301.1 | 296.6 | 253.5 | 58.7 | 16 | 96.2 | 6.4 | 247.9 | 15.1 | 209.5 | 109.3 | 66.1 | 86.5 | 67 | 88.8 | 125.7 | 126.2 | 114.4 | 101.5 | 63.8 | 72 | 288.2 | 359.2 | 402.3 | 65.9 | 288.8 | 48.2 | 81.4 | 53.6 | 340.6 | 387 | 311.3 | 417.3 | 357.8 | 516 | 458.4
2508.1 | 2269.1 | -6 | 0 | 0 | 376.8 | 351 | 300.6 | 296.3 | 251.3 | 58.5 | 16 | 96 | 6.1 | 244 | 15.1 | 208.1 | 108 | 64.9 | 86.4 | 66.9 | 89 | 125.5 | 125.4 | 114.1 | 101.4 | 63.6 | 71.9 | 287.8 | 358.6 | 402 | 65.8 | 288.6 | 47.5 | 81.4 | 52.5 | 340.3 | 386.8 | 311 | 417.2 | 357.4 | 515.4 | 458.1
2509.1 | 2270.1 | -6.1 | 0 | 0 | 376 | 350.6 | 300.4 | 295.9 | 252 | 58.5 | 16 | 95.8 | 6.7 | 239.7 | 15.6 | 206.8 | 107.7 | 72 | 86 | 66.9 | 88.7 | 124.6 | 125.3 | 113.9 | 100.7 | 63.5 | 71.6 | 287.9 | 358.6 | 401.7 | 65.8 | 288.5 | 48.2 | 81.4 | 52.7 | 340.1 | 387 | 310.6 | 417.1 | 357.1 | 514.9 | 457.8
2510.1 | 2271.1 | -6.1 | 0 | 0 | 375.4 | 349.8 | 300.2 | 295.6 | 252.1 | 58.4 | 16 | 95.7 | 6.4 | 244.2 | 15.5 | 205.5 | 106.2 | 70.6 | 85.5 | 66.9 | 88 | 123.8 | 124.7 | 114.1 | 100.1 | 63.2 | 71.4 | 288.4 | 358.7 | 401.5 | 65.8 | 288.2 | 48.2 | 81.3 | 52.3 | 339.9 | 386.6 | 310.2 | 416.9 | 356.7 | 514.4 | 457.6
2511.1 | 2272.1 | -5.9 | 0 | 0 | 374.7 | 349.4 | 299.9 | 295.3 | 251.1 | 58.3 | 16 | 95.5 | 5.4 | 236.2 | 16.2 | 204.2 | 105.2 | 68.7 | 85.2 | 66.9 | 87.3 | 123.4 | 124.3 | 114.4 | 100.1 | 63 | 71.4 | 288.7 | 358.3 | 401.2 | 65.8 | 288.1 | 48 | 81.4 | 51.7 | 339.6 | 385.9 | 309.9 | 416.7 | 356.3 | 513.8 | 457.3
2512.1 | 2273.1 | -5.7 | 0 | 0 | 374.5 | 349.1 | 299.5 | 295 | 249.8 | 58.2 | 16 | 95.4 | 5.3 | 239.2 | 17.2 | 203 | 103.7 | 66.7 | 84.9 | 66.9 | 86.6 | 123.1 | 124 | 114.7 | 100 | 62.9 | 71.4 | 288.4 | 358.2 | 400.9 | 65.9 | 288.2 | 47.7 | 81.4 | 51.5 | 339.4 | 385.4 | 309.4 | 416.5 | 356 | 513.3 | 457.1
2513.1 | 2274.1 | -5.8 | 0 | 0 | 374.5 | 348.8 | 299.2 | 294.7 | 249 | 58.1 | 16 | 95.3 | 4.7 | 242.9 | 17.1 | 201.7 | 102 | 72.2 | 84.5 | 66.8 | 86.3 | 122.1 | 123 | 115.4 | 99.5 | 62.6 | 71.4 | 288.3 | 357.6 | 400.6 | 66 | 288.1 | 47.5 | 81.3 | 51.4 | 339.1 | 384.2 | 309 | 416.3 | 355.7 | 512.8 | 456.8
2514.1 | 2275.1 | -5.5 | 0 | 0 | 373.9 | 348.2 | 299 | 294.3 | 247 | 58 | 16 | 95.3 | 4.5 | 241.2 | 16 | 200.5 | 99.9 | 72.3 | 84.1 | 66.9 | 86.1 | 121.3 | 122.6 | 115.3 | 98.5 | 62.4 | 71.4 | 287.5 | 357.5 | 400.4 | 65.9 | 287.9 | 47.7 | 81.4 | 51.7 | 338.9 | 383 | 308.7 | 416.2 | 355.3 | 512.2 | 456.6
2515.1 | 2276.1 | -5.1 | 0 | 0 | 373.1 | 348.1 | 298.8 | 293.9 | 245.1 | 57.9 | 16 | 95.3 | 4.6 | 243 | 15.2 | 199.2 | 98.5 | 71.5 | 83.7 | 66.9 | 85.4 | 121.4 | 122.3 | 115.2 | 98.2 | 62.3 | 71.2 | 285.9 | 357.3 | 400.1 | 65.6 | 288 | 47.9 | 81 | 51.6 | 338.6 | 382.6 | 308.3 | 416 | 355 | 511.7 | 456.3
2516.1 | 2277.1 | -5.2 | 0 | 0 | 372.4 | 347.4 | 298.4 | 293.5 | 242.2 | 57.8 | 16 | 95.3 | 4.9 | 244.5 | 13.2 | 198 | 97.3 | 70.9 | 83.4 | 66.9 | 84.9 | 120.5 | 121.6 | 115 | 97.3 | 62.1 | 70.9 | 285 | 356.9 | 399.8 | 65.5 | 288.2 | 47.7 | 80.9 | 51.3 | 338.4 | 382.3 | 307.9 | 415.9 | 354.7 | 511.2 | 456.1
2517.1 | 2278.1 | -5.6 | 0 | 0 | 371.9 | 347.1 | 297.9 | 293.1 | 237.7 | 57.7 | 16 | 95.2 | 5.5 | 247.5 | 12 | 196.8 | 96.2 | 70.6 | 83 | 66.8 | 84 | 120.2 | 121.4 | 114.7 | 97.3 | 62 | 70.8 | 284.5 | 356.3 | 399.6 | 65.4 | 288.3 | 47.6 | 80.9 | 51.1 | 338.1 | 381.6 | 307.5 | 415.9 | 354.3 | 510.7 | 455.9
2518.1 | 2279.1 | -5.6 | 0 | 0 | 371.3 | 347 | 297.3 | 292.7 | 234.9 | 57.6 | 16 | 95 | 5.4 | 240 | 11.1 | 195.6 | 94.4 | 70.6 | 82.6 | 66.8 | 83.4 | 119.6 | 120.9 | 114.5 | 97.2 | 61.8 | 70.6 | 283.9 | 355.9 | 399.3 | 65.2 | 288.4 | 47.7 | 80.7 | 50.5 | 337.9 | 381.8 | 307.1 | 415.8 | 354 | 510.1 | 455.6
2519.1 | 2280.1 | -5.5 | 0 | 0 | 370.8 | 346.8 | 297.1 | 292.3 | 232.8 | 57.5 | 16 | 94.8 | 5.8 | 276.2 | 9.4 | 194.4 | 93.7 | 70.2 | 82.2 | 66.7 | 83.1 | 119 | 120.4 | 114.2 | 97.2 | 61.6 | 70.5 | 283.5 | 355.9 | 399 | 65 | 288.4 | 47.5 | 80.6 | 50.4 | 337.6 | 380.8 | 306.7 | 415.7 | 353.7 | 509.6 | 455.4
2520.1 | 2281.1 | -5.7 | 0 | 0 | 370.6 | 346.5 | 296.9 | 291.9 | 229.8 | 57.4 | 16 | 94.6 | 6.6 | 253.6 | 8.6 | 193.3 | 92.4 | 69.7 | 81.9 | 66.6 | 82.3 | 119 | 120.5 | 113.4 | 97.2 | 61.4 | 70.3 | 283.6 | 355.6 | 398.7 | 65 | 288 | 47.5 | 80.6 | 50.2 | 337.3 | 380.5 | 306.4 | 415.6 | 353.3 | 509.1 | 455.1
2521.1 | 2282.1 | -5.7 | 0 | 0 | 370.2 | 345.8 | 296.7 | 291.6 | 225.4 | 57.3 | 16 | 94.5 | 6.4 | 250.5 | 8.6 | 192.2 | 91.4 | 69.5 | 81.5 | 66.5 | 82 | 118.5 | 120.9 | 112.7 | 96.9 | 61.3 | 70 | 283.2 | 355 | 398.4 | 64.9 | 287.8 | 47.5 | 80.4 | 50.8 | 337.1 | 380.9 | 306 | 415.5 | 353 | 508.6 | 454.9
2522.1 | 2283.1 | -5.8 | 0 | 0 | 369.9 | 344.9 | 296.4 | 291.2 | 221.3 | 57.2 | 16.1 | 94.3 | 6.2 | 248 | 10 | 191 | 90.2 | 69.3 | 81.2 | 66.4 | 81.9 | 118.2 | 120.7 | 113.4 | 96.9 | 61.1 | 69.9 | 282.3 | 354.8 | 398.2 | 65 | 287.1 | 47.5 | 80.2 | 50.1 | 336.8 | 380.6 | 305.7 | 415.4 | 352.6 | 508.1 | 454.6
2523.1 | 2284.1 | -6 | 0 | 0 | 369.6 | 344.6 | 296.2 | 290.9 | 216.9 | 57.2 | 16.1 | 94.1 | 6.3 | 248.9 | 11.3 | 189.9 | 89.3 | 68.9 | 80.8 | 66.3 | 81.5 | 117.5 | 120.4 | 113.2 | 96.9 | 60.9 | 69.6 | 282.7 | 354.9 | 397.9 | 65 | 286.8 | 47.3 | 80.2 | 49.4 | 336.6 | 379.8 | 305.3 | 415.2 | 352.3 | 507.5 | 454.3
2524.1 | 2285.1 | -5.9 | 0 | 0 | 369.2 | 343.8 | 296 | 290.7 | 212.3 | 57.1 | 16.1 | 94 | 5.5 | 242.1 | 9.8 | 188.8 | 88.6 | 68.7 | 80.5 | 66.3 | 81.1 | 117.4 | 119.1 | 113.2 | 96.8 | 60.7 | 69.4 | 282.7 | 354.8 | 397.6 | 64.8 | 286.7 | 48 | 80.3 | 48.9 | 336.3 | 379.9 | 305 | 415 | 351.9 | 507 | 454.1
2525.1 | 2286.1 | -5.8 | 0 | 0 | 368.6 | 343.1 | 295.6 | 290.4 | 209.5 | 57.1 | 16.1 | 93.9 | 5.8 | 257 | 10.4 | 187.7 | 86.9 | 68.4 | 80.2 | 66.3 | 80.4 | 117 | 118.3 | 113.1 | 96.6 | 60.5 | 69.1 | 282.5 | 354 | 397.4 | 64.5 | 286.3 | 47.2 | 79.8 | 50 | 336.1 | 379.7 | 304.7 | 414.8 | 351.6 | 506.5 | 453.9
2526.1 | 2287.1 | -5.9 | 0 | 0 | 368.1 | 342.9 | 295.3 | 290.1 | 205.7 | 57 | 16.1 | 93.9 | 5.9 | 239.6 | 11.2 | 186.6 | 85.5 | 68.2 | 79.9 | 66.2 | 79.7 | 116.9 | 118.8 | 113.6 | 96.7 | 60.3 | 68.9 | 282.2 | 353.5 | 397.1 | 64.5 | 286.1 | 47.7 | 79.8 | 49.4 | 335.8 | 380.4 | 304.4 | 414.7 | 351.3 | 506 | 453.6
2527.1 | 2288.1 | -5.8 | 0 | 0 | 367.7 | 341.9 | 295 | 289.8 | 201 | 56.8 | 16.1 | 93.7 | 6.2 | 233.1 | 11.3 | 185.5 | 84.1 | 67.9 | 79.6 | 66.1 | 79.3 | 116.3 | 118.5 | 112.9 | 96.5 | 60.1 | 68.6 | 282.5 | 353.4 | 396.8 | 64.4 | 285.9 | 47.9 | 79.7 | 49 | 335.6 | 380.2 | 304.1 | 414.5 | 350.9 | 505.5 | 453.4
2528.1 | 2289.1 | -5.9 | 0 | 0 | 367.7 | 340.8 | 294.5 | 289.5 | 194.1 | 56.7 | 16.1 | 93.5 | 7.1 | 235.4 | 12.3 | 184.4 | 83.6 | 67.6 | 79.3 | 66 | 78.6 | 115.4 | 118.1 | 111.6 | 96.5 | 59.9 | 68.3 | 282.7 | 353.4 | 396.6 | 64.3 | 285.9 | 47.3 | 79.6 | 48.8 | 335.3 | 380.5 | 303.8 | 414.3 | 350.6 | 505 | 453.1
2529.1 | 2290.1 | -6 | 0 | 0 | 367.6 | 339.9 | 294 | 289 | 186.7 | 56.6 | 16.1 | 93.5 | 6.1 | 235.2 | 10.8 | 183.4 | 82.6 | 67.4 | 79 | 66 | 77.9 | 114.9 | 117.5 | 112.8 | 96.2 | 59.8 | 68.2 | 282.4 | 352.9 | 396.3 | 64.1 | 285.7 | 46.9 | 79.5 | 48 | 335.1 | 380.7 | 303.5 | 414.2 | 350.3 | 504.4 | 452.9
2530.1 | 2291.1 | -5.9 | 0 | 0 | 367.5 | 338.6 | 293.6 | 288.7 | 181.8 | 56.6 | 16.1 | 93.3 | 7.2 | 235 | 9.3 | 182.4 | 81.3 | 67.1 | 78.7 | 66 | 77.4 | 114.5 | 117.2 | 113 | 95.9 | 59.7 | 68.1 | 281.7 | 352.9 | 396 | 64.1 | 285 | 47.3 | 79.6 | 47.8 | 334.9 | 380.9 | 303.2 | 414 | 350 | 503.9 | 452.7
2531.1 | 2292.1 | -5.9 | 0 | 0 | 367.5 | 337.9 | 293.3 | 288.4 | 177.3 | 56.6 | 16.1 | 93.2 | 7.1 | 231.7 | 8.1 | 181.3 | 80 | 66.7 | 78.5 | 66 | 77.3 | 114.1 | 117.2 | 113.6 | 96.2 | 59.5 | 67.8 | 281.1 | 352.8 | 395.8 | 64.1 | 284.7 | 47 | 79.6 | 47.5 | 334.6 | 380.8 | 302.9 | 413.8 | 349.6 | 503.4 | 452.4
2532.1 | 2293.1 | -6 | 0 | 0 | 367.6 | 337.8 | 293 | 288.2 | 172 | 56.6 | 16.1 | 93.1 | 6.8 | 207.7 | 10.4 | 180.3 | 80.4 | 66.5 | 78.2 | 66 | 77.1 | 113.8 | 116.7 | 113 | 96.1 | 59.4 | 67.4 | 281 | 352.3 | 395.5 | 64.1 | 284.3 | 46.9 | 79.4 | 47 | 334.4 | 380.6 | 302.6 | 413.6 | 349.3 | 502.9 | 452.1
2533.1 | 2294.1 | -5.8 | 0 | 0 | 367 | 337.6 | 292.5 | 287.9 | 167.9 | 56.7 | 16.1 | 92.9 | 6.1 | 214.5 | 12.7 | 179.3 | 79.4 | 66.3 | 77.9 | 66 | 76.8 | 113.2 | 116.6 | 112.8 | 96.2 | 59.2 | 67.1 | 280.7 | 351.9 | 395.2 | 64.1 | 284 | 47.3 | 79.4 | 46.9 | 334.2 | 380.8 | 302.3 | 413.4 | 349 | 502.4 | 451.9
2534.1 | 2295.1 | -5.6 | 0 | 0 | 366.4 | 337.2 | 292.2 | 287.7 | 164.7 | 56.7 | 16.1 | 92.6 | 6.6 | 235.7 | 10.6 | 178.3 | 78.7 | 66 | 77.5 | 66 | 76.5 | 112.4 | 116.1 | 113.1 | 95.8 | 59 | 67.1 | 280.7 | 352.2 | 394.9 | 64.2 | 283.7 | 47.1 | 79.5 | 46.9 | 333.9 | 380.7 | 301.9 | 413.3 | 348.7 | 501.9 | 451.6
2535.1 | 2296.1 | -5.1 | 0 | 0 | 365.7 | 336.6 | 291.8 | 287.4 | 161.6 | 56.7 | 16.1 | 92.5 | 6.2 | 220.1 | 11 | 177.2 | 77.9 | 65.6 | 77.2 | 66 | 76.1 | 111.9 | 115.5 | 112.6 | 95.6 | 58.9 | 67.1 | 280 | 351.9 | 394.7 | 64 | 283.3 | 46.9 | 79.2 | 47.2 | 333.7 | 380.2 | 301.5 | 413.1 | 348.3 | 501.4 | 451.4
2536.1 | 2297.1 | -5.4 | 0 | 0 | 365 | 335.7 | 291.4 | 287.2 | 157.3 | 56.8 | 16.1 | 92.3 | 5.8 | 213.8 | 13.4 | 176.2 | 77 | 65.3 | 76.9 | 66 | 75.9 | 111.5 | 115.5 | 112.6 | 95.7 | 58.7 | 66.9 | 278.7 | 351.2 | 394.4 | 63.9 | 283.2 | 46.8 | 79.1 | 47.3 | 333.4 | 380.3 | 301.2 | 413 | 348 | 500.9 | 451.2
2537.1 | 2298.1 | -5.9 | 0 | 0 | 364.5 | 334.7 | 291.1 | 287 | 149 | 56.8 | 16.1 | 92.1 | 5.5 | 228.6 | 13.5 | 175.2 | 76.7 | 65 | 76.7 | 66 | 75.6 | 111.2 | 114.9 | 113.5 | 95.4 | 58.6 | 66.6 | 278.4 | 351.2 | 394.2 | 63.8 | 282.7 | 46.2 | 78.8 | 47.3 | 333.2 | 379.5 | 300.9 | 412.8 | 347.7 | 500.3 | 450.9
2538.1 | 2299.1 | -6.2 | 0 | 0 | 364.5 | 334.3 | 290.9 | 286.8 | 136.6 | 56.7 | 16.1 | 92 | 6.1 | 218.7 | 13.5 | 174.2 | 76.7 | 64.7 | 76.4 | 65.9 | 75.4 | 111.1 | 114.7 | 113.7 | 95.3 | 58.5 | 66.3 | 278.3 | 350.9 | 393.9 | 63.7 | 281.8 | 47.5 | 78.5 | 47.4 | 332.9 | 378.5 | 300.5 | 412.8 | 347.4 | 500 | 450.7
2539.1 | 2300.1 | -6.4 | 0 | 0 | 364.6 | 334.3 | 290.6 | 286.6 | 121.4 | 56.6 | 16.1 | 91.9 | 5.6 | 222.2 | 14.6 | 173.3 | 76.1 | 65.1 | 76.2 | 65.8 | 75.3 | 110.8 | 114.3 | 114.1 | 95.2 | 58.4 | 66.3 | 278.5 | 350.6 | 393.6 | 63.6 | 281.3 | 49.3 | 78.6 | 47.4 | 332.7 | 378.4 | 300.2 | 412.6 | 347 | 499.5 | 450.4
2540.1 | 2301.1 | -6 | 0 | 0 | 364.3 | 334.2 | 290.1 | 286.3 | 101.7 | 56.5 | 16.1 | 91.8 | 5.3 | 245.6 | 11.9 | 172.3 | 76.4 | 64.7 | 76 | 65.7 | 75.3 | 110.1 | 113.6 | 113.3 | 95 | 58.2 | 66.1 | 278.5 | 350.1 | 393.3 | 63.4 | 281.1 | 49.2 | 78.6 | 46.7 | 332.4 | 378.3 | 299.9 | 412.5 | 346.7 | 499 | 450.2
2541.1 | 2302.1 | -5.9 | 0 | 0 | 364.4 | 334 | 289.8 | 286.1 | 85.1 | 56.3 | 16.1 | 91.7 | 5.4 | 216.2 | 11.4 | 171.4 | 75.8 | 64.2 | 75.8 | 65.6 | 75.3 | 109.5 | 113 | 113.6 | 95 | 58.1 | 65.9 | 278.6 | 350.1 | 393.1 | 63.3 | 281.1 | 49.3 | 78.3 | 46.6 | 332.2 | 377.8 | 299.6 | 412.4 | 346.4 | 498.5 | 449.9
2542.1 | 2303.1 | -6 | 0 | 0 | 364.1 | 333.7 | 289.6 | 285.8 | 69.8 | 56.1 | 16.1 | 91.5 | 5.5 | 217 | 13.8 | 170.4 | 75.5 | 64.2 | 75.6 | 65.6 | 75.2 | 108.9 | 112.8 | 114.4 | 95 | 57.9 | 65.7 | 278.2 | 349.6 | 392.8 | 63.2 | 281.2 | 49.3 | 78 | 46.4 | 332 | 377.5 | 299.3 | 412.3 | 346.1 | 498 | 449.7
2543.1 | 2304.1 | -5.8 | 0 | 0 | 364 | 333.2 | 289.3 | 285.5 | 57.8 | 55.9 | 16.1 | 91.4 | 5.2 | 219.2 | 14.4 | 169.5 | 74.6 | 64 | 75.4 | 65.6 | 75 | 108.7 | 112.9 | 114.8 | 94.8 | 57.8 | 65.8 | 278 | 348.9 | 392.6 | 63.2 | 281 | 49.5 | 77.8 | 47.1 | 331.7 | 377.7 | 298.9 | 412.1 | 345.7 | 497.5 | 449.4
2544.1 | 2305.1 | -5.8 | 0 | 0 | 363.6 | 332.6 | 289 | 285.2 | 51.5 | 55.8 | 16.1 | 91.3 | 5.8 | 209 | 15.6 | 168.6 | 73.9 | 64 | 75.2 | 65.5 | 74.7 | 108.3 | 112.7 | 115.2 | 94.7 | 57.7 | 65.5 | 277.5 | 349.1 | 392.3 | 63 | 281 | 48.5 | 77.6 | 47.9 | 331.5 | 377.4 | 298.6 | 411.9 | 345.4 | 497 | 449.2
2545.1 | 2306.1 | -5.8 | 0 | 0 | 363 | 332.2 | 288.7 | 284.9 | 48.4 | 55.7 | 16.2 | 91.1 | 6.3 | 209.3 | 15.4 | 167.7 | 73.8 | 64.1 | 75 | 65.5 | 74.3 | 107.9 | 112.2 | 115.2 | 94.6 | 57.5 | 65.2 | 277.3 | 348.7 | 392.1 | 62.8 | 280.7 | 48.1 | 77.4 | 47.9 | 331.3 | 377.3 | 298.2 | 411.7 | 345.1 | 496.5 | 448.9
2546.1 | 2307.1 | -5.8 | 0 | 0 | 362.5 | 331.9 | 288.5 | 284.6 | 48.9 | 55.5 | 16.2 | 90.9 | 6.4 | 205.1 | 15.8 | 166.8 | 73.8 | 63.8 | 74.8 | 65.4 | 73.8 | 107.7 | 111.8 | 116 | 94.9 | 57.5 | 65.2 | 277 | 348.4 | 391.8 | 62.8 | 280.3 | 47.2 | 77.5 | 47.7 | 331 | 376.6 | 297.8 | 411.6 | 344.8 | 496 | 448.7
2547.1 | 2308.1 | -6.2 | 0 | 0 | 362.1 | 331.6 | 288.3 | 284.3 | 49.2 | 55.4 | 16.2 | 90.8 | 5.8 | 225.8 | 14 | 165.9 | 74.1 | 63.7 | 74.6 | 65.3 | 73.7 | 107.2 | 111.6 | 116.5 | 95 | 57.4 | 65.2 | 276.7 | 348.2 | 391.6 | 62.9 | 280.2 | 47.9 | 77.4 | 47.6 | 330.8 | 376.2 | 297.5 | 411.4 | 344.5 | 495.5 | 448.5
2548.1 | 2309.1 | -6.4 | 0 | 0 | 361.9 | 331.2 | 288.2 | 284 | 49.3 | 55.4 | 16.2 | 90.8 | 5.7 | 235.4 | 10.9 | 165 | 74.3 | 63.3 | 74.4 | 65.2 | 73.5 | 106.7 | 111.5 | 115.7 | 95.1 | 57.3 | 65.2 | 276.6 | 347.1 | 391.3 | 62.8 | 279.7 | 49 | 77.5 | 47.8 | 330.6 | 375.9 | 297.2 | 411.3 | 344.2 | 495 | 448.2
2549.1 | 2310.1 | -6.2 | 0 | 0 | 361.1 | 331.2 | 288 | 283.8 | 48.8 | 55.3 | 16.2 | 90.7 | 5.8 | 222.4 | 10.3 | 164.1 | 74.6 | 63.1 | 74.2 | 65.1 | 73 | 106 | 110.6 | 115.1 | 95.2 | 57.2 | 64.9 | 275.7 | 346.7 | 391 | 62.7 | 279.4 | 48.6 | 77.5 | 48.6 | 330.3 | 375.8 | 296.8 | 411.2 | 343.9 | 494.5 | 448
2550.1 | 2311.1 | -5.8 | 0 | 0 | 360.9 | 331.1 | 287.7 | 283.7 | 47.2 | 55.2 | 16.2 | 90.7 | 5.8 | 213.8 | 9.5 | 163.3 | 74.2 | 62.9 | 74 | 65.1 | 72.8 | 105.6 | 110.4 | 115.7 | 94.8 | 57.1 | 64.5 | 275.1 | 346.7 | 390.8 | 62.8 | 279.1 | 48 | 77.7 | 47.9 | 330.1 | 375.8 | 296.5 | 411.1 | 343.6 | 494 | 447.8
2551.1 | 2312.1 | -5.7 | 0 | 0 | 360.3 | 331.1 | 287.4 | 283.5 | 47.5 | 55.1 | 16.2 | 90.6 | 5.9 | 238 | 9.7 | 162.4 | 73.8 | 62.6 | 73.8 | 65 | 72.6 | 105.7 | 110.1 | 113.9 | 94.8 | 57 | 64.3 | 273.5 | 346.2 | 390.5 | 62.8 | 278.8 | 47.4 | 77.7 | 47.4 | 329.9 | 375.8 | 296.2 | 410.9 | 343.3 | 493.6 | 447.5
2552.1 | 2313.1 | -5.9 | 0 | 0 | 360.1 | 331.5 | 287.2 | 283.3 | 48.1 | 55.1 | 16.2 | 90.4 | 5.6 | 227.9 | 10.6 | 161.5 | 73 | 62.4 | 73.6 | 64.9 | 72.4 | 105.5 | 110 | 114.1 | 94.7 | 56.9 | 64.4 | 273.6 | 345.9 | 390.3 | 62.7 | 278.5 | 46.8 | 77.7 | 47.5 | 329.6 | 375.3 | 295.9 | 410.7 | 343 | 493.1 | 447.3
2553.1 | 2314.1 | -6.1 | 0 | 0 | 359.7 | 331.7 | 287.1 | 283 | 49.2 | 55 | 16.2 | 90.3 | 5.1 | 213 | 10.7 | 160.7 | 72.2 | 62 | 73.5 | 64.8 | 72.2 | 104.9 | 109.7 | 113.6 | 94.6 | 56.8 | 64.3 | 273.6 | 345.6 | 390 | 62.6 | 278.3 | 47 | 77.3 | 47.6 | 329.4 | 374.4 | 295.6 | 410.5 | 342.6 | 492.6 | 447
2554.1 | 2315.1 | -5.9 | 0 | 0 | 359.2 | 331.3 | 286.9 | 282.6 | 45.6 | 55 | 16.2 | 90.2 | 6 | 238.4 | 9.9 | 159.8 | 71.4 | 61.9 | 73.2 | 64.6 | 72.1 | 104.4 | 109.4 | 113.7 | 94.5 | 56.7 | 64.3 | 273.3 | 345.4 | 389.8 | 62.5 | 278.1 | 48.6 | 77.4 | 47.2 | 329.2 | 374.2 | 295.3 | 410.3 | 342.3 | 492.1 | 446.8
2555.1 | 2316.1 | -5.8 | 0 | 0 | 358.9 | 330.9 | 286.6 | 282.2 | 46.6 | 54.9 | 16.2 | 90.2 | 6.2 | 199.7 | 8.1 | 159 | 70.9 | 61.9 | 73 | 64.5 | 72.1 | 104.2 | 109 | 114.4 | 94.9 | 56.7 | 64 | 272.9 | 345.1 | 389.5 | 62.5 | 277.6 | 48.8 | 77.4 | 47.2 | 329 | 374 | 295 | 410.1 | 342 | 491.6 | 446.5
2556.1 | 2317.1 | -5.6 | 0 | 0 | 358.4 | 330.5 | 286.4 | 281.9 | 47.5 | 54.8 | 16.2 | 90.2 | 5.3 | 235.1 | 9 | 158.2 | 70.4 | 61.9 | 72.7 | 64.4 | 72.2 | 103.5 | 108.9 | 115.8 | 95.2 | 56.6 | 63.6 | 272.9 | 344.7 | 389.2 | 62.5 | 276.9 | 48.8 | 77.3 | 47.9 | 328.8 | 374 | 294.7 | 409.9 | 341.7 | 491.1 | 446.3
2557.1 | 2318.1 | -5.5 | 0 | 0 | 358 | 330.6 | 286.1 | 281.6 | 50.1 | 54.7 | 16.2 | 90.2 | 5.3 | 216.5 | 7.7 | 157.4 | 70.3 | 61.6 | 72.5 | 64.3 | 72.2 | 103 | 108.3 | 116 | 95.2 | 56.5 | 63.6 | 273.4 | 344.5 | 389 | 62.4 | 276.2 | 49 | 77.2 | 48.3 | 328.6 | 373.3 | 294.4 | 409.7 | 341.4 | 490.7 | 446
2558.1 | 2319.1 | -5.7 | 0 | 0 | 357.4 | 330.2 | 285.8 | 281.3 | 48.3 | 54.6 | 16.2 | 90.1 | 4.8 | 245 | 6 | 156.6 | 69.7 | 61.5 | 72.3 | 64.3 | 72 | 102.7 | 108.1 | 116.3 | 95.2 | 56.4 | 63.6 | 273.5 | 344.4 | 388.8 | 62.3 | 275.6 | 48.6 | 77.4 | 48.8 | 328.4 | 372.8 | 294.1 | 409.5 | 341.1 | 490.2 | 445.8
2559.1 | 2320.1 | -5.9 | 0 | 0 | 356.9 | 329.5 | 285.6 | 281 | 49.3 | 54.5 | 16.2 | 90 | 5.3 | 251.9 | 5.2 | 155.8 | 69.5 | 61.3 | 72.2 | 64.2 | 71.9 | 102.4 | 107.9 | 115.6 | 95.2 | 56.3 | 63.7 | 273.2 | 344.1 | 388.5 | 62.2 | 275.1 | 48 | 77.4 | 48.6 | 328.2 | 373 | 293.8 | 409.4 | 340.8 | 489.7 | 445.6
2560.1 | 2321.1 | -5.9 | 0 | 0 | 356.2 | 329.8 | 285.2 | 280.7 | 50 | 54.4 | 16.2 | 89.9 | 5.5 | 205.3 | 5.1 | 154.9 | 69.5 | 61.1 | 72.1 | 64 | 71.7 | 102.2 | 107.4 | 115.3 | 95.4 | 56.2 | 63.3 | 272.6 | 344 | 388.2 | 62.1 | 274.7 | 48.5 | 77.2 | 48.6 | 328 | 373 | 293.6 | 409.2 | 340.5 | 489.2 | 445.3
2561.1 | 2322.1 | -5.9 | 0 | 0 | 355.5 | 329.5 | 284.9 | 280.5 | 51.8 | 54.3 | 16.2 | 89.8 | 5.5 | 210.5 | 6.7 | 154.2 | 69.6 | 61 | 71.9 | 63.8 | 71.5 | 102 | 106.8 | 114.3 | 95.3 | 56.2 | 63.4 | 271.7 | 343.9 | 388 | 62.1 | 274.5 | 48.7 | 77.1 | 49.1 | 327.8 | 373 | 293.4 | 409 | 340.2 | 488.7 | 445.1
2562.1 | 2323.1 | -5.9 | 0 | 0 | 355.3 | 328.7 | 284.5 | 280.3 | 50.4 | 54.3 | 16.2 | 89.7 | 5.1 | 223 | 9.2 | 153.4 | 68.7 | 60.9 | 71.7 | 63.6 | 71 | 101.3 | 106.8 | 115.4 | 94.8 | 56.1 | 63.3 | 271.5 | 343.6 | 387.7 | 62.1 | 274 | 49.3 | 77 | 49.5 | 327.5 | 373.1 | 293.1 | 408.9 | 339.9 | 488.3 | 444.9
2563.1 | 2324.1 | -5.8 | 0 | 0 | 355 | 327.1 | 284.1 | 280 | 47.5 | 54.2 | 16.2 | 89.6 | 5.5 | 201.4 | 9.2 | 152.6 | 67.6 | 60.9 | 71.6 | 63.5 | 70.7 | 100.8 | 106.4 | 116.1 | 94.7 | 56 | 63.4 | 271.8 | 343.9 | 387.5 | 62 | 274 | 49.8 | 76.9 | 49.3 | 327.3 | 372.5 | 292.8 | 408.8 | 339.5 | 487.8 | 444.6
2564.1 | 2325.1 | -5.8 | 0 | 0 | 354.8 | 325.5 | 283.8 | 279.7 | 48 | 54.2 | 16.3 | 89.5 | 4.9 | 245.3 | 8 | 151.9 | 67.2 | 60.9 | 71.3 | 63.3 | 70.7 | 100.6 | 105.9 | 116.2 | 94.6 | 55.9 | 63.1 | 271.8 | 343.9 | 387.2 | 61.9 | 273.9 | 49.8 | 76.8 | 48.8 | 327.1 | 372.1 | 292.5 | 408.6 | 339.2 | 487.3 | 444.4
2565.1 | 2326.1 | -5.7 | 0 | 0 | 354.6 | 324.7 | 283.7 | 279.4 | 48.7 | 54.2 | 16.3 | 89.4 | 5.4 | 227.2 | 6.8 | 151.1 | 67.2 | 60.6 | 71.1 | 63.1 | 70.5 | 100 | 105 | 116.9 | 94.7 | 55.8 | 63.1 | 271.4 | 343.9 | 386.9 | 61.8 | 274 | 49.7 | 76.8 | 48.7 | 327 | 371.9 | 292.2 | 408.4 | 338.9 | 486.9 | 444.1
2566.1 | 2327.1 | -5.7 | 0 | 0 | 354.3 | 324.3 | 283.6 | 278.8 | 47.1 | 54.2 | 16.3 | 89.3 | 6.3 | 217.1 | 6.8 | 150.4 | 67.2 | 60.6 | 71.1 | 62.9 | 70.1 | 100.1 | 105 | 117.3 | 94.7 | 55.7 | 63.5 | 271.3 | 343.4 | 386.7 | 61.7 | 273.9 | 50 | 76.6 | 48.2 | 326.7 | 371.2 | 292 | 408.3 | 338.6 | 486.4 | 443.9
2567.1 | 2328.1 | -5.7 | 0 | 0 | 354.1 | 324.2 | 283.5 | 278.3 | 48.9 | 54.2 | 16.3 | 89.2 | 6.5 | 229 | 7.8 | 149.7 | 66.5 | 60.8 | 70.9 | 62.7 | 69.9 | 99.4 | 105.1 | 117.8 | 94.7 | 55.6 | 63.3 | 271.4 | 342.9 | 386.4 | 61.8 | 273.8 | 49.8 | 76.6 | 47.6 | 326.5 | 370.4 | 291.7 | 408.2 | 338.3 | 485.9 | 443.6
2568.1 | 2329.1 | -5.8 | 0 | 0 | 353.9 | 323.9 | 283.4 | 277.7 | 48 | 54.2 | 16.3 | 89 | 5.7 | 233.1 | 7.8 | 148.9 | 65.9 | 61 | 70.8 | 62.6 | 69.9 | 99 | 104.7 | 118.2 | 95.3 | 55.5 | 63.4 | 270.5 | 342.5 | 386.1 | 61.7 | 273.5 | 49.8 | 76.4 | 47.4 | 326.4 | 370.2 | 291.4 | 408.1 | 338.1 | 485.5 | 443.4
2569.1 | 2330.1 | -6.1 | 0 | 0 | 353.4 | 323.4 | 283.1 | 277.1 | 47.6 | 54.2 | 16.3 | 88.9 | 4.3 | 205 | 7.5 | 148.2 | 65.8 | 61.1 | 70.7 | 62.4 | 69.7 | 98.7 | 104.3 | 118.7 | 95.6 | 55.3 | 63.5 | 269.8 | 341.9 | 385.9 | 61.8 | 273.3 | 49.6 | 76.4 | 47.7 | 326.1 | 369.6 | 291.2 | 408 | 337.8 | 485 | 443.2
2570.1 | 2331.1 | -6.1 | 0 | 0 | 353 | 322.3 | 282.9 | 276.6 | 48.7 | 54.1 | 16.3 | 88.8 | 4.8 | 221.5 | 7.9 | 147.5 | 65.7 | 61.2 | 70.5 | 62.2 | 69.7 | 98.6 | 104.3 | 119.2 | 96.1 | 55.2 | 63.4 | 269.4 | 341.8 | 385.6 | 61.6 | 273.2 | 49.9 | 76.4 | 48.1 | 325.9 | 369.8 | 290.8 | 407.9 | 337.5 | 484.6 | 442.9
2571.1 | 2332.1 | -6.1 | 0 | 0 | 352.7 | 321.2 | 282.6 | 276.2 | 48.5 | 54 | 16.3 | 88.7 | 4.8 | 216.4 | 13.2 | 146.8 | 65.3 | 61 | 70.4 | 62 | 69.7 | 98.1 | 104.9 | 119.2 | 96.1 | 55.1 | 63.3 | 269.5 | 341.6 | 385.4 | 61.4 | 273 | 50.4 | 76.3 | 48.5 | 325.7 | 370.1 | 290.5 | 407.8 | 337.2 | 484.1 | 442.7
2572.1 | 2333.1 | -6 | 0 | 0 | 352 | 320.2 | 282.3 | 275.9 | 47.2 | 54 | 16.3 | 88.7 | 5.1 | 216.8 | 13.3 | 146.1 | 64.8 | 61.1 | 70.2 | 61.8 | 69.7 | 98 | 104.5 | 119.4 | 95.8 | 54.9 | 63.2 | 269.2 | 341.3 | 385.2 | 61.4 | 272.6 | 50.7 | 76.2 | 49 | 325.5 | 370 | 290.3 | 407.6 | 336.9 | 483.6 | 442.4
2573.1 | 2334.1 | -5.6 | 0 | 0 | 351.3 | 319.5 | 282 | 275.7 | 44.6 | 54 | 16.3 | 88.7 | 4.7 | 211.2 | 12.1 | 145.4 | 64.2 | 61 | 70.1 | 61.6 | 69.7 | 97.9 | 104.2 | 118.2 | 95.8 | 54.8 | 63.1 | 269.4 | 340.3 | 384.9 | 61.4 | 272.5 | 49.9 | 76.1 | 48.6 | 325.3 | 369.7 | 290 | 407.5 | 336.6 | 483.2 | 442.2
2574.1 | 2335.1 | -5 | 0 | 0 | 350.9 | 319.2 | 281.7 | 275.4 | 44.2 | 53.9 | 16.3 | 88.6 | 5.2 | 215.9 | 10.8 | 144.8 | 63.2 | 61 | 70 | 61.4 | 69.6 | 98.2 | 103.6 | 118.8 | 96.1 | 54.7 | 63.1 | 269.4 | 340.5 | 384.7 | 61.3 | 272.2 | 49.9 | 76.4 | 48.6 | 325.1 | 370.1 | 289.7 | 407.5 | 336.3 | 482.7 | 442
2575.1 | 2336.1 | -4.9 | 0 | 0 | 350.5 | 319.1 | 281.3 | 275 | 43.8 | 53.7 | 16.3 | 88.6 | 5.5 | 211.4 | 10.3 | 144.1 | 62.3 | 60.9 | 69.9 | 61.2 | 69.6 | 97.8 | 103.7 | 118.8 | 95.6 | 54.6 | 63 | 269.2 | 340.2 | 384.4 | 61.3 | 272.1 | 50.6 | 76.4 | 48.3 | 324.9 | 369.7 | 289.5 | 407.4 | 336 | 482.2 | 441.7
2576.1 | 2337.1 | -5.1 | 0 | 0 | 350.5 | 319.1 | 281 | 274.4 | 41.8 | 53.7 | 16.3 | 88.5 | 5.8 | 210.8 | 10.6 | 143.4 | 62 | 60.4 | 69.8 | 61 | 69.6 | 97.8 | 103.7 | 117.3 | 95.4 | 54.5 | 62.8 | 269.7 | 340 | 384.2 | 61.2 | 271.9 | 51.1 | 76.3 | 48.1 | 324.7 | 369 | 289.2 | 407.4 | 335.7 | 481.8 | 441.5
2577.1 | 2338.1 | -5.5 | 0 | 0 | 350.5 | 319.2 | 280.8 | 274 | 44.1 | 53.5 | 16.3 | 88.4 | 6.2 | 215.7 | 12.2 | 142.7 | 61.6 | 60.1 | 69.7 | 60.8 | 69.6 | 97.8 | 103.3 | 115.9 | 95.9 | 54.4 | 62.7 | 269.7 | 340 | 383.9 | 61.3 | 271.7 | 50.7 | 76.2 | 47.8 | 324.5 | 368.5 | 289 | 407.5 | 335.4 | 481.3 | 441.3
2578.1 | 2339.1 | -5.7 | 0 | 0 | 350.4 | 318.9 | 280.5 | 273.6 | 45.9 | 53.5 | 16.3 | 88.2 | 7.4 | 220.3 | 11.9 | 142.1 | 61.1 | 59.8 | 69.6 | 60.6 | 69.6 | 97.4 | 103.3 | 115.9 | 95.9 | 54.2 | 62.7 | 269.1 | 339.5 | 383.7 | 61.4 | 271.5 | 51 | 76 | 48.5 | 324.3 | 367.9 | 288.7 | 407.5 | 335.1 | 480.9 | 441
2579.1 | 2340.1 | -5.8 | 0 | 0 | 350.1 | 318.7 | 280.3 | 273.2 | 45 | 53.5 | 16.3 | 88.1 | 6.4 | 215.2 | 12.3 | 141.4 | 60.3 | 59.3 | 69.5 | 60.5 | 69.5 | 97.1 | 102.8 | 115.7 | 96.3 | 54.1 | 62.5 | 269 | 339.4 | 383.4 | 61.2 | 271.5 | 50.8 | 75.9 | 48.6 | 324.1 | 366.7 | 288.4 | 407.6 | 334.8 | 480.4 | 440.8
2580.1 | 2341.1 | -6.1 | 0 | 0 | 349.8 | 318.5 | 280 | 272.7 | 41.9 | 53.4 | 16.3 | 88.1 | 5.1 | 237.8 | 10.5 | 140.8 | 60.1 | 59.1 | 69.4 | 60.3 | 69.5 | 96.7 | 102.8 | 116.9 | 96.9 | 53.9 | 62.3 | 269.5 | 339.5 | 383.1 | 61.1 | 271.6 | 51 | 75.9 | 48.4 | 323.9 | 366.6 | 288 | 407.6 | 334.5 | 479.9 | 440.6
2581.1 | 2342.1 | -6.3 | 0 | 0 | 349.7 | 318.2 | 279.7 | 272.3 | 40.8 | 53.3 | 16.3 | 88 | 5.2 | 243 | 8.2 | 140.1 | 60.2 | 58.8 | 69.3 | 60.2 | 69.3 | 96.7 | 102.1 | 116.9 | 96.7 | 53.8 | 62.2 | 269.9 | 339 | 382.8 | 61.1 | 271.2 | 50.7 | 75.8 | 48.8 | 323.7 | 367.1 | 287.7 | 407.8 | 334.2 | 479.5 | 440.3
2582.1 | 2343.1 | -6.2 | 0 | 0 | 349.4 | 317.3 | 279.4 | 271.9 | 43.4 | 53.2 | 16.3 | 87.9 | 4.5 | 252.9 | 7.5 | 139.5 | 59.7 | 58.6 | 69.1 | 60.1 | 69 | 96.5 | 102 | 116.2 | 96.8 | 53.7 | 61.9 | 270 | 338.6 | 382.5 | 61 | 270.7 | 50.8 | 75.8 | 48.1 | 323.5 | 367.7 | 287.4 | 407.8 | 333.9 | 479 | 440.1
2583.1 | 2344.1 | -6.1 | 0 | 0 | 349.2 | 316.9 | 279.1 | 271.6 | 42.3 | 53 | 16.3 | 87.8 | 4.4 | 221.1 | 8.4 | 138.9 | 59.3 | 58.3 | 69 | 60 | 68.8 | 96.2 | 101.8 | 117.6 | 96.4 | 53.6 | 61.7 | 269.1 | 338.3 | 382.3 | 61.1 | 270 | 51 | 75.8 | 48.5 | 323.4 | 367.5 | 287 | 407.8 | 333.6 | 478.6 | 439.8
2584.1 | 2345.1 | -6 | 0 | 0 | 348.7 | 316.9 | 278.7 | 271.2 | 38.9 | 52.9 | 16.4 | 87.7 | 4.9 | 180.8 | 7 | 138.2 | 59.3 | 57.9 | 68.9 | 60.1 | 68.7 | 95.5 | 101.4 | 118.2 | 96.4 | 53.4 | 61.7 | 268.7 | 338.4 | 382.1 | 61 | 269.5 | 50.5 | 75.8 | 48.5 | 323.2 | 367.6 | 286.7 | 407.9 | 333.3 | 478.1 | 439.6
2585.1 | 2346.1 | -5.9 | 0 | 0 | 348.4 | 316.5 | 278.4 | 270.8 | 39.1 | 52.8 | 16.4 | 87.6 | 4.5 | 242.3 | 6.4 | 137.6 | 59.1 | 57.7 | 68.7 | 60.1 | 68.8 | 95.5 | 101.2 | 118.3 | 97.1 | 53.3 | 61.5 | 268.8 | 338.2 | 381.8 | 61.1 | 268.9 | 50.6 | 75.6 | 47.5 | 323 | 367.3 | 286.4 | 407.9 | 333.1 | 477.7 | 439.4
2586.1 | 2347.1 | -5.8 | 0 | 0 | 348.1 | 315.7 | 278 | 270.4 | 38.5 | 52.8 | 16.4 | 87.6 | 4.8 | 246.6 | 7 | 137 | 58.7 | 57.4 | 68.4 | 60.1 | 68.7 | 95.1 | 100.7 | 117.9 | 97.7 | 53.2 | 61.4 | 268.3 | 338 | 381.6 | 61.1 | 268.5 | 50 | 75.5 | 47 | 322.8 | 367.3 | 286.1 | 408 | 332.8 | 477.2 | 439.1
2587.1 | 2348.1 | -5.8 | 0 | 0 | 347.7 | 315.1 | 277.8 | 269.9 | 40.8 | 52.7 | 16.4 | 87.6 | 4.1 | 204.8 | 9.3 | 136.4 | 58.7 | 57.1 | 68.2 | 60.1 | 68.7 | 94.9 | 100.4 | 115.2 | 97.7 | 53 | 61.3 | 267.9 | 337.6 | 381.3 | 61 | 268.3 | 50.7 | 75.3 | 46.4 | 322.6 | 367.1 | 285.8 | 408 | 332.5 | 476.8 | 438.9
2588.1 | 2349.1 | -5.5 | 0 | 0 | 347.2 | 314.6 | 277.5 | 269.6 | 42.4 | 52.7 | 16.4 | 87.5 | 4.2 | 207.7 | 12 | 135.8 | 58.2 | 56.8 | 68 | 60.1 | 68.7 | 95.1 | 99.9 | 116.1 | 97.3 | 52.9 | 61.2 | 267.7 | 336.9 | 381.1 | 61 | 267.8 | 50 | 75.2 | 46.7 | 322.4 | 366.5 | 285.5 | 408 | 332.2 | 476.3 | 438.6
2589.1 | 2350.1 | -5.3 | 0 | 0 | 346.7 | 314 | 277.1 | 269.4 | 42.8 | 52.7 | 16.4 | 87.3 | 4.5 | 211 | 12.6 | 135.2 | 57.7 | 56.5 | 67.9 | 60.1 | 68.8 | 94.5 | 99.7 | 116.9 | 97 | 52.8 | 61 | 267.3 | 336.6 | 380.8 | 60.9 | 267.2 | 50 | 75.3 | 47.7 | 322.2 | 366.3 | 285.1 | 408 | 331.9 | 475.9 | 438.4
2590.1 | 2351.1 | -5.4 | 0 | 0 | 346 | 313.3 | 276.7 | 269.4 | 42.9 | 52.7 | 16.4 | 87.3 | 4.7 | 214.6 | 11.7 | 134.6 | 57.2 | 56.4 | 67.7 | 60.1 | 68.9 | 94.2 | 99.8 | 118 | 97.5 | 52.6 | 60.9 | 267.1 | 336.3 | 380.6 | 60.9 | 266.9 | 50.3 | 75.1 | 47.3 | 322 | 366.6 | 284.8 | 407.9 | 331.7 | 475.4 | 438.2
2591.1 | 2352.1 | -5.5 | 0 | 0 | 345.2 | 312.7 | 276.3 | 269.3 | 42.4 | 52.7 | 16.4 | 87.2 | 4.3 | 213.1 | 13.3 | 134 | 57.1 | 56.5 | 67.6 | 60.1 | 69 | 94 | 99.4 | 118.5 | 97.7 | 52.5 | 60.8 | 266.9 | 335.7 | 380.4 | 60.7 | 266.4 | 50.2 | 75 | 46.7 | 321.8 | 366.6 | 284.4 | 407.8 | 331.4 | 475 | 437.9
2592.1 | 2353.1 | -5.8 | 0 | 0 | 344.9 | 312.2 | 275.9 | 269 | 42.7 | 52.7 | 16.4 | 87 | 4.6 | 213.6 | 13.7 | 133.4 | 57 | 56.6 | 67.5 | 60.1 | 69 | 93.7 | 99 | 119 | 98.4 | 52.4 | 60.4 | 266.2 | 335.7 | 380.1 | 60.7 | 266 | 49.9 | 75 | 46.3 | 321.6 | 366.8 | 284 | 407.7 | 331.1 | 474.5 | 437.7
2593.1 | 2354.1 | -5.7 | 0 | 0 | 344.9 | 312 | 275.8 | 268.8 | 41 | 52.6 | 16.4 | 87 | 4.6 | 203.5 | 12.9 | 132.9 | 57 | 56.7 | 67.4 | 60 | 68.9 | 93.3 | 98.9 | 119.2 | 98.9 | 52.2 | 59.9 | 266.2 | 335.3 | 379.9 | 60.8 | 265.6 | 49.8 | 74.8 | 46.9 | 321.4 | 367 | 283.7 | 407.6 | 330.8 | 474.1 | 437.4
2594.1 | 2355.1 | -5.4 | 0 | 0 | 344.6 | 311.5 | 275.5 | 268.6 | 39.5 | 52.5 | 16.4 | 87 | 4.7 | 202.3 | 11.6 | 132.3 | 57.1 | 56.8 | 67.3 | 60 | 68.9 | 92.7 | 98.3 | 119.2 | 98.8 | 52.1 | 59.4 | 266.1 | 335 | 379.6 | 60.8 | 265.3 | 49.5 | 74.7 | 47.4 | 321.2 | 366.5 | 283.3 | 407.5 | 330.5 | 473.7 | 437.2
2595.1 | 2356.1 | -5.5 | 0 | 0 | 344.2 | 311 | 275.4 | 268.4 | 39.5 | 52.4 | 16.4 | 86.9 | 4.5 | 204.1 | 10.7 | 131.8 | 56.6 | 56.9 | 67.3 | 59.9 | 68.9 | 92.3 | 97.6 | 119.2 | 98.8 | 52 | 58.9 | 266.1 | 334.5 | 379.4 | 60.7 | 264.4 | 49.7 | 74.7 | 47.5 | 321 | 366.6 | 283 | 407.5 | 330.2 | 473.2 | 437
2596.1 | 2357.1 | -5.6 | 0 | 0 | 343.9 | 310.6 | 275.3 | 268.2 | 38 | 52.3 | 16.4 | 86.9 | 4.6 | 215.8 | 10.8 | 131.3 | 56.2 | 56.8 | 67.2 | 59.8 | 68.9 | 91.8 | 97.7 | 119.4 | 98.7 | 51.8 | 58.5 | 266.2 | 334.2 | 379.2 | 60.5 | 263.2 | 49.6 | 74.6 | 47.7 | 320.8 | 367 | 282.6 | 407.4 | 330 | 472.8 | 436.7
2597.1 | 2358.1 | -5.5 | 0 | 0 | 343.7 | 309.9 | 275.1 | 268 | 38 | 52.3 | 16.4 | 86.9 | 4.7 | 226.3 | 11.3 | 130.7 | 56 | 56.8 | 67.1 | 59.7 | 68.8 | 91.4 | 97.5 | 119.4 | 99.3 | 51.7 | 58 | 266.2 | 333.8 | 378.9 | 60.5 | 262.1 | 49.8 | 74.6 | 48.2 | 320.6 | 367.2 | 282.3 | 407.4 | 329.7 | 472.4 | 436.5
2598.1 | 2359.1 | -5.4 | 0 | 0 | 343.8 | 309.4 | 274.9 | 267.8 | 38.1 | 52.2 | 16.4 | 86.9 | 4.5 | 259.9 | 9.5 | 130.2 | 56 | 56.9 | 67.1 | 59.7 | 68.8 | 91.2 | 97.1 | 119.3 | 99.5 | 51.6 | 57.6 | 266.3 | 333.5 | 378.7 | 60.4 | 261.3 | 48.8 | 74.3 | 47.1 | 320.5 | 367.2 | 282 | 407.5 | 329.4 | 471.9 | 436.3
2599.1 | 2360.1 | -5.5 | 0 | 0 | 343.4 | 309.1 | 274.6 | 267.5 | 38.7 | 52.1 | 16.4 | 86.9 | 4.1 | 221.3 | 8 | 129.7 | 55.7 | 56.9 | 67 | 59.7 | 68.7 | 91.1 | 96.5 | 119.3 | 100.1 | 51.4 | 57.5 | 266.7 | 332.8 | 378.5 | 60.5 | 260.8 | 49.4 | 74.1 | 47.1 | 320.3 | 367 | 281.6 | 407.5 | 329.1 | 471.5 | 436
2600.1 | 2361.1 | -5.6 | 0 | 0 | 343 | 308.6 | 274.3 | 267.2 | 38.4 | 52.1 | 16.4 | 86.8 | 4.4 | 240.3 | 8.1 | 129.1 | 55.2 | 56.9 | 66.9 | 59.6 | 68.7 | 90.5 | 96.2 | 119 | 100.3 | 51.3 | 57.2 | 266.7 | 332.7 | 378.2 | 60.4 | 260.1 | 49.2 | 74 | 47.9 | 320.1 | 366.8 | 281.3 | 407.5 | 328.8 | 471 | 435.8
2601.1 | 2362.1 | -5.6 | 0 | 0 | 342.9 | 308.4 | 274.1 | 266.8 | 36.4 | 52.1 | 16.4 | 86.7 | 4.2 | 220.1 | 7.6 | 128.6 | 54.7 | 56.8 | 66.8 | 59.6 | 68.7 | 90.4 | 95.8 | 118.6 | 100.7 | 51.1 | 57 | 266.2 | 332.4 | 378 | 60.3 | 259.4 | 49.2 | 73.8 | 48.4 | 319.9 | 366.7 | 281.1 | 407.4 | 328.5 | 470.6 | 435.6
2602.1 | 2363.1 | -5.7 | 0 | 0 | 343.1 | 307.7 | 273.8 | 266.5 | 38.2 | 52 | 16.4 | 86.6 | 4.6 | 219.7 | 7.4 | 128.1 | 55 | 56.9 | 66.8 | 59.5 | 68.6 | 90.1 | 95.5 | 118.5 | 100.8 | 51 | 56.7 | 265.5 | 332.1 | 377.8 | 60.3 | 259 | 49.1 | 73.7 | 48.3 | 319.7 | 365.4 | 280.8 | 407.3 | 328.3 | 470.2 | 435.3
2603.1 | 2364.1 | -5.8 | 0 | 0 | 342.7 | 307.2 | 273.5 | 266.3 | 38.5 | 52 | 16.5 | 86.5 | 4.5 | 230.1 | 6.8 | 127.5 | 55 | 56.7 | 66.7 | 59.5 | 68.6 | 89.7 | 95.2 | 118.2 | 100.4 | 50.9 | 56.8 | 265.8 | 331.8 | 377.5 | 60.2 | 258.6 | 49 | 73.6 | 48.3 | 319.5 | 364.1 | 280.5 | 407.3 | 328 | 469.7 | 435.1
2604.1 | 2365.1 | -5.7 | 0 | 0 | 342.5 | 306.8 | 273.3 | 266.2 | 38.2 | 51.9 | 16.5 | 86.5 | 4.3 | 191.5 | 6.4 | 127 | 55.1 | 56.5 | 66.6 | 59.3 | 68.5 | 89.3 | 94.8 | 118.5 | 100.7 | 50.8 | 56.6 | 266.1 | 331.5 | 377.3 | 60.1 | 258.3 | 48.9 | 73.5 | 48.5 | 319.3 | 363 | 280.2 | 407.2 | 327.7 | 469.3 | 434.8
2605.1 | 2366.1 | -5.6 | 0 | 0 | 342.1 | 306.9 | 272.9 | 265.9 | 40.5 | 51.8 | 16.5 | 86.5 | 4.4 | 215 | 4.6 | 126.5 | 55.5 | 56.6 | 66.5 | 59.2 | 68.5 | 89 | 94.5 | 118.5 | 101.3 | 50.7 | 56.5 | 265.6 | 330.7 | 377.1 | 59.9 | 258.2 | 48.9 | 73.5 | 48 | 319.2 | 362.9 | 279.9 | 407.2 | 327.4 | 468.9 | 434.6
2606.1 | 2367.1 | -5.4 | 0 | 0 | 341.8 | 306.6 | 272.5 | 265.6 | 40.9 | 51.8 | 16.5 | 86.4 | 4.4 | 243.1 | 4.3 | 125.9 | 55.8 | 56.6 | 66.5 | 59.1 | 68.5 | 88.6 | 94 | 118.4 | 101.8 | 50.6 | 56.5 | 265.9 | 330.4 | 376.8 | 59.8 | 255.2 | 49.6 | 73.5 | 47.4 | 319 | 362.9 | 279.6 | 407.1 | 327.2 | 468.4 | 434.4
2607.1 | 2368.1 | -5.3 | 0 | 0 | 341.3 | 305.7 | 272.1 | 265.3 | 37.3 | 51.7 | 16.5 | 86.4 | 4.2 | 225.8 | 4.6 | 125.4 | 55.5 | 56.5 | 66.4 | 59 | 68.4 | 88.2 | 93.7 | 118.4 | 101.9 | 50.5 | 56.3 | 266.7 | 330.4 | 376.6 | 59.8 | 245 | 50 | 73.4 | 47.1 | 318.8 | 363.3 | 279.4 | 407.1 | 326.9 | 468 | 434.2
2608.1 | 2369.1 | -5.4 | 0 | 0 | 340.7 | 305.3 | 271.8 | 265.1 | 35.4 | 51.7 | 16.5 | 86.4 | 4.3 | 212.4 | 5.6 | 124.9 | 54.9 | 56.4 | 66.4 | 59 | 68.3 | 87.9 | 93.4 | 118.1 | 101.4 | 50.4 | 56.3 | 267.6 | 330.4 | 376.3 | 59.7 | 238 | 49.8 | 73.4 | 47.2 | 318.6 | 362.8 | 279.1 | 407 | 326.6 | 467.6 | 433.9
2609.1 | 2370.1 | -5.5 | 0 | 0 | 340.3 | 305.1 | 271.5 | 265 | 35.9 | 51.7 | 16.5 | 86.4 | 4.2 | 211.2 | 6.7 | 124.4 | 55.1 | 56.2 | 66.5 | 58.9 | 68.3 | 87.8 | 93.3 | 117.8 | 101.7 | 50.3 | 56 | 268.2 | 330 | 376.1 | 59.7 | 234 | 49.8 | 73.3 | 47.2 | 318.4 | 362.2 | 278.8 | 406.9 | 326.4 | 467.2 | 433.7
2610.1 | 2371.1 | -5.4 | 0 | 0 | 340 | 304.6 | 271.3 | 264.8 | 38.3 | 51.7 | 16.5 | 86.4 | 4.6 | 215.1 | 7.2 | 123.9 | 55.1 | 56.1 | 66.6 | 58.8 | 68.3 | 87.7 | 93 | 116.7 | 101.1 | 50.2 | 56.2 | 267.9 | 329.5 | 375.9 | 59.6 | 232.5 | 49.6 | 73.4 | 47.8 | 318.3 | 361.3 | 278.4 | 406.8 | 326.1 | 466.7 | 433.5
2611.1 | 2372.1 | -5.2 | 0 | 0 | 339.9 | 304.2 | 271 | 264.6 | 39.3 | 51.7 | 16.5 | 86.3 | 4.5 | 227.3 | 8.1 | 123.4 | 54.5 | 56.1 | 66.6 | 58.7 | 68.4 | 87.6 | 92.6 | 117.3 | 101.4 | 50.1 | 56 | 267.6 | 329.7 | 375.6 | 59.5 | 234.8 | 50.4 | 73.4 | 47.7 | 318.1 | 361.4 | 278.2 | 406.7 | 325.8 | 466.3 | 433.2
2612.1 | 2373.1 | -5.3 | 0 | 0 | 339.7 | 303.9 | 270.6 | 264.4 | 38.5 | 51.7 | 16.5 | 86.3 | 4 | 234.4 | 7.5 | 122.9 | 54 | 55.9 | 66.5 | 58.6 | 68.3 | 87.2 | 91.8 | 117.4 | 101.5 | 50 | 56.2 | 268.1 | 328.9 | 375.4 | 59.5 | 238 | 50.2 | 73.3 | 47.1 | 317.9 | 360.9 | 277.9 | 406.6 | 325.5 | 465.9 | 433
2613.1 | 2374.1 | -5.4 | 0 | 0 | 339.5 | 303.1 | 270.4 | 264.1 | 39.2 | 51.6 | 16.5 | 86.3 | 4.3 | 254.5 | 6.5 | 122.3 | 53.6 | 56 | 66.5 | 58.5 | 68.2 | 86.8 | 91.3 | 117.1 | 101.5 | 49.9 | 56 | 267.8 | 328.7 | 375.2 | 59.3 | 241.1 | 50 | 73.3 | 47.3 | 317.7 | 360.6 | 277.6 | 406.5 | 325.2 | 465.4 | 432.7
2614.1 | 2375.1 | -5.4 | 0 | 0 | 339.2 | 302.9 | 270.2 | 263.8 | 39.2 | 51.6 | 16.5 | 86.3 | 4.7 | 244.3 | 6.9 | 121.8 | 53 | 56 | 66.5 | 58.4 | 68.2 | 86.4 | 91.2 | 116.2 | 101.2 | 49.8 | 56 | 268.2 | 328.3 | 374.9 | 59.3 | 243.5 | 50.1 | 73.3 | 48 | 317.5 | 360.3 | 277.4 | 406.4 | 325 | 465 | 432.5
2615.1 | 2376.1 | -5.4 | 0 | 0 | 338.8 | 302.6 | 269.9 | 263.4 | 36.6 | 51.6 | 16.5 | 86.2 | 4.6 | 240.2 | 8.1 | 121.3 | 52.6 | 55.8 | 66.4 | 58.3 | 68.3 | 85.9 | 90.7 | 116.5 | 101.4 | 49.7 | 55.9 | 268.6 | 327.8 | 374.7 | 59.2 | 245.8 | 50.4 | 73.2 | 48 | 317.3 | 360.5 | 277.1 | 406.3 | 324.7 | 464.6 | 432.3
2616.1 | 2377.1 | -5.4 | 0 | 0 | 338.7 | 302.1 | 269.6 | 263.1 | 38.1 | 51.5 | 16.5 | 86 | 4.7 | 240.6 | 7.8 | 120.8 | 52.2 | 55.7 | 66.3 | 58.2 | 68.3 | 85.8 | 90.7 | 116.7 | 101.4 | 49.6 | 55.9 | 268.8 | 327.8 | 374.5 | 59.2 | 247.8 | 50.5 | 73.1 | 47.1 | 317.1 | 361 | 276.9 | 406.2 | 324.4 | 464.2 | 432
2617.1 | 2378.1 | -5.3 | 0 | 0 | 338.2 | 301.8 | 269.3 | 263 | 38.3 | 51.5 | 16.5 | 85.9 | 4.7 | 272.1 | 7.4 | 120.3 | 51.4 | 55.5 | 66.2 | 58.1 | 68.4 | 85.9 | 90.4 | 116.8 | 101.2 | 49.6 | 55.7 | 268.1 | 327.3 | 374.3 | 59.1 | 249.4 | 50.5 | 73 | 47.9 | 317 | 361 | 276.7 | 406.1 | 324.2 | 463.8 | 431.8
2618.1 | 2379.1 | -5.4 | 0 | 0 | 337.8 | 301.6 | 269 | 262.7 | 36.5 | 51.5 | 16.5 | 85.8 | 4.9 | 247.2 | 7.6 | 119.8 | 50.5 | 55.5 | 66.1 | 58 | 68.3 | 85.3 | 90.2 | 117.1 | 101.6 | 49.4 | 55.8 | 267.1 | 326.8 | 374 | 58.9 | 250.7 | 50.1 | 72.8 | 47.5 | 316.8 | 361.2 | 276.4 | 406.1 | 323.9 | 463.3 | 431.6
2619.1 | 2380.1 | -5.4 | 0 | 0 | 337.2 | 301.1 | 268.8 | 262.4 | 37.4 | 51.4 | 16.5 | 85.7 | 4.9 | 242.2 | 8.5 | 119.3 | 50.2 | 55.3 | 65.9 | 57.9 | 68.2 | 84.7 | 89.9 | 117.2 | 101.7 | 49.4 | 55.7 | 267.3 | 326 | 373.8 | 58.9 | 251.5 | 49.2 | 72.6 | 47 | 316.6 | 361 | 276.1 | 406.1 | 323.7 | 462.9 | 431.3
2620.1 | 2381.1 | -5.5 | 0 | 0 | 336.4 | 301.1 | 268.6 | 262.1 | 37 | 51.3 | 16.5 | 85.6 | 5 | 237.5 | 8.6 | 118.9 | 50.2 | 55.3 | 65.7 | 57.8 | 68 | 84.5 | 89.3 | 117.1 | 102.2 | 49.3 | 55.8 | 267.4 | 325.8 | 373.5 | 58.8 | 252.2 | 49.5 | 72.6 | 48 | 316.4 | 360.2 | 275.9 | 406.2 | 323.4 | 462.5 | 431.1
2621.1 | 2382.1 | -5.4 | 0 | 0 | 335.8 | 300.9 | 268.3 | 261.6 | 35.4 | 51.3 | 16.6 | 85.4 | 4.2 | 229 | 7.9 | 118.4 | 50.1 | 55.2 | 65.5 | 57.7 | 68 | 84.1 | 89 | 117 | 101.7 | 49.2 | 55.6 | 267.3 | 325.3 | 373.3 | 58.8 | 252.5 | 49.3 | 72.5 | 48.5 | 316.2 | 360.1 | 275.6 | 406.2 | 323.2 | 462.1 | 430.9
2622.1 | 2383.1 | -5.5 | 0 | 0 | 335.7 | 301 | 268 | 261.2 | 38.7 | 51.2 | 16.6 | 85.4 | 4.5 | 219.7 | 6.9 | 117.9 | 50.2 | 55 | 65.4 | 57.6 | 67.9 | 83.8 | 89 | 116.9 | 101.9 | 49.1 | 55.5 | 267.6 | 325.4 | 373.1 | 59 | 252.5 | 49.4 | 72.4 | 48.3 | 316.1 | 359.3 | 275.3 | 406.3 | 322.9 | 461.7 | 430.7
2623.1 | 2384.1 | -5.5 | 0 | 0 | 335.4 | 300.9 | 267.7 | 260.9 | 39.5 | 51.2 | 16.6 | 85.3 | 5.4 | 226.8 | 5.9 | 117.4 | 50 | 55 | 65.2 | 57.6 | 67.8 | 83.5 | 88.3 | 116.4 | 102.1 | 49 | 55.6 | 268.1 | 325.4 | 372.9 | 58.8 | 252.5 | 49.7 | 72.3 | 48.2 | 315.9 | 358.5 | 275 | 406.4 | 322.6 | 461.3 | 430.4
2624.1 | 2385.1 | -5.6 | 0 | 0 | 334.9 | 300.3 | 267.6 | 260.6 | 38.8 | 51.2 | 16.6 | 85.2 | 5.4 | 254 | 5.4 | 116.9 | 49.7 | 54.6 | 65.1 | 57.5 | 67.8 | 83.1 | 87.8 | 116.5 | 102.2 | 48.9 | 55.5 | 268 | 325.3 | 372.6 | 59 | 252.4 | 49.4 | 72 | 48.3 | 315.7 | 358.5 | 274.7 | 406.5 | 322.4 | 460.8 | 430.2
2625.1 | 2386.1 | -5.7 | 0 | 0 | 334.4 | 300.2 | 267.4 | 260.4 | 38.7 | 51.2 | 16.6 | 85.1 | 5.5 | 241.7 | 5.4 | 116.4 | 49.3 | 54.4 | 65 | 57.4 | 67.7 | 82.7 | 88 | 116.7 | 102.1 | 48.8 | 55.3 | 268.3 | 324.7 | 372.4 | 58.9 | 252.3 | 49.4 | 71.9 | 47.9 | 315.5 | 358.9 | 274.4 | 406.5 | 322.1 | 460.4 | 429.9
2626.1 | 2387.1 | -5.7 | 0 | 0 | 333.8 | 300 | 267.2 | 260.2 | 38.1 | 51.2 | 16.6 | 85.1 | 4.7 | 231 | 5.1 | 115.9 | 49.3 | 52.4 | 65 | 57.4 | 67.6 | 82.5 | 88 | 116.6 | 101.9 | 48.7 | 55.3 | 268.6 | 324.7 | 372.1 | 58.7 | 252.2 | 49.4 | 71.8 | 48.3 | 315.4 | 359.1 | 274.1 | 406.5 | 321.9 | 460 | 429.7
2627.1 | 2388.1 | -5.7 | 0 | 0 | 333.5 | 299.7 | 267 | 259.9 | 37.7 | 51.1 | 16.6 | 85.1 | 4.7 | 210.7 | 5.2 | 115.4 | 49.4 | 50.8 | 65 | 57.4 | 67.5 | 82 | 87.9 | 116.6 | 101.4 | 48.6 | 55.3 | 268.1 | 324.3 | 371.9 | 58.7 | 252.5 | 49.3 | 71.7 | 48.3 | 315.2 | 359.3 | 273.8 | 406.5 | 321.6 | 459.6 | 429.5
2628.1 | 2389.1 | -5.8 | 0 | 0 | 333.4 | 299.2 | 266.9 | 259.6 | 39.1 | 51.1 | 16.6 | 85 | 4.5 | 216.7 | 6.6 | 114.9 | 49.2 | 50.1 | 65 | 57.4 | 67.1 | 81.8 | 87.7 | 116.5 | 101.4 | 48.6 | 55.3 | 268.3 | 324 | 371.7 | 58.7 | 252.8 | 49.1 | 71.6 | 48 | 315 | 359.1 | 273.6 | 406.4 | 321.3 | 459.2 | 429.3
2629.1 | 2390.1 | -6 | 0 | 0 | 333.4 | 299 | 266.7 | 259.3 | 37.3 | 51.1 | 16.6 | 84.9 | 3.9 | 210.9 | 8.3 | 114.4 | 49.2 | 49.3 | 64.8 | 57.4 | 66.8 | 81.2 | 87.6 | 116.3 | 101.5 | 48.5 | 55.2 | 269 | 323.4 | 371.5 | 58.5 | 253.2 | 49 | 71.6 | 48.2 | 314.8 | 358 | 273.3 | 406.3 | 321.1 | 458.8 | 429.1
2630.1 | 2391.1 | -5.8 | 0 | 0 | 333.4 | 298.7 | 266.5 | 258.9 | 35.1 | 51.1 | 16.6 | 84.8 | 3.8 | 193.2 | 8.4 | 113.9 | 48.7 | 48.4 | 64.6 | 57.3 | 66.8 | 80.6 | 86.9 | 115.9 | 101.3 | 48.4 | 55.1 | 268.7 | 322.7 | 371.2 | 58.3 | 253.7 | 49 | 71.6 | 48.1 | 314.7 | 356.6 | 273.1 | 406.2 | 320.8 | 458.4 | 428.8
2631.1 | 2392.1 | -5.8 | 0 | 0 | 333.6 | 298.2 | 266.2 | 258.6 | 36.2 | 51 | 16.6 | 84.8 | 4.3 | 203.2 | 8.6 | 113.4 | 48.1 | 48 | 64.4 | 57.2 | 66.8 | 80.3 | 86.9 | 115.8 | 100.7 | 48.3 | 54.8 | 268.4 | 322.2 | 371 | 58.2 | 254.3 | 48.5 | 71.5 | 47.7 | 314.5 | 356.3 | 272.8 | 406.1 | 320.6 | 458 | 428.6
2632.1 | 2393.1 | -5.5 | 0 | 0 | 333.6 | 297.6 | 266.1 | 258.4 | 37.7 | 51 | 16.6 | 84.7 | 4.5 | 215.9 | 9 | 113 | 48 | 47.4 | 64.4 | 57.1 | 66.8 | 80.1 | 86.8 | 115.7 | 100.9 | 48.2 | 54.8 | 268.6 | 322 | 370.8 | 58.2 | 254.6 | 49 | 71.4 | 47.8 | 314.3 | 356.1 | 272.6 | 406 | 320.3 | 457.6 | 428.3
2633.1 | 2394.1 | -5.2 | 0 | 0 | 333.4 | 297.2 | 265.8 | 258.2 | 36.2 | 51 | 16.6 | 84.6 | 4.7 | 207.5 | 8 | 112.5 | 48 | 47.6 | 64.4 | 57 | 66.8 | 79.8 | 86.7 | 115.3 | 100.6 | 48.2 | 54.9 | 268.7 | 322.2 | 370.5 | 58.2 | 254.2 | 48.9 | 71.3 | 47.8 | 314.1 | 356.3 | 272.3 | 405.9 | 320.1 | 457.2 | 428.1
2634.1 | 2395.1 | -4.9 | 0 | 0 | 333 | 296.5 | 265.6 | 258 | 36 | 50.9 | 16.6 | 84.5 | 5.5 | 246.5 | 6.1 | 112 | 47.8 | 47.9 | 64.3 | 56.9 | 66.5 | 79.6 | 86.2 | 115.1 | 100.4 | 48.1 | 54.8 | 269.1 | 322.1 | 370.3 | 58.1 | 252.1 | 49.1 | 71.4 | 47.9 | 314 | 356.2 | 272.1 | 405.8 | 319.8 | 456.8 | 427.9
2635.1 | 2396.1 | -5.1 | 0 | 0 | 332.5 | 296.5 | 265.3 | 257.7 | 36.4 | 50.9 | 16.6 | 84.4 | 4.9 | 202.7 | 6.7 | 111.5 | 48.1 | 47.7 | 64.3 | 56.8 | 66 | 79.5 | 85.7 | 115.1 | 100.2 | 48 | 54.7 | 269.4 | 322 | 370.1 | 58.1 | 249.8 | 49 | 71.3 | 48 | 313.8 | 355.8 | 271.8 | 405.7 | 319.6 | 456.4 | 427.6
2636.1 | 2397.1 | -5.4 | 0 | 0 | 332 | 296.4 | 264.9 | 257.6 | 36.2 | 50.9 | 16.6 | 84.3 | 4.8 | 203.9 | 8.2 | 111 | 48.2 | 47.4 | 64.2 | 56.7 | 65.7 | 79 | 85.7 | 114.9 | 100.3 | 47.9 | 54.7 | 269.6 | 321.4 | 369.8 | 58.1 | 248.3 | 48.6 | 71.2 | 48.2 | 313.6 | 355.6 | 271.5 | 405.7 | 319.3 | 456 | 427.4
2637.1 | 2398.1 | -5.5 | 0 | 0 | 331.6 | 296 | 264.7 | 257.3 | 37.2 | 50.8 | 16.6 | 84.2 | 4.5 | 198.5 | 9.8 | 110.5 | 48.3 | 47.1 | 64 | 56.6 | 65.6 | 78.9 | 85.8 | 114.7 | 100.4 | 47.9 | 54.9 | 269.7 | 320.7 | 369.6 | 57.9 | 247.2 | 48.2 | 71.2 | 47.5 | 313.4 | 355.2 | 271.2 | 405.7 | 319.1 | 455.6 | 427.2
2638.1 | 2399.1 | -5.8 | 0 | 0 | 331 | 295.4 | 264.4 | 257.1 | 37.9 | 50.8 | 16.7 | 84.2 | 4 | 202.4 | 9.4 | 110.1 | 48.3 | 46.9 | 63.7 | 56.6 | 65.5 | 78.7 | 85.4 | 114.6 | 99.9 | 47.8 | 55.1 | 269.3 | 320.4 | 369.4 | 57.8 | 246.3 | 48 | 71.1 | 47.5 | 313.3 | 354.9 | 271 | 405.7 | 318.8 | 455.2 | 427
2639.1 | 2400.1 | -5.7 | 0 | 0 | 330.8 | 294.7 | 264.2 | 257 | 36.6 | 50.7 | 16.7 | 84.1 | 4.1 | 208.3 | 9.5 | 109.6 | 48.4 | 46.4 | 63.5 | 56.5 | 65.3 | 78.2 | 85.1 | 114.6 | 99.5 | 47.7 | 55.2 | 269.4 | 320.1 | 369.2 | 57.9 | 245.7 | 48.1 | 70.8 | 47.4 | 313.1 | 354.8 | 270.7 | 405.6 | 318.6 | 454.8 | 426.7
2640.1 | 2401.1 | -5.7 | 0 | 0 | 330.4 | 294.2 | 263.9 | 256.8 | 36.6 | 50.7 | 16.7 | 84.1 | 4.1 | 213.7 | 9.7 | 109.1 | 48.3 | 46.3 | 63.5 | 56.4 | 65.1 | 77.9 | 84.6 | 114.5 | 98.5 | 47.6 | 55.3 | 269.9 | 319.6 | 369 | 57.9 | 245.4 | 48 | 70.7 | 47.1 | 312.9 | 355 | 270.4 | 405.7 | 318.3 | 454.4 | 426.5
2641.1 | 2402.1 | -5.5 | 0 | 0 | 329.7 | 293.8 | 263.5 | 256.6 | 38.8 | 50.7 | 16.7 | 84.1 | 3.9 | 213.5 | 9.2 | 108.7 | 48.4 | 46.1 | 63.4 | 56.4 | 65 | 77.8 | 84.3 | 114.5 | 97.9 | 47.5 | 55.4 | 270.4 | 319.4 | 368.7 | 57.8 | 245.3 | 47.8 | 70.7 | 47.3 | 312.7 | 354.2 | 270.1 | 405.7 | 318 | 454 | 426.3
2642.1 | 2403.1 | -5.4 | 0 | 0 | 329.2 | 293.6 | 263.2 | 256.4 | 36.9 | 50.6 | 16.7 | 84.2 | 4.2 | 209.6 | 9 | 108.2 | 49.2 | 46.2 | 63.4 | 56.3 | 64.8 | 77.5 | 84 | 114.4 | 97.9 | 47.5 | 55.5 | 270.5 | 318.9 | 368.5 | 57.6 | 245.4 | 48.2 | 70.8 | 47.4 | 312.6 | 352.9 | 269.8 | 405.7 | 317.8 | 453.6 | 426
2643.1 | 2404.1 | -5.5 | 0 | 0 | 329.3 | 293.2 | 263 | 256.2 | 36.3 | 50.6 | 16.7 | 84.1 | 4.5 | 234.5 | 8.5 | 107.7 | 49.8 | 45.9 | 63.3 | 56.2 | 64.7 | 77.2 | 84 | 114.3 | 97.7 | 47.4 | 55.5 | 269.9 | 318.5 | 368.3 | 57.5 | 245.3 | 47.5 | 70.7 | 47.2 | 312.4 | 351.9 | 269.4 | 405.6 | 317.5 | 453.2 | 425.8
2644.1 | 2405.1 | -5.4 | 0 | 0 | 329.4 | 293 | 262.8 | 256 | 38.2 | 50.6 | 16.7 | 84 | 4.3 | 231.7 | 7.5 | 107.3 | 49.4 | 45.7 | 63.1 | 56.1 | 64.6 | 77 | 84.1 | 113.6 | 97.4 | 47.3 | 55.6 | 269.5 | 318.4 | 368 | 57.4 | 245.5 | 47.2 | 70.6 | 47.2 | 312.2 | 351.8 | 269.1 | 405.5 | 317.2 | 452.8 | 425.6
2645.1 | 2406.1 | -5.3 | 0 | 0 | 329.4 | 292.6 | 262.5 | 255.7 | 37.4 | 50.6 | 16.7 | 83.9 | 4.8 | 222.7 | 6.8 | 106.8 | 49.4 | 45.6 | 63 | 56 | 64.7 | 76.8 | 83.5 | 111.7 | 96.9 | 47.3 | 55.6 | 269.4 | 318.3 | 367.8 | 57.2 | 245.6 | 48 | 70.5 | 47.4 | 312 | 352.1 | 268.8 | 405.4 | 317 | 452.4 | 425.3
2646.1 | 2407.1 | -5.3 | 0 | 0 | 328.9 | 292.4 | 262.3 | 255.5 | 36.5 | 50.6 | 16.7 | 83.8 | 4.9 | 232 | 7.5 | 106.3 | 49.5 | 45.6 | 62.8 | 55.9 | 64.6 | 76.6 | 83.5 | 110.9 | 96.3 | 47.2 | 55.7 | 269.9 | 318 | 367.6 | 57.2 | 245.4 | 47.9 | 70.4 | 47.5 | 311.9 | 352.2 | 268.4 | 405.3 | 316.7 | 452 | 425.1
2647.1 | 2408.1 | -5.5 | 0 | 0 | 328.3 | 292.2 | 262.2 | 255.3 | 35.7 | 50.5 | 16.7 | 83.7 | 5.2 | 230 | 7 | 105.9 | 49.5 | 45.8 | 62.6 | 55.8 | 64.5 | 76.1 | 83.4 | 109.7 | 96.7 | 47.1 | 55.8 | 270.1 | 317.5 | 367.4 | 57.3 | 245.4 | 47 | 70.3 | 47.5 | 311.7 | 351.9 | 268 | 405.1 | 316.5 | 451.6 | 424.9
2648.1 | 2409.1 | -5.7 | 0 | 0 | 327.9 | 291.8 | 262 | 255.1 | 37.7 | 50.5 | 16.7 | 83.7 | 4.7 | 203.2 | 6.7 | 105.4 | 49 | 46 | 62.4 | 55.7 | 64.3 | 75.9 | 83 | 109.3 | 96.7 | 47.1 | 55.8 | 270.3 | 317.4 | 367.1 | 57.2 | 245.3 | 47.2 | 70.2 | 47.6 | 311.5 | 351.8 | 267.7 | 404.9 | 316.2 | 451.2 | 424.6
2649.1 | 2410.1 | -5.7 | 0 | 0 | 327.4 | 291.5 | 261.8 | 255 | 37.1 | 50.5 | 16.7 | 83.6 | 5.1 | 206.1 | 7.2 | 104.9 | 48.8 | 46 | 62.2 | 55.7 | 64 | 75.7 | 83.3 | 110 | 96.7 | 47 | 55.9 | 270.1 | 317.4 | 366.9 | 57.1 | 245.4 | 47.8 | 70 | 47.4 | 311.3 | 351.3 | 267.5 | 404.8 | 316 | 450.8 | 424.4
2650.1 | 2411.1 | -5.7 | 0 | 0 | 326.5 | 291 | 261.5 | 254.9 | 34.9 | 50.4 | 16.7 | 83.5 | 5.1 | 207.3 | 8.9 | 104.5 | 48.8 | 46.1 | 62 | 55.6 | 63.8 | 75.3 | 83.1 | 110.4 | 96.8 | 47 | 55.9 | 270.3 | 317.2 | 366.7 | 57 | 245.6 | 47.7 | 70.2 | 47.5 | 311.2 | 350.3 | 267.2 | 404.7 | 315.7 | 450.4 | 424.2
2651.1 | 2412.1 | -5.8 | 0 | 0 | 326.4 | 290.5 | 261.3 | 254.7 | 35.9 | 50.4 | 16.7 | 83.4 | 4.4 | 201.5 | 11.8 | 104.1 | 48.9 | 46.6 | 61.8 | 55.5 | 63.7 | 75.1 | 82.6 | 110.1 | 96.3 | 46.9 | 56.1 | 270.9 | 317.1 | 366.5 | 56.9 | 245.5 | 47.7 | 70.2 | 47.5 | 311 | 350.2 | 266.9 | 404.7 | 315.5 | 450 | 424
2652.1 | 2413.1 | -5.9 | 0 | 0 | 326.2 | 290.2 | 261.1 | 254.5 | 37.5 | 50.3 | 16.7 | 83.3 | 5 | 200.8 | 10.4 | 103.6 | 48.9 | 47.2 | 61.7 | 55.5 | 63.5 | 75.1 | 82.8 | 109.7 | 95.7 | 46.9 | 56.2 | 271.3 | 316.9 | 366.2 | 56.8 | 245.6 | 47.6 | 70.1 | 47.2 | 310.8 | 349.7 | 266.6 | 404.5 | 315.2 | 449.6 | 423.7
2653.1 | 2414.1 | -5.8 | 0 | 0 | 325.8 | 290 | 260.7 | 254.3 | 37.6 | 50.2 | 16.7 | 83.3 | 5 | 222.2 | 9.5 | 103.2 | 48.9 | 47.5 | 61.6 | 55.4 | 63.5 | 74.9 | 83 | 110.2 | 96 | 46.8 | 56.3 | 271.7 | 316.5 | 366 | 57 | 245.5 | 47.1 | 69.9 | 47.3 | 310.6 | 349.4 | 266.3 | 404.4 | 315 | 449.2 | 423.5
2654.1 | 2415.1 | -5.8 | 0 | 0 | 325.3 | 289.5 | 260.3 | 254.1 | 37.1 | 50.1 | 16.7 | 83.2 | 5.3 | 209.5 | 11.3 | 102.7 | 48.4 | 47.5 | 61.5 | 55.3 | 63.3 | 74.8 | 82.8 | 110.5 | 96.2 | 46.7 | 56.3 | 272.1 | 315.9 | 365.8 | 57 | 245.1 | 47.3 | 70 | 47.1 | 310.5 | 348.9 | 266 | 404.3 | 314.8 | 448.8 | 423.3
2655.1 | 2416.1 | -5.8 | 0 | 0 | 324.9 | 289 | 259.9 | 253.9 | 35.4 | 50 | 16.7 | 83.1 | 5.2 | 205.8 | 10.1 | 102.3 | 47.8 | 47.6 | 61.4 | 55.2 | 63.2 | 74.8 | 82.7 | 110.7 | 96.3 | 46.7 | 56.3 | 272.7 | 315.9 | 365.6 | 56.8 | 244.6 | 47.7 | 70 | 46.4 | 310.3 | 349 | 265.7 | 404.3 | 314.5 | 448.4 | 423.1
2656.1 | 2417.1 | -5.6 | 0 | 0 | 324.7 | 288.8 | 259.5 | 253.8 | 36.7 | 49.9 | 16.7 | 83 | 5.2 | 183.2 | 9.4 | 101.9 | 47.5 | 47.6 | 61.3 | 55.1 | 63 | 74.4 | 82.4 | 110.6 | 96 | 46.6 | 56.4 | 273 | 315.8 | 365.3 | 56.5 | 244.1 | 48.2 | 70 | 46.5 | 310.1 | 348.9 | 265.4 | 404.2 | 314.3 | 448 | 422.8
2657.1 | 2418.1 | -5.7 | 0 | 0 | 324.4 | 288.2 | 259.2 | 253.6 | 37.3 | 49.9 | 16.8 | 82.9 | 5.1 | 208.6 | 11.3 | 101.4 | 47.4 | 47.6 | 61.1 | 55.1 | 62.8 | 73.8 | 82.5 | 110.9 | 95.6 | 46.5 | 56.4 | 272.8 | 315.5 | 365.1 | 56.5 | 244.2 | 49.6 | 70 | 46.7 | 310 | 348.8 | 265.1 | 404.1 | 314 | 447.6 | 422.6
2658.1 | 2419.1 | -5.8 | 0 | 0 | 324 | 287.7 | 258.8 | 253.5 | 36.7 | 49.8 | 16.8 | 82.9 | 5.5 | 202 | 11.5 | 101 | 47.4 | 47.6 | 61 | 55.1 | 62.8 | 73.5 | 82.4 | 111.6 | 95.9 | 46.4 | 56.5 | 273.3 | 315.6 | 364.9 | 56.5 | 244.9 | 49.8 | 70 | 46.7 | 309.8 | 348.4 | 264.9 | 403.9 | 313.8 | 447.3 | 422.4
2659.1 | 2420.1 | -5.9 | 0 | 0 | 323.8 | 287.2 | 258.3 | 253.3 | 36.4 | 49.7 | 16.8 | 82.9 | 4.5 | 210.9 | 11.8 | 100.6 | 47.2 | 47.2 | 60.8 | 55.1 | 62.7 | 73.5 | 82.2 | 111.6 | 95.6 | 46.4 | 56.5 | 273.2 | 315.5 | 364.7 | 56.5 | 245.9 | 49.4 | 69.9 | 46.5 | 309.6 | 348.3 | 264.6 | 403.8 | 313.5 | 446.9 | 422.1
2660.1 | 2421.1 | -6 | 0 | 0 | 323.5 | 287 | 257.9 | 253.2 | 37.7 | 49.7 | 16.8 | 82.9 | 4.9 | 206.9 | 12.4 | 100.1 | 46.8 | 47.1 | 60.6 | 55 | 62.6 | 73.2 | 81.9 | 111.3 | 95 | 46.3 | 56.6 | 273 | 314.6 | 364.5 | 56.3 | 246.4 | 49.2 | 69.8 | 46.3 | 309.5 | 347.9 | 264.4 | 403.7 | 313.3 | 446.5 | 421.9
2661.1 | 2422.1 | -5.9 | 0 | 0 | 323.1 | 286.6 | 257.6 | 253 | 37.4 | 49.7 | 16.8 | 82.8 | 4.4 | 205.3 | 12.8 | 99.7 | 47 | 46.9 | 60.5 | 55 | 62.4 | 73.1 | 81.6 | 110.9 | 94.9 | 46.2 | 56.5 | 272.8 | 314.4 | 364.3 | 56.1 | 247.1 | 48.9 | 69.8 | 46.6 | 309.3 | 347.3 | 264.2 | 403.6 | 313 | 446.1 | 421.7
2662.1 | 2423.1 | -5.7 | 0 | 0 | 322.7 | 286.1 | 257.4 | 252.9 | 35.9 | 49.7 | 16.8 | 82.7 | 4.4 | 217.3 | 12 | 99.3 | 47.8 | 46.9 | 60.4 | 54.9 | 62.3 | 72.7 | 81.3 | 110.8 | 94.7 | 46.1 | 56.6 | 272.9 | 314.1 | 364 | 56.2 | 248 | 48.4 | 69.7 | 46.8 | 309.1 | 347.6 | 264.1 | 403.5 | 312.8 | 445.7 | 421.4
2663.1 | 2424.1 | -5.6 | 0 | 0 | 322.5 | 285.7 | 257.2 | 252.8 | 36.5 | 49.7 | 16.8 | 82.6 | 4.7 | 205.8 | 10.4 | 98.9 | 48.4 | 46.4 | 60.2 | 54.8 | 61.9 | 72.3 | 80.9 | 110.3 | 94.6 | 46 | 56.6 | 273 | 314.1 | 363.8 | 56.3 | 248.5 | 48 | 69.5 | 46.6 | 308.9 | 347.8 | 263.9 | 403.4 | 312.5 | 445.4 | 421.2
2664.1 | 2425.1 | -5.6 | 0 | 0 | 322.1 | 285.3 | 257.1 | 252.7 | 36.2 | 49.8 | 16.8 | 82.5 | 5.4 | 191.7 | 8.5 | 98.5 | 48.8 | 46.2 | 60.1 | 54.8 | 61.8 | 72.2 | 80.9 | 110.1 | 94.3 | 45.9 | 56.6 | 273 | 313.8 | 363.6 | 56.2 | 249.1 | 47.8 | 69.4 | 46.4 | 308.8 | 347.8 | 263.7 | 403.4 | 312.3 | 445 | 421
2665.1 | 2426.1 | -5.6 | 0 | 0 | 321.8 | 285.1 | 257 | 252.6 | 36.5 | 49.8 | 16.8 | 82.4 | 5.7 | 186.8 | 7.4 | 98.1 | 49.6 | 46.3 | 59.9 | 54.7 | 61.8 | 72 | 80.9 | 110.2 | 94.1 | 45.9 | 56.6 | 273.2 | 313.8 | 363.4 | 56.2 | 249.7 | 48.1 | 69.5 | 46.4 | 308.6 | 347.5 | 263.5 | 403.4 | 312 | 444.6 | 420.8
2666.1 | 2427.1 | -5.6 | 0 | 0 | 321.6 | 284.4 | 256.6 | 252.4 | 35.6 | 49.8 | 16.8 | 82.3 | 5.6 | 201 | 9.7 | 97.7 | 49.7 | 46.4 | 59.8 | 54.6 | 61.7 | 72 | 81 | 109.9 | 93.8 | 45.8 | 56.5 | 273.5 | 313.8 | 363.2 | 56.1 | 250.3 | 48.7 | 69.4 | 46.6 | 308.4 | 346.9 | 263.3 | 403.4 | 311.8 | 444.2 | 420.5
2667.1 | 2428.1 | -5.6 | 0 | 0 | 321.1 | 283.7 | 256.3 | 252.3 | 36.2 | 49.7 | 16.8 | 82.1 | 5.7 | 202.3 | 11.2 | 97.2 | 49.9 | 46.6 | 59.6 | 54.6 | 61.6 | 71.5 | 81.2 | 108.9 | 93.5 | 45.7 | 56.5 | 273.1 | 313.2 | 362.9 | 56 | 250.6 | 47.7 | 69.4 | 46.5 | 308.3 | 346.6 | 263 | 403.3 | 311.5 | 443.8 | 420.3
2668.1 | 2429.1 | -5.7 | 0 | 0 | 320.4 | 283 | 256 | 252.1 | 38.6 | 49.7 | 16.8 | 81.9 | 5.3 | 208.3 | 12.8 | 96.8 | 50.2 | 46.7 | 59.5 | 54.5 | 61.4 | 71.5 | 81 | 108.3 | 93 | 45.7 | 56.6 | 272.4 | 313.2 | 362.7 | 56 | 250.6 | 47.6 | 69.3 | 46.2 | 308.1 | 346.3 | 262.8 | 403.3 | 311.3 | 443.4 | 420.1
2669.1 | 2430.1 | -5.7 | 0 | 0 | 319.8 | 282.6 | 255.7 | 252 | 35.7 | 49.6 | 16.8 | 81.8 | 5.3 | 203.3 | 14.1 | 96.4 | 50.5 | 46.9 | 59.4 | 54.5 | 61.2 | 71.1 | 80.6 | 108.2 | 92.6 | 45.6 | 56.6 | 272.3 | 312.8 | 362.5 | 55.9 | 250.7 | 48.3 | 69.1 | 46.9 | 308 | 346.1 | 262.6 | 403.3 | 311.1 | 443 | 419.9
2670.1 | 2431.1 | -5.8 | 0 | 0 | 319.1 | 282.3 | 255.4 | 251.8 | 34.4 | 49.6 | 16.8 | 81.8 | 4.8 | 218.5 | 12.6 | 96 | 50.9 | 46.9 | 59.4 | 54.5 | 61 | 71 | 80.6 | 108.2 | 92.6 | 45.5 | 56.6 | 272.2 | 312.3 | 362.3 | 55.7 | 250.8 | 47.8 | 69.1 | 47 | 307.8 | 345.5 | 262.4 | 403.3 | 310.8 | 442.7 | 419.6
2671.1 | 2432.1 | -5.6 | 0 | 0 | 318.8 | 282.2 | 255.2 | 251.6 | 34.2 | 49.5 | 16.8 | 81.7 | 4.9 | 236.8 | 8.9 | 95.7 | 51.1 | 47 | 59.3 | 54.4 | 60.9 | 70.8 | 80.5 | 108.2 | 92.3 | 45.4 | 56.6 | 271 | 312.2 | 362.1 | 55.7 | 250.6 | 47.5 | 69 | 46.7 | 307.6 | 345.4 | 262.2 | 403.3 | 310.6 | 442.3 | 419.4
2672.1 | 2433.1 | -5.5 | 0 | 0 | 318.5 | 282.1 | 255.1 | 251.4 | 35.3 | 49.4 | 16.8 | 81.6 | 5.5 | 191.6 | 7.6 | 95.3 | 50.3 | 46.8 | 59.3 | 54.3 | 60.8 | 70.6 | 80.5 | 108.1 | 92.1 | 45.3 | 56.5 | 271.1 | 312.6 | 361.9 | 55.7 | 250.6 | 47.1 | 69 | 46.3 | 307.5 | 345.4 | 262 | 403.2 | 310.4 | 441.9 | 419.2
2673.1 | 2434.1 | -5.5 | 0 | 0 | 318.3 | 281.8 | 254.9 | 251.2 | 35 | 49.3 | 16.8 | 81.6 | 5.2 | 228.4 | 6.2 | 94.9 | 50 | 46.6 | 59.2 | 54.2 | 60.7 | 70.5 | 80.5 | 108 | 91.5 | 45.3 | 56.6 | 271.6 | 312.5 | 361.7 | 55.7 | 250.6 | 46.9 | 68.8 | 46.5 | 307.3 | 345.4 | 261.7 | 403.2 | 310.1 | 441.5 | 418.9
2674.1 | 2435.1 | -5.5 | 0 | 0 | 318.2 | 281.6 | 254.5 | 251.1 | 35.2 | 49.1 | 16.8 | 81.6 | 4.8 | 205.2 | 9.1 | 94.5 | 49.5 | 46.1 | 59.1 | 54.1 | 60.8 | 70.3 | 80 | 108 | 91.3 | 45.2 | 56.6 | 271.7 | 312.3 | 361.5 | 55.6 | 250.5 | 46.4 | 68.9 | 46.5 | 307.2 | 345.5 | 261.4 | 403.2 | 309.9 | 441.2 | 418.7
2675.1 | 2436.1 | -5.4 | 0 | 0 | 318.3 | 281.5 | 253.9 | 251 | 37 | 49 | 16.8 | 81.5 | 5.8 | 206.4 | 12.9 | 94.1 | 49 | 45.6 | 59 | 53.9 | 60.7 | 70.2 | 79.5 | 108 | 91.2 | 45.1 | 56.7 | 272.5 | 311.7 | 361.2 | 55.4 | 250.4 | 46.5 | 68.8 | 46.4 | 307 | 345.4 | 261.1 | 403.2 | 309.6 | 440.8 | 418.5
2676.1 | 2437.1 | -5.5 | 0 | 0 | 318.4 | 281.3 | 253.5 | 250.8 | 36.9 | 48.9 | 16.9 | 81.4 | 6 | 210.6 | 11.9 | 93.7 | 48.6 | 45.1 | 58.9 | 53.7 | 60.7 | 69.8 | 79.4 | 108.1 | 91 | 45 | 56.7 | 273.1 | 311.3 | 361 | 55.3 | 250.5 | 47 | 68.8 | 45.9 | 306.8 | 345.7 | 260.8 | 403.2 | 309.4 | 440.4 | 418.3
2677.1 | 2438.1 | -5.8 | 0 | 0 | 318.5 | 281.1 | 253.4 | 250.7 | 37.6 | 49 | 16.9 | 81.3 | 6.6 | 215.5 | 11 | 93.4 | 48.2 | 44.6 | 58.8 | 53.6 | 60.7 | 69.7 | 79.5 | 108.2 | 91 | 45 | 56.6 | 272.5 | 311.1 | 360.8 | 55.3 | 250.3 | 47 | 68.7 | 46 | 306.7 | 346 | 260.5 | 403.1 | 309.2 | 440 | 418.1
2678.1 | 2439.1 | -5.9 | 0 | 0 | 318.4 | 280.7 | 253.2 | 250.5 | 36.9 | 49 | 16.9 | 81.2 | 7.1 | 215.3 | 11.1 | 93 | 48.4 | 44.3 | 58.7 | 53.4 | 60.7 | 69.6 | 79.5 | 107.3 | 90.7 | 44.9 | 56.6 | 271.8 | 310.3 | 360.6 | 55.3 | 250.1 | 47.7 | 68.6 | 46.6 | 306.5 | 345.9 | 260.1 | 403 | 308.9 | 439.7 | 417.9
2679.1 | 2440.1 | -6.2 | 0 | 0 | 318.4 | 280.2 | 253 | 250.1 | 36.6 | 48.9 | 16.9 | 81.1 | 6.3 | 229.2 | 10.6 | 92.6 | 48.1 | 44 | 58.6 | 53.2 | 60.7 | 69.5 | 79.5 | 106.5 | 90.8 | 44.8 | 56.5 | 271.5 | 311.2 | 360.4 | 55.1 | 249.8 | 47.3 | 68.6 | 47.1 | 306.4 | 346 | 259.8 | 402.9 | 308.7 | 439.3 | 417.6
2680.1 | 2441.1 | -6.1 | 0 | 0 | 318.2 | 279.8 | 252.8 | 249.8 | 34.6 | 48.9 | 16.9 | 81 | 5.5 | 243.6 | 9.6 | 92.2 | 48.1 | 43.8 | 58.5 | 53.1 | 60.6 | 69.4 | 79.5 | 107.1 | 90.7 | 44.8 | 56.4 | 270.9 | 311.3 | 360.2 | 55 | 249.4 | 46.8 | 68.6 | 47 | 306.2 | 345.9 | 259.4 | 402.7 | 308.5 | 438.9 | 417.4
2681.1 | 2442.1 | -6.2 | 0 | 0 | 318 | 279.3 | 252.5 | 249.4 | 35.7 | 48.9 | 16.9 | 81 | 4.6 | 235.2 | 9.4 | 91.9 | 47.8 | 43.8 | 58.4 | 52.9 | 60.6 | 69.3 | 79 | 106.1 | 90.6 | 44.7 | 56.3 | 270.9 | 311.2 | 359.9 | 54.9 | 249.4 | 47 | 68.5 | 46.9 | 306 | 346 | 259.2 | 402.5 | 308.2 | 438.5 | 417.2
2682.1 | 2443.1 | -6.1 | 0 | 0 | 318 | 279.1 | 252.3 | 249.2 | 37.1 | 48.8 | 16.9 | 80.9 | 5.2 | 205.3 | 8.8 | 91.5 | 47.5 | 44 | 58.3 | 52.8 | 60.6 | 69.2 | 79 | 105.7 | 90.8 | 44.6 | 56.3 | 271.2 | 311.3 | 359.7 | 54.8 | 249.6 | 47.4 | 68.3 | 47 | 305.9 | 345.6 | 258.9 | 402.4 | 308 | 438.1 | 417
2683.1 | 2444.1 | -5.9 | 0 | 0 | 317.5 | 278.7 | 252.1 | 248.9 | 37.6 | 48.8 | 16.9 | 80.7 | 6.4 | 238.4 | 9.1 | 91.1 | 47.7 | 43.9 | 58.2 | 52.6 | 60.5 | 69.1 | 79 | 105 | 90.7 | 44.5 | 56.2 | 271.5 | 311.1 | 359.5 | 54.6 | 249.7 | 47.8 | 68.3 | 47 | 305.7 | 345.4 | 258.5 | 402.2 | 307.8 | 437.7 | 416.7
2684.1 | 2445.1 | -5.7 | 0 | 0 | 317.4 | 278.3 | 252.1 | 248.5 | 38.5 | 48.7 | 16.9 | 80.6 | 5.1 | 212.4 | 11.6 | 90.8 | 48.2 | 43.7 | 58.1 | 52.5 | 60.5 | 68.9 | 79.3 | 104.6 | 90.2 | 44.5 | 56.2 | 271.7 | 310.9 | 359.3 | 54.6 | 249.8 | 47.7 | 68.2 | 46.8 | 305.6 | 345.5 | 258.2 | 402.1 | 307.5 | 437.4 | 416.5
2685.1 | 2446.1 | -5.5 | 0 | 0 | 317.2 | 278 | 251.9 | 248.2 | 38 | 48.6 | 16.9 | 80.6 | 4 | 217.2 | 11.3 | 90.4 | 48.1 | 43.6 | 58 | 52.4 | 60.5 | 68.5 | 79.3 | 105.3 | 89.8 | 44.4 | 56.1 | 271.7 | 311.1 | 359.1 | 54.6 | 249.5 | 48 | 68.1 | 46.1 | 305.4 | 345.3 | 257.9 | 402 | 307.3 | 437 | 416.3
2686.1 | 2447.1 | -5.5 | 0 | 0 | 316.9 | 277.9 | 251.5 | 247.8 | 35.7 | 48.6 | 16.9 | 80.5 | 4.3 | 228 | 10.1 | 90 | 47.9 | 43.3 | 57.9 | 52.3 | 60.4 | 68.6 | 78.8 | 105.4 | 90 | 44.4 | 56.1 | 272 | 311.1 | 358.9 | 54.5 | 248.8 | 47.2 | 68 | 46.1 | 305.2 | 345 | 257.6 | 401.9 | 307 | 436.6 | 416.1
2687.1 | 2448.1 | -5.4 | 0 | 0 | 316.7 | 277.9 | 251.1 | 247.5 | 35.7 | 48.4 | 16.9 | 80.5 | 4.5 | 216.9 | 12.4 | 89.7 | 48 | 43.1 | 57.9 | 52.1 | 60.3 | 68.8 | 79.1 | 105.2 | 89.6 | 44.3 | 56 | 272 | 310.3 | 358.7 | 54.4 | 248.3 | 47.1 | 67.9 | 46.4 | 305.1 | 345 | 257.4 | 401.9 | 306.8 | 436.2 | 415.8
2688.1 | 2449.1 | -5.3 | 0 | 0 | 316.5 | 277.7 | 250.7 | 247.1 | 34.1 | 48.3 | 16.9 | 80.5 | 4.3 | 241.5 | 10.2 | 89.3 | 47.8 | 43.2 | 57.8 | 52 | 60.3 | 68.4 | 79.2 | 105.3 | 88.8 | 44.2 | 56 | 271 | 310.3 | 358.5 | 54.4 | 248 | 47.2 | 67.7 | 46.4 | 304.9 | 344.8 | 257.1 | 401.8 | 306.6 | 435.9 | 415.6
2689.1 | 2450.1 | -5.2 | 0 | 0 | 316.3 | 277.7 | 250.4 | 246.9 | 34.3 | 48.1 | 16.9 | 80.4 | 4.3 | 204.9 | 10.7 | 88.9 | 47.9 | 43.2 | 57.7 | 51.9 | 60.2 | 68.1 | 79.4 | 105.5 | 88.6 | 44.1 | 56 | 270.8 | 310.5 | 358.2 | 54.5 | 247.7 | 47.2 | 67.7 | 46.4 | 304.8 | 344.4 | 256.8 | 401.8 | 306.3 | 435.5 | 415.4
2690.1 | 2451.1 | -5 | 0 | 0 | 315.8 | 277.9 | 250.1 | 246.7 | 35.2 | 48 | 16.9 | 80.3 | 4.7 | 208.6 | 11.9 | 88.6 | 47.7 | 43.3 | 57.6 | 51.8 | 60 | 68 | 79.5 | 104.9 | 88.4 | 44.1 | 55.9 | 270.6 | 310.6 | 358 | 54.4 | 247.6 | 47 | 67.6 | 46.3 | 304.6 | 344.4 | 256.6 | 401.7 | 306.1 | 435.2 | 415.2
2691.1 | 2452.1 | -4.9 | 0 | 0 | 315.5 | 277.3 | 249.8 | 246.5 | 35.5 | 47.9 | 16.9 | 80.2 | 5.5 | 205.1 | 9.5 | 88.3 | 47.7 | 43.5 | 57.5 | 51.7 | 59.8 | 67.9 | 79.1 | 104.4 | 88.2 | 44 | 55.8 | 270.5 | 309.9 | 357.8 | 54.3 | 247.3 | 46.7 | 67.6 | 45.9 | 304.5 | 344.3 | 256.4 | 401.5 | 305.9 | 434.8 | 415
2692.1 | 2453.1 | -5.1 | 0 | 0 | 315.1 | 276.7 | 249.5 | 246.3 | 36.6 | 47.8 | 16.9 | 80.1 | 5.6 | 233.5 | 7 | 87.9 | 47.9 | 43.6 | 57.4 | 51.6 | 59.6 | 67.8 | 79.1 | 104.8 | 87.8 | 44 | 55.7 | 270.7 | 310 | 357.6 | 54.3 | 247.1 | 46.9 | 67.6 | 45.6 | 304.3 | 344 | 256.1 | 401.3 | 305.7 | 434.5 | 414.7
2693.1 | 2454.1 | -5.2 | 0 | 0 | 314.8 | 276.1 | 249.5 | 246.1 | 35.6 | 47.8 | 16.9 | 80.1 | 4.8 | 235 | 6.9 | 87.6 | 47.9 | 43.8 | 57.3 | 51.5 | 59.6 | 67.6 | 79.1 | 104.9 | 87.3 | 43.9 | 55.5 | 271.8 | 310 | 357.4 | 54.2 | 247 | 46.7 | 67.4 | 45.8 | 304.1 | 343.5 | 255.9 | 401.1 | 305.4 | 434.1 | 414.5
2694.1 | 2455.1 | -5.2 | 0 | 0 | 314.6 | 275.5 | 249.2 | 245.9 | 35.3 | 47.8 | 16.9 | 80 | 4.9 | 203.2 | 8.3 | 87.3 | 48.4 | 44 | 57.3 | 51.4 | 59.6 | 67.5 | 79.1 | 104.6 | 86.9 | 43.9 | 55.2 | 272.5 | 309.5 | 357.2 | 54.1 | 246.9 | 46.8 | 67.5 | 46.1 | 304 | 343.1 | 255.7 | 401 | 305.2 | 433.7 | 414.3
2695.1 | 2456.1 | -5.3 | 0 | 0 | 314.4 | 275.1 | 249 | 245.6 | 37.3 | 47.7 | 17 | 79.9 | 5 | 234.7 | 9.1 | 86.9 | 48.2 | 44.1 | 57.2 | 51.3 | 59.5 | 67.4 | 78.5 | 104 | 86.8 | 43.8 | 55 | 272.2 | 309.1 | 357 | 54.1 | 247.1 | 46.4 | 67.4 | 46.2 | 303.8 | 342.5 | 255.5 | 400.9 | 305 | 433.4 | 414.1
2696.1 | 2457.1 | -5.4 | 0 | 0 | 314.3 | 274.4 | 248.9 | 245.2 | 37.4 | 47.7 | 17 | 79.8 | 4.7 | 237.2 | 8.4 | 86.6 | 48.4 | 44.3 | 57.1 | 51.2 | 59.4 | 67.4 | 76.9 | 103.7 | 86.4 | 43.7 | 54.7 | 272.1 | 308.9 | 356.7 | 54.1 | 247.2 | 46.5 | 67.3 | 46.2 | 303.7 | 342.5 | 255.2 | 400.7 | 304.8 | 433 | 413.9
2697.1 | 2458.1 | -5.4 | 0 | 0 | 314.1 | 273.7 | 249 | 244.9 | 36.8 | 47.8 | 17 | 79.7 | 4.8 | 249.3 | 8.8 | 86.2 | 48.5 | 44.6 | 57 | 50.8 | 59.2 | 67.3 | 77.9 | 103.2 | 85.9 | 43.7 | 54 | 271.7 | 309 | 356.5 | 54 | 247.2 | 46.6 | 67.4 | 45.6 | 303.5 | 342.3 | 255 | 400.5 | 304.5 | 432.7 | 413.6
2698.1 | 2459.1 | -5.5 | 0 | 0 | 313.6 | 273.3 | 249.1 | 244.7 | 35.4 | 47.8 | 17 | 79.7 | 5.1 | 245.4 | 10.4 | 85.9 | 48.5 | 44.5 | 56.9 | 50.6 | 59 | 67.2 | 77.6 | 103.5 | 86 | 43.6 | 53.8 | 271.4 | 308.5 | 356.3 | 54 | 247.4 | 46.8 | 67.3 | 45.5 | 303.4 | 341.6 | 254.7 | 400.3 | 304.3 | 432.3 | 413.4
2699.1 | 2460.1 | -5.6 | 0 | 0 | 313.1 | 273.4 | 249 | 244.5 | 35.2 | 47.8 | 17 | 79.6 | 5 | 262.3 | 10.7 | 85.5 | 48.6 | 44.1 | 56.9 | 50.7 | 58.8 | 67.1 | 77.2 | 102.4 | 85.8 | 43.6 | 53.3 | 271.1 | 308.4 | 356.1 | 54 | 247.5 | 46.4 | 67 | 45.6 | 303.2 | 340.6 | 254.5 | 400.2 | 304.1 | 431.9 | 413.2
2700.1 | 2461.1 | -5.6 | 0 | 0 | 312.6 | 273.6 | 248.9 | 244.3 | 36.3 | 47.8 | 17 | 79.5 | 4 | 235.5 | 9.7 | 85.2 | 48.7 | 43.8 | 56.8 | 50.8 | 58.8 | 67.2 | 77.6 | 101.9 | 85.4 | 43.5 | 52.7 | 271.1 | 307.9 | 355.9 | 53.9 | 247.5 | 46.2 | 67.1 | 45.6 | 303.1 | 339.8 | 254.4 | 400 | 303.9 | 431.6 | 413
2701.1 | 2462.1 | -5.9 | 0 | 0 | 312.3 | 273.5 | 248.7 | 244.1 | 36 | 47.7 | 17 | 79.4 | 4.5 | 250 | 8.2 | 84.9 | 48.9 | 43.2 | 56.7 | 50.8 | 58.7 | 67.1 | 77.9 | 101.9 | 85.1 | 43.4 | 52.3 | 270.9 | 308 | 355.7 | 53.8 | 247.3 | 46.9 | 67.1 | 45.7 | 302.9 | 339.5 | 254.2 | 399.8 | 303.7 | 431.2 | 412.8
2702.1 | 2463.1 | -5.9 | 0 | 0 | 312 | 273.5 | 248.6 | 244 | 37.1 | 47.7 | 17 | 79.3 | 4.8 | 232.6 | 7.7 | 84.6 | 49.2 | 42.9 | 56.7 | 50.7 | 58.6 | 66.7 | 77.8 | 102 | 85 | 43.4 | 52.3 | 270.1 | 307.7 | 355.5 | 53.9 | 247.4 | 46.9 | 67.1 | 45.3 | 302.8 | 339.4 | 254 | 399.6 | 303.4 | 430.9 | 412.5
2703.1 | 2464.1 | -5.8 | 0 | 0 | 311.9 | 273.5 | 248.4 | 244 | 35.7 | 47.7 | 17 | 79.3 | 4.5 | 272.9 | 7 | 84.2 | 49.1 | 42.5 | 56.6 | 50.7 | 58.6 | 66.7 | 77.7 | 101.8 | 84.8 | 43.3 | 52.2 | 270.4 | 307.2 | 355.3 | 53.8 | 247.4 | 46.2 | 67.1 | 45.5 | 302.6 | 339 | 253.8 | 399.4 | 303.2 | 430.5 | 412.3
2704.1 | 2465.1 | -5.9 | 0 | 0 | 311.7 | 273.5 | 248.3 | 243.8 | 34.4 | 47.7 | 17 | 79.2 | 5 | 218.1 | 6.7 | 83.9 | 49 | 42.3 | 56.6 | 50.6 | 58.6 | 66.6 | 77.4 | 101.7 | 84.7 | 43.3 | 51.5 | 270.4 | 306.3 | 355 | 53.8 | 247.4 | 46 | 67.1 | 45.9 | 302.5 | 338.7 | 253.7 | 399.2 | 303 | 430.1 | 412.1
2705.1 | 2466.1 | -5.8 | 0 | 0 | 311.3 | 273.2 | 248.1 | 243.6 | 33.7 | 47.7 | 17 | 79.1 | 4.5 | 227 | 6.7 | 83.6 | 48.7 | 42.1 | 56.5 | 50.5 | 58.5 | 66.6 | 77.6 | 101.6 | 84.5 | 43.3 | 50.9 | 270.8 | 305.9 | 354.8 | 53.8 | 247 | 45.8 | 67 | 46 | 302.3 | 338.8 | 253.5 | 399.1 | 302.8 | 429.8 | 411.9
2706.1 | 2467.1 | -5.7 | 0 | 0 | 310.9 | 272.9 | 247.9 | 243.5 | 32.2 | 47.6 | 17 | 79 | 5.3 | 234.3 | 7.7 | 83.2 | 48.7 | 41.9 | 56.4 | 50.4 | 58.4 | 66.5 | 77.6 | 100.1 | 84.5 | 43.3 | 50.7 | 271.1 | 305.6 | 354.6 | 53.7 | 246.8 | 46.2 | 67 | 45.6 | 302.2 | 338.5 | 253.2 | 398.9 | 302.6 | 429.4 | 411.6
2707.1 | 2468.1 | -5.6 | 0 | 0 | 310.7 | 272.3 | 247.7 | 243.4 | 34 | 47.6 | 17 | 78.9 | 6 | 212.3 | 7.2 | 82.9 | 48.5 | 41.7 | 56.3 | 50.3 | 58.3 | 66.3 | 77.4 | 100.6 | 83.9 | 43.3 | 50.6 | 271.3 | 305.4 | 354.4 | 53.6 | 246.8 | 46.3 | 66.9 | 45.5 | 302 | 337.3 | 253 | 398.7 | 302.3 | 429.1 | 411.4
2708.1 | 2469.1 | -5.6 | 0 | 0 | 310.6 | 271.5 | 247.5 | 243.2 | 34.9 | 47.6 | 17 | 78.8 | 5.8 | 230.7 | 7.5 | 82.6 | 49 | 41.5 | 56.2 | 50.1 | 58.3 | 66 | 77.4 | 101.2 | 83.4 | 43.2 | 50.4 | 271.1 | 305.7 | 354.2 | 53.6 | 246.8 | 45.8 | 66.9 | 45.6 | 301.9 | 337.2 | 252.8 | 398.6 | 302.1 | 428.7 | 411.2
2709.1 | 2470.1 | -5.6 | 0 | 0 | 310.2 | 271.1 | 247.2 | 242.9 | 35.7 | 47.5 | 17 | 78.8 | 6.2 | 244.9 | 9.8 | 82.3 | 49.5 | 41.4 | 56.1 | 50 | 58.1 | 66 | 77.2 | 101.5 | 83 | 43.1 | 49.9 | 270.9 | 305.3 | 354 | 53.5 | 246.5 | 45.8 | 66.8 | 45.6 | 301.7 | 336.6 | 252.6 | 398.4 | 301.9 | 428.4 | 411
2710.1 | 2471.1 | -5.8 | 0 | 0 | 309.7 | 270.7 | 247 | 242.7 | 36.1 | 47.5 | 17 | 78.7 | 5.6 | 235.5 | 12.1 | 81.9 | 49.8 | 41.2 | 56 | 49.8 | 58 | 65.8 | 76.9 | 101.7 | 82.9 | 43.1 | 49.3 | 270.7 | 305.5 | 353.8 | 53.5 | 246.4 | 46.4 | 66.5 | 45.2 | 301.6 | 336.2 | 252.4 | 398.2 | 301.7 | 428 | 410.8
2711.1 | 2472.1 | -5.9 | 0 | 0 | 309.2 | 270.2 | 246.8 | 242.4 | 35.6 | 47.4 | 17 | 78.6 | 6.1 | 272 | 11 | 81.6 | 50 | 40.8 | 56 | 49.6 | 57.8 | 65.8 | 77 | 101.5 | 82.7 | 43 | 49.2 | 270.8 | 305.2 | 353.6 | 53.5 | 246.3 | 45.9 | 66.4 | 45.3 | 301.4 | 336.1 | 252.1 | 398.1 | 301.5 | 427.7 | 410.6
2712.1 | 2473.1 | -5.9 | 0 | 0 | 308.8 | 269.6 | 246.6 | 242.3 | 35.2 | 47.4 | 17 | 78.5 | 5.2 | 250.5 | 8.1 | 81.3 | 49.7 | 40.7 | 55.9 | 49.5 | 57.8 | 65.5 | 74.9 | 101.5 | 82.5 | 42.9 | 49.2 | 271.1 | 305 | 353.4 | 53.4 | 246 | 46 | 66.5 | 45.6 | 301.3 | 336.2 | 251.9 | 397.9 | 301.3 | 427.3 | 410.4
2713.1 | 2474.1 | -5.7 | 0 | 0 | 308.3 | 269.3 | 246.2 | 242.2 | 35.9 | 47.3 | 17 | 78.5 | 4.6 | 250.4 | 8.6 | 81 | 50.1 | 40.6 | 55.8 | 49.4 | 57.7 | 65.4 | 76 | 101.5 | 82.4 | 42.8 | 48.7 | 271.4 | 305 | 353.2 | 53.3 | 245.5 | 46.1 | 66.3 | 45.4 | 301.1 | 336.3 | 251.6 | 397.7 | 301 | 427 | 410.1
2714.1 | 2475.1 | -5.6 | 0 | 0 | 307.7 | 269.1 | 245.8 | 242.1 | 36.1 | 47.3 | 17 | 78.4 | 5 | 226 | 8.8 | 80.7 | 50.6 | 40.5 | 55.7 | 49.4 | 57.7 | 65.5 | 76.7 | 101.4 | 82.3 | 42.8 | 48.3 | 271.4 | 304.2 | 353 | 53.3 | 244.7 | 46.7 | 66.3 | 44.9 | 301 | 336.2 | 251.4 | 397.6 | 300.8 | 426.6 | 409.9
2715.1 | 2476.1 | -5.5 | 0 | 0 | 307.4 | 268.6 | 245.4 | 241.8 | 36.4 | 47.3 | 17 | 78.4 | 4 | 187.7 | 7.5 | 80.4 | 50.7 | 40.5 | 55.7 | 49.3 | 57.7 | 65.5 | 76.9 | 101.2 | 82 | 42.7 | 48.2 | 271.2 | 304.2 | 352.8 | 53.2 | 244.1 | 45.7 | 66.3 | 45.5 | 300.9 | 336 | 251.2 | 397.4 | 300.6 | 426.3 | 409.7
2716.1 | 2477.1 | -5.4 | 0 | 0 | 307 | 268.4 | 245.1 | 241.5 | 35.2 | 47.3 | 17.1 | 78.4 | 4.3 | 229.5 | 5.9 | 80.1 | 50.7 | 40.3 | 55.6 | 49 | 57.6 | 65.3 | 76.8 | 101.1 | 81.6 | 42.7 | 48.3 | 271.6 | 304.3 | 352.6 | 53.1 | 243.7 | 45.6 | 66.5 | 45.6 | 300.7 | 335.8 | 250.9 | 397.3 | 300.4 | 425.9 | 409.5
2717.1 | 2478.1 | -5.3 | 0 | 0 | 306.6 | 268.1 | 244.6 | 241.2 | 34.9 | 47.2 | 17.1 | 78.3 | 4.1 | 222.8 | 6.3 | 79.8 | 50.9 | 40.3 | 55.6 | 49 | 57.5 | 65.3 | 76.8 | 101.4 | 81.3 | 42.6 | 48 | 272 | 304.8 | 352.4 | 53.1 | 243.2 | 45.4 | 66.5 | 45.3 | 300.6 | 335.8 | 250.6 | 397.1 | 300.2 | 425.6 | 409.3
2718.1 | 2479.1 | -5.2 | 0 | 0 | 306.3 | 267.5 | 244.3 | 240.9 | 36.4 | 47.2 | 17.1 | 78.2 | 3.9 | 224.2 | 7.7 | 79.4 | 51 | 40.5 | 55.5 | 48.9 | 57.3 | 65.3 | 76.8 | 101.7 | 80.9 | 42.5 | 47.7 | 272 | 305 | 352.2 | 52.9 | 243 | 45.8 | 66.6 | 44.7 | 300.4 | 335.6 | 250.4 | 397 | 300 | 425.2 | 409
2719.1 | 2480.1 | -5.3 | 0 | 0 | 306.1 | 266.7 | 244 | 240.5 | 36.1 | 47.2 | 17.1 | 78.2 | 4.5 | 228.1 | 9.7 | 79.1 | 51.6 | 40.6 | 55.5 | 48.6 | 57.2 | 65 | 76.6 | 101.4 | 80.8 | 42.5 | 47.6 | 272.3 | 304.7 | 352 | 52.8 | 242.8 | 45.4 | 66.4 | 44.5 | 300.3 | 335.3 | 250.1 | 396.8 | 299.8 | 424.9 | 408.8
2720.1 | 2481.1 | -5.4 | 0 | 0 | 305.9 | 266.1 | 243.7 | 240.2 | 34.5 | 47.1 | 17.1 | 78.1 | 5.4 | 214.8 | 9.6 | 78.8 | 51.5 | 40.8 | 55.5 | 48.7 | 57.1 | 64.8 | 76.5 | 101.3 | 80.5 | 42.4 | 47.7 | 272 | 304.5 | 351.8 | 52.7 | 243 | 45.7 | 66.5 | 44.6 | 300.1 | 334.9 | 249.8 | 396.7 | 299.6 | 424.5 | 408.6
2721.1 | 2482.1 | -5.5 | 0 | 0 | 305.8 | 266.1 | 243.4 | 239.8 | 34.3 | 47.1 | 17.1 | 78.1 | 5.4 | 219.7 | 8.3 | 78.5 | 51.7 | 41.1 | 55.4 | 48.4 | 57 | 64.7 | 76.7 | 101.3 | 81 | 42.3 | 47.5 | 272.6 | 304.3 | 351.6 | 52.7 | 243.2 | 45.2 | 66.3 | 44.1 | 300 | 334.8 | 249.5 | 396.6 | 299.4 | 424.2 | 408.4
2722.1 | 2483.1 | -5.3 | 0 | 0 | 305.5 | 265.8 | 243.1 | 239.3 | 34.4 | 47.1 | 17.1 | 78 | 5.6 | 241.1 | 7.3 | 78.2 | 51.7 | 41.4 | 55.3 | 48 | 57 | 64.6 | 76.5 | 101.4 | 81.3 | 42.2 | 47.3 | 273 | 305.3 | 351.4 | 52.8 | 243.1 | 45.7 | 66.2 | 44.3 | 299.8 | 334.7 | 249.4 | 396.5 | 299.2 | 423.8 | 408.2
2723.1 | 2484.1 | -5.4 | 0 | 0 | 305.3 | 265.5 | 242.8 | 239 | 33.7 | 47 | 17.1 | 78 | 6 | 222.1 | 6.6 | 77.9 | 51.9 | 41.6 | 55.3 | 47.9 | 56.9 | 64.6 | 76.4 | 100.2 | 81 | 42 | 47.2 | 273.5 | 305.1 | 351.1 | 52.8 | 243.1 | 45 | 66.2 | 44.2 | 299.7 | 334.8 | 249.2 | 396.3 | 298.9 | 423.5 | 407.9
2724.1 | 2485.1 | -5.6 | 0 | 0 | 305.1 | 265.2 | 242.5 | 238.8 | 31.7 | 47 | 17.1 | 77.8 | 5.7 | 227.4 | 6.3 | 77.6 | 52 | 41.8 | 55.2 | 47.1 | 56.7 | 64.6 | 75.9 | 99.3 | 80.2 | 42 | 47.4 | 273.5 | 304.4 | 350.9 | 52.8 | 242.9 | 44.9 | 66 | 44.1 | 299.6 | 334.6 | 248.9 | 396.1 | 298.7 | 423.1 | 407.7
2725.1 | 2486.1 | -5.7 | 0 | 0 | 304.9 | 265.2 | 242.1 | 238.6 | 34.1 | 47 | 17.1 | 77.7 | 5.3 | 248.2 | 6.3 | 77.3 | 51.9 | 41.9 | 55.2 | 47 | 56.7 | 64.4 | 75.8 | 99.9 | 79.8 | 41.9 | 47.5 | 273.4 | 303.9 | 350.7 | 52.8 | 242.8 | 44.8 | 65.7 | 44 | 299.4 | 334.8 | 248.7 | 396 | 298.5 | 422.8 | 407.5
2726.1 | 2487.1 | -5.8 | 0 | 0 | 304.6 | 265.6 | 242.1 | 238.4 | 33.9 | 46.9 | 17.1 | 77.7 | 4.6 | 244.6 | 7 | 77 | 51.1 | 41.9 | 55.1 | 47.6 | 56.6 | 64.3 | 75.7 | 99.8 | 79.7 | 41.8 | 46.9 | 273 | 302.8 | 350.6 | 52.7 | 242.8 | 44.9 | 65.8 | 44.2 | 299.3 | 334.1 | 248.4 | 395.7 | 298.3 | 422.4 | 407.3
2727.1 | 2488.1 | -5.9 | 0 | 0 | 304.5 | 265.7 | 242.1 | 238.2 | 34.4 | 46.9 | 17.1 | 77.7 | 4.4 | 239.1 | 9.8 | 76.7 | 50.2 | 42 | 55.1 | 48 | 56.6 | 64.2 | 75.5 | 99.1 | 79.9 | 41.8 | 47.1 | 272.4 | 302.8 | 350.4 | 52.7 | 242.7 | 44.9 | 65.8 | 44.3 | 299.1 | 334.1 | 248.2 | 395.5 | 298.1 | 422.1 | 407.1
2728.1 | 2489.1 | -5.9 | 0 | 0 | 304.4 | 265.7 | 241.7 | 237.9 | 34 | 46.8 | 17.1 | 77.6 | 5.2 | 244.2 | 11.5 | 76.4 | 50 | 41.7 | 55 | 48.3 | 56.5 | 64 | 75.6 | 99.3 | 79.9 | 41.8 | 47.1 | 271.7 | 302.7 | 350.1 | 52.6 | 242.6 | 45.3 | 65.8 | 43.8 | 299 | 333.7 | 247.9 | 395.3 | 297.9 | 421.8 | 406.9
2729.1 | 2490.1 | -5.7 | 0 | 0 | 304.4 | 265.4 | 241.2 | 237.7 | 33.1 | 46.7 | 17.1 | 77.6 | 5 | 260.9 | 11.7 | 76.1 | 49.5 | 41.6 | 55 | 48.5 | 56.3 | 64 | 75.4 | 99.4 | 79.7 | 41.7 | 47 | 271.2 | 302.9 | 349.9 | 52.5 | 242.7 | 45.1 | 65.8 | 44 | 298.8 | 332.8 | 247.7 | 395.1 | 297.7 | 421.4 | 406.7
2730.1 | 2491.1 | -5.5 | 0 | 0 | 304.1 | 265 | 240.7 | 237.5 | 31.6 | 46.6 | 17.1 | 77.6 | 4.3 | 241.7 | 11.3 | 75.8 | 49.2 | 41.5 | 54.9 | 48.4 | 56.1 | 63.9 | 75.3 | 97.5 | 79.6 | 41.7 | 47 | 270.6 | 302.6 | 349.7 | 52.6 | 242.6 | 44.3 | 65.7 | 44.1 | 298.7 | 332.3 | 247.4 | 394.9 | 297.5 | 421.1 | 406.4
2731.1 | 2492.1 | -5.4 | 0 | 0 | 303.7 | 264.7 | 240.6 | 237.3 | 31.9 | 46.5 | 17.1 | 77.5 | 4.6 | 243.5 | 10.1 | 75.5 | 49.1 | 41.3 | 54.8 | 48.3 | 55.9 | 63.9 | 75.2 | 97.7 | 79.4 | 41.6 | 46.9 | 271.1 | 301.9 | 349.5 | 52.5 | 242.2 | 44.2 | 65.8 | 44.3 | 298.6 | 332.1 | 247.2 | 394.8 | 297.3 | 420.8 | 406.2
2732.1 | 2493.1 | -5.4 | 0 | 0 | 303.4 | 264.6 | 240.8 | 237.1 | 33.7 | 46.4 | 17.1 | 77.5 | 4.5 | 230.8 | 9.8 | 75.2 | 48.9 | 41.2 | 54.8 | 48.4 | 55.8 | 63.9 | 75.1 | 97.9 | 79.1 | 41.6 | 46.9 | 271.5 | 301.4 | 349.3 | 52.3 | 241.9 | 45.2 | 65.6 | 44.2 | 298.4 | 331.9 | 247 | 394.6 | 297.1 | 420.4 | 406
2733.1 | 2494.1 | -5.3 | 0 | 0 | 303 | 264.2 | 240.7 | 237 | 33.3 | 46.4 | 17.1 | 77.4 | 4.6 | 230 | 9.7 | 74.9 | 48.8 | 41.1 | 54.7 | 48.3 | 55.7 | 63.7 | 74.9 | 98.3 | 78.8 | 41.6 | 46.8 | 271.4 | 301.3 | 349.1 | 52.2 | 241.7 | 44.9 | 65.6 | 44.2 | 298.3 | 331.5 | 246.8 | 394.4 | 296.8 | 420.1 | 405.8
2734.1 | 2495.1 | -5.2 | 0 | 0 | 302.6 | 263.5 | 240.7 | 237 | 33.5 | 46.3 | 17.1 | 77.3 | 4.7 | 213.5 | 9.1 | 74.7 | 49 | 41.2 | 54.6 | 48.4 | 55.6 | 63.6 | 74.9 | 99.1 | 79.1 | 41.5 | 46.8 | 271.8 | 300.8 | 348.9 | 52.1 | 241.6 | 45.1 | 65.4 | 43.8 | 298.1 | 332 | 246.5 | 394.2 | 296.6 | 419.7 | 405.6
2735.1 | 2496.1 | -4.7 | 0 | 0 | 302.2 | 263 | 240.7 | 236.9 | 33.8 | 46.3 | 17.2 | 77.1 | 5 | 221.1 | 8.1 | 74.4 | 49.1 | 41 | 54.6 | 48.4 | 55.6 | 63.5 | 74.9 | 99.3 | 79.2 | 41.5 | 46.7 | 272.3 | 300.6 | 348.7 | 52 | 241.6 | 45.6 | 65.5 | 43.8 | 298 | 331.9 | 246.3 | 394 | 296.4 | 419.4 | 405.4
2736.1 | 2497.1 | -4.5 | 0 | 0 | 301.9 | 263 | 240.8 | 236.8 | 34 | 46.2 | 17.2 | 77 | 5.4 | 245 | 8.9 | 74.1 | 48.6 | 40.9 | 54.6 | 48 | 55.6 | 63.5 | 74.7 | 99.6 | 79 | 41.5 | 46.6 | 272.7 | 300.3 | 348.5 | 52.1 | 241.5 | 44.8 | 65.4 | 43.9 | 297.8 | 331.7 | 246.1 | 393.8 | 296.2 | 419.1 | 405.2
2737.1 | 2498.1 | -4.9 | 0 | 0 | 301.8 | 263.1 | 240.7 | 236.7 | 33.1 | 46.2 | 17.2 | 76.9 | 5.7 | 231.9 | 8.5 | 73.8 | 48.4 | 40.8 | 54.5 | 48.1 | 55.5 | 63.5 | 74.6 | 99.9 | 78.7 | 41.4 | 46.5 | 272.5 | 300.3 | 348.3 | 51.9 | 241.4 | 44.6 | 65.4 | 44.3 | 297.7 | 331.4 | 245.8 | 393.6 | 296 | 418.7 | 405
2738.1 | 2499.1 | -5.4 | 0 | 0 | 301.5 | 263 | 240.7 | 236.6 | 32.9 | 46.2 | 17.2 | 76.9 | 5.3 | 257.2 | 9.3 | 73.5 | 47.9 | 40.8 | 54.5 | 47.7 | 55.5 | 63.3 | 74.2 | 99.8 | 78.8 | 41.4 | 46.5 | 272.5 | 299.8 | 348.2 | 51.9 | 241.3 | 44.5 | 65.4 | 44.1 | 297.5 | 331.4 | 245.6 | 393.3 | 295.8 | 418.4 | 404.7
2739.1 | 2500.1 | -5.7 | 0 | 0 | 301.5 | 262.9 | 240.5 | 236.5 | 33.3 | 46.2 | 17.2 | 76.9 | 4.8 | 227.6 | 9.8 | 73.2 | 48.2 | 40.6 | 54.5 | 47.6 | 55.5 | 63.3 | 72.4 | 99.8 | 78.6 | 41.4 | 46.5 | 272.4 | 299.4 | 348 | 51.9 | 241.2 | 44.9 | 65.4 | 43.6 | 297.4 | 330.8 | 245.3 | 393.2 | 295.6 | 418.1 | 404.5
2740.1 | 2501.1 | -5.6 | 0 | 0 | 301.5 | 262.6 | 240.4 | 236.4 | 33.5 | 46.1 | 17.2 | 76.9 | 4.5 | 223.4 | 8.4 | 73 | 48.1 | 40.4 | 54.4 | 47.1 | 55.4 | 63.3 | 73 | 98.8 | 78.8 | 41.3 | 46.4 | 271.9 | 299.3 | 347.8 | 51.7 | 240.9 | 44.7 | 65.3 | 43.7 | 297.3 | 330.7 | 245.1 | 393 | 295.4 | 417.8 | 404.3
2741.1 | 2502.1 | -5.6 | 0 | 0 | 301.3 | 262.4 | 240.4 | 236.3 | 33.5 | 46.1 | 17.2 | 76.8 | 4.4 | 242.5 | 9.2 | 72.7 | 48.1 | 40.3 | 54.4 | 47 | 55.4 | 63.2 | 73.1 | 98 | 78.8 | 41.2 | 46.4 | 271.4 | 299.3 | 347.6 | 51.7 | 240.5 | 44 | 65.2 | 43.9 | 297.1 | 330.8 | 244.8 | 392.8 | 295.2 | 417.4 | 404.1
2742.1 | 2503.1 | -5.5 | 0 | 0 | 300.9 | 262.2 | 240.4 | 236.3 | 32.8 | 46.1 | 17.2 | 76.7 | 4.7 | 248.6 | 11.2 | 72.5 | 48 | 40.1 | 54.3 | 47 | 55.3 | 63 | 73.5 | 97.2 | 78.9 | 41.1 | 46.4 | 271.9 | 299.4 | 347.4 | 51.8 | 240 | 44.4 | 65.1 | 44.5 | 297 | 330.6 | 244.6 | 392.6 | 295 | 417.1 | 403.9
2743.1 | 2504.1 | -5.4 | 0 | 0 | 300.6 | 262.3 | 240.2 | 236.2 | 33.2 | 46 | 17.2 | 76.8 | 3.7 | 242.5 | 11.2 | 72.2 | 47.9 | 40.1 | 54.3 | 46.8 | 55.2 | 63 | 73.8 | 98 | 78.8 | 41.1 | 46.2 | 272.2 | 299.1 | 347.2 | 51.8 | 239.5 | 44 | 65 | 44.1 | 296.8 | 330.3 | 244.3 | 392.4 | 294.8 | 416.8 | 403.7
2744.1 | 2505.1 | -5.4 | 0 | 0 | 300.3 | 262.2 | 240.1 | 236 | 33.2 | 46 | 17.2 | 76.7 | 3.8 | 242.7 | 10.3 | 71.9 | 47.9 | 40 | 54.2 | 47 | 55.1 | 62.9 | 74.1 | 98.9 | 78.4 | 41.1 | 46.1 | 272.7 | 298.6 | 347 | 51.8 | 239.1 | 43.8 | 65 | 44 | 296.7 | 329.8 | 244.1 | 392.2 | 294.6 | 416.4 | 403.5
2745.1 | 2506.1 | -5.4 | 0 | 0 | 300.2 | 262.1 | 240 | 235.8 | 35.4 | 46 | 17.2 | 76.6 | 4.6 | 225.1 | 9.1 | 71.7 | 48 | 39.7 | 54.1 | 47.5 | 55 | 62.7 | 74.2 | 99.2 | 78.4 | 41 | 45.9 | 273.2 | 298.2 | 346.8 | 51.8 | 238.8 | 43.8 | 65 | 43.9 | 296.5 | 329.5 | 243.9 | 392 | 294.4 | 416.1 | 403.3
2746.1 | 2507.1 | -5.5 | 0 | 0 | 300 | 262 | 240 | 235.7 | 34.5 | 46 | 17.2 | 76.6 | 5.3 | 247.5 | 9.1 | 71.4 | 48.4 | 39.7 | 54.1 | 47.4 | 54.9 | 62.7 | 74 | 99.2 | 78.4 | 41 | 46.1 | 273.1 | 297.9 | 346.6 | 51.8 | 238.6 | 43.3 | 65 | 44.1 | 296.4 | 329.6 | 243.6 | 391.8 | 294.2 | 415.8 | 403
2747.1 | 2508.1 | -5.4 | 0 | 0 | 299.9 | 261.7 | 239.9 | 235.4 | 34.2 | 46 | 17.2 | 76.5 | 5.4 | 229.2 | 8.5 | 71.2 | 48.7 | 39.6 | 54 | 47.4 | 54.9 | 62.6 | 73.7 | 98.9 | 77.3 | 41 | 45.9 | 272.9 | 297.8 | 346.4 | 51.5 | 238.4 | 43.5 | 65.1 | 44.2 | 296.2 | 328.8 | 243.3 | 391.7 | 294 | 415.5 | 402.8
2748.1 | 2509.1 | -5.5 | 0 | 0 | 299.6 | 261.5 | 239.6 | 235.2 | 32.7 | 46 | 17.2 | 76.4 | 5.2 | 243.2 | 8.8 | 70.9 | 48.6 | 39.3 | 54 | 47.4 | 54.8 | 62.5 | 73.7 | 99.2 | 77 | 40.9 | 45.9 | 273 | 297.2 | 346.2 | 51.4 | 238.2 | 43.2 | 65.1 | 43.9 | 296.1 | 328.3 | 243.1 | 391.5 | 293.8 | 415.1 | 402.6
2749.1 | 2510.1 | -5.5 | 0 | 0 | 299.5 | 261.5 | 239.5 | 234.9 | 34.8 | 46 | 17.2 | 76.4 | 5.5 | 248.3 | 9.9 | 70.7 | 48.3 | 39 | 53.9 | 47.6 | 54.7 | 62.3 | 73.9 | 99.1 | 77.3 | 40.8 | 45.9 | 273.6 | 297.2 | 346 | 51.3 | 237.9 | 43.3 | 65.1 | 43.7 | 295.9 | 328.1 | 242.8 | 391.3 | 293.6 | 414.8 | 402.4
2750.1 | 2511.1 | -5.6 | 0 | 0 | 299.6 | 261.5 | 239.5 | 234.7 | 34 | 45.9 | 17.2 | 76.3 | 6.2 | 246.4 | 11.1 | 70.4 | 48.3 | 38.8 | 53.9 | 47.7 | 54.6 | 62.3 | 73.9 | 99.1 | 77.5 | 40.8 | 45.9 | 273.9 | 296.9 | 345.8 | 51.2 | 237.5 | 42.7 | 65.1 | 43.7 | 295.8 | 327.4 | 242.6 | 391 | 293.4 | 414.5 | 402.2
2751.1 | 2512.1 | -5.7 | 0 | 0 | 299.2 | 261.3 | 239.2 | 234.3 | 33.5 | 45.9 | 17.2 | 76.2 | 5.9 | 242.8 | 11.5 | 70.2 | 48.9 | 38.7 | 53.9 | 47.4 | 54.5 | 62.3 | 73.6 | 99.2 | 77.1 | 40.7 | 45.9 | 274.3 | 296.4 | 345.6 | 51.1 | 236.6 | 43.1 | 65 | 44.1 | 295.6 | 327 | 242.3 | 390.8 | 293.2 | 414.2 | 402
2752.1 | 2513.1 | -5.8 | 0 | 0 | 299.1 | 261 | 238.9 | 234 | 32.6 | 45.8 | 17.2 | 76.2 | 5.6 | 247.6 | 11.1 | 70 | 49.4 | 38.5 | 53.8 | 47.1 | 54.4 | 62.2 | 73.6 | 99.2 | 76.6 | 40.6 | 45.9 | 274.6 | 296.9 | 345.4 | 51.1 | 235.8 | 43 | 65 | 43.8 | 295.5 | 326.7 | 242.1 | 390.6 | 293 | 413.8 | 401.8
2753.1 | 2514.1 | -5.8 | 0 | 0 | 298.9 | 260.6 | 238.7 | 233.7 | 31.4 | 45.8 | 17.3 | 76.2 | 5.5 | 232 | 10.4 | 69.7 | 49.6 | 38.5 | 53.8 | 47.4 | 54.3 | 62.1 | 73.4 | 99.2 | 76.2 | 40.5 | 45.8 | 275 | 296.4 | 345.2 | 51.1 | 235.5 | 43.1 | 64.9 | 43.5 | 295.4 | 326.5 | 241.9 | 390.4 | 292.8 | 413.5 | 401.6
2754.1 | 2515.1 | -5.8 | 0 | 0 | 298.5 | 260.4 | 238.5 | 233.4 | 30.3 | 45.7 | 17.3 | 76.1 | 4.4 | 244.8 | 11.1 | 69.5 | 50.1 | 38.6 | 53.8 | 47.4 | 54.3 | 62 | 73.6 | 99.1 | 75.7 | 40.4 | 45.9 | 275.3 | 296.5 | 345 | 51.1 | 235.2 | 43.2 | 64.8 | 43.1 | 295.2 | 326.2 | 241.7 | 390.2 | 292.7 | 413.2 | 401.4
2755.1 | 2516.1 | -5.9 | 0 | 0 | 298.3 | 260.2 | 238.4 | 233.1 | 31.7 | 45.7 | 17.3 | 76.1 | 4.5 | 254.8 | 12.3 | 69.3 | 50.4 | 38.7 | 53.7 | 47.4 | 54.2 | 61.9 | 73.6 | 99.1 | 75.4 | 40.3 | 45.8 | 275.8 | 297 | 344.8 | 51 | 235.2 | 42.9 | 64.8 | 43.7 | 295.1 | 326.2 | 241.5 | 390 | 292.4 | 412.9 | 401.1
2756.1 | 2517.1 | -5.9 | 0 | 0 | 298.1 | 259.9 | 238.2 | 232.9 | 32.7 | 45.7 | 17.3 | 76.1 | 4.6 | 244.7 | 10.9 | 69 | 50.6 | 38.7 | 53.7 | 47.5 | 54.1 | 61.7 | 73.8 | 98.9 | 75 | 40.2 | 45.9 | 276.1 | 296.4 | 344.7 | 50.9 | 235.1 | 43.1 | 64.8 | 44.2 | 294.9 | 326 | 241.2 | 389.8 | 292.2 | 412.5 | 400.9
2757.1 | 2518.1 | -5.8 | 0 | 0 | 297.9 | 259.2 | 238 | 232.7 | 32.1 | 45.6 | 17.3 | 76 | 4.7 | 264.1 | 9.5 | 68.8 | 50.5 | 38.6 | 53.7 | 47.5 | 54 | 61.7 | 73.8 | 98.8 | 74.8 | 40 | 45.9 | 276.3 | 295.8 | 344.5 | 50.9 | 235.2 | 43.3 | 64.7 | 44.1 | 294.8 | 325.8 | 241 | 389.6 | 292 | 412.2 | 400.7
2758.1 | 2519.1 | -5.6 | 0 | 0 | 297.8 | 258.4 | 237.9 | 232.5 | 32.2 | 45.6 | 17.3 | 75.9 | 4.6 | 267.7 | 8.1 | 68.6 | 50 | 38.5 | 53.6 | 47.5 | 54 | 61.7 | 73.5 | 98.6 | 74.8 | 39.8 | 46 | 276.5 | 295.6 | 344.3 | 51 | 235.2 | 42.9 | 64.6 | 43.5 | 294.7 | 325.6 | 240.9 | 389.4 | 291.8 | 411.9 | 400.5
2759.1 | 2520.1 | -5.5 | 0 | 0 | 297.7 | 257.9 | 237.8 | 232.4 | 32.3 | 45.6 | 17.3 | 75.9 | 4.6 | 255.8 | 8.7 | 68.4 | 49.9 | 38.5 | 53.6 | 47.2 | 53.9 | 61.6 | 73.5 | 97.3 | 74.8 | 39.6 | 46.1 | 276.8 | 295.5 | 344.1 | 51 | 235.6 | 42.7 | 64.5 | 43.4 | 294.5 | 325.4 | 240.7 | 389.2 | 291.6 | 411.6 | 400.3
2760.1 | 2521.1 | -5.4 | 0 | 0 | 297.4 | 257.3 | 237.6 | 232.2 | 33.3 | 45.6 | 17.3 | 76 | 5.1 | 270.9 | 10.4 | 68.2 | 49.7 | 38.8 | 53.5 | 46.8 | 53.9 | 61.4 | 73.6 | 97.1 | 74.7 | 39.6 | 46.2 | 276.8 | 295.6 | 343.9 | 50.9 | 236 | 43.1 | 64.4 | 43.8 | 294.4 | 325.1 | 240.6 | 389 | 291.4 | 411.2 | 400.1
2761.1 | 2522.1 | -5.4 | 0 | 0 | 297.2 | 257.1 | 237.3 | 232 | 35.3 | 45.5 | 17.3 | 76 | 4.5 | 270.8 | 10.4 | 67.9 | 49.2 | 38.9 | 53.4 | 46.7 | 53.8 | 61.4 | 72.9 | 97.7 | 74.5 | 39.5 | 46.3 | 277 | 295.6 | 343.7 | 50.9 | 236.1 | 42.9 | 64.3 | 44.1 | 294.2 | 324.9 | 240.5 | 388.9 | 291.3 | 410.9 | 399.9
2762.1 | 2523.1 | -5.5 | 0 | 0 | 297.2 | 257 | 237.2 | 231.9 | 35 | 45.5 | 17.3 | 75.9 | 4.5 | 243.3 | 9.9 | 67.7 | 48.9 | 38.9 | 53.4 | 46.6 | 53.8 | 61.3 | 73 | 97.9 | 74.5 | 39.4 | 46.2 | 277.3 | 295 | 343.5 | 50.7 | 236.3 | 43 | 64.3 | 44.5 | 294.1 | 324.9 | 240.4 | 388.6 | 291.1 | 410.6 | 399.7
2763.1 | 2524.1 | -5.6 | 0 | 0 | 297.1 | 256.8 | 237.2 | 231.7 | 32 | 45.5 | 17.3 | 75.9 | 5.4 | 282.8 | 9.6 | 67.5 | 48.9 | 38.6 | 53.3 | 46.8 | 53.6 | 61.3 | 73.1 | 98.2 | 74.4 | 39.3 | 46.2 | 277.5 | 295.3 | 343.3 | 50.7 | 236.3 | 43.4 | 64.3 | 44.6 | 293.9 | 324.9 | 240.2 | 388.4 | 290.9 | 410.3 | 399.5
2764.1 | 2525.1 | -5.6 | 0 | 0 | 296.8 | 256.6 | 237.3 | 231.4 | 33.6 | 45.5 | 17.3 | 75.9 | 6.2 | 270.3 | 14.3 | 67.3 | 48.9 | 38.3 | 53.2 | 46.4 | 53.5 | 61.3 | 72.9 | 98.2 | 74.5 | 39.2 | 46.2 | 277 | 295.2 | 343.1 | 50.6 | 236.4 | 43.6 | 64.2 | 43.9 | 293.8 | 324.7 | 240 | 388.2 | 290.7 | 410 | 399.2
2765.1 | 2526.1 | -5.6 | 0 | 0 | 296.3 | 256.7 | 237.1 | 231.1 | 33.6 | 45.5 | 17.3 | 75.8 | 6.7 | 263.4 | 20.2 | 67.1 | 49.5 | 38.4 | 53.2 | 46.6 | 53.4 | 61.1 | 72.7 | 97.6 | 74.2 | 39.2 | 46.2 | 276.9 | 294.9 | 342.9 | 50.6 | 236.5 | 43.5 | 64.1 | 43.9 | 293.7 | 324.7 | 239.9 | 388 | 290.5 | 409.7 | 399
2766.1 | 2527.1 | -5.7 | 0 | 0 | 296 | 256.8 | 237 | 230.8 | 32.8 | 45.5 | 17.3 | 75.8 | 6.2 | 262.3 | 20.9 | 66.9 | 50.2 | 38.5 | 53.1 | 46.6 | 53.2 | 61.1 | 72.6 | 96.1 | 74.1 | 39.1 | 46.2 | 276.5 | 294.4 | 342.8 | 50.6 | 236.5 | 43.2 | 64 | 44.1 | 293.5 | 324.4 | 239.7 | 387.9 | 290.3 | 409.3 | 398.8
2767.1 | 2528.1 | -6.1 | 0 | 0 | 295.6 | 256.7 | 237 | 230.5 | 33.5 | 45.4 | 17.3 | 75.8 | 5.7 | 256.7 | 18.4 | 66.7 | 50.5 | 38.6 | 53 | 46.6 | 53 | 61 | 72.2 | 96.6 | 74.4 | 39.1 | 46.2 | 276.3 | 294.1 | 342.6 | 50.6 | 236.4 | 43.3 | 64 | 44.1 | 293.4 | 324.2 | 239.5 | 387.7 | 290.1 | 409 | 398.6
2768.1 | 2529.1 | -6.2 | 0 | 0 | 295.5 | 256.5 | 237 | 230.3 | 33.5 | 45.4 | 17.3 | 75.8 | 4.5 | 255.7 | 16.8 | 66.5 | 50.6 | 38.7 | 52.9 | 46.8 | 52.9 | 60.9 | 72 | 96.4 | 74.4 | 39.1 | 46 | 276.7 | 293.6 | 342.4 | 49.7 | 236.1 | 43.1 | 64 | 43.8 | 293.3 | 323.7 | 239.4 | 387.5 | 289.9 | 408.7 | 398.4
2769.1 | 2530.1 | -6 | 0 | 0 | 295.6 | 256.2 | 236.9 | 230.2 | 33.4 | 45.4 | 17.3 | 75.8 | 3.3 | 249.1 | 15.2 | 66.3 | 50.7 | 38.8 | 52.8 | 46.7 | 52.8 | 61 | 71.8 | 97 | 73.6 | 39.1 | 45.8 | 276.8 | 293.7 | 342.2 | 49.9 | 235.8 | 43.2 | 64 | 43.8 | 293.1 | 323.1 | 239.2 | 387.3 | 289.7 | 408.4 | 398.2
2770.1 | 2531.1 | -5.9 | 0 | 0 | 295.5 | 256 | 236.7 | 230 | 32.9 | 45.4 | 17.3 | 75.7 | 3.2 | 245.3 | 14.2 | 66.1 | 50.4 | 38.9 | 52.7 | 46.4 | 52.7 | 60.9 | 72 | 97.3 | 73.2 | 39.1 | 45.8 | 277.3 | 293.5 | 342 | 50.3 | 235.4 | 42.7 | 63.9 | 44.4 | 293 | 322.6 | 239.1 | 387.2 | 289.5 | 408.1 | 398
2771.1 | 2532.1 | -5.8 | 0 | 0 | 295.4 | 255.7 | 236.6 | 229.7 | 32.6 | 45.4 | 17.3 | 75.7 | 3.6 | 245.4 | 13.6 | 65.9 | 49.9 | 39 | 52.6 | 46.6 | 52.6 | 60.8 | 72.2 | 97.5 | 73.2 | 39 | 45.8 | 277.9 | 293.8 | 341.8 | 50.5 | 235.4 | 42.9 | 63.7 | 44.2 | 292.8 | 322.2 | 239 | 387 | 289.3 | 407.7 | 397.8
2772.1 | 2533.1 | -5.6 | 0 | 0 | 295.3 | 255.3 | 236.5 | 229.4 | 35.1 | 45.3 | 17.4 | 75.6 | 4.3 | 255.1 | 12.6 | 65.7 | 49.6 | 39.1 | 52.5 | 46.6 | 52.5 | 60.7 | 72.3 | 97.7 | 73.2 | 38.9 | 45.6 | 278.5 | 293.5 | 341.6 | 50.5 | 235.5 | 42.6 | 63.7 | 43.6 | 292.7 | 322.1 | 238.8 | 386.8 | 289.1 | 407.4 | 397.6
2773.1 | 2534.1 | -5.6 | 0 | 0 | 295.3 | 254.8 | 236.3 | 229.1 | 35.6 | 45.2 | 17.4 | 75.6 | 4.3 | 266.4 | 12.9 | 65.5 | 49.6 | 39.1 | 52.5 | 46.5 | 52.4 | 60.6 | 71.8 | 97.6 | 73.4 | 38.9 | 45.7 | 278.8 | 293 | 341.4 | 50.4 | 235.4 | 43 | 63.7 | 43.6 | 292.6 | 321.6 | 238.7 | 386.5 | 288.9 | 407.1 | 397.4
2774.1 | 2535.1 | -5.5 | 0 | 0 | 295 | 254.2 | 236.1 | 229 | 33.7 | 45.1 | 17.4 | 75.5 | 5 | 266 | 12 | 65.3 | 49.4 | 39.2 | 52.5 | 46.5 | 52.4 | 60.5 | 71.9 | 97.5 | 73.4 | 38.9 | 45.5 | 278.9 | 292.9 | 341.3 | 50.4 | 235.3 | 43.5 | 63.7 | 43.7 | 292.4 | 321.7 | 238.6 | 386.3 | 288.7 | 406.8 | 397.2
2775.1 | 2536.1 | -5.5 | 0 | 0 | 294.3 | 253.8 | 236.1 | 228.9 | 32.9 | 45 | 17.4 | 75.4 | 4.8 | 270.1 | 11.7 | 65.1 | 49.7 | 39.1 | 52.4 | 46.5 | 52.3 | 60.4 | 71.5 | 97.2 | 73.3 | 38.9 | 45.6 | 279.2 | 293.3 | 341.1 | 50.4 | 234.2 | 43.5 | 63.2 | 43.6 | 292.3 | 321.5 | 238.5 | 386.1 | 288.5 | 406.5 | 397
2776.1 | 2537.1 | -5.5 | 0 | 0 | 293.9 | 253.5 | 236.1 | 228.8 | 39.8 | 44.9 | 17.4 | 75.4 | 4.5 | 268.4 | 12.3 | 65 | 49.7 | 39.1 | 52.4 | 46.5 | 52.2 | 60.4 | 71.6 | 97 | 72.9 | 38.8 | 45.6 | 279.2 | 292.4 | 340.9 | 39.2 | 230.4 | 42.9 | 47.6 | 43.4 | 292.1 | 321.3 | 238.4 | 385.8 | 288.3 | 406.2 | 396.8
2777.1 | 2538.1 | -5.4 | 0 | 0 | 293.8 | 253.1 | 236.2 | 228.6 | 50.6 | 44.9 | 17.4 | 75.3 | 4.6 | 262.7 | 12.6 | 64.8 | 49.5 | 39.1 | 52.3 | 46.2 | 52.1 | 60.3 | 70.9 | 96.8 | 73 | 38.6 | 45.6 | 279.1 | 291.7 | 340.7 | 36.6 | 228.9 | 41.8 | 48 | 43.4 | 292 | 321.2 | 238.3 | 385.6 | 288.1 | 405.9 | 396.5
2778.1 | 2539.1 | -5.5 | 0 | 0 | 293.7 | 252.7 | 236.1 | 228.4 | 58.4 | 44.8 | 17.4 | 75.2 | 4.3 | 266.5 | 13.4 | 64.6 | 49.5 | 39.2 | 52.2 | 46.2 | 52.1 | 60.3 | 72 | 96.7 | 73 | 38.6 | 45.6 | 279.4 | 291.9 | 340.5 | 37.4 | 229 | 41.5 | 48.7 | 42.9 | 291.9 | 321 | 238.1 | 385.4 | 288 | 405.6 | 396.3
2779.1 | 2540.1 | -5.6 | 0 | 0 | 293.7 | 252.5 | 235.8 | 228.3 | 62.7 | 44.7 | 17.4 | 75.2 | 4.2 | 274.4 | 13.2 | 64.4 | 49.6 | 39.3 | 52.1 | 46.2 | 52.1 | 60.3 | 72.5 | 96.3 | 73.6 | 38.6 | 45.6 | 280 | 291.4 | 340.4 | 38.3 | 230.5 | 42 | 50.4 | 43.3 | 291.7 | 320.9 | 238 | 385.2 | 287.8 | 405.2 | 396.1
2780.1 | 2541.1 | -5.6 | 0 | 0 | 293.6 | 252.7 | 235.8 | 228.1 | 64.7 | 44.7 | 17.4 | 75.1 | 4.4 | 273.1 | 12.5 | 64.2 | 49.7 | 39.4 | 52 | 46.3 | 52 | 60.2 | 72.8 | 96.3 | 75 | 38.7 | 45.4 | 280.2 | 290.8 | 340.2 | 39 | 231.8 | 42.4 | 51.6 | 43.8 | 291.6 | 320.9 | 237.9 | 385 | 287.6 | 404.9 | 395.9
2781.1 | 2542.1 | -5.6 | 0 | 0 | 293.7 | 252.7 | 235.9 | 228 | 66.1 | 44.7 | 17.4 | 75 | 4.6 | 268.6 | 11.6 | 64 | 50.4 | 39.3 | 52 | 46.3 | 51.9 | 60.3 | 73 | 95.9 | 75.8 | 38.7 | 45.4 | 280.4 | 290.8 | 340 | 40.2 | 233.1 | 44 | 52.6 | 43.8 | 291.5 | 320.7 | 237.8 | 384.8 | 287.5 | 404.6 | 395.7
2782.1 | 2543.1 | -5.6 | 0 | 0 | 293.4 | 252.6 | 235.9 | 227.9 | 66.6 | 44.6 | 17.4 | 74.9 | 4.9 | 264.7 | 11 | 63.8 | 50.8 | 39 | 52 | 46.3 | 51.7 | 60.2 | 73.4 | 95.9 | 75.9 | 38.6 | 45.3 | 280 | 290.6 | 339.8 | 41.3 | 234.3 | 44.3 | 53.4 | 43.5 | 291.4 | 320.3 | 237.6 | 384.6 | 287.3 | 404.3 | 395.5
2783.1 | 2544.1 | -5.5 | 0 | 0 | 293.3 | 252.7 | 235.9 | 228 | 66.6 | 44.6 | 17.4 | 74.9 | 4.7 | 268.1 | 11.3 | 63.7 | 51 | 38.9 | 51.9 | 46.3 | 51.7 | 60.2 | 73.5 | 95.7 | 75.9 | 38.6 | 45.4 | 280.3 | 290.9 | 339.7 | 42.1 | 235.9 | 44.8 | 54.1 | 43.2 | 291.2 | 320.1 | 237.5 | 384.4 | 287.1 | 404 | 395.3
2784.1 | 2545.1 | -5.5 | 0 | 0 | 293.4 | 252.7 | 235.8 | 228 | 66.6 | 44.5 | 17.4 | 74.9 | 4.8 | 259.3 | 12.1 | 63.5 | 51 | 38.6 | 51.9 | 46.3 | 51.7 | 60.1 | 73.5 | 95.7 | 75.7 | 38.5 | 45.4 | 280.6 | 290.7 | 339.5 | 43.2 | 237.6 | 45.1 | 54.7 | 43.4 | 291.1 | 319.8 | 237.3 | 384.2 | 286.9 | 403.7 | 395.1
2785.1 | 2546.1 | -5.5 | 0 | 0 | 293.4 | 252.6 | 235.8 | 228 | 66.5 | 44.6 | 17.4 | 74.8 | 4.9 | 260 | 13.9 | 63.3 | 51.2 | 38.5 | 51.8 | 46.3 | 51.7 | 60.1 | 73.9 | 96.2 | 75.9 | 38.5 | 45.5 | 281.1 | 290.8 | 339.3 | 44 | 238.9 | 45.8 | 55.2 | 43.5 | 291 | 320.1 | 237.3 | 384 | 286.8 | 403.4 | 394.9
2786.1 | 2547.1 | -5.5 | 0 | 0 | 293.3 | 252.6 | 235.8 | 227.9 | 66.4 | 44.6 | 17.4 | 74.8 | 5 | 266.1 | 14.4 | 63.1 | 51.2 | 38.2 | 51.8 | 46.3 | 51.7 | 60.1 | 74 | 96.5 | 76.1 | 38.5 | 45.6 | 281.9 | 290.5 | 339.1 | 44.8 | 240.1 | 45.9 | 55.7 | 43.4 | 290.8 | 320.8 | 237.2 | 383.8 | 286.6 | 403.1 | 394.7
2787.1 | 2548.1 | -5.3 | 0 | 0 | 293.2 | 252.5 | 235.8 | 227.8 | 66.3 | 44.6 | 17.4 | 74.8 | 4.5 | 261.7 | 14.3 | 63 | 50.8 | 37.9 | 51.7 | 46.3 | 51.6 | 60.2 | 74.3 | 96.5 | 76.2 | 38.4 | 45.7 | 283.1 | 291.4 | 338.9 | 45.5 | 241.6 | 46.7 | 56.1 | 43.5 | 290.7 | 320.7 | 237.2 | 383.6 | 286.4 | 402.8 | 394.5
2788.1 | 2549.1 | -4.8 | 0 | 0 | 293.2 | 252.3 | 236 | 227.7 | 66.3 | 44.6 | 17.4 | 74.8 | 4.8 | 253 | 14.2 | 62.8 | 50.8 | 37.9 | 51.7 | 46.4 | 51.4 | 60.1 | 74.4 | 96.5 | 75.9 | 38.4 | 45.8 | 283.8 | 292.4 | 338.8 | 46.2 | 243.2 | 49.8 | 56.6 | 43.6 | 290.6 | 320.5 | 237.1 | 383.4 | 286.2 | 402.5 | 394.3
2789.1 | 2550.1 | -5 | 0 | 0 | 293.2 | 252.4 | 236.1 | 227.6 | 66.3 | 44.5 | 17.4 | 74.8 | 4.4 | 260.4 | 13.2 | 62.6 | 50.9 | 37.9 | 51.6 | 46.4 | 51.3 | 60.1 | 74.5 | 96.5 | 75.5 | 38.4 | 45.9 | 284.5 | 292.4 | 338.6 | 46.8 | 244.5 | 51.7 | 57.1 | 43.8 | 290.5 | 320.5 | 237.1 | 383.2 | 286.1 | 402.2 | 394.1
2790.1 | 2551.1 | -5.1 | 0 | 0 | 293.3 | 252.7 | 236.2 | 227.6 | 66.3 | 44.5 | 17.4 | 74.8 | 4.3 | 256.8 | 12.9 | 62.5 | 51.3 | 37.9 | 51.5 | 46.4 | 51.3 | 60.1 | 74.8 | 96.3 | 75.7 | 38.3 | 45.9 | 285.5 | 292.9 | 338.4 | 47.5 | 245.7 | 53.5 | 57.5 | 44.1 | 290.4 | 319.8 | 237 | 382.9 | 285.9 | 401.9 | 393.9
2791.1 | 2552.1 | -5.2 | 0 | 0 | 293.2 | 252.9 | 236.2 | 227.5 | 66.2 | 44.4 | 17.5 | 74.8 | 3.9 | 244 | 13.2 | 62.3 | 51.5 | 38 | 51.4 | 46.4 | 51.2 | 60.1 | 75 | 96 | 75.5 | 38.3 | 46 | 285.9 | 292.1 | 338.2 | 48.1 | 246.7 | 55.5 | 58 | 44.5 | 290.3 | 319.4 | 237 | 382.7 | 285.7 | 401.6 | 393.7
2792.1 | 2553.1 | -5.4 | 0 | 0 | 293 | 253.1 | 236.1 | 227.5 | 66.3 | 44.3 | 17.5 | 74.8 | 3.8 | 254.4 | 11.8 | 62.2 | 51.7 | 38.1 | 51.4 | 46.4 | 51.2 | 60.1 | 75.1 | 95.8 | 75.8 | 38.3 | 46.1 | 285.7 | 291.8 | 338 | 48.7 | 247.6 | 57.1 | 58.5 | 44.8 | 290.1 | 318.9 | 237 | 382.5 | 285.6 | 401.3 | 393.5
2793.1 | 2554.1 | -5.5 | 0 | 0 | 292.9 | 253.2 | 236.2 | 227.4 | 66.6 | 44.3 | 17.5 | 74.7 | 4.1 | 256.8 | 10.7 | 62 | 51.9 | 38 | 51.3 | 46.4 | 51.2 | 60.1 | 75.2 | 95.8 | 76 | 38.3 | 46.2 | 285.1 | 291.5 | 337.9 | 49.3 | 248.4 | 58.1 | 59.1 | 45.2 | 290 | 318.4 | 236.9 | 382.3 | 285.4 | 401 | 393.3
2794.1 | 2555.1 | -5.5 | 0 | 0 | 293 | 253 | 236.2 | 227.3 | 66.9 | 44.2 | 17.5 | 74.7 | 4.9 | 249.5 | 10.8 | 61.8 | 51.3 | 38.2 | 51.3 | 46.4 | 51.2 | 60.2 | 75.2 | 95.8 | 76 | 38.3 | 46.3 | 284.9 | 290.3 | 337.7 | 49.6 | 249.3 | 59 | 59.6 | 45.4 | 289.9 | 317.8 | 236.9 | 382.1 | 285.2 | 400.7 | 393.1
2795.1 | 2556.1 | -5.5 | 0 | 0 | 293.2 | 252.7 | 236.1 | 227.3 | 66.9 | 44.2 | 17.5 | 74.7 | 4.9 | 249.2 | 10.5 | 61.7 | 51 | 38.2 | 51.2 | 46.2 | 51.3 | 60.2 | 75.2 | 95.9 | 75.6 | 38.3 | 46.5 | 284.9 | 290.3 | 337.5 | 50.4 | 250.1 | 59.8 | 60.1 | 45.8 | 289.8 | 317.9 | 236.8 | 381.9 | 285.1 | 400.4 | 392.9
2796.1 | 2557.1 | -5.5 | 0 | 0 | 293.1 | 252.6 | 235.9 | 227.2 | 66.6 | 44.2 | 17.5 | 74.6 | 6.1 | 262.6 | 10.2 | 61.5 | 50.7 | 38.1 | 51.2 | 46 | 51.3 | 60.3 | 75.2 | 95.9 | 75.1 | 38.2 | 46.5 | 284.8 | 290.3 | 337.4 | 50.8 | 251 | 60.4 | 60.6 | 46.1 | 289.7 | 317.7 | 236.7 | 381.6 | 284.9 | 400.1 | 392.7
2797.1 | 2558.1 | -5.5 | 0 | 0 | 292.9 | 252.6 | 235.7 | 227.2 | 66.3 | 44.1 | 17.5 | 74.5 | 5.7 | 265.2 | 10.4 | 61.4 | 50.8 | 38 | 51.1 | 45.8 | 51.2 | 60.4 | 75.2 | 95.7 | 74.7 | 38.2 | 46.6 | 284.7 | 289.8 | 337.2 | 50.8 | 251.7 | 60.8 | 61 | 46.5 | 289.6 | 317.7 | 236.7 | 381.4 | 284.7 | 399.8 | 392.5
2798.1 | 2559.1 | -5.5 | 0 | 0 | 292.8 | 252.6 | 235.8 | 227.3 | 66.1 | 44.1 | 17.5 | 74.5 | 5.9 | 260.1 | 9.7 | 61.2 | 51 | 37.8 | 51.1 | 45.6 | 51.2 | 60.5 | 75.4 | 95.7 | 74.1 | 38.2 | 46.7 | 284.8 | 290.1 | 337 | 50.9 | 252.4 | 61.1 | 61.4 | 46.6 | 289.5 | 317.6 | 236.6 | 381.1 | 284.6 | 399.5 | 392.3
2799.1 | 2560.1 | -5.6 | 0 | 0 | 292.6 | 252.8 | 236.8 | 227.2 | 66 | 44.1 | 17.5 | 74.4 | 5.3 | 261.2 | 10.5 | 61.1 | 51 | 37.8 | 51 | 45.4 | 51.1 | 60.6 | 75.7 | 95.6 | 73.9 | 38.2 | 46.8 | 284.7 | 290.9 | 336.8 | 51.2 | 253.1 | 61.4 | 61.7 | 47.3 | 289.4 | 317.4 | 236.5 | 380.9 | 284.4 | 399.2 | 392.1
2800.1 | 2561.1 | -5.8 | 0 | 0 | 292.4 | 252.8 | 236.9 | 227.1 | 65.9 | 44.1 | 17.5 | 74.3 | 5.7 | 257.5 | 10.1 | 60.9 | 51 | 37.7 | 51 | 45.3 | 51.1 | 60.5 | 75.8 | 95.6 | 73.5 | 38.2 | 46.9 | 284.9 | 291.1 | 336.7 | 52.1 | 253.7 | 61.7 | 62 | 48.1 | 289.3 | 317.2 | 236.4 | 380.6 | 284.2 | 398.9 | 391.9
2801.1 | 2562.1 | -5.9 | 0 | 0 | 292.3 | 252.8 | 237 | 226.9 | 65.8 | 44 | 17.5 | 74.3 | 5.9 | 225.2 | 9.4 | 60.7 | 51 | 37.6 | 50.9 | 45.2 | 51 | 60.6 | 76 | 95.7 | 73.4 | 38.2 | 47.1 | 285.2 | 290.1 | 336.5 | 52.3 | 254.2 | 61.8 | 62.4 | 48.1 | 289.1 | 316.9 | 236.3 | 380.3 | 284.1 | 398.7 | 391.7
2802.1 | 2563.1 | -5.9 | 0 | 0 | 292.4 | 252.9 | 237.1 | 226.9 | 65.8 | 44 | 17.5 | 74.2 | 7.1 | 228.2 | 8.2 | 60.6 | 50.9 | 37.5 | 50.8 | 45.1 | 50.9 | 60.6 | 76.1 | 95.5 | 73.3 | 38.2 | 47.2 | 285.5 | 289.7 | 336.3 | 52.3 | 254.7 | 61.9 | 62.7 | 48.1 | 289 | 317.1 | 236.3 | 380.1 | 283.9 | 398.4 | 391.5
2803.1 | 2564.1 | -6 | 0 | 0 | 292.4 | 253.1 | 237.2 | 226.9 | 65.7 | 44 | 17.5 | 74.1 | 7.3 | 251.6 | 7.3 | 60.5 | 51.2 | 37.2 | 50.8 | 44.9 | 50.8 | 60.6 | 75.8 | 95.4 | 73.1 | 38.2 | 47.4 | 285.7 | 289.4 | 336.2 | 52.4 | 255.1 | 62.2 | 63 | 48.5 | 288.9 | 316.9 | 236.2 | 379.8 | 283.7 | 398.1 | 391.3
2804.1 | 2565.1 | -6.2 | 0 | 0 | 291.9 | 253.3 | 237.3 | 226.9 | 65.4 | 44 | 17.5 | 74.1 | 7.3 | 246.6 | 8.6 | 60.3 | 51.1 | 37 | 50.7 | 44.8 | 50.7 | 60.6 | 75.8 | 95.2 | 72.8 | 38.2 | 47.5 | 285.7 | 289.1 | 336 | 52.5 | 255.5 | 62.4 | 63.2 | 49 | 288.8 | 316.7 | 236.2 | 379.6 | 283.6 | 397.8 | 391.1
2805.1 | 2566.1 | -6.2 | 0 | 0 | 291.5 | 253.4 | 237.3 | 226.8 | 65.3 | 44 | 17.5 | 74 | 6.3 | 246.7 | 10.7 | 60.2 | 51.3 | 36.9 | 50.7 | 44.7 | 50.7 | 60.6 | 76.2 | 95.1 | 72.7 | 38.2 | 47.5 | 285.7 | 289 | 335.8 | 52.8 | 255.9 | 62.5 | 63.6 | 49.1 | 288.7 | 316.8 | 236.1 | 379.4 | 283.4 | 397.5 | 390.9
2806.1 | 2567.1 | -6.2 | 0 | 0 | 291.4 | 253.4 | 237.2 | 226.8 | 65.3 | 44 | 17.5 | 73.9 | 5.6 | 255.4 | 15.3 | 60 | 51.8 | 36.8 | 50.6 | 44.7 | 50.7 | 60.7 | 76.2 | 95.1 | 72.8 | 38.2 | 47.6 | 285.8 | 288.5 | 335.6 | 53.1 | 256.3 | 62.6 | 63.9 | 49.5 | 288.6 | 316.8 | 236 | 379.1 | 283.2 | 397.2 | 390.7
2807.1 | 2568.1 | -6.4 | 0 | 0 | 291.3 | 253.4 | 237.2 | 226.8 | 65.4 | 44 | 17.6 | 73.8 | 5.6 | 254.1 | 19.5 | 59.9 | 52 | 36.6 | 50.6 | 44.6 | 50.7 | 60.7 | 76.3 | 95.1 | 72.5 | 38.2 | 47.7 | 286.2 | 288.7 | 335.5 | 53.4 | 256.6 | 62.8 | 64.3 | 49.6 | 288.5 | 316.6 | 236 | 378.8 | 283.1 | 396.9 | 390.5
2808.1 | 2569.1 | -6.4 | 0 | 0 | 291.4 | 253.4 | 237.2 | 226.9 | 65.6 | 44 | 17.6 | 73.8 | 5.1 | 250.5 | 18.9 | 59.8 | 52.4 | 36.5 | 50.6 | 44.5 | 50.6 | 60.9 | 76.5 | 94.9 | 72.2 | 38.3 | 47.8 | 286.7 | 289.1 | 335.3 | 53.6 | 256.9 | 62.8 | 64.5 | 49.9 | 288.4 | 316.6 | 235.9 | 378.6 | 282.9 | 396.6 | 390.3
2809.1 | 2570.1 | -6.3 | 0 | 0 | 291.4 | 253.1 | 237 | 226.9 | 65.8 | 43.9 | 17.6 | 73.7 | 5.6 | 256.7 | 19.2 | 59.7 | 52.6 | 36.5 | 50.5 | 44.4 | 50.5 | 60.8 | 76.7 | 94.7 | 71.9 | 38.3 | 47.9 | 286.6 | 288.4 | 335.1 | 54.5 | 257.2 | 63 | 64.8 | 50.3 | 288.3 | 316.5 | 235.9 | 378.3 | 282.8 | 396.4 | 390.1
2810.1 | 2571.1 | -6 | 0 | 0 | 291.3 | 253 | 236.9 | 226.7 | 65.9 | 43.9 | 17.6 | 73.6 | 6.1 | 267.5 | 16.8 | 59.5 | 52.8 | 36.3 | 50.4 | 44.4 | 50.5 | 60.9 | 76.9 | 94.6 | 71.9 | 38.3 | 48 | 286.4 | 288.1 | 335 | 55.1 | 257.4 | 63 | 65 | 50.5 | 288.2 | 316.3 | 235.8 | 378.1 | 282.6 | 396.1 | 389.9
2811.1 | 2572.1 | -6 | 0 | 0 | 291.2 | 252.8 | 236.8 | 226.7 | 65.7 | 43.8 | 17.6 | 73.5 | 6.3 | 261.3 | 15.7 | 59.4 | 53.1 | 36 | 50.4 | 44.3 | 50.4 | 60.9 | 76.9 | 94.3 | 71.9 | 38.3 | 48.1 | 286.5 | 287.7 | 334.8 | 54.9 | 257.6 | 63.2 | 65.3 | 50.8 | 288.1 | 316.1 | 235.8 | 377.9 | 282.5 | 395.8 | 389.7
2812.1 | 2573.1 | -5.8 | 0 | 0 | 291.1 | 252.7 | 236.9 | 226.6 | 66.1 | 43.7 | 17.6 | 73.4 | 6.9 | 276.2 | 14.9 | 59.3 | 53.3 | 36 | 50.3 | 44.2 | 50.3 | 61 | 77.2 | 94.1 | 71.6 | 38.3 | 48.2 | 286.6 | 287.6 | 334.6 | 54.9 | 257.8 | 63.3 | 65.5 | 51.4 | 288 | 316.1 | 235.7 | 377.6 | 282.3 | 395.5 | 389.5
2813.1 | 2574.1 | -5.8 | 0 | 0 | 291 | 252.5 | 236.9 | 226.6 | 66.4 | 43.6 | 17.6 | 73.3 | 7.4 | 264.9 | 18.5 | 59.2 | 53 | 35.9 | 50.3 | 44.1 | 50.2 | 61 | 77.2 | 94.1 | 71.3 | 38.3 | 48.3 | 286.3 | 286.8 | 334.5 | 54.9 | 257.9 | 63.4 | 65.7 | 51.7 | 287.9 | 316.1 | 235.7 | 377.4 | 282.2 | 395.2 | 389.3
2814.1 | 2575.1 | -5.9 | 0 | 0 | 291 | 252.4 | 236.9 | 226.6 | 66 | 43.6 | 17.6 | 73.1 | 6.6 | 262.6 | 17.9 | 59.1 | 52.9 | 35.8 | 50.3 | 44 | 50.2 | 61 | 77.4 | 93.8 | 71.4 | 38.4 | 48.3 | 285.8 | 287 | 334.3 | 54.9 | 258.2 | 63.6 | 65.8 | 51.8 | 287.8 | 315.7 | 235.6 | 377.1 | 282 | 394.9 | 389.1
2815.1 | 2576.1 | -6.1 | 0 | 0 | 291.1 | 252.4 | 236.9 | 226.6 | 66 | 43.5 | 17.6 | 73 | 6 | 265.3 | 20.7 | 59 | 52.8 | 35.8 | 50.2 | 44 | 50.3 | 61 | 77.4 | 93.4 | 71 | 38.4 | 48.4 | 286.1 | 286.5 | 334.1 | 55.1 | 258.4 | 63.6 | 66 | 52 | 287.7 | 315 | 235.5 | 376.9 | 281.9 | 394.7 | 388.9
2816.1 | 2577.1 | -6.1 | 0 | 0 | 291.1 | 252.3 | 236.9 | 226.6 | 66.2 | 43.4 | 17.6 | 72.8 | 6.1 | 256 | 22.7 | 58.9 | 52.7 | 35.8 | 50.2 | 43.9 | 50.2 | 61.1 | 77.5 | 93.2 | 70.6 | 38.4 | 48.5 | 285.8 | 286.5 | 334 | 55.3 | 258.5 | 63.7 | 66.1 | 52.3 | 287.6 | 314.9 | 235.4 | 376.7 | 281.7 | 394.4 | 388.7
2817.1 | 2578.1 | -6.2 | 0 | 0 | 291 | 252.3 | 236.9 | 226.6 | 66.3 | 43.4 | 17.6 | 72.7 | 6.2 | 258.2 | 19.7 | 58.8 | 52.5 | 35.7 | 50.2 | 43.9 | 50.2 | 61.1 | 77.5 | 93 | 70.5 | 38.4 | 48.6 | 285.9 | 286.3 | 333.8 | 55.4 | 258.7 | 63.8 | 66.3 | 52.8 | 287.4 | 314.8 | 235.3 | 376.4 | 281.6 | 394.1 | 388.5
2818.1 | 2579.1 | -6.3 | 0 | 0 | 291.2 | 252.3 | 236.9 | 226.5 | 66 | 43.3 | 17.6 | 72.6 | 6.7 | 266 | 17.7 | 58.7 | 52.7 | 35.4 | 50.1 | 43.9 | 50.2 | 61.1 | 77.7 | 92.7 | 70.4 | 38.5 | 48.7 | 286.2 | 286.5 | 333.6 | 55.6 | 258.9 | 63.9 | 66.5 | 52.9 | 287.3 | 314.7 | 235.3 | 376.2 | 281.4 | 393.8 | 388.3
2819.1 | 2580.1 | -6.2 | 0 | 0 | 291.2 | 252.3 | 236.8 | 226.5 | 65.8 | 43.3 | 17.6 | 72.5 | 7.8 | 264.8 | 17.4 | 58.6 | 52.8 | 35.1 | 50.1 | 43.8 | 50.1 | 61.1 | 78 | 92.7 | 70.4 | 38.5 | 48.7 | 286.2 | 285.4 | 333.5 | 55.7 | 259 | 63.9 | 66.6 | 53.4 | 287.2 | 314.5 | 235.2 | 376 | 281.3 | 393.5 | 388.1
2820.1 | 2581.1 | -6.3 | 0 | 0 | 291.1 | 252.4 | 236.7 | 226.6 | 65.6 | 43.2 | 17.6 | 72.3 | 7 | 259.5 | 17.4 | 58.5 | 52.7 | 34.9 | 50.1 | 43.8 | 50.1 | 61.1 | 78 | 92.4 | 70 | 38.5 | 48.8 | 286.3 | 285.3 | 333.3 | 55.9 | 259.1 | 64 | 66.8 | 54 | 287.1 | 314.5 | 235.2 | 375.7 | 281.1 | 393.3 | 387.9
2821.1 | 2582.1 | -6.3 | 0 | 0 | 291 | 252.3 | 236.7 | 226.6 | 65.6 | 43.1 | 17.6 | 72.2 | 6.1 | 253.8 | 16.6 | 58.4 | 53 | 34.8 | 50.1 | 43.8 | 50 | 61.2 | 78 | 92.4 | 69.9 | 38.5 | 48.9 | 286.3 | 285 | 333.1 | 56.1 | 259.1 | 63.8 | 67 | 54.4 | 287 | 314.1 | 235.2 | 375.5 | 281 | 393 | 387.7
2822.1 | 2583.1 | -6.1 | 0 | 0 | 290.8 | 252.2 | 236.7 | 226.7 | 65.9 | 43 | 17.6 | 72.1 | 5.8 | 254.3 | 18.1 | 58.3 | 53.3 | 34.6 | 50.1 | 43.7 | 50 | 61.3 | 77.9 | 92.4 | 70 | 38.6 | 48.9 | 286.4 | 284.3 | 333 | 56.3 | 259.2 | 64 | 67.1 | 54.7 | 286.9 | 313.6 | 235.1 | 375.2 | 280.8 | 392.7 | 387.5
2823.1 | 2584.1 | -6.1 | 0 | 0 | 290.9 | 251.9 | 236.9 | 226.7 | 66.3 | 43 | 17.6 | 72.1 | 5.7 | 251 | 19.3 | 58.2 | 52.7 | 34.4 | 50.1 | 43.7 | 50 | 61.4 | 78 | 92.4 | 70.3 | 38.6 | 48.9 | 286.2 | 285.2 | 332.8 | 56.4 | 259.3 | 63.8 | 67.3 | 54.8 | 286.8 | 313.4 | 235 | 375 | 280.6 | 392.4 | 387.3
2824.1 | 2585.1 | -6.3 | 0 | 0 | 290.9 | 251.6 | 236.9 | 226.7 | 65.8 | 43 | 17.6 | 72 | 5.9 | 254.5 | 18.8 | 58.1 | 52.4 | 34.4 | 50.1 | 43.7 | 49.9 | 61.5 | 78 | 92.3 | 70.3 | 38.7 | 49 | 286.2 | 285.2 | 332.6 | 56.6 | 259.4 | 64 | 67.4 | 55 | 286.7 | 313.1 | 234.9 | 374.7 | 280.5 | 392.2 | 387.1
2825.1 | 2586.1 | -6.4 | 0 | 0 | 290.8 | 251.4 | 236.5 | 226.7 | 66.1 | 43 | 17.6 | 72 | 5.3 | 256.4 | 19.7 | 58 | 52.3 | 34.3 | 50.1 | 43.6 | 49.7 | 61.6 | 78.3 | 92.2 | 70.4 | 38.7 | 49.1 | 286.4 | 284.6 | 332.5 | 56.8 | 259.4 | 64.2 | 67.6 | 55.3 | 286.6 | 312.2 | 234.8 | 374.5 | 280.3 | 391.9 | 386.9
2826.1 | 2587.1 | -6.4 | 0 | 0 | 290.8 | 251.1 | 236.3 | 226.8 | 66.8 | 42.9 | 17.6 | 71.9 | 6 | 254.2 | 18.3 | 57.9 | 51.8 | 34.3 | 50.1 | 43.6 | 49.6 | 61.6 | 78.4 | 92.1 | 70.2 | 38.7 | 49.1 | 286.7 | 283.8 | 332.3 | 57 | 259.3 | 64.4 | 67.8 | 55.7 | 286.5 | 311.5 | 234.5 | 374.2 | 280.2 | 391.6 | 386.7
2827.1 | 2588.1 | -6.3 | 0 | 0 | 290.5 | 250.4 | 236.4 | 226.9 | 66.3 | 42.8 | 17.6 | 71.9 | 6.4 | 260.6 | 17.1 | 57.8 | 51.8 | 34.1 | 50.1 | 43.6 | 49.6 | 61.7 | 78.5 | 92.3 | 70.5 | 38.8 | 49.2 | 286.9 | 283.6 | 332.2 | 57.1 | 259.3 | 64.5 | 67.9 | 55.9 | 286.4 | 311.3 | 234.3 | 373.9 | 280 | 391.3 | 386.5
2828.1 | 2589.1 | -6.3 | 0 | 0 | 290.3 | 249.8 | 236.5 | 226.9 | 65.7 | 42.8 | 17.6 | 71.8 | 5.9 | 261.6 | 15.8 | 57.8 | 51.8 | 34.1 | 50.1 | 43.5 | 49.6 | 61.7 | 78.6 | 92.2 | 70.3 | 38.8 | 49.2 | 287.3 | 283.7 | 332 | 57.2 | 259.2 | 64.5 | 68 | 56.1 | 286.3 | 311.4 | 234 | 373.7 | 279.9 | 391.1 | 386.3
2829.1 | 2590.1 | -6.3 | 0 | 0 | 290.3 | 249.5 | 236.5 | 226.9 | 65.7 | 42.8 | 17.7 | 71.7 | 4.7 | 255.7 | 17.2 | 57.7 | 51 | 34 | 50.1 | 43.5 | 49.5 | 61.7 | 78.5 | 92.1 | 70.2 | 38.9 | 49.3 | 287.5 | 282.7 | 331.8 | 57.4 | 259.3 | 64.6 | 68.2 | 56.2 | 286.2 | 311.1 | 233.7 | 373.4 | 279.7 | 390.8 | 386.1
2830.1 | 2591.1 | -6.4 | 0 | 0 | 290 | 249.6 | 236.6 | 226.8 | 66.2 | 42.7 | 17.7 | 71.6 | 4.3 | 265.1 | 16.3 | 57.6 | 51 | 33.9 | 50 | 43.5 | 49.5 | 61.9 | 78.5 | 91.9 | 70.2 | 38.9 | 49.3 | 287.4 | 282.7 | 331.7 | 57.5 | 259.3 | 64.6 | 68.2 | 56.6 | 286.1 | 311 | 233.5 | 373.2 | 279.6 | 390.5 | 385.9
2831.1 | 2592.1 | -6.3 | 0 | 0 | 289.7 | 249.7 | 236.5 | 226.7 | 67 | 42.8 | 17.7 | 71.6 | 5.1 | 263 | 15.2 | 57.5 | 51.3 | 33.7 | 50 | 43.5 | 49.5 | 61.9 | 78.7 | 91.9 | 69.9 | 39 | 49.4 | 287.5 | 282.8 | 331.5 | 57.6 | 259.4 | 64.7 | 68.4 | 56.8 | 286 | 310.8 | 233.2 | 373 | 279.4 | 390.2 | 385.7
2832.1 | 2593.1 | -6.2 | 0 | 0 | 289.6 | 249.6 | 236.2 | 226.6 | 68.4 | 42.8 | 17.7 | 71.5 | 6.9 | 256.6 | 15.3 | 57.5 | 51.2 | 33.5 | 50 | 43.5 | 49.5 | 61.9 | 78.9 | 92.1 | 69.5 | 39 | 49.4 | 287.8 | 282 | 331.4 | 57.8 | 259.4 | 64.5 | 68.4 | 57 | 285.9 | 310.6 | 233 | 372.7 | 279.3 | 390 | 385.5
2833.1 | 2594.1 | -6.1 | 0 | 0 | 289.4 | 249.3 | 235.9 | 226.6 | 70.8 | 42.8 | 17.7 | 71.4 | 6.9 | 268.8 | 15.3 | 57.4 | 51.2 | 33.4 | 50 | 43.4 | 49.4 | 61.9 | 78.8 | 92.2 | 69.5 | 39 | 49.5 | 287.9 | 281.8 | 331.2 | 57.9 | 259.4 | 64.4 | 68.5 | 57.4 | 285.8 | 310.5 | 232.7 | 372.4 | 279.1 | 389.7 | 385.3
2834.1 | 2595.1 | -5.9 | 0 | 0 | 289.4 | 249 | 235.8 | 226.4 | 74.5 | 42.7 | 17.7 | 71.3 | 6.1 | 251.5 | 14.1 | 57.3 | 51.3 | 33.2 | 50 | 43.4 | 49.4 | 61.9 | 79 | 92.3 | 69.5 | 39.1 | 49.5 | 287.9 | 282.6 | 331 | 58.1 | 259.4 | 64.6 | 68.6 | 57.7 | 285.6 | 310.4 | 232.5 | 372.1 | 279 | 389.4 | 385.1
2835.1 | 2596.1 | -6 | 0 | 0 | 289.3 | 248.7 | 235.7 | 226.4 | 80.6 | 42.7 | 17.7 | 71.3 | 5.4 | 247.1 | 16.2 | 57.2 | 52 | 33 | 50 | 43.4 | 49.3 | 61.9 | 79.2 | 92.3 | 69.4 | 39.1 | 49.6 | 287.2 | 282.5 | 330.9 | 58.2 | 259.4 | 64.9 | 68.7 | 58 | 285.5 | 310.2 | 232.3 | 371.9 | 278.8 | 389.1 | 384.9
2836.1 | 2597.1 | -5.7 | 0 | 0 | 289.3 | 248.3 | 235.5 | 226.3 | 89.5 | 42.7 | 17.7 | 71.2 | 4.7 | 243.8 | 16.8 | 57.2 | 52.3 | 32.7 | 50 | 43.4 | 49.2 | 61.9 | 79.5 | 92.4 | 69.2 | 39.2 | 49.6 | 287.1 | 283.2 | 330.7 | 58.3 | 259.3 | 64.8 | 68.7 | 58.3 | 285.4 | 310.1 | 232.1 | 371.6 | 278.6 | 388.9 | 384.7
2837.1 | 2598.1 | -5.8 | 0 | 0 | 289.4 | 248 | 235.3 | 226.1 | 101.1 | 42.6 | 17.7 | 71.2 | 4.9 | 253 | 14.6 | 57.1 | 52.2 | 32.6 | 50 | 43.4 | 49.2 | 62.1 | 79.7 | 92.6 | 68.9 | 39.2 | 49.6 | 287.1 | 282.7 | 330.6 | 58.5 | 259.3 | 64.9 | 68.9 | 58.5 | 285.3 | 309.9 | 232 | 371.3 | 278.5 | 388.6 | 384.5
2838.1 | 2599.1 | -5.8 | 0 | 0 | 289.2 | 248 | 235.2 | 226 | 115.2 | 42.6 | 17.7 | 71.2 | 5.1 | 256.7 | 14.7 | 57.1 | 51.8 | 32.5 | 50.1 | 43.4 | 49.2 | 62 | 79.7 | 92.6 | 68.8 | 39.2 | 49.7 | 287.3 | 281.6 | 330.4 | 58.6 | 259.2 | 64.9 | 68.9 | 58.6 | 285.2 | 309.8 | 231.8 | 371 | 278.3 | 388.4 | 384.4
2839.1 | 2600.1 | -6 | 0 | 0 | 289.1 | 248 | 235.3 | 225.9 | 130.1 | 42.6 | 17.7 | 71.1 | 5.5 | 248.3 | 13.6 | 57 | 51.7 | 32.5 | 50.1 | 43.4 | 49.2 | 62.1 | 79.6 | 92.6 | 68.9 | 39.3 | 49.7 | 287.2 | 281.2 | 330.2 | 58.7 | 259.1 | 65 | 69 | 58.6 | 285.1 | 309.8 | 231.7 | 370.7 | 278.2 | 388.1 | 384.2
2840.1 | 2601.1 | -5.8 | 0 | 0 | 289 | 248 | 235.3 | 225.9 | 143.6 | 42.5 | 17.7 | 71.1 | 5.3 | 247.3 | 14.1 | 57 | 51.7 | 32.6 | 50.1 | 43.4 | 49.2 | 62.2 | 79.7 | 92.3 | 68.8 | 39.3 | 49.7 | 287.5 | 281.6 | 330.1 | 58.8 | 259.1 | 65 | 69.1 | 58.8 | 284.9 | 309.8 | 231.5 | 370.4 | 278 | 387.8 | 384
2841.1 | 2602.1 | -5.9 | 0 | 0 | 289 | 248.1 | 235.1 | 225.8 | 155.8 | 42.5 | 17.7 | 71 | 5.2 | 256.5 | 13.6 | 56.9 | 51.6 | 32.6 | 50.1 | 43.3 | 49.1 | 62.2 | 79.7 | 91.9 | 68.9 | 39.4 | 49.8 | 287.4 | 281.7 | 329.9 | 58.9 | 259.1 | 65 | 69.2 | 59.1 | 284.8 | 309.8 | 231.3 | 370.1 | 277.9 | 387.6 | 383.8
2842.1 | 2603.1 | -5.8 | 0 | 0 | 288.7 | 248 | 235 | 225.8 | 166.5 | 42.5 | 17.7 | 70.9 | 4.4 | 253.2 | 13.9 | 56.9 | 51.9 | 32.6 | 50.1 | 43.3 | 49 | 62.3 | 79.7 | 91.5 | 69 | 39.4 | 49.9 | 287.1 | 281.3 | 329.8 | 59.1 | 259 | 65.2 | 69.3 | 59.5 | 284.7 | 309.3 | 231 | 369.8 | 277.7 | 387.3 | 383.6
2843.1 | 2604.1 | -5.8 | 0 | 0 | 288.4 | 247.7 | 235 | 225.7 | 176.1 | 42.4 | 17.7 | 70.9 | 4.2 | 255.4 | 12.7 | 56.8 | 52 | 32.7 | 50.1 | 43.3 | 48.9 | 62.5 | 80 | 91 | 68.9 | 39.5 | 49.9 | 287.2 | 281 | 329.6 | 59.3 | 259 | 65.3 | 69.4 | 59.7 | 284.6 | 309.1 | 230.8 | 369.6 | 277.6 | 387 | 383.4
2844.1 | 2605.1 | -5.7 | 0 | 0 | 288.1 | 247.7 | 235.1 | 225.6 | 184.8 | 42.4 | 17.7 | 70.9 | 4.6 | 268.6 | 12.9 | 56.8 | 51.9 | 32.9 | 50.1 | 43.3 | 48.8 | 62.4 | 80.2 | 90.7 | 69 | 39.5 | 49.9 | 287.2 | 280.8 | 329.4 | 59.4 | 258.9 | 65.3 | 69.5 | 59.9 | 284.5 | 309.1 | 230.6 | 369.3 | 277.4 | 386.8 | 383.2
2845.1 | 2606.1 | -5.8 | 0 | 0 | 288 | 247.6 | 235 | 225.5 | 192.6 | 42.4 | 17.7 | 70.8 | 4.8 | 262.8 | 14.4 | 56.7 | 52 | 33 | 50.1 | 43.3 | 48.8 | 62.3 | 79.9 | 90.5 | 69.1 | 39.6 | 49.9 | 287.6 | 280.5 | 329.3 | 59.5 | 259 | 65.2 | 69.7 | 59.9 | 284.4 | 308.7 | 230.4 | 369 | 277.2 | 386.5 | 383
2846.1 | 2607.1 | -5.6 | 0 | 0 | 287.6 | 247.5 | 234.7 | 225.4 | 199.7 | 42.3 | 17.7 | 70.8 | 4.7 | 252.9 | 13.2 | 56.7 | 52.6 | 33.1 | 50.2 | 43.3 | 48.6 | 62.5 | 80.1 | 90.5 | 69.3 | 39.7 | 50 | 287.6 | 280.6 | 329.1 | 59.7 | 259 | 65.4 | 69.8 | 60.1 | 284.2 | 308.1 | 230.2 | 368.7 | 277.1 | 386.2 | 382.8
2847.1 | 2608.1 | -5.5 | 0 | 0 | 287.3 | 247.5 | 234.4 | 225.3 | 205.7 | 42.2 | 17.8 | 70.8 | 4.7 | 266.2 | 12.8 | 56.6 | 52.6 | 33 | 50.2 | 43.3 | 48.5 | 62.5 | 79.8 | 90.4 | 69.2 | 39.7 | 50.1 | 287.7 | 280.3 | 329 | 59.7 | 258.9 | 65.4 | 69.9 | 60.4 | 284.1 | 307.9 | 229.9 | 368.4 | 276.9 | 386 | 382.6
2848.1 | 2609.1 | -5.5 | 0 | 0 | 286.9 | 247.5 | 234.2 | 225.3 | 211.2 | 42.1 | 17.8 | 70.8 | 5.2 | 254 | 13.1 | 56.6 | 52.7 | 33 | 50.2 | 43.3 | 48.3 | 62.4 | 79.8 | 90.3 | 69.3 | 39.8 | 50.1 | 288.3 | 280.6 | 328.8 | 59.9 | 258.9 | 65.4 | 70 | 60.6 | 284 | 307.4 | 229.7 | 368.2 | 276.8 | 385.7 | 382.4
2849.1 | 2610.1 | -5.5 | 0 | 0 | 286.9 | 247.3 | 234.3 | 225.3 | 216.1 | 42 | 17.8 | 70.8 | 5.3 | 253.5 | 12.3 | 56.6 | 52.1 | 33 | 50.2 | 43.3 | 48.3 | 62.5 | 79.7 | 90.2 | 69.3 | 39.8 | 50.2 | 288.3 | 280 | 328.7 | 60 | 258.8 | 65.3 | 70 | 60.8 | 283.9 | 307.2 | 229.5 | 367.9 | 276.6 | 385.4 | 382.2
2850.1 | 2611.1 | -5.4 | 0 | 0 | 286.8 | 247.1 | 234.4 | 225.2 | 220.7 | 41.9 | 17.8 | 70.8 | 5.7 | 260.3 | 11.2 | 56.5 | 52.2 | 32.9 | 50.2 | 43.3 | 48.2 | 62.5 | 79.4 | 90.1 | 69.5 | 39.9 | 50.2 | 288.4 | 280.6 | 328.5 | 60.1 | 258.9 | 65.4 | 70.1 | 61 | 283.8 | 307.2 | 229.3 | 367.6 | 276.5 | 385.2 | 382
2851.1 | 2612.1 | -5.4 | 0 | 0 | 286.8 | 247 | 234.4 | 225.1 | 224.8 | 41.8 | 17.8 | 70.8 | 5.5 | 253.6 | 12.2 | 56.5 | 52.7 | 32.8 | 50.3 | 43.4 | 48.2 | 62.5 | 79.4 | 90.1 | 69.3 | 39.9 | 50.3 | 288.9 | 280.8 | 328.3 | 60.2 | 258.9 | 65.3 | 70.1 | 61.2 | 283.6 | 307.1 | 229.1 | 367.3 | 276.3 | 384.9 | 381.8
2852.1 | 2613.1 | -5.5 | 0 | 0 | 286.7 | 247.1 | 234.3 | 225 | 228.3 | 41.8 | 17.8 | 70.7 | 5.8 | 257.9 | 13.2 | 56.5 | 52.4 | 32.7 | 50.3 | 43.4 | 48.1 | 62.6 | 79.5 | 89.9 | 69.3 | 40 | 50.3 | 289.4 | 280.7 | 328.2 | 60.3 | 258.8 | 65.1 | 70.2 | 61.4 | 283.5 | 306.9 | 228.9 | 367 | 276.1 | 384.7 | 381.6
2853.1 | 2614.1 | -5.6 | 0 | 0 | 286.6 | 247.3 | 234.1 | 224.8 | 231.6 | 41.8 | 17.8 | 70.6 | 4.8 | 263.6 | 11.8 | 56.4 | 51.7 | 32.6 | 50.3 | 43.4 | 48.1 | 62.6 | 79.6 | 89.6 | 69.2 | 40.1 | 50.4 | 290 | 281.6 | 328 | 60.4 | 258.8 | 65 | 70.2 | 61.6 | 283.4 | 306.7 | 228.7 | 366.7 | 276 | 384.4 | 381.5
2854.1 | 2615.1 | -5.6 | 0 | 0 | 286.3 | 247.4 | 234.1 | 224.8 | 234.6 | 41.8 | 17.8 | 70.5 | 5.1 | 248.6 | 11.2 | 56.4 | 51.4 | 32.7 | 50.3 | 43.4 | 48.1 | 62.7 | 79.7 | 89.6 | 69.1 | 40.1 | 50.5 | 290.3 | 282.1 | 327.9 | 60.5 | 258.8 | 65.1 | 70.3 | 61.7 | 283.3 | 306.4 | 228.5 | 366.4 | 275.8 | 384.2 | 381.3
2855.1 | 2616.1 | -5.8 | 0 | 0 | 286.3 | 247.3 | 234.1 | 224.6 | 237.3 | 41.8 | 17.8 | 70.5 | 6.2 | 250.6 | 11.2 | 56.3 | 51.4 | 32.8 | 50.4 | 43.4 | 48.1 | 62.7 | 79.8 | 89.6 | 69.1 | 40.2 | 50.6 | 290.1 | 282.2 | 327.7 | 60.6 | 258.7 | 65.3 | 70.4 | 61.9 | 283.1 | 306.2 | 228.3 | 366.1 | 275.7 | 383.9 | 381.1
2856.1 | 2617.1 | -5.8 | 0 | 0 | 286.1 | 247.2 | 234 | 224.5 | 239.6 | 41.8 | 17.8 | 70.5 | 5.4 | 243.4 | 11.1 | 56.3 | 51.4 | 32.8 | 50.4 | 43.4 | 48 | 62.7 | 80 | 89.7 | 69.1 | 40.3 | 50.6 | 290 | 280.9 | 327.6 | 60.7 | 258.7 | 65.3 | 70.4 | 62 | 283 | 306.2 | 228 | 365.8 | 275.5 | 383.6 | 380.9
2857.1 | 2618.1 | -5.7 | 0 | 0 | 285.8 | 247.2 | 233.9 | 224.3 | 241.5 | 41.8 | 17.8 | 70.4 | 4.8 | 258.9 | 11.1 | 56.3 | 51.4 | 32.8 | 50.4 | 43.4 | 47.9 | 62.7 | 80.4 | 90.4 | 68.9 | 40.3 | 50.6 | 289.8 | 280.8 | 327.4 | 60.8 | 258.6 | 65.3 | 70.4 | 62.3 | 282.9 | 306.2 | 227.8 | 365.5 | 275.4 | 383.4 | 380.7
2858.1 | 2619.1 | -5.9 | 0 | 0 | 285.2 | 247.2 | 233.9 | 224.2 | 243.4 | 41.8 | 17.8 | 70.3 | 5.1 | 242 | 11.5 | 56.2 | 51.3 | 32.8 | 50.5 | 43.4 | 47.8 | 62.8 | 80.4 | 91.1 | 69 | 40.4 | 50.6 | 289.8 | 280.9 | 327.3 | 61 | 258.6 | 65.7 | 70.5 | 62.4 | 282.8 | 306.2 | 227.5 | 365.2 | 275.2 | 383.1 | 380.5
2859.1 | 2620.1 | -6.1 | 0 | 0 | 284.7 | 246.9 | 233.9 | 224.1 | 245.3 | 41.8 | 17.8 | 70.2 | 5.3 | 253.2 | 11 | 56.2 | 51.2 | 32.9 | 50.5 | 43.4 | 47.7 | 62.9 | 80.4 | 90.8 | 69.2 | 40.4 | 50.6 | 289.8 | 280.2 | 327.1 | 61.2 | 258.5 | 65.7 | 70.6 | 62.5 | 282.7 | 306.1 | 227.2 | 364.9 | 275 | 382.9 | 380.3
2860.1 | 2621.1 | -6 | 0 | 0 | 284.5 | 246.8 | 233.7 | 224.1 | 246.8 | 41.9 | 17.8 | 70.2 | 4.5 | 247.5 | 11.2 | 56.2 | 51.2 | 32.7 | 50.5 | 43.5 | 47.6 | 62.9 | 80.6 | 90.6 | 69.2 | 40.5 | 50.6 | 290.1 | 280.4 | 327 | 61.2 | 258.5 | 65.6 | 70.7 | 62.7 | 282.5 | 305.9 | 226.9 | 364.6 | 274.9 | 382.6 | 380.1
2861.1 | 2622.1 | -6.1 | 0 | 0 | 284.1 | 246.9 | 233.4 | 224 | 248 | 41.8 | 17.8 | 70.2 | 4.9 | 247.2 | 10.2 | 56.1 | 51.7 | 32.7 | 50.5 | 43.5 | 47.7 | 63 | 80.7 | 90.2 | 69.1 | 40.6 | 50.7 | 290.5 | 280.7 | 326.8 | 61.3 | 258.3 | 65.2 | 70.7 | 62.8 | 282.4 | 305.5 | 226.6 | 364.3 | 274.7 | 382.3 | 379.9
2862.1 | 2623.1 | -6 | 0 | 0 | 283.5 | 246.8 | 233.2 | 224 | 249.2 | 41.8 | 17.8 | 70.2 | 5 | 265.4 | 10 | 56.1 | 51.9 | 32.7 | 50.6 | 43.5 | 47.7 | 62.9 | 80.7 | 90.1 | 69.3 | 40.6 | 50.8 | 291 | 281.4 | 326.7 | 61.4 | 258.3 | 64.7 | 70.8 | 62.7 | 282.3 | 305.6 | 226.4 | 364.1 | 274.6 | 382.1 | 379.7
2863.1 | 2624.1 | -6 | 0 | 0 | 283.3 | 246.7 | 233 | 223.9 | 250.4 | 41.8 | 17.8 | 70.2 | 3.9 | 245.4 | 10.1 | 56.1 | 51.3 | 32.8 | 50.6 | 43.5 | 47.6 | 63 | 80.4 | 90 | 69.3 | 40.7 | 50.9 | 291.3 | 281.3 | 326.5 | 61.5 | 258.3 | 64.9 | 70.9 | 62.6 | 282.2 | 305.7 | 226.2 | 363.8 | 274.4 | 381.8 | 379.5
2864.1 | 2625.1 | -6 | 0 | 0 | 283.3 | 246.5 | 232.9 | 223.8 | 251.5 | 41.8 | 17.8 | 70.2 | 3.8 | 247.4 | 10.8 | 56 | 51.1 | 32.9 | 50.6 | 43.5 | 47.5 | 63 | 80.5 | 90.1 | 69.4 | 40.8 | 51 | 291.4 | 280.3 | 326.3 | 61.6 | 258.3 | 65.5 | 70.9 | 62.8 | 282 | 305.8 | 226 | 363.5 | 274.2 | 381.6 | 379.3
2865.1 | 2626.1 | -5.9 | 0 | 0 | 283.1 | 246.3 | 232.9 | 223.7 | 252.4 | 41.8 | 17.8 | 70.3 | 4 | 257.3 | 10.5 | 56 | 50.8 | 32.9 | 50.7 | 43.5 | 47.5 | 63.1 | 80.8 | 89.9 | 69.5 | 40.8 | 50.9 | 291.1 | 280 | 326.2 | 61.6 | 258.2 | 65.5 | 70.9 | 63 | 281.9 | 305.5 | 225.7 | 363.2 | 274.1 | 381.3 | 379.1
2866.1 | 2627.1 | -5.8 | 0 | 0 | 283 | 246.2 | 232.8 | 223.6 | 253.2 | 41.8 | 17.8 | 70.3 | 4 | 270 | 9.6 | 56 | 50.7 | 32.9 | 50.7 | 43.5 | 47.4 | 63 | 80.8 | 89.8 | 69.6 | 40.9 | 51 | 291 | 280.5 | 326 | 61.7 | 258.1 | 65.7 | 70.9 | 63.1 | 281.8 | 305.3 | 225.6 | 362.9 | 273.9 | 381.1 | 378.9
2867.1 | 2628.1 | -5.8 | 0 | 0 | 282.8 | 246 | 232.6 | 223.4 | 254 | 41.9 | 17.8 | 70.3 | 4.3 | 256.9 | 8.8 | 55.9 | 50.6 | 32.9 | 50.7 | 43.6 | 47.5 | 63.1 | 80.5 | 89.7 | 69.6 | 41 | 51 | 291.2 | 279.7 | 325.9 | 61.8 | 258.1 | 65.8 | 71 | 63.3 | 281.7 | 305.1 | 225.5 | 362.6 | 273.8 | 380.8 | 378.8
2868.1 | 2629.1 | -5.7 | 0 | 0 | 282.6 | 245.7 | 232.6 | 223.2 | 254.8 | 41.8 | 17.9 | 70.4 | 4.7 | 258.7 | 8.1 | 55.9 | 50.6 | 32.8 | 50.7 | 43.6 | 47.5 | 63.1 | 80.5 | 89.7 | 69.7 | 41 | 51.2 | 291.4 | 279.6 | 325.7 | 61.9 | 258 | 65.8 | 71 | 63.4 | 281.6 | 305 | 225.3 | 362.4 | 273.6 | 380.5 | 378.6
2869.1 | 2630.1 | -5.6 | 0 | 0 | 282.2 | 245.4 | 232.6 | 223 | 255.4 | 41.7 | 17.9 | 70.3 | 4.2 | 265.4 | 11.9 | 55.9 | 51.1 | 32.8 | 50.8 | 43.6 | 47.5 | 63.2 | 80.6 | 89.6 | 69.5 | 41.1 | 51.2 | 291.3 | 278.5 | 325.5 | 62 | 257.8 | 65.8 | 71 | 63.5 | 281.4 | 304.8 | 225 | 362.1 | 273.4 | 380.3 | 378.4
2870.1 | 2631.1 | -5.7 | 0 | 0 | 282.3 | 245 | 232.4 | 222.8 | 255.8 | 41.7 | 17.9 | 70.3 | 4.3 | 264.2 | 14.3 | 55.9 | 51.8 | 32.6 | 50.8 | 43.6 | 47.4 | 63.1 | 80.9 | 89.4 | 69.2 | 41.2 | 51.3 | 291.3 | 278.1 | 325.4 | 62 | 257.6 | 65.8 | 71 | 63.7 | 281.3 | 304.7 | 224.8 | 361.8 | 273.3 | 380 | 378.2
2871.1 | 2632.1 | -5.6 | 0 | 0 | 282.2 | 244.8 | 232.3 | 222.6 | 256.2 | 41.6 | 17.9 | 70.3 | 4.8 | 235.7 | 13.6 | 55.8 | 52.4 | 32.5 | 50.9 | 43.6 | 47.4 | 63.1 | 80.9 | 89.1 | 68.8 | 41.2 | 51.4 | 291 | 277.8 | 325.2 | 62.1 | 257.4 | 65.5 | 71 | 63.9 | 281.2 | 304.4 | 224.6 | 361.6 | 273.1 | 379.8 | 378
2872.1 | 2633.1 | -5.6 | 0 | 0 | 282.1 | 244.6 | 232.3 | 222.4 | 256.5 | 41.6 | 17.9 | 70.4 | 4.5 | 271.8 | 13.4 | 55.8 | 52.8 | 32.5 | 50.9 | 43.6 | 47.3 | 63 | 80.8 | 89 | 68.8 | 41.3 | 51.4 | 291 | 278.3 | 325.1 | 62.2 | 257.4 | 65.7 | 71 | 64 | 281.1 | 304.1 | 224.4 | 361.3 | 272.9 | 379.5 | 377.8
2873.1 | 2634.1 | -5.6 | 0 | 0 | 282.3 | 244.5 | 232.2 | 222.2 | 256.7 | 41.5 | 17.9 | 70.3 | 3.8 | 269.1 | 11.2 | 55.8 | 53.1 | 32.6 | 51 | 43.7 | 47.3 | 63.1 | 80.8 | 88.9 | 68.9 | 41.4 | 51.5 | 290.8 | 278.5 | 325 | 62.3 | 257.2 | 65.8 | 71.1 | 64.1 | 281 | 303.6 | 224.2 | 361 | 272.8 | 379.3 | 377.6
2874.1 | 2635.1 | -5.6 | 0 | 0 | 282.4 | 244.3 | 232.1 | 222 | 256.8 | 41.5 | 17.9 | 70.2 | 4.5 | 257 | 13.4 | 55.8 | 53.2 | 32.6 | 51 | 43.7 | 47.2 | 63.2 | 80.9 | 88.7 | 68.9 | 41.5 | 51.5 | 291.4 | 277.6 | 324.8 | 62.3 | 257 | 66 | 71.1 | 64.3 | 280.8 | 303.2 | 224 | 360.7 | 272.7 | 379 | 377.4
2875.1 | 2636.1 | -5.5 | 0 | 0 | 282.4 | 244.1 | 232 | 221.7 | 257 | 41.4 | 17.9 | 70.2 | 5 | 257.7 | 15.9 | 55.7 | 53.2 | 32.8 | 51.1 | 43.7 | 47.2 | 63.1 | 81.1 | 88.4 | 69.1 | 41.5 | 51.6 | 291.4 | 277.4 | 324.6 | 62.4 | 256.9 | 66 | 71.1 | 64.3 | 280.7 | 303.1 | 223.8 | 360.5 | 272.5 | 378.8 | 377.2
2876.1 | 2637.1 | -5.6 | 0 | 0 | 282.2 | 244 | 231.9 | 221.6 | 257.1 | 41.5 | 17.9 | 70.1 | 5.8 | 258 | 15.7 | 55.7 | 53.4 | 32.8 | 51.1 | 43.7 | 47.2 | 63.1 | 81.2 | 88.2 | 69 | 41.6 | 51.6 | 291.7 | 277.3 | 324.5 | 62.5 | 256.9 | 66 | 71.1 | 64.3 | 280.6 | 303.1 | 223.7 | 360.2 | 272.4 | 378.5 | 377
2877.1 | 2638.1 | -5.7 | 0 | 0 | 282 | 244 | 231.8 | 221.5 | 257.3 | 41.4 | 17.9 | 70.1 | 5.1 | 248.6 | 17.2 | 55.7 | 53.7 | 32.9 | 51.1 | 43.7 | 47.2 | 63.2 | 81.5 | 88.1 | 69.1 | 41.7 | 51.6 | 291.7 | 276.9 | 324.3 | 62.6 | 256.7 | 66 | 71.1 | 64.4 | 280.5 | 302.8 | 223.6 | 359.9 | 272.2 | 378.3 | 376.9
2878.1 | 2639.1 | -5.8 | 0 | 0 | 281.6 | 244 | 231.7 | 221.4 | 257.5 | 41.4 | 17.9 | 70 | 5.1 | 253.9 | 14.7 | 55.7 | 53.3 | 32.9 | 51.2 | 43.8 | 47.3 | 63.2 | 81.5 | 88 | 69.1 | 41.8 | 51.7 | 291.9 | 276.5 | 324.2 | 62.7 | 256.7 | 65.9 | 71.1 | 64.4 | 280.3 | 302.3 | 223.4 | 359.6 | 272.1 | 378 | 376.7
2879.1 | 2640.1 | -6.1 | 0 | 0 | 281.3 | 243.9 | 231.5 | 221.3 | 257.6 | 41.3 | 17.9 | 69.9 | 5.3 | 264.2 | 12.7 | 55.7 | 53 | 33 | 51.2 | 43.8 | 47.3 | 63.3 | 81.4 | 87.4 | 69 | 41.8 | 51.7 | 292 | 276.6 | 324.1 | 62.8 | 256.6 | 65.7 | 71.1 | 64.5 | 280.2 | 301.9 | 223.2 | 359.4 | 271.9 | 377.8 | 376.5
2880.1 | 2641.1 | -6.1 | 0 | 0 | 281.2 | 243.9 | 231.1 | 221.2 | 257.8 | 41.3 | 17.9 | 69.8 | 5.2 | 251 | 11.2 | 55.6 | 52.7 | 33 | 51.2 | 43.8 | 47.2 | 63.3 | 81.2 | 87.5 | 69.1 | 41.9 | 51.7 | 291.8 | 276.2 | 323.9 | 62.9 | 256.4 | 65.8 | 71.2 | 64.6 | 280.1 | 301.4 | 223.1 | 359.1 | 271.8 | 377.5 | 376.3
2881.1 | 2642.1 | -6.1 | 0 | 0 | 280.9 | 243.9 | 230.9 | 221.1 | 257.7 | 41.2 | 17.9 | 69.8 | 5.1 | 255.2 | 11.8 | 55.6 | 52.7 | 32.9 | 51.3 | 43.8 | 47.2 | 63.3 | 81.2 | 87.4 | 69.2 | 42 | 51.8 | 291.6 | 275.6 | 323.7 | 63 | 256.2 | 65.5 | 71.2 | 64.7 | 280 | 301.2 | 222.9 | 358.9 | 271.6 | 377.3 | 376.1
2882.1 | 2643.1 | -6.2 | 0 | 0 | 280.6 | 243.9 | 231 | 221 | 257.8 | 41.2 | 17.9 | 69.8 | 4.5 | 259.7 | 12.9 | 55.6 | 52.8 | 32.9 | 51.3 | 43.8 | 47.2 | 63.3 | 80.9 | 87.3 | 69.2 | 42.1 | 51.8 | 291.4 | 275 | 323.6 | 63.1 | 256.1 | 65.6 | 71.3 | 64.8 | 279.9 | 301 | 222.7 | 358.6 | 271.4 | 377 | 375.9
2883.1 | 2644.1 | -6.1 | 0 | 0 | 280.3 | 243.9 | 231 | 220.9 | 257.8 | 41.2 | 17.9 | 69.7 | 4.4 | 260.1 | 12.1 | 55.6 | 52.5 | 32.9 | 51.3 | 43.9 | 47.1 | 63.4 | 81.4 | 87.2 | 69.3 | 42.2 | 51.9 | 291.5 | 275.2 | 323.4 | 63.2 | 255.9 | 65.6 | 71.3 | 65 | 279.7 | 300.8 | 222.6 | 358.3 | 271.3 | 376.8 | 375.7
2884.1 | 2645.1 | -6 | 0 | 0 | 280.4 | 243.7 | 231.1 | 220.7 | 257.8 | 41.2 | 17.9 | 69.7 | 5 | 267.3 | 11.8 | 55.6 | 52.6 | 33 | 51.4 | 43.9 | 47.1 | 63.3 | 81.5 | 86.9 | 69.2 | 42.2 | 51.9 | 291.6 | 274.5 | 323.3 | 63.3 | 255.8 | 65.7 | 71.4 | 65.2 | 279.6 | 300.6 | 222.4 | 358.1 | 271.1 | 376.5 | 375.5
2885.1 | 2646.1 | -5.8 | 0 | 0 | 280.3 | 243.4 | 231.1 | 220.4 | 257.9 | 41.2 | 17.9 | 69.7 | 5.3 | 255 | 12.4 | 55.6 | 52.3 | 33 | 51.4 | 43.9 | 47 | 63.3 | 81.4 | 86.9 | 69.3 | 42.3 | 51.9 | 291.4 | 273.9 | 323.2 | 63.4 | 255.8 | 65.7 | 71.4 | 65.2 | 279.5 | 300.2 | 222.3 | 357.9 | 271 | 376.3 | 375.3
2886.1 | 2647.1 | -5.5 | 0 | 0 | 280 | 243.3 | 230.9 | 220.3 | 257.9 | 41.2 | 18 | 69.8 | 4.8 | 258.4 | 13.5 | 55.6 | 52.5 | 33 | 51.5 | 43.9 | 46.9 | 63.3 | 81.4 | 86.9 | 68.8 | 42.4 | 51.8 | 290.9 | 274.5 | 323 | 63.5 | 255.5 | 65.5 | 71.5 | 65.3 | 279.4 | 300.2 | 222.2 | 357.6 | 270.8 | 376.1 | 375.1
2887.1 | 2648.1 | -5.5 | 0 | 0 | 279.6 | 243.5 | 230.8 | 220.1 | 257.9 | 41.2 | 17.9 | 69.8 | 4.4 | 254.7 | 13.4 | 55.5 | 51.9 | 32.8 | 51.5 | 43.9 | 46.9 | 63.3 | 81.4 | 86.9 | 68.6 | 42.5 | 51.9 | 291.3 | 274.6 | 322.9 | 63.6 | 255.2 | 65.7 | 71.6 | 65.4 | 279.3 | 299.9 | 221.9 | 357.4 | 270.7 | 375.8 | 375
2888.1 | 2649.1 | -5.8 | 0 | 0 | 279.5 | 243.8 | 230.7 | 219.9 | 257.9 | 41.2 | 17.9 | 69.7 | 4.4 | 257.1 | 12.6 | 55.5 | 52.2 | 32.8 | 51.5 | 44 | 46.9 | 63.3 | 81.4 | 86.8 | 68.5 | 42.6 | 51.9 | 291.7 | 274.7 | 322.7 | 63.6 | 255.2 | 65.8 | 71.6 | 65.5 | 279.2 | 299.9 | 221.8 | 357.1 | 270.5 | 375.5 | 374.8
2889.1 | 2650.1 | -5.9 | 0 | 0 | 279.3 | 243.9 | 230.5 | 219.9 | 257.9 | 41.1 | 18 | 69.7 | 4.6 | 259.7 | 13.7 | 55.5 | 52.4 | 32.7 | 51.5 | 44 | 46.8 | 63.4 | 81.6 | 86.9 | 68.6 | 42.6 | 52 | 291.9 | 273.5 | 322.6 | 63.7 | 255.2 | 65.8 | 71.6 | 65.6 | 279 | 299.4 | 221.7 | 356.9 | 270.4 | 375.3 | 374.6
2890.1 | 2651.1 | -6 | 0 | 0 | 279.2 | 244 | 230.2 | 220 | 258.1 | 41.1 | 17.9 | 69.7 | 4.4 | 264.4 | 14.4 | 55.5 | 52.8 | 32.7 | 51.6 | 44 | 46.8 | 63.4 | 81.6 | 87 | 68.7 | 42.7 | 52 | 292.1 | 273.2 | 322.4 | 63.8 | 255.2 | 66 | 71.7 | 65.7 | 278.9 | 299 | 221.5 | 356.7 | 270.3 | 375.1 | 374.4
2891.1 | 2652.1 | -5.9 | 0 | 0 | 279.1 | 243.9 | 230 | 220 | 258.1 | 41.1 | 18 | 69.7 | 4.3 | 253 | 14.5 | 55.5 | 52.9 | 32.8 | 51.6 | 44 | 46.7 | 63.4 | 81.6 | 87.3 | 68.7 | 42.8 | 52 | 292.3 | 272.8 | 322.3 | 63.9 | 255.2 | 65.7 | 71.8 | 65.6 | 278.8 | 298.5 | 221.4 | 356.5 | 270.1 | 374.8 | 374.2
2892.1 | 2653.1 | -5.8 | 0 | 0 | 278.7 | 243.5 | 229.8 | 219.9 | 258.2 | 41.1 | 18 | 69.6 | 5.1 | 262.6 | 12.6 | 55.5 | 52.9 | 32.7 | 51.7 | 44.1 | 46.6 | 63.5 | 81.3 | 87.3 | 68.7 | 42.9 | 52.1 | 292.3 | 272.9 | 322.1 | 63.9 | 255.2 | 65.4 | 71.8 | 65.7 | 278.7 | 298.4 | 221.3 | 356.3 | 270 | 374.6 | 374
2893.1 | 2654.1 | -5.8 | 0 | 0 | 278.6 | 243.2 | 229.6 | 219.8 | 258.5 | 41.1 | 18 | 69.5 | 5.8 | 261.9 | 11.9 | 55.5 | 53.1 | 32.7 | 51.7 | 44.1 | 46.6 | 63.6 | 81.2 | 87.2 | 68.4 | 43 | 52.2 | 292.2 | 272.4 | 322 | 64 | 255.3 | 65.1 | 71.8 | 65.7 | 278.6 | 298.2 | 221.3 | 356.1 | 269.9 | 374.3 | 373.8
2894.1 | 2655.1 | -5.9 | 0 | 0 | 278.6 | 243.2 | 229.5 | 219.7 | 258.5 | 41.1 | 18 | 69.4 | 4.9 | 257.2 | 12.9 | 55.5 | 53.4 | 32.7 | 51.8 | 44.1 | 46.6 | 63.5 | 81.5 | 87.1 | 68.6 | 43.1 | 52.2 | 292 | 271.9 | 321.8 | 64.1 | 255.1 | 64.7 | 71.8 | 65.7 | 278.5 | 298.2 | 221.2 | 355.9 | 269.7 | 374.1 | 373.6
2895.1 | 2656.1 | -5.9 | 0 | 0 | 278.2 | 243.3 | 229.4 | 219.5 | 258.4 | 41.1 | 18 | 69.3 | 4.8 | 262.8 | 11.6 | 55.5 | 53.3 | 32.6 | 51.8 | 44.1 | 46.6 | 63.5 | 81.4 | 87.1 | 68.7 | 43.2 | 52.3 | 292.1 | 271 | 321.7 | 64.2 | 254.9 | 65 | 71.8 | 65.9 | 278.4 | 298.3 | 221.1 | 355.7 | 269.6 | 373.8 | 373.5
2896.1 | 2657.1 | -6 | 0 | 0 | 277.7 | 243.2 | 229.2 | 219.4 | 258.1 | 41.1 | 18 | 69.3 | 3.4 | 262.3 | 11.9 | 55.4 | 52.6 | 32.6 | 51.8 | 44.2 | 46.6 | 63.5 | 81.2 | 87 | 68.7 | 43.2 | 52.3 | 292.4 | 271.3 | 321.6 | 64.3 | 254.8 | 65.1 | 71.9 | 66 | 278.3 | 298.1 | 221 | 355.5 | 269.5 | 373.6 | 373.3
2897.1 | 2658.1 | -5.8 | 0 | 0 | 277.5 | 242.9 | 228.9 | 219.4 | 257.9 | 41.1 | 18 | 69.2 | 4 | 259.2 | 12.6 | 55.4 | 52.7 | 32.6 | 51.9 | 44.2 | 46.5 | 63.6 | 81.6 | 87 | 68.7 | 43.3 | 52.3 | 292.3 | 271.2 | 321.4 | 64.4 | 254.6 | 65.7 | 72 | 66.1 | 278.2 | 298 | 220.8 | 355.3 | 269.3 | 373.3 | 373.1
2898.1 | 2659.1 | -5.8 | 0 | 0 | 277 | 242.3 | 228.7 | 219.4 | 257.8 | 41.1 | 18 | 69.2 | 4.2 | 251 | 12.6 | 55.4 | 53.5 | 32.6 | 51.9 | 44.2 | 46.5 | 63.6 | 81.7 | 87.1 | 68.8 | 43.4 | 52.4 | 292.4 | 270.9 | 321.2 | 64.4 | 254.6 | 66 | 72 | 66.1 | 278.1 | 297.9 | 220.6 | 355.1 | 269.2 | 373.1 | 372.9
2899.1 | 2660.1 | -5.9 | 0 | 0 | 277 | 242 | 228.5 | 219.3 | 257.7 | 41.1 | 18 | 69.2 | 4.2 | 251 | 10.2 | 55.4 | 53.6 | 32.6 | 52 | 44.3 | 46.4 | 63.5 | 81.8 | 87.3 | 68.8 | 43.5 | 52.5 | 292.6 | 271.6 | 321.1 | 64.5 | 254.6 | 66.1 | 72.1 | 66.2 | 278 | 297.4 | 220.5 | 354.9 | 269 | 372.9 | 372.7
2900.1 | 2661.1 | -5.7 | 0 | 0 | 276.7 | 242.1 | 228.4 | 219.2 | 257.7 | 41.1 | 18 | 69.2 | 3.9 | 243.1 | 7.4 | 55.4 | 53.4 | 32.6 | 52 | 44.3 | 46.3 | 63.4 | 82.1 | 87.5 | 69.1 | 43.6 | 52.5 | 293 | 270.6 | 321 | 64.5 | 254.5 | 66.2 | 72.1 | 66.3 | 277.9 | 297 | 220.4 | 354.7 | 268.9 | 372.6 | 372.5
2901.1 | 2662.1 | -5.7 | 0 | 0 | 276.8 | 242.1 | 228.3 | 219.2 | 257.6 | 41.1 | 18 | 69.2 | 4.5 | 224.2 | 6 | 55.4 | 53.5 | 32.6 | 52.1 | 44.3 | 46.2 | 63.5 | 82.5 | 87.6 | 69.1 | 43.7 | 52.6 | 293.2 | 270.3 | 320.8 | 64.6 | 254.4 | 66.5 | 72.1 | 66.5 | 277.8 | 296.8 | 220.2 | 354.4 | 268.8 | 372.4 | 372.3
2902.1 | 2663.1 | -5.7 | 0 | 0 | 276.6 | 242 | 228.1 | 219.1 | 257.7 | 41 | 18 | 69.2 | 4.9 | 225.8 | 6 | 55.4 | 53.4 | 32.6 | 52.1 | 44.3 | 46.2 | 63.6 | 82.1 | 87.4 | 69.2 | 43.8 | 52.6 | 293.2 | 270.4 | 320.7 | 64.6 | 254.2 | 66.4 | 72.1 | 66.5 | 277.7 | 296.7 | 220 | 354.2 | 268.6 | 372.2 | 372.2
2903.1 | 2664.1 | -5.8 | 0 | 0 | 276.4 | 241.8 | 228.1 | 219.1 | 257.7 | 41 | 18 | 69.1 | 5.7 | 241.1 | 6.9 | 55.4 | 53.5 | 32.4 | 52.2 | 44.4 | 46.1 | 63.8 | 82.1 | 87.3 | 68.8 | 43.9 | 52.7 | 293.4 | 270.9 | 320.5 | 64.7 | 254.2 | 66.3 | 72 | 66.4 | 277.6 | 296.4 | 219.9 | 354 | 268.5 | 371.9 | 372
2904.1 | 2665.1 | -5.9 | 0 | 0 | 276.4 | 241.5 | 228.1 | 219 | 257.5 | 41 | 18 | 69.1 | 5.8 | 221.3 | 6.4 | 55.4 | 53.4 | 32.4 | 52.2 | 44.4 | 46 | 63.8 | 82.2 | 87 | 68.7 | 44 | 52.7 | 293.7 | 271.7 | 320.4 | 64.7 | 254 | 66.6 | 72 | 66.4 | 277.5 | 296.2 | 219.8 | 353.8 | 268.3 | 371.7 | 371.8
2905.1 | 2666.1 | -5.9 | 0 | 0 | 276.4 | 241.3 | 228 | 218.9 | 257.3 | 40.9 | 18 | 69 | 4.2 | 228.7 | 5.2 | 55.4 | 53.4 | 32.3 | 52.2 | 44.4 | 46 | 63.7 | 82.2 | 87.2 | 68.7 | 44.1 | 52.7 | 293.9 | 271.2 | 320.3 | 64.8 | 254 | 66.5 | 71.9 | 66.4 | 277.4 | 296.2 | 219.7 | 353.5 | 268.2 | 371.4 | 371.6
2906.1 | 2667.1 | -6.1 | 0 | 0 | 276.3 | 241.1 | 227.9 | 218.7 | 257.2 | 40.9 | 18 | 69 | 4.4 | 253.2 | 5.3 | 55.4 | 53.7 | 32.4 | 52.3 | 44.4 | 45.9 | 63.8 | 82.6 | 86.9 | 68.7 | 44.2 | 52.7 | 294 | 272.4 | 320.1 | 64.8 | 253.9 | 66.7 | 71.9 | 66.4 | 277.3 | 295.9 | 219.5 | 353.3 | 268.1 | 371.2 | 371.4
2907.1 | 2668.1 | -6.1 | 0 | 0 | 276 | 241.1 | 227.6 | 218.5 | 257 | 40.8 | 18 | 68.9 | 4.7 | 235.5 | 7.4 | 55.4 | 53.6 | 32.6 | 52.3 | 44.5 | 45.8 | 63.7 | 82.9 | 86.5 | 68.6 | 44.3 | 52.7 | 293.8 | 271.6 | 319.9 | 64.8 | 253.8 | 66.6 | 71.9 | 66.5 | 277.2 | 295.9 | 219.4 | 353.1 | 267.9 | 371 | 371.2
2908.1 | 2669.1 | -6 | 0 | 0 | 275.9 | 240.9 | 227.3 | 218.2 | 256.8 | 40.7 | 18 | 69 | 5.6 | 235.3 | 8.9 | 55.4 | 53.9 | 32.8 | 52.4 | 44.5 | 45.8 | 63.8 | 83.3 | 86.6 | 68.5 | 44.4 | 52.7 | 294.1 | 271.8 | 319.8 | 64.8 | 253.7 | 66.5 | 71.8 | 66.7 | 277.1 | 295.8 | 219.2 | 352.9 | 267.8 | 370.7 | 371.1
2909.1 | 2670.1 | -5.9 | 0 | 0 | 275.7 | 240.5 | 227.1 | 218 | 256.6 | 40.6 | 18 | 69 | 5.7 | 247.4 | 8.8 | 55.4 | 53.4 | 32.9 | 52.4 | 44.5 | 45.7 | 63.8 | 83.6 | 86.8 | 68.3 | 44.5 | 52.8 | 294.2 | 272.9 | 319.7 | 64.8 | 253.5 | 66.5 | 71.8 | 66.8 | 277 | 295.7 | 219.1 | 352.7 | 267.6 | 370.5 | 370.9
2910.1 | 2671.1 | -5.8 | 0 | 0 | 275.4 | 240.2 | 227.1 | 217.8 | 256.4 | 40.6 | 18 | 68.9 | 6.1 | 244.9 | 10.3 | 55.4 | 53.1 | 32.8 | 52.4 | 44.5 | 45.7 | 63.8 | 83.8 | 86.5 | 68.3 | 44.6 | 52.8 | 294.5 | 273.7 | 319.5 | 64.9 | 253.4 | 66.5 | 71.7 | 66.9 | 276.8 | 295.5 | 218.9 | 352.5 | 267.5 | 370.3 | 370.7
2911.1 | 2672.1 | -5.9 | 0 | 0 | 275.4 | 240.3 | 227.1 | 217.6 | 256.3 | 40.5 | 18.1 | 68.9 | 5.3 | 250.4 | 10 | 55.4 | 52.7 | 32.7 | 52.5 | 44.6 | 45.7 | 63.8 | 84.4 | 86 | 68.5 | 44.7 | 52.9 | 294.9 | 273.8 | 319.4 | 64.9 | 253.2 | 66.3 | 71.7 | 66.8 | 276.7 | 295.4 | 218.7 | 352.3 | 267.4 | 370 | 370.5
2912.1 | 2673.1 | -6.1 | 0 | 0 | 275.3 | 240.3 | 227 | 217.5 | 256.2 | 40.5 | 18.1 | 68.8 | 6 | 241.7 | 10.4 | 55.4 | 53.1 | 32.8 | 52.5 | 44.6 | 45.7 | 63.8 | 84.9 | 85.4 | 68.5 | 44.8 | 52.8 | 295.1 | 273.1 | 319.3 | 64.9 | 253.2 | 66.3 | 71.6 | 66.8 | 276.6 | 295 | 218.6 | 352.1 | 267.2 | 369.8 | 370.3
2913.1 | 2674.1 | -6.1 | 0 | 0 | 274.7 | 240 | 226.8 | 217.4 | 256 | 40.5 | 18.1 | 68.8 | 4.9 | 234.6 | 10.8 | 55.4 | 53.3 | 32.9 | 52.6 | 44.6 | 45.6 | 63.8 | 85.2 | 85.2 | 68.4 | 44.8 | 52.9 | 295.3 | 272.4 | 319.1 | 65 | 253.1 | 66.3 | 71.7 | 66.9 | 276.5 | 294.5 | 218.4 | 351.9 | 267.1 | 369.6 | 370.1
2914.1 | 2675.1 | -6 | 0 | 0 | 274.5 | 239.6 | 226.7 | 217.2 | 255.8 | 40.5 | 18.1 | 68.8 | 5.4 | 210.8 | 8.6 | 55.4 | 53.6 | 33.2 | 52.6 | 44.6 | 45.6 | 63.8 | 85.6 | 85.2 | 68.3 | 44.9 | 52.8 | 295.8 | 272.8 | 318.9 | 65 | 252.9 | 65.9 | 71.7 | 67.1 | 276.4 | 294.5 | 218.2 | 351.6 | 267 | 369.3 | 370
2915.1 | 2676.1 | -6 | 0 | 0 | 274.4 | 239.4 | 226.6 | 217.1 | 255.5 | 40.5 | 18.1 | 68.8 | 4.9 | 282.7 | 6.3 | 55.4 | 53.4 | 33 | 52.7 | 44.7 | 45.5 | 63.7 | 86.1 | 85.2 | 68.3 | 45 | 52.8 | 295.9 | 272.3 | 318.8 | 65 | 252.7 | 65.5 | 71.7 | 67 | 276.3 | 294.4 | 218.2 | 351.4 | 266.8 | 369.1 | 369.8
2916.1 | 2677.1 | -5.9 | 0 | 0 | 274.4 | 239.3 | 226.3 | 217 | 255.3 | 40.5 | 18.1 | 68.8 | 4.3 | 239.7 | 5.3 | 55.4 | 53.2 | 32.9 | 52.7 | 44.7 | 45.5 | 63.7 | 86.6 | 85.4 | 68.4 | 45.1 | 52.8 | 296 | 272.1 | 318.6 | 65.1 | 252.7 | 65.6 | 71.7 | 67 | 276.2 | 294.6 | 218.1 | 351.2 | 266.7 | 368.9 | 369.6
2917.1 | 2678.1 | -6 | 0 | 0 | 274.3 | 239.1 | 226.1 | 216.9 | 255.3 | 40.4 | 18.1 | 68.7 | 3.7 | 235.7 | 8.7 | 55.4 | 53.4 | 33.1 | 52.8 | 44.7 | 45.5 | 63.8 | 86.7 | 85.6 | 68.3 | 45.2 | 52.9 | 296.4 | 272 | 318.5 | 65.2 | 252.6 | 65.9 | 71.7 | 67.1 | 276.1 | 294.4 | 218 | 351 | 266.6 | 368.7 | 369.4
2918.1 | 2679.1 | -6 | 0 | 0 | 274.2 | 238.9 | 226.2 | 216.7 | 255.2 | 40.4 | 18.1 | 68.6 | 5.2 | 216.7 | 11.3 | 55.4 | 53.8 | 33.1 | 52.8 | 44.8 | 45.5 | 63.7 | 88.7 | 85.4 | 68.4 | 45.3 | 52.9 | 296.9 | 271.8 | 318.4 | 65.2 | 252.6 | 66.1 | 71.7 | 67.2 | 276 | 294.4 | 218 | 350.8 | 266.4 | 368.4 | 369.2
2919.1 | 2680.1 | -6 | 0 | 0 | 274 | 238.7 | 226.2 | 216.6 | 255.2 | 40.4 | 18.1 | 68.6 | 5.4 | 213.4 | 10.6 | 55.4 | 53.6 | 33.2 | 52.8 | 44.8 | 45.5 | 63.7 | 90 | 85.3 | 68.4 | 45.4 | 52.9 | 296.7 | 271.2 | 318.2 | 65.3 | 252.6 | 66.2 | 71.7 | 67.3 | 275.9 | 294.3 | 217.9 | 350.6 | 266.3 | 368.2 | 369
2920.1 | 2681.1 | -5.9 | 0 | 0 | 273.7 | 238.5 | 226.1 | 216.4 | 255.3 | 40.4 | 18.1 | 68.6 | 5 | 247.6 | 9.2 | 55.4 | 53 | 33.1 | 52.9 | 44.8 | 45.5 | 63.7 | 90.9 | 85.1 | 68.5 | 45.5 | 52.9 | 296.8 | 270.8 | 318.1 | 65.3 | 252.6 | 66.3 | 71.8 | 67.3 | 275.8 | 294.3 | 217.7 | 350.4 | 266.2 | 367.9 | 368.9
2921.1 | 2682.1 | -5.9 | 0 | 0 | 273.5 | 238.1 | 225.9 | 216.3 | 255.3 | 40.4 | 18.1 | 68.6 | 4.8 | 227.6 | 7.6 | 55.4 | 52.8 | 33.2 | 52.9 | 44.8 | 45.5 | 63.8 | 91.6 | 85 | 68.5 | 45.6 | 52.9 | 297.1 | 269.9 | 318 | 65.4 | 252.4 | 66 | 71.9 | 67.3 | 275.7 | 294.3 | 217.5 | 350.2 | 266.1 | 367.7 | 368.7
2922.1 | 2683.1 | -6 | 0 | 0 | 272.9 | 237.7 | 225.9 | 216.3 | 255.3 | 40.4 | 18.1 | 68.5 | 5 | 235.2 | 7.1 | 55.5 | 52.3 | 33.2 | 53 | 44.9 | 45.5 | 63.8 | 92.5 | 85 | 68.6 | 45.7 | 53 | 297.4 | 271.4 | 317.8 | 65.4 | 252.4 | 65.7 | 72 | 67.2 | 275.6 | 294.1 | 217.4 | 350 | 265.9 | 367.5 | 368.5
2923.1 | 2684.1 | -6.1 | 0 | 0 | 272.6 | 237.3 | 225.9 | 216.1 | 255.4 | 40.4 | 18.1 | 68.4 | 5.8 | 243.7 | 7.8 | 55.4 | 52 | 33.2 | 53 | 44.9 | 45.4 | 63.8 | 93.5 | 85 | 68.8 | 45.8 | 53 | 297.5 | 271.9 | 317.7 | 65.4 | 252.5 | 65.5 | 72 | 67.2 | 275.5 | 294 | 217.3 | 349.8 | 265.8 | 367.2 | 368.3
2924.1 | 2685.1 | -6.2 | 0 | 0 | 272.1 | 237.1 | 225.8 | 216 | 255.4 | 40.3 | 18.1 | 68.4 | 5.1 | 248.4 | 8.2 | 55.5 | 51.9 | 33.3 | 53 | 44.9 | 45.4 | 63.7 | 94.1 | 84.8 | 68.8 | 45.9 | 53.1 | 297.5 | 271 | 317.6 | 65.4 | 252.5 | 65.3 | 72 | 67.1 | 275.4 | 294.1 | 217.2 | 349.6 | 265.6 | 367 | 368.1
2925.1 | 2686.1 | -6.1 | 0 | 0 | 271.9 | 236.9 | 225.6 | 215.8 | 255.5 | 40.3 | 18.1 | 68.4 | 5 | 245 | 8.8 | 55.5 | 52.1 | 33.3 | 53.1 | 45 | 45.5 | 63.7 | 94.4 | 84.2 | 68.8 | 46 | 53.1 | 297.4 | 269.6 | 317.4 | 65.5 | 252.4 | 65.6 | 71.9 | 67.3 | 275.3 | 294.1 | 217 | 349.4 | 265.5 | 366.8 | 367.9
2926.1 | 2687.1 | -6 | 0 | 0 | 271.8 | 236.7 | 225.3 | 215.6 | 255.4 | 40.3 | 18.1 | 68.3 | 4.9 | 238.3 | 11.7 | 55.5 | 52.5 | 33.3 | 53.1 | 45 | 45.4 | 63.7 | 94.9 | 83.8 | 68.9 | 46.1 | 53.1 | 297.2 | 269.9 | 317.3 | 65.5 | 252.2 | 65.1 | 71.9 | 67.4 | 275.2 | 294.1 | 216.9 | 349.1 | 265.4 | 366.5 | 367.8
2927.1 | 2688.1 | -5.9 | 0 | 0 | 271.8 | 236.4 | 225.3 | 215.5 | 255.4 | 40.3 | 18.1 | 68.2 | 5.3 | 237.4 | 11.8 | 55.5 | 52.5 | 33.2 | 53.2 | 45 | 45.3 | 63.8 | 95.8 | 83.9 | 68.8 | 46.2 | 53.1 | 297 | 269.3 | 317.1 | 65.5 | 252.3 | 65.6 | 72 | 67.4 | 275.1 | 293.9 | 216.8 | 348.9 | 265.3 | 366.3 | 367.6
2928.1 | 2689.1 | -5.8 | 0 | 0 | 271.8 | 236.2 | 225.4 | 215.4 | 255.4 | 40.2 | 18.2 | 68.2 | 4.5 | 242.1 | 10 | 55.5 | 52.6 | 33.1 | 53.2 | 45 | 45.3 | 63.8 | 96.6 | 84.1 | 68.8 | 46.3 | 53 | 296.9 | 268.8 | 317 | 65.5 | 252.3 | 65.9 | 72 | 67.4 | 274.9 | 293.5 | 216.8 | 348.7 | 265.1 | 366.1 | 367.4
2929.1 | 2690.1 | -5.8 | 0 | 0 | 271.7 | 236.1 | 225.3 | 215.5 | 255.4 | 40.1 | 18.2 | 68.1 | 3.6 | 236.8 | 11.3 | 55.5 | 52.3 | 33.2 | 53.3 | 45.1 | 45.3 | 63.8 | 97.1 | 83.8 | 68.7 | 46.4 | 53 | 296.7 | 268.4 | 316.9 | 65.5 | 252.3 | 65.8 | 72 | 67.3 | 274.8 | 293.2 | 216.8 | 348.5 | 265 | 365.9 | 367.2
2930.1 | 2691.1 | -6 | 0 | 0 | 271.5 | 236.1 | 225.1 | 215.5 | 255.3 | 40.1 | 18.2 | 68.1 | 3.5 | 239.2 | 11.8 | 55.5 | 52.5 | 33.2 | 53.3 | 45.1 | 45.2 | 63.8 | 97.4 | 83.6 | 68.5 | 46.5 | 53.2 | 296.7 | 268.2 | 316.7 | 65.6 | 252.2 | 65.7 | 72 | 67.3 | 274.7 | 293 | 216.8 | 348.3 | 264.9 | 365.7 | 367
2931.1 | 2692.1 | -6 | 0 | 0 | 271.4 | 236.3 | 224.8 | 215.3 | 255.2 | 40.1 | 18.2 | 68 | 4.4 | 243.3 | 11.8 | 55.6 | 52.5 | 33.2 | 53.3 | 45.1 | 45.3 | 63.8 | 97.9 | 83.6 | 68.6 | 46.6 | 53.3 | 296.8 | 267.9 | 316.6 | 65.6 | 252.1 | 66.1 | 72 | 67.3 | 274.6 | 292.8 | 216.7 | 348.1 | 264.7 | 365.4 | 366.8
2932.1 | 2693.1 | -6 | 0 | 0 | 271.2 | 236.3 | 224.7 | 215.2 | 255.1 | 40 | 18.2 | 68 | 4.8 | 248.6 | 11.8 | 55.5 | 52 | 33.5 | 53.4 | 45.1 | 45.3 | 63.8 | 98.8 | 83.3 | 68.7 | 46.7 | 53.3 | 296.9 | 268.5 | 316.4 | 65.6 | 252 | 66.2 | 72 | 67.5 | 274.5 | 292.7 | 216.6 | 347.9 | 264.6 | 365.2 | 366.7
2933.1 | 2694.1 | -5.9 | 0 | 0 | 271.2 | 236.2 | 224.7 | 215.1 | 254.9 | 40 | 18.2 | 68.1 | 5 | 242.9 | 10.4 | 55.6 | 52.5 | 33.5 | 53.4 | 45.2 | 45.3 | 63.9 | 99.2 | 83 | 68.5 | 46.8 | 53.3 | 297.2 | 267.6 | 316.3 | 65.7 | 251.9 | 65.9 | 72 | 67.6 | 274.4 | 292.5 | 216.5 | 347.7 | 264.4 | 365 | 366.5
2934.1 | 2695.1 | -5.7 | 0 | 0 | 271 | 236 | 224.4 | 214.9 | 254.7 | 40 | 18.2 | 68.1 | 6.1 | 248.8 | 9.1 | 55.6 | 52.3 | 33.4 | 53.5 | 45.2 | 45.3 | 63.8 | 99.6 | 82.9 | 68.5 | 46.9 | 53.4 | 297 | 266 | 316.2 | 65.7 | 251.7 | 65.9 | 72.1 | 67.7 | 274.3 | 292.5 | 216.4 | 347.5 | 264.3 | 364.7 | 366.3
2935.1 | 2696.1 | -5.8 | 0 | 0 | 271 | 235.6 | 224 | 214.8 | 254.7 | 40 | 18.2 | 68 | 6.6 | 244.4 | 8.7 | 55.6 | 52.7 | 33.2 | 53.5 | 45.2 | 45.2 | 63.9 | 100.2 | 83 | 68.5 | 47 | 53.4 | 297 | 266.6 | 316 | 65.7 | 251.7 | 66.2 | 72.1 | 67.6 | 274.2 | 292.5 | 216.3 | 347.3 | 264.2 | 364.5 | 366.1
2936.1 | 2697.1 | -5.7 | 0 | 0 | 270.8 | 235.3 | 223.8 | 214.8 | 254.6 | 40 | 18.2 | 67.9 | 6 | 260.9 | 8.1 | 55.6 | 53 | 33 | 53.5 | 45.2 | 45.1 | 64 | 100.7 | 82.8 | 68.4 | 47.1 | 53.4 | 297.1 | 266.7 | 315.9 | 65.7 | 251.8 | 66.4 | 72.2 | 67.7 | 274.1 | 292.5 | 216.1 | 347.1 | 264 | 364.3 | 366
2937.1 | 2698.1 | -5.8 | 0 | 0 | 270.6 | 235.1 | 223.4 | 214.7 | 254.5 | 40 | 18.2 | 67.8 | 6.5 | 256.9 | 8.8 | 55.6 | 53.3 | 33 | 53.6 | 45.2 | 45 | 64 | 101.3 | 82.7 | 68.3 | 47.2 | 53.4 | 297 | 266.1 | 315.7 | 65.8 | 251.7 | 66.5 | 72.3 | 67.7 | 273.9 | 292.5 | 216 | 346.9 | 263.9 | 364.1 | 365.8
2938.1 | 2699.1 | -6 | 0 | 0 | 270.4 | 235.1 | 223.1 | 214.7 | 254.4 | 40 | 18.2 | 67.7 | 5.4 | 249.3 | 9.8 | 55.6 | 53.3 | 33.1 | 53.6 | 45.3 | 45 | 64 | 101.5 | 82.7 | 68.1 | 47.3 | 53.5 | 296.9 | 265.8 | 315.6 | 65.8 | 251.5 | 66.5 | 72.3 | 67.9 | 273.9 | 292.5 | 215.8 | 346.7 | 263.8 | 363.9 | 365.6
2939.1 | 2700.1 | -6.2 | 0 | 0 | 270.4 | 235.1 | 223.2 | 214.6 | 254.2 | 40 | 18.2 | 67.6 | 5.1 | 240.2 | 11.2 | 55.6 | 52.7 | 33 | 53.6 | 45.3 | 45 | 64 | 102.3 | 82.9 | 68 | 47.4 | 53.6 | 296.9 | 265.6 | 315.5 | 65.8 | 251.5 | 66.2 | 72.3 | 68 | 273.7 | 292.4 | 215.7 | 346.5 | 263.6 | 363.6 | 365.4
2940.1 | 2701.1 | -6.2 | 0 | 0 | 270.5 | 235 | 223.3 | 214.4 | 254 | 40 | 18.2 | 67.5 | 3.9 | 245.3 | 14.3 | 55.6 | 52.5 | 32.9 | 53.7 | 45.3 | 45 | 64 | 102.8 | 83.1 | 68.2 | 47.5 | 53.6 | 297 | 265.9 | 315.3 | 65.8 | 251.4 | 66.3 | 72.3 | 68.1 | 273.6 | 292.1 | 215.6 | 346.3 | 263.5 | 363.4 | 365.3
2941.1 | 2702.1 | -6.2 | 0 | 0 | 270.3 | 234.9 | 223.2 | 214.2 | 253.8 | 40 | 18.2 | 67.5 | 4 | 241.2 | 14.2 | 55.6 | 52.5 | 32.8 | 53.7 | 45.3 | 45 | 64 | 103.1 | 83.3 | 68.3 | 47.6 | 53.7 | 297.3 | 265.6 | 315.2 | 65.8 | 251.4 | 66.4 | 72.4 | 68.1 | 273.5 | 291.9 | 215.4 | 346.1 | 263.4 | 363.2 | 365.1
2942.1 | 2703.1 | -6.1 | 0 | 0 | 270.2 | 234.9 | 222.8 | 213.9 | 253.6 | 40 | 18.2 | 67.5 | 3.9 | 230.7 | 13.8 | 55.6 | 52.7 | 32.8 | 53.7 | 45.3 | 45.1 | 63.9 | 103.9 | 83.7 | 68.2 | 47.7 | 53.7 | 297.3 | 265.2 | 315.1 | 65.8 | 251.2 | 66.6 | 72.5 | 68.1 | 273.4 | 291.6 | 215.3 | 345.9 | 263.3 | 363 | 364.9
2943.1 | 2704.1 | -6.1 | 0 | 0 | 270.1 | 235 | 222.5 | 213.7 | 253.6 | 40 | 18.2 | 67.5 | 4.3 | 236.1 | 13.6 | 55.7 | 52.8 | 32.7 | 53.8 | 45.4 | 45 | 64 | 104.9 | 84.2 | 68.1 | 47.8 | 53.7 | 297.4 | 265 | 314.9 | 65.8 | 251 | 66.7 | 72.6 | 68.1 | 273.3 | 291.4 | 215.2 | 345.7 | 263.1 | 362.7 | 364.7
2944.1 | 2705.1 | -5.9 | 0 | 0 | 269.8 | 235.1 | 222.4 | 213.5 | 253.4 | 40 | 18.2 | 67.5 | 5.1 | 238.9 | 11.4 | 55.7 | 52.7 | 32.9 | 53.8 | 45.4 | 45 | 64 | 105.4 | 84.6 | 68.1 | 47.9 | 53.6 | 297.5 | 265 | 314.8 | 65.8 | 250.8 | 66.5 | 72.6 | 68.2 | 273.2 | 291.4 | 215.1 | 345.4 | 263 | 362.5 | 364.5
2945.1 | 2706.1 | -5.9 | 0 | 0 | 269.6 | 235.2 | 222.4 | 213.3 | 253.4 | 40 | 18.2 | 67.5 | 5.2 | 211.7 | 9.7 | 55.7 | 52.8 | 32.9 | 53.9 | 45.4 | 45 | 64 | 106.3 | 84.3 | 68.2 | 48 | 53.5 | 297.6 | 264.6 | 314.6 | 65.8 | 250.8 | 66.6 | 72.6 | 68.3 | 273.1 | 291.4 | 215 | 345.3 | 262.9 | 362.3 | 364.4
2946.1 | 2707.1 | -6 | 0 | 0 | 269.4 | 235.2 | 222.4 | 213.1 | 253.3 | 40 | 18.2 | 67.4 | 4.8 | 225.5 | 10 | 55.7 | 52.6 | 32.9 | 53.9 | 45.5 | 45 | 64 | 107.4 | 83.8 | 68.2 | 48.1 | 53.6 | 297.7 | 264.4 | 314.5 | 65.8 | 250.6 | 66.6 | 72.7 | 68.3 | 273 | 291.3 | 214.9 | 345.1 | 262.7 | 362.1 | 364.2
2947.1 | 2708.1 | -6 | 0 | 0 | 269.1 | 235 | 222.4 | 212.8 | 253.1 | 39.9 | 18.2 | 67.4 | 5.4 | 249.3 | 9.6 | 55.7 | 52.5 | 33 | 54 | 45.5 | 45 | 64 | 108.7 | 83.9 | 68.2 | 48.2 | 53.6 | 297.7 | 265.2 | 314.4 | 65.8 | 250.6 | 65.9 | 72.8 | 68.2 | 272.9 | 291 | 214.7 | 344.8 | 262.6 | 361.8 | 364
2948.1 | 2709.1 | -6.1 | 0 | 0 | 268.7 | 234.9 | 222.3 | 212.5 | 252.9 | 39.8 | 18.2 | 67.3 | 5.2 | 242.9 | 13.2 | 55.7 | 52.4 | 33 | 54 | 45.5 | 45.1 | 64 | 110.2 | 83.9 | 68.3 | 48.3 | 53.6 | 297.8 | 264.4 | 314.2 | 65.8 | 250.6 | 65.9 | 72.8 | 67.9 | 272.8 | 290.8 | 214.6 | 344.6 | 262.5 | 361.6 | 363.8
2949.1 | 2710.1 | -6.2 | 0 | 0 | 268.6 | 234.8 | 222 | 212.4 | 252.7 | 39.7 | 18.2 | 67.2 | 5.6 | 253.2 | 15.3 | 55.7 | 52 | 33.2 | 54 | 45.5 | 45.1 | 64 | 111.5 | 84.2 | 68.3 | 48.4 | 53.6 | 297.9 | 265.6 | 314.1 | 65.8 | 250.4 | 66.3 | 72.8 | 68 | 272.7 | 290.6 | 214.4 | 344.4 | 262.4 | 361.4 | 363.7
2950.1 | 2711.1 | -6.2 | 0 | 0 | 268.4 | 234.5 | 221.7 | 212.4 | 252.4 | 39.7 | 18.2 | 67.3 | 3.8 | 232.3 | 12.8 | 55.7 | 52.1 | 33.3 | 54.1 | 45.6 | 45.1 | 64 | 112.5 | 84 | 68.3 | 48.5 | 53.6 | 298.2 | 265.5 | 313.9 | 65.8 | 250.3 | 66 | 72.9 | 68.1 | 272.6 | 290.6 | 214.3 | 344.2 | 262.2 | 361.2 | 363.5
2951.1 | 2712.1 | -6 | 0 | 0 | 268.3 | 234.6 | 221.4 | 212.4 | 252.1 | 39.6 | 18.2 | 67.3 | 4.3 | 239.4 | 11.2 | 55.7 | 51.6 | 33.2 | 54.1 | 45.6 | 45 | 64 | 113.4 | 83.4 | 68.4 | 48.6 | 53.6 | 298.3 | 265.4 | 313.8 | 65.9 | 250.3 | 66.2 | 73 | 68.3 | 272.5 | 290.5 | 214.2 | 344 | 262.1 | 361 | 363.3
2952.1 | 2713.1 | -6 | 0 | 0 | 268 | 234.7 | 221.2 | 212.2 | 251.8 | 39.6 | 18.3 | 67.2 | 4.2 | 243.8 | 12.1 | 55.7 | 51.1 | 33.2 | 54.1 | 45.6 | 45 | 64 | 114.2 | 83.4 | 68.4 | 48.7 | 53.7 | 298.3 | 264.5 | 313.7 | 65.9 | 250.1 | 66.4 | 73.1 | 68.2 | 272.4 | 290.5 | 214 | 343.7 | 262 | 360.8 | 363.1
2953.1 | 2714.1 | -5.9 | 0 | 0 | 267.8 | 234.6 | 221.1 | 212.1 | 251.5 | 39.5 | 18.3 | 67.2 | 4.9 | 242.1 | 11.8 | 55.7 | 51.3 | 33.1 | 54.2 | 45.6 | 45 | 64 | 115.2 | 83.8 | 68.6 | 48.8 | 53.7 | 298.4 | 264.8 | 313.5 | 65.8 | 249.9 | 66.4 | 73.1 | 68.3 | 272.2 | 290.5 | 213.9 | 343.6 | 261.8 | 360.5 | 362.9
2954.1 | 2715.1 | -5.8 | 0 | 0 | 267.4 | 234.5 | 220.9 | 212.1 | 251.2 | 39.4 | 18.3 | 67.2 | 4.8 | 248.3 | 14.1 | 55.8 | 51.3 | 33 | 54.2 | 45.7 | 45 | 64 | 116.3 | 84.2 | 68.6 | 48.9 | 53.7 | 298.7 | 265.3 | 313.4 | 65.7 | 249.9 | 66.2 | 73.1 | 68.2 | 272.1 | 290.3 | 214 | 343.3 | 261.7 | 360.3 | 362.8
2955.1 | 2716.1 | -5.8 | 0 | 0 | 267.1 | 234.4 | 220.8 | 212.1 | 251.1 | 39.4 | 18.3 | 67.1 | 3.9 | 250.3 | 14 | 55.8 | 51.6 | 33.1 | 54.3 | 45.7 | 44.9 | 64 | 117.4 | 84.1 | 68.7 | 49 | 53.7 | 299.1 | 266.1 | 313.3 | 65.7 | 249.7 | 66 | 73 | 68.3 | 272 | 290.1 | 214 | 343.1 | 261.6 | 360.1 | 362.6
2956.1 | 2717.1 | -5.8 | 0 | 0 | 267.2 | 234.3 | 220.7 | 212 | 251 | 39.4 | 18.3 | 67.1 | 3.8 | 235.9 | 13.5 | 55.8 | 51.8 | 33.1 | 54.3 | 45.7 | 44.9 | 64 | 118.3 | 83.6 | 68.7 | 49.1 | 53.7 | 299.4 | 266 | 313.1 | 65.7 | 249.5 | 65.9 | 72.9 | 68.3 | 271.9 | 290 | 214 | 342.9 | 261.5 | 359.9 | 362.4
2957.1 | 2718.1 | -5.7 | 0 | 0 | 267.1 | 234.2 | 220.5 | 211.8 | 251 | 39.3 | 18.3 | 67.1 | 4.7 | 233.6 | 12.2 | 55.8 | 51.7 | 33.1 | 54.3 | 45.7 | 44.9 | 64 | 119.3 | 83.1 | 68.8 | 49.2 | 53.8 | 299.4 | 266.1 | 313 | 65.7 | 249.5 | 65.5 | 73 | 68.3 | 271.8 | 290 | 213.9 | 342.7 | 261.4 | 359.7 | 362.2
2958.1 | 2719.1 | -5.7 | 0 | 0 | 266.9 | 234.1 | 220.3 | 211.7 | 250.9 | 39.3 | 18.3 | 67.1 | 5.3 | 232.2 | 10.8 | 55.8 | 51.1 | 33 | 54.4 | 45.8 | 44.9 | 64.1 | 120.3 | 82.8 | 68.8 | 49.3 | 53.8 | 299.6 | 266.3 | 312.9 | 65.8 | 249.4 | 65.2 | 73 | 68.1 | 271.7 | 289.8 | 213.8 | 342.5 | 261.2 | 359.4 | 362
2959.1 | 2720.1 | -5.9 | 0 | 0 | 266.8 | 234.3 | 220.2 | 211.6 | 250.8 | 39.3 | 18.3 | 67.1 | 4.8 | 233.7 | 10.5 | 55.8 | 50.9 | 32.9 | 54.4 | 45.8 | 44.8 | 64 | 121.3 | 82.9 | 68.8 | 49.4 | 53.8 | 300.1 | 267.2 | 312.8 | 65.8 | 249.2 | 65.4 | 73 | 68.1 | 271.6 | 289.6 | 213.6 | 342.3 | 261.1 | 359.2 | 361.9
2960.1 | 2721.1 | -5.9 | 0 | 0 | 266.7 | 234.4 | 220.3 | 211.4 | 250.7 | 39.3 | 18.3 | 67.1 | 5.1 | 248.1 | 9.9 | 55.8 | 51.3 | 33 | 54.4 | 45.8 | 44.8 | 64.1 | 122.6 | 83 | 68.7 | 49.5 | 53.8 | 300.4 | 266.3 | 312.6 | 65.7 | 249.1 | 65.5 | 73 | 68.1 | 271.5 | 289.4 | 213.5 | 342.1 | 261 | 359 | 361.7
2961.1 | 2722.1 | -5.8 | 0 | 0 | 266.6 | 234.3 | 220.3 | 211.2 | 250.6 | 39.3 | 18.3 | 67.1 | 5.3 | 260.1 | 10.6 | 55.9 | 51.7 | 32.9 | 54.5 | 45.8 | 44.9 | 64.1 | 123.9 | 82.9 | 68.5 | 49.6 | 53.8 | 300.4 | 266.1 | 312.5 | 65.7 | 249.1 | 65 | 72.9 | 67.9 | 271.4 | 289.1 | 213.4 | 341.9 | 260.8 | 358.8 | 361.5
2962.1 | 2723.1 | -5.7 | 0 | 0 | 266.4 | 234.1 | 220.2 | 211.1 | 250.5 | 39.3 | 18.3 | 67.1 | 5.1 | 253 | 12.2 | 55.9 | 52.3 | 32.8 | 54.5 | 45.9 | 44.9 | 64.1 | 124.9 | 82.7 | 68.5 | 49.7 | 53.8 | 300.3 | 264.8 | 312.3 | 65.7 | 249 | 64.5 | 72.9 | 68 | 271.3 | 289 | 213.3 | 341.7 | 260.7 | 358.6 | 361.3
2963.1 | 2724.1 | -5.5 | 0 | 0 | 266.2 | 233.9 | 220.1 | 210.9 | 250.5 | 39.3 | 18.3 | 67 | 5 | 253.6 | 13.3 | 55.9 | 51.9 | 32.7 | 54.5 | 45.9 | 44.9 | 64.1 | 125.7 | 82.7 | 68.5 | 49.8 | 53.9 | 300.1 | 262 | 312.2 | 65.7 | 248.9 | 64.3 | 72.8 | 67.9 | 271.2 | 288.9 | 213 | 341.5 | 260.6 | 358.4 | 361.2
2964.1 | 2725.1 | -5.7 | 0 | 0 | 266.2 | 233.9 | 220.1 | 210.7 | 250.5 | 39.3 | 18.3 | 67 | 5.1 | 258 | 13.6 | 55.9 | 52.2 | 32.7 | 54.6 | 45.9 | 44.9 | 64.1 | 126.7 | 82.8 | 68.7 | 49.9 | 53.9 | 300.2 | 262.2 | 312.1 | 65.7 | 248.9 | 64.1 | 72.8 | 68 | 271.1 | 288.7 | 212.9 | 341.3 | 260.4 | 358.1 | 361
2965.1 | 2726.1 | -6 | 0 | 0 | 266.2 | 233.8 | 220 | 210.6 | 250.5 | 39.3 | 18.3 | 66.9 | 4.4 | 247.5 | 13.1 | 55.9 | 52.9 | 32.6 | 54.6 | 45.9 | 44.9 | 64.1 | 127.6 | 82.7 | 68.7 | 50 | 53.9 | 300.2 | 262.6 | 311.9 | 65.7 | 249.1 | 64.7 | 72.8 | 68.1 | 271 | 288.7 | 212.7 | 341.1 | 260.3 | 357.9 | 360.8
2966.1 | 2727.1 | -6.1 | 0 | 0 | 266.2 | 233.7 | 219.8 | 210.4 | 250.4 | 39.3 | 18.3 | 66.8 | 4.5 | 246.9 | 13.8 | 55.9 | 53.2 | 32.6 | 54.6 | 45.9 | 44.9 | 64.1 | 128.5 | 82.7 | 68.7 | 50.1 | 54 | 300.2 | 263.1 | 311.8 | 65.7 | 249.1 | 64.7 | 72.8 | 68.3 | 270.9 | 288.6 | 212.7 | 340.9 | 260.1 | 357.7 | 360.6
2967.1 | 2728.1 | -6.1 | 0 | 0 | 266.2 | 233.6 | 219.6 | 210.2 | 250.3 | 39.3 | 18.3 | 66.8 | 5.3 | 263.6 | 14.7 | 55.9 | 53.2 | 32.6 | 54.7 | 46 | 44.8 | 64.1 | 128.9 | 82.6 | 68.6 | 50.2 | 54 | 300.3 | 263.3 | 311.7 | 65.7 | 249.1 | 65.4 | 72.9 | 68.4 | 270.8 | 288.5 | 212.6 | 340.7 | 260 | 357.5 | 360.5
2968.1 | 2729.1 | -6.1 | 0 | 0 | 266.2 | 233.4 | 219.4 | 210.1 | 250.1 | 39.2 | 18.3 | 66.8 | 5.4 | 250.8 | 15.6 | 55.9 | 52.8 | 32.6 | 54.7 | 46 | 44.8 | 64.1 | 129.8 | 82.7 | 68.5 | 50.3 | 54 | 300.7 | 261.8 | 311.5 | 65.7 | 249 | 65.9 | 72.9 | 68.2 | 270.7 | 288.2 | 212.5 | 340.5 | 259.9 | 357.3 | 360.3
2969.1 | 2730.1 | -6.1 | 0 | 0 | 265.9 | 233.3 | 219.2 | 210.1 | 249.9 | 39.2 | 18.3 | 66.8 | 5.5 | 246.5 | 14.7 | 55.9 | 52.4 | 32.6 | 54.7 | 46 | 44.7 | 64.1 | 130.8 | 83.2 | 68.6 | 50.4 | 54 | 300.8 | 261.5 | 311.4 | 65.6 | 248.7 | 65.4 | 72.8 | 68.2 | 270.6 | 287.8 | 212.5 | 340.3 | 259.8 | 357.1 | 360.1
2970.1 | 2731.1 | -6.1 | 0 | 0 | 265.8 | 233.3 | 219 | 210 | 249.8 | 39.1 | 18.3 | 66.8 | 4.2 | 252.6 | 15.1 | 55.9 | 52.1 | 32.6 | 54.8 | 46.1 | 44.7 | 64.1 | 131.2 | 83.1 | 68.5 | 50.5 | 54 | 301 | 262.8 | 311.3 | 65.6 | 248.6 | 65.7 | 72.7 | 68.1 | 270.5 | 287.5 | 212.3 | 340.1 | 259.7 | 356.8 | 359.9
2971.1 | 2732.1 | -6.1 | 0 | 0 | 265.7 | 233.2 | 218.7 | 209.9 | 249.7 | 39.1 | 18.3 | 66.8 | 4 | 255.5 | 13 | 55.9 | 52.1 | 32.6 | 54.8 | 46.1 | 44.6 | 64.1 | 131.8 | 83.2 | 68.4 | 50.6 | 54.1 | 301.5 | 263.2 | 311.1 | 65.6 | 248.4 | 65.8 | 72.8 | 68.3 | 270.4 | 287.4 | 212.2 | 339.9 | 259.6 | 356.6 | 359.8
2972.1 | 2733.1 | -6.1 | 0 | 0 | 265.4 | 233 | 218.4 | 209.7 | 249.4 | 39 | 18.3 | 66.8 | 4.9 | 246.8 | 9.8 | 56 | 52.7 | 32.6 | 54.9 | 46.1 | 44.6 | 64.2 | 132.8 | 83 | 68.4 | 50.7 | 54.1 | 301.6 | 263.6 | 311 | 65.6 | 248 | 65.6 | 73 | 68.4 | 270.3 | 287.4 | 212 | 339.7 | 259.4 | 356.4 | 359.6
2973.1 | 2734.1 | -6.1 | 0 | 0 | 265.3 | 232.9 | 218.1 | 209.6 | 249.2 | 39 | 18.3 | 66.7 | 5.7 | 238.7 | 8.7 | 56 | 52.9 | 32.6 | 54.9 | 46.1 | 44.6 | 64.2 | 133.7 | 82.6 | 68.4 | 50.8 | 54.2 | 301.5 | 266.8 | 310.9 | 65.7 | 248.1 | 65.4 | 73.1 | 68.4 | 270.2 | 287.3 | 211.8 | 339.5 | 259.3 | 356.2 | 359.4
2974.1 | 2735.1 | -5.9 | 0 | 0 | 265.1 | 233 | 218 | 209.4 | 249 | 38.9 | 18.3 | 66.6 | 6.5 | 252.4 | 8.5 | 56 | 53.3 | 32.7 | 54.9 | 46.2 | 44.6 | 64.2 | 134.4 | 82.6 | 68.4 | 50.9 | 54.3 | 301.3 | 263.8 | 310.8 | 65.7 | 248 | 65 | 73 | 68.2 | 270.1 | 287.3 | 211.6 | 339.2 | 259.2 | 356 | 359.2
2975.1 | 2736.1 | -6 | 0 | 0 | 264.8 | 233 | 218 | 209.3 | 248.9 | 38.9 | 18.3 | 66.5 | 6 | 271 | 7.2 | 56 | 52.7 | 32.7 | 54.9 | 46.2 | 44.6 | 64.2 | 134.8 | 82.7 | 68.4 | 51 | 54.4 | 301.4 | 262.8 | 310.6 | 65.6 | 248.1 | 65 | 73 | 68.2 | 270 | 287.3 | 211.4 | 339 | 259.1 | 355.8 | 359.1
2976.1 | 2737.1 | -5.9 | 0 | 0 | 264.5 | 232.9 | 218.1 | 209 | 248.9 | 38.9 | 18.3 | 66.5 | 5 | 277.6 | 5.5 | 56 | 51.9 | 32.7 | 55 | 46.2 | 44.6 | 64.3 | 135.5 | 82.9 | 68.3 | 51.1 | 54.4 | 301.2 | 261.7 | 310.5 | 65.7 | 248 | 65.6 | 73.1 | 68.1 | 269.9 | 287.1 | 211.3 | 338.8 | 259 | 355.6 | 358.9
2977.1 | 2738.1 | -5.9 | 0 | 0 | 264.3 | 232.7 | 218.3 | 208.8 | 248.9 | 38.9 | 18.3 | 66.5 | 5 | 248.9 | 5.4 | 56 | 51.7 | 32.7 | 55 | 46.2 | 44.6 | 64.3 | 136.3 | 83.1 | 68.3 | 51.2 | 54.4 | 301 | 261.2 | 310.3 | 65.7 | 247.9 | 65.6 | 73.1 | 68 | 269.8 | 286.8 | 211.2 | 338.6 | 258.8 | 355.4 | 358.7
2978.1 | 2739.1 | -6 | 0 | 0 | 264.2 | 232.4 | 218.4 | 208.7 | 249 | 38.9 | 18.4 | 66.5 | 5.8 | 245.5 | 6.7 | 56 | 51.2 | 32.5 | 55.1 | 46.2 | 44.5 | 64.3 | 136.6 | 83.2 | 68 | 51.3 | 54.3 | 301 | 261.1 | 310.2 | 65.7 | 248 | 65.5 | 73 | 68.1 | 269.7 | 286.6 | 211 | 338.4 | 258.7 | 355.2 | 358.5
2979.1 | 2740.1 | -6.1 | 0 | 0 | 264.1 | 232.1 | 218.3 | 208.5 | 249 | 38.8 | 18.4 | 66.4 | 8 | 229.1 | 7.6 | 56 | 51.1 | 32.3 | 55.1 | 46.2 | 44.4 | 64.3 | 137.4 | 83.2 | 68.1 | 51.4 | 54.3 | 301 | 260.3 | 310.1 | 65.7 | 248.1 | 65.4 | 72.8 | 68 | 269.5 | 286.3 | 210.9 | 338.2 | 258.6 | 355 | 358.4
2980.1 | 2741.1 | -6.1 | 0 | 0 | 264 | 231.8 | 218.1 | 208.5 | 249.1 | 38.7 | 18.4 | 66.3 | 8.8 | 249.2 | 9.1 | 56 | 50.9 | 32.4 | 55.1 | 46.3 | 44.4 | 64.3 | 138.4 | 83.1 | 68.1 | 51.6 | 54.4 | 300.8 | 260.6 | 310 | 65.7 | 248.1 | 65.5 | 72.8 | 68 | 269.4 | 286.2 | 210.8 | 338 | 258.5 | 354.8 | 358.2
2981.1 | 2742.1 | -6.4 | 0 | 0 | 264.2 | 231.7 | 217.9 | 208.4 | 249 | 38.7 | 18.4 | 66.2 | 7 | 240 | 10 | 56 | 50.5 | 32.5 | 55.2 | 46.3 | 44.3 | 64.3 | 139.2 | 82.9 | 68.1 | 51.6 | 54.5 | 300.8 | 261.4 | 309.8 | 65.7 | 248.1 | 65.6 | 72.7 | 68.1 | 269.3 | 285.7 | 210.7 | 337.8 | 258.3 | 354.6 | 358
2982.1 | 2743.1 | -6.6 | 0 | 0 | 264 | 231.8 | 217.7 | 208.4 | 248.8 | 38.7 | 18.4 | 66.2 | 5.8 | 264.5 | 10.1 | 56 | 50.8 | 32.5 | 55.2 | 46.3 | 44.3 | 64.3 | 139.9 | 82.9 | 68 | 51.7 | 54.5 | 300.8 | 258.6 | 309.7 | 65.7 | 247.9 | 65.7 | 72.8 | 68.1 | 269.2 | 285.4 | 210.4 | 337.6 | 258.2 | 354.3 | 357.8
2983.1 | 2744.1 | -6.7 | 0 | 0 | 263.7 | 231.9 | 217.7 | 208.3 | 248.3 | 38.7 | 18.4 | 66.1 | 5.2 | 241 | 10.3 | 56.1 | 50.7 | 32.5 | 55.3 | 46.3 | 44.2 | 64.3 | 140.5 | 82.7 | 68.1 | 51.8 | 54.5 | 300.8 | 256.6 | 309.6 | 65.7 | 247.9 | 65.6 | 72.9 | 68.2 | 269.1 | 285.2 | 210.3 | 337.4 | 258.1 | 354.1 | 357.7
2984.1 | 2745.1 | -6.6 | 0 | 0 | 263.3 | 232 | 217.6 | 208.1 | 248.1 | 38.7 | 18.4 | 66.1 | 4.7 | 238.6 | 12.2 | 56.1 | 50.4 | 32.7 | 55.3 | 46.3 | 44.2 | 64.3 | 141 | 82.4 | 68 | 51.9 | 54.6 | 300.7 | 256.7 | 309.4 | 65.7 | 247.5 | 65.4 | 72.9 | 68.2 | 269 | 285.1 | 210.3 | 337.2 | 258 | 353.9 | 357.5
2985.1 | 2746.1 | -6.4 | 0 | 0 | 263 | 232.1 | 217.5 | 207.9 | 247.9 | 38.7 | 18.4 | 66 | 5.1 | 256.9 | 11.8 | 56.1 | 50 | 32.9 | 55.3 | 46.4 | 44.2 | 64.3 | 141.7 | 82.4 | 67.8 | 52 | 54.7 | 300.7 | 258.5 | 309.3 | 65.7 | 247.4 | 65.2 | 72.8 | 68.3 | 268.9 | 284.7 | 210.3 | 337 | 257.9 | 353.7 | 357.3
2986.1 | 2747.1 | -6.3 | 0 | 0 | 262.9 | 232 | 217.4 | 207.7 | 247.6 | 38.7 | 18.4 | 65.9 | 4.8 | 252.1 | 12.7 | 56.1 | 50.4 | 32.9 | 55.4 | 46.4 | 44.2 | 64.3 | 142.4 | 82.4 | 67.9 | 52.1 | 54.7 | 301 | 259.6 | 309.2 | 65.7 | 247.4 | 65 | 72.8 | 68.4 | 268.8 | 284.5 | 210.2 | 336.8 | 257.8 | 353.5 | 357.2
2987.1 | 2748.1 | -6.1 | 0 | 0 | 263 | 231.8 | 217.3 | 207.7 | 247.4 | 38.6 | 18.4 | 65.8 | 5.1 | 262.4 | 12.7 | 56.1 | 51 | 32.9 | 55.4 | 46.4 | 44.2 | 64.3 | 142.8 | 82.6 | 67.9 | 52.2 | 54.7 | 301.4 | 260.6 | 309.1 | 65.6 | 247.4 | 65 | 72.6 | 68.4 | 268.7 | 284.5 | 210 | 336.6 | 257.7 | 353.3 | 357
2988.1 | 2749.1 | -6 | 0 | 0 | 263 | 231.5 | 217.1 | 207.5 | 247.2 | 38.6 | 18.4 | 65.7 | 5.2 | 243 | 14.4 | 56.1 | 51.2 | 33 | 55.4 | 46.4 | 44.1 | 64.4 | 142.8 | 82.2 | 68 | 52.3 | 54.8 | 301.8 | 261.3 | 308.9 | 65.7 | 247 | 65.3 | 72.6 | 68.4 | 268.6 | 284.3 | 209.9 | 336.4 | 257.5 | 353.1 | 356.8
2989.1 | 2750.1 | -6.1 | 0 | 0 | 262.8 | 231 | 216.9 | 207.4 | 247.1 | 38.6 | 18.4 | 65.6 | 5.5 | 253.6 | 13.1 | 56.1 | 51.6 | 33.1 | 55.5 | 46.4 | 44.1 | 64.4 | 143.4 | 82.1 | 67.9 | 52.4 | 54.9 | 302 | 262.6 | 308.8 | 65.8 | 246.8 | 65.2 | 72.6 | 68.4 | 268.5 | 284.3 | 209.8 | 336.2 | 257.4 | 352.9 | 356.6
2990.1 | 2751.1 | -6.2 | 0 | 0 | 262.7 | 230.7 | 216.7 | 207.2 | 247.3 | 38.6 | 18.4 | 65.6 | 6.4 | 247.3 | 14.9 | 56.1 | 51.3 | 33.1 | 55.5 | 46.5 | 44.1 | 64.4 | 144.1 | 81.7 | 67.8 | 52.5 | 54.9 | 302.2 | 263.1 | 308.6 | 65.8 | 247 | 65.1 | 72.5 | 68.4 | 268.4 | 284.1 | 209.5 | 336 | 257.3 | 352.7 | 356.5
2991.1 | 2752.1 | -6.1 | 0 | 0 | 262.4 | 230.4 | 216.6 | 207.1 | 247.3 | 38.6 | 18.4 | 65.5 | 7.2 | 248.4 | 17 | 56.1 | 51.2 | 33 | 55.6 | 46.5 | 44.1 | 64.4 | 144.7 | 81.5 | 67.8 | 52.6 | 54.9 | 302.4 | 263.3 | 308.5 | 65.8 | 247 | 64.4 | 72.4 | 68.5 | 268.3 | 284 | 209.3 | 335.8 | 257.1 | 352.5 | 356.3
2992.1 | 2753.1 | -6.2 | 0 | 0 | 261.9 | 230.1 | 216.1 | 207.1 | 247.3 | 38.6 | 18.4 | 65.5 | 6.2 | 253.3 | 17.5 | 56.1 | 51 | 32.6 | 55.6 | 46.5 | 44.1 | 64.4 | 145.3 | 81 | 67.8 | 52.7 | 55 | 302.5 | 262.9 | 308.4 | 65.9 | 247 | 64.4 | 72.5 | 68.2 | 268.2 | 283.8 | 209.1 | 335.6 | 257 | 352.3 | 356.1
2993.1 | 2754.1 | -6.4 | 0 | 0 | 261.7 | 230 | 215.9 | 207.1 | 247.4 | 38.7 | 18.4 | 65.4 | 5.9 | 256.1 | 16.7 | 56.1 | 50.3 | 32.5 | 55.6 | 46.5 | 44.1 | 64.4 | 145.9 | 80.9 | 67.8 | 52.8 | 55 | 302.7 | 262.2 | 308.3 | 65.9 | 247.1 | 63.8 | 72.5 | 68.2 | 268.1 | 283.7 | 208.9 | 335.4 | 256.9 | 352.1 | 356
2994.1 | 2755.1 | -6.3 | 0 | 0 | 261.6 | 229.9 | 215.9 | 207 | 247.5 | 38.7 | 18.4 | 65.3 | 5.6 | 247.9 | 16.4 | 56.1 | 50.4 | 32.4 | 55.7 | 46.6 | 44.1 | 64.5 | 146.1 | 81.2 | 67.8 | 52.9 | 55 | 302.9 | 260.6 | 308.1 | 65.9 | 247.2 | 63.4 | 72.7 | 68.4 | 268 | 283.6 | 208.7 | 335.2 | 256.7 | 351.9 | 355.8
2995.1 | 2756.1 | -6.4 | 0 | 0 | 261.2 | 229.8 | 215.8 | 206.8 | 247.6 | 38.7 | 18.5 | 65.2 | 5.5 | 261.5 | 14.9 | 56.2 | 50.4 | 32.3 | 55.7 | 46.6 | 44.1 | 64.4 | 146.7 | 81.6 | 67.8 | 53 | 55 | 303.1 | 259.7 | 308 | 65.9 | 247.3 | 63.8 | 72.8 | 68.3 | 267.9 | 283.4 | 208.7 | 335 | 256.6 | 351.7 | 355.6
2996.1 | 2757.1 | -6.5 | 0 | 0 | 260.6 | 229.6 | 215.7 | 206.7 | 247.7 | 38.7 | 18.5 | 65.2 | 5 | 263.2 | 14.8 | 56.2 | 50.3 | 32.4 | 55.8 | 46.6 | 44.1 | 64.4 | 147.3 | 81.3 | 67.9 | 53.1 | 54.9 | 303.3 | 260.8 | 307.9 | 66.1 | 247.2 | 64 | 73 | 68.1 | 267.8 | 283.2 | 208.6 | 334.8 | 256.5 | 351.5 | 355.4
2997.1 | 2758.1 | -6.5 | 0 | 0 | 260.5 | 229.4 | 215.6 | 206.7 | 247.7 | 38.6 | 18.5 | 65.1 | 4.4 | 253.6 | 15.4 | 56.2 | 50.3 | 32.5 | 55.8 | 46.6 | 44 | 64.4 | 148 | 80.7 | 67.7 | 53.2 | 55 | 303.4 | 261.4 | 307.7 | 66 | 247.2 | 63.9 | 73.1 | 68.2 | 267.7 | 283 | 208.3 | 334.6 | 256.3 | 351.3 | 355.3
2998.1 | 2759.1 | -6.5 | 0 | 0 | 260.4 | 229.2 | 215.5 | 206.7 | 247.5 | 38.6 | 18.5 | 65.1 | 3.8 | 256 | 16.6 | 56.2 | 50 | 32.5 | 55.8 | 46.7 | 44 | 64.4 | 148.3 | 80.5 | 67.8 | 53.3 | 55 | 303.4 | 260.1 | 307.6 | 66 | 247 | 63.4 | 73.1 | 68.1 | 267.6 | 282.8 | 208.1 | 334.4 | 256.2 | 351 | 355.1
2999.1 | 2760.1 | -6.4 | 0 | 0 | 260.2 | 228.9 | 215 | 206.7 | 247.3 | 38.6 | 18.5 | 65.1 | 3.6 | 245.4 | 14.4 | 56.2 | 49.9 | 32.5 | 55.9 | 46.7 | 44 | 64.5 | 149.1 | 80.3 | 67.8 | 53.4 | 55.1 | 303.2 | 259.8 | 307.5 | 66 | 247.1 | 63.2 | 73.1 | 68 | 267.5 | 282.6 | 208.1 | 334.2 | 256.1 | 350.8 | 354.9
3000.1 | 2761.1 | -6.3 | 0 | 0 | 259.7 | 228.7 | 214.7 | 206.8 | 247.2 | 38.6 | 18.5 | 65 | 4.2 | 255 | 10.8 | 56.2 | 50.4 | 32.4 | 55.9 | 46.7 | 44 | 64.5 | 149.2 | 80.4 | 67.7 | 53.5 | 55.1 | 303.1 | 259.2 | 307.3 | 66 | 247.2 | 63.1 | 73.1 | 68.2 | 267.4 | 282.4 | 207.9 | 334 | 256 | 350.6 | 354.8
3001.1 | 2762.1 | -6.2 | 0 | 0 | 259.6 | 228.4 | 214.6 | 206.9 | 247 | 38.6 | 18.5 | 65 | 5.2 | 266.7 | 11.8 | 56.2 | 50.9 | 32.5 | 56 | 46.7 | 44 | 64.5 | 149.2 | 80.3 | 67.9 | 53.6 | 55.2 | 303.2 | 259.2 | 307.2 | 65.9 | 247.1 | 64.1 | 73.1 | 68.2 | 267.3 | 282.2 | 207.6 | 333.8 | 255.8 | 350.4 | 354.6
3002.1 | 2763.1 | -6 | 0 | 0 | 259.8 | 228.2 | 214.6 | 206.9 | 246.9 | 38.5 | 18.5 | 65 | 5.5 | 250 | 12.2 | 56.2 | 50.5 | 32.4 | 56 | 46.7 | 44.1 | 64.5 | 149.6 | 80.2 | 67.7 | 53.7 | 55.4 | 303.1 | 258.8 | 307.1 | 65.9 | 246.9 | 63.9 | 72.9 | 68.2 | 267.1 | 282 | 207.5 | 333.6 | 255.7 | 350.2 | 354.4
3003.1 | 2764.1 | -5.9 | 0 | 0 | 259.7 | 228 | 214.5 | 206.8 | 246.8 | 38.5 | 18.5 | 64.9 | 5.7 | 253.5 | 13.5 | 56.2 | 50.8 | 32.3 | 56 | 46.8 | 44.1 | 64.6 | 150.1 | 80.4 | 67.6 | 53.8 | 55.4 | 303 | 258.8 | 307 | 65.9 | 246.8 | 64.5 | 72.8 | 68.1 | 267.1 | 281.9 | 207.5 | 333.4 | 255.6 | 350 | 354.3
3004.1 | 2765.1 | -5.8 | 0 | 0 | 259.8 | 227.9 | 214.1 | 206.6 | 246.7 | 38.5 | 18.5 | 64.9 | 5 | 246.7 | 14.1 | 56.3 | 51.3 | 32.2 | 56.1 | 46.8 | 44.1 | 64.6 | 150.5 | 80.6 | 67.6 | 53.9 | 55.4 | 303 | 258.8 | 306.9 | 65.9 | 246.8 | 65 | 72.8 | 68 | 266.9 | 281.7 | 207.6 | 333.2 | 255.5 | 349.8 | 354.1
3005.1 | 2766.1 | -6 | 0 | 0 | 259.8 | 227.8 | 214 | 206.4 | 246.5 | 38.5 | 18.5 | 64.9 | 5 | 251.1 | 12.5 | 56.3 | 51.2 | 32.2 | 56.1 | 46.8 | 44.1 | 64.6 | 150.8 | 80.8 | 67.4 | 54 | 55.4 | 303 | 258.1 | 306.7 | 65.9 | 246.6 | 65.3 | 72.7 | 67.9 | 266.8 | 281.5 | 207.5 | 333.1 | 255.4 | 349.6 | 353.9
3006.1 | 2767.1 | -6.1 | 0 | 0 | 259.5 | 227.5 | 214.2 | 206.5 | 246.3 | 38.4 | 18.5 | 64.9 | 4.6 | 247.9 | 15.7 | 56.3 | 51.7 | 32.1 | 56.1 | 46.8 | 44.1 | 64.6 | 151 | 81 | 67.5 | 54.1 | 55.4 | 303 | 256.9 | 306.6 | 65.9 | 246.4 | 64.2 | 72.7 | 68.1 | 266.7 | 281.2 | 207.4 | 332.9 | 255.3 | 349.4 | 353.7
3007.1 | 2768.1 | -6.3 | 0 | 0 | 259.4 | 227.4 | 214.3 | 206.6 | 246.1 | 38.4 | 18.5 | 64.9 | 5.2 | 247.6 | 15.3 | 56.3 | 51.1 | 31.9 | 56.2 | 46.8 | 44.1 | 64.6 | 151.7 | 81.3 | 67.5 | 54.2 | 55.5 | 302.9 | 254.9 | 306.5 | 65.9 | 246.4 | 63.9 | 72.7 | 68.2 | 266.6 | 281.1 | 207.2 | 332.7 | 255.1 | 349.2 | 353.6
3008.1 | 2769.1 | -6.3 | 0 | 0 | 259.2 | 227.3 | 214 | 206.5 | 245.9 | 38.4 | 18.5 | 64.9 | 4.1 | 249.5 | 13.1 | 56.3 | 51.7 | 31.8 | 56.2 | 46.9 | 44.2 | 64.6 | 151.8 | 81.4 | 67.5 | 54.2 | 55.4 | 302.9 | 255.4 | 306.3 | 65.9 | 246.3 | 64.1 | 72.6 | 68.3 | 266.5 | 280.9 | 207.1 | 332.5 | 255 | 349 | 353.4
3009.1 | 2770.1 | -6.1 | 0 | 0 | 259.1 | 227.3 | 213.6 | 206.4 | 245.8 | 38.4 | 18.5 | 64.8 | 3.9 | 233.5 | 11.9 | 56.3 | 51.6 | 31.6 | 56.2 | 46.9 | 44.2 | 64.6 | 151.9 | 81.4 | 67.6 | 54.3 | 55.4 | 303 | 256 | 306.2 | 65.9 | 246 | 64.5 | 72.4 | 68.1 | 266.4 | 280.7 | 207 | 332.3 | 254.9 | 348.8 | 353.2
3010.1 | 2771.1 | -6 | 0 | 0 | 259 | 227.4 | 213.6 | 206.4 | 245.8 | 38.4 | 18.5 | 64.7 | 3.6 | 247.3 | 9.7 | 56.3 | 51.5 | 31.6 | 56.3 | 46.9 | 44.1 | 64.6 | 152 | 81.1 | 67.6 | 54.4 | 55.3 | 303.1 | 257.9 | 306.1 | 65.9 | 246 | 64.4 | 72.3 | 68.1 | 266.3 | 280.4 | 206.9 | 332.2 | 254.8 | 348.6 | 353
3011.1 | 2772.1 | -6 | 0 | 0 | 258.8 | 227.3 | 213.7 | 206.2 | 245.8 | 38.3 | 18.5 | 64.7 | 4.2 | 248.5 | 8.9 | 56.3 | 51.2 | 31.6 | 56.3 | 46.9 | 44.2 | 64.6 | 152.3 | 81.6 | 67.6 | 54.5 | 55.3 | 303.6 | 258.4 | 305.9 | 65.9 | 245.7 | 64.1 | 72.3 | 68.1 | 266.2 | 280.1 | 206.7 | 332 | 254.7 | 348.4 | 352.9
3012.1 | 2773.1 | -6 | 0 | 0 | 258.5 | 227.2 | 213.7 | 206 | 245.8 | 38.3 | 18.5 | 64.7 | 4.2 | 239.4 | 8.2 | 56.3 | 50.8 | 31.7 | 56.3 | 46.9 | 44.2 | 64.6 | 152.5 | 81.5 | 67.4 | 54.6 | 55.2 | 304.1 | 258.5 | 305.8 | 66 | 245.7 | 64.3 | 72.4 | 68.3 | 266.1 | 279.9 | 206.6 | 331.8 | 254.6 | 348.2 | 352.7
3013.1 | 2774.1 | -6 | 0 | 0 | 258.2 | 227.2 | 213.7 | 205.9 | 245.6 | 38.2 | 18.5 | 64.6 | 4.5 | 235.9 | 8.3 | 56.4 | 50.4 | 31.8 | 56.4 | 46.9 | 44.1 | 64.6 | 152.8 | 80.8 | 67.4 | 54.7 | 55.1 | 304.2 | 258.4 | 305.7 | 66 | 245.7 | 64.5 | 72.5 | 68.4 | 266 | 279.5 | 206.5 | 331.6 | 254.5 | 348 | 352.5
3014.1 | 2775.1 | -6 | 0 | 0 | 257.9 | 227.1 | 213.7 | 205.8 | 245.4 | 38.1 | 18.5 | 64.6 | 4.2 | 257.9 | 9.8 | 56.4 | 50.1 | 31.8 | 56.4 | 46.9 | 44.1 | 64.5 | 153.1 | 79.9 | 67.5 | 54.8 | 55.2 | 304.3 | 257.5 | 305.6 | 66 | 245.9 | 64.2 | 72.4 | 68.4 | 265.9 | 279.3 | 206.4 | 331.4 | 254.4 | 347.8 | 352.4
3015.1 | 2776.1 | -6 | 0 | 0 | 257.8 | 226.9 | 213.5 | 205.7 | 245.3 | 38.1 | 18.5 | 64.6 | 4.8 | 244.5 | 12.2 | 56.4 | 50.2 | 31.6 | 56.4 | 47 | 44.1 | 64.5 | 153.1 | 79.4 | 67.6 | 54.8 | 55.3 | 304.3 | 256.9 | 305.4 | 66 | 245.8 | 64.3 | 72.5 | 68.4 | 265.8 | 279.4 | 206.3 | 331.3 | 254.3 | 347.6 | 352.2
3016.1 | 2777.1 | -5.9 | 0 | 0 | 257.9 | 226.7 | 213.4 | 205.7 | 245.1 | 38.1 | 18.5 | 64.6 | 4 | 257.5 | 12.3 | 56.4 | 50 | 31.6 | 56.5 | 47 | 44.1 | 64.6 | 153.4 | 79.3 | 67.5 | 54.9 | 55.3 | 304.4 | 257.4 | 305.3 | 66 | 245.9 | 63.8 | 72.6 | 68.5 | 265.7 | 279.4 | 206.1 | 331.1 | 254.1 | 347.4 | 352
3017.1 | 2778.1 | -5.9 | 0 | 0 | 257.7 | 226.6 | 213.3 | 205.5 | 245 | 38.1 | 18.5 | 64.6 | 4.3 | 257.6 | 12.5 | 56.4 | 49.9 | 31.7 | 56.5 | 47 | 44.1 | 64.6 | 153.8 | 79 | 67.5 | 55 | 55.3 | 304.4 | 257.7 | 305.2 | 66 | 245.7 | 63.8 | 72.6 | 68.3 | 265.6 | 279.3 | 206 | 330.9 | 254 | 347.2 | 351.9
3018.1 | 2779.1 | -5.9 | 0 | 0 | 257.8 | 226.5 | 213.3 | 205.2 | 244.9 | 38.1 | 18.5 | 64.6 | 4.8 | 247.6 | 12 | 56.4 | 50.2 | 31.7 | 56.5 | 47 | 44 | 64.6 | 153.6 | 78.8 | 67.5 | 55.1 | 55.2 | 304.5 | 258.6 | 305.1 | 66 | 245.3 | 63.5 | 72.6 | 68.1 | 265.5 | 279.3 | 206 | 330.7 | 253.9 | 347 | 351.7
3019.1 | 2780.1 | -5.9 | 0 | 0 | 257.7 | 226.7 | 213.3 | 205.2 | 244.7 | 38.2 | 18.5 | 64.5 | 4.8 | 266.7 | 11.2 | 56.5 | 49.9 | 31.8 | 56.6 | 47 | 44 | 64.6 | 153.8 | 78.8 | 67.4 | 55.2 | 55.2 | 304.7 | 258.3 | 305 | 65.9 | 245.2 | 62.8 | 72.6 | 68 | 265.4 | 279.2 | 206.1 | 330.5 | 253.8 | 346.8 | 351.5
3020.1 | 2781.1 | -5.9 | 0 | 0 | 257.4 | 226.8 | 213.1 | 205.3 | 244.4 | 38.2 | 18.5 | 64.6 | 4.9 | 251.1 | 10.1 | 56.5 | 49.6 | 31.9 | 56.6 | 47.1 | 44 | 64.7 | 154.1 | 78.9 | 67.6 | 55.3 | 55.2 | 304.9 | 259 | 304.8 | 65.9 | 245 | 62.7 | 72.5 | 68 | 265.3 | 279 | 205.9 | 330.3 | 253.7 | 346.6 | 351.4
3021.1 | 2782.1 | -5.8 | 0 | 0 | 257 | 226.8 | 212.9 | 205.3 | 244 | 38.2 | 18.5 | 64.6 | 4.8 | 237.7 | 10.5 | 56.5 | 49.4 | 31.9 | 56.7 | 47.1 | 43.9 | 64.8 | 154.6 | 78.9 | 67.4 | 55.4 | 55.2 | 304.8 | 257.7 | 304.7 | 65.8 | 244.9 | 63.1 | 72.4 | 68.1 | 265.2 | 278.8 | 205.8 | 330.2 | 253.6 | 346.5 | 351.2
3022.1 | 2783.1 | -5.9 | 0 | 0 | 256.6 | 226.5 | 212.9 | 205.3 | 243.6 | 38.2 | 18.5 | 64.5 | 5.3 | 265.2 | 10.6 | 56.5 | 48.9 | 31.9 | 56.7 | 47.1 | 43.9 | 64.8 | 154.7 | 79 | 67.3 | 55.4 | 55.3 | 304.8 | 257.4 | 304.6 | 65.8 | 244.7 | 63.6 | 72.4 | 68.2 | 265.1 | 278.7 | 205.8 | 330 | 253.5 | 346.2 | 351
3023.1 | 2784.1 | -5.9 | 0 | 0 | 256.5 | 226.5 | 212.9 | 205.3 | 243.2 | 38.2 | 18.6 | 64.4 | 4.7 | 244.7 | 10.2 | 56.5 | 48.1 | 31.8 | 56.7 | 47.1 | 43.9 | 64.8 | 155 | 79.2 | 67.4 | 55.5 | 55.3 | 305 | 257.8 | 304.5 | 65.9 | 244.7 | 64.4 | 72.4 | 68.1 | 265 | 278.5 | 205.8 | 329.8 | 253.3 | 346.1 | 350.9
3024.1 | 2785.1 | -5.9 | 0 | 0 | 256.5 | 226.5 | 212.9 | 205.1 | 243.1 | 38.1 | 18.6 | 64.4 | 4.8 | 242.6 | 11 | 56.5 | 47.9 | 31.8 | 56.8 | 47.1 | 43.8 | 64.8 | 155.3 | 79.3 | 67.2 | 55.6 | 55.3 | 305.2 | 257.8 | 304.3 | 65.9 | 244.7 | 64.5 | 72.5 | 68.2 | 264.9 | 278.3 | 205.7 | 329.6 | 253.3 | 345.9 | 350.7
3025.1 | 2786.1 | -6 | 0 | 0 | 256.5 | 226.1 | 212.9 | 204.8 | 243.2 | 38.1 | 18.6 | 64.3 | 5 | 248 | 10.3 | 56.6 | 48.1 | 31.8 | 56.8 | 47.2 | 43.8 | 64.8 | 155.6 | 79.1 | 67.3 | 55.7 | 55.3 | 305.2 | 257.5 | 304.2 | 65.9 | 244.7 | 65.1 | 72.5 | 68.4 | 264.8 | 278.3 | 205.6 | 329.4 | 253.1 | 345.7 | 350.5
3026.1 | 2787.1 | -6 | 0 | 0 | 256.4 | 225.7 | 212.7 | 204.5 | 243.2 | 38.1 | 18.6 | 64.3 | 4.7 | 237.9 | 11.2 | 56.6 | 48.6 | 31.9 | 56.8 | 47.2 | 43.7 | 64.8 | 155.1 | 78.7 | 67.5 | 55.8 | 55.3 | 305.2 | 256.5 | 304.1 | 65.9 | 244.6 | 64.9 | 72.5 | 68.5 | 264.7 | 278.3 | 205.6 | 329.3 | 253 | 345.5 | 350.4
3027.1 | 2788.1 | -6.2 | 0 | 0 | 256.1 | 225.4 | 212.7 | 204.3 | 243.4 | 38.1 | 18.6 | 64.2 | 4.7 | 229.5 | 11.8 | 56.6 | 48.3 | 32 | 56.9 | 47.2 | 43.7 | 64.8 | 155 | 78.2 | 67.6 | 55.8 | 55.2 | 305.2 | 257.4 | 304 | 65.9 | 244.8 | 65 | 72.5 | 68.4 | 264.6 | 278 | 205.7 | 329.1 | 252.9 | 345.3 | 350.2
3028.1 | 2789.1 | -6.3 | 0 | 0 | 255.8 | 225.4 | 212.7 | 204.2 | 243.5 | 38 | 18.6 | 64.2 | 5.7 | 234.7 | 9.1 | 56.6 | 48.1 | 32.1 | 56.9 | 47.2 | 43.6 | 64.9 | 155.1 | 77.7 | 67.6 | 55.9 | 55.3 | 305.3 | 257.6 | 303.8 | 66 | 244.8 | 63.5 | 72.5 | 68.3 | 264.5 | 278 | 205.6 | 328.9 | 252.8 | 345.1 | 350
3029.1 | 2790.1 | -6.2 | 0 | 0 | 255.4 | 225.4 | 212.4 | 204.2 | 243.5 | 38 | 18.6 | 64.3 | 4.5 | 236.2 | 8.1 | 56.6 | 48 | 32 | 56.9 | 47.2 | 43.5 | 64.9 | 155.1 | 77.7 | 67.5 | 56 | 55.4 | 305.1 | 258 | 303.7 | 66 | 244.4 | 63.1 | 72.5 | 68.2 | 264.4 | 277.9 | 205.6 | 328.7 | 252.7 | 344.9 | 349.9
3030.1 | 2791.1 | -6.2 | 0 | 0 | 255.2 | 225.2 | 212.3 | 204.1 | 243.4 | 38 | 18.6 | 64.3 | 4.1 | 260.9 | 8.2 | 56.6 | 48.2 | 32.1 | 56.9 | 47.2 | 43.5 | 64.9 | 155.1 | 78 | 67.6 | 56.1 | 55.3 | 304.8 | 256 | 303.6 | 66 | 244.6 | 62.9 | 72.7 | 68.2 | 264.3 | 277.6 | 205.4 | 328.5 | 252.6 | 344.7 | 349.7
3031.1 | 2792.1 | -6.1 | 0 | 0 | 255.2 | 225.1 | 212.3 | 204.1 | 243.4 | 38 | 18.6 | 64.3 | 4.4 | 249.9 | 9.8 | 56.7 | 48.7 | 32.2 | 57 | 47.3 | 43.4 | 65 | 155.6 | 78.1 | 67.4 | 56.2 | 55.2 | 304.7 | 255.1 | 303.5 | 66 | 244.6 | 62.4 | 72.8 | 68.4 | 264.2 | 277.5 | 205.3 | 328.4 | 252.4 | 344.5 | 349.5
3032.1 | 2793.1 | -5.9 | 0 | 0 | 255 | 225 | 212.1 | 204.2 | 243.4 | 38 | 18.6 | 64.3 | 4.8 | 263.8 | 10.8 | 56.7 | 49.8 | 32.1 | 57 | 47.3 | 43.3 | 65 | 155.7 | 78 | 67.1 | 56.3 | 55.2 | 305 | 254.7 | 303.4 | 66 | 244.6 | 62 | 72.8 | 68.1 | 264.1 | 277.3 | 205.3 | 328.2 | 252.3 | 344.3 | 349.4
3033.1 | 2794.1 | -5.9 | 0 | 0 | 254.6 | 224.9 | 212.1 | 204.2 | 243.2 | 38 | 18.6 | 64.2 | 5 | 254.7 | 11.6 | 56.7 | 49.8 | 32 | 57 | 47.3 | 43.3 | 65.1 | 155.7 | 78.3 | 67.4 | 56.3 | 55.2 | 305.3 | 255.8 | 303.2 | 66 | 244.5 | 62.4 | 72.8 | 67.9 | 264 | 277.3 | 205.4 | 328 | 252.2 | 344.1 | 349.2
3034.1 | 2795.1 | -5.9 | 0 | 0 | 254 | 224.6 | 211.9 | 204 | 243 | 38 | 18.6 | 64.2 | 4.6 | 286.8 | 10.1 | 56.7 | 48.8 | 31.9 | 57.1 | 47.3 | 43.2 | 65.1 | 155.8 | 78.4 | 67.4 | 56.4 | 55.2 | 305.5 | 256 | 303.1 | 65.9 | 244.5 | 62 | 72.6 | 68 | 263.9 | 277.3 | 205.3 | 327.8 | 252.1 | 343.9 | 349
3035.1 | 2796.1 | -6 | 0 | 0 | 253.9 | 224.2 | 211.7 | 203.9 | 242.8 | 38.1 | 18.6 | 64.2 | 4.2 | 247.5 | 10.1 | 56.7 | 49.1 | 32 | 57.1 | 47.3 | 43.2 | 65.1 | 156.2 | 77.8 | 67.3 | 56.5 | 55.2 | 305.6 | 255.8 | 303 | 66 | 244.3 | 61.6 | 72.6 | 68.2 | 263.8 | 277.1 | 205.2 | 327.7 | 252 | 343.7 | 348.9
3036.1 | 2797.1 | -6.1 | 0 | 0 | 254 | 224.2 | 211.6 | 203.6 | 242.5 | 38.1 | 18.6 | 64.2 | 4.7 | 250.1 | 11.5 | 56.8 | 48.9 | 31.8 | 57.1 | 47.4 | 43.2 | 65.2 | 156.3 | 77.1 | 67.2 | 56.6 | 55.3 | 305.6 | 255.6 | 302.9 | 65.9 | 244.4 | 62.2 | 72.5 | 68.1 | 263.7 | 276.8 | 205.2 | 327.5 | 251.9 | 343.5 | 348.7
3037.1 | 2798.1 | -5.9 | 0 | 0 | 254.1 | 224.1 | 211.4 | 203.3 | 242.4 | 38.1 | 18.6 | 64.2 | 4.7 | 236.3 | 11.1 | 56.8 | 48.4 | 31.5 | 57.1 | 47.4 | 43.1 | 65.1 | 156.4 | 76.8 | 67.4 | 56.7 | 55.3 | 305.5 | 255.3 | 302.7 | 65.8 | 244.1 | 62.9 | 72.3 | 68.1 | 263.6 | 276.7 | 205.1 | 327.3 | 251.7 | 343.3 | 348.5
3038.1 | 2799.1 | -6 | 0 | 0 | 254.1 | 224 | 211.2 | 203 | 242.2 | 38.1 | 18.6 | 64.2 | 5.1 | 247.3 | 10.8 | 56.8 | 48.7 | 31.4 | 57.2 | 47.4 | 43.1 | 65.1 | 156.8 | 76.4 | 67.6 | 56.7 | 55.3 | 305.3 | 254.2 | 302.6 | 65.9 | 244.3 | 62.2 | 72.3 | 68.3 | 263.5 | 276.4 | 205 | 327.1 | 251.6 | 343.2 | 348.4
3039.1 | 2800.1 | -6 | 0 | 0 | 254.1 | 224 | 211 | 202.9 | 242.1 | 38.1 | 18.6 | 64.1 | 4.7 | 242.8 | 10.5 | 56.8 | 49.1 | 31.3 | 57.2 | 47.4 | 43.1 | 65.2 | 156.9 | 76.3 | 67.7 | 56.8 | 55.4 | 304.9 | 254.5 | 302.5 | 66 | 244.1 | 61.9 | 72.4 | 68.3 | 263.4 | 276.2 | 205 | 326.9 | 251.5 | 342.9 | 348.2
3040.1 | 2801.1 | -6 | 0 | 0 | 254.1 | 224 | 210.6 | 203 | 242.1 | 38 | 18.6 | 64.1 | 4.4 | 248.8 | 10.3 | 56.8 | 49.6 | 31.2 | 57.2 | 47.4 | 43 | 65.2 | 156.7 | 76.3 | 67.6 | 56.9 | 55.4 | 304.6 | 253.7 | 302.4 | 66 | 244.1 | 61.7 | 72.4 | 68.1 | 263.3 | 276 | 205.1 | 326.8 | 251.4 | 342.8 | 348
3041.1 | 2802.1 | -5.9 | 0 | 0 | 254.2 | 223.8 | 210.4 | 203 | 242.1 | 38 | 18.6 | 64.1 | 4.6 | 247.1 | 10.6 | 56.9 | 49.1 | 31.3 | 57.2 | 47.4 | 43 | 65.3 | 156.7 | 76.6 | 67.4 | 57 | 55.4 | 304.3 | 253.8 | 302.3 | 65.9 | 244 | 62.3 | 72.4 | 68 | 263.2 | 275.9 | 205.1 | 326.6 | 251.3 | 342.6 | 347.9
3042.1 | 2803.1 | -5.9 | 0 | 0 | 254.3 | 223.4 | 210.4 | 202.9 | 242.1 | 38 | 18.6 | 64.1 | 4.6 | 258.1 | 10.2 | 56.9 | 49.2 | 31.3 | 57.3 | 47.5 | 43 | 65.3 | 157 | 76.5 | 67.5 | 57 | 55.3 | 304.2 | 253.4 | 302.1 | 66 | 243.8 | 62.8 | 72.4 | 68.1 | 263.1 | 275.7 | 205 | 326.4 | 251.2 | 342.4 | 347.7
3043.1 | 2804.1 | -5.9 | 0 | 0 | 254.3 | 223.2 | 210.3 | 202.9 | 242.1 | 37.9 | 18.6 | 64.1 | 4.9 | 261 | 10.4 | 56.9 | 49.1 | 31.2 | 57.3 | 47.5 | 43.1 | 65.3 | 156.6 | 75.9 | 67.6 | 57.1 | 55.3 | 304.2 | 253.3 | 302 | 65.9 | 243.8 | 63.2 | 72.4 | 68.3 | 263 | 275.4 | 204.9 | 326.2 | 251.1 | 342.2 | 347.5
3044.1 | 2805.1 | -6 | 0 | 0 | 254.3 | 223.3 | 210.3 | 202.7 | 242.1 | 37.9 | 18.6 | 64.1 | 5.2 | 255.8 | 10.8 | 56.9 | 49.9 | 31.3 | 57.3 | 47.5 | 43 | 65.3 | 156.8 | 75.5 | 67.6 | 57.2 | 55.4 | 304.5 | 252.5 | 301.9 | 66 | 243.7 | 62.9 | 72.5 | 68.4 | 262.9 | 275.1 | 204.8 | 326 | 251 | 342 | 347.4
3045.1 | 2806.1 | -6 | 0 | 0 | 254 | 223.5 | 210.1 | 202.5 | 242.1 | 37.9 | 18.6 | 64.1 | 5.7 | 257.7 | 12.1 | 57 | 50.2 | 31.3 | 57.4 | 47.5 | 43 | 65.3 | 156.5 | 75.3 | 67.5 | 57.3 | 55.5 | 304.6 | 252.2 | 301.8 | 66 | 243.3 | 62.5 | 72.6 | 68.4 | 262.8 | 275 | 204.8 | 325.9 | 250.9 | 341.8 | 347.2
3046.1 | 2807.1 | -6.2 | 0 | 0 | 253.7 | 223.7 | 210 | 202.4 | 241.9 | 37.8 | 18.6 | 64 | 6.4 | 249 | 11.5 | 57 | 49.6 | 31.1 | 57.4 | 47.5 | 43 | 65.4 | 156.6 | 75.2 | 67.1 | 57.4 | 55.4 | 304.8 | 251.9 | 301.7 | 66 | 243.5 | 63.1 | 72.5 | 68.3 | 262.7 | 274.7 | 204.8 | 325.7 | 250.8 | 341.6 | 347.1
3047.1 | 2808.1 | -6.2 | 0 | 0 | 253.6 | 223.7 | 209.8 | 202.4 | 241.7 | 37.8 | 18.6 | 64 | 5.9 | 255.1 | 11 | 57 | 49 | 31 | 57.4 | 47.5 | 43 | 65.5 | 156.7 | 74.6 | 67.1 | 57.4 | 55.5 | 304.9 | 252.8 | 301.5 | 65.9 | 243.5 | 63.1 | 72.3 | 68.3 | 262.6 | 274.6 | 204.8 | 325.5 | 250.6 | 341.4 | 346.9
3048.1 | 2809.1 | -6.4 | 0 | 0 | 253.5 | 223.5 | 209.3 | 202.3 | 241.5 | 37.8 | 18.6 | 64 | 4.4 | 244.1 | 10.5 | 57 | 49.3 | 31 | 57.5 | 47.5 | 43 | 65.6 | 156.6 | 74.4 | 67.5 | 57.5 | 55.6 | 305.1 | 254.4 | 301.4 | 65.9 | 243.4 | 62.6 | 72.2 | 68.2 | 262.5 | 274.5 | 204.7 | 325.3 | 250.5 | 341.2 | 346.7
3049.1 | 2810.1 | -6.5 | 0 | 0 | 253.3 | 223.3 | 208.9 | 202.1 | 241.4 | 37.8 | 18.7 | 64 | 3.9 | 246.1 | 12.7 | 57 | 49.8 | 31.1 | 57.5 | 47.5 | 43 | 65.7 | 156.6 | 74.6 | 67.5 | 57.6 | 55.5 | 305.3 | 254.5 | 301.3 | 65.9 | 243.2 | 61.8 | 72.1 | 68.1 | 262.4 | 274.3 | 204.6 | 325.2 | 250.4 | 341.1 | 346.6
3050.1 | 2811.1 | -6.4 | 0 | 0 | 253.3 | 223 | 208.7 | 201.9 | 241 | 37.8 | 18.7 | 63.9 | 4 | 244.2 | 13.9 | 57 | 50.2 | 31.1 | 57.5 | 47.6 | 42.9 | 65.8 | 157.1 | 74.8 | 67.6 | 57.7 | 55.5 | 305.5 | 253.7 | 301.2 | 65.9 | 243 | 61.3 | 72.1 | 68 | 262.2 | 274.1 | 204.5 | 325 | 250.3 | 340.9 | 346.4
3051.1 | 2812.1 | -6.4 | 0 | 0 | 253.2 | 223.2 | 208.7 | 201.8 | 240.5 | 37.8 | 18.7 | 63.8 | 3.4 | 258.4 | 15.3 | 57.1 | 50.3 | 31 | 57.5 | 47.6 | 42.9 | 65.8 | 157 | 74.8 | 67.7 | 57.7 | 55.4 | 305.6 | 254.3 | 301 | 65.9 | 243.1 | 61.4 | 72.2 | 68 | 262.1 | 273.8 | 204.3 | 324.8 | 250.2 | 340.7 | 346.2
3052.1 | 2813.1 | -6.4 | 0 | 0 | 253.2 | 223.1 | 208.6 | 201.8 | 240.3 | 37.8 | 18.7 | 63.8 | 4.4 | 264.8 | 15.6 | 57.1 | 50.3 | 30.9 | 57.6 | 47.6 | 42.9 | 65.9 | 156.9 | 74.7 | 67.7 | 57.8 | 55.5 | 305.6 | 254.4 | 300.9 | 65.8 | 243 | 62.7 | 72.1 | 68.3 | 262 | 273.6 | 204 | 324.6 | 250.1 | 340.5 | 346.1
3053.1 | 2814.1 | -6.4 | 0 | 0 | 253.1 | 222.5 | 208.4 | 201.7 | 240.2 | 37.8 | 18.7 | 63.7 | 4.8 | 247.8 | 14.5 | 57.1 | 50.7 | 30.9 | 57.6 | 47.6 | 42.9 | 66 | 157 | 74.9 | 67.7 | 57.9 | 55.3 | 305.6 | 255 | 300.8 | 65.8 | 242.9 | 63.6 | 71.9 | 68.1 | 261.9 | 273.3 | 203.8 | 324.4 | 249.9 | 340.3 | 345.9
3054.1 | 2815.1 | -6.3 | 0 | 0 | 252.8 | 222.1 | 208.1 | 201.6 | 239.9 | 37.8 | 18.7 | 63.7 | 5.4 | 241.2 | 13.5 | 57.1 | 50.8 | 30.9 | 57.6 | 47.6 | 42.9 | 66 | 157 | 75.1 | 67.7 | 57.9 | 55.3 | 305.5 | 254.7 | 300.7 | 65.8 | 242.9 | 64 | 71.9 | 67.9 | 261.8 | 273.2 | 203.8 | 324.3 | 249.8 | 340.1 | 345.8
3055.1 | 2816.1 | -6.1 | 0 | 0 | 252.7 | 222.4 | 208 | 201.5 | 239.6 | 37.7 | 18.7 | 63.6 | 5.7 | 243 | 12.3 | 57.1 | 51.2 | 31 | 57.6 | 47.6 | 42.9 | 66.1 | 157 | 75.2 | 67.8 | 58 | 55.1 | 305.4 | 254 | 300.5 | 65.8 | 242.7 | 63.9 | 71.7 | 68.1 | 261.7 | 273 | 203.7 | 324.1 | 249.7 | 339.9 | 345.6
3056.1 | 2817.1 | -6.1 | 0 | 0 | 252.5 | 222.6 | 208.1 | 201.2 | 239.4 | 37.7 | 18.7 | 63.7 | 4.4 | 248.3 | 11.3 | 57.2 | 51.1 | 31.1 | 57.7 | 47.7 | 42.9 | 66.2 | 156.8 | 75.4 | 67.8 | 58.1 | 55.1 | 305.5 | 252.8 | 300.4 | 65.8 | 242.5 | 63.9 | 71.6 | 68.2 | 261.6 | 272.8 | 203.5 | 323.9 | 249.6 | 339.7 | 345.4
3057.1 | 2818.1 | -6 | 0 | 0 | 252.1 | 222.7 | 208.3 | 201 | 239.4 | 37.7 | 18.7 | 63.7 | 4 | 243.1 | 11.8 | 57.2 | 50.9 | 31.1 | 57.7 | 47.7 | 42.9 | 66.3 | 156.9 | 75.5 | 67.8 | 58.2 | 55.2 | 305.7 | 252.9 | 300.3 | 65.8 | 242.4 | 63.9 | 71.8 | 68.2 | 261.5 | 272.6 | 203.4 | 323.7 | 249.5 | 339.6 | 345.3
3058.1 | 2819.1 | -6 | 0 | 0 | 251.6 | 222.7 | 208.2 | 200.9 | 239.4 | 37.6 | 18.7 | 63.8 | 3.9 | 240.9 | 12.9 | 57.2 | 50.6 | 31.1 | 57.7 | 47.7 | 42.9 | 66.3 | 157 | 75.6 | 67.9 | 58.2 | 55.2 | 305.8 | 253.3 | 300.2 | 65.8 | 242 | 64.7 | 71.6 | 68.2 | 261.4 | 272.5 | 203.4 | 323.5 | 249.4 | 339.4 | 345.1
3059.1 | 2820.1 | -6 | 0 | 0 | 251.3 | 222.6 | 208.1 | 200.7 | 239.5 | 37.6 | 18.7 | 63.8 | 4.8 | 238.7 | 14.6 | 57.2 | 50.2 | 31.1 | 57.7 | 47.7 | 42.9 | 66.4 | 156.9 | 75.4 | 67.9 | 58.3 | 55.3 | 305.9 | 253.9 | 300.1 | 65.8 | 241.9 | 64.1 | 71.3 | 68.3 | 261.3 | 272.2 | 203.3 | 323.4 | 249.3 | 339.2 | 344.9
3060.1 | 2821.1 | -6 | 0 | 0 | 251.1 | 222.3 | 208 | 200.5 | 239.4 | 37.5 | 18.7 | 63.8 | 4.4 | 246.7 | 16.2 | 57.3 | 49.8 | 31.1 | 57.8 | 47.7 | 42.9 | 66.4 | 157 | 75.3 | 68 | 58.4 | 55.4 | 306.1 | 254.1 | 299.9 | 65.8 | 241.9 | 63.2 | 71.2 | 68.3 | 261.2 | 272.1 | 203.2 | 323.2 | 249.2 | 339 | 344.8
3061.1 | 2822.1 | -6.1 | 0 | 0 | 251 | 222.1 | 207.8 | 200.2 | 239.3 | 37.5 | 18.7 | 63.8 | 5.2 | 248.6 | 15.7 | 57.3 | 49.7 | 31.1 | 57.8 | 47.7 | 43 | 66.5 | 157.3 | 75.2 | 67.8 | 58.4 | 55.4 | 306.2 | 253.8 | 299.8 | 65.8 | 241.8 | 62.8 | 71.4 | 68.3 | 261.1 | 271.9 | 203.1 | 323 | 249 | 338.8 | 344.6
3062.1 | 2823.1 | -6.1 | 0 | 0 | 251 | 222.1 | 207.8 | 200.1 | 239.1 | 37.5 | 18.7 | 63.8 | 5.8 | 255.9 | 15 | 57.3 | 50 | 31.1 | 57.8 | 47.7 | 43 | 66.5 | 157.1 | 74.7 | 67.9 | 58.5 | 55.4 | 306.3 | 253.7 | 299.7 | 65.9 | 241.7 | 62.2 | 71.7 | 68.4 | 261 | 271.6 | 202.9 | 322.8 | 248.9 | 338.6 | 344.5
3063.1 | 2824.1 | -6 | 0 | 0 | 250.8 | 221.9 | 207.8 | 200.1 | 238.9 | 37.5 | 18.7 | 63.7 | 6.4 | 258.4 | 14.3 | 57.3 | 50 | 30.9 | 57.9 | 47.8 | 43 | 66.5 | 157.1 | 75.1 | 67.9 | 58.6 | 55.3 | 306.5 | 253.1 | 299.6 | 65.8 | 241.2 | 62.5 | 71.7 | 68.2 | 260.9 | 271.5 | 202.8 | 322.6 | 248.8 | 338.4 | 344.3
3064.1 | 2825.1 | -6.1 | 0 | 0 | 250.6 | 221.8 | 207.7 | 200 | 238.9 | 37.5 | 18.7 | 63.7 | 6.2 | 273 | 15.4 | 57.4 | 50.3 | 30.8 | 57.9 | 47.8 | 43 | 66.6 | 157.3 | 75.2 | 67.8 | 58.6 | 55.3 | 306.6 | 252.9 | 299.5 | 65.8 | 241.3 | 62.8 | 71.3 | 68 | 260.8 | 271.5 | 202.7 | 322.4 | 248.7 | 338.2 | 344.1
3065.1 | 2826.1 | -6.3 | 0 | 0 | 250.4 | 221.9 | 207.4 | 200.1 | 238.8 | 37.5 | 18.7 | 63.6 | 5.4 | 259.7 | 15.8 | 57.4 | 50 | 30.8 | 57.9 | 47.8 | 43.1 | 66.6 | 157.2 | 75 | 67.7 | 58.7 | 55.3 | 306.4 | 253.4 | 299.4 | 65.8 | 241.1 | 63 | 71.2 | 68.2 | 260.7 | 271.5 | 202.7 | 322.2 | 248.5 | 338.1 | 344
3066.1 | 2827.1 | -6.4 | 0 | 0 | 250.2 | 221.9 | 207.2 | 200.1 | 238.7 | 37.5 | 18.7 | 63.6 | 6 | 266 | 13 | 57.4 | 49.4 | 30.7 | 57.9 | 47.8 | 43.1 | 66.6 | 157.2 | 74.8 | 67.5 | 58.8 | 55.3 | 306.2 | 253 | 299.2 | 65.8 | 241.1 | 62.6 | 71.4 | 68.1 | 260.6 | 271.5 | 202.5 | 322.1 | 248.4 | 337.9 | 343.8
3067.1 | 2828.1 | -6.4 | 0 | 0 | 250 | 221.8 | 207 | 200.1 | 238.4 | 37.5 | 18.7 | 63.5 | 5.9 | 262.7 | 12.1 | 57.4 | 48.8 | 30.8 | 57.9 | 47.8 | 43.1 | 66.7 | 157.4 | 75 | 67.5 | 58.8 | 55.3 | 306.1 | 253.2 | 299.1 | 65.8 | 241 | 63.6 | 71.7 | 68 | 260.5 | 271.4 | 202.4 | 321.9 | 248.3 | 337.7 | 343.7
3068.1 | 2829.1 | -6.4 | 0 | 0 | 249.7 | 221.8 | 207 | 199.9 | 238 | 37.4 | 18.7 | 63.5 | 5.1 | 254.7 | 13 | 57.4 | 48.7 | 30.9 | 58 | 47.8 | 43.1 | 66.7 | 157.4 | 75 | 67.6 | 58.9 | 55.4 | 305.8 | 253.4 | 299 | 65.8 | 240.9 | 63.8 | 71.8 | 68.2 | 260.4 | 271.2 | 202.4 | 321.7 | 248.2 | 337.5 | 343.5
3069.1 | 2830.1 | -6.4 | 0 | 0 | 249.7 | 221.8 | 206.9 | 199.7 | 238.2 | 37.4 | 18.7 | 63.5 | 5 | 239.7 | 12.8 | 57.5 | 49.1 | 31 | 58 | 47.9 | 43 | 66.7 | 157.4 | 74.9 | 67.6 | 59 | 55.3 | 305.8 | 252.9 | 298.9 | 65.7 | 241.1 | 64.1 | 71.8 | 68.2 | 260.3 | 271 | 202.2 | 321.5 | 248.1 | 337.3 | 343.3
3070.1 | 2831.1 | -6.4 | 0 | 0 | 249.5 | 221.6 | 206.7 | 199.6 | 238.2 | 37.4 | 18.7 | 63.4 | 4.7 | 259.3 | 12.2 | 57.5 | 48.9 | 31 | 58 | 47.9 | 43.1 | 66.7 | 157.4 | 74.1 | 67.6 | 59 | 55.4 | 305.8 | 251.7 | 298.7 | 65.8 | 240.9 | 63.3 | 71.7 | 68.1 | 260.2 | 270.8 | 202 | 321.4 | 248 | 337.2 | 343.2
3071.1 | 2832.1 | -6.3 | 0 | 0 | 249.3 | 221.3 | 206.6 | 199.4 | 238.2 | 37.3 | 18.7 | 63.4 | 4.7 | 251.6 | 12.4 | 57.5 | 48.2 | 31 | 58 | 47.9 | 43.1 | 66.8 | 157.4 | 73.7 | 67.8 | 59.1 | 55.4 | 305.9 | 250.7 | 298.6 | 65.8 | 240.8 | 62.9 | 71.9 | 67.7 | 260.1 | 270.5 | 201.9 | 321.2 | 247.9 | 337 | 343
3072.1 | 2833.1 | -6.2 | 0 | 0 | 249.1 | 221.1 | 206.4 | 199.2 | 237.8 | 37.3 | 18.7 | 63.3 | 5.5 | 242 | 11.4 | 57.5 | 47.6 | 31 | 58.1 | 47.9 | 43.1 | 66.8 | 157.8 | 73.3 | 67.8 | 59.2 | 55.5 | 306.2 | 252 | 298.5 | 65.8 | 240.8 | 63 | 72 | 67.8 | 260 | 270 | 201.7 | 321 | 247.7 | 336.8 | 342.9
3073.1 | 2834.1 | -6.3 | 0 | 0 | 248.7 | 221.1 | 206.2 | 198.9 | 237.5 | 37.3 | 18.7 | 63.2 | 4.7 | 265 | 9.7 | 57.5 | 48.2 | 31 | 58.1 | 47.9 | 43.1 | 66.8 | 157.9 | 73 | 67.9 | 59.2 | 55.5 | 306.4 | 253.1 | 298.4 | 65.8 | 240.7 | 63.4 | 71.9 | 68 | 259.8 | 269.8 | 201.5 | 320.9 | 247.6 | 336.6 | 342.7
3074.1 | 2835.1 | -6.2 | 0 | 0 | 248.2 | 221 | 206.2 | 198.6 | 237.5 | 37.2 | 18.7 | 63.1 | 4.4 | 265.2 | 11.2 | 57.6 | 48.9 | 31 | 58.1 | 47.9 | 43 | 66.8 | 157.9 | 73 | 67.8 | 59.3 | 55.4 | 306.4 | 253.2 | 298.3 | 65.8 | 240.8 | 62.8 | 71.8 | 67.9 | 259.7 | 269.7 | 201.4 | 320.7 | 247.5 | 336.4 | 342.5
3075.1 | 2836.1 | -6.2 | 0 | 0 | 247.9 | 220.8 | 206.2 | 198.5 | 237.4 | 37.2 | 18.8 | 63.1 | 3.8 | 263.6 | 13.5 | 57.6 | 48.9 | 31 | 58.1 | 47.9 | 43.1 | 66.8 | 157.8 | 72.6 | 67.7 | 59.3 | 55.3 | 306.3 | 253.7 | 298.1 | 65.7 | 240.8 | 62.2 | 71.6 | 67.9 | 259.6 | 269.5 | 201.1 | 320.5 | 247.4 | 336.2 | 342.4
3076.1 | 2837.1 | -6.3 | 0 | 0 | 247.7 | 220.5 | 206.1 | 198.5 | 236.9 | 37.2 | 18.8 | 63.1 | 3.8 | 264.4 | 14.3 | 57.6 | 48.4 | 31.1 | 58.1 | 48 | 43.1 | 66.9 | 158 | 72.2 | 67.7 | 59.4 | 55.3 | 306.3 | 252.6 | 298 | 65.6 | 240.6 | 62 | 71.2 | 68.1 | 259.5 | 269.4 | 201 | 320.3 | 247.3 | 336.1 | 342.2
3077.1 | 2838.1 | -6.1 | 0 | 0 | 247.9 | 220.4 | 205.8 | 198.5 | 236.6 | 37.1 | 18.8 | 63 | 4.2 | 262.6 | 14.4 | 57.6 | 47.8 | 31 | 58.2 | 48 | 43.2 | 66.9 | 157.8 | 72.1 | 67.8 | 59.5 | 55.3 | 306.4 | 250.3 | 297.9 | 65.6 | 240.4 | 62.9 | 70.9 | 68.2 | 259.4 | 269.2 | 201 | 320.1 | 247.2 | 335.9 | 342
3078.1 | 2839.1 | -6.1 | 0 | 0 | 247.8 | 220.3 | 205.6 | 198.5 | 236.2 | 37.1 | 18.8 | 63 | 4 | 264.8 | 14.9 | 57.6 | 48.3 | 31.1 | 58.2 | 48 | 43.2 | 66.9 | 157.9 | 72 | 67.9 | 59.5 | 55.3 | 306.3 | 251.3 | 297.8 | 65.6 | 240.1 | 63.7 | 70.7 | 68.3 | 259.3 | 269.1 | 200.9 | 320 | 247.1 | 335.7 | 341.9
3079.1 | 2840.1 | -6 | 0 | 0 | 247.7 | 220.2 | 205.6 | 198.3 | 236.3 | 37.1 | 18.8 | 62.9 | 4 | 259.9 | 14 | 57.7 | 48.7 | 31 | 58.2 | 48 | 43.3 | 66.9 | 158.1 | 72.1 | 68 | 59.6 | 55.3 | 306.2 | 251.9 | 297.6 | 65.6 | 240 | 63.8 | 70.6 | 68.2 | 259.2 | 268.9 | 200.7 | 319.8 | 247 | 335.5 | 341.7
3080.1 | 2841.1 | -6.1 | 0 | 0 | 247.6 | 220 | 205.8 | 198.2 | 236.5 | 37 | 18.8 | 62.9 | 3.8 | 269.7 | 12.7 | 57.7 | 49 | 30.9 | 58.2 | 48 | 43.3 | 66.9 | 158.3 | 72.3 | 68.1 | 59.7 | 55.3 | 306.1 | 252.1 | 297.5 | 65.7 | 240 | 64.2 | 70.5 | 68.1 | 259.1 | 268.7 | 200.6 | 319.6 | 246.9 | 335.3 | 341.6
3081.1 | 2842.1 | -6.1 | 0 | 0 | 247.3 | 220 | 205.9 | 198.1 | 236.6 | 37 | 18.8 | 62.9 | 4.1 | 257 | 12.3 | 57.7 | 49.4 | 30.8 | 58.3 | 48 | 43.2 | 66.9 | 157.9 | 72.6 | 68.2 | 59.7 | 55.3 | 306.1 | 250.8 | 297.4 | 65.7 | 239.7 | 63 | 70.6 | 68.2 | 259 | 268.5 | 200.5 | 319.5 | 246.8 | 335.2 | 341.4
3082.1 | 2843.1 | -6.1 | 0 | 0 | 247.1 | 219.9 | 205.8 | 198 | 236.7 | 37.1 | 18.8 | 62.9 | 3.4 | 262.5 | 12.2 | 57.7 | 49.7 | 30.7 | 58.3 | 48.1 | 43.2 | 67 | 157.6 | 72.8 | 68.3 | 59.8 | 55.3 | 306.1 | 248.9 | 297.3 | 65.7 | 239.3 | 62.4 | 70.7 | 68.3 | 258.9 | 268.3 | 200.3 | 319.3 | 246.7 | 335 | 341.3
3083.1 | 2844.1 | -6 | 0 | 0 | 246.9 | 219.7 | 205.6 | 197.9 | 236.7 | 37.1 | 18.8 | 62.9 | 3.9 | 252.9 | 11.6 | 57.8 | 49.6 | 30.7 | 58.3 | 48.1 | 43.2 | 67 | 157.7 | 72.9 | 68.2 | 59.8 | 55.3 | 306 | 249.6 | 297.2 | 65.7 | 239.3 | 63 | 71 | 68.3 | 258.8 | 268.1 | 200.2 | 319.1 | 246.6 | 334.8 | 341.1
3084.1 | 2845.1 | -5.9 | 0 | 0 | 246.7 | 219.5 | 205.4 | 197.7 | 236.7 | 37.1 | 18.8 | 62.9 | 4.2 | 261.3 | 11.3 | 57.8 | 50.3 | 30.6 | 58.3 | 48.1 | 43.1 | 66.9 | 157.9 | 73.1 | 68.2 | 59.9 | 55.4 | 305.9 | 250.5 | 297.1 | 65.8 | 239.1 | 63.3 | 71.2 | 68.2 | 258.7 | 267.9 | 200.2 | 318.9 | 246.4 | 334.6 | 340.9
3085.1 | 2846.1 | -5.8 | 0 | 0 | 246.6 | 219.5 | 205.3 | 197.7 | 236.7 | 37.1 | 18.8 | 62.9 | 4.2 | 270.7 | 12 | 57.8 | 50.8 | 30.3 | 58.3 | 48.1 | 43.1 | 66.9 | 158 | 73.2 | 68.3 | 60 | 55.5 | 305.9 | 250.8 | 296.9 | 65.8 | 239.1 | 62.6 | 71.5 | 68.2 | 258.6 | 267.7 | 200.1 | 318.8 | 246.3 | 334.4 | 340.8
3086.1 | 2847.1 | -5.9 | 0 | 0 | 246.4 | 219.4 | 205 | 197.8 | 236.7 | 37 | 18.8 | 62.9 | 4.5 | 260.4 | 13.2 | 57.8 | 50.1 | 30.4 | 58.4 | 48.1 | 43 | 67 | 157.5 | 73.3 | 68.3 | 60 | 55.4 | 305.8 | 250.8 | 296.8 | 65.7 | 239.2 | 62 | 71.4 | 68.3 | 258.5 | 267.5 | 200 | 318.6 | 246.2 | 334.3 | 340.6
3087.1 | 2848.1 | -6 | 0 | 0 | 246.2 | 219.1 | 204.8 | 197.8 | 236.7 | 37 | 18.8 | 62.8 | 4.4 | 269.2 | 14.3 | 57.9 | 50 | 30.6 | 58.4 | 48.1 | 43.1 | 67 | 157.4 | 73.2 | 68.3 | 60.1 | 55.4 | 305.8 | 251.3 | 296.7 | 65.7 | 239.2 | 61.7 | 71.2 | 68.3 | 258.4 | 267.4 | 200 | 318.4 | 246.1 | 334.1 | 340.5
3088.1 | 2849.1 | -6 | 0 | 0 | 246 | 218.9 | 204.5 | 197.7 | 236.8 | 36.9 | 18.8 | 62.8 | 4.6 | 261.2 | 14.3 | 57.9 | 50 | 30.6 | 58.4 | 48.1 | 43.1 | 67 | 157.4 | 72.7 | 68.4 | 60.1 | 55.4 | 305.8 | 251.6 | 296.6 | 65.6 | 239.1 | 62 | 71.1 | 68.3 | 258.3 | 267.2 | 199.9 | 318.2 | 246 | 333.9 | 340.3
3089.1 | 2850.1 | -6 | 0 | 0 | 245.8 | 218.7 | 204.1 | 197.6 | 236.5 | 36.8 | 18.8 | 62.8 | 5.9 | 255 | 11.9 | 57.9 | 49.9 | 30.6 | 58.4 | 48.1 | 43.1 | 67 | 157.7 | 72.5 | 68.4 | 60.2 | 55.3 | 305.8 | 251.3 | 296.5 | 65.8 | 239.1 | 62.5 | 70.9 | 68.3 | 258.2 | 267 | 199.9 | 318.1 | 245.9 | 333.7 | 340.2
3090.1 | 2851.1 | -6.1 | 0 | 0 | 245.5 | 218.6 | 203.9 | 197.4 | 236 | 36.7 | 18.8 | 62.8 | 5.2 | 262.4 | 12.3 | 57.9 | 50.1 | 30.7 | 58.5 | 48.1 | 43.1 | 67 | 157.4 | 72.4 | 68.5 | 60.3 | 55.3 | 305.8 | 250.9 | 296.4 | 66.2 | 239 | 64.2 | 71 | 68.3 | 258.1 | 266.8 | 199.9 | 317.9 | 245.8 | 333.6 | 340
3091.1 | 2852.1 | -6.1 | 0 | 0 | 245.4 | 218.5 | 203.6 | 197.1 | 235.6 | 36.7 | 18.8 | 62.8 | 4.7 | 256.3 | 15 | 57.9 | 50.2 | 30.7 | 58.5 | 48.2 | 43.1 | 67 | 156.9 | 72.2 | 68.6 | 60.3 | 55.3 | 305.8 | 250.7 | 296.2 | 66.7 | 238.7 | 62.8 | 71.4 | 68.2 | 258 | 266.7 | 199.7 | 317.7 | 245.7 | 333.4 | 339.8
3092.1 | 2853.1 | -6.2 | 0 | 0 | 245.4 | 218.3 | 203.6 | 197 | 235.1 | 36.7 | 18.8 | 62.8 | 4.1 | 257 | 14.9 | 58 | 50.2 | 30.6 | 58.5 | 48.2 | 43.1 | 67 | 156.4 | 72.2 | 68.5 | 60.4 | 55.4 | 305.7 | 250.5 | 296.1 | 69.1 | 238.5 | 63.1 | 71.8 | 68.4 | 257.9 | 266.5 | 199.6 | 317.6 | 245.6 | 333.2 | 339.7
3093.1 | 2854.1 | -6.3 | 0 | 0 | 245.5 | 218.2 | 203.7 | 197 | 234.9 | 36.7 | 18.8 | 62.7 | 4.4 | 261.1 | 14.3 | 58 | 50 | 30.6 | 58.5 | 48.2 | 43.1 | 67.1 | 156.1 | 72.2 | 68.3 | 60.4 | 55.5 | 305.7 | 250.6 | 296 | 69.4 | 238.3 | 64.3 | 72.2 | 68.6 | 257.9 | 266.3 | 199.6 | 317.4 | 245.5 | 333 | 339.5
3094.1 | 2855.1 | -6.3 | 0 | 0 | 245.4 | 218.1 | 203.5 | 197 | 234.7 | 36.7 | 18.8 | 62.7 | 5 | 251.6 | 12.5 | 58 | 49.5 | 30.6 | 58.6 | 48.2 | 43.1 | 67.1 | 155.8 | 72.2 | 68.5 | 60.5 | 55.5 | 305.8 | 250.4 | 295.9 | 74.2 | 238.3 | 64.6 | 72.8 | 68.6 | 257.8 | 266.1 | 199.5 | 317.3 | 245.3 | 332.8 | 339.4
3095.1 | 2856.1 | -6.4 | 0 | 0 | 245.3 | 217.8 | 203.3 | 197 | 234.5 | 36.8 | 18.8 | 62.6 | 4.1 | 246 | 11.5 | 58 | 49.6 | 30.7 | 58.6 | 48.2 | 43 | 67.1 | 155.7 | 72.5 | 68.3 | 60.6 | 55.5 | 305.7 | 249 | 295.8 | 74.2 | 238.2 | 64.4 | 73.5 | 68.6 | 257.7 | 265.8 | 199.3 | 317.1 | 245.2 | 332.7 | 339.2
3096.1 | 2857.1 | -6.3 | 0 | 0 | 245.3 | 217.6 | 203.2 | 196.9 | 234.3 | 36.8 | 18.8 | 62.5 | 4 | 273.7 | 10 | 58.1 | 50 | 30.7 | 58.6 | 48.2 | 43 | 67.2 | 155.4 | 72.9 | 68 | 60.6 | 55.7 | 305.6 | 247.4 | 295.7 | 74.2 | 238.1 | 63.8 | 73.8 | 68.5 | 257.6 | 265.6 | 199.2 | 316.9 | 245.1 | 332.5 | 339.1
3097.1 | 2858.1 | -6.3 | 0 | 0 | 245.1 | 217.4 | 203.2 | 196.7 | 234.3 | 36.9 | 18.8 | 62.6 | 5.4 | 249.3 | 9.6 | 58.1 | 50.1 | 30.7 | 58.6 | 48.2 | 43 | 67.2 | 155.3 | 73.2 | 68.2 | 60.7 | 55.6 | 305.6 | 246.3 | 295.5 | 74.2 | 238.2 | 64.1 | 76.4 | 68.4 | 257.4 | 265.4 | 199 | 316.8 | 245 | 332.3 | 338.9
3098.1 | 2859.1 | -6.1 | 0 | 0 | 244.9 | 217.2 | 203.3 | 196.6 | 233.9 | 36.9 | 18.8 | 62.5 | 5.2 | 245.7 | 9.3 | 58.1 | 50 | 30.8 | 58.6 | 48.3 | 43 | 67.2 | 155.1 | 73.2 | 68.2 | 60.7 | 55.6 | 305.7 | 247.3 | 295.4 | 79 | 237.9 | 64.3 | 81.7 | 68.7 | 257.4 | 265.3 | 199 | 316.6 | 244.9 | 332.1 | 338.8
3099.1 | 2860.1 | -6.1 | 0 | 0 | 244.8 | 216.9 | 203.2 | 196.4 | 233.9 | 36.8 | 18.8 | 62.6 | 4.2 | 255.5 | 10.7 | 58.1 | 50.2 | 30.8 | 58.6 | 48.3 | 43 | 67.2 | 154.9 | 73 | 68.2 | 60.8 | 55.6 | 305.7 | 248.2 | 295.3 | 79.7 | 237.9 | 63.7 | 82.4 | 68.8 | 257.3 | 265.2 | 198.9 | 316.4 | 244.8 | 332 | 338.6
3100.1 | 2861.1 | -6.2 | 0 | 0 | 244.6 | 216.8 | 203.1 | 196.2 | 233.9 | 36.7 | 18.8 | 62.6 | 5 | 249.5 | 11.1 | 58.1 | 50.2 | 30.7 | 58.7 | 48.3 | 43 | 67.2 | 153.8 | 73 | 68.4 | 60.9 | 55.5 | 305.8 | 249 | 295.2 | 80.7 | 237.9 | 62.5 | 84.2 | 69 | 257.2 | 265 | 198.8 | 316.3 | 244.7 | 331.8 | 338.5
3101.1 | 2862.1 | -6.2 | 0 | 0 | 244.5 | 216.9 | 203.1 | 196 | 233.4 | 36.6 | 18.9 | 62.5 | 4.6 | 245 | 9 | 58.2 | 49.8 | 30.7 | 58.7 | 48.3 | 43 | 67.3 | 151.4 | 72.5 | 68.4 | 60.9 | 55.5 | 305.9 | 252.2 | 295.1 | 80.9 | 237.6 | 64.8 | 85.1 | 68.8 | 257.1 | 264.9 | 198.7 | 316.1 | 244.6 | 331.6 | 338.3
3102.1 | 2863.1 | -6.3 | 0 | 0 | 244.4 | 217.1 | 203.2 | 195.9 | 232.5 | 36.6 | 18.8 | 62.5 | 4.1 | 231.6 | 8 | 58.2 | 49.2 | 30.7 | 58.7 | 48.3 | 43 | 67.3 | 151.5 | 72.6 | 68.3 | 61 | 55.5 | 306.1 | 251.4 | 295 | 81 | 236.2 | 65 | 85.8 | 68.9 | 257 | 264.8 | 198.5 | 316 | 244.5 | 331.4 | 338.1
3103.1 | 2864.1 | -6.3 | 0 | 0 | 244.3 | 217.3 | 203.2 | 195.8 | 232 | 36.6 | 18.9 | 62.5 | 5.1 | 250.7 | 8.2 | 58.2 | 48.7 | 30.8 | 58.7 | 48.3 | 43 | 67.3 | 152.1 | 72.8 | 68.3 | 61 | 55.6 | 306.1 | 250.6 | 294.9 | 81.6 | 235.8 | 64.3 | 85.4 | 68.6 | 256.9 | 264.6 | 198.4 | 315.8 | 244.4 | 331.3 | 338
3104.1 | 2865.1 | -6.2 | 0 | 0 | 244.1 | 217.4 | 203.1 | 195.6 | 231.6 | 36.6 | 18.9 | 62.5 | 6 | 257.6 | 9.2 | 58.2 | 48.6 | 30.9 | 58.7 | 48.3 | 43 | 67.3 | 152.2 | 73.1 | 68.6 | 61.1 | 55.5 | 306.1 | 250.4 | 294.8 | 80.9 | 235.8 | 65.1 | 84.7 | 68.2 | 256.8 | 264.4 | 198.3 | 315.6 | 244.3 | 331.1 | 337.8
3105.1 | 2866.1 | -6.2 | 0 | 0 | 244.1 | 217.3 | 203 | 195.5 | 231.2 | 36.6 | 18.9 | 62.5 | 5.9 | 240.4 | 8.4 | 58.2 | 48.6 | 31.1 | 58.8 | 48.3 | 42.9 | 67.4 | 152.2 | 73.3 | 68.7 | 61.1 | 55.3 | 306.1 | 250 | 294.7 | 80.5 | 234 | 65.5 | 85 | 68.3 | 256.7 | 264.2 | 198.2 | 315.5 | 244.2 | 330.9 | 337.7
3106.1 | 2867.1 | -6.2 | 0 | 0 | 243.9 | 217.2 | 202.8 | 195.5 | 230.5 | 36.7 | 18.9 | 62.4 | 5.5 | 232.7 | 8.1 | 58.3 | 48.3 | 31.2 | 58.8 | 48.4 | 42.9 | 67.4 | 152.3 | 73.4 | 68.8 | 61.2 | 55.2 | 306.1 | 249.6 | 294.5 | 82.5 | 232.8 | 65.9 | 86.7 | 68.4 | 256.6 | 264 | 198.1 | 315.3 | 244.1 | 330.7 | 337.5
3107.1 | 2868.1 | -6.2 | 0 | 0 | 243.7 | 217.3 | 202.4 | 195.4 | 230.4 | 36.7 | 18.9 | 62.4 | 5.3 | 257.6 | 8.3 | 58.3 | 47.9 | 31.3 | 58.8 | 48.4 | 42.9 | 67.5 | 152.2 | 73.3 | 68.7 | 61.2 | 55.2 | 306 | 249.2 | 294.4 | 81.7 | 233 | 66.8 | 86.4 | 68.4 | 256.5 | 263.8 | 198.2 | 315.1 | 244 | 330.6 | 337.4
3108.1 | 2869.1 | -6.2 | 0 | 0 | 243.4 | 217.4 | 202.2 | 195.3 | 230.3 | 36.7 | 18.9 | 62.4 | 5.4 | 227.9 | 10.2 | 58.3 | 48 | 31.2 | 58.8 | 48.4 | 42.8 | 67.5 | 151.9 | 73.2 | 68.7 | 61.3 | 55 | 306 | 247.9 | 294.3 | 81.6 | 233.4 | 67.6 | 86.2 | 68.7 | 256.4 | 263.7 | 198.3 | 315 | 243.9 | 330.4 | 337.2
3109.1 | 2870.1 | -6.3 | 0 | 0 | 243.2 | 217.5 | 202.3 | 195.2 | 230.3 | 36.7 | 18.9 | 62.4 | 4.9 | 233 | 9.2 | 58.3 | 48.7 | 31.3 | 58.8 | 48.4 | 42.8 | 67.5 | 151.7 | 72.9 | 68.8 | 61.3 | 55.1 | 306 | 247.3 | 294.2 | 81.1 | 233.6 | 66 | 85.8 | 68.9 | 256.3 | 263.6 | 198.3 | 314.8 | 243.7 | 330.2 | 337
3110.1 | 2871.1 | -6.2 | 0 | 0 | 243 | 217.5 | 202.2 | 195.3 | 230.1 | 36.6 | 18.9 | 62.3 | 4.9 | 233.2 | 8.4 | 58.3 | 48.7 | 31.2 | 58.9 | 48.4 | 42.8 | 67.5 | 151.8 | 72.5 | 68.7 | 61.4 | 55.1 | 306 | 246.7 | 294.1 | 80.2 | 233.6 | 65.3 | 85.3 | 68.8 | 256.2 | 263.5 | 198.2 | 314.7 | 243.6 | 330 | 336.9
3111.1 | 2872.1 | -6.2 | 0 | 0 | 242.9 | 217.4 | 201.9 | 195.5 | 229.3 | 36.6 | 18.9 | 62.2 | 4.4 | 230.6 | 8.1 | 58.4 | 49 | 31.1 | 58.9 | 48.4 | 42.8 | 67.6 | 151.6 | 72.2 | 68.7 | 61.4 | 55.2 | 306 | 246.4 | 294 | 79.2 | 233.9 | 66.4 | 84.9 | 68.7 | 256.1 | 263.4 | 198.2 | 314.5 | 243.5 | 329.9 | 336.7
3112.1 | 2873.1 | -6.2 | 0 | 0 | 242.9 | 217.4 | 201.6 | 195.5 | 228.7 | 36.6 | 18.9 | 62.2 | 5.2 | 255 | 8.2 | 58.4 | 49.3 | 31.1 | 58.9 | 48.4 | 42.8 | 67.6 | 151.8 | 72.1 | 68.9 | 61.5 | 55.2 | 305.9 | 245.7 | 293.9 | 78.5 | 234 | 67.4 | 84.4 | 68.5 | 256 | 263.3 | 198.3 | 314.4 | 243.4 | 329.7 | 336.6
3113.1 | 2874.1 | -6.2 | 0 | 0 | 242.9 | 217.1 | 201.6 | 195.4 | 228.7 | 36.6 | 18.9 | 62.1 | 5.2 | 231.8 | 10 | 58.4 | 49.7 | 31.1 | 58.9 | 48.4 | 42.8 | 67.7 | 151.8 | 71.4 | 68.8 | 61.5 | 55.4 | 305.9 | 244.8 | 293.8 | 78.7 | 234.1 | 67.5 | 84 | 68.4 | 255.9 | 263.2 | 198.3 | 314.2 | 243.3 | 329.5 | 336.4
3114.1 | 2875.1 | -6.1 | 0 | 0 | 242.8 | 216.7 | 201.7 | 195.2 | 229.2 | 36.6 | 18.9 | 62 | 5.2 | 238.8 | 11.8 | 58.4 | 49.9 | 31.1 | 58.9 | 48.5 | 42.8 | 67.7 | 151.7 | 71.3 | 68.7 | 61.6 | 55.6 | 305.8 | 245.9 | 293.7 | 77.9 | 234.3 | 66.7 | 83.6 | 68.6 | 255.9 | 263.2 | 198.2 | 314 | 243.2 | 329.4 | 336.3
3115.1 | 2876.1 | -6.1 | 0 | 0 | 242.5 | 216.6 | 201.9 | 195 | 229.8 | 36.6 | 18.9 | 62 | 3.6 | 239.9 | 13.4 | 58.4 | 49.9 | 30.9 | 58.9 | 48.5 | 42.9 | 67.8 | 151.9 | 71.8 | 68.8 | 61.7 | 55.6 | 305.7 | 246.4 | 293.6 | 77.4 | 234.3 | 65.2 | 83.3 | 68.8 | 255.8 | 263.1 | 198 | 313.9 | 243 | 329.2 | 336.1
3116.1 | 2877.1 | -6.1 | 0 | 0 | 242.3 | 216.6 | 202 | 194.9 | 230.1 | 36.6 | 18.9 | 62 | 3.2 | 253.3 | 12.4 | 58.5 | 50.1 | 30.8 | 59 | 48.5 | 42.9 | 67.8 | 152.1 | 72.1 | 68.9 | 61.7 | 55.5 | 305.7 | 246.9 | 293.5 | 76.8 | 234.3 | 64.9 | 82.8 | 68.9 | 255.7 | 263 | 197.9 | 313.7 | 242.9 | 329 | 335.9
3117.1 | 2878.1 | -6.3 | 0 | 0 | 242.2 | 216.4 | 202.1 | 194.7 | 230 | 36.6 | 18.9 | 62 | 3.6 | 244.7 | 11.9 | 58.5 | 49.7 | 30.7 | 59 | 48.5 | 43 | 67.9 | 152.2 | 72.1 | 68.9 | 61.8 | 55.5 | 305.8 | 247.9 | 293.3 | 77 | 234.3 | 64.6 | 82.4 | 68.9 | 255.6 | 262.8 | 197.8 | 313.6 | 242.9 | 328.8 | 335.8
3118.1 | 2879.1 | -6.3 | 0 | 0 | 242 | 216 | 201.8 | 194.4 | 229.9 | 36.5 | 18.9 | 62 | 4.2 | 254.6 | 12.7 | 58.5 | 49.2 | 30.7 | 59 | 48.5 | 43 | 67.9 | 151.7 | 72 | 68.8 | 61.8 | 55.4 | 305.8 | 249.3 | 293.2 | 76.5 | 234.6 | 64.1 | 82.1 | 68.8 | 255.5 | 262.7 | 197.7 | 313.4 | 242.8 | 328.7 | 335.6
3119.1 | 2880.1 | -6.2 | 0 | 0 | 241.9 | 215.6 | 201.7 | 194.2 | 230 | 36.5 | 18.9 | 61.9 | 4.9 | 262.5 | 12.2 | 58.5 | 49.3 | 30.7 | 59 | 48.5 | 43 | 67.9 | 151.4 | 71.9 | 68.9 | 61.9 | 55.3 | 305.7 | 246.9 | 293.1 | 76.1 | 234.5 | 63.4 | 81.8 | 68.7 | 255.4 | 262.5 | 197.7 | 313.2 | 242.7 | 328.5 | 335.5
3120.1 | 2881.1 | -6.2 | 0 | 0 | 242.1 | 215.5 | 201.8 | 194 | 230 | 36.6 | 18.9 | 61.8 | 5.1 | 273.7 | 12.2 | 58.6 | 49.7 | 30.7 | 59 | 48.5 | 43 | 67.9 | 151.8 | 71.4 | 68.9 | 61.9 | 55.4 | 305.6 | 245.8 | 293 | 75.8 | 234.6 | 63 | 81.5 | 68.8 | 255.3 | 262.4 | 197.7 | 313.1 | 242.6 | 328.4 | 335.3
3121.1 | 2882.1 | -6.1 | 0 | 0 | 242.2 | 215.7 | 201.7 | 193.8 | 230 | 36.6 | 18.9 | 61.8 | 4.9 | 262.9 | 13.7 | 58.6 | 50.2 | 30.8 | 59 | 48.5 | 43 | 67.9 | 151.6 | 70.9 | 69.2 | 62 | 55.4 | 305.5 | 245.8 | 292.9 | 75.4 | 234.7 | 62.4 | 81.2 | 68.8 | 255.2 | 262.3 | 197.7 | 312.9 | 242.5 | 328.2 | 335.2
3122.1 | 2883.1 | -6 | 0 | 0 | 242.2 | 215.9 | 201.6 | 193.7 | 229.3 | 36.6 | 18.9 | 61.8 | 4.4 | 254.4 | 15.8 | 58.6 | 49.8 | 30.8 | 59.1 | 48.5 | 43 | 67.9 | 151.4 | 70.4 | 69 | 62.1 | 55.4 | 305.5 | 246.2 | 292.8 | 75.1 | 234.6 | 62.4 | 81 | 68.9 | 255.1 | 262.2 | 197.7 | 312.8 | 242.4 | 328 | 335
3123.1 | 2884.1 | -6.1 | 0 | 0 | 242.1 | 215.9 | 201.6 | 193.7 | 229.2 | 36.5 | 18.9 | 61.8 | 4.1 | 248.7 | 15.1 | 58.6 | 50.4 | 30.8 | 59.1 | 48.5 | 43 | 68 | 151.5 | 70.5 | 69 | 62.1 | 55.5 | 305.5 | 247.2 | 292.7 | 75 | 234.8 | 62.7 | 80.8 | 68.6 | 255 | 262.1 | 197.8 | 312.6 | 242.3 | 327.8 | 334.9
3124.1 | 2885.1 | -6.2 | 0 | 0 | 241.6 | 215.5 | 201.6 | 193.6 | 229.3 | 36.4 | 18.9 | 61.7 | 4.7 | 252.4 | 13.4 | 58.6 | 50.2 | 30.8 | 59.1 | 48.5 | 43 | 68 | 151.5 | 70.6 | 69.1 | 62.2 | 55.4 | 305.5 | 248.3 | 292.5 | 74.7 | 234.9 | 62 | 80.5 | 68.2 | 254.9 | 262 | 197.7 | 312.5 | 242.2 | 327.7 | 334.7
3125.1 | 2886.1 | -6.2 | 0 | 0 | 241.4 | 215 | 201.5 | 193.6 | 229.3 | 36.3 | 18.9 | 61.7 | 5.3 | 262 | 12.9 | 58.7 | 50.1 | 30.9 | 59.1 | 48.5 | 43 | 68 | 151.4 | 70.5 | 69.1 | 62.2 | 55.3 | 305.5 | 246.8 | 292.4 | 74.4 | 234.8 | 61.9 | 80.1 | 68.1 | 254.8 | 261.9 | 197.7 | 312.3 | 242.1 | 327.5 | 334.6
3126.1 | 2887.1 | -6.2 | 0 | 0 | 241.3 | 214.8 | 201.5 | 193.6 | 229.2 | 36.3 | 18.9 | 61.7 | 5.2 | 251.3 | 13.2 | 58.7 | 50.7 | 30.9 | 59.1 | 48.5 | 42.9 | 68 | 151.5 | 70.1 | 68.9 | 62.3 | 55.4 | 305.5 | 246.6 | 292.3 | 74.3 | 234.9 | 62.3 | 79.8 | 68.3 | 254.7 | 261.8 | 197.6 | 312.1 | 242 | 327.4 | 334.4
3127.1 | 2888.1 | -6.1 | 0 | 0 | 241.4 | 215 | 201.5 | 193.5 | 229.2 | 36.3 | 18.9 | 61.6 | 4.1 | 269.1 | 13.4 | 58.7 | 51.1 | 30.9 | 59.1 | 48.6 | 42.9 | 68 | 151.6 | 70.1 | 69 | 62.4 | 55.4 | 305.6 | 246.5 | 292.2 | 74.2 | 234.7 | 63.3 | 79.7 | 68.5 | 254.7 | 261.6 | 197.5 | 312 | 241.9 | 327.2 | 334.2
3128.1 | 2889.1 | -6.2 | 0 | 0 | 241.3 | 215.1 | 201.2 | 193.3 | 229.1 | 36.3 | 18.9 | 61.6 | 4 | 248.3 | 15.1 | 58.7 | 50.8 | 30.9 | 59.2 | 48.6 | 42.9 | 68.1 | 151.7 | 70 | 69 | 62.4 | 55.3 | 305.7 | 246.8 | 292.1 | 74 | 234.6 | 63.3 | 79.5 | 68.5 | 254.6 | 261.5 | 197.3 | 311.8 | 241.8 | 327 | 334.1
3129.1 | 2890.1 | -6.2 | 0 | 0 | 241.2 | 215.2 | 201 | 193.2 | 228.9 | 36.3 | 18.9 | 61.5 | 5.1 | 244.8 | 17.5 | 58.7 | 49.8 | 31 | 59.2 | 48.6 | 42.9 | 68.1 | 151.5 | 69.7 | 69 | 62.5 | 55.3 | 305.7 | 247.2 | 292 | 73.8 | 234.4 | 62.8 | 79.3 | 68.4 | 254.5 | 261.4 | 197.1 | 311.7 | 241.7 | 326.8 | 333.9
3130.1 | 2891.1 | -6.2 | 0 | 0 | 241.1 | 215.4 | 201 | 193 | 229.1 | 36.3 | 18.9 | 61.5 | 5 | 261.7 | 16.8 | 58.7 | 49.5 | 31.1 | 59.2 | 48.6 | 42.9 | 68.1 | 151.3 | 69.9 | 69 | 62.5 | 55.4 | 305.8 | 246.9 | 291.9 | 73.7 | 234.5 | 62.2 | 79.3 | 68.4 | 254.4 | 261.2 | 197 | 311.5 | 241.6 | 326.7 | 333.8
3131.1 | 2892.1 | -6.3 | 0 | 0 | 241.1 | 215.5 | 201.1 | 192.8 | 229.3 | 36.3 | 18.9 | 61.5 | 5.1 | 250.9 | 15.6 | 58.8 | 49.6 | 31 | 59.2 | 48.6 | 42.8 | 68.1 | 151.6 | 70.2 | 69 | 62.6 | 55.4 | 305.9 | 247.5 | 291.8 | 73.7 | 234.6 | 61.7 | 79.2 | 68.5 | 254.3 | 261 | 196.8 | 311.4 | 241.5 | 326.5 | 333.6
3132.1 | 2893.1 | -6.3 | 0 | 0 | 241 | 215.6 | 200.8 | 192.7 | 229.4 | 36.3 | 18.9 | 61.5 | 5.1 | 250.2 | 17 | 58.8 | 49.8 | 31.1 | 59.2 | 48.6 | 42.8 | 68.1 | 151.6 | 70.3 | 68.7 | 62.6 | 55.4 | 305.9 | 247.6 | 291.7 | 73.5 | 234.8 | 61.6 | 79.2 | 68.6 | 254.2 | 260.7 | 196.7 | 311.2 | 241.4 | 326.3 | 333.5
3133.1 | 2894.1 | -6.3 | 0 | 0 | 241 | 215.6 | 200.6 | 192.5 | 229.6 | 36.3 | 18.9 | 61.4 | 6.1 | 253.9 | 17.4 | 58.8 | 49.9 | 31.1 | 59.3 | 48.6 | 42.9 | 68.2 | 151.4 | 70.5 | 68.5 | 62.7 | 55.5 | 305.8 | 248.6 | 291.6 | 73.1 | 234.8 | 61.4 | 79 | 68.1 | 254.1 | 260.5 | 196.7 | 311.1 | 241.3 | 326.2 | 333.3
3134.1 | 2895.1 | -6.3 | 0 | 0 | 240.9 | 215.5 | 200.4 | 192.4 | 229.4 | 36.3 | 19 | 61.4 | 5 | 261.7 | 19.7 | 58.8 | 50.4 | 31.1 | 59.3 | 48.6 | 42.9 | 68.2 | 151 | 70.8 | 68.7 | 62.8 | 55.5 | 305.7 | 246.2 | 291.4 | 72.9 | 234.7 | 61.1 | 78.9 | 68.2 | 254 | 260.3 | 196.5 | 310.9 | 241.2 | 326 | 333.2
3135.1 | 2896.1 | -6.5 | 0 | 0 | 240.7 | 215.3 | 200.3 | 192.2 | 229.2 | 36.3 | 19 | 61.4 | 5.6 | 269.3 | 21.4 | 58.8 | 50.1 | 31.2 | 59.3 | 48.6 | 42.9 | 68.2 | 150.7 | 71 | 68.7 | 62.8 | 55.5 | 305.8 | 246.4 | 291.3 | 72.8 | 234.3 | 61 | 78.8 | 68 | 253.9 | 260.1 | 196.4 | 310.7 | 241 | 325.9 | 333
3136.1 | 2897.1 | -6.5 | 0 | 0 | 240.5 | 214.9 | 200.3 | 192 | 228.7 | 36.3 | 19 | 61.4 | 6.1 | 257.9 | 22.7 | 58.8 | 50.1 | 31.3 | 59.3 | 48.7 | 42.8 | 68.2 | 150.6 | 71 | 68.8 | 62.9 | 55.7 | 305.8 | 247 | 291.2 | 72.8 | 233.9 | 60.8 | 78.6 | 68.1 | 253.8 | 259.9 | 196.2 | 310.6 | 240.9 | 325.7 | 332.9
3137.1 | 2898.1 | -6.4 | 0 | 0 | 240.2 | 214.7 | 200 | 192 | 228.2 | 36.3 | 19 | 61.4 | 7.3 | 257 | 22.6 | 58.9 | 49.3 | 31.3 | 59.3 | 48.7 | 42.8 | 68.2 | 150.4 | 71 | 68.9 | 62.9 | 55.6 | 305.8 | 246.7 | 291.1 | 72.8 | 233.4 | 60.9 | 78.5 | 68.1 | 253.7 | 259.7 | 196.1 | 310.4 | 240.8 | 325.5 | 332.7
3138.1 | 2899.1 | -6.5 | 0 | 0 | 240.2 | 214.6 | 200 | 191.9 | 227.8 | 36.3 | 19 | 61.3 | 5.8 | 256.1 | 20.9 | 58.9 | 48.7 | 31.3 | 59.3 | 48.7 | 42.8 | 68.3 | 150.3 | 71 | 68.8 | 63 | 55.4 | 305.8 | 247.2 | 291 | 72.7 | 233.5 | 60.9 | 78.4 | 68.1 | 253.6 | 259.6 | 196.1 | 310.3 | 240.7 | 325.4 | 332.6
3139.1 | 2900.1 | -6.5 | 0 | 0 | 240 | 214.7 | 199.9 | 191.9 | 227.6 | 36.3 | 19 | 61.2 | 5.7 | 250 | 19.7 | 58.9 | 49 | 31.2 | 59.3 | 48.7 | 42.8 | 68.3 | 150.3 | 70.7 | 68.7 | 63 | 55.4 | 305.8 | 247.6 | 290.9 | 72.6 | 233.5 | 61.1 | 78.3 | 67.9 | 253.5 | 259.5 | 196.1 | 310.1 | 240.6 | 325.2 | 332.4
3140.1 | 2901.1 | -6.4 | 0 | 0 | 239.8 | 214.8 | 199.5 | 191.9 | 227.6 | 36.2 | 19 | 61.2 | 5.7 | 237.9 | 17.4 | 58.9 | 48.9 | 31.2 | 59.4 | 48.7 | 42.8 | 68.3 | 150.2 | 70.4 | 68.9 | 63.1 | 55.4 | 305.8 | 247.3 | 290.8 | 72.3 | 233.5 | 61.4 | 78.1 | 67.8 | 253.4 | 259.4 | 196 | 309.9 | 240.5 | 325 | 332.3
3141.1 | 2902.1 | -6.4 | 0 | 0 | 239.7 | 214.8 | 199.5 | 191.7 | 227.6 | 36.2 | 19 | 61.2 | 4.1 | 243.8 | 15.7 | 58.9 | 48.7 | 31.4 | 59.4 | 48.7 | 42.8 | 68.3 | 149.8 | 70.4 | 68.9 | 63.1 | 55.4 | 305.8 | 247.4 | 290.7 | 72.2 | 233.5 | 62.5 | 78 | 68.1 | 253.4 | 259.4 | 196 | 309.8 | 240.4 | 324.9 | 332.1
3142.1 | 2903.1 | -6.5 | 0 | 0 | 239.7 | 214.7 | 199.5 | 191.7 | 227.2 | 36.2 | 19 | 61.2 | 4.6 | 233.5 | 15.7 | 58.9 | 49.1 | 31.4 | 59.4 | 48.7 | 42.8 | 68.3 | 149.8 | 70.3 | 68.9 | 63.2 | 55.4 | 305.8 | 247.3 | 290.6 | 72 | 233.4 | 62.7 | 77.9 | 68.4 | 253.3 | 259.3 | 195.9 | 309.6 | 240.3 | 324.7 | 332
3143.1 | 2904.1 | -6.4 | 0 | 0 | 239.7 | 214.7 | 199.5 | 191.6 | 226.9 | 36.1 | 19 | 61.2 | 5.3 | 239.4 | 14 | 58.9 | 48.9 | 31.4 | 59.4 | 48.7 | 42.7 | 68.3 | 149.6 | 70.4 | 68.9 | 63.2 | 55.6 | 305.7 | 247.4 | 290.4 | 72 | 233.1 | 62.8 | 77.7 | 68.4 | 253.2 | 259.2 | 195.8 | 309.5 | 240.2 | 324.6 | 331.8
3144.1 | 2905.1 | -6.3 | 0 | 0 | 239.7 | 214.5 | 199.3 | 191.6 | 227 | 36.1 | 19 | 61.2 | 4.9 | 240.8 | 12 | 59 | 48.6 | 31.4 | 59.4 | 48.7 | 42.7 | 68.4 | 150.1 | 70.8 | 68.9 | 63.3 | 55.7 | 305.5 | 247.4 | 290.3 | 71.8 | 232.8 | 63.2 | 77.5 | 68.3 | 253.1 | 259.1 | 195.7 | 309.3 | 240.1 | 324.4 | 331.7
3145.1 | 2906.1 | -6.2 | 0 | 0 | 239.4 | 214.4 | 199.3 | 191.6 | 227.1 | 36.1 | 19 | 61.1 | 4.5 | 255.9 | 12 | 59 | 48.2 | 31.2 | 59.4 | 48.7 | 42.7 | 68.4 | 150.3 | 71 | 68.9 | 63.3 | 55.6 | 305.5 | 247.2 | 290.2 | 71.7 | 232.8 | 62.8 | 77.4 | 68.4 | 253 | 259 | 195.6 | 309.1 | 240 | 324.2 | 331.5
3146.1 | 2907.1 | -6.2 | 0 | 0 | 239 | 214.4 | 199.4 | 191.6 | 227.1 | 36.1 | 19 | 61.1 | 4.1 | 259.5 | 14.3 | 59 | 47.7 | 31.1 | 59.4 | 48.8 | 42.7 | 68.4 | 150.3 | 70.7 | 68.9 | 63.4 | 55.5 | 305.4 | 245.9 | 290.1 | 71.6 | 232.6 | 62.3 | 77.3 | 68.1 | 252.9 | 258.8 | 195.7 | 309 | 239.9 | 324.1 | 331.4
3147.1 | 2908.1 | -6.1 | 0 | 0 | 238.8 | 214.2 | 199.4 | 191.5 | 227.1 | 36.1 | 19 | 61.1 | 4.2 | 266.2 | 14.1 | 59 | 47 | 31.2 | 59.4 | 48.8 | 42.6 | 68.4 | 150.5 | 70.4 | 68.9 | 63.4 | 55.5 | 305.4 | 244.8 | 290 | 71.6 | 232.2 | 62.9 | 77.2 | 68.3 | 252.8 | 258.7 | 195.6 | 308.8 | 239.8 | 323.9 | 331.2
3148.1 | 2909.1 | -6.1 | 0 | 0 | 238.7 | 214 | 199.2 | 191.6 | 227.3 | 36.1 | 19 | 61 | 3.9 | 258.9 | 13.9 | 59 | 47.7 | 31.1 | 59.5 | 48.8 | 42.5 | 68.4 | 150.8 | 70.1 | 69 | 63.5 | 55.5 | 305.3 | 243 | 289.9 | 71.4 | 231.8 | 63.4 | 77.1 | 68.3 | 252.7 | 258.5 | 195.5 | 308.7 | 239.7 | 323.7 | 331.1
3149.1 | 2910.1 | -6.2 | 0 | 0 | 238.5 | 213.9 | 199.1 | 191.6 | 227.3 | 35.9 | 19 | 61 | 3.7 | 245.9 | 13.2 | 59 | 48.1 | 31 | 59.5 | 48.8 | 42.5 | 68.4 | 150.7 | 69.6 | 69 | 63.5 | 55.6 | 305.2 | 242.3 | 289.8 | 71.4 | 231.5 | 63.5 | 77.1 | 68.3 | 252.6 | 258.4 | 195.4 | 308.5 | 239.6 | 323.6 | 330.9
3150.1 | 2911.1 | -6.2 | 0 | 0 | 238.3 | 213.7 | 198.9 | 191.4 | 227.3 | 35.9 | 19 | 60.9 | 3.5 | 248.7 | 10 | 59.1 | 48.2 | 30.9 | 59.5 | 48.8 | 42.5 | 68.4 | 150.4 | 69.8 | 69.2 | 63.6 | 55.5 | 305.2 | 242.7 | 289.7 | 71.4 | 231.5 | 63.1 | 77.1 | 68 | 252.5 | 258.2 | 195.3 | 308.4 | 239.5 | 323.4 | 330.8
3151.1 | 2912.1 | -6.2 | 0 | 0 | 238 | 213.5 | 198.9 | 191.3 | 227.1 | 35.8 | 19 | 60.8 | 4.4 | 259.8 | 8.2 | 59.1 | 48.5 | 30.8 | 59.5 | 48.8 | 42.4 | 68.5 | 150.2 | 69.9 | 69.2 | 63.6 | 55.4 | 305.1 | 244.5 | 289.6 | 71.4 | 231.4 | 63.6 | 77.1 | 67.9 | 252.4 | 258.1 | 195.2 | 308.2 | 239.4 | 323.3 | 330.6
3152.1 | 2913.1 | -6.1 | 0 | 0 | 237.9 | 213.3 | 198.9 | 191.2 | 226.8 | 35.8 | 19 | 60.8 | 5.1 | 234.2 | 8.9 | 59.1 | 48.8 | 30.8 | 59.5 | 48.8 | 42.4 | 68.5 | 150.5 | 70 | 69 | 63.7 | 55.4 | 305.1 | 244.1 | 289.5 | 71.3 | 231.2 | 63.8 | 77.1 | 67.9 | 252.3 | 257.9 | 195.1 | 308 | 239.3 | 323.1 | 330.5
3153.1 | 2914.1 | -6 | 0 | 0 | 237.7 | 213.3 | 198.9 | 191.1 | 226 | 35.7 | 19 | 60.7 | 5.4 | 249.1 | 8.3 | 59.1 | 48.5 | 30.5 | 59.5 | 48.8 | 42.4 | 68.5 | 150.7 | 70.2 | 69 | 63.7 | 55.3 | 305.1 | 243.8 | 289.4 | 71.4 | 231.2 | 62.7 | 77.2 | 68 | 252.2 | 257.7 | 194.9 | 307.9 | 239.2 | 322.9 | 330.3
3154.1 | 2915.1 | -6 | 0 | 0 | 237.6 | 213.4 | 198.8 | 191.1 | 225.6 | 35.7 | 19 | 60.7 | 6.2 | 245.9 | 7.4 | 59.1 | 48.2 | 30.5 | 59.5 | 48.9 | 42.4 | 68.5 | 150.6 | 70.3 | 69 | 63.7 | 55.2 | 305.1 | 244.2 | 289.3 | 71.4 | 231.2 | 62.2 | 77.4 | 68.2 | 252.1 | 257.5 | 194.7 | 307.7 | 239.1 | 322.8 | 330.2
3155.1 | 2916.1 | -6 | 0 | 0 | 237.6 | 213.6 | 198.4 | 190.9 | 225.8 | 35.6 | 19 | 60.6 | 6.2 | 244.9 | 7.6 | 59.1 | 48.6 | 30.5 | 59.6 | 48.9 | 42.4 | 68.6 | 150.5 | 70.4 | 68.9 | 63.8 | 55.2 | 305.1 | 243.8 | 289.2 | 71.3 | 231.3 | 61.7 | 77.5 | 68.1 | 252.1 | 257.3 | 194.6 | 307.6 | 238.9 | 322.6 | 330
3156.1 | 2917.1 | -6 | 0 | 0 | 237.7 | 213.4 | 198.2 | 190.7 | 226 | 35.6 | 19 | 60.5 | 5.5 | 260.1 | 10.1 | 59.2 | 48.8 | 30.6 | 59.6 | 48.9 | 42.4 | 68.6 | 150.4 | 70.4 | 68.9 | 63.8 | 55.2 | 305.1 | 243.5 | 289 | 71.2 | 231.3 | 61.4 | 77.5 | 68.2 | 252 | 257.1 | 194.5 | 307.4 | 238.8 | 322.4 | 329.9
3157.1 | 2918.1 | -6 | 0 | 0 | 237.6 | 213.3 | 198.1 | 190.6 | 225.7 | 35.6 | 19 | 60.4 | 5.9 | 257.2 | 12.9 | 59.2 | 49.3 | 30.6 | 59.6 | 48.9 | 42.4 | 68.6 | 150.5 | 70.5 | 68.8 | 63.9 | 55.2 | 305.1 | 244 | 288.9 | 71.2 | 231.1 | 61.5 | 77.6 | 68.4 | 251.9 | 256.9 | 194.4 | 307.3 | 238.7 | 322.3 | 329.7
3158.1 | 2919.1 | -6.3 | 0 | 0 | 237.4 | 213 | 198 | 190.5 | 225.7 | 35.6 | 19 | 60.3 | 6.4 | 248.8 | 13.1 | 59.2 | 49.5 | 30.6 | 59.6 | 48.9 | 42.4 | 68.6 | 150.5 | 70.4 | 68.8 | 63.9 | 55.2 | 305.1 | 244.8 | 288.8 | 71.3 | 230.8 | 62.3 | 77.7 | 68.4 | 251.8 | 256.8 | 194.4 | 307.1 | 238.6 | 322.1 | 329.6
3159.1 | 2920.1 | -6.5 | 0 | 0 | 237.4 | 213 | 197.9 | 190.4 | 225.7 | 35.6 | 19.1 | 60.3 | 5.7 | 238.6 | 12.8 | 59.2 | 49.6 | 30.6 | 59.6 | 48.9 | 42.4 | 68.6 | 150.6 | 70.3 | 68.9 | 64 | 55.3 | 305.2 | 245.3 | 288.7 | 71.4 | 230.5 | 62.3 | 77.8 | 68.2 | 251.7 | 256.7 | 194.4 | 307 | 238.5 | 322 | 329.4
3160.1 | 2921.1 | -6.6 | 0 | 0 | 237.3 | 213 | 197.9 | 190.3 | 225.8 | 35.6 | 19.1 | 60.2 | 6.1 | 240.2 | 14.9 | 59.2 | 50.1 | 30.6 | 59.6 | 48.9 | 42.4 | 68.6 | 150.8 | 70.4 | 69 | 64 | 55.4 | 305.2 | 245.3 | 288.6 | 71.2 | 230.1 | 62.3 | 77.9 | 67.9 | 251.6 | 256.5 | 194.3 | 306.8 | 238.4 | 321.8 | 329.3
3161.1 | 2922.1 | -6.6 | 0 | 0 | 237.1 | 213 | 197.8 | 190.1 | 225.9 | 35.6 | 19.1 | 60.2 | 6.4 | 231.7 | 16 | 59.2 | 50.3 | 30.6 | 59.6 | 48.9 | 42.3 | 68.6 | 150.8 | 70.6 | 68.9 | 64.1 | 55.3 | 305.3 | 245 | 288.5 | 71.1 | 229.9 | 61.7 | 77.8 | 68 | 251.5 | 256.4 | 194.2 | 306.7 | 238.3 | 321.7 | 329.1
3162.1 | 2923.1 | -6.6 | 0 | 0 | 236.9 | 212.9 | 197.7 | 189.9 | 226 | 35.6 | 19.1 | 60.2 | 6.4 | 242.8 | 12.2 | 59.3 | 50 | 30.8 | 59.7 | 48.9 | 42.2 | 68.6 | 151 | 70.7 | 68.9 | 64.1 | 55.4 | 305.2 | 243.5 | 288.4 | 71 | 229.8 | 61.4 | 77.8 | 68 | 251.4 | 256.4 | 194.1 | 306.5 | 238.2 | 321.5 | 329
3163.1 | 2924.1 | -6.5 | 0 | 0 | 236.7 | 212.7 | 197.6 | 189.8 | 226.1 | 35.6 | 19.1 | 60.2 | 6.5 | 224.1 | 9 | 59.3 | 50 | 30.9 | 59.7 | 48.9 | 42.2 | 68.6 | 151 | 70.4 | 69 | 64.2 | 55.3 | 305.3 | 243.1 | 288.3 | 71.1 | 229.8 | 61.6 | 78 | 68.2 | 251.3 | 256.2 | 194 | 306.4 | 238.1 | 321.3 | 328.9
3164.1 | 2925.1 | -6.5 | 0 | 0 | 236.3 | 212.6 | 197.5 | 189.7 | 226.2 | 35.6 | 19.1 | 60.1 | 6.8 | 254.4 | 8.8 | 59.3 | 50 | 30.9 | 59.7 | 48.9 | 42.2 | 68.7 | 151.2 | 69.6 | 68.9 | 64.2 | 55.3 | 305.3 | 243.3 | 288.2 | 71 | 229.9 | 61 | 78.1 | 68.1 | 251.2 | 256.1 | 193.9 | 306.2 | 238 | 321.2 | 328.7
3165.1 | 2926.1 | -6.5 | 0 | 0 | 235.8 | 212.6 | 197.3 | 189.6 | 226.1 | 35.6 | 19.1 | 60.1 | 6.2 | 231.9 | 8.8 | 59.3 | 49.8 | 30.8 | 59.7 | 48.9 | 42.2 | 68.7 | 151.3 | 69.5 | 68.9 | 64.2 | 55.3 | 305.3 | 243.6 | 288.1 | 70.8 | 229.8 | 60.7 | 78.2 | 67.9 | 251.1 | 255.9 | 193.8 | 306 | 237.9 | 321 | 328.5
3166.1 | 2927.1 | -6.5 | 0 | 0 | 235.4 | 212.6 | 197.2 | 189.5 | 226 | 35.6 | 19.1 | 60.1 | 4.2 | 239.8 | 12.8 | 59.3 | 50.3 | 30.8 | 59.7 | 48.9 | 42.1 | 68.7 | 151.3 | 69.8 | 68.8 | 64.3 | 55.2 | 305.2 | 243.7 | 288 | 70.8 | 229.5 | 60.4 | 78.3 | 67.7 | 251 | 255.8 | 193.6 | 305.9 | 237.8 | 320.9 | 328.4
3167.1 | 2928.1 | -6.5 | 0 | 0 | 235.2 | 212.6 | 197.1 | 189.6 | 226 | 35.6 | 19.1 | 60 | 4.5 | 233.2 | 15.2 | 59.3 | 50.1 | 30.9 | 59.7 | 49 | 42.1 | 68.7 | 151.3 | 69.5 | 68.8 | 64.3 | 55.1 | 305.2 | 244.1 | 287.9 | 70.7 | 229 | 60.8 | 78.4 | 67.7 | 250.9 | 255.7 | 193.4 | 305.7 | 237.7 | 320.7 | 328.3
3168.1 | 2929.1 | -6.5 | 0 | 0 | 235.1 | 212.7 | 197.1 | 189.5 | 225.9 | 35.5 | 19.1 | 60 | 4.8 | 241.5 | 16.2 | 59.3 | 48.9 | 30.8 | 59.7 | 49 | 42.1 | 68.7 | 151.2 | 69.4 | 69 | 64.4 | 55.1 | 305.1 | 245.7 | 287.7 | 70.4 | 228.6 | 61.5 | 78.4 | 68 | 250.8 | 255.6 | 193.2 | 305.6 | 237.6 | 320.5 | 328.1
3169.1 | 2930.1 | -6.4 | 0 | 0 | 235 | 212.6 | 197.2 | 189.3 | 225.6 | 35.4 | 19.1 | 60 | 4.6 | 256.8 | 14.2 | 59.4 | 48.6 | 30.6 | 59.8 | 49 | 42.1 | 68.7 | 151.6 | 69.2 | 69 | 64.4 | 55.1 | 305 | 245.1 | 287.6 | 70.2 | 228.3 | 62 | 78.3 | 68 | 250.7 | 255.5 | 192.9 | 305.4 | 237.5 | 320.4 | 328
3170.1 | 2931.1 | -6.3 | 0 | 0 | 234.9 | 212.5 | 197.2 | 189.3 | 225.2 | 35.4 | 19.1 | 59.9 | 4.9 | 257.8 | 12.5 | 59.4 | 49.1 | 30.4 | 59.8 | 49 | 42.2 | 68.6 | 151.7 | 69 | 69.2 | 64.5 | 55.1 | 304.9 | 245 | 287.5 | 70.1 | 228.4 | 62.2 | 78.3 | 67.9 | 250.6 | 255.3 | 192.8 | 305.3 | 237.4 | 320.2 | 327.8
3171.1 | 2932.1 | -6.3 | 0 | 0 | 234.5 | 212.4 | 197 | 189.2 | 225.2 | 35.3 | 19.1 | 59.9 | 4.7 | 244 | 12.3 | 59.4 | 49.3 | 30.4 | 59.8 | 49 | 42.2 | 68.6 | 151.4 | 69.1 | 69.3 | 64.5 | 55 | 304.9 | 244.4 | 287.4 | 70 | 228.3 | 61.7 | 78.4 | 67.4 | 250.5 | 255.2 | 192.8 | 305.1 | 237.3 | 320.1 | 327.7
3172.1 | 2933.1 | -6.2 | 0 | 0 | 234.2 | 212.4 | 196.8 | 189 | 225 | 35.3 | 19.1 | 59.8 | 5.6 | 254.7 | 14.5 | 59.4 | 49.3 | 30.5 | 59.8 | 49 | 42.2 | 68.6 | 151.1 | 69.1 | 69 | 64.5 | 54.9 | 304.9 | 244.6 | 287.3 | 69.8 | 228.5 | 61.2 | 78.5 | 67.4 | 250.4 | 255.1 | 192.7 | 305 | 237.2 | 319.9 | 327.5
3173.1 | 2934.1 | -6.1 | 0 | 0 | 234.1 | 212.5 | 196.7 | 188.8 | 224.9 | 35.2 | 19.1 | 59.8 | 4.5 | 263.2 | 15.5 | 59.4 | 49.2 | 30.4 | 59.8 | 49 | 42.2 | 68.6 | 151.2 | 68.8 | 68.8 | 64.6 | 54.8 | 304.8 | 245 | 287.2 | 69.8 | 228.8 | 60.7 | 78.6 | 67.4 | 250.3 | 254.9 | 192.6 | 304.8 | 237.1 | 319.8 | 327.4
3174.1 | 2935.1 | -6.2 | 0 | 0 | 234 | 212.4 | 196.7 | 188.8 | 224.9 | 35.2 | 19.1 | 59.8 | 4.2 | 255.3 | 15.1 | 59.5 | 48.8 | 30.4 | 59.8 | 49 | 42.1 | 68.6 | 151.3 | 68.9 | 68.7 | 64.6 | 54.8 | 304.8 | 244.7 | 287.1 | 69.7 | 228.9 | 60.5 | 78.7 | 67.6 | 250.2 | 254.7 | 192.5 | 304.7 | 237 | 319.6 | 327.2
3175.1 | 2936.1 | -6.3 | 0 | 0 | 233.8 | 212.3 | 196.6 | 188.7 | 225.3 | 35.2 | 19.1 | 59.8 | 4.3 | 282.3 | 10.9 | 59.5 | 48.8 | 30.5 | 59.8 | 49 | 42.1 | 68.6 | 151.2 | 69.2 | 68.7 | 64.6 | 54.9 | 304.7 | 244.9 | 287 | 69.8 | 228.9 | 60.2 | 78.9 | 67.9 | 250.1 | 254.5 | 192.4 | 304.5 | 236.9 | 319.4 | 327.1
3176.1 | 2937.1 | -6.3 | 0 | 0 | 233.8 | 212.2 | 196.4 | 188.6 | 225.7 | 35.1 | 19.1 | 59.7 | 4.5 | 266.1 | 9 | 59.5 | 49.3 | 30.5 | 59.8 | 49 | 42.1 | 68.6 | 151.3 | 69.4 | 68.4 | 64.7 | 54.9 | 304.7 | 245.5 | 286.9 | 69.7 | 228.9 | 59.9 | 79 | 68 | 250 | 254.4 | 192.3 | 304.4 | 236.8 | 319.3 | 326.9
3177.1 | 2938.1 | -6.3 | 0 | 0 | 233.8 | 212.1 | 196.1 | 188.3 | 225.5 | 35.1 | 19.1 | 59.6 | 4.8 | 261.3 | 10.8 | 59.5 | 49.4 | 30.4 | 59.9 | 49 | 42 | 68.6 | 151.3 | 69.4 | 68.3 | 64.7 | 54.9 | 304.6 | 244.8 | 286.8 | 69.6 | 228.8 | 59.6 | 79.1 | 68 | 249.9 | 254.2 | 192.3 | 304.2 | 236.7 | 319.1 | 326.8
3178.1 | 2939.1 | -6.1 | 0 | 0 | 233.6 | 211.9 | 195.8 | 188.2 | 225.3 | 35.1 | 19.1 | 59.6 | 5.7 | 251.2 | 15.1 | 59.5 | 49.8 | 30.4 | 59.9 | 49 | 41.9 | 68.6 | 151.5 | 69 | 68.5 | 64.8 | 54.9 | 304.5 | 244.5 | 286.7 | 69.5 | 228.8 | 59.4 | 79.2 | 67.8 | 249.8 | 254.1 | 192.3 | 304.1 | 236.6 | 319 | 326.6
3179.1 | 2940.1 | -6.1 | 0 | 0 | 233.5 | 211.7 | 195.5 | 188.1 | 225.3 | 35.1 | 19.1 | 59.6 | 7.4 | 255.5 | 17.8 | 59.5 | 49.2 | 30.5 | 59.9 | 49 | 41.9 | 68.6 | 151.8 | 68.7 | 68.6 | 64.8 | 55 | 304.4 | 243.2 | 286.6 | 69.4 | 228.7 | 59.2 | 79.3 | 67.8 | 249.8 | 253.9 | 192.2 | 303.9 | 236.5 | 318.8 | 326.5
3180.1 | 2941.1 | -6 | 0 | 0 | 233.3 | 211.6 | 195.1 | 188.2 | 225.4 | 35.1 | 19.1 | 59.6 | 8 | 255.5 | 18.9 | 59.6 | 49.2 | 30.5 | 59.9 | 49 | 41.9 | 68.6 | 151.7 | 68.8 | 68.6 | 64.9 | 55 | 304.5 | 242.8 | 286.5 | 69.6 | 228.5 | 58.9 | 79.5 | 67.7 | 249.7 | 253.8 | 192.2 | 303.7 | 236.4 | 318.7 | 326.3
3181.1 | 2942.1 | -6.2 | 0 | 0 | 233 | 211.7 | 194.8 | 188.2 | 225.4 | 35.1 | 19.1 | 59.6 | 6.5 | 253.9 | 18.4 | 59.6 | 49.2 | 30.5 | 59.9 | 49 | 41.9 | 68.6 | 151.9 | 68.9 | 68.7 | 64.9 | 55 | 304.5 | 242.6 | 286.4 | 69.6 | 228.4 | 58.8 | 79.7 | 67.5 | 249.6 | 253.7 | 192.2 | 303.6 | 236.3 | 318.5 | 326.2
3182.1 | 2943.1 | -6.6 | 0 | 0 | 232.8 | 211.5 | 194.5 | 188.3 | 225.3 | 35 | 19.1 | 59.5 | 6.7 | 246.7 | 18.3 | 59.6 | 48.9 | 30.4 | 59.9 | 49 | 41.8 | 68.6 | 152.2 | 69.1 | 68.5 | 64.9 | 55 | 304.5 | 242.9 | 286.2 | 69.2 | 228.1 | 59.5 | 79.8 | 67.6 | 249.5 | 253.5 | 192 | 303.4 | 236.2 | 318.3 | 326.1
3183.1 | 2944.1 | -6.7 | 0 | 0 | 232.6 | 211.1 | 194.4 | 188.4 | 225.2 | 35 | 19.1 | 59.4 | 6 | 235.2 | 18 | 59.6 | 48.3 | 30.3 | 59.9 | 49 | 41.8 | 68.6 | 151.9 | 69 | 68.4 | 65 | 55 | 304.5 | 243.2 | 286.1 | 69.1 | 227.8 | 60.2 | 79.9 | 67.5 | 249.4 | 253.4 | 191.8 | 303.3 | 236.1 | 318.2 | 325.9
3184.1 | 2945.1 | -6.7 | 0 | 0 | 232.5 | 210.9 | 194.2 | 188.3 | 224.9 | 34.9 | 19.1 | 59.3 | 6.3 | 243.8 | 20.5 | 59.6 | 49 | 30.3 | 60 | 49 | 41.8 | 68.6 | 151.8 | 69 | 68.5 | 65 | 55.1 | 304.5 | 243.1 | 286 | 69.2 | 227.6 | 60.7 | 80 | 67.5 | 249.3 | 253.3 | 191.9 | 303.2 | 236 | 318.1 | 325.8
3185.1 | 2946.1 | -6.6 | 0 | 0 | 232.4 | 210.9 | 193.9 | 188.2 | 224.2 | 34.9 | 19.1 | 59.3 | 5.9 | 242.4 | 20.4 | 59.6 | 49.5 | 30.5 | 60 | 49.1 | 41.7 | 68.6 | 151.6 | 69 | 68.7 | 65.1 | 55.3 | 304.5 | 243.8 | 285.9 | 69.3 | 227.6 | 60.7 | 80.1 | 67.5 | 249.2 | 253.1 | 191.8 | 303 | 235.9 | 317.9 | 325.6
3186.1 | 2947.1 | -6.6 | 0 | 0 | 232.6 | 210.9 | 193.8 | 188.2 | 223.4 | 34.9 | 19.1 | 59.2 | 6.1 | 252.8 | 20.1 | 59.6 | 49.4 | 30.6 | 60 | 49.1 | 41.7 | 68.6 | 151.3 | 69 | 68.8 | 65.1 | 55.3 | 304.6 | 243.8 | 285.8 | 69.3 | 227.5 | 60.3 | 80.4 | 67.5 | 249.1 | 252.8 | 191.7 | 302.8 | 235.8 | 317.7 | 325.5
3187.1 | 2948.1 | -6.5 | 0 | 0 | 232.4 | 210.6 | 194 | 188.1 | 223.4 | 34.8 | 19.1 | 59.2 | 5.5 | 264.9 | 17.9 | 59.7 | 49.3 | 30.6 | 60 | 49.1 | 41.6 | 68.6 | 151.3 | 69.1 | 68.9 | 65.1 | 55.3 | 304.5 | 243.5 | 285.7 | 69.2 | 227.3 | 60.3 | 80.6 | 67.6 | 249 | 252.6 | 191.5 | 302.7 | 235.7 | 317.6 | 325.3
3188.1 | 2949.1 | -6.4 | 0 | 0 | 232.3 | 210.3 | 194 | 187.9 | 223.4 | 34.8 | 19.1 | 59.2 | 5.1 | 248.2 | 15.2 | 59.7 | 48.9 | 30.6 | 60 | 49.1 | 41.6 | 68.6 | 151.6 | 69.4 | 68.7 | 65.2 | 55.3 | 304.5 | 243.7 | 285.6 | 68.9 | 227.2 | 60.4 | 80.8 | 67.7 | 248.9 | 252.5 | 191.4 | 302.5 | 235.6 | 317.4 | 325.2
3189.1 | 2950.1 | -6.3 | 0 | 0 | 232.2 | 210 | 194 | 187.6 | 223.3 | 34.8 | 19.1 | 59.2 | 4.6 | 247.5 | 15.7 | 59.7 | 48.5 | 30.5 | 60 | 49.1 | 41.6 | 68.6 | 151.5 | 69.6 | 68.9 | 65.2 | 55.4 | 304.5 | 244 | 285.5 | 68.7 | 227.2 | 60.9 | 80.8 | 67.6 | 248.8 | 252.4 | 191.3 | 302.4 | 235.5 | 317.3 | 325
3190.1 | 2951.1 | -6.2 | 0 | 0 | 232 | 209.8 | 194 | 187.4 | 223.1 | 34.7 | 19.2 | 59.1 | 5.3 | 258.8 | 18.3 | 59.7 | 48.5 | 30.2 | 60 | 49.1 | 41.6 | 68.6 | 151.5 | 70 | 69 | 65.3 | 55.4 | 304.4 | 244.2 | 285.4 | 68.8 | 227.2 | 60.6 | 80.9 | 67.7 | 248.7 | 252.3 | 191.2 | 302.2 | 235.4 | 317.1 | 324.9
3191.1 | 2952.1 | -6.2 | 0 | 0 | 231.7 | 209.7 | 193.9 | 187.3 | 223.2 | 34.8 | 19.2 | 59 | 6.6 | 259.9 | 19.3 | 59.7 | 49.2 | 29.9 | 60 | 49.1 | 41.7 | 68.6 | 151.3 | 70.1 | 69.1 | 65.3 | 55.4 | 304.4 | 244.3 | 285.3 | 68.8 | 227.3 | 60.3 | 81 | 67.8 | 248.6 | 252.2 | 191.2 | 302.1 | 235.3 | 317 | 324.7
3192.1 | 2953.1 | -6.4 | 0 | 0 | 231.6 | 209.7 | 193.6 | 187.3 | 223.2 | 34.8 | 19.1 | 58.9 | 6.1 | 254 | 19.4 | 59.7 | 49.8 | 29.7 | 60 | 49.1 | 41.7 | 68.6 | 151.5 | 70.4 | 69.2 | 65.4 | 55.4 | 304.3 | 243.7 | 285.2 | 68.6 | 227.3 | 59.8 | 81.1 | 67.8 | 248.5 | 252 | 191.1 | 301.9 | 235.2 | 316.8 | 324.6
3193.1 | 2954.1 | -6.4 | 0 | 0 | 231.4 | 209.6 | 193.6 | 187.2 | 223.1 | 34.8 | 19.2 | 58.9 | 6 | 260.5 | 18.3 | 59.7 | 49.8 | 29.5 | 60 | 49.1 | 41.6 | 68.5 | 151.4 | 70.2 | 69.2 | 65.4 | 55.1 | 304.2 | 243.2 | 285.1 | 68.7 | 227.4 | 59.6 | 81.2 | 67.6 | 248.5 | 251.9 | 191 | 301.8 | 235.1 | 316.7 | 324.4
3194.1 | 2955.1 | -6.4 | 0 | 0 | 231.1 | 209.5 | 193.6 | 187 | 222.8 | 34.8 | 19.2 | 58.9 | 6.1 | 254.9 | 17.2 | 59.8 | 49.3 | 29.4 | 60.1 | 49.1 | 41.6 | 68.5 | 151.2 | 69.8 | 69 | 65.4 | 55.1 | 304.2 | 243.4 | 285 | 68.7 | 227.3 | 59.5 | 81.4 | 67.4 | 248.4 | 251.9 | 191 | 301.7 | 235 | 316.5 | 324.3
3195.1 | 2956.1 | -6.5 | 0 | 0 | 231 | 209.3 | 193.4 | 186.9 | 222.3 | 34.8 | 19.2 | 58.8 | 6.5 | 251.6 | 15.7 | 59.8 | 48.7 | 29.4 | 60.1 | 49.1 | 41.6 | 68.6 | 151.1 | 69.3 | 68.9 | 65.5 | 55.1 | 304.1 | 243.5 | 284.9 | 68.5 | 227.2 | 59.5 | 81.5 | 67.2 | 248.3 | 251.8 | 191 | 301.5 | 234.9 | 316.4 | 324.2
3196.1 | 2957.1 | -6.5 | 0 | 0 | 230.8 | 209.2 | 193.2 | 186.8 | 221.8 | 34.7 | 19.2 | 58.7 | 6.9 | 256.7 | 15.7 | 59.8 | 48.4 | 29.6 | 60.1 | 49.1 | 41.6 | 68.6 | 150.9 | 69.3 | 68.8 | 65.5 | 55.2 | 304.1 | 243.2 | 284.8 | 68.4 | 227.1 | 59.8 | 81.6 | 67.4 | 248.2 | 251.7 | 190.9 | 301.4 | 234.8 | 316.2 | 324
3197.1 | 2958.1 | -6.4 | 0 | 0 | 230.7 | 208.9 | 193 | 186.7 | 221.6 | 34.7 | 19.2 | 58.6 | 6.3 | 259.9 | 17.9 | 59.8 | 48.5 | 29.7 | 60.1 | 49.1 | 41.6 | 68.6 | 150.6 | 69.1 | 68.9 | 65.6 | 55.2 | 304.2 | 243.3 | 284.7 | 68.5 | 227 | 59.6 | 81.8 | 67.4 | 248.1 | 251.6 | 190.9 | 301.2 | 234.6 | 316.1 | 323.9
3198.1 | 2959.1 | -6.5 | 0 | 0 | 230.4 | 208.7 | 192.8 | 186.8 | 221.7 | 34.7 | 19.2 | 58.6 | 4.9 | 255.7 | 19.8 | 59.8 | 48.3 | 29.6 | 60.1 | 49.1 | 41.6 | 68.6 | 150.3 | 69.2 | 69.1 | 65.6 | 55.2 | 304.2 | 243.6 | 284.5 | 68.5 | 227 | 59.7 | 82 | 67.4 | 248 | 251.6 | 190.7 | 301.1 | 234.5 | 315.9 | 323.7
3199.1 | 2960.1 | -6.6 | 0 | 0 | 230 | 208.7 | 192.6 | 186.8 | 222.1 | 34.7 | 19.2 | 58.6 | 6.4 | 251.2 | 20.6 | 59.8 | 48.2 | 29.5 | 60.1 | 49.1 | 41.6 | 68.5 | 150.2 | 69.2 | 69.2 | 65.6 | 55.2 | 304.2 | 243.9 | 284.5 | 68.5 | 227.1 | 59.3 | 82.2 | 67.2 | 247.9 | 251.5 | 190.5 | 300.9 | 234.4 | 315.8 | 323.6
3200.1 | 2961.1 | -6.4 | 0 | 0 | 229.7 | 208.8 | 192.6 | 186.7 | 222.5 | 34.7 | 19.2 | 58.5 | 7.2 | 257.7 | 19.3 | 59.9 | 48.3 | 29.5 | 60.2 | 49.1 | 41.7 | 68.6 | 150.1 | 69 | 69.1 | 65.7 | 55.2 | 304.1 | 243.5 | 284.4 | 68.4 | 227.2 | 59.1 | 82.5 | 67.2 | 247.8 | 251.5 | 190.4 | 300.8 | 234.3 | 315.6 | 323.4
3201.1 | 2962.1 | -6.4 | 0 | 0 | 229.5 | 208.8 | 192.6 | 186.6 | 222.9 | 34.7 | 19.2 | 58.4 | 6.7 | 245.6 | 18.7 | 59.9 | 48.1 | 29.4 | 60.1 | 49.1 | 41.6 | 68.6 | 150 | 69 | 69.1 | 65.7 | 55.3 | 304.1 | 243.4 | 284.2 | 68.4 | 227.4 | 58.8 | 82.7 | 67.2 | 247.7 | 251.3 | 190.4 | 300.6 | 234.2 | 315.5 | 323.3
3202.1 | 2963.1 | -6.4 | 0 | 0 | 229.4 | 208.6 | 192.5 | 186.7 | 223.4 | 34.7 | 19.2 | 58.3 | 5.6 | 245.6 | 20 | 59.9 | 48.3 | 29.5 | 60.2 | 49.1 | 41.6 | 68.6 | 149.8 | 69.1 | 69.2 | 65.8 | 55.3 | 304.1 | 243.1 | 284.2 | 68.3 | 227.4 | 58.9 | 83.1 | 67.1 | 247.6 | 251.2 | 190.1 | 300.5 | 234.1 | 315.3 | 323.2
3203.1 | 2964.1 | -6.6 | 0 | 0 | 229.3 | 208.4 | 192.6 | 186.4 | 223.5 | 34.7 | 19.2 | 58.2 | 5.7 | 242.2 | 20.3 | 59.9 | 48.1 | 29.6 | 60.2 | 49.2 | 41.5 | 68.6 | 149.8 | 68.8 | 69.2 | 65.8 | 55.3 | 304 | 243.2 | 284.1 | 68.2 | 227.6 | 59 | 83.3 | 67.1 | 247.6 | 251 | 189.9 | 300.3 | 234 | 315.2 | 323
3204.1 | 2965.1 | -6.5 | 0 | 0 | 229.3 | 208.1 | 192.7 | 186.2 | 223.5 | 34.7 | 19.2 | 58.2 | 5.9 | 247.7 | 18.3 | 59.9 | 48.4 | 29.5 | 60.2 | 49.2 | 41.5 | 68.6 | 149.8 | 68.4 | 69 | 65.9 | 55.4 | 304 | 243.7 | 283.9 | 68.1 | 227.6 | 58.7 | 83.5 | 67.2 | 247.5 | 250.8 | 189.7 | 300.2 | 233.9 | 315 | 322.9
3205.1 | 2966.1 | -6.4 | 0 | 0 | 229.1 | 207.9 | 192.8 | 186 | 223.4 | 34.7 | 19.2 | 58.1 | 5.8 | 252 | 16.3 | 59.9 | 48.8 | 29.3 | 60.2 | 49.2 | 41.6 | 68.6 | 149.7 | 68.3 | 68.9 | 65.9 | 55.5 | 304 | 243.8 | 283.8 | 68 | 227.4 | 58.4 | 83.7 | 67.2 | 247.4 | 250.6 | 189.5 | 300 | 233.8 | 314.9 | 322.7
3206.1 | 2967.1 | -6.3 | 0 | 0 | 229 | 207.6 | 192.8 | 185.9 | 223 | 34.6 | 19.2 | 58.1 | 5.2 | 250 | 17.2 | 59.9 | 49 | 29.3 | 60.2 | 49.2 | 41.6 | 68.6 | 149.8 | 68.5 | 69.2 | 65.9 | 55.4 | 304.1 | 244 | 283.7 | 68.1 | 227.2 | 58.2 | 83.8 | 67.4 | 247.3 | 250.5 | 189.2 | 299.9 | 233.7 | 314.7 | 322.6
3207.1 | 2968.1 | -6.3 | 0 | 0 | 228.8 | 207.4 | 192.5 | 185.7 | 222.7 | 34.5 | 19.2 | 58 | 6 | 253.4 | 17.3 | 59.9 | 48.5 | 29.2 | 60.2 | 49.2 | 41.7 | 68.5 | 149.4 | 68.7 | 69.3 | 66 | 55.4 | 304.1 | 244 | 283.6 | 68.2 | 227 | 58.1 | 84 | 67.4 | 247.2 | 250.4 | 189 | 299.8 | 233.6 | 314.6 | 322.4
3208.1 | 2969.1 | -6.4 | 0 | 0 | 228.6 | 207.2 | 192.1 | 185.6 | 222.8 | 34.5 | 19.2 | 58 | 6.1 | 261.3 | 15.4 | 59.9 | 48.1 | 29.2 | 60.2 | 49.2 | 41.6 | 68.6 | 149.3 | 68.7 | 69.2 | 66 | 55.4 | 304.1 | 243.9 | 283.5 | 68.2 | 227 | 57.8 | 84.3 | 67.4 | 247.1 | 250.2 | 188.9 | 299.6 | 233.5 | 314.4 | 322.3
3209.1 | 2970.1 | -6.5 | 0 | 0 | 228.6 | 206.9 | 192 | 185.4 | 222.9 | 34.5 | 19.2 | 57.9 | 6.2 | 263.6 | 13.7 | 60 | 48.6 | 29.1 | 60.2 | 49.2 | 41.6 | 68.5 | 149.3 | 68.7 | 69.3 | 66 | 55.5 | 304.1 | 243.9 | 283.4 | 68.2 | 226.9 | 57.7 | 84.6 | 67.3 | 247 | 250 | 188.7 | 299.5 | 233.4 | 314.3 | 322.2
3210.1 | 2971.1 | -6.5 | 0 | 0 | 228.6 | 206.7 | 192 | 185.3 | 222.8 | 34.5 | 19.2 | 57.9 | 6.7 | 255.7 | 14.9 | 60 | 48.9 | 29 | 60.2 | 49.2 | 41.6 | 68.5 | 149.6 | 68.6 | 69.4 | 66.1 | 55.5 | 304.1 | 243.6 | 283.3 | 68.2 | 226.9 | 57.9 | 84.9 | 66.8 | 246.9 | 250 | 188.5 | 299.3 | 233.3 | 314.1 | 322
3211.1 | 2972.1 | -6.6 | 0 | 0 | 228.5 | 206.6 | 191.8 | 185.5 | 222.4 | 34.5 | 19.2 | 57.9 | 7.7 | 263.8 | 16.4 | 60 | 48 | 28.8 | 60.2 | 49.2 | 41.7 | 68.6 | 149.4 | 68.7 | 69.4 | 66.1 | 55.5 | 304 | 243.3 | 283.2 | 68.1 | 226.9 | 57.6 | 85.1 | 66.9 | 246.8 | 250 | 188.5 | 299.2 | 233.2 | 314 | 321.9
3212.1 | 2973.1 | -6.6 | 0 | 0 | 228.4 | 206.6 | 191.5 | 185.6 | 222.1 | 34.5 | 19.2 | 57.9 | 6.8 | 257.4 | 17.7 | 60 | 48.2 | 28.8 | 60.2 | 49.2 | 41.7 | 68.6 | 149.5 | 68.9 | 69.3 | 66.1 | 55.3 | 303.9 | 243.4 | 283.1 | 68.1 | 226.9 | 57.5 | 85.3 | 66.6 | 246.7 | 249.9 | 188.6 | 299.1 | 233.2 | 313.8 | 321.7
3213.1 | 2974.1 | -6.6 | 0 | 0 | 228.2 | 206.6 | 191.4 | 185.5 | 221.8 | 34.5 | 19.2 | 57.9 | 6 | 250.8 | 17.6 | 60 | 48.2 | 28.7 | 60.3 | 49.2 | 41.7 | 68.6 | 149.5 | 69.2 | 69.2 | 66.2 | 55.3 | 303.9 | 243.6 | 283 | 68.2 | 226.9 | 57.3 | 85.6 | 66.6 | 246.6 | 249.8 | 188.5 | 298.9 | 233.1 | 313.7 | 321.6
3214.1 | 2975.1 | -6.7 | 0 | 0 | 227.9 | 206.5 | 191.3 | 185.3 | 221.2 | 34.5 | 19.2 | 57.8 | 5.4 | 227.6 | 18 | 60 | 48.6 | 28.7 | 60.3 | 49.2 | 41.7 | 68.6 | 149.7 | 69.3 | 69.3 | 66.2 | 55.4 | 303.9 | 243.5 | 282.9 | 68.1 | 226.8 | 57.2 | 85.8 | 66.8 | 246.6 | 249.6 | 188.4 | 298.8 | 233 | 313.5 | 321.4
3215.1 | 2976.1 | -6.6 | 0 | 0 | 227.7 | 206.2 | 191 | 185.3 | 220.8 | 34.4 | 19.2 | 57.7 | 3.8 | 244.5 | 16.6 | 60 | 49.4 | 28.8 | 60.3 | 49.3 | 41.8 | 68.6 | 149.8 | 69.5 | 69.3 | 66.3 | 55.4 | 303.9 | 243.3 | 282.8 | 68 | 226.7 | 57.1 | 86.1 | 66.8 | 246.5 | 249.4 | 188.2 | 298.6 | 232.9 | 313.4 | 321.3
3216.1 | 2977.1 | -6.5 | 0 | 0 | 227.3 | 206 | 191 | 185.3 | 221 | 34.4 | 19.2 | 57.6 | 4.2 | 237.1 | 15.1 | 60 | 49.4 | 28.8 | 60.3 | 49.3 | 41.8 | 68.5 | 149.8 | 69.6 | 69.4 | 66.3 | 55.4 | 303.9 | 243.4 | 282.7 | 67.8 | 226.6 | 57.1 | 86.3 | 66.8 | 246.4 | 249.3 | 188.1 | 298.5 | 232.8 | 313.2 | 321.2
3217.1 | 2978.1 | -6.3 | 0 | 0 | 227.2 | 205.7 | 191 | 185.2 | 221 | 34.4 | 19.2 | 57.6 | 3.5 | 252 | 13.6 | 60.1 | 49.4 | 28.9 | 60.3 | 49.3 | 41.8 | 68.5 | 149.8 | 69.7 | 69.4 | 66.3 | 55.4 | 303.8 | 244.2 | 282.6 | 67.8 | 226.5 | 58.1 | 86.5 | 66.8 | 246.3 | 249.1 | 187.9 | 298.3 | 232.7 | 313.1 | 321
3218.1 | 2979.1 | -6.1 | 0 | 0 | 227.3 | 205.7 | 190.7 | 185 | 220.6 | 34.3 | 19.2 | 57.6 | 4.6 | 248.2 | 12.3 | 60.1 | 50 | 29.1 | 60.3 | 49.3 | 41.8 | 68.5 | 149.7 | 69.2 | 69.5 | 66.4 | 55.4 | 303.7 | 243.3 | 282.5 | 67.8 | 226.4 | 58 | 86.6 | 67 | 246.2 | 249 | 187.8 | 298.2 | 232.6 | 312.9 | 320.9
3219.1 | 2980.1 | -6.2 | 0 | 0 | 227.6 | 205.7 | 190.5 | 184.8 | 220.4 | 34.3 | 19.2 | 57.6 | 3.8 | 232.1 | 13.5 | 60.1 | 50.1 | 29.1 | 60.3 | 49.3 | 41.8 | 68.5 | 149.7 | 68.7 | 69.7 | 66.4 | 55.3 | 303.7 | 243.2 | 282.4 | 67.9 | 226.3 | 58 | 86.9 | 67.1 | 246.1 | 248.8 | 187.7 | 298 | 232.5 | 312.8 | 320.7
3220.1 | 2981.1 | -6.2 | 0 | 0 | 227.6 | 205.8 | 190.1 | 184.9 | 220.3 | 34.3 | 19.2 | 57.6 | 3.5 | 244.9 | 11.7 | 60.1 | 49.4 | 29.1 | 60.3 | 49.3 | 41.8 | 68.5 | 149.8 | 68.1 | 69.8 | 66.4 | 55.4 | 303.6 | 243.1 | 282.3 | 67.9 | 226 | 57.7 | 87.1 | 67 | 246 | 248.6 | 187.6 | 297.9 | 232.4 | 312.6 | 320.6
3221.1 | 2982.1 | -6.2 | 0 | 0 | 227.3 | 205.7 | 189.8 | 184.9 | 220.4 | 34.3 | 19.2 | 57.6 | 3.9 | 248.2 | 10.2 | 60.1 | 49.3 | 29.3 | 60.3 | 49.3 | 41.8 | 68.5 | 149.9 | 67.7 | 70 | 66.5 | 55.4 | 303.5 | 243 | 282.2 | 67.7 | 225.7 | 57.7 | 87.2 | 67 | 245.9 | 248.5 | 187.6 | 297.8 | 232.3 | 312.5 | 320.5
3222.1 | 2983.1 | -6.2 | 0 | 0 | 227.1 | 205.8 | 189.8 | 184.8 | 220.5 | 34.3 | 19.2 | 57.6 | 3.7 | 228.9 | 11.8 | 60.1 | 49.5 | 29.4 | 60.4 | 49.3 | 41.7 | 68.6 | 149.6 | 68 | 69.9 | 66.5 | 55.3 | 303.5 | 242.1 | 282.1 | 67.6 | 225.3 | 57.8 | 87.2 | 67 | 245.8 | 248.2 | 187.5 | 297.6 | 232.2 | 312.3 | 320.3
3223.1 | 2984.1 | -6.3 | 0 | 0 | 226.9 | 205.8 | 189.9 | 184.8 | 220.3 | 34.3 | 19.2 | 57.6 | 3.3 | 237.1 | 11.8 | 60.2 | 48.9 | 29.4 | 60.4 | 49.3 | 41.7 | 68.6 | 149.5 | 68.2 | 69.8 | 66.6 | 55.3 | 303.4 | 242.4 | 281.9 | 67.7 | 225 | 58.7 | 87.3 | 67.2 | 245.7 | 248.1 | 187.5 | 297.5 | 232.1 | 312.2 | 320.2
3224.1 | 2985.1 | -6.4 | 0 | 0 | 226.8 | 205.8 | 189.9 | 184.6 | 220.2 | 34.3 | 19.2 | 57.6 | 3.4 | 242.8 | 12.4 | 60.2 | 48.7 | 29.5 | 60.4 | 49.3 | 41.6 | 68.5 | 149.5 | 68.1 | 69.8 | 66.6 | 55.3 | 303.4 | 242.3 | 281.8 | 67.6 | 224.7 | 59.5 | 87.4 | 67.3 | 245.7 | 248 | 187.4 | 297.3 | 232 | 312.1 | 320
3225.1 | 2986.1 | -6.2 | 0 | 0 | 226.9 | 205.6 | 189.9 | 184.4 | 220.3 | 34.3 | 19.2 | 57.7 | 3.3 | 213.2 | 12.1 | 60.2 | 48.6 | 29.4 | 60.4 | 49.3 | 41.6 | 68.5 | 149.4 | 67.9 | 69.8 | 66.6 | 55.3 | 303.4 | 242.5 | 281.7 | 67.6 | 224.7 | 59.3 | 87.5 | 67.4 | 245.6 | 247.9 | 187.3 | 297.2 | 231.9 | 311.9 | 319.9
3226.1 | 2987.1 | -6 | 0 | 0 | 226.7 | 205.3 | 189.7 | 184.3 | 220.3 | 34.3 | 19.2 | 57.7 | 3.3 | 246 | 10.6 | 60.2 | 48.9 | 29.3 | 60.4 | 49.3 | 41.6 | 68.5 | 149.6 | 67.8 | 69.8 | 66.7 | 55.3 | 303.3 | 241.8 | 281.6 | 67.7 | 224.4 | 59.3 | 87.7 | 67.3 | 245.5 | 247.8 | 187.3 | 297 | 231.8 | 311.8 | 319.7
3227.1 | 2988.1 | -6.2 | 0 | 0 | 226.6 | 205.1 | 189.7 | 184.3 | 220.4 | 34.3 | 19.3 | 57.6 | 3.9 | 236.6 | 8.6 | 60.2 | 48.9 | 29.5 | 60.4 | 49.3 | 41.5 | 68.5 | 149.3 | 67.9 | 69.9 | 66.7 | 55.3 | 303.3 | 241.8 | 281.6 | 67.6 | 224.4 | 59.4 | 87.9 | 67.4 | 245.4 | 247.6 | 187.3 | 296.9 | 231.7 | 311.6 | 319.6
3228.1 | 2989.1 | -6.1 | 0 | 0 | 226.5 | 205.1 | 189.7 | 184.1 | 220.3 | 34.3 | 19.3 | 57.6 | 4.2 | 252.7 | 7.7 | 60.3 | 49.1 | 29.7 | 60.4 | 49.3 | 41.5 | 68.5 | 149.2 | 68.4 | 69.8 | 66.7 | 55.4 | 303.3 | 241.9 | 281.5 | 67.6 | 224.4 | 59.1 | 88.1 | 67.5 | 245.3 | 247.5 | 187.1 | 296.8 | 231.6 | 311.5 | 319.5
3229.1 | 2990.1 | -6.1 | 0 | 0 | 226.4 | 205 | 189.6 | 183.9 | 219.9 | 34.3 | 19.3 | 57.6 | 4 | 237.5 | 7.7 | 60.3 | 49.1 | 29.7 | 60.4 | 49.3 | 41.4 | 68.4 | 149.3 | 68.8 | 70 | 66.8 | 55.4 | 303.2 | 241.9 | 281.3 | 67.6 | 224.4 | 58.9 | 88.2 | 67.4 | 245.2 | 247.3 | 187.1 | 296.6 | 231.5 | 311.3 | 319.3
3230.1 | 2991.1 | -6 | 0 | 0 | 226.2 | 205 | 189.6 | 183.7 | 220 | 34.3 | 19.3 | 57.6 | 3.8 | 226.3 | 6.9 | 60.3 | 48.9 | 29.7 | 60.4 | 49.3 | 41.4 | 68.4 | 149.1 | 69 | 70 | 66.8 | 55.4 | 303.2 | 242.2 | 281.3 | 67.6 | 224.4 | 59 | 88.4 | 67.6 | 245.1 | 247.2 | 187 | 296.5 | 231.4 | 311.2 | 319.2
3231.1 | 2992.1 | -5.9 | 0 | 0 | 226.1 | 204.9 | 189.5 | 183.6 | 219.9 | 34.4 | 19.3 | 57.7 | 4 | 227 | 6.3 | 60.3 | 49 | 29.8 | 60.5 | 49.4 | 41.4 | 68.4 | 148.9 | 69.2 | 69.9 | 66.9 | 55.4 | 303.1 | 242.2 | 281.1 | 67.5 | 224.1 | 58.9 | 88.5 | 67.4 | 245 | 247.1 | 186.8 | 296.3 | 231.3 | 311 | 319.1
3232.1 | 2993.1 | -6 | 0 | 0 | 226 | 204.8 | 189.2 | 183.6 | 219.1 | 34.4 | 19.3 | 57.7 | 4.5 | 218.7 | 7 | 60.3 | 49.7 | 30 | 60.5 | 49.3 | 41.3 | 68.4 | 148.7 | 69.3 | 69.9 | 66.9 | 55.5 | 303.1 | 242.4 | 281 | 67.6 | 223.9 | 59 | 88.6 | 67.3 | 245 | 247 | 186.7 | 296.2 | 231.2 | 310.9 | 318.9
3233.1 | 2994.1 | -6.1 | 0 | 0 | 225.9 | 204.7 | 189.2 | 183.5 | 218.5 | 34.4 | 19.3 | 57.7 | 4.4 | 245.5 | 6.8 | 60.3 | 49.2 | 30 | 60.5 | 49.4 | 41.3 | 68.4 | 148.7 | 69.5 | 70 | 66.9 | 55.3 | 303.1 | 242.6 | 281 | 67.6 | 223.7 | 58.9 | 88.8 | 67.2 | 244.9 | 246.9 | 186.6 | 296 | 231.1 | 310.7 | 318.8
3234.1 | 2995.1 | -6.1 | 0 | 0 | 225.6 | 204.7 | 189.3 | 183.4 | 218.2 | 34.4 | 19.3 | 57.8 | 3.8 | 231.7 | 7.7 | 60.4 | 49.2 | 30 | 60.5 | 49.4 | 41.3 | 68.4 | 148.5 | 69.6 | 69.8 | 66.9 | 55.4 | 303.1 | 242.2 | 280.8 | 67.6 | 223.7 | 58.8 | 88.9 | 67.1 | 244.8 | 246.8 | 186.6 | 295.9 | 231 | 310.6 | 318.6
3235.1 | 2996.1 | -6.1 | 0 | 0 | 225.3 | 204.6 | 189.1 | 183.2 | 217.9 | 34.4 | 19.3 | 57.7 | 3.4 | 239 | 8.6 | 60.4 | 50 | 29.9 | 60.5 | 49.4 | 41.4 | 68.4 | 148.6 | 69.8 | 70.1 | 67 | 55.3 | 303 | 242.1 | 280.8 | 67.6 | 223.7 | 58.6 | 89 | 67.1 | 244.7 | 246.6 | 186.4 | 295.7 | 230.9 | 310.4 | 318.5
3236.1 | 2997.1 | -6.3 | 0 | 0 | 225.1 | 204.6 | 188.8 | 183 | 217.6 | 34.3 | 19.3 | 57.7 | 3.3 | 224.3 | 10.4 | 60.4 | 50.5 | 29.7 | 60.5 | 49.4 | 41.4 | 68.4 | 148.6 | 69.9 | 70.2 | 67 | 55.3 | 302.9 | 241.7 | 280.6 | 67.6 | 223.6 | 58.3 | 89.1 | 66.7 | 244.6 | 246.5 | 186.2 | 295.6 | 230.8 | 310.3 | 318.4
3237.1 | 2998.1 | -6.3 | 0 | 0 | 225.1 | 204.6 | 188.6 | 182.9 | 217.8 | 34.3 | 19.3 | 57.7 | 3.3 | 216.9 | 10.4 | 60.4 | 50.2 | 29.5 | 60.5 | 49.4 | 41.4 | 68.3 | 148.6 | 70 | 70.2 | 67 | 55.3 | 302.8 | 241.6 | 280.5 | 67.4 | 223.5 | 58.2 | 89.2 | 66.7 | 244.5 | 246.4 | 186.2 | 295.5 | 230.7 | 310.2 | 318.2
3238.1 | 2999.1 | -6.4 | 0 | 0 | 225 | 204.5 | 188.3 | 182.9 | 218 | 34.3 | 19.3 | 57.7 | 3.8 | 213.8 | 10.9 | 60.4 | 49.8 | 29.4 | 60.5 | 49.4 | 41.4 | 68.3 | 148.3 | 70.4 | 70.3 | 67.1 | 55.3 | 302.7 | 241.1 | 280.4 | 67.3 | 223.7 | 58.1 | 89.3 | 66.8 | 244.4 | 246.3 | 186 | 295.3 | 230.6 | 310 | 318.1
3239.1 | 3000.1 | -6.4 | 0 | 0 | 224.8 | 204.3 | 187.9 | 182.9 | 218.1 | 34.2 | 19.3 | 57.7 | 4.3 | 222.8 | 10.2 | 60.4 | 49.6 | 29.1 | 60.5 | 49.4 | 41.4 | 68.3 | 148.5 | 70.5 | 70.4 | 67.1 | 55.1 | 302.7 | 242.1 | 280.3 | 67.3 | 223.7 | 57.9 | 89.3 | 66.8 | 244.3 | 246.1 | 185.8 | 295.2 | 230.5 | 309.9 | 318
3240.1 | 3001.1 | -6.3 | 0 | 0 | 224.7 | 204.2 | 187.6 | 182.7 | 218.3 | 34.2 | 19.3 | 57.7 | 4.1 | 214.5 | 9.3 | 60.4 | 48.7 | 29.1 | 60.5 | 49.4 | 41.4 | 68.3 | 148.6 | 70.6 | 70.4 | 67.1 | 55 | 302.7 | 242.5 | 280.2 | 67.4 | 223.9 | 57.8 | 89.3 | 66.9 | 244.3 | 246 | 185.7 | 295 | 230.4 | 309.7 | 317.8
3241.1 | 3002.1 | -6.3 | 0 | 0 | 224.5 | 204.1 | 187.6 | 182.6 | 218.2 | 34.2 | 19.3 | 57.8 | 3.7 | 211.4 | 9.2 | 60.5 | 48.3 | 29.1 | 60.5 | 49.4 | 41.4 | 68.3 | 148.7 | 70.1 | 70.4 | 67.2 | 55.1 | 302.6 | 242.4 | 280.1 | 67.4 | 224 | 57.7 | 89.5 | 67 | 244.2 | 245.8 | 185.6 | 294.9 | 230.3 | 309.6 | 317.7
3242.1 | 3003.1 | -6.3 | 0 | 0 | 224.4 | 204 | 187.5 | 182.3 | 218 | 34.2 | 19.3 | 57.8 | 3.4 | 209.7 | 9.7 | 60.5 | 48.4 | 29.1 | 60.6 | 49.4 | 41.4 | 68.3 | 149 | 69.1 | 70.5 | 67.2 | 55.1 | 302.5 | 242.5 | 280 | 67.3 | 223.9 | 57.6 | 89.5 | 67 | 244.1 | 245.7 | 185.6 | 294.8 | 230.3 | 309.5 | 317.6
3243.1 | 3004.1 | -6.4 | 0 | 0 | 224.3 | 204 | 187.2 | 182 | 217.7 | 34.2 | 19.3 | 57.9 | 3.3 | 215.5 | 10.6 | 60.5 | 48 | 29.2 | 60.6 | 49.4 | 41.4 | 68.3 | 149 | 69 | 70.3 | 67.2 | 55.1 | 302.4 | 242.3 | 279.9 | 67.2 | 223.4 | 57.4 | 89.5 | 66.9 | 244 | 245.5 | 185.6 | 294.6 | 230.2 | 309.3 | 317.4
3244.1 | 3005.1 | -6.4 | 0 | 0 | 224.2 | 204 | 187.2 | 181.9 | 217.9 | 34.2 | 19.3 | 57.9 | 3.9 | 215.7 | 10.9 | 60.5 | 48.7 | 29.3 | 60.6 | 49.4 | 41.4 | 68.3 | 148.7 | 68.9 | 70.5 | 67.2 | 55 | 302.4 | 242.6 | 279.8 | 67.1 | 223 | 57.3 | 89.5 | 66.7 | 243.9 | 245.5 | 185.4 | 294.5 | 230 | 309.2 | 317.3
3245.1 | 3006.1 | -6.3 | 0 | 0 | 224.2 | 203.9 | 187.3 | 182 | 218.2 | 34.1 | 19.3 | 58 | 4 | 229.9 | 10.9 | 60.5 | 48.9 | 29.3 | 60.6 | 49.4 | 41.4 | 68.3 | 148.8 | 68.5 | 70.6 | 67.3 | 55 | 302.4 | 242.7 | 279.8 | 67.3 | 222.5 | 57.2 | 89.5 | 66.7 | 243.8 | 245.4 | 185.2 | 294.4 | 229.9 | 309 | 317.2
3246.1 | 3007.1 | -6.3 | 0 | 0 | 224.2 | 203.6 | 187.2 | 181.9 | 218.3 | 34.1 | 19.3 | 58 | 4.3 | 227.8 | 9.7 | 60.5 | 48.4 | 29.6 | 60.6 | 49.4 | 41.4 | 68.3 | 148.7 | 68.2 | 70.4 | 67.3 | 55.1 | 302.3 | 242.8 | 279.6 | 67.2 | 222.3 | 57.1 | 89.5 | 66.8 | 243.7 | 245.3 | 185.1 | 294.2 | 229.8 | 308.9 | 317
3247.1 | 3008.1 | -6.1 | 0 | 0 | 224 | 203.3 | 187.2 | 181.8 | 218.4 | 34.1 | 19.3 | 58.1 | 4.3 | 241.8 | 7.4 | 60.6 | 48.2 | 29.7 | 60.6 | 49.4 | 41.4 | 68.3 | 148.4 | 68 | 70.4 | 67.3 | 55.2 | 302.2 | 242.8 | 279.5 | 67 | 222.2 | 57.2 | 89.6 | 66.9 | 243.6 | 245.3 | 184.9 | 294.1 | 229.8 | 308.8 | 316.9
3248.1 | 3009.1 | -6.2 | 0 | 0 | 223.8 | 203.1 | 187.1 | 181.7 | 218.4 | 34.1 | 19.3 | 58.1 | 4.3 | 205 | 7.5 | 60.6 | 48.4 | 29.7 | 60.6 | 49.4 | 41.4 | 68.3 | 148.6 | 67.6 | 70.3 | 67.4 | 55.2 | 302.1 | 242.8 | 279.4 | 66.9 | 222 | 57.3 | 89.5 | 66.9 | 243.5 | 245.2 | 184.8 | 293.9 | 229.7 | 308.6 | 316.7
3249.1 | 3010.1 | -6.2 | 0 | 0 | 223.6 | 203 | 186.8 | 181.6 | 218.5 | 34.1 | 19.3 | 58.1 | 4.9 | 216.8 | 7.3 | 60.6 | 49 | 29.7 | 60.6 | 49.4 | 41.4 | 68.3 | 148.6 | 67.4 | 70.6 | 67.4 | 55.2 | 302.1 | 243.1 | 279.3 | 67 | 221.9 | 57.7 | 89.6 | 66.9 | 243.5 | 245.1 | 184.7 | 293.8 | 229.6 | 308.5 | 316.6
3250.1 | 3011.1 | -6.2 | 0 | 0 | 223.5 | 202.9 | 186.7 | 181.4 | 218.3 | 34.1 | 19.3 | 58.2 | 5 | 237.1 | 6.5 | 60.6 | 49.1 | 29.8 | 60.6 | 49.4 | 41.4 | 68.3 | 148.8 | 67.3 | 70.7 | 67.4 | 55.3 | 302.1 | 243.2 | 279.2 | 67 | 222 | 57.6 | 89.6 | 67.1 | 243.4 | 244.9 | 184.7 | 293.6 | 229.5 | 308.3 | 316.5
3251.1 | 3012.1 | -6.3 | 0 | 0 | 223.3 | 202.8 | 186.6 | 181.4 | 218.2 | 34.1 | 19.3 | 58.2 | 5.2 | 190.4 | 5.8 | 60.6 | 49.6 | 29.8 | 60.6 | 49.4 | 41.5 | 68.3 | 148.5 | 67.2 | 70.7 | 67.5 | 55.2 | 302.1 | 243.8 | 279.1 | 67.2 | 222 | 57.6 | 89.8 | 67 | 243.3 | 244.8 | 184.6 | 293.5 | 229.4 | 308.2 | 316.3
3252.1 | 3013.1 | -6.4 | 0 | 0 | 223.3 | 202.6 | 186.5 | 181.4 | 218 | 34.2 | 19.3 | 58.2 | 4.6 | 225.1 | 5.7 | 60.6 | 49.6 | 29.8 | 60.6 | 49.4 | 41.5 | 68.3 | 148.3 | 66.9 | 70.7 | 67.5 | 55.2 | 302 | 243.3 | 279.1 | 67.1 | 221.7 | 57.6 | 90 | 66.6 | 243.2 | 244.6 | 184.4 | 293.4 | 229.3 | 308 | 316.2
3253.1 | 3014.1 | -6.3 | 0 | 0 | 223.2 | 202.5 | 186.4 | 181.5 | 217.9 | 34.2 | 19.3 | 58.2 | 4.4 | 220.2 | 6.6 | 60.6 | 49.1 | 29.8 | 60.6 | 49.4 | 41.5 | 68.3 | 148 | 66.8 | 70.6 | 67.5 | 55.1 | 302 | 243 | 278.9 | 67.1 | 221.4 | 57.5 | 90.2 | 66.7 | 243.1 | 244.5 | 184.3 | 293.2 | 229.2 | 307.9 | 316.1
3254.1 | 3015.1 | -6.3 | 0 | 0 | 223.2 | 202.5 | 186.1 | 181.5 | 218 | 34.2 | 19.3 | 58.1 | 4.8 | 224.1 | 7.9 | 60.6 | 49.1 | 29.8 | 60.6 | 49.4 | 41.5 | 68.3 | 147.9 | 66.5 | 70.8 | 67.6 | 55 | 301.9 | 243 | 278.8 | 66.8 | 221.3 | 57.5 | 90.3 | 66.9 | 243 | 244.3 | 184.2 | 293.1 | 229.1 | 307.8 | 315.9
3255.1 | 3016.1 | -6.3 | 0 | 0 | 223 | 202.5 | 186.2 | 181.4 | 218.1 | 34.2 | 19.4 | 58.1 | 4.9 | 229.3 | 9.3 | 60.7 | 49.6 | 29.8 | 60.7 | 49.4 | 41.5 | 68.2 | 148 | 66.3 | 70.7 | 67.6 | 55.1 | 301.8 | 242.9 | 278.7 | 66.6 | 221.2 | 57.3 | 90.3 | 66.9 | 242.9 | 244.2 | 184.1 | 292.9 | 229 | 307.6 | 315.8
3256.1 | 3017.1 | -6.3 | 0 | 0 | 222.8 | 202.4 | 186.2 | 181.2 | 218.2 | 34.2 | 19.4 | 58.1 | 4.1 | 209.4 | 8.8 | 60.7 | 49.7 | 29.8 | 60.7 | 49.5 | 41.5 | 68.3 | 148 | 66.3 | 70.8 | 67.6 | 55 | 301.8 | 243.1 | 278.6 | 66.6 | 221.2 | 57.1 | 90.4 | 67 | 242.9 | 244.1 | 184 | 292.8 | 228.9 | 307.5 | 315.7
3257.1 | 3018.1 | -6.3 | 0 | 0 | 222.5 | 202.3 | 186 | 181 | 218.2 | 34.2 | 19.4 | 58.1 | 3.9 | 216.1 | 9.3 | 60.7 | 48.6 | 29.7 | 60.7 | 49.5 | 41.5 | 68.2 | 148 | 66.3 | 70.9 | 67.7 | 55 | 301.7 | 243.2 | 278.6 | 66.6 | 221.1 | 57 | 90.4 | 66.9 | 242.8 | 244.1 | 183.9 | 292.7 | 228.8 | 307.3 | 315.5
3258.1 | 3019.1 | -6.3 | 0 | 0 | 222.2 | 202.1 | 185.7 | 181 | 217.8 | 34.3 | 19.4 | 58.1 | 3.8 | 221.5 | 8.5 | 60.7 | 48.1 | 29.7 | 60.7 | 49.5 | 41.5 | 68.2 | 147.8 | 66.3 | 71.1 | 67.7 | 55 | 301.6 | 242.9 | 278.4 | 66.5 | 221.1 | 57 | 90.5 | 66.9 | 242.7 | 244 | 183.9 | 292.5 | 228.7 | 307.2 | 315.4
3259.1 | 3020.1 | -6.3 | 0 | 0 | 221.9 | 201.8 | 185.4 | 181 | 217.4 | 34.3 | 19.4 | 58.1 | 4 | 237.9 | 8.2 | 60.7 | 47.8 | 29.8 | 60.7 | 49.5 | 41.5 | 68.2 | 147.7 | 66.3 | 71.3 | 67.7 | 55.1 | 301.6 | 242.9 | 278.3 | 66.6 | 221.2 | 57.6 | 90.6 | 67 | 242.6 | 243.9 | 183.9 | 292.4 | 228.6 | 307 | 315.3
3260.1 | 3021.1 | -6.4 | 0 | 0 | 221.7 | 201.7 | 185 | 181.2 | 217.5 | 34.3 | 19.4 | 58.1 | 4.2 | 222.4 | 8.9 | 60.7 | 47.6 | 29.8 | 60.7 | 49.5 | 41.5 | 68.2 | 147.6 | 66.2 | 70.9 | 67.7 | 55.2 | 301.5 | 242.9 | 278.2 | 66.5 | 221.1 | 57.6 | 90.8 | 67.1 | 242.5 | 243.8 | 183.7 | 292.3 | 228.5 | 306.9 | 315.1
3261.1 | 3022.1 | -6.5 | 0 | 0 | 221.6 | 201.7 | 184.7 | 181.1 | 217.6 | 34.3 | 19.4 | 58.1 | 4 | 236.7 | 9.3 | 60.7 | 47.7 | 29.7 | 60.7 | 49.5 | 41.5 | 68.2 | 147.2 | 65.9 | 70.9 | 67.8 | 55.2 | 301.4 | 242.9 | 278.2 | 66.5 | 221.2 | 57.4 | 91 | 66.9 | 242.4 | 243.6 | 183.5 | 292.1 | 228.4 | 306.8 | 315
3262.1 | 3023.1 | -6.3 | 0 | 0 | 221.6 | 201.6 | 184.6 | 181 | 217.6 | 34.3 | 19.4 | 58.1 | 3.6 | 229.3 | 8.3 | 60.7 | 47 | 29.6 | 60.7 | 49.5 | 41.6 | 68.2 | 147.5 | 65.9 | 70.8 | 67.8 | 55.2 | 301.4 | 243.1 | 278.1 | 66.5 | 221.1 | 57.2 | 91.1 | 66.5 | 242.3 | 243.5 | 183.4 | 292 | 228.3 | 306.6 | 314.9
3263.1 | 3024.1 | -6.3 | 0 | 0 | 221.8 | 201.4 | 184.5 | 180.9 | 217.7 | 34.2 | 19.4 | 58 | 3.6 | 203 | 7.2 | 60.8 | 46.8 | 29.5 | 60.7 | 49.5 | 41.6 | 68.2 | 147.4 | 65.9 | 70.9 | 67.8 | 55.2 | 301.4 | 243.3 | 278 | 66.3 | 221.1 | 57.1 | 91.1 | 66.2 | 242.3 | 243.4 | 183.3 | 291.8 | 228.2 | 306.5 | 314.8
3264.1 | 3025.1 | -6.3 | 0 | 0 | 221.6 | 201.2 | 184.5 | 180.9 | 217.6 | 34.2 | 19.4 | 57.9 | 3.6 | 213.3 | 8.4 | 60.8 | 46.6 | 29.5 | 60.7 | 49.5 | 41.6 | 68.2 | 147.4 | 65.8 | 71 | 67.8 | 55.3 | 301.3 | 243.8 | 277.8 | 66.2 | 220.9 | 57 | 91.1 | 66.3 | 242.2 | 243.2 | 183.3 | 291.7 | 228.1 | 306.4 | 314.6
3265.1 | 3026.1 | -6.3 | 0 | 0 | 221.3 | 201.2 | 184.5 | 180.8 | 217.2 | 34.2 | 19.4 | 57.9 | 4 | 221.2 | 8.8 | 60.8 | 47.1 | 29.6 | 60.7 | 49.5 | 41.7 | 68.2 | 147.4 | 65.7 | 71.3 | 67.9 | 55.2 | 301.3 | 243.4 | 277.7 | 66.2 | 220.9 | 56.9 | 91 | 66.6 | 242.1 | 243.1 | 183.2 | 291.6 | 228 | 306.2 | 314.5
3266.1 | 3027.1 | -6.3 | 0 | 0 | 221.1 | 201.2 | 184.4 | 180.5 | 217.2 | 34.2 | 19.4 | 57.9 | 3.9 | 214.9 | 11.2 | 60.8 | 47.5 | 29.6 | 60.7 | 49.5 | 41.7 | 68.2 | 147.3 | 65.7 | 71.1 | 67.9 | 55.2 | 301.2 | 243.1 | 277.6 | 66.2 | 220.9 | 57 | 91 | 66.5 | 242 | 243 | 183 | 291.4 | 227.9 | 306.1 | 314.4
3267.1 | 3028.1 | -6.4 | 0 | 0 | 220.8 | 201.1 | 184.3 | 180.3 | 216.8 | 34.2 | 19.4 | 57.9 | 3.9 | 201.4 | 13.9 | 60.8 | 47.7 | 29.5 | 60.8 | 49.5 | 41.6 | 68.2 | 147.4 | 66 | 70.9 | 67.9 | 55.2 | 301.1 | 243 | 277.5 | 66.2 | 220.7 | 56.9 | 91.2 | 66.4 | 241.9 | 242.9 | 182.8 | 291.3 | 227.8 | 305.9 | 314.2
3268.1 | 3029.1 | -6.3 | 0 | 0 | 220.6 | 201.1 | 184.3 | 180 | 216.8 | 34.2 | 19.4 | 57.8 | 4.1 | 209.5 | 14.8 | 60.8 | 47.7 | 29.6 | 60.8 | 49.5 | 41.7 | 68.2 | 147.6 | 65.9 | 71.2 | 68 | 55.3 | 301.1 | 242.9 | 277.4 | 66.4 | 220.5 | 56.7 | 91.5 | 66.5 | 241.8 | 242.7 | 182.7 | 291.1 | 227.7 | 305.8 | 314.1
3269.1 | 3030.1 | -6.4 | 0 | 0 | 220.5 | 201.1 | 184.2 | 179.9 | 216.5 | 34.2 | 19.4 | 57.8 | 4 | 216.3 | 13 | 60.8 | 48.1 | 29.6 | 60.8 | 49.5 | 41.7 | 68.2 | 147.5 | 65.9 | 71.6 | 68 | 55.3 | 301 | 243 | 277.3 | 66.5 | 220.5 | 56.6 | 91.6 | 66.4 | 241.7 | 242.6 | 182.5 | 291 | 227.6 | 305.7 | 314
3270.1 | 3031.1 | -6.3 | 0 | 0 | 220.4 | 200.9 | 184.1 | 179.9 | 215.5 | 34.2 | 19.4 | 57.7 | 3.7 | 218.2 | 12.3 | 60.9 | 48.2 | 29.7 | 60.8 | 49.5 | 41.7 | 68.2 | 147.1 | 66.2 | 71.5 | 68 | 55.3 | 301 | 243.1 | 277.3 | 66.6 | 220.3 | 56.7 | 91.8 | 66.4 | 241.7 | 242.6 | 182.3 | 290.9 | 227.5 | 305.5 | 313.9
3271.1 | 3032.1 | -6.3 | 0 | 0 | 220.4 | 200.5 | 184.2 | 179.8 | 214.6 | 34.1 | 19.4 | 57.7 | 4.2 | 224.9 | 10.4 | 60.9 | 48 | 29.6 | 60.8 | 49.5 | 41.7 | 68.2 | 147.1 | 66 | 71.6 | 68.1 | 55.4 | 300.9 | 242.8 | 277.2 | 66.4 | 220.3 | 56.7 | 91.9 | 66.4 | 241.6 | 242.5 | 182.2 | 290.8 | 227.5 | 305.4 | 313.8
3272.1 | 3033.1 | -6.4 | 0 | 0 | 220.2 | 200.3 | 184.3 | 179.8 | 213.5 | 34.1 | 19.4 | 57.7 | 3.6 | 228.6 | 9.5 | 60.9 | 48.2 | 29.6 | 60.8 | 49.5 | 41.7 | 68.2 | 147.3 | 66.2 | 71.5 | 68.1 | 55.4 | 300.8 | 242.6 | 277 | 66.4 | 220.2 | 56.4 | 91.9 | 66.4 | 241.5 | 242.4 | 182 | 290.6 | 227.4 | 305.2 | 313.6
3273.1 | 3034.1 | -6.3 | 0 | 0 | 220.1 | 200.2 | 184.3 | 179.7 | 213 | 34.1 | 19.4 | 57.7 | 3.6 | 236.6 | 8.7 | 60.9 | 48.5 | 29.8 | 60.8 | 49.5 | 41.6 | 68.2 | 147.3 | 66.2 | 71.5 | 68.1 | 55.2 | 300.7 | 242.7 | 276.9 | 66.4 | 220.2 | 56.4 | 92 | 66.1 | 241.4 | 242.4 | 182 | 290.5 | 227.3 | 305.1 | 313.5
3274.1 | 3035.1 | -6.2 | 0 | 0 | 220.1 | 200.2 | 184 | 179.7 | 213.3 | 34 | 19.4 | 57.7 | 3.5 | 236.5 | 7.8 | 60.9 | 48.7 | 29.8 | 60.8 | 49.5 | 41.6 | 68.2 | 147.3 | 65.9 | 71.5 | 68.1 | 55 | 300.7 | 243 | 276.8 | 66.1 | 220.2 | 56.6 | 91.9 | 65.9 | 241.3 | 242.3 | 182 | 290.3 | 227.2 | 305 | 313.4
3275.1 | 3036.1 | -6.3 | 0 | 0 | 219.9 | 200 | 183.9 | 179.8 | 213.7 | 34 | 19.4 | 57.7 | 4 | 225.4 | 9.5 | 60.9 | 49.3 | 30 | 60.8 | 49.5 | 41.6 | 68.2 | 147.4 | 65.7 | 71.5 | 68.2 | 55 | 300.6 | 242.7 | 276.7 | 65.8 | 220 | 56.5 | 91.8 | 66 | 241.2 | 242.2 | 182 | 290.2 | 227.1 | 304.8 | 313.2
3276.1 | 3037.1 | -6.3 | 0 | 0 | 219.8 | 199.9 | 183.8 | 179.7 | 213.3 | 34 | 19.4 | 57.6 | 3.9 | 245.7 | 9.3 | 60.9 | 49.4 | 30.2 | 60.8 | 49.5 | 41.7 | 68.1 | 147.1 | 65.2 | 71.4 | 68.2 | 54.9 | 300.6 | 242.5 | 276.7 | 65.9 | 220.1 | 56.3 | 91.8 | 66.2 | 241.1 | 242.1 | 181.9 | 290.1 | 227 | 304.7 | 313.1
3277.1 | 3038.1 | -6.3 | 0 | 0 | 219.6 | 199.7 | 183.7 | 179.5 | 212.8 | 34 | 19.4 | 57.5 | 4.5 | 242.6 | 10.2 | 61 | 48.8 | 30.3 | 60.8 | 49.5 | 41.6 | 68.1 | 147.1 | 64.7 | 71.8 | 68.2 | 54.9 | 300.6 | 242.9 | 276.6 | 66 | 220.2 | 56.4 | 91.8 | 66.3 | 241.1 | 242 | 181.8 | 289.9 | 226.9 | 304.6 | 313
3278.1 | 3039.1 | -6.4 | 0 | 0 | 219.3 | 199.6 | 183.6 | 179.5 | 212.2 | 34 | 19.4 | 57.5 | 4.1 | 249.1 | 12.3 | 61 | 48.3 | 30.3 | 60.9 | 49.5 | 41.5 | 68.1 | 147.1 | 64.3 | 71.9 | 68.3 | 54.8 | 300.5 | 243.9 | 276.5 | 66.2 | 220.3 | 56.5 | 91.9 | 66.1 | 241 | 241.8 | 181.8 | 289.8 | 226.8 | 304.4 | 312.8
3279.1 | 3040.1 | -6.4 | 0 | 0 | 219 | 199.5 | 183.4 | 179.4 | 211.9 | 34 | 19.4 | 57.6 | 3.9 | 249.6 | 11.6 | 61 | 48.8 | 30.3 | 60.9 | 49.5 | 41.5 | 68.1 | 147.1 | 64.2 | 71.9 | 68.3 | 54.8 | 300.4 | 243.7 | 276.4 | 66.2 | 220.3 | 56.6 | 92.1 | 66.1 | 240.9 | 241.6 | 181.7 | 289.7 | 226.7 | 304.3 | 312.7
3280.1 | 3041.1 | -6.4 | 0 | 0 | 218.6 | 199.3 | 183.2 | 179.2 | 211.8 | 34 | 19.4 | 57.6 | 3.7 | 244.9 | 10.7 | 61 | 49.6 | 30.3 | 60.9 | 49.5 | 41.4 | 68.1 | 147.2 | 64.3 | 71.7 | 68.3 | 54.8 | 300.4 | 243.7 | 276.2 | 66.1 | 220.5 | 56.7 | 92.2 | 66.4 | 240.8 | 241.5 | 181.5 | 289.5 | 226.6 | 304.2 | 312.6
3281.1 | 3042.1 | -6.4 | 0 | 0 | 218.4 | 199 | 183.1 | 179.1 | 212 | 34 | 19.4 | 57.6 | 4.1 | 234.4 | 8.3 | 61 | 50.1 | 30.2 | 60.9 | 49.6 | 41.4 | 68.1 | 147.4 | 64.4 | 71.4 | 68.3 | 54.8 | 300.4 | 243.5 | 276.1 | 66.1 | 220.8 | 56.8 | 92.5 | 66.5 | 240.7 | 241.4 | 181.3 | 289.4 | 226.5 | 304 | 312.5
3282.1 | 3043.1 | -6.4 | 0 | 0 | 218.4 | 198.7 | 183.2 | 179.1 | 212.5 | 34 | 19.4 | 57.4 | 4.2 | 245.1 | 6.7 | 61 | 50.2 | 30.1 | 60.9 | 49.6 | 41.4 | 68.1 | 147.6 | 64.6 | 71.6 | 68.4 | 54.9 | 300.3 | 243.8 | 276.1 | 66 | 220.9 | 56.9 | 92.6 | 66.4 | 240.6 | 241.3 | 181.2 | 289.2 | 226.4 | 303.9 | 312.3
3283.1 | 3044.1 | -6.4 | 0 | 0 | 218.3 | 198.3 | 183.4 | 179.1 | 212.7 | 34 | 19.4 | 57.3 | 3.9 | 233.5 | 6.3 | 61.1 | 49.4 | 30.1 | 60.9 | 49.6 | 41.4 | 68.1 | 147.4 | 64.8 | 71.5 | 68.4 | 55 | 300.2 | 243.4 | 276 | 65.8 | 221.1 | 57 | 92.7 | 66.4 | 240.5 | 241.2 | 181.1 | 289.1 | 226.3 | 303.7 | 312.2
3284.1 | 3045.1 | -6.4 | 0 | 0 | 218.2 | 197.8 | 183.5 | 179.2 | 213 | 34 | 19.4 | 57.3 | 4.2 | 226.7 | 7 | 61.1 | 49.1 | 30 | 60.9 | 49.6 | 41.3 | 68 | 147.4 | 64.9 | 71.9 | 68.4 | 55.1 | 300 | 243.3 | 275.9 | 65.8 | 221.4 | 57.1 | 92.8 | 66.4 | 240.4 | 241.1 | 181 | 289 | 226.2 | 303.6 | 312.1
3285.1 | 3046.1 | -6.4 | 0 | 0 | 218.3 | 197.4 | 183.4 | 179.1 | 213.3 | 33.9 | 19.4 | 57.3 | 3.7 | 235.7 | 6.3 | 61.1 | 48.6 | 30 | 60.9 | 49.6 | 41.3 | 68 | 147.2 | 65.3 | 71.8 | 68.4 | 55.1 | 299.9 | 243.1 | 275.8 | 65.5 | 221.5 | 57.2 | 92.8 | 66.2 | 240.4 | 241 | 180.8 | 288.8 | 226.1 | 303.5 | 311.9
3286.1 | 3047.1 | -6.4 | 0 | 0 | 218.5 | 197.1 | 183.4 | 178.9 | 213.6 | 33.9 | 19.4 | 57.2 | 3.6 | 231.6 | 6.6 | 61.1 | 48.7 | 30 | 60.9 | 49.6 | 41.3 | 68 | 146.7 | 65.7 | 71.9 | 68.5 | 55.1 | 299.8 | 243 | 275.7 | 65.5 | 221.5 | 57.1 | 92.9 | 66.1 | 240.3 | 240.8 | 180.7 | 288.7 | 226 | 303.3 | 311.8
3287.1 | 3048.1 | -6.3 | 0 | 0 | 218.5 | 197.2 | 183.1 | 178.9 | 213.8 | 33.9 | 19.4 | 57.2 | 3 | 233.2 | 9.7 | 61.1 | 49.1 | 30 | 60.9 | 49.6 | 41.3 | 68 | 146.5 | 66 | 72.2 | 68.5 | 54.9 | 299.8 | 242.9 | 275.6 | 65.7 | 221.6 | 57.2 | 92.9 | 66.3 | 240.2 | 240.6 | 180.6 | 288.6 | 225.9 | 303.2 | 311.7
3288.1 | 3049.1 | -6.4 | 0 | 0 | 218.4 | 197.3 | 182.9 | 178.9 | 214.1 | 33.9 | 19.4 | 57.3 | 3.2 | 233 | 9.4 | 61.1 | 48.9 | 30 | 61 | 49.6 | 41.3 | 68 | 146.3 | 66.1 | 72.4 | 68.5 | 55 | 299.7 | 243 | 275.5 | 65.6 | 221.7 | 57.2 | 93.1 | 66.3 | 240.1 | 240.5 | 180.5 | 288.4 | 225.8 | 303.1 | 311.6
3289.1 | 3050.1 | -6.4 | 0 | 0 | 218.3 | 197.3 | 182.6 | 178.8 | 214.3 | 33.8 | 19.4 | 57.4 | 3.8 | 203.7 | 11.3 | 61.2 | 48.6 | 29.8 | 61 | 49.6 | 41.3 | 68 | 146.2 | 66.3 | 72.4 | 68.5 | 55 | 299.6 | 243 | 275.4 | 65.5 | 221.6 | 57.2 | 93.2 | 66.2 | 240 | 240.3 | 180.4 | 288.3 | 225.7 | 302.9 | 311.4
3290.1 | 3051.1 | -6.4 | 0 | 0 | 218.1 | 197.4 | 182.4 | 178.6 | 214.4 | 33.9 | 19.4 | 57.4 | 4.1 | 196.6 | 12.9 | 61.2 | 48.8 | 29.7 | 61 | 49.6 | 41.3 | 67.9 | 146.2 | 66.5 | 72.3 | 68.6 | 54.9 | 299.6 | 242.8 | 275.3 | 65.4 | 221.6 | 57.1 | 93.2 | 66.2 | 239.9 | 240.2 | 180.3 | 288.1 | 225.6 | 302.8 | 311.3
3291.1 | 3052.1 | -6.4 | 0 | 0 | 218 | 197.6 | 182.3 | 178.5 | 214.3 | 33.9 | 19.4 | 57.3 | 4.5 | 218.4 | 11.7 | 61.2 | 49.1 | 29.6 | 61 | 49.6 | 41.3 | 67.9 | 146.2 | 66.7 | 72.3 | 68.6 | 54.9 | 299.6 | 242.8 | 275.2 | 65.5 | 221.5 | 57.4 | 93.2 | 65.9 | 239.8 | 239.9 | 180.1 | 288 | 225.5 | 302.7 | 311.2
3292.1 | 3053.1 | -6.4 | 0 | 0 | 218.1 | 197.6 | 182.2 | 178.2 | 214.4 | 33.8 | 19.4 | 57.3 | 3.9 | 204.9 | 9.9 | 61.2 | 48.9 | 29.6 | 61 | 49.6 | 41.3 | 67.9 | 145.8 | 67 | 72.3 | 68.6 | 54.8 | 299.5 | 243.1 | 275.1 | 65.6 | 221.2 | 57.3 | 93.3 | 66 | 239.7 | 239.8 | 180 | 287.9 | 225.5 | 302.5 | 311.1
3293.1 | 3054.1 | -6.4 | 0 | 0 | 217.8 | 197.6 | 182.1 | 178 | 214.6 | 33.8 | 19.5 | 57.3 | 3.7 | 210.2 | 10.1 | 61.2 | 48.5 | 29.6 | 61 | 49.6 | 41.3 | 67.9 | 145.7 | 67.1 | 72.3 | 68.6 | 54.7 | 299.5 | 242.9 | 275 | 65.3 | 221 | 57.1 | 93.5 | 66.1 | 239.6 | 239.7 | 179.9 | 287.7 | 225.4 | 302.4 | 310.9
3294.1 | 3055.1 | -6.4 | 0 | 0 | 217.6 | 197.3 | 182.1 | 177.8 | 214.6 | 33.7 | 19.5 | 57.3 | 3.7 | 240.9 | 8.7 | 61.2 | 49.3 | 29.6 | 61 | 49.6 | 41.3 | 67.9 | 145.3 | 67.1 | 72.4 | 68.7 | 54.8 | 299.4 | 242.9 | 274.9 | 65.3 | 220.6 | 56.9 | 93.4 | 66 | 239.6 | 239.7 | 179.8 | 287.6 | 225.3 | 302.3 | 310.8
3295.1 | 3056.1 | -6.4 | 0 | 0 | 217.4 | 197.1 | 182 | 177.6 | 213.7 | 33.7 | 19.5 | 57.3 | 4.1 | 220 | 7.6 | 61.2 | 49.8 | 29.7 | 61 | 49.6 | 41.3 | 67.9 | 145.4 | 66.7 | 72.3 | 68.7 | 54.8 | 299.3 | 242.9 | 274.8 | 65.4 | 220.4 | 57.2 | 93.6 | 66.1 | 239.5 | 239.7 | 179.7 | 287.5 | 225.2 | 302.1 | 310.7
3296.1 | 3057.1 | -6.3 | 0 | 0 | 217.4 | 197 | 181.7 | 177.5 | 212.6 | 33.7 | 19.5 | 57.3 | 4 | 207 | 8.3 | 61.2 | 49.5 | 29.8 | 61 | 49.6 | 41.3 | 67.8 | 145.3 | 66.2 | 72.6 | 68.7 | 54.7 | 299.2 | 243.1 | 274.7 | 65.5 | 220.4 | 57.1 | 93.8 | 66.2 | 239.4 | 239.5 | 179.6 | 287.3 | 225.1 | 302 | 310.5
3297.1 | 3058.1 | -6.3 | 0 | 0 | 217.1 | 197 | 181.7 | 177.4 | 212 | 33.6 | 19.5 | 57.3 | 4.2 | 214.8 | 10 | 61.3 | 48.9 | 29.9 | 61 | 49.6 | 41.3 | 67.8 | 145 | 65.6 | 72.5 | 68.7 | 54.8 | 299.1 | 243.1 | 274.6 | 65.6 | 220.4 | 57.3 | 94 | 66.2 | 239.3 | 239.4 | 179.5 | 287.2 | 225 | 301.9 | 310.4
3298.1 | 3059.1 | -6.3 | 0 | 0 | 217 | 196.9 | 181.7 | 177.2 | 212.1 | 33.6 | 19.5 | 57.3 | 4.3 | 226.2 | 9.3 | 61.3 | 48.8 | 29.9 | 61 | 49.6 | 41.2 | 67.8 | 144.7 | 65 | 72.6 | 68.8 | 54.8 | 299.1 | 243 | 274.5 | 65.5 | 220.2 | 57 | 94.2 | 66.3 | 239.2 | 239.3 | 179.4 | 287.1 | 224.9 | 301.7 | 310.3
3299.1 | 3060.1 | -6.4 | 0 | 0 | 216.7 | 196.8 | 181.8 | 177.3 | 211.5 | 33.6 | 19.5 | 57.2 | 4.7 | 196 | 11.7 | 61.3 | 48.6 | 29.9 | 61 | 49.6 | 41.2 | 67.8 | 145.1 | 65.1 | 72.7 | 68.8 | 54.8 | 299.1 | 243.1 | 274.4 | 65.4 | 220.2 | 56.7 | 94.5 | 66 | 239.1 | 239.3 | 179.3 | 286.9 | 224.8 | 301.6 | 310.2
3300.1 | 3061.1 | -6.4 | 0 | 0 | 216.6 | 196.7 | 181.6 | 177.3 | 211.3 | 33.6 | 19.5 | 57.3 | 3.9 | 195.4 | 12.6 | 61.3 | 47.8 | 29.9 | 61 | 49.6 | 41.2 | 67.8 | 145.1 | 64.9 | 72.6 | 68.8 | 54.8 | 299 | 243.2 | 274.3 | 65.2 | 220.2 | 56.5 | 94.6 | 65.8 | 239 | 239.2 | 179.2 | 286.8 | 224.7 | 301.5 | 310
3301.1 | 3062.1 | -6.4 | 0 | 0 | 216.3 | 196.7 | 181.5 | 177.3 | 211 | 33.6 | 19.5 | 57.3 | 3.7 | 211.5 | 12.5 | 61.3 | 48 | 30 | 61.1 | 49.6 | 41.2 | 67.8 | 144.9 | 64.7 | 72.7 | 68.8 | 54.7 | 299 | 243.1 | 274.2 | 65.1 | 220.1 | 56.5 | 94.5 | 65.6 | 239 | 239.1 | 179.1 | 286.6 | 224.6 | 301.3 | 309.9
3302.1 | 3063.1 | -6.4 | 0 | 0 | 215.9 | 196.6 | 181.3 | 177.3 | 210.6 | 33.7 | 19.5 | 57.3 | 4.1 | 230.9 | 11.2 | 61.3 | 48 | 30 | 61.1 | 49.6 | 41.2 | 67.8 | 145.1 | 64.4 | 72.6 | 68.9 | 54.6 | 298.9 | 242.7 | 274.1 | 65.3 | 220.2 | 56.3 | 94.7 | 65.9 | 238.9 | 239 | 178.9 | 286.5 | 224.6 | 301.2 | 309.8
3303.1 | 3064.1 | -6.3 | 0 | 0 | 215.8 | 196.3 | 181.2 | 177.3 | 210.3 | 33.7 | 19.5 | 57.3 | 4.3 | 214.5 | 9.2 | 61.3 | 47.7 | 29.8 | 61.1 | 49.6 | 41.2 | 67.8 | 144.8 | 64.2 | 72.8 | 68.9 | 54.6 | 298.8 | 242.7 | 274 | 65.3 | 220.2 | 56.3 | 94.9 | 65.6 | 238.8 | 238.9 | 178.9 | 286.4 | 224.5 | 301.1 | 309.6
3304.1 | 3065.1 | -6.4 | 0 | 0 | 215.8 | 196 | 181.1 | 177.1 | 210.2 | 33.7 | 19.5 | 57.3 | 4.4 | 224.6 | 7.6 | 61.3 | 47.2 | 29.8 | 61.1 | 49.6 | 41.2 | 67.8 | 144.5 | 64.3 | 72.9 | 68.9 | 54.7 | 298.8 | 242.7 | 273.9 | 65.3 | 220.2 | 56.3 | 95.1 | 65.7 | 238.7 | 238.7 | 178.8 | 286.2 | 224.4 | 300.9 | 309.5
3305.1 | 3066.1 | -6.4 | 0 | 0 | 215.9 | 195.9 | 181.1 | 176.9 | 210.1 | 33.7 | 19.5 | 57.2 | 4.2 | 232.6 | 5.6 | 61.4 | 46.5 | 29.8 | 61.1 | 49.6 | 41.1 | 67.7 | 144.6 | 64.4 | 73.1 | 68.9 | 54.7 | 298.7 | 242.3 | 273.8 | 65.2 | 220.2 | 56.3 | 95.3 | 65.5 | 238.6 | 238.6 | 178.6 | 286.1 | 224.3 | 300.8 | 309.4
3306.1 | 3067.1 | -6.4 | 0 | 0 | 215.9 | 195.9 | 180.9 | 176.7 | 210.2 | 33.7 | 19.5 | 57.2 | 4.4 | 223.3 | 4.9 | 61.4 | 46.2 | 29.7 | 61.1 | 49.7 | 41.1 | 67.7 | 144.7 | 64.3 | 73 | 69 | 54.8 | 298.6 | 241.9 | 273.7 | 65.3 | 220 | 56.3 | 95.4 | 65.7 | 238.5 | 238.6 | 178.5 | 286 | 224.2 | 300.7 | 309.3
3307.1 | 3068.1 | -6.4 | 0 | 0 | 215.9 | 196 | 180.9 | 176.7 | 210.1 | 33.6 | 19.5 | 57.2 | 4.6 | 224 | 5 | 61.4 | 46.6 | 29.7 | 61.1 | 49.6 | 41 | 67.8 | 144.6 | 64.4 | 72.8 | 69 | 54.6 | 298.5 | 241.8 | 273.6 | 65.3 | 219.9 | 56.3 | 95.7 | 65.9 | 238.4 | 238.4 | 178.4 | 285.8 | 224.1 | 300.5 | 309.2
3308.1 | 3069.1 | -6.4 | 0 | 0 | 215.7 | 195.9 | 180.8 | 176.8 | 209.8 | 33.6 | 19.5 | 57.2 | 3.9 | 228.1 | 5.3 | 61.4 | 46.7 | 29.7 | 61.1 | 49.7 | 41 | 67.7 | 144.3 | 64.4 | 73 | 69 | 54.6 | 298.4 | 241.9 | 273.6 | 65.2 | 219.9 | 56.5 | 95.9 | 65.8 | 238.3 | 238.3 | 178.3 | 285.7 | 224 | 300.4 | 309
3309.1 | 3070.1 | -6.3 | 0 | 0 | 215.6 | 195.9 | 180.6 | 176.9 | 209.6 | 33.6 | 19.5 | 57.2 | 3.8 | 231.5 | 5.7 | 61.4 | 46.9 | 29.7 | 61.1 | 49.7 | 41 | 67.7 | 143.8 | 64.2 | 73 | 69 | 54.6 | 298.3 | 241.9 | 273.5 | 65.2 | 219.9 | 56.5 | 96 | 65.5 | 238.3 | 238.1 | 178.2 | 285.5 | 223.9 | 300.3 | 308.9
3310.1 | 3071.1 | -6.2 | 0 | 0 | 215.5 | 195.8 | 180.4 | 177 | 209.8 | 33.6 | 19.5 | 57.2 | 4 | 244.3 | 7 | 61.4 | 46.7 | 29.7 | 61.1 | 49.7 | 40.9 | 67.7 | 144 | 64 | 72.9 | 69 | 54.7 | 298.3 | 242.5 | 273.4 | 65.1 | 220.1 | 56.6 | 96.1 | 65.7 | 238.2 | 238 | 178.1 | 285.4 | 223.8 | 300.1 | 308.8
3311.1 | 3072.1 | -6.3 | 0 | 0 | 215.4 | 195.8 | 180.2 | 177 | 210.1 | 33.6 | 19.5 | 57.2 | 3.8 | 218.3 | 7.1 | 61.4 | 47.3 | 29.7 | 61.1 | 49.7 | 40.9 | 67.7 | 144 | 63.9 | 72.7 | 69.1 | 54.8 | 298.3 | 242.3 | 273.3 | 65 | 220 | 56.7 | 96.2 | 65.9 | 238.1 | 237.8 | 177.9 | 285.3 | 223.7 | 300 | 308.6
3312.1 | 3073.1 | -6.3 | 0 | 0 | 215.1 | 195.6 | 179.9 | 176.9 | 209.8 | 33.6 | 19.5 | 57.1 | 4.2 | 227.3 | 7.3 | 61.5 | 47.9 | 29.7 | 61.1 | 49.7 | 40.8 | 67.7 | 143.9 | 64 | 73 | 69.1 | 54.9 | 298.2 | 242 | 273.2 | 64.9 | 219.9 | 56.8 | 96.2 | 65.9 | 238 | 237.8 | 177.8 | 285.1 | 223.6 | 299.9 | 308.5
3313.1 | 3074.1 | -6.4 | 0 | 0 | 215 | 195.3 | 179.9 | 176.9 | 209 | 33.6 | 19.5 | 57.1 | 4.5 | 199.7 | 6.9 | 61.5 | 48 | 29.6 | 61.1 | 49.7 | 40.8 | 67.7 | 143.9 | 64.3 | 72.8 | 69.1 | 54.8 | 298.1 | 241.6 | 273.1 | 64.9 | 220 | 56.9 | 96.3 | 65.7 | 237.9 | 237.7 | 177.7 | 285 | 223.5 | 299.7 | 308.4
3314.1 | 3075.1 | -6.4 | 0 | 0 | 214.8 | 195.1 | 179.6 | 176.6 | 208.7 | 33.6 | 19.5 | 57.1 | 4.2 | 212.6 | 6.9 | 61.5 | 48.7 | 29.5 | 61.1 | 49.7 | 40.8 | 67.7 | 144 | 64.7 | 72.5 | 69.1 | 54.7 | 298 | 241.5 | 273 | 65.1 | 220 | 56.9 | 96.4 | 65.9 | 237.8 | 237.5 | 177.6 | 284.9 | 223.4 | 299.6 | 308.3
3315.1 | 3076.1 | -6.4 | 0 | 0 | 214.6 | 195.1 | 179.5 | 176.3 | 208 | 33.6 | 19.5 | 57 | 3.6 | 213.6 | 8.5 | 61.5 | 49.9 | 29.5 | 61.2 | 49.7 | 40.8 | 67.7 | 144 | 64.7 | 72.6 | 69.1 | 54.8 | 298 | 241.5 | 272.9 | 65 | 220 | 56.9 | 96.4 | 66 | 237.7 | 237.3 | 177.5 | 284.7 | 223.3 | 299.5 | 308.1
3316.1 | 3077.1 | -6.3 | 0 | 0 | 214.3 | 195.1 | 179.5 | 176.1 | 207.9 | 33.6 | 19.5 | 57 | 3.3 | 237.5 | 7.2 | 61.5 | 50 | 29.6 | 61.2 | 49.7 | 40.8 | 67.6 | 143.7 | 64.7 | 72.7 | 69.2 | 54.7 | 297.9 | 241.8 | 272.8 | 64.9 | 220 | 57 | 96.6 | 66.1 | 237.6 | 237.1 | 177.5 | 284.6 | 223.2 | 299.4 | 308
3317.1 | 3078.1 | -6.3 | 0 | 0 | 214.2 | 195 | 179.4 | 175.9 | 207.9 | 33.6 | 19.5 | 57 | 3.3 | 231.7 | 6.9 | 61.5 | 50 | 29.6 | 61.2 | 49.7 | 40.8 | 67.6 | 143.5 | 64.7 | 72.6 | 69.2 | 54.7 | 297.8 | 241.8 | 272.7 | 64.8 | 220 | 57 | 96.7 | 65.7 | 237.5 | 237 | 177.3 | 284.4 | 223.2 | 299.2 | 307.9
3318.1 | 3079.1 | -6.3 | 0 | 0 | 214.2 | 194.9 | 179.3 | 175.6 | 208.3 | 33.6 | 19.5 | 56.9 | 3.5 | 230.8 | 6.6 | 61.5 | 49.1 | 29.4 | 61.2 | 49.7 | 40.8 | 67.6 | 143.2 | 64.7 | 72.8 | 69.2 | 54.8 | 297.8 | 241.5 | 272.6 | 64.9 | 219.9 | 57.2 | 96.8 | 65.5 | 237.5 | 236.9 | 177.3 | 284.3 | 223.1 | 299.1 | 307.8
3319.1 | 3080.1 | -6.3 | 0 | 0 | 214.2 | 194.8 | 179.1 | 175.3 | 208.8 | 33.6 | 19.5 | 56.9 | 3.7 | 228.2 | 6.2 | 61.6 | 48.5 | 29.2 | 61.2 | 49.7 | 40.8 | 67.6 | 143 | 64.9 | 73 | 69.2 | 54.8 | 297.7 | 241.4 | 272.5 | 64.8 | 219.8 | 57.4 | 96.8 | 65.9 | 237.4 | 236.9 | 177.2 | 284.2 | 223 | 299 | 307.6
3320.1 | 3081.1 | -6.3 | 0 | 0 | 214 | 194.7 | 179.2 | 175.2 | 209.2 | 33.6 | 19.5 | 56.9 | 3.5 | 213.4 | 7.4 | 61.6 | 47.9 | 29.2 | 61.2 | 49.7 | 40.7 | 67.6 | 143 | 64.6 | 73.1 | 69.2 | 54.8 | 297.7 | 241.6 | 272.4 | 64.7 | 219.6 | 57.5 | 96.9 | 65.9 | 237.3 | 236.8 | 177.1 | 284.1 | 222.9 | 298.8 | 307.5
3321.1 | 3082.1 | -6.3 | 0 | 0 | 213.8 | 194.7 | 179.4 | 175 | 209.5 | 33.6 | 19.5 | 56.8 | 3.6 | 208 | 10.8 | 61.6 | 47.5 | 29.1 | 61.2 | 49.7 | 40.7 | 67.6 | 143 | 64.2 | 73.2 | 69.3 | 54.7 | 297.6 | 241.7 | 272.3 | 64.5 | 219.3 | 57.7 | 96.9 | 65.9 | 237.2 | 236.7 | 177.1 | 283.9 | 222.8 | 298.7 | 307.4
3322.1 | 3083.1 | -6.2 | 0 | 0 | 213.7 | 194.7 | 179.4 | 175 | 209.9 | 33.6 | 19.5 | 56.7 | 3.5 | 210.2 | 10.9 | 61.6 | 47.9 | 29 | 61.2 | 49.7 | 40.7 | 67.6 | 143 | 64 | 73.3 | 69.3 | 54.6 | 297.6 | 241.6 | 272.2 | 64.5 | 219.1 | 57.7 | 96.7 | 65.9 | 237.1 | 236.7 | 177 | 283.8 | 222.7 | 298.6 | 307.2
3323.1 | 3084.1 | -6.1 | 0 | 0 | 213.7 | 194.7 | 179.1 | 175.1 | 209.9 | 33.5 | 19.5 | 56.7 | 3.4 | 224.1 | 8.8 | 61.6 | 48 | 29 | 61.2 | 49.7 | 40.8 | 67.5 | 143.2 | 63.8 | 73.1 | 69.3 | 54.5 | 297.5 | 241.7 | 272.1 | 64.4 | 219 | 58 | 96.6 | 65.9 | 237 | 236.6 | 176.9 | 283.6 | 222.6 | 298.4 | 307.1
3324.1 | 3085.1 | -6.1 | 0 | 0 | 213.6 | 194.5 | 178.9 | 175.1 | 209.7 | 33.5 | 19.5 | 56.7 | 3.9 | 235.8 | 6.4 | 61.6 | 47.9 | 29 | 61.2 | 49.7 | 40.8 | 67.6 | 143.2 | 63.6 | 72.8 | 69.3 | 54.6 | 297.5 | 241.9 | 272 | 64.4 | 219 | 58 | 96.6 | 65.8 | 236.9 | 236.5 | 177 | 283.5 | 222.5 | 298.3 | 307
3325.1 | 3086.1 | -6.2 | 0 | 0 | 213.3 | 194.4 | 178.7 | 174.9 | 209.3 | 33.5 | 19.5 | 56.7 | 3.8 | 274.9 | 5.1 | 61.6 | 48.4 | 29 | 61.2 | 49.7 | 40.8 | 67.6 | 142.8 | 63.9 | 73.3 | 69.4 | 54.7 | 297.4 | 241.8 | 271.9 | 64.4 | 219.1 | 57.9 | 96.7 | 65.5 | 236.9 | 236.4 | 176.9 | 283.4 | 222.4 | 298.2 | 306.9
3326.1 | 3087.1 | -6.2 | 0 | 0 | 213.1 | 194.3 | 178.8 | 174.9 | 208.4 | 33.5 | 19.5 | 56.7 | 4.2 | 232 | 4.5 | 61.6 | 48.6 | 28.9 | 61.2 | 49.7 | 40.8 | 67.5 | 142.6 | 63.7 | 73.4 | 69.4 | 54.7 | 297.3 | 241.7 | 271.8 | 64.4 | 219.1 | 57.7 | 96.8 | 65.5 | 236.8 | 236.2 | 176.8 | 283.3 | 222.3 | 298 | 306.7
3327.1 | 3088.1 | -6.3 | 0 | 0 | 212.9 | 194.1 | 178.9 | 174.9 | 207.8 | 33.5 | 19.5 | 56.7 | 4.6 | 206 | 6.4 | 61.6 | 48.6 | 28.9 | 61.3 | 49.7 | 40.8 | 67.5 | 142.7 | 63.2 | 73.3 | 69.4 | 54.7 | 297.3 | 242 | 271.7 | 64.3 | 219.3 | 57.7 | 96.9 | 65.8 | 236.7 | 236 | 176.6 | 283.1 | 222.2 | 297.9 | 306.6
3328.1 | 3089.1 | -6.3 | 0 | 0 | 212.6 | 193.7 | 178.8 | 174.7 | 207.3 | 33.5 | 19.5 | 56.8 | 3.9 | 214.7 | 9.8 | 61.7 | 48.2 | 28.8 | 61.3 | 49.7 | 40.8 | 67.5 | 142.9 | 63.4 | 73.3 | 69.4 | 54.7 | 297.2 | 242.1 | 271.6 | 64.4 | 219.5 | 57.7 | 96.9 | 66 | 236.6 | 235.9 | 176.5 | 283 | 222.1 | 297.8 | 306.5
3329.1 | 3090.1 | -6.2 | 0 | 0 | 212.5 | 193.2 | 178.5 | 174.6 | 206.6 | 33.5 | 19.5 | 56.8 | 4.2 | 222.6 | 9.7 | 61.7 | 48.1 | 28.7 | 61.3 | 49.7 | 40.8 | 67.5 | 143.1 | 63.7 | 73.5 | 69.4 | 54.6 | 297.2 | 242.2 | 271.6 | 64.6 | 219.5 | 57.7 | 97.2 | 65.9 | 236.5 | 235.8 | 176.3 | 282.9 | 222 | 297.6 | 306.4
3330.1 | 3091.1 | -6.2 | 0 | 0 | 212.5 | 192.8 | 178.4 | 174.6 | 206.8 | 33.5 | 19.5 | 56.8 | 3.8 | 212.2 | 8.2 | 61.7 | 47.8 | 28.7 | 61.3 | 49.7 | 40.9 | 67.4 | 143.2 | 63.7 | 73.7 | 69.4 | 54.4 | 297.1 | 242.4 | 271.4 | 64.6 | 219.6 | 57.5 | 97.4 | 65.7 | 236.4 | 235.6 | 176.1 | 282.7 | 221.9 | 297.5 | 306.3
3331.1 | 3092.1 | -6.4 | 0 | 0 | 212.5 | 192.6 | 178.1 | 174.7 | 206.9 | 33.4 | 19.6 | 56.8 | 3.9 | 255.1 | 6.6 | 61.7 | 48.3 | 28.7 | 61.3 | 49.7 | 40.9 | 67.4 | 143.4 | 63.7 | 73.9 | 69.5 | 54.4 | 297.1 | 242.4 | 271.4 | 64.5 | 219.7 | 57.4 | 97.4 | 65.4 | 236.3 | 235.4 | 176 | 282.6 | 221.8 | 297.4 | 306.1
3332.1 | 3093.1 | -6.4 | 0 | 0 | 212.5 | 192.4 | 177.8 | 174.6 | 207.1 | 33.4 | 19.6 | 56.8 | 4.4 | 248.7 | 6.4 | 61.7 | 48.2 | 28.8 | 61.3 | 49.7 | 40.9 | 67.4 | 143.5 | 63.7 | 74 | 69.5 | 54.3 | 297 | 242.3 | 271.3 | 64.6 | 219.8 | 57.4 | 97.5 | 65.4 | 236.2 | 235.2 | 175.9 | 282.5 | 221.7 | 297.2 | 306
3333.1 | 3094.1 | -6.3 | 0 | 0 | 212.3 | 192.2 | 177.8 | 174.6 | 207 | 33.4 | 19.6 | 56.8 | 3.9 | 240.2 | 7.5 | 61.7 | 48.8 | 28.9 | 61.3 | 49.7 | 41 | 67.5 | 143.3 | 63.7 | 73.9 | 69.5 | 54.3 | 296.9 | 242.2 | 271.2 | 64.6 | 219.9 | 57.3 | 97.8 | 65.7 | 236.2 | 235.1 | 175.8 | 282.3 | 221.7 | 297.1 | 305.9
3334.1 | 3095.1 | -6.3 | 0 | 0 | 212 | 191.8 | 178 | 174.5 | 207.1 | 33.4 | 19.6 | 56.8 | 4.1 | 217.2 | 7.4 | 61.7 | 49.4 | 28.9 | 61.3 | 49.7 | 41 | 67.5 | 143.3 | 63.6 | 73.8 | 69.5 | 54.3 | 296.9 | 242.1 | 271 | 64.4 | 219.9 | 57.1 | 97.8 | 65.6 | 236.1 | 235.1 | 175.7 | 282.2 | 221.6 | 297 | 305.8
3335.1 | 3096.1 | -6.3 | 0 | 0 | 211.8 | 191.6 | 177.8 | 174.4 | 206.7 | 33.3 | 19.6 | 56.8 | 4.3 | 252.4 | 7.1 | 61.7 | 49.6 | 28.7 | 61.3 | 49.7 | 41 | 67.4 | 143.4 | 63.2 | 73.8 | 69.5 | 54.4 | 296.8 | 242.1 | 271 | 64.2 | 220 | 57 | 97.7 | 65.5 | 236 | 234.9 | 175.8 | 282.1 | 221.5 | 296.9 | 305.6
3336.1 | 3097.1 | -6.3 | 0 | 0 | 211.7 | 191.6 | 177.5 | 174.1 | 206.1 | 33.3 | 19.6 | 56.9 | 4.7 | 226 | 7.6 | 61.8 | 49.7 | 28.7 | 61.3 | 49.7 | 41 | 67.4 | 143.1 | 63 | 73.7 | 69.6 | 54.5 | 296.7 | 242.2 | 270.9 | 64.2 | 220.1 | 57.7 | 97.7 | 65.4 | 235.9 | 234.8 | 175.7 | 282 | 221.4 | 296.7 | 305.5
3337.1 | 3098.1 | -6.3 | 0 | 0 | 211.6 | 191.7 | 177.5 | 173.8 | 205.8 | 33.3 | 19.6 | 56.8 | 5.8 | 217.1 | 7.5 | 61.8 | 49.7 | 28.7 | 61.3 | 49.7 | 41.1 | 67.4 | 143.1 | 63 | 73.7 | 69.6 | 54.7 | 296.7 | 242.1 | 270.8 | 64.2 | 220 | 57.9 | 97.6 | 65.3 | 235.8 | 234.7 | 175.6 | 281.8 | 221.3 | 296.6 | 305.4
3338.1 | 3099.1 | -6.4 | 0 | 0 | 211.4 | 191.8 | 177.2 | 173.5 | 205.4 | 33.2 | 19.6 | 56.7 | 6.1 | 198.5 | 6.1 | 61.8 | 49 | 28.8 | 61.3 | 49.7 | 41.1 | 67.4 | 143 | 63 | 73.7 | 69.6 | 54.8 | 296.6 | 241.9 | 270.7 | 64.2 | 220.1 | 57.9 | 97.6 | 65.5 | 235.7 | 234.5 | 175.5 | 281.7 | 221.2 | 296.5 | 305.3
3339.1 | 3100.1 | -6.4 | 0 | 0 | 211.2 | 191.9 | 177 | 173.5 | 205.5 | 33.2 | 19.6 | 56.7 | 5.9 | 250.1 | 5.8 | 61.8 | 48.7 | 28.9 | 61.3 | 49.7 | 41.1 | 67.4 | 143 | 63.1 | 73.8 | 69.6 | 54.8 | 296.5 | 241.9 | 270.6 | 64.3 | 220.2 | 58 | 97.8 | 65.4 | 235.6 | 234.4 | 175.3 | 281.5 | 221.1 | 296.4 | 305.1
3340.1 | 3101.1 | -6.5 | 0 | 0 | 211 | 191.9 | 176.8 | 173.4 | 206 | 33.2 | 19.6 | 56.6 | 5.5 | 234.8 | 7.6 | 61.8 | 49 | 29 | 61.3 | 49.7 | 41.1 | 67.4 | 143 | 63.3 | 73.8 | 69.6 | 54.9 | 296.4 | 242.1 | 270.5 | 64.2 | 220.3 | 57.8 | 97.9 | 65.2 | 235.5 | 234.2 | 175.2 | 281.4 | 221 | 296.2 | 305
3341.1 | 3102.1 | -6.6 | 0 | 0 | 210.8 | 191.9 | 176.6 | 173.3 | 206.6 | 33.2 | 19.6 | 56.6 | 5.9 | 232.3 | 8.3 | 61.8 | 49.6 | 29 | 61.3 | 49.7 | 41.1 | 67.4 | 143 | 63.5 | 74.1 | 69.6 | 55 | 296.4 | 242 | 270.4 | 64.2 | 219.9 | 58.2 | 97.9 | 65.2 | 235.4 | 234.1 | 175.1 | 281.3 | 220.9 | 296.1 | 304.9
3342.1 | 3103.1 | -6.6 | 0 | 0 | 210.6 | 191.9 | 176.7 | 173.2 | 207 | 33.1 | 19.6 | 56.5 | 6.6 | 231.6 | 8.4 | 61.8 | 49.6 | 28.8 | 61.3 | 49.7 | 41 | 67.4 | 143 | 63.8 | 74 | 69.6 | 55 | 296.3 | 242.1 | 270.3 | 64 | 219.5 | 58.3 | 97.9 | 65.3 | 235.4 | 234.1 | 174.9 | 281.2 | 220.8 | 296 | 304.8
3343.1 | 3104.1 | -6.6 | 0 | 0 | 210.5 | 191.9 | 176.7 | 173.1 | 207.4 | 33.2 | 19.6 | 56.4 | 5.7 | 209.8 | 9.1 | 61.8 | 49.5 | 28.8 | 61.3 | 49.7 | 41 | 67.4 | 142.9 | 64.1 | 73.9 | 69.7 | 55.1 | 296.3 | 242 | 270.2 | 64 | 219.2 | 58.4 | 97.8 | 65.3 | 235.3 | 234 | 174.7 | 281 | 220.7 | 295.9 | 304.6
3344.1 | 3105.1 | -6.7 | 0 | 0 | 210.5 | 191.9 | 176.5 | 173 | 207.1 | 33.2 | 19.6 | 56.3 | 6 | 215.1 | 12.5 | 61.8 | 48.9 | 28.8 | 61.3 | 49.7 | 41 | 67.4 | 142.9 | 64.3 | 73.9 | 69.7 | 55.1 | 296.2 | 242.1 | 270.1 | 63.9 | 219.2 | 58.8 | 97.8 | 65.2 | 235.2 | 234 | 174.6 | 280.9 | 220.6 | 295.7 | 304.5
3345.1 | 3106.1 | -6.7 | 0 | 0 | 210.4 | 191.9 | 176.2 | 173 | 206.7 | 33.2 | 19.6 | 56.3 | 5 | 226.2 | 13.8 | 61.8 | 49 | 28.8 | 61.4 | 49.7 | 41 | 67.4 | 142.7 | 64.5 | 74.2 | 69.7 | 55.1 | 296.2 | 242.1 | 270 | 63.9 | 219.3 | 58.7 | 97.7 | 65.4 | 235.1 | 234 | 174.5 | 280.8 | 220.5 | 295.6 | 304.4
3346.1 | 3107.1 | -6.7 | 0 | 0 | 210.3 | 191.8 | 176.2 | 173 | 206 | 33.2 | 19.6 | 56.3 | 4.5 | 251 | 11.2 | 61.8 | 49 | 28.9 | 61.4 | 49.7 | 41 | 67.4 | 142.5 | 64.5 | 74 | 69.7 | 55 | 296 | 242.1 | 269.9 | 63.9 | 219.5 | 58.4 | 97.7 | 65.6 | 235 | 233.8 | 174.4 | 280.6 | 220.4 | 295.5 | 304.3
3347.1 | 3108.1 | -6.7 | 0 | 0 | 210.2 | 191.8 | 176.2 | 172.7 | 206.1 | 33.2 | 19.6 | 56.3 | 4.8 | 238.4 | 12.7 | 61.9 | 48.6 | 28.8 | 61.4 | 49.7 | 41.1 | 67.3 | 142.1 | 65 | 74.1 | 69.7 | 55 | 296 | 242.3 | 269.8 | 64 | 219.6 | 58.2 | 97.8 | 65.5 | 234.9 | 233.7 | 174.3 | 280.5 | 220.3 | 295.4 | 304.1
3348.1 | 3109.1 | -6.5 | 0 | 0 | 210.1 | 191.7 | 176.2 | 172.7 | 206.5 | 33.2 | 19.6 | 56.2 | 5.2 | 222.3 | 11.9 | 61.9 | 48.2 | 28.8 | 61.4 | 49.7 | 41 | 67.3 | 141.6 | 65.2 | 74 | 69.7 | 55.1 | 295.9 | 242.5 | 269.7 | 63.8 | 219.5 | 58.3 | 97.7 | 65.1 | 234.8 | 233.5 | 174.3 | 280.4 | 220.2 | 295.2 | 304
3349.1 | 3110.1 | -6.4 | 0 | 0 | 210.1 | 191.6 | 176.2 | 172.6 | 206.8 | 33.2 | 19.6 | 56.2 | 5.5 | 239.3 | 10.2 | 61.9 | 47.3 | 28.7 | 61.4 | 49.7 | 41 | 67.3 | 141.6 | 65.4 | 74 | 69.7 | 55 | 295.8 | 242.6 | 269.6 | 63.7 | 219.4 | 58.5 | 97.5 | 65 | 234.8 | 233.4 | 174.2 | 280.3 | 220.1 | 295.1 | 303.9
3350.1 | 3111.1 | -6.3 | 0 | 0 | 210 | 191.4 | 176.2 | 172.6 | 206.8 | 33.2 | 19.6 | 56.2 | 4.7 | 237.4 | 12.8 | 61.9 | 47.3 | 28.7 | 61.4 | 49.8 | 41.1 | 67.2 | 141.7 | 65.4 | 74.1 | 69.8 | 54.9 | 295.8 | 242.8 | 269.5 | 63.6 | 219.5 | 58.8 | 97.4 | 64.9 | 234.7 | 233.3 | 174.1 | 280.1 | 220 | 295 | 303.8
3351.1 | 3112.1 | -6.3 | 0 | 0 | 209.8 | 191.4 | 176.1 | 172.5 | 207 | 33.2 | 19.6 | 56.1 | 4.3 | 242.5 | 12.7 | 61.9 | 47.2 | 28.7 | 61.4 | 49.8 | 41.1 | 67.3 | 141.3 | 65 | 74.1 | 69.8 | 54.8 | 295.7 | 243 | 269.4 | 63.6 | 219.6 | 58.6 | 97.4 | 64.9 | 234.6 | 233.2 | 173.9 | 280 | 219.9 | 294.8 | 303.7
3352.1 | 3113.1 | -6.3 | 0 | 0 | 209.8 | 191.5 | 175.8 | 172.4 | 207.3 | 33.2 | 19.6 | 56.1 | 4.2 | 241 | 10.4 | 61.9 | 47.1 | 28.7 | 61.4 | 49.8 | 41.2 | 67.2 | 141.4 | 64.8 | 74.4 | 69.8 | 54.8 | 295.7 | 242.8 | 269.3 | 63.5 | 219.4 | 58.7 | 97.4 | 64.6 | 234.5 | 233.2 | 173.8 | 279.9 | 219.8 | 294.7 | 303.5
3353.1 | 3114.1 | -6.3 | 0 | 0 | 209.8 | 191.4 | 175.8 | 172.1 | 207 | 33.1 | 19.6 | 56.1 | 3.8 | 219.6 | 9.5 | 61.9 | 47.6 | 28.8 | 61.4 | 49.8 | 41.2 | 67.2 | 141.6 | 64.5 | 74.1 | 69.8 | 54.8 | 295.6 | 242.6 | 269.3 | 63.5 | 219.4 | 58.8 | 97.3 | 64.8 | 234.4 | 233.1 | 173.7 | 279.7 | 219.7 | 294.6 | 303.4
3354.1 | 3115.1 | -6.3 | 0 | 0 | 209.6 | 191.2 | 175.6 | 171.9 | 206.2 | 33.1 | 19.6 | 56.1 | 3.3 | 235.9 | 7.7 | 61.9 | 47.6 | 28.8 | 61.4 | 49.8 | 41.1 | 67.2 | 141.3 | 64.2 | 74.4 | 69.8 | 55 | 295.5 | 242.6 | 269.2 | 63.5 | 219.4 | 58.9 | 97.3 | 64.8 | 234.3 | 233 | 173.6 | 279.6 | 219.6 | 294.5 | 303.3
3355.1 | 3116.1 | -6.3 | 0 | 0 | 209.4 | 191 | 175.4 | 171.8 | 205.8 | 33 | 19.6 | 56.1 | 3.2 | 202.2 | 10.9 | 61.9 | 46.7 | 28.7 | 61.4 | 49.8 | 41.1 | 67.2 | 141 | 64 | 74.5 | 69.8 | 54.9 | 295.4 | 242.7 | 269.1 | 63.6 | 219.5 | 59 | 97.3 | 64.7 | 234.2 | 232.8 | 173.5 | 279.5 | 219.5 | 294.3 | 303.2
3356.1 | 3117.1 | -6.3 | 0 | 0 | 209.2 | 190.8 | 175 | 171.6 | 205.6 | 33 | 19.6 | 56.1 | 3.2 | 201.9 | 12.5 | 61.9 | 46.5 | 28.6 | 61.4 | 49.8 | 41 | 67.2 | 140.8 | 63.9 | 74.6 | 69.8 | 55 | 295.4 | 242.6 | 269 | 63.5 | 219.7 | 59.2 | 97.3 | 65 | 234.1 | 232.8 | 173.4 | 279.4 | 219.5 | 294.2 | 303.1

## First Electrical Failures
SCDU-1 Location F XLPE cable | Time (s) | Offset Time (s) | C1 V5 | SCDU-3 Location G XLPE cable | Time (s) | Offset Time (s) | C3 V5
| 0 | -239 | 0.046856 |  | 0 | -239 | -0.019206
| 60 | -179 | 0.14424 |  | 60 | -179 | 0.078174
| 120 | -119 | 0.14424 |  | 120 | -119 | 0.17559
| 180 | -59 | 0.14424 |  | 180 | -59 | 0.078174
| 240 | 1 | 0.14424 |  | 240 | 1 | 0.17559
| 300 | 61 | 0.14424 |  | 300 | 61 | 0.17559
| 360 | 121 | 0.14424 |  | 360 | 121 | 0.17559
| 420 | 181 | 0.33904 |  | 420 | 181 | 0.17559
| 480 | 241 | 0.24166 |  | 480 | 241 | 0.27297
| 540 | 301 | 0.14424 |  | 540 | 301 | 0.27297
| 540.2 | 301.2 | 0.24166 |  | 540.2 | 301.2 | 0.17559
| 540.4 | 301.4 | 0.24166 |  | 540.4 | 301.4 | 0.17559
| 540.6 | 301.6 | 0.24166 |  | 540.6 | 301.6 | 0.17559
| 540.8 | 301.8 | 0.24166 |  | 540.8 | 301.8 | 0.27297
| 541 | 302 | 0.24166 |  | 541 | 302 | 0.17559
| 600 | 361 | 0.43642 |  | 600 | 361 | 0.27297
| 660 | 421 | 0.43642 |  | 660 | 421 | 0.27297
| 720 | 481 | 0.33904 |  | 720 | 481 | 0.27297
| 780 | 541 | 0.24166 |  | 780 | 541 | 0.27297
| 840 | 601 | 0.43642 |  | 840 | 601 | 0.27297
| 900 | 661 | 0.43642 |  | 900 | 661 | 0.37035
| 960 | 721 | 0.53384 |  | 960 | 721 | 0.27297
| 1020 | 781 | 0.43642 |  | 1020 | 781 | 0.27297
| 1080 | 841 | 0.53384 |  | 1080 | 841 | 0.27297
| 1140 | 901 | 0.43642 |  | 1140 | 901 | 0.37035
| 1200 | 961 | 0.33904 |  | 1200 | 961 | 0.27297
| 1260 | 1021 | 0.43642 |  | 1260 | 1021 | 0.078174
| 1320 | 1081 | 0.33904 |  | 1320 | 1081 | 0.37035
| 1380 | 1141 | 0.33904 |  | 1380 | 1141 | 0.37035
| 1390 | 1151 | 0.33904 |  | 1390 | 1151 | 0.37035
| 1400 | 1161 | 0.43642 |  | 1400 | 1161 | 0.37035
| 1410 | 1171 | 0.43642 |  | 1410 | 1171 | 0.37035
| 1420 | 1181 | 0.63122 |  | 1420 | 1181 | 0.37035
| 1430 | 1191 | 0.43642 |  | 1430 | 1191 | 0.46777
| 1440 | 1201 | 0.43642 |  | 1440 | 1201 | 0.37035
| 1450 | 1211 | 0.43642 |  | 1450 | 1211 | 0.46777
| 1460 | 1221 | 0.53384 |  | 1460 | 1221 | 0.37035
| 1470 | 1231 | 0.33904 |  | 1470 | 1231 | 0.27297
| 1480 | 1241 | 0.43642 |  | 1480 | 1241 | 0.37035
| 1490 | 1251 | 0.43642 |  | 1490 | 1251 | 0.37035
| 1500 | 1261 | 0.43642 |  | 1500 | 1261 | 0.46777
| 1510 | 1271 | 0.43642 |  | 1510 | 1271 | 0.46777
| 1520 | 1281 | 0.63122 |  | 1520 | 1281 | 0.27297
| 1530 | 1291 | 0.63122 |  | 1530 | 1291 | 0.37035
| 1540 | 1301 | 0.53384 |  | 1540 | 1301 | 0.37035
| 1550 | 1311 | 0.43642 |  | 1550 | 1311 | 0.37035
| 1560 | 1321 | 0.43642 |  | 1560 | 1321 | 0.46777
| 1570 | 1331 | 0.43642 |  | 1570 | 1331 | 0.46777
| 1580 | 1341 | 0.82602 |  | 1580 | 1341 | 0.37035
| 1590 | 1351 | 1.8 |  | 1590 | 1351 | 0.37035
| 1600 | 1361 | 2.7739 |  | 1600 | 1361 | 0.46777
| 1600.2 | 1361.2 | 3.0661 |  | 1600.2 | 1361.2 | 0.37035
| 1600.4 | 1361.4 | 3.4557 |  | 1600.4 | 1361.4 | 0.37035
| 1600.6 | 1361.6 | 4.4297 |  | 1600.6 | 1361.6 | 0.46777
| 1600.8 | 1361.8 | 3.7479 |  | 1600.8 | 1361.8 | 0.37035
| 1601 | 1362 | 3.5531 |  | 1601 | 1362 | 0.37035
| 1601.2 | 1362.2 | 5.8906 |  | 1601.2 | 1362.2 | 0.37035
| 1601.4 | 1362.4 | 4.0401 |  | 1601.4 | 1362.4 | 0.37035
| 1601.6 | 1362.6 | 2.7739 |  | 1601.6 | 1362.6 | 0.37035
| 1601.8 | 1362.8 | 2.4818 |  | 1601.8 | 1362.8 | 0.37035
| 1602 | 1363 | 2.5791 |  | 1602 | 1363 | 0.46777
| 1602.2 | 1363.2 | 2.7739 |  | 1602.2 | 1363.2 | 0.37035
| 1602.4 | 1363.4 | 2.7739 |  | 1602.4 | 1363.4 | 0.37035
| 1602.6 | 1363.6 | 2.9687 |  | 1602.6 | 1363.6 | 0.37035
| 1602.8 | 1363.8 | 2.8714 |  | 1602.8 | 1363.8 | 0.37035
| 1603 | 1364 | 2.8714 |  | 1603 | 1364 | 0.37035
| 1603.2 | 1364.2 | 2.8714 |  | 1603.2 | 1364.2 | 0.37035
| 1603.4 | 1364.4 | 2.8714 |  | 1603.4 | 1364.4 | 0.37035
| 1603.6 | 1364.6 | 2.7739 |  | 1603.6 | 1364.6 | 0.37035
| 1603.8 | 1364.8 | 2.8714 |  | 1603.8 | 1364.8 | 0.46777
| 1604 | 1365 | 2.8714 |  | 1604 | 1365 | 0.37035
| 1604.2 | 1365.2 | 3.0661 |  | 1604.2 | 1365.2 | 0.37035
| 1604.4 | 1365.4 | 3.4557 |  | 1604.4 | 1365.4 | 0.37035
| 1604.6 | 1365.6 | 4.3323 |  | 1604.6 | 1365.6 | 0.37035
| 1604.8 | 1365.8 | 4.3323 |  | 1604.8 | 1365.8 | 0.27297
| 1605 | 1366 | 4.0401 |  | 1605 | 1366 | 0.37035
| 1605.2 | 1366.2 | 3.8453 |  | 1605.2 | 1366.2 | 0.37035
| 1605.4 | 1366.4 | 3.8453 |  | 1605.4 | 1366.4 | 0.37035
| 1605.6 | 1366.6 | 3.9427 |  | 1605.6 | 1366.6 | 0.37035
| 1605.8 | 1366.8 | 4.6245 |  | 1605.8 | 1366.8 | 0.37035
| 1606 | 1367 | 4.3323 |  | 1606 | 1367 | 0.37035
| 1606.2 | 1367.2 | 5.6958 |  | 1606.2 | 1367.2 | 0.37035
| 1606.4 | 1367.4 | 5.4037 |  | 1606.4 | 1367.4 | 0.37035
| 1606.6 | 1367.6 | 5.8906 |  | 1606.6 | 1367.6 | 0.46777
| 1606.8 | 1367.8 | 6.8646 |  | 1606.8 | 1367.8 | 0.27297
| 1607 | 1368 | 7.936 |  | 1607 | 1368 | 0.37035
| 1607.2 | 1368.2 | 7.0594 |  | 1607.2 | 1368.2 | 0.37035
| 1607.4 | 1368.4 | 5.9881 |  | 1607.4 | 1368.4 | 0.37035
| 1607.6 | 1368.6 | 5.7933 |  | 1607.6 | 1368.6 | 0.27297
| 1607.8 | 1368.8 | 7.5464 |  | 1607.8 | 1368.8 | 0.27297
| 1608 | 1369 | 6.7672 |  | 1608 | 1369 | 0.37035
| 1608.2 | 1369.2 | 7.6438 |  | 1608.2 | 1369.2 | 0.17559
| 1608.4 | 1369.4 | 7.6438 |  | 1608.4 | 1369.4 | 0.37035
| 1608.6 | 1369.6 | 9.1047 |  | 1608.6 | 1369.6 | 0.37035
| 1608.8 | 1369.8 | 15.6303 |  | 1608.8 | 1369.8 | 0.37035
| 1609 | 1370 | 9.4943 |  | 1609 | 1370 | 0.37035
| 1609.2 | 1370.2 | 9.3969 |  | 1609.2 | 1370.2 | 0.37035
| 1609.4 | 1370.4 | 9.3969 |  | 1609.4 | 1370.4 | 0.37035
| 1609.6 | 1370.6 | 9.4943 |  | 1609.6 | 1370.6 | 0.46777
| 1609.8 | 1370.8 | 11.0527 |  | 1609.8 | 1370.8 | 0.27297
| 1610 | 1371 | 10.5657 |  | 1610 | 1371 | 0.37035
| 1610.2 | 1371.2 | 9.7865 |  | 1610.2 | 1371.2 | 0.37035
| 1610.4 | 1371.4 | 11.7344 |  | 1610.4 | 1371.4 | 0.37035
| 1610.6 | 1371.6 | 9.4943 |  | 1610.6 | 1371.6 | 0.27297
| 1610.8 | 1371.8 | 10.1761 |  | 1610.8 | 1371.8 | 0.37035
| 1611 | 1372 | 9.7865 |  | 1611 | 1372 | 0.37035
| 1611.2 | 1372.2 | 8.8125 |  | 1611.2 | 1372.2 | 0.37035
| 1611.4 | 1372.4 | 9.2995 |  | 1611.4 | 1372.4 | 0.37035
| 1611.6 | 1372.6 | 15.7277 |  | 1611.6 | 1372.6 | 0.46777
| 1611.8 | 1372.8 | 13.8771 |  | 1611.8 | 1372.8 | 0.37035
| 1612 | 1373 | 18.0652 |  | 1612 | 1373 | 0.27297
| 1612.2 | 1373.2 | 16.4095 |  | 1612.2 | 1373.2 | 0.37035
| 1612.4 | 1373.4 | 16.2147 |  | 1612.4 | 1373.4 | 0.27297
| 1612.6 | 1373.6 | 20.4027 |  | 1612.6 | 1373.6 | 0.37035
| 1612.8 | 1373.8 | 17.5782 |  | 1612.8 | 1373.8 | 0.37035
| 1613 | 1374 | 18.3574 |  | 1613 | 1374 | 0.37035
| 1613.2 | 1374.2 | 16.9938 |  | 1613.2 | 1374.2 | 0.46777
| 1613.4 | 1374.4 | 16.7991 |  | 1613.4 | 1374.4 | 0.37035
| 1613.6 | 1374.6 | 18.6496 |  | 1613.6 | 1374.6 | 0.37035
| 1613.8 | 1374.8 | 24.0064 |  | 1613.8 | 1374.8 | 0.37035
| 1614 | 1375 | 17.9678 |  | 1614 | 1375 | 0.27297
| 1614.2 | 1375.2 | 19.5262 |  | 1614.2 | 1375.2 | 0.37035
| 1614.4 | 1375.4 | 17.5782 |  | 1614.4 | 1375.4 | 0.27297
| 1614.6 | 1375.6 | 18.4548 |  | 1614.6 | 1375.6 | 0.37035
| 1614.8 | 1375.8 | 22.1559 |  | 1614.8 | 1375.8 | 0.37035
| 1615 | 1376 | 23.0324 |  | 1615 | 1376 | 0.37035
| 1615.2 | 1376.2 | 24.6882 |  | 1615.2 | 1376.2 | 0.37035
| 1615.4 | 1376.4 | 34.72 |  | 1615.4 | 1376.4 | 0.46777
| 1615.6 | 1376.6 | 35.8888 |  | 1615.6 | 1376.6 | 0.27297
| 1615.8 | 1376.8 | 28.9736 |  | 1615.8 | 1376.8 | 0.37035
| 1616 | 1377 | 25.8569 |  | 1616 | 1377 | 0.37035
| 1616.2 | 1377.2 | 30.9216 |  | 1616.2 | 1377.2 | 0.37035
| 1616.4 | 1377.4 | 47.6737 |  | 1616.4 | 1377.4 | 0.37035
| 1616.6 | 1377.6 | 117.1175 |  | 1616.6 | 1377.6 | 0.37035
| 1616.8 | 1377.8 | 123.156 |  | 1616.8 | 1377.8 | 0.37035
| 1617 | 1378 | 124.8118 |  | 1617 | 1378 | 0.37035
| 1617.2 | 1378.2 | 125.4936 |  | 1617.2 | 1378.2 | 0.37035
| 1617.4 | 1378.4 | 125.6884 |  | 1617.4 | 1378.4 | 0.37035
| 1617.6 | 1378.6 | 125.7858 |  | 1617.6 | 1378.6 | 0.46777
| 1617.8 | 1378.8 | 125.6884 |  | 1617.8 | 1378.8 | 0.46777
| 1618 | 1379 | 125.591 |  | 1618 | 1379 | 0.46777
| 1618.2 | 1379.2 | 125.6884 |  | 1618.2 | 1379.2 | 0.37035
| 1618.4 | 1379.4 | 125.6884 |  | 1618.4 | 1379.4 | 0.46777
| 1618.6 | 1379.6 | 125.6884 |  | 1618.6 | 1379.6 | 0.37035
| 1618.8 | 1379.8 | 125.2988 |  | 1618.8 | 1379.8 | 0.46777
| 1619 | 1380 | 125.4936 |  | 1619 | 1380 | 0.37035
| 1619.2 | 1380.2 | 125.6884 |  | 1619.2 | 1380.2 | 0.37035
| 1619.4 | 1380.4 | 125.6884 |  | 1619.4 | 1380.4 | 0.37035
| 1619.6 | 1380.6 | 126.3702 |  | 1619.6 | 1380.6 | 0.37035
| 1619.8 | 1380.8 | 126.4675 |  | 1619.8 | 1380.8 | 0.46777
| 1620 | 1381 | 126.4675 |  | 1620 | 1381 | 0.37035
| 1620.2 | 1381.2 | 126.5649 |  | 1620.2 | 1381.2 | 0.46777
| 1620.4 | 1381.4 | 126.5649 |  | 1620.4 | 1381.4 | 0.37035
| 1620.6 | 1381.6 | 125.9806 |  | 1620.6 | 1381.6 | 0.46777
| 1620.8 | 1381.8 | 126.0779 |  | 1620.8 | 1381.8 | 0.46777
| 1621 | 1382 | 126.1754 |  | 1621 | 1382 | 0.37035
| 1621.2 | 1382.2 | 126.1754 |  | 1621.2 | 1382.2 | 0.37035
| 1621.4 | 1382.4 | 126.1754 |  | 1621.4 | 1382.4 | 0.46777
| 1621.6 | 1382.6 | 126.2727 |  | 1621.6 | 1382.6 | 0.46777
| 1621.8 | 1382.8 | 126.2727 |  | 1621.8 | 1382.8 | 0.46777
| 1622 | 1383 | 126.1754 |  | 1622 | 1383 | 0.37035
| 1622.2 | 1383.2 | 126.1754 |  | 1622.2 | 1383.2 | 0.46777
| 1622.4 | 1383.4 | 126.0779 |  | 1622.4 | 1383.4 | 0.37035
| 1622.6 | 1383.6 | 126.1754 |  | 1622.6 | 1383.6 | 0.37035
| 1622.8 | 1383.8 | 126.0779 |  | 1622.8 | 1383.8 | 0.37035
| 1623 | 1384 | 125.9806 |  | 1623 | 1384 | 0.37035
| 1623.2 | 1384.2 | 125.9806 |  | 1623.2 | 1384.2 | 0.37035
| 1623.4 | 1384.4 | 125.9806 |  | 1623.4 | 1384.4 | 0.46777
| 1623.6 | 1384.6 | 125.9806 |  | 1623.6 | 1384.6 | 0.46777
| 1623.8 | 1384.8 | 125.8832 |  | 1623.8 | 1384.8 | 0.37035
| 1624 | 1385 | 125.8832 |  | 1624 | 1385 | 0.46777
| 1624.2 | 1385.2 | 126.0779 |  | 1624.2 | 1385.2 | 0.37035
| 1624.4 | 1385.4 | 125.8832 |  | 1624.4 | 1385.4 | 0.37035
| 1624.6 | 1385.6 | 125.7858 |  | 1624.6 | 1385.6 | 0.56516
| 1624.8 | 1385.8 | 125.7858 |  | 1624.8 | 1385.8 | 0.46777
| 1625 | 1386 | 125.6884 |  | 1625 | 1386 | 0.37035
| 1625.2 | 1386.2 | 125.7858 |  | 1625.2 | 1386.2 | 0.37035
| 1625.4 | 1386.4 | 125.7858 |  | 1625.4 | 1386.4 | 0.46777
| 1625.6 | 1386.6 | 125.8832 |  | 1625.6 | 1386.6 | 0.37035
| 1625.8 | 1386.8 | 125.7858 |  | 1625.8 | 1386.8 | 0.37035
| 1626 | 1387 | 125.6884 |  | 1626 | 1387 | 0.37035
| 1626.2 | 1387.2 | 125.7858 |  | 1626.2 | 1387.2 | 0.37035
| 1626.4 | 1387.4 | 125.591 |  | 1626.4 | 1387.4 | 0.46777
| 1626.6 | 1387.6 | 125.591 |  | 1626.6 | 1387.6 | 0.37035
| 1626.8 | 1387.8 | 125.6884 |  | 1626.8 | 1387.8 | 0.37035
| 1627 | 1388 | 125.6884 |  | 1627 | 1388 | 0.46777
| 1627.2 | 1388.2 | 125.4936 |  | 1627.2 | 1388.2 | 0.46777
| 1627.4 | 1388.4 | 125.7858 |  | 1627.4 | 1388.4 | 0.46777
| 1627.6 | 1388.6 | 125.7858 |  | 1627.6 | 1388.6 | 0.37035
| 1627.8 | 1388.8 | 125.7858 |  | 1627.8 | 1388.8 | 0.46777
| 1628 | 1389 | 125.3962 |  | 1628 | 1389 | 0.37035
| 1628.2 | 1389.2 | 125.4936 |  | 1628.2 | 1389.2 | 0.37035
| 1628.4 | 1389.4 | 125.591 |  | 1628.4 | 1389.4 | 0.37035
| 1628.6 | 1389.6 | 125.4936 |  | 1628.6 | 1389.6 | 0.46777
| 1628.8 | 1389.8 | 125.2988 |  | 1628.8 | 1389.8 | 0.37035
| 1629 | 1390 | 125.2988 |  | 1629 | 1390 | 0.37035
| 1629.2 | 1390.2 | 125.2988 |  | 1629.2 | 1390.2 | 0.46777
| 1629.4 | 1390.4 | 125.3962 |  | 1629.4 | 1390.4 | 0.46777
| 1629.6 | 1390.6 | 125.4936 |  | 1629.6 | 1390.6 | 0.27297
| 1629.8 | 1390.8 | 125.3962 |  | 1629.8 | 1390.8 | 0.37035
| 1630 | 1391 | 125.3962 |  | 1630 | 1391 | 0.56516
| 1630.2 | 1391.2 | 125.3962 |  | 1630.2 | 1391.2 | 0.37035
| 1630.4 | 1391.4 | 125.4936 |  | 1630.4 | 1391.4 | 0.46777
| 1630.6 | 1391.6 | 125.591 |  | 1630.6 | 1391.6 | 0.37035
| 1630.8 | 1391.8 | 125.591 |  | 1630.8 | 1391.8 | 0.46777
| 1631 | 1392 | 125.4936 |  | 1631 | 1392 | 0.37035
| 1631.2 | 1392.2 | 125.6884 |  | 1631.2 | 1392.2 | 0.46777
| 1631.4 | 1392.4 | 125.591 |  | 1631.4 | 1392.4 | 0.37035
| 1631.6 | 1392.6 | 125.4936 |  | 1631.6 | 1392.6 | 0.37035
| 1631.8 | 1392.8 | 125.591 |  | 1631.8 | 1392.8 | 0.46777
| 1632 | 1393 | 125.591 |  | 1632 | 1393 | 0.46777
| 1632.2 | 1393.2 | 126.2727 |  | 1632.2 | 1393.2 | 0.37035
| 1632.4 | 1393.4 | 125.2988 |  | 1632.4 | 1393.4 | 0.46777
| 1632.6 | 1393.6 | 125.2014 |  | 1632.6 | 1393.6 | 0.37035
| 1632.8 | 1393.8 | 125.3962 |  | 1632.8 | 1393.8 | 0.46777
| 1633 | 1394 | 125.3962 |  | 1633 | 1394 | 0.37035
| 1633.2 | 1394.2 | 125.4936 |  | 1633.2 | 1394.2 | 0.37035
| 1633.4 | 1394.4 | 125.4936 |  | 1633.4 | 1394.4 | 0.46777
| 1633.6 | 1394.6 | 125.2988 |  | 1633.6 | 1394.6 | 0.46777
| 1633.8 | 1394.8 | 125.2988 |  | 1633.8 | 1394.8 | 0.37035
| 1634 | 1395 | 125.2988 |  | 1634 | 1395 | 0.46777
| 1634.2 | 1395.2 | 125.591 |  | 1634.2 | 1395.2 | 0.46777
| 1634.4 | 1395.4 | 125.2014 |  | 1634.4 | 1395.4 | 0.46777
| 1634.6 | 1395.6 | 125.104 |  | 1634.6 | 1395.6 | 0.46777
| 1634.8 | 1395.8 | 125.2014 |  | 1634.8 | 1395.8 | 0.37035
| 1635 | 1396 | 125.591 |  | 1635 | 1396 | 0.46777
| 1635.2 | 1396.2 | 125.2014 |  | 1635.2 | 1396.2 | 0.46777
| 1635.4 | 1396.4 | 125.2014 |  | 1635.4 | 1396.4 | 0.37035
| 1635.6 | 1396.6 | 124.2274 |  | 1635.6 | 1396.6 | 0.37035
| 1635.8 | 1396.8 | 125.104 |  | 1635.8 | 1396.8 | 0.37035
| 1636 | 1397 | 125.2988 |  | 1636 | 1397 | 0.37035
| 1636.2 | 1397.2 | 125.2988 |  | 1636.2 | 1397.2 | 0.37035
| 1636.4 | 1397.4 | 125.4936 |  | 1636.4 | 1397.4 | 0.37035
| 1636.6 | 1397.6 | 125.3962 |  | 1636.6 | 1397.6 | 0.37035
| 1636.8 | 1397.8 | 125.3962 |  | 1636.8 | 1397.8 | 0.37035
| 1637 | 1398 | 125.3962 |  | 1637 | 1398 | 0.27297
| 1637.2 | 1398.2 | 125.3962 |  | 1637.2 | 1398.2 | 0.37035
| 1637.4 | 1398.4 | 125.0066 |  | 1637.4 | 1398.4 | 0.46777
| 1637.6 | 1398.6 | 125.591 |  | 1637.6 | 1398.6 | 0.46777
| 1637.8 | 1398.8 | 124.9092 |  | 1637.8 | 1398.8 | 0.46777
| 1638 | 1399 | 125.0066 |  | 1638 | 1399 | 0.46777
| 1638.2 | 1399.2 | 125.0066 |  | 1638.2 | 1399.2 | 0.46777
| 1638.4 | 1399.4 | 124.8118 |  | 1638.4 | 1399.4 | 0.46777
| 1638.6 | 1399.6 | 124.9092 |  | 1638.6 | 1399.6 | 0.46777
| 1638.8 | 1399.8 | 124.9092 |  | 1638.8 | 1399.8 | 0.46777
| 1639 | 1400 | 125.2014 |  | 1639 | 1400 | 0.37035
| 1639.2 | 1400.2 | 124.8118 |  | 1639.2 | 1400.2 | 0.37035
| 1639.4 | 1400.4 | 125.104 |  | 1639.4 | 1400.4 | 0.46777
| 1639.6 | 1400.6 | 125.0066 |  | 1639.6 | 1400.6 | 0.56516
| 1639.8 | 1400.8 | 125.2014 |  | 1639.8 | 1400.8 | 0.37035
| 1640 | 1401 | 125.2014 |  | 1640 | 1401 | 0.37035
| 1640.2 | 1401.2 | 125.0066 |  | 1640.2 | 1401.2 | 0.37035
| 1640.4 | 1401.4 | 124.617 |  | 1640.4 | 1401.4 | 0.37035
| 1640.6 | 1401.6 | 124.3248 |  | 1640.6 | 1401.6 | 0.37035
| 1640.8 | 1401.8 | 124.3248 |  | 1640.8 | 1401.8 | 0.37035
| 1641 | 1402 | 124.3248 |  | 1641 | 1402 | 0.37035
| 1641.2 | 1402.2 | 124.5196 |  | 1641.2 | 1402.2 | 0.37035
| 1641.4 | 1402.4 | 124.5196 |  | 1641.4 | 1402.4 | 0.37035
| 1641.6 | 1402.6 | 124.7144 |  | 1641.6 | 1402.6 | 0.37035
| 1641.8 | 1402.8 | 124.7144 |  | 1641.8 | 1402.8 | 0.46777
| 1642 | 1403 | 124.617 |  | 1642 | 1403 | 0.46777
| 1642.2 | 1403.2 | 124.2274 |  | 1642.2 | 1403.2 | 0.37035
| 1642.4 | 1403.4 | 124.5196 |  | 1642.4 | 1403.4 | 0.37035
| 1642.6 | 1403.6 | 124.3248 |  | 1642.6 | 1403.6 | 0.37035
| 1642.8 | 1403.8 | 124.13 |  | 1642.8 | 1403.8 | 0.46777
| 1643 | 1404 | 124.5196 |  | 1643 | 1404 | 0.37035
| 1643.2 | 1404.2 | 124.2274 |  | 1643.2 | 1404.2 | 0.37035
| 1643.4 | 1404.4 | 125.0066 |  | 1643.4 | 1404.4 | 0.37035
| 1643.6 | 1404.6 | 124.617 |  | 1643.6 | 1404.6 | 0.37035
| 1643.8 | 1404.8 | 125.9806 |  | 1643.8 | 1404.8 | 0.46777
| 1644 | 1405 | 126.2727 |  | 1644 | 1405 | 0.37035
| 1644.2 | 1405.2 | 126.3702 |  | 1644.2 | 1405.2 | 0.37035
| 1644.4 | 1405.4 | 126.2727 |  | 1644.4 | 1405.4 | 0.37035
| 1644.6 | 1405.6 | 126.3702 |  | 1644.6 | 1405.6 | 0.37035
| 1644.8 | 1405.8 | 126.5649 |  | 1644.8 | 1405.8 | 0.37035
| 1645 | 1406 | 127.0519 |  | 1645 | 1406 | 0.37035
| 1645.2 | 1406.2 | 127.0519 |  | 1645.2 | 1406.2 | 0.37035
| 1645.4 | 1406.4 | 126.9545 |  | 1645.4 | 1406.4 | 0.37035
| 1645.6 | 1406.6 | 126.6623 |  | 1645.6 | 1406.6 | 0.37035
| 1645.8 | 1406.8 | 126.4675 |  | 1645.8 | 1406.8 | 0.37035
| 1646 | 1407 | 126.2727 |  | 1646 | 1407 | 0.37035
| 1646.2 | 1407.2 | 126.2727 |  | 1646.2 | 1407.2 | 0.37035
| 1646.4 | 1407.4 | 126.3702 |  | 1646.4 | 1407.4 | 0.37035
| 1646.6 | 1407.6 | 126.4675 |  | 1646.6 | 1407.6 | 0.37035
| 1646.8 | 1407.8 | 126.1754 |  | 1646.8 | 1407.8 | 0.37035
| 1647 | 1408 | 126.1754 |  | 1647 | 1408 | 0.37035
| 1647.2 | 1408.2 | 126.1754 |  | 1647.2 | 1408.2 | 0.37035
| 1647.4 | 1408.4 | 126.0779 |  | 1647.4 | 1408.4 | 0.37035
| 1647.6 | 1408.6 | 126.0779 |  | 1647.6 | 1408.6 | 0.37035
| 1647.8 | 1408.8 | 125.9806 |  | 1647.8 | 1408.8 | 0.37035
| 1648 | 1409 | 125.7858 |  | 1648 | 1409 | 0.37035
| 1648.2 | 1409.2 | 125.591 |  | 1648.2 | 1409.2 | 0.37035
| 1648.4 | 1409.4 | 125.2988 |  | 1648.4 | 1409.4 | 0.37035
| 1648.6 | 1409.6 | 125.3962 |  | 1648.6 | 1409.6 | 0.37035
| 1648.8 | 1409.8 | 125.4936 |  | 1648.8 | 1409.8 | 0.46777
| 1649 | 1410 | 125.591 |  | 1649 | 1410 | 0.37035
| 1649.2 | 1410.2 | 125.4936 |  | 1649.2 | 1410.2 | 0.37035
| 1649.4 | 1410.4 | 124.9092 |  | 1649.4 | 1410.4 | 0.37035
| 1649.6 | 1410.6 | 124.7144 |  | 1649.6 | 1410.6 | 0.37035
| 1649.8 | 1410.8 | 124.9092 |  | 1649.8 | 1410.8 | 0.37035
| 1650 | 1411 | 124.8118 |  | 1650 | 1411 | 0.37035
| 1650.2 | 1411.2 | 124.9092 |  | 1650.2 | 1411.2 | 0.37035
| 1650.4 | 1411.4 | 124.7144 |  | 1650.4 | 1411.4 | 0.37035
| 1650.6 | 1411.6 | 124.8118 |  | 1650.6 | 1411.6 | 0.37035
| 1650.8 | 1411.8 | 124.7144 |  | 1650.8 | 1411.8 | 0.37035
| 1651 | 1412 | 124.8118 |  | 1651 | 1412 | 0.27297
| 1651.2 | 1412.2 | 124.8118 |  | 1651.2 | 1412.2 | 0.37035
| 1651.4 | 1412.4 | 124.9092 |  | 1651.4 | 1412.4 | 0.37035
| 1651.6 | 1412.6 | 124.9092 |  | 1651.6 | 1412.6 | 0.37035
| 1651.8 | 1412.8 | 124.7144 |  | 1651.8 | 1412.8 | 0.46777
| 1652 | 1413 | 124.7144 |  | 1652 | 1413 | 0.46777
| 1652.2 | 1413.2 | 124.8118 |  | 1652.2 | 1413.2 | 0.37035
| 1652.4 | 1413.4 | 124.8118 |  | 1652.4 | 1413.4 | 0.37035
| 1652.6 | 1413.6 | 124.7144 |  | 1652.6 | 1413.6 | 0.37035
| 1652.8 | 1413.8 | 124.617 |  | 1652.8 | 1413.8 | 0.37035
| 1653 | 1414 | 124.617 |  | 1653 | 1414 | 0.46777
| 1653.2 | 1414.2 | 124.5196 |  | 1653.2 | 1414.2 | 0.37035
| 1653.4 | 1414.4 | 124.4222 |  | 1653.4 | 1414.4 | 0.46777
| 1653.6 | 1414.6 | 124.4222 |  | 1653.6 | 1414.6 | 0.46777
| 1653.8 | 1414.8 | 124.3248 |  | 1653.8 | 1414.8 | 0.37035
| 1654 | 1415 | 124.2274 |  | 1654 | 1415 | 0.37035
| 1654.2 | 1415.2 | 124.3248 |  | 1654.2 | 1415.2 | 0.37035
| 1654.4 | 1415.4 | 124.3248 |  | 1654.4 | 1415.4 | 0.46777
| 1654.6 | 1415.6 | 124.2274 |  | 1654.6 | 1415.6 | 0.37035
| 1654.8 | 1415.8 | 124.5196 |  | 1654.8 | 1415.8 | 0.37035
| 1655 | 1416 | 124.4222 |  | 1655 | 1416 | 0.46777
| 1655.2 | 1416.2 | 124.3248 |  | 1655.2 | 1416.2 | 0.37035
| 1655.4 | 1416.4 | 124.3248 |  | 1655.4 | 1416.4 | 0.37035
| 1655.6 | 1416.6 | 124.3248 |  | 1655.6 | 1416.6 | 0.37035
| 1655.8 | 1416.8 | 124.2274 |  | 1655.8 | 1416.8 | 0.37035
| 1656 | 1417 | 124.2274 |  | 1656 | 1417 | 0.37035
| 1656.2 | 1417.2 | 124.3248 |  | 1656.2 | 1417.2 | 0.46777
| 1656.4 | 1417.4 | 124.4222 |  | 1656.4 | 1417.4 | 0.46777
| 1656.6 | 1417.6 | 124.4222 |  | 1656.6 | 1417.6 | 0.37035
| 1656.8 | 1417.8 | 124.5196 |  | 1656.8 | 1417.8 | 0.37035
| 1657 | 1418 | 124.617 |  | 1657 | 1418 | 0.37035
| 1657.2 | 1418.2 | 124.617 |  | 1657.2 | 1418.2 | 0.37035
| 1657.4 | 1418.4 | 124.617 |  | 1657.4 | 1418.4 | 0.46777
| 1657.6 | 1418.6 | 124.7144 |  | 1657.6 | 1418.6 | 0.46777
| 1657.8 | 1418.8 | 124.617 |  | 1657.8 | 1418.8 | 0.37035
| 1658 | 1419 | 124.617 |  | 1658 | 1419 | 0.37035
| 1658.2 | 1419.2 | 124.5196 |  | 1658.2 | 1419.2 | 0.37035
| 1658.4 | 1419.4 | 124.617 |  | 1658.4 | 1419.4 | 0.37035
| 1658.6 | 1419.6 | 124.5196 |  | 1658.6 | 1419.6 | 0.46777
| 1658.8 | 1419.8 | 124.5196 |  | 1658.8 | 1419.8 | 0.37035
| 1659 | 1420 | 124.5196 |  | 1659 | 1420 | 0.37035
| 1659.2 | 1420.2 | 124.3248 |  | 1659.2 | 1420.2 | 0.37035
| 1659.4 | 1420.4 | 124.3248 |  | 1659.4 | 1420.4 | 0.37035
| 1659.6 | 1420.6 | 124.3248 |  | 1659.6 | 1420.6 | 0.37035
| 1659.8 | 1420.8 | 124.3248 |  | 1659.8 | 1420.8 | 0.37035
| 1660 | 1421 | 124.2274 |  | 1660 | 1421 | 0.37035
| 1660.2 | 1421.2 | 124.3248 |  | 1660.2 | 1421.2 | 0.37035
| 1660.4 | 1421.4 | 124.4222 |  | 1660.4 | 1421.4 | 0.37035
| 1660.6 | 1421.6 | 124.3248 |  | 1660.6 | 1421.6 | 0.37035
| 1660.8 | 1421.8 | 124.2274 |  | 1660.8 | 1421.8 | 0.37035
| 1661 | 1422 | 124.13 |  | 1661 | 1422 | 0.37035
| 1661.2 | 1422.2 | 124.2274 |  | 1661.2 | 1422.2 | 0.37035
| 1661.4 | 1422.4 | 124.2274 |  | 1661.4 | 1422.4 | 0.27297
| 1661.6 | 1422.6 | 124.13 |  | 1661.6 | 1422.6 | 0.37035
| 1661.8 | 1422.8 | 124.13 |  | 1661.8 | 1422.8 | 0.46777
| 1662 | 1423 | 123.9352 |  | 1662 | 1423 | 0.37035
| 1662.2 | 1423.2 | 124.0326 |  | 1662.2 | 1423.2 | 0.37035
| 1662.4 | 1423.4 | 124.2274 |  | 1662.4 | 1423.4 | 0.37035
| 1662.6 | 1423.6 | 124.8118 |  | 1662.6 | 1423.6 | 0.37035
| 1662.8 | 1423.8 | 126.1754 |  | 1662.8 | 1423.8 | 0.37035
| 1663 | 1424 | 126.6623 |  | 1663 | 1424 | 0.37035
| 1663.2 | 1424.2 | 126.7597 |  | 1663.2 | 1424.2 | 0.37035
| 1663.4 | 1424.4 | 126.8571 |  | 1663.4 | 1424.4 | 0.37035
| 1663.6 | 1424.6 | 126.9545 |  | 1663.6 | 1424.6 | 0.37035
| 1663.8 | 1424.8 | 127.0519 |  | 1663.8 | 1424.8 | 0.46777
| 1664 | 1425 | 127.1493 |  | 1664 | 1425 | 0.37035
| 1664.2 | 1425.2 | 127.1493 |  | 1664.2 | 1425.2 | 0.37035
| 1664.4 | 1425.4 | 127.3441 |  | 1664.4 | 1425.4 | 0.27297
| 1664.6 | 1425.6 | 127.3441 |  | 1664.6 | 1425.6 | 0.37035
| 1664.8 | 1425.8 | 127.6363 |  | 1664.8 | 1425.8 | 0.37035
| 1665 | 1426 | 128.0259 |  | 1665 | 1426 | 0.37035
| 1665.2 | 1426.2 | 128.1233 |  | 1665.2 | 1426.2 | 0.37035
| 1665.4 | 1426.4 | 128.1233 |  | 1665.4 | 1426.4 | 0.37035
| 1665.6 | 1426.6 | 128.1233 |  | 1665.6 | 1426.6 | 0.75996
| 1665.8 | 1426.8 | 128.2207 |  | 1665.8 | 1426.8 | 0.37035
| 1666 | 1427 | 128.1233 |  | 1666 | 1427 | 0.37035
| 1666.2 | 1427.2 | 128.2207 |  | 1666.2 | 1427.2 | 0.37035
| 1666.4 | 1427.4 | 128.1233 |  | 1666.4 | 1427.4 | 0.37035
| 1666.6 | 1427.6 | 128.1233 |  | 1666.6 | 1427.6 | 0.37035
| 1666.8 | 1427.8 | 128.0259 |  | 1666.8 | 1427.8 | 0.37035
| 1667 | 1428 | 128.1233 |  | 1667 | 1428 | 0.46777
| 1667.2 | 1428.2 | 128.1233 |  | 1667.2 | 1428.2 | 0.37035
| 1667.4 | 1428.4 | 128.1233 |  | 1667.4 | 1428.4 | 0.37035
| 1667.6 | 1428.6 | 128.1233 |  | 1667.6 | 1428.6 | 0.37035
| 1667.8 | 1428.8 | 128.0259 |  | 1667.8 | 1428.8 | 0.37035
| 1668 | 1429 | 128.0259 |  | 1668 | 1429 | 0.37035
| 1668.2 | 1429.2 | 128.0259 |  | 1668.2 | 1429.2 | 0.37035
| 1668.4 | 1429.4 | 128.0259 |  | 1668.4 | 1429.4 | 0.37035
| 1668.6 | 1429.6 | 128.1233 |  | 1668.6 | 1429.6 | 0.46777
| 1668.8 | 1429.8 | 128.1233 |  | 1668.8 | 1429.8 | 0.37035
| 1669 | 1430 | 128.1233 |  | 1669 | 1430 | 0.46777
| 1669.2 | 1430.2 | 128.2207 |  | 1669.2 | 1430.2 | 0.37035
| 1669.4 | 1430.4 | 128.2207 |  | 1669.4 | 1430.4 | 0.37035
| 1669.6 | 1430.6 | 128.2207 |  | 1669.6 | 1430.6 | 0.46777
| 1669.8 | 1430.8 | 128.2207 |  | 1669.8 | 1430.8 | 0.37035
| 1670 | 1431 | 128.3181 |  | 1670 | 1431 | 0.46777
| 1670.2 | 1431.2 | 128.3181 |  | 1670.2 | 1431.2 | 0.37035
| 1670.4 | 1431.4 | 128.2207 |  | 1670.4 | 1431.4 | 0.37035
| 1670.6 | 1431.6 | 127.5389 |  | 1670.6 | 1431.6 | 0.37035
| 1670.8 | 1431.8 | 128.0259 |  | 1670.8 | 1431.8 | 0.46777
| 1671 | 1432 | 128.1233 |  | 1671 | 1432 | 0.37035
| 1671.2 | 1432.2 | 128.2207 |  | 1671.2 | 1432.2 | 0.46777
| 1671.4 | 1432.4 | 128.2207 |  | 1671.4 | 1432.4 | 0.37035
| 1671.6 | 1432.6 | 128.1233 |  | 1671.6 | 1432.6 | 0.37035
| 1671.8 | 1432.8 | 128.0259 |  | 1671.8 | 1432.8 | 0.46777
| 1672 | 1433 | 128.1233 |  | 1672 | 1433 | 0.37035
| 1672.2 | 1433.2 | 128.1233 |  | 1672.2 | 1433.2 | 0.37035
| 1672.4 | 1433.4 | 128.1233 |  | 1672.4 | 1433.4 | 0.37035
| 1672.6 | 1433.6 | 128.1233 |  | 1672.6 | 1433.6 | 0.46777
| 1672.8 | 1433.8 | 128.0259 |  | 1672.8 | 1433.8 | 0.37035
| 1673 | 1434 | 128.0259 |  | 1673 | 1434 | 0.46777
| 1673.2 | 1434.2 | 127.7337 |  | 1673.2 | 1434.2 | 0.37035
| 1673.4 | 1434.4 | 127.6363 |  | 1673.4 | 1434.4 | 0.46777
| 1673.6 | 1434.6 | 127.5389 |  | 1673.6 | 1434.6 | 0.46777
| 1673.8 | 1434.8 | 127.5389 |  | 1673.8 | 1434.8 | 0.46777
| 1674 | 1435 | 127.3441 |  | 1674 | 1435 | 0.37035
| 1674.2 | 1435.2 | 127.3441 |  | 1674.2 | 1435.2 | 0.37035
| 1674.4 | 1435.4 | 127.5389 |  | 1674.4 | 1435.4 | 0.46777
| 1674.6 | 1435.6 | 127.6363 |  | 1674.6 | 1435.6 | 0.46777
| 1674.8 | 1435.8 | 127.3441 |  | 1674.8 | 1435.8 | 0.46777
| 1675 | 1436 | 127.3441 |  | 1675 | 1436 | 0.46777
| 1675.2 | 1436.2 | 127.1493 |  | 1675.2 | 1436.2 | 0.37035
| 1675.4 | 1436.4 | 127.0519 |  | 1675.4 | 1436.4 | 0.46777
| 1675.6 | 1436.6 | 127.1493 |  | 1675.6 | 1436.6 | 0.37035
| 1675.8 | 1436.8 | 127.0519 |  | 1675.8 | 1436.8 | 0.46777
| 1676 | 1437 | 126.7597 |  | 1676 | 1437 | 0.46777
| 1676.2 | 1437.2 | 126.9545 |  | 1676.2 | 1437.2 | 0.37035
| 1676.4 | 1437.4 | 124.5196 |  | 1676.4 | 1437.4 | 0.46777
| 1676.6 | 1437.6 | 125.6884 |  | 1676.6 | 1437.6 | 0.46777
| 1676.8 | 1437.8 | 127.6363 |  | 1676.8 | 1437.8 | 0.37035
| 1677 | 1438 | 121.9873 |  | 1677 | 1438 | 0.27297
| 1677.2 | 1438.2 | 116.1435 |  | 1677.2 | 1438.2 | 0.27297
| 1677.4 | 1438.4 | 119.3576 |  | 1677.4 | 1438.4 | 0.75996
| 1677.6 | 1438.6 | 122.0847 |  | 1677.6 | 1438.6 | 0.46777
| 1677.8 | 1438.8 | 126.2727 |  | 1677.8 | 1438.8 | 0.46777
| 1678 | 1439 | 122.5717 |  | 1678 | 1439 | 0.17559
| 1678.2 | 1439.2 | 119.455 |  | 1678.2 | 1439.2 | 0.37035
| 1678.4 | 1439.4 | 124.8118 |  | 1678.4 | 1439.4 | 0.078174
| 1678.6 | 1439.6 | 121.7925 |  | 1678.6 | 1439.6 | 0.27297
| 1678.8 | 1439.8 | 120.3315 |  | 1678.8 | 1439.8 | 0.56516
| 1679 | 1440 | 103.6767 |  | 1679 | 1440 | 0.56516
| 1679.2 | 1440.2 | 31.8955 |  | 1679.2 | 1440.2 | 0.37035
| 1679.4 | 1440.4 | 4.8193 |  | 1679.4 | 1440.4 | 0.46777
| 1679.6 | 1440.6 | 1.8 |  | 1679.6 | 1440.6 | 0.46777
| 1679.8 | 1440.8 | 1.2156 |  | 1679.8 | 1440.8 | 0.46777
| 1680 | 1441 | 0.9234 |  | 1680 | 1441 | 0.37035
| 1720 | 1481 | 0.43642 |  | 1680.2 | 1441.2 | 0.37035
| 1780 | 1541 | 0.43642 |  | 1680.4 | 1441.4 | 0.37035
| 1840 | 1601 | 0.43642 |  | 1680.6 | 1441.6 | 0.46777
| 1890 | 1651 | 0.33904 |  | 1680.8 | 1441.8 | 0.46777
| 1940 | 1701 | 0.43642 |  | 1681 | 1442 | 0.46777
| 2000 | 1761 | 0.53384 |  | 1681.2 | 1442.2 | 0.46777
| 2060 | 1821 | 0.53384 |  | 1681.4 | 1442.4 | 0.46777
| 2120 | 1881 | 0.43642 |  | 1681.6 | 1442.6 | 0.46777
| 2180 | 1941 | 0.43642 |  | 1681.8 | 1442.8 | 0.46777
| 2220 | 1981 | 0.43642 |  | 1682 | 1443 | 0.46777
| 2220.2 | 1981.2 | 0.53384 |  | 1682.2 | 1443.2 | 0.37035
| 2220.4 | 1981.4 | 0.43642 |  | 1682.4 | 1443.4 | 0.46777
| 2220.6 | 1981.6 | 0.33904 |  | 1682.6 | 1443.6 | 0.46777
| 2220.8 | 1981.8 | 0.43642 |  | 1682.8 | 1443.8 | 0.37035
| 2221 | 1982 | 0.43642 |  | 1683 | 1444 | 0.46777
| 2221.2 | 1982.2 | 0.43642 |  | 1683.2 | 1444.2 | 0.46777
| 2221.4 | 1982.4 | 0.43642 |  | 1683.4 | 1444.4 | 0.46777
| 2221.6 | 1982.6 | 0.53384 |  | 1683.6 | 1444.6 | 0.46777
| 2221.8 | 1982.8 | 0.43642 |  | 1683.8 | 1444.8 | 0.37035
| 2222 | 1983 | 0.43642 |  | 1684 | 1445 | 0.46777
| 2222.2 | 1983.2 | 0.43642 |  | 1684.2 | 1445.2 | 0.37035
| 2222.4 | 1983.4 | 0.43642 |  | 1684.4 | 1445.4 | 0.37035
| 2222.6 | 1983.6 | 0.43642 |  | 1684.6 | 1445.6 | 0.37035
| 2222.8 | 1983.8 | 0.43642 |  | 1684.8 | 1445.8 | 0.46777
| 2223 | 1984 | 0.43642 |  | 1685 | 1446 | 0.46777
| 2223.2 | 1984.2 | 0.43642 |  | 1685.2 | 1446.2 | 0.46777
| 2223.4 | 1984.4 | 0.53384 |  | 1685.4 | 1446.4 | 0.46777
| 2223.6 | 1984.6 | 1.1182 |  | 1685.6 | 1446.6 | 0.37035
| 2223.8 | 1984.8 | 0.53384 |  | 1685.8 | 1446.8 | 0.37035
| 2224 | 1985 | 0.63122 |  | 1686 | 1447 | 0.46777
| 2224.2 | 1985.2 | 0.14424 |  | 1686.2 | 1447.2 | 0.46777
| 2224.4 | 1985.4 | 0.43642 |  | 1686.4 | 1447.4 | 0.46777
| 2224.6 | 1985.6 | 0.53384 |  | 1686.6 | 1447.6 | 0.46777
| 2224.8 | 1985.8 | 0.24166 |  | 1686.8 | 1447.8 | 0.46777
| 2225 | 1986 | 0.43642 |  | 1687 | 1448 | 0.46777
| 2225.2 | 1986.2 | 0.53384 |  | 1687.2 | 1448.2 | 0.37035
| 2225.4 | 1986.4 | 0.43642 |  | 1687.4 | 1448.4 | 0.46777
| 2225.6 | 1986.6 | 0.33904 |  | 1687.6 | 1448.6 | 0.46777
| 2225.8 | 1986.8 | 0.82602 |  | 1687.8 | 1448.8 | 0.37035
| 2226 | 1987 | 0.72864 |  | 1688 | 1449 | 0.37035
| 2226.2 | 1987.2 | 0.24166 |  | 1688.2 | 1449.2 | 0.37035
| 2226.4 | 1987.4 | 0.43642 |  | 1688.4 | 1449.4 | 0.37035
| 2226.6 | 1987.6 | 0.43642 |  | 1688.6 | 1449.6 | 0.37035
| 2226.8 | 1987.8 | 0.33904 |  | 1688.8 | 1449.8 | 0.37035
| 2227 | 1988 | 0.33904 |  | 1689 | 1450 | 0.37035
| 2227.2 | 1988.2 | 0.24166 |  | 1689.2 | 1450.2 | 0.37035
| 2227.4 | 1988.4 | 0.53384 |  | 1689.4 | 1450.4 | 0.37035
| 2227.6 | 1988.6 | 0.33904 |  | 1689.6 | 1450.6 | 0.27297
| 2227.8 | 1988.8 | 0.82602 |  | 1689.8 | 1450.8 | 0.37035
| 2228 | 1989 | -0.050564 |  | 1690 | 1451 | 0.37035
| 2228.2 | 1989.2 | 0.24166 |  | 1690.2 | 1451.2 | 0.46777
| 2228.4 | 1989.4 | 0.63122 |  | 1690.4 | 1451.4 | 0.37035
| 2228.6 | 1989.6 | 0.43642 |  | 1690.6 | 1451.6 | 0.37035
| 2228.8 | 1989.8 | 0.24166 |  | 1690.8 | 1451.8 | 0.37035
| 2229 | 1990 | 0.24166 |  | 1691 | 1452 | 0.37035
| 2229.2 | 1990.2 | 0.63122 |  | 1691.2 | 1452.2 | 0.37035
| 2229.4 | 1990.4 | 0.53384 |  | 1691.4 | 1452.4 | 0.37035
| 2229.6 | 1990.6 | 0.72864 |  | 1691.6 | 1452.6 | 0.46777
| 2229.8 | 1990.8 | 0.43642 |  | 1691.8 | 1452.8 | 0.37035
| 2230 | 1991 | 0.24166 |  | 1692 | 1453 | 0.37035
| 2230.2 | 1991.2 | 0.046856 |  | 1692.2 | 1453.2 | 0.46777
| 2230.4 | 1991.4 | 0.33904 |  | 1692.4 | 1453.4 | 0.37035
| 2230.6 | 1991.6 | 0.24166 |  | 1692.6 | 1453.6 | 0.37035
| 2230.8 | 1991.8 | -0.24532 |  | 1692.8 | 1453.8 | 0.37035
| 2231 | 1992 | 0.63122 |  | 1693 | 1454 | 0.37035
| 2231.2 | 1992.2 | 0.33904 |  | 1693.2 | 1454.2 | 0.37035
| 2231.4 | 1992.4 | 0.53384 |  | 1693.4 | 1454.4 | 0.27297
| 2231.6 | 1992.6 | 0.14424 |  | 1693.6 | 1454.6 | 0.37035
| 2231.8 | 1992.8 | 0.43642 |  | 1693.8 | 1454.8 | 0.37035
| 2232 | 1993 | 0.24166 |  | 1694 | 1455 | 0.37035
| 2232.2 | 1993.2 | 0.9234 |  | 1694.2 | 1455.2 | 0.37035
| 2232.4 | 1993.4 | 0.63122 |  | 1694.4 | 1455.4 | 0.37035
| 2232.6 | 1993.6 | 1.0208 |  | 1694.6 | 1455.6 | 0.37035
| 2232.8 | 1993.8 | 0.046856 |  | 1694.8 | 1455.8 | 0.37035
| 2233 | 1994 | 0.14424 |  | 1695 | 1456 | 0.37035
| 2233.2 | 1994.2 | 0.24166 |  | 1695.2 | 1456.2 | 0.37035
| 2233.4 | 1994.4 | 0.72864 |  | 1695.4 | 1456.4 | 0.37035
| 2233.6 | 1994.6 | 0.63122 |  | 1695.6 | 1456.6 | 0.27297
| 2233.8 | 1994.8 | 0.63122 |  | 1695.8 | 1456.8 | 0.37035
| 2234 | 1995 | 0.63122 |  | 1696 | 1457 | 0.37035
| 2234.2 | 1995.2 | 0.24166 |  | 1696.2 | 1457.2 | 0.37035
| 2234.4 | 1995.4 | 0.53384 |  | 1696.4 | 1457.4 | 0.37035
| 2234.6 | 1995.6 | 0.24166 |  | 1696.6 | 1457.6 | 0.37035
| 2234.8 | 1995.8 | 0.53384 |  | 1696.8 | 1457.8 | 0.46777
| 2235 | 1996 | 0.24166 |  | 1697 | 1458 | 0.37035
| 2235.2 | 1996.2 | 0.72864 |  | 1697.2 | 1458.2 | 0.37035
| 2235.4 | 1996.4 | 0.43642 |  | 1697.4 | 1458.4 | 0.37035
| 2235.6 | 1996.6 | 0.33904 |  | 1697.6 | 1458.6 | 0.37035
| 2235.8 | 1996.8 | 0.33904 |  | 1697.8 | 1458.8 | 0.37035
| 2236 | 1997 | 0.43642 |  | 1698 | 1459 | 0.46777
| 2236.2 | 1997.2 | 0.63122 |  | 1698.2 | 1459.2 | 0.37035
| 2236.4 | 1997.4 | 0.33904 |  | 1698.4 | 1459.4 | 0.37035
| 2236.6 | 1997.6 | 0.72864 |  | 1698.6 | 1459.6 | 0.46777
| 2236.8 | 1997.8 | 0.53384 |  | 1698.8 | 1459.8 | 0.46777
| 2237 | 1998 | 0.63122 |  | 1699 | 1460 | 0.37035
| 2237.2 | 1998.2 | 0.43642 |  | 1699.2 | 1460.2 | 0.37035
| 2237.4 | 1998.4 | 0.33904 |  | 1699.4 | 1460.4 | 0.37035
| 2237.6 | 1998.6 | 0.43642 |  | 1699.6 | 1460.6 | 0.37035
| 2237.8 | 1998.8 | 0.53384 |  | 1699.8 | 1460.8 | 0.46777
| 2238 | 1999 | 0.9234 |  | 1700 | 1461 | 0.37035
| 2238.2 | 1999.2 | 0.33904 |  | 1700.2 | 1461.2 | 0.37035
| 2238.4 | 1999.4 | 0.43642 |  | 1700.4 | 1461.4 | 0.37035
| 2238.6 | 1999.6 | 0.046856 |  | 1700.6 | 1461.6 | 0.37035
| 2238.8 | 1999.8 | 0.53384 |  | 1700.8 | 1461.8 | 0.46777
| 2239 | 2000 | 0.33904 |  | 1701 | 1462 | 0.46777
| 2239.2 | 2000.2 | 0.72864 |  | 1701.2 | 1462.2 | 0.37035
| 2239.4 | 2000.4 | 0.24166 |  | 1701.4 | 1462.4 | 0.37035
| 2239.6 | 2000.6 | 0.72864 |  | 1701.6 | 1462.6 | 0.37035
| 2239.8 | 2000.8 | 0.24166 |  | 1701.8 | 1462.8 | 0.37035
| 2240 | 2001 | 0.53384 |  | 1702 | 1463 | 0.37035
| 2240.2 | 2001.2 | 1.2156 |  | 1702.2 | 1463.2 | 0.37035
| 2240.4 | 2001.4 | 0.53384 |  | 1702.4 | 1463.4 | 0.37035
| 2240.6 | 2001.6 | 0.33904 |  | 1702.6 | 1463.6 | 0.37035
| 2240.8 | 2001.8 | 0.14424 |  | 1702.8 | 1463.8 | 0.37035
| 2241 | 2002 | -0.53755 |  | 1703 | 1464 | 0.37035
| 2241.2 | 2002.2 | 0.24166 |  | 1703.2 | 1464.2 | 0.37035
| 2241.4 | 2002.4 | -0.050564 |  | 1703.4 | 1464.4 | 0.37035
| 2241.6 | 2002.6 | 0.9234 |  | 1703.6 | 1464.6 | 0.37035
| 2241.8 | 2002.8 | -1.1219 |  | 1703.8 | 1464.8 | 0.37035
| 2242 | 2003 | 0.43642 |  | 1704 | 1465 | 0.37035
| 2242.2 | 2003.2 | 0.53384 |  | 1704.2 | 1465.2 | 0.37035
| 2242.4 | 2003.4 | 0.43642 |  | 1704.4 | 1465.4 | 0.37035
| 2242.6 | 2003.6 | 0.43642 |  | 1704.6 | 1465.6 | 0.37035
| 2242.8 | 2003.8 | 0.43642 |  | 1704.8 | 1465.8 | 0.37035
| 2243 | 2004 | 0.43642 |  | 1705 | 1466 | 0.37035
| 2243.2 | 2004.2 | 0.43642 |  | 1705.2 | 1466.2 | 0.37035
| 2243.4 | 2004.4 | 0.53384 |  | 1705.4 | 1466.4 | 0.37035
| 2243.6 | 2004.6 | 0.43642 |  | 1705.6 | 1466.6 | 0.37035
| 2243.8 | 2004.8 | 0.53384 |  | 1705.8 | 1466.8 | 0.37035
| 2244 | 2005 | 0.43642 |  | 1706 | 1467 | 0.37035
| 2244.2 | 2005.2 | 0.33904 |  | 1706.2 | 1467.2 | 0.37035
| 2244.4 | 2005.4 | 0.33904 |  | 1706.4 | 1467.4 | 0.37035
| 2244.6 | 2005.6 | 0.53384 |  | 1706.6 | 1467.6 | 0.37035
| 2244.8 | 2005.8 | 0.43642 |  | 1706.8 | 1467.8 | 0.46777
| 2245 | 2006 | 0.33904 |  | 1707 | 1468 | 0.37035
| 2245.2 | 2006.2 | 0.43642 |  | 1707.2 | 1468.2 | 0.37035
| 2245.4 | 2006.4 | 0.43642 |  | 1707.4 | 1468.4 | 0.37035
| 2245.6 | 2006.6 | 0.24166 |  | 1707.6 | 1468.6 | 0.37035
| 2245.8 | 2006.8 | 0.43642 |  | 1707.8 | 1468.8 | 0.46777
| 2246 | 2007 | 0.43642 |  | 1708 | 1469 | 0.37035
| 2246.2 | 2007.2 | 0.53384 |  | 1708.2 | 1469.2 | 0.37035
| 2246.4 | 2007.4 | 0.43642 |  | 1708.4 | 1469.4 | 0.37035
| 2246.6 | 2007.6 | 0.53384 |  | 1708.6 | 1469.6 | 0.46777
| 2246.8 | 2007.8 | 0.43642 |  | 1708.8 | 1469.8 | 0.46777
| 2247 | 2008 | 0.43642 |  | 1709 | 1470 | 0.37035
| 2247.2 | 2008.2 | 0.43642 |  | 1709.2 | 1470.2 | 0.56516
| 2247.4 | 2008.4 | 0.43642 |  | 1709.4 | 1470.4 | 0.46777
| 2247.6 | 2008.6 | 0.33904 |  | 1709.6 | 1470.6 | 0.27297
| 2247.8 | 2008.8 | 0.43642 |  | 1709.8 | 1470.8 | 0.37035
| 2248 | 2009 | 0.43642 |  | 1710 | 1471 | 0.37035
| 2248.2 | 2009.2 | 0.43642 |  | 1710.2 | 1471.2 | 0.37035
| 2248.4 | 2009.4 | 0.43642 |  | 1710.4 | 1471.4 | 0.46777
| 2248.6 | 2009.6 | 0.43642 |  | 1710.6 | 1471.6 | 0.37035
| 2248.8 | 2009.8 | 0.53384 |  | 1710.8 | 1471.8 | 0.37035
| 2249 | 2010 | 0.43642 |  | 1711 | 1472 | 0.37035
| 2249.2 | 2010.2 | 0.43642 |  | 1711.2 | 1472.2 | 0.37035
| 2249.4 | 2010.4 | 0.53384 |  | 1711.4 | 1472.4 | 0.37035
| 2249.6 | 2010.6 | 0.43642 |  | 1711.6 | 1472.6 | 0.37035
| 2249.8 | 2010.8 | 0.43642 |  | 1711.8 | 1472.8 | 0.37035
| 2250 | 2011 | 0.53384 |  | 1712 | 1473 | 0.37035
| 2300 | 2061 | 0.43642 |  | 1712.2 | 1473.2 | 0.37035
| 2360 | 2121 | 0.43642 |  | 1712.4 | 1473.4 | 0.37035
| 2420 | 2181 | 0.53384 |  | 1712.6 | 1473.6 | 0.37035
| 2480 | 2241 | 0.53384 |  | 1712.8 | 1473.8 | 0.37035
| 2540 | 2301 | 0.43642 |  | 1713 | 1474 | 0.37035
[5 empty] | 1713.2 | 1474.2 | 0.37035
[5 empty] | 1713.4 | 1474.4 | 0.46777
[5 empty] | 1713.6 | 1474.6 | 0.46777
[5 empty] | 1713.8 | 1474.8 | 0.46777
[5 empty] | 1714 | 1475 | 0.37035
[5 empty] | 1714.2 | 1475.2 | 0.37035
[5 empty] | 1714.4 | 1475.4 | 0.46777
[5 empty] | 1714.6 | 1475.6 | 0.37035
[5 empty] | 1714.8 | 1475.8 | 0.46777
[5 empty] | 1715 | 1476 | 0.37035
[5 empty] | 1715.2 | 1476.2 | 0.37035
[5 empty] | 1715.4 | 1476.4 | 0.37035
[5 empty] | 1715.6 | 1476.6 | 0.46777
[5 empty] | 1715.8 | 1476.8 | 0.37035
[5 empty] | 1716 | 1477 | 0.37035
[5 empty] | 1716.2 | 1477.2 | 0.46777
[5 empty] | 1716.4 | 1477.4 | 0.37035
[5 empty] | 1716.6 | 1477.6 | 0.37035
[5 empty] | 1716.8 | 1477.8 | 0.46777
[5 empty] | 1717 | 1478 | 0.46777
[5 empty] | 1717.2 | 1478.2 | 0.37035
[5 empty] | 1717.4 | 1478.4 | 0.46777
[5 empty] | 1717.6 | 1478.6 | 0.37035
[5 empty] | 1717.8 | 1478.8 | 0.46777
[5 empty] | 1718 | 1479 | 0.46777
[5 empty] | 1718.2 | 1479.2 | 0.37035
[5 empty] | 1718.4 | 1479.4 | 0.46777
[5 empty] | 1718.6 | 1479.6 | 0.37035
[5 empty] | 1718.8 | 1479.8 | 0.46777
[5 empty] | 1719 | 1480 | 0.46777
[5 empty] | 1719.2 | 1480.2 | 0.46777
[5 empty] | 1719.4 | 1480.4 | 0.46777
[5 empty] | 1719.6 | 1480.6 | 0.37035
[5 empty] | 1719.8 | 1480.8 | 0.46777
[5 empty] | 1720 | 1481 | 0.37035
[5 empty] | 1720.2 | 1481.2 | 0.46777
[5 empty] | 1720.4 | 1481.4 | 0.37035
[5 empty] | 1720.6 | 1481.6 | 0.46777
[5 empty] | 1720.8 | 1481.8 | 0.37035
[5 empty] | 1721 | 1482 | 0.46777
[5 empty] | 1721.2 | 1482.2 | 0.46777
[5 empty] | 1721.4 | 1482.4 | 0.37035
[5 empty] | 1721.6 | 1482.6 | 0.46777
[5 empty] | 1721.8 | 1482.8 | 0.37035
[5 empty] | 1722 | 1483 | 0.46777
[5 empty] | 1722.2 | 1483.2 | 0.46777
[5 empty] | 1722.4 | 1483.4 | 0.37035
[5 empty] | 1722.6 | 1483.6 | 0.37035
[5 empty] | 1722.8 | 1483.8 | 0.46777
[5 empty] | 1723 | 1484 | 0.37035
[5 empty] | 1723.2 | 1484.2 | 0.37035
[5 empty] | 1723.4 | 1484.4 | 0.37035
[5 empty] | 1723.6 | 1484.6 | 0.37035
[5 empty] | 1723.8 | 1484.8 | 0.37035
[5 empty] | 1724 | 1485 | 0.37035
[5 empty] | 1724.2 | 1485.2 | 0.37035
[5 empty] | 1724.4 | 1485.4 | 0.37035
[5 empty] | 1724.6 | 1485.6 | 0.46777
[5 empty] | 1724.8 | 1485.8 | 0.37035
[5 empty] | 1725 | 1486 | 0.37035
[5 empty] | 1725.2 | 1486.2 | 0.37035
[5 empty] | 1725.4 | 1486.4 | 0.46777
[5 empty] | 1725.6 | 1486.6 | 0.37035
[5 empty] | 1725.8 | 1486.8 | 0.46777
[5 empty] | 1726 | 1487 | 0.37035
[5 empty] | 1726.2 | 1487.2 | 0.46777
[5 empty] | 1726.4 | 1487.4 | 0.37035
[5 empty] | 1726.6 | 1487.6 | 0.46777
[5 empty] | 1726.8 | 1487.8 | 0.46777
[5 empty] | 1727 | 1488 | 0.46777
[5 empty] | 1727.2 | 1488.2 | 0.46777
[5 empty] | 1727.4 | 1488.4 | 0.37035
[5 empty] | 1727.6 | 1488.6 | 0.37035
[5 empty] | 1727.8 | 1488.8 | 0.46777
[5 empty] | 1728 | 1489 | 0.37035
[5 empty] | 1728.2 | 1489.2 | 0.37035
[5 empty] | 1728.4 | 1489.4 | 0.37035
[5 empty] | 1728.6 | 1489.6 | 0.37035
[5 empty] | 1728.8 | 1489.8 | 0.37035
[5 empty] | 1729 | 1490 | 0.46777
[5 empty] | 1729.2 | 1490.2 | 0.37035
[5 empty] | 1729.4 | 1490.4 | 0.46777
[5 empty] | 1729.6 | 1490.6 | 0.37035
[5 empty] | 1729.8 | 1490.8 | 0.46777
[5 empty] | 1730 | 1491 | 0.46777
[5 empty] | 1730.2 | 1491.2 | 0.66258
[5 empty] | 1730.4 | 1491.4 | 0.37035
[5 empty] | 1730.6 | 1491.6 | 0.37035
[5 empty] | 1730.8 | 1491.8 | 0.46777
[5 empty] | 1731 | 1492 | 0.37035
[5 empty] | 1731.2 | 1492.2 | 0.46777
[5 empty] | 1731.4 | 1492.4 | 0.46777
[5 empty] | 1731.6 | 1492.6 | 0.37035
[5 empty] | 1731.8 | 1492.8 | 0.46777
[5 empty] | 1732 | 1493 | 0.37035
[5 empty] | 1732.2 | 1493.2 | 0.37035
[5 empty] | 1732.4 | 1493.4 | 0.37035
[5 empty] | 1732.6 | 1493.6 | 0.46777
[5 empty] | 1732.8 | 1493.8 | 0.37035
[5 empty] | 1733 | 1494 | 0.46777
[5 empty] | 1733.2 | 1494.2 | 0.46777
[5 empty] | 1733.4 | 1494.4 | 0.46777
[5 empty] | 1733.6 | 1494.6 | 0.46777
[5 empty] | 1733.8 | 1494.8 | 0.46777
[5 empty] | 1734 | 1495 | 0.46777
[5 empty] | 1734.2 | 1495.2 | 0.46777
[5 empty] | 1734.4 | 1495.4 | 0.46777
[5 empty] | 1734.6 | 1495.6 | 0.46777
[5 empty] | 1734.8 | 1495.8 | 0.46777
[5 empty] | 1735 | 1496 | 0.46777
[5 empty] | 1735.2 | 1496.2 | 0.37035
[5 empty] | 1735.4 | 1496.4 | 0.46777
[5 empty] | 1735.6 | 1496.6 | 0.37035
[5 empty] | 1735.8 | 1496.8 | 0.37035
[5 empty] | 1736 | 1497 | 0.46777
[5 empty] | 1736.2 | 1497.2 | 0.46777
[5 empty] | 1736.4 | 1497.4 | 0.37035
[5 empty] | 1736.6 | 1497.6 | 0.37035
[5 empty] | 1736.8 | 1497.8 | 0.46777
[5 empty] | 1737 | 1498 | 0.37035
[5 empty] | 1737.2 | 1498.2 | 0.37035
[5 empty] | 1737.4 | 1498.4 | 0.37035
[5 empty] | 1737.6 | 1498.6 | 0.37035
[5 empty] | 1737.8 | 1498.8 | 0.46777
[5 empty] | 1738 | 1499 | 0.46777
[5 empty] | 1738.2 | 1499.2 | 0.37035
[5 empty] | 1738.4 | 1499.4 | 0.37035
[5 empty] | 1738.6 | 1499.6 | 0.37035
[5 empty] | 1738.8 | 1499.8 | 0.37035
[5 empty] | 1739 | 1500 | 0.37035
[5 empty] | 1739.2 | 1500.2 | 0.37035
[5 empty] | 1739.4 | 1500.4 | 0.46777
[5 empty] | 1739.6 | 1500.6 | 0.46777
[5 empty] | 1739.8 | 1500.8 | 0.37035
[5 empty] | 1740 | 1501 | 0.37035
[5 empty] | 1740.2 | 1501.2 | 0.27297
[5 empty] | 1740.4 | 1501.4 | 0.37035
[5 empty] | 1740.6 | 1501.6 | 0.37035
[5 empty] | 1740.8 | 1501.8 | 0.37035
[5 empty] | 1741 | 1502 | 0.46777
[5 empty] | 1741.2 | 1502.2 | 0.37035
[5 empty] | 1741.4 | 1502.4 | 0.37035
[5 empty] | 1741.6 | 1502.6 | 0.37035
[5 empty] | 1741.8 | 1502.8 | 0.37035
[5 empty] | 1742 | 1503 | 0.27297
[5 empty] | 1742.2 | 1503.2 | 0.37035
[5 empty] | 1742.4 | 1503.4 | 0.37035
[5 empty] | 1742.6 | 1503.6 | 0.37035
[5 empty] | 1742.8 | 1503.8 | 0.37035
[5 empty] | 1743 | 1504 | 0.46777
[5 empty] | 1743.2 | 1504.2 | 0.37035
[5 empty] | 1743.4 | 1504.4 | 0.37035
[5 empty] | 1743.6 | 1504.6 | 0.46777
[5 empty] | 1743.8 | 1504.8 | 0.37035
[5 empty] | 1744 | 1505 | 0.37035
[5 empty] | 1744.2 | 1505.2 | 0.46777
[5 empty] | 1744.4 | 1505.4 | 0.37035
[5 empty] | 1744.6 | 1505.6 | 0.37035
[5 empty] | 1744.8 | 1505.8 | 0.37035
[5 empty] | 1745 | 1506 | 0.37035
[5 empty] | 1745.2 | 1506.2 | 0.37035
[5 empty] | 1745.4 | 1506.4 | 0.37035
[5 empty] | 1745.6 | 1506.6 | 0.37035
[5 empty] | 1745.8 | 1506.8 | 0.37035
[5 empty] | 1746 | 1507 | 0.37035
[5 empty] | 1746.2 | 1507.2 | 0.46777
[5 empty] | 1746.4 | 1507.4 | 0.46777
[5 empty] | 1746.6 | 1507.6 | 0.37035
[5 empty] | 1746.8 | 1507.8 | 0.37035
[5 empty] | 1747 | 1508 | 0.37035
[5 empty] | 1747.2 | 1508.2 | 0.37035
[5 empty] | 1747.4 | 1508.4 | 0.37035
[5 empty] | 1747.6 | 1508.6 | 0.37035
[5 empty] | 1747.8 | 1508.8 | 0.37035
[5 empty] | 1748 | 1509 | 0.37035
[5 empty] | 1748.2 | 1509.2 | 0.46777
[5 empty] | 1748.4 | 1509.4 | 0.37035
[5 empty] | 1748.6 | 1509.6 | 0.37035
[5 empty] | 1748.8 | 1509.8 | 0.37035
[5 empty] | 1749 | 1510 | 0.37035
[5 empty] | 1749.2 | 1510.2 | 0.46777
[5 empty] | 1749.4 | 1510.4 | 0.37035
[5 empty] | 1749.6 | 1510.6 | 0.37035
[5 empty] | 1749.8 | 1510.8 | 0.46777
[5 empty] | 1750 | 1511 | 0.37035
[5 empty] | 1750.2 | 1511.2 | 0.46777
[5 empty] | 1750.4 | 1511.4 | 0.37035
[5 empty] | 1750.6 | 1511.6 | 0.37035
[5 empty] | 1750.8 | 1511.8 | 0.37035
[5 empty] | 1751 | 1512 | 0.37035
[5 empty] | 1751.2 | 1512.2 | 0.46777
[5 empty] | 1751.4 | 1512.4 | 0.46777
[5 empty] | 1751.6 | 1512.6 | 0.37035
[5 empty] | 1751.8 | 1512.8 | 0.37035
[5 empty] | 1752 | 1513 | 0.37035
[5 empty] | 1752.2 | 1513.2 | 0.37035
[5 empty] | 1752.4 | 1513.4 | 0.37035
[5 empty] | 1752.6 | 1513.6 | 0.37035
[5 empty] | 1752.8 | 1513.8 | 0.37035
[5 empty] | 1753 | 1514 | 0.37035
[5 empty] | 1753.2 | 1514.2 | 0.46777
[5 empty] | 1753.4 | 1514.4 | 0.46777
[5 empty] | 1753.6 | 1514.6 | 0.37035
[5 empty] | 1753.8 | 1514.8 | 0.37035
[5 empty] | 1754 | 1515 | 0.37035
[5 empty] | 1754.2 | 1515.2 | 0.46777
[5 empty] | 1754.4 | 1515.4 | 0.37035
[5 empty] | 1754.6 | 1515.6 | 0.37035
[5 empty] | 1754.8 | 1515.8 | 0.37035
[5 empty] | 1755 | 1516 | 0.46777
[5 empty] | 1755.2 | 1516.2 | 0.37035
[5 empty] | 1755.4 | 1516.4 | 0.37035
[5 empty] | 1755.6 | 1516.6 | 0.46777
[5 empty] | 1755.8 | 1516.8 | 0.46777
[5 empty] | 1756 | 1517 | 0.37035
[5 empty] | 1756.2 | 1517.2 | 0.37035
[5 empty] | 1756.4 | 1517.4 | 0.37035
[5 empty] | 1756.6 | 1517.6 | 0.37035
[5 empty] | 1756.8 | 1517.8 | 0.46777
[5 empty] | 1757 | 1518 | 0.37035
[5 empty] | 1757.2 | 1518.2 | 0.37035
[5 empty] | 1757.4 | 1518.4 | 0.46777
[5 empty] | 1757.6 | 1518.6 | 0.46777
[5 empty] | 1757.8 | 1518.8 | 0.46777
[5 empty] | 1758 | 1519 | 0.37035
[5 empty] | 1758.2 | 1519.2 | 0.46777
[5 empty] | 1758.4 | 1519.4 | 0.46777
[5 empty] | 1758.6 | 1519.6 | 0.46777
[5 empty] | 1758.8 | 1519.8 | 0.37035
[5 empty] | 1759 | 1520 | 0.37035
[5 empty] | 1759.2 | 1520.2 | 0.46777
[5 empty] | 1759.4 | 1520.4 | 0.46777
[5 empty] | 1759.6 | 1520.6 | 0.37035
[5 empty] | 1759.8 | 1520.8 | 0.37035
[5 empty] | 1760 | 1521 | 0.46777
[5 empty] | 1760.2 | 1521.2 | 0.37035
[5 empty] | 1760.4 | 1521.4 | 0.37035
[5 empty] | 1760.6 | 1521.6 | 0.46777
[5 empty] | 1760.8 | 1521.8 | 0.46777
[5 empty] | 1761 | 1522 | 0.37035
[5 empty] | 1761.2 | 1522.2 | 0.27297
[5 empty] | 1761.4 | 1522.4 | 0.37035
[5 empty] | 1761.6 | 1522.6 | 0.46777
[5 empty] | 1761.8 | 1522.8 | 0.46777
[5 empty] | 1762 | 1523 | 0.37035
[5 empty] | 1762.2 | 1523.2 | 0.37035
[5 empty] | 1762.4 | 1523.4 | 0.46777
[5 empty] | 1762.6 | 1523.6 | 0.37035
[5 empty] | 1762.8 | 1523.8 | 0.46777
[5 empty] | 1763 | 1524 | 0.37035
[5 empty] | 1763.2 | 1524.2 | 0.37035
[5 empty] | 1763.4 | 1524.4 | 0.37035
[5 empty] | 1763.6 | 1524.6 | 0.37035
[5 empty] | 1763.8 | 1524.8 | 0.37035
[5 empty] | 1764 | 1525 | 0.37035
[5 empty] | 1764.2 | 1525.2 | 0.37035
[5 empty] | 1764.4 | 1525.4 | 0.37035
[5 empty] | 1764.6 | 1525.6 | 0.078174
[5 empty] | 1764.8 | 1525.8 | 0.37035
[5 empty] | 1765 | 1526 | 0.37035
[5 empty] | 1765.2 | 1526.2 | 0.37035
[5 empty] | 1765.4 | 1526.4 | 0.37035
[5 empty] | 1765.6 | 1526.6 | 0.37035
[5 empty] | 1765.8 | 1526.8 | 0.17559
[5 empty] | 1766 | 1527 | 0.37035
[5 empty] | 1766.2 | 1527.2 | 0.46777
[5 empty] | 1766.4 | 1527.4 | 0.37035
[5 empty] | 1766.6 | 1527.6 | 0.37035
[5 empty] | 1766.8 | 1527.8 | 0.37035
[5 empty] | 1767 | 1528 | 0.37035
[5 empty] | 1767.2 | 1528.2 | 0.37035
[5 empty] | 1767.4 | 1528.4 | 0.27297
[5 empty] | 1767.6 | 1528.6 | 0.37035
[5 empty] | 1767.8 | 1528.8 | 0.46777
[5 empty] | 1768 | 1529 | 0.37035
[5 empty] | 1768.2 | 1529.2 | 0.46777
[5 empty] | 1768.4 | 1529.4 | 0.37035
[5 empty] | 1768.6 | 1529.6 | 0.37035
[5 empty] | 1768.8 | 1529.8 | 0.37035
[5 empty] | 1769 | 1530 | 0.37035
[5 empty] | 1769.2 | 1530.2 | 0.46777
[5 empty] | 1769.4 | 1530.4 | 0.37035
[5 empty] | 1769.6 | 1530.6 | 0.37035
[5 empty] | 1769.8 | 1530.8 | 0.37035
[5 empty] | 1770 | 1531 | 0.37035
[5 empty] | 1770.2 | 1531.2 | 0.46777
[5 empty] | 1770.4 | 1531.4 | 0.37035
[5 empty] | 1770.6 | 1531.6 | 0.37035
[5 empty] | 1770.8 | 1531.8 | 0.37035
[5 empty] | 1771 | 1532 | 0.66258
[5 empty] | 1771.2 | 1532.2 | 0.37035
[5 empty] | 1771.4 | 1532.4 | 0.37035
[5 empty] | 1771.6 | 1532.6 | 0.37035
[5 empty] | 1771.8 | 1532.8 | 0.37035
[5 empty] | 1772 | 1533 | 0.37035
[5 empty] | 1772.2 | 1533.2 | 0.37035
[5 empty] | 1772.4 | 1533.4 | 0.46777
[5 empty] | 1772.6 | 1533.6 | 0.37035
[5 empty] | 1772.8 | 1533.8 | 0.37035
[5 empty] | 1773 | 1534 | 0.37035
[5 empty] | 1773.2 | 1534.2 | 0.37035
[5 empty] | 1773.4 | 1534.4 | 0.37035
[5 empty] | 1773.6 | 1534.6 | 0.37035
[5 empty] | 1773.8 | 1534.8 | 0.37035
[5 empty] | 1774 | 1535 | 0.37035
[5 empty] | 1774.2 | 1535.2 | 0.37035
[5 empty] | 1774.4 | 1535.4 | 0.37035
[5 empty] | 1774.6 | 1535.6 | 0.37035
[5 empty] | 1774.8 | 1535.8 | 0.37035
[5 empty] | 1775 | 1536 | 0.46777
[5 empty] | 1775.2 | 1536.2 | 0.37035
[5 empty] | 1775.4 | 1536.4 | 0.37035
[5 empty] | 1775.6 | 1536.6 | 0.37035
[5 empty] | 1775.8 | 1536.8 | 0.37035
[5 empty] | 1776 | 1537 | 0.46777
[5 empty] | 1776.2 | 1537.2 | 0.37035
[5 empty] | 1776.4 | 1537.4 | 0.37035
[5 empty] | 1776.6 | 1537.6 | 0.46777
[5 empty] | 1776.8 | 1537.8 | 0.37035
[5 empty] | 1777 | 1538 | 0.37035
[5 empty] | 1777.2 | 1538.2 | 0.37035
[5 empty] | 1777.4 | 1538.4 | 0.46777
[5 empty] | 1777.6 | 1538.6 | 0.37035
[5 empty] | 1777.8 | 1538.8 | 0.37035
[5 empty] | 1778 | 1539 | 0.37035
[5 empty] | 1778.2 | 1539.2 | 0.46777
[5 empty] | 1778.4 | 1539.4 | 0.37035
[5 empty] | 1778.6 | 1539.6 | 0.46777
[5 empty] | 1778.8 | 1539.8 | 0.37035
[5 empty] | 1779 | 1540 | 0.37035
[5 empty] | 1779.2 | 1540.2 | 0.37035
[5 empty] | 1779.4 | 1540.4 | 0.37035
[5 empty] | 1779.6 | 1540.6 | 0.37035
[5 empty] | 1779.8 | 1540.8 | 0.37035
[5 empty] | 1780 | 1541 | 0.37035
[5 empty] | 1780.2 | 1541.2 | 0.46777
[5 empty] | 1780.4 | 1541.4 | 0.46777
[5 empty] | 1780.6 | 1541.6 | 0.46777
[5 empty] | 1780.8 | 1541.8 | 0.37035
[5 empty] | 1781 | 1542 | 0.37035
[5 empty] | 1781.2 | 1542.2 | 0.37035
[5 empty] | 1781.4 | 1542.4 | 0.37035
[5 empty] | 1781.6 | 1542.6 | 0.46777
[5 empty] | 1781.8 | 1542.8 | 0.46777
[5 empty] | 1782 | 1543 | 0.37035
[5 empty] | 1782.2 | 1543.2 | 0.46777
[5 empty] | 1782.4 | 1543.4 | 0.37035
[5 empty] | 1782.6 | 1543.6 | 0.37035
[5 empty] | 1782.8 | 1543.8 | 0.37035
[5 empty] | 1783 | 1544 | 0.37035
[5 empty] | 1783.2 | 1544.2 | 0.46777
[5 empty] | 1783.4 | 1544.4 | 0.37035
[5 empty] | 1783.6 | 1544.6 | 0.46777
[5 empty] | 1783.8 | 1544.8 | 0.37035
[5 empty] | 1784 | 1545 | 0.46777
[5 empty] | 1784.2 | 1545.2 | 0.37035
[5 empty] | 1784.4 | 1545.4 | 0.46777
[5 empty] | 1784.6 | 1545.6 | 0.46777
[5 empty] | 1784.8 | 1545.8 | 0.46777
[5 empty] | 1785 | 1546 | 0.37035
[5 empty] | 1785.2 | 1546.2 | 0.46777
[5 empty] | 1785.4 | 1546.4 | 0.37035
[5 empty] | 1785.6 | 1546.6 | 0.37035
[5 empty] | 1785.8 | 1546.8 | 0.46777
[5 empty] | 1786 | 1547 | 0.46777
[5 empty] | 1786.2 | 1547.2 | 0.37035
[5 empty] | 1786.4 | 1547.4 | 0.46777
[5 empty] | 1786.6 | 1547.6 | 0.46777
[5 empty] | 1786.8 | 1547.8 | 0.37035
[5 empty] | 1787 | 1548 | 0.37035
[5 empty] | 1787.2 | 1548.2 | 0.37035
[5 empty] | 1787.4 | 1548.4 | 0.37035
[5 empty] | 1787.6 | 1548.6 | 0.37035
[5 empty] | 1787.8 | 1548.8 | 0.46777
[5 empty] | 1788 | 1549 | 0.37035
[5 empty] | 1788.2 | 1549.2 | 0.37035
[5 empty] | 1788.4 | 1549.4 | 0.37035
[5 empty] | 1788.6 | 1549.6 | 0.37035
[5 empty] | 1788.8 | 1549.8 | 0.46777
[5 empty] | 1789 | 1550 | 0.46777
[5 empty] | 1789.2 | 1550.2 | 0.37035
[5 empty] | 1789.4 | 1550.4 | 0.46777
[5 empty] | 1789.6 | 1550.6 | 0.46777
[5 empty] | 1789.8 | 1550.8 | 0.37035
[5 empty] | 1790 | 1551 | 0.46777
[5 empty] | 1790.2 | 1551.2 | 0.46777
[5 empty] | 1790.4 | 1551.4 | 0.37035
[5 empty] | 1790.6 | 1551.6 | 0.37035
[5 empty] | 1790.8 | 1551.8 | 0.37035
[5 empty] | 1791 | 1552 | 0.46777
[5 empty] | 1791.2 | 1552.2 | 0.46777
[5 empty] | 1791.4 | 1552.4 | 0.37035
[5 empty] | 1791.6 | 1552.6 | 0.46777
[5 empty] | 1791.8 | 1552.8 | 0.46777
[5 empty] | 1792 | 1553 | 0.37035
[5 empty] | 1792.2 | 1553.2 | 0.46777
[5 empty] | 1792.4 | 1553.4 | 0.46777
[5 empty] | 1792.6 | 1553.6 | 0.46777
[5 empty] | 1792.8 | 1553.8 | 0.46777
[5 empty] | 1793 | 1554 | 0.37035
[5 empty] | 1793.2 | 1554.2 | 0.37035
[5 empty] | 1793.4 | 1554.4 | 0.37035
[5 empty] | 1793.6 | 1554.6 | 0.46777
[5 empty] | 1793.8 | 1554.8 | 0.37035
[5 empty] | 1794 | 1555 | 0.37035
[5 empty] | 1794.2 | 1555.2 | 0.37035
[5 empty] | 1794.4 | 1555.4 | 0.37035
[5 empty] | 1794.6 | 1555.6 | 0.46777
[5 empty] | 1794.8 | 1555.8 | 0.37035
[5 empty] | 1795 | 1556 | 0.46777
[5 empty] | 1795.2 | 1556.2 | 0.37035
[5 empty] | 1795.4 | 1556.4 | 0.37035
[5 empty] | 1795.6 | 1556.6 | 0.46777
[5 empty] | 1795.8 | 1556.8 | 0.46777
[5 empty] | 1796 | 1557 | 0.46777
[5 empty] | 1796.2 | 1557.2 | 0.46777
[5 empty] | 1796.4 | 1557.4 | 0.37035
[5 empty] | 1796.6 | 1557.6 | 0.37035
[5 empty] | 1796.8 | 1557.8 | 0.46777
[5 empty] | 1797 | 1558 | 0.37035
[5 empty] | 1797.2 | 1558.2 | 0.37035
[5 empty] | 1797.4 | 1558.4 | 0.37035
[5 empty] | 1797.6 | 1558.6 | 0.46777
[5 empty] | 1797.8 | 1558.8 | 0.37035
[5 empty] | 1798 | 1559 | 0.37035
[5 empty] | 1798.2 | 1559.2 | 0.46777
[5 empty] | 1798.4 | 1559.4 | 0.46777
[5 empty] | 1798.6 | 1559.6 | 0.37035
[5 empty] | 1798.8 | 1559.8 | 0.46777
[5 empty] | 1799 | 1560 | 0.37035
[5 empty] | 1799.2 | 1560.2 | 0.46777
[5 empty] | 1799.4 | 1560.4 | 0.46777
[5 empty] | 1799.6 | 1560.6 | 0.37035
[5 empty] | 1799.8 | 1560.8 | 0.46777
[5 empty] | 1800 | 1561 | 0.37035
[5 empty] | 1800.2 | 1561.2 | 0.37035
[5 empty] | 1800.4 | 1561.4 | 0.46777
[5 empty] | 1800.6 | 1561.6 | 0.37035
[5 empty] | 1800.8 | 1561.8 | 0.46777
[5 empty] | 1801 | 1562 | 0.46777
[5 empty] | 1801.2 | 1562.2 | 0.37035
[5 empty] | 1801.4 | 1562.4 | 0.46777
[5 empty] | 1801.6 | 1562.6 | 0.46777
[5 empty] | 1801.8 | 1562.8 | 0.46777
[5 empty] | 1802 | 1563 | 0.46777
[5 empty] | 1802.2 | 1563.2 | 0.46777
[5 empty] | 1802.4 | 1563.4 | 0.46777
[5 empty] | 1802.6 | 1563.6 | 0.46777
[5 empty] | 1802.8 | 1563.8 | 0.46777
[5 empty] | 1803 | 1564 | 0.46777
[5 empty] | 1803.2 | 1564.2 | 0.37035
[5 empty] | 1803.4 | 1564.4 | 0.46777
[5 empty] | 1803.6 | 1564.6 | 0.46777
[5 empty] | 1803.8 | 1564.8 | 0.46777
[5 empty] | 1804 | 1565 | 0.37035
[5 empty] | 1804.2 | 1565.2 | 0.37035
[5 empty] | 1804.4 | 1565.4 | 0.46777
[5 empty] | 1804.6 | 1565.6 | 0.46777
[5 empty] | 1804.8 | 1565.8 | 0.46777
[5 empty] | 1805 | 1566 | 0.46777
[5 empty] | 1805.2 | 1566.2 | 0.37035
[5 empty] | 1805.4 | 1566.4 | 0.37035
[5 empty] | 1805.6 | 1566.6 | 0.46777
[5 empty] | 1805.8 | 1566.8 | 0.37035
[5 empty] | 1806 | 1567 | 0.46777
[5 empty] | 1806.2 | 1567.2 | 0.46777
[5 empty] | 1806.4 | 1567.4 | 0.46777
[5 empty] | 1806.6 | 1567.6 | 0.46777
[5 empty] | 1806.8 | 1567.8 | 0.37035
[5 empty] | 1807 | 1568 | 0.46777
[5 empty] | 1807.2 | 1568.2 | 0.37035
[5 empty] | 1807.4 | 1568.4 | 0.46777
[5 empty] | 1807.6 | 1568.6 | 0.37035
[5 empty] | 1807.8 | 1568.8 | 0.75996
[5 empty] | 1808 | 1569 | 0.37035
[5 empty] | 1808.2 | 1569.2 | 0.37035
[5 empty] | 1808.4 | 1569.4 | 0.37035
[5 empty] | 1808.6 | 1569.6 | 0.46777
[5 empty] | 1808.8 | 1569.8 | 0.37035
[5 empty] | 1809 | 1570 | 0.46777
[5 empty] | 1809.2 | 1570.2 | 0.46777
[5 empty] | 1809.4 | 1570.4 | 0.46777
[5 empty] | 1809.6 | 1570.6 | 0.37035
[5 empty] | 1809.8 | 1570.8 | 0.46777
[5 empty] | 1810 | 1571 | 0.37035
[5 empty] | 1810.2 | 1571.2 | 0.37035
[5 empty] | 1810.4 | 1571.4 | 0.46777
[5 empty] | 1810.6 | 1571.6 | 0.37035
[5 empty] | 1810.8 | 1571.8 | 0.37035
[5 empty] | 1811 | 1572 | 0.46777
[5 empty] | 1811.2 | 1572.2 | 0.37035
[5 empty] | 1811.4 | 1572.4 | 0.37035
[5 empty] | 1811.6 | 1572.6 | 0.46777
[5 empty] | 1811.8 | 1572.8 | 0.37035
[5 empty] | 1812 | 1573 | 0.37035
[5 empty] | 1812.2 | 1573.2 | 0.46777
[5 empty] | 1812.4 | 1573.4 | 0.37035
[5 empty] | 1812.6 | 1573.6 | 0.46777
[5 empty] | 1812.8 | 1573.8 | 0.37035
[5 empty] | 1813 | 1574 | 0.37035
[5 empty] | 1813.2 | 1574.2 | 0.37035
[5 empty] | 1813.4 | 1574.4 | 0.37035
[5 empty] | 1813.6 | 1574.6 | 0.37035
[5 empty] | 1813.8 | 1574.8 | 0.46777
[5 empty] | 1814 | 1575 | 0.37035
[5 empty] | 1814.2 | 1575.2 | 0.37035
[5 empty] | 1814.4 | 1575.4 | 0.37035
[5 empty] | 1814.6 | 1575.6 | 0.46777
[5 empty] | 1814.8 | 1575.8 | 0.37035
[5 empty] | 1815 | 1576 | 0.46777
[5 empty] | 1815.2 | 1576.2 | 0.46777
[5 empty] | 1815.4 | 1576.4 | 0.46777
[5 empty] | 1815.6 | 1576.6 | 0.37035
[5 empty] | 1815.8 | 1576.8 | 0.46777
[5 empty] | 1816 | 1577 | 0.46777
[5 empty] | 1816.2 | 1577.2 | 0.37035
[5 empty] | 1816.4 | 1577.4 | 0.37035
[5 empty] | 1816.6 | 1577.6 | 0.37035
[5 empty] | 1816.8 | 1577.8 | 0.46777
[5 empty] | 1817 | 1578 | 0.37035
[5 empty] | 1817.2 | 1578.2 | 0.37035
[5 empty] | 1817.4 | 1578.4 | 0.37035
[5 empty] | 1817.6 | 1578.6 | 0.37035
[5 empty] | 1817.8 | 1578.8 | 0.37035
[5 empty] | 1818 | 1579 | 0.37035
[5 empty] | 1818.2 | 1579.2 | 0.46777
[5 empty] | 1818.4 | 1579.4 | 0.37035
[5 empty] | 1818.6 | 1579.6 | 0.46777
[5 empty] | 1818.8 | 1579.8 | 0.46777
[5 empty] | 1819 | 1580 | 0.46777
[5 empty] | 1819.2 | 1580.2 | 0.37035
[5 empty] | 1819.4 | 1580.4 | 0.37035
[5 empty] | 1819.6 | 1580.6 | 0.37035
[5 empty] | 1819.8 | 1580.8 | 0.37035
[5 empty] | 1820 | 1581 | 0.37035
[5 empty] | 1820.2 | 1581.2 | 0.46777
[5 empty] | 1820.4 | 1581.4 | 0.37035
[5 empty] | 1820.6 | 1581.6 | 0.37035
[5 empty] | 1820.8 | 1581.8 | 0.37035
[5 empty] | 1821 | 1582 | 0.46777
[5 empty] | 1821.2 | 1582.2 | 0.46777
[5 empty] | 1821.4 | 1582.4 | 0.46777
[5 empty] | 1821.6 | 1582.6 | 0.37035
[5 empty] | 1821.8 | 1582.8 | 0.37035
[5 empty] | 1822 | 1583 | 0.37035
[5 empty] | 1822.2 | 1583.2 | 0.56516
[5 empty] | 1822.4 | 1583.4 | 0.46777
[5 empty] | 1822.6 | 1583.6 | 0.46777
[5 empty] | 1822.8 | 1583.8 | 0.37035
[5 empty] | 1823 | 1584 | 0.37035
[5 empty] | 1823.2 | 1584.2 | 0.37035
[5 empty] | 1823.4 | 1584.4 | 0.37035
[5 empty] | 1823.6 | 1584.6 | 0.37035
[5 empty] | 1823.8 | 1584.8 | 0.37035
[5 empty] | 1824 | 1585 | 0.37035
[5 empty] | 1824.2 | 1585.2 | 0.37035
[5 empty] | 1824.4 | 1585.4 | 0.46777
[5 empty] | 1824.6 | 1585.6 | 0.37035
[5 empty] | 1824.8 | 1585.8 | 0.37035
[5 empty] | 1825 | 1586 | 0.37035
[5 empty] | 1825.2 | 1586.2 | 0.37035
[5 empty] | 1825.4 | 1586.4 | 0.37035
[5 empty] | 1825.6 | 1586.6 | 0.46777
[5 empty] | 1825.8 | 1586.8 | 0.37035
[5 empty] | 1826 | 1587 | 0.37035
[5 empty] | 1826.2 | 1587.2 | 0.37035
[5 empty] | 1826.4 | 1587.4 | 0.37035
[5 empty] | 1826.6 | 1587.6 | 0.37035
[5 empty] | 1826.8 | 1587.8 | 0.37035
[5 empty] | 1827 | 1588 | 0.46777
[5 empty] | 1827.2 | 1588.2 | 0.37035
[5 empty] | 1827.4 | 1588.4 | 0.46777
[5 empty] | 1827.6 | 1588.6 | -0.11663
[5 empty] | 1827.8 | 1588.8 | 0.37035
[5 empty] | 1828 | 1589 | 0.46777
[5 empty] | 1828.2 | 1589.2 | 0.37035
[5 empty] | 1828.4 | 1589.4 | 0.46777
[5 empty] | 1828.6 | 1589.6 | 0.46777
[5 empty] | 1828.8 | 1589.8 | 0.46777
[5 empty] | 1829 | 1590 | 0.46777
[5 empty] | 1829.2 | 1590.2 | 0.46777
[5 empty] | 1829.4 | 1590.4 | 0.37035
[5 empty] | 1829.6 | 1590.6 | 0.37035
[5 empty] | 1829.8 | 1590.8 | 0.56516
[5 empty] | 1830 | 1591 | 0.37035
[5 empty] | 1830.2 | 1591.2 | 0.46777
[5 empty] | 1830.4 | 1591.4 | 0.46777
[5 empty] | 1830.6 | 1591.6 | 0.46777
[5 empty] | 1830.8 | 1591.8 | 0.46777
[5 empty] | 1831 | 1592 | 0.46777
[5 empty] | 1831.2 | 1592.2 | 0.37035
[5 empty] | 1831.4 | 1592.4 | 0.37035
[5 empty] | 1831.6 | 1592.6 | 0.46777
[5 empty] | 1831.8 | 1592.8 | 0.37035
[5 empty] | 1832 | 1593 | 0.37035
[5 empty] | 1832.2 | 1593.2 | 0.46777
[5 empty] | 1832.4 | 1593.4 | 0.37035
[5 empty] | 1832.6 | 1593.6 | 0.46777
[5 empty] | 1832.8 | 1593.8 | 0.46777
[5 empty] | 1833 | 1594 | 0.37035
[5 empty] | 1833.2 | 1594.2 | 0.46777
[5 empty] | 1833.4 | 1594.4 | 0.37035
[5 empty] | 1833.6 | 1594.6 | 0.46777
[5 empty] | 1833.8 | 1594.8 | 0.37035
[5 empty] | 1834 | 1595 | 0.46777
[5 empty] | 1834.2 | 1595.2 | 0.56516
[5 empty] | 1834.4 | 1595.4 | 0.37035
[5 empty] | 1834.6 | 1595.6 | 0.37035
[5 empty] | 1834.8 | 1595.8 | 0.37035
[5 empty] | 1835 | 1596 | 0.46777
[5 empty] | 1835.2 | 1596.2 | 0.37035
[5 empty] | 1835.4 | 1596.4 | 0.46777
[5 empty] | 1835.6 | 1596.6 | 0.37035
[5 empty] | 1835.8 | 1596.8 | 0.37035
[5 empty] | 1836 | 1597 | 0.46777
[5 empty] | 1836.2 | 1597.2 | 0.27297
[5 empty] | 1836.4 | 1597.4 | 0.46777
[5 empty] | 1836.6 | 1597.6 | 0.37035
[5 empty] | 1836.8 | 1597.8 | 0.46777
[5 empty] | 1837 | 1598 | 0.37035
[5 empty] | 1837.2 | 1598.2 | 0.46777
[5 empty] | 1837.4 | 1598.4 | 0.46777
[5 empty] | 1837.6 | 1598.6 | 0.46777
[5 empty] | 1837.8 | 1598.8 | 0.46777
[5 empty] | 1838 | 1599 | 0.46777
[5 empty] | 1838.2 | 1599.2 | 0.37035
[5 empty] | 1838.4 | 1599.4 | 0.46777
[5 empty] | 1838.6 | 1599.6 | 0.46777
[5 empty] | 1838.8 | 1599.8 | 0.37035
[5 empty] | 1839 | 1600 | 0.46777
[5 empty] | 1839.2 | 1600.2 | 0.46777
[5 empty] | 1839.4 | 1600.4 | 0.37035
[5 empty] | 1839.6 | 1600.6 | 0.37035
[5 empty] | 1839.8 | 1600.8 | 0.46777
[5 empty] | 1840 | 1601 | 0.37035
[5 empty] | 1840.2 | 1601.2 | 0.37035
[5 empty] | 1840.4 | 1601.4 | 0.46777
[5 empty] | 1840.6 | 1601.6 | 0.46777
[5 empty] | 1840.8 | 1601.8 | 0.46777
[5 empty] | 1841 | 1602 | 0.46777
[5 empty] | 1841.2 | 1602.2 | 0.46777
[5 empty] | 1841.4 | 1602.4 | 0.46777
[5 empty] | 1841.6 | 1602.6 | 0.37035
[5 empty] | 1841.8 | 1602.8 | 0.46777
[5 empty] | 1842 | 1603 | 0.37035
[5 empty] | 1842.2 | 1603.2 | 0.37035
[5 empty] | 1842.4 | 1603.4 | 0.37035
[5 empty] | 1842.6 | 1603.6 | 0.46777
[5 empty] | 1842.8 | 1603.8 | 0.46777
[5 empty] | 1843 | 1604 | 0.46777
[5 empty] | 1843.2 | 1604.2 | 0.46777
[5 empty] | 1843.4 | 1604.4 | 0.46777
[5 empty] | 1843.6 | 1604.6 | 0.37035
[5 empty] | 1843.8 | 1604.8 | 0.46777
[5 empty] | 1844 | 1605 | 0.46777
[5 empty] | 1844.2 | 1605.2 | 0.37035
[5 empty] | 1844.4 | 1605.4 | 0.46777
[5 empty] | 1844.6 | 1605.6 | 0.46777
[5 empty] | 1844.8 | 1605.8 | 0.46777
[5 empty] | 1845 | 1606 | 0.46777
[5 empty] | 1845.2 | 1606.2 | 0.37035
[5 empty] | 1845.4 | 1606.4 | 0.37035
[5 empty] | 1845.6 | 1606.6 | 0.37035
[5 empty] | 1845.8 | 1606.8 | 0.37035
[5 empty] | 1846 | 1607 | 0.37035
[5 empty] | 1846.2 | 1607.2 | 0.37035
[5 empty] | 1846.4 | 1607.4 | 0.46777
[5 empty] | 1846.6 | 1607.6 | 0.46777
[5 empty] | 1846.8 | 1607.8 | 0.46777
[5 empty] | 1847 | 1608 | 0.46777
[5 empty] | 1847.2 | 1608.2 | 0.46777
[5 empty] | 1847.4 | 1608.4 | 0.46777
[5 empty] | 1847.6 | 1608.6 | 0.46777
[5 empty] | 1847.8 | 1608.8 | 0.37035
[5 empty] | 1848 | 1609 | 0.46777
[5 empty] | 1848.2 | 1609.2 | 0.37035
[5 empty] | 1848.4 | 1609.4 | 0.37035
[5 empty] | 1848.6 | 1609.6 | 0.37035
[5 empty] | 1848.8 | 1609.8 | 0.46777
[5 empty] | 1849 | 1610 | 0.37035
[5 empty] | 1849.2 | 1610.2 | 0.46777
[5 empty] | 1849.4 | 1610.4 | 0.46777
[5 empty] | 1849.6 | 1610.6 | 0.46777
[5 empty] | 1849.8 | 1610.8 | 0.37035
[5 empty] | 1850 | 1611 | 0.46777
[5 empty] | 1850.2 | 1611.2 | 0.46777
[5 empty] | 1850.4 | 1611.4 | 0.46777
[5 empty] | 1850.6 | 1611.6 | 0.46777
[5 empty] | 1850.8 | 1611.8 | 0.56516
[5 empty] | 1851 | 1612 | 0.46777
[5 empty] | 1851.2 | 1612.2 | 0.46777
[5 empty] | 1851.4 | 1612.4 | 0.46777
[5 empty] | 1851.6 | 1612.6 | 0.37035
[5 empty] | 1851.8 | 1612.8 | 0.46777
[5 empty] | 1852 | 1613 | 0.46777
[5 empty] | 1852.2 | 1613.2 | 0.37035
[5 empty] | 1852.4 | 1613.4 | 0.46777
[5 empty] | 1852.6 | 1613.6 | 0.46777
[5 empty] | 1852.8 | 1613.8 | 0.078174
[5 empty] | 1853 | 1614 | 0.46777
[5 empty] | 1853.2 | 1614.2 | 0.46777
[5 empty] | 1853.4 | 1614.4 | 0.46777
[5 empty] | 1853.6 | 1614.6 | 0.46777
[5 empty] | 1853.8 | 1614.8 | 0.46777
[5 empty] | 1854 | 1615 | 0.46777
[5 empty] | 1854.2 | 1615.2 | 0.37035
[5 empty] | 1854.4 | 1615.4 | 0.37035
[5 empty] | 1854.6 | 1615.6 | 0.46777
[5 empty] | 1854.8 | 1615.8 | 0.46777
[5 empty] | 1855 | 1616 | 0.46777
[5 empty] | 1855.2 | 1616.2 | 0.37035
[5 empty] | 1855.4 | 1616.4 | 0.46777
[5 empty] | 1855.6 | 1616.6 | 0.46777
[5 empty] | 1855.8 | 1616.8 | 0.46777
[5 empty] | 1856 | 1617 | 0.46777
[5 empty] | 1856.2 | 1617.2 | 0.37035
[5 empty] | 1856.4 | 1617.4 | 0.46777
[5 empty] | 1856.6 | 1617.6 | 0.37035
[5 empty] | 1856.8 | 1617.8 | 0.46777
[5 empty] | 1857 | 1618 | 0.46777
[5 empty] | 1857.2 | 1618.2 | 0.46777
[5 empty] | 1857.4 | 1618.4 | 0.46777
[5 empty] | 1857.6 | 1618.6 | 0.46777
[5 empty] | 1857.8 | 1618.8 | 0.37035
[5 empty] | 1858 | 1619 | 0.46777
[5 empty] | 1858.2 | 1619.2 | 0.46777
[5 empty] | 1858.4 | 1619.4 | 0.37035
[5 empty] | 1858.6 | 1619.6 | 0.46777
[5 empty] | 1858.8 | 1619.8 | 0.46777
[5 empty] | 1859 | 1620 | 0.46777
[5 empty] | 1859.2 | 1620.2 | 0.46777
[5 empty] | 1859.4 | 1620.4 | 0.37035
[5 empty] | 1859.6 | 1620.6 | 0.46777
[5 empty] | 1859.8 | 1620.8 | 0.37035
[5 empty] | 1860 | 1621 | 0.37035
[5 empty] | 1860.2 | 1621.2 | 0.46777
[5 empty] | 1860.4 | 1621.4 | 0.37035
[5 empty] | 1860.6 | 1621.6 | 0.46777
[5 empty] | 1860.8 | 1621.8 | 0.46777
[5 empty] | 1861 | 1622 | 0.37035
[5 empty] | 1861.2 | 1622.2 | 0.37035
[5 empty] | 1861.4 | 1622.4 | 0.37035
[5 empty] | 1861.6 | 1622.6 | 0.46777
[5 empty] | 1861.8 | 1622.8 | 0.46777
[5 empty] | 1862 | 1623 | 0.37035
[5 empty] | 1862.2 | 1623.2 | 0.46777
[5 empty] | 1862.4 | 1623.4 | 0.46777
[5 empty] | 1862.6 | 1623.6 | 0.37035
[5 empty] | 1862.8 | 1623.8 | 0.37035
[5 empty] | 1863 | 1624 | 0.46777
[5 empty] | 1863.2 | 1624.2 | 0.37035
[5 empty] | 1863.4 | 1624.4 | 0.37035
[5 empty] | 1863.6 | 1624.6 | 0.46777
[5 empty] | 1863.8 | 1624.8 | 0.37035
[5 empty] | 1864 | 1625 | 0.37035
[5 empty] | 1864.2 | 1625.2 | 0.37035
[5 empty] | 1864.4 | 1625.4 | 0.37035
[5 empty] | 1864.6 | 1625.6 | 0.46777
[5 empty] | 1864.8 | 1625.8 | 0.46777
[5 empty] | 1865 | 1626 | 0.37035
[5 empty] | 1865.2 | 1626.2 | 0.37035
[5 empty] | 1865.4 | 1626.4 | 0.46777
[5 empty] | 1865.6 | 1626.6 | 0.37035
[5 empty] | 1865.8 | 1626.8 | 0.37035
[5 empty] | 1866 | 1627 | 0.37035
[5 empty] | 1866.2 | 1627.2 | 0.37035
[5 empty] | 1866.4 | 1627.4 | 0.37035
[5 empty] | 1866.6 | 1627.6 | 0.37035
[5 empty] | 1866.8 | 1627.8 | 0.37035
[5 empty] | 1867 | 1628 | 0.37035
[5 empty] | 1867.2 | 1628.2 | 0.46777
[5 empty] | 1867.4 | 1628.4 | 0.46777
[5 empty] | 1867.6 | 1628.6 | 0.37035
[5 empty] | 1867.8 | 1628.8 | 0.37035
[5 empty] | 1868 | 1629 | 0.46777
[5 empty] | 1868.2 | 1629.2 | 0.37035
[5 empty] | 1868.4 | 1629.4 | 0.37035
[5 empty] | 1868.6 | 1629.6 | 0.37035
[5 empty] | 1868.8 | 1629.8 | 0.37035
[5 empty] | 1869 | 1630 | 0.37035
[5 empty] | 1869.2 | 1630.2 | 0.37035
[5 empty] | 1869.4 | 1630.4 | 0.37035
[5 empty] | 1869.6 | 1630.6 | 0.37035
[5 empty] | 1869.8 | 1630.8 | 0.37035
[5 empty] | 1870 | 1631 | 0.37035
[5 empty] | 1870.2 | 1631.2 | 0.46777
[5 empty] | 1870.4 | 1631.4 | 0.37035
[5 empty] | 1870.6 | 1631.6 | 0.37035
[5 empty] | 1870.8 | 1631.8 | 0.46777
[5 empty] | 1871 | 1632 | 0.37035
[5 empty] | 1871.2 | 1632.2 | 0.46777
[5 empty] | 1871.4 | 1632.4 | 0.37035
[5 empty] | 1871.6 | 1632.6 | 0.37035
[5 empty] | 1871.8 | 1632.8 | 0.46777
[5 empty] | 1872 | 1633 | 0.37035
[5 empty] | 1872.2 | 1633.2 | 0.46777
[5 empty] | 1872.4 | 1633.4 | 0.46777
[5 empty] | 1872.6 | 1633.6 | 0.46777
[5 empty] | 1872.8 | 1633.8 | 0.46777
[5 empty] | 1873 | 1634 | 0.37035
[5 empty] | 1873.2 | 1634.2 | 0.37035
[5 empty] | 1873.4 | 1634.4 | 0.46777
[5 empty] | 1873.6 | 1634.6 | 0.37035
[5 empty] | 1873.8 | 1634.8 | 0.46777
[5 empty] | 1874 | 1635 | 0.46777
[5 empty] | 1874.2 | 1635.2 | 0.37035
[5 empty] | 1874.4 | 1635.4 | 0.37035
[5 empty] | 1874.6 | 1635.6 | 0.46777
[5 empty] | 1874.8 | 1635.8 | 0.37035
[5 empty] | 1875 | 1636 | 0.37035
[5 empty] | 1875.2 | 1636.2 | 0.37035
[5 empty] | 1875.4 | 1636.4 | 0.46777
[5 empty] | 1875.6 | 1636.6 | 0.37035
[5 empty] | 1875.8 | 1636.8 | 0.37035
[5 empty] | 1876 | 1637 | 0.37035
[5 empty] | 1876.2 | 1637.2 | 0.46777
[5 empty] | 1876.4 | 1637.4 | 0.46777
[5 empty] | 1876.6 | 1637.6 | 0.46777
[5 empty] | 1876.8 | 1637.8 | 0.37035
[5 empty] | 1877 | 1638 | 0.37035
[5 empty] | 1877.2 | 1638.2 | 0.46777
[5 empty] | 1877.4 | 1638.4 | 0.46777
[5 empty] | 1877.6 | 1638.6 | 0.46777
[5 empty] | 1877.8 | 1638.8 | 0.46777
[5 empty] | 1878 | 1639 | 0.37035
[5 empty] | 1878.2 | 1639.2 | 0.46777
[5 empty] | 1878.4 | 1639.4 | 0.37035
[5 empty] | 1878.6 | 1639.6 | 0.37035
[5 empty] | 1878.8 | 1639.8 | 0.37035
[5 empty] | 1879 | 1640 | 0.37035
[5 empty] | 1879.2 | 1640.2 | 0.46777
[5 empty] | 1879.4 | 1640.4 | 0.37035
[5 empty] | 1879.6 | 1640.6 | 0.46777
[5 empty] | 1879.8 | 1640.8 | 0.37035
[5 empty] | 1880 | 1641 | 0.46777
[5 empty] | 1880.2 | 1641.2 | 0.37035
[5 empty] | 1880.4 | 1641.4 | 0.46777
[5 empty] | 1880.6 | 1641.6 | 0.46777
[5 empty] | 1880.8 | 1641.8 | 0.37035
[5 empty] | 1881 | 1642 | 0.46777
[5 empty] | 1881.2 | 1642.2 | 0.37035
[5 empty] | 1881.4 | 1642.4 | 0.46777
[5 empty] | 1881.6 | 1642.6 | 0.37035
[5 empty] | 1881.8 | 1642.8 | 0.46777
[5 empty] | 1882 | 1643 | 0.37035
[5 empty] | 1882.2 | 1643.2 | 0.37035
[5 empty] | 1882.4 | 1643.4 | 0.37035
[5 empty] | 1882.6 | 1643.6 | 0.37035
[5 empty] | 1882.8 | 1643.8 | 0.37035
[5 empty] | 1883 | 1644 | 0.46777
[5 empty] | 1883.2 | 1644.2 | 0.46777
[5 empty] | 1883.4 | 1644.4 | 0.37035
[5 empty] | 1883.6 | 1644.6 | 0.37035
[5 empty] | 1883.8 | 1644.8 | 0.37035
[5 empty] | 1884 | 1645 | 0.56516
[5 empty] | 1884.2 | 1645.2 | 0.37035
[5 empty] | 1884.4 | 1645.4 | 0.46777
[5 empty] | 1884.6 | 1645.6 | 0.37035
[5 empty] | 1884.8 | 1645.8 | 0.37035
[5 empty] | 1885 | 1646 | 0.37035
[5 empty] | 1885.2 | 1646.2 | 0.37035
[5 empty] | 1885.4 | 1646.4 | 0.37035
[5 empty] | 1885.6 | 1646.6 | 0.46777
[5 empty] | 1885.8 | 1646.8 | 0.37035
[5 empty] | 1886 | 1647 | 0.56516
[5 empty] | 1886.2 | 1647.2 | 0.37035
[5 empty] | 1886.4 | 1647.4 | 0.46777
[5 empty] | 1886.6 | 1647.6 | 0.46777
[5 empty] | 1886.8 | 1647.8 | 0.37035
[5 empty] | 1887 | 1648 | 0.37035
[5 empty] | 1887.2 | 1648.2 | 0.46777
[5 empty] | 1887.4 | 1648.4 | 0.37035
[5 empty] | 1887.6 | 1648.6 | 0.37035
[5 empty] | 1887.8 | 1648.8 | 0.37035
[5 empty] | 1888 | 1649 | 0.37035
[5 empty] | 1888.2 | 1649.2 | 0.37035
[5 empty] | 1888.4 | 1649.4 | 0.37035
[5 empty] | 1888.6 | 1649.6 | 0.37035
[5 empty] | 1888.8 | 1649.8 | 0.37035
[5 empty] | 1889 | 1650 | 0.37035
[5 empty] | 1889.2 | 1650.2 | 0.37035
[5 empty] | 1889.4 | 1650.4 | 0.37035
[5 empty] | 1889.6 | 1650.6 | 0.37035
[5 empty] | 1889.8 | 1650.8 | 0.37035
[5 empty] | 1890 | 1651 | 0.37035
[5 empty] | 1890.2 | 1651.2 | 0.37035
[5 empty] | 1890.4 | 1651.4 | 0.37035
[5 empty] | 1890.6 | 1651.6 | 0.37035
[5 empty] | 1890.8 | 1651.8 | 0.46777
[5 empty] | 1891 | 1652 | 0.37035
[5 empty] | 1891.2 | 1652.2 | 0.37035
[5 empty] | 1891.4 | 1652.4 | 0.37035
[5 empty] | 1891.6 | 1652.6 | 0.37035
[5 empty] | 1891.8 | 1652.8 | 0.37035
[5 empty] | 1892 | 1653 | 0.37035
[5 empty] | 1892.2 | 1653.2 | 0.37035
[5 empty] | 1892.4 | 1653.4 | 0.37035
[5 empty] | 1892.6 | 1653.6 | 0.37035
[5 empty] | 1892.8 | 1653.8 | 0.37035
[5 empty] | 1893 | 1654 | 0.37035
[5 empty] | 1893.2 | 1654.2 | 0.37035
[5 empty] | 1893.4 | 1654.4 | 0.37035
[5 empty] | 1893.6 | 1654.6 | 0.37035
[5 empty] | 1893.8 | 1654.8 | 0.37035
[5 empty] | 1894 | 1655 | 0.37035
[5 empty] | 1894.2 | 1655.2 | 0.46777
[5 empty] | 1894.4 | 1655.4 | 0.37035
[5 empty] | 1894.6 | 1655.6 | 0.37035
[5 empty] | 1894.8 | 1655.8 | 0.37035
[5 empty] | 1895 | 1656 | 0.37035
[5 empty] | 1895.2 | 1656.2 | 0.37035
[5 empty] | 1895.4 | 1656.4 | 0.37035
[5 empty] | 1895.6 | 1656.6 | 0.37035
[5 empty] | 1895.8 | 1656.8 | 0.37035
[5 empty] | 1896 | 1657 | 0.37035
[5 empty] | 1896.2 | 1657.2 | 0.37035
[5 empty] | 1896.4 | 1657.4 | 0.37035
[5 empty] | 1896.6 | 1657.6 | 0.37035
[5 empty] | 1896.8 | 1657.8 | 0.37035
[5 empty] | 1897 | 1658 | 0.37035
[5 empty] | 1897.2 | 1658.2 | 0.46777
[5 empty] | 1897.4 | 1658.4 | 0.46777
[5 empty] | 1897.6 | 1658.6 | 0.27297
[5 empty] | 1897.8 | 1658.8 | 0.46777
[5 empty] | 1898 | 1659 | 0.37035
[5 empty] | 1898.2 | 1659.2 | 0.37035
[5 empty] | 1898.4 | 1659.4 | 0.37035
[5 empty] | 1898.6 | 1659.6 | 0.46777
[5 empty] | 1898.8 | 1659.8 | 0.46777
[5 empty] | 1899 | 1660 | 0.46777
[5 empty] | 1899.2 | 1660.2 | 0.37035
[5 empty] | 1899.4 | 1660.4 | 0.37035
[5 empty] | 1899.6 | 1660.6 | 0.46777
[5 empty] | 1899.8 | 1660.8 | 0.37035
[5 empty] | 1900 | 1661 | 0.37035
[5 empty] | 1900.2 | 1661.2 | 0.46777
[5 empty] | 1900.4 | 1661.4 | 0.37035
[5 empty] | 1900.6 | 1661.6 | 0.37035
[5 empty] | 1900.8 | 1661.8 | 0.37035
[5 empty] | 1901 | 1662 | 0.37035
[5 empty] | 1901.2 | 1662.2 | 0.46777
[5 empty] | 1901.4 | 1662.4 | 0.46777
[5 empty] | 1901.6 | 1662.6 | 0.37035
[5 empty] | 1901.8 | 1662.8 | 0.46777
[5 empty] | 1902 | 1663 | 0.37035
[5 empty] | 1902.2 | 1663.2 | 0.46777
[5 empty] | 1902.4 | 1663.4 | 0.37035
[5 empty] | 1902.6 | 1663.6 | 0.37035
[5 empty] | 1902.8 | 1663.8 | 0.46777
[5 empty] | 1903 | 1664 | 0.37035
[5 empty] | 1903.2 | 1664.2 | 0.46777
[5 empty] | 1903.4 | 1664.4 | 0.37035
[5 empty] | 1903.6 | 1664.6 | 0.46777
[5 empty] | 1903.8 | 1664.8 | 0.37035
[5 empty] | 1904 | 1665 | 0.46777
[5 empty] | 1904.2 | 1665.2 | 0.46777
[5 empty] | 1904.4 | 1665.4 | 0.37035
[5 empty] | 1904.6 | 1665.6 | 0.37035
[5 empty] | 1904.8 | 1665.8 | 0.37035
[5 empty] | 1905 | 1666 | 0.46777
[5 empty] | 1905.2 | 1666.2 | 0.46777
[5 empty] | 1905.4 | 1666.4 | 0.46777
[5 empty] | 1905.6 | 1666.6 | 0.37035
[5 empty] | 1905.8 | 1666.8 | 0.46777
[5 empty] | 1906 | 1667 | 0.46777
[5 empty] | 1906.2 | 1667.2 | 0.46777
[5 empty] | 1906.4 | 1667.4 | 0.46777
[5 empty] | 1906.6 | 1667.6 | 0.46777
[5 empty] | 1906.8 | 1667.8 | 0.37035
[5 empty] | 1907 | 1668 | 0.46777
[5 empty] | 1907.2 | 1668.2 | 0.46777
[5 empty] | 1907.4 | 1668.4 | 0.37035
[5 empty] | 1907.6 | 1668.6 | 0.46777
[5 empty] | 1907.8 | 1668.8 | 0.46777
[5 empty] | 1908 | 1669 | 0.37035
[5 empty] | 1908.2 | 1669.2 | 0.46777
[5 empty] | 1908.4 | 1669.4 | 0.37035
[5 empty] | 1908.6 | 1669.6 | 0.46777
[5 empty] | 1908.8 | 1669.8 | 0.46777
[5 empty] | 1909 | 1670 | 0.46777
[5 empty] | 1909.2 | 1670.2 | 0.46777
[5 empty] | 1909.4 | 1670.4 | 0.46777
[5 empty] | 1909.6 | 1670.6 | 0.46777
[5 empty] | 1909.8 | 1670.8 | 0.46777
[5 empty] | 1910 | 1671 | 0.46777
[5 empty] | 1910.2 | 1671.2 | 0.37035
[5 empty] | 1910.4 | 1671.4 | 0.46777
[5 empty] | 1910.6 | 1671.6 | 0.46777
[5 empty] | 1910.8 | 1671.8 | 0.37035
[5 empty] | 1911 | 1672 | 0.46777
[5 empty] | 1911.2 | 1672.2 | 0.37035
[5 empty] | 1911.4 | 1672.4 | 0.46777
[5 empty] | 1911.6 | 1672.6 | 0.46777
[5 empty] | 1911.8 | 1672.8 | 0.46777
[5 empty] | 1912 | 1673 | 0.37035
[5 empty] | 1912.2 | 1673.2 | 0.46777
[5 empty] | 1912.4 | 1673.4 | 0.46777
[5 empty] | 1912.6 | 1673.6 | 0.46777
[5 empty] | 1912.8 | 1673.8 | 0.37035
[5 empty] | 1913 | 1674 | 0.46777
[5 empty] | 1913.2 | 1674.2 | 0.46777
[5 empty] | 1913.4 | 1674.4 | 0.46777
[5 empty] | 1913.6 | 1674.6 | 0.46777
[5 empty] | 1913.8 | 1674.8 | 0.37035
[5 empty] | 1914 | 1675 | 0.46777
[5 empty] | 1914.2 | 1675.2 | 0.46777
[5 empty] | 1914.4 | 1675.4 | 0.46777
[5 empty] | 1914.6 | 1675.6 | 0.37035
[5 empty] | 1914.8 | 1675.8 | 0.37035
[5 empty] | 1915 | 1676 | 0.46777
[5 empty] | 1915.2 | 1676.2 | 0.37035
[5 empty] | 1915.4 | 1676.4 | 0.46777
[5 empty] | 1915.6 | 1676.6 | 0.37035
[5 empty] | 1915.8 | 1676.8 | 0.37035
[5 empty] | 1916 | 1677 | 0.46777
[5 empty] | 1916.2 | 1677.2 | 0.46777
[5 empty] | 1916.4 | 1677.4 | 0.37035
[5 empty] | 1916.6 | 1677.6 | 0.46777
[5 empty] | 1916.8 | 1677.8 | 0.46777
[5 empty] | 1917 | 1678 | 0.37035
[5 empty] | 1917.2 | 1678.2 | 0.46777
[5 empty] | 1917.4 | 1678.4 | 0.37035
[5 empty] | 1917.6 | 1678.6 | 0.37035
[5 empty] | 1917.8 | 1678.8 | 0.46777
[5 empty] | 1918 | 1679 | 0.46777
[5 empty] | 1918.2 | 1679.2 | 0.46777
[5 empty] | 1918.4 | 1679.4 | 0.37035
[5 empty] | 1918.6 | 1679.6 | 0.46777
[5 empty] | 1918.8 | 1679.8 | 0.37035
[5 empty] | 1919 | 1680 | 0.46777
[5 empty] | 1919.2 | 1680.2 | 0.37035
[5 empty] | 1919.4 | 1680.4 | 0.46777
[5 empty] | 1919.6 | 1680.6 | 0.37035
[5 empty] | 1919.8 | 1680.8 | 0.46777
[5 empty] | 1920 | 1681 | 0.37035
[5 empty] | 1920.2 | 1681.2 | 0.37035
[5 empty] | 1920.4 | 1681.4 | 0.37035
[5 empty] | 1920.6 | 1681.6 | 0.46777
[5 empty] | 1920.8 | 1681.8 | 0.46777
[5 empty] | 1921 | 1682 | 0.46777
[5 empty] | 1921.2 | 1682.2 | 0.46777
[5 empty] | 1921.4 | 1682.4 | 0.46777
[5 empty] | 1921.6 | 1682.6 | 0.37035
[5 empty] | 1921.8 | 1682.8 | 0.37035
[5 empty] | 1922 | 1683 | 0.46777
[5 empty] | 1922.2 | 1683.2 | 0.37035
[5 empty] | 1922.4 | 1683.4 | 0.37035
[5 empty] | 1922.6 | 1683.6 | 0.37035
[5 empty] | 1922.8 | 1683.8 | 0.46777
[5 empty] | 1923 | 1684 | 0.37035
[5 empty] | 1923.2 | 1684.2 | 0.46777
[5 empty] | 1923.4 | 1684.4 | 0.46777
[5 empty] | 1923.6 | 1684.6 | 0.37035
[5 empty] | 1923.8 | 1684.8 | 0.37035
[5 empty] | 1924 | 1685 | 0.46777
[5 empty] | 1924.2 | 1685.2 | 0.46777
[5 empty] | 1924.4 | 1685.4 | 0.37035
[5 empty] | 1924.6 | 1685.6 | 0.46777
[5 empty] | 1924.8 | 1685.8 | 0.46777
[5 empty] | 1925 | 1686 | 0.46777
[5 empty] | 1925.2 | 1686.2 | 0.46777
[5 empty] | 1925.4 | 1686.4 | 0.37035
[5 empty] | 1925.6 | 1686.6 | 0.46777
[5 empty] | 1925.8 | 1686.8 | 0.46777
[5 empty] | 1926 | 1687 | 0.46777
[5 empty] | 1926.2 | 1687.2 | 0.37035
[5 empty] | 1926.4 | 1687.4 | 0.46777
[5 empty] | 1926.6 | 1687.6 | 0.46777
[5 empty] | 1926.8 | 1687.8 | 0.37035
[5 empty] | 1927 | 1688 | 0.46777
[5 empty] | 1927.2 | 1688.2 | 0.46777
[5 empty] | 1927.4 | 1688.4 | 0.46777
[5 empty] | 1927.6 | 1688.6 | 0.37035
[5 empty] | 1927.8 | 1688.8 | 0.46777
[5 empty] | 1928 | 1689 | 0.37035
[5 empty] | 1928.2 | 1689.2 | 0.46777
[5 empty] | 1928.4 | 1689.4 | 0.37035
[5 empty] | 1928.6 | 1689.6 | 0.37035
[5 empty] | 1928.8 | 1689.8 | 0.46777
[5 empty] | 1929 | 1690 | 0.46777
[5 empty] | 1929.2 | 1690.2 | 0.46777
[5 empty] | 1929.4 | 1690.4 | 0.46777
[5 empty] | 1929.6 | 1690.6 | 0.37035
[5 empty] | 1929.8 | 1690.8 | 0.46777
[5 empty] | 1930 | 1691 | 0.46777
[5 empty] | 1930.2 | 1691.2 | 0.46777
[5 empty] | 1930.4 | 1691.4 | 0.46777
[5 empty] | 1930.6 | 1691.6 | 0.46777
[5 empty] | 1930.8 | 1691.8 | 0.56516
[5 empty] | 1931 | 1692 | 0.46777
[5 empty] | 1931.2 | 1692.2 | 0.46777
[5 empty] | 1931.4 | 1692.4 | 0.46777
[5 empty] | 1931.6 | 1692.6 | 0.46777
[5 empty] | 1931.8 | 1692.8 | 0.27297
[5 empty] | 1932 | 1693 | 0.46777
[5 empty] | 1932.2 | 1693.2 | 0.46777
[5 empty] | 1932.4 | 1693.4 | 0.46777
[5 empty] | 1932.6 | 1693.6 | 0.46777
[5 empty] | 1932.8 | 1693.8 | 0.46777
[5 empty] | 1933 | 1694 | 0.46777
[5 empty] | 1933.2 | 1694.2 | 0.46777
[5 empty] | 1933.4 | 1694.4 | 0.46777
[5 empty] | 1933.6 | 1694.6 | 0.46777
[5 empty] | 1933.8 | 1694.8 | 0.46777
[5 empty] | 1934 | 1695 | 0.46777
[5 empty] | 1934.2 | 1695.2 | 0.46777
[5 empty] | 1934.4 | 1695.4 | 0.37035
[5 empty] | 1934.6 | 1695.6 | 0.46777
[5 empty] | 1934.8 | 1695.8 | 0.46777
[5 empty] | 1935 | 1696 | 0.46777
[5 empty] | 1935.2 | 1696.2 | 0.46777
[5 empty] | 1935.4 | 1696.4 | 0.37035
[5 empty] | 1935.6 | 1696.6 | 0.46777
[5 empty] | 1935.8 | 1696.8 | 0.46777
[5 empty] | 1936 | 1697 | 0.37035
[5 empty] | 1936.2 | 1697.2 | 0.46777
[5 empty] | 1936.4 | 1697.4 | 0.37035
[5 empty] | 1936.6 | 1697.6 | 0.46777
[5 empty] | 1936.8 | 1697.8 | 0.46777
[5 empty] | 1937 | 1698 | 0.37035
[5 empty] | 1937.2 | 1698.2 | 0.46777
[5 empty] | 1937.4 | 1698.4 | 0.46777
[5 empty] | 1937.6 | 1698.6 | 0.46777
[5 empty] | 1937.8 | 1698.8 | 0.37035
[5 empty] | 1938 | 1699 | 0.46777
[5 empty] | 1938.2 | 1699.2 | 0.46777
[5 empty] | 1938.4 | 1699.4 | 0.37035
[5 empty] | 1938.6 | 1699.6 | 0.37035
[5 empty] | 1938.8 | 1699.8 | 0.37035
[5 empty] | 1939 | 1700 | 0.37035
[5 empty] | 1939.2 | 1700.2 | 0.46777
[5 empty] | 1939.4 | 1700.4 | 0.46777
[5 empty] | 1939.6 | 1700.6 | 0.46777
[5 empty] | 1939.8 | 1700.8 | 0.46777
[5 empty] | 1940 | 1701 | 0.37035
[5 empty] | 1940.2 | 1701.2 | 0.37035
[5 empty] | 1940.4 | 1701.4 | 0.37035
[5 empty] | 1940.6 | 1701.6 | 0.46777
[5 empty] | 1940.8 | 1701.8 | 0.37035
[5 empty] | 1941 | 1702 | 0.46777
[5 empty] | 1941.2 | 1702.2 | 0.37035
[5 empty] | 1941.4 | 1702.4 | 0.46777
[5 empty] | 1941.6 | 1702.6 | 0.37035
[5 empty] | 1941.8 | 1702.8 | 0.46777
[5 empty] | 1942 | 1703 | 0.37035
[5 empty] | 1942.2 | 1703.2 | 0.37035
[5 empty] | 1942.4 | 1703.4 | 0.46777
[5 empty] | 1942.6 | 1703.6 | 0.46777
[5 empty] | 1942.8 | 1703.8 | 0.37035
[5 empty] | 1943 | 1704 | 0.46777
[5 empty] | 1943.2 | 1704.2 | 0.46777
[5 empty] | 1943.4 | 1704.4 | 0.37035
[5 empty] | 1943.6 | 1704.6 | 0.37035
[5 empty] | 1943.8 | 1704.8 | 0.46777
[5 empty] | 1944 | 1705 | 0.37035
[5 empty] | 1944.2 | 1705.2 | 0.46777
[5 empty] | 1944.4 | 1705.4 | 0.46777
[5 empty] | 1944.6 | 1705.6 | 0.37035
[5 empty] | 1944.8 | 1705.8 | 0.46777
[5 empty] | 1945 | 1706 | 0.46777
[5 empty] | 1945.2 | 1706.2 | 0.37035
[5 empty] | 1945.4 | 1706.4 | 0.46777
[5 empty] | 1945.6 | 1706.6 | 0.46777
[5 empty] | 1945.8 | 1706.8 | 0.37035
[5 empty] | 1946 | 1707 | 0.46777
[5 empty] | 1946.2 | 1707.2 | 0.46777
[5 empty] | 1946.4 | 1707.4 | 0.46777
[5 empty] | 1946.6 | 1707.6 | 0.46777
[5 empty] | 1946.8 | 1707.8 | 0.37035
[5 empty] | 1947 | 1708 | 0.46777
[5 empty] | 1947.2 | 1708.2 | 0.37035
[5 empty] | 1947.4 | 1708.4 | 0.37035
[5 empty] | 1947.6 | 1708.6 | 0.37035
[5 empty] | 1947.8 | 1708.8 | 0.37035
[5 empty] | 1948 | 1709 | 0.37035
[5 empty] | 1948.2 | 1709.2 | 0.37035
[5 empty] | 1948.4 | 1709.4 | 0.46777
[5 empty] | 1948.6 | 1709.6 | 0.37035
[5 empty] | 1948.8 | 1709.8 | 0.37035
[5 empty] | 1949 | 1710 | 0.37035
[5 empty] | 1949.2 | 1710.2 | 0.37035
[5 empty] | 1949.4 | 1710.4 | 0.46777
[5 empty] | 1949.6 | 1710.6 | 0.37035
[5 empty] | 1949.8 | 1710.8 | 0.37035
[5 empty] | 1950 | 1711 | 0.37035
[5 empty] | 1950.2 | 1711.2 | 0.46777
[5 empty] | 1950.4 | 1711.4 | 0.46777
[5 empty] | 1950.6 | 1711.6 | 0.46777
[5 empty] | 1950.8 | 1711.8 | 0.46777
[5 empty] | 1951 | 1712 | 0.46777
[5 empty] | 1951.2 | 1712.2 | 0.37035
[5 empty] | 1951.4 | 1712.4 | 0.37035
[5 empty] | 1951.6 | 1712.6 | 0.37035
[5 empty] | 1951.8 | 1712.8 | 0.37035
[5 empty] | 1952 | 1713 | 0.37035
[5 empty] | 1952.2 | 1713.2 | 0.37035
[5 empty] | 1952.4 | 1713.4 | 0.37035
[5 empty] | 1952.6 | 1713.6 | 0.37035
[5 empty] | 1952.8 | 1713.8 | 0.46777
[5 empty] | 1953 | 1714 | 0.37035
[5 empty] | 1953.2 | 1714.2 | 0.37035
[5 empty] | 1953.4 | 1714.4 | 0.46777
[5 empty] | 1953.6 | 1714.6 | 0.46777
[5 empty] | 1953.8 | 1714.8 | 0.46777
[5 empty] | 1954 | 1715 | 0.37035
[5 empty] | 1954.2 | 1715.2 | 0.37035
[5 empty] | 1954.4 | 1715.4 | 0.46777
[5 empty] | 1954.6 | 1715.6 | 0.37035
[5 empty] | 1954.8 | 1715.8 | 0.46777
[5 empty] | 1955 | 1716 | 0.46777
[5 empty] | 1955.2 | 1716.2 | 0.37035
[5 empty] | 1955.4 | 1716.4 | 0.46777
[5 empty] | 1955.6 | 1716.6 | 0.37035
[5 empty] | 1955.8 | 1716.8 | 0.37035
[5 empty] | 1956 | 1717 | 0.46777
[5 empty] | 1956.2 | 1717.2 | 0.46777
[5 empty] | 1956.4 | 1717.4 | 0.37035
[5 empty] | 1956.6 | 1717.6 | 0.37035
[5 empty] | 1956.8 | 1717.8 | 0.37035
[5 empty] | 1957 | 1718 | 0.37035
[5 empty] | 1957.2 | 1718.2 | 0.37035
[5 empty] | 1957.4 | 1718.4 | 0.46777
[5 empty] | 1957.6 | 1718.6 | 0.46777
[5 empty] | 1957.8 | 1718.8 | 0.37035
[5 empty] | 1958 | 1719 | 0.46777
[5 empty] | 1958.2 | 1719.2 | 0.37035
[5 empty] | 1958.4 | 1719.4 | 0.37035
[5 empty] | 1958.6 | 1719.6 | 0.27297
[5 empty] | 1958.8 | 1719.8 | 0.37035
[5 empty] | 1959 | 1720 | 0.46777
[5 empty] | 1959.2 | 1720.2 | 0.46777
[5 empty] | 1959.4 | 1720.4 | 0.46777
[5 empty] | 1959.6 | 1720.6 | 0.56516
[5 empty] | 1959.8 | 1720.8 | 0.46777
[5 empty] | 1960 | 1721 | 0.46777
[5 empty] | 1960.2 | 1721.2 | 0.46777
[5 empty] | 1960.4 | 1721.4 | 0.46777
[5 empty] | 1960.6 | 1721.6 | 0.37035
[5 empty] | 1960.8 | 1721.8 | 0.46777
[5 empty] | 1961 | 1722 | 0.37035
[5 empty] | 1961.2 | 1722.2 | 0.37035
[5 empty] | 1961.4 | 1722.4 | 0.46777
[5 empty] | 1961.6 | 1722.6 | 0.37035
[5 empty] | 1961.8 | 1722.8 | 0.37035
[5 empty] | 1962 | 1723 | 0.37035
[5 empty] | 1962.2 | 1723.2 | 0.37035
[5 empty] | 1962.4 | 1723.4 | 0.37035
[5 empty] | 1962.6 | 1723.6 | 0.46777
[5 empty] | 1962.8 | 1723.8 | 0.37035
[5 empty] | 1963 | 1724 | 0.46777
[5 empty] | 1963.2 | 1724.2 | 0.46777
[5 empty] | 1963.4 | 1724.4 | 0.46777
[5 empty] | 1963.6 | 1724.6 | 0.46777
[5 empty] | 1963.8 | 1724.8 | 0.46777
[5 empty] | 1964 | 1725 | 0.37035
[5 empty] | 1964.2 | 1725.2 | 0.37035
[5 empty] | 1964.4 | 1725.4 | 0.37035
[5 empty] | 1964.6 | 1725.6 | 0.37035
[5 empty] | 1964.8 | 1725.8 | 0.37035
[5 empty] | 1965 | 1726 | 0.37035
[5 empty] | 1965.2 | 1726.2 | 0.46777
[5 empty] | 1965.4 | 1726.4 | 0.46777
[5 empty] | 1965.6 | 1726.6 | 0.37035
[5 empty] | 1965.8 | 1726.8 | 0.46777
[5 empty] | 1966 | 1727 | 0.46777
[5 empty] | 1966.2 | 1727.2 | 0.37035
[5 empty] | 1966.4 | 1727.4 | 0.37035
[5 empty] | 1966.6 | 1727.6 | 0.46777
[5 empty] | 1966.8 | 1727.8 | 0.46777
[5 empty] | 1967 | 1728 | 0.46777
[5 empty] | 1967.2 | 1728.2 | 0.46777
[5 empty] | 1967.4 | 1728.4 | 0.37035
[5 empty] | 1967.6 | 1728.6 | 0.37035
[5 empty] | 1967.8 | 1728.8 | 0.37035
[5 empty] | 1968 | 1729 | 0.37035
[5 empty] | 1968.2 | 1729.2 | 0.37035
[5 empty] | 1968.4 | 1729.4 | 0.37035
[5 empty] | 1968.6 | 1729.6 | 0.37035
[5 empty] | 1968.8 | 1729.8 | 0.37035
[5 empty] | 1969 | 1730 | 0.37035
[5 empty] | 1969.2 | 1730.2 | 0.37035
[5 empty] | 1969.4 | 1730.4 | 0.46777
[5 empty] | 1969.6 | 1730.6 | 0.46777
[5 empty] | 1969.8 | 1730.8 | 0.46777
[5 empty] | 1970 | 1731 | 0.37035
[5 empty] | 1970.2 | 1731.2 | 0.37035
[5 empty] | 1970.4 | 1731.4 | 0.37035
[5 empty] | 1970.6 | 1731.6 | 0.46777
[5 empty] | 1970.8 | 1731.8 | 0.37035
[5 empty] | 1971 | 1732 | 0.37035
[5 empty] | 1971.2 | 1732.2 | 0.46777
[5 empty] | 1971.4 | 1732.4 | 0.37035
[5 empty] | 1971.6 | 1732.6 | 0.46777
[5 empty] | 1971.8 | 1732.8 | 0.37035
[5 empty] | 1972 | 1733 | 0.46777
[5 empty] | 1972.2 | 1733.2 | 0.37035
[5 empty] | 1972.4 | 1733.4 | 0.46777
[5 empty] | 1972.6 | 1733.6 | 0.37035
[5 empty] | 1972.8 | 1733.8 | 0.37035
[5 empty] | 1973 | 1734 | 0.46777
[5 empty] | 1973.2 | 1734.2 | 0.37035
[5 empty] | 1973.4 | 1734.4 | 0.37035
[5 empty] | 1973.6 | 1734.6 | 0.37035
[5 empty] | 1973.8 | 1734.8 | 0.37035
[5 empty] | 1974 | 1735 | 0.37035
[5 empty] | 1974.2 | 1735.2 | 0.37035
[5 empty] | 1974.4 | 1735.4 | 0.37035
[5 empty] | 1974.6 | 1735.6 | 0.37035
[5 empty] | 1974.8 | 1735.8 | 0.37035
[5 empty] | 1975 | 1736 | 0.46777
[5 empty] | 1975.2 | 1736.2 | 0.46777
[5 empty] | 1975.4 | 1736.4 | 0.37035
[5 empty] | 1975.6 | 1736.6 | 0.37035
[5 empty] | 1975.8 | 1736.8 | 0.37035
[5 empty] | 1976 | 1737 | 0.46777
[5 empty] | 1976.2 | 1737.2 | 0.46777
[5 empty] | 1976.4 | 1737.4 | 0.46777
[5 empty] | 1976.6 | 1737.6 | 0.37035
[5 empty] | 1976.8 | 1737.8 | 0.37035
[5 empty] | 1977 | 1738 | 0.46777
[5 empty] | 1977.2 | 1738.2 | 0.37035
[5 empty] | 1977.4 | 1738.4 | 0.46777
[5 empty] | 1977.6 | 1738.6 | 0.46777
[5 empty] | 1977.8 | 1738.8 | 0.46777
[5 empty] | 1978 | 1739 | 0.46777
[5 empty] | 1978.2 | 1739.2 | 0.46777
[5 empty] | 1978.4 | 1739.4 | 0.37035
[5 empty] | 1978.6 | 1739.6 | 0.37035
[5 empty] | 1978.8 | 1739.8 | 0.37035
[5 empty] | 1979 | 1740 | 0.46777
[5 empty] | 1979.2 | 1740.2 | 0.46777
[5 empty] | 1979.4 | 1740.4 | 0.46777
[5 empty] | 1979.6 | 1740.6 | 0.46777
[5 empty] | 1979.8 | 1740.8 | 0.46777
[5 empty] | 1980 | 1741 | 0.46777
[5 empty] | 1980.2 | 1741.2 | 0.46777
[5 empty] | 1980.4 | 1741.4 | 0.46777
[5 empty] | 1980.6 | 1741.6 | 0.46777
[5 empty] | 1980.8 | 1741.8 | 0.46777
[5 empty] | 1981 | 1742 | 0.46777
[5 empty] | 1981.2 | 1742.2 | 0.46777
[5 empty] | 1981.4 | 1742.4 | 0.46777
[5 empty] | 1981.6 | 1742.6 | 0.46777
[5 empty] | 1981.8 | 1742.8 | 0.46777
[5 empty] | 1982 | 1743 | 0.46777
[5 empty] | 1982.2 | 1743.2 | 0.37035
[5 empty] | 1982.4 | 1743.4 | 0.46777
[5 empty] | 1982.6 | 1743.6 | 0.46777
[5 empty] | 1982.8 | 1743.8 | 0.46777
[5 empty] | 1983 | 1744 | 0.37035
[5 empty] | 1983.2 | 1744.2 | 0.46777
[5 empty] | 1983.4 | 1744.4 | 0.46777
[5 empty] | 1983.6 | 1744.6 | 0.46777
[5 empty] | 1983.8 | 1744.8 | 0.46777
[5 empty] | 1984 | 1745 | 0.37035
[5 empty] | 1984.2 | 1745.2 | 0.46777
[5 empty] | 1984.4 | 1745.4 | 0.46777
[5 empty] | 1984.6 | 1745.6 | 0.46777
[5 empty] | 1984.8 | 1745.8 | 0.46777
[5 empty] | 1985 | 1746 | 0.46777
[5 empty] | 1985.2 | 1746.2 | 0.46777
[5 empty] | 1985.4 | 1746.4 | 0.37035
[5 empty] | 1985.6 | 1746.6 | 0.37035
[5 empty] | 1985.8 | 1746.8 | 0.46777
[5 empty] | 1986 | 1747 | 0.46777
[5 empty] | 1986.2 | 1747.2 | 0.37035
[5 empty] | 1986.4 | 1747.4 | 0.46777
[5 empty] | 1986.6 | 1747.6 | 0.46777
[5 empty] | 1986.8 | 1747.8 | 0.37035
[5 empty] | 1987 | 1748 | 0.46777
[5 empty] | 1987.2 | 1748.2 | 0.46777
[5 empty] | 1987.4 | 1748.4 | 0.46777
[5 empty] | 1987.6 | 1748.6 | 0.46777
[5 empty] | 1987.8 | 1748.8 | 0.46777
[5 empty] | 1988 | 1749 | 0.46777
[5 empty] | 1988.2 | 1749.2 | 0.46777
[5 empty] | 1988.4 | 1749.4 | 0.46777
[5 empty] | 1988.6 | 1749.6 | 0.46777
[5 empty] | 1988.8 | 1749.8 | 0.46777
[5 empty] | 1989 | 1750 | 0.37035
[5 empty] | 1989.2 | 1750.2 | 0.46777
[5 empty] | 1989.4 | 1750.4 | 0.46777
[5 empty] | 1989.6 | 1750.6 | 0.46777
[5 empty] | 1989.8 | 1750.8 | 0.46777
[5 empty] | 1990 | 1751 | 0.46777
[5 empty] | 1990.2 | 1751.2 | 0.46777
[5 empty] | 1990.4 | 1751.4 | 0.46777
[5 empty] | 1990.6 | 1751.6 | 0.46777
[5 empty] | 1990.8 | 1751.8 | 0.37035
[5 empty] | 1991 | 1752 | 0.46777
[5 empty] | 1991.2 | 1752.2 | 0.46777
[5 empty] | 1991.4 | 1752.4 | 0.46777
[5 empty] | 1991.6 | 1752.6 | 0.46777
[5 empty] | 1991.8 | 1752.8 | 0.46777
[5 empty] | 1992 | 1753 | 0.46777
[5 empty] | 1992.2 | 1753.2 | 0.46777
[5 empty] | 1992.4 | 1753.4 | 0.37035
[5 empty] | 1992.6 | 1753.6 | 0.46777
[5 empty] | 1992.8 | 1753.8 | 0.46777
[5 empty] | 1993 | 1754 | 0.46777
[5 empty] | 1993.2 | 1754.2 | 0.46777
[5 empty] | 1993.4 | 1754.4 | 0.46777
[5 empty] | 1993.6 | 1754.6 | 0.37035
[5 empty] | 1993.8 | 1754.8 | 0.37035
[5 empty] | 1994 | 1755 | 0.46777
[5 empty] | 1994.2 | 1755.2 | 0.46777
[5 empty] | 1994.4 | 1755.4 | 0.46777
[5 empty] | 1994.6 | 1755.6 | 0.37035
[5 empty] | 1994.8 | 1755.8 | 0.37035
[5 empty] | 1995 | 1756 | 0.46777
[5 empty] | 1995.2 | 1756.2 | 0.46777
[5 empty] | 1995.4 | 1756.4 | 0.46777
[5 empty] | 1995.6 | 1756.6 | 0.37035
[5 empty] | 1995.8 | 1756.8 | 0.46777
[5 empty] | 1996 | 1757 | 0.46777
[5 empty] | 1996.2 | 1757.2 | 0.46777
[5 empty] | 1996.4 | 1757.4 | 0.56516
[5 empty] | 1996.6 | 1757.6 | 0.46777
[5 empty] | 1996.8 | 1757.8 | 0.46777
[5 empty] | 1997 | 1758 | 0.46777
[5 empty] | 1997.2 | 1758.2 | 0.46777
[5 empty] | 1997.4 | 1758.4 | 0.56516
[5 empty] | 1997.6 | 1758.6 | 0.46777
[5 empty] | 1997.8 | 1758.8 | 0.56516
[5 empty] | 1998 | 1759 | 0.46777
[5 empty] | 1998.2 | 1759.2 | 0.56516
[5 empty] | 1998.4 | 1759.4 | 0.56516
[5 empty] | 1998.6 | 1759.6 | 0.46777
[5 empty] | 1998.8 | 1759.8 | 0.46777
[5 empty] | 1999 | 1760 | 0.46777
[5 empty] | 1999.2 | 1760.2 | 7.7725
[5 empty] | 1999.4 | 1760.4 | 0.56516
[5 empty] | 1999.6 | 1760.6 | 0.56516
[5 empty] | 1999.8 | 1760.8 | 0.56516
[5 empty] | 2000 | 1761 | 0.56516
[5 empty] | 2000.2 | 1761.2 | 0.56516
[5 empty] | 2000.4 | 1761.4 | 0.56516
[5 empty] | 2000.6 | 1761.6 | 0.56516
[5 empty] | 2000.8 | 1761.8 | 0.56516
[5 empty] | 2001 | 1762 | 0.56516
[5 empty] | 2001.2 | 1762.2 | 0.66258
[5 empty] | 2001.4 | 1762.4 | 0.56516
[5 empty] | 2001.6 | 1762.6 | 0.66258
[5 empty] | 2001.8 | 1762.8 | 0.56516
[5 empty] | 2002 | 1763 | 0.56516
[5 empty] | 2002.2 | 1763.2 | 0.56516
[5 empty] | 2002.4 | 1763.4 | 0.66258
[5 empty] | 2002.6 | 1763.6 | 0.56516
[5 empty] | 2002.8 | 1763.8 | 0.56516
[5 empty] | 2003 | 1764 | 0.56516
[5 empty] | 2003.2 | 1764.2 | 0.56516
[5 empty] | 2003.4 | 1764.4 | 0.56516
[5 empty] | 2003.6 | 1764.6 | 0.56516
[5 empty] | 2003.8 | 1764.8 | 0.56516
[5 empty] | 2004 | 1765 | 0.56516
[5 empty] | 2004.2 | 1765.2 | 0.56516
[5 empty] | 2004.4 | 1765.4 | 0.56516
[5 empty] | 2004.6 | 1765.6 | 0.56516
[5 empty] | 2004.8 | 1765.8 | 0.56516
[5 empty] | 2005 | 1766 | 0.56516
[5 empty] | 2005.2 | 1766.2 | 0.56516
[5 empty] | 2005.4 | 1766.4 | 0.56516
[5 empty] | 2005.6 | 1766.6 | 0.56516
[5 empty] | 2005.8 | 1766.8 | 0.66258
[5 empty] | 2006 | 1767 | 0.66258
[5 empty] | 2006.2 | 1767.2 | 0.56516
[5 empty] | 2006.4 | 1767.4 | 0.66258
[5 empty] | 2006.6 | 1767.6 | 0.56516
[5 empty] | 2006.8 | 1767.8 | 0.66258
[5 empty] | 2007 | 1768 | 0.66258
[5 empty] | 2007.2 | 1768.2 | 0.56516
[5 empty] | 2007.4 | 1768.4 | 0.66258
[5 empty] | 2007.6 | 1768.6 | 0.66258
[5 empty] | 2007.8 | 1768.8 | 0.66258
[5 empty] | 2008 | 1769 | 0.75996
[5 empty] | 2008.2 | 1769.2 | 0.66258
[5 empty] | 2008.4 | 1769.4 | 0.66258
[5 empty] | 2008.6 | 1769.6 | 0.66258
[5 empty] | 2008.8 | 1769.8 | 0.66258
[5 empty] | 2009 | 1770 | 0.66258
[5 empty] | 2009.2 | 1770.2 | 0.66258
[5 empty] | 2009.4 | 1770.4 | 0.66258
[5 empty] | 2009.6 | 1770.6 | 0.66258
[5 empty] | 2009.8 | 1770.8 | 0.66258
[5 empty] | 2010 | 1771 | 0.66258
[5 empty] | 2010.2 | 1771.2 | 0.75996
[5 empty] | 2010.4 | 1771.4 | 0.66258
[5 empty] | 2010.6 | 1771.6 | 0.66258
[5 empty] | 2010.8 | 1771.8 | 0.75996
[5 empty] | 2011 | 1772 | 0.75996
[5 empty] | 2011.2 | 1772.2 | 0.66258
[5 empty] | 2011.4 | 1772.4 | 0.66258
[5 empty] | 2011.6 | 1772.6 | 0.75996
[5 empty] | 2011.8 | 1772.8 | 0.75996
[5 empty] | 2012 | 1773 | 0.75996
[5 empty] | 2012.2 | 1773.2 | 0.75996
[5 empty] | 2012.4 | 1773.4 | 0.66258
[5 empty] | 2012.6 | 1773.6 | 0.75996
[5 empty] | 2012.8 | 1773.8 | 0.75996
[5 empty] | 2013 | 1774 | 0.66258
[5 empty] | 2013.2 | 1774.2 | 0.75996
[5 empty] | 2013.4 | 1774.4 | 0.66258
[5 empty] | 2013.6 | 1774.6 | 0.75996
[5 empty] | 2013.8 | 1774.8 | 0.75996
[5 empty] | 2014 | 1775 | 0.75996
[5 empty] | 2014.2 | 1775.2 | 0.85734
[5 empty] | 2014.4 | 1775.4 | 0.75996
[5 empty] | 2014.6 | 1775.6 | 0.75996
[5 empty] | 2014.8 | 1775.8 | 0.75996
[5 empty] | 2015 | 1776 | 0.75996
[5 empty] | 2015.2 | 1776.2 | 0.85734
[5 empty] | 2015.4 | 1776.4 | 0.75996
[5 empty] | 2015.6 | 1776.6 | 0.75996
[5 empty] | 2015.8 | 1776.8 | 0.85734
[5 empty] | 2016 | 1777 | 0.85734
[5 empty] | 2016.2 | 1777.2 | 0.75996
[5 empty] | 2016.4 | 1777.4 | 0.85734
[5 empty] | 2016.6 | 1777.6 | 0.85734
[5 empty] | 2016.8 | 1777.8 | 0.85734
[5 empty] | 2017 | 1778 | 0.85734
[5 empty] | 2017.2 | 1778.2 | 0.85734
[5 empty] | 2017.4 | 1778.4 | 0.85734
[5 empty] | 2017.6 | 1778.6 | 0.85734
[5 empty] | 2017.8 | 1778.8 | 0.85734
[5 empty] | 2018 | 1779 | 0.85734
[5 empty] | 2018.2 | 1779.2 | 0.85734
[5 empty] | 2018.4 | 1779.4 | 0.85734
[5 empty] | 2018.6 | 1779.6 | 0.95476
[5 empty] | 2018.8 | 1779.8 | 0.95476
[5 empty] | 2019 | 1780 | 0.85734
[5 empty] | 2019.2 | 1780.2 | 0.85734
[5 empty] | 2019.4 | 1780.4 | 0.85734
[5 empty] | 2019.6 | 1780.6 | 0.85734
[5 empty] | 2019.8 | 1780.8 | 0.95476
[5 empty] | 2020 | 1781 | 0.85734
[5 empty] | 2020.2 | 1781.2 | 0.95476
[5 empty] | 2020.4 | 1781.4 | 0.85734
[5 empty] | 2020.6 | 1781.6 | 0.95476
[5 empty] | 2020.8 | 1781.8 | 0.95476
[5 empty] | 2021 | 1782 | 0.95476
[5 empty] | 2021.2 | 1782.2 | 0.95476
[5 empty] | 2021.4 | 1782.4 | 0.95476
[5 empty] | 2021.6 | 1782.6 | 0.95476
[5 empty] | 2021.8 | 1782.8 | 1.0521
[5 empty] | 2022 | 1783 | 0.95476
[5 empty] | 2022.2 | 1783.2 | 0.95476
[5 empty] | 2022.4 | 1783.4 | 0.95476
[5 empty] | 2022.6 | 1783.6 | 0.95476
[5 empty] | 2022.8 | 1783.8 | 1.0521
[5 empty] | 2023 | 1784 | 1.0521
[5 empty] | 2023.2 | 1784.2 | 0.95476
[5 empty] | 2023.4 | 1784.4 | 0.85734
[5 empty] | 2023.6 | 1784.6 | 0.95476
[5 empty] | 2023.8 | 1784.8 | 1.0521
[5 empty] | 2024 | 1785 | 0.95476
[5 empty] | 2024.2 | 1785.2 | 1.0521
[5 empty] | 2024.4 | 1785.4 | 0.95476
[5 empty] | 2024.6 | 1785.6 | 0.95476
[5 empty] | 2024.8 | 1785.8 | 1.0521
[5 empty] | 2025 | 1786 | 1.0521
[5 empty] | 2025.2 | 1786.2 | 1.0521
[5 empty] | 2025.4 | 1786.4 | 1.0521
[5 empty] | 2025.6 | 1786.6 | 1.0521
[5 empty] | 2025.8 | 1786.8 | 1.0521
[5 empty] | 2026 | 1787 | 1.1496
[5 empty] | 2026.2 | 1787.2 | 1.1496
[5 empty] | 2026.4 | 1787.4 | 1.1496
[5 empty] | 2026.6 | 1787.6 | 1.0521
[5 empty] | 2026.8 | 1787.8 | 1.0521
[5 empty] | 2027 | 1788 | 1.0521
[5 empty] | 2027.2 | 1788.2 | 1.1496
[5 empty] | 2027.4 | 1788.4 | 1.0521
[5 empty] | 2027.6 | 1788.6 | 1.0521
[5 empty] | 2027.8 | 1788.8 | 1.0521
[5 empty] | 2028 | 1789 | 1.1496
[5 empty] | 2028.2 | 1789.2 | 1.1496
[5 empty] | 2028.4 | 1789.4 | 1.1496
[5 empty] | 2028.6 | 1789.6 | 1.1496
[5 empty] | 2028.8 | 1789.8 | 1.1496
[5 empty] | 2029 | 1790 | 1.1496
[5 empty] | 2029.2 | 1790.2 | 1.1496
[5 empty] | 2029.4 | 1790.4 | 1.3443
[5 empty] | 2029.6 | 1790.6 | 1.2469
[5 empty] | 2029.8 | 1790.8 | 1.2469
[5 empty] | 2030 | 1791 | 1.1496
[5 empty] | 2030.2 | 1791.2 | 1.1496
[5 empty] | 2030.4 | 1791.4 | 1.2469
[5 empty] | 2030.6 | 1791.6 | 1.2469
[5 empty] | 2030.8 | 1791.8 | 1.2469
[5 empty] | 2031 | 1792 | 1.2469
[5 empty] | 2031.2 | 1792.2 | 1.1496
[5 empty] | 2031.4 | 1792.4 | 1.2469
[5 empty] | 2031.6 | 1792.6 | 1.2469
[5 empty] | 2031.8 | 1792.8 | 1.2469
[5 empty] | 2032 | 1793 | 1.2469
[5 empty] | 2032.2 | 1793.2 | 1.3443
[5 empty] | 2032.4 | 1793.4 | 1.3443
[5 empty] | 2032.6 | 1793.6 | 1.2469
[5 empty] | 2032.8 | 1793.8 | 1.2469
[5 empty] | 2033 | 1794 | 1.3443
[5 empty] | 2033.2 | 1794.2 | 1.3443
[5 empty] | 2033.4 | 1794.4 | 1.3443
[5 empty] | 2033.6 | 1794.6 | 1.3443
[5 empty] | 2033.8 | 1794.8 | 1.3443
[5 empty] | 2034 | 1795 | 1.3443
[5 empty] | 2034.2 | 1795.2 | 1.3443
[5 empty] | 2034.4 | 1795.4 | 1.3443
[5 empty] | 2034.6 | 1795.6 | 1.3443
[5 empty] | 2034.8 | 1795.8 | 1.3443
[5 empty] | 2035 | 1796 | 1.3443
[5 empty] | 2035.2 | 1796.2 | 1.3443
[5 empty] | 2035.4 | 1796.4 | 1.3443
[5 empty] | 2035.6 | 1796.6 | 1.3443
[5 empty] | 2035.8 | 1796.8 | 1.3443
[5 empty] | 2036 | 1797 | 1.3443
[5 empty] | 2036.2 | 1797.2 | 1.3443
[5 empty] | 2036.4 | 1797.4 | 1.4417
[5 empty] | 2036.6 | 1797.6 | 1.3443
[5 empty] | 2036.8 | 1797.8 | 1.4417
[5 empty] | 2037 | 1798 | 1.4417
[5 empty] | 2037.2 | 1798.2 | 1.4417
[5 empty] | 2037.4 | 1798.4 | 1.4417
[5 empty] | 2037.6 | 1798.6 | 1.4417
[5 empty] | 2037.8 | 1798.8 | 1.4417
[5 empty] | 2038 | 1799 | 1.4417
[5 empty] | 2038.2 | 1799.2 | 1.4417
[5 empty] | 2038.4 | 1799.4 | 1.5391
[5 empty] | 2038.6 | 1799.6 | 1.4417
[5 empty] | 2038.8 | 1799.8 | 1.5391
[5 empty] | 2039 | 1800 | 1.5391
[5 empty] | 2039.2 | 1800.2 | 1.4417
[5 empty] | 2039.4 | 1800.4 | 1.5391
[5 empty] | 2039.6 | 1800.6 | 1.4417
[5 empty] | 2039.8 | 1800.8 | 1.5391
[5 empty] | 2040 | 1801 | 1.5391
[5 empty] | 2040.2 | 1801.2 | 1.5391
[5 empty] | 2040.4 | 1801.4 | 1.5391
[5 empty] | 2040.6 | 1801.6 | 1.5391
[5 empty] | 2040.8 | 1801.8 | 1.4417
[5 empty] | 2041 | 1802 | 1.5391
[5 empty] | 2041.2 | 1802.2 | 1.5391
[5 empty] | 2041.4 | 1802.4 | 1.5391
[5 empty] | 2041.6 | 1802.6 | 1.5391
[5 empty] | 2041.8 | 1802.8 | 1.5391
[5 empty] | 2042 | 1803 | 1.6365
[5 empty] | 2042.2 | 1803.2 | 1.5391
[5 empty] | 2042.4 | 1803.4 | 1.1496
[5 empty] | 2042.6 | 1803.6 | 1.6365
[5 empty] | 2042.8 | 1803.8 | 1.6365
[5 empty] | 2043 | 1804 | 1.6365
[5 empty] | 2043.2 | 1804.2 | 1.5391
[5 empty] | 2043.4 | 1804.4 | 1.5391
[5 empty] | 2043.6 | 1804.6 | 1.5391
[5 empty] | 2043.8 | 1804.8 | 1.6365
[5 empty] | 2044 | 1805 | 1.6365
[5 empty] | 2044.2 | 1805.2 | 1.6365
[5 empty] | 2044.4 | 1805.4 | 1.7339
[5 empty] | 2044.6 | 1805.6 | 1.6365
[5 empty] | 2044.8 | 1805.8 | 1.6365
[5 empty] | 2045 | 1806 | 1.7339
[5 empty] | 2045.2 | 1806.2 | 1.6365
[5 empty] | 2045.4 | 1806.4 | 1.6365
[5 empty] | 2045.6 | 1806.6 | 1.6365
[5 empty] | 2045.8 | 1806.8 | 1.7339
[5 empty] | 2046 | 1807 | 1.6365
[5 empty] | 2046.2 | 1807.2 | 1.6365
[5 empty] | 2046.4 | 1807.4 | 1.6365
[5 empty] | 2046.6 | 1807.6 | 1.6365
[5 empty] | 2046.8 | 1807.8 | 1.7339
[5 empty] | 2047 | 1808 | 1.7339
[5 empty] | 2047.2 | 1808.2 | 1.7339
[5 empty] | 2047.4 | 1808.4 | 1.6365
[5 empty] | 2047.6 | 1808.6 | 1.7339
[5 empty] | 2047.8 | 1808.8 | 1.7339
[5 empty] | 2048 | 1809 | 1.7339
[5 empty] | 2048.2 | 1809.2 | 1.7339
[5 empty] | 2048.4 | 1809.4 | 1.7339
[5 empty] | 2048.6 | 1809.6 | 1.7339
[5 empty] | 2048.8 | 1809.8 | 1.7339
[5 empty] | 2049 | 1810 | 1.7339
[5 empty] | 2049.2 | 1810.2 | 1.8313
[5 empty] | 2049.4 | 1810.4 | 1.8313
[5 empty] | 2049.6 | 1810.6 | 1.7339
[5 empty] | 2049.8 | 1810.8 | 1.8313
[5 empty] | 2050 | 1811 | 1.8313
[5 empty] | 2050.2 | 1811.2 | 1.8313
[5 empty] | 2050.4 | 1811.4 | 1.8313
[5 empty] | 2050.6 | 1811.6 | 1.8313
[5 empty] | 2050.8 | 1811.8 | 1.8313
[5 empty] | 2051 | 1812 | 1.8313
[5 empty] | 2051.2 | 1812.2 | 1.8313
[5 empty] | 2051.4 | 1812.4 | 1.8313
[5 empty] | 2051.6 | 1812.6 | 1.8313
[5 empty] | 2051.8 | 1812.8 | 1.8313
[5 empty] | 2052 | 1813 | 1.9287
[5 empty] | 2052.2 | 1813.2 | 1.8313
[5 empty] | 2052.4 | 1813.4 | 1.8313
[5 empty] | 2052.6 | 1813.6 | 1.8313
[5 empty] | 2052.8 | 1813.8 | 1.8313
[5 empty] | 2053 | 1814 | 1.8313
[5 empty] | 2053.2 | 1814.2 | 1.9287
[5 empty] | 2053.4 | 1814.4 | 1.9287
[5 empty] | 2053.6 | 1814.6 | 1.9287
[5 empty] | 2053.8 | 1814.8 | 1.9287
[5 empty] | 2054 | 1815 | 1.9287
[5 empty] | 2054.2 | 1815.2 | 1.9287
[5 empty] | 2054.4 | 1815.4 | 2.0261
[5 empty] | 2054.6 | 1815.6 | 1.9287
[5 empty] | 2054.8 | 1815.8 | 1.9287
[5 empty] | 2055 | 1816 | 1.9287
[5 empty] | 2055.2 | 1816.2 | 1.9287
[5 empty] | 2055.4 | 1816.4 | 2.0261
[5 empty] | 2055.6 | 1816.6 | 2.0261
[5 empty] | 2055.8 | 1816.8 | 2.0261
[5 empty] | 2056 | 1817 | 1.9287
[5 empty] | 2056.2 | 1817.2 | 2.0261
[5 empty] | 2056.4 | 1817.4 | 2.0261
[5 empty] | 2056.6 | 1817.6 | 2.0261
[5 empty] | 2056.8 | 1817.8 | 2.1235
[5 empty] | 2057 | 1818 | 2.0261
[5 empty] | 2057.2 | 1818.2 | 2.1235
[5 empty] | 2057.4 | 1818.4 | 2.1235
[5 empty] | 2057.6 | 1818.6 | 2.1235
[5 empty] | 2057.8 | 1818.8 | 2.1235
[5 empty] | 2058 | 1819 | 2.2209
[5 empty] | 2058.2 | 1819.2 | 2.1235
[5 empty] | 2058.4 | 1819.4 | 2.1235
[5 empty] | 2058.6 | 1819.6 | 2.1235
[5 empty] | 2058.8 | 1819.8 | 2.1235
[5 empty] | 2059 | 1820 | 2.1235
[5 empty] | 2059.2 | 1820.2 | 2.1235
[5 empty] | 2059.4 | 1820.4 | 2.1235
[5 empty] | 2059.6 | 1820.6 | 2.1235
[5 empty] | 2059.8 | 1820.8 | 2.1235
[5 empty] | 2060 | 1821 | 2.2209
[5 empty] | 2060.2 | 1821.2 | 2.1235
[5 empty] | 2060.4 | 1821.4 | 2.2209
[5 empty] | 2060.6 | 1821.6 | 2.1235
[5 empty] | 2060.8 | 1821.8 | 2.1235
[5 empty] | 2061 | 1822 | 2.2209
[5 empty] | 2061.2 | 1822.2 | 2.2209
[5 empty] | 2061.4 | 1822.4 | 2.1235
[5 empty] | 2061.6 | 1822.6 | 2.2209
[5 empty] | 2061.8 | 1822.8 | 2.2209
[5 empty] | 2062 | 1823 | 2.2209
[5 empty] | 2062.2 | 1823.2 | 2.2209
[5 empty] | 2062.4 | 1823.4 | 2.1235
[5 empty] | 2062.6 | 1823.6 | 2.2209
[5 empty] | 2062.8 | 1823.8 | 2.2209
[5 empty] | 2063 | 1824 | 2.2209
[5 empty] | 2063.2 | 1824.2 | 2.2209
[5 empty] | 2063.4 | 1824.4 | 2.2209
[5 empty] | 2063.6 | 1824.6 | 2.2209
[5 empty] | 2063.8 | 1824.8 | 2.3183
[5 empty] | 2064 | 1825 | 2.3183
[5 empty] | 2064.2 | 1825.2 | 2.2209
[5 empty] | 2064.4 | 1825.4 | 2.2209
[5 empty] | 2064.6 | 1825.6 | 2.3183
[5 empty] | 2064.8 | 1825.8 | 2.2209
[5 empty] | 2065 | 1826 | 2.3183
[5 empty] | 2065.2 | 1826.2 | 2.3183
[5 empty] | 2065.4 | 1826.4 | 2.2209
[5 empty] | 2065.6 | 1826.6 | 2.3183
[5 empty] | 2065.8 | 1826.8 | 2.3183
[5 empty] | 2066 | 1827 | 2.3183
[5 empty] | 2066.2 | 1827.2 | 2.4157
[5 empty] | 2066.4 | 1827.4 | 2.3183
[5 empty] | 2066.6 | 1827.6 | 2.4157
[5 empty] | 2066.8 | 1827.8 | 2.3183
[5 empty] | 2067 | 1828 | 2.4157
[5 empty] | 2067.2 | 1828.2 | 2.3183
[5 empty] | 2067.4 | 1828.4 | 2.4157
[5 empty] | 2067.6 | 1828.6 | 2.3183
[5 empty] | 2067.8 | 1828.8 | 2.4157
[5 empty] | 2068 | 1829 | 2.3183
[5 empty] | 2068.2 | 1829.2 | 2.5131
[5 empty] | 2068.4 | 1829.4 | 2.4157
[5 empty] | 2068.6 | 1829.6 | 2.4157
[5 empty] | 2068.8 | 1829.8 | 2.4157
[5 empty] | 2069 | 1830 | 2.4157
[5 empty] | 2069.2 | 1830.2 | 2.4157
[5 empty] | 2069.4 | 1830.4 | 2.4157
[5 empty] | 2069.6 | 1830.6 | 2.4157
[5 empty] | 2069.8 | 1830.8 | 2.4157
[5 empty] | 2070 | 1831 | 2.3183
[5 empty] | 2070.2 | 1831.2 | 2.5131
[5 empty] | 2070.4 | 1831.4 | 2.5131
[5 empty] | 2070.6 | 1831.6 | 2.4157
[5 empty] | 2070.8 | 1831.8 | 2.5131
[5 empty] | 2071 | 1832 | 2.4157
[5 empty] | 2071.2 | 1832.2 | 2.5131
[5 empty] | 2071.4 | 1832.4 | 2.5131
[5 empty] | 2071.6 | 1832.6 | 2.5131
[5 empty] | 2071.8 | 1832.8 | 2.5131
[5 empty] | 2072 | 1833 | 2.6105
[5 empty] | 2072.2 | 1833.2 | 2.4157
[5 empty] | 2072.4 | 1833.4 | 2.5131
[5 empty] | 2072.6 | 1833.6 | 2.5131
[5 empty] | 2072.8 | 1833.8 | 2.5131
[5 empty] | 2073 | 1834 | 2.5131
[5 empty] | 2073.2 | 1834.2 | 2.5131
[5 empty] | 2073.4 | 1834.4 | 2.6105
[5 empty] | 2073.6 | 1834.6 | 2.6105
[5 empty] | 2073.8 | 1834.8 | 2.6105
[5 empty] | 2074 | 1835 | 2.5131
[5 empty] | 2074.2 | 1835.2 | 2.5131
[5 empty] | 2074.4 | 1835.4 | 2.6105
[5 empty] | 2074.6 | 1835.6 | 2.5131
[5 empty] | 2074.8 | 1835.8 | 2.6105
[5 empty] | 2075 | 1836 | 2.6105
[5 empty] | 2075.2 | 1836.2 | 2.6105
[5 empty] | 2075.4 | 1836.4 | 2.6105
[5 empty] | 2075.6 | 1836.6 | 2.7079
[5 empty] | 2075.8 | 1836.8 | 2.6105
[5 empty] | 2076 | 1837 | 2.7079
[5 empty] | 2076.2 | 1837.2 | 2.7079
[5 empty] | 2076.4 | 1837.4 | 2.6105
[5 empty] | 2076.6 | 1837.6 | 2.6105
[5 empty] | 2076.8 | 1837.8 | 2.6105
[5 empty] | 2077 | 1838 | 2.6105
[5 empty] | 2077.2 | 1838.2 | 2.6105
[5 empty] | 2077.4 | 1838.4 | 2.7079
[5 empty] | 2077.6 | 1838.6 | 2.7079
[5 empty] | 2077.8 | 1838.8 | 2.8053
[5 empty] | 2078 | 1839 | 2.7079
[5 empty] | 2078.2 | 1839.2 | 2.7079
[5 empty] | 2078.4 | 1839.4 | 2.7079
[5 empty] | 2078.6 | 1839.6 | 2.8053
[5 empty] | 2078.8 | 1839.8 | 2.7079
[5 empty] | 2079 | 1840 | 2.8053
[5 empty] | 2079.2 | 1840.2 | 2.7079
[5 empty] | 2079.4 | 1840.4 | 2.7079
[5 empty] | 2079.6 | 1840.6 | 2.8053
[5 empty] | 2079.8 | 1840.8 | 2.8053
[5 empty] | 2080 | 1841 | 2.8053
[5 empty] | 2080.2 | 1841.2 | 2.8053
[5 empty] | 2080.4 | 1841.4 | 2.8053
[5 empty] | 2080.6 | 1841.6 | 2.8053
[5 empty] | 2080.8 | 1841.8 | 2.8053
[5 empty] | 2081 | 1842 | 2.8053
[5 empty] | 2081.2 | 1842.2 | 2.9027
[5 empty] | 2081.4 | 1842.4 | 2.9027
[5 empty] | 2081.6 | 1842.6 | 2.8053
[5 empty] | 2081.8 | 1842.8 | 2.9027
[5 empty] | 2082 | 1843 | 2.9027
[5 empty] | 2082.2 | 1843.2 | 2.9027
[5 empty] | 2082.4 | 1843.4 | 2.9027
[5 empty] | 2082.6 | 1843.6 | 2.9027
[5 empty] | 2082.8 | 1843.8 | 2.9027
[5 empty] | 2083 | 1844 | 2.9027
[5 empty] | 2083.2 | 1844.2 | 3.0001
[5 empty] | 2083.4 | 1844.4 | 3.0001
[5 empty] | 2083.6 | 1844.6 | 3.0001
[5 empty] | 2083.8 | 1844.8 | 2.9027
[5 empty] | 2084 | 1845 | 2.9027
[5 empty] | 2084.2 | 1845.2 | 3.0001
[5 empty] | 2084.4 | 1845.4 | 2.9027
[5 empty] | 2084.6 | 1845.6 | 3.0001
[5 empty] | 2084.8 | 1845.8 | 3.0001
[5 empty] | 2085 | 1846 | 3.0001
[5 empty] | 2085.2 | 1846.2 | 3.0975
[5 empty] | 2085.4 | 1846.4 | 3.0001
[5 empty] | 2085.6 | 1846.6 | 3.0975
[5 empty] | 2085.8 | 1846.8 | 3.0001
[5 empty] | 2086 | 1847 | 3.0001
[5 empty] | 2086.2 | 1847.2 | 3.0975
[5 empty] | 2086.4 | 1847.4 | 3.0001
[5 empty] | 2086.6 | 1847.6 | 3.0001
[5 empty] | 2086.8 | 1847.8 | 3.0975
[5 empty] | 2087 | 1848 | 3.0975
[5 empty] | 2087.2 | 1848.2 | 3.0001
[5 empty] | 2087.4 | 1848.4 | 3.0975
[5 empty] | 2087.6 | 1848.6 | 3.0975
[5 empty] | 2087.8 | 1848.8 | 3.1949
[5 empty] | 2088 | 1849 | 3.0975
[5 empty] | 2088.2 | 1849.2 | 3.0975
[5 empty] | 2088.4 | 1849.4 | 3.1949
[5 empty] | 2088.6 | 1849.6 | 3.0975
[5 empty] | 2088.8 | 1849.8 | 3.0975
[5 empty] | 2089 | 1850 | 3.0975
[5 empty] | 2089.2 | 1850.2 | 3.1949
[5 empty] | 2089.4 | 1850.4 | 3.1949
[5 empty] | 2089.6 | 1850.6 | 3.1949
[5 empty] | 2089.8 | 1850.8 | 3.2923
[5 empty] | 2090 | 1851 | 3.1949
[5 empty] | 2090.2 | 1851.2 | 3.1949
[5 empty] | 2090.4 | 1851.4 | 3.1949
[5 empty] | 2090.6 | 1851.6 | 3.2923
[5 empty] | 2090.8 | 1851.8 | 3.1949
[5 empty] | 2091 | 1852 | 3.2923
[5 empty] | 2091.2 | 1852.2 | 3.2923
[5 empty] | 2091.4 | 1852.4 | 3.2923
[5 empty] | 2091.6 | 1852.6 | 3.1949
[5 empty] | 2091.8 | 1852.8 | 3.1949
[5 empty] | 2092 | 1853 | 3.3897
[5 empty] | 2092.2 | 1853.2 | 3.2923
[5 empty] | 2092.4 | 1853.4 | 3.2923
[5 empty] | 2092.6 | 1853.6 | 3.2923
[5 empty] | 2092.8 | 1853.8 | 3.2923
[5 empty] | 2093 | 1854 | 3.3897
[5 empty] | 2093.2 | 1854.2 | 3.3897
[5 empty] | 2093.4 | 1854.4 | 3.3897
[5 empty] | 2093.6 | 1854.6 | 3.3897
[5 empty] | 2093.8 | 1854.8 | 3.3897
[5 empty] | 2094 | 1855 | 3.2923
[5 empty] | 2094.2 | 1855.2 | 3.3897
[5 empty] | 2094.4 | 1855.4 | 3.3897
[5 empty] | 2094.6 | 1855.6 | 3.3897
[5 empty] | 2094.8 | 1855.8 | 3.487
[5 empty] | 2095 | 1856 | 3.3897
[5 empty] | 2095.2 | 1856.2 | 3.3897
[5 empty] | 2095.4 | 1856.4 | 3.487
[5 empty] | 2095.6 | 1856.6 | 3.487
[5 empty] | 2095.8 | 1856.8 | 3.487
[5 empty] | 2096 | 1857 | 3.487
[5 empty] | 2096.2 | 1857.2 | 3.487
[5 empty] | 2096.4 | 1857.4 | 3.487
[5 empty] | 2096.6 | 1857.6 | 3.487
[5 empty] | 2096.8 | 1857.8 | 3.487
[5 empty] | 2097 | 1858 | 3.487
[5 empty] | 2097.2 | 1858.2 | 3.487
[5 empty] | 2097.4 | 1858.4 | 3.487
[5 empty] | 2097.6 | 1858.6 | 3.5845
[5 empty] | 2097.8 | 1858.8 | 3.487
[5 empty] | 2098 | 1859 | 3.487
[5 empty] | 2098.2 | 1859.2 | 3.487
[5 empty] | 2098.4 | 1859.4 | 3.5845
[5 empty] | 2098.6 | 1859.6 | 3.5845
[5 empty] | 2098.8 | 1859.8 | 3.5845
[5 empty] | 2099 | 1860 | 3.5845
[5 empty] | 2099.2 | 1860.2 | 3.5845
[5 empty] | 2099.4 | 1860.4 | 3.6818
[5 empty] | 2099.6 | 1860.6 | 3.5845
[5 empty] | 2099.8 | 1860.8 | 3.6818
[5 empty] | 2100 | 1861 | 3.6818
[5 empty] | 2100.2 | 1861.2 | 3.6818
[5 empty] | 2100.4 | 1861.4 | 3.6818
[5 empty] | 2100.6 | 1861.6 | 3.6818
[5 empty] | 2100.8 | 1861.8 | 3.6818
[5 empty] | 2101 | 1862 | 3.5845
[5 empty] | 2101.2 | 1862.2 | 3.6818
[5 empty] | 2101.4 | 1862.4 | 3.6818
[5 empty] | 2101.6 | 1862.6 | 3.6818
[5 empty] | 2101.8 | 1862.8 | 3.6818
[5 empty] | 2102 | 1863 | 3.6818
[5 empty] | 2102.2 | 1863.2 | 3.6818
[5 empty] | 2102.4 | 1863.4 | 3.7793
[5 empty] | 2102.6 | 1863.6 | 3.7793
[5 empty] | 2102.8 | 1863.8 | 3.7793
[5 empty] | 2103 | 1864 | 3.6818
[5 empty] | 2103.2 | 1864.2 | 3.7793
[5 empty] | 2103.4 | 1864.4 | 3.7793
[5 empty] | 2103.6 | 1864.6 | 3.7793
[5 empty] | 2103.8 | 1864.8 | 3.7793
[5 empty] | 2104 | 1865 | 3.7793
[5 empty] | 2104.2 | 1865.2 | 3.8766
[5 empty] | 2104.4 | 1865.4 | 3.8766
[5 empty] | 2104.6 | 1865.6 | 3.8766
[5 empty] | 2104.8 | 1865.8 | 3.8766
[5 empty] | 2105 | 1866 | 3.7793
[5 empty] | 2105.2 | 1866.2 | 3.8766
[5 empty] | 2105.4 | 1866.4 | 3.7793
[5 empty] | 2105.6 | 1866.6 | 3.8766
[5 empty] | 2105.8 | 1866.8 | 3.974
[5 empty] | 2106 | 1867 | 3.7793
[5 empty] | 2106.2 | 1867.2 | 3.7793
[5 empty] | 2106.4 | 1867.4 | 3.8766
[5 empty] | 2106.6 | 1867.6 | 3.974
[5 empty] | 2106.8 | 1867.8 | 3.8766
[5 empty] | 2107 | 1868 | 3.974
[5 empty] | 2107.2 | 1868.2 | 3.8766
[5 empty] | 2107.4 | 1868.4 | 3.974
[5 empty] | 2107.6 | 1868.6 | 3.974
[5 empty] | 2107.8 | 1868.8 | 3.974
[5 empty] | 2108 | 1869 | 3.974
[5 empty] | 2108.2 | 1869.2 | 4.0714
[5 empty] | 2108.4 | 1869.4 | 4.0714
[5 empty] | 2108.6 | 1869.6 | 4.0714
[5 empty] | 2108.8 | 1869.8 | 3.974
[5 empty] | 2109 | 1870 | 4.0714
[5 empty] | 2109.2 | 1870.2 | 4.0714
[5 empty] | 2109.4 | 1870.4 | 4.0714
[5 empty] | 2109.6 | 1870.6 | 4.1688
[5 empty] | 2109.8 | 1870.8 | 4.0714
[5 empty] | 2110 | 1871 | 4.0714
[5 empty] | 2110.2 | 1871.2 | 4.0714
[5 empty] | 2110.4 | 1871.4 | 4.0714
[5 empty] | 2110.6 | 1871.6 | 4.0714
[5 empty] | 2110.8 | 1871.8 | 4.1688
[5 empty] | 2111 | 1872 | 4.1688
[5 empty] | 2111.2 | 1872.2 | 4.0714
[5 empty] | 2111.4 | 1872.4 | 4.1688
[5 empty] | 2111.6 | 1872.6 | 4.1688
[5 empty] | 2111.8 | 1872.8 | 4.1688
[5 empty] | 2112 | 1873 | 4.2662
[5 empty] | 2112.2 | 1873.2 | 4.2662
[5 empty] | 2112.4 | 1873.4 | 4.0714
[5 empty] | 2112.6 | 1873.6 | 4.2662
[5 empty] | 2112.8 | 1873.8 | 4.1688
[5 empty] | 2113 | 1874 | 4.2662
[5 empty] | 2113.2 | 1874.2 | 4.1688
[5 empty] | 2113.4 | 1874.4 | 4.2662
[5 empty] | 2113.6 | 1874.6 | 4.2662
[5 empty] | 2113.8 | 1874.8 | 4.2662
[5 empty] | 2114 | 1875 | 4.2662
[5 empty] | 2114.2 | 1875.2 | 4.2662
[5 empty] | 2114.4 | 1875.4 | 4.3636
[5 empty] | 2114.6 | 1875.6 | 4.3636
[5 empty] | 2114.8 | 1875.8 | 4.2662
[5 empty] | 2115 | 1876 | 4.2662
[5 empty] | 2115.2 | 1876.2 | 4.461
[5 empty] | 2115.4 | 1876.4 | 4.2662
[5 empty] | 2115.6 | 1876.6 | 4.2662
[5 empty] | 2115.8 | 1876.8 | 4.3636
[5 empty] | 2116 | 1877 | 4.461
[5 empty] | 2116.2 | 1877.2 | 4.3636
[5 empty] | 2116.4 | 1877.4 | 4.3636
[5 empty] | 2116.6 | 1877.6 | 4.3636
[5 empty] | 2116.8 | 1877.8 | 4.3636
[5 empty] | 2117 | 1878 | 4.3636
[5 empty] | 2117.2 | 1878.2 | 4.3636
[5 empty] | 2117.4 | 1878.4 | 4.461
[5 empty] | 2117.6 | 1878.6 | 4.3636
[5 empty] | 2117.8 | 1878.8 | 4.3636
[5 empty] | 2118 | 1879 | 4.461
[5 empty] | 2118.2 | 1879.2 | 4.461
[5 empty] | 2118.4 | 1879.4 | 4.461
[5 empty] | 2118.6 | 1879.6 | 4.461
[5 empty] | 2118.8 | 1879.8 | 4.461
[5 empty] | 2119 | 1880 | 4.461
[5 empty] | 2119.2 | 1880.2 | 4.461
[5 empty] | 2119.4 | 1880.4 | 4.5584
[5 empty] | 2119.6 | 1880.6 | 4.7532
[5 empty] | 2119.8 | 1880.8 | 4.5584
[5 empty] | 2120 | 1881 | 4.5584
[5 empty] | 2120.2 | 1881.2 | 4.5584
[5 empty] | 2120.4 | 1881.4 | 4.5584
[5 empty] | 2120.6 | 1881.6 | 4.5584
[5 empty] | 2120.8 | 1881.8 | 4.5584
[5 empty] | 2121 | 1882 | 4.6558
[5 empty] | 2121.2 | 1882.2 | 4.5584
[5 empty] | 2121.4 | 1882.4 | 4.5584
[5 empty] | 2121.6 | 1882.6 | 4.5584
[5 empty] | 2121.8 | 1882.8 | 4.6558
[5 empty] | 2122 | 1883 | 4.5584
[5 empty] | 2122.2 | 1883.2 | 4.5584
[5 empty] | 2122.4 | 1883.4 | 4.6558
[5 empty] | 2122.6 | 1883.6 | 4.6558
[5 empty] | 2122.8 | 1883.8 | 4.6558
[5 empty] | 2123 | 1884 | 4.6558
[5 empty] | 2123.2 | 1884.2 | 4.7532
[5 empty] | 2123.4 | 1884.4 | 4.6558
[5 empty] | 2123.6 | 1884.6 | 4.6558
[5 empty] | 2123.8 | 1884.8 | 4.7532
[5 empty] | 2124 | 1885 | 4.6558
[5 empty] | 2124.2 | 1885.2 | 4.7532
[5 empty] | 2124.4 | 1885.4 | 4.7532
[5 empty] | 2124.6 | 1885.6 | 4.6558
[5 empty] | 2124.8 | 1885.8 | 4.7532
[5 empty] | 2125 | 1886 | 4.7532
[5 empty] | 2125.2 | 1886.2 | 4.6558
[5 empty] | 2125.4 | 1886.4 | 4.7532
[5 empty] | 2125.6 | 1886.6 | 4.8506
[5 empty] | 2125.8 | 1886.8 | 4.7532
[5 empty] | 2126 | 1887 | 4.7532
[5 empty] | 2126.2 | 1887.2 | 4.8506
[5 empty] | 2126.4 | 1887.4 | 4.8506
[5 empty] | 2126.6 | 1887.6 | 4.8506
[5 empty] | 2126.8 | 1887.8 | 4.948
[5 empty] | 2127 | 1888 | 4.8506
[5 empty] | 2127.2 | 1888.2 | 4.948
[5 empty] | 2127.4 | 1888.4 | 4.8506
[5 empty] | 2127.6 | 1888.6 | 4.948
[5 empty] | 2127.8 | 1888.8 | 4.8506
[5 empty] | 2128 | 1889 | 4.8506
[5 empty] | 2128.2 | 1889.2 | 4.7532
[5 empty] | 2128.4 | 1889.4 | 4.8506
[5 empty] | 2128.6 | 1889.6 | 4.948
[5 empty] | 2128.8 | 1889.8 | 4.948
[5 empty] | 2129 | 1890 | 4.948
[5 empty] | 2129.2 | 1890.2 | 4.948
[5 empty] | 2129.4 | 1890.4 | 4.948
[5 empty] | 2129.6 | 1890.6 | 5.0454
[5 empty] | 2129.8 | 1890.8 | 5.0454
[5 empty] | 2130 | 1891 | 5.0454
[5 empty] | 2130.2 | 1891.2 | 5.0454
[5 empty] | 2130.4 | 1891.4 | 5.0454
[5 empty] | 2130.6 | 1891.6 | 5.1428
[5 empty] | 2130.8 | 1891.8 | 5.1428
[5 empty] | 2131 | 1892 | 5.1428
[5 empty] | 2131.2 | 1892.2 | 5.0454
[5 empty] | 2131.4 | 1892.4 | 5.1428
[5 empty] | 2131.6 | 1892.6 | 5.1428
[5 empty] | 2131.8 | 1892.8 | 5.1428
[5 empty] | 2132 | 1893 | 5.1428
[5 empty] | 2132.2 | 1893.2 | 5.1428
[5 empty] | 2132.4 | 1893.4 | 5.1428
[5 empty] | 2132.6 | 1893.6 | 5.2402
[5 empty] | 2132.8 | 1893.8 | 5.2402
[5 empty] | 2133 | 1894 | 5.2402
[5 empty] | 2133.2 | 1894.2 | 5.2402
[5 empty] | 2133.4 | 1894.4 | 5.2402
[5 empty] | 2133.6 | 1894.6 | 5.2402
[5 empty] | 2133.8 | 1894.8 | 5.2402
[5 empty] | 2134 | 1895 | 5.2402
[5 empty] | 2134.2 | 1895.2 | 5.3376
[5 empty] | 2134.4 | 1895.4 | 5.2402
[5 empty] | 2134.6 | 1895.6 | 5.3376
[5 empty] | 2134.8 | 1895.8 | 5.3376
[5 empty] | 2135 | 1896 | 5.3376
[5 empty] | 2135.2 | 1896.2 | 5.3376
[5 empty] | 2135.4 | 1896.4 | 5.435
[5 empty] | 2135.6 | 1896.6 | 5.3376
[5 empty] | 2135.8 | 1896.8 | 5.3376
[5 empty] | 2136 | 1897 | 5.3376
[5 empty] | 2136.2 | 1897.2 | 5.3376
[5 empty] | 2136.4 | 1897.4 | 5.435
[5 empty] | 2136.6 | 1897.6 | 5.435
[5 empty] | 2136.8 | 1897.8 | 5.3376
[5 empty] | 2137 | 1898 | 5.435
[5 empty] | 2137.2 | 1898.2 | 5.435
[5 empty] | 2137.4 | 1898.4 | 5.435
[5 empty] | 2137.6 | 1898.6 | 5.435
[5 empty] | 2137.8 | 1898.8 | 5.435
[5 empty] | 2138 | 1899 | 5.435
[5 empty] | 2138.2 | 1899.2 | 5.5324
[5 empty] | 2138.4 | 1899.4 | 5.5324
[5 empty] | 2138.6 | 1899.6 | 5.5324
[5 empty] | 2138.8 | 1899.8 | 5.435
[5 empty] | 2139 | 1900 | 5.5324
[5 empty] | 2139.2 | 1900.2 | 5.5324
[5 empty] | 2139.4 | 1900.4 | 5.5324
[5 empty] | 2139.6 | 1900.6 | 5.5324
[5 empty] | 2139.8 | 1900.8 | 5.6298
[5 empty] | 2140 | 1901 | 5.6298
[5 empty] | 2140.2 | 1901.2 | 5.6298
[5 empty] | 2140.4 | 1901.4 | 5.6298
[5 empty] | 2140.6 | 1901.6 | 5.6298
[5 empty] | 2140.8 | 1901.8 | 5.6298
[5 empty] | 2141 | 1902 | 5.6298
[5 empty] | 2141.2 | 1902.2 | 5.6298
[5 empty] | 2141.4 | 1902.4 | 5.6298
[5 empty] | 2141.6 | 1902.6 | 5.6298
[5 empty] | 2141.8 | 1902.8 | 5.6298
[5 empty] | 2142 | 1903 | 5.6298
[5 empty] | 2142.2 | 1903.2 | 5.7272
[5 empty] | 2142.4 | 1903.4 | 5.7272
[5 empty] | 2142.6 | 1903.6 | 5.7272
[5 empty] | 2142.8 | 1903.8 | 5.7272
[5 empty] | 2143 | 1904 | 5.7272
[5 empty] | 2143.2 | 1904.2 | 5.7272
[5 empty] | 2143.4 | 1904.4 | 5.7272
[5 empty] | 2143.6 | 1904.6 | 5.8246
[5 empty] | 2143.8 | 1904.8 | 5.8246
[5 empty] | 2144 | 1905 | 5.7272
[5 empty] | 2144.2 | 1905.2 | 5.8246
[5 empty] | 2144.4 | 1905.4 | 5.8246
[5 empty] | 2144.6 | 1905.6 | 5.8246
[5 empty] | 2144.8 | 1905.8 | 5.8246
[5 empty] | 2145 | 1906 | 5.922
[5 empty] | 2145.2 | 1906.2 | 5.922
[5 empty] | 2145.4 | 1906.4 | 5.8246
[5 empty] | 2145.6 | 1906.6 | 5.922
[5 empty] | 2145.8 | 1906.8 | 5.922
[5 empty] | 2146 | 1907 | 5.922
[5 empty] | 2146.2 | 1907.2 | 5.922
[5 empty] | 2146.4 | 1907.4 | 6.0194
[5 empty] | 2146.6 | 1907.6 | 5.922
[5 empty] | 2146.8 | 1907.8 | 5.922
[5 empty] | 2147 | 1908 | 5.922
[5 empty] | 2147.2 | 1908.2 | 5.922
[5 empty] | 2147.4 | 1908.4 | 6.0194
[5 empty] | 2147.6 | 1908.6 | 6.0194
[5 empty] | 2147.8 | 1908.8 | 5.922
[5 empty] | 2148 | 1909 | 6.0194
[5 empty] | 2148.2 | 1909.2 | 5.922
[5 empty] | 2148.4 | 1909.4 | 6.0194
[5 empty] | 2148.6 | 1909.6 | 6.0194
[5 empty] | 2148.8 | 1909.8 | 6.1168
[5 empty] | 2149 | 1910 | 6.1168
[5 empty] | 2149.2 | 1910.2 | 6.1168
[5 empty] | 2149.4 | 1910.4 | 6.0194
[5 empty] | 2149.6 | 1910.6 | 6.1168
[5 empty] | 2149.8 | 1910.8 | 6.1168
[5 empty] | 2150 | 1911 | 6.1168
[5 empty] | 2150.2 | 1911.2 | 6.2142
[5 empty] | 2150.4 | 1911.4 | 6.2142
[5 empty] | 2150.6 | 1911.6 | 6.1168
[5 empty] | 2150.8 | 1911.8 | 6.2142
[5 empty] | 2151 | 1912 | 6.2142
[5 empty] | 2151.2 | 1912.2 | 6.2142
[5 empty] | 2151.4 | 1912.4 | 6.2142
[5 empty] | 2151.6 | 1912.6 | 6.2142
[5 empty] | 2151.8 | 1912.8 | 6.2142
[5 empty] | 2152 | 1913 | 6.2142
[5 empty] | 2152.2 | 1913.2 | 6.2142
[5 empty] | 2152.4 | 1913.4 | 6.3116
[5 empty] | 2152.6 | 1913.6 | 6.2142
[5 empty] | 2152.8 | 1913.8 | 6.3116
[5 empty] | 2153 | 1914 | 6.3116
[5 empty] | 2153.2 | 1914.2 | 6.3116
[5 empty] | 2153.4 | 1914.4 | 6.3116
[5 empty] | 2153.6 | 1914.6 | 6.3116
[5 empty] | 2153.8 | 1914.8 | 6.3116
[5 empty] | 2154 | 1915 | 6.3116
[5 empty] | 2154.2 | 1915.2 | 6.3116
[5 empty] | 2154.4 | 1915.4 | 6.3116
[5 empty] | 2154.6 | 1915.6 | 6.3116
[5 empty] | 2154.8 | 1915.8 | 6.409
[5 empty] | 2155 | 1916 | 6.409
[5 empty] | 2155.2 | 1916.2 | 6.409
[5 empty] | 2155.4 | 1916.4 | 6.409
[5 empty] | 2155.6 | 1916.6 | 6.409
[5 empty] | 2155.8 | 1916.8 | 6.409
[5 empty] | 2156 | 1917 | 6.409
[5 empty] | 2156.2 | 1917.2 | 6.409
[5 empty] | 2156.4 | 1917.4 | 6.5064
[5 empty] | 2156.6 | 1917.6 | 6.409
[5 empty] | 2156.8 | 1917.8 | 6.409
[5 empty] | 2157 | 1918 | 6.409
[5 empty] | 2157.2 | 1918.2 | 6.409
[5 empty] | 2157.4 | 1918.4 | 6.5064
[5 empty] | 2157.6 | 1918.6 | 6.5064
[5 empty] | 2157.8 | 1918.8 | 6.5064
[5 empty] | 2158 | 1919 | 6.5064
[5 empty] | 2158.2 | 1919.2 | 6.5064
[5 empty] | 2158.4 | 1919.4 | 6.5064
[5 empty] | 2158.6 | 1919.6 | 6.5064
[5 empty] | 2158.8 | 1919.8 | 6.6037
[5 empty] | 2159 | 1920 | 6.5064
[5 empty] | 2159.2 | 1920.2 | 6.6037
[5 empty] | 2159.4 | 1920.4 | 6.5064
[5 empty] | 2159.6 | 1920.6 | 6.6037
[5 empty] | 2159.8 | 1920.8 | 6.6037
[5 empty] | 2160 | 1921 | 6.6037
[5 empty] | 2160.2 | 1921.2 | 6.6037
[5 empty] | 2160.4 | 1921.4 | 6.6037
[5 empty] | 2160.6 | 1921.6 | 6.6037
[5 empty] | 2160.8 | 1921.8 | 6.6037
[5 empty] | 2161 | 1922 | 6.6037
[5 empty] | 2161.2 | 1922.2 | 6.6037
[5 empty] | 2161.4 | 1922.4 | 6.6037
[5 empty] | 2161.6 | 1922.6 | 6.6037
[5 empty] | 2161.8 | 1922.8 | 6.7012
[5 empty] | 2162 | 1923 | 6.7012
[5 empty] | 2162.2 | 1923.2 | 6.7012
[5 empty] | 2162.4 | 1923.4 | 6.7012
[5 empty] | 2162.6 | 1923.6 | 6.6037
[5 empty] | 2162.8 | 1923.8 | 6.7012
[5 empty] | 2163 | 1924 | 6.7012
[5 empty] | 2163.2 | 1924.2 | 6.7985
[5 empty] | 2163.4 | 1924.4 | 6.7985
[5 empty] | 2163.6 | 1924.6 | 6.7985
[5 empty] | 2163.8 | 1924.8 | 6.7985
[5 empty] | 2164 | 1925 | 6.7985
[5 empty] | 2164.2 | 1925.2 | 6.7985
[5 empty] | 2164.4 | 1925.4 | 6.7985
[5 empty] | 2164.6 | 1925.6 | 6.7985
[5 empty] | 2164.8 | 1925.8 | 6.896
[5 empty] | 2165 | 1926 | 6.7985
[5 empty] | 2165.2 | 1926.2 | 6.896
[5 empty] | 2165.4 | 1926.4 | 6.896
[5 empty] | 2165.6 | 1926.6 | 6.896
[5 empty] | 2165.8 | 1926.8 | 6.896
[5 empty] | 2166 | 1927 | 6.896
[5 empty] | 2166.2 | 1927.2 | 6.896
[5 empty] | 2166.4 | 1927.4 | 6.896
[5 empty] | 2166.6 | 1927.6 | 6.896
[5 empty] | 2166.8 | 1927.8 | 6.896
[5 empty] | 2167 | 1928 | 6.896
[5 empty] | 2167.2 | 1928.2 | 6.9933
[5 empty] | 2167.4 | 1928.4 | 6.9933
[5 empty] | 2167.6 | 1928.6 | 6.896
[5 empty] | 2167.8 | 1928.8 | 6.9933
[5 empty] | 2168 | 1929 | 6.9933
[5 empty] | 2168.2 | 1929.2 | 6.9933
[5 empty] | 2168.4 | 1929.4 | 7.0907
[5 empty] | 2168.6 | 1929.6 | 7.0907
[5 empty] | 2168.8 | 1929.8 | 7.0907
[5 empty] | 2169 | 1930 | 7.1881
[5 empty] | 2169.2 | 1930.2 | 7.1881
[5 empty] | 2169.4 | 1930.4 | 7.1881
[5 empty] | 2169.6 | 1930.6 | 7.1881
[5 empty] | 2169.8 | 1930.8 | 7.1881
[5 empty] | 2170 | 1931 | 7.1881
[5 empty] | 2170.2 | 1931.2 | 7.1881
[5 empty] | 2170.4 | 1931.4 | 7.1881
[5 empty] | 2170.6 | 1931.6 | 7.1881
[5 empty] | 2170.8 | 1931.8 | 7.1881
[5 empty] | 2171 | 1932 | 7.1881
[5 empty] | 2171.2 | 1932.2 | 7.2855
[5 empty] | 2171.4 | 1932.4 | 7.2855
[5 empty] | 2171.6 | 1932.6 | 7.3829
[5 empty] | 2171.8 | 1932.8 | 7.3829
[5 empty] | 2172 | 1933 | 7.3829
[5 empty] | 2172.2 | 1933.2 | 7.3829
[5 empty] | 2172.4 | 1933.4 | 7.3829
[5 empty] | 2172.6 | 1933.6 | 6.9933
[5 empty] | 2172.8 | 1933.8 | 7.4803
[5 empty] | 2173 | 1934 | 7.4803
[5 empty] | 2173.2 | 1934.2 | 7.4803
[5 empty] | 2173.4 | 1934.4 | 7.4803
[5 empty] | 2173.6 | 1934.6 | 7.4803
[5 empty] | 2173.8 | 1934.8 | 7.4803
[5 empty] | 2174 | 1935 | 7.5777
[5 empty] | 2174.2 | 1935.2 | 7.5777
[5 empty] | 2174.4 | 1935.4 | 7.5777
[5 empty] | 2174.6 | 1935.6 | 7.4803
[5 empty] | 2174.8 | 1935.8 | 7.6751
[5 empty] | 2175 | 1936 | 7.6751
[5 empty] | 2175.2 | 1936.2 | 7.5777
[5 empty] | 2175.4 | 1936.4 | 7.5777
[5 empty] | 2175.6 | 1936.6 | 7.6751
[5 empty] | 2175.8 | 1936.8 | 7.8699
[5 empty] | 2176 | 1937 | 7.5777
[5 empty] | 2176.2 | 1937.2 | 7.6751
[5 empty] | 2176.4 | 1937.4 | 7.5777
[5 empty] | 2176.6 | 1937.6 | 7.5777
[5 empty] | 2176.8 | 1937.8 | 7.6751
[5 empty] | 2177 | 1938 | 7.6751
[5 empty] | 2177.2 | 1938.2 | 7.6751
[5 empty] | 2177.4 | 1938.4 | 7.6751
[5 empty] | 2177.6 | 1938.6 | 7.7725
[5 empty] | 2177.8 | 1938.8 | 7.6751
[5 empty] | 2178 | 1939 | 7.7725
[5 empty] | 2178.2 | 1939.2 | 7.7725
[5 empty] | 2178.4 | 1939.4 | 7.7725
[5 empty] | 2178.6 | 1939.6 | 7.7725
[5 empty] | 2178.8 | 1939.8 | 7.8699
[5 empty] | 2179 | 1940 | 7.7725
[5 empty] | 2179.2 | 1940.2 | 7.7725
[5 empty] | 2179.4 | 1940.4 | 7.8699
[5 empty] | 2179.6 | 1940.6 | 7.8699
[5 empty] | 2179.8 | 1940.8 | 7.8699
[5 empty] | 2180 | 1941 | 7.8699
[5 empty] | 2180.2 | 1941.2 | 7.8699
[5 empty] | 2180.4 | 1941.4 | 7.8699
[5 empty] | 2180.6 | 1941.6 | 7.9673
[5 empty] | 2180.8 | 1941.8 | 7.9673
[5 empty] | 2181 | 1942 | 8.0647
[5 empty] | 2181.2 | 1942.2 | 8.0647
[5 empty] | 2181.4 | 1942.4 | 8.0647
[5 empty] | 2181.6 | 1942.6 | 8.0647
[5 empty] | 2181.8 | 1942.8 | 8.0647
[5 empty] | 2182 | 1943 | 8.0647
[5 empty] | 2182.2 | 1943.2 | 8.0647
[5 empty] | 2182.4 | 1943.4 | 8.0647
[5 empty] | 2182.6 | 1943.6 | 8.0647
[5 empty] | 2182.8 | 1943.8 | 7.9673
[5 empty] | 2183 | 1944 | 7.9673
[5 empty] | 2183.2 | 1944.2 | 8.0647
[5 empty] | 2183.4 | 1944.4 | 7.9673
[5 empty] | 2183.6 | 1944.6 | 8.0647
[5 empty] | 2183.8 | 1944.8 | 8.0647
[5 empty] | 2184 | 1945 | 8.0647
[5 empty] | 2184.2 | 1945.2 | 8.0647
[5 empty] | 2184.4 | 1945.4 | 7.9673
[5 empty] | 2184.6 | 1945.6 | 8.1621
[5 empty] | 2184.8 | 1945.8 | 8.0647
[5 empty] | 2185 | 1946 | 8.0647
[5 empty] | 2185.2 | 1946.2 | 8.1621
[5 empty] | 2185.4 | 1946.4 | 8.0647
[5 empty] | 2185.6 | 1946.6 | 8.0647
[5 empty] | 2185.8 | 1946.8 | 8.1621
[5 empty] | 2186 | 1947 | 8.0647
[5 empty] | 2186.2 | 1947.2 | 8.1621
[5 empty] | 2186.4 | 1947.4 | 8.2595
[5 empty] | 2186.6 | 1947.6 | 8.1621
[5 empty] | 2186.8 | 1947.8 | 8.2595
[5 empty] | 2187 | 1948 | 8.1621
[5 empty] | 2187.2 | 1948.2 | 8.2595
[5 empty] | 2187.4 | 1948.4 | 8.1621
[5 empty] | 2187.6 | 1948.6 | 8.1621
[5 empty] | 2187.8 | 1948.8 | 8.2595
[5 empty] | 2188 | 1949 | 8.2595
[5 empty] | 2188.2 | 1949.2 | 8.1621
[5 empty] | 2188.4 | 1949.4 | 8.2595
[5 empty] | 2188.6 | 1949.6 | 8.3569
[5 empty] | 2188.8 | 1949.8 | 8.4543
[5 empty] | 2189 | 1950 | 8.3569
[5 empty] | 2189.2 | 1950.2 | 8.4543
[5 empty] | 2189.4 | 1950.4 | 8.4543
[5 empty] | 2189.6 | 1950.6 | 8.4543
[5 empty] | 2189.8 | 1950.8 | 8.4543
[5 empty] | 2190 | 1951 | 8.4543
[5 empty] | 2190.2 | 1951.2 | 8.5517
[5 empty] | 2190.4 | 1951.4 | 8.5517
[5 empty] | 2190.6 | 1951.6 | 8.6491
[5 empty] | 2190.8 | 1951.8 | 8.6491
[5 empty] | 2191 | 1952 | 8.5517
[5 empty] | 2191.2 | 1952.2 | 8.6491
[5 empty] | 2191.4 | 1952.4 | 8.6491
[5 empty] | 2191.6 | 1952.6 | 8.7465
[5 empty] | 2191.8 | 1952.8 | 8.8439
[5 empty] | 2192 | 1953 | 8.8439
[5 empty] | 2192.2 | 1953.2 | 8.8439
[5 empty] | 2192.4 | 1953.4 | 8.8439
[5 empty] | 2192.6 | 1953.6 | 8.9413
[5 empty] | 2192.8 | 1953.8 | 8.9413
[5 empty] | 2193 | 1954 | 8.9413
[5 empty] | 2193.2 | 1954.2 | 9.3309
[5 empty] | 2193.4 | 1954.4 | 9.1361
[5 empty] | 2193.6 | 1954.6 | 9.1361
[5 empty] | 2193.8 | 1954.8 | 9.2334
[5 empty] | 2194 | 1955 | 9.1361
[5 empty] | 2194.2 | 1955.2 | 9.2334
[5 empty] | 2194.4 | 1955.4 | 9.2334
[5 empty] | 2194.6 | 1955.6 | 9.3309
[5 empty] | 2194.8 | 1955.8 | 9.3309
[5 empty] | 2195 | 1956 | 9.4282
[5 empty] | 2195.2 | 1956.2 | 9.4282
[5 empty] | 2195.4 | 1956.4 | 9.5257
[5 empty] | 2195.6 | 1956.6 | 9.623
[5 empty] | 2195.8 | 1956.8 | 9.623
[5 empty] | 2196 | 1957 | 9.7204
[5 empty] | 2196.2 | 1957.2 | 9.623
[5 empty] | 2196.4 | 1957.4 | 9.9152
[5 empty] | 2196.6 | 1957.6 | 10.8892
[5 empty] | 2196.8 | 1957.8 | 11.7658
[5 empty] | 2197 | 1958 | 12.4475
[5 empty] | 2197.2 | 1958.2 | 12.0579
[5 empty] | 2197.4 | 1958.4 | 13.5189
[5 empty] | 2197.6 | 1958.6 | 12.2527
[5 empty] | 2197.8 | 1958.8 | 15.8564
[5 empty] | 2198 | 1959 | 23.8429
[5 empty] | 2198.2 | 1959.2 | 23.9403
[5 empty] | 2198.4 | 1959.4 | 19.7523
[5 empty] | 2198.6 | 1959.6 | 19.8497
[5 empty] | 2198.8 | 1959.8 | 22.4794
[5 empty] | 2199 | 1960 | 11.2788
[5 empty] | 2199.2 | 1960.2 | 13.8111
[5 empty] | 2199.4 | 1960.4 | 14.7851
[5 empty] | 2199.6 | 1960.6 | 22.2846
[5 empty] | 2199.8 | 1960.8 | 12.7397
[5 empty] | 2200 | 1961 | 106.63
[5 empty] | 2200.2 | 1961.2 | 124.5509
[5 empty] | 2200.4 | 1961.4 | 124.6483
[5 empty] | 2200.6 | 1961.6 | 126.2067
[5 empty] | 2200.8 | 1961.8 | 126.3041
[5 empty] | 2201 | 1962 | 126.3041
[5 empty] | 2201.2 | 1962.2 | 126.3041
[5 empty] | 2201.4 | 1962.4 | 126.4015
[5 empty] | 2201.6 | 1962.6 | 126.3041
[5 empty] | 2201.8 | 1962.8 | 126.4989
[5 empty] | 2202 | 1963 | 126.4015
[5 empty] | 2202.2 | 1963.2 | 126.4989
[5 empty] | 2202.4 | 1963.4 | 126.4989
[5 empty] | 2202.6 | 1963.6 | 126.3041
[5 empty] | 2202.8 | 1963.8 | 126.4015
[5 empty] | 2203 | 1964 | 126.4015
[5 empty] | 2203.2 | 1964.2 | 126.3041
[5 empty] | 2203.4 | 1964.4 | 126.3041
[5 empty] | 2203.6 | 1964.6 | 126.2067
[5 empty] | 2203.8 | 1964.8 | 126.3041
[5 empty] | 2204 | 1965 | 126.2067
[5 empty] | 2204.2 | 1965.2 | 126.2067
[5 empty] | 2204.4 | 1965.4 | 81.6965
[5 empty] | 2204.6 | 1965.6 | 30.9529
[5 empty] | 2204.8 | 1965.8 | 31.0503
[5 empty] | 2205 | 1966 | 40.7899
[5 empty] | 2205.2 | 1966.2 | 119.1941
[5 empty] | 2205.4 | 1966.4 | 126.3041
[5 empty] | 2205.6 | 1966.6 | 126.7911
[5 empty] | 2205.8 | 1966.8 | 126.8885
[5 empty] | 2206 | 1967 | 126.7911
[5 empty] | 2206.2 | 1967.2 | 126.8885
[5 empty] | 2206.4 | 1967.4 | 126.8885
[5 empty] | 2206.6 | 1967.6 | 126.8885
[5 empty] | 2206.8 | 1967.8 | 126.9859
[5 empty] | 2207 | 1968 | 126.8885
[5 empty] | 2207.2 | 1968.2 | 126.8885
[5 empty] | 2207.4 | 1968.4 | 126.8885
[5 empty] | 2207.6 | 1968.6 | 126.9859
[5 empty] | 2207.8 | 1968.8 | 127.0833
[5 empty] | 2208 | 1969 | 126.9859
[5 empty] | 2208.2 | 1969.2 | 126.9859
[5 empty] | 2208.4 | 1969.4 | 126.9859
[5 empty] | 2208.6 | 1969.6 | 126.9859
[5 empty] | 2208.8 | 1969.8 | 126.9859
[5 empty] | 2209 | 1970 | 126.9859
[5 empty] | 2209.2 | 1970.2 | 127.0833
[5 empty] | 2209.4 | 1970.4 | 127.0833
[5 empty] | 2209.6 | 1970.6 | 127.0833
[5 empty] | 2209.8 | 1970.8 | 126.9859
[5 empty] | 2210 | 1971 | 126.7911
[5 empty] | 2210.2 | 1971.2 | 126.8885
[5 empty] | 2210.4 | 1971.4 | 126.8885
[5 empty] | 2210.6 | 1971.6 | 126.8885
[5 empty] | 2210.8 | 1971.8 | 126.8885
[5 empty] | 2211 | 1972 | 126.8885
[5 empty] | 2211.2 | 1972.2 | 126.8885
[5 empty] | 2211.4 | 1972.4 | 126.9859
[5 empty] | 2211.6 | 1972.6 | 126.9859
[5 empty] | 2211.8 | 1972.8 | 126.9859
[5 empty] | 2212 | 1973 | 126.7911
[5 empty] | 2212.2 | 1973.2 | 126.7911
[5 empty] | 2212.4 | 1973.4 | 126.6937
[5 empty] | 2212.6 | 1973.6 | 126.6937
[5 empty] | 2212.8 | 1973.8 | 126.7911
[5 empty] | 2213 | 1974 | 126.6937
[5 empty] | 2213.2 | 1974.2 | 126.7911
[5 empty] | 2213.4 | 1974.4 | 126.7911
[5 empty] | 2213.6 | 1974.6 | 126.7911
[5 empty] | 2213.8 | 1974.8 | 126.6937
[5 empty] | 2214 | 1975 | 126.5963
[5 empty] | 2214.2 | 1975.2 | 126.6937
[5 empty] | 2214.4 | 1975.4 | 126.5963
[5 empty] | 2214.6 | 1975.6 | 126.5963
[5 empty] | 2214.8 | 1975.8 | 126.6937
[5 empty] | 2215 | 1976 | 126.5963
[5 empty] | 2215.2 | 1976.2 | 126.6937
[5 empty] | 2215.4 | 1976.4 | 126.6937
[5 empty] | 2215.6 | 1976.6 | 126.6937
[5 empty] | 2215.8 | 1976.8 | 126.5963
[5 empty] | 2216 | 1977 | 126.5963
[5 empty] | 2216.2 | 1977.2 | 126.9859
[5 empty] | 2216.4 | 1977.4 | 126.6937
[5 empty] | 2216.6 | 1977.6 | 126.5963
[5 empty] | 2216.8 | 1977.8 | 126.4989
[5 empty] | 2217 | 1978 | 126.4989
[5 empty] | 2217.2 | 1978.2 | 126.4015
[5 empty] | 2217.4 | 1978.4 | 126.4015
[5 empty] | 2217.6 | 1978.6 | 126.3041
[5 empty] | 2217.8 | 1978.8 | 126.4989
[5 empty] | 2218 | 1979 | 126.4015
[5 empty] | 2218.2 | 1979.2 | 126.3041
[5 empty] | 2218.4 | 1979.4 | 126.2067
[5 empty] | 2218.6 | 1979.6 | 126.2067
[5 empty] | 2218.8 | 1979.8 | 126.2067
[5 empty] | 2219 | 1980 | 126.2067
[5 empty] | 2219.2 | 1980.2 | 126.1093
[5 empty] | 2219.4 | 1980.4 | 126.1093
[5 empty] | 2219.6 | 1980.6 | 126.1093
[5 empty] | 2219.8 | 1980.8 | 126.0119
[5 empty] | 2220 | 1981 | 125.9145
[5 empty] | 2220.2 | 1981.2 | 125.9145
[5 empty] | 2220.4 | 1981.4 | 125.9145
[5 empty] | 2220.6 | 1981.6 | 109.2597
[5 empty] | 2220.8 | 1981.8 | 125.6223
[5 empty] | 2221 | 1982 | 126.7911
[5 empty] | 2221.2 | 1982.2 | 126.6937
[5 empty] | 2221.4 | 1982.4 | 126.5963
[5 empty] | 2221.6 | 1982.6 | 126.5963
[5 empty] | 2221.8 | 1982.8 | 126.6937
[5 empty] | 2222 | 1983 | 126.7911
[5 empty] | 2222.2 | 1983.2 | 126.6937
[5 empty] | 2222.4 | 1983.4 | 126.8885
[5 empty] | 2222.6 | 1983.6 | 126.8885
[5 empty] | 2222.8 | 1983.8 | 126.6937
[5 empty] | 2223 | 1984 | 126.7911
[5 empty] | 2223.2 | 1984.2 | 126.6937
[5 empty] | 2223.4 | 1984.4 | 126.4989
[5 empty] | 2223.6 | 1984.6 | 126.3041
[5 empty] | 2223.8 | 1984.8 | 121.5317
[5 empty] | 2224 | 1985 | 122.603
[5 empty] | 2224.2 | 1985.2 | 122.7978
[5 empty] | 2224.4 | 1985.4 | 124.1614
[5 empty] | 2224.6 | 1985.6 | 126.3041
[5 empty] | 2224.8 | 1985.8 | 126.4989
[5 empty] | 2225 | 1986 | 126.3041
[5 empty] | 2225.2 | 1986.2 | 126.4989
[5 empty] | 2225.4 | 1986.4 | 126.4989
[5 empty] | 2225.6 | 1986.6 | 126.1093
[5 empty] | 2225.8 | 1986.8 | 126.4015
[5 empty] | 2226 | 1987 | 126.2067
[5 empty] | 2226.2 | 1987.2 | 126.0119
[5 empty] | 2226.4 | 1987.4 | 125.3301
[5 empty] | 2226.6 | 1987.6 | 126.1093
[5 empty] | 2226.8 | 1987.8 | 126.0119
[5 empty] | 2227 | 1988 | 126.4015
[5 empty] | 2227.2 | 1988.2 | 126.2067
[5 empty] | 2227.4 | 1988.4 | 126.3041
[5 empty] | 2227.6 | 1988.6 | 125.6223
[5 empty] | 2227.8 | 1988.8 | 125.3301
[5 empty] | 2228 | 1989 | 124.2587
[5 empty] | 2228.2 | 1989.2 | 125.9145
[5 empty] | 2228.4 | 1989.4 | 126.1093
[5 empty] | 2228.6 | 1989.6 | 125.2327
[5 empty] | 2228.8 | 1989.8 | 122.9926
[5 empty] | 2229 | 1990 | 123.2848
[5 empty] | 2229.2 | 1990.2 | 121.9212
[5 empty] | 2229.4 | 1990.4 | 123.1874
[5 empty] | 2229.6 | 1990.6 | 123.4796
[5 empty] | 2229.8 | 1990.8 | 123.2848
[5 empty] | 2230 | 1991 | 123.8692
[5 empty] | 2230.2 | 1991.2 | 120.3629
[5 empty] | 2230.4 | 1991.4 | 117.8306
[5 empty] | 2230.6 | 1991.6 | 117.6358
[5 empty] | 2230.8 | 1991.8 | 119.2915
[5 empty] | 2231 | 1992 | 120.3629
[5 empty] | 2231.2 | 1992.2 | 124.0639
[5 empty] | 2231.4 | 1992.4 | 124.9405
[5 empty] | 2231.6 | 1992.6 | 123.8692
[5 empty] | 2231.8 | 1992.8 | 123.8692
[5 empty] | 2232 | 1993 | 121.2395
[5 empty] | 2232.2 | 1993.2 | 119.7785
[5 empty] | 2232.4 | 1993.4 | 121.3369
[5 empty] | 2232.6 | 1993.6 | 120.3629
[5 empty] | 2232.8 | 1993.8 | 120.9473
[5 empty] | 2233 | 1994 | 122.7978
[5 empty] | 2233.2 | 1994.2 | 123.8692
[5 empty] | 2233.4 | 1994.4 | 123.8692
[5 empty] | 2233.6 | 1994.6 | 124.1614
[5 empty] | 2233.8 | 1994.8 | 125.4275
[5 empty] | 2234 | 1995 | 124.6483
[5 empty] | 2234.2 | 1995.2 | 125.3301
[5 empty] | 2234.4 | 1995.4 | 124.0639
[5 empty] | 2234.6 | 1995.6 | 124.4535
[5 empty] | 2234.8 | 1995.8 | 122.3108
[5 empty] | 2235 | 1996 | 123.7718
[5 empty] | 2235.2 | 1996.2 | 124.9405
[5 empty] | 2235.4 | 1996.4 | 120.3629
[5 empty] | 2235.6 | 1996.6 | 120.0707
[5 empty] | 2235.8 | 1996.8 | 123.7718
[5 empty] | 2236 | 1997 | 123.6744
[5 empty] | 2236.2 | 1997.2 | 125.1353
[5 empty] | 2236.4 | 1997.4 | 125.0379
[5 empty] | 2236.6 | 1997.6 | 124.1614
[5 empty] | 2236.8 | 1997.8 | 124.8431
[5 empty] | 2237 | 1998 | 124.4535
[5 empty] | 2237.2 | 1998.2 | 122.9926
[5 empty] | 2237.4 | 1998.4 | 122.7004
[5 empty] | 2237.6 | 1998.6 | 123.1874
[5 empty] | 2237.8 | 1998.8 | 122.7004
[5 empty] | 2238 | 1999 | 120.8499
[5 empty] | 2238.2 | 1999.2 | 122.8952
[5 empty] | 2238.4 | 1999.4 | 124.4535
[5 empty] | 2238.6 | 1999.6 | 121.8238
[5 empty] | 2238.8 | 1999.8 | 124.2587
[5 empty] | 2239 | 2000 | 125.0379
[5 empty] | 2239.2 | 2000.2 | 124.7457
[5 empty] | 2239.4 | 2000.4 | 121.4342
[5 empty] | 2239.6 | 2000.6 | 124.1614
[5 empty] | 2239.8 | 2000.8 | 124.7457
[5 empty] | 2240 | 2001 | 124.7457
[5 empty] | 2240.2 | 2001.2 | 124.1614
[5 empty] | 2240.4 | 2001.4 | 123.577
[5 empty] | 2240.6 | 2001.6 | 123.1874
[5 empty] | 2240.8 | 2001.8 | 124.1614
[5 empty] | 2241 | 2002 | 123.6744
[5 empty] | 2241.2 | 2002.2 | 119.5837
[5 empty] | 2241.4 | 2002.4 | 109.6493
[5 empty] | 2241.6 | 2002.6 | 102.5393
[5 empty] | 2241.8 | 2002.8 | 102.4419
[5 empty] | 2242 | 2003 | 30.6607
[5 empty] | 2242.2 | 2003.2 | 4.5584
[5 empty] | 2242.4 | 2003.4 | 1.7339
[5 empty] | 2242.6 | 2003.6 | 1.1496
[5 empty] | 2242.8 | 2003.8 | 0.95476
[5 empty] | 2243 | 2004 | 0.85734
[5 empty] | 2243.2 | 2004.2 | 0.75996
[5 empty] | 2243.4 | 2004.4 | 0.66258
[5 empty] | 2243.6 | 2004.6 | 0.75996
[5 empty] | 2243.8 | 2004.8 | 0.66258
[5 empty] | 2244 | 2005 | 0.66258
[5 empty] | 2244.2 | 2005.2 | 0.66258
[5 empty] | 2244.4 | 2005.4 | 0.66258
[5 empty] | 2244.6 | 2005.6 | 0.56516
[5 empty] | 2244.8 | 2005.8 | 0.66258
[5 empty] | 2245 | 2006 | 0.56516
[5 empty] | 2245.2 | 2006.2 | 0.56516
[5 empty] | 2245.4 | 2006.4 | 0.56516
[5 empty] | 2245.6 | 2006.6 | 0.56516
[5 empty] | 2245.8 | 2006.8 | 0.56516
[5 empty] | 2246 | 2007 | 0.56516
[5 empty] | 2246.2 | 2007.2 | 0.56516
[5 empty] | 2246.4 | 2007.4 | 0.46777
[5 empty] | 2246.6 | 2007.6 | 0.46777
[5 empty] | 2246.8 | 2007.8 | 0.46777
[5 empty] | 2247 | 2008 | 0.56516
[5 empty] | 2247.2 | 2008.2 | 0.46777
[5 empty] | 2247.4 | 2008.4 | 0.56516
[5 empty] | 2247.6 | 2008.6 | 0.46777
[5 empty] | 2247.8 | 2008.8 | 0.46777
[5 empty] | 2248 | 2009 | 0.56516
[5 empty] | 2248.2 | 2009.2 | 0.46777
[5 empty] | 2248.4 | 2009.4 | 0.56516
[5 empty] | 2248.6 | 2009.6 | 0.46777
[5 empty] | 2248.8 | 2009.8 | 0.46777
[5 empty] | 2249 | 2010 | 0.46777
[5 empty] | 2249.2 | 2010.2 | 0.56516
[5 empty] | 2249.4 | 2010.4 | 0.46777
[5 empty] | 2249.6 | 2010.6 | 0.56516
[5 empty] | 2249.8 | 2010.8 | 0.46777
[5 empty] | 2250 | 2011 | 0.46777
[5 empty] | 2300 | 2061 | 0.46777
[5 empty] | 2360 | 2121 | 0.56516
[5 empty] | 2420 | 2181 | 0.46777
[5 empty] | 2480 | 2241 | 0.46777