## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 14, Location G, IRMS #2
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE/CSPE, EPR/CPE, PE/PVC, PVC/PVC, XLPE/PVC & Tefzel/Tefzel control cables (Items 10, 2, 15, 1, 3 & 12). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position F in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 300 kW heat release rate. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 236 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
236 | 0 | Ignited Gas Burner
871 | 635 | Conductor C5 shorts to ground at less than 100 ohms (4)
881 | 645 | Conductors C5 & C6 short together at less than 100 ohms (17) | Cable C shorts internally
911 | 675 | Conductor C6 shorts to ground at less than 100 ohms (54) | Cable C shorted to ground
1242 | 1006 | Conductor B4 shorts to ground at less than 1000 ohms (378)
1285 | 1049 | Conductor B3 shorts to ground at less than 100 ohms (30) and the existing ground fault on conductor B4 decreases to less than 100 ohms (4) | Cable B shorted to ground
1286 | 1050 | Conductors B3 & B4 short together at less than 100 ohms (73) | Cable B shorted internally
1949 | 1713 | Extinguished Gas Burner
1990 | 1754 | Conductor A2 shorts to ground at less than 100 ohms (37)
2017 | 1781 | Conductors A1 & A2 short together at less than 1000 ohms (361) | Cable A shorts internally
2022 | 1786 | Conductor A1 shorts to ground at less than 100 ohms (25) | Cable A shorted to ground
Additional Observations
Observation 1 | The cables usually shorted internally prior to shorting to ground.
Observation 2 | The progression of cable failure was that the lower cables failed before the top cable.
Observation 3 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
|  |  |  | Cable D = | PVC | (Item #1)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | TEFZEL | (Item #12)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| G1 | = | Center of bundle, under jacket
| G2 | = | Air above bundle
| G3 | = | Air below bundle
| G4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | PE | (Item #15)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 14 |  |  | 2006-11-29 | 11:22
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-235 | 503375.9997 | -232 | 500775.9997 | -229 | 505775.9997 | -226.5 | 516375.9997 | -223.5 | 521575.9997 | -220.5 | 505775.9997 | -218 | 501375.9997 | -215 | 526975.9997 | -212.5 | 518175.9997 | -209.5 | 508575.9997 | -206.5 | #REF! | -204 | 517775.9997 | -201 | 520575.9997 | -198.5 | 524775.9997 | -195.5 | 524775.9997
-192.5 | 503375.9997 | -190 | 500775.9997 | -187.5 | 505775.9997 | -184.5 | 516375.9997 | -181.5 | 521575.9997 | -179 | 505775.9997 | -176 | 501375.9997 | -173.5 | 526975.9997 | -170.5 | 518175.9997 | -167.5 | 508575.9997 | -165 | #REF! | -162 | 517775.9997 | -159.5 | 520575.9997 | -156.5 | 524775.9997 | -153.5 | 524775.9997
-151 | 503375.9997 | -148 | 500775.9997 | -145.5 | 505775.9997 | -142.5 | 516375.9997 | -139.5 | 521575.9997 | -136.5 | 505775.9997 | -134 | 501375.9997 | -131.5 | 526975.9997 | -128.5 | 518175.9997 | -125.5 | 508575.9997 | -123 | #REF! | -120 | 517775.9997 | -117.5 | 520575.9997 | -114.5 | 524775.9997 | -111.5 | 524775.9997
-109 | 503375.9997 | -106 | 500775.9997 | -103.5 | 505775.9997 | -100.5 | 516375.9997 | -97.5 | 521575.9997 | -95 | 505775.9997 | -92 | 501375.9997 | -89 | 526975.9997 | -86.5 | 518175.9997 | -83.5 | 508575.9997 | -81 | #REF! | -78 | 517775.9997 | -75 | 520575.9997 | -72.5 | 524775.9997 | -69.5 | 524775.9997
-67 | 503375.9997 | -64 | 500775.9997 | -61 | 505775.9997 | -58.5 | 516375.9997 | -55.5 | 521575.9997 | -53 | 505775.9997 | -50 | 501375.9997 | -47.5 | 526975.9997 | -44.5 | 518175.9997 | -41.5 | 508575.9997 | -39 | #REF! | -36 | 517775.9997 | -33.5 | 520575.9997 | -30.5 | 524775.9997 | -27.5 | 524775.9997
-25 | 503375.9997 | -22 | 500775.9997 | -19.5 | 505775.9997 | -16.5 | 516375.9997 | -13.5 | 521575.9997 | -11 | 505775.9997 | -8 | 501375.9997 | -5.5 | 526975.9997 | -2.5 | 518175.9997 | 0.5 | 508575.9997 | 3 | #REF! | 6 | 517775.9997 | 8.5 | 520575.9997 | 11.5 | 524775.9997 | 14.5 | 524775.9997
17 | 503375.9997 | 20 | 500775.9997 | 22.5 | 505775.9997 | 25.5 | 516375.9997 | 28.5 | 521575.9997 | 31 | 505775.9997 | 34 | 501375.9997 | 36.5 | 526975.9997 | 39.5 | 518175.9997 | 42.5 | 508575.9997 | 45 | #REF! | 48 | 517775.9997 | 50.5 | 520575.9997 | 53.5 | 524775.9997 | 56.5 | 524775.9997
59 | 503375.9997 | 62 | 500775.9997 | 64.5 | 505775.9997 | 67.5 | 516375.9997 | 70.5 | 521575.9997 | 73 | 505775.9997 | 76 | 501375.9997 | 78.5 | 526975.9997 | 81.5 | 518175.9997 | 84.5 | 508575.9997 | 87 | #REF! | 90 | 517775.9997 | 92.5 | 520575.9997 | 95.5 | 524775.9997 | 98.5 | 524775.9997
101 | 503375.9997 | 104 | 500775.9997 | 106.5 | 505775.9997 | 109.5 | 516375.9997 | 112.5 | 521575.9997 | 115 | 505775.9997 | 118 | 501375.9997 | 120.5 | 526975.9997 | 123.5 | 518175.9997 | 126.5 | 508575.9997 | 129 | #REF! | 132 | 517775.9997 | 134.5 | 520575.9997 | 137.5 | 524775.9997 | 140.5 | 524775.9997
143 | 503375.9997 | 146 | 500775.9997 | 148.5 | 505775.9997 | 151.5 | 516375.9997 | 154.5 | 521575.9997 | 157 | 505775.9997 | 160 | 501375.9997 | 162.5 | 526975.9997 | 165.5 | 518175.9997 | 168.5 | 508575.9997 | 192 | #REF! | 174 | 517775.9997 | 176.5 | 520575.9997 | 179.5 | 524775.9997 | 182.5 | 524775.9997
185 | 503375.9997 | 188 | 500775.9997 | 190.5 | 505775.9997 | 193.5 | 516375.9997 | 196.5 | 521575.9997 | 199 | 505775.9997 | 202 | 501375.9997 | 204.5 | 526975.9997 | 207.5 | 518175.9997 | 210.5 | 508575.9997 | 234 | #REF! | 216 | 517775.9997 | 218.5 | 520575.9997 | 221.5 | 524775.9997 | 224.5 | 524775.9997
227 | 503375.9997 | 230 | 500775.9997 | 232.5 | 505775.9997 | 235.5 | 516375.9997 | 238.5 | 521575.9997 | 241 | 505775.9997 | 244 | 501375.9997 | 246.5 | 526975.9997 | 249.5 | 518175.9997 | 252.5 | 508575.9997 | 276 | #REF! | 258 | 517775.9997 | 260.5 | 520575.9997 | 263.5 | 524775.9997 | 266.5 | 524775.9997
269 | 503375.9997 | 272 | 500775.9997 | 274.5 | 505775.9997 | 277.5 | 516375.9997 | 280.5 | 521575.9997 | 283 | 505775.9997 | 286 | 501375.9997 | 288.5 | 526975.9997 | 291.5 | 518175.9997 | 294.5 | 508575.9997 | 318 | #REF! | 300 | 517775.9997 | 302.5 | 520575.9997 | 305.5 | 524775.9997 | 308.5 | 524775.9997
311 | 503375.9997 | 314 | 500775.9997 | 316.5 | 505775.9997 | 319.5 | 516375.9997 | 322.5 | 521575.9997 | 325 | 505775.9997 | 328 | 501375.9997 | 330.5 | 526975.9997 | 333.5 | 518175.9997 | 336.5 | 508575.9997 | 360 | #REF! | 342 | 517775.9997 | 344.5 | 520575.9997 | 347.5 | 524775.9997 | 350.5 | 524775.9997
353 | 503375.9997 | 356 | 500775.9997 | 358.5 | 505775.9997 | 361.5 | 516375.9997 | 364.5 | 521575.9997 | 367 | 505775.9997 | 370 | 501375.9997 | 372.5 | 526975.9997 | 375.5 | 518175.9997 | 378.5 | 508575.9997 | 402 | #REF! | 384 | 517775.9997 | 386.5 | 520575.9997 | 389.5 | 524775.9997 | 392.5 | 524775.9997
395 | 503375.9997 | 398 | 500775.9997 | 400.5 | 505775.9997 | 403.5 | 516375.9997 | 406.5 | 521575.9997 | 409 | 505775.9997 | 412 | 501375.9997 | 414.5 | 526975.9997 | 417.5 | 518175.9997 | 420.5 | 508575.9997 | 444 | #REF! | 426 | 517775.9997 | 428.5 | 520575.9997 | 431.5 | 524775.9997 | 434.5 | 524775.9997
437 | 503375.9997 | 440 | 500775.9997 | 442.5 | 505775.9997 | 445.5 | 516375.9997 | 448.5 | 521575.9997 | 451 | 505775.9997 | 454 | 501375.9997 | 456.5 | 526975.9997 | 459.5 | 518175.9997 | 462.5 | 508575.9997 | 486 | #REF! | 468 | 517775.9997 | 470.5 | 520575.9997 | 473.5 | 524775.9997 | 476.5 | 524775.9997
479 | 503375.9997 | 482 | 500775.9997 | 484.5 | 505775.9997 | 487.5 | 516375.9997 | 490.5 | 521575.9997 | 493 | 505775.9997 | 496 | 501375.9997 | 498.5 | 526975.9997 | 501.5 | 518175.9997 | 504.5 | 508575.9997 | 528 | #REF! | 510 | 517775.9997 | 512.5 | 520575.9997 | 515.5 | 524775.9997 | 518.5 | 524775.9997
521 | 503375.9997 | 524 | 500775.9997 | 526.5 | 505775.9997 | 529.5 | 516375.9997 | 532.5 | 521575.9997 | 535 | 505775.9997 | 538 | 501375.9997 | 540.5 | 526975.9997 | 543.5 | 518175.9997 | 546.5 | 508575.9997 | 570 | #REF! | 552 | 517775.9997 | 554.5 | 520575.9997 | 557.5 | 524775.9997 | 560.5 | 524775.9997
563 | 503375.9997 | 566 | 500775.9997 | 568.5 | 505775.9997 | 571.5 | 516375.9997 | 574.5 | 521575.9997 | 577 | 505775.9997 | 579.5 | 501375.9997 | 582.5 | 526975.9997 | 585.5 | 518175.9997 | 588.5 | 508575.9997 | 612 | #REF! | 594 | 517775.9997 | 596.5 | 520575.9997 | 599.5 | 524775.9997 | 602.5 | 524775.9997
605 | 503375.9997 | 608 | 500775.9997 | 610.5 | 505775.9997 | 613.5 | 516375.9997 | 616.5 | 521575.9997 | 619 | 505775.9997 | 622 | 501375.9997 | 624.5 | 526975.9997 | 627.5 | 129394.0289 | 630.5 | 508575.9997 | 654 | #REF! | 636 | 517775.9997 | 638.5 | 520575.9997 | 641.5 | 524775.9997 | 644.5 | 17.401
647 | 251637.9994 | 650 | 500775.9997 | 652.5 | 505775.9997 | 655.5 | 516375.9997 | 658.5 | 130318.9988 | 661 | 252837.9994 | 663.5 | 501375.9997 | 666.5 | 526975.9997 | 669.5 | 86279.3315 | 672 | 254237.9994 | 696 | #REF! | 678 | 86212.6648 | 680.5 | 260237.9994 | 683.5 | 87379.3315 | 686 | 33.8822
689 | 83812.6648 | 692 | 250337.9994 | 694.5 | 252837.9994 | 697.5 | 258137.9994 | 700 | 86845.9982 | 703 | 84212.6648 | 706 | 250637.9994 | 708.5 | 263437.9994 | 711.5 | 129468.9988 | 714 | 84679.3315 | 738 | #REF! | 719.5 | 129368.9988 | 722.5 | 130068.9988 | 725.5 | 87379.3315 | 728.5 | 5.0485
731 | 83812.6648 | 734 | 125118.9988 | 736.5 | 252837.9994 | 739.5 | 258137.9994 | 742.5 | 130318.9988 | 745 | 126368.9988 | 748 | 250637.9994 | 750.5 | 263437.9994 | 753.5 | 129468.9988 | 756 | 84679.3315 | 780 | #REF! | 762 | 129368.9988 | 764.5 | 86679.3315 | 767.5 | 87379.3315 | 770.5 | 18.7194
773 | 83812.6648 | 775.5 | 250337.9994 | 778.5 | 252837.9994 | 781.5 | 258137.9994 | 784 | 130318.9988 | 787 | 84212.6648 | 789.5 | 250637.9994 | 792.5 | 263437.9994 | 795.5 | 129468.9988 | 798 | 84679.3315 | 822 | #REF! | 803.5 | 129368.9988 | 806.5 | 130068.9988 | 809.5 | 131118.9988 | 812 | 25.3943
815 | 125768.9988 | 818 | 250337.9994 | 820.5 | 252837.9994 | 823.5 | 258137.9994 | 826.5 | 130318.9988 | 829 | 126368.9988 | 832 | 250637.9994 | 834.5 | 263437.9994 | 837.5 | 129468.9988 | 840.5 | 127068.9988 | 864 | #REF! | 846 | 129368.9988 | 848.5 | 130068.9988 | 851.5 | 131118.9988 | 854 | 3.9626
857 | 125768.9988 | 859.5 | 250337.9994 | 862.5 | 252837.9994 | 865.5 | 258137.9994 | 868 | 130318.9988 | 871 | 126368.9988 | 873.5 | 250637.9994 | 876.5 | 263437.9994 | 879.5 | 129468.9988 | 882 | 127068.9988 | 906 | #REF! | 888 | 129368.9988 | 890.5 | 130068.9988 | 893.5 | 131118.9988 | 896 | 16.0575
899 | 83812.6648 | 901.5 | 250337.9994 | 904.5 | 252837.9994 | 907.5 | 258137.9994 | 910 | 130318.9988 | 913 | 126368.9988 | 916 | 250637.9994 | 918.5 | 263437.9994 | 921.5 | 129468.9988 | 924 | 127068.9988 | 948 | #REF! | 930 | 258837.9994 | 932.5 | 130068.9988 | 935.5 | 131118.9988 | 938.5 | 5.0924
941 | 125768.9988 | 944 | 250337.9994 | 946.5 | 252837.9994 | 949.5 | 258137.9994 | 952 | 130318.9988 | 955 | 126368.9988 | 957.5 | 250637.9994 | 960.5 | 263437.9994 | 963.5 | 129468.9988 | 966 | 127068.9988 | 990 | #REF! | 971.5 | 129368.9988 | 974.5 | 130068.9988 | 977.5 | 131118.9988 | 980 | 6.8319
983 | 125768.9988 | 985.5 | 250337.9994 | 988.5 | 252837.9994 | 991.5 | 258137.9994 | 994 | 130318.9988 | 997 | 126368.9988 | 999.5 | 250637.9994 | 1002.5 | 263437.9994 | 1005.5 | 129468.9988 | 1008 | 127068.9988 | 1032 | #REF! | 1013.5 | 129368.9988 | 1016.5 | 130068.9988 | 1019.5 | 377.694 | 1022 | 20.0668
1025 | 83812.6648 | 1027.5 | 250337.9994 | 1030.5 | 252837.9994 | 1033.5 | 258137.9994 | 1036 | 130318.9988 | 1039 | 126368.9988 | 1042 | 250637.9994 | 1044.5 | 263437.9994 | 1047.5 | 129468.9988 | 1050 | 73.379 | 1074 | #REF! | 1056 | 35.1956 | 1058.5 | 5.295 | 1061.5 | 39.351 | 1064 | 21.3861
1067 | 83812.6648 | 1069.5 | 250337.9994 | 1072.5 | 126368.9988 | 1075.5 | 129018.9988 | 1078.5 | 130318.9988 | 1081 | 126368.9988 | 1083.5 | 125268.9988 | 1086.5 | 263437.9994 | 1089.5 | 129468.9988 | 1092 | 538.2698 | 1116 | #REF! | 1097.5 | 52.186 | 1100.5 | 22.8676 | 1103.5 | 6.8773 | 1106 | 33.0459
1109 | 125768.9988 | 1112 | 125118.9988 | 1114.5 | 126368.9988 | 1117.5 | 129018.9988 | 1120 | 130318.9988 | 1123 | 126368.9988 | 1125.5 | 125268.9988 | 1128.5 | 263437.9994 | 1131.5 | 129468.9988 | 1134.5 | 76.6064 | 1158 | #REF! | 1140 | 75.6129 | 1142.5 | 27.454 | 1145.5 | 37.7764 | 1148 | 1.9782
1151 | 125768.9988 | 1153.5 | 125118.9988 | 1156.5 | 126368.9988 | 1159.5 | 129018.9988 | 1162 | 130318.9988 | 1165 | 126368.9988 | 1167.5 | 125268.9988 | 1170.5 | 263437.9994 | 1173.5 | 129468.9988 | 1176 | 309.4576 | 1200 | #REF! | 1181.5 | 27.5331 | 1184.5 | 26.182 | 1187.5 | 13.9172 | 1190 | 19.7272
1193 | 125768.9988 | 1195.5 | 125118.9988 | 1198.5 | 126368.9988 | 1201.5 | 129018.9988 | 1204 | 130318.9988 | 1207 | 126368.9988 | 1209.5 | 125268.9988 | 1212.5 | 263437.9994 | 1215.5 | 129468.9988 | 1218 | 439.1385 | 1242 | #REF! | 1223.5 | 33.6206 | 1226.5 | 3.8921 | 1229.5 | 23.3885 | 1232 | 18.8862
1235 | 125768.9988 | 1237.5 | 125118.9988 | 1240.5 | 252837.9994 | 1243.5 | 129018.9988 | 1246 | 130318.9988 | 1249 | 84212.6648 | 1251.5 | 125268.9988 | 1254.5 | 263437.9994 | 1257.5 | 259037.9994 | 1260 | 7168.5727 | 1284 | #REF! | 1265.5 | 12.3794 | 1268.5 | 26.7514 | 1271.5 | 2.3108 | 1274 | 0.96412
1277 | 251238.1986 | 1279.5 | 250337.9994 | 1282.5 | 126368.9988 | 1285.5 | 129018.9988 | 1288 | 260737.9994 | 1291 | 126368.9988 | 1293.5 | 125268.9988 | 1296.5 | 263437.9994 | 1299.5 | 129468.9988 | 1302 | 26.9833 | 1326 | #REF! | 1307.5 | 17.7241 | 1310.5 | 2.9907 | 1313.5 | 6.651 | 1316 | 26.0147
1319 | 125519.1589 | 1321.5 | 250337.9994 | 1324.5 | 252837.9994 | 1327.5 | 129018.9988 | 1330 | 130318.9988 | 1333 | 126368.9988 | 1335.5 | 250637.9994 | 1338.5 | 131668.9988 | 1341.5 | 129468.9988 | 1344 | 22.5109 | 1368 | #REF! | 1349.5 | 5.7463 | 1352.5 | 29.6746 | 1355.5 | 13.3051 | 1358 | 1.3601
1361 | 41689.8587 | 1363.5 | 250337.9994 | 1366.5 | 126368.9988 | 1369.5 | 129018.9988 | 1372 | 130318.9988 | 1375 | 126368.9988 | 1377.5 | 125268.9988 | 1380.5 | 263437.9994 | 1383.5 | 129468.9988 | 1386 | 25.1188 | 1410 | #REF! | 1391.5 | 33.2676 | 1394.5 | 20.4618 | 1397.5 | 3.2788 | 1400 | 25.7037
1403 | 11759.225 | 1405.5 | 250337.9994 | 1408.5 | 126368.9988 | 1411.5 | 129018.9988 | 1414 | 130318.9988 | 1417 | 126368.9988 | 1419.5 | 125268.9988 | 1422.5 | 263437.9994 | 1425.5 | 129468.9988 | 1428 | 5.1393 | 1452 | #REF! | 1433.5 | 28.0523 | 1436.5 | 29.2773 | 1439.5 | 15.1607 | 1442 | 4.8733
1445 | 6947.5025 | 1447.5 | 250337.9994 | 1450.5 | 126368.9988 | 1453.5 | 129018.9988 | 1456 | 130318.9988 | 1459 | 126368.9988 | 1461.5 | 125268.9988 | 1464.5 | 263437.9994 | 1467.5 | 129468.9988 | 1470 | 14.1058 | 1494 | #REF! | 1475.5 | 17.448 | 1478.5 | 31.5606 | 1481.5 | 14.4839 | 1484 | 0.45207
1487 | 3814.8488 | 1489.5 | 250337.9994 | 1492.5 | 126368.9988 | 1495.5 | 129018.9988 | 1498 | 130318.9988 | 1501 | 126368.9988 | 1503.5 | 125268.9988 | 1506.5 | 263437.9994 | 1509.5 | 129468.9988 | 1512 | 0.87402 | 1536 | #REF! | 1517.5 | 13.4002 | 1520.5 | 3.0759 | 1523.5 | 19.3894 | 1526 | 2.0197
1529 | 2555.4064 | 1531.5 | 250337.9994 | 1534.5 | 126368.9988 | 1537.5 | 129018.9988 | 1540 | 260737.9994 | 1543 | 126368.9988 | 1545.5 | 250637.9994 | 1548.5 | 263437.9994 | 1551.5 | 129468.9988 | 1554 | 35.6053 | 1578 | #REF! | 1559.5 | 14.807 | 1562.5 | 31.0163 | 1565.5 | 35.5861 | 1568 | 7.0135
1571 | 1849.1727 | 1573.5 | 125118.9988 | 1576.5 | 126368.9988 | 1579.5 | 129018.9988 | 1582 | 130318.9988 | 1585 | 126368.9988 | 1587.5 | 125268.9988 | 1590.5 | 263437.9994 | 1593.5 | 129468.9988 | 1596 | 10471.3171 | 1620 | #REF! | 1601.5 | 36.2904 | 1604.5 | 2.6089 | 1607.5 | 34.4456 | 1610 | 15.6866
1613 | 1750.7182 | 1615.5 | 125118.9988 | 1618.5 | 126368.9988 | 1621.5 | 258137.9994 | 1624 | 130318.9988 | 1627 | 126368.9988 | 1629.5 | 125268.9988 | 1632.5 | 263437.9994 | 1635.5 | 129468.9988 | 1638 | 172.3173 | 1662 | #REF! | 1643.5 | 42.354 | 1646.5 | 31.0163 | 1649.5 | 14.5357 | 1652 | 27.9762
1655 | 1266.2532 | 1657.5 | 250337.9994 | 1660.5 | 252837.9994 | 1663.5 | 258137.9994 | 1666 | 260737.9994 | 1669 | 252837.9994 | 1671.5 | 250637.9994 | 1674.5 | 263437.9994 | 1677.5 | 259037.9994 | 1680 | 844.992 | 1704 | #REF! | 1685.5 | 5.7914 | 1688.5 | 3.2895 | 1691.5 | 11.3099 | 1694 | 30.3965
1697 | 1022.4924 | 1699.5 | 250337.9994 | 1702.5 | 126368.9988 | 1705.5 | 258137.9994 | 1708 | 260737.9994 | 1711 | 252837.9994 | 1713.5 | 250637.9994 | 1716.5 | 263437.9994 | 1719.5 | 259037.9994 | 1722 | 2.0157 | 1746 | #REF! | 1727.5 | 17.5031 | 1730.5 | 1.7703 | 1733 | 8.3011 | 1736 | 35.0135
1739 | 1431.1364 | 1741.5 | 250337.9994 | 1744.5 | 252837.9994 | 1747.5 | 258137.9994 | 1750 | 130318.9988 | 1753 | 252837.9994 | 1755.5 | 2484.8686 | 1758.5 | 39.7118 | 1761.5 | 36.0294 | 1764 | 27.6388 | 1788 | #REF! | 1769.5 | 17.6688 | 1772.5 | 12.3369 | 1775.5 | 2.4361 | 1778 | 12.3488
1781 | 360.7253 | 1783.5 | 636.3748 | 1786.5 | 160.4384 | 1789.5 | 23.2459 | 1792 | 31.6105 | 1795 | 4.2382 | 1797.5 | 2.5694 | 1800.5 | 10.1321 | 1803.5 | 29.669 | 1806 | 13.8941 | 1830 | #REF! | 1811.5 | 25.1219 | 1814.5 | 33.3603 | 1817.5 | 2.7296 | 1820 | 3.8766
1823 | 1220.0615 | 1825.5 | 6.5782 | 1828.5 | 27.1265 | 1831.5 | 23.794 | 1834 | 17.9875 | 1837 | 1.6162 | 1839.5 | 30.8074 | 1842.5 | 20.1213 | 1845.5 | 23.5582 | 1848 | 11.8182 | 1872 | #REF! | 1853.5 | 3.541 | 1856.5 | 12.6395 | 1859.5 | 33.6722 | 1862 | 24.3532
1865 | 9481.9083 | 1867.5 | 23.6198 | 1870.5 | 12.2183 | 1873.5 | 13.3472 | 1876 | 28.2829 | 1879 | 15.5088 | 1881.5 | 18.117 | 1884.5 | 37.1772 | 1887.5 | 30.6772 | 1890 | 1193.62 | 1914 | #REF! | 1895.5 | 3.5842 | 1898.5 | 30.6784 | 1901.5 | 37.4065 | 1904 | 21.91
1907 | 328.7992 | 1909.5 | 17.4597 | 1912.5 | 6.9461 | 1915.5 | 29.6814 | 1918 | 35.3263 | 1921 | 0.68618 | 1923.5 | 16.417 | 1926.5 | 23.1347 | 1929.5 | 10.9184 | 1932 | 11588.8536 | #REF! | #REF! | 1937.5 | 21.844 | 1940.5 | 40.0554 | 1943.5 | 14.3804 | 1946 | 30.1306
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 14 |  |  | 2006-11-29 | 11:22
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-229.2 | 500776 |  | -220.2 | 501376 | -214.5 | #REF! | -211.2 | 501376 | -208.9 | #REF! | -206.8 | 517776
-187.2 | 500776 |  | -178.3 | 501376 | -172.7 | #REF! | -169.4 | 501376 | -167.2 | #REF! | -164.8 | 517776
-145.3 | 500776 |  | -136.3 | 501376 | -130.6 | #REF! | -127.4 | 501376 | -125.2 | #REF! | -122.8 | 517776
-103.3 | 500776 |  | -94.3 | 501376 | -88.7 | #REF! | -85.3 | 501376 | -83 | #REF! | -80.8 | 517776
-61.2 | 500776 |  | -52.4 | 501376 | -46.7 | #REF! | -43.3 | 501376 | -41.2 | #REF! | -38.8 | 517776
-19.3 | 500776 |  | -10.4 | 501376 | -4.7 | #REF! | -1.4 | 501376 | 0.8 | #REF! | 3.2 | 517776
22.7 | 500776 |  | 31.6 | 501376 | 37.3 | #REF! | 40.6 | 501376 | 42.8 | #REF! | 45.2 | 517776
64.7 | 500776 |  | 73.6 | 501376 | 79.3 | #REF! | 82.6 | 501376 | 84.8 | #REF! | 87.2 | 517776
106.7 | 500776 |  | 115.6 | 501376 | 121.3 | #REF! | 124.6 | 501376 | 126.8 | #REF! | 129.2 | 517776
148.7 | 500776 |  | 157.6 | 501376 | 167.5 | #REF! | 166.6 | 501376 | 173 | #REF! | 171.2 | 517776
190.7 | 500776 |  | 199.6 | 501376 | 209.5 | #REF! | 208.6 | 501376 | 215 | #REF! | 213.2 | 517776
232.7 | 500776 |  | 241.6 | 501376 | 251.5 | #REF! | 250.6 | 501376 | 257 | #REF! | 255.2 | 517776
274.7 | 500776 |  | 283.6 | 501376 | 293.5 | #REF! | 292.6 | 501376 | 299 | #REF! | 297.2 | 517776
316.7 | 500776 |  | 325.6 | 501376 | 335.5 | #REF! | 334.6 | 501376 | 341 | #REF! | 339.2 | 517776
358.7 | 500776 |  | 367.6 | 501376 | 377.5 | #REF! | 376.6 | 501376 | 383 | #REF! | 381.2 | 517776
400.7 | 500776 |  | 409.6 | 501376 | 419.5 | #REF! | 418.6 | 501376 | 425 | #REF! | 423.2 | 517776
442.7 | 500776 |  | 451.6 | 501376 | 461.5 | #REF! | 460.6 | 501376 | 467 | #REF! | 465.2 | 517776
484.7 | 500776 |  | 493.6 | 501376 | 503.5 | #REF! | 502.6 | 501376 | 509 | #REF! | 507.2 | 517776
526.7 | 500776 |  | 535.6 | 501376 | 545.5 | #REF! | 544.6 | 501376 | 551 | #REF! | 549.2 | 517776
568.7 | 500776 |  | 577.5 | 501376 | 587.5 | #REF! | 586.5 | 501376 | 593 | #REF! | 591.2 | 517776
610.7 | 500776 |  | 619.6 | 259138.0193 | 629.5 | #REF! | 628.6 | 501376 | 635 | #REF! | 633.2 | 131119
652.7 | 130319 |  | 661.5 | 86279.3333 | 671.4 | #REF! | 670.4 | 87379.3333 | 676.9 | #REF! | 675.1 | 53.5623
694.6 | 83812.6667 |  | 703.6 | 84212.6667 | 713.3 | #REF! | 712.5 | 87379.3333 | 719 | #REF! | 717 | 2.8947
736.7 | 83812.6667 |  | 745.6 | 83812.6667 | 755.4 | #REF! | 754.5 | 86679.3333 | 761 | #REF! | 759.2 | 2.9976
778.5 | 83812.6667 |  | 787.5 | 84212.6667 | 797.2 | #REF! | 796.4 | 130069 | 802.9 | #REF! | 800.9 | 4.8913
820.7 | 125769 |  | 829.6 | 125769 | 839.5 | #REF! | 838.6 | 130069 | 844.9 | #REF! | 843.1 | 0.98986
862.5 | 125769 |  | 871.5 | 125769 | 881.3 | #REF! | 880.4 | 127069 | 886.9 | #REF! | 885 | 0.63612
904.5 | 83812.6667 |  | 913.6 | 126369 | 923.3 | #REF! | 922.5 | 130069 | 929 | #REF! | 927.1 | 0.62807
946.6 | 125769 |  | 955.5 | 125769 | 965.3 | #REF! | 964.4 | 130069 | 970.9 | #REF! | 968.9 | 2.0094
988.5 | 125769 |  | 997.5 | 125769 | 1007.2 | #REF! | 1006.4 | 378.0291 | 1012.9 | #REF! | 1010.9 | 3.6076
1030.5 | 83812.6667 |  | 1039.6 | 125769 | 1049.3 | #REF! | 1048.5 | 3.7091 | 1054.9 | #REF! | 1053 | 3.2408
1072.6 | 83812.6667 |  | 1081.5 | 125269 | 1091.2 | #REF! | 1090.4 | 8.3559 | 1096.9 | #REF! | 1095 | 2.9976
1114.6 | 125119 |  | 1123.5 | 125269 | 1133.5 | #REF! | 1132.5 | 13.2727 | 1138.9 | #REF! | 1137 | 9.1644
1156.5 | 125119 |  | 1165.5 | 125269 | 1175.2 | #REF! | 1174.4 | 15.3067 | 1180.9 | #REF! | 1178.9 | 0.66667
1198.5 | 125119 |  | 1207.5 | 125269 | 1217.2 | #REF! | 1216.4 | 1.7793 | 1222.9 | #REF! | 1220.9 | 1.1712
1240.5 | 125119 |  | 1249.5 | 84212.6667 | 1259.2 | #REF! | 1258.4 | 3.8536 | 1264.9 | #REF! | 1262.9 | 7.4815
1282.5 | 125743.9751 |  | 1291.5 | 125269 | 1301.2 | #REF! | 1300.4 | 3.1558 | 1306.9 | #REF! | 1304.9 | 0.9435
1324.5 | 125718.9204 |  | 1333.5 | 126369 | 1343.2 | #REF! | 1342.4 | 6.3286 | 1348.9 | #REF! | 1346.9 | 0.63194
1366.5 | 83678.8016 |  | 1375.5 | 125269 | 1385.2 | #REF! | 1384.4 | 4.8075 | 1390.9 | #REF! | 1388.9 | 1.5329
1408.5 | 126369 |  | 1417.5 | 41553.8097 | 1427.2 | #REF! | 1426.4 | 3.3054 | 1432.9 | #REF! | 1430.9 | 1.7838
1450.5 | 36010.7863 |  | 1459.5 | 27776.888 | 1469.2 | #REF! | 1468.4 | 0.68804 | 1474.9 | #REF! | 1472.9 | 6.8133
1492.5 | 12308.7648 |  | 1501.5 | 28936.5937 | 1511.2 | #REF! | 1510.4 | 4.5954 | 1516.9 | #REF! | 1514.9 | 2.428
1534.5 | 9398.9616 |  | 1543.5 | 19974.1693 | 1553.2 | #REF! | 1552.4 | 4.3224 | 1558.9 | #REF! | 1556.9 | 2.4904
1576.5 | 10204.0756 |  | 1585.5 | 16119.101 | 1595.2 | #REF! | 1594.4 | 4.1352 | 1600.9 | #REF! | 1598.9 | 3.2408
1618.5 | 3887.3913 |  | 1627.5 | 12169.7965 | 1637.2 | #REF! | 1636.4 | 0.65181 | 1642.9 | #REF! | 1640.9 | 5.2978
1660.5 | 4851.0057 |  | 1669.5 | 10714.0302 | 1679.2 | #REF! | 1678.4 | 4.806 | 1684.9 | #REF! | 1682.9 | 2.1557
1702.5 | 15394.9265 |  | 1711.5 | 7161.1332 | 1721.2 | #REF! | 1720.3 | 3.3087 | 1726.9 | #REF! | 1724.8 | 4.6404
1744.5 | 3142.01 |  | 1753.5 | 37.1826 | 1763.2 | #REF! | 1762.4 | 0.65181 | 1768.9 | #REF! | 1766.9 | 7.5324
1786.5 | 24.5121 |  | 1795.5 | 4.0407 | 1805.2 | #REF! | 1804.4 | 3.3894 | 1810.9 | #REF! | 1808.9 | 2.6753
1828.5 | 7.994 |  | 1837.5 | 2.1286 | 1847.2 | #REF! | 1846.4 | 14.0333 | 1852.9 | #REF! | 1850.9 | 2.5549
1870.5 | 13.5779 |  | 1879.5 | 16.8305 | 1889.2 | #REF! | 1888.4 | 0.65757 | 1894.9 | #REF! | 1892.9 | 0.63661
1912.5 | 0.65617 |  | 1921.5 | 2.1972 | #REF! | #REF! | 1930.4 | 15.7644 | #REF! | #REF! | 1934.9 | 0.82136
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39050.4688 | 0 | 0 | 39050.4688 | 0 | 0 |  | -195.5 | 40.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4693 | 0 | 0 | 39050.4693 | 0 | 0 |  | -153.5 | 82.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4698 | 0 | 0 | 39050.4698 | 0 | 0 |  | -111.5 | 124.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4702 | 0 | 0 | 39050.4703 | 0 | 0 |  | -69.5 | 166.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4707 | 0 | 0 | 39050.4707 | 0 | 0 |  | -27.5 | 208.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4712 | 0 | 0 | 39050.4712 | 0 | 0 |  | 14.5 | 250.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4717 | 0 | 0 | 39050.4717 | 0 | 0 |  | 56.5 | 292.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4722 | 0 | 0 | 39050.4722 | 0 | 0 |  | 98.5 | 334.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4727 | 0 | 0 | 39050.4727 | 0 | 0 |  | 140.5 | 376.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4732 | 0 | 0 | 39050.4732 | 0 | 0 |  | 182.5 | 418.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4736 | 0 | 0 | 39050.4737 | 0 | 0 |  | 224.5 | 460.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4741 | 0 | 0 | 39050.4741 | 0 | 0 |  | 266.5 | 502.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4746 | 0 | 0 | 39050.4746 | 0 | 0 |  | 308.5 | 544.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4751 | 0 | 0 | 39050.4751 | 0 | 0 |  | 350.5 | 586.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4756 | 0 | 0 | 39050.4756 | 0 | 0 |  | 392.5 | 628.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4761 | 0 | 0 | 39050.4761 | 0 | 0 |  | 434.5 | 670.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4766 | 0 | 0 | 39050.4766 | 0 | 0 |  | 476.5 | 712.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.477 | 0 | 0 | 39050.4771 | 0 | 0 |  | 518.5 | 754.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4775 | 0 | 0 | 39050.4775 | 0 | 0 |  | 560.5 | 796.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.478 | 0 | 0 | 39050.478 | 0 | 0 |  | 602.5 | 838.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4785 | 2210 | 0 | 39050.4785 | 2 | 0 |  | 644.5 | 880.5 | 134.9206 | 0 | 0.1221 | 0 | 1.3492 | 0 | 0.001221 | 0 | 1.3492 | 0.001221 | 18.7502 | 131119 | 17.401
39050.479 | 1943 | 0 | 39050.479 | 1709 | 0 |  | 686 | 922 | 118.6203 | 0 | 104.3346 | 0 | 1.1862 | 0 | 1.0433 | 0 | 1.1862 | 1.0433 | 35.0685 | 53.5623 | 33.8822
39050.4795 | 2463 | 0 | 39050.4795 | 2163 | 0 |  | 728.5 | 964.5 | 150.3663 | 0 | 132.0513 | 0 | 1.5037 | 0 | 1.3205 | 0 | 1.5037 | 1.3205 | 6.5522 | 21.3306 | 5.0485
39050.48 | 2186 | 0 | 39050.48 | 2281 | 0 |  | 770.5 | 1006.5 | 133.4554 | 0 | 139.2552 | 0 | 1.3346 | 0 | 1.3926 | 0 | 1.3346 | 1.3926 | 20.054 | 15.0539 | 18.7194
39050.4804 | 2072 | 0 | 39050.4805 | 2502 | 0 |  | 812 | 1048 | 126.4957 | 0 | 152.7473 | 0 | 1.265 | 0 | 1.5275 | 0 | 1.265 | 1.5275 | 26.6593 | 4.8913 | 25.3943
39050.4809 | 2488 | 0 | 39050.4809 | 2089 | 0 |  | 854 | 1090 | 151.8926 | 0 | 127.5336 | 0 | 1.5189 | 0 | 1.2753 | 0 | 1.5189 | 1.2753 | 5.4815 | 25.6285 | 3.9626
39050.4814 | 2235 | 0 | 39050.4814 | 1951 | 0 |  | 896 | 1132 | 136.4469 | 0 | 119.1087 | 0 | 1.3645 | 0 | 1.1911 | 0 | 1.3645 | 1.1911 | 17.4219 | 34.5146 | 16.0575
39050.4819 | 2462 | 0 | 39050.4819 | 2442 | 0 |  | 938.5 | 1174.5 | 150.3053 | 0 | 149.0842 | 0 | 1.5031 | 0 | 1.4908 | 0 | 1.5031 | 1.4908 | 6.5955 | 7.4685 | 5.0924
39050.4824 | 2423 | 0 | 39050.4824 | 2488 | 0 |  | 980 | 1216 | 147.9243 | 0 | 151.8926 | 0 | 1.4792 | 0 | 1.5189 | 0 | 1.4792 | 1.5189 | 8.3112 | 5.4815 | 6.8319
39050.4829 | 2162 | 0 | 39050.4829 | 2533 | 0 |  | 1022 | 1258 | 131.9902 | 0 | 154.6398 | 0 | 1.3199 | 0 | 1.5464 | 0 | 1.3199 | 1.5464 | 21.3867 | 3.6076 | 20.0668
39050.4834 | 2139 | 0 | 39050.4834 | 2542 | 0 |  | 1064 | 1300 | 130.5861 | 0 | 155.1893 | 0 | 1.3059 | 0 | 1.5519 | 0 | 1.3059 | 1.5519 | 22.6919 | 3.2408 | 21.3861
39050.4838 | 1955 | 0 | 39050.4839 | 2260 | 0 |  | 1106 | 1342 | 119.3529 | 0 | 137.9731 | 0 | 1.1935 | 0 | 1.3797 | 0 | 1.1935 | 1.3797 | 34.2394 | 16.123 | 33.0459
39050.4843 | 2535 | 0 | 39050.4844 | 2015 | 0 |  | 1148 | 1384 | 154.7619 | 0 | 123.0159 | 0 | 1.5476 | 0 | 1.2302 | 0 | 1.5476 | 1.2302 | 3.5258 | 30.2422 | 1.9782
39050.4848 | 2168 | 0 | 39050.4848 | 2607 | 0 |  | 1190 | 1426 | 132.3565 | 0 | 159.1575 | 0 | 1.3236 | 0 | 1.5916 | 0 | 1.3236 | 1.5916 | 21.0507 | 0.66667 | 19.7272
39050.4853 | 2183 | 0 | 39050.4853 | 2594 | 0 |  | 1232 | 1468 | 133.2723 | 0 | 158.3639 | 0 | 1.3327 | 0 | 1.5836 | 0 | 1.3327 | 1.5836 | 20.219 | 1.1712 | 18.8862
39050.4858 | 2608 | 0 | 39050.4858 | 2058 | 0 |  | 1274 | 1510 | 159.2186 | 0 | 125.641 | 0 | 1.5922 | 0 | 1.2564 | 0 | 1.5922 | 1.2564 | 0.62807 | 27.5209 | 0.96412
39050.4863 | 2062 | 0 | 39050.4863 | 2419 | 0 |  | 1316 | 1552 | 125.8852 | 0 | 147.6801 | 0 | 1.2589 | 0 | 1.4768 | 0 | 1.2589 | 1.4768 | 27.2735 | 8.4903 | 26.0147
39050.4868 | 2550 | 0 | 39050.4868 | 2112 | 0 |  | 1358 | 1594 | 155.6777 | 0 | 128.9377 | 0 | 1.5568 | 0 | 1.2894 | 0 | 1.5568 | 1.2894 | 2.9169 | 24.2604 | 1.3601
39050.4872 | 2067 | 0 | 39050.4873 | 2505 | 0 |  | 1400 | 1636 | 126.1905 | 0 | 152.9304 | 0 | 1.2619 | 0 | 1.5293 | 0 | 1.2619 | 1.5293 | 26.9657 | 4.7657 | 25.7037
39050.4877 | 2467 | 0 | 39050.4878 | 2219 | 0 |  | 1442 | 1678 | 150.6105 | 0 | 135.4701 | 0 | 1.5061 | 0 | 1.3547 | 0 | 1.5061 | 1.3547 | 6.3794 | 18.2686 | 4.8733
39050.4882 | 2595 | 0 | 39050.4882 | 2037 | 0 |  | 1484 | 1720 | 158.4249 | 0 | 124.359 | 0 | 1.5842 | 0 | 1.2436 | 0 | 1.5842 | 1.2436 | 1.1322 | 28.8355 | 0.45207
39050.4887 | 2534 | 0 | 39050.4887 | 1948 | 0 |  | 1526 | 1762 | 154.7009 | 0 | 118.9255 | 0 | 1.547 | 0 | 1.1893 | 0 | 1.547 | 1.1893 | 3.5667 | 34.7218 | 2.0197
39050.4892 | 2419 | 0 | 39050.4892 | 2516 | 0 |  | 1568 | 1804 | 147.6801 | 0 | 153.602 | 0 | 1.4768 | 0 | 1.536 | 0 | 1.4768 | 1.536 | 8.4903 | 4.3076 | 7.0135
39050.4897 | 2242 | 0 | 39050.4897 | 2402 | 0 |  | 1610 | 1846 | 136.8742 | 0 | 146.6422 | 0 | 1.3687 | 0 | 1.4664 | 0 | 1.3687 | 1.4664 | 17.0553 | 9.2581 | 15.6866
39050.4902 | 2031 | 0 | 39050.4902 | 1963 | 0 |  | 1652 | 1888 | 123.9927 | 0 | 119.8413 | 0 | 1.2399 | 0 | 1.1984 | 0 | 1.2399 | 1.1984 | 29.2161 | 33.6923 | 27.9762
39050.4906 | 1994 | 0 | 39050.4907 | 2569 | 0 |  | 1694 | 1930 | 121.7338 | 0 | 156.8376 | 0 | 1.2173 | 0 | 1.5684 | 0 | 1.2173 | 1.5684 | 31.6138 | 2.1557 | 30.3965
39050.4911 | 1927 | 0 | 39050.4912 | 2038 | 0 |  | 1736 | 1972 | 117.6435 | 0 | 124.42 | 0 | 1.1764 | 0 | 1.2442 | 0 | 1.1764 | 1.2442 | 36.1899 | 28.7723 | 35.0135
39050.4916 | 2307 | 0 | 39050.4916 | 2276 | 0 |  | 1778 | 2014 | 140.8425 | 0 | 138.9499 | 0 | 1.4084 | 0 | 1.3895 | 0 | 1.4084 | 1.3895 | 13.7573 | 15.3067 | 12.3488
39050.4921 | 2490 | 0 | 39050.4921 | 2556 | 0 |  | 1820 | 2056 | 152.0147 | 0 | 156.044 | 0 | 1.5201 | 0 | 1.5604 | 0 | 1.5201 | 1.5604 | 5.3968 | 2.6753 | 3.8766
39050.4926 | 2089 | 0 | 39050.4926 | 2280 | 0 |  | 1862 | 2098 | 127.5336 | 0 | 139.1941 | 0 | 1.2753 | 0 | 1.3919 | 0 | 1.2753 | 1.3919 | 25.6285 | 15.1044 | 24.3532
39050.4931 | 2130 | 0 | 39050.4931 | 2515 | 0 |  | 1904 | 2140 | 130.0366 | 0 | 153.5409 | 0 | 1.3004 | 0 | 1.5354 | 0 | 1.3004 | 1.5354 | 23.2103 | 4.3491 | 21.91
39050.4936 | 1998 | 0 | 39050.4936 | 2168 | 0 |  | 1946 | 2182 | 121.978 | 0 | 132.3565 | 0 | 1.2198 | 0 | 1.3236 | 0 | 1.2198 | 1.3236 | 31.3504 | 21.0507 | 30.1306

## B4-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39050.4688 | 0 | 0 | 39050.4688 | 0 | 0 |  | -198.5 | 37.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4692 | 0 | 0 | 39050.4692 | 0 | 0 |  | -156.5 | 79.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4697 | 0 | 0 | 39050.4697 | 0 | 0 |  | -114.5 | 121.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4702 | 0 | 0 | 39050.4702 | 0 | 0 |  | -72.5 | 163.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4707 | 0 | 0 | 39050.4707 | 0 | 0 |  | -30.5 | 205.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4712 | 0 | 0 | 39050.4712 | 0 | 0 |  | 11.5 | 247.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4717 | 0 | 0 | 39050.4717 | 0 | 0 |  | 53.5 | 289.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4722 | 0 | 0 | 39050.4722 | 0 | 0 |  | 95.5 | 331.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4726 | 0 | 0 | 39050.4727 | 0 | 0 |  | 137.5 | 373.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4731 | 0 | 0 | 39050.4731 | 0 | 0 |  | 179.5 | 415.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4736 | 0 | 0 | 39050.4736 | 0 | 0 |  | 221.5 | 457.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4741 | 0 | 0 | 39050.4741 | 0 | 0 |  | 263.5 | 499.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4746 | 0 | 0 | 39050.4746 | 0 | 0 |  | 305.5 | 541.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4751 | 0 | 0 | 39050.4751 | 0 | 0 |  | 347.5 | 583.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4756 | 0 | 0 | 39050.4756 | 0 | 0 |  | 389.5 | 625.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.476 | 0 | 0 | 39050.4761 | 0 | 0 |  | 431.5 | 667.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4765 | 0 | 0 | 39050.4765 | 0 | 0 |  | 473.5 | 709.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.477 | 0 | 0 | 39050.477 | 0 | 0 |  | 515.5 | 751.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4775 | 0 | 0 | 39050.4775 | 0 | 0 |  | 557.5 | 793.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.478 | 0 | 0 | 39050.478 | 0 | 0 |  | 599.5 | 835.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.4785 | 0 | 0 | 39050.4785 | 0 | 0 |  | 641.5 | 877.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39050.479 | 3 | 0 | 39050.479 | 1 | 0 |  | 683.5 | 919.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 87379.3333 | 262338 | 87379.3315
39050.4794 | 3 | 0 | 39050.4795 | 1978 | 0 |  | 725.5 | 961.5 | 0.18315 | 0 | 120.757 | 0 | 0.0018315 | 0 | 1.2076 | 0 | 0.0018315 | 1.2076 | 87379.3333 | 32.6785 | 87379.3315
39050.4799 | 3 | 0 | 39050.4799 | 2548 | 0 |  | 767.5 | 1003.5 | 0.18315 | 0 | 155.5556 | 0 | 0.0018315 | 0 | 1.5556 | 0 | 0.0018315 | 1.5556 | 87379.3333 | 2.9976 | 87379.3315
39050.4804 | 2 | 0 | 39050.4804 | 2252 | 0 |  | 809.5 | 1045.5 | 0.1221 | 0 | 137.4847 | 0 | 0.001221 | 0 | 1.3748 | 0 | 0.001221 | 1.3748 | 131119 | 16.5355 | 131118.9988
39050.4809 | 2 | 0 | 39050.4809 | 2230 | 0 |  | 851.5 | 1087.5 | 0.1221 | 0 | 136.1416 | 0 | 0.001221 | 0 | 1.3614 | 0 | 0.001221 | 1.3614 | 131119 | 17.6852 | 131118.9988
39050.4814 | 2 | 0 | 39050.4814 | 2464 | 0 |  | 893.5 | 1129.5 | 0.1221 | 0 | 150.4274 | 0 | 0.001221 | 0 | 1.5043 | 0 | 0.001221 | 1.5043 | 131119 | 6.5089 | 131118.9988
39050.4819 | 2 | 0 | 39050.4819 | 2608 | 0 |  | 935.5 | 1171.5 | 0.1221 | 0 | 159.2186 | 0 | 0.001221 | 0 | 1.5922 | 0 | 0.001221 | 1.5922 | 131119 | 0.62807 | 131118.9988
39050.4824 | 2 | 0 | 39050.4824 | 2542 | 0 |  | 977.5 | 1213.5 | 0.1221 | 0 | 155.1893 | 0 | 0.001221 | 0 | 1.5519 | 0 | 0.001221 | 1.5519 | 131119 | 3.2408 | 131118.9988
39050.4828 | 549 | 0 | 39050.4829 | 2452 | 0 |  | 1019.5 | 1255.5 | 33.5165 | 0 | 149.6947 | 0 | 0.33516 | 0 | 1.4969 | 0 | 0.33516 | 1.4969 | 378.0291 | 7.0302 | 377.694
39050.4833 | 1868 | 0 | 39050.4833 | 1934 | 0 |  | 1061.5 | 1297.5 | 114.0415 | 0 | 118.0708 | 0 | 1.1404 | 0 | 1.1807 | 0 | 1.1404 | 1.1807 | 40.4914 | 35.697 | 39.351
39050.4838 | 2422 | 0 | 39050.4838 | 2548 | 0 |  | 1103.5 | 1339.5 | 147.8632 | 0 | 155.5556 | 0 | 1.4786 | 0 | 1.5556 | 0 | 1.4786 | 1.5556 | 8.3559 | 2.9976 | 6.8773
39050.4843 | 1889 | 0 | 39050.4843 | 2115 | 0 |  | 1145.5 | 1381.5 | 115.3236 | 0 | 129.1209 | 0 | 1.1532 | 0 | 1.2912 | 0 | 1.1532 | 1.2912 | 38.9296 | 24.0842 | 37.7764
39050.4848 | 2276 | 0 | 39050.4848 | 2595 | 0 |  | 1187.5 | 1423.5 | 138.9499 | 0 | 158.4249 | 0 | 1.3895 | 0 | 1.5842 | 0 | 1.3895 | 1.5842 | 15.3067 | 1.1322 | 13.9172
39050.4853 | 2105 | 0 | 39050.4853 | 2532 | 0 |  | 1229.5 | 1465.5 | 128.5104 | 0 | 154.5788 | 0 | 1.2851 | 0 | 1.5458 | 0 | 1.2851 | 1.5458 | 24.6736 | 3.6485 | 23.3885
39050.4858 | 2527 | 0 | 39050.4858 | 2155 | 0 |  | 1271.5 | 1507.5 | 154.2735 | 0 | 131.5629 | 0 | 1.5427 | 0 | 1.3156 | 0 | 1.5427 | 1.3156 | 3.8536 | 21.781 | 2.3108
39050.4863 | 2427 | 0 | 39050.4863 | 2570 | 0 |  | 1313.5 | 1549.5 | 148.1685 | 0 | 156.8987 | 0 | 1.4817 | 0 | 1.569 | 0 | 1.4817 | 1.569 | 8.1327 | 2.116 | 6.651
39050.4867 | 2288 | 0 | 39050.4867 | 2247 | 0 |  | 1355.5 | 1591.5 | 139.6825 | 0 | 137.1795 | 0 | 1.3968 | 0 | 1.3718 | 0 | 1.3968 | 1.3718 | 14.7019 | 16.7948 | 13.3051
39050.4872 | 2504 | 0 | 39050.4872 | 1962 | 0 |  | 1397.5 | 1633.5 | 152.8694 | 0 | 119.7802 | 0 | 1.5287 | 0 | 1.1978 | 0 | 1.5287 | 1.1978 | 4.8075 | 33.7604 | 3.2788
39050.4877 | 2252 | 0 | 39050.4877 | 2509 | 0 |  | 1439.5 | 1675.5 | 137.4847 | 0 | 153.1746 | 0 | 1.3748 | 0 | 1.5317 | 0 | 1.3748 | 1.5317 | 16.5355 | 4.5986 | 15.1607
39050.4882 | 2265 | 0 | 39050.4882 | 2362 | 0 |  | 1481.5 | 1717.5 | 138.2784 | 0 | 144.2002 | 0 | 1.3828 | 0 | 1.442 | 0 | 1.3828 | 1.442 | 15.8667 | 11.1084 | 14.4839
39050.4887 | 2174 | 0 | 39050.4887 | 1953 | 0 |  | 1523.5 | 1759.5 | 132.7228 | 0 | 119.2308 | 0 | 1.3272 | 0 | 1.1923 | 0 | 1.3272 | 1.1923 | 20.7167 | 34.3769 | 19.3894
39050.4892 | 1919 | 0 | 39050.4892 | 1965 | 0 |  | 1565.5 | 1801.5 | 117.1551 | 0 | 119.9634 | 0 | 1.1716 | 0 | 1.1996 | 0 | 1.1716 | 1.1996 | 36.7577 | 33.5562 | 35.5861
39050.4897 | 1935 | 0 | 39050.4897 | 2542 | 0 |  | 1607.5 | 1843.5 | 118.1319 | 0 | 155.1893 | 0 | 1.1813 | 0 | 1.5519 | 0 | 1.1813 | 1.5519 | 35.6269 | 3.2408 | 34.4456
39050.4901 | 2264 | 0 | 39050.4902 | 2203 | 0 |  | 1649.5 | 1885.5 | 138.2173 | 0 | 134.4933 | 0 | 1.3822 | 0 | 1.3449 | 0 | 1.3822 | 1.3449 | 15.9178 | 19.1276 | 14.5357
39050.4906 | 2328 | 0 | 39050.4906 | 2390 | 0 |  | 1691.5 | 1927.5 | 142.1245 | 0 | 145.9096 | 0 | 1.4212 | 0 | 1.4591 | 0 | 1.4212 | 1.4591 | 12.7311 | 9.8067 | 11.3099
39050.4911 | 2391 | 0 | 39050.4911 | 2508 | 0 |  | 1733 | 1969 | 145.9707 | 0 | 153.1136 | 0 | 1.4597 | 0 | 1.5311 | 0 | 1.4597 | 1.5311 | 9.7608 | 4.6404 | 8.3011
39050.4916 | 2524 | 0 | 39050.4916 | 2168 | 0 |  | 1775.5 | 2011.5 | 154.0904 | 0 | 132.3565 | 0 | 1.5409 | 0 | 1.3236 | 0 | 1.5409 | 1.3236 | 3.977 | 21.0507 | 2.4361
39050.4921 | 2517 | 0 | 39050.4921 | 2389 | 0 |  | 1817.5 | 2053.5 | 153.663 | 0 | 145.8486 | 0 | 1.5366 | 0 | 1.4585 | 0 | 1.5366 | 1.4585 | 4.2662 | 9.8527 | 2.7296
39050.4926 | 1946 | 0 | 39050.4926 | 2559 | 0 |  | 1859.5 | 2095.5 | 118.8034 | 0 | 156.2271 | 0 | 1.188 | 0 | 1.5623 | 0 | 1.188 | 1.5623 | 34.8602 | 2.5549 | 33.6722
39050.4931 | 1894 | 0 | 39050.4931 | 2115 | 0 |  | 1901.5 | 2137.5 | 115.6288 | 0 | 129.1209 | 0 | 1.1563 | 0 | 1.2912 | 0 | 1.1563 | 1.2912 | 38.5628 | 24.0842 | 37.4065
39050.4935 | 2267 | 0 | 39050.4936 | 2603 | 0 |  | 1943.5 | 2179.5 | 138.4005 | 0 | 158.9133 | 0 | 1.384 | 0 | 1.5891 | 0 | 1.384 | 1.5891 | 15.7644 | 0.82136 | 14.3804

## B4-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 158.9365 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39050.4687 | 0 | 0 | 39050.4687 | 0 | 0 |  | -201 | 35 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4692 | 0 | 0 | 39050.4692 | 0 | 0 |  | -159.5 | 76.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4697 | 0 | 0 | 39050.4697 | 0 | 0 |  | -117.5 | 118.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4702 | 0 | 0 | 39050.4702 | 0 | 0 |  | -75 | 161 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4707 | 0 | 0 | 39050.4707 | 0 | 0 |  | -33.5 | 202.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4711 | 0 | 0 | 39050.4712 | 0 | 0 |  | 8.5 | 244.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4716 | 0 | 0 | 39050.4716 | 0 | 0 |  | 50.5 | 286.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4721 | 0 | 0 | 39050.4721 | 0 | 0 |  | 92.5 | 328.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4726 | 0 | 0 | 39050.4726 | 0 | 0 |  | 134.5 | 370.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4731 | 0 | 0 | 39050.4731 | 0 | 0 |  | 176.5 | 412.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4736 | 0 | 0 | 39050.4736 | 0 | 0 |  | 218.5 | 454.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4741 | 0 | 0 | 39050.4741 | 0 | 0 |  | 260.5 | 496.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4745 | 0 | 0 | 39050.4746 | 0 | 0 |  | 302.5 | 538.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.475 | 0 | 0 | 39050.475 | 0 | 0 |  | 344.5 | 580.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4755 | 0 | 0 | 39050.4755 | 0 | 0 |  | 386.5 | 622.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.476 | 0 | 0 | 39050.476 | 0 | 0 |  | 428.5 | 664.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4765 | 0 | 0 | 39050.4765 | 0 | 0 |  | 470.5 | 706.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.477 | 0 | 0 | 39050.477 | 0 | 0 |  | 512.5 | 748.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4775 | 0 | 0 | 39050.4775 | 0 | 0 |  | 554.5 | 790.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.478 | 0 | 0 | 39050.478 | 0 | 0 |  | 596.5 | 832.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4784 | 0 | 0 | 39050.4784 | 0 | 0 |  | 638.5 | 874.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520576 | 520576 | 520575.9997
39050.4789 | 1 | 0 | 39050.4789 | 2098 | 0 |  | 680.5 | 916.5 | 0.06105 | 0 | 128.083 | 0 | 0.0006105 | 0 | 1.2808 | 0 | 0.0006105 | 1.2808 | 260238 | 24.0887 | 260237.9994
39050.4794 | 2 | 0 | 39050.4794 | 2506 | 0 |  | 722.5 | 958.5 | 0.1221 | 0 | 152.9915 | 0 | 0.001221 | 0 | 1.5299 | 0 | 0.001221 | 1.5299 | 130069 | 3.8859 | 130068.9988
39050.4799 | 3 | 0 | 39050.4799 | 1957 | 0 |  | 764.5 | 1000.5 | 0.18315 | 0 | 119.475 | 0 | 0.0018315 | 0 | 1.1947 | 0 | 0.0018315 | 1.1947 | 86679.3333 | 33.0291 | 86679.3315
39050.4804 | 2 | 0 | 39050.4804 | 2064 | 0 |  | 806.5 | 1042.5 | 0.1221 | 0 | 126.0073 | 0 | 0.001221 | 0 | 1.2601 | 0 | 0.001221 | 1.2601 | 130069 | 26.1328 | 130068.9988
39050.4809 | 2 | 0 | 39050.4809 | 2175 | 0 |  | 848.5 | 1084.5 | 0.1221 | 0 | 132.7839 | 0 | 0.001221 | 0 | 1.3278 | 0 | 0.001221 | 1.3278 | 130069 | 19.6956 | 130068.9988
39050.4814 | 2 | 0 | 39050.4814 | 2414 | 0 |  | 890.5 | 1126.5 | 0.1221 | 0 | 147.3748 | 0 | 0.001221 | 0 | 1.4737 | 0 | 0.001221 | 1.4737 | 130069 | 7.8451 | 130068.9988
39050.4818 | 2 | 0 | 39050.4819 | 1977 | 0 |  | 932.5 | 1168.5 | 0.1221 | 0 | 120.696 | 0 | 0.001221 | 0 | 1.207 | 0 | 0.001221 | 1.207 | 130069 | 31.6834 | 130068.9988
39050.4823 | 2 | 0 | 39050.4823 | 2310 | 0 |  | 974.5 | 1210.5 | 0.1221 | 0 | 141.0256 | 0 | 0.001221 | 0 | 1.4103 | 0 | 0.001221 | 1.4103 | 130069 | 12.7004 | 130068.9988
39050.4828 | 2 | 0 | 39050.4828 | 2131 | 0 |  | 1016.5 | 1252.5 | 0.1221 | 0 | 130.0977 | 0 | 0.001221 | 0 | 1.301 | 0 | 0.001221 | 1.301 | 130069 | 22.1671 | 130068.9988
39050.4833 | 2438 | 0 | 39050.4833 | 2481 | 0 |  | 1058.5 | 1294.5 | 148.84 | 0 | 151.4652 | 0 | 1.4884 | 0 | 1.5147 | 0 | 1.4884 | 1.5147 | 6.7834 | 4.9327 | 5.295
39050.4838 | 2097 | 0 | 39050.4838 | 2282 | 0 |  | 1100.5 | 1336.5 | 128.022 | 0 | 139.3162 | 0 | 1.2802 | 0 | 1.3932 | 0 | 1.2802 | 1.3932 | 24.1478 | 14.0833 | 22.8676
39050.4843 | 2023 | 0 | 39050.4843 | 2156 | 0 |  | 1142.5 | 1378.5 | 123.5043 | 0 | 131.6239 | 0 | 1.235 | 0 | 1.3162 | 0 | 1.235 | 1.3162 | 28.6891 | 20.7505 | 27.454
39050.4848 | 2043 | 0 | 39050.4848 | 2040 | 0 |  | 1184.5 | 1420.5 | 124.7253 | 0 | 124.5421 | 0 | 1.2473 | 0 | 1.2454 | 0 | 1.2473 | 1.2454 | 27.4293 | 27.6167 | 26.182
39050.4852 | 2470 | 0 | 39050.4853 | 2542 | 0 |  | 1226.5 | 1462.5 | 150.7937 | 0 | 155.1893 | 0 | 1.5079 | 0 | 1.5519 | 0 | 1.5079 | 1.5519 | 5.4 | 2.4146 | 3.8921
39050.4857 | 2034 | 0 | 39050.4857 | 2090 | 0 |  | 1268.5 | 1504.5 | 124.1758 | 0 | 127.5946 | 0 | 1.2418 | 0 | 1.2759 | 0 | 1.2418 | 1.2759 | 27.9931 | 24.5636 | 26.7514
39050.4862 | 2491 | 0 | 39050.4862 | 2366 | 0 |  | 1310.5 | 1546.5 | 152.0757 | 0 | 144.4444 | 0 | 1.5208 | 0 | 1.4444 | 0 | 1.5208 | 1.4444 | 4.5114 | 10.033 | 2.9907
39050.4867 | 1989 | 0 | 39050.4867 | 2048 | 0 |  | 1352.5 | 1588.5 | 121.4286 | 0 | 125.0305 | 0 | 1.2143 | 0 | 1.2503 | 0 | 1.2143 | 1.2503 | 30.8889 | 27.1182 | 29.6746
39050.4872 | 2138 | 0 | 39050.4872 | 2539 | 0 |  | 1394.5 | 1630.5 | 130.525 | 0 | 155.0061 | 0 | 1.3053 | 0 | 1.5501 | 0 | 1.3053 | 1.5501 | 21.7671 | 2.5356 | 20.4618
39050.4877 | 1995 | 0 | 39050.4877 | 2354 | 0 |  | 1436.5 | 1672.5 | 121.7949 | 0 | 143.7118 | 0 | 1.2179 | 0 | 1.4371 | 0 | 1.2179 | 1.4371 | 30.4952 | 10.5939 | 29.2773
39050.4882 | 1961 | 0 | 39050.4882 | 2120 | 0 |  | 1478.5 | 1714.5 | 119.7192 | 0 | 129.4261 | 0 | 1.1972 | 0 | 1.2943 | 0 | 1.1972 | 1.2943 | 32.7578 | 22.8009 | 31.5606
39050.4886 | 2489 | 0 | 39050.4887 | 2023 | 0 |  | 1520.5 | 1756.5 | 151.9536 | 0 | 123.5043 | 0 | 1.5195 | 0 | 1.235 | 0 | 1.5195 | 1.235 | 4.5954 | 28.6891 | 3.0759
39050.4891 | 1969 | 0 | 39050.4891 | 1918 | 0 |  | 1562.5 | 1798.5 | 120.2076 | 0 | 117.094 | 0 | 1.2021 | 0 | 1.1709 | 0 | 1.2021 | 1.1709 | 32.2184 | 35.7341 | 31.0163
39050.4896 | 2500 | 0 | 39050.4896 | 2387 | 0 |  | 1604.5 | 1840.5 | 152.6252 | 0 | 145.7265 | 0 | 1.5263 | 0 | 1.4573 | 0 | 1.5263 | 1.4573 | 4.1352 | 9.0649 | 2.6089
39050.4901 | 1969 | 0 | 39050.4901 | 2559 | 0 |  | 1646.5 | 1882.5 | 120.2076 | 0 | 156.2271 | 0 | 1.2021 | 0 | 1.5623 | 0 | 1.2021 | 1.5623 | 32.2184 | 1.7343 | 31.0163
39050.4906 | 2484 | 0 | 39050.4906 | 2093 | 0 |  | 1688.5 | 1924.5 | 151.6484 | 0 | 127.7778 | 0 | 1.5165 | 0 | 1.2778 | 0 | 1.5165 | 1.2778 | 4.806 | 24.3851 | 3.2895
39050.4911 | 2520 | 0 | 39050.4911 | 2490 | 0 |  | 1730.5 | 1966.5 | 153.8462 | 0 | 152.0147 | 0 | 1.5385 | 0 | 1.5201 | 0 | 1.5385 | 1.5201 | 3.3087 | 4.5534 | 1.7703
39050.4916 | 2289 | 0 | 39050.4916 | 1978 | 0 |  | 1772.5 | 2008.5 | 139.7436 | 0 | 120.757 | 0 | 1.3974 | 0 | 1.2076 | 0 | 1.3974 | 1.2076 | 13.7344 | 31.6168 | 12.3369
39050.492 | 1935 | 0 | 39050.4921 | 2587 | 0 |  | 1814.5 | 2050.5 | 118.1319 | 0 | 157.9365 | 0 | 1.1813 | 0 | 1.5794 | 0 | 1.1813 | 1.5794 | 34.5416 | 0.63317 | 33.3603
39050.4925 | 2283 | 0 | 39050.4925 | 2276 | 0 |  | 1856.5 | 2092.5 | 139.3773 | 0 | 138.9499 | 0 | 1.3938 | 0 | 1.3895 | 0 | 1.3938 | 1.3895 | 14.0333 | 14.384 | 12.6395
39050.493 | 1974 | 0 | 39050.493 | 2299 | 0 |  | 1898.5 | 2134.5 | 120.5128 | 0 | 140.3541 | 0 | 1.2051 | 0 | 1.4035 | 0 | 1.2051 | 1.4035 | 31.8835 | 13.2397 | 30.6784
39050.4935 | 1844 | 0 | 39050.4935 | 2112 | 0 |  | 1940.5 | 2176.5 | 112.5763 | 0 | 128.9377 | 0 | 1.1258 | 0 | 1.2894 | 0 | 1.1258 | 1.2894 | 41.1811 | 23.2661 | 40.0554

## B3-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 158.0818 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39050.4687 | 0 | 0 | 39050.4687 | 0 | 0 |  | -204 | 32 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4692 | 0 | 0 | 39050.4692 | 0 | 0 |  | -162 | 74 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4697 | 0 | 0 | 39050.4697 | 0 | 0 |  | -120 | 116 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4701 | 0 | 0 | 39050.4702 | 0 | 0 |  | -78 | 158 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4706 | 0 | 0 | 39050.4706 | 0 | 0 |  | -36 | 200 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4711 | 0 | 0 | 39050.4711 | 0 | 0 |  | 6 | 242 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4716 | 0 | 0 | 39050.4716 | 0 | 0 |  | 48 | 284 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4721 | 0 | 0 | 39050.4721 | 0 | 0 |  | 90 | 326 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4726 | 0 | 0 | 39050.4726 | 0 | 0 |  | 132 | 368 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4731 | 0 | 0 | 39050.4731 | 0 | 0 |  | 174 | 410 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4735 | 0 | 0 | 39050.4736 | 0 | 0 |  | 216 | 452 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.474 | 0 | 0 | 39050.4741 | 0 | 0 |  | 258 | 494 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4745 | 0 | 0 | 39050.4745 | 0 | 0 |  | 300 | 536 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.475 | 0 | 0 | 39050.475 | 0 | 0 |  | 342 | 578 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4755 | 0 | 0 | 39050.4755 | 0 | 0 |  | 384 | 620 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.476 | 0 | 0 | 39050.476 | 0 | 0 |  | 426 | 662 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4765 | 0 | 0 | 39050.4765 | 0 | 0 |  | 468 | 704 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4769 | 0 | 0 | 39050.477 | 0 | 0 |  | 510 | 746 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4774 | 0 | 0 | 39050.4775 | 0 | 0 |  | 552 | 788 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4779 | 0 | 0 | 39050.4779 | 0 | 0 |  | 594 | 830 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4784 | 0 | 0 | 39050.4784 | 0 | 0 |  | 636 | 872 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39050.4789 | 3 | 0 | 39050.4789 | 1 | 0 |  | 678 | 914 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 86212.6667 | 258838 | 86212.6648
39050.4794 | 2 | 0 | 39050.4794 | 2247 | 0 |  | 719.5 | 955.5 | 0.1221 | 0 | 137.1795 | 0 | 0.001221 | 0 | 1.3718 | 0 | 0.001221 | 1.3718 | 129369 | 15.2372 | 129368.9988
39050.4799 | 2 | 0 | 39050.4799 | 2110 | 0 |  | 762 | 998 | 0.1221 | 0 | 128.8156 | 0 | 0.001221 | 0 | 1.2882 | 0 | 0.001221 | 1.2882 | 129369 | 22.7194 | 129368.9988
39050.4803 | 2 | 0 | 39050.4804 | 2083 | 0 |  | 803.5 | 1039.5 | 0.1221 | 0 | 127.1673 | 0 | 0.001221 | 0 | 1.2717 | 0 | 0.001221 | 1.2717 | 129369 | 24.3101 | 129368.9988
39050.4808 | 2 | 0 | 39050.4809 | 2564 | 0 |  | 846 | 1082 | 0.1221 | 0 | 156.5324 | 0 | 0.001221 | 0 | 1.5653 | 0 | 0.001221 | 1.5653 | 129369 | 0.98986 | 129368.9988
39050.4813 | 2 | 0 | 39050.4813 | 2556 | 0 |  | 888 | 1124 | 0.1221 | 0 | 156.044 | 0 | 0.001221 | 0 | 1.5604 | 0 | 0.001221 | 1.5604 | 129369 | 1.3059 | 129368.9988
39050.4818 | 1 | 0 | 39050.4818 | 2065 | 0 |  | 930 | 1166 | 0.06105 | 0 | 126.0684 | 0 | 0.0006105 | 0 | 1.2607 | 0 | 0.0006105 | 1.2607 | 258838 | 25.3937 | 258837.9994
39050.4823 | 2 | 0 | 39050.4823 | 2502 | 0 |  | 971.5 | 1207.5 | 0.1221 | 0 | 152.7473 | 0 | 0.001221 | 0 | 1.5275 | 0 | 0.001221 | 1.5275 | 129369 | 3.4924 | 129368.9988
39050.4828 | 2 | 0 | 39050.4828 | 2091 | 0 |  | 1013.5 | 1249.5 | 0.1221 | 0 | 127.6557 | 0 | 0.001221 | 0 | 1.2766 | 0 | 0.001221 | 1.2766 | 129369 | 23.8345 | 129368.9988
39050.4833 | 1899 | 0 | 39050.4833 | 1939 | 0 |  | 1056 | 1292 | 115.9341 | 0 | 118.3761 | 0 | 1.1593 | 0 | 1.1838 | 0 | 1.1593 | 1.1838 | 36.3549 | 33.542 | 35.1956
39050.4837 | 1690 | 0 | 39050.4838 | 2009 | 0 |  | 1097.5 | 1333.5 | 103.1746 | 0 | 122.6496 | 0 | 1.0317 | 0 | 1.2265 | 0 | 1.0317 | 1.2265 | 53.2178 | 28.889 | 52.186
39050.4842 | 1467 | 0 | 39050.4843 | 2372 | 0 |  | 1140 | 1376 | 89.5604 | 0 | 144.8107 | 0 | 0.8956 | 0 | 1.4481 | 0 | 0.8956 | 1.4481 | 76.5085 | 9.1644 | 75.6129
39050.4847 | 2011 | 0 | 39050.4847 | 2205 | 0 |  | 1181.5 | 1417.5 | 122.7717 | 0 | 134.6154 | 0 | 1.2277 | 0 | 1.3462 | 0 | 1.2277 | 1.3462 | 28.7608 | 17.4322 | 27.5331
39050.4852 | 1921 | 0 | 39050.4852 | 2257 | 0 |  | 1223.5 | 1459.5 | 117.2772 | 0 | 137.79 | 0 | 1.1728 | 0 | 1.3779 | 0 | 1.1728 | 1.3779 | 34.7933 | 14.7266 | 33.6206
39050.4857 | 2276 | 0 | 39050.4857 | 2074 | 0 |  | 1265.5 | 1501.5 | 138.9499 | 0 | 126.6178 | 0 | 1.3895 | 0 | 1.2662 | 0 | 1.3895 | 1.2662 | 13.7689 | 24.8496 | 12.3794
39050.4862 | 2175 | 0 | 39050.4862 | 2145 | 0 |  | 1307.5 | 1543.5 | 132.7839 | 0 | 130.9524 | 0 | 1.3278 | 0 | 1.3095 | 0 | 1.3278 | 1.3095 | 19.052 | 20.717 | 17.7241
39050.4867 | 2415 | 0 | 39050.4867 | 2196 | 0 |  | 1349.5 | 1585.5 | 147.4359 | 0 | 134.0659 | 0 | 1.4744 | 0 | 1.3407 | 0 | 1.4744 | 1.3407 | 7.2207 | 17.9135 | 5.7463
39050.4872 | 1926 | 0 | 39050.4872 | 2308 | 0 |  | 1391.5 | 1627.5 | 117.5824 | 0 | 140.9035 | 0 | 1.1758 | 0 | 1.409 | 0 | 1.1758 | 1.409 | 34.4434 | 12.1915 | 33.2676
39050.4876 | 2003 | 0 | 39050.4877 | 2544 | 0 |  | 1433.5 | 1669.5 | 122.2833 | 0 | 155.3114 | 0 | 1.2228 | 0 | 1.5531 | 0 | 1.2228 | 1.5531 | 29.2751 | 1.7838 | 28.0523
39050.4881 | 2180 | 0 | 39050.4881 | 2276 | 0 |  | 1475.5 | 1711.5 | 133.0891 | 0 | 138.9499 | 0 | 1.3309 | 0 | 1.3895 | 0 | 1.3309 | 1.3895 | 18.7789 | 13.7689 | 17.448
39050.4886 | 2256 | 0 | 39050.4886 | 2528 | 0 |  | 1517.5 | 1753.5 | 137.7289 | 0 | 154.3346 | 0 | 1.3773 | 0 | 1.5433 | 0 | 1.3773 | 1.5433 | 14.7775 | 2.428 | 13.4002
39050.4891 | 2229 | 0 | 39050.4891 | 1898 | 0 |  | 1559.5 | 1795.5 | 136.0806 | 0 | 115.873 | 0 | 1.3608 | 0 | 1.1587 | 0 | 1.3608 | 1.1587 | 16.1678 | 36.4268 | 14.807
39050.4896 | 1884 | 0 | 39050.4896 | 2185 | 0 |  | 1601.5 | 1837.5 | 115.0183 | 0 | 133.3944 | 0 | 1.1502 | 0 | 1.3339 | 0 | 1.1502 | 1.3339 | 37.4406 | 18.5071 | 36.2904
39050.4901 | 1805 | 0 | 39050.4901 | 2052 | 0 |  | 1643.5 | 1879.5 | 110.1954 | 0 | 125.2747 | 0 | 1.102 | 0 | 1.2527 | 0 | 1.102 | 1.2527 | 43.456 | 26.1881 | 42.354
39050.4906 | 2414 | 0 | 39050.4906 | 2097 | 0 |  | 1685.5 | 1921.5 | 147.3748 | 0 | 128.022 | 0 | 1.4737 | 0 | 1.2802 | 0 | 1.4737 | 1.2802 | 7.2651 | 23.4802 | 5.7914
39050.491 | 2179 | 0 | 39050.4911 | 2097 | 0 |  | 1727.5 | 1963.5 | 133.0281 | 0 | 128.022 | 0 | 1.3303 | 0 | 1.2802 | 0 | 1.3303 | 1.2802 | 18.8334 | 23.4802 | 17.5031
39050.4915 | 2176 | 0 | 39050.4915 | 2408 | 0 |  | 1769.5 | 2005.5 | 132.8449 | 0 | 147.0085 | 0 | 1.3284 | 0 | 1.4701 | 0 | 1.3284 | 1.4701 | 18.9972 | 7.5324 | 17.6688
39050.492 | 2049 | 0 | 39050.492 | 2446 | 0 |  | 1811.5 | 2047.5 | 125.0916 | 0 | 149.3284 | 0 | 1.2509 | 0 | 1.4933 | 0 | 1.2509 | 1.4933 | 26.3729 | 5.8618 | 25.1219
39050.4925 | 2465 | 0 | 39050.4925 | 2278 | 0 |  | 1853.5 | 2089.5 | 150.4884 | 0 | 139.072 | 0 | 1.5049 | 0 | 1.3907 | 0 | 1.5049 | 1.3907 | 5.0458 | 13.669 | 3.541
39050.493 | 2464 | 0 | 39050.493 | 2573 | 0 |  | 1895.5 | 2131.5 | 150.4274 | 0 | 157.0818 | 0 | 1.5043 | 0 | 1.5708 | 0 | 1.5043 | 1.5708 | 5.0885 | 0.63661 | 3.5842
39050.4935 | 2103 | 0 | 39050.4935 | 2522 | 0 |  | 1937.5 | 2173.5 | 128.3883 | 0 | 153.9683 | 0 | 1.2839 | 0 | 1.5397 | 0 | 1.2839 | 1.5397 | 23.1279 | 2.6717 | 21.844

## B3-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | #REF! |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39050.4687 | 0 | 0 | 39050.4687 | 0 | 0 |  | -206.5 | 29.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4691 | 0 | 0 | 39050.4692 | 0 | 0 |  | -165 | 71 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4696 | 0 | 0 | 39050.4696 | 0 | 0 |  | -123 | 113 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4701 | 0 | 0 | 39050.4701 | 0 | 0 |  | -81 | 155 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4706 | 0 | 0 | 39050.4706 | 0 | 0 |  | -39 | 197 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4711 | 0 | 0 | 39050.4711 | 0 | 0 |  | 3 | 239 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4716 | 0 | 0 | 39050.4716 | 0 | 0 |  | 45 | 281 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.472 | 0 | 0 | 39050.4721 | 0 | 0 |  | 87 | 323 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4725 | 0 | 0 | 39050.4726 | 0 | 0 |  | 129 | 365 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.473 | 0 | 0 | 39050.4735 | 0 | 0 |  | 192 | 428 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4735 | 0 | 0 | 39050.474 | 0 | 0 |  | 234 | 470 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.474 | 0 | 0 | 39050.4745 | 0 | 0 |  | 276 | 512 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4745 | 0 | 0 | 39050.475 | 0 | 0 |  | 318 | 554 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.475 | 0 | 0 | 39050.4755 | 0 | 0 |  | 360 | 596 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4755 | 0 | 0 | 39050.476 | 0 | 0 |  | 402 | 638 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4759 | 0 | 0 | 39050.4764 | 0 | 0 |  | 444 | 680 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4764 | 0 | 0 | 39050.4769 | 0 | 0 |  | 486 | 722 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4769 | 0 | 0 | 39050.4774 | 0 | 0 |  | 528 | 764 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4774 | 0 | 0 | 39050.4779 | 0 | 0 |  | 570 | 806 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4779 | 0 | 0 | 39050.4784 | 0 | 0 |  | 612 | 848 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #REF! | #REF! | #REF!
39050.4784 | 0 | 0 | 39050.4789 | 2506 | 0 |  | 654 | 890 | 0.030525 | 0 | 152.9915 | 0 | 0.00030525 | 0 | 1.5299 | 0 | 0.00030525 | 1.5299 | #REF! | #REF! | #REF!
39050.4789 | 0 | 0 | 39050.4794 | 2420 | 0 |  | 696 | 932 | 0.030525 | 0 | 147.7411 | 0 | 0.00030525 | 0 | 1.4774 | 0 | 0.00030525 | 1.4774 | #REF! | #REF! | #REF!
39050.4793 | 1 | 0 | 39050.4798 | 2213 | 0 |  | 738 | 974 | 0.06105 | 0 | 135.1038 | 0 | 0.0006105 | 0 | 1.351 | 0 | 0.0006105 | 1.351 | #REF! | #REF! | #REF!
39050.4798 | 1 | 0 | 39050.4803 | 1956 | 0 |  | 780 | 1016 | 0.06105 | 0 | 119.4139 | 0 | 0.0006105 | 0 | 1.1941 | 0 | 0.0006105 | 1.1941 | #REF! | #REF! | #REF!
39050.4803 | 1 | 0 | 39050.4808 | 2152 | 0 |  | 822 | 1058 | 0.06105 | 0 | 131.3797 | 0 | 0.0006105 | 0 | 1.3138 | 0 | 0.0006105 | 1.3138 | #REF! | #REF! | #REF!
39050.4808 | 1 | 0 | 39050.4813 | 2166 | 0 |  | 864 | 1100 | 0.06105 | 0 | 132.2344 | 0 | 0.0006105 | 0 | 1.3223 | 0 | 0.0006105 | 1.3223 | #REF! | #REF! | #REF!
39050.4813 | 1 | 0 | 39050.4818 | 2437 | 0 |  | 906 | 1142 | 0.06105 | 0 | 148.779 | 0 | 0.0006105 | 0 | 1.4878 | 0 | 0.0006105 | 1.4878 | #REF! | #REF! | #REF!
39050.4818 | 1 | 0 | 39050.4823 | 2573 | 0 |  | 948 | 1184 | 0.06105 | 0 | 157.0818 | 0 | 0.0006105 | 0 | 1.5708 | 0 | 0.0006105 | 1.5708 | #REF! | #REF! | #REF!
39050.4823 | 1 | 0 | 39050.4828 | 1952 | 0 |  | 990 | 1226 | 0.06105 | 0 | 119.1697 | 0 | 0.0006105 | 0 | 1.1917 | 0 | 0.0006105 | 1.1917 | #REF! | #REF! | #REF!
39050.4827 | 1 | 0 | 39050.4833 | 1981 | 0 |  | 1032 | 1268 | 0.06105 | 0 | 120.9402 | 0 | 0.0006105 | 0 | 1.2094 | 0 | 0.0006105 | 1.2094 | #REF! | #REF! | #REF!
39050.4832 | 1997 | 0 | 39050.4837 | 2555 | 0 |  | 1074 | 1310 | 121.917 | 0 | 155.9829 | 0 | 1.2192 | 0 | 1.5598 | 0 | 1.2192 | 1.5598 | #REF! | #REF! | #REF!
39050.4837 | 1451 | 0 | 39050.4842 | 2007 | 0 |  | 1116 | 1352 | 88.5836 | 0 | 122.5275 | 0 | 0.88584 | 0 | 1.2253 | 0 | 0.88584 | 1.2253 | #REF! | #REF! | #REF!
39050.4842 | 2037 | 0 | 39050.4847 | 2424 | 0 |  | 1158 | 1394 | 124.359 | 0 | 147.9853 | 0 | 1.2436 | 0 | 1.4799 | 0 | 1.2436 | 1.4799 | #REF! | #REF! | #REF!
39050.4847 | 1889 | 0 | 39050.4852 | 2589 | 0 |  | 1200 | 1436 | 115.3236 | 0 | 158.0586 | 0 | 1.1532 | 0 | 1.5806 | 0 | 1.1532 | 1.5806 | #REF! | #REF! | #REF!
39050.4852 | 2092 | 0 | 39050.4857 | 2015 | 0 |  | 1242 | 1478 | 127.7167 | 0 | 123.0159 | 0 | 1.2772 | 0 | 1.2302 | 0 | 1.2772 | 1.2302 | #REF! | #REF! | #REF!
39050.4857 | 2010 | 0 | 39050.4862 | 2394 | 0 |  | 1284 | 1520 | 122.7106 | 0 | 146.1538 | 0 | 1.2271 | 0 | 1.4615 | 0 | 1.2271 | 1.4615 | #REF! | #REF! | #REF!
39050.4861 | 2410 | 0 | 39050.4867 | 2548 | 0 |  | 1326 | 1562 | 147.1306 | 0 | 155.5556 | 0 | 1.4713 | 0 | 1.5556 | 0 | 1.4713 | 1.5556 | #REF! | #REF! | #REF!
39050.4866 | 1927 | 0 | 39050.4871 | 2571 | 0 |  | 1368 | 1604 | 117.6435 | 0 | 156.9597 | 0 | 1.1764 | 0 | 1.5696 | 0 | 1.1764 | 1.5696 | #REF! | #REF! | #REF!
39050.4871 | 2027 | 0 | 39050.4876 | 2327 | 0 |  | 1410 | 1646 | 123.7485 | 0 | 142.0635 | 0 | 1.2375 | 0 | 1.4206 | 0 | 1.2375 | 1.4206 | #REF! | #REF! | #REF!
39050.4876 | 2034 | 0 | 39050.4881 | 2463 | 0 |  | 1452 | 1688 | 124.1758 | 0 | 150.3663 | 0 | 1.2418 | 0 | 1.5037 | 0 | 1.2418 | 1.5037 | #REF! | #REF! | #REF!
39050.4881 | 1995 | 0 | 39050.4886 | 2275 | 0 |  | 1494 | 1730 | 121.7949 | 0 | 138.8889 | 0 | 1.2179 | 0 | 1.3889 | 0 | 1.2179 | 1.3889 | #REF! | #REF! | #REF!
39050.4886 | 1834 | 0 | 39050.4891 | 2115 | 0 |  | 1536 | 1772 | 111.9658 | 0 | 129.1209 | 0 | 1.1197 | 0 | 1.2912 | 0 | 1.1197 | 1.2912 | #REF! | #REF! | #REF!
39050.4891 | 1965 | 0 | 39050.4896 | 1974 | 0 |  | 1578 | 1814 | 119.9634 | 0 | 120.5128 | 0 | 1.1996 | 0 | 1.2051 | 0 | 1.1996 | 1.2051 | #REF! | #REF! | #REF!
39050.4895 | 2085 | 0 | 39050.4901 | 2355 | 0 |  | 1620 | 1856 | 127.2894 | 0 | 143.7729 | 0 | 1.2729 | 0 | 1.4377 | 0 | 1.2729 | 1.4377 | #REF! | #REF! | #REF!
39050.49 | 2243 | 0 | 39050.4905 | 2348 | 0 |  | 1662 | 1898 | 136.9353 | 0 | 143.3455 | 0 | 1.3694 | 0 | 1.4335 | 0 | 1.3694 | 1.4335 | #REF! | #REF! | #REF!
39050.4905 | 1811 | 0 | 39050.491 | 2236 | 0 |  | 1704 | 1940 | 110.5617 | 0 | 136.5079 | 0 | 1.1056 | 0 | 1.3651 | 0 | 1.1056 | 1.3651 | #REF! | #REF! | #REF!
39050.491 | 2100 | 0 | 39050.4915 | 2578 | 0 |  | 1746 | 1982 | 128.2051 | 0 | 157.3871 | 0 | 1.2821 | 0 | 1.5739 | 0 | 1.2821 | 1.5739 | #REF! | #REF! | #REF!
39050.4915 | 2480 | 0 | 39050.492 | 2022 | 0 |  | 1788 | 2024 | 151.4042 | 0 | 123.4432 | 0 | 1.514 | 0 | 1.2344 | 0 | 1.514 | 1.2344 | #REF! | #REF! | #REF!
39050.492 | 2231 | 0 | 39050.4925 | 2122 | 0 |  | 1830 | 2066 | 136.2027 | 0 | 129.5482 | 0 | 1.362 | 0 | 1.2955 | 0 | 1.362 | 1.2955 | #REF! | #REF! | #REF!
39050.4925 | 2508 | 0 | 39050.493 | 2505 | 0 |  | 1872 | 2108 | 153.1136 | 0 | 152.9304 | 0 | 1.5311 | 0 | 1.5293 | 0 | 1.5311 | 1.5293 | #REF! | #REF! | #REF!
39050.493 | 2378 | 0 | 39050.4935 | 2176 | 0 |  | 1914 | 2150 | 145.177 | 0 | 132.8449 | 0 | 1.4518 | 0 | 1.3284 | 0 | 1.4518 | 1.3284 | #REF! | #REF! | #REF!
39050.4934 | 2041 | 0 | [6 empty] | 124.6032 | 0 | 0.030525 | #REF! | 1.246 | 0 | 0.00030525 | #REF! | 1.246 | #REF! | #REF! | #REF! | #REF!

## B3-B4
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 155.2735 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39050.4686 | 0 | 0 | 39050.4686 | 0 | 0 |  | -209.5 | 26.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4691 | 0 | 0 | 39050.4691 | 0 | 0 |  | -167.5 | 68.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4696 | 0 | 0 | 39050.4696 | 0 | 0 |  | -125.5 | 110.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4701 | 0 | 0 | 39050.4701 | 0 | 0 |  | -83.5 | 152.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4706 | 0 | 0 | 39050.4706 | 0 | 0 |  | -41.5 | 194.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4711 | 0 | 0 | 39050.4711 | 0 | 0 |  | 0.5 | 236.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4715 | 0 | 0 | 39050.4716 | 0 | 0 |  | 42.5 | 278.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.472 | 0 | 0 | 39050.472 | 0 | 0 |  | 84.5 | 320.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4725 | 0 | 0 | 39050.4725 | 0 | 0 |  | 126.5 | 362.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.473 | 0 | 0 | 39050.473 | 0 | 0 |  | 168.5 | 404.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4735 | 0 | 0 | 39050.4735 | 0 | 0 |  | 210.5 | 446.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.474 | 0 | 0 | 39050.474 | 0 | 0 |  | 252.5 | 488.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4745 | 0 | 0 | 39050.4745 | 0 | 0 |  | 294.5 | 530.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4749 | 0 | 0 | 39050.475 | 0 | 0 |  | 336.5 | 572.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4754 | 0 | 0 | 39050.4754 | 0 | 0 |  | 378.5 | 614.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4759 | 0 | 0 | 39050.4759 | 0 | 0 |  | 420.5 | 656.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4764 | 0 | 0 | 39050.4764 | 0 | 0 |  | 462.5 | 698.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4769 | 0 | 0 | 39050.4769 | 0 | 0 |  | 504.5 | 740.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4774 | 0 | 0 | 39050.4774 | 0 | 0 |  | 546.5 | 782.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4779 | 0 | 0 | 39050.4779 | 0 | 0 |  | 588.5 | 824.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4783 | 0 | 0 | 39050.4784 | 0 | 0 |  | 630.5 | 866.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508576 | 508576 | 508575.9997
39050.4788 | 1 | 0 | 39050.4788 | 0 | 0 |  | 672 | 908 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 254238 | 508576 | 254237.9994
39050.4793 | 3 | 0 | 39050.4793 | 2 | 0 |  | 714 | 950 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 84679.3333 | 127069 | 84679.3315
39050.4798 | 3 | 0 | 39050.4798 | 1 | 0 |  | 756 | 992 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 84679.3333 | 254238 | 84679.3315
39050.4803 | 3 | 0 | 39050.4803 | 1 | 0 |  | 798 | 1034 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 84679.3333 | 254238 | 84679.3315
39050.4808 | 2 | 0 | 39050.4808 | 1 | 0 |  | 840.5 | 1076.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127069 | 254238 | 127068.9988
39050.4812 | 2 | 0 | 39050.4813 | 2 | 0 |  | 882 | 1118 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 127069 | 127069 | 127068.9988
39050.4817 | 2 | 0 | 39050.4818 | 1 | 0 |  | 924 | 1160 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127069 | 254238 | 127068.9988
39050.4822 | 2 | 0 | 39050.4822 | 1 | 0 |  | 966 | 1202 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127069 | 254238 | 127068.9988
39050.4827 | 2 | 0 | 39050.4827 | 1 | 0 |  | 1008 | 1244 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127069 | 254238 | 127068.9988
39050.4832 | 2070 | 22 | 39050.4832 | 2453 | 4 |  | 1050 | 1286 | 126.3736 | 1.3431 | 149.7558 | 0.2442 | 1.2637 | 0.013431 | 1.4976 | 0.002442 | 1.2503 | 1.4951 | 32.5377 | 3.7091 | 73.379
39050.4837 | 1877 | 10 | 39050.4837 | 2336 | 4 |  | 1092 | 1328 | 114.591 | 0.6105 | 142.6129 | 0.2442 | 1.1459 | 0.006105 | 1.4261 | 0.002442 | 1.1398 | 1.4237 | 37.9691 | 8.9332 | 538.2698
39050.4842 | 1721 | 440 | 39050.4842 | 1592 | 589 |  | 1134.5 | 1370.5 | 105.0672 | 26.862 | 97.1917 | 35.9585 | 1.0507 | 0.26862 | 0.97192 | 0.35958 | 0.78205 | 0.61233 | 67.3061 | 743.8864 | 76.6064
39050.4847 | 2349 | 14 | 39050.4847 | 1954 | 7 |  | 1176 | 1412 | 143.4066 | 0.8547 | 119.2918 | 0.42735 | 1.4341 | 0.008547 | 1.1929 | 0.0042735 | 1.4255 | 1.1886 | 8.4856 | 31.6105 | 309.4576
39050.4851 | 2039 | 2 | 39050.4852 | 2499 | 1 |  | 1218 | 1454 | 124.4811 | 0.1221 | 152.5641 | 0.06105 | 1.2448 | 0.001221 | 1.5256 | 0.0006105 | 1.2436 | 1.525 | 26.207 | 1.7793 | 439.1385
39050.4856 | 2143 | 1 | 39050.4856 | 2088 | 1 |  | 1260 | 1496 | 130.8303 | 0.06105 | 127.4725 | 0.06105 | 1.3083 | 0.0006105 | 1.2747 | 0.0006105 | 1.3077 | 1.2741 | 18.7319 | 21.8758 | 7168.5727
39050.4861 | 1984 | 0 | 39050.4861 | 2450 | 0 |  | 1302 | 1538 | 121.1233 | 0 | 149.5726 | 0 | 1.2112 | 0 | 1.4957 | 0 | 1.2112 | 1.4957 | 28.1946 | 3.8114 | 26.9833
39050.4866 | 2055 | 0 | 39050.4866 | 2392 | 0 |  | 1344 | 1580 | 125.4579 | 0 | 146.0317 | 0 | 1.2546 | 0 | 1.4603 | 0 | 1.2546 | 1.4603 | 23.7655 | 6.3286 | 22.5109
39050.4871 | 2013 | 0 | 39050.4871 | 2253 | 0 |  | 1386 | 1622 | 122.8938 | 0 | 137.5458 | 0 | 1.2289 | 0 | 1.3755 | 0 | 1.2289 | 1.3755 | 26.3477 | 12.8886 | 25.1188
39050.4876 | 2386 | 0 | 39050.4876 | 2462 | 0 |  | 1428 | 1664 | 145.6654 | 0 | 150.3053 | 0 | 1.4567 | 0 | 1.5031 | 0 | 1.4567 | 1.5031 | 6.596 | 3.3054 | 5.1393
39050.4881 | 2203 | 0 | 39050.4881 | 2527 | 1 |  | 1470 | 1706 | 134.4933 | 0 | 154.2735 | 0.06105 | 1.3449 | 0 | 1.5427 | 0.0006105 | 1.3449 | 1.5421 | 15.4507 | 0.68804 | 14.1058
39050.4885 | 2484 | 0 | 39050.4886 | 2039 | 0 |  | 1512 | 1748 | 151.6484 | 0 | 124.4811 | 0 | 1.5165 | 0 | 1.2448 | 0 | 1.5165 | 1.2448 | 2.3905 | 24.7366 | 0.87402
39050.489 | 1860 | 0 | 39050.4891 | 2439 | 1 |  | 1554 | 1790 | 113.5531 | 0 | 148.9011 | 0.06105 | 1.1355 | 0 | 1.489 | 0.0006105 | 1.1355 | 1.4884 | 36.7409 | 4.3224 | 35.6053
39050.4895 | 1925 | 1 | 39050.4895 | 2112 | 0 |  | 1596 | 1832 | 117.5214 | 0.06105 | 128.9377 | 0 | 1.1752 | 0.0006105 | 1.2894 | 0 | 1.1746 | 1.2894 | 32.2223 | 20.4252 | 10471.3171
39050.49 | 2466 | 1 | 39050.49 | 2486 | 0 |  | 1638 | 1874 | 150.5495 | 0.06105 | 151.7705 | 0 | 1.5055 | 0.0006105 | 1.5177 | 0 | 1.5049 | 1.5177 | 3.1953 | 2.3081 | 172.3173
39050.4905 | 2359 | 5 | 39050.4905 | 1954 | 3 |  | 1680 | 1916 | 144.0171 | 0.30525 | 119.2918 | 0.18315 | 1.4402 | 0.0030525 | 1.1929 | 0.0018315 | 1.4371 | 1.1911 | 7.887 | 30.8098 | 844.992
39050.491 | 2457 | 0 | 39050.491 | 2400 | 0 |  | 1722 | 1958 | 150 | 0 | 146.5201 | 0 | 1.5 | 0 | 1.4652 | 0 | 1.5 | 1.4652 | 3.5157 | 5.9742 | 2.0157
39050.4915 | 1974 | 0 | 39050.4915 | 2453 | 0 |  | 1764 | 2000 | 120.5128 | 0 | 149.7558 | 0 | 1.2051 | 0 | 1.4976 | 0 | 1.2051 | 1.4976 | 28.844 | 3.6845 | 27.6388
39050.4919 | 2207 | 0 | 39050.492 | 2460 | 0 |  | 1806 | 2042 | 134.7375 | 0 | 150.1832 | 0 | 1.3474 | 0 | 1.5018 | 0 | 1.3474 | 1.5018 | 15.2415 | 3.3894 | 13.8941
39050.4924 | 2247 | 0 | 39050.4925 | 1933 | 1 |  | 1848 | 2084 | 137.1795 | 0 | 118.0098 | 0.06105 | 1.3718 | 0 | 1.1801 | 0.0006105 | 1.3718 | 1.1795 | 13.19 | 31.6449 | 11.8182
39050.4929 | 2496 | 1 | 39050.4929 | 1944 | 4 |  | 1890 | 2126 | 152.381 | 0.06105 | 118.6813 | 0.2442 | 1.5238 | 0.0006105 | 1.1868 | 0.002442 | 1.5232 | 1.1844 | 1.9012 | 34.6541 | 1193.62
39050.4934 | 1959 | 1 | 39050.4934 | 2039 | 1 |  | 1932 | 2168 | 119.5971 | 0.06105 | 124.4811 | 0.06105 | 1.196 | 0.0006105 | 1.2448 | 0.0006105 | 1.1954 | 1.2442 | 29.9074 | 24.7894 | 11588.8536

## A2-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 158.2039 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39050.4686 | 0 | 0 | 39050.4686 | 0 | 0 |  | -212.5 | 23.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4691 | 0 | 0 | 39050.4691 | 0 | 0 |  | -170.5 | 65.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4696 | 0 | 0 | 39050.4696 | 0 | 0 |  | -128.5 | 107.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.47 | 0 | 0 | 39050.4701 | 0 | 0 |  | -86.5 | 149.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4705 | 0 | 0 | 39050.4705 | 0 | 0 |  | -44.5 | 191.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.471 | 0 | 0 | 39050.471 | 0 | 0 |  | -2.5 | 233.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4715 | 0 | 0 | 39050.4715 | 0 | 0 |  | 39.5 | 275.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.472 | 0 | 0 | 39050.472 | 0 | 0 |  | 81.5 | 317.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4725 | 0 | 0 | 39050.4725 | 0 | 0 |  | 123.5 | 359.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.473 | 0 | 0 | 39050.473 | 0 | 0 |  | 165.5 | 401.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4734 | 0 | 0 | 39050.4735 | 0 | 0 |  | 207.5 | 443.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4739 | 0 | 0 | 39050.4739 | 0 | 0 |  | 249.5 | 485.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4744 | 0 | 0 | 39050.4744 | 0 | 0 |  | 291.5 | 527.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4749 | 0 | 0 | 39050.4749 | 0 | 0 |  | 333.5 | 569.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4754 | 0 | 0 | 39050.4754 | 0 | 0 |  | 375.5 | 611.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4759 | 0 | 0 | 39050.4759 | 0 | 0 |  | 417.5 | 653.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4764 | 0 | 0 | 39050.4764 | 0 | 0 |  | 459.5 | 695.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4769 | 0 | 0 | 39050.4769 | 0 | 0 |  | 501.5 | 737.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4773 | 0 | 0 | 39050.4773 | 0 | 0 |  | 543.5 | 779.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4778 | 0 | 0 | 39050.4778 | 0 | 0 |  | 585.5 | 821.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518176 | 518176 | 518175.9997
39050.4783 | 1 | 2 | 39050.4783 | 0 | 0 |  | 627.5 | 863.5 | 0.06105 | 0.1221 | 0.030525 | 0 | 0.0006105 | 0.001221 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 259138.0193 | 518176 | 129394.0289
39050.4788 | 3 | 0 | 39050.4788 | 1 | 0 |  | 669.5 | 905.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 86279.3333 | 259038 | 86279.3315
39050.4793 | 2 | 0 | 39050.4793 | 2292 | 0 |  | 711.5 | 947.5 | 0.1221 | 0 | 139.9267 | 0 | 0.001221 | 0 | 1.3993 | 0 | 0.001221 | 1.3993 | 129469 | 13.062 | 129468.9988
39050.4798 | 2 | 0 | 39050.4798 | 2133 | 0 |  | 753.5 | 989.5 | 0.1221 | 0 | 130.2198 | 0 | 0.001221 | 0 | 1.3022 | 0 | 0.001221 | 1.3022 | 129469 | 21.4899 | 129468.9988
39050.4803 | 2 | 0 | 39050.4803 | 2374 | 0 |  | 795.5 | 1031.5 | 0.1221 | 0 | 144.9328 | 0 | 0.001221 | 0 | 1.4493 | 0 | 0.001221 | 1.4493 | 129469 | 9.1567 | 129468.9988
39050.4807 | 2 | 0 | 39050.4808 | 2311 | 0 |  | 837.5 | 1073.5 | 0.1221 | 0 | 141.0867 | 0 | 0.001221 | 0 | 1.4109 | 0 | 0.001221 | 1.4109 | 129469 | 12.1324 | 129468.9988
39050.4812 | 2 | 0 | 39050.4812 | 2575 | 0 |  | 879.5 | 1115.5 | 0.1221 | 0 | 157.2039 | 0 | 0.001221 | 0 | 1.572 | 0 | 0.001221 | 1.572 | 129469 | 0.63612 | 129468.9988
39050.4817 | 2 | 0 | 39050.4817 | 2311 | 0 |  | 921.5 | 1157.5 | 0.1221 | 0 | 141.0867 | 0 | 0.001221 | 0 | 1.4109 | 0 | 0.001221 | 1.4109 | 129469 | 12.1324 | 129468.9988
39050.4822 | 2 | 0 | 39050.4822 | 1969 | 0 |  | 963.5 | 1199.5 | 0.1221 | 0 | 120.2076 | 0 | 0.001221 | 0 | 1.2021 | 0 | 0.001221 | 1.2021 | 129469 | 31.6089 | 129468.9988
39050.4827 | 2 | 0 | 39050.4827 | 2097 | 0 |  | 1005.5 | 1241.5 | 0.1221 | 0 | 128.022 | 0 | 0.001221 | 0 | 1.2802 | 0 | 0.001221 | 1.2802 | 129469 | 23.5756 | 129468.9988
39050.4832 | 2 | 0 | 39050.4832 | 1997 | 0 |  | 1047.5 | 1283.5 | 0.1221 | 0 | 121.917 | 0 | 0.001221 | 0 | 1.2192 | 0 | 0.001221 | 1.2192 | 129469 | 29.7636 | 129468.9988
39050.4837 | 2 | 0 | 39050.4837 | 2022 | 0 |  | 1089.5 | 1325.5 | 0.1221 | 0 | 123.4432 | 0 | 0.001221 | 0 | 1.2344 | 0 | 0.001221 | 1.2344 | 129469 | 28.1592 | 129468.9988
39050.4841 | 2 | 0 | 39050.4842 | 2174 | 0 |  | 1131.5 | 1367.5 | 0.1221 | 0 | 132.7228 | 0 | 0.001221 | 0 | 1.3272 | 0 | 0.001221 | 1.3272 | 129469 | 19.1987 | 129468.9988
39050.4846 | 2 | 0 | 39050.4846 | 2280 | 0 |  | 1173.5 | 1409.5 | 0.1221 | 0 | 139.1941 | 0 | 0.001221 | 0 | 1.3919 | 0 | 0.001221 | 1.3919 | 129469 | 13.657 | 129468.9988
39050.4851 | 2 | 0 | 39050.4851 | 1998 | 0 |  | 1215.5 | 1451.5 | 0.1221 | 0 | 121.978 | 0 | 0.001221 | 0 | 1.2198 | 0 | 0.001221 | 1.2198 | 129469 | 29.6987 | 129468.9988
39050.4856 | 1 | 0 | 39050.4856 | 2411 | 0 |  | 1257.5 | 1493.5 | 0.06105 | 0 | 147.1917 | 0 | 0.0006105 | 0 | 1.4719 | 0 | 0.0006105 | 1.4719 | 259038 | 7.4815 | 259037.9994
39050.4861 | 2 | 0 | 39050.4861 | 2203 | 0 |  | 1299.5 | 1535.5 | 0.1221 | 0 | 134.4933 | 0 | 0.001221 | 0 | 1.3449 | 0 | 0.001221 | 1.3449 | 129469 | 17.6296 | 129468.9988
39050.4866 | 2 | 0 | 39050.4866 | 2262 | 0 |  | 1341.5 | 1577.5 | 0.1221 | 0 | 138.0952 | 0 | 0.001221 | 0 | 1.381 | 0 | 0.001221 | 1.381 | 129469 | 14.5615 | 129468.9988
39050.4871 | 2 | 0 | 39050.4871 | 2279 | 0 |  | 1383.5 | 1619.5 | 0.1221 | 0 | 139.1331 | 0 | 0.001221 | 0 | 1.3913 | 0 | 0.001221 | 1.3913 | 129469 | 13.7069 | 129468.9988
39050.4875 | 2 | 0 | 39050.4876 | 2178 | 0 |  | 1425.5 | 1661.5 | 0.1221 | 0 | 132.967 | 0 | 0.001221 | 0 | 1.3297 | 0 | 0.001221 | 1.3297 | 129469 | 18.9798 | 129468.9988
39050.488 | 2 | 0 | 39050.488 | 2212 | 0 |  | 1467.5 | 1703.5 | 0.1221 | 0 | 135.0427 | 0 | 0.001221 | 0 | 1.3504 | 0 | 0.001221 | 1.3504 | 129469 | 17.151 | 129468.9988
39050.4885 | 2 | 0 | 39050.4885 | 2330 | 0 |  | 1509.5 | 1745.5 | 0.1221 | 0 | 142.2466 | 0 | 0.001221 | 0 | 1.4225 | 0 | 0.001221 | 1.4225 | 129469 | 11.218 | 129468.9988
39050.489 | 2 | 0 | 39050.489 | 2494 | 0 |  | 1551.5 | 1787.5 | 0.1221 | 0 | 152.2589 | 0 | 0.001221 | 0 | 1.5226 | 0 | 0.001221 | 1.5226 | 129469 | 3.9046 | 129468.9988
39050.4895 | 2 | 0 | 39050.4895 | 2291 | 0 |  | 1593.5 | 1829.5 | 0.1221 | 0 | 139.8657 | 0 | 0.001221 | 0 | 1.3987 | 0 | 0.001221 | 1.3987 | 129469 | 13.1113 | 129468.9988
39050.49 | 2 | 0 | 39050.49 | 2461 | 0 |  | 1635.5 | 1871.5 | 0.1221 | 0 | 150.2442 | 0 | 0.001221 | 0 | 1.5024 | 0 | 0.001221 | 1.5024 | 129469 | 5.2978 | 129468.9988
39050.4905 | 1 | 0 | 39050.4905 | 2144 | 0 |  | 1677.5 | 1913.5 | 0.06105 | 0 | 130.8913 | 0 | 0.0006105 | 0 | 1.3089 | 0 | 0.0006105 | 1.3089 | 259038 | 20.8666 | 259037.9994
39050.4909 | 1 | 0 | 39050.491 | 2313 | 0 |  | 1719.5 | 1955.5 | 0.06105 | 0 | 141.2088 | 0 | 0.0006105 | 0 | 1.4121 | 0 | 0.0006105 | 1.4121 | 259038 | 12.0355 | 259037.9994
39050.4914 | 1889 | 0 | 39050.4914 | 2320 | 0 |  | 1761.5 | 1997.5 | 115.3236 | 0 | 141.6361 | 0 | 1.1532 | 0 | 1.4164 | 0 | 1.1532 | 1.4164 | 37.1826 | 11.6974 | 36.0294
39050.4919 | 1980 | 0 | 39050.4919 | 2089 | 0 |  | 1803.5 | 2039.5 | 120.8791 | 0 | 127.5336 | 0 | 1.2088 | 0 | 1.2753 | 0 | 1.2088 | 1.2753 | 30.8778 | 24.0488 | 29.669
39050.4924 | 2076 | 0 | 39050.4924 | 1971 | 0 |  | 1845.5 | 2081.5 | 126.7399 | 0 | 120.3297 | 0 | 1.2674 | 0 | 1.2033 | 0 | 1.2674 | 1.2033 | 24.8256 | 31.4754 | 23.5582
39050.4929 | 1965 | 0 | 39050.4929 | 2532 | 0 |  | 1887.5 | 2123.5 | 119.9634 | 0 | 154.5788 | 0 | 1.1996 | 0 | 1.5458 | 0 | 1.1996 | 1.5458 | 31.8768 | 2.3452 | 30.6772
39050.4934 | 2307 | 0 | 39050.4934 | 2013 | 0 |  | 1929.5 | 2165.5 | 140.8425 | 0 | 122.8938 | 0 | 1.4084 | 0 | 1.2289 | 0 | 1.4084 | 1.2289 | 12.3268 | 28.7322 | 10.9184

## A2-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 160.8901 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39050.4686 | 0 | 0 | 39050.4686 | 0 | 0 |  | -215 | 21 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.469 | 0 | 0 | 39050.4691 | 0 | 0 |  | -173.5 | 62.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4695 | 0 | 0 | 39050.4695 | 0 | 0 |  | -131.5 | 104.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.47 | 0 | 0 | 39050.47 | 0 | 0 |  | -89 | 147 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4705 | 0 | 0 | 39050.4705 | 0 | 0 |  | -47.5 | 188.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.471 | 0 | 0 | 39050.471 | 0 | 0 |  | -5.5 | 230.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4715 | 0 | 0 | 39050.4715 | 0 | 0 |  | 36.5 | 272.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.472 | 0 | 0 | 39050.472 | 0 | 0 |  | 78.5 | 314.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4724 | 0 | 0 | 39050.4725 | 0 | 0 |  | 120.5 | 356.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4729 | 0 | 0 | 39050.4729 | 0 | 0 |  | 162.5 | 398.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4734 | 0 | 0 | 39050.4734 | 0 | 0 |  | 204.5 | 440.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4739 | 0 | 0 | 39050.4739 | 0 | 0 |  | 246.5 | 482.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4744 | 0 | 0 | 39050.4744 | 0 | 0 |  | 288.5 | 524.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4749 | 0 | 0 | 39050.4749 | 0 | 0 |  | 330.5 | 566.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4754 | 0 | 0 | 39050.4754 | 0 | 0 |  | 372.5 | 608.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4758 | 0 | 0 | 39050.4759 | 0 | 0 |  | 414.5 | 650.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4763 | 0 | 0 | 39050.4763 | 0 | 0 |  | 456.5 | 692.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4768 | 0 | 0 | 39050.4768 | 0 | 0 |  | 498.5 | 734.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4773 | 0 | 0 | 39050.4773 | 0 | 0 |  | 540.5 | 776.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4778 | 0 | 0 | 39050.4778 | 0 | 0 |  | 582.5 | 818.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4783 | 0 | 0 | 39050.4783 | 0 | 0 |  | 624.5 | 860.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526976 | 526976 | 526975.9997
39050.4788 | 0 | 0 | 39050.4788 | 1920 | 0 |  | 666.5 | 902.5 | 0.030525 | 0 | 117.2161 | 0 | 0.00030525 | 0 | 1.1722 | 0 | 0.00030525 | 1.1722 | 526976 | 37.2594 | 526975.9997
39050.4792 | 1 | 0 | 39050.4793 | 2197 | 0 |  | 708.5 | 944.5 | 0.06105 | 0 | 134.127 | 0 | 0.0006105 | 0 | 1.3413 | 0 | 0.0006105 | 1.3413 | 263438 | 19.9536 | 263437.9994
39050.4797 | 1 | 0 | 39050.4797 | 2363 | 0 |  | 750.5 | 986.5 | 0.06105 | 0 | 144.2613 | 0 | 0.0006105 | 0 | 1.4426 | 0 | 0.0006105 | 1.4426 | 263438 | 11.5269 | 263437.9994
39050.4802 | 1 | 0 | 39050.4802 | 1993 | 0 |  | 792.5 | 1028.5 | 0.06105 | 0 | 121.6728 | 0 | 0.0006105 | 0 | 1.2167 | 0 | 0.0006105 | 1.2167 | 263438 | 32.2318 | 263437.9994
39050.4807 | 1 | 0 | 39050.4807 | 2093 | 0 |  | 834.5 | 1070.5 | 0.06105 | 0 | 127.7778 | 0 | 0.0006105 | 0 | 1.2778 | 0 | 0.0006105 | 1.2778 | 263438 | 25.914 | 263437.9994
39050.4812 | 1 | 0 | 39050.4812 | 1975 | 0 |  | 876.5 | 1112.5 | 0.06105 | 0 | 120.5739 | 0 | 0.0006105 | 0 | 1.2057 | 0 | 0.0006105 | 1.2057 | 263438 | 33.437 | 263437.9994
39050.4817 | 1 | 0 | 39050.4817 | 2352 | 0 |  | 918.5 | 1154.5 | 0.06105 | 0 | 143.5897 | 0 | 0.0006105 | 0 | 1.4359 | 0 | 0.0006105 | 1.4359 | 263438 | 12.0485 | 263437.9994
39050.4822 | 1 | 0 | 39050.4822 | 2036 | 0 |  | 960.5 | 1196.5 | 0.06105 | 0 | 124.2979 | 0 | 0.0006105 | 0 | 1.243 | 0 | 0.0006105 | 1.243 | 263438 | 29.4391 | 263437.9994
39050.4827 | 1 | 0 | 39050.4827 | 2298 | 0 |  | 1002.5 | 1238.5 | 0.06105 | 0 | 140.293 | 0 | 0.0006105 | 0 | 1.4029 | 0 | 0.0006105 | 1.4029 | 263438 | 14.6815 | 263437.9994
39050.4831 | 1 | 0 | 39050.4831 | 2170 | 0 |  | 1044.5 | 1280.5 | 0.06105 | 0 | 132.4786 | 0 | 0.0006105 | 0 | 1.3248 | 0 | 0.0006105 | 1.3248 | 263438 | 21.4461 | 263437.9994
39050.4836 | 1 | 0 | 39050.4836 | 2516 | 0 |  | 1086.5 | 1322.5 | 0.06105 | 0 | 153.602 | 0 | 0.0006105 | 0 | 1.536 | 0 | 0.0006105 | 1.536 | 263438 | 4.7448 | 263437.9994
39050.4841 | 1 | 0 | 39050.4841 | 2068 | 0 |  | 1128.5 | 1364.5 | 0.06105 | 0 | 126.2515 | 0 | 0.0006105 | 0 | 1.2625 | 0 | 0.0006105 | 1.2625 | 263438 | 27.4362 | 263437.9994
39050.4846 | 1 | 0 | 39050.4846 | 2539 | 0 |  | 1170.5 | 1406.5 | 0.06105 | 0 | 155.0061 | 0 | 0.0006105 | 0 | 1.5501 | 0 | 0.0006105 | 1.5501 | 263438 | 3.796 | 263437.9994
39050.4851 | 1 | 0 | 39050.4851 | 2593 | 0 |  | 1212.5 | 1448.5 | 0.06105 | 0 | 158.3028 | 0 | 0.0006105 | 0 | 1.583 | 0 | 0.0006105 | 1.583 | 263438 | 1.6344 | 263437.9994
39050.4856 | 1 | 0 | 39050.4856 | 2619 | 0 |  | 1254.5 | 1490.5 | 0.06105 | 0 | 159.8901 | 0 | 0.0006105 | 0 | 1.5989 | 0 | 0.0006105 | 1.5989 | 263438 | 0.62543 | 263437.9994
39050.4861 | 1 | 0 | 39050.4861 | 2067 | 0 |  | 1296.5 | 1532.5 | 0.06105 | 0 | 126.1905 | 0 | 0.0006105 | 0 | 1.2619 | 0 | 0.0006105 | 1.2619 | 263438 | 27.4978 | 263437.9994
39050.4865 | 2 | 0 | 39050.4866 | 2512 | 0 |  | 1338.5 | 1574.5 | 0.1221 | 0 | 153.3578 | 0 | 0.001221 | 0 | 1.5336 | 0 | 0.001221 | 1.5336 | 131669 | 4.9116 | 131668.9988
39050.487 | 1 | 0 | 39050.487 | 2061 | 0 |  | 1380.5 | 1616.5 | 0.06105 | 0 | 125.8242 | 0 | 0.0006105 | 0 | 1.2582 | 0 | 0.0006105 | 1.2582 | 263438 | 27.869 | 263437.9994
39050.4875 | 1 | 0 | 39050.4875 | 2377 | 0 |  | 1422.5 | 1658.5 | 0.06105 | 0 | 145.116 | 0 | 0.0006105 | 0 | 1.4512 | 0 | 0.0006105 | 1.4512 | 263438 | 10.87 | 263437.9994
39050.488 | 1 | 0 | 39050.488 | 2560 | 0 |  | 1464.5 | 1700.5 | 0.06105 | 0 | 156.2882 | 0 | 0.0006105 | 0 | 1.5629 | 0 | 0.0006105 | 1.5629 | 263438 | 2.9445 | 263437.9994
39050.4885 | 1 | 0 | 39050.4885 | 1938 | 0 |  | 1506.5 | 1742.5 | 0.06105 | 0 | 118.315 | 0 | 0.0006105 | 0 | 1.1832 | 0 | 0.0006105 | 1.1832 | 263438 | 35.9845 | 263437.9994
39050.489 | 1 | 0 | 39050.489 | 2590 | 0 |  | 1548.5 | 1784.5 | 0.06105 | 0 | 158.1197 | 0 | 0.0006105 | 0 | 1.5812 | 0 | 0.0006105 | 1.5812 | 263438 | 1.7521 | 263437.9994
39050.4895 | 1 | 0 | 39050.4895 | 2042 | 0 |  | 1590.5 | 1826.5 | 0.06105 | 0 | 124.6642 | 0 | 0.0006105 | 0 | 1.2466 | 0 | 0.0006105 | 1.2466 | 263438 | 29.0588 | 263437.9994
39050.4899 | 1 | 0 | 39050.49 | 2274 | 0 |  | 1632.5 | 1868.5 | 0.06105 | 0 | 138.8278 | 0 | 0.0006105 | 0 | 1.3883 | 0 | 0.0006105 | 1.3883 | 263438 | 15.8918 | 263437.9994
39050.4904 | 1 | 0 | 39050.4904 | 2086 | 0 |  | 1674.5 | 1910.5 | 0.06105 | 0 | 127.3504 | 0 | 0.0006105 | 0 | 1.2735 | 0 | 0.0006105 | 1.2735 | 263438 | 26.3365 | 263437.9994
39050.4909 | 1 | 0 | 39050.4909 | 2004 | 0 |  | 1716.5 | 1952.5 | 0.06105 | 0 | 122.3443 | 0 | 0.0006105 | 0 | 1.2234 | 0 | 0.0006105 | 1.2234 | 263438 | 31.506 | 263437.9994
39050.4914 | 1871 | 0 | 39050.4914 | 2378 | 0 |  | 1758.5 | 1994.5 | 114.2247 | 0 | 145.177 | 0 | 1.1422 | 0 | 1.4518 | 0 | 1.1422 | 1.4518 | 40.8541 | 10.8234 | 39.7118
39050.4919 | 2362 | 0 | 39050.4919 | 2141 | 0 |  | 1800.5 | 2036.5 | 144.2002 | 0 | 130.7082 | 0 | 1.442 | 0 | 1.3071 | 0 | 1.442 | 1.3071 | 11.5741 | 23.0911 | 10.1321
39050.4924 | 2170 | 0 | 39050.4924 | 2198 | 0 |  | 1842.5 | 2078.5 | 132.4786 | 0 | 134.188 | 0 | 1.3248 | 0 | 1.3419 | 0 | 1.3248 | 1.3419 | 21.4461 | 19.899 | 20.1213
39050.4929 | 1905 | 0 | 39050.4929 | 2035 | 0 |  | 1884.5 | 2120.5 | 116.3004 | 0 | 124.2369 | 0 | 1.163 | 0 | 1.2424 | 0 | 1.163 | 1.2424 | 38.3402 | 29.5027 | 37.1772
39050.4933 | 2118 | 0 | 39050.4934 | 2101 | 0 |  | 1926.5 | 2162.5 | 129.304 | 0 | 128.2662 | 0 | 1.293 | 0 | 1.2827 | 0 | 1.293 | 1.2827 | 24.4278 | 25.4346 | 23.1347

## A2-B4
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 153.0757 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39050.4685 | 0 | 0 | 39050.4685 | 0 | 0 |  | -218 | 18 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.469 | 0 | 0 | 39050.469 | 0 | 0 |  | -176 | 60 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4695 | 0 | 0 | 39050.4695 | 0 | 0 |  | -134 | 102 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.47 | 0 | 0 | 39050.47 | 0 | 0 |  | -92 | 144 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4705 | 0 | 0 | 39050.4705 | 0 | 0 |  | -50 | 186 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4709 | 0 | 0 | 39050.471 | 0 | 0 |  | -8 | 228 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4714 | 0 | 0 | 39050.4715 | 0 | 0 |  | 34 | 270 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4719 | 0 | 0 | 39050.4719 | 0 | 0 |  | 76 | 312 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4724 | 0 | 0 | 39050.4724 | 0 | 0 |  | 118 | 354 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4729 | 0 | 0 | 39050.4729 | 0 | 0 |  | 160 | 396 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4734 | 0 | 0 | 39050.4734 | 0 | 0 |  | 202 | 438 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4739 | 0 | 0 | 39050.4739 | 0 | 0 |  | 244 | 480 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4744 | 0 | 0 | 39050.4744 | 0 | 0 |  | 286 | 522 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4748 | 0 | 0 | 39050.4749 | 0 | 0 |  | 328 | 564 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4753 | 0 | 0 | 39050.4753 | 0 | 0 |  | 370 | 606 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4758 | 0 | 0 | 39050.4758 | 0 | 0 |  | 412 | 648 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4763 | 0 | 0 | 39050.4763 | 0 | 0 |  | 454 | 690 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4768 | 0 | 0 | 39050.4768 | 0 | 0 |  | 496 | 732 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4773 | 0 | 0 | 39050.4773 | 0 | 0 |  | 538 | 774 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4778 | 0 | 0 | 39050.4778 | 0 | 0 |  | 579.5 | 815.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4782 | 0 | 0 | 39050.4783 | 0 | 0 |  | 622 | 858 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4787 | 0 | 0 | 39050.4787 | 0 | 0 |  | 663.5 | 899.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39050.4792 | 1 | 0 | 39050.4792 | 1 | 0 |  | 706 | 942 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4797 | 1 | 0 | 39050.4797 | 1 | 0 |  | 748 | 984 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4802 | 1 | 0 | 39050.4802 | 1 | 0 |  | 789.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4807 | 1 | 0 | 39050.4807 | 1 | 0 |  | 832 | 1068 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4812 | 1 | 0 | 39050.4812 | 1 | 0 |  | 873.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4816 | 1 | 0 | 39050.4817 | 1 | 0 |  | 916 | 1152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4821 | 1 | 0 | 39050.4821 | 1 | 0 |  | 957.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4826 | 1 | 0 | 39050.4826 | 1 | 0 |  | 999.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4831 | 1 | 0 | 39050.4831 | 1 | 0 |  | 1042 | 1278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4836 | 2 | 0 | 39050.4836 | 2 | 0 |  | 1083.5 | 1319.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125269 | 125269 | 125268.9988
39050.4841 | 2 | 0 | 39050.4841 | 2 | 0 |  | 1125.5 | 1361.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125269 | 125269 | 125268.9988
39050.4846 | 2 | 0 | 39050.4846 | 2 | 0 |  | 1167.5 | 1403.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125269 | 125269 | 125268.9988
39050.485 | 2 | 0 | 39050.4851 | 2 | 0 |  | 1209.5 | 1445.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125269 | 125269 | 125268.9988
39050.4855 | 2 | 0 | 39050.4855 | 1 | 0 |  | 1251.5 | 1487.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125269 | 250638 | 125268.9988
39050.486 | 2 | 0 | 39050.486 | 1 | 0 |  | 1293.5 | 1529.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125269 | 250638 | 125268.9988
39050.4865 | 1 | 0 | 39050.4865 | 2 | 0 |  | 1335.5 | 1571.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250638 | 125269 | 250637.9994
39050.487 | 2 | 0 | 39050.487 | 1 | 0 |  | 1377.5 | 1613.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125269 | 250638 | 125268.9988
39050.4875 | 2 | 0 | 39050.4875 | 1 | 0 |  | 1419.5 | 1655.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125269 | 250638 | 125268.9988
39050.488 | 2 | 0 | 39050.488 | 2 | 0 |  | 1461.5 | 1697.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125269 | 125269 | 125268.9988
39050.4884 | 2 | 0 | 39050.4885 | 1 | 0 |  | 1503.5 | 1739.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125269 | 250638 | 125268.9988
39050.4889 | 1 | 0 | 39050.4889 | 1 | 0 |  | 1545.5 | 1781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4894 | 2 | 0 | 39050.4894 | 1 | 0 |  | 1587.5 | 1823.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125269 | 250638 | 125268.9988
39050.4899 | 2 | 0 | 39050.4899 | 1 | 0 |  | 1629.5 | 1865.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125269 | 250638 | 125268.9988
39050.4904 | 1 | 0 | 39050.4904 | 1 | 0 |  | 1671.5 | 1907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4909 | 1 | 0 | 39050.4909 | 1 | 0 |  | 1713.5 | 1949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39050.4914 | 97 | 0 | 39050.4914 | 986 | 0 |  | 1755.5 | 1991.5 | 5.9219 | 0 | 60.1954 | 0 | 0.059219 | 0 | 0.60195 | 0 | 0.059219 | 0.60195 | 2484.9278 | 154.2982 | 2484.8686
39050.4919 | 2410 | 0 | 39050.4919 | 1885 | 0 |  | 1797.5 | 2033.5 | 147.1306 | 0 | 115.0794 | 0 | 1.4713 | 0 | 1.1508 | 0 | 1.4713 | 1.1508 | 4.0407 | 33.0175 | 2.5694
39050.4923 | 1900 | 0 | 39050.4923 | 1929 | 0 |  | 1839.5 | 2075.5 | 115.9951 | 0 | 117.7656 | 0 | 1.16 | 0 | 1.1777 | 0 | 1.16 | 1.1777 | 31.9674 | 29.9834 | 30.8074
39050.4928 | 2100 | 0 | 39050.4928 | 2491 | 0 |  | 1881.5 | 2117.5 | 128.2051 | 0 | 152.0757 | 0 | 1.2821 | 0 | 1.5208 | 0 | 1.2821 | 1.5208 | 19.399 | 0.65757 | 18.117
39050.4933 | 2130 | 0 | 39050.4933 | 1909 | 0 |  | 1923.5 | 2159.5 | 130.0366 | 0 | 116.5446 | 0 | 1.3004 | 0 | 1.1654 | 0 | 1.3004 | 1.1654 | 17.7174 | 31.3452 | 16.417

## A2-B3
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 154.4188 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39050.4685 | 0 | 0 | 39050.4685 | 0 | 0 |  | -220.5 | 15.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.469 | 0 | 0 | 39050.469 | 0 | 0 |  | -179 | 57 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4695 | 0 | 0 | 39050.4695 | 0 | 0 |  | -136.5 | 99.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4699 | 0 | 0 | 39050.47 | 0 | 0 |  | -95 | 141 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4704 | 0 | 0 | 39050.4705 | 0 | 0 |  | -53 | 183 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4709 | 0 | 0 | 39050.4709 | 0 | 0 |  | -11 | 225 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4714 | 0 | 0 | 39050.4714 | 0 | 0 |  | 31 | 267 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4719 | 0 | 0 | 39050.4719 | 0 | 0 |  | 73 | 309 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4724 | 0 | 0 | 39050.4724 | 0 | 0 |  | 115 | 351 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4729 | 0 | 0 | 39050.4729 | 0 | 0 |  | 157 | 393 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4733 | 0 | 0 | 39050.4734 | 0 | 0 |  | 199 | 435 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4738 | 0 | 0 | 39050.4739 | 0 | 0 |  | 241 | 477 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4743 | 0 | 0 | 39050.4743 | 0 | 0 |  | 283 | 519 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4748 | 0 | 0 | 39050.4748 | 0 | 0 |  | 325 | 561 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4753 | 0 | 0 | 39050.4753 | 0 | 0 |  | 367 | 603 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4758 | 0 | 0 | 39050.4758 | 0 | 0 |  | 409 | 645 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4763 | 0 | 0 | 39050.4763 | 0 | 0 |  | 451 | 687 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4767 | 0 | 0 | 39050.4768 | 0 | 0 |  | 493 | 729 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4772 | 0 | 0 | 39050.4773 | 0 | 0 |  | 535 | 771 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4777 | 0 | 0 | 39050.4777 | 0 | 0 |  | 577 | 813 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4782 | 0 | 0 | 39050.4782 | 0 | 0 |  | 619 | 855 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4787 | 1 | 0 | 39050.4787 | 0 | 0 |  | 661 | 897 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 252838 | 505776 | 252837.9994
39050.4792 | 3 | 0 | 39050.4792 | 1 | 0 |  | 703 | 939 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 84212.6667 | 252838 | 84212.6648
39050.4797 | 2 | 0 | 39050.4797 | 1 | 0 |  | 745 | 981 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126369 | 252838 | 126368.9988
39050.4802 | 3 | 0 | 39050.4802 | 1 | 0 |  | 787 | 1023 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 84212.6667 | 252838 | 84212.6648
39050.4806 | 2 | 0 | 39050.4807 | 1 | 0 |  | 829 | 1065 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126369 | 252838 | 126368.9988
39050.4811 | 2 | 0 | 39050.4811 | 1 | 0 |  | 871 | 1107 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126369 | 252838 | 126368.9988
39050.4816 | 2 | 0 | 39050.4816 | 1 | 0 |  | 913 | 1149 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126369 | 252838 | 126368.9988
39050.4821 | 2 | 0 | 39050.4821 | 1 | 0 |  | 955 | 1191 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126369 | 252838 | 126368.9988
39050.4826 | 2 | 0 | 39050.4826 | 2 | 0 |  | 997 | 1233 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 126369 | 126369 | 126368.9988
39050.4831 | 2 | 0 | 39050.4831 | 989 | 0 |  | 1039 | 1275 | 0.1221 | 0 | 60.3785 | 0 | 0.001221 | 0 | 0.60379 | 0 | 0.001221 | 0.60379 | 126369 | 155.7513 | 126368.9988
39050.4836 | 2 | 0 | 39050.4836 | 2150 | 0 |  | 1081 | 1317 | 0.1221 | 0 | 131.2576 | 0 | 0.001221 | 0 | 1.3126 | 0 | 0.001221 | 1.3126 | 126369 | 17.6456 | 126368.9988
39050.484 | 2 | 0 | 39050.4841 | 1643 | 0 |  | 1123 | 1359 | 0.1221 | 0 | 100.3053 | 0 | 0.001221 | 0 | 1.0031 | 0 | 0.001221 | 1.0031 | 126369 | 53.9489 | 126368.9988
39050.4845 | 2 | 0 | 39050.4845 | 2081 | 0 |  | 1165 | 1401 | 0.1221 | 0 | 127.0452 | 0 | 0.001221 | 0 | 1.2705 | 0 | 0.001221 | 1.2705 | 126369 | 21.5464 | 126368.9988
39050.485 | 2 | 0 | 39050.485 | 2370 | 0 |  | 1207 | 1443 | 0.1221 | 0 | 144.6886 | 0 | 0.001221 | 0 | 1.4469 | 0 | 0.001221 | 1.4469 | 126369 | 6.7249 | 126368.9988
39050.4855 | 3 | 0 | 39050.4855 | 1905 | 0 |  | 1249 | 1485 | 0.18315 | 0 | 116.3004 | 0 | 0.0018315 | 0 | 1.163 | 0 | 0.0018315 | 1.163 | 84212.6667 | 32.7759 | 84212.6648
39050.486 | 2 | 0 | 39050.486 | 1994 | 0 |  | 1291 | 1527 | 0.1221 | 0 | 121.7338 | 0 | 0.001221 | 0 | 1.2173 | 0 | 0.001221 | 1.2173 | 126369 | 26.8495 | 126368.9988
39050.4865 | 2 | 0 | 39050.4865 | 2462 | 0 |  | 1333 | 1569 | 0.1221 | 0 | 150.3053 | 0 | 0.001221 | 0 | 1.5031 | 0 | 0.001221 | 1.5031 | 126369 | 2.7368 | 126368.9988
39050.487 | 2 | 0 | 39050.487 | 1970 | 0 |  | 1375 | 1611 | 0.1221 | 0 | 120.2686 | 0 | 0.001221 | 0 | 1.2027 | 0 | 0.001221 | 1.2027 | 126369 | 28.3949 | 126368.9988
39050.4874 | 2 | 0 | 39050.4875 | 1917 | 0 |  | 1417 | 1653 | 0.1221 | 0 | 117.033 | 0 | 0.001221 | 0 | 1.1703 | 0 | 0.001221 | 1.1703 | 126369 | 31.9447 | 126368.9988
39050.4879 | 2 | 0 | 39050.488 | 2099 | 0 |  | 1459 | 1695 | 0.1221 | 0 | 128.1441 | 0 | 0.001221 | 0 | 1.2814 | 0 | 0.001221 | 1.2814 | 126369 | 20.504 | 126368.9988
39050.4884 | 2 | 0 | 39050.4884 | 2491 | 0 |  | 1501 | 1737 | 0.1221 | 0 | 152.0757 | 0 | 0.001221 | 0 | 1.5208 | 0 | 0.001221 | 1.5208 | 126369 | 1.5407 | 126368.9988
39050.4889 | 2 | 0 | 39050.4889 | 2200 | 0 |  | 1543 | 1779 | 0.1221 | 0 | 134.3101 | 0 | 0.001221 | 0 | 1.3431 | 0 | 0.001221 | 1.3431 | 126369 | 14.9718 | 126368.9988
39050.4894 | 2 | 0 | 39050.4894 | 2018 | 0 |  | 1585 | 1821 | 0.1221 | 0 | 123.199 | 0 | 0.001221 | 0 | 1.232 | 0 | 0.001221 | 1.232 | 126369 | 25.3409 | 126368.9988
39050.4899 | 2 | 0 | 39050.4899 | 2069 | 0 |  | 1627 | 1863 | 0.1221 | 0 | 126.3126 | 0 | 0.001221 | 0 | 1.2631 | 0 | 0.001221 | 1.2631 | 126369 | 22.2513 | 126368.9988
39050.4904 | 1 | 0 | 39050.4904 | 2322 | 0 |  | 1669 | 1905 | 0.06105 | 0 | 141.7582 | 0 | 0.0006105 | 0 | 1.4176 | 0 | 0.0006105 | 1.4176 | 252838 | 8.9311 | 252837.9994
39050.4908 | 1 | 0 | 39050.4909 | 2143 | 0 |  | 1711 | 1947 | 0.06105 | 0 | 130.8303 | 0 | 0.0006105 | 0 | 1.3083 | 0 | 0.0006105 | 1.3083 | 252838 | 18.0299 | 252837.9994
39050.4913 | 1 | 0 | 39050.4914 | 2337 | 0 |  | 1753 | 1989 | 0.06105 | 0 | 142.674 | 0 | 0.0006105 | 0 | 1.4267 | 0 | 0.0006105 | 1.4267 | 252838 | 8.2319 | 252837.9994
39050.4918 | 2393 | 0 | 39050.4918 | 1959 | 0 |  | 1795 | 2031 | 146.0928 | 0 | 119.5971 | 0 | 1.4609 | 0 | 1.196 | 0 | 1.4609 | 1.196 | 5.6991 | 29.1159 | 4.2382
39050.4923 | 2453 | 0 | 39050.4923 | 2485 | 0 |  | 1837 | 2073 | 149.7558 | 0 | 151.7094 | 0 | 1.4976 | 0 | 1.5171 | 0 | 1.4976 | 1.5171 | 3.1137 | 1.7859 | 1.6162
39050.4928 | 2165 | 0 | 39050.4928 | 2346 | 0 |  | 1879 | 2115 | 132.1734 | 0 | 143.2234 | 0 | 1.3217 | 0 | 1.4322 | 0 | 1.3217 | 1.4322 | 16.8305 | 7.8167 | 15.5088
39050.4933 | 2475 | 0 | 39050.4933 | 2513 | 0 |  | 1921 | 2157 | 151.0989 | 0 | 153.4188 | 0 | 1.511 | 0 | 1.5342 | 0 | 1.511 | 1.5342 | 2.1972 | 0.65181 | 0.68618

## A1-C6
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 159.2418 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39050.4685 | 0 | 0 | 39050.4685 | 0 | 0 |  | -223.5 | 12.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4689 | 0 | 0 | 39050.469 | 0 | 0 |  | -181.5 | 54.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4694 | 0 | 0 | 39050.4694 | 0 | 0 |  | -139.5 | 96.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4699 | 0 | 0 | 39050.4699 | 0 | 0 |  | -97.5 | 138.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4704 | 0 | 0 | 39050.4704 | 0 | 0 |  | -55.5 | 180.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4709 | 0 | 0 | 39050.4709 | 0 | 0 |  | -13.5 | 222.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4714 | 0 | 0 | 39050.4714 | 0 | 0 |  | 28.5 | 264.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4719 | 0 | 0 | 39050.4719 | 0 | 0 |  | 70.5 | 306.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4723 | 0 | 0 | 39050.4724 | 0 | 0 |  | 112.5 | 348.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4728 | 0 | 0 | 39050.4728 | 0 | 0 |  | 154.5 | 390.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4733 | 0 | 0 | 39050.4733 | 0 | 0 |  | 196.5 | 432.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4738 | 0 | 0 | 39050.4738 | 0 | 0 |  | 238.5 | 474.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4743 | 0 | 0 | 39050.4743 | 0 | 0 |  | 280.5 | 516.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4748 | 0 | 0 | 39050.4748 | 0 | 0 |  | 322.5 | 558.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4753 | 0 | 0 | 39050.4753 | 0 | 0 |  | 364.5 | 600.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4758 | 0 | 0 | 39050.4758 | 0 | 0 |  | 406.5 | 642.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4762 | 0 | 0 | 39050.4762 | 0 | 0 |  | 448.5 | 684.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4767 | 0 | 0 | 39050.4767 | 0 | 0 |  | 490.5 | 726.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4772 | 0 | 0 | 39050.4772 | 0 | 0 |  | 532.5 | 768.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4777 | 0 | 0 | 39050.4777 | 0 | 0 |  | 574.5 | 810.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4782 | 0 | 0 | 39050.4782 | 0 | 0 |  | 616.5 | 852.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521576 | 521576 | 521575.9997
39050.4787 | 2 | 0 | 39050.4787 | 1 | 0 |  | 658.5 | 894.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 130319 | 260738 | 130318.9988
39050.4791 | 3 | 0 | 39050.4792 | 2535 | 0 |  | 700 | 936 | 0.18315 | 0 | 154.7619 | 0 | 0.0018315 | 0 | 1.5476 | 0 | 0.0018315 | 1.5476 | 86846 | 2.8947 | 86845.9982
39050.4796 | 2 | 0 | 39050.4797 | 1967 | 0 |  | 742.5 | 978.5 | 0.1221 | 0 | 120.0855 | 0 | 0.001221 | 0 | 1.2009 | 0 | 0.001221 | 1.2009 | 130319 | 32.607 | 130318.9988
39050.4801 | 2 | 0 | 39050.4801 | 2315 | 0 |  | 784 | 1020 | 0.1221 | 0 | 141.3309 | 0 | 0.001221 | 0 | 1.4133 | 0 | 0.001221 | 1.4133 | 130319 | 12.673 | 130318.9988
39050.4806 | 2 | 0 | 39050.4806 | 2297 | 0 |  | 826.5 | 1062.5 | 0.1221 | 0 | 140.232 | 0 | 0.001221 | 0 | 1.4023 | 0 | 0.001221 | 1.4023 | 130319 | 13.5559 | 130318.9988
39050.4811 | 2 | 0 | 39050.4811 | 2189 | 0 |  | 868 | 1104 | 0.1221 | 0 | 133.6386 | 0 | 0.001221 | 0 | 1.3364 | 0 | 0.001221 | 1.3364 | 130319 | 19.1585 | 130318.9988
39050.4816 | 2 | 0 | 39050.4816 | 2459 | 0 |  | 910 | 1146 | 0.1221 | 0 | 150.1221 | 0 | 0.001221 | 0 | 1.5012 | 0 | 0.001221 | 1.5012 | 130319 | 6.0748 | 130318.9988
39050.4821 | 2 | 0 | 39050.4821 | 2557 | 0 |  | 952 | 1188 | 0.1221 | 0 | 156.105 | 0 | 0.001221 | 0 | 1.5611 | 0 | 0.001221 | 1.5611 | 130319 | 2.0094 | 130318.9988
39050.4825 | 2 | 0 | 39050.4826 | 2240 | 0 |  | 994 | 1230 | 0.1221 | 0 | 136.7521 | 0 | 0.001221 | 0 | 1.3675 | 0 | 0.001221 | 1.3675 | 130319 | 16.4455 | 130318.9988
39050.483 | 2 | 0 | 39050.4831 | 2118 | 0 |  | 1036 | 1272 | 0.1221 | 0 | 129.304 | 0 | 0.001221 | 0 | 1.293 | 0 | 0.001221 | 1.293 | 130319 | 23.153 | 130318.9988
39050.4835 | 2 | 0 | 39050.4835 | 2004 | 0 |  | 1078.5 | 1314.5 | 0.1221 | 0 | 122.3443 | 0 | 0.001221 | 0 | 1.2234 | 0 | 0.001221 | 1.2234 | 130319 | 30.1587 | 130318.9988
39050.484 | 2 | 0 | 39050.484 | 2028 | 0 |  | 1120 | 1356 | 0.1221 | 0 | 123.8095 | 0 | 0.001221 | 0 | 1.2381 | 0 | 0.001221 | 1.2381 | 130319 | 28.6183 | 130318.9988
39050.4845 | 2 | 0 | 39050.4845 | 2563 | 0 |  | 1162 | 1398 | 0.1221 | 0 | 156.4713 | 0 | 0.001221 | 0 | 1.5647 | 0 | 0.001221 | 1.5647 | 130319 | 1.7706 | 130318.9988
39050.485 | 2 | 0 | 39050.485 | 2067 | 0 |  | 1204 | 1440 | 0.1221 | 0 | 126.1905 | 0 | 0.001221 | 0 | 1.2619 | 0 | 0.001221 | 1.2619 | 130319 | 26.1916 | 130318.9988
39050.4855 | 2 | 0 | 39050.4855 | 2068 | 0 |  | 1246 | 1482 | 0.1221 | 0 | 126.2515 | 0 | 0.001221 | 0 | 1.2625 | 0 | 0.001221 | 1.2625 | 130319 | 26.1306 | 130318.9988
39050.4859 | 1 | 0 | 39050.486 | 2584 | 0 |  | 1288 | 1524 | 0.06105 | 0 | 157.7534 | 0 | 0.0006105 | 0 | 1.5775 | 0 | 0.0006105 | 1.5775 | 260738 | 0.9435 | 260737.9994
39050.4864 | 2 | 0 | 39050.4865 | 2592 | 0 |  | 1330 | 1566 | 0.1221 | 0 | 158.2418 | 0 | 0.001221 | 0 | 1.5824 | 0 | 0.001221 | 1.5824 | 130319 | 0.63194 | 130318.9988
39050.4869 | 2 | 0 | 39050.4869 | 2569 | 0 |  | 1372 | 1608 | 0.1221 | 0 | 156.8376 | 0 | 0.001221 | 0 | 1.5684 | 0 | 0.001221 | 1.5684 | 130319 | 1.5329 | 130318.9988
39050.4874 | 2 | 0 | 39050.4874 | 2234 | 0 |  | 1414 | 1650 | 0.1221 | 0 | 136.3858 | 0 | 0.001221 | 0 | 1.3639 | 0 | 0.001221 | 1.3639 | 130319 | 16.7583 | 130318.9988
39050.4879 | 2 | 0 | 39050.4879 | 2442 | 0 |  | 1456 | 1692 | 0.1221 | 0 | 149.0842 | 0 | 0.001221 | 0 | 1.4908 | 0 | 0.001221 | 1.4908 | 130319 | 6.8133 | 130318.9988
39050.4884 | 2 | 0 | 39050.4884 | 2097 | 0 |  | 1498 | 1734 | 0.1221 | 0 | 128.022 | 0 | 0.001221 | 0 | 1.2802 | 0 | 0.001221 | 1.2802 | 130319 | 24.3863 | 130318.9988
39050.4889 | 1 | 0 | 39050.4889 | 2545 | 0 |  | 1540 | 1776 | 0.06105 | 0 | 155.3724 | 0 | 0.0006105 | 0 | 1.5537 | 0 | 0.0006105 | 1.5537 | 260738 | 2.4904 | 260737.9994
39050.4894 | 2 | 0 | 39050.4894 | 2141 | 0 |  | 1582 | 1818 | 0.1221 | 0 | 130.7082 | 0 | 0.001221 | 0 | 1.3071 | 0 | 0.001221 | 1.3071 | 130319 | 21.83 | 130318.9988
39050.4898 | 2 | 0 | 39050.4899 | 2431 | 0 |  | 1624 | 1860 | 0.1221 | 0 | 148.4127 | 0 | 0.001221 | 0 | 1.4841 | 0 | 0.001221 | 1.4841 | 130319 | 7.2966 | 130318.9988
39050.4903 | 1 | 0 | 39050.4903 | 1949 | 0 |  | 1666 | 1902 | 0.06105 | 0 | 118.9866 | 0 | 0.0006105 | 0 | 1.1899 | 0 | 0.0006105 | 1.1899 | 260738 | 33.8317 | 260737.9994
39050.4908 | 1 | 0 | 39050.4908 | 2291 | 0 |  | 1708 | 1944 | 0.06105 | 0 | 139.8657 | 0 | 0.0006105 | 0 | 1.3987 | 0 | 0.0006105 | 1.3987 | 260738 | 13.8533 | 260737.9994
39050.4913 | 2 | 0 | 39050.4913 | 2123 | 0 |  | 1750 | 1986 | 0.1221 | 0 | 129.6093 | 0 | 0.001221 | 0 | 1.2961 | 0 | 0.001221 | 1.2961 | 130319 | 22.8629 | 130318.9988
39050.4918 | 1964 | 0 | 39050.4918 | 1986 | 0 |  | 1792 | 2028 | 119.9023 | 0 | 121.2454 | 0 | 1.199 | 0 | 1.2125 | 0 | 1.199 | 1.2125 | 32.8096 | 31.3384 | 31.6105
39050.4923 | 2186 | 0 | 39050.4923 | 1985 | 0 |  | 1834 | 2070 | 133.4554 | 0 | 121.1844 | 0 | 1.3346 | 0 | 1.2118 | 0 | 1.3346 | 1.2118 | 19.322 | 31.4045 | 17.9875
39050.4928 | 2014 | 0 | 39050.4928 | 2353 | 0 |  | 1876 | 2112 | 122.9548 | 0 | 143.6508 | 0 | 1.2295 | 0 | 1.4365 | 0 | 1.2295 | 1.4365 | 29.5124 | 10.8534 | 28.2829
39050.4932 | 1911 | 0 | 39050.4933 | 2261 | 0 |  | 1918 | 2154 | 116.6667 | 0 | 138.0342 | 0 | 1.1667 | 0 | 1.3803 | 0 | 1.1667 | 1.3803 | 36.4929 | 15.364 | 35.3263

## A1-C5
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 157.6545 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39050.4684 | 0 | 0 | 39050.4684 | 0 | 0 |  | -226.5 | 9.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4689 | 0 | 0 | 39050.4689 | 0 | 0 |  | -184.5 | 51.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4694 | 0 | 0 | 39050.4694 | 0 | 0 |  | -142.5 | 93.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4699 | 0 | 0 | 39050.4699 | 0 | 0 |  | -100.5 | 135.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4704 | 0 | 0 | 39050.4704 | 0 | 0 |  | -58.5 | 177.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4709 | 0 | 0 | 39050.4709 | 0 | 0 |  | -16.5 | 219.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4713 | 0 | 0 | 39050.4714 | 0 | 0 |  | 25.5 | 261.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4718 | 0 | 0 | 39050.4718 | 0 | 0 |  | 67.5 | 303.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4723 | 0 | 0 | 39050.4723 | 0 | 0 |  | 109.5 | 345.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4728 | 0 | 0 | 39050.4728 | 0 | 0 |  | 151.5 | 387.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4733 | 0 | 0 | 39050.4733 | 0 | 0 |  | 193.5 | 429.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4738 | 0 | 0 | 39050.4738 | 0 | 0 |  | 235.5 | 471.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4743 | 0 | 0 | 39050.4743 | 0 | 0 |  | 277.5 | 513.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4747 | 0 | 0 | 39050.4748 | 0 | 0 |  | 319.5 | 555.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4752 | 0 | 0 | 39050.4752 | 0 | 0 |  | 361.5 | 597.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4757 | 0 | 0 | 39050.4757 | 0 | 0 |  | 403.5 | 639.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4762 | 0 | 0 | 39050.4762 | 0 | 0 |  | 445.5 | 681.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4767 | 0 | 0 | 39050.4767 | 0 | 0 |  | 487.5 | 723.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4772 | 0 | 0 | 39050.4772 | 0 | 0 |  | 529.5 | 765.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4777 | 0 | 0 | 39050.4777 | 0 | 0 |  | 571.5 | 807.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4781 | 0 | 0 | 39050.4782 | 0 | 0 |  | 613.5 | 849.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516376 | 516376 | 516375.9997
39050.4786 | 0 | 0 | 39050.4786 | 2422 | 0 |  | 655.5 | 891.5 | 0.030525 | 0 | 147.8632 | 0 | 0.00030525 | 0 | 1.4786 | 0 | 0.00030525 | 1.4786 | 516376 | 6.6218 | 516375.9997
39050.4791 | 1 | 0 | 39050.4791 | 2064 | 0 |  | 697.5 | 933.5 | 0.06105 | 0 | 126.0073 | 0 | 0.0006105 | 0 | 1.2601 | 0 | 0.0006105 | 1.2601 | 258138 | 25.1153 | 258137.9994
39050.4796 | 1 | 0 | 39050.4796 | 2109 | 0 |  | 739.5 | 975.5 | 0.06105 | 0 | 128.7546 | 0 | 0.0006105 | 0 | 1.2875 | 0 | 0.0006105 | 1.2875 | 258138 | 22.4457 | 258137.9994
39050.4801 | 1 | 0 | 39050.4801 | 2343 | 0 |  | 781.5 | 1017.5 | 0.06105 | 0 | 143.0403 | 0 | 0.0006105 | 0 | 1.4304 | 0 | 0.0006105 | 1.4304 | 258138 | 10.2168 | 258137.9994
39050.4806 | 1 | 0 | 39050.4806 | 1949 | 0 |  | 823.5 | 1059.5 | 0.06105 | 0 | 118.9866 | 0 | 0.0006105 | 0 | 1.1899 | 0 | 0.0006105 | 1.1899 | 258138 | 32.4977 | 258137.9994
39050.4811 | 1 | 0 | 39050.4811 | 2301 | 0 |  | 865.5 | 1101.5 | 0.06105 | 0 | 140.4762 | 0 | 0.0006105 | 0 | 1.4048 | 0 | 0.0006105 | 1.4048 | 258138 | 12.2286 | 258137.9994
39050.4816 | 1 | 0 | 39050.4816 | 2450 | 0 |  | 907.5 | 1143.5 | 0.06105 | 0 | 149.5726 | 0 | 0.0006105 | 0 | 1.4957 | 0 | 0.0006105 | 1.4957 | 258138 | 5.4033 | 258137.9994
39050.482 | 1 | 0 | 39050.482 | 2024 | 0 |  | 949.5 | 1185.5 | 0.06105 | 0 | 123.5653 | 0 | 0.0006105 | 0 | 1.2357 | 0 | 0.0006105 | 1.2357 | 258138 | 27.5879 | 258137.9994
39050.4825 | 1 | 0 | 39050.4825 | 2559 | 0 |  | 991.5 | 1227.5 | 0.06105 | 0 | 156.2271 | 0 | 0.0006105 | 0 | 1.5623 | 0 | 0.0006105 | 1.5623 | 258138 | 0.91364 | 258137.9994
39050.483 | 1 | 0 | 39050.483 | 2330 | 0 |  | 1033.5 | 1269.5 | 0.06105 | 0 | 142.2466 | 0 | 0.0006105 | 0 | 1.4225 | 0 | 0.0006105 | 1.4225 | 258138 | 10.8318 | 258137.9994
39050.4835 | 2 | 0 | 39050.4835 | 2513 | 0 |  | 1075.5 | 1311.5 | 0.1221 | 0 | 153.4188 | 0 | 0.001221 | 0 | 1.5342 | 0 | 0.001221 | 1.5342 | 129019 | 2.7608 | 129018.9988
39050.484 | 2 | 0 | 39050.484 | 2161 | 0 |  | 1117.5 | 1353.5 | 0.1221 | 0 | 131.9292 | 0 | 0.001221 | 0 | 1.3193 | 0 | 0.001221 | 1.3193 | 129019 | 19.4993 | 129018.9988
39050.4845 | 2 | 0 | 39050.4845 | 2156 | 0 |  | 1159.5 | 1395.5 | 0.1221 | 0 | 131.6239 | 0 | 0.001221 | 0 | 1.3162 | 0 | 0.001221 | 1.3162 | 129019 | 19.7764 | 129018.9988
39050.485 | 2 | 0 | 39050.485 | 2054 | 0 |  | 1201.5 | 1437.5 | 0.1221 | 0 | 125.3968 | 0 | 0.001221 | 0 | 1.254 | 0 | 0.001221 | 1.254 | 129019 | 25.7244 | 129018.9988
39050.4854 | 2 | 0 | 39050.4855 | 2254 | 0 |  | 1243.5 | 1479.5 | 0.1221 | 0 | 137.6068 | 0 | 0.001221 | 0 | 1.3761 | 0 | 0.001221 | 1.3761 | 129019 | 14.5688 | 129018.9988
39050.4859 | 2 | 0 | 39050.4859 | 2078 | 0 |  | 1285.5 | 1521.5 | 0.1221 | 0 | 126.862 | 0 | 0.001221 | 0 | 1.2686 | 0 | 0.001221 | 1.2686 | 129019 | 24.2724 | 129018.9988
39050.4864 | 2 | 0 | 39050.4864 | 2298 | 0 |  | 1327.5 | 1563.5 | 0.1221 | 0 | 140.293 | 0 | 0.001221 | 0 | 1.4029 | 0 | 0.001221 | 1.4029 | 129019 | 12.3751 | 129018.9988
39050.4869 | 2 | 0 | 39050.4869 | 1972 | 0 |  | 1369.5 | 1605.5 | 0.1221 | 0 | 120.3907 | 0 | 0.001221 | 0 | 1.2039 | 0 | 0.001221 | 1.2039 | 129019 | 30.9523 | 129018.9988
39050.4874 | 2 | 0 | 39050.4874 | 2506 | 0 |  | 1411.5 | 1647.5 | 0.1221 | 0 | 152.9915 | 0 | 0.001221 | 0 | 1.5299 | 0 | 0.001221 | 1.5299 | 129019 | 3.0479 | 129018.9988
39050.4879 | 2 | 0 | 39050.4879 | 2566 | 0 |  | 1453.5 | 1689.5 | 0.1221 | 0 | 156.6545 | 0 | 0.001221 | 0 | 1.5665 | 0 | 0.001221 | 1.5665 | 129019 | 0.63835 | 129018.9988
39050.4884 | 2 | 0 | 39050.4884 | 2212 | 0 |  | 1495.5 | 1731.5 | 0.1221 | 0 | 135.0427 | 0 | 0.001221 | 0 | 1.3504 | 0 | 0.001221 | 1.3504 | 129019 | 16.7441 | 129018.9988
39050.4888 | 2 | 0 | 39050.4889 | 2377 | 0 |  | 1537.5 | 1773.5 | 0.1221 | 0 | 145.116 | 0 | 0.001221 | 0 | 1.4512 | 0 | 0.001221 | 1.4512 | 129019 | 8.6403 | 129018.9988
39050.4893 | 2 | 0 | 39050.4893 | 2313 | 0 |  | 1579.5 | 1815.5 | 0.1221 | 0 | 141.2088 | 0 | 0.001221 | 0 | 1.4121 | 0 | 0.001221 | 1.4121 | 129019 | 11.6463 | 129018.9988
39050.4898 | 1 | 0 | 39050.4898 | 1969 | 0 |  | 1621.5 | 1857.5 | 0.06105 | 0 | 120.2076 | 0 | 0.0006105 | 0 | 1.2021 | 0 | 0.0006105 | 1.2021 | 258138 | 31.1519 | 258137.9994
39050.4903 | 1 | 0 | 39050.4903 | 2428 | 0 |  | 1663.5 | 1899.5 | 0.06105 | 0 | 148.2295 | 0 | 0.0006105 | 0 | 1.4823 | 0 | 0.0006105 | 1.4823 | 258138 | 6.3583 | 258137.9994
39050.4908 | 1 | 0 | 39050.4908 | 2467 | 0 |  | 1705.5 | 1941.5 | 0.06105 | 0 | 150.6105 | 0 | 0.0006105 | 0 | 1.5061 | 0 | 0.0006105 | 1.5061 | 258138 | 4.6769 | 258137.9994
39050.4913 | 1 | 0 | 39050.4913 | 2532 | 0 |  | 1747.5 | 1983.5 | 0.06105 | 0 | 154.5788 | 0 | 0.0006105 | 0 | 1.5458 | 0 | 0.0006105 | 1.5458 | 258138 | 1.9897 | 258137.9994
39050.4918 | 2074 | 0 | 39050.4918 | 2414 | 0 |  | 1789.5 | 2025.5 | 126.6178 | 0 | 147.3748 | 0 | 1.2662 | 0 | 1.4737 | 0 | 1.2662 | 1.4737 | 24.5121 | 6.9751 | 23.2459
39050.4922 | 2065 | 0 | 39050.4923 | 2006 | 0 |  | 1831.5 | 2067.5 | 126.0684 | 0 | 122.4664 | 0 | 1.2607 | 0 | 1.2247 | 0 | 1.2607 | 1.2247 | 25.0547 | 28.7328 | 23.794
39050.4927 | 2251 | 0 | 39050.4927 | 2561 | 0 |  | 1873.5 | 2109.5 | 137.4237 | 0 | 156.3492 | 0 | 1.3742 | 0 | 1.5635 | 0 | 1.3742 | 1.5635 | 14.7215 | 0.83483 | 13.3472
39050.4932 | 1973 | 0 | 39050.4932 | 2047 | 0 |  | 1915.5 | 2151.5 | 120.4518 | 0 | 124.9695 | 0 | 1.2045 | 0 | 1.2497 | 0 | 1.2045 | 1.2497 | 30.886 | 26.1544 | 29.6814

## A1-B4
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 154.4188 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39050.4684 | 0 | 0 | 39050.4684 | 0 | 0 |  | -229 | 7 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4689 | 0 | 0 | 39050.4689 | 0 | 0 |  | -187.5 | 48.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4694 | 0 | 0 | 39050.4694 | 0 | 0 |  | -145.5 | 90.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4698 | 0 | 0 | 39050.4699 | 0 | 0 |  | -103.5 | 132.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4703 | 0 | 0 | 39050.4704 | 0 | 0 |  | -61 | 175 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4708 | 0 | 0 | 39050.4708 | 0 | 0 |  | -19.5 | 216.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4713 | 0 | 0 | 39050.4713 | 0 | 0 |  | 22.5 | 258.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4718 | 0 | 0 | 39050.4718 | 0 | 0 |  | 64.5 | 300.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4723 | 0 | 0 | 39050.4723 | 0 | 0 |  | 106.5 | 342.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4728 | 0 | 0 | 39050.4728 | 0 | 0 |  | 148.5 | 384.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4733 | 0 | 0 | 39050.4733 | 0 | 0 |  | 190.5 | 426.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4737 | 0 | 0 | 39050.4737 | 0 | 0 |  | 232.5 | 468.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4742 | 0 | 0 | 39050.4742 | 0 | 0 |  | 274.5 | 510.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4747 | 0 | 0 | 39050.4747 | 0 | 0 |  | 316.5 | 552.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4752 | 0 | 0 | 39050.4752 | 0 | 0 |  | 358.5 | 594.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4757 | 0 | 0 | 39050.4757 | 0 | 0 |  | 400.5 | 636.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4762 | 0 | 0 | 39050.4762 | 0 | 0 |  | 442.5 | 678.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4767 | 0 | 0 | 39050.4767 | 0 | 0 |  | 484.5 | 720.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4771 | 0 | 0 | 39050.4772 | 0 | 0 |  | 526.5 | 762.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4776 | 0 | 0 | 39050.4776 | 0 | 0 |  | 568.5 | 804.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4781 | 0 | 0 | 39050.4781 | 0 | 0 |  | 610.5 | 846.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4786 | 0 | 0 | 39050.4786 | 0 | 0 |  | 652.5 | 888.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39050.4791 | 1 | 0 | 39050.4791 | 1 | 0 |  | 694.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.4796 | 1 | 0 | 39050.4796 | 1 | 0 |  | 736.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.4801 | 1 | 0 | 39050.4801 | 1 | 0 |  | 778.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.4805 | 1 | 0 | 39050.4806 | 1 | 0 |  | 820.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.481 | 1 | 0 | 39050.481 | 1 | 0 |  | 862.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.4815 | 1 | 0 | 39050.4815 | 1 | 0 |  | 904.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.482 | 1 | 0 | 39050.482 | 1 | 0 |  | 946.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.4825 | 1 | 0 | 39050.4825 | 1 | 0 |  | 988.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
39050.483 | 1 | 0 | 39050.483 | 1858 | 0 |  | 1030.5 | 1266.5 | 0.06105 | 0 | 113.431 | 0 | 0.0006105 | 0 | 1.1343 | 0 | 0.0006105 | 1.1343 | 252838 | 36.1346 | 252837.9994
39050.4835 | 2 | 0 | 39050.4835 | 2220 | 0 |  | 1072.5 | 1308.5 | 0.1221 | 0 | 135.5311 | 0 | 0.001221 | 0 | 1.3553 | 0 | 0.001221 | 1.3553 | 126369 | 13.936 | 126368.9988
39050.4839 | 2 | 0 | 39050.484 | 2233 | 0 |  | 1114.5 | 1350.5 | 0.1221 | 0 | 136.3248 | 0 | 0.001221 | 0 | 1.3632 | 0 | 0.001221 | 1.3632 | 126369 | 13.2727 | 126368.9988
39050.4844 | 2 | 0 | 39050.4844 | 2191 | 0 |  | 1156.5 | 1392.5 | 0.1221 | 0 | 133.7607 | 0 | 0.001221 | 0 | 1.3376 | 0 | 0.001221 | 1.3376 | 126369 | 15.4441 | 126368.9988
39050.4849 | 2 | 0 | 39050.4849 | 2483 | 0 |  | 1198.5 | 1434.5 | 0.1221 | 0 | 151.5873 | 0 | 0.001221 | 0 | 1.5159 | 0 | 0.001221 | 1.5159 | 126369 | 1.8679 | 126368.9988
39050.4854 | 1 | 0 | 39050.4854 | 1983 | 0 |  | 1240.5 | 1476.5 | 0.06105 | 0 | 121.0623 | 0 | 0.0006105 | 0 | 1.2106 | 0 | 0.0006105 | 1.2106 | 252838 | 27.5532 | 252837.9994
39050.4859 | 2 | 0 | 39050.4859 | 2452 | 0 |  | 1282.5 | 1518.5 | 0.1221 | 0 | 149.6947 | 0 | 0.001221 | 0 | 1.4969 | 0 | 0.001221 | 1.4969 | 126369 | 3.1558 | 126368.9988
39050.4864 | 1 | 0 | 39050.4864 | 2245 | 0 |  | 1324.5 | 1560.5 | 0.06105 | 0 | 137.0574 | 0 | 0.0006105 | 0 | 1.3706 | 0 | 0.0006105 | 1.3706 | 252838 | 12.6673 | 252837.9994
39050.4869 | 2 | 0 | 39050.4869 | 2065 | 0 |  | 1366.5 | 1602.5 | 0.1221 | 0 | 126.0684 | 0 | 0.001221 | 0 | 1.2607 | 0 | 0.001221 | 1.2607 | 126369 | 22.4881 | 126368.9988
39050.4873 | 2 | 0 | 39050.4874 | 2041 | 0 |  | 1408.5 | 1644.5 | 0.1221 | 0 | 124.6032 | 0 | 0.001221 | 0 | 1.246 | 0 | 0.001221 | 1.246 | 126369 | 23.9285 | 126368.9988
39050.4878 | 2 | 0 | 39050.4878 | 2351 | 0 |  | 1450.5 | 1686.5 | 0.1221 | 0 | 143.5287 | 0 | 0.001221 | 0 | 1.4353 | 0 | 0.001221 | 1.4353 | 126369 | 7.5874 | 126368.9988
39050.4883 | 2 | 0 | 39050.4883 | 1929 | 0 |  | 1492.5 | 1728.5 | 0.1221 | 0 | 117.7656 | 0 | 0.001221 | 0 | 1.1777 | 0 | 0.001221 | 1.1777 | 126369 | 31.1239 | 126368.9988
39050.4888 | 2 | 0 | 39050.4888 | 1998 | 0 |  | 1534.5 | 1770.5 | 0.1221 | 0 | 121.978 | 0 | 0.001221 | 0 | 1.2198 | 0 | 0.001221 | 1.2198 | 126369 | 26.5956 | 126368.9988
39050.4893 | 2 | 0 | 39050.4893 | 2025 | 0 |  | 1576.5 | 1812.5 | 0.1221 | 0 | 123.6264 | 0 | 0.001221 | 0 | 1.2363 | 0 | 0.001221 | 1.2363 | 126369 | 24.9077 | 126368.9988
39050.4898 | 2 | 0 | 39050.4898 | 2513 | 0 |  | 1618.5 | 1854.5 | 0.1221 | 0 | 153.4188 | 0 | 0.001221 | 0 | 1.5342 | 0 | 0.001221 | 1.5342 | 126369 | 0.65181 | 126368.9988
39050.4903 | 1 | 0 | 39050.4903 | 1996 | 0 |  | 1660.5 | 1896.5 | 0.06105 | 0 | 121.8559 | 0 | 0.0006105 | 0 | 1.2186 | 0 | 0.0006105 | 1.2186 | 252838 | 26.7224 | 252837.9994
39050.4908 | 2 | 0 | 39050.4908 | 2296 | 0 |  | 1702.5 | 1938.5 | 0.1221 | 0 | 140.1709 | 0 | 0.001221 | 0 | 1.4017 | 0 | 0.001221 | 1.4017 | 126369 | 10.1646 | 126368.9988
39050.4912 | 1 | 0 | 39050.4912 | 2513 | 0 |  | 1744.5 | 1980.5 | 0.06105 | 0 | 153.4188 | 0 | 0.0006105 | 0 | 1.5342 | 0 | 0.0006105 | 1.5342 | 252838 | 0.65181 | 252837.9994
39050.4917 | 969 | 0 | 39050.4917 | 2299 | 0 |  | 1786.5 | 2022.5 | 59.1575 | 0 | 140.3541 | 0 | 0.59158 | 0 | 1.4035 | 0 | 0.59158 | 1.4035 | 161.0299 | 10.0209 | 160.4384
39050.4922 | 1971 | 0 | 39050.4922 | 2075 | 0 |  | 1828.5 | 2064.5 | 120.3297 | 0 | 126.6789 | 0 | 1.2033 | 0 | 1.2668 | 0 | 1.2033 | 1.2668 | 28.3298 | 21.8978 | 27.1265
39050.4927 | 2227 | 0 | 39050.4927 | 1898 | 0 |  | 1870.5 | 2106.5 | 135.9585 | 0 | 115.873 | 0 | 1.3596 | 0 | 1.1587 | 0 | 1.3596 | 1.1587 | 13.5779 | 33.2655 | 12.2183
39050.4932 | 2334 | 0 | 39050.4932 | 2080 | 0 |  | 1912.5 | 2148.5 | 142.4908 | 0 | 126.9841 | 0 | 1.4249 | 0 | 1.2698 | 0 | 1.4249 | 1.2698 | 8.371 | 21.6048 | 6.9461

## A1-B3
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 152.8926 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39050.4684 | 0 | 0 | 39050.4684 | 0 | 0 |  | -232 | 4 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4688 | 0 | 0 | 39050.4689 | 0 | 0 |  | -190 | 46 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4693 | 0 | 0 | 39050.4694 | 0 | 0 |  | -148 | 88 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4698 | 0 | 0 | 39050.4698 | 0 | 0 |  | -106 | 130 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4703 | 0 | 0 | 39050.4703 | 0 | 0 |  | -64 | 172 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4708 | 0 | 0 | 39050.4708 | 0 | 0 |  | -22 | 214 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4713 | 0 | 0 | 39050.4713 | 0 | 0 |  | 20 | 256 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4718 | 0 | 0 | 39050.4718 | 0 | 0 |  | 62 | 298 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4722 | 0 | 0 | 39050.4723 | 0 | 0 |  | 104 | 340 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4727 | 0 | 0 | 39050.4728 | 0 | 0 |  | 146 | 382 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4732 | 0 | 0 | 39050.4732 | 0 | 0 |  | 188 | 424 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4737 | 0 | 0 | 39050.4737 | 0 | 0 |  | 230 | 466 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4742 | 0 | 0 | 39050.4742 | 0 | 0 |  | 272 | 508 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4747 | 0 | 0 | 39050.4747 | 0 | 0 |  | 314 | 550 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4752 | 0 | 0 | 39050.4752 | 0 | 0 |  | 356 | 592 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4756 | 0 | 0 | 39050.4757 | 0 | 0 |  | 398 | 634 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4761 | 0 | 0 | 39050.4762 | 0 | 0 |  | 440 | 676 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4766 | 0 | 0 | 39050.4766 | 0 | 0 |  | 482 | 718 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4771 | 0 | 0 | 39050.4771 | 0 | 0 |  | 524 | 760 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4776 | 0 | 0 | 39050.4776 | 0 | 0 |  | 566 | 802 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4781 | 0 | 0 | 39050.4781 | 0 | 0 |  | 608 | 844 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4786 | 0 | 0 | 39050.4786 | 0 | 0 |  | 650 | 886 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39050.4791 | 1 | 0 | 39050.4791 | 1 | 0 |  | 692 | 928 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39050.4795 | 2 | 0 | 39050.4796 | 2 | 0 |  | 734 | 970 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125119 | 125119 | 125118.9988
39050.48 | 1 | 0 | 39050.48 | 1 | 0 |  | 775.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39050.4805 | 1 | 0 | 39050.4805 | 1 | 0 |  | 818 | 1054 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39050.481 | 1 | 0 | 39050.481 | 1 | 0 |  | 859.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39050.4815 | 1 | 0 | 39050.4815 | 1 | 0 |  | 901.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39050.482 | 1 | 0 | 39050.482 | 1 | 0 |  | 944 | 1180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39050.4825 | 1 | 0 | 39050.4825 | 1 | 0 |  | 985.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
39050.4829 | 1 | 0 | 39050.483 | 72 | 0 |  | 1027.5 | 1263.5 | 0.06105 | 0 | 4.3956 | 0 | 0.0006105 | 0 | 0.043956 | 0 | 0.0006105 | 0.043956 | 250338 | 3378.3056 | 250337.9994
39050.4834 | 1 | 0 | 39050.4834 | 2025 | 0 |  | 1069.5 | 1305.5 | 0.06105 | 0 | 123.6264 | 0 | 0.0006105 | 0 | 1.2363 | 0 | 0.0006105 | 1.2363 | 250338 | 23.6731 | 250337.9994
39050.4839 | 2 | 0 | 39050.4839 | 2345 | 0 |  | 1112 | 1348 | 0.1221 | 0 | 143.1624 | 0 | 0.001221 | 0 | 1.4316 | 0 | 0.001221 | 1.4316 | 125119 | 6.7966 | 125118.9988
39050.4844 | 2 | 0 | 39050.4844 | 2084 | 0 |  | 1153.5 | 1389.5 | 0.1221 | 0 | 127.2283 | 0 | 0.001221 | 0 | 1.2723 | 0 | 0.001221 | 1.2723 | 125119 | 20.1718 | 125118.9988
39050.4849 | 2 | 0 | 39050.4849 | 2185 | 0 |  | 1195.5 | 1431.5 | 0.1221 | 0 | 133.3944 | 0 | 0.001221 | 0 | 1.3339 | 0 | 0.001221 | 1.3339 | 125119 | 14.6169 | 125118.9988
39050.4854 | 2 | 0 | 39050.4854 | 2471 | 0 |  | 1237.5 | 1473.5 | 0.1221 | 0 | 150.8547 | 0 | 0.001221 | 0 | 1.5085 | 0 | 0.001221 | 1.5085 | 125119 | 1.3509 | 125118.9988
39050.4859 | 1 | 0 | 39050.4859 | 2488 | 0 |  | 1279.5 | 1515.5 | 0.06105 | 0 | 151.8926 | 0 | 0.0006105 | 0 | 1.5189 | 0 | 0.0006105 | 1.5189 | 250338 | 0.65836 | 250337.9994
39050.4863 | 1 | 0 | 39050.4864 | 2409 | 0 |  | 1321.5 | 1557.5 | 0.06105 | 0 | 147.0696 | 0 | 0.0006105 | 0 | 1.4707 | 0 | 0.0006105 | 1.4707 | 250338 | 3.9593 | 250337.9994
39050.4868 | 1 | 0 | 39050.4868 | 2252 | 0 |  | 1363.5 | 1599.5 | 0.06105 | 0 | 137.4847 | 0 | 0.0006105 | 0 | 1.3748 | 0 | 0.0006105 | 1.3748 | 250338 | 11.2069 | 250337.9994
39050.4873 | 1 | 0 | 39050.4873 | 2100 | 0 |  | 1405.5 | 1641.5 | 0.06105 | 0 | 128.2051 | 0 | 0.0006105 | 0 | 1.2821 | 0 | 0.0006105 | 1.2821 | 250338 | 19.2562 | 250337.9994
39050.4878 | 1 | 0 | 39050.4878 | 2078 | 0 |  | 1447.5 | 1683.5 | 0.06105 | 0 | 126.862 | 0 | 0.0006105 | 0 | 1.2686 | 0 | 0.0006105 | 1.2686 | 250338 | 20.5188 | 250337.9994
39050.4883 | 1 | 0 | 39050.4883 | 2459 | 0 |  | 1489.5 | 1725.5 | 0.06105 | 0 | 150.1221 | 0 | 0.0006105 | 0 | 1.5012 | 0 | 0.0006105 | 1.5012 | 250338 | 1.8455 | 250337.9994
39050.4888 | 1 | 0 | 39050.4888 | 1947 | 0 |  | 1531.5 | 1767.5 | 0.06105 | 0 | 118.8645 | 0 | 0.0006105 | 0 | 1.1886 | 0 | 0.0006105 | 1.1886 | 250338 | 28.6276 | 250337.9994
39050.4893 | 2 | 0 | 39050.4893 | 2139 | 0 |  | 1573.5 | 1809.5 | 0.1221 | 0 | 130.5861 | 0 | 0.001221 | 0 | 1.3059 | 0 | 0.001221 | 1.3059 | 125119 | 17.0818 | 125118.9988
39050.4897 | 2 | 0 | 39050.4898 | 2014 | 0 |  | 1615.5 | 1851.5 | 0.1221 | 0 | 122.9548 | 0 | 0.001221 | 0 | 1.2295 | 0 | 0.001221 | 1.2295 | 125119 | 24.3486 | 125118.9988
39050.4902 | 1 | 0 | 39050.4902 | 2308 | 0 |  | 1657.5 | 1893.5 | 0.06105 | 0 | 140.9035 | 0 | 0.0006105 | 0 | 1.409 | 0 | 0.0006105 | 1.409 | 250338 | 8.5087 | 250337.9994
39050.4907 | 1 | 0 | 39050.4907 | 1947 | 0 |  | 1699.5 | 1935.5 | 0.06105 | 0 | 118.8645 | 0 | 0.0006105 | 0 | 1.1886 | 0 | 0.0006105 | 1.1886 | 250338 | 28.6276 | 250337.9994
39050.4912 | 1 | 0 | 39050.4912 | 2277 | 0 |  | 1741.5 | 1977.5 | 0.06105 | 0 | 139.011 | 0 | 0.0006105 | 0 | 1.3901 | 0 | 0.0006105 | 1.3901 | 250338 | 9.9859 | 250337.9994
39050.4917 | 340 | 0 | 39050.4917 | 2404 | 0 |  | 1783.5 | 2019.5 | 20.757 | 0 | 146.7643 | 0 | 0.20757 | 0 | 1.4676 | 0 | 0.20757 | 1.4676 | 636.5824 | 4.1755 | 636.3748
39050.4922 | 2319 | 0 | 39050.4922 | 2384 | 0 |  | 1825.5 | 2061.5 | 141.5751 | 0 | 145.5433 | 0 | 1.4158 | 0 | 1.4554 | 0 | 1.4158 | 1.4554 | 7.994 | 5.0495 | 6.5782
39050.4927 | 2006 | 0 | 39050.4927 | 2396 | 0 |  | 1867.5 | 2103.5 | 122.4664 | 0 | 146.2759 | 0 | 1.2247 | 0 | 1.4628 | 0 | 1.2247 | 1.4628 | 24.8445 | 4.5234 | 23.6198
39050.4931 | 2109 | 0 | 39050.4932 | 2349 | 0 |  | 1909.5 | 2145.5 | 128.7546 | 0 | 143.4066 | 0 | 1.2875 | 0 | 1.4341 | 0 | 1.2875 | 1.4341 | 18.7473 | 6.6147 | 17.4597

## A1-A2
Open Burn Test 14 |  |  | 2006-11-29 | 11:22 |  |  | Vs = |  | 153.6862 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 300 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39050.4683 | 0 | 0 | 39050.4683 | 0 | 0 |  | -235 | 1 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4688 | 0 | 0 | 39050.4688 | 0 | 0 |  | -192.5 | 43.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4693 | 0 | 0 | 39050.4693 | 0 | 0 |  | -151 | 85 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4698 | 0 | 0 | 39050.4698 | 0 | 0 |  | -109 | 127 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4703 | 0 | 0 | 39050.4703 | 0 | 0 |  | -67 | 169 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4708 | 0 | 0 | 39050.4708 | 0 | 0 |  | -25 | 211 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4712 | 0 | 0 | 39050.4713 | 0 | 0 |  | 17 | 253 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4717 | 0 | 0 | 39050.4717 | 0 | 0 |  | 59 | 295 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4722 | 0 | 0 | 39050.4722 | 0 | 0 |  | 101 | 337 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4727 | 0 | 0 | 39050.4727 | 0 | 0 |  | 143 | 379 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4732 | 0 | 0 | 39050.4732 | 0 | 0 |  | 185 | 421 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4737 | 0 | 0 | 39050.4737 | 0 | 0 |  | 227 | 463 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4742 | 0 | 0 | 39050.4742 | 0 | 0 |  | 269 | 505 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4746 | 0 | 0 | 39050.4747 | 0 | 0 |  | 311 | 547 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4751 | 0 | 0 | 39050.4752 | 0 | 0 |  | 353 | 589 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4756 | 0 | 0 | 39050.4756 | 0 | 0 |  | 395 | 631 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4761 | 0 | 0 | 39050.4761 | 0 | 0 |  | 437 | 673 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4766 | 0 | 0 | 39050.4766 | 0 | 0 |  | 479 | 715 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4771 | 0 | 0 | 39050.4771 | 0 | 0 |  | 521 | 757 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4776 | 0 | 0 | 39050.4776 | 0 | 0 |  | 563 | 799 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.478 | 0 | 0 | 39050.4781 | 0 | 0 |  | 605 | 841 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 503376 | 503376 | 503375.9997
39050.4785 | 1 | 0 | 39050.4786 | 0 | 0 |  | 647 | 883 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 251638 | 503376 | 251637.9994
39050.479 | 3 | 0 | 39050.479 | 2 | 0 |  | 689 | 925 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 83812.6667 | 125769 | 83812.6648
39050.4795 | 3 | 0 | 39050.4795 | 3 | 0 |  | 731 | 967 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 83812.6667 | 83812.6667 | 83812.6648
39050.48 | 3 | 0 | 39050.48 | 1 | 0 |  | 773 | 1009 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 83812.6667 | 251638 | 83812.6648
39050.4805 | 2 | 0 | 39050.4805 | 2 | 0 |  | 815 | 1051 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125769 | 125769 | 125768.9988
39050.481 | 2 | 0 | 39050.481 | 2 | 0 |  | 857 | 1093 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125769 | 125769 | 125768.9988
39050.4814 | 3 | 0 | 39050.4815 | 1 | 0 |  | 899 | 1135 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 83812.6667 | 251638 | 83812.6648
39050.4819 | 2 | 0 | 39050.482 | 2 | 0 |  | 941 | 1177 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125769 | 125769 | 125768.9988
39050.4824 | 2 | 0 | 39050.4824 | 2 | 0 |  | 983 | 1219 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125769 | 125769 | 125768.9988
39050.4829 | 3 | 0 | 39050.4829 | 2 | 0 |  | 1025 | 1261 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 83812.6667 | 125769 | 83812.6648
39050.4834 | 3 | 0 | 39050.4834 | 2 | 0 |  | 1067 | 1303 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 83812.6667 | 125769 | 83812.6648
39050.4839 | 2 | 0 | 39050.4839 | 2 | 0 |  | 1109 | 1345 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125769 | 125769 | 125768.9988
39050.4844 | 2 | 0 | 39050.4844 | 2 | 0 |  | 1151 | 1387 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125769 | 125769 | 125768.9988
39050.4848 | 2 | 0 | 39050.4849 | 1 | 0 |  | 1193 | 1429 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125769 | 251638 | 125768.9988
39050.4853 | 2 | 0 | 39050.4854 | 2 | 1 |  | 1235 | 1471 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 125769 | 251638 | 125768.9988
39050.4858 | 3 | 1 | 39050.4858 | 2 | 1 |  | 1277 | 1513 | 0.18315 | 0.06105 | 0.1221 | 0.06105 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 125743.9751 | 251738.199 | 251238.1986
39050.4863 | 4 | 2 | 39050.4863 | 3 | 2 |  | 1319 | 1555 | 0.2442 | 0.1221 | 0.18315 | 0.1221 | 0.002442 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 125718.9204 | 251838.6376 | 125519.1589
39050.4868 | 9 | 6 | 39050.4868 | 8 | 7 |  | 1361 | 1597 | 0.54945 | 0.3663 | 0.4884 | 0.42735 | 0.0054945 | 0.003663 | 0.004884 | 0.0042735 | 0.0018315 | 0.0006105 | 83678.8016 | 253054.8852 | 41689.8587
39050.4873 | 21 | 21 | 39050.4873 | 24 | 18 |  | 1403 | 1639 | 1.2821 | 1.2821 | 1.4652 | 1.0989 | 0.012821 | 0.012821 | 0.014652 | 0.010989 | 0 | 0.003663 | 4939719.0194 | 41553.8097 | 11759.225
39050.4878 | 42 | 35 | 39050.4878 | 46 | 37 |  | 1445 | 1681 | 2.5641 | 2.1368 | 2.8083 | 2.2589 | 0.025641 | 0.021368 | 0.028083 | 0.022589 | 0.0042735 | 0.0054945 | 36010.7863 | 27776.888 | 6947.5025
39050.4883 | 82 | 62 | 39050.4883 | 80 | 71 |  | 1487 | 1723 | 5.0061 | 3.7851 | 4.884 | 4.3346 | 0.050061 | 0.037851 | 0.04884 | 0.043346 | 0.01221 | 0.0054945 | 12308.7648 | 28936.5937 | 3814.8488
39050.4887 | 116 | 90 | 39050.4888 | 95 | 82 |  | 1529 | 1765 | 7.0818 | 5.4945 | 5.7998 | 5.0061 | 0.070818 | 0.054945 | 0.057998 | 0.050061 | 0.015873 | 0.0079365 | 9398.9616 | 19974.1693 | 2555.4064
39050.4892 | 145 | 121 | 39050.4892 | 150 | 134 |  | 1571 | 1807 | 8.8523 | 7.3871 | 9.1575 | 8.1807 | 0.088523 | 0.073871 | 0.091575 | 0.081807 | 0.014652 | 0.009768 | 10204.0756 | 16119.101 | 1849.1727
39050.4897 | 186 | 125 | 39050.4897 | 166 | 143 |  | 1613 | 1849 | 11.3553 | 7.6313 | 10.1343 | 8.7302 | 0.11355 | 0.076313 | 0.10134 | 0.087302 | 0.037241 | 0.014042 | 3887.3913 | 12169.7965 | 1750.7182
39050.4902 | 216 | 167 | 39050.4902 | 179 | 154 |  | 1655 | 1891 | 13.1868 | 10.1954 | 10.928 | 9.4017 | 0.13187 | 0.10195 | 0.10928 | 0.094017 | 0.029915 | 0.015263 | 4851.0057 | 10714.0302 | 1266.2532
39050.4907 | 187 | 205 | 39050.4907 | 184 | 218 |  | 1697 | 1933 | 11.4164 | 12.5153 | 11.2332 | 13.3089 | 0.11416 | 0.12515 | 0.11233 | 0.13309 | 0.010989 | 0.020757 | 15394.9265 | 7161.1332 | 1022.4924
39050.4912 | 223 | 148 | 39050.4912 | 171 | 209 |  | 1739 | 1975 | 13.6142 | 9.0354 | 10.4396 | 12.7595 | 0.13614 | 0.090354 | 0.1044 | 0.12759 | 0.045788 | 0.023199 | 3142.01 | 7484.8938 | 1431.1364
39050.4917 | 546 | 0 | 39050.4917 | 1991 | 1 |  | 1781 | 2017 | 33.3333 | 0 | 121.5507 | 0.06105 | 0.33333 | 0 | 1.2155 | 0.0006105 | 0.33333 | 1.2149 | 361.0586 | 26.5015 | 360.7253
39050.4921 | 1931 | 1 | 39050.4922 | 2465 | 1 |  | 1823 | 2059 | 117.8877 | 0.06105 | 150.4884 | 0.06105 | 1.1789 | 0.0006105 | 1.5049 | 0.0006105 | 1.1783 | 1.5043 | 31.1404 | 2.1286 | 1220.0615
39050.4926 | 2132 | 1 | 39050.4927 | 1898 | 1 |  | 1865 | 2101 | 130.1587 | 0.06105 | 115.873 | 0.06105 | 1.3016 | 0.0006105 | 1.1587 | 0.0006105 | 1.301 | 1.1581 | 18.1104 | 32.7458 | 9481.9083
39050.4931 | 2501 | 1 | 39050.4931 | 2012 | 1 |  | 1907 | 2143 | 152.6862 | 0.06105 | 122.8327 | 0.06105 | 1.5269 | 0.0006105 | 1.2283 | 0.0006105 | 1.5263 | 1.2277 | 0.65617 | 27.1914 | 328.7992

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 14 |  |  | 2006-11-29 | 11:22
39050.4683 | 0 | 0 | 1 | Mixed | 7-C | Tray G | IRMS | 2
39050.4688 | 0 | 0 | 1 |  | 300 kW |  | Bundle
39050.4693 | 0 | 0 | 1
39050.4698 | 0 | 0 | 1
39050.4703 | 0 | 0 | 1
39050.4708 | 0 | 0 | 1
39050.4712 | 0 | 0 | 1
39050.4717 | 0 | 0 | 1
39050.4722 | 0 | 0 | 1
39050.4727 | 0 | 0 | 1
39050.4732 | 0 | 0 | 1
39050.4737 | 0 | 0 | 1
39050.4742 | 0 | 0 | 1
39050.4746 | 0 | 0 | 1
39050.4751 | 0 | 0 | 1
39050.4756 | 0 | 0 | 1
39050.4761 | 0 | 0 | 1
39050.4766 | 0 | 0 | 1
39050.4771 | 0 | 0 | 1
39050.4776 | 0 | 0 | 1
39050.478 | 0 | 0 | 1
39050.4785 | 1 | 0 | 1
39050.479 | 3 | 0 | 1
39050.4795 | 3 | 0 | 1
39050.48 | 3 | 0 | 1
39050.4805 | 2 | 0 | 1
39050.481 | 2 | 0 | 1
39050.4814 | 3 | 0 | 1
39050.4819 | 2 | 0 | 1
39050.4824 | 2 | 0 | 1
39050.4829 | 3 | 0 | 1
39050.4834 | 3 | 0 | 1
39050.4839 | 2 | 0 | 1
39050.4844 | 2 | 0 | 1
39050.4848 | 2 | 0 | 1
39050.4853 | 2 | 0 | 1
39050.4858 | 3 | 1 | 1
39050.4863 | 4 | 2 | 1
39050.4868 | 9 | 6 | 1
39050.4873 | 21 | 21 | 1
39050.4878 | 42 | 35 | 1
39050.4883 | 82 | 62 | 1
39050.4887 | 116 | 90 | 1
39050.4892 | 145 | 121 | 1
39050.4897 | 186 | 125 | 1
39050.4902 | 216 | 167 | 1
39050.4907 | 187 | 205 | 1
39050.4912 | 223 | 148 | 1
39050.4917 | 546 | 0 | 1
39050.4921 | 1931 | 1 | 1
39050.4926 | 2132 | 1 | 1
39050.4931 | 2501 | 1 | 1
1
39050.4683 | 0 | 0 | 2
39050.4688 | 0 | 0 | 2
39050.4693 | 0 | 0 | 2
39050.4698 | 0 | 0 | 2
39050.4703 | 0 | 0 | 2
39050.4708 | 0 | 0 | 2
39050.4713 | 0 | 0 | 2
39050.4717 | 0 | 0 | 2
39050.4722 | 0 | 0 | 2
39050.4727 | 0 | 0 | 2
39050.4732 | 0 | 0 | 2
39050.4737 | 0 | 0 | 2
39050.4742 | 0 | 0 | 2
39050.4747 | 0 | 0 | 2
39050.4752 | 0 | 0 | 2
39050.4756 | 0 | 0 | 2
39050.4761 | 0 | 0 | 2
39050.4766 | 0 | 0 | 2
39050.4771 | 0 | 0 | 2
39050.4776 | 0 | 0 | 2
39050.4781 | 0 | 0 | 2
39050.4786 | 0 | 0 | 2
39050.479 | 2 | 0 | 2
39050.4795 | 3 | 0 | 2
39050.48 | 1 | 0 | 2
39050.4805 | 2 | 0 | 2
39050.481 | 2 | 0 | 2
39050.4815 | 1 | 0 | 2
39050.482 | 2 | 0 | 2
39050.4824 | 2 | 0 | 2
39050.4829 | 2 | 0 | 2
39050.4834 | 2 | 0 | 2
39050.4839 | 2 | 0 | 2
39050.4844 | 2 | 0 | 2
39050.4849 | 1 | 0 | 2
39050.4854 | 2 | 1 | 2
39050.4858 | 2 | 1 | 2
39050.4863 | 3 | 2 | 2
39050.4868 | 8 | 7 | 2
39050.4873 | 24 | 18 | 2
39050.4878 | 46 | 37 | 2
39050.4883 | 80 | 71 | 2
39050.4888 | 95 | 82 | 2
39050.4892 | 150 | 134 | 2
39050.4897 | 166 | 143 | 2
39050.4902 | 179 | 154 | 2
39050.4907 | 184 | 218 | 2
39050.4912 | 171 | 209 | 2
39050.4917 | 1991 | 1 | 2
39050.4922 | 2465 | 1 | 2
39050.4927 | 1898 | 1 | 2
39050.4931 | 2012 | 1 | 2
2
39050.4684 | 0 | 0 | 3
39050.4688 | 0 | 0 | 3
39050.4693 | 0 | 0 | 3
39050.4698 | 0 | 0 | 3
39050.4703 | 0 | 0 | 3
39050.4708 | 0 | 0 | 3
39050.4713 | 0 | 0 | 3
39050.4718 | 0 | 0 | 3
39050.4722 | 0 | 0 | 3
39050.4727 | 0 | 0 | 3
39050.4732 | 0 | 0 | 3
39050.4737 | 0 | 0 | 3
39050.4742 | 0 | 0 | 3
39050.4747 | 0 | 0 | 3
39050.4752 | 0 | 0 | 3
39050.4756 | 0 | 0 | 3
39050.4761 | 0 | 0 | 3
39050.4766 | 0 | 0 | 3
39050.4771 | 0 | 0 | 3
39050.4776 | 0 | 0 | 3
39050.4781 | 0 | 0 | 3
39050.4786 | 0 | 0 | 3
39050.4791 | 1 | 0 | 3
39050.4795 | 2 | 0 | 3
39050.48 | 1 | 0 | 3
39050.4805 | 1 | 0 | 3
39050.481 | 1 | 0 | 3
39050.4815 | 1 | 0 | 3
39050.482 | 1 | 0 | 3
39050.4825 | 1 | 0 | 3
39050.4829 | 1 | 0 | 3
39050.4834 | 1 | 0 | 3
39050.4839 | 2 | 0 | 3
39050.4844 | 2 | 0 | 3
39050.4849 | 2 | 0 | 3
39050.4854 | 2 | 0 | 3
39050.4859 | 1 | 0 | 3
39050.4863 | 1 | 0 | 3
39050.4868 | 1 | 0 | 3
39050.4873 | 1 | 0 | 3
39050.4878 | 1 | 0 | 3
39050.4883 | 1 | 0 | 3
39050.4888 | 1 | 0 | 3
39050.4893 | 2 | 0 | 3
39050.4897 | 2 | 0 | 3
39050.4902 | 1 | 0 | 3
39050.4907 | 1 | 0 | 3
39050.4912 | 1 | 0 | 3
39050.4917 | 340 | 0 | 3
39050.4922 | 2319 | 0 | 3
39050.4927 | 2006 | 0 | 3
39050.4931 | 2109 | 0 | 3
3
39050.4684 | 0 | 0 | 4
39050.4689 | 0 | 0 | 4
39050.4694 | 0 | 0 | 4
39050.4698 | 0 | 0 | 4
39050.4703 | 0 | 0 | 4
39050.4708 | 0 | 0 | 4
39050.4713 | 0 | 0 | 4
39050.4718 | 0 | 0 | 4
39050.4723 | 0 | 0 | 4
39050.4728 | 0 | 0 | 4
39050.4732 | 0 | 0 | 4
39050.4737 | 0 | 0 | 4
39050.4742 | 0 | 0 | 4
39050.4747 | 0 | 0 | 4
39050.4752 | 0 | 0 | 4
39050.4757 | 0 | 0 | 4
39050.4762 | 0 | 0 | 4
39050.4766 | 0 | 0 | 4
39050.4771 | 0 | 0 | 4
39050.4776 | 0 | 0 | 4
39050.4781 | 0 | 0 | 4
39050.4786 | 0 | 0 | 4
39050.4791 | 1 | 0 | 4
39050.4796 | 2 | 0 | 4
39050.48 | 1 | 0 | 4
39050.4805 | 1 | 0 | 4
39050.481 | 1 | 0 | 4
39050.4815 | 1 | 0 | 4
39050.482 | 1 | 0 | 4
39050.4825 | 1 | 0 | 4
39050.483 | 72 | 0 | 4
39050.4834 | 2025 | 0 | 4
39050.4839 | 2345 | 0 | 4
39050.4844 | 2084 | 0 | 4
39050.4849 | 2185 | 0 | 4
39050.4854 | 2471 | 0 | 4
39050.4859 | 2488 | 0 | 4
39050.4864 | 2409 | 0 | 4
39050.4868 | 2252 | 0 | 4
39050.4873 | 2100 | 0 | 4
39050.4878 | 2078 | 0 | 4
39050.4883 | 2459 | 0 | 4
39050.4888 | 1947 | 0 | 4
39050.4893 | 2139 | 0 | 4
39050.4898 | 2014 | 0 | 4
39050.4902 | 2308 | 0 | 4
39050.4907 | 1947 | 0 | 4
39050.4912 | 2277 | 0 | 4
39050.4917 | 2404 | 0 | 4
39050.4922 | 2384 | 0 | 4
39050.4927 | 2396 | 0 | 4
39050.4932 | 2349 | 0 | 4
4
39050.4684 | 0 | 0 | 5
39050.4689 | 0 | 0 | 5
39050.4694 | 0 | 0 | 5
39050.4698 | 0 | 0 | 5
39050.4703 | 0 | 0 | 5
39050.4708 | 0 | 0 | 5
39050.4713 | 0 | 0 | 5
39050.4718 | 0 | 0 | 5
39050.4723 | 0 | 0 | 5
39050.4728 | 0 | 0 | 5
39050.4733 | 0 | 0 | 5
39050.4737 | 0 | 0 | 5
39050.4742 | 0 | 0 | 5
39050.4747 | 0 | 0 | 5
39050.4752 | 0 | 0 | 5
39050.4757 | 0 | 0 | 5
39050.4762 | 0 | 0 | 5
39050.4767 | 0 | 0 | 5
39050.4771 | 0 | 0 | 5
39050.4776 | 0 | 0 | 5
39050.4781 | 0 | 0 | 5
39050.4786 | 0 | 0 | 5
39050.4791 | 1 | 0 | 5
39050.4796 | 1 | 0 | 5
39050.4801 | 1 | 0 | 5
39050.4805 | 1 | 0 | 5
39050.481 | 1 | 0 | 5
39050.4815 | 1 | 0 | 5
39050.482 | 1 | 0 | 5
39050.4825 | 1 | 0 | 5
39050.483 | 1 | 0 | 5
39050.4835 | 2 | 0 | 5
39050.4839 | 2 | 0 | 5
39050.4844 | 2 | 0 | 5
39050.4849 | 2 | 0 | 5
39050.4854 | 1 | 0 | 5
39050.4859 | 2 | 0 | 5
39050.4864 | 1 | 0 | 5
39050.4869 | 2 | 0 | 5
39050.4873 | 2 | 0 | 5
39050.4878 | 2 | 0 | 5
39050.4883 | 2 | 0 | 5
39050.4888 | 2 | 0 | 5
39050.4893 | 2 | 0 | 5
39050.4898 | 2 | 0 | 5
39050.4903 | 1 | 0 | 5
39050.4908 | 2 | 0 | 5
39050.4912 | 1 | 0 | 5
39050.4917 | 969 | 0 | 5
39050.4922 | 1971 | 0 | 5
39050.4927 | 2227 | 0 | 5
39050.4932 | 2334 | 0 | 5
5
39050.4684 | 0 | 0 | 6
39050.4689 | 0 | 0 | 6
39050.4694 | 0 | 0 | 6
39050.4699 | 0 | 0 | 6
39050.4704 | 0 | 0 | 6
39050.4708 | 0 | 0 | 6
39050.4713 | 0 | 0 | 6
39050.4718 | 0 | 0 | 6
39050.4723 | 0 | 0 | 6
39050.4728 | 0 | 0 | 6
39050.4733 | 0 | 0 | 6
39050.4737 | 0 | 0 | 6
39050.4742 | 0 | 0 | 6
39050.4747 | 0 | 0 | 6
39050.4752 | 0 | 0 | 6
39050.4757 | 0 | 0 | 6
39050.4762 | 0 | 0 | 6
39050.4767 | 0 | 0 | 6
39050.4772 | 0 | 0 | 6
39050.4776 | 0 | 0 | 6
39050.4781 | 0 | 0 | 6
39050.4786 | 0 | 0 | 6
39050.4791 | 1 | 0 | 6
39050.4796 | 1 | 0 | 6
39050.4801 | 1 | 0 | 6
39050.4806 | 1 | 0 | 6
39050.481 | 1 | 0 | 6
39050.4815 | 1 | 0 | 6
39050.482 | 1 | 0 | 6
39050.4825 | 1 | 0 | 6
39050.483 | 1858 | 0 | 6
39050.4835 | 2220 | 0 | 6
39050.484 | 2233 | 0 | 6
39050.4844 | 2191 | 0 | 6
39050.4849 | 2483 | 0 | 6
39050.4854 | 1983 | 0 | 6
39050.4859 | 2452 | 0 | 6
39050.4864 | 2245 | 0 | 6
39050.4869 | 2065 | 0 | 6
39050.4874 | 2041 | 0 | 6
39050.4878 | 2351 | 0 | 6
39050.4883 | 1929 | 0 | 6
39050.4888 | 1998 | 0 | 6
39050.4893 | 2025 | 0 | 6
39050.4898 | 2513 | 0 | 6
39050.4903 | 1996 | 0 | 6
39050.4908 | 2296 | 0 | 6
39050.4912 | 2513 | 0 | 6
39050.4917 | 2299 | 0 | 6
39050.4922 | 2075 | 0 | 6
39050.4927 | 1898 | 0 | 6
39050.4932 | 2080 | 0 | 6
6
39050.4684 | 0 | 0 | 7
39050.4689 | 0 | 0 | 7
39050.4694 | 0 | 0 | 7
39050.4699 | 0 | 0 | 7
39050.4704 | 0 | 0 | 7
39050.4709 | 0 | 0 | 7
39050.4713 | 0 | 0 | 7
39050.4718 | 0 | 0 | 7
39050.4723 | 0 | 0 | 7
39050.4728 | 0 | 0 | 7
39050.4733 | 0 | 0 | 7
39050.4738 | 0 | 0 | 7
39050.4743 | 0 | 0 | 7
39050.4747 | 0 | 0 | 7
39050.4752 | 0 | 0 | 7
39050.4757 | 0 | 0 | 7
39050.4762 | 0 | 0 | 7
39050.4767 | 0 | 0 | 7
39050.4772 | 0 | 0 | 7
39050.4777 | 0 | 0 | 7
39050.4781 | 0 | 0 | 7
39050.4786 | 0 | 0 | 7
39050.4791 | 1 | 0 | 7
39050.4796 | 1 | 0 | 7
39050.4801 | 1 | 0 | 7
39050.4806 | 1 | 0 | 7
39050.4811 | 1 | 0 | 7
39050.4816 | 1 | 0 | 7
39050.482 | 1 | 0 | 7
39050.4825 | 1 | 0 | 7
39050.483 | 1 | 0 | 7
39050.4835 | 2 | 0 | 7
39050.484 | 2 | 0 | 7
39050.4845 | 2 | 0 | 7
39050.485 | 2 | 0 | 7
39050.4854 | 2 | 0 | 7
39050.4859 | 2 | 0 | 7
39050.4864 | 2 | 0 | 7
39050.4869 | 2 | 0 | 7
39050.4874 | 2 | 0 | 7
39050.4879 | 2 | 0 | 7
39050.4884 | 2 | 0 | 7
39050.4888 | 2 | 0 | 7
39050.4893 | 2 | 0 | 7
39050.4898 | 1 | 0 | 7
39050.4903 | 1 | 0 | 7
39050.4908 | 1 | 0 | 7
39050.4913 | 1 | 0 | 7
39050.4918 | 2074 | 0 | 7
39050.4922 | 2065 | 0 | 7
39050.4927 | 2251 | 0 | 7
39050.4932 | 1973 | 0 | 7
7
39050.4684 | 0 | 0 | 8
39050.4689 | 0 | 0 | 8
39050.4694 | 0 | 0 | 8
39050.4699 | 0 | 0 | 8
39050.4704 | 0 | 0 | 8
39050.4709 | 0 | 0 | 8
39050.4714 | 0 | 0 | 8
39050.4718 | 0 | 0 | 8
39050.4723 | 0 | 0 | 8
39050.4728 | 0 | 0 | 8
39050.4733 | 0 | 0 | 8
39050.4738 | 0 | 0 | 8
39050.4743 | 0 | 0 | 8
39050.4748 | 0 | 0 | 8
39050.4752 | 0 | 0 | 8
39050.4757 | 0 | 0 | 8
39050.4762 | 0 | 0 | 8
39050.4767 | 0 | 0 | 8
39050.4772 | 0 | 0 | 8
39050.4777 | 0 | 0 | 8
39050.4782 | 0 | 0 | 8
39050.4786 | 2422 | 0 | 8
39050.4791 | 2064 | 0 | 8
39050.4796 | 2109 | 0 | 8
39050.4801 | 2343 | 0 | 8
39050.4806 | 1949 | 0 | 8
39050.4811 | 2301 | 0 | 8
39050.4816 | 2450 | 0 | 8
39050.482 | 2024 | 0 | 8
39050.4825 | 2559 | 0 | 8
39050.483 | 2330 | 0 | 8
39050.4835 | 2513 | 0 | 8
39050.484 | 2161 | 0 | 8
39050.4845 | 2156 | 0 | 8
39050.485 | 2054 | 0 | 8
39050.4855 | 2254 | 0 | 8
39050.4859 | 2078 | 0 | 8
39050.4864 | 2298 | 0 | 8
39050.4869 | 1972 | 0 | 8
39050.4874 | 2506 | 0 | 8
39050.4879 | 2566 | 0 | 8
39050.4884 | 2212 | 0 | 8
39050.4889 | 2377 | 0 | 8
39050.4893 | 2313 | 0 | 8
39050.4898 | 1969 | 0 | 8
39050.4903 | 2428 | 0 | 8
39050.4908 | 2467 | 0 | 8
39050.4913 | 2532 | 0 | 8
39050.4918 | 2414 | 0 | 8
39050.4923 | 2006 | 0 | 8
39050.4927 | 2561 | 0 | 8
39050.4932 | 2047 | 0 | 8
8
39050.4685 | 0 | 0 | 9
39050.4689 | 0 | 0 | 9
39050.4694 | 0 | 0 | 9
39050.4699 | 0 | 0 | 9
39050.4704 | 0 | 0 | 9
39050.4709 | 0 | 0 | 9
39050.4714 | 0 | 0 | 9
39050.4719 | 0 | 0 | 9
39050.4723 | 0 | 0 | 9
39050.4728 | 0 | 0 | 9
39050.4733 | 0 | 0 | 9
39050.4738 | 0 | 0 | 9
39050.4743 | 0 | 0 | 9
39050.4748 | 0 | 0 | 9
39050.4753 | 0 | 0 | 9
39050.4758 | 0 | 0 | 9
39050.4762 | 0 | 0 | 9
39050.4767 | 0 | 0 | 9
39050.4772 | 0 | 0 | 9
39050.4777 | 0 | 0 | 9
39050.4782 | 0 | 0 | 9
39050.4787 | 2 | 0 | 9
39050.4791 | 3 | 0 | 9
39050.4796 | 2 | 0 | 9
39050.4801 | 2 | 0 | 9
39050.4806 | 2 | 0 | 9
39050.4811 | 2 | 0 | 9
39050.4816 | 2 | 0 | 9
39050.4821 | 2 | 0 | 9
39050.4825 | 2 | 0 | 9
39050.483 | 2 | 0 | 9
39050.4835 | 2 | 0 | 9
39050.484 | 2 | 0 | 9
39050.4845 | 2 | 0 | 9
39050.485 | 2 | 0 | 9
39050.4855 | 2 | 0 | 9
39050.4859 | 1 | 0 | 9
39050.4864 | 2 | 0 | 9
39050.4869 | 2 | 0 | 9
39050.4874 | 2 | 0 | 9
39050.4879 | 2 | 0 | 9
39050.4884 | 2 | 0 | 9
39050.4889 | 1 | 0 | 9
39050.4894 | 2 | 0 | 9
39050.4898 | 2 | 0 | 9
39050.4903 | 1 | 0 | 9
39050.4908 | 1 | 0 | 9
39050.4913 | 2 | 0 | 9
39050.4918 | 1964 | 0 | 9
39050.4923 | 2186 | 0 | 9
39050.4928 | 2014 | 0 | 9
39050.4932 | 1911 | 0 | 9
9
39050.4685 | 0 | 0 | 10
39050.469 | 0 | 0 | 10
39050.4694 | 0 | 0 | 10
39050.4699 | 0 | 0 | 10
39050.4704 | 0 | 0 | 10
39050.4709 | 0 | 0 | 10
39050.4714 | 0 | 0 | 10
39050.4719 | 0 | 0 | 10
39050.4724 | 0 | 0 | 10
39050.4728 | 0 | 0 | 10
39050.4733 | 0 | 0 | 10
39050.4738 | 0 | 0 | 10
39050.4743 | 0 | 0 | 10
39050.4748 | 0 | 0 | 10
39050.4753 | 0 | 0 | 10
39050.4758 | 0 | 0 | 10
39050.4762 | 0 | 0 | 10
39050.4767 | 0 | 0 | 10
39050.4772 | 0 | 0 | 10
39050.4777 | 0 | 0 | 10
39050.4782 | 0 | 0 | 10
39050.4787 | 1 | 0 | 10
39050.4792 | 2535 | 0 | 10
39050.4797 | 1967 | 0 | 10
39050.4801 | 2315 | 0 | 10
39050.4806 | 2297 | 0 | 10
39050.4811 | 2189 | 0 | 10
39050.4816 | 2459 | 0 | 10
39050.4821 | 2557 | 0 | 10
39050.4826 | 2240 | 0 | 10
39050.4831 | 2118 | 0 | 10
39050.4835 | 2004 | 0 | 10
39050.484 | 2028 | 0 | 10
39050.4845 | 2563 | 0 | 10
39050.485 | 2067 | 0 | 10
39050.4855 | 2068 | 0 | 10
39050.486 | 2584 | 0 | 10
39050.4865 | 2592 | 0 | 10
39050.4869 | 2569 | 0 | 10
39050.4874 | 2234 | 0 | 10
39050.4879 | 2442 | 0 | 10
39050.4884 | 2097 | 0 | 10
39050.4889 | 2545 | 0 | 10
39050.4894 | 2141 | 0 | 10
39050.4899 | 2431 | 0 | 10
39050.4903 | 1949 | 0 | 10
39050.4908 | 2291 | 0 | 10
39050.4913 | 2123 | 0 | 10
39050.4918 | 1986 | 0 | 10
39050.4923 | 1985 | 0 | 10
39050.4928 | 2353 | 0 | 10
39050.4933 | 2261 | 0 | 10
10
39050.4685 | 0 | 0 | 11
39050.469 | 0 | 0 | 11
39050.4695 | 0 | 0 | 11
39050.4699 | 0 | 0 | 11
39050.4704 | 0 | 0 | 11
39050.4709 | 0 | 0 | 11
39050.4714 | 0 | 0 | 11
39050.4719 | 0 | 0 | 11
39050.4724 | 0 | 0 | 11
39050.4729 | 0 | 0 | 11
39050.4733 | 0 | 0 | 11
39050.4738 | 0 | 0 | 11
39050.4743 | 0 | 0 | 11
39050.4748 | 0 | 0 | 11
39050.4753 | 0 | 0 | 11
39050.4758 | 0 | 0 | 11
39050.4763 | 0 | 0 | 11
39050.4767 | 0 | 0 | 11
39050.4772 | 0 | 0 | 11
39050.4777 | 0 | 0 | 11
39050.4782 | 0 | 0 | 11
39050.4787 | 1 | 0 | 11
39050.4792 | 3 | 0 | 11
39050.4797 | 2 | 0 | 11
39050.4802 | 3 | 0 | 11
39050.4806 | 2 | 0 | 11
39050.4811 | 2 | 0 | 11
39050.4816 | 2 | 0 | 11
39050.4821 | 2 | 0 | 11
39050.4826 | 2 | 0 | 11
39050.4831 | 2 | 0 | 11
39050.4836 | 2 | 0 | 11
39050.484 | 2 | 0 | 11
39050.4845 | 2 | 0 | 11
39050.485 | 2 | 0 | 11
39050.4855 | 3 | 0 | 11
39050.486 | 2 | 0 | 11
39050.4865 | 2 | 0 | 11
39050.487 | 2 | 0 | 11
39050.4874 | 2 | 0 | 11
39050.4879 | 2 | 0 | 11
39050.4884 | 2 | 0 | 11
39050.4889 | 2 | 0 | 11
39050.4894 | 2 | 0 | 11
39050.4899 | 2 | 0 | 11
39050.4904 | 1 | 0 | 11
39050.4908 | 1 | 0 | 11
39050.4913 | 1 | 0 | 11
39050.4918 | 2393 | 0 | 11
39050.4923 | 2453 | 0 | 11
39050.4928 | 2165 | 0 | 11
39050.4933 | 2475 | 0 | 11
11
39050.4685 | 0 | 0 | 12
39050.469 | 0 | 0 | 12
39050.4695 | 0 | 0 | 12
39050.47 | 0 | 0 | 12
39050.4705 | 0 | 0 | 12
39050.4709 | 0 | 0 | 12
39050.4714 | 0 | 0 | 12
39050.4719 | 0 | 0 | 12
39050.4724 | 0 | 0 | 12
39050.4729 | 0 | 0 | 12
39050.4734 | 0 | 0 | 12
39050.4739 | 0 | 0 | 12
39050.4743 | 0 | 0 | 12
39050.4748 | 0 | 0 | 12
39050.4753 | 0 | 0 | 12
39050.4758 | 0 | 0 | 12
39050.4763 | 0 | 0 | 12
39050.4768 | 0 | 0 | 12
39050.4773 | 0 | 0 | 12
39050.4777 | 0 | 0 | 12
39050.4782 | 0 | 0 | 12
39050.4787 | 0 | 0 | 12
39050.4792 | 1 | 0 | 12
39050.4797 | 1 | 0 | 12
39050.4802 | 1 | 0 | 12
39050.4807 | 1 | 0 | 12
39050.4811 | 1 | 0 | 12
39050.4816 | 1 | 0 | 12
39050.4821 | 1 | 0 | 12
39050.4826 | 2 | 0 | 12
39050.4831 | 989 | 0 | 12
39050.4836 | 2150 | 0 | 12
39050.4841 | 1643 | 0 | 12
39050.4845 | 2081 | 0 | 12
39050.485 | 2370 | 0 | 12
39050.4855 | 1905 | 0 | 12
39050.486 | 1994 | 0 | 12
39050.4865 | 2462 | 0 | 12
39050.487 | 1970 | 0 | 12
39050.4875 | 1917 | 0 | 12
39050.488 | 2099 | 0 | 12
39050.4884 | 2491 | 0 | 12
39050.4889 | 2200 | 0 | 12
39050.4894 | 2018 | 0 | 12
39050.4899 | 2069 | 0 | 12
39050.4904 | 2322 | 0 | 12
39050.4909 | 2143 | 0 | 12
39050.4914 | 2337 | 0 | 12
39050.4918 | 1959 | 0 | 12
39050.4923 | 2485 | 0 | 12
39050.4928 | 2346 | 0 | 12
39050.4933 | 2513 | 0 | 12
12
39050.4685 | 0 | 0 | 13
39050.469 | 0 | 0 | 13
39050.4695 | 0 | 0 | 13
39050.47 | 0 | 0 | 13
39050.4705 | 0 | 0 | 13
39050.4709 | 0 | 0 | 13
39050.4714 | 0 | 0 | 13
39050.4719 | 0 | 0 | 13
39050.4724 | 0 | 0 | 13
39050.4729 | 0 | 0 | 13
39050.4734 | 0 | 0 | 13
39050.4739 | 0 | 0 | 13
39050.4744 | 0 | 0 | 13
39050.4748 | 0 | 0 | 13
39050.4753 | 0 | 0 | 13
39050.4758 | 0 | 0 | 13
39050.4763 | 0 | 0 | 13
39050.4768 | 0 | 0 | 13
39050.4773 | 0 | 0 | 13
39050.4778 | 0 | 0 | 13
39050.4782 | 0 | 0 | 13
39050.4787 | 0 | 0 | 13
39050.4792 | 1 | 0 | 13
39050.4797 | 1 | 0 | 13
39050.4802 | 1 | 0 | 13
39050.4807 | 1 | 0 | 13
39050.4812 | 1 | 0 | 13
39050.4816 | 1 | 0 | 13
39050.4821 | 1 | 0 | 13
39050.4826 | 1 | 0 | 13
39050.4831 | 1 | 0 | 13
39050.4836 | 2 | 0 | 13
39050.4841 | 2 | 0 | 13
39050.4846 | 2 | 0 | 13
39050.485 | 2 | 0 | 13
39050.4855 | 2 | 0 | 13
39050.486 | 2 | 0 | 13
39050.4865 | 1 | 0 | 13
39050.487 | 2 | 0 | 13
39050.4875 | 2 | 0 | 13
39050.488 | 2 | 0 | 13
39050.4884 | 2 | 0 | 13
39050.4889 | 1 | 0 | 13
39050.4894 | 2 | 0 | 13
39050.4899 | 2 | 0 | 13
39050.4904 | 1 | 0 | 13
39050.4909 | 1 | 0 | 13
39050.4914 | 97 | 0 | 13
39050.4919 | 2410 | 0 | 13
39050.4923 | 1900 | 0 | 13
39050.4928 | 2100 | 0 | 13
39050.4933 | 2130 | 0 | 13
13
39050.4685 | 0 | 0 | 14
39050.469 | 0 | 0 | 14
39050.4695 | 0 | 0 | 14
39050.47 | 0 | 0 | 14
39050.4705 | 0 | 0 | 14
39050.471 | 0 | 0 | 14
39050.4715 | 0 | 0 | 14
39050.4719 | 0 | 0 | 14
39050.4724 | 0 | 0 | 14
39050.4729 | 0 | 0 | 14
39050.4734 | 0 | 0 | 14
39050.4739 | 0 | 0 | 14
39050.4744 | 0 | 0 | 14
39050.4749 | 0 | 0 | 14
39050.4753 | 0 | 0 | 14
39050.4758 | 0 | 0 | 14
39050.4763 | 0 | 0 | 14
39050.4768 | 0 | 0 | 14
39050.4773 | 0 | 0 | 14
39050.4778 | 0 | 0 | 14
39050.4783 | 0 | 0 | 14
39050.4787 | 0 | 0 | 14
39050.4792 | 1 | 0 | 14
39050.4797 | 1 | 0 | 14
39050.4802 | 1 | 0 | 14
39050.4807 | 1 | 0 | 14
39050.4812 | 1 | 0 | 14
39050.4817 | 1 | 0 | 14
39050.4821 | 1 | 0 | 14
39050.4826 | 1 | 0 | 14
39050.4831 | 1 | 0 | 14
39050.4836 | 2 | 0 | 14
39050.4841 | 2 | 0 | 14
39050.4846 | 2 | 0 | 14
39050.4851 | 2 | 0 | 14
39050.4855 | 1 | 0 | 14
39050.486 | 1 | 0 | 14
39050.4865 | 2 | 0 | 14
39050.487 | 1 | 0 | 14
39050.4875 | 1 | 0 | 14
39050.488 | 2 | 0 | 14
39050.4885 | 1 | 0 | 14
39050.4889 | 1 | 0 | 14
39050.4894 | 1 | 0 | 14
39050.4899 | 1 | 0 | 14
39050.4904 | 1 | 0 | 14
39050.4909 | 1 | 0 | 14
39050.4914 | 986 | 0 | 14
39050.4919 | 1885 | 0 | 14
39050.4923 | 1929 | 0 | 14
39050.4928 | 2491 | 0 | 14
39050.4933 | 1909 | 0 | 14
14
39050.4686 | 0 | 0 | 15
39050.469 | 0 | 0 | 15
39050.4695 | 0 | 0 | 15
39050.47 | 0 | 0 | 15
39050.4705 | 0 | 0 | 15
39050.471 | 0 | 0 | 15
39050.4715 | 0 | 0 | 15
39050.472 | 0 | 0 | 15
39050.4724 | 0 | 0 | 15
39050.4729 | 0 | 0 | 15
39050.4734 | 0 | 0 | 15
39050.4739 | 0 | 0 | 15
39050.4744 | 0 | 0 | 15
39050.4749 | 0 | 0 | 15
39050.4754 | 0 | 0 | 15
39050.4758 | 0 | 0 | 15
39050.4763 | 0 | 0 | 15
39050.4768 | 0 | 0 | 15
39050.4773 | 0 | 0 | 15
39050.4778 | 0 | 0 | 15
39050.4783 | 0 | 0 | 15
39050.4788 | 0 | 0 | 15
39050.4792 | 1 | 0 | 15
39050.4797 | 1 | 0 | 15
39050.4802 | 1 | 0 | 15
39050.4807 | 1 | 0 | 15
39050.4812 | 1 | 0 | 15
39050.4817 | 1 | 0 | 15
39050.4822 | 1 | 0 | 15
39050.4827 | 1 | 0 | 15
39050.4831 | 1 | 0 | 15
39050.4836 | 1 | 0 | 15
39050.4841 | 1 | 0 | 15
39050.4846 | 1 | 0 | 15
39050.4851 | 1 | 0 | 15
39050.4856 | 1 | 0 | 15
39050.4861 | 1 | 0 | 15
39050.4865 | 2 | 0 | 15
39050.487 | 1 | 0 | 15
39050.4875 | 1 | 0 | 15
39050.488 | 1 | 0 | 15
39050.4885 | 1 | 0 | 15
39050.489 | 1 | 0 | 15
39050.4895 | 1 | 0 | 15
39050.4899 | 1 | 0 | 15
39050.4904 | 1 | 0 | 15
39050.4909 | 1 | 0 | 15
39050.4914 | 1871 | 0 | 15
39050.4919 | 2362 | 0 | 15
39050.4924 | 2170 | 0 | 15
39050.4929 | 1905 | 0 | 15
39050.4933 | 2118 | 0 | 15
15
39050.4686 | 0 | 0 | 16
39050.4691 | 0 | 0 | 16
39050.4695 | 0 | 0 | 16
39050.47 | 0 | 0 | 16
39050.4705 | 0 | 0 | 16
39050.471 | 0 | 0 | 16
39050.4715 | 0 | 0 | 16
39050.472 | 0 | 0 | 16
39050.4725 | 0 | 0 | 16
39050.4729 | 0 | 0 | 16
39050.4734 | 0 | 0 | 16
39050.4739 | 0 | 0 | 16
39050.4744 | 0 | 0 | 16
39050.4749 | 0 | 0 | 16
39050.4754 | 0 | 0 | 16
39050.4759 | 0 | 0 | 16
39050.4763 | 0 | 0 | 16
39050.4768 | 0 | 0 | 16
39050.4773 | 0 | 0 | 16
39050.4778 | 0 | 0 | 16
39050.4783 | 0 | 0 | 16
39050.4788 | 1920 | 0 | 16
39050.4793 | 2197 | 0 | 16
39050.4797 | 2363 | 0 | 16
39050.4802 | 1993 | 0 | 16
39050.4807 | 2093 | 0 | 16
39050.4812 | 1975 | 0 | 16
39050.4817 | 2352 | 0 | 16
39050.4822 | 2036 | 0 | 16
39050.4827 | 2298 | 0 | 16
39050.4831 | 2170 | 0 | 16
39050.4836 | 2516 | 0 | 16
39050.4841 | 2068 | 0 | 16
39050.4846 | 2539 | 0 | 16
39050.4851 | 2593 | 0 | 16
39050.4856 | 2619 | 0 | 16
39050.4861 | 2067 | 0 | 16
39050.4866 | 2512 | 0 | 16
39050.487 | 2061 | 0 | 16
39050.4875 | 2377 | 0 | 16
39050.488 | 2560 | 0 | 16
39050.4885 | 1938 | 0 | 16
39050.489 | 2590 | 0 | 16
39050.4895 | 2042 | 0 | 16
39050.49 | 2274 | 0 | 16
39050.4904 | 2086 | 0 | 16
39050.4909 | 2004 | 0 | 16
39050.4914 | 2378 | 0 | 16
39050.4919 | 2141 | 0 | 16
39050.4924 | 2198 | 0 | 16
39050.4929 | 2035 | 0 | 16
39050.4934 | 2101 | 0 | 16
16
39050.4686 | 0 | 0 | 17
39050.4691 | 0 | 0 | 17
39050.4696 | 0 | 0 | 17
39050.47 | 0 | 0 | 17
39050.4705 | 0 | 0 | 17
39050.471 | 0 | 0 | 17
39050.4715 | 0 | 0 | 17
39050.472 | 0 | 0 | 17
39050.4725 | 0 | 0 | 17
39050.473 | 0 | 0 | 17
39050.4734 | 0 | 0 | 17
39050.4739 | 0 | 0 | 17
39050.4744 | 0 | 0 | 17
39050.4749 | 0 | 0 | 17
39050.4754 | 0 | 0 | 17
39050.4759 | 0 | 0 | 17
39050.4764 | 0 | 0 | 17
39050.4769 | 0 | 0 | 17
39050.4773 | 0 | 0 | 17
39050.4778 | 0 | 0 | 17
39050.4783 | 1 | 2 | 17
39050.4788 | 3 | 0 | 17
39050.4793 | 2 | 0 | 17
39050.4798 | 2 | 0 | 17
39050.4803 | 2 | 0 | 17
39050.4807 | 2 | 0 | 17
39050.4812 | 2 | 0 | 17
39050.4817 | 2 | 0 | 17
39050.4822 | 2 | 0 | 17
39050.4827 | 2 | 0 | 17
39050.4832 | 2 | 0 | 17
39050.4837 | 2 | 0 | 17
39050.4841 | 2 | 0 | 17
39050.4846 | 2 | 0 | 17
39050.4851 | 2 | 0 | 17
39050.4856 | 1 | 0 | 17
39050.4861 | 2 | 0 | 17
39050.4866 | 2 | 0 | 17
39050.4871 | 2 | 0 | 17
39050.4875 | 2 | 0 | 17
39050.488 | 2 | 0 | 17
39050.4885 | 2 | 0 | 17
39050.489 | 2 | 0 | 17
39050.4895 | 2 | 0 | 17
39050.49 | 2 | 0 | 17
39050.4905 | 1 | 0 | 17
39050.4909 | 1 | 0 | 17
39050.4914 | 1889 | 0 | 17
39050.4919 | 1980 | 0 | 17
39050.4924 | 2076 | 0 | 17
39050.4929 | 1965 | 0 | 17
39050.4934 | 2307 | 0 | 17
17
39050.4686 | 0 | 0 | 18
39050.4691 | 0 | 0 | 18
39050.4696 | 0 | 0 | 18
39050.4701 | 0 | 0 | 18
39050.4705 | 0 | 0 | 18
39050.471 | 0 | 0 | 18
39050.4715 | 0 | 0 | 18
39050.472 | 0 | 0 | 18
39050.4725 | 0 | 0 | 18
39050.473 | 0 | 0 | 18
39050.4735 | 0 | 0 | 18
39050.4739 | 0 | 0 | 18
39050.4744 | 0 | 0 | 18
39050.4749 | 0 | 0 | 18
39050.4754 | 0 | 0 | 18
39050.4759 | 0 | 0 | 18
39050.4764 | 0 | 0 | 18
39050.4769 | 0 | 0 | 18
39050.4773 | 0 | 0 | 18
39050.4778 | 0 | 0 | 18
39050.4783 | 0 | 0 | 18
39050.4788 | 1 | 0 | 18
39050.4793 | 2292 | 0 | 18
39050.4798 | 2133 | 0 | 18
39050.4803 | 2374 | 0 | 18
39050.4808 | 2311 | 0 | 18
39050.4812 | 2575 | 0 | 18
39050.4817 | 2311 | 0 | 18
39050.4822 | 1969 | 0 | 18
39050.4827 | 2097 | 0 | 18
39050.4832 | 1997 | 0 | 18
39050.4837 | 2022 | 0 | 18
39050.4842 | 2174 | 0 | 18
39050.4846 | 2280 | 0 | 18
39050.4851 | 1998 | 0 | 18
39050.4856 | 2411 | 0 | 18
39050.4861 | 2203 | 0 | 18
39050.4866 | 2262 | 0 | 18
39050.4871 | 2279 | 0 | 18
39050.4876 | 2178 | 0 | 18
39050.488 | 2212 | 0 | 18
39050.4885 | 2330 | 0 | 18
39050.489 | 2494 | 0 | 18
39050.4895 | 2291 | 0 | 18
39050.49 | 2461 | 0 | 18
39050.4905 | 2144 | 0 | 18
39050.491 | 2313 | 0 | 18
39050.4914 | 2320 | 0 | 18
39050.4919 | 2089 | 0 | 18
39050.4924 | 1971 | 0 | 18
39050.4929 | 2532 | 0 | 18
39050.4934 | 2013 | 0 | 18
18
39050.4686 | 0 | 0 | 19
39050.4691 | 0 | 0 | 19
39050.4696 | 0 | 0 | 19
39050.4701 | 0 | 0 | 19
39050.4706 | 0 | 0 | 19
39050.4711 | 0 | 0 | 19
39050.4715 | 0 | 0 | 19
39050.472 | 0 | 0 | 19
39050.4725 | 0 | 0 | 19
39050.473 | 0 | 0 | 19
39050.4735 | 0 | 0 | 19
39050.474 | 0 | 0 | 19
39050.4745 | 0 | 0 | 19
39050.4749 | 0 | 0 | 19
39050.4754 | 0 | 0 | 19
39050.4759 | 0 | 0 | 19
39050.4764 | 0 | 0 | 19
39050.4769 | 0 | 0 | 19
39050.4774 | 0 | 0 | 19
39050.4779 | 0 | 0 | 19
39050.4783 | 0 | 0 | 19
39050.4788 | 1 | 0 | 19
39050.4793 | 3 | 0 | 19
39050.4798 | 3 | 0 | 19
39050.4803 | 3 | 0 | 19
39050.4808 | 2 | 0 | 19
39050.4812 | 2 | 0 | 19
39050.4817 | 2 | 0 | 19
39050.4822 | 2 | 0 | 19
39050.4827 | 2 | 0 | 19
39050.4832 | 2070 | 22 | 19
39050.4837 | 1877 | 10 | 19
39050.4842 | 1721 | 440 | 19
39050.4847 | 2349 | 14 | 19
39050.4851 | 2039 | 2 | 19
39050.4856 | 2143 | 1 | 19
39050.4861 | 1984 | 0 | 19
39050.4866 | 2055 | 0 | 19
39050.4871 | 2013 | 0 | 19
39050.4876 | 2386 | 0 | 19
39050.4881 | 2203 | 0 | 19
39050.4885 | 2484 | 0 | 19
39050.489 | 1860 | 0 | 19
39050.4895 | 1925 | 1 | 19
39050.49 | 2466 | 1 | 19
39050.4905 | 2359 | 5 | 19
39050.491 | 2457 | 0 | 19
39050.4915 | 1974 | 0 | 19
39050.4919 | 2207 | 0 | 19
39050.4924 | 2247 | 0 | 19
39050.4929 | 2496 | 1 | 19
39050.4934 | 1959 | 1 | 19
19
39050.4686 | 0 | 0 | 20
39050.4691 | 0 | 0 | 20
39050.4696 | 0 | 0 | 20
39050.4701 | 0 | 0 | 20
39050.4706 | 0 | 0 | 20
39050.4711 | 0 | 0 | 20
39050.4716 | 0 | 0 | 20
39050.472 | 0 | 0 | 20
39050.4725 | 0 | 0 | 20
39050.473 | 0 | 0 | 20
39050.4735 | 0 | 0 | 20
39050.474 | 0 | 0 | 20
39050.4745 | 0 | 0 | 20
39050.475 | 0 | 0 | 20
39050.4754 | 0 | 0 | 20
39050.4759 | 0 | 0 | 20
39050.4764 | 0 | 0 | 20
39050.4769 | 0 | 0 | 20
39050.4774 | 0 | 0 | 20
39050.4779 | 0 | 0 | 20
39050.4784 | 0 | 0 | 20
39050.4788 | 0 | 0 | 20
39050.4793 | 2 | 0 | 20
39050.4798 | 1 | 0 | 20
39050.4803 | 1 | 0 | 20
39050.4808 | 1 | 0 | 20
39050.4813 | 2 | 0 | 20
39050.4818 | 1 | 0 | 20
39050.4822 | 1 | 0 | 20
39050.4827 | 1 | 0 | 20
39050.4832 | 2453 | 4 | 20
39050.4837 | 2336 | 4 | 20
39050.4842 | 1592 | 589 | 20
39050.4847 | 1954 | 7 | 20
39050.4852 | 2499 | 1 | 20
39050.4856 | 2088 | 1 | 20
39050.4861 | 2450 | 0 | 20
39050.4866 | 2392 | 0 | 20
39050.4871 | 2253 | 0 | 20
39050.4876 | 2462 | 0 | 20
39050.4881 | 2527 | 1 | 20
39050.4886 | 2039 | 0 | 20
39050.4891 | 2439 | 1 | 20
39050.4895 | 2112 | 0 | 20
39050.49 | 2486 | 0 | 20
39050.4905 | 1954 | 3 | 20
39050.491 | 2400 | 0 | 20
39050.4915 | 2453 | 0 | 20
39050.492 | 2460 | 0 | 20
39050.4925 | 1933 | 1 | 20
39050.4929 | 1944 | 4 | 20
39050.4934 | 2039 | 1 | 20
20
39050.4687 | 0 | 0 | 21
39050.4691 | 0 | 0 | 21
39050.4696 | 0 | 0 | 21
39050.4701 | 0 | 0 | 21
39050.4706 | 0 | 0 | 21
39050.4711 | 0 | 0 | 21
39050.4716 | 0 | 0 | 21
39050.472 | 0 | 0 | 21
39050.4725 | 0 | 0 | 21
39050.473 | 0 | 0 | 21
39050.4735 | 0 | 0 | 21
39050.474 | 0 | 0 | 21
39050.4745 | 0 | 0 | 21
39050.475 | 0 | 0 | 21
39050.4755 | 0 | 0 | 21
39050.4759 | 0 | 0 | 21
39050.4764 | 0 | 0 | 21
39050.4769 | 0 | 0 | 21
39050.4774 | 0 | 0 | 21
39050.4779 | 0 | 0 | 21
39050.4784 | 0 | 0 | 21
39050.4789 | 0 | 0 | 21
39050.4793 | 1 | 0 | 21
39050.4798 | 1 | 0 | 21
39050.4803 | 1 | 0 | 21
39050.4808 | 1 | 0 | 21
39050.4813 | 1 | 0 | 21
39050.4818 | 1 | 0 | 21
39050.4823 | 1 | 0 | 21
39050.4827 | 1 | 0 | 21
39050.4832 | 1997 | 0 | 21
39050.4837 | 1451 | 0 | 21
39050.4842 | 2037 | 0 | 21
39050.4847 | 1889 | 0 | 21
39050.4852 | 2092 | 0 | 21
39050.4857 | 2010 | 0 | 21
39050.4861 | 2410 | 0 | 21
39050.4866 | 1927 | 0 | 21
39050.4871 | 2027 | 0 | 21
39050.4876 | 2034 | 0 | 21
39050.4881 | 1995 | 0 | 21
39050.4886 | 1834 | 0 | 21
39050.4891 | 1965 | 0 | 21
39050.4895 | 2085 | 0 | 21
39050.49 | 2243 | 0 | 21
39050.4905 | 1811 | 0 | 21
39050.491 | 2100 | 0 | 21
39050.4915 | 2480 | 0 | 21
39050.492 | 2231 | 0 | 21
39050.4925 | 2508 | 0 | 21
39050.493 | 2378 | 0 | 21
39050.4934 | 2041 | 0 | 21
21
39050.4687 | 0 | 0 | 22
39050.4692 | 0 | 0 | 22
39050.4696 | 0 | 0 | 22
39050.4701 | 0 | 0 | 22
39050.4706 | 0 | 0 | 22
39050.4711 | 0 | 0 | 22
39050.4716 | 0 | 0 | 22
39050.4721 | 0 | 0 | 22
39050.4726 | 0 | 0 | 22
39050.4735 | 0 | 0 | 22
39050.474 | 0 | 0 | 22
39050.4745 | 0 | 0 | 22
39050.475 | 0 | 0 | 22
39050.4755 | 0 | 0 | 22
39050.476 | 0 | 0 | 22
39050.4764 | 0 | 0 | 22
39050.4769 | 0 | 0 | 22
39050.4774 | 0 | 0 | 22
39050.4779 | 0 | 0 | 22
39050.4784 | 0 | 0 | 22
39050.4789 | 2506 | 0 | 22
39050.4794 | 2420 | 0 | 22
39050.4798 | 2213 | 0 | 22
39050.4803 | 1956 | 0 | 22
39050.4808 | 2152 | 0 | 22
39050.4813 | 2166 | 0 | 22
39050.4818 | 2437 | 0 | 22
39050.4823 | 2573 | 0 | 22
39050.4828 | 1952 | 0 | 22
39050.4833 | 1981 | 0 | 22
39050.4837 | 2555 | 0 | 22
39050.4842 | 2007 | 0 | 22
39050.4847 | 2424 | 0 | 22
39050.4852 | 2589 | 0 | 22
39050.4857 | 2015 | 0 | 22
39050.4862 | 2394 | 0 | 22
39050.4867 | 2548 | 0 | 22
39050.4871 | 2571 | 0 | 22
39050.4876 | 2327 | 0 | 22
39050.4881 | 2463 | 0 | 22
39050.4886 | 2275 | 0 | 22
39050.4891 | 2115 | 0 | 22
39050.4896 | 1974 | 0 | 22
39050.4901 | 2355 | 0 | 22
39050.4905 | 2348 | 0 | 22
39050.491 | 2236 | 0 | 22
39050.4915 | 2578 | 0 | 22
39050.492 | 2022 | 0 | 22
39050.4925 | 2122 | 0 | 22
39050.493 | 2505 | 0 | 22
39050.4935 | 2176 | 0 | 22
22
39050.4687 | 0 | 0 | 23
39050.4692 | 0 | 0 | 23
39050.4697 | 0 | 0 | 23
39050.4701 | 0 | 0 | 23
39050.4706 | 0 | 0 | 23
39050.4711 | 0 | 0 | 23
39050.4716 | 0 | 0 | 23
39050.4721 | 0 | 0 | 23
39050.4726 | 0 | 0 | 23
39050.4731 | 0 | 0 | 23
39050.4735 | 0 | 0 | 23
39050.474 | 0 | 0 | 23
39050.4745 | 0 | 0 | 23
39050.475 | 0 | 0 | 23
39050.4755 | 0 | 0 | 23
39050.476 | 0 | 0 | 23
39050.4765 | 0 | 0 | 23
39050.4769 | 0 | 0 | 23
39050.4774 | 0 | 0 | 23
39050.4779 | 0 | 0 | 23
39050.4784 | 0 | 0 | 23
39050.4789 | 3 | 0 | 23
39050.4794 | 2 | 0 | 23
39050.4799 | 2 | 0 | 23
39050.4803 | 2 | 0 | 23
39050.4808 | 2 | 0 | 23
39050.4813 | 2 | 0 | 23
39050.4818 | 1 | 0 | 23
39050.4823 | 2 | 0 | 23
39050.4828 | 2 | 0 | 23
39050.4833 | 1899 | 0 | 23
39050.4837 | 1690 | 0 | 23
39050.4842 | 1467 | 0 | 23
39050.4847 | 2011 | 0 | 23
39050.4852 | 1921 | 0 | 23
39050.4857 | 2276 | 0 | 23
39050.4862 | 2175 | 0 | 23
39050.4867 | 2415 | 0 | 23
39050.4872 | 1926 | 0 | 23
39050.4876 | 2003 | 0 | 23
39050.4881 | 2180 | 0 | 23
39050.4886 | 2256 | 0 | 23
39050.4891 | 2229 | 0 | 23
39050.4896 | 1884 | 0 | 23
39050.4901 | 1805 | 0 | 23
39050.4906 | 2414 | 0 | 23
39050.491 | 2179 | 0 | 23
39050.4915 | 2176 | 0 | 23
39050.492 | 2049 | 0 | 23
39050.4925 | 2465 | 0 | 23
39050.493 | 2464 | 0 | 23
39050.4935 | 2103 | 0 | 23
23
39050.4687 | 0 | 0 | 24
39050.4692 | 0 | 0 | 24
39050.4697 | 0 | 0 | 24
39050.4702 | 0 | 0 | 24
39050.4706 | 0 | 0 | 24
39050.4711 | 0 | 0 | 24
39050.4716 | 0 | 0 | 24
39050.4721 | 0 | 0 | 24
39050.4726 | 0 | 0 | 24
39050.4731 | 0 | 0 | 24
39050.4736 | 0 | 0 | 24
39050.4741 | 0 | 0 | 24
39050.4745 | 0 | 0 | 24
39050.475 | 0 | 0 | 24
39050.4755 | 0 | 0 | 24
39050.476 | 0 | 0 | 24
39050.4765 | 0 | 0 | 24
39050.477 | 0 | 0 | 24
39050.4775 | 0 | 0 | 24
39050.4779 | 0 | 0 | 24
39050.4784 | 0 | 0 | 24
39050.4789 | 1 | 0 | 24
39050.4794 | 2247 | 0 | 24
39050.4799 | 2110 | 0 | 24
39050.4804 | 2083 | 0 | 24
39050.4809 | 2564 | 0 | 24
39050.4813 | 2556 | 0 | 24
39050.4818 | 2065 | 0 | 24
39050.4823 | 2502 | 0 | 24
39050.4828 | 2091 | 0 | 24
39050.4833 | 1939 | 0 | 24
39050.4838 | 2009 | 0 | 24
39050.4843 | 2372 | 0 | 24
39050.4847 | 2205 | 0 | 24
39050.4852 | 2257 | 0 | 24
39050.4857 | 2074 | 0 | 24
39050.4862 | 2145 | 0 | 24
39050.4867 | 2196 | 0 | 24
39050.4872 | 2308 | 0 | 24
39050.4877 | 2544 | 0 | 24
39050.4881 | 2276 | 0 | 24
39050.4886 | 2528 | 0 | 24
39050.4891 | 1898 | 0 | 24
39050.4896 | 2185 | 0 | 24
39050.4901 | 2052 | 0 | 24
39050.4906 | 2097 | 0 | 24
39050.4911 | 2097 | 0 | 24
39050.4915 | 2408 | 0 | 24
39050.492 | 2446 | 0 | 24
39050.4925 | 2278 | 0 | 24
39050.493 | 2573 | 0 | 24
39050.4935 | 2522 | 0 | 24
24
39050.4687 | 0 | 0 | 25
39050.4692 | 0 | 0 | 25
39050.4697 | 0 | 0 | 25
39050.4702 | 0 | 0 | 25
39050.4707 | 0 | 0 | 25
39050.4711 | 0 | 0 | 25
39050.4716 | 0 | 0 | 25
39050.4721 | 0 | 0 | 25
39050.4726 | 0 | 0 | 25
39050.4731 | 0 | 0 | 25
39050.4736 | 0 | 0 | 25
39050.4741 | 0 | 0 | 25
39050.4745 | 0 | 0 | 25
39050.475 | 0 | 0 | 25
39050.4755 | 0 | 0 | 25
39050.476 | 0 | 0 | 25
39050.4765 | 0 | 0 | 25
39050.477 | 0 | 0 | 25
39050.4775 | 0 | 0 | 25
39050.478 | 0 | 0 | 25
39050.4784 | 0 | 0 | 25
39050.4789 | 1 | 0 | 25
39050.4794 | 2 | 0 | 25
39050.4799 | 3 | 0 | 25
39050.4804 | 2 | 0 | 25
39050.4809 | 2 | 0 | 25
39050.4814 | 2 | 0 | 25
39050.4818 | 2 | 0 | 25
39050.4823 | 2 | 0 | 25
39050.4828 | 2 | 0 | 25
39050.4833 | 2438 | 0 | 25
39050.4838 | 2097 | 0 | 25
39050.4843 | 2023 | 0 | 25
39050.4848 | 2043 | 0 | 25
39050.4852 | 2470 | 0 | 25
39050.4857 | 2034 | 0 | 25
39050.4862 | 2491 | 0 | 25
39050.4867 | 1989 | 0 | 25
39050.4872 | 2138 | 0 | 25
39050.4877 | 1995 | 0 | 25
39050.4882 | 1961 | 0 | 25
39050.4886 | 2489 | 0 | 25
39050.4891 | 1969 | 0 | 25
39050.4896 | 2500 | 0 | 25
39050.4901 | 1969 | 0 | 25
39050.4906 | 2484 | 0 | 25
39050.4911 | 2520 | 0 | 25
39050.4916 | 2289 | 0 | 25
39050.492 | 1935 | 0 | 25
39050.4925 | 2283 | 0 | 25
39050.493 | 1974 | 0 | 25
39050.4935 | 1844 | 0 | 25
25
39050.4687 | 0 | 0 | 26
39050.4692 | 0 | 0 | 26
39050.4697 | 0 | 0 | 26
39050.4702 | 0 | 0 | 26
39050.4707 | 0 | 0 | 26
39050.4712 | 0 | 0 | 26
39050.4716 | 0 | 0 | 26
39050.4721 | 0 | 0 | 26
39050.4726 | 0 | 0 | 26
39050.4731 | 0 | 0 | 26
39050.4736 | 0 | 0 | 26
39050.4741 | 0 | 0 | 26
39050.4746 | 0 | 0 | 26
39050.475 | 0 | 0 | 26
39050.4755 | 0 | 0 | 26
39050.476 | 0 | 0 | 26
39050.4765 | 0 | 0 | 26
39050.477 | 0 | 0 | 26
39050.4775 | 0 | 0 | 26
39050.478 | 0 | 0 | 26
39050.4784 | 0 | 0 | 26
39050.4789 | 2098 | 0 | 26
39050.4794 | 2506 | 0 | 26
39050.4799 | 1957 | 0 | 26
39050.4804 | 2064 | 0 | 26
39050.4809 | 2175 | 0 | 26
39050.4814 | 2414 | 0 | 26
39050.4819 | 1977 | 0 | 26
39050.4823 | 2310 | 0 | 26
39050.4828 | 2131 | 0 | 26
39050.4833 | 2481 | 0 | 26
39050.4838 | 2282 | 0 | 26
39050.4843 | 2156 | 0 | 26
39050.4848 | 2040 | 0 | 26
39050.4853 | 2542 | 0 | 26
39050.4857 | 2090 | 0 | 26
39050.4862 | 2366 | 0 | 26
39050.4867 | 2048 | 0 | 26
39050.4872 | 2539 | 0 | 26
39050.4877 | 2354 | 0 | 26
39050.4882 | 2120 | 0 | 26
39050.4887 | 2023 | 0 | 26
39050.4891 | 1918 | 0 | 26
39050.4896 | 2387 | 0 | 26
39050.4901 | 2559 | 0 | 26
39050.4906 | 2093 | 0 | 26
39050.4911 | 2490 | 0 | 26
39050.4916 | 1978 | 0 | 26
39050.4921 | 2587 | 0 | 26
39050.4925 | 2276 | 0 | 26
39050.493 | 2299 | 0 | 26
39050.4935 | 2112 | 0 | 26
26
39050.4688 | 0 | 0 | 27
39050.4692 | 0 | 0 | 27
39050.4697 | 0 | 0 | 27
39050.4702 | 0 | 0 | 27
39050.4707 | 0 | 0 | 27
39050.4712 | 0 | 0 | 27
39050.4717 | 0 | 0 | 27
39050.4722 | 0 | 0 | 27
39050.4726 | 0 | 0 | 27
39050.4731 | 0 | 0 | 27
39050.4736 | 0 | 0 | 27
39050.4741 | 0 | 0 | 27
39050.4746 | 0 | 0 | 27
39050.4751 | 0 | 0 | 27
39050.4756 | 0 | 0 | 27
39050.476 | 0 | 0 | 27
39050.4765 | 0 | 0 | 27
39050.477 | 0 | 0 | 27
39050.4775 | 0 | 0 | 27
39050.478 | 0 | 0 | 27
39050.4785 | 0 | 0 | 27
39050.479 | 3 | 0 | 27
39050.4794 | 3 | 0 | 27
39050.4799 | 3 | 0 | 27
39050.4804 | 2 | 0 | 27
39050.4809 | 2 | 0 | 27
39050.4814 | 2 | 0 | 27
39050.4819 | 2 | 0 | 27
39050.4824 | 2 | 0 | 27
39050.4828 | 549 | 0 | 27
39050.4833 | 1868 | 0 | 27
39050.4838 | 2422 | 0 | 27
39050.4843 | 1889 | 0 | 27
39050.4848 | 2276 | 0 | 27
39050.4853 | 2105 | 0 | 27
39050.4858 | 2527 | 0 | 27
39050.4863 | 2427 | 0 | 27
39050.4867 | 2288 | 0 | 27
39050.4872 | 2504 | 0 | 27
39050.4877 | 2252 | 0 | 27
39050.4882 | 2265 | 0 | 27
39050.4887 | 2174 | 0 | 27
39050.4892 | 1919 | 0 | 27
39050.4897 | 1935 | 0 | 27
39050.4901 | 2264 | 0 | 27
39050.4906 | 2328 | 0 | 27
39050.4911 | 2391 | 0 | 27
39050.4916 | 2524 | 0 | 27
39050.4921 | 2517 | 0 | 27
39050.4926 | 1946 | 0 | 27
39050.4931 | 1894 | 0 | 27
39050.4935 | 2267 | 0 | 27
27
39050.4688 | 0 | 0 | 28
39050.4692 | 0 | 0 | 28
39050.4697 | 0 | 0 | 28
39050.4702 | 0 | 0 | 28
39050.4707 | 0 | 0 | 28
39050.4712 | 0 | 0 | 28
39050.4717 | 0 | 0 | 28
39050.4722 | 0 | 0 | 28
39050.4727 | 0 | 0 | 28
39050.4731 | 0 | 0 | 28
39050.4736 | 0 | 0 | 28
39050.4741 | 0 | 0 | 28
39050.4746 | 0 | 0 | 28
39050.4751 | 0 | 0 | 28
39050.4756 | 0 | 0 | 28
39050.4761 | 0 | 0 | 28
39050.4765 | 0 | 0 | 28
39050.477 | 0 | 0 | 28
39050.4775 | 0 | 0 | 28
39050.478 | 0 | 0 | 28
39050.4785 | 0 | 0 | 28
39050.479 | 1 | 0 | 28
39050.4795 | 1978 | 0 | 28
39050.4799 | 2548 | 0 | 28
39050.4804 | 2252 | 0 | 28
39050.4809 | 2230 | 0 | 28
39050.4814 | 2464 | 0 | 28
39050.4819 | 2608 | 0 | 28
39050.4824 | 2542 | 0 | 28
39050.4829 | 2452 | 0 | 28
39050.4833 | 1934 | 0 | 28
39050.4838 | 2548 | 0 | 28
39050.4843 | 2115 | 0 | 28
39050.4848 | 2595 | 0 | 28
39050.4853 | 2532 | 0 | 28
39050.4858 | 2155 | 0 | 28
39050.4863 | 2570 | 0 | 28
39050.4867 | 2247 | 0 | 28
39050.4872 | 1962 | 0 | 28
39050.4877 | 2509 | 0 | 28
39050.4882 | 2362 | 0 | 28
39050.4887 | 1953 | 0 | 28
39050.4892 | 1965 | 0 | 28
39050.4897 | 2542 | 0 | 28
39050.4902 | 2203 | 0 | 28
39050.4906 | 2390 | 0 | 28
39050.4911 | 2508 | 0 | 28
39050.4916 | 2168 | 0 | 28
39050.4921 | 2389 | 0 | 28
39050.4926 | 2559 | 0 | 28
39050.4931 | 2115 | 0 | 28
39050.4936 | 2603 | 0 | 28
28
39050.4688 | 0 | 0 | 29
39050.4693 | 0 | 0 | 29
39050.4698 | 0 | 0 | 29
39050.4702 | 0 | 0 | 29
39050.4707 | 0 | 0 | 29
39050.4712 | 0 | 0 | 29
39050.4717 | 0 | 0 | 29
39050.4722 | 0 | 0 | 29
39050.4727 | 0 | 0 | 29
39050.4732 | 0 | 0 | 29
39050.4736 | 0 | 0 | 29
39050.4741 | 0 | 0 | 29
39050.4746 | 0 | 0 | 29
39050.4751 | 0 | 0 | 29
39050.4756 | 0 | 0 | 29
39050.4761 | 0 | 0 | 29
39050.4766 | 0 | 0 | 29
39050.477 | 0 | 0 | 29
39050.4775 | 0 | 0 | 29
39050.478 | 0 | 0 | 29
39050.4785 | 2210 | 0 | 29
39050.479 | 1943 | 0 | 29
39050.4795 | 2463 | 0 | 29
39050.48 | 2186 | 0 | 29
39050.4804 | 2072 | 0 | 29
39050.4809 | 2488 | 0 | 29
39050.4814 | 2235 | 0 | 29
39050.4819 | 2462 | 0 | 29
39050.4824 | 2423 | 0 | 29
39050.4829 | 2162 | 0 | 29
39050.4834 | 2139 | 0 | 29
39050.4838 | 1955 | 0 | 29
39050.4843 | 2535 | 0 | 29
39050.4848 | 2168 | 0 | 29
39050.4853 | 2183 | 0 | 29
39050.4858 | 2608 | 0 | 29
39050.4863 | 2062 | 0 | 29
39050.4868 | 2550 | 0 | 29
39050.4872 | 2067 | 0 | 29
39050.4877 | 2467 | 0 | 29
39050.4882 | 2595 | 0 | 29
39050.4887 | 2534 | 0 | 29
39050.4892 | 2419 | 0 | 29
39050.4897 | 2242 | 0 | 29
39050.4902 | 2031 | 0 | 29
39050.4906 | 1994 | 0 | 29
39050.4911 | 1927 | 0 | 29
39050.4916 | 2307 | 0 | 29
39050.4921 | 2490 | 0 | 29
39050.4926 | 2089 | 0 | 29
39050.4931 | 2130 | 0 | 29
39050.4936 | 1998 | 0 | 29
29
39050.4688 | 0 | 0 | 30
39050.4693 | 0 | 0 | 30
39050.4698 | 0 | 0 | 30
39050.4703 | 0 | 0 | 30
39050.4707 | 0 | 0 | 30
39050.4712 | 0 | 0 | 30
39050.4717 | 0 | 0 | 30
39050.4722 | 0 | 0 | 30
39050.4727 | 0 | 0 | 30
39050.4732 | 0 | 0 | 30
39050.4737 | 0 | 0 | 30
39050.4741 | 0 | 0 | 30
39050.4746 | 0 | 0 | 30
39050.4751 | 0 | 0 | 30
39050.4756 | 0 | 0 | 30
39050.4761 | 0 | 0 | 30
39050.4766 | 0 | 0 | 30
39050.4771 | 0 | 0 | 30
39050.4775 | 0 | 0 | 30
39050.478 | 0 | 0 | 30
39050.4785 | 2 | 0 | 30
39050.479 | 1709 | 0 | 30
39050.4795 | 2163 | 0 | 30
39050.48 | 2281 | 0 | 30
39050.4805 | 2502 | 0 | 30
39050.4809 | 2089 | 0 | 30
39050.4814 | 1951 | 0 | 30
39050.4819 | 2442 | 0 | 30
39050.4824 | 2488 | 0 | 30
39050.4829 | 2533 | 0 | 30
39050.4834 | 2542 | 0 | 30
39050.4839 | 2260 | 0 | 30
39050.4844 | 2015 | 0 | 30
39050.4848 | 2607 | 0 | 30
39050.4853 | 2594 | 0 | 30
39050.4858 | 2058 | 0 | 30
39050.4863 | 2419 | 0 | 30
39050.4868 | 2112 | 0 | 30
39050.4873 | 2505 | 0 | 30
39050.4878 | 2219 | 0 | 30
39050.4882 | 2037 | 0 | 30
39050.4887 | 1948 | 0 | 30
39050.4892 | 2516 | 0 | 30
39050.4897 | 2402 | 0 | 30
39050.4902 | 1963 | 0 | 30
39050.4907 | 2569 | 0 | 30
39050.4912 | 2038 | 0 | 30
39050.4916 | 2276 | 0 | 30
39050.4921 | 2556 | 0 | 30
39050.4926 | 2280 | 0 | 30
39050.4931 | 2515 | 0 | 30
39050.4936 | 2168 | 0 | 30
30

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above | Air below | Intra-bundle | TRAY G
0 | -236 | 11.8 | 11 | 10.2 | 12.1 | 9.9
1 | -235 | 11.7 | 11 | 10.2 | 12.1 | 9.9
2 | -234 | 11.7 | 11 | 10.2 | 12.1 | 9.9
3 | -233 | 11.8 | 11 | 10.2 | 12.1 | 9.9
4 | -232 | 11.8 | 11 | 10.2 | 12.1 | 9.9
5 | -231 | 11.8 | 11 | 10.2 | 12.1 | 9.9
6 | -230 | 11.8 | 11 | 10.2 | 12.1 | 9.9
7 | -229 | 11.8 | 11 | 10.2 | 12.1 | 10
8 | -228 | 11.8 | 11 | 10.2 | 12.1 | 9.9
9 | -227 | 11.7 | 11 | 10.2 | 12.1 | 9.9
10 | -226 | 11.8 | 11 | 10.2 | 12.1 | 9.9
11 | -225 | 11.7 | 11 | 10.2 | 12.1 | 9.9
12 | -224 | 11.7 | 11 | 10.2 | 12.1 | 9.9
13 | -223 | 11.7 | 11 | 10.2 | 12.1 | 9.9
14 | -222 | 11.7 | 11 | 10.2 | 12.1 | 9.9
15 | -221 | 11.7 | 11 | 10.2 | 12.1 | 9.9
16 | -220 | 11.7 | 11 | 10.2 | 12.1 | 9.9
17 | -219 | 11.7 | 11 | 10.2 | 12.1 | 9.9
18 | -218 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
19 | -217 | 11.8 | 11.1 | 10.2 | 12.1 | 9.9
20 | -216 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
21 | -215 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
22 | -214 | 11.8 | 11.1 | 10.2 | 12.1 | 9.9
23 | -213 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
24 | -212 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
25 | -211 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
26 | -210 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
27 | -209 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
28 | -208 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
29 | -207 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
30 | -206 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
31 | -205 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
32 | -204 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
33 | -203 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
34 | -202 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
35 | -201 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
36 | -200 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
37 | -199 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
38 | -198 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
39 | -197 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
40 | -196 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
41 | -195 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
42 | -194 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
43 | -193 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
44 | -192 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
45 | -191 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
46 | -190 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
47 | -189 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
48 | -188 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
49 | -187 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
50 | -186 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
51 | -185 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
52 | -184 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
53 | -183 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
54 | -182 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
55 | -181 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
56 | -180 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
57 | -179 | 11.7 | 11.1 | 10.2 | 12.1 | 10
58 | -178 | 11.7 | 11.1 | 10.3 | 12.1 | 9.9
59 | -177 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
60 | -176 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
61 | -175 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
62 | -174 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
63 | -173 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
64 | -172 | 11.7 | 11.1 | 10.2 | 12.1 | 10
65 | -171 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
66 | -170 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
67 | -169 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
68 | -168 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
69 | -167 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
70 | -166 | 11.7 | 11.1 | 10.2 | 12.1 | 10
71 | -165 | 11.7 | 11.1 | 10.2 | 12.1 | 10
72 | -164 | 11.7 | 11.1 | 10.2 | 12.1 | 10
73 | -163 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
74 | -162 | 11.7 | 11.1 | 10.2 | 12.1 | 10
75 | -161 | 11.7 | 11.1 | 10.2 | 12.1 | 10
76 | -160 | 11.7 | 11.1 | 10.2 | 12.1 | 10
77 | -159 | 11.7 | 11.1 | 10.2 | 12.1 | 10
78 | -158 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
79 | -157 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
80 | -156 | 11.7 | 11.1 | 10.2 | 12.1 | 10
81 | -155 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
82 | -154 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
83 | -153 | 11.7 | 11.1 | 10.1 | 12.1 | 10
84 | -152 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
85 | -151 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
86 | -150 | 11.7 | 11 | 10.1 | 12.1 | 9.9
87 | -149 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
88 | -148 | 11.7 | 11.1 | 10.1 | 12.1 | 10
89 | -147 | 11.7 | 11 | 10.1 | 12.1 | 9.9
90 | -146 | 11.7 | 11 | 10 | 12.1 | 9.9
91 | -145 | 11.7 | 11 | 10 | 12.1 | 9.9
92 | -144 | 11.7 | 11 | 10 | 12.1 | 10
93 | -143 | 11.7 | 11 | 10 | 12.1 | 9.9
94 | -142 | 11.7 | 11 | 10.1 | 12.1 | 9.9
95 | -141 | 11.7 | 11 | 10.1 | 12.1 | 10
96 | -140 | 11.7 | 11 | 10.1 | 12.1 | 10
97 | -139 | 11.7 | 11 | 10.1 | 12.1 | 10
98 | -138 | 11.7 | 11 | 10.1 | 12.1 | 9.9
99 | -137 | 11.7 | 11 | 10.1 | 12.1 | 10
100 | -136 | 11.7 | 11 | 10.2 | 12.1 | 10
101 | -135 | 11.7 | 11 | 10.2 | 12.1 | 10
102 | -134 | 11.7 | 11 | 10.2 | 12.1 | 10
103 | -133 | 11.7 | 11 | 10.2 | 12.1 | 10
104 | -132 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
105 | -131 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
106 | -130 | 11.7 | 11.1 | 10.2 | 12.1 | 10
107 | -129 | 11.7 | 11.1 | 10.2 | 12.1 | 10
108 | -128 | 11.7 | 11.1 | 10.2 | 12.1 | 10
109 | -127 | 11.7 | 11 | 10.2 | 12.1 | 10
110 | -126 | 11.7 | 11 | 10.2 | 12.1 | 10
111 | -125 | 11.7 | 11 | 10.2 | 12.1 | 10
112 | -124 | 11.7 | 11 | 10.2 | 12.1 | 10
113 | -123 | 11.7 | 11 | 10.2 | 12.1 | 10
114 | -122 | 11.7 | 11 | 10.2 | 12.1 | 10
115 | -121 | 11.7 | 11 | 10.2 | 12.1 | 10
116 | -120 | 11.7 | 11.1 | 10.2 | 12.1 | 10
117 | -119 | 11.7 | 11.1 | 10.2 | 12.1 | 10
118 | -118 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
119 | -117 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
120 | -116 | 11.7 | 11.1 | 10.2 | 12.1 | 10
121 | -115 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
122 | -114 | 11.7 | 11.1 | 10.2 | 12.1 | 10
123 | -113 | 11.7 | 11.1 | 10.2 | 12.1 | 10
124 | -112 | 11.7 | 11.1 | 10.2 | 12.1 | 10
125 | -111 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
126 | -110 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
127 | -109 | 11.7 | 11.1 | 10.1 | 12.1 | 9.9
128 | -108 | 11.7 | 11.1 | 10.2 | 12.1 | 10
129 | -107 | 11.7 | 11 | 10.2 | 12.1 | 10
130 | -106 | 11.7 | 11 | 10.1 | 12.1 | 10
131 | -105 | 11.7 | 11 | 10.1 | 12.1 | 9.9
132 | -104 | 11.7 | 11 | 10.1 | 12.1 | 10
133 | -103 | 11.7 | 11 | 10.1 | 12.1 | 9.9
134 | -102 | 11.7 | 11 | 10.1 | 12.1 | 10
135 | -101 | 11.7 | 11 | 10.1 | 12.1 | 10
136 | -100 | 11.7 | 11 | 10.1 | 12.1 | 10
137 | -99 | 11.7 | 11 | 10.1 | 12.1 | 10
138 | -98 | 11.7 | 11 | 10.1 | 12.1 | 10
139 | -97 | 11.7 | 11 | 10.1 | 12.1 | 10
140 | -96 | 11.7 | 11 | 10.1 | 12.1 | 10
141 | -95 | 11.7 | 11 | 10.1 | 12.1 | 10
142 | -94 | 11.7 | 11 | 10.1 | 12.1 | 10
143 | -93 | 11.7 | 11 | 10.1 | 12.1 | 10
144 | -92 | 11.7 | 11 | 10.1 | 12.1 | 10
145 | -91 | 11.7 | 11 | 10.1 | 12.1 | 10
146 | -90 | 11.7 | 11 | 10.2 | 12.1 | 10
147 | -89 | 11.7 | 11 | 10.1 | 12.1 | 10
148 | -88 | 11.7 | 11 | 10.1 | 12.1 | 10
149 | -87 | 11.7 | 11 | 10.1 | 12.1 | 10
150 | -86 | 11.7 | 11 | 10.2 | 12.1 | 9.9
151 | -85 | 11.7 | 11 | 10.2 | 12.1 | 9.9
152 | -84 | 11.7 | 11 | 10.2 | 12.1 | 9.9
153 | -83 | 11.7 | 11 | 10.2 | 12.1 | 10
154 | -82 | 11.7 | 11 | 10.1 | 12.1 | 10
155 | -81 | 11.7 | 11 | 10.2 | 12.1 | 10
156 | -80 | 11.7 | 11 | 10.2 | 12.1 | 9.9
157 | -79 | 11.7 | 11.1 | 10.2 | 12.1 | 9.9
158 | -78 | 11.7 | 11.1 | 10.1 | 12.1 | 10
159 | -77 | 11.7 | 11.1 | 10.1 | 12.1 | 10
160 | -76 | 11.7 | 11.1 | 10.2 | 12.1 | 10
161 | -75 | 11.7 | 11.1 | 10.2 | 12.1 | 10
162 | -74 | 11.7 | 11 | 10.2 | 12.1 | 10
163 | -73 | 11.7 | 11.1 | 10.2 | 12.1 | 10
164 | -72 | 11.7 | 11.1 | 10.2 | 12.1 | 10
165 | -71 | 11.7 | 11.1 | 10.2 | 12.1 | 10
166 | -70 | 11.7 | 11.1 | 10.2 | 12.1 | 10
167 | -69 | 11.7 | 11.1 | 10.2 | 12.1 | 10
168 | -68 | 11.7 | 11.1 | 10.2 | 12.1 | 10
169 | -67 | 11.7 | 11.1 | 10.2 | 12.1 | 10
170 | -66 | 11.7 | 11.1 | 10.2 | 12.1 | 10
171 | -65 | 11.7 | 11.1 | 10.2 | 12.1 | 10
172 | -64 | 11.7 | 11.1 | 10.2 | 12.1 | 10
173 | -63 | 11.7 | 11.1 | 10.2 | 12.1 | 10
174 | -62 | 11.7 | 11.1 | 10.2 | 12.1 | 10
175 | -61 | 11.7 | 11.1 | 10.2 | 12.1 | 10
176 | -60 | 11.7 | 11.1 | 10.3 | 12.1 | 10
177 | -59 | 11.7 | 11.1 | 10.3 | 12.1 | 10
178 | -58 | 11.7 | 11.1 | 10.3 | 12.1 | 10
179 | -57 | 11.7 | 11.1 | 10.3 | 12.1 | 10
180 | -56 | 11.7 | 11.1 | 10.3 | 12.1 | 10
181 | -55 | 11.7 | 11.1 | 10.3 | 12.1 | 10
182 | -54 | 11.7 | 11.1 | 10.2 | 12.1 | 10
183 | -53 | 11.7 | 11.1 | 10.2 | 12.1 | 10
184 | -52 | 11.7 | 11.1 | 10.2 | 12.1 | 10
185 | -51 | 11.7 | 11.1 | 10.2 | 12.1 | 10
186 | -50 | 11.7 | 11.1 | 10.2 | 12.1 | 10
187 | -49 | 11.7 | 11.1 | 10.2 | 12.1 | 10
188 | -48 | 11.7 | 11.1 | 10.2 | 12.1 | 10
189 | -47 | 11.7 | 11.1 | 10.2 | 12.1 | 10
190 | -46 | 11.7 | 11.1 | 10.1 | 12.1 | 10
191 | -45 | 11.7 | 11 | 10.1 | 12.1 | 10
192 | -44 | 11.7 | 11 | 10.1 | 12.1 | 10
193 | -43 | 11.7 | 11 | 10.1 | 12.1 | 10
194 | -42 | 11.7 | 11 | 10.1 | 12.1 | 10
195 | -41 | 11.7 | 11 | 10.1 | 12.1 | 10
196 | -40 | 11.7 | 11 | 10.1 | 12.1 | 10
197 | -39 | 11.7 | 11 | 10.1 | 12.1 | 10
198 | -38 | 11.7 | 11 | 10.1 | 12.1 | 10
199 | -37 | 11.7 | 11 | 10.1 | 12.1 | 10
200 | -36 | 11.7 | 11 | 10.1 | 12.1 | 10
201 | -35 | 11.7 | 11 | 10.1 | 12.1 | 10
202 | -34 | 11.7 | 11.1 | 10 | 12.1 | 10
203 | -33 | 11.7 | 11 | 10 | 12.1 | 10
204 | -32 | 11.7 | 11 | 10 | 12.1 | 10
205 | -31 | 11.7 | 11 | 10 | 12.1 | 10
206 | -30 | 11.7 | 11 | 10.1 | 12.1 | 10
207 | -29 | 11.7 | 11 | 10.1 | 12.1 | 10
208 | -28 | 11.7 | 11 | 10.1 | 12.1 | 10
209 | -27 | 11.7 | 11 | 10.1 | 12.1 | 10
210 | -26 | 11.7 | 11 | 10.1 | 12.1 | 10
211 | -25 | 11.7 | 11 | 10.1 | 12.1 | 10
212 | -24 | 11.7 | 11.1 | 10.1 | 12.1 | 10
213 | -23 | 11.7 | 11.1 | 10.2 | 12.1 | 10
214 | -22 | 11.7 | 11 | 10.2 | 12.1 | 10
215 | -21 | 11.7 | 11.1 | 10.2 | 12.1 | 10
216 | -20 | 11.7 | 11.1 | 10.2 | 12.1 | 10
217 | -19 | 11.7 | 11.1 | 10.2 | 12.1 | 10
218 | -18 | 11.7 | 11.1 | 10.2 | 12.1 | 10
219 | -17 | 11.7 | 11.1 | 10.2 | 12.1 | 10
220 | -16 | 11.7 | 11.1 | 10.2 | 12.1 | 10
221 | -15 | 11.7 | 11.1 | 10.2 | 12.1 | 10
222 | -14 | 11.7 | 11.1 | 10.1 | 12.1 | 10
223 | -13 | 11.7 | 11.1 | 10.1 | 12.1 | 10
224 | -12 | 11.7 | 11.1 | 10.1 | 12.1 | 10
225 | -11 | 11.7 | 11.1 | 10.2 | 12.1 | 10
226 | -10 | 11.7 | 11.1 | 10.1 | 12.1 | 10
227 | -9 | 11.7 | 11 | 10.2 | 12.1 | 10
228 | -8 | 11.7 | 11.1 | 10.2 | 12.1 | 10
229 | -7 | 11.7 | 11.1 | 10.2 | 12.1 | 10
230 | -6 | 11.7 | 11.1 | 10.2 | 12 | 10
231 | -5 | 11.7 | 11.1 | 10.2 | 12.1 | 10
232 | -4 | 11.7 | 11.1 | 10.2 | 12.1 | 10
233 | -3 | 11.7 | 11.1 | 10.2 | 12.1 | 10
234 | -2 | 11.7 | 11.1 | 10.2 | 12.1 | 10
235 | -1 | 11.7 | 11.1 | 10.2 | 12.1 | 10
236 | 0 | 11.7 | 11.1 | 10.2 | 12.1 | 10
237 | 1 | 11.7 | 11.1 | 10.3 | 12.1 | 10
238 | 2 | 11.7 | 11.1 | 10.2 | 12.1 | 10
239 | 3 | 11.7 | 11.1 | 10.3 | 12.1 | 10
240 | 4 | 11.7 | 11.1 | 10.3 | 12.1 | 10.1
241 | 5 | 11.7 | 11.2 | 10.4 | 12.1 | 10.1
242 | 6 | 11.7 | 11.4 | 10.6 | 12.1 | 10.3
243 | 7 | 11.7 | 11.8 | 10.8 | 12.1 | 10.4
244 | 8 | 11.7 | 12 | 11 | 12.1 | 10.6
245 | 9 | 11.7 | 12.2 | 11.4 | 12.1 | 10.8
246 | 10 | 11.7 | 13 | 12.1 | 12.1 | 11
247 | 11 | 11.7 | 14.9 | 13.2 | 12.1 | 11.2
248 | 12 | 11.7 | 18 | 15.1 | 12.1 | 11.6
249 | 13 | 11.7 | 20.7 | 16.8 | 12.1 | 12
250 | 14 | 11.7 | 23.4 | 18.4 | 12.1 | 12.3
251 | 15 | 11.7 | 28 | 20.4 | 12.1 | 12.6
252 | 16 | 11.7 | 31.3 | 22.7 | 12.1 | 12.9
253 | 17 | 11.7 | 34.9 | 25.1 | 12.1 | 13.3
254 | 18 | 11.7 | 38 | 27.6 | 12.1 | 13.8
255 | 19 | 11.7 | 41.3 | 30.2 | 12.1 | 14.2
256 | 20 | 11.8 | 46.1 | 32.9 | 12.1 | 14.7
257 | 21 | 11.8 | 50.4 | 35.7 | 12.1 | 15.1
258 | 22 | 11.7 | 53.6 | 38.5 | 12.1 | 15.7
259 | 23 | 11.8 | 56.8 | 41.1 | 12.1 | 16.1
260 | 24 | 11.8 | 59.5 | 43.4 | 12.1 | 16.8
261 | 25 | 11.8 | 62 | 45.6 | 12.2 | 17.2
262 | 26 | 11.8 | 64.8 | 48 | 12.1 | 17.5
263 | 27 | 11.8 | 68.7 | 50.4 | 12.2 | 18
264 | 28 | 11.8 | 71.6 | 53.4 | 12.2 | 18.4
265 | 29 | 11.8 | 74.7 | 56.6 | 12.2 | 18.8
266 | 30 | 11.8 | 78 | 59.4 | 12.2 | 19.3
267 | 31 | 11.8 | 81 | 62.9 | 12.2 | 20
268 | 32 | 11.8 | 84.1 | 65.9 | 12.2 | 20.4
269 | 33 | 11.9 | 87.2 | 68.7 | 12.2 | 20.8
270 | 34 | 11.9 | 91.3 | 71.1 | 12.2 | 21.3
271 | 35 | 11.9 | 95 | 74.4 | 12.2 | 21.9
272 | 36 | 11.9 | 98.2 | 76.9 | 12.2 | 22.7
273 | 37 | 11.9 | 101 | 79.2 | 12.2 | 23.2
274 | 38 | 12 | 104.1 | 82.4 | 12.2 | 23.8
275 | 39 | 12 | 106.9 | 86.3 | 12.2 | 24.2
276 | 40 | 12 | 109.5 | 88.7 | 12.2 | 24.7
277 | 41 | 12 | 112.2 | 90.8 | 12.2 | 25.6
278 | 42 | 12 | 115.3 | 92.8 | 12.3 | 26.1
279 | 43 | 12.1 | 118.3 | 95 | 12.3 | 26.7
280 | 44 | 12.1 | 121.3 | 96.9 | 12.3 | 27.5
281 | 45 | 12.1 | 124.3 | 98.9 | 12.3 | 28.1
282 | 46 | 12.1 | 127.3 | 101.2 | 12.3 | 28.6
283 | 47 | 12.2 | 130 | 103.6 | 12.3 | 29
284 | 48 | 12.2 | 133.6 | 107.4 | 12.3 | 29.6
285 | 49 | 12.3 | 135.3 | 110.4 | 12.3 | 30.2
286 | 50 | 12.3 | 137.1 | 112.8 | 12.3 | 30.8
287 | 51 | 12.3 | 138.7 | 114.8 | 12.3 | 31.5
288 | 52 | 12.4 | 140.5 | 116.2 | 12.4 | 32.3
289 | 53 | 12.4 | 142.4 | 118 | 12.4 | 32.7
290 | 54 | 12.5 | 145.4 | 120.6 | 12.4 | 33.2
291 | 55 | 12.5 | 148.5 | 122.9 | 12.4 | 33.8
292 | 56 | 12.5 | 150.3 | 125 | 12.4 | 34.5
293 | 57 | 12.6 | 151.8 | 126.8 | 12.4 | 35.1
294 | 58 | 12.6 | 153 | 127.9 | 12.5 | 35.8
295 | 59 | 12.7 | 154.4 | 129 | 12.5 | 36.4
296 | 60 | 12.7 | 155.4 | 130.3 | 12.5 | 36.9
297 | 61 | 12.8 | 157.4 | 131.9 | 12.5 | 37.3
298 | 62 | 12.8 | 159 | 133.6 | 12.5 | 37.9
299 | 63 | 12.9 | 160 | 134.8 | 12.6 | 38.3
300 | 64 | 12.9 | 160.8 | 136.7 | 12.6 | 38.9
301 | 65 | 13 | 162.3 | 137.4 | 12.6 | 39.4
302 | 66 | 13.1 | 163.5 | 138.3 | 12.6 | 39.9
303 | 67 | 13.1 | 164.5 | 139.5 | 12.7 | 40.5
304 | 68 | 13.2 | 165.7 | 141.5 | 12.7 | 41.1
305 | 69 | 13.2 | 167 | 143.5 | 12.7 | 41.7
306 | 70 | 13.3 | 167.8 | 144.5 | 12.8 | 42.3
307 | 71 | 13.4 | 168.8 | 145.4 | 12.8 | 42.9
308 | 72 | 13.5 | 169.8 | 146.1 | 12.8 | 43.3
309 | 73 | 13.5 | 171.1 | 146.9 | 12.9 | 43.9
310 | 74 | 13.6 | 172.8 | 148.1 | 12.9 | 44.5
311 | 75 | 13.7 | 174.1 | 149.2 | 12.9 | 44.9
312 | 76 | 13.7 | 175.2 | 150.4 | 13 | 45.4
313 | 77 | 13.8 | 176.5 | 151.6 | 13 | 46.1
314 | 78 | 13.9 | 177.8 | 153.2 | 13.1 | 46.6
315 | 79 | 13.9 | 179.4 | 155.6 | 13.1 | 47.2
316 | 80 | 14 | 180.2 | 157.7 | 13.1 | 47.8
317 | 81 | 14.1 | 181.3 | 157.9 | 13.2 | 48.2
318 | 82 | 14.2 | 182.1 | 158.5 | 13.2 | 48.9
319 | 83 | 14.2 | 182.3 | 159 | 13.3 | 49.6
320 | 84 | 14.3 | 183 | 159.8 | 13.3 | 49.8
321 | 85 | 14.4 | 183.7 | 160.4 | 13.4 | 50.3
322 | 86 | 14.5 | 183.9 | 161.3 | 13.4 | 50.9
323 | 87 | 14.6 | 185.3 | 162 | 13.5 | 51.5
324 | 88 | 14.6 | 186.2 | 162.7 | 13.5 | 52
325 | 89 | 14.7 | 186.9 | 163.3 | 13.6 | 52.6
326 | 90 | 14.8 | 188.1 | 164.2 | 13.7 | 53.1
327 | 91 | 14.9 | 189.2 | 165.5 | 13.7 | 53.4
328 | 92 | 15 | 189.8 | 166.7 | 13.8 | 53.9
329 | 93 | 15.1 | 189.9 | 167.4 | 13.8 | 54.5
330 | 94 | 15.1 | 190.2 | 168.6 | 13.9 | 55.1
331 | 95 | 15.2 | 190.9 | 170.2 | 14 | 55.6
332 | 96 | 15.3 | 191.6 | 170.6 | 14.1 | 56.1
333 | 97 | 15.4 | 192.5 | 170.7 | 14.1 | 56.7
334 | 98 | 15.5 | 193.7 | 171 | 14.2 | 57.1
335 | 99 | 15.6 | 194.9 | 171.3 | 14.2 | 57.5
336 | 100 | 15.7 | 195.8 | 172.2 | 14.3 | 58
337 | 101 | 15.8 | 196.4 | 173.2 | 14.4 | 58.5
338 | 102 | 15.9 | 197.3 | 174.1 | 14.5 | 59.1
339 | 103 | 16 | 199.1 | 175.2 | 14.5 | 59.5
340 | 104 | 16.1 | 200 | 176.3 | 14.6 | 60
341 | 105 | 16.2 | 200.6 | 177 | 14.7 | 60.5
342 | 106 | 16.3 | 201.7 | 178.5 | 14.8 | 61
343 | 107 | 16.4 | 203 | 179.3 | 14.9 | 61.5
344 | 108 | 16.5 | 203.1 | 180.1 | 14.9 | 61.9
345 | 109 | 16.6 | 203.8 | 181.1 | 15 | 62.2
346 | 110 | 16.7 | 204.4 | 181.6 | 15.2 | 62.8
347 | 111 | 16.8 | 204.5 | 181.6 | 15.3 | 63.2
348 | 112 | 16.9 | 204.2 | 181.5 | 15.4 | 63.7
349 | 113 | 17 | 204 | 181.7 | 15.5 | 64.1
350 | 114 | 17.1 | 204.6 | 182 | 15.6 | 64.4
351 | 115 | 17.3 | 205.6 | 183.1 | 15.7 | 64.9
352 | 116 | 17.4 | 206.1 | 183.9 | 15.9 | 65.3
353 | 117 | 17.5 | 206.5 | 184.4 | 16 | 65.7
354 | 118 | 17.6 | 206.8 | 184.7 | 16.1 | 66.1
355 | 119 | 17.7 | 206.9 | 184.8 | 16.2 | 66.5
356 | 120 | 17.8 | 206.9 | 186 | 16.3 | 67.1
357 | 121 | 18 | 206.8 | 187.3 | 16.4 | 67.6
358 | 122 | 18.1 | 206.7 | 187.5 | 16.5 | 68
359 | 123 | 18.2 | 207 | 188 | 16.7 | 68.3
360 | 124 | 18.3 | 207.5 | 188.7 | 16.8 | 68.7
361 | 125 | 18.5 | 207.7 | 188.4 | 16.9 | 69.2
362 | 126 | 18.6 | 208.1 | 188.2 | 17 | 69.7
363 | 127 | 18.7 | 208.5 | 189.1 | 17.1 | 70
364 | 128 | 18.9 | 209.8 | 189.9 | 17.3 | 70.3
365 | 129 | 19 | 210.7 | 190.5 | 17.5 | 70.7
366 | 130 | 19.1 | 211 | 190.9 | 17.6 | 71.2
367 | 131 | 19.3 | 211.9 | 191.5 | 17.7 | 71.7
368 | 132 | 19.4 | 214.8 | 192 | 17.9 | 72.3
369 | 133 | 19.5 | 216.5 | 192.6 | 18 | 72.6
370 | 134 | 19.7 | 218 | 193.6 | 18.2 | 73.1
371 | 135 | 19.8 | 219.1 | 194.6 | 18.3 | 73.5
372 | 136 | 20 | 219.1 | 195 | 18.4 | 73.8
373 | 137 | 20.1 | 219 | 195.1 | 18.6 | 74.1
374 | 138 | 20.2 | 219 | 195.9 | 18.8 | 74.4
375 | 139 | 20.4 | 218.8 | 195.8 | 18.9 | 74.8
376 | 140 | 20.5 | 219 | 196 | 19.1 | 75.2
377 | 141 | 20.7 | 219.3 | 196.2 | 19.2 | 75.4
378 | 142 | 20.8 | 219.6 | 196.2 | 19.3 | 75.6
379 | 143 | 21 | 220.1 | 196.3 | 19.5 | 76.1
380 | 144 | 21.1 | 220 | 197.7 | 19.7 | 76.4
381 | 145 | 21.3 | 220 | 197.7 | 19.8 | 76.6
382 | 146 | 21.4 | 220.5 | 198.4 | 20 | 77
383 | 147 | 21.6 | 220.6 | 198.4 | 20.1 | 77.5
384 | 148 | 21.7 | 220.9 | 198.1 | 20.3 | 77.9
385 | 149 | 21.9 | 221.2 | 198 | 20.5 | 78.2
386 | 150 | 22 | 221.1 | 198.1 | 20.6 | 78.6
387 | 151 | 22.2 | 221.2 | 197.9 | 20.8 | 79
388 | 152 | 22.3 | 221.7 | 198.1 | 21 | 79.3
389 | 153 | 22.5 | 222.8 | 198.4 | 21.2 | 79.4
390 | 154 | 22.6 | 223.4 | 198.9 | 21.3 | 79.7
391 | 155 | 22.8 | 223.8 | 199.3 | 21.5 | 80.1
392 | 156 | 22.9 | 224.1 | 199.4 | 21.7 | 80.5
393 | 157 | 23.1 | 223.9 | 199.7 | 21.9 | 80.8
394 | 158 | 23.3 | 223.8 | 199.9 | 22.1 | 80.9
395 | 159 | 23.4 | 223.5 | 200.3 | 22.3 | 81.2
396 | 160 | 23.6 | 223.1 | 201 | 22.5 | 81.7
397 | 161 | 23.7 | 223 | 201.8 | 22.6 | 82.1
398 | 162 | 23.9 | 222.6 | 202.1 | 22.8 | 82.5
399 | 163 | 24.1 | 222.5 | 203.3 | 23 | 82.9
400 | 164 | 24.2 | 222 | 204.3 | 23.2 | 83.3
401 | 165 | 24.4 | 223.7 | 204.3 | 23.3 | 83.6
402 | 166 | 24.6 | 223.9 | 204.8 | 23.5 | 84
403 | 167 | 24.7 | 223.9 | 204.8 | 23.7 | 84.6
404 | 168 | 24.9 | 223.8 | 205.3 | 23.9 | 85
405 | 169 | 25 | 224.1 | 206.3 | 24.1 | 85.5
406 | 170 | 25.2 | 224.4 | 206.8 | 24.3 | 85.9
407 | 171 | 25.4 | 224.5 | 206.7 | 24.5 | 86.2
408 | 172 | 25.5 | 225.1 | 206.6 | 24.7 | 86.5
409 | 173 | 25.7 | 225.1 | 207.1 | 24.9 | 86.9
410 | 174 | 25.9 | 225.1 | 206.9 | 25 | 87.1
411 | 175 | 26 | 225.4 | 206.9 | 25.2 | 87.4
412 | 176 | 26.2 | 225.5 | 206.7 | 25.4 | 87.5
413 | 177 | 26.4 | 225.8 | 206.3 | 25.5 | 87.6
414 | 178 | 26.5 | 226.2 | 206.2 | 25.7 | 87.8
415 | 179 | 26.7 | 226.4 | 206.2 | 25.9 | 88
416 | 180 | 26.9 | 226.6 | 206.2 | 26.1 | 88.2
417 | 181 | 27 | 227.7 | 206.9 | 26.3 | 88.7
418 | 182 | 27.2 | 228.1 | 207.3 | 26.5 | 89.1
419 | 183 | 27.4 | 228.2 | 207.8 | 26.7 | 89.6
420 | 184 | 27.5 | 228.2 | 208.5 | 26.9 | 90
421 | 185 | 27.7 | 228.5 | 208.7 | 27.1 | 90.3
422 | 186 | 27.9 | 228.5 | 208.8 | 27.3 | 90.7
423 | 187 | 28 | 228.4 | 208.8 | 27.4 | 91.1
424 | 188 | 28.2 | 228.8 | 208.7 | 27.6 | 91.3
425 | 189 | 28.4 | 228.8 | 208.4 | 27.8 | 91.5
426 | 190 | 28.6 | 228.9 | 208.1 | 28 | 91.6
427 | 191 | 28.7 | 229.6 | 208.2 | 28.2 | 91.8
428 | 192 | 28.9 | 230.3 | 208.2 | 28.3 | 92.3
429 | 193 | 29.1 | 230.5 | 208.4 | 28.5 | 92.5
430 | 194 | 29.2 | 230.8 | 209.1 | 28.7 | 92.9
431 | 195 | 29.4 | 230.8 | 209.6 | 28.9 | 93.2
432 | 196 | 29.6 | 230.9 | 209.7 | 29.1 | 93.6
433 | 197 | 29.8 | 231.2 | 210.1 | 29.2 | 93.9
434 | 198 | 29.9 | 232.1 | 210.1 | 29.4 | 94.2
435 | 199 | 30.1 | 232.9 | 210.5 | 29.6 | 94.5
436 | 200 | 30.3 | 233.1 | 210.7 | 29.8 | 95
437 | 201 | 30.5 | 233.9 | 210.9 | 29.9 | 95.3
438 | 202 | 30.6 | 234.2 | 211.2 | 30.1 | 95.7
439 | 203 | 30.8 | 234.9 | 211.6 | 30.3 | 96
440 | 204 | 31 | 234.8 | 212.5 | 30.5 | 96.5
441 | 205 | 31.2 | 234.5 | 212.4 | 30.6 | 97
442 | 206 | 31.3 | 234.9 | 213.2 | 30.8 | 97.3
443 | 207 | 31.5 | 235.2 | 213.7 | 31 | 97.5
444 | 208 | 31.7 | 235.6 | 214.5 | 31.2 | 97.8
445 | 209 | 31.8 | 235.6 | 215.5 | 31.4 | 98.4
446 | 210 | 32 | 235.4 | 216.7 | 31.6 | 98.8
447 | 211 | 32.2 | 236.2 | 217.5 | 31.7 | 99.4
448 | 212 | 32.4 | 237.5 | 218.9 | 31.9 | 99.8
449 | 213 | 32.5 | 238.2 | 220.2 | 32.1 | 100.5
450 | 214 | 32.7 | 239 | 221.6 | 32.3 | 101
451 | 215 | 32.9 | 239.9 | 222.4 | 32.5 | 101.5
452 | 216 | 33.1 | 239.2 | 222.8 | 32.7 | 101.8
453 | 217 | 33.2 | 239.2 | 222.8 | 32.9 | 102.2
454 | 218 | 33.4 | 239.1 | 222.5 | 33 | 102.5
455 | 219 | 33.6 | 238.9 | 222.7 | 33.2 | 102.8
456 | 220 | 33.8 | 239.2 | 224.1 | 33.4 | 103.1
457 | 221 | 33.9 | 240.2 | 225.6 | 33.6 | 103.4
458 | 222 | 34.1 | 240.3 | 226.7 | 33.7 | 104
459 | 223 | 34.3 | 240.7 | 227.7 | 33.9 | 104.4
460 | 224 | 34.5 | 241.2 | 228.3 | 34.1 | 104.7
461 | 225 | 34.7 | 242.3 | 228.9 | 34.3 | 105.1
462 | 226 | 34.8 | 243.9 | 229.2 | 34.5 | 105.6
463 | 227 | 35 | 244.2 | 229.3 | 34.7 | 105.9
464 | 228 | 35.2 | 245.1 | 229.2 | 34.9 | 106.2
465 | 229 | 35.4 | 245.4 | 229 | 35.1 | 106.4
466 | 230 | 35.5 | 245.9 | 228.8 | 35.2 | 106.8
467 | 231 | 35.7 | 246.4 | 228.4 | 35.4 | 106.8
468 | 232 | 35.9 | 246.7 | 228.2 | 35.6 | 107.2
469 | 233 | 36.1 | 247 | 228.4 | 35.8 | 107.6
470 | 234 | 36.3 | 247.6 | 229.4 | 36 | 107.9
471 | 235 | 36.5 | 247.7 | 229.5 | 36.2 | 108.4
472 | 236 | 36.6 | 249.7 | 230.5 | 36.5 | 109
473 | 237 | 36.8 | 252.3 | 231.2 | 36.7 | 109.3
474 | 238 | 37 | 252.2 | 231.4 | 36.9 | 109.6
475 | 239 | 37.2 | 251.9 | 231.7 | 37.1 | 110
476 | 240 | 37.4 | 251.9 | 231.8 | 37.3 | 110.6
477 | 241 | 37.6 | 252.6 | 232.2 | 37.6 | 110.9
478 | 242 | 37.8 | 253 | 233.5 | 37.9 | 111.4
479 | 243 | 37.9 | 252.8 | 234.2 | 38.1 | 111.7
480 | 244 | 38.1 | 252.9 | 235.9 | 38.3 | 112
481 | 245 | 38.3 | 252.6 | 237.2 | 38.6 | 112.4
482 | 246 | 38.5 | 252.6 | 238 | 38.9 | 112.8
483 | 247 | 38.7 | 253 | 238.5 | 39.1 | 113.2
484 | 248 | 38.9 | 253.3 | 239.2 | 39.4 | 113.6
485 | 249 | 39 | 253.8 | 239.5 | 39.6 | 114
486 | 250 | 39.2 | 254 | 239.5 | 39.8 | 114.5
487 | 251 | 39.4 | 254.4 | 239.2 | 40 | 114.9
488 | 252 | 39.6 | 254.3 | 239.4 | 40.3 | 115.3
489 | 253 | 39.8 | 254.6 | 239.5 | 40.5 | 115.5
490 | 254 | 40 | 256.4 | 240.2 | 40.7 | 115.9
491 | 255 | 40.2 | 257.6 | 240.7 | 41 | 116.4
492 | 256 | 40.4 | 258.3 | 240.9 | 41.2 | 116.7
493 | 257 | 40.6 | 258.4 | 240.4 | 41.4 | 117
494 | 258 | 40.7 | 258.2 | 240.2 | 41.6 | 117.3
495 | 259 | 40.9 | 258 | 240 | 41.9 | 117.6
496 | 260 | 41.1 | 258 | 239.7 | 42.1 | 118
497 | 261 | 41.3 | 258.2 | 239.3 | 42.3 | 118.2
498 | 262 | 41.5 | 259 | 239.2 | 42.6 | 118.4
499 | 263 | 41.7 | 258.8 | 239.7 | 42.8 | 119
500 | 264 | 41.9 | 258.4 | 239.9 | 43.1 | 119.5
501 | 265 | 42 | 258.1 | 240 | 43.3 | 119.8
502 | 266 | 42.2 | 257.8 | 239.9 | 43.5 | 120.1
503 | 267 | 42.4 | 258.5 | 240.6 | 43.8 | 120.4
504 | 268 | 42.6 | 259.2 | 241 | 44 | 120.7
505 | 269 | 42.8 | 260.2 | 241.5 | 44.2 | 121.2
506 | 270 | 43 | 260.3 | 242.2 | 44.5 | 121.7
507 | 271 | 43.1 | 260.3 | 242.3 | 44.7 | 122.2
508 | 272 | 43.3 | 260.2 | 242.8 | 44.9 | 122.5
509 | 273 | 43.5 | 259.6 | 243.4 | 45.2 | 122.9
510 | 274 | 43.7 | 258.9 | 244.2 | 45.4 | 123.2
511 | 275 | 43.9 | 258.8 | 244.4 | 45.6 | 123.7
512 | 276 | 44.1 | 259.2 | 244.5 | 45.9 | 124.3
513 | 277 | 44.3 | 259.7 | 245.2 | 46.1 | 124.7
514 | 278 | 44.4 | 259.2 | 246 | 46.3 | 125
515 | 279 | 44.6 | 259.7 | 246.4 | 46.5 | 125.6
516 | 280 | 44.8 | 259.9 | 246.4 | 46.7 | 126
517 | 281 | 45 | 260.3 | 246.3 | 47 | 126.4
518 | 282 | 45.2 | 260.3 | 246.1 | 47.2 | 126.8
519 | 283 | 45.4 | 261 | 246.3 | 47.4 | 127.1
520 | 284 | 45.6 | 262.1 | 246.5 | 47.6 | 127.5
521 | 285 | 45.7 | 264 | 247.4 | 47.8 | 127.8
522 | 286 | 45.9 | 265.2 | 248.2 | 48 | 128.5
523 | 287 | 46.1 | 265 | 248.7 | 48.3 | 128.9
524 | 288 | 46.3 | 265.1 | 248.4 | 48.5 | 129.2
525 | 289 | 46.5 | 264.8 | 248.4 | 48.7 | 129.7
526 | 290 | 46.7 | 265.4 | 248.5 | 48.9 | 130.1
527 | 291 | 46.8 | 266.3 | 248.7 | 49.1 | 130.7
528 | 292 | 47.1 | 267.3 | 248.6 | 49.3 | 131.2
529 | 293 | 47.2 | 268.5 | 249 | 49.5 | 131.6
530 | 294 | 47.4 | 268.5 | 249.6 | 49.7 | 131.7
531 | 295 | 47.6 | 268.9 | 249.8 | 49.9 | 131.9
532 | 296 | 47.8 | 269.3 | 249.5 | 50.1 | 132.2
533 | 297 | 48 | 269.1 | 249.2 | 50.3 | 132.5
534 | 298 | 48.2 | 269 | 249 | 50.5 | 132.8
535 | 299 | 48.4 | 269.5 | 249.2 | 50.7 | 133
536 | 300 | 48.5 | 270.2 | 249.3 | 50.9 | 133.4
537 | 301 | 48.7 | 270.9 | 249.2 | 51.1 | 133.9
538 | 302 | 48.9 | 270.9 | 249.1 | 51.3 | 134.3
539 | 303 | 49.1 | 271.3 | 249.3 | 51.5 | 134.4
540 | 304 | 49.3 | 271.6 | 249.6 | 51.6 | 134.8
541 | 305 | 49.5 | 272 | 249.7 | 51.8 | 135.1
542 | 306 | 49.7 | 272 | 250.1 | 52 | 135.4
543 | 307 | 49.8 | 271.8 | 250.5 | 52.2 | 135.8
544 | 308 | 50 | 273.1 | 250.6 | 52.4 | 136.1
545 | 309 | 50.2 | 273.9 | 251 | 52.6 | 136.5
546 | 310 | 50.4 | 273.6 | 250.5 | 52.8 | 136.8
547 | 311 | 50.6 | 274.2 | 250.4 | 53 | 137.3
548 | 312 | 50.8 | 274.8 | 250.4 | 53.2 | 137.7
549 | 313 | 51 | 275.2 | 250.3 | 53.4 | 138.1
550 | 314 | 51.2 | 275.1 | 250.1 | 53.6 | 138.4
551 | 315 | 51.4 | 275.8 | 250.7 | 53.8 | 138.6
552 | 316 | 51.5 | 275.6 | 250.8 | 53.9 | 138.9
553 | 317 | 51.7 | 275.5 | 250.8 | 54.1 | 139.3
554 | 318 | 51.9 | 275.8 | 251.3 | 54.3 | 139.7
555 | 319 | 52.1 | 275.8 | 251.9 | 54.5 | 140.1
556 | 320 | 52.3 | 275.8 | 252.4 | 54.8 | 140.6
557 | 321 | 52.5 | 276.5 | 252.3 | 55 | 140.9
558 | 322 | 52.7 | 278 | 252.3 | 55.2 | 141.4
559 | 323 | 52.9 | 278.9 | 253.1 | 55.4 | 142
560 | 324 | 53.1 | 279.7 | 253.2 | 55.6 | 142.6
561 | 325 | 53.3 | 280.1 | 253.9 | 55.9 | 142.9
562 | 326 | 53.5 | 280.3 | 255.2 | 56.1 | 143.4
563 | 327 | 53.6 | 279.8 | 255.7 | 56.4 | 143.9
564 | 328 | 53.8 | 279.6 | 256 | 56.6 | 144.3
565 | 329 | 54 | 279.5 | 256.4 | 56.8 | 144.9
566 | 330 | 54.2 | 279.8 | 256.4 | 57.1 | 145.2
567 | 331 | 54.4 | 280 | 256.2 | 57.3 | 145.5
568 | 332 | 54.6 | 280.4 | 256.3 | 57.5 | 145.9
569 | 333 | 54.8 | 280.7 | 256.4 | 57.8 | 146.2
570 | 334 | 55 | 281.9 | 256.8 | 58 | 146.7
571 | 335 | 55.1 | 281.5 | 256.5 | 58.2 | 147.2
572 | 336 | 55.3 | 280.9 | 256.8 | 58.4 | 147.6
573 | 337 | 55.5 | 280.9 | 256.9 | 58.6 | 148
574 | 338 | 55.7 | 281.2 | 256.8 | 58.9 | 148.2
575 | 339 | 55.9 | 281.4 | 256.8 | 59.1 | 148.5
576 | 340 | 56.1 | 281.2 | 256.9 | 59.3 | 149
577 | 341 | 56.3 | 281.6 | 257.5 | 59.5 | 149.3
578 | 342 | 56.5 | 281.9 | 258.2 | 59.7 | 149.8
579 | 343 | 56.7 | 282.9 | 258.8 | 59.9 | 150.2
580 | 344 | 56.8 | 283 | 258.9 | 60.2 | 150.5
581 | 345 | 57 | 283.2 | 259.1 | 60.4 | 150.9
582 | 346 | 57.2 | 284 | 259.4 | 60.6 | 151.3
583 | 347 | 57.4 | 284.5 | 259.4 | 60.8 | 151.7
584 | 348 | 57.6 | 285.7 | 259.3 | 61 | 152.1
585 | 349 | 57.7 | 286.8 | 259.6 | 61.2 | 152.5
586 | 350 | 57.9 | 287.9 | 260.1 | 61.5 | 152.9
587 | 351 | 58.1 | 288.7 | 260.5 | 61.7 | 153.5
588 | 352 | 58.3 | 289.8 | 261.8 | 61.9 | 154.1
589 | 353 | 58.5 | 290.7 | 263.2 | 62.2 | 154.6
590 | 354 | 58.6 | 291.7 | 264.3 | 62.4 | 155.1
591 | 355 | 58.8 | 292.9 | 264.4 | 62.6 | 155.7
592 | 356 | 59 | 294.6 | 264.7 | 62.9 | 156.1
593 | 357 | 59.2 | 296.3 | 266 | 63.1 | 156.5
594 | 358 | 59.3 | 297.2 | 267.6 | 63.4 | 157
595 | 359 | 59.5 | 297.8 | 269 | 63.6 | 157.7
596 | 360 | 59.7 | 300.3 | 269.7 | 63.9 | 158.1
597 | 361 | 59.9 | 301.1 | 270.1 | 64.1 | 158.6
598 | 362 | 60.1 | 301.3 | 270.1 | 64.4 | 159.1
599 | 363 | 60.2 | 301.1 | 271.5 | 64.7 | 159.6
600 | 364 | 60.4 | 300.5 | 272.3 | 64.9 | 160.2
601 | 365 | 60.6 | 300.3 | 272.6 | 65.2 | 160.8
602 | 366 | 60.8 | 300.3 | 272.8 | 65.4 | 161.3
603 | 367 | 61 | 300.5 | 272.9 | 65.7 | 161.6
604 | 368 | 61.1 | 300.1 | 272.9 | 65.9 | 161.9
605 | 369 | 61.3 | 300.1 | 273.9 | 66.2 | 162.3
606 | 370 | 61.5 | 299.7 | 274.9 | 66.4 | 163
607 | 371 | 61.7 | 300.1 | 275 | 66.7 | 163.4
608 | 372 | 61.9 | 299.6 | 275 | 66.9 | 163.6
609 | 373 | 62.1 | 299.3 | 274.8 | 67.2 | 164
610 | 374 | 62.2 | 298.8 | 274.7 | 67.4 | 164.3
611 | 375 | 62.4 | 298.6 | 274.8 | 67.7 | 164.7
612 | 376 | 62.6 | 298 | 275 | 67.9 | 165
613 | 377 | 62.8 | 297.3 | 275.1 | 68.2 | 165.4
614 | 378 | 63 | 297.2 | 274.4 | 68.4 | 165.7
615 | 379 | 63.1 | 297 | 274.5 | 68.7 | 166.1
616 | 380 | 63.3 | 296.8 | 274 | 68.9 | 166.6
617 | 381 | 63.5 | 296.5 | 273.7 | 69.2 | 167
618 | 382 | 63.7 | 297.3 | 274 | 69.4 | 167.4
619 | 383 | 63.9 | 297.8 | 274.1 | 69.7 | 167.9
620 | 384 | 64.1 | 298.5 | 274.1 | 70 | 168.3
621 | 385 | 64.2 | 298.7 | 274.6 | 70.2 | 168.8
622 | 386 | 64.4 | 298.4 | 274.9 | 70.5 | 169.4
623 | 387 | 64.6 | 298.2 | 275.2 | 70.7 | 169.9
624 | 388 | 64.8 | 297.9 | 275.9 | 71 | 170.4
625 | 389 | 65 | 297.3 | 276.6 | 71.3 | 170.8
626 | 390 | 65.2 | 297.5 | 276.4 | 71.5 | 171.1
627 | 391 | 65.3 | 298.5 | 276.2 | 71.8 | 171.3
628 | 392 | 65.5 | 299.6 | 276 | 72 | 171.5
629 | 393 | 65.7 | 301 | 276 | 72.3 | 171.9
630 | 394 | 65.9 | 301.9 | 276.3 | 72.6 | 172.3
631 | 395 | 66.1 | 302.6 | 276.7 | 72.8 | 172.8
632 | 396 | 66.3 | 303.2 | 277.7 | 73.1 | 173.3
633 | 397 | 66.5 | 303.4 | 278.8 | 73.4 | 173.9
634 | 398 | 66.7 | 303.5 | 278.8 | 73.6 | 174.5
635 | 399 | 66.9 | 303.1 | 279.1 | 73.9 | 175
636 | 400 | 67.1 | 302.8 | 278.9 | 74.2 | 175.3
637 | 401 | 67.3 | 302.9 | 278.9 | 74.5 | 175.6
638 | 402 | 67.5 | 302.9 | 278.9 | 74.8 | 176.2
639 | 403 | 67.7 | 304.6 | 279 | 75 | 176.5
640 | 404 | 67.9 | 308.4 | 280.1 | 75.3 | 176.9
641 | 405 | 68.1 | 312.3 | 281.9 | 75.6 | 177.6
642 | 406 | 68.3 | 312.8 | 282.6 | 75.9 | 178.1
643 | 407 | 68.5 | 313.6 | 283.7 | 76.2 | 178.7
644 | 408 | 68.7 | 313.1 | 284.1 | 76.4 | 179.1
645 | 409 | 68.9 | 313 | 284.3 | 76.7 | 179.5
646 | 410 | 69.1 | 313.1 | 284.8 | 77 | 180
647 | 411 | 69.3 | 313.6 | 285.3 | 77.2 | 180.5
648 | 412 | 69.6 | 314.1 | 286.4 | 77.5 | 181.1
649 | 413 | 69.8 | 314.5 | 286.7 | 77.8 | 181.5
650 | 414 | 70 | 315.5 | 287.8 | 78.1 | 181.9
651 | 415 | 70.2 | 315.9 | 288.8 | 78.3 | 182.4
652 | 416 | 70.4 | 316.1 | 289.4 | 78.6 | 182.8
653 | 417 | 70.6 | 316.2 | 289 | 78.9 | 183.4
654 | 418 | 70.8 | 316.2 | 288.9 | 79.2 | 183.8
655 | 419 | 71 | 316.6 | 289.2 | 79.4 | 184.2
656 | 420 | 71.2 | 316.6 | 289.5 | 79.7 | 184.6
657 | 421 | 71.5 | 316.8 | 289.1 | 80 | 184.9
658 | 422 | 71.7 | 317.6 | 289.5 | 80.2 | 185.4
659 | 423 | 71.9 | 317.3 | 290.3 | 80.5 | 185.9
660 | 424 | 72.1 | 316.8 | 290.4 | 80.8 | 186.4
661 | 425 | 72.3 | 316.5 | 290.9 | 81.1 | 186.9
662 | 426 | 72.6 | 316.3 | 291.6 | 81.3 | 187.3
663 | 427 | 72.8 | 315.8 | 292 | 81.6 | 187.7
664 | 428 | 73 | 315.8 | 291.7 | 81.9 | 188.2
665 | 429 | 73.2 | 316.3 | 291.7 | 82.2 | 188.6
666 | 430 | 73.4 | 316.8 | 291.8 | 82.5 | 189
667 | 431 | 73.6 | 316.7 | 292.2 | 82.7 | 189.5
668 | 432 | 73.9 | 316.6 | 291.9 | 83 | 189.9
669 | 433 | 74.1 | 317.6 | 291.9 | 83.3 | 190.3
670 | 434 | 74.3 | 321.6 | 292.4 | 83.6 | 190.8
671 | 435 | 74.5 | 321.8 | 293.4 | 83.9 | 191.4
672 | 436 | 74.8 | 321.5 | 293.7 | 84.1 | 192
673 | 437 | 75 | 321.1 | 293.5 | 84.4 | 192.4
674 | 438 | 75.2 | 319.8 | 293.1 | 84.7 | 192.8
675 | 439 | 75.5 | 319.3 | 292.9 | 85 | 193.3
676 | 440 | 75.7 | 319.4 | 292.5 | 85.2 | 193.9
677 | 441 | 75.9 | 319.5 | 292.2 | 85.5 | 194.1
678 | 442 | 76.1 | 320.1 | 292.4 | 85.8 | 194.7
679 | 443 | 76.3 | 320.3 | 292.7 | 86.1 | 195.2
680 | 444 | 76.6 | 320.5 | 293.4 | 86.4 | 195.6
681 | 445 | 76.8 | 320.4 | 293 | 86.6 | 196
682 | 446 | 77 | 320.7 | 293 | 86.9 | 196.3
683 | 447 | 77.3 | 321.2 | 293.3 | 87.2 | 196.7
684 | 448 | 77.5 | 321.6 | 293 | 87.5 | 197.1
685 | 449 | 77.7 | 322.1 | 293.6 | 87.8 | 197.6
686 | 450 | 78 | 322.2 | 294.2 | 88 | 198.2
687 | 451 | 78.2 | 322.8 | 294.6 | 88.3 | 198.8
688 | 452 | 78.4 | 323.3 | 294.9 | 88.6 | 199.2
689 | 453 | 78.6 | 323.5 | 295.3 | 88.9 | 199.9
690 | 454 | 78.9 | 323.8 | 295.7 | 89.2 | 200.2
691 | 455 | 79.1 | 323.7 | 296 | 89.5 | 200.7
692 | 456 | 79.3 | 324.1 | 296.2 | 89.8 | 201.1
693 | 457 | 79.6 | 324.1 | 297.1 | 90.1 | 201.6
694 | 458 | 79.8 | 323.9 | 297.5 | 90.3 | 202
695 | 459 | 80 | 324.1 | 297.6 | 90.7 | 202.3
696 | 460 | 80.3 | 324.1 | 298.2 | 91 | 203
697 | 461 | 80.5 | 324.5 | 299.6 | 91.3 | 203.6
698 | 462 | 80.7 | 324.4 | 300.6 | 91.6 | 204.2
699 | 463 | 81 | 326.1 | 301.4 | 92 | 204.6
700 | 464 | 81.2 | 326 | 302.2 | 92.3 | 205.1
701 | 465 | 81.4 | 326.7 | 302.4 | 92.6 | 205.7
702 | 466 | 81.6 | 328 | 302.5 | 93 | 206.2
703 | 467 | 81.9 | 328.9 | 302.9 | 93.3 | 206.9
704 | 468 | 82.1 | 328.8 | 303.3 | 93.7 | 207.4
705 | 469 | 82.3 | 328.8 | 303.4 | 94 | 207.8
706 | 470 | 82.6 | 328.4 | 303.4 | 94.3 | 208.2
707 | 471 | 82.8 | 328.6 | 303.3 | 94.7 | 208.6
708 | 472 | 83 | 329.1 | 303.9 | 95 | 209.1
709 | 473 | 83.3 | 330.3 | 303.9 | 95.4 | 209.6
710 | 474 | 83.5 | 331 | 303.9 | 95.7 | 210
711 | 475 | 83.7 | 331 | 303.6 | 96 | 210.2
712 | 476 | 84 | 330.4 | 303.2 | 96.4 | 210.6
713 | 477 | 84.2 | 330.4 | 303.2 | 96.7 | 211.2
714 | 478 | 84.4 | 330.8 | 303.3 | 97.1 | 211.4
715 | 479 | 84.6 | 331.7 | 303.1 | 97.5 | 211.7
716 | 480 | 84.9 | 332.2 | 303.6 | 97.8 | 212.1
717 | 481 | 85.1 | 332.3 | 303.8 | 98.2 | 212.6
718 | 482 | 85.3 | 331.9 | 304.5 | 98.6 | 213
719 | 483 | 85.6 | 332.3 | 304.7 | 99 | 213.6
720 | 484 | 85.8 | 332.3 | 305.3 | 100.5 | 214
721 | 485 | 86 | 332.3 | 305.7 | 102.3 | 214.4
722 | 486 | 86.3 | 332.1 | 306.5 | 103.9 | 215
723 | 487 | 86.5 | 331.6 | 307.4 | 105.3 | 215.5
724 | 488 | 86.7 | 330.8 | 308.4 | 106.6 | 216
725 | 489 | 87 | 330.6 | 309.1 | 107.8 | 216.3
726 | 490 | 87.2 | 330.4 | 308.6 | 109 | 216.7
727 | 491 | 87.5 | 330.2 | 308.7 | 110.2 | 217.1
728 | 492 | 87.7 | 330.1 | 309 | 111.3 | 217.6
729 | 493 | 88 | 330.7 | 309.2 | 112.4 | 218.2
730 | 494 | 88.2 | 332.5 | 308.6 | 113.5 | 218.6
731 | 495 | 88.5 | 333 | 308.7 | 114.5 | 219.1
732 | 496 | 88.7 | 333 | 309 | 115.5 | 219.8
733 | 497 | 89 | 332.8 | 308.6 | 116.3 | 220
734 | 498 | 89.2 | 332.6 | 309 | 117.1 | 220.2
735 | 499 | 89.5 | 332.2 | 308.5 | 117.9 | 220.6
736 | 500 | 89.8 | 332.4 | 307.8 | 118.6 | 220.8
737 | 501 | 90 | 332.5 | 307.1 | 119.3 | 221.1
738 | 502 | 90.3 | 332.2 | 306.7 | 120 | 221.3
739 | 503 | 90.6 | 331.9 | 306.1 | 120.6 | 221.6
740 | 504 | 90.9 | 332.8 | 305.5 | 121.3 | 222
741 | 505 | 91.1 | 332.7 | 305.2 | 121.9 | 222.4
742 | 506 | 91.4 | 332.7 | 305.7 | 122.5 | 222.9
743 | 507 | 91.7 | 333.5 | 305.5 | 123 | 223.2
744 | 508 | 92 | 333.7 | 306.1 | 123.6 | 223.7
745 | 509 | 92.2 | 333.6 | 306.2 | 124.1 | 223.9
746 | 510 | 92.5 | 334 | 305.5 | 124.7 | 224.2
747 | 511 | 92.8 | 333.9 | 304.8 | 125.1 | 224.5
748 | 512 | 93.1 | 333.4 | 304.2 | 125.6 | 224.8
749 | 513 | 93.4 | 332.6 | 303.5 | 126.1 | 225.1
750 | 514 | 93.7 | 332 | 303.1 | 126.5 | 225.4
751 | 515 | 94 | 331.4 | 302.9 | 126.9 | 225.6
752 | 516 | 94.3 | 330.9 | 302.6 | 127.3 | 225.8
753 | 517 | 94.6 | 330.1 | 302.1 | 127.7 | 226.1
754 | 518 | 94.9 | 329.2 | 301.8 | 128.1 | 226.3
755 | 519 | 95.2 | 329.5 | 301.7 | 128.5 | 226.7
756 | 520 | 95.5 | 330.7 | 301.4 | 128.9 | 226.9
757 | 521 | 95.8 | 330.7 | 301.6 | 129.3 | 227.4
758 | 522 | 96.1 | 330.8 | 301.6 | 129.7 | 227.8
759 | 523 | 96.5 | 330.6 | 302.3 | 130.1 | 228
760 | 524 | 96.8 | 330.4 | 302.8 | 130.5 | 228.2
761 | 525 | 97.2 | 330.4 | 302.9 | 130.9 | 228.4
762 | 526 | 97.5 | 330.1 | 303.2 | 131.2 | 228.8
763 | 527 | 97.9 | 329.9 | 303.3 | 131.6 | 229.2
764 | 528 | 98.3 | 329.9 | 303.3 | 131.9 | 229.5
765 | 529 | 98.6 | 330 | 303.3 | 132.2 | 229.7
766 | 530 | 99 | 330 | 303.2 | 132.5 | 229.9
767 | 531 | 99.4 | 329.8 | 302.5 | 132.9 | 230.4
768 | 532 | 99.8 | 330.3 | 302.6 | 133.2 | 230.8
769 | 533 | 100.2 | 331.4 | 302.8 | 133.7 | 231.4
770 | 534 | 100.6 | 332.9 | 303.1 | 134.1 | 231.9
771 | 535 | 101 | 333.8 | 303.6 | 134.5 | 232.3
772 | 536 | 101.4 | 334.2 | 304.9 | 134.8 | 232.9
773 | 537 | 101.7 | 334.8 | 306.7 | 135.2 | 233.5
774 | 538 | 102.1 | 335.9 | 308.4 | 135.8 | 234.1
775 | 539 | 102.5 | 336.4 | 309.7 | 136.2 | 234.4
776 | 540 | 102.9 | 336.2 | 310.6 | 136.7 | 234.8
777 | 541 | 103.3 | 335.9 | 310.6 | 137 | 235
778 | 542 | 103.7 | 335.7 | 310.6 | 137.4 | 235.2
779 | 543 | 104.1 | 335.7 | 310.4 | 137.8 | 235.6
780 | 544 | 104.4 | 335.9 | 310.2 | 138.3 | 235.8
781 | 545 | 104.8 | 336 | 309.4 | 138.7 | 236
782 | 546 | 105.2 | 336.2 | 308.7 | 139.1 | 236.3
783 | 547 | 105.6 | 337.4 | 308.5 | 139.6 | 236.4
784 | 548 | 105.9 | 338.3 | 308 | 140.1 | 236.5
785 | 549 | 106.3 | 339.1 | 308 | 140.6 | 236.8
786 | 550 | 106.7 | 339.8 | 308 | 141 | 237
787 | 551 | 107.1 | 340.3 | 308.5 | 141.4 | 237.2
788 | 552 | 107.5 | 340.3 | 308 | 141.8 | 237.6
789 | 553 | 107.8 | 340.1 | 308.5 | 142.3 | 237.9
790 | 554 | 108.2 | 339.9 | 309 | 142.7 | 238.2
791 | 555 | 108.6 | 339.4 | 308.5 | 143.1 | 238.5
792 | 556 | 108.9 | 339.3 | 308.6 | 143.5 | 238.8
793 | 557 | 109.3 | 339 | 308.6 | 143.9 | 239.3
794 | 558 | 109.7 | 338.5 | 308.4 | 144.3 | 239.6
795 | 559 | 110.1 | 338 | 308.2 | 144.8 | 239.8
796 | 560 | 110.4 | 337.8 | 308 | 145.1 | 240.1
797 | 561 | 110.8 | 337.4 | 308.2 | 145.6 | 240.4
798 | 562 | 111.2 | 337.1 | 308.2 | 146 | 240.6
799 | 563 | 111.6 | 337.2 | 307.9 | 146.4 | 240.8
800 | 564 | 112 | 337.3 | 308 | 146.9 | 241
801 | 565 | 112.4 | 338.1 | 307.9 | 147.2 | 241.3
802 | 566 | 112.8 | 337.7 | 308 | 147.7 | 241.7
803 | 567 | 113.2 | 337.5 | 308 | 148.1 | 241.8
804 | 568 | 113.5 | 337.3 | 307.8 | 148.6 | 242
805 | 569 | 113.9 | 337 | 307.8 | 149 | 242.3
806 | 570 | 114.3 | 336.9 | 307.6 | 149.5 | 242.4
807 | 571 | 114.7 | 337.2 | 307.5 | 150 | 242.6
808 | 572 | 115.1 | 337.4 | 307.2 | 150.5 | 242.8
809 | 573 | 115.4 | 338.5 | 307.2 | 151 | 243.1
810 | 574 | 115.8 | 339.4 | 307.2 | 151.6 | 243.4
811 | 575 | 116.2 | 340.1 | 307.7 | 152.1 | 243.6
812 | 576 | 116.6 | 341.1 | 308 | 152.6 | 243.9
813 | 577 | 117 | 342 | 308.3 | 153.2 | 244.3
814 | 578 | 117.3 | 342.2 | 308.8 | 153.7 | 244.6
815 | 579 | 117.7 | 341.9 | 309 | 154.1 | 244.9
816 | 580 | 118.1 | 342.1 | 308.6 | 154.6 | 245.4
817 | 581 | 118.5 | 342 | 308.6 | 155.1 | 245.7
818 | 582 | 118.9 | 341.7 | 308.9 | 155.6 | 245.9
819 | 583 | 119.2 | 341.9 | 309.3 | 156.1 | 246.3
820 | 584 | 119.6 | 342.6 | 310.2 | 156.7 | 246.8
821 | 585 | 120 | 343.4 | 310.9 | 157.3 | 247.3
822 | 586 | 120.4 | 343.5 | 312 | 157.8 | 247.9
823 | 587 | 120.8 | 343.7 | 313.2 | 158.4 | 248.4
824 | 588 | 121.2 | 344.2 | 314.3 | 159 | 248.8
825 | 589 | 121.6 | 344.5 | 314.3 | 159.6 | 249
826 | 590 | 122 | 344.8 | 314.9 | 160.2 | 249.2
827 | 591 | 122.3 | 345.7 | 315.7 | 160.6 | 249.6
828 | 592 | 122.7 | 345.7 | 316.7 | 161.2 | 250.1
829 | 593 | 123.1 | 346.1 | 317.6 | 161.7 | 250.6
830 | 594 | 123.5 | 346.7 | 318.2 | 162.3 | 250.9
831 | 595 | 123.8 | 347.7 | 319.1 | 162.9 | 251.3
832 | 596 | 124.2 | 349.2 | 319.7 | 163.6 | 251.8
833 | 597 | 124.6 | 350.3 | 320.3 | 164.2 | 252.2
834 | 598 | 125 | 350.6 | 321.1 | 164.9 | 252.4
835 | 599 | 125.4 | 351.3 | 321.7 | 165.5 | 252.7
836 | 600 | 125.8 | 351.1 | 321.4 | 166 | 253.1
837 | 601 | 126.1 | 350.5 | 321.2 | 166.5 | 253.3
838 | 602 | 126.5 | 350.4 | 320.6 | 166.8 | 253.5
839 | 603 | 126.9 | 350.2 | 320 | 167.3 | 253.8
840 | 604 | 127.2 | 349.9 | 320.1 | 167.8 | 254.1
841 | 605 | 127.6 | 349.9 | 320.9 | 168.3 | 254.7
842 | 606 | 128 | 350.3 | 321.4 | 168.8 | 255.1
843 | 607 | 128.4 | 351.2 | 322.2 | 169.4 | 255.4
844 | 608 | 128.8 | 352.1 | 323 | 170.1 | 255.7
845 | 609 | 129.1 | 352.5 | 323.4 | 170.7 | 256
846 | 610 | 129.5 | 352.3 | 323.9 | 171.2 | 256.2
847 | 611 | 129.9 | 351.8 | 324.7 | 171.7 | 256.3
848 | 612 | 130.3 | 351.4 | 324.6 | 172.1 | 256.4
849 | 613 | 130.6 | 351.1 | 324.1 | 172.6 | 256.7
850 | 614 | 131 | 351 | 323.7 | 173.1 | 257.2
851 | 615 | 131.4 | 352.3 | 324.2 | 173.7 | 257.5
852 | 616 | 131.7 | 356.3 | 324.9 | 174.4 | 257.8
853 | 617 | 132.1 | 356 | 325.5 | 174.9 | 258.1
854 | 618 | 132.5 | 355.6 | 326.2 | 175.3 | 258.4
855 | 619 | 132.9 | 355.3 | 326.5 | 175.8 | 258.7
856 | 620 | 133.2 | 355 | 326.4 | 176.3 | 258.9
857 | 621 | 133.6 | 355.1 | 326.6 | 177 | 259.1
858 | 622 | 134 | 354.9 | 327 | 177.5 | 259.5
859 | 623 | 134.3 | 355 | 327.3 | 178 | 259.9
860 | 624 | 134.7 | 356.1 | 327.6 | 178.6 | 260.3
861 | 625 | 135.1 | 356.5 | 328.7 | 179.2 | 261
862 | 626 | 135.5 | 357 | 329.6 | 179.7 | 261.4
863 | 627 | 135.9 | 356.9 | 329.8 | 180.3 | 261.5
864 | 628 | 136.3 | 357.2 | 330.2 | 180.8 | 261.8
865 | 629 | 136.6 | 357.2 | 331.2 | 181.3 | 262
866 | 630 | 137 | 357 | 331.1 | 181.8 | 262.3
867 | 631 | 137.4 | 357 | 331.1 | 182.3 | 262.7
868 | 632 | 137.8 | 357.2 | 331.4 | 182.8 | 263
869 | 633 | 138.1 | 357.7 | 331.5 | 183.4 | 263.5
870 | 634 | 138.5 | 358.4 | 331.6 | 183.9 | 263.8
871 | 635 | 138.9 | 359 | 331.6 | 184.5 | 264.1
872 | 636 | 139.3 | 359.9 | 332 | 185 | 264.5
873 | 637 | 139.7 | 361 | 332.2 | 185.6 | 264.8
874 | 638 | 140.1 | 361.9 | 332 | 186.1 | 265.1
875 | 639 | 140.4 | 363.1 | 332.5 | 186.7 | 265.5
876 | 640 | 140.8 | 365.9 | 333.5 | 187.4 | 265.9
877 | 641 | 141.2 | 367.6 | 334.3 | 188.2 | 266.4
878 | 642 | 141.6 | 369.4 | 334.8 | 188.9 | 266.8
879 | 643 | 142 | 370.5 | 335.3 | 189.4 | 267.1
880 | 644 | 142.3 | 370.4 | 336.8 | 190 | 267.4
881 | 645 | 142.7 | 370.4 | 337.9 | 190.5 | 267.6
882 | 646 | 143.1 | 370.1 | 338 | 191 | 267.9
883 | 647 | 143.5 | 369.6 | 338.7 | 191.5 | 268.2
884 | 648 | 143.9 | 369.2 | 339 | 191.9 | 268.4
885 | 649 | 144.3 | 368.8 | 340.4 | 192.3 | 268.7
886 | 650 | 144.7 | 368.7 | 340.6 | 192.7 | 269.1
887 | 651 | 145.1 | 368.4 | 340.4 | 193.2 | 269.4
888 | 652 | 145.5 | 368.4 | 340.1 | 193.8 | 269.7
889 | 653 | 145.8 | 368.8 | 339.7 | 194.3 | 269.8
890 | 654 | 146.2 | 368.3 | 339.4 | 194.9 | 269.9
891 | 655 | 146.6 | 368.3 | 338.7 | 195.5 | 270.2
892 | 656 | 147 | 367.4 | 338.2 | 195.9 | 270.3
893 | 657 | 147.4 | 366.3 | 337.8 | 196.4 | 270.3
894 | 658 | 147.7 | 365.2 | 337.5 | 196.7 | 270.4
895 | 659 | 148.1 | 364.7 | 337.3 | 197.2 | 270.9
896 | 660 | 148.5 | 364.6 | 337.1 | 197.8 | 271.2
897 | 661 | 148.9 | 364.9 | 336.9 | 198.4 | 271.4
898 | 662 | 149.3 | 365.8 | 337.5 | 199.1 | 271.8
899 | 663 | 149.7 | 367.8 | 338.5 | 199.8 | 272.2
900 | 664 | 150 | 368.8 | 339 | 200.5 | 272.5
901 | 665 | 150.4 | 369.4 | 339.7 | 201 | 272.7
902 | 666 | 150.8 | 369.7 | 340.1 | 201.6 | 273.1
903 | 667 | 151.2 | 369.7 | 340.2 | 202.2 | 273.3
904 | 668 | 151.6 | 369.6 | 340.9 | 202.6 | 273.5
905 | 669 | 152 | 369.3 | 340.9 | 203.1 | 273.7
906 | 670 | 152.3 | 369.3 | 341.6 | 203.7 | 274
907 | 671 | 152.7 | 370.1 | 342.3 | 204.3 | 274.4
908 | 672 | 153.1 | 370.5 | 343 | 205.1 | 274.6
909 | 673 | 153.5 | 371.7 | 343.8 | 205.8 | 274.9
910 | 674 | 153.9 | 373.3 | 344.9 | 206.5 | 275.2
911 | 675 | 154.3 | 374.7 | 345.2 | 207.2 | 275.6
912 | 676 | 154.7 | 375.2 | 346 | 207.9 | 276.2
913 | 677 | 155.1 | 376.5 | 346.6 | 208.6 | 276.7
914 | 678 | 155.5 | 378.3 | 346.9 | 209.3 | 277.1
915 | 679 | 155.9 | 378.8 | 347.4 | 210.1 | 277.3
916 | 680 | 156.2 | 379.1 | 347.8 | 210.9 | 277.4
917 | 681 | 156.7 | 378.9 | 348.3 | 211.6 | 277.6
918 | 682 | 157.1 | 378.9 | 348.4 | 212.2 | 278
919 | 683 | 157.5 | 379.9 | 348.2 | 213 | 278.3
920 | 684 | 157.9 | 380.6 | 348.2 | 213.8 | 278.6
921 | 685 | 158.3 | 381.1 | 348.4 | 214.4 | 279
922 | 686 | 158.7 | 381.2 | 348.6 | 215.1 | 279.2
923 | 687 | 159.1 | 380.8 | 348.8 | 215.8 | 279.3
924 | 688 | 159.5 | 380.3 | 349.4 | 216.4 | 279.6
925 | 689 | 160 | 380.5 | 350.7 | 217 | 279.8
926 | 690 | 160.4 | 380.6 | 351 | 217.6 | 280.1
927 | 691 | 160.8 | 380.6 | 351.2 | 218.3 | 280.3
928 | 692 | 161.2 | 380.9 | 351 | 219 | 280.6
929 | 693 | 161.7 | 381.4 | 351 | 219.7 | 281
930 | 694 | 162.1 | 382.6 | 351 | 220.4 | 281.5
931 | 695 | 162.5 | 384.3 | 351.1 | 221.3 | 281.8
932 | 696 | 163 | 385.2 | 351 | 222.1 | 282.1
933 | 697 | 163.4 | 385.3 | 351.5 | 222.8 | 282.3
934 | 698 | 163.8 | 385.6 | 352 | 223.6 | 282.7
935 | 699 | 164.3 | 386 | 352.5 | 224.2 | 282.9
936 | 700 | 164.7 | 387 | 352.7 | 224.9 | 283.1
937 | 701 | 165.2 | 387.5 | 352.5 | 225.6 | 283.4
938 | 702 | 165.6 | 386.9 | 352.2 | 226.1 | 283.7
939 | 703 | 166.1 | 386.8 | 352.2 | 226.7 | 284
940 | 704 | 166.5 | 387 | 352.7 | 227.2 | 284.4
941 | 705 | 167 | 386.9 | 352.9 | 227.8 | 284.7
942 | 706 | 167.4 | 388 | 353.7 | 228.5 | 285.1
943 | 707 | 167.9 | 388.9 | 354.4 | 229.2 | 285.4
944 | 708 | 168.3 | 389.5 | 355 | 229.9 | 285.6
945 | 709 | 168.8 | 389.9 | 356 | 230.7 | 285.8
946 | 710 | 169.3 | 390 | 356.6 | 231.6 | 286
947 | 711 | 169.8 | 390.4 | 356.8 | 232.4 | 286.1
948 | 712 | 170.2 | 390.6 | 356.4 | 233.2 | 286.3
949 | 713 | 170.7 | 390.6 | 356.1 | 234 | 286.6
950 | 714 | 171.2 | 391 | 356.1 | 234.8 | 287
951 | 715 | 171.7 | 392.4 | 356 | 235.4 | 287.2
952 | 716 | 172.2 | 392.1 | 356.2 | 236.1 | 287.5
953 | 717 | 172.7 | 392.5 | 356.5 | 236.8 | 287.9
954 | 718 | 173.1 | 393.1 | 356.6 | 237.4 | 288.2
955 | 719 | 173.6 | 393.5 | 357.2 | 238.1 | 288.5
956 | 720 | 174.1 | 393.9 | 358.6 | 238.8 | 288.9
957 | 721 | 174.6 | 394.2 | 360.3 | 239.5 | 289
958 | 722 | 175.1 | 395.1 | 361.7 | 240.2 | 289.3
959 | 723 | 175.7 | 395.8 | 364 | 240.9 | 289.7
960 | 724 | 176.2 | 397 | 366.1 | 241.6 | 290.1
961 | 725 | 176.7 | 398 | 367.3 | 242.4 | 290.4
962 | 726 | 177.2 | 399.1 | 368 | 243.2 | 290.8
963 | 727 | 177.7 | 399.5 | 368.3 | 243.9 | 291
964 | 728 | 178.3 | 398.9 | 368.5 | 244.5 | 291.2
965 | 729 | 178.8 | 398.1 | 368.4 | 245.1 | 291.4
966 | 730 | 179.4 | 398.5 | 368.7 | 245.8 | 291.6
967 | 731 | 179.9 | 397.9 | 368.7 | 246.5 | 291.7
968 | 732 | 180.5 | 397.7 | 368.6 | 247.1 | 292
969 | 733 | 181 | 397.7 | 368 | 247.7 | 292.4
970 | 734 | 181.6 | 397.6 | 367.3 | 248.3 | 292.6
971 | 735 | 182.2 | 397.7 | 366.8 | 248.8 | 293
972 | 736 | 182.8 | 399 | 367.7 | 249.5 | 293.4
973 | 737 | 183.4 | 401.5 | 368.8 | 250.3 | 293.9
974 | 738 | 184 | 402.9 | 369.7 | 251.1 | 294.2
975 | 739 | 184.6 | 404.1 | 371.7 | 251.8 | 294.6
976 | 740 | 185.2 | 404.2 | 372.9 | 252.4 | 295.1
977 | 741 | 185.8 | 404 | 373.1 | 253 | 295.4
978 | 742 | 186.4 | 403.4 | 373.7 | 253.6 | 295.6
979 | 743 | 187 | 402.9 | 374.6 | 254 | 296
980 | 744 | 187.6 | 402.4 | 375.4 | 254.5 | 296.4
981 | 745 | 188.3 | 401.9 | 375.5 | 255 | 296.7
982 | 746 | 188.9 | 401.7 | 374.8 | 255.5 | 297.1
983 | 747 | 189.6 | 401.7 | 373.9 | 256 | 297.3
984 | 748 | 190.2 | 401.5 | 372.9 | 256.6 | 297.4
985 | 749 | 190.8 | 401.8 | 373.2 | 257.2 | 297.5
986 | 750 | 191.5 | 401.8 | 373.1 | 257.7 | 297.8
987 | 751 | 192.2 | 405 | 373 | 258.4 | 298.2
988 | 752 | 192.8 | 404.6 | 373.1 | 259 | 298.5
989 | 753 | 193.5 | 404.6 | 373.5 | 259.5 | 298.9
990 | 754 | 194.2 | 404.8 | 374.4 | 260.2 | 299.4
991 | 755 | 194.9 | 405.5 | 375.1 | 260.8 | 299.7
992 | 756 | 195.6 | 406.1 | 375 | 261.4 | 300.1
993 | 757 | 196.4 | 406.8 | 375.7 | 262.1 | 300.6
994 | 758 | 197.1 | 407.4 | 376.4 | 262.8 | 300.9
995 | 759 | 197.8 | 408.3 | 377.3 | 263.5 | 301.2
996 | 760 | 198.5 | 409.5 | 378.2 | 264.3 | 301.6
997 | 761 | 199.1 | 409.9 | 379 | 265.1 | 301.9
998 | 762 | 199.8 | 410.1 | 379.7 | 265.7 | 302.2
999 | 763 | 200.5 | 410 | 379.7 | 266.3 | 302.5
1000 | 764 | 201.2 | 409.3 | 379.5 | 266.8 | 302.8
1001 | 765 | 201.9 | 409 | 379.5 | 267.3 | 303
1002 | 766 | 202.6 | 409.3 | 380.3 | 267.9 | 303.3
1003 | 767 | 203.3 | 409.2 | 380.8 | 268.4 | 303.6
1004 | 768 | 204 | 409.5 | 380.5 | 268.9 | 304
1005 | 769 | 204.7 | 409.4 | 380.4 | 269.5 | 304.3
1006 | 770 | 205.4 | 409.6 | 380.6 | 270 | 304.7
1007 | 771 | 206.1 | 409.6 | 380.6 | 270.6 | 304.9
1008 | 772 | 206.8 | 409.4 | 380.4 | 271.1 | 305.3
1009 | 773 | 207.5 | 409 | 380.3 | 271.6 | 305.5
1010 | 774 | 208.2 | 408.1 | 379.9 | 272.1 | 305.8
1011 | 775 | 208.9 | 406.9 | 379.4 | 272.5 | 306
1012 | 776 | 209.7 | 405.9 | 379.2 | 272.8 | 306.2
1013 | 777 | 210.4 | 405.4 | 379.1 | 273.1 | 306.4
1014 | 778 | 211.1 | 405.4 | 378.9 | 273.3 | 306.7
1015 | 779 | 211.7 | 404.6 | 378.1 | 273.6 | 306.9
1016 | 780 | 212.4 | 403.6 | 377.9 | 273.8 | 307.1
1017 | 781 | 213 | 402.8 | 377.2 | 274 | 307.3
1018 | 782 | 213.5 | 402.4 | 376.4 | 274.2 | 307.5
1019 | 783 | 214.1 | 401.5 | 376 | 274.5 | 307.6
1020 | 784 | 214.6 | 401.1 | 375.9 | 274.7 | 307.7
1021 | 785 | 215 | 400.7 | 375.9 | 275 | 308
1022 | 786 | 215.5 | 400.5 | 375.9 | 275.3 | 308.4
1023 | 787 | 215.9 | 400.8 | 376.3 | 275.5 | 308.7
1024 | 788 | 216.3 | 402.6 | 376.9 | 275.9 | 309.1
1025 | 789 | 216.7 | 403.8 | 377.5 | 276.2 | 309.5
1026 | 790 | 217.1 | 404 | 378 | 276.5 | 309.8
1027 | 791 | 217.5 | 404.5 | 378.2 | 276.9 | 310.1
1028 | 792 | 217.8 | 404.4 | 378.3 | 277.3 | 310.4
1029 | 793 | 218.2 | 404.1 | 378.6 | 277.6 | 310.6
1030 | 794 | 218.6 | 404.1 | 378.7 | 277.9 | 310.8
1031 | 795 | 219 | 403.6 | 378.1 | 278.3 | 311
1032 | 796 | 219.4 | 402.7 | 378 | 278.6 | 311.2
1033 | 797 | 219.8 | 402.7 | 377.8 | 278.9 | 311.4
1034 | 798 | 220.1 | 402.3 | 377.9 | 279.2 | 311.6
1035 | 799 | 220.5 | 402 | 378 | 279.5 | 311.8
1036 | 800 | 220.9 | 401.9 | 378.3 | 279.9 | 312.1
1037 | 801 | 221.3 | 402.3 | 379.2 | 280.2 | 312.5
1038 | 802 | 221.7 | 403.1 | 380.2 | 280.6 | 312.8
1039 | 803 | 222.1 | 403.6 | 381.6 | 280.9 | 312.9
1040 | 804 | 222.5 | 403.6 | 382.4 | 281.3 | 313.2
1041 | 805 | 222.9 | 404.2 | 383.1 | 281.6 | 313.6
1042 | 806 | 223.3 | 404.6 | 384.1 | 282 | 313.9
1043 | 807 | 223.7 | 404.9 | 385.2 | 282.4 | 314.3
1044 | 808 | 224.1 | 406.3 | 386.4 | 282.8 | 314.6
1045 | 809 | 224.5 | 407.6 | 386.4 | 283.3 | 314.9
1046 | 810 | 224.9 | 408.9 | 386.7 | 283.7 | 315.2
1047 | 811 | 225.3 | 409.2 | 386.7 | 284.1 | 315.3
1048 | 812 | 225.7 | 408.9 | 386.4 | 284.5 | 315.4
1049 | 813 | 226.1 | 408.3 | 386 | 284.8 | 315.6
1050 | 814 | 226.6 | 407.7 | 385.7 | 285.1 | 315.8
1051 | 815 | 227 | 407.5 | 385.9 | 285.5 | 316
1052 | 816 | 227.4 | 407.7 | 386 | 285.8 | 316.3
1053 | 817 | 227.8 | 407.8 | 385.6 | 286.2 | 316.5
1054 | 818 | 228.3 | 408.2 | 385.4 | 286.6 | 316.8
1055 | 819 | 228.7 | 409 | 385.3 | 287 | 317.1
1056 | 820 | 229.1 | 409.2 | 385.4 | 287.4 | 317.4
1057 | 821 | 229.5 | 409.1 | 385.3 | 287.7 | 317.7
1058 | 822 | 229.9 | 409.3 | 385.4 | 288.1 | 318
1059 | 823 | 230.3 | 409.6 | 385.4 | 288.5 | 318.3
1060 | 824 | 230.7 | 409.9 | 385.4 | 288.8 | 318.6
1061 | 825 | 231.1 | 410.2 | 385.1 | 289.2 | 318.8
1062 | 826 | 231.5 | 410.8 | 385.3 | 289.6 | 319.1
1063 | 827 | 231.9 | 411.3 | 385.7 | 290 | 319.4
1064 | 828 | 232.3 | 412.1 | 386.6 | 290.5 | 319.8
1065 | 829 | 232.7 | 412.4 | 387.7 | 290.9 | 320.2
1066 | 830 | 233.1 | 412.7 | 388.3 | 291.3 | 320.4
1067 | 831 | 233.5 | 413.5 | 389.5 | 291.8 | 320.9
1068 | 832 | 233.9 | 415.1 | 391.1 | 292.2 | 321.3
1069 | 833 | 234.3 | 415.5 | 392.2 | 292.6 | 321.6
1070 | 834 | 234.7 | 415.6 | 392.1 | 293 | 321.8
1071 | 835 | 235.1 | 415.1 | 391.8 | 293.3 | 322.2
1072 | 836 | 235.6 | 414.8 | 391.2 | 293.7 | 322.5
1073 | 837 | 236 | 414.6 | 390.5 | 294 | 322.7
1074 | 838 | 236.5 | 414.3 | 390.5 | 294.3 | 323
1075 | 839 | 236.9 | 413.4 | 390.2 | 294.6 | 323.1
1076 | 840 | 237.4 | 413 | 390.3 | 294.9 | 323.3
1077 | 841 | 237.8 | 413.1 | 390.4 | 295.3 | 323.6
1078 | 842 | 238.2 | 413.2 | 390.3 | 295.6 | 323.7
1079 | 843 | 238.6 | 413.7 | 390.8 | 296 | 324.1
1080 | 844 | 239.1 | 414.1 | 390.8 | 296.4 | 324.3
1081 | 845 | 239.5 | 413.8 | 390.5 | 296.7 | 324.3
1082 | 846 | 239.9 | 413.3 | 389.6 | 297 | 324.5
1083 | 847 | 240.4 | 413 | 389.1 | 297.4 | 324.6
1084 | 848 | 240.8 | 412.6 | 388.4 | 297.6 | 324.8
1085 | 849 | 241.2 | 412.3 | 387.8 | 297.9 | 324.9
1086 | 850 | 241.7 | 412.2 | 387.2 | 298.3 | 325.1
1087 | 851 | 242.1 | 412.4 | 387.1 | 298.6 | 325.4
1088 | 852 | 242.4 | 412.7 | 386.5 | 299 | 325.6
1089 | 853 | 242.8 | 412.9 | 386.5 | 299.4 | 325.8
1090 | 854 | 243.2 | 413.4 | 386.5 | 299.8 | 326.1
1091 | 855 | 243.6 | 414.5 | 387.3 | 300.1 | 326.5
1092 | 856 | 243.9 | 415 | 388.6 | 300.5 | 326.6
1093 | 857 | 244.3 | 415.4 | 389.9 | 301 | 326.9
1094 | 858 | 244.6 | 415.7 | 389.7 | 301.4 | 327.1
1095 | 859 | 244.8 | 415.5 | 390.1 | 301.8 | 327.3
1096 | 860 | 245 | 415 | 390.4 | 302.1 | 327.5
1097 | 861 | 245.2 | 414.9 | 390.8 | 302.5 | 327.8
1098 | 862 | 245.6 | 415 | 390.8 | 302.8 | 328.1
1099 | 863 | 246 | 415.1 | 390.7 | 303.2 | 328.3
1100 | 864 | 246.4 | 414.8 | 390.5 | 303.6 | 328.5
1101 | 865 | 246.8 | 414.8 | 390.4 | 303.9 | 328.8
1102 | 866 | 247.3 | 414.6 | 389.9 | 304.3 | 328.9
1103 | 867 | 247.9 | 414.6 | 389.8 | 304.7 | 329
1104 | 868 | 248.5 | 414.8 | 389.2 | 305 | 329.1
1105 | 869 | 249.1 | 414.5 | 388.6 | 305.4 | 329.3
1106 | 870 | 249.7 | 414.3 | 388.1 | 305.7 | 329.5
1107 | 871 | 250.4 | 414.5 | 387.7 | 306.1 | 329.7
1108 | 872 | 251.1 | 414.9 | 387.8 | 306.4 | 329.8
1109 | 873 | 251.8 | 415.4 | 388.7 | 306.8 | 330.2
1110 | 874 | 252.4 | 416.7 | 389.2 | 307.3 | 330.6
1111 | 875 | 253.1 | 417.7 | 389.1 | 307.7 | 330.8
1112 | 876 | 253.8 | 417.9 | 389.2 | 308.2 | 331
1113 | 877 | 254.5 | 418 | 389.8 | 308.6 | 331.2
1114 | 878 | 255.1 | 418.6 | 391.6 | 309 | 331.7
1115 | 879 | 255.7 | 419.4 | 393.2 | 309.5 | 332.2
1116 | 880 | 256.3 | 420.2 | 394 | 310 | 332.5
1117 | 881 | 256.8 | 420.6 | 394.5 | 310.4 | 332.8
1118 | 882 | 257.3 | 419.9 | 394.3 | 310.9 | 332.9
1119 | 883 | 257.8 | 419.3 | 394.4 | 311.3 | 333.2
1120 | 884 | 258.3 | 418.7 | 394.3 | 311.7 | 333.3
1121 | 885 | 258.7 | 418.1 | 394.3 | 312 | 333.3
1122 | 886 | 259.2 | 417.2 | 393.7 | 312.3 | 333.3
1123 | 887 | 259.7 | 417.4 | 393.4 | 312.6 | 333.4
1124 | 888 | 260.3 | 417.7 | 393.4 | 313 | 333.7
1125 | 889 | 260.8 | 418.3 | 393.3 | 313.4 | 333.9
1126 | 890 | 261.3 | 418.2 | 392.7 | 313.8 | 334
1127 | 891 | 261.8 | 418.1 | 392.2 | 314.2 | 334.2
1128 | 892 | 262.2 | 417.9 | 392 | 314.6 | 334.4
1129 | 893 | 262.6 | 418.2 | 392.4 | 315 | 334.8
1130 | 894 | 263 | 419.3 | 392.1 | 315.5 | 335.1
1131 | 895 | 263.5 | 419.9 | 392.2 | 316 | 335.2
1132 | 896 | 263.9 | 419.8 | 393.2 | 316.4 | 335.6
1133 | 897 | 264.3 | 419.9 | 393.6 | 316.9 | 335.8
1134 | 898 | 264.7 | 420.3 | 393.5 | 317.3 | 336
1135 | 899 | 265.1 | 419.7 | 393.1 | 317.7 | 336.2
1136 | 900 | 265.5 | 418.6 | 392.7 | 318 | 336.4
1137 | 901 | 265.9 | 417.5 | 392.6 | 318.3 | 336.6
1138 | 902 | 266.4 | 417.5 | 393.5 | 318.7 | 336.8
1139 | 903 | 267 | 418.4 | 395.8 | 319.2 | 337.4
1140 | 904 | 267.4 | 419.4 | 398 | 319.7 | 338
1141 | 905 | 267.9 | 420 | 398.6 | 320.1 | 338.2
1142 | 906 | 268.3 | 420.9 | 399 | 320.6 | 338.4
1143 | 907 | 268.7 | 421 | 399.8 | 321 | 338.7
1144 | 908 | 269.2 | 420.6 | 400.3 | 321.4 | 338.9
1145 | 909 | 269.6 | 419.8 | 400 | 321.8 | 339.1
1146 | 910 | 269.9 | 419.2 | 400.2 | 322.1 | 339.3
1147 | 911 | 270.3 | 419.2 | 400.9 | 322.5 | 339.6
1148 | 912 | 270.7 | 418.9 | 401 | 322.9 | 339.8
1149 | 913 | 271 | 418.6 | 400.9 | 323.2 | 339.9
1150 | 914 | 271.4 | 418.5 | 400.5 | 323.6 | 340.2
1151 | 915 | 271.7 | 418.6 | 400.2 | 324 | 340.4
1152 | 916 | 272.1 | 418.7 | 399.9 | 324.4 | 340.6
1153 | 917 | 272.5 | 418.6 | 399.4 | 324.7 | 340.8
1154 | 918 | 272.9 | 418.2 | 399 | 325.1 | 341
1155 | 919 | 273.3 | 417.9 | 398.3 | 325.4 | 341.1
1156 | 920 | 273.7 | 417.6 | 398.5 | 325.7 | 341.3
1157 | 921 | 274 | 418.5 | 399.4 | 326.1 | 341.8
1158 | 922 | 274.3 | 419.2 | 399.7 | 326.5 | 341.9
1159 | 923 | 274.6 | 419.6 | 399.9 | 326.9 | 342.1
1160 | 924 | 274.9 | 419.4 | 399.4 | 327.3 | 342.1
1161 | 925 | 275.2 | 418.7 | 398.9 | 327.6 | 342.2
1162 | 926 | 275.5 | 417.9 | 398.4 | 327.9 | 342.3
1163 | 927 | 275.8 | 417.5 | 397.6 | 328.3 | 342.3
1164 | 928 | 276.1 | 417.1 | 396.8 | 328.6 | 342.3
1165 | 929 | 276.5 | 416.4 | 396.2 | 328.9 | 342.2
1166 | 930 | 276.8 | 415.7 | 396.1 | 329.2 | 342.3
1167 | 931 | 277.1 | 415.1 | 396 | 329.4 | 342.4
1168 | 932 | 277.4 | 415.3 | 395.2 | 329.7 | 342.6
1169 | 933 | 277.6 | 415.8 | 395 | 330.1 | 342.7
1170 | 934 | 277.9 | 416 | 394.6 | 330.4 | 342.9
1171 | 935 | 278.2 | 416.3 | 394.5 | 330.8 | 343
1172 | 936 | 278.5 | 416.3 | 395.1 | 331.1 | 343.2
1173 | 937 | 278.7 | 416.4 | 395.3 | 331.4 | 343.4
1174 | 938 | 279 | 416.6 | 394.9 | 331.8 | 343.5
1175 | 939 | 279.2 | 416.7 | 394.9 | 332.1 | 343.6
1176 | 940 | 279.4 | 417 | 395.5 | 332.4 | 343.8
1177 | 941 | 279.6 | 417.6 | 396.3 | 332.9 | 344.1
1178 | 942 | 279.9 | 418.6 | 396.5 | 333.4 | 344.4
1179 | 943 | 280.2 | 419.2 | 396.7 | 334 | 344.5
1180 | 944 | 280.4 | 419.8 | 397.5 | 334.6 | 344.8
1181 | 945 | 280.7 | 420.7 | 398.9 | 335.1 | 345.1
1182 | 946 | 281 | 421.2 | 400.2 | 335.6 | 345.4
1183 | 947 | 281.2 | 421.4 | 400.6 | 336 | 345.7
1184 | 948 | 281.5 | 421.2 | 400.9 | 336.4 | 345.8
1185 | 949 | 281.8 | 420.7 | 400.7 | 336.8 | 346
1186 | 950 | 282 | 420.1 | 400.7 | 337.1 | 346.3
1187 | 951 | 282.3 | 419.8 | 400.9 | 337.4 | 346.5
1188 | 952 | 282.5 | 419.5 | 400.5 | 337.8 | 346.5
1189 | 953 | 282.8 | 419.3 | 400 | 338.1 | 346.7
1190 | 954 | 283 | 418.6 | 399.3 | 338.4 | 346.9
1191 | 955 | 283.3 | 418.7 | 399.2 | 338.8 | 347
1192 | 956 | 283.5 | 419.6 | 399.4 | 339.2 | 347.2
1193 | 957 | 283.7 | 419.3 | 399.2 | 339.4 | 347.3
1194 | 958 | 283.9 | 418.8 | 399 | 339.8 | 347.5
1195 | 959 | 284.1 | 418.2 | 398.4 | 340 | 347.6
1196 | 960 | 284.3 | 417.7 | 397.6 | 340.3 | 347.6
1197 | 961 | 284.6 | 418.6 | 397.1 | 340.6 | 347.6
1198 | 962 | 284.8 | 418.7 | 396.4 | 340.9 | 347.7
1199 | 963 | 285 | 418.5 | 396 | 341.2 | 347.8
1200 | 964 | 285.2 | 418.2 | 395.7 | 341.4 | 347.9
1201 | 965 | 285.4 | 417.4 | 395 | 341.8 | 347.9
1202 | 966 | 285.6 | 416.7 | 394.7 | 342.1 | 347.9
1203 | 967 | 285.8 | 416.9 | 395.2 | 342.4 | 348.2
1204 | 968 | 286 | 417.2 | 395.1 | 342.7 | 348.3
1205 | 969 | 286.2 | 416.9 | 395.3 | 343 | 348.4
1206 | 970 | 286.4 | 416.9 | 396.2 | 343.4 | 348.7
1207 | 971 | 286.6 | 417.4 | 396.5 | 343.7 | 348.9
1208 | 972 | 286.8 | 418.2 | 397.3 | 344.1 | 349.2
1209 | 973 | 287.1 | 418.8 | 397.9 | 344.5 | 349.4
1210 | 974 | 287.3 | 419.4 | 398.1 | 344.8 | 349.6
1211 | 975 | 287.5 | 419.3 | 398.4 | 345.2 | 349.8
1212 | 976 | 287.8 | 419.1 | 398.8 | 345.5 | 350.1
1213 | 977 | 288 | 419.3 | 399.6 | 345.9 | 350.4
1214 | 978 | 288.2 | 419.7 | 400.5 | 346.3 | 350.6
1215 | 979 | 288.4 | 420.3 | 401.7 | 346.7 | 350.8
1216 | 980 | 288.7 | 421.5 | 402.9 | 347.2 | 351
1217 | 981 | 288.9 | 422.5 | 403.8 | 347.6 | 351.3
1218 | 982 | 289.1 | 422.5 | 404.2 | 348 | 351.5
1219 | 983 | 289.4 | 422.1 | 404.3 | 348.3 | 351.5
1220 | 984 | 289.6 | 421.8 | 404.6 | 348.6 | 351.6
1221 | 985 | 289.9 | 421.5 | 404.1 | 348.8 | 351.6
1222 | 986 | 290.2 | 420.8 | 403.5 | 349 | 351.6
1223 | 987 | 290.4 | 420.1 | 403.2 | 349.3 | 351.6
1224 | 988 | 290.6 | 419.7 | 402.5 | 349.5 | 351.7
1225 | 989 | 290.8 | 419.5 | 401.6 | 349.7 | 351.7
1226 | 990 | 291 | 419.4 | 400.6 | 349.9 | 351.8
1227 | 991 | 291.3 | 419.1 | 399.6 | 350.2 | 351.9
1228 | 992 | 291.5 | 418.8 | 399 | 350.4 | 351.9
1229 | 993 | 291.7 | 419 | 398.6 | 350.6 | 352
1230 | 994 | 291.9 | 419 | 398.5 | 350.9 | 352.2
1231 | 995 | 292.1 | 418.9 | 398.6 | 351.2 | 352.3
1232 | 996 | 292.3 | 418.7 | 398.4 | 351.5 | 352.5
1233 | 997 | 292.6 | 418.5 | 398 | 351.8 | 352.5
1234 | 998 | 292.8 | 418.4 | 398.9 | 352.1 | 352.8
1235 | 999 | 293 | 418.6 | 399.6 | 352.4 | 353
1236 | 1000 | 293.2 | 418.5 | 399.7 | 352.6 | 353.1
1237 | 1001 | 293.4 | 418.5 | 400.1 | 352.9 | 353.3
1238 | 1002 | 293.6 | 418.7 | 400.6 | 353.2 | 353.5
1239 | 1003 | 293.8 | 419.3 | 400.9 | 353.5 | 353.7
1240 | 1004 | 294 | 419.6 | 400.9 | 353.8 | 353.8
1241 | 1005 | 294.3 | 419.9 | 401 | 354 | 354
1242 | 1006 | 294.5 | 420.5 | 401.3 | 354.3 | 354.2
1243 | 1007 | 294.7 | 421.3 | 402.4 | 354.7 | 354.4
1244 | 1008 | 294.9 | 422.1 | 403.4 | 355.1 | 354.8
1245 | 1009 | 295.1 | 422.7 | 403.7 | 355.5 | 354.9
1246 | 1010 | 295.4 | 423.3 | 404.1 | 355.9 | 355.1
1247 | 1011 | 295.6 | 423.6 | 404.6 | 356.2 | 355.3
1248 | 1012 | 295.9 | 423.9 | 405.1 | 356.5 | 355.6
1249 | 1013 | 296.1 | 423.7 | 404.7 | 356.8 | 355.8
1250 | 1014 | 296.4 | 423.3 | 404.3 | 357.1 | 355.9
1251 | 1015 | 296.6 | 422.4 | 403.9 | 357.3 | 356
1252 | 1016 | 296.9 | 421.4 | 403.4 | 357.4 | 356.2
1253 | 1017 | 297.1 | 420.2 | 402.6 | 357.6 | 356.3
1254 | 1018 | 297.3 | 419.5 | 402.1 | 357.7 | 356.3
1255 | 1019 | 297.5 | 419 | 402 | 357.8 | 356.4
1256 | 1020 | 297.7 | 418.6 | 401.9 | 358 | 356.4
1257 | 1021 | 297.9 | 418.3 | 401.7 | 358.2 | 356.4
1258 | 1022 | 298.1 | 418.1 | 401.9 | 358.4 | 356.6
1259 | 1023 | 298.3 | 417.7 | 401.4 | 358.6 | 356.7
1260 | 1024 | 298.5 | 417.4 | 400.8 | 358.7 | 356.7
1261 | 1025 | 298.7 | 416.9 | 400.5 | 358.9 | 356.7
1262 | 1026 | 298.9 | 416.8 | 400.2 | 359.1 | 356.8
1263 | 1027 | 299.1 | 417 | 400.2 | 359.3 | 357.1
1264 | 1028 | 299.3 | 417.5 | 400.3 | 359.6 | 357.2
1265 | 1029 | 299.5 | 417.6 | 400.7 | 359.8 | 357.5
1266 | 1030 | 299.7 | 417.5 | 400.8 | 360.1 | 357.6
1267 | 1031 | 299.9 | 417.8 | 400.9 | 360.3 | 357.6
1268 | 1032 | 300.1 | 418.5 | 401.6 | 360.6 | 357.8
1269 | 1033 | 300.4 | 418.9 | 402.1 | 360.9 | 358
1270 | 1034 | 300.6 | 418.9 | 401.4 | 361.2 | 358.1
1271 | 1035 | 300.8 | 419 | 401.1 | 361.4 | 358.1
1272 | 1036 | 301 | 418.7 | 400.6 | 361.6 | 358.1
1273 | 1037 | 301.3 | 418.8 | 400.9 | 361.8 | 358.2
1274 | 1038 | 301.5 | 419.4 | 401 | 362.1 | 358.4
1275 | 1039 | 301.7 | 419.5 | 401.8 | 362.3 | 358.7
1276 | 1040 | 301.9 | 419.6 | 403 | 362.5 | 359.1
1277 | 1041 | 302.2 | 420.1 | 404.3 | 362.8 | 359.4
1278 | 1042 | 302.4 | 420.4 | 405.4 | 363.1 | 359.7
1279 | 1043 | 302.6 | 420.5 | 406.4 | 363.4 | 359.9
1280 | 1044 | 302.9 | 420.9 | 406.1 | 363.6 | 360.1
1281 | 1045 | 303.1 | 421.1 | 406.2 | 363.9 | 360.3
1282 | 1046 | 303.3 | 421.6 | 406.6 | 364.2 | 360.5
1283 | 1047 | 303.6 | 421.8 | 406.5 | 364.5 | 360.7
1284 | 1048 | 303.8 | 421.8 | 406.4 | 364.8 | 361
1285 | 1049 | 304.1 | 421.8 | 406.2 | 365.1 | 361.2
1286 | 1050 | 304.3 | 421.5 | 406.1 | 365.4 | 361.4
1287 | 1051 | 304.6 | 421.1 | 406.3 | 365.6 | 361.7
1288 | 1052 | 304.8 | 421.5 | 406.7 | 365.9 | 361.9
1289 | 1053 | 305.1 | 422.4 | 407.4 | 366.2 | 362.2
1290 | 1054 | 305.3 | 423.5 | 407.9 | 366.6 | 362.4
1291 | 1055 | 305.6 | 425 | 408.2 | 366.9 | 362.6
1292 | 1056 | 305.9 | 426.3 | 408.5 | 367.3 | 362.8
1293 | 1057 | 306.1 | 427.3 | 408.9 | 367.6 | 363.1
1294 | 1058 | 306.4 | 427.7 | 409 | 368 | 363.4
1295 | 1059 | 306.6 | 428.1 | 408.6 | 368.4 | 363.5
1296 | 1060 | 306.9 | 428.3 | 408.4 | 368.7 | 363.6
1297 | 1061 | 307.2 | 428 | 408 | 369 | 363.8
1298 | 1062 | 307.5 | 428 | 408.2 | 369.3 | 364
1299 | 1063 | 307.7 | 428.2 | 408.3 | 369.7 | 364.1
1300 | 1064 | 308 | 428.6 | 408.2 | 370 | 364.1
1301 | 1065 | 308.3 | 428.2 | 407.5 | 370.2 | 364.2
1302 | 1066 | 308.5 | 428 | 406.7 | 370.5 | 364.2
1303 | 1067 | 308.8 | 427.1 | 406.1 | 370.6 | 364.2
1304 | 1068 | 309.1 | 426.2 | 406.2 | 370.8 | 364.2
1305 | 1069 | 309.3 | 425.9 | 406.3 | 371 | 364.2
1306 | 1070 | 309.6 | 425.7 | 405.5 | 371.2 | 364.1
1307 | 1071 | 309.8 | 425.1 | 404.5 | 371.4 | 364.1
1308 | 1072 | 310 | 424.3 | 403.5 | 371.5 | 364
1309 | 1073 | 310.3 | 423.9 | 403 | 371.7 | 364.1
1310 | 1074 | 310.5 | 423.5 | 402.2 | 371.9 | 364.1
1311 | 1075 | 310.7 | 423.1 | 401.3 | 372.1 | 363.9
1312 | 1076 | 310.9 | 422.9 | 400.9 | 372.3 | 363.9
1313 | 1077 | 311.2 | 422.6 | 400.6 | 372.4 | 364
1314 | 1078 | 311.4 | 422.2 | 400.3 | 372.6 | 364
1315 | 1079 | 311.6 | 421.6 | 399.6 | 372.8 | 363.9
1316 | 1080 | 311.5 | 421.3 | 400 | 372.8 | 363.6
1317 | 1081 | 312.1 | 421 | 399 | 373.2 | 364.1
1318 | 1082 | 312.3 | 420.9 | 399.2 | 373.4 | 364.2
1319 | 1083 | 312.5 | 420.8 | 399.9 | 373.7 | 364.4
1320 | 1084 | 312.8 | 421.2 | 400.6 | 373.9 | 364.6
1321 | 1085 | 313.1 | 421.3 | 400.3 | 374.1 | 364.5
1322 | 1086 | 313.3 | 421.1 | 399.6 | 374.3 | 364.4
1323 | 1087 | 313.5 | 420.8 | 399.3 | 374.4 | 364.4
1324 | 1088 | 313.8 | 420.1 | 399.5 | 374.4 | 364.6
1325 | 1089 | 314 | 419.9 | 399.6 | 374.6 | 364.7
1326 | 1090 | 314.2 | 419.9 | 398.8 | 374.8 | 364.6
1327 | 1091 | 314.4 | 420 | 398.8 | 375 | 364.6
1328 | 1092 | 314.7 | 420.4 | 399.1 | 375.2 | 364.9
1329 | 1093 | 314.9 | 421.2 | 399.9 | 375.5 | 365
1330 | 1094 | 315.2 | 422.1 | 400.9 | 375.9 | 365.2
1331 | 1095 | 315.4 | 423.2 | 401.7 | 376.3 | 365.4
1332 | 1096 | 315.7 | 425 | 402.8 | 376.7 | 365.7
1333 | 1097 | 316 | 426.7 | 403.6 | 377.2 | 366
1334 | 1098 | 316.3 | 427.5 | 403.7 | 377.6 | 366.1
1335 | 1099 | 316.6 | 428.6 | 404.3 | 378 | 366.3
1336 | 1100 | 317 | 429.9 | 405.4 | 378.4 | 366.7
1337 | 1101 | 317.3 | 430.1 | 406.1 | 378.7 | 367.1
1338 | 1102 | 317.6 | 430.5 | 406.5 | 379 | 367.3
1339 | 1103 | 317.9 | 430.3 | 406.5 | 379.2 | 367.4
1340 | 1104 | 318.2 | 429.6 | 406.4 | 379.4 | 367.5
1341 | 1105 | 318.5 | 430.2 | 406.8 | 379.7 | 367.7
1342 | 1106 | 318.7 | 429.6 | 407.1 | 379.9 | 367.9
1343 | 1107 | 319 | 429.3 | 407.6 | 380.1 | 368.1
1344 | 1108 | 319.3 | 429.3 | 407.8 | 380.4 | 368.2
1345 | 1109 | 319.5 | 429.2 | 407.9 | 380.5 | 368.4
1346 | 1110 | 319.8 | 428.9 | 407.8 | 380.7 | 368.5
1347 | 1111 | 320.1 | 428.6 | 407.4 | 380.9 | 368.5
1348 | 1112 | 320.4 | 428.5 | 406.8 | 381 | 368.7
1349 | 1113 | 320.6 | 428.3 | 406.4 | 381.2 | 368.8
1350 | 1114 | 320.9 | 428 | 406.2 | 381.3 | 368.9
1351 | 1115 | 321.2 | 427.8 | 405.8 | 381.4 | 369.1
1352 | 1116 | 321.4 | 427.4 | 405.1 | 381.6 | 369.1
1353 | 1117 | 321.7 | 426.7 | 404.4 | 381.7 | 369.2
1354 | 1118 | 321.9 | 426.1 | 404.3 | 381.8 | 369.4
1355 | 1119 | 322.2 | 425.4 | 403.8 | 381.9 | 369.3
1356 | 1120 | 322.4 | 425 | 403.4 | 382 | 369.3
1357 | 1121 | 322.7 | 424.9 | 402.9 | 382.1 | 369.5
1358 | 1122 | 322.9 | 424.8 | 402.9 | 382.3 | 369.6
1359 | 1123 | 323.1 | 425.2 | 403.2 | 382.5 | 369.7
1360 | 1124 | 323.4 | 425.8 | 403.3 | 382.7 | 369.8
1361 | 1125 | 323.6 | 426.1 | 403.4 | 382.9 | 369.9
1362 | 1126 | 323.9 | 426.1 | 403.5 | 383.1 | 370
1363 | 1127 | 324.2 | 426 | 403.6 | 383.3 | 370.1
1364 | 1128 | 324.4 | 426.3 | 403.9 | 383.4 | 370.2
1365 | 1129 | 324.7 | 426.8 | 404.5 | 383.6 | 370.3
1366 | 1130 | 324.9 | 427.3 | 405.5 | 383.8 | 370.5
1367 | 1131 | 325.2 | 427.8 | 406.6 | 384.1 | 370.6
1368 | 1132 | 325.5 | 428.4 | 406.9 | 384.4 | 370.8
1369 | 1133 | 325.8 | 429.1 | 406.6 | 384.5 | 370.9
1370 | 1134 | 326.1 | 429.7 | 406.5 | 384.8 | 371
1371 | 1135 | 326.3 | 430.8 | 407.3 | 385 | 371.4
1372 | 1136 | 326.6 | 431.4 | 408 | 385.3 | 371.6
1373 | 1137 | 326.9 | 431.6 | 407.9 | 385.6 | 371.7
1374 | 1138 | 327.1 | 431.9 | 407.9 | 385.8 | 371.9
1375 | 1139 | 327.4 | 432 | 407.9 | 386.1 | 372.2
1376 | 1140 | 327.7 | 432.5 | 407.9 | 386.2 | 372.3
1377 | 1141 | 328 | 432.1 | 407.5 | 386.4 | 372.4
1378 | 1142 | 328.2 | 431.2 | 407.3 | 386.5 | 372.6
1379 | 1143 | 328.5 | 430.4 | 407.2 | 386.6 | 372.6
1380 | 1144 | 328.8 | 430.2 | 407.4 | 386.8 | 372.7
1381 | 1145 | 329 | 430.2 | 407.9 | 387 | 372.9
1382 | 1146 | 329.3 | 430.9 | 408.1 | 387.2 | 373
1383 | 1147 | 329.6 | 431.1 | 408 | 387.4 | 373.1
1384 | 1148 | 329.9 | 431.3 | 407.6 | 387.5 | 373.2
1385 | 1149 | 330.2 | 431.9 | 407 | 387.7 | 373.2
1386 | 1150 | 330.5 | 432.9 | 406.1 | 387.8 | 373.3
1387 | 1151 | 330.7 | 433.2 | 405.4 | 387.9 | 373.2
1388 | 1152 | 331 | 432.7 | 405.7 | 388 | 373.4
1389 | 1153 | 331.2 | 432.2 | 406.9 | 388.1 | 373.5
1390 | 1154 | 331.5 | 431.3 | 407.9 | 388.2 | 373.6
1391 | 1155 | 331.7 | 430.8 | 409 | 388.3 | 373.8
1392 | 1156 | 332 | 430.6 | 409.6 | 388.5 | 374
1393 | 1157 | 332.3 | 430.6 | 409.9 | 388.8 | 374.1
1394 | 1158 | 332.5 | 430.7 | 410.8 | 389 | 374.2
1395 | 1159 | 332.8 | 430.7 | 412.4 | 389.2 | 374.4
1396 | 1160 | 333 | 430.9 | 412.7 | 389.4 | 374.7
1397 | 1161 | 333.3 | 431.2 | 412.2 | 389.6 | 374.7
1398 | 1162 | 333.6 | 432.2 | 411.4 | 389.7 | 374.7
1399 | 1163 | 333.9 | 432.2 | 410.9 | 389.8 | 374.8
1400 | 1164 | 334.2 | 430.7 | 410.6 | 389.9 | 374.9
1401 | 1165 | 334.4 | 429.7 | 409.7 | 390 | 374.8
1402 | 1166 | 334.7 | 428.6 | 409.4 | 390 | 374.7
1403 | 1167 | 334.9 | 427.6 | 410.2 | 390.1 | 374.6
1404 | 1168 | 335.2 | 426.6 | 409.4 | 390.1 | 374.5
1405 | 1169 | 335.4 | 425.8 | 408.4 | 390.2 | 374.5
1406 | 1170 | 335.7 | 425.5 | 407.2 | 390.2 | 374.4
1407 | 1171 | 335.9 | 425.6 | 406.6 | 390.2 | 374.5
1408 | 1172 | 336.2 | 425.1 | 406 | 390.3 | 374.4
1409 | 1173 | 336.4 | 424.3 | 405.7 | 390.3 | 374.3
1410 | 1174 | 336.6 | 423.5 | 405.4 | 390.3 | 374.4
1411 | 1175 | 336.8 | 423.1 | 406.3 | 390.4 | 374.7
1412 | 1176 | 337 | 423.3 | 406.7 | 390.5 | 374.8
1413 | 1177 | 337.3 | 423.1 | 406.4 | 390.6 | 374.8
1414 | 1178 | 337.5 | 423 | 407.2 | 390.7 | 375
1415 | 1179 | 337.7 | 423.8 | 408.5 | 390.8 | 375.3
1416 | 1180 | 338 | 424.3 | 409 | 390.9 | 375.4
1417 | 1181 | 338.2 | 424.9 | 408.7 | 391 | 375.6
1418 | 1182 | 338.5 | 425.7 | 408.8 | 391.1 | 375.7
1419 | 1183 | 338.7 | 426.3 | 408.8 | 391.1 | 375.7
1420 | 1184 | 338.9 | 426.5 | 409 | 391.2 | 375.9
1421 | 1185 | 339.1 | 426.4 | 409.2 | 391.3 | 376
1422 | 1186 | 339.3 | 426.5 | 409.2 | 391.4 | 376.2
1423 | 1187 | 339.5 | 426.2 | 409 | 391.4 | 376.2
1424 | 1188 | 339.8 | 426.3 | 409 | 391.5 | 376.4
1425 | 1189 | 340.1 | 427 | 409 | 391.6 | 376.5
1426 | 1190 | 340.3 | 427.9 | 409.9 | 391.7 | 376.7
1427 | 1191 | 340.5 | 428.7 | 410.8 | 391.8 | 377
1428 | 1192 | 340.8 | 429.2 | 411.5 | 392 | 377.2
1429 | 1193 | 341.1 | 429.7 | 412.5 | 392.1 | 377.4
1430 | 1194 | 341.3 | 430.9 | 413.7 | 392.4 | 377.8
1431 | 1195 | 341.6 | 431.8 | 414.6 | 392.5 | 377.9
1432 | 1196 | 341.8 | 432.4 | 415.1 | 392.7 | 378.1
1433 | 1197 | 342.1 | 432.7 | 415.3 | 392.8 | 378.3
1434 | 1198 | 342.3 | 432.7 | 414.6 | 392.8 | 378.4
1435 | 1199 | 342.6 | 432.6 | 413.7 | 392.9 | 378.6
1436 | 1200 | 342.8 | 432.7 | 413.3 | 392.9 | 378.7
1437 | 1201 | 343 | 432.8 | 413.5 | 393 | 378.9
1438 | 1202 | 343.3 | 432.5 | 413.9 | 393 | 379.2
1439 | 1203 | 343.5 | 432 | 414 | 393.1 | 379.2
1440 | 1204 | 343.7 | 431.3 | 413.8 | 393.1 | 379.3
1441 | 1205 | 343.9 | 430.5 | 413.8 | 393.2 | 379.4
1442 | 1206 | 344.1 | 429.7 | 413.3 | 393.2 | 379.4
1443 | 1207 | 344.3 | 428.8 | 412.9 | 393.2 | 379.4
1444 | 1208 | 344.5 | 427.8 | 412.7 | 393.3 | 379.5
1445 | 1209 | 344.8 | 427.3 | 412.1 | 393.3 | 379.5
1446 | 1210 | 345 | 427.1 | 411.6 | 393.4 | 379.5
1447 | 1211 | 345.3 | 426.7 | 411.2 | 393.5 | 379.5
1448 | 1212 | 345.6 | 426.2 | 411.2 | 393.5 | 379.7
1449 | 1213 | 345.8 | 425.9 | 411.1 | 393.6 | 379.8
1450 | 1214 | 346.1 | 425.5 | 411.1 | 393.6 | 379.8
1451 | 1215 | 346.4 | 425 | 411.3 | 393.7 | 379.8
1452 | 1216 | 346.7 | 424.9 | 411.5 | 393.7 | 379.9
1453 | 1217 | 347 | 425.4 | 410.9 | 393.8 | 379.9
1454 | 1218 | 347.3 | 425.5 | 410.5 | 393.9 | 379.9
1455 | 1219 | 347.5 | 425.5 | 410.2 | 394 | 380
1456 | 1220 | 347.8 | 425.7 | 410 | 394.2 | 380.1
1457 | 1221 | 348.1 | 425.9 | 409.8 | 394.3 | 380.2
1458 | 1222 | 348.4 | 426.3 | 410.4 | 394.5 | 380.3
1459 | 1223 | 348.7 | 426.5 | 410.1 | 394.6 | 380.4
1460 | 1224 | 348.9 | 426 | 409.9 | 394.7 | 380.5
1461 | 1225 | 349.2 | 426.1 | 410.1 | 394.8 | 380.6
1462 | 1226 | 349.5 | 426.3 | 410.6 | 394.9 | 380.7
1463 | 1227 | 349.7 | 426.5 | 411.1 | 395 | 380.8
1464 | 1228 | 350 | 426.6 | 411.9 | 395.1 | 380.8
1465 | 1229 | 350.2 | 427.7 | 413 | 395.2 | 381.1
1466 | 1230 | 350.5 | 429 | 413.4 | 395.3 | 381.4
1467 | 1231 | 350.7 | 430 | 413.6 | 395.5 | 381.6
1468 | 1232 | 350.9 | 431 | 414.1 | 395.6 | 381.9
1469 | 1233 | 351.2 | 431.6 | 414.8 | 395.8 | 382.1
1470 | 1234 | 351.4 | 432.1 | 415 | 395.9 | 382.2
1471 | 1235 | 351.7 | 432.1 | 415.3 | 396 | 382.4
1472 | 1236 | 351.9 | 431.7 | 415.6 | 396.1 | 382.6
1473 | 1237 | 352.2 | 431.3 | 415.7 | 396.2 | 382.6
1474 | 1238 | 352.4 | 430.7 | 415.3 | 396.3 | 382.7
1475 | 1239 | 352.6 | 430.2 | 415.6 | 396.4 | 382.9
1476 | 1240 | 352.9 | 430.3 | 415.8 | 396.4 | 383.1
1477 | 1241 | 353.1 | 430 | 413.6 | 396.5 | 383.2
1478 | 1242 | 353.3 | 428.9 | 412.9 | 396.5 | 383
1479 | 1243 | 353.5 | 427.9 | 412.6 | 396.5 | 383.1
1480 | 1244 | 353.7 | 427.3 | 412.9 | 396.6 | 383.4
1481 | 1245 | 353.9 | 428 | 413.2 | 396.7 | 383.6
1482 | 1246 | 354.1 | 428.5 | 413.6 | 396.8 | 383.7
1483 | 1247 | 354.4 | 429.2 | 414.1 | 397 | 383.8
1484 | 1248 | 354.6 | 429.8 | 414.6 | 397.1 | 384
1485 | 1249 | 354.9 | 430.6 | 415.2 | 397.3 | 384.2
1486 | 1250 | 355.1 | 431.8 | 416 | 397.5 | 384.4
1487 | 1251 | 355.4 | 432.2 | 416.6 | 397.7 | 384.7
1488 | 1252 | 355.7 | 432.3 | 416.9 | 397.9 | 384.9
1489 | 1253 | 356 | 432.4 | 416.9 | 398.1 | 385
1490 | 1254 | 356.2 | 432.4 | 416.8 | 398.3 | 385.2
1491 | 1255 | 356.5 | 432.6 | 417 | 398.4 | 385.4
1492 | 1256 | 356.8 | 433.2 | 417.3 | 398.6 | 385.6
1493 | 1257 | 357.1 | 433.2 | 417.9 | 398.7 | 385.6
1494 | 1258 | 357.3 | 433.5 | 417.6 | 398.8 | 385.6
1495 | 1259 | 357.6 | 433.7 | 418.4 | 398.9 | 385.7
1496 | 1260 | 357.9 | 433.8 | 418.5 | 399.1 | 385.8
1497 | 1261 | 358.2 | 434 | 418.4 | 399.3 | 385.9
1498 | 1262 | 358.4 | 433.8 | 418.2 | 399.5 | 386
1499 | 1263 | 358.7 | 433.8 | 418.5 | 399.7 | 386.3
1500 | 1264 | 359.1 | 434 | 418.9 | 399.9 | 386.6
1501 | 1265 | 359.4 | 434.2 | 418.9 | 400.1 | 386.6
1502 | 1266 | 359.7 | 434.6 | 419 | 400.4 | 386.7
1503 | 1267 | 360 | 435.1 | 419.9 | 400.6 | 387.1
1504 | 1268 | 360.4 | 436.1 | 420.9 | 400.8 | 387.5
1505 | 1269 | 360.7 | 436.9 | 421.7 | 401.1 | 387.9
1506 | 1270 | 361.1 | 438.6 | 422.2 | 401.4 | 388.1
1507 | 1271 | 361.5 | 439.4 | 422.3 | 401.7 | 388.2
1508 | 1272 | 361.8 | 439.9 | 422.1 | 402 | 388.3
1509 | 1273 | 362.2 | 439.9 | 421.7 | 402.3 | 388.4
1510 | 1274 | 362.6 | 439.8 | 421.4 | 402.5 | 388.5
1511 | 1275 | 362.9 | 439.5 | 421.6 | 402.7 | 388.6
1512 | 1276 | 363.3 | 439.1 | 421.7 | 402.8 | 388.7
1513 | 1277 | 363.7 | 439.1 | 422 | 403 | 388.8
1514 | 1278 | 364 | 438.7 | 422.1 | 403.2 | 389.2
1515 | 1279 | 364.4 | 439.2 | 422.2 | 403.4 | 389.4
1516 | 1280 | 364.7 | 439.4 | 422.4 | 403.6 | 389.6
1517 | 1281 | 365.1 | 439.5 | 422.6 | 403.8 | 389.8
1518 | 1282 | 365.5 | 439.6 | 423.7 | 404 | 390
1519 | 1283 | 365.8 | 440.1 | 424.3 | 404.3 | 390.3
1520 | 1284 | 366.2 | 441.3 | 425.2 | 404.6 | 390.6
1521 | 1285 | 366.6 | 442.9 | 426.2 | 404.8 | 390.9
1522 | 1286 | 367 | 443.7 | 426.6 | 405.1 | 391
1523 | 1287 | 367.4 | 443.3 | 426.7 | 405.4 | 391
1524 | 1288 | 367.8 | 443 | 426.3 | 405.7 | 391
1525 | 1289 | 368.3 | 442.5 | 426 | 405.9 | 391.2
1526 | 1290 | 368.8 | 442.7 | 426.4 | 406.2 | 391.3
1527 | 1291 | 369.2 | 443.9 | 426.9 | 406.5 | 391.4
1528 | 1292 | 369.7 | 444.9 | 426.8 | 406.8 | 391.4
1529 | 1293 | 370.2 | 445.6 | 426.5 | 407.1 | 391.5
1530 | 1294 | 370.7 | 445.8 | 426.2 | 407.4 | 391.6
1531 | 1295 | 371.1 | 446.2 | 426.6 | 407.7 | 391.8
1532 | 1296 | 371.6 | 446.8 | 427.5 | 408 | 391.9
1533 | 1297 | 372.1 | 447.8 | 429.3 | 408.2 | 392.2
1534 | 1298 | 372.6 | 449.1 | 429.8 | 408.5 | 392.4
1535 | 1299 | 373 | 449.5 | 430.8 | 408.8 | 392.7
1536 | 1300 | 373.5 | 449.9 | 431.2 | 409.1 | 393
1537 | 1301 | 374 | 449.6 | 431.3 | 409.3 | 393.1
1538 | 1302 | 374.5 | 449.8 | 431.2 | 409.6 | 393.3
1539 | 1303 | 375 | 450.1 | 431.1 | 409.9 | 393.4
1540 | 1304 | 375.4 | 450.3 | 430.6 | 410.1 | 393.5
1541 | 1305 | 375.9 | 450.2 | 430 | 410.3 | 393.4
1542 | 1306 | 376.3 | 450.4 | 429.4 | 410.5 | 393.4
1543 | 1307 | 376.8 | 450 | 429 | 410.6 | 393.6
1544 | 1308 | 377.2 | 448.9 | 429 | 410.7 | 393.7
1545 | 1309 | 377.6 | 448 | 428.3 | 410.9 | 393.7
1546 | 1310 | 378.1 | 447.1 | 427.6 | 411.1 | 393.6
1547 | 1311 | 378.5 | 446.5 | 427.2 | 411.2 | 393.5
1548 | 1312 | 378.9 | 446.9 | 426 | 411.3 | 393.4
1549 | 1313 | 379.3 | 447.1 | 424.8 | 411.4 | 393.5
1550 | 1314 | 379.7 | 446.9 | 423.7 | 411.6 | 393.4
1551 | 1315 | 380.2 | 446.3 | 422.8 | 411.7 | 393.4
1552 | 1316 | 380.6 | 445.5 | 422 | 411.9 | 393.4
1553 | 1317 | 381 | 445.2 | 421.7 | 412 | 393.5
1554 | 1318 | 381.5 | 445.8 | 421.9 | 412.3 | 393.8
1555 | 1319 | 381.9 | 446.5 | 422.3 | 412.5 | 393.9
1556 | 1320 | 382.4 | 446.9 | 422.3 | 412.8 | 394
1557 | 1321 | 382.8 | 447.3 | 421.8 | 413 | 394
1558 | 1322 | 383.3 | 447.3 | 421.3 | 413.2 | 394.1
1559 | 1323 | 383.7 | 447.1 | 420.6 | 413.4 | 394.2
1560 | 1324 | 384.1 | 446.8 | 419.9 | 413.6 | 394.1
1561 | 1325 | 384.6 | 446.8 | 419.8 | 413.8 | 394.2
1562 | 1326 | 385 | 446.6 | 419.7 | 414 | 394.2
1563 | 1327 | 385.4 | 446.7 | 419.7 | 414.2 | 394.3
1564 | 1328 | 385.9 | 447.3 | 420.7 | 414.3 | 394.6
1565 | 1329 | 386.3 | 448.2 | 421.8 | 414.5 | 394.8
1566 | 1330 | 386.7 | 449.1 | 422 | 414.8 | 395.1
1567 | 1331 | 387.2 | 449.9 | 422.6 | 415.1 | 395.4
1568 | 1332 | 387.6 | 450.7 | 423.3 | 415.4 | 395.5
1569 | 1333 | 388.1 | 451.1 | 423.9 | 415.7 | 395.7
1570 | 1334 | 388.5 | 451.3 | 424.7 | 415.9 | 395.9
1571 | 1335 | 389 | 450.9 | 425.2 | 416.1 | 395.9
1572 | 1336 | 389.4 | 451.1 | 425.3 | 416.3 | 396.1
1573 | 1337 | 389.8 | 451.6 | 425.6 | 416.4 | 396.3
1574 | 1338 | 390.1 | 451.8 | 425.6 | 416.6 | 396.5
1575 | 1339 | 390.5 | 451.9 | 425.6 | 416.7 | 396.6
1576 | 1340 | 390.9 | 451.7 | 426.5 | 416.9 | 396.9
1577 | 1341 | 391.3 | 451.6 | 426.2 | 417.1 | 397
1578 | 1342 | 391.7 | 451.5 | 425.6 | 417.3 | 397.1
1579 | 1343 | 392 | 451.5 | 425.8 | 417.4 | 397.3
1580 | 1344 | 392.4 | 452.1 | 427.1 | 417.6 | 397.6
1581 | 1345 | 392.7 | 452.2 | 427.5 | 417.8 | 397.6
1582 | 1346 | 393.1 | 452.4 | 428.1 | 417.9 | 397.7
1583 | 1347 | 393.4 | 452.2 | 428.1 | 418 | 397.9
1584 | 1348 | 393.7 | 451.2 | 427.7 | 418.1 | 398
1585 | 1349 | 394 | 450.3 | 427.2 | 418.2 | 397.9
1586 | 1350 | 394.3 | 449.6 | 426.9 | 418.2 | 398
1587 | 1351 | 394.6 | 449.2 | 426.3 | 418.3 | 398.1
1588 | 1352 | 395 | 449.4 | 426.6 | 418.5 | 398.2
1589 | 1353 | 395.3 | 449.2 | 426.6 | 418.6 | 398.2
1590 | 1354 | 395.6 | 449.3 | 426.2 | 418.7 | 398.2
1591 | 1355 | 395.9 | 449.6 | 425.6 | 418.9 | 398.1
1592 | 1356 | 396.3 | 449.7 | 425.6 | 419.1 | 398.2
1593 | 1357 | 396.6 | 449.7 | 425.6 | 419.2 | 398.2
1594 | 1358 | 396.9 | 449.4 | 425.9 | 419.4 | 398.2
1595 | 1359 | 397.2 | 449.9 | 426.3 | 419.6 | 398.4
1596 | 1360 | 397.6 | 451 | 425.9 | 419.8 | 398.5
1597 | 1361 | 397.9 | 451.5 | 425 | 420 | 398.5
1598 | 1362 | 398.2 | 451.4 | 424.3 | 420.1 | 398.5
1599 | 1363 | 398.6 | 451.3 | 424.2 | 420.3 | 398.6
1600 | 1364 | 398.8 | 451 | 423.9 | 420.4 | 398.7
1601 | 1365 | 399.1 | 450.7 | 423.6 | 420.5 | 398.8
1602 | 1366 | 399.4 | 450.3 | 423.2 | 420.6 | 398.8
1603 | 1367 | 399.7 | 450 | 423.3 | 420.7 | 398.9
1604 | 1368 | 400 | 450 | 423.6 | 420.8 | 399.1
1605 | 1369 | 400.2 | 450.3 | 423.2 | 420.9 | 399.2
1606 | 1370 | 400.6 | 451.2 | 422.8 | 421.2 | 399
1607 | 1371 | 400.9 | 451.6 | 422.4 | 421.3 | 399.1
1608 | 1372 | 401.2 | 452.4 | 422.4 | 421.4 | 399.3
1609 | 1373 | 401.5 | 453.1 | 422.6 | 421.6 | 399.4
1610 | 1374 | 401.8 | 454.4 | 423 | 421.8 | 399.5
1611 | 1375 | 402.1 | 454.8 | 422.8 | 422.1 | 399.5
1612 | 1376 | 402.5 | 454.7 | 422.4 | 422.3 | 399.6
1613 | 1377 | 402.8 | 454.5 | 423 | 422.6 | 399.7
1614 | 1378 | 403.2 | 454.3 | 423.8 | 422.7 | 399.7
1615 | 1379 | 403.5 | 453.7 | 424.6 | 422.9 | 399.8
1616 | 1380 | 403.7 | 453.5 | 424.9 | 422.9 | 399.8
1617 | 1381 | 404 | 453 | 424.5 | 423 | 399.8
1618 | 1382 | 404.2 | 452.3 | 424 | 423.1 | 399.8
1619 | 1383 | 404.5 | 451.8 | 423.2 | 423.2 | 399.7
1620 | 1384 | 404.7 | 451.4 | 422.3 | 423.2 | 399.6
1621 | 1385 | 405 | 451.3 | 421.3 | 423.3 | 399.5
1622 | 1386 | 405.2 | 450.7 | 420.6 | 423.4 | 399.5
1623 | 1387 | 405.4 | 449.8 | 420.3 | 423.4 | 399.5
1624 | 1388 | 405.6 | 448.8 | 420 | 423.5 | 399.4
1625 | 1389 | 405.9 | 448.2 | 419.9 | 423.6 | 399.4
1626 | 1390 | 406.1 | 448.2 | 420.4 | 423.7 | 399.5
1627 | 1391 | 406.4 | 448.3 | 420.6 | 423.9 | 399.6
1628 | 1392 | 406.6 | 448.6 | 421.1 | 424 | 399.8
1629 | 1393 | 406.9 | 448.7 | 420.9 | 424.2 | 399.9
1630 | 1394 | 407.1 | 449 | 421.1 | 424.3 | 400.1
1631 | 1395 | 407.3 | 449.1 | 422 | 424.5 | 400.3
1632 | 1396 | 407.5 | 449.1 | 422.7 | 424.6 | 400.5
1633 | 1397 | 407.8 | 449.3 | 423.7 | 424.7 | 400.7
1634 | 1398 | 408 | 449.6 | 424.2 | 424.9 | 400.8
1635 | 1399 | 408.2 | 450.2 | 424.9 | 425 | 400.9
1636 | 1400 | 408.5 | 450.5 | 425.6 | 425.2 | 401
1637 | 1401 | 408.7 | 451.1 | 426.8 | 425.3 | 401.2
1638 | 1402 | 409 | 452.2 | 427.3 | 425.5 | 401.4
1639 | 1403 | 409.2 | 453.2 | 427.8 | 425.7 | 401.6
1640 | 1404 | 409.5 | 454.5 | 428.8 | 425.9 | 401.9
1641 | 1405 | 409.8 | 455.6 | 429.7 | 426.2 | 402.1
1642 | 1406 | 410 | 455.9 | 429.8 | 426.4 | 402.2
1643 | 1407 | 410.3 | 455.6 | 430.2 | 426.6 | 402.2
1644 | 1408 | 410.6 | 456 | 430.4 | 426.8 | 402.3
1645 | 1409 | 410.9 | 456.4 | 430 | 426.9 | 402.4
1646 | 1410 | 411.2 | 456.1 | 429.9 | 427.1 | 402.7
1647 | 1411 | 411.5 | 455.9 | 430.1 | 427.3 | 403
1648 | 1412 | 411.9 | 456.6 | 430.4 | 427.6 | 403.3
1649 | 1413 | 412.2 | 456.9 | 430 | 427.8 | 403.5
1650 | 1414 | 412.6 | 456.6 | 429.8 | 428 | 403.7
1651 | 1415 | 412.9 | 456.1 | 430.1 | 428.2 | 403.9
1652 | 1416 | 413.3 | 456 | 430.2 | 428.5 | 404.2
1653 | 1417 | 413.6 | 456.4 | 431.3 | 428.7 | 404.5
1654 | 1418 | 414 | 456.9 | 431.3 | 428.9 | 404.5
1655 | 1419 | 414.3 | 457.7 | 431 | 429.1 | 404.5
1656 | 1420 | 414.6 | 458.2 | 430.5 | 429.3 | 404.5
1657 | 1421 | 414.9 | 458.1 | 429.8 | 429.5 | 404.7
1658 | 1422 | 415.2 | 457.8 | 429.4 | 429.6 | 404.8
1659 | 1423 | 415.5 | 457.2 | 429.1 | 429.8 | 404.7
1660 | 1424 | 415.8 | 457 | 428.3 | 430 | 404.7
1661 | 1425 | 416.1 | 457.5 | 427.6 | 430.1 | 404.7
1662 | 1426 | 416.3 | 457.8 | 427.4 | 430.3 | 404.7
1663 | 1427 | 416.6 | 458.2 | 428 | 430.4 | 404.9
1664 | 1428 | 416.9 | 459.3 | 428.8 | 430.7 | 405.1
1665 | 1429 | 417.2 | 460.8 | 428.9 | 430.9 | 405.2
1666 | 1430 | 417.5 | 462.1 | 428.5 | 431.2 | 405.3
1667 | 1431 | 417.8 | 462 | 428.9 | 431.5 | 405.5
1668 | 1432 | 418 | 462 | 429.4 | 431.7 | 405.6
1669 | 1433 | 418.3 | 462.4 | 429.4 | 431.9 | 405.7
1670 | 1434 | 418.5 | 462.6 | 429.5 | 432 | 405.7
1671 | 1435 | 418.7 | 462.8 | 429.2 | 432.1 | 405.7
1672 | 1436 | 419 | 462.8 | 428.7 | 432.2 | 405.7
1673 | 1437 | 419.1 | 462 | 428.9 | 432.2 | 405.8
1674 | 1438 | 419.3 | 461.3 | 429 | 432.3 | 405.9
1675 | 1439 | 419.5 | 460.3 | 428.7 | 432.3 | 405.9
1676 | 1440 | 419.7 | 459.5 | 427.8 | 432.5 | 405.7
1677 | 1441 | 419.9 | 459.1 | 427.1 | 432.6 | 405.5
1678 | 1442 | 420.1 | 458.7 | 426.5 | 432.7 | 405.4
1679 | 1443 | 420.4 | 458 | 426.5 | 432.9 | 405.3
1680 | 1444 | 420.6 | 457.5 | 425.8 | 433 | 405.2
1681 | 1445 | 420.8 | 457.2 | 424.9 | 433.2 | 405
1682 | 1446 | 421 | 456.9 | 424.6 | 433.3 | 404.9
1683 | 1447 | 421.2 | 456.8 | 424.3 | 433.4 | 404.9
1684 | 1448 | 421.3 | 456.6 | 424 | 433.5 | 404.9
1685 | 1449 | 421.4 | 456.1 | 423.2 | 433.6 | 404.7
1686 | 1450 | 421.6 | 455.7 | 422.6 | 433.6 | 404.7
1687 | 1451 | 421.7 | 455.5 | 422.4 | 433.7 | 404.7
1688 | 1452 | 421.8 | 455.5 | 422.6 | 433.8 | 404.7
1689 | 1453 | 422 | 455 | 422.5 | 433.9 | 404.8
1690 | 1454 | 422.1 | 454.4 | 422.3 | 434 | 404.8
1691 | 1455 | 422.2 | 453.8 | 422.2 | 434 | 404.7
1692 | 1456 | 422.3 | 453.3 | 421.9 | 434.1 | 404.6
1693 | 1457 | 422.4 | 453.2 | 421.7 | 434.2 | 404.6
1694 | 1458 | 422.5 | 453.2 | 421.3 | 434.2 | 404.6
1695 | 1459 | 422.6 | 453 | 420.8 | 434.3 | 404.6
1696 | 1460 | 422.7 | 452.9 | 420.6 | 434.4 | 404.6
1697 | 1461 | 422.8 | 453.5 | 420.4 | 434.6 | 404.6
1698 | 1462 | 423 | 453.6 | 420.1 | 434.7 | 404.5
1699 | 1463 | 423.1 | 453.3 | 419.7 | 434.9 | 404.4
1700 | 1464 | 423.3 | 453.1 | 419.3 | 435 | 404.4
1701 | 1465 | 423.4 | 453.2 | 419.3 | 435.1 | 404.4
1702 | 1466 | 423.5 | 453 | 418.6 | 435.1 | 404.2
1703 | 1467 | 423.6 | 452.5 | 417.9 | 435.2 | 404.1
1704 | 1468 | 423.6 | 452.1 | 418 | 435.2 | 404.1
1705 | 1469 | 423.7 | 451.9 | 417.6 | 435.3 | 404.1
1706 | 1470 | 423.8 | 451.4 | 417.7 | 435.3 | 404.1
1707 | 1471 | 423.8 | 450.8 | 418.6 | 435.4 | 404.2
1708 | 1472 | 423.9 | 450.1 | 419.3 | 435.4 | 404.4
1709 | 1473 | 424 | 449.6 | 420.7 | 435.5 | 404.5
1710 | 1474 | 424 | 449.2 | 422.3 | 435.5 | 404.7
1711 | 1475 | 424 | 449.5 | 423.1 | 435.5 | 404.7
1712 | 1476 | 424.1 | 450.1 | 423.5 | 435.6 | 404.7
1713 | 1477 | 424.1 | 450.4 | 423.4 | 435.7 | 404.7
1714 | 1478 | 424.1 | 450.7 | 423.2 | 435.8 | 404.7
1715 | 1479 | 424.2 | 450.1 | 422.6 | 435.8 | 404.7
1716 | 1480 | 424.2 | 449.4 | 422 | 435.9 | 404.7
1717 | 1481 | 424.3 | 448.9 | 422.1 | 436 | 404.8
1718 | 1482 | 424.4 | 448.6 | 423.2 | 436.2 | 405.1
1719 | 1483 | 424.5 | 449.2 | 424.5 | 436.3 | 405.3
1720 | 1484 | 424.6 | 449.6 | 425 | 436.4 | 405.5
1721 | 1485 | 424.6 | 450 | 424.8 | 436.5 | 405.4
1722 | 1486 | 424.7 | 449.9 | 423.9 | 436.5 | 405.4
1723 | 1487 | 424.7 | 449.5 | 423.8 | 436.6 | 405.4
1724 | 1488 | 424.8 | 449 | 423.9 | 436.7 | 405.5
1725 | 1489 | 424.8 | 449 | 423.2 | 436.8 | 405.4
1726 | 1490 | 424.9 | 448.5 | 423.1 | 436.9 | 405.5
1727 | 1491 | 425 | 448.1 | 423.1 | 437 | 405.5
1728 | 1492 | 425.1 | 448.2 | 423 | 437.1 | 405.6
1729 | 1493 | 425.1 | 448.8 | 423.3 | 437.3 | 405.7
1730 | 1494 | 425.2 | 449.4 | 423.4 | 437.4 | 405.8
1731 | 1495 | 425.3 | 450.1 | 424.1 | 437.6 | 406
1732 | 1496 | 425.3 | 450.6 | 424.8 | 437.8 | 406.2
1733 | 1497 | 425.4 | 450.4 | 424.5 | 437.9 | 406.3
1734 | 1498 | 425.5 | 450.4 | 425 | 438 | 406.5
1735 | 1499 | 425.6 | 450.6 | 426.1 | 438.1 | 406.6
1736 | 1500 | 425.6 | 450.8 | 425.9 | 438.2 | 406.7
1737 | 1501 | 425.7 | 451 | 425.8 | 438.3 | 406.7
1738 | 1502 | 425.7 | 450.9 | 425.7 | 438.4 | 406.8
1739 | 1503 | 425.8 | 450.5 | 425.4 | 438.5 | 407.1
1740 | 1504 | 425.8 | 450.7 | 425.6 | 438.5 | 407.1
1741 | 1505 | 425.8 | 452.1 | 425.4 | 438.6 | 407.1
1742 | 1506 | 425.8 | 452.3 | 425.4 | 438.6 | 407.1
1743 | 1507 | 425.9 | 452.5 | 425.8 | 438.7 | 407.2
1744 | 1508 | 425.9 | 452.5 | 425.5 | 438.8 | 407.3
1745 | 1509 | 426 | 452.6 | 425.8 | 438.9 | 407.4
1746 | 1510 | 426 | 452.5 | 426.2 | 439 | 407.4
1747 | 1511 | 426.1 | 452.1 | 426.2 | 439.2 | 407.4
1748 | 1512 | 426.1 | 451.7 | 426.2 | 439.3 | 407.4
1749 | 1513 | 426.2 | 451.8 | 426.2 | 439.5 | 407.3
1750 | 1514 | 426.3 | 452.4 | 426.2 | 439.6 | 407.3
1751 | 1515 | 426.3 | 452.7 | 426.8 | 439.6 | 407.5
1752 | 1516 | 426.3 | 452.5 | 426.8 | 439.7 | 407.5
1753 | 1517 | 426.3 | 452.2 | 426 | 439.7 | 407.4
1754 | 1518 | 426.4 | 451.8 | 425.8 | 439.8 | 407.4
1755 | 1519 | 426.4 | 451.4 | 425.6 | 439.9 | 407.5
1756 | 1520 | 426.5 | 451.5 | 425.5 | 440 | 407.6
1757 | 1521 | 426.5 | 453.2 | 426.7 | 440.1 | 407.9
1758 | 1522 | 426.5 | 454.9 | 427.3 | 440.2 | 408.2
1759 | 1523 | 426.5 | 456.3 | 428 | 440.3 | 408.4
1760 | 1524 | 426.6 | 457.7 | 428.8 | 440.4 | 408.4
1761 | 1525 | 426.6 | 458.4 | 429.2 | 440.5 | 408.5
1762 | 1526 | 426.7 | 458.4 | 429.1 | 440.7 | 408.5
1763 | 1527 | 426.8 | 458.3 | 429.1 | 440.9 | 408.4
1764 | 1528 | 426.9 | 457.6 | 428.1 | 441.1 | 408.4
1765 | 1529 | 426.9 | 457 | 427.3 | 441.2 | 408.2
1766 | 1530 | 427 | 456.9 | 427 | 441.3 | 408.1
1767 | 1531 | 427 | 456.1 | 426.4 | 441.4 | 408.1
1768 | 1532 | 427.1 | 455.5 | 426.4 | 441.5 | 408.2
1769 | 1533 | 427.2 | 455.2 | 426.5 | 441.7 | 408.3
1770 | 1534 | 427.3 | 455.5 | 426.5 | 441.8 | 408.3
1771 | 1535 | 427.4 | 455.4 | 427.1 | 442 | 408.3
1772 | 1536 | 427.4 | 456.5 | 427.2 | 442.1 | 408.4
1773 | 1537 | 427.5 | 458.2 | 427.3 | 442.2 | 408.4
1774 | 1538 | 427.5 | 459.6 | 427.5 | 442.3 | 408.5
1775 | 1539 | 427.6 | 460.5 | 427.1 | 442.4 | 408.4
1776 | 1540 | 427.6 | 460.2 | 427 | 442.4 | 408.4
1777 | 1541 | 427.7 | 459.4 | 427.5 | 442.5 | 408.4
1778 | 1542 | 427.8 | 458.9 | 427 | 442.7 | 408.4
1779 | 1543 | 427.8 | 458.4 | 426.6 | 442.7 | 408.3
1780 | 1544 | 427.9 | 457.3 | 426.6 | 442.8 | 408.4
1781 | 1545 | 427.9 | 456.2 | 426.9 | 442.9 | 408.5
1782 | 1546 | 428 | 456.3 | 427 | 443 | 408.6
1783 | 1547 | 428 | 456.4 | 427.1 | 443.1 | 408.5
1784 | 1548 | 428.1 | 455.7 | 426.7 | 443.1 | 408.5
1785 | 1549 | 428.1 | 454.8 | 427 | 443.2 | 408.5
1786 | 1550 | 428.1 | 453.7 | 427.5 | 443.2 | 408.6
1787 | 1551 | 428.2 | 453 | 427.8 | 443.3 | 408.6
1788 | 1552 | 428.2 | 452.2 | 428 | 443.4 | 408.5
1789 | 1553 | 428.3 | 451.4 | 427.8 | 443.6 | 408.5
1790 | 1554 | 428.4 | 451.5 | 428.2 | 443.7 | 408.6
1791 | 1555 | 428.4 | 452.4 | 428.6 | 443.8 | 408.7
1792 | 1556 | 428.5 | 453.8 | 428.2 | 443.9 | 408.8
1793 | 1557 | 428.5 | 453.7 | 428.4 | 444 | 408.9
1794 | 1558 | 428.5 | 454.3 | 428.2 | 444 | 409
1795 | 1559 | 428.6 | 455.5 | 427.1 | 444.1 | 409
1796 | 1560 | 428.6 | 457 | 427 | 444.1 | 409.1
1797 | 1561 | 428.6 | 457.7 | 427.9 | 444.2 | 409.2
1798 | 1562 | 428.6 | 458.1 | 428.3 | 444.3 | 409.3
1799 | 1563 | 428.7 | 458.1 | 428.9 | 444.4 | 409.5
1800 | 1564 | 428.7 | 458.4 | 429.5 | 444.5 | 409.7
1801 | 1565 | 428.8 | 459.4 | 429.9 | 444.7 | 409.8
1802 | 1566 | 428.9 | 459.8 | 429.4 | 444.8 | 409.7
1803 | 1567 | 428.9 | 459.4 | 428.7 | 444.9 | 409.6
1804 | 1568 | 429 | 458.7 | 428.1 | 445 | 409.6
1805 | 1569 | 429 | 457.8 | 428.4 | 445.1 | 409.6
1806 | 1570 | 429.1 | 457.6 | 427.8 | 445.1 | 409.6
1807 | 1571 | 429.1 | 458.5 | 427.9 | 445.2 | 409.6
1808 | 1572 | 429.1 | 458.6 | 428.6 | 445.2 | 409.7
1809 | 1573 | 429.2 | 458.5 | 428.3 | 445.3 | 409.7
1810 | 1574 | 429.2 | 458.9 | 428.1 | 445.4 | 409.8
1811 | 1575 | 429.3 | 458.8 | 428.3 | 445.5 | 409.9
1812 | 1576 | 429.3 | 458.9 | 429 | 445.6 | 410
1813 | 1577 | 429.4 | 459.9 | 429.9 | 445.7 | 410.2
1814 | 1578 | 429.5 | 460.5 | 429.5 | 445.8 | 410.3
1815 | 1579 | 429.5 | 460.6 | 429 | 446 | 410.3
1816 | 1580 | 429.6 | 461.3 | 429.6 | 446.1 | 410.5
1817 | 1581 | 429.7 | 463.2 | 430.3 | 446.2 | 410.8
1818 | 1582 | 429.8 | 465 | 431.8 | 446.5 | 411
1819 | 1583 | 429.9 | 466.5 | 433.9 | 446.8 | 411.2
1820 | 1584 | 430 | 468.4 | 434.3 | 447 | 411.3
1821 | 1585 | 430.2 | 469.3 | 435 | 447.3 | 411.4
1822 | 1586 | 430.3 | 469.4 | 434.9 | 447.6 | 411.4
1823 | 1587 | 430.5 | 468.9 | 435.2 | 447.8 | 411.4
1824 | 1588 | 430.7 | 468.1 | 435 | 448.1 | 411.3
1825 | 1589 | 430.8 | 467.5 | 435 | 448.3 | 411.3
1826 | 1590 | 431 | 467.4 | 434.4 | 448.4 | 411.3
1827 | 1591 | 431.1 | 467.5 | 434.5 | 448.5 | 411.3
1828 | 1592 | 431.2 | 467.2 | 434.5 | 448.6 | 411.4
1829 | 1593 | 431.3 | 466.5 | 434.5 | 448.7 | 411.5
1830 | 1594 | 431.4 | 465.5 | 434.5 | 448.8 | 411.4
1831 | 1595 | 431.5 | 464.7 | 434.4 | 448.8 | 411.2
1832 | 1596 | 431.5 | 463.6 | 433.5 | 448.8 | 411.1
1833 | 1597 | 431.6 | 462.8 | 433.9 | 448.9 | 411.1
1834 | 1598 | 431.6 | 462 | 433.7 | 448.9 | 411.2
1835 | 1599 | 431.6 | 461.3 | 434.3 | 448.9 | 411.3
1836 | 1600 | 431.7 | 460.9 | 434.8 | 448.9 | 411.3
1837 | 1601 | 431.7 | 461.1 | 434.1 | 448.9 | 411.2
1838 | 1602 | 431.7 | 461 | 434.1 | 448.9 | 411.3
1839 | 1603 | 431.7 | 460.8 | 433.8 | 449 | 411.3
1840 | 1604 | 431.8 | 460.1 | 433.9 | 449.1 | 411.3
1841 | 1605 | 431.8 | 459.4 | 433.5 | 449.2 | 411.4
1842 | 1606 | 431.9 | 458.4 | 433.9 | 449.3 | 411.5
1843 | 1607 | 431.9 | 457.8 | 434.1 | 449.4 | 411.5
1844 | 1608 | 432 | 457.8 | 433.4 | 449.5 | 411.5
1845 | 1609 | 432.1 | 458.8 | 433.3 | 449.6 | 411.4
1846 | 1610 | 432.1 | 458.8 | 433.2 | 449.6 | 411.5
1847 | 1611 | 432.2 | 458.9 | 433.2 | 449.8 | 411.5
1848 | 1612 | 432.3 | 459.1 | 432.9 | 449.9 | 411.5
1849 | 1613 | 432.4 | 458.7 | 433.2 | 450 | 411.6
1850 | 1614 | 432.4 | 458.4 | 433.5 | 450.1 | 411.7
1851 | 1615 | 432.5 | 458.8 | 432.9 | 450.1 | 411.5
1852 | 1616 | 432.5 | 460.4 | 432 | 450.1 | 411.4
1853 | 1617 | 432.5 | 461.1 | 431.4 | 450.1 | 411.3
1854 | 1618 | 432.5 | 460.6 | 432 | 450 | 411.4
1855 | 1619 | 432.6 | 459.7 | 432.6 | 450 | 411.5
1856 | 1620 | 432.6 | 459.3 | 433 | 450.1 | 411.7
1857 | 1621 | 432.6 | 459.8 | 432.8 | 450.2 | 411.7
1858 | 1622 | 432.7 | 460 | 432.9 | 450.3 | 411.7
1859 | 1623 | 432.8 | 459.6 | 432.1 | 450.4 | 411.6
1860 | 1624 | 432.9 | 459.5 | 431.8 | 450.6 | 411.7
1861 | 1625 | 433 | 459.7 | 432.4 | 450.8 | 411.7
1862 | 1626 | 433.1 | 459.6 | 432.5 | 451 | 411.8
1863 | 1627 | 433.2 | 458.8 | 433 | 451.1 | 411.7
1864 | 1628 | 433.3 | 457.6 | 432.7 | 451.1 | 411.7
1865 | 1629 | 433.4 | 456.7 | 432.3 | 451.3 | 411.8
1866 | 1630 | 433.6 | 455.9 | 432 | 451.5 | 411.8
1867 | 1631 | 433.7 | 455.3 | 431.6 | 451.7 | 411.7
1868 | 1632 | 433.9 | 455 | 431.5 | 451.8 | 411.8
1869 | 1633 | 434 | 454.9 | 432.4 | 452 | 411.9
1870 | 1634 | 434.1 | 455.2 | 432 | 452.1 | 411.9
1871 | 1635 | 434.3 | 455.5 | 431.4 | 452.1 | 412
1872 | 1636 | 434.4 | 456.1 | 432.9 | 452.2 | 412.2
1873 | 1637 | 434.4 | 457.7 | 433.1 | 452.2 | 412.3
1874 | 1638 | 434.5 | 460.3 | 433.2 | 452.2 | 412.4
1875 | 1639 | 434.5 | 461.7 | 433.4 | 452.3 | 412.3
1876 | 1640 | 434.6 | 462.3 | 433 | 452.3 | 412.3
1877 | 1641 | 434.6 | 461.9 | 433.7 | 452.4 | 412.5
1878 | 1642 | 434.8 | 462.9 | 434.6 | 452.6 | 412.6
1879 | 1643 | 434.9 | 464.5 | 433.9 | 452.8 | 412.6
1880 | 1644 | 434.9 | 464.6 | 433 | 452.9 | 412.5
1881 | 1645 | 435.1 | 463.1 | 433.3 | 453.1 | 412.4
1882 | 1646 | 435.2 | 463.3 | 432.5 | 453.2 | 412.4
1883 | 1647 | 435.4 | 463.1 | 432.4 | 453.3 | 412.4
1884 | 1648 | 435.5 | 463 | 432.3 | 453.4 | 412.4
1885 | 1649 | 435.5 | 463 | 433.2 | 453.4 | 412.5
1886 | 1650 | 435.6 | 462.5 | 433.7 | 453.5 | 412.5
1887 | 1651 | 435.7 | 461.8 | 433.8 | 453.5 | 412.5
1888 | 1652 | 435.7 | 461.2 | 433.3 | 453.5 | 412.4
1889 | 1653 | 435.8 | 460.8 | 433.3 | 453.5 | 412.3
1890 | 1654 | 435.9 | 460.1 | 432.8 | 453.5 | 412.4
1891 | 1655 | 436 | 459.8 | 433 | 453.6 | 412.4
1892 | 1656 | 436 | 459.8 | 433.3 | 453.6 | 412.5
1893 | 1657 | 436.1 | 460.1 | 433.3 | 453.8 | 412.5
1894 | 1658 | 436.2 | 460.1 | 433.3 | 453.9 | 412.5
1895 | 1659 | 436.3 | 459.3 | 433.3 | 454.1 | 412.4
1896 | 1660 | 436.5 | 458.9 | 433.9 | 454.2 | 412.4
1897 | 1661 | 436.6 | 458.9 | 435.5 | 454.2 | 412.4
1898 | 1662 | 436.6 | 458.7 | 436.4 | 454.2 | 412.3
1899 | 1663 | 436.6 | 458.8 | 436.2 | 454.1 | 412.2
1900 | 1664 | 436.7 | 459.1 | 436.5 | 454.2 | 412.3
1901 | 1665 | 436.7 | 458.8 | 437.7 | 454.2 | 412.4
1902 | 1666 | 436.8 | 458.5 | 437.8 | 454.4 | 412.3
1903 | 1667 | 436.9 | 458.5 | 437.3 | 454.6 | 412.2
1904 | 1668 | 437 | 458.1 | 436.1 | 454.6 | 412.1
1905 | 1669 | 437.1 | 457.7 | 436.3 | 454.7 | 412.2
1906 | 1670 | 437.2 | 457 | 437.6 | 454.7 | 412.1
1907 | 1671 | 437.3 | 456.3 | 438 | 454.7 | 412
1908 | 1672 | 437.3 | 456.2 | 437.2 | 454.7 | 411.9
1909 | 1673 | 437.4 | 456 | 436.6 | 454.8 | 411.9
1910 | 1674 | 437.5 | 455.3 | 435.2 | 454.8 | 411.8
1911 | 1675 | 437.6 | 454.5 | 434.4 | 454.9 | 411.7
1912 | 1676 | 437.7 | 453.8 | 434.5 | 455 | 411.7
1913 | 1677 | 437.8 | 453.4 | 434.7 | 455.1 | 411.7
1914 | 1678 | 437.9 | 453 | 434.8 | 455.2 | 411.6
1915 | 1679 | 437.9 | 452.4 | 433.6 | 455.2 | 411.5
1916 | 1680 | 438 | 451.6 | 433 | 455.3 | 411.5
1917 | 1681 | 438.1 | 450.8 | 432.3 | 455.4 | 411.5
1918 | 1682 | 438.2 | 450 | 431.7 | 455.5 | 411.5
1919 | 1683 | 438.4 | 449.6 | 431.4 | 455.7 | 411.5
1920 | 1684 | 438.4 | 449.3 | 431 | 455.6 | 411.6
1921 | 1685 | 438.5 | 448.8 | 430.5 | 455.5 | 411.5
1922 | 1686 | 438.5 | 448.5 | 430.4 | 455.5 | 411.5
1923 | 1687 | 438.5 | 448.6 | 431.2 | 455.4 | 411.6
1924 | 1688 | 438.5 | 449.6 | 431.3 | 455.4 | 411.7
1925 | 1689 | 438.5 | 451.7 | 431.9 | 455.4 | 411.7
1926 | 1690 | 438.6 | 453.3 | 432.1 | 455.3 | 411.6
1927 | 1691 | 438.6 | 454.6 | 432.3 | 455.3 | 411.5
1928 | 1692 | 438.6 | 455.1 | 432.2 | 455.3 | 411.6
1929 | 1693 | 438.6 | 456.3 | 432 | 455.2 | 411.5
1930 | 1694 | 438.6 | 457.9 | 431.1 | 455.1 | 411.4
1931 | 1695 | 438.6 | 458.6 | 430.5 | 455 | 411.4
1932 | 1696 | 438.6 | 459.7 | 430.7 | 455.2 | 411.4
1933 | 1697 | 438.7 | 459.4 | 430.9 | 455.5 | 411.3
1934 | 1698 | 438.9 | 458.7 | 430.8 | 455.8 | 411.3
1935 | 1699 | 439.1 | 458 | 430.9 | 456.1 | 411.4
1936 | 1700 | 439.3 | 457.8 | 431 | 456.3 | 411.4
1937 | 1701 | 439.5 | 458.3 | 430.5 | 456.5 | 411.4
1938 | 1702 | 439.7 | 458.4 | 430.2 | 456.6 | 411.4
1939 | 1703 | 439.8 | 458.6 | 429.6 | 456.7 | 411.4
1940 | 1704 | 439.9 | 460 | 429.6 | 456.8 | 411.5
1941 | 1705 | 440.1 | 461.1 | 429.5 | 457 | 411.5
1942 | 1706 | 440.2 | 462.9 | 429.8 | 457.1 | 411.5
1943 | 1707 | 440.4 | 463.2 | 434.9 | 457.2 | 412
1944 | 1708 | 440.5 | 464.2 | 439.6 | 457.4 | 415.5
1945 | 1709 | 440.6 | 465.8 | 441.1 | 457.5 | 415.1
1946 | 1710 | 440.8 | 466.9 | 441.5 | 457.8 | 414.7
1947 | 1711 | 441.1 | 466.7 | 440.9 | 458.1 | 414.6
1948 | 1712 | 441.3 | 466.2 | 440.3 | 458.3 | 414.5
1949 | 1713 | 441.5 | 465.6 | 439.4 | 458.4 | 414.5
1950 | 1714 | 441.6 | 465.1 | 439.2 | 458.4 | 414.5
1951 | 1715 | 441.7 | 466.6 | 438.8 | 458.4 | 414.4
1952 | 1716 | 441.8 | 476.5 | 437.6 | 458.6 | 414.2
1953 | 1717 | 441.9 | 477.9 | 436.7 | 458.7 | 413.9
1954 | 1718 | 442 | 476.7 | 435.6 | 458.8 | 413.5
1955 | 1719 | 442.1 | 474.5 | 433.8 | 458.9 | 413.1
1956 | 1720 | 442.3 | 472.1 | 431.9 | 459 | 412.6
1957 | 1721 | 442.4 | 469.8 | 428.8 | 458.9 | 412.1
1958 | 1722 | 442.3 | 468.1 | 426.7 | 458.7 | 411.5
1959 | 1723 | 442.3 | 466.5 | 423.8 | 458.4 | 411
1960 | 1724 | 442.3 | 465.2 | 420.7 | 458.2 | 410.4
1961 | 1725 | 442.2 | 463.3 | 417.9 | 458 | 409.8
1962 | 1726 | 442.1 | 461 | 415.1 | 457.8 | 409.3
1963 | 1727 | 442.1 | 458.6 | 412.8 | 457.7 | 408.8
1964 | 1728 | 442 | 456.3 | 410 | 457.5 | 408.2
1965 | 1729 | 441.8 | 455.6 | 407.3 | 457.2 | 407.6
1966 | 1730 | 441.7 | 455.5 | 405.2 | 456.8 | 407.1
1967 | 1731 | 441.5 | 454.3 | 403.1 | 456.4 | 406.6
1968 | 1732 | 441.3 | 451.5 | 401 | 456 | 406.1
1969 | 1733 | 441.1 | 449.5 | 399.3 | 455.8 | 405.6
1970 | 1734 | 441 | 448.1 | 397.4 | 455.6 | 405
1971 | 1735 | 440.8 | 445.8 | 395.6 | 455.4 | 404.5
1972 | 1736 | 440.7 | 444.3 | 393.9 | 455.2 | 404
1973 | 1737 | 440.5 | 444.8 | 392 | 455 | 403.6
1974 | 1738 | 440.3 | 443.2 | 390.1 | 454.7 | 403.1
1975 | 1739 | 440.2 | 442.2 | 388.8 | 454.5 | 402.6
1976 | 1740 | 440 | 441.3 | 387.9 | 454.2 | 402.1
1977 | 1741 | 439.9 | 439.4 | 386.3 | 454 | 401.7
1978 | 1742 | 439.8 | 438.9 | 384.6 | 453.8 | 401.2
1979 | 1743 | 439.6 | 438.2 | 383.3 | 453.5 | 400.7
1980 | 1744 | 439.4 | 436.5 | 381.8 | 453.2 | 400.2
1981 | 1745 | 439.3 | 434.3 | 380.4 | 452.9 | 399.8
1982 | 1746 | 439.1 | 433.1 | 379.4 | 452.6 | 399.3
1983 | 1747 | 438.9 | 432.7 | 378 | 452.3 | 398.9
1984 | 1748 | 438.7 | 431.2 | 376.7 | 452 | 398.4
1985 | 1749 | 438.5 | 431.7 | 375.5 | 451.7 | 397.9
1986 | 1750 | 438.3 | 433.2 | 374.5 | 451.4 | 397.5
1987 | 1751 | 438.1 | 434.2 | 373.8 | 451 | 397.1
1988 | 1752 | 437.9 | 434.3 | 372.7 | 450.7 | 396.7
1989 | 1753 | 437.7 | 433.9 | 371.9 | 450.5 | 396.3
1990 | 1754 | 437.5 | 434.9 | 371 | 450.3 | 395.8
1991 | 1755 | 437.4 | 435.8 | 370.1 | 450.1 | 395.4
1992 | 1756 | 437.2 | 435.9 | 369.6 | 449.8 | 395
1993 | 1757 | 437.1 | 434.9 | 369.2 | 449.4 | 394.6
1994 | 1758 | 436.9 | 433.3 | 368.2 | 449.1 | 394.2
1995 | 1759 | 436.7 | 432.8 | 367.2 | 448.8 | 393.8
1996 | 1760 | 436.6 | 431.3 | 366.2 | 448.7 | 393.4
1997 | 1761 | 436.4 | 429.4 | 365.3 | 448.6 | 393
1998 | 1762 | 436.3 | 428.5 | 364.3 | 448.4 | 392.7
1999 | 1763 | 436.1 | 428.9 | 363.3 | 448.1 | 392.3
2000 | 1764 | 435.9 | 428.6 | 362.3 | 447.8 | 391.8
2001 | 1765 | 435.8 | 427.6 | 361.4 | 447.7 | 391.4
2002 | 1766 | 435.6 | 426.1 | 360.9 | 447.5 | 391.1
2003 | 1767 | 435.5 | 424.9 | 360 | 447.3 | 390.7
2004 | 1768 | 435.3 | 423.6 | 359 | 447.1 | 390.3
2005 | 1769 | 435.1 | 422.1 | 357.9 | 446.8 | 389.9
2006 | 1770 | 435 | 421.4 | 357.1 | 446.6 | 389.5
2007 | 1771 | 434.8 | 422.3 | 356.4 | 446.4 | 389.1
2008 | 1772 | 434.6 | 423.1 | 355.7 | 446.2 | 388.8
2009 | 1773 | 434.5 | 422.2 | 355 | 445.9 | 388.4
2010 | 1774 | 434.3 | 421.7 | 354.2 | 445.6 | 388
2011 | 1775 | 434.1 | 420.8 | 353.3 | 445.5 | 387.6
2012 | 1776 | 434 | 419.4 | 352.5 | 445.3 | 387.2
2013 | 1777 | 433.8 | 419.1 | 352 | 445.1 | 386.9
2014 | 1778 | 433.7 | 420 | 351.4 | 444.8 | 386.5
2015 | 1779 | 433.5 | 420.9 | 350.9 | 444.6 | 386.1
2016 | 1780 | 433.3 | 420.7 | 350.3 | 444.4 | 385.7
2017 | 1781 | 433.2 | 419.5 | 349.6 | 444.2 | 385.3
2018 | 1782 | 433 | 418.8 | 349 | 444.1 | 384.9
2019 | 1783 | 432.9 | 417.5 | 348.3 | 444 | 384.5
2020 | 1784 | 432.8 | 415.8 | 347.6 | 443.9 | 384.2
2021 | 1785 | 432.7 | 414 | 347.1 | 443.7 | 383.8
2022 | 1786 | 432.6 | 412.2 | 346.6 | 443.5 | 383.4
2023 | 1787 | 432.4 | 411.2 | 346 | 443.2 | 383
2024 | 1788 | 432.3 | 411.1 | 345.4 | 443 | 382.7
2025 | 1789 | 432.1 | 412.4 | 344.8 | 442.6 | 382.3
2026 | 1790 | 432 | 413.2 | 344.2 | 442.3 | 381.9
2027 | 1791 | 431.8 | 412.4 | 343.6 | 442 | 381.5
2028 | 1792 | 431.6 | 412.4 | 343 | 441.7 | 381.2
2029 | 1793 | 431.5 | 412.6 | 342.5 | 441.4 | 380.8
2030 | 1794 | 431.3 | 412.7 | 341.9 | 441.2 | 380.4
2031 | 1795 | 431.2 | 413.1 | 341.5 | 441 | 380.1
2032 | 1796 | 431 | 413.1 | 340.9 | 440.8 | 379.7
2033 | 1797 | 430.9 | 412.8 | 340.4 | 440.6 | 379.3
2034 | 1798 | 430.8 | 411.6 | 339.9 | 440.5 | 378.9
2035 | 1799 | 430.6 | 410.8 | 339.4 | 440.3 | 378.5
2036 | 1800 | 430.5 | 410.9 | 338.9 | 440.1 | 378.2
2037 | 1801 | 430.3 | 410.1 | 338.4 | 439.9 | 377.8
2038 | 1802 | 430.2 | 409.8 | 338 | 439.7 | 377.5
2039 | 1803 | 430.1 | 408.8 | 337.5 | 439.6 | 377.1
2040 | 1804 | 430 | 408.3 | 336.9 | 439.4 | 376.7
2041 | 1805 | 429.8 | 407.5 | 336.3 | 439.2 | 376.4
2042 | 1806 | 429.7 | 406.9 | 335.8 | 439 | 376
2043 | 1807 | 429.6 | 407 | 335.5 | 438.7 | 375.7
2044 | 1808 | 429.4 | 406.7 | 335.1 | 438.5 | 375.3
2045 | 1809 | 429.3 | 406.6 | 334.7 | 438.3 | 374.9
2046 | 1810 | 429.1 | 406.9 | 334.3 | 438 | 374.6
2047 | 1811 | 429 | 406.8 | 333.9 | 437.8 | 374.2
2048 | 1812 | 428.8 | 406.4 | 333.5 | 437.7 | 373.9
2049 | 1813 | 428.7 | 405.4 | 333.1 | 437.5 | 373.5
2050 | 1814 | 428.5 | 405.2 | 332.6 | 437.3 | 373.2
2051 | 1815 | 428.4 | 405 | 332.1 | 437.1 | 372.8
2052 | 1816 | 428.2 | 404.6 | 331.7 | 436.9 | 372.5
2053 | 1817 | 428.1 | 403.9 | 331.3 | 436.7 | 372.1
2054 | 1818 | 427.9 | 404.2 | 330.9 | 436.5 | 371.7
2055 | 1819 | 427.8 | 404.2 | 330.5 | 436.2 | 371.4
2056 | 1820 | 427.6 | 403.6 | 330.2 | 436 | 371.1
2057 | 1821 | 427.4 | 404.1 | 329.9 | 435.8 | 370.7
2058 | 1822 | 427.3 | 403.7 | 329.5 | 435.6 | 370.3
2059 | 1823 | 427.1 | 404.1 | 329.1 | 435.3 | 370
2060 | 1824 | 426.9 | 404.4 | 328.8 | 435.1 | 369.7
2061 | 1825 | 426.8 | 403.4 | 328.4 | 434.9 | 369.3
2062 | 1826 | 426.7 | 403.4 | 328 | 434.7 | 369
2063 | 1827 | 426.5 | 403.4 | 327.6 | 434.5 | 368.6
2064 | 1828 | 426.4 | 402.8 | 327.2 | 434.4 | 368.3
2065 | 1829 | 426.3 | 403.3 | 326.8 | 434.3 | 367.9
2066 | 1830 | 426.1 | 403 | 326.5 | 434.2 | 367.6
2067 | 1831 | 426 | 403.4 | 326.1 | 434.1 | 367.3
2068 | 1832 | 425.9 | 402.6 | 325.7 | 434.1 | 366.9
2069 | 1833 | 425.8 | 401.2 | 325.4 | 434.1 | 366.6
2070 | 1834 | 425.7 | 399.8 | 325 | 434.1 | 366.2
2071 | 1835 | 425.6 | 398.2 | 324.7 | 434 | 365.9
2072 | 1836 | 425.5 | 398.1 | 324.2 | 433.8 | 365.6
2073 | 1837 | 425.4 | 397.8 | 323.8 | 433.6 | 365.2
2074 | 1838 | 425.3 | 397.8 | 323.5 | 433.5 | 364.9
2075 | 1839 | 425.2 | 397.7 | 323.2 | 433.4 | 364.6
2076 | 1840 | 425.1 | 397.6 | 322.9 | 433.3 | 364.2
2077 | 1841 | 425 | 397.2 | 322.6 | 433 | 363.9
2078 | 1842 | 424.9 | 397.1 | 322.2 | 432.8 | 363.6
2079 | 1843 | 424.8 | 397.1 | 321.9 | 432.7 | 363.2
2080 | 1844 | 424.7 | 397.3 | 321.5 | 432.5 | 362.9
2081 | 1845 | 424.6 | 397 | 321.1 | 432.4 | 362.5
2082 | 1846 | 424.5 | 396.4 | 320.7 | 432.2 | 362.2
2083 | 1847 | 424.4 | 395.4 | 320.2 | 432 | 361.9
2084 | 1848 | 424.3 | 394.9 | 319.8 | 431.9 | 361.5
2085 | 1849 | 424.2 | 395 | 319.7 | 431.7 | 361.2
2086 | 1850 | 424.1 | 394.2 | 319.2 | 431.5 | 360.9
2087 | 1851 | 424 | 393.8 | 318.9 | 431.4 | 360.6
2088 | 1852 | 423.9 | 393.3 | 318.8 | 431.2 | 360.3
2089 | 1853 | 423.8 | 393 | 318.3 | 431 | 359.9
2090 | 1854 | 423.7 | 392.7 | 318 | 430.9 | 359.6
2091 | 1855 | 423.6 | 391.9 | 317.7 | 430.7 | 359.3
2092 | 1856 | 423.5 | 391.4 | 317.4 | 430.6 | 359
2093 | 1857 | 423.4 | 391.2 | 317.1 | 430.4 | 358.7
2094 | 1858 | 423.3 | 390.6 | 316.8 | 430.3 | 358.3
2095 | 1859 | 423.2 | 389.9 | 316.4 | 430.1 | 358
2096 | 1860 | 423.2 | 389.5 | 316.1 | 430 | 357.7
2097 | 1861 | 423.1 | 389.1 | 315.8 | 429.8 | 357.4
2098 | 1862 | 423 | 389.3 | 315.5 | 429.7 | 357.1
2099 | 1863 | 422.9 | 389.4 | 315.5 | 429.7 | 356.8
2100 | 1864 | 422.9 | 389.6 | 314.9 | 429.6 | 356.5
2101 | 1865 | 422.8 | 389.6 | 314.7 | 429.5 | 356.2
2102 | 1866 | 422.7 | 388.9 | 314.5 | 429.4 | 355.9
2103 | 1867 | 422.6 | 388.6 | 313.9 | 429.1 | 355.6
2104 | 1868 | 422.5 | 388.8 | 313.7 | 429 | 355.2
2105 | 1869 | 422.4 | 388.3 | 313.4 | 428.8 | 354.9
2106 | 1870 | 422.3 | 388.5 | 313.1 | 428.7 | 354.6
2107 | 1871 | 422.2 | 388.3 | 312.8 | 428.6 | 354.3
2108 | 1872 | 422.1 | 387 | 312.6 | 428.5 | 354
2109 | 1873 | 422 | 387.1 | 312.4 | 428.3 | 353.7
2110 | 1874 | 422 | 387.2 | 312.3 | 428.2 | 353.4
2111 | 1875 | 421.9 | 386.6 | 311.9 | 428 | 353.1
2112 | 1876 | 421.8 | 386.2 | 311.6 | 427.9 | 352.8
2113 | 1877 | 421.7 | 385.9 | 311.6 | 427.7 | 352.5
2114 | 1878 | 421.6 | 385.1 | 311.1 | 427.5 | 352.2
2115 | 1879 | 421.5 | 385.2 | 310.8 | 427.4 | 351.9
2116 | 1880 | 421.4 | 385.2 | 310.5 | 427.3 | 351.6
2117 | 1881 | 421.3 | 385.8 | 310.2 | 427.1 | 351.3
2118 | 1882 | 421.2 | 385.9 | 310.1 | 427 | 351
2119 | 1883 | 421.1 | 385.7 | 309.8 | 426.8 | 350.7
2120 | 1884 | 421 | 385.5 | 309.4 | 426.8 | 350.4
2121 | 1885 | 420.9 | 385.2 | 309.2 | 426.7 | 350.1
2122 | 1886 | 420.8 | 384.3 | 308.8 | 426.6 | 349.8
2123 | 1887 | 420.7 | 383.6 | 308.4 | 426.4 | 349.5
2124 | 1888 | 420.6 | 383.2 | 308.4 | 426.2 | 349.3
2125 | 1889 | 420.4 | 383.5 | 307.9 | 426 | 349
2126 | 1890 | 420.3 | 383.6 | 307.6 | 425.9 | 348.7
2127 | 1891 | 420.2 | 383.1 | 307.5 | 425.9 | 348.4
2128 | 1892 | 420.1 | 382.5 | 307.1 | 425.8 | 348.1
2129 | 1893 | 420 | 382.3 | 306.8 | 425.6 | 347.8
2130 | 1894 | 419.9 | 381.4 | 306.5 | 425.5 | 347.5
2131 | 1895 | 419.8 | 380.2 | 306.1 | 425.4 | 347.2
2132 | 1896 | 419.7 | 379.9 | 305.8 | 425.3 | 346.9
2133 | 1897 | 419.6 | 379.7 | 305.5 | 425.2 | 346.6
2134 | 1898 | 419.5 | 378.8 | 305.1 | 425.2 | 346.3
2135 | 1899 | 419.4 | 378.9 | 304.7 | 425 | 346
2136 | 1900 | 419.3 | 378.8 | 304.3 | 424.9 | 345.7
2137 | 1901 | 419.3 | 378.8 | 304 | 424.8 | 345.4
2138 | 1902 | 419.2 | 378.5 | 303.8 | 424.7 | 345.1
2139 | 1903 | 419 | 379.2 | 303.6 | 424.5 | 344.9
2140 | 1904 | 418.9 | 378.8 | 303.4 | 424.4 | 344.6
2141 | 1905 | 418.8 | 378.1 | 303.3 | 424.3 | 344.3
2142 | 1906 | 418.7 | 377 | 302.8 | 424.1 | 344
2143 | 1907 | 418.5 | 376.1 | 302.5 | 423.9 | 343.7
2144 | 1908 | 418.4 | 375.9 | 302.3 | 423.8 | 343.4
2145 | 1909 | 418.2 | 375.7 | 301.8 | 423.6 | 343.1
2146 | 1910 | 418.1 | 375.4 | 301.4 | 423.5 | 342.8
2147 | 1911 | 417.9 | 374.9 | 301.1 | 423.4 | 342.6
2148 | 1912 | 417.8 | 374.9 | 300.9 | 423.2 | 342.3
2149 | 1913 | 417.6 | 375.5 | 300.6 | 423.1 | 342
2150 | 1914 | 417.5 | 375.5 | 300.3 | 423 | 341.7
2151 | 1915 | 417.3 | 376 | 300 | 422.9 | 341.4
2152 | 1916 | 417.2 | 375.6 | 299.8 | 422.8 | 341.1
2153 | 1917 | 417 | 375 | 299.4 | 422.6 | 340.9
2154 | 1918 | 416.9 | 375 | 299 | 422.4 | 340.6
2155 | 1919 | 416.7 | 375.1 | 298.8 | 422.2 | 340.3
2156 | 1920 | 416.6 | 374.7 | 298.3 | 422.1 | 340
2157 | 1921 | 416.5 | 374.4 | 298 | 422 | 339.7
2158 | 1922 | 416.3 | 373.6 | 297.8 | 421.9 | 339.4
2159 | 1923 | 416.2 | 373.4 | 297.6 | 421.8 | 339.2
2160 | 1924 | 416.1 | 372.5 | 297.4 | 421.7 | 338.9
2161 | 1925 | 415.9 | 372.7 | 297.3 | 421.6 | 338.6
2162 | 1926 | 415.8 | 372.8 | 297 | 421.5 | 338.3
2163 | 1927 | 415.6 | 371.7 | 296.8 | 421.3 | 338.1
2164 | 1928 | 415.5 | 370.9 | 296.5 | 421.1 | 337.8
2165 | 1929 | 415.3 | 370.4 | 296.3 | 421.1 | 337.5
2166 | 1930 | 415.1 | 370.1 | 296.2 | 420.9 | 337.3
2167 | 1931 | 414.9 | 369.8 | 295.9 | 420.7 | 337
2168 | 1932 | 414.7 | 370.1 | 295.5 | 420.4 | 336.7
2169 | 1933 | 414.5 | 370.7 | 295.4 | 420.2 | 336.5
2170 | 1934 | 414.3 | 370.4 | 295.2 | 420 | 336.2
2171 | 1935 | 414.1 | 370.3 | 294.9 | 419.8 | 335.9
2172 | 1936 | 413.9 | 369.7 | 294.6 | 419.6 | 335.7
2173 | 1937 | 413.7 | 369.3 | 294.2 | 419.3 | 335.4
2174 | 1938 | 413.6 | 369.1 | 293.9 | 419.2 | 335.1
2175 | 1939 | 413.4 | 368.1 | 293.6 | 419.1 | 334.8
2176 | 1940 | 413.2 | 367 | 293.3 | 419 | 334.6
2177 | 1941 | 413.1 | 367 | 293.1 | 418.9 | 334.3
2178 | 1942 | 413 | 366.9 | 292.8 | 418.8 | 334
2179 | 1943 | 412.8 | 366.5 | 292.4 | 418.7 | 333.8
2180 | 1944 | 412.7 | 366.2 | 292.1 | 418.6 | 333.5
2181 | 1945 | 412.6 | 365.6 | 291.8 | 418.4 | 333.2
2182 | 1946 | 412.4 | 365.2 | 291.5 | 418.1 | 332.9
2183 | 1947 | 412.3 | 364.5 | 291.4 | 417.9 | 332.7
2184 | 1948 | 412.1 | 364.1 | 291.2 | 417.7 | 332.4
2185 | 1949 | 411.9 | 363.3 | 291 | 417.5 | 332.2
2186 | 1950 | 411.7 | 362.9 | 290.7 | 417.3 | 331.9
2187 | 1951 | 411.4 | 362 | 290.2 | 417.1 | 331.6
2188 | 1952 | 411.2 | 361 | 289.9 | 416.9 | 331.4
2189 | 1953 | 411 | 360.8 | 289.6 | 416.7 | 331.1
2190 | 1954 | 410.8 | 360.7 | 289.3 | 416.5 | 330.9
2191 | 1955 | 410.6 | 361.1 | 289.1 | 416.2 | 330.6
2192 | 1956 | 410.3 | 361.4 | 288.9 | 416 | 330.4
2193 | 1957 | 410.1 | 361.2 | 288.7 | 415.9 | 330.1
2194 | 1958 | 409.9 | 360.9 | 288.5 | 415.7 | 329.9
2195 | 1959 | 409.7 | 360.9 | 288.2 | 415.5 | 329.6
2196 | 1960 | 409.5 | 360.8 | 288 | 415.3 | 329.4
2197 | 1961 | 409.3 | 361 | 287.8 | 415 | 329.1
2198 | 1962 | 409.1 | 361.1 | 287.3 | 414.7 | 328.9
2199 | 1963 | 408.9 | 360.5 | 287 | 414.5 | 328.6
2200 | 1964 | 408.7 | 360 | 286.9 | 414.4 | 328.4
2201 | 1965 | 408.5 | 359.8 | 286.7 | 414.3 | 328.1
2202 | 1966 | 408.4 | 359 | 286.6 | 414.1 | 327.9
2203 | 1967 | 408.2 | 358.5 | 286.3 | 413.9 | 327.6
2204 | 1968 | 408 | 357.9 | 285.9 | 413.7 | 327.4
2205 | 1969 | 407.8 | 357 | 285.7 | 413.5 | 327.2
2206 | 1970 | 407.6 | 356.5 | 285.5 | 413.2 | 326.9
2207 | 1971 | 407.3 | 355.9 | 285.4 | 413 | 326.7
2208 | 1972 | 407.1 | 355.4 | 285.3 | 412.9 | 326.4

## Test Facts
Last row in IRMS data sheets: | 57
Time when gas burner was ignited: | 632