## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 13, Location G, IRMS #2
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE/CSPE, EPR/CPE, PE/PVC, PVC/PVC, XLPE/PVC & Tefzel/Tefzel control cables (Items 10, 2, 15, 1, 3 & 12). Cable specimens present: Three lengths of cable were monitored for electrical performance (A, B & C [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position F in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 150 kW heat release rate, increased to ~300 kW during the test run. Electrical repsonse monitoring: IRMS system using 6 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 239 seconds of baseline data monitoring. Special Note: Vita-Link cable was used in place of silicone rubber during this test.
DAQ Time | Burner Time | Event | Interpretation
236 | 0 | Ignited Gas Burner
1952-1956 | 1716-1720 | Conductors B3 & B4 both short to ground at less than 100 ohms (5 & 4) | Cable B shorted to ground
1958 | 1722 | Conductors B3 & B4 short together at less than 100 ohms (6) | Cable B shorts internally
2148-2157 | 1912-1921 | Conductors A1 & A2 both short to ground at less than 100 ohms (11 & 8) | Cable A shorted to ground
2184 | 1948 | Conductors A1 & A2 short together at less than 1000 ohms (575) | Cable A shorts internally
2280 | 2044 | Extinguished Gas Burner
2330 | 2094 | Water sprinkler initiated
2762 | 2526 | Water sprinkler shut off
Additional Observations
Observation 1 | The cables that failed usually shorted to ground prior to shorting internally.
Observation 2 | Cable C did not show any signs of failure.
Observation 3 | There was no evidence of cable-to-cable interactions prior to internal cable shorting or shorting to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | Vita-Link | (Item #11)
|  |  |  | Cable D = | XLPO | (Item #8)
|  |  |  | Cable E = | PE | (Item #15)
|  |  |  | Cable F = | TEFZEL | (Item #12)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| G1 | = | Center of bundle, under jacket
| G2 | = | Air above bundle
| G3 | = | Air below bundle
| G4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | Vita-Link | (Item #11)
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 13 |  |  | 2006-11-28 | 9:21
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | C5-C6
-235.5 | 501175.9997 | -232.5 | 511375.9997 | -230 | 505375.9997 | -227 | 501375.9997 | -224 | 494375.9997 | -221.5 | 508775.9997 | -218.5 | 500975.9997 | -215.5 | 496375.9997 | -213 | 498375.9997 | -210 | 511575.9997 | -207.5 | 515575.9997 | -204.5 | 511375.9997 | -202 | 510175.9997 | -199 | 507975.9997 | -196.5 | #VALUE!
-193.5 | 501175.9997 | -190.5 | 511375.9997 | -188 | 505375.9997 | -185 | 501375.9997 | -182.5 | 494375.9997 | -179.5 | 508775.9997 | -176.5 | 500975.9997 | -174 | 496375.9997 | -171 | 498375.9997 | -168.5 | 511575.9997 | -165.5 | 515575.9997 | -162.5 | 511375.9997 | -160 | 510175.9997 | -157 | 507975.9997 | -154.5 | #VALUE!
-151.5 | 501175.9997 | -148.5 | 511375.9997 | -146 | 505375.9997 | -143 | 501375.9997 | -140.5 | 494375.9997 | -137.5 | 508775.9997 | -134.5 | 500975.9997 | -132 | 496375.9997 | -129 | 498375.9997 | -126.5 | 511575.9997 | -123.5 | 515575.9997 | -120.5 | 511375.9997 | -118 | 510175.9997 | -115 | 507975.9997 | -112.5 | #VALUE!
-109.5 | 501175.9997 | -106.5 | 511375.9997 | -104 | 505375.9997 | -101 | 501375.9997 | -98.5 | 494375.9997 | -95.5 | 508775.9997 | -92.5 | 500975.9997 | -89.5 | 496375.9997 | -87 | 498375.9997 | -84.5 | 511575.9997 | -81.5 | 515575.9997 | -78.5 | 511375.9997 | -76 | 510175.9997 | -73 | 507975.9997 | -70.5 | #VALUE!
-67.5 | 501175.9997 | -64.5 | 511375.9997 | -62 | 505375.9997 | -59 | 501375.9997 | -56.5 | 494375.9997 | -53.5 | 508775.9997 | -50.5 | 500975.9997 | -48 | 496375.9997 | -45 | 498375.9997 | -42.5 | 511575.9997 | -39.5 | 515575.9997 | -36.5 | 511375.9997 | -34 | 510175.9997 | -31 | 507975.9997 | -28.5 | #VALUE!
-25.5 | 501175.9997 | -22.5 | 511375.9997 | -20 | 505375.9997 | -17 | 501375.9997 | -14.5 | 494375.9997 | -11.5 | 508775.9997 | -8.5 | 500975.9997 | -6 | 496375.9997 | -3 | 498375.9997 | -0.5 | 511575.9997 | 2.5 | 515575.9997 | 5.5 | 511375.9997 | 8 | 510175.9997 | 11 | 507975.9997 | 34.5 | #VALUE!
16.5 | 501175.9997 | 19.5 | 511375.9997 | 22 | 505375.9997 | 25 | 501375.9997 | 27.5 | 494375.9997 | 30.5 | 508775.9997 | 33.5 | 500975.9997 | 36 | 496375.9997 | 39 | 498375.9997 | 41.5 | 511575.9997 | 44.5 | 515575.9997 | 47.5 | 511375.9997 | 50 | 510175.9997 | 53 | 507975.9997 | 76.5 | #VALUE!
58.5 | 501175.9997 | 61.5 | 511375.9997 | 64 | 505375.9997 | 67 | 501375.9997 | 69.5 | 494375.9997 | 72.5 | 508775.9997 | 75.5 | 500975.9997 | 78 | 496375.9997 | 81 | 498375.9997 | 83.5 | 511575.9997 | 86.5 | 515575.9997 | 89.5 | 511375.9997 | 92 | 510175.9997 | 95 | 507975.9997 | 118.5 | #VALUE!
100.5 | 501175.9997 | 103.5 | 511375.9997 | 106 | 505375.9997 | 109 | 501375.9997 | 111.5 | 494375.9997 | 114.5 | 508775.9997 | 117.5 | 500975.9997 | 120 | 496375.9997 | 123 | 498375.9997 | 125.5 | 511575.9997 | 128.5 | 515575.9997 | 131.5 | 511375.9997 | 134 | 510175.9997 | 137 | 507975.9997 | 160.5 | #VALUE!
142.5 | 501175.9997 | 145.5 | 511375.9997 | 148 | 505375.9997 | 151 | 501375.9997 | 153.5 | 494375.9997 | 156.5 | 508775.9997 | 159.5 | 500975.9997 | 162 | 496375.9997 | 165 | 498375.9997 | 167.5 | 511575.9997 | 170.5 | 515575.9997 | 173.5 | 511375.9997 | 176 | 510175.9997 | 179 | 507975.9997 | 202.5 | #VALUE!
184.5 | 501175.9997 | 187.5 | 511375.9997 | 190 | 505375.9997 | 193 | 501375.9997 | 195.5 | 494375.9997 | 198.5 | 508775.9997 | 201.5 | 500975.9997 | 204 | 496375.9997 | 207 | 498375.9997 | 209.5 | 511575.9997 | 212.5 | 515575.9997 | 215.5 | 511375.9997 | 218 | 510175.9997 | 221 | 507975.9997 | 244.5 | #VALUE!
226.5 | 501175.9997 | 229.5 | 511375.9997 | 232 | 505375.9997 | 235 | 501375.9997 | 237.5 | 494375.9997 | 240.5 | 508775.9997 | 243.5 | 500975.9997 | 246 | 496375.9997 | 249 | 498375.9997 | 251.5 | 511575.9997 | 254.5 | 515575.9997 | 257.5 | 511375.9997 | 260 | 510175.9997 | 263 | 507975.9997 | 286.5 | #VALUE!
268.5 | 501175.9997 | 271.5 | 511375.9997 | 274 | 505375.9997 | 277 | 501375.9997 | 279.5 | 494375.9997 | 282.5 | 508775.9997 | 285.5 | 500975.9997 | 288 | 496375.9997 | 291 | 498375.9997 | 293.5 | 511575.9997 | 296.5 | 515575.9997 | 299.5 | 511375.9997 | 302 | 510175.9997 | 305 | 507975.9997 | 328.5 | #VALUE!
310.5 | 501175.9997 | 313.5 | 511375.9997 | 316 | 505375.9997 | 319 | 501375.9997 | 321.5 | 494375.9997 | 324.5 | 508775.9997 | 327.5 | 500975.9997 | 330 | 496375.9997 | 333 | 498375.9997 | 335.5 | 511575.9997 | 338.5 | 515575.9997 | 341.5 | 511375.9997 | 344 | 510175.9997 | 347 | 507975.9997 | 370.5 | #VALUE!
352.5 | 501175.9997 | 355.5 | 511375.9997 | 358 | 505375.9997 | 361 | 501375.9997 | 363.5 | 494375.9997 | 366.5 | 508775.9997 | 369.5 | 500975.9997 | 372 | 496375.9997 | 375 | 498375.9997 | 377.5 | 511575.9997 | 380.5 | 515575.9997 | 383.5 | 511375.9997 | 386 | 510175.9997 | 389 | 507975.9997 | 412.5 | #VALUE!
394.5 | 501175.9997 | 397.5 | 511375.9997 | 400 | 505375.9997 | 403 | 501375.9997 | 405.5 | 494375.9997 | 408.5 | 508775.9997 | 411.5 | 500975.9997 | 414 | 496375.9997 | 417 | 498375.9997 | 419.5 | 511575.9997 | 422.5 | 515575.9997 | 425.5 | 511375.9997 | 428 | 510175.9997 | 431 | 507975.9997 | 454.5 | #VALUE!
436.5 | 501175.9997 | 439.5 | 511375.9997 | 442 | 505375.9997 | 444.5 | 501375.9997 | 447.5 | 494375.9997 | 450.5 | 508775.9997 | 453 | 500975.9997 | 456 | 496375.9997 | 459 | 498375.9997 | 461.5 | 511575.9997 | 464.5 | 515575.9997 | 467.5 | 511375.9997 | 470 | 510175.9997 | 473 | 507975.9997 | 496.5 | #VALUE!
478.5 | 501175.9997 | 481.5 | 511375.9997 | 484 | 505375.9997 | 487 | 501375.9997 | 489.5 | 494375.9997 | 492.5 | 508775.9997 | 495.5 | 500975.9997 | 498 | 496375.9997 | 501 | 498375.9997 | 503.5 | 511575.9997 | 506.5 | 515575.9997 | 509.5 | 511375.9997 | 512 | 510175.9997 | 515 | 507975.9997 | 538.5 | #VALUE!
520.5 | 501175.9997 | 523 | 511375.9997 | 526 | 505375.9997 | 529 | 501375.9997 | 531.5 | 494375.9997 | 534.5 | 508775.9997 | 537.5 | 500975.9997 | 540 | 496375.9997 | 543 | 498375.9997 | 545.5 | 511575.9997 | 548.5 | 515575.9997 | 551.5 | 511375.9997 | 554 | 510175.9997 | 557 | 507975.9997 | 580.5 | #VALUE!
562.5 | 501175.9997 | 565 | 511375.9997 | 568 | 505375.9997 | 571 | 501375.9997 | 573.5 | 494375.9997 | 576.5 | 508775.9997 | 579 | 500975.9997 | 582 | 496375.9997 | 584.5 | 498375.9997 | 587.5 | 511575.9997 | 590.5 | 515575.9997 | 593.5 | 511375.9997 | 596 | 510175.9997 | 599 | 507975.9997 | 622.5 | #VALUE!
604.5 | 501175.9997 | 607.5 | 511375.9997 | 610 | 505375.9997 | 612.5 | 501375.9997 | 615.5 | 494375.9997 | 618.5 | 508775.9997 | 621.5 | 500975.9997 | 624 | 496375.9997 | 627 | 498375.9997 | 629.5 | 511575.9997 | 632.5 | 515575.9997 | 635.5 | 511375.9997 | 638 | 510175.9997 | 641 | 507975.9997 | 664.5 | #VALUE!
646.5 | 501175.9997 | 649.5 | 511375.9997 | 652 | 505375.9997 | 655 | 501375.9997 | 657.5 | 494375.9997 | 660.5 | 508775.9997 | 663.5 | 500975.9997 | 666 | 496375.9997 | 668.5 | 498375.9997 | 671.5 | 511575.9997 | 674.5 | 515575.9997 | 677.5 | 511375.9997 | 680 | 510175.9997 | 683 | 507975.9997 | 706.5 | #VALUE!
688.5 | 501175.9997 | 691.5 | 511375.9997 | 694 | 505375.9997 | 697 | 501375.9997 | 699.5 | 494375.9997 | 702.5 | 508775.9997 | 705.5 | 500975.9997 | 708 | 496375.9997 | 711 | 498375.9997 | 713.5 | 511575.9997 | 716.5 | 515575.9997 | 719 | 511375.9997 | 722 | 510175.9997 | 724.5 | 507975.9997 | 748.5 | #VALUE!
730.5 | 501175.9997 | 733.5 | 511375.9997 | 736 | 505375.9997 | 738.5 | 501375.9997 | 741.5 | 494375.9997 | 744.5 | 508775.9997 | 747.5 | 500975.9997 | 750 | 496375.9997 | 753 | 498375.9997 | 755.5 | 511575.9997 | 758.5 | 515575.9997 | 761 | 511375.9997 | 764 | 510175.9997 | 766.5 | 507975.9997 | 790.5 | #VALUE!
772.5 | 501175.9997 | 775 | 511375.9997 | 778 | 505375.9997 | 780.5 | 501375.9997 | 783.5 | 494375.9997 | 786.5 | 508775.9997 | 789 | 500975.9997 | 792 | 496375.9997 | 794.5 | 498375.9997 | 797.5 | 511575.9997 | 800.5 | 515575.9997 | 803 | 511375.9997 | 806 | 510175.9997 | 809 | 507975.9997 | 832.5 | #VALUE!
814.5 | 501175.9997 | 817 | 511375.9997 | 820 | 505375.9997 | 822.5 | 501375.9997 | 825.5 | 494375.9997 | 828.5 | 508775.9997 | 831 | 500975.9997 | 834 | 496375.9997 | 836.5 | 498375.9997 | 839.5 | 511575.9997 | 842.5 | 515575.9997 | 845 | 511375.9997 | 848 | 510175.9997 | 850.5 | 507975.9997 | 874.5 | #VALUE!
856.5 | 501175.9997 | 859.5 | 511375.9997 | 862 | 505375.9997 | 865 | 501375.9997 | 867.5 | 494375.9997 | 870.5 | 508775.9997 | 873.5 | 500975.9997 | 876 | 496375.9997 | 878.5 | 498375.9997 | 881.5 | 511575.9997 | 884.5 | 515575.9997 | 887.5 | 511375.9997 | 890 | 510175.9997 | 893 | 507975.9997 | 916.5 | #VALUE!
898.5 | 501175.9997 | 901.5 | 511375.9997 | 904 | 505375.9997 | 906.5 | 501375.9997 | 909.5 | 494375.9997 | 912.5 | 508775.9997 | 915.5 | 500975.9997 | 918 | 496375.9997 | 920.5 | 498375.9997 | 923.5 | 511575.9997 | 926.5 | 515575.9997 | 929 | 511375.9997 | 932 | 510175.9997 | 934.5 | 507975.9997 | 958.5 | #VALUE!
940.5 | 501175.9997 | 943 | 511375.9997 | 946 | 505375.9997 | 948.5 | 501375.9997 | 951.5 | 494375.9997 | 954.5 | 508775.9997 | 957 | 500975.9997 | 960 | 496375.9997 | 962.5 | 498375.9997 | 965.5 | 511575.9997 | 968.5 | 515575.9997 | 971 | 511375.9997 | 974 | 510175.9997 | 976.5 | 507975.9997 | 1000.5 | #VALUE!
982.5 | 501175.9997 | 985 | 511375.9997 | 988 | 505375.9997 | 990.5 | 501375.9997 | 993.5 | 494375.9997 | 996.5 | 508775.9997 | 999 | 500975.9997 | 1002 | 496375.9997 | 1004.5 | 498375.9997 | 1007.5 | 511575.9997 | 1010.5 | 515575.9997 | 1013 | 511375.9997 | 1016 | 510175.9997 | 1018.5 | 507975.9997 | 1042.5 | #VALUE!
1024.5 | 501175.9997 | 1027 | 511375.9997 | 1030 | 505375.9997 | 1032.5 | 501375.9997 | 1035.5 | 494375.9997 | 1038.5 | 508775.9997 | 1041.5 | 500975.9997 | 1044 | 496375.9997 | 1046.5 | 498375.9997 | 1049.5 | 511575.9997 | 1052.5 | 515575.9997 | 1055.5 | 511375.9997 | 1058 | 510175.9997 | 1060.5 | 507975.9997 | 1084.5 | #VALUE!
1066.5 | 501175.9997 | 1069 | 511375.9997 | 1072 | 505375.9997 | 1074.5 | 501375.9997 | 1077.5 | 494375.9997 | 1080.5 | 508775.9997 | 1083 | 500975.9997 | 1086 | 496375.9997 | 1088.5 | 498375.9997 | 1091.5 | 511575.9997 | 1094.5 | 515575.9997 | 1097 | 511375.9997 | 1100 | 510175.9997 | 1102.5 | 507975.9997 | 1126.5 | #VALUE!
1108.5 | 501175.9997 | 1111 | 511375.9997 | 1114 | 505375.9997 | 1116.5 | 501375.9997 | 1119.5 | 494375.9997 | 1122.5 | 508775.9997 | 1125 | 500975.9997 | 1128 | 496375.9997 | 1130.5 | 498375.9997 | 1133.5 | 511575.9997 | 1136.5 | 515575.9997 | 1139 | 511375.9997 | 1142 | 510175.9997 | 1144.5 | 507975.9997 | 1168.5 | #VALUE!
1150.5 | 501175.9997 | 1153 | 511375.9997 | 1156 | 505375.9997 | 1158.5 | 501375.9997 | 1161.5 | 494375.9997 | 1164.5 | 508775.9997 | 1167 | 500975.9997 | 1170 | 496375.9997 | 1172.5 | 498375.9997 | 1175.5 | 511575.9997 | 1178.5 | 515575.9997 | 1181 | 511375.9997 | 1184 | 510175.9997 | 1186.5 | 507975.9997 | 1210.5 | #VALUE!
1192.5 | 501175.9997 | 1195 | 511375.9997 | 1198 | 505375.9997 | 1200.5 | 501375.9997 | 1203.5 | 494375.9997 | 1206.5 | 508775.9997 | 1209 | 500975.9997 | 1212 | 496375.9997 | 1214.5 | 498375.9997 | 1217.5 | 511575.9997 | 1220.5 | 515575.9997 | 1223 | 511375.9997 | 1226 | 510175.9997 | 1228.5 | 507975.9997 | 1252.5 | #VALUE!
1234.5 | 501175.9997 | 1237 | 511375.9997 | 1240 | 505375.9997 | 1242.5 | 250538.0299 | 1245.5 | 494375.9997 | 1248.5 | 508775.9997 | 1251 | 500975.9997 | 1254 | 496375.9997 | 1256.5 | 498375.9997 | 1259.5 | 511575.9997 | 1262.5 | 515575.9997 | 1265 | 511375.9997 | 1268 | 510175.9997 | 1270.5 | 507975.9997 | 1294.5 | #VALUE!
1276.5 | 501175.9997 | 1279 | 511375.9997 | 1282 | 505375.9997 | 1284.5 | 501375.9997 | 1287.5 | 494375.9997 | 1290.5 | 508775.9997 | 1293 | 500975.9997 | 1296 | 496375.9997 | 1298.5 | 498375.9997 | 1301.5 | 511575.9997 | 1304.5 | 515575.9997 | 1307 | 511375.9997 | 1310 | 510175.9997 | 1312.5 | 507975.9997 | 1336.5 | #VALUE!
1318.5 | 250438.0299 | 1321 | 511375.9997 | 1324 | 505375.9997 | 1326.5 | 501375.9997 | 1329.5 | 494375.9997 | 1332.5 | 508775.9997 | 1335 | 500975.9997 | 1338 | 496375.9997 | 1340.5 | 498375.9997 | 1343.5 | 511575.9997 | 1346.5 | 515575.9997 | 1349 | 511375.9997 | 1352 | 510175.9997 | 1354.5 | 507975.9997 | 1378.5 | #VALUE!
1360.5 | 501175.9997 | 1363 | 511375.9997 | 1366 | 505375.9997 | 1368.5 | 501375.9997 | 1371.5 | 247038.0303 | 1374.5 | 508775.9997 | 1377 | 500975.9997 | 1380 | 496375.9997 | 1382.5 | 498375.9997 | 1385.5 | 511575.9997 | 1388.5 | 515575.9997 | 1391 | 511375.9997 | 1394 | 510175.9997 | 1396.5 | 253838.0295 | 1420.5 | #VALUE!
1402.5 | 501175.9997 | 1405 | 511375.9997 | 1408 | 505375.9997 | 1410.5 | 501375.9997 | 1413.5 | 494375.9997 | 1416.5 | 508775.9997 | 1419 | 500975.9997 | 1422 | 496375.9997 | 1424.5 | 498375.9997 | 1427.5 | 511575.9997 | 1430.5 | 515575.9997 | 1433 | 511375.9997 | 1436 | 510175.9997 | 1438.5 | 507975.9997 | 1462.5 | #VALUE!
1444.5 | 501175.9997 | 1447 | 511375.9997 | 1450 | 505375.9997 | 1452.5 | 501375.9997 | 1455.5 | 494375.9997 | 1458.5 | 508775.9997 | 1461 | 500975.9997 | 1464 | 496375.9997 | 1466.5 | 498375.9997 | 1469.5 | 511575.9997 | 1472.5 | 515575.9997 | 1475 | 511375.9997 | 1478 | 510175.9997 | 1480.5 | 507975.9997 | 1504.5 | #VALUE!
1486.5 | 501175.9997 | 1489 | 511375.9997 | 1492 | 505375.9997 | 1494.5 | 501375.9997 | 1497.5 | 494375.9997 | 1500.5 | 508775.9997 | 1503 | 500975.9997 | 1506 | 496375.9997 | 1508.5 | 498375.9997 | 1511.5 | 511575.9997 | 1514.5 | 515575.9997 | 1517 | 511375.9997 | 1520 | 510175.9997 | 1522.5 | 507975.9997 | 1546.5 | #VALUE!
1528.5 | 501175.9997 | 1531 | 511375.9997 | 1534 | 505375.9997 | 1536.5 | 501375.9997 | 1539.5 | 494375.9997 | 1542.5 | 508775.9997 | 1545 | 500975.9997 | 1548 | 496375.9997 | 1550.5 | 498375.9997 | 1553.5 | 511575.9997 | 1556.5 | 515575.9997 | 1559 | 511375.9997 | 1562 | 510175.9997 | 1564.5 | 507975.9997 | 1588.5 | #VALUE!
1570.5 | 501175.9997 | 1573 | 511375.9997 | 1576 | 505375.9997 | 1578.5 | 501375.9997 | 1581.5 | 494375.9997 | 1584.5 | 508775.9997 | 1587 | 500975.9997 | 1590 | 496375.9997 | 1592.5 | 498375.9997 | 1595.5 | 511575.9997 | 1598.5 | 515575.9997 | 1601 | 511375.9997 | 1604 | 510175.9997 | 1606.5 | 507975.9997 | 1630.5 | #VALUE!
1612.5 | 501175.9997 | 1615 | 511375.9997 | 1618 | 505375.9997 | 1620.5 | 501375.9997 | 1623.5 | 494375.9997 | 1626.5 | 508775.9997 | 1629 | 500975.9997 | 1632 | 496375.9997 | 1634.5 | 498375.9997 | 1637.5 | 511575.9997 | 1640.5 | 515575.9997 | 1643 | 511375.9997 | 1646 | 510175.9997 | 1648.5 | 507975.9997 | 1672.5 | #VALUE!
1654.5 | 501175.9997 | 1657 | 511375.9997 | 1660 | 505375.9997 | 1662.5 | 501375.9997 | 1665.5 | 494375.9997 | 1668.5 | 508775.9997 | 1671 | 500975.9997 | 1674 | 496375.9997 | 1676.5 | 498375.9997 | 1679.5 | 511575.9997 | 1682.5 | 515575.9997 | 1685 | 511375.9997 | 1688 | 510175.9997 | 1690.5 | 507975.9997 | 1714.5 | #VALUE!
1696 | 501175.9997 | 1699 | 511375.9997 | 1702 | 505375.9997 | 1704.5 | 501375.9997 | 1707.5 | 494375.9997 | 1710 | 508775.9997 | 1713 | 500975.9997 | 1715.5 | 496375.9997 | 1718.5 | 498375.9997 | 1721.5 | 5.9048 | 1724.5 | 63825.6205 | 1727 | 13035.4509 | 1729.5 | 21133.8575 | 1732.5 | 41729.7851 | 1756.5 | #VALUE!
1738 | 250537.9994 | 1741 | 511375.9997 | 1743.5 | 505375.9997 | 1746.5 | 250538.0299 | 1749.5 | 494375.9997 | 1752.5 | 508775.9997 | 1755 | 500975.9997 | 1757.5 | 496375.9997 | 1760.5 | 498375.9997 | 1763.5 | 11.671 | 1766.5 | 13635.3553 | 1769 | 19830.2428 | 1772 | 59526.3322 | 1774.5 | 30631.9698 | 1798.5 | #VALUE!
1780.5 | 125019.1396 | 1783 | 511375.9997 | 1786 | 252637.9994 | 1788.5 | 501375.9997 | 1791.5 | 494375.9997 | 1794.5 | 508775.9997 | 1797 | 500975.9997 | 1800 | 496375.9997 | 1802.5 | 498375.9997 | 1805.5 | 13.5205 | 1808.5 | 17234.6572 | 1811 | 33831.3842 | 1815 | 30532.0154 | 1816.5 | 39530.2181 | 1840.5 | #VALUE!
1822.5 | 9754.3934 | 1825 | 511375.9997 | 1828 | 252637.9994 | 1830.5 | 501375.9997 | 1833.5 | 494375.9997 | 1836.5 | 508775.9997 | 1839 | 500975.9997 | 1842 | 496375.9997 | 1844.5 | 498375.9997 | 1847.5 | 0.68446 | 1850.5 | 1537.7018 | 1853 | 60226.2227 | 1856 | 1537.6986 | 1858.5 | 33531.399 | 1882.5 | #VALUE!
1864.5 | 2589.5922 | 1867 | 511375.9997 | 1870 | 505375.9997 | 1872.5 | 250637.9994 | 1875.5 | 494375.9997 | 1878 | 508775.9997 | 1881 | 500975.9997 | 1883.5 | 496375.9997 | 1886.5 | 498375.9997 | 1889.5 | 12470.6324 | 1892 | 11335.8013 | 1895 | 10233.9967 | 1897.5 | 20334.0143 | 1900.5 | 46728.801 | 1924.5 | #VALUE!
1906.5 | 1414.9108 | 1909 | 429.1834 | 1912 | 228.1885 | 1914.5 | 127112.6472 | 1917.5 | 23633.2196 | 1920.5 | 1446.156 | 1923 | 26.2352 | 1926 | 167870.348 | 1928.5 | 18034.3814 | 1931.5 | 31.1037 | 1934.5 | 19534.2112 | 1937 | 48128.5884 | 1940 | 11135.8173 | 1942.5 | 6836.6541 | 1966.5 | #VALUE!
1948.5 | 574.7246 | 1951 | 36.0605 | 1954 | 7.57 | 1956.5 | 19730.128 | 1959.5 | 1737.6485 | 1962.5 | 4381.1697 | 1965 | 0.68005 | 1968 | 27326.9872 | 1970.5 | 22933.3984 | 1973.5 | 0.26026 | 1976.5 | 15335.0257 | 1979 | 54927.2589 | 1982 | 17334.6022 | 1984.5 | 1537.6973 | 2008.5 | #VALUE!
1990.5 | 769.0615 | 1993 | 19.452 | 1995.5 | 20.594 | 1998.5 | 53427.3439 | 2001.5 | 31031.7231 | 2004 | 7003.6451 | 2007 | 10.7331 | 2009.5 | 29726.0204 | 2012.5 | 53716.4391 | 2015.5 | 13.9396 | 2018 | 22533.6294 | 2021 | 47019.607 | 2024 | 53127.5864 | 2026.5 | 51917.555 | 2050.5 | #VALUE!
2032.5 | 7949.8681 | 2035 | 22.1006 | 2038 | 3.1791 | 2040.5 | 6836.6364 | 2043.5 | 10235.9295 | 2046 | 1097.3567 | 2049 | 3.6807 | 2052 | 57926.3302 | 2054.5 | 20933.7996 | 2057.5 | 3054.7012 | 2060 | 29132.3496 | 2063 | 6636.7022 | 2065.5 | 56626.9005 | 2068.5 | 29532.1863 | 2092.5 | #VALUE!
2074 | 1780.5027 | 2077 | 89.2728 | 2079.5 | 1.1948 | 2082.5 | 53016.8472 | 2085.5 | 38930.1254 | 2088 | 1863.596 | 2091 | 11.9127 | 2093.5 | 8836.2199 | 2096.5 | 44229.1254 | 2099.5 | 0.46339 | 2102 | 36230.9727 | 2105 | 6135.5999 | 2107.5 | 5037.0127 | 2110.5 | 58026.5769 | 2134.5 | #VALUE!
2116 | 3078.3578 | 2119 | 12.0836 | 2121.5 | 26.0474 | 2124.5 | 15834.8417 | 2127.5 | 49827.921 | 2130 | 2253.1683 | 2133 | 1.3609 | 2135.5 | 43320.5418 | 2138.5 | 37830.4093 | 2141.5 | 26.5046 | 2144 | 2137.5854 | 2147 | 1537.6993 | 2149.5 | 37830.5848 | 2152.5 | 57326.7147 | 2176.5 | #VALUE!
2158 | 363.5723 | 2161 | 4.4658 | 2164 | 7.3325 | 2166.5 | 14735.0611 | 2169.5 | 30731.7837 | 2172 | 6281.8653 | 2175 | 2.2245 | 2177.5 | 21133.7424 | 2180.5 | 26432.6962 | 2183.5 | 17.0694 | 2186 | 56327.0749 | 2189 | 37030.7586 | 2191.5 | 22433.6028 | 2194.5 | 57326.7147 | 2218.5 | #VALUE!
2200 | 9.7211 | 2203 | 18.4802 | 2205.5 | 14.2286 | 2208.5 | 1537.6933 | 2211.5 | 26332.6736 | 2214 | 1310.5984 | 2217 | 23.7955 | 2219.5 | 50827.7602 | 2222.5 | 42229.5266 | 2225.5 | 27.4122 | 2228 | 36730.8758 | 2231 | 46428.9208 | 2233.5 | 54227.3709 | 2236.5 | 50628.0334 | 2260.5 | #VALUE!
2242 | 623.2034 | 2245 | 33.0827 | 2247.5 | 25.5319 | 2250.5 | 8336.3373 | 2253.5 | 16334.6959 | 2256 | 5844.2593 | 2259 | 30.9125 | 2261.5 | 1537.3804 | 2264.5 | 49917.9637 | 2267.5 | 27.4775 | 2270 | 37723.3637 | 2273 | 15634.9426 | 2275.5 | 57526.7241 | 2278.5 | 43329.4702 | 2302.5 | #VALUE!
2284 | 776.9223 | 2287 | 2.1148 | 2289.5 | 10.4012 | 2292.5 | 3037.3942 | 2295.5 | 32031.5208 | 2298 | 6274.7744 | 2301 | 30.9828 | 2303.5 | 28332.2922 | 2306.5 | 29332.1145 | 2309.5 | 0.30095 | 2312 | 61426.0859 | 2315 | 55427.1612 | 2317.5 | 10935.8565 | 2320.5 | 31531.7927 | 2344.5 | #VALUE!
2326 | 2026.5029 | 2329 | 22.7654 | 2331.5 | 27.4863 | 2334.5 | 10333.877 | 2337.5 | 51727.5368 | 2340 | 10567.1804 | 2343 | 1.2753 | 2345.5 | 57414.8617 | 2348.5 | 4937.0094 | 2351.5 | 14.7334 | 2354 | 32731.6514 | 2357 | 7734.9742 | 2359.5 | 61325.9794 | 2362.5 | 11535.7291 | 2386.5 | #VALUE!
2368 | 743.9919 | 2371 | 23.6834 | 2373.5 | 9.9029 | 2376.5 | 50128.0019 | 2379.5 | 1537.689 | 2382 | 8579.4018 | 2385 | 1.6185 | 2387.5 | 34531.0434 | 2390.5 | 17830.843 | 2393.5 | 27.1516 | 2396 | 11533.5251 | 2399 | 53727.4935 | 2401.5 | 62825.6855 | 2404.5 | 39730.1787 | 2428.5 | #VALUE!
2410 | 187.4449 | 2413 | 768.9352 | 2415.5 | 3221.0919 | 2418.5 | 25732.8676 | 2421.5 | 24133.1185 | 2424 | 728.1731 | 2427 | 8987.613 | 2429.5 | 17334.5078 | 2432.5 | 23333.3181 | 2435.5 | 675.286 | 2438 | 13635.3553 | 2441 | 63725.5384 | 2443.5 | 15235.0138 | 2446.5 | 50528.0531 | 2470.5 | #VALUE!
2452 | 612.0494 | 2455 | 737.3643 | 2457.5 | 594.1661 | 2460.5 | 37722.9492 | 2463.5 | 52527.375 | 2466 | 1469.2203 | 2469 | 1758.7097 | 2471.5 | 64325.0411 | 2474.5 | 26632.6561 | 2477.5 | 765.8626 | 2480 | 53127.6955 | 2483 | 65925.1083 | 2485.5 | 55027.2141 | 2488.5 | 38630.3952 | 2512.5 | #VALUE!
2494 | 161.6011 | 2497 | 1549.3425 | 2499.5 | 4791.36 | 2502.5 | 61613.4174 | 2505.5 | 24033.1387 | 2508 | 847.8793 | 2511 | 1128.4281 | 2513.5 | 65124.8799 | 2516.5 | 54227.1192 | 2519.5 | 2959.7389 | 2522 | 14635.1614 | 2525 | 68024.6977 | 2527.5 | 13735.3077 | 2530.5 | 34031.3006 | 2554.5 | #VALUE!
2536 | 705.3318 | 2539 | 3805.9824 | 2541.5 | 9936.043 | 2544.5 | 52517.0467 | 2547.5 | 13435.2824 | 2550 | 11957.796 | 2553 | 2156.3645 | 2555.5 | 40329.8751 | 2558.5 | 19334.1206 | 2561.5 | 4180.1898 | 2564 | 64725.446 | 2567 | 5436.9368 | 2569.5 | 15534.955 | 2572.5 | 63825.4353 | 2596.5 | #VALUE!
2578 | 2627.1768 | 2581 | 2633.059 | 2583.5 | 7.3799 | 2586.5 | 35330.9532 | 2589.5 | 4237.1429 | 2592 | 4586.4322 | 2595 | 8932.4711 | 2597.5 | 25032.9569 | 2600.5 | 55726.8183 | 2603.5 | 12.3322 | 2606 | 58726.6095 | 2609 | 30232.0881 | 2611.5 | 55027.2141 | 2614.5 | 43629.4111 | 2638.5 | #VALUE!
2620 | 1341.7898 | 2623 | 21.6214 | 2625.5 | 250.2617 | 2628.5 | 36730.674 | 2631.5 | 61225.6156 | 2634 | 6622.9842 | 2637 | 10.8856 | 2639.5 | 62125.4842 | 2642.5 | 16134.7625 | 2645.5 | 802.361 | 2648 | 35631.0891 | 2651 | 57326.7897 | 2653.5 | 33331.4667 | 2656.5 | 42129.7064 | 2680.5 | #VALUE!
2662 | 583.5301 | 2665 | 8.2886 | 2667.5 | 6.5324 | 2670.5 | 40629.8963 | 2673.5 | 15434.8779 | 2676 | 6922.4331 | 2679 | 12.1723 | 2681.5 | 11935.5955 | 2684.5 | 30131.954 | 2687.5 | 9095.4129 | 2690 | 64925.4072 | 2693 | 2437.5233 | 2695.5 | 37830.5848 | 2698.5 | 21033.8593 | 2722.5 | #VALUE!
2704 | 3846.0084 | 2707 | 31.6061 | 2709.5 | 33.6489 | 2712 | 29526.2196 | 2715.5 | 6436.698 | 2718 | 11233.9794 | 2721 | 10.6316 | 2723.5 | 43420.5015 | 2726.5 | 1537.3829 | 2729.5 | 25.9277 | 2732 | 45020.5324 | 2735 | 56016.0877 | 2737.5 | 40330.0949 | 2740.5 | 35031.1038 | 2764.5 | #VALUE!
2746 | 8512.5753 | 2749 | 7.39 | 2751.5 | 28.4859 | 2754.5 | 37123.1885 | 2757.5 | 10035.97 | 2760 | 837.8522 | 2763 | 28.9744 | 2765.5 | 43020.6626 | 2768.5 | 45928.7843 | 2771.5 | 17.0694 | 2774 | 43029.6541 | 2777 | 38830.4067 | 2779.5 | 9536.1308 | 2782.5 | 9536.1227 | 2806.5 | #VALUE!
2788 | 3160.5377 | 2791 | 32.5164 | 2793.5 | 6.3924 | 2796.5 | 31131.7907 | 2799.5 | 8936.1924 | 2802 | 3266.3912 | 2805 | 1.1472 | 2807.5 | 6735.2857 | 2810.5 | 41429.6871 | 2813.5 | 3.5804 | 2816 | 61714.0555 | 2819 | 58526.5551 | 2821.5 | 12235.6017 | 2824.5 | 54227.3248 | 2848.5 | #VALUE!
2830 | 475.8118 | 2832.5 | 16.1436 | 2835.5 | 1.7909 | 2838.5 | 33131.3919 | 2841 | 18934.1701 | 2844 | 4619.0759 | 2847 | 27.6908 | 2849.5 | 2137.5694 | 2852.5 | 21333.7194 | 2855.5 | 2.4974 | 2858 | 28232.5241 | 2861 | 24633.183 | 2863.5 | 60826.0774 | 2866.5 | 44729.1946 | 2890 | #VALUE!
2872 | 324.1116 | 2874.5 | 974.033 | 2877.5 | 15.253 | 2880.5 | 13032.8001 | 2883 | 25632.8151 | 2886 | 9519.5318 | 2888.5 | 12.3809 | 2891.5 | 59925.9273 | 2894.5 | 61125.735 | 2897 | 21.3717 | 2900 | 57215.8008 | 2902.5 | 11735.7051 | 2905.5 | 60326.1754 | 2908.5 | 38230.474 | 2932 | #VALUE!
2914 | 1379.0003 | 2916.5 | 2.371 | 2919.5 | 13.3795 | 2922.5 | 2836.8681 | 2925 | 54826.9099 | 2928 | 174.9182 | 2930.5 | 20.1246 | 2933.5 | 24133.1381 | 2936.5 | 1537.6915 | 2939.5 | 24.664 | 2942 | 18330.8878 | 2945 | 1737.6602 | 2947.5 | 53027.606 | 2950.5 | 17834.4891 | 2974.5 | #VALUE!
2956 | 3326.0931 | 2959 | 2.2001 | 2961.5 | 1.7481 | 2964.5 | 41529.7169 | 2967.5 | 52327.4155 | 2970 | 3777.1899 | 2973 | 11.8609 | 2975.5 | 59825.9475 | 2978.5 | 2737.4507 | 2981.5 | 29.333 | 2984 | 6236.7903 | 2987 | 59426.3791 | 2989.5 | 61225.999 | 2992.5 | 42229.6867 | 2996 | #VALUE!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 13 |  |  | 2006-11-28 | 9:21
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G
-229.8 | 494376 |  | -220.8 | 496376 | -215.2 | 508776 | -211.9 | 500976 | -209.7 | #VALUE! | -207.4 | #VALUE!
-187.9 | 494376 |  | -178.9 | 496376 | -173.3 | 508776 | -170 | 500976 | -167.8 | #VALUE! | -165.5 | #VALUE!
-145.9 | 494376 |  | -136.9 | 496376 | -131.3 | 508776 | -128 | 500976 | -125.8 | #VALUE! | -123.5 | #VALUE!
-103.9 | 494376 |  | -94.8 | 496376 | -89.3 | 508776 | -86 | 500976 | -83.7 | #VALUE! | -81.5 | #VALUE!
-61.9 | 494376 |  | -52.9 | 496376 | -47.3 | 508776 | -44 | 500976 | -41.8 | #VALUE! | -39.5 | #VALUE!
-19.9 | 494376 |  | -10.9 | 496376 | -5.3 | 508776 | -2 | 500976 | 4.4 | #VALUE! | 6.7 | #VALUE!
22.1 | 494376 |  | 31.1 | 496376 | 36.7 | 508776 | 40 | 500976 | 46.4 | #VALUE! | 48.7 | #VALUE!
64.1 | 494376 |  | 73.1 | 496376 | 78.7 | 508776 | 82 | 500976 | 88.4 | #VALUE! | 90.7 | #VALUE!
106.1 | 494376 |  | 115.1 | 496376 | 120.7 | 508776 | 124 | 500976 | 130.4 | #VALUE! | 132.7 | #VALUE!
148.1 | 494376 |  | 157.1 | 496376 | 162.7 | 508776 | 166 | 500976 | 172.4 | #VALUE! | 174.7 | #VALUE!
190.1 | 494376 |  | 199.1 | 496376 | 204.7 | 508776 | 208 | 500976 | 214.4 | #VALUE! | 216.7 | #VALUE!
232.1 | 494376 |  | 241.1 | 496376 | 246.7 | 508776 | 250 | 500976 | 256.4 | #VALUE! | 258.7 | #VALUE!
274.1 | 494376 |  | 283.1 | 496376 | 288.7 | 508776 | 292 | 500976 | 298.4 | #VALUE! | 300.7 | #VALUE!
316.1 | 494376 |  | 325.1 | 496376 | 330.7 | 508776 | 334 | 500976 | 340.4 | #VALUE! | 342.7 | #VALUE!
358.1 | 494376 |  | 367.1 | 496376 | 372.7 | 508776 | 376 | 500976 | 382.4 | #VALUE! | 384.7 | #VALUE!
400.1 | 494376 |  | 409.1 | 496376 | 414.7 | 508776 | 418 | 500976 | 424.4 | #VALUE! | 426.7 | #VALUE!
442 | 494376 |  | 451 | 496376 | 456.7 | 508776 | 459.9 | 500976 | 466.3 | #VALUE! | 468.7 | #VALUE!
484.1 | 494376 |  | 493.1 | 496376 | 498.7 | 508776 | 502 | 500976 | 508.4 | #VALUE! | 510.7 | #VALUE!
526 | 494376 |  | 535.1 | 496376 | 540.6 | 508776 | 544 | 500976 | 550.4 | #VALUE! | 552.7 | #VALUE!
568 | 494376 |  | 576.9 | 496376 | 582.6 | 508776 | 585.9 | 500976 | 592.4 | #VALUE! | 594.6 | #VALUE!
610 | 494376 |  | 619.1 | 496376 | 624.7 | 508776 | 628 | 500976 | 634.3 | #VALUE! | 636.7 | #VALUE!
652.1 | 494376 |  | 661 | 496376 | 666.7 | 508776 | 670 | 500976 | 676.4 | #VALUE! | 678.6 | #VALUE!
694.1 | 494376 |  | 703.1 | 496376 | 708.6 | 508776 | 711.9 | 500976 | 718.4 | #VALUE! | 720.5 | #VALUE!
736 | 494376 |  | 745.1 | 496376 | 750.6 | 508776 | 753.9 | 500976 | 760.3 | #VALUE! | 762.5 | #VALUE!
777.9 | 494376 |  | 786.9 | 496376 | 792.5 | 508776 | 795.9 | 500976 | 802.3 | #VALUE! | 804.5 | #VALUE!
819.9 | 494376 |  | 828.9 | 496376 | 834.5 | 508776 | 837.8 | 500976 | 844.3 | #VALUE! | 846.4 | #VALUE!
862.1 | 494376 |  | 871 | 496376 | 876.7 | 508776 | 880 | 500976 | 886.4 | #VALUE! | 888.6 | #VALUE!
904 | 494376 |  | 913 | 496376 | 918.6 | 508776 | 921.9 | 500976 | 928.3 | #VALUE! | 930.4 | #VALUE!
945.9 | 494376 |  | 954.9 | 496376 | 960.5 | 508776 | 963.8 | 500976 | 970.3 | #VALUE! | 972.4 | #VALUE!
987.9 | 494376 |  | 996.9 | 496376 | 1002.5 | 508776 | 1005.8 | 500976 | 1012.3 | #VALUE! | 1014.4 | #VALUE!
1029.9 | 494376 |  | 1039 | 496376 | 1044.6 | 508776 | 1047.9 | 500976 | 1054.3 | #VALUE! | 1056.5 | #VALUE!
1071.9 | 494376 |  | 1080.9 | 496376 | 1086.5 | 508776 | 1089.8 | 500976 | 1096.3 | #VALUE! | 1098.4 | #VALUE!
1113.9 | 494376 |  | 1122.9 | 496376 | 1128.5 | 508776 | 1131.8 | 500976 | 1138.3 | #VALUE! | 1140.4 | #VALUE!
1155.9 | 494376 |  | 1164.9 | 496376 | 1170.5 | 508776 | 1173.8 | 500976 | 1180.3 | #VALUE! | 1182.4 | #VALUE!
1197.9 | 494376 |  | 1206.9 | 496376 | 1212.5 | 508776 | 1215.8 | 500976 | 1222.3 | #VALUE! | 1224.4 | #VALUE!
1239.9 | 494376 |  | 1248.9 | 496376 | 1254.5 | 508776 | 1257.8 | 500976 | 1264.3 | #VALUE! | 1266.4 | #VALUE!
1281.9 | 494376 |  | 1290.9 | 496376 | 1296.5 | 508776 | 1299.8 | 500976 | 1306.3 | #VALUE! | 1308.4 | #VALUE!
1323.9 | 494376 |  | 1332.9 | 496376 | 1338.5 | 508776 | 1341.8 | 500976 | 1348.3 | #VALUE! | 1350.4 | #VALUE!
1365.9 | 494576.0809 |  | 1374.9 | 496376 | 1380.5 | 508776 | 1383.8 | 500976 | 1390.3 | #VALUE! | 1392.4 | #VALUE!
1407.9 | 494376 |  | 1416.9 | 496376 | 1422.5 | 508776 | 1425.8 | 500976 | 1432.3 | #VALUE! | 1434.4 | #VALUE!
1449.9 | 494376 |  | 1458.9 | 496376 | 1464.5 | 508776 | 1467.8 | 500976 | 1474.3 | #VALUE! | 1476.4 | #VALUE!
1491.9 | 494376 |  | 1500.9 | 496376 | 1506.5 | 508776 | 1509.8 | 500976 | 1516.3 | #VALUE! | 1518.4 | #VALUE!
1533.9 | 494376 |  | 1542.9 | 496376 | 1548.5 | 508776 | 1551.8 | 500976 | 1558.3 | #VALUE! | 1560.4 | #VALUE!
1575.9 | 494376 |  | 1584.9 | 496376 | 1590.5 | 508776 | 1593.8 | 500976 | 1600.3 | #VALUE! | 1602.4 | #VALUE!
1617.9 | 494376 |  | 1626.9 | 496376 | 1632.5 | 508776 | 1635.8 | 500976 | 1642.3 | #VALUE! | 1644.4 | #VALUE!
1659.9 | 494376 |  | 1668.9 | 496376 | 1674.5 | 508776 | 1677.8 | 500976 | 1684.3 | #VALUE! | 1686.4 | #VALUE!
1701.8 | 494376 |  | 1710.6 | 496376 | 1716.4 | 5.4177 | 1719.7 | 3.7461 | 1726.1 | #VALUE! | 1728.4 | #VALUE!
1743.7 | 250538 |  | 1752.7 | 496376 | 1758.5 | 5.6303 | 1761.7 | 2.8226 | 1768.2 | #VALUE! | 1770.4 | #VALUE!
1785.9 | 250537.8401 |  | 1794.9 | 250738.3201 | 1800.5 | 7.2121 | 1804 | 6.7306 | 1810.5 | #VALUE! | 1812.4 | #VALUE!
1827.9 | 50860.4988 |  | 1836.9 | 19078.9044 | 1842.5 | 0.63959 | 1845.8 | 0.64641 | 1852.3 | #VALUE! | 1854.4 | #VALUE!
1869.9 | 5185.8139 |  | 1878.7 | 6946.0836 | 1884.3 | 2.0096 | 1887.7 | 8.7119 | 1894 | #VALUE! | 1896.4 | #VALUE!
1911.9 | 10.6258 |  | 1920.9 | 7.8519 | 1926.5 | 0.64794 | 1929.8 | 2.8089 | 1936.3 | #VALUE! | 1938.4 | #VALUE!
1953.9 | 0.74929 |  | 1962.9 | 2.177 | 1968.5 | 1.2819 | 1971.8 | 0.64923 | 1978.3 | #VALUE! | 1980.4 | #VALUE!
1995.8 | 14.4157 |  | 2004.7 | 1.6409 | 2010.3 | 9.6291 | 2013.7 | 1.2017 | 2020.1 | #VALUE! | 2022.4 | #VALUE!
2037.9 | 2.8469 |  | 2046.8 | 5.1355 | 2052.3 | 2.7071 | 2055.7 | 5.1965 | 2062.1 | #VALUE! | 2064.4 | #VALUE!
2079.7 | 2.6973 |  | 2088.6 | 3.7366 | 2094.3 | 0.64463 | 2097.6 | 0.64437 | 2104 | #VALUE! | 2106.4 | #VALUE!
2121.7 | 5.2748 |  | 2130.6 | 2.8481 | 2136.3 | 0.64488 | 2139.6 | 0.6581 | 2146 | #VALUE! | 2148.4 | #VALUE!
2163.8 | 5.9395 |  | 2172.6 | 0.65895 | 2178.3 | 16.9968 | 2181.7 | 9.6938 | 2188 | #VALUE! | 2190.4 | #VALUE!
2205.7 | 0.65783 |  | 2214.6 | 20.4729 | 2220.3 | 3.0531 | 2223.6 | 1.8284 | 2230 | #VALUE! | 2232.4 | #VALUE!
2247.7 | 3.4839 |  | 2256.6 | 0.6645 | 2262.3 | 6.5602 | 2265.6 | 2.3352 | 2272 | #VALUE! | 2274.4 | #VALUE!
2289.7 | 1.2679 |  | 2298.6 | 12.944 | 2304.3 | 1.2418 | 2307.6 | 4.5238 | 2314 | #VALUE! | 2316.4 | #VALUE!
2331.7 | 4.3455 |  | 2340.6 | 2.0639 | 2346.3 | 3.163 | 2349.6 | 4.8031 | 2356 | #VALUE! | 2358.4 | #VALUE!
2373.7 | 0.66721 |  | 2382.6 | 3.1021 | 2388.3 | 4.729 | 2391.6 | 17.2493 | 2398 | #VALUE! | 2400.4 | #VALUE!
2415.7 | 6.4332 |  | 2424.6 | 7.3393 | 2430.3 | 5.3143 | 2433.6 | 6.234 | 2440 | #VALUE! | 2442.4 | #VALUE!
2457.7 | 5.5781 |  | 2466.6 | 12.0225 | 2472.3 | 23.8079 | 2475.6 | 7.0976 | 2482 | #VALUE! | 2484.4 | #VALUE!
2499.7 | 10.8242 |  | 2508.6 | 27.8943 | 2514.3 | 5.214 | 2517.6 | 5.7371 | 2524 | #VALUE! | 2526.4 | #VALUE!
2541.7 | 5.7954 |  | 2550.6 | 8.4623 | 2556.3 | 2.2143 | 2559.6 | 6.5322 | 2566 | #VALUE! | 2568.4 | #VALUE!
2583.7 | 1.7867 |  | 2592.6 | 7.7344 | 2598.3 | 13.4656 | 2601.6 | 11.8173 | 2608 | #VALUE! | 2610.4 | #VALUE!
2625.7 | 6.0215 |  | 2634.6 | 6.9721 | 2640.3 | 3.2988 | 2643.6 | 1.8284 | 2650 | #VALUE! | 2652.4 | #VALUE!
2667.7 | 6.709 |  | 2676.6 | 3.8075 | 2682.3 | 1.0028 | 2685.6 | 5.7569 | 2692 | #VALUE! | 2694.4 | #VALUE!
2709.6 | 2.7174 |  | 2718.6 | 0.66182 | 2724.3 | 3.2451 | 2727.6 | 12.4497 | 2733.9 | #VALUE! | 2736.4 | #VALUE!
2751.7 | 4.2776 |  | 2760.6 | 4.777 | 2766.3 | 4.2552 | 2769.6 | 3.4943 | 2776 | #VALUE! | 2778.4 | #VALUE!
2793.7 | 3.7959 |  | 2802.6 | 2.6374 | 2808.3 | 5.0669 | 2811.6 | 5.0836 | 2818 | #VALUE! | 2820.4 | #VALUE!
2835.5 | 3.2848 |  | 2844.6 | 0.91013 | 2850.2 | 3.9992 | 2853.6 | 0.65233 | 2859.9 | #VALUE! | 2862.2 | #VALUE!
2877.5 | 2.9563 |  | 2886.5 | 13.7258 | 2892 | 4.2977 | 2895.4 | 8.0837 | 2901.9 | #VALUE! | 2904.1 | #VALUE!
2919.5 | 1.1861 |  | 2928.5 | 0.66182 | 2934.2 | 0.72419 | 2937.5 | 7.6008 | 2944 | #VALUE! | 2946.3 | #VALUE!
2961.7 | 3.2426 |  | 2970.6 | 1.1523 | 2976.3 | 2.5211 | 2979.6 | 11.6977 | 2981.9 | #VALUE! | 2984.3 | #VALUE!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C5-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | #VALUE! |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39049.3848 | 0 | 0 | 39049.3848 | 0 | 0 |  | -196.5 | 39.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3852 | 0 | 0 | 39049.3853 | 0 | 0 |  | -154.5 | 81.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3857 | 0 | 0 | 39049.3857 | 0 | 0 |  | -112.5 | 123.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3862 | 0 | 0 | 39049.3862 | 0 | 0 |  | -70.5 | 165.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3867 | 0 | 0 | 39049.3867 | 0 | 0 |  | -28.5 | 207.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3877 | 0 | 0 | 39049.3872 | 0 | 0 |  | 34.5 | 270.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3882 | 0 | 0 | 39049.3877 | 0 | 0 |  | 76.5 | 312.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3886 | 0 | 0 | 39049.3882 | 0 | 0 |  | 118.5 | 354.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3891 | 0 | 0 | 39049.3887 | 0 | 0 |  | 160.5 | 396.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3896 | 0 | 0 | 39049.3891 | 0 | 0 |  | 202.5 | 438.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3901 | 0 | 0 | 39049.3896 | 0 | 0 |  | 244.5 | 480.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3906 | 0 | 0 | 39049.3901 | 0 | 0 |  | 286.5 | 522.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3911 | 0 | 0 | 39049.3906 | 0 | 0 |  | 328.5 | 564.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3916 | 0 | 0 | 39049.3911 | 0 | 0 |  | 370.5 | 606.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.392 | 0 | 0 | 39049.3916 | 0 | 0 |  | 412.5 | 648.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3925 | 0 | 0 | 39049.3921 | 0 | 0 |  | 454.5 | 690.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.393 | 0 | 0 | 39049.3925 | 0 | 0 |  | 496.5 | 732.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3935 | 0 | 0 | 39049.393 | 0 | 0 |  | 538.5 | 774.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.394 | 0 | 0 | 39049.3935 | 0 | 0 |  | 580.5 | 816.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3945 | 0 | 0 | 39049.394 | 0 | 0 |  | 622.5 | 858.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.395 | 0 | 0 | 39049.3945 | 0 | 0 |  | 664.5 | 900.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3955 | 0 | 0 | 39049.395 | 0 | 0 |  | 706.5 | 942.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3959 | 0 | 0 | 39049.3955 | 0 | 0 |  | 748.5 | 984.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3964 | 0 | 0 | 39049.3959 | 0 | 0 |  | 790.5 | 1026.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3969 | 0 | 0 | 39049.3964 | 0 | 0 |  | 832.5 | 1068.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3974 | 0 | 0 | 39049.3969 | 0 | 0 |  | 874.5 | 1110.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3979 | 0 | 0 | 39049.3974 | 0 | 0 |  | 916.5 | 1152.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3984 | 0 | 0 | 39049.3979 | 0 | 0 |  | 958.5 | 1194.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3989 | 0 | 0 | 39049.3984 | 0 | 0 |  | 1000.5 | 1236.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3993 | 0 | 0 | 39049.3989 | 0 | 0 |  | 1042.5 | 1278.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.3998 | 0 | 0 | 39049.3994 | 0 | 0 |  | 1084.5 | 1320.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4003 | 0 | 0 | 39049.3998 | 0 | 0 |  | 1126.5 | 1362.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4008 | 0 | 0 | 39049.4003 | 0 | 0 |  | 1168.5 | 1404.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4013 | 0 | 0 | 39049.4008 | 0 | 0 |  | 1210.5 | 1446.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4018 | 0 | 0 | 39049.4013 | 0 | 0 |  | 1252.5 | 1488.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4023 | 0 | 0 | 39049.4018 | 0 | 0 |  | 1294.5 | 1530.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4027 | 0 | 0 | 39049.4023 | 0 | 0 |  | 1336.5 | 1572.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4032 | 0 | 0 | 39049.4028 | 0 | 0 |  | 1378.5 | 1614.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4037 | 0 | 0 | 39049.4032 | 0 | 0 |  | 1420.5 | 1656.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4042 | 0 | 0 | 39049.4037 | 0 | 0 |  | 1462.5 | 1698.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4047 | 0 | 0 | 39049.4042 | 0 | 0 |  | 1504.5 | 1740.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4052 | 0 | 0 | 39049.4047 | 0 | 0 |  | 1546.5 | 1782.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4057 | 0 | 0 | 39049.4052 | 0 | 0 |  | 1588.5 | 1824.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4061 | 0 | 0 | 39049.4057 | 0 | 0 |  | 1630.5 | 1866.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4066 | 0 | 0 | 39049.4062 | 0 | 0 |  | 1672.5 | 1908.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4071 | 0 | 0 | 39049.4066 | 0 | 0 |  | 1714.5 | 1950.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4076 | 0 | 0 | 39049.4071 | 0 | 0 |  | 1756.5 | 1992.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4081 | 0 | 0 | 39049.4076 | 0 | 0 |  | 1798.5 | 2034.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4086 | 0 | 0 | 39049.4081 | 1 | 0 |  | 1840.5 | 2076.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
39049.4091 | 0 | 0 | 39049.4086 | 0 | 0 |  | 1882.5 | 2118.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4095 | 0 | 0 | 39049.4091 | 0 | 1 |  | 1924.5 | 2160.5 | 0.030525 | 0 | 0.030525 | 0.06105 | 0.00030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.41 | 0 | 0 | 39049.4096 | 0 | 0 |  | 1966.5 | 2202.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4105 | 0 | 0 | 39049.41 | 0 | 0 |  | 2008.5 | 2244.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.411 | 0 | 0 | 39049.4105 | 0 | 0 |  | 2050.5 | 2286.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4115 | 0 | 0 | 39049.411 | 0 | 0 |  | 2092.5 | 2328.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.412 | 0 | 0 | 39049.4115 | 0 | 0 |  | 2134.5 | 2370.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4125 | 0 | 0 | 39049.412 | 0 | 0 |  | 2176.5 | 2412.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.413 | 0 | 0 | 39049.4125 | 0 | 0 |  | 2218.5 | 2454.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4134 | 0 | 0 | 39049.413 | 0 | 0 |  | 2260.5 | 2496.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4139 | 0 | 0 | 39049.4134 | 0 | 0 |  | 2302.5 | 2538.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4144 | 0 | 0 | 39049.4139 | 0 | 0 |  | 2344.5 | 2580.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4149 | 0 | 0 | 39049.4144 | 0 | 0 |  | 2386.5 | 2622.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4154 | 0 | 0 | 39049.4149 | 0 | 0 |  | 2428.5 | 2664.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4159 | 0 | 0 | 39049.4154 | 0 | 0 |  | 2470.5 | 2706.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4164 | 0 | 0 | 39049.4159 | 0 | 0 |  | 2512.5 | 2748.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4168 | 0 | 0 | 39049.4164 | 0 | 0 |  | 2554.5 | 2790.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4173 | 0 | 0 | 39049.4169 | 0 | 0 |  | 2596.5 | 2832.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4178 | 0 | 0 | 39049.4173 | 0 | 0 |  | 2638.5 | 2874.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4183 | 0 | 0 | 39049.4178 | 0 | 0 |  | 2680.5 | 2916.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4188 | 0 | 0 | 39049.4183 | 0 | 0 |  | 2722.5 | 2958.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4193 | 0 | 0 | 39049.4188 | 0 | 0 |  | 2764.5 | 3000.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4198 | 0 | 0 | 39049.4193 | 0 | 0 |  | 2806.5 | 3042.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4202 | 0 | 0 | 39049.4198 | 0 | 0 |  | 2848.5 | 3084.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4207 | 0 | 0 | 39049.4203 | 0 | 0 |  | 2890 | 3126 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4212 | 0 | 0 | 39049.4207 | 0 | 0 |  | 2932 | 3168 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
39049.4217 | 0 | 0 | 39049.4212 | 0 | 0 |  | 2974.5 | 3210.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | #VALUE! | #VALUE! | #VALUE!
|  |  | 39049.4217 | 0 | 0 |  | 2996 | 3232 | #VALUE! | #VALUE! | 0.030525 | 0 | #VALUE! | #VALUE! | 0.00030525 | 0 | #VALUE! | 0.00030525 | #VALUE! | #VALUE! | #VALUE!

## B4-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 155.0904 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39049.3847 | 0 | 0 | 39049.3847 | 0 | 0 |  | -199 | 37 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3852 | 0 | 0 | 39049.3852 | 0 | 0 |  | -157 | 79 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3857 | 0 | 0 | 39049.3857 | 0 | 0 |  | -115 | 121 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3862 | 0 | 0 | 39049.3862 | 0 | 0 |  | -73 | 163 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3867 | 0 | 0 | 39049.3867 | 0 | 0 |  | -31 | 205 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3872 | 0 | 0 | 39049.3872 | 0 | 0 |  | 11 | 247 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3876 | 0 | 0 | 39049.3877 | 0 | 0 |  | 53 | 289 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3881 | 0 | 0 | 39049.3881 | 0 | 0 |  | 95 | 331 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3886 | 0 | 0 | 39049.3886 | 0 | 0 |  | 137 | 373 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3891 | 0 | 0 | 39049.3891 | 0 | 0 |  | 179 | 415 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3896 | 0 | 0 | 39049.3896 | 0 | 0 |  | 221 | 457 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3901 | 0 | 0 | 39049.3901 | 0 | 0 |  | 263 | 499 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3906 | 0 | 0 | 39049.3906 | 0 | 0 |  | 305 | 541 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.391 | 0 | 0 | 39049.3911 | 0 | 0 |  | 347 | 583 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3915 | 0 | 0 | 39049.3916 | 0 | 0 |  | 389 | 625 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.392 | 0 | 0 | 39049.392 | 0 | 0 |  | 431 | 667 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3925 | 0 | 0 | 39049.3925 | 0 | 0 |  | 473 | 709 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.393 | 0 | 0 | 39049.393 | 0 | 0 |  | 515 | 751 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3935 | 0 | 0 | 39049.3935 | 0 | 0 |  | 557 | 793 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.394 | 0 | 0 | 39049.394 | 0 | 0 |  | 599 | 835 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3944 | 0 | 0 | 39049.3945 | 0 | 0 |  | 641 | 877 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3949 | 0 | 0 | 39049.395 | 0 | 0 |  | 683 | 919 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3954 | 0 | 0 | 39049.3954 | 0 | 0 |  | 724.5 | 960.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3959 | 0 | 0 | 39049.3959 | 0 | 0 |  | 766.5 | 1002.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3964 | 0 | 0 | 39049.3964 | 0 | 0 |  | 809 | 1045 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3969 | 0 | 0 | 39049.3969 | 0 | 0 |  | 850.5 | 1086.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3974 | 0 | 0 | 39049.3974 | 0 | 0 |  | 893 | 1129 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3978 | 0 | 0 | 39049.3979 | 0 | 0 |  | 934.5 | 1170.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3983 | 0 | 0 | 39049.3983 | 0 | 0 |  | 976.5 | 1212.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3988 | 0 | 0 | 39049.3988 | 0 | 0 |  | 1018.5 | 1254.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3993 | 0 | 0 | 39049.3993 | 0 | 0 |  | 1060.5 | 1296.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.3998 | 0 | 0 | 39049.3998 | 0 | 0 |  | 1102.5 | 1338.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4003 | 0 | 0 | 39049.4003 | 0 | 0 |  | 1144.5 | 1380.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4008 | 0 | 0 | 39049.4008 | 0 | 0 |  | 1186.5 | 1422.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4013 | 0 | 0 | 39049.4013 | 0 | 0 |  | 1228.5 | 1464.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4017 | 0 | 0 | 39049.4017 | 0 | 0 |  | 1270.5 | 1506.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4022 | 0 | 0 | 39049.4022 | 0 | 0 |  | 1312.5 | 1548.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4027 | 0 | 0 | 39049.4027 | 0 | 0 |  | 1354.5 | 1590.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4032 | 0 | 1 | 39049.4032 | 0 | 0 |  | 1396.5 | 1632.5 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508176.0788 | 507976 | 253838.0295
39049.4037 | 0 | 0 | 39049.4037 | 0 | 0 |  | 1438.5 | 1674.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4042 | 0 | 0 | 39049.4042 | 0 | 0 |  | 1480.5 | 1716.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4047 | 0 | 0 | 39049.4047 | 0 | 0 |  | 1522.5 | 1758.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4051 | 0 | 0 | 39049.4052 | 0 | 0 |  | 1564.5 | 1800.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4056 | 0 | 0 | 39049.4056 | 0 | 0 |  | 1606.5 | 1842.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4061 | 0 | 0 | 39049.4061 | 0 | 0 |  | 1648.5 | 1884.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4066 | 0 | 0 | 39049.4066 | 0 | 0 |  | 1690.5 | 1926.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39049.4071 | 2122 | 1 | 39049.4071 | 0 | 0 |  | 1732.5 | 1968.5 | 129.5482 | 0.06105 | 0.030525 | 0 | 1.2955 | 0.0006105 | 0.00030525 | 0 | 1.2949 | 0.00030525 | 19.7256 | 507975.9995 | 41729.7851
39049.4076 | 2233 | 1 | 39049.4076 | 0 | 0 |  | 1774.5 | 2010.5 | 136.3248 | 0.06105 | 0.030525 | 0 | 1.3632 | 0.0006105 | 0.00030525 | 0 | 1.3626 | 0.00030525 | 13.7715 | 507976.0005 | 30631.9698
39049.4081 | 2144 | 1 | 39049.4081 | 0 | 0 |  | 1816.5 | 2052.5 | 130.8913 | 0.06105 | 0.030525 | 0 | 1.3089 | 0.0006105 | 0.00030525 | 0 | 1.3083 | 0.00030525 | 18.4965 | 507975.9995 | 39530.2181
39049.4085 | 2204 | 1 | 39049.4086 | 0 | 0 |  | 1858.5 | 2094.5 | 134.5543 | 0.06105 | 0.030525 | 0 | 1.3455 | 0.0006105 | 0.00030525 | 0 | 1.3449 | 0.00030525 | 15.2692 | 507976.0005 | 33531.399
39049.409 | 2072 | 1 | 39049.409 | 0 | 0 |  | 1900.5 | 2136.5 | 126.4957 | 0.06105 | 0.030525 | 0 | 1.265 | 0.0006105 | 0.00030525 | 0 | 1.2643 | 0.00030525 | 22.6161 | 507976.0005 | 46728.801
39049.4095 | 2471 | 1 | 39049.4095 | 0 | 0 |  | 1942.5 | 2178.5 | 150.8547 | 0.06105 | 0.030525 | 0 | 1.5085 | 0.0006105 | 0.00030525 | 0 | 1.5079 | 0.00030525 | 2.8089 | 507976.0005 | 6836.6541
39049.41 | 2524 | 1 | 39049.41 | 0 | 0 |  | 1984.5 | 2220.5 | 154.0904 | 0.06105 | 0.030525 | 0 | 1.5409 | 0.0006105 | 0.00030525 | 0 | 1.5403 | 0.00030525 | 0.64923 | 507975.9995 | 1537.6973
39049.4105 | 2020 | 1 | 39049.4105 | 1 | 0 |  | 2026.5 | 2262.5 | 123.3211 | 0.06105 | 0.06105 | 0 | 1.2332 | 0.0006105 | 0.0006105 | 0 | 1.2326 | 0.0006105 | 25.7742 | 253938 | 51917.555
39049.411 | 2244 | 1 | 39049.411 | 0 | 0 |  | 2068.5 | 2304.5 | 136.9963 | 0.06105 | 0.030525 | 0 | 1.37 | 0.0006105 | 0.00030525 | 0 | 1.3694 | 0.00030525 | 13.2136 | 507976.0005 | 29532.1863
39049.4115 | 1959 | 1 | 39049.4115 | 0 | 0 |  | 2110.5 | 2346.5 | 119.5971 | 0.06105 | 0.030525 | 0 | 1.196 | 0.0006105 | 0.00030525 | 0 | 1.1954 | 0.00030525 | 29.6925 | 507976.0005 | 58026.5769
39049.4119 | 1966 | 1 | 39049.412 | 0 | 0 |  | 2152.5 | 2388.5 | 120.0244 | 0.06105 | 0.030525 | 0 | 1.2002 | 0.0006105 | 0.00030525 | 0 | 1.1996 | 0.00030525 | 29.2305 | 507976.0005 | 57326.7147
39049.4124 | 1966 | 1 | 39049.4124 | 0 | 0 |  | 2194.5 | 2430.5 | 120.0244 | 0.06105 | 0.030525 | 0 | 1.2002 | 0.0006105 | 0.00030525 | 0 | 1.1996 | 0.00030525 | 29.2305 | 507976.0005 | 57326.7147
39049.4129 | 2033 | 1 | 39049.4129 | 0 | 0 |  | 2236.5 | 2472.5 | 124.1148 | 0.06105 | 0.030525 | 0 | 1.2411 | 0.0006105 | 0.00030525 | 0 | 1.2405 | 0.00030525 | 24.9695 | 507975.9995 | 50628.0334
39049.4134 | 2106 | 1 | 39049.4134 | 0 | 0 |  | 2278.5 | 2514.5 | 128.5714 | 0.06105 | 0.030525 | 0 | 1.2857 | 0.0006105 | 0.00030525 | 0 | 1.2851 | 0.00030525 | 20.6356 | 507975.9995 | 43329.4702
39049.4139 | 2224 | 1 | 39049.4139 | 0 | 0 |  | 2320.5 | 2556.5 | 135.7753 | 0.06105 | 0.030525 | 0 | 1.3578 | 0.0006105 | 0.00030525 | 0 | 1.3571 | 0.00030525 | 14.2321 | 507976.0005 | 31531.7927
39049.4144 | 2424 | 1 | 39049.4144 | 0 | 0 |  | 2362.5 | 2598.5 | 147.9853 | 0.06105 | 0.030525 | 0 | 1.4799 | 0.0006105 | 0.00030525 | 0 | 1.4792 | 0.00030525 | 4.8031 | 507976.0014 | 11535.7291
39049.4149 | 2142 | 1 | 39049.4149 | 0 | 0 |  | 2404.5 | 2640.5 | 130.7692 | 0.06105 | 0.030525 | 0 | 1.3077 | 0.0006105 | 0.00030525 | 0 | 1.3071 | 0.00030525 | 18.6072 | 507976.0005 | 39730.1787
39049.4153 | 2034 | 1 | 39049.4154 | 0 | 0 |  | 2446.5 | 2682.5 | 124.1758 | 0.06105 | 0.030525 | 0 | 1.2418 | 0.0006105 | 0.00030525 | 0 | 1.2411 | 0.00030525 | 24.908 | 507976.0005 | 50528.0531
39049.4158 | 2153 | 1 | 39049.4158 | 0 | 0 |  | 2488.5 | 2724.5 | 131.4408 | 0.06105 | 0.030525 | 0 | 1.3144 | 0.0006105 | 0.00030525 | 0 | 1.3138 | 0.00030525 | 18.0009 | 507976.0005 | 38630.3952
39049.4163 | 2199 | 1 | 39049.4163 | 0 | 0 |  | 2530.5 | 2766.5 | 134.2491 | 0.06105 | 0.030525 | 0 | 1.3425 | 0.0006105 | 0.00030525 | 0 | 1.3419 | 0.00030525 | 15.5314 | 507976.0005 | 34031.3006
39049.4168 | 1901 | 1 | 39049.4168 | 0 | 0 |  | 2572.5 | 2808.5 | 116.0562 | 0.06105 | 0.030525 | 0 | 1.1606 | 0.0006105 | 0.00030525 | 0 | 1.16 | 0.00030525 | 33.6516 | 507975.9995 | 63825.4353
39049.4173 | 2103 | 1 | 39049.4173 | 0 | 0 |  | 2614.5 | 2850.5 | 128.3883 | 0.06105 | 0.030525 | 0 | 1.2839 | 0.0006105 | 0.00030525 | 0 | 1.2833 | 0.00030525 | 20.8078 | 507976.0014 | 43629.4111
39049.4178 | 2118 | 1 | 39049.4178 | 0 | 0 |  | 2656.5 | 2892.5 | 129.304 | 0.06105 | 0.030525 | 0 | 1.293 | 0.0006105 | 0.00030525 | 0 | 1.2924 | 0.00030525 | 19.9518 | 507976.0014 | 42129.7064
39049.4183 | 2329 | 1 | 39049.4183 | 0 | 0 |  | 2698.5 | 2934.5 | 142.1856 | 0.06105 | 0.030525 | 0 | 1.4219 | 0.0006105 | 0.00030525 | 0 | 1.4212 | 0.00030525 | 9.0799 | 507975.9995 | 21033.8593
39049.4187 | 2189 | 1 | 39049.4188 | 0 | 0 |  | 2740.5 | 2976.5 | 133.6386 | 0.06105 | 0.030525 | 0 | 1.3364 | 0.0006105 | 0.00030525 | 0 | 1.3358 | 0.00030525 | 16.0594 | 507976.0005 | 35031.1038
39049.4192 | 2444 | 1 | 39049.4192 | 0 | 0 |  | 2782.5 | 3018.5 | 149.2063 | 0.06105 | 0.030525 | 0 | 1.4921 | 0.0006105 | 0.00030525 | 0 | 1.4915 | 0.00030525 | 3.9451 | 507976.0005 | 9536.1227
39049.4197 | 1997 | 1 | 39049.4197 | 0 | 0 |  | 2824.5 | 3060.5 | 121.917 | 0.06105 | 0.030525 | 0 | 1.2192 | 0.0006105 | 0.00030525 | 0 | 1.2186 | 0.00030525 | 27.2234 | 507976.0005 | 54227.3248
39049.4202 | 2092 | 1 | 39049.4202 | 0 | 0 |  | 2866.5 | 3102.5 | 127.7167 | 0.06105 | 0.030525 | 0 | 1.2772 | 0.0006105 | 0.00030525 | 0 | 1.2766 | 0.00030525 | 21.4433 | 507975.9995 | 44729.1946
39049.4207 | 2157 | 1 | 39049.4207 | 0 | 0 |  | 2908.5 | 3144.5 | 131.685 | 0.06105 | 0.030525 | 0 | 1.3168 | 0.0006105 | 0.00030525 | 0 | 1.3162 | 0.00030525 | 17.782 | 507975.9995 | 38230.474
39049.4212 | 2361 | 1 | 39049.4212 | 0 | 0 |  | 2950.5 | 3186.5 | 144.1392 | 0.06105 | 0.030525 | 0 | 1.4414 | 0.0006105 | 0.00030525 | 0 | 1.4408 | 0.00030525 | 7.6008 | 507975.9995 | 17834.4891
39049.4217 | 2117 | 1 | 39049.4217 | 0 | 0 |  | 2992.5 | 3228.5 | 129.243 | 0.06105 | 0.030525 | 0 | 1.2924 | 0.0006105 | 0.00030525 | 0 | 1.2918 | 0.00030525 | 20.0085 | 507976.0005 | 42229.6867

## B4-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 155.7619 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39049.3847 | 0 | 0 | 39049.3847 | 0 | 0 |  | -202 | 34 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3852 | 0 | 0 | 39049.3852 | 0 | 0 |  | -160 | 76 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3857 | 0 | 0 | 39049.3857 | 0 | 0 |  | -118 | 118 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3861 | 0 | 0 | 39049.3862 | 0 | 0 |  | -76 | 160 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3866 | 0 | 0 | 39049.3867 | 0 | 0 |  | -34 | 202 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3871 | 0 | 0 | 39049.3871 | 0 | 0 |  | 8 | 244 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3876 | 0 | 0 | 39049.3876 | 0 | 0 |  | 50 | 286 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3881 | 0 | 0 | 39049.3881 | 0 | 0 |  | 92 | 328 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3886 | 0 | 0 | 39049.3886 | 0 | 0 |  | 134 | 370 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3891 | 0 | 0 | 39049.3891 | 0 | 0 |  | 176 | 412 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3895 | 0 | 0 | 39049.3896 | 0 | 0 |  | 218 | 454 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.39 | 0 | 0 | 39049.3901 | 0 | 0 |  | 260 | 496 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3905 | 0 | 0 | 39049.3905 | 0 | 0 |  | 302 | 538 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.391 | 0 | 0 | 39049.391 | 0 | 0 |  | 344 | 580 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3915 | 0 | 0 | 39049.3915 | 0 | 0 |  | 386 | 622 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.392 | 0 | 0 | 39049.392 | 0 | 0 |  | 428 | 664 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3925 | 0 | 0 | 39049.3925 | 0 | 0 |  | 470 | 706 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.393 | 0 | 0 | 39049.393 | 0 | 0 |  | 512 | 748 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3934 | 0 | 0 | 39049.3935 | 0 | 0 |  | 554 | 790 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3939 | 0 | 0 | 39049.3939 | 0 | 0 |  | 596 | 832 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3944 | 0 | 0 | 39049.3944 | 0 | 0 |  | 638 | 874 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3949 | 0 | 0 | 39049.3949 | 0 | 0 |  | 680 | 916 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3954 | 0 | 0 | 39049.3954 | 0 | 0 |  | 722 | 958 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3959 | 0 | 0 | 39049.3959 | 0 | 0 |  | 764 | 1000 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3964 | 0 | 0 | 39049.3964 | 0 | 0 |  | 806 | 1042 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3968 | 0 | 0 | 39049.3969 | 0 | 0 |  | 848 | 1084 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3973 | 0 | 0 | 39049.3973 | 0 | 0 |  | 890 | 1126 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3978 | 0 | 0 | 39049.3978 | 0 | 0 |  | 932 | 1168 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3983 | 0 | 0 | 39049.3983 | 0 | 0 |  | 974 | 1210 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3988 | 0 | 0 | 39049.3988 | 0 | 0 |  | 1016 | 1252 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3993 | 0 | 0 | 39049.3993 | 0 | 0 |  | 1058 | 1294 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.3998 | 0 | 0 | 39049.3998 | 0 | 0 |  | 1100 | 1336 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4002 | 0 | 0 | 39049.4003 | 0 | 0 |  | 1142 | 1378 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4007 | 0 | 0 | 39049.4008 | 0 | 0 |  | 1184 | 1420 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4012 | 0 | 0 | 39049.4012 | 0 | 0 |  | 1226 | 1462 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4017 | 0 | 0 | 39049.4017 | 0 | 0 |  | 1268 | 1504 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4022 | 0 | 0 | 39049.4022 | 0 | 0 |  | 1310 | 1546 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4027 | 0 | 0 | 39049.4027 | 0 | 0 |  | 1352 | 1588 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4032 | 0 | 0 | 39049.4032 | 0 | 0 |  | 1394 | 1630 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4036 | 0 | 0 | 39049.4037 | 0 | 0 |  | 1436 | 1672 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4041 | 0 | 0 | 39049.4042 | 0 | 0 |  | 1478 | 1714 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4046 | 0 | 0 | 39049.4046 | 0 | 0 |  | 1520 | 1756 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4051 | 0 | 0 | 39049.4051 | 0 | 0 |  | 1562 | 1798 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4056 | 0 | 0 | 39049.4056 | 0 | 0 |  | 1604 | 1840 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4061 | 0 | 0 | 39049.4061 | 0 | 0 |  | 1646 | 1882 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.4066 | 0 | 0 | 39049.4066 | 0 | 0 |  | 1688 | 1924 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39049.407 | 2339 | 1 | 39049.4071 | 0 | 0 |  | 1729.5 | 1965.5 | 142.7961 | 0.06105 | 0.030525 | 0 | 1.428 | 0.0006105 | 0.00030525 | 0 | 1.4274 | 0.00030525 | 9.0838 | 510175.9994 | 21133.8575
39049.4075 | 1955 | 1 | 39049.4076 | 0 | 0 |  | 1772 | 2008 | 119.3529 | 0.06105 | 0.030525 | 0 | 1.1935 | 0.0006105 | 0.00030525 | 0 | 1.1929 | 0.00030525 | 30.521 | 510176.0003 | 59526.3322
| 2245 | 1 | 39049.408 | 0 | 0 |  | 1815 | 2051 | 137.0574 | 0.06105 | 0.030525 | 0 | 1.3706 | 0.0006105 | 0.00030525 | 0 | 1.37 | 0.00030525 | 13.6533 | 510176.0003 | 30532.0154
39049.4085 | 2535 | 1 | 39049.4085 | 0 | 0 |  | 1856 | 2092 | 154.7619 | 0.06105 | 0.030525 | 0 | 1.5476 | 0.0006105 | 0.00030525 | 0 | 1.547 | 0.00030525 | 0.64641 | 510175.9994 | 1537.6986
39049.409 | 2347 | 1 | 39049.409 | 0 | 0 |  | 1897.5 | 2133.5 | 143.2845 | 0.06105 | 0.030525 | 0 | 1.4328 | 0.0006105 | 0.00030525 | 0 | 1.4322 | 0.00030525 | 8.7119 | 510176.0013 | 20334.0143
39049.4095 | 2439 | 1 | 39049.4095 | 0 | 0 |  | 1940 | 2176 | 148.9011 | 0.06105 | 0.030525 | 0 | 1.489 | 0.0006105 | 0.00030525 | 0 | 1.4884 | 0.00030525 | 4.6095 | 510176.0003 | 11135.8173
39049.41 | 2377 | 1 | 39049.41 | 0 | 0 |  | 1982 | 2218 | 145.116 | 0.06105 | 0.030525 | 0 | 1.4512 | 0.0006105 | 0.00030525 | 0 | 1.4505 | 0.00030525 | 7.3392 | 510176.0003 | 17334.6022
39049.4105 | 2019 | 1 | 39049.4105 | 0 | 0 |  | 2024 | 2260 | 123.2601 | 0.06105 | 0.030525 | 0 | 1.2326 | 0.0006105 | 0.00030525 | 0 | 1.232 | 0.00030525 | 26.3816 | 510176.0003 | 53127.5864
39049.4109 | 1984 | 1 | 39049.4109 | 0 | 0 |  | 2065.5 | 2301.5 | 121.1233 | 0.06105 | 0.030525 | 0 | 1.2112 | 0.0006105 | 0.00030525 | 0 | 1.2106 | 0.00030525 | 28.6122 | 510175.9994 | 56626.9005
39049.4114 | 2500 | 1 | 39049.4114 | 0 | 0 |  | 2107.5 | 2343.5 | 152.6252 | 0.06105 | 0.030525 | 0 | 1.5263 | 0.0006105 | 0.00030525 | 0 | 1.5256 | 0.00030525 | 2.056 | 510176.0003 | 5037.0127
39049.4119 | 2172 | 1 | 39049.4119 | 0 | 0 |  | 2149.5 | 2385.5 | 132.6007 | 0.06105 | 0.030525 | 0 | 1.326 | 0.0006105 | 0.00030525 | 0 | 1.3254 | 0.00030525 | 17.4749 | 510176.0003 | 37830.5848
39049.4124 | 2326 | 1 | 39049.4124 | 0 | 0 |  | 2191.5 | 2427.5 | 142.0024 | 0.06105 | 0.030525 | 0 | 1.42 | 0.0006105 | 0.00030525 | 0 | 1.4194 | 0.00030525 | 9.6938 | 510176.0003 | 22433.6028
39049.4129 | 2008 | 1 | 39049.4129 | 0 | 0 |  | 2233.5 | 2469.5 | 122.5885 | 0.06105 | 0.030525 | 0 | 1.2259 | 0.0006105 | 0.00030525 | 0 | 1.2253 | 0.00030525 | 27.0742 | 510176.0003 | 54227.3709
39049.4134 | 1975 | 1 | 39049.4134 | 0 | 0 |  | 2275.5 | 2511.5 | 120.5739 | 0.06105 | 0.030525 | 0 | 1.2057 | 0.0006105 | 0.00030525 | 0 | 1.2051 | 0.00030525 | 29.1986 | 510176.0003 | 57526.7241
39049.4139 | 2441 | 1 | 39049.4139 | 0 | 0 |  | 2317.5 | 2553.5 | 149.0232 | 0.06105 | 0.030525 | 0 | 1.4902 | 0.0006105 | 0.00030525 | 0 | 1.4896 | 0.00030525 | 4.5238 | 510176.0003 | 10935.8565
39049.4143 | 1937 | 1 | 39049.4144 | 0 | 0 |  | 2359.5 | 2595.5 | 118.254 | 0.06105 | 0.030525 | 0 | 1.1825 | 0.0006105 | 0.00030525 | 0 | 1.1819 | 0.00030525 | 31.7345 | 510176.0003 | 61325.9794
39049.4148 | 1922 | 1 | 39049.4148 | 0 | 0 |  | 2401.5 | 2637.5 | 117.3382 | 0.06105 | 0.030525 | 0 | 1.1734 | 0.0006105 | 0.00030525 | 0 | 1.1728 | 0.00030525 | 32.7631 | 510176.0003 | 62825.6855
39049.4153 | 2398 | 1 | 39049.4153 | 0 | 0 |  | 2443.5 | 2679.5 | 146.398 | 0.06105 | 0.030525 | 0 | 1.464 | 0.0006105 | 0.00030525 | 0 | 1.4634 | 0.00030525 | 6.3988 | 510175.9994 | 15235.0138
39049.4158 | 2000 | 1 | 39049.4158 | 0 | 0 |  | 2485.5 | 2721.5 | 122.1001 | 0.06105 | 0.030525 | 0 | 1.221 | 0.0006105 | 0.00030525 | 0 | 1.2204 | 0.00030525 | 27.5828 | 510175.9994 | 55027.2141
39049.4163 | 2413 | 1 | 39049.4163 | 0 | 0 |  | 2527.5 | 2763.5 | 147.3138 | 0.06105 | 0.030525 | 0 | 1.4731 | 0.0006105 | 0.00030525 | 0 | 1.4725 | 0.00030525 | 5.7371 | 510176.0013 | 13735.3077
39049.4168 | 2395 | 1 | 39049.4168 | 0 | 0 |  | 2569.5 | 2805.5 | 146.2149 | 0.06105 | 0.030525 | 0 | 1.4621 | 0.0006105 | 0.00030525 | 0 | 1.4615 | 0.00030525 | 6.5322 | 510176.0003 | 15534.955
39049.4173 | 2000 | 1 | 39049.4173 | 0 | 0 |  | 2611.5 | 2847.5 | 122.1001 | 0.06105 | 0.030525 | 0 | 1.221 | 0.0006105 | 0.00030525 | 0 | 1.2204 | 0.00030525 | 27.5828 | 510175.9994 | 55027.2141
39049.4177 | 2217 | 1 | 39049.4178 | 0 | 0 |  | 2653.5 | 2889.5 | 135.348 | 0.06105 | 0.030525 | 0 | 1.3535 | 0.0006105 | 0.00030525 | 0 | 1.3529 | 0.00030525 | 15.0894 | 510176.0003 | 33331.4667
39049.4182 | 2172 | 1 | 39049.4182 | 0 | 0 |  | 2695.5 | 2931.5 | 132.6007 | 0.06105 | 0.030525 | 0 | 1.326 | 0.0006105 | 0.00030525 | 0 | 1.3254 | 0.00030525 | 17.4749 | 510176.0003 | 37830.5848
39049.4187 | 2147 | 1 | 39049.4187 | 0 | 0 |  | 2737.5 | 2973.5 | 131.0745 | 0.06105 | 0.030525 | 0 | 1.3107 | 0.0006105 | 0.00030525 | 0 | 1.3101 | 0.00030525 | 18.8434 | 510175.9994 | 40330.0949
39049.4192 | 2455 | 1 | 39049.4192 | 0 | 0 |  | 2779.5 | 3015.5 | 149.8779 | 0.06105 | 0.030525 | 0 | 1.4988 | 0.0006105 | 0.00030525 | 0 | 1.4982 | 0.00030525 | 3.9275 | 510176.0003 | 9536.1308
39049.4197 | 2428 | 1 | 39049.4197 | 0 | 0 |  | 2821.5 | 3057.5 | 148.2295 | 0.06105 | 0.030525 | 0 | 1.4823 | 0.0006105 | 0.00030525 | 0 | 1.4817 | 0.00030525 | 5.0836 | 510176.0003 | 12235.6017
39049.4202 | 1942 | 1 | 39049.4202 | 0 | 0 |  | 2863.5 | 3099.5 | 118.5592 | 0.06105 | 0.030525 | 0 | 1.1856 | 0.0006105 | 0.00030525 | 0 | 1.185 | 0.00030525 | 31.3952 | 510176.0003 | 60826.0774
39049.4207 | 1947 | 1 | 39049.4207 | 0 | 0 |  | 2905.5 | 3141.5 | 118.8645 | 0.06105 | 0.030525 | 0 | 1.1886 | 0.0006105 | 0.00030525 | 0 | 1.188 | 0.00030525 | 31.0576 | 510176.0003 | 60326.1754
39049.4211 | 2020 | 1 | 39049.4212 | 0 | 0 |  | 2947.5 | 3183.5 | 123.3211 | 0.06105 | 0.030525 | 0 | 1.2332 | 0.0006105 | 0.00030525 | 0 | 1.2326 | 0.00030525 | 26.319 | 510176.0003 | 53027.606
39049.4216 | 1938 | 1 | 39049.4216 | 0 | 0 |  | 2989.5 | 3225.5 | 118.315 | 0.06105 | 0.030525 | 0 | 1.1832 | 0.0006105 | 0.00030525 | 0 | 1.1825 | 0.00030525 | 31.6665 | 510176.0003 | 61225.999

## B3-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.1282 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39049.3847 | 0 | 0 | 39049.3847 | 0 | 0 |  | -204.5 | 31.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3852 | 0 | 0 | 39049.3852 | 0 | 0 |  | -162.5 | 73.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3856 | 0 | 0 | 39049.3856 | 0 | 0 |  | -120.5 | 115.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3861 | 0 | 0 | 39049.3861 | 0 | 0 |  | -78.5 | 157.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3866 | 0 | 0 | 39049.3866 | 0 | 0 |  | -36.5 | 199.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3871 | 0 | 0 | 39049.3871 | 0 | 0 |  | 5.5 | 241.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3876 | 0 | 0 | 39049.3876 | 0 | 0 |  | 47.5 | 283.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3881 | 0 | 0 | 39049.3881 | 0 | 0 |  | 89.5 | 325.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3886 | 0 | 0 | 39049.3886 | 0 | 0 |  | 131.5 | 367.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.389 | 0 | 0 | 39049.3891 | 0 | 0 |  | 173.5 | 409.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3895 | 0 | 0 | 39049.3895 | 0 | 0 |  | 215.5 | 451.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.39 | 0 | 0 | 39049.39 | 0 | 0 |  | 257.5 | 493.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3905 | 0 | 0 | 39049.3905 | 0 | 0 |  | 299.5 | 535.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.391 | 0 | 0 | 39049.391 | 0 | 0 |  | 341.5 | 577.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3915 | 0 | 0 | 39049.3915 | 0 | 0 |  | 383.5 | 619.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.392 | 0 | 0 | 39049.392 | 0 | 0 |  | 425.5 | 661.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3924 | 0 | 0 | 39049.3925 | 0 | 0 |  | 467.5 | 703.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3929 | 0 | 0 | 39049.3929 | 0 | 0 |  | 509.5 | 745.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3934 | 0 | 0 | 39049.3934 | 0 | 0 |  | 551.5 | 787.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3939 | 0 | 0 | 39049.3939 | 0 | 0 |  | 593.5 | 829.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3944 | 0 | 0 | 39049.3944 | 0 | 0 |  | 635.5 | 871.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3949 | 0 | 0 | 39049.3949 | 0 | 0 |  | 677.5 | 913.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3953 | 0 | 0 | 39049.3954 | 0 | 0 |  | 719 | 955 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3958 | 0 | 0 | 39049.3959 | 0 | 0 |  | 761 | 997 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3963 | 0 | 0 | 39049.3963 | 0 | 0 |  | 803 | 1039 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3968 | 0 | 0 | 39049.3968 | 0 | 0 |  | 845 | 1081 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3973 | 0 | 0 | 39049.3973 | 0 | 0 |  | 887.5 | 1123.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3978 | 0 | 0 | 39049.3978 | 0 | 0 |  | 929 | 1165 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3983 | 0 | 0 | 39049.3983 | 0 | 0 |  | 971 | 1207 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3988 | 0 | 0 | 39049.3988 | 0 | 0 |  | 1013 | 1249 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3992 | 0 | 0 | 39049.3993 | 0 | 0 |  | 1055.5 | 1291.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3997 | 0 | 0 | 39049.3997 | 0 | 0 |  | 1097 | 1333 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4002 | 0 | 0 | 39049.4002 | 0 | 0 |  | 1139 | 1375 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4007 | 0 | 0 | 39049.4007 | 0 | 0 |  | 1181 | 1417 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4012 | 0 | 0 | 39049.4012 | 0 | 0 |  | 1223 | 1459 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4017 | 0 | 0 | 39049.4017 | 0 | 0 |  | 1265 | 1501 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4022 | 0 | 0 | 39049.4022 | 0 | 0 |  | 1307 | 1543 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4026 | 0 | 0 | 39049.4027 | 0 | 0 |  | 1349 | 1585 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4031 | 0 | 0 | 39049.4031 | 0 | 0 |  | 1391 | 1627 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4036 | 0 | 0 | 39049.4036 | 0 | 0 |  | 1433 | 1669 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4041 | 0 | 0 | 39049.4041 | 0 | 0 |  | 1475 | 1711 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4046 | 0 | 0 | 39049.4046 | 0 | 0 |  | 1517 | 1753 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4051 | 0 | 0 | 39049.4051 | 0 | 0 |  | 1559 | 1795 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4056 | 0 | 0 | 39049.4056 | 0 | 0 |  | 1601 | 1837 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.406 | 0 | 0 | 39049.4061 | 0 | 0 |  | 1643 | 1879 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4065 | 0 | 0 | 39049.4066 | 0 | 0 |  | 1685 | 1921 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.407 | 2426 | 1 | 39049.407 | 0 | 0 |  | 1727 | 1963 | 148.1074 | 0.06105 | 0.030525 | 0 | 1.4811 | 0.0006105 | 0.00030525 | 0 | 1.4805 | 0.00030525 | 5.4177 | 511375.9998 | 13035.4509
39049.4075 | 2358 | 1 | 39049.4075 | 1 | 0 |  | 1769 | 2005 | 143.956 | 0.06105 | 0.06105 | 0 | 1.4396 | 0.0006105 | 0.0006105 | 0 | 1.4389 | 0.0006105 | 8.4591 | 255638.0001 | 19830.2428
39049.408 | 2218 | 1 | 39049.408 | 0 | 0 |  | 1811 | 2047 | 135.409 | 0.06105 | 0.030525 | 0 | 1.3541 | 0.0006105 | 0.00030525 | 0 | 1.3535 | 0.00030525 | 15.3081 | 511375.9998 | 33831.3842
39049.4085 | 1954 | 1 | 39049.4085 | 0 | 0 |  | 1853 | 2089 | 119.2918 | 0.06105 | 0.030525 | 0 | 1.1929 | 0.0006105 | 0.00030525 | 0 | 1.1923 | 0.00030525 | 30.895 | 511375.9998 | 60226.2227
39049.409 | 2454 | 1 | 39049.409 | 1 | 0 |  | 1895 | 2131 | 149.8168 | 0.06105 | 0.06105 | 0 | 1.4982 | 0.0006105 | 0.0006105 | 0 | 1.4976 | 0.0006105 | 4.2144 | 255638.0001 | 10233.9967
39049.4094 | 2075 | 1 | 39049.4095 | 0 | 0 |  | 1937 | 2173 | 126.6789 | 0.06105 | 0.030525 | 0 | 1.2668 | 0.0006105 | 0.00030525 | 0 | 1.2662 | 0.00030525 | 23.2584 | 511375.9998 | 48128.5884
39049.4099 | 2007 | 1 | 39049.41 | 0 | 0 |  | 1979 | 2215 | 122.5275 | 0.06105 | 0.030525 | 0 | 1.2253 | 0.0006105 | 0.00030525 | 0 | 1.2247 | 0.00030525 | 27.4367 | 511376.0008 | 54927.2589
39049.4104 | 2086 | 1 | 39049.4104 | 1 | 0 |  | 2021 | 2257 | 127.3504 | 0.06105 | 0.06105 | 0 | 1.2735 | 0.0006105 | 0.0006105 | 0 | 1.2729 | 0.0006105 | 22.6082 | 255638.0001 | 47019.607
39049.4109 | 2490 | 1 | 39049.4109 | 0 | 0 |  | 2063 | 2299 | 152.0147 | 0.06105 | 0.030525 | 0 | 1.5201 | 0.0006105 | 0.00030525 | 0 | 1.5195 | 0.00030525 | 2.7071 | 511376.0008 | 6636.7022
39049.4114 | 2495 | 1 | 39049.4114 | 1 | 0 |  | 2105 | 2341 | 152.3199 | 0.06105 | 0.06105 | 0 | 1.5232 | 0.0006105 | 0.0006105 | 0 | 1.5226 | 0.0006105 | 2.5012 | 255638.0001 | 6135.5999
39049.4119 | 2541 | 1 | 39049.4119 | 0 | 0 |  | 2147 | 2383 | 155.1282 | 0.06105 | 0.030525 | 0 | 1.5513 | 0.0006105 | 0.00030525 | 0 | 1.5507 | 0.00030525 | 0.64488 | 511375.9998 | 1537.6993
39049.4124 | 2186 | 1 | 39049.4124 | 0 | 0 |  | 2189 | 2425 | 133.4554 | 0.06105 | 0.030525 | 0 | 1.3346 | 0.0006105 | 0.00030525 | 0 | 1.3339 | 0.00030525 | 16.9968 | 511376.0008 | 37030.7586
39049.4128 | 2092 | 1 | 39049.4129 | 0 | 0 |  | 2231 | 2467 | 127.7167 | 0.06105 | 0.030525 | 0 | 1.2772 | 0.0006105 | 0.00030525 | 0 | 1.2766 | 0.00030525 | 22.2563 | 511376.0008 | 46428.9208
39049.4133 | 2400 | 1 | 39049.4134 | 0 | 0 |  | 2273 | 2509 | 146.5201 | 0.06105 | 0.030525 | 0 | 1.4652 | 0.0006105 | 0.00030525 | 0 | 1.4646 | 0.00030525 | 6.5602 | 511375.9998 | 15634.9426
39049.4138 | 2002 | 1 | 39049.4138 | 0 | 0 |  | 2315 | 2551 | 122.2222 | 0.06105 | 0.030525 | 0 | 1.2222 | 0.0006105 | 0.00030525 | 0 | 1.2216 | 0.00030525 | 27.7551 | 511375.9998 | 55427.1612
39049.4143 | 2479 | 1 | 39049.4143 | 1 | 0 |  | 2357 | 2593 | 151.3431 | 0.06105 | 0.06105 | 0 | 1.5134 | 0.0006105 | 0.0006105 | 0 | 1.5128 | 0.0006105 | 3.163 | 255638.0001 | 7734.9742
39049.4148 | 2019 | 1 | 39049.4148 | 0 | 0 |  | 2399 | 2635 | 123.2601 | 0.06105 | 0.030525 | 0 | 1.2326 | 0.0006105 | 0.00030525 | 0 | 1.232 | 0.00030525 | 26.6789 | 511375.9998 | 53727.4935
39049.4153 | 1919 | 1 | 39049.4153 | 0 | 0 |  | 2441 | 2677 | 117.1551 | 0.06105 | 0.030525 | 0 | 1.1716 | 0.0006105 | 0.00030525 | 0 | 1.1709 | 0.00030525 | 33.2836 | 511376.0008 | 63725.5384
39049.4158 | 1897 | 1 | 39049.4158 | 0 | 0 |  | 2483 | 2719 | 115.812 | 0.06105 | 0.030525 | 0 | 1.1581 | 0.0006105 | 0.00030525 | 0 | 1.1575 | 0.00030525 | 34.8302 | 511375.9998 | 65925.1083
39049.4163 | 1876 | 1 | 39049.4163 | 0 | 0 |  | 2525 | 2761 | 114.5299 | 0.06105 | 0.030525 | 0 | 1.1453 | 0.0006105 | 0.00030525 | 0 | 1.1447 | 0.00030525 | 36.3403 | 511376.0008 | 68024.6977
39049.4167 | 2502 | 1 | 39049.4168 | 0 | 0 |  | 2567 | 2803 | 152.7473 | 0.06105 | 0.030525 | 0 | 1.5275 | 0.0006105 | 0.00030525 | 0 | 1.5269 | 0.00030525 | 2.2143 | 511375.9998 | 5436.9368
39049.4172 | 2254 | 1 | 39049.4172 | 0 | 0 |  | 2609 | 2845 | 137.6068 | 0.06105 | 0.030525 | 0 | 1.3761 | 0.0006105 | 0.00030525 | 0 | 1.3755 | 0.00030525 | 13.4656 | 511375.9998 | 30232.0881
39049.4177 | 1983 | 1 | 39049.4177 | 0 | 0 |  | 2651 | 2887 | 121.0623 | 0.06105 | 0.030525 | 0 | 1.2106 | 0.0006105 | 0.00030525 | 0 | 1.21 | 0.00030525 | 28.9798 | 511376.0008 | 57326.7897
39049.4182 | 2532 | 1 | 39049.4182 | 0 | 0 |  | 2693 | 2929 | 154.5788 | 0.06105 | 0.030525 | 0 | 1.5458 | 0.0006105 | 0.00030525 | 0 | 1.5452 | 0.00030525 | 1.0028 | 511375.9998 | 2437.5233
39049.4187 | 1996 | 1 | 39049.4187 | 1 | 0 |  | 2735 | 2971 | 121.8559 | 0.06105 | 0.06105 | 0 | 1.2186 | 0.0006105 | 0.0006105 | 0 | 1.2179 | 0.0006105 | 28.1394 | 255638.0001 | 56016.0877
39049.4192 | 2168 | 1 | 39049.4192 | 0 | 0 |  | 2777 | 3013 | 132.3565 | 0.06105 | 0.030525 | 0 | 1.3236 | 0.0006105 | 0.00030525 | 0 | 1.323 | 0.00030525 | 17.9686 | 511375.9998 | 38830.4067
39049.4197 | 1971 | 1 | 39049.4197 | 0 | 0 |  | 2819 | 3055 | 120.3297 | 0.06105 | 0.030525 | 0 | 1.2033 | 0.0006105 | 0.00030525 | 0 | 1.2027 | 0.00030525 | 29.7655 | 511375.9989 | 58526.5551
39049.4201 | 2310 | 1 | 39049.4202 | 0 | 0 |  | 2861 | 3097 | 141.0256 | 0.06105 | 0.030525 | 0 | 1.4103 | 0.0006105 | 0.00030525 | 0 | 1.4096 | 0.00030525 | 10.7137 | 511376.0008 | 24633.183
39049.4206 | 2439 | 1 | 39049.4206 | 0 | 0 |  | 2902.5 | 3138.5 | 148.9011 | 0.06105 | 0.030525 | 0 | 1.489 | 0.0006105 | 0.00030525 | 0 | 1.4884 | 0.00030525 | 4.8556 | 511376.0008 | 11735.7051
39049.4211 | 2539 | 1 | 39049.4211 | 0 | 0 |  | 2945 | 3181 | 155.0061 | 0.06105 | 0.030525 | 0 | 1.5501 | 0.0006105 | 0.00030525 | 0 | 1.5495 | 0.00030525 | 0.72419 | 511376.0008 | 1737.6602
39049.4216 | 1962 | 1 | 39049.4216 | 0 | 0 |  | 2987 | 3223 | 119.7802 | 0.06105 | 0.030525 | 0 | 1.1978 | 0.0006105 | 0.00030525 | 0 | 1.1972 | 0.00030525 | 30.361 | 511376.0008 | 59426.3791

## B3-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 157.4103 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39049.3846 | 0 | 0 | 39049.3846 | 0 | 0 |  | -207.5 | 28.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3851 | 0 | 0 | 39049.3851 | 0 | 0 |  | -165.5 | 70.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3856 | 0 | 0 | 39049.3856 | 0 | 0 |  | -123.5 | 112.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3861 | 0 | 0 | 39049.3861 | 0 | 0 |  | -81.5 | 154.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3866 | 0 | 0 | 39049.3866 | 0 | 0 |  | -39.5 | 196.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3871 | 0 | 0 | 39049.3871 | 0 | 0 |  | 2.5 | 238.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3875 | 0 | 0 | 39049.3876 | 0 | 0 |  | 44.5 | 280.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.388 | 0 | 0 | 39049.388 | 0 | 0 |  | 86.5 | 322.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3885 | 0 | 0 | 39049.3885 | 0 | 0 |  | 128.5 | 364.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.389 | 0 | 0 | 39049.389 | 0 | 0 |  | 170.5 | 406.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3895 | 0 | 0 | 39049.3895 | 0 | 0 |  | 212.5 | 448.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.39 | 0 | 0 | 39049.39 | 0 | 0 |  | 254.5 | 490.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3905 | 0 | 0 | 39049.3905 | 0 | 0 |  | 296.5 | 532.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3909 | 0 | 0 | 39049.391 | 0 | 0 |  | 338.5 | 574.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3914 | 0 | 0 | 39049.3914 | 0 | 0 |  | 380.5 | 616.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3919 | 0 | 0 | 39049.3919 | 0 | 0 |  | 422.5 | 658.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3924 | 0 | 0 | 39049.3924 | 0 | 0 |  | 464.5 | 700.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3929 | 0 | 0 | 39049.3929 | 0 | 0 |  | 506.5 | 742.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3934 | 0 | 0 | 39049.3934 | 0 | 0 |  | 548.5 | 784.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3939 | 0 | 0 | 39049.3939 | 0 | 0 |  | 590.5 | 826.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3944 | 0 | 0 | 39049.3944 | 0 | 0 |  | 632.5 | 868.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3948 | 0 | 0 | 39049.3948 | 0 | 0 |  | 674.5 | 910.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3953 | 0 | 0 | 39049.3953 | 0 | 0 |  | 716.5 | 952.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3958 | 0 | 0 | 39049.3958 | 0 | 0 |  | 758.5 | 994.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3963 | 0 | 0 | 39049.3963 | 0 | 0 |  | 800.5 | 1036.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3968 | 0 | 0 | 39049.3968 | 0 | 0 |  | 842.5 | 1078.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3973 | 0 | 0 | 39049.3973 | 0 | 0 |  | 884.5 | 1120.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3978 | 0 | 0 | 39049.3978 | 0 | 0 |  | 926.5 | 1162.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3982 | 0 | 0 | 39049.3983 | 0 | 0 |  | 968.5 | 1204.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3987 | 0 | 0 | 39049.3987 | 0 | 0 |  | 1010.5 | 1246.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3992 | 0 | 0 | 39049.3992 | 0 | 0 |  | 1052.5 | 1288.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.3997 | 0 | 0 | 39049.3997 | 0 | 0 |  | 1094.5 | 1330.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4002 | 0 | 0 | 39049.4002 | 0 | 0 |  | 1136.5 | 1372.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4007 | 0 | 0 | 39049.4007 | 0 | 0 |  | 1178.5 | 1414.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4012 | 0 | 0 | 39049.4012 | 0 | 0 |  | 1220.5 | 1456.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4016 | 0 | 0 | 39049.4017 | 0 | 0 |  | 1262.5 | 1498.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4021 | 0 | 0 | 39049.4021 | 0 | 0 |  | 1304.5 | 1540.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4026 | 0 | 0 | 39049.4026 | 0 | 0 |  | 1346.5 | 1582.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4031 | 0 | 0 | 39049.4031 | 0 | 0 |  | 1388.5 | 1624.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4036 | 0 | 0 | 39049.4036 | 0 | 0 |  | 1430.5 | 1666.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4041 | 0 | 0 | 39049.4041 | 0 | 0 |  | 1472.5 | 1708.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4046 | 0 | 0 | 39049.4046 | 0 | 0 |  | 1514.5 | 1750.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.405 | 0 | 0 | 39049.4051 | 0 | 0 |  | 1556.5 | 1792.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4055 | 0 | 0 | 39049.4055 | 0 | 0 |  | 1598.5 | 1834.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.406 | 0 | 0 | 39049.406 | 0 | 0 |  | 1640.5 | 1876.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.4065 | 0 | 0 | 39049.4065 | 0 | 0 |  | 1682.5 | 1918.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515576 | 515576 | 515575.9997
39049.407 | 1939 | 1 | 39049.407 | 0 | 0 |  | 1724.5 | 1960.5 | 118.3761 | 0.06105 | 0.030525 | 0 | 1.1838 | 0.0006105 | 0.00030525 | 0 | 1.1832 | 0.00030525 | 32.9917 | 515576.0016 | 63825.6205
39049.4075 | 2441 | 1 | 39049.4075 | 0 | 0 |  | 1766.5 | 2002.5 | 149.0232 | 0.06105 | 0.030525 | 0 | 1.4902 | 0.0006105 | 0.00030525 | 0 | 1.4896 | 0.00030525 | 5.6303 | 515576.0006 | 13635.3553
39049.408 | 2405 | 1 | 39049.408 | 0 | 0 |  | 1808.5 | 2044.5 | 146.8254 | 0.06105 | 0.030525 | 0 | 1.4683 | 0.0006105 | 0.00030525 | 0 | 1.4676 | 0.00030525 | 7.2121 | 515575.9996 | 17234.6572
39049.4084 | 2562 | 1 | 39049.4085 | 0 | 0 |  | 1850.5 | 2086.5 | 156.4103 | 0.06105 | 0.030525 | 0 | 1.5641 | 0.0006105 | 0.00030525 | 0 | 1.5635 | 0.00030525 | 0.63959 | 515576.0006 | 1537.7018
39049.4089 | 2464 | 1 | 39049.4089 | 0 | 0 |  | 1892 | 2128 | 150.4274 | 0.06105 | 0.030525 | 0 | 1.5043 | 0.0006105 | 0.00030525 | 0 | 1.5037 | 0.00030525 | 4.6439 | 515576.0006 | 11335.8013
39049.4094 | 2382 | 1 | 39049.4094 | 0 | 0 |  | 1934.5 | 2170.5 | 145.4212 | 0.06105 | 0.030525 | 0 | 1.4542 | 0.0006105 | 0.00030525 | 0 | 1.4536 | 0.00030525 | 8.2478 | 515575.9996 | 19534.2112
39049.4099 | 2424 | 1 | 39049.4099 | 0 | 0 |  | 1976.5 | 2212.5 | 147.9853 | 0.06105 | 0.030525 | 0 | 1.4799 | 0.0006105 | 0.00030525 | 0 | 1.4792 | 0.00030525 | 6.3714 | 515576.0016 | 15335.0257
39049.4104 | 2352 | 1 | 39049.4104 | 0 | 0 |  | 2018 | 2254 | 143.5897 | 0.06105 | 0.030525 | 0 | 1.4359 | 0.0006105 | 0.00030525 | 0 | 1.4353 | 0.00030525 | 9.6291 | 515576.0006 | 22533.6294
39049.4109 | 2286 | 1 | 39049.4109 | 0 | 0 |  | 2060 | 2296 | 139.5604 | 0.06105 | 0.030525 | 0 | 1.3956 | 0.0006105 | 0.00030525 | 0 | 1.395 | 0.00030525 | 12.7956 | 515575.9996 | 29132.3496
39049.4114 | 2215 | 1 | 39049.4114 | 0 | 0 |  | 2102 | 2338 | 135.2259 | 0.06105 | 0.030525 | 0 | 1.3523 | 0.0006105 | 0.00030525 | 0 | 1.3516 | 0.00030525 | 16.4128 | 515576.0016 | 36230.9727
39049.4118 | 2556 | 1 | 39049.4119 | 0 | 0 |  | 2144 | 2380 | 156.044 | 0.06105 | 0.030525 | 0 | 1.5604 | 0.0006105 | 0.00030525 | 0 | 1.5598 | 0.00030525 | 0.87593 | 515576.0006 | 2137.5854
39049.4123 | 2014 | 1 | 39049.4123 | 0 | 0 |  | 2186 | 2422 | 122.9548 | 0.06105 | 0.030525 | 0 | 1.2295 | 0.0006105 | 0.00030525 | 0 | 1.2289 | 0.00030525 | 28.0368 | 515575.9996 | 56327.0749
39049.4128 | 2210 | 1 | 39049.4128 | 0 | 0 |  | 2228 | 2464 | 134.9206 | 0.06105 | 0.030525 | 0 | 1.3492 | 0.0006105 | 0.00030525 | 0 | 1.3486 | 0.00030525 | 16.6763 | 515576.0006 | 36730.8758
39049.4133 | 2200 | 1 | 39049.4133 | 1 | 0 |  | 2270 | 2506 | 134.3101 | 0.06105 | 0.06105 | 0 | 1.3431 | 0.0006105 | 0.0006105 | 0 | 1.3425 | 0.0006105 | 17.2069 | 257738 | 37723.3637
39049.4138 | 1963 | 1 | 39049.4138 | 0 | 0 |  | 2312 | 2548 | 119.8413 | 0.06105 | 0.030525 | 0 | 1.1984 | 0.0006105 | 0.00030525 | 0 | 1.1978 | 0.00030525 | 31.3649 | 515576.0006 | 61426.0859
39049.4143 | 2250 | 1 | 39049.4143 | 0 | 0 |  | 2354 | 2590 | 137.3626 | 0.06105 | 0.030525 | 0 | 1.3736 | 0.0006105 | 0.00030525 | 0 | 1.373 | 0.00030525 | 14.6012 | 515576.0006 | 32731.6514
39049.4148 | 2462 | 1 | 39049.4148 | 1 | 0 |  | 2396 | 2632 | 150.3053 | 0.06105 | 0.06105 | 0 | 1.5031 | 0.0006105 | 0.0006105 | 0 | 1.5024 | 0.0006105 | 4.729 | 257738.0002 | 11533.5251
39049.4152 | 2441 | 1 | 39049.4153 | 0 | 0 |  | 2438 | 2674 | 149.0232 | 0.06105 | 0.030525 | 0 | 1.4902 | 0.0006105 | 0.00030525 | 0 | 1.4896 | 0.00030525 | 5.6303 | 515576.0006 | 13635.3553
39049.4157 | 2046 | 1 | 39049.4158 | 0 | 0 |  | 2480 | 2716 | 124.9084 | 0.06105 | 0.030525 | 0 | 1.2491 | 0.0006105 | 0.00030525 | 0 | 1.2485 | 0.00030525 | 26.0333 | 515575.9996 | 53127.6955
39049.4162 | 2431 | 1 | 39049.4162 | 0 | 0 |  | 2522 | 2758 | 148.4127 | 0.06105 | 0.030525 | 0 | 1.4841 | 0.0006105 | 0.00030525 | 0 | 1.4835 | 0.00030525 | 6.065 | 515575.9996 | 14635.1614
39049.4167 | 1930 | 1 | 39049.4167 | 0 | 0 |  | 2564 | 2800 | 117.8266 | 0.06105 | 0.030525 | 0 | 1.1783 | 0.0006105 | 0.00030525 | 0 | 1.1777 | 0.00030525 | 33.6122 | 515575.9996 | 64725.446
39049.4172 | 1990 | 1 | 39049.4172 | 0 | 0 |  | 2606 | 2842 | 121.4896 | 0.06105 | 0.030525 | 0 | 1.2149 | 0.0006105 | 0.00030525 | 0 | 1.2143 | 0.00030525 | 29.5817 | 515576.0006 | 58726.6095
39049.4177 | 2221 | 1 | 39049.4177 | 0 | 0 |  | 2648 | 2884 | 135.5922 | 0.06105 | 0.030525 | 0 | 1.3559 | 0.0006105 | 0.00030525 | 0 | 1.3553 | 0.00030525 | 16.0982 | 515576.0006 | 35631.0891
39049.4182 | 1928 | 1 | 39049.4182 | 0 | 0 |  | 2690 | 2926 | 117.7045 | 0.06105 | 0.030525 | 0 | 1.177 | 0.0006105 | 0.00030525 | 0 | 1.1764 | 0.00030525 | 33.7509 | 515575.9996 | 64925.4072
39049.4186 | 2127 | 1 | 39049.4187 | 1 | 0 |  | 2732 | 2968 | 129.8535 | 0.06105 | 0.06105 | 0 | 1.2985 | 0.0006105 | 0.0006105 | 0 | 1.2979 | 0.0006105 | 21.2314 | 257738 | 45020.5324
39049.4191 | 2147 | 1 | 39049.4192 | 0 | 0 |  | 2774 | 3010 | 131.0745 | 0.06105 | 0.030525 | 0 | 1.3107 | 0.0006105 | 0.00030525 | 0 | 1.3101 | 0.00030525 | 20.1016 | 515576.0006 | 43029.6541
39049.4196 | 1960 | 1 | 39049.4196 | 1 | 0 |  | 2816 | 3052 | 119.6581 | 0.06105 | 0.06105 | 0 | 1.1966 | 0.0006105 | 0.0006105 | 0 | 1.196 | 0.0006105 | 31.5661 | 257738.0002 | 61714.0555
39049.4201 | 2295 | 1 | 39049.4201 | 0 | 0 |  | 2858 | 3094 | 140.1099 | 0.06105 | 0.030525 | 0 | 1.4011 | 0.0006105 | 0.00030525 | 0 | 1.4005 | 0.00030525 | 12.3531 | 515575.9996 | 28232.5241
39049.4206 | 2005 | 1 | 39049.4206 | 1 | 0 |  | 2900 | 3136 | 122.4054 | 0.06105 | 0.06105 | 0 | 1.2241 | 0.0006105 | 0.0006105 | 0 | 1.2234 | 0.0006105 | 28.6118 | 257738 | 57215.8008
39049.4211 | 2394 | 1 | 39049.4211 | 1 | 0 |  | 2942 | 3178 | 146.1538 | 0.06105 | 0.06105 | 0 | 1.4615 | 0.0006105 | 0.0006105 | 0 | 1.4609 | 0.0006105 | 7.705 | 257738 | 18330.8878
39049.4216 | 2515 | 1 | 39049.4216 | 0 | 0 |  | 2984 | 3220 | 153.5409 | 0.06105 | 0.030525 | 0 | 1.5354 | 0.0006105 | 0.00030525 | 0 | 1.5348 | 0.00030525 | 2.5211 | 515575.9996 | 6236.7903

## B3-B4
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.1893 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39049.3846 | 0 | 0 | 39049.3846 | 0 | 0 |  | -210 | 26 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3851 | 0 | 0 | 39049.3851 | 0 | 0 |  | -168.5 | 67.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3856 | 0 | 0 | 39049.3856 | 0 | 0 |  | -126.5 | 109.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3861 | 0 | 0 | 39049.3861 | 0 | 0 |  | -84.5 | 151.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3865 | 0 | 0 | 39049.3866 | 0 | 0 |  | -42.5 | 193.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.387 | 0 | 0 | 39049.387 | 0 | 0 |  | -0.5 | 235.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3875 | 0 | 0 | 39049.3875 | 0 | 0 |  | 41.5 | 277.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.388 | 0 | 0 | 39049.388 | 0 | 0 |  | 83.5 | 319.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3885 | 0 | 0 | 39049.3885 | 0 | 0 |  | 125.5 | 361.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.389 | 0 | 0 | 39049.389 | 0 | 0 |  | 167.5 | 403.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3895 | 0 | 0 | 39049.3895 | 0 | 0 |  | 209.5 | 445.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3899 | 0 | 0 | 39049.39 | 0 | 0 |  | 251.5 | 487.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3904 | 0 | 0 | 39049.3904 | 0 | 0 |  | 293.5 | 529.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3909 | 0 | 0 | 39049.3909 | 0 | 0 |  | 335.5 | 571.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3914 | 0 | 0 | 39049.3914 | 0 | 0 |  | 377.5 | 613.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3919 | 0 | 0 | 39049.3919 | 0 | 0 |  | 419.5 | 655.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3924 | 0 | 0 | 39049.3924 | 0 | 0 |  | 461.5 | 697.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3929 | 0 | 0 | 39049.3929 | 0 | 0 |  | 503.5 | 739.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3933 | 0 | 0 | 39049.3934 | 0 | 0 |  | 545.5 | 781.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3938 | 0 | 0 | 39049.3938 | 0 | 0 |  | 587.5 | 823.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3943 | 0 | 0 | 39049.3943 | 0 | 0 |  | 629.5 | 865.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3948 | 0 | 0 | 39049.3948 | 0 | 0 |  | 671.5 | 907.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3953 | 0 | 0 | 39049.3953 | 0 | 0 |  | 713.5 | 949.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3958 | 0 | 0 | 39049.3958 | 0 | 0 |  | 755.5 | 991.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3963 | 0 | 0 | 39049.3963 | 0 | 0 |  | 797.5 | 1033.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3967 | 0 | 0 | 39049.3968 | 0 | 0 |  | 839.5 | 1075.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3972 | 0 | 0 | 39049.3972 | 0 | 0 |  | 881.5 | 1117.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3977 | 0 | 0 | 39049.3977 | 0 | 0 |  | 923.5 | 1159.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3982 | 0 | 0 | 39049.3982 | 0 | 0 |  | 965.5 | 1201.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3987 | 0 | 0 | 39049.3987 | 0 | 0 |  | 1007.5 | 1243.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3992 | 0 | 0 | 39049.3992 | 0 | 0 |  | 1049.5 | 1285.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.3997 | 0 | 0 | 39049.3997 | 0 | 0 |  | 1091.5 | 1327.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4002 | 0 | 0 | 39049.4002 | 0 | 0 |  | 1133.5 | 1369.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4006 | 0 | 0 | 39049.4006 | 0 | 0 |  | 1175.5 | 1411.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4011 | 0 | 0 | 39049.4011 | 0 | 0 |  | 1217.5 | 1453.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4016 | 0 | 0 | 39049.4016 | 0 | 0 |  | 1259.5 | 1495.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4021 | 0 | 0 | 39049.4021 | 0 | 0 |  | 1301.5 | 1537.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4026 | 0 | 0 | 39049.4026 | 0 | 0 |  | 1343.5 | 1579.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4031 | 0 | 0 | 39049.4031 | 0 | 0 |  | 1385.5 | 1621.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4036 | 0 | 0 | 39049.4036 | 0 | 0 |  | 1427.5 | 1663.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.404 | 0 | 0 | 39049.4041 | 0 | 0 |  | 1469.5 | 1705.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4045 | 0 | 0 | 39049.4045 | 0 | 0 |  | 1511.5 | 1747.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.405 | 0 | 0 | 39049.405 | 0 | 0 |  | 1553.5 | 1789.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4055 | 0 | 0 | 39049.4055 | 0 | 0 |  | 1595.5 | 1831.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.406 | 0 | 0 | 39049.406 | 0 | 0 |  | 1637.5 | 1873.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.4065 | 0 | 0 | 39049.4065 | 0 | 0 |  | 1679.5 | 1915.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39049.407 | 2383 | 0 | 39049.407 | 2466 | 0 |  | 1721.5 | 1957.5 | 145.4823 | 0 | 150.5495 | 0 | 1.4548 | 0 | 1.5055 | 0 | 1.4548 | 1.5055 | 7.3596 | 3.7461 | 5.9048
39049.4074 | 2263 | 0 | 39049.4075 | 2329 | 0 |  | 1763.5 | 1999.5 | 138.1563 | 0 | 142.1856 | 0 | 1.3816 | 0 | 1.4219 | 0 | 1.3816 | 1.4219 | 13.0526 | 9.8489 | 11.671
39049.4079 | 2227 | 0 | 39049.4079 | 2014 | 0 |  | 1805.5 | 2041.5 | 135.9585 | 0 | 122.9548 | 0 | 1.3596 | 0 | 1.2295 | 0 | 1.3596 | 1.2295 | 14.8801 | 27.0298 | 13.5205
39049.4084 | 2503 | 0 | 39049.4084 | 2001 | 0 |  | 1847.5 | 2083.5 | 152.8083 | 0 | 122.1612 | 0 | 1.5281 | 0 | 1.2216 | 0 | 1.5281 | 1.2216 | 2.2125 | 27.8551 | 0.68446
39049.4089 | 1987 | 1 | 39049.4089 | 2000 | 1 |  | 1889.5 | 2125.5 | 121.3065 | 0.06105 | 122.1001 | 0.06105 | 1.2131 | 0.0006105 | 1.221 | 0.0006105 | 1.2125 | 1.2204 | 28.8223 | 27.9815 | 12470.6324
39049.4094 | 1934 | 0 | 39049.4094 | 2268 | 0 |  | 1931.5 | 2167.5 | 118.0708 | 0 | 138.4615 | 0 | 1.1807 | 0 | 1.3846 | 0 | 1.1807 | 1.3846 | 32.2844 | 12.8034 | 31.1037
39049.4099 | 2526 | 0 | 39049.4099 | 2447 | 0 |  | 1973.5 | 2209.5 | 154.2125 | 0 | 149.3895 | 0 | 1.5421 | 0 | 1.4939 | 0 | 1.5421 | 1.4939 | 1.2819 | 4.5517 | 0.26026
39049.4104 | 2219 | 0 | 39049.4104 | 2528 | 0 |  | 2015.5 | 2251.5 | 135.4701 | 0 | 154.3346 | 0 | 1.3547 | 0 | 1.5433 | 0 | 1.3547 | 1.5433 | 15.2943 | 1.2017 | 13.9396
39049.4108 | 1939 | 1 | 39049.4109 | 2432 | 0 |  | 2057.5 | 2293.5 | 118.3761 | 0.06105 | 148.4737 | 0 | 1.1838 | 0.0006105 | 1.4847 | 0 | 1.1832 | 1.4847 | 32.2803 | 5.1965 | 3054.7012
39049.4113 | 2531 | 0 | 39049.4113 | 2542 | 0 |  | 2099.5 | 2335.5 | 154.5177 | 0 | 155.1893 | 0 | 1.5452 | 0 | 1.5519 | 0 | 1.5452 | 1.5519 | 1.0818 | 0.64437 | 0.46339
39049.4118 | 2003 | 0 | 39049.4118 | 1969 | 0 |  | 2141.5 | 2377.5 | 122.2833 | 0 | 120.2076 | 0 | 1.2228 | 0 | 1.2021 | 0 | 1.2228 | 1.2021 | 27.7274 | 29.933 | 26.5046
39049.4123 | 2161 | 0 | 39049.4123 | 1962 | 0 |  | 2183.5 | 2419.5 | 131.9292 | 0 | 119.7802 | 0 | 1.3193 | 0 | 1.1978 | 0 | 1.3193 | 1.1978 | 18.3887 | 30.3965 | 17.0694
39049.4128 | 1989 | 0 | 39049.4128 | 2297 | 0 |  | 2225.5 | 2461.5 | 121.4286 | 0 | 140.232 | 0 | 1.2143 | 0 | 1.4023 | 0 | 1.2143 | 1.4023 | 28.6264 | 11.3792 | 27.4122
39049.4133 | 1988 | 0 | 39049.4133 | 2500 | 0 |  | 2267.5 | 2503.5 | 121.3675 | 0 | 152.6252 | 0 | 1.2137 | 0 | 1.5263 | 0 | 1.2137 | 1.5263 | 28.6911 | 2.3352 | 27.4775
39049.4138 | 2527 | 0 | 39049.4138 | 2041 | 0 |  | 2309.5 | 2545.5 | 154.2735 | 0 | 124.6032 | 0 | 1.5427 | 0 | 1.246 | 0 | 1.5427 | 1.246 | 1.2418 | 25.3493 | 0.30095
39049.4142 | 2204 | 0 | 39049.4143 | 2186 | 1 |  | 2351.5 | 2587.5 | 134.5543 | 0 | 133.4554 | 0.06105 | 1.3455 | 0 | 1.3346 | 0.0006105 | 1.3455 | 1.3339 | 16.0789 | 17.0883 | 14.7334
39049.4147 | 1993 | 0 | 39049.4147 | 2182 | 0 |  | 2393.5 | 2629.5 | 121.6728 | 0 | 133.2112 | 0 | 1.2167 | 0 | 1.3321 | 0 | 1.2167 | 1.3321 | 28.3683 | 17.2493 | 27.1516
39049.4152 | 1978 | 5 | 39049.4152 | 2409 | 3 |  | 2435.5 | 2671.5 | 120.757 | 0.30525 | 147.0696 | 0.18315 | 1.2076 | 0.0030525 | 1.4707 | 0.0018315 | 1.2045 | 1.4689 | 30.6626 | 6.234 | 675.286
39049.4157 | 1859 | 6 | 39049.4157 | 2390 | 5 |  | 2477.5 | 2713.5 | 113.4921 | 0.3663 | 145.9096 | 0.30525 | 1.1349 | 0.003663 | 1.4591 | 0.0030525 | 1.1313 | 1.456 | 39.5473 | 7.0976 | 765.8626
39049.4162 | 1878 | 3 | 39049.4162 | 2224 | 2 |  | 2519.5 | 2755.5 | 114.652 | 0.18315 | 135.7753 | 0.1221 | 1.1465 | 0.0018315 | 1.3578 | 0.001221 | 1.1447 | 1.3565 | 36.6759 | 15.0856 | 2959.7389
39049.4167 | 1908 | 2 | 39049.4167 | 2229 | 1 |  | 2561.5 | 2797.5 | 116.4835 | 0.1221 | 136.0806 | 0.06105 | 1.1648 | 0.001221 | 1.3608 | 0.0006105 | 1.1636 | 1.3602 | 34.3664 | 14.803 | 4180.1898
39049.4172 | 2250 | 0 | 39049.4172 | 2289 | 1 |  | 2603.5 | 2839.5 | 137.3626 | 0 | 139.7436 | 0.06105 | 1.3736 | 0 | 1.3974 | 0.0006105 | 1.3736 | 1.3968 | 13.7058 | 11.8173 | 12.3322
39049.4177 | 2477 | 1 | 39049.4177 | 2303 | 0 |  | 2645.5 | 2881.5 | 151.221 | 0.06105 | 140.5983 | 0 | 1.5122 | 0.0006105 | 1.406 | 0 | 1.5116 | 1.406 | 3.2988 | 11.089 | 802.361
39049.4181 | 2043 | 1 | 39049.4181 | 2106 | 0 |  | 2687.5 | 2923.5 | 124.7253 | 0.06105 | 128.5714 | 0 | 1.2473 | 0.0006105 | 1.2857 | 0 | 1.2466 | 1.2857 | 25.2967 | 21.4805 | 9095.4129
39049.4186 | 2012 | 0 | 39049.4186 | 2098 | 0 |  | 2729.5 | 2965.5 | 122.8327 | 0 | 128.083 | 0 | 1.2283 | 0 | 1.2808 | 0 | 1.2283 | 1.2808 | 27.1561 | 21.9438 | 25.9277
39049.4191 | 2161 | 0 | 39049.4191 | 2472 | 0 |  | 2771.5 | 3007.5 | 131.9292 | 0 | 150.9158 | 0 | 1.3193 | 0 | 1.5092 | 0 | 1.3193 | 1.5092 | 18.3887 | 3.4943 | 17.0694
39049.4196 | 2435 | 0 | 39049.4196 | 1988 | 0 |  | 2813.5 | 3049.5 | 148.6569 | 0 | 121.3675 | 0 | 1.4866 | 0 | 1.2137 | 0 | 1.4866 | 1.2137 | 5.0669 | 28.6911 | 3.5804
39049.4201 | 2460 | 0 | 39049.4201 | 2309 | 0 |  | 2855.5 | 3091.5 | 150.1832 | 0 | 140.9646 | 0 | 1.5018 | 0 | 1.4096 | 0 | 1.5018 | 1.4096 | 3.9992 | 10.8003 | 2.4974
39049.4206 | 2086 | 0 | 39049.4206 | 2060 | 0 |  | 2897 | 3133 | 127.3504 | 0 | 125.7631 | 0 | 1.2735 | 0 | 1.2576 | 0 | 1.2735 | 1.2576 | 22.6453 | 24.1932 | 21.3717
39049.4211 | 2032 | 0 | 39049.4211 | 1995 | 0 |  | 2939.5 | 3175.5 | 124.0537 | 0 | 121.7949 | 0 | 1.2405 | 0 | 1.2179 | 0 | 1.2405 | 1.2179 | 25.9045 | 28.2396 | 24.664
39049.4215 | 1960 | 0 | 39049.4216 | 1922 | 0 |  | 2981.5 | 3217.5 | 119.6581 | 0 | 117.3382 | 0 | 1.1966 | 0 | 1.1734 | 0 | 1.1966 | 1.1734 | 30.5296 | 33.1103 | 29.333

## A2-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 152.16 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39049.3846 | 0 | 0 | 39049.3846 | 0 | 0 |  | -213 | 23 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.385 | 0 | 0 | 39049.3851 | 0 | 0 |  | -171 | 65 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3855 | 0 | 0 | 39049.3856 | 0 | 0 |  | -129 | 107 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.386 | 0 | 0 | 39049.386 | 0 | 0 |  | -87 | 149 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3865 | 0 | 0 | 39049.3865 | 0 | 0 |  | -45 | 191 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.387 | 0 | 0 | 39049.387 | 0 | 0 |  | -3 | 233 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3875 | 0 | 0 | 39049.3875 | 0 | 0 |  | 39 | 275 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.388 | 0 | 0 | 39049.388 | 0 | 0 |  | 81 | 317 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3884 | 0 | 0 | 39049.3885 | 0 | 0 |  | 123 | 359 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3889 | 0 | 0 | 39049.389 | 0 | 0 |  | 165 | 401 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3894 | 0 | 0 | 39049.3894 | 0 | 0 |  | 207 | 443 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3899 | 0 | 0 | 39049.3899 | 0 | 0 |  | 249 | 485 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3904 | 0 | 0 | 39049.3904 | 0 | 0 |  | 291 | 527 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3909 | 0 | 0 | 39049.3909 | 0 | 0 |  | 333 | 569 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3914 | 0 | 0 | 39049.3914 | 0 | 0 |  | 375 | 611 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3919 | 0 | 0 | 39049.3919 | 0 | 0 |  | 417 | 653 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3923 | 0 | 0 | 39049.3924 | 0 | 0 |  | 459 | 695 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3928 | 0 | 0 | 39049.3928 | 0 | 0 |  | 501 | 737 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3933 | 0 | 0 | 39049.3933 | 0 | 0 |  | 543 | 779 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3938 | 0 | 0 | 39049.3938 | 0 | 0 |  | 584.5 | 820.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3943 | 0 | 0 | 39049.3943 | 0 | 0 |  | 627 | 863 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3948 | 0 | 0 | 39049.3948 | 0 | 0 |  | 668.5 | 904.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3953 | 0 | 0 | 39049.3953 | 0 | 0 |  | 711 | 947 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3957 | 0 | 0 | 39049.3958 | 0 | 0 |  | 753 | 989 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3962 | 0 | 0 | 39049.3962 | 0 | 0 |  | 794.5 | 1030.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3967 | 0 | 0 | 39049.3967 | 0 | 0 |  | 836.5 | 1072.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3972 | 0 | 0 | 39049.3972 | 0 | 0 |  | 878.5 | 1114.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3977 | 0 | 0 | 39049.3977 | 0 | 0 |  | 920.5 | 1156.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3982 | 0 | 0 | 39049.3982 | 0 | 0 |  | 962.5 | 1198.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3987 | 0 | 0 | 39049.3987 | 0 | 0 |  | 1004.5 | 1240.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3991 | 0 | 0 | 39049.3992 | 0 | 0 |  | 1046.5 | 1282.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.3996 | 0 | 0 | 39049.3996 | 0 | 0 |  | 1088.5 | 1324.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4001 | 0 | 0 | 39049.4001 | 0 | 0 |  | 1130.5 | 1366.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4006 | 0 | 0 | 39049.4006 | 0 | 0 |  | 1172.5 | 1408.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4011 | 0 | 0 | 39049.4011 | 0 | 0 |  | 1214.5 | 1450.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4016 | 0 | 0 | 39049.4016 | 0 | 0 |  | 1256.5 | 1492.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4021 | 0 | 0 | 39049.4021 | 0 | 0 |  | 1298.5 | 1534.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4025 | 0 | 0 | 39049.4026 | 0 | 0 |  | 1340.5 | 1576.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.403 | 0 | 0 | 39049.403 | 0 | 0 |  | 1382.5 | 1618.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4035 | 0 | 0 | 39049.4035 | 0 | 0 |  | 1424.5 | 1660.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.404 | 0 | 0 | 39049.404 | 0 | 0 |  | 1466.5 | 1702.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4045 | 0 | 0 | 39049.4045 | 0 | 0 |  | 1508.5 | 1744.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.405 | 0 | 0 | 39049.405 | 0 | 0 |  | 1550.5 | 1786.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4055 | 0 | 0 | 39049.4055 | 0 | 0 |  | 1592.5 | 1828.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4059 | 0 | 0 | 39049.406 | 0 | 0 |  | 1634.5 | 1870.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4064 | 0 | 0 | 39049.4064 | 0 | 0 |  | 1676.5 | 1912.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4069 | 0 | 0 | 39049.4069 | 0 | 0 |  | 1718.5 | 1954.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4074 | 0 | 0 | 39049.4074 | 0 | 0 |  | 1760.5 | 1996.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4079 | 0 | 0 | 39049.4079 | 0 | 0 |  | 1802.5 | 2038.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4084 | 0 | 0 | 39049.4084 | 0 | 0 |  | 1844.5 | 2080.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4089 | 0 | 0 | 39049.4089 | 0 | 0 |  | 1886.5 | 2122.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39049.4094 | 2311 | 1 | 39049.4094 | 0 | 0 |  | 1928.5 | 2164.5 | 141.0867 | 0.06105 | 0.030525 | 0 | 1.4109 | 0.0006105 | 0.00030525 | 0 | 1.4103 | 0.00030525 | 7.8519 | 498376.0003 | 18034.3814
39049.4098 | 2262 | 1 | 39049.4098 | 0 | 0 |  | 1970.5 | 2206.5 | 138.0952 | 0.06105 | 0.030525 | 0 | 1.381 | 0.0006105 | 0.00030525 | 0 | 1.3803 | 0.00030525 | 10.1893 | 498376.0003 | 22933.3984
39049.4103 | 1954 | 1 | 39049.4103 | 1 | 0 |  | 2012.5 | 2248.5 | 119.2918 | 0.06105 | 0.06105 | 0 | 1.1929 | 0.0006105 | 0.0006105 | 0 | 1.1923 | 0.0006105 | 27.5668 | 249138.0002 | 53716.4391
39049.4108 | 2282 | 1 | 39049.4108 | 0 | 0 |  | 2054.5 | 2290.5 | 139.3162 | 0.06105 | 0.030525 | 0 | 1.3932 | 0.0006105 | 0.00030525 | 0 | 1.3926 | 0.00030525 | 9.2231 | 498375.9994 | 20933.7996
39049.4113 | 2049 | 1 | 39049.4113 | 0 | 0 |  | 2096.5 | 2332.5 | 125.0916 | 0.06105 | 0.030525 | 0 | 1.2509 | 0.0006105 | 0.00030525 | 0 | 1.2503 | 0.00030525 | 21.6494 | 498375.9994 | 44229.1254
39049.4118 | 2113 | 1 | 39049.4118 | 0 | 0 |  | 2138.5 | 2374.5 | 128.9988 | 0.06105 | 0.030525 | 0 | 1.29 | 0.0006105 | 0.00030525 | 0 | 1.2894 | 0.00030525 | 17.9631 | 498376.0003 | 37830.4093
39049.4123 | 2227 | 1 | 39049.4123 | 0 | 0 |  | 2180.5 | 2416.5 | 135.9585 | 0.06105 | 0.030525 | 0 | 1.3596 | 0.0006105 | 0.00030525 | 0 | 1.359 | 0.00030525 | 11.9218 | 498376.0003 | 26432.6962
39049.4128 | 2069 | 1 | 39049.4128 | 0 | 0 |  | 2222.5 | 2458.5 | 126.3126 | 0.06105 | 0.030525 | 0 | 1.2631 | 0.0006105 | 0.00030525 | 0 | 1.2625 | 0.00030525 | 20.4729 | 498376.0003 | 42229.5266
39049.4132 | 1992 | 1 | 39049.4133 | 1 | 0 |  | 2264.5 | 2500.5 | 121.6117 | 0.06105 | 0.06105 | 0 | 1.2161 | 0.0006105 | 0.0006105 | 0 | 1.2155 | 0.0006105 | 25.1321 | 249138 | 49917.9637
39049.4137 | 2198 | 1 | 39049.4137 | 0 | 0 |  | 2306.5 | 2542.5 | 134.188 | 0.06105 | 0.030525 | 0 | 1.3419 | 0.0006105 | 0.00030525 | 0 | 1.3413 | 0.00030525 | 13.3992 | 498376.0003 | 29332.1145
39049.4142 | 2442 | 1 | 39049.4142 | 0 | 0 |  | 2348.5 | 2584.5 | 149.0842 | 0.06105 | 0.030525 | 0 | 1.4908 | 0.0006105 | 0.00030525 | 0 | 1.4902 | 0.00030525 | 2.0639 | 498376.0003 | 4937.0094
39049.4147 | 2313 | 1 | 39049.4147 | 1 | 0 |  | 2390.5 | 2626.5 | 141.2088 | 0.06105 | 0.06105 | 0 | 1.4121 | 0.0006105 | 0.0006105 | 0 | 1.4115 | 0.0006105 | 7.7587 | 249138 | 17830.843
39049.4152 | 2258 | 1 | 39049.4152 | 0 | 0 |  | 2432.5 | 2668.5 | 137.851 | 0.06105 | 0.030525 | 0 | 1.3785 | 0.0006105 | 0.00030525 | 0 | 1.3779 | 0.00030525 | 10.3846 | 498375.9994 | 23333.3181
39049.4157 | 2225 | 1 | 39049.4157 | 0 | 0 |  | 2474.5 | 2710.5 | 135.8364 | 0.06105 | 0.030525 | 0 | 1.3584 | 0.0006105 | 0.00030525 | 0 | 1.3578 | 0.00030525 | 12.0225 | 498376.0003 | 26632.6561
39049.4162 | 1949 | 1 | 39049.4162 | 0 | 0 |  | 2516.5 | 2752.5 | 118.9866 | 0.06105 | 0.030525 | 0 | 1.1899 | 0.0006105 | 0.00030525 | 0 | 1.1893 | 0.00030525 | 27.8943 | 498376.0003 | 54227.1192
39049.4166 | 2298 | 1 | 39049.4167 | 0 | 0 |  | 2558.5 | 2794.5 | 140.293 | 0.06105 | 0.030525 | 0 | 1.4029 | 0.0006105 | 0.00030525 | 0 | 1.4023 | 0.00030525 | 8.4623 | 498376.0003 | 19334.1206
39049.4171 | 1934 | 1 | 39049.4171 | 0 | 0 |  | 2600.5 | 2836.5 | 118.0708 | 0.06105 | 0.030525 | 0 | 1.1807 | 0.0006105 | 0.00030525 | 0 | 1.1801 | 0.00030525 | 28.8867 | 498376.0003 | 55726.8183
39049.4176 | 2330 | 1 | 39049.4176 | 0 | 0 |  | 2642.5 | 2878.5 | 142.2466 | 0.06105 | 0.030525 | 0 | 1.4225 | 0.0006105 | 0.00030525 | 0 | 1.4219 | 0.00030525 | 6.9721 | 498376.0003 | 16134.7625
39049.4181 | 2190 | 1 | 39049.4181 | 0 | 0 |  | 2684.5 | 2920.5 | 133.6996 | 0.06105 | 0.030525 | 0 | 1.337 | 0.0006105 | 0.00030525 | 0 | 1.3364 | 0.00030525 | 13.8136 | 498376.0003 | 30131.954
39049.4186 | 2476 | 1 | 39049.4186 | 1 | 0 |  | 2726.5 | 2962.5 | 151.16 | 0.06105 | 0.06105 | 0 | 1.5116 | 0.0006105 | 0.0006105 | 0 | 1.511 | 0.0006105 | 0.66182 | 249138 | 1537.3829
39049.4191 | 2032 | 1 | 39049.4191 | 0 | 0 |  | 2768.5 | 3004.5 | 124.0537 | 0.06105 | 0.030525 | 0 | 1.2405 | 0.0006105 | 0.00030525 | 0 | 1.2399 | 0.00030525 | 22.6677 | 498376.0003 | 45928.7843
39049.4196 | 2077 | 1 | 39049.4196 | 0 | 0 |  | 2810.5 | 3046.5 | 126.801 | 0.06105 | 0.030525 | 0 | 1.268 | 0.0006105 | 0.00030525 | 0 | 1.2674 | 0.00030525 | 20.0087 | 498376.0003 | 41429.6871
39049.42 | 2278 | 1 | 39049.4201 | 0 | 0 |  | 2852.5 | 3088.5 | 139.072 | 0.06105 | 0.030525 | 0 | 1.3907 | 0.0006105 | 0.00030525 | 0 | 1.3901 | 0.00030525 | 9.415 | 498376.0003 | 21333.7194
39049.4205 | 1880 | 1 | 39049.4205 | 0 | 0 |  | 2894.5 | 3130.5 | 114.7741 | 0.06105 | 0.030525 | 0 | 1.1477 | 0.0006105 | 0.00030525 | 0 | 1.1471 | 0.00030525 | 32.5907 | 498376.0003 | 61125.735
39049.421 | 2476 | 1 | 39049.421 | 0 | 0 |  | 2936.5 | 3172.5 | 151.16 | 0.06105 | 0.030525 | 0 | 1.5116 | 0.0006105 | 0.00030525 | 0 | 1.511 | 0.00030525 | 0.66182 | 498376.0012 | 1537.6915
39049.4215 | 2464 | 1 | 39049.4215 | 0 | 0 |  | 2978.5 | 3214.5 | 150.4274 | 0.06105 | 0.030525 | 0 | 1.5043 | 0.0006105 | 0.00030525 | 0 | 1.5037 | 0.00030525 | 1.1523 | 498376.0003 | 2737.4507

## A2-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 151.5495 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39049.3845 | 0 | 0 | 39049.3845 | 0 | 0 |  | -215.5 | 20.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.385 | 0 | 0 | 39049.385 | 0 | 0 |  | -174 | 62 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3855 | 0 | 0 | 39049.3855 | 0 | 0 |  | -132 | 104 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.386 | 0 | 0 | 39049.386 | 0 | 0 |  | -89.5 | 146.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3865 | 0 | 0 | 39049.3865 | 0 | 0 |  | -48 | 188 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.387 | 0 | 0 | 39049.387 | 0 | 0 |  | -6 | 230 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3874 | 0 | 0 | 39049.3875 | 0 | 0 |  | 36 | 272 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3879 | 0 | 0 | 39049.388 | 0 | 0 |  | 78 | 314 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3884 | 0 | 0 | 39049.3884 | 0 | 0 |  | 120 | 356 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3889 | 0 | 0 | 39049.3889 | 0 | 0 |  | 162 | 398 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3894 | 0 | 0 | 39049.3894 | 0 | 0 |  | 204 | 440 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3899 | 0 | 0 | 39049.3899 | 0 | 0 |  | 246 | 482 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3904 | 0 | 0 | 39049.3904 | 0 | 0 |  | 288 | 524 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3908 | 0 | 0 | 39049.3909 | 0 | 0 |  | 330 | 566 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3913 | 0 | 0 | 39049.3914 | 0 | 0 |  | 372 | 608 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3918 | 0 | 0 | 39049.3918 | 0 | 0 |  | 414 | 650 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3923 | 0 | 0 | 39049.3923 | 0 | 0 |  | 456 | 692 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3928 | 0 | 0 | 39049.3928 | 0 | 0 |  | 498 | 734 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3933 | 0 | 0 | 39049.3933 | 0 | 0 |  | 540 | 776 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3938 | 0 | 0 | 39049.3938 | 0 | 0 |  | 582 | 818 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3942 | 0 | 0 | 39049.3943 | 0 | 0 |  | 624 | 860 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3947 | 0 | 0 | 39049.3948 | 0 | 0 |  | 666 | 902 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3952 | 0 | 0 | 39049.3952 | 0 | 0 |  | 708 | 944 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3957 | 0 | 0 | 39049.3957 | 0 | 0 |  | 750 | 986 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3962 | 0 | 0 | 39049.3962 | 0 | 0 |  | 792 | 1028 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3967 | 0 | 0 | 39049.3967 | 0 | 0 |  | 834 | 1070 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3972 | 0 | 0 | 39049.3972 | 0 | 0 |  | 876 | 1112 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3977 | 0 | 0 | 39049.3977 | 0 | 0 |  | 918 | 1154 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3981 | 0 | 0 | 39049.3982 | 0 | 0 |  | 960 | 1196 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3986 | 0 | 0 | 39049.3986 | 0 | 0 |  | 1002 | 1238 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3991 | 0 | 0 | 39049.3991 | 0 | 0 |  | 1044 | 1280 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.3996 | 0 | 0 | 39049.3996 | 0 | 0 |  | 1086 | 1322 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4001 | 0 | 0 | 39049.4001 | 0 | 0 |  | 1128 | 1364 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4006 | 0 | 0 | 39049.4006 | 0 | 0 |  | 1170 | 1406 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4011 | 0 | 0 | 39049.4011 | 0 | 0 |  | 1212 | 1448 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4015 | 0 | 0 | 39049.4016 | 0 | 0 |  | 1254 | 1490 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.402 | 0 | 0 | 39049.402 | 0 | 0 |  | 1296 | 1532 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4025 | 0 | 0 | 39049.4025 | 0 | 0 |  | 1338 | 1574 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.403 | 0 | 0 | 39049.403 | 0 | 0 |  | 1380 | 1616 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4035 | 0 | 0 | 39049.4035 | 0 | 0 |  | 1422 | 1658 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.404 | 0 | 0 | 39049.404 | 0 | 0 |  | 1464 | 1700 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4045 | 0 | 0 | 39049.4045 | 0 | 0 |  | 1506 | 1742 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4049 | 0 | 0 | 39049.405 | 0 | 0 |  | 1548 | 1784 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4054 | 0 | 0 | 39049.4055 | 0 | 0 |  | 1590 | 1826 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4059 | 0 | 0 | 39049.4059 | 0 | 0 |  | 1632 | 1868 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4064 | 0 | 0 | 39049.4064 | 0 | 0 |  | 1674 | 1910 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4069 | 0 | 0 | 39049.4069 | 0 | 0 |  | 1715.5 | 1951.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4074 | 0 | 0 | 39049.4074 | 0 | 0 |  | 1757.5 | 1993.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4079 | 0 | 0 | 39049.4079 | 0 | 0 |  | 1800 | 2036 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4083 | 0 | 0 | 39049.4084 | 0 | 0 |  | 1842 | 2078 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4088 | 0 | 0 | 39049.4088 | 0 | 0 |  | 1883.5 | 2119.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 496376 | 496376 | 496375.9997
39049.4093 | 802 | 1 | 39049.4093 | 1 | 0 |  | 1926 | 2162 | 48.9621 | 0.06105 | 0.06105 | 0 | 0.48962 | 0.0006105 | 0.0006105 | 0 | 0.48901 | 0.0006105 | 209.7854 | 248138.0001 | 167870.348
39049.4098 | 2208 | 1 | 39049.4098 | 1 | 0 |  | 1968 | 2204 | 134.7985 | 0.06105 | 0.06105 | 0 | 1.348 | 0.0006105 | 0.0006105 | 0 | 1.3474 | 0.0006105 | 12.4323 | 248137.9999 | 27326.9872
39049.4103 | 2184 | 1 | 39049.4103 | 1 | 0 |  | 2009.5 | 2245.5 | 133.3333 | 0.06105 | 0.06105 | 0 | 1.3333 | 0.0006105 | 0.0006105 | 0 | 1.3327 | 0.0006105 | 13.6683 | 248138.0002 | 29726.0204
39049.4108 | 1902 | 1 | 39049.4108 | 0 | 0 |  | 2052 | 2288 | 116.1172 | 0.06105 | 0.030525 | 0 | 1.1612 | 0.0006105 | 0.00030525 | 0 | 1.1606 | 0.00030525 | 30.5303 | 496376.001 | 57926.3302
39049.4113 | 2393 | 1 | 39049.4113 | 0 | 0 |  | 2093.5 | 2329.5 | 146.0928 | 0.06105 | 0.030525 | 0 | 1.4609 | 0.0006105 | 0.00030525 | 0 | 1.4603 | 0.00030525 | 3.7366 | 496376.0001 | 8836.2199
39049.4117 | 2048 | 1 | 39049.4118 | 1 | 0 |  | 2135.5 | 2371.5 | 125.0305 | 0.06105 | 0.06105 | 0 | 1.2503 | 0.0006105 | 0.0006105 | 0 | 1.2497 | 0.0006105 | 21.2203 | 248138.0002 | 43320.5418
39049.4122 | 2270 | 1 | 39049.4122 | 0 | 0 |  | 2177.5 | 2413.5 | 138.5836 | 0.06105 | 0.030525 | 0 | 1.3858 | 0.0006105 | 0.00030525 | 0 | 1.3852 | 0.00030525 | 9.3601 | 496376.0001 | 21133.7424
39049.4127 | 1973 | 1 | 39049.4127 | 0 | 0 |  | 2219.5 | 2455.5 | 120.4518 | 0.06105 | 0.030525 | 0 | 1.2045 | 0.0006105 | 0.00030525 | 0 | 1.2039 | 0.00030525 | 25.8306 | 496376.0001 | 50827.7602
39049.4132 | 2466 | 1 | 39049.4132 | 1 | 0 |  | 2261.5 | 2497.5 | 150.5495 | 0.06105 | 0.06105 | 0 | 1.5055 | 0.0006105 | 0.0006105 | 0 | 1.5049 | 0.0006105 | 0.6645 | 248138.0002 | 1537.3804
39049.4137 | 2198 | 1 | 39049.4137 | 0 | 0 |  | 2303.5 | 2539.5 | 134.188 | 0.06105 | 0.030525 | 0 | 1.3419 | 0.0006105 | 0.00030525 | 0 | 1.3413 | 0.00030525 | 12.944 | 496376.0001 | 28332.2922
39049.4142 | 1907 | 1 | 39049.4142 | 1 | 0 |  | 2345.5 | 2581.5 | 116.4225 | 0.06105 | 0.06105 | 0 | 1.1642 | 0.0006105 | 0.0006105 | 0 | 1.1636 | 0.0006105 | 30.1878 | 248137.9999 | 57414.8617
39049.4147 | 2136 | 1 | 39049.4147 | 0 | 0 |  | 2387.5 | 2623.5 | 130.4029 | 0.06105 | 0.030525 | 0 | 1.304 | 0.0006105 | 0.00030525 | 0 | 1.3034 | 0.00030525 | 16.2239 | 496376.0001 | 34531.0434
39049.4152 | 2308 | 1 | 39049.4152 | 0 | 0 |  | 2429.5 | 2665.5 | 140.9035 | 0.06105 | 0.030525 | 0 | 1.409 | 0.0006105 | 0.00030525 | 0 | 1.4084 | 0.00030525 | 7.5587 | 496376.0001 | 17334.5078
39049.4156 | 1838 | 1 | 39049.4156 | 0 | 0 |  | 2471.5 | 2707.5 | 112.21 | 0.06105 | 0.030525 | 0 | 1.1221 | 0.0006105 | 0.00030525 | 0 | 1.1215 | 0.00030525 | 35.0778 | 496376.001 | 64325.0411
39049.4161 | 1830 | 1 | 39049.4161 | 0 | 0 |  | 2513.5 | 2749.5 | 111.7216 | 0.06105 | 0.030525 | 0 | 1.1172 | 0.0006105 | 0.00030525 | 0 | 1.1166 | 0.00030525 | 35.6687 | 496376.0001 | 65124.8799
39049.4166 | 2078 | 1 | 39049.4166 | 0 | 0 |  | 2555.5 | 2791.5 | 126.862 | 0.06105 | 0.030525 | 0 | 1.2686 | 0.0006105 | 0.00030525 | 0 | 1.268 | 0.00030525 | 19.4694 | 496376.0001 | 40329.8751
39049.4171 | 2231 | 1 | 39049.4171 | 0 | 0 |  | 2597.5 | 2833.5 | 136.2027 | 0.06105 | 0.030525 | 0 | 1.362 | 0.0006105 | 0.00030525 | 0 | 1.3614 | 0.00030525 | 11.2726 | 496375.9992 | 25032.9569
39049.4176 | 1860 | 1 | 39049.4176 | 0 | 0 |  | 2639.5 | 2875.5 | 113.5531 | 0.06105 | 0.030525 | 0 | 1.1355 | 0.0006105 | 0.00030525 | 0 | 1.1349 | 0.00030525 | 33.4793 | 496376.0001 | 62125.4842
39049.4181 | 2362 | 1 | 39049.4181 | 0 | 0 |  | 2681.5 | 2917.5 | 144.2002 | 0.06105 | 0.030525 | 0 | 1.442 | 0.0006105 | 0.00030525 | 0 | 1.4414 | 0.00030525 | 5.0987 | 496376.0001 | 11935.5955
39049.4186 | 2047 | 1 | 39049.4186 | 1 | 0 |  | 2723.5 | 2959.5 | 124.9695 | 0.06105 | 0.06105 | 0 | 1.2497 | 0.0006105 | 0.0006105 | 0 | 1.2491 | 0.0006105 | 21.2796 | 248137.9999 | 43420.5015
39049.419 | 2051 | 1 | 39049.4191 | 1 | 0 |  | 2765.5 | 3001.5 | 125.2137 | 0.06105 | 0.06105 | 0 | 1.2521 | 0.0006105 | 0.0006105 | 0 | 1.2515 | 0.0006105 | 21.0429 | 248137.9999 | 43020.6626
39049.4195 | 2414 | 1 | 39049.4195 | 1 | 0 |  | 2807.5 | 3043.5 | 147.3748 | 0.06105 | 0.06105 | 0 | 1.4737 | 0.0006105 | 0.0006105 | 0 | 1.4731 | 0.0006105 | 2.8338 | 248137.9999 | 6735.2857
39049.42 | 2460 | 1 | 39049.42 | 0 | 0 |  | 2849.5 | 3085.5 | 150.1832 | 0.06105 | 0.030525 | 0 | 1.5018 | 0.0006105 | 0.00030525 | 0 | 1.5012 | 0.00030525 | 0.91013 | 496376.001 | 2137.5694
39049.4205 | 1882 | 1 | 39049.4205 | 0 | 0 |  | 2891.5 | 3127.5 | 114.8962 | 0.06105 | 0.030525 | 0 | 1.149 | 0.0006105 | 0.00030525 | 0 | 1.1484 | 0.00030525 | 31.9181 | 496375.9992 | 59925.9273
39049.421 | 2240 | 1 | 39049.421 | 0 | 0 |  | 2933.5 | 3169.5 | 136.7521 | 0.06105 | 0.030525 | 0 | 1.3675 | 0.0006105 | 0.00030525 | 0 | 1.3669 | 0.00030525 | 10.8254 | 496376.0001 | 24133.1381
39049.4215 | 1883 | 1 | 39049.4215 | 0 | 0 |  | 2975.5 | 3211.5 | 114.9573 | 0.06105 | 0.030525 | 0 | 1.1496 | 0.0006105 | 0.00030525 | 0 | 1.149 | 0.00030525 | 31.848 | 496376.0001 | 59825.9475

## A2-B4
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 152.9536 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39049.3845 | 0 | 0 | 39049.3845 | 0 | 0 |  | -218.5 | 17.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.385 | 0 | 0 | 39049.385 | 0 | 0 |  | -176.5 | 59.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3855 | 0 | 0 | 39049.3855 | 0 | 0 |  | -134.5 | 101.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.386 | 0 | 0 | 39049.386 | 0 | 0 |  | -92.5 | 143.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3864 | 0 | 0 | 39049.3865 | 0 | 0 |  | -50.5 | 185.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3869 | 0 | 0 | 39049.3869 | 0 | 0 |  | -8.5 | 227.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3874 | 0 | 0 | 39049.3874 | 0 | 0 |  | 33.5 | 269.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3879 | 0 | 0 | 39049.3879 | 0 | 0 |  | 75.5 | 311.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3884 | 0 | 0 | 39049.3884 | 0 | 0 |  | 117.5 | 353.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3889 | 0 | 0 | 39049.3889 | 0 | 0 |  | 159.5 | 395.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3894 | 0 | 0 | 39049.3894 | 0 | 0 |  | 201.5 | 437.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3898 | 0 | 0 | 39049.3899 | 0 | 0 |  | 243.5 | 479.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3903 | 0 | 0 | 39049.3903 | 0 | 0 |  | 285.5 | 521.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3908 | 0 | 0 | 39049.3908 | 0 | 0 |  | 327.5 | 563.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3913 | 0 | 0 | 39049.3913 | 0 | 0 |  | 369.5 | 605.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3918 | 0 | 0 | 39049.3918 | 0 | 0 |  | 411.5 | 647.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3923 | 0 | 0 | 39049.3923 | 0 | 0 |  | 453 | 689 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3928 | 0 | 0 | 39049.3928 | 0 | 0 |  | 495.5 | 731.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3933 | 0 | 0 | 39049.3933 | 0 | 0 |  | 537.5 | 773.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3937 | 0 | 0 | 39049.3938 | 0 | 0 |  | 579 | 815 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3942 | 0 | 0 | 39049.3942 | 0 | 0 |  | 621.5 | 857.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3947 | 0 | 0 | 39049.3947 | 0 | 0 |  | 663.5 | 899.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3952 | 0 | 0 | 39049.3952 | 0 | 0 |  | 705.5 | 941.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3957 | 0 | 0 | 39049.3957 | 0 | 0 |  | 747.5 | 983.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3962 | 0 | 0 | 39049.3962 | 0 | 0 |  | 789 | 1025 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3966 | 0 | 0 | 39049.3967 | 0 | 0 |  | 831 | 1067 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3971 | 0 | 0 | 39049.3972 | 0 | 0 |  | 873.5 | 1109.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3976 | 0 | 0 | 39049.3976 | 0 | 0 |  | 915.5 | 1151.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3981 | 0 | 0 | 39049.3981 | 0 | 0 |  | 957 | 1193 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3986 | 0 | 0 | 39049.3986 | 0 | 0 |  | 999 | 1235 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3991 | 0 | 0 | 39049.3991 | 0 | 0 |  | 1041.5 | 1277.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.3996 | 0 | 0 | 39049.3996 | 0 | 0 |  | 1083 | 1319 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4 | 0 | 0 | 39049.4001 | 0 | 0 |  | 1125 | 1361 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4005 | 0 | 0 | 39049.4006 | 0 | 0 |  | 1167 | 1403 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.401 | 0 | 0 | 39049.401 | 0 | 0 |  | 1209 | 1445 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4015 | 0 | 0 | 39049.4015 | 0 | 0 |  | 1251 | 1487 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.402 | 0 | 0 | 39049.402 | 0 | 0 |  | 1293 | 1529 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4025 | 0 | 0 | 39049.4025 | 0 | 0 |  | 1335 | 1571 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.403 | 0 | 0 | 39049.403 | 0 | 0 |  | 1377 | 1613 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4034 | 0 | 0 | 39049.4035 | 0 | 0 |  | 1419 | 1655 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4039 | 0 | 0 | 39049.404 | 0 | 0 |  | 1461 | 1697 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4044 | 0 | 0 | 39049.4044 | 0 | 0 |  | 1503 | 1739 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4049 | 0 | 0 | 39049.4049 | 0 | 0 |  | 1545 | 1781 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4054 | 0 | 0 | 39049.4054 | 0 | 0 |  | 1587 | 1823 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4059 | 0 | 0 | 39049.4059 | 0 | 0 |  | 1629 | 1865 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4064 | 0 | 0 | 39049.4064 | 0 | 0 |  | 1671 | 1907 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4069 | 0 | 0 | 39049.4069 | 0 | 0 |  | 1713 | 1949 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4073 | 0 | 0 | 39049.4074 | 0 | 0 |  | 1755 | 1991 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4078 | 0 | 0 | 39049.4078 | 0 | 0 |  | 1797 | 2033 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4083 | 0 | 0 | 39049.4083 | 0 | 0 |  | 1839 | 2075 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4088 | 0 | 0 | 39049.4088 | 0 | 0 |  | 1881 | 2117 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39049.4093 | 1966 | 0 | 39049.4093 | 485 | 0 |  | 1923 | 2159 | 120.0244 | 0 | 29.6093 | 0 | 1.2002 | 0 | 0.29609 | 0 | 1.2002 | 0.29609 | 27.4354 | 416.5732 | 26.2352
39049.4098 | 2452 | 0 | 39049.4098 | 2298 | 0 |  | 1965 | 2201 | 149.6947 | 0 | 140.293 | 0 | 1.4969 | 0 | 1.4029 | 0 | 1.4969 | 1.4029 | 2.177 | 9.0244 | 0.68005
39049.4103 | 2235 | 0 | 39049.4103 | 2056 | 0 |  | 2007 | 2243 | 136.4469 | 0 | 125.5189 | 0 | 1.3645 | 0 | 1.2552 | 0 | 1.3645 | 1.2552 | 12.0975 | 21.857 | 10.7331
39049.4107 | 2383 | 0 | 39049.4108 | 1975 | 0 |  | 2049 | 2285 | 145.4823 | 0 | 120.5739 | 0 | 1.4548 | 0 | 1.2057 | 0 | 1.4548 | 1.2057 | 5.1355 | 26.8547 | 3.6807
39049.4112 | 2212 | 0 | 39049.4112 | 1988 | 0 |  | 2091 | 2327 | 135.0427 | 0 | 121.3675 | 0 | 1.3504 | 0 | 1.2137 | 0 | 1.3504 | 1.2137 | 13.2631 | 26.0252 | 11.9127
39049.4117 | 2436 | 0 | 39049.4117 | 2489 | 0 |  | 2133 | 2369 | 148.7179 | 0 | 151.9536 | 0 | 1.4872 | 0 | 1.5195 | 0 | 1.4872 | 1.5195 | 2.8481 | 0.6581 | 1.3609
39049.4122 | 2416 | 0 | 39049.4122 | 2040 | 0 |  | 2175 | 2411 | 147.4969 | 0 | 124.5421 | 0 | 1.475 | 0 | 1.2454 | 0 | 1.475 | 1.2454 | 3.6995 | 22.8127 | 2.2245
39049.4127 | 2004 | 0 | 39049.4127 | 2177 | 0 |  | 2217 | 2453 | 122.3443 | 0 | 132.906 | 0 | 1.2234 | 0 | 1.3291 | 0 | 1.2234 | 1.3291 | 25.019 | 15.0841 | 23.7955
39049.4132 | 1897 | 0 | 39049.4132 | 1906 | 0 |  | 2259 | 2495 | 115.812 | 0 | 116.3614 | 0 | 1.1581 | 0 | 1.1636 | 0 | 1.1581 | 1.1636 | 32.0706 | 31.447 | 30.9125
39049.4137 | 1896 | 0 | 39049.4137 | 1918 | 0 |  | 2301 | 2537 | 115.7509 | 0 | 117.094 | 0 | 1.1575 | 0 | 1.1709 | 0 | 1.1575 | 1.1709 | 32.1403 | 30.6246 | 30.9828
39049.4141 | 2438 | 0 | 39049.4142 | 2340 | 0 |  | 2343 | 2579 | 148.84 | 0 | 142.8571 | 0 | 1.4884 | 0 | 1.4286 | 0 | 1.4884 | 1.4286 | 2.7637 | 7.0675 | 1.2753
39049.4146 | 2430 | 0 | 39049.4147 | 1900 | 0 |  | 2385 | 2621 | 148.3516 | 0 | 115.9951 | 0 | 1.4835 | 0 | 1.16 | 0 | 1.4835 | 1.16 | 3.1021 | 31.8621 | 1.6185
39049.4151 | 2153 | 1 | 39049.4151 | 1870 | 3 |  | 2427 | 2663 | 131.4408 | 0.06105 | 114.1636 | 0.18315 | 1.3144 | 0.0006105 | 1.1416 | 0.0018315 | 1.3138 | 1.1398 | 16.3967 | 34.3689 | 8987.613
39049.4156 | 2130 | 6 | 39049.4156 | 1801 | 6 |  | 2469 | 2705 | 130.0366 | 0.3663 | 109.9512 | 0.3663 | 1.3004 | 0.003663 | 1.0995 | 0.003663 | 1.2967 | 1.0958 | 17.799 | 39.9923 | 1758.7097
39049.4161 | 1851 | 5 | 39049.4161 | 2289 | 4 |  | 2511 | 2747 | 113.0037 | 0.30525 | 139.7436 | 0.2442 | 1.13 | 0.0030525 | 1.3974 | 0.002442 | 1.127 | 1.395 | 36.4872 | 9.5152 | 1128.4281
39049.4166 | 1876 | 4 | 39049.4166 | 2162 | 4 |  | 2553 | 2789 | 114.5299 | 0.2442 | 131.9902 | 0.2442 | 1.1453 | 0.002442 | 1.3199 | 0.002442 | 1.1429 | 1.3175 | 34.0758 | 15.999 | 2156.3645
39049.4171 | 2156 | 1 | 39049.4171 | 1863 | 0 |  | 2595 | 2831 | 131.6239 | 0.06105 | 113.7363 | 0 | 1.3162 | 0.0006105 | 1.1374 | 0 | 1.3156 | 1.1374 | 16.2344 | 34.4809 | 8932.4711
39049.4175 | 2232 | 0 | 39049.4176 | 2431 | 0 |  | 2637 | 2873 | 136.2637 | 0 | 148.4127 | 0 | 1.3626 | 0 | 1.4841 | 0 | 1.3626 | 1.4841 | 12.2482 | 3.0596 | 10.8856
39049.418 | 2207 | 0 | 39049.4181 | 2369 | 0 |  | 2679 | 2915 | 134.7375 | 0 | 144.6276 | 0 | 1.3474 | 0 | 1.4463 | 0 | 1.3474 | 1.4463 | 13.5197 | 5.7569 | 12.1723
39049.4185 | 2237 | 0 | 39049.4185 | 2228 | 0 |  | 2721 | 2957 | 136.569 | 0 | 136.0195 | 0 | 1.3657 | 0 | 1.3602 | 0 | 1.3657 | 1.3602 | 11.9973 | 12.4497 | 10.6316
39049.419 | 1925 | 0 | 39049.419 | 2172 | 0 |  | 2763 | 2999 | 117.5214 | 0 | 132.6007 | 0 | 1.1752 | 0 | 1.326 | 0 | 1.1752 | 1.326 | 30.1496 | 15.349 | 28.9744
39049.4195 | 2441 | 0 | 39049.4195 | 1965 | 0 |  | 2805 | 3041 | 149.0232 | 0 | 119.9634 | 0 | 1.4902 | 0 | 1.1996 | 0 | 1.4902 | 1.1996 | 2.6374 | 27.5003 | 1.1472
39049.42 | 1944 | 0 | 39049.42 | 2430 | 0 |  | 2847 | 3083 | 118.6813 | 0 | 148.3516 | 0 | 1.1868 | 0 | 1.4835 | 0 | 1.1868 | 1.4835 | 28.8776 | 3.1021 | 27.6908
39049.4205 | 2203 | 0 | 39049.4205 | 2318 | 0 |  | 2888.5 | 3124.5 | 134.4933 | 0 | 141.514 | 0 | 1.3449 | 0 | 1.4151 | 0 | 1.3449 | 1.4151 | 13.7258 | 8.0837 | 12.3809
39049.4209 | 2064 | 0 | 39049.421 | 1907 | 0 |  | 2930.5 | 3166.5 | 126.0073 | 0 | 116.4225 | 0 | 1.2601 | 0 | 1.1642 | 0 | 1.2601 | 1.1642 | 21.3847 | 31.3781 | 20.1246
39049.4214 | 2213 | 0 | 39049.4215 | 2243 | 0 |  | 2973 | 3209 | 135.1038 | 0 | 136.9353 | 0 | 1.351 | 0 | 1.3694 | 0 | 1.351 | 1.3694 | 13.2119 | 11.6977 | 11.8609

## A2-B3
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 155.3346 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39049.3845 | 0 | 0 | 39049.3845 | 0 | 0 |  | -221.5 | 14.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.385 | 0 | 0 | 39049.385 | 0 | 0 |  | -179.5 | 56.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3854 | 0 | 0 | 39049.3855 | 0 | 0 |  | -137.5 | 98.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3859 | 0 | 0 | 39049.3859 | 0 | 0 |  | -95.5 | 140.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3864 | 0 | 0 | 39049.3864 | 0 | 0 |  | -53.5 | 182.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3869 | 0 | 0 | 39049.3869 | 0 | 0 |  | -11.5 | 224.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3874 | 0 | 0 | 39049.3874 | 0 | 0 |  | 30.5 | 266.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3879 | 0 | 0 | 39049.3879 | 0 | 0 |  | 72.5 | 308.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3884 | 0 | 0 | 39049.3884 | 0 | 0 |  | 114.5 | 350.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3888 | 0 | 0 | 39049.3889 | 0 | 0 |  | 156.5 | 392.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3893 | 0 | 0 | 39049.3893 | 0 | 0 |  | 198.5 | 434.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3898 | 0 | 0 | 39049.3898 | 0 | 0 |  | 240.5 | 476.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3903 | 0 | 0 | 39049.3903 | 0 | 0 |  | 282.5 | 518.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3908 | 0 | 0 | 39049.3908 | 0 | 0 |  | 324.5 | 560.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3913 | 0 | 0 | 39049.3913 | 0 | 0 |  | 366.5 | 602.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3918 | 0 | 0 | 39049.3918 | 0 | 0 |  | 408.5 | 644.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3922 | 0 | 0 | 39049.3923 | 0 | 0 |  | 450.5 | 686.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3927 | 0 | 0 | 39049.3927 | 0 | 0 |  | 492.5 | 728.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3932 | 0 | 0 | 39049.3932 | 0 | 0 |  | 534.5 | 770.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3937 | 0 | 0 | 39049.3937 | 0 | 0 |  | 576.5 | 812.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3942 | 0 | 0 | 39049.3942 | 0 | 0 |  | 618.5 | 854.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3947 | 0 | 0 | 39049.3947 | 0 | 0 |  | 660.5 | 896.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3952 | 0 | 0 | 39049.3952 | 0 | 0 |  | 702.5 | 938.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3956 | 0 | 0 | 39049.3957 | 0 | 0 |  | 744.5 | 980.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3961 | 0 | 0 | 39049.3961 | 0 | 0 |  | 786.5 | 1022.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3966 | 0 | 0 | 39049.3966 | 0 | 0 |  | 828.5 | 1064.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3971 | 0 | 0 | 39049.3971 | 0 | 0 |  | 870.5 | 1106.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3976 | 0 | 0 | 39049.3976 | 0 | 0 |  | 912.5 | 1148.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3981 | 0 | 0 | 39049.3981 | 0 | 0 |  | 954.5 | 1190.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3986 | 0 | 0 | 39049.3986 | 0 | 0 |  | 996.5 | 1232.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3991 | 0 | 0 | 39049.3991 | 0 | 0 |  | 1038.5 | 1274.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.3995 | 0 | 0 | 39049.3995 | 0 | 0 |  | 1080.5 | 1316.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4 | 0 | 0 | 39049.4 | 0 | 0 |  | 1122.5 | 1358.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4005 | 0 | 0 | 39049.4005 | 0 | 0 |  | 1164.5 | 1400.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.401 | 0 | 0 | 39049.401 | 0 | 0 |  | 1206.5 | 1442.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4015 | 0 | 0 | 39049.4015 | 0 | 0 |  | 1248.5 | 1484.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.402 | 0 | 0 | 39049.402 | 0 | 0 |  | 1290.5 | 1526.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4025 | 0 | 0 | 39049.4025 | 0 | 0 |  | 1332.5 | 1568.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4029 | 0 | 0 | 39049.403 | 0 | 0 |  | 1374.5 | 1610.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4034 | 0 | 0 | 39049.4034 | 0 | 0 |  | 1416.5 | 1652.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4039 | 0 | 0 | 39049.4039 | 0 | 0 |  | 1458.5 | 1694.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4044 | 0 | 0 | 39049.4044 | 0 | 0 |  | 1500.5 | 1736.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4049 | 0 | 0 | 39049.4049 | 0 | 0 |  | 1542.5 | 1778.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4054 | 0 | 0 | 39049.4054 | 0 | 1 |  | 1584.5 | 1820.5 | 0.030525 | 0 | 0.030525 | 0.06105 | 0.00030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4059 | 0 | 0 | 39049.4059 | 0 | 0 |  | 1626.5 | 1862.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4063 | 0 | 0 | 39049.4064 | 0 | 0 |  | 1668.5 | 1904.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508776 | 508776 | 508775.9997
39049.4068 | 0 | 0 | 39049.4068 | 2135 | 2 |  | 1710 | 1946 | 0.030525 | 0 | 130.3419 | 0.1221 | 0.00030525 | 0 | 1.3034 | 0.001221 | 0.00030525 | 1.3022 | 508776 | 19.2865 | 508775.9997
39049.4073 | 0 | 0 | 39049.4073 | 2124 | 0 |  | 1752.5 | 1988.5 | 0.030525 | 0 | 129.6703 | 0 | 0.00030525 | 0 | 1.2967 | 0 | 0.00030525 | 1.2967 | 508776 | 19.7919 | 508775.9997
39049.4078 | 0 | 0 | 39049.4078 | 2210 | 0 |  | 1794.5 | 2030.5 | 0.030525 | 0 | 134.9206 | 0 | 0.00030525 | 0 | 1.3492 | 0 | 0.00030525 | 1.3492 | 508776 | 15.1303 | 508775.9997
39049.4083 | 0 | 0 | 39049.4083 | 2479 | 0 |  | 1836.5 | 2072.5 | 0.030525 | 0 | 151.3431 | 0 | 0.00030525 | 0 | 1.5134 | 0 | 0.00030525 | 1.5134 | 508776 | 2.6374 | 508775.9997
39049.4088 | 0 | 0 | 39049.4088 | 2421 | 0 |  | 1878 | 2114 | 0.030525 | 0 | 147.8022 | 0 | 0.00030525 | 0 | 1.478 | 0 | 0.00030525 | 1.478 | 508776 | 5.0962 | 508775.9997
39049.4093 | 297 | 1 | 39049.4093 | 2528 | 0 |  | 1920.5 | 2156.5 | 18.1319 | 0.06105 | 154.3346 | 0 | 0.18132 | 0.0006105 | 1.5433 | 0 | 0.18071 | 1.5433 | 1586.3996 | 0.64794 | 1446.156
39049.4097 | 2211 | 1 | 39049.4098 | 2209 | 0 |  | 1962.5 | 2198.5 | 134.9817 | 0.06105 | 134.8596 | 0 | 1.3498 | 0.0006105 | 1.3486 | 0 | 1.3492 | 1.3486 | 15.1302 | 15.1824 | 4381.1697
39049.4102 | 1956 | 1 | 39049.4102 | 2241 | 0 |  | 2004 | 2240 | 119.4139 | 0.06105 | 136.8132 | 0 | 1.1941 | 0.0006105 | 1.3681 | 0 | 1.1935 | 1.3681 | 30.2103 | 13.5377 | 7003.6451
39049.4107 | 2129 | 1 | 39049.4107 | 2477 | 0 |  | 2046 | 2282 | 129.9756 | 0.06105 | 151.221 | 0 | 1.2998 | 0.0006105 | 1.5122 | 0 | 1.2991 | 1.5122 | 19.8629 | 2.7202 | 1097.3567
39049.4112 | 2354 | 1 | 39049.4112 | 2294 | 0 |  | 2088 | 2324 | 143.7118 | 0.06105 | 140.0488 | 0 | 1.4371 | 0.0006105 | 1.4005 | 0 | 1.4365 | 1.4005 | 8.1226 | 10.9146 | 1863.596
39049.4117 | 2024 | 1 | 39049.4117 | 2434 | 0 |  | 2130 | 2366 | 123.5653 | 0.06105 | 148.5958 | 0 | 1.2357 | 0.0006105 | 1.486 | 0 | 1.235 | 1.486 | 26.0067 | 4.5349 | 2253.1683
39049.4122 | 2172 | 1 | 39049.4122 | 2114 | 0 |  | 2172 | 2408 | 132.6007 | 0.06105 | 129.0598 | 0 | 1.326 | 0.0006105 | 1.2906 | 0 | 1.3254 | 1.2906 | 17.1914 | 20.3586 | 6281.8653
39049.4127 | 2101 | 1 | 39049.4127 | 2469 | 0 |  | 2214 | 2450 | 128.2662 | 0.06105 | 150.7326 | 0 | 1.2827 | 0.0006105 | 1.5073 | 0 | 1.2821 | 1.5073 | 21.4479 | 3.0531 | 1310.5984
39049.4131 | 2211 | 1 | 39049.4132 | 2097 | 0 |  | 2256 | 2492 | 134.9817 | 0.06105 | 128.022 | 0 | 1.3498 | 0.0006105 | 1.2802 | 0 | 1.3492 | 1.2802 | 15.1171 | 21.3343 | 5844.2593
39049.4136 | 1898 | 1 | 39049.4136 | 2297 | 0 |  | 2298 | 2534 | 115.873 | 0.06105 | 140.232 | 0 | 1.1587 | 0.0006105 | 1.4023 | 0 | 1.1581 | 1.4023 | 34.2414 | 10.7697 | 6274.7744
39049.4141 | 1885 | 1 | 39049.4141 | 2136 | 0 |  | 2340 | 2576 | 115.0794 | 0.06105 | 130.4029 | 0 | 1.1508 | 0.0006105 | 1.304 | 0 | 1.1502 | 1.304 | 35.0964 | 19.1189 | 10567.1804
39049.4146 | 2119 | 1 | 39049.4146 | 2030 | 0 |  | 2382 | 2618 | 129.3651 | 0.06105 | 123.9316 | 0 | 1.2937 | 0.0006105 | 1.2393 | 0 | 1.293 | 1.2393 | 20.1215 | 25.3389 | 8579.4018
39049.4151 | 2372 | 3 | 39049.4151 | 2220 | 2 |  | 2424 | 2660 | 144.8107 | 0.18315 | 135.5311 | 0.1221 | 1.4481 | 0.0018315 | 1.3553 | 0.001221 | 1.4463 | 1.3541 | 7.3393 | 14.8068 | 728.1731
39049.4156 | 1906 | 11 | 39049.4156 | 1895 | 6 |  | 2466 | 2702 | 116.3614 | 0.67155 | 115.6899 | 0.3663 | 1.1636 | 0.0067155 | 1.1569 | 0.003663 | 1.1569 | 1.1532 | 34.2607 | 34.6986 | 1469.2203
39049.4161 | 1856 | 4 | 39049.4161 | 2419 | 4 |  | 2508 | 2744 | 113.3089 | 0.2442 | 147.6801 | 0.2442 | 1.1331 | 0.002442 | 1.4768 | 0.002442 | 1.1306 | 1.4744 | 38.7758 | 5.214 | 847.8793
39049.4165 | 2027 | 1 | 39049.4166 | 1962 | 6 |  | 2550 | 2786 | 123.7485 | 0.06105 | 119.7802 | 0.3663 | 1.2375 | 0.0006105 | 1.1978 | 0.003663 | 1.2369 | 1.1941 | 25.5789 | 30.1354 | 11957.796
39049.417 | 2362 | 1 | 39049.417 | 1901 | 0 |  | 2592 | 2828 | 144.2002 | 0.06105 | 116.0562 | 0 | 1.442 | 0.0006105 | 1.1606 | 0 | 1.4414 | 1.1606 | 7.7344 | 33.8443 | 4586.4322
39049.4175 | 1957 | 1 | 39049.4175 | 2257 | 0 |  | 2634 | 2870 | 119.475 | 0.06105 | 137.79 | 0 | 1.1947 | 0.0006105 | 1.3779 | 0 | 1.1941 | 1.3779 | 30.1507 | 12.7328 | 6622.9842
39049.418 | 2180 | 1 | 39049.418 | 2061 | 1 |  | 2676 | 2912 | 133.0891 | 0.06105 | 125.8242 | 0.06105 | 1.3309 | 0.0006105 | 1.2582 | 0.0006105 | 1.3303 | 1.2576 | 16.755 | 23.5332 | 6922.4331
39049.4185 | 2044 | 1 | 39049.4185 | 1972 | 0 |  | 2718 | 2954 | 124.7863 | 0.06105 | 120.3907 | 0 | 1.2479 | 0.0006105 | 1.2039 | 0 | 1.2473 | 1.2039 | 24.5338 | 29.0254 | 11233.9794
39049.419 | 2429 | 1 | 39049.419 | 2358 | 0 |  | 2760 | 2996 | 148.2906 | 0.06105 | 143.956 | 0 | 1.4829 | 0.0006105 | 1.4396 | 0 | 1.4823 | 1.4396 | 4.777 | 7.9042 | 837.8522
39049.4195 | 2273 | 1 | 39049.4195 | 2237 | 0 |  | 2802 | 3038 | 138.7668 | 0.06105 | 136.569 | 0 | 1.3877 | 0.0006105 | 1.3657 | 0 | 1.3871 | 1.3657 | 11.9829 | 13.7407 | 3266.3912
39049.4199 | 2331 | 1 | 39049.42 | 1991 | 0 |  | 2844 | 3080 | 142.3077 | 0.06105 | 121.5507 | 0 | 1.4231 | 0.0006105 | 1.2155 | 0 | 1.4225 | 1.2155 | 9.1721 | 27.7941 | 4619.0759
39049.4204 | 2066 | 1 | 39049.4205 | 2037 | 0 |  | 2886 | 3122 | 126.1294 | 0.06105 | 124.359 | 0 | 1.2613 | 0.0006105 | 1.2436 | 0 | 1.2607 | 1.2436 | 23.2112 | 24.9082 | 9519.5318
39049.4209 | 2325 | 1 | 39049.4209 | 2524 | 0 |  | 2928 | 3164 | 141.9414 | 0.06105 | 154.0904 | 0 | 1.4194 | 0.0006105 | 1.5409 | 0 | 1.4188 | 1.5409 | 9.9711 | 0.80745 | 174.9182
39049.4214 | 2294 | 1 | 39049.4214 | 2159 | 0 |  | 2970 | 3206 | 140.0488 | 0.06105 | 131.8071 | 0 | 1.4005 | 0.0006105 | 1.3181 | 0 | 1.3999 | 1.3181 | 10.9461 | 17.8499 | 3777.1899

## A1-C6
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 150.9389 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39049.3844 | 0 | 0 | 39049.3845 | 0 | 0 |  | -224 | 12 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3849 | 0 | 0 | 39049.3849 | 0 | 0 |  | -182.5 | 53.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3854 | 0 | 0 | 39049.3854 | 0 | 0 |  | -140.5 | 95.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3859 | 0 | 0 | 39049.3859 | 0 | 0 |  | -98.5 | 137.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3864 | 0 | 0 | 39049.3864 | 0 | 0 |  | -56.5 | 179.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3869 | 0 | 0 | 39049.3869 | 0 | 0 |  | -14.5 | 221.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3873 | 0 | 0 | 39049.3874 | 0 | 0 |  | 27.5 | 263.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3878 | 0 | 0 | 39049.3878 | 0 | 0 |  | 69.5 | 305.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3883 | 0 | 0 | 39049.3883 | 0 | 0 |  | 111.5 | 347.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3888 | 0 | 0 | 39049.3888 | 0 | 0 |  | 153.5 | 389.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3893 | 0 | 0 | 39049.3893 | 0 | 0 |  | 195.5 | 431.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3898 | 0 | 0 | 39049.3898 | 0 | 0 |  | 237.5 | 473.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3903 | 0 | 0 | 39049.3903 | 0 | 0 |  | 279.5 | 515.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3908 | 0 | 0 | 39049.3908 | 0 | 0 |  | 321.5 | 557.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3912 | 0 | 0 | 39049.3913 | 0 | 0 |  | 363.5 | 599.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3917 | 0 | 0 | 39049.3917 | 0 | 0 |  | 405.5 | 641.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3922 | 0 | 0 | 39049.3922 | 0 | 0 |  | 447.5 | 683.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3927 | 0 | 0 | 39049.3927 | 0 | 0 |  | 489.5 | 725.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3932 | 0 | 0 | 39049.3932 | 0 | 0 |  | 531.5 | 767.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3937 | 0 | 0 | 39049.3937 | 0 | 0 |  | 573.5 | 809.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3942 | 0 | 0 | 39049.3942 | 0 | 0 |  | 615.5 | 851.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3946 | 0 | 0 | 39049.3947 | 0 | 0 |  | 657.5 | 893.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3951 | 0 | 0 | 39049.3951 | 0 | 0 |  | 699.5 | 935.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3956 | 0 | 0 | 39049.3956 | 0 | 0 |  | 741.5 | 977.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3961 | 0 | 0 | 39049.3961 | 0 | 0 |  | 783.5 | 1019.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3966 | 0 | 0 | 39049.3966 | 0 | 0 |  | 825.5 | 1061.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3971 | 0 | 0 | 39049.3971 | 0 | 0 |  | 867.5 | 1103.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3976 | 0 | 0 | 39049.3976 | 0 | 0 |  | 909.5 | 1145.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.398 | 0 | 0 | 39049.3981 | 0 | 0 |  | 951.5 | 1187.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3985 | 0 | 0 | 39049.3985 | 0 | 0 |  | 993.5 | 1229.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.399 | 0 | 0 | 39049.399 | 0 | 0 |  | 1035.5 | 1271.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.3995 | 0 | 0 | 39049.3995 | 0 | 0 |  | 1077.5 | 1313.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4 | 0 | 0 | 39049.4 | 0 | 0 |  | 1119.5 | 1355.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4005 | 0 | 0 | 39049.4005 | 0 | 0 |  | 1161.5 | 1397.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.401 | 0 | 0 | 39049.401 | 0 | 0 |  | 1203.5 | 1439.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4014 | 0 | 0 | 39049.4015 | 0 | 0 |  | 1245.5 | 1481.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4019 | 0 | 0 | 39049.4019 | 0 | 0 |  | 1287.5 | 1523.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4024 | 0 | 0 | 39049.4024 | 0 | 0 |  | 1329.5 | 1565.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4029 | 0 | 1 | 39049.4029 | 0 | 0 |  | 1371.5 | 1607.5 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494576.0809 | 494376 | 247038.0303
39049.4034 | 0 | 0 | 39049.4034 | 0 | 0 |  | 1413.5 | 1649.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4039 | 0 | 0 | 39049.4039 | 0 | 0 |  | 1455.5 | 1691.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4044 | 0 | 0 | 39049.4044 | 0 | 0 |  | 1497.5 | 1733.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4048 | 0 | 0 | 39049.4049 | 0 | 0 |  | 1539.5 | 1775.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4053 | 0 | 0 | 39049.4053 | 0 | 0 |  | 1581.5 | 1817.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4058 | 0 | 0 | 39049.4058 | 0 | 0 |  | 1623.5 | 1859.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4063 | 0 | 0 | 39049.4063 | 0 | 0 |  | 1665.5 | 1901.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4068 | 0 | 0 | 39049.4068 | 0 | 0 |  | 1707.5 | 1943.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4073 | 0 | 0 | 39049.4073 | 0 | 0 |  | 1749.5 | 1985.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4078 | 0 | 0 | 39049.4078 | 0 | 0 |  | 1791.5 | 2027.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4083 | 0 | 0 | 39049.4083 | 0 | 0 |  | 1833.5 | 2069.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4087 | 0 | 0 | 39049.4088 | 0 | 0 |  | 1875.5 | 2111.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 494376 | 494376 | 494375.9997
39049.4092 | 2235 | 1 | 39049.4092 | 0 | 0 |  | 1917.5 | 2153.5 | 136.4469 | 0.06105 | 0.030525 | 0 | 1.3645 | 0.0006105 | 0.00030525 | 0 | 1.3639 | 0.00030525 | 10.6258 | 494376.0009 | 23633.2196
39049.4097 | 2454 | 1 | 39049.4097 | 0 | 0 |  | 1959.5 | 2195.5 | 149.8168 | 0.06105 | 0.030525 | 0 | 1.4982 | 0.0006105 | 0.00030525 | 0 | 1.4976 | 0.00030525 | 0.74929 | 494376 | 1737.6485
39049.4102 | 2161 | 1 | 39049.4102 | 0 | 0 |  | 2001.5 | 2237.5 | 131.9292 | 0.06105 | 0.030525 | 0 | 1.3193 | 0.0006105 | 0.00030525 | 0 | 1.3187 | 0.00030525 | 14.4157 | 494375.9991 | 31031.7231
39049.4107 | 2369 | 1 | 39049.4107 | 0 | 0 |  | 2043.5 | 2279.5 | 144.6276 | 0.06105 | 0.030525 | 0 | 1.4463 | 0.0006105 | 0.00030525 | 0 | 1.4457 | 0.00030525 | 4.3657 | 494376 | 10235.9295
39049.4112 | 2082 | 1 | 39049.4112 | 0 | 0 |  | 2085.5 | 2321.5 | 127.1062 | 0.06105 | 0.030525 | 0 | 1.2711 | 0.0006105 | 0.00030525 | 0 | 1.2705 | 0.00030525 | 18.7593 | 494376 | 38930.1254
39049.4117 | 1973 | 1 | 39049.4117 | 0 | 0 |  | 2127.5 | 2363.5 | 120.4518 | 0.06105 | 0.030525 | 0 | 1.2045 | 0.0006105 | 0.00030525 | 0 | 1.2039 | 0.00030525 | 25.3235 | 494376.0009 | 49827.921
39049.4121 | 2164 | 1 | 39049.4122 | 0 | 0 |  | 2169.5 | 2405.5 | 132.1123 | 0.06105 | 0.030525 | 0 | 1.3211 | 0.0006105 | 0.00030525 | 0 | 1.3205 | 0.00030525 | 14.2571 | 494376 | 30731.7837
39049.4126 | 2208 | 1 | 39049.4126 | 0 | 0 |  | 2211.5 | 2447.5 | 134.7985 | 0.06105 | 0.030525 | 0 | 1.348 | 0.0006105 | 0.00030525 | 0 | 1.3474 | 0.00030525 | 11.9792 | 494376.0009 | 26332.6736
39049.4131 | 2308 | 1 | 39049.4131 | 0 | 0 |  | 2253.5 | 2489.5 | 140.9035 | 0.06105 | 0.030525 | 0 | 1.409 | 0.0006105 | 0.00030525 | 0 | 1.4084 | 0.00030525 | 7.1253 | 494376 | 16334.6959
39049.4136 | 2151 | 1 | 39049.4136 | 0 | 0 |  | 2295.5 | 2531.5 | 131.3187 | 0.06105 | 0.030525 | 0 | 1.3132 | 0.0006105 | 0.00030525 | 0 | 1.3126 | 0.00030525 | 14.9479 | 494376 | 32031.5208
39049.4141 | 1954 | 1 | 39049.4141 | 0 | 0 |  | 2337.5 | 2573.5 | 119.2918 | 0.06105 | 0.030525 | 0 | 1.1929 | 0.0006105 | 0.00030525 | 0 | 1.1923 | 0.00030525 | 26.5428 | 494376 | 51727.5368
39049.4146 | 2456 | 1 | 39049.4146 | 0 | 0 |  | 2379.5 | 2615.5 | 149.9389 | 0.06105 | 0.030525 | 0 | 1.4994 | 0.0006105 | 0.00030525 | 0 | 1.4988 | 0.00030525 | 0.66721 | 494376 | 1537.689
39049.4151 | 2230 | 1 | 39049.4151 | 0 | 0 |  | 2421.5 | 2657.5 | 136.1416 | 0.06105 | 0.030525 | 0 | 1.3614 | 0.0006105 | 0.00030525 | 0 | 1.3608 | 0.00030525 | 10.8739 | 494376 | 24133.1185
39049.4155 | 1946 | 1 | 39049.4156 | 0 | 0 |  | 2463.5 | 2699.5 | 118.8034 | 0.06105 | 0.030525 | 0 | 1.188 | 0.0006105 | 0.00030525 | 0 | 1.1874 | 0.00030525 | 27.0632 | 494376 | 52527.375
39049.416 | 2231 | 1 | 39049.416 | 0 | 0 |  | 2505.5 | 2741.5 | 136.2027 | 0.06105 | 0.030525 | 0 | 1.362 | 0.0006105 | 0.00030525 | 0 | 1.3614 | 0.00030525 | 10.8242 | 494376 | 24033.1387
39049.4165 | 2337 | 1 | 39049.4165 | 0 | 0 |  | 2547.5 | 2783.5 | 142.674 | 0.06105 | 0.030525 | 0 | 1.4267 | 0.0006105 | 0.00030525 | 0 | 1.4261 | 0.00030525 | 5.7954 | 494376 | 13435.2824
39049.417 | 2429 | 1 | 39049.417 | 0 | 0 |  | 2589.5 | 2825.5 | 148.2906 | 0.06105 | 0.030525 | 0 | 1.4829 | 0.0006105 | 0.00030525 | 0 | 1.4823 | 0.00030525 | 1.7867 | 494376.0009 | 4237.1429
39049.4175 | 1859 | 1 | 39049.4175 | 0 | 0 |  | 2631.5 | 2867.5 | 113.4921 | 0.06105 | 0.030525 | 0 | 1.1349 | 0.0006105 | 0.00030525 | 0 | 1.1343 | 0.00030525 | 33.0129 | 494376 | 61225.6156
39049.418 | 2317 | 1 | 39049.418 | 0 | 0 |  | 2673.5 | 2909.5 | 141.453 | 0.06105 | 0.030525 | 0 | 1.4145 | 0.0006105 | 0.00030525 | 0 | 1.4139 | 0.00030525 | 6.709 | 494376 | 15434.8779
39049.4185 | 2407 | 1 | 39049.4185 | 0 | 0 |  | 2715.5 | 2951.5 | 146.9475 | 0.06105 | 0.030525 | 0 | 1.4695 | 0.0006105 | 0.00030525 | 0 | 1.4689 | 0.00030525 | 2.7174 | 494375.9991 | 6436.698
39049.4189 | 2371 | 1 | 39049.419 | 0 | 0 |  | 2757.5 | 2993.5 | 144.7497 | 0.06105 | 0.030525 | 0 | 1.4475 | 0.0006105 | 0.00030525 | 0 | 1.4469 | 0.00030525 | 4.2776 | 494376 | 10035.97
39049.4194 | 2382 | 1 | 39049.4194 | 0 | 0 |  | 2799.5 | 3035.5 | 145.4212 | 0.06105 | 0.030525 | 0 | 1.4542 | 0.0006105 | 0.00030525 | 0 | 1.4536 | 0.00030525 | 3.7959 | 494376.0009 | 8936.1924
39049.4199 | 2282 | 1 | 39049.4199 | 0 | 0 |  | 2841 | 3077 | 139.3162 | 0.06105 | 0.030525 | 0 | 1.3932 | 0.0006105 | 0.00030525 | 0 | 1.3926 | 0.00030525 | 8.3463 | 494376 | 18934.1701
39049.4204 | 2215 | 1 | 39049.4204 | 0 | 0 |  | 2883 | 3119 | 135.2259 | 0.06105 | 0.030525 | 0 | 1.3523 | 0.0006105 | 0.00030525 | 0 | 1.3516 | 0.00030525 | 11.6251 | 494376 | 25632.8151
39049.4209 | 1923 | 1 | 39049.4209 | 0 | 0 |  | 2925 | 3161 | 117.3993 | 0.06105 | 0.030525 | 0 | 1.174 | 0.0006105 | 0.00030525 | 0 | 1.1734 | 0.00030525 | 28.5838 | 494376.0009 | 54826.9099
39049.4214 | 1948 | 1 | 39049.4214 | 0 | 0 |  | 2967.5 | 3203.5 | 118.9255 | 0.06105 | 0.030525 | 0 | 1.1893 | 0.0006105 | 0.00030525 | 0 | 1.1886 | 0.00030525 | 26.9327 | 494376 | 52327.4155

## A1-C5
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 153.0757 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39049.3844 | 0 | 0 | 39049.3844 | 0 | 0 |  | -227 | 9 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3849 | 0 | 0 | 39049.3849 | 0 | 0 |  | -185 | 51 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3854 | 0 | 0 | 39049.3854 | 0 | 0 |  | -143 | 93 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3859 | 0 | 0 | 39049.3859 | 0 | 0 |  | -101 | 135 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3863 | 0 | 0 | 39049.3864 | 0 | 0 |  | -59 | 177 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3868 | 0 | 0 | 39049.3869 | 0 | 0 |  | -17 | 219 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3873 | 0 | 0 | 39049.3873 | 0 | 0 |  | 25 | 261 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3878 | 0 | 0 | 39049.3878 | 0 | 0 |  | 67 | 303 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3883 | 0 | 0 | 39049.3883 | 0 | 0 |  | 109 | 345 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3888 | 0 | 0 | 39049.3888 | 0 | 0 |  | 151 | 387 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3893 | 0 | 0 | 39049.3893 | 0 | 0 |  | 193 | 429 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3897 | 0 | 0 | 39049.3898 | 0 | 0 |  | 235 | 471 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3902 | 0 | 0 | 39049.3903 | 0 | 0 |  | 277 | 513 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3907 | 0 | 0 | 39049.3907 | 0 | 0 |  | 319 | 555 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3912 | 0 | 0 | 39049.3912 | 0 | 0 |  | 361 | 597 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3917 | 0 | 0 | 39049.3917 | 0 | 0 |  | 403 | 639 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3922 | 0 | 0 | 39049.3922 | 0 | 0 |  | 444.5 | 680.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3927 | 0 | 0 | 39049.3927 | 0 | 0 |  | 487 | 723 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3931 | 0 | 0 | 39049.3932 | 0 | 0 |  | 529 | 765 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3936 | 0 | 0 | 39049.3937 | 0 | 0 |  | 571 | 807 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3941 | 0 | 0 | 39049.3941 | 0 | 0 |  | 612.5 | 848.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3946 | 0 | 0 | 39049.3946 | 0 | 0 |  | 655 | 891 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3951 | 0 | 0 | 39049.3951 | 0 | 0 |  | 697 | 933 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3956 | 0 | 0 | 39049.3956 | 0 | 0 |  | 738.5 | 974.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3961 | 0 | 0 | 39049.3961 | 0 | 0 |  | 780.5 | 1016.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3966 | 0 | 0 | 39049.3966 | 0 | 0 |  | 822.5 | 1058.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.397 | 0 | 0 | 39049.3971 | 0 | 0 |  | 865 | 1101 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3975 | 0 | 0 | 39049.3975 | 0 | 0 |  | 906.5 | 1142.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.398 | 0 | 0 | 39049.398 | 0 | 0 |  | 948.5 | 1184.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3985 | 0 | 0 | 39049.3985 | 0 | 0 |  | 990.5 | 1226.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.399 | 0 | 0 | 39049.399 | 0 | 0 |  | 1032.5 | 1268.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.3995 | 0 | 0 | 39049.3995 | 0 | 0 |  | 1074.5 | 1310.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4 | 0 | 0 | 39049.4 | 0 | 0 |  | 1116.5 | 1352.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4004 | 0 | 0 | 39049.4005 | 0 | 0 |  | 1158.5 | 1394.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4009 | 0 | 0 | 39049.4009 | 0 | 0 |  | 1200.5 | 1436.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4014 | 0 | 1 | 39049.4014 | 0 | 0 |  | 1242.5 | 1478.5 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501576.0798 | 501376 | 250538.0299
39049.4019 | 0 | 0 | 39049.4019 | 0 | 0 |  | 1284.5 | 1520.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4024 | 0 | 0 | 39049.4024 | 0 | 0 |  | 1326.5 | 1562.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4029 | 0 | 0 | 39049.4029 | 0 | 0 |  | 1368.5 | 1604.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4034 | 0 | 0 | 39049.4034 | 0 | 0 |  | 1410.5 | 1646.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4038 | 0 | 0 | 39049.4039 | 0 | 0 |  | 1452.5 | 1688.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4043 | 0 | 0 | 39049.4043 | 0 | 0 |  | 1494.5 | 1730.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4048 | 0 | 0 | 39049.4048 | 0 | 0 |  | 1536.5 | 1772.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4053 | 0 | 0 | 39049.4053 | 0 | 0 |  | 1578.5 | 1814.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4058 | 0 | 0 | 39049.4058 | 0 | 0 |  | 1620.5 | 1856.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4063 | 0 | 0 | 39049.4063 | 0 | 0 |  | 1662.5 | 1898.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4068 | 0 | 0 | 39049.4068 | 0 | 0 |  | 1704.5 | 1940.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4072 | 0 | 1 | 39049.4073 | 0 | 0 |  | 1746.5 | 1982.5 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501576.0798 | 501376 | 250538.0299
39049.4077 | 0 | 0 | 39049.4077 | 0 | 0 |  | 1788.5 | 2024.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4082 | 0 | 0 | 39049.4082 | 0 | 1 |  | 1830.5 | 2066.5 | 0.030525 | 0 | 0.030525 | 0.06105 | 0.00030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0.00030525 | 501376 | 501376 | 501375.9997
39049.4087 | 1 | 0 | 39049.4087 | 0 | 0 |  | 1872.5 | 2108.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 250638 | 501376 | 250637.9994
39049.4092 | 1235 | 1 | 39049.4092 | 0 | 0 |  | 1914.5 | 2150.5 | 75.3968 | 0.06105 | 0.030525 | 0 | 0.75397 | 0.0006105 | 0.00030525 | 0 | 0.75336 | 0.00030525 | 103.1102 | 501376.0001 | 127112.6472
39049.4097 | 2309 | 1 | 39049.4097 | 1 | 0 |  | 1956.5 | 2192.5 | 140.9646 | 0.06105 | 0.06105 | 0 | 1.4096 | 0.0006105 | 0.0006105 | 0 | 1.409 | 0.0006105 | 8.5953 | 250638.0003 | 19730.128
39049.4102 | 1972 | 1 | 39049.4102 | 0 | 0 |  | 1998.5 | 2234.5 | 120.3907 | 0.06105 | 0.030525 | 0 | 1.2039 | 0.0006105 | 0.00030525 | 0 | 1.2033 | 0.00030525 | 27.1629 | 501376.001 | 53427.3439
39049.4106 | 2438 | 1 | 39049.4107 | 0 | 0 |  | 2040.5 | 2276.5 | 148.84 | 0.06105 | 0.030525 | 0 | 1.4884 | 0.0006105 | 0.00030525 | 0 | 1.4878 | 0.00030525 | 2.8469 | 501376.0001 | 6836.6364
39049.4111 | 1976 | 1 | 39049.4111 | 1 | 0 |  | 2082.5 | 2318.5 | 120.6349 | 0.06105 | 0.06105 | 0 | 1.2063 | 0.0006105 | 0.0006105 | 0 | 1.2057 | 0.0006105 | 26.9053 | 250638 | 53016.8472
39049.4116 | 2348 | 1 | 39049.4116 | 0 | 0 |  | 2124.5 | 2360.5 | 143.3455 | 0.06105 | 0.030525 | 0 | 1.4335 | 0.0006105 | 0.00030525 | 0 | 1.4328 | 0.00030525 | 6.7908 | 501376.001 | 15834.8417
39049.4121 | 2359 | 1 | 39049.4121 | 0 | 0 |  | 2166.5 | 2402.5 | 144.0171 | 0.06105 | 0.030525 | 0 | 1.4402 | 0.0006105 | 0.00030525 | 0 | 1.4396 | 0.00030525 | 6.2926 | 501376.0001 | 14735.0611
39049.4126 | 2491 | 1 | 39049.4126 | 0 | 0 |  | 2208.5 | 2444.5 | 152.0757 | 0.06105 | 0.030525 | 0 | 1.5208 | 0.0006105 | 0.00030525 | 0 | 1.5201 | 0.00030525 | 0.65783 | 501376.0001 | 1537.6933
39049.4131 | 2423 | 1 | 39049.4131 | 0 | 0 |  | 2250.5 | 2486.5 | 147.9243 | 0.06105 | 0.030525 | 0 | 1.4792 | 0.0006105 | 0.00030525 | 0 | 1.4786 | 0.00030525 | 3.4839 | 501376.0001 | 8336.3373
39049.4136 | 2476 | 1 | 39049.4136 | 0 | 0 |  | 2292.5 | 2528.5 | 151.16 | 0.06105 | 0.030525 | 0 | 1.5116 | 0.0006105 | 0.00030525 | 0 | 1.511 | 0.00030525 | 1.2679 | 501376.0001 | 3037.3942
39049.4141 | 2403 | 1 | 39049.4141 | 1 | 0 |  | 2334.5 | 2570.5 | 146.7033 | 0.06105 | 0.06105 | 0 | 1.467 | 0.0006105 | 0.0006105 | 0 | 1.4664 | 0.0006105 | 4.3455 | 250637.9998 | 10333.877
39049.4145 | 2005 | 1 | 39049.4145 | 0 | 0 |  | 2376.5 | 2612.5 | 122.4054 | 0.06105 | 0.030525 | 0 | 1.2241 | 0.0006105 | 0.00030525 | 0 | 1.2234 | 0.00030525 | 25.0689 | 501376.0001 | 50128.0019
39049.415 | 2249 | 1 | 39049.415 | 0 | 0 |  | 2418.5 | 2654.5 | 137.3016 | 0.06105 | 0.030525 | 0 | 1.373 | 0.0006105 | 0.00030525 | 0 | 1.3724 | 0.00030525 | 11.4938 | 501376.0001 | 25732.8676
39049.4155 | 2129 | 1 | 39049.4155 | 1 | 0 |  | 2460.5 | 2696.5 | 129.9756 | 0.06105 | 0.06105 | 0 | 1.2998 | 0.0006105 | 0.0006105 | 0 | 1.2991 | 0.0006105 | 17.781 | 250638 | 37722.9492
39049.416 | 1890 | 1 | 39049.416 | 1 | 0 |  | 2502.5 | 2738.5 | 115.3846 | 0.06105 | 0.06105 | 0 | 1.1538 | 0.0006105 | 0.0006105 | 0 | 1.1532 | 0.0006105 | 32.6829 | 250638 | 61613.4174
39049.4165 | 1981 | 1 | 39049.4165 | 1 | 0 |  | 2544.5 | 2780.5 | 120.9402 | 0.06105 | 0.06105 | 0 | 1.2094 | 0.0006105 | 0.0006105 | 0 | 1.2088 | 0.0006105 | 26.5849 | 250638.0003 | 52517.0467
39049.417 | 2153 | 1 | 39049.417 | 0 | 0 |  | 2586.5 | 2822.5 | 131.4408 | 0.06105 | 0.030525 | 0 | 1.3144 | 0.0006105 | 0.00030525 | 0 | 1.3138 | 0.00030525 | 16.4675 | 501376.0001 | 35330.9532
39049.4175 | 2139 | 1 | 39049.4175 | 0 | 0 |  | 2628.5 | 2864.5 | 130.5861 | 0.06105 | 0.030525 | 0 | 1.3059 | 0.0006105 | 0.00030525 | 0 | 1.3053 | 0.00030525 | 17.2301 | 501376.0001 | 36730.674
39049.4179 | 2100 | 1 | 39049.418 | 0 | 0 |  | 2670.5 | 2906.5 | 128.2051 | 0.06105 | 0.030525 | 0 | 1.2821 | 0.0006105 | 0.00030525 | 0 | 1.2814 | 0.00030525 | 19.4083 | 501376.0001 | 40629.8963
39049.4184 | 2211 | 1 |  | 1 | 0 |  | 2712 | 2948 | 134.9817 | 0.06105 | 0.06105 | 0 | 1.3498 | 0.0006105 | 0.0006105 | 0 | 1.3492 | 0.0006105 | 13.4109 | 250638 | 29526.2196
39049.4189 | 2135 | 1 | 39049.4189 | 1 | 0 |  | 2754.5 | 2990.5 | 130.3419 | 0.06105 | 0.06105 | 0 | 1.3034 | 0.0006105 | 0.0006105 | 0 | 1.3028 | 0.0006105 | 17.4499 | 250638 | 37123.1885
39049.4194 | 2195 | 1 | 39049.4194 | 0 | 0 |  | 2796.5 | 3032.5 | 134.0049 | 0.06105 | 0.030525 | 0 | 1.34 | 0.0006105 | 0.00030525 | 0 | 1.3394 | 0.00030525 | 14.2379 | 501376.001 | 31131.7907
39049.4199 | 2175 | 1 | 39049.4199 | 0 | 0 |  | 2838.5 | 3074.5 | 132.7839 | 0.06105 | 0.030525 | 0 | 1.3278 | 0.0006105 | 0.00030525 | 0 | 1.3272 | 0.00030525 | 15.2889 | 501376.0001 | 33131.3919
39049.4204 | 2376 | 1 | 39049.4204 | 1 | 0 |  | 2880.5 | 3116.5 | 145.0549 | 0.06105 | 0.06105 | 0 | 1.4505 | 0.0006105 | 0.0006105 | 0 | 1.4499 | 0.0006105 | 5.5318 | 250637.9998 | 13032.8001
39049.4209 | 2478 | 1 | 39049.4209 | 1 | 0 |  | 2922.5 | 3158.5 | 151.2821 | 0.06105 | 0.06105 | 0 | 1.5128 | 0.0006105 | 0.0006105 | 0 | 1.5122 | 0.0006105 | 1.1861 | 250638 | 2836.8681
39049.4213 | 2091 | 1 | 39049.4214 | 0 | 0 |  | 2964.5 | 3200.5 | 127.6557 | 0.06105 | 0.030525 | 0 | 1.2766 | 0.0006105 | 0.00030525 | 0 | 1.2759 | 0.00030525 | 19.9225 | 501376.0001 | 41529.7169

## A1-B4
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 154.2967 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39049.3844 | 0 | 0 | 39049.3844 | 0 | 0 |  | -230 | 6 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3848 | 0 | 0 | 39049.3849 | 0 | 0 |  | -188 | 48 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3853 | 0 | 0 | 39049.3854 | 0 | 0 |  | -146 | 90 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3858 | 0 | 0 | 39049.3858 | 0 | 0 |  | -104 | 132 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3863 | 0 | 0 | 39049.3863 | 0 | 0 |  | -62 | 174 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3868 | 0 | 0 | 39049.3868 | 0 | 0 |  | -20 | 216 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3873 | 0 | 0 | 39049.3873 | 0 | 0 |  | 22 | 258 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3878 | 0 | 0 | 39049.3878 | 0 | 0 |  | 64 | 300 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3883 | 0 | 0 | 39049.3883 | 0 | 0 |  | 106 | 342 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3887 | 0 | 0 | 39049.3888 | 0 | 0 |  | 148 | 384 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3892 | 0 | 0 | 39049.3892 | 0 | 0 |  | 190 | 426 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3897 | 0 | 0 | 39049.3897 | 0 | 0 |  | 232 | 468 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3902 | 0 | 0 | 39049.3902 | 0 | 0 |  | 274 | 510 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3907 | 0 | 0 | 39049.3907 | 0 | 0 |  | 316 | 552 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3912 | 0 | 0 | 39049.3912 | 0 | 0 |  | 358 | 594 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3917 | 0 | 0 | 39049.3917 | 0 | 0 |  | 400 | 636 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3921 | 0 | 0 | 39049.3922 | 0 | 0 |  | 442 | 678 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3926 | 0 | 0 | 39049.3927 | 0 | 0 |  | 484 | 720 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3931 | 0 | 0 | 39049.3931 | 0 | 0 |  | 526 | 762 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3936 | 0 | 0 | 39049.3936 | 0 | 0 |  | 568 | 804 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3941 | 0 | 0 | 39049.3941 | 0 | 0 |  | 610 | 846 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3946 | 0 | 0 | 39049.3946 | 0 | 0 |  | 652 | 888 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3951 | 0 | 0 | 39049.3951 | 0 | 0 |  | 694 | 930 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3955 | 0 | 0 | 39049.3956 | 0 | 0 |  | 736 | 972 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.396 | 0 | 0 | 39049.3961 | 0 | 0 |  | 778 | 1014 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3965 | 0 | 0 | 39049.3965 | 0 | 0 |  | 820 | 1056 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.397 | 0 | 0 | 39049.397 | 0 | 0 |  | 862 | 1098 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3975 | 0 | 0 | 39049.3975 | 0 | 0 |  | 904 | 1140 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.398 | 0 | 0 | 39049.398 | 0 | 0 |  | 946 | 1182 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3985 | 0 | 0 | 39049.3985 | 0 | 0 |  | 988 | 1224 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3989 | 0 | 0 | 39049.399 | 0 | 0 |  | 1030 | 1266 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3994 | 0 | 0 | 39049.3995 | 0 | 0 |  | 1072 | 1308 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.3999 | 0 | 0 | 39049.3999 | 0 | 0 |  | 1114 | 1350 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4004 | 0 | 0 | 39049.4004 | 0 | 0 |  | 1156 | 1392 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4009 | 0 | 0 | 39049.4009 | 0 | 0 |  | 1198 | 1434 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4014 | 0 | 0 | 39049.4014 | 0 | 0 |  | 1240 | 1476 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4019 | 0 | 0 | 39049.4019 | 0 | 0 |  | 1282 | 1518 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4023 | 0 | 0 | 39049.4024 | 0 | 0 |  | 1324 | 1560 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4028 | 0 | 0 | 39049.4029 | 0 | 0 |  | 1366 | 1602 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4033 | 0 | 0 | 39049.4033 | 0 | 0 |  | 1408 | 1644 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4038 | 0 | 0 | 39049.4038 | 0 | 0 |  | 1450 | 1686 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4043 | 0 | 0 | 39049.4043 | 0 | 0 |  | 1492 | 1728 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4048 | 0 | 0 | 39049.4048 | 0 | 0 |  | 1534 | 1770 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4053 | 0 | 0 | 39049.4053 | 0 | 0 |  | 1576 | 1812 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4058 | 0 | 0 | 39049.4058 | 0 | 0 |  | 1618 | 1854 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4062 | 0 | 0 | 39049.4063 | 0 | 0 |  | 1660 | 1896 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505376 | 505376 | 505375.9997
39049.4067 | 0 | 0 | 39049.4067 | 2050 | 5 |  | 1702 | 1938 | 0.030525 | 0 | 125.1526 | 0.30525 | 0.00030525 | 0 | 1.2515 | 0.0030525 | 0.00030525 | 1.2485 | 505376 | 23.5883 | 505375.9997
39049.4072 | 0 | 0 | 39049.4072 | 2459 | 1 |  | 1743.5 | 1979.5 | 0.030525 | 0 | 150.1221 | 0.06105 | 0.00030525 | 0 | 1.5012 | 0.0006105 | 0.00030525 | 1.5006 | 505376 | 2.8226 | 505375.9997
39049.4077 | 1 | 0 | 39049.4077 | 2368 | 0 |  | 1786 | 2022 | 0.06105 | 0 | 144.5665 | 0 | 0.0006105 | 0 | 1.4457 | 0 | 0.0006105 | 1.4457 | 252638 | 6.7306 | 252637.9994
39049.4082 | 1 | 0 | 39049.4082 | 2103 | 0 |  | 1828 | 2064 | 0.06105 | 0 | 128.3883 | 0 | 0.0006105 | 0 | 1.2839 | 0 | 0.0006105 | 1.2839 | 252638 | 20.1797 | 252637.9994
39049.4087 | 0 | 0 | 39049.4087 | 1958 | 0 |  | 1870 | 2106 | 0.030525 | 0 | 119.536 | 0 | 0.00030525 | 0 | 1.1954 | 0 | 0.00030525 | 1.1954 | 505376 | 29.0797 | 505375.9997
39049.4092 | 769 | 0 | 39049.4092 | 1922 | 0 |  | 1912 | 2148 | 46.9475 | 0 | 117.3382 | 0 | 0.46947 | 0 | 1.1734 | 0 | 0.46947 | 1.1734 | 228.658 | 31.4974 | 228.1885
39049.4096 | 2319 | 0 | 39049.4097 | 2065 | 0 |  | 1954 | 2190 | 141.5751 | 0 | 126.0684 | 0 | 1.4158 | 0 | 1.2607 | 0 | 1.4158 | 1.2607 | 8.9858 | 22.3913 | 7.57
39049.4101 | 2074 | 0 | 39049.4101 | 2048 | 0 |  | 1995.5 | 2231.5 | 126.6178 | 0 | 125.0305 | 0 | 1.2662 | 0 | 1.2503 | 0 | 1.2662 | 1.2503 | 21.8602 | 23.4072 | 20.594
39049.4106 | 2415 | 0 | 39049.4106 | 2011 | 0 |  | 2038 | 2274 | 147.4359 | 0 | 122.7717 | 0 | 1.4744 | 0 | 1.2277 | 0 | 1.4744 | 1.2277 | 4.6534 | 25.6778 | 3.1791
39049.4111 | 2461 | 0 | 39049.4111 | 2322 | 0 |  | 2079.5 | 2315.5 | 150.2442 | 0 | 141.7582 | 0 | 1.5024 | 0 | 1.4176 | 0 | 1.5024 | 1.4176 | 2.6973 | 8.845 | 1.1948
39049.4116 | 1986 | 0 | 39049.4116 | 2074 | 0 |  | 2121.5 | 2357.5 | 121.2454 | 0 | 126.6178 | 0 | 1.2125 | 0 | 1.2662 | 0 | 1.2125 | 1.2662 | 27.2598 | 21.8602 | 26.0474
39049.4121 | 2324 | 0 | 39049.4121 | 2018 | 0 |  | 2164 | 2400 | 141.8803 | 0 | 123.199 | 0 | 1.4188 | 0 | 1.232 | 0 | 1.4188 | 1.232 | 8.7513 | 25.2418 | 7.3325
39049.4126 | 2187 | 0 | 39049.4126 | 2482 | 0 |  | 2205.5 | 2441.5 | 133.5165 | 0 | 151.5263 | 0 | 1.3352 | 0 | 1.5153 | 0 | 1.3352 | 1.5153 | 15.5638 | 1.8284 | 14.2286
39049.413 | 1994 | 0 | 39049.4131 | 2121 | 0 |  | 2247.5 | 2483.5 | 121.7338 | 0 | 129.4872 | 0 | 1.2173 | 0 | 1.2949 | 0 | 1.2173 | 1.2949 | 26.7492 | 19.1598 | 25.5319
39049.4135 | 2261 | 0 | 39049.4135 | 2153 | 0 |  | 2289.5 | 2525.5 | 138.0342 | 0 | 131.4408 | 0 | 1.3803 | 0 | 1.3144 | 0 | 1.3803 | 1.3144 | 11.7815 | 17.3888 | 10.4012
39049.414 | 1964 | 0 | 39049.414 | 2194 | 0 |  | 2331.5 | 2567.5 | 119.9023 | 0 | 133.9438 | 0 | 1.199 | 0 | 1.3394 | 0 | 1.199 | 1.3394 | 28.6853 | 15.1951 | 27.4863
39049.4145 | 2271 | 0 | 39049.4145 | 1965 | 0 |  | 2373.5 | 2609.5 | 138.6447 | 0 | 119.9634 | 0 | 1.3864 | 0 | 1.1996 | 0 | 1.3864 | 1.1996 | 11.2893 | 28.6198 | 9.9029
39049.415 | 2064 | 2 | 39049.415 | 2176 | 2 |  | 2415.5 | 2651.5 | 126.0073 | 0.1221 | 132.8449 | 0.1221 | 1.2601 | 0.001221 | 1.3284 | 0.001221 | 1.2589 | 1.3272 | 22.6075 | 16.2289 | 3221.0919
39049.4155 | 2395 | 3 | 39049.4155 | 2187 | 3 |  | 2457.5 | 2693.5 | 146.2149 | 0.18315 | 133.5165 | 0.18315 | 1.4621 | 0.0018315 | 1.3352 | 0.0018315 | 1.4603 | 1.3333 | 5.5781 | 15.9786 | 594.1661
39049.416 | 1993 | 2 | 39049.416 | 2075 | 3 |  | 2499.5 | 2735.5 | 121.6728 | 0.1221 | 126.6789 | 0.18315 | 1.2167 | 0.001221 | 1.2668 | 0.0018315 | 1.2155 | 1.265 | 26.9632 | 21.9509 | 4791.36
39049.4164 | 1960 | 1 | 39049.4165 | 2084 | 0 |  | 2541.5 | 2777.5 | 119.6581 | 0.06105 | 127.2283 | 0 | 1.1966 | 0.0006105 | 1.2723 | 0 | 1.196 | 1.2723 | 29.0324 | 21.2754 | 9936.043
39049.4169 | 2323 | 0 | 39049.4169 | 1982 | 1 |  | 2583.5 | 2819.5 | 141.8193 | 0 | 121.0012 | 0.06105 | 1.4182 | 0 | 1.21 | 0.0006105 | 1.4182 | 1.2094 | 8.7981 | 27.581 | 7.3799
39049.4174 | 2387 | 1 | 39049.4174 | 2482 | 0 |  | 2625.5 | 2861.5 | 145.7265 | 0.06105 | 151.5263 | 0 | 1.4573 | 0.0006105 | 1.5153 | 0 | 1.4567 | 1.5153 | 6.0215 | 1.8284 | 250.2617
39049.4179 | 2341 | 0 | 39049.4179 | 2332 | 0 |  | 2667.5 | 2903.5 | 142.9182 | 0 | 142.3687 | 0 | 1.4292 | 0 | 1.4237 | 0 | 1.4292 | 1.4237 | 7.9616 | 8.3782 | 6.5324
39049.4184 | 1875 | 0 | 39049.4184 | 2072 | 0 |  | 2709.5 | 2945.5 | 114.4689 | 0 | 126.4957 | 0 | 1.1447 | 0 | 1.265 | 0 | 1.1447 | 1.265 | 34.7936 | 21.9778 | 33.6489
39049.4189 | 1949 | 0 | 39049.4189 | 2269 | 0 |  | 2751.5 | 2987.5 | 118.9866 | 0 | 138.5226 | 0 | 1.1899 | 0 | 1.3852 | 0 | 1.1899 | 1.3852 | 29.6757 | 11.3874 | 28.4859
39049.4194 | 2344 | 0 | 39049.4194 | 1930 | 0 |  | 2793.5 | 3029.5 | 143.1013 | 0 | 117.8266 | 0 | 1.431 | 0 | 1.1783 | 0 | 1.431 | 1.1783 | 7.8234 | 30.9523 | 6.3924
39049.4198 | 2447 | 0 | 39049.4199 | 2511 | 0 |  | 2835.5 | 3071.5 | 149.3895 | 0 | 153.2967 | 0 | 1.4939 | 0 | 1.533 | 0 | 1.4939 | 1.533 | 3.2848 | 0.65233 | 1.7909
39049.4203 | 2168 | 0 | 39049.4203 | 2189 | 0 |  | 2877.5 | 3113.5 | 132.3565 | 0 | 133.6386 | 0 | 1.3236 | 0 | 1.3364 | 0 | 1.3236 | 1.3364 | 16.5766 | 15.4582 | 15.253
39049.4208 | 2203 | 0 | 39049.4208 | 2317 | 0 |  | 2919.5 | 3155.5 | 134.4933 | 0 | 141.453 | 0 | 1.3449 | 0 | 1.4145 | 0 | 1.3449 | 1.4145 | 14.7245 | 9.0798 | 13.3795
39049.4213 | 2448 | 0 | 39049.4213 | 2186 | 0 |  | 2961.5 | 3197.5 | 149.4505 | 0 | 133.4554 | 0 | 1.4945 | 0 | 1.3346 | 0 | 1.4945 | 1.3346 | 3.2426 | 15.6167 | 1.7481

## A1-B3
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 156.1282 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39049.3843 | 0 | 0 | 39049.3844 | 0 | 0 |  | -232.5 | 3.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3848 | 0 | 0 | 39049.3848 | 0 | 0 |  | -190.5 | 45.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3853 | 0 | 0 | 39049.3853 | 0 | 0 |  | -148.5 | 87.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3858 | 0 | 0 | 39049.3858 | 0 | 0 |  | -106.5 | 129.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3863 | 0 | 0 | 39049.3863 | 0 | 0 |  | -64.5 | 171.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3868 | 0 | 0 | 39049.3868 | 0 | 0 |  | -22.5 | 213.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3873 | 0 | 0 | 39049.3873 | 0 | 0 |  | 19.5 | 255.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3877 | 0 | 0 | 39049.3878 | 0 | 0 |  | 61.5 | 297.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3882 | 0 | 0 | 39049.3882 | 0 | 0 |  | 103.5 | 339.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3887 | 0 | 0 | 39049.3887 | 0 | 0 |  | 145.5 | 381.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3892 | 0 | 0 | 39049.3892 | 0 | 0 |  | 187.5 | 423.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3897 | 0 | 0 | 39049.3897 | 0 | 0 |  | 229.5 | 465.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3902 | 0 | 0 | 39049.3902 | 0 | 0 |  | 271.5 | 507.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3907 | 0 | 0 | 39049.3907 | 0 | 0 |  | 313.5 | 549.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3911 | 0 | 0 | 39049.3912 | 0 | 0 |  | 355.5 | 591.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3916 | 0 | 0 | 39049.3916 | 0 | 0 |  | 397.5 | 633.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3921 | 0 | 0 | 39049.3921 | 0 | 0 |  | 439.5 | 675.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3926 | 0 | 0 | 39049.3926 | 0 | 0 |  | 481.5 | 717.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3931 | 0 | 0 | 39049.3931 | 0 | 0 |  | 523 | 759 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3936 | 0 | 0 | 39049.3936 | 0 | 0 |  | 565 | 801 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3941 | 0 | 0 | 39049.3941 | 0 | 0 |  | 607.5 | 843.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3945 | 0 | 0 | 39049.3946 | 0 | 0 |  | 649.5 | 885.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.395 | 0 | 0 | 39049.395 | 0 | 0 |  | 691.5 | 927.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3955 | 0 | 0 | 39049.3955 | 0 | 0 |  | 733.5 | 969.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.396 | 0 | 0 | 39049.396 | 0 | 0 |  | 775 | 1011 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3965 | 0 | 0 | 39049.3965 | 0 | 0 |  | 817 | 1053 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.397 | 0 | 0 | 39049.397 | 0 | 0 |  | 859.5 | 1095.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3975 | 0 | 0 | 39049.3975 | 0 | 0 |  | 901.5 | 1137.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3979 | 0 | 0 | 39049.398 | 0 | 0 |  | 943 | 1179 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3984 | 0 | 0 | 39049.3984 | 0 | 0 |  | 985 | 1221 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3989 | 0 | 0 | 39049.3989 | 0 | 0 |  | 1027 | 1263 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3994 | 0 | 0 | 39049.3994 | 0 | 0 |  | 1069 | 1305 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.3999 | 0 | 0 | 39049.3999 | 0 | 0 |  | 1111 | 1347 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4004 | 0 | 0 | 39049.4004 | 0 | 0 |  | 1153 | 1389 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4009 | 0 | 0 | 39049.4009 | 0 | 0 |  | 1195 | 1431 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4013 | 0 | 0 | 39049.4014 | 0 | 0 |  | 1237 | 1473 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4018 | 0 | 0 | 39049.4019 | 0 | 0 |  | 1279 | 1515 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4023 | 0 | 0 | 39049.4023 | 0 | 0 |  | 1321 | 1557 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4028 | 0 | 0 | 39049.4028 | 0 | 0 |  | 1363 | 1599 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4033 | 0 | 0 | 39049.4033 | 0 | 0 |  | 1405 | 1641 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4038 | 0 | 0 | 39049.4038 | 0 | 0 |  | 1447 | 1683 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4043 | 0 | 0 | 39049.4043 | 0 | 0 |  | 1489 | 1725 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4047 | 0 | 0 | 39049.4048 | 0 | 0 |  | 1531 | 1767 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4052 | 0 | 0 | 39049.4053 | 0 | 0 |  | 1573 | 1809 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4057 | 0 | 0 | 39049.4057 | 0 | 0 |  | 1615 | 1851 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4062 | 0 | 0 | 39049.4062 | 0 | 0 |  | 1657 | 1893 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4067 | 0 | 0 | 39049.4067 | 0 | 0 |  | 1699 | 1935 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
39049.4072 | 0 | 0 | 39049.4072 | 2130 | 0 |  | 1741 | 1977 | 0.030525 | 0 | 130.0366 | 0 | 0.00030525 | 0 | 1.3004 | 0 | 0.00030525 | 1.3004 | 511376 | 20.0648 | 511375.9997
39049.4077 | 0 | 0 | 39049.4077 | 2306 | 0 |  | 1783 | 2019 | 0.030525 | 0 | 140.7814 | 0 | 0.00030525 | 0 | 1.4078 | 0 | 0.00030525 | 1.4078 | 511376 | 10.9011 | 511375.9997
39049.4081 | 0 | 0 | 39049.4082 | 2510 | 0 |  | 1825 | 2061 | 0.030525 | 0 | 153.2357 | 0 | 0.00030525 | 0 | 1.5324 | 0 | 0.00030525 | 1.5324 | 511376 | 1.8876 | 511375.9997
39049.4086 | 0 | 0 | 39049.4087 | 2508 | 1 |  | 1867 | 2103 | 0.030525 | 0 | 153.1136 | 0.06105 | 0.00030525 | 0 | 1.5311 | 0.0006105 | 0.00030525 | 1.5305 | 511376 | 2.0096 | 511375.9997
39049.4091 | 483 | 0 | 39049.4091 | 2361 | 0 |  | 1909 | 2145 | 29.4872 | 0 | 144.1392 | 0 | 0.29487 | 0 | 1.4414 | 0 | 0.29487 | 1.4414 | 429.4783 | 8.3177 | 429.1834
39049.4096 | 1864 | 0 | 39049.4096 | 2323 | 0 |  | 1951 | 2187 | 113.7973 | 0 | 141.8193 | 0 | 1.138 | 0 | 1.4182 | 0 | 1.138 | 1.4182 | 37.1985 | 10.0895 | 36.0605
39049.4101 | 2118 | 0 | 39049.4101 | 2183 | 0 |  | 1993 | 2229 | 129.304 | 0 | 133.2723 | 0 | 1.293 | 0 | 1.3327 | 0 | 1.293 | 1.3327 | 20.745 | 17.1498 | 19.452
39049.4106 | 2073 | 0 | 39049.4106 | 1937 | 0 |  | 2035 | 2271 | 126.5568 | 0 | 118.254 | 0 | 1.2656 | 0 | 1.1825 | 0 | 1.2656 | 1.1825 | 23.3661 | 32.0279 | 22.1006
39049.4111 | 2417 | 1 | 39049.4111 | 2541 | 0 |  | 2077 | 2313 | 147.558 | 0.06105 | 155.1282 | 0 | 1.4756 | 0.0006105 | 1.5513 | 0 | 1.475 | 1.5513 | 6.2091 | 0.64463 | 89.2728
39049.4116 | 2254 | 0 | 39049.4116 | 2250 | 0 |  | 2119 | 2355 | 137.6068 | 0 | 137.3626 | 0 | 1.3761 | 0 | 1.3736 | 0 | 1.3761 | 1.3736 | 13.4596 | 13.6613 | 12.0836
39049.412 | 2414 | 0 | 39049.4121 | 2019 | 0 |  | 2161 | 2397 | 147.3748 | 0 | 123.2601 | 0 | 1.4737 | 0 | 1.2326 | 0 | 1.4737 | 1.2326 | 5.9395 | 26.6657 | 4.4658
39049.4125 | 2135 | 0 | 39049.4125 | 2219 | 0 |  | 2203 | 2439 | 130.3419 | 0 | 135.4701 | 0 | 1.3034 | 0 | 1.3547 | 0 | 1.3034 | 1.3547 | 19.7836 | 15.2492 | 18.4802
39049.413 | 1905 | 0 | 39049.413 | 2335 | 0 |  | 2245 | 2481 | 116.3004 | 0 | 142.5519 | 0 | 1.163 | 0 | 1.4255 | 0 | 1.163 | 1.4255 | 34.2457 | 9.5238 | 33.0827
39049.4135 | 2468 | 0 | 39049.4135 | 2030 | 0 |  | 2287 | 2523 | 150.6716 | 0 | 123.9316 | 0 | 1.5067 | 0 | 1.2393 | 0 | 1.5067 | 1.2393 | 3.6216 | 25.9793 | 2.1148
39049.414 | 2062 | 0 | 39049.414 | 2473 | 0 |  | 2329 | 2565 | 125.8852 | 0 | 150.9768 | 0 | 1.2589 | 0 | 1.5098 | 0 | 1.2589 | 1.5098 | 24.0242 | 3.4121 | 22.7654
39049.4145 | 2047 | 0 | 39049.4145 | 1999 | 0 |  | 2371 | 2607 | 124.9695 | 0 | 122.0391 | 0 | 1.2497 | 0 | 1.2204 | 0 | 1.2497 | 1.2204 | 24.9331 | 27.933 | 23.6834
39049.415 | 2404 | 1 | 39049.415 | 2430 | 2 |  | 2413 | 2649 | 146.7643 | 0.06105 | 148.3516 | 0.1221 | 1.4676 | 0.0006105 | 1.4835 | 0.001221 | 1.467 | 1.4823 | 6.4332 | 5.3143 | 768.9352
39049.4154 | 2400 | 4 | 39049.4155 | 2078 | 4 |  | 2455 | 2691 | 146.5201 | 0.2442 | 126.862 | 0.2442 | 1.4652 | 0.002442 | 1.2686 | 0.002442 | 1.4628 | 1.2662 | 6.6148 | 23.8079 | 737.3643
39049.4159 | 2184 | 3 | 39049.4159 | 2239 | 3 |  | 2497 | 2733 | 133.3333 | 0.18315 | 136.6911 | 0.18315 | 1.3333 | 0.0018315 | 1.3669 | 0.0018315 | 1.3315 | 1.3651 | 17.2854 | 14.3502 | 1549.3425
39049.4164 | 2168 | 2 | 39049.4164 | 2060 | 4 |  | 2539 | 2775 | 132.3565 | 0.1221 | 125.7631 | 0.2442 | 1.3236 | 0.001221 | 1.2576 | 0.002442 | 1.3223 | 1.2552 | 18.045 | 24.4553 | 3805.9824
39049.4169 | 2383 | 1 | 39049.4169 | 2169 | 0 |  | 2581 | 2817 | 145.4823 | 0.06105 | 132.4176 | 0 | 1.4548 | 0.0006105 | 1.3242 | 0 | 1.4542 | 1.3242 | 7.3379 | 17.9059 | 2633.059
39049.4174 | 2081 | 0 | 39049.4174 | 2257 | 0 |  | 2623 | 2859 | 127.0452 | 0 | 137.79 | 0 | 1.2705 | 0 | 1.3779 | 0 | 1.2705 | 1.3779 | 22.8919 | 13.3088 | 21.6214
39049.4179 | 2331 | 0 | 39049.4179 | 2380 | 0 |  | 2665 | 2901 | 142.3077 | 0 | 145.2991 | 0 | 1.4231 | 0 | 1.453 | 0 | 1.4231 | 1.453 | 9.7117 | 7.4529 | 8.2886
39049.4184 | 1926 | 0 | 39049.4184 | 2477 | 0 |  | 2707 | 2943 | 117.5824 | 0 | 151.221 | 0 | 1.1758 | 0 | 1.5122 | 0 | 1.1758 | 1.5122 | 32.7819 | 3.2451 | 31.6061
39049.4188 | 2350 | 0 | 39049.4189 | 2453 | 0 |  | 2749 | 2985 | 143.4676 | 0 | 149.7558 | 0 | 1.4347 | 0 | 1.4976 | 0 | 1.4347 | 1.4976 | 8.8247 | 4.2552 | 7.39
39049.4193 | 1913 | 0 | 39049.4194 | 2189 | 0 |  | 2791 | 3027 | 116.7888 | 0 | 133.6386 | 0 | 1.1679 | 0 | 1.3364 | 0 | 1.1679 | 1.3364 | 33.6843 | 16.8287 | 32.5164
39049.4198 | 2177 | 0 | 39049.4198 | 2182 | 0 |  | 2832.5 | 3068.5 | 132.906 | 0 | 133.2112 | 0 | 1.3291 | 0 | 1.3321 | 0 | 1.3291 | 1.3321 | 17.4727 | 17.2035 | 16.1436
39049.4203 | 2320 | 1 | 39049.4203 | 2452 | 0 |  | 2874.5 | 3110.5 | 141.6361 | 0.06105 | 149.6947 | 0 | 1.4164 | 0.0006105 | 1.4969 | 0 | 1.4158 | 1.4969 | 10.3401 | 4.2977 | 974.033
39049.4208 | 2462 | 0 | 39049.4208 | 2233 | 0 |  | 2916.5 | 3152.5 | 150.3053 | 0 | 136.3248 | 0 | 1.5031 | 0 | 1.3632 | 0 | 1.5031 | 1.3632 | 3.8741 | 14.5266 | 2.371
39049.4213 | 2466 | 0 | 39049.4213 | 1977 | 0 |  | 2959 | 3195 | 150.5495 | 0 | 120.696 | 0 | 1.5055 | 0 | 1.207 | 0 | 1.5055 | 1.207 | 3.7056 | 29.3566 | 2.2001

## A1-A2
Open Burn Test 13 |  |  | 2006-11-28 | 9:21 |  |  | Vs = |  | 153.0147 |  | R = | 100
Mixed | 7-C | Tray G | IRMS | 2
0 | 150 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39049.3843 | 0 | 0 | 39049.3843 | 0 | 0 |  | -235.5 | 0.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3848 | 0 | 0 | 39049.3848 | 0 | 0 |  | -193.5 | 42.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3853 | 0 | 0 | 39049.3853 | 0 | 0 |  | -151.5 | 84.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3858 | 0 | 0 | 39049.3858 | 0 | 0 |  | -109.5 | 126.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3863 | 0 | 0 | 39049.3863 | 0 | 0 |  | -67.5 | 168.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3867 | 0 | 0 | 39049.3867 | 0 | 0 |  | -25.5 | 210.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3872 | 0 | 0 | 39049.3872 | 0 | 0 |  | 16.5 | 252.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3877 | 0 | 0 | 39049.3877 | 0 | 0 |  | 58.5 | 294.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3882 | 0 | 0 | 39049.3882 | 0 | 0 |  | 100.5 | 336.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3887 | 0 | 0 | 39049.3887 | 0 | 0 |  | 142.5 | 378.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3892 | 0 | 0 | 39049.3892 | 0 | 0 |  | 184.5 | 420.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3897 | 0 | 0 | 39049.3897 | 0 | 0 |  | 226.5 | 462.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3901 | 0 | 0 | 39049.3902 | 0 | 0 |  | 268.5 | 504.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3906 | 0 | 0 | 39049.3906 | 0 | 0 |  | 310.5 | 546.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3911 | 0 | 0 | 39049.3911 | 0 | 0 |  | 352.5 | 588.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3916 | 0 | 0 | 39049.3916 | 0 | 0 |  | 394.5 | 630.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3921 | 0 | 0 | 39049.3921 | 0 | 0 |  | 436.5 | 672.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3926 | 0 | 0 | 39049.3926 | 0 | 0 |  | 478.5 | 714.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3931 | 0 | 0 | 39049.3931 | 0 | 0 |  | 520.5 | 756.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3935 | 0 | 0 | 39049.3936 | 0 | 0 |  | 562.5 | 798.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.394 | 0 | 0 | 39049.394 | 0 | 0 |  | 604.5 | 840.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3945 | 0 | 0 | 39049.3945 | 0 | 0 |  | 646.5 | 882.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.395 | 0 | 0 | 39049.395 | 0 | 0 |  | 688.5 | 924.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3955 | 0 | 0 | 39049.3955 | 0 | 0 |  | 730.5 | 966.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.396 | 0 | 0 | 39049.396 | 0 | 0 |  | 772.5 | 1008.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3965 | 0 | 0 | 39049.3965 | 0 | 0 |  | 814.5 | 1050.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3969 | 0 | 0 | 39049.397 | 0 | 0 |  | 856.5 | 1092.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3974 | 0 | 0 | 39049.3974 | 0 | 0 |  | 898.5 | 1134.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3979 | 0 | 0 | 39049.3979 | 0 | 0 |  | 940.5 | 1176.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3984 | 0 | 0 | 39049.3984 | 0 | 0 |  | 982.5 | 1218.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3989 | 0 | 0 | 39049.3989 | 0 | 0 |  | 1024.5 | 1260.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3994 | 0 | 0 | 39049.3994 | 0 | 0 |  | 1066.5 | 1302.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.3999 | 0 | 0 | 39049.3999 | 0 | 0 |  | 1108.5 | 1344.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4003 | 0 | 0 | 39049.4004 | 0 | 0 |  | 1150.5 | 1386.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4008 | 0 | 0 | 39049.4008 | 0 | 0 |  | 1192.5 | 1428.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4013 | 0 | 0 | 39049.4013 | 0 | 0 |  | 1234.5 | 1470.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4018 | 0 | 0 | 39049.4018 | 0 | 0 |  | 1276.5 | 1512.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4023 | 0 | 1 | 39049.4023 | 0 | 0 |  | 1318.5 | 1554.5 | 0.030525 | 0.06105 | 0.030525 | 0 | 0.00030525 | 0.0006105 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501376.0798 | 501176 | 250438.0299
39049.4028 | 0 | 0 | 39049.4028 | 0 | 0 |  | 1360.5 | 1596.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4033 | 0 | 0 | 39049.4033 | 0 | 0 |  | 1402.5 | 1638.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4037 | 0 | 0 | 39049.4038 | 0 | 0 |  | 1444.5 | 1680.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4042 | 0 | 0 | 39049.4042 | 0 | 0 |  | 1486.5 | 1722.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4047 | 0 | 0 | 39049.4047 | 0 | 0 |  | 1528.5 | 1764.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4052 | 0 | 0 | 39049.4052 | 0 | 0 |  | 1570.5 | 1806.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4057 | 0 | 0 | 39049.4057 | 0 | 0 |  | 1612.5 | 1848.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4062 | 0 | 0 | 39049.4062 | 0 | 0 |  | 1654.5 | 1890.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4067 | 0 | 0 | 39049.4067 | 0 | 0 |  | 1696 | 1932 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 501176 | 501176 | 501175.9997
39049.4071 | 1 | 0 | 39049.4072 | 0 | 0 |  | 1738 | 1974 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 250538 | 501176 | 250537.9994
39049.4076 | 3 | 2 | 39049.4077 | 3 | 4 |  | 1780.5 | 2016.5 | 0.18315 | 0.1221 | 0.18315 | 0.2442 | 0.0018315 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 0.0006105 | 250537.8401 | 250738.3201 | 125019.1396
39049.4081 | 30 | 25 | 39049.4081 | 34 | 21 |  | 1822.5 | 2058.5 | 1.8315 | 1.5263 | 2.0757 | 1.2821 | 0.018315 | 0.015263 | 0.020757 | 0.012821 | 0.0030525 | 0.0079365 | 50860.4988 | 19078.9044 | 9754.3934
39049.4086 | 134 | 87 | 39049.4086 | 125 | 89 |  | 1864.5 | 2100.5 | 8.1807 | 5.3114 | 7.6313 | 5.4335 | 0.081807 | 0.053114 | 0.076313 | 0.054335 | 0.028694 | 0.021978 | 5185.8139 | 6946.0836 | 2589.5922
39049.4091 | 191 | 148 | 39049.4091 | 236 | 154 |  | 1906.5 | 2142.5 | 11.6606 | 9.0354 | 14.4078 | 9.4017 | 0.11661 | 0.090354 | 0.14408 | 0.094017 | 0.026252 | 0.050061 | 6122.3297 | 2856.3766 | 1414.9108
39049.4096 | 2361 | 3 | 39049.4096 | 2207 | 2 |  | 1948.5 | 2184.5 | 144.1392 | 0.18315 | 134.7375 | 0.1221 | 1.4414 | 0.0018315 | 1.3474 | 0.001221 | 1.4396 | 1.3462 | 6.2229 | 13.7782 | 574.7246
39049.4101 | 2029 | 1 | 39049.4101 | 2466 | 1 |  | 1990.5 | 2226.5 | 123.8706 | 0.06105 | 150.5495 | 0.06105 | 1.2387 | 0.0006105 | 1.5055 | 0.0006105 | 1.2381 | 1.5049 | 24.2687 | 1.6409 | 769.0615
39049.4106 | 1988 | 1 | 39049.4106 | 2122 | 1 |  | 2032.5 | 2268.5 | 121.3675 | 0.06105 | 129.5482 | 0.06105 | 1.2137 | 0.0006105 | 1.2955 | 0.0006105 | 1.2131 | 1.2949 | 26.1611 | 18.1553 | 7949.8681
39049.411 | 2425 | 1 | 39049.4111 | 1958 | 1 |  | 2074 | 2310 | 148.0464 | 0.06105 | 119.536 | 0.06105 | 1.4805 | 0.0006105 | 1.1954 | 0.0006105 | 1.4799 | 1.1947 | 3.3621 | 28.4539 | 1780.5027
39049.4115 | 2381 | 1 | 39049.4115 | 1891 | 1 |  | 2116 | 2352 | 145.3602 | 0.06105 | 115.4457 | 0.06105 | 1.4536 | 0.0006105 | 1.1545 | 0.0006105 | 1.453 | 1.1538 | 5.2748 | 32.8897 | 3078.3578
39049.412 | 1950 | 1 | 39049.412 | 2490 | 1 |  | 2158 | 2394 | 119.0476 | 0.06105 | 152.0147 | 0.06105 | 1.1905 | 0.0006105 | 1.5201 | 0.0006105 | 1.1899 | 1.5195 | 30.9574 | 0.65895 | 363.5723
39049.4125 | 2256 | 0 | 39049.4125 | 2028 | 0 |  | 2200 | 2436 | 137.7289 | 0 | 123.8095 | 0 | 1.3773 | 0 | 1.2381 | 0 | 1.3773 | 1.2381 | 11.0984 | 23.5888 | 9.7211
39049.413 | 2077 | 1 | 39049.413 | 2470 | 1 |  | 2242 | 2478 | 126.801 | 0.06105 | 150.7937 | 0.06105 | 1.268 | 0.0006105 | 1.5079 | 0.0006105 | 1.2674 | 1.5073 | 21.3807 | 1.4763 | 623.2034
39049.4135 | 2449 | 1 | 39049.4135 | 2167 | 1 |  | 2284 | 2520 | 149.5116 | 0.06105 | 132.2955 | 0.06105 | 1.4951 | 0.0006105 | 1.323 | 0.0006105 | 1.4945 | 1.3223 | 2.35 | 15.9825 | 776.9223
39049.4139 | 2361 | 1 | 39049.414 | 2157 | 1 |  | 2326 | 2562 | 144.1392 | 0.06105 | 131.685 | 0.06105 | 1.4414 | 0.0006105 | 1.3168 | 0.0006105 | 1.4408 | 1.3162 | 6.1762 | 16.3276 | 2026.5029
39049.4144 | 2354 | 1 | 39049.4145 | 2384 | 1 |  | 2368 | 2604 | 143.7118 | 0.06105 | 145.5433 | 0.06105 | 1.4371 | 0.0006105 | 1.4554 | 0.0006105 | 1.4365 | 1.4548 | 6.5297 | 5.1688 | 743.9919
39049.4149 | 2338 | 19 | 39049.4149 | 1926 | 5 |  | 2410 | 2646 | 142.735 | 1.16 | 117.5824 | 0.30525 | 1.4274 | 0.0116 | 1.1758 | 0.0030525 | 1.4158 | 1.1728 | 7.456 | 31.3052 | 187.4449
39049.4154 | 1803 | 31 | 39049.4154 | 1827 | 29 |  | 2452 | 2688 | 110.0733 | 1.8926 | 111.5385 | 1.7705 | 1.1007 | 0.018926 | 1.1154 | 0.017705 | 1.0818 | 1.0977 | 41.5429 | 39.3116 | 612.0494
39049.4159 | 1969 | 84 | 39049.4159 | 1813 | 46 |  | 2494 | 2730 | 120.2076 | 5.1282 | 110.6838 | 2.8083 | 1.2021 | 0.051282 | 1.1068 | 0.028083 | 1.1508 | 1.0788 | 31.8269 | 42.7361 | 161.6011
39049.4164 | 2040 | 8 | 39049.4164 | 2203 | 8 |  | 2536 | 2772 | 124.5421 | 0.4884 | 134.4933 | 0.4884 | 1.2454 | 0.004884 | 1.3449 | 0.004884 | 1.2405 | 1.34 | 23.614 | 14.0381 | 705.3318
39049.4169 | 1878 | 3 | 39049.4169 | 2192 | 3 |  | 2578 | 2814 | 114.652 | 0.18315 | 133.8217 | 0.18315 | 1.1465 | 0.0018315 | 1.3382 | 0.0018315 | 1.1447 | 1.3364 | 33.8896 | 14.4201 | 2627.1768
39049.4173 | 2056 | 4 | 39049.4174 | 2207 | 3 |  | 2620 | 2856 | 125.5189 | 0.2442 | 134.7375 | 0.18315 | 1.2552 | 0.002442 | 1.3474 | 0.0018315 | 1.2527 | 1.3455 | 22.2659 | 13.667 | 1341.7898
39049.4178 | 1866 | 4 | 39049.4179 | 2415 | 4 |  | 2662 | 2898 | 113.9194 | 0.2442 | 147.4359 | 0.2442 | 1.1392 | 0.002442 | 1.4744 | 0.002442 | 1.1368 | 1.4719 | 36.4485 | 3.8075 | 583.5301
39049.4183 | 2013 | 1 | 39049.4183 | 2311 | 1 |  | 2704 | 2940 | 122.8938 | 0.06105 | 141.0867 | 0.06105 | 1.2289 | 0.0006105 | 1.4109 | 0.0006105 | 1.2283 | 1.4103 | 24.6666 | 8.4729 | 3846.0084
39049.4188 | 1938 | 1 | 39049.4188 | 2131 | 1 |  | 2746 | 2982 | 118.315 | 0.06105 | 130.0977 | 0.06105 | 1.1832 | 0.0006105 | 1.301 | 0.0006105 | 1.1825 | 1.3004 | 29.4294 | 17.6516 | 8512.5753
39049.4193 | 2209 | 1 | 39049.4193 | 2240 | 1 |  | 2788 | 3024 | 134.8596 | 0.06105 | 136.7521 | 0.06105 | 1.3486 | 0.0006105 | 1.3675 | 0.0006105 | 1.348 | 1.3669 | 13.5196 | 11.9367 | 3160.5377
39049.4198 | 2383 | 4 | 39049.4198 | 2110 | 1 |  | 2830 | 3066 | 145.4823 | 0.2442 | 128.8156 | 0.06105 | 1.4548 | 0.002442 | 1.2882 | 0.0006105 | 1.4524 | 1.2875 | 5.2326 | 18.9666 | 475.8118
39049.4203 | 2435 | 5 | 39049.4203 | 1937 | 5 |  | 2872 | 3108 | 148.6569 | 0.30525 | 118.254 | 0.30525 | 1.4866 | 0.0030525 | 1.1825 | 0.0030525 | 1.4835 | 1.1795 | 2.9563 | 32.2985 | 324.1116
39049.4208 | 1994 | 6 | 39049.4208 | 2100 | 4 |  | 2914 | 3150 | 121.7338 | 0.3663 | 128.2051 | 0.2442 | 1.2173 | 0.003663 | 1.2821 | 0.002442 | 1.2137 | 1.2796 | 26.1782 | 19.5307 | 1379.0003
39049.4212 | 2364 | 1 | 39049.4213 | 1925 | 2 |  | 2956 | 3192 | 144.3223 | 0.06105 | 117.5214 | 0.1221 | 1.4432 | 0.0006105 | 1.1752 | 0.001221 | 1.4426 | 1.174 | 6.0337 | 30.7632 | 3326.0931

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 13 |  |  | 2006-11-28 | 9:21
39049.3843 | 0 | 0 | 1 | Mixed | 7-C | Tray G | IRMS | 2
39049.3848 | 0 | 0 | 1 |  | 150 kW |  | Bundle
39049.3853 | 0 | 0 | 1
39049.3858 | 0 | 0 | 1
39049.3863 | 0 | 0 | 1
39049.3867 | 0 | 0 | 1
39049.3872 | 0 | 0 | 1
39049.3877 | 0 | 0 | 1
39049.3882 | 0 | 0 | 1
39049.3887 | 0 | 0 | 1
39049.3892 | 0 | 0 | 1
39049.3897 | 0 | 0 | 1
39049.3901 | 0 | 0 | 1
39049.3906 | 0 | 0 | 1
39049.3911 | 0 | 0 | 1
39049.3916 | 0 | 0 | 1
39049.3921 | 0 | 0 | 1
39049.3926 | 0 | 0 | 1
39049.3931 | 0 | 0 | 1
39049.3935 | 0 | 0 | 1
39049.394 | 0 | 0 | 1
39049.3945 | 0 | 0 | 1
39049.395 | 0 | 0 | 1
39049.3955 | 0 | 0 | 1
39049.396 | 0 | 0 | 1
39049.3965 | 0 | 0 | 1
39049.3969 | 0 | 0 | 1
39049.3974 | 0 | 0 | 1
39049.3979 | 0 | 0 | 1
39049.3984 | 0 | 0 | 1
39049.3989 | 0 | 0 | 1
39049.3994 | 0 | 0 | 1
39049.3999 | 0 | 0 | 1
39049.4003 | 0 | 0 | 1
39049.4008 | 0 | 0 | 1
39049.4013 | 0 | 0 | 1
39049.4018 | 0 | 0 | 1
39049.4023 | 0 | 1 | 1
39049.4028 | 0 | 0 | 1
39049.4033 | 0 | 0 | 1
39049.4037 | 0 | 0 | 1
39049.4042 | 0 | 0 | 1
39049.4047 | 0 | 0 | 1
39049.4052 | 0 | 0 | 1
39049.4057 | 0 | 0 | 1
39049.4062 | 0 | 0 | 1
39049.4067 | 0 | 0 | 1
39049.4071 | 1 | 0 | 1
39049.4076 | 3 | 2 | 1
39049.4081 | 30 | 25 | 1
39049.4086 | 134 | 87 | 1
39049.4091 | 191 | 148 | 1
39049.4096 | 2361 | 3 | 1
39049.4101 | 2029 | 1 | 1
39049.4106 | 1988 | 1 | 1
39049.411 | 2425 | 1 | 1
39049.4115 | 2381 | 1 | 1
39049.412 | 1950 | 1 | 1
39049.4125 | 2256 | 0 | 1
39049.413 | 2077 | 1 | 1
39049.4135 | 2449 | 1 | 1
39049.4139 | 2361 | 1 | 1
39049.4144 | 2354 | 1 | 1
39049.4149 | 2338 | 19 | 1
39049.4154 | 1803 | 31 | 1
39049.4159 | 1969 | 84 | 1
39049.4164 | 2040 | 8 | 1
39049.4169 | 1878 | 3 | 1
39049.4173 | 2056 | 4 | 1
39049.4178 | 1866 | 4 | 1
39049.4183 | 2013 | 1 | 1
39049.4188 | 1938 | 1 | 1
39049.4193 | 2209 | 1 | 1
39049.4198 | 2383 | 4 | 1
39049.4203 | 2435 | 5 | 1
39049.4208 | 1994 | 6 | 1
39049.4212 | 2364 | 1 | 1
1
39049.3843 | 0 | 0 | 2
39049.3848 | 0 | 0 | 2
39049.3853 | 0 | 0 | 2
39049.3858 | 0 | 0 | 2
39049.3863 | 0 | 0 | 2
39049.3867 | 0 | 0 | 2
39049.3872 | 0 | 0 | 2
39049.3877 | 0 | 0 | 2
39049.3882 | 0 | 0 | 2
39049.3887 | 0 | 0 | 2
39049.3892 | 0 | 0 | 2
39049.3897 | 0 | 0 | 2
39049.3902 | 0 | 0 | 2
39049.3906 | 0 | 0 | 2
39049.3911 | 0 | 0 | 2
39049.3916 | 0 | 0 | 2
39049.3921 | 0 | 0 | 2
39049.3926 | 0 | 0 | 2
39049.3931 | 0 | 0 | 2
39049.3936 | 0 | 0 | 2
39049.394 | 0 | 0 | 2
39049.3945 | 0 | 0 | 2
39049.395 | 0 | 0 | 2
39049.3955 | 0 | 0 | 2
39049.396 | 0 | 0 | 2
39049.3965 | 0 | 0 | 2
39049.397 | 0 | 0 | 2
39049.3974 | 0 | 0 | 2
39049.3979 | 0 | 0 | 2
39049.3984 | 0 | 0 | 2
39049.3989 | 0 | 0 | 2
39049.3994 | 0 | 0 | 2
39049.3999 | 0 | 0 | 2
39049.4004 | 0 | 0 | 2
39049.4008 | 0 | 0 | 2
39049.4013 | 0 | 0 | 2
39049.4018 | 0 | 0 | 2
39049.4023 | 0 | 0 | 2
39049.4028 | 0 | 0 | 2
39049.4033 | 0 | 0 | 2
39049.4038 | 0 | 0 | 2
39049.4042 | 0 | 0 | 2
39049.4047 | 0 | 0 | 2
39049.4052 | 0 | 0 | 2
39049.4057 | 0 | 0 | 2
39049.4062 | 0 | 0 | 2
39049.4067 | 0 | 0 | 2
39049.4072 | 0 | 0 | 2
39049.4077 | 3 | 4 | 2
39049.4081 | 34 | 21 | 2
39049.4086 | 125 | 89 | 2
39049.4091 | 236 | 154 | 2
39049.4096 | 2207 | 2 | 2
39049.4101 | 2466 | 1 | 2
39049.4106 | 2122 | 1 | 2
39049.4111 | 1958 | 1 | 2
39049.4115 | 1891 | 1 | 2
39049.412 | 2490 | 1 | 2
39049.4125 | 2028 | 0 | 2
39049.413 | 2470 | 1 | 2
39049.4135 | 2167 | 1 | 2
39049.414 | 2157 | 1 | 2
39049.4145 | 2384 | 1 | 2
39049.4149 | 1926 | 5 | 2
39049.4154 | 1827 | 29 | 2
39049.4159 | 1813 | 46 | 2
39049.4164 | 2203 | 8 | 2
39049.4169 | 2192 | 3 | 2
39049.4174 | 2207 | 3 | 2
39049.4179 | 2415 | 4 | 2
39049.4183 | 2311 | 1 | 2
39049.4188 | 2131 | 1 | 2
39049.4193 | 2240 | 1 | 2
39049.4198 | 2110 | 1 | 2
39049.4203 | 1937 | 5 | 2
39049.4208 | 2100 | 4 | 2
39049.4213 | 1925 | 2 | 2
2
39049.3843 | 0 | 0 | 3
39049.3848 | 0 | 0 | 3
39049.3853 | 0 | 0 | 3
39049.3858 | 0 | 0 | 3
39049.3863 | 0 | 0 | 3
39049.3868 | 0 | 0 | 3
39049.3873 | 0 | 0 | 3
39049.3877 | 0 | 0 | 3
39049.3882 | 0 | 0 | 3
39049.3887 | 0 | 0 | 3
39049.3892 | 0 | 0 | 3
39049.3897 | 0 | 0 | 3
39049.3902 | 0 | 0 | 3
39049.3907 | 0 | 0 | 3
39049.3911 | 0 | 0 | 3
39049.3916 | 0 | 0 | 3
39049.3921 | 0 | 0 | 3
39049.3926 | 0 | 0 | 3
39049.3931 | 0 | 0 | 3
39049.3936 | 0 | 0 | 3
39049.3941 | 0 | 0 | 3
39049.3945 | 0 | 0 | 3
39049.395 | 0 | 0 | 3
39049.3955 | 0 | 0 | 3
39049.396 | 0 | 0 | 3
39049.3965 | 0 | 0 | 3
39049.397 | 0 | 0 | 3
39049.3975 | 0 | 0 | 3
39049.3979 | 0 | 0 | 3
39049.3984 | 0 | 0 | 3
39049.3989 | 0 | 0 | 3
39049.3994 | 0 | 0 | 3
39049.3999 | 0 | 0 | 3
39049.4004 | 0 | 0 | 3
39049.4009 | 0 | 0 | 3
39049.4013 | 0 | 0 | 3
39049.4018 | 0 | 0 | 3
39049.4023 | 0 | 0 | 3
39049.4028 | 0 | 0 | 3
39049.4033 | 0 | 0 | 3
39049.4038 | 0 | 0 | 3
39049.4043 | 0 | 0 | 3
39049.4047 | 0 | 0 | 3
39049.4052 | 0 | 0 | 3
39049.4057 | 0 | 0 | 3
39049.4062 | 0 | 0 | 3
39049.4067 | 0 | 0 | 3
39049.4072 | 0 | 0 | 3
39049.4077 | 0 | 0 | 3
39049.4081 | 0 | 0 | 3
39049.4086 | 0 | 0 | 3
39049.4091 | 483 | 0 | 3
39049.4096 | 1864 | 0 | 3
39049.4101 | 2118 | 0 | 3
39049.4106 | 2073 | 0 | 3
39049.4111 | 2417 | 1 | 3
39049.4116 | 2254 | 0 | 3
39049.412 | 2414 | 0 | 3
39049.4125 | 2135 | 0 | 3
39049.413 | 1905 | 0 | 3
39049.4135 | 2468 | 0 | 3
39049.414 | 2062 | 0 | 3
39049.4145 | 2047 | 0 | 3
39049.415 | 2404 | 1 | 3
39049.4154 | 2400 | 4 | 3
39049.4159 | 2184 | 3 | 3
39049.4164 | 2168 | 2 | 3
39049.4169 | 2383 | 1 | 3
39049.4174 | 2081 | 0 | 3
39049.4179 | 2331 | 0 | 3
39049.4184 | 1926 | 0 | 3
39049.4188 | 2350 | 0 | 3
39049.4193 | 1913 | 0 | 3
39049.4198 | 2177 | 0 | 3
39049.4203 | 2320 | 1 | 3
39049.4208 | 2462 | 0 | 3
39049.4213 | 2466 | 0 | 3
3
39049.3844 | 0 | 0 | 4
39049.3848 | 0 | 0 | 4
39049.3853 | 0 | 0 | 4
39049.3858 | 0 | 0 | 4
39049.3863 | 0 | 0 | 4
39049.3868 | 0 | 0 | 4
39049.3873 | 0 | 0 | 4
39049.3878 | 0 | 0 | 4
39049.3882 | 0 | 0 | 4
39049.3887 | 0 | 0 | 4
39049.3892 | 0 | 0 | 4
39049.3897 | 0 | 0 | 4
39049.3902 | 0 | 0 | 4
39049.3907 | 0 | 0 | 4
39049.3912 | 0 | 0 | 4
39049.3916 | 0 | 0 | 4
39049.3921 | 0 | 0 | 4
39049.3926 | 0 | 0 | 4
39049.3931 | 0 | 0 | 4
39049.3936 | 0 | 0 | 4
39049.3941 | 0 | 0 | 4
39049.3946 | 0 | 0 | 4
39049.395 | 0 | 0 | 4
39049.3955 | 0 | 0 | 4
39049.396 | 0 | 0 | 4
39049.3965 | 0 | 0 | 4
39049.397 | 0 | 0 | 4
39049.3975 | 0 | 0 | 4
39049.398 | 0 | 0 | 4
39049.3984 | 0 | 0 | 4
39049.3989 | 0 | 0 | 4
39049.3994 | 0 | 0 | 4
39049.3999 | 0 | 0 | 4
39049.4004 | 0 | 0 | 4
39049.4009 | 0 | 0 | 4
39049.4014 | 0 | 0 | 4
39049.4019 | 0 | 0 | 4
39049.4023 | 0 | 0 | 4
39049.4028 | 0 | 0 | 4
39049.4033 | 0 | 0 | 4
39049.4038 | 0 | 0 | 4
39049.4043 | 0 | 0 | 4
39049.4048 | 0 | 0 | 4
39049.4053 | 0 | 0 | 4
39049.4057 | 0 | 0 | 4
39049.4062 | 0 | 0 | 4
39049.4067 | 0 | 0 | 4
39049.4072 | 2130 | 0 | 4
39049.4077 | 2306 | 0 | 4
39049.4082 | 2510 | 0 | 4
39049.4087 | 2508 | 1 | 4
39049.4091 | 2361 | 0 | 4
39049.4096 | 2323 | 0 | 4
39049.4101 | 2183 | 0 | 4
39049.4106 | 1937 | 0 | 4
39049.4111 | 2541 | 0 | 4
39049.4116 | 2250 | 0 | 4
39049.4121 | 2019 | 0 | 4
39049.4125 | 2219 | 0 | 4
39049.413 | 2335 | 0 | 4
39049.4135 | 2030 | 0 | 4
39049.414 | 2473 | 0 | 4
39049.4145 | 1999 | 0 | 4
39049.415 | 2430 | 2 | 4
39049.4155 | 2078 | 4 | 4
39049.4159 | 2239 | 3 | 4
39049.4164 | 2060 | 4 | 4
39049.4169 | 2169 | 0 | 4
39049.4174 | 2257 | 0 | 4
39049.4179 | 2380 | 0 | 4
39049.4184 | 2477 | 0 | 4
39049.4189 | 2453 | 0 | 4
39049.4194 | 2189 | 0 | 4
39049.4198 | 2182 | 0 | 4
39049.4203 | 2452 | 0 | 4
39049.4208 | 2233 | 0 | 4
39049.4213 | 1977 | 0 | 4
4
39049.3844 | 0 | 0 | 5
39049.3848 | 0 | 0 | 5
39049.3853 | 0 | 0 | 5
39049.3858 | 0 | 0 | 5
39049.3863 | 0 | 0 | 5
39049.3868 | 0 | 0 | 5
39049.3873 | 0 | 0 | 5
39049.3878 | 0 | 0 | 5
39049.3883 | 0 | 0 | 5
39049.3887 | 0 | 0 | 5
39049.3892 | 0 | 0 | 5
39049.3897 | 0 | 0 | 5
39049.3902 | 0 | 0 | 5
39049.3907 | 0 | 0 | 5
39049.3912 | 0 | 0 | 5
39049.3917 | 0 | 0 | 5
39049.3921 | 0 | 0 | 5
39049.3926 | 0 | 0 | 5
39049.3931 | 0 | 0 | 5
39049.3936 | 0 | 0 | 5
39049.3941 | 0 | 0 | 5
39049.3946 | 0 | 0 | 5
39049.3951 | 0 | 0 | 5
39049.3955 | 0 | 0 | 5
39049.396 | 0 | 0 | 5
39049.3965 | 0 | 0 | 5
39049.397 | 0 | 0 | 5
39049.3975 | 0 | 0 | 5
39049.398 | 0 | 0 | 5
39049.3985 | 0 | 0 | 5
39049.3989 | 0 | 0 | 5
39049.3994 | 0 | 0 | 5
39049.3999 | 0 | 0 | 5
39049.4004 | 0 | 0 | 5
39049.4009 | 0 | 0 | 5
39049.4014 | 0 | 0 | 5
39049.4019 | 0 | 0 | 5
39049.4023 | 0 | 0 | 5
39049.4028 | 0 | 0 | 5
39049.4033 | 0 | 0 | 5
39049.4038 | 0 | 0 | 5
39049.4043 | 0 | 0 | 5
39049.4048 | 0 | 0 | 5
39049.4053 | 0 | 0 | 5
39049.4058 | 0 | 0 | 5
39049.4062 | 0 | 0 | 5
39049.4067 | 0 | 0 | 5
39049.4072 | 0 | 0 | 5
39049.4077 | 1 | 0 | 5
39049.4082 | 1 | 0 | 5
39049.4087 | 0 | 0 | 5
39049.4092 | 769 | 0 | 5
39049.4096 | 2319 | 0 | 5
39049.4101 | 2074 | 0 | 5
39049.4106 | 2415 | 0 | 5
39049.4111 | 2461 | 0 | 5
39049.4116 | 1986 | 0 | 5
39049.4121 | 2324 | 0 | 5
39049.4126 | 2187 | 0 | 5
39049.413 | 1994 | 0 | 5
39049.4135 | 2261 | 0 | 5
39049.414 | 1964 | 0 | 5
39049.4145 | 2271 | 0 | 5
39049.415 | 2064 | 2 | 5
39049.4155 | 2395 | 3 | 5
39049.416 | 1993 | 2 | 5
39049.4164 | 1960 | 1 | 5
39049.4169 | 2323 | 0 | 5
39049.4174 | 2387 | 1 | 5
39049.4179 | 2341 | 0 | 5
39049.4184 | 1875 | 0 | 5
39049.4189 | 1949 | 0 | 5
39049.4194 | 2344 | 0 | 5
39049.4198 | 2447 | 0 | 5
39049.4203 | 2168 | 0 | 5
39049.4208 | 2203 | 0 | 5
39049.4213 | 2448 | 0 | 5
5
39049.3844 | 0 | 0 | 6
39049.3849 | 0 | 0 | 6
39049.3854 | 0 | 0 | 6
39049.3858 | 0 | 0 | 6
39049.3863 | 0 | 0 | 6
39049.3868 | 0 | 0 | 6
39049.3873 | 0 | 0 | 6
39049.3878 | 0 | 0 | 6
39049.3883 | 0 | 0 | 6
39049.3888 | 0 | 0 | 6
39049.3892 | 0 | 0 | 6
39049.3897 | 0 | 0 | 6
39049.3902 | 0 | 0 | 6
39049.3907 | 0 | 0 | 6
39049.3912 | 0 | 0 | 6
39049.3917 | 0 | 0 | 6
39049.3922 | 0 | 0 | 6
39049.3927 | 0 | 0 | 6
39049.3931 | 0 | 0 | 6
39049.3936 | 0 | 0 | 6
39049.3941 | 0 | 0 | 6
39049.3946 | 0 | 0 | 6
39049.3951 | 0 | 0 | 6
39049.3956 | 0 | 0 | 6
39049.3961 | 0 | 0 | 6
39049.3965 | 0 | 0 | 6
39049.397 | 0 | 0 | 6
39049.3975 | 0 | 0 | 6
39049.398 | 0 | 0 | 6
39049.3985 | 0 | 0 | 6
39049.399 | 0 | 0 | 6
39049.3995 | 0 | 0 | 6
39049.3999 | 0 | 0 | 6
39049.4004 | 0 | 0 | 6
39049.4009 | 0 | 0 | 6
39049.4014 | 0 | 0 | 6
39049.4019 | 0 | 0 | 6
39049.4024 | 0 | 0 | 6
39049.4029 | 0 | 0 | 6
39049.4033 | 0 | 0 | 6
39049.4038 | 0 | 0 | 6
39049.4043 | 0 | 0 | 6
39049.4048 | 0 | 0 | 6
39049.4053 | 0 | 0 | 6
39049.4058 | 0 | 0 | 6
39049.4063 | 0 | 0 | 6
39049.4067 | 2050 | 5 | 6
39049.4072 | 2459 | 1 | 6
39049.4077 | 2368 | 0 | 6
39049.4082 | 2103 | 0 | 6
39049.4087 | 1958 | 0 | 6
39049.4092 | 1922 | 0 | 6
39049.4097 | 2065 | 0 | 6
39049.4101 | 2048 | 0 | 6
39049.4106 | 2011 | 0 | 6
39049.4111 | 2322 | 0 | 6
39049.4116 | 2074 | 0 | 6
39049.4121 | 2018 | 0 | 6
39049.4126 | 2482 | 0 | 6
39049.4131 | 2121 | 0 | 6
39049.4135 | 2153 | 0 | 6
39049.414 | 2194 | 0 | 6
39049.4145 | 1965 | 0 | 6
39049.415 | 2176 | 2 | 6
39049.4155 | 2187 | 3 | 6
39049.416 | 2075 | 3 | 6
39049.4165 | 2084 | 0 | 6
39049.4169 | 1982 | 1 | 6
39049.4174 | 2482 | 0 | 6
39049.4179 | 2332 | 0 | 6
39049.4184 | 2072 | 0 | 6
39049.4189 | 2269 | 0 | 6
39049.4194 | 1930 | 0 | 6
39049.4199 | 2511 | 0 | 6
39049.4203 | 2189 | 0 | 6
39049.4208 | 2317 | 0 | 6
39049.4213 | 2186 | 0 | 6
6
39049.3844 | 0 | 0 | 7
39049.3849 | 0 | 0 | 7
39049.3854 | 0 | 0 | 7
39049.3859 | 0 | 0 | 7
39049.3863 | 0 | 0 | 7
39049.3868 | 0 | 0 | 7
39049.3873 | 0 | 0 | 7
39049.3878 | 0 | 0 | 7
39049.3883 | 0 | 0 | 7
39049.3888 | 0 | 0 | 7
39049.3893 | 0 | 0 | 7
39049.3897 | 0 | 0 | 7
39049.3902 | 0 | 0 | 7
39049.3907 | 0 | 0 | 7
39049.3912 | 0 | 0 | 7
39049.3917 | 0 | 0 | 7
39049.3922 | 0 | 0 | 7
39049.3927 | 0 | 0 | 7
39049.3931 | 0 | 0 | 7
39049.3936 | 0 | 0 | 7
39049.3941 | 0 | 0 | 7
39049.3946 | 0 | 0 | 7
39049.3951 | 0 | 0 | 7
39049.3956 | 0 | 0 | 7
39049.3961 | 0 | 0 | 7
39049.3966 | 0 | 0 | 7
39049.397 | 0 | 0 | 7
39049.3975 | 0 | 0 | 7
39049.398 | 0 | 0 | 7
39049.3985 | 0 | 0 | 7
39049.399 | 0 | 0 | 7
39049.3995 | 0 | 0 | 7
39049.4 | 0 | 0 | 7
39049.4004 | 0 | 0 | 7
39049.4009 | 0 | 0 | 7
39049.4014 | 0 | 1 | 7
39049.4019 | 0 | 0 | 7
39049.4024 | 0 | 0 | 7
39049.4029 | 0 | 0 | 7
39049.4034 | 0 | 0 | 7
39049.4038 | 0 | 0 | 7
39049.4043 | 0 | 0 | 7
39049.4048 | 0 | 0 | 7
39049.4053 | 0 | 0 | 7
39049.4058 | 0 | 0 | 7
39049.4063 | 0 | 0 | 7
39049.4068 | 0 | 0 | 7
39049.4072 | 0 | 1 | 7
39049.4077 | 0 | 0 | 7
39049.4082 | 0 | 0 | 7
39049.4087 | 1 | 0 | 7
39049.4092 | 1235 | 0 | 7
39049.4097 | 2309 | 0 | 7
39049.4102 | 1972 | 0 | 7
39049.4106 | 2438 | 0 | 7
39049.4111 | 1976 | 0 | 7
39049.4116 | 2348 | 0 | 7
39049.4121 | 2359 | 0 | 7
39049.4126 | 2491 | 0 | 7
39049.4131 | 2423 | 0 | 7
39049.4136 | 2476 | 0 | 7
39049.4141 | 2403 | 0 | 7
39049.4145 | 2005 | 0 | 7
39049.415 | 2249 | 0 | 7
39049.4155 | 2129 | 0 | 7
39049.416 | 1890 | 0 | 7
39049.4165 | 1981 | 0 | 7
39049.417 | 2153 | 0 | 7
39049.4175 | 2139 | 0 | 7
39049.4179 | 2100 | 0 | 7
39049.4184 | 2211 | 0 | 7
39049.4189 | 2135 | 0 | 7
39049.4194 | 2195 | 0 | 7
39049.4199 | 2175 | 0 | 7
39049.4204 | 2376 | 0 | 7
39049.4209 | 2478 | 0 | 7
39049.4213 | 2091 | 0 | 7
7
39049.3844 | 0 | 0 | 8
39049.3849 | 0 | 0 | 8
39049.3854 | 0 | 0 | 8
39049.3859 | 0 | 0 | 8
39049.3864 | 0 | 0 | 8
39049.3869 | 0 | 0 | 8
39049.3873 | 0 | 0 | 8
39049.3878 | 0 | 0 | 8
39049.3883 | 0 | 0 | 8
39049.3888 | 0 | 0 | 8
39049.3893 | 0 | 0 | 8
39049.3898 | 0 | 0 | 8
39049.3903 | 0 | 0 | 8
39049.3907 | 0 | 0 | 8
39049.3912 | 0 | 0 | 8
39049.3917 | 0 | 0 | 8
39049.3922 | 0 | 0 | 8
39049.3927 | 0 | 0 | 8
39049.3932 | 0 | 0 | 8
39049.3937 | 0 | 0 | 8
39049.3941 | 0 | 0 | 8
39049.3946 | 0 | 0 | 8
39049.3951 | 0 | 0 | 8
39049.3956 | 0 | 0 | 8
39049.3961 | 0 | 0 | 8
39049.3966 | 0 | 0 | 8
39049.3971 | 0 | 0 | 8
39049.3975 | 0 | 0 | 8
39049.398 | 0 | 0 | 8
39049.3985 | 0 | 0 | 8
39049.399 | 0 | 0 | 8
39049.3995 | 0 | 0 | 8
39049.4 | 0 | 0 | 8
39049.4005 | 0 | 0 | 8
39049.4009 | 0 | 0 | 8
39049.4014 | 0 | 0 | 8
39049.4019 | 0 | 0 | 8
39049.4024 | 0 | 0 | 8
39049.4029 | 0 | 0 | 8
39049.4034 | 0 | 0 | 8
39049.4039 | 0 | 0 | 8
39049.4043 | 0 | 0 | 8
39049.4048 | 0 | 0 | 8
39049.4053 | 0 | 0 | 8
39049.4058 | 0 | 0 | 8
39049.4063 | 0 | 0 | 8
39049.4068 | 0 | 0 | 8
39049.4073 | 0 | 0 | 8
39049.4077 | 0 | 0 | 8
39049.4082 | 0 | 1 | 8
39049.4087 | 0 | 0 | 8
39049.4092 | 0 | 0 | 8
39049.4097 | 1 | 0 | 8
39049.4102 | 0 | 0 | 8
39049.4107 | 0 | 0 | 8
39049.4111 | 1 | 0 | 8
39049.4116 | 0 | 0 | 8
39049.4121 | 0 | 0 | 8
39049.4126 | 0 | 0 | 8
39049.4131 | 0 | 0 | 8
39049.4136 | 0 | 0 | 8
39049.4141 | 1 | 0 | 8
39049.4145 | 0 | 0 | 8
39049.415 | 0 | 0 | 8
39049.4155 | 1 | 0 | 8
39049.416 | 1 | 0 | 8
39049.4165 | 1 | 0 | 8
39049.417 | 0 | 0 | 8
39049.4175 | 0 | 0 | 8
39049.418 | 0 | 0 | 8
39049.4189 | 1 | 0 | 8
39049.4194 | 0 | 0 | 8
39049.4199 | 0 | 0 | 8
39049.4204 | 1 | 0 | 8
39049.4209 | 1 | 0 | 8
39049.4214 | 0 | 0 | 8
8
39049.3844 | 0 | 0 | 9
39049.3849 | 0 | 0 | 9
39049.3854 | 0 | 0 | 9
39049.3859 | 0 | 0 | 9
39049.3864 | 0 | 0 | 9
39049.3869 | 0 | 0 | 9
39049.3873 | 0 | 0 | 9
39049.3878 | 0 | 0 | 9
39049.3883 | 0 | 0 | 9
39049.3888 | 0 | 0 | 9
39049.3893 | 0 | 0 | 9
39049.3898 | 0 | 0 | 9
39049.3903 | 0 | 0 | 9
39049.3908 | 0 | 0 | 9
39049.3912 | 0 | 0 | 9
39049.3917 | 0 | 0 | 9
39049.3922 | 0 | 0 | 9
39049.3927 | 0 | 0 | 9
39049.3932 | 0 | 0 | 9
39049.3937 | 0 | 0 | 9
39049.3942 | 0 | 0 | 9
39049.3946 | 0 | 0 | 9
39049.3951 | 0 | 0 | 9
39049.3956 | 0 | 0 | 9
39049.3961 | 0 | 0 | 9
39049.3966 | 0 | 0 | 9
39049.3971 | 0 | 0 | 9
39049.3976 | 0 | 0 | 9
39049.398 | 0 | 0 | 9
39049.3985 | 0 | 0 | 9
39049.399 | 0 | 0 | 9
39049.3995 | 0 | 0 | 9
39049.4 | 0 | 0 | 9
39049.4005 | 0 | 0 | 9
39049.401 | 0 | 0 | 9
39049.4014 | 0 | 0 | 9
39049.4019 | 0 | 0 | 9
39049.4024 | 0 | 0 | 9
39049.4029 | 0 | 1 | 9
39049.4034 | 0 | 0 | 9
39049.4039 | 0 | 0 | 9
39049.4044 | 0 | 0 | 9
39049.4048 | 0 | 0 | 9
39049.4053 | 0 | 0 | 9
39049.4058 | 0 | 0 | 9
39049.4063 | 0 | 0 | 9
39049.4068 | 0 | 0 | 9
39049.4073 | 0 | 0 | 9
39049.4078 | 0 | 0 | 9
39049.4083 | 0 | 0 | 9
39049.4087 | 0 | 0 | 9
39049.4092 | 2235 | 0 | 9
39049.4097 | 2454 | 0 | 9
39049.4102 | 2161 | 0 | 9
39049.4107 | 2369 | 0 | 9
39049.4112 | 2082 | 0 | 9
39049.4117 | 1973 | 0 | 9
39049.4121 | 2164 | 0 | 9
39049.4126 | 2208 | 0 | 9
39049.4131 | 2308 | 0 | 9
39049.4136 | 2151 | 0 | 9
39049.4141 | 1954 | 0 | 9
39049.4146 | 2456 | 0 | 9
39049.4151 | 2230 | 0 | 9
39049.4155 | 1946 | 0 | 9
39049.416 | 2231 | 0 | 9
39049.4165 | 2337 | 0 | 9
39049.417 | 2429 | 0 | 9
39049.4175 | 1859 | 0 | 9
39049.418 | 2317 | 0 | 9
39049.4185 | 2407 | 0 | 9
39049.4189 | 2371 | 0 | 9
39049.4194 | 2382 | 0 | 9
39049.4199 | 2282 | 0 | 9
39049.4204 | 2215 | 0 | 9
39049.4209 | 1923 | 0 | 9
39049.4214 | 1948 | 0 | 9
9
39049.3845 | 0 | 0 | 10
39049.3849 | 0 | 0 | 10
39049.3854 | 0 | 0 | 10
39049.3859 | 0 | 0 | 10
39049.3864 | 0 | 0 | 10
39049.3869 | 0 | 0 | 10
39049.3874 | 0 | 0 | 10
39049.3878 | 0 | 0 | 10
39049.3883 | 0 | 0 | 10
39049.3888 | 0 | 0 | 10
39049.3893 | 0 | 0 | 10
39049.3898 | 0 | 0 | 10
39049.3903 | 0 | 0 | 10
39049.3908 | 0 | 0 | 10
39049.3913 | 0 | 0 | 10
39049.3917 | 0 | 0 | 10
39049.3922 | 0 | 0 | 10
39049.3927 | 0 | 0 | 10
39049.3932 | 0 | 0 | 10
39049.3937 | 0 | 0 | 10
39049.3942 | 0 | 0 | 10
39049.3947 | 0 | 0 | 10
39049.3951 | 0 | 0 | 10
39049.3956 | 0 | 0 | 10
39049.3961 | 0 | 0 | 10
39049.3966 | 0 | 0 | 10
39049.3971 | 0 | 0 | 10
39049.3976 | 0 | 0 | 10
39049.3981 | 0 | 0 | 10
39049.3985 | 0 | 0 | 10
39049.399 | 0 | 0 | 10
39049.3995 | 0 | 0 | 10
39049.4 | 0 | 0 | 10
39049.4005 | 0 | 0 | 10
39049.401 | 0 | 0 | 10
39049.4015 | 0 | 0 | 10
39049.4019 | 0 | 0 | 10
39049.4024 | 0 | 0 | 10
39049.4029 | 0 | 0 | 10
39049.4034 | 0 | 0 | 10
39049.4039 | 0 | 0 | 10
39049.4044 | 0 | 0 | 10
39049.4049 | 0 | 0 | 10
39049.4053 | 0 | 0 | 10
39049.4058 | 0 | 0 | 10
39049.4063 | 0 | 0 | 10
39049.4068 | 0 | 0 | 10
39049.4073 | 0 | 0 | 10
39049.4078 | 0 | 0 | 10
39049.4083 | 0 | 0 | 10
39049.4088 | 0 | 0 | 10
39049.4092 | 0 | 0 | 10
39049.4097 | 0 | 0 | 10
39049.4102 | 0 | 0 | 10
39049.4107 | 0 | 0 | 10
39049.4112 | 0 | 0 | 10
39049.4117 | 0 | 0 | 10
39049.4122 | 0 | 0 | 10
39049.4126 | 0 | 0 | 10
39049.4131 | 0 | 0 | 10
39049.4136 | 0 | 0 | 10
39049.4141 | 0 | 0 | 10
39049.4146 | 0 | 0 | 10
39049.4151 | 0 | 0 | 10
39049.4156 | 0 | 0 | 10
39049.416 | 0 | 0 | 10
39049.4165 | 0 | 0 | 10
39049.417 | 0 | 0 | 10
39049.4175 | 0 | 0 | 10
39049.418 | 0 | 0 | 10
39049.4185 | 0 | 0 | 10
39049.419 | 0 | 0 | 10
39049.4194 | 0 | 0 | 10
39049.4199 | 0 | 0 | 10
39049.4204 | 0 | 0 | 10
39049.4209 | 0 | 0 | 10
39049.4214 | 0 | 0 | 10
10
39049.3845 | 0 | 0 | 11
39049.385 | 0 | 0 | 11
39049.3854 | 0 | 0 | 11
39049.3859 | 0 | 0 | 11
39049.3864 | 0 | 0 | 11
39049.3869 | 0 | 0 | 11
39049.3874 | 0 | 0 | 11
39049.3879 | 0 | 0 | 11
39049.3884 | 0 | 0 | 11
39049.3888 | 0 | 0 | 11
39049.3893 | 0 | 0 | 11
39049.3898 | 0 | 0 | 11
39049.3903 | 0 | 0 | 11
39049.3908 | 0 | 0 | 11
39049.3913 | 0 | 0 | 11
39049.3918 | 0 | 0 | 11
39049.3922 | 0 | 0 | 11
39049.3927 | 0 | 0 | 11
39049.3932 | 0 | 0 | 11
39049.3937 | 0 | 0 | 11
39049.3942 | 0 | 0 | 11
39049.3947 | 0 | 0 | 11
39049.3952 | 0 | 0 | 11
39049.3956 | 0 | 0 | 11
39049.3961 | 0 | 0 | 11
39049.3966 | 0 | 0 | 11
39049.3971 | 0 | 0 | 11
39049.3976 | 0 | 0 | 11
39049.3981 | 0 | 0 | 11
39049.3986 | 0 | 0 | 11
39049.3991 | 0 | 0 | 11
39049.3995 | 0 | 0 | 11
39049.4 | 0 | 0 | 11
39049.4005 | 0 | 0 | 11
39049.401 | 0 | 0 | 11
39049.4015 | 0 | 0 | 11
39049.402 | 0 | 0 | 11
39049.4025 | 0 | 0 | 11
39049.4029 | 0 | 0 | 11
39049.4034 | 0 | 0 | 11
39049.4039 | 0 | 0 | 11
39049.4044 | 0 | 0 | 11
39049.4049 | 0 | 0 | 11
39049.4054 | 0 | 0 | 11
39049.4059 | 0 | 0 | 11
39049.4063 | 0 | 0 | 11
39049.4068 | 0 | 0 | 11
39049.4073 | 0 | 0 | 11
39049.4078 | 0 | 0 | 11
39049.4083 | 0 | 0 | 11
39049.4088 | 0 | 0 | 11
39049.4093 | 297 | 0 | 11
39049.4097 | 2211 | 0 | 11
39049.4102 | 1956 | 0 | 11
39049.4107 | 2129 | 0 | 11
39049.4112 | 2354 | 0 | 11
39049.4117 | 2024 | 0 | 11
39049.4122 | 2172 | 0 | 11
39049.4127 | 2101 | 0 | 11
39049.4131 | 2211 | 0 | 11
39049.4136 | 1898 | 0 | 11
39049.4141 | 1885 | 0 | 11
39049.4146 | 2119 | 0 | 11
39049.4151 | 2372 | 3 | 11
39049.4156 | 1906 | 11 | 11
39049.4161 | 1856 | 4 | 11
39049.4165 | 2027 | 1 | 11
39049.417 | 2362 | 0 | 11
39049.4175 | 1957 | 1 | 11
39049.418 | 2180 | 0 | 11
39049.4185 | 2044 | 0 | 11
39049.419 | 2429 | 0 | 11
39049.4195 | 2273 | 0 | 11
39049.4199 | 2331 | 0 | 11
39049.4204 | 2066 | 0 | 11
39049.4209 | 2325 | 1 | 11
39049.4214 | 2294 | 0 | 11
11
39049.3845 | 0 | 0 | 12
39049.385 | 0 | 0 | 12
39049.3855 | 0 | 0 | 12
39049.3859 | 0 | 0 | 12
39049.3864 | 0 | 0 | 12
39049.3869 | 0 | 0 | 12
39049.3874 | 0 | 0 | 12
39049.3879 | 0 | 0 | 12
39049.3884 | 0 | 0 | 12
39049.3889 | 0 | 0 | 12
39049.3893 | 0 | 0 | 12
39049.3898 | 0 | 0 | 12
39049.3903 | 0 | 0 | 12
39049.3908 | 0 | 0 | 12
39049.3913 | 0 | 0 | 12
39049.3918 | 0 | 0 | 12
39049.3923 | 0 | 0 | 12
39049.3927 | 0 | 0 | 12
39049.3932 | 0 | 0 | 12
39049.3937 | 0 | 0 | 12
39049.3942 | 0 | 0 | 12
39049.3947 | 0 | 0 | 12
39049.3952 | 0 | 0 | 12
39049.3957 | 0 | 0 | 12
39049.3961 | 0 | 0 | 12
39049.3966 | 0 | 0 | 12
39049.3971 | 0 | 0 | 12
39049.3976 | 0 | 0 | 12
39049.3981 | 0 | 0 | 12
39049.3986 | 0 | 0 | 12
39049.3991 | 0 | 0 | 12
39049.3995 | 0 | 0 | 12
39049.4 | 0 | 0 | 12
39049.4005 | 0 | 0 | 12
39049.401 | 0 | 0 | 12
39049.4015 | 0 | 0 | 12
39049.402 | 0 | 0 | 12
39049.4025 | 0 | 0 | 12
39049.403 | 0 | 0 | 12
39049.4034 | 0 | 0 | 12
39049.4039 | 0 | 0 | 12
39049.4044 | 0 | 0 | 12
39049.4049 | 0 | 0 | 12
39049.4054 | 0 | 1 | 12
39049.4059 | 0 | 0 | 12
39049.4064 | 0 | 0 | 12
39049.4068 | 2135 | 2 | 12
39049.4073 | 2124 | 0 | 12
39049.4078 | 2210 | 0 | 12
39049.4083 | 2479 | 0 | 12
39049.4088 | 2421 | 0 | 12
39049.4093 | 2528 | 0 | 12
39049.4098 | 2209 | 0 | 12
39049.4102 | 2241 | 0 | 12
39049.4107 | 2477 | 0 | 12
39049.4112 | 2294 | 0 | 12
39049.4117 | 2434 | 0 | 12
39049.4122 | 2114 | 0 | 12
39049.4127 | 2469 | 0 | 12
39049.4132 | 2097 | 0 | 12
39049.4136 | 2297 | 0 | 12
39049.4141 | 2136 | 0 | 12
39049.4146 | 2030 | 0 | 12
39049.4151 | 2220 | 2 | 12
39049.4156 | 1895 | 6 | 12
39049.4161 | 2419 | 4 | 12
39049.4166 | 1962 | 6 | 12
39049.417 | 1901 | 0 | 12
39049.4175 | 2257 | 0 | 12
39049.418 | 2061 | 1 | 12
39049.4185 | 1972 | 0 | 12
39049.419 | 2358 | 0 | 12
39049.4195 | 2237 | 0 | 12
39049.42 | 1991 | 0 | 12
39049.4205 | 2037 | 0 | 12
39049.4209 | 2524 | 0 | 12
39049.4214 | 2159 | 0 | 12
12
39049.3845 | 0 | 0 | 13
39049.385 | 0 | 0 | 13
39049.3855 | 0 | 0 | 13
39049.386 | 0 | 0 | 13
39049.3864 | 0 | 0 | 13
39049.3869 | 0 | 0 | 13
39049.3874 | 0 | 0 | 13
39049.3879 | 0 | 0 | 13
39049.3884 | 0 | 0 | 13
39049.3889 | 0 | 0 | 13
39049.3894 | 0 | 0 | 13
39049.3898 | 0 | 0 | 13
39049.3903 | 0 | 0 | 13
39049.3908 | 0 | 0 | 13
39049.3913 | 0 | 0 | 13
39049.3918 | 0 | 0 | 13
39049.3923 | 0 | 0 | 13
39049.3928 | 0 | 0 | 13
39049.3933 | 0 | 0 | 13
39049.3937 | 0 | 0 | 13
39049.3942 | 0 | 0 | 13
39049.3947 | 0 | 0 | 13
39049.3952 | 0 | 0 | 13
39049.3957 | 0 | 0 | 13
39049.3962 | 0 | 0 | 13
39049.3966 | 0 | 0 | 13
39049.3971 | 0 | 0 | 13
39049.3976 | 0 | 0 | 13
39049.3981 | 0 | 0 | 13
39049.3986 | 0 | 0 | 13
39049.3991 | 0 | 0 | 13
39049.3996 | 0 | 0 | 13
39049.4 | 0 | 0 | 13
39049.4005 | 0 | 0 | 13
39049.401 | 0 | 0 | 13
39049.4015 | 0 | 0 | 13
39049.402 | 0 | 0 | 13
39049.4025 | 0 | 0 | 13
39049.403 | 0 | 0 | 13
39049.4034 | 0 | 0 | 13
39049.4039 | 0 | 0 | 13
39049.4044 | 0 | 0 | 13
39049.4049 | 0 | 0 | 13
39049.4054 | 0 | 0 | 13
39049.4059 | 0 | 0 | 13
39049.4064 | 0 | 0 | 13
39049.4069 | 0 | 0 | 13
39049.4073 | 0 | 0 | 13
39049.4078 | 0 | 0 | 13
39049.4083 | 0 | 0 | 13
39049.4088 | 0 | 0 | 13
39049.4093 | 1966 | 0 | 13
39049.4098 | 2452 | 0 | 13
39049.4103 | 2235 | 0 | 13
39049.4107 | 2383 | 0 | 13
39049.4112 | 2212 | 0 | 13
39049.4117 | 2436 | 0 | 13
39049.4122 | 2416 | 0 | 13
39049.4127 | 2004 | 0 | 13
39049.4132 | 1897 | 0 | 13
39049.4137 | 1896 | 0 | 13
39049.4141 | 2438 | 0 | 13
39049.4146 | 2430 | 0 | 13
39049.4151 | 2153 | 1 | 13
39049.4156 | 2130 | 6 | 13
39049.4161 | 1851 | 5 | 13
39049.4166 | 1876 | 4 | 13
39049.4171 | 2156 | 1 | 13
39049.4175 | 2232 | 0 | 13
39049.418 | 2207 | 0 | 13
39049.4185 | 2237 | 0 | 13
39049.419 | 1925 | 0 | 13
39049.4195 | 2441 | 0 | 13
39049.42 | 1944 | 0 | 13
39049.4205 | 2203 | 0 | 13
39049.4209 | 2064 | 0 | 13
39049.4214 | 2213 | 0 | 13
13
39049.3845 | 0 | 0 | 14
39049.385 | 0 | 0 | 14
39049.3855 | 0 | 0 | 14
39049.386 | 0 | 0 | 14
39049.3865 | 0 | 0 | 14
39049.3869 | 0 | 0 | 14
39049.3874 | 0 | 0 | 14
39049.3879 | 0 | 0 | 14
39049.3884 | 0 | 0 | 14
39049.3889 | 0 | 0 | 14
39049.3894 | 0 | 0 | 14
39049.3899 | 0 | 0 | 14
39049.3903 | 0 | 0 | 14
39049.3908 | 0 | 0 | 14
39049.3913 | 0 | 0 | 14
39049.3918 | 0 | 0 | 14
39049.3923 | 0 | 0 | 14
39049.3928 | 0 | 0 | 14
39049.3933 | 0 | 0 | 14
39049.3938 | 0 | 0 | 14
39049.3942 | 0 | 0 | 14
39049.3947 | 0 | 0 | 14
39049.3952 | 0 | 0 | 14
39049.3957 | 0 | 0 | 14
39049.3962 | 0 | 0 | 14
39049.3967 | 0 | 0 | 14
39049.3972 | 0 | 0 | 14
39049.3976 | 0 | 0 | 14
39049.3981 | 0 | 0 | 14
39049.3986 | 0 | 0 | 14
39049.3991 | 0 | 0 | 14
39049.3996 | 0 | 0 | 14
39049.4001 | 0 | 0 | 14
39049.4006 | 0 | 0 | 14
39049.401 | 0 | 0 | 14
39049.4015 | 0 | 0 | 14
39049.402 | 0 | 0 | 14
39049.4025 | 0 | 0 | 14
39049.403 | 0 | 0 | 14
39049.4035 | 0 | 0 | 14
39049.404 | 0 | 0 | 14
39049.4044 | 0 | 0 | 14
39049.4049 | 0 | 0 | 14
39049.4054 | 0 | 0 | 14
39049.4059 | 0 | 0 | 14
39049.4064 | 0 | 0 | 14
39049.4069 | 0 | 0 | 14
39049.4074 | 0 | 0 | 14
39049.4078 | 0 | 0 | 14
39049.4083 | 0 | 0 | 14
39049.4088 | 0 | 0 | 14
39049.4093 | 485 | 0 | 14
39049.4098 | 2298 | 0 | 14
39049.4103 | 2056 | 0 | 14
39049.4108 | 1975 | 0 | 14
39049.4112 | 1988 | 0 | 14
39049.4117 | 2489 | 0 | 14
39049.4122 | 2040 | 0 | 14
39049.4127 | 2177 | 0 | 14
39049.4132 | 1906 | 0 | 14
39049.4137 | 1918 | 0 | 14
39049.4142 | 2340 | 0 | 14
39049.4147 | 1900 | 0 | 14
39049.4151 | 1870 | 3 | 14
39049.4156 | 1801 | 6 | 14
39049.4161 | 2289 | 4 | 14
39049.4166 | 2162 | 4 | 14
39049.4171 | 1863 | 0 | 14
39049.4176 | 2431 | 0 | 14
39049.4181 | 2369 | 0 | 14
39049.4185 | 2228 | 0 | 14
39049.419 | 2172 | 0 | 14
39049.4195 | 1965 | 0 | 14
39049.42 | 2430 | 0 | 14
39049.4205 | 2318 | 0 | 14
39049.421 | 1907 | 0 | 14
39049.4215 | 2243 | 0 | 14
14
39049.3845 | 0 | 0 | 15
39049.385 | 0 | 0 | 15
39049.3855 | 0 | 0 | 15
39049.386 | 0 | 0 | 15
39049.3865 | 0 | 0 | 15
39049.387 | 0 | 0 | 15
39049.3874 | 0 | 0 | 15
39049.3879 | 0 | 0 | 15
39049.3884 | 0 | 0 | 15
39049.3889 | 0 | 0 | 15
39049.3894 | 0 | 0 | 15
39049.3899 | 0 | 0 | 15
39049.3904 | 0 | 0 | 15
39049.3908 | 0 | 0 | 15
39049.3913 | 0 | 0 | 15
39049.3918 | 0 | 0 | 15
39049.3923 | 0 | 0 | 15
39049.3928 | 0 | 0 | 15
39049.3933 | 0 | 0 | 15
39049.3938 | 0 | 0 | 15
39049.3942 | 0 | 0 | 15
39049.3947 | 0 | 0 | 15
39049.3952 | 0 | 0 | 15
39049.3957 | 0 | 0 | 15
39049.3962 | 0 | 0 | 15
39049.3967 | 0 | 0 | 15
39049.3972 | 0 | 0 | 15
39049.3977 | 0 | 0 | 15
39049.3981 | 0 | 0 | 15
39049.3986 | 0 | 0 | 15
39049.3991 | 0 | 0 | 15
39049.3996 | 0 | 0 | 15
39049.4001 | 0 | 0 | 15
39049.4006 | 0 | 0 | 15
39049.4011 | 0 | 0 | 15
39049.4015 | 0 | 0 | 15
39049.402 | 0 | 0 | 15
39049.4025 | 0 | 0 | 15
39049.403 | 0 | 0 | 15
39049.4035 | 0 | 0 | 15
39049.404 | 0 | 0 | 15
39049.4045 | 0 | 0 | 15
39049.4049 | 0 | 0 | 15
39049.4054 | 0 | 0 | 15
39049.4059 | 0 | 0 | 15
39049.4064 | 0 | 0 | 15
39049.4069 | 0 | 0 | 15
39049.4074 | 0 | 0 | 15
39049.4079 | 0 | 0 | 15
39049.4083 | 0 | 0 | 15
39049.4088 | 0 | 0 | 15
39049.4093 | 802 | 0 | 15
39049.4098 | 2208 | 0 | 15
39049.4103 | 2184 | 0 | 15
39049.4108 | 1902 | 0 | 15
39049.4113 | 2393 | 0 | 15
39049.4117 | 2048 | 0 | 15
39049.4122 | 2270 | 0 | 15
39049.4127 | 1973 | 0 | 15
39049.4132 | 2466 | 0 | 15
39049.4137 | 2198 | 0 | 15
39049.4142 | 1907 | 0 | 15
39049.4147 | 2136 | 0 | 15
39049.4152 | 2308 | 0 | 15
39049.4156 | 1838 | 0 | 15
39049.4161 | 1830 | 0 | 15
39049.4166 | 2078 | 0 | 15
39049.4171 | 2231 | 0 | 15
39049.4176 | 1860 | 0 | 15
39049.4181 | 2362 | 0 | 15
39049.4186 | 2047 | 0 | 15
39049.419 | 2051 | 0 | 15
39049.4195 | 2414 | 0 | 15
39049.42 | 2460 | 0 | 15
39049.4205 | 1882 | 0 | 15
39049.421 | 2240 | 0 | 15
39049.4215 | 1883 | 0 | 15
15
39049.3845 | 0 | 0 | 16
39049.385 | 0 | 0 | 16
39049.3855 | 0 | 0 | 16
39049.386 | 0 | 0 | 16
39049.3865 | 0 | 0 | 16
39049.387 | 0 | 0 | 16
39049.3875 | 0 | 0 | 16
39049.388 | 0 | 0 | 16
39049.3884 | 0 | 0 | 16
39049.3889 | 0 | 0 | 16
39049.3894 | 0 | 0 | 16
39049.3899 | 0 | 0 | 16
39049.3904 | 0 | 0 | 16
39049.3909 | 0 | 0 | 16
39049.3914 | 0 | 0 | 16
39049.3918 | 0 | 0 | 16
39049.3923 | 0 | 0 | 16
39049.3928 | 0 | 0 | 16
39049.3933 | 0 | 0 | 16
39049.3938 | 0 | 0 | 16
39049.3943 | 0 | 0 | 16
39049.3948 | 0 | 0 | 16
39049.3952 | 0 | 0 | 16
39049.3957 | 0 | 0 | 16
39049.3962 | 0 | 0 | 16
39049.3967 | 0 | 0 | 16
39049.3972 | 0 | 0 | 16
39049.3977 | 0 | 0 | 16
39049.3982 | 0 | 0 | 16
39049.3986 | 0 | 0 | 16
39049.3991 | 0 | 0 | 16
39049.3996 | 0 | 0 | 16
39049.4001 | 0 | 0 | 16
39049.4006 | 0 | 0 | 16
39049.4011 | 0 | 0 | 16
39049.4016 | 0 | 0 | 16
39049.402 | 0 | 0 | 16
39049.4025 | 0 | 0 | 16
39049.403 | 0 | 0 | 16
39049.4035 | 0 | 0 | 16
39049.404 | 0 | 0 | 16
39049.4045 | 0 | 0 | 16
39049.405 | 0 | 0 | 16
39049.4055 | 0 | 0 | 16
39049.4059 | 0 | 0 | 16
39049.4064 | 0 | 0 | 16
39049.4069 | 0 | 0 | 16
39049.4074 | 0 | 0 | 16
39049.4079 | 0 | 0 | 16
39049.4084 | 0 | 0 | 16
39049.4088 | 0 | 0 | 16
39049.4093 | 1 | 0 | 16
39049.4098 | 1 | 0 | 16
39049.4103 | 1 | 0 | 16
39049.4108 | 0 | 0 | 16
39049.4113 | 0 | 0 | 16
39049.4118 | 1 | 0 | 16
39049.4122 | 0 | 0 | 16
39049.4127 | 0 | 0 | 16
39049.4132 | 1 | 0 | 16
39049.4137 | 0 | 0 | 16
39049.4142 | 1 | 0 | 16
39049.4147 | 0 | 0 | 16
39049.4152 | 0 | 0 | 16
39049.4156 | 0 | 0 | 16
39049.4161 | 0 | 0 | 16
39049.4166 | 0 | 0 | 16
39049.4171 | 0 | 0 | 16
39049.4176 | 0 | 0 | 16
39049.4181 | 0 | 0 | 16
39049.4186 | 1 | 0 | 16
39049.4191 | 1 | 0 | 16
39049.4195 | 1 | 0 | 16
39049.42 | 0 | 0 | 16
39049.4205 | 0 | 0 | 16
39049.421 | 0 | 0 | 16
39049.4215 | 0 | 0 | 16
16
39049.3846 | 0 | 0 | 17
39049.385 | 0 | 0 | 17
39049.3855 | 0 | 0 | 17
39049.386 | 0 | 0 | 17
39049.3865 | 0 | 0 | 17
39049.387 | 0 | 0 | 17
39049.3875 | 0 | 0 | 17
39049.388 | 0 | 0 | 17
39049.3884 | 0 | 0 | 17
39049.3889 | 0 | 0 | 17
39049.3894 | 0 | 0 | 17
39049.3899 | 0 | 0 | 17
39049.3904 | 0 | 0 | 17
39049.3909 | 0 | 0 | 17
39049.3914 | 0 | 0 | 17
39049.3919 | 0 | 0 | 17
39049.3923 | 0 | 0 | 17
39049.3928 | 0 | 0 | 17
39049.3933 | 0 | 0 | 17
39049.3938 | 0 | 0 | 17
39049.3943 | 0 | 0 | 17
39049.3948 | 0 | 0 | 17
39049.3953 | 0 | 0 | 17
39049.3957 | 0 | 0 | 17
39049.3962 | 0 | 0 | 17
39049.3967 | 0 | 0 | 17
39049.3972 | 0 | 0 | 17
39049.3977 | 0 | 0 | 17
39049.3982 | 0 | 0 | 17
39049.3987 | 0 | 0 | 17
39049.3991 | 0 | 0 | 17
39049.3996 | 0 | 0 | 17
39049.4001 | 0 | 0 | 17
39049.4006 | 0 | 0 | 17
39049.4011 | 0 | 0 | 17
39049.4016 | 0 | 0 | 17
39049.4021 | 0 | 0 | 17
39049.4025 | 0 | 0 | 17
39049.403 | 0 | 0 | 17
39049.4035 | 0 | 0 | 17
39049.404 | 0 | 0 | 17
39049.4045 | 0 | 0 | 17
39049.405 | 0 | 0 | 17
39049.4055 | 0 | 0 | 17
39049.4059 | 0 | 0 | 17
39049.4064 | 0 | 0 | 17
39049.4069 | 0 | 0 | 17
39049.4074 | 0 | 0 | 17
39049.4079 | 0 | 0 | 17
39049.4084 | 0 | 0 | 17
39049.4089 | 0 | 0 | 17
39049.4094 | 2311 | 1 | 17
39049.4098 | 2262 | 0 | 17
39049.4103 | 1954 | 0 | 17
39049.4108 | 2282 | 0 | 17
39049.4113 | 2049 | 0 | 17
39049.4118 | 2113 | 0 | 17
39049.4123 | 2227 | 0 | 17
39049.4128 | 2069 | 0 | 17
39049.4132 | 1992 | 0 | 17
39049.4137 | 2198 | 0 | 17
39049.4142 | 2442 | 0 | 17
39049.4147 | 2313 | 0 | 17
39049.4152 | 2258 | 0 | 17
39049.4157 | 2225 | 0 | 17
39049.4162 | 1949 | 0 | 17
39049.4166 | 2298 | 0 | 17
39049.4171 | 1934 | 0 | 17
39049.4176 | 2330 | 0 | 17
39049.4181 | 2190 | 0 | 17
39049.4186 | 2476 | 0 | 17
39049.4191 | 2032 | 0 | 17
39049.4196 | 2077 | 0 | 17
39049.42 | 2278 | 0 | 17
39049.4205 | 1880 | 0 | 17
39049.421 | 2476 | 0 | 17
39049.4215 | 2464 | 0 | 17
17
39049.3846 | 0 | 0 | 18
39049.3851 | 0 | 0 | 18
39049.3856 | 0 | 0 | 18
39049.386 | 0 | 0 | 18
39049.3865 | 0 | 0 | 18
39049.387 | 0 | 0 | 18
39049.3875 | 0 | 0 | 18
39049.388 | 0 | 0 | 18
39049.3885 | 0 | 0 | 18
39049.389 | 0 | 0 | 18
39049.3894 | 0 | 0 | 18
39049.3899 | 0 | 0 | 18
39049.3904 | 0 | 0 | 18
39049.3909 | 0 | 0 | 18
39049.3914 | 0 | 0 | 18
39049.3919 | 0 | 0 | 18
39049.3924 | 0 | 0 | 18
39049.3928 | 0 | 0 | 18
39049.3933 | 0 | 0 | 18
39049.3938 | 0 | 0 | 18
39049.3943 | 0 | 0 | 18
39049.3948 | 0 | 0 | 18
39049.3953 | 0 | 0 | 18
39049.3958 | 0 | 0 | 18
39049.3962 | 0 | 0 | 18
39049.3967 | 0 | 0 | 18
39049.3972 | 0 | 0 | 18
39049.3977 | 0 | 0 | 18
39049.3982 | 0 | 0 | 18
39049.3987 | 0 | 0 | 18
39049.3992 | 0 | 0 | 18
39049.3996 | 0 | 0 | 18
39049.4001 | 0 | 0 | 18
39049.4006 | 0 | 0 | 18
39049.4011 | 0 | 0 | 18
39049.4016 | 0 | 0 | 18
39049.4021 | 0 | 0 | 18
39049.4026 | 0 | 0 | 18
39049.403 | 0 | 0 | 18
39049.4035 | 0 | 0 | 18
39049.404 | 0 | 0 | 18
39049.4045 | 0 | 0 | 18
39049.405 | 0 | 0 | 18
39049.4055 | 0 | 0 | 18
39049.406 | 0 | 0 | 18
39049.4064 | 0 | 0 | 18
39049.4069 | 0 | 0 | 18
39049.4074 | 0 | 0 | 18
39049.4079 | 0 | 0 | 18
39049.4084 | 0 | 0 | 18
39049.4089 | 0 | 0 | 18
39049.4094 | 0 | 0 | 18
39049.4098 | 0 | 0 | 18
39049.4103 | 1 | 0 | 18
39049.4108 | 0 | 0 | 18
39049.4113 | 0 | 0 | 18
39049.4118 | 0 | 0 | 18
39049.4123 | 0 | 0 | 18
39049.4128 | 0 | 0 | 18
39049.4133 | 1 | 0 | 18
39049.4137 | 0 | 0 | 18
39049.4142 | 0 | 0 | 18
39049.4147 | 1 | 0 | 18
39049.4152 | 0 | 0 | 18
39049.4157 | 0 | 0 | 18
39049.4162 | 0 | 0 | 18
39049.4167 | 0 | 0 | 18
39049.4171 | 0 | 0 | 18
39049.4176 | 0 | 0 | 18
39049.4181 | 0 | 0 | 18
39049.4186 | 1 | 0 | 18
39049.4191 | 0 | 0 | 18
39049.4196 | 0 | 0 | 18
39049.4201 | 0 | 0 | 18
39049.4205 | 0 | 0 | 18
39049.421 | 0 | 0 | 18
39049.4215 | 0 | 0 | 18
18
39049.3846 | 0 | 0 | 19
39049.3851 | 0 | 0 | 19
39049.3856 | 0 | 0 | 19
39049.3861 | 0 | 0 | 19
39049.3865 | 0 | 0 | 19
39049.387 | 0 | 0 | 19
39049.3875 | 0 | 0 | 19
39049.388 | 0 | 0 | 19
39049.3885 | 0 | 0 | 19
39049.389 | 0 | 0 | 19
39049.3895 | 0 | 0 | 19
39049.3899 | 0 | 0 | 19
39049.3904 | 0 | 0 | 19
39049.3909 | 0 | 0 | 19
39049.3914 | 0 | 0 | 19
39049.3919 | 0 | 0 | 19
39049.3924 | 0 | 0 | 19
39049.3929 | 0 | 0 | 19
39049.3933 | 0 | 0 | 19
39049.3938 | 0 | 0 | 19
39049.3943 | 0 | 0 | 19
39049.3948 | 0 | 0 | 19
39049.3953 | 0 | 0 | 19
39049.3958 | 0 | 0 | 19
39049.3963 | 0 | 0 | 19
39049.3967 | 0 | 0 | 19
39049.3972 | 0 | 0 | 19
39049.3977 | 0 | 0 | 19
39049.3982 | 0 | 0 | 19
39049.3987 | 0 | 0 | 19
39049.3992 | 0 | 0 | 19
39049.3997 | 0 | 0 | 19
39049.4002 | 0 | 0 | 19
39049.4006 | 0 | 0 | 19
39049.4011 | 0 | 0 | 19
39049.4016 | 0 | 0 | 19
39049.4021 | 0 | 0 | 19
39049.4026 | 0 | 0 | 19
39049.4031 | 0 | 0 | 19
39049.4036 | 0 | 0 | 19
39049.404 | 0 | 0 | 19
39049.4045 | 0 | 0 | 19
39049.405 | 0 | 0 | 19
39049.4055 | 0 | 0 | 19
39049.406 | 0 | 0 | 19
39049.4065 | 0 | 0 | 19
39049.407 | 2383 | 0 | 19
39049.4074 | 2263 | 0 | 19
39049.4079 | 2227 | 0 | 19
39049.4084 | 2503 | 0 | 19
39049.4089 | 1987 | 1 | 19
39049.4094 | 1934 | 0 | 19
39049.4099 | 2526 | 0 | 19
39049.4104 | 2219 | 0 | 19
39049.4108 | 1939 | 1 | 19
39049.4113 | 2531 | 0 | 19
39049.4118 | 2003 | 0 | 19
39049.4123 | 2161 | 0 | 19
39049.4128 | 1989 | 0 | 19
39049.4133 | 1988 | 0 | 19
39049.4138 | 2527 | 0 | 19
39049.4142 | 2204 | 0 | 19
39049.4147 | 1993 | 0 | 19
39049.4152 | 1978 | 5 | 19
39049.4157 | 1859 | 6 | 19
39049.4162 | 1878 | 3 | 19
39049.4167 | 1908 | 2 | 19
39049.4172 | 2250 | 0 | 19
39049.4177 | 2477 | 1 | 19
39049.4181 | 2043 | 1 | 19
39049.4186 | 2012 | 0 | 19
39049.4191 | 2161 | 0 | 19
39049.4196 | 2435 | 0 | 19
39049.4201 | 2460 | 0 | 19
39049.4206 | 2086 | 0 | 19
39049.4211 | 2032 | 0 | 19
39049.4215 | 1960 | 0 | 19
19
39049.3846 | 0 | 0 | 20
39049.3851 | 0 | 0 | 20
39049.3856 | 0 | 0 | 20
39049.3861 | 0 | 0 | 20
39049.3866 | 0 | 0 | 20
39049.387 | 0 | 0 | 20
39049.3875 | 0 | 0 | 20
39049.388 | 0 | 0 | 20
39049.3885 | 0 | 0 | 20
39049.389 | 0 | 0 | 20
39049.3895 | 0 | 0 | 20
39049.39 | 0 | 0 | 20
39049.3904 | 0 | 0 | 20
39049.3909 | 0 | 0 | 20
39049.3914 | 0 | 0 | 20
39049.3919 | 0 | 0 | 20
39049.3924 | 0 | 0 | 20
39049.3929 | 0 | 0 | 20
39049.3934 | 0 | 0 | 20
39049.3938 | 0 | 0 | 20
39049.3943 | 0 | 0 | 20
39049.3948 | 0 | 0 | 20
39049.3953 | 0 | 0 | 20
39049.3958 | 0 | 0 | 20
39049.3963 | 0 | 0 | 20
39049.3968 | 0 | 0 | 20
39049.3972 | 0 | 0 | 20
39049.3977 | 0 | 0 | 20
39049.3982 | 0 | 0 | 20
39049.3987 | 0 | 0 | 20
39049.3992 | 0 | 0 | 20
39049.3997 | 0 | 0 | 20
39049.4002 | 0 | 0 | 20
39049.4006 | 0 | 0 | 20
39049.4011 | 0 | 0 | 20
39049.4016 | 0 | 0 | 20
39049.4021 | 0 | 0 | 20
39049.4026 | 0 | 0 | 20
39049.4031 | 0 | 0 | 20
39049.4036 | 0 | 0 | 20
39049.4041 | 0 | 0 | 20
39049.4045 | 0 | 0 | 20
39049.405 | 0 | 0 | 20
39049.4055 | 0 | 0 | 20
39049.406 | 0 | 0 | 20
39049.4065 | 0 | 0 | 20
39049.407 | 2466 | 0 | 20
39049.4075 | 2329 | 0 | 20
39049.4079 | 2014 | 0 | 20
39049.4084 | 2001 | 0 | 20
39049.4089 | 2000 | 1 | 20
39049.4094 | 2268 | 0 | 20
39049.4099 | 2447 | 0 | 20
39049.4104 | 2528 | 0 | 20
39049.4109 | 2432 | 0 | 20
39049.4113 | 2542 | 0 | 20
39049.4118 | 1969 | 0 | 20
39049.4123 | 1962 | 0 | 20
39049.4128 | 2297 | 0 | 20
39049.4133 | 2500 | 0 | 20
39049.4138 | 2041 | 0 | 20
39049.4143 | 2186 | 1 | 20
39049.4147 | 2182 | 0 | 20
39049.4152 | 2409 | 3 | 20
39049.4157 | 2390 | 5 | 20
39049.4162 | 2224 | 2 | 20
39049.4167 | 2229 | 1 | 20
39049.4172 | 2289 | 1 | 20
39049.4177 | 2303 | 0 | 20
39049.4181 | 2106 | 0 | 20
39049.4186 | 2098 | 0 | 20
39049.4191 | 2472 | 0 | 20
39049.4196 | 1988 | 0 | 20
39049.4201 | 2309 | 0 | 20
39049.4206 | 2060 | 0 | 20
39049.4211 | 1995 | 0 | 20
39049.4216 | 1922 | 0 | 20
20
39049.3846 | 0 | 0 | 21
39049.3851 | 0 | 0 | 21
39049.3856 | 0 | 0 | 21
39049.3861 | 0 | 0 | 21
39049.3866 | 0 | 0 | 21
39049.3871 | 0 | 0 | 21
39049.3875 | 0 | 0 | 21
39049.388 | 0 | 0 | 21
39049.3885 | 0 | 0 | 21
39049.389 | 0 | 0 | 21
39049.3895 | 0 | 0 | 21
39049.39 | 0 | 0 | 21
39049.3905 | 0 | 0 | 21
39049.3909 | 0 | 0 | 21
39049.3914 | 0 | 0 | 21
39049.3919 | 0 | 0 | 21
39049.3924 | 0 | 0 | 21
39049.3929 | 0 | 0 | 21
39049.3934 | 0 | 0 | 21
39049.3939 | 0 | 0 | 21
39049.3944 | 0 | 0 | 21
39049.3948 | 0 | 0 | 21
39049.3953 | 0 | 0 | 21
39049.3958 | 0 | 0 | 21
39049.3963 | 0 | 0 | 21
39049.3968 | 0 | 0 | 21
39049.3973 | 0 | 0 | 21
39049.3978 | 0 | 0 | 21
39049.3982 | 0 | 0 | 21
39049.3987 | 0 | 0 | 21
39049.3992 | 0 | 0 | 21
39049.3997 | 0 | 0 | 21
39049.4002 | 0 | 0 | 21
39049.4007 | 0 | 0 | 21
39049.4012 | 0 | 0 | 21
39049.4016 | 0 | 0 | 21
39049.4021 | 0 | 0 | 21
39049.4026 | 0 | 0 | 21
39049.4031 | 0 | 0 | 21
39049.4036 | 0 | 0 | 21
39049.4041 | 0 | 0 | 21
39049.4046 | 0 | 0 | 21
39049.405 | 0 | 0 | 21
39049.4055 | 0 | 0 | 21
39049.406 | 0 | 0 | 21
39049.4065 | 0 | 0 | 21
39049.407 | 1939 | 0 | 21
39049.4075 | 2441 | 0 | 21
39049.408 | 2405 | 0 | 21
39049.4084 | 2562 | 0 | 21
39049.4089 | 2464 | 0 | 21
39049.4094 | 2382 | 0 | 21
39049.4099 | 2424 | 0 | 21
39049.4104 | 2352 | 0 | 21
39049.4109 | 2286 | 0 | 21
39049.4114 | 2215 | 0 | 21
39049.4118 | 2556 | 0 | 21
39049.4123 | 2014 | 0 | 21
39049.4128 | 2210 | 0 | 21
39049.4133 | 2200 | 0 | 21
39049.4138 | 1963 | 0 | 21
39049.4143 | 2250 | 0 | 21
39049.4148 | 2462 | 0 | 21
39049.4152 | 2441 | 0 | 21
39049.4157 | 2046 | 0 | 21
39049.4162 | 2431 | 0 | 21
39049.4167 | 1930 | 0 | 21
39049.4172 | 1990 | 0 | 21
39049.4177 | 2221 | 0 | 21
39049.4182 | 1928 | 0 | 21
39049.4186 | 2127 | 0 | 21
39049.4191 | 2147 | 0 | 21
39049.4196 | 1960 | 0 | 21
39049.4201 | 2295 | 0 | 21
39049.4206 | 2005 | 0 | 21
39049.4211 | 2394 | 0 | 21
39049.4216 | 2515 | 0 | 21
21
39049.3846 | 0 | 0 | 22
39049.3851 | 0 | 0 | 22
39049.3856 | 0 | 0 | 22
39049.3861 | 0 | 0 | 22
39049.3866 | 0 | 0 | 22
39049.3871 | 0 | 0 | 22
39049.3876 | 0 | 0 | 22
39049.388 | 0 | 0 | 22
39049.3885 | 0 | 0 | 22
39049.389 | 0 | 0 | 22
39049.3895 | 0 | 0 | 22
39049.39 | 0 | 0 | 22
39049.3905 | 0 | 0 | 22
39049.391 | 0 | 0 | 22
39049.3914 | 0 | 0 | 22
39049.3919 | 0 | 0 | 22
39049.3924 | 0 | 0 | 22
39049.3929 | 0 | 0 | 22
39049.3934 | 0 | 0 | 22
39049.3939 | 0 | 0 | 22
39049.3944 | 0 | 0 | 22
39049.3948 | 0 | 0 | 22
39049.3953 | 0 | 0 | 22
39049.3958 | 0 | 0 | 22
39049.3963 | 0 | 0 | 22
39049.3968 | 0 | 0 | 22
39049.3973 | 0 | 0 | 22
39049.3978 | 0 | 0 | 22
39049.3983 | 0 | 0 | 22
39049.3987 | 0 | 0 | 22
39049.3992 | 0 | 0 | 22
39049.3997 | 0 | 0 | 22
39049.4002 | 0 | 0 | 22
39049.4007 | 0 | 0 | 22
39049.4012 | 0 | 0 | 22
39049.4017 | 0 | 0 | 22
39049.4021 | 0 | 0 | 22
39049.4026 | 0 | 0 | 22
39049.4031 | 0 | 0 | 22
39049.4036 | 0 | 0 | 22
39049.4041 | 0 | 0 | 22
39049.4046 | 0 | 0 | 22
39049.4051 | 0 | 0 | 22
39049.4055 | 0 | 0 | 22
39049.406 | 0 | 0 | 22
39049.4065 | 0 | 0 | 22
39049.407 | 0 | 0 | 22
39049.4075 | 0 | 0 | 22
39049.408 | 0 | 0 | 22
39049.4085 | 0 | 0 | 22
39049.4089 | 0 | 0 | 22
39049.4094 | 0 | 0 | 22
39049.4099 | 0 | 0 | 22
39049.4104 | 0 | 0 | 22
39049.4109 | 0 | 0 | 22
39049.4114 | 0 | 0 | 22
39049.4119 | 0 | 0 | 22
39049.4123 | 0 | 0 | 22
39049.4128 | 0 | 0 | 22
39049.4133 | 1 | 0 | 22
39049.4138 | 0 | 0 | 22
39049.4143 | 0 | 0 | 22
39049.4148 | 1 | 0 | 22
39049.4153 | 0 | 0 | 22
39049.4158 | 0 | 0 | 22
39049.4162 | 0 | 0 | 22
39049.4167 | 0 | 0 | 22
39049.4172 | 0 | 0 | 22
39049.4177 | 0 | 0 | 22
39049.4182 | 0 | 0 | 22
39049.4187 | 1 | 0 | 22
39049.4192 | 0 | 0 | 22
39049.4196 | 1 | 0 | 22
39049.4201 | 0 | 0 | 22
39049.4206 | 1 | 0 | 22
39049.4211 | 1 | 0 | 22
39049.4216 | 0 | 0 | 22
22
39049.3847 | 0 | 0 | 23
39049.3852 | 0 | 0 | 23
39049.3856 | 0 | 0 | 23
39049.3861 | 0 | 0 | 23
39049.3866 | 0 | 0 | 23
39049.3871 | 0 | 0 | 23
39049.3876 | 0 | 0 | 23
39049.3881 | 0 | 0 | 23
39049.3886 | 0 | 0 | 23
39049.389 | 0 | 0 | 23
39049.3895 | 0 | 0 | 23
39049.39 | 0 | 0 | 23
39049.3905 | 0 | 0 | 23
39049.391 | 0 | 0 | 23
39049.3915 | 0 | 0 | 23
39049.392 | 0 | 0 | 23
39049.3924 | 0 | 0 | 23
39049.3929 | 0 | 0 | 23
39049.3934 | 0 | 0 | 23
39049.3939 | 0 | 0 | 23
39049.3944 | 0 | 0 | 23
39049.3949 | 0 | 0 | 23
39049.3953 | 0 | 0 | 23
39049.3958 | 0 | 0 | 23
39049.3963 | 0 | 0 | 23
39049.3968 | 0 | 0 | 23
39049.3973 | 0 | 0 | 23
39049.3978 | 0 | 0 | 23
39049.3983 | 0 | 0 | 23
39049.3988 | 0 | 0 | 23
39049.3992 | 0 | 0 | 23
39049.3997 | 0 | 0 | 23
39049.4002 | 0 | 0 | 23
39049.4007 | 0 | 0 | 23
39049.4012 | 0 | 0 | 23
39049.4017 | 0 | 0 | 23
39049.4022 | 0 | 0 | 23
39049.4026 | 0 | 0 | 23
39049.4031 | 0 | 0 | 23
39049.4036 | 0 | 0 | 23
39049.4041 | 0 | 0 | 23
39049.4046 | 0 | 0 | 23
39049.4051 | 0 | 0 | 23
39049.4056 | 0 | 0 | 23
39049.406 | 0 | 0 | 23
39049.4065 | 0 | 0 | 23
39049.407 | 2426 | 0 | 23
39049.4075 | 2358 | 0 | 23
39049.408 | 2218 | 0 | 23
39049.4085 | 1954 | 0 | 23
39049.409 | 2454 | 0 | 23
39049.4094 | 2075 | 0 | 23
39049.4099 | 2007 | 0 | 23
39049.4104 | 2086 | 0 | 23
39049.4109 | 2490 | 0 | 23
39049.4114 | 2495 | 0 | 23
39049.4119 | 2541 | 0 | 23
39049.4124 | 2186 | 0 | 23
39049.4128 | 2092 | 0 | 23
39049.4133 | 2400 | 0 | 23
39049.4138 | 2002 | 0 | 23
39049.4143 | 2479 | 0 | 23
39049.4148 | 2019 | 0 | 23
39049.4153 | 1919 | 0 | 23
39049.4158 | 1897 | 0 | 23
39049.4163 | 1876 | 0 | 23
39049.4167 | 2502 | 0 | 23
39049.4172 | 2254 | 0 | 23
39049.4177 | 1983 | 0 | 23
39049.4182 | 2532 | 0 | 23
39049.4187 | 1996 | 0 | 23
39049.4192 | 2168 | 0 | 23
39049.4197 | 1971 | 0 | 23
39049.4201 | 2310 | 0 | 23
39049.4206 | 2439 | 0 | 23
39049.4211 | 2539 | 0 | 23
39049.4216 | 1962 | 0 | 23
23
39049.3847 | 0 | 0 | 24
39049.3852 | 0 | 0 | 24
39049.3856 | 0 | 0 | 24
39049.3861 | 0 | 0 | 24
39049.3866 | 0 | 0 | 24
39049.3871 | 0 | 0 | 24
39049.3876 | 0 | 0 | 24
39049.3881 | 0 | 0 | 24
39049.3886 | 0 | 0 | 24
39049.3891 | 0 | 0 | 24
39049.3895 | 0 | 0 | 24
39049.39 | 0 | 0 | 24
39049.3905 | 0 | 0 | 24
39049.391 | 0 | 0 | 24
39049.3915 | 0 | 0 | 24
39049.392 | 0 | 0 | 24
39049.3925 | 0 | 0 | 24
39049.3929 | 0 | 0 | 24
39049.3934 | 0 | 0 | 24
39049.3939 | 0 | 0 | 24
39049.3944 | 0 | 0 | 24
39049.3949 | 0 | 0 | 24
39049.3954 | 0 | 0 | 24
39049.3959 | 0 | 0 | 24
39049.3963 | 0 | 0 | 24
39049.3968 | 0 | 0 | 24
39049.3973 | 0 | 0 | 24
39049.3978 | 0 | 0 | 24
39049.3983 | 0 | 0 | 24
39049.3988 | 0 | 0 | 24
39049.3993 | 0 | 0 | 24
39049.3997 | 0 | 0 | 24
39049.4002 | 0 | 0 | 24
39049.4007 | 0 | 0 | 24
39049.4012 | 0 | 0 | 24
39049.4017 | 0 | 0 | 24
39049.4022 | 0 | 0 | 24
39049.4027 | 0 | 0 | 24
39049.4031 | 0 | 0 | 24
39049.4036 | 0 | 0 | 24
39049.4041 | 0 | 0 | 24
39049.4046 | 0 | 0 | 24
39049.4051 | 0 | 0 | 24
39049.4056 | 0 | 0 | 24
39049.4061 | 0 | 0 | 24
39049.4066 | 0 | 0 | 24
39049.407 | 0 | 0 | 24
39049.4075 | 1 | 0 | 24
39049.408 | 0 | 0 | 24
39049.4085 | 0 | 0 | 24
39049.409 | 1 | 0 | 24
39049.4095 | 0 | 0 | 24
39049.41 | 0 | 0 | 24
39049.4104 | 1 | 0 | 24
39049.4109 | 0 | 0 | 24
39049.4114 | 1 | 0 | 24
39049.4119 | 0 | 0 | 24
39049.4124 | 0 | 0 | 24
39049.4129 | 0 | 0 | 24
39049.4134 | 0 | 0 | 24
39049.4138 | 0 | 0 | 24
39049.4143 | 1 | 0 | 24
39049.4148 | 0 | 0 | 24
39049.4153 | 0 | 0 | 24
39049.4158 | 0 | 0 | 24
39049.4163 | 0 | 0 | 24
39049.4168 | 0 | 0 | 24
39049.4172 | 0 | 0 | 24
39049.4177 | 0 | 0 | 24
39049.4182 | 0 | 0 | 24
39049.4187 | 1 | 0 | 24
39049.4192 | 0 | 0 | 24
39049.4197 | 0 | 0 | 24
39049.4202 | 0 | 0 | 24
39049.4206 | 0 | 0 | 24
39049.4211 | 0 | 0 | 24
39049.4216 | 0 | 0 | 24
24
39049.3847 | 0 | 0 | 25
39049.3852 | 0 | 0 | 25
39049.3857 | 0 | 0 | 25
39049.3861 | 0 | 0 | 25
39049.3866 | 0 | 0 | 25
39049.3871 | 0 | 0 | 25
39049.3876 | 0 | 0 | 25
39049.3881 | 0 | 0 | 25
39049.3886 | 0 | 0 | 25
39049.3891 | 0 | 0 | 25
39049.3895 | 0 | 0 | 25
39049.39 | 0 | 0 | 25
39049.3905 | 0 | 0 | 25
39049.391 | 0 | 0 | 25
39049.3915 | 0 | 0 | 25
39049.392 | 0 | 0 | 25
39049.3925 | 0 | 0 | 25
39049.393 | 0 | 0 | 25
39049.3934 | 0 | 0 | 25
39049.3939 | 0 | 0 | 25
39049.3944 | 0 | 0 | 25
39049.3949 | 0 | 0 | 25
39049.3954 | 0 | 0 | 25
39049.3959 | 0 | 0 | 25
39049.3964 | 0 | 0 | 25
39049.3968 | 0 | 0 | 25
39049.3973 | 0 | 0 | 25
39049.3978 | 0 | 0 | 25
39049.3983 | 0 | 0 | 25
39049.3988 | 0 | 0 | 25
39049.3993 | 0 | 0 | 25
39049.3998 | 0 | 0 | 25
39049.4002 | 0 | 0 | 25
39049.4007 | 0 | 0 | 25
39049.4012 | 0 | 0 | 25
39049.4017 | 0 | 0 | 25
39049.4022 | 0 | 0 | 25
39049.4027 | 0 | 0 | 25
39049.4032 | 0 | 0 | 25
39049.4036 | 0 | 0 | 25
39049.4041 | 0 | 0 | 25
39049.4046 | 0 | 0 | 25
39049.4051 | 0 | 0 | 25
39049.4056 | 0 | 0 | 25
39049.4061 | 0 | 0 | 25
39049.4066 | 0 | 0 | 25
39049.407 | 2339 | 0 | 25
39049.4075 | 1955 | 0 | 25
39049.4085 | 2535 | 0 | 25
39049.409 | 2347 | 0 | 25
39049.4095 | 2439 | 0 | 25
39049.41 | 2377 | 0 | 25
39049.4105 | 2019 | 0 | 25
39049.4109 | 1984 | 0 | 25
39049.4114 | 2500 | 0 | 25
39049.4119 | 2172 | 0 | 25
39049.4124 | 2326 | 0 | 25
39049.4129 | 2008 | 0 | 25
39049.4134 | 1975 | 0 | 25
39049.4139 | 2441 | 0 | 25
39049.4143 | 1937 | 0 | 25
39049.4148 | 1922 | 0 | 25
39049.4153 | 2398 | 0 | 25
39049.4158 | 2000 | 0 | 25
39049.4163 | 2413 | 0 | 25
39049.4168 | 2395 | 0 | 25
39049.4173 | 2000 | 0 | 25
39049.4177 | 2217 | 0 | 25
39049.4182 | 2172 | 0 | 25
39049.4187 | 2147 | 0 | 25
39049.4192 | 2455 | 0 | 25
39049.4197 | 2428 | 0 | 25
39049.4202 | 1942 | 0 | 25
39049.4207 | 1947 | 0 | 25
39049.4211 | 2020 | 0 | 25
39049.4216 | 1938 | 0 | 25
25
39049.3847 | 0 | 0 | 26
39049.3852 | 0 | 0 | 26
39049.3857 | 0 | 0 | 26
39049.3862 | 0 | 0 | 26
39049.3867 | 0 | 0 | 26
39049.3871 | 0 | 0 | 26
39049.3876 | 0 | 0 | 26
39049.3881 | 0 | 0 | 26
39049.3886 | 0 | 0 | 26
39049.3891 | 0 | 0 | 26
39049.3896 | 0 | 0 | 26
39049.3901 | 0 | 0 | 26
39049.3905 | 0 | 0 | 26
39049.391 | 0 | 0 | 26
39049.3915 | 0 | 0 | 26
39049.392 | 0 | 0 | 26
39049.3925 | 0 | 0 | 26
39049.393 | 0 | 0 | 26
39049.3935 | 0 | 0 | 26
39049.3939 | 0 | 0 | 26
39049.3944 | 0 | 0 | 26
39049.3949 | 0 | 0 | 26
39049.3954 | 0 | 0 | 26
39049.3959 | 0 | 0 | 26
39049.3964 | 0 | 0 | 26
39049.3969 | 0 | 0 | 26
39049.3973 | 0 | 0 | 26
39049.3978 | 0 | 0 | 26
39049.3983 | 0 | 0 | 26
39049.3988 | 0 | 0 | 26
39049.3993 | 0 | 0 | 26
39049.3998 | 0 | 0 | 26
39049.4003 | 0 | 0 | 26
39049.4008 | 0 | 0 | 26
39049.4012 | 0 | 0 | 26
39049.4017 | 0 | 0 | 26
39049.4022 | 0 | 0 | 26
39049.4027 | 0 | 0 | 26
39049.4032 | 0 | 0 | 26
39049.4037 | 0 | 0 | 26
39049.4042 | 0 | 0 | 26
39049.4046 | 0 | 0 | 26
39049.4051 | 0 | 0 | 26
39049.4056 | 0 | 0 | 26
39049.4061 | 0 | 0 | 26
39049.4066 | 0 | 0 | 26
39049.4071 | 0 | 0 | 26
39049.4076 | 0 | 0 | 26
39049.408 | 0 | 0 | 26
39049.4085 | 0 | 0 | 26
39049.409 | 0 | 0 | 26
39049.4095 | 0 | 0 | 26
39049.41 | 0 | 0 | 26
39049.4105 | 0 | 0 | 26
39049.4109 | 0 | 0 | 26
39049.4114 | 0 | 0 | 26
39049.4119 | 0 | 0 | 26
39049.4124 | 0 | 0 | 26
39049.4129 | 0 | 0 | 26
39049.4134 | 0 | 0 | 26
39049.4139 | 0 | 0 | 26
39049.4144 | 0 | 0 | 26
39049.4148 | 0 | 0 | 26
39049.4153 | 0 | 0 | 26
39049.4158 | 0 | 0 | 26
39049.4163 | 0 | 0 | 26
39049.4168 | 0 | 0 | 26
39049.4173 | 0 | 0 | 26
39049.4178 | 0 | 0 | 26
39049.4182 | 0 | 0 | 26
39049.4187 | 0 | 0 | 26
39049.4192 | 0 | 0 | 26
39049.4197 | 0 | 0 | 26
39049.4202 | 0 | 0 | 26
39049.4207 | 0 | 0 | 26
39049.4212 | 0 | 0 | 26
39049.4216 | 0 | 0 | 26
26
39049.3847 | 0 | 0 | 27
39049.3852 | 0 | 0 | 27
39049.3857 | 0 | 0 | 27
39049.3862 | 0 | 0 | 27
39049.3867 | 0 | 0 | 27
39049.3872 | 0 | 0 | 27
39049.3876 | 0 | 0 | 27
39049.3881 | 0 | 0 | 27
39049.3886 | 0 | 0 | 27
39049.3891 | 0 | 0 | 27
39049.3896 | 0 | 0 | 27
39049.3901 | 0 | 0 | 27
39049.3906 | 0 | 0 | 27
39049.391 | 0 | 0 | 27
39049.3915 | 0 | 0 | 27
39049.392 | 0 | 0 | 27
39049.3925 | 0 | 0 | 27
39049.393 | 0 | 0 | 27
39049.3935 | 0 | 0 | 27
39049.394 | 0 | 0 | 27
39049.3944 | 0 | 0 | 27
39049.3949 | 0 | 0 | 27
39049.3954 | 0 | 0 | 27
39049.3959 | 0 | 0 | 27
39049.3964 | 0 | 0 | 27
39049.3969 | 0 | 0 | 27
39049.3974 | 0 | 0 | 27
39049.3978 | 0 | 0 | 27
39049.3983 | 0 | 0 | 27
39049.3988 | 0 | 0 | 27
39049.3993 | 0 | 0 | 27
39049.3998 | 0 | 0 | 27
39049.4003 | 0 | 0 | 27
39049.4008 | 0 | 0 | 27
39049.4013 | 0 | 0 | 27
39049.4017 | 0 | 0 | 27
39049.4022 | 0 | 0 | 27
39049.4027 | 0 | 0 | 27
39049.4032 | 0 | 1 | 27
39049.4037 | 0 | 0 | 27
39049.4042 | 0 | 0 | 27
39049.4047 | 0 | 0 | 27
39049.4051 | 0 | 0 | 27
39049.4056 | 0 | 0 | 27
39049.4061 | 0 | 0 | 27
39049.4066 | 0 | 0 | 27
39049.4071 | 2122 | 0 | 27
39049.4076 | 2233 | 0 | 27
39049.4081 | 2144 | 0 | 27
39049.4085 | 2204 | 0 | 27
39049.409 | 2072 | 0 | 27
39049.4095 | 2471 | 0 | 27
39049.41 | 2524 | 0 | 27
39049.4105 | 2020 | 0 | 27
39049.411 | 2244 | 0 | 27
39049.4115 | 1959 | 0 | 27
39049.4119 | 1966 | 0 | 27
39049.4124 | 1966 | 0 | 27
39049.4129 | 2033 | 0 | 27
39049.4134 | 2106 | 0 | 27
39049.4139 | 2224 | 0 | 27
39049.4144 | 2424 | 0 | 27
39049.4149 | 2142 | 0 | 27
39049.4153 | 2034 | 0 | 27
39049.4158 | 2153 | 0 | 27
39049.4163 | 2199 | 0 | 27
39049.4168 | 1901 | 0 | 27
39049.4173 | 2103 | 0 | 27
39049.4178 | 2118 | 0 | 27
39049.4183 | 2329 | 0 | 27
39049.4187 | 2189 | 0 | 27
39049.4192 | 2444 | 0 | 27
39049.4197 | 1997 | 0 | 27
39049.4202 | 2092 | 0 | 27
39049.4207 | 2157 | 0 | 27
39049.4212 | 2361 | 0 | 27
39049.4217 | 2117 | 0 | 27
27
39049.3847 | 0 | 0 | 28
39049.3852 | 0 | 0 | 28
39049.3857 | 0 | 0 | 28
39049.3862 | 0 | 0 | 28
39049.3867 | 0 | 0 | 28
39049.3872 | 0 | 0 | 28
39049.3877 | 0 | 0 | 28
39049.3881 | 0 | 0 | 28
39049.3886 | 0 | 0 | 28
39049.3891 | 0 | 0 | 28
39049.3896 | 0 | 0 | 28
39049.3901 | 0 | 0 | 28
39049.3906 | 0 | 0 | 28
39049.3911 | 0 | 0 | 28
39049.3916 | 0 | 0 | 28
39049.392 | 0 | 0 | 28
39049.3925 | 0 | 0 | 28
39049.393 | 0 | 0 | 28
39049.3935 | 0 | 0 | 28
39049.394 | 0 | 0 | 28
39049.3945 | 0 | 0 | 28
39049.395 | 0 | 0 | 28
39049.3954 | 0 | 0 | 28
39049.3959 | 0 | 0 | 28
39049.3964 | 0 | 0 | 28
39049.3969 | 0 | 0 | 28
39049.3974 | 0 | 0 | 28
39049.3979 | 0 | 0 | 28
39049.3983 | 0 | 0 | 28
39049.3988 | 0 | 0 | 28
39049.3993 | 0 | 0 | 28
39049.3998 | 0 | 0 | 28
39049.4003 | 0 | 0 | 28
39049.4008 | 0 | 0 | 28
39049.4013 | 0 | 0 | 28
39049.4017 | 0 | 0 | 28
39049.4022 | 0 | 0 | 28
39049.4027 | 0 | 0 | 28
39049.4032 | 0 | 0 | 28
39049.4037 | 0 | 0 | 28
39049.4042 | 0 | 0 | 28
39049.4047 | 0 | 0 | 28
39049.4052 | 0 | 0 | 28
39049.4056 | 0 | 0 | 28
39049.4061 | 0 | 0 | 28
39049.4066 | 0 | 0 | 28
39049.4071 | 0 | 0 | 28
39049.4076 | 0 | 0 | 28
39049.4081 | 0 | 0 | 28
39049.4086 | 0 | 0 | 28
39049.409 | 0 | 0 | 28
39049.4095 | 0 | 0 | 28
39049.41 | 0 | 0 | 28
39049.4105 | 1 | 0 | 28
39049.411 | 0 | 0 | 28
39049.4115 | 0 | 0 | 28
39049.412 | 0 | 0 | 28
39049.4124 | 0 | 0 | 28
39049.4129 | 0 | 0 | 28
39049.4134 | 0 | 0 | 28
39049.4139 | 0 | 0 | 28
39049.4144 | 0 | 0 | 28
39049.4149 | 0 | 0 | 28
39049.4154 | 0 | 0 | 28
39049.4158 | 0 | 0 | 28
39049.4163 | 0 | 0 | 28
39049.4168 | 0 | 0 | 28
39049.4173 | 0 | 0 | 28
39049.4178 | 0 | 0 | 28
39049.4183 | 0 | 0 | 28
39049.4188 | 0 | 0 | 28
39049.4192 | 0 | 0 | 28
39049.4197 | 0 | 0 | 28
39049.4202 | 0 | 0 | 28
39049.4207 | 0 | 0 | 28
39049.4212 | 0 | 0 | 28
39049.4217 | 0 | 0 | 28
28
39049.3848 | 0 | 0 | 29
39049.3852 | 0 | 0 | 29
39049.3857 | 0 | 0 | 29
39049.3862 | 0 | 0 | 29
39049.3867 | 0 | 0 | 29
39049.3877 | 0 | 0 | 29
39049.3882 | 0 | 0 | 29
39049.3886 | 0 | 0 | 29
39049.3891 | 0 | 0 | 29
39049.3896 | 0 | 0 | 29
39049.3901 | 0 | 0 | 29
39049.3906 | 0 | 0 | 29
39049.3911 | 0 | 0 | 29
39049.3916 | 0 | 0 | 29
39049.392 | 0 | 0 | 29
39049.3925 | 0 | 0 | 29
39049.393 | 0 | 0 | 29
39049.3935 | 0 | 0 | 29
39049.394 | 0 | 0 | 29
39049.3945 | 0 | 0 | 29
39049.395 | 0 | 0 | 29
39049.3955 | 0 | 0 | 29
39049.3959 | 0 | 0 | 29
39049.3964 | 0 | 0 | 29
39049.3969 | 0 | 0 | 29
39049.3974 | 0 | 0 | 29
39049.3979 | 0 | 0 | 29
39049.3984 | 0 | 0 | 29
39049.3989 | 0 | 0 | 29
39049.3993 | 0 | 0 | 29
39049.3998 | 0 | 0 | 29
39049.4003 | 0 | 0 | 29
39049.4008 | 0 | 0 | 29
39049.4013 | 0 | 0 | 29
39049.4018 | 0 | 0 | 29
39049.4023 | 0 | 0 | 29
39049.4027 | 0 | 0 | 29
39049.4032 | 0 | 0 | 29
39049.4037 | 0 | 0 | 29
39049.4042 | 0 | 0 | 29
39049.4047 | 0 | 0 | 29
39049.4052 | 0 | 0 | 29
39049.4057 | 0 | 0 | 29
39049.4061 | 0 | 0 | 29
39049.4066 | 0 | 0 | 29
39049.4071 | 0 | 0 | 29
39049.4076 | 0 | 0 | 29
39049.4081 | 0 | 0 | 29
39049.4086 | 0 | 0 | 29
39049.4091 | 0 | 0 | 29
39049.4095 | 0 | 0 | 29
39049.41 | 0 | 0 | 29
39049.4105 | 0 | 0 | 29
39049.411 | 0 | 0 | 29
39049.4115 | 0 | 0 | 29
39049.412 | 0 | 0 | 29
39049.4125 | 0 | 0 | 29
39049.413 | 0 | 0 | 29
39049.4134 | 0 | 0 | 29
39049.4139 | 0 | 0 | 29
39049.4144 | 0 | 0 | 29
39049.4149 | 0 | 0 | 29
39049.4154 | 0 | 0 | 29
39049.4159 | 0 | 0 | 29
39049.4164 | 0 | 0 | 29
39049.4168 | 0 | 0 | 29
39049.4173 | 0 | 0 | 29
39049.4178 | 0 | 0 | 29
39049.4183 | 0 | 0 | 29
39049.4188 | 0 | 0 | 29
39049.4193 | 0 | 0 | 29
39049.4198 | 0 | 0 | 29
39049.4202 | 0 | 0 | 29
39049.4207 | 0 | 0 | 29
39049.4212 | 0 | 0 | 29
39049.4217 | 0 | 0 | 29
29
39049.3848 | 0 | 0 | 30
39049.3853 | 0 | 0 | 30
39049.3857 | 0 | 0 | 30
39049.3862 | 0 | 0 | 30
39049.3867 | 0 | 0 | 30
39049.3872 | 0 | 0 | 30
39049.3877 | 0 | 0 | 30
39049.3882 | 0 | 0 | 30
39049.3887 | 0 | 0 | 30
39049.3891 | 0 | 0 | 30
39049.3896 | 0 | 0 | 30
39049.3901 | 0 | 0 | 30
39049.3906 | 0 | 0 | 30
39049.3911 | 0 | 0 | 30
39049.3916 | 0 | 0 | 30
39049.3921 | 0 | 0 | 30
39049.3925 | 0 | 0 | 30
39049.393 | 0 | 0 | 30
39049.3935 | 0 | 0 | 30
39049.394 | 0 | 0 | 30
39049.3945 | 0 | 0 | 30
39049.395 | 0 | 0 | 30
39049.3955 | 0 | 0 | 30
39049.3959 | 0 | 0 | 30
39049.3964 | 0 | 0 | 30
39049.3969 | 0 | 0 | 30
39049.3974 | 0 | 0 | 30
39049.3979 | 0 | 0 | 30
39049.3984 | 0 | 0 | 30
39049.3989 | 0 | 0 | 30
39049.3994 | 0 | 0 | 30
39049.3998 | 0 | 0 | 30
39049.4003 | 0 | 0 | 30
39049.4008 | 0 | 0 | 30
39049.4013 | 0 | 0 | 30
39049.4018 | 0 | 0 | 30
39049.4023 | 0 | 0 | 30
39049.4028 | 0 | 0 | 30
39049.4032 | 0 | 0 | 30
39049.4037 | 0 | 0 | 30
39049.4042 | 0 | 0 | 30
39049.4047 | 0 | 0 | 30
39049.4052 | 0 | 0 | 30
39049.4057 | 0 | 0 | 30
39049.4062 | 0 | 0 | 30
39049.4066 | 0 | 0 | 30
39049.4071 | 0 | 0 | 30
39049.4076 | 0 | 0 | 30
39049.4081 | 1 | 0 | 30
39049.4086 | 0 | 0 | 30
39049.4091 | 0 | 1 | 30
39049.4096 | 0 | 0 | 30
39049.41 | 0 | 0 | 30
39049.4105 | 0 | 0 | 30
39049.411 | 0 | 0 | 30
39049.4115 | 0 | 0 | 30
39049.412 | 0 | 0 | 30
39049.4125 | 0 | 0 | 30
39049.413 | 0 | 0 | 30
39049.4134 | 0 | 0 | 30
39049.4139 | 0 | 0 | 30
39049.4144 | 0 | 0 | 30
39049.4149 | 0 | 0 | 30
39049.4154 | 0 | 0 | 30
39049.4159 | 0 | 0 | 30
39049.4164 | 0 | 0 | 30
39049.4169 | 0 | 0 | 30
39049.4173 | 0 | 0 | 30
39049.4178 | 0 | 0 | 30
39049.4183 | 0 | 0 | 30
39049.4188 | 0 | 0 | 30
39049.4193 | 0 | 0 | 30
39049.4198 | 0 | 0 | 30
39049.4203 | 0 | 0 | 30
39049.4207 | 0 | 0 | 30
39049.4212 | 0 | 0 | 30
39049.4217 | 0 | 0 | 30
30

## Temperatures
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY G
0 | -236 | 12.8 | 12.6 | 11.9 | 12.6 | 9.5
1 | -235 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
2 | -234 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
3 | -233 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
4 | -232 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
5 | -231 | 12.8 | 12.6 | 11.9 | 12.6 | 9.5
6 | -230 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
7 | -229 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
8 | -228 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
9 | -227 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
10 | -226 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
11 | -225 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
12 | -224 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
13 | -223 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
14 | -222 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
15 | -221 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
16 | -220 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
17 | -219 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
18 | -218 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
19 | -217 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
20 | -216 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
21 | -215 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
22 | -214 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
23 | -213 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
24 | -212 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
25 | -211 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
26 | -210 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
27 | -209 | 12.7 | 12.6 | 12 | 12.5 | 9.5
28 | -208 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
29 | -207 | 12.7 | 12.6 | 12 | 12.6 | 9.5
30 | -206 | 12.7 | 12.6 | 12 | 12.6 | 9.5
31 | -205 | 12.7 | 12.6 | 12 | 12.6 | 9.5
32 | -204 | 12.7 | 12.6 | 12 | 12.5 | 9.5
33 | -203 | 12.7 | 12.6 | 12 | 12.6 | 9.5
34 | -202 | 12.7 | 12.6 | 12 | 12.6 | 9.5
35 | -201 | 12.7 | 12.6 | 12 | 12.5 | 9.5
36 | -200 | 12.7 | 12.6 | 12 | 12.5 | 9.5
37 | -199 | 12.7 | 12.6 | 12 | 12.5 | 9.5
38 | -198 | 12.7 | 12.6 | 12 | 12.6 | 9.5
39 | -197 | 12.7 | 12.6 | 12 | 12.5 | 9.5
40 | -196 | 12.7 | 12.6 | 12 | 12.6 | 9.5
41 | -195 | 12.7 | 12.6 | 12 | 12.5 | 9.5
42 | -194 | 12.7 | 12.6 | 12 | 12.5 | 9.5
43 | -193 | 12.7 | 12.6 | 12 | 12.5 | 9.5
44 | -192 | 12.7 | 12.6 | 12 | 12.5 | 9.5
45 | -191 | 12.7 | 12.6 | 12 | 12.6 | 9.5
46 | -190 | 12.7 | 12.6 | 12 | 12.6 | 9.5
47 | -189 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
48 | -188 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
49 | -187 | 12.8 | 12.6 | 11.9 | 12.5 | 9.5
50 | -186 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
51 | -185 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
52 | -184 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
53 | -183 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
54 | -182 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
55 | -181 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
56 | -180 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
57 | -179 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
58 | -178 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
59 | -177 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
60 | -176 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
61 | -175 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
62 | -174 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
63 | -173 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
64 | -172 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
65 | -171 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
66 | -170 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
67 | -169 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
68 | -168 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
69 | -167 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
70 | -166 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
71 | -165 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
72 | -164 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
73 | -163 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
74 | -162 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
75 | -161 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
76 | -160 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
77 | -159 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
78 | -158 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
79 | -157 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
80 | -156 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
81 | -155 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
82 | -154 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
83 | -153 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
84 | -152 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
85 | -151 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
86 | -150 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
87 | -149 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
88 | -148 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
89 | -147 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
90 | -146 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
91 | -145 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
92 | -144 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
93 | -143 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
94 | -142 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
95 | -141 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
96 | -140 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
97 | -139 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
98 | -138 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
99 | -137 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
100 | -136 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
101 | -135 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
102 | -134 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
103 | -133 | 12.7 | 12.6 | 12 | 12.5 | 9.5
104 | -132 | 12.7 | 12.6 | 12 | 12.6 | 9.5
105 | -131 | 12.7 | 12.6 | 12 | 12.5 | 9.5
106 | -130 | 12.7 | 12.6 | 12 | 12.5 | 9.5
107 | -129 | 12.7 | 12.6 | 12 | 12.5 | 9.5
108 | -128 | 12.7 | 12.6 | 12 | 12.5 | 9.5
109 | -127 | 12.7 | 12.6 | 12 | 12.5 | 9.5
110 | -126 | 12.7 | 12.6 | 12 | 12.6 | 9.5
111 | -125 | 12.7 | 12.6 | 12 | 12.6 | 9.5
112 | -124 | 12.7 | 12.6 | 12 | 12.5 | 9.5
113 | -123 | 12.7 | 12.6 | 12 | 12.5 | 9.5
114 | -122 | 12.7 | 12.6 | 12 | 12.5 | 9.5
115 | -121 | 12.7 | 12.6 | 12 | 12.5 | 9.5
116 | -120 | 12.7 | 12.6 | 12 | 12.6 | 9.5
117 | -119 | 12.7 | 12.6 | 12 | 12.5 | 9.5
118 | -118 | 12.7 | 12.6 | 12 | 12.5 | 9.5
119 | -117 | 12.7 | 12.6 | 12 | 12.5 | 9.5
120 | -116 | 12.7 | 12.6 | 12 | 12.6 | 9.5
121 | -115 | 12.7 | 12.6 | 12 | 12.5 | 9.5
122 | -114 | 12.7 | 12.6 | 12 | 12.5 | 9.5
123 | -113 | 12.7 | 12.6 | 12 | 12.5 | 9.5
124 | -112 | 12.7 | 12.6 | 12 | 12.6 | 9.5
125 | -111 | 12.7 | 12.6 | 12 | 12.6 | 9.5
126 | -110 | 12.7 | 12.6 | 12 | 12.6 | 9.5
127 | -109 | 12.7 | 12.6 | 12 | 12.6 | 9.5
128 | -108 | 12.7 | 12.6 | 12 | 12.6 | 9.5
129 | -107 | 12.7 | 12.6 | 12 | 12.5 | 9.5
130 | -106 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
131 | -105 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
132 | -104 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
133 | -103 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
134 | -102 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
135 | -101 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
136 | -100 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
137 | -99 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
138 | -98 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
139 | -97 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
140 | -96 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
141 | -95 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
142 | -94 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
143 | -93 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
144 | -92 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
145 | -91 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
146 | -90 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
147 | -89 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
148 | -88 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
149 | -87 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
150 | -86 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
151 | -85 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
152 | -84 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
153 | -83 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
154 | -82 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
155 | -81 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
156 | -80 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
157 | -79 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
158 | -78 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
159 | -77 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
160 | -76 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
161 | -75 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
162 | -74 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
163 | -73 | 12.7 | 12.6 | 11.9 | 12.6 | 9.5
164 | -72 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
165 | -71 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
166 | -70 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
167 | -69 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
168 | -68 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
169 | -67 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
170 | -66 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
171 | -65 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
172 | -64 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
173 | -63 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
174 | -62 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
175 | -61 | 12.7 | 12.6 | 11.8 | 12.6 | 9.5
176 | -60 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
177 | -59 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
178 | -58 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
179 | -57 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
180 | -56 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
181 | -55 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
182 | -54 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
183 | -53 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
184 | -52 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
185 | -51 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
186 | -50 | 12.7 | 12.6 | 11.9 | 12.5 | 9.5
187 | -49 | 12.7 | 12.6 | 12 | 12.5 | 9.5
188 | -48 | 12.7 | 12.6 | 12 | 12.5 | 9.5
189 | -47 | 12.7 | 12.6 | 12 | 12.5 | 9.5
190 | -46 | 12.7 | 12.6 | 12 | 12.5 | 9.5
191 | -45 | 12.7 | 12.6 | 12 | 12.5 | 9.5
192 | -44 | 12.7 | 12.6 | 12 | 12.5 | 9.5
193 | -43 | 12.7 | 12.6 | 12 | 12.6 | 9.5
194 | -42 | 12.7 | 12.6 | 12 | 12.5 | 9.5
195 | -41 | 12.7 | 12.6 | 12 | 12.5 | 9.5
196 | -40 | 12.7 | 12.6 | 12 | 12.5 | 9.5
197 | -39 | 12.7 | 12.6 | 12 | 12.5 | 9.5
198 | -38 | 12.7 | 12.6 | 12 | 12.5 | 9.5
199 | -37 | 12.7 | 12.6 | 12 | 12.5 | 9.5
200 | -36 | 12.7 | 12.6 | 12 | 12.5 | 9.5
201 | -35 | 12.7 | 12.6 | 12 | 12.5 | 9.5
202 | -34 | 12.7 | 12.6 | 12 | 12.5 | 9.5
203 | -33 | 12.7 | 12.6 | 12 | 12.5 | 9.5
204 | -32 | 12.7 | 12.6 | 12 | 12.6 | 9.5
205 | -31 | 12.7 | 12.6 | 12 | 12.5 | 9.5
206 | -30 | 12.7 | 12.6 | 12 | 12.5 | 9.5
207 | -29 | 12.7 | 12.6 | 12 | 12.5 | 9.5
208 | -28 | 12.7 | 12.6 | 12 | 12.5 | 9.5
209 | -27 | 12.7 | 12.6 | 12 | 12.5 | 9.5
210 | -26 | 12.7 | 12.6 | 12 | 12.5 | 9.5
211 | -25 | 12.7 | 12.6 | 12 | 12.5 | 9.5
212 | -24 | 12.7 | 12.6 | 12 | 12.5 | 9.5
213 | -23 | 12.7 | 12.6 | 12 | 12.5 | 9.5
214 | -22 | 12.7 | 12.6 | 12 | 12.5 | 9.5
215 | -21 | 12.7 | 12.6 | 12 | 12.5 | 9.5
216 | -20 | 12.7 | 12.6 | 12 | 12.5 | 9.5
217 | -19 | 12.7 | 12.6 | 12 | 12.5 | 9.5
218 | -18 | 12.7 | 12.6 | 12 | 12.6 | 9.5
219 | -17 | 12.7 | 12.6 | 12 | 12.5 | 9.5
220 | -16 | 12.7 | 12.6 | 12 | 12.5 | 9.5
221 | -15 | 12.7 | 12.6 | 12 | 12.5 | 9.5
222 | -14 | 12.7 | 12.6 | 12 | 12.5 | 9.5
223 | -13 | 12.7 | 12.6 | 12 | 12.5 | 9.5
224 | -12 | 12.7 | 12.6 | 12 | 12.5 | 9.5
225 | -11 | 12.7 | 12.6 | 12 | 12.5 | 9.5
226 | -10 | 12.7 | 12.6 | 12 | 12.5 | 9.5
227 | -9 | 12.7 | 12.6 | 12 | 12.5 | 9.5
228 | -8 | 12.7 | 12.6 | 12 | 12.5 | 9.5
229 | -7 | 12.7 | 12.6 | 12 | 12.5 | 9.5
230 | -6 | 12.7 | 12.6 | 12 | 12.5 | 9.5
231 | -5 | 12.7 | 12.6 | 12 | 12.5 | 9.5
232 | -4 | 12.7 | 12.6 | 12 | 12.5 | 9.5
233 | -3 | 12.7 | 12.6 | 12 | 12.5 | 9.5
234 | -2 | 12.7 | 12.6 | 12 | 12.5 | 9.5
235 | -1 | 12.7 | 12.6 | 12 | 12.5 | 9.5
236 | 0 | 12.7 | 12.6 | 12 | 12.5 | 9.5
237 | 1 | 12.7 | 12.6 | 12 | 12.5 | 9.5
238 | 2 | 12.7 | 12.6 | 12 | 12.5 | 9.5
239 | 3 | 12.7 | 12.6 | 12 | 12.5 | 9.5
240 | 4 | 12.7 | 12.6 | 12 | 12.5 | 9.5
241 | 5 | 12.7 | 12.6 | 12 | 12.5 | 9.5
242 | 6 | 12.7 | 12.6 | 12 | 12.5 | 9.5
243 | 7 | 12.7 | 12.6 | 12 | 12.5 | 9.5
244 | 8 | 12.7 | 12.6 | 12 | 12.5 | 9.5
245 | 9 | 12.7 | 12.6 | 12 | 12.5 | 9.5
246 | 10 | 12.7 | 12.6 | 12 | 12.5 | 9.6
247 | 11 | 12.8 | 12.6 | 12.1 | 12.5 | 9.6
248 | 12 | 12.8 | 12.6 | 12.2 | 12.5 | 9.7
249 | 13 | 12.8 | 12.7 | 12.3 | 12.6 | 9.8
250 | 14 | 12.8 | 12.8 | 12.4 | 12.6 | 9.8
251 | 15 | 12.8 | 13 | 12.5 | 12.6 | 9.9
252 | 16 | 12.9 | 13.1 | 12.7 | 12.6 | 10
253 | 17 | 12.9 | 13.5 | 12.9 | 12.6 | 10.1
254 | 18 | 13 | 14.1 | 13.3 | 12.7 | 10.3
255 | 19 | 13.1 | 14.8 | 13.9 | 12.7 | 10.4
256 | 20 | 13.1 | 15.8 | 14.5 | 12.7 | 10.5
257 | 21 | 13.2 | 16.8 | 15.4 | 12.8 | 10.6
258 | 22 | 13.3 | 17.8 | 16.5 | 12.8 | 10.7
259 | 23 | 13.4 | 19.1 | 17.4 | 12.9 | 10.9
260 | 24 | 13.5 | 20.5 | 18.4 | 12.9 | 11
261 | 25 | 13.5 | 21.8 | 19.6 | 13 | 11.2
262 | 26 | 13.6 | 23.3 | 20.4 | 13 | 11.5
263 | 27 | 13.7 | 25.2 | 21.6 | 13.1 | 11.7
264 | 28 | 13.8 | 26.6 | 22.8 | 13.2 | 11.9
265 | 29 | 13.9 | 28.1 | 24 | 13.3 | 12
266 | 30 | 14 | 29.6 | 25.5 | 13.4 | 12.2
267 | 31 | 14.1 | 31.4 | 26.8 | 13.4 | 12.3
268 | 32 | 14.1 | 33.6 | 28.1 | 13.6 | 12.5
269 | 33 | 14.2 | 35.5 | 29.4 | 13.7 | 12.8
270 | 34 | 14.3 | 36.8 | 30.6 | 13.7 | 13.1
271 | 35 | 14.4 | 38.2 | 32 | 13.8 | 13.3
272 | 36 | 14.4 | 39.5 | 33.8 | 13.8 | 13.6
273 | 37 | 14.5 | 41 | 35.1 | 14 | 13.8
274 | 38 | 14.6 | 42.8 | 36.3 | 14.1 | 14
275 | 39 | 14.7 | 44.3 | 37.8 | 14.2 | 14.2
276 | 40 | 14.8 | 46 | 39 | 14.3 | 14.4
277 | 41 | 14.8 | 47.6 | 40.3 | 14.5 | 14.5
278 | 42 | 14.9 | 49.4 | 41.7 | 14.6 | 14.8
279 | 43 | 15 | 50.6 | 43.7 | 14.6 | 15.1
280 | 44 | 15.1 | 52 | 45 | 14.7 | 15.2
281 | 45 | 15.2 | 53.6 | 46.8 | 14.8 | 15.4
282 | 46 | 15.3 | 55.1 | 48.6 | 14.9 | 15.7
283 | 47 | 15.3 | 56.5 | 50.2 | 15 | 16
284 | 48 | 15.4 | 57.7 | 51.9 | 15.1 | 16.2
285 | 49 | 15.5 | 58.9 | 53.4 | 15.2 | 16.5
286 | 50 | 15.6 | 60.4 | 54.6 | 15.5 | 16.7
287 | 51 | 15.7 | 62 | 56.1 | 15.6 | 17
288 | 52 | 15.8 | 63.6 | 57 | 15.7 | 17.4
289 | 53 | 15.9 | 65.2 | 58.2 | 15.6 | 17.8
290 | 54 | 15.9 | 66.2 | 59.4 | 15.7 | 18
291 | 55 | 16 | 67.1 | 60.3 | 15.8 | 18.2
292 | 56 | 16.1 | 68.3 | 61.4 | 15.8 | 18.4
293 | 57 | 16.1 | 69.6 | 62.4 | 15.8 | 18.7
294 | 58 | 16.2 | 71 | 63.7 | 15.9 | 19
295 | 59 | 16.3 | 72.4 | 64.8 | 16 | 19.2
296 | 60 | 16.3 | 73.6 | 65.7 | 16.1 | 19.5
297 | 61 | 16.4 | 74.9 | 66.6 | 16.2 | 19.8
298 | 62 | 16.5 | 76 | 67.8 | 16.2 | 20.2
299 | 63 | 16.6 | 76.9 | 69.6 | 16.4 | 20.4
300 | 64 | 16.6 | 78.1 | 70.8 | 16.5 | 20.7
301 | 65 | 16.7 | 79 | 71.5 | 16.7 | 21
302 | 66 | 16.8 | 80.3 | 72.5 | 16.7 | 21.2
303 | 67 | 16.8 | 81 | 73.4 | 16.8 | 21.4
304 | 68 | 16.9 | 81.9 | 74.3 | 16.9 | 21.7
305 | 69 | 17 | 82.6 | 75.3 | 17 | 22
306 | 70 | 17.1 | 83.8 | 75.9 | 17.1 | 22.4
307 | 71 | 17.1 | 85 | 76.4 | 17.1 | 22.4
308 | 72 | 17.2 | 86.1 | 77 | 17.2 | 22.6
309 | 73 | 17.3 | 86.9 | 77.4 | 17.2 | 23
310 | 74 | 17.4 | 87.5 | 78.1 | 17.4 | 23.4
311 | 75 | 17.5 | 88.4 | 78.7 | 17.5 | 23.7
312 | 76 | 17.5 | 89.4 | 79.5 | 17.6 | 23.9
313 | 77 | 17.6 | 90.2 | 80.8 | 17.7 | 24.2
314 | 78 | 17.7 | 91.2 | 81.5 | 17.8 | 24.5
315 | 79 | 17.8 | 91.9 | 82.3 | 17.9 | 24.7
316 | 80 | 17.8 | 92.4 | 83.3 | 18 | 25
317 | 81 | 17.9 | 93.2 | 83.8 | 18.3 | 25.3
318 | 82 | 18 | 94 | 84.2 | 18.5 | 25.5
319 | 83 | 18.1 | 95.9 | 84.6 | 18.6 | 25.7
320 | 84 | 18.2 | 96.4 | 85.5 | 18.7 | 26
321 | 85 | 18.2 | 97 | 86.7 | 18.8 | 26.3
322 | 86 | 18.3 | 97.6 | 87.2 | 19 | 26.6
323 | 87 | 18.4 | 98.1 | 87.4 | 19 | 26.9
324 | 88 | 18.4 | 98.6 | 87.9 | 19.1 | 27.1
325 | 89 | 18.5 | 98.7 | 88.5 | 19.1 | 27.5
326 | 90 | 18.6 | 99 | 89.1 | 19.1 | 27.7
327 | 91 | 18.7 | 99.5 | 90.1 | 19.2 | 28
328 | 92 | 18.7 | 100 | 90.6 | 19.4 | 28.1
329 | 93 | 18.8 | 100.5 | 91 | 19.5 | 28.4
330 | 94 | 18.9 | 101.2 | 91.1 | 19.5 | 28.8
331 | 95 | 19 | 101.8 | 91.8 | 19.6 | 29.1
332 | 96 | 19.1 | 102.2 | 92.4 | 19.8 | 29.3
333 | 97 | 19.2 | 102.7 | 92.8 | 19.9 | 29.5
334 | 98 | 19.3 | 103.2 | 93.5 | 20 | 29.8
335 | 99 | 19.3 | 103.5 | 94 | 20.1 | 30
336 | 100 | 19.4 | 104.1 | 95 | 20.1 | 30.2
337 | 101 | 19.5 | 104.6 | 95.6 | 20.2 | 30.5
338 | 102 | 19.6 | 105.1 | 96 | 20.5 | 30.8
339 | 103 | 19.7 | 105.6 | 96.2 | 20.6 | 31.1
340 | 104 | 19.7 | 106 | 96.4 | 20.8 | 31.4
341 | 105 | 19.8 | 106.2 | 96.7 | 20.9 | 31.7
342 | 106 | 19.9 | 106.6 | 96.8 | 20.9 | 32
343 | 107 | 19.9 | 107.1 | 97 | 20.9 | 32.2
344 | 108 | 20 | 107.4 | 97.2 | 20.9 | 32.5
345 | 109 | 20.1 | 107.9 | 97.6 | 21.1 | 32.8
346 | 110 | 20.1 | 108.2 | 98 | 21.1 | 33.2
347 | 111 | 20.2 | 108.7 | 98 | 21.2 | 33.5
348 | 112 | 20.3 | 109.1 | 98.8 | 21.3 | 33.6
349 | 113 | 20.3 | 109.5 | 99.4 | 21.4 | 33.8
350 | 114 | 20.4 | 109.7 | 100.1 | 21.6 | 34
351 | 115 | 20.5 | 109.8 | 100.8 | 21.6 | 34.2
352 | 116 | 20.6 | 110.2 | 101 | 21.8 | 34.4
353 | 117 | 20.6 | 110.7 | 101.1 | 21.9 | 34.4
354 | 118 | 20.7 | 111.1 | 101.2 | 21.9 | 34.6
355 | 119 | 20.8 | 111.5 | 101.4 | 21.9 | 34.9
356 | 120 | 20.9 | 111.7 | 101.7 | 22 | 35
357 | 121 | 20.9 | 111.8 | 102.3 | 22.2 | 35.2
358 | 122 | 21 | 112.3 | 102.6 | 22.3 | 35.5
359 | 123 | 21.1 | 112.9 | 102.7 | 22.4 | 35.8
360 | 124 | 21.1 | 113.2 | 102.7 | 22.4 | 35.8
361 | 125 | 21.2 | 113.5 | 102.8 | 22.6 | 35.9
362 | 126 | 21.3 | 113.7 | 102.8 | 22.8 | 36.1
363 | 127 | 21.3 | 113.8 | 103.2 | 22.9 | 36.5
364 | 128 | 21.4 | 114 | 103.2 | 23.1 | 36.7
365 | 129 | 21.4 | 114.2 | 103.2 | 23.2 | 36.9
366 | 130 | 21.5 | 114.5 | 103.6 | 23.2 | 37
367 | 131 | 21.6 | 114.4 | 104.1 | 23.3 | 37.1
368 | 132 | 21.6 | 114.5 | 104.3 | 23.3 | 37.3
369 | 133 | 21.7 | 114.8 | 104.7 | 23.4 | 37.6
370 | 134 | 21.8 | 115 | 105 | 23.4 | 37.8
371 | 135 | 21.8 | 115.3 | 105.2 | 23.5 | 38
372 | 136 | 21.9 | 115.5 | 105.4 | 23.6 | 38.2
373 | 137 | 22 | 115.6 | 105.5 | 23.6 | 38.4
374 | 138 | 22 | 115.5 | 106.1 | 23.6 | 38.6
375 | 139 | 22.1 | 115.4 | 106.9 | 23.8 | 38.8
376 | 140 | 22.2 | 115.6 | 107 | 23.9 | 39
377 | 141 | 22.3 | 115.6 | 106.7 | 24.1 | 39.3
378 | 142 | 22.3 | 115.8 | 106.6 | 24.2 | 39.4
379 | 143 | 22.4 | 116.1 | 107.3 | 24.2 | 39.6
380 | 144 | 22.5 | 116.4 | 107.4 | 24.3 | 39.7
381 | 145 | 22.6 | 116.8 | 107.6 | 24.4 | 39.9
382 | 146 | 22.7 | 117.2 | 108.2 | 24.5 | 40.1
383 | 147 | 22.7 | 117.9 | 108.9 | 24.6 | 40.3
384 | 148 | 22.8 | 118.3 | 109.3 | 24.8 | 40.5
385 | 149 | 22.9 | 118.7 | 109.4 | 24.9 | 40.7
386 | 150 | 23 | 119.2 | 109.9 | 25 | 41
387 | 151 | 23.1 | 119.2 | 110.1 | 25.2 | 41.3
388 | 152 | 23.2 | 119.4 | 110.1 | 25.3 | 41.4
389 | 153 | 23.2 | 119.5 | 110.2 | 25.3 | 41.5
390 | 154 | 23.3 | 119.4 | 110.8 | 25.4 | 41.8
391 | 155 | 23.4 | 119.5 | 111.2 | 25.6 | 42
392 | 156 | 23.5 | 119.4 | 111.5 | 25.6 | 42.2
393 | 157 | 23.6 | 119.3 | 111.9 | 25.8 | 42.4
394 | 158 | 23.6 | 119.6 | 111.9 | 25.9 | 42.6
395 | 159 | 23.7 | 120.6 | 111.9 | 25.9 | 42.7
396 | 160 | 23.8 | 120.9 | 111.8 | 26 | 42.8
397 | 161 | 23.9 | 120.9 | 111.7 | 26.1 | 43
398 | 162 | 24 | 121.1 | 111.5 | 26.2 | 43.1
399 | 163 | 24.1 | 121.4 | 111.4 | 26.4 | 43.4
400 | 164 | 24.1 | 121.4 | 112 | 26.5 | 43.6
401 | 165 | 24.2 | 121.3 | 112.3 | 26.6 | 43.8
402 | 166 | 24.3 | 121.4 | 112.1 | 26.6 | 44
403 | 167 | 24.4 | 121.5 | 112.5 | 26.7 | 44.1
404 | 168 | 24.5 | 121.5 | 113.1 | 26.7 | 44.3
405 | 169 | 24.6 | 121.4 | 113.5 | 26.8 | 44.4
406 | 170 | 24.6 | 121.5 | 113.3 | 26.8 | 44.5
407 | 171 | 24.7 | 121.6 | 113.2 | 26.8 | 44.7
408 | 172 | 24.8 | 121.7 | 113.3 | 27 | 44.8
409 | 173 | 24.9 | 121.8 | 113.3 | 27 | 45
410 | 174 | 25 | 121.9 | 113.6 | 27.1 | 45.1
411 | 175 | 25 | 121.9 | 113.9 | 27.2 | 45.2
412 | 176 | 25.1 | 121.9 | 114.4 | 27.2 | 45.3
413 | 177 | 25.2 | 121.9 | 115 | 27.4 | 45.6
414 | 178 | 25.3 | 122 | 115.5 | 27.5 | 45.8
415 | 179 | 25.4 | 122.2 | 115.6 | 27.6 | 45.8
416 | 180 | 25.4 | 122.2 | 115.4 | 27.5 | 45.9
417 | 181 | 25.5 | 122.1 | 115.1 | 27.6 | 46.1
418 | 182 | 25.6 | 122.2 | 114.9 | 27.6 | 46.2
419 | 183 | 25.7 | 122.4 | 115.3 | 27.7 | 46.4
420 | 184 | 25.8 | 122.6 | 115.9 | 27.8 | 46.5
421 | 185 | 25.8 | 122.6 | 116.1 | 27.9 | 46.6
422 | 186 | 25.9 | 122.6 | 115.8 | 28 | 46.7
423 | 187 | 26 | 122.7 | 115.4 | 28 | 46.8
424 | 188 | 26 | 122.9 | 115.1 | 28.1 | 46.9
425 | 189 | 26.1 | 122.8 | 115.1 | 28.2 | 47.1
426 | 190 | 26.2 | 122.9 | 114.9 | 28.3 | 47.2
427 | 191 | 26.2 | 123 | 114.7 | 28.4 | 47.3
428 | 192 | 26.3 | 123.2 | 114.6 | 28.5 | 47.4
429 | 193 | 26.4 | 123.2 | 114.6 | 28.6 | 47.5
430 | 194 | 26.5 | 123.5 | 114.6 | 28.6 | 47.5
431 | 195 | 26.5 | 123.7 | 114.6 | 28.7 | 47.6
432 | 196 | 26.6 | 124 | 115.2 | 28.8 | 47.7
433 | 197 | 26.7 | 124.1 | 115.4 | 28.9 | 47.8
434 | 198 | 26.8 | 124.1 | 115.5 | 29 | 47.9
435 | 199 | 26.9 | 123.9 | 115.6 | 29.1 | 48
436 | 200 | 26.9 | 123.8 | 115.5 | 29.2 | 48
437 | 201 | 27 | 123.8 | 115.4 | 29.2 | 48.2
438 | 202 | 27.1 | 123.7 | 115.3 | 29.3 | 48.2
439 | 203 | 27.2 | 123.7 | 115.1 | 29.3 | 48.4
440 | 204 | 27.2 | 123.7 | 114.8 | 29.5 | 48.5
441 | 205 | 27.3 | 123.6 | 114.9 | 29.7 | 48.6
442 | 206 | 27.4 | 123.7 | 115.2 | 29.7 | 48.7
443 | 207 | 27.5 | 123.8 | 115.3 | 29.8 | 49
444 | 208 | 27.6 | 123.7 | 115.3 | 29.9 | 49.1
445 | 209 | 27.6 | 123.8 | 115.2 | 30 | 49.3
446 | 210 | 27.7 | 123.8 | 115.1 | 30.1 | 49.3
447 | 211 | 27.8 | 123.8 | 115.1 | 30.4 | 49.4
448 | 212 | 27.9 | 123.7 | 115.1 | 30.5 | 49.5
449 | 213 | 28 | 123.7 | 115 | 30.6 | 49.6
450 | 214 | 28 | 123.8 | 114.9 | 30.6 | 49.7
451 | 215 | 28.1 | 123.8 | 115.1 | 30.7 | 49.8
452 | 216 | 28.2 | 123.8 | 115.2 | 30.8 | 50
453 | 217 | 28.3 | 123.9 | 115.1 | 30.9 | 50.1
454 | 218 | 28.4 | 124.6 | 114.9 | 31.1 | 50.2
455 | 219 | 28.5 | 125 | 115.3 | 31.1 | 50.4
456 | 220 | 28.5 | 125.2 | 115.9 | 31.3 | 50.5
457 | 221 | 28.6 | 125.1 | 116.5 | 31.4 | 50.7
458 | 222 | 28.7 | 125.2 | 116.2 | 31.5 | 51
459 | 223 | 28.8 | 125.4 | 116.1 | 31.6 | 51.1
460 | 224 | 28.9 | 125.7 | 116.2 | 31.7 | 51.3
461 | 225 | 29 | 125.7 | 116.7 | 31.8 | 51.4
462 | 226 | 29.1 | 125.7 | 117.2 | 31.9 | 51.6
463 | 227 | 29.1 | 125.7 | 117.2 | 31.9 | 51.7
464 | 228 | 29.2 | 125.8 | 117.2 | 31.9 | 51.9
465 | 229 | 29.3 | 126.1 | 117.3 | 32 | 52
466 | 230 | 29.4 | 126.1 | 117.7 | 32.2 | 52.1
467 | 231 | 29.4 | 126.2 | 117.6 | 32.3 | 52.2
468 | 232 | 29.5 | 126.5 | 117.5 | 32.6 | 52.3
469 | 233 | 29.6 | 126.7 | 117.7 | 32.6 | 52.4
470 | 234 | 29.7 | 126.6 | 118.2 | 32.7 | 52.5
471 | 235 | 29.8 | 126.6 | 118.4 | 32.8 | 52.6
472 | 236 | 29.9 | 126.7 | 118.7 | 32.9 | 52.7
473 | 237 | 30 | 126.7 | 119 | 33 | 52.9
474 | 238 | 30 | 126.7 | 118.9 | 33.1 | 53.1
475 | 239 | 30.1 | 126.8 | 118.7 | 33.2 | 53.2
476 | 240 | 30.2 | 126.8 | 118.9 | 33.3 | 53.4
477 | 241 | 30.3 | 127 | 119.3 | 33.4 | 53.6
478 | 242 | 30.3 | 127.1 | 119.7 | 33.5 | 53.7
479 | 243 | 30.4 | 127.2 | 119.8 | 33.6 | 53.8
480 | 244 | 30.5 | 127.3 | 119.9 | 33.8 | 53.8
481 | 245 | 30.6 | 127.5 | 119.7 | 33.9 | 53.9
482 | 246 | 30.7 | 127.9 | 119.7 | 34.1 | 54
483 | 247 | 30.7 | 128.2 | 119.5 | 34.2 | 54.1
484 | 248 | 30.8 | 128.3 | 119.4 | 34.3 | 54.3
485 | 249 | 30.9 | 128.3 | 119.2 | 34.3 | 54.4
486 | 250 | 31 | 128.3 | 119.1 | 34.3 | 54.5
487 | 251 | 31.1 | 128.4 | 119 | 34.4 | 54.6
488 | 252 | 31.1 | 128.5 | 119 | 34.5 | 54.6
489 | 253 | 31.2 | 128.7 | 119.1 | 34.5 | 54.8
490 | 254 | 31.3 | 129 | 119.5 | 34.7 | 54.8
491 | 255 | 31.4 | 129.2 | 119.8 | 34.8 | 55
492 | 256 | 31.5 | 129.5 | 119.9 | 34.9 | 55.1
493 | 257 | 31.6 | 129.7 | 119.9 | 34.9 | 55.2
494 | 258 | 31.7 | 129.8 | 120.6 | 35 | 55.3
495 | 259 | 31.7 | 129.9 | 121.2 | 35.1 | 55.4
496 | 260 | 31.8 | 129.9 | 121.4 | 35.2 | 55.4
497 | 261 | 31.9 | 130.1 | 121.4 | 35.3 | 55.6
498 | 262 | 32 | 130.3 | 121.4 | 35.4 | 55.8
499 | 263 | 32.1 | 130.5 | 121.8 | 35.6 | 55.9
500 | 264 | 32.1 | 130.6 | 122.2 | 35.7 | 56.1
501 | 265 | 32.2 | 130.9 | 122.1 | 35.8 | 56.3
502 | 266 | 32.3 | 131.2 | 122.3 | 35.9 | 56.4
503 | 267 | 32.4 | 131.6 | 122.9 | 35.9 | 56.5
504 | 268 | 32.5 | 131.7 | 123.1 | 36 | 56.7
505 | 269 | 32.6 | 131.7 | 123.2 | 36.1 | 56.8
506 | 270 | 32.7 | 131.7 | 123 | 36.2 | 56.9
507 | 271 | 32.8 | 131.6 | 122.9 | 36.3 | 57
508 | 272 | 32.9 | 131.8 | 123.3 | 36.4 | 57.1
509 | 273 | 32.9 | 131.9 | 123.5 | 36.5 | 57.1
510 | 274 | 33 | 132.1 | 123.3 | 36.6 | 57.2
511 | 275 | 33.1 | 132.2 | 123.2 | 36.7 | 57.3
512 | 276 | 33.2 | 132 | 123.1 | 36.9 | 57.4
513 | 277 | 33.3 | 132 | 123.3 | 37 | 57.4
514 | 278 | 33.4 | 132.1 | 123.4 | 37 | 57.6
515 | 279 | 33.4 | 132.1 | 123.6 | 37.2 | 57.7
516 | 280 | 33.5 | 132.1 | 123.9 | 37.2 | 57.8
517 | 281 | 33.6 | 132 | 123.9 | 37.3 | 58
518 | 282 | 33.7 | 132 | 123.8 | 37.5 | 58
519 | 283 | 33.7 | 132.1 | 123.8 | 37.7 | 58.1
520 | 284 | 33.8 | 132.4 | 123.8 | 37.8 | 58.2
521 | 285 | 33.9 | 132.5 | 123.8 | 37.9 | 58.4
522 | 286 | 34 | 132.7 | 123.9 | 38 | 58.4
523 | 287 | 34.1 | 132.7 | 124.1 | 38.1 | 58.5
524 | 288 | 34.1 | 132.7 | 124.8 | 38.2 | 58.6
525 | 289 | 34.2 | 132.9 | 124.9 | 38.3 | 58.8
526 | 290 | 34.3 | 133.3 | 125.2 | 38.4 | 58.9
527 | 291 | 34.4 | 133.6 | 125.1 | 38.5 | 59.1
528 | 292 | 34.5 | 133.8 | 124.9 | 38.6 | 59.3
529 | 293 | 34.5 | 133.9 | 124.7 | 38.7 | 59.4
530 | 294 | 34.6 | 133.8 | 124.9 | 38.7 | 59.6
531 | 295 | 34.7 | 134.1 | 125.3 | 38.9 | 59.7
532 | 296 | 34.8 | 134.5 | 125.7 | 38.9 | 59.9
533 | 297 | 34.9 | 134.9 | 126.1 | 39 | 60.1
534 | 298 | 35 | 135.2 | 126.4 | 39.1 | 60.3
535 | 299 | 35 | 135.3 | 126.7 | 39.1 | 60.4
536 | 300 | 35.1 | 135.4 | 126.7 | 39.2 | 60.6
537 | 301 | 35.2 | 135.4 | 126.5 | 39.3 | 60.7
538 | 302 | 35.3 | 135.5 | 126.4 | 39.4 | 60.8
539 | 303 | 35.4 | 135.7 | 126.3 | 39.6 | 60.9
540 | 304 | 35.4 | 136 | 126.3 | 39.7 | 61
541 | 305 | 35.5 | 136 | 126.3 | 39.8 | 61.1
542 | 306 | 35.6 | 136.1 | 126.3 | 39.9 | 61.3
543 | 307 | 35.7 | 136.1 | 126.5 | 39.9 | 61.3
544 | 308 | 35.8 | 136.2 | 126.5 | 40 | 61.4
545 | 309 | 35.9 | 136.3 | 126.6 | 40.2 | 61.5
546 | 310 | 36 | 136.3 | 126.6 | 40.3 | 61.7
547 | 311 | 36.1 | 136.4 | 126.8 | 40.3 | 61.9
548 | 312 | 36.2 | 136.6 | 127.2 | 40.4 | 62.1
549 | 313 | 36.2 | 136.7 | 127.4 | 40.5 | 62.2
550 | 314 | 36.3 | 136.6 | 127.3 | 40.6 | 62.2
551 | 315 | 36.4 | 136.7 | 127.2 | 40.7 | 62.3
552 | 316 | 36.5 | 136.7 | 127.3 | 40.8 | 62.4
553 | 317 | 36.6 | 136.6 | 127.6 | 40.8 | 62.4
554 | 318 | 36.7 | 136.7 | 127.7 | 40.9 | 62.5
555 | 319 | 36.7 | 136.8 | 127.9 | 41 | 62.6
556 | 320 | 36.8 | 136.8 | 128.3 | 41.1 | 62.7
557 | 321 | 36.9 | 136.9 | 128.6 | 41.2 | 62.8
558 | 322 | 37 | 137.1 | 128.4 | 41.3 | 62.9
559 | 323 | 37.1 | 137.3 | 128.4 | 41.5 | 63
560 | 324 | 37.2 | 137.4 | 128.4 | 41.7 | 63.1
561 | 325 | 37.3 | 138 | 128.6 | 41.8 | 63.2
562 | 326 | 37.3 | 138.4 | 128.9 | 41.9 | 63.3
563 | 327 | 37.4 | 138.7 | 129 | 42.1 | 63.5
564 | 328 | 37.5 | 139.1 | 129.3 | 42.2 | 63.7
565 | 329 | 37.6 | 139.7 | 129.9 | 42.4 | 63.8
566 | 330 | 37.7 | 140.2 | 130.8 | 42.6 | 64
567 | 331 | 37.9 | 140.8 | 131.5 | 42.7 | 64.3
568 | 332 | 38 | 141.3 | 131.8 | 42.8 | 64.5
569 | 333 | 38.1 | 141.6 | 132.7 | 42.9 | 64.8
570 | 334 | 38.2 | 142 | 133.2 | 43 | 65
571 | 335 | 38.3 | 142.2 | 133.5 | 43.1 | 65.1
572 | 336 | 38.4 | 142.6 | 133.8 | 43.4 | 65.3
573 | 337 | 38.5 | 143.3 | 134.2 | 43.5 | 65.4
574 | 338 | 38.6 | 143.8 | 134.7 | 43.8 | 65.6
575 | 339 | 38.7 | 144.3 | 135.4 | 43.8 | 65.8
576 | 340 | 38.8 | 144.8 | 135.6 | 44 | 66
577 | 341 | 38.9 | 145.4 | 135.7 | 44.1 | 66.2
578 | 342 | 39 | 146.1 | 136.1 | 44.2 | 66.4
579 | 343 | 39.1 | 146.7 | 137.1 | 44.4 | 66.6
580 | 344 | 39.2 | 147.4 | 137.5 | 44.5 | 66.9
581 | 345 | 39.3 | 148.2 | 137.9 | 44.7 | 67
582 | 346 | 39.4 | 149 | 138.6 | 44.8 | 67.3
583 | 347 | 39.5 | 149.6 | 139.5 | 45 | 67.5
584 | 348 | 39.6 | 150.3 | 140.1 | 45.3 | 67.7
585 | 349 | 39.8 | 152.2 | 141.3 | 45.5 | 68
586 | 350 | 39.9 | 153.2 | 142.4 | 45.8 | 68.3
587 | 351 | 40 | 154.2 | 142.5 | 46 | 68.4
588 | 352 | 40.2 | 155.2 | 142.9 | 46.3 | 68.6
589 | 353 | 40.3 | 156.2 | 143.6 | 46.6 | 68.9
590 | 354 | 40.4 | 156.6 | 144.8 | 46.6 | 69.2
591 | 355 | 40.6 | 156.9 | 146.1 | 46.8 | 69.5
592 | 356 | 40.7 | 157.5 | 147.1 | 46.9 | 69.6
593 | 357 | 40.9 | 158 | 147.4 | 47 | 69.9
594 | 358 | 41 | 158.6 | 147.4 | 47.2 | 70.2
595 | 359 | 41.1 | 159.2 | 147.7 | 47.4 | 70.4
596 | 360 | 41.3 | 160 | 148.2 | 47.5 | 70.7
597 | 361 | 41.4 | 160.3 | 148.8 | 47.6 | 70.9
598 | 362 | 41.5 | 160.7 | 148.7 | 47.7 | 71
599 | 363 | 41.6 | 161 | 148.8 | 47.8 | 71.2
600 | 364 | 41.8 | 161.6 | 149.1 | 47.9 | 71.3
601 | 365 | 41.9 | 162.3 | 149.6 | 47.9 | 71.4
602 | 366 | 42 | 162.8 | 150.6 | 48.1 | 71.6
603 | 367 | 42.1 | 163.3 | 151.6 | 48.2 | 71.9
604 | 368 | 42.2 | 163.8 | 151.7 | 48.3 | 72.2
605 | 369 | 42.3 | 164.2 | 152.4 | 48.4 | 72.3
606 | 370 | 42.4 | 164.7 | 152.8 | 48.5 | 72.6
607 | 371 | 42.5 | 165.4 | 153.2 | 48.6 | 72.7
608 | 372 | 42.6 | 166 | 153.9 | 48.8 | 73.1
609 | 373 | 42.7 | 166.4 | 154.3 | 48.9 | 73.2
610 | 374 | 42.8 | 166.5 | 154.9 | 49 | 73.4
611 | 375 | 43 | 166.9 | 155.5 | 49.2 | 73.6
612 | 376 | 43.1 | 167.3 | 155.9 | 49.3 | 73.8
613 | 377 | 43.2 | 167.5 | 156.5 | 49.3 | 74
614 | 378 | 43.3 | 167.6 | 157.1 | 49.4 | 74.2
615 | 379 | 43.4 | 167.8 | 157.4 | 49.5 | 74.4
616 | 380 | 43.5 | 168.1 | 158.1 | 49.6 | 74.5
617 | 381 | 43.6 | 168.3 | 158.6 | 49.8 | 74.7
618 | 382 | 43.7 | 168.4 | 158.5 | 49.9 | 75
619 | 383 | 43.8 | 168.7 | 158.9 | 50 | 75.2
620 | 384 | 43.9 | 169.1 | 159.6 | 50.2 | 75.4
621 | 385 | 44 | 169.7 | 159.6 | 50.4 | 75.6
622 | 386 | 44.1 | 170.8 | 160.1 | 50.5 | 75.7
623 | 387 | 44.2 | 171.3 | 160.7 | 50.5 | 76
624 | 388 | 44.3 | 171.6 | 161.2 | 50.7 | 76.3
625 | 389 | 44.4 | 172 | 161.9 | 50.8 | 76.5
626 | 390 | 44.5 | 172.2 | 162.5 | 50.9 | 76.7
627 | 391 | 44.7 | 172.8 | 162.4 | 51 | 76.9
628 | 392 | 44.8 | 173.2 | 162.8 | 51.1 | 77.2
629 | 393 | 44.9 | 173.4 | 162.8 | 51.2 | 77.3
630 | 394 | 45 | 173.5 | 163.4 | 51.4 | 77.5
631 | 395 | 45.1 | 173.4 | 163.8 | 51.5 | 77.6
632 | 396 | 45.3 | 173.6 | 163.8 | 51.6 | 77.8
633 | 397 | 45.4 | 173.9 | 163.8 | 51.9 | 77.9
634 | 398 | 45.5 | 174.2 | 163.8 | 52.1 | 78
635 | 399 | 45.6 | 174.2 | 164 | 52.2 | 78.1
636 | 400 | 45.7 | 174.2 | 164.5 | 52.3 | 78.3
637 | 401 | 45.9 | 174.5 | 164.5 | 52.5 | 78.5
638 | 402 | 46 | 174.6 | 164.6 | 52.6 | 78.7
639 | 403 | 46.1 | 174.6 | 164.6 | 52.8 | 78.8
640 | 404 | 46.2 | 174.7 | 164.4 | 53 | 78.9
641 | 405 | 46.3 | 175.2 | 164.4 | 53.2 | 79.1
642 | 406 | 46.4 | 175.2 | 165 | 53.4 | 79.3
643 | 407 | 46.5 | 175.6 | 164.8 | 53.5 | 79.5
644 | 408 | 46.7 | 175.9 | 164.9 | 53.6 | 79.6
645 | 409 | 46.8 | 176.2 | 165.1 | 53.7 | 79.7
646 | 410 | 46.9 | 176.6 | 166 | 53.9 | 79.9
647 | 411 | 47 | 177.1 | 166.9 | 54.1 | 80.1
648 | 412 | 47.1 | 177.4 | 166.8 | 54.2 | 80.5
649 | 413 | 47.3 | 177.6 | 167 | 54.2 | 80.6
650 | 414 | 47.4 | 178.2 | 167 | 54.3 | 80.7
651 | 415 | 47.5 | 178.7 | 167 | 54.6 | 80.9
652 | 416 | 47.6 | 179.2 | 167 | 54.7 | 81.2
653 | 417 | 47.8 | 179.5 | 167.2 | 55 | 81.3
654 | 418 | 47.9 | 179.6 | 168 | 55.2 | 81.7
655 | 419 | 48 | 180.3 | 168.4 | 55.4 | 81.9
656 | 420 | 48.2 | 180.7 | 168.5 | 55.8 | 82.1
657 | 421 | 48.3 | 180.8 | 169.1 | 56 | 82.3
658 | 422 | 48.4 | 181 | 168.9 | 56.2 | 82.6
659 | 423 | 48.6 | 181.4 | 169 | 56.4 | 82.8
660 | 424 | 48.7 | 181.4 | 169.4 | 56.6 | 83.1
661 | 425 | 48.9 | 181.6 | 169.5 | 56.8 | 83.2
662 | 426 | 49 | 181.7 | 169.4 | 57.1 | 83.4
663 | 427 | 49.1 | 181.9 | 169.4 | 57.2 | 83.6
664 | 428 | 49.3 | 181.9 | 169.5 | 57.2 | 83.9
665 | 429 | 49.4 | 182 | 169.4 | 57.4 | 84.1
666 | 430 | 49.5 | 182.1 | 169.5 | 57.5 | 84.2
667 | 431 | 49.7 | 182.3 | 169.9 | 57.6 | 84.4
668 | 432 | 49.8 | 182.5 | 170.1 | 57.7 | 84.6
669 | 433 | 49.9 | 182.4 | 170.5 | 57.8 | 84.6
670 | 434 | 50.1 | 182.2 | 170.6 | 57.9 | 84.8
671 | 435 | 50.2 | 182.2 | 170.3 | 57.9 | 84.9
672 | 436 | 50.3 | 182.2 | 170.4 | 58 | 85.1
673 | 437 | 50.4 | 182 | 170.4 | 58.2 | 85.2
674 | 438 | 50.6 | 182.2 | 170.5 | 58.3 | 85.4
675 | 439 | 50.7 | 182.4 | 170.4 | 58.5 | 85.8
676 | 440 | 50.8 | 182.5 | 170.7 | 58.7 | 86
677 | 441 | 50.9 | 182.8 | 170.9 | 58.9 | 86.2
678 | 442 | 51.1 | 183 | 171 | 59 | 86.4
679 | 443 | 51.2 | 183.1 | 171.4 | 59.2 | 86.5
680 | 444 | 51.3 | 183.3 | 171.6 | 59.2 | 86.8
681 | 445 | 51.5 | 183.4 | 172.2 | 59.3 | 86.8
682 | 446 | 51.6 | 183.5 | 172.3 | 59.5 | 86.9
683 | 447 | 51.7 | 183.6 | 172.4 | 59.6 | 87.3
684 | 448 | 51.8 | 183.8 | 172.5 | 59.7 | 87.5
685 | 449 | 52 | 184.1 | 173.5 | 59.8 | 87.6
686 | 450 | 52.1 | 184.3 | 174.5 | 60 | 87.8
687 | 451 | 52.2 | 184.6 | 175.1 | 60.1 | 88.1
688 | 452 | 52.4 | 184.8 | 175.2 | 60.2 | 88.4
689 | 453 | 52.5 | 184.9 | 175.1 | 60.4 | 88.6
690 | 454 | 52.6 | 184.9 | 175.4 | 60.6 | 88.7
691 | 455 | 52.7 | 184.9 | 175.8 | 60.8 | 89.1
692 | 456 | 52.8 | 185.2 | 175.8 | 60.9 | 89.4
693 | 457 | 53 | 185.5 | 175.9 | 61.1 | 89.6
694 | 458 | 53.1 | 185.9 | 176 | 61.3 | 89.7
695 | 459 | 53.2 | 186.4 | 175.9 | 61.4 | 90.1
696 | 460 | 53.3 | 186.7 | 177 | 61.6 | 90.4
697 | 461 | 53.4 | 187.1 | 177.5 | 61.8 | 90.7
698 | 462 | 53.6 | 187.4 | 177.4 | 62 | 90.9
699 | 463 | 53.7 | 187.6 | 177.7 | 62.1 | 91.1
700 | 464 | 53.8 | 188 | 178.2 | 62.4 | 91.3
701 | 465 | 53.9 | 188.2 | 178.7 | 62.5 | 91.6
702 | 466 | 54.1 | 188.4 | 178.4 | 62.6 | 91.8
703 | 467 | 54.2 | 189 | 178.1 | 62.6 | 92
704 | 468 | 54.4 | 189.5 | 178.6 | 62.7 | 92.1
705 | 469 | 54.5 | 189.9 | 179.3 | 62.9 | 92.2
706 | 470 | 54.6 | 189.9 | 179.3 | 63 | 92.4
707 | 471 | 54.8 | 190 | 179.1 | 63.1 | 92.6
708 | 472 | 54.9 | 190.4 | 179.4 | 63.2 | 92.6
709 | 473 | 55 | 190.8 | 179.2 | 63.2 | 92.7
710 | 474 | 55.1 | 190.6 | 179.5 | 63.5 | 93
711 | 475 | 55.2 | 190.7 | 179.6 | 63.7 | 93
712 | 476 | 55.3 | 190.9 | 179.6 | 63.8 | 93.3
713 | 477 | 55.5 | 191 | 179.8 | 63.9 | 93.5
714 | 478 | 55.6 | 191.7 | 180.1 | 64.1 | 93.6
715 | 479 | 55.7 | 192.4 | 179.8 | 64.3 | 93.7
716 | 480 | 55.9 | 192.5 | 179.9 | 64.3 | 93.8
717 | 481 | 56 | 192.4 | 180.4 | 64.4 | 94.1
718 | 482 | 56.1 | 192.2 | 180.3 | 64.6 | 94.3
719 | 483 | 56.2 | 192.3 | 180.7 | 64.7 | 94.5
720 | 484 | 56.3 | 192.8 | 181.3 | 64.9 | 94.6
721 | 485 | 56.5 | 193.1 | 182.1 | 65 | 94.8
722 | 486 | 56.6 | 193.5 | 182.5 | 65.3 | 95.1
723 | 487 | 56.7 | 193.7 | 183.1 | 65.5 | 95.3
724 | 488 | 56.8 | 193.9 | 183.3 | 65.7 | 95.4
725 | 489 | 57 | 194 | 183.5 | 65.9 | 95.7
726 | 490 | 57.1 | 194 | 183.7 | 66.2 | 95.9
727 | 491 | 57.2 | 194 | 183.7 | 66.5 | 96.1
728 | 492 | 57.4 | 194.1 | 183.6 | 66.7 | 96.3
729 | 493 | 57.5 | 194.1 | 183.1 | 67 | 96.4
730 | 494 | 57.6 | 194.1 | 182.9 | 67 | 96.6
731 | 495 | 57.8 | 194.3 | 183 | 67.2 | 96.9
732 | 496 | 57.9 | 194.7 | 183 | 67.5 | 97
733 | 497 | 58 | 195.4 | 183.2 | 67.7 | 97.2
734 | 498 | 58.2 | 195.2 | 183.7 | 67.8 | 97.5
735 | 499 | 58.3 | 195.3 | 183.5 | 67.9 | 97.6
736 | 500 | 58.5 | 195.5 | 183.8 | 68 | 97.9
737 | 501 | 58.6 | 195.4 | 184.2 | 68.1 | 98.1
738 | 502 | 58.7 | 195.3 | 184.3 | 68.3 | 98.4
739 | 503 | 58.8 | 195.2 | 184.7 | 68.5 | 98.6
740 | 504 | 59 | 195.3 | 184.8 | 68.7 | 98.8
741 | 505 | 59.1 | 195.4 | 185 | 68.9 | 99.2
742 | 506 | 59.3 | 195.3 | 185 | 68.9 | 99.3
743 | 507 | 59.4 | 195.3 | 184.8 | 68.9 | 99.5
744 | 508 | 59.6 | 195.7 | 184.6 | 69.1 | 99.7
745 | 509 | 59.7 | 195.5 | 184.8 | 69.2 | 99.8
746 | 510 | 59.8 | 195.5 | 184.5 | 69.3 | 99.8
747 | 511 | 60 | 195.7 | 184.1 | 69.5 | 100
748 | 512 | 60.1 | 196.6 | 184.3 | 69.8 | 100.2
749 | 513 | 60.2 | 197.6 | 184.6 | 70 | 100.4
750 | 514 | 60.4 | 197.6 | 184.7 | 70.2 | 100.7
751 | 515 | 60.5 | 197.6 | 184.7 | 70.2 | 100.9
752 | 516 | 60.6 | 197.3 | 185.3 | 70.3 | 101
753 | 517 | 60.8 | 197.2 | 185.2 | 70.5 | 101.2
754 | 518 | 60.9 | 197 | 185.3 | 70.6 | 101.4
755 | 519 | 61 | 197.1 | 185.3 | 70.8 | 101.7
756 | 520 | 61.2 | 197.4 | 185.2 | 70.9 | 101.9
757 | 521 | 61.3 | 197.6 | 185.2 | 71.1 | 102.2
758 | 522 | 61.4 | 197.6 | 185.7 | 71.2 | 102.4
759 | 523 | 61.6 | 198.1 | 185.8 | 71.3 | 102.8
760 | 524 | 61.7 | 198.5 | 185.8 | 71.5 | 103
761 | 525 | 61.8 | 198.8 | 186.4 | 71.7 | 103.2
762 | 526 | 62 | 198.7 | 186.3 | 71.7 | 103.4
763 | 527 | 62.1 | 198.8 | 186.1 | 71.9 | 103.6
764 | 528 | 62.2 | 199 | 186.2 | 72 | 103.7
765 | 529 | 62.3 | 199 | 186.6 | 72.1 | 103.8
766 | 530 | 62.5 | 199 | 187.1 | 72.2 | 103.9
767 | 531 | 62.6 | 198.9 | 187.1 | 72.3 | 104.1
768 | 532 | 62.7 | 198.9 | 187.1 | 72.4 | 104.3
769 | 533 | 62.8 | 198.9 | 186.9 | 72.5 | 104.6
770 | 534 | 63 | 199.2 | 186.6 | 72.7 | 104.7
771 | 535 | 63.1 | 199.8 | 186.5 | 73 | 104.9
772 | 536 | 63.2 | 200.2 | 186.7 | 73.2 | 105.1
773 | 537 | 63.4 | 200.4 | 187.4 | 73.3 | 105.3
774 | 538 | 63.5 | 200.4 | 188 | 73.4 | 105.5
775 | 539 | 63.6 | 200.8 | 188 | 73.6 | 105.6
776 | 540 | 63.8 | 201.2 | 188.6 | 73.8 | 105.8
777 | 541 | 63.9 | 201.5 | 189.1 | 74 | 106.1
778 | 542 | 64 | 201.8 | 189.3 | 74.1 | 106.2
779 | 543 | 64.2 | 202 | 189.2 | 74.2 | 106.4
780 | 544 | 64.3 | 201.9 | 189.8 | 74.2 | 106.7
781 | 545 | 64.4 | 201.7 | 190.7 | 74.4 | 107
782 | 546 | 64.5 | 201.7 | 191.2 | 74.5 | 107.2
783 | 547 | 64.7 | 201.7 | 191 | 74.7 | 107.4
784 | 548 | 64.8 | 201.7 | 190.7 | 74.8 | 107.7
785 | 549 | 64.9 | 201.9 | 190.5 | 75 | 107.9
786 | 550 | 65.1 | 202.6 | 190.5 | 75.2 | 108
787 | 551 | 65.2 | 203 | 190.6 | 75.4 | 108.3
788 | 552 | 65.3 | 203.1 | 190.8 | 75.7 | 108.5
789 | 553 | 65.5 | 203 | 190.7 | 75.8 | 108.6
790 | 554 | 65.6 | 202.8 | 190.6 | 76.2 | 108.7
791 | 555 | 65.7 | 203.3 | 190.9 | 76.3 | 108.9
792 | 556 | 65.9 | 203.4 | 191.2 | 76.5 | 109.1
793 | 557 | 66 | 203.3 | 191.5 | 76.6 | 109.4
794 | 558 | 66.1 | 203.3 | 191.7 | 76.7 | 109.6
795 | 559 | 66.3 | 203.3 | 191.9 | 76.8 | 109.8
796 | 560 | 66.4 | 203.2 | 191.9 | 77 | 110.2
797 | 561 | 66.5 | 203.1 | 192 | 77.2 | 110.5
798 | 562 | 66.7 | 203.1 | 191.7 | 77.4 | 110.7
799 | 563 | 66.8 | 203.2 | 191.6 | 77.6 | 110.7
800 | 564 | 66.9 | 203.3 | 191.5 | 77.8 | 111
801 | 565 | 67.1 | 203.4 | 191.3 | 77.9 | 111.2
802 | 566 | 67.2 | 203.8 | 191.4 | 78.1 | 111.4
803 | 567 | 67.3 | 204 | 191.5 | 78.2 | 111.6
804 | 568 | 67.5 | 204.1 | 191.9 | 78.2 | 111.8
805 | 569 | 67.6 | 204.3 | 192.5 | 78.3 | 111.9
806 | 570 | 67.7 | 204.4 | 193.5 | 78.4 | 112.3
807 | 571 | 67.8 | 204.7 | 194 | 78.5 | 112.5
808 | 572 | 68 | 205.2 | 194 | 78.6 | 112.7
809 | 573 | 68.1 | 205.7 | 194.6 | 78.7 | 113
810 | 574 | 68.2 | 206.1 | 194.7 | 78.9 | 113.3
811 | 575 | 68.3 | 206.2 | 195.1 | 79.1 | 113.6
812 | 576 | 68.5 | 206.4 | 195.1 | 79.2 | 113.8
813 | 577 | 68.6 | 206.4 | 195.4 | 79.3 | 114
814 | 578 | 68.7 | 206.6 | 195.7 | 79.5 | 114.3
815 | 579 | 68.8 | 206.4 | 196.3 | 79.6 | 114.7
816 | 580 | 68.9 | 206.5 | 197 | 79.8 | 115
817 | 581 | 69.1 | 206.6 | 197.1 | 79.9 | 115.2
818 | 582 | 69.2 | 206.8 | 197.4 | 80.1 | 115.5
819 | 583 | 69.4 | 206.8 | 197.3 | 80.3 | 115.7
820 | 584 | 69.5 | 206.8 | 197.3 | 80.5 | 115.9
821 | 585 | 69.7 | 206.8 | 197.6 | 80.7 | 116.1
822 | 586 | 69.8 | 206.8 | 198.4 | 80.8 | 116.4
823 | 587 | 69.9 | 206.6 | 198.8 | 80.9 | 116.6
824 | 588 | 70.1 | 206.8 | 198.4 | 81 | 116.9
825 | 589 | 70.2 | 207.2 | 198.2 | 81.1 | 117.2
826 | 590 | 70.4 | 207.5 | 197.8 | 81.1 | 117.4
827 | 591 | 70.5 | 207.6 | 197.5 | 81.4 | 117.6
828 | 592 | 70.6 | 207.8 | 198.3 | 81.5 | 117.8
829 | 593 | 70.8 | 208.1 | 199 | 81.6 | 118.1
830 | 594 | 70.9 | 208.3 | 199.2 | 81.8 | 118.3
831 | 595 | 71.1 | 208.6 | 198.9 | 82 | 118.6
832 | 596 | 71.2 | 208.8 | 198.8 | 82.3 | 118.9
833 | 597 | 71.4 | 209 | 198.5 | 82.5 | 119.1
834 | 598 | 71.5 | 209.5 | 198.5 | 82.7 | 119.3
835 | 599 | 71.7 | 209.9 | 198.6 | 82.9 | 119.6
836 | 600 | 71.8 | 210.1 | 199 | 83 | 119.9
837 | 601 | 72 | 210.5 | 199.4 | 83.2 | 120.1
838 | 602 | 72.1 | 210.5 | 199.5 | 83.4 | 120.2
839 | 603 | 72.3 | 210.5 | 199.9 | 83.5 | 120.4
840 | 604 | 72.4 | 210.4 | 199.9 | 83.7 | 120.7
841 | 605 | 72.6 | 210.2 | 199.7 | 83.8 | 120.8
842 | 606 | 72.7 | 210.3 | 199.3 | 83.9 | 121
843 | 607 | 72.8 | 210.5 | 199.1 | 84 | 121
844 | 608 | 72.9 | 211 | 199.2 | 84.1 | 121
845 | 609 | 73.1 | 211.1 | 200.2 | 84.2 | 121.2
846 | 610 | 73.2 | 211.2 | 200.6 | 84.4 | 121.4
847 | 611 | 73.3 | 211.3 | 200.6 | 84.6 | 121.6
848 | 612 | 73.4 | 211.4 | 200.9 | 84.7 | 121.8
849 | 613 | 73.5 | 211.3 | 200.8 | 84.9 | 122
850 | 614 | 73.7 | 211.6 | 200.8 | 85 | 122.2
851 | 615 | 73.8 | 211.6 | 200.4 | 85.1 | 122.4
852 | 616 | 73.9 | 211.8 | 200.1 | 85.3 | 122.6
853 | 617 | 74 | 211.9 | 200 | 85.5 | 122.7
854 | 618 | 74.1 | 212.2 | 199.8 | 85.7 | 122.8
855 | 619 | 74.3 | 212.2 | 199.8 | 85.8 | 123
856 | 620 | 74.4 | 212.1 | 199.8 | 85.9 | 123.4
857 | 621 | 74.5 | 211.8 | 200.2 | 86 | 123.6
858 | 622 | 74.6 | 211.8 | 200.9 | 86.1 | 123.8
859 | 623 | 74.7 | 211.8 | 201.3 | 86.1 | 124
860 | 624 | 74.8 | 211.9 | 201 | 86.2 | 124.2
861 | 625 | 75 | 212.5 | 200.7 | 86.3 | 124.5
862 | 626 | 75.1 | 212.8 | 201.4 | 86.4 | 124.6
863 | 627 | 75.2 | 213 | 202.3 | 86.5 | 124.8
864 | 628 | 75.3 | 213.3 | 202.9 | 86.6 | 125.2
865 | 629 | 75.4 | 213.3 | 202.9 | 86.8 | 125.4
866 | 630 | 75.5 | 213.4 | 203.2 | 87 | 125.6
867 | 631 | 75.7 | 213.3 | 203.3 | 87.2 | 125.9
868 | 632 | 75.8 | 213.7 | 203.1 | 87.5 | 126.1
869 | 633 | 76 | 214.1 | 203.2 | 87.8 | 126.2
870 | 634 | 76.1 | 214.3 | 203.1 | 88.1 | 126.4
871 | 635 | 76.3 | 214.2 | 203.9 | 88.3 | 126.7
872 | 636 | 76.4 | 214.3 | 204.1 | 88.5 | 127
873 | 637 | 76.6 | 214.2 | 204.2 | 88.7 | 127.1
874 | 638 | 76.7 | 214.4 | 204.2 | 89 | 127.4
875 | 639 | 76.9 | 214 | 204.3 | 89.2 | 127.8
876 | 640 | 77.1 | 214.9 | 204.6 | 89.3 | 128.2
877 | 641 | 77.2 | 216.1 | 204.8 | 89.7 | 128.3
878 | 642 | 77.4 | 215.9 | 204.7 | 89.8 | 128.5
879 | 643 | 77.6 | 217.1 | 204.9 | 90 | 128.8
880 | 644 | 77.8 | 218.3 | 205.5 | 90.1 | 129.2
881 | 645 | 78 | 218.1 | 205.7 | 90.2 | 129.4
882 | 646 | 78.1 | 218.5 | 205.6 | 90.3 | 129.4
883 | 647 | 78.3 | 218.5 | 205.5 | 90.4 | 129.7
884 | 648 | 78.4 | 218.4 | 205.6 | 90.6 | 130
885 | 649 | 78.5 | 218.2 | 205.5 | 90.7 | 130.1
886 | 650 | 78.7 | 218.2 | 205.7 | 90.9 | 130.2
887 | 651 | 78.8 | 218.2 | 205.8 | 90.9 | 130.4
888 | 652 | 78.9 | 218.4 | 206.4 | 91 | 130.6
889 | 653 | 79.1 | 218.5 | 206.7 | 91.2 | 130.7
890 | 654 | 79.2 | 218.7 | 206.8 | 91.3 | 131
891 | 655 | 79.3 | 218.9 | 206.5 | 91.5 | 131.1
892 | 656 | 79.5 | 219.4 | 206.5 | 91.7 | 131.2
893 | 657 | 79.6 | 219.8 | 206.7 | 91.8 | 131.4
894 | 658 | 79.7 | 219.9 | 207.3 | 91.9 | 131.5
895 | 659 | 79.9 | 219.8 | 207.8 | 92 | 131.8
896 | 660 | 80 | 220 | 208.1 | 92.2 | 132.1
897 | 661 | 80.1 | 220.1 | 208.3 | 92.4 | 132.3
898 | 662 | 80.2 | 220.2 | 208.1 | 92.6 | 132.6
899 | 663 | 80.4 | 220.6 | 208.9 | 92.7 | 132.8
900 | 664 | 80.5 | 221.1 | 209.5 | 92.9 | 133.1
901 | 665 | 80.7 | 221.1 | 209.7 | 93 | 133.2
902 | 666 | 80.8 | 221.1 | 209.9 | 93.1 | 133.4
903 | 667 | 81 | 220.9 | 210.1 | 93.4 | 133.6
904 | 668 | 81.1 | 220.7 | 210 | 93.5 | 133.9
905 | 669 | 81.2 | 220.7 | 210.1 | 93.6 | 134.1
906 | 670 | 81.4 | 221 | 209.9 | 93.6 | 134.4
907 | 671 | 81.5 | 221.1 | 210.4 | 93.7 | 134.5
908 | 672 | 81.6 | 220.9 | 210.8 | 93.9 | 134.8
909 | 673 | 81.7 | 221 | 210.9 | 94.1 | 135
910 | 674 | 81.9 | 221.3 | 211.4 | 94.3 | 135.2
911 | 675 | 82 | 221.8 | 211.3 | 94.4 | 135.4
912 | 676 | 82.1 | 222.3 | 211.3 | 94.5 | 135.7
913 | 677 | 82.3 | 223 | 211.6 | 94.6 | 135.9
914 | 678 | 82.4 | 223.4 | 211.8 | 94.8 | 136.1
915 | 679 | 82.5 | 224.6 | 211.9 | 95 | 136.4
916 | 680 | 82.7 | 225.2 | 212.5 | 95.2 | 136.8
917 | 681 | 82.8 | 225.3 | 212.5 | 95.4 | 136.9
918 | 682 | 82.9 | 225.5 | 213.3 | 95.6 | 137.1
919 | 683 | 83.1 | 225.8 | 213.9 | 95.9 | 137.6
920 | 684 | 83.2 | 226.1 | 213.8 | 96.1 | 137.9
921 | 685 | 83.4 | 226.8 | 213.9 | 96.4 | 138.2
922 | 686 | 83.5 | 227.5 | 214.9 | 96.8 | 138.5
923 | 687 | 83.7 | 227.7 | 215.7 | 97 | 138.7
924 | 688 | 83.9 | 227.9 | 216.1 | 97.1 | 139
925 | 689 | 84.1 | 228.1 | 217 | 97.4 | 139.3
926 | 690 | 84.2 | 228.5 | 217.8 | 97.7 | 139.8
927 | 691 | 84.4 | 228.9 | 217.8 | 98 | 140
928 | 692 | 84.6 | 229.7 | 218.1 | 98.2 | 140.3
929 | 693 | 84.8 | 229.9 | 219.1 | 98.3 | 140.7
930 | 694 | 85 | 230.5 | 220 | 98.6 | 141.1
931 | 695 | 85.2 | 230.9 | 221.2 | 98.8 | 141.5
932 | 696 | 85.4 | 231.4 | 221.4 | 99 | 141.9
933 | 697 | 85.6 | 231.7 | 221.9 | 99.1 | 142.1
934 | 698 | 85.8 | 232 | 222.1 | 99.2 | 142.4
935 | 699 | 85.9 | 233.8 | 222.1 | 99.4 | 142.6
936 | 700 | 86.1 | 234 | 222.3 | 99.6 | 142.9
937 | 701 | 86.3 | 234 | 223.1 | 99.9 | 143.1
938 | 702 | 86.5 | 234.1 | 223.3 | 100.2 | 143.3
939 | 703 | 86.7 | 234.4 | 223.5 | 100.4 | 143.5
940 | 704 | 86.9 | 234.9 | 223.8 | 100.7 | 143.8
941 | 705 | 87.1 | 235 | 223.6 | 101 | 144
942 | 706 | 87.3 | 235.3 | 223.6 | 101.2 | 144.2
943 | 707 | 87.5 | 235.6 | 223.6 | 101.6 | 144.5
944 | 708 | 87.6 | 236.1 | 223.4 | 101.7 | 144.6
945 | 709 | 87.8 | 236.4 | 223.8 | 101.9 | 144.8
946 | 710 | 88 | 236.6 | 224.1 | 102.2 | 145
947 | 711 | 88.2 | 236.7 | 224.3 | 102.4 | 145.4
948 | 712 | 88.3 | 236.9 | 224.6 | 102.6 | 145.6
949 | 713 | 88.5 | 237.4 | 224.9 | 102.7 | 145.8
950 | 714 | 88.7 | 237.6 | 225.5 | 102.8 | 146.1
951 | 715 | 88.8 | 238.2 | 225.9 | 102.9 | 146.5
952 | 716 | 89 | 239.1 | 225.9 | 103.2 | 146.8
953 | 717 | 89.2 | 239.4 | 226.6 | 103.3 | 147.2
954 | 718 | 89.3 | 239.7 | 226.6 | 103.5 | 147.4
955 | 719 | 89.5 | 240.4 | 226.4 | 103.6 | 147.7
956 | 720 | 89.6 | 240.8 | 226.5 | 103.9 | 148
957 | 721 | 89.8 | 240.9 | 226.8 | 103.9 | 148.2
958 | 722 | 89.9 | 241 | 227 | 104 | 148.5
959 | 723 | 90 | 241.3 | 226.9 | 104.3 | 148.8
960 | 724 | 90.2 | 243.5 | 227.4 | 104.5 | 149.2
961 | 725 | 90.3 | 244.5 | 228.4 | 104.7 | 149.5
962 | 726 | 90.5 | 244.5 | 228.7 | 104.9 | 149.7
963 | 727 | 90.6 | 244.7 | 229.3 | 105.1 | 150.1
964 | 728 | 90.8 | 244.9 | 229.2 | 105.2 | 150.5
965 | 729 | 90.9 | 245 | 229.4 | 105.3 | 150.8
966 | 730 | 91.1 | 246 | 229.5 | 105.5 | 151
967 | 731 | 91.2 | 246.4 | 230.1 | 105.7 | 151.3
968 | 732 | 91.4 | 246.8 | 230.2 | 106 | 151.6
969 | 733 | 91.5 | 247.2 | 230.3 | 106.2 | 151.9
970 | 734 | 91.7 | 246.9 | 230.2 | 106.4 | 152.1
971 | 735 | 91.8 | 246.7 | 230.6 | 106.5 | 152.2
972 | 736 | 92 | 246.7 | 230.4 | 106.5 | 152.4
973 | 737 | 92.1 | 246.8 | 230.4 | 106.6 | 152.7
974 | 738 | 92.2 | 247 | 230.4 | 106.8 | 153.1
975 | 739 | 92.3 | 247.5 | 230.4 | 107 | 153.2
976 | 740 | 92.5 | 247.9 | 230.7 | 107.1 | 153.4
977 | 741 | 92.6 | 248.2 | 230.9 | 107.3 | 153.7
978 | 742 | 92.7 | 248.4 | 231.1 | 107.5 | 154.1
979 | 743 | 92.9 | 248.6 | 231.2 | 107.6 | 154.3
980 | 744 | 93 | 249 | 231.9 | 107.7 | 154.6
981 | 745 | 93.1 | 249.2 | 232.5 | 107.9 | 154.8
982 | 746 | 93.3 | 249.4 | 233.4 | 108.1 | 155
983 | 747 | 93.4 | 249.7 | 234.1 | 108.2 | 155.3
984 | 748 | 93.5 | 249.9 | 234.5 | 108.3 | 155.6
985 | 749 | 93.7 | 249.9 | 234.7 | 108.5 | 155.9
986 | 750 | 93.8 | 250.3 | 234.9 | 108.6 | 156.3
987 | 751 | 93.9 | 250.5 | 235.2 | 108.8 | 156.5
988 | 752 | 94.1 | 250.6 | 235.1 | 109.1 | 156.8
989 | 753 | 94.2 | 250.8 | 235.9 | 109.2 | 157.1
990 | 754 | 94.4 | 251.1 | 236.2 | 109.5 | 157.4
991 | 755 | 94.5 | 251.5 | 236.1 | 109.7 | 157.7
992 | 756 | 94.6 | 251.7 | 236.1 | 109.9 | 158
993 | 757 | 94.8 | 252 | 236.4 | 110.1 | 158.3
994 | 758 | 94.9 | 252.1 | 236.2 | 110.3 | 158.6
995 | 759 | 95.1 | 252.2 | 236.4 | 110.5 | 158.9
996 | 760 | 95.2 | 252.3 | 236.6 | 110.6 | 159.3
997 | 761 | 95.3 | 252.6 | 237 | 110.8 | 159.6
998 | 762 | 95.5 | 254 | 237.8 | 111 | 159.8
999 | 763 | 95.6 | 254 | 238.2 | 111.1 | 160.2
1000 | 764 | 95.8 | 254.2 | 238.3 | 111.3 | 160.5
1001 | 765 | 95.9 | 254.5 | 238.6 | 111.5 | 160.6
1002 | 766 | 96.1 | 254.7 | 239.3 | 111.7 | 160.8
1003 | 767 | 96.2 | 254.7 | 239.6 | 111.8 | 161.1
1004 | 768 | 96.3 | 254.6 | 239.5 | 111.8 | 161.4
1005 | 769 | 96.5 | 254.9 | 239 | 112 | 161.6
1006 | 770 | 96.6 | 255 | 238.6 | 112.2 | 161.8
1007 | 771 | 96.8 | 255 | 238.3 | 112.4 | 162.1
1008 | 772 | 96.9 | 255.1 | 238.1 | 112.6 | 162.3
1009 | 773 | 97 | 255.3 | 238 | 112.8 | 162.5
1010 | 774 | 97.2 | 255.4 | 237.8 | 113 | 162.6
1011 | 775 | 97.3 | 255.4 | 238.2 | 113.1 | 162.8
1012 | 776 | 97.4 | 255.5 | 238.8 | 113.3 | 163.1
1013 | 777 | 97.5 | 255.5 | 239.8 | 113.5 | 163.2
1014 | 778 | 97.7 | 255.7 | 239.7 | 113.6 | 163.5
1015 | 779 | 97.8 | 255.8 | 240.5 | 113.9 | 163.7
1016 | 780 | 97.9 | 255.8 | 240.9 | 114 | 163.9
1017 | 781 | 98.1 | 256.2 | 240.8 | 114.1 | 164
1018 | 782 | 98.2 | 256.6 | 240.9 | 114.3 | 164.2
1019 | 783 | 98.3 | 256.9 | 241.2 | 114.5 | 164.5
1020 | 784 | 98.4 | 257.5 | 242 | 114.6 | 164.9
1021 | 785 | 98.6 | 257.8 | 243.2 | 114.8 | 165.2
1022 | 786 | 98.7 | 258 | 243.8 | 115 | 165.5
1023 | 787 | 98.9 | 258.1 | 243.5 | 115.2 | 165.8
1024 | 788 | 99 | 258.5 | 243.7 | 115.5 | 166.2
1025 | 789 | 99.2 | 259.2 | 243.9 | 115.7 | 166.4
1026 | 790 | 99.3 | 259.6 | 243.6 | 115.9 | 166.4
1027 | 791 | 99.4 | 259.7 | 243.7 | 116.1 | 166.6
1028 | 792 | 99.6 | 260.2 | 244.5 | 116.2 | 167
1029 | 793 | 99.8 | 260.5 | 245 | 116.4 | 167.3
1030 | 794 | 99.9 | 260.8 | 244.9 | 116.5 | 167.5
1031 | 795 | 100.1 | 261 | 245.1 | 116.6 | 167.8
1032 | 796 | 100.2 | 261.2 | 245.9 | 116.8 | 168.1
1033 | 797 | 100.4 | 261.6 | 246.6 | 117 | 168.3
1034 | 798 | 100.6 | 261.7 | 247.1 | 117.3 | 168.6
1035 | 799 | 100.7 | 261.8 | 246.6 | 117.5 | 168.9
1036 | 800 | 100.9 | 262 | 246.4 | 117.7 | 169.2
1037 | 801 | 101 | 262 | 246.3 | 117.8 | 169.6
1038 | 802 | 101.2 | 262.1 | 246.3 | 118 | 169.9
1039 | 803 | 101.3 | 262.3 | 246.6 | 118.3 | 170.3
1040 | 804 | 101.5 | 262.9 | 247 | 118.5 | 170.5
1041 | 805 | 101.7 | 263.1 | 247.8 | 118.7 | 170.8
1042 | 806 | 101.8 | 263.1 | 247.7 | 118.9 | 171.1
1043 | 807 | 102 | 263.2 | 247.8 | 119.1 | 171.4
1044 | 808 | 102.1 | 263.3 | 247.6 | 119.4 | 171.7
1045 | 809 | 102.3 | 263.6 | 248 | 119.7 | 172
1046 | 810 | 102.5 | 263.7 | 249 | 119.9 | 172.3
1047 | 811 | 102.6 | 264.1 | 249.8 | 120.2 | 172.6
1048 | 812 | 102.8 | 264.5 | 250.5 | 120.3 | 172.9
1049 | 813 | 103 | 264.3 | 250.9 | 120.5 | 173.2
1050 | 814 | 103.2 | 264.2 | 251.1 | 120.6 | 173.6
1051 | 815 | 103.3 | 264.3 | 250.8 | 120.9 | 173.8
1052 | 816 | 103.5 | 264.5 | 251.3 | 121 | 174
1053 | 817 | 103.7 | 264.5 | 251.4 | 121.2 | 174.3
1054 | 818 | 103.9 | 264.7 | 251.5 | 121.3 | 174.5
1055 | 819 | 104.1 | 264.8 | 251.3 | 121.5 | 174.8
1056 | 820 | 104.2 | 264.7 | 251.1 | 121.6 | 175.2
1057 | 821 | 104.4 | 264.9 | 251.2 | 121.8 | 175.3
1058 | 822 | 104.6 | 265.3 | 251.5 | 122 | 175.5
1059 | 823 | 104.7 | 265.4 | 251.5 | 122.2 | 175.7
1060 | 824 | 104.9 | 265.7 | 252.1 | 122.4 | 175.9
1061 | 825 | 105.1 | 265.9 | 252.8 | 122.6 | 176.2
1062 | 826 | 105.2 | 266 | 253 | 122.7 | 176.5
1063 | 827 | 105.4 | 266.1 | 252.9 | 122.9 | 176.6
1064 | 828 | 105.5 | 266.3 | 252.5 | 123.1 | 176.9
1065 | 829 | 105.7 | 267.2 | 252.3 | 123.3 | 177.2
1066 | 830 | 105.8 | 269 | 252.3 | 123.5 | 177.6
1067 | 831 | 106 | 269.1 | 252.7 | 123.6 | 177.8
1068 | 832 | 106.2 | 269.5 | 252.7 | 123.8 | 178
1069 | 833 | 106.3 | 269.2 | 252.7 | 124 | 178.2
1070 | 834 | 106.5 | 268.8 | 253.4 | 124.1 | 178.5
1071 | 835 | 106.6 | 268.8 | 254 | 124.3 | 178.7
1072 | 836 | 106.8 | 268.7 | 253.7 | 124.4 | 178.8
1073 | 837 | 106.9 | 268.8 | 253.4 | 124.4 | 179
1074 | 838 | 107.1 | 268.9 | 253.5 | 124.6 | 179.1
1075 | 839 | 107.2 | 269.2 | 253.6 | 124.7 | 179.3
1076 | 840 | 107.4 | 269.7 | 253.1 | 124.8 | 179.4
1077 | 841 | 107.5 | 269.7 | 252.8 | 124.9 | 179.6
1078 | 842 | 107.7 | 269.9 | 252.7 | 125.1 | 179.8
1079 | 843 | 107.8 | 270.2 | 252.7 | 125.3 | 180
1080 | 844 | 107.9 | 270.6 | 253.1 | 125.5 | 180.3
1081 | 845 | 108 | 270.5 | 254 | 125.7 | 180.5
1082 | 846 | 108.2 | 270.5 | 253.9 | 125.9 | 180.8
1083 | 847 | 108.3 | 270.7 | 253.9 | 126.1 | 181
1084 | 848 | 108.4 | 271.2 | 254.1 | 126.3 | 181.2
1085 | 849 | 108.6 | 270.9 | 254.8 | 126.6 | 181.6
1086 | 850 | 108.7 | 270.6 | 254.8 | 126.7 | 181.7
1087 | 851 | 108.8 | 270.4 | 254.7 | 127.1 | 181.8
1088 | 852 | 109 | 270.5 | 254.8 | 127.3 | 182.1
1089 | 853 | 109.1 | 271.3 | 255 | 127.4 | 182.5
1090 | 854 | 109.2 | 271.9 | 255.6 | 127.7 | 182.9
1091 | 855 | 109.4 | 272.4 | 256.4 | 128 | 183.4
1092 | 856 | 109.6 | 273.3 | 257 | 128.4 | 183.7
1093 | 857 | 109.7 | 274.1 | 257.7 | 128.7 | 184
1094 | 858 | 109.9 | 274.7 | 258 | 129.1 | 184.3
1095 | 859 | 110.1 | 275.2 | 258.4 | 129.4 | 184.6
1096 | 860 | 110.3 | 275.4 | 258.9 | 129.6 | 185.1
1097 | 861 | 110.5 | 275.1 | 259.4 | 129.7 | 185.4
1098 | 862 | 110.7 | 274.9 | 259.6 | 129.9 | 185.7
1099 | 863 | 110.9 | 274.6 | 260.1 | 130.2 | 186.2
1100 | 864 | 111.1 | 274.7 | 260.2 | 130.5 | 186.6
1101 | 865 | 111.3 | 274.8 | 260 | 130.7 | 186.9
1102 | 866 | 111.5 | 274.9 | 259.9 | 131 | 187.3
1103 | 867 | 111.7 | 275.4 | 260.1 | 131.2 | 187.6
1104 | 868 | 111.9 | 275.9 | 260.4 | 131.5 | 187.9
1105 | 869 | 112.1 | 276.3 | 260.4 | 131.7 | 188.1
1106 | 870 | 112.3 | 276.2 | 260.5 | 132 | 188.4
1107 | 871 | 112.5 | 276.1 | 260.7 | 132.2 | 188.6
1108 | 872 | 112.7 | 276 | 260.7 | 132.3 | 188.9
1109 | 873 | 112.9 | 275.7 | 260.8 | 132.5 | 189.1
1110 | 874 | 113.1 | 275.1 | 261 | 132.7 | 189.5
1111 | 875 | 113.3 | 274.7 | 261.1 | 132.8 | 189.8
1112 | 876 | 113.5 | 274.6 | 261.6 | 133 | 190
1113 | 877 | 113.7 | 274.5 | 261.9 | 133.2 | 190.1
1114 | 878 | 113.9 | 274.4 | 261.4 | 133.3 | 190.3
1115 | 879 | 114 | 274.1 | 261.2 | 133.4 | 190.3
1116 | 880 | 114.2 | 273.8 | 261.5 | 133.5 | 190.5
1117 | 881 | 114.4 | 273.5 | 261.3 | 133.7 | 190.7
1118 | 882 | 114.5 | 274 | 260.9 | 133.8 | 190.9
1119 | 883 | 114.6 | 274.3 | 261.3 | 133.9 | 191.1
1120 | 884 | 114.8 | 274.5 | 261.7 | 134.1 | 191.3
1121 | 885 | 114.9 | 274.8 | 262.2 | 134.2 | 191.5
1122 | 886 | 115.1 | 274.9 | 262.7 | 134.4 | 191.8
1123 | 887 | 115.2 | 275 | 263 | 134.5 | 192.1
1124 | 888 | 115.3 | 275.3 | 263 | 134.7 | 192.5
1125 | 889 | 115.5 | 275.7 | 262.9 | 134.9 | 192.7
1126 | 890 | 115.6 | 277.2 | 262.9 | 135.2 | 193
1127 | 891 | 115.7 | 277.7 | 263.3 | 135.4 | 193.3
1128 | 892 | 115.9 | 277.7 | 263.2 | 135.6 | 193.7
1129 | 893 | 116 | 277.8 | 263.2 | 135.8 | 193.9
1130 | 894 | 116.2 | 277.7 | 262.8 | 136 | 194.1
1131 | 895 | 116.4 | 277.5 | 262.5 | 136.2 | 194.4
1132 | 896 | 116.5 | 277.8 | 262.5 | 136.4 | 194.5
1133 | 897 | 116.7 | 278.3 | 262.9 | 136.5 | 194.6
1134 | 898 | 116.8 | 278.7 | 263.1 | 136.7 | 194.9
1135 | 899 | 116.9 | 278.7 | 263.4 | 136.8 | 195.1
1136 | 900 | 117.1 | 278.8 | 263.9 | 137 | 195.3
1137 | 901 | 117.2 | 279.3 | 263.8 | 137.2 | 195.6
1138 | 902 | 117.3 | 279.8 | 264.3 | 137.4 | 195.9
1139 | 903 | 117.4 | 280.5 | 264.8 | 137.6 | 196.2
1140 | 904 | 117.6 | 280.8 | 265.2 | 137.7 | 196.4
1141 | 905 | 117.7 | 280.9 | 265.4 | 137.9 | 196.7
1142 | 906 | 117.8 | 281.2 | 265 | 138.2 | 196.8
1143 | 907 | 117.9 | 281.3 | 265.6 | 138.4 | 197
1144 | 908 | 118.1 | 281.1 | 265.9 | 138.7 | 197.2
1145 | 909 | 118.2 | 281.3 | 265.5 | 139 | 197.3
1146 | 910 | 118.3 | 281.3 | 265.3 | 139.2 | 197.4
1147 | 911 | 118.4 | 281.3 | 265.8 | 139.4 | 197.7
1148 | 912 | 118.6 | 281.4 | 266 | 139.6 | 197.9
1149 | 913 | 118.7 | 281.5 | 265.7 | 139.8 | 198.1
1150 | 914 | 118.8 | 281.3 | 265.8 | 140 | 198.3
1151 | 915 | 118.9 | 281 | 265.3 | 140.2 | 198.5
1152 | 916 | 119.1 | 281.1 | 264.8 | 140.4 | 198.6
1153 | 917 | 119.2 | 281.2 | 264.8 | 140.6 | 198.8
1154 | 918 | 119.3 | 281.4 | 264.5 | 140.9 | 198.9
1155 | 919 | 119.4 | 282 | 264.3 | 141.3 | 199.1
1156 | 920 | 119.6 | 282 | 264 | 141.4 | 199.3
1157 | 921 | 119.7 | 282.2 | 264 | 141.6 | 199.5
1158 | 922 | 119.8 | 282.8 | 264.6 | 141.8 | 199.6
1159 | 923 | 119.9 | 282.8 | 265.1 | 142.1 | 199.9
1160 | 924 | 120.1 | 282.9 | 265.4 | 142.2 | 200.2
1161 | 925 | 120.2 | 282.9 | 265.8 | 142.5 | 200.4
1162 | 926 | 120.3 | 283.2 | 266.1 | 142.8 | 200.8
1163 | 927 | 120.5 | 284.1 | 266.8 | 143.2 | 201.2
1164 | 928 | 120.6 | 284.7 | 267.7 | 143.5 | 201.6
1165 | 929 | 120.8 | 285.1 | 268.4 | 143.9 | 201.8
1166 | 930 | 120.9 | 285.8 | 268.5 | 144.5 | 202.1
1167 | 931 | 121.1 | 286.5 | 268.4 | 144.5 | 202.4
1168 | 932 | 121.3 | 285.5 | 269.1 | 144.7 | 202.5
1169 | 933 | 121.4 | 285.3 | 268.8 | 145 | 202.8
1170 | 934 | 121.6 | 285.5 | 269.3 | 145.3 | 203
1171 | 935 | 121.8 | 286.2 | 270.1 | 145.7 | 203.4
1172 | 936 | 121.9 | 287.1 | 270.7 | 146.2 | 203.8
1173 | 937 | 122.1 | 287.6 | 271 | 146.6 | 204.2
1174 | 938 | 122.3 | 287.6 | 271.5 | 146.9 | 204.5
1175 | 939 | 122.5 | 287.7 | 272.3 | 147.2 | 204.7
1176 | 940 | 122.7 | 287.4 | 272.4 | 147.5 | 204.9
1177 | 941 | 122.9 | 287 | 272 | 147.7 | 205.1
1178 | 942 | 123 | 286.7 | 271.6 | 147.9 | 205.3
1179 | 943 | 123.2 | 286.6 | 271.7 | 148.1 | 205.6
1180 | 944 | 123.4 | 286.5 | 271.7 | 148.3 | 205.7
1181 | 945 | 123.5 | 286.8 | 271.7 | 148.4 | 205.8
1182 | 946 | 123.7 | 287.9 | 271.5 | 148.6 | 205.9
1183 | 947 | 123.8 | 288.5 | 271.9 | 148.7 | 206.1
1184 | 948 | 124 | 288.8 | 272.5 | 148.9 | 206.3
1185 | 949 | 124.1 | 288.8 | 272.6 | 149.1 | 206.5
1186 | 950 | 124.2 | 288.6 | 272.5 | 149.4 | 206.6
1187 | 951 | 124.3 | 288.5 | 271.8 | 149.5 | 206.7
1188 | 952 | 124.5 | 288.4 | 271 | 149.7 | 206.8
1189 | 953 | 124.6 | 288.6 | 270.8 | 149.8 | 207
1190 | 954 | 124.6 | 288.9 | 270.6 | 150.1 | 207.2
1191 | 955 | 124.7 | 289.6 | 270.6 | 150.3 | 207.3
1192 | 956 | 124.8 | 290.1 | 270.9 | 150.7 | 207.5
1193 | 957 | 124.9 | 290.5 | 271.2 | 151 | 207.7
1194 | 958 | 125 | 290.9 | 271.9 | 151.2 | 208.1
1195 | 959 | 125.1 | 291.1 | 272 | 151.4 | 208.4
1196 | 960 | 125.1 | 291.3 | 272.6 | 151.5 | 208.8
1197 | 961 | 125.2 | 291.6 | 273.3 | 151.8 | 209.1
1198 | 962 | 125.3 | 291.9 | 273.4 | 152.1 | 209.3
1199 | 963 | 125.4 | 292.1 | 273.7 | 152.5 | 209.6
1200 | 964 | 125.5 | 292.7 | 274.6 | 152.9 | 209.9
1201 | 965 | 125.6 | 292.9 | 275.2 | 153.3 | 210.2
1202 | 966 | 125.7 | 292.9 | 275.3 | 153.6 | 210.5
1203 | 967 | 125.9 | 293.5 | 275.3 | 154.1 | 210.7
1204 | 968 | 126 | 293.7 | 276 | 154.4 | 211
1205 | 969 | 126.1 | 294 | 276.8 | 154.6 | 211.3
1206 | 970 | 126.3 | 294.3 | 276.9 | 154.9 | 211.7
1207 | 971 | 126.4 | 294.2 | 276.8 | 155.2 | 211.9
1208 | 972 | 126.6 | 294 | 276.4 | 155.4 | 212
1209 | 973 | 126.7 | 293.3 | 276 | 155.5 | 212.2
1210 | 974 | 126.9 | 292.8 | 275.8 | 155.6 | 212.4
1211 | 975 | 127 | 292.2 | 275.9 | 155.7 | 212.7
1212 | 976 | 127.1 | 292 | 275.8 | 156 | 213
1213 | 977 | 127.3 | 292.1 | 276.1 | 156.3 | 213.1
1214 | 978 | 127.3 | 292.5 | 277 | 156.5 | 213.3
1215 | 979 | 127.5 | 293.6 | 278.2 | 157 | 213.8
1216 | 980 | 127.6 | 294.4 | 279.1 | 157.4 | 214.4
1217 | 981 | 127.8 | 294.8 | 279.3 | 157.8 | 214.6
1218 | 982 | 127.9 | 295.2 | 279.5 | 158.2 | 214.8
1219 | 983 | 128 | 295.2 | 279.7 | 158.4 | 215.1
1220 | 984 | 128.2 | 295.3 | 279.5 | 158.7 | 215.3
1221 | 985 | 128.3 | 295.2 | 279.8 | 158.9 | 215.5
1222 | 986 | 128.4 | 294.8 | 280.1 | 159.1 | 215.7
1223 | 987 | 128.6 | 294.6 | 279.7 | 159.2 | 215.9
1224 | 988 | 128.7 | 294.5 | 279.3 | 159.4 | 216
1225 | 989 | 128.8 | 294.7 | 279.1 | 159.5 | 216
1226 | 990 | 128.9 | 295.1 | 279.1 | 159.7 | 216.2
1227 | 991 | 129 | 295.3 | 279.4 | 159.9 | 216.5
1228 | 992 | 129.1 | 295.8 | 279.7 | 160.1 | 216.7
1229 | 993 | 129.2 | 296.3 | 280.1 | 160.4 | 216.9
1230 | 994 | 129.3 | 296.3 | 280.1 | 160.6 | 217.2
1231 | 995 | 129.4 | 297 | 279.7 | 160.8 | 217.3
1232 | 996 | 129.5 | 297.2 | 279.5 | 161 | 217.4
1233 | 997 | 129.6 | 297.4 | 279.4 | 161.2 | 217.6
1234 | 998 | 129.7 | 297.7 | 279.5 | 161.4 | 217.8
1235 | 999 | 129.8 | 297.6 | 279.8 | 161.7 | 218
1236 | 1000 | 129.9 | 297.3 | 279.9 | 161.9 | 218.1
1237 | 1001 | 130 | 297.1 | 279.8 | 162 | 218.3
1238 | 1002 | 130.1 | 297.1 | 279.9 | 162.2 | 218.5
1239 | 1003 | 130.2 | 297.3 | 279.6 | 162.5 | 218.8
1240 | 1004 | 130.3 | 297.3 | 279.4 | 162.9 | 218.9
1241 | 1005 | 130.5 | 296.8 | 279.4 | 163.2 | 219
1242 | 1006 | 130.6 | 296.5 | 279.9 | 163.4 | 219.2
1243 | 1007 | 130.7 | 296.5 | 279.7 | 163.7 | 219.4
1244 | 1008 | 130.8 | 296.2 | 279.7 | 164 | 219.6
1245 | 1009 | 130.9 | 296.2 | 279.7 | 164.2 | 219.7
1246 | 1010 | 131 | 296.2 | 279.4 | 164.2 | 219.9
1247 | 1011 | 131.2 | 296.3 | 279.2 | 164.4 | 220.1
1248 | 1012 | 131.3 | 296.2 | 279.4 | 164.5 | 220.1
1249 | 1013 | 131.4 | 296.3 | 279.5 | 164.7 | 220.2
1250 | 1014 | 131.5 | 296.2 | 279.8 | 164.8 | 220.3
1251 | 1015 | 131.6 | 296.4 | 279.3 | 165 | 220.5
1252 | 1016 | 131.7 | 296.4 | 279 | 165.3 | 220.7
1253 | 1017 | 131.8 | 296.4 | 279.4 | 165.5 | 220.9
1254 | 1018 | 132 | 296.4 | 279.5 | 165.6 | 221.1
1255 | 1019 | 132.1 | 296.5 | 279.5 | 165.8 | 221.4
1256 | 1020 | 132.2 | 296.3 | 279.6 | 166 | 221.6
1257 | 1021 | 132.3 | 296.2 | 279.2 | 166.2 | 221.7
1258 | 1022 | 132.4 | 296.5 | 279.4 | 166.4 | 221.9
1259 | 1023 | 132.6 | 296.7 | 279.7 | 166.8 | 222.1
1260 | 1024 | 132.7 | 296.9 | 280 | 167 | 222.3
1261 | 1025 | 132.8 | 297 | 280 | 167.3 | 222.5
1262 | 1026 | 133 | 297.2 | 280.6 | 167.5 | 222.7
1263 | 1027 | 133.1 | 297.7 | 281.4 | 167.7 | 223.1
1264 | 1028 | 133.3 | 298.2 | 281.9 | 168 | 223.5
1265 | 1029 | 133.4 | 299.3 | 282.7 | 168.4 | 223.8
1266 | 1030 | 133.6 | 299.6 | 283.3 | 168.7 | 224
1267 | 1031 | 133.7 | 300 | 283.2 | 168.9 | 224
1268 | 1032 | 133.9 | 300.1 | 283 | 169.1 | 224.1
1269 | 1033 | 134.1 | 300 | 282.8 | 169.3 | 224.2
1270 | 1034 | 134.2 | 299.9 | 282.9 | 169.5 | 224.4
1271 | 1035 | 134.4 | 299.5 | 283.3 | 169.6 | 224.6
1272 | 1036 | 134.6 | 299.2 | 282.8 | 169.8 | 224.8
1273 | 1037 | 134.7 | 299.1 | 282.6 | 170 | 225
1274 | 1038 | 134.9 | 299.5 | 283.1 | 170.3 | 225.3
1275 | 1039 | 135.1 | 300.5 | 283.7 | 170.7 | 225.7
1276 | 1040 | 135.2 | 301.4 | 284.2 | 171 | 225.9
1277 | 1041 | 135.4 | 302.1 | 284.9 | 171.5 | 226.2
1278 | 1042 | 135.6 | 302.7 | 285.5 | 171.8 | 226.4
1279 | 1043 | 135.7 | 303 | 285.8 | 172.1 | 226.6
1280 | 1044 | 135.9 | 302.8 | 286.3 | 172.3 | 226.8
1281 | 1045 | 136.1 | 302.2 | 286.4 | 172.4 | 227
1282 | 1046 | 136.3 | 302 | 286.3 | 172.6 | 227.3
1283 | 1047 | 136.5 | 302 | 286 | 172.8 | 227.3
1284 | 1048 | 136.6 | 301.9 | 285.7 | 173 | 227.4
1285 | 1049 | 136.8 | 302 | 285.5 | 173.2 | 227.5
1286 | 1050 | 137 | 302 | 285.2 | 173.4 | 227.6
1287 | 1051 | 137.2 | 302.1 | 284.9 | 173.5 | 227.7
1288 | 1052 | 137.3 | 302.4 | 285.1 | 173.6 | 227.8
1289 | 1053 | 137.5 | 302.8 | 285.1 | 173.9 | 227.9
1290 | 1054 | 137.7 | 303.2 | 285 | 174.1 | 228.2
1291 | 1055 | 137.8 | 303.4 | 285 | 174.4 | 228.3
1292 | 1056 | 138 | 303.9 | 285 | 174.6 | 228.6
1293 | 1057 | 138.1 | 304.2 | 285.5 | 174.7 | 228.8
1294 | 1058 | 138.3 | 304.8 | 286.2 | 175 | 229.1
1295 | 1059 | 138.5 | 305.5 | 287 | 175.3 | 229.4
1296 | 1060 | 138.6 | 306.9 | 287.5 | 175.5 | 229.7
1297 | 1061 | 138.8 | 307.3 | 288.3 | 175.9 | 230
1298 | 1062 | 138.9 | 307.5 | 288.6 | 176.1 | 230.3
1299 | 1063 | 139.1 | 307.5 | 289.1 | 176.4 | 230.7
1300 | 1064 | 139.3 | 307.7 | 289.4 | 176.8 | 231
1301 | 1065 | 139.5 | 308.1 | 290.1 | 177.2 | 231.3
1302 | 1066 | 139.7 | 308 | 290.4 | 177.6 | 231.7
1303 | 1067 | 139.9 | 308.1 | 290.9 | 177.8 | 231.8
1304 | 1068 | 140 | 307.9 | 291.6 | 178.2 | 232
1305 | 1069 | 140.2 | 307.8 | 291.9 | 178.4 | 232.3
1306 | 1070 | 140.4 | 308 | 291.7 | 178.8 | 232.4
1307 | 1071 | 140.6 | 307.7 | 291.7 | 179 | 232.6
1308 | 1072 | 140.9 | 307.6 | 291.6 | 179.1 | 232.7
1309 | 1073 | 141 | 307.5 | 291.1 | 179.3 | 232.8
1310 | 1074 | 141.2 | 307.4 | 290.8 | 179.4 | 233
1311 | 1075 | 141.4 | 307.3 | 290.8 | 179.5 | 233.1
1312 | 1076 | 141.6 | 308.6 | 290.8 | 179.8 | 233.2
1313 | 1077 | 141.8 | 308.4 | 290.9 | 179.9 | 233.3
1314 | 1078 | 142 | 308.5 | 290.7 | 180 | 233.4
1315 | 1079 | 142.2 | 308.8 | 290.7 | 180.3 | 233.6
1316 | 1080 | 142.3 | 309.2 | 290.7 | 180.5 | 233.7
1317 | 1081 | 142.5 | 309.7 | 291.1 | 180.8 | 233.8
1318 | 1082 | 142.7 | 310 | 291.5 | 181 | 234
1319 | 1083 | 142.9 | 310.4 | 291.6 | 181.3 | 234.3
1320 | 1084 | 143 | 310.8 | 292.2 | 181.6 | 234.5
1321 | 1085 | 143.2 | 311 | 292.6 | 181.9 | 234.8
1322 | 1086 | 143.4 | 311.5 | 293.2 | 182.1 | 235.1
1323 | 1087 | 143.6 | 311.7 | 293.3 | 182.4 | 235.4
1324 | 1088 | 143.8 | 313.5 | 293.4 | 182.7 | 235.6
1325 | 1089 | 143.9 | 314.4 | 293.8 | 183.1 | 236
1326 | 1090 | 144.1 | 315 | 294 | 183.5 | 236.3
1327 | 1091 | 144.3 | 315.6 | 294.5 | 183.8 | 236.6
1328 | 1092 | 144.5 | 315.8 | 295 | 184.2 | 236.8
1329 | 1093 | 144.7 | 315.3 | 295 | 184.5 | 236.9
1330 | 1094 | 144.9 | 314.9 | 294.8 | 184.7 | 237
1331 | 1095 | 145.1 | 314.6 | 294.8 | 185 | 237.1
1332 | 1096 | 145.3 | 314.2 | 295 | 185.2 | 237.3
1333 | 1097 | 145.4 | 313.7 | 295.4 | 185.3 | 237.4
1334 | 1098 | 145.5 | 313.2 | 295.4 | 185.4 | 237.5
1335 | 1099 | 145.6 | 312.8 | 294.8 | 185.5 | 237.5
1336 | 1100 | 145.8 | 312.5 | 294.5 | 185.6 | 237.5
1337 | 1101 | 145.9 | 312.3 | 294.7 | 185.7 | 237.7
1338 | 1102 | 146.1 | 312.5 | 295.1 | 185.9 | 237.9
1339 | 1103 | 146.2 | 313.5 | 295.4 | 186.4 | 238.2
1340 | 1104 | 146.4 | 314.5 | 295.8 | 186.8 | 238.5
1341 | 1105 | 146.6 | 315.2 | 296.6 | 187.1 | 238.8
1342 | 1106 | 146.8 | 315.3 | 296.9 | 187.3 | 238.9
1343 | 1107 | 146.9 | 315.3 | 297.3 | 187.5 | 239.1
1344 | 1108 | 147.1 | 315.3 | 297.9 | 187.8 | 239.5
1345 | 1109 | 147.3 | 315.3 | 297.6 | 188.1 | 239.6
1346 | 1110 | 147.5 | 315.3 | 297.4 | 188.3 | 239.8
1347 | 1111 | 147.7 | 315.4 | 297.3 | 188.6 | 240
1348 | 1112 | 147.9 | 316 | 297.4 | 188.8 | 240.2
1349 | 1113 | 148 | 316.5 | 297.3 | 189 | 240.4
1350 | 1114 | 148.2 | 317.1 | 297.6 | 189.4 | 240.7
1351 | 1115 | 148.4 | 317.9 | 298.3 | 189.8 | 241.1
1352 | 1116 | 148.6 | 318.4 | 299 | 190.1 | 241.4
1353 | 1117 | 148.8 | 319 | 299.9 | 190.4 | 241.6
1354 | 1118 | 149 | 319.4 | 300.4 | 190.6 | 241.8
1355 | 1119 | 149.2 | 319.5 | 300.9 | 190.8 | 242.1
1356 | 1120 | 149.4 | 319.4 | 301.1 | 191.1 | 242.3
1357 | 1121 | 149.6 | 319.3 | 301.2 | 191.3 | 242.4
1358 | 1122 | 149.8 | 319.2 | 301.6 | 191.4 | 242.6
1359 | 1123 | 150 | 319.4 | 302.1 | 191.6 | 242.8
1360 | 1124 | 150.2 | 319.3 | 302.4 | 191.9 | 243
1361 | 1125 | 150.4 | 320.2 | 303 | 192.2 | 243.2
1362 | 1126 | 150.6 | 321.2 | 302.9 | 192.4 | 243.2
1363 | 1127 | 150.8 | 321 | 303.5 | 192.7 | 243.5
1364 | 1128 | 151 | 321.4 | 303.3 | 193.1 | 243.9
1365 | 1129 | 151.2 | 321.9 | 303.5 | 193.4 | 244.1
1366 | 1130 | 151.4 | 322.1 | 303.4 | 193.7 | 244.2
1367 | 1131 | 151.6 | 322.2 | 303.4 | 193.9 | 244.5
1368 | 1132 | 151.8 | 322.6 | 303.5 | 194.2 | 244.7
1369 | 1133 | 152 | 322.4 | 304.1 | 194.4 | 245
1370 | 1134 | 152.2 | 322.5 | 304.3 | 194.7 | 245.3
1371 | 1135 | 152.5 | 322.5 | 304.8 | 195 | 245.6
1372 | 1136 | 152.7 | 322.4 | 305.3 | 195.2 | 245.9
1373 | 1137 | 152.9 | 322.5 | 305.6 | 195.4 | 246.1
1374 | 1138 | 153.1 | 322.6 | 306.4 | 195.6 | 246.4
1375 | 1139 | 153.3 | 322.2 | 306.4 | 195.7 | 246.6
1376 | 1140 | 153.5 | 322.1 | 306.6 | 195.9 | 246.7
1377 | 1141 | 153.7 | 322.2 | 306.9 | 196.1 | 246.8
1378 | 1142 | 154 | 322.6 | 307.5 | 196.4 | 247.2
1379 | 1143 | 154.2 | 322.9 | 308.1 | 196.7 | 247.6
1380 | 1144 | 154.4 | 322.8 | 307.7 | 196.9 | 247.7
1381 | 1145 | 154.6 | 323.1 | 307.4 | 197 | 247.9
1382 | 1146 | 154.9 | 323.2 | 307.6 | 197.2 | 248.1
1383 | 1147 | 155.1 | 323.7 | 307.7 | 197.5 | 248.4
1384 | 1148 | 155.3 | 324.3 | 308.1 | 197.8 | 248.6
1385 | 1149 | 155.6 | 324.8 | 308 | 198.2 | 248.8
1386 | 1150 | 155.8 | 325.3 | 307.8 | 198.6 | 249.1
1387 | 1151 | 156 | 325.6 | 307.9 | 198.9 | 249.3
1388 | 1152 | 156.3 | 326.3 | 307.9 | 199 | 249.4
1389 | 1153 | 156.5 | 326.4 | 308.7 | 199.2 | 249.5
1390 | 1154 | 156.8 | 325.9 | 309 | 199.5 | 249.8
1391 | 1155 | 157 | 325.7 | 308.7 | 199.7 | 250
1392 | 1156 | 157.2 | 325.8 | 308.2 | 199.8 | 250.1
1393 | 1157 | 157.5 | 326 | 308 | 200 | 250.2
1394 | 1158 | 157.7 | 327.1 | 307.8 | 200.2 | 250.3
1395 | 1159 | 158 | 328.1 | 308 | 200.5 | 250.6
1396 | 1160 | 158.2 | 329.4 | 308.7 | 201 | 250.9
1397 | 1161 | 158.5 | 330.7 | 309.1 | 201.4 | 251.1
1398 | 1162 | 158.7 | 331.5 | 309.2 | 201.8 | 251.4
1399 | 1163 | 159 | 332.6 | 309.5 | 202.2 | 251.6
1400 | 1164 | 159.2 | 333 | 309.5 | 202.5 | 251.6
1401 | 1165 | 159.5 | 333 | 309.3 | 202.9 | 251.7
1402 | 1166 | 159.8 | 333.1 | 309 | 203.1 | 251.9
1403 | 1167 | 160 | 332.8 | 308.4 | 203.2 | 252
1404 | 1168 | 160.3 | 332.8 | 308.2 | 203.4 | 252.1
1405 | 1169 | 160.6 | 333.4 | 308.9 | 203.7 | 252.3
1406 | 1170 | 160.8 | 333.9 | 310 | 204.1 | 252.8
1407 | 1171 | 161.1 | 334.2 | 310.3 | 204.4 | 253.1
1408 | 1172 | 161.3 | 334.4 | 310.7 | 204.8 | 253.3
1409 | 1173 | 161.6 | 334.1 | 310.4 | 205.1 | 253.3
1410 | 1174 | 161.9 | 334.1 | 310.5 | 205.5 | 253.5
1411 | 1175 | 162.1 | 334.3 | 310.3 | 205.9 | 253.6
1412.1 | 1176.1 | 162.4 | 334.2 | 310 | 206.2 | 253.7
1413.1 | 1177.1 | 162.7 | 333.6 | 310.2 | 206.5 | 253.9
1414.1 | 1178.1 | 163 | 333.2 | 311.1 | 206.9 | 254.1
1415.1 | 1179.1 | 163.3 | 333.2 | 311 | 207.3 | 254.2
1416.1 | 1180.1 | 163.6 | 333.7 | 311 | 207.9 | 254.3
1417.1 | 1181.1 | 163.9 | 334.4 | 311.1 | 208.4 | 254.6
1418.1 | 1182.1 | 164.2 | 334.9 | 311.2 | 208.8 | 254.8
1419.1 | 1183.1 | 164.5 | 334.7 | 311.6 | 209.1 | 254.9
1420.1 | 1184.1 | 164.8 | 334.4 | 312.1 | 209.3 | 255
1421.1 | 1185.1 | 165.1 | 334.2 | 312.4 | 209.5 | 255.1
1422.1 | 1186.1 | 165.4 | 334.6 | 312.2 | 209.8 | 255.2
1423.1 | 1187.1 | 165.7 | 334.7 | 312.4 | 210.1 | 255.5
1424.1 | 1188.1 | 166 | 334.5 | 312.5 | 210.3 | 255.6
1425.1 | 1189.1 | 166.3 | 335 | 313.1 | 210.5 | 255.7
1426.1 | 1190.1 | 166.6 | 335.2 | 312.6 | 210.8 | 255.7
1427.1 | 1191.1 | 166.8 | 335.2 | 312.8 | 211 | 255.8
1428.1 | 1192.1 | 167.1 | 335.4 | 312.8 | 211.2 | 255.9
1429.1 | 1193.1 | 167.4 | 335.9 | 312.8 | 211.4 | 256
1430.1 | 1194.1 | 167.6 | 337 | 312.9 | 211.7 | 256.2
1431.1 | 1195.1 | 167.9 | 337.2 | 312.5 | 211.9 | 256.5
1432.1 | 1196.1 | 168.2 | 337.5 | 312.6 | 212.2 | 256.7
1433.1 | 1197.1 | 168.4 | 338.2 | 313.5 | 212.7 | 257
1434.1 | 1198.1 | 168.7 | 339.1 | 314.3 | 213.1 | 257.2
1435.1 | 1199.1 | 169 | 339.1 | 315.2 | 213.5 | 257.5
1436.1 | 1200.1 | 169.2 | 339.5 | 315.6 | 214 | 257.8
1437.1 | 1201.1 | 169.5 | 339.8 | 316.5 | 214.5 | 258
1438.1 | 1202.1 | 169.8 | 340.2 | 316.7 | 214.9 | 258.1
1439.1 | 1203.1 | 170.1 | 340.1 | 317.3 | 215.2 | 258.3
1440.1 | 1204.1 | 170.4 | 340 | 318 | 215.4 | 258.4
1441.1 | 1205.1 | 170.7 | 340.2 | 318.7 | 215.9 | 258.7
1442.1 | 1206.1 | 171 | 340.3 | 318.8 | 216.3 | 259
1443.1 | 1207.1 | 171.4 | 340.2 | 319.2 | 216.6 | 259.2
1444.1 | 1208.1 | 171.7 | 339.9 | 319.4 | 216.7 | 259.3
1445.1 | 1209.1 | 172 | 339.9 | 319.4 | 216.9 | 259.5
1446.1 | 1210.1 | 172.3 | 339.9 | 319.3 | 217.2 | 259.9
1447.1 | 1211.1 | 172.6 | 339.7 | 319.6 | 217.5 | 260
1448.1 | 1212.1 | 172.9 | 339.4 | 320.4 | 217.7 | 260.3
1449.1 | 1213.1 | 173.2 | 339.6 | 320.1 | 218 | 260.2
1450.1 | 1214.1 | 173.6 | 339.2 | 319.5 | 218.1 | 260.2
1451.1 | 1215.1 | 173.8 | 338.9 | 319.1 | 218.3 | 260.4
1452.1 | 1216.1 | 174.1 | 338.9 | 319.2 | 218.5 | 260.7
1453.1 | 1217.1 | 174.4 | 339.5 | 319.4 | 218.9 | 260.8
1454.1 | 1218.1 | 174.7 | 341 | 319.9 | 219.3 | 261.1
1455.1 | 1219.1 | 174.9 | 341.5 | 320.3 | 219.7 | 261.2
1456.1 | 1220.1 | 175.2 | 342.1 | 321 | 220.2 | 261.5
1457.1 | 1221.1 | 175.5 | 342.8 | 321.5 | 220.6 | 261.7
1458.1 | 1222.1 | 175.7 | 343 | 321.5 | 220.9 | 261.8
1459.1 | 1223.1 | 176 | 342.9 | 321.2 | 221.2 | 262
1460.1 | 1224.1 | 176.3 | 342.8 | 320.8 | 221.5 | 262
1461.1 | 1225.1 | 176.6 | 342.9 | 320.5 | 221.9 | 262.1
1462.1 | 1226.1 | 176.9 | 342.9 | 320.4 | 222.1 | 262.3
1463.1 | 1227.1 | 177.2 | 342.7 | 320.4 | 222.3 | 262.6
1464.1 | 1228.1 | 177.5 | 342.7 | 320.6 | 222.6 | 262.7
1465.1 | 1229.1 | 177.8 | 342.7 | 320.4 | 222.9 | 262.9
1466.1 | 1230.1 | 178.1 | 342.6 | 320.2 | 223 | 263
1467.1 | 1231.1 | 178.4 | 342.4 | 319.7 | 223.1 | 263
1468.1 | 1232.1 | 178.6 | 342.1 | 319.4 | 223.3 | 263.1
1469.1 | 1233.1 | 178.9 | 342.1 | 319.3 | 223.4 | 263.1
1470.1 | 1234.1 | 179.2 | 342 | 319 | 223.6 | 263.2
1471.1 | 1235.1 | 179.4 | 342.1 | 319.1 | 223.7 | 263.3
1472.1 | 1236.1 | 179.7 | 342.4 | 320 | 224 | 263.5
1473.1 | 1237.1 | 179.9 | 342.7 | 320.3 | 224.3 | 263.6
1474.1 | 1238.1 | 180.1 | 343.2 | 320.5 | 224.7 | 263.8
1475.1 | 1239.1 | 180.4 | 343.4 | 320.9 | 224.8 | 264
1476.1 | 1240.1 | 180.6 | 343.6 | 320.7 | 225 | 264.1
1477.1 | 1241.1 | 180.9 | 343.5 | 320.8 | 225.1 | 264.1
1478.1 | 1242.1 | 181.1 | 343.2 | 320.1 | 225.2 | 264.3
1479.1 | 1243.1 | 181.4 | 343 | 319.7 | 225.2 | 264.3
1480.1 | 1244.1 | 181.6 | 342.8 | 319.5 | 225.4 | 264.4
1481.1 | 1245.1 | 181.8 | 342.8 | 318.8 | 225.6 | 264.4
1482.1 | 1246.1 | 182.1 | 342.8 | 318.3 | 225.9 | 264.4
1483.1 | 1247.1 | 182.3 | 342.9 | 318 | 226 | 264.6
1484.1 | 1248.1 | 182.5 | 342.9 | 318 | 226.2 | 264.8
1485.1 | 1249.1 | 182.7 | 342.6 | 318.1 | 226.4 | 265
1486.1 | 1250.1 | 183 | 342.7 | 317.8 | 226.6 | 265
1487.1 | 1251.1 | 183.2 | 342.9 | 317.6 | 226.9 | 265
1488.1 | 1252.1 | 183.4 | 342.8 | 317.9 | 227 | 265
1489.1 | 1253.1 | 183.6 | 342.8 | 317.9 | 227.3 | 265.1
1490.1 | 1254.1 | 183.9 | 343.2 | 317.7 | 227.7 | 265.1
1491.1 | 1255.1 | 184.1 | 343.6 | 317.3 | 228 | 265.2
1492.1 | 1256.1 | 184.3 | 344 | 317.1 | 228.3 | 265.4
1493.1 | 1257.1 | 184.5 | 344.6 | 317.1 | 228.7 | 265.5
1494.1 | 1258.1 | 184.7 | 345.2 | 317.8 | 229 | 265.7
1495.1 | 1259.1 | 184.9 | 345.9 | 317.9 | 229.4 | 265.9
1496.1 | 1260.1 | 185.1 | 346.4 | 318.7 | 229.7 | 266.2
1497.1 | 1261.1 | 185.4 | 347 | 319.3 | 230.1 | 266.4
1498.1 | 1262.1 | 185.6 | 347.8 | 319.8 | 230.5 | 266.6
1499.1 | 1263.1 | 185.9 | 348.5 | 320.8 | 230.9 | 267
1500.1 | 1264.1 | 186.2 | 349.2 | 321.4 | 231.2 | 267.2
1501.1 | 1265.1 | 186.5 | 349.1 | 322.1 | 231.6 | 267.5
1502.1 | 1266.1 | 186.8 | 349.2 | 322.7 | 231.8 | 267.7
1503.1 | 1267.1 | 187.1 | 349.7 | 323.6 | 232.2 | 267.9
1504.1 | 1268.1 | 187.4 | 349.8 | 324 | 232.5 | 268
1505.1 | 1269.1 | 187.8 | 350 | 325.8 | 232.8 | 268.4
1506.1 | 1270.1 | 188.1 | 350.2 | 325.9 | 233.1 | 268.7
1507.1 | 1271.1 | 188.4 | 350.1 | 326.2 | 233.4 | 269.1
1508.1 | 1272.1 | 188.8 | 350.6 | 326.5 | 233.7 | 269.3
1509.1 | 1273.1 | 189.1 | 350.9 | 327.2 | 234 | 269.5
1510.1 | 1274.1 | 189.4 | 351.2 | 327 | 234.3 | 269.7
1511.1 | 1275.1 | 189.7 | 351.6 | 327.5 | 234.6 | 269.9
1512.1 | 1276.1 | 190.1 | 352.5 | 328.2 | 235.2 | 270.2
1513.1 | 1277.1 | 190.4 | 353.1 | 328.5 | 235.5 | 270.4
1514.1 | 1278.1 | 190.7 | 353.8 | 329.7 | 235.9 | 270.8
1515.1 | 1279.1 | 191.1 | 354.8 | 331.1 | 236.3 | 271
1516.1 | 1280.1 | 191.4 | 354.8 | 331.4 | 236.5 | 271.1
1517.1 | 1281.1 | 191.8 | 355 | 331.9 | 236.8 | 271.3
1518.1 | 1282.1 | 192.2 | 356 | 333 | 237.3 | 271.6
1519.1 | 1283.1 | 192.5 | 356.6 | 332.8 | 237.8 | 271.8
1520.1 | 1284.1 | 192.9 | 356.6 | 333.6 | 238 | 271.8
1521.1 | 1285.1 | 193.2 | 356.8 | 334.3 | 238.3 | 272
1522.1 | 1286.1 | 193.5 | 357 | 334.5 | 238.4 | 272.1
1523.1 | 1287.1 | 193.9 | 356.8 | 334.2 | 238.6 | 272.2
1524.1 | 1288.1 | 194.2 | 356.6 | 334.1 | 238.8 | 272.4
1525.1 | 1289.1 | 194.5 | 356.6 | 334.4 | 238.9 | 272.6
1526.1 | 1290.1 | 194.7 | 356.2 | 335 | 239 | 272.9
1527.1 | 1291.1 | 195 | 356.7 | 335.2 | 239.3 | 273.2
1528.1 | 1292.1 | 195.3 | 357.3 | 335.7 | 239.6 | 273.5
1529.1 | 1293.1 | 195.5 | 357.7 | 336.4 | 240 | 273.8
1530.1 | 1294.1 | 195.8 | 358 | 336.4 | 240.3 | 273.9
1531.1 | 1295.1 | 196.1 | 358.4 | 336.5 | 240.6 | 274.1
1532.1 | 1296.1 | 196.4 | 359.2 | 336.3 | 241 | 274.1
1533.1 | 1297.1 | 196.8 | 359.5 | 336.1 | 241.3 | 274.3
1534.1 | 1298.1 | 197 | 359.7 | 336.4 | 241.7 | 274.5
1535.1 | 1299.1 | 197.4 | 360 | 337.5 | 241.9 | 275
1536.1 | 1300.1 | 197.7 | 360.7 | 338 | 242.2 | 275.2
1537.1 | 1301.1 | 198 | 361.4 | 338.5 | 242.5 | 275.5
1538.1 | 1302.1 | 198.3 | 361.6 | 339.4 | 242.7 | 275.7
1539.1 | 1303.1 | 198.7 | 361.8 | 340.1 | 242.9 | 276
1540.1 | 1304.1 | 199 | 362.1 | 340 | 243.2 | 276
1541.1 | 1305.1 | 199.4 | 362 | 339.6 | 243.4 | 276.2
1542.1 | 1306.1 | 199.7 | 362.7 | 340 | 243.7 | 276.6
1543.1 | 1307.1 | 200 | 363 | 340.1 | 244 | 276.7
1544.1 | 1308.1 | 200.4 | 363.1 | 340.4 | 244.1 | 276.9
1545.1 | 1309.1 | 200.7 | 363.2 | 340 | 244.2 | 277.1
1546.1 | 1310.1 | 201 | 363.5 | 339.9 | 244.4 | 277.2
1547.1 | 1311.1 | 201.3 | 364.3 | 340.1 | 244.8 | 277.5
1548.1 | 1312.1 | 201.7 | 365.1 | 340.4 | 245.3 | 277.7
1549.1 | 1313.1 | 202 | 365.5 | 340.3 | 245.5 | 277.8
1550.1 | 1314.1 | 202.3 | 365.6 | 340.4 | 245.6 | 278.1
1551.1 | 1315.1 | 202.7 | 366.2 | 340.2 | 245.9 | 278.3
1552.1 | 1316.1 | 203 | 366.1 | 339.9 | 246.1 | 278.3
1553.1 | 1317.1 | 203.3 | 366 | 339.4 | 246.3 | 278.4
1554.1 | 1318.1 | 203.6 | 366.1 | 339.3 | 246.4 | 278.5
1555.1 | 1319.1 | 203.9 | 366.4 | 339.7 | 246.6 | 278.8
1556.1 | 1320.1 | 204.2 | 366.6 | 339.9 | 246.8 | 279
1557.1 | 1321.1 | 204.5 | 367 | 340.6 | 247 | 279.3
1558.1 | 1322.1 | 204.8 | 367.4 | 341.1 | 247.2 | 279.7
1559.1 | 1323.1 | 205.2 | 367.5 | 341.9 | 247.5 | 280
1560.1 | 1324.1 | 205.5 | 367.6 | 342 | 247.7 | 280.1
1561.1 | 1325.1 | 205.9 | 367.9 | 342 | 247.9 | 280.1
1562.1 | 1326.1 | 206.2 | 368.2 | 341.9 | 248.2 | 280.2
1563.1 | 1327.1 | 206.6 | 368.4 | 341.8 | 248.3 | 280.4
1564.1 | 1328.1 | 207 | 368.9 | 341.7 | 248.6 | 280.6
1565.1 | 1329.1 | 207.4 | 369.2 | 341.6 | 248.9 | 280.7
1566.1 | 1330.1 | 207.8 | 369.5 | 342.6 | 249.2 | 280.9
1567.1 | 1331.1 | 208.2 | 370.2 | 343.9 | 249.5 | 281.3
1568.1 | 1332.1 | 208.6 | 371 | 344.6 | 250 | 281.5
1569.1 | 1333.1 | 209.1 | 371.9 | 344.9 | 250.5 | 281.7
1570.1 | 1334.1 | 209.5 | 372.7 | 346.1 | 251 | 281.9
1571.1 | 1335.1 | 210 | 373.3 | 347.4 | 251.3 | 282.2
1572.1 | 1336.1 | 210.5 | 373.7 | 347 | 251.6 | 282.4
1573.1 | 1337.1 | 211 | 373.7 | 347 | 251.8 | 282.5
1574.1 | 1338.1 | 211.4 | 374.7 | 347.9 | 252.2 | 282.9
1575.1 | 1339.1 | 211.9 | 376 | 348.5 | 252.6 | 283.1
1576.1 | 1340.1 | 212.4 | 377 | 348.9 | 253 | 283.5
1577.1 | 1341.1 | 212.9 | 377.3 | 349.4 | 253.3 | 283.8
1578.1 | 1342.1 | 213.4 | 378.2 | 350.5 | 253.7 | 284.2
1579.1 | 1343.1 | 213.9 | 378.5 | 351.3 | 253.9 | 284.6
1580.1 | 1344.1 | 214.4 | 378.5 | 351.2 | 254.1 | 284.7
1581.1 | 1345.1 | 214.9 | 378.7 | 351.2 | 254.4 | 284.8
1582.1 | 1346.1 | 215.3 | 378.6 | 351.2 | 254.6 | 285.1
1583.1 | 1347.1 | 215.7 | 378.3 | 351.5 | 254.7 | 285.4
1584.1 | 1348.1 | 216 | 378 | 351.3 | 254.8 | 285.4
1585.1 | 1349.1 | 216.3 | 377.7 | 350.7 | 255 | 285.6
1586.1 | 1350.1 | 216.6 | 377.4 | 350.4 | 255.1 | 285.7
1587.1 | 1351.1 | 216.8 | 377.8 | 349.9 | 255.3 | 285.8
1588.1 | 1352.1 | 217.1 | 378.3 | 349.7 | 255.5 | 285.9
1589.1 | 1353.1 | 217.3 | 378.9 | 349.6 | 255.7 | 286
1590.1 | 1354.1 | 217.6 | 379.1 | 349.5 | 255.9 | 286
1591.1 | 1355.1 | 217.8 | 379.3 | 349.4 | 256.1 | 286
1592.1 | 1356.1 | 218 | 379.7 | 349.5 | 256.3 | 286.1
1593.1 | 1357.1 | 218.3 | 380.2 | 349.6 | 256.5 | 286.3
1594.1 | 1358.1 | 218.6 | 380.9 | 349.7 | 256.8 | 286.5
1595.1 | 1359.1 | 218.9 | 381.3 | 349.5 | 257 | 286.7
1596.1 | 1360.1 | 219.3 | 381.1 | 349.7 | 257.2 | 286.9
1597.1 | 1361.1 | 219.6 | 381 | 350.6 | 257.4 | 287.2
1598.1 | 1362.1 | 220 | 381.1 | 351.4 | 257.5 | 287.5
1599.1 | 1363.1 | 220.4 | 381.1 | 351.7 | 257.7 | 287.8
1600.1 | 1364.1 | 220.8 | 381.3 | 351.8 | 257.7 | 288.2
1601.1 | 1365.1 | 221.1 | 381.4 | 351.6 | 257.8 | 288.3
1602.1 | 1366.1 | 221.5 | 381.7 | 350.9 | 258 | 288.3
1603.1 | 1367.1 | 221.9 | 381.6 | 350.4 | 258.2 | 288.3
1604.1 | 1368.1 | 222.2 | 381.7 | 350.7 | 258.3 | 288.4
1605.1 | 1369.1 | 222.6 | 381.7 | 350 | 258.5 | 288.6
1606.1 | 1370.1 | 223 | 381.7 | 349.8 | 258.6 | 288.7
1607.1 | 1371.1 | 223.4 | 382.2 | 350.1 | 258.8 | 288.7
1608.1 | 1372.1 | 223.7 | 382.7 | 350.3 | 259 | 288.9
1609.1 | 1373.1 | 224.1 | 383.2 | 350.5 | 259.2 | 289.1
1610.1 | 1374.1 | 224.5 | 383.3 | 350.7 | 259.3 | 289.2
1611.1 | 1375.1 | 224.9 | 383.3 | 351.1 | 259.4 | 289.3
1612.1 | 1376.1 | 225.3 | 383 | 351.7 | 259.5 | 289.5
1613.1 | 1377.1 | 225.7 | 382.8 | 351.4 | 259.7 | 289.9
1614.1 | 1378.1 | 226.2 | 382.9 | 351.9 | 259.9 | 290.1
1615.1 | 1379.1 | 226.7 | 383.5 | 352.8 | 260.1 | 290.4
1616.1 | 1380.1 | 227.2 | 384 | 353.7 | 260.3 | 290.7
1617.1 | 1381.1 | 227.8 | 384.4 | 353.9 | 260.5 | 291.1
1618.1 | 1382.1 | 228.5 | 384.8 | 354.4 | 260.7 | 291.4
1619.1 | 1383.1 | 229.1 | 384.8 | 355.2 | 260.9 | 291.7
1620.1 | 1384.1 | 229.8 | 385.6 | 356.3 | 261.1 | 292
1621.1 | 1385.1 | 230.4 | 386.3 | 357 | 261.4 | 292.3
1622.1 | 1386.1 | 231 | 386.5 | 357.1 | 261.5 | 292.5
1623.1 | 1387.1 | 231.7 | 386.4 | 356.8 | 261.6 | 292.6
1624.1 | 1388.1 | 232.2 | 386 | 356.1 | 261.6 | 292.7
1625.1 | 1389.1 | 232.7 | 385.9 | 355.2 | 261.7 | 292.8
1626.1 | 1390.1 | 233.2 | 385.7 | 354.6 | 261.7 | 293
1627.1 | 1391.1 | 233.6 | 385.7 | 355 | 261.9 | 293.3
1628.1 | 1392.1 | 234.1 | 386.6 | 355.7 | 262.1 | 293.6
1629.1 | 1393.1 | 234.7 | 387.4 | 356.6 | 262.3 | 294.1
1630.1 | 1394.1 | 235.2 | 387.4 | 357.1 | 262.4 | 294.4
1631.1 | 1395.1 | 235.8 | 387.1 | 358.3 | 262.5 | 294.5
1632.1 | 1396.1 | 236.4 | 386.8 | 358.4 | 262.5 | 294.7
1633.1 | 1397.1 | 236.9 | 386.8 | 358.4 | 262.7 | 294.9
1634.1 | 1398.1 | 237.4 | 386.6 | 358.3 | 262.7 | 295
1635.1 | 1399.1 | 237.9 | 386.2 | 358.2 | 262.7 | 295.1
1636.1 | 1400.1 | 238.2 | 385.9 | 358.2 | 262.7 | 295.2
1637.1 | 1401.1 | 238.6 | 385.8 | 357.6 | 262.8 | 295.4
1638.1 | 1402.1 | 238.9 | 385.6 | 357.3 | 262.9 | 295.4
1639.1 | 1403.1 | 239.1 | 385.8 | 357.4 | 263 | 295.4
1640.1 | 1404.1 | 239.3 | 386.2 | 357.3 | 263.1 | 295.5
1641.1 | 1405.1 | 239.5 | 386.3 | 357.2 | 263.2 | 295.7
1642.1 | 1406.1 | 239.7 | 386.4 | 357.2 | 263.3 | 295.9
1643.1 | 1407.1 | 239.9 | 386.6 | 357.1 | 263.4 | 295.9
1644.1 | 1408.1 | 240.1 | 387.1 | 357.6 | 263.5 | 296
1645.1 | 1409.1 | 240.3 | 387.4 | 357.9 | 263.7 | 296.2
1646.1 | 1410.1 | 240.4 | 387.4 | 358.3 | 263.8 | 296.5
1647.1 | 1411.1 | 240.6 | 387.2 | 358.4 | 264 | 296.7
1648.1 | 1412.1 | 240.9 | 387.1 | 358.8 | 264.1 | 296.9
1649.1 | 1413.1 | 241.2 | 387 | 359.4 | 264.3 | 297.3
1650.1 | 1414.1 | 241.4 | 387.5 | 360.2 | 264.6 | 297.6
1651.1 | 1415.1 | 241.7 | 387.6 | 360.5 | 264.7 | 297.8
1652.1 | 1416.1 | 242.1 | 387.6 | 360.6 | 264.9 | 297.9
1653.1 | 1417.1 | 242.4 | 387.5 | 360.9 | 265.1 | 298.2
1654.1 | 1418.1 | 242.7 | 387.4 | 361 | 265.3 | 298.5
1655.1 | 1419.1 | 243.1 | 387.2 | 361.5 | 265.4 | 298.8
1656.1 | 1420.1 | 243.5 | 387 | 362 | 265.6 | 299.2
1657.1 | 1421.1 | 243.9 | 386.7 | 362 | 265.7 | 299.3
1658.1 | 1422.1 | 244.4 | 386.2 | 362 | 265.8 | 299.5
1659.1 | 1423.1 | 244.7 | 385.8 | 362.1 | 266 | 299.6
1660.1 | 1424.1 | 245.1 | 385.3 | 362.3 | 266.1 | 299.7
1661.1 | 1425.1 | 245.4 | 385.2 | 362.4 | 266.2 | 299.9
1662.1 | 1426.1 | 245.7 | 385.5 | 362.7 | 266.3 | 300.3
1663.1 | 1427.1 | 246 | 385.5 | 362.6 | 266.5 | 300.4
1664.1 | 1428.1 | 246.3 | 385.4 | 362.3 | 266.7 | 300.7
1665.1 | 1429.1 | 246.6 | 385.3 | 362.1 | 266.9 | 300.9
1666.1 | 1430.1 | 247 | 385.2 | 362.1 | 267 | 301.1
1667.1 | 1431.1 | 247.3 | 384.9 | 361.5 | 267.2 | 301.3
1668.1 | 1432.1 | 247.7 | 385.1 | 361.6 | 267.4 | 301.4
1669.1 | 1433.1 | 248.1 | 385.5 | 361.9 | 267.6 | 301.6
1670.1 | 1434.1 | 248.5 | 385.9 | 362.5 | 267.8 | 301.8
1671.1 | 1435.1 | 248.9 | 386.4 | 363 | 268.1 | 302.1
1672.1 | 1436.1 | 249.4 | 387 | 363.5 | 268.3 | 302.4
1673.1 | 1437.1 | 249.8 | 388 | 364.6 | 268.6 | 302.7
1674.1 | 1438.1 | 250.4 | 388.6 | 365.9 | 269 | 303.1
1675.1 | 1439.1 | 250.9 | 389.3 | 366.3 | 269.3 | 303.4
1676.1 | 1440.1 | 251.6 | 390 | 366.8 | 269.6 | 303.8
1677.1 | 1441.1 | 252.2 | 391 | 367.7 | 269.9 | 304.1
1678.1 | 1442.1 | 252.9 | 392.1 | 368.4 | 270.2 | 304.3
1679.1 | 1443.1 | 253.6 | 392.5 | 369.3 | 270.4 | 304.6
1680.1 | 1444.1 | 254.3 | 392.6 | 369.9 | 270.6 | 305
1681.1 | 1445.1 | 255 | 393.1 | 370 | 270.8 | 305.2
1682.1 | 1446.1 | 255.5 | 393.4 | 369.7 | 270.9 | 305.4
1683.1 | 1447.1 | 255.9 | 393.1 | 369.5 | 271.1 | 305.5
1684.1 | 1448.1 | 256.3 | 392.7 | 369.6 | 271.2 | 305.5
1685.1 | 1449.1 | 256.6 | 392.7 | 369.6 | 271.4 | 305.7
1686.1 | 1450.1 | 256.8 | 392.7 | 369.5 | 271.6 | 305.9
1687.1 | 1451.1 | 257.1 | 392.6 | 369.5 | 271.8 | 306.1
1688.1 | 1452.1 | 257.4 | 392.8 | 369.7 | 272 | 306.3
1689.1 | 1453.1 | 257.6 | 393 | 369.4 | 272.2 | 306.5
1690.1 | 1454.1 | 257.9 | 393.1 | 369 | 272.4 | 306.8
1691.1 | 1455.1 | 258.2 | 393.2 | 368.8 | 272.6 | 307.1
1692.1 | 1456.1 | 258.4 | 393.9 | 369.5 | 272.9 | 307.5
1693.1 | 1457.1 | 258.7 | 394.1 | 369.6 | 273.1 | 307.6
1694.1 | 1458.1 | 259 | 394.1 | 369.6 | 273.3 | 307.8
1695.1 | 1459.1 | 259.4 | 394.3 | 369.6 | 273.5 | 307.9
1696.1 | 1460.1 | 259.6 | 394.8 | 369.4 | 273.6 | 308
1697.1 | 1461.1 | 259.9 | 394.8 | 369.5 | 273.8 | 308.3
1698.1 | 1462.1 | 260.1 | 394.8 | 369.7 | 274.1 | 308.5
1699.1 | 1463.1 | 260.3 | 394.6 | 370.5 | 274.2 | 308.9
1700.1 | 1464.1 | 260.6 | 394.6 | 371.2 | 274.4 | 309.3
1701.1 | 1465.1 | 260.9 | 394.8 | 370.8 | 274.6 | 309.3
1702.1 | 1466.1 | 261.1 | 394.5 | 370.4 | 274.7 | 309.5
1703.1 | 1467.1 | 261.3 | 394.3 | 370.2 | 274.9 | 309.6
1704.1 | 1468.1 | 261.6 | 394.3 | 370.5 | 275.1 | 309.9
1705.1 | 1469.1 | 261.8 | 394.6 | 370.3 | 275.3 | 310
1706.1 | 1470.1 | 262 | 394.7 | 369.4 | 275.4 | 310.2
1707.1 | 1471.1 | 262.2 | 394.9 | 370.2 | 275.7 | 310.6
1708.1 | 1472.1 | 262.4 | 395.4 | 371.3 | 276 | 311
1709.1 | 1473.1 | 262.7 | 396.1 | 372 | 276.3 | 311.2
1710.1 | 1474.1 | 263 | 396.5 | 372.4 | 276.5 | 311.5
1711.1 | 1475.1 | 263.3 | 396.8 | 372.6 | 276.6 | 311.6
1712.1 | 1476.1 | 263.7 | 397 | 372.5 | 276.9 | 311.8
1713.1 | 1477.1 | 264 | 397.3 | 372.4 | 277.1 | 312
1714.1 | 1478.1 | 264.3 | 397.9 | 372.7 | 277.3 | 312.1
1715.1 | 1479.1 | 264.6 | 398.1 | 372.9 | 277.5 | 312.2
1716.1 | 1480.1 | 264.9 | 398.3 | 373.1 | 277.7 | 312.3
1717.1 | 1481.1 | 265.1 | 398.3 | 373.7 | 278 | 312.6
1718.1 | 1482.1 | 265.4 | 398.5 | 374.2 | 278.2 | 312.9
1719.1 | 1483.1 | 265.7 | 398.5 | 373.9 | 278.4 | 313
1720.1 | 1484.1 | 266 | 398.5 | 373.7 | 278.6 | 313.1
1721.1 | 1485.1 | 266.2 | 398.3 | 373.9 | 278.8 | 313.2
1722.1 | 1486.1 | 266.4 | 398.3 | 374.2 | 279.1 | 313.4
1723.1 | 1487.1 | 266.6 | 398.4 | 374.8 | 279.3 | 313.6
1724.1 | 1488.1 | 266.8 | 398.6 | 375.1 | 279.6 | 314
1725.1 | 1489.1 | 267.1 | 399 | 375.4 | 279.9 | 314.2
1726.1 | 1490.1 | 267.3 | 399.8 | 376.2 | 280.3 | 314.5
1727.1 | 1491.1 | 267.6 | 400.5 | 376.7 | 280.6 | 314.8
1728.1 | 1492.1 | 267.9 | 401.4 | 377.7 | 281 | 315.2
1729.1 | 1493.1 | 268.3 | 401.9 | 378.7 | 281.3 | 315.7
1730.1 | 1494.1 | 268.7 | 402.2 | 379.1 | 281.6 | 316
1731.1 | 1495.1 | 269.1 | 402.4 | 379.3 | 281.9 | 316.2
1732.1 | 1496.1 | 269.6 | 402.7 | 379.4 | 282.3 | 316.4
1733.1 | 1497.1 | 270 | 403.4 | 380.1 | 282.8 | 316.9
1734.1 | 1498.1 | 270.5 | 404 | 381.5 | 283.2 | 317.3
1735.1 | 1499.1 | 271 | 404.4 | 382.3 | 283.6 | 317.7
1736.1 | 1500.1 | 271.5 | 404.6 | 382.4 | 283.9 | 317.9
1737.1 | 1501.1 | 271.9 | 404.7 | 382.5 | 284.2 | 318.1
1738.1 | 1502.1 | 272.3 | 405 | 382.6 | 284.5 | 318.5
1739.1 | 1503.1 | 272.8 | 405.5 | 382.6 | 284.8 | 318.6
1740.1 | 1504.1 | 273.2 | 406.2 | 383.1 | 285.2 | 318.9
1741.1 | 1505.1 | 273.6 | 406.4 | 383.1 | 285.4 | 319.2
1742.1 | 1506.1 | 274 | 406.4 | 382.9 | 285.7 | 319.3
1743.1 | 1507.1 | 274.4 | 406.4 | 383 | 285.9 | 319.5
1744.1 | 1508.1 | 274.7 | 406.2 | 383.1 | 286.1 | 319.7
1745.1 | 1509.1 | 275 | 406.6 | 382.8 | 286.4 | 319.7
1746.1 | 1510.1 | 275.2 | 406.7 | 382.6 | 286.6 | 319.8
1747.1 | 1511.1 | 275.4 | 407.1 | 382 | 286.9 | 319.9
1748.1 | 1512.1 | 275.5 | 407.7 | 381.8 | 287.3 | 320.1
1749.1 | 1513.1 | 275.7 | 408.3 | 382.1 | 287.6 | 320.3
1750.1 | 1514.1 | 275.8 | 408.5 | 382.2 | 287.8 | 320.5
1751.1 | 1515.1 | 275.9 | 408.8 | 382.2 | 288.1 | 320.5
1752.1 | 1516.1 | 275.9 | 409.2 | 382 | 288.4 | 320.7
1753.1 | 1517.1 | 276 | 409.4 | 382.1 | 288.7 | 321
1754.1 | 1518.1 | 276.2 | 409.9 | 382.6 | 289.1 | 321.3
1755.1 | 1519.1 | 276.3 | 410.5 | 383.5 | 289.5 | 321.7
1756.1 | 1520.1 | 276.6 | 411.1 | 384.2 | 289.8 | 322.1
1757.1 | 1521.1 | 276.8 | 411.3 | 385.3 | 290.1 | 322.4
1758.1 | 1522.1 | 277.1 | 411.3 | 385.9 | 290.5 | 322.8
1759.1 | 1523.1 | 277.4 | 411 | 386.2 | 290.7 | 323
1760.1 | 1524.1 | 277.7 | 410.8 | 386.2 | 291 | 323.3
1761.1 | 1525.1 | 277.9 | 410.7 | 385.8 | 291.3 | 323.5
1762.1 | 1526.1 | 278.1 | 410.6 | 386.1 | 291.6 | 323.8
1763.1 | 1527.1 | 278.4 | 410.7 | 385.9 | 292 | 324
1764.1 | 1528.1 | 278.6 | 411.2 | 385.8 | 292.4 | 324.3
1765.1 | 1529.1 | 278.8 | 411.5 | 386.3 | 292.7 | 324.5
1766.1 | 1530.1 | 279.1 | 411.8 | 386.4 | 293 | 324.8
1767.1 | 1531.1 | 279.3 | 412.1 | 386.4 | 293.4 | 325
1768.1 | 1532.1 | 279.6 | 412.5 | 386.8 | 293.9 | 325.3
1769.1 | 1533.1 | 279.9 | 413.2 | 387.1 | 294.4 | 325.7
1770.1 | 1534.1 | 280.2 | 413.9 | 387.5 | 294.8 | 326
1771.1 | 1535.1 | 280.5 | 414.4 | 388.1 | 295.2 | 326.2
1772.1 | 1536.1 | 280.8 | 414.7 | 388.7 | 295.6 | 326.6
1773.1 | 1537.1 | 281.2 | 415.3 | 389 | 296 | 327
1774.1 | 1538.1 | 281.5 | 416.1 | 389.4 | 296.5 | 327.4
1775.1 | 1539.1 | 281.8 | 416.3 | 389.5 | 296.9 | 327.8
1776.1 | 1540.1 | 282.1 | 416.4 | 389.7 | 297.3 | 328.1
1777.1 | 1541.1 | 282.4 | 416.6 | 390.1 | 297.7 | 328.3
1778.1 | 1542.1 | 282.8 | 417.1 | 390.8 | 298.2 | 328.6
1779.1 | 1543.1 | 283.1 | 417.5 | 391.3 | 298.6 | 328.9
1780.1 | 1544.1 | 283.4 | 418.3 | 391.6 | 299.1 | 329.3
1781.1 | 1545.1 | 283.7 | 418.9 | 392.1 | 299.5 | 329.6
1782.1 | 1546.1 | 284 | 419.5 | 393.2 | 300 | 330
1783.1 | 1547.1 | 284.3 | 420.4 | 393.8 | 300.5 | 330.3
1784.1 | 1548.1 | 284.6 | 421.2 | 394.3 | 301 | 330.7
1785.1 | 1549.1 | 284.9 | 422.3 | 395.3 | 301.8 | 331.2
1786.1 | 1550.1 | 285.3 | 423.2 | 396.1 | 302.3 | 331.6
1787.1 | 1551.1 | 285.6 | 423.9 | 397.4 | 302.8 | 332
1788.1 | 1552.1 | 286.1 | 424.6 | 399.5 | 303.4 | 332.7
1789.1 | 1553.1 | 286.7 | 425.2 | 401.1 | 304 | 333.3
1790.1 | 1554.1 | 287.3 | 426 | 402.2 | 304.5 | 333.6
1791.1 | 1555.1 | 287.9 | 426.5 | 403.6 | 305 | 334
1792.1 | 1556.1 | 288.5 | 426.7 | 403.7 | 305.3 | 334.3
1793.1 | 1557.1 | 288.9 | 426.9 | 403.6 | 305.7 | 334.6
1794.1 | 1558.1 | 289.3 | 427.1 | 403.6 | 306.1 | 334.8
1795.1 | 1559.1 | 289.7 | 427.3 | 403.4 | 306.6 | 335.1
1796.1 | 1560.1 | 289.9 | 427.4 | 403.3 | 307.1 | 335.4
1797.1 | 1561.1 | 290.1 | 427.6 | 403.2 | 307.5 | 335.7
1798.1 | 1562.1 | 290.3 | 427.9 | 402.9 | 308 | 336
1799.1 | 1563.1 | 290.5 | 428 | 402.5 | 308.4 | 336.3
1800.1 | 1564.1 | 290.7 | 427.9 | 401.7 | 308.8 | 336.5
1801.1 | 1565.1 | 290.9 | 427.8 | 401.1 | 309.1 | 336.8
1802.1 | 1566.1 | 291.1 | 427.6 | 401.2 | 309.5 | 337.1
1803.1 | 1567.1 | 291.3 | 427.4 | 401.1 | 309.8 | 337.2
1804.1 | 1568.1 | 291.4 | 427.1 | 401.1 | 310.2 | 337.5
1805.1 | 1569.1 | 291.6 | 427.6 | 401.8 | 310.7 | 338
1806.1 | 1570.1 | 291.8 | 428.5 | 402.4 | 311.4 | 338.4
1807.1 | 1571.1 | 292.1 | 429.3 | 403.5 | 311.9 | 338.9
1808.1 | 1572.1 | 292.5 | 429.6 | 404 | 312.3 | 339.3
1809.1 | 1573.1 | 292.8 | 429.9 | 404.3 | 312.8 | 339.5
1810.1 | 1574.1 | 293.2 | 430.1 | 404.4 | 313.2 | 339.7
1811.1 | 1575.1 | 293.5 | 430.9 | 405.2 | 313.9 | 340.1
1812.1 | 1576.1 | 293.9 | 431.8 | 406.1 | 314.7 | 340.5
1813.1 | 1577.1 | 294.3 | 432.9 | 406.9 | 315.4 | 340.9
1814.1 | 1578.1 | 294.7 | 433.4 | 407.3 | 315.9 | 341.1
1815.1 | 1579.1 | 295.1 | 433.8 | 407.8 | 316.5 | 341.4
1816.1 | 1580.1 | 295.5 | 434.8 | 408.7 | 317.2 | 341.9
1817.1 | 1581.1 | 295.9 | 435.5 | 409 | 317.6 | 342.1
1818.1 | 1582.1 | 296.2 | 435.6 | 409 | 317.9 | 342.4
1819.1 | 1583.1 | 296.5 | 435.6 | 408.8 | 318.2 | 342.7
1820.1 | 1584.1 | 296.8 | 435.7 | 408.8 | 318.6 | 343
1821.1 | 1585.1 | 297 | 435.7 | 408.6 | 318.9 | 343.3
1822.1 | 1586.1 | 297.1 | 436.1 | 408.6 | 319.3 | 343.6
1823.1 | 1587.1 | 297.3 | 437 | 408.8 | 320 | 344.1
1824.1 | 1588.1 | 297.6 | 437.6 | 409.1 | 320.6 | 344.4
1825.1 | 1589.1 | 297.8 | 438.4 | 409.5 | 321.3 | 344.8
1826.1 | 1590.1 | 298.2 | 440.1 | 410.5 | 322.2 | 345.4
1827.1 | 1591.1 | 298.7 | 441.1 | 410.5 | 322.7 | 345.7
1828.1 | 1592.1 | 299.1 | 441.1 | 410.9 | 323.2 | 346.1
1829.1 | 1593.1 | 299.5 | 441.5 | 412.1 | 323.8 | 346.6
1830.1 | 1594.1 | 300 | 442.4 | 413 | 324.4 | 346.9
1831.1 | 1595.1 | 300.4 | 443.3 | 413.6 | 325 | 347.3
1832.1 | 1596.1 | 300.9 | 444.4 | 415.1 | 325.7 | 348
1833.1 | 1597.1 | 301.4 | 445.7 | 416.5 | 326.6 | 348.6
1834.1 | 1598.1 | 301.9 | 446.7 | 417.4 | 327.2 | 349
1835.1 | 1599.1 | 302.4 | 447.6 | 418 | 327.8 | 349.4
1836.1 | 1600.1 | 302.9 | 448.6 | 419 | 328.5 | 349.9
1837.1 | 1601.1 | 303.3 | 449.9 | 420.3 | 329.4 | 350.5
1838.1 | 1602.1 | 303.8 | 451.7 | 420.9 | 330.1 | 351
1839.1 | 1603.1 | 304.3 | 452.4 | 420.8 | 330.5 | 351.2
1840.1 | 1604.1 | 304.7 | 452.7 | 421.3 | 331 | 351.6
1841.1 | 1605.1 | 305.1 | 452.9 | 422.1 | 331.6 | 352.1
1842.1 | 1606.1 | 305.6 | 453.4 | 422.7 | 332.3 | 352.7
1843.1 | 1607.1 | 306 | 453.6 | 422.7 | 332.8 | 353
1844.1 | 1608.1 | 306.5 | 453.9 | 422.8 | 333.3 | 353.3
1845.1 | 1609.1 | 306.8 | 453.9 | 422.6 | 333.7 | 353.6
1846.1 | 1610.1 | 307.1 | 453.7 | 422.4 | 334.1 | 353.9
1847.1 | 1611.1 | 307.4 | 453.9 | 422.2 | 334.6 | 354.2
1848.1 | 1612.1 | 307.7 | 453.9 | 421.8 | 335 | 354.4
1849.1 | 1613.1 | 307.9 | 453.7 | 421.7 | 335.5 | 354.7
1850.1 | 1614.1 | 308.1 | 453.2 | 421.3 | 335.7 | 354.9
1851.1 | 1615.1 | 308.2 | 452.5 | 420.8 | 336 | 355.1
1852.1 | 1616.1 | 308.3 | 452.1 | 420.4 | 336.2 | 355.4
1853.1 | 1617.1 | 308.4 | 452.1 | 420.1 | 336.6 | 355.6
1854.1 | 1618.1 | 308.6 | 452.5 | 419.9 | 337.1 | 355.9
1855.1 | 1619.1 | 308.8 | 453.3 | 420.2 | 337.9 | 356.3
1856.1 | 1620.1 | 309.1 | 454.5 | 420.7 | 338.7 | 356.8
1857.1 | 1621.1 | 309.4 | 455 | 421.3 | 339.3 | 357.2
1858.1 | 1622.1 | 309.8 | 455.3 | 421.7 | 339.8 | 357.6
1859.1 | 1623.1 | 310.1 | 455.2 | 421.8 | 340.1 | 357.8
1860.1 | 1624.1 | 310.5 | 455.1 | 422 | 340.5 | 358.1
1861.1 | 1625.1 | 310.8 | 455.5 | 422.4 | 341 | 358.4
1862.1 | 1626.1 | 311 | 455.8 | 422.3 | 341.5 | 358.7
1863.1 | 1627.1 | 311.3 | 456.1 | 422.6 | 342.1 | 359.1
1864.1 | 1628.1 | 311.6 | 456.6 | 422.8 | 342.6 | 359.5
1865.1 | 1629.1 | 311.9 | 457.3 | 423.6 | 343.3 | 360.1
1866.1 | 1630.1 | 312.3 | 458.1 | 424.7 | 344 | 360.5
1867.1 | 1631.1 | 312.7 | 459 | 425.2 | 344.7 | 361
1868.1 | 1632.1 | 313.2 | 460 | 426.1 | 345.5 | 361.4
1869.1 | 1633.1 | 313.8 | 461.1 | 427.4 | 346.3 | 361.8
1870.1 | 1634.1 | 314.4 | 462.2 | 429 | 347 | 362.3
1871.1 | 1635.1 | 315.1 | 463.2 | 429.9 | 347.5 | 362.8
1872.1 | 1636.1 | 315.7 | 463.6 | 429.5 | 347.9 | 363.1
1873.1 | 1637.1 | 316.2 | 463.6 | 429.2 | 348.3 | 363.3
1874.1 | 1638.1 | 316.6 | 463.7 | 429.2 | 348.8 | 363.6
1875.1 | 1639.1 | 316.9 | 463.9 | 429.2 | 349.2 | 363.9
1876.1 | 1640.1 | 317.3 | 463.8 | 429.2 | 349.7 | 364.2
1877.1 | 1641.1 | 317.6 | 464 | 429.1 | 350.2 | 364.5
1878.1 | 1642.1 | 317.9 | 464.1 | 428.7 | 350.6 | 364.8
1879.1 | 1643.1 | 318.2 | 464.2 | 428.9 | 351.1 | 365.2
1880.1 | 1644.1 | 318.5 | 464.9 | 429.6 | 351.8 | 365.8
1881.1 | 1645.1 | 318.8 | 465.6 | 429.7 | 352.3 | 366.1
1882.1 | 1646.1 | 319.2 | 465.9 | 429.7 | 352.7 | 366.4
1883.1 | 1647.1 | 319.5 | 466.5 | 430.3 | 353.3 | 366.8
1884.1 | 1648.1 | 319.9 | 467.5 | 431 | 354.1 | 367.3
1885.1 | 1649.1 | 320.4 | 468.9 | 432.1 | 355 | 367.8
1886.1 | 1650.1 | 320.8 | 469.7 | 432.5 | 355.5 | 368.2
1887.1 | 1651.1 | 321.3 | 471.2 | 433.2 | 356.1 | 368.6
1888.1 | 1652.1 | 321.7 | 472.3 | 434.2 | 356.7 | 369.1
1889.1 | 1653.1 | 322.2 | 473.1 | 434.9 | 357.3 | 369.6
1890.1 | 1654.1 | 322.6 | 474.2 | 435.2 | 357.8 | 370.1
1891.1 | 1655.1 | 323.1 | 474.9 | 435.8 | 358.4 | 370.4
1892.1 | 1656.1 | 323.5 | 475.8 | 435.9 | 358.9 | 370.6
1893.1 | 1657.1 | 323.8 | 476.6 | 435.8 | 359.3 | 370.9
1894.1 | 1658.1 | 324 | 476.5 | 435.6 | 359.6 | 371.2
1895.1 | 1659.1 | 324.1 | 476.7 | 435.5 | 360.1 | 371.6
1896.1 | 1660.1 | 324.4 | 476.7 | 435.2 | 360.5 | 372
1897.1 | 1661.1 | 324.6 | 476.5 | 435 | 360.8 | 372.3
1898.1 | 1662.1 | 324.9 | 476.8 | 434.6 | 361.2 | 372.7
1899.1 | 1663.1 | 325.2 | 476.7 | 434.4 | 361.5 | 372.9
1900.1 | 1664.1 | 325.5 | 476.6 | 434 | 361.9 | 373.1
1901.1 | 1665.1 | 325.8 | 476.2 | 433.7 | 362.2 | 373.3
1902.1 | 1666.1 | 326 | 475.9 | 433.4 | 362.4 | 373.6
1903.1 | 1667.1 | 326.2 | 475.6 | 433.2 | 362.8 | 373.9
1904.1 | 1668.1 | 326.4 | 475.5 | 432.7 | 363.3 | 374
1905.1 | 1669.1 | 326.6 | 475.4 | 432 | 363.6 | 374.2
1906.1 | 1670.1 | 326.7 | 475.4 | 431.4 | 363.9 | 374.4
1907.1 | 1671.1 | 326.8 | 475.5 | 431 | 364.3 | 374.6
1908.1 | 1672.1 | 326.9 | 475.1 | 430.4 | 364.5 | 374.6
1909.1 | 1673.1 | 326.9 | 474.7 | 429.7 | 364.7 | 374.7
1910.1 | 1674.1 | 326.9 | 474.1 | 429.3 | 364.9 | 374.9
1911.1 | 1675.1 | 326.9 | 473.8 | 429.2 | 365.2 | 375.2
1912.1 | 1676.1 | 327 | 473.4 | 429.1 | 365.5 | 375.4
1913.1 | 1677.1 | 327.2 | 472.7 | 428.9 | 365.9 | 375.7
1914.1 | 1678.1 | 327.3 | 472.5 | 429 | 366.1 | 376
1915.1 | 1679.1 | 327.5 | 472.4 | 429 | 366.5 | 376.2
1916.1 | 1680.1 | 327.7 | 471.8 | 428.8 | 366.7 | 376.3
1917.1 | 1681.1 | 327.8 | 471.5 | 428.6 | 367 | 376.6
1918.1 | 1682.1 | 328 | 471.4 | 428.8 | 367.3 | 377
1919.1 | 1683.1 | 328.2 | 471.6 | 428.9 | 367.8 | 377.1
1920.1 | 1684.1 | 328.4 | 471.9 | 429.4 | 368.3 | 377.4
1921.1 | 1685.1 | 328.7 | 472.3 | 429.2 | 368.8 | 377.6
1922.1 | 1686.1 | 329 | 472.9 | 429.3 | 369.2 | 377.8
1923.1 | 1687.1 | 329.3 | 473.1 | 429.6 | 369.5 | 378.3
1924.1 | 1688.1 | 329.5 | 473.2 | 429.8 | 369.9 | 378.5
1925.1 | 1689.1 | 329.9 | 473.7 | 430.6 | 370.4 | 378.9
1926.1 | 1690.1 | 330.2 | 474.8 | 431.2 | 371 | 379.3
1927.1 | 1691.1 | 330.6 | 475.6 | 431.7 | 371.5 | 379.6
1928.1 | 1692.1 | 331.1 | 476.8 | 432.1 | 372.1 | 380
1929.1 | 1693.1 | 331.6 | 478.3 | 432.9 | 372.7 | 380.2
1930.1 | 1694.1 | 331.9 | 479.1 | 433.9 | 373.2 | 380.5
1931.1 | 1695.1 | 332.3 | 479.2 | 434.1 | 373.5 | 380.8
1932.1 | 1696.1 | 332.6 | 478.9 | 433.7 | 373.7 | 380.9
1933.1 | 1697.1 | 332.8 | 478.6 | 433 | 373.9 | 381
1934.1 | 1698.1 | 332.9 | 478.9 | 433.3 | 374.4 | 381.3
1935.1 | 1699.1 | 333.1 | 478.9 | 433.1 | 374.7 | 381.5
1936.1 | 1700.1 | 333.3 | 478.5 | 432.9 | 374.9 | 381.7
1937.1 | 1701.1 | 333.4 | 478.3 | 433.1 | 375.1 | 381.9
1938.1 | 1702.1 | 333.6 | 478.6 | 433.8 | 375.4 | 382.3
1939.1 | 1703.1 | 333.9 | 478 | 433.9 | 375.6 | 382.4
1940.1 | 1704.1 | 334.1 | 477.7 | 433.3 | 375.7 | 382.4
1941.1 | 1705.1 | 334.2 | 477.9 | 433 | 376 | 382.6
1942.1 | 1706.1 | 334.3 | 478.1 | 433.1 | 376.4 | 382.9
1943.1 | 1707.1 | 334.5 | 478.4 | 433.6 | 376.7 | 383.1
1944.1 | 1708.1 | 334.6 | 478.6 | 433.8 | 377 | 383.4
1945.1 | 1709.1 | 334.9 | 478.9 | 433.8 | 377.4 | 383.7
1946.1 | 1710.1 | 335.1 | 479.3 | 433.6 | 377.8 | 384
1947.1 | 1711.1 | 335.4 | 479.8 | 433.3 | 378.1 | 384.2
1948.1 | 1712.1 | 335.6 | 480.1 | 433.4 | 378.4 | 384.3
1949.1 | 1713.1 | 335.9 | 480 | 433.9 | 378.6 | 384.6
1950.1 | 1714.1 | 336.1 | 480.7 | 434.3 | 379 | 384.8
1951.1 | 1715.1 | 336.4 | 481.2 | 434.7 | 379.5 | 385.1
1952.1 | 1716.1 | 336.7 | 481.6 | 435.1 | 379.8 | 385.4
1953.1 | 1717.1 | 337.1 | 482.5 | 435.8 | 380.2 | 385.9
1954.1 | 1718.1 | 337.5 | 483 | 436.6 | 380.7 | 386.3
1955.1 | 1719.1 | 338.1 | 483.6 | 436.8 | 381 | 386.6
1956.1 | 1720.1 | 338.6 | 484.1 | 436.8 | 381.3 | 386.8
1957.1 | 1721.1 | 339.1 | 484.1 | 437 | 381.6 | 387
1958.1 | 1722.1 | 339.4 | 484.2 | 437.5 | 381.9 | 387.3
1959.1 | 1723.1 | 339.8 | 485.1 | 438 | 382.4 | 387.5
1960.1 | 1724.1 | 340 | 485.7 | 438.2 | 382.8 | 387.7
1961.1 | 1725.1 | 340.2 | 485.8 | 438.2 | 383 | 387.9
1962.1 | 1726.1 | 340.3 | 485.7 | 438.7 | 383.4 | 388.3
1963.1 | 1727.1 | 340.5 | 486.4 | 438.8 | 383.9 | 388.6
1964.1 | 1728.1 | 340.8 | 486.7 | 438.7 | 384.3 | 388.8
1965.1 | 1729.1 | 341.1 | 487.3 | 438.9 | 384.8 | 389.2
1966.1 | 1730.1 | 341.3 | 487.6 | 439.2 | 385.3 | 389.5
1967.1 | 1731.1 | 341.6 | 487.6 | 439.4 | 385.7 | 389.7
1968.1 | 1732.1 | 341.9 | 488.2 | 439.5 | 386.1 | 390
1969.1 | 1733.1 | 342.1 | 489.3 | 439.3 | 386.6 | 390.1
1970.1 | 1734.1 | 342.3 | 489.8 | 439.6 | 387 | 390.3
1971.1 | 1735.1 | 342.5 | 490.2 | 439.8 | 387.4 | 390.6
1972.1 | 1736.1 | 342.7 | 490.6 | 440 | 387.9 | 390.8
1973.1 | 1737.1 | 342.9 | 491.2 | 440.5 | 388.4 | 391.2
1974.1 | 1738.1 | 343.1 | 491.2 | 440.9 | 388.6 | 391.4
1975.1 | 1739.1 | 343.4 | 491.4 | 440.8 | 388.9 | 391.5
1976.1 | 1740.1 | 343.5 | 491.8 | 441.1 | 389.2 | 391.7
1977.1 | 1741.1 | 343.6 | 491.4 | 441.1 | 389.4 | 391.8
1978.1 | 1742.1 | 343.7 | 490.7 | 441 | 389.6 | 392
1979.1 | 1743.1 | 343.8 | 490.3 | 440.7 | 389.8 | 392.1
1980.1 | 1744.1 | 343.9 | 490.5 | 440.8 | 390.2 | 392.3
1981.1 | 1745.1 | 344 | 490.8 | 441 | 390.6 | 392.6
1982.1 | 1746.1 | 344.2 | 491 | 440.9 | 391.1 | 392.9
1983.1 | 1747.1 | 344.3 | 491 | 440.6 | 391.4 | 393.1
1984.1 | 1748.1 | 344.4 | 490.4 | 440.3 | 391.5 | 393.2
1985.1 | 1749.1 | 344.5 | 489.5 | 440.1 | 391.7 | 393.4
1986.1 | 1750.1 | 344.5 | 488.8 | 440.3 | 391.9 | 393.6
1987.1 | 1751.1 | 344.6 | 488.7 | 440.2 | 392.3 | 393.7
1988.1 | 1752.1 | 344.7 | 488.6 | 439.9 | 392.6 | 393.8
1989.1 | 1753.1 | 344.7 | 488.2 | 439.5 | 392.8 | 394
1990.1 | 1754.1 | 344.7 | 487.8 | 439.1 | 393.1 | 394.2
1991.1 | 1755.1 | 344.8 | 488.2 | 439.6 | 393.5 | 394.6
1992.1 | 1756.1 | 345 | 489.2 | 440.6 | 394.1 | 395
1993.1 | 1757.1 | 345.5 | 490.7 | 441.7 | 394.9 | 395.6
1994.1 | 1758.1 | 346 | 491.5 | 442.7 | 395.3 | 395.9
1995.1 | 1759.1 | 346.5 | 491.8 | 443.6 | 395.7 | 396.2
1996.1 | 1760.1 | 347 | 493.1 | 445.7 | 396.1 | 396.5
1997.1 | 1761.1 | 347.5 | 493.8 | 446.8 | 396.3 | 396.8
1998.1 | 1762.1 | 347.9 | 493.8 | 446.8 | 396.6 | 397
1999.1 | 1763.1 | 348.1 | 493.3 | 446.3 | 396.8 | 397.3
2000.1 | 1764.1 | 348.3 | 492.6 | 445.9 | 397 | 397.5
2001.1 | 1765.1 | 348.4 | 492.3 | 445.7 | 397.2 | 397.8
2002.1 | 1766.1 | 348.6 | 492.9 | 445.7 | 397.7 | 398.1
2003.1 | 1767.1 | 348.7 | 493.9 | 445.5 | 398.2 | 398.2
2004.1 | 1768.1 | 348.9 | 494.8 | 444.8 | 398.6 | 398.3
2005.1 | 1769.1 | 348.9 | 494.6 | 444.4 | 398.9 | 398.4
2006.1 | 1770.1 | 348.9 | 494 | 444.4 | 399.1 | 398.7
2007.1 | 1771.1 | 348.9 | 493.4 | 444.2 | 399.4 | 398.8
2008.1 | 1772.1 | 348.8 | 493 | 443.8 | 399.6 | 398.9
2009.1 | 1773.1 | 348.8 | 493.1 | 443.9 | 400 | 399.1
2010.1 | 1774.1 | 348.8 | 493.9 | 444.1 | 400.5 | 399.4
2011.1 | 1775.1 | 349 | 494.7 | 444.5 | 400.9 | 399.7
2012.1 | 1776.1 | 349.2 | 495.2 | 444.6 | 401.3 | 399.9
2013.1 | 1777.1 | 349.4 | 495.8 | 444.6 | 401.7 | 400
2014.1 | 1778.1 | 349.6 | 495.8 | 444.3 | 402 | 400.2
2015.1 | 1779.1 | 349.8 | 495 | 444.4 | 402.3 | 400.4
2016.1 | 1780.1 | 349.9 | 494.5 | 444.1 | 402.6 | 400.4
2017.1 | 1781.1 | 349.8 | 494.7 | 443.7 | 402.9 | 400.3
2018.1 | 1782.1 | 349.8 | 495 | 443.6 | 403.2 | 400.5
2019.1 | 1783.1 | 349.8 | 495.2 | 443.7 | 403.6 | 400.7
2020.1 | 1784.1 | 349.8 | 495.2 | 443.6 | 404 | 400.8
2021.1 | 1785.1 | 349.9 | 495.5 | 443.3 | 404.4 | 400.9
2022.1 | 1786.1 | 349.9 | 495.5 | 443.1 | 404.7 | 401
2023.1 | 1787.1 | 350 | 495.6 | 443.8 | 405.1 | 401.3
2024.1 | 1788.1 | 350.2 | 496.2 | 444.3 | 405.6 | 401.5
2025.1 | 1789.1 | 350.5 | 498 | 444.8 | 406.1 | 401.7
2026.1 | 1790.1 | 350.8 | 498.7 | 444.8 | 406.5 | 401.9
2027.1 | 1791.1 | 351.1 | 499 | 444.7 | 406.8 | 402
2028.1 | 1792.1 | 351.3 | 498.9 | 444.7 | 407.1 | 402.1
2029.1 | 1793.1 | 351.4 | 498.2 | 444.5 | 407.3 | 402.2
2030.1 | 1794.1 | 351.5 | 497.7 | 444.3 | 407.5 | 402.3
2031.1 | 1795.1 | 351.6 | 497.3 | 444.3 | 407.7 | 402.5
2032.1 | 1796.1 | 351.8 | 497.9 | 444.4 | 408 | 402.6
2033.1 | 1797.1 | 352 | 497.4 | 444.6 | 408.4 | 402.8
2034.1 | 1798.1 | 352.1 | 497.2 | 444.6 | 408.6 | 403
2035.1 | 1799.1 | 352.2 | 497.2 | 444.5 | 408.9 | 403.1
2036.1 | 1800.1 | 352.3 | 497.1 | 444.5 | 409.2 | 403.2
2037.1 | 1801.1 | 352.4 | 497.1 | 444.8 | 409.5 | 403.4
2038.1 | 1802.1 | 352.5 | 497.6 | 445.1 | 409.8 | 403.6
2039.1 | 1803.1 | 352.7 | 497.9 | 445.6 | 410.2 | 403.8
2040.1 | 1804.1 | 352.9 | 498 | 445.8 | 410.6 | 404
2041.1 | 1805.1 | 353.1 | 498.4 | 446.1 | 411 | 404.3
2042.1 | 1806.1 | 353.3 | 499.2 | 446.6 | 411.5 | 404.6
2043.1 | 1807.1 | 353.6 | 500 | 447.1 | 411.9 | 404.8
2044.1 | 1808.1 | 353.9 | 500.3 | 447.7 | 412.4 | 405
2045.1 | 1809.1 | 354.2 | 500.8 | 448.3 | 412.8 | 405.3
2046.1 | 1810.1 | 354.5 | 501.4 | 448.4 | 413.2 | 405.5
2047.1 | 1811.1 | 354.8 | 501.3 | 448.5 | 413.4 | 405.7
2048.1 | 1812.1 | 355 | 501.3 | 448.1 | 413.7 | 405.7
2049.1 | 1813.1 | 355.1 | 501.2 | 447.5 | 413.9 | 405.7
2050.1 | 1814.1 | 355.1 | 500.9 | 447.4 | 414.2 | 405.8
2051.1 | 1815.1 | 355.1 | 500.6 | 447 | 414.5 | 405.9
2052.1 | 1816.1 | 355.1 | 500.3 | 446.5 | 414.8 | 406
2053.1 | 1817.1 | 355.1 | 500 | 446.1 | 415.1 | 406
2054.1 | 1818.1 | 355.1 | 499.8 | 446 | 415.4 | 406.2
2055.1 | 1819.1 | 355.1 | 499.4 | 445.5 | 415.7 | 406.1
2056.1 | 1820.1 | 355.1 | 499.6 | 445.1 | 416 | 406.1
2057.1 | 1821.1 | 355 | 499.4 | 445.2 | 416.2 | 406.3
2058.1 | 1822.1 | 355.1 | 499.8 | 445.3 | 416.5 | 406.6
2059.1 | 1823.1 | 355.2 | 500.2 | 445.3 | 416.9 | 406.7
2060.1 | 1824.1 | 355.2 | 500 | 445.1 | 417.2 | 406.8
2061.1 | 1825.1 | 355.3 | 499.7 | 445.3 | 417.4 | 407
2062.1 | 1826.1 | 355.5 | 499.4 | 445.5 | 417.7 | 407.2
2063.1 | 1827.1 | 355.7 | 499.5 | 446.8 | 418.1 | 407.4
2064.1 | 1828.1 | 356 | 500 | 447.3 | 418.4 | 407.6
2065.1 | 1829.1 | 356.3 | 500.1 | 447.6 | 418.8 | 407.8
2066.1 | 1830.1 | 356.7 | 500.1 | 448 | 419.1 | 408.1
2067.1 | 1831.1 | 357 | 499.9 | 447.9 | 419.4 | 408.2
2068.1 | 1832.1 | 357.3 | 500 | 447.7 | 419.6 | 408.3
2069.1 | 1833.1 | 357.5 | 500.4 | 447.6 | 419.8 | 408.3
2070.1 | 1834.1 | 357.6 | 500.7 | 448.4 | 420.1 | 408.5
2071.1 | 1835.1 | 357.8 | 500.3 | 449.1 | 420.4 | 408.7
2072.1 | 1836.1 | 358 | 500.1 | 449.8 | 420.6 | 408.9
2073.1 | 1837.1 | 358.2 | 500.4 | 449.9 | 421 | 409.2
2074.1 | 1838.1 | 358.5 | 500.4 | 450.1 | 421.3 | 409.4
2075.1 | 1839.1 | 358.8 | 500.1 | 450.5 | 421.7 | 409.7
2076.1 | 1840.1 | 359.1 | 500.3 | 450.7 | 422.1 | 409.8
2077.1 | 1841.1 | 359.3 | 501.1 | 451.1 | 422.6 | 410.1
2078.1 | 1842.1 | 359.6 | 501.9 | 451.4 | 422.9 | 410.3
2079.1 | 1843.1 | 359.8 | 502.7 | 451.6 | 423.3 | 410.5
2080.1 | 1844.1 | 360 | 502.7 | 452 | 423.5 | 410.7
2081.1 | 1845.1 | 360.2 | 502.1 | 452.6 | 423.7 | 411.1
2082.1 | 1846.1 | 360.5 | 502.7 | 453.4 | 424.1 | 411.5
2083.1 | 1847.1 | 360.9 | 503.1 | 454 | 424.5 | 411.7
2084.1 | 1848.1 | 361.3 | 503.9 | 454.6 | 424.9 | 412.1
2085.1 | 1849.1 | 361.7 | 504.7 | 455.2 | 425.4 | 412.3
2086.1 | 1850.1 | 362 | 504.7 | 455.7 | 425.7 | 412.5
2087.1 | 1851.1 | 362.3 | 504.5 | 456.6 | 426.2 | 412.8
2088.1 | 1852.1 | 362.6 | 504.5 | 457.4 | 426.6 | 413
2089.1 | 1853.1 | 362.9 | 504.7 | 457.7 | 427 | 413.2
2090.1 | 1854.1 | 363.2 | 504.7 | 458.2 | 427.4 | 413.4
2091.1 | 1855.1 | 363.4 | 504.4 | 458.7 | 427.7 | 413.8
2092.1 | 1856.1 | 363.7 | 504.9 | 459.3 | 428.2 | 414.1
2093.1 | 1857.1 | 364 | 506 | 459.7 | 428.8 | 414.4
2094.1 | 1858.1 | 364.3 | 506.7 | 460 | 429.2 | 414.6
2095.1 | 1859.1 | 364.6 | 506.8 | 460.2 | 429.6 | 414.8
2096.1 | 1860.1 | 364.9 | 506.3 | 459.8 | 429.8 | 414.9
2097.1 | 1861.1 | 365.1 | 506.3 | 459.6 | 430.1 | 414.9
2098.1 | 1862.1 | 365.2 | 506.4 | 459.5 | 430.4 | 415.1
2099.1 | 1863.1 | 365.4 | 506.9 | 459.5 | 430.9 | 415.2
2100.1 | 1864.1 | 365.6 | 507.1 | 459.1 | 431.3 | 415.2
2101.1 | 1865.1 | 365.6 | 506.4 | 458.8 | 431.6 | 415.3
2102.1 | 1866.1 | 365.7 | 506 | 458.6 | 432 | 415.4
2103.1 | 1867.1 | 365.8 | 506 | 458.8 | 432.3 | 415.6
2104.1 | 1868.1 | 366 | 506.6 | 459.8 | 433 | 416.1
2105.1 | 1869.1 | 366.3 | 508.2 | 460.5 | 433.6 | 416.4
2106.1 | 1870.1 | 366.7 | 508.5 | 460.6 | 434 | 416.6
2107.1 | 1871.1 | 367 | 510.1 | 460.9 | 434.6 | 417
2108.1 | 1872.1 | 367.4 | 511.3 | 461.4 | 435.2 | 417.3
2109.1 | 1873.1 | 367.9 | 512.7 | 461.8 | 435.9 | 417.6
2110.1 | 1874.1 | 368.3 | 513.6 | 464 | 436.4 | 418.1
2111.1 | 1875.1 | 368.7 | 514.1 | 465.8 | 436.9 | 418.9
2112.1 | 1876.1 | 369.2 | 514.7 | 468 | 437.6 | 419.8
2113.1 | 1877.1 | 369.8 | 516.3 | 469.3 | 438.2 | 420.1
2114.1 | 1878.1 | 370.4 | 516.7 | 469.5 | 438.6 | 420.3
2115.1 | 1879.1 | 370.9 | 516.3 | 469.1 | 438.9 | 420.4
2116.1 | 1880.1 | 371.3 | 515.8 | 468.5 | 439.3 | 420.5
2117.1 | 1881.1 | 371.5 | 516.5 | 468.1 | 439.9 | 420.6
2118.1 | 1882.1 | 371.7 | 517.3 | 468 | 440.5 | 420.8
2119.1 | 1883.1 | 371.9 | 517.4 | 468.9 | 441 | 421.2
2120.1 | 1884.1 | 372.3 | 517.9 | 471.4 | 441.6 | 421.9
2121.1 | 1885.1 | 372.6 | 517.7 | 471.6 | 441.9 | 422.2
2122.1 | 1886.1 | 373 | 516.9 | 471.1 | 442.2 | 422.2
2123.1 | 1887.1 | 373.2 | 515.7 | 470.5 | 442.3 | 422.3
2124.1 | 1888.1 | 373.4 | 514.4 | 470.1 | 442.4 | 422.4
2125.1 | 1889.1 | 373.5 | 513.8 | 469.8 | 442.6 | 422.5
2126.1 | 1890.1 | 373.6 | 513.4 | 469.9 | 442.8 | 422.6
2127.1 | 1891.1 | 373.6 | 513.7 | 469.6 | 443.2 | 422.7
2128.1 | 1892.1 | 373.7 | 513 | 469.4 | 443.5 | 422.9
2129.1 | 1893.1 | 373.8 | 512.8 | 469.5 | 443.8 | 423.1
2130.1 | 1894.1 | 373.9 | 513.2 | 469.3 | 444.2 | 423.3
2131.1 | 1895.1 | 374.1 | 513.5 | 469.1 | 444.6 | 423.5
2132.1 | 1896.1 | 374.2 | 513.6 | 469.5 | 445 | 423.7
2133.1 | 1897.1 | 374.3 | 514 | 470.2 | 445.5 | 423.9
2134.1 | 1898.1 | 374.5 | 514.4 | 470.9 | 445.9 | 424.2
2135.1 | 1899.1 | 374.8 | 514.8 | 471.3 | 446.3 | 424.5
2136.1 | 1900.1 | 375.2 | 514.5 | 471.3 | 446.4 | 424.8
2137.1 | 1901.1 | 375.5 | 513.7 | 471 | 446.5 | 424.9
2138.1 | 1902.1 | 375.8 | 513.2 | 471 | 446.8 | 425.1
2139.1 | 1903.1 | 376.1 | 513.4 | 471.1 | 447.4 | 425.4
2140.1 | 1904.1 | 376.4 | 514.5 | 471.1 | 448.1 | 425.6
2141.1 | 1905.1 | 376.8 | 515.3 | 470.8 | 448.5 | 425.7
2142.1 | 1906.1 | 377.1 | 515.4 | 470.8 | 448.7 | 425.9
2143.1 | 1907.1 | 377.4 | 515.2 | 471.2 | 448.6 | 426
2144.1 | 1908.1 | 377.7 | 515.3 | 472.2 | 448.6 | 426.4
2145.1 | 1909.1 | 378 | 515.2 | 472.9 | 448.6 | 426.8
2146.1 | 1910.1 | 378.3 | 515.1 | 473.1 | 448.6 | 427.2
2147.1 | 1911.1 | 378.5 | 514.9 | 472.9 | 448.7 | 427.3
2148.1 | 1912.1 | 378.8 | 514.9 | 472.7 | 448.7 | 427.5
2149.1 | 1913.1 | 379 | 516.4 | 472.4 | 448.7 | 427.5
2150.1 | 1914.1 | 379.1 | 516.1 | 472.1 | 448.6 | 427.5
2151.1 | 1915.1 | 379.2 | 515.7 | 471.6 | 448.6 | 427.6
2152.1 | 1916.1 | 379.1 | 515.4 | 470.9 | 448.6 | 427.6
2153.1 | 1917.1 | 379.1 | 514.8 | 470.2 | 448.6 | 427.7
2154.1 | 1918.1 | 379.1 | 514 | 469.7 | 448.5 | 428
2155.1 | 1919.1 | 379.2 | 513.4 | 469.8 | 448.3 | 428.2
2156.1 | 1920.1 | 379.3 | 513.9 | 469.7 | 448.3 | 428.3
2157.1 | 1921.1 | 379.5 | 514.2 | 470 | 448.4 | 428.5
2158.1 | 1922.1 | 379.7 | 514.4 | 470.8 | 448.3 | 428.8
2159.1 | 1923.1 | 380 | 515.3 | 471.4 | 448.4 | 429
2160.1 | 1924.1 | 380.3 | 515.6 | 471.3 | 448.2 | 429.1
2161.1 | 1925.1 | 380.5 | 515.5 | 471.1 | 448 | 429.1
2162.1 | 1926.1 | 380.8 | 515.3 | 471.4 | 447.9 | 429.4
2163.1 | 1927.1 | 381.2 | 515.9 | 472.2 | 448.3 | 429.7
2164.1 | 1928.1 | 381.6 | 517.9 | 473.3 | 448.8 | 430
2165.1 | 1929.1 | 382.1 | 520.3 | 474.3 | 449.5 | 430.3
2166.1 | 1930.1 | 382.5 | 521.5 | 474.7 | 450 | 430.7
2167.1 | 1931.1 | 383 | 522.4 | 475 | 450.4 | 431
2168.1 | 1932.1 | 383.4 | 522.2 | 474.5 | 450.6 | 431
2169.1 | 1933.1 | 383.7 | 521.3 | 473.9 | 450.6 | 431.1
2170.1 | 1934.1 | 383.8 | 520.2 | 473.7 | 450.7 | 431.2
2171.1 | 1935.1 | 384.1 | 519.9 | 473.6 | 451 | 431.5
2172.1 | 1936.1 | 384.3 | 520.3 | 473.7 | 451.5 | 431.7
2173.1 | 1937.1 | 384.4 | 519.8 | 473.6 | 451.8 | 431.8
2174.1 | 1938.1 | 384.5 | 519 | 473.1 | 451.9 | 431.9
2175.1 | 1939.1 | 384.7 | 518.2 | 472.6 | 452.2 | 432
2176.1 | 1940.1 | 384.9 | 517.5 | 472.2 | 452.5 | 432
2177.1 | 1941.1 | 385 | 517 | 471.9 | 452.9 | 432.1
2178.1 | 1942.1 | 385.2 | 516.5 | 472.3 | 453.4 | 432.2
2179.1 | 1943.1 | 385.5 | 516.4 | 474.3 | 453.9 | 433.1
2180.1 | 1944.1 | 386 | 516.5 | 475.4 | 454.4 | 433.6
2181.1 | 1945.1 | 386.6 | 516.9 | 475.9 | 455.1 | 433.8
2182.1 | 1946.1 | 387.1 | 519.1 | 476.9 | 456.2 | 434.1
2183.1 | 1947.1 | 387.7 | 522.2 | 478 | 458.1 | 434.4
2184.1 | 1948.1 | 388.3 | 524.3 | 479.2 | 459.5 | 434.6
2185.1 | 1949.1 | 388.8 | 524.5 | 480.4 | 460.2 | 434.8
2186.1 | 1950.1 | 389.3 | 525.1 | 480.6 | 460.6 | 435
2187.1 | 1951.1 | 389.8 | 525.1 | 480.5 | 461.2 | 435.2
2188.1 | 1952.1 | 390.2 | 525.3 | 480.2 | 462 | 435.3
2189.1 | 1953.1 | 390.5 | 526 | 479.7 | 462.6 | 435.4
2190.1 | 1954.1 | 390.6 | 525.7 | 479.6 | 463.3 | 435.5
2191.1 | 1955.1 | 390.9 | 526.1 | 479.6 | 464.1 | 435.6
2192.1 | 1956.1 | 391 | 526.7 | 479.4 | 464.8 | 435.7
2193.1 | 1957.1 | 391 | 526 | 478.3 | 465.1 | 435.6
2194.1 | 1958.1 | 391.1 | 524.8 | 477.5 | 465.5 | 435.8
2195.1 | 1959.1 | 391.2 | 524.9 | 477.3 | 466.5 | 436
2196.1 | 1960.1 | 391.3 | 525.5 | 476.8 | 467.2 | 436.2
2197.1 | 1961.1 | 391.4 | 526.1 | 476.7 | 467.7 | 436.3
2198.1 | 1962.1 | 391.6 | 526 | 476.7 | 468.4 | 436.6
2199.1 | 1963.1 | 391.8 | 526.5 | 476.7 | 469.3 | 436.8
2200.1 | 1964.1 | 392.1 | 529.4 | 476.6 | 470.2 | 436.8
2201.1 | 1965.1 | 392.2 | 530.3 | 476.4 | 470.7 | 436.8
2202.1 | 1966.1 | 392.4 | 529.3 | 476.4 | 470.9 | 436.9
2203.1 | 1967.1 | 392.5 | 528.9 | 476.8 | 471.3 | 437
2204.1 | 1968.1 | 392.7 | 530.5 | 477.3 | 472 | 437.2
2205.1 | 1969.1 | 393.1 | 533.6 | 478.4 | 473 | 437.4
2206.1 | 1970.1 | 393.5 | 534 | 479.3 | 473.7 | 437.7
2207.1 | 1971.1 | 394 | 533.3 | 479.7 | 474 | 437.9
2208.1 | 1972.1 | 394.3 | 532.6 | 480.2 | 474.1 | 438
2209.1 | 1973.1 | 394.7 | 533.1 | 481.5 | 474.9 | 438.4
2210.1 | 1974.1 | 395.2 | 534.9 | 483.7 | 475.9 | 438.8
2211.1 | 1975.1 | 395.9 | 535 | 484.5 | 476.3 | 439
2212.1 | 1976.1 | 396.4 | 534.8 | 485.1 | 476.4 | 439.2
2213.1 | 1977.1 | 396.8 | 535 | 486.2 | 476.4 | 439.5
2214.1 | 1978.1 | 397.3 | 535.4 | 485.9 | 476.4 | 439.7
2215.1 | 1979.1 | 397.7 | 534.6 | 485.6 | 476.3 | 439.7
2216.1 | 1980.1 | 398 | 534 | 485.8 | 476.5 | 439.8
2217.1 | 1981.1 | 398.2 | 534.2 | 486.3 | 476.6 | 440.3
2218.1 | 1982.1 | 398.6 | 534.7 | 487 | 476.9 | 440.9
2219.1 | 1983.1 | 399 | 536.5 | 487.1 | 477 | 441
2220.1 | 1984.1 | 399.3 | 535.5 | 488 | 477 | 441.3
2221.1 | 1985.1 | 399.6 | 535.6 | 488.7 | 477.1 | 441.9
2222.1 | 1986.1 | 400 | 536.9 | 489.6 | 477.4 | 442
2223.1 | 1987.1 | 400.5 | 536.5 | 489.5 | 477.2 | 442.2
2224.1 | 1988.1 | 400.9 | 535.8 | 489.8 | 477.2 | 442.4
2225.1 | 1989.1 | 401.3 | 535.1 | 490.5 | 477.3 | 442.8
2226.1 | 1990.1 | 401.7 | 535.2 | 490.6 | 477.3 | 442.9
2227.1 | 1991.1 | 402 | 535.7 | 490.7 | 477.4 | 443.2
2228.1 | 1992.1 | 402.3 | 535.6 | 490.5 | 477.7 | 443.5
2229.1 | 1993.1 | 402.5 | 536.8 | 489.6 | 478.2 | 443.6
2230.1 | 1994.1 | 402.6 | 537.8 | 488.7 | 478.5 | 443.6
2231.1 | 1995.1 | 402.6 | 537 | 489.3 | 478.6 | 443.8
2232.1 | 1996.1 | 402.7 | 538.5 | 489.6 | 478.7 | 444.1
2233.1 | 1997.1 | 402.9 | 539.8 | 489.3 | 479 | 444.3
2234.1 | 1998.1 | 403 | 539.5 | 489 | 479 | 444.3
2235.1 | 1999.1 | 403.2 | 540.2 | 490.3 | 479.6 | 444.8
2236.1 | 2000.1 | 403.6 | 542.8 | 491.7 | 480.5 | 445.4
2237.1 | 2001.1 | 404.4 | 542.7 | 491.1 | 480.4 | 445.5
2238.1 | 2002.1 | 405.1 | 540.5 | 494.3 | 480 | 446.4
2239.1 | 2003.1 | 405.5 | 539.1 | 499.5 | 479.7 | 447.6
2240.1 | 2004.1 | 405.9 | 538.9 | 502.4 | 479.8 | 448.2
2241.1 | 2005.1 | 406.3 | 538.8 | 503.9 | 479.8 | 448.8
2242.1 | 2006.1 | 406.8 | 538.9 | 503.9 | 479.9 | 448.9
2243.1 | 2007.1 | 407.2 | 538.8 | 502.9 | 480.2 | 448.9
2244.1 | 2008.1 | 407.6 | 537.5 | 500.7 | 480 | 448.9
2245.1 | 2009.1 | 407.8 | 535.8 | 498.8 | 479.9 | 448.8
2246.1 | 2010.1 | 407.8 | 534.3 | 496.9 | 479.7 | 448.8
2247.1 | 2011.1 | 407.8 | 533.5 | 495.8 | 479.8 | 448.9
2248.1 | 2012.1 | 407.9 | 533.6 | 496.2 | 480.1 | 449.1
2249.1 | 2013.1 | 408.1 | 534.6 | 497.2 | 480.3 | 449.2
2250.1 | 2014.1 | 408.5 | 534.9 | 499.2 | 480.6 | 450.1
2251.1 | 2015.1 | 409 | 535.1 | 499.5 | 480.7 | 450.6
2252.1 | 2016.1 | 409.4 | 533.7 | 498.6 | 480.5 | 450.7
2253.1 | 2017.1 | 409.7 | 533.3 | 498.2 | 480.8 | 450.8
2254.1 | 2018.1 | 409.9 | 534 | 496.8 | 480.9 | 450.7
2255.1 | 2019.1 | 410.1 | 533.7 | 495.2 | 481 | 450.7
2256.1 | 2020.1 | 410.3 | 533.9 | 496.4 | 481.4 | 450.9
2257.1 | 2021.1 | 410.7 | 537 | 499.4 | 482.6 | 451.7
2258.1 | 2022.1 | 411.6 | 544.1 | 501.1 | 484.6 | 452.6
2259.1 | 2023.1 | 412.4 | 545.3 | 501.1 | 484.8 | 452.8
2260.1 | 2024.1 | 413 | 544 | 501 | 484.7 | 453
2261.1 | 2025.1 | 413.3 | 546.2 | 502 | 485.8 | 453.3
2262.1 | 2026.1 | 413.6 | 556 | 502.4 | 487.3 | 453.6
2263.1 | 2027.1 | 413.8 | 559.6 | 501.7 | 487.9 | 453.8
2264.1 | 2028.1 | 413.8 | 560.8 | 500.2 | 488 | 453.7
2265.1 | 2029.1 | 413.9 | 558.7 | 498.4 | 487.7 | 453.6
2266.1 | 2030.1 | 413.9 | 556.2 | 496.7 | 487.4 | 453.6
2267.1 | 2031.1 | 413.7 | 553.6 | 495.4 | 487.4 | 453.7
2268.1 | 2032.1 | 413.5 | 553.5 | 494.4 | 487.7 | 453.8
2269.1 | 2033.1 | 413.5 | 554.3 | 493.3 | 488 | 453.8
2270.1 | 2034.1 | 413.5 | 554 | 492.5 | 487.8 | 453.8
2271.1 | 2035.1 | 413.5 | 552.5 | 492.4 | 487.4 | 453.9
2272.1 | 2036.1 | 413.6 | 550.5 | 491.9 | 487.1 | 454
2273.1 | 2037.1 | 413.5 | 548.4 | 490.9 | 486.8 | 453.9
2274.1 | 2038.1 | 413.4 | 546.6 | 490 | 486.6 | 453.9
2275.1 | 2039.1 | 413.5 | 547 | 490.3 | 486.8 | 454
2276.1 | 2040.1 | 413.5 | 548.2 | 491.5 | 486.9 | 454.2
2277.1 | 2041.1 | 413.5 | 547 | 491.6 | 487 | 454.2
2278.1 | 2042.1 | 413.6 | 546 | 490.4 | 486.8 | 454.1
2279.1 | 2043.1 | 413.6 | 545.2 | 489.8 | 486.5 | 454
2280.1 | 2044.1 | 413.6 | 544.6 | 490 | 486.4 | 454.1
2281.1 | 2045.1 | 413.5 | 545.3 | 489.5 | 486.2 | 454.1
2282.1 | 2046.1 | 413.4 | 544.5 | 488.7 | 485.8 | 453.9
2283.1 | 2047.1 | 413.1 | 543 | 486.8 | 485.4 | 453.5
2284.1 | 2048.1 | 412.8 | 540.5 | 483.8 | 484.5 | 453
2285.1 | 2049.1 | 412.5 | 538.6 | 480.8 | 483.8 | 452.4
2286.1 | 2050.1 | 412 | 537.9 | 477.6 | 483.5 | 451.8
2287.1 | 2051.1 | 411.5 | 537.4 | 474.1 | 483.1 | 451.2
2288.1 | 2052.1 | 410.9 | 536.6 | 470.7 | 482.8 | 450.6
2289.1 | 2053.1 | 410.3 | 536.5 | 467.8 | 482.5 | 450
2290.1 | 2054.1 | 409.5 | 535.3 | 465 | 482 | 449.4
2291.1 | 2055.1 | 408.7 | 533 | 462.8 | 481.6 | 448.9
2292.1 | 2056.1 | 407.9 | 530.8 | 460 | 481.2 | 448.4
2293.1 | 2057.1 | 407.3 | 529.4 | 457.8 | 481 | 447.8
2294.1 | 2058.1 | 406.5 | 528 | 455.7 | 480.5 | 447.3
2295.1 | 2059.1 | 405.7 | 526 | 453.4 | 480 | 446.8
2296.1 | 2060.1 | 405 | 523.8 | 451.3 | 479.5 | 446.2
2297.1 | 2061.1 | 404.3 | 522.4 | 449.4 | 479.1 | 445.7
2298.1 | 2062.1 | 403.6 | 521 | 447.5 | 478.8 | 445.2
2299.1 | 2063.1 | 403 | 520.6 | 445.7 | 478.6 | 444.7
2300.1 | 2064.1 | 402.3 | 520.8 | 444.2 | 478.3 | 444.2
2301.1 | 2065.1 | 401.7 | 520.6 | 442.7 | 478 | 443.7
2302.1 | 2066.1 | 401.1 | 520.3 | 440.9 | 477.8 | 443.3
2303.1 | 2067.1 | 400.5 | 519.7 | 439.5 | 477.7 | 442.7
2304.1 | 2068.1 | 400 | 518.5 | 438.4 | 478.1 | 442.2
2305.1 | 2069.1 | 399.5 | 517.7 | 437.3 | 478.1 | 441.8
2306.1 | 2070.1 | 399 | 517.2 | 436.1 | 477.8 | 441.2
2307.1 | 2071.1 | 398.5 | 516.7 | 434.9 | 477.1 | 440.7
2308.1 | 2072.1 | 398 | 516.9 | 433.6 | 476.8 | 440.2
2309.1 | 2073.1 | 397.5 | 516.2 | 432.5 | 476.6 | 439.7
2310.1 | 2074.1 | 397 | 515.4 | 431.6 | 476 | 439.3
2311.1 | 2075.1 | 396.5 | 515.1 | 430.8 | 475.5 | 438.9
2312.1 | 2076.1 | 396 | 514.2 | 430.3 | 475 | 438.4
2313.1 | 2077.1 | 395.5 | 513.3 | 429.7 | 474.6 | 438
2314.1 | 2078.1 | 395.1 | 512.4 | 428.9 | 473.8 | 437.6
2315.1 | 2079.1 | 394.6 | 511.9 | 428.1 | 473.4 | 437.2
2316.1 | 2080.1 | 394.2 | 511 | 427.8 | 472.7 | 436.7
2317.1 | 2081.1 | 393.8 | 509.8 | 427.5 | 472.1 | 436.3
2318.1 | 2082.1 | 393.4 | 508.2 | 427.1 | 471.6 | 435.9
2319.1 | 2083.1 | 393 | 506.7 | 426.8 | 471.2 | 435.4
2320.1 | 2084.1 | 392.6 | 505.4 | 426.4 | 471 | 435
2321.1 | 2085.1 | 392.2 | 504.4 | 425.9 | 470.9 | 434.5
2322.1 | 2086.1 | 391.8 | 503.4 | 425.5 | 470.7 | 434.1
2323.1 | 2087.1 | 391.4 | 502.4 | 425 | 470.4 | 433.7
2324.1 | 2088.1 | 391.1 | 501.3 | 424.4 | 470.4 | 433.3
2325.1 | 2089.1 | 390.8 | 500.2 | 423.7 | 470 | 432.9
2326.1 | 2090.1 | 390.4 | 499.1 | 423 | 469.7 | 432.4
2327.1 | 2091.1 | 390.1 | 497.8 | 422.5 | 469.5 | 432
2328.1 | 2092.1 | 389.8 | 496.5 | 422 | 469.3 | 431.6
2329.1 | 2093.1 | 389.5 | 495.7 | 421.6 | 469.3 | 431.2
2330.1 | 2094.1 | 389.2 | 494.8 | 421.2 | 469 | 430.8
2331.1 | 2095.1 | 388.9 | 493.7 | 421.1 | 468.7 | 430.4
2332.1 | 2096.1 | 388.6 | 492.8 | 421 | 468.3 | 430
2333.1 | 2097.1 | 388.3 | 491.5 | 420.8 | 467.6 | 429.6
2334.1 | 2098.1 | 388 | 490.1 | 420.3 | 466.7 | 429.3
2335.1 | 2099.1 | 387.8 | 488.3 | 419.7 | 466.1 | 429
2336.1 | 2100.1 | 387.5 | 486.9 | 419.4 | 465.4 | 428.6
2337.1 | 2101.1 | 387.1 | 485.3 | 418.8 | 464.8 | 428.2
2338.1 | 2102.1 | 386.8 | 483.7 | 417.9 | 464.2 | 427.7
2339.1 | 2103.1 | 386.5 | 482.3 | 416.9 | 463.8 | 427.2
2340.1 | 2104.1 | 386.2 | 481.4 | 416 | 463.5 | 426.8
2341.1 | 2105.1 | 385.8 | 480.4 | 415.2 | 463 | 426.3
2342.1 | 2106.1 | 385.5 | 479.3 | 414.3 | 462.7 | 425.9
2343.1 | 2107.1 | 385.2 | 478 | 413.3 | 462.3 | 425.4
2344.1 | 2108.1 | 384.8 | 476.9 | 412.6 | 462.1 | 425.1
2345.1 | 2109.1 | 384.5 | 475.6 | 411.7 | 461.8 | 424.7
2346.1 | 2110.1 | 384.1 | 474.7 | 410.9 | 461.5 | 424.3
2347.1 | 2111.1 | 383.8 | 473.3 | 410.2 | 461.2 | 423.9
2348.1 | 2112.1 | 383.4 | 471.9 | 409.5 | 460.9 | 423.5
2349.1 | 2113.1 | 383.1 | 470.7 | 408.9 | 460.6 | 423.1
2350.1 | 2114.1 | 382.8 | 469.8 | 408.4 | 460.4 | 422.7
2351.1 | 2115.1 | 382.5 | 468.7 | 407.6 | 460.1 | 422.3
2352.1 | 2116.1 | 382.3 | 467.5 | 406.5 | 459.8 | 421.9
2353.1 | 2117.1 | 382 | 466.1 | 405.4 | 459.4 | 421.5
2354.1 | 2118.1 | 381.7 | 464.8 | 404.5 | 459 | 421.1
2355.1 | 2119.1 | 381.5 | 464.3 | 404 | 458.5 | 420.7
2356.1 | 2120.1 | 381.2 | 463.6 | 403.4 | 458 | 420.4
2357.1 | 2121.1 | 381 | 462.6 | 402.8 | 457.5 | 420
2358.1 | 2122.1 | 380.8 | 462.2 | 402.1 | 457.1 | 419.5
2359.1 | 2123.1 | 380.6 | 462 | 401.5 | 456.7 | 419.1
2360.1 | 2124.1 | 380.3 | 461.5 | 401.3 | 456.2 | 418.8
2361.1 | 2125.1 | 380.1 | 461 | 400.8 | 455.7 | 418.5
2362.1 | 2126.1 | 379.8 | 460.6 | 400.2 | 455.2 | 418.1
2363.1 | 2127.1 | 379.6 | 460.2 | 399.3 | 454.7 | 417.7
2364.1 | 2128.1 | 379.3 | 459.5 | 398.6 | 454.2 | 417.3
2365.1 | 2129.1 | 379 | 458.8 | 397.9 | 453.9 | 416.9
2366.1 | 2130.1 | 378.8 | 458.1 | 397.3 | 453.5 | 416.4
2367.1 | 2131.1 | 378.5 | 457.2 | 396.4 | 453.2 | 416
2368.1 | 2132.1 | 378.2 | 456.6 | 395.3 | 452.8 | 415.5
2369.1 | 2133.1 | 377.9 | 456 | 394.3 | 452.4 | 415
2370.1 | 2134.1 | 377.5 | 455.4 | 393.3 | 452.1 | 414.6
2371.1 | 2135.1 | 377.2 | 455.4 | 392.5 | 451.7 | 414.1
2372.1 | 2136.1 | 376.9 | 455.3 | 391.5 | 451.3 | 413.6
2373.1 | 2137.1 | 376.6 | 454.6 | 390.4 | 451.1 | 413.2
2374.1 | 2138.1 | 376.3 | 454 | 389.3 | 450.8 | 412.7
2375.1 | 2139.1 | 376 | 453.6 | 388.2 | 450.5 | 412.2
2376.1 | 2140.1 | 375.7 | 453.1 | 387.1 | 450 | 411.8
2377.1 | 2141.1 | 375.4 | 452.7 | 386 | 449.4 | 411.3
2378.1 | 2142.1 | 375.1 | 452.1 | 384.9 | 448.9 | 410.8
2379.1 | 2143.1 | 374.8 | 451.6 | 383.9 | 448.4 | 410.3
2380.1 | 2144.1 | 374.5 | 451.2 | 382.9 | 447.9 | 409.8
2381.1 | 2145.1 | 374.2 | 450.8 | 382 | 447.4 | 409.4
2382.1 | 2146.1 | 373.8 | 450.4 | 381.3 | 447 | 408.9
2383.1 | 2147.1 | 373.5 | 450 | 380.4 | 446.5 | 408.4
2384.1 | 2148.1 | 373.2 | 449.6 | 379.5 | 446.1 | 407.9
2385.1 | 2149.1 | 372.9 | 449.1 | 378.6 | 445.7 | 407.4
2386.1 | 2150.1 | 372.6 | 448.6 | 377.8 | 445.3 | 406.9
2387.1 | 2151.1 | 372.3 | 448.4 | 377.3 | 444.9 | 406.4
2388.1 | 2152.1 | 372 | 447.8 | 377 | 444.5 | 406
2389.1 | 2153.1 | 371.6 | 447 | 376.3 | 444.2 | 405.6
2390.1 | 2154.1 | 371.3 | 446.6 | 375.5 | 443.9 | 405.1
2391.1 | 2155.1 | 371 | 446.1 | 374.6 | 443.5 | 404.7
2392.1 | 2156.1 | 370.7 | 445.8 | 373.7 | 443.2 | 404.2
2393.1 | 2157.1 | 370.4 | 445.7 | 372.7 | 442.9 | 403.7
2394.1 | 2158.1 | 370.2 | 445.7 | 371.9 | 442.5 | 403.3
2395.1 | 2159.1 | 369.9 | 445.4 | 371.1 | 442.2 | 402.9
2396.1 | 2160.1 | 369.6 | 444.9 | 370.3 | 441.8 | 402.4
2397.1 | 2161.1 | 369.3 | 444.4 | 369.4 | 441.6 | 402
2398.1 | 2162.1 | 369 | 443.9 | 368.5 | 441.2 | 401.5
2399.1 | 2163.1 | 368.7 | 443.4 | 367.6 | 440.9 | 401.1
2400.1 | 2164.1 | 368.4 | 442.7 | 366.7 | 440.6 | 400.6
2401.1 | 2165.1 | 368.1 | 442.2 | 366 | 440.3 | 400.2
2402.1 | 2166.1 | 367.8 | 441.9 | 365.7 | 440 | 399.7
2403.1 | 2167.1 | 367.5 | 441.8 | 365.1 | 439.7 | 399.3
2404.1 | 2168.1 | 367.2 | 440.7 | 364.3 | 439.4 | 398.8
2405.1 | 2169.1 | 366.9 | 439.5 | 363.5 | 439.1 | 398.4
2406.1 | 2170.1 | 366.6 | 438.2 | 362.6 | 438.8 | 397.9
2407.1 | 2171.1 | 366.3 | 437.2 | 361.7 | 438.5 | 397.4
2408.1 | 2172.1 | 366 | 436.6 | 360.8 | 438.2 | 397
2409.1 | 2173.1 | 365.7 | 436.1 | 359.9 | 437.8 | 396.6
2410.1 | 2174.1 | 365.4 | 435.2 | 359 | 437.4 | 396.1
2411.1 | 2175.1 | 365.1 | 434.5 | 358.3 | 437.1 | 395.6
2412.1 | 2176.1 | 364.8 | 433.9 | 357.5 | 436.8 | 395.2
2413.1 | 2177.1 | 364.5 | 433.3 | 356.6 | 436.5 | 394.7
2414.1 | 2178.1 | 364.3 | 433 | 355.8 | 436.1 | 394.3
2415.1 | 2179.1 | 364 | 432.7 | 355 | 435.7 | 393.8
2416.1 | 2180.1 | 363.7 | 432.2 | 354.3 | 435.3 | 393.4
2417.1 | 2181.1 | 363.4 | 431.1 | 353.6 | 434.8 | 393
2418.1 | 2182.1 | 363.1 | 429.6 | 352.8 | 434.4 | 392.5
2419.1 | 2183.1 | 362.8 | 428.5 | 352.1 | 434.1 | 392.1
2420.1 | 2184.1 | 362.6 | 427.8 | 351.4 | 433.8 | 391.6
2421.1 | 2185.1 | 362.3 | 427.5 | 350.7 | 433.4 | 391.2
2422.1 | 2186.1 | 362.1 | 427.3 | 350.2 | 433.1 | 390.7
2423.1 | 2187.1 | 361.8 | 427 | 349.6 | 432.7 | 390.3
2424.1 | 2188.1 | 361.5 | 426.8 | 348.9 | 432.3 | 389.9
2425.1 | 2189.1 | 361.3 | 426.7 | 348.1 | 432 | 389.4
2426.1 | 2190.1 | 361 | 426.5 | 347.4 | 431.6 | 389
2427.1 | 2191.1 | 360.7 | 426.1 | 346.8 | 431.2 | 388.5
2428.1 | 2192.1 | 360.4 | 425.6 | 346.2 | 430.8 | 388.1
2429.1 | 2193.1 | 360.2 | 424.9 | 345.5 | 430.4 | 387.7
2430.1 | 2194.1 | 359.9 | 424.4 | 345 | 430.1 | 387.3
2431.1 | 2195.1 | 359.6 | 424.2 | 344.4 | 429.9 | 386.8
2432.1 | 2196.1 | 359.3 | 423.8 | 343.9 | 429.7 | 386.4
2433.1 | 2197.1 | 359.1 | 423.5 | 343.3 | 429.4 | 386
2434.1 | 2198.1 | 358.8 | 423.2 | 342.7 | 429.2 | 385.6
2435.1 | 2199.1 | 358.6 | 422.8 | 342 | 429 | 385.2
2436.1 | 2200.1 | 358.3 | 422.3 | 341.5 | 428.7 | 384.8
2437.1 | 2201.1 | 358 | 421.2 | 340.9 | 428.5 | 384.4
2438.1 | 2202.1 | 357.8 | 420 | 340.4 | 428.3 | 383.9
2439.1 | 2203.1 | 357.5 | 419.2 | 339.9 | 428.2 | 383.5
2440.1 | 2204.1 | 357.3 | 419 | 339.4 | 428.1 | 383.1
2441.1 | 2205.1 | 357 | 418.1 | 338.9 | 427.9 | 382.7
2442.1 | 2206.1 | 356.8 | 417.8 | 338.8 | 427.8 | 382.3
2443.1 | 2207.1 | 356.5 | 417.7 | 339 | 427.7 | 381.9
2444.1 | 2208.1 | 356.2 | 417.4 | 338.7 | 427.6 | 381.4
2445.1 | 2209.1 | 356 | 416.9 | 338.4 | 427.5 | 381
2446.1 | 2210.1 | 355.7 | 416.6 | 337.9 | 427.4 | 380.6
2447.1 | 2211.1 | 355.5 | 415.9 | 337.3 | 427.3 | 380.2
2448.1 | 2212.1 | 355.2 | 415.9 | 336.8 | 427.2 | 379.8
2449.1 | 2213.1 | 355 | 415.7 | 336.2 | 427.1 | 379.5
2450.1 | 2214.1 | 354.8 | 415.6 | 335.6 | 426.9 | 379
2451.1 | 2215.1 | 354.5 | 415.6 | 335 | 426.8 | 378.6
2452.1 | 2216.1 | 354.3 | 415.3 | 334.4 | 426.7 | 378.2
2453.1 | 2217.1 | 354 | 414.2 | 333.8 | 426.5 | 377.8
2454.1 | 2218.1 | 353.8 | 413 | 333 | 426.4 | 377.4
2455.1 | 2219.1 | 353.5 | 412.2 | 332.4 | 426.2 | 377
2456.1 | 2220.1 | 353.3 | 411 | 331.8 | 426 | 376.6
2457.1 | 2221.1 | 353 | 410.4 | 331.2 | 425.8 | 376.2
2458.1 | 2222.1 | 352.7 | 410.1 | 330.7 | 425.7 | 375.9
2459.1 | 2223.1 | 352.5 | 409.9 | 330.2 | 425.6 | 375.5
2460.1 | 2224.1 | 352.2 | 409.5 | 329.7 | 425.5 | 375.1
2461.1 | 2225.1 | 351.9 | 408.7 | 329.2 | 425.4 | 374.7
2462.1 | 2226.1 | 351.7 | 408.9 | 328.8 | 425.3 | 374.3
2463.1 | 2227.1 | 351.4 | 408.5 | 328.4 | 425.2 | 373.9
2464.1 | 2228.1 | 351.2 | 408.3 | 327.8 | 425.2 | 373.5
2465.1 | 2229.1 | 350.9 | 408.3 | 327.3 | 425.1 | 373.2
2466.1 | 2230.1 | 350.7 | 407.7 | 326.7 | 425 | 372.8
2467.1 | 2231.1 | 350.4 | 406.5 | 326.3 | 424.9 | 372.4
2468.1 | 2232.1 | 350.2 | 405.5 | 325.9 | 424.8 | 372
2469.1 | 2233.1 | 349.9 | 404.9 | 325.6 | 424.6 | 371.6
2470.1 | 2234.1 | 349.7 | 404.1 | 325.1 | 424.4 | 371.2
2471.1 | 2235.1 | 349.5 | 403.1 | 324.7 | 424.2 | 370.8
2472.1 | 2236.1 | 349.2 | 401.7 | 324.3 | 423.9 | 370.4
2473.1 | 2237.1 | 349 | 400.7 | 323.9 | 423.6 | 370
2474.1 | 2238.1 | 348.8 | 400.1 | 323.6 | 423.3 | 369.6
2475.1 | 2239.1 | 348.5 | 398.8 | 323.3 | 423 | 369.3
2476.1 | 2240.1 | 348.3 | 398.5 | 322.9 | 422.8 | 368.9
2477.1 | 2241.1 | 348 | 397.7 | 322.6 | 422.5 | 368.5
2478.1 | 2242.1 | 347.8 | 397 | 322.2 | 422.3 | 368.1
2479.1 | 2243.1 | 347.5 | 397 | 321.9 | 422.1 | 367.8
2480.1 | 2244.1 | 347.3 | 396.1 | 321.6 | 421.8 | 367.4
2481.1 | 2245.1 | 347.1 | 395.7 | 321.2 | 421.6 | 367
2482.1 | 2246.1 | 346.8 | 396.2 | 320.9 | 421.4 | 366.7
2483.1 | 2247.1 | 346.6 | 396.2 | 320.6 | 421.2 | 366.3
2484.1 | 2248.1 | 346.3 | 396.5 | 320.2 | 420.9 | 366
2485.1 | 2249.1 | 346.1 | 396.9 | 319.9 | 420.7 | 365.6
2486.1 | 2250.1 | 345.8 | 397 | 319.6 | 420.5 | 365.2
2487.1 | 2251.1 | 345.6 | 396.6 | 319.3 | 420.4 | 364.9
2488.1 | 2252.1 | 345.3 | 396 | 318.9 | 420.2 | 364.5
2489.1 | 2253.1 | 345.1 | 395.4 | 318.6 | 420 | 364.2
2490.1 | 2254.1 | 344.8 | 395.4 | 318.2 | 419.8 | 363.8
2491.1 | 2255.1 | 344.6 | 395.1 | 317.9 | 419.7 | 363.5
2492.1 | 2256.1 | 344.3 | 393.9 | 317.5 | 419.5 | 363.1
2493.1 | 2257.1 | 344.1 | 393.2 | 317.1 | 419.3 | 362.8
2494.1 | 2258.1 | 343.8 | 392.9 | 316.8 | 419.1 | 362.4
2495.1 | 2259.1 | 343.6 | 391.9 | 316.3 | 418.9 | 362.1
2496.1 | 2260.1 | 343.3 | 390.7 | 315.9 | 418.7 | 361.7
2497.1 | 2261.1 | 343.1 | 390 | 315.5 | 418.6 | 361.3
2498.1 | 2262.1 | 342.8 | 389.3 | 315.1 | 418.4 | 361
2499.1 | 2263.1 | 342.5 | 388 | 314.7 | 418.3 | 360.6
2500.1 | 2264.1 | 342.3 | 387.4 | 314.2 | 418.2 | 360.3
2501.1 | 2265.1 | 342 | 387.1 | 313.8 | 418 | 359.9
2502.1 | 2266.1 | 341.8 | 386.6 | 313.3 | 417.9 | 359.5
2503.1 | 2267.1 | 341.6 | 385.6 | 312.8 | 417.8 | 359.2
2504.1 | 2268.1 | 341.3 | 385.7 | 312.4 | 417.7 | 358.8
2505.1 | 2269.1 | 341.1 | 386.6 | 312.1 | 417.5 | 358.5
2506.1 | 2270.1 | 340.8 | 387 | 311.7 | 417.4 | 358.1
2507.1 | 2271.1 | 340.6 | 387 | 311.3 | 417.3 | 357.8
2508.1 | 2272.1 | 340.3 | 386.8 | 311 | 417.2 | 357.4
2509.1 | 2273.1 | 340.1 | 387 | 310.6 | 417.1 | 357.1
2510.1 | 2274.1 | 339.9 | 386.6 | 310.2 | 416.9 | 356.7
2511.1 | 2275.1 | 339.6 | 385.9 | 309.9 | 416.7 | 356.3
2512.1 | 2276.1 | 339.4 | 385.4 | 309.4 | 416.5 | 356
2513.1 | 2277.1 | 339.1 | 384.2 | 309 | 416.3 | 355.7
2514.1 | 2278.1 | 338.9 | 383 | 308.7 | 416.2 | 355.3
2515.1 | 2279.1 | 338.6 | 382.6 | 308.3 | 416 | 355
2516.1 | 2280.1 | 338.4 | 382.3 | 307.9 | 415.9 | 354.7
2517.1 | 2281.1 | 338.1 | 381.6 | 307.5 | 415.9 | 354.3
2518.1 | 2282.1 | 337.9 | 381.8 | 307.1 | 415.8 | 354
2519.1 | 2283.1 | 337.6 | 380.8 | 306.7 | 415.7 | 353.7
2520.1 | 2284.1 | 337.3 | 380.5 | 306.4 | 415.6 | 353.3
2521.1 | 2285.1 | 337.1 | 380.9 | 306 | 415.5 | 353
2522.1 | 2286.1 | 336.8 | 380.6 | 305.7 | 415.4 | 352.6
2523.1 | 2287.1 | 336.6 | 379.8 | 305.3 | 415.2 | 352.3
2524.1 | 2288.1 | 336.3 | 379.9 | 305 | 415 | 351.9
2525.1 | 2289.1 | 336.1 | 379.7 | 304.7 | 414.8 | 351.6
2526.1 | 2290.1 | 335.8 | 380.4 | 304.4 | 414.7 | 351.3
2527.1 | 2291.1 | 335.6 | 380.2 | 304.1 | 414.5 | 350.9
2528.1 | 2292.1 | 335.3 | 380.5 | 303.8 | 414.3 | 350.6
2529.1 | 2293.1 | 335.1 | 380.7 | 303.5 | 414.2 | 350.3
2530.1 | 2294.1 | 334.9 | 380.9 | 303.2 | 414 | 350
2531.1 | 2295.1 | 334.6 | 380.8 | 302.9 | 413.8 | 349.6
2532.1 | 2296.1 | 334.4 | 380.6 | 302.6 | 413.6 | 349.3
2533.1 | 2297.1 | 334.2 | 380.8 | 302.3 | 413.4 | 349
2534.1 | 2298.1 | 333.9 | 380.7 | 301.9 | 413.3 | 348.7
2535.1 | 2299.1 | 333.7 | 380.2 | 301.5 | 413.1 | 348.3
2536.1 | 2300.1 | 333.4 | 380.3 | 301.2 | 413 | 348
2537.1 | 2301.1 | 333.2 | 379.5 | 300.9 | 412.8 | 347.7
2538.1 | 2302.1 | 332.9 | 378.5 | 300.5 | 412.8 | 347.4
2539.1 | 2303.1 | 332.7 | 378.4 | 300.2 | 412.6 | 347
2540.1 | 2304.1 | 332.4 | 378.3 | 299.9 | 412.5 | 346.7
2541.1 | 2305.1 | 332.2 | 377.8 | 299.6 | 412.4 | 346.4
2542.1 | 2306.1 | 332 | 377.5 | 299.3 | 412.3 | 346.1
2543.1 | 2307.1 | 331.7 | 377.7 | 298.9 | 412.1 | 345.7
2544.1 | 2308.1 | 331.5 | 377.4 | 298.6 | 411.9 | 345.4
2545.1 | 2309.1 | 331.3 | 377.3 | 298.2 | 411.7 | 345.1
2546.1 | 2310.1 | 331 | 376.6 | 297.8 | 411.6 | 344.8
2547.1 | 2311.1 | 330.8 | 376.2 | 297.5 | 411.4 | 344.5
2548.1 | 2312.1 | 330.6 | 375.9 | 297.2 | 411.3 | 344.2
2549.1 | 2313.1 | 330.3 | 375.8 | 296.8 | 411.2 | 343.9
2550.1 | 2314.1 | 330.1 | 375.8 | 296.5 | 411.1 | 343.6
2551.1 | 2315.1 | 329.9 | 375.8 | 296.2 | 410.9 | 343.3
2552.1 | 2316.1 | 329.6 | 375.3 | 295.9 | 410.7 | 343
2553.1 | 2317.1 | 329.4 | 374.4 | 295.6 | 410.5 | 342.6
2554.1 | 2318.1 | 329.2 | 374.2 | 295.3 | 410.3 | 342.3
2555.1 | 2319.1 | 329 | 374 | 295 | 410.1 | 342
2556.1 | 2320.1 | 328.8 | 374 | 294.7 | 409.9 | 341.7
2557.1 | 2321.1 | 328.6 | 373.3 | 294.4 | 409.7 | 341.4
2558.1 | 2322.1 | 328.4 | 372.8 | 294.1 | 409.5 | 341.1
2559.1 | 2323.1 | 328.2 | 373 | 293.8 | 409.4 | 340.8
2560.1 | 2324.1 | 328 | 373 | 293.6 | 409.2 | 340.5
2561.1 | 2325.1 | 327.8 | 373 | 293.4 | 409 | 340.2
2562.1 | 2326.1 | 327.5 | 373.1 | 293.1 | 408.9 | 339.9
2563.1 | 2327.1 | 327.3 | 372.5 | 292.8 | 408.8 | 339.5
2564.1 | 2328.1 | 327.1 | 372.1 | 292.5 | 408.6 | 339.2
2565.1 | 2329.1 | 327 | 371.9 | 292.2 | 408.4 | 338.9
2566.1 | 2330.1 | 326.7 | 371.2 | 292 | 408.3 | 338.6
2567.1 | 2331.1 | 326.5 | 370.4 | 291.7 | 408.2 | 338.3
2568.1 | 2332.1 | 326.4 | 370.2 | 291.4 | 408.1 | 338.1
2569.1 | 2333.1 | 326.1 | 369.6 | 291.2 | 408 | 337.8
2570.1 | 2334.1 | 325.9 | 369.8 | 290.8 | 407.9 | 337.5
2571.1 | 2335.1 | 325.7 | 370.1 | 290.5 | 407.8 | 337.2
2572.1 | 2336.1 | 325.5 | 370 | 290.3 | 407.6 | 336.9
2573.1 | 2337.1 | 325.3 | 369.7 | 290 | 407.5 | 336.6
2574.1 | 2338.1 | 325.1 | 370.1 | 289.7 | 407.5 | 336.3
2575.1 | 2339.1 | 324.9 | 369.7 | 289.5 | 407.4 | 336
2576.1 | 2340.1 | 324.7 | 369 | 289.2 | 407.4 | 335.7
2577.1 | 2341.1 | 324.5 | 368.5 | 289 | 407.5 | 335.4
2578.1 | 2342.1 | 324.3 | 367.9 | 288.7 | 407.5 | 335.1
2579.1 | 2343.1 | 324.1 | 366.7 | 288.4 | 407.6 | 334.8
2580.1 | 2344.1 | 323.9 | 366.6 | 288 | 407.6 | 334.5
2581.1 | 2345.1 | 323.7 | 367.1 | 287.7 | 407.8 | 334.2
2582.1 | 2346.1 | 323.5 | 367.7 | 287.4 | 407.8 | 333.9
2583.1 | 2347.1 | 323.4 | 367.5 | 287 | 407.8 | 333.6
2584.1 | 2348.1 | 323.2 | 367.6 | 286.7 | 407.9 | 333.3
2585.1 | 2349.1 | 323 | 367.3 | 286.4 | 407.9 | 333.1
2586.1 | 2350.1 | 322.8 | 367.3 | 286.1 | 408 | 332.8
2587.1 | 2351.1 | 322.6 | 367.1 | 285.8 | 408 | 332.5
2588.1 | 2352.1 | 322.4 | 366.5 | 285.5 | 408 | 332.2
2589.1 | 2353.1 | 322.2 | 366.3 | 285.1 | 408 | 331.9
2590.1 | 2354.1 | 322 | 366.6 | 284.8 | 407.9 | 331.7
2591.1 | 2355.1 | 321.8 | 366.6 | 284.4 | 407.8 | 331.4
2592.1 | 2356.1 | 321.6 | 366.8 | 284 | 407.7 | 331.1
2593.1 | 2357.1 | 321.4 | 367 | 283.7 | 407.6 | 330.8
2594.1 | 2358.1 | 321.2 | 366.5 | 283.3 | 407.5 | 330.5
2595.1 | 2359.1 | 321 | 366.6 | 283 | 407.5 | 330.2
2596.1 | 2360.1 | 320.8 | 367 | 282.6 | 407.4 | 330
2597.1 | 2361.1 | 320.6 | 367.2 | 282.3 | 407.4 | 329.7
2598.1 | 2362.1 | 320.5 | 367.2 | 282 | 407.5 | 329.4
2599.1 | 2363.1 | 320.3 | 367 | 281.6 | 407.5 | 329.1
2600.1 | 2364.1 | 320.1 | 366.8 | 281.3 | 407.5 | 328.8
2601.1 | 2365.1 | 319.9 | 366.7 | 281.1 | 407.4 | 328.5
2602.1 | 2366.1 | 319.7 | 365.4 | 280.8 | 407.3 | 328.3
2603.1 | 2367.1 | 319.5 | 364.1 | 280.5 | 407.3 | 328
2604.1 | 2368.1 | 319.3 | 363 | 280.2 | 407.2 | 327.7
2605.1 | 2369.1 | 319.2 | 362.9 | 279.9 | 407.2 | 327.4
2606.1 | 2370.1 | 319 | 362.9 | 279.6 | 407.1 | 327.2
2607.1 | 2371.1 | 318.8 | 363.3 | 279.4 | 407.1 | 326.9
2608.1 | 2372.1 | 318.6 | 362.8 | 279.1 | 407 | 326.6
2609.1 | 2373.1 | 318.4 | 362.2 | 278.8 | 406.9 | 326.4
2610.1 | 2374.1 | 318.3 | 361.3 | 278.4 | 406.8 | 326.1
2611.1 | 2375.1 | 318.1 | 361.4 | 278.2 | 406.7 | 325.8
2612.1 | 2376.1 | 317.9 | 360.9 | 277.9 | 406.6 | 325.5
2613.1 | 2377.1 | 317.7 | 360.6 | 277.6 | 406.5 | 325.2
2614.1 | 2378.1 | 317.5 | 360.3 | 277.4 | 406.4 | 325
2615.1 | 2379.1 | 317.3 | 360.5 | 277.1 | 406.3 | 324.7
2616.1 | 2380.1 | 317.1 | 361 | 276.9 | 406.2 | 324.4
2617.1 | 2381.1 | 317 | 361 | 276.7 | 406.1 | 324.2
2618.1 | 2382.1 | 316.8 | 361.2 | 276.4 | 406.1 | 323.9
2619.1 | 2383.1 | 316.6 | 361 | 276.1 | 406.1 | 323.7
2620.1 | 2384.1 | 316.4 | 360.2 | 275.9 | 406.2 | 323.4
2621.1 | 2385.1 | 316.2 | 360.1 | 275.6 | 406.2 | 323.2
2622.1 | 2386.1 | 316.1 | 359.3 | 275.3 | 406.3 | 322.9
2623.1 | 2387.1 | 315.9 | 358.5 | 275 | 406.4 | 322.6
2624.1 | 2388.1 | 315.7 | 358.5 | 274.7 | 406.5 | 322.4
2625.1 | 2389.1 | 315.5 | 358.9 | 274.4 | 406.5 | 322.1
2626.1 | 2390.1 | 315.4 | 359.1 | 274.1 | 406.5 | 321.9
2627.1 | 2391.1 | 315.2 | 359.3 | 273.8 | 406.5 | 321.6
2628.1 | 2392.1 | 315 | 359.1 | 273.6 | 406.4 | 321.3
2629.1 | 2393.1 | 314.8 | 358 | 273.3 | 406.3 | 321.1
2630.1 | 2394.1 | 314.7 | 356.6 | 273.1 | 406.2 | 320.8
2631.1 | 2395.1 | 314.5 | 356.3 | 272.8 | 406.1 | 320.6
2632.1 | 2396.1 | 314.3 | 356.1 | 272.6 | 406 | 320.3
2633.1 | 2397.1 | 314.1 | 356.3 | 272.3 | 405.9 | 320.1
2634.1 | 2398.1 | 314 | 356.2 | 272.1 | 405.8 | 319.8
2635.1 | 2399.1 | 313.8 | 355.8 | 271.8 | 405.7 | 319.6
2636.1 | 2400.1 | 313.6 | 355.6 | 271.5 | 405.7 | 319.3
2637.1 | 2401.1 | 313.4 | 355.2 | 271.2 | 405.7 | 319.1
2638.1 | 2402.1 | 313.3 | 354.9 | 271 | 405.7 | 318.8
2639.1 | 2403.1 | 313.1 | 354.8 | 270.7 | 405.6 | 318.6
2640.1 | 2404.1 | 312.9 | 355 | 270.4 | 405.7 | 318.3
2641.1 | 2405.1 | 312.7 | 354.2 | 270.1 | 405.7 | 318
2642.1 | 2406.1 | 312.6 | 352.9 | 269.8 | 405.7 | 317.8
2643.1 | 2407.1 | 312.4 | 351.9 | 269.4 | 405.6 | 317.5
2644.1 | 2408.1 | 312.2 | 351.8 | 269.1 | 405.5 | 317.2
2645.1 | 2409.1 | 312 | 352.1 | 268.8 | 405.4 | 317
2646.1 | 2410.1 | 311.9 | 352.2 | 268.4 | 405.3 | 316.7
2647.1 | 2411.1 | 311.7 | 351.9 | 268 | 405.1 | 316.5
2648.1 | 2412.1 | 311.5 | 351.8 | 267.7 | 404.9 | 316.2
2649.1 | 2413.1 | 311.3 | 351.3 | 267.5 | 404.8 | 316
2650.1 | 2414.1 | 311.2 | 350.3 | 267.2 | 404.7 | 315.7
2651.1 | 2415.1 | 311 | 350.2 | 266.9 | 404.7 | 315.5
2652.1 | 2416.1 | 310.8 | 349.7 | 266.6 | 404.5 | 315.2
2653.1 | 2417.1 | 310.6 | 349.4 | 266.3 | 404.4 | 315
2654.1 | 2418.1 | 310.5 | 348.9 | 266 | 404.3 | 314.8
2655.1 | 2419.1 | 310.3 | 349 | 265.7 | 404.3 | 314.5
2656.1 | 2420.1 | 310.1 | 348.9 | 265.4 | 404.2 | 314.3
2657.1 | 2421.1 | 310 | 348.8 | 265.1 | 404.1 | 314
2658.1 | 2422.1 | 309.8 | 348.4 | 264.9 | 403.9 | 313.8
2659.1 | 2423.1 | 309.6 | 348.3 | 264.6 | 403.8 | 313.5
2660.1 | 2424.1 | 309.5 | 347.9 | 264.4 | 403.7 | 313.3
2661.1 | 2425.1 | 309.3 | 347.3 | 264.2 | 403.6 | 313
2662.1 | 2426.1 | 309.1 | 347.6 | 264.1 | 403.5 | 312.8
2663.1 | 2427.1 | 308.9 | 347.8 | 263.9 | 403.4 | 312.5
2664.1 | 2428.1 | 308.8 | 347.8 | 263.7 | 403.4 | 312.3
2665.1 | 2429.1 | 308.6 | 347.5 | 263.5 | 403.4 | 312
2666.1 | 2430.1 | 308.4 | 346.9 | 263.3 | 403.4 | 311.8
2667.1 | 2431.1 | 308.3 | 346.6 | 263 | 403.3 | 311.5
2668.1 | 2432.1 | 308.1 | 346.3 | 262.8 | 403.3 | 311.3
2669.1 | 2433.1 | 308 | 346.1 | 262.6 | 403.3 | 311.1
2670.1 | 2434.1 | 307.8 | 345.5 | 262.4 | 403.3 | 310.8
2671.1 | 2435.1 | 307.6 | 345.4 | 262.2 | 403.3 | 310.6
2672.1 | 2436.1 | 307.5 | 345.4 | 262 | 403.2 | 310.4
2673.1 | 2437.1 | 307.3 | 345.4 | 261.7 | 403.2 | 310.1
2674.1 | 2438.1 | 307.2 | 345.5 | 261.4 | 403.2 | 309.9
2675.1 | 2439.1 | 307 | 345.4 | 261.1 | 403.2 | 309.6
2676.1 | 2440.1 | 306.8 | 345.7 | 260.8 | 403.2 | 309.4
2677.1 | 2441.1 | 306.7 | 346 | 260.5 | 403.1 | 309.2
2678.1 | 2442.1 | 306.5 | 345.9 | 260.1 | 403 | 308.9
2679.1 | 2443.1 | 306.4 | 346 | 259.8 | 402.9 | 308.7
2680.1 | 2444.1 | 306.2 | 345.9 | 259.4 | 402.7 | 308.5
2681.1 | 2445.1 | 306 | 346 | 259.2 | 402.5 | 308.2
2682.1 | 2446.1 | 305.9 | 345.6 | 258.9 | 402.4 | 308
2683.1 | 2447.1 | 305.7 | 345.4 | 258.5 | 402.2 | 307.8
2684.1 | 2448.1 | 305.6 | 345.5 | 258.2 | 402.1 | 307.5
2685.1 | 2449.1 | 305.4 | 345.3 | 257.9 | 402 | 307.3
2686.1 | 2450.1 | 305.2 | 345 | 257.6 | 401.9 | 307
2687.1 | 2451.1 | 305.1 | 345 | 257.4 | 401.9 | 306.8
2688.1 | 2452.1 | 304.9 | 344.8 | 257.1 | 401.8 | 306.6
2689.1 | 2453.1 | 304.8 | 344.4 | 256.8 | 401.8 | 306.3
2690.1 | 2454.1 | 304.6 | 344.4 | 256.6 | 401.7 | 306.1
2691.1 | 2455.1 | 304.5 | 344.3 | 256.4 | 401.5 | 305.9
2692.1 | 2456.1 | 304.3 | 344 | 256.1 | 401.3 | 305.7
2693.1 | 2457.1 | 304.1 | 343.5 | 255.9 | 401.1 | 305.4
2694.1 | 2458.1 | 304 | 343.1 | 255.7 | 401 | 305.2
2695.1 | 2459.1 | 303.8 | 342.5 | 255.5 | 400.9 | 305
2696.1 | 2460.1 | 303.7 | 342.5 | 255.2 | 400.7 | 304.8
2697.1 | 2461.1 | 303.5 | 342.3 | 255 | 400.5 | 304.5
2698.1 | 2462.1 | 303.4 | 341.6 | 254.7 | 400.3 | 304.3
2699.1 | 2463.1 | 303.2 | 340.6 | 254.5 | 400.2 | 304.1
2700.1 | 2464.1 | 303.1 | 339.8 | 254.4 | 400 | 303.9
2701.1 | 2465.1 | 302.9 | 339.5 | 254.2 | 399.8 | 303.7
2702.1 | 2466.1 | 302.8 | 339.4 | 254 | 399.6 | 303.4
2703.1 | 2467.1 | 302.6 | 339 | 253.8 | 399.4 | 303.2
2704.1 | 2468.1 | 302.5 | 338.7 | 253.7 | 399.2 | 303
2705.1 | 2469.1 | 302.3 | 338.8 | 253.5 | 399.1 | 302.8
2706.1 | 2470.1 | 302.2 | 338.5 | 253.2 | 398.9 | 302.6
2707.1 | 2471.1 | 302 | 337.3 | 253 | 398.7 | 302.3
2708.1 | 2472.1 | 301.9 | 337.2 | 252.8 | 398.6 | 302.1
2709.1 | 2473.1 | 301.7 | 336.6 | 252.6 | 398.4 | 301.9
2710.1 | 2474.1 | 301.6 | 336.2 | 252.4 | 398.2 | 301.7
2711.1 | 2475.1 | 301.4 | 336.1 | 252.1 | 398.1 | 301.5
2712.1 | 2476.1 | 301.3 | 336.2 | 251.9 | 397.9 | 301.3
2713.1 | 2477.1 | 301.1 | 336.3 | 251.6 | 397.7 | 301
2714.1 | 2478.1 | 301 | 336.2 | 251.4 | 397.6 | 300.8
2715.1 | 2479.1 | 300.9 | 336 | 251.2 | 397.4 | 300.6
2716.1 | 2480.1 | 300.7 | 335.8 | 250.9 | 397.3 | 300.4
2717.1 | 2481.1 | 300.6 | 335.8 | 250.6 | 397.1 | 300.2
2718.1 | 2482.1 | 300.4 | 335.6 | 250.4 | 397 | 300
2719.1 | 2483.1 | 300.3 | 335.3 | 250.1 | 396.8 | 299.8
2720.1 | 2484.1 | 300.1 | 334.9 | 249.8 | 396.7 | 299.6
2721.1 | 2485.1 | 300 | 334.8 | 249.5 | 396.6 | 299.4
2722.1 | 2486.1 | 299.8 | 334.7 | 249.4 | 396.5 | 299.2
2723.1 | 2487.1 | 299.7 | 334.8 | 249.2 | 396.3 | 298.9
2724.1 | 2488.1 | 299.6 | 334.6 | 248.9 | 396.1 | 298.7
2725.1 | 2489.1 | 299.4 | 334.8 | 248.7 | 396 | 298.5
2726.1 | 2490.1 | 299.3 | 334.1 | 248.4 | 395.7 | 298.3
2727.1 | 2491.1 | 299.1 | 334.1 | 248.2 | 395.5 | 298.1
2728.1 | 2492.1 | 299 | 333.7 | 247.9 | 395.3 | 297.9
2729.1 | 2493.1 | 298.8 | 332.8 | 247.7 | 395.1 | 297.7
2730.1 | 2494.1 | 298.7 | 332.3 | 247.4 | 394.9 | 297.5
2731.1 | 2495.1 | 298.6 | 332.1 | 247.2 | 394.8 | 297.3
2732.1 | 2496.1 | 298.4 | 331.9 | 247 | 394.6 | 297.1
2733.1 | 2497.1 | 298.3 | 331.5 | 246.8 | 394.4 | 296.8
2734.1 | 2498.1 | 298.1 | 332 | 246.5 | 394.2 | 296.6
2735.1 | 2499.1 | 298 | 331.9 | 246.3 | 394 | 296.4
2736.1 | 2500.1 | 297.8 | 331.7 | 246.1 | 393.8 | 296.2
2737.1 | 2501.1 | 297.7 | 331.4 | 245.8 | 393.6 | 296
2738.1 | 2502.1 | 297.5 | 331.4 | 245.6 | 393.3 | 295.8
2739.1 | 2503.1 | 297.4 | 330.8 | 245.3 | 393.2 | 295.6
2740.1 | 2504.1 | 297.3 | 330.7 | 245.1 | 393 | 295.4
2741.1 | 2505.1 | 297.1 | 330.8 | 244.8 | 392.8 | 295.2
2742.1 | 2506.1 | 297 | 330.6 | 244.6 | 392.6 | 295
2743.1 | 2507.1 | 296.8 | 330.3 | 244.3 | 392.4 | 294.8
2744.1 | 2508.1 | 296.7 | 329.8 | 244.1 | 392.2 | 294.6
2745.1 | 2509.1 | 296.5 | 329.5 | 243.9 | 392 | 294.4
2746.1 | 2510.1 | 296.4 | 329.6 | 243.6 | 391.8 | 294.2
2747.1 | 2511.1 | 296.2 | 328.8 | 243.3 | 391.7 | 294
2748.1 | 2512.1 | 296.1 | 328.3 | 243.1 | 391.5 | 293.8
2749.1 | 2513.1 | 295.9 | 328.1 | 242.8 | 391.3 | 293.6
2750.1 | 2514.1 | 295.8 | 327.4 | 242.6 | 391 | 293.4
2751.1 | 2515.1 | 295.6 | 327 | 242.3 | 390.8 | 293.2
2752.1 | 2516.1 | 295.5 | 326.7 | 242.1 | 390.6 | 293
2753.1 | 2517.1 | 295.4 | 326.5 | 241.9 | 390.4 | 292.8
2754.1 | 2518.1 | 295.2 | 326.2 | 241.7 | 390.2 | 292.7
2755.1 | 2519.1 | 295.1 | 326.2 | 241.5 | 390 | 292.4
2756.1 | 2520.1 | 294.9 | 326 | 241.2 | 389.8 | 292.2
2757.1 | 2521.1 | 294.8 | 325.8 | 241 | 389.6 | 292
2758.1 | 2522.1 | 294.7 | 325.6 | 240.9 | 389.4 | 291.8
2759.1 | 2523.1 | 294.5 | 325.4 | 240.7 | 389.2 | 291.6
2760.1 | 2524.1 | 294.4 | 325.1 | 240.6 | 389 | 291.4
2761.1 | 2525.1 | 294.2 | 324.9 | 240.5 | 388.9 | 291.3
2762.1 | 2526.1 | 294.1 | 324.9 | 240.4 | 388.6 | 291.1
2763.1 | 2527.1 | 293.9 | 324.9 | 240.2 | 388.4 | 290.9
2764.1 | 2528.1 | 293.8 | 324.7 | 240 | 388.2 | 290.7
2765.1 | 2529.1 | 293.7 | 324.7 | 239.9 | 388 | 290.5
2766.1 | 2530.1 | 293.5 | 324.4 | 239.7 | 387.9 | 290.3
2767.1 | 2531.1 | 293.4 | 324.2 | 239.5 | 387.7 | 290.1
2768.1 | 2532.1 | 293.3 | 323.7 | 239.4 | 387.5 | 289.9
2769.1 | 2533.1 | 293.1 | 323.1 | 239.2 | 387.3 | 289.7
2770.1 | 2534.1 | 293 | 322.6 | 239.1 | 387.2 | 289.5
2771.1 | 2535.1 | 292.8 | 322.2 | 239 | 387 | 289.3
2772.1 | 2536.1 | 292.7 | 322.1 | 238.8 | 386.8 | 289.1
2773.1 | 2537.1 | 292.6 | 321.6 | 238.7 | 386.5 | 288.9
2774.1 | 2538.1 | 292.4 | 321.7 | 238.6 | 386.3 | 288.7
2775.1 | 2539.1 | 292.3 | 321.5 | 238.5 | 386.1 | 288.5
2776.1 | 2540.1 | 292.1 | 321.3 | 238.4 | 385.8 | 288.3
2777.1 | 2541.1 | 292 | 321.2 | 238.3 | 385.6 | 288.1
2778.1 | 2542.1 | 291.9 | 321 | 238.1 | 385.4 | 288
2779.1 | 2543.1 | 291.7 | 320.9 | 238 | 385.2 | 287.8
2780.1 | 2544.1 | 291.6 | 320.9 | 237.9 | 385 | 287.6
2781.1 | 2545.1 | 291.5 | 320.7 | 237.8 | 384.8 | 287.5
2782.1 | 2546.1 | 291.4 | 320.3 | 237.6 | 384.6 | 287.3
2783.1 | 2547.1 | 291.2 | 320.1 | 237.5 | 384.4 | 287.1
2784.1 | 2548.1 | 291.1 | 319.8 | 237.3 | 384.2 | 286.9
2785.1 | 2549.1 | 291 | 320.1 | 237.3 | 384 | 286.8
2786.1 | 2550.1 | 290.8 | 320.8 | 237.2 | 383.8 | 286.6
2787.1 | 2551.1 | 290.7 | 320.7 | 237.2 | 383.6 | 286.4
2788.1 | 2552.1 | 290.6 | 320.5 | 237.1 | 383.4 | 286.2
2789.1 | 2553.1 | 290.5 | 320.5 | 237.1 | 383.2 | 286.1
2790.1 | 2554.1 | 290.4 | 319.8 | 237 | 382.9 | 285.9
2791.1 | 2555.1 | 290.3 | 319.4 | 237 | 382.7 | 285.7
2792.1 | 2556.1 | 290.1 | 318.9 | 237 | 382.5 | 285.6
2793.1 | 2557.1 | 290 | 318.4 | 236.9 | 382.3 | 285.4
2794.1 | 2558.1 | 289.9 | 317.8 | 236.9 | 382.1 | 285.2
2795.1 | 2559.1 | 289.8 | 317.9 | 236.8 | 381.9 | 285.1
2796.1 | 2560.1 | 289.7 | 317.7 | 236.7 | 381.6 | 284.9
2797.1 | 2561.1 | 289.6 | 317.7 | 236.7 | 381.4 | 284.7
2798.1 | 2562.1 | 289.5 | 317.6 | 236.6 | 381.1 | 284.6
2799.1 | 2563.1 | 289.4 | 317.4 | 236.5 | 380.9 | 284.4
2800.1 | 2564.1 | 289.3 | 317.2 | 236.4 | 380.6 | 284.2
2801.1 | 2565.1 | 289.1 | 316.9 | 236.3 | 380.3 | 284.1
2802.1 | 2566.1 | 289 | 317.1 | 236.3 | 380.1 | 283.9
2803.1 | 2567.1 | 288.9 | 316.9 | 236.2 | 379.8 | 283.7
2804.1 | 2568.1 | 288.8 | 316.7 | 236.2 | 379.6 | 283.6
2805.1 | 2569.1 | 288.7 | 316.8 | 236.1 | 379.4 | 283.4
2806.1 | 2570.1 | 288.6 | 316.8 | 236 | 379.1 | 283.2
2807.1 | 2571.1 | 288.5 | 316.6 | 236 | 378.8 | 283.1
2808.1 | 2572.1 | 288.4 | 316.6 | 235.9 | 378.6 | 282.9
2809.1 | 2573.1 | 288.3 | 316.5 | 235.9 | 378.3 | 282.8
2810.1 | 2574.1 | 288.2 | 316.3 | 235.8 | 378.1 | 282.6
2811.1 | 2575.1 | 288.1 | 316.1 | 235.8 | 377.9 | 282.5
2812.1 | 2576.1 | 288 | 316.1 | 235.7 | 377.6 | 282.3
2813.1 | 2577.1 | 287.9 | 316.1 | 235.7 | 377.4 | 282.2
2814.1 | 2578.1 | 287.8 | 315.7 | 235.6 | 377.1 | 282
2815.1 | 2579.1 | 287.7 | 315 | 235.5 | 376.9 | 281.9
2816.1 | 2580.1 | 287.6 | 314.9 | 235.4 | 376.7 | 281.7
2817.1 | 2581.1 | 287.4 | 314.8 | 235.3 | 376.4 | 281.6
2818.1 | 2582.1 | 287.3 | 314.7 | 235.3 | 376.2 | 281.4
2819.1 | 2583.1 | 287.2 | 314.5 | 235.2 | 376 | 281.3
2820.1 | 2584.1 | 287.1 | 314.5 | 235.2 | 375.7 | 281.1
2821.1 | 2585.1 | 287 | 314.1 | 235.2 | 375.5 | 281
2822.1 | 2586.1 | 286.9 | 313.6 | 235.1 | 375.2 | 280.8
2823.1 | 2587.1 | 286.8 | 313.4 | 235 | 375 | 280.6
2824.1 | 2588.1 | 286.7 | 313.1 | 234.9 | 374.7 | 280.5
2825.1 | 2589.1 | 286.6 | 312.2 | 234.8 | 374.5 | 280.3
2826.1 | 2590.1 | 286.5 | 311.5 | 234.5 | 374.2 | 280.2
2827.1 | 2591.1 | 286.4 | 311.3 | 234.3 | 373.9 | 280
2828.1 | 2592.1 | 286.3 | 311.4 | 234 | 373.7 | 279.9
2829.1 | 2593.1 | 286.2 | 311.1 | 233.7 | 373.4 | 279.7
2830.1 | 2594.1 | 286.1 | 311 | 233.5 | 373.2 | 279.6
2831.1 | 2595.1 | 286 | 310.8 | 233.2 | 373 | 279.4
2832.1 | 2596.1 | 285.9 | 310.6 | 233 | 372.7 | 279.3
2833.1 | 2597.1 | 285.8 | 310.5 | 232.7 | 372.4 | 279.1
2834.1 | 2598.1 | 285.6 | 310.4 | 232.5 | 372.1 | 279
2835.1 | 2599.1 | 285.5 | 310.2 | 232.3 | 371.9 | 278.8
2836.1 | 2600.1 | 285.4 | 310.1 | 232.1 | 371.6 | 278.6
2837.1 | 2601.1 | 285.3 | 309.9 | 232 | 371.3 | 278.5
2838.1 | 2602.1 | 285.2 | 309.8 | 231.8 | 371 | 278.3
2839.1 | 2603.1 | 285.1 | 309.8 | 231.7 | 370.7 | 278.2
2840.1 | 2604.1 | 284.9 | 309.8 | 231.5 | 370.4 | 278
2841.1 | 2605.1 | 284.8 | 309.8 | 231.3 | 370.1 | 277.9
2842.1 | 2606.1 | 284.7 | 309.3 | 231 | 369.8 | 277.7
2843.1 | 2607.1 | 284.6 | 309.1 | 230.8 | 369.6 | 277.6
2844.1 | 2608.1 | 284.5 | 309.1 | 230.6 | 369.3 | 277.4
2845.1 | 2609.1 | 284.4 | 308.7 | 230.4 | 369 | 277.2
2846.1 | 2610.1 | 284.2 | 308.1 | 230.2 | 368.7 | 277.1
2847.1 | 2611.1 | 284.1 | 307.9 | 229.9 | 368.4 | 276.9
2848.1 | 2612.1 | 284 | 307.4 | 229.7 | 368.2 | 276.8
2849.1 | 2613.1 | 283.9 | 307.2 | 229.5 | 367.9 | 276.6
2850.1 | 2614.1 | 283.8 | 307.2 | 229.3 | 367.6 | 276.5
2851.1 | 2615.1 | 283.6 | 307.1 | 229.1 | 367.3 | 276.3
2852.1 | 2616.1 | 283.5 | 306.9 | 228.9 | 367 | 276.1
2853.1 | 2617.1 | 283.4 | 306.7 | 228.7 | 366.7 | 276
2854.1 | 2618.1 | 283.3 | 306.4 | 228.5 | 366.4 | 275.8
2855.1 | 2619.1 | 283.1 | 306.2 | 228.3 | 366.1 | 275.7
2856.1 | 2620.1 | 283 | 306.2 | 228 | 365.8 | 275.5
2857.1 | 2621.1 | 282.9 | 306.2 | 227.8 | 365.5 | 275.4
2858.1 | 2622.1 | 282.8 | 306.2 | 227.5 | 365.2 | 275.2
2859.1 | 2623.1 | 282.7 | 306.1 | 227.2 | 364.9 | 275
2860.1 | 2624.1 | 282.5 | 305.9 | 226.9 | 364.6 | 274.9
2861.1 | 2625.1 | 282.4 | 305.5 | 226.6 | 364.3 | 274.7
2862.1 | 2626.1 | 282.3 | 305.6 | 226.4 | 364.1 | 274.6
2863.1 | 2627.1 | 282.2 | 305.7 | 226.2 | 363.8 | 274.4
2864.1 | 2628.1 | 282 | 305.8 | 226 | 363.5 | 274.2
2865.1 | 2629.1 | 281.9 | 305.5 | 225.7 | 363.2 | 274.1
2866.1 | 2630.1 | 281.8 | 305.3 | 225.6 | 362.9 | 273.9
2867.1 | 2631.1 | 281.7 | 305.1 | 225.5 | 362.6 | 273.8
2868.1 | 2632.1 | 281.6 | 305 | 225.3 | 362.4 | 273.6
2869.1 | 2633.1 | 281.4 | 304.8 | 225 | 362.1 | 273.4
2870.1 | 2634.1 | 281.3 | 304.7 | 224.8 | 361.8 | 273.3
2871.1 | 2635.1 | 281.2 | 304.4 | 224.6 | 361.6 | 273.1
2872.1 | 2636.1 | 281.1 | 304.1 | 224.4 | 361.3 | 272.9
2873.1 | 2637.1 | 281 | 303.6 | 224.2 | 361 | 272.8
2874.1 | 2638.1 | 280.8 | 303.2 | 224 | 360.7 | 272.7
2875.1 | 2639.1 | 280.7 | 303.1 | 223.8 | 360.5 | 272.5
2876.1 | 2640.1 | 280.6 | 303.1 | 223.7 | 360.2 | 272.4
2877.1 | 2641.1 | 280.5 | 302.8 | 223.6 | 359.9 | 272.2
2878.1 | 2642.1 | 280.3 | 302.3 | 223.4 | 359.6 | 272.1
2879.1 | 2643.1 | 280.2 | 301.9 | 223.2 | 359.4 | 271.9
2880.1 | 2644.1 | 280.1 | 301.4 | 223.1 | 359.1 | 271.8
2881.1 | 2645.1 | 280 | 301.2 | 222.9 | 358.9 | 271.6
2882.1 | 2646.1 | 279.9 | 301 | 222.7 | 358.6 | 271.4
2883.1 | 2647.1 | 279.7 | 300.8 | 222.6 | 358.3 | 271.3
2884.1 | 2648.1 | 279.6 | 300.6 | 222.4 | 358.1 | 271.1
2885.1 | 2649.1 | 279.5 | 300.2 | 222.3 | 357.9 | 271
2886.1 | 2650.1 | 279.4 | 300.2 | 222.2 | 357.6 | 270.8
2887.1 | 2651.1 | 279.3 | 299.9 | 221.9 | 357.4 | 270.7
2888.1 | 2652.1 | 279.2 | 299.9 | 221.8 | 357.1 | 270.5
2889.1 | 2653.1 | 279 | 299.4 | 221.7 | 356.9 | 270.4
2890.1 | 2654.1 | 278.9 | 299 | 221.5 | 356.7 | 270.3
2891.1 | 2655.1 | 278.8 | 298.5 | 221.4 | 356.5 | 270.1
2892.1 | 2656.1 | 278.7 | 298.4 | 221.3 | 356.3 | 270
2893.1 | 2657.1 | 278.6 | 298.2 | 221.3 | 356.1 | 269.9
2894.1 | 2658.1 | 278.5 | 298.2 | 221.2 | 355.9 | 269.7
2895.1 | 2659.1 | 278.4 | 298.3 | 221.1 | 355.7 | 269.6
2896.1 | 2660.1 | 278.3 | 298.1 | 221 | 355.5 | 269.5
2897.1 | 2661.1 | 278.2 | 298 | 220.8 | 355.3 | 269.3
2898.1 | 2662.1 | 278.1 | 297.9 | 220.6 | 355.1 | 269.2
2899.1 | 2663.1 | 278 | 297.4 | 220.5 | 354.9 | 269
2900.1 | 2664.1 | 277.9 | 297 | 220.4 | 354.7 | 268.9
2901.1 | 2665.1 | 277.8 | 296.8 | 220.2 | 354.4 | 268.8
2902.1 | 2666.1 | 277.7 | 296.7 | 220 | 354.2 | 268.6
2903.1 | 2667.1 | 277.6 | 296.4 | 219.9 | 354 | 268.5
2904.1 | 2668.1 | 277.5 | 296.2 | 219.8 | 353.8 | 268.3
2905.1 | 2669.1 | 277.4 | 296.2 | 219.7 | 353.5 | 268.2
2906.1 | 2670.1 | 277.3 | 295.9 | 219.5 | 353.3 | 268.1
2907.1 | 2671.1 | 277.2 | 295.9 | 219.4 | 353.1 | 267.9
2908.1 | 2672.1 | 277.1 | 295.8 | 219.2 | 352.9 | 267.8
2909.1 | 2673.1 | 277 | 295.7 | 219.1 | 352.7 | 267.6
2910.1 | 2674.1 | 276.8 | 295.5 | 218.9 | 352.5 | 267.5
2911.1 | 2675.1 | 276.7 | 295.4 | 218.7 | 352.3 | 267.4
2912.1 | 2676.1 | 276.6 | 295 | 218.6 | 352.1 | 267.2
2913.1 | 2677.1 | 276.5 | 294.5 | 218.4 | 351.9 | 267.1
2914.1 | 2678.1 | 276.4 | 294.5 | 218.2 | 351.6 | 267
2915.1 | 2679.1 | 276.3 | 294.4 | 218.2 | 351.4 | 266.8
2916.1 | 2680.1 | 276.2 | 294.6 | 218.1 | 351.2 | 266.7
2917.1 | 2681.1 | 276.1 | 294.4 | 218 | 351 | 266.6
2918.1 | 2682.1 | 276 | 294.4 | 218 | 350.8 | 266.4
2919.1 | 2683.1 | 275.9 | 294.3 | 217.9 | 350.6 | 266.3
2920.1 | 2684.1 | 275.8 | 294.3 | 217.7 | 350.4 | 266.2
2921.1 | 2685.1 | 275.7 | 294.3 | 217.5 | 350.2 | 266.1
2922.1 | 2686.1 | 275.6 | 294.1 | 217.4 | 350 | 265.9
2923.1 | 2687.1 | 275.5 | 294 | 217.3 | 349.8 | 265.8
2924.1 | 2688.1 | 275.4 | 294.1 | 217.2 | 349.6 | 265.6
2925.1 | 2689.1 | 275.3 | 294.1 | 217 | 349.4 | 265.5
2926.1 | 2690.1 | 275.2 | 294.1 | 216.9 | 349.1 | 265.4
2927.1 | 2691.1 | 275.1 | 293.9 | 216.8 | 348.9 | 265.3
2928.1 | 2692.1 | 274.9 | 293.5 | 216.8 | 348.7 | 265.1
2929.1 | 2693.1 | 274.8 | 293.2 | 216.8 | 348.5 | 265
2930.1 | 2694.1 | 274.7 | 293 | 216.8 | 348.3 | 264.9
2931.1 | 2695.1 | 274.6 | 292.8 | 216.7 | 348.1 | 264.7
2932.1 | 2696.1 | 274.5 | 292.7 | 216.6 | 347.9 | 264.6
2933.1 | 2697.1 | 274.4 | 292.5 | 216.5 | 347.7 | 264.4
2934.1 | 2698.1 | 274.3 | 292.5 | 216.4 | 347.5 | 264.3
2935.1 | 2699.1 | 274.2 | 292.5 | 216.3 | 347.3 | 264.2
2936.1 | 2700.1 | 274.1 | 292.5 | 216.1 | 347.1 | 264
2937.1 | 2701.1 | 273.9 | 292.5 | 216 | 346.9 | 263.9
2938.1 | 2702.1 | 273.9 | 292.5 | 215.8 | 346.7 | 263.8
2939.1 | 2703.1 | 273.7 | 292.4 | 215.7 | 346.5 | 263.6
2940.1 | 2704.1 | 273.6 | 292.1 | 215.6 | 346.3 | 263.5
2941.1 | 2705.1 | 273.5 | 291.9 | 215.4 | 346.1 | 263.4
2942.1 | 2706.1 | 273.4 | 291.6 | 215.3 | 345.9 | 263.3
2943.1 | 2707.1 | 273.3 | 291.4 | 215.2 | 345.7 | 263.1
2944.1 | 2708.1 | 273.2 | 291.4 | 215.1 | 345.4 | 263
2945.1 | 2709.1 | 273.1 | 291.4 | 215 | 345.3 | 262.9
2946.1 | 2710.1 | 273 | 291.3 | 214.9 | 345.1 | 262.7
2947.1 | 2711.1 | 272.9 | 291 | 214.7 | 344.8 | 262.6
2948.1 | 2712.1 | 272.8 | 290.8 | 214.6 | 344.6 | 262.5
2949.1 | 2713.1 | 272.7 | 290.6 | 214.4 | 344.4 | 262.4
2950.1 | 2714.1 | 272.6 | 290.6 | 214.3 | 344.2 | 262.2
2951.1 | 2715.1 | 272.5 | 290.5 | 214.2 | 344 | 262.1
2952.1 | 2716.1 | 272.4 | 290.5 | 214 | 343.7 | 262
2953.1 | 2717.1 | 272.2 | 290.5 | 213.9 | 343.6 | 261.8
2954.1 | 2718.1 | 272.1 | 290.3 | 214 | 343.3 | 261.7
2955.1 | 2719.1 | 272 | 290.1 | 214 | 343.1 | 261.6
2956.1 | 2720.1 | 271.9 | 290 | 214 | 342.9 | 261.5
2957.1 | 2721.1 | 271.8 | 290 | 213.9 | 342.7 | 261.4
2958.1 | 2722.1 | 271.7 | 289.8 | 213.8 | 342.5 | 261.2
2959.1 | 2723.1 | 271.6 | 289.6 | 213.6 | 342.3 | 261.1
2960.1 | 2724.1 | 271.5 | 289.4 | 213.5 | 342.1 | 261
2961.1 | 2725.1 | 271.4 | 289.1 | 213.4 | 341.9 | 260.8
2962.1 | 2726.1 | 271.3 | 289 | 213.3 | 341.7 | 260.7
2963.1 | 2727.1 | 271.2 | 288.9 | 213 | 341.5 | 260.6
2964.1 | 2728.1 | 271.1 | 288.7 | 212.9 | 341.3 | 260.4
2965.1 | 2729.1 | 271 | 288.7 | 212.7 | 341.1 | 260.3
2966.1 | 2730.1 | 270.9 | 288.6 | 212.7 | 340.9 | 260.1
2967.1 | 2731.1 | 270.8 | 288.5 | 212.6 | 340.7 | 260
2968.1 | 2732.1 | 270.7 | 288.2 | 212.5 | 340.5 | 259.9
2969.1 | 2733.1 | 270.6 | 287.8 | 212.5 | 340.3 | 259.8
2970.1 | 2734.1 | 270.5 | 287.5 | 212.3 | 340.1 | 259.7
2971.1 | 2735.1 | 270.4 | 287.4 | 212.2 | 339.9 | 259.6
2972.1 | 2736.1 | 270.3 | 287.4 | 212 | 339.7 | 259.4
2973.1 | 2737.1 | 270.2 | 287.3 | 211.8 | 339.5 | 259.3
2974.1 | 2738.1 | 270.1 | 287.3 | 211.6 | 339.2 | 259.2
2975.1 | 2739.1 | 270 | 287.3 | 211.4 | 339 | 259.1
2976.1 | 2740.1 | 269.9 | 287.1 | 211.3 | 338.8 | 259
2977.1 | 2741.1 | 269.8 | 286.8 | 211.2 | 338.6 | 258.8
2978.1 | 2742.1 | 269.7 | 286.6 | 211 | 338.4 | 258.7
2979.1 | 2743.1 | 269.5 | 286.3 | 210.9 | 338.2 | 258.6
2980.1 | 2744.1 | 269.4 | 286.2 | 210.8 | 338 | 258.5
2981.1 | 2745.1 | 269.3 | 285.7 | 210.7 | 337.8 | 258.3
2982.1 | 2746.1 | 269.2 | 285.4 | 210.4 | 337.6 | 258.2
2983.1 | 2747.1 | 269.1 | 285.2 | 210.3 | 337.4 | 258.1
2984.1 | 2748.1 | 269 | 285.1 | 210.3 | 337.2 | 258
2985.1 | 2749.1 | 268.9 | 284.7 | 210.3 | 337 | 257.9
2986.1 | 2750.1 | 268.8 | 284.5 | 210.2 | 336.8 | 257.8
2987.1 | 2751.1 | 268.7 | 284.5 | 210 | 336.6 | 257.7
2988.1 | 2752.1 | 268.6 | 284.3 | 209.9 | 336.4 | 257.5
2989.1 | 2753.1 | 268.5 | 284.3 | 209.8 | 336.2 | 257.4
2990.1 | 2754.1 | 268.4 | 284.1 | 209.5 | 336 | 257.3
2991.1 | 2755.1 | 268.3 | 284 | 209.3 | 335.8 | 257.1
2992.1 | 2756.1 | 268.2 | 283.8 | 209.1 | 335.6 | 257
2993.1 | 2757.1 | 268.1 | 283.7 | 208.9 | 335.4 | 256.9
2994.1 | 2758.1 | 268 | 283.6 | 208.7 | 335.2 | 256.7
2995.1 | 2759.1 | 267.9 | 283.4 | 208.7 | 335 | 256.6
2996.1 | 2760.1 | 267.8 | 283.2 | 208.6 | 334.8 | 256.5
2997.1 | 2761.1 | 267.7 | 283 | 208.3 | 334.6 | 256.3
2998.1 | 2762.1 | 267.6 | 282.8 | 208.1 | 334.4 | 256.2
2999.1 | 2763.1 | 267.5 | 282.6 | 208.1 | 334.2 | 256.1
3000.1 | 2764.1 | 267.4 | 282.4 | 207.9 | 334 | 256
3001.1 | 2765.1 | 267.3 | 282.2 | 207.6 | 333.8 | 255.8
3002.1 | 2766.1 | 267.1 | 282 | 207.5 | 333.6 | 255.7
3003.1 | 2767.1 | 267.1 | 281.9 | 207.5 | 333.4 | 255.6
3004.1 | 2768.1 | 266.9 | 281.7 | 207.6 | 333.2 | 255.5
3005.1 | 2769.1 | 266.8 | 281.5 | 207.5 | 333.1 | 255.4
3006.1 | 2770.1 | 266.7 | 281.2 | 207.4 | 332.9 | 255.3
3007.1 | 2771.1 | 266.6 | 281.1 | 207.2 | 332.7 | 255.1
3008.1 | 2772.1 | 266.5 | 280.9 | 207.1 | 332.5 | 255
3009.1 | 2773.1 | 266.4 | 280.7 | 207 | 332.3 | 254.9
3010.1 | 2774.1 | 266.3 | 280.4 | 206.9 | 332.2 | 254.8
3011.1 | 2775.1 | 266.2 | 280.1 | 206.7 | 332 | 254.7
3012.1 | 2776.1 | 266.1 | 279.9 | 206.6 | 331.8 | 254.6
3013.1 | 2777.1 | 266 | 279.5 | 206.5 | 331.6 | 254.5
3014.1 | 2778.1 | 265.9 | 279.3 | 206.4 | 331.4 | 254.4
3015.1 | 2779.1 | 265.8 | 279.4 | 206.3 | 331.3 | 254.3
3016.1 | 2780.1 | 265.7 | 279.4 | 206.1 | 331.1 | 254.1
3017.1 | 2781.1 | 265.6 | 279.3 | 206 | 330.9 | 254
3018.1 | 2782.1 | 265.5 | 279.3 | 206 | 330.7 | 253.9
3019.1 | 2783.1 | 265.4 | 279.2 | 206.1 | 330.5 | 253.8
3020.1 | 2784.1 | 265.3 | 279 | 205.9 | 330.3 | 253.7
3021.1 | 2785.1 | 265.2 | 278.8 | 205.8 | 330.2 | 253.6
3022.1 | 2786.1 | 265.1 | 278.7 | 205.8 | 330 | 253.5
3023.1 | 2787.1 | 265 | 278.5 | 205.8 | 329.8 | 253.3
3024.1 | 2788.1 | 264.9 | 278.3 | 205.7 | 329.6 | 253.3
3025.1 | 2789.1 | 264.8 | 278.3 | 205.6 | 329.4 | 253.1
3026.1 | 2790.1 | 264.7 | 278.3 | 205.6 | 329.3 | 253
3027.1 | 2791.1 | 264.6 | 278 | 205.7 | 329.1 | 252.9
3028.1 | 2792.1 | 264.5 | 278 | 205.6 | 328.9 | 252.8
3029.1 | 2793.1 | 264.4 | 277.9 | 205.6 | 328.7 | 252.7
3030.1 | 2794.1 | 264.3 | 277.6 | 205.4 | 328.5 | 252.6
3031.1 | 2795.1 | 264.2 | 277.5 | 205.3 | 328.4 | 252.4
3032.1 | 2796.1 | 264.1 | 277.3 | 205.3 | 328.2 | 252.3
3033.1 | 2797.1 | 264 | 277.3 | 205.4 | 328 | 252.2
3034.1 | 2798.1 | 263.9 | 277.3 | 205.3 | 327.8 | 252.1
3035.1 | 2799.1 | 263.8 | 277.1 | 205.2 | 327.7 | 252
3036.1 | 2800.1 | 263.7 | 276.8 | 205.2 | 327.5 | 251.9
3037.1 | 2801.1 | 263.6 | 276.7 | 205.1 | 327.3 | 251.7
3038.1 | 2802.1 | 263.5 | 276.4 | 205 | 327.1 | 251.6
3039.1 | 2803.1 | 263.4 | 276.2 | 205 | 326.9 | 251.5
3040.1 | 2804.1 | 263.3 | 276 | 205.1 | 326.8 | 251.4
3041.1 | 2805.1 | 263.2 | 275.9 | 205.1 | 326.6 | 251.3
3042.1 | 2806.1 | 263.1 | 275.7 | 205 | 326.4 | 251.2
3043.1 | 2807.1 | 263 | 275.4 | 204.9 | 326.2 | 251.1
3044.1 | 2808.1 | 262.9 | 275.1 | 204.8 | 326 | 251
3045.1 | 2809.1 | 262.8 | 275 | 204.8 | 325.9 | 250.9
3046.1 | 2810.1 | 262.7 | 274.7 | 204.8 | 325.7 | 250.8
3047.1 | 2811.1 | 262.6 | 274.6 | 204.8 | 325.5 | 250.6
3048.1 | 2812.1 | 262.5 | 274.5 | 204.7 | 325.3 | 250.5
3049.1 | 2813.1 | 262.4 | 274.3 | 204.6 | 325.2 | 250.4
3050.1 | 2814.1 | 262.2 | 274.1 | 204.5 | 325 | 250.3
3051.1 | 2815.1 | 262.1 | 273.8 | 204.3 | 324.8 | 250.2
3052.1 | 2816.1 | 262 | 273.6 | 204 | 324.6 | 250.1
3053.1 | 2817.1 | 261.9 | 273.3 | 203.8 | 324.4 | 249.9
3054.1 | 2818.1 | 261.8 | 273.2 | 203.8 | 324.3 | 249.8
3055.1 | 2819.1 | 261.7 | 273 | 203.7 | 324.1 | 249.7
3056.1 | 2820.1 | 261.6 | 272.8 | 203.5 | 323.9 | 249.6
3057.1 | 2821.1 | 261.5 | 272.6 | 203.4 | 323.7 | 249.5
3058.1 | 2822.1 | 261.4 | 272.5 | 203.4 | 323.5 | 249.4
3059.1 | 2823.1 | 261.3 | 272.2 | 203.3 | 323.4 | 249.3
3060.1 | 2824.1 | 261.2 | 272.1 | 203.2 | 323.2 | 249.2
3061.1 | 2825.1 | 261.1 | 271.9 | 203.1 | 323 | 249
3062.1 | 2826.1 | 261 | 271.6 | 202.9 | 322.8 | 248.9
3063.1 | 2827.1 | 260.9 | 271.5 | 202.8 | 322.6 | 248.8
3064.1 | 2828.1 | 260.8 | 271.5 | 202.7 | 322.4 | 248.7
3065.1 | 2829.1 | 260.7 | 271.5 | 202.7 | 322.2 | 248.5
3066.1 | 2830.1 | 260.6 | 271.5 | 202.5 | 322.1 | 248.4
3067.1 | 2831.1 | 260.5 | 271.4 | 202.4 | 321.9 | 248.3
3068.1 | 2832.1 | 260.4 | 271.2 | 202.4 | 321.7 | 248.2
3069.1 | 2833.1 | 260.3 | 271 | 202.2 | 321.5 | 248.1
3070.1 | 2834.1 | 260.2 | 270.8 | 202 | 321.4 | 248
3071.1 | 2835.1 | 260.1 | 270.5 | 201.9 | 321.2 | 247.9
3072.1 | 2836.1 | 260 | 270 | 201.7 | 321 | 247.7
3073.1 | 2837.1 | 259.8 | 269.8 | 201.5 | 320.9 | 247.6
3074.1 | 2838.1 | 259.7 | 269.7 | 201.4 | 320.7 | 247.5
3075.1 | 2839.1 | 259.6 | 269.5 | 201.1 | 320.5 | 247.4
3076.1 | 2840.1 | 259.5 | 269.4 | 201 | 320.3 | 247.3
3077.1 | 2841.1 | 259.4 | 269.2 | 201 | 320.1 | 247.2
3078.1 | 2842.1 | 259.3 | 269.1 | 200.9 | 320 | 247.1
3079.1 | 2843.1 | 259.2 | 268.9 | 200.7 | 319.8 | 247
3080.1 | 2844.1 | 259.1 | 268.7 | 200.6 | 319.6 | 246.9
3081.1 | 2845.1 | 259 | 268.5 | 200.5 | 319.5 | 246.8
3082.1 | 2846.1 | 258.9 | 268.3 | 200.3 | 319.3 | 246.7
3083.1 | 2847.1 | 258.8 | 268.1 | 200.2 | 319.1 | 246.6
3084.1 | 2848.1 | 258.7 | 267.9 | 200.2 | 318.9 | 246.4
3085.1 | 2849.1 | 258.6 | 267.7 | 200.1 | 318.8 | 246.3
3086.1 | 2850.1 | 258.5 | 267.5 | 200 | 318.6 | 246.2
3087.1 | 2851.1 | 258.4 | 267.4 | 200 | 318.4 | 246.1
3088.1 | 2852.1 | 258.3 | 267.2 | 199.9 | 318.2 | 246
3089.1 | 2853.1 | 258.2 | 267 | 199.9 | 318.1 | 245.9
3090.1 | 2854.1 | 258.1 | 266.8 | 199.9 | 317.9 | 245.8
3091.1 | 2855.1 | 258 | 266.7 | 199.7 | 317.7 | 245.7
3092.1 | 2856.1 | 257.9 | 266.5 | 199.6 | 317.6 | 245.6
3093.1 | 2857.1 | 257.9 | 266.3 | 199.6 | 317.4 | 245.5
3094.1 | 2858.1 | 257.8 | 266.1 | 199.5 | 317.3 | 245.3
3095.1 | 2859.1 | 257.7 | 265.8 | 199.3 | 317.1 | 245.2
3096.1 | 2860.1 | 257.6 | 265.6 | 199.2 | 316.9 | 245.1
3097.1 | 2861.1 | 257.4 | 265.4 | 199 | 316.8 | 245
3098.1 | 2862.1 | 257.4 | 265.3 | 199 | 316.6 | 244.9
3099.1 | 2863.1 | 257.3 | 265.2 | 198.9 | 316.4 | 244.8
3100.1 | 2864.1 | 257.2 | 265 | 198.8 | 316.3 | 244.7
3101.1 | 2865.1 | 257.1 | 264.9 | 198.7 | 316.1 | 244.6
3102.1 | 2866.1 | 257 | 264.8 | 198.5 | 316 | 244.5
3103.1 | 2867.1 | 256.9 | 264.6 | 198.4 | 315.8 | 244.4
3104.1 | 2868.1 | 256.8 | 264.4 | 198.3 | 315.6 | 244.3
3105.1 | 2869.1 | 256.7 | 264.2 | 198.2 | 315.5 | 244.2
3106.1 | 2870.1 | 256.6 | 264 | 198.1 | 315.3 | 244.1
3107.1 | 2871.1 | 256.5 | 263.8 | 198.2 | 315.1 | 244
3108.1 | 2872.1 | 256.4 | 263.7 | 198.3 | 315 | 243.9
3109.1 | 2873.1 | 256.3 | 263.6 | 198.3 | 314.8 | 243.7
3110.1 | 2874.1 | 256.2 | 263.5 | 198.2 | 314.7 | 243.6
3111.1 | 2875.1 | 256.1 | 263.4 | 198.2 | 314.5 | 243.5
3112.1 | 2876.1 | 256 | 263.3 | 198.3 | 314.4 | 243.4
3113.1 | 2877.1 | 255.9 | 263.2 | 198.3 | 314.2 | 243.3
3114.1 | 2878.1 | 255.9 | 263.2 | 198.2 | 314 | 243.2
3115.1 | 2879.1 | 255.8 | 263.1 | 198 | 313.9 | 243
3116.1 | 2880.1 | 255.7 | 263 | 197.9 | 313.7 | 242.9
3117.1 | 2881.1 | 255.6 | 262.8 | 197.8 | 313.6 | 242.9
3118.1 | 2882.1 | 255.5 | 262.7 | 197.7 | 313.4 | 242.8
3119.1 | 2883.1 | 255.4 | 262.5 | 197.7 | 313.2 | 242.7
3120.1 | 2884.1 | 255.3 | 262.4 | 197.7 | 313.1 | 242.6
3121.1 | 2885.1 | 255.2 | 262.3 | 197.7 | 312.9 | 242.5
3122.1 | 2886.1 | 255.1 | 262.2 | 197.7 | 312.8 | 242.4
3123.1 | 2887.1 | 255 | 262.1 | 197.8 | 312.6 | 242.3
3124.1 | 2888.1 | 254.9 | 262 | 197.7 | 312.5 | 242.2
3125.1 | 2889.1 | 254.8 | 261.9 | 197.7 | 312.3 | 242.1
3126.1 | 2890.1 | 254.7 | 261.8 | 197.6 | 312.1 | 242
3127.1 | 2891.1 | 254.7 | 261.6 | 197.5 | 312 | 241.9
3128.1 | 2892.1 | 254.6 | 261.5 | 197.3 | 311.8 | 241.8
3129.1 | 2893.1 | 254.5 | 261.4 | 197.1 | 311.7 | 241.7
3130.1 | 2894.1 | 254.4 | 261.2 | 197 | 311.5 | 241.6
3131.1 | 2895.1 | 254.3 | 261 | 196.8 | 311.4 | 241.5
3132.1 | 2896.1 | 254.2 | 260.7 | 196.7 | 311.2 | 241.4
3133.1 | 2897.1 | 254.1 | 260.5 | 196.7 | 311.1 | 241.3
3134.1 | 2898.1 | 254 | 260.3 | 196.5 | 310.9 | 241.2
3135.1 | 2899.1 | 253.9 | 260.1 | 196.4 | 310.7 | 241
3136.1 | 2900.1 | 253.8 | 259.9 | 196.2 | 310.6 | 240.9
3137.1 | 2901.1 | 253.7 | 259.7 | 196.1 | 310.4 | 240.8
3138.1 | 2902.1 | 253.6 | 259.6 | 196.1 | 310.3 | 240.7
3139.1 | 2903.1 | 253.5 | 259.5 | 196.1 | 310.1 | 240.6
3140.1 | 2904.1 | 253.4 | 259.4 | 196 | 309.9 | 240.5
3141.1 | 2905.1 | 253.4 | 259.4 | 196 | 309.8 | 240.4
3142.1 | 2906.1 | 253.3 | 259.3 | 195.9 | 309.6 | 240.3
3143.1 | 2907.1 | 253.2 | 259.2 | 195.8 | 309.5 | 240.2
3144.1 | 2908.1 | 253.1 | 259.1 | 195.7 | 309.3 | 240.1
3145.1 | 2909.1 | 253 | 259 | 195.6 | 309.1 | 240
3146.1 | 2910.1 | 252.9 | 258.8 | 195.7 | 309 | 239.9
3147.1 | 2911.1 | 252.8 | 258.7 | 195.6 | 308.8 | 239.8
3148.1 | 2912.1 | 252.7 | 258.5 | 195.5 | 308.7 | 239.7
3149.1 | 2913.1 | 252.6 | 258.4 | 195.4 | 308.5 | 239.6
3150.1 | 2914.1 | 252.5 | 258.2 | 195.3 | 308.4 | 239.5
3151.1 | 2915.1 | 252.4 | 258.1 | 195.2 | 308.2 | 239.4
3152.1 | 2916.1 | 252.3 | 257.9 | 195.1 | 308 | 239.3
3153.1 | 2917.1 | 252.2 | 257.7 | 194.9 | 307.9 | 239.2
3154.1 | 2918.1 | 252.1 | 257.5 | 194.7 | 307.7 | 239.1
3155.1 | 2919.1 | 252.1 | 257.3 | 194.6 | 307.6 | 238.9
3156.1 | 2920.1 | 252 | 257.1 | 194.5 | 307.4 | 238.8
3157.1 | 2921.1 | 251.9 | 256.9 | 194.4 | 307.3 | 238.7
3158.1 | 2922.1 | 251.8 | 256.8 | 194.4 | 307.1 | 238.6
3159.1 | 2923.1 | 251.7 | 256.7 | 194.4 | 307 | 238.5
3160.1 | 2924.1 | 251.6 | 256.5 | 194.3 | 306.8 | 238.4
3161.1 | 2925.1 | 251.5 | 256.4 | 194.2 | 306.7 | 238.3
3162.1 | 2926.1 | 251.4 | 256.4 | 194.1 | 306.5 | 238.2
3163.1 | 2927.1 | 251.3 | 256.2 | 194 | 306.4 | 238.1
3164.1 | 2928.1 | 251.2 | 256.1 | 193.9 | 306.2 | 238
3165.1 | 2929.1 | 251.1 | 255.9 | 193.8 | 306 | 237.9
3166.1 | 2930.1 | 251 | 255.8 | 193.6 | 305.9 | 237.8
3167.1 | 2931.1 | 250.9 | 255.7 | 193.4 | 305.7 | 237.7
3168.1 | 2932.1 | 250.8 | 255.6 | 193.2 | 305.6 | 237.6
3169.1 | 2933.1 | 250.7 | 255.5 | 192.9 | 305.4 | 237.5
3170.1 | 2934.1 | 250.6 | 255.3 | 192.8 | 305.3 | 237.4
3171.1 | 2935.1 | 250.5 | 255.2 | 192.8 | 305.1 | 237.3
3172.1 | 2936.1 | 250.4 | 255.1 | 192.7 | 305 | 237.2
3173.1 | 2937.1 | 250.3 | 254.9 | 192.6 | 304.8 | 237.1
3174.1 | 2938.1 | 250.2 | 254.7 | 192.5 | 304.7 | 237
3175.1 | 2939.1 | 250.1 | 254.5 | 192.4 | 304.5 | 236.9
3176.1 | 2940.1 | 250 | 254.4 | 192.3 | 304.4 | 236.8
3177.1 | 2941.1 | 249.9 | 254.2 | 192.3 | 304.2 | 236.7
3178.1 | 2942.1 | 249.8 | 254.1 | 192.3 | 304.1 | 236.6
3179.1 | 2943.1 | 249.8 | 253.9 | 192.2 | 303.9 | 236.5
3180.1 | 2944.1 | 249.7 | 253.8 | 192.2 | 303.7 | 236.4
3181.1 | 2945.1 | 249.6 | 253.7 | 192.2 | 303.6 | 236.3
3182.1 | 2946.1 | 249.5 | 253.5 | 192 | 303.4 | 236.2
3183.1 | 2947.1 | 249.4 | 253.4 | 191.8 | 303.3 | 236.1
3184.1 | 2948.1 | 249.3 | 253.3 | 191.9 | 303.2 | 236
3185.1 | 2949.1 | 249.2 | 253.1 | 191.8 | 303 | 235.9
3186.1 | 2950.1 | 249.1 | 252.8 | 191.7 | 302.8 | 235.8
3187.1 | 2951.1 | 249 | 252.6 | 191.5 | 302.7 | 235.7
3188.1 | 2952.1 | 248.9 | 252.5 | 191.4 | 302.5 | 235.6
3189.1 | 2953.1 | 248.8 | 252.4 | 191.3 | 302.4 | 235.5
3190.1 | 2954.1 | 248.7 | 252.3 | 191.2 | 302.2 | 235.4
3191.1 | 2955.1 | 248.6 | 252.2 | 191.2 | 302.1 | 235.3
3192.1 | 2956.1 | 248.5 | 252 | 191.1 | 301.9 | 235.2
3193.1 | 2957.1 | 248.5 | 251.9 | 191 | 301.8 | 235.1
3194.1 | 2958.1 | 248.4 | 251.9 | 191 | 301.7 | 235
3195.1 | 2959.1 | 248.3 | 251.8 | 191 | 301.5 | 234.9
3196.1 | 2960.1 | 248.2 | 251.7 | 190.9 | 301.4 | 234.8
3197.1 | 2961.1 | 248.1 | 251.6 | 190.9 | 301.2 | 234.6
3198.1 | 2962.1 | 248 | 251.6 | 190.7 | 301.1 | 234.5
3199.1 | 2963.1 | 247.9 | 251.5 | 190.5 | 300.9 | 234.4
3200.1 | 2964.1 | 247.8 | 251.5 | 190.4 | 300.8 | 234.3
3201.1 | 2965.1 | 247.7 | 251.3 | 190.4 | 300.6 | 234.2
3202.1 | 2966.1 | 247.6 | 251.2 | 190.1 | 300.5 | 234.1
3203.1 | 2967.1 | 247.6 | 251 | 189.9 | 300.3 | 234
3204.1 | 2968.1 | 247.5 | 250.8 | 189.7 | 300.2 | 233.9
3205.1 | 2969.1 | 247.4 | 250.6 | 189.5 | 300 | 233.8
3206.1 | 2970.1 | 247.3 | 250.5 | 189.2 | 299.9 | 233.7
3207.1 | 2971.1 | 247.2 | 250.4 | 189 | 299.8 | 233.6
3208.1 | 2972.1 | 247.1 | 250.2 | 188.9 | 299.6 | 233.5
3209.1 | 2973.1 | 247 | 250 | 188.7 | 299.5 | 233.4
3210.1 | 2974.1 | 246.9 | 250 | 188.5 | 299.3 | 233.3
3211.1 | 2975.1 | 246.8 | 250 | 188.5 | 299.2 | 233.2
3212.1 | 2976.1 | 246.7 | 249.9 | 188.6 | 299.1 | 233.2
3213.1 | 2977.1 | 246.6 | 249.8 | 188.5 | 298.9 | 233.1
3214.1 | 2978.1 | 246.6 | 249.6 | 188.4 | 298.8 | 233
3215.1 | 2979.1 | 246.5 | 249.4 | 188.2 | 298.6 | 232.9
3216.1 | 2980.1 | 246.4 | 249.3 | 188.1 | 298.5 | 232.8
3217.1 | 2981.1 | 246.3 | 249.1 | 187.9 | 298.3 | 232.7
3218.1 | 2982.1 | 246.2 | 249 | 187.8 | 298.2 | 232.6
3219.1 | 2983.1 | 246.1 | 248.8 | 187.7 | 298 | 232.5
3220.1 | 2984.1 | 246 | 248.6 | 187.6 | 297.9 | 232.4
3221.1 | 2985.1 | 245.9 | 248.5 | 187.6 | 297.8 | 232.3
3222.1 | 2986.1 | 245.8 | 248.2 | 187.5 | 297.6 | 232.2
3223.1 | 2987.1 | 245.7 | 248.1 | 187.5 | 297.5 | 232.1
3224.1 | 2988.1 | 245.7 | 248 | 187.4 | 297.3 | 232
3225.1 | 2989.1 | 245.6 | 247.9 | 187.3 | 297.2 | 231.9
3226.1 | 2990.1 | 245.5 | 247.8 | 187.3 | 297 | 231.8
3227.1 | 2991.1 | 245.4 | 247.6 | 187.3 | 296.9 | 231.7
3228.1 | 2992.1 | 245.3 | 247.5 | 187.1 | 296.8 | 231.6
3229.1 | 2993.1 | 245.2 | 247.3 | 187.1 | 296.6 | 231.5
3230.1 | 2994.1 | 245.1 | 247.2 | 187 | 296.5 | 231.4
3231.1 | 2995.1 | 245 | 247.1 | 186.8 | 296.3 | 231.3
3232.1 | 2996.1 | 245 | 247 | 186.7 | 296.2 | 231.2
3233.1 | 2997.1 | 244.9 | 246.9 | 186.6 | 296 | 231.1
3234.1 | 2998.1 | 244.8 | 246.8 | 186.6 | 295.9 | 231
3235.1 | 2999.1 | 244.7 | 246.6 | 186.4 | 295.7 | 230.9
3236.1 | 3000.1 | 244.6 | 246.5 | 186.2 | 295.6 | 230.8
3237.1 | 3001.1 | 244.5 | 246.4 | 186.2 | 295.5 | 230.7
3238.1 | 3002.1 | 244.4 | 246.3 | 186 | 295.3 | 230.6
3239.1 | 3003.1 | 244.3 | 246.1 | 185.8 | 295.2 | 230.5
3240.1 | 3004.1 | 244.3 | 246 | 185.7 | 295 | 230.4
3241.1 | 3005.1 | 244.2 | 245.8 | 185.6 | 294.9 | 230.3
3242.1 | 3006.1 | 244.1 | 245.7 | 185.6 | 294.8 | 230.3
3243.1 | 3007.1 | 244 | 245.5 | 185.6 | 294.6 | 230.2
3244.1 | 3008.1 | 243.9 | 245.5 | 185.4 | 294.5 | 230
3245.1 | 3009.1 | 243.8 | 245.4 | 185.2 | 294.4 | 229.9
3246.1 | 3010.1 | 243.7 | 245.3 | 185.1 | 294.2 | 229.8
3247.1 | 3011.1 | 243.6 | 245.3 | 184.9 | 294.1 | 229.8
3248.1 | 3012.1 | 243.5 | 245.2 | 184.8 | 293.9 | 229.7
3249.1 | 3013.1 | 243.5 | 245.1 | 184.7 | 293.8 | 229.6
3250.1 | 3014.1 | 243.4 | 244.9 | 184.7 | 293.6 | 229.5
3251.1 | 3015.1 | 243.3 | 244.8 | 184.6 | 293.5 | 229.4
3252.1 | 3016.1 | 243.2 | 244.6 | 184.4 | 293.4 | 229.3
3253.1 | 3017.1 | 243.1 | 244.5 | 184.3 | 293.2 | 229.2
3254.1 | 3018.1 | 243 | 244.3 | 184.2 | 293.1 | 229.1
3255.1 | 3019.1 | 242.9 | 244.2 | 184.1 | 292.9 | 229
3256.1 | 3020.1 | 242.9 | 244.1 | 184 | 292.8 | 228.9
3257.1 | 3021.1 | 242.8 | 244.1 | 183.9 | 292.7 | 228.8
3258.1 | 3022.1 | 242.7 | 244 | 183.9 | 292.5 | 228.7
3259.1 | 3023.1 | 242.6 | 243.9 | 183.9 | 292.4 | 228.6
3260.1 | 3024.1 | 242.5 | 243.8 | 183.7 | 292.3 | 228.5
3261.1 | 3025.1 | 242.4 | 243.6 | 183.5 | 292.1 | 228.4
3262.1 | 3026.1 | 242.3 | 243.5 | 183.4 | 292 | 228.3
3263.1 | 3027.1 | 242.3 | 243.4 | 183.3 | 291.8 | 228.2
3264.1 | 3028.1 | 242.2 | 243.2 | 183.3 | 291.7 | 228.1
3265.1 | 3029.1 | 242.1 | 243.1 | 183.2 | 291.6 | 228
3266.1 | 3030.1 | 242 | 243 | 183 | 291.4 | 227.9
3267.1 | 3031.1 | 241.9 | 242.9 | 182.8 | 291.3 | 227.8
3268.1 | 3032.1 | 241.8 | 242.7 | 182.7 | 291.1 | 227.7
3269.1 | 3033.1 | 241.7 | 242.6 | 182.5 | 291 | 227.6
3270.1 | 3034.1 | 241.7 | 242.6 | 182.3 | 290.9 | 227.5
3271.1 | 3035.1 | 241.6 | 242.5 | 182.2 | 290.8 | 227.5
3272.1 | 3036.1 | 241.5 | 242.4 | 182 | 290.6 | 227.4
3273.1 | 3037.1 | 241.4 | 242.4 | 182 | 290.5 | 227.3
3274.1 | 3038.1 | 241.3 | 242.3 | 182 | 290.3 | 227.2
3275.1 | 3039.1 | 241.2 | 242.2 | 182 | 290.2 | 227.1
3276.1 | 3040.1 | 241.1 | 242.1 | 181.9 | 290.1 | 227
3277.1 | 3041.1 | 241.1 | 242 | 181.8 | 289.9 | 226.9
3278.1 | 3042.1 | 241 | 241.8 | 181.8 | 289.8 | 226.8
3279.1 | 3043.1 | 240.9 | 241.6 | 181.7 | 289.7 | 226.7
3280.1 | 3044.1 | 240.8 | 241.5 | 181.5 | 289.5 | 226.6
3281.1 | 3045.1 | 240.7 | 241.4 | 181.3 | 289.4 | 226.5
3282.1 | 3046.1 | 240.6 | 241.3 | 181.2 | 289.2 | 226.4
3283.1 | 3047.1 | 240.5 | 241.2 | 181.1 | 289.1 | 226.3
3284.1 | 3048.1 | 240.4 | 241.1 | 181 | 289 | 226.2
3285.1 | 3049.1 | 240.4 | 241 | 180.8 | 288.8 | 226.1
3286.1 | 3050.1 | 240.3 | 240.8 | 180.7 | 288.7 | 226
3287.1 | 3051.1 | 240.2 | 240.6 | 180.6 | 288.6 | 225.9
3288.1 | 3052.1 | 240.1 | 240.5 | 180.5 | 288.4 | 225.8
3289.1 | 3053.1 | 240 | 240.3 | 180.4 | 288.3 | 225.7
3290.1 | 3054.1 | 239.9 | 240.2 | 180.3 | 288.1 | 225.6
3291.1 | 3055.1 | 239.8 | 239.9 | 180.1 | 288 | 225.5
3292.1 | 3056.1 | 239.7 | 239.8 | 180 | 287.9 | 225.5
3293.1 | 3057.1 | 239.6 | 239.7 | 179.9 | 287.7 | 225.4
3294.1 | 3058.1 | 239.6 | 239.7 | 179.8 | 287.6 | 225.3
3295.1 | 3059.1 | 239.5 | 239.7 | 179.7 | 287.5 | 225.2
3296.1 | 3060.1 | 239.4 | 239.5 | 179.6 | 287.3 | 225.1
3297.1 | 3061.1 | 239.3 | 239.4 | 179.5 | 287.2 | 225
3298.1 | 3062.1 | 239.2 | 239.3 | 179.4 | 287.1 | 224.9
3299.1 | 3063.1 | 239.1 | 239.3 | 179.3 | 286.9 | 224.8
3300.1 | 3064.1 | 239 | 239.2 | 179.2 | 286.8 | 224.7
3301.1 | 3065.1 | 239 | 239.1 | 179.1 | 286.6 | 224.6
3302.1 | 3066.1 | 238.9 | 239 | 178.9 | 286.5 | 224.6
3303.1 | 3067.1 | 238.8 | 238.9 | 178.9 | 286.4 | 224.5
3304.1 | 3068.1 | 238.7 | 238.7 | 178.8 | 286.2 | 224.4
3305.1 | 3069.1 | 238.6 | 238.6 | 178.6 | 286.1 | 224.3
3306.1 | 3070.1 | 238.5 | 238.6 | 178.5 | 286 | 224.2
3307.1 | 3071.1 | 238.4 | 238.4 | 178.4 | 285.8 | 224.1
3308.1 | 3072.1 | 238.3 | 238.3 | 178.3 | 285.7 | 224
3309.1 | 3073.1 | 238.3 | 238.1 | 178.2 | 285.5 | 223.9
3310.1 | 3074.1 | 238.2 | 238 | 178.1 | 285.4 | 223.8
3311.1 | 3075.1 | 238.1 | 237.8 | 177.9 | 285.3 | 223.7
3312.1 | 3076.1 | 238 | 237.8 | 177.8 | 285.1 | 223.6
3313.1 | 3077.1 | 237.9 | 237.7 | 177.7 | 285 | 223.5
3314.1 | 3078.1 | 237.8 | 237.5 | 177.6 | 284.9 | 223.4
3315.1 | 3079.1 | 237.7 | 237.3 | 177.5 | 284.7 | 223.3
3316.1 | 3080.1 | 237.6 | 237.1 | 177.5 | 284.6 | 223.2
3317.1 | 3081.1 | 237.5 | 237 | 177.3 | 284.4 | 223.2
3318.1 | 3082.1 | 237.5 | 236.9 | 177.3 | 284.3 | 223.1
3319.1 | 3083.1 | 237.4 | 236.9 | 177.2 | 284.2 | 223
3320.1 | 3084.1 | 237.3 | 236.8 | 177.1 | 284.1 | 222.9
3321.1 | 3085.1 | 237.2 | 236.7 | 177.1 | 283.9 | 222.8
3322.1 | 3086.1 | 237.1 | 236.7 | 177 | 283.8 | 222.7
3323.1 | 3087.1 | 237 | 236.6 | 176.9 | 283.6 | 222.6
3324.1 | 3088.1 | 236.9 | 236.5 | 177 | 283.5 | 222.5
3325.1 | 3089.1 | 236.9 | 236.4 | 176.9 | 283.4 | 222.4
3326.1 | 3090.1 | 236.8 | 236.2 | 176.8 | 283.3 | 222.3
3327.1 | 3091.1 | 236.7 | 236 | 176.6 | 283.1 | 222.2
3328.1 | 3092.1 | 236.6 | 235.9 | 176.5 | 283 | 222.1
3329.1 | 3093.1 | 236.5 | 235.8 | 176.3 | 282.9 | 222
3330.1 | 3094.1 | 236.4 | 235.6 | 176.1 | 282.7 | 221.9
3331.1 | 3095.1 | 236.3 | 235.4 | 176 | 282.6 | 221.8
3332.1 | 3096.1 | 236.2 | 235.2 | 175.9 | 282.5 | 221.7
3333.1 | 3097.1 | 236.2 | 235.1 | 175.8 | 282.3 | 221.7
3334.1 | 3098.1 | 236.1 | 235.1 | 175.7 | 282.2 | 221.6
3335.1 | 3099.1 | 236 | 234.9 | 175.8 | 282.1 | 221.5
3336.1 | 3100.1 | 235.9 | 234.8 | 175.7 | 282 | 221.4
3337.1 | 3101.1 | 235.8 | 234.7 | 175.6 | 281.8 | 221.3
3338.1 | 3102.1 | 235.7 | 234.5 | 175.5 | 281.7 | 221.2
3339.1 | 3103.1 | 235.6 | 234.4 | 175.3 | 281.5 | 221.1
3340.1 | 3104.1 | 235.5 | 234.2 | 175.2 | 281.4 | 221
3341.1 | 3105.1 | 235.4 | 234.1 | 175.1 | 281.3 | 220.9
3342.1 | 3106.1 | 235.4 | 234.1 | 174.9 | 281.2 | 220.8
3343.1 | 3107.1 | 235.3 | 234 | 174.7 | 281 | 220.7
3344.1 | 3108.1 | 235.2 | 234 | 174.6 | 280.9 | 220.6
3345.1 | 3109.1 | 235.1 | 234 | 174.5 | 280.8 | 220.5
3346.1 | 3110.1 | 235 | 233.8 | 174.4 | 280.6 | 220.4
3347.1 | 3111.1 | 234.9 | 233.7 | 174.3 | 280.5 | 220.3
3348.1 | 3112.1 | 234.8 | 233.5 | 174.3 | 280.4 | 220.2
3349.1 | 3113.1 | 234.8 | 233.4 | 174.2 | 280.3 | 220.1
3350.1 | 3114.1 | 234.7 | 233.3 | 174.1 | 280.1 | 220
3351.1 | 3115.1 | 234.6 | 233.2 | 173.9 | 280 | 219.9
3352.1 | 3116.1 | 234.5 | 233.2 | 173.8 | 279.9 | 219.8
3353.1 | 3117.1 | 234.4 | 233.1 | 173.7 | 279.7 | 219.7
3354.1 | 3118.1 | 234.3 | 233 | 173.6 | 279.6 | 219.6
3355.1 | 3119.1 | 234.2 | 232.8 | 173.5 | 279.5 | 219.5
3356.1 | 3120.1 | 234.1 | 232.8 | 173.4 | 279.4 | 219.5

## Test Facts
Last row in IRMS data sheets: | 82
Time when gas burner was ignited: | 239