## Test Facts
Last row in IRMS data sheets: | 32
Time when Penlight power was initiated: | 92

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 19
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, XLPO jacketed, control cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 92 seconds of baseline data monitoring. Special Note: Test setup included a thermocouple on the inner surface of one center tray rung.
DAQ Time | Penlight Time | Event | Interpretation
92 | 0 | Initated Penlight Heating
1027 | 935 | Conductor 2 shorts to conductor 7 at less than 100 ohms (37) | Initial failure is by conductor to conductor shorting
1036-1039 | 944-947 | Conductor 3 shorts to conductors 6 & 7 (130 & 58)
1045-1048 | 953-956 | Conductor 4 shorts to conductors 6 & 7 (146 & 88)
1050 | 958 | Conductor 5 shorts to conductor 6 at less than 100 ohms (89)
1053-1056 | 961-964 | Conductor 7 shorts to conductors 5 & 6 (135 & 50)
1066 | 974 | Conductor 1 shorts to ground at less than 1000 ohms (309) | First ground short
1070-1073 | 978-981 | Conductor 1 shorts to conductors 6 & 7 (173 & 21)
1076-1084 | 984-992 | Conductor 2 shorts to conductors 3, 4, 5 & 6 at less than 100 ohms (44, 39, 85 & 49)
1077-1090 | 985-998 | Conductors 2, 3 & 4 all short to ground at less than 1000 ohms (338, 784 & 445)
1090-1098 | 998-1006 | Conductor 3 shorts to conductors 4 & 5 at less than 100 ohms (55 & 48); the existing short between conductors 3 & 6 degrades to less than 100 ohms (54)
1098 | 1006 | Conductor 7 shorts to ground at less than 1000 ohms (326)
1101 | 1009 | Conductor 4 shorts to conductor 5 at less than 100 ohms (21)
1104-1112 | 1012-1020 | The existing shorts between conductors 4 & 6 and between conductors 5 & 7 degrade to less than 100 ohms (53, 27)
1118-1126 | 1026-1034 | Conductor 1 shorts to conductors 2, 3, 4 & 5 at less than 100 ohms (1, 67, 34 & 20)
1149-1157 | 1057-1065 | The existing ground faults on conductors 4, 5, 6 & 7 all degrade to less than 100 ohms (67, <1, <1 & 7)
1183-1203 | 1091-1111 | The existing ground faults on conductors 1, 2 & 3 all degrade to less than 100 ohms (7, 1 & <1) | All conductors are shorted to ground
Additional Observations
Observation 1 | The progression of failure modes for this cable followed that expected for a typical thermoset-insulated cable: conductor-to-conductor shorts followed by shorting to ground.
Observation 2 | It took 935 s (15.6 min.) from the start of Penlight heating for the first conductor-to-conductor short to occur, and it took 974 s (16.2 min.) for the first conductor-to-ground short.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 19 |  |  | 2006-07-12 | 9:58
XLPO | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums Overall
-84.6667 | 226938 |  | -73.0833 | 233638 | -65.1667 | 227738 | -59.9167 | 227438 | -56.75 | 226938 | -54.5 | 227438 | -52.0833 | 228138 | -84.6667 | 226938
-25.9167 | 226938 |  | -14.25 | 233638 | -6.3333 | 227738 | -1.3333 | 227438 | 2.0833 | 226938 | 4.5 | 60034.5 | 6.75 | 228138 | -25.9167 | 60034.5
32.75 | 226938 |  | 44.5 | 233638 | 52.3333 | 227738 | 57.5833 | 227438 | 61.1667 | 226938 | 63.1667 | 227438 | 65.6667 | 228138 | 32.75 | 226938
91.5833 | 226938 |  | 103.25 | 127469 | 111.25 | 227738 | 116.3333 | 227438 | 119.6667 | 226938 | 122 | 119619 | 124.25 | 228138 | 91.5833 | 119619
150.4167 | 226938 |  | 162.0833 | 233638 | 169.9167 | 227738 | 175.25 | 227438 | 178.4167 | 226938 | 180.6667 | 227438 | 183.0833 | 228138 | 150.4167 | 226938
209.25 | 226938 |  | 220.9167 | 127469 | 228.75 | 227738 | 233.8333 | 124919 | 237.0833 | 226938 | 239.5 | 227438 | 242 | 124819 | 209.25 | 124819
267.9167 | 226938 |  | 279.6667 | 233638 | 287.5833 | 227738 | 292.5833 | 227438 | 296.0833 | 226938 | 298.25 | 227438 | 300.75 | 228138 | 267.9167 | 226938
326.8333 | 226938 |  | 338.4167 | 233638 | 346.4167 | 227738 | 351.5 | 227438 | 354.75 | 226938 | 357.1667 | 227438 | 359.4167 | 228138 | 326.8333 | 226938
385.5 | 226938 |  | 397.25 | 233638 | 405.1667 | 227738 | 410.3333 | 227438 | 413.5833 | 226938 | 415.8333 | 227438 | 418.1667 | 228138 | 385.5 | 226938
444.4167 | 226938 |  | 456.0833 | 233638 | 464 | 227738 | 469.0833 | 227438 | 472.3333 | 226938 | 474.6667 | 227438 | 477.0833 | 228138 | 444.4167 | 226938
503.0833 | 226938 |  | 515.0833 | 233638 | 522.8333 | 227738 | 527.8333 | 227438 | 531.4167 | 226938 | 533.5833 | 227438 | 535.8333 | 228138 | 503.0833 | 226938
561.8333 | 226938 |  | 573.6667 | 233638 | 581.3333 | 227738 | 586.5833 | 227438 | 590 | 226938 | 592.3333 | 227438 | 594.5833 | 228138 | 561.8333 | 226938
620.8333 | 226938 |  | 632.4167 | 233638 | 640.3333 | 227738 | 645.5 | 227438 | 648.75 | 226938 | 651 | 227438 | 653.3333 | 228138 | 620.8333 | 226938
679.5 | 226938 |  | 691.1667 | 233638 | 699.1667 | 227738 | 704.25 | 227438 | 707.5 | 226938 | 709.8333 | 227438 | 712.0833 | 228138 | 679.5 | 226938
738.3333 | 226938 |  | 750 | 233638 | 757.8333 | 227738 | 763.0833 | 227438 | 766.25 | 226938 | 768.5833 | 227438 | 771.0833 | 228138 | 738.3333 | 226938
797.0833 | 226938 |  | 808.75 | 233638 | 816.75 | 227738 | 821.75 | 227438 | 825.0833 | 113419 | 827.5 | 227438 | 829.75 | 228138 | 797.0833 | 113419
855.9167 | 226938 |  | 867.5833 | 233638 | 875.4167 | 227738 | 880.5833 | 227438 | 884 | 226938 | 886.25 | 113819 | 888.5833 | 228138 | 855.9167 | 113819
914.6667 | 226938 |  | 926.3333 | 2104.3785 | 934.3333 | 1277.6845 | 939.5 | 12108.1981 | 942.6667 | 3932.5842 | 945 | 2485.3741 | 947.3333 | 1742.3909 | 914.6667 | 1277.6845
973.5 | 308.7922 |  | 985.1667 | 338.3587 | 993.1667 | 784.4238 | 998.25 | 445.4784 | 1001.5 | 2269.7587 | 1003.8333 | 4801.4761 | 1006.0833 | 326.0257 | 973.5 | 308.7922
1032.3333 | 264.989 |  | 1044 | 263.8976 | 1051.8333 | 653.0761 | 1057.0833 | 67.3684 | 1060.25 | 0.68463 | 1062.5833 | 0.69852 | 1065.0833 | 7.1888 | 1032.3333 | 0.68463
1091.0833 | 7.3598 |  | 1102.75 | 1.0459 | 1110.75 | 0.74455 | 1115.75 | 0.66169 | 1119.0833 | 0.69085 | 1121.5 | 0.73541 | 1123.75 | 0.65814 | 1091.0833 | 0.65814
1149.9167 | 0.70088 |  | 1161.5 | 0.66839 | 1169.4167 | 0.64731 | 1174.5833 | 0.68867 | 1178 | 4.4954 | 1180.25 | 0.6532 | 1182.5 | 11.7015 | 1149.9167 | 0.64731
1208.6667 | 45.2212 |  | 1220.3333 | 40.3814 | 1228.3333 | 1.0937 | 1233.4167 | 1.0931 | 1236.6667 | 30.3635 | 1239 | 2.1679 | 1241.25 | 2.1651 | 1208.6667 | 1.0931
1267.5 | 43.5538 |  | 1279.1667 | 10.0697 | 1287.1667 | 50.1587 | 1292.25 | 297.3023 | 1295.4167 | 8.1886 | 1297.75 | 12.3205 | 1300.0833 | 191.5884 | 1267.5 | 8.1886
1326.3333 | 92.1231 |  | 1337.9167 | 37.5315 | 1345.75 | 0.18698 | 1351 | 5.2786 | 1354.1667 | 0.13056 | 1356.5 | 0.47328 | 1359 | 20.921 | 1326.3333 | 0.13056
1385 | 34.3031 |  | 1396.6667 | 13.0397 | 1404.75 | 23.1555 | 1409.6667 | 13.3105 | 1413 | 1.1889 | 1415.25 | 26.3164 | 1417.6667 | 2.3068 | 1385 | 1.1889
1443.8333 | 14.2803 |  | 1455.5833 | 31.3758 | 1463.4167 | 12.2574 | 1468.5 | 19.3475 | 1471.9167 | 33.4488 | 1474.25 | 14.296 | 1476.5 | 28.6138 | 1443.8333 | 12.2574
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 19 |  |  | 2006-07-12 | 9:58
XLPO | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-84.6667 | 238921.3333 |  | -73.0833 | 244454.6667 | -65.1667 | 243654.6667 | -59.9167 | 238421.3333 | -56.75 | 244071.3333 | -54.5 | 240271.3333 | -52.0833 | 243938 | -84.6667 | 238421.3333
-25.9167 | 238921.3333 |  | -14.25 | 244454.6667 | -6.3333 | 243654.6667 | -1.3333 | 238421.3333 | 2.0833 | 244071.3333 | 4.5 | 210204.0833 | 6.75 | 243938 | -25.9167 | 210204.0833
32.75 | 238921.3333 |  | 44.5 | 244454.6667 | 52.3333 | 243654.6667 | 57.5833 | 238421.3333 | 61.1667 | 244071.3333 | 63.1667 | 240271.3333 | 65.6667 | 243938 | 32.75 | 238421.3333
91.5833 | 238921.3333 |  | 103.25 | 223193.1667 | 111.25 | 243654.6667 | 116.3333 | 238421.3333 | 119.6667 | 244071.3333 | 122 | 220318.1667 | 124.25 | 243938 | 91.5833 | 220318.1667
150.4167 | 238921.3333 |  | 162.0833 | 244454.6667 | 169.9167 | 243654.6667 | 175.25 | 238421.3333 | 178.4167 | 244071.3333 | 180.6667 | 240271.3333 | 183.0833 | 243938 | 150.4167 | 238421.3333
209.25 | 238921.3333 |  | 220.9167 | 223193.1667 | 228.75 | 243654.6667 | 233.8333 | 217584.8333 | 237.0833 | 244071.3333 | 239.5 | 240271.3333 | 242 | 223118.1667 | 209.25 | 217584.8333
267.9167 | 238921.3333 |  | 279.6667 | 244454.6667 | 287.5833 | 243654.6667 | 292.5833 | 238421.3333 | 296.0833 | 244071.3333 | 298.25 | 240271.3333 | 300.75 | 243938 | 267.9167 | 238421.3333
326.8333 | 238921.3333 |  | 338.4167 | 244454.6667 | 346.4167 | 243654.6667 | 351.5 | 238421.3333 | 354.75 | 244071.3333 | 357.1667 | 240271.3333 | 359.4167 | 243938 | 326.8333 | 238421.3333
385.5 | 238921.3333 |  | 397.25 | 244454.6667 | 405.1667 | 243654.6667 | 410.3333 | 238421.3333 | 413.5833 | 244071.3333 | 415.8333 | 240271.3333 | 418.1667 | 243938 | 385.5 | 238421.3333
444.4167 | 238921.3333 |  | 456.0833 | 244454.6667 | 464 | 243654.6667 | 469.0833 | 238421.3333 | 472.3333 | 244071.3333 | 474.6667 | 240271.3333 | 477.0833 | 243938 | 444.4167 | 238421.3333
503.0833 | 238921.3333 |  | 515.0833 | 244454.6667 | 522.8333 | 243654.6667 | 527.8333 | 238421.3333 | 531.4167 | 244071.3333 | 533.5833 | 240271.3333 | 535.8333 | 243938 | 503.0833 | 238421.3333
561.8333 | 238921.3333 |  | 573.6667 | 244454.6667 | 581.3333 | 243654.6667 | 586.5833 | 238421.3333 | 590 | 244071.3333 | 592.3333 | 240271.3333 | 594.5833 | 243938 | 561.8333 | 238421.3333
620.8333 | 238921.3333 |  | 632.4167 | 244454.6667 | 640.3333 | 243654.6667 | 645.5 | 238421.3333 | 648.75 | 244071.3333 | 651 | 240271.3333 | 653.3333 | 243938 | 620.8333 | 238421.3333
679.5 | 238921.3333 |  | 691.1667 | 244454.6667 | 699.1667 | 243654.6667 | 704.25 | 238421.3333 | 707.5 | 244071.3333 | 709.8333 | 240271.3333 | 712.0833 | 243938 | 679.5 | 238421.3333
738.3333 | 238921.3333 |  | 750 | 244454.6667 | 757.8333 | 243654.6667 | 763.0833 | 238421.3333 | 766.25 | 244071.3333 | 768.5833 | 240271.3333 | 771.0833 | 243938 | 738.3333 | 238421.3333
797.0833 | 238921.3333 |  | 808.75 | 244454.6667 | 816.75 | 243654.6667 | 821.75 | 238421.3333 | 825.0833 | 225151.5 | 827.5 | 240271.3333 | 829.75 | 243938 | 797.0833 | 225151.5
855.9167 | 238921.3333 |  | 867.5833 | 244454.6667 | 875.4167 | 243654.6667 | 880.5833 | 238421.3333 | 884 | 244071.3333 | 886.25 | 221284.8333 | 888.5833 | 243938 | 855.9167 | 221284.8333
914.6667 | 238921.3333 |  | 926.3333 | 203615.7297 | 934.3333 | 99140.4032 | 939.5 | 243534.8587 | 942.6667 | 105154.6051 | 945 | 66406.7409 | 947.3333 | 43045.6498 | 914.6667 | 43045.6498
973.5 | 45595765.1023 |  | 985.1667 | 13809.5476 | 993.1667 | 18008780.7808 | 998.25 | 42129.1904 | 1001.5 | 25773.0898 | 1003.8333 | 17373.1672 | 1006.0833 | 4460.9549 | 973.5 | 4460.9549
1032.3333 | 34449.4535 |  | 1044 | 54970.5338 | 1051.8333 | 6746.7163 | 1057.0833 | 12062.5936 | 1060.25 | 4029.9265 | 1062.5833 | 1874.7594 | 1065.0833 | 1184.5816 | 1032.3333 | 1184.5816
1091.0833 | 27.061 |  | 1102.75 | 6.7772 | 1110.75 | 9.4052 | 1115.75 | 5.4681 | 1119.0833 | 13.63 | 1121.5 | 9.192 | 1123.75 | 5.3653 | 1091.0833 | 5.3653
1149.9167 | 11.7139 |  | 1161.5 | 15.5809 | 1169.4167 | 5.3465 | 1174.5833 | 15.3914 | 1178 | 27.1803 | 1180.25 | 68.241 | 1182.5 | 57.0459 | 1149.9167 | 5.3465
1208.6667 | 63.3313 |  | 1220.3333 | 104.4806 | 1228.3333 | 36.6415 | 1233.4167 | 114.9005 | 1236.6667 | 314.5333 | 1239 | 111.5739 | 1241.25 | 95.4152 | 1208.6667 | 36.6415
1267.5 | 163.8825 |  | 1279.1667 | 395.8819 | 1287.1667 | 921.8775 | 1292.25 | 2278.2465 | 1295.4167 | 315.2381 | 1297.75 | 416.6743 | 1300.0833 | 546.9458 | 1267.5 | 163.8825
1326.3333 | 1645.1381 |  | 1337.9167 | 438.3616 | 1345.75 | 224.3571 | 1351 | 327.7024 | 1354.1667 | 34.4953 | 1356.5 | 509.2486 | 1359 | 1402.9135 | 1326.3333 | 34.4953
1385 | 378.5435 |  | 1396.6667 | 551.4206 | 1404.75 | 396.4929 | 1409.6667 | 98.9532 | 1413 | 42.9891 | 1415.25 | 42.0653 | 1417.6667 | 655.8297 | 1385 | 42.0653
1443.8333 | 33.6963 |  | 1455.5833 | 408.9053 | 1463.4167 | 577.3594 | 1468.5 | 1003.1199 | 1471.9167 | 1718.3896 | 1474.25 | 4073.8084 | 1476.5 | 58923.0672 | 1443.8333 | 33.6963
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 19 |  |  | 2006-07-12 | 9:58
XLPO | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-91.5 | 236537.9994 | -89 | 254737.9994 | -86 | 233837.9994 | -83.5 | 226937.9994 | -80.5 | 253337.9994 | -77.5 | 228137.9994 | -75 | 255037.9994 | -72 | 233637.9994 | -69.5 | 253937.9994 | -66.5 | 240437.9994 | -64 | 247137.9994 | -61 | 240137.9994 | -58 | 244537.9994 | -55.5 | 227737.9994 | -52.5 | 239737.9994 | -49.5 | 249937.9994 | -47 | 227437.9994 | -44 | 245537.9994 | -41.5 | 239337.9994 | -38.5 | 249737.9994 | -36 | 253337.9994 | -91.5 | 226937.9994
-33 | 236537.9994 | -30 | 254737.9994 | -27.5 | 233837.9994 | -24.5 | 226937.9994 | -21.5 | 253337.9994 | -19 | 228137.9994 | -16 | 255037.9994 | -13.5 | 233637.9994 | -10.5 | 253937.9994 | -7.5 | 240437.9994 | -5 | 247137.9994 | -2.5 | 240137.9994 | 0.5 | 244537.9994 | 3.5 | 227737.9994 | 6.5 | 239737.9994 | 9 | 249937.9994 | 12 | 227437.9994 | 14.5 | 245537.9994 | 17.5 | 239337.9994 | 20.5 | 249737.9994 | 23 | 253337.9994 | -33 | 226937.9994
25.5 | 236537.9994 | 28.5 | 254737.9994 | 31.5 | 233837.9994 | 34.5 | 226937.9994 | 37 | 253337.9994 | 39.5 | 228137.9994 | 42.5 | 255037.9994 | 45.5 | 233637.9994 | 48.5 | 253937.9994 | 51 | 240437.9994 | 54 | 247137.9994 | 56.5 | 240137.9994 | 59.5 | 244537.9994 | 62 | 227737.9994 | 65 | 239737.9994 | 68 | 249937.9994 | 70.5 | 227437.9994 | 73.5 | 245537.9994 | 76.5 | 239337.9994 | 80 | 249737.9994 | 82 | 253337.9994 | 25.5 | 226937.9994
84.5 | 236537.9994 | 87.5 | 254737.9994 | 90 | 233837.9994 | 93 | 226937.9994 | 96 | 253337.9994 | 98.5 | 228137.9994 | 101.5 | 127468.9988 | 104 | 233637.9994 | 107 | 253937.9994 | 110 | 240437.9994 | 112.5 | 247137.9994 | 115.5 | 240137.9994 | 118.5 | 244537.9994 | 121 | 227737.9994 | 123.5 | 239737.9994 | 126.5 | 249937.9994 | 129.5 | 227437.9994 | 132.5 | 245537.9994 | 135 | 239337.9994 | 138 | 249737.9994 | 140.5 | 253337.9994 | 84.5 | 127468.9988
143.5 | 236537.9994 | 146 | 254737.9994 | 149 | 233837.9994 | 152 | 226937.9994 | 154.5 | 253337.9994 | 157.5 | 228137.9994 | 160 | 255037.9994 | 163 | 233637.9994 | 166 | 253937.9994 | 168.5 | 240437.9994 | 171.5 | 247137.9994 | 174.5 | 240137.9994 | 177 | 244537.9994 | 179.5 | 227737.9994 | 182.5 | 239737.9994 | 185.5 | 249937.9994 | 188.5 | 227437.9994 | 191 | 245537.9994 | 193.5 | 239337.9994 | 196.5 | 249737.9994 | 199.5 | 253337.9994 | 143.5 | 226937.9994
202.5 | 236537.9994 | 205 | 254737.9994 | 207.5 | 233837.9994 | 210.5 | 226937.9994 | 213.5 | 253337.9994 | 216.5 | 228137.9994 | 219 | 127468.9988 | 221.5 | 233637.9994 | 224.5 | 253937.9994 | 227.5 | 240437.9994 | 230.5 | 247137.9994 | 233 | 240137.9994 | 235.5 | 244537.9994 | 238.5 | 227737.9994 | 241.5 | 239737.9994 | 244 | 124918.9988 | 247 | 227437.9994 | 250 | 245537.9994 | 252.5 | 239337.9994 | 255.5 | 249737.9994 | 258 | 253337.9994 | 202.5 | 124918.9988
261 | 236537.9994 | 263.5 | 254737.9994 | 266.5 | 233837.9994 | 269.5 | 226937.9994 | 272 | 253337.9994 | 275 | 228137.9994 | 278 | 255037.9994 | 280.5 | 233637.9994 | 283.5 | 253937.9994 | 286 | 240437.9994 | 289 | 247137.9994 | 291.5 | 240137.9994 | 294.5 | 244537.9994 | 297.5 | 227737.9994 | 300.5 | 239737.9994 | 303 | 249937.9994 | 305.5 | 227437.9994 | 308.5 | 245537.9994 | 311.5 | 239337.9994 | 314.5 | 249737.9994 | 317 | 253337.9994 | 261 | 226937.9994
320 | 236537.9994 | 322.5 | 254737.9994 | 325.5 | 233837.9994 | 328 | 226937.9994 | 331 | 253337.9994 | 334 | 228137.9994 | 336.5 | 255037.9994 | 339.5 | 233637.9994 | 342 | 253937.9994 | 345 | 240437.9994 | 347.5 | 247137.9994 | 350.5 | 240137.9994 | 353.5 | 244537.9994 | 356.5 | 227737.9994 | 359 | 239737.9994 | 361.5 | 249937.9994 | 364.5 | 227437.9994 | 367.5 | 245537.9994 | 370.5 | 239337.9994 | 373 | 249737.9994 | 375.5 | 253337.9994 | 320 | 226937.9994
378.5 | 236537.9994 | 381.5 | 254737.9994 | 384 | 233837.9994 | 387 | 226937.9994 | 389.5 | 253337.9994 | 392.5 | 228137.9994 | 395.5 | 255037.9994 | 398.5 | 233637.9994 | 401 | 253937.9994 | 403.5 | 240437.9994 | 406.5 | 247137.9994 | 409.5 | 240137.9994 | 412 | 244537.9994 | 415 | 227737.9994 | 417.5 | 239737.9994 | 420.5 | 249937.9994 | 423.5 | 227437.9994 | 426 | 245537.9994 | 429 | 239337.9994 | 432 | 249737.9994 | 434.5 | 253337.9994 | 378.5 | 226937.9994
437.5 | 236537.9994 | 440.5 | 254737.9994 | 443 | 233837.9994 | 445.5 | 226937.9994 | 448.5 | 253337.9994 | 451.5 | 228137.9994 | 454.5 | 255037.9994 | 457 | 233637.9994 | 459.5 | 253937.9994 | 462.5 | 240437.9994 | 465.5 | 247137.9994 | 468 | 240137.9994 | 471 | 244537.9994 | 473.5 | 227737.9994 | 476.5 | 239737.9994 | 479.5 | 249937.9994 | 482 | 227437.9994 | 485 | 245537.9994 | 488 | 239337.9994 | 490.5 | 249737.9994 | 493.5 | 253337.9994 | 437.5 | 226937.9994
496 | 236537.9994 | 499 | 254737.9994 | 501.5 | 233837.9994 | 504.5 | 226937.9994 | 507.5 | 253337.9994 | 510 | 228137.9994 | 513 | 255037.9994 | 516 | 233637.9994 | 520 | 253937.9994 | 521.5 | 240437.9994 | 524 | 247137.9994 | 527 | 240137.9994 | 530 | 244537.9994 | 532.5 | 227737.9994 | 535.5 | 239737.9994 | 538 | 249937.9994 | 541 | 227437.9994 | 543.5 | 245537.9994 | 546.5 | 239337.9994 | 549.5 | 249737.9994 | 552.5 | 253337.9994 | 496 | 226937.9994
555 | 236537.9994 | 557 | 254737.9994 | 560.5 | 233837.9994 | 563.5 | 226937.9994 | 566 | 253337.9994 | 569 | 228137.9994 | 571.5 | 255037.9994 | 574.5 | 233637.9994 | 577.5 | 253937.9994 | 580.5 | 240437.9994 | 583 | 247137.9994 | 585.5 | 240137.9994 | 588.5 | 244537.9994 | 591.5 | 227737.9994 | 594 | 239737.9994 | 597 | 249937.9994 | 599.5 | 227437.9994 | 602.5 | 245537.9994 | 605.5 | 239337.9994 | 608 | 249737.9994 | 611 | 253337.9994 | 555 | 226937.9994
614 | 236537.9994 | 616.5 | 254737.9994 | 619.5 | 233837.9994 | 622.5 | 226937.9994 | 625 | 253337.9994 | 627.5 | 228137.9994 | 630.5 | 255037.9994 | 633.5 | 233637.9994 | 636 | 253937.9994 | 639 | 240437.9994 | 641.5 | 247137.9994 | 644.5 | 240137.9994 | 647.5 | 244537.9994 | 650 | 227737.9994 | 653 | 239737.9994 | 655.5 | 249937.9994 | 658.5 | 227437.9994 | 661.5 | 245537.9994 | 664 | 239337.9994 | 667 | 249737.9994 | 669.5 | 253337.9994 | 614 | 226937.9994
672.5 | 236537.9994 | 675.5 | 254737.9994 | 678 | 233837.9994 | 681 | 226937.9994 | 683.5 | 253337.9994 | 686.5 | 228137.9994 | 689.5 | 255037.9994 | 692 | 233637.9994 | 695 | 253937.9994 | 697.5 | 240437.9994 | 700.5 | 247137.9994 | 703.5 | 240137.9994 | 706 | 244537.9994 | 709 | 227737.9994 | 711.5 | 239737.9994 | 714.5 | 249937.9994 | 717.5 | 227437.9994 | 720 | 245537.9994 | 723 | 239337.9994 | 725.5 | 249737.9994 | 728.5 | 253337.9994 | 672.5 | 226937.9994
731.5 | 236537.9994 | 734 | 254737.9994 | 737 | 233837.9994 | 739.5 | 226937.9994 | 742.5 | 253337.9994 | 745.5 | 228137.9994 | 748 | 255037.9994 | 751 | 233637.9994 | 753.5 | 253937.9994 | 756.5 | 240437.9994 | 759.5 | 247137.9994 | 762 | 240137.9994 | 765 | 244537.9994 | 767.5 | 227737.9994 | 770.5 | 239737.9994 | 773.5 | 249937.9994 | 776 | 227437.9994 | 779 | 245537.9994 | 781.5 | 239337.9994 | 784.5 | 249737.9994 | 787.5 | 253337.9994 | 731.5 | 226937.9994
790 | 236537.9994 | 793 | 254737.9994 | 795.5 | 233837.9994 | 798.5 | 226937.9994 | 801.5 | 253337.9994 | 804 | 228137.9994 | 807 | 255037.9994 | 809.5 | 233637.9994 | 812.5 | 253937.9994 | 815.5 | 240437.9994 | 818 | 247137.9994 | 821 | 240137.9994 | 823.5 | 244537.9994 | 826.5 | 227737.9994 | 829.5 | 239737.9994 | 832 | 249937.9994 | 835 | 227437.9994 | 837.5 | 245537.9994 | 840.5 | 239337.9994 | 843.5 | 249737.9994 | 846 | 253337.9994 | 790 | 226937.9994
849 | 236537.9994 | 851.5 | 254737.9994 | 854.5 | 233837.9994 | 857.5 | 226937.9994 | 860 | 253337.9994 | 863 | 228137.9994 | 865.5 | 255037.9994 | 868.5 | 233637.9994 | 871.5 | 253937.9994 | 874 | 240437.9994 | 877 | 247137.9994 | 879.5 | 240137.9994 | 882.5 | 244537.9994 | 885.5 | 227737.9994 | 888 | 239737.9994 | 891 | 249937.9994 | 893.5 | 227437.9994 | 896.5 | 245537.9994 | 899.5 | 239337.9994 | 902 | 249737.9994 | 905 | 253337.9994 | 849 | 226937.9994
907.5 | 236537.9994 | 910.5 | 254737.9994 | 913.5 | 233837.9994 | 916 | 226937.9994 | 919 | 253337.9994 | 921.5 | 228137.9994 | 924.5 | 255037.9994 | 927.5 | 233637.9994 | 930 | 253937.9994 | 933 | 240437.9994 | 935.5 | 37.0374 | 938.5 | 59884.5728 | 941.5 | 121919.2453 | 944 | 129.5641 | 947 | 58.2071 | 949.5 | 2130.0084 | 952.5 | 145.6059 | 955.5 | 87.5185 | 958 | 89.4119 | 961 | 134.9884 | 963.5 | 49.9453 | 907.5 | 37.0374
966.5 | 26126.8839 | 969.5 | 63559.4412 | 972 | 116719.0641 | 975 | 226537.1963 | 977.5 | 172.8958 | 980.5 | 21.3621 | 983.5 | 43.9127 | 986 | 38.8043 | 989 | 85.3159 | 991.5 | 48.6968 | 994.5 | 49.0038 | 997.5 | 54.7406 | 1000 | 47.9778 | 1003 | 54.4553 | 1005.5 | 16.5462 | 1008.5 | 21.3095 | 1011.5 | 52.6653 | 1014 | 11.71 | 1017 | 60.6159 | 1019.5 | 27.0498 | 1022.5 | 74.5182 | 966.5 | 11.71
1025.5 | 1.4516 | 1028 | 67.3497 | 1031 | 33.5329 | 1033.5 | 20.4972 | 1036.5 | 40.0217 | 1039.5 | 5.7462 | 1042 | 672.5616 | 1045 | 16.4669 | 1047.5 | 35.6734 | 1050.5 | 49.2825 | 1053.5 | 36.7973 | 1056 | 44.2066 | 1059 | 52.8772 | 1061.5 | 23.573 | 1064.5 | 235.5548 | 1067.5 | 29.712 | 1070 | 21.4382 | 1073 | 18.2267 | 1075.5 | 28.3793 | 1078.5 | 11.6026 | 1081.5 | 1405.4046 | 1025.5 | 1.4516
1084 | 1275.4004 | 1087 | 829.8892 | 1089.5 | 4804.3405 | 1092.5 | 237.1573 | 1095.5 | 1318.4816 | 1098 | 475.5289 | 1101 | 1727.0314 | 1103.5 | 13.0725 | 1106.5 | 5.8971 | 1109.5 | 96.0262 | 1112 | 109.8486 | 1115 | 966.4538 | 1117.5 | 328.4846 | 1120.5 | 1129.5369 | 1123.5 | 7.9004 | 1126 | 168.7328 | 1129 | 45.4013 | 1131.5 | 12.8257 | 1134.5 | 1663.3351 | 1137.5 | 501.0644 | 1140 | 24.3163 | 1084 | 5.8971
1143 | 111.0766 | 1145.5 | 137.9159 | 1148.5 | 257.8916 | 1151.5 | 1417.0053 | 1154 | 148.8579 | 1157 | 3481.8972 | 1159.5 | 339.1837 | 1162.5 | 6092.7904 | 1165.5 | 4437.2938 | 1168 | 164.3318 | 1170.5 | 288.4073 | 1173.5 | 205.4464 | 1176.5 | 341.02 | 1179.5 | 224.0489 | 1182 | 546.7188 | 1185 | 251.3728 | 1187.5 | 50.1236 | 1190.5 | 32.0645 | 1193.5 | 45.5634 | 1196 | 38.674 | 1199 | 136.6725 | 1143 | 32.0645
1201.5 | 24.9791 | 1204.5 | 16.9158 | 1207.5 | 26.6318 | 1210 | 5.7573 | 1213 | 27.9758 | 1215.5 | 17.923 | 1218.5 | 19.8058 | 1221.5 | 68.8208 | 1224 | 45.4916 | 1227 | 70.8784 | 1229.5 | 64.9273 | 1232.5 | 19.2729 | 1235.5 | 18.7677 | 1238 | 6.78 | 1241 | 0.96235 | 1243.5 | 59.1211 | 1246.5 | 0.99306 | 1249 | 71.7681 | 1252 | 9.8846 | 1255 | 6.5569 | 1257.5 | 49.6755 | 1201.5 | 0.96235
1260.5 | 3.4609 | 1263.5 | 14.2104 | 1266 | 38.7569 | 1269 | 3.5611 | 1271.5 | 9.3879 | 1274.5 | 18.5431 | 1277.5 | 59.8312 | 1280 | 10.7733 | 1283 | 2.1645 | 1285.5 | 5.2627 | 1288.5 | 31.3004 | 1291.5 | 20.0576 | 1294 | 8.3692 | 1297 | 27.2296 | 1299.5 | 5.2677 | 1302.5 | 56.3016 | 1305.5 | 2.2667 | 1308 | 25.4003 | 1310.5 | 32.6482 | 1313.5 | 6.7478 | 1316.5 | 49.9628 | 1260.5 | 2.1645
1319.5 | 9.5813 | 1322 | 58.4208 | 1325 | 18.1739 | 1327.5 | 4.2795 | 1330.5 | 32.9682 | 1333.5 | 15.443 | 1336 | 75.5746 | 1338.5 | 28.6978 | 1341.5 | 18.6639 | 1344.5 | 20.6592 | 1347.5 | 13.0688 | 1350 | 0.17848 | 1352.5 | 0.056509 | 1355.5 | 0.028567 | 1358.5 | 6.7556 | 1361.5 | 16.4541 | 1364 | 1.119 | 1367 | 48.6231 | 1369.5 | 2.0889 | 1372.5 | 2.1769 | 1375 | 7.3762 | 1319.5 | 0.028567
1378 | 3.3443 | 1381 | 22.8926 | 1383.5 | 46.6888 | 1386.5 | 17.8506 | 1389 | 33.3507 | 1392 | 16.5776 | 1395 | 22.4556 | 1397.5 | 9.2255 | 1400.5 | 21.3896 | 1403 | 5.6733 | 1406 | 20.5858 | 1409 | 9.4679 | 1411.5 | 32.6455 | 1414.5 | 8.8865 | 1417.5 | 37.1682 | 1420 | 7.6715 | 1422.5 | 5.9064 | 1425.5 | 32.6364 | 1428.5 | 8.3089 | 1431 | 0.96976 | 1434 | 12.5235 | 1378 | 0.96976
1437 | 1.7332 | 1439.5 | 6.3255 | 1442.5 | 7.1837 | 1445 | 1.6244 | 1448 | 4.855 | 1451 | 44.6115 | 1453.5 | 9.8512 | 1456.5 | 39.2915 | 1460 | 62.2924 | 1462 | 9.2914 | 1464.5 | 53.409 | 1467.5 | 58.3319 | 1470.5 | 36.6687 | 1473.5 | 38.6235 | 1476 | 10.7478 | 1478.5 | 15.8779 | 1481.5 | 41.8153 | 1484.5 | 28.2365 | 1487.5 | 52.9488 | 1490 | 36.2549 | 1493 | 62.2253 | 1437 | 1.6244
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -92 | 38.069 | 33.5268 | 33.4902 | 33.3822 | 33.5912 | 31.2299 | 30.5583 | 34.7565
0.6309 | -91.3691 | 38.0609 | 33.5254 | 33.4832 | 33.3794 | 33.5851 | 31.2267 | 30.5583 | 34.7528
1.5122 | -90.4878 | 38.0561 | 33.5192 | 33.4842 | 33.3771 | 33.5851 | 31.2288 | 30.5593 | 34.7521
2.5136 | -89.4864 | 38.058 | 33.5192 | 33.4926 | 33.3783 | 33.5889 | 31.2216 | 30.555 | 34.7442
3.505 | -88.495 | 38.0459 | 33.5227 | 33.4921 | 33.3747 | 33.58 | 31.2267 | 30.5534 | 34.7444
4.5065 | -87.4935 | 38.0399 | 33.5193 | 33.4887 | 33.3796 | 33.581 | 31.2301 | 30.5575 | 34.7471
5.5079 | -86.4921 | 38.0473 | 33.5237 | 33.4828 | 33.3804 | 33.5852 | 31.2284 | 30.5553 | 34.7426
6.5094 | -85.4906 | 38.04 | 33.5249 | 33.491 | 33.3804 | 33.5899 | 31.2294 | 30.5539 | 34.7295
7.5108 | -84.4892 | 38.0415 | 33.5164 | 33.4847 | 33.3809 | 33.5794 | 31.2176 | 30.549 | 34.7335
8.5122 | -83.4878 | 38.0355 | 33.5177 | 33.4841 | 33.378 | 33.5888 | 31.2158 | 30.5486 | 34.7336
9.5137 | -82.4863 | 38.0284 | 33.5227 | 33.4938 | 33.3795 | 33.5828 | 31.2188 | 30.5459 | 34.7171
10.5151 | -81.4849 | 38.0244 | 33.5192 | 33.4842 | 33.3795 | 33.5772 | 31.2187 | 30.5511 | 34.736
11.5065 | -80.4935 | 38.0149 | 33.5154 | 33.4851 | 33.3773 | 33.5847 | 31.2178 | 30.5412 | 34.7327
12.508 | -79.492 | 38.006 | 33.5208 | 33.4926 | 33.3754 | 33.5823 | 31.2177 | 30.5484 | 34.7294
13.5094 | -78.4906 | 37.9997 | 33.5177 | 33.475 | 33.3761 | 33.5764 | 31.2109 | 30.5486 | 34.7245
14.5109 | -77.4891 | 37.9973 | 33.5182 | 33.4918 | 33.3768 | 33.5806 | 31.2184 | 30.55 | 34.7174
15.5123 | -76.4877 | 37.9872 | 33.5179 | 33.4977 | 33.3817 | 33.5883 | 31.2116 | 30.5463 | 34.7231
16.5137 | -75.4863 | 37.9857 | 33.5214 | 33.4934 | 33.3807 | 33.5826 | 31.2251 | 30.5396 | 34.7068
17.5052 | -74.4948 | 37.9754 | 33.5248 | 33.4856 | 33.379 | 33.5885 | 31.2155 | 30.5375 | 34.7129
18.5066 | -73.4934 | 37.9667 | 33.5183 | 33.4929 | 33.384 | 33.5885 | 31.2108 | 30.5382 | 34.7136
19.5081 | -72.4919 | 37.957 | 33.5202 | 33.4901 | 33.3784 | 33.5789 | 31.2184 | 30.545 | 34.6982
20.5095 | -71.4905 | 37.9621 | 33.5191 | 33.4918 | 33.3789 | 33.5886 | 31.2187 | 30.542 | 34.6996
21.5109 | -70.4891 | 37.9562 | 33.5187 | 33.4978 | 33.3818 | 33.5851 | 31.2147 | 30.5421 | 34.7025
22.5124 | -69.4876 | 37.956 | 33.5163 | 33.4934 | 33.3831 | 33.5803 | 31.2139 | 30.5502 | 34.7059
23.5138 | -68.4862 | 37.9562 | 33.5147 | 33.4853 | 33.3778 | 33.5921 | 31.215 | 30.5447 | 34.696
24.5052 | -67.4948 | 37.9461 | 33.52 | 33.5024 | 33.3864 | 33.5797 | 31.2147 | 30.5416 | 34.6903
25.5067 | -66.4933 | 37.943 | 33.5153 | 33.4915 | 33.3781 | 33.5845 | 31.2177 | 30.5401 | 34.694
26.5081 | -65.4919 | 37.9282 | 33.5125 | 33.4914 | 33.3801 | 33.5806 | 31.2144 | 30.535 | 34.6901
27.5096 | -64.4904 | 37.9287 | 33.5102 | 33.4951 | 33.3798 | 33.5803 | 31.2071 | 30.5307 | 34.6874
28.511 | -63.489 | 37.9197 | 33.5133 | 33.4882 | 33.3799 | 33.5802 | 31.2075 | 30.5262 | 34.6848
29.5124 | -62.4876 | 37.9148 | 33.5123 | 33.4907 | 33.3813 | 33.5788 | 31.1945 | 30.5369 | 34.6796
30.5139 | -61.4861 | 37.9016 | 33.5149 | 33.4902 | 33.3735 | 33.5752 | 31.1971 | 30.5355 | 34.6828
31.5153 | -60.4847 | 37.8906 | 33.5158 | 33.4792 | 33.3819 | 33.5719 | 31.2043 | 30.5286 | 34.6762
32.5067 | -59.4933 | 37.8848 | 33.5181 | 33.4911 | 33.3845 | 33.5801 | 31.2127 | 30.5307 | 34.6776
33.5082 | -58.4918 | 37.8835 | 33.5188 | 33.4958 | 33.3838 | 33.5745 | 31.2134 | 30.5302 | 34.6776
34.5096 | -57.4904 | 37.8767 | 33.517 | 33.4961 | 33.3794 | 33.5727 | 31.2116 | 30.532 | 34.6699
35.5111 | -56.4889 | 37.8764 | 33.5102 | 33.4942 | 33.3836 | 33.582 | 31.2186 | 30.5366 | 34.6699
36.5125 | -55.4875 | 37.8656 | 33.5128 | 33.4853 | 33.3778 | 33.5727 | 31.2142 | 30.5247 | 34.6671
37.5139 | -54.4861 | 37.8615 | 33.5162 | 33.4887 | 33.3835 | 33.5737 | 31.2153 | 30.5259 | 34.6548
38.5054 | -53.4946 | 37.8577 | 33.5137 | 33.4993 | 33.3756 | 33.5653 | 31.2106 | 30.5223 | 34.6673
39.5068 | -52.4932 | 37.8429 | 33.506 | 33.4975 | 33.3813 | 33.5666 | 31.2112 | 30.5275 | 34.662
40.5082 | -51.4918 | 37.8394 | 33.5135 | 33.4918 | 33.3801 | 33.567 | 31.2163 | 30.5258 | 34.6493
41.5097 | -50.4903 | 37.8342 | 33.5089 | 33.5016 | 33.3736 | 33.5718 | 31.2007 | 30.5257 | 34.6619
42.5111 | -49.4889 | 37.8298 | 33.5072 | 33.4848 | 33.381 | 33.5673 | 31.1957 | 30.5296 | 34.654
43.5126 | -48.4874 | 37.8265 | 33.5091 | 33.4912 | 33.3717 | 33.5718 | 31.196 | 30.5156 | 34.6506
44.514 | -47.486 | 37.8192 | 33.5135 | 33.4898 | 33.3785 | 33.5785 | 31.1938 | 30.5134 | 34.6484
45.5054 | -46.4946 | 37.8076 | 33.5122 | 33.4866 | 33.3755 | 33.5707 | 31.2026 | 30.5238 | 34.6396
46.5069 | -45.4931 | 37.8032 | 33.5193 | 33.4879 | 33.3843 | 33.5684 | 31.1919 | 30.5223 | 34.6351
47.5083 | -44.4917 | 37.7959 | 33.5122 | 33.4936 | 33.3777 | 33.5733 | 31.1714 | 30.5246 | 34.6282
48.5098 | -43.4902 | 37.7888 | 33.5147 | 33.494 | 33.3802 | 33.5608 | 31.1676 | 30.5215 | 34.6349
49.5112 | -42.4888 | 37.7802 | 33.5089 | 33.4957 | 33.3736 | 33.5685 | 31.1694 | 30.524 | 34.6391
50.5126 | -41.4874 | 37.7813 | 33.5137 | 33.4874 | 33.3763 | 33.5623 | 31.1712 | 30.5155 | 34.6325
51.5141 | -40.4859 | 37.7732 | 33.5048 | 33.4977 | 33.3808 | 33.5621 | 31.1675 | 30.5152 | 34.6343
52.5055 | -39.4945 | 37.7711 | 33.5066 | 33.4952 | 33.3776 | 33.5596 | 31.1603 | 30.51 | 34.6314
53.5069 | -38.4931 | 37.7655 | 33.4914 | 33.4826 | 33.3807 | 33.5585 | 31.1608 | 30.5145 | 34.6186
54.5084 | -37.4916 | 37.75 | 33.491 | 33.4884 | 33.3806 | 33.5615 | 31.1621 | 30.516 | 34.6281
55.5098 | -36.4902 | 37.7466 | 33.4938 | 33.4934 | 33.38 | 33.5609 | 31.1634 | 30.5143 | 34.6229
56.5113 | -35.4887 | 37.7407 | 33.4953 | 33.4935 | 33.3771 | 33.56 | 31.168 | 30.509 | 34.6208
57.5127 | -34.4873 | 37.7225 | 33.4877 | 33.4883 | 33.3749 | 33.5422 | 31.1625 | 30.5094 | 34.6109
58.5141 | -33.4859 | 37.716 | 33.4948 | 33.5043 | 33.3778 | 33.5308 | 31.1675 | 30.5144 | 34.601
59.5056 | -32.4944 | 37.7152 | 33.4821 | 33.4919 | 33.3761 | 33.5361 | 31.1642 | 30.5137 | 34.6094
60.507 | -31.493 | 37.7052 | 33.4912 | 33.4932 | 33.3758 | 33.5384 | 31.1643 | 30.5152 | 34.6008
61.5084 | -30.4916 | 37.7051 | 33.4939 | 33.502 | 33.3762 | 33.5451 | 31.1633 | 30.5158 | 34.6113
62.5099 | -29.4901 | 37.697 | 33.4949 | 33.4845 | 33.3789 | 33.5293 | 31.1601 | 30.5155 | 34.6079
63.5113 | -28.4887 | 37.6892 | 33.4923 | 33.4929 | 33.3771 | 33.5378 | 31.1579 | 30.5158 | 34.5972
64.5128 | -27.4872 | 37.6826 | 33.4961 | 33.4967 | 33.3704 | 33.533 | 31.1554 | 30.5197 | 34.5973
65.5142 | -26.4858 | 37.6711 | 33.4918 | 33.4894 | 33.3727 | 33.5292 | 31.1476 | 30.5222 | 34.5935
66.5056 | -25.4944 | 37.6637 | 33.4928 | 33.4786 | 33.3748 | 33.5405 | 31.1549 | 30.5246 | 34.5957
67.5071 | -24.4929 | 37.6578 | 33.4933 | 33.4923 | 33.3754 | 33.5396 | 31.155 | 30.522 | 34.5915
68.5085 | -23.4915 | 37.6571 | 33.4973 | 33.4865 | 33.3785 | 33.53 | 31.1386 | 30.5212 | 34.592
69.51 | -22.49 | 37.6397 | 33.4938 | 33.4923 | 33.3754 | 33.5359 | 31.1358 | 30.5179 | 34.5745
70.5114 | -21.4886 | 37.631 | 33.4933 | 33.4904 | 33.3721 | 33.5292 | 31.1479 | 30.5216 | 34.5821
71.5128 | -20.4872 | 37.6206 | 33.499 | 33.4893 | 33.373 | 33.5427 | 31.1529 | 30.5197 | 34.5789
72.5143 | -19.4857 | 37.613 | 33.4936 | 33.4836 | 33.37 | 33.5408 | 31.1506 | 30.5188 | 34.5752
73.5057 | -18.4943 | 37.6007 | 33.4936 | 33.4902 | 33.3712 | 33.5375 | 31.1532 | 30.5181 | 34.5686
74.5071 | -17.4929 | 37.5877 | 33.4936 | 33.4872 | 33.3705 | 33.5345 | 31.1445 | 30.5174 | 34.5778
75.5086 | -16.4914 | 37.5857 | 33.4953 | 33.4728 | 33.3786 | 33.5367 | 31.1406 | 30.5213 | 34.5542
76.51 | -15.49 | 37.5835 | 33.4956 | 33.481 | 33.3701 | 33.5353 | 31.142 | 30.5239 | 34.5753
77.5115 | -14.4885 | 37.5779 | 33.4973 | 33.4975 | 33.377 | 33.5373 | 31.1456 | 30.5129 | 34.5698
78.5129 | -13.4871 | 37.5727 | 33.4949 | 33.4909 | 33.3665 | 33.5405 | 31.1465 | 30.5206 | 34.5618
79.5143 | -12.4857 | 37.5596 | 33.4981 | 33.4888 | 33.3672 | 33.5427 | 31.1499 | 30.5181 | 34.5602
80.5058 | -11.4942 | 37.5568 | 33.4981 | 33.4914 | 33.3715 | 33.5263 | 31.1527 | 30.5182 | 34.5471
81.5072 | -10.4928 | 37.5592 | 33.4938 | 33.4848 | 33.3707 | 33.5326 | 31.1592 | 30.5117 | 34.5524
82.5086 | -9.4914 | 37.5483 | 33.4985 | 33.4748 | 33.3691 | 33.5368 | 31.1586 | 30.5118 | 34.5429
83.5101 | -8.4899 | 37.5426 | 33.4946 | 33.4882 | 33.3727 | 33.5324 | 31.1645 | 30.5104 | 34.5532
84.5115 | -7.4885 | 37.5432 | 33.4983 | 33.4861 | 33.3687 | 33.5275 | 31.1645 | 30.517 | 34.5401
85.513 | -6.487 | 37.5329 | 33.4956 | 33.4911 | 33.3697 | 33.5278 | 31.1617 | 30.5152 | 34.5409
86.5144 | -5.4856 | 37.5192 | 33.4974 | 33.4774 | 33.3725 | 33.529 | 31.1622 | 30.513 | 34.543
87.5058 | -4.4942 | 37.501 | 33.5001 | 33.4824 | 33.3704 | 33.5354 | 31.1599 | 30.5225 | 34.5318
88.5073 | -3.4927 | 37.5 | 33.4997 | 33.4881 | 33.3712 | 33.5305 | 31.1591 | 30.5115 | 34.5431
89.5087 | -2.4913 | 37.5023 | 33.2812 | 33.4745 | 33.2765 | 33.8248 | 31.237 | 30.5014 | 34.4672
90.5101 | -1.4899 | 37.4994 | 33.4128 | 33.491 | 33.3387 | 33.64 | 31.169 | 30.506 | 34.5139
91.5116 | -0.4884 | 37.6883 | 33.4513 | 33.492 | 33.3552 | 33.6265 | 31.1629 | 30.5121 | 34.5187
92.513 | 0.513 | 38.3777 | 33.4643 | 33.4834 | 33.3644 | 33.5985 | 31.1684 | 30.527 | 34.5249
93.5045 | 1.5045 | 39.6776 | 33.4693 | 33.4845 | 33.3659 | 33.5824 | 31.1817 | 30.5318 | 34.5161
94.5059 | 2.5059 | 41.5417 | 33.4819 | 33.4835 | 33.3673 | 33.5849 | 31.2108 | 30.5499 | 34.5322
95.5073 | 3.5073 | 43.8981 | 33.4852 | 33.4844 | 33.3665 | 33.594 | 31.2438 | 30.5717 | 34.5384
96.5088 | 4.5088 | 46.6663 | 33.5025 | 33.4951 | 33.3749 | 33.6153 | 31.299 | 30.61 | 34.5698
97.5102 | 5.5102 | 49.7884 | 33.5203 | 33.4888 | 33.381 | 33.6484 | 31.3575 | 30.6504 | 34.5923
98.5117 | 6.5117 | 53.1808 | 33.527 | 33.4891 | 33.3853 | 33.6808 | 31.4365 | 30.6937 | 34.6188
99.5131 | 7.5131 | 56.8432 | 33.5595 | 33.491 | 33.4024 | 33.7269 | 31.5174 | 30.7583 | 34.6454
100.5145 | 8.5145 | 60.7268 | 33.5803 | 33.4876 | 33.4143 | 33.7758 | 31.609 | 30.8219 | 34.6786
101.506 | 9.506 | 64.8163 | 33.6208 | 33.4982 | 33.4331 | 33.8412 | 31.7183 | 30.8945 | 34.7282
102.5074 | 10.5074 | 69.0825 | 33.6571 | 33.4972 | 33.4551 | 33.9166 | 31.8371 | 30.9727 | 34.7902
103.5088 | 11.5088 | 73.4736 | 33.6958 | 33.4981 | 33.4785 | 34.0096 | 31.9756 | 31.0681 | 34.8429
104.5103 | 12.5103 | 78.0354 | 33.7451 | 33.5056 | 33.5066 | 34.0934 | 32.1271 | 31.1719 | 34.9064
105.5117 | 13.5117 | 82.7173 | 33.8024 | 33.4967 | 33.5364 | 34.1915 | 32.2804 | 31.288 | 34.9825
106.5132 | 14.5132 | 87.5306 | 33.8641 | 33.5147 | 33.5828 | 34.2992 | 32.4596 | 31.4006 | 35.069
107.5146 | 15.5146 | 92.4211 | 33.9381 | 33.5203 | 33.6169 | 34.4295 | 32.6804 | 31.5489 | 35.1665
108.516 | 16.516 | 97.4441 | 34.0132 | 33.5341 | 33.6734 | 34.5775 | 32.8969 | 31.7086 | 35.2629
109.5075 | 17.5075 | 102.5089 | 34.1033 | 33.5564 | 33.7234 | 34.7274 | 33.1354 | 31.8922 | 35.3834
110.6191 | 18.6191 | 108.2057 | 34.2122 | 33.5684 | 33.7918 | 34.8997 | 33.3973 | 32.0887 | 35.5221
111.5103 | 19.5103 | 112.804 | 34.3077 | 33.5869 | 33.8452 | 35.0513 | 33.633 | 32.2602 | 35.636
112.5118 | 20.5118 | 117.9784 | 34.4225 | 33.6092 | 33.9249 | 35.2446 | 33.906 | 32.4426 | 35.8016
113.5132 | 21.5132 | 123.2968 | 34.5369 | 33.6344 | 34.0087 | 35.4286 | 34.1851 | 32.6662 | 35.9663
114.5046 | 22.5046 | 128.6526 | 34.6787 | 33.6672 | 34.1007 | 35.6526 | 34.5007 | 32.9086 | 36.1564
115.5061 | 23.5061 | 134.0442 | 34.8308 | 33.7021 | 34.1895 | 35.8856 | 34.9111 | 33.1614 | 36.3355
116.5075 | 24.5075 | 139.4936 | 34.9875 | 33.7276 | 34.2869 | 36.1373 | 35.2667 | 33.44 | 36.5492
117.509 | 25.509 | 144.9203 | 35.1466 | 33.7756 | 34.4049 | 36.3836 | 35.633 | 33.7208 | 36.7592
118.5104 | 26.5104 | 150.3421 | 35.3202 | 33.8187 | 34.5187 | 36.6594 | 36.0374 | 34.0132 | 37.0184
119.5719 | 27.5719 | 156.1399 | 35.5147 | 33.8668 | 34.6542 | 36.973 | 36.4788 | 34.2971 | 37.2856
120.5133 | 28.5133 | 161.2515 | 35.7008 | 33.9145 | 34.788 | 37.262 | 36.8409 | 34.593 | 37.5519
121.5147 | 29.5147 | 166.737 | 35.9073 | 33.9872 | 34.9355 | 37.5887 | 37.2877 | 34.928 | 37.8378
122.5062 | 30.5062 | 172.1802 | 36.1157 | 34.0543 | 35.0873 | 37.9401 | 37.7917 | 35.2611 | 38.1627
123.5076 | 31.5076 | 177.6392 | 36.353 | 34.1181 | 35.2547 | 38.3084 | 38.3337 | 35.6089 | 38.4621
124.509 | 32.509 | 183.1242 | 36.5976 | 34.1944 | 35.4229 | 38.6848 | 38.8281 | 35.9825 | 38.8216
125.5105 | 33.5105 | 188.5671 | 36.8523 | 34.2837 | 35.6167 | 39.0781 | 39.3507 | 36.4033 | 39.1818
126.5119 | 34.5119 | 194.0142 | 37.1108 | 34.3715 | 35.8129 | 39.4897 | 39.8594 | 36.8097 | 39.5609
127.5134 | 35.5134 | 199.3971 | 37.4114 | 34.461 | 36.0227 | 39.9294 | 40.3836 | 37.2125 | 39.9385
128.5148 | 36.5148 | 204.9141 | 37.7121 | 34.5746 | 36.2421 | 40.3911 | 40.9575 | 37.6185 | 40.3687
129.5162 | 37.5162 | 210.3677 | 38.0127 | 34.6832 | 36.4766 | 40.8735 | 41.5475 | 38.2 | 40.8208
130.5077 | 38.5077 | 215.8561 | 38.3252 | 34.8043 | 36.7208 | 41.366 | 42.1567 | 38.6442 | 41.2962
131.5091 | 39.5091 | 221.3877 | 38.6588 | 34.9216 | 36.9765 | 41.8797 | 42.8244 | 39.0894 | 41.7895
132.5105 | 40.5105 | 226.8277 | 39.0133 | 35.0546 | 37.2391 | 42.4143 | 43.4878 | 39.5578 | 42.3171
133.512 | 41.512 | 232.2976 | 39.3867 | 35.1972 | 37.5171 | 42.9649 | 44.1717 | 40.1014 | 42.84
134.5134 | 42.5134 | 237.7756 | 39.7613 | 35.3464 | 37.8103 | 43.5361 | 44.8962 | 40.6843 | 43.4044
135.5149 | 43.5149 | 243.2491 | 40.1547 | 35.4963 | 38.1064 | 44.1214 | 45.6447 | 41.3216 | 43.9852
136.5063 | 44.5063 | 248.684 | 40.5664 | 35.6609 | 38.4152 | 44.73 | 46.4356 | 41.8853 | 44.6304
137.5077 | 45.5077 | 254.0492 | 40.979 | 35.836 | 38.744 | 45.3578 | 47.2069 | 42.5153 | 45.2599
138.5092 | 46.5092 | 259.4383 | 41.4122 | 36.0185 | 39.0711 | 45.9973 | 47.9971 | 43.1222 | 45.9024
139.5106 | 47.5106 | 264.7696 | 41.8457 | 36.2165 | 39.4087 | 46.6471 | 48.8498 | 43.712 | 46.6293
140.512 | 48.512 | 270.1693 | 42.2986 | 36.4118 | 39.7552 | 47.316 | 49.6298 | 44.3938 | 47.3809
141.5135 | 49.5135 | 275.6458 | 42.744 | 36.6204 | 40.1188 | 47.9939 | 50.4724 | 45.0959 | 48.1345
142.5049 | 50.5049 | 280.9371 | 43.2093 | 36.8446 | 40.4956 | 48.6709 | 51.3776 | 45.7931 | 48.9221
143.5064 | 51.5064 | 286.238 | 43.6829 | 37.0647 | 40.8659 | 49.3806 | 52.2965 | 46.5074 | 49.7431
144.5078 | 52.5078 | 291.6446 | 44.1611 | 37.3024 | 41.264 | 50.1047 | 53.1861 | 47.2345 | 50.5796
145.5092 | 53.5092 | 296.9739 | 44.6443 | 37.5425 | 41.6548 | 50.8573 | 54.1819 | 47.9546 | 51.4477
146.5107 | 54.5107 | 302.263 | 45.1331 | 37.7946 | 42.0684 | 51.6432 | 55.146 | 48.6942 | 52.3564
147.5121 | 55.5121 | 307.4851 | 45.6371 | 38.0625 | 42.4999 | 52.4572 | 56.1968 | 49.4262 | 53.2921
148.5136 | 56.5136 | 312.7411 | 46.1598 | 38.3395 | 42.9425 | 53.306 | 57.246 | 50.1796 | 54.2649
149.515 | 57.515 | 317.9842 | 46.72 | 38.603 | 43.396 | 54.2035 | 58.3759 | 51.0437 | 55.2482
150.5064 | 58.5064 | 323.2197 | 47.2998 | 38.9116 | 43.8732 | 55.1224 | 59.4337 | 51.9231 | 56.2612
151.5079 | 59.5079 | 328.4711 | 47.8934 | 39.2045 | 44.366 | 56.066 | 60.4839 | 52.7744 | 57.3136
152.5093 | 60.5093 | 333.7473 | 48.5043 | 39.5096 | 44.8629 | 57.0603 | 61.5939 | 53.7033 | 58.4165
153.5107 | 61.5107 | 338.9361 | 49.1369 | 39.8277 | 45.3907 | 58.1069 | 62.7086 | 54.5782 | 59.5098
154.5122 | 62.5122 | 344.1722 | 49.8007 | 40.1656 | 45.9188 | 59.1758 | 63.8642 | 55.371 | 60.6825
155.5136 | 63.5136 | 349.2513 | 50.491 | 40.5003 | 46.4668 | 60.2875 | 65.0566 | 56.3584 | 61.8896
156.5151 | 64.5151 | 354.2824 | 51.2057 | 40.8429 | 47.0385 | 61.4261 | 66.2449 | 57.3371 | 63.1331
157.5065 | 65.5065 | 359.4191 | 51.9484 | 41.2187 | 47.6263 | 62.6126 | 67.5421 | 58.2713 | 64.39
158.5079 | 66.5079 | 364.4384 | 52.7084 | 41.5877 | 48.2191 | 63.8206 | 68.95 | 59.2386 | 65.7336
159.5094 | 67.5094 | 369.4531 | 53.4917 | 41.9785 | 48.8395 | 65.1111 | 70.1556 | 60.2318 | 67.1011
160.5108 | 68.5108 | 374.4563 | 54.2853 | 42.3729 | 49.4773 | 66.4908 | 71.3567 | 61.134 | 68.4583
161.5122 | 69.5122 | 379.382 | 55.104 | 42.7744 | 50.1371 | 67.948 | 72.5952 | 62.114 | 69.87
162.5137 | 70.5137 | 384.2329 | 55.9343 | 43.2098 | 50.82 | 69.5184 | 73.8963 | 63.194 | 71.3168
163.5051 | 71.5051 | 389.0908 | 56.7992 | 43.6296 | 51.5419 | 71.2056 | 75.2368 | 64.1877 | 72.795
164.5166 | 72.5166 | 393.9092 | 57.681 | 44.0968 | 52.2909 | 72.9598 | 76.5963 | 65.2827 | 74.3612
165.508 | 73.508 | 398.7491 | 58.5943 | 44.5583 | 53.0733 | 74.7876 | 77.9333 | 66.4224 | 75.8832
166.5094 | 74.5094 | 403.5643 | 59.5468 | 45.0376 | 53.8821 | 76.6822 | 79.3286 | 67.5335 | 77.4697
167.5109 | 75.5109 | 408.3717 | 60.5403 | 45.5258 | 54.7162 | 78.6093 | 80.6768 | 68.7109 | 79.1349
168.5123 | 76.5123 | 413.1258 | 61.5894 | 46.0358 | 55.5854 | 80.6099 | 82.1313 | 69.8691 | 80.877
169.5137 | 77.5137 | 418.0402 | 62.6994 | 46.5639 | 56.481 | 82.6531 | 83.6783 | 71.1592 | 82.5819
170.5152 | 78.5152 | 422.848 | 63.8692 | 47.1043 | 57.4164 | 84.7492 | 85.1571 | 72.3523 | 84.3748
171.5066 | 79.5066 | 427.5135 | 65.087 | 47.6744 | 58.38 | 86.8733 | 86.6792 | 73.6365 | 86.161
172.5081 | 80.5081 | 432.3562 | 66.2577 | 48.2381 | 59.3078 | 89.1634 | 88.1541 | 74.8978 | 87.9772
173.5095 | 81.5095 | 436.9833 | 67.4587 | 48.8431 | 60.2861 | 91.5389 | 89.644 | 76.1744 | 89.8063
174.5109 | 82.5109 | 441.2609 | 68.7773 | 49.4579 | 61.3187 | 93.7837 | 91.1949 | 77.5498 | 91.7304
175.5124 | 83.5124 | 445.0302 | 70.1443 | 50.0785 | 62.3736 | 96.0384 | 92.688 | 78.8668 | 93.6731
176.5138 | 84.5138 | 448.6561 | 71.5427 | 50.7156 | 63.4536 | 98.2881 | 94.289 | 80.2077 | 95.6528
177.5052 | 85.5052 | 451.9114 | 72.9702 | 51.3898 | 64.5658 | 100.5643 | 95.8945 | 81.5643 | 97.6528
178.5067 | 86.5067 | 455.0148 | 74.3625 | 52.0747 | 65.6924 | 102.8975 | 97.5005 | 82.8941 | 99.6839
179.5081 | 87.5081 | 457.872 | 75.7844 | 52.7712 | 66.8395 | 105.248 | 99.0536 | 84.2957 | 101.7529
180.5096 | 88.5096 | 460.7582 | 77.2303 | 53.4906 | 68.0045 | 107.5369 | 100.6874 | 85.731 | 103.8558
181.511 | 89.511 | 463.6104 | 78.6131 | 54.226 | 69.1716 | 109.971 | 102.3092 | 87.2041 | 105.9131
182.5124 | 90.5124 | 466.365 | 80.0663 | 54.9894 | 70.3735 | 112.2969 | 103.984 | 88.7086 | 108.018
183.5139 | 91.5139 | 468.9973 | 81.5184 | 55.7371 | 71.5888 | 114.6669 | 105.7104 | 90.2117 | 110.1658
184.5053 | 92.5053 | 471.5701 | 82.9331 | 56.5199 | 72.8089 | 117.0742 | 107.4062 | 91.6967 | 112.2988
185.5067 | 93.5067 | 473.7115 | 84.5359 | 57.3338 | 74.1224 | 119.2982 | 109.0273 | 93.196 | 114.519
186.5082 | 94.5082 | 475.6484 | 86.0308 | 58.1507 | 75.4063 | 121.6495 | 110.7201 | 94.7472 | 116.6954
187.5096 | 95.5096 | 477.2088 | 87.5266 | 58.9816 | 76.7176 | 124.0184 | 112.302 | 96.3029 | 118.8745
188.5111 | 96.5111 | 478.4667 | 89.0302 | 59.8082 | 78.0447 | 126.3378 | 113.9014 | 97.7696 | 121.0458
189.5125 | 97.5125 | 479.6541 | 90.5362 | 60.6717 | 79.4081 | 128.6601 | 115.5812 | 99.2023 | 123.2399
190.5139 | 98.5139 | 480.4449 | 92.0317 | 61.5498 | 80.8016 | 130.9439 | 117.1817 | 100.723 | 125.421
191.5154 | 99.5154 | 481.0804 | 93.5219 | 62.4313 | 82.2297 | 133.1825 | 118.7131 | 102.1832 | 127.6018
192.5168 | 100.5168 | 481.6164 | 94.9979 | 63.3224 | 83.6763 | 135.3918 | 120.1784 | 103.6007 | 129.7712
193.5083 | 101.5083 | 482.0966 | 96.4661 | 64.2213 | 85.1502 | 137.5183 | 121.6218 | 105.0133 | 131.9121
194.5097 | 102.5097 | 482.477 | 97.9241 | 65.123 | 86.6224 | 139.6234 | 123.0355 | 106.4185 | 134.0718
195.5111 | 103.5111 | 482.6316 | 99.3744 | 66.056 | 88.0894 | 141.6562 | 124.4668 | 107.7133 | 136.2092
196.5126 | 104.5126 | 482.7773 | 100.7771 | 66.9964 | 89.5634 | 143.6568 | 125.8386 | 109.0448 | 138.3431
197.514 | 105.514 | 482.6984 | 102.1875 | 67.9375 | 91.024 | 145.5913 | 127.1896 | 110.3349 | 140.4355
198.5054 | 106.5054 | 482.4584 | 103.5781 | 68.8761 | 92.4696 | 147.4898 | 128.519 | 111.6156 | 142.5422
199.5069 | 107.5069 | 482.1723 | 104.9651 | 69.8247 | 93.9236 | 149.327 | 129.7914 | 112.8754 | 144.6171
200.5083 | 108.5083 | 481.7184 | 106.3244 | 70.7731 | 95.3605 | 151.1096 | 131.038 | 114.1099 | 146.6778
201.5098 | 109.5098 | 481.2126 | 107.6625 | 71.7402 | 96.7873 | 152.8448 | 132.2687 | 115.2913 | 148.7408
202.5112 | 110.5112 | 480.7973 | 108.981 | 72.7026 | 98.2579 | 154.5241 | 133.4344 | 116.4373 | 150.7991
203.5126 | 111.5126 | 480.309 | 110.2591 | 73.6566 | 99.6189 | 156.2077 | 134.5528 | 117.6344 | 152.8242
204.5141 | 112.5141 | 479.8818 | 111.5083 | 74.6173 | 100.9525 | 157.8252 | 135.7076 | 118.7516 | 154.8354
205.5055 | 113.5055 | 479.4836 | 112.7174 | 75.586 | 102.1517 | 159.4067 | 136.8211 | 119.8752 | 156.8487
206.5069 | 114.5069 | 479.1221 | 113.9192 | 76.5537 | 103.2277 | 160.9732 | 137.9288 | 120.9916 | 158.8381
207.5084 | 115.5084 | 478.7121 | 115.097 | 77.511 | 104.3243 | 162.5098 | 138.983 | 122.0264 | 160.8151
208.5098 | 116.5098 | 478.2437 | 116.2715 | 78.4686 | 105.4251 | 163.9947 | 140.082 | 123.1258 | 162.779
209.5113 | 117.5113 | 477.7608 | 117.4268 | 79.4298 | 106.5474 | 165.4141 | 141.1148 | 124.1931 | 164.7406
210.5127 | 118.5127 | 477.4523 | 118.5523 | 80.3783 | 107.6628 | 166.8403 | 142.2515 | 125.2696 | 166.6814
211.5141 | 119.5141 | 477.2128 | 119.6519 | 81.3297 | 108.6456 | 168.2257 | 143.2213 | 126.2981 | 168.6153
212.5156 | 120.5156 | 476.9997 | 120.7054 | 82.2731 | 109.5976 | 169.558 | 144.2316 | 127.4214 | 170.5119
213.507 | 121.507 | 476.8796 | 121.7553 | 83.2257 | 110.5218 | 170.872 | 145.2184 | 128.4877 | 172.4475
214.5084 | 122.5084 | 476.765 | 122.7966 | 84.1614 | 111.4202 | 172.1938 | 146.187 | 129.4424 | 174.348
215.5099 | 123.5099 | 476.6348 | 123.8224 | 85.1067 | 112.3437 | 173.4808 | 147.1919 | 130.3974 | 176.2504
216.5113 | 124.5113 | 476.4293 | 124.8367 | 86.0582 | 113.3137 | 174.766 | 148.3452 | 131.3779 | 178.1113
217.5128 | 125.5128 | 476.3475 | 125.8528 | 86.996 | 114.2606 | 175.9944 | 149.463 | 132.3587 | 179.9862
218.5142 | 126.5142 | 476.2914 | 126.8454 | 87.9312 | 115.2286 | 177.2313 | 150.3788 | 133.297 | 181.8531
219.5056 | 127.5056 | 476.3366 | 127.8362 | 88.8568 | 116.1908 | 178.4567 | 151.2628 | 134.296 | 183.7046
220.5071 | 128.5071 | 476.4172 | 128.825 | 89.7824 | 117.1546 | 179.6192 | 152.253 | 135.2736 | 185.5456
221.5085 | 129.5085 | 476.5756 | 129.7992 | 90.7119 | 118.099 | 180.7755 | 153.2079 | 136.2062 | 187.3803
222.51 | 130.51 | 476.7002 | 130.7729 | 91.6371 | 119.0037 | 181.9377 | 154.2327 | 137.1403 | 189.1971
223.5114 | 131.5114 | 476.9379 | 131.7278 | 92.561 | 119.9459 | 183.071 | 155.1207 | 138.0056 | 191.0195
224.5128 | 132.5128 | 477.2403 | 132.7022 | 93.4771 | 120.9413 | 184.1876 | 156.0498 | 138.8638 | 192.8261
225.5143 | 133.5143 | 477.3472 | 133.6401 | 94.4031 | 121.9597 | 185.2982 | 156.9251 | 139.7346 | 194.6248
226.5057 | 134.5057 | 477.4338 | 134.5794 | 95.3423 | 123.0333 | 186.3866 | 157.8007 | 140.6853 | 196.4131
227.5071 | 135.5071 | 477.6089 | 135.5107 | 96.2701 | 124.1211 | 187.4742 | 158.6663 | 141.5996 | 198.1848
228.5086 | 136.5086 | 477.8513 | 136.4309 | 97.2231 | 125.1826 | 188.5572 | 159.5637 | 142.5357 | 199.9522
229.51 | 137.51 | 478.0563 | 137.3414 | 98.1862 | 126.1837 | 189.6337 | 160.4543 | 143.3891 | 201.7435
230.5115 | 138.5115 | 478.2575 | 138.2353 | 99.1971 | 127.1067 | 190.7183 | 161.4135 | 144.3024 | 203.4933
231.5129 | 139.5129 | 478.5386 | 139.1387 | 100.2057 | 128.164 | 191.8005 | 162.2867 | 145.18 | 205.2402
232.5143 | 140.5143 | 478.7673 | 140.0393 | 101.2596 | 129.204 | 192.8489 | 163.1512 | 146.0556 | 206.9782
233.5158 | 141.5158 | 478.9357 | 140.9465 | 102.2935 | 130.2285 | 193.8784 | 163.9984 | 146.8815 | 208.6897
234.5072 | 142.5072 | 479.0845 | 141.8383 | 103.3416 | 131.2562 | 194.9049 | 164.829 | 147.756 | 210.4251
235.5086 | 143.5086 | 479.2851 | 142.7584 | 104.3751 | 132.2944 | 195.9235 | 165.6931 | 148.6397 | 212.1172
236.5101 | 144.5101 | 479.5847 | 143.6706 | 105.4065 | 133.3324 | 196.9353 | 166.5597 | 149.4779 | 213.813
237.5115 | 145.5115 | 479.8249 | 144.5971 | 106.4343 | 134.3585 | 197.9059 | 167.4455 | 150.3673 | 215.5038
238.513 | 146.513 | 479.8613 | 145.5386 | 107.4592 | 135.3784 | 198.8761 | 168.2534 | 151.2106 | 217.1711
239.5144 | 147.5144 | 479.8266 | 146.4875 | 108.4627 | 136.3875 | 199.8213 | 169.0721 | 152.0642 | 218.828
240.5058 | 148.5058 | 479.8493 | 147.4523 | 109.4592 | 137.3782 | 200.7346 | 169.8855 | 152.8309 | 220.4663
241.5073 | 149.5073 | 479.9019 | 148.4134 | 110.4379 | 138.3558 | 201.656 | 170.7329 | 153.6135 | 222.0801
242.5087 | 150.5087 | 479.9581 | 149.3789 | 111.4159 | 139.3201 | 202.5572 | 171.5395 | 154.4389 | 223.7178
243.5102 | 151.5102 | 479.9893 | 150.3443 | 112.3849 | 140.2684 | 203.4424 | 172.2998 | 155.2822 | 225.3129
244.5116 | 152.5116 | 479.9348 | 151.3156 | 113.3601 | 141.216 | 204.3362 | 173.0664 | 156.1391 | 226.8975
245.513 | 153.513 | 479.7314 | 152.2811 | 114.3526 | 142.1678 | 205.1852 | 173.837 | 156.9534 | 228.4757
246.5145 | 154.5145 | 479.7053 | 153.2456 | 115.3655 | 143.1171 | 205.9851 | 174.625 | 157.793 | 230.0238
247.5059 | 155.5059 | 479.6458 | 154.2093 | 116.4029 | 144.0573 | 206.7661 | 175.4164 | 158.5721 | 231.5731
248.5073 | 156.5073 | 479.6825 | 155.1882 | 117.4721 | 144.9856 | 207.5821 | 176.1621 | 159.4051 | 233.104
249.5088 | 157.5088 | 479.789 | 156.1888 | 118.5911 | 145.9239 | 208.431 | 176.8553 | 160.1609 | 234.6112
250.5102 | 158.5102 | 479.8397 | 157.1825 | 119.7412 | 146.8853 | 209.2749 | 177.638 | 160.9374 | 236.1159
251.5117 | 159.5117 | 479.8089 | 158.1887 | 120.9114 | 147.8644 | 210.0912 | 178.3328 | 161.7118 | 237.597
252.5131 | 160.5131 | 479.8177 | 159.1987 | 122.0913 | 148.8357 | 210.9306 | 179.1828 | 162.4996 | 239.0823
253.5145 | 161.5145 | 479.9653 | 160.2229 | 123.2502 | 149.8332 | 211.7793 | 179.8888 | 163.1903 | 240.5445
254.516 | 162.516 | 480.1091 | 161.2701 | 124.4226 | 150.8311 | 212.6263 | 180.583 | 163.9121 | 242.0006
255.5074 | 163.5074 | 480.1737 | 162.3221 | 125.5633 | 151.8555 | 213.4928 | 181.3236 | 164.6731 | 243.4465
256.5088 | 164.5088 | 480.1402 | 163.3782 | 126.6985 | 152.8757 | 214.3563 | 182.0763 | 165.4263 | 244.8778
257.5103 | 165.5103 | 480.2074 | 164.4427 | 127.8152 | 153.8931 | 215.2553 | 182.8252 | 166.2119 | 246.2963
258.5117 | 166.5117 | 480.2404 | 165.5386 | 128.9531 | 154.9291 | 216.1444 | 183.5462 | 166.9642 | 247.7221
259.5132 | 167.5132 | 480.2357 | 166.6376 | 130.0756 | 155.9475 | 217.0356 | 184.2759 | 167.7423 | 249.13
260.5146 | 168.5146 | 480.4195 | 167.7493 | 131.2058 | 156.9866 | 217.8906 | 184.9838 | 168.4815 | 250.5297
261.506 | 169.506 | 480.6277 | 168.8618 | 132.3409 | 158.0292 | 218.7493 | 185.7131 | 169.2697 | 251.9005
262.5075 | 170.5075 | 480.5998 | 169.9793 | 133.474 | 159.0681 | 219.5866 | 186.4886 | 170.0094 | 253.2911
263.5089 | 171.5089 | 480.6569 | 171.0937 | 134.5931 | 160.0997 | 220.455 | 187.2134 | 170.763 | 254.659
264.5103 | 172.5103 | 480.681 | 172.2019 | 135.7323 | 161.1331 | 221.2926 | 187.8901 | 171.5285 | 256.0112
265.5118 | 173.5118 | 480.7249 | 173.309 | 136.8778 | 162.1742 | 222.1539 | 188.6226 | 172.2447 | 257.3573
266.5132 | 174.5132 | 480.672 | 174.4024 | 138.0242 | 163.2115 | 222.9995 | 189.3118 | 173.0324 | 258.7069
267.5147 | 175.5147 | 480.6491 | 175.5036 | 139.1934 | 164.2565 | 223.8631 | 190.0371 | 173.7519 | 260.0292
268.5061 | 176.5061 | 480.7573 | 176.5969 | 140.3883 | 165.2995 | 224.6932 | 190.7556 | 174.4641 | 261.3532
269.5075 | 177.5075 | 480.7252 | 177.6797 | 141.5868 | 166.3523 | 225.5192 | 191.5276 | 175.2334 | 262.6464
270.509 | 178.509 | 480.6729 | 178.771 | 142.7998 | 167.3967 | 226.3296 | 192.2417 | 175.8572 | 263.9293
271.5104 | 179.5104 | 480.6529 | 179.8679 | 144.0117 | 168.4363 | 227.1362 | 193.0024 | 176.5898 | 265.219
272.5119 | 180.5119 | 480.7122 | 180.9693 | 145.231 | 169.4791 | 227.9828 | 193.7595 | 177.3144 | 266.4881
273.5133 | 181.5133 | 480.6667 | 182.0689 | 146.4457 | 170.5195 | 228.811 | 194.5213 | 178.0513 | 267.7426
274.5147 | 182.5147 | 480.5492 | 183.1752 | 147.6487 | 171.5673 | 229.6295 | 195.2689 | 178.8315 | 268.9946
275.5162 | 183.5162 | 480.4502 | 184.2783 | 148.8723 | 172.6187 | 230.4611 | 195.9664 | 179.5254 | 270.2405
276.5076 | 184.5076 | 480.6408 | 185.4048 | 150.0747 | 173.652 | 231.2922 | 196.7259 | 180.1991 | 271.4809
277.509 | 185.509 | 480.7915 | 186.5277 | 151.273 | 174.7011 | 232.1107 | 197.4615 | 180.9866 | 272.6899
278.5105 | 186.5105 | 481.0287 | 187.6356 | 152.4675 | 175.7469 | 232.9329 | 198.0851 | 181.706 | 273.9247
279.5119 | 187.5119 | 481.0781 | 188.7429 | 153.6537 | 176.7811 | 233.7605 | 198.8342 | 182.3608 | 275.132
280.5134 | 188.5134 | 481.0537 | 189.8547 | 154.842 | 177.8353 | 234.5943 | 199.5746 | 183.0753 | 276.3355
281.5148 | 189.5148 | 480.997 | 190.9696 | 156.0059 | 178.872 | 235.39 | 200.2777 | 183.7744 | 277.5186
282.5062 | 190.5062 | 481.0065 | 192.0888 | 157.182 | 179.9179 | 236.1349 | 201.0396 | 184.5542 | 278.6886
283.5077 | 191.5077 | 480.889 | 193.1938 | 158.3438 | 180.9714 | 236.8965 | 201.7698 | 185.3116 | 279.8457
284.5091 | 192.5091 | 480.9163 | 194.3163 | 159.4986 | 182.0069 | 237.6484 | 202.5434 | 186.0179 | 281.006
285.5105 | 193.5105 | 480.963 | 195.4278 | 160.661 | 183.0487 | 238.4275 | 203.236 | 186.703 | 282.1564
286.512 | 194.512 | 480.8443 | 196.5492 | 161.8093 | 184.0815 | 239.1969 | 203.903 | 187.4281 | 283.289
287.5134 | 195.5134 | 480.7414 | 197.6767 | 162.969 | 185.1225 | 239.971 | 204.5857 | 188.1288 | 284.4184
288.5048 | 196.5048 | 480.782 | 198.7986 | 164.1172 | 186.1631 | 240.7332 | 205.3253 | 188.8001 | 285.5303
289.5063 | 197.5063 | 480.9031 | 199.9218 | 165.2576 | 187.1926 | 241.4803 | 206.049 | 189.4988 | 286.6259
290.5077 | 198.5077 | 480.9575 | 201.0592 | 166.3831 | 188.2246 | 242.2081 | 206.8289 | 190.1398 | 287.726
291.5092 | 199.5092 | 480.917 | 202.199 | 167.5263 | 189.2611 | 242.9268 | 207.6122 | 190.8015 | 288.8054
292.5106 | 200.5106 | 480.8158 | 203.3481 | 168.6469 | 190.2869 | 243.6518 | 208.3439 | 191.5591 | 289.8772
293.512 | 201.512 | 480.7196 | 204.5154 | 169.7721 | 191.3177 | 244.3775 | 208.9911 | 192.2066 | 290.9252
294.5135 | 202.5135 | 480.7003 | 205.6754 | 170.9003 | 192.3415 | 245.113 | 209.7192 | 192.9352 | 292.0017
295.5049 | 203.5049 | 480.5726 | 206.8439 | 172.0301 | 193.3624 | 245.8227 | 210.4141 | 193.6165 | 293.0229
296.5164 | 204.5164 | 480.3727 | 208.0282 | 173.1552 | 194.3728 | 246.5224 | 211.0064 | 194.3389 | 294.0803
297.5078 | 205.5078 | 480.3645 | 209.2191 | 174.2477 | 195.3856 | 247.1995 | 211.6787 | 195.0738 | 295.1045
298.5092 | 206.5092 | 480.371 | 210.4372 | 175.35 | 196.3862 | 247.8798 | 212.3954 | 195.7648 | 296.1201
299.5107 | 207.5107 | 480.456 | 211.6689 | 176.4405 | 197.3886 | 248.5535 | 212.9945 | 196.4529 | 297.1389
300.5121 | 208.5121 | 480.4765 | 212.9422 | 177.5183 | 198.3992 | 249.2024 | 213.7297 | 197.0763 | 298.12
301.5136 | 209.5136 | 480.5648 | 214.2707 | 178.6003 | 199.4203 | 249.8669 | 214.4573 | 197.7534 | 299.1205
302.515 | 210.515 | 480.7203 | 215.6827 | 179.6624 | 200.4639 | 250.4837 | 215.1113 | 198.41 | 300.1205
303.5064 | 211.5064 | 480.8946 | 217.1374 | 180.7198 | 201.5171 | 251.0885 | 215.7474 | 199.0014 | 301.0919
304.5079 | 212.5079 | 480.9113 | 218.5204 | 181.7794 | 202.5775 | 251.6597 | 216.4663 | 199.7623 | 302.0556
305.5093 | 213.5093 | 481.0007 | 219.8116 | 182.8351 | 203.6366 | 252.2133 | 217.1454 | 200.4598 | 303.0086
306.5107 | 214.5107 | 480.9 | 221.2066 | 183.8884 | 204.674 | 252.7507 | 217.8778 | 201.2036 | 303.9585
307.5122 | 215.5122 | 480.778 | 222.6123 | 184.9368 | 205.7027 | 253.2701 | 218.5277 | 201.9043 | 304.9078
308.5136 | 216.5136 | 480.6807 | 223.9809 | 186.0027 | 206.7251 | 253.7882 | 219.1572 | 202.5395 | 305.8324
309.505 | 217.505 | 480.6722 | 225.3233 | 187.0502 | 207.7443 | 253.8408 | 219.7934 | 203.1654 | 306.7562
310.5065 | 218.5065 | 480.6763 | 226.6399 | 188.1023 | 208.7637 | 253.7709 | 220.4373 | 203.8755 | 307.6837
311.5079 | 219.5079 | 480.809 | 227.9463 | 189.1389 | 209.7648 | 253.7244 | 221.1885 | 204.6488 | 308.5799
312.5094 | 220.5094 | 480.7666 | 229.27 | 190.1899 | 210.7747 | 253.7535 | 221.7998 | 205.3359 | 309.4744
313.5108 | 221.5108 | 480.777 | 230.653 | 191.24 | 211.8169 | 253.7888 | 222.4938 | 205.9755 | 310.3453
314.5122 | 222.5122 | 480.74 | 232.098 | 192.2848 | 212.8238 | 253.923 | 223.1373 | 206.6874 | 311.2335
315.5137 | 223.5137 | 480.711 | 233.6701 | 193.329 | 213.7924 | 254.1921 | 223.7884 | 207.305 | 312.1091
316.5051 | 224.5051 | 480.7611 | 235.4293 | 194.3702 | 214.7518 | 254.5566 | 224.3889 | 208.0105 | 312.9529
317.5166 | 225.5166 | 480.7594 | 237.1372 | 195.4225 | 215.7136 | 254.9855 | 225.0844 | 208.6982 | 313.8033
318.508 | 226.508 | 480.6977 | 238.7501 | 196.4496 | 216.648 | 255.4517 | 225.7481 | 209.3364 | 314.6543
319.5094 | 227.5094 | 480.6853 | 240.2855 | 197.5083 | 217.558 | 255.9153 | 226.4227 | 209.8908 | 315.4895
320.5109 | 228.5109 | 480.6791 | 241.7414 | 198.5459 | 218.4325 | 256.346 | 227.1086 | 210.5686 | 316.3173
321.5123 | 229.5123 | 480.8617 | 243.1511 | 199.5829 | 219.2926 | 256.6986 | 227.7857 | 211.1968 | 317.1339
322.5138 | 230.5138 | 480.7613 | 244.4908 | 200.6264 | 220.1688 | 257.0465 | 228.4786 | 211.8859 | 317.9407
323.5152 | 231.5152 | 480.6617 | 245.8402 | 201.666 | 221.0396 | 257.3565 | 229.1173 | 212.5595 | 318.7467
324.5066 | 232.5066 | 480.4957 | 247.1482 | 202.7173 | 221.9159 | 257.5776 | 229.7625 | 213.2207 | 319.5392
325.5081 | 233.5081 | 480.3899 | 248.376 | 203.7301 | 222.7887 | 257.729 | 230.3756 | 213.9133 | 320.3541
326.5095 | 234.5095 | 480.1461 | 249.55 | 204.7588 | 223.6817 | 257.8657 | 230.9753 | 214.5227 | 321.1259
327.5109 | 235.5109 | 479.8783 | 250.6412 | 205.7624 | 224.5782 | 258.0372 | 231.5898 | 215.0995 | 321.8948
328.5124 | 236.5124 | 479.8232 | 251.6299 | 206.7966 | 225.4853 | 258.228 | 232.0902 | 215.7766 | 322.6641
329.5138 | 237.5138 | 479.7637 | 252.5775 | 207.792 | 226.3746 | 258.4599 | 232.5467 | 216.4293 | 323.4202
330.5052 | 238.5052 | 479.7647 | 253.4962 | 208.7947 | 227.2681 | 258.7553 | 233.0665 | 217.0477 | 324.1668
331.5067 | 239.5067 | 479.8186 | 254.4265 | 209.8108 | 228.1822 | 259.1 | 233.6662 | 217.6866 | 324.9273
332.5081 | 240.5081 | 479.7684 | 255.3254 | 210.8085 | 229.1184 | 259.476 | 234.2848 | 218.3527 | 325.6624
333.5096 | 241.5096 | 479.8402 | 256.1972 | 211.7947 | 230.0125 | 259.8599 | 234.9246 | 219.0249 | 326.372
334.511 | 242.511 | 480.0689 | 257.0558 | 212.7786 | 230.8611 | 260.263 | 235.5444 | 219.6297 | 327.1076
335.5124 | 243.5124 | 480.1664 | 257.8999 | 213.761 | 231.6646 | 260.6727 | 236.2875 | 220.2718 | 327.8298
336.5139 | 244.5139 | 480.1361 | 258.7377 | 214.7151 | 232.4606 | 261.1171 | 236.8626 | 220.957 | 328.5348
337.5053 | 245.5053 | 480.0702 | 259.565 | 215.6703 | 233.2713 | 261.5595 | 237.505 | 221.5579 | 329.2558
338.5067 | 246.5067 | 480.0114 | 260.377 | 216.604 | 234.0657 | 262.0027 | 238.107 | 222.154 | 329.9553
339.5082 | 247.5082 | 479.8528 | 261.1955 | 217.551 | 234.8533 | 262.4026 | 238.6864 | 222.7523 | 330.655
340.5096 | 248.5096 | 479.746 | 262.0094 | 218.4868 | 235.5953 | 262.7939 | 239.2068 | 223.3176 | 331.329
341.5111 | 249.5111 | 479.776 | 262.8136 | 219.4364 | 236.347 | 263.1865 | 239.6465 | 223.8704 | 331.9741
342.5125 | 250.5125 | 479.6782 | 263.6124 | 220.3942 | 237.1011 | 263.5539 | 240.2131 | 224.5412 | 332.6574
343.5139 | 251.5139 | 479.6784 | 264.4096 | 221.3578 | 237.8658 | 263.9281 | 240.8089 | 225.1815 | 333.3054
344.5154 | 252.5154 | 479.7615 | 265.2067 | 222.315 | 238.6467 | 264.3361 | 241.3954 | 225.7934 | 333.9493
345.5068 | 253.5068 | 479.8431 | 265.9947 | 223.2594 | 239.4558 | 264.7711 | 242.0344 | 226.4616 | 334.5981
346.5083 | 254.5083 | 479.9718 | 266.7797 | 224.2071 | 240.262 | 265.2343 | 242.609 | 227.1036 | 335.2385
347.5097 | 255.5097 | 480.1869 | 267.5618 | 225.1461 | 241.0866 | 265.7297 | 243.1964 | 227.7085 | 335.8681
348.5111 | 256.5111 | 480.385 | 268.3585 | 226.1057 | 241.9212 | 266.2795 | 243.8812 | 228.3241 | 336.4869
349.5126 | 257.5126 | 480.6658 | 269.1378 | 227.0365 | 242.7635 | 266.8565 | 244.5294 | 228.9886 | 337.1055
350.514 | 258.514 | 480.7682 | 269.9327 | 227.9839 | 243.6163 | 267.4429 | 245.1346 | 229.6197 | 337.7365
351.5054 | 259.5054 | 480.7 | 270.7167 | 228.9161 | 244.4637 | 268.0238 | 245.6934 | 230.2189 | 338.3578
352.5069 | 260.5069 | 480.7501 | 271.5029 | 229.8486 | 245.3107 | 268.5987 | 246.2577 | 230.8144 | 338.9832
353.5083 | 261.5083 | 480.9593 | 272.2805 | 230.7881 | 246.1622 | 269.1742 | 246.8921 | 231.4128 | 339.5735
354.5098 | 262.5098 | 481.2076 | 273.0403 | 231.7229 | 247.004 | 269.745 | 247.455 | 232.0525 | 340.1622
355.5112 | 263.5112 | 481.2834 | 273.7919 | 232.6386 | 247.8454 | 270.2955 | 248.004 | 232.6457 | 340.7391
356.5126 | 264.5126 | 481.1846 | 274.55 | 233.5512 | 248.6692 | 270.8592 | 248.6015 | 233.1696 | 341.3288
357.5141 | 265.5141 | 480.9421 | 275.3237 | 234.465 | 249.5085 | 271.4499 | 249.0761 | 233.7922 | 341.8748
358.5055 | 266.5055 | 480.8782 | 276.0849 | 235.3823 | 250.3282 | 272.0573 | 249.6691 | 234.3505 | 342.4377
359.5069 | 267.5069 | 481.0701 | 276.8345 | 236.278 | 251.1523 | 272.6743 | 250.1714 | 234.9178 | 343.0105
360.5084 | 268.5084 | 481.2764 | 277.5808 | 237.1772 | 251.9642 | 273.3051 | 250.7813 | 235.4967 | 343.5811
361.5098 | 269.5098 | 481.2432 | 278.3195 | 238.0708 | 252.7824 | 273.9483 | 251.3613 | 236.0724 | 344.1182
362.5113 | 270.5113 | 480.9997 | 279.0708 | 238.9628 | 253.5935 | 274.586 | 251.8835 | 236.723 | 344.6605
363.5127 | 271.5127 | 480.825 | 279.8216 | 239.8358 | 254.4107 | 275.2502 | 252.4225 | 237.2436 | 345.1989
364.5141 | 272.5141 | 480.6869 | 280.5729 | 240.7145 | 255.2137 | 275.9099 | 252.9139 | 237.819 | 345.747
365.5156 | 273.5156 | 480.4738 | 281.3345 | 241.5736 | 256.0037 | 276.5643 | 253.3967 | 238.432 | 346.2898
366.507 | 274.507 | 480.262 | 282.0912 | 242.4447 | 256.7966 | 277.2246 | 253.9075 | 238.9944 | 346.8103
367.5085 | 275.5085 | 480.1641 | 282.8486 | 243.3175 | 257.58 | 277.8814 | 254.4046 | 239.5618 | 347.3267
368.5099 | 276.5099 | 480.1646 | 283.5881 | 244.1723 | 258.3479 | 278.5345 | 254.8945 | 240.2338 | 347.8593
369.5113 | 277.5113 | 480.1623 | 284.3142 | 245.0397 | 259.1383 | 279.1775 | 255.4381 | 240.7278 | 348.3676
370.5128 | 278.5128 | 480.2051 | 285.0218 | 245.9096 | 259.906 | 279.8177 | 255.9788 | 241.298 | 348.8585
371.5142 | 279.5142 | 480.2976 | 285.7365 | 246.7576 | 260.6693 | 280.4426 | 256.4987 | 241.8258 | 349.374
372.5056 | 280.5056 | 480.3234 | 286.4425 | 247.615 | 261.4338 | 281.0992 | 257.0472 | 242.4273 | 349.8681
373.5071 | 281.5071 | 480.1779 | 287.1469 | 248.4387 | 262.1866 | 281.7215 | 257.5361 | 242.945 | 350.3622
374.5085 | 282.5085 | 480.0476 | 287.8473 | 249.2864 | 262.9366 | 282.3581 | 258.0269 | 243.5168 | 350.8472
375.51 | 283.51 | 479.9288 | 288.5509 | 250.137 | 263.6962 | 283.0259 | 258.5227 | 243.9808 | 351.3043
376.5114 | 284.5114 | 479.9226 | 289.225 | 250.973 | 264.4196 | 283.6644 | 258.9948 | 244.5278 | 351.774
377.5128 | 285.5128 | 479.9713 | 289.9123 | 251.8095 | 265.1298 | 284.3047 | 259.4675 | 245.0437 | 352.2216
378.5143 | 286.5143 | 479.9197 | 290.5747 | 252.6361 | 265.8322 | 284.944 | 259.9961 | 245.6315 | 352.6891
379.5057 | 287.5057 | 479.7679 | 291.2057 | 253.4591 | 266.5394 | 285.583 | 260.4924 | 246.1636 | 353.1135
380.5071 | 288.5071 | 479.5547 | 291.8159 | 254.2881 | 267.2509 | 286.2307 | 260.9366 | 246.6843 | 353.5671
381.5086 | 289.5086 | 479.4423 | 292.4443 | 255.1128 | 267.9555 | 286.8751 | 261.3771 | 247.237 | 354.0157
382.51 | 290.51 | 479.3995 | 293.0772 | 255.907 | 268.687 | 287.5162 | 262.0241 | 247.7215 | 354.4645
383.5115 | 291.5115 | 479.5369 | 293.726 | 256.7142 | 269.4125 | 288.1543 | 262.5899 | 248.1976 | 354.9057
384.5129 | 292.5129 | 479.6747 | 294.3963 | 257.5146 | 270.1468 | 288.7501 | 263.0892 | 248.7913 | 355.3228
385.5143 | 293.5143 | 479.7146 | 295.0518 | 258.3056 | 270.8675 | 289.3819 | 263.4133 | 249.2639 | 355.7433
386.5158 | 294.5158 | 479.6722 | 295.6879 | 259.099 | 271.5761 | 289.9856 | 263.7794 | 249.7197 | 356.1761
387.5072 | 295.5072 | 479.5638 | 296.3257 | 259.8805 | 272.2721 | 290.5958 | 264.298 | 250.2459 | 356.6026
388.5086 | 296.5086 | 479.5085 | 296.9521 | 260.6681 | 272.9579 | 291.1858 | 264.6943 | 250.765 | 357.0123
389.5101 | 297.5101 | 479.5404 | 297.5573 | 261.4366 | 273.6432 | 291.7933 | 265.2532 | 251.2353 | 357.4323
390.5115 | 298.5115 | 479.4513 | 298.1823 | 262.2191 | 274.3279 | 292.3958 | 265.7177 | 251.735 | 357.8413
391.513 | 299.513 | 479.353 | 298.7955 | 262.9882 | 275.0146 | 293.0072 | 266.1663 | 252.203 | 358.2541
392.5144 | 300.5144 | 479.3095 | 299.4097 | 263.7629 | 275.7103 | 293.5999 | 266.5698 | 252.6857 | 358.6758
393.5058 | 301.5058 | 479.3361 | 300.0114 | 264.5217 | 276.4139 | 294.1873 | 266.9413 | 253.1571 | 359.0506
394.5073 | 302.5073 | 479.4965 | 300.5333 | 265.2814 | 277.1258 | 294.7696 | 267.3641 | 253.5969 | 359.4515
395.5087 | 303.5087 | 479.6032 | 300.9772 | 266.0393 | 277.8436 | 295.3652 | 267.6373 | 254.1848 | 359.8536
396.5102 | 304.5102 | 479.6559 | 301.4213 | 266.7851 | 278.5305 | 295.9557 | 268.2078 | 254.6681 | 360.2339
397.5116 | 305.5116 | 479.6546 | 301.9071 | 267.5214 | 279.2002 | 296.5547 | 268.7092 | 255.1576 | 360.6323
398.513 | 306.513 | 479.6223 | 302.4059 | 268.2793 | 279.8765 | 297.1441 | 269.204 | 255.6141 | 361.0079
399.5145 | 307.5145 | 479.6309 | 302.9321 | 269.0276 | 280.5615 | 297.7363 | 269.6785 | 256.2011 | 361.375
400.5059 | 308.5059 | 479.6262 | 303.4674 | 269.7617 | 281.2568 | 298.2978 | 270.1007 | 256.6721 | 361.7827
401.5073 | 309.5073 | 479.8224 | 304.0389 | 270.5025 | 281.909 | 298.803 | 270.57 | 257.2412 | 362.179
402.5088 | 310.5088 | 479.9322 | 304.5326 | 271.2349 | 282.5761 | 299.4464 | 270.9028 | 257.7542 | 362.5614
403.5102 | 311.5102 | 479.9507 | 304.9989 | 271.9755 | 283.2609 | 300.0822 | 271.2535 | 258.2359 | 362.923
404.5117 | 312.5117 | 480.0142 | 305.4847 | 272.7114 | 284.0021 | 300.6687 | 271.6166 | 258.6861 | 363.3034
405.5131 | 313.5131 | 479.9726 | 305.9823 | 273.4446 | 284.7756 | 301.2538 | 272.1005 | 259.0778 | 363.697
406.5145 | 314.5145 | 479.9684 | 306.4474 | 274.1652 | 285.5698 | 301.8404 | 272.5609 | 259.5373 | 364.0522
407.516 | 315.516 | 480.0312 | 306.9211 | 274.8857 | 286.4143 | 302.3559 | 272.9283 | 260.037 | 364.4293
408.5074 | 316.5074 | 480.0263 | 307.3257 | 275.6056 | 287.26 | 302.9198 | 273.4914 | 260.5086 | 364.7787
409.5088 | 317.5088 | 480.1354 | 307.7273 | 276.3305 | 288.0944 | 303.4756 | 274.0481 | 260.9675 | 365.1479
410.5103 | 318.5103 | 480.1373 | 308.1212 | 277.0384 | 288.9278 | 304.0646 | 274.4427 | 261.4623 | 365.508
411.5117 | 319.5117 | 480.2262 | 308.5215 | 277.7468 | 289.7411 | 304.6259 | 274.9161 | 261.8991 | 365.8341
412.5132 | 320.5132 | 480.4718 | 308.9525 | 278.4636 | 290.5422 | 305.2063 | 275.2839 | 262.4009 | 366.1699
413.5146 | 321.5146 | 480.6409 | 309.4306 | 279.1713 | 291.3206 | 305.7901 | 275.6837 | 262.8988 | 366.5393
414.506 | 322.506 | 480.6051 | 309.9068 | 279.8604 | 292.0936 | 306.3615 | 276.1388 | 263.4249 | 366.846
415.5075 | 323.5075 | 480.6552 | 310.3642 | 280.5594 | 292.8186 | 306.9211 | 276.6893 | 263.9359 | 367.1861
416.5089 | 324.5089 | 480.7928 | 310.7845 | 281.2445 | 293.5062 | 307.4908 | 277.3481 | 264.3735 | 367.5219
417.5104 | 325.5104 | 480.8726 | 311.2157 | 281.9417 | 294.1775 | 308.0481 | 278.0103 | 264.8614 | 367.8631
418.5118 | 326.5118 | 480.9959 | 311.6914 | 282.634 | 294.8291 | 308.6192 | 278.4521 | 265.3149 | 368.1905
419.5132 | 327.5132 | 481.067 | 312.1875 | 283.3024 | 295.4856 | 309.2015 | 278.8375 | 265.8058 | 368.5142
420.5147 | 328.5147 | 481.2146 | 312.6553 | 283.983 | 296.1285 | 309.788 | 279.046 | 266.2535 | 368.8464
421.5061 | 329.5061 | 481.1952 | 313.1318 | 284.6605 | 296.7731 | 310.3668 | 279.474 | 266.6905 | 369.1637
422.5075 | 330.5075 | 481.2685 | 313.7073 | 285.318 | 297.4092 | 310.9471 | 279.9967 | 267.109 | 369.4722
423.509 | 331.509 | 481.2962 | 314.2868 | 285.9866 | 298.0495 | 311.5247 | 280.4986 | 267.5249 | 369.8115
424.5104 | 332.5104 | 481.2406 | 314.8062 | 286.6574 | 298.7056 | 312.1077 | 280.9297 | 267.9874 | 370.1249
425.5119 | 333.5119 | 481.2137 | 315.3025 | 287.3006 | 299.3407 | 312.6706 | 281.3501 | 268.4344 | 370.4434
426.5133 | 334.5133 | 481.1533 | 315.7383 | 287.9636 | 299.9652 | 313.2147 | 281.7216 | 268.9011 | 370.7663
427.5147 | 335.5147 | 481.1644 | 316.0482 | 288.599 | 300.5836 | 313.766 | 281.9987 | 269.3183 | 371.0855
428.5162 | 336.5162 | 481.0115 | 316.2734 | 289.2674 | 301.2052 | 314.3362 | 282.4542 | 269.7585 | 371.3976
429.5076 | 337.5076 | 480.912 | 316.5232 | 289.9129 | 301.8061 | 314.8719 | 282.9334 | 270.1596 | 371.7046
430.509 | 338.509 | 481.0028 | 316.8137 | 290.5579 | 302.4176 | 315.4048 | 283.2907 | 270.6371 | 371.9701
431.5105 | 339.5105 | 480.9054 | 317.207 | 291.2016 | 303.0286 | 315.9448 | 283.6256 | 271.169 | 372.2697
432.5119 | 340.5119 | 480.9245 | 317.7853 | 291.8351 | 303.652 | 316.4816 | 283.8886 | 271.6152 | 372.529
433.5134 | 341.5134 | 480.9104 | 318.1908 | 292.4812 | 304.2938 | 317.0274 | 284.2442 | 272.0067 | 372.8048
434.5148 | 342.5148 | 480.9396 | 318.7112 | 293.1251 | 304.9445 | 317.5541 | 284.4646 | 272.4589 | 373.0854
435.5062 | 343.5062 | 480.8263 | 319.1146 | 293.7745 | 305.5782 | 318.0611 | 284.8921 | 272.896 | 373.3854
436.5077 | 344.5077 | 480.6018 | 319.5732 | 294.4096 | 306.1962 | 318.5492 | 285.2019 | 273.317 | 373.6565
437.5091 | 345.5091 | 480.4396 | 319.7885 | 295.0484 | 306.8189 | 319.0454 | 285.5667 | 273.7052 | 373.9286
438.5105 | 346.5105 | 480.3555 | 319.7419 | 295.6766 | 307.4332 | 319.5249 | 285.9483 | 274.1379 | 374.1877
439.512 | 347.512 | 480.1531 | 319.6775 | 296.3082 | 308.0518 | 320.0225 | 286.3808 | 274.5607 | 374.445
440.5134 | 348.5134 | 480.1996 | 319.8524 | 296.9348 | 308.6501 | 320.5198 | 286.8766 | 274.9214 | 374.7016
441.5049 | 349.5049 | 480.3365 | 319.9648 | 297.5711 | 309.2698 | 320.9953 | 287.4142 | 275.3422 | 374.984
442.5063 | 350.5063 | 480.3483 | 319.9596 | 298.1797 | 309.8722 | 321.4867 | 287.8676 | 275.7866 | 375.2331
443.5077 | 351.5077 | 480.1671 | 320.0528 | 298.795 | 310.4529 | 321.998 | 288.2231 | 276.2604 | 375.4798
444.5092 | 352.5092 | 480.2212 | 320.3017 | 299.4044 | 311.0291 | 322.4922 | 288.6872 | 276.5995 | 375.7292
445.5106 | 353.5106 | 480.3409 | 320.6595 | 300.0083 | 311.5661 | 323.0189 | 289.0093 | 277.0416 | 375.9816
446.5121 | 354.5121 | 480.3692 | 321.007 | 300.617 | 312.1004 | 323.5315 | 289.4119 | 277.4218 | 376.2335
447.5135 | 355.5135 | 480.2542 | 321.291 | 301.2043 | 312.6457 | 324.0298 | 289.6921 | 277.8874 | 376.4505
448.5049 | 356.5049 | 480.1722 | 321.5157 | 301.8067 | 313.2092 | 324.5103 | 290.0671 | 278.262 | 376.7006
449.5164 | 357.5164 | 480.0219 | 321.7392 | 302.3972 | 313.7948 | 324.9985 | 290.449 | 278.6047 | 376.9533
450.5078 | 358.5078 | 479.9513 | 321.8889 | 302.9857 | 314.3669 | 325.4554 | 290.8592 | 278.9773 | 377.2065
451.5092 | 359.5092 | 479.9007 | 322.0732 | 303.5557 | 314.9063 | 325.9225 | 291.1752 | 279.389 | 377.4526
452.5107 | 360.5107 | 479.8443 | 322.2417 | 304.1375 | 315.4497 | 326.362 | 291.5451 | 279.723 | 377.6885
453.5121 | 361.5121 | 479.9595 | 322.3953 | 304.7013 | 316.0011 | 326.7722 | 291.7958 | 280.1374 | 377.9335
454.5136 | 362.5136 | 480.1174 | 322.5696 | 305.2745 | 316.5655 | 327.1259 | 292.0995 | 280.4672 | 378.1506
455.515 | 363.515 | 480.0885 | 322.7718 | 305.8289 | 317.1032 | 327.4008 | 292.4072 | 280.8593 | 378.3583
456.5064 | 364.5064 | 480.1425 | 323.0002 | 306.3895 | 317.6338 | 327.6116 | 292.744 | 281.2105 | 378.5725
457.5079 | 365.5079 | 480.341 | 323.2484 | 306.9386 | 318.1468 | 327.794 | 293.3101 | 281.5833 | 378.7931
458.5093 | 366.5093 | 480.3127 | 323.5853 | 307.4811 | 318.6529 | 327.9927 | 293.8104 | 282.0519 | 379.0085
459.5107 | 367.5107 | 480.5083 | 323.9963 | 308.0325 | 319.1666 | 328.1315 | 294.207 | 282.4847 | 379.2487
460.5122 | 368.5122 | 480.7413 | 324.3381 | 308.5716 | 319.6551 | 328.2717 | 294.5406 | 282.8556 | 379.459
461.5136 | 369.5136 | 480.7902 | 324.6669 | 309.1005 | 320.1302 | 328.4612 | 294.7875 | 283.2329 | 379.6667
462.505 | 370.505 | 480.7604 | 324.9779 | 309.6349 | 320.6028 | 328.6983 | 295.0831 | 283.6453 | 379.8547
463.5065 | 371.5065 | 480.6871 | 325.3287 | 310.157 | 321.0988 | 328.9302 | 295.4887 | 284.0275 | 380.0456
464.5079 | 372.5079 | 480.7234 | 325.7068 | 310.6917 | 321.5652 | 329.1258 | 295.7788 | 284.3371 | 380.2569
465.5094 | 373.5094 | 480.8421 | 326.0975 | 311.2152 | 322.0285 | 329.4192 | 296.0705 | 284.8693 | 380.4492
466.5108 | 374.5108 | 480.7839 | 326.4556 | 311.7191 | 322.5821 | 329.1447 | 296.3823 | 285.2729 | 380.6473
467.5122 | 375.5122 | 480.6891 | 326.827 | 312.2416 | 323.208 | 328.7811 | 296.848 | 285.6135 | 380.837
468.5137 | 376.5137 | 480.6828 | 327.1842 | 312.7473 | 323.8211 | 328.5677 | 297.389 | 286.0669 | 381.0134
469.5051 | 377.5051 | 480.7507 | 327.5529 | 313.2422 | 324.4341 | 328.4125 | 297.803 | 286.5634 | 381.1934
470.5166 | 378.5166 | 480.6543 | 327.9281 | 313.7516 | 325.0667 | 328.3719 | 298.2018 | 286.9477 | 381.3847
471.538 | 379.538 | 480.6203 | 328.2912 | 314.2505 | 325.7084 | 328.4118 | 298.4866 | 287.3917 | 381.5865
472.5094 | 380.5094 | 480.5194 | 328.6351 | 314.7477 | 326.3291 | 328.4905 | 298.7222 | 287.7951 | 381.7747
473.5109 | 381.5109 | 480.3171 | 328.9977 | 315.2394 | 326.9496 | 328.6153 | 299.0329 | 288.1281 | 381.9515
474.5123 | 382.5123 | 480.1716 | 329.3395 | 315.7296 | 327.5464 | 328.768 | 299.2933 | 288.539 | 382.1143
475.5138 | 383.5138 | 480.2429 | 329.6604 | 316.2261 | 328.1155 | 328.9579 | 299.638 | 288.8852 | 382.298
476.5152 | 384.5152 | 480.2065 | 330.0051 | 316.712 | 328.6708 | 329.1603 | 300.0972 | 289.2812 | 382.4864
477.5066 | 385.5066 | 480.0794 | 330.358 | 317.1808 | 329.2154 | 329.4039 | 300.407 | 289.673 | 382.6568
478.5081 | 386.5081 | 479.79 | 330.7294 | 317.6573 | 329.7604 | 329.667 | 300.7434 | 290.0986 | 382.8058
479.5095 | 387.5095 | 479.6977 | 331.119 | 318.1339 | 330.2961 | 329.9468 | 301.0783 | 290.5073 | 382.9486
480.5109 | 388.5109 | 479.7173 | 331.4758 | 318.5939 | 330.8253 | 330.2249 | 301.4675 | 290.9099 | 383.0974
481.5124 | 389.5124 | 479.5844 | 331.8122 | 319.0665 | 331.3601 | 330.5353 | 301.8096 | 291.266 | 383.2415
482.5138 | 390.5138 | 479.4244 | 332.1213 | 319.518 | 331.8889 | 330.8381 | 302.2482 | 291.5712 | 383.3702
483.5052 | 391.5052 | 479.4294 | 332.443 | 319.9695 | 332.4149 | 331.1387 | 302.6547 | 291.9576 | 383.5164
484.5067 | 392.5067 | 479.3696 | 332.7871 | 320.4299 | 332.9143 | 331.4484 | 302.961 | 292.3 | 383.6503
485.5081 | 393.5081 | 479.2056 | 333.113 | 320.8666 | 333.3723 | 331.7536 | 303.217 | 292.6517 | 383.7643
486.5096 | 394.5096 | 479.0301 | 333.4189 | 321.3069 | 333.8279 | 332.0603 | 303.5565 | 293.073 | 383.8894
487.511 | 395.511 | 478.9214 | 333.7614 | 321.7364 | 334.272 | 332.3967 | 304.0243 | 293.4882 | 384.004
488.5124 | 396.5124 | 478.7596 | 334.0971 | 322.177 | 334.7129 | 332.7578 | 304.3115 | 293.8941 | 384.1283
489.5139 | 397.5139 | 478.6957 | 334.4264 | 322.598 | 335.1159 | 333.1459 | 304.5494 | 294.2791 | 384.2559
490.5153 | 398.5153 | 478.7574 | 334.7637 | 323.0256 | 335.5171 | 333.5326 | 304.8481 | 294.6995 | 384.405
491.5168 | 399.5168 | 478.8172 | 335.0722 | 323.4362 | 335.8911 | 333.9165 | 305.2291 | 295.0518 | 384.5304
492.5082 | 400.5082 | 478.8866 | 335.3644 | 323.8514 | 336.2618 | 334.3006 | 305.5212 | 295.3837 | 384.6544
493.5096 | 401.5096 | 479.0423 | 335.6502 | 324.2681 | 336.6214 | 334.6921 | 305.8636 | 295.7126 | 384.7588
494.5111 | 402.5111 | 478.9878 | 335.9577 | 324.6852 | 337.0031 | 335.0392 | 306.0971 | 296.0602 | 384.8697
495.5125 | 403.5125 | 479.0418 | 336.2381 | 325.0785 | 337.3686 | 335.381 | 306.3748 | 296.3788 | 384.9527
496.514 | 404.514 | 479.3269 | 336.515 | 325.4945 | 337.7216 | 335.7417 | 306.6551 | 296.7456 | 385.0763
497.5154 | 405.5154 | 479.3755 | 336.7973 | 325.8856 | 338.0571 | 336.0859 | 306.9299 | 297.1121 | 385.1596
498.5068 | 406.5068 | 479.3626 | 337.0833 | 326.2942 | 338.3667 | 336.4654 | 307.2177 | 297.4531 | 385.2927
499.5083 | 407.5083 | 479.4729 | 337.3673 | 326.6633 | 338.6864 | 336.8373 | 307.493 | 297.8296 | 385.4096
500.5097 | 408.5097 | 479.623 | 337.6507 | 327.0412 | 338.9783 | 337.2175 | 307.7613 | 298.1554 | 385.5221
501.5111 | 409.5111 | 479.6861 | 337.9364 | 327.4175 | 339.256 | 337.5656 | 308.0758 | 298.525 | 385.6483
502.5126 | 410.5126 | 479.621 | 338.232 | 327.7993 | 339.5436 | 337.9274 | 308.2517 | 298.9008 | 385.751
503.514 | 411.514 | 479.787 | 338.5043 | 328.1633 | 339.8004 | 338.2877 | 308.5216 | 299.2426 | 385.8651
504.5054 | 412.5054 | 479.8854 | 338.7466 | 328.5396 | 340.0476 | 338.6215 | 308.8825 | 299.6166 | 385.976
505.5069 | 413.5069 | 479.8694 | 338.9721 | 328.9054 | 340.2941 | 338.9749 | 309.2116 | 300.0338 | 386.0944
506.5083 | 414.5083 | 479.8547 | 339.2209 | 329.2642 | 340.5354 | 339.3008 | 309.5918 | 300.398 | 386.1873
507.5098 | 415.5098 | 479.8486 | 339.4955 | 329.6222 | 340.7781 | 339.6119 | 309.7655 | 300.769 | 386.3051
508.5112 | 416.5112 | 479.987 | 339.7664 | 329.9798 | 341.0383 | 339.9313 | 310.0264 | 301.1154 | 386.4091
509.5126 | 417.5126 | 480.1325 | 340.0344 | 330.3381 | 341.276 | 340.2402 | 310.2507 | 301.4247 | 386.5247
510.5141 | 418.5141 | 480.1956 | 340.2935 | 330.6772 | 341.5126 | 340.5524 | 310.5756 | 301.7736 | 386.6319
511.5155 | 419.5155 | 480.0682 | 340.5478 | 331.0474 | 341.7457 | 340.829 | 310.7913 | 302.189 | 386.7192
512.5069 | 420.5069 | 479.9888 | 340.8012 | 331.373 | 341.9732 | 341.1412 | 311.1236 | 302.6208 | 386.8115
513.5084 | 421.5084 | 479.867 | 341.0451 | 331.7274 | 342.1939 | 341.4417 | 311.4724 | 302.8425 | 386.9035
514.5098 | 422.5098 | 479.8612 | 341.2895 | 332.0606 | 342.4022 | 341.7498 | 311.7879 | 303.1291 | 387.0002
515.5113 | 423.5113 | 479.8338 | 341.5403 | 332.3993 | 342.6291 | 342.0414 | 312.0384 | 303.3985 | 387.1182
516.5127 | 424.5127 | 479.7108 | 341.7596 | 332.7359 | 342.8334 | 342.3077 | 312.2812 | 303.7219 | 387.207
517.5141 | 425.5141 | 479.61 | 342.0011 | 333.0612 | 343.0342 | 342.5598 | 312.4911 | 303.984 | 387.2981
518.5056 | 426.5056 | 479.4487 | 342.2297 | 333.384 | 343.2213 | 342.8087 | 312.6819 | 304.2871 | 387.4037
519.507 | 427.507 | 479.3816 | 342.4851 | 333.7232 | 343.4047 | 343.0479 | 313.0041 | 304.5388 | 387.4753
520.5085 | 428.5085 | 479.308 | 342.7212 | 334.0312 | 343.6006 | 343.2781 | 313.3785 | 304.822 | 387.5789
521.5099 | 429.5099 | 479.3405 | 342.9685 | 334.3469 | 343.7866 | 343.5153 | 313.7711 | 305.1663 | 387.6604
522.5113 | 430.5113 | 479.3322 | 343.2074 | 334.6723 | 343.9693 | 343.7399 | 314.1374 | 305.4373 | 387.7484
523.5128 | 431.5128 | 479.2304 | 343.4377 | 334.9936 | 344.1488 | 343.9706 | 314.3956 | 305.705 | 387.83
524.5142 | 432.5142 | 479.139 | 343.6535 | 335.3054 | 344.3279 | 344.1817 | 314.7476 | 306.0463 | 387.9134
525.5056 | 433.5056 | 479.1343 | 343.8911 | 335.607 | 344.4972 | 344.4006 | 315.0986 | 306.2764 | 387.9835
526.5071 | 434.5071 | 479.1733 | 344.0998 | 335.9094 | 344.6688 | 344.5967 | 315.5847 | 306.6476 | 388.05
527.5085 | 435.5085 | 479.1812 | 344.3046 | 336.2095 | 344.8411 | 344.7949 | 315.7853 | 306.9395 | 388.1281
528.51 | 436.51 | 479.4052 | 344.5165 | 336.502 | 345.0043 | 344.9719 | 316.0556 | 307.2563 | 388.2164
529.5114 | 437.5114 | 479.5307 | 344.7215 | 336.8127 | 345.1525 | 345.1532 | 316.2597 | 307.6467 | 388.2904
530.5128 | 438.5128 | 479.6696 | 344.9321 | 337.0992 | 345.3111 | 345.3171 | 316.5713 | 307.8941 | 388.3555
531.5143 | 439.5143 | 479.6622 | 345.1379 | 337.3883 | 345.4563 | 345.4903 | 316.9062 | 308.2806 | 388.4427
532.5057 | 440.5057 | 479.8167 | 345.3422 | 337.6718 | 345.6016 | 345.6777 | 317.2801 | 308.5509 | 388.5192
533.5071 | 441.5071 | 479.8893 | 345.553 | 337.961 | 345.7444 | 345.8439 | 317.4874 | 308.8813 | 388.5938
534.5086 | 442.5086 | 479.8864 | 345.7606 | 338.254 | 345.9012 | 346.0258 | 317.7836 | 309.1629 | 388.6683
535.51 | 443.51 | 479.8111 | 345.9523 | 338.5356 | 346.0488 | 346.2006 | 318.0152 | 309.5022 | 388.728
536.5115 | 444.5115 | 479.8383 | 346.1477 | 338.8072 | 346.2014 | 346.3614 | 318.262 | 309.802 | 388.8065
537.5129 | 445.5129 | 479.9382 | 346.3254 | 339.0828 | 346.3616 | 346.529 | 318.4159 | 310.0945 | 388.8747
538.5143 | 446.5143 | 480.0463 | 346.5092 | 339.3461 | 346.5129 | 346.6931 | 318.6247 | 310.3885 | 388.9499
539.5158 | 447.5158 | 480.0691 | 346.6946 | 339.6229 | 346.6722 | 346.861 | 318.8978 | 310.6736 | 389.0284
540.5172 | 448.5172 | 480.0652 | 346.8692 | 339.8947 | 346.8224 | 347.0061 | 319.2479 | 310.9359 | 389.1168
541.5087 | 449.5087 | 480.0435 | 347.0632 | 340.1451 | 346.988 | 347.1649 | 319.5702 | 311.242 | 389.1838
542.5101 | 450.5101 | 480.053 | 347.2499 | 340.4159 | 347.15 | 347.3186 | 320.0139 | 311.5616 | 389.2453
543.5115 | 451.5115 | 480.1666 | 347.4307 | 340.6774 | 347.311 | 347.4791 | 320.2729 | 311.8496 | 389.3207
544.513 | 452.513 | 480.2541 | 347.6212 | 340.9368 | 347.4781 | 347.6336 | 320.5364 | 312.2022 | 389.4392
545.5144 | 453.5144 | 480.5937 | 347.7936 | 341.1769 | 347.6353 | 347.7812 | 320.7685 | 312.5521 | 389.5243
546.5058 | 454.5058 | 480.7212 | 347.9732 | 341.44 | 347.7924 | 347.9633 | 320.9945 | 312.8491 | 389.6019
547.5073 | 455.5073 | 480.6155 | 348.164 | 341.7042 | 347.9626 | 348.1118 | 321.21 | 313.1008 | 389.6933
548.5087 | 456.5087 | 480.4938 | 348.3753 | 341.9523 | 348.1307 | 348.278 | 321.3073 | 313.4563 | 389.7759
549.5102 | 457.5102 | 480.4331 | 348.569 | 342.2082 | 348.2971 | 348.4374 | 321.652 | 313.7313 | 389.8521
550.5116 | 458.5116 | 480.4867 | 348.7607 | 342.4544 | 348.4543 | 348.5897 | 321.8089 | 314.0056 | 389.9211
551.513 | 459.513 | 480.4609 | 348.9499 | 342.7043 | 348.6178 | 348.7275 | 322.0297 | 314.2965 | 390.0112
552.5145 | 460.5145 | 480.5501 | 349.1389 | 342.9589 | 348.7838 | 348.8866 | 322.2925 | 314.565 | 390.0879
553.5059 | 461.5059 | 480.6502 | 349.3067 | 343.1934 | 348.9487 | 349.0393 | 322.5587 | 314.8544 | 390.175
554.5073 | 462.5073 | 480.7953 | 349.4845 | 343.4415 | 349.1219 | 349.1813 | 322.8538 | 315.1766 | 390.2871
555.5088 | 463.5088 | 480.8418 | 349.6636 | 343.6791 | 349.2803 | 349.3442 | 323.071 | 315.5131 | 390.3785
556.5102 | 464.5102 | 480.8928 | 349.8418 | 343.9088 | 349.4444 | 349.4887 | 323.3122 | 315.8447 | 390.4574
557.5117 | 465.5117 | 480.923 | 350.026 | 344.1616 | 349.6098 | 349.6367 | 323.5472 | 316.0819 | 390.5151
558.5131 | 466.5131 | 480.9892 | 350.2068 | 344.3865 | 349.7674 | 349.797 | 323.7354 | 316.4374 | 390.6287
559.5145 | 467.5145 | 480.9855 | 350.4053 | 344.6186 | 349.9241 | 349.9409 | 324.0009 | 316.7255 | 390.696
560.506 | 468.506 | 481.0826 | 350.5927 | 344.8486 | 350.0792 | 350.0789 | 324.0775 | 317.0375 | 390.7893
561.5074 | 469.5074 | 481.2294 | 350.7843 | 345.0844 | 350.2288 | 350.2285 | 324.0588 | 317.3709 | 390.8646
562.5088 | 470.5088 | 481.4587 | 350.9627 | 345.319 | 350.3768 | 350.3739 | 324.1886 | 317.6623 | 390.9641
563.5103 | 471.5103 | 481.6755 | 351.1381 | 345.5477 | 350.5183 | 350.5259 | 324.3804 | 317.8803 | 391.0432
564.5117 | 472.5117 | 481.9805 | 351.3265 | 345.7789 | 350.6758 | 350.6712 | 324.7651 | 318.1842 | 391.1472
565.5132 | 473.5132 | 481.9908 | 351.5202 | 346.0069 | 350.8225 | 350.7995 | 325.0086 | 318.4902 | 391.2358
566.5146 | 474.5146 | 482.0997 | 351.7195 | 346.2407 | 350.9577 | 350.9589 | 325.324 | 318.7309 | 391.3079
567.506 | 475.506 | 482.2106 | 351.9092 | 346.4612 | 351.1131 | 351.1061 | 325.6522 | 319.0367 | 391.3972
568.5075 | 476.5075 | 482.2777 | 352.092 | 346.6904 | 351.2479 | 351.255 | 325.9889 | 319.2747 | 391.4716
569.5089 | 477.5089 | 482.3664 | 352.2662 | 346.9145 | 351.4036 | 351.4118 | 326.2832 | 319.5775 | 391.5455
570.5104 | 478.5104 | 482.347 | 352.4511 | 347.1443 | 351.5419 | 351.555 | 326.4728 | 319.826 | 391.6452
571.5118 | 479.5118 | 482.0528 | 352.6393 | 347.3707 | 351.6885 | 351.7153 | 326.5391 | 320.1356 | 391.7291
572.5132 | 480.5132 | 481.8394 | 352.8305 | 347.5799 | 351.8322 | 351.8526 | 326.7284 | 320.4169 | 391.812
573.5147 | 481.5147 | 481.6614 | 353.0222 | 347.7929 | 351.9722 | 352.0028 | 326.9663 | 320.6209 | 391.8702
574.5061 | 482.5061 | 481.5914 | 353.2085 | 348.0095 | 352.112 | 352.1362 | 327.2732 | 320.9328 | 391.9404
575.5075 | 483.5075 | 481.4394 | 353.3893 | 348.231 | 352.2603 | 352.286 | 327.5793 | 321.2044 | 392.0282
576.509 | 484.509 | 481.2421 | 353.5743 | 348.4433 | 352.4051 | 352.4313 | 327.8409 | 321.4296 | 392.0826
577.5104 | 485.5104 | 481.1022 | 353.7587 | 348.6614 | 352.5455 | 352.5773 | 328.0797 | 321.7251 | 392.1549
578.5119 | 486.5119 | 480.9109 | 353.9367 | 348.8801 | 352.6817 | 352.7207 | 328.3086 | 322.0349 | 392.2233
579.5133 | 487.5133 | 480.7682 | 354.1175 | 349.0893 | 352.8275 | 352.8467 | 328.4479 | 322.2789 | 392.2922
580.5147 | 488.5147 | 480.6277 | 354.2986 | 349.3007 | 352.9648 | 352.9814 | 328.5953 | 322.4228 | 392.3648
581.5162 | 489.5162 | 480.4454 | 354.4756 | 349.4967 | 353.0943 | 353.1173 | 328.768 | 322.6536 | 392.4336
582.5076 | 490.5076 | 480.1672 | 354.6543 | 349.7123 | 353.2287 | 353.2558 | 328.9331 | 322.899 | 392.4654
583.509 | 491.509 | 479.915 | 354.8347 | 349.9211 | 353.3671 | 353.3939 | 329.0934 | 323.0815 | 392.5498
584.5105 | 492.5105 | 479.7065 | 355.0026 | 350.1222 | 353.4958 | 353.5152 | 329.2484 | 323.2716 | 392.5989
585.5119 | 493.5119 | 479.4649 | 355.1794 | 350.329 | 353.6378 | 353.6664 | 329.4435 | 323.4532 | 392.64
586.5134 | 494.5134 | 479.311 | 355.3449 | 350.5347 | 353.7672 | 353.7841 | 329.7247 | 323.6831 | 392.6982
587.5148 | 495.5148 | 479.1224 | 355.5252 | 350.7323 | 353.9078 | 353.9178 | 329.9506 | 323.9266 | 392.7687
588.5062 | 496.5062 | 478.9908 | 355.6902 | 350.9304 | 354.0426 | 354.046 | 330.2359 | 324.1789 | 392.821
589.5077 | 497.5077 | 478.9165 | 355.8563 | 351.1207 | 354.1761 | 354.1528 | 330.4247 | 324.3978 | 392.8885
590.5091 | 498.5091 | 478.9066 | 356.0245 | 351.3329 | 354.314 | 354.2684 | 330.6323 | 324.6361 | 392.9266
591.5106 | 499.5106 | 478.8918 | 356.1989 | 351.5264 | 354.4549 | 354.3896 | 330.7873 | 324.7959 | 392.9408
592.512 | 500.512 | 478.928 | 356.3817 | 351.7289 | 354.5825 | 354.5047 | 331.0373 | 324.9925 | 392.9801
593.5134 | 501.5134 | 478.8176 | 356.5679 | 351.9306 | 354.7173 | 354.6243 | 331.2154 | 325.2734 | 393.0285
594.5149 | 502.5149 | 478.6741 | 356.7546 | 352.1336 | 354.8566 | 354.7453 | 331.3706 | 325.4826 | 393.069
595.5063 | 503.5063 | 478.5751 | 356.9375 | 352.3212 | 354.9843 | 354.8557 | 331.5111 | 325.7224 | 393.0989
596.5077 | 504.5077 | 478.4953 | 357.113 | 352.5143 | 355.1156 | 354.9813 | 331.7837 | 325.9684 | 393.1211
597.5092 | 505.5092 | 478.6069 | 357.2904 | 352.7214 | 355.2441 | 355.0861 | 332.1305 | 326.142 | 393.1848
598.5106 | 506.5106 | 478.6668 | 357.4641 | 352.9043 | 355.3745 | 355.2153 | 332.4241 | 326.393 | 393.2201
599.5121 | 507.5121 | 478.9181 | 357.625 | 353.1023 | 355.5092 | 355.334 | 332.7989 | 326.581 | 393.2425
600.5135 | 508.5135 | 479.0438 | 357.7965 | 353.2892 | 355.6441 | 355.4565 | 332.9518 | 326.7662 | 393.269
601.5049 | 509.5049 | 479.074 | 357.9637 | 353.4854 | 355.7804 | 355.5704 | 333.1194 | 327.0116 | 393.3138
602.5064 | 510.5064 | 479.2258 | 358.136 | 353.6664 | 355.9117 | 355.6803 | 333.278 | 327.2276 | 393.3633
603.5078 | 511.5078 | 479.2832 | 358.3128 | 353.8526 | 356.0463 | 355.7982 | 333.4212 | 327.3463 | 393.4059
604.5092 | 512.5092 | 479.2318 | 358.4801 | 354.0513 | 356.1818 | 355.9151 | 333.6415 | 327.5711 | 393.4521
605.5107 | 513.5107 | 479.2191 | 358.651 | 354.239 | 356.3299 | 356.0418 | 333.8683 | 327.7715 | 393.5118
606.5121 | 514.5121 | 479.1883 | 358.8201 | 354.425 | 356.4672 | 356.162 | 334.043 | 328.0216 | 393.5564
607.5136 | 515.5136 | 479.2848 | 358.9939 | 354.6121 | 356.6118 | 356.2751 | 334.2214 | 328.1597 | 393.5685
608.515 | 516.515 | 479.2945 | 359.1661 | 354.7939 | 356.7519 | 356.412 | 334.4039 | 328.3374 | 393.6345
609.5064 | 517.5064 | 479.277 | 359.3361 | 354.9947 | 356.8908 | 356.5304 | 334.5314 | 328.5479 | 393.6688
610.5079 | 518.5079 | 479.2214 | 359.5065 | 355.1801 | 357.0262 | 356.6538 | 334.6703 | 328.7192 | 393.7135
611.5093 | 519.5093 | 479.3183 | 359.676 | 355.3721 | 357.1754 | 356.7838 | 334.847 | 328.9403 | 393.758
612.5107 | 520.5107 | 479.3487 | 359.8381 | 355.5454 | 357.3087 | 356.9102 | 335.0152 | 329.1294 | 393.824
613.5122 | 521.5122 | 479.3822 | 360.0067 | 355.7399 | 357.4512 | 357.03 | 335.2171 | 329.4493 | 393.8651
614.5136 | 522.5136 | 479.3584 | 360.1828 | 355.9078 | 357.5859 | 357.1519 | 335.3887 | 329.6622 | 393.916
615.5051 | 523.5051 | 479.4138 | 360.348 | 356.1102 | 357.7314 | 357.2612 | 335.544 | 329.7368 | 393.9627
616.5065 | 524.5065 | 479.4316 | 360.5195 | 356.2837 | 357.8705 | 357.3983 | 335.7367 | 329.9231 | 394.007
617.5079 | 525.5079 | 479.4126 | 360.6939 | 356.463 | 358.0136 | 357.5143 | 335.8645 | 330.0908 | 394.0629
618.5094 | 526.5094 | 479.4358 | 360.8572 | 356.6435 | 358.1511 | 357.6281 | 336.088 | 330.2851 | 394.1049
619.5108 | 527.5108 | 479.5384 | 361.0319 | 356.8306 | 358.2979 | 357.7433 | 336.2747 | 330.4907 | 394.173
620.5123 | 528.5123 | 479.5491 | 361.1962 | 357.0158 | 358.4412 | 357.8531 | 336.5168 | 330.678 | 394.2208
621.5137 | 529.5137 | 479.4739 | 361.3645 | 357.1792 | 358.5746 | 357.9719 | 336.6389 | 330.8416 | 394.2643
622.5151 | 530.5151 | 479.3751 | 361.5234 | 357.3678 | 358.709 | 358.0736 | 336.7927 | 331.0905 | 394.3157
623.5166 | 531.5166 | 479.2919 | 361.6837 | 357.5546 | 358.8505 | 358.1839 | 336.939 | 331.2561 | 394.3657
624.508 | 532.508 | 479.407 | 361.8409 | 357.7289 | 358.9868 | 358.3013 | 337.1009 | 331.484 | 394.3983
625.5094 | 533.5094 | 479.5694 | 361.9913 | 357.9078 | 359.1218 | 358.4108 | 337.2765 | 331.6371 | 394.4719
626.5109 | 534.5109 | 479.6006 | 362.1542 | 358.0895 | 359.266 | 358.5218 | 337.3427 | 331.8198 | 394.5126
627.5123 | 535.5123 | 479.5443 | 362.2964 | 358.2553 | 359.3996 | 358.6442 | 337.4671 | 331.9766 | 394.5788
628.5138 | 536.5138 | 479.3856 | 362.4488 | 358.4482 | 359.5391 | 358.7532 | 337.6139 | 332.21 | 394.6223
629.5152 | 537.5152 | 479.2585 | 362.598 | 358.6267 | 359.6771 | 358.8685 | 337.7286 | 332.4002 | 394.6727
630.5066 | 538.5066 | 479.2416 | 362.7542 | 358.7974 | 359.8095 | 358.9907 | 337.9127 | 332.5439 | 394.7237
631.5081 | 539.5081 | 479.4383 | 362.9037 | 358.9927 | 359.938 | 359.1107 | 338.1223 | 332.7233 | 394.7621
632.5095 | 540.5095 | 479.4809 | 363.0589 | 359.176 | 360.0655 | 359.23 | 338.3211 | 332.9424 | 394.7766
633.5109 | 541.5109 | 479.4701 | 363.2285 | 359.3687 | 360.1889 | 359.3448 | 338.5186 | 333.0311 | 394.8233
634.5124 | 542.5124 | 479.4118 | 363.3939 | 359.5479 | 360.3135 | 359.4513 | 338.7199 | 333.2274 | 394.8656
635.5138 | 543.5138 | 479.3818 | 363.5566 | 359.7289 | 360.4347 | 359.5566 | 338.7739 | 333.3294 | 394.8848
636.5153 | 544.5153 | 479.2412 | 363.7205 | 359.9238 | 360.5453 | 359.6835 | 338.8835 | 333.4756 | 394.9339
637.5067 | 545.5067 | 479.1271 | 363.8797 | 360.1163 | 360.6768 | 359.7885 | 339.017 | 333.6118 | 394.9561
638.5081 | 546.5081 | 479.1985 | 364.0395 | 360.288 | 360.7934 | 359.9123 | 339.0719 | 333.7322 | 394.9854
639.5096 | 547.5096 | 479.2924 | 364.1962 | 360.4864 | 360.9041 | 360.0054 | 339.1768 | 333.8404 | 395.0339
640.511 | 548.511 | 479.3691 | 364.3625 | 360.686 | 361.0293 | 360.1214 | 339.252 | 333.9764 | 395.0642
641.5124 | 549.5124 | 479.2973 | 364.5132 | 360.8728 | 361.1509 | 360.2381 | 339.4811 | 334.1043 | 395.1134
642.5139 | 550.5139 | 479.2288 | 364.6891 | 361.0513 | 361.2748 | 360.3559 | 339.648 | 334.2628 | 395.1216
643.5053 | 551.5053 | 479.2213 | 364.8639 | 361.2398 | 361.3977 | 360.4785 | 339.8175 | 334.4169 | 395.1588
644.5068 | 552.5068 | 479.2129 | 365.0412 | 361.4373 | 361.5192 | 360.5962 | 340.0242 | 334.5741 | 395.1877
645.5082 | 553.5082 | 479.2086 | 365.2122 | 361.625 | 361.6585 | 360.7159 | 340.2084 | 334.7198 | 395.2249
646.5096 | 554.5096 | 479.3682 | 365.3961 | 361.8214 | 361.7887 | 360.8323 | 340.398 | 334.8478 | 395.2665
647.5111 | 555.5111 | 479.541 | 365.5738 | 362.0078 | 361.9233 | 360.9625 | 340.4781 | 334.9802 | 395.2902
648.5125 | 556.5125 | 479.7796 | 365.7551 | 362.1929 | 362.0553 | 361.0842 | 340.6318 | 335.1318 | 395.3487
649.514 | 557.514 | 479.8682 | 365.9443 | 362.3939 | 362.2005 | 361.2099 | 340.8087 | 335.2806 | 395.3654
650.5054 | 558.5054 | 479.9014 | 366.1406 | 362.5864 | 362.339 | 361.3415 | 340.9342 | 335.4196 | 395.4218
651.5068 | 559.5068 | 479.7833 | 366.3365 | 362.7788 | 362.478 | 361.4746 | 341.0544 | 335.5641 | 395.4415
652.5083 | 560.5083 | 479.8227 | 366.5262 | 362.9805 | 362.6201 | 361.6022 | 341.2421 | 335.7278 | 395.4701
653.5097 | 561.5097 | 479.835 | 366.7325 | 363.1745 | 362.7591 | 361.7475 | 341.3915 | 335.9113 | 395.5048
654.5111 | 562.5111 | 479.8416 | 366.9233 | 363.3668 | 362.9064 | 361.8805 | 341.5837 | 336.0458 | 395.5523
655.5126 | 563.5126 | 479.8498 | 367.1206 | 363.5512 | 363.0422 | 362.0073 | 341.7153 | 336.2078 | 395.5782
656.514 | 564.514 | 479.6895 | 367.3237 | 363.7571 | 363.1854 | 362.1396 | 341.8395 | 336.3744 | 395.6146
657.5054 | 565.5054 | 479.5578 | 367.521 | 363.9568 | 363.3324 | 362.2782 | 341.9993 | 336.5594 | 395.6639
658.5069 | 566.5069 | 479.4516 | 367.7287 | 364.1483 | 363.4725 | 362.4224 | 342.1975 | 336.7552 | 395.7126
659.5083 | 567.5083 | 479.2825 | 367.9375 | 364.3355 | 363.6236 | 362.5603 | 342.312 | 336.9075 | 395.7426
660.5098 | 568.5098 | 479.1721 | 368.153 | 364.5207 | 363.7638 | 362.7037 | 342.4287 | 337.0554 | 395.7684
661.5112 | 569.5112 | 479.1136 | 368.3731 | 364.7274 | 363.909 | 362.8361 | 342.5834 | 337.2017 | 395.8011
662.5126 | 570.5126 | 479.1323 | 368.5801 | 364.9157 | 364.0537 | 362.9708 | 342.6451 | 337.3299 | 395.8569
663.5141 | 571.5141 | 479.0859 | 368.8056 | 365.1087 | 364.2042 | 363.1044 | 342.7676 | 337.4686 | 395.9015
664.5155 | 572.5155 | 479.2681 | 369.0399 | 365.3132 | 364.3549 | 363.2392 | 342.9212 | 337.6222 | 395.9237
665.517 | 573.517 | 479.3694 | 369.2663 | 365.5079 | 364.501 | 363.3823 | 343.0839 | 337.7597 | 395.9682
666.5084 | 574.5084 | 479.4804 | 369.4981 | 365.6979 | 364.6483 | 363.5167 | 343.2147 | 337.9488 | 396.0053
667.5098 | 575.5098 | 479.426 | 369.7297 | 365.9043 | 364.7976 | 363.6683 | 343.3983 | 338.1058 | 396.0443
668.5113 | 576.5113 | 479.4895 | 369.9525 | 366.0959 | 364.94 | 363.8017 | 343.5319 | 338.2642 | 396.0785
669.5127 | 577.5127 | 479.6027 | 370.1993 | 366.2868 | 365.0921 | 363.9434 | 343.6624 | 338.4534 | 396.1336
670.5142 | 578.5142 | 479.5534 | 370.4418 | 366.4716 | 365.2326 | 364.0964 | 343.7857 | 338.5784 | 396.1802
671.5156 | 579.5156 | 479.5513 | 370.6863 | 366.662 | 365.3897 | 364.2205 | 343.8304 | 338.7392 | 396.2377
672.507 | 580.507 | 479.6328 | 370.9334 | 366.8583 | 365.54 | 364.364 | 343.9063 | 338.856 | 396.2766
673.5085 | 581.5085 | 479.7262 | 371.1914 | 367.051 | 365.6938 | 364.5089 | 343.9534 | 339.0028 | 396.3249
674.5099 | 582.5099 | 479.8328 | 371.4609 | 367.2424 | 365.8438 | 364.6603 | 344.0473 | 339.193 | 396.3636
675.5113 | 583.5113 | 479.9273 | 371.7285 | 367.4199 | 365.9977 | 364.8132 | 344.1941 | 339.3867 | 396.413
676.5128 | 584.5128 | 479.8264 | 372.0072 | 367.6122 | 366.1531 | 364.964 | 344.3682 | 339.5597 | 396.4584
677.5142 | 585.5142 | 479.9966 | 372.3037 | 367.8033 | 366.3112 | 365.1074 | 344.5304 | 339.725 | 396.5262
678.5056 | 586.5056 | 480.0375 | 372.6176 | 367.9816 | 366.4659 | 365.2577 | 344.609 | 339.8717 | 396.578
679.5071 | 587.5071 | 479.9634 | 372.9033 | 368.1694 | 366.6234 | 365.4152 | 344.758 | 339.9941 | 396.6257
680.5085 | 588.5085 | 480.011 | 373.1918 | 368.3524 | 366.7816 | 365.5786 | 344.8716 | 340.132 | 396.6855
681.51 | 589.51 | 479.959 | 373.4824 | 368.5291 | 366.9395 | 365.7265 | 344.9655 | 340.2565 | 396.719
682.5214 | 590.5214 | 479.9673 | 373.78 | 368.7127 | 367.0995 | 365.8666 | 345.0896 | 340.4057 | 396.7684
683.5128 | 591.5128 | 479.8652 | 374.0546 | 368.8804 | 367.2612 | 366.0155 | 345.1382 | 340.5686 | 396.7954
684.5143 | 592.5143 | 479.703 | 374.3354 | 369.0459 | 367.4247 | 366.1698 | 345.2061 | 340.7309 | 396.8313
685.5157 | 593.5157 | 479.5575 | 374.6145 | 369.2059 | 367.5789 | 366.3291 | 345.2729 | 340.8581 | 396.8585
686.5071 | 594.5071 | 479.4406 | 374.9075 | 369.3802 | 367.7488 | 366.4751 | 345.3585 | 341.0612 | 396.8795
687.5086 | 595.5086 | 479.2591 | 375.196 | 369.5387 | 367.9171 | 366.6318 | 345.4195 | 341.1948 | 396.9118
688.51 | 596.51 | 479.0037 | 375.4874 | 369.7017 | 368.0826 | 366.7968 | 345.5587 | 341.3418 | 396.9651
689.5115 | 597.5115 | 478.8353 | 375.7851 | 369.8547 | 368.2467 | 366.9639 | 345.7039 | 341.5441 | 396.9861
690.5129 | 598.5129 | 478.6835 | 376.0843 | 370.0111 | 368.4128 | 367.1047 | 345.79 | 341.6501 | 397.0121
691.5143 | 599.5143 | 478.6829 | 376.3768 | 370.1632 | 368.5847 | 367.2516 | 345.8312 | 341.7344 | 397.069
692.5158 | 600.5158 | 478.6739 | 376.6616 | 370.294 | 368.7434 | 367.3997 | 345.9267 | 341.8735 | 397.1086
693.5072 | 601.5072 | 478.6766 | 376.9493 | 370.4365 | 368.9082 | 367.5431 | 346.0337 | 341.9808 | 397.1623
694.5087 | 602.5087 | 478.6736 | 377.2471 | 370.5778 | 369.0693 | 367.6901 | 346.1119 | 342.1445 | 397.1915
695.5101 | 603.5101 | 478.7763 | 377.5393 | 370.7012 | 369.2329 | 367.8389 | 346.156 | 342.3046 | 397.2364
696.5115 | 604.5115 | 478.7323 | 377.8018 | 370.8322 | 369.3887 | 367.9877 | 346.079 | 342.4434 | 397.2646
697.513 | 605.513 | 478.5608 | 378.0073 | 370.9512 | 369.5473 | 368.139 | 346.1021 | 342.5745 | 397.2961
698.5144 | 606.5144 | 478.52 | 378.1551 | 371.0818 | 369.7001 | 368.2802 | 346.1351 | 342.7204 | 397.3508
699.5058 | 607.5058 | 478.5022 | 378.3322 | 371.1976 | 369.8475 | 368.4357 | 346.1483 | 342.8318 | 397.3721
700.5073 | 608.5073 | 478.4662 | 378.5224 | 371.3106 | 369.9918 | 368.5773 | 346.2312 | 342.9749 | 397.419
701.5087 | 609.5087 | 478.3692 | 378.713 | 371.4207 | 370.1407 | 368.7283 | 346.3528 | 343.1166 | 397.4522
702.5102 | 610.5102 | 478.3665 | 378.9238 | 371.5323 | 370.2776 | 368.8829 | 346.4546 | 343.2649 | 397.4927
703.5116 | 611.5116 | 478.4951 | 379.1348 | 371.6313 | 370.4149 | 369.0365 | 346.5857 | 343.4354 | 397.5279
704.513 | 612.513 | 478.5551 | 379.3473 | 371.7378 | 370.5521 | 369.1916 | 346.7705 | 343.5698 | 397.5772
705.5145 | 613.5145 | 478.5844 | 379.574 | 371.8272 | 370.6877 | 369.3422 | 346.9757 | 343.713 | 397.6048
706.5059 | 614.5059 | 478.7614 | 379.7946 | 371.9107 | 370.8168 | 369.5057 | 347.1273 | 343.8496 | 397.6316
707.5073 | 615.5073 | 478.9731 | 380.005 | 372.0061 | 370.9558 | 369.6565 | 347.1852 | 344.0292 | 397.7019
708.5088 | 616.5088 | 479.2123 | 380.2142 | 372.0898 | 371.077 | 369.8039 | 347.2883 | 344.1504 | 397.7523
709.5102 | 617.5102 | 479.377 | 380.4308 | 372.1755 | 371.2085 | 369.969 | 347.4239 | 344.2906 | 397.7953
710.5117 | 618.5117 | 479.5741 | 380.6482 | 372.2514 | 371.3326 | 370.1155 | 347.5288 | 344.435 | 397.8316
711.5131 | 619.5131 | 479.7817 | 380.8726 | 372.3332 | 371.4548 | 370.2842 | 347.6088 | 344.5735 | 397.8724
712.5145 | 620.5145 | 479.9725 | 381.0904 | 372.4124 | 371.5823 | 370.4519 | 347.6737 | 344.7054 | 397.9223
713.516 | 621.516 | 479.9115 | 381.3219 | 372.4935 | 371.7 | 370.6105 | 347.7355 | 344.816 | 397.9486
714.5074 | 622.5074 | 479.8398 | 381.5376 | 372.5706 | 371.8105 | 370.7681 | 347.8208 | 344.926 | 398.0028
715.5089 | 623.5089 | 479.7923 | 381.7627 | 372.644 | 371.9239 | 370.9296 | 347.8719 | 345.0995 | 398.0539
716.5103 | 624.5103 | 479.7313 | 381.9738 | 372.7096 | 372.0348 | 371.0898 | 347.9299 | 345.2384 | 398.0835
717.5117 | 625.5117 | 479.7492 | 382.1882 | 372.7799 | 372.1372 | 371.2398 | 348.003 | 345.3386 | 398.1282
718.5232 | 626.5232 | 479.6976 | 382.3851 | 372.8465 | 372.2373 | 371.3964 | 348.0605 | 345.4687 | 398.1518
719.5146 | 627.5146 | 479.5937 | 382.5844 | 372.921 | 372.3428 | 371.5472 | 348.1243 | 345.6422 | 398.1946
720.506 | 628.506 | 479.6004 | 382.7871 | 372.9936 | 372.4371 | 371.6915 | 348.1322 | 345.7818 | 398.2373
721.5075 | 629.5075 | 479.5651 | 382.9925 | 373.0745 | 372.5326 | 371.8501 | 348.2114 | 345.8484 | 398.2837
722.5089 | 630.5089 | 479.7067 | 383.2067 | 373.1552 | 372.6258 | 372.0044 | 348.2825 | 345.9246 | 398.3308
723.5104 | 631.5104 | 479.8076 | 383.4107 | 373.2241 | 372.7128 | 372.1503 | 348.3605 | 346.0259 | 398.3592
724.5118 | 632.5118 | 479.668 | 383.6139 | 373.3033 | 372.7977 | 372.2848 | 348.4227 | 346.1386 | 398.3852
725.5132 | 633.5132 | 479.7307 | 383.8213 | 373.379 | 372.885 | 372.4188 | 348.4995 | 346.2068 | 398.44
726.5047 | 634.5047 | 479.7148 | 384.0259 | 373.4467 | 372.9772 | 372.5509 | 348.5593 | 346.3286 | 398.5027
727.5161 | 635.5161 | 479.7369 | 384.2228 | 373.538 | 373.0535 | 372.6779 | 348.6243 | 346.4159 | 398.543
728.5075 | 636.5075 | 479.5042 | 384.4224 | 373.6043 | 373.1434 | 372.8015 | 348.6716 | 346.5086 | 398.5811
729.509 | 637.509 | 479.4305 | 384.6214 | 373.6762 | 373.2332 | 372.9331 | 348.7014 | 346.5739 | 398.617
730.5104 | 638.5104 | 479.4158 | 384.8097 | 373.7515 | 373.3188 | 373.0477 | 348.7911 | 346.6687 | 398.6478
731.5119 | 639.5119 | 479.3836 | 385.0019 | 373.8361 | 373.405 | 373.1649 | 348.8443 | 346.7574 | 398.6809
732.5133 | 640.5133 | 479.3502 | 385.1962 | 373.8955 | 373.491 | 373.301 | 348.8541 | 346.8462 | 398.7193
733.5147 | 641.5147 | 479.32 | 385.3837 | 373.9774 | 373.5799 | 373.4072 | 348.8541 | 346.9487 | 398.7552
734.5062 | 642.5062 | 479.3571 | 385.5703 | 374.0605 | 373.6632 | 373.5308 | 348.7978 | 347.0648 | 398.8015
735.5076 | 643.5076 | 479.2873 | 385.7481 | 374.1292 | 373.7571 | 373.6586 | 348.7477 | 347.181 | 398.8277
736.509 | 644.509 | 479.247 | 385.9331 | 374.2128 | 373.8455 | 373.778 | 348.8257 | 347.2865 | 398.8581
737.5105 | 645.5105 | 479.1909 | 386.1205 | 374.2835 | 373.9413 | 373.8915 | 348.8913 | 347.3784 | 398.8964
738.5119 | 646.5119 | 479.0797 | 386.3002 | 374.3649 | 374.0379 | 374.0089 | 348.9634 | 347.44 | 398.9347
739.5134 | 647.5134 | 479.2092 | 386.4859 | 374.4466 | 374.1346 | 374.1269 | 349.0504 | 347.5823 | 398.9634
740.5148 | 648.5148 | 479.2819 | 386.6759 | 374.5328 | 374.2352 | 374.2481 | 349.1174 | 347.6602 | 398.9901
741.5062 | 649.5062 | 479.3831 | 386.8684 | 374.6173 | 374.3289 | 374.3543 | 349.1851 | 347.7664 | 399.0444
742.5077 | 650.5077 | 479.5171 | 387.0515 | 374.7034 | 374.4273 | 374.4664 | 349.2325 | 347.871 | 399.0793
743.5091 | 651.5091 | 479.6278 | 387.2416 | 374.781 | 374.5341 | 374.5774 | 349.3058 | 347.9614 | 399.1134
744.5106 | 652.5106 | 479.7199 | 387.4368 | 374.8699 | 374.641 | 374.6743 | 349.3484 | 348.0359 | 399.1529
745.512 | 653.512 | 479.807 | 387.6321 | 374.9656 | 374.7449 | 374.7821 | 349.4216 | 348.1169 | 399.1808
746.5134 | 654.5134 | 479.8934 | 387.8257 | 375.0614 | 374.8497 | 374.8929 | 349.5077 | 348.211 | 399.2204
747.5049 | 655.5049 | 479.9618 | 388.0244 | 375.1416 | 374.9565 | 374.9856 | 349.5295 | 348.3022 | 399.2601
748.5063 | 656.5063 | 480.1152 | 388.2249 | 375.2291 | 375.064 | 375.0871 | 349.5988 | 348.3939 | 399.2987
749.5077 | 657.5077 | 480.3069 | 388.4216 | 375.3205 | 375.17 | 375.1844 | 349.6933 | 348.4415 | 399.3466
750.5092 | 658.5092 | 480.4272 | 388.6288 | 375.4032 | 375.2757 | 375.2804 | 349.7903 | 348.5299 | 399.3934
751.5106 | 659.5106 | 480.471 | 388.8409 | 375.4983 | 375.3885 | 375.3873 | 349.8627 | 348.5982 | 399.4411
752.5121 | 660.5121 | 480.4811 | 389.0451 | 375.5875 | 375.4952 | 375.4837 | 349.94 | 348.6704 | 399.4834
753.5135 | 661.5135 | 480.4563 | 389.2522 | 375.6852 | 375.6102 | 375.5867 | 350.039 | 348.7406 | 399.52
754.5149 | 662.5149 | 480.4756 | 389.4495 | 375.7828 | 375.7191 | 375.6937 | 350.0968 | 348.8243 | 399.5534
755.5164 | 663.5164 | 480.5405 | 389.6523 | 375.8796 | 375.8218 | 375.7812 | 350.226 | 348.9113 | 399.6044
756.5078 | 664.5078 | 480.6512 | 389.8607 | 375.9628 | 375.94 | 375.8925 | 350.3368 | 349.0027 | 399.6552
757.5092 | 665.5092 | 480.627 | 390.0768 | 376.0472 | 376.055 | 376.0055 | 350.2989 | 349.1298 | 399.7045
758.5107 | 666.5107 | 480.7093 | 390.2776 | 376.1453 | 376.1753 | 376.1157 | 350.272 | 349.2227 | 399.7655
759.5121 | 667.5121 | 480.8966 | 390.4829 | 376.2388 | 376.2951 | 376.2299 | 350.2621 | 349.3057 | 399.8304
760.5136 | 668.5136 | 481.0053 | 390.6848 | 376.3479 | 376.4131 | 376.3412 | 350.3363 | 349.4095 | 399.888
761.515 | 669.515 | 481.0881 | 390.8869 | 376.4458 | 376.5309 | 376.4565 | 350.4001 | 349.49 | 399.9554
762.5064 | 670.5064 | 481.1752 | 391.0847 | 376.5431 | 376.6577 | 376.5733 | 350.4739 | 349.5649 | 400.0196
763.5079 | 671.5079 | 481.358 | 391.2774 | 376.642 | 376.7809 | 376.6876 | 350.5232 | 349.6591 | 400.0781
764.5093 | 672.5093 | 481.5253 | 391.4837 | 376.7544 | 376.91 | 376.8102 | 350.5416 | 349.7503 | 400.1401
765.5108 | 673.5108 | 481.5399 | 391.698 | 376.8567 | 377.031 | 376.9195 | 350.5496 | 349.7997 | 400.1918
766.5122 | 674.5122 | 481.7228 | 391.9059 | 376.9459 | 377.1666 | 377.0531 | 350.5164 | 349.8505 | 400.245
767.5136 | 675.5136 | 481.7798 | 392.1249 | 377.052 | 377.2961 | 377.1578 | 350.4901 | 349.9092 | 400.317
768.5051 | 676.5051 | 481.7409 | 392.3551 | 377.1674 | 377.4357 | 377.2779 | 350.5021 | 349.9883 | 400.3856
769.5065 | 677.5065 | 481.7693 | 392.5723 | 377.2742 | 377.5741 | 377.4142 | 350.5422 | 350.068 | 400.4549
770.5079 | 678.5079 | 481.9166 | 392.7972 | 377.3888 | 377.7009 | 377.5326 | 350.5896 | 350.1268 | 400.5137
771.5094 | 679.5094 | 481.9417 | 393.0191 | 377.4986 | 377.8352 | 377.6675 | 350.6178 | 350.1949 | 400.5645
772.5108 | 680.5108 | 481.9205 | 393.2387 | 377.6158 | 377.9608 | 377.7897 | 350.7061 | 350.2693 | 400.6253
773.5123 | 681.5123 | 481.948 | 393.4536 | 377.7329 | 378.0935 | 377.9077 | 350.8204 | 350.3301 | 400.6868
774.5137 | 682.5137 | 482.033 | 393.677 | 377.8523 | 378.232 | 378.0275 | 350.9424 | 350.3942 | 400.7323
775.5051 | 683.5051 | 482.1204 | 393.9009 | 377.9728 | 378.3638 | 378.1461 | 351.0398 | 350.4516 | 400.782
776.5066 | 684.5066 | 482.2403 | 394.1235 | 378.0927 | 378.4969 | 378.2873 | 351.0841 | 350.5139 | 400.8357
777.508 | 685.508 | 482.435 | 394.3529 | 378.2047 | 378.6302 | 378.4083 | 351.1437 | 350.5824 | 400.898
778.5094 | 686.5094 | 482.5349 | 394.5778 | 378.3279 | 378.7631 | 378.5533 | 351.2114 | 350.6421 | 400.951
779.5109 | 687.5109 | 482.368 | 394.8081 | 378.4452 | 378.9033 | 378.6948 | 351.2974 | 350.7216 | 401.0117
780.5123 | 688.5123 | 482.2653 | 395.0394 | 378.5706 | 379.0423 | 378.8376 | 351.3912 | 350.7564 | 401.0678
781.5138 | 689.5138 | 482.147 | 395.284 | 378.7023 | 379.1808 | 378.9779 | 351.4931 | 350.7869 | 401.1305
782.5052 | 690.5052 | 482.0095 | 395.5227 | 378.8208 | 379.3175 | 379.1177 | 351.5559 | 350.825 | 401.1792
783.5066 | 691.5066 | 481.7377 | 395.7684 | 378.9345 | 379.4584 | 379.2565 | 351.6078 | 350.8633 | 401.2367
784.5081 | 692.5081 | 481.4057 | 396.0129 | 379.0714 | 379.5953 | 379.4171 | 351.6556 | 350.9059 | 401.2883
785.5095 | 693.5095 | 481.1515 | 396.2512 | 379.2008 | 379.7428 | 379.5542 | 351.7304 | 350.9563 | 401.345
786.5109 | 694.5109 | 480.9555 | 396.4912 | 379.3182 | 379.8881 | 379.699 | 351.8036 | 350.9999 | 401.3923
787.5124 | 695.5124 | 480.7952 | 396.7249 | 379.4545 | 380.0241 | 379.8447 | 351.8347 | 351.0322 | 401.4558
788.5138 | 696.5138 | 480.7228 | 396.9653 | 379.5908 | 380.1719 | 379.9989 | 351.8589 | 351.0728 | 401.4899
789.5053 | 697.5053 | 480.6382 | 397.1977 | 379.7175 | 380.3077 | 380.1324 | 351.8758 | 351.1049 | 401.5247
790.5067 | 698.5067 | 480.5014 | 397.4215 | 379.8482 | 380.4565 | 380.2784 | 351.8945 | 351.1548 | 401.555
791.5081 | 699.5081 | 480.2162 | 397.6508 | 379.9891 | 380.5897 | 380.414 | 351.9235 | 351.1824 | 401.5831
792.5096 | 700.5096 | 479.9986 | 397.8767 | 380.1152 | 380.7251 | 380.5494 | 351.9809 | 351.211 | 401.6141
793.511 | 701.511 | 479.8119 | 398.0997 | 380.2573 | 380.8622 | 380.6914 | 351.9894 | 351.2216 | 401.6502
794.5125 | 702.5125 | 479.8468 | 398.335 | 380.381 | 381.0011 | 380.8342 | 352.0254 | 351.2528 | 401.6859
795.5139 | 703.5139 | 479.7214 | 398.5503 | 380.5064 | 381.1291 | 380.9749 | 352.0408 | 351.2893 | 401.7124
796.5153 | 704.5153 | 479.7343 | 398.7595 | 380.6394 | 381.2606 | 381.1253 | 352.089 | 351.3521 | 401.7418
797.5168 | 705.5168 | 479.813 | 398.9692 | 380.7838 | 381.3963 | 381.2706 | 352.1063 | 351.3889 | 401.7765
798.5082 | 706.5082 | 479.7088 | 399.1815 | 380.929 | 381.5329 | 381.4182 | 352.1519 | 351.446 | 401.8166
799.5096 | 707.5096 | 479.5519 | 399.3909 | 381.0542 | 381.6654 | 381.5765 | 352.1857 | 351.4973 | 401.837
800.5111 | 708.5111 | 479.4924 | 399.5847 | 381.2004 | 381.8091 | 381.7199 | 352.1793 | 351.515 | 401.8663
801.5125 | 709.5125 | 479.3884 | 399.7819 | 381.3537 | 381.9443 | 381.8616 | 352.2013 | 351.5807 | 401.8868
802.514 | 710.514 | 479.2 | 399.9892 | 381.4929 | 382.0784 | 382.0272 | 352.2647 | 351.6143 | 401.9122
803.5154 | 711.5154 | 479.1181 | 400.1919 | 381.6239 | 382.2044 | 382.1526 | 352.2893 | 351.6432 | 401.9371
804.5068 | 712.5068 | 479.0382 | 400.3992 | 381.7759 | 382.3507 | 382.3163 | 352.2828 | 351.6736 | 401.9643
805.5083 | 713.5083 | 478.8733 | 400.6077 | 381.912 | 382.4776 | 382.4653 | 352.2948 | 351.6922 | 402.0193
806.5097 | 714.5097 | 478.8238 | 400.8058 | 382.053 | 382.616 | 382.6134 | 352.3259 | 351.7361 | 402.0268
807.5111 | 715.5111 | 478.7702 | 401.0051 | 382.1952 | 382.7548 | 382.761 | 352.3852 | 351.7564 | 402.0573
808.5126 | 716.5126 | 478.7291 | 401.1997 | 382.3336 | 382.8927 | 382.927 | 352.4204 | 351.7809 | 402.0848
809.514 | 717.514 | 478.7225 | 401.3955 | 382.4675 | 383.0184 | 383.0697 | 352.4726 | 351.8152 | 402.1216
810.5054 | 718.5054 | 478.7187 | 401.5929 | 382.6118 | 383.1537 | 383.235 | 352.5011 | 351.8523 | 402.1211
811.5069 | 719.5069 | 478.923 | 401.7941 | 382.7481 | 383.285 | 383.3998 | 352.5598 | 351.9045 | 402.169
812.5083 | 720.5083 | 478.9935 | 402 | 382.889 | 383.4209 | 383.5461 | 352.6157 | 351.9374 | 402.1784
813.5098 | 721.5098 | 478.9397 | 402.2068 | 383.0169 | 383.5493 | 383.7063 | 352.7092 | 351.9776 | 402.2043
814.5112 | 722.5112 | 478.8652 | 402.4126 | 383.1513 | 383.6846 | 383.8722 | 352.7622 | 352.0245 | 402.2089
815.5126 | 723.5126 | 478.9054 | 402.6174 | 383.2982 | 383.8155 | 384.031 | 352.7897 | 352.0641 | 402.2427
816.5141 | 724.5141 | 478.8376 | 402.8112 | 383.438 | 383.9483 | 384.1785 | 352.8298 | 352.0946 | 402.256
817.5055 | 725.5055 | 478.741 | 403.0137 | 383.5727 | 384.0865 | 384.3401 | 352.9162 | 352.1257 | 402.2783
818.507 | 726.507 | 478.6611 | 403.2126 | 383.7173 | 384.2367 | 384.4941 | 352.9994 | 352.1375 | 402.305
819.5084 | 727.5084 | 478.6543 | 403.4144 | 383.8615 | 384.3764 | 384.6573 | 353.0865 | 352.179 | 402.3283
820.5098 | 728.5098 | 478.5806 | 403.6232 | 383.9888 | 384.5288 | 384.8337 | 353.1749 | 352.204 | 402.3508
821.5113 | 729.5113 | 478.5686 | 403.8376 | 384.1266 | 384.6811 | 384.9991 | 353.2555 | 352.2402 | 402.3798
822.5127 | 730.5127 | 478.6181 | 404.0496 | 384.2791 | 384.8422 | 385.1637 | 353.3572 | 352.2921 | 402.4166
823.5142 | 731.5142 | 478.6461 | 404.2522 | 384.4101 | 385.0054 | 385.3364 | 353.4353 | 352.3208 | 402.4483
824.5056 | 732.5056 | 478.6798 | 404.4463 | 384.5405 | 385.1763 | 385.5238 | 353.4502 | 352.3492 | 402.4746
825.507 | 733.507 | 478.7993 | 404.6485 | 384.6771 | 385.3446 | 385.7115 | 353.4441 | 352.399 | 402.5091
826.5085 | 734.5085 | 479.118 | 404.8423 | 384.8131 | 385.5268 | 385.8948 | 353.4243 | 352.4138 | 402.5338
827.5099 | 735.5099 | 479.446 | 405.0315 | 384.9545 | 385.7101 | 386.0814 | 353.4307 | 352.4612 | 402.5686
828.5113 | 736.5113 | 479.7209 | 405.2276 | 385.0917 | 385.8926 | 386.2702 | 353.47 | 352.5003 | 402.6204
829.5128 | 737.5128 | 479.6878 | 405.4322 | 385.2318 | 386.0659 | 386.4564 | 353.5431 | 352.5506 | 402.6444
830.5142 | 738.5142 | 479.8422 | 405.6423 | 385.3853 | 386.25 | 386.6606 | 353.579 | 352.5726 | 402.667
831.5056 | 739.5056 | 479.7734 | 405.8617 | 385.5326 | 386.4269 | 386.8404 | 353.6243 | 352.6245 | 402.6974
832.5271 | 740.5271 | 479.596 | 406.0746 | 385.7048 | 386.6072 | 387.041 | 353.6928 | 352.6628 | 402.7216
833.5085 | 741.5085 | 479.4239 | 406.2911 | 385.8615 | 386.7814 | 387.2325 | 353.7642 | 352.6923 | 402.7496
834.51 | 742.51 | 479.2381 | 406.5169 | 386.017 | 386.955 | 387.435 | 353.7424 | 352.7377 | 402.7671
835.5114 | 743.5114 | 479.0637 | 406.7318 | 386.176 | 387.1342 | 387.6422 | 353.7143 | 352.7855 | 402.8044
836.5128 | 744.5128 | 479.0005 | 406.9466 | 386.3411 | 387.3031 | 387.8498 | 353.6924 | 352.7852 | 402.8163
837.5143 | 745.5143 | 478.8882 | 407.161 | 386.5074 | 387.4786 | 388.0477 | 353.6897 | 352.8276 | 402.8288
838.5157 | 746.5157 | 478.7836 | 407.3826 | 386.6682 | 387.6586 | 388.2545 | 353.7324 | 352.8822 | 402.8371
839.5072 | 747.5072 | 478.7312 | 407.5874 | 386.8309 | 387.8315 | 388.4597 | 353.8201 | 352.9378 | 402.8699
840.5086 | 748.5086 | 478.7217 | 407.7972 | 387.0025 | 388.0153 | 388.6683 | 353.8421 | 352.9743 | 402.896
841.51 | 749.51 | 478.7096 | 407.9861 | 387.1717 | 388.1997 | 388.8583 | 353.8471 | 352.9951 | 402.9073
842.5115 | 750.5115 | 478.6167 | 408.1844 | 387.3467 | 388.3837 | 389.0592 | 353.8159 | 353.0394 | 402.9583
843.5129 | 751.5129 | 478.715 | 408.3908 | 387.4948 | 388.5624 | 389.2654 | 353.8737 | 353.0992 | 402.9784
844.5144 | 752.5144 | 478.811 | 408.5983 | 387.6709 | 388.7454 | 389.4658 | 353.9354 | 353.1532 | 403.0056
845.5158 | 753.5158 | 478.8023 | 408.8034 | 387.834 | 388.9288 | 389.6637 | 353.9903 | 353.1879 | 403.0327
846.5072 | 754.5072 | 478.7995 | 409.003 | 388.0087 | 389.1096 | 389.8621 | 354.0418 | 353.2372 | 403.0611
847.5087 | 755.5087 | 478.934 | 409.2171 | 388.1808 | 389.2991 | 390.0594 | 354.0916 | 353.2747 | 403.092
848.5101 | 756.5101 | 478.9629 | 409.4284 | 388.3499 | 389.4766 | 390.2409 | 354.1451 | 353.3297 | 403.0854
849.5115 | 757.5115 | 478.9693 | 409.641 | 388.5295 | 389.6539 | 390.4521 | 354.2045 | 353.3787 | 403.1078
850.513 | 758.513 | 479.2387 | 409.8466 | 388.7055 | 389.8416 | 390.6271 | 354.2799 | 353.3983 | 403.1383
851.5144 | 759.5144 | 479.5652 | 410.0471 | 388.8671 | 390.022 | 390.8189 | 354.301 | 353.4372 | 403.1771
852.5058 | 760.5058 | 479.9275 | 410.2565 | 389.052 | 390.2128 | 391.0177 | 354.3459 | 353.4821 | 403.2087
853.5073 | 761.5073 | 480.099 | 410.4657 | 389.2289 | 390.3931 | 391.2106 | 354.3706 | 353.5273 | 403.2365
854.5087 | 762.5087 | 480.0864 | 410.6702 | 389.4067 | 390.5744 | 391.4087 | 354.4002 | 353.5428 | 403.291
855.5102 | 763.5102 | 480.0765 | 410.8869 | 389.5915 | 390.7603 | 391.5956 | 354.4473 | 353.5906 | 403.3095
856.5116 | 764.5116 | 480.0751 | 411.1104 | 389.7775 | 390.9465 | 391.7962 | 354.4891 | 353.6342 | 403.3474
857.513 | 765.513 | 480.0392 | 411.3329 | 389.939 | 391.1293 | 391.9974 | 354.5204 | 353.6657 | 403.3495
858.5145 | 766.5145 | 479.9285 | 411.5412 | 390.1354 | 391.3075 | 392.1887 | 354.5822 | 353.6898 | 403.3856
859.5059 | 767.5059 | 479.7862 | 411.7535 | 390.3117 | 391.4901 | 392.3911 | 354.6201 | 353.7211 | 403.4042
860.5073 | 768.5073 | 479.6412 | 411.9555 | 390.4909 | 391.6602 | 392.57 | 354.6314 | 353.7494 | 403.4168
861.5088 | 769.5088 | 479.4971 | 412.1595 | 390.7027 | 391.8387 | 392.7588 | 354.6532 | 353.7933 | 403.4384
862.5102 | 770.5102 | 479.3913 | 412.3596 | 390.8775 | 392.0058 | 392.9362 | 354.7217 | 353.8298 | 403.452
863.5117 | 771.5117 | 479.2898 | 412.5616 | 391.0728 | 392.183 | 393.1194 | 354.8045 | 353.8614 | 403.4637
864.5131 | 772.5131 | 479.2041 | 412.7717 | 391.266 | 392.3603 | 393.2928 | 354.8986 | 353.8642 | 403.5013
865.5145 | 773.5145 | 479.2127 | 412.9749 | 391.4494 | 392.5355 | 393.4804 | 354.9459 | 353.8827 | 403.5495
866.516 | 774.516 | 479.1506 | 413.177 | 391.6425 | 392.7145 | 393.665 | 354.9817 | 353.9369 | 403.5595
867.5074 | 775.5074 | 479.0288 | 413.3797 | 391.8449 | 392.8933 | 393.8377 | 355.0354 | 353.9693 | 403.5949
868.5089 | 776.5089 | 479.0296 | 413.588 | 392.0412 | 393.0741 | 394.0265 | 355.0756 | 353.9974 | 403.6075
869.5103 | 777.5103 | 479.1256 | 413.7974 | 392.2329 | 393.2501 | 394.2131 | 355.1118 | 353.9901 | 403.6188
870.5117 | 778.5117 | 479.1799 | 413.9883 | 392.4164 | 393.4338 | 394.4109 | 355.1771 | 354.0231 | 403.6543
871.5132 | 779.5132 | 479.1404 | 414.1811 | 392.6165 | 393.6178 | 394.6082 | 355.2477 | 354.0498 | 403.6658
872.5146 | 780.5146 | 479.0062 | 414.3638 | 392.8196 | 393.7957 | 394.7921 | 355.2625 | 354.106 | 403.6742
873.506 | 781.506 | 478.9765 | 414.5377 | 393.0145 | 393.9788 | 394.9799 | 355.2467 | 354.1136 | 403.6913
874.5075 | 782.5075 | 478.8556 | 414.7045 | 393.2114 | 394.1581 | 395.1681 | 355.2822 | 354.1319 | 403.7259
875.5089 | 783.5089 | 478.8212 | 414.866 | 393.4193 | 394.3456 | 395.3716 | 355.302 | 354.1285 | 403.7636
876.5104 | 784.5104 | 478.7143 | 415.0263 | 393.6221 | 394.5285 | 395.5524 | 355.3025 | 354.1513 | 403.8011
877.5118 | 785.5118 | 478.6428 | 415.1882 | 393.8267 | 394.7213 | 395.7433 | 355.3518 | 354.1628 | 403.8299
878.5132 | 786.5132 | 478.8431 | 415.3435 | 394.0351 | 394.9102 | 395.9303 | 355.4114 | 354.2015 | 403.8898
879.5147 | 787.5147 | 479.085 | 415.5072 | 394.2428 | 395.098 | 396.1255 | 355.4687 | 354.2188 | 403.9074
880.5061 | 788.5061 | 479.1518 | 415.6588 | 394.4369 | 395.2943 | 396.3085 | 355.475 | 354.2595 | 403.9635
881.5075 | 789.5075 | 479.2049 | 415.8168 | 394.6554 | 395.4813 | 396.4984 | 355.4919 | 354.2672 | 404.0039
882.509 | 790.509 | 479.1003 | 415.9844 | 394.8589 | 395.6748 | 396.6745 | 355.5325 | 354.3099 | 404.0219
883.5104 | 791.5104 | 478.9724 | 416.1634 | 395.0692 | 395.8568 | 396.8496 | 355.5795 | 354.3425 | 404.0478
884.5119 | 792.5119 | 478.6911 | 416.3357 | 395.2692 | 396.0446 | 397.0409 | 355.618 | 354.3783 | 404.0718
885.5133 | 793.5133 | 478.5413 | 416.5103 | 395.4829 | 396.2275 | 397.2102 | 355.7285 | 354.412 | 404.109
886.5147 | 794.5147 | 478.5352 | 416.6926 | 395.691 | 396.3978 | 397.3816 | 355.8279 | 354.4511 | 404.14
887.5162 | 795.5162 | 478.5509 | 416.8791 | 395.8934 | 396.5703 | 397.5623 | 355.884 | 354.5086 | 404.176
888.5076 | 796.5076 | 478.4618 | 417.0517 | 396.0892 | 396.738 | 397.7347 | 355.9554 | 354.5561 | 404.1831
889.5091 | 797.5091 | 478.4707 | 417.2224 | 396.3035 | 396.906 | 397.9071 | 356.0119 | 354.5922 | 404.2108
890.5105 | 798.5105 | 478.4719 | 417.3848 | 396.5118 | 397.078 | 398.0739 | 356.0426 | 354.6349 | 404.219
891.5119 | 799.5119 | 478.3685 | 417.5627 | 396.7205 | 397.2502 | 398.2399 | 356.0693 | 354.6625 | 404.2782
892.5134 | 800.5134 | 478.2635 | 417.7308 | 396.9279 | 397.422 | 398.4216 | 356.105 | 354.6857 | 404.3179
893.5148 | 801.5148 | 478.3903 | 417.8996 | 397.1437 | 397.5922 | 398.6022 | 356.1231 | 354.6979 | 404.3168
894.5062 | 802.5062 | 478.345 | 418.0559 | 397.3499 | 397.7657 | 398.7742 | 356.1603 | 354.7112 | 404.3509
895.5077 | 803.5077 | 478.2794 | 418.2245 | 397.5612 | 397.935 | 398.9399 | 356.2113 | 354.7361 | 404.3541
896.5091 | 804.5091 | 478.2488 | 418.3765 | 397.7562 | 398.1106 | 399.1046 | 356.2611 | 354.7961 | 404.383
897.5106 | 805.5106 | 478.3328 | 418.5324 | 397.9611 | 398.2865 | 399.2809 | 356.2604 | 354.8146 | 404.409
898.512 | 806.512 | 478.3767 | 418.6975 | 398.1765 | 398.4519 | 399.446 | 356.2438 | 354.8527 | 404.4281
899.5134 | 807.5134 | 478.4181 | 418.8572 | 398.389 | 398.6189 | 399.6146 | 356.2321 | 354.8918 | 404.4511
900.5049 | 808.5049 | 478.2164 | 419.0112 | 398.5939 | 398.7864 | 399.7849 | 356.2186 | 354.9297 | 404.458
901.5063 | 809.5063 | 478.2203 | 419.1565 | 398.8146 | 398.9458 | 399.9365 | 356.2025 | 354.9668 | 404.4817
902.5077 | 810.5077 | 478.075 | 419.3147 | 399.0102 | 399.1151 | 400.1153 | 356.2025 | 355.019 | 404.4869
903.5092 | 811.5092 | 477.9544 | 419.4609 | 399.2187 | 399.2834 | 400.2798 | 356.2274 | 355.0602 | 404.5177
904.5106 | 812.5106 | 477.8468 | 419.6182 | 399.4175 | 399.451 | 400.4333 | 356.2605 | 355.0983 | 404.5271
905.5121 | 813.5121 | 477.7226 | 419.7576 | 399.6355 | 399.6098 | 400.5862 | 356.3023 | 355.1221 | 404.5354
906.5135 | 814.5135 | 477.641 | 419.8905 | 399.85 | 399.787 | 400.7367 | 356.3154 | 355.1619 | 404.562
907.5049 | 815.5049 | 477.6151 | 420.0152 | 400.0652 | 399.9447 | 400.888 | 356.3541 | 355.2042 | 404.5714
908.5064 | 816.5064 | 477.5666 | 420.151 | 400.2603 | 400.1135 | 401.0429 | 356.4156 | 355.2446 | 404.5869
909.5078 | 817.5078 | 477.5367 | 420.2858 | 400.4621 | 400.2741 | 401.1985 | 356.5031 | 355.3018 | 404.632
910.5092 | 818.5092 | 477.6772 | 420.4173 | 400.6761 | 400.4391 | 401.3578 | 356.5813 | 355.33 | 404.6514
911.5107 | 819.5107 | 477.8265 | 420.5528 | 400.8746 | 400.6069 | 401.5117 | 356.6388 | 355.3754 | 404.703
912.5121 | 820.5121 | 478.0436 | 420.6829 | 401.0827 | 400.7698 | 401.6644 | 356.7399 | 355.4518 | 404.7332
913.5136 | 821.5136 | 478.3092 | 420.8174 | 401.2873 | 400.9359 | 401.8194 | 356.798 | 355.478 | 404.7508
914.515 | 822.515 | 478.515 | 420.9462 | 401.4866 | 401.1056 | 401.9649 | 356.7932 | 355.5358 | 404.7836
915.5064 | 823.5064 | 478.7038 | 421.086 | 401.6987 | 401.2753 | 402.1112 | 356.8245 | 355.619 | 404.8298
916.5079 | 824.5079 | 478.9099 | 421.2421 | 401.896 | 401.4405 | 402.2648 | 356.885 | 355.6822 | 404.8605
917.5093 | 825.5093 | 479.0137 | 421.3891 | 402.0977 | 401.6006 | 402.402 | 356.9989 | 355.7552 | 404.8968
918.5108 | 826.5108 | 479.333 | 421.541 | 402.2982 | 401.7798 | 402.5475 | 357.0702 | 355.8147 | 404.9516
919.5122 | 827.5122 | 479.5084 | 421.7077 | 402.4926 | 401.9477 | 402.6807 | 357.1396 | 355.8685 | 405.0044
920.5136 | 828.5136 | 479.7726 | 421.8808 | 402.683 | 402.1076 | 402.8261 | 357.1976 | 355.9398 | 405.0509
921.5151 | 829.5151 | 479.8066 | 422.0424 | 402.8863 | 402.289 | 402.946 | 357.2107 | 356.0037 | 405.1032
922.5165 | 830.5165 | 479.8539 | 422.2116 | 403.0915 | 402.4581 | 403.0658 | 357.2607 | 356.0618 | 405.116
923.5079 | 831.5079 | 479.927 | 422.3791 | 403.2981 | 402.6259 | 403.1952 | 357.3449 | 356.1045 | 405.1734
924.5094 | 832.5094 | 479.8421 | 422.5552 | 403.4961 | 402.7997 | 403.3174 | 357.3732 | 356.1621 | 405.2026
925.5108 | 833.5108 | 479.6422 | 422.7362 | 403.6881 | 402.9775 | 403.4561 | 357.3957 | 356.2113 | 405.2412
926.5123 | 834.5123 | 479.5078 | 422.9045 | 403.8861 | 403.1448 | 403.5935 | 357.4486 | 356.2657 | 405.289
927.5137 | 835.5137 | 479.3857 | 423.0734 | 404.0767 | 403.3226 | 403.7299 | 357.5182 | 356.3174 | 405.3262
928.5151 | 836.5151 | 479.334 | 423.2334 | 404.2847 | 403.5035 | 403.86 | 357.6401 | 356.3601 | 405.3519
929.5166 | 837.5166 | 479.378 | 423.3973 | 404.4853 | 403.6957 | 404.0094 | 357.7033 | 356.412 | 405.4158
930.508 | 838.508 | 479.3153 | 423.5683 | 404.6857 | 403.8744 | 404.157 | 357.7716 | 356.4571 | 405.4353
931.5094 | 839.5094 | 479.2394 | 423.7278 | 404.8918 | 404.0783 | 404.3007 | 357.8199 | 356.4975 | 405.4934
932.5109 | 840.5109 | 479.2577 | 423.8948 | 405.083 | 404.2685 | 404.4596 | 357.8753 | 356.5425 | 405.534
933.5123 | 841.5123 | 479.2602 | 424.0572 | 405.2731 | 404.4561 | 404.6065 | 357.9385 | 356.5885 | 405.5734
934.5138 | 842.5138 | 479.1991 | 424.2112 | 405.4857 | 404.6474 | 404.7768 | 358.0168 | 356.6493 | 405.6078
935.5152 | 843.5152 | 479.2334 | 424.3731 | 405.688 | 404.8439 | 404.9448 | 358.1259 | 356.675 | 405.6712
936.5066 | 844.5066 | 479.4073 | 424.5322 | 405.8788 | 405.0282 | 405.1042 | 358.2069 | 356.7455 | 405.7103
937.5081 | 845.5081 | 479.5887 | 424.7002 | 406.0807 | 405.2256 | 405.2815 | 358.2665 | 356.7831 | 405.7406
938.5095 | 846.5095 | 479.6932 | 424.8635 | 406.2908 | 405.4071 | 405.453 | 358.3089 | 356.8267 | 405.7956
939.511 | 847.511 | 479.8268 | 425.0208 | 406.4818 | 405.5983 | 405.6207 | 358.3501 | 356.8685 | 405.8486
940.5124 | 848.5124 | 479.9433 | 425.1832 | 406.6659 | 405.7721 | 405.7905 | 358.3899 | 356.9211 | 405.878
941.5138 | 849.5138 | 479.7677 | 425.3264 | 406.8828 | 405.953 | 405.952 | 358.4214 | 356.9715 | 405.9135
942.5053 | 850.5053 | 479.5809 | 425.4818 | 407.0704 | 406.1299 | 406.1108 | 358.4622 | 357.0146 | 405.9495
943.5067 | 851.5067 | 479.5898 | 425.6256 | 407.2727 | 406.3058 | 406.2781 | 358.4826 | 357.048 | 405.9795
944.5081 | 852.5081 | 479.5925 | 425.7692 | 407.4644 | 406.4826 | 406.4447 | 358.5231 | 357.084 | 406.022
945.5096 | 853.5096 | 479.5066 | 425.9019 | 407.6547 | 406.6612 | 406.6191 | 358.5615 | 357.1317 | 406.0589
946.511 | 854.511 | 479.4272 | 426.0336 | 407.8526 | 406.8314 | 406.7954 | 358.6409 | 357.169 | 406.1005
947.5125 | 855.5125 | 479.3594 | 426.1844 | 408.0583 | 407.0209 | 406.9622 | 358.7453 | 357.2377 | 406.1565
948.5139 | 856.5139 | 479.3713 | 426.3233 | 408.2493 | 407.1979 | 407.142 | 358.7835 | 357.2598 | 406.1978
949.5053 | 857.5053 | 479.4433 | 426.4644 | 408.4281 | 407.378 | 407.3175 | 358.7824 | 357.3069 | 406.1985
950.5068 | 858.5068 | 479.5128 | 426.6143 | 408.6114 | 407.5585 | 407.4927 | 358.8329 | 357.3569 | 406.2337
951.5082 | 859.5082 | 479.4294 | 426.7695 | 408.805 | 407.7366 | 407.6586 | 358.8486 | 357.3926 | 406.2938
952.5096 | 860.5096 | 479.4017 | 426.9277 | 408.9975 | 407.9229 | 407.821 | 358.8842 | 357.4401 | 406.3309
953.5111 | 861.5111 | 479.5428 | 427.0919 | 409.2105 | 408.117 | 407.9843 | 358.8944 | 357.5071 | 406.3821
954.5125 | 862.5125 | 479.6519 | 427.2513 | 409.4029 | 408.2963 | 408.1485 | 358.932 | 357.5495 | 406.4134
955.514 | 863.514 | 479.8329 | 427.4159 | 409.5829 | 408.4789 | 408.2895 | 358.9418 | 357.5959 | 406.4355
956.5154 | 864.5154 | 480.1228 | 427.5836 | 409.788 | 408.6809 | 408.44 | 358.9097 | 357.6498 | 406.4641
957.5068 | 865.5068 | 480.1436 | 427.7586 | 409.9573 | 408.8653 | 408.5858 | 358.9268 | 357.6921 | 406.4659
958.5083 | 866.5083 | 479.9811 | 427.9253 | 410.1498 | 409.0599 | 408.7329 | 358.9768 | 357.7214 | 406.4709
959.5097 | 867.5097 | 479.9681 | 428.0985 | 410.3548 | 409.2521 | 408.8799 | 359.0099 | 357.7628 | 406.5015
960.5111 | 868.5111 | 479.954 | 428.2669 | 410.5431 | 409.4361 | 409.0341 | 359.0241 | 357.8256 | 406.5433
961.5126 | 869.5126 | 479.9196 | 428.4279 | 410.7217 | 409.6213 | 409.1807 | 359.0468 | 357.8724 | 406.5586
962.514 | 870.514 | 479.8062 | 428.5909 | 410.9087 | 409.8178 | 409.3372 | 359.1049 | 357.9023 | 406.5705
963.5155 | 871.5155 | 479.8111 | 428.7598 | 411.0952 | 410.0084 | 409.4865 | 359.1846 | 357.9341 | 406.5729
964.5069 | 872.5069 | 479.7503 | 428.925 | 411.2798 | 410.1921 | 409.6366 | 359.2747 | 357.9739 | 406.5863
965.5083 | 873.5083 | 479.7852 | 429.0903 | 411.4738 | 410.3757 | 409.808 | 359.3433 | 358.0153 | 406.6052
966.5098 | 874.5098 | 479.7672 | 429.256 | 411.6551 | 410.555 | 409.9667 | 359.4271 | 358.0495 | 406.6536
967.5112 | 875.5112 | 479.7014 | 429.407 | 411.8304 | 410.7316 | 410.1396 | 359.4908 | 358.1099 | 406.6779
968.5127 | 876.5127 | 479.6027 | 429.5617 | 412.0211 | 410.9051 | 410.2988 | 359.5429 | 358.1267 | 406.6894
969.5141 | 877.5141 | 479.422 | 429.7163 | 412.2104 | 411.0696 | 410.4701 | 359.5752 | 358.1888 | 406.6815
970.5155 | 878.5155 | 479.0857 | 429.8713 | 412.3899 | 411.2437 | 410.6377 | 359.6232 | 358.2306 | 406.7205
971.517 | 879.517 | 479.034 | 430.0338 | 412.5739 | 411.4149 | 410.8102 | 359.6772 | 358.2729 | 406.723
972.5084 | 880.5084 | 479.0562 | 430.1872 | 412.7493 | 411.5906 | 410.9772 | 359.7072 | 358.3497 | 406.7371
973.5098 | 881.5098 | 478.9836 | 430.3464 | 412.9261 | 411.7659 | 411.1507 | 359.7649 | 358.3901 | 406.7694
974.5113 | 882.5113 | 478.8707 | 430.5014 | 413.1107 | 411.946 | 411.3152 | 359.8189 | 358.4534 | 406.7875
975.5127 | 883.5127 | 478.7019 | 430.6574 | 413.2958 | 412.1342 | 411.5021 | 359.8497 | 358.4956 | 406.7886
976.5142 | 884.5142 | 478.5839 | 430.8049 | 413.472 | 412.3125 | 411.6594 | 359.8728 | 358.5471 | 406.8286
977.5156 | 885.5156 | 478.5643 | 430.956 | 413.6479 | 412.4898 | 411.8244 | 359.9066 | 358.6251 | 406.8704
978.507 | 886.507 | 478.3541 | 431.1101 | 413.8321 | 412.6699 | 411.9894 | 359.9244 | 358.6438 | 406.9002
979.5085 | 887.5085 | 478.3832 | 431.2481 | 414.0008 | 412.8487 | 412.1573 | 359.963 | 358.7178 | 406.9159
980.5099 | 888.5099 | 478.3879 | 431.3809 | 414.1768 | 413.0229 | 412.324 | 360.0263 | 358.7639 | 406.9675
981.5113 | 889.5113 | 478.5971 | 431.5365 | 414.3534 | 413.1946 | 412.4835 | 360.0999 | 358.8066 | 406.9876
982.5128 | 890.5128 | 478.697 | 431.7079 | 414.5338 | 413.3863 | 412.6316 | 360.1584 | 358.8521 | 407.0381
983.5142 | 891.5142 | 478.6586 | 431.8676 | 414.7159 | 413.5598 | 412.781 | 360.218 | 358.9268 | 407.0601
984.5056 | 892.5056 | 478.6608 | 432.0072 | 414.8811 | 413.7471 | 412.9476 | 360.2546 | 358.9845 | 407.0729
985.5071 | 893.5071 | 478.5371 | 432.1437 | 415.0599 | 413.9275 | 413.0957 | 360.2791 | 359.0488 | 407.097
986.5085 | 894.5085 | 478.4411 | 432.2749 | 415.2417 | 414.1101 | 413.2537 | 360.2758 | 359.1044 | 407.1224
987.51 | 895.51 | 478.5197 | 432.3955 | 415.4072 | 414.2837 | 413.4108 | 360.3367 | 359.1613 | 407.1349
988.5114 | 896.5114 | 478.5766 | 432.5092 | 415.574 | 414.4749 | 413.5578 | 360.3947 | 359.1994 | 407.1626
989.5128 | 897.5128 | 478.6174 | 432.6341 | 415.7434 | 414.6536 | 413.7146 | 360.4784 | 359.2352 | 407.1893
990.5143 | 898.5143 | 478.7346 | 432.768 | 415.9216 | 414.8395 | 413.8524 | 360.5555 | 359.2789 | 407.2158
991.5157 | 899.5157 | 478.8773 | 432.8711 | 416.0782 | 415.0292 | 414.0058 | 360.6268 | 359.315 | 407.2427
992.5072 | 900.5072 | 478.9014 | 432.999 | 416.2475 | 415.2163 | 414.1424 | 360.6836 | 359.3513 | 407.282
993.5086 | 901.5086 | 478.9923 | 433.1823 | 416.4236 | 415.4112 | 414.2764 | 360.7196 | 359.408 | 407.3272
994.51 | 902.51 | 479.0868 | 433.288 | 416.5891 | 415.592 | 414.4164 | 360.7378 | 359.4535 | 407.3631
995.5115 | 903.5115 | 479.248 | 433.4727 | 416.7587 | 415.77 | 414.5586 | 360.7931 | 359.5307 | 407.3873
996.5129 | 904.5129 | 479.4079 | 433.5792 | 416.9168 | 415.9494 | 414.6998 | 360.8696 | 359.6022 | 407.4165
997.5144 | 905.5144 | 479.4584 | 433.6931 | 417.0827 | 416.1157 | 414.8555 | 360.9796 | 359.6531 | 407.4467
998.5158 | 906.5158 | 479.4121 | 433.7987 | 417.2417 | 416.2707 | 414.9834 | 361.0788 | 359.7205 | 407.4599
999.5072 | 907.5072 | 479.4372 | 433.9077 | 417.4107 | 416.4242 | 415.136 | 361.104 | 359.7645 | 407.475
1000.5087 | 908.5087 | 479.3231 | 434.0393 | 417.5693 | 416.5636 | 415.2865 | 361.1166 | 359.8074 | 407.5151
1001.5101 | 909.5101 | 479.515 | 434.1706 | 417.7358 | 416.7117 | 415.4192 | 361.1578 | 359.8276 | 407.5686
1002.5115 | 910.5115 | 479.6186 | 434.3293 | 417.8935 | 416.8613 | 415.5857 | 361.2095 | 359.8785 | 407.5814
1003.513 | 911.513 | 479.6208 | 434.5508 | 418.0571 | 417.024 | 415.7207 | 361.2556 | 359.9298 | 407.6314
1004.5144 | 912.5144 | 479.6139 | 434.6246 | 418.2097 | 417.1775 | 415.8724 | 361.3188 | 359.9817 | 407.6576
1005.5058 | 913.5058 | 479.556 | 434.6978 | 418.3642 | 417.3578 | 416.0229 | 361.3928 | 360.0509 | 407.6918
1006.5073 | 914.5073 | 479.4709 | 434.7987 | 418.5345 | 417.529 | 416.1549 | 361.4893 | 360.1206 | 407.745
1007.5087 | 915.5087 | 479.3182 | 434.8829 | 418.6937 | 417.7069 | 416.2872 | 361.5901 | 360.1642 | 407.7613
1008.5102 | 916.5102 | 479.2294 | 434.926 | 418.8447 | 417.8915 | 416.427 | 361.7044 | 360.211 | 407.7904
1009.5116 | 917.5116 | 479.2295 | 435.0408 | 419.0111 | 418.0755 | 416.563 | 361.8057 | 360.2461 | 407.823
1010.513 | 918.513 | 479.1963 | 435.1524 | 419.1653 | 418.2655 | 416.6985 | 361.8698 | 360.3084 | 407.8405
1011.5145 | 919.5145 | 479.182 | 435.1728 | 419.3099 | 418.4427 | 416.8307 | 361.9339 | 360.35 | 407.8641
1012.5159 | 920.5159 | 479.0293 | 435.2349 | 419.4704 | 418.6214 | 416.9703 | 362.0071 | 360.3885 | 407.9235
1013.5775 | 921.5775 | 478.9139 | 435.3044 | 419.6462 | 418.7952 | 417.1008 | 362.0911 | 360.4427 | 407.9498
1014.5088 | 922.5088 | 478.7621 | 435.3755 | 419.8004 | 418.9483 | 417.216 | 362.15 | 360.4746 | 407.9749
1015.5102 | 923.5102 | 478.7518 | 435.4745 | 419.949 | 419.1113 | 417.3597 | 362.193 | 360.5501 | 407.9987
1016.5117 | 924.5117 | 478.6889 | 435.5486 | 420.1088 | 419.2736 | 417.4751 | 362.2247 | 360.6055 | 408.0234
1017.5231 | 925.5231 | 478.6083 | 435.5591 | 420.264 | 419.4426 | 417.6175 | 362.2542 | 360.6379 | 408.0283
1018.5146 | 926.5146 | 478.5893 | 435.5979 | 420.4236 | 419.6043 | 417.7523 | 362.3341 | 360.6606 | 408.0647
1019.516 | 927.516 | 478.7016 | 435.6093 | 420.6018 | 419.7615 | 417.8932 | 362.4182 | 360.7149 | 408.0936
1020.5074 | 928.5074 | 478.6729 | 435.7156 | 420.7566 | 419.9267 | 418.0198 | 362.5229 | 360.7808 | 408.1231
1021.5089 | 929.5089 | 478.5394 | 435.7622 | 420.9102 | 420.0941 | 418.1477 | 362.6002 | 360.8355 | 408.1387
1022.5103 | 930.5103 | 478.5847 | 435.7827 | 421.061 | 420.2695 | 418.279 | 362.6737 | 360.8864 | 408.1384
1023.5117 | 931.5117 | 478.6841 | 435.7538 | 421.2282 | 420.4472 | 418.3997 | 362.7207 | 360.95 | 408.188
1024.5132 | 932.5132 | 478.6113 | 435.7743 | 421.3873 | 420.6104 | 418.5229 | 362.7902 | 361.0188 | 408.2154
1025.5046 | 933.5046 | 478.5211 | 435.7202 | 421.5356 | 420.7884 | 418.6276 | 362.8188 | 361.0517 | 408.2292
1026.506 | 934.506 | 478.5027 | 435.6698 | 421.6957 | 420.9634 | 418.7454 | 362.8122 | 361.0872 | 408.2477 | Time of first failure
1027.5075 | 935.5075 | 478.6322 | 435.6209 | 421.8452 | 421.131 | 418.8758 | 362.8587 | 361.1428 | 408.274 | 935 | 0
1028.5089 | 936.5089 | 478.869 | 435.606 | 421.996 | 421.2953 | 418.9818 | 362.927 | 361.1856 | 408.2858 | 935 | 900
1029.5104 | 937.5104 | 478.891 | 435.5867 | 422.1661 | 421.4636 | 419.1012 | 362.99 | 361.2175 | 408.3166
1030.5118 | 938.5118 | 478.9161 | 435.5351 | 422.3124 | 421.6192 | 419.2167 | 363.0292 | 361.2615 | 408.3645
1031.5132 | 939.5132 | 478.9858 | 435.4961 | 422.4757 | 421.7809 | 419.3305 | 363.0695 | 361.3034 | 408.3953
1032.5047 | 940.5047 | 479.042 | 435.4619 | 422.6313 | 421.9365 | 419.4476 | 363.144 | 361.3602 | 408.4291
1033.5061 | 941.5061 | 479.0118 | 435.4591 | 422.778 | 422.0984 | 419.561 | 363.1845 | 361.4291 | 408.4565
1034.5075 | 942.5075 | 479.1736 | 435.4469 | 422.9283 | 422.2468 | 419.6748 | 363.155 | 361.4712 | 408.5032
1035.509 | 943.509 | 479.269 | 435.4317 | 423.0864 | 422.4018 | 419.7874 | 363.1189 | 361.5203 | 408.5129
1036.5104 | 944.5104 | 479.3764 | 435.3756 | 423.2461 | 422.5525 | 419.9107 | 363.1801 | 361.5809 | 408.545
1037.5119 | 945.5119 | 479.5395 | 435.2904 | 423.3946 | 422.7057 | 420.0247 | 363.3256 | 361.6173 | 408.5954
1038.5133 | 946.5133 | 479.6163 | 435.2372 | 423.5428 | 422.8571 | 420.1257 | 363.4151 | 361.6569 | 408.6169
1039.5147 | 947.5147 | 479.7337 | 435.2106 | 423.6774 | 423.0016 | 420.2373 | 363.418 | 361.734 | 408.6635
1040.5162 | 948.5162 | 479.7428 | 435.1783 | 423.834 | 423.1488 | 420.3493 | 363.4124 | 361.7819 | 408.6994
1041.5076 | 949.5076 | 479.6699 | 435.1324 | 423.9836 | 423.2969 | 420.4657 | 363.4435 | 361.8097 | 408.7176
1042.5091 | 950.5091 | 479.7318 | 435.0827 | 424.1162 | 423.4405 | 420.5819 | 363.4977 | 361.8531 | 408.7404
1043.5105 | 951.5105 | 479.7039 | 435.0188 | 424.2693 | 423.5846 | 420.6967 | 363.576 | 361.9058 | 408.7514
1044.5119 | 952.5119 | 479.6888 | 434.9819 | 424.3956 | 423.7197 | 420.8224 | 363.5858 | 361.9599 | 408.7584
1045.5134 | 953.5134 | 479.7014 | 434.9721 | 424.5391 | 423.8542 | 420.9344 | 363.6273 | 362.0029 | 408.7806
1046.5148 | 954.5148 | 479.5542 | 434.9543 | 424.6764 | 423.9794 | 421.054 | 363.6629 | 362.0529 | 408.8122
1047.5062 | 955.5062 | 479.344 | 434.9285 | 424.8195 | 424.1024 | 421.1551 | 363.6868 | 362.082 | 408.8472
1048.5077 | 956.5077 | 479.4233 | 434.8804 | 424.9604 | 424.2228 | 421.2538 | 363.7193 | 362.1164 | 408.862
1049.5091 | 957.5091 | 479.469 | 434.8407 | 425.0953 | 424.3319 | 421.3531 | 363.7734 | 362.1673 | 408.8916
1050.5106 | 958.5106 | 479.4215 | 434.7928 | 425.2232 | 424.4424 | 421.441 | 363.7989 | 362.1903 | 408.9131
1051.512 | 959.512 | 479.3208 | 434.7821 | 425.3538 | 424.549 | 421.5455 | 363.8444 | 362.2303 | 408.9517
1052.5134 | 960.5134 | 479.3214 | 434.7945 | 425.4912 | 424.6533 | 421.6419 | 363.9385 | 362.2733 | 408.9791
1053.5149 | 961.5149 | 479.2524 | 434.7988 | 425.6155 | 424.7499 | 421.7332 | 364.0242 | 362.3334 | 409.0055
1054.5163 | 962.5163 | 479.205 | 434.7742 | 425.7419 | 424.8516 | 421.8261 | 364.1125 | 362.3751 | 409.0297
1055.5077 | 963.5077 | 479.2827 | 434.7643 | 425.866 | 424.9516 | 421.9308 | 364.1977 | 362.4126 | 409.0625
1056.5092 | 964.5092 | 479.4146 | 434.7069 | 425.9915 | 425.0552 | 422.0192 | 364.2491 | 362.4322 | 409.1167
1057.5106 | 965.5106 | 479.5165 | 434.7321 | 426.1146 | 425.1615 | 422.1097 | 364.3071 | 362.4602 | 409.1416
1058.5121 | 966.5121 | 479.4465 | 434.7396 | 426.243 | 425.2611 | 422.2037 | 364.3201 | 362.5055 | 409.1525
1059.5135 | 967.5135 | 479.294 | 434.7623 | 426.3679 | 425.3658 | 422.2998 | 364.3133 | 362.5696 | 409.1655
1060.5149 | 968.5149 | 479.0978 | 434.7671 | 426.4872 | 425.4648 | 422.3939 | 364.3718 | 362.6152 | 409.195
1061.5064 | 969.5064 | 479.0471 | 434.7694 | 426.6067 | 425.5576 | 422.4831 | 364.4309 | 362.6475 | 409.2016
1062.5078 | 970.5078 | 479.1217 | 434.8072 | 426.7391 | 425.6461 | 422.5747 | 364.4907 | 362.6998 | 409.2334
1063.5093 | 971.5093 | 479.1279 | 434.8809 | 426.8721 | 425.7419 | 422.6571 | 364.5663 | 362.7247 | 409.2525
1064.5107 | 972.5107 | 479.2696 | 434.9423 | 426.9914 | 425.823 | 422.7432 | 364.6209 | 362.7455 | 409.2686
1065.5121 | 973.5121 | 479.3406 | 434.9935 | 427.1224 | 425.9166 | 422.8347 | 364.6838 | 362.7818 | 409.2916
1066.5136 | 974.5136 | 479.2454 | 435.02 | 427.2354 | 426.0006 | 422.9214 | 364.756 | 362.8049 | 409.2871
1067.515 | 975.515 | 479.3616 | 435.1075 | 427.3578 | 426.0971 | 423.0139 | 364.796 | 362.8409 | 409.3164
1068.5064 | 976.5064 | 479.4852 | 435.1332 | 427.4781 | 426.1812 | 423.1023 | 364.8304 | 362.8737 | 409.3339
1069.5079 | 977.5079 | 479.6168 | 435.1362 | 427.6048 | 426.2672 | 423.1942 | 364.9243 | 362.9137 | 409.3567
1070.5093 | 978.5093 | 479.7682 | 435.1864 | 427.7399 | 426.3562 | 423.28 | 364.9654 | 362.9624 | 409.3558
1071.5108 | 979.5108 | 479.7835 | 435.2217 | 427.8649 | 426.4567 | 423.3774 | 365.0037 | 363.0068 | 409.3855
1072.5122 | 980.5122 | 479.6373 | 435.2841 | 427.9962 | 426.5486 | 423.4628 | 365.0829 | 363.0444 | 409.3813
1073.5136 | 981.5136 | 479.6551 | 435.3806 | 428.1282 | 426.6455 | 423.5326 | 365.1238 | 363.0742 | 409.4028
1074.5051 | 982.5051 | 479.8501 | 435.4214 | 428.2844 | 426.7311 | 423.609 | 365.1729 | 363.0988 | 409.3925
1075.5065 | 983.5065 | 479.8191 | 435.4516 | 428.4371 | 426.8159 | 423.697 | 365.2394 | 363.1585 | 409.4118
1076.5079 | 984.5079 | 479.7023 | 435.5301 | 428.5805 | 426.8932 | 423.7701 | 365.2766 | 363.2135 | 409.4366
1077.5094 | 985.5094 | 479.4535 | 435.5987 | 428.7187 | 426.9719 | 423.8449 | 365.3044 | 363.2465 | 409.4222
1078.5108 | 986.5108 | 479.3102 | 435.7092 | 428.8685 | 427.0441 | 423.9122 | 365.315 | 363.2976 | 409.4321
1079.5123 | 987.5123 | 479.1876 | 435.7945 | 428.9985 | 427.1131 | 423.9742 | 365.3467 | 363.3474 | 409.4385
1080.5137 | 988.5137 | 479.1432 | 435.8918 | 429.0984 | 427.1788 | 424.0372 | 365.3544 | 363.3842 | 409.4619
1081.5051 | 989.5051 | 479.1724 | 435.9274 | 429.2071 | 427.2646 | 424.0951 | 365.3643 | 363.4398 | 409.4562
1082.5166 | 990.5166 | 479.1722 | 435.9407 | 429.337 | 427.4244 | 424.1528 | 365.3806 | 363.4902 | 409.4584
1083.508 | 991.508 | 479.3067 | 435.9631 | 429.4599 | 427.6237 | 424.2053 | 365.4268 | 363.5537 | 409.4518
1084.5094 | 992.5094 | 479.3471 | 435.9559 | 429.5732 | 427.811 | 424.2646 | 365.4485 | 363.604 | 409.4579
1085.5109 | 993.5109 | 479.506 | 436.0105 | 429.7004 | 428.0306 | 424.3363 | 365.5011 | 363.6532 | 409.4524
1086.5123 | 994.5123 | 479.5715 | 436.0301 | 429.8143 | 428.2831 | 424.3933 | 365.617 | 363.6982 | 409.4739
1087.5138 | 995.5138 | 479.6188 | 436.0912 | 429.9273 | 428.5504 | 424.4466 | 365.7289 | 363.7339 | 409.4569
1088.5152 | 996.5152 | 479.5101 | 436.1268 | 430.0491 | 428.7893 | 424.4958 | 365.782 | 363.7695 | 409.4616
1089.5066 | 997.5066 | 479.4035 | 436.1724 | 430.204 | 429.001 | 424.5578 | 365.8353 | 363.8005 | 409.4572
1090.5081 | 998.5081 | 479.1179 | 436.2326 | 430.3408 | 429.1882 | 424.6092 | 365.8741 | 363.8296 | 409.4574
1091.5095 | 999.5095 | 478.9055 | 436.3007 | 430.499 | 429.3495 | 424.6621 | 365.9295 | 363.8773 | 409.4477
1092.511 | 1000.511 | 478.8585 | 436.3412 | 430.6536 | 429.5116 | 424.7008 | 366.015 | 363.9109 | 409.459
1093.5124 | 1001.5124 | 479.0066 | 436.3664 | 430.799 | 429.6628 | 424.7519 | 366.0875 | 363.9303 | 409.4733
1094.5138 | 1002.5138 | 479.1071 | 436.3893 | 430.9425 | 429.8037 | 424.8001 | 366.1238 | 363.973 | 409.4519
1095.5153 | 1003.5153 | 479.0823 | 436.3888 | 431.0819 | 429.9388 | 424.8246 | 366.1574 | 364.0143 | 409.4663
1096.5167 | 1004.5167 | 479.1468 | 436.4721 | 431.231 | 430.0778 | 424.8751 | 366.1936 | 364.0644 | 409.4896
1097.5081 | 1005.5081 | 479.0784 | 436.54 | 431.3661 | 430.2004 | 424.9082 | 366.2361 | 364.0926 | 409.5121
1098.5096 | 1006.5096 | 479.0043 | 436.6007 | 431.4994 | 430.281 | 424.9423 | 366.2707 | 364.1406 | 409.5341
1099.511 | 1007.511 | 478.8317 | 436.6841 | 431.6244 | 430.3842 | 424.9893 | 366.3533 | 364.1632 | 409.5419
1100.5125 | 1008.5125 | 478.7277 | 436.7363 | 431.7433 | 430.533 | 425.0328 | 366.4556 | 364.221 | 409.5653
1101.5139 | 1009.5139 | 478.7829 | 436.7497 | 431.882 | 430.6781 | 425.0784 | 366.5021 | 364.2657 | 409.5787
1102.5153 | 1010.5153 | 478.862 | 436.7592 | 432.0066 | 430.8196 | 425.1329 | 366.5564 | 364.321 | 409.5758
1103.5168 | 1011.5168 | 478.7903 | 436.7678 | 432.1216 | 430.9353 | 425.173 | 366.5787 | 364.3656 | 409.6014
1104.5082 | 1012.5082 | 478.696 | 436.9529 | 432.2467 | 431.0518 | 425.2146 | 366.6402 | 364.4164 | 409.6151
1105.5096 | 1013.5096 | 478.5495 | 437.0535 | 432.3763 | 431.1452 | 425.2707 | 366.6879 | 364.4537 | 409.6287
1106.5111 | 1014.5111 | 478.7418 | 437.006 | 432.5244 | 431.2612 | 425.326 | 366.7655 | 364.5277 | 409.6221
1107.5125 | 1015.5125 | 478.7854 | 437.0132 | 432.6757 | 431.3844 | 425.3761 | 366.8167 | 364.5912 | 409.6138
1108.514 | 1016.514 | 478.6324 | 437.1174 | 432.8309 | 431.514 | 425.4326 | 366.8495 | 364.6603 | 409.6481
1109.5154 | 1017.5154 | 478.5153 | 437.1119 | 432.9624 | 431.6651 | 425.4719 | 366.851 | 364.7474 | 409.6677
1110.5068 | 1018.5068 | 478.4141 | 437.0885 | 433.0926 | 431.8117 | 425.5223 | 366.8993 | 364.8221 | 409.7179
1111.5083 | 1019.5083 | 478.23 | 437.1481 | 433.2216 | 431.9486 | 425.5501 | 366.9946 | 364.9136 | 409.7736
1112.5097 | 1020.5097 | 478.1586 | 437.4215 | 433.3431 | 432.0816 | 425.5976 | 367.078 | 365.0247 | 409.8771
1113.5112 | 1021.5112 | 478.231 | 437.8025 | 433.5489 | 432.258 | 425.6533 | 367.1757 | 365.1368 | 409.9996
1114.5126 | 1022.5126 | 478.4185 | 438.2808 | 433.834 | 432.5043 | 425.7146 | 367.2668 | 365.2498 | 410.1702
1115.514 | 1023.514 | 478.6662 | 438.7914 | 434.2562 | 432.9959 | 425.7779 | 367.3739 | 365.3995 | 410.4195
1116.5155 | 1024.5155 | 478.9273 | 439.064 | 434.6844 | 433.8717 | 425.8599 | 367.5277 | 365.5747 | 410.743
1117.5069 | 1025.5069 | 479.07 | 439.2978 | 435.1855 | 435.3394 | 425.9529 | 367.7133 | 365.7781 | 411.1332
1118.5083 | 1026.5083 | 479.3383 | 439.5384 | 435.7442 | 436.7153 | 426.0663 | 367.8797 | 365.9927 | 411.6572
1119.5098 | 1027.5098 | 479.7227 | 439.8955 | 436.3931 | 438.1166 | 426.1849 | 368.1092 | 366.246 | 412.2842
1120.5112 | 1028.5112 | 480.0687 | 440.2257 | 437.1065 | 439.7624 | 426.3476 | 368.3315 | 366.5403 | 413.1012
1121.5127 | 1029.5127 | 480.3902 | 440.8858 | 437.8809 | 442.1064 | 426.5757 | 368.3317 | 366.8653 | 414.0736
1122.5141 | 1030.5141 | 480.7604 | 441.4021 | 438.6767 | 445.1382 | 426.8824 | 368.4993 | 367.2257 | 415.2036
1123.5055 | 1031.5055 | 481.1119 | 442.15 | 439.5126 | 448.6991 | 427.3145 | 368.6224 | 367.5847 | 416.4632
1124.507 | 1032.507 | 481.5113 | 443.025 | 440.6122 | 452.4945 | 427.9443 | 369.0466 | 367.9897 | 417.8623
1125.5084 | 1033.5084 | 481.934 | 443.7933 | 441.5593 | 456.7338 | 428.7061 | 369.4475 | 368.4275 | 419.4446
1126.5098 | 1034.5098 | 482.0991 | 444.6598 | 442.3705 | 461.7604 | 429.6682 | 369.9203 | 368.89 | 421.1534
1127.5113 | 1035.5113 | 482.3292 | 445.5697 | 443.3596 | 466.668 | 430.8202 | 370.141 | 369.3679 | 423.0203
1128.5127 | 1036.5127 | 482.395 | 446.4723 | 444.4004 | 471.9921 | 432.2118 | 370.5107 | 369.8512 | 424.9425
1129.5142 | 1037.5142 | 482.4008 | 447.6771 | 445.3438 | 476.7493 | 433.7999 | 371.0734 | 370.3721 | 426.8854
1130.5156 | 1038.5156 | 482.3997 | 448.6042 | 446.2749 | 480.9949 | 435.4884 | 371.5521 | 370.8956 | 428.8515
1131.507 | 1039.507 | 482.4633 | 449.6032 | 447.1152 | 484.1028 | 437.3804 | 372.1389 | 371.4503 | 430.7841
1132.5085 | 1040.5085 | 482.5239 | 450.7397 | 448.0175 | 487.6994 | 439.4467 | 372.8268 | 372.0843 | 432.8313
1133.5099 | 1041.5099 | 482.4363 | 452.1459 | 449.1276 | 490.9608 | 441.4675 | 373.4638 | 372.7274 | 434.8789
1134.5113 | 1042.5113 | 482.2831 | 453.2966 | 450.3085 | 494.288 | 443.2336 | 374.3801 | 373.5316 | 436.9094
1135.5128 | 1043.5128 | 482.0796 | 454.5533 | 451.3574 | 497.5084 | 444.8217 | 375.1041 | 374.5837 | 438.8968
1136.5142 | 1044.5142 | 481.8187 | 455.6927 | 452.6484 | 500.7261 | 446.4674 | 376.3217 | 375.7386 | 440.9056
1137.5157 | 1045.5157 | 481.5231 | 457.0929 | 454.1013 | 503.3755 | 448.1275 | 377.8839 | 376.9545 | 442.992
1138.5071 | 1046.5071 | 481.2152 | 458.2188 | 455.3231 | 505.9958 | 449.6769 | 380.2033 | 378.2846 | 445.0545
1139.5085 | 1047.5085 | 480.8273 | 459.1656 | 456.5496 | 508.4856 | 451.2456 | 383.7588 | 379.6919 | 447.0416
1140.51 | 1048.51 | 480.4353 | 460.3686 | 458.4433 | 510.822 | 452.851 | 386.6597 | 381.1314 | 449.0087
1141.5114 | 1049.5114 | 480.1983 | 461.7606 | 460.5389 | 512.8632 | 454.243 | 388.7348 | 382.5426 | 450.9058
1142.5129 | 1050.5129 | 479.7251 | 462.6179 | 462.4622 | 514.0538 | 455.7318 | 391.4374 | 383.9829 | 452.7668
1143.5143 | 1051.5143 | 479.2163 | 463.5438 | 464.3195 | 515.7738 | 457.3256 | 394.223 | 385.5444 | 454.6304
1144.5157 | 1052.5157 | 478.7252 | 464.8704 | 466.3972 | 517.6308 | 458.7798 | 398.2096 | 387.125 | 456.4107
1145.5072 | 1053.5072 | 478.3154 | 466.3082 | 468.6239 | 519.2106 | 460.3345 | 402.7061 | 388.7996 | 458.1963
1146.5086 | 1054.5086 | 477.8452 | 467.5596 | 470.7587 | 520.9026 | 461.6535 | 405.7326 | 390.5779 | 460.0062
1147.51 | 1055.51 | 477.4669 | 468.6397 | 472.5615 | 522.0868 | 463.2967 | 407.3945 | 392.3231 | 461.6415
1148.5115 | 1056.5115 | 476.8526 | 469.7676 | 474.6985 | 523.8348 | 465.0385 | 409.4331 | 394.0667 | 463.4596
1149.5129 | 1057.5129 | 476.2141 | 470.9417 | 476.4723 | 525.8832 | 466.6942 | 412.1266 | 395.9414 | 465.1623
1150.5144 | 1058.5144 | 475.5285 | 472.0102 | 478.1438 | 527.9361 | 468.2995 | 416.411 | 397.6904 | 466.8361
1151.5158 | 1059.5158 | 474.9751 | 473.3129 | 480.1167 | 530.0407 | 469.8315 | 421.0149 | 399.4512 | 468.4827
1152.5072 | 1060.5072 | 474.2502 | 474.36 | 482.2649 | 532.1627 | 471.3903 | 425.7446 | 401.2694 | 470.1295
1153.5087 | 1061.5087 | 473.67 | 475.2435 | 484.5691 | 534.7733 | 472.6739 | 431.1266 | 403.1597 | 471.7507
1154.5101 | 1062.5101 | 473.1351 | 476.8071 | 486.7796 | 536.8942 | 473.7406 | 435.9351 | 405.0446 | 473.2739
1155.5115 | 1063.5115 | 472.4817 | 477.872 | 488.6872 | 538.5178 | 474.9059 | 440.53 | 406.9173 | 474.7906
1156.513 | 1064.513 | 471.845 | 479.0865 | 490.5906 | 540.0609 | 476.4576 | 444.5538 | 408.8973 | 476.3447
1157.5044 | 1065.5044 | 471.1995 | 479.7555 | 491.9206 | 541.9731 | 477.7349 | 448.3511 | 410.9415 | 477.8365
1158.5058 | 1066.5058 | 470.5686 | 480.9957 | 493.5765 | 543.4173 | 479.1832 | 452.6899 | 412.9791 | 479.3015
1159.5073 | 1067.5073 | 469.889 | 482.0537 | 494.9988 | 545.0725 | 480.358 | 456.7125 | 415.0278 | 480.8041
1160.5087 | 1068.5087 | 469.3217 | 483.1637 | 496.0871 | 546.619 | 481.3701 | 460.6522 | 417.0975 | 482.3578
1161.5102 | 1069.5102 | 468.8901 | 484.141 | 497.1103 | 547.9094 | 482.2702 | 464.4416 | 419.1517 | 483.9297
1162.5116 | 1070.5116 | 468.4202 | 485.3212 | 498.3182 | 548.6835 | 482.5542 | 468.0165 | 421.1794 | 485.5129
1163.513 | 1071.513 | 467.9687 | 486.4108 | 499.5163 | 550.0422 | 483.7783 | 470.9605 | 423.0258 | 487.094
1164.5145 | 1072.5145 | 467.3654 | 487.6553 | 500.6983 | 550.9499 | 484.5367 | 473.3335 | 424.9768 | 488.6569
1165.5059 | 1073.5059 | 466.7055 | 488.9015 | 502.2361 | 551.2764 | 485.598 | 475.8685 | 426.8063 | 490.2708
1166.5074 | 1074.5074 | 466.1188 | 490.0199 | 503.7367 | 552.0024 | 487.0719 | 477.8365 | 428.6324 | 491.9351
1167.5088 | 1075.5088 | 465.5624 | 491.1928 | 505.0842 | 552.3955 | 488.3074 | 479.8229 | 430.3388 | 493.5928
1168.5102 | 1076.5102 | 465.0818 | 492.2966 | 506.1755 | 552.5604 | 489.5914 | 481.6043 | 432.0677 | 495.1887
1169.5117 | 1077.5117 | 464.6853 | 493.3858 | 507.1473 | 553.3121 | 490.6605 | 483.6023 | 433.819 | 496.7121
1170.5131 | 1078.5131 | 464.2065 | 494.4126 | 508.1019 | 554.2701 | 491.5212 | 485.7573 | 435.4557 | 498.1453
1171.5146 | 1079.5146 | 463.8586 | 495.5974 | 509.0393 | 554.7366 | 492.055 | 488.26 | 437.1346 | 499.6727
1172.516 | 1080.516 | 463.3918 | 496.8358 | 510.1642 | 555.4626 | 493.4266 | 490.1073 | 438.6702 | 500.9582
1173.5074 | 1081.5074 | 462.8673 | 498.2968 | 511.6351 | 556.0514 | 494.0227 | 492.2157 | 440.0556 | 502.2469
1174.5089 | 1082.5089 | 462.3454 | 499.6325 | 513.0052 | 556.8392 | 494.8703 | 493.7626 | 441.557 | 503.6147
1175.5103 | 1083.5103 | 461.8477 | 500.7164 | 514.2979 | 557.3139 | 495.5071 | 495.6795 | 442.9207 | 505.045
1176.5117 | 1084.5117 | 461.294 | 501.7927 | 515.5512 | 558.056 | 496.5256 | 497.4114 | 444.3966 | 506.4664
1177.5132 | 1085.5132 | 460.579 | 502.8677 | 516.8164 | 558.9259 | 497.4128 | 498.4383 | 445.8135 | 507.783
1178.5046 | 1086.5046 | 460.1225 | 503.9538 | 518.064 | 559.9699 | 498.3787 | 499.1172 | 447.1236 | 509.0471
1179.506 | 1087.506 | 459.6013 | 505.0388 | 519.2429 | 560.9722 | 499.367 | 500.1752 | 448.5062 | 510.3049
1180.5075 | 1088.5075 | 459.04 | 506.1603 | 520.466 | 562.4003 | 500.0244 | 501.124 | 449.7097 | 511.6015
1181.5089 | 1089.5089 | 458.6614 | 507.1837 | 521.7316 | 563.77 | 501.027 | 502.1518 | 451.0647 | 512.8223
1182.5104 | 1090.5104 | 458.1147 | 508.1231 | 522.9099 | 564.649 | 501.5514 | 503.1188 | 452.405 | 514.0775
1183.5118 | 1091.5118 | 457.6172 | 509.0405 | 524.0217 | 565.5488 | 502.1011 | 503.8183 | 453.5269 | 515.2967
1184.5132 | 1092.5132 | 457.231 | 509.9687 | 525.1254 | 566.4863 | 502.9333 | 504.0899 | 454.718 | 516.52
1185.5147 | 1093.5147 | 456.7106 | 510.9614 | 526.3766 | 567.6839 | 503.801 | 504.3348 | 455.7332 | 517.6994
1186.5161 | 1094.5161 | 456.0992 | 511.9331 | 527.4828 | 569.208 | 504.7491 | 504.3065 | 456.6194 | 518.7684
1187.5076 | 1095.5076 | 455.5437 | 512.8821 | 528.5669 | 570.4036 | 505.7512 | 504.5014 | 457.5718 | 519.7612
1188.509 | 1096.509 | 454.9339 | 513.8278 | 529.5088 | 571.4787 | 506.7556 | 504.3356 | 458.3248 | 520.6898
1189.5104 | 1097.5104 | 454.5203 | 514.8048 | 530.4932 | 572.3024 | 507.8668 | 504.2992 | 459.0264 | 521.7256
1190.5119 | 1098.5119 | 454.0526 | 515.8137 | 531.4504 | 573.2736 | 508.9781 | 503.9165 | 459.9094 | 522.7697
1191.5133 | 1099.5133 | 453.4282 | 516.8431 | 532.4716 | 573.9607 | 510.0381 | 503.365 | 460.6022 | 523.8287
1192.5148 | 1100.5148 | 452.8079 | 517.8748 | 533.5323 | 574.4966 | 511.2199 | 502.5933 | 461.2395 | 524.7334
1193.5262 | 1101.5262 | 452.2433 | 518.8484 | 534.7308 | 575.1945 | 512.4073 | 501.8899 | 462.0126 | 525.5744
1194.5076 | 1102.5076 | 451.6481 | 519.7887 | 535.96 | 575.6612 | 513.5739 | 501.271 | 462.8076 | 526.2701
1195.5091 | 1103.5091 | 451.0067 | 520.7346 | 537.1419 | 576.0223 | 514.7836 | 500.9883 | 463.5781 | 526.8512
1196.5105 | 1104.5105 | 450.5136 | 521.7612 | 538.382 | 576.5125 | 515.9973 | 501.1062 | 464.3156 | 527.5321
1197.5119 | 1105.5119 | 449.8997 | 522.7004 | 539.5183 | 576.6756 | 517.2877 | 501.0845 | 465.1562 | 528.1402
1198.5134 | 1106.5134 | 449.2689 | 523.6944 | 540.6116 | 576.9684 | 518.5661 | 500.7469 | 466.1239 | 528.7694
1199.5048 | 1107.5048 | 448.617 | 524.6198 | 541.5831 | 577.9641 | 519.8496 | 500.5731 | 467.0465 | 529.315
1200.5062 | 1108.5062 | 448.0449 | 525.6609 | 542.5467 | 578.742 | 521.1443 | 500.2663 | 467.9112 | 529.8379
1201.5077 | 1109.5077 | 447.2598 | 526.657 | 543.3943 | 579.8724 | 522.442 | 500.1026 | 468.8842 | 530.271
1202.5091 | 1110.5091 | 446.5302 | 527.588 | 544.1368 | 580.7552 | 523.8165 | 500.1476 | 469.8403 | 530.7769
1203.5106 | 1111.5106 | 445.9965 | 528.4807 | 544.7202 | 581.9425 | 525.1163 | 500.1962 | 470.984 | 531.1908
1204.512 | 1112.512 | 445.4293 | 529.3536 | 545.3066 | 583.0325 | 526.4651 | 500.1476 | 472.1267 | 531.57
1205.5134 | 1113.5134 | 444.8053 | 530.2236 | 545.8167 | 583.8013 | 527.811 | 500.3009 | 473.1287 | 531.9113
1206.5049 | 1114.5049 | 444.2023 | 530.9646 | 546.1274 | 584.5517 | 529.1855 | 500.7511 | 474.242 | 532.2764
1207.5063 | 1115.5063 | 443.4165 | 531.7858 | 546.4791 | 585.5874 | 530.4861 | 500.6186 | 475.1741 | 532.5529
1208.5077 | 1116.5077 | 442.6448 | 532.5339 | 546.7487 | 586.4898 | 531.8016 | 500.545 | 476.2769 | 532.8117
1209.5092 | 1117.5092 | 441.9515 | 533.2992 | 547.0215 | 587.2416 | 533.0273 | 501.0594 | 477.3666 | 533.0615
1210.5106 | 1118.5106 | 441.3285 | 533.9638 | 547.1565 | 588.2913 | 534.2477 | 501.1383 | 478.3472 | 533.2971
1211.5121 | 1119.5121 | 440.6591 | 534.7029 | 547.3486 | 588.8649 | 535.3655 | 501.6024 | 479.2471 | 533.4485
1212.5135 | 1120.5135 | 439.9895 | 535.4199 | 547.5656 | 589.4807 | 536.4934 | 501.6005 | 480.0574 | 533.5518
1213.5149 | 1121.5149 | 439.4599 | 536.1092 | 547.7183 | 589.8189 | 537.4915 | 501.6445 | 480.8793 | 533.6254
1214.5064 | 1122.5064 | 438.9301 | 536.8223 | 547.8403 | 590.3044 | 538.4413 | 501.8314 | 481.8133 | 533.741
1215.5078 | 1123.5078 | 438.3974 | 537.4706 | 547.9531 | 590.5587 | 539.2522 | 502.275 | 482.6974 | 533.7994
1216.5093 | 1124.5093 | 437.8091 | 538.1837 | 548.146 | 590.8138 | 539.98 | 502.8107 | 483.6041 | 533.8313
1217.5107 | 1125.5107 | 437.0395 | 538.8575 | 548.2939 | 590.9956 | 540.6442 | 503.4829 | 484.4072 | 533.843
1218.5121 | 1126.5121 | 436.2835 | 539.5307 | 548.4495 | 591.8901 | 541.2301 | 504.185 | 485.1093 | 533.7867
1219.5136 | 1127.5136 | 435.5504 | 540.098 | 548.5543 | 591.9572 | 541.7452 | 505.0532 | 485.8024 | 533.8098
1220.505 | 1128.505 | 434.8944 | 540.771 | 548.6704 | 591.6964 | 542.143 | 505.654 | 486.5107 | 533.7461
1221.5064 | 1129.5064 | 434.2384 | 541.3668 | 548.743 | 591.2191 | 542.4331 | 505.8054 | 487.1535 | 533.6639
1222.5079 | 1130.5079 | 433.6638 | 541.9295 | 548.8065 | 590.48 | 542.64 | 505.5 | 487.7716 | 533.5645
1223.5093 | 1131.5093 | 432.9966 | 542.5132 | 548.9054 | 589.8576 | 542.8217 | 505.6433 | 488.3529 | 533.528
1224.5108 | 1132.5108 | 432.4089 | 543.071 | 548.9417 | 589.4624 | 543.0468 | 506.0321 | 488.7385 | 533.4293
1225.5122 | 1133.5122 | 431.9012 | 543.6166 | 548.9648 | 588.8738 | 543.1953 | 506.4038 | 488.9676 | 533.3166
1226.5136 | 1134.5136 | 431.1816 | 544.1225 | 549.0035 | 588.3957 | 543.4485 | 506.6027 | 489.1483 | 533.1727
1227.5151 | 1135.5151 | 430.5174 | 544.5336 | 549.036 | 587.6991 | 543.6303 | 506.9393 | 489.3454 | 533.0298
1228.5165 | 1136.5165 | 429.8292 | 544.9493 | 549.0291 | 587.0181 | 543.6773 | 507.3364 | 489.5089 | 532.8467
1229.5079 | 1137.5079 | 429.1571 | 545.289 | 549.0395 | 586.4546 | 543.7563 | 506.9943 | 489.6731 | 532.6154
1230.5094 | 1138.5094 | 428.588 | 545.7395 | 549.0375 | 586.0722 | 543.8882 | 507.7603 | 489.731 | 532.2961
1231.5108 | 1139.5108 | 427.9279 | 546.1777 | 549.0654 | 585.4824 | 543.9962 | 507.6832 | 489.8105 | 531.9962
1232.5123 | 1140.5123 | 427.2589 | 546.5379 | 549.0309 | 584.9271 | 544.1832 | 508.1722 | 490.0057 | 531.7025
1233.5137 | 1141.5137 | 426.5545 | 546.801 | 549.0312 | 584.1333 | 544.2286 | 508.3824 | 490.1472 | 531.4329
1234.5151 | 1142.5151 | 425.9548 | 547.0876 | 549.0007 | 583.7877 | 544.3043 | 508.7478 | 490.2962 | 531.0775
1235.5066 | 1143.5066 | 425.4544 | 547.2152 | 548.9831 | 583.1732 | 544.2461 | 508.8615 | 490.4465 | 530.7149
1236.508 | 1144.508 | 424.9439 | 547.5482 | 548.9704 | 582.8305 | 544.2324 | 509.0612 | 490.4623 | 530.3265
1237.5095 | 1145.5095 | 424.4196 | 547.7178 | 548.936 | 583.9262 | 544.2012 | 509.1096 | 490.5214 | 529.901
1238.5109 | 1146.5109 | 423.8628 | 548.0097 | 548.8809 | 584.7381 | 544.2285 | 509.6934 | 490.445 | 529.4723
1239.5123 | 1147.5123 | 423.2691 | 548.1916 | 548.8261 | 583.2575 | 544.1746 | 509.6867 | 490.3825 | 528.9477
1240.5138 | 1148.5138 | 422.5693 | 548.3182 | 548.805 | 581.1045 | 544.1433 | 509.8013 | 490.3705 | 528.4047
1241.5052 | 1149.5052 | 421.9114 | 548.4159 | 548.736 | 579.42 | 544.0422 | 509.6769 | 490.3032 | 527.8161
1242.5066 | 1150.5066 | 421.2482 | 548.4826 | 548.6311 | 578.1923 | 543.9616 | 509.3758 | 490.2562 | 527.2205
1243.5081 | 1151.5081 | 420.7084 | 548.5938 | 548.5772 | 575.4539 | 543.7345 | 509.7438 | 490.2461 | 526.5988
1244.5095 | 1152.5095 | 420.151 | 548.813 | 548.4799 | 573.1918 | 543.6343 | 509.7273 | 490.2879 | 525.9287
1245.511 | 1153.511 | 419.5218 | 548.8696 | 548.3928 | 571.413 | 543.507 | 509.8868 | 490.3841 | 525.2633
1246.5124 | 1154.5124 | 418.8641 | 549.0025 | 548.2983 | 570.0416 | 543.1963 | 509.9994 | 490.3994 | 524.5754
1247.5138 | 1155.5138 | 418.2819 | 549.0626 | 548.1948 | 568.9418 | 542.8523 | 509.9303 | 490.1769 | 523.8747
1248.5053 | 1156.5053 | 417.6005 | 549.1028 | 548.107 | 568.2176 | 542.5181 | 509.6858 | 490.0542 | 523.1285
1249.5067 | 1157.5067 | 416.9098 | 549.0992 | 547.9984 | 567.1728 | 542.3147 | 509.803 | 489.9831 | 522.3942
1250.5081 | 1158.5081 | 416.2747 | 549.0157 | 547.8902 | 566.6984 | 542.1618 | 510.1838 | 489.8822 | 521.5905
1251.5096 | 1159.5096 | 415.6937 | 549.0192 | 547.7599 | 565.963 | 541.8818 | 510.4211 | 489.7386 | 520.7488
1252.511 | 1160.511 | 415.023 | 548.9494 | 547.6549 | 565.3429 | 541.5797 | 510.7302 | 489.5557 | 519.8818
1253.5125 | 1161.5125 | 414.3664 | 548.9832 | 547.4869 | 564.9275 | 541.3298 | 511.1356 | 489.3595 | 518.9433
1254.5139 | 1162.5139 | 413.7456 | 548.8728 | 547.3425 | 564.2922 | 541.0082 | 511.5288 | 489.2583 | 517.9453
1255.5153 | 1163.5153 | 413.0421 | 548.8611 | 547.2146 | 564.2585 | 540.766 | 511.9222 | 489.1468 | 516.9174
1256.5168 | 1164.5168 | 412.4386 | 548.7834 | 547.101 | 564.0783 | 540.4714 | 512.082 | 489.2389 | 515.852
1257.5082 | 1165.5082 | 411.9721 | 548.6567 | 546.9848 | 563.4635 | 540.18 | 512.3225 | 489.3536 | 514.8017
1258.5096 | 1166.5096 | 411.5089 | 548.5627 | 546.8462 | 562.9715 | 539.8125 | 512.2838 | 489.4425 | 513.7182
1259.5111 | 1167.5111 | 410.9307 | 548.5155 | 546.7189 | 562.8288 | 539.5004 | 512.155 | 489.5101 | 512.6474
1260.5125 | 1168.5125 | 410.3287 | 548.4676 | 546.579 | 562.5393 | 539.1172 | 512.0316 | 489.5977 | 511.5278
1261.514 | 1169.514 | 409.856 | 548.4218 | 546.4101 | 561.9741 | 538.8692 | 511.7867 | 489.7588 | 510.3557
1262.5054 | 1170.5054 | 409.2734 | 548.3271 | 546.2755 | 561.459 | 538.5018 | 511.9366 | 490.0087 | 509.1737
1263.5068 | 1171.5068 | 408.6068 | 548.2814 | 546.1457 | 560.8121 | 538.1659 | 512.2285 | 490.1633 | 507.9287
1264.5083 | 1172.5083 | 408.0889 | 548.1885 | 545.9845 | 560.1945 | 537.859 | 512.7454 | 490.2179 | 506.6463
1265.5097 | 1173.5097 | 407.5089 | 548.0083 | 545.8424 | 559.8307 | 537.5977 | 513.1945 | 490.3776 | 505.3517
1266.5112 | 1174.5112 | 406.969 | 547.9046 | 545.7128 | 559.4832 | 537.2807 | 513.7095 | 490.4333 | 504.02
1267.5126 | 1175.5126 | 406.4344 | 547.7761 | 545.5872 | 559.4015 | 537.0023 | 513.467 | 490.5252 | 502.6713
1268.514 | 1176.514 | 405.8556 | 547.6276 | 545.4437 | 558.9474 | 536.6606 | 513.4161 | 490.5416 | 501.3443
1269.5155 | 1177.5155 | 405.3088 | 547.462 | 545.2922 | 558.6214 | 536.4084 | 513.4869 | 490.4826 | 499.9753
1270.5069 | 1178.5069 | 404.7064 | 547.2841 | 545.1386 | 558.4539 | 536.2221 | 513.6521 | 490.3474 | 498.7235
1271.5083 | 1179.5083 | 404.0725 | 547.1187 | 544.9701 | 558.2876 | 535.9293 | 513.9224 | 490.357 | 497.3615
1272.5098 | 1180.5098 | 403.4264 | 546.9054 | 544.807 | 558.0137 | 535.5986 | 514.3511 | 490.2686 | 496.0396
1273.5112 | 1181.5112 | 402.7782 | 546.7596 | 544.6569 | 557.5248 | 535.3351 | 514.5233 | 490.179 | 494.6878
1274.5127 | 1182.5127 | 402.1224 | 546.588 | 544.517 | 556.8171 | 535.0349 | 514.5957 | 490.1108 | 493.3687
1275.5141 | 1183.5141 | 401.4197 | 546.4182 | 544.3812 | 556.2648 | 534.7514 | 514.7661 | 490.0891 | 492.0495
1276.5155 | 1184.5155 | 400.8152 | 546.1622 | 544.2348 | 555.7357 | 534.5264 | 514.8938 | 490.064 | 490.7301
1277.507 | 1185.507 | 400.3724 | 545.9588 | 544.058 | 555.3369 | 534.2977 | 514.9981 | 490.0064 | 489.4295
1278.5084 | 1186.5084 | 400.0647 | 545.6939 | 543.8981 | 554.7384 | 534.038 | 515.1854 | 489.9467 | 488.1329
1279.5098 | 1187.5098 | 399.6915 | 545.4402 | 543.7422 | 553.9662 | 533.7476 | 515.2769 | 489.8403 | 486.8581
1280.5113 | 1188.5113 | 399.1321 | 545.3153 | 543.6047 | 553.2446 | 533.3712 | 515.2403 | 489.787 | 485.5705
1281.5127 | 1189.5127 | 398.5128 | 545.127 | 543.4107 | 552.6053 | 533.0217 | 515.3818 | 489.6766 | 484.2832
1282.5142 | 1190.5142 | 397.789 | 544.8758 | 543.2333 | 552.034 | 532.7144 | 515.8402 | 489.6419 | 483.0059
1283.5056 | 1191.5056 | 397.1119 | 544.6404 | 543.0748 | 551.1876 | 532.3836 | 516.3115 | 489.5056 | 481.7798
1284.507 | 1192.507 | 396.4942 | 544.3912 | 542.8942 | 550.2671 | 532.1573 | 516.7033 | 489.4539 | 480.5696
1285.5085 | 1193.5085 | 395.9944 | 544.1799 | 542.731 | 549.0892 | 531.9248 | 516.9555 | 489.4421 | 479.3892
1286.5099 | 1194.5099 | 395.4981 | 543.9529 | 542.5267 | 548.2137 | 531.6973 | 516.9677 | 489.3953 | 478.2172
1287.5114 | 1195.5114 | 394.903 | 543.6947 | 542.377 | 546.7802 | 531.444 | 516.9998 | 489.3878 | 477.0339
1288.5128 | 1196.5128 | 394.3495 | 543.4476 | 542.212 | 546.1079 | 531.1262 | 517.1117 | 489.408 | 475.8563
1289.5142 | 1197.5142 | 393.7497 | 543.1667 | 542.0129 | 545.3299 | 530.8125 | 517.1766 | 489.4414 | 474.6885
1290.5057 | 1198.5057 | 393.1689 | 542.9904 | 541.8332 | 544.2339 | 530.6728 | 517.2499 | 489.4342 | 473.5252
1291.5071 | 1199.5071 | 392.6689 | 542.723 | 541.6281 | 543.278 | 530.4348 | 517.4666 | 489.4324 | 472.3593
1292.5085 | 1200.5085 | 392.1717 | 542.5039 | 541.4379 | 542.1425 | 530.17 | 517.5461 | 489.3822 | 471.198
1293.51 | 1201.51 | 391.6108 | 542.3006 | 541.2608 | 540.924 | 529.8575 | 517.6609 | 489.4297 | 470.0269
1294.5114 | 1202.5114 | 391.0969 | 542.0819 | 541.0756 | 539.6803 | 529.6774 | 517.9285 | 489.4969 | 468.901
1295.5129 | 1203.5129 | 390.5664 | 541.9327 | 540.8697 | 538.4443 | 529.4822 | 518.052 | 489.5357 | 467.7845
1296.5143 | 1204.5143 | 390.0088 | 541.696 | 540.6894 | 537.1444 | 529.1462 | 518.241 | 489.572 | 466.6764
1297.5157 | 1205.5157 | 389.3946 | 541.4921 | 540.5486 | 535.8021 | 528.8838 | 518.3021 | 489.5716 | 465.5744
1298.5072 | 1206.5072 | 388.8888 | 541.2178 | 540.3822 | 534.38 | 528.6221 | 518.5753 | 489.535 | 464.4695
1299.5086 | 1207.5086 | 388.3461 | 541.0684 | 540.2449 | 532.9194 | 528.3949 | 518.8298 | 489.5364 | 463.3614
1300.51 | 1208.51 | 387.8963 | 540.8343 | 540.0708 | 531.3376 | 528.2051 | 519.2043 | 489.569 | 462.321
1301.5115 | 1209.5115 | 387.5035 | 540.5683 | 539.8883 | 530.0471 | 528.0345 | 519.5251 | 489.5777 | 461.28
1302.5129 | 1210.5129 | 386.9312 | 540.3678 | 539.7195 | 528.5426 | 527.7613 | 519.7921 | 489.5761 | 460.1683
1303.5144 | 1211.5144 | 386.4431 | 540.096 | 539.5573 | 526.8794 | 527.5493 | 520.1 | 489.5641 | 459.1442
1304.5158 | 1212.5158 | 385.9772 | 539.9208 | 539.3866 | 525.5055 | 527.3991 | 520.3376 | 489.5536 | 458.1311
1305.5072 | 1213.5072 | 385.5435 | 539.6769 | 539.1755 | 524.0685 | 527.205 | 520.763 | 489.516 | 457.08
1306.5087 | 1214.5087 | 384.9462 | 539.3976 | 538.9975 | 522.6596 | 526.943 | 521.118 | 489.5045 | 456.0638
1307.5101 | 1215.5101 | 384.3037 | 539.1908 | 538.813 | 521.4362 | 526.696 | 521.6251 | 489.4497 | 455.0064
1308.5115 | 1216.5115 | 383.6708 | 538.95 | 538.6274 | 520.1075 | 526.3995 | 522.1213 | 489.4616 | 453.9927
1309.513 | 1217.513 | 383.0387 | 538.7345 | 538.4436 | 518.8229 | 526.1981 | 522.421 | 489.5523 | 453.0018
1310.5144 | 1218.5144 | 382.4994 | 538.4941 | 538.2795 | 517.4454 | 525.9213 | 522.7316 | 489.5991 | 452.0201
1311.5159 | 1219.5159 | 381.8834 | 538.2781 | 538.0825 | 516.2854 | 525.741 | 523.2962 | 489.6922 | 451.0258
1312.5073 | 1220.5073 | 381.1675 | 538.0314 | 537.8992 | 515.1483 | 525.4966 | 523.8341 | 489.7987 | 450.0534
1313.5087 | 1221.5087 | 380.4374 | 537.847 | 537.7206 | 514.1403 | 525.3069 | 524.3841 | 489.9436 | 449.0842
1314.5102 | 1222.5102 | 379.7339 | 537.701 | 537.5379 | 512.841 | 525.1112 | 525.2282 | 490.079 | 448.1024
1315.5116 | 1223.5116 | 379.068 | 537.4261 | 537.3551 | 511.6745 | 524.9241 | 526.148 | 490.1577 | 447.1475
1316.5131 | 1224.5131 | 378.5163 | 537.2179 | 537.1596 | 509.9447 | 524.7936 | 526.9419 | 490.2565 | 446.2169
1317.5145 | 1225.5145 | 378.0072 | 536.9804 | 536.9697 | 508.6483 | 524.6202 | 527.6896 | 490.3658 | 445.2857
1318.5159 | 1226.5159 | 377.4137 | 536.7275 | 536.7873 | 507.8593 | 524.5338 | 528.5431 | 490.4501 | 444.3412
1319.5074 | 1227.5074 | 376.902 | 536.4965 | 536.5898 | 506.7398 | 524.3656 | 529.4599 | 490.5099 | 443.4255
1320.5088 | 1228.5088 | 376.3826 | 536.2859 | 536.3708 | 505.8042 | 524.1411 | 530.4252 | 490.5914 | 442.4979
1321.5102 | 1229.5102 | 375.7627 | 536.0477 | 536.1943 | 504.9345 | 523.9458 | 531.5886 | 490.6759 | 441.5853
1322.5117 | 1230.5117 | 375.1727 | 535.8628 | 535.9964 | 503.9231 | 523.7545 | 532.7412 | 490.7104 | 440.6773
1323.5131 | 1231.5131 | 374.5568 | 535.6201 | 535.8035 | 502.876 | 523.5783 | 533.9772 | 490.7858 | 439.7813
1324.5146 | 1232.5146 | 374.111 | 535.3885 | 535.6153 | 501.9499 | 523.4371 | 534.8874 | 490.8235 | 438.8904
1325.516 | 1233.516 | 373.6727 | 535.1292 | 535.3998 | 500.8886 | 523.2117 | 536.0164 | 490.8156 | 438.0012
1326.5074 | 1234.5074 | 373.141 | 534.8795 | 535.2029 | 499.9976 | 523.1029 | 537.7719 | 490.867 | 437.1176
1327.5089 | 1235.5089 | 372.5668 | 534.6791 | 534.9977 | 498.951 | 522.8184 | 539.5758 | 490.8931 | 436.2411
1328.5103 | 1236.5103 | 372.076 | 534.4048 | 534.8046 | 497.5646 | 522.575 | 540.4157 | 490.9391 | 435.3586
1329.5117 | 1237.5117 | 371.4767 | 534.1374 | 534.5859 | 496.6658 | 522.3477 | 541.1749 | 491.008 | 434.4808
1330.5132 | 1238.5132 | 370.8956 | 533.9487 | 534.4014 | 495.7123 | 522.1078 | 541.4603 | 491.1005 | 433.6201
1331.5046 | 1239.5046 | 370.324 | 533.7304 | 534.188 | 494.8833 | 521.855 | 541.535 | 491.212 | 432.777
1332.506 | 1240.506 | 369.7844 | 533.488 | 533.9652 | 493.9375 | 521.6019 | 541.407 | 491.3265 | 431.9096
1333.5075 | 1241.5075 | 369.2651 | 533.269 | 533.7688 | 492.9516 | 521.4585 | 541.2239 | 491.4526 | 431.07
1334.5089 | 1242.5089 | 368.8468 | 533.0761 | 533.5684 | 492.203 | 521.2087 | 541.0093 | 491.5479 | 430.2032
1335.5104 | 1243.5104 | 368.4617 | 532.8785 | 533.3844 | 491.2336 | 520.9991 | 540.9106 | 491.6507 | 429.3679
1336.5118 | 1244.5118 | 368.1239 | 532.6186 | 533.1759 | 490.3589 | 520.8011 | 540.7911 | 491.7592 | 428.5162
1337.5132 | 1245.5132 | 367.7536 | 532.3509 | 532.9435 | 489.6445 | 520.6767 | 540.5181 | 491.8726 | 427.6624
1338.5147 | 1246.5147 | 367.3648 | 532.1615 | 532.7106 | 488.8107 | 520.4688 | 540.2312 | 491.9799 | 426.8032
1339.5161 | 1247.5161 | 366.7764 | 531.9521 | 532.5061 | 488.0417 | 520.1882 | 539.9965 | 492.0402 | 425.9587
1340.5076 | 1248.5076 | 366.1366 | 531.7915 | 532.2975 | 487.1704 | 519.969 | 539.4869 | 492.098 | 425.1375
1341.509 | 1249.509 | 365.5691 | 531.5596 | 532.0931 | 486.2654 | 519.7395 | 539.1729 | 492.1628 | 424.3238
1342.5104 | 1250.5104 | 365.1375 | 531.3217 | 531.8719 | 485.323 | 519.4838 | 538.8688 | 492.1937 | 423.4902
1343.5119 | 1251.5119 | 364.7219 | 531.1782 | 531.6702 | 484.5755 | 519.2407 | 538.3518 | 492.1695 | 422.663
1344.5133 | 1252.5133 | 364.1547 | 530.9885 | 531.471 | 483.5726 | 519.0813 | 537.5755 | 492.1532 | 421.8648
1345.5148 | 1253.5148 | 363.6819 | 530.8082 | 531.2613 | 483.0958 | 518.8328 | 536.9233 | 492.1018 | 421.0574
1346.5162 | 1254.5162 | 363.2644 | 530.609 | 531.0626 | 482.2162 | 518.5869 | 536.1622 | 492.041 | 420.2669
1347.5076 | 1255.5076 | 362.7817 | 530.4405 | 530.8794 | 481.326 | 518.2945 | 535.3815 | 491.9917 | 419.4686
1348.5091 | 1256.5091 | 362.2894 | 530.2177 | 530.6765 | 480.5454 | 518.0332 | 534.5376 | 491.9657 | 418.6776
1349.5105 | 1257.5105 | 361.7236 | 530.0166 | 530.4708 | 479.7135 | 517.7622 | 533.6173 | 491.9586 | 417.8905
1350.5119 | 1258.5119 | 361.2406 | 529.838 | 530.2738 | 478.8681 | 517.5178 | 532.6564 | 491.9607 | 417.1337
1351.5134 | 1259.5134 | 360.6888 | 529.6606 | 530.0831 | 477.8576 | 517.2669 | 531.8555 | 491.9708 | 416.3598
1352.5048 | 1260.5048 | 360.1371 | 529.4326 | 529.8708 | 477.1808 | 517.064 | 530.8678 | 491.9949 | 415.604
1353.5163 | 1261.5163 | 359.5642 | 529.2532 | 529.6915 | 476.4958 | 516.7993 | 529.9538 | 492.011 | 414.8638
1354.5077 | 1262.5077 | 359.0423 | 529.0303 | 529.4948 | 475.7936 | 516.6062 | 529.0581 | 492.0384 | 414.1003
1355.5091 | 1263.5091 | 358.5357 | 528.8255 | 529.2909 | 474.9063 | 516.3585 | 528.0901 | 492.0569 | 413.3589
1356.5106 | 1264.5106 | 358.029 | 528.6246 | 529.1059 | 474.1829 | 516.0948 | 527.1457 | 492.0816 | 412.5859
1357.512 | 1265.512 | 357.6323 | 528.4099 | 528.8989 | 473.2933 | 515.8295 | 526.1609 | 492.1153 | 411.8343
1358.5134 | 1266.5134 | 357.1786 | 528.2258 | 528.6912 | 472.5266 | 515.5558 | 525.0801 | 492.1595 | 411.0768
1359.5149 | 1267.5149 | 356.6661 | 528.0055 | 528.4656 | 471.8176 | 515.311 | 524.2299 | 492.1956 | 410.3256
1360.5163 | 1268.5163 | 356.0649 | 527.8563 | 528.2566 | 470.272 | 515.0539 | 523.5828 | 492.2464 | 409.5835
1361.5078 | 1269.5078 | 355.3754 | 527.673 | 528.0397 | 469.4452 | 514.7491 | 522.7133 | 492.3085 | 408.8387
1362.5092 | 1270.5092 | 354.8141 | 527.4869 | 527.8195 | 468.5946 | 514.5053 | 521.9972 | 492.3708 | 408.0929
1363.5106 | 1271.5106 | 354.3672 | 527.262 | 527.5921 | 467.7711 | 514.3055 | 520.9844 | 492.4377 | 407.3582
1364.5121 | 1272.5121 | 353.8235 | 527.0769 | 527.3706 | 467.0817 | 514.0096 | 520.0235 | 492.5107 | 406.631
1365.5135 | 1273.5135 | 353.1062 | 526.9 | 527.146 | 466.5206 | 513.7373 | 519.2542 | 492.586 | 405.9307
1366.515 | 1274.515 | 352.4996 | 526.709 | 526.926 | 465.894 | 513.4665 | 518.5809 | 492.6836 | 405.2156
1367.5064 | 1275.5064 | 351.9831 | 526.4926 | 526.6787 | 465.0474 | 513.214 | 517.7 | 492.7943 | 404.526
1368.5078 | 1276.5078 | 351.5348 | 526.2749 | 526.4456 | 464.2629 | 512.9788 | 516.7428 | 492.918 | 403.8055
1369.5093 | 1277.5093 | 351.0991 | 526.0408 | 526.2237 | 463.138 | 512.763 | 515.8334 | 493.0534 | 403.0978
1370.5107 | 1278.5107 | 350.6164 | 525.8513 | 525.9914 | 462.5209 | 512.5136 | 515.068 | 493.2023 | 402.3991
1371.5121 | 1279.5121 | 350.0947 | 525.6721 | 525.7822 | 461.8299 | 512.2838 | 514.2608 | 493.415 | 401.6897
1372.5136 | 1280.5136 | 349.7382 | 525.4819 | 525.5469 | 461.1507 | 512.0154 | 513.4094 | 493.6723 | 400.9721
1373.505 | 1281.505 | 349.4334 | 525.2996 | 525.3392 | 460.5176 | 511.7608 | 512.4078 | 493.9219 | 400.2711
1374.6266 | 1282.6266 | 348.9514 | 525.0604 | 525.1141 | 459.4339 | 511.5154 | 511.4061 | 494.1889 | 399.4974
1375.5079 | 1283.5079 | 348.537 | 524.8937 | 524.9182 | 458.8515 | 511.2516 | 510.5893 | 494.4458 | 398.8893
1376.5093 | 1284.5093 | 347.9817 | 524.6884 | 524.6833 | 458.0483 | 510.9528 | 509.6549 | 494.7432 | 398.2036
1377.5108 | 1285.5108 | 347.4407 | 524.4906 | 524.4684 | 457.3862 | 510.6892 | 508.7876 | 495.0442 | 397.5287
1378.5122 | 1286.5122 | 346.8553 | 524.3018 | 524.2347 | 456.617 | 510.4208 | 507.9148 | 495.3537 | 396.8436
1379.5136 | 1287.5136 | 346.3999 | 524.1031 | 524.0086 | 455.8887 | 510.2344 | 507.0359 | 495.6782 | 396.1544
1380.5051 | 1288.5051 | 346.0189 | 523.9101 | 523.8004 | 455.2564 | 509.986 | 506.1291 | 496.0001 | 395.4935
1381.5165 | 1289.5165 | 345.5123 | 523.7086 | 523.5403 | 454.5438 | 509.7813 | 505.1838 | 496.34 | 394.8021
1382.5079 | 1290.5079 | 344.997 | 523.4982 | 523.3433 | 453.8368 | 509.4619 | 504.2488 | 496.7451 | 394.1163
1383.5094 | 1291.5094 | 344.4423 | 523.2721 | 523.0914 | 453.2741 | 509.1496 | 503.3455 | 497.1624 | 393.4319
1384.5108 | 1292.5108 | 343.8132 | 523.0817 | 522.8657 | 452.2721 | 508.8526 | 502.4788 | 497.5901 | 392.7563
1385.5123 | 1293.5123 | 343.2223 | 522.8798 | 522.659 | 451.3945 | 508.5778 | 501.4792 | 498.027 | 392.075
1386.5137 | 1294.5137 | 342.6071 | 522.6727 | 522.438 | 450.7053 | 508.2672 | 500.5473 | 498.4384 | 391.4193
1387.5151 | 1295.5151 | 342.0005 | 522.4619 | 522.2089 | 450.2101 | 508.0105 | 499.9187 | 498.8214 | 390.7481
1388.5066 | 1296.5066 | 341.3778 | 522.2785 | 521.98 | 449.5368 | 507.7163 | 498.921 | 499.2552 | 390.0882
1389.508 | 1297.508 | 340.8057 | 522.0985 | 521.7542 | 448.7285 | 507.4239 | 497.966 | 499.594 | 389.4066
1390.5095 | 1298.5095 | 340.2706 | 521.9004 | 521.5513 | 448.0174 | 507.1241 | 497.0098 | 499.9743 | 388.737
1391.5109 | 1299.5109 | 339.7667 | 521.7002 | 521.3766 | 447.2945 | 506.8491 | 495.9501 | 500.2807 | 388.0986
1392.5123 | 1300.5123 | 339.2745 | 521.4862 | 521.1579 | 446.5511 | 506.5785 | 494.9975 | 500.751 | 387.4406
1393.5138 | 1301.5138 | 338.7144 | 521.2737 | 520.9711 | 445.8932 | 506.3494 | 493.8788 | 501.164 | 386.801
1394.5052 | 1302.5052 | 338.226 | 521.0827 | 520.7345 | 445.3131 | 506.0936 | 492.8788 | 501.4837 | 386.1639
1395.5066 | 1303.5066 | 337.7356 | 520.8691 | 520.4781 | 444.6593 | 505.9224 | 491.8798 | 501.7402 | 385.5489
1396.5081 | 1304.5081 | 337.2738 | 520.6595 | 520.2446 | 443.9414 | 505.6761 | 491.0637 | 502.1165 | 384.9272
1397.5095 | 1305.5095 | 336.9371 | 520.4659 | 520.0106 | 443.2316 | 505.4306 | 490.2191 | 502.5228 | 384.2865
1398.511 | 1306.511 | 336.6011 | 520.2436 | 519.7867 | 442.7063 | 505.2012 | 489.3167 | 502.8755 | 383.6414
1399.5124 | 1307.5124 | 336.1166 | 520.0249 | 519.5488 | 442.0409 | 504.9778 | 488.2966 | 503.2624 | 383.0325
1400.5138 | 1308.5138 | 335.6004 | 519.8105 | 519.3274 | 441.2282 | 504.6944 | 487.3116 | 503.7918 | 382.4081
1401.5153 | 1309.5153 | 335.0799 | 519.5961 | 519.0901 | 440.6841 | 504.415 | 486.4202 | 504.2416 | 381.7752
1402.5167 | 1310.5167 | 334.5526 | 519.3901 | 518.8369 | 440.0019 | 504.169 | 485.4236 | 504.6328 | 381.169
1403.5081 | 1311.5081 | 334.0257 | 519.1909 | 518.613 | 438.7106 | 503.9464 | 484.4995 | 505.0601 | 380.5633
1404.5096 | 1312.5096 | 333.4849 | 519.0057 | 518.3924 | 438.1993 | 503.6352 | 483.5401 | 505.5446 | 379.9663
1405.511 | 1313.511 | 333.0266 | 518.7905 | 518.1697 | 437.1081 | 503.3729 | 482.6401 | 505.9853 | 379.342
1406.5125 | 1314.5125 | 332.6365 | 518.5842 | 517.9427 | 436.4672 | 503.1142 | 481.7526 | 506.3666 | 378.7313
1407.5139 | 1315.5139 | 332.1868 | 518.3741 | 517.7352 | 435.6733 | 502.8294 | 480.8762 | 506.7752 | 378.144
1408.5153 | 1316.5153 | 331.6793 | 518.1721 | 517.5208 | 435.0535 | 502.5198 | 479.9803 | 507.0239 | 377.5212
1409.5068 | 1317.5068 | 331.2142 | 517.9716 | 517.2996 | 434.4403 | 502.2305 | 479.1669 | 507.3765 | 376.91
1410.5082 | 1318.5082 | 330.7897 | 517.756 | 517.1034 | 433.8296 | 501.9373 | 478.3244 | 507.7547 | 376.2838
1411.5097 | 1319.5097 | 330.3264 | 517.5455 | 516.8366 | 433.3509 | 501.6638 | 477.4727 | 508.0538 | 375.6764
1412.5111 | 1320.5111 | 329.7958 | 517.344 | 516.5863 | 432.852 | 501.424 | 476.6458 | 508.2145 | 375.0688
1413.5125 | 1321.5125 | 329.3833 | 517.1216 | 516.3383 | 431.8855 | 501.1906 | 475.7502 | 508.3898 | 374.46
1414.514 | 1322.514 | 328.9977 | 516.9135 | 516.1068 | 430.9732 | 500.8896 | 474.8584 | 508.6223 | 373.8911
1415.5054 | 1323.5054 | 328.6142 | 516.7217 | 515.8889 | 430.2281 | 500.6357 | 473.9788 | 508.8717 | 373.2793
1416.5068 | 1324.5068 | 328.1307 | 516.5219 | 515.6671 | 429.6335 | 500.3635 | 473.1159 | 509.0544 | 372.7007
1417.5083 | 1325.5083 | 327.7554 | 516.3327 | 515.4272 | 428.9468 | 500.1165 | 472.2635 | 509.1467 | 372.1025
1418.5097 | 1326.5097 | 327.4163 | 516.1379 | 515.1742 | 428.5977 | 500.008 | 471.4179 | 509.2214 | 371.5057
1419.5112 | 1327.5112 | 327.1429 | 515.9536 | 514.9322 | 428.0934 | 499.7476 | 470.5748 | 509.2387 | 370.902
1420.5126 | 1328.5126 | 326.7985 | 515.7557 | 514.7011 | 427.5704 | 499.5091 | 469.7048 | 509.1889 | 370.2959
1421.514 | 1329.514 | 326.5155 | 515.56 | 514.4736 | 427.0171 | 499.2111 | 468.8711 | 509.1092 | 369.6862
1422.5055 | 1330.5055 | 326.2609 | 515.3762 | 514.2191 | 426.4969 | 498.9439 | 467.9913 | 509.0293 | 369.1159
1423.5069 | 1331.5069 | 325.9541 | 515.1842 | 514.0123 | 425.916 | 498.6463 | 467.1439 | 508.8841 | 368.5383
1424.5083 | 1332.5083 | 325.6647 | 514.9813 | 513.7829 | 425.2689 | 498.358 | 466.3271 | 508.6842 | 367.9599
1425.5098 | 1333.5098 | 325.2783 | 514.7758 | 513.5477 | 424.5778 | 498.0832 | 465.5067 | 508.5187 | 367.4051
1426.5112 | 1334.5112 | 324.8561 | 514.5738 | 513.3337 | 423.9301 | 497.8196 | 464.7218 | 508.2815 | 366.8204
1427.5127 | 1335.5127 | 324.5052 | 514.3724 | 513.0559 | 423.0267 | 497.5348 | 463.9132 | 508.0375 | 366.2406
1428.5141 | 1336.5141 | 324.0336 | 514.1437 | 512.7417 | 421.9913 | 497.2093 | 463.1125 | 507.8528 | 365.6515
1429.5155 | 1337.5155 | 323.5192 | 513.9039 | 512.4697 | 421.2942 | 496.9249 | 462.3214 | 507.5731 | 365.0851
1430.507 | 1338.507 | 323.0438 | 513.6839 | 512.1758 | 420.771 | 496.6219 | 461.5615 | 507.2966 | 364.4941
1431.5084 | 1339.5084 | 322.5987 | 513.4784 | 511.9068 | 419.9706 | 496.3076 | 460.7841 | 506.9543 | 363.9102
1432.5098 | 1340.5098 | 322.1142 | 513.255 | 511.5992 | 419.5414 | 496.0146 | 460.0498 | 506.5988 | 363.3415
1433.5113 | 1341.5113 | 321.7376 | 513.0575 | 511.3072 | 418.9489 | 495.6814 | 459.2841 | 506.1735 | 362.7782
1434.5127 | 1342.5127 | 321.3827 | 512.8544 | 511.0338 | 418.1908 | 495.3726 | 458.523 | 505.7748 | 362.1937
1435.5142 | 1343.5142 | 321.0375 | 512.6277 | 510.7388 | 417.8712 | 495.0724 | 457.7715 | 505.3616 | 361.6297
1436.5056 | 1344.5056 | 320.6967 | 512.404 | 510.4638 | 417.2299 | 494.765 | 457.0195 | 504.9209 | 361.0742
1437.517 | 1345.517 | 320.3503 | 512.1686 | 510.1841 | 416.5021 | 494.4545 | 456.2755 | 504.4615 | 360.517
1438.5085 | 1346.5085 | 319.9938 | 511.9412 | 509.8673 | 416.0101 | 494.1238 | 455.5201 | 503.9992 | 359.9463
1439.5099 | 1347.5099 | 319.6183 | 511.717 | 509.5663 | 415.4988 | 493.7711 | 454.7964 | 503.5503 | 359.3779
1440.5114 | 1348.5114 | 319.2745 | 511.4756 | 509.2853 | 414.8477 | 493.4104 | 454.0481 | 503.0251 | 358.8007
1441.5128 | 1349.5128 | 318.8562 | 511.2385 | 509.0283 | 413.9724 | 493.0982 | 453.3169 | 502.4822 | 358.2482
1442.5142 | 1350.5142 | 318.5023 | 511.0069 | 508.7162 | 413.514 | 492.7379 | 452.5903 | 501.9565 | 357.7113
1443.5057 | 1351.5057 | 318.0854 | 510.7964 | 508.4193 | 413.0582 | 492.3793 | 451.839 | 501.3314 | 357.1448
1444.5071 | 1352.5071 | 317.6523 | 510.5892 | 508.1154 | 412.377 | 492.081 | 451.08 | 500.7401 | 356.5943
1445.5085 | 1353.5085 | 317.1791 | 510.3623 | 507.7747 | 411.9491 | 491.7304 | 450.3709 | 500.0632 | 356.0448
1446.51 | 1354.51 | 316.7672 | 510.1396 | 507.469 | 411.4981 | 491.396 | 449.6306 | 499.5587 | 355.4983
1447.5114 | 1355.5114 | 316.4198 | 509.9106 | 507.1674 | 410.6252 | 491.0041 | 448.8707 | 498.8825 | 354.9407
1448.5129 | 1356.5129 | 316.0022 | 509.6745 | 506.8395 | 409.9704 | 490.5947 | 448.0941 | 498.1983 | 354.3965
1449.5143 | 1357.5143 | 315.5981 | 509.4752 | 506.5099 | 409.1901 | 490.2002 | 447.3288 | 497.5419 | 353.8566
1450.5157 | 1358.5157 | 315.1427 | 509.2556 | 506.1811 | 408.3477 | 489.8034 | 446.5633 | 496.8682 | 353.3052
1451.5072 | 1359.5072 | 314.6924 | 509.0088 | 505.8413 | 407.8796 | 489.3724 | 445.8122 | 496.1478 | 352.747
1452.5086 | 1360.5086 | 314.1674 | 508.7761 | 505.5116 | 407.2644 | 488.94 | 445.0493 | 495.3956 | 352.2089
1453.51 | 1361.51 | 313.7336 | 508.5297 | 505.1716 | 406.5325 | 488.5121 | 444.2814 | 494.6506 | 351.6452
1454.5115 | 1362.5115 | 313.3589 | 508.2755 | 504.8178 | 406.0546 | 488.0612 | 443.5103 | 493.947 | 351.0974
1455.5129 | 1363.5129 | 312.9605 | 508.0081 | 504.4324 | 405.3339 | 487.6365 | 442.746 | 493.1416 | 350.5467
1456.5144 | 1364.5144 | 312.5631 | 507.7119 | 504.0724 | 404.9369 | 487.2008 | 441.9523 | 492.3385 | 349.9744
1457.5058 | 1365.5058 | 312.1416 | 507.4577 | 503.7375 | 403.5655 | 486.7841 | 441.1576 | 491.5225 | 349.4596
1458.5072 | 1366.5072 | 311.6961 | 507.2188 | 503.3823 | 402.8014 | 486.3637 | 440.3181 | 490.772 | 348.9104
1459.5087 | 1367.5087 | 311.3193 | 506.9766 | 503.029 | 401.8918 | 485.9385 | 439.4907 | 489.953 | 348.3548
1460.5101 | 1368.5101 | 310.9 | 506.734 | 502.6401 | 401.4721 | 485.5038 | 438.6616 | 489.129 | 347.8254
1461.5116 | 1369.5116 | 310.5472 | 506.4543 | 502.2517 | 400.9438 | 485.0913 | 437.7883 | 488.3303 | 347.295
1462.513 | 1370.513 | 310.1663 | 506.1678 | 501.8597 | 400.6033 | 484.6615 | 436.893 | 487.5023 | 346.7875
1463.5144 | 1371.5144 | 309.6863 | 505.8713 | 501.4836 | 400.2998 | 484.2516 | 435.9409 | 486.6242 | 346.2502
1464.5059 | 1372.5059 | 309.2138 | 505.5739 | 501.0797 | 399.9261 | 483.8472 | 435.0287 | 485.7418 | 345.7191
1465.5073 | 1373.5073 | 308.7646 | 505.2878 | 500.7154 | 399.3017 | 483.4154 | 434.1167 | 484.8367 | 345.1934
1466.5087 | 1374.5087 | 308.3421 | 505.0071 | 500.3489 | 398.4901 | 482.996 | 433.1897 | 483.9585 | 344.6488
1467.5102 | 1375.5102 | 307.9697 | 504.7243 | 499.9523 | 397.6405 | 482.5917 | 432.2677 | 483.0754 | 344.125
1468.5116 | 1376.5116 | 307.5391 | 504.4847 | 499.703 | 397.2513 | 482.1285 | 431.3211 | 482.1749 | 343.5767
1469.5131 | 1377.5131 | 307.0744 | 504.2502 | 499.3019 | 396.4063 | 481.6961 | 430.3771 | 481.2524 | 343.0719
1470.5145 | 1378.5145 | 306.5618 | 503.9795 | 498.8853 | 395.959 | 481.2608 | 429.4308 | 480.3105 | 342.5307
1471.5159 | 1379.5159 | 306.0847 | 503.6842 | 498.4795 | 395.6915 | 480.7972 | 428.4908 | 479.375 | 342.0167
1472.5074 | 1380.5074 | 305.7372 | 503.3769 | 498.0759 | 395.2512 | 480.339 | 427.558 | 478.4337 | 341.4795
1473.5088 | 1381.5088 | 305.3575 | 503.0776 | 497.678 | 394.7808 | 479.8743 | 426.6141 | 477.4748 | 340.9578
1474.5102 | 1382.5102 | 304.9816 | 502.7935 | 497.2988 | 394.0243 | 479.4312 | 425.6682 | 476.5149 | 340.4398
1475.5117 | 1383.5117 | 304.612 | 502.5257 | 496.8983 | 393.6001 | 478.9571 | 424.7421 | 475.5468 | 339.908
1476.5131 | 1384.5131 | 304.224 | 502.215 | 496.4704 | 393.3138 | 478.4855 | 423.8164 | 474.5053 | 339.3718
1477.5146 | 1385.5146 | 303.9015 | 501.8756 | 496.0661 | 393.0437 | 477.9987 | 422.8933 | 473.4888 | 338.8563
1478.506 | 1386.506 | 303.6015 | 501.5464 | 495.6667 | 392.4928 | 477.5577 | 421.9484 | 472.4613 | 338.3293
1479.5074 | 1387.5074 | 303.1999 | 501.2212 | 495.2666 | 392.1696 | 477.1611 | 421.0158 | 471.468 | 337.799
1480.5089 | 1388.5089 | 302.8155 | 500.9166 | 494.8798 | 391.7671 | 476.7329 | 420.1111 | 470.46 | 337.3125
1481.5103 | 1389.5103 | 302.399 | 500.586 | 494.4853 | 391.4969 | 476.2371 | 419.2128 | 469.4554 | 336.8177
1482.5117 | 1390.5117 | 301.9459 | 500.2784 | 494.1037 | 390.6812 | 475.7771 | 418.332 | 468.4434 | 336.3049
1483.5132 | 1391.5132 | 301.4816 | 500.0488 | 493.6932 | 390.3903 | 475.3246 | 417.4244 | 467.4429 | 335.8077
1484.5146 | 1392.5146 | 301.0728 | 499.715 | 493.3035 | 390.0416 | 474.8594 | 416.5066 | 466.3863 | 335.3076
1485.5161 | 1393.5161 | 300.682 | 499.3712 | 492.9363 | 389.5776 | 474.3858 | 415.5873 | 465.3369 | 334.8213
1486.5075 | 1394.5075 | 300.2093 | 498.9848 | 492.5244 | 389.1962 | 473.9142 | 414.6402 | 464.2935 | 334.3392
1487.5089 | 1395.5089 | 299.6649 | 498.6163 | 492.097 | 388.9172 | 473.4156 | 413.7052 | 463.2284 | 333.8294
1488.5104 | 1396.5104 | 299.1856 | 498.2642 | 491.6886 | 388.0048 | 472.9755 | 412.7545 | 462.1668 | 333.3333
1489.5118 | 1397.5118 | 298.6854 | 497.8847 | 491.2779 | 387.6795 | 472.5193 | 411.7578 | 461.1128 | 332.836
1490.5133 | 1398.5133 | 298.1861 | 497.4995 | 490.8403 | 387.309 | 472.0723 | 410.7369 | 460.0473 | 332.3586
1491.5147 | 1399.5147 | 297.6792 | 497.1348 | 490.4231 | 386.6688 | 471.6492 | 409.7324 | 459.0051 | 331.8784
1492.5161 | 1400.5161 | 297.2634 | 496.7888 | 490.0296 | 386.0248 | 471.2083 | 408.7635 | 457.9707 | 331.4025
1493.5076 | 1401.5076 | 296.9341 | 496.4106 | 489.6025 | 385.5177 | 470.7665 | 407.825 | 456.9481 | 330.9353
1494.509 | 1402.509 | 296.5867 | 496.033 | 489.1861 | 384.9996 | 470.3557 | 406.9259 | 455.9117 | 330.4665
1495.5104 | 1403.5104 | 296.2428 | 495.6572 | 488.7781 | 384.5401 | 469.9653 | 406.0256 | 454.8323 | 330.0009
1496.5119 | 1404.5119 | 295.9181 | 495.3101 | 488.3944 | 383.8412 | 469.5619 | 405.1268 | 453.7664 | 329.5339
1497.5133 | 1405.5133 | 295.5898 | 494.9593 | 487.9632 | 383.5033 | 469.1721 | 404.2337 | 452.6742 | 329.053
1498.5148 | 1406.5148 | 295.2495 | 494.5793 | 487.5416 | 383.0609 | 468.7621 | 403.361 | 451.6097 | 328.5852
1499.5062 | 1407.5062 | 294.869 | 494.2178 | 487.1424 | 382.6591 | 468.3534 | 402.5087 | 450.5247 | 328.1237
1500.5076 | 1408.5076 | 294.4839 | 493.8465 | 486.7181 | 382.1532 | 467.9907 | 401.6195 | 449.4375 | 327.6639
1501.5091 | 1409.5091 | 294.0868 | 493.4327 | 486.2951 | 381.7021 | 467.6374 | 400.7447 | 448.3756 | 327.1922
1502.5105 | 1410.5105 | 293.7116 | 493.0324 | 485.8855 | 381.345 | 467.2644 | 399.8602 | 447.3186 | 326.6447
1503.5119 | 1411.5119 | 293.3536 | 492.6538 | 485.4594 | 381.0587 | 466.8971 | 398.9881 | 446.2663 | 326.2328
1504.5134 | 1412.5134 | 293.0218 | 492.2978 | 485.0319 | 380.5261 | 466.5277 | 398.1423 | 445.1907 | 325.7782
1505.5048 | 1413.5048 | 292.725 | 491.9202 | 484.5987 | 380.0903 | 466.1402 | 397.285 | 444.1368 | 325.3186
1506.5062 | 1414.5062 | 292.3942 | 491.5235 | 484.1811 | 379.3518 | 465.7635 | 396.432 | 443.0621 | 324.8476
1507.5077 | 1415.5077 | 291.9777 | 491.1057 | 483.7301 | 378.9631 | 465.4148 | 395.6019 | 441.9909 | 324.3774
1508.5091 | 1416.5091 | 291.5829 | 490.6846 | 483.2956 | 378.5719 | 465.0476 | 394.7898 | 440.915 | 323.9333
1509.5106 | 1417.5106 | 291.2574 | 490.2773 | 482.8522 | 378.1414 | 464.6986 | 394.0006 | 439.8613 | 323.4724
1510.512 | 1418.512 | 290.8835 | 489.8629 | 482.4071 | 377.5066 | 464.3621 | 393.2161 | 438.8046 | 323.0202
1511.5134 | 1419.5134 | 290.4874 | 489.4386 | 481.9729 | 376.9218 | 464.0398 | 392.4457 | 437.7396 | 322.5671
1512.5149 | 1420.5149 | 290.0917 | 489.0173 | 481.5266 | 376.0974 | 463.7111 | 391.6623 | 436.6874 | 322.107
1513.5163 | 1421.5163 | 289.5999 | 488.6322 | 481.0956 | 375.6936 | 463.3825 | 390.903 | 435.6563 | 321.6406
1514.5078 | 1422.5078 | 289.1235 | 488.2192 | 480.6437 | 375.4057 | 463.0579 | 390.1339 | 434.5976 | 321.1779
1515.5092 | 1423.5092 | 288.7163 | 487.7991 | 480.1868 | 375.2116 | 462.7471 | 389.368 | 433.5554 | 320.7267
1516.5106 | 1424.5106 | 288.3 | 487.394 | 479.7487 | 374.1887 | 462.3834 | 388.5733 | 432.5126 | 320.2483
1517.5121 | 1425.5121 | 287.8769 | 487.0049 | 479.3051 | 373.544 | 462.0383 | 387.8065 | 431.4783 | 319.789
1518.5135 | 1426.5135 | 287.5252 | 486.592 | 478.8593 | 372.9631 | 461.6784 | 387.0828 | 430.4523 | 319.3482
1519.515 | 1427.515 | 287.1745 | 486.1624 | 478.408 | 372.7404 | 461.3135 | 386.3837 | 429.4246 | 318.8928
1520.5064 | 1428.5064 | 286.8602 | 485.7446 | 477.9649 | 372.3054 | 460.947 | 385.7228 | 428.4157 | 318.4595
1521.5078 | 1429.5078 | 286.6039 | 485.3515 | 477.5118 | 371.9091 | 460.599 | 385.0682 | 427.4036 | 317.9692
1522.5093 | 1430.5093 | 286.3026 | 484.9709 | 477.0699 | 371.5137 | 460.1954 | 384.4018 | 426.4031 | 317.5566
1523.5107 | 1431.5107 | 285.9612 | 484.566 | 476.629 | 371.0684 | 459.8231 | 383.7354 | 425.4097 | 317.1233
1524.5121 | 1432.5121 | 285.6171 | 484.1585 | 476.1985 | 370.6958 | 459.4488 | 383.0973 | 424.4484 | 316.6741
1525.5136 | 1433.5136 | 285.2898 | 483.7341 | 475.7583 | 370.0083 | 459.0584 | 382.4591 | 423.4874 | 316.2506
1526.515 | 1434.515 | 284.9509 | 483.3232 | 475.3329 | 369.5687 | 458.6621 | 381.8069 | 422.5473 | 315.8223
1527.5064 | 1435.5064 | 284.5697 | 482.9277 | 474.8859 | 369.032 | 458.2494 | 381.1169 | 421.5955 | 315.3775
1528.5079 | 1436.5079 | 284.1965 | 482.535 | 474.4446 | 368.6395 | 457.855 | 380.4067 | 420.6632 | 314.9521
1529.5093 | 1437.5093 | 283.7569 | 482.1129 | 474.0007 | 368.532 | 457.4485 | 379.6798 | 419.7476 | 314.5292
1530.5108 | 1438.5108 | 283.3411 | 481.6955 | 473.5595 | 368.1153 | 457.0228 | 378.9589 | 418.8492 | 314.1011
1531.5122 | 1439.5122 | 282.9611 | 481.2886 | 473.1323 | 367.6106 | 456.6074 | 378.266 | 417.9438 | 313.6493
1532.5136 | 1440.5136 | 282.5709 | 480.8532 | 472.7079 | 367.12 | 456.1784 | 377.5657 | 417.0525 | 313.2203
1533.5151 | 1441.5151 | 282.2211 | 480.4018 | 472.2782 | 366.2433 | 455.7479 | 376.864 | 416.1816 | 312.7782
1534.5165 | 1442.5165 | 281.8013 | 479.9642 | 471.8694 | 365.9366 | 455.287 | 376.1517 | 415.3012 | 312.3579
1535.508 | 1443.508 | 281.4237 | 479.5369 | 471.4722 | 365.2771 | 454.8353 | 375.4693 | 414.434 | 311.9262
1536.5094 | 1444.5094 | 281.0707 | 479.1316 | 471.0377 | 364.8443 | 454.378 | 374.7883 | 413.5687 | 311.4915
1537.5108 | 1445.5108 | 280.6295 | 478.7038 | 470.6108 | 364.1563 | 453.924 | 374.113 | 412.6998 | 311.0743
1538.5123 | 1446.5123 | 280.2087 | 478.271 | 470.1742 | 363.5669 | 453.494 | 373.4395 | 411.8448 | 310.6545
1539.5137 | 1447.5137 | 279.7292 | 477.8297 | 469.7383 | 363.054 | 453.0389 | 372.7672 | 411.01 | 310.2146
1540.5051 | 1448.5051 | 279.3312 | 477.4158 | 469.2921 | 362.3041 | 452.5981 | 372.1172 | 410.1732 | 309.8085
1541.5066 | 1449.5066 | 278.8788 | 476.9754 | 468.8287 | 361.8646 | 452.1253 | 371.4435 | 409.3362 | 309.3918
1542.508 | 1450.508 | 278.3942 | 476.5421 | 468.3537 | 361.3637 | 451.6979 | 370.7664 | 408.5148 | 308.9608
1543.5095 | 1451.5095 | 277.9713 | 476.1159 | 467.8644 | 360.9939 | 451.2493 | 370.1238 | 407.7012 | 308.5471
1544.5109 | 1452.5109 | 277.6109 | 475.6822 | 467.3841 | 360.5617 | 450.7919 | 369.475 | 406.8867 | 308.1438
1545.5123 | 1453.5123 | 277.2431 | 475.2508 | 466.8869 | 359.9408 | 450.3274 | 368.8282 | 406.0854 | 307.738
1546.5138 | 1454.5138 | 276.8663 | 474.8115 | 466.3691 | 359.5681 | 449.8726 | 368.1997 | 405.294 | 307.3169
1547.5152 | 1455.5152 | 276.599 | 474.3779 | 465.8747 | 359.1953 | 449.4121 | 367.5762 | 404.5054 | 306.9153
1548.5066 | 1456.5066 | 276.3056 | 473.9356 | 465.3609 | 358.7641 | 448.9531 | 366.9451 | 403.7111 | 306.5329
1549.5081 | 1457.5081 | 275.9759 | 473.5308 | 464.849 | 357.6094 | 448.5075 | 366.331 | 402.933 | 306.1068
1550.5095 | 1458.5095 | 275.5202 | 473.1218 | 464.3307 | 356.7804 | 448.0642 | 365.7235 | 402.1613 | 305.7045
1551.511 | 1459.511 | 275.1304 | 472.6764 | 463.8039 | 356.586 | 447.5975 | 365.1044 | 401.3831 | 305.2866
1552.5124 | 1460.5124 | 274.7447 | 472.2255 | 463.277 | 356.1545 | 447.1217 | 364.4754 | 400.6073 | 304.8909
1553.5138 | 1461.5138 | 274.4174 | 471.7738 | 462.7564 | 355.889 | 446.6579 | 363.8597 | 399.8383 | 304.5061
1554.5153 | 1462.5153 | 274.1066 | 471.3185 | 462.2273 | 355.4123 | 446.1895 | 363.2309 | 399.0919 | 304.1103
1555.5067 | 1463.5067 | 273.746 | 470.8804 | 461.7019 | 354.941 | 445.7236 | 362.6187 | 398.3457 | 303.7084
1556.5081 | 1464.5081 | 273.3092 | 470.4216 | 461.1667 | 354.5997 | 445.2516 | 361.9836 | 397.6059 | 303.3012
1557.5096 | 1465.5096 | 272.9055 | 469.9731 | 460.6273 | 354.2338 | 444.7844 | 361.4047 | 396.8703 | 302.9175
1558.511 | 1466.511 | 272.5113 | 469.5111 | 460.0739 | 353.8891 | 444.3079 | 360.8172 | 396.14 | 302.499
1559.5125 | 1467.5125 | 272.189 | 469.0411 | 459.5146 | 353.4552 | 443.8397 | 360.2383 | 395.4055 | 302.1201
1560.5139 | 1468.5139 | 271.8803 | 468.5808 | 458.9695 | 352.8531 | 443.3599 | 359.659 | 394.6672 | 301.7111
1561.5153 | 1469.5153 | 271.5757 | 468.1279 | 458.4057 | 352.4924 | 442.855 | 359.0935 | 393.9399 | 301.3301
1562.5168 | 1470.5168 | 271.2226 | 467.6806 | 457.8425 | 352.0342 | 442.3754 | 358.4879 | 393.2259 | 300.9335
1563.5082 | 1471.5082 | 270.8563 | 467.2118 | 457.2511 | 351.5239 | 441.8673 | 357.8353 | 392.513 | 300.5508
1564.5097 | 1472.5097 | 270.4724 | 466.7445 | 456.6722 | 350.9132 | 441.3868 | 357.1607 | 391.8101 | 300.1554
1565.5111 | 1473.5111 | 270.1217 | 466.2691 | 456.0673 | 350.5313 | 440.885 | 356.5446 | 391.117 | 299.7721
1566.5125 | 1474.5125 | 269.7807 | 465.7938 | 455.4555 | 349.597 | 440.3706 | 355.9378 | 390.4231 | 299.3753
1567.514 | 1475.514 | 269.4895 | 465.3317 | 454.8364 | 349.0918 | 439.8694 | 355.367 | 389.7503 | 298.9887
1568.5054 | 1476.5054 | 269.1371 | 464.8492 | 454.2136 | 347.9888 | 439.3716 | 354.8098 | 389.0965 | 298.6055
1569.5068 | 1477.5068 | 268.7805 | 464.3514 | 453.5772 | 347.7513 | 438.8391 | 354.2463 | 388.4355 | 298.2122
1570.5083 | 1478.5083 | 268.4231 | 463.8768 | 452.9218 | 347.2925 | 438.3417 | 353.6489 | 387.7886 | 297.8449
1571.5097 | 1479.5097 | 268.0598 | 463.3931 | 452.2654 | 346.8673 | 437.8225 | 353.0535 | 387.1506 | 297.4705
1572.5112 | 1480.5112 | 267.6416 | 462.8735 | 451.5879 | 346.3959 | 437.3248 | 352.4845 | 386.5253 | 297.095
1573.5126 | 1481.5126 | 267.2587 | 462.3573 | 450.8931 | 345.8927 | 436.7875 | 351.889 | 385.901 | 296.716
1574.514 | 1482.514 | 266.8964 | 461.8338 | 450.1808 | 345.3794 | 436.2741 | 351.3105 | 385.2881 | 296.3335
1575.5155 | 1483.5155 | 266.6182 | 461.3144 | 449.4597 | 344.8354 | 435.7298 | 350.7382 | 384.6717 | 295.9655
1576.5069 | 1484.5069 | 266.3482 | 460.7803 | 448.7321 | 344.4012 | 435.1834 | 350.2125 | 384.0461 | 295.5864
1577.5083 | 1485.5083 | 266.0524 | 460.2489 | 447.9775 | 343.9609 | 434.6384 | 349.6229 | 383.433 | 295.2052
1578.5098 | 1486.5098 | 265.7707 | 459.7166 | 447.1966 | 343.5069 | 434.0953 | 349.0621 | 382.8106 | 294.8334
1579.5112 | 1487.5112 | 265.4762 | 459.1689 | 446.418 | 343.0221 | 433.5469 | 348.5387 | 382.1986 | 294.4678
1580.5127 | 1488.5127 | 265.1732 | 458.5975 | 445.6193 | 342.7374 | 432.9839 | 347.9952 | 381.5812 | 294.1202
1581.5141 | 1489.5141 | 264.7946 | 458.0329 | 444.8071 | 342.3121 | 432.4215 | 347.4252 | 380.9732 | 293.7582
1582.5055 | 1490.5055 | 264.423 | 457.4667 | 443.9992 | 342.0142 | 431.8609 | 346.9085 | 380.3657 | 293.3966
1583.507 | 1491.507 | 264.0849 | 456.889 | 443.151 | 341.4671 | 431.3071 | 346.3656 | 379.7776 | 293.0301
1584.5084 | 1492.5084 | 263.7718 | 456.3008 | 442.3253 | 340.8507 | 430.7413 | 345.8035 | 379.1911 | 292.685
1585.5099 | 1493.5099 | 263.5281 | 455.6769 | 441.4771 | 340.2357 | 430.1625 | 345.2253 | 378.6096 | 292.3076
1586.5113 | 1494.5113 | 263.2253 | 455.0826 | 440.6064 | 339.642 | 429.5873 | 344.687 | 378.0354 | 291.9643
1587.5127 | 1495.5127 | 262.9086 | 454.4684 | 439.7259 | 339.1725 | 429.0086 | 344.1551 | 377.4638 | 291.6173
1588.5142 | 1496.5142 | 262.6083 | 453.837 | 438.8411 | 338.6023 | 428.4092 | 343.6173 | 376.9059 | 291.2695
1589.5056 | 1497.5056 | 262.3338 | 453.2041 | 437.9379 | 338.0448 | 427.8144 | 343.0943 | 376.3339 | 290.8998
1590.507 | 1498.507 | 262.0887 | 452.5501 | 437.0515 | 337.3491 | 427.1911 | 342.565 | 375.7757 | 290.5423
1591.5085 | 1499.5085 | 261.8812 | 451.8842 | 436.1261 | 336.7082 | 426.5975 | 342.0661 | 375.2109 | 290.1681
1592.5099 | 1500.5099 | 261.6234 | 451.2072 | 435.2186 | 336.06 | 425.9884 | 341.5444 | 374.6515 | 289.7957
1593.5114 | 1501.5114 | 261.3548 | 450.5134 | 434.3023 | 335.4989 | 425.3722 | 341.0304 | 374.0957 | 289.4619
1594.5128 | 1502.5128 | 261.152 | 449.8034 | 433.3694 | 334.816 | 424.7347 | 340.5273 | 373.5337 | 289.0803

## C6-7
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 154.7241 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38910.415 | 1 | 0 | 38910.4151 | 1 | 0 | -36 | 56 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4157 | 1 | 0 | 38910.4158 | 1 | 0 | 23 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4164 | 1 | 0 | 38910.4164 | 1 | 0 | 82 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4171 | 1 | 0 | 38910.4171 | 1 | 0 | 140.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4178 | 1 | 0 | 38910.4178 | 1 | 0 | 199.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4184 | 1 | 0 | 38910.4185 | 1 | 0 | 258 | 350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4191 | 1 | 0 | 38910.4192 | 1 | 0 | 317 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4198 | 1 | 0 | 38910.4198 | 1 | 0 | 375.5 | 467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4205 | 1 | 0 | 38910.4205 | 1 | 0 | 434.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4212 | 1 | 0 | 38910.4212 | 1 | 0 | 493.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4219 | 1 | 0 | 38910.4219 | 1 | 0 | 552.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4225 | 1 | 0 | 38910.4226 | 1 | 0 | 611 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4232 | 1 | 0 | 38910.4232 | 1 | 0 | 669.5 | 761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4239 | 1 | 0 | 38910.4239 | 1 | 0 | 728.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4246 | 1 | 0 | 38910.4246 | 1 | 0 | 787.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4253 | 1 | 0 | 38910.4253 | 1 | 0 | 846 | 938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4259 | 1 | 0 | 38910.426 | 1 | 0 | 905 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4266 | 1021 | 997 | 38910.4266 | 991 | 1079 | 963.5 | 1055.5 | 62.3321 | 60.8669 | 60.5006 | 65.873 | 0.62332 | 0.60867 | 0.60501 | 0.65873 | 0.014652 | 0.053724 | 2485.3741 | 2702.5242 | 49.9453
38910.4273 | 903 | 931 | 38910.4273 | 978 | 952 | 1022.5 | 1114.5 | 55.1282 | 56.8376 | 59.707 | 58.1197 | 0.55128 | 0.56838 | 0.59707 | 0.5812 | 0.017094 | 0.015873 | 8531.2854 | 10486.9784 | 74.5182
38910.428 | 2196 | 5 | 38910.428 | 2008 | 5 | 1081.5 | 1173.5 | 134.0659 | 0.30525 | 122.5885 | 0.30525 | 1.3407 | 0.0030525 | 1.2259 | 0.0030525 | 1.3376 | 1.2228 | 15.5772 | 26.7076 | 1405.4046
38910.4287 | 2458 | 2 | 38910.4287 | 2518 | 1 | 1140 | 1232 | 150.0611 | 0.1221 | 153.7241 | 0.06105 | 1.5006 | 0.001221 | 1.5372 | 0.0006105 | 1.4994 | 1.5366 | 3.5491 | 0.65814 | 24.3163
38910.4293 | 1678 | 208 | 38910.4294 | 1651 | 216 | 1199 | 1291 | 102.442 | 12.6984 | 100.7937 | 13.1868 | 1.0244 | 0.12698 | 1.0079 | 0.13187 | 0.89744 | 0.87607 | 71.1518 | 78.0769 | 136.6725
38910.43 | 1376 | 651 | 38910.43 | 1456 | 645 | 1257.5 | 1349.5 | 84.0049 | 39.7436 | 88.8889 | 39.3773 | 0.84005 | 0.39744 | 0.88889 | 0.39377 | 0.44261 | 0.49512 | 326.662 | 175.7613 | 49.6755
38910.4307 | 1150 | 864 | 38910.4307 | 1136 | 787 | 1316.5 | 1408.5 | 70.2076 | 52.7473 | 69.3529 | 48.0464 | 0.70208 | 0.52747 | 0.69353 | 0.48046 | 0.1746 | 0.21306 | 1276.334 | 486.6655 | 49.9628
38910.4314 | 1978 | 811 | 38910.4314 | 1754 | 519 | 1375 | 1467 | 120.757 | 49.5116 | 107.0818 | 31.685 | 1.2076 | 0.49512 | 1.0708 | 0.31685 | 0.71245 | 0.75397 | 14.6111 | 30.709 | 7.3762
38910.4321 | 1114 | 946 | 38910.4321 | 1771 | 709 | 1434 | 1526 | 68.0098 | 57.7534 | 108.1197 | 43.2845 | 0.6801 | 0.57753 | 1.0812 | 0.43284 | 0.10256 | 0.64835 | 47.1901 | 33.2874 | 12.5235
38910.4327 | 959 | 971 | 38910.4328 | 964 | 932 | 1493 | 1585 | 58.547 | 59.2796 | 58.8523 | 56.8987 | 0.58547 | 0.5928 | 0.58852 | 0.56899 | 0.007326 | 0.019536 | 12831.5759 | 350074.4027 | 62.2253

## C5-7
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 152.5263 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38910.415 | 1 | 0 | 38910.415 | 1 | 0 | -38.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4157 | 1 | 0 | 38910.4157 | 1 | 0 | 20.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
| 1 | 0 | 38910.4164 | 1 | 0 | 80 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4171 | 1 | 0 | 38910.4171 | 1 | 0 | 138 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4177 | 1 | 0 | 38910.4178 | 1 | 0 | 196.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4184 | 1 | 0 | 38910.4184 | 2 | 0 | 255.5 | 347.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249738 | 124819 | 249737.9994
38910.4191 | 1 | 0 | 38910.4191 | 1 | 0 | 314.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4198 | 1 | 0 | 38910.4198 | 1 | 0 | 373 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4205 | 1 | 0 | 38910.4205 | 1 | 0 | 432 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4211 | 1 | 0 | 38910.4212 | 1 | 0 | 490.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4218 | 1 | 0 | 38910.4218 | 1 | 0 | 549.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4225 | 1 | 0 | 38910.4225 | 1 | 0 | 608 | 700 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4232 | 1 | 0 | 38910.4232 | 1 | 0 | 667 | 759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4239 | 1 | 0 | 38910.4239 | 1 | 0 | 725.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4245 | 1 | 0 | 38910.4246 | 1 | 0 | 784.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4252 | 1 | 0 | 38910.4252 | 1 | 0 | 843.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4259 | 1 | 0 | 38910.4259 | 1 | 0 | 902 | 994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38910.4266 | 760 | 736 | 38910.4266 | 848 | 825 | 961 | 1053 | 46.398 | 44.9328 | 51.7705 | 50.3663 | 0.46398 | 0.44933 | 0.5177 | 0.50366 | 0.014652 | 0.014042 | 9972.1159 | 11206.5437 | 134.9884
38910.4273 | 1108 | 1086 | 38910.4273 | 1126 | 1126 | 1019.5 | 1111.5 | 67.6435 | 66.3004 | 68.7424 | 68.7424 | 0.67643 | 0.663 | 0.68742 | 0.68742 | 0.013431 | 0 | 2269.7587 | 2766.4044 | 27.0498
38910.428 | 2482 | 6 | 38910.428 | 2390 | 6 | 1078.5 | 1170.5 | 151.5263 | 0.3663 | 145.9096 | 0.3663 | 1.5153 | 0.003663 | 1.4591 | 0.003663 | 1.5116 | 1.4554 | 0.68463 | 7.1888 | 11.6026
38910.4286 | 2320 | 2 | 38910.4286 | 2358 | 2 | 1137.5 | 1229.5 | 141.6361 | 0.1221 | 143.956 | 0.1221 | 1.4164 | 0.001221 | 1.4396 | 0.001221 | 1.4151 | 1.4383 | 7.8073 | 6.0239 | 501.0644
38910.4293 | 2057 | 247 | 38910.4293 | 1915 | 290 | 1196 | 1288 | 125.58 | 15.0794 | 116.9109 | 17.7045 | 1.2558 | 0.15079 | 1.1691 | 0.17705 | 1.105 | 0.99206 | 28.3957 | 96.6309 | 38.674
38910.43 | 1635 | 760 | 38910.43 | 1626 | 645 | 1255 | 1347 | 99.8168 | 46.398 | 99.2674 | 39.3773 | 0.99817 | 0.46398 | 0.99267 | 0.39377 | 0.53419 | 0.5989 | 1479.7887 | 93.0625 | 6.5569
38910.4307 | 1485 | 919 | 38910.4307 | 1395 | 970 | 1313.5 | 1405.5 | 90.6593 | 56.105 | 85.1648 | 59.2186 | 0.90659 | 0.56105 | 0.85165 | 0.59219 | 0.34554 | 0.25946 | 96.9116 | 191.5884 | 6.7478
38910.4314 | 1296 | 1068 | 38910.4314 | 1823 | 493 | 1372.5 | 1464.5 | 79.1209 | 65.2015 | 111.2943 | 30.0977 | 0.79121 | 0.65201 | 1.1129 | 0.30098 | 0.13919 | 0.81197 | 22.5464 | 20.921 | 2.1769
38910.432 | 2267 | 406 | 38910.432 | 1023 | 920 | 1431 | 1523 | 138.4005 | 24.7863 | 62.4542 | 56.1661 | 1.384 | 0.24786 | 0.62454 | 0.56166 | 1.1361 | 0.062882 | 1.1889 | 2.3068 | 0.96976
38910.4327 | 1109 | 1008 | 38910.4327 | 1078 | 976 | 1490 | 1582 | 67.7045 | 61.5385 | 65.812 | 59.5849 | 0.67705 | 0.61538 | 0.65812 | 0.59585 | 0.061661 | 0.062271 | 2434.9941 | 2293.978 | 36.2549

## C5-6
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 146.177 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38910.415 | 1 | 0 | 38910.415 | 1 | 0 | -41.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4157 | 1 | 0 | 38910.4157 | 1 | 0 | 17.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4164 | 1 | 0 | 38910.4164 | 1 | 0 | 76.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.417 | 1 | 0 | 38910.417 | 2 | 0 | 135 | 227 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 239338 | 119619 | 239337.9994
38910.4177 | 1 | 0 | 38910.4177 | 1 | 0 | 193.5 | 285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4184 | 1 | 0 | 38910.4184 | 1 | 0 | 252.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4191 | 1 | 0 | 38910.4191 | 1 | 0 | 311.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4198 | 1 | 0 | 38910.4198 | 1 | 0 | 370.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4204 | 1 | 0 | 38910.4205 | 1 | 0 | 429 | 521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4211 | 1 | 0 | 38910.4211 | 1 | 0 | 488 | 580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4218 | 1 | 0 | 38910.4218 | 1 | 0 | 546.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4225 | 1 | 0 | 38910.4225 | 1 | 0 | 605.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4231 | 1 | 0 | 38910.4232 | 1 | 0 | 664 | 756 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4238 | 1 | 0 | 38910.4239 | 1 | 0 | 723 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4245 | 1 | 0 | 38910.4245 | 1 | 0 | 781.5 | 873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4252 | 1 | 0 | 38910.4252 | 1 | 0 | 840.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4259 | 1 | 0 | 38910.4259 | 1 | 0 | 899.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38910.4266 | 837 | 819 | 38910.4266 | 696 | 677 | 958 | 1050 | 51.0989 | 50 | 42.4908 | 41.3309 | 0.51099 | 0.5 | 0.42491 | 0.41331 | 0.010989 | 0.0116 | 13927.9302 | 12011.7997 | 89.4119
38910.4272 | 931 | 904 | 38910.4273 | 923 | 959 | 1017 | 1109 | 56.8376 | 55.1893 | 56.3492 | 58.547 | 0.56838 | 0.55189 | 0.56349 | 0.58547 | 0.016484 | 0.021978 | 17906.244 | 4801.4761 | 60.6159
38910.4279 | 2101 | 7 | 38910.4279 | 2378 | 7 | 1075.5 | 1167.5 | 128.2662 | 0.42735 | 145.177 | 0.42735 | 1.2827 | 0.0042735 | 1.4518 | 0.0042735 | 1.2784 | 1.4475 | 26.8691 | 0.69852 | 28.3793
38910.4286 | 2154 | 2 | 38910.4286 | 2063 | 2 | 1134.5 | 1226.5 | 131.5018 | 0.1221 | 125.9463 | 0.1221 | 1.315 | 0.001221 | 1.2595 | 0.001221 | 1.3138 | 1.2582 | 11.2345 | 16.2187 | 1663.3351
38910.4293 | 2010 | 240 | 38910.4293 | 1912 | 356 | 1193.5 | 1285.5 | 122.7106 | 14.652 | 116.7277 | 21.7338 | 1.2271 | 0.14652 | 1.1673 | 0.21734 | 1.0806 | 0.94994 | 20.8124 | 312.1877 | 45.5634
38910.43 | 1705 | 589 | 38910.43 | 1308 | 647 | 1252 | 1344 | 104.0904 | 35.9585 | 79.8535 | 39.4994 | 1.0409 | 0.35958 | 0.79853 | 0.39499 | 0.68132 | 0.40354 | 44.6918 | 138.0948 | 9.8846
38910.4306 | 1237 | 837 | 38910.4306 | 1205 | 819 | 1310.5 | 1402.5 | 75.5189 | 51.0989 | 73.5653 | 50 | 0.75519 | 0.51099 | 0.73565 | 0.5 | 0.2442 | 0.23565 | 452.6506 | 579.9994 | 32.6482
38910.4313 | 1198 | 943 | 38910.4313 | 2043 | 588 | 1369.5 | 1461.5 | 73.138 | 57.5702 | 124.7253 | 35.8974 | 0.73138 | 0.5757 | 1.2473 | 0.35897 | 0.15568 | 0.88828 | 10.4564 | 8.4298 | 2.0889
38910.432 | 2119 | 429 | 38910.432 | 2110 | 590 | 1428.5 | 1520.5 | 129.3651 | 26.1905 | 128.8156 | 36.0195 | 1.2937 | 0.2619 | 1.2882 | 0.3602 | 1.0317 | 0.92796 | 101.9359 | 30.2145 | 8.3089
38910.4327 | 996 | 901 | 38910.4327 | 991 | 895 | 1487.5 | 1579.5 | 60.8059 | 55.0061 | 60.5006 | 54.6398 | 0.60806 | 0.55006 | 0.60501 | 0.5464 | 0.057998 | 0.058608 | 2468.8971 | 2348.7926 | 52.9488

## C4-7
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 149.9621 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38910.415 | 1 | 0 | 38910.415 | 1 | 0 | -44 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4156 | 1 | 0 | 38910.4156 | 1 | 0 | 14.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4163 | 1 | 0 | 38910.4163 | 1 | 0 | 73.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.417 | 1 | 0 | 38910.417 | 1 | 0 | 132.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4177 | 1 | 0 | 38910.4177 | 1 | 0 | 191 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4184 | 1 | 0 | 38910.4184 | 1 | 0 | 250 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.419 | 1 | 0 | 38910.4191 | 1 | 0 | 308.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4197 | 1 | 0 | 38910.4197 | 1 | 0 | 367.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4204 | 1 | 0 | 38910.4204 | 1 | 0 | 426 | 518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4211 | 1 | 0 | 38910.4211 | 1 | 0 | 485 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4218 | 1 | 0 | 38910.4218 | 1 | 0 | 543.5 | 635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4224 | 1 | 0 | 38910.4225 | 1 | 0 | 602.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4231 | 1 | 0 | 38910.4231 | 1 | 0 | 661.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4238 | 1 | 0 | 38910.4238 | 1 | 0 | 720 | 812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4245 | 1 | 0 | 38910.4245 | 1 | 0 | 779 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4252 | 1 | 0 | 38910.4252 | 1 | 0 | 837.5 | 929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4258 | 1 | 0 | 38910.4259 | 1 | 0 | 896.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38910.4265 | 866 | 842 | 38910.4265 | 969 | 999 | 955.5 | 1047.5 | 52.8694 | 51.4042 | 59.1575 | 60.989 | 0.52869 | 0.51404 | 0.59158 | 0.60989 | 0.014652 | 0.018315 | 14605.0003 | 6422.2276 | 87.5185
38910.4272 | 1163 | 1143 | 38910.4272 | 1165 | 1097 | 1014 | 1106 | 71.0012 | 69.7802 | 71.1233 | 66.9719 | 0.71001 | 0.6978 | 0.71123 | 0.66972 | 0.01221 | 0.041514 | 802.3178 | 809.4589 | 11.71
38910.4279 | 1725 | 560 | 38910.4279 | 1007 | 11 | 1073 | 1165 | 105.3114 | 34.188 | 61.4774 | 0.67155 | 1.0531 | 0.34188 | 0.61477 | 0.0067155 | 0.71123 | 0.60806 | 93.2011 | 147.2651 | 18.2267
38910.4286 | 2440 | 3 | 38910.4286 | 2394 | 2 | 1131.5 | 1223.5 | 148.9621 | 0.18315 | 146.1538 | 0.1221 | 1.4896 | 0.0018315 | 1.4615 | 0.001221 | 1.4878 | 1.4603 | 0.7013 | 2.9609 | 12.8257
38910.4292 | 2089 | 228 | 38910.4293 | 1776 | 361 | 1190.5 | 1282.5 | 127.5336 | 13.9194 | 108.4249 | 22.0391 | 1.2753 | 0.13919 | 1.0842 | 0.22039 | 1.1361 | 0.86386 | 17.7677 | 110.3118 | 32.0645
38910.4299 | 1385 | 494 | 38910.4299 | 1518 | 602 | 1249 | 1341 | 84.5543 | 30.1587 | 92.674 | 36.7521 | 0.84554 | 0.30159 | 0.92674 | 0.36752 | 0.54396 | 0.55922 | 184.5639 | 159.0944 | 71.7681
38910.4306 | 1239 | 947 | 38910.4306 | 1388 | 899 | 1308 | 1400 | 75.641 | 57.8144 | 84.7375 | 54.884 | 0.75641 | 0.57814 | 0.84737 | 0.54884 | 0.17827 | 0.29853 | 297.3023 | 806.1256 | 25.4003
38910.4313 | 1222 | 812 | 38910.4313 | 1029 | 819 | 1367 | 1459 | 74.6032 | 49.5726 | 62.8205 | 50 | 0.74603 | 0.49573 | 0.62821 | 0.5 | 0.25031 | 0.12821 | 264.5011 | 1432.5434 | 48.6231
38910.432 | 2260 | 827 | 38910.432 | 2095 | 604 | 1425.5 | 1517.5 | 137.9731 | 50.4884 | 127.8999 | 36.8742 | 1.3797 | 0.50488 | 1.279 | 0.36874 | 0.87485 | 0.91026 | 59.919 | 74.8242 | 32.6364
38910.4327 | 1189 | 925 | 38910.4327 | 1087 | 1054 | 1484.5 | 1576.5 | 72.5885 | 56.4713 | 66.3614 | 64.3468 | 0.72589 | 0.56471 | 0.66361 | 0.64347 | 0.16117 | 0.020147 | 229.7869 | 321.688 | 28.2365

## C4-6
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 138.9121 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38910.4149 | 1 | 0 | 38910.4149 | 1 | 0 | -47 | 45 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4156 | 1 | 0 | 38910.4156 | 1 | 0 | 12 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4163 | 1 | 0 | 38910.4163 | 1 | 0 | 70.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.417 | 1 | 0 | 38910.417 | 1 | 0 | 129.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4177 | 1 | 0 | 38910.4177 | 1 | 0 | 188.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4183 | 1 | 0 | 38910.4183 | 1 | 0 | 247 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.419 | 1 | 0 | 38910.419 | 1 | 0 | 305.5 | 397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4197 | 1 | 0 | 38910.4197 | 1 | 0 | 364.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4204 | 1 | 0 | 38910.4204 | 1 | 0 | 423.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.421 | 1 | 0 | 38910.4211 | 1 | 0 | 482 | 574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4217 | 1 | 0 | 38910.4217 | 1 | 0 | 541 | 633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4224 | 1 | 0 | 38910.4224 | 1 | 0 | 599.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4231 | 1 | 0 | 38910.4231 | 1 | 0 | 658.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4238 | 1 | 0 | 38910.4238 | 1 | 0 | 717.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4244 | 1 | 0 | 38910.4245 | 1 | 0 | 776 | 868 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4251 | 1 | 0 | 38910.4252 | 1 | 0 | 835 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4258 | 1 | 0 | 38910.4258 | 1 | 0 | 893.5 | 985.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38910.4265 | 655 | 653 | 38910.4265 | 734 | 764 | 952.5 | 1044.5 | 39.9878 | 39.8657 | 44.8107 | 46.6422 | 0.39988 | 0.39866 | 0.44811 | 0.46642 | 0.001221 | 0.018315 | 12108.1981 | 5736.8752 | 145.6059
38910.4272 | 878 | 914 | 38910.4272 | 906 | 880 | 1011.5 | 1103.5 | 53.602 | 55.7998 | 55.3114 | 53.7241 | 0.53602 | 0.558 | 0.55311 | 0.53724 | 0.021978 | 0.015873 | 4344.1612 | 23844.644 | 52.6653
38910.4278 | 1977 | 717 | 38910.4279 | 1655 | 592 | 1070 | 1162 | 120.696 | 43.7729 | 101.0379 | 36.1416 | 1.207 | 0.43773 | 1.0104 | 0.36142 | 0.76923 | 0.64896 | 1226.9708 | 58.0247 | 21.4382
38910.4285 | 2149 | 2 | 38910.4286 | 2259 | 2 | 1129 | 1221 | 131.1966 | 0.1221 | 137.9121 | 0.1221 | 1.312 | 0.001221 | 1.3791 | 0.001221 | 1.3107 | 1.3779 | 6.7401 | 0.73541 | 45.4013
38910.4292 | 1910 | 101 | 38910.4292 | 1978 | 151 | 1187.5 | 1279.5 | 116.6056 | 6.1661 | 120.757 | 9.2186 | 1.1661 | 0.061661 | 1.2076 | 0.092186 | 1.1044 | 1.1154 | 26.4281 | 23.6836 | 50.1236
38910.4299 | 1978 | 559 | 38910.4299 | 1386 | 488 | 1246.5 | 1338.5 | 120.757 | 34.127 | 84.6154 | 29.7924 | 1.2076 | 0.34127 | 0.84615 | 0.29792 | 0.8663 | 0.54823 | 1.0931 | 2.1679 | 0.99306
38910.4306 | 1377 | 927 | 38910.4306 | 1406 | 968 | 1305.5 | 1397.5 | 84.0659 | 56.5934 | 85.8364 | 59.0965 | 0.84066 | 0.56593 | 0.85836 | 0.59096 | 0.27473 | 0.2674 | 785.5616 | 276.19 | 2.2667
38910.4313 | 1284 | 1003 | 38910.4313 | 1243 | 967 | 1364 | 1456 | 78.3883 | 61.2332 | 75.8852 | 59.0354 | 0.78388 | 0.61233 | 0.75885 | 0.59035 | 0.17155 | 0.1685 | 403.7433 | 2829.1066 | 1.119
38910.4319 | 1916 | 280 | 38910.4319 | 1881 | 397 | 1422.5 | 1514.5 | 116.9719 | 17.094 | 114.8352 | 24.2369 | 1.1697 | 0.17094 | 1.1484 | 0.24237 | 0.99878 | 0.90598 | 13.3105 | 26.3164 | 5.9064
38910.4326 | 1000 | 896 | 38910.4326 | 969 | 888 | 1481.5 | 1573.5 | 61.0501 | 54.7009 | 59.1575 | 54.2125 | 0.6105 | 0.54701 | 0.59158 | 0.54212 | 0.063492 | 0.049451 | 1375.4417 | 7946.8724 | 41.8153

## C4-5
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 152.6484 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38910.4149 | 1 | 0 | 38910.4149 | 1 | 0 | -49.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4156 | 1 | 0 | 38910.4156 | 1 | 0 | 9 | 101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4163 | 1 | 0 | 38910.4163 | 1 | 0 | 68 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4169 | 1 | 0 | 38910.4169 | 1 | 0 | 126.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4176 | 1 | 0 | 38910.4176 | 1 | 0 | 185.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4183 | 2 | 0 | 38910.4183 | 1 | 0 | 244 | 336 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124919 | 249938 | 124918.9988
38910.419 | 1 | 0 | 38910.419 | 1 | 0 | 303 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4197 | 1 | 0 | 38910.4197 | 1 | 0 | 361.5 | 453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4203 | 1 | 0 | 38910.4203 | 1 | 0 | 420.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.421 | 1 | 0 | 38910.421 | 1 | 0 | 479.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4217 | 1 | 0 | 38910.4217 | 1 | 0 | 538 | 630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4224 | 1 | 0 | 38910.4224 | 1 | 0 | 597 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4231 | 1 | 0 | 38910.4231 | 1 | 0 | 655.5 | 747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4237 | 1 | 0 | 38910.4238 | 1 | 0 | 714.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4244 | 1 | 0 | 38910.4244 | 1 | 0 | 773.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4251 | 1 | 0 | 38910.4251 | 1 | 0 | 832 | 924 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4258 | 1 | 0 | 38910.4258 | 1 | 0 | 891 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38910.4265 | 102 | 105 | 38910.4265 | 637 | 696 | 949.5 | 1041.5 | 6.2271 | 6.4103 | 38.8889 | 42.4908 | 0.062271 | 0.064103 | 0.38889 | 0.42491 | 0.0018315 | 0.03602 | 726781.9536 | 3932.5842 | 2130.0084
38910.4271 | 1127 | 1126 | 38910.4272 | 961 | 935 | 1008.5 | 1100.5 | 68.8034 | 68.7424 | 58.6691 | 57.0818 | 0.68803 | 0.68742 | 0.58669 | 0.57082 | 0.0006105 | 0.015873 | 3826.507 | 3227.173 | 21.3095
38910.4278 | 1581 | 617 | 38910.4278 | 1910 | 657 | 1067.5 | 1159.5 | 96.5201 | 37.6679 | 116.6056 | 40.1099 | 0.9652 | 0.37668 | 1.1661 | 0.4011 | 0.58852 | 0.76496 | 67.3684 | 153.9789 | 29.712
38910.4285 | 2484 | 2 | 38910.4285 | 1985 | 2 | 1126 | 1218 | 151.6484 | 0.1221 | 121.1844 | 0.1221 | 1.5165 | 0.001221 | 1.2118 | 0.001221 | 1.5153 | 1.2106 | 0.66169 | 30.6638 | 168.7328
38910.4292 | 2316 | 25 | 38910.4292 | 2020 | 97 | 1185 | 1277 | 141.3919 | 1.5263 | 123.3211 | 5.9219 | 1.4139 | 0.015263 | 1.2332 | 0.059219 | 1.3987 | 1.174 | 8.1852 | 65.0977 | 251.3728
38910.4299 | 1541 | 430 | 38910.4299 | 1719 | 522 | 1243.5 | 1335.5 | 94.0781 | 26.2515 | 104.9451 | 31.8681 | 0.94078 | 0.26252 | 1.0495 | 0.31868 | 0.67827 | 0.73077 | 148.6066 | 92.3904 | 59.1211
38910.4305 | 1086 | 810 | 38910.4306 | 1294 | 872 | 1302.5 | 1394.5 | 66.3004 | 49.4505 | 78.9988 | 53.2357 | 0.663 | 0.49451 | 0.78999 | 0.53236 | 0.1685 | 0.25763 | 11287.3485 | 307.4362 | 56.3016
38910.4312 | 1847 | 390 | 38910.4312 | 1220 | 1022 | 1361.5 | 1453.5 | 112.7595 | 23.8095 | 74.4811 | 62.3932 | 1.1276 | 0.2381 | 0.74481 | 0.62393 | 0.8895 | 0.12088 | 24.4923 | 32.213 | 16.4541
38910.4319 | 1065 | 894 | 38910.4319 | 1889 | 750 | 1420 | 1512 | 65.0183 | 54.5788 | 115.3236 | 45.7875 | 0.65018 | 0.54579 | 1.1532 | 0.45788 | 0.1044 | 0.69536 | 22.6615 | 14.5059 | 7.6715
38910.4326 | 1225 | 1096 | 38910.4326 | 1233 | 1111 | 1478.5 | 1570.5 | 74.7863 | 66.9109 | 75.2747 | 67.8266 | 0.74786 | 0.66911 | 0.75275 | 0.67827 | 0.078755 | 0.074481 | 1338.935 | 3247.7267 | 15.8779

## C3-7
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 146.4212 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38910.4149 | 1 | 0 | 38910.4149 | 1 | 0 | -52.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4155 | 1 | 0 | 38910.4156 | 1 | 0 | 6.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4162 | 1 | 0 | 38910.4162 | 1 | 0 | 65 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4169 | 1 | 0 | 38910.4169 | 1 | 0 | 123.5 | 215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4176 | 1 | 0 | 38910.4176 | 1 | 0 | 182.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4183 | 1 | 0 | 38910.4183 | 1 | 0 | 241.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4189 | 1 | 0 | 38910.419 | 1 | 0 | 300.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4196 | 1 | 0 | 38910.4196 | 1 | 0 | 359 | 451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4203 | 1 | 0 | 38910.4203 | 1 | 0 | 417.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.421 | 1 | 0 | 38910.421 | 1 | 0 | 476.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4217 | 1 | 0 | 38910.4217 | 1 | 0 | 535.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4223 | 1 | 0 | 38910.4224 | 1 | 0 | 594 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.423 | 1 | 0 | 38910.423 | 1 | 0 | 653 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4237 | 1 | 0 | 38910.4237 | 1 | 0 | 711.5 | 803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4244 | 1 | 0 | 38910.4244 | 1 | 0 | 770.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4251 | 1 | 0 | 38910.4251 | 1 | 0 | 829.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4257 | 1 | 0 | 38910.4258 | 1 | 0 | 888 | 980 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38910.4264 | 941 | 917 | 38910.4264 | 942 | 916 | 947 | 1039 | 57.4481 | 55.9829 | 57.5092 | 55.9219 | 0.57448 | 0.55983 | 0.57509 | 0.55922 | 0.014652 | 0.015873 | 11542.7345 | 8062.2125 | 58.2071
38910.4271 | 1111 | 1085 | 38910.4271 | 1068 | 1154 | 1005.5 | 1097.5 | 67.8266 | 66.2393 | 65.2015 | 70.4518 | 0.67827 | 0.66239 | 0.65201 | 0.70452 | 0.015873 | 0.052503 | 784.4238 | 785.5607 | 16.5462
38910.4278 | 431 | 398 | 38910.4278 | 1359 | 574 | 1064.5 | 1156.5 | 26.3126 | 24.2979 | 82.967 | 35.0427 | 0.26313 | 0.24298 | 0.82967 | 0.35043 | 0.020147 | 0.47924 | 653.0761 | 148.37 | 235.5548
38910.4285 | 2382 | 2 | 38910.4285 | 2375 | 2 | 1123.5 | 1215.5 | 145.4212 | 0.1221 | 144.9939 | 0.1221 | 1.4542 | 0.001221 | 1.4499 | 0.001221 | 1.453 | 1.4487 | 0.74455 | 1.111 | 7.9004
38910.4291 | 2306 | 3 | 38910.4292 | 1963 | 1 | 1182 | 1274 | 140.7814 | 0.18315 | 119.8413 | 0.06105 | 1.4078 | 0.0018315 | 1.1984 | 0.0006105 | 1.406 | 1.1978 | 4.0347 | 22.4745 | 546.7188
38910.4298 | 2150 | 455 | 38910.4298 | 1533 | 449 | 1241 | 1333 | 131.2576 | 27.7778 | 93.5897 | 27.4115 | 1.3126 | 0.27778 | 0.9359 | 0.27411 | 1.0348 | 0.66178 | 1.0937 | 2.1651 | 0.96235
38910.4305 | 1398 | 945 | 38910.4305 | 1183 | 777 | 1299.5 | 1391.5 | 85.348 | 57.6923 | 72.2222 | 47.4359 | 0.85348 | 0.57692 | 0.72222 | 0.47436 | 0.27656 | 0.24786 | 288.5471 | 888.9564 | 5.2677
38910.4312 | 1317 | 1012 | 38910.4312 | 1056 | 817 | 1358.5 | 1450.5 | 80.4029 | 61.7827 | 64.4689 | 49.8779 | 0.80403 | 0.61783 | 0.64469 | 0.49878 | 0.1862 | 0.14591 | 372.8973 | 6743.9938 | 6.7556
38910.4319 | 1137 | 913 | 38910.4319 | 1028 | 856 | 1417.5 | 1509.5 | 69.4139 | 55.7387 | 62.7595 | 52.2589 | 0.69414 | 0.55739 | 0.62759 | 0.52259 | 0.13675 | 0.10501 | 631.6598 | 3756.1115 | 37.1682
38910.4325 | 1028 | 924 | 38910.4326 | 1764 | 416 | 1476 | 1568 | 62.7595 | 56.4103 | 107.6923 | 25.3968 | 0.62759 | 0.5641 | 1.0769 | 0.25397 | 0.063492 | 0.82295 | 41.1129 | 28.6138 | 10.7478

## C3-6
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 139.0952 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38910.4148 | 1 | 0 | 38910.4148 | 1 | 0 | -55.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4155 | 1 | 0 | 38910.4155 | 1 | 0 | 3.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4162 | 1 | 0 | 38910.4162 | 1 | 0 | 62 | 154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4169 | 1 | 0 | 38910.4169 | 1 | 0 | 121 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4175 | 1 | 0 | 38910.4176 | 1 | 0 | 179.5 | 271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4182 | 1 | 0 | 38910.4182 | 1 | 0 | 238.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4189 | 1 | 0 | 38910.4189 | 1 | 0 | 297.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4196 | 1 | 0 | 38910.4196 | 1 | 0 | 356.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4203 | 1 | 0 | 38910.4203 | 1 | 0 | 415 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4209 | 1 | 0 | 38910.421 | 1 | 0 | 473.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4216 | 1 | 0 | 38910.4216 | 1 | 0 | 532.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4223 | 1 | 0 | 38910.4223 | 1 | 0 | 591.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.423 | 1 | 0 | 38910.423 | 1 | 0 | 650 | 742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4237 | 1 | 0 | 38910.4237 | 1 | 0 | 709 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4244 | 1 | 0 | 38910.4244 | 1 | 0 | 767.5 | 859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.425 | 1 | 0 | 38910.425 | 1 | 0 | 826.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38910.4257 | 1 | 0 | 38910.4257 | 2 | 0 | 885.5 | 977.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 227738 | 113819 | 227737.9994
38910.4264 | 759 | 654 | 38910.4264 | 747 | 723 | 944 | 1036 | 46.337 | 39.9267 | 45.6044 | 44.1392 | 0.46337 | 0.39927 | 0.45604 | 0.44139 | 0.064103 | 0.014652 | 1277.6845 | 4699.3962 | 129.5641
38910.4271 | 876 | 907 | 38910.4271 | 1029 | 1005 | 1003 | 1095 | 53.4799 | 55.3724 | 62.8205 | 61.3553 | 0.5348 | 0.55372 | 0.62821 | 0.61355 | 0.018926 | 0.014652 | 4955.3819 | 33594.333 | 54.4553
38910.4278 | 1033 | 1004 | 38910.4278 | 1115 | 1084 | 1061.5 | 1153.5 | 63.0647 | 61.2943 | 68.0708 | 66.1783 | 0.63065 | 0.61294 | 0.68071 | 0.66178 | 0.017705 | 0.018926 | 13791.5618 | 5027.5449 | 23.573
38910.4284 | 2051 | 2 | 38910.4284 | 2052 | 2 | 1120.5 | 1212.5 | 125.2137 | 0.1221 | 125.2747 | 0.1221 | 1.2521 | 0.001221 | 1.2527 | 0.001221 | 1.2509 | 1.2515 | 11.1952 | 11.14 | 1129.5369
38910.4291 | 2068 | 1 | 38910.4291 | 2254 | 0 | 1179.5 | 1271.5 | 126.2515 | 0.06105 | 137.6068 | 0 | 1.2625 | 0.0006105 | 1.3761 | 0 | 1.2619 | 1.3761 | 10.6546 | 1.0816 | 224.0489
38910.4298 | 1555 | 448 | 38910.4298 | 2260 | 320 | 1238 | 1330 | 94.9328 | 27.3504 | 137.9731 | 19.536 | 0.94933 | 0.2735 | 1.3797 | 0.19536 | 0.67582 | 1.1844 | 15.3238 | 12.3975 | 6.78
38910.4305 | 1169 | 798 | 38910.4305 | 1330 | 879 | 1297 | 1389 | 71.3675 | 48.7179 | 81.1966 | 53.663 | 0.71368 | 0.48718 | 0.81197 | 0.53663 | 0.2265 | 0.27534 | 4356.7019 | 230.9454 | 27.2296
38910.4312 | 1852 | 402 | 38910.4312 | 1290 | 1032 | 1355.5 | 1447.5 | 113.0647 | 24.5421 | 78.7546 | 63.0037 | 1.1306 | 0.24542 | 0.78755 | 0.63004 | 0.88523 | 0.15751 | 0.49355 | 0.47328 | 0.028567
38910.4318 | 2040 | 369 | 38910.4319 | 1816 | 713 | 1414.5 | 1506.5 | 124.5421 | 22.5275 | 110.8669 | 43.5287 | 1.2454 | 0.22527 | 1.1087 | 0.43529 | 1.0201 | 0.67338 | 41.8114 | 33.519 | 8.8865
38910.4325 | 2262 | 881 | 38910.4325 | 2225 | 882 | 1473.5 | 1565.5 | 138.0952 | 53.7851 | 135.8364 | 53.8462 | 1.381 | 0.53785 | 1.3584 | 0.53846 | 0.8431 | 0.8199 | 69.9587 | 64.8946 | 38.6235

## C3-5
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 149.3516 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38910.4148 | 1 | 0 | 38910.4148 | 1 | 0 | -58 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4155 | 1 | 0 | 38910.4155 | 1 | 0 | 0.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4162 | 1 | 0 | 38910.4162 | 1 | 0 | 59.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4168 | 1 | 0 | 38910.4169 | 1 | 0 | 118.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4175 | 1 | 0 | 38910.4175 | 1 | 0 | 177 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4182 | 1 | 0 | 38910.4182 | 1 | 0 | 235.5 | 327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4189 | 1 | 0 | 38910.4189 | 1 | 0 | 294.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4196 | 1 | 0 | 38910.4196 | 1 | 0 | 353.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4202 | 1 | 0 | 38910.4203 | 1 | 0 | 412 | 504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4209 | 1 | 0 | 38910.4209 | 1 | 0 | 471 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4216 | 1 | 0 | 38910.4216 | 1 | 0 | 530 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4223 | 1 | 0 | 38910.4223 | 1 | 0 | 588.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.423 | 1 | 0 | 38910.423 | 1 | 0 | 647.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4236 | 1 | 0 | 38910.4237 | 1 | 0 | 706 | 798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4243 | 1 | 0 | 38910.4243 | 1 | 0 | 765 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.425 | 1 | 0 | 38910.425 | 1 | 0 | 823.5 | 915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4257 | 1 | 0 | 38910.4257 | 1 | 0 | 882.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38910.4264 | 4 | 2 | 38910.4264 | 8 | 6 | 941.5 | 1033.5 | 0.2442 | 0.1221 | 0.4884 | 0.3663 | 0.002442 | 0.001221 | 0.004884 | 0.003663 | 0.001221 | 0.001221 | 122219 | 122219 | 121919.2453
38910.427 | 998 | 975 | 38910.4271 | 839 | 865 | 1000 | 1092 | 60.928 | 59.5238 | 51.221 | 52.8083 | 0.60928 | 0.59524 | 0.51221 | 0.52808 | 0.014042 | 0.015873 | 12777.584 | 8358.566 | 47.9778
38910.4277 | 983 | 954 | 38910.4277 | 940 | 913 | 1059 | 1151 | 60.0122 | 58.2418 | 57.3871 | 55.7387 | 0.60012 | 0.58242 | 0.57387 | 0.55739 | 0.017705 | 0.016484 | 7437.9588 | 10229.9967 | 52.8772
38910.4284 | 2411 | 2 | 38910.4284 | 1992 | 2 | 1117.5 | 1209.5 | 147.1917 | 0.1221 | 121.6117 | 0.1221 | 1.4719 | 0.001221 | 1.2161 | 0.001221 | 1.4707 | 1.2149 | 1.4737 | 24.5044 | 328.4846
38910.4291 | 2430 | 1 | 38910.4291 | 1937 | 1 | 1176.5 | 1268.5 | 148.3516 | 0.06105 | 118.254 | 0.06105 | 1.4835 | 0.0006105 | 1.1825 | 0.0006105 | 1.4829 | 1.1819 | 0.67533 | 28.49 | 341.02
38910.4298 | 1821 | 473 | 38910.4298 | 1615 | 390 | 1235.5 | 1327.5 | 111.1722 | 28.8767 | 98.5958 | 23.8095 | 1.1117 | 0.28877 | 0.98596 | 0.2381 | 0.82295 | 0.74786 | 61.9756 | 139.5589 | 18.7677
38910.4304 | 1391 | 960 | 38910.4305 | 1268 | 846 | 1294 | 1386 | 84.9206 | 58.6081 | 77.4115 | 51.6484 | 0.84921 | 0.58608 | 0.77411 | 0.51648 | 0.26313 | 0.25763 | 419.8825 | 534.3763 | 8.3692
38910.4311 | 1314 | 790 | 38910.4311 | 1945 | 717 | 1352.5 | 1444.5 | 80.2198 | 48.2295 | 118.7424 | 43.7729 | 0.8022 | 0.4823 | 1.1874 | 0.43773 | 0.3199 | 0.74969 | 0.18698 | 0.13056 | 0.056509
38910.4318 | 1753 | 370 | 38910.4318 | 1931 | 508 | 1411.5 | 1503.5 | 107.0208 | 22.5885 | 117.8877 | 31.0134 | 1.0702 | 0.22589 | 1.1789 | 0.31013 | 0.84432 | 0.86874 | 90.9448 | 59.6215 | 32.6455
38910.4325 | 1038 | 996 | 38910.4325 | 1235 | 1111 | 1470.5 | 1562.5 | 63.37 | 60.8059 | 75.3968 | 67.8266 | 0.6337 | 0.60806 | 0.75397 | 0.67827 | 0.025641 | 0.075702 | 825.4992 | 774.4374 | 36.6687

## C3-4
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 146.6654 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38910.4148 | 1 | 0 | 38910.4148 | 1 | 0 | -61 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4154 | 1 | 0 | 38910.4155 | 1 | 0 | -2.5 | 89.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4161 | 1 | 0 | 38910.4161 | 1 | 0 | 56.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4168 | 1 | 0 | 38910.4168 | 1 | 0 | 115.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4175 | 1 | 0 | 38910.4175 | 1 | 0 | 174.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4182 | 1 | 0 | 38910.4182 | 1 | 0 | 233 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4188 | 1 | 0 | 38910.4189 | 1 | 0 | 291.5 | 383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4195 | 1 | 0 | 38910.4195 | 1 | 0 | 350.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4202 | 1 | 0 | 38910.4202 | 1 | 0 | 409.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4209 | 1 | 0 | 38910.4209 | 1 | 0 | 468 | 560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4216 | 1 | 0 | 38910.4216 | 1 | 0 | 527 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4222 | 1 | 0 | 38910.4223 | 1 | 0 | 585.5 | 677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4229 | 1 | 0 | 38910.4229 | 1 | 0 | 644.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4236 | 1 | 0 | 38910.4236 | 1 | 0 | 703.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4243 | 1 | 0 | 38910.4243 | 1 | 0 | 762 | 854 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.425 | 1 | 0 | 38910.425 | 1 | 0 | 821 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4256 | 1 | 0 | 38910.4257 | 1 | 0 | 879.5 | 971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240138 | 240138 | 240137.9994
38910.4263 | 2 | 4 | 38910.4263 | 2 | 1 | 938.5 | 1030.5 | 0.1221 | 0.2442 | 0.1221 | 0.06105 | 0.001221 | 0.002442 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 120119 | 240238 | 59884.5728
38910.427 | 958 | 930 | 38910.427 | 1056 | 1109 | 997.5 | 1089.5 | 58.486 | 56.7766 | 64.4689 | 67.7045 | 0.58486 | 0.56777 | 0.64469 | 0.67705 | 0.017094 | 0.032357 | 7879.2682 | 9618.7637 | 54.7406
38910.4277 | 961 | 999 | 38910.4277 | 917 | 892 | 1056 | 1148 | 58.6691 | 60.989 | 55.9829 | 54.4567 | 0.58669 | 0.60989 | 0.55983 | 0.54457 | 0.023199 | 0.015263 | 3971.7549 | 58446.9967 | 44.2066
38910.4284 | 2112 | 2 | 38910.4284 | 2243 | 3 | 1115 | 1207 | 128.9377 | 0.1221 | 136.9353 | 0.18315 | 1.2894 | 0.001221 | 1.3694 | 0.0018315 | 1.2882 | 1.3675 | 13.9461 | 7.1842 | 966.4538
38910.4291 | 2101 | 1 | 38910.4291 | 2386 | 1 | 1173.5 | 1265.5 | 128.2662 | 0.06105 | 145.6654 | 0.06105 | 1.2827 | 0.0006105 | 1.4567 | 0.0006105 | 1.2821 | 1.456 | 15.4175 | 0.68867 | 205.4464
38910.4297 | 1791 | 477 | 38910.4297 | 1482 | 379 | 1232.5 | 1324.5 | 109.3407 | 29.1209 | 90.4762 | 23.138 | 1.0934 | 0.29121 | 0.90476 | 0.23138 | 0.8022 | 0.67338 | 55.8975 | 216.5735 | 19.2729
38910.4304 | 1350 | 852 | 38910.4304 | 1382 | 966 | 1291.5 | 1383.5 | 82.4176 | 52.0147 | 84.3712 | 58.9744 | 0.82418 | 0.52015 | 0.84371 | 0.58974 | 0.30403 | 0.25397 | 163.1538 | 579.4999 | 20.0576
38910.4311 | 1925 | 495 | 38910.4311 | 1211 | 1006 | 1350 | 1442 | 117.5214 | 30.2198 | 73.9316 | 61.4164 | 1.1752 | 0.3022 | 0.73932 | 0.61416 | 0.87302 | 0.12515 | 4.4171 | 5.2786 | 0.17848
38910.4318 | 2081 | 387 | 38910.4318 | 1744 | 230 | 1409 | 1501 | 127.0452 | 23.6264 | 106.4713 | 14.0415 | 1.2705 | 0.23626 | 1.0647 | 0.14042 | 1.0342 | 0.9243 | 23.1555 | 126.4374 | 9.4679
38910.4325 | 985 | 876 | 38910.4325 | 1096 | 979 | 1467.5 | 1559.5 | 60.1343 | 53.4799 | 66.9109 | 59.768 | 0.60134 | 0.5348 | 0.66911 | 0.59768 | 0.066545 | 0.071429 | 2491.097 | 1681.3118 | 58.3319

## C2-7
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 150.9389 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38910.4147 | 1 | 0 | 38910.4147 | 1 | 0 | -64 | 28 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4154 | 1 | 0 | 38910.4154 | 1 | 0 | -5 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4161 | 1 | 0 | 38910.4161 | 1 | 0 | 54 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4168 | 1 | 0 | 38910.4168 | 1 | 0 | 112.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4175 | 1 | 0 | 38910.4175 | 1 | 0 | 171.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4181 | 1 | 0 | 38910.4181 | 1 | 0 | 230.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4188 | 1 | 0 | 38910.4188 | 1 | 0 | 289 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4195 | 1 | 0 | 38910.4195 | 1 | 0 | 347.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4202 | 1 | 0 | 38910.4202 | 1 | 0 | 406.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4209 | 1 | 0 | 38910.4209 | 1 | 0 | 465.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4215 | 1 | 0 | 38910.4216 | 1 | 0 | 524 | 616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4222 | 1 | 0 | 38910.4222 | 1 | 0 | 583 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4229 | 1 | 0 | 38910.4229 | 1 | 0 | 641.5 | 733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4236 | 1 | 0 | 38910.4236 | 1 | 0 | 700.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4243 | 1 | 0 | 38910.4243 | 1 | 0 | 759.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4249 | 1 | 0 | 38910.425 | 1 | 0 | 818 | 910 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4256 | 1 | 0 | 38910.4256 | 1 | 0 | 877 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38910.4263 | 1039 | 1030 | 38910.4263 | 1016 | 1074 | 935.5 | 1027.5 | 63.431 | 62.8816 | 62.0269 | 65.5678 | 0.63431 | 0.62882 | 0.62027 | 0.65568 | 0.0054945 | 0.035409 | 2104.3785 | 1742.3909 | 37.0374
38910.427 | 1008 | 980 | 38910.427 | 1063 | 1037 | 994.5 | 1086.5 | 61.5385 | 59.8291 | 64.8962 | 63.3089 | 0.61538 | 0.59829 | 0.64896 | 0.63309 | 0.017094 | 0.015873 | 7492.2038 | 11591.3011 | 49.0038
38910.4277 | 969 | 1085 | 38910.4277 | 930 | 903 | 1053.5 | 1145.5 | 59.1575 | 66.2393 | 56.7766 | 55.1282 | 0.59158 | 0.66239 | 0.56777 | 0.55128 | 0.070818 | 0.016484 | 894.9462 | 2087.1201 | 36.7973
38910.4283 | 2447 | 3 | 38910.4284 | 2151 | 3 | 1112 | 1204 | 149.3895 | 0.18315 | 131.3187 | 0.18315 | 1.4939 | 0.0018315 | 1.3132 | 0.0018315 | 1.4921 | 1.3114 | 1.0459 | 17.2677 | 109.8486
38910.429 | 2456 | 1 | 38910.429 | 2037 | 1 | 1170.5 | 1262.5 | 149.9389 | 0.06105 | 124.359 | 0.06105 | 1.4994 | 0.0006105 | 1.2436 | 0.0006105 | 1.4988 | 1.243 | 0.66839 | 23.0801 | 288.4073
38910.4297 | 1690 | 328 | 38910.4297 | 1698 | 362 | 1229.5 | 1321.5 | 103.1746 | 20.0244 | 103.663 | 22.1001 | 1.0317 | 0.20024 | 1.0366 | 0.221 | 0.8315 | 0.81563 | 79.0147 | 88.2125 | 64.9273
38910.4304 | 1270 | 846 | 38910.4304 | 1345 | 861 | 1288.5 | 1380.5 | 77.5336 | 51.6484 | 82.1123 | 52.5641 | 0.77534 | 0.51648 | 0.82112 | 0.52564 | 0.25885 | 0.29548 | 914.9202 | 289.1508 | 31.3004
38910.4311 | 1231 | 769 | 38910.4311 | 2130 | 927 | 1347.5 | 1439.5 | 75.1526 | 46.9475 | 130.0366 | 56.5934 | 0.75153 | 0.46947 | 1.3004 | 0.56593 | 0.28205 | 0.73443 | 37.5315 | 27.0245 | 13.0688
38910.4317 | 1851 | 282 | 38910.4318 | 2159 | 483 | 1406 | 1498 | 113.0037 | 17.2161 | 131.8071 | 29.4872 | 1.13 | 0.17216 | 1.3181 | 0.29487 | 0.95788 | 1.0232 | 307.0216 | 20.635 | 20.5858
38910.4324 | 2125 | 891 | 38910.4324 | 1127 | 1101 | 1464.5 | 1556.5 | 129.7314 | 54.3956 | 68.8034 | 67.2161 | 1.2973 | 0.54396 | 0.68803 | 0.67216 | 0.75336 | 0.015873 | 31.3758 | 702.4458 | 53.409

## C2-6
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 146.8486 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38910.4147 | 1 | 0 | 38910.4147 | 1 | 0 | -66.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4154 | 1 | 0 | 38910.4154 | 4 | 0 | -7.5 | 84.5 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 240438 | 60034.5 | 240437.9994
38910.4161 | 1 | 0 | 38910.4161 | 1 | 0 | 51 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4167 | 1 | 0 | 38910.4168 | 1 | 0 | 110 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4174 | 1 | 0 | 38910.4174 | 1 | 0 | 168.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4181 | 1 | 0 | 38910.4181 | 1 | 0 | 227.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4188 | 1 | 0 | 38910.4188 | 1 | 0 | 286 | 378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4195 | 1 | 0 | 38910.4195 | 1 | 0 | 345 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4201 | 1 | 0 | 38910.4202 | 1 | 0 | 403.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4208 | 1 | 0 | 38910.4208 | 1 | 0 | 462.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4215 | 1 | 0 | 38910.4215 | 1 | 0 | 521.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4222 | 1 | 0 | 38910.4222 | 1 | 0 | 580.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4229 | 1 | 0 | 38910.4229 | 1 | 0 | 639 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4235 | 1 | 0 | 38910.4236 | 1 | 0 | 697.5 | 789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4242 | 1 | 0 | 38910.4242 | 1 | 0 | 756.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4249 | 1 | 0 | 38910.4249 | 1 | 0 | 815.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4256 | 1 | 0 | 38910.4256 | 1 | 0 | 874 | 966 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240438 | 240438 | 240437.9994
38910.4263 | 1 | 0 | 38910.4263 | 2 | 0 | 933 | 1025 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 240438 | 120169 | 240437.9994
38910.4269 | 982 | 956 | 38910.427 | 1075 | 1129 | 991.5 | 1083.5 | 59.9512 | 58.3639 | 65.6288 | 68.9255 | 0.59951 | 0.58364 | 0.65629 | 0.68926 | 0.015873 | 0.032967 | 4780.4776 | 25325.5129 | 48.6968
38910.4276 | 933 | 977 | 38910.4276 | 882 | 936 | 1050.5 | 1142.5 | 56.9597 | 59.6459 | 53.8462 | 57.1429 | 0.5696 | 0.59646 | 0.53846 | 0.57143 | 0.026862 | 0.032967 | 9309.4269 | 3466.5072 | 49.2825
38910.4283 | 2380 | 3 | 38910.4283 | 2132 | 3 | 1109.5 | 1201.5 | 145.2991 | 0.18315 | 130.1587 | 0.18315 | 1.453 | 0.0018315 | 1.3016 | 0.0018315 | 1.4512 | 1.2998 | 1.0769 | 14.7739 | 96.0262
38910.429 | 2164 | 1 | 38910.429 | 2389 | 1 | 1168 | 1260 | 132.1123 | 0.06105 | 145.8486 | 0.06105 | 1.3211 | 0.0006105 | 1.4585 | 0.0006105 | 1.3205 | 1.4579 | 11.963 | 0.68834 | 164.3318
38910.4297 | 1452 | 369 | 38910.4297 | 1550 | 298 | 1227 | 1319 | 88.6447 | 22.5275 | 94.6276 | 18.1929 | 0.88645 | 0.22527 | 0.94628 | 0.18193 | 0.66117 | 0.76435 | 151.9289 | 81.013 | 70.8784
38910.4303 | 1738 | 451 | 38910.4304 | 1664 | 913 | 1285.5 | 1377.5 | 106.105 | 27.5336 | 101.5873 | 55.7387 | 1.0611 | 0.27534 | 1.0159 | 0.55739 | 0.78571 | 0.45849 | 13.4891 | 12.3205 | 5.2627
38910.431 | 1063 | 786 | 38910.431 | 1748 | 495 | 1344.5 | 1436.5 | 64.8962 | 47.9853 | 106.7155 | 30.2198 | 0.64896 | 0.47985 | 1.0672 | 0.3022 | 0.16911 | 0.76496 | 61.4606 | 41.2138 | 20.6592
38910.4317 | 1716 | 594 | 38910.4317 | 1713 | 384 | 1403 | 1495 | 104.7619 | 36.2637 | 104.5788 | 23.4432 | 1.0476 | 0.36264 | 1.0458 | 0.23443 | 0.68498 | 0.81136 | 1981.7435 | 54.6351 | 5.6733
38910.4324 | 1174 | 1119 | 38910.4324 | 1035 | 1048 | 1462 | 1554 | 71.6728 | 68.315 | 63.1868 | 63.9805 | 0.71673 | 0.68315 | 0.63187 | 0.6398 | 0.033578 | 0.0079365 | 846.2899 | 1236.4186 | 9.2914

## C2-5
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 155.0904 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38910.4147 | 1 | 0 | 38910.4147 | 1 | 0 | -69.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4153 | 1 | 0 | 38910.4154 | 1 | 0 | -10.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.416 | 1 | 0 | 38910.416 | 1 | 0 | 48.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4167 | 1 | 0 | 38910.4167 | 1 | 0 | 107 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4174 | 1 | 0 | 38910.4174 | 1 | 0 | 166 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4181 | 1 | 0 | 38910.4181 | 1 | 0 | 224.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4187 | 1 | 0 | 38910.4188 | 1 | 0 | 283.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4194 | 1 | 0 | 38910.4194 | 1 | 0 | 342 | 434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4201 | 1 | 0 | 38910.4201 | 1 | 0 | 401 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4208 | 1 | 0 | 38910.4208 | 1 | 0 | 459.5 | 551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4215 | 1 | 0 | 38910.4215 | 1 | 0 | 520 | 612 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4222 | 1 | 0 | 38910.4222 | 1 | 0 | 577.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4228 | 1 | 0 | 38910.4228 | 1 | 0 | 636 | 728 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4235 | 1 | 0 | 38910.4235 | 1 | 0 | 695 | 787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4242 | 1 | 0 | 38910.4242 | 1 | 0 | 753.5 | 845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4249 | 1 | 0 | 38910.4249 | 1 | 0 | 812.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4256 | 1 | 0 | 38910.4256 | 1 | 0 | 871.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4262 | 1 | 0 | 38910.4262 | 1 | 0 | 930 | 1022 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38910.4269 | 904 | 879 | 38910.4269 | 1017 | 992 | 989 | 1081 | 55.1893 | 53.663 | 62.0879 | 60.5617 | 0.55189 | 0.53663 | 0.62088 | 0.60562 | 0.015263 | 0.015263 | 10061.52 | 10061.52 | 85.3159
38910.4276 | 1090 | 1066 | 38910.4276 | 291 | 318 | 1047.5 | 1139.5 | 66.5446 | 65.0794 | 17.7656 | 19.4139 | 0.66545 | 0.65079 | 0.17766 | 0.19414 | 0.014652 | 0.016484 | 11599.6264 | 9272.5313 | 35.6734
38910.4283 | 2502 | 4 | 38910.4283 | 2524 | 3 | 1106.5 | 1198.5 | 152.7473 | 0.2442 | 154.0904 | 0.18315 | 1.5275 | 0.002442 | 1.5409 | 0.0018315 | 1.525 | 1.5391 | 2 | 0.69085 | 5.8971
38910.429 | 2214 | 1 | 38910.429 | 2195 | 1 | 1165.5 | 1257.5 | 135.1648 | 0.06105 | 134.0049 | 0.06105 | 1.3516 | 0.0006105 | 1.34 | 0.0006105 | 1.351 | 1.3394 | 14.7906 | 15.7907 | 4437.2938
38910.4296 | 1781 | 398 | 38910.4297 | 1733 | 404 | 1224 | 1316 | 108.7302 | 24.2979 | 105.7998 | 24.6642 | 1.0873 | 0.24298 | 1.058 | 0.24664 | 0.84432 | 0.81136 | 76.9684 | 100.4067 | 45.4916
38910.4303 | 1392 | 893 | 38910.4303 | 1949 | 839 | 1283 | 1375 | 84.9817 | 54.5177 | 118.9866 | 51.221 | 0.84982 | 0.54518 | 1.1899 | 0.51221 | 0.30464 | 0.67766 | 10.0697 | 8.1886 | 2.1645
38910.431 | 1053 | 827 | 38910.431 | 1867 | 727 | 1341.5 | 1433.5 | 64.2857 | 50.4884 | 113.9805 | 44.3834 | 0.64286 | 0.50488 | 1.1398 | 0.44383 | 0.13797 | 0.69597 | 50.6381 | 30.5023 | 18.6639
38910.4317 | 1100 | 863 | 38910.4317 | 1771 | 657 | 1400.5 | 1492.5 | 67.1551 | 52.6862 | 108.1197 | 40.1099 | 0.67155 | 0.52686 | 1.0812 | 0.4011 | 0.14469 | 0.6801 | 69.4713 | 46.9955 | 21.3896
| 1100 | 863 | 38910.4324 | 1233 | 1100 | 1460 | 1552 | 67.1551 | 52.6862 | 75.2747 | 67.1551 | 0.67155 | 0.52686 | 0.75275 | 0.67155 | 0.14469 | 0.081197 | 478.7121 | 1350.8336 | 62.2924

## C2-4
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 142.6972 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38910.4146 | 1 | 0 | 38910.4147 | 1 | 0 | -72 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4153 | 1 | 0 | 38910.4153 | 1 | 0 | -13.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.416 | 1 | 0 | 38910.416 | 1 | 0 | 45.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4167 | 1 | 0 | 38910.4167 | 1 | 0 | 104 | 196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4173 | 1 | 0 | 38910.4174 | 1 | 0 | 163 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.418 | 1 | 0 | 38910.418 | 1 | 0 | 221.5 | 313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4187 | 1 | 0 | 38910.4187 | 1 | 0 | 280.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4194 | 1 | 0 | 38910.4194 | 1 | 0 | 339.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4201 | 1 | 0 | 38910.4201 | 1 | 0 | 398.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4208 | 1 | 0 | 38910.4208 | 1 | 0 | 457 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4214 | 1 | 0 | 38910.4215 | 1 | 0 | 516 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4221 | 1 | 0 | 38910.4221 | 1 | 0 | 574.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4228 | 1 | 0 | 38910.4228 | 1 | 0 | 633.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4235 | 1 | 0 | 38910.4235 | 1 | 0 | 692 | 784 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4242 | 1 | 0 | 38910.4242 | 1 | 0 | 751 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4248 | 1 | 0 | 38910.4248 | 1 | 0 | 809.5 | 901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4255 | 1 | 0 | 38910.4255 | 1 | 0 | 868.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4262 | 1 | 0 | 38910.4262 | 1 | 0 | 927.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38910.4269 | 1054 | 870 | 38910.4269 | 1074 | 1122 | 986 | 1078 | 64.3468 | 53.1136 | 65.5678 | 68.4982 | 0.64347 | 0.53114 | 0.65568 | 0.68498 | 0.11233 | 0.029304 | 338.3587 | 445.4784 | 38.8043
38910.4276 | 1046 | 1100 | 38910.4276 | 1088 | 1063 | 1045 | 1137 | 63.8584 | 67.1551 | 66.4225 | 64.8962 | 0.63858 | 0.67155 | 0.66422 | 0.64896 | 0.032967 | 0.015263 | 1111.241 | 1768.1869 | 16.4669
38910.4282 | 2261 | 4 | 38910.4283 | 2321 | 3 | 1103.5 | 1195.5 | 138.0342 | 0.2442 | 141.6972 | 0.18315 | 1.3803 | 0.002442 | 1.417 | 0.0018315 | 1.3779 | 1.4151 | 4.4737 | 0.7277 | 13.0725
38910.4289 | 1957 | 1 | 38910.4289 | 1962 | 0 | 1162.5 | 1254.5 | 119.475 | 0.06105 | 119.7802 | 0 | 1.1947 | 0.0006105 | 1.1978 | 0 | 1.1941 | 1.1978 | 19.4989 | 19.1325 | 6092.7904
38910.4296 | 1470 | 356 | 38910.4296 | 1524 | 348 | 1221.5 | 1313.5 | 89.7436 | 21.7338 | 93.0403 | 21.2454 | 0.89744 | 0.21734 | 0.9304 | 0.21245 | 0.6801 | 0.71795 | 119.3194 | 91.9753 | 68.8208
38910.4303 | 1333 | 884 | 38910.4303 | 1390 | 863 | 1280 | 1372 | 81.3797 | 53.9683 | 84.8596 | 52.6862 | 0.8138 | 0.53968 | 0.8486 | 0.52686 | 0.27411 | 0.32173 | 465.8363 | 378.7618 | 10.7733
38910.431 | 1160 | 891 | 38910.431 | 1060 | 797 | 1338.5 | 1430.5 | 70.8181 | 54.3956 | 64.7131 | 48.6569 | 0.70818 | 0.54396 | 0.64713 | 0.48657 | 0.16422 | 0.16056 | 726.4079 | 833.3528 | 28.6978
38910.4316 | 1793 | 937 | 38910.4317 | 2036 | 358 | 1397.5 | 1489.5 | 109.4628 | 57.2039 | 124.2979 | 21.8559 | 1.0946 | 0.57204 | 1.243 | 0.21856 | 0.52259 | 1.0244 | 13.0397 | 28.2331 | 9.2255
38910.4323 | 1004 | 938 | 38910.4323 | 1179 | 1036 | 1456.5 | 1548.5 | 61.2943 | 57.265 | 71.978 | 63.2479 | 0.61294 | 0.57265 | 0.71978 | 0.63248 | 0.040293 | 0.087302 | 993.0367 | 1373.8964 | 39.2915

## C2-3
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 155.7619 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38910.4146 | 1 | 0 | 38910.4146 | 1 | 0 | -75 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4153 | 1 | 0 | 38910.4153 | 1 | 0 | -16 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.416 | 1 | 0 | 38910.416 | 1 | 0 | 42.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4166 | 2 | 0 | 38910.4167 | 1 | 0 | 101.5 | 193.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127469 | 255038 | 127468.9988
38910.4173 | 1 | 0 | 38910.4173 | 1 | 0 | 160 | 252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.418 | 2 | 0 | 38910.418 | 1 | 0 | 219 | 311 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127469 | 255038 | 127468.9988
38910.4187 | 1 | 0 | 38910.4187 | 1 | 0 | 278 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4194 | 1 | 0 | 38910.4194 | 1 | 0 | 336.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.42 | 1 | 0 | 38910.4201 | 1 | 0 | 395.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4207 | 1 | 0 | 38910.4207 | 1 | 0 | 454.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4214 | 1 | 0 | 38910.4214 | 1 | 0 | 513 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4221 | 1 | 0 | 38910.4221 | 1 | 0 | 571.5 | 663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4228 | 1 | 0 | 38910.4228 | 1 | 0 | 630.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4234 | 1 | 0 | 38910.4235 | 1 | 0 | 689.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4241 | 1 | 0 | 38910.4241 | 1 | 0 | 748 | 840 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4248 | 1 | 0 | 38910.4248 | 1 | 0 | 807 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4255 | 1 | 0 | 38910.4255 | 1 | 0 | 865.5 | 957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38910.4262 | 1 | 0 | 38910.4262 | 127 | 124 | 924.5 | 1016.5 | 0.06105 | 0 | 7.7534 | 7.5702 | 0.0006105 | 0 | 0.077534 | 0.075702 | 0.0006105 | 0.0018315 | 255038 | 84946 | 255037.9994
38910.4269 | 962 | 1081 | 38910.4269 | 1089 | 1062 | 983.5 | 1075.5 | 58.7302 | 65.9951 | 66.4835 | 64.8352 | 0.5873 | 0.65995 | 0.66484 | 0.64835 | 0.07265 | 0.016484 | 812.128 | 1409.2844 | 43.9127
38910.4275 | 294 | 285 | 38910.4275 | 1048 | 1099 | 1042 | 1134 | 17.9487 | 17.3993 | 63.9805 | 67.094 | 0.17949 | 0.17399 | 0.6398 | 0.67094 | 0.0054945 | 0.031136 | 306644.0646 | 3448.7584 | 672.5616
38910.4282 | 2173 | 3 | 38910.4282 | 2202 | 3 | 1101 | 1193 | 132.6618 | 0.18315 | 134.4322 | 0.18315 | 1.3266 | 0.0018315 | 1.3443 | 0.0018315 | 1.3248 | 1.3425 | 17.5887 | 16.0123 | 1727.0314
38910.4289 | 2023 | 1 | 38910.4289 | 2535 | 1 | 1159.5 | 1251.5 | 123.5043 | 0.06105 | 154.7619 | 0.06105 | 1.235 | 0.0006105 | 1.5476 | 0.0006105 | 1.2344 | 1.547 | 28.2932 | 0.64731 | 339.1837
38910.4296 | 1863 | 405 | 38910.4296 | 1943 | 247 | 1218.5 | 1310.5 | 113.7363 | 24.7253 | 118.6203 | 15.0794 | 1.1374 | 0.24725 | 1.1862 | 0.15079 | 0.89011 | 1.0354 | 159.2709 | 39.4817 | 19.8058
38910.4303 | 1188 | 743 | 38910.4303 | 1426 | 883 | 1277.5 | 1369.5 | 72.5275 | 45.3602 | 87.0574 | 53.9072 | 0.72527 | 0.4536 | 0.87057 | 0.53907 | 0.27167 | 0.3315 | 902.2042 | 252.8213 | 59.8312
38910.4309 | 1054 | 791 | 38910.4309 | 1125 | 802 | 1336 | 1428 | 64.3468 | 48.2906 | 68.6813 | 48.9621 | 0.64347 | 0.48291 | 0.68681 | 0.48962 | 0.16056 | 0.19719 | 1254.9222 | 550.531 | 75.5746
38910.4316 | 2232 | 420 | 38910.4316 | 1863 | 879 | 1395 | 1487 | 136.2637 | 25.641 | 113.7363 | 53.663 | 1.3626 | 0.25641 | 1.1374 | 0.53663 | 1.1062 | 0.60073 | 17.9033 | 1495.4898 | 22.4556
38910.4323 | 1102 | 963 | 38910.4323 | 1822 | 761 | 1453.5 | 1545.5 | 67.2772 | 58.7912 | 111.2332 | 46.4591 | 0.67277 | 0.58791 | 1.1123 | 0.46459 | 0.08486 | 0.64774 | 35.2369 | 24.231 | 9.8512

## C1-7
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 139.3394 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38910.4146 | 1 | 0 | 38910.4146 | 1 | 0 | -77.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4152 | 1 | 0 | 38910.4153 | 1 | 0 | -19 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4159 | 1 | 0 | 38910.4159 | 1 | 0 | 39.5 | 131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4166 | 1 | 0 | 38910.4166 | 1 | 0 | 98.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4173 | 1 | 0 | 38910.4173 | 1 | 0 | 157.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.418 | 1 | 0 | 38910.418 | 1 | 0 | 216.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4186 | 1 | 0 | 38910.4187 | 1 | 0 | 275 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4193 | 1 | 0 | 38910.4194 | 1 | 0 | 334 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.42 | 1 | 0 | 38910.42 | 1 | 0 | 392.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4207 | 1 | 0 | 38910.4207 | 1 | 0 | 451.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4214 | 1 | 0 | 38910.4214 | 1 | 0 | 510 | 602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.422 | 1 | 0 | 38910.4221 | 1 | 0 | 569 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4227 | 1 | 0 | 38910.4227 | 1 | 0 | 627.5 | 719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4234 | 1 | 0 | 38910.4234 | 1 | 0 | 686.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4241 | 1 | 0 | 38910.4241 | 1 | 0 | 745.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4248 | 1 | 0 | 38910.4248 | 1 | 0 | 804 | 896 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4255 | 1 | 0 | 38910.4255 | 1 | 0 | 863 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4261 | 1 | 0 | 38910.4261 | 1 | 0 | 921.5 | 1013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38910.4268 | 938 | 1051 | 38910.4268 | 1148 | 1130 | 980.5 | 1072.5 | 57.265 | 64.1636 | 70.0855 | 68.9866 | 0.57265 | 0.64164 | 0.70085 | 0.68987 | 0.068987 | 0.010989 | 308.7922 | 326.0257 | 21.3621
38910.4275 | 1121 | 1097 | 38910.4275 | 1041 | 1014 | 1039.5 | 1131.5 | 68.4371 | 66.9719 | 63.5531 | 61.9048 | 0.68437 | 0.66972 | 0.63553 | 0.61905 | 0.014652 | 0.016484 | 189154.5511 | 4690.8376 | 5.7462
38910.4282 | 1923 | 3 | 38910.4282 | 2192 | 4 | 1098 | 1190 | 117.3993 | 0.18315 | 133.8217 | 0.2442 | 1.174 | 0.0018315 | 1.3382 | 0.002442 | 1.1722 | 1.3358 | 19.4464 | 4.1699 | 475.5289
38910.4289 | 1949 | 1 | 38910.4289 | 2044 | 1 | 1157 | 1249 | 118.9866 | 0.06105 | 124.7863 | 0.06105 | 1.1899 | 0.0006105 | 1.2479 | 0.0006105 | 1.1893 | 1.2473 | 17.1894 | 11.7015 | 3481.8972
38910.4295 | 1769 | 340 | 38910.4295 | 1825 | 383 | 1215.5 | 1307.5 | 107.9976 | 20.757 | 111.4164 | 23.3822 | 1.08 | 0.20757 | 1.1142 | 0.23382 | 0.87241 | 0.88034 | 64.0413 | 54.1952 | 17.923
38910.4302 | 1304 | 805 | 38910.4302 | 1190 | 736 | 1274.5 | 1366.5 | 79.6093 | 49.1453 | 72.6496 | 44.9328 | 0.79609 | 0.49145 | 0.7265 | 0.44933 | 0.30464 | 0.27717 | 265.1501 | 619.1881 | 18.5431
38910.4309 | 1164 | 895 | 38910.4309 | 1374 | 1007 | 1333.5 | 1425.5 | 71.0623 | 54.6398 | 83.8828 | 61.4774 | 0.71062 | 0.5464 | 0.83883 | 0.61477 | 0.16422 | 0.22405 | 136.3072 | 162.2891 | 15.443
38910.4316 | 1985 | 610 | 38910.4316 | 1763 | 762 | 1392 | 1484 | 121.1844 | 37.2405 | 107.6313 | 46.5201 | 1.2118 | 0.37241 | 1.0763 | 0.4652 | 0.83944 | 0.61111 | 299.7627 | 47.8133 | 16.5776
38910.4323 | 2120 | 936 | 38910.4323 | 2266 | 667 | 1451 | 1543 | 129.4261 | 57.1429 | 138.3394 | 40.7204 | 1.2943 | 0.57143 | 1.3834 | 0.4072 | 0.72283 | 0.97619 | 42.0811 | 117.2746 | 44.6115

## C1-6
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 154.7241 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38910.4145 | 1 | 0 | 38910.4145 | 1 | 0 | -80.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4152 | 1 | 0 | 38910.4152 | 1 | 0 | -21.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4159 | 1 | 0 | 38910.4159 | 1 | 0 | 37 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4166 | 1 | 0 | 38910.4166 | 1 | 0 | 96 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4173 | 1 | 0 | 38910.4173 | 1 | 0 | 154.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4179 | 1 | 0 | 38910.418 | 1 | 0 | 213.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4186 | 1 | 0 | 38910.4186 | 1 | 0 | 272 | 364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4193 | 1 | 0 | 38910.4193 | 1 | 0 | 331 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.42 | 1 | 0 | 38910.42 | 1 | 0 | 389.5 | 481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4207 | 1 | 0 | 38910.4207 | 1 | 0 | 448.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4213 | 1 | 0 | 38910.4214 | 1 | 0 | 507.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.422 | 1 | 0 | 38910.422 | 1 | 0 | 566 | 658 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4227 | 1 | 0 | 38910.4227 | 1 | 0 | 625 | 717 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4234 | 1 | 0 | 38910.4234 | 1 | 0 | 683.5 | 775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4241 | 1 | 0 | 38910.4241 | 1 | 0 | 742.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4247 | 1 | 0 | 38910.4248 | 1 | 0 | 801.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4254 | 1 | 0 | 38910.4254 | 1 | 0 | 860 | 952 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4261 | 1 | 0 | 38910.4261 | 1 | 0 | 919 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38910.4268 | 689 | 671 | 38910.4268 | 1001 | 977 | 977.5 | 1069.5 | 42.0635 | 40.9646 | 61.1111 | 59.6459 | 0.42063 | 0.40965 | 0.61111 | 0.59646 | 0.010989 | 0.014652 | 18910.4292 | 8141.7519 | 172.8958
38910.4275 | 1023 | 1068 | 38910.4275 | 1204 | 1187 | 1036.5 | 1128.5 | 62.4542 | 65.2015 | 73.5043 | 72.4664 | 0.62454 | 0.65201 | 0.73504 | 0.72466 | 0.027473 | 0.010379 | 1781.2854 | 2680.2036 | 40.0217
38910.4281 | 2039 | 3 | 38910.4282 | 2332 | 3 | 1095.5 | 1187.5 | 124.4811 | 0.18315 | 142.3687 | 0.18315 | 1.2448 | 0.0018315 | 1.4237 | 0.0018315 | 1.243 | 1.4219 | 24.7485 | 8.735 | 1318.4816
38910.4288 | 2304 | 1 | 38910.4288 | 2518 | 1 | 1154 | 1246 | 140.6593 | 0.06105 | 153.7241 | 0.06105 | 1.4066 | 0.0006105 | 1.5372 | 0.0006105 | 1.406 | 1.5366 | 10.7158 | 0.6532 | 148.8579
38910.4295 | 1966 | 370 | 38910.4295 | 1775 | 336 | 1213 | 1305 | 120.0244 | 22.5885 | 108.3639 | 20.5128 | 1.2002 | 0.22589 | 1.0836 | 0.20513 | 0.97436 | 0.87851 | 45.2212 | 109.1086 | 27.9758
38910.4302 | 1669 | 740 | 38910.4302 | 1308 | 831 | 1271.5 | 1363.5 | 101.8926 | 45.177 | 79.8535 | 50.7326 | 1.0189 | 0.45177 | 0.79853 | 0.50733 | 0.56716 | 0.29121 | 56.7632 | 124.2564 | 9.3879
38910.4309 | 1217 | 859 | 38910.4309 | 1601 | 756 | 1330.5 | 1422.5 | 74.2979 | 52.442 | 97.7411 | 46.1538 | 0.74298 | 0.52442 | 0.97741 | 0.46154 | 0.21856 | 0.51587 | 148.1248 | 161.6571 | 32.9682
38910.4315 | 1773 | 404 | 38910.4316 | 1999 | 580 | 1389 | 1481 | 108.2418 | 24.6642 | 122.0391 | 35.409 | 1.0824 | 0.24664 | 1.2204 | 0.35409 | 0.83578 | 0.8663 | 108.5485 | 60.517 | 33.3507
38910.4322 | 1149 | 998 | 38910.4322 | 1921 | 616 | 1448 | 1540 | 70.1465 | 60.928 | 117.2772 | 37.6068 | 0.70147 | 0.60928 | 1.1728 | 0.37607 | 0.092186 | 0.7967 | 19.4249 | 14.296 | 4.855

## C1-5
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 138.6068 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38910.4145 | 1 | 0 | 38910.4145 | 1 | 0 | -83.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4152 | 1 | 0 | 38910.4152 | 1 | 0 | -24.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4159 | 1 | 0 | 38910.4159 | 1 | 0 | 34.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4165 | 1 | 0 | 38910.4166 | 1 | 0 | 93 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4172 | 1 | 0 | 38910.4172 | 1 | 0 | 152 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4179 | 1 | 0 | 38910.4179 | 1 | 0 | 210.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4186 | 1 | 0 | 38910.4186 | 1 | 0 | 269.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4193 | 1 | 0 | 38910.4193 | 1 | 0 | 328 | 420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4199 | 1 | 0 | 38910.42 | 1 | 0 | 387 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4206 | 1 | 0 | 38910.4206 | 1 | 0 | 445.5 | 537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4213 | 1 | 0 | 38910.4213 | 1 | 0 | 504.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.422 | 1 | 0 | 38910.422 | 1 | 0 | 563.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4227 | 1 | 0 | 38910.4227 | 1 | 0 | 622.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4233 | 1 | 0 | 38910.4234 | 1 | 0 | 681 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.424 | 1 | 0 | 38910.424 | 1 | 0 | 739.5 | 831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4247 | 1 | 0 | 38910.4247 | 2 | 0 | 798.5 | 890.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 226938 | 113419 | 226937.9994
38910.4254 | 1 | 0 | 38910.4254 | 1 | 0 | 857.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4261 | 1 | 0 | 38910.4261 | 1 | 0 | 916 | 1008 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226938 | 226938 | 226937.9994
38910.4267 | 2 | 1 | 38910.4268 | 26 | 24 | 975 | 1067 | 0.1221 | 0.06105 | 1.5873 | 1.4652 | 0.001221 | 0.0006105 | 0.015873 | 0.014652 | 0.0006105 | 0.001221 | 227039.2487 | 112815.2772 | 226537.1963
38910.4274 | 1004 | 1047 | 38910.4274 | 1058 | 1031 | 1033.5 | 1125.5 | 61.2943 | 63.9194 | 64.591 | 62.9426 | 0.61294 | 0.63919 | 0.64591 | 0.62943 | 0.026252 | 0.016484 | 1910.3645 | 4495.4982 | 20.4972
38910.4281 | 2119 | 4 | 38910.4281 | 2128 | 4 | 1092.5 | 1184.5 | 129.3651 | 0.2442 | 129.9145 | 0.2442 | 1.2937 | 0.002442 | 1.2991 | 0.002442 | 1.2912 | 1.2967 | 7.3598 | 6.8794 | 237.1573
38910.4288 | 1940 | 1 | 38910.4288 | 2173 | 1 | 1151.5 | 1243.5 | 118.4371 | 0.06105 | 132.6618 | 0.06105 | 1.1844 | 0.0006105 | 1.3266 | 0.0006105 | 1.1838 | 1.326 | 17.2364 | 4.4954 | 1417.0053
38910.4295 | 1885 | 309 | 38910.4295 | 1972 | 404 | 1210 | 1302 | 115.0794 | 18.8645 | 120.3907 | 24.6642 | 1.1508 | 0.18864 | 1.2039 | 0.24664 | 0.96215 | 0.95726 | 69.0237 | 30.3635 | 5.7573
38910.4302 | 1385 | 849 | 38910.4302 | 1292 | 775 | 1269 | 1361 | 84.5543 | 51.8315 | 78.8767 | 47.3138 | 0.84554 | 0.51832 | 0.78877 | 0.47314 | 0.32723 | 0.31563 | 243.6433 | 491.8656 | 3.5611
38910.4308 | 1228 | 964 | 38910.4308 | 1316 | 767 | 1327.5 | 1419.5 | 74.9695 | 58.8523 | 80.3419 | 46.8254 | 0.74969 | 0.58852 | 0.80342 | 0.46825 | 0.16117 | 0.33516 | 92.1231 | 111.1229 | 4.2795
38910.4315 | 2117 | 526 | 38910.4315 | 1790 | 384 | 1386.5 | 1478.5 | 129.243 | 32.1123 | 109.2796 | 23.4432 | 1.2924 | 0.32112 | 1.0928 | 0.23443 | 0.97131 | 0.85836 | 518.8463 | 33.6869 | 17.8506
38910.4322 | 1114 | 1086 | 38910.4322 | 2254 | 601 | 1445 | 1537 | 68.0098 | 66.3004 | 137.6068 | 36.6911 | 0.6801 | 0.663 | 1.3761 | 0.36691 | 0.017094 | 1.0092 | 35.312 | 33.4488 | 1.6244

## C1-4
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 142.8193 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38910.4145 | 1 | 0 | 38910.4145 | 1 | 0 | -86 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4152 | 1 | 0 | 38910.4152 | 1 | 0 | -27.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4158 | 1 | 0 | 38910.4158 | 1 | 0 | 31.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4165 | 1 | 0 | 38910.4165 | 1 | 0 | 90 | 182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4172 | 1 | 0 | 38910.4172 | 1 | 0 | 149 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4179 | 1 | 0 | 38910.4179 | 1 | 0 | 207.5 | 299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4186 | 1 | 0 | 38910.4186 | 1 | 0 | 266.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4192 | 1 | 0 | 38910.4192 | 1 | 0 | 325.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4199 | 1 | 0 | 38910.4199 | 1 | 0 | 384 | 476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4206 | 1 | 0 | 38910.4206 | 1 | 0 | 443 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4213 | 1 | 0 | 38910.4213 | 2 | 1 | 501.5 | 593.5 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.422 | 1 | 0 | 38910.422 | 1 | 0 | 560.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4226 | 1 | 0 | 38910.4227 | 1 | 0 | 619.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4233 | 1 | 0 | 38910.4233 | 1 | 0 | 678 | 770 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.424 | 1 | 0 | 38910.424 | 1 | 0 | 737 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4247 | 1 | 0 | 38910.4247 | 1 | 0 | 795.5 | 887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4254 | 1 | 0 | 38910.4254 | 1 | 0 | 854.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.426 | 1 | 0 | 38910.4261 | 1 | 0 | 913.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233838 | 233838 | 233837.9994
38910.4267 | 2 | 2 | 38910.4267 | 2 | 1 | 972 | 1064 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 273167163.22 | 233737.9144 | 116719.0641
38910.4274 | 1017 | 988 | 38910.4274 | 996 | 969 | 1031 | 1123 | 62.0879 | 60.3175 | 60.8059 | 59.1575 | 0.62088 | 0.60317 | 0.60806 | 0.59158 | 0.017705 | 0.016484 | 6668.9913 | 10772.8375 | 33.5329
38910.4281 | 1334 | 3 | 38910.4281 | 2004 | 3 | 1089.5 | 1181.5 | 81.4408 | 0.18315 | 122.3443 | 0.18315 | 0.81441 | 0.0018315 | 1.2234 | 0.0018315 | 0.81258 | 1.2216 | 76.5633 | 16.7935 | 4804.3405
38910.4288 | 2323 | 1 | 38910.4288 | 1971 | 1 | 1148.5 | 1240.5 | 141.8193 | 0.06105 | 120.3297 | 0.06105 | 1.4182 | 0.0006105 | 1.2033 | 0.0006105 | 1.4176 | 1.2027 | 0.70694 | 20.1461 | 257.8916
38910.4294 | 1788 | 300 | 38910.4295 | 1805 | 260 | 1207.5 | 1299.5 | 109.1575 | 18.315 | 110.1954 | 15.873 | 1.0916 | 0.18315 | 1.102 | 0.15873 | 0.90842 | 0.94322 | 65.3224 | 46.5904 | 26.6318
38910.4301 | 1260 | 719 | 38910.4301 | 1310 | 772 | 1266 | 1358 | 76.9231 | 43.895 | 79.9756 | 47.1306 | 0.76923 | 0.43895 | 0.79976 | 0.47131 | 0.33028 | 0.32845 | 326.9335 | 341.0052 | 38.7569
38910.4308 | 1259 | 883 | 38910.4308 | 1307 | 922 | 1325 | 1417 | 76.862 | 53.9072 | 79.7924 | 56.2882 | 0.76862 | 0.53907 | 0.79792 | 0.56288 | 0.22955 | 0.23504 | 624.7148 | 434.8463 | 18.1739
38910.4315 | 2013 | 822 | 38910.4315 | 2068 | 508 | 1383.5 | 1475.5 | 122.8938 | 50.1832 | 126.2515 | 31.0134 | 1.2289 | 0.50183 | 1.2625 | 0.31013 | 0.72711 | 0.95238 | 34.3031 | 343.1576 | 46.6888
38910.4322 | 1042 | 899 | 38910.4322 | 2169 | 650 | 1442.5 | 1534.5 | 63.6142 | 54.884 | 132.4176 | 39.6825 | 0.63614 | 0.54884 | 1.3242 | 0.39683 | 0.087302 | 0.92735 | 27.0875 | 19.3475 | 7.1837

## C1-3
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 155.5788 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38910.4144 | 1 | 0 | 38910.4145 | 1 | 0 | -89 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4151 | 1 | 0 | 38910.4151 | 1 | 0 | -30 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4158 | 1 | 0 | 38910.4158 | 1 | 0 | 28.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4165 | 1 | 0 | 38910.4165 | 1 | 0 | 87.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4172 | 1 | 0 | 38910.4172 | 1 | 0 | 146 | 238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4178 | 1 | 0 | 38910.4179 | 1 | 0 | 205 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4185 | 1 | 0 | 38910.4185 | 1 | 0 | 263.5 | 355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4192 | 1 | 0 | 38910.4192 | 1 | 0 | 322.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4199 | 1 | 0 | 38910.4199 | 1 | 0 | 381.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4206 | 1 | 0 | 38910.4206 | 1 | 0 | 440.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4212 | 1 | 0 | 38910.4213 | 1 | 0 | 499 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4219 | 1 | 0 |  | 1 | 0 | 557 | 649 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4226 | 1 | 0 | 38910.4226 | 1 | 0 | 616.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4233 | 1 | 0 | 38910.4233 | 1 | 0 | 675.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.424 | 1 | 0 | 38910.424 | 1 | 0 | 734 | 826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4246 | 1 | 0 | 38910.4247 | 1 | 0 | 793 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4253 | 1 | 0 | 38910.4253 | 1 | 0 | 851.5 | 943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.426 | 1 | 0 | 38910.426 | 1 | 0 | 910.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38910.4267 | 2 | 4 | 38910.4267 | 3 | 3 | 969.5 | 1061.5 | 0.1221 | 0.2442 | 0.18315 | 0.18315 | 0.001221 | 0.002442 | 0.0018315 | 0.0018315 | 0.001221 | 0 | 127318.7643 | 108024878.7426 | 63559.4412
38910.4274 | 931 | 963 | 38910.4274 | 1017 | 989 | 1028 | 1120 | 56.8376 | 58.7912 | 62.0879 | 60.3785 | 0.56838 | 0.58791 | 0.62088 | 0.60379 | 0.019536 | 0.017094 | 6916.5396 | 11177.1876 | 67.3497
38910.428 | 2257 | 4 | 38910.4281 | 2258 | 4 | 1087 | 1179 | 137.79 | 0.2442 | 137.851 | 0.2442 | 1.3779 | 0.002442 | 1.3785 | 0.002442 | 1.3755 | 1.3761 | 13.1112 | 13.0596 | 829.8892
38910.4287 | 2119 | 2 | 38910.4287 | 2532 | 2 | 1145.5 | 1237.5 | 129.3651 | 0.1221 | 154.5788 | 0.1221 | 1.2937 | 0.001221 | 1.5458 | 0.001221 | 1.2924 | 1.5446 | 23.7342 | 0.64959 | 137.9159
38910.4294 | 2003 | 355 | 38910.4294 | 1947 | 246 | 1204.5 | 1296.5 | 122.2833 | 21.6728 | 118.8645 | 15.0183 | 1.2228 | 0.21673 | 1.1886 | 0.15018 | 1.0061 | 1.0385 | 62.1484 | 46.0766 | 16.9158
38910.4301 | 1495 | 739 | 38910.4301 | 1885 | 712 | 1263.5 | 1355.5 | 91.2698 | 45.116 | 115.0794 | 43.4676 | 0.9127 | 0.45116 | 1.1508 | 0.43468 | 0.46154 | 0.71612 | 47.2511 | 50.1587 | 14.2104
38910.4308 | 1076 | 854 | 38910.4308 | 1143 | 797 | 1322 | 1414 | 65.6899 | 52.1368 | 69.7802 | 48.6569 | 0.6569 | 0.52137 | 0.6978 | 0.48657 | 0.13553 | 0.21123 | 8410.5701 | 417.6168 | 58.4208
38910.4314 | 1681 | 591 | 38910.4315 | 1013 | 881 | 1381 | 1473 | 102.6252 | 36.0806 | 61.8437 | 53.7851 | 1.0263 | 0.36081 | 0.61844 | 0.53785 | 0.66545 | 0.080586 | 50.8342 | 95.8963 | 22.8926
38910.4321 | 1814 | 465 | 38910.4321 | 2152 | 673 | 1439.5 | 1531.5 | 110.7448 | 28.3883 | 131.3797 | 41.0867 | 1.1074 | 0.28388 | 1.3138 | 0.41087 | 0.82357 | 0.90293 | 14.2803 | 12.2574 | 6.3255

## C1-2
Penlight Test 19 |  |  | 2006-07-12 | 9:58 |  | Vs = |  | 144.4676 |  | R = | 100
XLPO | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38910.4144 | 1 | 0 | 38910.4144 | 1 | 0 | -91.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4151 | 1 | 0 | 38910.4151 | 1 | 0 | -33 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4158 | 1 | 0 | 38910.4158 | 1 | 0 | 25.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4164 | 1 | 0 | 38910.4165 | 1 | 0 | 84.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4171 | 1 | 0 | 38910.4171 | 1 | 0 | 143.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4178 | 1 | 0 | 38910.4178 | 1 | 0 | 202.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4185 | 1 | 0 | 38910.4185 | 1 | 0 | 261 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4192 | 1 | 0 | 38910.4192 | 1 | 0 | 320 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4198 | 1 | 0 | 38910.4199 | 1 | 0 | 378.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4205 | 1 | 0 | 38910.4205 | 1 | 0 | 437.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4212 | 1 | 0 | 38910.4212 | 1 | 0 | 496 | 588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4219 | 1 | 0 | 38910.4219 | 1 | 0 | 555 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4226 | 1 | 0 | 38910.4226 | 1 | 0 | 614 | 706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4233 | 1 | 0 | 38910.4233 | 1 | 0 | 672.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4239 | 1 | 0 | 38910.4239 | 1 | 0 | 731.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4246 | 1 | 0 | 38910.4246 | 1 | 0 | 790 | 882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4253 | 1 | 0 | 38910.4253 | 1 | 0 | 849 | 941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.426 | 1 | 0 | 38910.426 | 1 | 0 | 907.5 | 999.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38910.4267 | 2 | 9 | 38910.4267 | 2 | 6 | 966.5 | 1058.5 | 0.1221 | 0.54945 | 0.1221 | 0.3663 | 0.001221 | 0.0054945 | 0.001221 | 0.003663 | 0.0042735 | 0.002442 | 33850.1597 | 59372.5974 | 26126.8839
38910.4273 | 1175 | 1168 | 38910.4273 | 1118 | 1166 | 1025.5 | 1117.5 | 71.7338 | 71.3065 | 68.254 | 71.1844 | 0.71734 | 0.71306 | 0.68254 | 0.71184 | 0.0042735 | 0.029304 | 264.989 | 263.8976 | 1.4516
38910.428 | 1959 | 4 | 38910.428 | 2070 | 4 | 1084 | 1176 | 119.5971 | 0.2442 | 126.3736 | 0.2442 | 1.196 | 0.002442 | 1.2637 | 0.002442 | 1.1935 | 1.2613 | 21.1365 | 14.4782 | 1275.4004
38910.4287 | 2350 | 2 | 38910.4287 | 2023 | 1 | 1143 | 1235 | 143.4676 | 0.1221 | 123.5043 | 0.06105 | 1.4347 | 0.001221 | 1.235 | 0.0006105 | 1.4335 | 1.2344 | 0.70088 | 18.2715 | 111.0766
38910.4294 | 1804 | 301 | 38910.4294 | 1870 | 273 | 1201.5 | 1293.5 | 110.1343 | 18.3761 | 114.1636 | 16.6667 | 1.1013 | 0.18376 | 1.1416 | 0.16667 | 0.91758 | 0.97497 | 74.2311 | 40.3814 | 24.9791
38910.4301 | 1544 | 758 | 38910.4301 | 1495 | 838 | 1260.5 | 1352.5 | 94.2613 | 46.2759 | 91.2698 | 51.16 | 0.94261 | 0.46276 | 0.9127 | 0.5116 | 0.47985 | 0.4011 | 43.5538 | 68.772 | 3.4609
38910.4307 | 1335 | 925 | 38910.4308 | 1372 | 963 | 1319.5 | 1411.5 | 81.5018 | 56.4713 | 83.7607 | 58.7912 | 0.81502 | 0.56471 | 0.83761 | 0.58791 | 0.25031 | 0.24969 | 458.9887 | 499.2096 | 9.5813
38910.4314 | 1265 | 1062 | 38910.4314 | 1247 | 1022 | 1378 | 1470 | 77.2283 | 64.8352 | 76.1294 | 62.3932 | 0.77228 | 0.64835 | 0.76129 | 0.62393 | 0.12393 | 0.13736 | 1258.9664 | 919.3442 | 3.3443
38910.4321 | 1254 | 1067 | 38910.4321 | 2171 | 958 | 1437 | 1529 | 76.5568 | 65.1404 | 132.5397 | 58.486 | 0.76557 | 0.6514 | 1.3254 | 0.58486 | 0.11416 | 0.74054 | 63.992 | 68.7805 | 1.7332

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 19 |  |  | 2006-07-12 | 9:58
38910.4144 | 1 | 0 | 1 | XLPO | 7-C | Tray
38910.4151 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38910.4158 | 1 | 0 | 1
38910.4164 | 1 | 0 | 1
38910.4171 | 1 | 0 | 1
38910.4178 | 1 | 0 | 1
38910.4185 | 1 | 0 | 1
38910.4192 | 1 | 0 | 1
38910.4198 | 1 | 0 | 1
38910.4205 | 1 | 0 | 1
38910.4212 | 1 | 0 | 1
38910.4219 | 1 | 0 | 1
38910.4226 | 1 | 0 | 1
38910.4233 | 1 | 0 | 1
38910.4239 | 1 | 0 | 1
38910.4246 | 1 | 0 | 1
38910.4253 | 1 | 0 | 1
38910.426 | 1 | 0 | 1
38910.4267 | 2 | 9 | 1
38910.4273 | 1175 | 1168 | 1
38910.428 | 1959 | 4 | 1
38910.4287 | 2350 | 2 | 1
38910.4294 | 1804 | 301 | 1
38910.4301 | 1544 | 758 | 1
38910.4307 | 1335 | 925 | 1
38910.4314 | 1265 | 1062 | 1
38910.4321 | 1254 | 1067 | 1
38910.4144 | 1 | 0 | 2
38910.4151 | 1 | 0 | 2
38910.4158 | 1 | 0 | 2
38910.4165 | 1 | 0 | 2
38910.4171 | 1 | 0 | 2
38910.4178 | 1 | 0 | 2
38910.4185 | 1 | 0 | 2
38910.4192 | 1 | 0 | 2
38910.4199 | 1 | 0 | 2
38910.4205 | 1 | 0 | 2
38910.4212 | 1 | 0 | 2
38910.4219 | 1 | 0 | 2
38910.4226 | 1 | 0 | 2
38910.4233 | 1 | 0 | 2
38910.4239 | 1 | 0 | 2
38910.4246 | 1 | 0 | 2
38910.4253 | 1 | 0 | 2
38910.426 | 1 | 0 | 2
38910.4267 | 2 | 6 | 2
38910.4273 | 1118 | 1166 | 2
38910.428 | 2070 | 4 | 2
38910.4287 | 2023 | 1 | 2
38910.4294 | 1870 | 273 | 2
38910.4301 | 1495 | 838 | 2
38910.4308 | 1372 | 963 | 2
38910.4314 | 1247 | 1022 | 2
38910.4321 | 2171 | 958 | 2
38910.4144 | 1 | 0 | 3
38910.4151 | 1 | 0 | 3
38910.4158 | 1 | 0 | 3
38910.4165 | 1 | 0 | 3
38910.4172 | 1 | 0 | 3
38910.4178 | 1 | 0 | 3
38910.4185 | 1 | 0 | 3
38910.4192 | 1 | 0 | 3
38910.4199 | 1 | 0 | 3
38910.4206 | 1 | 0 | 3
38910.4212 | 1 | 0 | 3
38910.4219 | 1 | 0 | 3
38910.4226 | 1 | 0 | 3
38910.4233 | 1 | 0 | 3
38910.424 | 1 | 0 | 3
38910.4246 | 1 | 0 | 3
38910.4253 | 1 | 0 | 3
38910.426 | 1 | 0 | 3
38910.4267 | 2 | 4 | 3
38910.4274 | 931 | 963 | 3
38910.428 | 2257 | 4 | 3
38910.4287 | 2119 | 2 | 3
38910.4294 | 2003 | 355 | 3
38910.4301 | 1495 | 739 | 3
38910.4308 | 1076 | 854 | 3
38910.4314 | 1681 | 591 | 3
38910.4321 | 1814 | 465 | 3
38910.4145 | 1 | 0 | 4
38910.4151 | 1 | 0 | 4
38910.4158 | 1 | 0 | 4
38910.4165 | 1 | 0 | 4
38910.4172 | 1 | 0 | 4
38910.4179 | 1 | 0 | 4
38910.4185 | 1 | 0 | 4
38910.4192 | 1 | 0 | 4
38910.4199 | 1 | 0 | 4
38910.4206 | 1 | 0 | 4
38910.4213 | 1 | 0 | 4
38910.4226 | 1 | 0 | 4
38910.4233 | 1 | 0 | 4
38910.424 | 1 | 0 | 4
38910.4247 | 1 | 0 | 4
38910.4253 | 1 | 0 | 4
38910.426 | 1 | 0 | 4
38910.4267 | 3 | 3 | 4
38910.4274 | 1017 | 989 | 4
38910.4281 | 2258 | 4 | 4
38910.4287 | 2532 | 2 | 4
38910.4294 | 1947 | 246 | 4
38910.4301 | 1885 | 712 | 4
38910.4308 | 1143 | 797 | 4
38910.4315 | 1013 | 881 | 4
38910.4321 | 2152 | 673 | 4
38910.4145 | 1 | 0 | 5
38910.4152 | 1 | 0 | 5
38910.4158 | 1 | 0 | 5
38910.4165 | 1 | 0 | 5
38910.4172 | 1 | 0 | 5
38910.4179 | 1 | 0 | 5
38910.4186 | 1 | 0 | 5
38910.4192 | 1 | 0 | 5
38910.4199 | 1 | 0 | 5
38910.4206 | 1 | 0 | 5
38910.4213 | 1 | 0 | 5
38910.422 | 1 | 0 | 5
38910.4226 | 1 | 0 | 5
38910.4233 | 1 | 0 | 5
38910.424 | 1 | 0 | 5
38910.4247 | 1 | 0 | 5
38910.4254 | 1 | 0 | 5
38910.426 | 1 | 0 | 5
38910.4267 | 2 | 2 | 5
38910.4274 | 1017 | 988 | 5
38910.4281 | 1334 | 3 | 5
38910.4288 | 2323 | 1 | 5
38910.4294 | 1788 | 300 | 5
38910.4301 | 1260 | 719 | 5
38910.4308 | 1259 | 883 | 5
38910.4315 | 2013 | 822 | 5
38910.4322 | 1042 | 899 | 5
38910.4145 | 1 | 0 | 6
38910.4152 | 1 | 0 | 6
38910.4158 | 1 | 0 | 6
38910.4165 | 1 | 0 | 6
38910.4172 | 1 | 0 | 6
38910.4179 | 1 | 0 | 6
38910.4186 | 1 | 0 | 6
38910.4192 | 1 | 0 | 6
38910.4199 | 1 | 0 | 6
38910.4206 | 1 | 0 | 6
38910.4213 | 2 | 1 | 6
38910.422 | 1 | 0 | 6
38910.4227 | 1 | 0 | 6
38910.4233 | 1 | 0 | 6
38910.424 | 1 | 0 | 6
38910.4247 | 1 | 0 | 6
38910.4254 | 1 | 0 | 6
38910.4261 | 1 | 0 | 6
38910.4267 | 2 | 2 | 6
38910.4274 | 996 | 969 | 6
38910.4281 | 2004 | 3 | 6
38910.4288 | 1971 | 1 | 6
38910.4295 | 1805 | 260 | 6
38910.4301 | 1310 | 772 | 6
38910.4308 | 1307 | 922 | 6
38910.4315 | 2068 | 508 | 6
38910.4322 | 2169 | 650 | 6
38910.4145 | 1 | 0 | 7
38910.4152 | 1 | 0 | 7
38910.4159 | 1 | 0 | 7
38910.4165 | 1 | 0 | 7
38910.4172 | 1 | 0 | 7
38910.4179 | 1 | 0 | 7
38910.4186 | 1 | 0 | 7
38910.4193 | 1 | 0 | 7
38910.4199 | 1 | 0 | 7
38910.4206 | 1 | 0 | 7
38910.4213 | 1 | 0 | 7
38910.422 | 1 | 0 | 7
38910.4227 | 1 | 0 | 7
38910.4233 | 1 | 0 | 7
38910.424 | 1 | 0 | 7
38910.4247 | 1 | 0 | 7
38910.4254 | 1 | 0 | 7
38910.4261 | 1 | 0 | 7
38910.4267 | 2 | 1 | 7
38910.4274 | 1004 | 1047 | 7
38910.4281 | 2119 | 4 | 7
38910.4288 | 1940 | 1 | 7
38910.4295 | 1885 | 309 | 7
38910.4302 | 1385 | 849 | 7
38910.4308 | 1228 | 964 | 7
38910.4315 | 2117 | 526 | 7
38910.4322 | 1114 | 1086 | 7
38910.4145 | 1 | 0 | 8
38910.4152 | 1 | 0 | 8
38910.4159 | 1 | 0 | 8
38910.4166 | 1 | 0 | 8
38910.4172 | 1 | 0 | 8
38910.4179 | 1 | 0 | 8
38910.4186 | 1 | 0 | 8
38910.4193 | 1 | 0 | 8
38910.42 | 1 | 0 | 8
38910.4206 | 1 | 0 | 8
38910.4213 | 1 | 0 | 8
38910.422 | 1 | 0 | 8
38910.4227 | 1 | 0 | 8
38910.4234 | 1 | 0 | 8
38910.424 | 1 | 0 | 8
38910.4247 | 2 | 0 | 8
38910.4254 | 1 | 0 | 8
38910.4261 | 1 | 0 | 8
38910.4268 | 26 | 24 | 8
38910.4274 | 1058 | 1031 | 8
38910.4281 | 2128 | 4 | 8
38910.4288 | 2173 | 1 | 8
38910.4295 | 1972 | 404 | 8
38910.4302 | 1292 | 775 | 8
38910.4308 | 1316 | 767 | 8
38910.4315 | 1790 | 384 | 8
38910.4322 | 2254 | 601 | 8
38910.4145 | 1 | 0 | 9
38910.4152 | 1 | 0 | 9
38910.4159 | 1 | 0 | 9
38910.4166 | 1 | 0 | 9
38910.4173 | 1 | 0 | 9
38910.4179 | 1 | 0 | 9
38910.4186 | 1 | 0 | 9
38910.4193 | 1 | 0 | 9
38910.42 | 1 | 0 | 9
38910.4207 | 1 | 0 | 9
38910.4213 | 1 | 0 | 9
38910.422 | 1 | 0 | 9
38910.4227 | 1 | 0 | 9
38910.4234 | 1 | 0 | 9
38910.4241 | 1 | 0 | 9
38910.4247 | 1 | 0 | 9
38910.4254 | 1 | 0 | 9
38910.4261 | 1 | 0 | 9
38910.4268 | 689 | 671 | 9
38910.4275 | 1023 | 1068 | 9
38910.4281 | 2039 | 3 | 9
38910.4288 | 2304 | 1 | 9
38910.4295 | 1966 | 370 | 9
38910.4302 | 1669 | 740 | 9
38910.4309 | 1217 | 859 | 9
38910.4315 | 1773 | 404 | 9
38910.4322 | 1149 | 998 | 9
38910.4145 | 1 | 0 | 10
38910.4152 | 1 | 0 | 10
38910.4159 | 1 | 0 | 10
38910.4166 | 1 | 0 | 10
38910.4173 | 1 | 0 | 10
38910.418 | 1 | 0 | 10
38910.4186 | 1 | 0 | 10
38910.4193 | 1 | 0 | 10
38910.42 | 1 | 0 | 10
38910.4207 | 1 | 0 | 10
38910.4214 | 1 | 0 | 10
38910.422 | 1 | 0 | 10
38910.4227 | 1 | 0 | 10
38910.4234 | 1 | 0 | 10
38910.4241 | 1 | 0 | 10
38910.4248 | 1 | 0 | 10
38910.4254 | 1 | 0 | 10
38910.4261 | 1 | 0 | 10
38910.4268 | 1001 | 977 | 10
38910.4275 | 1204 | 1187 | 10
38910.4282 | 2332 | 3 | 10
38910.4288 | 2518 | 1 | 10
38910.4295 | 1775 | 336 | 10
38910.4302 | 1308 | 831 | 10
38910.4309 | 1601 | 756 | 10
38910.4316 | 1999 | 580 | 10
38910.4322 | 1921 | 616 | 10
38910.4146 | 1 | 0 | 11
38910.4152 | 1 | 0 | 11
38910.4159 | 1 | 0 | 11
38910.4166 | 1 | 0 | 11
38910.4173 | 1 | 0 | 11
38910.418 | 1 | 0 | 11
38910.4186 | 1 | 0 | 11
38910.4193 | 1 | 0 | 11
38910.42 | 1 | 0 | 11
38910.4207 | 1 | 0 | 11
38910.4214 | 1 | 0 | 11
38910.422 | 1 | 0 | 11
38910.4227 | 1 | 0 | 11
38910.4234 | 1 | 0 | 11
38910.4241 | 1 | 0 | 11
38910.4248 | 1 | 0 | 11
38910.4255 | 1 | 0 | 11
38910.4261 | 1 | 0 | 11
38910.4268 | 938 | 1051 | 11
38910.4275 | 1121 | 1097 | 11
38910.4282 | 1923 | 3 | 11
38910.4289 | 1949 | 1 | 11
38910.4295 | 1769 | 340 | 11
38910.4302 | 1304 | 805 | 11
38910.4309 | 1164 | 895 | 11
38910.4316 | 1985 | 610 | 11
38910.4323 | 2120 | 936 | 11
38910.4146 | 1 | 0 | 12
38910.4153 | 1 | 0 | 12
38910.4159 | 1 | 0 | 12
38910.4166 | 1 | 0 | 12
38910.4173 | 1 | 0 | 12
38910.418 | 1 | 0 | 12
38910.4187 | 1 | 0 | 12
38910.4194 | 1 | 0 | 12
38910.42 | 1 | 0 | 12
38910.4207 | 1 | 0 | 12
38910.4214 | 1 | 0 | 12
38910.4221 | 1 | 0 | 12
38910.4227 | 1 | 0 | 12
38910.4234 | 1 | 0 | 12
38910.4241 | 1 | 0 | 12
38910.4248 | 1 | 0 | 12
38910.4255 | 1 | 0 | 12
38910.4261 | 1 | 0 | 12
38910.4268 | 1148 | 1130 | 12
38910.4275 | 1041 | 1014 | 12
38910.4282 | 2192 | 4 | 12
38910.4289 | 2044 | 1 | 12
38910.4295 | 1825 | 383 | 12
38910.4302 | 1190 | 736 | 12
38910.4309 | 1374 | 1007 | 12
38910.4316 | 1763 | 762 | 12
38910.4323 | 2266 | 667 | 12
38910.4146 | 1 | 0 | 13
38910.4153 | 1 | 0 | 13
38910.416 | 1 | 0 | 13
38910.4166 | 2 | 0 | 13
38910.4173 | 1 | 0 | 13
38910.418 | 2 | 0 | 13
38910.4187 | 1 | 0 | 13
38910.4194 | 1 | 0 | 13
38910.42 | 1 | 0 | 13
38910.4207 | 1 | 0 | 13
38910.4214 | 1 | 0 | 13
38910.4221 | 1 | 0 | 13
38910.4228 | 1 | 0 | 13
38910.4234 | 1 | 0 | 13
38910.4241 | 1 | 0 | 13
38910.4248 | 1 | 0 | 13
38910.4255 | 1 | 0 | 13
38910.4262 | 1 | 0 | 13
38910.4269 | 962 | 1081 | 13
38910.4275 | 294 | 285 | 13
38910.4282 | 2173 | 3 | 13
38910.4289 | 2023 | 1 | 13
38910.4296 | 1863 | 405 | 13
38910.4303 | 1188 | 743 | 13
38910.4309 | 1054 | 791 | 13
38910.4316 | 2232 | 420 | 13
38910.4323 | 1102 | 963 | 13
38910.4146 | 1 | 0 | 14
38910.4153 | 1 | 0 | 14
38910.416 | 1 | 0 | 14
38910.4167 | 1 | 0 | 14
38910.4173 | 1 | 0 | 14
38910.418 | 1 | 0 | 14
38910.4187 | 1 | 0 | 14
38910.4194 | 1 | 0 | 14
38910.4201 | 1 | 0 | 14
38910.4207 | 1 | 0 | 14
38910.4214 | 1 | 0 | 14
38910.4221 | 1 | 0 | 14
38910.4228 | 1 | 0 | 14
38910.4235 | 1 | 0 | 14
38910.4241 | 1 | 0 | 14
38910.4248 | 1 | 0 | 14
38910.4255 | 1 | 0 | 14
38910.4262 | 127 | 124 | 14
38910.4269 | 1089 | 1062 | 14
38910.4275 | 1048 | 1099 | 14
38910.4282 | 2202 | 3 | 14
38910.4289 | 2535 | 1 | 14
38910.4296 | 1943 | 247 | 14
38910.4303 | 1426 | 883 | 14
38910.4309 | 1125 | 802 | 14
38910.4316 | 1863 | 879 | 14
38910.4323 | 1822 | 761 | 14
38910.4146 | 1 | 0 | 15
38910.4153 | 1 | 0 | 15
38910.416 | 1 | 0 | 15
38910.4167 | 1 | 0 | 15
38910.4173 | 1 | 0 | 15
38910.418 | 1 | 0 | 15
38910.4187 | 1 | 0 | 15
38910.4194 | 1 | 0 | 15
38910.4201 | 1 | 0 | 15
38910.4208 | 1 | 0 | 15
38910.4214 | 1 | 0 | 15
38910.4221 | 1 | 0 | 15
38910.4228 | 1 | 0 | 15
38910.4235 | 1 | 0 | 15
38910.4242 | 1 | 0 | 15
38910.4248 | 1 | 0 | 15
38910.4255 | 1 | 0 | 15
38910.4262 | 1 | 0 | 15
38910.4269 | 1054 | 870 | 15
38910.4276 | 1046 | 1100 | 15
38910.4282 | 2261 | 4 | 15
38910.4289 | 1957 | 1 | 15
38910.4296 | 1470 | 356 | 15
38910.4303 | 1333 | 884 | 15
38910.431 | 1160 | 891 | 15
38910.4316 | 1793 | 937 | 15
38910.4323 | 1004 | 938 | 15
38910.4147 | 1 | 0 | 16
38910.4153 | 1 | 0 | 16
38910.416 | 1 | 0 | 16
38910.4167 | 1 | 0 | 16
38910.4174 | 1 | 0 | 16
38910.418 | 1 | 0 | 16
38910.4187 | 1 | 0 | 16
38910.4194 | 1 | 0 | 16
38910.4201 | 1 | 0 | 16
38910.4208 | 1 | 0 | 16
38910.4215 | 1 | 0 | 16
38910.4221 | 1 | 0 | 16
38910.4228 | 1 | 0 | 16
38910.4235 | 1 | 0 | 16
38910.4242 | 1 | 0 | 16
38910.4248 | 1 | 0 | 16
38910.4255 | 1 | 0 | 16
38910.4262 | 1 | 0 | 16
38910.4269 | 1074 | 1122 | 16
38910.4276 | 1088 | 1063 | 16
38910.4283 | 2321 | 3 | 16
38910.4289 | 1962 | 0 | 16
38910.4296 | 1524 | 348 | 16
38910.4303 | 1390 | 863 | 16
38910.431 | 1060 | 797 | 16
38910.4317 | 2036 | 358 | 16
38910.4323 | 1179 | 1036 | 16
38910.4147 | 1 | 0 | 17
38910.4153 | 1 | 0 | 17
38910.416 | 1 | 0 | 17
38910.4167 | 1 | 0 | 17
38910.4174 | 1 | 0 | 17
38910.4181 | 1 | 0 | 17
38910.4187 | 1 | 0 | 17
38910.4194 | 1 | 0 | 17
38910.4201 | 1 | 0 | 17
38910.4208 | 1 | 0 | 17
38910.4215 | 1 | 0 | 17
38910.4222 | 1 | 0 | 17
38910.4228 | 1 | 0 | 17
38910.4235 | 1 | 0 | 17
38910.4242 | 1 | 0 | 17
38910.4249 | 1 | 0 | 17
38910.4256 | 1 | 0 | 17
38910.4262 | 1 | 0 | 17
38910.4269 | 904 | 879 | 17
38910.4276 | 1090 | 1066 | 17
38910.4283 | 2502 | 4 | 17
38910.429 | 2214 | 1 | 17
38910.4296 | 1781 | 398 | 17
38910.4303 | 1392 | 893 | 17
38910.431 | 1053 | 827 | 17
38910.4317 | 1100 | 863 | 17
38910.4147 | 1 | 0 | 18
38910.4154 | 1 | 0 | 18
38910.416 | 1 | 0 | 18
38910.4167 | 1 | 0 | 18
38910.4174 | 1 | 0 | 18
38910.4181 | 1 | 0 | 18
38910.4188 | 1 | 0 | 18
38910.4194 | 1 | 0 | 18
38910.4201 | 1 | 0 | 18
38910.4208 | 1 | 0 | 18
38910.4215 | 1 | 0 | 18
38910.4222 | 1 | 0 | 18
38910.4228 | 1 | 0 | 18
38910.4235 | 1 | 0 | 18
38910.4242 | 1 | 0 | 18
38910.4249 | 1 | 0 | 18
38910.4256 | 1 | 0 | 18
38910.4262 | 1 | 0 | 18
38910.4269 | 1017 | 992 | 18
38910.4276 | 291 | 318 | 18
38910.4283 | 2524 | 3 | 18
38910.429 | 2195 | 1 | 18
38910.4297 | 1733 | 404 | 18
38910.4303 | 1949 | 839 | 18
38910.431 | 1867 | 727 | 18
38910.4317 | 1771 | 657 | 18
38910.4324 | 1233 | 1100 | 18
38910.4147 | 1 | 0 | 19
38910.4154 | 1 | 0 | 19
38910.4161 | 1 | 0 | 19
38910.4167 | 1 | 0 | 19
38910.4174 | 1 | 0 | 19
38910.4181 | 1 | 0 | 19
38910.4188 | 1 | 0 | 19
38910.4195 | 1 | 0 | 19
38910.4201 | 1 | 0 | 19
38910.4208 | 1 | 0 | 19
38910.4222 | 1 | 0 | 19
38910.4229 | 1 | 0 | 19
38910.4235 | 1 | 0 | 19
38910.4242 | 1 | 0 | 19
38910.4249 | 1 | 0 | 19
38910.4256 | 1 | 0 | 19
38910.4263 | 1 | 0 | 19
38910.4269 | 982 | 956 | 19
38910.4276 | 933 | 977 | 19
38910.4283 | 2380 | 3 | 19
38910.429 | 2164 | 1 | 19
38910.4297 | 1452 | 369 | 19
38910.4303 | 1738 | 451 | 19
38910.431 | 1063 | 786 | 19
38910.4317 | 1716 | 594 | 19
38910.4324 | 1174 | 1119 | 19
38910.4147 | 1 | 0 | 20
38910.4154 | 4 | 0 | 20
38910.4161 | 1 | 0 | 20
38910.4168 | 1 | 0 | 20
38910.4174 | 1 | 0 | 20
38910.4181 | 1 | 0 | 20
38910.4188 | 1 | 0 | 20
38910.4195 | 1 | 0 | 20
38910.4202 | 1 | 0 | 20
38910.4208 | 1 | 0 | 20
38910.4222 | 1 | 0 | 20
38910.4229 | 1 | 0 | 20
38910.4236 | 1 | 0 | 20
38910.4242 | 1 | 0 | 20
38910.4249 | 1 | 0 | 20
38910.4256 | 1 | 0 | 20
38910.4263 | 2 | 0 | 20
38910.427 | 1075 | 1129 | 20
38910.4276 | 882 | 936 | 20
38910.4283 | 2132 | 3 | 20
38910.429 | 2389 | 1 | 20
38910.4297 | 1550 | 298 | 20
38910.4304 | 1664 | 913 | 20
38910.431 | 1748 | 495 | 20
38910.4317 | 1713 | 384 | 20
38910.4324 | 1035 | 1048 | 20
38910.4147 | 1 | 0 | 21
38910.4154 | 1 | 0 | 21
38910.4161 | 1 | 0 | 21
38910.4168 | 1 | 0 | 21
38910.4175 | 1 | 0 | 21
38910.4181 | 1 | 0 | 21
38910.4188 | 1 | 0 | 21
38910.4195 | 1 | 0 | 21
38910.4202 | 1 | 0 | 21
38910.4209 | 1 | 0 | 21
38910.4215 | 1 | 0 | 21
38910.4222 | 1 | 0 | 21
38910.4229 | 1 | 0 | 21
38910.4236 | 1 | 0 | 21
38910.4243 | 1 | 0 | 21
38910.4249 | 1 | 0 | 21
38910.4256 | 1 | 0 | 21
38910.4263 | 1039 | 1030 | 21
38910.427 | 1008 | 980 | 21
38910.4277 | 969 | 1085 | 21
38910.4283 | 2447 | 3 | 21
38910.429 | 2456 | 1 | 21
38910.4297 | 1690 | 328 | 21
38910.4304 | 1270 | 846 | 21
38910.4311 | 1231 | 769 | 21
38910.4317 | 1851 | 282 | 21
38910.4324 | 2125 | 891 | 21
38910.4147 | 1 | 0 | 22
38910.4154 | 1 | 0 | 22
38910.4161 | 1 | 0 | 22
38910.4168 | 1 | 0 | 22
38910.4175 | 1 | 0 | 22
38910.4181 | 1 | 0 | 22
38910.4188 | 1 | 0 | 22
38910.4195 | 1 | 0 | 22
38910.4202 | 1 | 0 | 22
38910.4209 | 1 | 0 | 22
38910.4216 | 1 | 0 | 22
38910.4222 | 1 | 0 | 22
38910.4229 | 1 | 0 | 22
38910.4236 | 1 | 0 | 22
38910.4243 | 1 | 0 | 22
38910.425 | 1 | 0 | 22
38910.4256 | 1 | 0 | 22
38910.4263 | 1016 | 1074 | 22
38910.427 | 1063 | 1037 | 22
38910.4277 | 930 | 903 | 22
38910.4284 | 2151 | 3 | 22
38910.429 | 2037 | 1 | 22
38910.4297 | 1698 | 362 | 22
38910.4304 | 1345 | 861 | 22
38910.4311 | 2130 | 927 | 22
38910.4318 | 2159 | 483 | 22
38910.4324 | 1127 | 1101 | 22
38910.4148 | 1 | 0 | 23
38910.4154 | 1 | 0 | 23
38910.4161 | 1 | 0 | 23
38910.4168 | 1 | 0 | 23
38910.4175 | 1 | 0 | 23
38910.4182 | 1 | 0 | 23
38910.4188 | 1 | 0 | 23
38910.4195 | 1 | 0 | 23
38910.4202 | 1 | 0 | 23
38910.4209 | 1 | 0 | 23
38910.4216 | 1 | 0 | 23
38910.4222 | 1 | 0 | 23
38910.4229 | 1 | 0 | 23
38910.4236 | 1 | 0 | 23
38910.4243 | 1 | 0 | 23
38910.425 | 1 | 0 | 23
38910.4256 | 1 | 0 | 23
38910.4263 | 2 | 4 | 23
38910.427 | 958 | 930 | 23
38910.4277 | 961 | 999 | 23
38910.4284 | 2112 | 2 | 23
38910.4291 | 2101 | 1 | 23
38910.4297 | 1791 | 477 | 23
38910.4304 | 1350 | 852 | 23
38910.4311 | 1925 | 495 | 23
38910.4318 | 2081 | 387 | 23
38910.4325 | 985 | 876 | 23
38910.4148 | 1 | 0 | 24
38910.4155 | 1 | 0 | 24
38910.4161 | 1 | 0 | 24
38910.4168 | 1 | 0 | 24
38910.4175 | 1 | 0 | 24
38910.4182 | 1 | 0 | 24
38910.4189 | 1 | 0 | 24
38910.4195 | 1 | 0 | 24
38910.4202 | 1 | 0 | 24
38910.4209 | 1 | 0 | 24
38910.4216 | 1 | 0 | 24
38910.4223 | 1 | 0 | 24
38910.4229 | 1 | 0 | 24
38910.4236 | 1 | 0 | 24
38910.4243 | 1 | 0 | 24
38910.425 | 1 | 0 | 24
38910.4257 | 1 | 0 | 24
38910.4263 | 2 | 1 | 24
38910.427 | 1056 | 1109 | 24
38910.4277 | 917 | 892 | 24
38910.4284 | 2243 | 3 | 24
38910.4291 | 2386 | 1 | 24
38910.4297 | 1482 | 379 | 24
38910.4304 | 1382 | 966 | 24
38910.4311 | 1211 | 1006 | 24
38910.4318 | 1744 | 230 | 24
38910.4325 | 1096 | 979 | 24
38910.4148 | 1 | 0 | 25
38910.4155 | 1 | 0 | 25
38910.4162 | 1 | 0 | 25
38910.4168 | 1 | 0 | 25
38910.4175 | 1 | 0 | 25
38910.4182 | 1 | 0 | 25
38910.4189 | 1 | 0 | 25
38910.4196 | 1 | 0 | 25
38910.4202 | 1 | 0 | 25
38910.4209 | 1 | 0 | 25
38910.4216 | 1 | 0 | 25
38910.4223 | 1 | 0 | 25
38910.423 | 1 | 0 | 25
38910.4236 | 1 | 0 | 25
38910.4243 | 1 | 0 | 25
38910.425 | 1 | 0 | 25
38910.4257 | 1 | 0 | 25
38910.4264 | 4 | 2 | 25
38910.427 | 998 | 975 | 25
38910.4277 | 983 | 954 | 25
38910.4284 | 2411 | 2 | 25
38910.4291 | 2430 | 1 | 25
38910.4298 | 1821 | 473 | 25
38910.4304 | 1391 | 960 | 25
38910.4311 | 1314 | 790 | 25
38910.4318 | 1753 | 370 | 25
38910.4325 | 1038 | 996 | 25
38910.4148 | 1 | 0 | 26
38910.4155 | 1 | 0 | 26
38910.4162 | 1 | 0 | 26
38910.4169 | 1 | 0 | 26
38910.4175 | 1 | 0 | 26
38910.4182 | 1 | 0 | 26
38910.4189 | 1 | 0 | 26
38910.4196 | 1 | 0 | 26
38910.4203 | 1 | 0 | 26
38910.4209 | 1 | 0 | 26
38910.4216 | 1 | 0 | 26
38910.4223 | 1 | 0 | 26
38910.423 | 1 | 0 | 26
38910.4237 | 1 | 0 | 26
38910.4243 | 1 | 0 | 26
38910.425 | 1 | 0 | 26
38910.4257 | 1 | 0 | 26
38910.4264 | 8 | 6 | 26
38910.4271 | 839 | 865 | 26
38910.4277 | 940 | 913 | 26
38910.4284 | 1992 | 2 | 26
38910.4291 | 1937 | 1 | 26
38910.4298 | 1615 | 390 | 26
38910.4305 | 1268 | 846 | 26
38910.4311 | 1945 | 717 | 26
38910.4318 | 1931 | 508 | 26
38910.4325 | 1235 | 1111 | 26
38910.4148 | 1 | 0 | 27
38910.4155 | 1 | 0 | 27
38910.4162 | 1 | 0 | 27
38910.4169 | 1 | 0 | 27
38910.4175 | 1 | 0 | 27
38910.4182 | 1 | 0 | 27
38910.4189 | 1 | 0 | 27
38910.4196 | 1 | 0 | 27
38910.4203 | 1 | 0 | 27
38910.4209 | 1 | 0 | 27
38910.4216 | 1 | 0 | 27
38910.4223 | 1 | 0 | 27
38910.423 | 1 | 0 | 27
38910.4237 | 1 | 0 | 27
38910.4244 | 1 | 0 | 27
38910.425 | 1 | 0 | 27
38910.4257 | 1 | 0 | 27
38910.4264 | 759 | 654 | 27
38910.4271 | 876 | 907 | 27
38910.4278 | 1033 | 1004 | 27
38910.4284 | 2051 | 2 | 27
38910.4291 | 2068 | 1 | 27
38910.4298 | 1555 | 448 | 27
38910.4305 | 1169 | 798 | 27
38910.4312 | 1852 | 402 | 27
38910.4318 | 2040 | 369 | 27
38910.4325 | 2262 | 881 | 27
38910.4148 | 1 | 0 | 28
38910.4155 | 1 | 0 | 28
38910.4162 | 1 | 0 | 28
38910.4169 | 1 | 0 | 28
38910.4176 | 1 | 0 | 28
38910.4182 | 1 | 0 | 28
38910.4189 | 1 | 0 | 28
38910.4196 | 1 | 0 | 28
38910.4203 | 1 | 0 | 28
38910.421 | 1 | 0 | 28
38910.4216 | 1 | 0 | 28
38910.4223 | 1 | 0 | 28
38910.423 | 1 | 0 | 28
38910.4237 | 1 | 0 | 28
38910.4244 | 1 | 0 | 28
38910.425 | 1 | 0 | 28
38910.4257 | 2 | 0 | 28
38910.4264 | 747 | 723 | 28
38910.4271 | 1029 | 1005 | 28
38910.4278 | 1115 | 1084 | 28
38910.4284 | 2052 | 2 | 28
38910.4291 | 2254 | 0 | 28
38910.4298 | 2260 | 320 | 28
38910.4305 | 1330 | 879 | 28
38910.4312 | 1290 | 1032 | 28
38910.4319 | 1816 | 713 | 28
38910.4325 | 2225 | 882 | 28
38910.4149 | 1 | 0 | 29
38910.4155 | 1 | 0 | 29
38910.4162 | 1 | 0 | 29
38910.4169 | 1 | 0 | 29
38910.4176 | 1 | 0 | 29
38910.4183 | 1 | 0 | 29
38910.4189 | 1 | 0 | 29
38910.4196 | 1 | 0 | 29
38910.4203 | 1 | 0 | 29
38910.421 | 1 | 0 | 29
38910.4217 | 1 | 0 | 29
38910.4223 | 1 | 0 | 29
38910.423 | 1 | 0 | 29
38910.4237 | 1 | 0 | 29
38910.4244 | 1 | 0 | 29
38910.4251 | 1 | 0 | 29
38910.4257 | 1 | 0 | 29
38910.4264 | 941 | 917 | 29
38910.4271 | 1111 | 1085 | 29
38910.4278 | 431 | 398 | 29
38910.4285 | 2382 | 2 | 29
38910.4291 | 2306 | 3 | 29
38910.4298 | 2150 | 455 | 29
38910.4305 | 1398 | 945 | 29
38910.4312 | 1317 | 1012 | 29
38910.4319 | 1137 | 913 | 29
38910.4325 | 1028 | 924 | 29
38910.4149 | 1 | 0 | 30
38910.4156 | 1 | 0 | 30
38910.4162 | 1 | 0 | 30
38910.4169 | 1 | 0 | 30
38910.4176 | 1 | 0 | 30
38910.4183 | 1 | 0 | 30
38910.419 | 1 | 0 | 30
38910.4196 | 1 | 0 | 30
38910.4203 | 1 | 0 | 30
38910.421 | 1 | 0 | 30
38910.4217 | 1 | 0 | 30
38910.4224 | 1 | 0 | 30
38910.423 | 1 | 0 | 30
38910.4237 | 1 | 0 | 30
38910.4244 | 1 | 0 | 30
38910.4251 | 1 | 0 | 30
38910.4258 | 1 | 0 | 30
38910.4264 | 942 | 916 | 30
38910.4271 | 1068 | 1154 | 30
38910.4278 | 1359 | 574 | 30
38910.4285 | 2375 | 2 | 30
38910.4292 | 1963 | 1 | 30
38910.4298 | 1533 | 449 | 30
38910.4305 | 1183 | 777 | 30
38910.4312 | 1056 | 817 | 30
38910.4319 | 1028 | 856 | 30
38910.4326 | 1764 | 416 | 30
38910.4149 | 1 | 0 | 31
38910.4156 | 1 | 0 | 31
38910.4163 | 1 | 0 | 31
38910.4169 | 1 | 0 | 31
38910.4176 | 1 | 0 | 31
38910.4183 | 2 | 0 | 31
38910.419 | 1 | 0 | 31
38910.4197 | 1 | 0 | 31
38910.4203 | 1 | 0 | 31
38910.421 | 1 | 0 | 31
38910.4217 | 1 | 0 | 31
38910.4224 | 1 | 0 | 31
38910.4231 | 1 | 0 | 31
38910.4237 | 1 | 0 | 31
38910.4244 | 1 | 0 | 31
38910.4251 | 1 | 0 | 31
38910.4258 | 1 | 0 | 31
38910.4265 | 102 | 105 | 31
38910.4271 | 1127 | 1126 | 31
38910.4278 | 1581 | 617 | 31
38910.4285 | 2484 | 2 | 31
38910.4292 | 2316 | 25 | 31
38910.4299 | 1541 | 430 | 31
38910.4305 | 1086 | 810 | 31
38910.4312 | 1847 | 390 | 31
38910.4319 | 1065 | 894 | 31
38910.4326 | 1225 | 1096 | 31
38910.4149 | 1 | 0 | 32
38910.4156 | 1 | 0 | 32
38910.4163 | 1 | 0 | 32
38910.4169 | 1 | 0 | 32
38910.4176 | 1 | 0 | 32
38910.4183 | 1 | 0 | 32
38910.419 | 1 | 0 | 32
38910.4197 | 1 | 0 | 32
38910.4203 | 1 | 0 | 32
38910.421 | 1 | 0 | 32
38910.4217 | 1 | 0 | 32
38910.4224 | 1 | 0 | 32
38910.4231 | 1 | 0 | 32
38910.4238 | 1 | 0 | 32
38910.4244 | 1 | 0 | 32
38910.4251 | 1 | 0 | 32
38910.4258 | 1 | 0 | 32
38910.4265 | 637 | 696 | 32
38910.4272 | 961 | 935 | 32
38910.4278 | 1910 | 657 | 32
38910.4285 | 1985 | 2 | 32
38910.4292 | 2020 | 97 | 32
38910.4299 | 1719 | 522 | 32
38910.4306 | 1294 | 872 | 32
38910.4312 | 1220 | 1022 | 32
38910.4319 | 1889 | 750 | 32
38910.4326 | 1233 | 1111 | 32
38910.4149 | 1 | 0 | 33
38910.4156 | 1 | 0 | 33
38910.4163 | 1 | 0 | 33
38910.417 | 1 | 0 | 33
38910.4177 | 1 | 0 | 33
38910.4183 | 1 | 0 | 33
38910.419 | 1 | 0 | 33
38910.4197 | 1 | 0 | 33
38910.4204 | 1 | 0 | 33
38910.421 | 1 | 0 | 33
38910.4217 | 1 | 0 | 33
38910.4224 | 1 | 0 | 33
38910.4231 | 1 | 0 | 33
38910.4238 | 1 | 0 | 33
38910.4244 | 1 | 0 | 33
38910.4251 | 1 | 0 | 33
38910.4258 | 1 | 0 | 33
38910.4265 | 655 | 653 | 33
38910.4272 | 878 | 914 | 33
38910.4278 | 1977 | 717 | 33
38910.4285 | 2149 | 2 | 33
38910.4292 | 1910 | 101 | 33
38910.4299 | 1978 | 559 | 33
38910.4306 | 1377 | 927 | 33
38910.4313 | 1284 | 1003 | 33
38910.4319 | 1916 | 280 | 33
38910.4326 | 1000 | 896 | 33
38910.4149 | 1 | 0 | 34
38910.4156 | 1 | 0 | 34
38910.4163 | 1 | 0 | 34
38910.417 | 1 | 0 | 34
38910.4177 | 1 | 0 | 34
38910.4183 | 1 | 0 | 34
38910.419 | 1 | 0 | 34
38910.4197 | 1 | 0 | 34
38910.4204 | 1 | 0 | 34
38910.4211 | 1 | 0 | 34
38910.4217 | 1 | 0 | 34
38910.4224 | 1 | 0 | 34
38910.4231 | 1 | 0 | 34
38910.4238 | 1 | 0 | 34
38910.4245 | 1 | 0 | 34
38910.4252 | 1 | 0 | 34
38910.4258 | 1 | 0 | 34
38910.4265 | 734 | 764 | 34
38910.4272 | 906 | 880 | 34
38910.4279 | 1655 | 592 | 34
38910.4286 | 2259 | 2 | 34
38910.4292 | 1978 | 151 | 34
38910.4299 | 1386 | 488 | 34
38910.4306 | 1406 | 968 | 34
38910.4313 | 1243 | 967 | 34
38910.4319 | 1881 | 397 | 34
38910.4326 | 969 | 888 | 34
38910.415 | 1 | 0 | 35
38910.4156 | 1 | 0 | 35
38910.4163 | 1 | 0 | 35
38910.417 | 1 | 0 | 35
38910.4177 | 1 | 0 | 35
38910.4184 | 1 | 0 | 35
38910.419 | 1 | 0 | 35
38910.4197 | 1 | 0 | 35
38910.4204 | 1 | 0 | 35
38910.4211 | 1 | 0 | 35
38910.4218 | 1 | 0 | 35
38910.4224 | 1 | 0 | 35
38910.4231 | 1 | 0 | 35
38910.4238 | 1 | 0 | 35
38910.4245 | 1 | 0 | 35
38910.4252 | 1 | 0 | 35
38910.4258 | 1 | 0 | 35
38910.4265 | 866 | 842 | 35
38910.4272 | 1163 | 1143 | 35
38910.4279 | 1725 | 560 | 35
38910.4286 | 2440 | 3 | 35
38910.4292 | 2089 | 228 | 35
38910.4299 | 1385 | 494 | 35
38910.4306 | 1239 | 947 | 35
38910.4313 | 1222 | 812 | 35
38910.432 | 2260 | 827 | 35
38910.4327 | 1189 | 925 | 35
38910.415 | 1 | 0 | 36
38910.4156 | 1 | 0 | 36
38910.4163 | 1 | 0 | 36
38910.417 | 1 | 0 | 36
38910.4177 | 1 | 0 | 36
38910.4184 | 1 | 0 | 36
38910.4191 | 1 | 0 | 36
38910.4197 | 1 | 0 | 36
38910.4204 | 1 | 0 | 36
38910.4211 | 1 | 0 | 36
38910.4218 | 1 | 0 | 36
38910.4225 | 1 | 0 | 36
38910.4231 | 1 | 0 | 36
38910.4238 | 1 | 0 | 36
38910.4245 | 1 | 0 | 36
38910.4252 | 1 | 0 | 36
38910.4259 | 1 | 0 | 36
38910.4265 | 969 | 999 | 36
38910.4272 | 1165 | 1097 | 36
38910.4279 | 1007 | 11 | 36
38910.4286 | 2394 | 2 | 36
38910.4293 | 1776 | 361 | 36
38910.4299 | 1518 | 602 | 36
38910.4306 | 1388 | 899 | 36
38910.4313 | 1029 | 819 | 36
38910.432 | 2095 | 604 | 36
38910.4327 | 1087 | 1054 | 36
38910.415 | 1 | 0 | 37
38910.4157 | 1 | 0 | 37
38910.4164 | 1 | 0 | 37
38910.417 | 1 | 0 | 37
38910.4177 | 1 | 0 | 37
38910.4184 | 1 | 0 | 37
38910.4191 | 1 | 0 | 37
38910.4198 | 1 | 0 | 37
38910.4204 | 1 | 0 | 37
38910.4211 | 1 | 0 | 37
38910.4218 | 1 | 0 | 37
38910.4225 | 1 | 0 | 37
38910.4231 | 1 | 0 | 37
38910.4238 | 1 | 0 | 37
38910.4245 | 1 | 0 | 37
38910.4252 | 1 | 0 | 37
38910.4259 | 1 | 0 | 37
38910.4266 | 837 | 819 | 37
38910.4272 | 931 | 904 | 37
38910.4279 | 2101 | 7 | 37
38910.4286 | 2154 | 2 | 37
38910.4293 | 2010 | 240 | 37
38910.43 | 1705 | 589 | 37
38910.4306 | 1237 | 837 | 37
38910.4313 | 1198 | 943 | 37
38910.432 | 2119 | 429 | 37
38910.4327 | 996 | 901 | 37
38910.415 | 1 | 0 | 38
38910.4157 | 1 | 0 | 38
38910.4164 | 1 | 0 | 38
38910.417 | 2 | 0 | 38
38910.4177 | 1 | 0 | 38
38910.4184 | 1 | 0 | 38
38910.4191 | 1 | 0 | 38
38910.4198 | 1 | 0 | 38
38910.4205 | 1 | 0 | 38
38910.4211 | 1 | 0 | 38
38910.4218 | 1 | 0 | 38
38910.4225 | 1 | 0 | 38
38910.4232 | 1 | 0 | 38
38910.4239 | 1 | 0 | 38
38910.4245 | 1 | 0 | 38
38910.4252 | 1 | 0 | 38
38910.4259 | 1 | 0 | 38
38910.4266 | 696 | 677 | 38
38910.4273 | 923 | 959 | 38
38910.4279 | 2378 | 7 | 38
38910.4286 | 2063 | 2 | 38
38910.4293 | 1912 | 356 | 38
38910.43 | 1308 | 647 | 38
38910.4306 | 1205 | 819 | 38
38910.4313 | 2043 | 588 | 38
38910.432 | 2110 | 590 | 38
38910.4327 | 991 | 895 | 38
38910.415 | 1 | 0 | 39
38910.4157 | 1 | 0 | 39
38910.4171 | 1 | 0 | 39
38910.4177 | 1 | 0 | 39
38910.4184 | 1 | 0 | 39
38910.4191 | 1 | 0 | 39
38910.4198 | 1 | 0 | 39
38910.4205 | 1 | 0 | 39
38910.4211 | 1 | 0 | 39
38910.4218 | 1 | 0 | 39
38910.4225 | 1 | 0 | 39
38910.4232 | 1 | 0 | 39
38910.4239 | 1 | 0 | 39
38910.4245 | 1 | 0 | 39
38910.4252 | 1 | 0 | 39
38910.4259 | 1 | 0 | 39
38910.4266 | 760 | 736 | 39
38910.4273 | 1108 | 1086 | 39
38910.428 | 2482 | 6 | 39
38910.4286 | 2320 | 2 | 39
38910.4293 | 2057 | 247 | 39
38910.43 | 1635 | 760 | 39
38910.4307 | 1485 | 919 | 39
38910.4314 | 1296 | 1068 | 39
38910.432 | 2267 | 406 | 39
38910.4327 | 1109 | 1008 | 39
38910.415 | 1 | 0 | 40
38910.4157 | 1 | 0 | 40
38910.4164 | 1 | 0 | 40
38910.4171 | 1 | 0 | 40
38910.4178 | 1 | 0 | 40
38910.4184 | 2 | 0 | 40
38910.4191 | 1 | 0 | 40
38910.4198 | 1 | 0 | 40
38910.4205 | 1 | 0 | 40
38910.4212 | 1 | 0 | 40
38910.4218 | 1 | 0 | 40
38910.4225 | 1 | 0 | 40
38910.4232 | 1 | 0 | 40
38910.4239 | 1 | 0 | 40
38910.4246 | 1 | 0 | 40
38910.4252 | 1 | 0 | 40
38910.4259 | 1 | 0 | 40
38910.4266 | 848 | 825 | 40
38910.4273 | 1126 | 1126 | 40
38910.428 | 2390 | 6 | 40
38910.4286 | 2358 | 2 | 40
38910.4293 | 1915 | 290 | 40
38910.43 | 1626 | 645 | 40
38910.4307 | 1395 | 970 | 40
38910.4314 | 1823 | 493 | 40
38910.432 | 1023 | 920 | 40
38910.4327 | 1078 | 976 | 40
38910.415 | 1 | 0 | 41
38910.4157 | 1 | 0 | 41
38910.4164 | 1 | 0 | 41
38910.4171 | 1 | 0 | 41
38910.4178 | 1 | 0 | 41
38910.4184 | 1 | 0 | 41
38910.4191 | 1 | 0 | 41
38910.4198 | 1 | 0 | 41
38910.4205 | 1 | 0 | 41
38910.4212 | 1 | 0 | 41
38910.4219 | 1 | 0 | 41
38910.4225 | 1 | 0 | 41
38910.4232 | 1 | 0 | 41
38910.4239 | 1 | 0 | 41
38910.4246 | 1 | 0 | 41
38910.4253 | 1 | 0 | 41
38910.4259 | 1 | 0 | 41
38910.4266 | 1021 | 997 | 41
38910.4273 | 903 | 931 | 41
38910.428 | 2196 | 5 | 41
38910.4287 | 2458 | 2 | 41
38910.4293 | 1678 | 208 | 41
38910.43 | 1376 | 651 | 41
38910.4307 | 1150 | 864 | 41
38910.4314 | 1978 | 811 | 41
38910.4321 | 1114 | 946 | 41
38910.4327 | 959 | 971 | 41
38910.4151 | 1 | 0 | 42
38910.4158 | 1 | 0 | 42
38910.4164 | 1 | 0 | 42
38910.4171 | 1 | 0 | 42
38910.4178 | 1 | 0 | 42
38910.4185 | 1 | 0 | 42
38910.4192 | 1 | 0 | 42
38910.4198 | 1 | 0 | 42
38910.4205 | 1 | 0 | 42
38910.4212 | 1 | 0 | 42
38910.4219 | 1 | 0 | 42
38910.4226 | 1 | 0 | 42
38910.4232 | 1 | 0 | 42
38910.4239 | 1 | 0 | 42
38910.4246 | 1 | 0 | 42
38910.4253 | 1 | 0 | 42
38910.426 | 1 | 0 | 42
38910.4266 | 991 | 1079 | 42
38910.4273 | 978 | 952 | 42
38910.428 | 2008 | 5 | 42
38910.4287 | 2518 | 1 | 42
38910.4294 | 1651 | 216 | 42
38910.43 | 1456 | 645 | 42
38910.4307 | 1136 | 787 | 42
38910.4314 | 1754 | 519 | 42
38910.4321 | 1771 | 709 | 42
38910.4328 | 964 | 932 | 42