## Test Facts
Penlight Ignition Time | 101

## RawData
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43
38889.4874 | 1 | 0 | 1 | PE/PVC | 7-C | Tray
38889.4878 | 1 | 0 | 1 | 325 C | 7.2 kW/m2 |  | Conductors
38889.4883 | 1 | 0 | 1
38889.4887 | 1 | 0 | 1
38889.4891 | 1 | 0 | 1
38889.4896 | 1 | 0 | 1
38889.49 | 1 | 0 | 1
38889.4905 | 1 | 0 | 1
38889.4909 | 1 | 0 | 1
38889.4913 | 1 | 0 | 1
38889.4918 | 1 | 0 | 1
38889.4922 | 1 | 0 | 1
38889.4926 | 1 | 0 | 1
38889.4931 | 1 | 0 | 1
38889.4935 | 1 | 0 | 1
38889.494 | 1 | 0 | 1
38889.4944 | 1 | 0 | 1
38889.4948 | 1 | 0 | 1
38889.4953 | 1 | 0 | 1
38889.4957 | 1 | 0 | 1
38889.4961 | 1 | 0 | 1
38889.4966 | 1 | 0 | 1
38889.497 | 1 | 0 | 1
38889.4975 | 1 | 0 | 1
38889.4979 | 1 | 0 | 1
38889.4983 | 1 | 0 | 1
38889.4988 | 1 | 0 | 1
38889.4992 | 2 | 0 | 1
38889.4996 | 2 | 0 | 1
38889.5001 | 2 | 0 | 1
38889.5005 | 2 | 0 | 1
38889.5009 | 2 | 0 | 1
38889.5014 | 2 | 0 | 1
38889.5018 | 922 | 1024 | 1
38889.5023 | 118 | 130 | 1
38889.5031 | 1019 | 1061 | 1
38889.5036 | 1141 | 1177 | 1
38889.504 | 951 | 924 | 1
38889.5045 | 1005 | 1045 | 1
38889.5049 | 1010 | 982 | 1
38889.5053 | 1128 | 1098 | 1
38889.5058 | 1009 | 983 | 1
38889.5062 | 1148 | 1184 | 1
38889.5066 | 1079 | 1051 | 1
38889.5071 | 1075 | 1048 | 1
38889.5075 | 1179 | 1155 | 1
38889.508 | 1052 | 1026 | 1
38889.5084 | 1117 | 1169 | 1
38889.5088 | 950 | 924 | 1
38889.5097 | 1013 | 987 | 1
38889.5101 | 1020 | 1063 | 1
38889.511 | 1130 | 1180 | 1
38889.5114 | 1181 | 1173 | 1
38889.5128 | 1065 | 1114 | 1
38889.5132 | 4 | 0 | 1
38889.4874 | 1 | 0 | 2
38889.4878 | 1 | 0 | 2
38889.4883 | 1 | 0 | 2
38889.4887 | 1 | 0 | 2
38889.4892 | 1 | 0 | 2
38889.4896 | 1 | 0 | 2
38889.49 | 1 | 0 | 2
38889.4905 | 1 | 0 | 2
38889.4909 | 1 | 0 | 2
38889.4913 | 1 | 0 | 2
38889.4918 | 1 | 0 | 2
38889.4922 | 1 | 0 | 2
38889.4927 | 1 | 0 | 2
38889.4931 | 1 | 0 | 2
38889.4935 | 1 | 0 | 2
38889.494 | 1 | 0 | 2
38889.4944 | 1 | 0 | 2
38889.4948 | 1 | 0 | 2
38889.4953 | 1 | 0 | 2
38889.4957 | 1 | 0 | 2
38889.4962 | 1 | 0 | 2
38889.4966 | 1 | 0 | 2
38889.497 | 1 | 0 | 2
38889.4975 | 1 | 0 | 2
38889.4979 | 1 | 0 | 2
38889.4983 | 1 | 0 | 2
38889.4988 | 1 | 0 | 2
38889.4992 | 1 | 0 | 2
38889.4997 | 1 | 0 | 2
38889.5001 | 1 | 0 | 2
38889.5005 | 1 | 0 | 2
38889.501 | 1 | 0 | 2
38889.5014 | 1 | 0 | 2
38889.5023 | 97 | 102 | 2
38889.5027 | 935 | 1028 | 2
38889.5031 | 1189 | 1165 | 2
38889.5036 | 1165 | 1139 | 2
38889.504 | 1120 | 1172 | 2
38889.5045 | 1195 | 1176 | 2
38889.5049 | 1187 | 1164 | 2
38889.5053 | 1013 | 986 | 2
38889.5058 | 1070 | 1122 | 2
38889.5062 | 1137 | 1108 | 2
38889.5067 | 1188 | 1182 | 2
38889.5071 | 1112 | 1085 | 2
38889.5075 | 950 | 925 | 2
38889.508 | 1201 | 1186 | 2
38889.5084 | 1188 | 1164 | 2
38889.5088 | 1148 | 1119 | 2
38889.5097 | 1071 | 1043 | 2
38889.5102 | 1204 | 1191 | 2
38889.5106 | 1078 | 1094 | 2
38889.511 | 964 | 940 | 2
38889.5115 | 1040 | 1086 | 2
38889.5128 | 1118 | 1183 | 2
38889.4874 | 1 | 0 | 3
38889.4878 | 1 | 0 | 3
38889.4883 | 1 | 0 | 3
38889.4887 | 1 | 0 | 3
38889.4892 | 2 | 0 | 3
38889.4896 | 1 | 0 | 3
38889.49 | 1 | 0 | 3
38889.4905 | 1 | 0 | 3
38889.4909 | 1 | 0 | 3
38889.4914 | 1 | 0 | 3
38889.4918 | 1 | 0 | 3
38889.4922 | 1 | 0 | 3
38889.4927 | 1 | 0 | 3
38889.4931 | 1 | 0 | 3
38889.4935 | 1 | 0 | 3
38889.494 | 1 | 0 | 3
38889.4944 | 1 | 0 | 3
38889.4948 | 1 | 0 | 3
38889.4953 | 1 | 0 | 3
38889.4957 | 1 | 0 | 3
38889.4962 | 1 | 0 | 3
38889.4966 | 1 | 0 | 3
38889.497 | 1 | 0 | 3
38889.4975 | 1 | 0 | 3
38889.4979 | 1 | 0 | 3
38889.4984 | 1 | 0 | 3
38889.4988 | 1 | 0 | 3
38889.4992 | 1 | 0 | 3
38889.4997 | 1 | 0 | 3
38889.5001 | 1 | 0 | 3
38889.5005 | 1 | 0 | 3
38889.501 | 1 | 0 | 3
38889.5014 | 1 | 0 | 3
38889.5019 | 1 | 0 | 3
38889.5023 | 1 | 0 | 3
38889.5027 | 1 | 1 | 3
38889.5032 | 1 | 1 | 3
38889.5036 | 2 | 1 | 3
38889.504 | 1 | 1 | 3
38889.5045 | 1 | 0 | 3
38889.5049 | 1 | 0 | 3
38889.5053 | 2 | 1 | 3
38889.5058 | 1 | 1 | 3
38889.5062 | 2 | 0 | 3
38889.5067 | 1 | 0 | 3
38889.5071 | 1 | 1 | 3
38889.5075 | 2 | 1 | 3
38889.508 | 1 | 0 | 3
38889.5084 | 1 | 1 | 3
38889.5089 | 1 | 1 | 3
38889.5097 | 2 | 0 | 3
38889.5102 | 2 | 1 | 3
38889.5106 | 1 | 1 | 3
38889.511 | 1 | 0 | 3
38889.5115 | 1 | 0 | 3
38889.5119 | 1 | 0 | 3
38889.5123 | 1 | 0 | 3
38889.5128 | 1 | 1 | 3
38889.5132 | 1 | 1 | 3
38889.4874 | 1 | 0 | 4
38889.4879 | 1 | 0 | 4
38889.4883 | 1 | 0 | 4
38889.4887 | 1 | 0 | 4
38889.4892 | 1 | 0 | 4
38889.4896 | 1 | 0 | 4
38889.49 | 1 | 0 | 4
38889.4905 | 1 | 0 | 4
38889.4909 | 1 | 0 | 4
38889.4914 | 1 | 0 | 4
38889.4918 | 1 | 0 | 4
38889.4922 | 1 | 0 | 4
38889.4927 | 1 | 0 | 4
38889.4931 | 1 | 0 | 4
38889.4936 | 1 | 0 | 4
38889.494 | 1 | 0 | 4
38889.4944 | 1 | 0 | 4
38889.4949 | 1 | 0 | 4
38889.4953 | 1 | 0 | 4
38889.4957 | 1 | 0 | 4
38889.4962 | 1 | 0 | 4
38889.4966 | 1 | 0 | 4
38889.497 | 1 | 0 | 4
38889.4975 | 1 | 0 | 4
38889.4979 | 1 | 0 | 4
38889.4984 | 1 | 0 | 4
38889.4988 | 1 | 0 | 4
38889.4992 | 1 | 0 | 4
38889.4997 | 1 | 0 | 4
38889.5001 | 1 | 0 | 4
38889.5005 | 1 | 0 | 4
38889.501 | 2 | 0 | 4
38889.5014 | 1 | 0 | 4
38889.5019 | 1 | 0 | 4
38889.5023 | 1 | 0 | 4
38889.5027 | 1 | 0 | 4
38889.5032 | 1 | 0 | 4
38889.5036 | 1 | 0 | 4
38889.5041 | 1 | 0 | 4
38889.5045 | 1 | 0 | 4
38889.5049 | 1 | 0 | 4
38889.5054 | 1 | 0 | 4
38889.5058 | 1 | 0 | 4
38889.5062 | 1 | 0 | 4
38889.5067 | 1 | 0 | 4
38889.5071 | 1 | 0 | 4
38889.5075 | 2 | 0 | 4
38889.508 | 1 | 0 | 4
38889.5084 | 1 | 0 | 4
38889.5089 | 1 | 0 | 4
38889.5097 | 1 | 0 | 4
38889.5102 | 2 | 0 | 4
38889.5106 | 1 | 0 | 4
38889.511 | 2 | 0 | 4
38889.5115 | 1 | 0 | 4
38889.5119 | 1 | 0 | 4
38889.5124 | 1 | 0 | 4
38889.5128 | 1 | 0 | 4
38889.5132 | 1 | 0 | 4
38889.4874 | 1 | 0 | 5
38889.4879 | 1 | 0 | 5
38889.4883 | 1 | 0 | 5
38889.4887 | 1 | 0 | 5
38889.4892 | 1 | 0 | 5
38889.4896 | 1 | 0 | 5
38889.4901 | 1 | 0 | 5
38889.4905 | 1 | 0 | 5
38889.4909 | 1 | 0 | 5
38889.4914 | 1 | 0 | 5
38889.4918 | 1 | 0 | 5
38889.4922 | 1 | 0 | 5
38889.4927 | 1 | 0 | 5
38889.4931 | 1 | 0 | 5
38889.4936 | 1 | 0 | 5
38889.494 | 1 | 0 | 5
38889.4944 | 1 | 0 | 5
38889.4949 | 1 | 0 | 5
38889.4953 | 1 | 0 | 5
38889.4957 | 1 | 0 | 5
38889.4962 | 1 | 0 | 5
38889.4966 | 1 | 0 | 5
38889.4971 | 1 | 0 | 5
38889.4975 | 1 | 0 | 5
38889.4979 | 1 | 0 | 5
38889.4984 | 1 | 0 | 5
38889.4988 | 1 | 0 | 5
38889.4992 | 1 | 0 | 5
38889.4997 | 1 | 0 | 5
38889.5001 | 1 | 0 | 5
38889.5006 | 1 | 0 | 5
38889.501 | 1 | 0 | 5
38889.5014 | 1 | 0 | 5
38889.5019 | 1 | 0 | 5
38889.5023 | 1 | 0 | 5
38889.5027 | 1 | 0 | 5
38889.5032 | 1 | 0 | 5
38889.5036 | 1 | 0 | 5
38889.5041 | 1 | 0 | 5
38889.5045 | 1 | 0 | 5
38889.5049 | 1 | 0 | 5
38889.5058 | 1 | 0 | 5
38889.5062 | 1 | 0 | 5
38889.5067 | 1 | 0 | 5
38889.5071 | 1 | 0 | 5
38889.5076 | 1201 | 1018 | 5
38889.508 | 4 | 3 | 5
38889.5084 | 1 | 0 | 5
38889.5089 | 1 | 0 | 5
38889.5097 | 1 | 0 | 5
38889.5102 | 1 | 0 | 5
38889.5106 | 1 | 0 | 5
38889.5111 | 2 | 0 | 5
38889.5115 | 1 | 0 | 5
38889.5119 | 1 | 0 | 5
38889.5124 | 1 | 0 | 5
38889.5128 | 1 | 0 | 5
38889.5132 | 2 | 0 | 5
38889.4874 | 1 | 0 | 6
38889.4879 | 1 | 0 | 6
38889.4883 | 1 | 0 | 6
38889.4888 | 1 | 0 | 6
38889.4892 | 2 | 0 | 6
38889.4896 | 1 | 0 | 6
38889.4901 | 1 | 0 | 6
38889.4905 | 1 | 0 | 6
38889.4909 | 1 | 0 | 6
38889.4914 | 1 | 0 | 6
38889.4918 | 1 | 0 | 6
38889.4923 | 1 | 0 | 6
38889.4927 | 1 | 0 | 6
38889.4931 | 1 | 0 | 6
38889.4936 | 1 | 0 | 6
38889.494 | 1 | 0 | 6
38889.4944 | 1 | 0 | 6
38889.4949 | 1 | 0 | 6
38889.4953 | 1 | 0 | 6
38889.4958 | 1 | 0 | 6
38889.4962 | 2 | 0 | 6
38889.4966 | 1 | 0 | 6
38889.4971 | 1 | 0 | 6
38889.4975 | 1 | 0 | 6
38889.4979 | 1 | 0 | 6
38889.4984 | 1 | 0 | 6
38889.4988 | 1 | 0 | 6
38889.4993 | 1 | 0 | 6
38889.4997 | 1 | 0 | 6
38889.5001 | 1 | 0 | 6
38889.5006 | 1 | 0 | 6
38889.501 | 1 | 0 | 6
38889.5014 | 1 | 0 | 6
38889.5019 | 1 | 0 | 6
38889.5023 | 1 | 0 | 6
38889.5028 | 1 | 0 | 6
38889.5032 | 1 | 0 | 6
38889.5036 | 1 | 0 | 6
38889.5041 | 1 | 0 | 6
38889.5045 | 1 | 0 | 6
38889.5049 | 1 | 0 | 6
38889.5054 | 1 | 0 | 6
38889.5058 | 1 | 0 | 6
38889.5063 | 2 | 0 | 6
38889.5067 | 1 | 0 | 6
38889.5071 | 1 | 0 | 6
38889.5076 | 1038 | 1013 | 6
38889.508 | 19 | 17 | 6
38889.5084 | 1 | 0 | 6
38889.5089 | 1 | 0 | 6
38889.5098 | 1 | 0 | 6
38889.5102 | 1 | 0 | 6
38889.5106 | 1 | 0 | 6
38889.5111 | 1 | 0 | 6
38889.5115 | 1 | 0 | 6
38889.5119 | 1 | 0 | 6
38889.5124 | 1 | 0 | 6
38889.5128 | 1 | 0 | 6
38889.5133 | 1 | 0 | 6
38889.4875 | 1 | 0 | 7
38889.4879 | 1 | 0 | 7
38889.4883 | 1 | 0 | 7
38889.4888 | 1 | 0 | 7
38889.4892 | 1 | 0 | 7
38889.4896 | 1 | 0 | 7
38889.4901 | 1 | 0 | 7
38889.4905 | 1 | 0 | 7
38889.491 | 1 | 0 | 7
38889.4914 | 1 | 0 | 7
38889.4918 | 1 | 0 | 7
38889.4923 | 1 | 0 | 7
38889.4927 | 1 | 0 | 7
38889.4931 | 1 | 0 | 7
38889.4936 | 1 | 0 | 7
38889.494 | 1 | 0 | 7
38889.4945 | 1 | 0 | 7
38889.4949 | 1 | 0 | 7
38889.4953 | 1 | 0 | 7
38889.4958 | 1 | 0 | 7
38889.4962 | 1 | 0 | 7
38889.4966 | 1 | 0 | 7
38889.4971 | 1 | 0 | 7
38889.4975 | 1 | 0 | 7
38889.498 | 1 | 0 | 7
38889.4984 | 1 | 0 | 7
38889.4988 | 1 | 0 | 7
38889.4993 | 1 | 0 | 7
38889.4997 | 1 | 0 | 7
38889.5001 | 1 | 0 | 7
38889.5006 | 1 | 0 | 7
38889.501 | 1 | 0 | 7
38889.5015 | 1 | 0 | 7
38889.5019 | 1 | 0 | 7
38889.5023 | 1 | 0 | 7
38889.5028 | 1 | 0 | 7
38889.5032 | 1 | 0 | 7
38889.5036 | 1 | 0 | 7
38889.5041 | 1 | 0 | 7
38889.5045 | 1 | 0 | 7
38889.505 | 1 | 0 | 7
38889.5054 | 1 | 0 | 7
38889.5058 | 1 | 0 | 7
38889.5063 | 1 | 0 | 7
38889.5067 | 1 | 0 | 7
38889.5071 | 1 | 0 | 7
38889.5076 | 1 | 1 | 7
38889.508 | 1 | 0 | 7
38889.5084 | 1 | 0 | 7
38889.5089 | 1 | 0 | 7
38889.5098 | 1 | 0 | 7
38889.5102 | 1 | 0 | 7
38889.5106 | 1 | 0 | 7
38889.5111 | 1 | 0 | 7
38889.5115 | 1 | 0 | 7
38889.512 | 1 | 0 | 7
38889.5124 | 2 | 0 | 7
38889.5128 | 1 | 0 | 7
38889.5133 | 1 | 0 | 7
38889.4875 | 1 | 0 | 8
38889.4879 | 1 | 0 | 8
38889.4883 | 1 | 0 | 8
38889.4888 | 1 | 0 | 8
38889.4892 | 1 | 0 | 8
38889.4897 | 1 | 0 | 8
38889.4901 | 1 | 0 | 8
38889.4905 | 1 | 0 | 8
38889.491 | 1 | 0 | 8
38889.4914 | 1 | 0 | 8
38889.4918 | 1 | 0 | 8
38889.4923 | 1 | 0 | 8
38889.4927 | 1 | 0 | 8
38889.4932 | 1 | 0 | 8
38889.4936 | 1 | 0 | 8
38889.494 | 1 | 0 | 8
38889.4945 | 1 | 0 | 8
38889.4949 | 1 | 0 | 8
38889.4953 | 1 | 0 | 8
38889.4958 | 1 | 0 | 8
38889.4962 | 1 | 0 | 8
38889.4967 | 1 | 0 | 8
38889.4971 | 1 | 0 | 8
38889.4975 | 1 | 0 | 8
38889.498 | 1 | 0 | 8
38889.4984 | 1 | 0 | 8
38889.4988 | 1 | 0 | 8
38889.4993 | 1 | 0 | 8
38889.4997 | 1 | 0 | 8
38889.5002 | 1 | 0 | 8
38889.5006 | 1 | 0 | 8
38889.501 | 1 | 0 | 8
38889.5015 | 1 | 0 | 8
38889.5019 | 1 | 0 | 8
38889.5023 | 1 | 0 | 8
38889.5028 | 1 | 0 | 8
38889.5032 | 1 | 0 | 8
38889.5037 | 1 | 0 | 8
38889.5041 | 1 | 0 | 8
38889.5045 | 1 | 0 | 8
38889.505 | 1 | 0 | 8
38889.5054 | 1 | 0 | 8
38889.5058 | 1 | 0 | 8
38889.5063 | 1 | 0 | 8
38889.5067 | 1 | 0 | 8
38889.5072 | 1 | 0 | 8
38889.5076 | 1 | 0 | 8
38889.508 | 1 | 0 | 8
38889.5085 | 1 | 0 | 8
38889.5089 | 1 | 0 | 8
38889.5098 | 1 | 0 | 8
38889.5102 | 1 | 0 | 8
38889.5106 | 1 | 0 | 8
38889.5111 | 1 | 0 | 8
38889.5115 | 1 | 0 | 8
38889.512 | 1 | 0 | 8
38889.5124 | 1 | 0 | 8
38889.5128 | 1 | 0 | 8
38889.5133 | 1 | 0 | 8
38889.4875 | 1 | 0 | 9
38889.4879 | 1 | 0 | 9
38889.4884 | 1 | 0 | 9
38889.4888 | 1 | 0 | 9
38889.4892 | 1 | 0 | 9
38889.4897 | 1 | 0 | 9
38889.4901 | 1 | 0 | 9
38889.4905 | 1 | 0 | 9
38889.491 | 1 | 0 | 9
38889.4914 | 1 | 0 | 9
38889.4919 | 1 | 0 | 9
38889.4923 | 1 | 0 | 9
38889.4927 | 1 | 0 | 9
38889.4932 | 1 | 0 | 9
38889.4936 | 1 | 0 | 9
38889.494 | 1 | 0 | 9
38889.4945 | 1 | 0 | 9
38889.4949 | 1 | 0 | 9
38889.4953 | 1 | 0 | 9
38889.4958 | 1 | 0 | 9
38889.4962 | 1 | 0 | 9
38889.4967 | 1 | 0 | 9
38889.4971 | 1 | 0 | 9
38889.4975 | 1 | 0 | 9
38889.498 | 1 | 0 | 9
38889.4984 | 1 | 0 | 9
38889.4989 | 1 | 0 | 9
38889.4993 | 1 | 0 | 9
38889.4997 | 1 | 0 | 9
38889.5002 | 1 | 0 | 9
38889.5006 | 1 | 0 | 9
38889.501 | 1 | 0 | 9
38889.5015 | 1 | 0 | 9
38889.5019 | 1 | 0 | 9
38889.5023 | 1 | 0 | 9
38889.5028 | 1 | 0 | 9
38889.5032 | 1 | 0 | 9
38889.5037 | 1 | 0 | 9
38889.5041 | 1 | 0 | 9
38889.5045 | 1 | 0 | 9
38889.505 | 1 | 0 | 9
38889.5054 | 1 | 0 | 9
38889.5058 | 1 | 0 | 9
38889.5063 | 1 | 0 | 9
38889.5067 | 1 | 0 | 9
38889.5072 | 1 | 0 | 9
38889.5076 | 1 | 0 | 9
38889.508 | 1 | 0 | 9
38889.5085 | 1 | 0 | 9
38889.5089 | 1 | 0 | 9
38889.5098 | 1 | 0 | 9
38889.5102 | 1 | 0 | 9
38889.5107 | 1 | 0 | 9
38889.5111 | 1 | 0 | 9
38889.5115 | 1 | 0 | 9
38889.512 | 1 | 0 | 9
38889.5124 | 1 | 0 | 9
38889.5128 | 1 | 0 | 9
38889.5133 | 1 | 0 | 9
38889.4875 | 1 | 0 | 10
38889.4879 | 1 | 0 | 10
38889.4884 | 1 | 0 | 10
38889.4888 | 1 | 0 | 10
38889.4892 | 1 | 0 | 10
38889.4897 | 1 | 0 | 10
38889.4901 | 1 | 0 | 10
38889.4906 | 1 | 0 | 10
38889.491 | 1 | 0 | 10
38889.4914 | 1 | 0 | 10
38889.4919 | 1 | 0 | 10
38889.4923 | 1 | 0 | 10
38889.4927 | 1 | 0 | 10
38889.4932 | 1 | 0 | 10
38889.4936 | 1 | 0 | 10
38889.4941 | 1 | 0 | 10
38889.4945 | 1 | 0 | 10
38889.4949 | 1 | 0 | 10
38889.4954 | 1 | 0 | 10
38889.4958 | 1 | 0 | 10
38889.4962 | 1 | 0 | 10
38889.4967 | 1 | 0 | 10
38889.4971 | 1 | 0 | 10
38889.4975 | 1 | 0 | 10
38889.498 | 1 | 0 | 10
38889.4984 | 1 | 0 | 10
38889.4989 | 1 | 0 | 10
38889.4993 | 1 | 0 | 10
38889.4997 | 1 | 0 | 10
38889.5002 | 1 | 0 | 10
38889.5006 | 1 | 0 | 10
38889.501 | 1 | 0 | 10
38889.5015 | 1 | 0 | 10
38889.5019 | 1 | 0 | 10
38889.5024 | 1 | 0 | 10
38889.5028 | 1 | 1 | 10
38889.5032 | 1 | 0 | 10
38889.5037 | 1 | 0 | 10
38889.5041 | 1 | 0 | 10
38889.5045 | 1 | 0 | 10
38889.505 | 1 | 0 | 10
38889.5054 | 1 | 0 | 10
38889.5059 | 1 | 0 | 10
38889.5063 | 1 | 0 | 10
38889.5067 | 1 | 0 | 10
38889.5072 | 1 | 0 | 10
38889.5076 | 1 | 0 | 10
38889.508 | 1 | 0 | 10
38889.5085 | 1 | 0 | 10
38889.5089 | 1 | 0 | 10
38889.5098 | 1 | 0 | 10
38889.5102 | 1 | 0 | 10
38889.5107 | 1 | 0 | 10
38889.5111 | 1 | 0 | 10
38889.5116 | 1 | 0 | 10
38889.512 | 1 | 0 | 10
38889.5124 | 1 | 0 | 10
38889.5129 | 1 | 0 | 10
38889.5133 | 1 | 0 | 10
38889.4875 | 1 | 0 | 11
38889.4879 | 1 | 0 | 11
38889.4884 | 1 | 0 | 11
38889.4888 | 1 | 0 | 11
38889.4892 | 1 | 0 | 11
38889.4897 | 1 | 0 | 11
38889.4901 | 1 | 0 | 11
38889.4906 | 1 | 0 | 11
38889.491 | 1 | 0 | 11
38889.4914 | 1 | 0 | 11
38889.4919 | 1 | 0 | 11
38889.4923 | 1 | 0 | 11
38889.4927 | 1 | 0 | 11
38889.4932 | 1 | 0 | 11
38889.4936 | 1 | 0 | 11
38889.4941 | 1 | 0 | 11
38889.4945 | 1 | 0 | 11
38889.4949 | 1 | 0 | 11
38889.4954 | 1 | 0 | 11
38889.4958 | 1 | 0 | 11
38889.4962 | 1 | 0 | 11
38889.4967 | 1 | 0 | 11
38889.4971 | 1 | 0 | 11
38889.4976 | 1 | 0 | 11
38889.498 | 1 | 0 | 11
38889.4984 | 1 | 0 | 11
38889.4989 | 1 | 0 | 11
38889.4993 | 1 | 0 | 11
38889.4997 | 1 | 0 | 11
38889.5002 | 1 | 0 | 11
38889.5006 | 1 | 0 | 11
38889.5011 | 1 | 0 | 11
38889.5015 | 2 | 0 | 11
38889.5019 | 1 | 0 | 11
38889.5024 | 1 | 0 | 11
38889.5028 | 1 | 0 | 11
38889.5032 | 1 | 0 | 11
38889.5037 | 1 | 0 | 11
38889.5041 | 1 | 0 | 11
38889.5046 | 1 | 0 | 11
38889.505 | 1 | 0 | 11
38889.5054 | 1 | 0 | 11
38889.5059 | 1 | 0 | 11
38889.5063 | 1 | 0 | 11
38889.5067 | 1 | 0 | 11
38889.5072 | 1 | 0 | 11
38889.5076 | 1 | 0 | 11
38889.5081 | 1 | 0 | 11
38889.5085 | 1 | 0 | 11
38889.5089 | 1 | 0 | 11
38889.5098 | 1 | 0 | 11
38889.5102 | 1 | 0 | 11
38889.5107 | 1 | 0 | 11
38889.5111 | 1 | 0 | 11
38889.5116 | 1 | 0 | 11
38889.512 | 1 | 0 | 11
38889.5124 | 1 | 0 | 11
38889.5129 | 1 | 0 | 11
38889.5133 | 1 | 0 | 11
38889.4875 | 1 | 0 | 12
38889.488 | 1 | 0 | 12
38889.4884 | 1 | 0 | 12
38889.4888 | 1 | 0 | 12
38889.4893 | 1 | 0 | 12
38889.4897 | 1 | 0 | 12
38889.4901 | 1 | 0 | 12
38889.4906 | 1 | 0 | 12
38889.491 | 1 | 0 | 12
38889.4914 | 1 | 0 | 12
38889.4919 | 1 | 0 | 12
38889.4923 | 1 | 0 | 12
38889.4928 | 1 | 0 | 12
38889.4932 | 1 | 0 | 12
38889.4936 | 1 | 0 | 12
38889.4941 | 1 | 0 | 12
38889.4945 | 1 | 0 | 12
38889.4949 | 1 | 0 | 12
38889.4954 | 1 | 0 | 12
38889.4958 | 1 | 0 | 12
38889.4963 | 1 | 0 | 12
38889.4967 | 1 | 0 | 12
38889.4971 | 1 | 0 | 12
38889.4976 | 2 | 0 | 12
38889.498 | 1 | 0 | 12
38889.4984 | 2 | 0 | 12
38889.4989 | 1999 | 0 | 12
38889.4993 | 2071 | 0 | 12
38889.4998 | 2317 | 0 | 12
38889.5002 | 2019 | 0 | 12
38889.5006 | 2563 | 0 | 12
38889.5011 | 2483 | 0 | 12
38889.5015 | 2054 | 0 | 12
38889.5019 | 2261 | 0 | 12
38889.5024 | 2529 | 0 | 12
38889.5028 | 2575 | 0 | 12
38889.5033 | 2093 | 0 | 12
38889.5037 | 2154 | 0 | 12
38889.5041 | 2167 | 0 | 12
38889.5046 | 2560 | 0 | 12
38889.505 | 2230 | 0 | 12
38889.5054 | 2262 | 0 | 12
38889.5059 | 2008 | 0 | 12
38889.5063 | 2219 | 0 | 12
38889.5068 | 2177 | 0 | 12
38889.5072 | 2160 | 0 | 12
38889.5076 | 2112 | 0 | 12
38889.5081 | 2412 | 0 | 12
38889.5085 | 2091 | 0 | 12
38889.5089 | 2140 | 0 | 12
38889.5098 | 2528 | 0 | 12
38889.5103 | 2082 | 0 | 12
38889.5107 | 2437 | 0 | 12
38889.5111 | 2203 | 0 | 12
38889.5116 | 2030 | 0 | 12
38889.512 | 2221 | 0 | 12
38889.5124 | 2527 | 0 | 12
38889.5129 | 1930 | 0 | 12
38889.5133 | 2027 | 0 | 12
38889.4875 | 1 | 0 | 13
38889.488 | 1 | 0 | 13
38889.4884 | 1 | 0 | 13
38889.4888 | 1 | 0 | 13
38889.4893 | 1 | 0 | 13
38889.4897 | 1 | 0 | 13
38889.4901 | 1 | 0 | 13
38889.4906 | 1 | 0 | 13
38889.491 | 1 | 0 | 13
38889.4915 | 1 | 0 | 13
38889.4919 | 1 | 0 | 13
38889.4923 | 1 | 0 | 13
38889.4928 | 1 | 0 | 13
38889.4932 | 1 | 0 | 13
38889.4936 | 1 | 0 | 13
38889.4941 | 1 | 0 | 13
38889.4945 | 2 | 0 | 13
38889.495 | 1 | 0 | 13
38889.4954 | 1 | 0 | 13
38889.4958 | 1 | 0 | 13
38889.4963 | 1 | 0 | 13
38889.4967 | 1 | 0 | 13
38889.4971 | 1 | 0 | 13
38889.4976 | 1 | 0 | 13
38889.498 | 1 | 0 | 13
38889.4984 | 1 | 0 | 13
38889.4989 | 1 | 0 | 13
38889.4993 | 2 | 0 | 13
38889.4998 | 2 | 0 | 13
38889.5002 | 2 | 0 | 13
38889.5006 | 1 | 0 | 13
38889.5011 | 2 | 0 | 13
38889.5015 | 2 | 0 | 13
38889.502 | 1 | 0 | 13
38889.5024 | 2 | 0 | 13
38889.5028 | 2 | 0 | 13
38889.5033 | 1 | 0 | 13
38889.5037 | 1 | 0 | 13
38889.5041 | 2 | 0 | 13
38889.5046 | 1 | 0 | 13
38889.505 | 2 | 0 | 13
38889.5055 | 2 | 0 | 13
38889.5059 | 1 | 0 | 13
38889.5063 | 2 | 0 | 13
38889.5068 | 2 | 0 | 13
38889.5072 | 2 | 0 | 13
38889.5076 | 2 | 0 | 13
38889.5081 | 1 | 0 | 13
38889.5085 | 2 | 0 | 13
38889.509 | 2 | 0 | 13
38889.5098 | 2 | 0 | 13
38889.5103 | 1 | 0 | 13
38889.5107 | 2 | 0 | 13
38889.5111 | 2 | 0 | 13
38889.5116 | 1 | 0 | 13
38889.512 | 2 | 0 | 13
38889.5125 | 2 | 0 | 13
38889.5129 | 1 | 0 | 13
38889.5133 | 2 | 0 | 13
38889.4875 | 1 | 0 | 14
38889.488 | 1 | 0 | 14
38889.4884 | 1 | 0 | 14
38889.4888 | 1 | 0 | 14
38889.4893 | 1 | 0 | 14
38889.4897 | 1 | 0 | 14
38889.4902 | 1 | 0 | 14
38889.4906 | 1 | 0 | 14
38889.491 | 1 | 0 | 14
38889.4915 | 1 | 0 | 14
38889.4919 | 1 | 0 | 14
38889.4923 | 1 | 0 | 14
38889.4928 | 1 | 0 | 14
38889.4932 | 1 | 0 | 14
38889.4937 | 1 | 0 | 14
38889.4941 | 1 | 0 | 14
38889.4945 | 1 | 0 | 14
38889.495 | 1 | 0 | 14
38889.4954 | 1 | 0 | 14
38889.4958 | 1 | 0 | 14
38889.4963 | 1 | 0 | 14
38889.4967 | 1 | 0 | 14
38889.4972 | 1 | 0 | 14
38889.4976 | 1 | 0 | 14
38889.498 | 1 | 0 | 14
38889.4985 | 1 | 0 | 14
38889.4989 | 1 | 0 | 14
38889.4993 | 1 | 0 | 14
38889.4998 | 1 | 0 | 14
38889.5002 | 1 | 0 | 14
38889.5006 | 1 | 0 | 14
38889.5011 | 1 | 0 | 14
38889.5015 | 1 | 0 | 14
38889.502 | 1 | 0 | 14
38889.5024 | 1 | 0 | 14
38889.5028 | 1 | 0 | 14
38889.5033 | 1 | 0 | 14
38889.5037 | 2 | 0 | 14
38889.5042 | 1 | 0 | 14
38889.5046 | 1 | 0 | 14
38889.505 | 1 | 0 | 14
38889.5055 | 1 | 0 | 14
38889.5059 | 1 | 0 | 14
38889.5063 | 1 | 0 | 14
38889.5068 | 1 | 0 | 14
38889.5072 | 1 | 0 | 14
38889.5077 | 1 | 0 | 14
38889.5081 | 1 | 0 | 14
38889.5085 | 1 | 0 | 14
38889.509 | 1 | 0 | 14
38889.5098 | 1 | 0 | 14
38889.5103 | 1 | 0 | 14
38889.5107 | 1 | 0 | 14
38889.5111 | 1 | 0 | 14
38889.5116 | 1 | 0 | 14
38889.512 | 1 | 0 | 14
38889.5125 | 1 | 0 | 14
38889.5129 | 1 | 0 | 14
38889.5133 | 1 | 0 | 14
38889.4875 | 1 | 0 | 15
38889.488 | 1 | 0 | 15
38889.4884 | 1 | 0 | 15
38889.4889 | 1 | 0 | 15
38889.4893 | 1 | 0 | 15
38889.4897 | 1 | 0 | 15
38889.4902 | 1 | 0 | 15
38889.4906 | 1 | 0 | 15
38889.491 | 1 | 0 | 15
38889.4915 | 1 | 0 | 15
38889.4919 | 1 | 0 | 15
38889.4923 | 1 | 0 | 15
38889.4928 | 1 | 0 | 15
38889.4932 | 1 | 0 | 15
38889.4937 | 1 | 0 | 15
38889.4941 | 1 | 0 | 15
38889.4945 | 1 | 0 | 15
38889.495 | 1 | 0 | 15
38889.4954 | 1 | 0 | 15
38889.4959 | 1 | 0 | 15
38889.4963 | 1 | 0 | 15
38889.4967 | 1 | 0 | 15
38889.4972 | 1 | 0 | 15
38889.4976 | 1 | 0 | 15
38889.498 | 1 | 0 | 15
38889.4985 | 1 | 0 | 15
38889.4989 | 1 | 0 | 15
38889.4994 | 1 | 0 | 15
38889.4998 | 1 | 0 | 15
38889.5002 | 1 | 0 | 15
38889.5007 | 1 | 0 | 15
38889.5011 | 1 | 0 | 15
38889.5015 | 1 | 0 | 15
38889.502 | 1 | 0 | 15
38889.5024 | 1 | 0 | 15
38889.5028 | 1 | 0 | 15
38889.5037 | 1 | 0 | 15
38889.5042 | 1 | 0 | 15
38889.5046 | 1 | 0 | 15
38889.505 | 1 | 0 | 15
38889.5055 | 1 | 0 | 15
38889.5059 | 1 | 0 | 15
38889.5064 | 1 | 0 | 15
38889.5068 | 1 | 0 | 15
38889.5072 | 1089 | 1153 | 15
38889.5077 | 989 | 961 | 15
38889.5081 | 1 | 0 | 15
38889.5085 | 1 | 0 | 15
38889.509 | 1 | 0 | 15
38889.5098 | 1 | 0 | 15
38889.5103 | 1 | 0 | 15
38889.5107 | 1 | 0 | 15
38889.5112 | 1 | 0 | 15
38889.5116 | 1 | 0 | 15
38889.512 | 1 | 0 | 15
38889.5125 | 1 | 0 | 15
38889.5129 | 1 | 0 | 15
38889.5133 | 1 | 0 | 15
38889.4875 | 1 | 0 | 16
38889.488 | 1 | 0 | 16
38889.4884 | 1 | 0 | 16
38889.4889 | 1 | 0 | 16
38889.4893 | 1 | 0 | 16
38889.4897 | 1 | 0 | 16
38889.4902 | 1 | 0 | 16
38889.4906 | 1 | 0 | 16
38889.4911 | 1 | 0 | 16
38889.4915 | 1 | 0 | 16
38889.4919 | 1 | 0 | 16
38889.4924 | 1 | 0 | 16
38889.4928 | 1 | 0 | 16
38889.4932 | 1 | 0 | 16
38889.4937 | 1 | 0 | 16
38889.4941 | 1 | 0 | 16
38889.4945 | 1 | 0 | 16
38889.495 | 1 | 0 | 16
38889.4954 | 1 | 0 | 16
38889.4959 | 1 | 0 | 16
38889.4963 | 1 | 0 | 16
38889.4967 | 1 | 0 | 16
38889.4972 | 1 | 0 | 16
38889.4976 | 1 | 0 | 16
38889.498 | 1 | 0 | 16
38889.4985 | 1 | 0 | 16
38889.4989 | 1 | 0 | 16
38889.4994 | 1 | 0 | 16
38889.4998 | 1 | 0 | 16
38889.5002 | 1 | 0 | 16
38889.5007 | 1 | 0 | 16
38889.5011 | 1 | 0 | 16
38889.5016 | 1 | 0 | 16
38889.502 | 1 | 0 | 16
38889.5024 | 1 | 0 | 16
38889.5029 | 1 | 0 | 16
38889.5033 | 1 | 0 | 16
38889.5037 | 1 | 0 | 16
38889.5042 | 1 | 0 | 16
38889.5046 | 1 | 0 | 16
38889.505 | 1 | 0 | 16
38889.5055 | 1 | 0 | 16
38889.5059 | 1 | 0 | 16
38889.5064 | 2 | 0 | 16
38889.5068 | 2 | 0 | 16
38889.5072 | 1004 | 1103 | 16
38889.5077 | 1130 | 1083 | 16
38889.5081 | 1 | 0 | 16
38889.5085 | 1 | 0 | 16
38889.509 | 1 | 0 | 16
38889.5099 | 1 | 0 | 16
38889.5103 | 1 | 0 | 16
38889.5107 | 1 | 0 | 16
38889.5112 | 1 | 0 | 16
38889.5116 | 1 | 0 | 16
38889.512 | 1 | 0 | 16
38889.5125 | 1 | 0 | 16
38889.5129 | 1 | 1 | 16
38889.5134 | 1 | 0 | 16
38889.4876 | 1 | 0 | 17
38889.488 | 1 | 0 | 17
38889.4884 | 1 | 0 | 17
38889.4889 | 1 | 0 | 17
38889.4893 | 1 | 0 | 17
38889.4897 | 1 | 0 | 17
38889.4902 | 1 | 0 | 17
38889.4906 | 1 | 0 | 17
38889.4911 | 1 | 0 | 17
38889.4915 | 1 | 0 | 17
38889.4919 | 1 | 0 | 17
38889.4924 | 1 | 0 | 17
38889.4928 | 1 | 0 | 17
38889.4933 | 1 | 0 | 17
38889.4937 | 1 | 0 | 17
38889.4941 | 1 | 0 | 17
38889.4946 | 1 | 0 | 17
38889.495 | 1 | 0 | 17
38889.4954 | 1 | 0 | 17
38889.4959 | 1 | 0 | 17
38889.4963 | 1 | 0 | 17
38889.4967 | 1 | 0 | 17
38889.4972 | 1 | 0 | 17
38889.4976 | 1 | 0 | 17
38889.4981 | 1 | 0 | 17
38889.4985 | 1 | 0 | 17
38889.4989 | 1 | 0 | 17
38889.4994 | 1 | 0 | 17
38889.4998 | 1 | 0 | 17
38889.5002 | 1 | 0 | 17
38889.5007 | 1 | 0 | 17
38889.5011 | 1 | 0 | 17
38889.5016 | 1 | 0 | 17
38889.502 | 1 | 0 | 17
38889.5024 | 1 | 0 | 17
38889.5029 | 1 | 0 | 17
38889.5033 | 1 | 0 | 17
38889.5038 | 2 | 0 | 17
38889.5042 | 1 | 0 | 17
38889.5046 | 1 | 0 | 17
38889.5051 | 1 | 0 | 17
38889.5055 | 1 | 0 | 17
38889.5059 | 1 | 0 | 17
38889.5064 | 1 | 0 | 17
38889.5068 | 1 | 0 | 17
38889.5072 | 1 | 1 | 17
38889.5077 | 1 | 1 | 17
38889.5081 | 1 | 0 | 17
38889.5086 | 1 | 0 | 17
38889.509 | 1 | 0 | 17
38889.5099 | 1 | 0 | 17
38889.5103 | 1 | 0 | 17
38889.5107 | 1 | 0 | 17
38889.5112 | 1 | 0 | 17
38889.5116 | 1 | 0 | 17
38889.5121 | 1 | 0 | 17
38889.5125 | 1 | 0 | 17
38889.5129 | 1 | 0 | 17
38889.5134 | 1 | 0 | 17
38889.4876 | 1 | 0 | 18
38889.4884 | 1 | 0 | 18
38889.4889 | 1 | 0 | 18
38889.4893 | 1 | 0 | 18
38889.4898 | 1 | 0 | 18
38889.4902 | 1 | 0 | 18
38889.4906 | 1 | 0 | 18
38889.4911 | 1 | 0 | 18
38889.4915 | 1 | 0 | 18
38889.4919 | 1 | 0 | 18
38889.4924 | 1 | 0 | 18
38889.4928 | 1 | 0 | 18
38889.4933 | 2 | 0 | 18
38889.4937 | 1 | 0 | 18
38889.4941 | 1 | 0 | 18
38889.4946 | 1 | 0 | 18
38889.495 | 1 | 0 | 18
38889.4954 | 1 | 0 | 18
38889.4959 | 1 | 0 | 18
38889.4963 | 1 | 0 | 18
38889.4968 | 1 | 0 | 18
38889.4972 | 1 | 0 | 18
38889.4976 | 2 | 0 | 18
38889.4981 | 1 | 0 | 18
38889.4985 | 1 | 0 | 18
38889.4989 | 1 | 0 | 18
38889.4994 | 1 | 0 | 18
38889.4998 | 1 | 0 | 18
38889.5003 | 1 | 0 | 18
38889.5007 | 1 | 0 | 18
38889.5011 | 1 | 0 | 18
38889.5016 | 1 | 0 | 18
38889.502 | 1 | 0 | 18
38889.5024 | 1 | 0 | 18
38889.5029 | 1 | 0 | 18
38889.5033 | 1 | 0 | 18
38889.5038 | 1 | 0 | 18
38889.5042 | 1 | 0 | 18
38889.5046 | 1 | 0 | 18
38889.5051 | 1 | 0 | 18
38889.5055 | 1 | 0 | 18
38889.5059 | 1 | 0 | 18
38889.5064 | 1 | 0 | 18
38889.5068 | 1 | 0 | 18
38889.5073 | 1 | 0 | 18
38889.5077 | 1 | 0 | 18
38889.5081 | 1 | 0 | 18
38889.5086 | 2 | 0 | 18
38889.509 | 1 | 0 | 18
38889.5099 | 1 | 0 | 18
38889.5103 | 1 | 0 | 18
38889.5108 | 1 | 0 | 18
38889.5112 | 1 | 0 | 18
38889.5116 | 1 | 0 | 18
38889.5121 | 1 | 0 | 18
38889.5125 | 1 | 0 | 18
38889.5129 | 1 | 0 | 18
38889.5134 | 1 | 0 | 18
38889.4876 | 1 | 0 | 19
38889.488 | 1 | 0 | 19
38889.4885 | 1 | 0 | 19
38889.4889 | 1 | 0 | 19
38889.4893 | 1 | 0 | 19
38889.4898 | 1 | 0 | 19
38889.4902 | 1 | 0 | 19
38889.4906 | 1 | 0 | 19
38889.4911 | 1 | 0 | 19
38889.4915 | 1 | 0 | 19
38889.492 | 1 | 0 | 19
38889.4924 | 1 | 0 | 19
38889.4928 | 1 | 0 | 19
38889.4933 | 1 | 0 | 19
38889.4937 | 1 | 0 | 19
38889.4941 | 1 | 0 | 19
38889.4946 | 1 | 0 | 19
38889.495 | 1 | 0 | 19
38889.4955 | 1 | 0 | 19
38889.4959 | 1 | 0 | 19
38889.4963 | 1 | 0 | 19
38889.4968 | 1 | 0 | 19
38889.4972 | 1 | 0 | 19
38889.4976 | 2 | 0 | 19
38889.4981 | 1 | 0 | 19
38889.4985 | 1 | 0 | 19
38889.499 | 1 | 0 | 19
38889.4994 | 1 | 0 | 19
38889.4998 | 1 | 0 | 19
38889.5003 | 1 | 0 | 19
38889.5007 | 2 | 0 | 19
38889.5011 | 1 | 0 | 19
38889.5016 | 1 | 0 | 19
38889.502 | 1 | 0 | 19
38889.5025 | 1 | 0 | 19
38889.5029 | 1 | 0 | 19
38889.5033 | 1 | 0 | 19
38889.5038 | 1 | 0 | 19
38889.5042 | 1 | 0 | 19
38889.5046 | 1 | 0 | 19
38889.5051 | 1 | 0 | 19
38889.5055 | 1 | 0 | 19
38889.5059 | 1 | 0 | 19
38889.5064 | 1 | 0 | 19
38889.5068 | 1 | 0 | 19
38889.5073 | 1 | 0 | 19
38889.5077 | 1 | 0 | 19
38889.5081 | 1 | 0 | 19
38889.5086 | 1 | 0 | 19
38889.509 | 1 | 0 | 19
38889.5099 | 1 | 0 | 19
38889.5103 | 1 | 0 | 19
38889.5108 | 1 | 0 | 19
38889.5112 | 1 | 0 | 19
38889.5116 | 1 | 0 | 19
38889.5121 | 1 | 0 | 19
38889.5125 | 1 | 0 | 19
38889.513 | 1 | 0 | 19
38889.5134 | 1 | 0 | 19
38889.4876 | 1 | 0 | 20
38889.488 | 1 | 0 | 20
38889.4885 | 1 | 0 | 20
38889.4889 | 1 | 0 | 20
38889.4893 | 1 | 0 | 20
38889.4898 | 1 | 0 | 20
38889.4902 | 1 | 0 | 20
38889.4907 | 1 | 0 | 20
38889.4911 | 1 | 0 | 20
38889.4915 | 1 | 0 | 20
38889.492 | 1 | 0 | 20
38889.4924 | 1 | 0 | 20
38889.4928 | 1 | 0 | 20
38889.4933 | 1 | 0 | 20
38889.4937 | 2 | 0 | 20
38889.4942 | 1 | 0 | 20
38889.4946 | 1 | 0 | 20
38889.495 | 1 | 0 | 20
38889.4955 | 1 | 0 | 20
38889.4959 | 1 | 0 | 20
38889.4963 | 1 | 0 | 20
38889.4968 | 1 | 0 | 20
38889.4972 | 1 | 0 | 20
38889.4977 | 1 | 0 | 20
38889.4981 | 1 | 0 | 20
38889.4985 | 2 | 0 | 20
38889.499 | 1 | 0 | 20
38889.4994 | 1 | 0 | 20
38889.4998 | 1 | 0 | 20
38889.5003 | 1 | 0 | 20
38889.5007 | 1 | 0 | 20
38889.5011 | 1 | 0 | 20
38889.5016 | 1 | 0 | 20
38889.502 | 1 | 0 | 20
38889.5025 | 1 | 0 | 20
38889.5029 | 1 | 0 | 20
38889.5033 | 1 | 0 | 20
38889.5038 | 1 | 0 | 20
38889.5042 | 1 | 0 | 20
38889.5047 | 1 | 0 | 20
38889.5051 | 1 | 0 | 20
38889.5055 | 1 | 0 | 20
38889.506 | 1 | 0 | 20
38889.5064 | 1 | 0 | 20
38889.5068 | 1 | 0 | 20
38889.5073 | 1 | 0 | 20
38889.5077 | 1 | 0 | 20
38889.5081 | 1 | 0 | 20
38889.5086 | 1 | 0 | 20
38889.509 | 1 | 0 | 20
38889.5099 | 1 | 0 | 20
38889.5103 | 1 | 0 | 20
38889.5108 | 1 | 0 | 20
38889.5112 | 1 | 0 | 20
38889.5117 | 1 | 0 | 20
38889.5121 | 1 | 0 | 20
38889.5125 | 1 | 0 | 20
38889.513 | 1 | 0 | 20
38889.5134 | 1 | 0 | 20
38889.4876 | 1 | 0 | 21
38889.488 | 1 | 0 | 21
38889.4885 | 2 | 0 | 21
38889.4889 | 1 | 0 | 21
38889.4894 | 1 | 0 | 21
38889.4898 | 1 | 0 | 21
38889.4902 | 1 | 0 | 21
38889.4907 | 1 | 0 | 21
38889.4911 | 1 | 0 | 21
38889.4915 | 1 | 0 | 21
38889.492 | 1 | 0 | 21
38889.4924 | 1 | 0 | 21
38889.4928 | 1 | 0 | 21
38889.4933 | 1 | 0 | 21
38889.4937 | 1 | 0 | 21
38889.4942 | 1 | 0 | 21
38889.4946 | 1 | 0 | 21
38889.495 | 1 | 0 | 21
38889.4955 | 1 | 0 | 21
38889.4959 | 1 | 0 | 21
38889.4964 | 1 | 0 | 21
38889.4968 | 1 | 0 | 21
38889.4972 | 1 | 0 | 21
38889.4977 | 1 | 0 | 21
38889.4981 | 1 | 0 | 21
38889.4985 | 1 | 0 | 21
38889.499 | 1 | 0 | 21
38889.4994 | 1 | 0 | 21
38889.4998 | 2 | 0 | 21
38889.5003 | 1 | 0 | 21
38889.5007 | 1 | 0 | 21
38889.5012 | 1 | 0 | 21
38889.5016 | 1 | 0 | 21
38889.502 | 1 | 0 | 21
38889.5025 | 1 | 0 | 21
38889.5029 | 1 | 0 | 21
38889.5033 | 1 | 1 | 21
38889.5038 | 1 | 0 | 21
38889.5042 | 1 | 0 | 21
38889.5047 | 1 | 0 | 21
38889.5051 | 1 | 0 | 21
38889.5055 | 1 | 0 | 21
38889.506 | 1 | 0 | 21
38889.5064 | 1 | 0 | 21
38889.5069 | 1 | 0 | 21
38889.5073 | 1 | 0 | 21
38889.5077 | 1 | 0 | 21
38889.5082 | 1 | 0 | 21
38889.5086 | 1 | 0 | 21
38889.509 | 1 | 0 | 21
38889.5099 | 1 | 0 | 21
38889.5103 | 1 | 0 | 21
38889.5108 | 1 | 0 | 21
38889.5112 | 1 | 0 | 21
38889.5117 | 1 | 0 | 21
38889.5121 | 1 | 0 | 21
38889.5125 | 1 | 0 | 21
38889.513 | 1 | 0 | 21
38889.5134 | 1 | 0 | 21
38889.4876 | 1 | 0 | 22
38889.4881 | 1 | 0 | 22
38889.4885 | 1 | 0 | 22
38889.4889 | 1 | 0 | 22
38889.4894 | 1 | 0 | 22
38889.4898 | 1 | 0 | 22
38889.4902 | 1 | 0 | 22
38889.4907 | 1 | 0 | 22
38889.4911 | 1 | 0 | 22
38889.4916 | 1 | 0 | 22
38889.492 | 1 | 0 | 22
38889.4924 | 1 | 0 | 22
38889.4929 | 1 | 0 | 22
38889.4933 | 1 | 0 | 22
38889.4937 | 1 | 0 | 22
38889.4942 | 1 | 0 | 22
38889.4946 | 1 | 0 | 22
38889.495 | 1 | 0 | 22
38889.4955 | 1 | 1 | 22
38889.4959 | 1 | 0 | 22
38889.4964 | 1 | 0 | 22
38889.4968 | 1 | 0 | 22
38889.4972 | 1 | 0 | 22
38889.4977 | 1 | 0 | 22
38889.4981 | 1 | 0 | 22
38889.4986 | 1 | 0 | 22
38889.499 | 2220 | 0 | 22
38889.4994 | 2044 | 1 | 22
38889.4999 | 2429 | 0 | 22
38889.5003 | 2193 | 0 | 22
38889.5007 | 2367 | 0 | 22
38889.5012 | 2298 | 0 | 22
38889.5016 | 2125 | 0 | 22
38889.502 | 2396 | 0 | 22
38889.5025 | 2455 | 0 | 22
38889.5029 | 2018 | 0 | 22
38889.5034 | 1991 | 0 | 22
38889.5038 | 2171 | 0 | 22
38889.5042 | 2311 | 0 | 22
38889.5047 | 2235 | 0 | 22
38889.5051 | 1985 | 0 | 22
38889.5055 | 2566 | 0 | 22
38889.506 | 2219 | 0 | 22
38889.5064 | 2105 | 0 | 22
38889.5069 | 2448 | 0 | 22
38889.5073 | 2418 | 0 | 22
38889.5077 | 1988 | 0 | 22
38889.5082 | 2324 | 0 | 22
38889.5086 | 2228 | 0 | 22
38889.5091 | 1983 | 0 | 22
38889.5099 | 2299 | 0 | 22
38889.5104 | 2054 | 0 | 22
38889.5108 | 2514 | 0 | 22
38889.5112 | 1961 | 0 | 22
38889.5117 | 2329 | 0 | 22
38889.5121 | 2118 | 0 | 22
38889.5125 | 2008 | 0 | 22
38889.513 | 1857 | 0 | 22
38889.5134 | 2207 | 0 | 22
38889.4876 | 1 | 0 | 23
38889.4881 | 1 | 0 | 23
38889.4885 | 1 | 0 | 23
38889.4889 | 1 | 0 | 23
38889.4894 | 1 | 0 | 23
38889.4898 | 1 | 0 | 23
38889.4902 | 1 | 0 | 23
38889.4907 | 1 | 0 | 23
38889.4911 | 1 | 0 | 23
38889.4916 | 1 | 0 | 23
38889.492 | 1 | 0 | 23
38889.4924 | 1 | 0 | 23
38889.4929 | 1 | 0 | 23
38889.4933 | 1 | 0 | 23
38889.4938 | 1 | 0 | 23
38889.4942 | 1 | 0 | 23
38889.4946 | 1 | 0 | 23
38889.4951 | 1 | 0 | 23
38889.4955 | 1 | 0 | 23
38889.4959 | 1 | 0 | 23
38889.4964 | 1 | 0 | 23
38889.4968 | 1 | 0 | 23
38889.4972 | 1 | 0 | 23
38889.4977 | 1 | 0 | 23
38889.4981 | 1 | 0 | 23
38889.4986 | 1 | 0 | 23
38889.499 | 1 | 0 | 23
38889.4994 | 2 | 0 | 23
38889.4999 | 2 | 0 | 23
38889.5003 | 2 | 0 | 23
38889.5008 | 2 | 0 | 23
38889.5012 | 2 | 0 | 23
38889.5016 | 2 | 0 | 23
38889.5021 | 2 | 0 | 23
38889.5025 | 2 | 0 | 23
38889.5029 | 2 | 0 | 23
38889.5034 | 2 | 0 | 23
38889.5038 | 2 | 0 | 23
38889.5042 | 1 | 0 | 23
38889.5047 | 1 | 0 | 23
38889.5051 | 1 | 0 | 23
38889.5056 | 1 | 0 | 23
38889.506 | 2 | 0 | 23
38889.5064 | 2 | 0 | 23
38889.5069 | 2 | 0 | 23
38889.5073 | 2 | 0 | 23
38889.5077 | 2 | 0 | 23
38889.5082 | 2 | 0 | 23
38889.5086 | 1 | 0 | 23
38889.5091 | 1 | 0 | 23
38889.5099 | 2 | 0 | 23
38889.5104 | 2 | 0 | 23
38889.5108 | 2 | 0 | 23
38889.5112 | 2 | 0 | 23
38889.5117 | 2 | 0 | 23
38889.5121 | 1 | 0 | 23
38889.5126 | 1 | 0 | 23
38889.513 | 2 | 0 | 23
38889.5134 | 2 | 0 | 23
38889.4876 | 1 | 0 | 24
38889.4881 | 1 | 0 | 24
38889.4885 | 1 | 0 | 24
38889.4889 | 1 | 0 | 24
38889.4894 | 1 | 0 | 24
38889.4898 | 1 | 0 | 24
38889.4903 | 1 | 0 | 24
38889.4907 | 1 | 0 | 24
38889.4911 | 1 | 0 | 24
38889.4916 | 1 | 0 | 24
38889.492 | 1 | 0 | 24
38889.4924 | 1 | 0 | 24
38889.4929 | 1 | 0 | 24
38889.4933 | 1 | 0 | 24
38889.4938 | 1 | 0 | 24
38889.4942 | 1 | 0 | 24
38889.4946 | 1 | 0 | 24
38889.4951 | 1 | 0 | 24
38889.4955 | 1 | 0 | 24
38889.4959 | 1 | 0 | 24
38889.4964 | 1 | 0 | 24
38889.4968 | 1 | 0 | 24
38889.4973 | 1 | 0 | 24
38889.4977 | 1 | 0 | 24
38889.4981 | 1 | 0 | 24
38889.4986 | 1 | 0 | 24
38889.499 | 1 | 0 | 24
38889.4994 | 1 | 0 | 24
38889.4999 | 2 | 0 | 24
38889.5003 | 1 | 0 | 24
38889.5008 | 1 | 0 | 24
38889.5012 | 1 | 0 | 24
38889.5016 | 1 | 0 | 24
38889.5021 | 1 | 0 | 24
38889.5025 | 1 | 0 | 24
38889.5029 | 1 | 0 | 24
38889.5034 | 2 | 0 | 24
38889.5038 | 1 | 0 | 24
38889.5043 | 1 | 0 | 24
38889.5047 | 1 | 0 | 24
38889.5051 | 1 | 0 | 24
38889.5056 | 1 | 0 | 24
38889.506 | 1 | 0 | 24
38889.5064 | 1 | 0 | 24
38889.5069 | 1 | 0 | 24
38889.5073 | 2 | 0 | 24
38889.5078 | 1 | 0 | 24
38889.5082 | 1 | 0 | 24
38889.5086 | 1 | 0 | 24
38889.5091 | 1 | 0 | 24
38889.5099 | 1 | 0 | 24
38889.5104 | 1 | 0 | 24
38889.5108 | 1 | 0 | 24
38889.5113 | 1 | 0 | 24
38889.5117 | 1 | 0 | 24
38889.5121 | 1 | 0 | 24
38889.5126 | 1 | 0 | 24
38889.513 | 1 | 0 | 24
38889.5134 | 1 | 0 | 24
38889.4876 | 1 | 0 | 25
38889.4881 | 1 | 0 | 25
38889.4885 | 1 | 0 | 25
38889.489 | 1 | 0 | 25
38889.4894 | 1 | 0 | 25
38889.4898 | 1 | 0 | 25
38889.4903 | 1 | 0 | 25
38889.4907 | 1 | 0 | 25
38889.4911 | 1 | 0 | 25
38889.4916 | 1 | 0 | 25
38889.492 | 1 | 0 | 25
38889.4925 | 1 | 0 | 25
38889.4929 | 1 | 0 | 25
38889.4933 | 1 | 0 | 25
38889.4938 | 1 | 0 | 25
38889.4942 | 1 | 0 | 25
38889.4946 | 1 | 0 | 25
38889.4951 | 1 | 0 | 25
38889.4955 | 1 | 0 | 25
38889.496 | 1 | 0 | 25
38889.4964 | 1 | 0 | 25
38889.4968 | 1 | 0 | 25
38889.4973 | 1 | 0 | 25
38889.4977 | 1 | 0 | 25
38889.4981 | 1 | 0 | 25
38889.4986 | 1 | 0 | 25
38889.499 | 1 | 0 | 25
38889.4995 | 1 | 0 | 25
38889.4999 | 1 | 0 | 25
38889.5003 | 1 | 0 | 25
38889.5008 | 1 | 0 | 25
38889.5012 | 1 | 0 | 25
38889.5016 | 1 | 0 | 25
38889.5021 | 1 | 0 | 25
38889.5025 | 1 | 0 | 25
38889.503 | 1 | 0 | 25
38889.5034 | 1 | 0 | 25
38889.5038 | 1 | 0 | 25
38889.5043 | 1 | 0 | 25
38889.5047 | 1 | 0 | 25
38889.5051 | 1 | 0 | 25
38889.5056 | 1 | 0 | 25
38889.506 | 1 | 0 | 25
38889.5065 | 1 | 0 | 25
38889.5069 | 1 | 0 | 25
38889.5073 | 1 | 0 | 25
38889.5078 | 1 | 0 | 25
38889.5082 | 1 | 0 | 25
38889.5086 | 1 | 0 | 25
38889.5091 | 1 | 0 | 25
38889.5095 | 1 | 0 | 25
38889.51 | 1 | 0 | 25
38889.5104 | 1 | 0 | 25
38889.5108 | 1 | 0 | 25
38889.5113 | 1 | 0 | 25
38889.5117 | 1 | 0 | 25
38889.5121 | 1 | 0 | 25
38889.5126 | 1 | 0 | 25
38889.513 | 1 | 0 | 25
38889.5134 | 1 | 0 | 25
38889.4877 | 1 | 0 | 26
38889.4881 | 1 | 0 | 26
38889.4885 | 1 | 0 | 26
38889.489 | 1 | 0 | 26
38889.4894 | 1 | 0 | 26
38889.4898 | 1 | 0 | 26
38889.4903 | 1 | 0 | 26
38889.4907 | 1 | 0 | 26
38889.4912 | 1 | 0 | 26
38889.4916 | 1 | 0 | 26
38889.492 | 1 | 0 | 26
38889.4925 | 1 | 0 | 26
38889.4929 | 1 | 0 | 26
38889.4933 | 1 | 0 | 26
38889.4938 | 1 | 0 | 26
38889.4942 | 1 | 0 | 26
38889.4947 | 1 | 0 | 26
38889.4951 | 1 | 0 | 26
38889.4955 | 1 | 0 | 26
38889.496 | 1 | 0 | 26
38889.4964 | 2 | 0 | 26
38889.4968 | 1 | 0 | 26
38889.4973 | 1 | 0 | 26
38889.4977 | 1 | 0 | 26
38889.4981 | 1 | 0 | 26
38889.4986 | 1 | 0 | 26
38889.499 | 1 | 0 | 26
38889.4995 | 1 | 0 | 26
38889.4999 | 1 | 0 | 26
38889.5003 | 1 | 0 | 26
38889.5008 | 2 | 0 | 26
38889.5012 | 1 | 0 | 26
38889.5017 | 1 | 0 | 26
38889.5021 | 1 | 0 | 26
38889.5025 | 1 | 0 | 26
38889.503 | 1 | 0 | 26
38889.5034 | 2 | 0 | 26
38889.5038 | 1 | 0 | 26
38889.5043 | 1 | 0 | 26
38889.5047 | 1 | 0 | 26
38889.5052 | 1 | 0 | 26
38889.5056 | 1 | 0 | 26
38889.506 | 1 | 0 | 26
38889.5065 | 1 | 0 | 26
38889.5069 | 1 | 0 | 26
38889.5073 | 1 | 0 | 26
38889.5078 | 1 | 0 | 26
38889.5082 | 1 | 0 | 26
38889.5086 | 1 | 0 | 26
38889.5091 | 1 | 0 | 26
38889.5095 | 1 | 0 | 26
38889.51 | 1 | 0 | 26
38889.5104 | 1 | 0 | 26
38889.5108 | 1 | 0 | 26
38889.5113 | 1 | 0 | 26
38889.5117 | 1 | 0 | 26
38889.5122 | 1 | 0 | 26
38889.5126 | 1 | 0 | 26
38889.513 | 1 | 0 | 26
38889.5135 | 1 | 0 | 26
38889.4877 | 1 | 0 | 27
38889.4881 | 1 | 0 | 27
38889.4885 | 1 | 0 | 27
38889.489 | 2 | 0 | 27
38889.4894 | 1 | 0 | 27
38889.4898 | 1 | 0 | 27
38889.4903 | 1 | 0 | 27
38889.4907 | 1 | 0 | 27
38889.4912 | 1 | 0 | 27
38889.4916 | 1 | 0 | 27
38889.492 | 1 | 0 | 27
38889.4925 | 1 | 0 | 27
38889.4929 | 1 | 0 | 27
38889.4933 | 1 | 0 | 27
38889.4938 | 1 | 0 | 27
38889.4942 | 1 | 0 | 27
38889.4947 | 1 | 0 | 27
38889.4951 | 1 | 0 | 27
38889.4955 | 1 | 0 | 27
38889.496 | 1 | 0 | 27
38889.4964 | 1 | 0 | 27
38889.4969 | 1 | 0 | 27
38889.4973 | 1 | 0 | 27
38889.4977 | 1 | 0 | 27
38889.4982 | 1 | 0 | 27
38889.4986 | 1 | 0 | 27
38889.499 | 1 | 0 | 27
38889.4995 | 1 | 0 | 27
38889.4999 | 1 | 0 | 27
38889.5003 | 1 | 0 | 27
38889.5008 | 1 | 0 | 27
38889.5012 | 1 | 0 | 27
38889.5017 | 1 | 0 | 27
38889.5021 | 1 | 0 | 27
38889.5025 | 1 | 0 | 27
38889.503 | 1 | 0 | 27
38889.5034 | 1 | 0 | 27
38889.5039 | 1 | 0 | 27
38889.5043 | 1 | 0 | 27
38889.5047 | 1 | 0 | 27
38889.5052 | 1 | 0 | 27
38889.5056 | 1 | 0 | 27
38889.506 | 1 | 0 | 27
38889.5065 | 1 | 0 | 27
38889.5069 | 1 | 0 | 27
38889.5073 | 1 | 0 | 27
38889.5078 | 1 | 0 | 27
38889.5082 | 1 | 0 | 27
38889.5087 | 2 | 0 | 27
38889.5091 | 1 | 0 | 27
38889.5095 | 1 | 0 | 27
38889.51 | 1 | 0 | 27
38889.5104 | 1 | 0 | 27
38889.5108 | 1 | 0 | 27
38889.5113 | 1 | 0 | 27
38889.5117 | 1 | 0 | 27
38889.5122 | 1 | 0 | 27
38889.5126 | 1 | 0 | 27
38889.513 | 1 | 0 | 27
38889.5135 | 1 | 0 | 27
38889.4877 | 1 | 0 | 28
38889.4881 | 1 | 0 | 28
38889.4886 | 1 | 0 | 28
38889.489 | 1 | 0 | 28
38889.4894 | 1 | 0 | 28
38889.4899 | 1 | 0 | 28
38889.4903 | 1 | 0 | 28
38889.4907 | 1 | 0 | 28
38889.4912 | 1 | 0 | 28
38889.4916 | 1 | 0 | 28
38889.492 | 1 | 0 | 28
38889.4925 | 1 | 0 | 28
38889.4929 | 1 | 0 | 28
38889.4934 | 1 | 0 | 28
38889.4938 | 1 | 0 | 28
38889.4942 | 1 | 0 | 28
38889.4947 | 1 | 0 | 28
38889.4951 | 1 | 0 | 28
38889.4955 | 1 | 0 | 28
38889.496 | 1 | 0 | 28
38889.4964 | 1 | 0 | 28
38889.4969 | 1 | 0 | 28
38889.4973 | 1 | 0 | 28
38889.4977 | 1 | 0 | 28
38889.4982 | 1 | 0 | 28
38889.4986 | 1 | 0 | 28
38889.4991 | 1 | 0 | 28
38889.4995 | 1 | 0 | 28
38889.4999 | 1 | 0 | 28
38889.5004 | 1 | 0 | 28
38889.5008 | 1 | 0 | 28
38889.5012 | 1 | 0 | 28
38889.5017 | 1 | 0 | 28
38889.5021 | 1 | 0 | 28
38889.5025 | 1 | 0 | 28
38889.503 | 1 | 0 | 28
38889.5034 | 1 | 0 | 28
38889.5039 | 1 | 0 | 28
38889.5043 | 1 | 0 | 28
38889.5047 | 1 | 0 | 28
38889.5052 | 1 | 0 | 28
38889.5056 | 1 | 0 | 28
38889.5061 | 1 | 0 | 28
38889.5065 | 1 | 0 | 28
38889.5069 | 1 | 0 | 28
38889.5074 | 1 | 0 | 28
38889.5078 | 1 | 0 | 28
38889.5082 | 1 | 0 | 28
38889.5087 | 1 | 0 | 28
38889.5091 | 1 | 0 | 28
38889.5095 | 2 | 0 | 28
38889.51 | 1 | 0 | 28
38889.5104 | 1 | 0 | 28
38889.5109 | 1 | 0 | 28
38889.5113 | 1 | 0 | 28
38889.5117 | 1 | 0 | 28
38889.5122 | 1 | 0 | 28
38889.5126 | 1 | 0 | 28
38889.513 | 1 | 0 | 28
38889.5135 | 1 | 0 | 28
38889.4877 | 1 | 0 | 29
38889.4881 | 1 | 0 | 29
38889.4886 | 1 | 0 | 29
38889.489 | 1 | 0 | 29
38889.4894 | 1 | 0 | 29
38889.4899 | 1 | 0 | 29
38889.4903 | 1 | 0 | 29
38889.4908 | 1 | 0 | 29
38889.4912 | 1 | 0 | 29
38889.4916 | 1 | 0 | 29
38889.4921 | 1 | 0 | 29
38889.4925 | 1 | 0 | 29
38889.4929 | 1 | 0 | 29
38889.4934 | 1 | 0 | 29
38889.4938 | 1 | 0 | 29
38889.4942 | 1 | 0 | 29
38889.4947 | 1 | 0 | 29
38889.4951 | 1 | 0 | 29
38889.4956 | 1 | 0 | 29
38889.496 | 1 | 0 | 29
38889.4964 | 1 | 0 | 29
38889.4969 | 1 | 0 | 29
38889.4973 | 1 | 0 | 29
38889.4977 | 1 | 0 | 29
38889.4982 | 1 | 0 | 29
38889.4986 | 1 | 0 | 29
38889.4991 | 1 | 0 | 29
38889.4995 | 1 | 0 | 29
38889.4999 | 1 | 0 | 29
38889.5004 | 1 | 0 | 29
38889.5008 | 1 | 0 | 29
38889.5013 | 1 | 0 | 29
38889.5017 | 1 | 1 | 29
38889.5021 | 1 | 0 | 29
38889.5026 | 1 | 0 | 29
38889.503 | 1 | 0 | 29
38889.5034 | 1 | 0 | 29
38889.5039 | 1 | 0 | 29
38889.5043 | 1 | 0 | 29
38889.5047 | 1 | 0 | 29
38889.5052 | 1 | 0 | 29
38889.5056 | 1 | 0 | 29
38889.5061 | 1 | 0 | 29
38889.5065 | 1 | 0 | 29
38889.5069 | 1 | 0 | 29
38889.5074 | 1 | 0 | 29
38889.5078 | 1 | 0 | 29
38889.5082 | 2 | 0 | 29
38889.5087 | 1 | 0 | 29
38889.5091 | 1 | 0 | 29
38889.5096 | 1 | 0 | 29
38889.51 | 1 | 0 | 29
38889.5104 | 1 | 0 | 29
38889.5109 | 1 | 0 | 29
38889.5113 | 1 | 0 | 29
38889.5117 | 1 | 0 | 29
38889.5122 | 1 | 0 | 29
38889.5126 | 1 | 0 | 29
38889.5131 | 1 | 0 | 29
38889.5135 | 1 | 0 | 29
38889.4877 | 1 | 0 | 30
38889.4881 | 1 | 0 | 30
38889.4886 | 1 | 0 | 30
38889.489 | 1 | 0 | 30
38889.4894 | 1 | 0 | 30
38889.4899 | 1 | 0 | 30
38889.4903 | 1 | 0 | 30
38889.4908 | 1 | 0 | 30
38889.4912 | 1 | 0 | 30
38889.4916 | 1 | 0 | 30
38889.4921 | 1 | 0 | 30
38889.4925 | 1 | 0 | 30
38889.4929 | 1 | 0 | 30
38889.4934 | 1 | 0 | 30
38889.4938 | 1 | 0 | 30
38889.4943 | 1 | 0 | 30
38889.4947 | 1 | 0 | 30
38889.4951 | 1 | 0 | 30
38889.4956 | 1 | 0 | 30
38889.496 | 1 | 0 | 30
38889.4964 | 1 | 0 | 30
38889.4969 | 1 | 0 | 30
38889.4973 | 1 | 0 | 30
38889.4978 | 1 | 0 | 30
38889.4982 | 1 | 0 | 30
38889.4986 | 1 | 0 | 30
38889.4991 | 2564 | 0 | 30
38889.4995 | 2479 | 0 | 30
38889.4999 | 2091 | 0 | 30
38889.5004 | 2540 | 0 | 30
38889.5008 | 2269 | 0 | 30
38889.5013 | 2303 | 0 | 30
38889.5017 | 2378 | 0 | 30
38889.5021 | 2107 | 0 | 30
38889.5026 | 2151 | 0 | 30
38889.503 | 2573 | 0 | 30
38889.5034 | 2325 | 0 | 30
38889.5039 | 2538 | 0 | 30
38889.5043 | 1984 | 0 | 30
38889.5048 | 2124 | 0 | 30
38889.5052 | 2014 | 0 | 30
38889.5056 | 2471 | 0 | 30
38889.5061 | 2470 | 0 | 30
38889.5065 | 2376 | 0 | 30
38889.5069 | 2480 | 0 | 30
38889.5074 | 2032 | 0 | 30
38889.5078 | 2081 | 0 | 30
38889.5083 | 2497 | 0 | 30
38889.5087 | 2162 | 0 | 30
38889.5091 | 2536 | 0 | 30
38889.5096 | 2250 | 0 | 30
38889.51 | 1961 | 0 | 30
38889.5104 | 1997 | 0 | 30
38889.5109 | 1959 | 0 | 30
38889.5113 | 2449 | 0 | 30
38889.5118 | 2551 | 0 | 30
38889.5122 | 2328 | 0 | 30
38889.5126 | 2013 | 0 | 30
38889.5131 | 1868 | 0 | 30
38889.5135 | 1934 | 0 | 30
38889.4877 | 1 | 0 | 31
38889.4881 | 1 | 0 | 31
38889.4886 | 1 | 0 | 31
38889.489 | 1 | 0 | 31
38889.4895 | 1 | 0 | 31
38889.4899 | 1 | 0 | 31
38889.4903 | 1 | 0 | 31
38889.4908 | 1 | 0 | 31
38889.4912 | 1 | 0 | 31
38889.4916 | 1 | 0 | 31
38889.4921 | 1 | 0 | 31
38889.4925 | 1 | 0 | 31
38889.493 | 1 | 0 | 31
38889.4934 | 1 | 0 | 31
38889.4938 | 1 | 0 | 31
38889.4943 | 1 | 0 | 31
38889.4947 | 1 | 0 | 31
38889.4951 | 1 | 0 | 31
38889.4956 | 1 | 0 | 31
38889.496 | 1 | 0 | 31
38889.4965 | 1 | 0 | 31
38889.4969 | 1 | 0 | 31
38889.4973 | 1 | 0 | 31
38889.4978 | 1 | 0 | 31
38889.4982 | 1 | 0 | 31
38889.4986 | 1 | 0 | 31
38889.4991 | 1 | 0 | 31
38889.4995 | 2 | 0 | 31
38889.5 | 2 | 0 | 31
38889.5004 | 2 | 0 | 31
38889.5008 | 2 | 0 | 31
38889.5013 | 1 | 0 | 31
38889.5017 | 1 | 0 | 31
38889.5021 | 2 | 0 | 31
38889.5026 | 2 | 0 | 31
38889.503 | 1 | 0 | 31
38889.5034 | 2 | 0 | 31
38889.5039 | 2 | 0 | 31
38889.5043 | 2 | 0 | 31
38889.5048 | 2 | 0 | 31
38889.5052 | 1 | 0 | 31
38889.5056 | 1 | 0 | 31
38889.5061 | 1 | 0 | 31
38889.5065 | 1 | 0 | 31
38889.507 | 1 | 0 | 31
38889.5074 | 2 | 0 | 31
38889.5078 | 2 | 0 | 31
38889.5083 | 1025 | 1069 | 31
38889.5087 | 935 | 913 | 31
38889.5091 | 992 | 966 | 31
38889.5096 | 1138 | 1186 | 31
38889.51 | 1142 | 1114 | 31
38889.5105 | 1056 | 1030 | 31
38889.5109 | 985 | 960 | 31
38889.5113 | 1055 | 1030 | 31
38889.5118 | 1125 | 1183 | 31
38889.5122 | 1156 | 1130 | 31
38889.5126 | 1143 | 1115 | 31
38889.5131 | 1095 | 1149 | 31
38889.5135 | 1013 | 1117 | 31
38889.4877 | 1 | 0 | 32
38889.4882 | 1 | 0 | 32
38889.4886 | 1 | 0 | 32
38889.489 | 1 | 0 | 32
38889.4895 | 1 | 0 | 32
38889.4899 | 1 | 0 | 32
38889.4903 | 1 | 0 | 32
38889.4908 | 1 | 0 | 32
38889.4912 | 1 | 0 | 32
38889.4917 | 1 | 0 | 32
38889.4921 | 1 | 0 | 32
38889.4925 | 1 | 0 | 32
38889.493 | 1 | 0 | 32
38889.4934 | 1 | 0 | 32
38889.4938 | 1 | 0 | 32
38889.4943 | 1 | 0 | 32
38889.4947 | 1 | 0 | 32
38889.4952 | 1 | 0 | 32
38889.4956 | 1 | 0 | 32
38889.496 | 1 | 0 | 32
38889.4965 | 1 | 0 | 32
38889.4969 | 1 | 0 | 32
38889.4973 | 1 | 0 | 32
38889.4978 | 1 | 0 | 32
38889.4982 | 1 | 0 | 32
38889.4987 | 1 | 0 | 32
38889.4991 | 1 | 0 | 32
38889.4995 | 1 | 0 | 32
38889.5 | 1 | 0 | 32
38889.5004 | 1 | 0 | 32
38889.5008 | 1 | 0 | 32
38889.5013 | 1 | 0 | 32
38889.5017 | 1 | 0 | 32
38889.5022 | 1 | 0 | 32
38889.5026 | 1 | 0 | 32
38889.503 | 1 | 0 | 32
38889.5035 | 1 | 0 | 32
38889.5039 | 1 | 0 | 32
38889.5043 | 1 | 0 | 32
38889.5048 | 1 | 0 | 32
38889.5052 | 1 | 0 | 32
38889.5056 | 1 | 0 | 32
38889.5061 | 1 | 0 | 32
38889.5065 | 1 | 0 | 32
38889.507 | 1 | 0 | 32
38889.5074 | 1 | 0 | 32
38889.5078 | 1 | 0 | 32
38889.5083 | 1056 | 1146 | 32
38889.5087 | 1025 | 998 | 32
38889.5092 | 1196 | 950 | 32
38889.5096 | 1065 | 938 | 32
38889.51 | 984 | 945 | 32
38889.5105 | 1024 | 1069 | 32
38889.5109 | 996 | 970 | 32
38889.5113 | 1203 | 1187 | 32
38889.5118 | 984 | 959 | 32
38889.5122 | 995 | 1107 | 32
38889.5127 | 1090 | 1142 | 32
38889.5131 | 1197 | 1139 | 32
38889.5135 | 953 | 928 | 32
38889.4877 | 1 | 0 | 33
38889.4882 | 1 | 0 | 33
38889.4886 | 1 | 0 | 33
38889.489 | 1 | 0 | 33
38889.4895 | 1 | 0 | 33
38889.4899 | 1 | 0 | 33
38889.4903 | 1 | 0 | 33
38889.4908 | 1 | 0 | 33
38889.4912 | 1 | 0 | 33
38889.4917 | 1 | 0 | 33
38889.4921 | 1 | 0 | 33
38889.4925 | 1 | 0 | 33
38889.493 | 1 | 0 | 33
38889.4934 | 1 | 0 | 33
38889.4939 | 1 | 0 | 33
38889.4943 | 1 | 0 | 33
38889.4947 | 1 | 0 | 33
38889.4952 | 1 | 0 | 33
38889.4956 | 1 | 0 | 33
38889.496 | 1 | 0 | 33
38889.4965 | 1 | 0 | 33
38889.4969 | 1 | 0 | 33
38889.4973 | 1 | 0 | 33
38889.4978 | 1 | 0 | 33
38889.4982 | 1 | 0 | 33
38889.4987 | 1 | 0 | 33
38889.4991 | 1 | 0 | 33
38889.4995 | 1 | 0 | 33
38889.5 | 1 | 0 | 33
38889.5004 | 1 | 0 | 33
38889.5009 | 1 | 0 | 33
38889.5013 | 1 | 0 | 33
38889.5017 | 1 | 0 | 33
38889.5022 | 1 | 0 | 33
38889.5026 | 1 | 0 | 33
38889.503 | 1 | 0 | 33
38889.5035 | 1 | 0 | 33
38889.5039 | 1 | 0 | 33
38889.5044 | 2 | 0 | 33
38889.5048 | 1 | 0 | 33
38889.5052 | 1 | 0 | 33
38889.5057 | 1 | 0 | 33
38889.5061 | 1 | 0 | 33
38889.5065 | 1 | 0 | 33
38889.507 | 1 | 0 | 33
38889.5074 | 1 | 0 | 33
38889.5078 | 1 | 0 | 33
38889.5083 | 1 | 0 | 33
38889.5087 | 1 | 1 | 33
38889.5092 | 1 | 1 | 33
38889.5096 | 1 | 0 | 33
38889.51 | 1 | 1 | 33
38889.5105 | 2 | 1 | 33
38889.5109 | 2 | 1 | 33
38889.5113 | 1 | 1 | 33
38889.5118 | 1 | 1 | 33
38889.5122 | 1 | 0 | 33
38889.5127 | 1 | 1 | 33
38889.5131 | 1 | 1 | 33
38889.5135 | 2 | 1 | 33
38889.4877 | 1 | 0 | 34
38889.4882 | 1 | 0 | 34
38889.4886 | 1 | 0 | 34
38889.4891 | 1 | 0 | 34
38889.4895 | 1 | 0 | 34
38889.4899 | 1 | 0 | 34
38889.4904 | 2 | 0 | 34
38889.4908 | 1 | 0 | 34
38889.4912 | 1 | 0 | 34
38889.4917 | 1 | 0 | 34
38889.4921 | 1 | 0 | 34
38889.4925 | 1 | 0 | 34
38889.493 | 1 | 0 | 34
38889.4934 | 1 | 0 | 34
38889.4939 | 1 | 0 | 34
38889.4943 | 1 | 0 | 34
38889.4947 | 1 | 0 | 34
38889.4952 | 1 | 0 | 34
38889.4956 | 1 | 0 | 34
38889.4961 | 1 | 0 | 34
38889.4965 | 1 | 0 | 34
38889.4969 | 1 | 0 | 34
38889.4974 | 1 | 0 | 34
38889.4978 | 1 | 0 | 34
38889.4982 | 1 | 0 | 34
38889.4987 | 1 | 0 | 34
38889.4991 | 1 | 0 | 34
38889.4995 | 1 | 0 | 34
38889.5 | 1 | 0 | 34
38889.5004 | 1 | 0 | 34
38889.5009 | 1 | 0 | 34
38889.5013 | 1 | 0 | 34
38889.5017 | 1 | 0 | 34
38889.5022 | 1 | 0 | 34
38889.5026 | 1 | 0 | 34
38889.503 | 1 | 0 | 34
38889.5035 | 1 | 0 | 34
38889.5039 | 1 | 0 | 34
38889.5044 | 1 | 0 | 34
38889.5048 | 1 | 0 | 34
38889.5052 | 1 | 0 | 34
38889.5057 | 1 | 0 | 34
38889.5061 | 1 | 0 | 34
38889.5066 | 2 | 0 | 34
38889.507 | 1 | 0 | 34
38889.5074 | 1 | 0 | 34
38889.5079 | 1 | 0 | 34
38889.5083 | 1 | 0 | 34
38889.5087 | 1 | 0 | 34
38889.5092 | 1 | 0 | 34
38889.5096 | 1 | 0 | 34
38889.51 | 1 | 0 | 34
38889.5105 | 1 | 0 | 34
38889.5109 | 1 | 0 | 34
38889.5114 | 1 | 0 | 34
38889.5118 | 1 | 0 | 34
38889.5122 | 1 | 0 | 34
38889.5127 | 1 | 0 | 34
38889.5131 | 1 | 0 | 34
38889.5135 | 1 | 0 | 34
38889.4877 | 1 | 0 | 35
38889.4882 | 1 | 0 | 35
38889.4886 | 1 | 0 | 35
38889.4891 | 1 | 0 | 35
38889.4895 | 1 | 0 | 35
38889.4899 | 1 | 0 | 35
38889.4904 | 2 | 0 | 35
38889.4908 | 1 | 0 | 35
38889.4912 | 1 | 0 | 35
38889.4917 | 1 | 0 | 35
38889.4921 | 1 | 0 | 35
38889.4926 | 1 | 0 | 35
38889.493 | 1 | 0 | 35
38889.4934 | 1 | 0 | 35
38889.4939 | 1 | 0 | 35
38889.4943 | 1 | 0 | 35
38889.4947 | 1 | 0 | 35
38889.4952 | 1 | 0 | 35
38889.4956 | 1 | 0 | 35
38889.4961 | 1 | 0 | 35
38889.4965 | 1 | 0 | 35
38889.4969 | 1 | 0 | 35
38889.4974 | 1 | 0 | 35
38889.4978 | 1 | 0 | 35
38889.4983 | 1 | 0 | 35
38889.4987 | 1 | 0 | 35
38889.4991 | 1 | 0 | 35
38889.4996 | 1 | 0 | 35
38889.5 | 1 | 0 | 35
38889.5004 | 1 | 0 | 35
38889.5009 | 1 | 0 | 35
38889.5013 | 1 | 0 | 35
38889.5017 | 1 | 0 | 35
38889.5022 | 1 | 0 | 35
38889.5026 | 1 | 0 | 35
38889.5031 | 1 | 0 | 35
38889.5035 | 1 | 0 | 35
38889.5039 | 1 | 0 | 35
38889.5044 | 1 | 0 | 35
38889.5048 | 1 | 0 | 35
38889.5052 | 1 | 0 | 35
38889.5057 | 1 | 0 | 35
38889.5061 | 1 | 0 | 35
38889.5066 | 1 | 0 | 35
38889.507 | 1 | 0 | 35
38889.5074 | 1 | 0 | 35
38889.5079 | 1 | 0 | 35
38889.5083 | 1 | 0 | 35
38889.5088 | 1 | 0 | 35
38889.5092 | 1 | 0 | 35
38889.5096 | 1 | 0 | 35
38889.5101 | 1 | 0 | 35
38889.5105 | 1 | 0 | 35
38889.5109 | 1 | 0 | 35
38889.5114 | 1 | 0 | 35
38889.5118 | 1 | 0 | 35
38889.5122 | 1 | 0 | 35
38889.5127 | 1 | 0 | 35
38889.5131 | 1 | 0 | 35
38889.5136 | 1 | 0 | 35
38889.4878 | 1 | 0 | 36
38889.4882 | 1 | 0 | 36
38889.4886 | 1 | 0 | 36
38889.4891 | 1 | 0 | 36
38889.4895 | 1 | 0 | 36
38889.4899 | 1 | 0 | 36
38889.4904 | 2 | 0 | 36
38889.4908 | 1 | 0 | 36
38889.4913 | 1 | 0 | 36
38889.4917 | 1 | 0 | 36
38889.4921 | 1 | 0 | 36
38889.4926 | 1 | 0 | 36
38889.493 | 1 | 0 | 36
38889.4934 | 1 | 0 | 36
38889.4939 | 1 | 0 | 36
38889.4943 | 1 | 0 | 36
38889.4948 | 1 | 0 | 36
38889.4952 | 1 | 0 | 36
38889.4956 | 1 | 0 | 36
38889.4961 | 1 | 0 | 36
38889.4965 | 1 | 0 | 36
38889.4969 | 1 | 0 | 36
38889.4974 | 1 | 0 | 36
38889.4978 | 1 | 0 | 36
38889.4983 | 1 | 0 | 36
38889.4987 | 1 | 0 | 36
38889.4991 | 2376 | 0 | 36
38889.4996 | 2003 | 0 | 36
38889.5 | 2047 | 0 | 36
38889.5004 | 2267 | 0 | 36
38889.5009 | 2066 | 0 | 36
38889.5013 | 2151 | 0 | 36
38889.5018 | 2444 | 0 | 36
38889.5022 | 2573 | 0 | 36
38889.5026 | 2574 | 0 | 36
38889.5031 | 1982 | 0 | 36
38889.5035 | 2528 | 0 | 36
38889.5039 | 2429 | 0 | 36
38889.5044 | 2114 | 0 | 36
38889.5048 | 2571 | 0 | 36
38889.5053 | 2284 | 0 | 36
38889.5057 | 2268 | 0 | 36
38889.5061 | 2187 | 0 | 36
38889.5066 | 2070 | 0 | 36
38889.507 | 2269 | 0 | 36
38889.5074 | 2119 | 0 | 36
38889.5079 | 2013 | 0 | 36
38889.5083 | 2414 | 0 | 36
38889.5088 | 2038 | 0 | 36
38889.5092 | 2319 | 0 | 36
38889.5096 | 2355 | 0 | 36
38889.5101 | 2340 | 0 | 36
38889.5105 | 2354 | 0 | 36
38889.5109 | 2114 | 0 | 36
38889.5114 | 2145 | 0 | 36
38889.5118 | 2100 | 0 | 36
38889.5123 | 1988 | 0 | 36
38889.5127 | 2239 | 0 | 36
38889.5131 | 2188 | 0 | 36
38889.5136 | 1963 | 0 | 36
38889.4878 | 1 | 0 | 37
38889.4882 | 1 | 0 | 37
38889.4886 | 1 | 0 | 37
38889.4891 | 1 | 0 | 37
38889.4895 | 1 | 0 | 37
38889.49 | 1 | 0 | 37
38889.4904 | 1 | 0 | 37
38889.4908 | 1 | 0 | 37
38889.4913 | 1 | 0 | 37
38889.4917 | 1 | 0 | 37
38889.4921 | 1 | 0 | 37
38889.4926 | 1 | 0 | 37
38889.493 | 1 | 0 | 37
38889.4935 | 1 | 0 | 37
38889.4939 | 1 | 0 | 37
38889.4943 | 1 | 0 | 37
38889.4948 | 1 | 0 | 37
38889.4952 | 1 | 0 | 37
38889.4956 | 1 | 0 | 37
38889.4961 | 1 | 0 | 37
38889.4965 | 1 | 0 | 37
38889.497 | 1 | 0 | 37
38889.4974 | 1 | 0 | 37
38889.4978 | 1 | 0 | 37
38889.4983 | 2 | 0 | 37
38889.4987 | 1 | 0 | 37
38889.4991 | 2 | 0 | 37
38889.4996 | 2 | 0 | 37
38889.5 | 1 | 0 | 37
38889.5005 | 2 | 0 | 37
38889.5009 | 3 | 0 | 37
38889.5013 | 2 | 0 | 37
38889.5018 | 2 | 0 | 37
38889.5022 | 2 | 0 | 37
38889.5026 | 2 | 0 | 37
38889.5031 | 2 | 0 | 37
38889.5035 | 2 | 0 | 37
38889.504 | 1 | 0 | 37
38889.5044 | 1 | 0 | 37
38889.5048 | 2 | 0 | 37
38889.5053 | 2 | 0 | 37
38889.5057 | 2 | 0 | 37
38889.5061 | 2 | 0 | 37
38889.5066 | 2 | 0 | 37
38889.507 | 2 | 0 | 37
38889.5079 | 2 | 0 | 37
38889.5083 | 2 | 0 | 37
38889.5088 | 2 | 0 | 37
38889.5092 | 2 | 0 | 37
38889.5096 | 2 | 0 | 37
38889.5101 | 2 | 0 | 37
38889.5105 | 2 | 0 | 37
38889.5109 | 2 | 0 | 37
38889.5114 | 2 | 0 | 37
38889.5118 | 2 | 0 | 37
38889.5123 | 2 | 0 | 37
38889.5127 | 3 | 0 | 37
38889.5131 | 1 | 0 | 37
38889.5136 | 2 | 0 | 37
38889.4878 | 1 | 0 | 38
38889.4882 | 1 | 0 | 38
38889.4887 | 1 | 0 | 38
38889.4891 | 1 | 0 | 38
38889.4895 | 1 | 0 | 38
38889.49 | 1 | 0 | 38
38889.4904 | 1 | 0 | 38
38889.4908 | 1 | 0 | 38
38889.4913 | 1 | 0 | 38
38889.4917 | 1 | 0 | 38
38889.4922 | 1 | 0 | 38
38889.4926 | 1 | 0 | 38
38889.493 | 1 | 0 | 38
38889.4935 | 1 | 0 | 38
38889.4939 | 1 | 0 | 38
38889.4943 | 1 | 0 | 38
38889.4948 | 1 | 0 | 38
38889.4952 | 1 | 0 | 38
38889.4956 | 1 | 0 | 38
38889.4961 | 1 | 0 | 38
38889.4965 | 2 | 0 | 38
38889.497 | 1 | 0 | 38
38889.4974 | 1 | 0 | 38
38889.4978 | 1 | 0 | 38
38889.4983 | 1 | 0 | 38
38889.4987 | 1 | 0 | 38
38889.4992 | 1 | 0 | 38
38889.4996 | 1 | 0 | 38
38889.5 | 1 | 0 | 38
38889.5005 | 1 | 0 | 38
38889.5009 | 2 | 0 | 38
38889.5013 | 1 | 0 | 38
38889.5018 | 1 | 0 | 38
38889.5022 | 1 | 0 | 38
38889.5027 | 1 | 0 | 38
38889.5031 | 1 | 0 | 38
38889.5035 | 1 | 0 | 38
38889.504 | 1 | 0 | 38
38889.5044 | 1 | 0 | 38
38889.5048 | 1 | 0 | 38
38889.5053 | 1 | 0 | 38
38889.5057 | 1 | 0 | 38
38889.5061 | 1 | 0 | 38
38889.5066 | 1 | 0 | 38
38889.507 | 1 | 0 | 38
38889.5075 | 1 | 0 | 38
38889.5079 | 1 | 0 | 38
38889.5083 | 1 | 0 | 38
38889.5088 | 1 | 0 | 38
38889.5092 | 1 | 0 | 38
38889.5097 | 1 | 0 | 38
38889.5101 | 1 | 0 | 38
38889.5105 | 1 | 0 | 38
38889.511 | 1 | 0 | 38
38889.5114 | 1 | 0 | 38
38889.5118 | 1 | 0 | 38
38889.5123 | 1 | 0 | 38
38889.5127 | 1 | 0 | 38
38889.5131 | 2 | 0 | 38
38889.5136 | 1 | 0 | 38
38889.4878 | 1 | 0 | 39
38889.4882 | 1 | 0 | 39
38889.4887 | 1 | 0 | 39
38889.4891 | 1 | 0 | 39
38889.4895 | 1 | 0 | 39
38889.49 | 1 | 0 | 39
38889.4904 | 1 | 0 | 39
38889.4909 | 1 | 0 | 39
38889.4913 | 1 | 0 | 39
38889.4917 | 1 | 0 | 39
38889.4922 | 1 | 0 | 39
38889.4926 | 1 | 0 | 39
38889.493 | 1 | 0 | 39
38889.4935 | 1 | 0 | 39
38889.4939 | 1 | 0 | 39
38889.4944 | 1 | 0 | 39
38889.4948 | 1 | 0 | 39
38889.4952 | 1 | 0 | 39
38889.4957 | 1 | 0 | 39
38889.4961 | 1 | 0 | 39
38889.4965 | 1 | 0 | 39
38889.497 | 1 | 0 | 39
38889.4974 | 1 | 0 | 39
38889.4978 | 1 | 0 | 39
38889.4983 | 1 | 0 | 39
38889.4987 | 1 | 0 | 39
38889.4992 | 1 | 0 | 39
38889.4996 | 1 | 0 | 39
38889.5 | 1 | 0 | 39
38889.5005 | 2 | 0 | 39
38889.5009 | 2 | 0 | 39
38889.5014 | 1 | 0 | 39
38889.5018 | 1 | 0 | 39
38889.5022 | 1 | 0 | 39
38889.5027 | 1 | 0 | 39
38889.5031 | 1 | 1 | 39
38889.5035 | 1 | 0 | 39
38889.504 | 1 | 0 | 39
38889.5044 | 1 | 0 | 39
38889.5048 | 1 | 0 | 39
38889.5053 | 1 | 0 | 39
38889.5057 | 1 | 0 | 39
38889.5062 | 1 | 0 | 39
38889.5066 | 1 | 0 | 39
38889.507 | 1 | 0 | 39
38889.5075 | 1 | 0 | 39
38889.5079 | 1 | 0 | 39
38889.5083 | 1 | 0 | 39
38889.5088 | 1 | 0 | 39
38889.5092 | 1 | 0 | 39
38889.5097 | 1 | 0 | 39
38889.5101 | 1 | 0 | 39
38889.5105 | 1 | 0 | 39
38889.511 | 1 | 0 | 39
38889.5114 | 1 | 0 | 39
38889.5119 | 1 | 0 | 39
38889.5123 | 2 | 0 | 39
38889.5127 | 1 | 0 | 39
38889.5132 | 1 | 0 | 39
38889.5136 | 1 | 0 | 39
38889.4878 | 1 | 0 | 40
38889.4882 | 1 | 0 | 40
38889.4887 | 1 | 0 | 40
38889.4891 | 1 | 0 | 40
38889.4895 | 1 | 0 | 40
38889.49 | 1 | 0 | 40
38889.4904 | 1 | 0 | 40
38889.4909 | 1 | 0 | 40
38889.4913 | 1 | 0 | 40
38889.4917 | 1 | 0 | 40
38889.4922 | 1 | 0 | 40
38889.4926 | 1 | 0 | 40
38889.4931 | 1 | 0 | 40
38889.4935 | 1 | 0 | 40
38889.4939 | 1 | 0 | 40
38889.4944 | 1 | 0 | 40
38889.4948 | 1 | 0 | 40
38889.4952 | 1 | 0 | 40
38889.4957 | 1 | 0 | 40
38889.4961 | 1 | 0 | 40
38889.4966 | 1 | 0 | 40
38889.497 | 1 | 0 | 40
38889.4974 | 1 | 0 | 40
38889.4979 | 1 | 0 | 40
38889.4983 | 1 | 0 | 40
38889.4987 | 1 | 0 | 40
38889.4992 | 2158 | 0 | 40
38889.4996 | 2376 | 0 | 40
38889.5 | 2521 | 0 | 40
38889.5005 | 2348 | 0 | 40
38889.5009 | 2485 | 0 | 40
38889.5014 | 2015 | 0 | 40
38889.5018 | 2566 | 0 | 40
38889.5022 | 2533 | 0 | 40
38889.5027 | 2084 | 0 | 40
38889.5031 | 2574 | 0 | 40
38889.5036 | 2011 | 0 | 40
38889.504 | 2295 | 0 | 40
38889.5044 | 2522 | 0 | 40
38889.5049 | 1983 | 0 | 40
38889.5053 | 2364 | 0 | 40
38889.5057 | 2567 | 0 | 40
38889.5062 | 2490 | 0 | 40
38889.5066 | 2130 | 0 | 40
38889.507 | 1984 | 0 | 40
38889.5075 | 2252 | 0 | 40
38889.5079 | 2382 | 0 | 40
38889.5084 | 2111 | 0 | 40
38889.5088 | 2449 | 0 | 40
38889.5092 | 2074 | 0 | 40
38889.5097 | 2413 | 0 | 40
38889.5101 | 2084 | 0 | 40
38889.5105 | 2392 | 0 | 40
38889.511 | 2342 | 0 | 40
38889.5114 | 2539 | 0 | 40
38889.5119 | 2283 | 0 | 40
38889.5123 | 2155 | 0 | 40
38889.5127 | 1856 | 0 | 40
38889.5132 | 2087 | 0 | 40
38889.5136 | 1935 | 0 | 40
38889.4878 | 1 | 0 | 41
38889.4883 | 1 | 0 | 41
38889.4887 | 1 | 0 | 41
38889.4891 | 2 | 0 | 41
38889.4896 | 1 | 0 | 41
38889.49 | 1 | 0 | 41
38889.4904 | 2 | 0 | 41
38889.4909 | 1 | 0 | 41
38889.4913 | 1 | 0 | 41
38889.4917 | 1 | 0 | 41
38889.4922 | 1 | 0 | 41
38889.4926 | 1 | 0 | 41
38889.4931 | 1 | 0 | 41
38889.4935 | 1 | 0 | 41
38889.4939 | 1 | 0 | 41
38889.4944 | 1 | 0 | 41
38889.4948 | 1 | 0 | 41
38889.4952 | 1 | 0 | 41
38889.4957 | 1 | 0 | 41
38889.4961 | 1 | 0 | 41
38889.4966 | 2 | 0 | 41
38889.497 | 1 | 0 | 41
38889.4974 | 1 | 0 | 41
38889.4979 | 1 | 0 | 41
38889.4983 | 1 | 0 | 41
38889.4987 | 1 | 0 | 41
38889.4992 | 3 | 0 | 41
38889.4996 | 2 | 0 | 41
38889.5001 | 1 | 0 | 41
38889.5005 | 2 | 0 | 41
38889.5009 | 2 | 0 | 41
38889.5014 | 2 | 0 | 41
38889.5018 | 2 | 0 | 41
38889.5022 | 2 | 0 | 41
38889.5027 | 2 | 0 | 41
38889.5031 | 2 | 0 | 41
38889.5036 | 2 | 0 | 41
38889.504 | 2 | 0 | 41
38889.5044 | 2 | 0 | 41
38889.5049 | 2 | 0 | 41
38889.5053 | 2 | 0 | 41
38889.5057 | 2 | 0 | 41
38889.5062 | 1 | 0 | 41
38889.5066 | 2 | 0 | 41
38889.5071 | 2 | 0 | 41
38889.5075 | 2 | 0 | 41
38889.5079 | 1 | 0 | 41
38889.5084 | 2 | 0 | 41
38889.5088 | 2 | 0 | 41
38889.5092 | 2 | 0 | 41
38889.5097 | 2 | 0 | 41
38889.5101 | 2 | 0 | 41
38889.5106 | 2 | 0 | 41
38889.511 | 1 | 0 | 41
38889.5114 | 2 | 0 | 41
38889.5119 | 2 | 0 | 41
38889.5123 | 1 | 0 | 41
38889.5127 | 1 | 0 | 41
38889.5132 | 2 | 0 | 41
38889.5136 | 2 | 0 | 41
38889.4878 | 1 | 0 | 42
38889.4883 | 1 | 0 | 42
38889.4887 | 1 | 0 | 42
38889.4891 | 2 | 0 | 42
38889.4896 | 1 | 0 | 42
38889.49 | 1 | 0 | 42
38889.4905 | 1 | 0 | 42
38889.4909 | 1 | 0 | 42
38889.4913 | 1 | 0 | 42
38889.4918 | 1 | 0 | 42
38889.4922 | 1 | 0 | 42
38889.4926 | 1 | 0 | 42
38889.4931 | 1 | 0 | 42
38889.4935 | 1 | 0 | 42
38889.4939 | 1 | 0 | 42
38889.4944 | 1 | 0 | 42
38889.4948 | 1 | 0 | 42
38889.4953 | 1 | 0 | 42
38889.4957 | 1 | 0 | 42
38889.4961 | 1 | 0 | 42
38889.4966 | 1 | 0 | 42
38889.497 | 1 | 0 | 42
38889.4974 | 1 | 0 | 42
38889.4979 | 1 | 0 | 42
38889.4983 | 1 | 0 | 42
38889.4988 | 1 | 1 | 42
38889.4992 | 2443 | 0 | 42
38889.4996 | 2416 | 0 | 42
38889.5001 | 2167 | 0 | 42
38889.5005 | 2566 | 0 | 42
38889.5009 | 2551 | 0 | 42
38889.5014 | 2032 | 0 | 42
38889.5018 | 2285 | 0 | 42
38889.5023 | 2182 | 0 | 42
38889.5027 | 2008 | 0 | 42
38889.5031 | 2575 | 0 | 42
38889.5036 | 2389 | 0 | 42
38889.504 | 2322 | 0 | 42
38889.5044 | 2079 | 0 | 42
38889.5049 | 2056 | 0 | 42
38889.5053 | 2036 | 0 | 42
38889.5058 | 2483 | 0 | 42
38889.5062 | 2453 | 0 | 42
38889.5066 | 2061 | 0 | 42
38889.5071 | 2098 | 0 | 42
38889.5075 | 2228 | 0 | 42
38889.5079 | 2022 | 0 | 42
38889.5084 | 2522 | 0 | 42
38889.5088 | 2249 | 0 | 42
38889.5093 | 2152 | 0 | 42
38889.5097 | 2169 | 0 | 42
38889.5101 | 2115 | 0 | 42
38889.5106 | 2540 | 0 | 42
38889.511 | 2467 | 0 | 42
38889.5114 | 2092 | 0 | 42
38889.5119 | 2562 | 0 | 42
38889.5123 | 2553 | 0 | 42
38889.5128 | 2165 | 0 | 42
38889.5132 | 1900 | 0 | 42
38889.5136 | 2054 | 0 | 42

## C-G
Average Conductor to Ground Resistances
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-96.1667 | 219174.6667 |  | -88.6667 | 219024.6667 | -83.5 | 219141.3333 | -80.3333 | 219158 | -78.3333 | 219158 | -76.6667 | 219174.6667 | -75.1667 | 258821.3333 | -96.1667 | 219024.6667
-58.3333 | 219174.6667 |  | -50.9167 | 219024.6667 | -46 | 219141.3333 | -42.6667 | 219158 | -40.4167 | 219158 | -38.8333 | 219174.6667 | -37.1667 | 258821.3333 | -58.3333 | 219024.6667
-20.6667 | 219174.6667 |  | -13.1667 | 197504.8333 | -8 | 219141.3333 | -4.8333 | 219158 | -2.5 | 219158 | -1 | 219174.6667 | 0.33333 | 258821.3333 | -20.6667 | 197504.8333
17.0833 | 219174.6667 |  | 24.5833 | 219024.6667 | 29.75 | 201532.8333 | 33.1667 | 219158 | 35.0833 | 219158 | 36.5 | 197579.8333 | 38 | 237226.5 | 17.0833 | 197579.8333
54.9167 | 201566.1667 |  | 62.4167 | 219024.6667 | 67.6667 | 219141.3333 | 70.9167 | 201549.5 | 72.8333 | 219158 | 74.3333 | 219174.6667 | 75.9167 | 258821.3333 | 54.9167 | 201549.5
92.75 | 219174.6667 |  | 100.25 | 219024.6667 | 105.25 | 219141.3333 | 108.5 | 219158 | 110.6667 | 219158 | 112.25 | 219174.6667 | 113.8333 | 258821.3333 | 92.75 | 219024.6667
130.5833 | 219174.6667 |  | 138 | 219024.6667 | 143 | 219141.3333 | 146.25 | 197571.5 | 148.5833 | 219158 | 150.1667 | 179971.3333 | 151.75 | 237234.8333 | 130.5833 | 179971.3333
168.3333 | 219174.6667 |  | 175.8333 | 219024.6667 | 181 | 219141.3333 | 184.1667 | 219158 | 186.5 | 219158 | 188 | 219174.6667 | 189.3333 | 258821.3333 | 168.3333 | 219024.6667
206.1667 | 219174.6667 |  | 213.5833 | 219024.6667 | 218.75 | 219141.3333 | 222.1667 | 219158 | 224.1667 | 219158 | 225.5 | 219174.6667 | 227 | 258821.3333 | 206.1667 | 219024.6667
243.9167 | 219174.6667 |  | 251.5 | 219024.6667 | 256.5833 | 219141.3333 | 260 | 219158 | 261.75 | 219158 | 263.3333 | 219174.6667 | 264.9167 | 258821.3333 | 243.9167 | 219024.6667
281.8333 | 219174.6667 |  | 289.3333 | 219024.6667 | 294.5 | 219141.3333 | 297.6667 | 219158 | 299.6667 | 219158 | 301.3333 | 219174.6667 | 302.8333 | 258821.3333 | 281.8333 | 219024.6667
319.5 | 219174.6667 |  | 327.0833 | 219024.6667 | 332 | 219141.3333 | 335.3333 | 219158 | 337.6667 | 219158 | 339.0833 | 219174.6667 | 340.6667 | 258821.3333 | 319.5 | 219024.6667
357.25 | 219174.6667 |  | 364.75 | 219024.6667 | 369.9167 | 219141.3333 | 373.1667 | 219158 | 375.5 | 219158 | 376.8333 | 219174.6667 | 378.25 | 258821.3333 | 357.25 | 219024.6667
395.1667 | 219174.6667 |  | 402.5833 | 219024.6667 | 407.6667 | 219141.3333 | 411.1667 | 219158 | 413.1667 | 201549.5 | 414.4167 | 219174.6667 | 416 | 258821.3333 | 395.1667 | 201549.5
432.9167 | 219174.6667 |  | 440.3333 | 219024.6667 | 445.5 | 219141.3333 | 448.8333 | 219158 | 450.6667 | 219158 | 452.3333 | 201566.1667 | 453.9167 | 258821.3333 | 432.9167 | 201566.1667
470.6667 | 219174.6667 |  | 478.1667 | 219024.6667 | 483.0833 | 219141.3333 | 486.4167 | 219158 | 488.6667 | 219158 | 490.1667 | 219174.6667 | 491.8333 | 258821.3333 | 470.6667 | 219024.6667
508.4167 | 219174.6667 |  | 515.9167 | 201416.1667 | 521 | 219141.3333 | 524.25 | 219158 | 526.5833 | 219158 | 528.0833 | 219174.6667 | 529.5833 | 258821.3333 | 508.4167 | 201416.1667
546.25 | 219174.6667 |  | 553.6667 | 219024.6667 | 558.8333 | 219141.3333 | 562.1667 | 219158 | 564.4167 | 219158 | 565.75 | 219174.6667 | 567.0833 | 258821.3333 | 546.25 | 219024.6667
584.0833 | 219174.6667 |  | 591.5833 | 219024.6667 | 596.75 | 219141.3333 | 600.1667 | 219158 | 602.0833 | 219158 | 603.5 | 219174.6667 | 605 | 258821.3333 | 584.0833 | 219024.6667
621.8333 | 219174.6667 |  | 629.4167 | 219024.6667 | 634.5833 | 219141.3333 | 637.8333 | 219158 | 639.75 | 219158 | 641.3333 | 219174.6667 | 642.9167 | 258821.3333 | 621.8333 | 219024.6667
659.75 | 219174.6667 |  | 667.25 | 219024.6667 | 672.1667 | 219141.3333 | 675.3333 | 201549.5 | 677.6667 | 201549.5 | 679.1667 | 179971.3333 | 680.8333 | 258821.3333 | 659.75 | 179971.3333
697.5 | 219174.6667 |  | 705 | 219024.6667 | 710 | 219141.3333 | 713.25 | 219158 | 715.5833 | 219158 | 717.0833 | 219174.6667 | 718.5833 | 258821.3333 | 697.5 | 219024.6667
735.1667 | 219174.6667 |  | 742.6667 | 219024.6667 | 747.9167 | 219141.3333 | 751.1667 | 219158 | 753.4167 | 219158 | 754.6667 | 219174.6667 | 756.1667 | 258821.3333 | 735.1667 | 219024.6667
773.0833 | 219174.6667 |  | 780.5833 | 201416.1667 | 785.75 | 219141.3333 | 789.1667 | 219158 | 791 | 201549.5 | 792.4167 | 219174.6667 | 794 | 237226.5 | 773.0833 | 201416.1667
810.8333 | 219174.6667 |  | 818.4167 | 219024.6667 | 823.5833 | 219141.3333 | 826.8333 | 219158 | 828.75 | 201549.5 | 830.3333 | 219174.6667 | 831.9167 | 258821.3333 | 810.8333 | 201549.5
848.75 | 219174.6667 |  | 856.1667 | 219024.6667 | 861.0833 | 219141.3333 | 864.3333 | 219158 | 866.6667 | 219158 | 868.1667 | 201566.1667 | 869.8333 | 237226.5 | 848.75 | 201566.1667
886.3333 | 219174.6667 |  | 893.8333 | 219024.6667 | 899 | 219141.3333 | 902.25 | 219158 | 904.5833 | 201549.5 | 906 | 190381.5556 | 907.3333 | 13.6799 | 886.3333 | 13.6799
924.1667 | 201566.1667 |  | 931.75 | 201416.1667 | 936.9167 | 201532.8333 | 940.1667 | 201549.5 | 942.4167 | 201549.5 | 943.75 | 197579.8333 | 945.1667 | 16.9313 | 924.1667 | 16.9313
962 | 201566.1667 |  | 969.5 | 179896.3333 | 974.6667 | 201532.8333 | 978.1667 | 183941 | 979.9167 | 219158 | 981.4167 | 219174.6667 | 983 | 15.1454 | 962 | 15.1454
999.8333 | 201566.1667 |  | 1007.3333 | 201416.1667 | 1012.5833 | 201532.8333 | 1015.75 | 201549.5 | 1017.75 | 179963 | 1019.3333 | 197579.8333 | 1020.9167 | 12.271 | 999.8333 | 12.271
1037.6667 | 201566.1667 |  | 1045.1667 | 201416.1667 | 1050.0833 | 201532.8333 | 1053.5 | 201549.5 | 1055.6667 | 156485 | 1057.25 | 179971.3333 | 1058.8333 | 9.2552 | 1037.6667 | 9.2552
1075.25 | 201566.1667 |  | 1082.75 | 201416.1667 | 1088 | 183924.3333 | 1091.1667 | 219158 | 1093.5 | 201549.5 | 1094.8333 | 197579.8333 | 1096.3333 | 17.6142 | 1075.25 | 17.6142
1113.1667 | 179971.3333 |  | 1120.6667 | 201416.1667 | 1125.8333 | 162227.844 | 1129.1667 | 219158 | 1131.3333 | 201549.5 | 1132.6667 | 197579.8333 | 1134 | 12.8205 | 1113.1667 | 12.8205
1150.9167 | 184166.6812 |  | 1158.4167 | 198044.778 | 1163.75 | 201532.8333 | 1167.0833 | 201549.5 | 1168.8333 | 201549.5 | 1170.4167 | 197579.8333 | 1171.9167 | 11.1646 | 1150.9167 | 11.1646
1188.75 | 186812.3104 |  | 1196.25 | 173850.5692 | 1201.3333 | 201532.8333 | 1204.6667 | 201549.5 | 1206.6667 | 201549.5 | 1208.3333 | 197579.8333 | 1209.8333 | 13.6705 | 1188.75 | 13.6705
1226.6667 | 74493433.0678 |  | 1234.25 | 169284.3734 | 1239 | 201532.8333 | 1242.3333 | 219158 | 1244.6667 | 158667.7979 | 1246.1667 | 197579.8333 | 1247.75 | 10.2013 | 1226.6667 | 10.2013
1264.3333 | 74492863.2248 |  | 1271.8333 | 154354.5982 | 1276.9167 | 201532.8333 | 1280.25 | 183941 | 1282.5 | 183941 | 1283.9167 | 197579.8333 | 1285.25 | 17.4392 | 1264.3333 | 17.4392
1302.1667 | 185954.9678 |  | 1309.6667 | 166920.9455 | 1314.8333 | 183924.3333 | 1318.1667 | 201549.5 | 1320.3333 | 219158 | 1321.6667 | 197579.8333 | 1323 | 12.0657 | 1302.1667 | 12.0657
1339.9167 | 74492637.7136 |  | 1347.4167 | 166263.8595 | 1352.6667 | 219141.3333 | 1356 | 183941 | 1357.8333 | 219158 | 1359.3333 | 197579.8333 | 1361 | 18.6219 | 1339.9167 | 18.6219
1377.8333 | 184183.5689 |  | 1385.3333 | 184185.2303 | 1390.5 | 219141.3333 | 1393.6667 | 201549.5 | 1395.6667 | 201549.5 | 1397.3333 | 197579.8333 | 1398.8333 | 16.017 | 1377.8333 | 16.017
1415.6667 | 184580.8017 |  | 1423.1667 | 173292.8391 | 1428 | 219141.3333 | 1431.3333 | 219158 | 1433.6667 | 201549.5 | 1435.0833 | 197579.8333 | 1436.75 | 20.8562 | 1415.6667 | 20.8562
1453.3333 | 183978.8729 |  | 1460.75 | 166220.9359 | 1465.9167 | 219141.3333 | 1469.25 | 219158 | 1471.4167 | 201549.5 | 1472.8333 | 197579.8333 | 1474.1667 | 6.5801 | 1453.3333 | 6.5801
1491.0833 | 74492615.7525 |  | 1498.6667 | 183855.8845 | 1503.8333 | 201532.8333 | 1507.1667 | 219158 | 1509.1667 | 201549.5 | 1510.5833 | 219174.6667 | 1512 | 13.0631 | 1491.0833 | 13.0631
1529 | 174067.0934 |  | 1536.5 | 166797.7392 | 1541.6667 | 201532.8333 | 1545.0833 | 183941 | 1546.8333 | 201549.5 | 1548.3333 | 179971.3333 | 1549.9167 | 20.1546 | 1529 | 20.1546
1566.8333 | 184217.4219 |  | 1574.3333 | 166624.1987 | 1579.5 | 201532.8333 | 1582.5833 | 201549.5 | 1584.6667 | 201549.5 | 1586.25 | 197579.8333 | 1587.8333 | 16.1964 | 1566.8333 | 16.1964
1604.5833 | 74493869.6733 |  | 1612 | 74440963.3847 | 1617 | 201532.8333 | 1620.25 | 148814.3476 | 1622.6667 | 201549.5 | 1624.25 | 197579.8333 | 1625.75 | 17.9634 | 1604.5833 | 17.9634
1642.25 | 74457713.4193 |  | 1649.8333 | 74440418.553 | 1654.9167 | 183924.3333 | 1658.1667 | 131211.6932 | 1660.5 | 201549.5 | 1661.9167 | 219174.6667 | 1663.25 | 23.7693 | 1642.25 | 23.7693
1680.1667 | 184523.9085 |  | 1687.5833 | 185635.798 | 1692.75 | 179954.6667 | 1696.1667 | 166303.0672 | 1698.0833 | 166375.489 | 1699.4167 | 197579.8333 | 1701 | 9.1701 | 1680.1667 | 9.1701
1717.9167 | 74492947.3319 |  | 1725.4167 | 169185.7955 | 1730.5833 | 201532.8333 | 1733.9167 | 74501207.8454 | 1735.75 | 149511.9805 | 1737.3333 | 197579.8333 | 1738.9167 | 17.9507 | 1717.9167 | 17.9507
1755.75 | 74493445.7084 |  | 1763.25 | 170544.7735 | 1768.3333 | 219141.3333 | 1771.5833 | 74492573.9385 | 1773.6667 | 166356.6658 | 1775.25 | 197579.8333 | 1776.8333 | 18.4068 | 1755.75 | 18.4068
1831.25 | 169947.745 |  | 1838.75 | 167003.6083 | 1825 | 201532.8333 | 1828.25 | 183972.7235 | 1824.25 | 166368.3341 | 1825.5833 | 179971.3333 | 1827.0833 | 11.1227 | 1831.25 | 11.1227
1869.0833 | 184170.7363 |  | 1876.5 | 184127.8471 | 1862.9167 | 183924.3333 | 1866.1667 | 74492626.7071 | 1861.8333 | 166427.9327 | 1863.3333 | 197579.8333 | 1864.8333 | 23.2928 | 1869.0833 | 23.2928
1907 | 74492665.1374 |  | 1914.4167 | 166331.9031 | 1900.75 | 201532.8333 | 1903.9167 | 184003.9143 | 1899.5 | 166397.5334 | 1901.0833 | 197579.8333 | 1902.6667 | 9.846 | 1907 | 9.846
1944.75 | 166377.4531 |  | 1952.25 | 166230.2942 | 1938.25 | 183924.3333 | 1941.5 | 185805.7019 | 1937.4167 | 167428.2898 | 1939 | 219174.6667 | 1940.5 | 19.9462 | 1944.75 | 19.9462
1982.3333 | 184074.9059 |  | 1989.8333 | 183957.8239 | 1976 | 201532.8333 | 1979.3333 | 74493255.8502 | 1975.3333 | 198307.5315 | 1976.8333 | 197579.8333 | 1978.1667 | 15.154 | 1982.3333 | 15.154
2032.9167 | 184168.1419 |  | 2040.3333 | 166667.3024 | 2014 | 219141.3333 | 2017.1667 | 74492574.16 | 2013.1667 | 166360.0659 | 2014.4167 | 197579.8333 | 2016 | 13.0114 | 2032.9167 | 13.0114
[5 empty] | 2051.9167 | 219141.3333 | 2055.1667 | 183988.5997 | 2050.8333 | 144801.1303 | 2052.3333 | 219174.6667 | 2053.75 | 15.7312
[5 empty] | 2089.6667 | 201532.8333 | 2093 | 74492724.9763 | 2088.5 | 160733.2812 | 2090 | 219174.6667 | 2091.6667 | 29.4865
[5 empty] | 2127 | 201532.8333 | 2130.5 | 74492930.3495 | 2126.3333 | 186505.4709 | 2128 | 179971.3333 | 2129.5 | 27.0613

## C-C
Conductor to Conductor Resistances
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-100.5 | 211201.9994 | -98.5 | 211201.9994 | -97.5 | 211201.9994 | -95.5 | 211201.9994 | -93.5 | 211201.9994 | -91.5 | 259037.9994 | -89.5 | 211201.9994 | -88.5 | 211201.9994 | -86.5 | 211201.9994 | -84.5 | 211201.9994 | -82.5 | 258137.9994 | -80.5 | 211201.9994 | -79.5 | 211201.9994 | -77.5 | 211201.9994 | -75.5 | 258837.9994 | -73.5 | 211201.9994 | -71.5 | 211201.9994 | -70.5 | 258937.9994 | -68.5 | 211201.9994 | -66.5 | 258937.9994 | -64.5 | 259037.9994 | -100.5 | 211201.9994
-62.5 | 211201.9994 | -61.5 | 211201.9994 | -59.5 | 211201.9994 | -57.5 | 211201.9994 | -55.5 | 211201.9994 | -53.5 | 259037.9994 | -52.5 | 211201.9994 | -50.5 | 211201.9994 | -49 | 211201.9994 | -46.5 | 211201.9994 | -44.5 | 258137.9994 | -43.5 | 211201.9994 | -41.5 | 211201.9994 | -39.5 | 211201.9994 | -37.5 | 258837.9994 | -35.5 | 211201.9994 | -34.5 | 211201.9994 | -32.5 | 258937.9994 | -30.5 | 211201.9994 | -28.5 | 258937.9994 | -26.5 | 259037.9994 | -62.5 | 211201.9994
-25.5 | 211201.9994 | -23.5 | 211201.9994 | -21.5 | 211201.9994 | -19.5 | 211201.9994 | -17.5 | 211201.9994 | -16.5 | 259037.9994 | -14.5 | 211201.9994 | -12.5 | 211201.9994 | -10.5 | 211201.9994 | -8.5 | 211201.9994 | -7.5 | 129018.9988 | -5.5 | 211201.9994 | -3.5 | 211201.9994 | -1.5 | 211201.9994 | 0.5 | 258837.9994 | 1.5 | 211201.9994 | 3.5 | 211201.9994 | 5.5 | 258937.9994 | 7.5 | 211201.9994 | 9.5 | 258937.9994 | 10.5 | 259037.9994 | -25.5 | 129018.9988
12.5 | 211201.9994 | 14.5 | 211201.9994 | 16.5 | 211201.9994 | 18 | 211201.9994 | 19.5 | 211201.9994 | 21.5 | 259037.9994 | 23.5 | 211201.9994 | 25.5 | 211201.9994 | 27 | 211201.9994 | 28.5 | 211201.9994 | 30.5 | 258137.9994 | 32.5 | 211201.9994 | 34.5 | 211201.9994 | 36 | 105550.9988 | 37.5 | 258837.9994 | 39.5 | 211201.9994 | 41.5 | 211201.9994 | 43.5 | 258937.9994 | 45 | 211201.9994 | 46.5 | 258937.9994 | 48.5 | 129468.9988 | 12.5 | 105550.9988
50.5 | 211201.9994 | 52.5 | 105550.9988 | 54 | 211201.9994 | 55.5 | 211201.9994 | 57.5 | 211201.9994 | 59.5 | 259037.9994 | 61.5 | 211201.9994 | 63 | 211201.9994 | 64.5 | 211201.9994 | 66.5 | 211201.9994 | 68.5 | 258137.9994 | 70.5 | 211201.9994 | 72.5 | 211201.9994 | 73.5 | 211201.9994 | 75.5 | 258837.9994 | 77.5 | 211201.9994 | 79.5 | 211201.9994 | 81 | 258937.9994 | 82.5 | 211201.9994 | 84.5 | 258937.9994 | 86.5 | 259037.9994 | 50.5 | 105550.9988
88.5 | 211201.9994 | 90 | 211201.9994 | 91.5 | 211201.9994 | 93.5 | 211201.9994 | 95.5 | 211201.9994 | 97.5 | 259037.9994 | 99 | 211201.9994 | 100.5 | 211201.9994 | 102.5 | 211201.9994 | 104.5 | 211201.9994 | 106.5 | 258137.9994 | 108 | 211201.9994 | 109.5 | 211201.9994 | 111.5 | 211201.9994 | 113.5 | 258837.9994 | 115.5 | 211201.9994 | 117 | 211201.9994 | 118.5 | 258937.9994 | 120.5 | 211201.9994 | 122.5 | 258937.9994 | 124.5 | 259037.9994 | 88.5 | 211201.9994
126 | 211201.9994 | 127.5 | 211201.9994 | 129.5 | 211201.9994 | 131.5 | 211201.9994 | 133.5 | 211201.9994 | 135.5 | 259037.9994 | 136.5 | 211201.9994 | 138.5 | 211201.9994 | 140.5 | 211201.9994 | 142.5 | 211201.9994 | 144 | 258137.9994 | 145.5 | 211201.9994 | 147.5 | 211201.9994 | 149.5 | 211201.9994 | 151.5 | 258837.9994 | 153 | 211201.9994 | 154.5 | 211201.9994 | 156.5 | 129418.9988 | 158.5 | 211201.9994 | 160.5 | 258937.9994 | 162.5 | 129468.9988 | 126 | 129418.9988
163.5 | 211201.9994 | 165.5 | 211201.9994 | 167.5 | 211201.9994 | 169.5 | 211201.9994 | 171.5 | 211201.9994 | 172.5 | 259037.9994 | 174.5 | 211201.9994 | 176.5 | 211201.9994 | 178.5 | 211201.9994 | 180.5 | 211201.9994 | 181.5 | 258137.9994 | 183.5 | 211201.9994 | 185.5 | 211201.9994 | 187.5 | 211201.9994 | 189.5 | 258837.9994 | 190.5 | 211201.9994 | 192.5 | 211201.9994 | 194.5 | 258937.9994 | 196.5 | 211201.9994 | 198.5 | 258937.9994 | 199.5 | 259037.9994 | 163.5 | 211201.9994
201.5 | 211201.9994 | 203.5 | 211201.9994 | 205.5 | 211201.9994 | 207.5 | 211201.9994 | 208.5 | 211201.9994 | 210.5 | 259037.9994 | 212.5 | 211201.9994 | 214.5 | 211201.9994 | 216 | 211201.9994 | 217.5 | 211201.9994 | 219.5 | 258137.9994 | 221.5 | 211201.9994 | 223.5 | 211201.9994 | 225 | 211201.9994 | 226.5 | 258837.9994 | 228.5 | 211201.9994 | 230.5 | 211201.9994 | 232.5 | 258937.9994 | 234 | 211201.9994 | 235.5 | 258937.9994 | 237.5 | 259037.9994 | 201.5 | 211201.9994
239.5 | 211201.9994 | 241.5 | 211201.9994 | 243 | 211201.9994 | 244.5 | 211201.9994 | 246.5 | 211201.9994 | 248.5 | 259037.9994 | 250.5 | 211201.9994 | 252.5 | 211201.9994 | 253.5 | 211201.9994 | 255.5 | 211201.9994 | 257.5 | 258137.9994 | 259.5 | 211201.9994 | 261 | 211201.9994 | 262.5 | 211201.9994 | 264.5 | 258837.9994 | 266.5 | 211201.9994 | 268.5 | 211201.9994 | 270 | 258937.9994 | 271.5 | 211201.9994 | 273.5 | 258937.9994 | 275.5 | 259037.9994 | 239.5 | 211201.9994
277.5 | 211201.9994 | 279.5 | 211201.9994 | 280.5 | 211201.9994 | 282.5 | 211201.9994 | 284.5 | 211201.9994 | 286.5 | 259037.9994 | 288.5 | 211201.9994 | 289.5 | 211201.9994 | 291.5 | 211201.9994 | 293.5 | 211201.9994 | 295.5 | 258137.9994 | 297.5 | 211201.9994 | 298.5 | 211201.9994 | 300.5 | 211201.9994 | 302.5 | 258837.9994 | 304.5 | 211201.9994 | 306.5 | 211201.9994 | 307.5 | 258937.9994 | 309.5 | 211201.9994 | 311.5 | 258937.9994 | 313.5 | 259037.9994 | 277.5 | 211201.9994
315 | 211201.9994 | 316.5 | 211201.9994 | 318.5 | 211201.9994 | 320.5 | 211201.9994 | 322.5 | 211201.9994 | 324 | 259037.9994 | 325.5 | 211201.9994 | 327.5 | 211201.9994 | 329.5 | 211201.9994 | 331.5 | 211201.9994 | 333.5 | 258137.9994 | 334.5 | 211201.9994 | 336.5 | 211201.9994 | 338.5 | 211201.9994 | 340.5 | 258837.9994 | 342.5 | 211201.9994 | 343.5 | 211201.9994 | 345.5 | 258937.9994 | 347.5 | 211201.9994 | 349.5 | 258937.9994 | 351 | 259037.9994 | 315 | 211201.9994
352.5 | 211201.9994 | 354.5 | 211201.9994 | 356.5 | 211201.9994 | 358.5 | 211201.9994 | 360 | 211201.9994 | 361.5 | 259037.9994 | 363.5 | 211201.9994 | 365.5 | 211201.9994 | 367.5 | 211201.9994 | 369 | 211201.9994 | 370.5 | 258137.9994 | 372.5 | 211201.9994 | 374.5 | 211201.9994 | 376.5 | 211201.9994 | 378 | 258837.9994 | 379.5 | 211201.9994 | 381.5 | 211201.9994 | 383.5 | 258937.9994 | 385.5 | 211201.9994 | 387.5 | 258937.9994 | 388.5 | 259037.9994 | 352.5 | 211201.9994
390.5 | 211201.9994 | 392.5 | 211201.9994 | 394.5 | 211201.9994 | 396.5 | 211201.9994 | 397.5 | 211201.9994 | 399.5 | 259037.9994 | 401.5 | 211201.9994 | 403.5 | 211201.9994 | 405 | 211201.9994 | 406.5 | 211201.9994 | 408.5 | 258137.9994 | 410.5 | 211201.9994 | 412.5 | 211201.9994 | 413.5 | 211201.9994 | 415.5 | 258837.9994 | 417.5 | 211201.9994 | 419.5 | 211201.9994 | 421.5 | 258937.9994 | 423 | 211201.9994 | 424.5 | 258937.9994 | 426.5 | 259037.9994 | 390.5 | 211201.9994
428.5 | 211201.9994 | 430.5 | 211201.9994 | 432 | 211201.9994 | 433.5 | 211201.9994 | 435.5 | 211201.9994 | 437.5 | 259037.9994 | 439.5 | 211201.9994 | 440.5 | 211201.9994 | 442.5 | 211201.9994 | 444.5 | 211201.9994 | 446.5 | 258137.9994 | 448.5 | 211201.9994 | 449.5 | 211201.9994 | 451.5 | 211201.9994 | 453.5 | 258837.9994 | 455.5 | 211201.9994 | 457.5 | 211201.9994 | 459 | 258937.9994 | 460.5 | 211201.9994 | 462.5 | 258937.9994 | 464.5 | 259037.9994 | 428.5 | 211201.9994
466.5 | 211201.9994 | 467.5 | 211201.9994 | 469.5 | 211201.9994 | 471.5 | 211201.9994 | 473.5 | 211201.9994 | 475.5 | 259037.9994 | 476.5 | 211201.9994 | 478.5 | 211201.9994 | 480.5 | 211201.9994 | 482.5 | 211201.9994 | 484.5 | 258137.9994 | 486 | 211201.9994 | 487.5 | 211201.9994 | 489.5 | 211201.9994 | 491.5 | 258837.9994 | 493.5 | 211201.9994 | 494.5 | 211201.9994 | 496.5 | 258937.9994 | 498.5 | 211201.9994 | 500.5 | 258937.9994 | 502.5 | 259037.9994 | 466.5 | 211201.9994
503.5 | 211201.9994 | 505.5 | 211201.9994 | 507.5 | 211201.9994 | 509.5 | 211201.9994 | 511.5 | 211201.9994 | 513 | 259037.9994 | 514.5 | 105550.9988 | 516.5 | 211201.9994 | 518.5 | 211201.9994 | 520.5 | 211201.9994 | 522 | 258137.9994 | 523.5 | 211201.9994 | 525.5 | 211201.9994 | 527.5 | 211201.9994 | 529.5 | 258837.9994 | 531 | 211201.9994 | 532.5 | 211201.9994 | 534.5 | 258937.9994 | 536.5 | 211201.9994 | 538.5 | 258937.9994 | 540 | 259037.9994 | 503.5 | 105550.9988
541.5 | 211201.9994 | 543.5 | 211201.9994 | 545.5 | 211201.9994 | 547.5 | 211201.9994 | 549 | 211201.9994 | 550.5 | 259037.9994 | 552.5 | 211201.9994 | 554.5 | 211201.9994 | 556.5 | 211201.9994 | 557.5 | 211201.9994 | 559.5 | 258137.9994 | 561.5 | 211201.9994 | 563.5 | 211201.9994 | 565.5 | 211201.9994 | 566.5 | 258837.9994 | 568.5 | 211201.9994 | 570.5 | 211201.9994 | 572.5 | 258937.9994 | 574.5 | 211201.9994 | 576 | 258937.9994 | 577.5 | 259037.9994 | 541.5 | 211201.9994
579.5 | 211201.9994 | 581.5 | 211201.9994 | 583.5 | 211201.9994 | 585 | 211201.9994 | 586.5 | 211201.9994 | 588.5 | 259037.9994 | 590.5 | 211201.9994 | 592.5 | 211201.9994 | 594 | 211201.9994 | 595.5 | 211201.9994 | 597.5 | 258137.9994 | 599.5 | 211201.9994 | 601.5 | 211201.9994 | 603 | 211201.9994 | 604.5 | 258837.9994 | 606.5 | 211201.9994 | 608.5 | 211201.9994 | 610.5 | 258937.9994 | 612 | 211201.9994 | 613.5 | 258937.9994 | 615.5 | 259037.9994 | 579.5 | 211201.9994
617.5 | 211201.9994 | 619.5 | 211201.9994 | 620.5 | 211201.9994 | 622.5 | 211201.9994 | 624.5 | 211201.9994 | 626.5 | 259037.9994 | 628.5 | 211201.9994 | 630 | 211201.9994 | 631.5 | 211201.9994 | 633.5 | 211201.9994 | 635.5 | 258137.9994 | 637.5 | 211201.9994 | 639 | 211201.9994 | 640.5 | 211201.9994 | 642.5 | 258837.9994 | 644.5 | 211201.9994 | 646.5 | 211201.9994 | 648 | 258937.9994 | 649.5 | 211201.9994 | 651.5 | 258937.9994 | 653.5 | 259037.9994 | 617.5 | 211201.9994
655.5 | 211201.9994 | 657 | 211201.9994 | 658.5 | 211201.9994 | 660.5 | 211201.9994 | 662.5 | 211201.9994 | 664.5 | 259037.9994 | 666 | 211201.9994 | 667.5 | 211201.9994 | 669.5 | 211201.9994 | 671.5 | 211201.9994 | 673.5 | 258137.9994 | 674.5 | 211201.9994 | 676.5 | 211201.9994 | 678.5 | 211201.9994 | 680.5 | 258837.9994 | 682.5 | 211201.9994 | 683.5 | 211201.9994 | 685.5 | 258937.9994 | 687.5 | 211201.9994 | 689.5 | 258937.9994 | 691.5 | 129468.9988 | 655.5 | 129468.9988
693 | 211201.9994 | 694.5 | 211201.9994 | 696.5 | 211201.9994 | 698.5 | 211201.9994 | 700.5 | 211201.9994 | 702 | 259037.9994 | 703.5 | 211201.9994 | 705.5 | 211201.9994 | 707.5 | 211201.9994 | 709.5 | 211201.9994 | 711 | 258137.9994 | 712.5 | 211201.9994 | 714.5 | 211201.9994 | 716.5 | 211201.9994 | 718.5 | 258837.9994 | 720 | 211201.9994 | 721.5 | 211201.9994 | 723.5 | 258937.9994 | 725.5 | 211201.9994 | 727.5 | 258937.9994 | 729 | 259037.9994 | 693 | 211201.9994
730.5 | 211201.9994 | 732.5 | 211201.9994 | 734.5 | 211201.9994 | 736.5 | 211201.9994 | 737.5 | 211201.9994 | 739.5 | 259037.9994 | 741.5 | 211201.9994 | 743.5 | 211201.9994 | 745.5 | 211201.9994 | 746.5 | 211201.9994 | 748.5 | 258137.9994 | 750.5 | 211201.9994 | 752.5 | 211201.9994 | 754.5 | 211201.9994 | 756 | 258837.9994 | 757.5 | 211201.9994 | 759.5 | 211201.9994 | 761.5 | 258937.9994 | 763.5 | 211201.9994 | 765 | 258937.9994 | 766.5 | 259037.9994 | 730.5 | 211201.9994
768.5 | 211201.9994 | 770.5 | 211201.9994 | 772.5 | 211201.9994 | 774 | 211201.9994 | 775.5 | 211201.9994 | 777.5 | 259037.9994 | 779.5 | 211201.9994 | 781.5 | 211201.9994 | 783 | 211201.9994 | 784.5 | 105550.9988 | 786.5 | 258137.9994 | 788.5 | 211201.9994 | 790.5 | 211201.9994 | 792 | 211201.9994 | 793.5 | 258837.9994 | 795.5 | 211201.9994 | 797.5 | 211201.9994 | 799.5 | 258937.9994 | 800.5 | 211201.9994 | 802.5 | 258937.9994 | 804.5 | 259037.9994 | 768.5 | 105550.9988
806.5 | 211201.9994 | 808.5 | 211201.9994 | 809.5 | 211201.9994 | 811.5 | 211201.9994 | 813.5 | 211201.9994 | 815.5 | 259037.9994 | 817.5 | 211201.9994 | 819 | 211201.9994 | 820.5 | 211201.9994 | 822.5 | 211201.9994 | 824.5 | 258137.9994 | 826.5 | 211201.9994 | 828 | 211201.9994 | 829.5 | 211201.9994 | 831.5 | 258837.9994 | 833.5 | 211201.9994 | 835.5 | 211201.9994 | 837 | 258937.9994 | 838.5 | 105550.9988 | 840.5 | 258937.9994 | 842.5 | 259037.9994 | 806.5 | 105550.9988
844.5 | 211201.9994 | 846 | 211201.9994 | 847.5 | 211201.9994 | 849.5 | 211201.9994 | 851.5 | 211201.9994 | 853.5 | 259037.9994 | 854.5 | 211201.9994 | 856.5 | 211201.9994 | 858.5 | 211201.9994 | 860.5 | 211201.9994 | 862.5 | 258137.9994 | 863.5 | 211201.9994 | 865.5 | 211201.9994 | 867.5 | 211201.9994 | 869.5 | 258837.9994 | 871.5 | 211201.9994 | 872.5 | 211201.9994 | 874.5 | 258937.9994 | 876.5 | 211201.9994 | 878.5 | 258937.9994 | 880.5 | 259037.9994 | 844.5 | 211201.9994
881.5 | 211201.9994 | 883.5 | 211201.9994 | 885.5 | 211201.9994 | 887.5 | 211201.9994 | 889.5 | 211201.9994 | 890.5 | 259037.9994 | 892.5 | 211201.9994 | 894.5 | 211201.9994 | 896.5 | 211201.9994 | 898.5 | 211201.9994 | 899.5 | 258137.9994 | 901.5 | 211201.9994 | 903.5 | 211201.9994 | 905.5 | 211201.9994 | 907.5 | 258837.9994 | 909 | 211201.9994 | 910.5 | 211201.9994 | 912.5 | 258937.9994 | 914.5 | 105550.9988 | 916.5 | 258937.9994 | 917.5 | 86279.3315 | 881.5 | 86279.3315
919.5 | 105550.9988 | 921.5 | 211201.9994 | 923.5 | 211201.9994 | 925.5 | 211201.9994 | 926.5 | 211201.9994 | 928.5 | 259037.9994 | 930.5 | 105550.9988 | 932.5 | 211201.9994 | 934.5 | 211201.9994 | 936 | 211201.9994 | 937.5 | 258137.9994 | 939.5 | 105550.9988 | 941.5 | 211201.9994 | 943.5 | 211201.9994 | 945 | 258837.9994 | 946.5 | 105550.9988 | 948.5 | 211201.9994 | 950.5 | 258937.9994 | 952.5 | 105550.9988 | 954 | 258937.9994 | 955.5 | 129468.9988 | 919.5 | 105550.9988
957.5 | 105550.9988 | 959.5 | 211201.9994 | 961.5 | 211201.9994 | 962.5 | 211201.9994 | 964.5 | 211201.9994 | 966.5 | 259037.9994 | 968.5 | 105550.9988 | 970.5 | 211201.9994 | 971.5 | 211201.9994 | 973.5 | 211201.9994 | 975.5 | 129018.9988 | 977.5 | 105550.9988 | 979.5 | 211201.9994 | 980.5 | 211201.9994 | 982.5 | 258837.9994 | 984.5 | 105550.9988 | 986.5 | 211201.9994 | 988.5 | 258937.9994 | 990 | 211201.9994 | 991.5 | 258937.9994 | 993.5 | 259037.9994 | 957.5 | 105550.9988
995.5 | 105550.9988 | 997.5 | 211201.9994 | 998.5 | 211201.9994 | 1000.5 | 211201.9994 | 1002.5 | 211201.9994 | 1004.5 | 259037.9994 | 1006.5 | 105550.9988 | 1007.5 | 211201.9994 | 1009.5 | 211201.9994 | 1011.5 | 211201.9994 | 1013.5 | 258137.9994 | 1015.5 | 105550.9988 | 1017 | 211201.9994 | 1018.5 | 211201.9994 | 1020.5 | 258837.9994 | 1022.5 | 105550.9988 | 1024.5 | 211201.9994 | 1026 | 258937.9994 | 1027.5 | 105550.9988 | 1029.5 | 129418.9988 | 1031.5 | 129468.9988 | 995.5 | 105550.9988
1033.5 | 105550.9988 | 1034.5 | 211201.9994 | 1036.5 | 211201.9994 | 1038.5 | 211201.9994 | 1040.5 | 211201.9994 | 1042.5 | 259037.9994 | 1043.5 | 211201.9994 | 1045.5 | 211201.9994 | 1047.5 | 211201.9994 | 1049.5 | 105550.9988 | 1051.5 | 258137.9994 | 1053 | 105550.9988 | 1054.5 | 211201.9994 | 1056.5 | 211201.9994 | 1058.5 | 258837.9994 | 1060.5 | 105550.9988 | 1062 | 211201.9994 | 1063.5 | 258937.9994 | 1065.5 | 70333.9982 | 1067.5 | 129418.9988 | 1069.5 | 129468.9988 | 1033.5 | 70333.9982
1070.5 | 105550.9988 | 1072.5 | 211201.9994 | 1074.5 | 211201.9994 | 1076.5 | 211201.9994 | 1078 | 211201.9994 | 1079.5 | 259037.9994 | 1081.5 | 105550.9988 | 1083.5 | 211201.9994 | 1085.5 | 211201.9994 | 1087 | 211201.9994 | 1088.5 | 258137.9994 | 1090.5 | 105550.9988 | 1092.5 | 211201.9994 | 1094.5 | 211201.9994 | 1096.5 | 258837.9994 | 1097.5 | 211201.9994 | 1099.5 | 211201.9994 | 1101.5 | 258937.9994 | 1103.5 | 105550.9988 | 1105.5 | 258937.9994 | 1106.5 | 129468.9988 | 1070.5 | 105550.9988
1108.5 | 105550.9988 | 1110.5 | 211201.9994 | 1112.5 | 211201.9994 | 1114.5 | 211201.9994 | 1115.5 | 211201.9994 | 1117.5 | 129468.9988 | 1119.5 | 105550.9988 | 1121.5 | 211201.9994 | 1123.5 | 211201.9994 | 1124.5 | 211201.9994 | 1126.5 | 258137.9994 | 1128.5 | 105550.9988 | 1130.5 | 211201.9994 | 1132.5 | 211201.9994 | 1133.5 | 21121.6733 | 1135.5 | 211201.9994 | 1137.5 | 211201.9994 | 1139.5 | 258937.9994 | 1141.5 | 105550.9988 | 1142.5 | 258937.9994 | 1144.5 | 129468.9988 | 1108.5 | 21121.6733
1146 | 16.2915 | 1148.5 | 211201.9994 | 1150.5 | 211201.9994 | 1151.5 | 211201.9994 | 1153.5 | 211201.9994 | 1155.5 | 259037.9994 | 1157.5 | 211201.9994 | 1159.5 | 211201.9994 | 1160.5 | 211201.9994 | 1162.5 | 211201.9994 | 1164.5 | 258137.9994 | 1166.5 | 105550.9988 | 1168.5 | 211201.9994 | 1170 | 211201.9994 | 1171.5 | 258837.9994 | 1173.5 | 105550.9988 | 1175.5 | 211201.9994 | 1177 | 258937.9994 | 1178.5 | 105550.9988 | 1180.5 | 258937.9994 | 1182.5 | 129468.9988 | 1146 | 16.2915
1184.5 | 1431.5058 | 1186 | 211201.9994 | 1187.5 | 211201.9994 | 1189.5 | 211201.9994 | 1191.5 | 211201.9994 | 1193.5 | 259037.9994 | 1195 | 105550.9988 | 1196.5 | 211201.9994 | 1198.5 | 211201.9994 | 1200.5 | 211201.9994 | 1202.5 | 258137.9994 | 1204.5 | 105550.9988 | 1205.5 | 211201.9994 | 1207.5 | 211201.9994 | 1209.5 | 258837.9994 | 1211.5 | 105550.9988 | 1213.5 | 211201.9994 | 1214.5 | 258937.9994 | 1216.5 | 105550.9988 | 1218.5 | 258937.9994 | 1220.5 | 129468.9988 | 1184.5 | 1431.5058
1223 | 158.2045 | 1223.5 | 211002.0947 | 1225.5 | 211201.9994 | 1227.5 | 211201.9994 | 1229.5 | 211201.9994 | 1231 | 259037.9994 | 1232.5 | 105550.9988 | 1234.5 | 211201.9994 | 1236.5 | 211201.9994 | 1238.5 | 211201.9994 | 1240.5 | 258137.9994 | 1241.5 | 105550.9988 | 1243.5 | 211201.9994 | 1245.5 | 211201.9994 | 1247.5 | 258837.9994 | 1249.5 | 211201.9994 | 1250.5 | 211201.9994 | 1252.5 | 258937.9994 | 1254.5 | 105550.9988 | 1256.5 | 1636.7353 | 1258.5 | 129468.9988 | 1223 | 158.2045
1259.5 | 3.0466 | 1261.5 | 211002.0947 | 1263.5 | 211201.9994 | 1265.5 | 211201.9994 | 1267.5 | 211201.9994 | 1268.5 | 259037.9994 | 1270.5 | 211201.9994 | 1273 | 211201.9994 | 1274.5 | 211201.9994 | 1276 | 211201.9994 | 1277.5 | 59092.1988 | 1279.5 | 105550.9988 | 1281.5 | 211201.9994 | 1283.5 | 211201.9994 | 1285 | 258837.9994 | 1286.5 | 105550.9988 | 1288.5 | 211201.9994 | 1290.5 | 258937.9994 | 1292.5 | 105550.9988 | 1294.5 | 258937.9994 | 1295.5 | 129468.9988 | 1259.5 | 3.0466
1297.5 | 17.0133 | 1299.5 | 210902.142 | 1301.5 | 211201.9994 | 1303.5 | 211201.9994 | 1304.5 | 211201.9994 | 1306.5 | 259037.9994 | 1308.5 | 211201.9994 | 1310.5 | 211201.9994 | 1312.5 | 105550.9988 | 1313.5 | 211201.9994 | 1315.5 | 258137.9994 | 1317.5 | 105550.9988 | 1319.5 | 211201.9994 | 1321.5 | 211201.9994 | 1322.5 | 258837.9994 | 1324.5 | 105550.9988 | 1326.5 | 211201.9994 | 1328.5 | 258937.9994 | 1330.5 | 211201.9994 | 1331.5 | 258937.9994 | 1333.5 | 129468.9988 | 1297.5 | 17.0133
1335.5 | 19.1233 | 1337.5 | 211002.0947 | 1339 | 211201.9994 | 1340.5 | 211201.9994 | 1342.5 | 211201.9994 | 1344.5 | 259037.9994 | 1346.5 | 105550.9988 | 1348 | 211201.9994 | 1349.5 | 211201.9994 | 1351.5 | 211201.9994 | 1353.5 | 258137.9994 | 1355.5 | 211201.9994 | 1357.5 | 211201.9994 | 1358.5 | 211201.9994 | 1360.5 | 258837.9994 | 1362.5 | 105550.9988 | 1364.5 | 105550.9988 | 1366.5 | 258937.9994 | 1367.5 | 211201.9994 | 1369.5 | 258937.9994 | 1371.5 | 129468.9988 | 1335.5 | 19.1233
1373.5 | 5.7644 | 1375.5 | 211201.9994 | 1376.5 | 211201.9994 | 1378.5 | 211201.9994 | 1380.5 | 211201.9994 | 1382.5 | 259037.9994 | 1384.5 | 211201.9994 | 1385.5 | 211201.9994 | 1387.5 | 211201.9994 | 1389.5 | 211201.9994 | 1391.5 | 258137.9994 | 1393.5 | 211201.9994 | 1394.5 | 211201.9994 | 1396.5 | 211201.9994 | 1398.5 | 258837.9994 | 1400.5 | 105550.9988 | 1402.5 | 211201.9994 | 1403.5 | 258937.9994 | 1405.5 | 105550.9988 | 1407.5 | 258937.9994 | 1409.5 | 129468.9988 | 1373.5 | 5.7644
1411.5 | 12.2949 | 1412.5 | 211201.9994 | 1414.5 | 211201.9994 | 1416.5 | 211201.9994 | 1418.5 | 211201.9994 | 1420.5 | 259037.9994 | 1421.5 | 105550.9988 | 1423.5 | 211201.9994 | 1425.5 | 211201.9994 | 1427.5 | 211201.9994 | 1429.5 | 258137.9994 | 1430.5 | 211201.9994 | 1432.5 | 211201.9994 | 1434.5 | 211201.9994 | 1436.5 | 258837.9994 | 1438.5 | 211201.9994 | 1439.5 | 211201.9994 | 1441.5 | 258937.9994 | 1443.5 | 105550.9988 | 1445.5 | 258937.9994 | 1447 | 129468.9988 | 1411.5 | 12.2949
1448.5 | 2.4118 | 1450.5 | 210902.142 | 1453 | 211201.9994 | 1454.5 | 211201.9994 | 1456 | 211201.9994 | 1457.5 | 259037.9994 | 1459.5 | 105550.9988 | 1461.5 | 211201.9994 | 1463.5 | 211201.9994 | 1465 | 211201.9994 | 1466.5 | 258137.9994 | 1468.5 | 211201.9994 | 1470.5 | 211201.9994 | 1472.5 | 211201.9994 | 1474 | 258837.9994 | 1475.5 | 211201.9994 | 1477.5 | 211201.9994 | 1479.5 | 258937.9994 | 1481.5 | 105550.9988 | 1483 | 258937.9994 | 1484.5 | 129468.9988 | 1448.5 | 2.4118
1486.5 | 8.0559 | 1488.5 | 211002.0947 | 1490.5 | 211201.9994 | 1492 | 211201.9994 | 1493.5 | 211201.9994 | 1495.5 | 259037.9994 | 1497.5 | 211201.9994 | 1499.5 | 211201.9994 | 1501.5 | 211201.9994 | 1502.5 | 211201.9994 | 1504.5 | 258137.9994 | 1506.5 | 105550.9988 | 1508.5 | 211201.9994 | 1510.5 | 211201.9994 | 1511.5 | 258837.9994 | 1513.5 | 211201.9994 | 1515.5 | 211201.9994 | 1517.5 | 258937.9994 | 1519 | 105550.9988 | 1520.5 | 258937.9994 | 1522.5 | 259037.9994 | 1486.5 | 8.0559
1524.5 | 17.98 | 1526.5 | 105550.9988 | 1528.5 | 211201.9994 | 1529.5 | 211201.9994 | 1531.5 | 211201.9994 | 1533.5 | 259037.9994 | 1535.5 | 105550.9988 | 1537.5 | 211201.9994 | 1538.5 | 211201.9994 | 1540.5 | 211201.9994 | 1542.5 | 258137.9994 | 1544.5 | 105550.9988 | 1546.5 | 211201.9994 | 1547.5 | 211201.9994 | 1549.5 | 258837.9994 | 1551.5 | 211201.9994 | 1553.5 | 211201.9994 | 1555 | 258937.9994 | 1556.5 | 105550.9988 | 1558.5 | 258937.9994 | 1560.5 | 129468.9988 | 1524.5 | 17.98
1562.5 | 1.5523 | 1564.5 | 211201.9994 | 1565.5 | 211201.9994 | 1567.5 | 211201.9994 | 1569.5 | 211201.9994 | 1571.5 | 259037.9994 | 1573.5 | 105550.9988 | 1574.5 | 211201.9994 | 1576.5 | 211201.9994 | 1578.5 | 211201.9994 | 1580.5 | 258137.9994 | 1582.5 | 105550.9988 | 1583.5 | 211201.9994 | 1585.5 | 211201.9994 | 1587.5 | 258837.9994 | 1589.5 | 211201.9994 | 1591 | 211201.9994 | 1592.5 | 258937.9994 | 1594.5 | 105550.9988 | 1596.5 | 258937.9994 | 1598.5 | 129468.9988 | 1562.5 | 1.5523
1600 | 0.94012 | 1601.5 | 211002.0947 | 1603.5 | 211201.9994 | 1605.5 | 211201.9994 | 1607.5 | 211201.9994 | 1609.5 | 259037.9994 | 1610.5 | 105550.9988 | 1612.5 | 9.1229 | 1614.5 | 211002.0947 | 1616.5 | 211201.9994 | 1618 | 258137.9994 | 1619.5 | 105550.9988 | 1621.5 | 211201.9994 | 1623.5 | 211201.9994 | 1625.5 | 258837.9994 | 1627 | 105550.9988 | 1628.5 | 211201.9994 | 1630.5 | 258937.9994 | 1633 | 105550.9988 | 1634.5 | 258937.9994 | 1636.5 | 129468.9988 | 1600 | 0.94012
1637.5 | 18.7081 | 1639.5 | 210802.284 | 1641.5 | 2.7103 | 1643.5 | 211002.0947 | 1645 | 211201.9994 | 1646.5 | 259037.9994 | 1648.5 | 105550.9988 | 1650.5 | 13.1253 | 1652.5 | 211002.0947 | 1654.5 | 211201.9994 | 1655.5 | 258137.9994 | 1657.5 | 105550.9988 | 1659.5 | 211201.9994 | 1661.5 | 211201.9994 | 1663 | 258837.9994 | 1664.5 | 105550.9988 | 1666.5 | 211201.9994 | 1668.5 | 258937.9994 | 1670.5 | 105550.9988 | 1672.5 | 258937.9994 | 1673.5 | 259037.9994 | 1637.5 | 2.7103
1675.5 | 3.3821 | 1677.5 | 211201.9994 | 1679.5 | 70133.9509 | 1681.5 | 211201.9994 | 1682.5 | 211201.9994 | 1684.5 | 259037.9994 | 1686.5 | 211201.9994 | 1688.5 | 211201.9994 | 1690 | 211201.9994 | 1691.5 | 211201.9994 | 1693.5 | 258137.9994 | 1695.5 | 105550.9988 | 1697.5 | 211201.9994 | 1699 | 211201.9994 | 1700.5 | 129368.9988 | 1702.5 | 1.0894 | 1704.5 | 211201.9994 | 1706.5 | 258937.9994 | 1707.5 | 105550.9988 | 1709.5 | 258937.9994 | 1711.5 | 129468.9988 | 1675.5 | 1.0894
1713.5 | 14.7147 | 1715.5 | 211002.0947 | 1717 | 211201.9994 | 1718.5 | 211201.9994 | 1720.5 | 211201.9994 | 1722.5 | 259037.9994 | 1724.5 | 105550.9988 | 1726 | 211201.9994 | 1727.5 | 211201.9994 | 1729.5 | 211201.9994 | 1731.5 | 258137.9994 | 1733.5 | 211201.9994 | 1735 | 211201.9994 | 1736.5 | 105550.9988 | 1738.5 | 258837.9994 | 1740.5 | 28.4134 | 1742.5 | 211002.0947 | 1744 | 258937.9994 | 1745.5 | 105550.9988 | 1747.5 | 258937.9994 | 1749.5 | 129468.9988 | 1713.5 | 14.7147
1751.5 | 25.7688 | 1753 | 211002.0947 | 1754.5 | 211201.9994 | 1756.5 | 211201.9994 | 1758.5 | 211201.9994 | 1760.5 | 259037.9994 | 1762 | 105550.9988 | 1763.5 | 211201.9994 | 1765.5 | 211201.9994 | 1767.5 | 211201.9994 | 1769.5 | 258137.9994 | 1771.5 | 211201.9994 | 1772.5 | 211201.9994 | 1774.5 | 211201.9994 | 1776.5 | 258837.9994 | 1778.5 | 4.9799 | 1780 | 211002.0947 | 1781.5 | 258937.9994 | 1783.5 | 105550.9988 | 1785.5 | 258937.9994 | 1787.5 | 129468.9988 | 1751.5 | 4.9799
1826.5 | 11.2136 | 1828.5 | 105550.9988 | 1830.5 | 211201.9994 | 1832.5 | 211201.9994 | 1834 | 211201.9994 | 1835.5 | 259037.9994 | 1837.5 | 105550.9988 | 1839.5 | 211201.9994 | 1841.5 | 211201.9994 | 1843 | 211201.9994 | 1844.5 | 258137.9994 | 1846.5 | 105550.9988 | 1810.5 | 211201.9994 | 1812.5 | 211201.9994 | 1814.5 | 258837.9994 | 1816 | 9.5153 | 1817.5 | 211201.9994 | 1819.5 | 258937.9994 | 1821.5 | 105550.9988 | 1823.5 | 258937.9994 | 1825 | 129468.9988 | 1826.5 | 9.5153
1864.5 | 2.6771 | 1866.5 | 210802.284 | 1868.5 | 211201.9994 | 1870 | 211201.9994 | 1871.5 | 211201.9994 | 1873.5 | 259037.9994 | 1875.5 | 211201.9994 | 1877.5 | 211201.9994 | 1878.5 | 211201.9994 | 1880.5 | 211201.9994 | 1882.5 | 258137.9994 | 1884.5 | 105550.9988 | 1848.5 | 211201.9994 | 1850.5 | 211201.9994 | 1852 | 258837.9994 | 1853.5 | 10.5933 | 1855.5 | 211002.0947 | 1857.5 | 258937.9994 | 1859.5 | 105550.9988 | 1861 | 258937.9994 | 1862.5 | 129468.9988 | 1864.5 | 2.6771
1903 | 6.545 | 1904.5 | 211002.0947 | 1906 | 211201.9994 | 1907.5 | 211201.9994 | 1909.5 | 211201.9994 | 1911.5 | 259037.9994 | 1913.5 | 105550.9988 | 1914.5 | 211201.9994 | 1916.5 | 211201.9994 | 1918.5 | 211201.9994 | 1920.5 | 258137.9994 | 1922.5 | 105550.9988 | 1886.5 | 211201.9994 | 1888 | 211201.9994 | 1889.5 | 258837.9994 | 1891.5 | 1.951 | 1893.5 | 210902.142 | 1895.5 | 258937.9994 | 1896.5 | 105550.9988 | 1898.5 | 258937.9994 | 1900.5 | 129468.9988 | 1903 | 1.951
1940.5 | 7.7552 | 1942 | 211201.9994 | 1943.5 | 105550.9988 | 1945.5 | 211201.9994 | 1947.5 | 211201.9994 | 1949.5 | 259037.9994 | 1951 | 105550.9988 | 1952.5 | 211201.9994 | 1954.5 | 211201.9994 | 1956.5 | 211201.9994 | 1958.5 | 258137.9994 | 1959.5 | 105550.9988 | 1924 | 211201.9994 | 1925.5 | 211201.9994 | 1927.5 | 258837.9994 | 1929.5 | 17.2359 | 1931.5 | 210902.142 | 1932.5 | 258937.9994 | 1934.5 | 105550.9988 | 1936.5 | 258937.9994 | 1938.5 | 259037.9994 | 1940.5 | 7.7552
1977.5 | 18.2636 | 1979.5 | 211201.9994 | 1981.5 | 211201.9994 | 1983.5 | 211201.9994 | 1985.5 | 211201.9994 | 1986.5 | 259037.9994 | 1988.5 | 211201.9994 | 1990.5 | 211201.9994 | 1992.5 | 211201.9994 | 1994.5 | 211201.9994 | 1995.5 | 258137.9994 | 1997.5 | 105550.9988 | 1961.5 | 211201.9994 | 1963.5 | 211201.9994 | 1965.5 | 258837.9994 | 1967.5 | 2.719 | 1968.5 | 211002.0947 | 1970.5 | 258937.9994 | 1972.5 | 105550.9988 | 1974.5 | 258937.9994 | 1976.5 | 129468.9988 | 1977.5 | 2.719
2091.5 | 5.7119 | 2017.5 | 211201.9994 | 2019.5 | 211201.9994 | 2021.5 | 211201.9994 | 2023 | 211201.9994 | 2024.5 | 259037.9994 | 2026.5 | 105550.9988 | 2028.5 | 211201.9994 | 2030.5 | 211201.9994 | 2031.5 | 211201.9994 | 2033.5 | 258137.9994 | 2035.5 | 211201.9994 | 1999.5 | 211201.9994 | 2001.5 | 211201.9994 | 2003.5 | 258837.9994 | 2004.5 | 6.5167 | 2006.5 | 211002.0947 | 2008.5 | 258937.9994 | 2010.5 | 105550.9988 | 2012.5 | 258937.9994 | 2013.5 | 129468.9988 | 2091.5 | 5.7119
|  | 2055.5 | 211201.9994 | 2057.5 | 211201.9994 | 2059 | 105550.9988 | 2060.5 | 211201.9994 | 2062.5 | 259037.9994 | 2064.5 | 105550.9988 | 2066.5 | 211201.9994 | 2068 | 211201.9994 | 2069.5 | 211201.9994 | 2071.5 | 258137.9994 | 2073.5 | 211201.9994 | 2037.5 | 211201.9994 | 2039.5 | 211201.9994 | 2041 | 258837.9994 | 2042.5 | 10.6801 | 2044.5 | 211201.9994 | 2046.5 | 258937.9994 | 2048.5 | 105550.9988 | 2049.5 | 129418.9988 | 2051.5 | 259037.9994 | 0 | 10.6801
|  | 2093.5 | 211002.0947 | 2095 | 211201.9994 | 2096.5 | 211201.9994 | 2098.5 | 211201.9994 | 2100.5 | 259037.9994 | 2102.5 | 211201.9994 | 2104 | 211201.9994 | 2105.5 | 211201.9994 | 2107.5 | 211201.9994 | 2109.5 | 258137.9994 | 2111.5 | 105550.9988 | 2075.5 | 211201.9994 | 2076.5 | 211201.9994 | 2078.5 | 258837.9994 | 2080.5 | 12.2009 | 2082.5 | 211002.0947 | 2084.5 | 258937.9994 | 2085.5 | 70333.9982 | 2087.5 | 258937.9994 | 2089.5 | 259037.9994 | 0 | 12.2009
|  | 2130.5 | 211002.0947 | 2132.5 | 105550.9988 | 2134.5 | 211201.9994 | 2136.5 | 211201.9994 | 2138.5 | 259037.9994 | 2139.5 | 105550.9988 | 2141.5 | 211201.9994 | 2143.5 | 211201.9994 | 2145.5 | 211201.9994 | 2147.5 | 258137.9994 | 2148.5 | 105550.9988 | 2112.5 | 211201.9994 | 2114.5 | 211201.9994 | 2116.5 | 258837.9994 | 2118.5 | 11.3254 | 2120.5 | 211002.0947 | 2121.5 | 258937.9994 | 2123.5 | 211201.9994 | 2125.5 | 258937.9994 | 2127.5 | 129468.9988 | 0 | 11.3254

## PenTemps
Penlight Time | DAQ Time | Shroud Temp | Cable Temp
-101 | 0 | 39.4713 | 29.2757
-100.2089 | 0.7911 | 39.4732 | 29.2802
-99.2174 | 1.7826 | 39.4592 | 29.2869
-98.226 | 2.774 | 39.4573 | 29.2883
-97.2246 | 3.7754 | 39.4474 | 29.2886
-96.2231 | 4.7769 | 39.4341 | 29.2876
-95.2217 | 5.7783 | 39.4258 | 29.2981
-94.2203 | 6.7797 | 39.4136 | 29.2955
-93.2188 | 7.7812 | 39.4137 | 29.3096
-92.2174 | 8.7826 | 39.4095 | 29.3086
-91.2159 | 9.7841 | 39.3978 | 29.3158
-90.2245 | 10.7755 | 39.3955 | 29.3186
-89.2231 | 11.7769 | 39.3837 | 29.3191
-88.2216 | 12.7784 | 39.3767 | 29.3236
-87.2202 | 13.7798 | 39.3769 | 29.3293
-86.2187 | 14.7813 | 39.3654 | 29.3362
-85.2173 | 15.7827 | 39.3449 | 29.3388
-84.2159 | 16.7841 | 39.3414 | 29.3406
-83.2244 | 17.7756 | 39.3287 | 29.3372
-82.223 | 18.777 | 39.3183 | 29.3565
-81.2216 | 19.7784 | 39.3157 | 29.3618
-80.2201 | 20.7799 | 39.3136 | 29.3605
-79.0985 | 21.9015 | 39.2988 | 29.3655
-78.2172 | 22.7828 | 39.2991 | 29.3673
-77.2258 | 23.7742 | 39.2966 | 29.3647
-76.2144 | 24.7856 | 39.2867 | 29.366
-75.2229 | 25.7771 | 39.2735 | 29.3701
-74.2215 | 26.7785 | 39.2567 | 29.38
-73.2201 | 27.7799 | 39.2597 | 29.3787
-72.2186 | 28.7814 | 39.2541 | 29.3858
-71.2172 | 29.7828 | 39.2476 | 29.3888
-70.2157 | 30.7843 | 39.2381 | 29.3916
-69.1142 | 31.8858 | 39.2332 | 29.3919
-68.2229 | 32.7771 | 39.2194 | 29.4035
-67.2214 | 33.7786 | 39.2171 | 29.3991
-66.22 | 34.78 | 39.2037 | 29.4038
-65.2185 | 35.7815 | 39.2021 | 29.4098
-64.2171 | 36.7829 | 39.1968 | 29.4153
-63.2257 | 37.7743 | 39.1902 | 29.417
-62.2142 | 38.7858 | 39.1801 | 29.4237
-61.2228 | 39.7772 | 39.1684 | 29.4314
-60.2214 | 40.7786 | 39.1586 | 29.4349
-59.2199 | 41.7801 | 39.1531 | 29.4342
-58.2185 | 42.7815 | 39.144 | 29.4383
-57.217 | 43.783 | 39.1454 | 29.4385
-56.2156 | 44.7844 | 39.1292 | 29.4522
-55.2242 | 45.7758 | 39.119 | 29.449
-54.2127 | 46.7873 | 39.1096 | 29.4553
-53.2213 | 47.7787 | 39.1054 | 29.4598
-52.2199 | 48.7801 | 39.102 | 29.4657
-51.2184 | 49.7816 | 39.095 | 29.4639
-50.217 | 50.783 | 39.0946 | 29.471
-49.2256 | 51.7744 | 39.0888 | 29.4733
-48.2141 | 52.7859 | 39.0791 | 29.4741
-47.2227 | 53.7773 | 39.0731 | 29.483
-46.2212 | 54.7788 | 39.0544 | 29.484
-45.2198 | 55.7802 | 39.062 | 29.4911
-44.2184 | 56.7816 | 39.0521 | 29.4888
-43.2169 | 57.7831 | 39.0394 | 29.4997
-42.2155 | 58.7845 | 39.034 | 29.4983
-41.224 | 59.776 | 39.029 | 29.5055
-40.2226 | 60.7774 | 39.0196 | 29.5133
-39.2212 | 61.7788 | 39.0121 | 29.5158
-38.2197 | 62.7803 | 39.0069 | 29.5192
-37.2183 | 63.7817 | 38.9948 | 29.517
-36.2168 | 64.7832 | 38.9975 | 29.5262
-35.2254 | 65.7746 | 38.9817 | 29.5351
-34.214 | 66.786 | 38.9826 | 29.5366
-33.2225 | 67.7775 | 38.9811 | 29.5311
-32.2211 | 68.7789 | 38.9787 | 29.5339
-31.2197 | 69.7803 | 38.9707 | 29.5416
-30.2182 | 70.7818 | 38.9609 | 29.5469
-29.2168 | 71.7832 | 38.9484 | 29.5493
-28.2153 | 72.7847 | 38.9438 | 29.5573
-27.2239 | 73.7761 | 38.9362 | 29.557
-26.2125 | 74.7875 | 38.9362 | 29.5623
-25.221 | 75.779 | 38.9236 | 29.5685
-24.2196 | 76.7804 | 38.9224 | 29.5654
-23.2182 | 77.7818 | 38.9086 | 29.5733
-22.2167 | 78.7833 | 38.9088 | 29.5723
-21.2253 | 79.7747 | 38.8896 | 29.579
-20.2138 | 80.7862 | 38.8906 | 29.5761
-19.2224 | 81.7776 | 38.8855 | 29.5836
-18.221 | 82.779 | 38.8844 | 29.5842
-17.2195 | 83.7805 | 38.8762 | 29.5916
-16.2181 | 84.7819 | 38.8763 | 29.5863
-15.2166 | 85.7834 | 38.8713 | 29.5939
-14.2152 | 86.7848 | 38.8705 | 29.5965
-13.2238 | 87.7762 | 38.8618 | 29.5936
-12.2123 | 88.7877 | 38.866 | 29.601
-11.2209 | 89.7791 | 38.8476 | 29.6045
-10.2195 | 90.7805 | 38.8401 | 29.6074
-9.218 | 91.782 | 38.8321 | 29.6099
-8.2166 | 92.7834 | 38.8275 | 29.6132
-7.2252 | 93.7748 | 38.8156 | 29.6158
-6.2137 | 94.7863 | 38.8054 | 29.6256
-5.2223 | 95.7777 | 38.7949 | 29.6339
-4.2208 | 96.7792 | 38.7839 | 29.6304
-3.2194 | 97.7806 | 38.7758 | 29.6348
-2.218 | 98.782 | 38.7604 | 29.6345
-1.2165 | 99.7835 | 38.751 | 29.6404
-0.2151 | 100.7849 | 38.8384 | 29.6444
0.7763 | 101.7763 | 39.2881 | 29.6485
1.7778 | 102.7778 | 40.2559 | 29.6561
2.7792 | 103.7792 | 41.7902 | 29.6562
3.7807 | 104.7807 | 43.8309 | 29.658
4.7821 | 105.7821 | 46.26 | 29.6664
5.7835 | 106.7835 | 49.0502 | 29.6815
6.775 | 107.775 | 52.1268 | 29.6863
7.7864 | 108.7864 | 55.4985 | 29.7079
8.7779 | 109.7779 | 59.1267 | 29.7247
9.7793 | 110.7793 | 63.0054 | 29.7539
10.7807 | 111.7807 | 67.0527 | 29.7864
11.7822 | 112.7822 | 71.2567 | 29.8224
12.7736 | 113.7736 | 75.5604 | 29.8626
13.7851 | 114.7851 | 80.08 | 29.9193
14.7765 | 115.7765 | 84.6881 | 29.9797
15.7879 | 116.7879 | 89.4825 | 30.0446
16.7794 | 117.7794 | 94.3273 | 30.1195
17.7808 | 118.7808 | 99.2903 | 30.2019
18.7822 | 119.7822 | 104.285 | 30.2946
19.7837 | 120.7837 | 109.4702 | 30.4059
20.7751 | 121.7751 | 114.6676 | 30.5256
21.7866 | 122.7866 | 119.92 | 30.6486
22.778 | 123.778 | 125.2405 | 30.7853
23.7794 | 124.7794 | 130.6323 | 30.9321
24.7809 | 125.7809 | 136.0246 | 31.0941
25.7823 | 126.7823 | 141.5188 | 31.277
26.7837 | 127.7837 | 146.9291 | 31.4649
27.7852 | 128.7852 | 152.3971 | 31.6672
28.7766 | 129.7766 | 157.8614 | 31.8753
29.7881 | 130.7881 | 163.3596 | 32.107
30.7795 | 131.7795 | 168.8432 | 32.3531
31.7809 | 132.7809 | 174.4125 | 32.6162
32.7824 | 133.7824 | 179.9061 | 32.881
33.7838 | 134.7838 | 185.6038 | 33.174
34.7752 | 135.7752 | 191.1029 | 33.4853
35.7867 | 136.7867 | 196.5181 | 33.8092
36.7781 | 137.7781 | 202.0041 | 34.1475
37.7796 | 138.7796 | 207.4516 | 34.5187
38.781 | 139.781 | 212.9606 | 34.8937
39.7824 | 140.7824 | 218.4447 | 35.2858
40.7839 | 141.7839 | 223.8651 | 35.7073
41.7853 | 142.7853 | 229.4384 | 36.1489
42.7767 | 143.7767 | 235.0144 | 36.602
43.7782 | 144.7782 | 240.6341 | 37.088
44.7796 | 145.7796 | 246.1369 | 37.5958
45.7811 | 146.7811 | 251.5823 | 38.1223
46.7825 | 147.7825 | 257.0084 | 38.6769
47.7839 | 148.7839 | 262.4182 | 39.2455
48.7754 | 149.7754 | 267.8096 | 39.8394
49.7768 | 150.7768 | 273.1034 | 40.4734
50.7782 | 151.7782 | 278.5109 | 41.1211
51.7797 | 152.7797 | 283.8396 | 41.7978
52.7811 | 153.7811 | 289.0773 | 42.515
53.7826 | 154.7826 | 294.4151 | 43.2481
54.774 | 155.774 | 299.5751 | 44.0226
55.7854 | 156.7854 | 304.5308 | 44.8181
56.7769 | 157.7769 | 308.9788 | 45.6551
57.7783 | 158.7783 | 313.0796 | 46.5054
58.7798 | 159.7798 | 316.893 | 47.376
59.7812 | 160.7812 | 320.4864 | 48.2849
60.7826 | 161.7826 | 323.9238 | 49.1995
61.7841 | 162.7841 | 327.4955 | 50.1233
62.7755 | 163.7755 | 330.9177 | 51.056
63.787 | 164.787 | 333.9686 | 52.0033
64.7784 | 165.7784 | 336.6561 | 52.937
65.7798 | 166.7798 | 339.2093 | 53.8809
66.7813 | 167.7813 | 341.3959 | 54.8261
67.7827 | 168.7827 | 343.2375 | 55.8038
68.7741 | 169.7741 | 344.7462 | 56.7851
69.7856 | 170.7856 | 346.2332 | 57.8055
70.777 | 171.777 | 347.5037 | 58.8179
71.7885 | 172.7885 | 348.5127 | 59.8553
72.7799 | 173.7799 | 349.3349 | 60.8997
73.7813 | 174.7813 | 349.9652 | 61.9544
74.7828 | 175.7828 | 350.2366 | 63.0277
75.7842 | 176.7842 | 350.4979 | 64.1033
76.7756 | 177.7756 | 350.7619 | 65.1822
77.7871 | 178.7871 | 350.8526 | 66.2744
78.7785 | 179.7785 | 350.9412 | 67.3536
79.7799 | 180.7799 | 350.9266 | 68.4463
80.7814 | 181.7814 | 350.7474 | 69.5145
81.7828 | 182.7828 | 350.5649 | 70.5907
82.7843 | 183.7843 | 350.4148 | 71.6576
83.7857 | 184.7857 | 350.3257 | 72.7093
84.7771 | 185.7771 | 350.0881 | 73.7493
85.7786 | 186.7786 | 349.8633 | 74.7858
86.78 | 187.78 | 349.6738 | 75.8046
87.7815 | 188.7815 | 349.5528 | 76.8272
88.7729 | 189.7729 | 349.4692 | 77.8211
89.7843 | 190.7843 | 349.1686 | 78.8129
90.7758 | 191.7758 | 348.8585 | 79.8007
91.7772 | 192.7772 | 348.5516 | 80.779
92.7786 | 193.7786 | 348.3605 | 81.7368
93.7801 | 194.7801 | 348.0795 | 82.6992
94.7815 | 195.7815 | 347.5479 | 83.6343
95.783 | 196.783 | 347.1013 | 84.5739
96.7744 | 197.7744 | 346.6815 | 85.4958
97.7858 | 198.7858 | 346.2942 | 86.4106
98.7773 | 199.7773 | 345.8672 | 87.3102
99.7787 | 200.7787 | 345.4805 | 88.1972
100.7801 | 201.7801 | 345.1673 | 89.0768
101.7816 | 202.7816 | 344.8758 | 89.9337
102.783 | 203.783 | 344.4865 | 90.7841
103.7845 | 204.7845 | 344.0147 | 91.6181
104.7759 | 205.7759 | 343.4806 | 92.4529
105.7773 | 206.7773 | 343.0222 | 93.2678
106.7788 | 207.7788 | 342.5713 | 94.0814
107.7802 | 208.7802 | 342.0923 | 94.8956
108.7817 | 209.7817 | 341.5353 | 95.6808
109.7831 | 210.7831 | 340.883 | 96.4789
110.7745 | 211.7745 | 340.392 | 97.2601
111.786 | 212.786 | 339.9879 | 98.0383
112.7774 | 213.7774 | 339.6078 | 98.7947
113.7788 | 214.7788 | 339.1436 | 99.5607
114.7803 | 215.7803 | 338.7177 | 100.2952
115.7817 | 216.7817 | 338.274 | 101.0291
116.7731 | 217.7731 | 337.7445 | 101.7396
117.7846 | 218.7846 | 337.2316 | 102.4509
118.776 | 219.776 | 336.5992 | 103.1296
119.7875 | 220.7875 | 335.9356 | 103.8013
120.7789 | 221.7789 | 335.2371 | 104.4813
121.7803 | 222.7803 | 334.6199 | 105.134
122.7818 | 223.7818 | 333.9906 | 105.7799
123.7832 | 224.7832 | 333.354 | 106.4191
124.7847 | 225.7847 | 332.8402 | 107.0623
125.7861 | 226.7861 | 332.3791 | 107.6962
126.7775 | 227.7775 | 331.9742 | 108.3349
127.779 | 228.779 | 331.5578 | 108.969
128.7804 | 229.7804 | 331.1493 | 109.5829
129.7818 | 230.7818 | 330.5308 | 110.2016
130.7833 | 231.7833 | 329.8684 | 110.8049
131.7847 | 232.7847 | 329.2977 | 111.412
132.7762 | 233.7762 | 328.8946 | 111.9994
133.7776 | 234.7776 | 328.3728 | 112.6004
134.779 | 235.779 | 327.919 | 113.1814
135.7805 | 236.7805 | 327.388 | 113.7692
136.7819 | 237.7819 | 326.8954 | 114.3274
137.7834 | 238.7834 | 326.3356 | 114.8882
138.7748 | 239.7748 | 325.6617 | 115.4313
139.7862 | 240.7862 | 325.1316 | 115.9542
140.7777 | 241.7777 | 324.5862 | 116.4642
141.7791 | 242.7791 | 324.1159 | 116.9677
142.7805 | 243.7805 | 323.8213 | 117.4675
143.782 | 244.782 | 323.3833 | 117.9607
144.7834 | 245.7834 | 322.8167 | 118.453
145.7849 | 246.7849 | 322.1398 | 118.9623
146.7763 | 247.7763 | 321.5889 | 119.4536
147.7877 | 248.7877 | 320.9994 | 119.951
148.7792 | 249.7792 | 320.5549 | 120.4433
149.7806 | 250.7806 | 320.3197 | 120.9307
150.782 | 251.782 | 320.1418 | 121.4113
151.7835 | 252.7835 | 319.8948 | 121.9078
152.7749 | 253.7749 | 319.7781 | 122.3887
153.7764 | 254.7764 | 319.7267 | 122.8669
154.7778 | 255.7778 | 319.6705 | 123.3617
155.7792 | 256.7792 | 319.5288 | 123.8406
156.7807 | 257.7807 | 319.4917 | 124.3226
157.7821 | 258.7821 | 319.6388 | 124.796
158.7836 | 259.7836 | 319.8367 | 125.2555
159.785 | 260.785 | 320.1221 | 125.7087
160.7764 | 261.7764 | 320.4961 | 126.1594
161.7879 | 262.7879 | 320.8341 | 126.6126
162.7793 | 263.7793 | 321.3193 | 127.0776
163.7807 | 264.7807 | 321.8265 | 127.5482
164.7822 | 265.7822 | 322.2851 | 128.008
165.7836 | 266.7836 | 322.8235 | 128.4737
166.775 | 267.775 | 323.3946 | 128.9376
167.7865 | 268.7865 | 323.8406 | 129.4109
168.7779 | 269.7779 | 324.1522 | 129.8749
169.7794 | 270.7794 | 324.4987 | 130.3578
170.7808 | 271.7808 | 324.9066 | 130.8436
171.7822 | 272.7822 | 325.2129 | 131.3379
172.7837 | 273.7837 | 325.712 | 131.8495
173.7851 | 274.7851 | 326.1666 | 132.3749
174.7765 | 275.7765 | 326.5826 | 132.9239
175.778 | 276.778 | 326.9857 | 133.4637
176.7794 | 277.7794 | 327.2805 | 134.0062
177.7809 | 278.7809 | 327.6569 | 134.5583
178.7823 | 279.7823 | 328.1257 | 135.1167
179.7837 | 280.7837 | 328.732 | 135.6722
180.7752 | 281.7752 | 329.2458 | 136.2351
181.7866 | 282.7866 | 329.6431 | 136.8107
182.7781 | 283.7781 | 329.9129 | 137.3846
183.7795 | 284.7795 | 330.1659 | 137.9632
184.7809 | 285.7809 | 330.4448 | 138.5441
185.7824 | 286.7824 | 330.8016 | 139.1365
186.7738 | 287.7738 | 331.1981 | 139.7241
187.7853 | 288.7853 | 331.5162 | 140.32
188.7767 | 289.7767 | 331.8116 | 140.9155
189.7781 | 290.7781 | 332.0439 | 141.5063
190.7796 | 291.7796 | 332.2258 | 142.1027
191.781 | 292.781 | 332.3347 | 142.7091
192.7824 | 293.7824 | 332.5607 | 143.3042
193.7839 | 294.7839 | 332.633 | 143.8836
194.7753 | 295.7753 | 332.6532 | 144.4657
195.7767 | 296.7767 | 332.8291 | 145.059
196.7782 | 297.7782 | 332.9989 | 145.6468
197.7796 | 298.7796 | 333.1943 | 146.2378
198.7811 | 299.7811 | 333.2744 | 146.827
199.7825 | 300.7825 | 333.3201 | 147.4118
200.7839 | 301.7839 | 333.3269 | 147.976
201.7854 | 302.7854 | 333.3106 | 148.5514
202.7768 | 303.7768 | 333.3546 | 149.1457
203.7782 | 304.7782 | 333.386 | 149.7435
204.7797 | 305.7797 | 333.4681 | 150.3397
205.7811 | 306.7811 | 333.4926 | 150.9484
206.7826 | 307.7826 | 333.3207 | 151.5399
207.784 | 308.784 | 333.2055 | 152.1523
208.7754 | 309.7754 | 333.1782 | 152.7414
209.7869 | 310.7869 | 333.1817 | 153.3148
210.7783 | 311.7783 | 333.0773 | 153.882
211.7798 | 312.7798 | 333.0764 | 154.4582
212.7812 | 313.7812 | 332.989 | 155.016
213.7826 | 314.7826 | 332.8664 | 155.5696
214.7841 | 315.7841 | 332.8104 | 156.1062
215.7855 | 316.7855 | 332.8207 | 156.6548
216.7769 | 317.7769 | 332.8247 | 157.1953
217.7784 | 318.7784 | 332.7597 | 157.7454
218.7798 | 319.7798 | 332.7164 | 158.3094
219.7813 | 320.7813 | 332.6474 | 158.8674
220.7827 | 321.7827 | 332.5866 | 159.4182
221.7841 | 322.7841 | 332.4809 | 159.9726
222.7756 | 323.7756 | 332.2891 | 160.537
223.787 | 324.787 | 332.165 | 161.1119
224.7784 | 325.7784 | 331.9409 | 161.6617
225.7799 | 326.7799 | 331.7513 | 162.2193
226.7813 | 327.7813 | 331.702 | 162.7734
227.7828 | 328.7828 | 331.5639 | 163.3506
228.7742 | 329.7742 | 331.4639 | 163.9223
229.7856 | 330.7856 | 331.4234 | 164.4751
230.7771 | 331.7771 | 331.4092 | 164.9829
231.7785 | 332.7785 | 331.3903 | 165.4842
232.78 | 333.78 | 331.3841 | 165.9929
233.7814 | 334.7814 | 331.2908 | 166.5352
234.7828 | 335.7828 | 331.1379 | 167.0431
235.7843 | 336.7843 | 331.0047 | 167.5267
236.7757 | 337.7757 | 330.866 | 168.0016
237.7771 | 338.7771 | 330.8372 | 168.5049
238.7786 | 339.7786 | 330.8848 | 169.0126
239.78 | 340.78 | 330.8946 | 169.5415
240.7815 | 341.7815 | 330.9692 | 170.0637
241.7829 | 342.7829 | 330.9899 | 170.6018
242.7743 | 343.7743 | 330.9837 | 171.1036
243.7858 | 344.7858 | 330.9404 | 171.6334
244.7772 | 345.7772 | 330.9715 | 172.1607
245.7786 | 346.7786 | 330.9627 | 172.6714
246.7801 | 347.7801 | 330.9433 | 173.1561
247.7815 | 348.7815 | 330.9651 | 173.6622
248.783 | 349.783 | 330.8871 | 174.1338
249.7844 | 350.7844 | 330.7493 | 174.5938
250.7758 | 351.7758 | 330.7629 | 175.058
251.7873 | 352.7873 | 330.8707 | 175.5242
252.7787 | 353.7787 | 330.9913 | 176.0121
253.7801 | 354.7801 | 331.0111 | 176.4876
254.7816 | 355.7816 | 331.0101 | 176.9312
255.783 | 356.783 | 331.0077 | 177.3655
256.7845 | 357.7845 | 331.0449 | 177.8195
257.7859 | 358.7859 | 331.046 | 178.2226
258.7773 | 359.7773 | 331.0955 | 178.6635
259.7788 | 360.7788 | 331.1791 | 179.1465
260.7802 | 361.7802 | 331.0699 | 179.6026
261.7817 | 362.7817 | 330.9932 | 180.0948
262.7731 | 363.7731 | 330.9955 | 180.584
263.7845 | 364.7845 | 331.0129 | 181.0624
264.776 | 365.776 | 331.0393 | 181.5609
265.7874 | 366.7874 | 330.9907 | 182.0482
266.7788 | 367.7788 | 330.9447 | 182.5416
267.7803 | 368.7803 | 330.835 | 183.0415
268.7817 | 369.7817 | 330.7734 | 183.5284
269.7832 | 370.7832 | 330.7488 | 184.0127
270.7746 | 371.7746 | 330.8002 | 184.4432
271.786 | 372.786 | 330.7214 | 184.8688
272.7775 | 373.7775 | 330.6596 | 185.3249
273.7789 | 374.7789 | 330.5878 | 185.7969
274.7803 | 375.7803 | 330.5476 | 186.2962
275.7818 | 376.7818 | 330.5371 | 186.7757
276.7832 | 377.7832 | 330.4994 | 187.2543
277.7847 | 378.7847 | 330.5962 | 187.7203
278.7761 | 379.7761 | 330.7692 | 188.1843
279.7775 | 380.7775 | 330.8339 | 188.6335
280.779 | 381.779 | 330.8004 | 189.1048
281.8205 | 382.8205 | 330.7955 | 189.5902
282.7819 | 383.7819 | 330.9459 | 190.0296
283.7833 | 384.7833 | 331.0279 | 190.4808
284.7747 | 385.7747 | 331.1194 | 190.9412
285.7862 | 386.7862 | 331.0679 | 191.4178
286.7776 | 387.7776 | 331.0096 | 191.8966
287.779 | 388.779 | 331.1425 | 192.3596
288.7805 | 389.7805 | 331.139 | 192.8073
289.7819 | 390.7819 | 331.0304 | 193.2663
290.7834 | 391.7834 | 330.9595 | 193.643
291.7848 | 392.7848 | 330.957 | 193.9997
292.7762 | 393.7762 | 330.9768 | 194.4325
293.7877 | 394.7877 | 331.0277 | 194.743
294.7791 | 395.7791 | 331.0182 | 195.0995
295.7805 | 396.7805 | 331.0899 | 195.4581
296.782 | 397.782 | 331.034 | 195.8183
297.7834 | 398.7834 | 331.076 | 196.2598
298.7748 | 399.7748 | 331.1967 | 196.6829
299.7763 | 400.7763 | 331.3252 | 197.1137
300.7777 | 401.7777 | 331.3844 | 197.5512
301.7792 | 402.7792 | 331.448 | 197.8977
302.7806 | 403.7806 | 331.5183 | 198.2542
303.782 | 404.782 | 331.6101 | 198.5488
304.7735 | 405.7735 | 331.6688 | 198.8398
305.7849 | 406.7849 | 331.7379 | 199.1543
306.7764 | 407.7764 | 331.7333 | 199.498
307.7778 | 408.7778 | 331.6968 | 199.8677
308.7792 | 409.7792 | 331.6758 | 200.2236
309.7807 | 410.7807 | 331.7394 | 200.5404
310.7821 | 411.7821 | 331.8733 | 200.6884
311.7836 | 412.7836 | 332.0562 | 200.9958
312.775 | 413.775 | 332.1579 | 201.2384
313.7864 | 414.7864 | 332.1504 | 201.5374
314.7779 | 415.7779 | 332.1126 | 201.9008
315.7793 | 416.7793 | 332.1069 | 202.25
316.7807 | 417.7807 | 332.1203 | 202.5202
317.7822 | 418.7822 | 332.056 | 202.657
318.7736 | 419.7736 | 331.9807 | 202.8313
319.7851 | 420.7851 | 331.9608 | 203.0911
320.7765 | 421.7765 | 332.0035 | 203.4034
321.7779 | 422.7779 | 332.0571 | 203.6545
322.7794 | 423.7794 | 332.0855 | 203.7717
323.7808 | 424.7808 | 331.9951 | 204.0801
324.7822 | 425.7822 | 332.104 | 204.4157
325.7837 | 426.7837 | 332.3004 | 204.7171
326.7751 | 427.7751 | 332.3612 | 204.8623
327.7866 | 428.7866 | 332.3016 | 205.2269
328.778 | 429.778 | 332.2929 | 205.5026
329.7794 | 430.7794 | 332.3464 | 205.5464
330.7809 | 431.7809 | 332.3551 | 205.9142
331.7823 | 432.7823 | 332.3365 | 206.279
332.7838 | 433.7838 | 332.3635 | 206.6259
333.7852 | 434.7852 | 332.3461 | 206.9217
334.7766 | 435.7766 | 332.3273 | 207.0969
335.7881 | 436.7881 | 332.4104 | 207.3754
336.7795 | 437.7795 | 332.5521 | 207.5706
337.7809 | 438.7809 | 332.6839 | 207.7309
338.7724 | 439.7724 | 332.7718 | 208.0889
339.7838 | 440.7838 | 332.7204 | 208.32
340.7752 | 441.7752 | 332.6435 | 208.4181
341.7767 | 442.7767 | 332.6576 | 208.7543
342.7781 | 443.7781 | 332.665 | 208.9414
343.7796 | 444.7796 | 332.6456 | 209.2245
344.781 | 445.781 | 332.6146 | 209.2911
345.7824 | 446.7824 | 332.5846 | 209.2788
346.7839 | 447.7839 | 332.4643 | 209.4788
347.7853 | 448.7853 | 332.3667 | 209.8178
348.7767 | 449.7767 | 332.315 | 210.1439
349.7782 | 450.7782 | 332.3075 | 210.3094
350.7796 | 451.7796 | 332.2496 | 210.6355
351.7811 | 452.7811 | 332.2108 | 210.9266
352.7825 | 453.7825 | 332.1268 | 211.1753
353.7839 | 454.7839 | 332.1034 | 211.3131
354.7754 | 455.7754 | 332.0938 | 211.4394
355.7868 | 456.7868 | 332.0508 | 211.463
356.7783 | 457.7783 | 332.0189 | 211.729
357.7797 | 458.7797 | 332.0073 | 211.5968
358.7811 | 459.7811 | 332.0706 | 211.8035
359.7826 | 460.7826 | 332.1216 | 212.0453
360.774 | 461.774 | 332.0476 | 212.2469
361.7855 | 462.7855 | 332.0745 | 212.4221
362.7769 | 463.7769 | 332.0246 | 212.6209
363.7783 | 464.7783 | 332.0533 | 212.96
364.7798 | 465.7798 | 332.0392 | 213.1157
365.7812 | 466.7812 | 331.9433 | 213.3806
366.7826 | 467.7826 | 331.8762 | 213.6597
367.7841 | 468.7841 | 331.8364 | 213.9439
368.7755 | 469.7755 | 331.7546 | 214.0976
369.787 | 470.787 | 331.8209 | 214.243
370.7784 | 471.7784 | 331.6881 | 214.2843
371.7798 | 472.7798 | 331.549 | 214.4284
372.7813 | 473.7813 | 331.4587 | 214.5102
373.7827 | 474.7827 | 331.4042 | 214.7516
374.7741 | 475.7741 | 331.4189 | 215.0109
375.7756 | 476.7756 | 331.3397 | 215.1989
376.777 | 477.777 | 331.2415 | 215.1827
377.7885 | 478.7885 | 331.1229 | 215.4991
378.7799 | 479.7799 | 330.9425 | 215.6811
379.7813 | 480.7813 | 330.6803 | 215.8013
380.7828 | 481.7828 | 330.4832 | 215.8602
381.7842 | 482.7842 | 330.404 | 216.1205
382.7756 | 483.7756 | 330.3489 | 216.3609
383.7771 | 484.7771 | 330.3981 | 216.646
384.7785 | 485.7785 | 330.5776 | 216.8734
385.78 | 486.78 | 330.6849 | 217.1669
386.7814 | 487.7814 | 330.696 | 217.4375
387.7828 | 488.7828 | 330.6782 | 217.7278
388.7743 | 489.7743 | 330.6658 | 217.9873
389.7857 | 490.7857 | 330.7027 | 218.0462
390.7771 | 491.7771 | 330.7561 | 218.2665
391.7786 | 492.7786 | 330.7384 | 218.3625
392.78 | 493.78 | 330.7117 | 218.6896
393.7815 | 494.7815 | 330.664 | 219.0319
394.7829 | 495.7829 | 330.7043 | 219.2772
395.7843 | 496.7843 | 330.6533 | 219.495
396.7758 | 497.7758 | 330.6415 | 219.8423
397.7872 | 498.7872 | 330.5049 | 220.1588
398.7786 | 499.7786 | 330.545 | 220.3764
399.7801 | 500.7801 | 330.6018 | 220.5573
400.7815 | 501.7815 | 330.6327 | 220.7104
401.783 | 502.783 | 330.6152 | 220.9126
402.7844 | 503.7844 | 330.6072 | 221.1496
403.7858 | 504.7858 | 330.8043 | 221.3366
404.7773 | 505.7773 | 331.1072 | 221.6019
405.7787 | 506.7787 | 331.2825 | 221.8702
406.7802 | 507.7802 | 331.4035 | 221.8708
407.7816 | 508.7816 | 331.4512 | 222.1451
408.783 | 509.783 | 331.5104 | 222.2652
409.7845 | 510.7845 | 331.6897 | 222.4801
410.7759 | 511.7759 | 331.7044 | 222.7806
411.7773 | 512.7773 | 331.6573 | 222.9104
412.7788 | 513.7788 | 331.5841 | 223.1215
413.7802 | 514.7802 | 331.6712 | 223.2052
414.7817 | 515.7817 | 331.6926 | 223.5574
415.7831 | 516.7831 | 331.5383 | 223.8044
416.7745 | 517.7745 | 331.4419 | 224.0772
417.776 | 518.776 | 331.3659 | 224.3606
418.7774 | 519.7774 | 331.2895 | 224.6119
419.7788 | 520.7788 | 331.2252 | 224.833
420.7803 | 521.7803 | 331.1493 | 224.7539
421.7817 | 522.7817 | 331.0694 | 224.9328
422.7832 | 523.7832 | 331.122 | 225.1868
423.7846 | 524.7846 | 331.1202 | 225.3777
424.776 | 525.776 | 331.0559 | 225.5697
425.7775 | 526.7775 | 330.9796 | 225.7002
426.7789 | 527.7789 | 330.9908 | 225.9405
427.7803 | 528.7803 | 330.9919 | 226.1789
428.7818 | 529.7818 | 330.8814 | 226.43
429.7832 | 530.7832 | 330.7819 | 226.6246
430.7747 | 531.7747 | 330.8687 | 226.8474
431.7861 | 532.7861 | 331.0117 | 227.0141
432.7775 | 533.7775 | 331.0747 | 227.1643
433.779 | 534.779 | 331.138 | 227.3538
434.7804 | 535.7804 | 331.3033 | 227.5159
435.7819 | 536.7819 | 331.3121 | 227.5916
436.7733 | 537.7733 | 331.3032 | 227.7446
437.7847 | 538.7847 | 331.3428 | 228.1004
438.7762 | 539.7762 | 331.4782 | 228.4198
439.7776 | 540.7776 | 331.5219 | 228.4915
440.779 | 541.779 | 331.6155 | 228.5522
441.7805 | 542.7805 | 331.6681 | 228.869
442.7819 | 543.7819 | 331.6695 | 229.1792
443.7834 | 544.7834 | 331.6267 | 229.4397
444.7748 | 545.7748 | 331.4692 | 229.5966
445.7862 | 546.7862 | 331.4793 | 229.713
446.7777 | 547.7777 | 331.6246 | 229.7814
447.7791 | 548.7791 | 331.6899 | 229.7157
448.7805 | 549.7805 | 331.6493 | 229.5563
449.782 | 550.782 | 331.5468 | 229.6852
450.7834 | 551.7834 | 331.4963 | 229.9847
451.7849 | 552.7849 | 331.4791 | 230.0542
452.7763 | 553.7763 | 331.3372 | 230.2202
453.7877 | 554.7877 | 331.2603 | 230.4895
454.7792 | 555.7792 | 331.2792 | 230.7717
455.7806 | 556.7806 | 331.2936 | 230.8493
456.7821 | 557.7821 | 331.2459 | 231.0403
457.7835 | 558.7835 | 331.2906 | 231.0598
458.7749 | 559.7749 | 331.3502 | 230.8524
459.7864 | 560.7864 | 331.2834 | 230.9266
460.7778 | 561.7778 | 331.1669 | 231.1426
461.7792 | 562.7792 | 331.03 | 231.411
462.7807 | 563.7807 | 330.8176 | 231.6186
463.7821 | 564.7821 | 330.703 | 231.4967
464.7836 | 565.7836 | 330.6768 | 231.7344
465.785 | 566.785 | 330.7159 | 232.0927
466.7764 | 567.7764 | 330.7366 | 232.3853
467.7779 | 568.7779 | 330.7174 | 232.3923
468.7793 | 569.7793 | 330.716 | 232.6349
469.7807 | 570.7807 | 330.7636 | 232.5969
470.7822 | 571.7822 | 330.6316 | 232.7889
471.7836 | 572.7836 | 330.467 | 233.0998
472.775 | 573.775 | 330.2818 | 233.1408
473.7865 | 574.7865 | 330.1987 | 233.4335
474.7779 | 575.7779 | 330.0643 | 233.5875
475.7794 | 576.7794 | 329.9178 | 233.8007
476.7808 | 577.7808 | 329.8391 | 234.0173
477.7822 | 578.7822 | 329.7413 | 234.0564
478.7737 | 579.7737 | 329.6492 | 234.0507
479.7851 | 580.7851 | 329.6481 | 234.2983
480.7766 | 581.7766 | 329.7286 | 234.2667
481.778 | 582.778 | 329.7988 | 234.5967
482.7794 | 583.7794 | 329.7661 | 234.3194
483.7809 | 584.7809 | 329.7922 | 234.5084
484.7823 | 585.7823 | 329.8499 | 234.7442
485.7838 | 586.7838 | 329.8514 | 234.4573
486.7752 | 587.7752 | 329.8463 | 234.7879
487.7766 | 588.7766 | 329.7288 | 234.9581
488.7781 | 589.7781 | 329.6268 | 235.1703
489.7795 | 590.7795 | 329.7311 | 235.478
490.7809 | 591.7809 | 329.6892 | 235.5921
491.7824 | 592.7824 | 329.6323 | 235.6735
492.7738 | 593.7738 | 329.6078 | 235.4193
493.7853 | 594.7853 | 329.6642 | 235.6348
494.7767 | 595.7767 | 329.7388 | 235.5532
495.7781 | 596.7781 | 329.7304 | 235.4526
496.7796 | 597.7796 | 329.7527 | 235.7743
497.781 | 598.781 | 329.69 | 235.8753
498.7824 | 599.7824 | 329.6893 | 236.1089
499.7839 | 600.7839 | 329.6262 | 236.4232
500.7753 | 601.7753 | 329.5601 | 236.2379
501.7868 | 602.7868 | 329.479 | 236.2946
502.7782 | 603.7782 | 329.4922 | 236.5272
503.7796 | 604.7796 | 329.495 | 236.5849
504.7811 | 605.7811 | 329.462 | 236.5709
505.7825 | 606.7825 | 329.4607 | 236.9237
506.7739 | 607.7739 | 329.4289 | 237.1992
507.7854 | 608.7854 | 329.4234 | 237.3874
508.7768 | 609.7768 | 329.5021 | 237.517
509.7783 | 610.7783 | 329.718 | 237.207
510.7797 | 611.7797 | 329.8606 | 237.6561
511.7811 | 612.7811 | 329.9884 | 237.6334
512.7726 | 613.7726 | 330.0574 | 237.7645
513.784 | 614.784 | 330.2839 | 237.9819
514.7754 | 615.7754 | 330.516 | 238.3261
515.7769 | 616.7769 | 330.7184 | 238.3593
516.7783 | 617.7783 | 330.8165 | 238.5658
517.7798 | 618.7798 | 330.7442 | 238.837
518.7812 | 619.7812 | 330.7712 | 238.9555
519.7826 | 620.7826 | 330.9185 | 239.3524
520.7741 | 621.7741 | 331.0335 | 239.5459
521.7855 | 622.7855 | 331.184 | 239.7343
522.7769 | 623.7769 | 331.3851 | 239.9401
523.7884 | 624.7884 | 331.5278 | 240.2569
524.7798 | 625.7798 | 331.4974 | 240.141
525.7813 | 626.7813 | 331.3579 | 240.2705
526.7827 | 627.7827 | 331.3519 | 240.2064
527.7841 | 628.7841 | 331.402 | 240.4756
528.7756 | 629.7756 | 331.4889 | 240.8408
529.787 | 630.787 | 331.5293 | 241.0399
530.7785 | 631.7785 | 331.5419 | 240.6567
531.7799 | 632.7799 | 331.5227 | 240.5746
532.7813 | 633.7813 | 331.5518 | 240.9927
533.7828 | 634.7828 | 331.4484 | 241.2391
534.7842 | 635.7842 | 331.3961 | 241.5875
535.7857 | 636.7857 | 331.3292 | 241.8716
536.7771 | 637.7771 | 331.2133 | 241.8399
537.7785 | 638.7785 | 331.0151 | 241.9584
538.78 | 639.78 | 331.0102 | 242.0323
539.7814 | 640.7814 | 331.1332 | 242.138
540.7828 | 641.7828 | 331.2006 | 242.2085
541.7843 | 642.7843 | 331.2686 | 242.1406
542.7757 | 643.7757 | 331.2838 | 242.4514
543.7872 | 644.7872 | 331.2784 | 242.6261
544.7786 | 645.7786 | 331.1176 | 242.4789
545.78 | 646.78 | 331.0559 | 242.7951
546.7815 | 647.7815 | 330.9597 | 242.8593
547.7829 | 648.7829 | 330.8162 | 243.0681
548.7743 | 649.7743 | 330.635 | 243.1629
549.7858 | 650.7858 | 330.5806 | 243.2686
550.7772 | 651.7772 | 330.5744 | 243.4133
551.7786 | 652.7786 | 330.5346 | 243.6732
552.7801 | 653.7801 | 330.5093 | 243.9031
553.7815 | 654.7815 | 330.4452 | 243.8199
554.773 | 655.773 | 330.4076 | 244.136
555.7844 | 656.7844 | 330.4615 | 244.3278
556.7758 | 657.7758 | 330.5293 | 244.595
557.7773 | 658.7773 | 330.4963 | 244.7738
558.7787 | 659.7787 | 330.5319 | 244.9101
559.7802 | 660.7802 | 330.588 | 244.8753
560.7816 | 661.7816 | 330.6578 | 244.9797
561.783 | 662.783 | 330.8233 | 245.0361
562.7845 | 663.7845 | 330.8658 | 245.2279
563.7859 | 664.7859 | 330.8532 | 245.4939
564.7773 | 665.7773 | 330.9798 | 245.6266
565.7788 | 666.7788 | 331.0872 | 245.4767
566.7802 | 667.7802 | 331.0025 | 245.7806
567.7817 | 668.7817 | 331.0383 | 245.262
568.7731 | 669.7731 | 331.1424 | 245.4825
569.7845 | 670.7845 | 331.2642 | 245.7371
570.776 | 671.776 | 331.2975 | 245.8693
571.7874 | 672.7874 | 331.4166 | 246.1225
572.7788 | 673.7788 | 331.4504 | 246.4402
573.7803 | 674.7803 | 331.5526 | 246.3304
574.7817 | 675.7817 | 331.5202 | 246.5022
575.7832 | 676.7832 | 331.5296 | 246.6417
576.7746 | 677.7746 | 331.6601 | 246.4826
577.786 | 678.786 | 331.6994 | 245.6485
578.7775 | 679.7775 | 331.7846 | 245.8679
579.7789 | 680.7789 | 331.7999 | 245.9728
580.7804 | 681.7804 | 331.6881 | 246.4891
581.7818 | 682.7818 | 331.608 | 246.7165
582.7832 | 683.7832 | 331.496 | 247.0008
583.7847 | 684.7847 | 331.5127 | 247.3637
584.7761 | 685.7761 | 331.5467 | 247.709
585.7876 | 686.7876 | 331.5517 | 247.6551
586.779 | 687.779 | 331.5709 | 247.8715
587.7804 | 688.7804 | 331.5444 | 247.8843
588.7819 | 689.7819 | 331.5242 | 248.0266
589.7833 | 690.7833 | 331.527 | 248.2988
590.7747 | 691.7747 | 331.4993 | 248.5931
591.7862 | 692.7862 | 331.5649 | 248.8393
592.7776 | 693.7776 | 331.5985 | 248.5633
593.779 | 694.779 | 331.5782 | 248.6379
594.7805 | 695.7805 | 331.5756 | 248.3323
595.7819 | 696.7819 | 331.6132 | 248.4564
596.7834 | 697.7834 | 331.5875 | 248.0123
597.7848 | 698.7848 | 331.4385 | 248.5117
598.7762 | 699.7762 | 331.3781 | 248.6558
599.7777 | 700.7777 | 331.2377 | 248.4492
600.7791 | 701.7791 | 331.1451 | 248.7981
601.7805 | 702.7805 | 331.1222 | 248.7793
602.782 | 703.782 | 331.0846 | 248.8399
603.7834 | 704.7834 | 331.0554 | 248.8787
604.7749 | 705.7749 | 331.0865 | 249.0802
605.7863 | 706.7863 | 331.0867 | 249.3234
606.7777 | 707.7777 | 330.9957 | 248.8649
607.7792 | 708.7792 | 330.843 | 249.0146
608.7806 | 709.7806 | 330.7577 | 247.9885
609.7821 | 710.7821 | 330.725 | 247.9339
610.7735 | 711.7735 | 330.6716 | 248.4301
611.7849 | 712.7849 | 330.6704 | 248.9209
612.7764 | 713.7764 | 330.659 | 249.2358
613.7778 | 714.7778 | 330.6986 | 249.6516
614.7792 | 715.7792 | 330.7019 | 250.0225
615.7807 | 716.7807 | 330.7434 | 250.0141
616.7821 | 717.7821 | 330.7251 | 249.7614
617.7836 | 718.7836 | 330.7007 | 249.7982
618.775 | 719.775 | 330.7771 | 249.9136
619.7864 | 720.7864 | 330.709 | 250.1009
620.7779 | 721.7779 | 330.5163 | 250.4209
621.7793 | 722.7793 | 330.5909 | 250.6819
622.7807 | 723.7807 | 330.778 | 250.8442
623.7822 | 724.7822 | 331.0484 | 251.1182
624.7736 | 725.7736 | 331.2275 | 250.6158
625.7851 | 726.7851 | 331.2254 | 250.1229
626.7765 | 727.7765 | 331.3516 | 250.6517
627.7779 | 728.7779 | 331.4994 | 250.7798
628.7794 | 729.7794 | 331.4077 | 250.9407
629.7808 | 730.7808 | 331.3333 | 250.4011
630.7823 | 731.7823 | 331.2478 | 250.8577
631.7837 | 732.7837 | 331.2546 | 251.2217
632.7751 | 733.7751 | 331.3463 | 251.4589
633.7766 | 734.7766 | 331.4067 | 251.8884
634.778 | 735.778 | 331.4676 | 252.1809
635.7794 | 736.7794 | 331.5299 | 252.3866
636.7809 | 737.7809 | 331.4828 | 252.6369
637.7823 | 738.7823 | 331.3874 | 252.3541
638.7838 | 739.7838 | 331.569 | 252.6608
639.7852 | 740.7852 | 331.6371 | 252.7863
640.7766 | 741.7766 | 331.5674 | 252.9615
641.7781 | 742.7781 | 331.6458 | 253.0533
642.7995 | 743.7995 | 331.7101 | 253.0625
643.7809 | 744.7809 | 331.6831 | 252.8527
644.7824 | 745.7824 | 331.6329 | 252.9633
645.7838 | 746.7838 | 331.5957 | 252.6147
646.7752 | 747.7752 | 331.5603 | 252.7444
647.7867 | 748.7867 | 331.5648 | 252.9824
648.7781 | 749.7781 | 331.6723 | 253.2957
649.7796 | 750.7796 | 331.6399 | 253.1601
650.781 | 751.781 | 331.531 | 252.8635
651.7824 | 752.7824 | 331.3711 | 252.0418
652.7739 | 753.7739 | 331.2918 | 252.4423
653.7853 | 754.7853 | 331.2985 | 252.0689
654.7768 | 755.7768 | 331.2025 | 252.0765
655.7782 | 756.7782 | 331.1789 | 252.651
656.7796 | 757.7796 | 331.185 | 252.9817
657.7811 | 758.7811 | 331.1375 | 253.3669
658.7825 | 759.7825 | 331.1371 | 253.3994
659.784 | 760.784 | 331.2513 | 253.6922
660.7754 | 761.7754 | 331.2247 | 253.7329
661.7868 | 762.7868 | 331.0764 | 252.6274
662.7783 | 763.7783 | 331.0469 | 253.1695
663.7797 | 764.7797 | 331.0428 | 253.2933
664.7811 | 765.7811 | 330.9579 | 253.5023
665.7826 | 766.7826 | 331.0299 | 252.6557
666.774 | 767.774 | 331.0165 | 252.7219
667.7855 | 768.7855 | 331.1163 | 252.737
668.7769 | 769.7769 | 331.1504 | 251.9872
669.7783 | 770.7783 | 331.1355 | 251.5495
670.7798 | 771.7798 | 331.0744 | 252.1708
671.7812 | 772.7812 | 331.0816 | 251.434
672.7826 | 773.7826 | 331.119 | 251.7651
673.7841 | 774.7841 | 331.2122 | 252.1269
674.7755 | 775.7755 | 331.1674 | 252.1406
675.787 | 776.787 | 331.1867 | 251.7221
676.7784 | 777.7784 | 331.3087 | 251.8946
677.7798 | 778.7798 | 331.3877 | 252.1502
678.7813 | 779.7813 | 331.3557 | 252.7405
679.7827 | 780.7827 | 331.2405 | 252.7958
680.7842 | 781.7842 | 331.2967 | 252.8686
681.7856 | 782.7856 | 331.4154 | 253.3915
682.777 | 783.777 | 331.2601 | 252.9605
683.7885 | 784.7885 | 331.1659 | 253.2586
684.7799 | 785.7799 | 331.1531 | 253.5162
685.7813 | 786.7813 | 331.195 | 253.4352
686.7828 | 787.7828 | 331.2594 | 253.0162
687.7842 | 788.7842 | 331.3991 | 252.7
688.7756 | 789.7756 | 331.6068 | 252.6979
689.7771 | 790.7771 | 331.7091 | 253.2156
690.7785 | 791.7785 | 331.7462 | 253.4167
691.78 | 792.78 | 331.8014 | 253.6013
692.7814 | 793.7814 | 331.8063 | 253.5563
693.7828 | 794.7828 | 331.8564 | 253.8458
694.7743 | 795.7743 | 331.9535 | 254.2929
695.7857 | 796.7857 | 332.0271 | 254.5998
696.7771 | 797.7771 | 332.0715 | 255.006
697.7786 | 798.7786 | 332.0671 | 255.2369
698.78 | 799.78 | 331.9306 | 255.4057
699.7815 | 800.7815 | 331.8827 | 255.5482
700.7829 | 801.7829 | 331.8142 | 255.2875
701.7843 | 802.7843 | 331.7733 | 255.5298
702.7758 | 803.7758 | 331.6815 | 255.9166
703.7872 | 804.7872 | 331.5892 | 256.1504
704.7787 | 805.7787 | 331.5975 | 256.2789
705.7801 | 806.7801 | 331.5719 | 256.569
706.7815 | 807.7815 | 331.4573 | 256.612
707.783 | 808.783 | 331.3605 | 256.5771
708.7744 | 809.7744 | 331.1844 | 256.5106
709.7859 | 810.7859 | 331.0601 | 256.469
710.7873 | 811.7873 | 331.0792 | 255.812
711.7787 | 812.7787 | 331.127 | 255.4168
712.7802 | 813.7802 | 331.1876 | 255.1676
713.7816 | 814.7816 | 331.3098 | 255.1678
714.783 | 815.783 | 331.4124 | 254.1485
715.7845 | 816.7845 | 331.4331 | 254.4749
716.7759 | 817.7759 | 331.3689 | 254.7877
717.7773 | 818.7773 | 331.3146 | 254.5823
718.7788 | 819.7788 | 331.1491 | 254.7617
719.7802 | 820.7802 | 331.0201 | 254.1473
720.7817 | 821.7817 | 330.9301 | 254.114
721.7831 | 822.7831 | 330.8255 | 254.7745
722.7745 | 823.7745 | 330.8309 | 254.9866
723.786 | 824.786 | 330.7238 | 254.9964
724.7774 | 825.7774 | 330.7321 | 255.3316
725.7788 | 826.7788 | 330.7737 | 255.7701
726.7803 | 827.7803 | 330.7685 | 255.9503
727.7817 | 828.7817 | 330.7697 | 256.4536
728.7732 | 829.7732 | 330.7868 | 256.6853
729.7846 | 830.7846 | 330.6874 | 256.6928
730.776 | 831.776 | 330.7159 | 256.8156
731.7775 | 832.7775 | 330.7618 | 256.3781
732.7789 | 833.7789 | 330.7927 | 255.9933
733.7804 | 834.7804 | 330.8698 | 256.1272
734.7818 | 835.7818 | 330.9135 | 256.4005
735.7832 | 836.7832 | 330.9652 | 256.3745
736.7747 | 837.7747 | 330.885 | 255.8445
737.7861 | 838.7861 | 330.7925 | 255.8179
738.7775 | 839.7775 | 330.8161 | 256.2362
739.779 | 840.779 | 330.6937 | 256.3238
740.7804 | 841.7804 | 330.6229 | 255.6078
741.7819 | 842.7819 | 330.556 | 255.1676
742.7833 | 843.7833 | 330.5442 | 255.7702
743.7847 | 844.7847 | 330.6598 | 255.185
744.7762 | 845.7762 | 330.7307 | 254.9478
745.7876 | 846.7876 | 330.7159 | 255.411
746.779 | 847.779 | 330.7048 | 255.2062
747.7805 | 848.7805 | 330.638 | 255.4759
748.7819 | 849.7819 | 330.5883 | 255.787
749.7834 | 850.7834 | 330.7383 | 254.9997
750.7748 | 851.7748 | 330.8583 | 254.2804
751.7862 | 852.7862 | 330.7852 | 254.5402
752.7777 | 853.7777 | 330.6516 | 254.4394
753.7791 | 854.7791 | 330.6397 | 254.8824
754.7806 | 855.7806 | 330.5819 | 255.184
755.782 | 856.782 | 330.6852 | 255.0377
756.7834 | 857.7834 | 330.8231 | 254.7366
757.7849 | 858.7849 | 330.8154 | 255.3542
758.7763 | 859.7763 | 330.785 | 255.2789
759.7777 | 860.7777 | 330.8179 | 255.8748
760.7792 | 861.7792 | 330.8741 | 255.0378
761.7806 | 862.7806 | 330.873 | 255.548
762.7821 | 863.7821 | 330.8283 | 255.9965
763.7835 | 864.7835 | 330.7771 | 256.3558
764.7749 | 865.7749 | 330.6752 | 256.732
765.7864 | 866.7864 | 330.6096 | 256.9678
766.7778 | 867.7778 | 330.5763 | 256.7783
767.7792 | 868.7792 | 330.5106 | 257.0827
768.7807 | 869.7807 | 330.5558 | 256.9407
769.7821 | 870.7821 | 330.7071 | 257.1059
770.7836 | 871.7836 | 330.8585 | 257.5556
771.785 | 872.785 | 330.949 | 257.9204
772.7764 | 873.7764 | 331.026 | 258.153
773.7779 | 874.7779 | 331.0535 | 258.395
774.7793 | 875.7793 | 331.0698 | 258.5528
775.7807 | 876.7807 | 331.1412 | 258.039
776.7822 | 877.7822 | 331.2044 | 257.9703
777.7836 | 878.7836 | 331.1915 | 258.355
778.7751 | 879.7751 | 331.1566 | 258.7402
779.7865 | 880.7865 | 331.1647 | 258.8909
780.7779 | 881.7779 | 331.2593 | 258.2029
781.7794 | 882.7794 | 331.2373 | 258.6217
782.7808 | 883.7808 | 331.1641 | 258.9655
783.7823 | 884.7823 | 331.1874 | 259.2409
784.7737 | 885.7737 | 331.1776 | 259.2656
785.7851 | 886.7851 | 331.0724 | 258.8645
786.7766 | 887.7766 | 331.0745 | 259.2423
787.788 | 888.788 | 331.1166 | 259.3706
788.7794 | 889.7794 | 331.0607 | 259.6561
789.7809 | 890.7809 | 330.978 | 259.3537
790.7823 | 891.7823 | 330.9057 | 258.5054
791.7838 | 892.7838 | 330.8951 | 258.3647
792.7752 | 893.7752 | 330.9576 | 257.946
793.7866 | 894.7866 | 331.0608 | 258.7234
794.7781 | 895.7781 | 331.164 | 258.9001
795.7795 | 896.7795 | 331.163 | 259.2382
796.7809 | 897.7809 | 331.0937 | 259.6035
797.7824 | 898.7824 | 330.997 | 259.9739
798.7838 | 899.7838 | 330.9508 | 260.1946
799.7853 | 900.7853 | 330.9247 | 260.3738
800.7767 | 901.7767 | 330.9687 | 260.7545
801.7781 | 902.7781 | 331.0569 | 261.007
802.7796 | 903.7796 | 331.1267 | 261.2554
803.781 | 904.781 | 331.1558 | 261.2809
804.7825 | 905.7825 | 331.069 | 261.3307
805.7839 | 906.7839 | 330.9798 | 261.2044
806.7753 | 907.7753 | 330.7821 | 261.1465
807.7868 | 908.7868 | 330.6119 | 261.5956
808.7782 | 909.7782 | 330.4346 | 261.8151
809.7796 | 910.7796 | 330.3283 | 262.1131
810.7811 | 911.7811 | 330.2483 | 262.4388
811.7825 | 912.7825 | 330.1427 | 262.6396
812.784 | 913.784 | 330.1363 | 262.8531
813.7854 | 914.7854 | 330.1601 | 262.724
814.7768 | 915.7768 | 330.0553 | 262.6222
815.7783 | 916.7783 | 329.8994 | 262.5951
816.7797 | 917.7797 | 329.7219 | 262.3256
817.7811 | 918.7811 | 329.5859 | 262.339
818.7826 | 919.7826 | 329.6016 | 262.8363
819.784 | 920.784 | 329.5971 | 263.1151
820.7754 | 921.7754 | 329.7258 | 262.4115
821.7869 | 922.7869 | 329.8218 | 262.1342
822.7783 | 923.7783 | 329.9084 | 261.9676
823.8699 | 924.8699 | 330.041 | 261.6773
824.7812 | 925.7812 | 330.0932 | 262.1314
825.7826 | 926.7826 | 330.1519 | 262.5941
826.7741 | 927.7741 | 330.2902 | 262.7672
827.7855 | 928.7855 | 330.3358 | 262.8906
828.777 | 929.777 | 330.3823 | 262.6219
829.7784 | 930.7784 | 330.326 | 262.3048
830.88 | 931.88 | 330.3653 | 262.7658
831.7813 | 932.7813 | 330.3344 | 263.3189
832.7827 | 933.7827 | 330.3145 | 263.0367
833.7842 | 934.7842 | 330.415 | 262.8579
834.7756 | 935.7756 | 330.4845 | 262.8865
835.787 | 936.787 | 330.4891 | 263.5074
836.7785 | 937.7785 | 330.6055 | 263.9037
837.7799 | 938.7799 | 330.6937 | 263.8947
838.7813 | 939.7813 | 330.8089 | 264.3142
839.7828 | 940.7828 | 330.9182 | 264.4525
840.7742 | 941.7742 | 330.9515 | 264.8108
841.7857 | 942.7857 | 330.9166 | 264.9761
842.7771 | 943.7771 | 330.9803 | 264.9529
843.7785 | 944.7785 | 331.1583 | 265.3458
844.78 | 945.78 | 331.2655 | 265.3447
845.7814 | 946.7814 | 331.3475 | 264.7816
846.7828 | 947.7828 | 331.2781 | 265.1664
847.7843 | 948.7843 | 331.2694 | 265.5795
848.7757 | 949.7757 | 331.3642 | 265.6987
849.7872 | 950.7872 | 331.3685 | 265.6635
850.7786 | 951.7786 | 331.3199 | 265.8919
851.78 | 952.78 | 331.2893 | 265.9775
852.7815 | 953.7815 | 331.3169 | 266.1881
853.7829 | 954.7829 | 331.4371 | 266.3778
854.7743 | 955.7743 | 331.5624 | 266.7792
855.7858 | 956.7858 | 331.5889 | 266.9449
856.7772 | 957.7772 | 331.5887 | 266.7793
857.7787 | 958.7787 | 331.5968 | 266.9877
858.7801 | 959.7801 | 331.5956 | 267.1704
859.7815 | 960.7815 | 331.7124 | 266.7625
860.783 | 961.783 | 331.7992 | 266.9378
861.7844 | 962.7844 | 331.8584 | 266.9652
862.7758 | 963.7758 | 331.8634 | 267.2915
863.7773 | 964.7773 | 331.8608 | 267.5129
864.7787 | 965.7787 | 331.9462 | 267.3714
865.7802 | 966.7802 | 331.9466 | 267.7483
866.7816 | 967.7816 | 331.9002 | 267.8282
867.783 | 968.783 | 331.8795 | 268.1605
868.7745 | 969.7745 | 331.8942 | 268.3713
869.7859 | 970.7859 | 331.8696 | 268.5472
870.7773 | 971.7773 | 331.8753 | 268.6254
871.7788 | 972.7788 | 331.8313 | 268.6751
872.7802 | 973.7802 | 331.7932 | 269.0212
873.7817 | 974.7817 | 331.7029 | 269.2866
874.7831 | 975.7831 | 331.671 | 269.0978
875.7845 | 976.7845 | 331.6418 | 269.3138
876.776 | 977.776 | 331.7117 | 269.3198
877.7874 | 978.7874 | 331.6772 | 269.3559
878.7789 | 979.7789 | 331.6423 | 269.5233
879.7803 | 980.7803 | 331.6968 | 269.7171
880.7817 | 981.7817 | 331.7086 | 269.8031
881.7832 | 982.7832 | 331.7379 | 269.3922
882.7746 | 983.7746 | 331.7929 | 269.3244
883.7861 | 984.7861 | 331.8063 | 269.5834
884.7775 | 985.7775 | 331.8308 | 269.6313
885.7789 | 986.7789 | 331.861 | 269.01
886.7804 | 987.7804 | 331.8246 | 268.9946
887.7818 | 988.7818 | 331.8513 | 269.1852
888.7832 | 989.7832 | 331.8229 | 269.675
889.7847 | 990.7847 | 331.8491 | 269.7081
890.7761 | 991.7761 | 331.7682 | 269.8238
891.7876 | 992.7876 | 331.7667 | 269.7941
892.779 | 993.779 | 331.7724 | 269.311
893.7804 | 994.7804 | 331.7423 | 269.3097
894.7819 | 995.7819 | 331.7416 | 269.5826
895.7833 | 996.7833 | 331.7766 | 269.8274
896.7747 | 997.7747 | 331.6775 | 269.884
897.7862 | 998.7862 | 331.517 | 269.6051
898.7776 | 999.7776 | 331.3508 | 269.8803
899.779 | 1000.779 | 331.2135 | 270.1438
900.7805 | 1001.7805 | 331.0556 | 269.6811
901.7819 | 1002.7819 | 330.8313 | 269.6444
902.7834 | 1003.7834 | 330.7742 | 269.8283
903.7848 | 1004.7848 | 330.8305 | 270.078
904.7762 | 1005.7762 | 330.913 | 270.2131
905.7777 | 1006.7777 | 330.9343 | 270.0731
906.7791 | 1007.7791 | 330.9323 | 270.4954 | Time of first failure
907.7806 | 1008.7806 | 330.9215 | 270.5857 | 907 | 0
908.782 | 1009.782 | 330.8753 | 270.5351 | 907 | 900
909.7834 | 1010.7834 | 330.8128 | 270.8718
910.7749 | 1011.7749 | 330.8451 | 270.7692
911.7863 | 1012.7863 | 330.8695 | 270.9774
912.7777 | 1013.7777 | 330.8136 | 271.1464
913.7792 | 1014.7792 | 330.754 | 271.2862
914.7806 | 1015.7806 | 330.7188 | 271.5281
915.7821 | 1016.7821 | 330.7313 | 271.825
916.7835 | 1017.7835 | 330.6349 | 271.9181
917.7849 | 1018.7849 | 330.6005 | 271.7241
918.7764 | 1019.7764 | 330.5386 | 271.8595
919.7778 | 1020.7778 | 330.512 | 271.6994
920.7792 | 1021.7792 | 330.5548 | 271.3075
921.7807 | 1022.7807 | 330.5467 | 271.5498
922.7821 | 1023.7821 | 330.5291 | 271.7303
923.7836 | 1024.7836 | 330.4769 | 271.741
924.775 | 1025.775 | 330.4285 | 271.7885
925.7864 | 1026.7864 | 330.419 | 272.1002
926.7779 | 1027.7779 | 330.4754 | 272.3826
927.7793 | 1028.7793 | 330.5171 | 272.5054
928.7808 | 1029.7808 | 330.6118 | 272.5686
929.7822 | 1030.7822 | 330.6133 | 272.8176
930.7836 | 1031.7836 | 330.4862 | 272.9458
931.7851 | 1032.7851 | 330.3851 | 272.5712
932.7765 | 1033.7765 | 330.2916 | 272.7531
933.788 | 1034.788 | 330.2511 | 272.3632
934.7794 | 1035.7794 | 330.2075 | 272.6246
935.7808 | 1036.7808 | 330.0728 | 272.8303
936.7823 | 1037.7823 | 329.8775 | 273.0109
937.7837 | 1038.7837 | 329.7705 | 273.0882
938.7751 | 1039.7751 | 329.7846 | 272.9795
939.7866 | 1040.7866 | 329.8492 | 273.0928
940.778 | 1041.778 | 329.9177 | 273.3001
941.7794 | 1042.7794 | 329.9064 | 273.5036
942.7809 | 1043.7809 | 329.9248 | 273.4355
943.7823 | 1044.7823 | 329.8725 | 273.5455
944.7838 | 1045.7838 | 329.8249 | 273.5296
945.7852 | 1046.7852 | 329.8831 | 273.6174
946.7766 | 1047.7766 | 330.05 | 273.7833
947.7781 | 1048.7781 | 330.1428 | 273.8519
948.7795 | 1049.7795 | 330.1248 | 273.8539
949.7809 | 1050.7809 | 330.1355 | 274.151
950.7824 | 1051.7824 | 330.2543 | 274.2514
951.7838 | 1052.7838 | 330.3448 | 274.3413
952.7753 | 1053.7753 | 330.4183 | 274.5734
953.7867 | 1054.7867 | 330.4151 | 274.513
954.7781 | 1055.7781 | 330.533 | 274.5849
955.7796 | 1056.7796 | 330.614 | 274.7342
956.781 | 1057.781 | 330.6582 | 274.9282
957.7825 | 1058.7825 | 330.8067 | 274.5787
958.7739 | 1059.7739 | 330.8731 | 274.0825
959.7853 | 1060.7853 | 330.7753 | 274.3302
960.7768 | 1061.7768 | 330.6259 | 274.369
961.7782 | 1062.7782 | 330.5736 | 274.3796
962.7796 | 1063.7796 | 330.5766 | 274.4369
963.7811 | 1064.7811 | 330.6522 | 274.1509
964.7825 | 1065.7825 | 330.7583 | 274.3028
965.784 | 1066.784 | 330.8204 | 274.5554
966.7754 | 1067.7754 | 330.9211 | 274.4609
967.7868 | 1068.7868 | 330.9993 | 274.6173
968.7783 | 1069.7783 | 331.1514 | 274.8124
969.7797 | 1070.7797 | 331.2582 | 274.8877
970.7811 | 1071.7811 | 331.418 | 275.1113
971.7826 | 1072.7826 | 331.5343 | 275.3782
972.774 | 1073.774 | 331.6439 | 275.3869
973.7855 | 1074.7855 | 331.657 | 275.3816
974.7769 | 1075.7769 | 331.634 | 275.3946
975.7783 | 1076.7783 | 331.602 | 275.3762
976.7798 | 1077.7798 | 331.5186 | 275.4593
977.7812 | 1078.7812 | 331.5737 | 275.5883
978.7827 | 1079.7827 | 331.6308 | 275.7479
979.7841 | 1080.7841 | 331.6691 | 275.6833
980.7755 | 1081.7755 | 331.6364 | 275.4872
981.787 | 1082.787 | 331.5593 | 275.6046
982.7784 | 1083.7784 | 331.406 | 275.3686
983.7798 | 1084.7798 | 331.2655 | 275.441
984.7813 | 1085.7813 | 331.1283 | 275.2968
985.7827 | 1086.7827 | 331.1263 | 275.4776
986.7842 | 1087.7842 | 331.1829 | 275.6207
987.7856 | 1088.7856 | 331.124 | 275.8791
988.777 | 1089.777 | 330.9671 | 275.808
989.7785 | 1090.7785 | 330.9189 | 275.6207
990.7799 | 1091.7799 | 330.884 | 274.8993
991.7813 | 1092.7813 | 330.8988 | 274.4809
992.7828 | 1093.7828 | 330.8327 | 274.6701
993.7842 | 1094.7842 | 330.75 | 274.9489
994.7756 | 1095.7756 | 330.6683 | 275.2209
995.7871 | 1096.7871 | 330.5582 | 275.476
996.7785 | 1097.7785 | 330.5457 | 275.5745
997.78 | 1098.78 | 330.5906 | 275.6776
998.7814 | 1099.7814 | 330.5782 | 275.6199
999.7828 | 1100.7828 | 330.5818 | 275.7613
1000.7743 | 1101.7743 | 330.6148 | 275.8613
1001.7857 | 1102.7857 | 330.5785 | 275.3451
1002.7772 | 1103.7772 | 330.5535 | 275.4334
1003.7886 | 1104.7886 | 330.5641 | 275.0163
1004.78 | 1105.78 | 330.568 | 275.2184
1005.7815 | 1106.7815 | 330.6088 | 275.5419
1006.7829 | 1107.7829 | 330.498 | 275.679
1007.7844 | 1108.7844 | 330.3444 | 275.6354
1008.7758 | 1109.7758 | 330.4026 | 275.4808
1009.7872 | 1110.7872 | 330.3871 | 275.6845
1010.7787 | 1111.7787 | 330.2168 | 275.5029
1011.7801 | 1112.7801 | 330.0275 | 275.5087
1012.7815 | 1113.7815 | 329.8663 | 275.7092
1013.783 | 1114.783 | 329.8855 | 275.1359
1014.7744 | 1115.7744 | 329.9823 | 275.2774
1015.7859 | 1116.7859 | 330.0389 | 275.3336
1016.7773 | 1117.7773 | 330.078 | 275.1125
1017.7787 | 1118.7787 | 330.146 | 275.1087
1018.7802 | 1119.7802 | 330.2316 | 275.0337
1019.7816 | 1120.7816 | 330.2962 | 275.2913
1020.783 | 1121.783 | 330.2918 | 275.5051
1021.7845 | 1122.7845 | 330.2078 | 275.5833
1022.7759 | 1123.7759 | 330.1797 | 275.709
1023.7874 | 1124.7874 | 330.1398 | 275.6941
1024.7788 | 1125.7788 | 330.0905 | 275.5757
1025.7802 | 1126.7802 | 330.1012 | 275.5012
1026.7817 | 1127.7817 | 330.1117 | 275.7899
1027.7831 | 1128.7831 | 330.0664 | 276.083
1028.7745 | 1129.7745 | 330.0294 | 276.2616
1029.786 | 1130.786 | 330.0643 | 276.2065
1030.7774 | 1131.7774 | 330.2117 | 276.2627
1031.7789 | 1132.7789 | 330.3146 | 276.5012
1032.7803 | 1133.7803 | 330.4428 | 276.606
1033.7817 | 1134.7817 | 330.6178 | 276.7199
1034.7832 | 1135.7832 | 330.7294 | 276.6149
1035.7846 | 1136.7846 | 330.7055 | 276.3503
1036.776 | 1137.776 | 330.4809 | 276.4492
1037.7775 | 1138.7775 | 330.4161 | 276.7076
1038.7789 | 1139.7789 | 330.3892 | 276.6875
1039.7804 | 1140.7804 | 330.3776 | 276.6058
1040.7818 | 1141.7818 | 330.3104 | 276.7761
1041.7832 | 1142.7832 | 330.2019 | 276.348
1042.7747 | 1143.7747 | 330.2193 | 276.3206
1043.7861 | 1144.7861 | 330.1884 | 276.4367
1044.7775 | 1145.7775 | 330.0441 | 276.4015
1045.779 | 1146.779 | 330.0578 | 276.4417
1046.7804 | 1147.7804 | 329.9625 | 276.5819
1047.7819 | 1148.7819 | 329.993 | 276.7673
1048.7833 | 1149.7833 | 330.0741 | 276.8452
1049.7847 | 1150.7847 | 330.2223 | 276.7
1050.7762 | 1151.7762 | 330.3808 | 276.6732
1051.7876 | 1152.7876 | 330.4773 | 276.7428
1052.7791 | 1153.7791 | 330.5211 | 276.9704
1053.7805 | 1154.7805 | 330.6311 | 276.7112
1054.7819 | 1155.7819 | 330.6753 | 276.8581
1055.7834 | 1156.7834 | 330.6915 | 276.7668
1056.7748 | 1157.7748 | 330.7261 | 277.0388
1057.7863 | 1158.7863 | 330.6375 | 277.2941
1058.7777 | 1159.7777 | 330.5422 | 276.8183
1059.7791 | 1160.7791 | 330.5558 | 276.9975
1060.7806 | 1161.7806 | 330.6422 | 277.0081
1061.782 | 1162.782 | 330.7236 | 277.0166
1062.7834 | 1163.7834 | 330.734 | 277.3029
1063.7849 | 1164.7849 | 330.7881 | 277.3765
1064.7763 | 1165.7763 | 330.9128 | 277.6083
1065.7878 | 1166.7878 | 330.9754 | 277.8128
1066.7792 | 1167.7792 | 331.0133 | 277.9632
1067.7806 | 1168.7806 | 331.1233 | 277.8201
1068.7821 | 1169.7821 | 331.191 | 277.6866
1069.7835 | 1170.7835 | 331.2259 | 277.4057
1070.7749 | 1171.7749 | 331.2016 | 277.6708
1071.7964 | 1172.7964 | 331.3 | 277.666
1072.7778 | 1173.7778 | 331.3175 | 277.7428
1073.7792 | 1174.7792 | 331.348 | 277.8887
1074.7807 | 1175.7807 | 331.4003 | 278.0934
1075.7821 | 1176.7821 | 331.4143 | 278.1364
1076.7836 | 1177.7836 | 331.4155 | 278.1344
1077.785 | 1178.785 | 331.406 | 277.9115
1078.7764 | 1179.7764 | 331.4411 | 277.9555
1079.7779 | 1180.7779 | 331.443 | 277.8682
1080.7793 | 1181.7793 | 331.3931 | 277.7922
1081.7808 | 1182.7808 | 331.4247 | 277.9727
1082.7822 | 1183.7822 | 331.4755 | 278.1207
1083.7836 | 1184.7836 | 331.4736 | 278.1129
1084.7751 | 1185.7751 | 331.4005 | 278.2526
1085.7865 | 1186.7865 | 331.3752 | 278.2454
1086.7779 | 1187.7779 | 331.3212 | 278.5063
1087.7794 | 1188.7794 | 331.3966 | 278.6634
1088.7808 | 1189.7808 | 331.478 | 278.8981
1089.7823 | 1190.7823 | 331.4428 | 279.0064
1090.7837 | 1191.7837 | 331.4055 | 279.2217
1091.7851 | 1192.7851 | 331.4339 | 279.3059
1092.7766 | 1193.7766 | 331.5141 | 279.3188
1093.778 | 1194.778 | 331.596 | 278.6197
1094.7794 | 1195.7794 | 331.6112 | 278.7779
1095.7809 | 1196.7809 | 331.7243 | 278.8916
1096.7823 | 1197.7823 | 331.781 | 278.9847
1097.7838 | 1198.7838 | 331.8211 | 279.1162
1098.7752 | 1199.7752 | 331.7968 | 279.0061
1099.7866 | 1200.7866 | 331.7946 | 278.6039
1100.7781 | 1201.7781 | 331.7252 | 278.8894
1101.7795 | 1202.7795 | 331.743 | 279.0499
1102.781 | 1203.781 | 331.7171 | 279.0416
1103.7824 | 1204.7824 | 331.701 | 278.9624
1104.7838 | 1205.7838 | 331.7625 | 278.9573
1105.7853 | 1206.7853 | 331.8172 | 279.0752
1106.7767 | 1207.7767 | 331.828 | 278.0857
1107.7882 | 1208.7882 | 331.7074 | 278.2846
1108.7796 | 1209.7796 | 331.6538 | 278.3444
1109.781 | 1210.781 | 331.6805 | 278.534
1110.7825 | 1211.7825 | 331.5853 | 278.6381
1111.7839 | 1212.7839 | 331.5762 | 278.5082
1112.7753 | 1213.7753 | 331.5751 | 278.5058
1113.7868 | 1214.7868 | 331.5028 | 278.5777
1114.7782 | 1215.7782 | 331.3789 | 278.6722
1115.7796 | 1216.7796 | 331.3179 | 278.567
1116.7811 | 1217.7811 | 331.2595 | 277.8756
1117.7825 | 1218.7825 | 331.251 | 277.8159
1118.784 | 1219.784 | 331.2522 | 278.091
1119.7854 | 1220.7854 | 331.1866 | 277.7657
1120.7768 | 1221.7768 | 331.1103 | 277.9548
1121.7783 | 1222.7783 | 331.1285 | 278.2811
1122.7797 | 1223.7797 | 331.1154 | 278.0969
1123.7811 | 1224.7811 | 331.1197 | 278.3848
1124.7826 | 1225.7826 | 331.0386 | 278.609
1125.784 | 1226.784 | 331.0168 | 278.6295
1126.7755 | 1227.7755 | 331.0384 | 278.7832
1127.7869 | 1228.7869 | 331.1555 | 278.999
1128.7783 | 1229.7783 | 331.2632 | 278.9227
1129.7798 | 1230.7798 | 331.2192 | 278.8403
1130.7812 | 1231.7812 | 331.2177 | 278.5317
1131.7827 | 1232.7827 | 331.2685 | 278.2923
1132.7741 | 1233.7741 | 331.3053 | 278.5106
1133.7855 | 1234.7855 | 331.331 | 278.3151
1134.777 | 1235.777 | 331.3236 | 278.3486
1135.7784 | 1236.7784 | 331.2809 | 278.3081
1136.7798 | 1237.7798 | 331.2805 | 278.0379
1137.7813 | 1238.7813 | 331.1628 | 277.5165
1138.7827 | 1239.7827 | 331.1216 | 277.4182
1139.7842 | 1240.7842 | 331.1403 | 277.994
1140.7756 | 1241.7756 | 331.1809 | 277.8511
1141.777 | 1242.777 | 331.1913 | 277.5066
1142.7785 | 1243.7785 | 331.1526 | 277.3121
1143.7799 | 1244.7799 | 331.1113 | 277.8156
1144.7813 | 1245.7813 | 331.1317 | 278.1578
1145.7828 | 1246.7828 | 331.0887 | 277.9382
1146.7842 | 1247.7842 | 331.1499 | 277.806
1147.7857 | 1248.7857 | 331.2118 | 277.9719
1148.7771 | 1249.7771 | 331.3316 | 277.9178
1149.7785 | 1250.7785 | 331.4753 | 277.4971
1150.78 | 1251.78 | 331.5275 | 277.9401
1151.7814 | 1252.7814 | 331.5155 | 278.0996
1152.7829 | 1253.7829 | 331.6405 | 278.037
1153.7843 | 1254.7843 | 331.6463 | 278.1391
1154.7757 | 1255.7757 | 331.6469 | 278.076
1155.7872 | 1256.7872 | 331.7011 | 278.2916
1156.7786 | 1257.7786 | 331.7012 | 277.668
1157.78 | 1258.78 | 331.7161 | 277.6745
1158.7815 | 1259.7815 | 331.747 | 278.0879
1159.7829 | 1260.7829 | 331.7281 | 278.3601
1160.7743 | 1261.7743 | 331.7141 | 278.1364
1161.7858 | 1262.7858 | 331.7075 | 278.6141
1162.7772 | 1263.7772 | 331.6824 | 278.6857
1163.7787 | 1264.7787 | 331.6363 | 278.7713
1164.7801 | 1265.7801 | 331.5554 | 278.8745
1165.7815 | 1266.7815 | 331.5355 | 279.0382
1166.783 | 1267.783 | 331.5228 | 278.9359
1167.7844 | 1268.7844 | 331.4736 | 279.2139
1168.7758 | 1269.7758 | 331.4696 | 279.4517
1169.7873 | 1270.7873 | 331.5516 | 279.2073
1170.7787 | 1271.7787 | 331.5733 | 278.6377
1171.7802 | 1272.7802 | 331.4954 | 278.7953
1172.7816 | 1273.7816 | 331.4061 | 279.0494
1173.783 | 1274.783 | 331.3938 | 279.0404
1174.7745 | 1275.7745 | 331.4234 | 278.9904
1175.7859 | 1276.7859 | 331.4319 | 278.6274
1176.7774 | 1277.7774 | 331.416 | 278.8674
1177.7788 | 1278.7788 | 331.3899 | 278.6249
1178.7802 | 1279.7802 | 331.3274 | 278.2034
1179.7817 | 1280.7817 | 331.1927 | 278.0465
1180.7831 | 1281.7831 | 331.166 | 278.2028
1181.7846 | 1282.7846 | 331.1586 | 278.2587
1182.776 | 1283.776 | 331.1137 | 278.3314
1183.7874 | 1284.7874 | 331.0199 | 278.2705
1184.899 | 1285.899 | 330.9912 | 277.6737
1185.7803 | 1286.7803 | 330.9093 | 277.6501
1186.7817 | 1287.7817 | 330.8175 | 278.0352
1187.7832 | 1288.7832 | 330.8413 | 278.3161
1188.7746 | 1289.7746 | 330.7931 | 278.5449
1189.7861 | 1290.7861 | 330.6604 | 278.7361
1190.7775 | 1291.7775 | 330.5972 | 278.7634
1191.7889 | 1292.7889 | 330.6697 | 278.411
1192.7804 | 1293.7804 | 330.6961 | 277.8231
1193.7818 | 1294.7818 | 330.7088 | 277.4686
1194.7832 | 1295.7832 | 330.6152 | 277.2117
1195.7847 | 1296.7847 | 330.5084 | 277.0018
1196.7761 | 1297.7761 | 330.4947 | 277.4247
1197.7776 | 1298.7776 | 330.4556 | 277.7713
1198.779 | 1299.779 | 330.3606 | 277.7459
1199.7804 | 1300.7804 | 330.2248 | 277.5696
1200.7819 | 1301.7819 | 330.131 | 277.4614
1201.7833 | 1302.7833 | 330.205 | 277.4486
1202.7747 | 1303.7747 | 330.2286 | 277.443
1203.7862 | 1304.7862 | 330.2616 | 277.0805
1204.7776 | 1305.7776 | 330.3236 | 277.3631
1205.7791 | 1306.7791 | 330.4088 | 277.6141
1206.7805 | 1307.7805 | 330.4583 | 277.0812
1207.7819 | 1308.7819 | 330.4895 | 276.9554
1208.7834 | 1309.7834 | 330.5116 | 277.1529
1209.7848 | 1310.7848 | 330.5409 | 276.9625
1210.7762 | 1311.7762 | 330.6113 | 277.4537
1211.7777 | 1312.7777 | 330.6527 | 277.6323
1212.7791 | 1313.7791 | 330.6329 | 278.008
1213.7806 | 1314.7806 | 330.5552 | 278.2317
1214.782 | 1315.782 | 330.5685 | 277.7625
1215.7834 | 1316.7834 | 330.5236 | 277.2631
1216.7749 | 1317.7749 | 330.5133 | 277.4126
1217.7863 | 1318.7863 | 330.5178 | 277.6464
1218.7777 | 1319.7777 | 330.6065 | 277.6657
1219.7792 | 1320.7792 | 330.6712 | 277.7239
1220.7806 | 1321.7806 | 330.7202 | 277.7089
1221.7821 | 1322.7821 | 330.793 | 277.5911
1222.7735 | 1323.7735 | 330.8306 | 277.5687
1223.7849 | 1324.7849 | 330.8337 | 277.3793
1224.7764 | 1325.7764 | 330.9389 | 276.9048
1225.7778 | 1326.7778 | 330.9747 | 276.396
1226.7793 | 1327.7793 | 331.0012 | 276.405
1227.7807 | 1328.7807 | 330.9992 | 276.6236
1228.7821 | 1329.7821 | 331.0566 | 277.1031
1229.7836 | 1330.7836 | 331.0382 | 277.4101
1230.775 | 1331.775 | 331.0267 | 277.1216
1231.7865 | 1332.7865 | 331.1033 | 277.6601
1232.7779 | 1333.7779 | 331.1705 | 277.2938
1233.7793 | 1334.7793 | 331.2512 | 277.5707
1234.7808 | 1335.7808 | 331.2145 | 277.7756
1235.7822 | 1336.7822 | 331.1108 | 276.8182
1236.7836 | 1337.7836 | 331.0555 | 276.1217
1237.7851 | 1338.7851 | 331.1049 | 275.9087
1238.7765 | 1339.7765 | 331.2187 | 275.9141
1239.788 | 1340.788 | 331.3984 | 276.048
1240.7794 | 1341.7794 | 331.4841 | 275.7863
1241.7808 | 1342.7808 | 331.505 | 276.2449
1242.7823 | 1343.7823 | 331.5488 | 276.7372
1243.7837 | 1344.7837 | 331.6076 | 276.9282
1244.7851 | 1345.7851 | 331.6627 | 276.8527
1245.7866 | 1346.7866 | 331.6459 | 276.5722
1246.778 | 1347.778 | 331.6619 | 276.8534
1247.7794 | 1348.7794 | 331.6578 | 277.3005
1248.7809 | 1349.7809 | 331.6263 | 277.3076
1249.7823 | 1350.7823 | 331.7244 | 277.4059
1250.7838 | 1351.7838 | 331.9369 | 276.499
1251.7852 | 1352.7852 | 332.092 | 277.0623
1252.7766 | 1353.7766 | 332.1163 | 277.0938
1253.7781 | 1354.7781 | 332.0929 | 277.3871
1254.7795 | 1355.7795 | 332.0648 | 277.7012
1255.781 | 1356.781 | 332.0263 | 278.1895
1256.7824 | 1357.7824 | 332.0872 | 278.5288
1257.7838 | 1358.7838 | 332.0726 | 278.6814
1258.7753 | 1359.7753 | 332.0446 | 278.1248
1259.7867 | 1360.7867 | 332.0354 | 278.2521
1260.7781 | 1361.7781 | 332.0058 | 277.6951
1261.7796 | 1362.7796 | 331.9373 | 278.0489
1262.781 | 1363.781 | 331.9629 | 277.9178
1263.7825 | 1364.7825 | 331.9487 | 278.3869
1264.7839 | 1365.7839 | 331.8712 | 278.2272
1265.7853 | 1366.7853 | 331.8675 | 278.353
1266.7768 | 1367.7768 | 331.7681 | 278.4599
1267.7782 | 1368.7782 | 331.7377 | 278.5465
1268.7796 | 1369.7796 | 331.7331 | 278.2211
1269.7811 | 1370.7811 | 331.6091 | 278.7022
1270.7825 | 1371.7825 | 331.6284 | 278.7684
1271.784 | 1372.784 | 331.6849 | 278.9885
1272.7754 | 1373.7754 | 331.6674 | 278.9768
1273.7868 | 1374.7868 | 331.6084 | 279.1321
1274.7783 | 1375.7783 | 331.6203 | 279.3455
1275.7797 | 1376.7797 | 331.6505 | 279.4599
1276.7812 | 1377.7812 | 331.6398 | 279.6969
1277.7826 | 1378.7826 | 331.5607 | 279.1904
1278.774 | 1379.774 | 331.5467 | 278.9147
1279.7855 | 1380.7855 | 331.4669 | 279.1988
1280.7769 | 1381.7769 | 331.4006 | 278.8754
1281.7783 | 1382.7783 | 331.3952 | 278.3889
1282.7798 | 1383.7798 | 331.3654 | 278.529
1283.7812 | 1384.7812 | 331.2735 | 278.7258
1284.7827 | 1385.7827 | 331.1941 | 279.0033
1285.7841 | 1386.7841 | 331.2039 | 279.3785
1286.7755 | 1387.7755 | 331.1676 | 279.4391
1287.787 | 1388.787 | 331.1074 | 278.9436
1288.7784 | 1389.7784 | 331.0426 | 278.9694
1289.7798 | 1390.7798 | 330.9875 | 279.1377
1290.7813 | 1391.7813 | 330.9325 | 279.3998
1291.7827 | 1392.7827 | 330.9936 | 279.2728
1292.7842 | 1393.7842 | 331.0898 | 279.461
1293.7856 | 1394.7856 | 331.1561 | 279.5851
1294.777 | 1395.777 | 331.2043 | 279.2411
1295.7785 | 1396.7785 | 331.3014 | 279.1319
1296.7799 | 1397.7799 | 331.3936 | 279.0757
1297.7813 | 1398.7813 | 331.4206 | 278.5049
1298.7828 | 1399.7828 | 331.4597 | 278.1329
1299.7842 | 1400.7842 | 331.5191 | 278.2209
1300.7757 | 1401.7757 | 331.6314 | 278.5888
1301.7871 | 1402.7871 | 331.6324 | 279.0179
1302.7785 | 1403.7785 | 331.5247 | 278.8381
1303.78 | 1404.78 | 331.3964 | 278.6099
1304.7814 | 1405.7814 | 331.4525 | 278.073
1305.7829 | 1406.7829 | 331.6176 | 278.3401
1306.7743 | 1407.7743 | 331.7263 | 278.3918
1307.7857 | 1408.7857 | 331.7381 | 278.5784
1308.7772 | 1409.7772 | 331.7196 | 278.262
1309.7786 | 1410.7786 | 331.7858 | 278.5829
1310.78 | 1411.78 | 331.7714 | 278.9307
1311.7815 | 1412.7815 | 331.814 | 278.5387
1312.7829 | 1413.7829 | 331.85 | 278.6586
1313.7844 | 1414.7844 | 332.0292 | 279.0099
1314.7758 | 1415.7758 | 332.1702 | 279.3452
1315.7872 | 1416.7872 | 332.2286 | 279.6496
1316.7787 | 1417.7787 | 332.2012 | 279.1761
1317.7801 | 1418.7801 | 332.2055 | 279.1542
1318.7815 | 1419.7815 | 332.2067 | 279.3313
1319.783 | 1420.783 | 332.214 | 279.0629
1320.7844 | 1421.7844 | 332.1924 | 278.8364
1321.7859 | 1422.7859 | 332.1513 | 279.154
1322.7773 | 1423.7773 | 332.0407 | 279.3226
1323.7887 | 1424.7887 | 331.9001 | 278.4156
1324.7802 | 1425.7802 | 331.8057 | 277.7762
1325.7816 | 1426.7816 | 331.6786 | 277.9021
1326.7831 | 1427.7831 | 331.612 | 277.5775
1327.7845 | 1428.7845 | 331.5923 | 277.6003
1328.7759 | 1429.7759 | 331.3545 | 278.0288
1329.7874 | 1430.7874 | 331.1031 | 277.5255
1330.7788 | 1431.7788 | 330.8353 | 277.2161
1331.7802 | 1432.7802 | 330.7733 | 277.5445
1332.7817 | 1433.7817 | 330.7799 | 277.9094
1333.7831 | 1434.7831 | 330.8683 | 278.0934
1334.7745 | 1435.7745 | 330.8611 | 278.4718
1335.786 | 1436.786 | 330.9116 | 278.7242
1336.7774 | 1437.7774 | 330.9021 | 279.0388
1337.7789 | 1438.7789 | 330.9369 | 279.2087
1338.7803 | 1439.7803 | 330.9635 | 278.8705
1339.7817 | 1440.7817 | 331.0567 | 278.8317
1340.7832 | 1441.7832 | 331.1322 | 279.0018
1341.7846 | 1442.7846 | 331.2151 | 279.1597
1342.776 | 1443.776 | 331.2063 | 279.1856
1343.7875 | 1444.7875 | 331.108 | 278.3893
1344.7789 | 1445.7789 | 331.0123 | 278.0367
1345.7804 | 1446.7804 | 331.0997 | 278.1594
1346.7818 | 1447.7818 | 331.0909 | 278.2066
1347.7832 | 1448.7832 | 331.0293 | 278.2954
1348.7747 | 1449.7747 | 331.0499 | 278.346
1349.7861 | 1450.7861 | 331.0825 | 278.7844
1350.7776 | 1451.7776 | 331.1389 | 279.2349
1351.779 | 1452.779 | 331.2394 | 279.5028
1352.7804 | 1453.7804 | 331.2813 | 279.5271
1353.7819 | 1454.7819 | 331.2392 | 279.677
1354.7833 | 1455.7833 | 331.2333 | 279.314
1355.7848 | 1456.7848 | 331.306 | 279.0215
1356.7762 | 1457.7762 | 331.2924 | 279.2522
1357.7876 | 1458.7876 | 331.2183 | 279.5306
1358.7791 | 1459.7791 | 331.1896 | 279.504
1359.7805 | 1460.7805 | 331.1974 | 279.2177
1360.7819 | 1461.7819 | 331.2045 | 279.2807
1361.7834 | 1462.7834 | 331.1905 | 279.5639
1362.7748 | 1463.7748 | 331.1795 | 279.7303
1363.7863 | 1464.7863 | 331.1773 | 279.6997
1364.7777 | 1465.7777 | 331.2073 | 279.5314
1365.7791 | 1466.7791 | 331.1071 | 279.4745
1366.7806 | 1467.7806 | 331.0545 | 279.2629
1367.782 | 1468.782 | 331.0948 | 278.9271
1368.7834 | 1469.7834 | 331.173 | 278.8167
1369.7849 | 1470.7849 | 331.1651 | 279.045
1370.7763 | 1471.7763 | 331.1014 | 279.024
1371.7878 | 1472.7878 | 331.0484 | 278.9015
1372.7792 | 1473.7792 | 330.929 | 278.9046
1373.7806 | 1474.7806 | 330.6548 | 278.1277
1374.7821 | 1475.7821 | 330.4798 | 277.7765
1375.7835 | 1476.7835 | 330.2733 | 277.9888
1376.7749 | 1477.7749 | 330.1115 | 277.4399
1377.7864 | 1478.7864 | 329.9944 | 277.9726
1378.7778 | 1479.7778 | 329.9831 | 278.4965
1379.7793 | 1480.7793 | 330.058 | 278.9235
1380.7807 | 1481.7807 | 330.1719 | 279.3203
1381.7821 | 1482.7821 | 330.2028 | 279.1175
1382.7736 | 1483.7736 | 330.1672 | 279.4079
1383.785 | 1484.785 | 330.2105 | 279.4766
1384.7764 | 1485.7764 | 330.3088 | 279.1348
1385.7879 | 1486.7879 | 330.4462 | 279.0797
1386.7793 | 1487.7793 | 330.5403 | 278.9285
1387.7808 | 1488.7808 | 330.597 | 278.8644
1388.7822 | 1489.7822 | 330.697 | 279.3093
1389.7836 | 1490.7836 | 330.776 | 279.6298
1390.7751 | 1491.7751 | 330.8115 | 279.8065
1391.7865 | 1492.7865 | 330.8087 | 279.0526
1392.7779 | 1493.7779 | 330.8601 | 278.4805
1393.7794 | 1494.7794 | 330.906 | 277.9426
1394.7808 | 1495.7808 | 330.9072 | 278.1991
1395.7823 | 1496.7823 | 330.9274 | 278.1587
1396.7837 | 1497.7837 | 330.9319 | 278.1458
1397.7851 | 1498.7851 | 330.944 | 278.3313
1398.7766 | 1499.7766 | 330.8632 | 278.3909
1399.778 | 1500.778 | 330.9724 | 278.322
1400.7795 | 1501.7795 | 331.1291 | 278.4741
1401.7809 | 1502.7809 | 331.2157 | 278.1276
1402.7823 | 1503.7823 | 331.3314 | 278.1463
1403.7838 | 1504.7838 | 331.3497 | 278.445
1404.7752 | 1505.7752 | 331.3266 | 278.4567
1405.7867 | 1506.7867 | 331.4741 | 278.272
1406.7781 | 1507.7781 | 331.6318 | 278.3553
1407.7795 | 1508.7795 | 331.7811 | 278.881
1408.781 | 1509.781 | 331.8736 | 278.8822
1409.7824 | 1510.7824 | 331.8629 | 279.1679
1410.7838 | 1511.7838 | 331.8689 | 279.4313
1411.7853 | 1512.7853 | 331.9513 | 279.2484
1412.7767 | 1513.7767 | 332.0336 | 279.5497
1413.7781 | 1514.7781 | 332.1345 | 279.52
1414.7796 | 1515.7796 | 332.2019 | 279.8498
1415.781 | 1516.781 | 332.2195 | 279.8604
1416.7825 | 1517.7825 | 332.1614 | 279.3794
1417.7839 | 1518.7839 | 332.1205 | 279.5828
1418.7753 | 1519.7753 | 331.9604 | 279.6966
1419.7868 | 1520.7868 | 331.8815 | 279.1459
1420.7782 | 1521.7782 | 331.8263 | 279.1293
1421.7796 | 1522.7796 | 331.7679 | 278.8383
1422.7811 | 1523.7811 | 331.8533 | 278.4688
1423.7825 | 1524.7825 | 331.9132 | 278.2579
1424.784 | 1525.784 | 331.9283 | 278.2767
1425.7854 | 1526.7854 | 331.9634 | 277.8901
1426.7768 | 1527.7768 | 331.9432 | 277.4381
1427.7783 | 1528.7783 | 331.9531 | 277.5636
1428.7797 | 1529.7797 | 332.0013 | 277.7912
1429.7812 | 1530.7812 | 332.0139 | 277.2545
1430.7826 | 1531.7826 | 331.9942 | 277.0551
1431.784 | 1532.784 | 332.0826 | 277.2567
1432.7755 | 1533.7755 | 332.1516 | 277.2578
1433.7869 | 1534.7869 | 332.1886 | 276.8751
1434.7783 | 1535.7783 | 332.1964 | 276.9987
1435.7798 | 1536.7798 | 332.2668 | 277.1171
1436.7812 | 1537.7812 | 332.2885 | 277.2023
1437.7827 | 1538.7827 | 332.2858 | 277.483
1438.7741 | 1539.7741 | 332.2399 | 278.0851
1439.7855 | 1540.7855 | 332.3063 | 277.17
1440.777 | 1541.777 | 332.2998 | 277.6926
1441.7884 | 1542.7884 | 332.3904 | 278.1078
1442.7798 | 1543.7798 | 332.4534 | 278.3837
1443.7813 | 1544.7813 | 332.4179 | 278.463
1444.7827 | 1545.7827 | 332.2989 | 278.5252
1445.7842 | 1546.7842 | 332.207 | 278.7517
1446.7756 | 1547.7756 | 332.1023 | 278.8079
1447.787 | 1548.787 | 332.007 | 278.478
1448.7785 | 1549.7785 | 331.8747 | 277.9932
1449.7799 | 1550.7799 | 331.7991 | 277.6636
1450.7814 | 1551.7814 | 331.6646 | 278.3345
1451.7828 | 1552.7828 | 331.6968 | 278.4354
1452.7742 | 1553.7742 | 331.6297 | 278.561
1453.7857 | 1554.7857 | 331.4076 | 278.3323
1454.7771 | 1555.7771 | 331.1125 | 278.6073
1455.7785 | 1556.7785 | 330.9092 | 278.5109
1456.78 | 1557.78 | 330.8592 | 278.4183
1457.7814 | 1558.7814 | 330.8934 | 278.8816
1458.7728 | 1559.7728 | 330.9551 | 278.7182
1459.7843 | 1560.7843 | 330.9169 | 279.062
1460.7757 | 1561.7757 | 330.9344 | 278.9683
1461.7872 | 1562.7872 | 330.973 | 278.8595
1462.7786 | 1563.7786 | 330.999 | 279.2273
1463.78 | 1564.78 | 330.9137 | 279.2
1464.7815 | 1565.7815 | 330.8753 | 279.0101
1465.7829 | 1566.7829 | 330.93 | 279.3708
1466.7844 | 1567.7844 | 331.0288 | 279.5987
1467.7858 | 1568.7858 | 331.0729 | 279.872
1468.7772 | 1569.7772 | 331.1 | 280.1515
1469.7787 | 1570.7787 | 331.2289 | 280.0717
1470.7801 | 1571.7801 | 331.2461 | 279.5926
1471.7815 | 1572.7815 | 331.207 | 279.3334
1472.783 | 1573.783 | 331.2341 | 279.3951
1473.7844 | 1574.7844 | 331.256 | 279.188
1474.7759 | 1575.7759 | 331.2626 | 279.0532
1475.7873 | 1576.7873 | 331.2462 | 278.9595
1476.7787 | 1577.7787 | 331.1979 | 278.2207
1477.7802 | 1578.7802 | 331.155 | 278.5171
1478.7816 | 1579.7816 | 331.1857 | 278.7783
1479.7831 | 1580.7831 | 331.2369 | 278.8301
1480.7845 | 1581.7845 | 331.277 | 278.3812
1481.7859 | 1582.7859 | 331.2818 | 278.5897
1482.7774 | 1583.7774 | 331.2355 | 278.3799
1483.7788 | 1584.7788 | 331.2268 | 278.0861
1484.7802 | 1585.7802 | 331.1888 | 278.2815
1485.7817 | 1586.7817 | 331.1353 | 278.6158
1486.7831 | 1587.7831 | 331.1083 | 277.8369
1487.7846 | 1588.7846 | 331.1166 | 277.9074
1488.776 | 1589.776 | 331.1679 | 278.0207
1489.7774 | 1590.7774 | 330.9843 | 277.9641
1490.7789 | 1591.7789 | 330.9349 | 278.4108
1491.7803 | 1592.7803 | 330.9205 | 278.8975
1492.7817 | 1593.7817 | 330.9211 | 278.5496
1493.7832 | 1594.7832 | 330.8734 | 279.0506
1494.7846 | 1595.7846 | 330.7903 | 279.0933
1495.7861 | 1596.7861 | 330.7227 | 279.4444
1496.7775 | 1597.7775 | 330.7709 | 279.1349
1497.7789 | 1598.7789 | 330.8084 | 279.3626
1498.7804 | 1599.7804 | 330.8086 | 278.6078
1499.7818 | 1600.7818 | 330.8305 | 278.4189
1500.7732 | 1601.7732 | 330.8535 | 278.1128
1501.7847 | 1602.7847 | 330.7486 | 277.7721
1502.7761 | 1603.7761 | 330.7097 | 278.0169
1503.7776 | 1604.7776 | 330.7171 | 278.4339
1504.779 | 1605.779 | 330.7496 | 278.0441
1505.7804 | 1606.7804 | 330.7395 | 278.562
1506.7819 | 1607.7819 | 330.7133 | 278.9131
1507.7833 | 1608.7833 | 330.6961 | 279.1949
1508.7747 | 1609.7747 | 330.7332 | 279.2396
1509.7862 | 1610.7862 | 330.7149 | 279.3479
1510.7776 | 1611.7776 | 330.6637 | 279.7225
1511.7791 | 1612.7791 | 330.6091 | 279.1758
1512.7805 | 1613.7805 | 330.6227 | 279.1333
1513.7819 | 1614.7819 | 330.678 | 279.6639
1514.7834 | 1615.7834 | 330.7549 | 279.9539
1515.7848 | 1616.7848 | 330.7605 | 279.4859
1516.7762 | 1617.7762 | 330.7177 | 279.5936
1517.7877 | 1618.7877 | 330.6691 | 280.0781
1518.7791 | 1619.7791 | 330.7247 | 279.973
1519.7806 | 1620.7806 | 330.7933 | 279.7559
1520.782 | 1621.782 | 330.8316 | 279.8135
1521.7834 | 1622.7834 | 330.8618 | 280.0365
1522.7749 | 1623.7749 | 330.859 | 280.2083
1523.7863 | 1624.7863 | 330.9359 | 280.2146
1524.7778 | 1625.7778 | 331.0075 | 280.3987
1525.7792 | 1626.7792 | 331.0599 | 280.7281
1526.7806 | 1627.7806 | 331.0915 | 280.7073
1527.7821 | 1628.7821 | 331.091 | 280.6518
1528.7835 | 1629.7835 | 331.2129 | 280.6672
1529.785 | 1630.785 | 331.3234 | 280.9009
1530.7764 | 1631.7764 | 331.3427 | 280.7584
1531.7878 | 1632.7878 | 331.3699 | 280.8432
1532.7793 | 1633.7793 | 331.2989 | 280.4594
1533.7807 | 1634.7807 | 331.1926 | 280.4088
1534.7821 | 1635.7821 | 331.2149 | 279.9149
1535.7836 | 1636.7836 | 331.3489 | 280.2989
1536.775 | 1637.775 | 331.4478 | 280.5821
1537.7865 | 1638.7865 | 331.4307 | 280.5846
1538.7779 | 1639.7779 | 331.3844 | 280.8531
1539.7793 | 1640.7793 | 331.372 | 280.6206
1540.7808 | 1641.7808 | 331.2651 | 280.174
1541.7822 | 1642.7822 | 331.1452 | 280.1637
1542.7836 | 1643.7836 | 331.0671 | 280.2476
1543.7851 | 1644.7851 | 331.0131 | 280.1043
1544.7765 | 1645.7765 | 330.9563 | 280.304
1545.798 | 1646.798 | 330.8695 | 280.7042
1546.7794 | 1647.7794 | 330.795 | 280.7849
1547.7808 | 1648.7808 | 330.778 | 280.5218
1548.7823 | 1649.7823 | 330.753 | 279.8451
1549.7837 | 1650.7837 | 330.7419 | 279.7968
1550.7751 | 1651.7751 | 330.7408 | 279.7075
1551.7866 | 1652.7866 | 330.6758 | 280.1487
1552.778 | 1653.778 | 330.7261 | 280.1523
1553.7795 | 1654.7795 | 330.7775 | 279.7849
1554.7809 | 1655.7809 | 330.8023 | 279.3772
1555.7823 | 1656.7823 | 330.8887 | 278.9505
1556.7738 | 1657.7738 | 330.9661 | 279.0115
1557.7852 | 1658.7852 | 331.0942 | 279.2313
1558.7766 | 1659.7766 | 331.0966 | 279.4181
1559.7881 | 1660.7881 | 331.0277 | 278.5038
1560.7795 | 1661.7795 | 331.0545 | 278.547
1561.781 | 1662.781 | 331.0595 | 278.9709
1562.7824 | 1663.7824 | 331.1096 | 279.2898
1563.7838 | 1664.7838 | 331.1428 | 279.2903
1564.7753 | 1665.7753 | 331.2358 | 278.7435
1565.7867 | 1666.7867 | 331.3435 | 278.9093
1566.7781 | 1667.7781 | 331.381 | 278.8822
1567.7796 | 1668.7796 | 331.509 | 279.1693
1568.781 | 1669.781 | 331.4874 | 279.4222
1569.7825 | 1670.7825 | 331.4597 | 279.2729
1570.7839 | 1671.7839 | 331.4713 | 279.8396
1571.7853 | 1672.7853 | 331.5866 | 280.178
1572.7768 | 1673.7768 | 331.6801 | 280.2054
1573.7782 | 1674.7782 | 331.6902 | 280.635
1574.7797 | 1675.7797 | 331.7358 | 280.9829
1575.7811 | 1676.7811 | 331.8148 | 280.9661
1576.7825 | 1677.7825 | 331.8167 | 281.1594
1577.784 | 1678.784 | 331.8719 | 280.4522
1578.7754 | 1679.7754 | 331.9465 | 280.2975
1579.7768 | 1680.7768 | 332.0366 | 280.6411
1580.7783 | 1681.7783 | 332.1655 | 280.8071
1581.7797 | 1682.7797 | 332.1949 | 281.0727
1582.7812 | 1683.7812 | 332.1486 | 281.238
1583.7826 | 1684.7826 | 332.0695 | 281.2614
1584.784 | 1685.784 | 332.0635 | 281.5899
1585.7755 | 1686.7755 | 332.1477 | 281.7138
1586.7769 | 1687.7769 | 332.2411 | 281.4643
1587.7783 | 1688.7783 | 332.2152 | 281.219
1588.7798 | 1689.7798 | 332.2849 | 281.2776
1589.7812 | 1690.7812 | 332.3269 | 281.4395
1590.7827 | 1691.7827 | 332.3315 | 281.6039
1591.7741 | 1692.7741 | 332.2895 | 281.466
1592.7755 | 1693.7755 | 332.3125 | 281.7471
1593.777 | 1694.777 | 332.2923 | 281.6474
1594.7784 | 1695.7784 | 332.2544 | 280.9258
1595.7798 | 1696.7798 | 332.2469 | 280.4494
1596.7813 | 1697.7813 | 332.2178 | 280.3899
1597.7827 | 1698.7827 | 332.1459 | 280.7707
1598.7842 | 1699.7842 | 332.0187 | 280.8999
1599.7756 | 1700.7756 | 332.0323 | 281.2146
1600.777 | 1701.777 | 331.9501 | 280.6561
1601.7785 | 1702.7785 | 331.8825 | 280.3942
1602.7799 | 1703.7799 | 331.9152 | 280.6574
1603.7814 | 1704.7814 | 331.9419 | 280.0666
1604.7828 | 1705.7828 | 331.9549 | 279.1245
1605.7742 | 1706.7742 | 331.9669 | 279.1639
1606.7757 | 1707.7757 | 331.9337 | 279.3503
1607.7771 | 1708.7771 | 331.9502 | 279.8843
1608.7785 | 1709.7785 | 331.9509 | 279.5018
1609.78 | 1710.78 | 331.8192 | 279.06
1610.8014 | 1711.8014 | 331.6896 | 278.697
1611.7829 | 1712.7829 | 331.5228 | 278.9212
1612.7743 | 1713.7743 | 331.4109 | 279.0625
1613.7757 | 1714.7757 | 331.3229 | 279.3496
1614.7772 | 1715.7772 | 331.2996 | 278.8502
1615.7786 | 1716.7786 | 331.2839 | 278.9687
1616.78 | 1717.78 | 331.2529 | 279.4894
1617.7815 | 1718.7815 | 331.1867 | 279.2541
1618.7829 | 1719.7829 | 331.2185 | 279.5565
1619.7844 | 1720.7844 | 331.1488 | 279.6517
1620.7758 | 1721.7758 | 331.1073 | 278.6479
1621.7772 | 1722.7772 | 331.1736 | 278.9984
1622.7787 | 1723.7787 | 331.1639 | 279.4756
1623.7801 | 1724.7801 | 331.0965 | 279.8364
1624.7816 | 1725.7816 | 330.9768 | 279.8982
1625.783 | 1726.783 | 330.9897 | 279.2465
1626.7844 | 1727.7844 | 330.952 | 279.3843
1627.7759 | 1728.7759 | 330.9091 | 279.5747
1628.7773 | 1729.7773 | 330.897 | 279.3345
1629.7787 | 1730.7787 | 330.9444 | 278.627
1630.7802 | 1731.7802 | 331.0206 | 278.8057
1631.7816 | 1732.7816 | 330.9552 | 279.3161
1632.773 | 1733.773 | 330.929 | 279.1551
1633.7745 | 1734.7745 | 330.9267 | 279.5818
1634.7759 | 1735.7759 | 330.878 | 279.9148
1635.7774 | 1736.7774 | 330.7647 | 279.8493
1636.7788 | 1737.7788 | 330.6911 | 280.2346
1637.7802 | 1738.7802 | 330.6655 | 280.3762
1638.7817 | 1739.7817 | 330.6683 | 280.529
1639.7831 | 1740.7831 | 330.6509 | 280.344
1640.7745 | 1741.7745 | 330.6279 | 279.5112
1641.776 | 1742.776 | 330.6337 | 279.0928
1642.7774 | 1743.7774 | 330.6442 | 279.5051
1643.7789 | 1744.7789 | 330.6409 | 279.6889
1644.7803 | 1745.7803 | 330.6656 | 280.1536
1645.7817 | 1746.7817 | 330.7294 | 280.2108
1646.7832 | 1747.7832 | 330.7875 | 280.2854
1647.7846 | 1748.7846 | 330.7706 | 280.5212
1648.7761 | 1749.7761 | 330.8323 | 280.8135
1649.7775 | 1750.7775 | 330.9382 | 280.8899
1650.7789 | 1751.7789 | 331.0237 | 280.9819
1651.7804 | 1752.7804 | 331.0839 | 280.356
1652.7818 | 1753.7818 | 331.0425 | 279.7961
1653.7732 | 1754.7732 | 331.0258 | 279.802
1654.7747 | 1755.7747 | 331.103 | 280.1243
1655.7761 | 1756.7761 | 331.1395 | 280.3117
1656.7776 | 1757.7776 | 331.1816 | 279.6485
1657.779 | 1758.779 | 331.2851 | 279.9825
1658.7804 | 1759.7804 | 331.3528 | 280.4169
1659.7819 | 1760.7819 | 331.4418 | 280.6233
1660.7833 | 1761.7833 | 331.5087 | 280.1455
1661.7747 | 1762.7747 | 331.4991 | 280.4184
1662.7762 | 1763.7762 | 331.5816 | 279.8659
1663.7776 | 1764.7776 | 331.6628 | 279.7599
1664.7791 | 1765.7791 | 331.7728 | 279.4584
1665.7805 | 1766.7805 | 331.84 | 279.8359
1666.7819 | 1767.7819 | 331.8734 | 280.3939
1667.7834 | 1768.7834 | 331.8724 | 280.4825
1668.7748 | 1769.7748 | 331.8666 | 280.3717
1669.7763 | 1770.7763 | 331.7914 | 280.8049
1670.7777 | 1771.7777 | 331.7721 | 281.108
1671.7791 | 1772.7791 | 331.8166 | 280.9597
1672.7806 | 1773.7806 | 331.87 | 280.9949
1673.782 | 1774.782 | 331.872 | 281.0964
1674.7734 | 1775.7734 | 331.8683 | 280.5826
1675.7749 | 1776.7749 | 331.8462 | 280.5474
1676.7763 | 1777.7763 | 331.8169 | 280.2856
1677.7778 | 1778.7778 | 331.7906 | 280.2606
1678.7792 | 1779.7792 | 331.8232 | 280.1339
1679.7806 | 1780.7806 | 331.718 | 279.6716
1680.7821 | 1781.7821 | 331.5527 | 278.9622
1681.7835 | 1782.7835 | 331.2758 | 278.7373
1682.7749 | 1783.7749 | 331.1512 | 279.0155
1683.7764 | 1784.7764 | 331.1563 | 279.2978
1684.7778 | 1785.7778 | 331.166 | 279.728
1685.7793 | 1786.7793 | 331.2057 | 279.6148
1686.7807 | 1787.7807 | 331.2726 | 279.9062
1687.7821 | 1788.7821 | 331.2761 | 280.1748
1688.7836 | 1789.7836 | 331.1659 | 280.4729
1689.775 | 1790.775 | 331.1243 | 280.3706
1690.7764 | 1791.7764 | 331.1616 | 280.1584
1691.7779 | 1792.7779 | 331.0733 | 280.3043
1692.7793 | 1793.7793 | 331.0614 | 279.9825
1693.7808 | 1794.7808 | 331.0453 | 280.0089
1694.7822 | 1795.7822 | 331.1127 | 280.1317
1695.7736 | 1796.7736 | 331.1854 | 280.3895
1696.7751 | 1797.7751 | 331.2224 | 280.1816
1697.7765 | 1798.7765 | 331.2045 | 280.6039
1698.778 | 1799.778 | 331.1753 | 280.9047
1699.7794 | 1800.7794 | 331.1396 | 281.1138
1700.7808 | 1801.7808 | 331.1468 | 281.2962
1701.7823 | 1802.7823 | 331.0978 | 281.4376
1702.7837 | 1803.7837 | 331.0764 | 280.9356
1703.7751 | 1804.7751 | 331.0488 | 280.7365
1704.7766 | 1805.7766 | 331.0778 | 280.5864
1705.778 | 1806.778 | 331.099 | 279.9352
1706.7795 | 1807.7795 | 331.0801 | 279.6977
1707.7809 | 1808.7809 | 331.0747 | 280.1723
1708.7823 | 1809.7823 | 331.1112 | 280.613
1709.7738 | 1810.7738 | 331.1974 | 280.6402
1710.7752 | 1811.7752 | 331.2929 | 280.6657
1711.7766 | 1812.7766 | 331.4093 | 280.809
1712.7781 | 1813.7781 | 331.521 | 280.5228
1713.7795 | 1814.7795 | 331.6958 | 279.8837
1714.781 | 1815.781 | 331.7659 | 280.1236
1715.7824 | 1816.7824 | 331.8393 | 280.0635
1716.7738 | 1817.7738 | 331.8176 | 280.1759
1717.7753 | 1818.7753 | 331.7825 | 279.8952
1718.7767 | 1819.7767 | 331.6968 | 280.2258
1719.7782 | 1820.7782 | 331.7011 | 280.5144
1720.7796 | 1821.7796 | 331.7983 | 280.1855
1721.781 | 1822.781 | 331.819 | 280.3943
1722.7825 | 1823.7825 | 331.897 | 280.4031
1723.7839 | 1824.7839 | 331.8709 | 279.9857
1724.7753 | 1825.7753 | 331.8319 | 280.2864
1725.7768 | 1826.7768 | 331.8287 | 280.6909
1726.7982 | 1827.7982 | 331.8176 | 280.7917
1727.7797 | 1828.7797 | 331.7651 | 281.1313
1728.7811 | 1829.7811 | 331.8181 | 281.0623
1729.7825 | 1830.7825 | 331.9113 | 280.9793
1730.8841 | 1831.8841 | 331.878 | 281.0473
1731.7754 | 1832.7754 | 331.8355 | 280.1759
1732.7768 | 1833.7768 | 331.8524 | 280.4367
1733.7783 | 1834.7783 | 331.9094 | 280.817
1734.7797 | 1835.7797 | 331.9 | 281.1659
1735.7812 | 1836.7812 | 331.8285 | 281.1106
1736.7826 | 1837.7826 | 331.9127 | 280.9134
1737.784 | 1838.784 | 331.9047 | 280.4273
1738.7755 | 1839.7755 | 331.8685 | 280.4064
1739.7769 | 1840.7769 | 331.8978 | 280.1893
1740.7783 | 1841.7783 | 331.8683 | 280.6359
1741.7798 | 1842.7798 | 331.7562 | 280.7572
1742.7812 | 1843.7812 | 331.6271 | 280.4362
1743.7827 | 1844.7827 | 331.5 | 280.8354
1744.7841 | 1845.7841 | 331.4593 | 280.8519
1745.7755 | 1846.7755 | 331.4956 | 280.3621
1746.777 | 1847.777 | 331.5109 | 279.9805
1747.7784 | 1848.7784 | 331.5566 | 279.7947
1748.7799 | 1849.7799 | 331.5037 | 279.6177
1749.7813 | 1850.7813 | 331.4314 | 279.3992
1750.7827 | 1851.7827 | 331.286 | 279.0219
1751.7742 | 1852.7742 | 331.2926 | 279.3361
1752.7756 | 1853.7756 | 331.3811 | 279.8496
1753.777 | 1854.777 | 331.3363 | 280.1484
1754.7785 | 1855.7785 | 331.3474 | 280.373
1755.7799 | 1856.7799 | 331.4292 | 280.4944
1756.7814 | 1857.7814 | 331.394 | 280.6361
1757.7828 | 1858.7828 | 331.3962 | 280.7006
1758.7842 | 1859.7842 | 331.3878 | 280.7029
1759.7757 | 1860.7757 | 331.3775 | 280.8244
1760.7771 | 1861.7771 | 331.3844 | 280.5075
1761.7785 | 1862.7785 | 331.3888 | 280.6276
1762.78 | 1863.78 | 331.3951 | 279.9928
1763.7814 | 1864.7814 | 331.3796 | 280.2755
1764.7829 | 1865.7829 | 331.3983 | 280.1479
1765.7743 | 1866.7743 | 331.3512 | 280.1538
1766.7757 | 1867.7757 | 331.3196 | 279.9697
1767.7772 | 1868.7772 | 331.3111 | 279.6814
1768.7786 | 1869.7786 | 331.2937 | 279.9059
1769.78 | 1870.78 | 331.311 | 279.8055
1770.7815 | 1871.7815 | 331.3304 | 280.3504
1771.7829 | 1872.7829 | 331.2651 | 280.455
1772.7744 | 1873.7744 | 331.214 | 279.9472
1773.7758 | 1874.7758 | 331.1197 | 279.9082
1774.7772 | 1875.7772 | 331.0528 | 279.7058
1775.7787 | 1876.7787 | 331.0669 | 279.8042
1776.7801 | 1877.7801 | 331.0499 | 279.7141
1777.7816 | 1878.7816 | 331.01 | 280.1177
1778.783 | 1879.783 | 331.0705 | 280.354
1779.7844 | 1880.7844 | 331.1129 | 280.2012
1780.7759 | 1881.7759 | 331.2436 | 279.7474
1781.7773 | 1882.7773 | 331.273 | 279.9641
1782.7787 | 1883.7787 | 331.2903 | 279.8539
1783.7802 | 1884.7802 | 331.2974 | 279.7998
1784.7816 | 1885.7816 | 331.3441 | 280.2136
1785.7831 | 1886.7831 | 331.4105 | 280.5989
1786.7745 | 1887.7745 | 331.4775 | 280.4695
1787.7759 | 1888.7759 | 331.5748 | 280.7167
1788.7774 | 1889.7774 | 331.5745 | 279.7955
1789.7788 | 1890.7788 | 331.6005 | 279.5957
1790.7802 | 1891.7802 | 331.6732 | 279.4612
1791.7817 | 1892.7817 | 331.6881 | 279.1894
1792.7831 | 1893.7831 | 331.6521 | 279.5593
1793.7746 | 1894.7746 | 331.7325 | 280.0048
1794.776 | 1895.776 | 331.705 | 280.2929
1795.7774 | 1896.7774 | 331.6224 | 280.7508
1796.7789 | 1897.7789 | 331.603 | 280.9414
1797.7803 | 1898.7803 | 331.5847 | 281.1929
1798.7818 | 1899.7818 | 331.58 | 281.5481
1799.7832 | 1900.7832 | 331.3815 | 281.7979
1800.7746 | 1901.7746 | 331.2498 | 281.8382
1801.7761 | 1902.7761 | 331.2097 | 282.1065
1802.7775 | 1903.7775 | 331.1755 | 282.1461
1803.7789 | 1904.7789 | 331.2144 | 281.9097
1804.7804 | 1905.7804 | 331.104 | 282.0007
1805.7818 | 1906.7818 | 330.9439 | 281.7955
1806.7833 | 1907.7833 | 330.9238 | 282.0108
1807.7747 | 1908.7747 | 330.8742 | 282.038
1808.7761 | 1909.7761 | 330.7827 | 282.2835
1809.7776 | 1910.7776 | 330.6259 | 282.268
1810.779 | 1911.779 | 330.5131 | 282.1608
1811.7804 | 1912.7804 | 330.4781 | 281.8078
1812.7819 | 1913.7819 | 330.4585 | 281.8415
1813.7833 | 1914.7833 | 330.4603 | 281.8049
1814.7747 | 1915.7747 | 330.4903 | 281.8576
1815.7762 | 1916.7762 | 330.5434 | 282.0099
1816.7776 | 1917.7776 | 330.5331 | 281.5844
1817.7791 | 1918.7791 | 330.5066 | 281.4041
1818.7805 | 1919.7805 | 330.4661 | 280.7214
1819.7819 | 1920.7819 | 330.4303 | 280.5533
1820.7834 | 1921.7834 | 330.4538 | 280.7704
1821.7748 | 1922.7748 | 330.4967 | 280.8735
1822.7763 | 1923.7763 | 330.5268 | 281.0533
1823.7777 | 1924.7777 | 330.547 | 281.312
1824.7791 | 1925.7791 | 330.4792 | 281.0684
1825.7806 | 1926.7806 | 330.4143 | 281.0294
1826.782 | 1927.782 | 330.4578 | 281.188
1827.7835 | 1928.7835 | 330.5755 | 281.2721
1828.7749 | 1929.7749 | 330.6828 | 281.4179
1829.7763 | 1930.7763 | 330.7353 | 281.4678
1830.7778 | 1931.7778 | 330.7126 | 281.4525
1831.7792 | 1932.7792 | 330.6512 | 281.5323
1832.7806 | 1933.7806 | 330.7903 | 281.4986
1833.7821 | 1934.7821 | 330.9556 | 281.7469
1834.7835 | 1935.7835 | 330.9487 | 282.0437
1835.7749 | 1936.7749 | 330.9562 | 281.8223
1836.7764 | 1937.7764 | 330.981 | 281.787
1837.7778 | 1938.7778 | 331.023 | 281.6194
1838.7793 | 1939.7793 | 331.0681 | 281.0651
1839.7807 | 1940.7807 | 331.1148 | 281.3867
1840.7821 | 1941.7821 | 331.1596 | 281.6643
1841.7736 | 1942.7736 | 331.1759 | 281.725
1842.775 | 1943.775 | 331.2082 | 281.6046
1843.7765 | 1944.7765 | 331.21 | 281.0837
1844.7779 | 1945.7779 | 331.2319 | 281.1648
1845.7793 | 1946.7793 | 331.2957 | 281.3636
1846.7808 | 1947.7808 | 331.2922 | 281.4899
1847.7822 | 1948.7822 | 331.3079 | 281.5855
1848.7837 | 1949.7837 | 331.2693 | 281.6999
1849.7751 | 1950.7751 | 331.211 | 281.8241
1850.7765 | 1951.7765 | 331.2802 | 282.0479
1851.778 | 1952.778 | 331.2732 | 282.1522
1852.7794 | 1953.7794 | 331.1899 | 281.1461
1853.7808 | 1954.7808 | 331.1113 | 280.7154
1854.7823 | 1955.7823 | 331.0118 | 280.4196
1855.7837 | 1956.7837 | 330.9869 | 280.7988
1856.7751 | 1957.7751 | 331.011 | 281.2548
1857.7766 | 1958.7766 | 331.0267 | 281.4558
1858.778 | 1959.778 | 331.0048 | 281.4095
1859.7795 | 1960.7795 | 330.9994 | 281.3412
1860.7809 | 1961.7809 | 330.8981 | 281.5924
1861.7823 | 1962.7823 | 330.8582 | 281.7651
1862.7738 | 1963.7738 | 330.8374 | 282.1407
1863.7752 | 1964.7752 | 330.8526 | 282.228
1864.7766 | 1965.7766 | 330.8438 | 281.8088
1865.7781 | 1966.7781 | 330.7857 | 282.1996
1866.7795 | 1967.7795 | 330.786 | 282.3093
1867.781 | 1968.781 | 330.9021 | 282.2656
1868.7824 | 1969.7824 | 330.965 | 281.6905
1869.7838 | 1970.7838 | 330.9604 | 281.8144
1870.7753 | 1971.7753 | 330.9521 | 282.0679
1871.7767 | 1972.7767 | 330.8718 | 282.0597
1872.7782 | 1973.7782 | 330.813 | 282.1448
1873.7796 | 1974.7796 | 330.6884 | 281.6257
1874.781 | 1975.781 | 330.5783 | 281.5263
1875.7825 | 1976.7825 | 330.4162 | 280.1872
1876.7839 | 1977.7839 | 330.1706 | 279.9912
1877.7753 | 1978.7753 | 329.9128 | 280.4594
1878.7768 | 1979.7768 | 329.6058 | 280.4788
1879.7782 | 1980.7782 | 329.3825 | 280.6804
1880.7797 | 1981.7797 | 329.016 | 280.4873
1881.7811 | 1982.7811 | 328.7042 | 280.5752
1882.7825 | 1983.7825 | 328.4251 | 280.7097
1883.774 | 1984.774 | 328.0181 | 280.7992
1884.7754 | 1985.7754 | 327.6486 | 280.3533
1885.7768 | 1986.7768 | 327.3239 | 279.5821
1886.7783 | 1987.7783 | 327.0005 | 279.7977
1887.7797 | 1988.7797 | 326.6774 | 280.1755
1888.7812 | 1989.7812 | 326.3351 | 280.0316
1889.7826 | 1990.7826 | 326.0138 | 280.1907
1890.774 | 1991.774 | 325.6995 | 280.0799
1891.7755 | 1992.7755 | 325.1973 | 278.9208
1892.7769 | 1993.7769 | 324.7634 | 278.6563
1893.7784 | 1994.7784 | 324.5015 | 278.9928
1894.7798 | 1995.7798 | 324.1248 | 279.055
1895.7812 | 1996.7812 | 323.76 | 279.245
1896.7827 | 1997.7827 | 323.3634 | 279.4652
1897.7841 | 1998.7841 | 322.9097 | 279.3151
1898.7755 | 1999.7755 | 322.4568 | 279.1466
1899.777 | 2000.777 | 322.0174 | 278.1077
1900.7784 | 2001.7784 | 321.5609 | 277.4869
1901.7799 | 2002.7799 | 321.1512 | 277.899
1902.7813 | 2003.7813 | 320.7407 | 277.8422
1903.7827 | 2004.7827 | 320.3281 | 277.8
1904.7842 | 2005.7842 | 319.8792 | 278.1528
1905.7756 | 2006.7756 | 319.4552 | 278.2909
1906.7971 | 2007.7971 | 319.0221 | 278.1934
1907.7785 | 2008.7785 | 318.5961 | 278.2536
1908.7799 | 2009.7799 | 318.2229 | 278.2314
1909.7814 | 2010.7814 | 317.7597 | 278.0665
1910.7828 | 2011.7828 | 317.2772 | 278.0177
1911.7742 | 2012.7742 | 316.8808 | 277.4799
1912.7757 | 2013.7757 | 316.3977 | 277.3185
1913.7771 | 2014.7771 | 315.9437 | 277.3588
1914.7785 | 2015.7785 | 315.4502 | 277.3794
1915.78 | 2016.78 | 314.9963 | 277.2665
1916.7814 | 2017.7814 | 314.5882 | 277.1245
1917.7829 | 2018.7829 | 314.1772 | 277.1014
1918.7743 | 2019.7743 | 313.729 | 276.9925
1919.7757 | 2020.7757 | 313.1303 | 276.7811
1920.7772 | 2021.7772 | 312.6867 | 276.8097
1921.7786 | 2022.7786 | 312.299 | 276.5513
1922.7801 | 2023.7801 | 311.836 | 275.5684
1923.7815 | 2024.7815 | 311.3738 | 275.428
1924.7829 | 2025.7829 | 310.9133 | 274.814
1925.7744 | 2026.7744 | 310.4959 | 274.224
1926.7758 | 2027.7758 | 310.1246 | 273.6588
1927.7772 | 2028.7772 | 309.735 | 274.0558
1928.7787 | 2029.7787 | 309.3638 | 274.3263
1929.7801 | 2030.7801 | 308.9365 | 274.3027
1930.7816 | 2031.7816 | 308.5921 | 273.9826
1931.783 | 2032.783 | 308.1904 | 272.9099
1932.7844 | 2033.7844 | 307.6769 | 272.5747
1933.7759 | 2034.7759 | 307.2199 | 272.3647
1934.7773 | 2035.7773 | 306.7593 | 272.457
1935.7787 | 2036.7787 | 306.3931 | 272.6371
1936.7802 | 2037.7802 | 305.9929 | 272.2889
1937.7816 | 2038.7816 | 305.6145 | 272.3096
1938.7831 | 2039.7831 | 305.2494 | 271.9959
1939.7745 | 2040.7745 | 304.8787 | 271.8613
1940.7759 | 2041.7759 | 304.4568 | 270.8876
1941.7774 | 2042.7774 | 303.9847 | 270.6019
1942.7788 | 2043.7788 | 303.5326 | 270.7888
1943.7802 | 2044.7802 | 302.9933 | 270.8272
1944.7817 | 2045.7817 | 302.5307 | 270.817
1945.7831 | 2046.7831 | 302.1332 | 270.6891
1946.7746 | 2047.7746 | 301.6938 | 270.6136
1947.776 | 2048.776 | 301.206 | 270.5154
1948.7774 | 2049.7774 | 300.7185 | 269.7214
1949.7789 | 2050.7789 | 300.2817 | 269.2701
1950.7803 | 2051.7803 | 299.8421 | 269.0596
1951.7818 | 2052.7818 | 299.4297 | 268.9348
1952.7832 | 2053.7832 | 299.0169 | 268.8762
1953.7846 | 2054.7846 | 298.6335 | 268.5015
1954.7761 | 2055.7761 | 298.2068 | 268.5503
1955.7775 | 2056.7775 | 297.8113 | 268.5346
1956.7789 | 2057.7789 | 297.4705 | 268.2036
1957.7804 | 2058.7804 | 297.0634 | 267.6011
1958.7818 | 2059.7818 | 296.6746 | 266.7623
1959.7833 | 2060.7833 | 296.2648 | 266.9622
1960.7747 | 2061.7747 | 295.834 | 266.7293
1961.7761 | 2062.7761 | 295.5001 | 266.0448
1962.7776 | 2063.7776 | 295.0984 | 265.6742
1963.779 | 2064.779 | 294.705 | 265.0298
1964.7804 | 2065.7804 | 294.2409 | 265.1414
1965.7819 | 2066.7819 | 293.7844 | 265.0014
1966.7833 | 2067.7833 | 293.2717 | 264.4477
1967.7748 | 2068.7748 | 292.8383 | 264.6547
1968.7762 | 2069.7762 | 292.4443 | 264.262
1969.7776 | 2070.7776 | 292.0665 | 263.9665
1970.7791 | 2071.7791 | 291.614 | 263.7833
1971.7805 | 2072.7805 | 291.122 | 263.8289
1972.782 | 2073.782 | 290.7354 | 263.745
1973.7834 | 2074.7834 | 290.3434 | 263.6792
1974.7748 | 2075.7748 | 289.93 | 263.6717
1975.7763 | 2076.7763 | 289.5633 | 263.4924
1976.7777 | 2077.7777 | 289.2038 | 262.7611
1977.7791 | 2078.7791 | 288.8044 | 262.2531
1978.7806 | 2079.7806 | 288.3972 | 261.6973
1979.782 | 2080.782 | 287.8691 | 261.3534
1980.7835 | 2081.7835 | 287.4015 | 261.059
1981.7749 | 2082.7749 | 286.9989 | 261.2329
1982.7763 | 2083.7763 | 286.5686 | 260.9791
1983.7778 | 2084.7778 | 286.219 | 261.0425
1984.7792 | 2085.7792 | 285.8998 | 261.1675
1985.7806 | 2086.7806 | 285.5352 | 261.1456
1986.7821 | 2087.7821 | 285.1347 | 260.6787
1987.7835 | 2088.7835 | 284.7193 | 260.7657
1988.7749 | 2089.7749 | 284.3433 | 260.603
1989.7764 | 2090.7764 | 283.9463 | 260.0184
1990.7778 | 2091.7778 | 283.5472 | 260.0751
1991.7793 | 2092.7793 | 283.1426 | 259.8565
1992.7807 | 2093.7807 | 282.7956 | 259.1138
1993.7821 | 2094.7821 | 282.4876 | 259.1508
1994.7836 | 2095.7836 | 282.157 | 259.2916
1995.775 | 2096.775 | 281.7516 | 259.183
1996.7765 | 2097.7765 | 281.3091 | 259.0686
1997.7779 | 2098.7779 | 280.8865 | 258.6604
1998.7793 | 2099.7793 | 280.4996 | 258.3125
1999.7808 | 2100.7808 | 280.0829 | 258.3441
2000.7822 | 2101.7822 | 279.636 | 258.2871
2001.7837 | 2102.7837 | 279.2298 | 258.0887
2002.7751 | 2103.7751 | 278.853 | 257.9351
2003.7765 | 2104.7765 | 278.5393 | 257.6119
2004.778 | 2105.778 | 278.1779 | 257.1175
2005.7794 | 2106.7794 | 277.7146 | 256.2628
2006.7808 | 2107.7808 | 277.3105 | 255.0633
2007.7823 | 2108.7823 | 276.8908 | 255.3217
2008.7837 | 2109.7837 | 276.4802 | 255.4722
2009.7751 | 2110.7751 | 276.0629 | 254.7821
2010.7766 | 2111.7766 | 275.6557 | 254.5772
2011.778 | 2112.778 | 275.293 | 253.9103
2012.7795 | 2113.7795 | 274.9223 | 253.9799
2013.7809 | 2114.7809 | 274.4875 | 253.8737
2014.7823 | 2115.7823 | 274.0273 | 252.8188
2015.7738 | 2116.7738 | 273.6043 | 252.9744
2016.7752 | 2117.7752 | 273.1721 | 252.7552
2017.7767 | 2118.7767 | 272.7638 | 252.0919
2018.7781 | 2119.7781 | 272.4399 | 251.6071
2019.7795 | 2120.7795 | 272.0574 | 251.9246
2020.781 | 2121.781 | 271.7015 | 252.101
2021.7824 | 2122.7824 | 271.3256 | 252.1732
2022.7839 | 2123.7839 | 270.9475 | 252.2599
2023.7753 | 2124.7753 | 270.562 | 252.2994
2024.7767 | 2125.7767 | 270.1926 | 252.1111
2025.7782 | 2126.7782 | 269.8362 | 252.0103
2026.7796 | 2127.7796 | 269.4811 | 251.9043
2027.781 | 2128.781 | 269.1568 | 251.8933
2028.7825 | 2129.7825 | 268.8021 | 251.7698
2029.7839 | 2130.7839 | 268.4344 | 251.5475
2030.7753 | 2131.7753 | 268.0775 | 251.2278
2031.7768 | 2132.7768 | 267.7059 | 251.0272
2032.7782 | 2133.7782 | 267.3199 | 250.6217
2033.7797 | 2134.7797 | 266.9034 | 250.6092
2034.7811 | 2135.7811 | 266.5841 | 249.7117
2035.7825 | 2136.7825 | 266.281 | 249.668
2036.774 | 2137.774 | 265.9337 | 249.5051
2037.7754 | 2138.7754 | 265.578 | 249.0648
2038.7768 | 2139.7768 | 265.1851 | 249.0732
2039.7783 | 2140.7783 | 264.8046 | 249.1125
2040.7797 | 2141.7797 | 264.5016 | 249.0834
2041.7812 | 2142.7812 | 264.2214 | 248.7191
2042.7826 | 2143.7826 | 263.8856 | 248.7187
2043.774 | 2144.774 | 263.5535 | 248.5957
2044.7755 | 2145.7755 | 263.2398 | 248.3979
2045.7769 | 2146.7769 | 262.9216 | 248.289
2046.7784 | 2147.7784 | 262.5596 | 248.1812
2047.7798 | 2148.7798 | 262.2106 | 248.0221
2048.7812 | 2149.7812 | 261.8651 | 247.848
2049.7827 | 2150.7827 | 261.467 | 247.7281
2050.7841 | 2151.7841 | 261.1162 | 247.6047
2051.7755 | 2152.7755 | 260.7542 | 247.3098
2052.777 | 2153.777 | 260.3757 | 247.1106
2053.7784 | 2154.7784 | 260.0085 | 246.861
2054.7799 | 2155.7799 | 259.6244 | 246.6943
2055.7813 | 2156.7813 | 259.3339 | 246.5326
2056.7827 | 2157.7827 | 258.9867 | 246.0639
2057.7742 | 2158.7742 | 258.6415 | 245.8409
2058.7756 | 2159.7756 | 258.2861 | 245.7714
2059.777 | 2160.777 | 257.8971 | 245.7085
2060.7785 | 2161.7785 | 257.4923 | 245.5362
2061.7799 | 2162.7799 | 257.0686 | 245.2297
2062.7814 | 2163.7814 | 256.6792 | 245.1077
2063.7828 | 2164.7828 | 256.2959 | 245.0071
2064.7742 | 2165.7742 | 255.9034 | 244.8235
2065.7757 | 2166.7757 | 255.5188 | 244.6286
2066.7771 | 2167.7771 | 255.15 | 244.3101
2067.7786 | 2168.7786 | 254.8318 | 243.2653
2068.78 | 2169.78 | 254.4998 | 242.8346
2069.7814 | 2170.7814 | 254.1161 | 241.8962
2070.7829 | 2171.7829 | 253.6457 | 241.8494
2071.7743 | 2172.7743 | 253.2448 | 241.7896
2072.7757 | 2173.7757 | 252.8655 | 241.716
2073.7772 | 2174.7772 | 252.5875 | 241.546
2074.7786 | 2175.7786 | 252.2734 | 241.5638
2075.7801 | 2176.7801 | 251.8849 | 241.3961
2076.7815 | 2177.7815 | 251.4409 | 241.1823
2077.7829 | 2178.7829 | 251.0848 | 241.0678
2078.7744 | 2179.7744 | 250.8128 | 240.882
2079.7758 | 2180.7758 | 250.5461 | 240.6909
2080.7772 | 2181.7772 | 250.2181 | 240.5924
2081.7787 | 2182.7787 | 249.8929 | 240.4454
2082.7801 | 2183.7801 | 249.5801 | 240.1669
2083.7816 | 2184.7816 | 249.2514 | 240.0035
2084.783 | 2185.783 | 248.9184 | 239.9226
2085.7744 | 2186.7744 | 248.6525 | 239.6087
2086.7759 | 2187.7759 | 248.3773 | 239.4764
2087.8875 | 2188.8875 | 248.033 | 239.3212
2088.7787 | 2189.7787 | 247.7726 | 239.0597
2089.7802 | 2190.7802 | 247.4781 | 238.8686
2090.7816 | 2191.7816 | 247.1948 | 238.5124
2091.7831 | 2192.7831 | 246.9266 | 238.4331
2092.7845 | 2193.7845 | 246.5998 | 238.1658
2093.7759 | 2194.7759 | 246.2361 | 237.9146
2094.7774 | 2195.7774 | 245.916 | 237.2823
2095.7788 | 2196.7788 | 245.6591 | 236.8853
2096.7803 | 2197.7803 | 245.3452 | 236.6175
2097.7817 | 2198.7817 | 244.9977 | 236.6529
2098.7831 | 2199.7831 | 244.6482 | 236.6239
2099.7746 | 2200.7746 | 244.3244 | 236.1509
2100.776 | 2201.776 | 243.9857 | 235.8118
2101.7774 | 2202.7774 | 243.6335 | 235.1305
2102.7789 | 2203.7789 | 243.3014 | 235.0285
2103.7803 | 2204.7803 | 242.9927 | 235.0015
2104.7818 | 2205.7818 | 242.7286 | 234.786
2105.7832 | 2206.7832 | 242.4822 | 234.6894
2106.7746 | 2207.7746 | 242.1848 | 234.5963
2107.7761 | 2208.7761 | 241.8712 | 233.9578
2108.7775 | 2209.7775 | 241.5827 | 233.8995
2109.7789 | 2210.7789 | 241.2796 | 233.6106
2110.7804 | 2211.7804 | 241.0512 | 232.9871
2111.7818 | 2212.7818 | 240.7222 | 233.0097
2112.7833 | 2213.7833 | 240.3577 | 232.7695
2113.7747 | 2214.7747 | 239.9115 | 232.5655
2114.7761 | 2215.7761 | 239.5146 | 232.513
2115.7776 | 2216.7776 | 239.1997 | 232.3904
2116.779 | 2217.779 | 238.9216 | 232.3203
2117.7804 | 2218.7804 | 238.624 | 231.8407
2118.7819 | 2219.7819 | 238.3376 | 231.7109
2119.7833 | 2220.7833 | 238.0933 | 231.6026
2120.7748 | 2221.7748 | 237.8339 | 231.506
2121.7762 | 2222.7762 | 237.5508 | 231.361
2122.7776 | 2223.7776 | 237.2637 | 231.2638
2123.7791 | 2224.7791 | 236.9122 | 231.0523
2124.7805 | 2225.7805 | 236.555 | 230.8324
2125.782 | 2226.782 | 236.2303 | 230.7171
2126.7834 | 2227.7834 | 235.9358 | 230.402
2127.7748 | 2228.7748 | 235.6351 | 230.1693
2128.7763 | 2229.7763 | 235.3254 | 230.011
2129.7777 | 2230.7777 | 235.0396 | 229.7659
2130.7791 | 2231.7791 | 234.8004 | 229.6819
2131.7806 | 2232.7806 | 234.525 | 229.5617
2132.782 | 2233.782 | 234.2351 | 229.3133
2133.7835 | 2234.7835 | 233.9839 | 228.9961
2134.7749 | 2235.7749 | 233.7161 | 228.7346
2135.7763 | 2236.7763 | 233.4333 | 228.8478
2136.7778 | 2237.7778 | 233.1272 | 228.52
2137.7792 | 2238.7792 | 232.8137 | 228.2729
2138.7806 | 2239.7806 | 232.5186 | 228.1159
2139.7821 | 2240.7821 | 232.2178 | 227.8413
2140.7735 | 2241.7735 | 231.8908 | 227.6347
2141.775 | 2242.775 | 231.5883 | 227.422
2142.7764 | 2243.7764 | 231.3174 | 227.2896
2143.7778 | 2244.7778 | 231.0412 | 227.1054
2144.7793 | 2245.7793 | 230.7305 | 226.9134
2145.7807 | 2246.7807 | 230.4252 | 226.6481
2146.7822 | 2247.7822 | 230.1224 | 226.5245
2147.7836 | 2248.7836 | 229.8455 | 226.3023
2148.775 | 2249.775 | 229.5938 | 226.1443
2149.7765 | 2250.7765 | 229.3156 | 225.9431
2150.7779 | 2251.7779 | 229.0063 | 225.682
2151.7793 | 2252.7793 | 228.685 | 224.5579
2152.7808 | 2253.7808 | 228.373 | 224.1145
2153.7822 | 2254.7822 | 228.0785 | 224.0423
2154.7837 | 2255.7837 | 227.7891 | 223.9207
2155.7751 | 2256.7751 | 227.5239 | 223.8688
2156.7765 | 2257.7765 | 227.2622 | 223.6884
2157.778 | 2258.778 | 227.0175 | 223.5187
2158.7794 | 2259.7794 | 226.7718 | 223.1544
2159.7808 | 2260.7808 | 226.489 | 222.8393
2160.7823 | 2261.7823 | 226.1854 | 222.7755
2161.7737 | 2262.7737 | 225.8899 | 222.5559
2162.7751 | 2263.7751 | 225.6208 | 222.5
2163.7766 | 2264.7766 | 225.3331 | 222.1496
2164.778 | 2265.778 | 225.0305 | 222.0116

## C6-7
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 158.2039 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38889.4878 | 1 | 0 | 38889.4878 | 1 | 0 | -64.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4883 | 1 | 0 | 38889.4883 | 1 | 0 | -26.5 | 74.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4887 | 1 | 0 | 38889.4887 | 1 | 0 | 10.5 | 111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4891 | 2 | 0 | 38889.4891 | 2 | 0 | 48.5 | 149.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 129469 | 129469 | 129468.9988
38889.4896 | 1 | 0 | 38889.4896 | 1 | 0 | 86.5 | 187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.49 | 1 | 0 | 38889.49 | 1 | 0 | 124.5 | 225.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4904 | 2 | 0 | 38889.4905 | 1 | 0 | 162.5 | 263.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129469 | 259038 | 129468.9988
38889.4909 | 1 | 0 | 38889.4909 | 1 | 0 | 199.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4913 | 1 | 0 | 38889.4913 | 1 | 0 | 237.5 | 338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4917 | 1 | 0 | 38889.4918 | 1 | 0 | 275.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4922 | 1 | 0 | 38889.4922 | 1 | 0 | 313.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4926 | 1 | 0 | 38889.4926 | 1 | 0 | 351 | 452 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4931 | 1 | 0 | 38889.4931 | 1 | 0 | 388.5 | 489.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4935 | 1 | 0 | 38889.4935 | 1 | 0 | 426.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4939 | 1 | 0 | 38889.4939 | 1 | 0 | 464.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4944 | 1 | 0 | 38889.4944 | 1 | 0 | 502.5 | 603.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4948 | 1 | 0 | 38889.4948 | 1 | 0 | 540 | 641 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4952 | 1 | 0 | 38889.4953 | 1 | 0 | 577.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4957 | 1 | 0 | 38889.4957 | 1 | 0 | 615.5 | 716.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4961 | 1 | 0 | 38889.4961 | 1 | 0 | 653.5 | 754.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4966 | 2 | 0 | 38889.4966 | 1 | 0 | 691.5 | 792.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129469 | 259038 | 129468.9988
38889.497 | 1 | 0 | 38889.497 | 1 | 0 | 729 | 830 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4974 | 1 | 0 | 38889.4974 | 1 | 0 | 766.5 | 867.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4979 | 1 | 0 | 38889.4979 | 1 | 0 | 804.5 | 905.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4983 | 1 | 0 | 38889.4983 | 1 | 0 | 842.5 | 943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4987 | 1 | 0 | 38889.4988 | 1 | 1 | 880.5 | 981.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 259038 | 259038 | 259037.9994
38889.4992 | 3 | 0 | 38889.4992 | 2443 | 0 | 917.5 | 1018.5 | 0.18315 | 0 | 149.1453 | 0 | 0.0018315 | 0 | 1.4915 | 0 | 0.0018315 | 1.4915 | 86279.3333 | 6.0737 | 86279.3315
38889.4996 | 2 | 0 | 38889.4996 | 2416 | 0 | 955.5 | 1056.5 | 0.1221 | 0 | 147.4969 | 0 | 0.001221 | 0 | 1.475 | 0 | 0.001221 | 1.475 | 129469 | 7.2591 | 129468.9988
38889.5001 | 1 | 0 | 38889.5001 | 2167 | 0 | 993.5 | 1094.5 | 0.06105 | 0 | 132.2955 | 0 | 0.0006105 | 0 | 1.323 | 0 | 0.0006105 | 1.323 | 259038 | 19.5838 | 259037.9994
38889.5005 | 2 | 0 | 38889.5005 | 2566 | 0 | 1031.5 | 1132.5 | 0.1221 | 0 | 156.6545 | 0 | 0.001221 | 0 | 1.5665 | 0 | 0.001221 | 1.5665 | 129469 | 0.98909 | 129468.9988
38889.5009 | 2 | 0 | 38889.5009 | 2551 | 0 | 1069.5 | 1170.5 | 0.1221 | 0 | 155.7387 | 0 | 0.001221 | 0 | 1.5574 | 0 | 0.001221 | 1.5574 | 129469 | 1.5829 | 129468.9988
38889.5014 | 2 | 0 | 38889.5014 | 2032 | 0 | 1106.5 | 1207.5 | 0.1221 | 0 | 124.0537 | 0 | 0.001221 | 0 | 1.2405 | 0 | 0.001221 | 1.2405 | 129469 | 27.5285 | 129468.9988
38889.5018 | 2 | 0 | 38889.5018 | 2285 | 0 | 1144.5 | 1245.5 | 0.1221 | 0 | 139.4994 | 0 | 0.001221 | 0 | 1.395 | 0 | 0.001221 | 1.395 | 129469 | 13.4083 | 129468.9988
38889.5022 | 2 | 0 | 38889.5023 | 2182 | 0 | 1182.5 | 1283.5 | 0.1221 | 0 | 133.2112 | 0 | 0.001221 | 0 | 1.3321 | 0 | 0.001221 | 1.3321 | 129469 | 18.7617 | 129468.9988
38889.5027 | 2 | 0 | 38889.5027 | 2008 | 0 | 1220.5 | 1321.5 | 0.1221 | 0 | 122.5885 | 0 | 0.001221 | 0 | 1.2259 | 0 | 0.001221 | 1.2259 | 129469 | 29.0528 | 129468.9988
38889.5031 | 2 | 0 | 38889.5031 | 2575 | 0 | 1258.5 | 1359.5 | 0.1221 | 0 | 157.2039 | 0 | 0.001221 | 0 | 1.572 | 0 | 0.001221 | 1.572 | 129469 | 0.63612 | 129468.9988
38889.5036 | 2 | 0 | 38889.5036 | 2389 | 0 | 1295.5 | 1396.5 | 0.1221 | 0 | 145.8486 | 0 | 0.001221 | 0 | 1.4585 | 0 | 0.001221 | 1.4585 | 129469 | 8.4713 | 129468.9988
38889.504 | 2 | 0 | 38889.504 | 2322 | 0 | 1333.5 | 1434.5 | 0.1221 | 0 | 141.7582 | 0 | 0.001221 | 0 | 1.4176 | 0 | 0.001221 | 1.4176 | 129469 | 11.6012 | 129468.9988
38889.5044 | 2 | 0 | 38889.5044 | 2079 | 0 | 1371.5 | 1472.5 | 0.1221 | 0 | 126.9231 | 0 | 0.001221 | 0 | 1.2692 | 0 | 0.001221 | 1.2692 | 129469 | 24.6455 | 129468.9988
38889.5049 | 2 | 0 | 38889.5049 | 2056 | 0 | 1409.5 | 1510.5 | 0.1221 | 0 | 125.5189 | 0 | 0.001221 | 0 | 1.2552 | 0 | 0.001221 | 1.2552 | 129469 | 26.0399 | 129468.9988
38889.5053 | 2 | 0 | 38889.5053 | 2036 | 0 | 1447 | 1548 | 0.1221 | 0 | 124.2979 | 0 | 0.001221 | 0 | 1.243 | 0 | 0.001221 | 1.243 | 129469 | 27.278 | 129468.9988
38889.5057 | 2 | 0 | 38889.5058 | 2483 | 0 | 1484.5 | 1585.5 | 0.1221 | 0 | 151.5873 | 0 | 0.001221 | 0 | 1.5159 | 0 | 0.001221 | 1.5159 | 129469 | 4.3649 | 129468.9988
38889.5062 | 1 | 0 | 38889.5062 | 2453 | 0 | 1522.5 | 1623.5 | 0.06105 | 0 | 149.7558 | 0 | 0.0006105 | 0 | 1.4976 | 0 | 0.0006105 | 1.4976 | 259038 | 5.6413 | 259037.9994
38889.5066 | 2 | 0 | 38889.5066 | 2061 | 0 | 1560.5 | 1661.5 | 0.1221 | 0 | 125.8242 | 0 | 0.001221 | 0 | 1.2582 | 0 | 0.001221 | 1.2582 | 129469 | 25.7341 | 129468.9988
38889.5071 | 2 | 0 | 38889.5071 | 2098 | 0 | 1598.5 | 1699.5 | 0.1221 | 0 | 128.083 | 0 | 0.001221 | 0 | 1.2808 | 0 | 0.001221 | 1.2808 | 129469 | 23.5167 | 129468.9988
38889.5075 | 2 | 0 | 38889.5075 | 2228 | 0 | 1636.5 | 1737.5 | 0.1221 | 0 | 136.0195 | 0 | 0.001221 | 0 | 1.3602 | 0 | 0.001221 | 1.3602 | 129469 | 16.3097 | 129468.9988
38889.5079 | 1 | 0 | 38889.5079 | 2022 | 0 | 1673.5 | 1774.5 | 0.06105 | 0 | 123.4432 | 0 | 0.0006105 | 0 | 1.2344 | 0 | 0.0006105 | 1.2344 | 259038 | 28.1592 | 259037.9994
38889.5084 | 2 | 0 | 38889.5084 | 2522 | 0 | 1711.5 | 1812.5 | 0.1221 | 0 | 153.9683 | 0 | 0.001221 | 0 | 1.5397 | 0 | 0.001221 | 1.5397 | 129469 | 2.751 | 129468.9988
38889.5088 | 2 | 0 | 38889.5088 | 2249 | 0 | 1749.5 | 1850.5 | 0.1221 | 0 | 137.3016 | 0 | 0.001221 | 0 | 1.373 | 0 | 0.001221 | 1.373 | 129469 | 15.2237 | 129468.9988
38889.5092 | 2 | 0 | 38889.5093 | 2152 | 0 | 1787.5 | 1888.5 | 0.1221 | 0 | 131.3797 | 0 | 0.001221 | 0 | 1.3138 | 0 | 0.001221 | 1.3138 | 129469 | 20.4173 | 129468.9988
38889.5097 | 2 | 0 | 38889.5097 | 2169 | 0 | 1825 | 1926 | 0.1221 | 0 | 132.4176 | 0 | 0.001221 | 0 | 1.3242 | 0 | 0.001221 | 1.3242 | 129469 | 19.4735 | 129468.9988
38889.5101 | 2 | 0 | 38889.5101 | 2115 | 0 | 1862.5 | 1963.5 | 0.1221 | 0 | 129.1209 | 0 | 0.001221 | 0 | 1.2912 | 0 | 0.001221 | 1.2912 | 129469 | 22.5239 | 129468.9988
38889.5106 | 2 | 0 | 38889.5106 | 2540 | 0 | 1900.5 | 2001.5 | 0.1221 | 0 | 155.0672 | 0 | 0.001221 | 0 | 1.5507 | 0 | 0.001221 | 1.5507 | 129469 | 2.0228 | 129468.9988
38889.511 | 1 | 0 | 38889.511 | 2467 | 0 | 1938.5 | 2039.5 | 0.06105 | 0 | 150.6105 | 0 | 0.0006105 | 0 | 1.5061 | 0 | 0.0006105 | 1.5061 | 259038 | 5.0418 | 259037.9994
38889.5114 | 2 | 0 | 38889.5114 | 2092 | 0 | 1976.5 | 2077.5 | 0.1221 | 0 | 127.7167 | 0 | 0.001221 | 0 | 1.2772 | 0 | 0.001221 | 1.2772 | 129469 | 23.8709 | 129468.9988
38889.5119 | 2 | 0 | 38889.5119 | 2562 | 0 | 2013.5 | 2114.5 | 0.1221 | 0 | 156.4103 | 0 | 0.001221 | 0 | 1.5641 | 0 | 0.001221 | 1.5641 | 129469 | 1.1468 | 129468.9988
38889.5123 | 1 | 0 | 38889.5123 | 2553 | 0 | 2051.5 | 2152.5 | 0.06105 | 0 | 155.8608 | 0 | 0.0006105 | 0 | 1.5586 | 0 | 0.0006105 | 1.5586 | 259038 | 1.5033 | 259037.9994
38889.5127 | 1 | 0 | 38889.5128 | 2165 | 0 | 2089.5 | 2190.5 | 0.06105 | 0 | 132.1734 | 0 | 0.0006105 | 0 | 1.3217 | 0 | 0.0006105 | 1.3217 | 259038 | 19.6942 | 259037.9994
38889.5132 | 2 | 0 | 38889.5132 | 1900 | 0 | 2127.5 | 2228.5 | 0.1221 | 0 | 115.9951 | 0 | 0.001221 | 0 | 1.16 | 0 | 0.001221 | 1.16 | 129469 | 36.3884 | 129468.9988
38889.5136 | 2 | 0 | 38889.5136 | 2054 | 0 | 2165.5 | 2266.5 | 0.1221 | 0 | 125.3968 | 0 | 0.001221 | 0 | 1.254 | 0 | 0.001221 | 1.254 | 129469 | 26.1626 | 129468.9988

## C5-7
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 158.1429 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38889.4878 | 1 | 0 | 38889.4878 | 1 | 0 | -66.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4882 | 1 | 0 | 38889.4882 | 1 | 0 | -28.5 | 72.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4887 | 1 | 0 | 38889.4887 | 1 | 0 | 9.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4891 | 1 | 0 | 38889.4891 | 1 | 0 | 46.5 | 147.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4895 | 1 | 0 | 38889.4895 | 1 | 0 | 84.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.49 | 1 | 0 | 38889.49 | 1 | 0 | 122.5 | 223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4904 | 1 | 0 | 38889.4904 | 1 | 0 | 160.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4909 | 1 | 0 | 38889.4909 | 1 | 0 | 198.5 | 299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4913 | 1 | 0 | 38889.4913 | 1 | 0 | 235.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4917 | 1 | 0 | 38889.4917 | 1 | 0 | 273.5 | 374.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4922 | 1 | 0 | 38889.4922 | 1 | 0 | 311.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4926 | 1 | 0 | 38889.4926 | 1 | 0 | 349.5 | 450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.493 | 1 | 0 | 38889.4931 | 1 | 0 | 387.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4935 | 1 | 0 | 38889.4935 | 1 | 0 | 424.5 | 525.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4939 | 1 | 0 | 38889.4939 | 1 | 0 | 462.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4944 | 1 | 0 | 38889.4944 | 1 | 0 | 500.5 | 601.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4948 | 1 | 0 | 38889.4948 | 1 | 0 | 538.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4952 | 1 | 0 | 38889.4952 | 1 | 0 | 576 | 677 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4957 | 1 | 0 | 38889.4957 | 1 | 0 | 613.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4961 | 1 | 0 | 38889.4961 | 1 | 0 | 651.5 | 752.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4965 | 1 | 0 | 38889.4966 | 1 | 0 | 689.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.497 | 1 | 0 | 38889.497 | 1 | 0 | 727.5 | 828.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4974 | 1 | 0 | 38889.4974 | 1 | 0 | 765 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4978 | 1 | 0 | 38889.4979 | 1 | 0 | 802.5 | 903.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4983 | 1 | 0 | 38889.4983 | 1 | 0 | 840.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4987 | 1 | 0 | 38889.4987 | 1 | 0 | 878.5 | 979.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4992 | 1 | 0 | 38889.4992 | 2158 | 0 | 916.5 | 1017.5 | 0.06105 | 0 | 131.746 | 0 | 0.0006105 | 0 | 1.3175 | 0 | 0.0006105 | 1.3175 | 258938 | 20.0361 | 258937.9994
38889.4996 | 1 | 0 | 38889.4996 | 2376 | 0 | 954 | 1055 | 0.06105 | 0 | 145.0549 | 0 | 0.0006105 | 0 | 1.4505 | 0 | 0.0006105 | 1.4505 | 258938 | 9.0227 | 258937.9994
38889.5 | 1 | 0 | 38889.5 | 2521 | 0 | 991.5 | 1092.5 | 0.06105 | 0 | 153.9072 | 0 | 0.0006105 | 0 | 1.5391 | 0 | 0.0006105 | 1.5391 | 258938 | 2.7521 | 258937.9994
38889.5005 | 2 | 0 | 38889.5005 | 2348 | 0 | 1029.5 | 1130.5 | 0.1221 | 0 | 143.3455 | 0 | 0.001221 | 0 | 1.4335 | 0 | 0.001221 | 1.4335 | 129419 | 10.3228 | 129418.9988
38889.5009 | 2 | 0 | 38889.5009 | 2485 | 0 | 1067.5 | 1168.5 | 0.1221 | 0 | 151.7094 | 0 | 0.001221 | 0 | 1.5171 | 0 | 0.001221 | 1.5171 | 129419 | 4.2406 | 129418.9988
38889.5014 | 1 | 0 | 38889.5014 | 2015 | 0 | 1105.5 | 1206.5 | 0.06105 | 0 | 123.0159 | 0 | 0.0006105 | 0 | 1.2302 | 0 | 0.0006105 | 1.2302 | 258938 | 28.5548 | 258937.9994
38889.5018 | 1 | 0 | 38889.5018 | 2566 | 0 | 1142.5 | 1243.5 | 0.06105 | 0 | 156.6545 | 0 | 0.0006105 | 0 | 1.5665 | 0 | 0.0006105 | 1.5665 | 258938 | 0.95012 | 258937.9994
38889.5022 | 1 | 0 | 38889.5022 | 2533 | 0 | 1180.5 | 1281.5 | 0.06105 | 0 | 154.6398 | 0 | 0.0006105 | 0 | 1.5464 | 0 | 0.0006105 | 1.5464 | 258938 | 2.2653 | 258937.9994
38889.5027 | 1 | 0 | 38889.5027 | 2084 | 0 | 1218.5 | 1319.5 | 0.06105 | 0 | 127.2283 | 0 | 0.0006105 | 0 | 1.2723 | 0 | 0.0006105 | 1.2723 | 258938 | 24.2985 | 258937.9994
38889.5031 | 1 | 1 | 38889.5031 | 2574 | 0 | 1256.5 | 1357.5 | 0.06105 | 0.06105 | 157.1429 | 0 | 0.0006105 | 0.0006105 | 1.5714 | 0 | 0 | 1.5714 | 1647.7873 | 0.63636 | 1636.7353
38889.5035 | 1 | 0 | 38889.5036 | 2011 | 0 | 1294.5 | 1395.5 | 0.06105 | 0 | 122.7717 | 0 | 0.0006105 | 0 | 1.2277 | 0 | 0.0006105 | 1.2277 | 258938 | 28.8105 | 258937.9994
38889.504 | 1 | 0 | 38889.504 | 2295 | 0 | 1331.5 | 1432.5 | 0.06105 | 0 | 140.1099 | 0 | 0.0006105 | 0 | 1.4011 | 0 | 0.0006105 | 1.4011 | 258938 | 12.8706 | 258937.9994
38889.5044 | 1 | 0 | 38889.5044 | 2522 | 0 | 1369.5 | 1470.5 | 0.06105 | 0 | 153.9683 | 0 | 0.0006105 | 0 | 1.5397 | 0 | 0.0006105 | 1.5397 | 258938 | 2.7113 | 258937.9994
38889.5048 | 1 | 0 | 38889.5049 | 1983 | 0 | 1407.5 | 1508.5 | 0.06105 | 0 | 121.0623 | 0 | 0.0006105 | 0 | 1.2106 | 0 | 0.0006105 | 1.2106 | 258938 | 30.6293 | 258937.9994
38889.5053 | 1 | 0 | 38889.5053 | 2364 | 0 | 1445.5 | 1546.5 | 0.06105 | 0 | 144.3223 | 0 | 0.0006105 | 0 | 1.4432 | 0 | 0.0006105 | 1.4432 | 258938 | 9.5761 | 258937.9994
38889.5057 | 1 | 0 | 38889.5057 | 2567 | 0 | 1483 | 1584 | 0.06105 | 0 | 156.7155 | 0 | 0.0006105 | 0 | 1.5672 | 0 | 0.0006105 | 1.5672 | 258938 | 0.91079 | 258937.9994
38889.5062 | 1 | 0 | 38889.5062 | 2490 | 0 | 1520.5 | 1621.5 | 0.06105 | 0 | 152.0147 | 0 | 0.0006105 | 0 | 1.5201 | 0 | 0.0006105 | 1.5201 | 258938 | 4.0313 | 258937.9994
38889.5066 | 1 | 0 | 38889.5066 | 2130 | 0 | 1558.5 | 1659.5 | 0.06105 | 0 | 130.0366 | 0 | 0.0006105 | 0 | 1.3004 | 0 | 0.0006105 | 1.3004 | 258938 | 21.6141 | 258937.9994
38889.507 | 1 | 0 | 38889.507 | 1984 | 0 | 1596.5 | 1697.5 | 0.06105 | 0 | 121.1233 | 0 | 0.0006105 | 0 | 1.2112 | 0 | 0.0006105 | 1.2112 | 258938 | 30.5635 | 258937.9994
38889.5075 | 1 | 0 | 38889.5075 | 2252 | 0 | 1634.5 | 1735.5 | 0.06105 | 0 | 137.4847 | 0 | 0.0006105 | 0 | 1.3748 | 0 | 0.0006105 | 1.3748 | 258938 | 15.0258 | 258937.9994
38889.5079 | 1 | 0 | 38889.5079 | 2382 | 0 | 1672.5 | 1773.5 | 0.06105 | 0 | 145.4212 | 0 | 0.0006105 | 0 | 1.4542 | 0 | 0.0006105 | 1.4542 | 258938 | 8.7481 | 258937.9994
38889.5083 | 1 | 0 | 38889.5084 | 2111 | 0 | 1709.5 | 1810.5 | 0.06105 | 0 | 128.8767 | 0 | 0.0006105 | 0 | 1.2888 | 0 | 0.0006105 | 1.2888 | 258938 | 22.7087 | 258937.9994
38889.5088 | 1 | 0 | 38889.5088 | 2449 | 0 | 1747.5 | 1848.5 | 0.06105 | 0 | 149.5116 | 0 | 0.0006105 | 0 | 1.4951 | 0 | 0.0006105 | 1.4951 | 258938 | 5.773 | 258937.9994
38889.5092 | 1 | 0 | 38889.5092 | 2074 | 0 | 1785.5 | 1886.5 | 0.06105 | 0 | 126.6178 | 0 | 0.0006105 | 0 | 1.2662 | 0 | 0.0006105 | 1.2662 | 258938 | 24.8978 | 258937.9994
38889.5097 | 1 | 0 | 38889.5097 | 2413 | 0 | 1823.5 | 1924.5 | 0.06105 | 0 | 147.3138 | 0 | 0.0006105 | 0 | 1.4731 | 0 | 0.0006105 | 1.4731 | 258938 | 7.351 | 258937.9994
38889.5101 | 1 | 0 | 38889.5101 | 2084 | 0 | 1861 | 1962 | 0.06105 | 0 | 127.2283 | 0 | 0.0006105 | 0 | 1.2723 | 0 | 0.0006105 | 1.2723 | 258938 | 24.2985 | 258937.9994
38889.5105 | 1 | 0 | 38889.5105 | 2392 | 0 | 1898.5 | 1999.5 | 0.06105 | 0 | 146.0317 | 0 | 0.0006105 | 0 | 1.4603 | 0 | 0.0006105 | 1.4603 | 258938 | 8.2935 | 258937.9994
38889.511 | 1 | 0 | 38889.511 | 2342 | 0 | 1936.5 | 2037.5 | 0.06105 | 0 | 142.9792 | 0 | 0.0006105 | 0 | 1.4298 | 0 | 0.0006105 | 1.4298 | 258938 | 10.6055 | 258937.9994
38889.5114 | 1 | 0 | 38889.5114 | 2539 | 0 | 1974.5 | 2075.5 | 0.06105 | 0 | 155.0061 | 0 | 0.0006105 | 0 | 1.5501 | 0 | 0.0006105 | 1.5501 | 258938 | 2.0236 | 258937.9994
38889.5119 | 1 | 0 | 38889.5119 | 2283 | 0 | 2012.5 | 2113.5 | 0.06105 | 0 | 139.3773 | 0 | 0.0006105 | 0 | 1.3938 | 0 | 0.0006105 | 1.3938 | 258938 | 13.4639 | 258937.9994
38889.5123 | 2 | 0 | 38889.5123 | 2155 | 0 | 2049.5 | 2150.5 | 0.1221 | 0 | 131.5629 | 0 | 0.001221 | 0 | 1.3156 | 0 | 0.001221 | 1.3156 | 129419 | 20.2032 | 129418.9988
38889.5127 | 1 | 0 | 38889.5127 | 1856 | 0 | 2087.5 | 2188.5 | 0.06105 | 0 | 113.3089 | 0 | 0.0006105 | 0 | 1.1331 | 0 | 0.0006105 | 1.1331 | 258938 | 39.5679 | 258937.9994
38889.5132 | 1 | 0 | 38889.5132 | 2087 | 0 | 2125.5 | 2226.5 | 0.06105 | 0 | 127.4115 | 0 | 0.0006105 | 0 | 1.2741 | 0 | 0.0006105 | 1.2741 | 258938 | 24.1198 | 258937.9994
38889.5136 | 1 | 0 | 38889.5136 | 1935 | 0 | 2163.5 | 2264.5 | 0.06105 | 0 | 118.1319 | 0 | 0.0006105 | 0 | 1.1813 | 0 | 0.0006105 | 1.1813 | 258938 | 33.8698 | 258937.9994

## C5-6
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38889.4878 | 1 | 0 | 38889.4878 | 1 | 0 | -68.5 | 32.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4882 | 1 | 0 | 38889.4882 | 1 | 0 | -30.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4886 | 1 | 0 | 38889.4887 | 1 | 0 | 7.5 | 108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4891 | 1 | 0 | 38889.4891 | 1 | 0 | 45 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4895 | 1 | 0 | 38889.4895 | 1 | 0 | 82.5 | 183.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.49 | 1 | 0 | 38889.49 | 1 | 0 | 120.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4904 | 1 | 0 | 38889.4904 | 1 | 0 | 158.5 | 259.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4908 | 1 | 0 | 38889.4908 | 1 | 0 | 196.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4913 | 1 | 0 | 38889.4913 | 1 | 0 | 234 | 335 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4917 | 1 | 0 | 38889.4917 | 1 | 0 | 271.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4921 | 1 | 0 | 38889.4922 | 1 | 0 | 309.5 | 410.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4926 | 1 | 0 | 38889.4926 | 1 | 0 | 347.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.493 | 1 | 0 | 38889.493 | 1 | 0 | 385.5 | 486.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4935 | 1 | 0 | 38889.4935 | 1 | 0 | 423 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4939 | 1 | 0 | 38889.4939 | 1 | 0 | 460.5 | 561.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4943 | 1 | 0 | 38889.4943 | 1 | 0 | 498.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4948 | 1 | 0 | 38889.4948 | 1 | 0 | 536.5 | 637.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4952 | 1 | 0 | 38889.4952 | 1 | 0 | 574.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4956 | 1 | 0 | 38889.4956 | 1 | 0 | 612 | 713 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4961 | 1 | 0 | 38889.4961 | 1 | 0 | 649.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4965 | 1 | 0 | 38889.4965 | 2 | 0 | 687.5 | 788.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.497 | 1 | 0 | 38889.497 | 1 | 0 | 725.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4974 | 1 | 0 | 38889.4974 | 1 | 0 | 763.5 | 864.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4978 | 1 | 0 | 38889.4978 | 1 | 0 | 800.5 | 901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4983 | 2 | 0 | 38889.4983 | 1 | 0 | 838.5 | 939.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4987 | 1 | 0 | 38889.4987 | 1 | 0 | 876.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4991 | 2 | 0 | 38889.4992 | 1 | 0 | 914.5 | 1015.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4996 | 2 | 0 | 38889.4996 | 1 | 0 | 952.5 | 1053.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5 | 1 | 0 | 38889.5 | 1 | 0 | 990 | 1091 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5005 | 2 | 0 | 38889.5005 | 1 | 0 | 1027.5 | 1128.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5009 | 3 | 0 | 38889.5009 | 2 | 0 | 1065.5 | 1166.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38889.5013 | 2 | 0 | 38889.5013 | 1 | 0 | 1103.5 | 1204.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5018 | 2 | 0 | 38889.5018 | 1 | 0 | 1141.5 | 1242.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5022 | 2 | 0 | 38889.5022 | 1 | 0 | 1178.5 | 1279.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5026 | 2 | 0 | 38889.5027 | 1 | 0 | 1216.5 | 1317.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5031 | 2 | 0 | 38889.5031 | 1 | 0 | 1254.5 | 1355.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5035 | 2 | 0 | 38889.5035 | 1 | 0 | 1292.5 | 1393.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.504 | 1 | 0 | 38889.504 | 1 | 0 | 1330.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5044 | 1 | 0 | 38889.5044 | 1 | 0 | 1367.5 | 1468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5048 | 2 | 0 | 38889.5048 | 1 | 0 | 1405.5 | 1506.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5053 | 2 | 0 | 38889.5053 | 1 | 0 | 1443.5 | 1544.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5057 | 2 | 0 | 38889.5057 | 1 | 0 | 1481.5 | 1582.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5061 | 2 | 0 | 38889.5061 | 1 | 0 | 1519 | 1620 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5066 | 2 | 0 | 38889.5066 | 1 | 0 | 1556.5 | 1657.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.507 | 2 | 0 | 38889.507 | 1 | 0 | 1594.5 | 1695.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
| 2 | 0 | 38889.5075 | 1 | 0 | 1633 | 1734 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5079 | 2 | 0 | 38889.5079 | 1 | 0 | 1670.5 | 1771.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5083 | 2 | 0 | 38889.5083 | 1 | 0 | 1707.5 | 1808.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5088 | 2 | 0 | 38889.5088 | 1 | 0 | 1745.5 | 1846.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5092 | 2 | 0 | 38889.5092 | 1 | 0 | 1783.5 | 1884.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5096 | 2 | 0 | 38889.5097 | 1 | 0 | 1821.5 | 1922.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5101 | 2 | 0 | 38889.5101 | 1 | 0 | 1859.5 | 1960.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5105 | 2 | 0 | 38889.5105 | 1 | 0 | 1896.5 | 1997.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5109 | 2 | 0 | 38889.511 | 1 | 0 | 1934.5 | 2035.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5114 | 2 | 0 | 38889.5114 | 1 | 0 | 1972.5 | 2073.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5118 | 2 | 0 | 38889.5118 | 1 | 0 | 2010.5 | 2111.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5123 | 2 | 0 | 38889.5123 | 1 | 0 | 2048.5 | 2149.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5127 | 3 | 0 | 38889.5127 | 1 | 0 | 2085.5 | 2186.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 70334 | 211202 | 70333.9982
38889.5131 | 1 | 0 | 38889.5131 | 2 | 0 | 2123.5 | 2224.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5136 | 2 | 0 | 38889.5136 | 1 | 0 | 2161.5 | 2262.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## C4-7
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 158.1429 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38889.4877 | 1 | 0 | 38889.4878 | 1 | 0 | -70.5 | 30.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4882 | 1 | 0 | 38889.4882 | 1 | 0 | -32.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4886 | 1 | 0 | 38889.4886 | 1 | 0 | 5.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4891 | 1 | 0 | 38889.4891 | 1 | 0 | 43.5 | 144.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4895 | 1 | 0 | 38889.4895 | 1 | 0 | 81 | 182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4899 | 1 | 0 | 38889.4899 | 1 | 0 | 118.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4904 | 2 | 0 | 38889.4904 | 2 | 0 | 156.5 | 257.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 129419 | 129419 | 129418.9988
38889.4908 | 1 | 0 | 38889.4908 | 1 | 0 | 194.5 | 295.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4912 | 1 | 0 | 38889.4913 | 1 | 0 | 232.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4917 | 1 | 0 | 38889.4917 | 1 | 0 | 270 | 371 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4921 | 1 | 0 | 38889.4921 | 1 | 0 | 307.5 | 408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4926 | 1 | 0 | 38889.4926 | 1 | 0 | 345.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.493 | 1 | 0 | 38889.493 | 1 | 0 | 383.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4934 | 1 | 0 | 38889.4934 | 1 | 0 | 421.5 | 522.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4939 | 1 | 0 | 38889.4939 | 1 | 0 | 459 | 560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4943 | 1 | 0 | 38889.4943 | 1 | 0 | 496.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4947 | 1 | 0 | 38889.4948 | 1 | 0 | 534.5 | 635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4952 | 1 | 0 | 38889.4952 | 1 | 0 | 572.5 | 673.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4956 | 1 | 0 | 38889.4956 | 1 | 0 | 610.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4961 | 1 | 0 | 38889.4961 | 1 | 0 | 648 | 749 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4965 | 1 | 0 | 38889.4965 | 1 | 0 | 685.5 | 786.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4969 | 1 | 0 | 38889.4969 | 1 | 0 | 723.5 | 824.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4974 | 1 | 0 | 38889.4974 | 1 | 0 | 761.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4978 | 1 | 0 | 38889.4978 | 1 | 0 | 799.5 | 900.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4983 | 1 | 0 | 38889.4983 | 1 | 0 | 837 | 938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4987 | 1 | 0 | 38889.4987 | 1 | 0 | 874.5 | 975.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
38889.4991 | 1 | 0 | 38889.4991 | 2376 | 0 | 912.5 | 1013.5 | 0.06105 | 0 | 145.0549 | 0 | 0.0006105 | 0 | 1.4505 | 0 | 0.0006105 | 1.4505 | 258938 | 9.0227 | 258937.9994
38889.4996 | 1 | 0 | 38889.4996 | 2003 | 0 | 950.5 | 1051.5 | 0.06105 | 0 | 122.2833 | 0 | 0.0006105 | 0 | 1.2228 | 0 | 0.0006105 | 1.2228 | 258938 | 29.325 | 258937.9994
38889.5 | 1 | 0 | 38889.5 | 2047 | 0 | 988.5 | 1089.5 | 0.06105 | 0 | 124.9695 | 0 | 0.0006105 | 0 | 1.2497 | 0 | 0.0006105 | 1.2497 | 258938 | 26.5452 | 258937.9994
38889.5004 | 1 | 0 | 38889.5004 | 2267 | 0 | 1026 | 1127 | 0.06105 | 0 | 138.4005 | 0 | 0.0006105 | 0 | 1.384 | 0 | 0.0006105 | 1.384 | 258938 | 14.2647 | 258937.9994
38889.5009 | 1 | 0 | 38889.5009 | 2066 | 0 | 1063.5 | 1164.5 | 0.06105 | 0 | 126.1294 | 0 | 0.0006105 | 0 | 1.2613 | 0 | 0.0006105 | 1.2613 | 258938 | 25.3814 | 258937.9994
38889.5013 | 1 | 0 | 38889.5013 | 2151 | 0 | 1101.5 | 1202.5 | 0.06105 | 0 | 131.3187 | 0 | 0.0006105 | 0 | 1.3132 | 0 | 0.0006105 | 1.3132 | 258938 | 20.4268 | 258937.9994
38889.5017 | 1 | 0 | 38889.5018 | 2444 | 0 | 1139.5 | 1240.5 | 0.06105 | 0 | 149.2063 | 0 | 0.0006105 | 0 | 1.4921 | 0 | 0.0006105 | 1.4921 | 258938 | 5.9894 | 258937.9994
38889.5022 | 1 | 0 | 38889.5022 | 2573 | 0 | 1177 | 1278 | 0.06105 | 0 | 157.0818 | 0 | 0.0006105 | 0 | 1.5708 | 0 | 0.0006105 | 1.5708 | 258938 | 0.67548 | 258937.9994
38889.5026 | 1 | 0 | 38889.5026 | 2574 | 0 | 1214.5 | 1315.5 | 0.06105 | 0 | 157.1429 | 0 | 0.0006105 | 0 | 1.5714 | 0 | 0.0006105 | 1.5714 | 258938 | 0.63636 | 258937.9994
38889.5031 | 1 | 0 | 38889.5031 | 1982 | 0 | 1252.5 | 1353.5 | 0.06105 | 0 | 121.0012 | 0 | 0.0006105 | 0 | 1.21 | 0 | 0.0006105 | 1.21 | 258938 | 30.6953 | 258937.9994
38889.5035 | 1 | 0 | 38889.5035 | 2528 | 0 | 1290.5 | 1391.5 | 0.06105 | 0 | 154.3346 | 0 | 0.0006105 | 0 | 1.5433 | 0 | 0.0006105 | 1.5433 | 258938 | 2.4676 | 258937.9994
38889.5039 | 1 | 0 | 38889.5039 | 2429 | 0 | 1328.5 | 1429.5 | 0.06105 | 0 | 148.2906 | 0 | 0.0006105 | 0 | 1.4829 | 0 | 0.0006105 | 1.4829 | 258938 | 6.6439 | 258937.9994
38889.5044 | 1 | 0 | 38889.5044 | 2114 | 0 | 1366.5 | 1467.5 | 0.06105 | 0 | 129.0598 | 0 | 0.0006105 | 0 | 1.2906 | 0 | 0.0006105 | 1.2906 | 258938 | 22.5345 | 258937.9994
38889.5048 | 1 | 0 | 38889.5048 | 2571 | 0 | 1403.5 | 1504.5 | 0.06105 | 0 | 156.9597 | 0 | 0.0006105 | 0 | 1.5696 | 0 | 0.0006105 | 1.5696 | 258938 | 0.75379 | 258937.9994
38889.5052 | 1 | 0 | 38889.5053 | 2284 | 0 | 1441.5 | 1542.5 | 0.06105 | 0 | 139.4383 | 0 | 0.0006105 | 0 | 1.3944 | 0 | 0.0006105 | 1.3944 | 258938 | 13.4142 | 258937.9994
38889.5057 | 1 | 0 | 38889.5057 | 2268 | 0 | 1479.5 | 1580.5 | 0.06105 | 0 | 138.4615 | 0 | 0.0006105 | 0 | 1.3846 | 0 | 0.0006105 | 1.3846 | 258938 | 14.2143 | 258937.9994
38889.5061 | 1 | 0 | 38889.5061 | 2187 | 0 | 1517.5 | 1618.5 | 0.06105 | 0 | 133.5165 | 0 | 0.0006105 | 0 | 1.3352 | 0 | 0.0006105 | 1.3352 | 258938 | 18.4444 | 258937.9994
38889.5066 | 1 | 0 | 38889.5066 | 2070 | 0 | 1555 | 1656 | 0.06105 | 0 | 126.3736 | 0 | 0.0006105 | 0 | 1.2637 | 0 | 0.0006105 | 1.2637 | 258938 | 25.1391 | 258937.9994
38889.507 | 1 | 0 | 38889.507 | 2269 | 0 | 1592.5 | 1693.5 | 0.06105 | 0 | 138.5226 | 0 | 0.0006105 | 0 | 1.3852 | 0 | 0.0006105 | 1.3852 | 258938 | 14.1639 | 258937.9994
38889.5074 | 1 | 0 | 38889.5074 | 2119 | 0 | 1630.5 | 1731.5 | 0.06105 | 0 | 129.3651 | 0 | 0.0006105 | 0 | 1.2937 | 0 | 0.0006105 | 1.2937 | 258938 | 22.2454 | 258937.9994
38889.5079 | 1 | 0 | 38889.5079 | 2013 | 0 | 1668.5 | 1769.5 | 0.06105 | 0 | 122.8938 | 0 | 0.0006105 | 0 | 1.2289 | 0 | 0.0006105 | 1.2289 | 258938 | 28.6826 | 258937.9994
38889.5083 | 1 | 0 | 38889.5083 | 2414 | 0 | 1706.5 | 1807.5 | 0.06105 | 0 | 147.3748 | 0 | 0.0006105 | 0 | 1.4737 | 0 | 0.0006105 | 1.4737 | 258938 | 7.3065 | 258937.9994
38889.5088 | 1 | 0 | 38889.5088 | 2038 | 0 | 1744 | 1845 | 0.06105 | 0 | 124.42 | 0 | 0.0006105 | 0 | 1.2442 | 0 | 0.0006105 | 1.2442 | 258938 | 27.104 | 258937.9994
38889.5092 | 1 | 0 | 38889.5092 | 2319 | 0 | 1781.5 | 1882.5 | 0.06105 | 0 | 141.5751 | 0 | 0.0006105 | 0 | 1.4158 | 0 | 0.0006105 | 1.4158 | 258938 | 11.7025 | 258937.9994
38889.5096 | 1 | 0 | 38889.5096 | 2355 | 0 | 1819.5 | 1920.5 | 0.06105 | 0 | 143.7729 | 0 | 0.0006105 | 0 | 1.4377 | 0 | 0.0006105 | 1.4377 | 258938 | 9.9949 | 258937.9994
38889.5101 | 1 | 0 | 38889.5101 | 2340 | 0 | 1857.5 | 1958.5 | 0.06105 | 0 | 142.8571 | 0 | 0.0006105 | 0 | 1.4286 | 0 | 0.0006105 | 1.4286 | 258938 | 10.7 | 258937.9994
38889.5105 | 1 | 0 | 38889.5105 | 2354 | 0 | 1895.5 | 1996.5 | 0.06105 | 0 | 143.7118 | 0 | 0.0006105 | 0 | 1.4371 | 0 | 0.0006105 | 1.4371 | 258938 | 10.0416 | 258937.9994
38889.5109 | 1 | 0 | 38889.5109 | 2114 | 0 | 1932.5 | 2033.5 | 0.06105 | 0 | 129.0598 | 0 | 0.0006105 | 0 | 1.2906 | 0 | 0.0006105 | 1.2906 | 258938 | 22.5345 | 258937.9994
38889.5114 | 1 | 0 | 38889.5114 | 2145 | 0 | 1970.5 | 2071.5 | 0.06105 | 0 | 130.9524 | 0 | 0.0006105 | 0 | 1.3095 | 0 | 0.0006105 | 1.3095 | 258938 | 20.7636 | 258937.9994
38889.5118 | 1 | 0 | 38889.5118 | 2100 | 0 | 2008.5 | 2109.5 | 0.06105 | 0 | 128.2051 | 0 | 0.0006105 | 0 | 1.2821 | 0 | 0.0006105 | 1.2821 | 258938 | 23.3514 | 258937.9994
38889.5122 | 1 | 0 | 38889.5123 | 1988 | 0 | 2046.5 | 2147.5 | 0.06105 | 0 | 121.3675 | 0 | 0.0006105 | 0 | 1.2137 | 0 | 0.0006105 | 1.2137 | 258938 | 30.3008 | 258937.9994
38889.5127 | 1 | 0 | 38889.5127 | 2239 | 0 | 2084.5 | 2185.5 | 0.06105 | 0 | 136.6911 | 0 | 0.0006105 | 0 | 1.3669 | 0 | 0.0006105 | 1.3669 | 258938 | 15.6936 | 258937.9994
38889.5131 | 1 | 0 | 38889.5131 | 2188 | 0 | 2121.5 | 2222.5 | 0.06105 | 0 | 133.5775 | 0 | 0.0006105 | 0 | 1.3358 | 0 | 0.0006105 | 1.3358 | 258938 | 18.3903 | 258937.9994
38889.5136 | 1 | 0 | 38889.5136 | 1963 | 0 | 2159.5 | 2260.5 | 0.06105 | 0 | 119.8413 | 0 | 0.0006105 | 0 | 1.1984 | 0 | 0.0006105 | 1.1984 | 258938 | 31.9603 | 258937.9994

## C4-6
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38889.4877 | 1 | 0 | 38889.4877 | 1 | 0 | -71.5 | 29.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4882 | 1 | 0 | 38889.4882 | 1 | 0 | -34.5 | 66.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4886 | 1 | 0 | 38889.4886 | 1 | 0 | 3.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.489 | 1 | 0 | 38889.4891 | 1 | 0 | 41.5 | 142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4895 | 1 | 0 | 38889.4895 | 1 | 0 | 79.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4899 | 1 | 0 | 38889.4899 | 1 | 0 | 117 | 218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4903 | 1 | 0 | 38889.4904 | 2 | 0 | 154.5 | 255.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.4908 | 1 | 0 | 38889.4908 | 1 | 0 | 192.5 | 293.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4912 | 1 | 0 | 38889.4912 | 1 | 0 | 230.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4917 | 1 | 0 | 38889.4917 | 1 | 0 | 268.5 | 369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4921 | 1 | 0 | 38889.4921 | 1 | 0 | 306.5 | 407.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4925 | 1 | 0 | 38889.4925 | 1 | 0 | 343.5 | 444.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.493 | 1 | 0 | 38889.493 | 1 | 0 | 381.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4934 | 1 | 0 | 38889.4934 | 1 | 0 | 419.5 | 520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4939 | 1 | 0 | 38889.4939 | 1 | 0 | 457.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4943 | 1 | 0 | 38889.4943 | 1 | 0 | 494.5 | 595.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4947 | 1 | 0 | 38889.4947 | 1 | 0 | 532.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4952 | 1 | 0 | 38889.4952 | 1 | 0 | 570.5 | 671.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4956 | 1 | 0 | 38889.4956 | 1 | 0 | 608.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.496 | 1 | 0 | 38889.4961 | 1 | 0 | 646.5 | 747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4965 | 1 | 0 | 38889.4965 | 1 | 0 | 683.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4969 | 1 | 0 | 38889.4969 | 1 | 0 | 721.5 | 822.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4973 | 1 | 0 | 38889.4974 | 1 | 0 | 759.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4978 | 1 | 0 | 38889.4978 | 1 | 0 | 797.5 | 898.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4982 | 1 | 0 | 38889.4982 | 1 | 0 | 835.5 | 936.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4987 | 1 | 0 | 38889.4987 | 1 | 0 | 872.5 | 973.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4991 | 1 | 0 | 38889.4991 | 1 | 0 | 910.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4995 | 1 | 0 | 38889.4995 | 1 | 0 | 948.5 | 1049.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5 | 1 | 0 | 38889.5 | 1 | 0 | 986.5 | 1087.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5004 | 1 | 0 | 38889.5004 | 1 | 0 | 1024.5 | 1125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5009 | 1 | 0 | 38889.5009 | 1 | 0 | 1062 | 1163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5013 | 1 | 0 | 38889.5013 | 1 | 0 | 1099.5 | 1200.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5017 | 1 | 0 | 38889.5017 | 1 | 0 | 1137.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5022 | 1 | 0 | 38889.5022 | 1 | 0 | 1175.5 | 1276.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5026 | 1 | 0 | 38889.5026 | 1 | 0 | 1213.5 | 1314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.503 | 1 | 0 | 38889.503 | 1 | 0 | 1250.5 | 1351.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5035 | 1 | 0 | 38889.5035 | 1 | 0 | 1288.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5039 | 1 | 0 | 38889.5039 | 1 | 0 | 1326.5 | 1427.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5044 | 2 | 0 | 38889.5044 | 1 | 0 | 1364.5 | 1465.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5048 | 1 | 0 | 38889.5048 | 1 | 0 | 1402.5 | 1503.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5052 | 1 | 0 | 38889.5052 | 1 | 0 | 1439.5 | 1540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5057 | 1 | 0 | 38889.5057 | 1 | 0 | 1477.5 | 1578.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5061 | 1 | 0 | 38889.5061 | 1 | 0 | 1515.5 | 1616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5065 | 1 | 0 | 38889.5066 | 2 | 0 | 1553.5 | 1654.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.507 | 1 | 0 | 38889.507 | 1 | 0 | 1591 | 1692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5074 | 1 | 0 | 38889.5074 | 1 | 0 | 1628.5 | 1729.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5078 | 1 | 0 | 38889.5079 | 1 | 0 | 1666.5 | 1767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5083 | 1 | 0 | 38889.5083 | 1 | 0 | 1704.5 | 1805.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5087 | 1 | 1 | 38889.5087 | 1 | 0 | 1742.5 | 1843.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5092 | 1 | 1 | 38889.5092 | 1 | 0 | 1780 | 1881 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5096 | 1 | 0 | 38889.5096 | 1 | 0 | 1817.5 | 1918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.51 | 1 | 1 | 38889.51 | 1 | 0 | 1855.5 | 1956.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5105 | 2 | 1 | 38889.5105 | 1 | 0 | 1893.5 | 1994.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38889.5109 | 2 | 1 | 38889.5109 | 1 | 0 | 1931.5 | 2032.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38889.5113 | 1 | 1 | 38889.5114 | 1 | 0 | 1968.5 | 2069.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5118 | 1 | 1 | 38889.5118 | 1 | 0 | 2006.5 | 2107.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5122 | 1 | 0 | 38889.5122 | 1 | 0 | 2044.5 | 2145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5127 | 1 | 1 | 38889.5127 | 1 | 0 | 2082.5 | 2183.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5131 | 1 | 1 | 38889.5131 | 1 | 0 | 2120.5 | 2221.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5135 | 2 | 1 | 38889.5135 | 1 | 0 | 2157.5 | 2258.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142

## C4-5
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38889.4877 | 1 | 0 | 38889.4877 | 1 | 0 | -73.5 | 27.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4881 | 1 | 0 | 38889.4882 | 1 | 0 | -35.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4886 | 1 | 0 | 38889.4886 | 1 | 0 | 1.5 | 102.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.489 | 1 | 0 | 38889.489 | 1 | 0 | 39.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4895 | 1 | 0 | 38889.4895 | 1 | 0 | 77.5 | 178.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4899 | 1 | 0 | 38889.4899 | 1 | 0 | 115.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4903 | 1 | 0 | 38889.4903 | 1 | 0 | 153 | 254 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4908 | 1 | 0 | 38889.4908 | 1 | 0 | 190.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4912 | 1 | 0 | 38889.4912 | 1 | 0 | 228.5 | 329.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4916 | 1 | 0 | 38889.4917 | 1 | 0 | 266.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4921 | 1 | 0 | 38889.4921 | 1 | 0 | 304.5 | 405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4925 | 1 | 0 | 38889.4925 | 1 | 0 | 342.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.493 | 1 | 0 | 38889.493 | 1 | 0 | 379.5 | 480.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4934 | 1 | 0 | 38889.4934 | 1 | 0 | 417.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4938 | 1 | 0 | 38889.4938 | 1 | 0 | 455.5 | 556.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4943 | 1 | 0 | 38889.4943 | 1 | 0 | 493.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4947 | 1 | 0 | 38889.4947 | 1 | 0 | 531 | 632 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4951 | 1 | 0 | 38889.4952 | 1 | 0 | 568.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4956 | 1 | 0 | 38889.4956 | 1 | 0 | 606.5 | 707.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.496 | 1 | 0 | 38889.496 | 1 | 0 | 644.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4965 | 1 | 0 | 38889.4965 | 1 | 0 | 682.5 | 783.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4969 | 1 | 0 | 38889.4969 | 1 | 0 | 720 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4973 | 1 | 0 | 38889.4973 | 1 | 0 | 757.5 | 858.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4978 | 1 | 0 | 38889.4978 | 1 | 0 | 795.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4982 | 1 | 0 | 38889.4982 | 1 | 0 | 833.5 | 934.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4986 | 1 | 0 | 38889.4987 | 1 | 0 | 871.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4991 | 1 | 0 | 38889.4991 | 1 | 0 | 909 | 1010 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4995 | 2 | 0 | 38889.4995 | 1 | 0 | 946.5 | 1047.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5 | 2 | 0 | 38889.5 | 1 | 0 | 984.5 | 1085.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5004 | 2 | 0 | 38889.5004 | 1 | 0 | 1022.5 | 1123.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5008 | 2 | 0 | 38889.5008 | 1 | 0 | 1060.5 | 1161.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5013 | 1 | 0 | 38889.5013 | 1 | 0 | 1097.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5017 | 1 | 0 | 38889.5017 | 1 | 0 | 1135.5 | 1236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5021 | 2 | 0 | 38889.5022 | 1 | 0 | 1173.5 | 1274.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5026 | 2 | 0 | 38889.5026 | 1 | 0 | 1211.5 | 1312.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.503 | 1 | 0 | 38889.503 | 1 | 0 | 1249.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5034 | 2 | 0 | 38889.5035 | 1 | 0 | 1286.5 | 1387.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5039 | 2 | 0 | 38889.5039 | 1 | 0 | 1324.5 | 1425.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5043 | 2 | 0 | 38889.5043 | 1 | 0 | 1362.5 | 1463.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5048 | 2 | 0 | 38889.5048 | 1 | 0 | 1400.5 | 1501.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5052 | 1 | 0 | 38889.5052 | 1 | 0 | 1438.5 | 1539.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5056 | 1 | 0 | 38889.5056 | 1 | 0 | 1475.5 | 1576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5061 | 1 | 0 | 38889.5061 | 1 | 0 | 1513.5 | 1614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5065 | 1 | 0 | 38889.5065 | 1 | 0 | 1551.5 | 1652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.507 | 1 | 0 | 38889.507 | 1 | 0 | 1589.5 | 1690.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5074 | 2 | 0 | 38889.5074 | 1 | 0 | 1627 | 1728 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5078 | 2 | 0 | 38889.5078 | 1 | 0 | 1664.5 | 1765.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5083 | 1025 | 1069 | 38889.5083 | 1056 | 1146 | 1702.5 | 1803.5 | 62.5763 | 65.2625 | 64.4689 | 69.9634 | 0.62576 | 0.65263 | 0.64469 | 0.69963 | 0.026862 | 0.054945 | 150.9324 | 157.9338 | 1.0894
38889.5087 | 935 | 913 | 38889.5087 | 1025 | 998 | 1740.5 | 1841.5 | 57.0818 | 55.7387 | 62.5763 | 60.928 | 0.57082 | 0.55739 | 0.62576 | 0.60928 | 0.013431 | 0.016484 | 51855.0325 | 4627.8828 | 28.4134
38889.5091 | 992 | 966 | 38889.5092 | 1196 | 950 | 1778.5 | 1879.5 | 60.5617 | 58.9744 | 73.0159 | 57.9976 | 0.60562 | 0.58974 | 0.73016 | 0.57998 | 0.015873 | 0.15018 | 51.5908 | 44.995 | 4.9799
38889.5096 | 1138 | 1186 | 38889.5096 | 1065 | 938 | 1816 | 1917 | 69.475 | 72.4054 | 65.0183 | 57.265 | 0.69475 | 0.72405 | 0.65018 | 0.57265 | 0.029304 | 0.077534 | 90.3411 | 115.0044 | 9.5153
38889.51 | 1142 | 1114 | 38889.51 | 984 | 945 | 1853.5 | 1954.5 | 69.7192 | 68.0098 | 60.0733 | 57.6923 | 0.69719 | 0.6801 | 0.60073 | 0.57692 | 0.017094 | 0.02381 | 368.2023 | 472.5963 | 10.5933
38889.5105 | 1056 | 1030 | 38889.5105 | 1024 | 1069 | 1891.5 | 1992.5 | 64.4689 | 62.8816 | 62.5153 | 65.2625 | 0.64469 | 0.62882 | 0.62515 | 0.65263 | 0.015873 | 0.027473 | 277.4859 | 290.2002 | 1.951
38889.5109 | 985 | 960 | 38889.5109 | 996 | 970 | 1929.5 | 2030.5 | 60.1343 | 58.6081 | 60.8059 | 59.2186 | 0.60134 | 0.58608 | 0.60806 | 0.59219 | 0.015263 | 0.015873 | 11088.2111 | 6474.7387 | 17.2359
38889.5113 | 1055 | 1030 | 38889.5113 | 1203 | 1187 | 1967.5 | 2068.5 | 64.4078 | 62.8816 | 73.4432 | 72.4664 | 0.64408 | 0.62882 | 0.73443 | 0.72466 | 0.015263 | 0.009768 | 4143.061 | 191750.1888 | 2.719
38889.5118 | 1125 | 1183 | 38889.5118 | 984 | 959 | 2004.5 | 2105.5 | 68.6813 | 72.2222 | 60.0733 | 58.547 | 0.68681 | 0.72222 | 0.60073 | 0.58547 | 0.035409 | 0.015263 | 52.9202 | 65.3952 | 6.5167
38889.5122 | 1156 | 1130 | 38889.5122 | 995 | 1107 | 2042.5 | 2143.5 | 70.5739 | 68.9866 | 60.7448 | 67.5824 | 0.70574 | 0.68987 | 0.60745 | 0.67582 | 0.015873 | 0.068376 | 185.5983 | 230.7815 | 10.6801
38889.5126 | 1143 | 1115 | 38889.5127 | 1090 | 1142 | 2080.5 | 2181.5 | 69.7802 | 68.0708 | 66.5446 | 69.7192 | 0.6978 | 0.68071 | 0.66545 | 0.69719 | 0.017094 | 0.031746 | 957.8181 | 1521.6871 | 12.2009
38889.5131 | 1095 | 1149 | 38889.5131 | 1197 | 1139 | 2118.5 | 2219.5 | 66.8498 | 70.1465 | 73.0769 | 69.536 | 0.6685 | 0.70147 | 0.73077 | 0.69536 | 0.032967 | 0.035409 | 2190.0569 | 15286.8256 | 11.3254
38889.5135 | 1013 | 1117 | 38889.5135 | 953 | 928 | 2156.5 | 2257.5 | 61.8437 | 68.1929 | 58.1807 | 56.6545 | 0.61844 | 0.68193 | 0.58181 | 0.56654 | 0.063492 | 0.015263 | 258.2795 | 346.999 | 1.1801

## C3-7
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 158.0818 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38889.4877 | 1 | 0 | 38889.4877 | 1 | 0 | -75.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4881 | 1 | 0 | 38889.4881 | 1 | 0 | -37.5 | 63.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4886 | 1 | 0 | 38889.4886 | 1 | 0 | 0.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.489 | 1 | 0 | 38889.489 | 1 | 0 | 37.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4894 | 1 | 0 | 38889.4894 | 1 | 0 | 75.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4899 | 1 | 0 | 38889.4899 | 1 | 0 | 113.5 | 214.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4903 | 1 | 0 | 38889.4903 | 1 | 0 | 151.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4908 | 1 | 0 | 38889.4908 | 1 | 0 | 189.5 | 290.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4912 | 1 | 0 | 38889.4912 | 1 | 0 | 226.5 | 327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4916 | 1 | 0 | 38889.4916 | 1 | 0 | 264.5 | 365.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4921 | 1 | 0 | 38889.4921 | 1 | 0 | 302.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4925 | 1 | 0 | 38889.4925 | 1 | 0 | 340.5 | 441.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4929 | 1 | 0 | 38889.4929 | 1 | 0 | 378 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4934 | 1 | 0 | 38889.4934 | 1 | 0 | 415.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4938 | 1 | 0 | 38889.4938 | 1 | 0 | 453.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4942 | 1 | 0 | 38889.4943 | 1 | 0 | 491.5 | 592.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4947 | 1 | 0 | 38889.4947 | 1 | 0 | 529.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4951 | 1 | 0 | 38889.4951 | 1 | 0 | 566.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4956 | 1 | 0 | 38889.4956 | 1 | 0 | 604.5 | 705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.496 | 1 | 0 | 38889.496 | 1 | 0 | 642.5 | 743.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4964 | 1 | 0 | 38889.4964 | 1 | 0 | 680.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4969 | 1 | 0 | 38889.4969 | 1 | 0 | 718.5 | 819.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4973 | 1 | 0 | 38889.4973 | 1 | 0 | 756 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4977 | 1 | 0 | 38889.4978 | 1 | 0 | 793.5 | 894.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4982 | 1 | 0 | 38889.4982 | 1 | 0 | 831.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4986 | 1 | 0 | 38889.4986 | 1 | 0 | 869.5 | 970.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38889.4991 | 1 | 0 | 38889.4991 | 2564 | 0 | 907.5 | 1008.5 | 0.06105 | 0 | 156.5324 | 0 | 0.0006105 | 0 | 1.5653 | 0 | 0.0006105 | 1.5653 | 258838 | 0.98986 | 258837.9994
38889.4995 | 1 | 0 | 38889.4995 | 2479 | 0 | 945 | 1046 | 0.06105 | 0 | 151.3431 | 0 | 0.0006105 | 0 | 1.5134 | 0 | 0.0006105 | 1.5134 | 258838 | 4.4526 | 258837.9994
38889.4999 | 1 | 0 | 38889.4999 | 2091 | 0 | 982.5 | 1083.5 | 0.06105 | 0 | 127.6557 | 0 | 0.0006105 | 0 | 1.2766 | 0 | 0.0006105 | 1.2766 | 258838 | 23.8345 | 258837.9994
38889.5004 | 1 | 0 | 38889.5004 | 2540 | 0 | 1020.5 | 1121.5 | 0.06105 | 0 | 155.0672 | 0 | 0.0006105 | 0 | 1.5507 | 0 | 0.0006105 | 1.5507 | 258838 | 1.9441 | 258837.9994
38889.5008 | 1 | 0 | 38889.5008 | 2269 | 0 | 1058.5 | 1159.5 | 0.06105 | 0 | 138.5226 | 0 | 0.0006105 | 0 | 1.3852 | 0 | 0.0006105 | 1.3852 | 258838 | 14.1199 | 258837.9994
38889.5013 | 1 | 0 | 38889.5013 | 2303 | 0 | 1096.5 | 1197.5 | 0.06105 | 0 | 140.5983 | 0 | 0.0006105 | 0 | 1.406 | 0 | 0.0006105 | 1.406 | 258838 | 12.4351 | 258837.9994
38889.5017 | 1 | 1 | 38889.5017 | 2378 | 0 | 1133.5 | 1234.5 | 0.06105 | 0.06105 | 145.177 | 0 | 0.0006105 | 0.0006105 | 1.4518 | 0 | 0 | 1.4518 | 23008.0641 | 8.889 | 21121.6733
38889.5021 | 1 | 0 | 38889.5021 | 2107 | 0 | 1171.5 | 1272.5 | 0.06105 | 0 | 128.6325 | 0 | 0.0006105 | 0 | 1.2863 | 0 | 0.0006105 | 1.2863 | 258838 | 22.8942 | 258837.9994
38889.5026 | 1 | 0 | 38889.5026 | 2151 | 0 | 1209.5 | 1310.5 | 0.06105 | 0 | 131.3187 | 0 | 0.0006105 | 0 | 1.3132 | 0 | 0.0006105 | 1.3132 | 258838 | 20.3803 | 258837.9994
38889.503 | 1 | 0 | 38889.503 | 2573 | 0 | 1247.5 | 1348.5 | 0.06105 | 0 | 157.0818 | 0 | 0.0006105 | 0 | 1.5708 | 0 | 0.0006105 | 1.5708 | 258838 | 0.63661 | 258837.9994
38889.5034 | 1 | 0 | 38889.5034 | 2325 | 0 | 1285 | 1386 | 0.06105 | 0 | 141.9414 | 0 | 0.0006105 | 0 | 1.4194 | 0 | 0.0006105 | 1.4194 | 258838 | 11.3712 | 258837.9994
38889.5039 | 1 | 0 | 38889.5039 | 2538 | 0 | 1322.5 | 1423.5 | 0.06105 | 0 | 154.9451 | 0 | 0.0006105 | 0 | 1.5495 | 0 | 0.0006105 | 1.5495 | 258838 | 2.0244 | 258837.9994
38889.5043 | 1 | 0 | 38889.5043 | 1984 | 0 | 1360.5 | 1461.5 | 0.06105 | 0 | 121.1233 | 0 | 0.0006105 | 0 | 1.2112 | 0 | 0.0006105 | 1.2112 | 258838 | 30.5131 | 258837.9994
38889.5047 | 1 | 0 | 38889.5048 | 2124 | 0 | 1398.5 | 1499.5 | 0.06105 | 0 | 129.6703 | 0 | 0.0006105 | 0 | 1.2967 | 0 | 0.0006105 | 1.2967 | 258838 | 21.9105 | 258837.9994
38889.5052 | 1 | 0 | 38889.5052 | 2014 | 0 | 1436.5 | 1537.5 | 0.06105 | 0 | 122.9548 | 0 | 0.0006105 | 0 | 1.2295 | 0 | 0.0006105 | 1.2295 | 258838 | 28.569 | 258837.9994
38889.5056 | 1 | 0 | 38889.5056 | 2471 | 0 | 1474 | 1575 | 0.06105 | 0 | 150.8547 | 0 | 0.0006105 | 0 | 1.5085 | 0 | 0.0006105 | 1.5085 | 258838 | 4.7908 | 258837.9994
38889.5061 | 1 | 0 | 38889.5061 | 2470 | 0 | 1511.5 | 1612.5 | 0.06105 | 0 | 150.7937 | 0 | 0.0006105 | 0 | 1.5079 | 0 | 0.0006105 | 1.5079 | 258838 | 4.8332 | 258837.9994
38889.5065 | 1 | 0 | 38889.5065 | 2376 | 0 | 1549.5 | 1650.5 | 0.06105 | 0 | 145.0549 | 0 | 0.0006105 | 0 | 1.4505 | 0 | 0.0006105 | 1.4505 | 258838 | 8.9806 | 258837.9994
38889.5069 | 1 | 0 | 38889.5069 | 2480 | 0 | 1587.5 | 1688.5 | 0.06105 | 0 | 151.4042 | 0 | 0.0006105 | 0 | 1.514 | 0 | 0.0006105 | 1.514 | 258838 | 4.4105 | 258837.9994
38889.5074 | 1 | 0 | 38889.5074 | 2032 | 0 | 1625.5 | 1726.5 | 0.06105 | 0 | 124.0537 | 0 | 0.0006105 | 0 | 1.2405 | 0 | 0.0006105 | 1.2405 | 258838 | 27.4301 | 258837.9994
38889.5078 | 1 | 0 | 38889.5078 | 2081 | 0 | 1663 | 1764 | 0.06105 | 0 | 127.0452 | 0 | 0.0006105 | 0 | 1.2705 | 0 | 0.0006105 | 1.2705 | 258838 | 24.4296 | 258837.9994
38889.5082 | 2 | 0 | 38889.5083 | 2497 | 0 | 1700.5 | 1801.5 | 0.1221 | 0 | 152.442 | 0 | 0.001221 | 0 | 1.5244 | 0 | 0.001221 | 1.5244 | 129369 | 3.6996 | 129368.9988
38889.5087 | 1 | 0 | 38889.5087 | 2162 | 0 | 1738.5 | 1839.5 | 0.06105 | 0 | 131.9902 | 0 | 0.0006105 | 0 | 1.3199 | 0 | 0.0006105 | 1.3199 | 258838 | 19.7678 | 258837.9994
38889.5091 | 1 | 0 | 38889.5091 | 2536 | 0 | 1776.5 | 1877.5 | 0.06105 | 0 | 154.823 | 0 | 0.0006105 | 0 | 1.5482 | 0 | 0.0006105 | 1.5482 | 258838 | 2.1049 | 258837.9994
38889.5096 | 1 | 0 | 38889.5096 | 2250 | 0 | 1814.5 | 1915.5 | 0.06105 | 0 | 137.3626 | 0 | 0.0006105 | 0 | 1.3736 | 0 | 0.0006105 | 1.3736 | 258838 | 15.0836 | 258837.9994
38889.51 | 1 | 0 | 38889.51 | 1961 | 0 | 1852 | 1953 | 0.06105 | 0 | 119.7192 | 0 | 0.0006105 | 0 | 1.1972 | 0 | 0.0006105 | 1.1972 | 258838 | 32.0439 | 258837.9994
38889.5104 | 1 | 0 | 38889.5104 | 1997 | 0 | 1889.5 | 1990.5 | 0.06105 | 0 | 121.917 | 0 | 0.0006105 | 0 | 1.2192 | 0 | 0.0006105 | 1.2192 | 258838 | 29.6635 | 258837.9994
38889.5109 | 1 | 0 | 38889.5109 | 1959 | 0 | 1927.5 | 2028.5 | 0.06105 | 0 | 119.5971 | 0 | 0.0006105 | 0 | 1.196 | 0 | 0.0006105 | 1.196 | 258838 | 32.1787 | 258837.9994
38889.5113 | 1 | 0 | 38889.5113 | 2449 | 0 | 1965.5 | 2066.5 | 0.06105 | 0 | 149.5116 | 0 | 0.0006105 | 0 | 1.4951 | 0 | 0.0006105 | 1.4951 | 258838 | 5.7321 | 258837.9994
38889.5117 | 1 | 0 | 38889.5118 | 2551 | 0 | 2003.5 | 2104.5 | 0.06105 | 0 | 155.7387 | 0 | 0.0006105 | 0 | 1.5574 | 0 | 0.0006105 | 1.5574 | 258838 | 1.5045 | 258837.9994
38889.5122 | 1 | 0 | 38889.5122 | 2328 | 0 | 2041 | 2142 | 0.06105 | 0 | 142.1245 | 0 | 0.0006105 | 0 | 1.4212 | 0 | 0.0006105 | 1.4212 | 258838 | 11.2277 | 258837.9994
38889.5126 | 1 | 0 | 38889.5126 | 2013 | 0 | 2078.5 | 2179.5 | 0.06105 | 0 | 122.8938 | 0 | 0.0006105 | 0 | 1.2289 | 0 | 0.0006105 | 1.2289 | 258838 | 28.6329 | 258837.9994
38889.5131 | 1 | 0 | 38889.5131 | 1868 | 0 | 2116.5 | 2217.5 | 0.06105 | 0 | 114.0415 | 0 | 0.0006105 | 0 | 1.1404 | 0 | 0.0006105 | 1.1404 | 258838 | 38.6178 | 258837.9994
38889.5135 | 1 | 0 | 38889.5135 | 1934 | 0 | 2154.5 | 2255.5 | 0.06105 | 0 | 118.0708 | 0 | 0.0006105 | 0 | 1.1807 | 0 | 0.0006105 | 1.1807 | 258838 | 33.8873 | 258837.9994

## C3-6
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38889.4877 | 1 | 0 | 38889.4877 | 1 | 0 | -77.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4881 | 1 | 0 | 38889.4881 | 1 | 0 | -39.5 | 61.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4885 | 1 | 0 | 38889.4886 | 1 | 0 | -1.5 | 99.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.489 | 2 | 0 | 38889.489 | 1 | 0 | 36 | 137 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4894 | 1 | 0 | 38889.4894 | 1 | 0 | 73.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4898 | 1 | 0 | 38889.4899 | 1 | 0 | 111.5 | 212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4903 | 1 | 0 | 38889.4903 | 1 | 0 | 149.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4907 | 1 | 0 | 38889.4907 | 1 | 0 | 187.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4912 | 1 | 0 | 38889.4912 | 1 | 0 | 225 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4916 | 1 | 0 | 38889.4916 | 1 | 0 | 262.5 | 363.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.492 | 1 | 0 | 38889.492 | 1 | 0 | 300.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4925 | 1 | 0 | 38889.4925 | 1 | 0 | 338.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4929 | 1 | 0 | 38889.4929 | 1 | 0 | 376.5 | 477.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4933 | 1 | 0 | 38889.4934 | 1 | 0 | 413.5 | 514.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4938 | 1 | 0 | 38889.4938 | 1 | 0 | 451.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4942 | 1 | 0 | 38889.4942 | 1 | 0 | 489.5 | 590.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4947 | 1 | 0 | 38889.4947 | 1 | 0 | 527.5 | 628.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4951 | 1 | 0 | 38889.4951 | 1 | 0 | 565.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4955 | 1 | 0 | 38889.4955 | 1 | 0 | 603 | 704 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.496 | 1 | 0 | 38889.496 | 1 | 0 | 640.5 | 741.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4964 | 1 | 0 | 38889.4964 | 1 | 0 | 678.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4969 | 1 | 0 | 38889.4969 | 1 | 0 | 716.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4973 | 1 | 0 | 38889.4973 | 1 | 0 | 754.5 | 855.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4977 | 1 | 0 | 38889.4977 | 1 | 0 | 792 | 893 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4982 | 1 | 0 | 38889.4982 | 1 | 0 | 829.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4986 | 1 | 0 | 38889.4986 | 1 | 0 | 867.5 | 968.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.499 | 1 | 0 | 38889.4991 | 1 | 0 | 905.5 | 1006.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4995 | 1 | 0 | 38889.4995 | 1 | 0 | 943.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4999 | 1 | 0 | 38889.4999 | 1 | 0 | 980.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5003 | 1 | 0 | 38889.5004 | 1 | 0 | 1018.5 | 1119.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5008 | 1 | 0 | 38889.5008 | 1 | 0 | 1056.5 | 1157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5012 | 1 | 0 | 38889.5012 | 1 | 0 | 1094.5 | 1195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5017 | 1 | 0 | 38889.5017 | 1 | 0 | 1132.5 | 1233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5021 | 1 | 0 | 38889.5021 | 1 | 0 | 1170 | 1271 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5025 | 1 | 0 | 38889.5025 | 1 | 0 | 1207.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.503 | 1 | 0 | 38889.503 | 1 | 0 | 1245.5 | 1346.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5034 | 1 | 0 | 38889.5034 | 1 | 0 | 1283.5 | 1384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5039 | 1 | 0 | 38889.5039 | 1 | 0 | 1321.5 | 1422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5043 | 1 | 0 | 38889.5043 | 1 | 0 | 1358.5 | 1459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5047 | 1 | 0 | 38889.5047 | 1 | 0 | 1396.5 | 1497.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5052 | 1 | 0 | 38889.5052 | 1 | 0 | 1434.5 | 1535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5056 | 1 | 0 | 38889.5056 | 1 | 0 | 1472.5 | 1573.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.506 | 1 | 0 | 38889.5061 | 1 | 0 | 1510.5 | 1611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5065 | 1 | 0 | 38889.5065 | 1 | 0 | 1547.5 | 1648.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5069 | 1 | 0 | 38889.5069 | 1 | 0 | 1585.5 | 1686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5073 | 1 | 0 | 38889.5074 | 1 | 0 | 1623.5 | 1724.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5078 | 1 | 0 | 38889.5078 | 1 | 0 | 1661.5 | 1762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5082 | 1 | 0 | 38889.5082 | 1 | 0 | 1699 | 1800 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5087 | 2 | 0 | 38889.5087 | 1 | 0 | 1736.5 | 1837.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5091 | 1 | 0 | 38889.5091 | 1 | 0 | 1774.5 | 1875.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5095 | 1 | 0 | 38889.5095 | 2 | 0 | 1812.5 | 1913.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.51 | 1 | 0 | 38889.51 | 1 | 0 | 1850.5 | 1951.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5104 | 1 | 0 | 38889.5104 | 1 | 0 | 1888 | 1989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5108 | 1 | 0 | 38889.5109 | 1 | 0 | 1925.5 | 2026.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5113 | 1 | 0 | 38889.5113 | 1 | 0 | 1963.5 | 2064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5117 | 1 | 0 | 38889.5117 | 1 | 0 | 2001.5 | 2102.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5122 | 1 | 0 | 38889.5122 | 1 | 0 | 2039.5 | 2140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5126 | 1 | 0 | 38889.5126 | 1 | 0 | 2076.5 | 2177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.513 | 1 | 0 | 38889.513 | 1 | 0 | 2114.5 | 2215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5135 | 1 | 0 | 38889.5135 | 1 | 0 | 2152.5 | 2253.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-5
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38889.4876 | 1 | 0 | 38889.4877 | 1 | 0 | -79.5 | 21.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4881 | 1 | 0 | 38889.4881 | 1 | 0 | -41.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4885 | 1 | 0 | 38889.4885 | 1 | 0 | -3.5 | 97.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.489 | 1 | 0 | 38889.489 | 1 | 0 | 34.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4894 | 1 | 0 | 38889.4894 | 1 | 0 | 72.5 | 173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4898 | 1 | 0 | 38889.4898 | 1 | 0 | 109.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4903 | 1 | 0 | 38889.4903 | 1 | 0 | 147.5 | 248.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4907 | 1 | 0 | 38889.4907 | 1 | 0 | 185.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4911 | 1 | 0 | 38889.4912 | 1 | 0 | 223.5 | 324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4916 | 1 | 0 | 38889.4916 | 1 | 0 | 261 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.492 | 1 | 0 | 38889.492 | 1 | 0 | 298.5 | 399.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4925 | 1 | 0 | 38889.4925 | 1 | 0 | 336.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4929 | 1 | 0 | 38889.4929 | 1 | 0 | 374.5 | 475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4933 | 1 | 0 | 38889.4933 | 1 | 0 | 412.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4938 | 1 | 0 | 38889.4938 | 1 | 0 | 449.5 | 550.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4942 | 1 | 0 | 38889.4942 | 1 | 0 | 487.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4946 | 1 | 0 | 38889.4947 | 1 | 0 | 525.5 | 626.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4951 | 1 | 0 | 38889.4951 | 1 | 0 | 563.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4955 | 1 | 0 | 38889.4955 | 1 | 0 | 601.5 | 702.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.496 | 1 | 0 | 38889.496 | 1 | 0 | 639 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4964 | 1 | 0 | 38889.4964 | 2 | 0 | 676.5 | 777.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.4968 | 1 | 0 | 38889.4968 | 1 | 0 | 714.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4973 | 1 | 0 | 38889.4973 | 1 | 0 | 752.5 | 853.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4977 | 1 | 0 | 38889.4977 | 1 | 0 | 790.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4981 | 1 | 0 | 38889.4981 | 1 | 0 | 828 | 929 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4986 | 1 | 0 | 38889.4986 | 1 | 0 | 865.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.499 | 1 | 0 | 38889.499 | 1 | 0 | 903.5 | 1004.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4995 | 1 | 0 | 38889.4995 | 1 | 0 | 941.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4999 | 1 | 0 | 38889.4999 | 1 | 0 | 979.5 | 1080.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5003 | 1 | 0 | 38889.5003 | 1 | 0 | 1017 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5008 | 1 | 0 | 38889.5008 | 2 | 0 | 1054.5 | 1155.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5012 | 1 | 0 | 38889.5012 | 1 | 0 | 1092.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5016 | 1 | 0 | 38889.5017 | 1 | 0 | 1130.5 | 1231.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5021 | 1 | 0 | 38889.5021 | 1 | 0 | 1168.5 | 1269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5025 | 1 | 0 | 38889.5025 | 1 | 0 | 1205.5 | 1306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.503 | 1 | 0 | 38889.503 | 1 | 0 | 1243.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5034 | 1 | 0 | 38889.5034 | 2 | 0 | 1281.5 | 1382.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5038 | 1 | 0 | 38889.5038 | 1 | 0 | 1319.5 | 1420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5043 | 1 | 0 | 38889.5043 | 1 | 0 | 1357.5 | 1458.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5047 | 1 | 0 | 38889.5047 | 1 | 0 | 1394.5 | 1495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5051 | 1 | 0 | 38889.5052 | 1 | 0 | 1432.5 | 1533.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5056 | 1 | 0 | 38889.5056 | 1 | 0 | 1470.5 | 1571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.506 | 1 | 0 | 38889.506 | 1 | 0 | 1508.5 | 1609.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5065 | 1 | 0 | 38889.5065 | 1 | 0 | 1546.5 | 1647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5069 | 1 | 0 | 38889.5069 | 1 | 0 | 1583.5 | 1684.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5073 | 1 | 0 | 38889.5073 | 1 | 0 | 1621.5 | 1722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5078 | 1 | 0 | 38889.5078 | 1 | 0 | 1659.5 | 1760.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5082 | 1 | 0 | 38889.5082 | 1 | 0 | 1697.5 | 1798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5086 | 1 | 0 | 38889.5086 | 1 | 0 | 1735 | 1836 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5091 | 1 | 0 | 38889.5091 | 1 | 0 | 1772.5 | 1873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5095 | 1 | 0 | 38889.5095 | 1 | 0 | 1810.5 | 1911.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.51 | 1 | 0 | 38889.51 | 1 | 0 | 1848.5 | 1949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5104 | 1 | 0 | 38889.5104 | 1 | 0 | 1886.5 | 1987.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5108 | 1 | 0 | 38889.5108 | 1 | 0 | 1924 | 2025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5113 | 1 | 0 | 38889.5113 | 1 | 0 | 1961.5 | 2062.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5117 | 1 | 0 | 38889.5117 | 1 | 0 | 1999.5 | 2100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5121 | 1 | 0 | 38889.5122 | 1 | 0 | 2037.5 | 2138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5126 | 1 | 0 | 38889.5126 | 1 | 0 | 2075.5 | 2176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.513 | 1 | 0 | 38889.513 | 1 | 0 | 2112.5 | 2213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5134 | 1 | 0 | 38889.5135 | 1 | 0 | 2150.5 | 2251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-4
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38889.4876 | 1 | 0 | 38889.4876 | 1 | 0 | -80.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4881 | 1 | 0 | 38889.4881 | 1 | 0 | -43.5 | 57.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4885 | 1 | 0 | 38889.4885 | 1 | 0 | -5.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4889 | 1 | 0 | 38889.4889 | 1 | 0 | 32.5 | 133.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4894 | 1 | 0 | 38889.4894 | 1 | 0 | 70.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4898 | 1 | 0 | 38889.4898 | 1 | 0 | 108 | 209 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4902 | 1 | 0 | 38889.4903 | 1 | 0 | 145.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4907 | 1 | 0 | 38889.4907 | 1 | 0 | 183.5 | 284.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4911 | 1 | 0 | 38889.4911 | 1 | 0 | 221.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4916 | 1 | 0 | 38889.4916 | 1 | 0 | 259.5 | 360.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.492 | 1 | 0 | 38889.492 | 1 | 0 | 297.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4924 | 1 | 0 | 38889.4924 | 1 | 0 | 334.5 | 435.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4929 | 1 | 0 | 38889.4929 | 1 | 0 | 372.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4933 | 1 | 0 | 38889.4933 | 1 | 0 | 410.5 | 511.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4938 | 1 | 0 | 38889.4938 | 1 | 0 | 448.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4942 | 1 | 0 | 38889.4942 | 1 | 0 | 486 | 587 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4946 | 1 | 0 | 38889.4946 | 1 | 0 | 523.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4951 | 1 | 0 | 38889.4951 | 1 | 0 | 561.5 | 662.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4955 | 1 | 0 | 38889.4955 | 1 | 0 | 599.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4959 | 1 | 0 | 38889.4959 | 1 | 0 | 637.5 | 738.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4964 | 1 | 0 | 38889.4964 | 1 | 0 | 674.5 | 775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4968 | 1 | 0 | 38889.4968 | 1 | 0 | 712.5 | 813.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4972 | 1 | 0 | 38889.4973 | 1 | 0 | 750.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4977 | 1 | 0 | 38889.4977 | 1 | 0 | 788.5 | 889.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4981 | 1 | 0 | 38889.4981 | 1 | 0 | 826.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4986 | 1 | 0 | 38889.4986 | 1 | 0 | 863.5 | 964.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.499 | 1 | 0 | 38889.499 | 1 | 0 | 901.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4994 | 2 | 0 | 38889.4994 | 1 | 0 | 939.5 | 1040.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4999 | 2 | 0 | 38889.4999 | 2 | 0 | 977.5 | 1078.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38889.5003 | 2 | 0 | 38889.5003 | 1 | 0 | 1015.5 | 1116.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5008 | 2 | 0 | 38889.5008 | 1 | 0 | 1053 | 1154 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5012 | 2 | 0 | 38889.5012 | 1 | 0 | 1090.5 | 1191.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5016 | 2 | 0 | 38889.5016 | 1 | 0 | 1128.5 | 1229.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5021 | 2 | 0 | 38889.5021 | 1 | 0 | 1166.5 | 1267.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5025 | 2 | 0 | 38889.5025 | 1 | 0 | 1204.5 | 1305.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5029 | 2 | 0 | 38889.5029 | 1 | 0 | 1241.5 | 1342.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5034 | 2 | 0 | 38889.5034 | 2 | 0 | 1279.5 | 1380.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38889.5038 | 2 | 0 | 38889.5038 | 1 | 0 | 1317.5 | 1418.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5042 | 1 | 0 | 38889.5043 | 1 | 0 | 1355.5 | 1456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5047 | 1 | 0 | 38889.5047 | 1 | 0 | 1393.5 | 1494.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5051 | 1 | 0 | 38889.5051 | 1 | 0 | 1430.5 | 1531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5056 | 1 | 0 | 38889.5056 | 1 | 0 | 1468.5 | 1569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.506 | 2 | 0 | 38889.506 | 1 | 0 | 1506.5 | 1607.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5064 | 2 | 0 | 38889.5064 | 1 | 0 | 1544.5 | 1645.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5069 | 2 | 0 | 38889.5069 | 1 | 0 | 1582.5 | 1683.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5073 | 2 | 0 | 38889.5073 | 2 | 0 | 1619.5 | 1720.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38889.5077 | 2 | 0 | 38889.5078 | 1 | 0 | 1657.5 | 1758.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5082 | 2 | 0 | 38889.5082 | 1 | 0 | 1695.5 | 1796.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5086 | 1 | 0 | 38889.5086 | 1 | 0 | 1733.5 | 1834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5091 | 1 | 0 | 38889.5091 | 1 | 0 | 1771.5 | 1872.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5099 | 2 | 0 | 38889.5099 | 1 | 0 | 1846.5 | 1947.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5104 | 2 | 0 | 38889.5104 | 1 | 0 | 1884.5 | 1985.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5108 | 2 | 0 | 38889.5108 | 1 | 0 | 1922.5 | 2023.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5112 | 2 | 0 | 38889.5113 | 1 | 0 | 1959.5 | 2060.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5117 | 2 | 0 | 38889.5117 | 1 | 0 | 1997.5 | 2098.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5121 | 1 | 0 | 38889.5121 | 1 | 0 | 2035.5 | 2136.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5126 | 1 | 0 | 38889.5126 | 1 | 0 | 2073.5 | 2174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.513 | 2 | 0 | 38889.513 | 1 | 0 | 2111.5 | 2212.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5134 | 2 | 0 | 38889.5134 | 1 | 0 | 2148.5 | 2249.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## C2-7
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 157.6545 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38889.4876 | 1 | 0 | 38889.4876 | 1 | 0 | -82.5 | 18.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.488 | 1 | 0 | 38889.4881 | 1 | 0 | -44.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4885 | 2 | 0 | 38889.4885 | 1 | 0 | -7.5 | 93.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129019 | 258138 | 129018.9988
38889.4889 | 1 | 0 | 38889.4889 | 1 | 0 | 30.5 | 131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4894 | 1 | 0 | 38889.4894 | 1 | 0 | 68.5 | 169.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4898 | 1 | 0 | 38889.4898 | 1 | 0 | 106.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4902 | 1 | 0 | 38889.4902 | 1 | 0 | 144 | 245 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4907 | 1 | 0 | 38889.4907 | 1 | 0 | 181.5 | 282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4911 | 1 | 0 | 38889.4911 | 1 | 0 | 219.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4915 | 1 | 0 | 38889.4916 | 1 | 0 | 257.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.492 | 1 | 0 | 38889.492 | 1 | 0 | 295.5 | 396.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4924 | 1 | 0 | 38889.4924 | 1 | 0 | 333.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4928 | 1 | 0 | 38889.4929 | 1 | 0 | 370.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4933 | 1 | 0 | 38889.4933 | 1 | 0 | 408.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4937 | 1 | 0 | 38889.4937 | 1 | 0 | 446.5 | 547.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4942 | 1 | 0 | 38889.4942 | 1 | 0 | 484.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4946 | 1 | 0 | 38889.4946 | 1 | 0 | 522 | 623 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.495 | 1 | 0 | 38889.495 | 1 | 0 | 559.5 | 660.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4955 | 1 | 0 | 38889.4955 | 1 | 1 | 597.5 | 698.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 258138 | 258138 | 258137.9994
38889.4959 | 1 | 0 | 38889.4959 | 1 | 0 | 635.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4964 | 1 | 0 | 38889.4964 | 1 | 0 | 673.5 | 774.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4968 | 1 | 0 | 38889.4968 | 1 | 0 | 711 | 812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4972 | 1 | 0 | 38889.4972 | 1 | 0 | 748.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4977 | 1 | 0 | 38889.4977 | 1 | 0 | 786.5 | 887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4981 | 1 | 0 | 38889.4981 | 1 | 0 | 824.5 | 925.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.4985 | 1 | 0 | 38889.4986 | 1 | 0 | 862.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38889.499 | 1 | 0 | 38889.499 | 2220 | 0 | 899.5 | 1000.5 | 0.06105 | 0 | 135.5311 | 0 | 0.0006105 | 0 | 1.3553 | 0 | 0.0006105 | 1.3553 | 258138 | 16.3234 | 258137.9994
38889.4994 | 1 | 0 | 38889.4994 | 2044 | 1 | 937.5 | 1038.5 | 0.06105 | 0 | 124.7863 | 0.06105 | 0.0006105 | 0 | 1.2479 | 0.0006105 | 0.0006105 | 1.2473 | 258138 | 26.4014 | 258137.9994
38889.4998 | 2 | 0 | 38889.4999 | 2429 | 0 | 975.5 | 1076.5 | 0.1221 | 0 | 148.2906 | 0 | 0.001221 | 0 | 1.4829 | 0 | 0.001221 | 1.4829 | 129019 | 6.3145 | 129018.9988
38889.5003 | 1 | 0 | 38889.5003 | 2193 | 0 | 1013.5 | 1114.5 | 0.06105 | 0 | 133.8828 | 0 | 0.0006105 | 0 | 1.3388 | 0 | 0.0006105 | 1.3388 | 258138 | 17.7556 | 258137.9994
38889.5007 | 1 | 0 | 38889.5007 | 2367 | 0 | 1051.5 | 1152.5 | 0.06105 | 0 | 144.5055 | 0 | 0.0006105 | 0 | 1.4451 | 0 | 0.0006105 | 1.4451 | 258138 | 9.0993 | 258137.9994
38889.5012 | 1 | 0 | 38889.5012 | 2298 | 0 | 1088.5 | 1189.5 | 0.06105 | 0 | 140.293 | 0 | 0.0006105 | 0 | 1.4029 | 0 | 0.0006105 | 1.4029 | 258138 | 12.3751 | 258137.9994
38889.5016 | 1 | 0 | 38889.5016 | 2125 | 0 | 1126.5 | 1227.5 | 0.06105 | 0 | 129.7314 | 0 | 0.0006105 | 0 | 1.2973 | 0 | 0.0006105 | 1.2973 | 258138 | 21.5238 | 258137.9994
38889.502 | 1 | 0 | 38889.502 | 2396 | 0 | 1164.5 | 1265.5 | 0.06105 | 0 | 146.2759 | 0 | 0.0006105 | 0 | 1.4628 | 0 | 0.0006105 | 1.4628 | 258138 | 7.7788 | 258137.9994
38889.5025 | 1 | 0 | 38889.5025 | 2455 | 0 | 1202.5 | 1303.5 | 0.06105 | 0 | 149.8779 | 0 | 0.0006105 | 0 | 1.4988 | 0 | 0.0006105 | 1.4988 | 258138 | 5.1886 | 258137.9994
38889.5029 | 1 | 0 | 38889.5029 | 2018 | 0 | 1240.5 | 1341.5 | 0.06105 | 0 | 123.199 | 0 | 0.0006105 | 0 | 1.232 | 0 | 0.0006105 | 1.232 | 258138 | 27.9673 | 258137.9994
38889.5033 | 1 | 1 | 38889.5034 | 1991 | 0 | 1277.5 | 1378.5 | 0.06105 | 0.06105 | 121.5507 | 0 | 0.0006105 | 0.0006105 | 1.2155 | 0 | 0 | 1.2155 | 76673.8576 | 29.7027 | 59092.1988
38889.5038 | 1 | 0 | 38889.5038 | 2171 | 0 | 1315.5 | 1416.5 | 0.06105 | 0 | 132.5397 | 0 | 0.0006105 | 0 | 1.3254 | 0 | 0.0006105 | 1.3254 | 258138 | 18.9489 | 258137.9994
38889.5042 | 1 | 0 | 38889.5042 | 2311 | 0 | 1353.5 | 1454.5 | 0.06105 | 0 | 141.0867 | 0 | 0.0006105 | 0 | 1.4109 | 0 | 0.0006105 | 1.4109 | 258138 | 11.743 | 258137.9994
38889.5047 | 1 | 0 | 38889.5047 | 2235 | 0 | 1391.5 | 1492.5 | 0.06105 | 0 | 136.4469 | 0 | 0.0006105 | 0 | 1.3645 | 0 | 0.0006105 | 1.3645 | 258138 | 15.5427 | 258137.9994
38889.5051 | 1 | 0 | 38889.5051 | 1985 | 0 | 1429.5 | 1530.5 | 0.06105 | 0 | 121.1844 | 0 | 0.0006105 | 0 | 1.2118 | 0 | 0.0006105 | 1.2118 | 258138 | 30.0947 | 258137.9994
38889.5055 | 1 | 0 | 38889.5055 | 2566 | 0 | 1466.5 | 1567.5 | 0.06105 | 0 | 156.6545 | 0 | 0.0006105 | 0 | 1.5665 | 0 | 0.0006105 | 1.5665 | 258138 | 0.63835 | 258137.9994
38889.506 | 1 | 0 | 38889.506 | 2219 | 0 | 1504.5 | 1605.5 | 0.06105 | 0 | 135.4701 | 0 | 0.0006105 | 0 | 1.3547 | 0 | 0.0006105 | 1.3547 | 258138 | 16.3758 | 258137.9994
38889.5064 | 1 | 0 | 38889.5064 | 2105 | 0 | 1542.5 | 1643.5 | 0.06105 | 0 | 128.5104 | 0 | 0.0006105 | 0 | 1.2851 | 0 | 0.0006105 | 1.2851 | 258138 | 22.6784 | 258137.9994
38889.5069 | 1 | 0 | 38889.5069 | 2448 | 0 | 1580.5 | 1681.5 | 0.06105 | 0 | 149.4505 | 0 | 0.0006105 | 0 | 1.4945 | 0 | 0.0006105 | 1.4945 | 258138 | 5.4894 | 258137.9994
38889.5073 | 1 | 0 | 38889.5073 | 2418 | 0 | 1618 | 1719 | 0.06105 | 0 | 147.619 | 0 | 0.0006105 | 0 | 1.4762 | 0 | 0.0006105 | 1.4762 | 258138 | 6.7982 | 258137.9994
38889.5077 | 1 | 0 | 38889.5077 | 1988 | 0 | 1655.5 | 1756.5 | 0.06105 | 0 | 121.3675 | 0 | 0.0006105 | 0 | 1.2137 | 0 | 0.0006105 | 1.2137 | 258138 | 29.8984 | 258137.9994
38889.5082 | 1 | 0 | 38889.5082 | 2324 | 0 | 1693.5 | 1794.5 | 0.06105 | 0 | 141.8803 | 0 | 0.0006105 | 0 | 1.4188 | 0 | 0.0006105 | 1.4188 | 258138 | 11.1179 | 258137.9994
38889.5086 | 1 | 0 | 38889.5086 | 2228 | 0 | 1731.5 | 1832.5 | 0.06105 | 0 | 136.0195 | 0 | 0.0006105 | 0 | 1.3602 | 0 | 0.0006105 | 1.3602 | 258138 | 15.9057 | 258137.9994
38889.509 | 1 | 0 | 38889.5091 | 1983 | 0 | 1769.5 | 1870.5 | 0.06105 | 0 | 121.0623 | 0 | 0.0006105 | 0 | 1.2106 | 0 | 0.0006105 | 1.2106 | 258138 | 30.2259 | 258137.9994
38889.5099 | 1 | 0 | 38889.5099 | 2299 | 0 | 1844.5 | 1945.5 | 0.06105 | 0 | 140.3541 | 0 | 0.0006105 | 0 | 1.4035 | 0 | 0.0006105 | 1.4035 | 258138 | 12.3262 | 258137.9994
38889.5103 | 1 | 0 | 38889.5104 | 2054 | 0 | 1882.5 | 1983.5 | 0.06105 | 0 | 125.3968 | 0 | 0.0006105 | 0 | 1.254 | 0 | 0.0006105 | 1.254 | 258138 | 25.7244 | 258137.9994
38889.5108 | 1 | 0 | 38889.5108 | 2514 | 0 | 1920.5 | 2021.5 | 0.06105 | 0 | 153.4799 | 0 | 0.0006105 | 0 | 1.5348 | 0 | 0.0006105 | 1.5348 | 258138 | 2.72 | 258137.9994
38889.5112 | 1 | 0 | 38889.5112 | 1961 | 0 | 1958.5 | 2059.5 | 0.06105 | 0 | 119.7192 | 0 | 0.0006105 | 0 | 1.1972 | 0 | 0.0006105 | 1.1972 | 258138 | 31.6869 | 258137.9994
38889.5117 | 1 | 0 | 38889.5117 | 2329 | 0 | 1995.5 | 2096.5 | 0.06105 | 0 | 142.1856 | 0 | 0.0006105 | 0 | 1.4219 | 0 | 0.0006105 | 1.4219 | 258138 | 10.8793 | 258137.9994
38889.5121 | 1 | 0 | 38889.5121 | 2118 | 0 | 2033.5 | 2134.5 | 0.06105 | 0 | 129.304 | 0 | 0.0006105 | 0 | 1.293 | 0 | 0.0006105 | 1.293 | 258138 | 21.9254 | 258137.9994
38889.5125 | 1 | 0 | 38889.5125 | 2008 | 0 | 2071.5 | 2172.5 | 0.06105 | 0 | 122.5885 | 0 | 0.0006105 | 0 | 1.2259 | 0 | 0.0006105 | 1.2259 | 258138 | 28.6046 | 258137.9994
38889.513 | 1 | 0 | 38889.513 | 1857 | 0 | 2109.5 | 2210.5 | 0.06105 | 0 | 113.37 | 0 | 0.0006105 | 0 | 1.1337 | 0 | 0.0006105 | 1.1337 | 258138 | 39.0619 | 258137.9994
38889.5134 | 1 | 0 | 38889.5134 | 2207 | 0 | 2147.5 | 2248.5 | 0.06105 | 0 | 134.7375 | 0 | 0.0006105 | 0 | 1.3474 | 0 | 0.0006105 | 1.3474 | 258138 | 17.0086 | 258137.9994

## C2-6
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38889.4876 | 1 | 0 | 38889.4876 | 1 | 0 | -84.5 | 16.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.488 | 1 | 0 | 38889.488 | 1 | 0 | -46.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4885 | 1 | 0 | 38889.4885 | 1 | 0 | -8.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4889 | 1 | 0 | 38889.4889 | 1 | 0 | 28.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4893 | 1 | 0 | 38889.4893 | 1 | 0 | 66.5 | 167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4898 | 1 | 0 | 38889.4898 | 1 | 0 | 104.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4902 | 1 | 0 | 38889.4902 | 1 | 0 | 142.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4906 | 1 | 0 | 38889.4907 | 1 | 0 | 180.5 | 281.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4911 | 1 | 0 | 38889.4911 | 1 | 0 | 217.5 | 318.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4915 | 1 | 0 | 38889.4915 | 1 | 0 | 255.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.492 | 1 | 0 | 38889.492 | 1 | 0 | 293.5 | 394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4924 | 1 | 0 | 38889.4924 | 1 | 0 | 331.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4928 | 1 | 0 | 38889.4928 | 1 | 0 | 369 | 470 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4933 | 1 | 0 | 38889.4933 | 1 | 0 | 406.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4937 | 1 | 0 | 38889.4937 | 2 | 0 | 444.5 | 545.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.4941 | 1 | 0 | 38889.4942 | 1 | 0 | 482.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4946 | 1 | 0 | 38889.4946 | 1 | 0 | 520.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.495 | 1 | 0 | 38889.495 | 1 | 0 | 557.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4955 | 1 | 0 | 38889.4955 | 1 | 0 | 595.5 | 696.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4959 | 1 | 0 | 38889.4959 | 1 | 0 | 633.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4963 | 1 | 0 | 38889.4963 | 1 | 0 | 671.5 | 772.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4968 | 1 | 0 | 38889.4968 | 1 | 0 | 709.5 | 810.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4972 | 1 | 0 | 38889.4972 | 1 | 0 | 746.5 | 847.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4976 | 2 | 0 | 38889.4977 | 1 | 0 | 784.5 | 885.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4981 | 1 | 0 | 38889.4981 | 1 | 0 | 822.5 | 923.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4985 | 1 | 0 | 38889.4985 | 2 | 0 | 860.5 | 961.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.499 | 1 | 0 | 38889.499 | 1 | 0 | 898.5 | 999.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4994 | 1 | 0 | 38889.4994 | 1 | 0 | 936 | 1037 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4998 | 1 | 0 | 38889.4998 | 1 | 0 | 973.5 | 1074.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5003 | 1 | 0 | 38889.5003 | 1 | 0 | 1011.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5007 | 2 | 0 | 38889.5007 | 1 | 0 | 1049.5 | 1150.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5011 | 1 | 0 | 38889.5011 | 1 | 0 | 1087 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5016 | 1 | 0 | 38889.5016 | 1 | 0 | 1124.5 | 1225.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.502 | 1 | 0 | 38889.502 | 1 | 0 | 1162.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5025 | 1 | 0 | 38889.5025 | 1 | 0 | 1200.5 | 1301.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5029 | 1 | 0 | 38889.5029 | 1 | 0 | 1238.5 | 1339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5033 | 1 | 0 | 38889.5033 | 1 | 0 | 1276 | 1377 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5038 | 1 | 0 | 38889.5038 | 1 | 0 | 1313.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5042 | 1 | 0 | 38889.5042 | 1 | 0 | 1351.5 | 1452.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5046 | 1 | 0 | 38889.5047 | 1 | 0 | 1389.5 | 1490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5051 | 1 | 0 | 38889.5051 | 1 | 0 | 1427.5 | 1528.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5055 | 1 | 0 | 38889.5055 | 1 | 0 | 1465 | 1566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5059 | 1 | 0 | 38889.506 | 1 | 0 | 1502.5 | 1603.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5064 | 1 | 0 | 38889.5064 | 1 | 0 | 1540.5 | 1641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5068 | 1 | 0 | 38889.5068 | 1 | 0 | 1578.5 | 1679.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5073 | 1 | 0 | 38889.5073 | 1 | 0 | 1616.5 | 1717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5077 | 1 | 0 | 38889.5077 | 1 | 0 | 1654.5 | 1755.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5081 | 1 | 0 | 38889.5081 | 1 | 0 | 1691.5 | 1792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5086 | 1 | 0 | 38889.5086 | 1 | 0 | 1729.5 | 1830.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.509 | 1 | 0 | 38889.509 | 1 | 0 | 1767.5 | 1868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5099 | 1 | 0 | 38889.5099 | 1 | 0 | 1843 | 1944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5103 | 1 | 0 | 38889.5103 | 1 | 0 | 1880.5 | 1981.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5108 | 1 | 0 | 38889.5108 | 1 | 0 | 1918.5 | 2019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5112 | 1 | 0 | 38889.5112 | 1 | 0 | 1956.5 | 2057.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5116 | 1 | 0 | 38889.5117 | 1 | 0 | 1994.5 | 2095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5121 | 1 | 0 | 38889.5121 | 1 | 0 | 2031.5 | 2132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5125 | 1 | 0 | 38889.5125 | 1 | 0 | 2069.5 | 2170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.513 | 1 | 0 | 38889.513 | 1 | 0 | 2107.5 | 2208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5134 | 1 | 0 | 38889.5134 | 1 | 0 | 2145.5 | 2246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-5
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38889.4876 | 1 | 0 | 38889.4876 | 1 | 0 | -86.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.488 | 1 | 0 |  | 1 | 0 | -49 | 52 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4884 | 1 | 0 | 38889.4884 | 1 | 0 | -10.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4889 | 1 | 0 | 38889.4889 | 1 | 0 | 27 | 128 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4893 | 1 | 0 | 38889.4893 | 1 | 0 | 64.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4897 | 1 | 0 | 38889.4898 | 1 | 0 | 102.5 | 203.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4902 | 1 | 0 | 38889.4902 | 1 | 0 | 140.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4906 | 1 | 0 | 38889.4906 | 1 | 0 | 178.5 | 279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4911 | 1 | 0 | 38889.4911 | 1 | 0 | 216 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4915 | 1 | 0 | 38889.4915 | 1 | 0 | 253.5 | 354.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4919 | 1 | 0 | 38889.4919 | 1 | 0 | 291.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4924 | 1 | 0 | 38889.4924 | 1 | 0 | 329.5 | 430.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4928 | 1 | 0 | 38889.4928 | 1 | 0 | 367.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4933 | 1 | 0 | 38889.4933 | 2 | 0 | 405 | 506 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.4937 | 1 | 0 | 38889.4937 | 1 | 0 | 442.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4941 | 1 | 0 | 38889.4941 | 1 | 0 | 480.5 | 581.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4946 | 1 | 0 | 38889.4946 | 1 | 0 | 518.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.495 | 1 | 0 | 38889.495 | 1 | 0 | 556.5 | 657.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4954 | 1 | 0 | 38889.4954 | 1 | 0 | 594 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4959 | 1 | 0 | 38889.4959 | 1 | 0 | 631.5 | 732.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4963 | 1 | 0 | 38889.4963 | 1 | 0 | 669.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4967 | 1 | 0 | 38889.4968 | 1 | 0 | 707.5 | 808.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4972 | 1 | 0 | 38889.4972 | 1 | 0 | 745.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4976 | 1 | 0 | 38889.4976 | 2 | 0 | 783 | 884 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.4981 | 1 | 0 | 38889.4981 | 1 | 0 | 820.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4985 | 1 | 0 | 38889.4985 | 1 | 0 | 858.5 | 959.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4989 | 1 | 0 | 38889.4989 | 1 | 0 | 896.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4994 | 1 | 0 | 38889.4994 | 1 | 0 | 934.5 | 1035.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4998 | 1 | 0 | 38889.4998 | 1 | 0 | 971.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5002 | 1 | 0 | 38889.5003 | 1 | 0 | 1009.5 | 1110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5007 | 1 | 0 | 38889.5007 | 1 | 0 | 1047.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5011 | 1 | 0 | 38889.5011 | 1 | 0 | 1085.5 | 1186.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5016 | 1 | 0 | 38889.5016 | 1 | 0 | 1123.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.502 | 1 | 0 | 38889.502 | 1 | 0 | 1160.5 | 1261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5024 | 1 | 0 | 38889.5024 | 1 | 0 | 1198.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5029 | 1 | 0 | 38889.5029 | 1 | 0 | 1236.5 | 1337.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5033 | 1 | 0 | 38889.5033 | 1 | 0 | 1274.5 | 1375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5038 | 2 | 0 | 38889.5038 | 1 | 0 | 1312.5 | 1413.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5042 | 1 | 0 | 38889.5042 | 1 | 0 | 1349.5 | 1450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5046 | 1 | 0 | 38889.5046 | 1 | 0 | 1387.5 | 1488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5051 | 1 | 0 | 38889.5051 | 1 | 0 | 1425.5 | 1526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5055 | 1 | 0 | 38889.5055 | 1 | 0 | 1463.5 | 1564.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5059 | 1 | 0 | 38889.5059 | 1 | 0 | 1501.5 | 1602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5064 | 1 | 0 | 38889.5064 | 1 | 0 | 1538.5 | 1639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5068 | 1 | 0 | 38889.5068 | 1 | 0 | 1576.5 | 1677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5072 | 1 | 1 | 38889.5073 | 1 | 0 | 1614.5 | 1715.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5077 | 1 | 1 | 38889.5077 | 1 | 0 | 1652.5 | 1753.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5081 | 1 | 0 | 38889.5081 | 1 | 0 | 1690 | 1791 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5086 | 1 | 0 | 38889.5086 | 2 | 0 | 1727.5 | 1828.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.509 | 1 | 0 | 38889.509 | 1 | 0 | 1765.5 | 1866.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5099 | 1 | 0 | 38889.5099 | 1 | 0 | 1841.5 | 1942.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5103 | 1 | 0 | 38889.5103 | 1 | 0 | 1878.5 | 1979.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5107 | 1 | 0 | 38889.5108 | 1 | 0 | 1916.5 | 2017.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5112 | 1 | 0 | 38889.5112 | 1 | 0 | 1954.5 | 2055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5116 | 1 | 0 | 38889.5116 | 1 | 0 | 1992.5 | 2093.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5121 | 1 | 0 | 38889.5121 | 1 | 0 | 2030.5 | 2131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5125 | 1 | 0 | 38889.5125 | 1 | 0 | 2068 | 2169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5129 | 1 | 0 | 38889.5129 | 1 | 0 | 2105.5 | 2206.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5134 | 1 | 0 | 38889.5134 | 1 | 0 | 2143.5 | 2244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-4
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38889.4875 | 1 | 0 | 38889.4875 | 1 | 0 | -88.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.488 | 1 | 0 | 38889.488 | 1 | 0 | -50.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4884 | 1 | 0 | 38889.4884 | 1 | 0 | -12.5 | 88.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4889 | 1 | 0 | 38889.4889 | 1 | 0 | 25.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4893 | 1 | 0 | 38889.4893 | 1 | 0 | 63 | 164 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4897 | 1 | 0 | 38889.4897 | 1 | 0 | 100.5 | 201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4902 | 1 | 0 | 38889.4902 | 1 | 0 | 138.5 | 239.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4906 | 1 | 0 | 38889.4906 | 1 | 0 | 176.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.491 | 1 | 0 | 38889.4911 | 1 | 0 | 214.5 | 315.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4915 | 1 | 0 | 38889.4915 | 1 | 0 | 252.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4919 | 1 | 0 | 38889.4919 | 1 | 0 | 289.5 | 390.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4923 | 1 | 0 | 38889.4924 | 1 | 0 | 327.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4928 | 1 | 0 | 38889.4928 | 1 | 0 | 365.5 | 466.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4932 | 1 | 0 | 38889.4932 | 1 | 0 | 403.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4937 | 1 | 0 | 38889.4937 | 1 | 0 | 440.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4941 | 1 | 0 | 38889.4941 | 1 | 0 | 478.5 | 579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4945 | 1 | 0 | 38889.4945 | 1 | 0 | 516.5 | 617.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.495 | 1 | 0 | 38889.495 | 1 | 0 | 554.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4954 | 1 | 0 | 38889.4954 | 1 | 0 | 592.5 | 693.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4959 | 1 | 0 | 38889.4959 | 1 | 0 | 630 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4963 | 1 | 0 | 38889.4963 | 1 | 0 | 667.5 | 768.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4967 | 1 | 0 | 38889.4967 | 1 | 0 | 705.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4972 | 1 | 0 | 38889.4972 | 1 | 0 | 743.5 | 844.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4976 | 1 | 0 | 38889.4976 | 1 | 0 | 781.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.498 | 1 | 0 | 38889.498 | 1 | 0 | 819 | 920 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4985 | 1 | 0 | 38889.4985 | 1 | 0 | 856.5 | 957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4989 | 1 | 0 | 38889.4989 | 1 | 0 | 894.5 | 995.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4994 | 1 | 0 | 38889.4994 | 1 | 0 | 932.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4998 | 1 | 0 | 38889.4998 | 1 | 0 | 970.5 | 1071.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5002 | 1 | 0 | 38889.5002 | 1 | 0 | 1007.5 | 1108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5007 | 1 | 0 | 38889.5007 | 1 | 0 | 1045.5 | 1146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5011 | 1 | 0 | 38889.5011 | 1 | 0 | 1083.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5015 | 1 | 0 | 38889.5016 | 1 | 0 | 1121.5 | 1222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.502 | 1 | 0 | 38889.502 | 1 | 0 | 1159.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5024 | 1 | 0 | 38889.5024 | 1 | 0 | 1196.5 | 1297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5028 | 1 | 0 | 38889.5029 | 1 | 0 | 1234.5 | 1335.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38889.5033 | 1 | 0 | 1273 | 1374 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5037 | 1 | 0 | 38889.5037 | 1 | 0 | 1310.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5042 | 1 | 0 | 38889.5042 | 1 | 0 | 1348 | 1449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5046 | 1 | 0 | 38889.5046 | 1 | 0 | 1385.5 | 1486.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.505 | 1 | 0 | 38889.505 | 1 | 0 | 1423.5 | 1524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5055 | 1 | 0 | 38889.5055 | 1 | 0 | 1461.5 | 1562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5059 | 1 | 0 | 38889.5059 | 1 | 0 | 1499.5 | 1600.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5064 | 1 | 0 | 38889.5064 | 2 | 0 | 1537.5 | 1638.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5068 | 1 | 0 | 38889.5068 | 2 | 0 | 1574.5 | 1675.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5072 | 1089 | 1153 | 38889.5072 | 1004 | 1103 | 1612.5 | 1713.5 | 66.4835 | 70.3907 | 61.2943 | 67.3382 | 0.66484 | 0.70391 | 0.61294 | 0.67338 | 0.039072 | 0.06044 | 315.2681 | 442.0855 | 9.1229
38889.5077 | 989 | 961 | 38889.5077 | 1130 | 1083 | 1650.5 | 1751.5 | 60.3785 | 58.6691 | 68.9866 | 66.1172 | 0.60379 | 0.58669 | 0.68987 | 0.66117 | 0.017094 | 0.028694 | 363.7317 | 341.9631 | 13.1253
38889.5081 | 1 | 0 | 38889.5081 | 1 | 0 | 1688.5 | 1789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5085 | 1 | 0 | 38889.5085 | 1 | 0 | 1726 | 1827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.509 | 1 | 0 | 38889.509 | 1 | 0 | 1763.5 | 1864.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5098 | 1 | 0 | 38889.5099 | 1 | 0 | 1839.5 | 1940.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5103 | 1 | 0 | 38889.5103 | 1 | 0 | 1877.5 | 1978.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5107 | 1 | 0 | 38889.5107 | 1 | 0 | 1914.5 | 2015.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5112 | 1 | 0 | 38889.5112 | 1 | 0 | 1952.5 | 2053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5116 | 1 | 0 | 38889.5116 | 1 | 0 | 1990.5 | 2091.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.512 | 1 | 0 | 38889.512 | 1 | 0 | 2028.5 | 2129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5125 | 1 | 0 | 38889.5125 | 1 | 0 | 2066.5 | 2167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5129 | 1 | 0 | 38889.5129 | 1 | 1 | 2104 | 2205 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211202 | 211202 | 211201.9994
38889.5133 | 1 | 0 | 38889.5134 | 1 | 0 | 2141.5 | 2242.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-3
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38889.4875 | 1 | 0 | 38889.4875 | 1 | 0 | -89.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.488 | 1 | 0 | 38889.488 | 1 | 0 | -52.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4884 | 1 | 0 | 38889.4884 | 1 | 0 | -14.5 | 86.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4888 | 1 | 0 | 38889.4888 | 1 | 0 | 23.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4893 | 1 | 0 | 38889.4893 | 1 | 0 | 61.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4897 | 1 | 0 | 38889.4897 | 1 | 0 | 99 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4901 | 1 | 0 | 38889.4902 | 1 | 0 | 136.5 | 237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4906 | 1 | 0 | 38889.4906 | 1 | 0 | 174.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.491 | 1 | 0 | 38889.491 | 1 | 0 | 212.5 | 313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4915 | 1 | 0 | 38889.4915 | 1 | 0 | 250.5 | 351.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4919 | 1 | 0 | 38889.4919 | 1 | 0 | 288.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4923 | 1 | 0 | 38889.4923 | 1 | 0 | 325.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4928 | 1 | 0 | 38889.4928 | 1 | 0 | 363.5 | 464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4932 | 1 | 0 | 38889.4932 | 1 | 0 | 401.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4936 | 1 | 0 | 38889.4937 | 1 | 0 | 439.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4941 | 1 | 0 | 38889.4941 | 1 | 0 | 476.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4945 | 2 | 0 | 38889.4945 | 1 | 0 | 514.5 | 615.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.495 | 1 | 0 | 38889.495 | 1 | 0 | 552.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4954 | 1 | 0 | 38889.4954 | 1 | 0 | 590.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4958 | 1 | 0 | 38889.4958 | 1 | 0 | 628.5 | 729.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4963 | 1 | 0 | 38889.4963 | 1 | 0 | 666 | 767 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4967 | 1 | 0 | 38889.4967 | 1 | 0 | 703.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4971 | 1 | 0 | 38889.4972 | 1 | 0 | 741.5 | 842.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4976 | 1 | 0 | 38889.4976 | 1 | 0 | 779.5 | 880.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.498 | 1 | 0 | 38889.498 | 1 | 0 | 817.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4984 | 1 | 0 | 38889.4985 | 1 | 0 | 854.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4989 | 1 | 0 | 38889.4989 | 1 | 0 | 892.5 | 993.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4993 | 2 | 0 | 38889.4993 | 1 | 0 | 930.5 | 1031.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4998 | 2 | 0 | 38889.4998 | 1 | 0 | 968.5 | 1069.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5002 | 2 | 0 | 38889.5002 | 1 | 0 | 1006.5 | 1107.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5006 | 1 | 0 | 38889.5006 | 1 | 0 | 1043.5 | 1144.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5011 | 2 | 0 | 38889.5011 | 1 | 0 | 1081.5 | 1182.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5015 | 2 | 0 | 38889.5015 | 1 | 0 | 1119.5 | 1220.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.502 | 1 | 0 | 38889.502 | 1 | 0 | 1157.5 | 1258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5024 | 2 | 0 | 38889.5024 | 1 | 0 | 1195 | 1296 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5028 | 2 | 0 | 38889.5028 | 1 | 0 | 1232.5 | 1333.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5033 | 1 | 0 | 38889.5033 | 1 | 0 | 1270.5 | 1371.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5037 | 1 | 0 | 38889.5037 | 2 | 0 | 1308.5 | 1409.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5041 | 2 | 0 | 38889.5042 | 1 | 0 | 1346.5 | 1447.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5046 | 1 | 0 | 38889.5046 | 1 | 0 | 1384.5 | 1485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.505 | 2 | 0 | 38889.505 | 1 | 0 | 1421.5 | 1522.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5055 | 2 | 0 | 38889.5055 | 1 | 0 | 1459.5 | 1560.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5059 | 1 | 0 | 38889.5059 | 1 | 0 | 1497.5 | 1598.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5063 | 2 | 0 | 38889.5063 | 1 | 0 | 1535.5 | 1636.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5068 | 2 | 0 | 38889.5068 | 1 | 0 | 1573.5 | 1674.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5072 | 2 | 0 | 38889.5072 | 1 | 0 | 1610.5 | 1711.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5076 | 2 | 0 | 38889.5077 | 1 | 0 | 1648.5 | 1749.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5081 | 1 | 0 | 38889.5081 | 1 | 0 | 1686.5 | 1787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5085 | 2 | 0 | 38889.5085 | 1 | 0 | 1724.5 | 1825.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.509 | 2 | 0 | 38889.509 | 1 | 0 | 1762 | 1863 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5098 | 2 | 0 | 38889.5098 | 1 | 0 | 1837.5 | 1938.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5103 | 1 | 0 | 38889.5103 | 1 | 0 | 1875.5 | 1976.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5107 | 2 | 0 | 38889.5107 | 1 | 0 | 1913.5 | 2014.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5111 | 2 | 0 | 38889.5111 | 1 | 0 | 1951 | 2052 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5116 | 1 | 0 | 38889.5116 | 1 | 0 | 1988.5 | 2089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.512 | 2 | 0 | 38889.512 | 1 | 0 | 2026.5 | 2127.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5125 | 2 | 0 | 38889.5125 | 1 | 0 | 2064.5 | 2165.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5129 | 1 | 0 | 38889.5129 | 1 | 0 | 2102.5 | 2203.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5133 | 2 | 0 | 38889.5133 | 1 | 0 | 2139.5 | 2240.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## C1-7
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 158.2039 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38889.4875 | 1 | 0 | 38889.4875 | 1 | 0 | -91.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4879 | 1 | 0 | 38889.488 | 1 | 0 | -53.5 | 47.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4884 | 1 | 0 | 38889.4884 | 1 | 0 | -16.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4888 | 1 | 0 | 38889.4888 | 1 | 0 | 21.5 | 122.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4892 | 1 | 0 | 38889.4893 | 1 | 0 | 59.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4897 | 1 | 0 | 38889.4897 | 1 | 0 | 97.5 | 198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4901 | 1 | 0 | 38889.4901 | 1 | 0 | 135.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4906 | 1 | 0 | 38889.4906 | 1 | 0 | 172.5 | 273.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.491 | 1 | 0 | 38889.491 | 1 | 0 | 210.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4914 | 1 | 0 | 38889.4914 | 1 | 0 | 248.5 | 349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4919 | 1 | 0 | 38889.4919 | 1 | 0 | 286.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4923 | 1 | 0 | 38889.4923 | 1 | 0 | 324 | 425 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4927 | 1 | 0 | 38889.4928 | 1 | 0 | 361.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4932 | 1 | 0 | 38889.4932 | 1 | 0 | 399.5 | 500.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4936 | 1 | 0 | 38889.4936 | 1 | 0 | 437.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4941 | 1 | 0 | 38889.4941 | 1 | 0 | 475.5 | 576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4945 | 1 | 0 | 38889.4945 | 1 | 0 | 513 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4949 | 1 | 0 | 38889.4949 | 1 | 0 | 550.5 | 651.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4954 | 1 | 0 | 38889.4954 | 1 | 0 | 588.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4958 | 1 | 0 | 38889.4958 | 1 | 0 | 626.5 | 727.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4962 | 1 | 0 | 38889.4963 | 1 | 0 | 664.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4967 | 1 | 0 | 38889.4967 | 1 | 0 | 702 | 803 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4971 | 1 | 0 | 38889.4971 | 1 | 0 | 739.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4976 | 1 | 0 | 38889.4976 | 2 | 0 | 777.5 | 878.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 259038 | 129469 | 259037.9994
38889.498 | 1 | 0 | 38889.498 | 1 | 0 | 815.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38889.4984 | 1 | 0 | 38889.4984 | 2 | 0 | 853.5 | 954.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 259038 | 129469 | 259037.9994
38889.4989 | 1 | 0 | 38889.4989 | 1999 | 0 | 890.5 | 991.5 | 0.06105 | 0 | 122.0391 | 0 | 0.0006105 | 0 | 1.2204 | 0 | 0.0006105 | 1.2204 | 259038 | 29.6338 | 259037.9994
38889.4993 | 1 | 0 | 38889.4993 | 2071 | 0 | 928.5 | 1029.5 | 0.06105 | 0 | 126.4347 | 0 | 0.0006105 | 0 | 1.2643 | 0 | 0.0006105 | 1.2643 | 259038 | 25.127 | 259037.9994
38889.4997 | 1 | 0 | 38889.4998 | 2317 | 0 | 966.5 | 1067.5 | 0.06105 | 0 | 141.453 | 0 | 0.0006105 | 0 | 1.4145 | 0 | 0.0006105 | 1.4145 | 259038 | 11.842 | 259037.9994
38889.5002 | 1 | 0 | 38889.5002 | 2019 | 0 | 1004.5 | 1105.5 | 0.06105 | 0 | 123.2601 | 0 | 0.0006105 | 0 | 1.2326 | 0 | 0.0006105 | 1.2326 | 259038 | 28.3497 | 259037.9994
38889.5006 | 1 | 0 | 38889.5006 | 2563 | 0 | 1042.5 | 1143.5 | 0.06105 | 0 | 156.4713 | 0 | 0.0006105 | 0 | 1.5647 | 0 | 0.0006105 | 1.5647 | 259038 | 1.1073 | 259037.9994
38889.5011 | 1 | 0 | 38889.5011 | 2483 | 0 | 1079.5 | 1180.5 | 0.06105 | 0 | 151.5873 | 0 | 0.0006105 | 0 | 1.5159 | 0 | 0.0006105 | 1.5159 | 259038 | 4.3649 | 259037.9994
38889.5015 | 2 | 0 | 38889.5015 | 2054 | 0 | 1117.5 | 1218.5 | 0.1221 | 0 | 125.3968 | 0 | 0.001221 | 0 | 1.254 | 0 | 0.001221 | 1.254 | 129469 | 26.1626 | 129468.9988
38889.5019 | 1 | 0 | 38889.5019 | 2261 | 0 | 1155.5 | 1256.5 | 0.06105 | 0 | 138.0342 | 0 | 0.0006105 | 0 | 1.3803 | 0 | 0.0006105 | 1.3803 | 259038 | 14.6121 | 259037.9994
38889.5024 | 1 | 0 | 38889.5024 | 2529 | 0 | 1193.5 | 1294.5 | 0.06105 | 0 | 154.3956 | 0 | 0.0006105 | 0 | 1.544 | 0 | 0.0006105 | 1.544 | 259038 | 2.4666 | 259037.9994
38889.5028 | 1 | 0 | 38889.5028 | 2575 | 0 | 1231 | 1332 | 0.06105 | 0 | 157.2039 | 0 | 0.0006105 | 0 | 1.572 | 0 | 0.0006105 | 1.572 | 259038 | 0.63612 | 259037.9994
38889.5032 | 1 | 0 | 38889.5033 | 2093 | 0 | 1268.5 | 1369.5 | 0.06105 | 0 | 127.7778 | 0 | 0.0006105 | 0 | 1.2778 | 0 | 0.0006105 | 1.2778 | 259038 | 23.8118 | 259037.9994
38889.5037 | 1 | 0 | 38889.5037 | 2154 | 0 | 1306.5 | 1407.5 | 0.06105 | 0 | 131.5018 | 0 | 0.0006105 | 0 | 1.315 | 0 | 0.0006105 | 1.315 | 259038 | 20.3055 | 259037.9994
38889.5041 | 1 | 0 | 38889.5041 | 2167 | 0 | 1344.5 | 1445.5 | 0.06105 | 0 | 132.2955 | 0 | 0.0006105 | 0 | 1.323 | 0 | 0.0006105 | 1.323 | 259038 | 19.5838 | 259037.9994
38889.5046 | 1 | 0 | 38889.5046 | 2560 | 0 | 1382.5 | 1483.5 | 0.06105 | 0 | 156.2882 | 0 | 0.0006105 | 0 | 1.5629 | 0 | 0.0006105 | 1.5629 | 259038 | 1.2258 | 259037.9994
38889.505 | 1 | 0 | 38889.505 | 2230 | 0 | 1420.5 | 1521.5 | 0.06105 | 0 | 136.1416 | 0 | 0.0006105 | 0 | 1.3614 | 0 | 0.0006105 | 1.3614 | 259038 | 16.2054 | 259037.9994
38889.5054 | 1 | 0 | 38889.5054 | 2262 | 0 | 1457.5 | 1558.5 | 0.06105 | 0 | 138.0952 | 0 | 0.0006105 | 0 | 1.381 | 0 | 0.0006105 | 1.381 | 259038 | 14.5615 | 259037.9994
38889.5059 | 1 | 0 | 38889.5059 | 2008 | 0 | 1495.5 | 1596.5 | 0.06105 | 0 | 122.5885 | 0 | 0.0006105 | 0 | 1.2259 | 0 | 0.0006105 | 1.2259 | 259038 | 29.0528 | 259037.9994
38889.5063 | 1 | 0 | 38889.5063 | 2219 | 0 | 1533.5 | 1634.5 | 0.06105 | 0 | 135.4701 | 0 | 0.0006105 | 0 | 1.3547 | 0 | 0.0006105 | 1.3547 | 259038 | 16.7814 | 259037.9994
38889.5067 | 1 | 0 | 38889.5068 | 2177 | 0 | 1571.5 | 1672.5 | 0.06105 | 0 | 132.906 | 0 | 0.0006105 | 0 | 1.3291 | 0 | 0.0006105 | 1.3291 | 259038 | 19.0345 | 259037.9994
38889.5072 | 1 | 0 | 38889.5072 | 2160 | 0 | 1609.5 | 1710.5 | 0.06105 | 0 | 131.8681 | 0 | 0.0006105 | 0 | 1.3187 | 0 | 0.0006105 | 1.3187 | 259038 | 19.9713 | 259037.9994
38889.5076 | 1 | 0 | 38889.5076 | 2112 | 0 | 1646.5 | 1747.5 | 0.06105 | 0 | 128.9377 | 0 | 0.0006105 | 0 | 1.2894 | 0 | 0.0006105 | 1.2894 | 259038 | 22.6979 | 259037.9994
38889.5081 | 1 | 0 | 38889.5081 | 2412 | 0 | 1684.5 | 1785.5 | 0.06105 | 0 | 147.2527 | 0 | 0.0006105 | 0 | 1.4725 | 0 | 0.0006105 | 1.4725 | 259038 | 7.437 | 259037.9994
38889.5085 | 1 | 0 | 38889.5085 | 2091 | 0 | 1722.5 | 1823.5 | 0.06105 | 0 | 127.6557 | 0 | 0.0006105 | 0 | 1.2766 | 0 | 0.0006105 | 1.2766 | 259038 | 23.9302 | 259037.9994
38889.5089 | 1 | 0 | 38889.5089 | 2140 | 0 | 1760.5 | 1861.5 | 0.06105 | 0 | 130.6471 | 0 | 0.0006105 | 0 | 1.3065 | 0 | 0.0006105 | 1.3065 | 259038 | 21.0925 | 259037.9994
38889.5098 | 1 | 0 | 38889.5098 | 2528 | 0 | 1835.5 | 1936.5 | 0.06105 | 0 | 154.3346 | 0 | 0.0006105 | 0 | 1.5433 | 0 | 0.0006105 | 1.5433 | 259038 | 2.5071 | 259037.9994
38889.5102 | 1 | 0 | 38889.5103 | 2082 | 0 | 1873.5 | 1974.5 | 0.06105 | 0 | 127.1062 | 0 | 0.0006105 | 0 | 1.2711 | 0 | 0.0006105 | 1.2711 | 259038 | 24.4659 | 259037.9994
38889.5107 | 1 | 0 | 38889.5107 | 2437 | 0 | 1911.5 | 2012.5 | 0.06105 | 0 | 148.779 | 0 | 0.0006105 | 0 | 1.4878 | 0 | 0.0006105 | 1.4878 | 259038 | 6.3348 | 259037.9994
38889.5111 | 1 | 0 | 38889.5111 | 2203 | 0 | 1949.5 | 2050.5 | 0.06105 | 0 | 134.4933 | 0 | 0.0006105 | 0 | 1.3449 | 0 | 0.0006105 | 1.3449 | 259038 | 17.6296 | 259037.9994
38889.5116 | 1 | 0 | 38889.5116 | 2030 | 0 | 1986.5 | 2087.5 | 0.06105 | 0 | 123.9316 | 0 | 0.0006105 | 0 | 1.2393 | 0 | 0.0006105 | 1.2393 | 259038 | 27.6542 | 259037.9994
38889.512 | 1 | 0 | 38889.512 | 2221 | 0 | 2024.5 | 2125.5 | 0.06105 | 0 | 135.5922 | 0 | 0.0006105 | 0 | 1.3559 | 0 | 0.0006105 | 1.3559 | 259038 | 16.6763 | 259037.9994
38889.5124 | 1 | 0 | 38889.5124 | 2527 | 0 | 2062.5 | 2163.5 | 0.06105 | 0 | 154.2735 | 0 | 0.0006105 | 0 | 1.5427 | 0 | 0.0006105 | 1.5427 | 259038 | 2.5477 | 259037.9994
38889.5129 | 1 | 0 | 38889.5129 | 1930 | 0 | 2100.5 | 2201.5 | 0.06105 | 0 | 117.8266 | 0 | 0.0006105 | 0 | 1.1783 | 0 | 0.0006105 | 1.1783 | 259038 | 34.2684 | 259037.9994
38889.5133 | 1 | 0 | 38889.5133 | 2027 | 0 | 2138.5 | 2239.5 | 0.06105 | 0 | 123.7485 | 0 | 0.0006105 | 0 | 1.2375 | 0 | 0.0006105 | 1.2375 | 259038 | 27.8431 | 259037.9994

## C1-6
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38889.4875 | 1 | 0 | 38889.4875 | 1 | 0 | -93.5 | 7.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4879 | 1 | 0 | 38889.4879 | 1 | 0 | -55.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4884 | 1 | 0 | 38889.4884 | 1 | 0 | -17.5 | 83.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4888 | 1 | 0 | 38889.4888 | 1 | 0 | 19.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4892 | 1 | 0 | 38889.4892 | 1 | 0 | 57.5 | 158.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4897 | 1 | 0 | 38889.4897 | 1 | 0 | 95.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4901 | 1 | 0 | 38889.4901 | 1 | 0 | 133.5 | 234.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4905 | 1 | 0 | 38889.4906 | 1 | 0 | 171.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.491 | 1 | 0 | 38889.491 | 1 | 0 | 208.5 | 309.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4914 | 1 | 0 | 38889.4914 | 1 | 0 | 246.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4919 | 1 | 0 | 38889.4919 | 1 | 0 | 284.5 | 385.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4923 | 1 | 0 | 38889.4923 | 1 | 0 | 322.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4927 | 1 | 0 | 38889.4927 | 1 | 0 | 360 | 461 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4932 | 1 | 0 | 38889.4932 | 1 | 0 | 397.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4936 | 1 | 0 | 38889.4936 | 1 | 0 | 435.5 | 536.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.494 | 1 | 0 | 38889.4941 | 1 | 0 | 473.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4945 | 1 | 0 | 38889.4945 | 1 | 0 | 511.5 | 612.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4949 | 1 | 0 | 38889.4949 | 1 | 0 | 549 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4953 | 1 | 0 | 38889.4954 | 1 | 0 | 586.5 | 687.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4958 | 1 | 0 | 38889.4958 | 1 | 0 | 624.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4962 | 1 | 0 | 38889.4962 | 1 | 0 | 662.5 | 763.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4967 | 1 | 0 | 38889.4967 | 1 | 0 | 700.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4971 | 1 | 0 | 38889.4971 | 1 | 0 | 737.5 | 838.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4975 | 1 | 0 | 38889.4975 | 1 | 0 | 775.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.498 | 1 | 0 | 38889.498 | 1 | 0 | 813.5 | 914.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4984 | 1 | 0 | 38889.4984 | 1 | 0 | 851.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4989 | 1 | 0 | 38889.4989 | 1 | 0 | 889.5 | 990.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4993 | 1 | 0 | 38889.4993 | 1 | 0 | 926.5 | 1027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4997 | 1 | 0 | 38889.4997 | 1 | 0 | 964.5 | 1065.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5002 | 1 | 0 | 38889.5002 | 1 | 0 | 1002.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5006 | 1 | 0 | 38889.5006 | 1 | 0 | 1040.5 | 1141.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.501 | 1 | 0 | 38889.501 | 1 | 0 | 1078 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5015 | 1 | 0 | 38889.5015 | 1 | 0 | 1115.5 | 1216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5019 | 1 | 0 | 38889.5019 | 1 | 0 | 1153.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5023 | 1 | 0 | 38889.5024 | 1 | 0 | 1191.5 | 1292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5028 | 1 | 0 | 38889.5028 | 1 | 1 | 1229.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211202 | 211202 | 211201.9994
38889.5032 | 1 | 0 | 38889.5032 | 1 | 0 | 1267.5 | 1368.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5037 | 1 | 0 | 38889.5037 | 1 | 0 | 1304.5 | 1405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5041 | 1 | 0 | 38889.5041 | 1 | 0 | 1342.5 | 1443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5045 | 1 | 0 | 38889.5045 | 1 | 0 | 1380.5 | 1481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.505 | 1 | 0 | 38889.505 | 1 | 0 | 1418.5 | 1519.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5054 | 1 | 0 | 38889.5054 | 1 | 0 | 1456 | 1557 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5058 | 1 | 0 | 38889.5059 | 1 | 0 | 1493.5 | 1594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5063 | 1 | 0 | 38889.5063 | 1 | 0 | 1531.5 | 1632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5067 | 1 | 0 | 38889.5067 | 1 | 0 | 1569.5 | 1670.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5072 | 1 | 0 | 38889.5072 | 1 | 0 | 1607.5 | 1708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5076 | 1 | 0 | 38889.5076 | 1 | 0 | 1645 | 1746 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.508 | 1 | 0 | 38889.508 | 1 | 0 | 1682.5 | 1783.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5085 | 1 | 0 | 38889.5085 | 1 | 0 | 1720.5 | 1821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5089 | 1 | 0 | 38889.5089 | 1 | 0 | 1758.5 | 1859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5098 | 1 | 0 | 38889.5098 | 1 | 0 | 1834 | 1935 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5102 | 1 | 0 | 38889.5102 | 1 | 0 | 1871.5 | 1972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5107 | 1 | 0 | 38889.5107 | 1 | 0 | 1909.5 | 2010.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5111 | 1 | 0 | 38889.5111 | 1 | 0 | 1947.5 | 2048.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5115 | 1 | 0 | 38889.5116 | 1 | 0 | 1985.5 | 2086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.512 | 1 | 0 | 38889.512 | 1 | 0 | 2023 | 2124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5124 | 1 | 0 | 38889.5124 | 1 | 0 | 2060.5 | 2161.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5128 | 1 | 0 | 38889.5129 | 1 | 0 | 2098.5 | 2199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5133 | 1 | 0 | 38889.5133 | 1 | 0 | 2136.5 | 2237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-5
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38889.4875 | 1 | 0 | 38889.4875 | 1 | 0 | -95.5 | 5.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4879 | 1 | 0 | 38889.4879 | 1 | 0 | -57.5 | 43.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4883 | 1 | 0 | 38889.4883 | 1 | 0 | -19.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4888 | 1 | 0 | 38889.4888 | 1 | 0 | 18 | 119 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4892 | 1 | 0 | 38889.4892 | 1 | 0 | 55.5 | 156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4896 | 1 | 0 | 38889.4897 | 1 | 0 | 93.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4901 | 1 | 0 | 38889.4901 | 1 | 0 | 131.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4905 | 1 | 0 | 38889.4905 | 1 | 0 | 169.5 | 270.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.491 | 1 | 0 | 38889.491 | 1 | 0 | 207.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4914 | 1 | 0 | 38889.4914 | 1 | 0 | 244.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4918 | 1 | 0 | 38889.4918 | 1 | 0 | 282.5 | 383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4923 | 1 | 0 | 38889.4923 | 1 | 0 | 320.5 | 421.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4927 | 1 | 0 | 38889.4927 | 1 | 0 | 358.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4931 | 1 | 0 | 38889.4932 | 1 | 0 | 396.5 | 497.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4936 | 1 | 0 | 38889.4936 | 1 | 0 | 433.5 | 534.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.494 | 1 | 0 | 38889.494 | 1 | 0 | 471.5 | 572.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4945 | 1 | 0 | 38889.4945 | 1 | 0 | 509.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4949 | 1 | 0 | 38889.4949 | 1 | 0 | 547.5 | 648.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4953 | 1 | 0 | 38889.4953 | 1 | 0 | 585 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4958 | 1 | 0 | 38889.4958 | 1 | 0 | 622.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4962 | 1 | 0 | 38889.4962 | 1 | 0 | 660.5 | 761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4966 | 1 | 0 | 38889.4967 | 1 | 0 | 698.5 | 799.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4971 | 1 | 0 | 38889.4971 | 1 | 0 | 736.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4975 | 1 | 0 | 38889.4975 | 1 | 0 | 774 | 875 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.498 | 1 | 0 | 38889.498 | 1 | 0 | 811.5 | 912.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4984 | 1 | 0 | 38889.4984 | 1 | 0 | 849.5 | 950.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4988 | 1 | 0 | 38889.4988 | 1 | 0 | 887.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4993 | 1 | 0 | 38889.4993 | 1 | 0 | 925.5 | 1026.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4997 | 1 | 0 | 38889.4997 | 1 | 0 | 962.5 | 1063.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5001 | 1 | 0 | 38889.5002 | 1 | 0 | 1000.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5006 | 1 | 0 | 38889.5006 | 1 | 0 | 1038.5 | 1139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.501 | 1 | 0 | 38889.501 | 1 | 0 | 1076.5 | 1177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5015 | 1 | 0 | 38889.5015 | 1 | 0 | 1114.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5019 | 1 | 0 | 38889.5019 | 1 | 0 | 1151.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5023 | 1 | 0 | 38889.5023 | 1 | 0 | 1189.5 | 1290.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5028 | 1 | 0 | 38889.5028 | 1 | 0 | 1227.5 | 1328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5032 | 1 | 0 | 38889.5032 | 1 | 0 | 1265.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5036 | 1 | 0 | 38889.5037 | 1 | 0 | 1303.5 | 1404.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5041 | 1 | 0 | 38889.5041 | 1 | 0 | 1340.5 | 1441.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5045 | 1 | 0 | 38889.5045 | 1 | 0 | 1378.5 | 1479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.505 | 1 | 0 | 38889.505 | 1 | 0 | 1416.5 | 1517.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5054 | 1 | 0 | 38889.5054 | 1 | 0 | 1454.5 | 1555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5058 | 1 | 0 | 38889.5058 | 1 | 0 | 1492 | 1593 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5063 | 1 | 0 | 38889.5063 | 1 | 0 | 1529.5 | 1630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5067 | 1 | 0 | 38889.5067 | 1 | 0 | 1567.5 | 1668.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5071 | 1 | 0 | 38889.5072 | 1 | 0 | 1605.5 | 1706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5076 | 1 | 1 | 38889.5076 | 1 | 0 | 1643.5 | 1744.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.508 | 1 | 0 | 38889.508 | 1 | 0 | 1681.5 | 1782.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5084 | 1 | 0 | 38889.5085 | 1 | 0 | 1718.5 | 1819.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5089 | 1 | 0 | 38889.5089 | 1 | 0 | 1756.5 | 1857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5098 | 1 | 0 | 38889.5098 | 1 | 0 | 1832.5 | 1933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5102 | 1 | 0 | 38889.5102 | 1 | 0 | 1870 | 1971 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5106 | 1 | 0 | 38889.5106 | 1 | 0 | 1907.5 | 2008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5111 | 1 | 0 | 38889.5111 | 1 | 0 | 1945.5 | 2046.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5115 | 1 | 0 | 38889.5115 | 1 | 0 | 1983.5 | 2084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.512 | 1 | 0 | 38889.512 | 1 | 0 | 2021.5 | 2122.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5124 | 2 | 0 | 38889.5124 | 1 | 0 | 2059 | 2160 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5128 | 1 | 0 | 38889.5128 | 1 | 0 | 2096.5 | 2197.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5133 | 1 | 0 | 38889.5133 | 1 | 0 | 2134.5 | 2235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-4
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38889.4874 | 1 | 0 | 38889.4874 | 1 | 0 | -97.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4879 | 1 | 0 | 38889.4879 | 1 | 0 | -59.5 | 41.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4883 | 1 | 0 | 38889.4883 | 1 | 0 | -21.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4887 | 1 | 0 | 38889.4888 | 1 | 0 | 16.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4892 | 1 | 0 | 38889.4892 | 2 | 0 | 54 | 155 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.4896 | 1 | 0 | 38889.4896 | 1 | 0 | 91.5 | 192.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4901 | 1 | 0 | 38889.4901 | 1 | 0 | 129.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4905 | 1 | 0 | 38889.4905 | 1 | 0 | 167.5 | 268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4909 | 1 | 0 | 38889.4909 | 1 | 0 | 205.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4914 | 1 | 0 | 38889.4914 | 1 | 0 | 243 | 344 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4918 | 1 | 0 | 38889.4918 | 1 | 0 | 280.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4922 | 1 | 0 | 38889.4923 | 1 | 0 | 318.5 | 419.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4927 | 1 | 0 | 38889.4927 | 1 | 0 | 356.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4931 | 1 | 0 | 38889.4931 | 1 | 0 | 394.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4936 | 1 | 0 | 38889.4936 | 1 | 0 | 432 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.494 | 1 | 0 | 38889.494 | 1 | 0 | 469.5 | 570.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4944 | 1 | 0 | 38889.4944 | 1 | 0 | 507.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4949 | 1 | 0 | 38889.4949 | 1 | 0 | 545.5 | 646.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4953 | 1 | 0 | 38889.4953 | 1 | 0 | 583.5 | 684.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4957 | 1 | 0 | 38889.4958 | 1 | 0 | 620.5 | 721.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4962 | 1 | 0 | 38889.4962 | 2 | 0 | 658.5 | 759.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.4966 | 1 | 0 | 38889.4966 | 1 | 0 | 696.5 | 797.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4971 | 1 | 0 | 38889.4971 | 1 | 0 | 734.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4975 | 1 | 0 | 38889.4975 | 1 | 0 | 772.5 | 873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4979 | 1 | 0 | 38889.4979 | 1 | 0 | 809.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4984 | 1 | 0 | 38889.4984 | 1 | 0 | 847.5 | 948.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4988 | 1 | 0 | 38889.4988 | 1 | 0 | 885.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4992 | 1 | 0 | 38889.4993 | 1 | 0 | 923.5 | 1024.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4997 | 1 | 0 | 38889.4997 | 1 | 0 | 961.5 | 1062.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5001 | 1 | 0 | 38889.5001 | 1 | 0 | 998.5 | 1099.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5006 | 1 | 0 | 38889.5006 | 1 | 0 | 1036.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.501 | 1 | 0 | 38889.501 | 1 | 0 | 1074.5 | 1175.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5014 | 1 | 0 | 38889.5014 | 1 | 0 | 1112.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5019 | 1 | 0 | 38889.5019 | 1 | 0 | 1150.5 | 1251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5023 | 1 | 0 | 38889.5023 | 1 | 0 | 1187.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5027 | 1 | 0 | 38889.5028 | 1 | 0 | 1225.5 | 1326.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5032 | 1 | 0 | 38889.5032 | 1 | 0 | 1263.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5036 | 1 | 0 | 38889.5036 | 1 | 0 | 1301.5 | 1402.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5041 | 1 | 0 | 38889.5041 | 1 | 0 | 1339 | 1440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5045 | 1 | 0 | 38889.5045 | 1 | 0 | 1376.5 | 1477.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5049 | 1 | 0 | 38889.5049 | 1 | 0 | 1414.5 | 1515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38889.5054 | 1 | 0 | 1453 | 1554 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5058 | 1 | 0 | 38889.5058 | 1 | 0 | 1490.5 | 1591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5062 | 1 | 0 | 38889.5063 | 2 | 0 | 1528.5 | 1629.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5067 | 1 | 0 | 38889.5067 | 1 | 0 | 1565.5 | 1666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5071 | 1 | 0 | 38889.5071 | 1 | 0 | 1603.5 | 1704.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5076 | 1201 | 1018 | 38889.5076 | 1038 | 1013 | 1641.5 | 1742.5 | 73.3211 | 62.149 | 63.37 | 61.8437 | 0.73321 | 0.62149 | 0.6337 | 0.61844 | 0.11172 | 0.015263 | 29.6559 | 35.1964 | 2.7103
38889.508 | 4 | 3 | 38889.508 | 19 | 17 | 1679.5 | 1780.5 | 0.2442 | 0.18315 | 1.16 | 1.0379 | 0.002442 | 0.0018315 | 0.0116 | 0.010379 | 0.0006105 | 0.001221 | 211505.5919 | 105123.4709 | 70133.9509
38889.5084 | 1 | 0 | 38889.5084 | 1 | 0 | 1717 | 1818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5089 | 1 | 0 | 38889.5089 | 1 | 0 | 1754.5 | 1855.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5097 | 1 | 0 | 38889.5098 | 1 | 0 | 1830.5 | 1931.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5102 | 1 | 0 | 38889.5102 | 1 | 0 | 1868.5 | 1969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5106 | 1 | 0 | 38889.5106 | 1 | 0 | 1906 | 2007 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5111 | 2 | 0 | 38889.5111 | 1 | 0 | 1943.5 | 2044.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5115 | 1 | 0 | 38889.5115 | 1 | 0 | 1981.5 | 2082.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5119 | 1 | 0 | 38889.5119 | 1 | 0 | 2019.5 | 2120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5124 | 1 | 0 | 38889.5124 | 1 | 0 | 2057.5 | 2158.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5128 | 1 | 0 | 38889.5128 | 1 | 0 | 2095 | 2196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5132 | 2 | 0 | 38889.5133 | 1 | 0 | 2132.5 | 2233.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## C1-3
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38889.4874 | 1 | 0 | 38889.4874 | 1 | 0 | -98.5 | 2.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4878 | 1 | 0 | 38889.4879 | 1 | 0 | -61.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4883 | 1 | 0 | 38889.4883 | 1 | 0 | -23.5 | 77.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4887 | 1 | 0 | 38889.4887 | 1 | 0 | 14.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4892 | 2 | 0 | 38889.4892 | 1 | 0 | 52.5 | 153.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4896 | 1 | 0 | 38889.4896 | 1 | 0 | 90 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.49 | 1 | 0 | 38889.49 | 1 | 0 | 127.5 | 228.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4905 | 1 | 0 | 38889.4905 | 1 | 0 | 165.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4909 | 1 | 0 | 38889.4909 | 1 | 0 | 203.5 | 304.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4914 | 1 | 0 | 38889.4914 | 1 | 0 | 241.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4918 | 1 | 0 | 38889.4918 | 1 | 0 | 279.5 | 380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4922 | 1 | 0 | 38889.4922 | 1 | 0 | 316.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4927 | 1 | 0 | 38889.4927 | 1 | 0 | 354.5 | 455.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4931 | 1 | 0 | 38889.4931 | 1 | 0 | 392.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4935 | 1 | 0 | 38889.4936 | 1 | 0 | 430.5 | 531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.494 | 1 | 0 | 38889.494 | 1 | 0 | 467.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4944 | 1 | 0 | 38889.4944 | 1 | 0 | 505.5 | 606.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4948 | 1 | 0 | 38889.4949 | 1 | 0 | 543.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4953 | 1 | 0 | 38889.4953 | 1 | 0 | 581.5 | 682.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4957 | 1 | 0 | 38889.4957 | 1 | 0 | 619.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4962 | 1 | 0 | 38889.4962 | 1 | 0 | 657 | 758 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4966 | 1 | 0 | 38889.4966 | 1 | 0 | 694.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.497 | 1 | 0 | 38889.497 | 1 | 0 | 732.5 | 833.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4975 | 1 | 0 | 38889.4975 | 1 | 0 | 770.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4979 | 1 | 0 | 38889.4979 | 1 | 0 | 808.5 | 909.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4984 | 1 | 0 | 38889.4984 | 1 | 0 | 846 | 947 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4988 | 1 | 0 | 38889.4988 | 1 | 0 | 883.5 | 984.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4992 | 1 | 0 | 38889.4992 | 1 | 0 | 921.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4997 | 1 | 0 | 38889.4997 | 1 | 0 | 959.5 | 1060.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5001 | 1 | 0 | 38889.5001 | 1 | 0 | 997.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5005 | 1 | 0 | 38889.5005 | 1 | 0 | 1034.5 | 1135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.501 | 1 | 0 | 38889.501 | 2 | 0 | 1072.5 | 1173.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5014 | 1 | 0 | 38889.5014 | 1 | 0 | 1110.5 | 1211.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5019 | 1 | 0 | 38889.5019 | 1 | 0 | 1148.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5023 | 1 | 0 | 38889.5023 | 1 | 0 | 1186 | 1287 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5027 | 1 | 1 | 38889.5027 | 1 | 0 | 1223.5 | 1324.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5032 | 1 | 1 | 38889.5032 | 1 | 0 | 1261.5 | 1362.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5036 | 2 | 1 | 38889.5036 | 1 | 0 | 1299.5 | 1400.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38889.504 | 1 | 1 | 38889.5041 | 1 | 0 | 1337.5 | 1438.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5045 | 1 | 0 | 38889.5045 | 1 | 0 | 1375.5 | 1476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5049 | 1 | 0 | 38889.5049 | 1 | 0 | 1412.5 | 1513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5053 | 2 | 1 | 38889.5054 | 1 | 0 | 1450.5 | 1551.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38889.5058 | 1 | 1 | 38889.5058 | 1 | 0 | 1488.5 | 1589.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5062 | 2 | 0 | 38889.5062 | 1 | 0 | 1526.5 | 1627.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5067 | 1 | 0 | 38889.5067 | 1 | 0 | 1564.5 | 1665.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5071 | 1 | 1 | 38889.5071 | 1 | 0 | 1601.5 | 1702.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5075 | 2 | 1 | 38889.5075 | 2 | 0 | 1639.5 | 1740.5 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211302.1897 | 105551 | 210802.284
38889.508 | 1 | 0 | 38889.508 | 1 | 0 | 1677.5 | 1778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5084 | 1 | 1 | 38889.5084 | 1 | 0 | 1715.5 | 1816.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5089 | 1 | 1 | 38889.5089 | 1 | 0 | 1753 | 1854 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5097 | 2 | 0 | 38889.5097 | 1 | 0 | 1828.5 | 1929.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5102 | 2 | 1 | 38889.5102 | 2 | 0 | 1866.5 | 1967.5 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211302.1897 | 105551 | 210802.284
38889.5106 | 1 | 1 | 38889.5106 | 1 | 0 | 1904.5 | 2005.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.511 | 1 | 0 | 38889.511 | 2 | 0 | 1942 | 2043 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38889.5115 | 1 | 0 | 38889.5115 | 1 | 0 | 1979.5 | 2080.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5119 | 1 | 0 | 38889.5119 | 1 | 0 | 2017.5 | 2118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5123 | 1 | 0 | 38889.5124 | 1 | 0 | 2055.5 | 2156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.5128 | 1 | 1 | 38889.5128 | 1 | 0 | 2093.5 | 2194.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38889.5132 | 1 | 1 | 38889.5132 | 1 | 0 | 2130.5 | 2231.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947

## C1-2
Penlight Shakedown Test 20 |  |  | 2006-06-21 | 11:43 |  | Vs = |  | 129 |  | R = | 100
PE/PVC | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38889.4874 | 1 | 0 | 38889.4874 | 1 | 0 | -100.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4878 | 1 | 0 | 38889.4878 | 1 | 0 | -62.5 | 38.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4883 | 1 | 0 | 38889.4883 | 1 | 0 | -25.5 | 75.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4887 | 1 | 0 | 38889.4887 | 1 | 0 | 12.5 | 113.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4891 | 1 | 0 | 38889.4892 | 1 | 0 | 50.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4896 | 1 | 0 | 38889.4896 | 1 | 0 | 88.5 | 189.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.49 | 1 | 0 | 38889.49 | 1 | 0 | 126 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4905 | 1 | 0 | 38889.4905 | 1 | 0 | 163.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4909 | 1 | 0 | 38889.4909 | 1 | 0 | 201.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4913 | 1 | 0 | 38889.4913 | 1 | 0 | 239.5 | 340.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4918 | 1 | 0 | 38889.4918 | 1 | 0 | 277.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4922 | 1 | 0 | 38889.4922 | 1 | 0 | 315 | 416 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4926 | 1 | 0 | 38889.4927 | 1 | 0 | 352.5 | 453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4931 | 1 | 0 | 38889.4931 | 1 | 0 | 390.5 | 491.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4935 | 1 | 0 | 38889.4935 | 1 | 0 | 428.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.494 | 1 | 0 | 38889.494 | 1 | 0 | 466.5 | 567.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4944 | 1 | 0 | 38889.4944 | 1 | 0 | 503.5 | 604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4948 | 1 | 0 | 38889.4948 | 1 | 0 | 541.5 | 642.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4953 | 1 | 0 | 38889.4953 | 1 | 0 | 579.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4957 | 1 | 0 | 38889.4957 | 1 | 0 | 617.5 | 718.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4961 | 1 | 0 | 38889.4962 | 1 | 0 | 655.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4966 | 1 | 0 | 38889.4966 | 1 | 0 | 693 | 794 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.497 | 1 | 0 | 38889.497 | 1 | 0 | 730.5 | 831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4975 | 1 | 0 | 38889.4975 | 1 | 0 | 768.5 | 869.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4979 | 1 | 0 | 38889.4979 | 1 | 0 | 806.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4983 | 1 | 0 | 38889.4983 | 1 | 0 | 844.5 | 945.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4988 | 1 | 0 | 38889.4988 | 1 | 0 | 881.5 | 982.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38889.4992 | 2 | 0 | 38889.4992 | 1 | 0 | 919.5 | 1020.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.4996 | 2 | 0 | 38889.4997 | 1 | 0 | 957.5 | 1058.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5001 | 2 | 0 | 38889.5001 | 1 | 0 | 995.5 | 1096.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5005 | 2 | 0 | 38889.5005 | 1 | 0 | 1033.5 | 1134.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5009 | 2 | 0 | 38889.501 | 1 | 0 | 1070.5 | 1171.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5014 | 2 | 0 | 38889.5014 | 1 | 0 | 1108.5 | 1209.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38889.5018 | 922 | 1024 |  | 49 | 51 | 1146 | 1247 | 56.2882 | 62.5153 | 2.9915 | 3.1136 | 0.56288 | 0.62515 | 0.029915 | 0.031136 | 0.062271 | 0.001221 | 1154.0875 | 85322.6677 | 16.2915
38889.5023 | 118 | 130 | 38889.5023 | 97 | 102 | 1184.5 | 1285.5 | 7.2039 | 7.9365 | 5.9219 | 6.2271 | 0.072039 | 0.079365 | 0.059219 | 0.062271 | 0.007326 | 0.0030525 | 17027.8623 | 45808.4152 | 1431.5058
| 569 | 596 | 38889.5027 | 935 | 1028 | 1223 | 1324 | 34.7375 | 36.3858 | 57.0818 | 62.7595 | 0.34737 | 0.36386 | 0.57082 | 0.62759 | 0.016484 | 0.056777 | 5106.367 | 18411.2403 | 158.2045
38889.5031 | 1019 | 1061 | 38889.5031 | 1189 | 1165 | 1259.5 | 1360.5 | 62.21 | 64.7741 | 72.5885 | 71.1233 | 0.6221 | 0.64774 | 0.72589 | 0.71123 | 0.025641 | 0.014652 | 1687.3086 | 4645.7319 | 3.0466
38889.5036 | 1141 | 1177 | 38889.5036 | 1165 | 1139 | 1297.5 | 1398.5 | 69.6581 | 71.8559 | 71.1233 | 69.536 | 0.69658 | 0.71856 | 0.71123 | 0.69536 | 0.021978 | 0.015873 | 11883.807 | 4230.6727 | 17.0133
38889.504 | 951 | 924 | 38889.504 | 1120 | 1172 | 1335.5 | 1436.5 | 58.0586 | 56.4103 | 68.3761 | 71.5507 | 0.58059 | 0.5641 | 0.68376 | 0.71551 | 0.016484 | 0.031746 | 334.2417 | 288.1569 | 19.1233
38889.5045 | 1005 | 1045 | 38889.5045 | 1195 | 1176 | 1373.5 | 1474.5 | 61.3553 | 63.7973 | 72.9548 | 71.7949 | 0.61355 | 0.63797 | 0.72955 | 0.71795 | 0.02442 | 0.0116 | 1255.4132 | 2165.3818 | 5.7644
38889.5049 | 1010 | 982 | 38889.5049 | 1187 | 1164 | 1411.5 | 1512.5 | 61.6606 | 59.9512 | 72.4664 | 71.0623 | 0.61661 | 0.59951 | 0.72466 | 0.71062 | 0.017094 | 0.014042 | 3638.8104 | 42462.0343 | 12.2949
38889.5053 | 1128 | 1098 | 38889.5053 | 1013 | 986 | 1448.5 | 1549.5 | 68.8645 | 67.033 | 61.8437 | 60.1954 | 0.68864 | 0.67033 | 0.61844 | 0.60195 | 0.018315 | 0.016484 | 27.2372 | 30.6153 | 2.4118
38889.5058 | 1009 | 983 | 38889.5058 | 1070 | 1122 | 1486.5 | 1587.5 | 61.5995 | 60.0122 | 65.3236 | 68.4982 | 0.616 | 0.60012 | 0.65324 | 0.68498 | 0.015873 | 0.031746 | 202.4752 | 189.3072 | 8.0559
38889.5062 | 1148 | 1184 | 38889.5062 | 1137 | 1108 | 1524.5 | 1625.5 | 70.0855 | 72.2833 | 69.4139 | 67.6435 | 0.70085 | 0.72283 | 0.69414 | 0.67643 | 0.021978 | 0.017705 | 46207.5606 | 3491.4354 | 17.98
38889.5066 | 1079 | 1051 | 38889.5067 | 1188 | 1182 | 1562.5 | 1663.5 | 65.873 | 64.1636 | 72.5275 | 72.1612 | 0.65873 | 0.64164 | 0.72527 | 0.72161 | 0.017094 | 0.003663 | 1458.5314 | 2450.192 | 1.5523
38889.5071 | 1075 | 1048 | 38889.5071 | 1112 | 1085 | 1600 | 1701 | 65.6288 | 63.9805 | 67.8877 | 66.2393 | 0.65629 | 0.6398 | 0.67888 | 0.66239 | 0.016484 | 0.016484 | 7726 | 7726 | 0.94012
38889.5075 | 1179 | 1155 | 38889.5075 | 950 | 925 | 1637.5 | 1738.5 | 71.978 | 70.5128 | 57.9976 | 56.4713 | 0.71978 | 0.70513 | 0.57998 | 0.56471 | 0.014652 | 0.015263 | 1860.6305 | 4408.5461 | 18.7081
38889.508 | 1052 | 1026 | 38889.508 | 1201 | 1186 | 1675.5 | 1776.5 | 64.2247 | 62.6374 | 73.3211 | 72.4054 | 0.64225 | 0.62637 | 0.73321 | 0.72405 | 0.015873 | 0.0091575 | 2993.8593 | 10868.7878 | 3.3821
38889.5084 | 1117 | 1169 | 38889.5084 | 1188 | 1164 | 1713.5 | 1814.5 | 68.1929 | 71.3675 | 72.5275 | 71.0623 | 0.68193 | 0.71368 | 0.72527 | 0.71062 | 0.031746 | 0.014652 | 2191.9516 | 17819.7728 | 14.7147
38889.5088 | 950 | 924 | 38889.5088 | 1148 | 1119 | 1751.5 | 1852.5 | 57.9976 | 56.4103 | 70.0855 | 68.315 | 0.57998 | 0.5641 | 0.70085 | 0.68315 | 0.015873 | 0.017705 | 5182.2103 | 25973.6412 | 25.7688
38889.5097 | 1013 | 987 | 38889.5097 | 1071 | 1043 | 1826.5 | 1927.5 | 61.8437 | 60.2564 | 65.3846 | 63.6752 | 0.61844 | 0.60256 | 0.65385 | 0.63675 | 0.015873 | 0.017094 | 21491.4699 | 4726.6499 | 11.2136
38889.5101 | 1020 | 1063 | 38889.5102 | 1204 | 1191 | 1864.5 | 1965.5 | 62.2711 | 64.8962 | 73.5043 | 72.7106 | 0.62271 | 0.64896 | 0.73504 | 0.72711 | 0.026252 | 0.0079365 | 1078.2281 | 1821.0827 | 2.6771
| 1075 | 1122 | 38889.5106 | 1078 | 1094 | 1903 | 2004 | 65.6288 | 68.4982 | 65.812 | 66.7888 | 0.65629 | 0.68498 | 0.65812 | 0.66789 | 0.028694 | 0.009768 | 498.7843 | 696.4185 | 6.545
38889.511 | 1130 | 1180 | 38889.511 | 964 | 940 | 1940.5 | 2041.5 | 68.9866 | 72.0391 | 58.8523 | 57.3871 | 0.68987 | 0.72039 | 0.58852 | 0.57387 | 0.030525 | 0.014652 | 69.7183 | 86.7655 | 7.7552
38889.5114 | 1181 | 1173 | 38889.5115 | 1040 | 1086 | 1977.5 | 2078.5 | 72.1001 | 71.6117 | 63.4921 | 66.3004 | 0.721 | 0.71612 | 0.63492 | 0.663 | 0.004884 | 0.028083 | 603.4356 | 800.9435 | 18.2636
38889.5128 | 1065 | 1114 | 38889.5128 | 1118 | 1183 | 2091.5 | 2192.5 | 65.0183 | 68.0098 | 68.254 | 72.2222 | 0.65018 | 0.6801 | 0.68254 | 0.72222 | 0.029915 | 0.039683 | 1162.8516 | 2708.8144 | 5.7119