## Test Facts
Penlight Ignition Time | 82

## RawData
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15
38880.5934 | 1 | 0 | 1 | EPR | 7-C | Tray
38880.5936 | 1 | 0 | 1 | 650 C | 41 kW/m2 |  | Conductors
38880.5939 | 9 | 0 | 1
38880.5941 | 1 | 1 | 1
38880.5943 | 1 | 0 | 1
38880.5946 | 1 | 0 | 1
38880.5951 | 1 | 0 | 1
38880.5953 | 1 | 0 | 1
38880.5956 | 1 | 0 | 1
38880.5958 | 1 | 0 | 1
38880.596 | 1 | 0 | 1
38880.5963 | 1 | 0 | 1
38880.5965 | 1 | 0 | 1
38880.5968 | 3 | 1 | 1
38880.597 | 310 | 194 | 1
38880.5973 | 2344 | 1 | 1
38880.5975 | 2448 | 0 | 1
38880.5977 | 1872 | 0 | 1
38880.598 | 1696 | 0 | 1
38880.5982 | 2400 | 0 | 1
38880.5985 | 1900 | 0 | 1
38880.5987 | 2360 | 0 | 1
38880.599 | 2461 | 0 | 1
38880.5992 | 2211 | 0 | 1
38880.5994 | 2347 | 0 | 1
38880.5997 | 2033 | 0 | 1
38880.5999 | 1646 | 0 | 1
38880.5934 | 1 | 0 | 2
38880.5936 | 1 | 0 | 2
38880.5939 | 1 | 0 | 2
38880.5941 | 1 | 0 | 2
38880.5944 | 1 | 0 | 2
38880.5946 | 1 | 0 | 2
38880.5951 | 1 | 0 | 2
38880.5953 | 1 | 0 | 2
38880.5956 | 1 | 0 | 2
38880.5958 | 1 | 0 | 2
38880.5961 | 1 | 0 | 2
38880.5963 | 1 | 0 | 2
38880.5965 | 1 | 0 | 2
38880.5968 | 199 | 0 | 2
38880.597 | 641 | 1 | 2
38880.5973 | 2093 | 0 | 2
38880.5975 | 2095 | 0 | 2
38880.5978 | 2003 | 0 | 2
38880.598 | 2172 | 0 | 2
38880.5982 | 2389 | 0 | 2
38880.5985 | 2109 | 0 | 2
38880.5987 | 2208 | 0 | 2
38880.599 | 1971 | 0 | 2
38880.5992 | 2117 | 0 | 2
38880.5995 | 2133 | 0 | 2
38880.5997 | 2068 | 0 | 2
38880.5999 | 2393 | 0 | 2
38880.5934 | 2 | 0 | 3
38880.5936 | 1 | 0 | 3
38880.5939 | 1 | 0 | 3
38880.5941 | 1 | 0 | 3
38880.5944 | 1 | 0 | 3
38880.5946 | 1 | 0 | 3
38880.5951 | 1 | 0 | 3
38880.5953 | 1 | 0 | 3
38880.5956 | 2 | 0 | 3
38880.5958 | 1 | 0 | 3
38880.5961 | 2 | 0 | 3
38880.5963 | 1 | 0 | 3
38880.5965 | 1 | 0 | 3
38880.5968 | 2 | 0 | 3
38880.597 | 4 | 0 | 3
38880.5973 | 1956 | 0 | 3
38880.5975 | 2169 | 0 | 3
38880.5978 | 1989 | 0 | 3
38880.598 | 1587 | 0 | 3
38880.5982 | 2148 | 0 | 3
38880.5985 | 2183 | 97 | 3
38880.5987 | 2219 | 1 | 3
38880.599 | 2283 | 0 | 3
38880.5992 | 2130 | 0 | 3
38880.5995 | 2335 | 3 | 3
38880.5997 | 1862 | 31 | 3
38880.5999 | 1721 | 8 | 3
38880.5934 | 1 | 0 | 4
38880.5936 | 1 | 0 | 4
38880.5939 | 1 | 0 | 4
38880.5941 | 1 | 0 | 4
38880.5944 | 1 | 0 | 4
38880.5946 | 1 | 0 | 4
38880.5951 | 1 | 0 | 4
38880.5953 | 1 | 0 | 4
38880.5956 | 2 | 0 | 4
38880.5958 | 1 | 0 | 4
38880.5961 | 1 | 0 | 4
38880.5963 | 1 | 0 | 4
38880.5966 | 1 | 0 | 4
38880.5968 | 51 | 0 | 4
38880.597 | 1754 | 0 | 4
38880.5973 | 1723 | 0 | 4
38880.5975 | 1622 | 0 | 4
38880.5978 | 2275 | 0 | 4
38880.598 | 2285 | 0 | 4
38880.5983 | 1632 | 0 | 4
38880.5985 | 2032 | 1 | 4
38880.5987 | 2410 | 2 | 4
38880.599 | 1398 | 0 | 4
38880.5992 | 2124 | 0 | 4
38880.5995 | 1899 | 27 | 4
38880.5997 | 1380 | 23 | 4
38880.6 | 627 | 395 | 4
38880.5934 | 1 | 0 | 5
38880.5936 | 1 | 0 | 5
38880.5939 | 1 | 0 | 5
38880.5941 | 1 | 0 | 5
38880.5944 | 1 | 0 | 5
38880.5946 | 1 | 0 | 5
38880.5951 | 1 | 0 | 5
38880.5953 | 2 | 0 | 5
38880.5956 | 2 | 0 | 5
38880.5958 | 1 | 0 | 5
38880.5961 | 1 | 0 | 5
38880.5963 | 2 | 0 | 5
38880.5966 | 1 | 0 | 5
38880.5968 | 2 | 0 | 5
38880.597 | 26 | 0 | 5
38880.5973 | 2334 | 0 | 5
38880.5975 | 2418 | 0 | 5
38880.5978 | 1868 | 0 | 5
38880.598 | 1884 | 0 | 5
38880.5983 | 1951 | 0 | 5
38880.5985 | 1885 | 0 | 5
38880.5987 | 2363 | 0 | 5
38880.599 | 2102 | 0 | 5
38880.5992 | 2331 | 0 | 5
38880.5995 | 1856 | 7 | 5
38880.5997 | 1851 | 4 | 5
38880.6 | 1432 | 366 | 5
38880.5934 | 1 | 0 | 6
38880.5936 | 1 | 0 | 6
38880.5939 | 1 | 0 | 6
38880.5941 | 1 | 0 | 6
38880.5944 | 1 | 0 | 6
38880.5946 | 2 | 0 | 6
38880.5951 | 1 | 0 | 6
38880.5953 | 1 | 0 | 6
38880.5956 | 2 | 0 | 6
38880.5958 | 1 | 0 | 6
38880.5961 | 1 | 0 | 6
38880.5963 | 2 | 0 | 6
38880.5966 | 1 | 0 | 6
38880.5968 | 1 | 0 | 6
38880.597 | 2483 | 0 | 6
38880.5973 | 2346 | 0 | 6
38880.5975 | 2520 | 0 | 6
38880.5978 | 1952 | 0 | 6
38880.598 | 2159 | 0 | 6
38880.5983 | 2023 | 0 | 6
38880.5985 | 2068 | 0 | 6
38880.5987 | 1934 | 0 | 6
38880.599 | 2021 | 0 | 6
38880.5992 | 2111 | 0 | 6
38880.5995 | 2148 | 2 | 6
38880.5997 | 2099 | 1 | 6
38880.6 | 2122 | 1 | 6
38880.5934 | 1 | 0 | 7
38880.5936 | 1 | 1 | 7
38880.5939 | 1 | 0 | 7
38880.5941 | 1 | 0 | 7
38880.5944 | 1 | 0 | 7
38880.5946 | 1 | 0 | 7
38880.5951 | 1 | 1 | 7
38880.5953 | 1 | 0 | 7
38880.5956 | 2 | 0 | 7
38880.5958 | 1 | 0 | 7
38880.5961 | 1 | 0 | 7
38880.5963 | 2 | 0 | 7
38880.5966 | 1 | 0 | 7
38880.5968 | 1 | 0 | 7
38880.597 | 396 | 0 | 7
38880.5973 | 2096 | 0 | 7
38880.5975 | 2326 | 0 | 7
38880.5978 | 2088 | 0 | 7
38880.598 | 1350 | 0 | 7
38880.5983 | 2299 | 0 | 7
38880.5985 | 2228 | 0 | 7
38880.5987 | 2320 | 0 | 7
38880.599 | 2463 | 0 | 7
38880.5992 | 1954 | 1 | 7
38880.5995 | 2258 | 0 | 7
38880.5997 | 1427 | 0 | 7
38880.6 | 921 | 340 | 7
38880.5934 | 1 | 1 | 8
38880.5937 | 2 | 0 | 8
38880.5939 | 1 | 1 | 8
38880.5941 | 1 | 0 | 8
38880.5944 | 1 | 0 | 8
38880.5946 | 1 | 0 | 8
38880.5951 | 1 | 0 | 8
38880.5954 | 1 | 0 | 8
38880.5956 | 2 | 0 | 8
38880.5958 | 1 | 0 | 8
38880.5961 | 1 | 0 | 8
38880.5963 | 1 | 0 | 8
38880.5966 | 1 | 0 | 8
38880.5968 | 1 | 0 | 8
38880.5971 | 1927 | 0 | 8
38880.5973 | 2097 | 0 | 8
38880.5975 | 2153 | 0 | 8
38880.5978 | 1966 | 0 | 8
38880.598 | 1963 | 0 | 8
38880.5983 | 2056 | 0 | 8
38880.5985 | 2484 | 0 | 8
38880.5988 | 2064 | 0 | 8
38880.599 | 2469 | 0 | 8
38880.5992 | 2381 | 0 | 8
38880.5995 | 2087 | 0 | 8
38880.5997 | 1884 | 0 | 8
38880.6 | 1661 | 4 | 8
38880.5934 | 1 | 0 | 9
38880.5937 | 1 | 0 | 9
38880.5939 | 1 | 0 | 9
38880.5941 | 1 | 0 | 9
38880.5944 | 1 | 0 | 9
38880.5946 | 1 | 0 | 9
38880.5951 | 1 | 0 | 9
38880.5954 | 1 | 0 | 9
38880.5956 | 2 | 0 | 9
38880.5958 | 1 | 0 | 9
38880.5961 | 1 | 0 | 9
38880.5963 | 1 | 0 | 9
38880.5966 | 2 | 0 | 9
38880.5968 | 1 | 0 | 9
38880.5971 | 619 | 0 | 9
38880.5973 | 2507 | 0 | 9
38880.5975 | 2044 | 0 | 9
38880.5978 | 2053 | 201 | 9
38880.598 | 2225 | 96 | 9
38880.5983 | 2176 | 2 | 9
38880.5985 | 2288 | 92 | 9
38880.5988 | 1976 | 0 | 9
38880.599 | 2012 | 0 | 9
38880.5992 | 2249 | 0 | 9
38880.5995 | 1782 | 0 | 9
38880.5997 | 1495 | 0 | 9
38880.6 | 1379 | 1 | 9
38880.5934 | 1 | 0 | 10
38880.5937 | 1 | 1 | 10
38880.5939 | 1 | 0 | 10
38880.5942 | 1 | 0 | 10
38880.5944 | 1 | 0 | 10
38880.5946 | 1 | 0 | 10
38880.5951 | 1 | 0 | 10
38880.5954 | 1 | 0 | 10
38880.5956 | 1 | 0 | 10
38880.5959 | 1 | 0 | 10
38880.5961 | 1 | 0 | 10
38880.5963 | 2 | 0 | 10
38880.5966 | 1 | 0 | 10
38880.5968 | 1 | 0 | 10
38880.5971 | 2094 | 0 | 10
38880.5973 | 2076 | 0 | 10
38880.5976 | 2375 | 0 | 10
38880.5978 | 1981 | 172 | 10
38880.598 | 2268 | 8 | 10
38880.5983 | 1921 | 2 | 10
38880.5985 | 1944 | 71 | 10
38880.5988 | 2438 | 0 | 10
38880.599 | 2257 | 0 | 10
38880.5993 | 2067 | 0 | 10
38880.5995 | 1559 | 0 | 10
38880.5997 | 1963 | 1 | 10
38880.6 | 1751 | 0 | 10
38880.5934 | 1 | 0 | 11
38880.5937 | 1 | 0 | 11
38880.5939 | 1 | 1 | 11
38880.5942 | 1 | 0 | 11
38880.5944 | 1 | 0 | 11
38880.5946 | 1 | 0 | 11
38880.5951 | 1 | 0 | 11
38880.5954 | 1 | 0 | 11
38880.5956 | 1 | 0 | 11
38880.5959 | 1 | 0 | 11
38880.5961 | 1 | 0 | 11
38880.5963 | 1 | 0 | 11
38880.5966 | 1 | 0 | 11
38880.5968 | 1 | 1 | 11
38880.5971 | 1014 | 570 | 11
38880.5973 | 1962 | 0 | 11
38880.5976 | 2159 | 0 | 11
38880.5978 | 2013 | 2 | 11
38880.598 | 2169 | 0 | 11
38880.5983 | 2440 | 0 | 11
38880.5985 | 1776 | 0 | 11
38880.5988 | 2168 | 0 | 11
38880.599 | 2436 | 0 | 11
38880.5993 | 2177 | 0 | 11
38880.5995 | 2117 | 0 | 11
38880.5997 | 1506 | 1 | 11
38880.6 | 1484 | 0 | 11
38880.5934 | 1 | 1 | 12
38880.5937 | 1 | 0 | 12
38880.5939 | 1 | 0 | 12
38880.5942 | 1 | 0 | 12
38880.5944 | 1 | 0 | 12
38880.5947 | 1 | 0 | 12
38880.5951 | 1 | 0 | 12
38880.5954 | 1 | 0 | 12
38880.5956 | 1 | 0 | 12
38880.5959 | 1 | 0 | 12
38880.5961 | 1 | 0 | 12
38880.5964 | 1 | 0 | 12
38880.5966 | 1 | 0 | 12
38880.5968 | 14 | 0 | 12
38880.5971 | 863 | 234 | 12
38880.5973 | 2279 | 0 | 12
38880.5976 | 2126 | 0 | 12
38880.5978 | 1708 | 4 | 12
38880.5981 | 2329 | 0 | 12
38880.5983 | 2334 | 0 | 12
38880.5985 | 2020 | 0 | 12
38880.5988 | 2028 | 0 | 12
38880.5993 | 1909 | 0 | 12
38880.5995 | 2085 | 0 | 12
38880.5998 | 2050 | 0 | 12
38880.6 | 2367 | 0 | 12
38880.5934 | 1 | 0 | 13
38880.5937 | 1 | 0 | 13
38880.5939 | 1 | 0 | 13
38880.5942 | 1 | 0 | 13
38880.5944 | 1 | 0 | 13
38880.5947 | 2 | 0 | 13
38880.5951 | 1 | 0 | 13
38880.5954 | 1 | 0 | 13
38880.5956 | 1 | 0 | 13
38880.5959 | 1 | 0 | 13
38880.5961 | 1 | 0 | 13
38880.5964 | 1 | 0 | 13
38880.5966 | 1 | 0 | 13
38880.5968 | 170 | 5 | 13
38880.5971 | 468 | 1 | 13
38880.5973 | 2291 | 0 | 13
38880.5976 | 2134 | 0 | 13
38880.5978 | 2330 | 1 | 13
38880.5981 | 2427 | 0 | 13
38880.5983 | 2089 | 0 | 13
38880.5985 | 1979 | 0 | 13
38880.5988 | 2358 | 0 | 13
38880.599 | 2256 | 0 | 13
38880.5993 | 2559 | 0 | 13
38880.5995 | 2023 | 0 | 13
38880.5998 | 2023 | 0 | 13
38880.6 | 2340 | 0 | 13
38880.5934 | 1 | 0 | 14
38880.5937 | 1 | 0 | 14
38880.5939 | 1 | 0 | 14
38880.5942 | 1 | 0 | 14
38880.5944 | 1 | 0 | 14
38880.5947 | 1 | 1 | 14
38880.5952 | 1 | 0 | 14
38880.5954 | 1 | 0 | 14
38880.5956 | 1 | 0 | 14
38880.5959 | 1 | 0 | 14
38880.5961 | 1 | 0 | 14
38880.5964 | 1 | 0 | 14
38880.5966 | 1 | 0 | 14
38880.5969 | 205 | 24 | 14
38880.5971 | 2039 | 0 | 14
38880.5973 | 1950 | 0 | 14
38880.5976 | 1341 | 0 | 14
38880.5978 | 2380 | 0 | 14
38880.5981 | 2136 | 0 | 14
38880.5983 | 1637 | 0 | 14
38880.5986 | 1586 | 0 | 14
38880.5988 | 2288 | 0 | 14
38880.599 | 1328 | 0 | 14
38880.5993 | 2191 | 0 | 14
38880.5995 | 2118 | 0 | 14
38880.5998 | 1720 | 0 | 14
38880.6 | 2213 | 0 | 14
38880.5934 | 1 | 0 | 15
38880.5937 | 1 | 0 | 15
38880.5939 | 1 | 0 | 15
38880.5942 | 1 | 0 | 15
38880.5944 | 1 | 0 | 15
38880.5947 | 1 | 0 | 15
38880.5952 | 1 | 0 | 15
38880.5954 | 1 | 0 | 15
38880.5956 | 1 | 0 | 15
38880.5959 | 1 | 0 | 15
38880.5961 | 1 | 0 | 15
38880.5964 | 1 | 0 | 15
38880.5966 | 1 | 0 | 15
38880.5969 | 114 | 0 | 15
38880.5971 | 517 | 0 | 15
38880.5973 | 2238 | 0 | 15
38880.5976 | 2414 | 0 | 15
38880.5978 | 2286 | 0 | 15
38880.5981 | 2202 | 0 | 15
38880.5983 | 2538 | 0 | 15
38880.5986 | 2469 | 0 | 15
38880.5988 | 2135 | 0 | 15
38880.599 | 2555 | 0 | 15
38880.5993 | 2255 | 0 | 15
38880.5995 | 2277 | 0 | 15
38880.5998 | 2009 | 0 | 15
38880.6 | 2521 | 0 | 15
38880.5935 | 1 | 0 | 16
38880.5937 | 1 | 0 | 16
38880.5939 | 1 | 0 | 16
38880.5942 | 1 | 0 | 16
38880.5944 | 1 | 0 | 16
38880.5947 | 1 | 0 | 16
38880.5952 | 1 | 0 | 16
38880.5954 | 1 | 0 | 16
38880.5956 | 1 | 0 | 16
38880.5959 | 1 | 0 | 16
38880.5961 | 1 | 0 | 16
38880.5964 | 1 | 0 | 16
38880.5966 | 1 | 0 | 16
38880.5969 | 2461 | 0 | 16
38880.5971 | 2507 | 1 | 16
38880.5973 | 2148 | 0 | 16
38880.5976 | 2159 | 0 | 16
38880.5978 | 1995 | 0 | 16
38880.5981 | 2133 | 0 | 16
38880.5983 | 2512 | 0 | 16
38880.5986 | 1933 | 0 | 16
38880.5988 | 2477 | 0 | 16
38880.5991 | 2257 | 0 | 16
38880.5993 | 2127 | 0 | 16
38880.5995 | 1932 | 0 | 16
38880.5998 | 2341 | 0 | 16
38880.6 | 2045 | 0 | 16
38880.5935 | 1 | 0 | 17
38880.5937 | 1 | 1 | 17
38880.5939 | 1 | 0 | 17
38880.5942 | 1 | 0 | 17
38880.5944 | 1 | 0 | 17
38880.5947 | 1 | 0 | 17
38880.5952 | 1 | 0 | 17
38880.5954 | 1 | 0 | 17
38880.5956 | 1 | 0 | 17
38880.5959 | 1 | 1 | 17
38880.5961 | 2 | 0 | 17
38880.5964 | 1 | 0 | 17
38880.5966 | 1 | 0 | 17
38880.5969 | 152 | 0 | 17
38880.5971 | 505 | 0 | 17
38880.5973 | 2001 | 0 | 17
38880.5976 | 2061 | 0 | 17
38880.5978 | 2500 | 0 | 17
38880.5981 | 1993 | 0 | 17
38880.5983 | 2445 | 0 | 17
38880.5986 | 2506 | 0 | 17
38880.5988 | 2546 | 0 | 17
38880.5991 | 2197 | 0 | 17
38880.5993 | 2013 | 0 | 17
38880.5995 | 2531 | 0 | 17
38880.5998 | 2323 | 0 | 17
38880.6 | 2240 | 0 | 17
38880.5935 | 1 | 0 | 18
38880.5937 | 1 | 0 | 18
38880.594 | 1 | 0 | 18
38880.5942 | 1 | 0 | 18
38880.5944 | 1 | 0 | 18
38880.5947 | 1 | 0 | 18
38880.5952 | 1 | 0 | 18
38880.5954 | 1 | 0 | 18
38880.5957 | 1 | 0 | 18
38880.5959 | 1 | 0 | 18
38880.5961 | 1 | 0 | 18
38880.5964 | 2 | 0 | 18
38880.5966 | 1 | 0 | 18
38880.5969 | 203 | 0 | 18
38880.5971 | 1999 | 0 | 18
38880.5974 | 2499 | 0 | 18
38880.5976 | 2041 | 0 | 18
38880.5978 | 2311 | 0 | 18
38880.5981 | 2519 | 0 | 18
38880.5986 | 1931 | 0 | 18
38880.5988 | 2326 | 0 | 18
38880.5991 | 2290 | 0 | 18
38880.5993 | 2393 | 0 | 18
38880.5995 | 2269 | 0 | 18
38880.5998 | 1877 | 0 | 18
38880.6 | 2122 | 0 | 18
38880.5935 | 1 | 0 | 19
38880.5937 | 1 | 0 | 19
38880.594 | 1 | 0 | 19
38880.5942 | 1 | 0 | 19
38880.5944 | 1 | 0 | 19
38880.5947 | 1 | 0 | 19
38880.5952 | 1 | 0 | 19
38880.5954 | 1 | 0 | 19
38880.5957 | 1 | 0 | 19
38880.5959 | 1 | 0 | 19
38880.5961 | 1 | 0 | 19
38880.5964 | 1 | 0 | 19
38880.5966 | 1 | 0 | 19
38880.5969 | 68 | 0 | 19
38880.5971 | 879 | 0 | 19
38880.5974 | 2486 | 0 | 19
38880.5976 | 2454 | 0 | 19
38880.5978 | 2165 | 0 | 19
38880.5981 | 2343 | 0 | 19
38880.5983 | 2234 | 0 | 19
38880.5986 | 2535 | 0 | 19
38880.5988 | 2147 | 0 | 19
38880.5991 | 2518 | 0 | 19
38880.5993 | 2391 | 0 | 19
38880.5995 | 2298 | 0 | 19
38880.5998 | 1975 | 0 | 19
38880.6 | 2049 | 0 | 19
38880.5935 | 1 | 0 | 20
38880.5937 | 1 | 0 | 20
38880.594 | 1 | 0 | 20
38880.5942 | 1 | 0 | 20
38880.5945 | 1 | 0 | 20
38880.5947 | 1 | 0 | 20
38880.5952 | 1 | 0 | 20
38880.5954 | 1 | 0 | 20
38880.5957 | 1 | 0 | 20
38880.5959 | 1 | 0 | 20
38880.5962 | 1 | 0 | 20
38880.5964 | 1 | 0 | 20
38880.5966 | 2 | 0 | 20
38880.5969 | 105 | 0 | 20
38880.5971 | 1901 | 0 | 20
38880.5974 | 2311 | 0 | 20
38880.5976 | 2487 | 0 | 20
38880.5979 | 2162 | 0 | 20
38880.5981 | 2437 | 0 | 20
38880.5983 | 1973 | 0 | 20
38880.5986 | 2207 | 0 | 20
38880.5988 | 1890 | 0 | 20
38880.5991 | 2282 | 0 | 20
38880.5993 | 2043 | 0 | 20
38880.5996 | 1755 | 0 | 20
38880.5998 | 2190 | 0 | 20
38880.6 | 1972 | 0 | 20
38880.5935 | 1 | 1 | 21
38880.5937 | 1 | 0 | 21
38880.594 | 1 | 0 | 21
38880.5942 | 1 | 0 | 21
38880.5945 | 1 | 0 | 21
38880.5947 | 1 | 0 | 21
38880.5952 | 1 | 0 | 21
38880.5954 | 1 | 0 | 21
38880.5957 | 1 | 0 | 21
38880.5959 | 1 | 1 | 21
38880.5962 | 1 | 0 | 21
38880.5964 | 1 | 0 | 21
38880.5966 | 1 | 0 | 21
38880.5969 | 466 | 225 | 21
38880.5971 | 609 | 31 | 21
38880.5974 | 2155 | 0 | 21
38880.5976 | 2204 | 0 | 21
38880.5979 | 2041 | 0 | 21
38880.5981 | 2459 | 0 | 21
38880.5983 | 2262 | 0 | 21
38880.5986 | 2184 | 0 | 21
38880.5988 | 2411 | 0 | 21
38880.5991 | 2177 | 0 | 21
38880.5993 | 1990 | 0 | 21
38880.5996 | 2279 | 0 | 21
38880.5998 | 2418 | 0 | 21
38880.6 | 2298 | 0 | 21
38880.5935 | 1 | 0 | 22
38880.5937 | 1 | 0 | 22
38880.594 | 1 | 0 | 22
38880.5942 | 1 | 0 | 22
38880.5945 | 1 | 0 | 22
38880.5947 | 1 | 0 | 22
38880.5952 | 1 | 0 | 22
38880.5954 | 1 | 0 | 22
38880.5957 | 1 | 0 | 22
38880.5959 | 1 | 0 | 22
38880.5962 | 1 | 0 | 22
38880.5964 | 1 | 0 | 22
38880.5967 | 1 | 0 | 22
38880.5969 | 312 | 24 | 22
38880.5971 | 922 | 36 | 22
38880.5974 | 1983 | 0 | 22
38880.5976 | 1857 | 0 | 22
38880.5979 | 2396 | 0 | 22
38880.5981 | 2048 | 0 | 22
38880.5984 | 2413 | 0 | 22
38880.5986 | 2426 | 0 | 22
38880.5988 | 2135 | 0 | 22
38880.5991 | 2363 | 0 | 22
38880.5993 | 2432 | 0 | 22
38880.5996 | 2013 | 0 | 22
38880.5998 | 2134 | 0 | 22
38880.6001 | 2125 | 0 | 22
38880.5935 | 1 | 0 | 23
38880.5937 | 1 | 0 | 23
38880.594 | 1 | 0 | 23
38880.5942 | 1 | 0 | 23
38880.5945 | 1 | 0 | 23
38880.5947 | 1 | 0 | 23
38880.5952 | 1 | 0 | 23
38880.5954 | 1 | 0 | 23
38880.5957 | 2 | 0 | 23
38880.5959 | 1 | 0 | 23
38880.5962 | 1 | 0 | 23
38880.5964 | 1 | 0 | 23
38880.5967 | 1 | 0 | 23
38880.5969 | 225 | 0 | 23
38880.5971 | 2418 | 0 | 23
38880.5974 | 1654 | 0 | 23
38880.5976 | 1803 | 0 | 23
38880.5979 | 2070 | 0 | 23
38880.5981 | 1827 | 0 | 23
38880.5984 | 1754 | 0 | 23
38880.5986 | 1578 | 0 | 23
38880.5988 | 1958 | 0 | 23
38880.5991 | 1648 | 0 | 23
38880.5993 | 2276 | 0 | 23
38880.5996 | 1720 | 1 | 23
38880.5998 | 2194 | 0 | 23
38880.6001 | 935 | 397 | 23
38880.5935 | 1 | 0 | 24
38880.5938 | 1 | 0 | 24
38880.594 | 1 | 0 | 24
38880.5942 | 1 | 0 | 24
38880.5945 | 1 | 0 | 24
38880.5947 | 1 | 0 | 24
38880.5952 | 2 | 0 | 24
38880.5955 | 1 | 0 | 24
38880.5957 | 1 | 0 | 24
38880.5959 | 1 | 0 | 24
38880.5962 | 1 | 0 | 24
38880.5964 | 1 | 0 | 24
38880.5967 | 1 | 0 | 24
38880.5969 | 2470 | 0 | 24
38880.5972 | 2495 | 0 | 24
38880.5974 | 2561 | 0 | 24
38880.5979 | 2124 | 0 | 24
38880.5981 | 2346 | 0 | 24
38880.5984 | 2294 | 0 | 24
38880.5986 | 2412 | 0 | 24
38880.5989 | 2336 | 0 | 24
38880.5991 | 2105 | 0 | 24
38880.5993 | 2012 | 0 | 24
38880.5996 | 2266 | 1 | 24
38880.5998 | 1907 | 0 | 24
38880.6001 | 1822 | 0 | 24
38880.5935 | 1 | 0 | 25
38880.5938 | 1 | 0 | 25
38880.594 | 1 | 0 | 25
38880.5942 | 1 | 0 | 25
38880.5945 | 1 | 0 | 25
38880.5947 | 1 | 0 | 25
38880.5952 | 1 | 0 | 25
38880.5955 | 1 | 0 | 25
38880.5957 | 1 | 0 | 25
38880.5959 | 1 | 1 | 25
38880.5962 | 1 | 0 | 25
38880.5964 | 1 | 0 | 25
38880.5967 | 1 | 0 | 25
38880.5969 | 136 | 0 | 25
38880.5972 | 2196 | 0 | 25
38880.5974 | 1901 | 0 | 25
38880.5976 | 2337 | 0 | 25
38880.5979 | 1957 | 0 | 25
38880.5981 | 2142 | 0 | 25
38880.5984 | 1285 | 0 | 25
38880.5986 | 1571 | 1 | 25
38880.5989 | 1503 | 0 | 25
38880.5991 | 1704 | 0 | 25
38880.5993 | 1894 | 0 | 25
38880.5996 | 1431 | 0 | 25
38880.5998 | 1716 | 0 | 25
38880.6001 | 496 | 0 | 25
38880.5935 | 1 | 0 | 26
38880.5938 | 1 | 0 | 26
38880.594 | 1 | 0 | 26
38880.5942 | 1 | 0 | 26
38880.5945 | 1 | 0 | 26
38880.5947 | 1 | 0 | 26
38880.5952 | 1 | 0 | 26
38880.5955 | 1 | 0 | 26
38880.5957 | 1 | 0 | 26
38880.5959 | 1 | 0 | 26
38880.5962 | 1 | 0 | 26
38880.5964 | 1 | 0 | 26
38880.5967 | 1 | 0 | 26
38880.5969 | 2326 | 0 | 26
38880.5972 | 2106 | 0 | 26
38880.5974 | 2164 | 0 | 26
38880.5977 | 2494 | 0 | 26
38880.5979 | 2082 | 0 | 26
38880.5981 | 2079 | 0 | 26
38880.5984 | 1928 | 0 | 26
38880.5986 | 2049 | 0 | 26
38880.5989 | 2424 | 0 | 26
38880.5991 | 2444 | 0 | 26
38880.5994 | 2039 | 0 | 26
38880.5996 | 1962 | 0 | 26
38880.5998 | 2344 | 0 | 26
38880.6001 | 1985 | 2 | 26
38880.5935 | 2 | 0 | 27
38880.5938 | 1 | 0 | 27
38880.594 | 1 | 0 | 27
38880.5942 | 1 | 0 | 27
38880.5945 | 1 | 0 | 27
38880.5947 | 1 | 0 | 27
38880.5952 | 1 | 0 | 27
38880.5955 | 1 | 0 | 27
38880.5957 | 1 | 0 | 27
38880.5959 | 1 | 0 | 27
38880.5962 | 1 | 0 | 27
38880.5964 | 2 | 0 | 27
38880.5967 | 1 | 0 | 27
38880.5969 | 426 | 0 | 27
38880.5972 | 2477 | 0 | 27
38880.5974 | 1699 | 0 | 27
38880.5977 | 2328 | 0 | 27
38880.5979 | 2295 | 0 | 27
38880.5981 | 2344 | 0 | 27
38880.5984 | 1981 | 0 | 27
38880.5986 | 1775 | 1 | 27
38880.5989 | 1556 | 0 | 27
38880.5991 | 2093 | 0 | 27
38880.5994 | 2203 | 0 | 27
38880.5996 | 1343 | 0 | 27
38880.5998 | 1797 | 2 | 27
38880.6001 | 790 | 0 | 27
38880.5935 | 1 | 0 | 28
38880.5938 | 1 | 0 | 28
38880.594 | 1 | 0 | 28
38880.5943 | 1 | 0 | 28
38880.5945 | 1 | 0 | 28
38880.5947 | 1 | 0 | 28
38880.5952 | 1 | 0 | 28
38880.5955 | 1 | 0 | 28
38880.5957 | 1 | 0 | 28
38880.596 | 1 | 0 | 28
38880.5962 | 1 | 0 | 28
38880.5964 | 1 | 0 | 28
38880.5967 | 3 | 0 | 28
38880.5969 | 861 | 0 | 28
38880.5972 | 1621 | 0 | 28
38880.5974 | 2454 | 0 | 28
38880.5977 | 2195 | 0 | 28
38880.5979 | 2164 | 0 | 28
38880.5981 | 2397 | 0 | 28
38880.5984 | 2172 | 0 | 28
38880.5986 | 2035 | 0 | 28
38880.5989 | 2008 | 0 | 28
38880.5991 | 2289 | 0 | 28
38880.5994 | 2170 | 0 | 28
38880.5996 | 1915 | 0 | 28
38880.5998 | 1266 | 0 | 28
38880.6001 | 1796 | 0 | 28
38880.5935 | 1 | 0 | 29
38880.5938 | 1 | 0 | 29
38880.594 | 2 | 0 | 29
38880.5943 | 1 | 0 | 29
38880.5945 | 1 | 0 | 29
38880.5947 | 1 | 0 | 29
38880.5952 | 1 | 0 | 29
38880.5955 | 1 | 0 | 29
38880.5957 | 1 | 0 | 29
38880.596 | 1 | 0 | 29
38880.5962 | 1 | 0 | 29
38880.5964 | 1 | 0 | 29
38880.5967 | 1 | 0 | 29
38880.5969 | 551 | 10 | 29
38880.5972 | 2159 | 0 | 29
38880.5974 | 1448 | 1 | 29
38880.5977 | 1880 | 0 | 29
38880.5979 | 1930 | 0 | 29
38880.5981 | 1943 | 0 | 29
38880.5984 | 1833 | 0 | 29
38880.5986 | 1898 | 2 | 29
38880.5989 | 1250 | 0 | 29
38880.5991 | 1668 | 0 | 29
38880.5994 | 2028 | 0 | 29
38880.5996 | 1084 | 1 | 29
38880.5998 | 766 | 0 | 29
38880.6001 | 539 | 0 | 29
38880.5935 | 1 | 0 | 30
38880.5938 | 2 | 0 | 30
38880.594 | 1 | 0 | 30
38880.5943 | 1 | 0 | 30
38880.5945 | 1 | 0 | 30
38880.5948 | 1 | 1 | 30
38880.5952 | 1 | 0 | 30
38880.5955 | 1 | 0 | 30
38880.5957 | 1 | 0 | 30
38880.596 | 1 | 0 | 30
38880.5962 | 1 | 0 | 30
38880.5965 | 1 | 0 | 30
38880.5967 | 1 | 0 | 30
38880.5972 | 1146 | 0 | 30
38880.5974 | 2410 | 0 | 30
38880.5977 | 1988 | 0 | 30
38880.5979 | 1877 | 0 | 30
38880.5982 | 1979 | 0 | 30
38880.5984 | 1926 | 0 | 30
38880.5986 | 2142 | 0 | 30
38880.5989 | 2206 | 0 | 30
38880.5991 | 1962 | 0 | 30
38880.5994 | 2089 | 0 | 30
38880.5996 | 2320 | 0 | 30
38880.5999 | 2376 | 0 | 30
38880.6001 | 2016 | 0 | 30
38880.5935 | 1 | 0 | 31
38880.5938 | 1 | 0 | 31
38880.594 | 1 | 0 | 31
38880.5943 | 1 | 0 | 31
38880.5945 | 1 | 0 | 31
38880.5948 | 1 | 0 | 31
38880.5952 | 1 | 0 | 31
38880.5955 | 1 | 0 | 31
38880.5957 | 1 | 0 | 31
38880.596 | 1 | 0 | 31
38880.5962 | 1 | 0 | 31
38880.5965 | 1 | 0 | 31
38880.5967 | 1 | 0 | 31
38880.5969 | 1926 | 0 | 31
38880.5972 | 2095 | 0 | 31
38880.5974 | 2231 | 0 | 31
38880.5977 | 2263 | 0 | 31
38880.5979 | 2520 | 0 | 31
38880.5982 | 2057 | 0 | 31
38880.5984 | 1970 | 0 | 31
38880.5986 | 1970 | 0 | 31
38880.5989 | 2297 | 0 | 31
38880.5991 | 1976 | 0 | 31
38880.5994 | 1842 | 0 | 31
38880.5996 | 2247 | 0 | 31
38880.5999 | 1936 | 62 | 31
38880.6001 | 1946 | 42 | 31
38880.5936 | 1 | 0 | 32
38880.5938 | 1 | 0 | 32
38880.594 | 1 | 0 | 32
38880.5943 | 1 | 0 | 32
38880.5945 | 1 | 0 | 32
38880.5948 | 1 | 0 | 32
38880.5953 | 1 | 0 | 32
38880.5955 | 1 | 0 | 32
38880.5957 | 1 | 0 | 32
38880.596 | 1 | 0 | 32
38880.5962 | 1 | 0 | 32
38880.5965 | 1 | 0 | 32
38880.5967 | 1 | 0 | 32
38880.597 | 2377 | 1 | 32
38880.5972 | 2521 | 0 | 32
38880.5974 | 2037 | 0 | 32
38880.5977 | 2385 | 0 | 32
38880.5979 | 2046 | 0 | 32
38880.5982 | 2397 | 0 | 32
38880.5984 | 2338 | 0 | 32
38880.5987 | 2486 | 0 | 32
38880.5989 | 2300 | 0 | 32
38880.5991 | 2342 | 0 | 32
38880.5994 | 2402 | 0 | 32
38880.5996 | 2296 | 0 | 32
38880.5999 | 1792 | 87 | 32
38880.6001 | 1703 | 73 | 32
38880.5936 | 2 | 0 | 33
38880.5938 | 1 | 0 | 33
38880.594 | 1 | 0 | 33
38880.5943 | 1 | 0 | 33
38880.5945 | 1 | 0 | 33
38880.5948 | 1 | 0 | 33
38880.5953 | 1 | 0 | 33
38880.5955 | 1 | 0 | 33
38880.5957 | 1 | 0 | 33
38880.596 | 1 | 0 | 33
38880.5962 | 1 | 0 | 33
38880.5965 | 1 | 0 | 33
38880.5967 | 1 | 0 | 33
38880.597 | 2253 | 1 | 33
38880.5972 | 2469 | 0 | 33
38880.5974 | 2255 | 0 | 33
38880.5977 | 2199 | 0 | 33
38880.5979 | 2506 | 0 | 33
38880.5982 | 2398 | 0 | 33
38880.5984 | 2212 | 0 | 33
38880.5987 | 2300 | 0 | 33
38880.5989 | 1986 | 0 | 33
38880.5991 | 2105 | 0 | 33
38880.5994 | 2137 | 0 | 33
38880.5996 | 2011 | 0 | 33
38880.5999 | 1906 | 1 | 33
38880.6001 | 1679 | 0 | 33
38880.5936 | 1 | 0 | 34
38880.5938 | 1 | 0 | 34
38880.5941 | 1 | 0 | 34
38880.5943 | 1 | 0 | 34
38880.5945 | 1 | 0 | 34
38880.5948 | 1 | 0 | 34
38880.5953 | 1 | 0 | 34
38880.5955 | 1 | 0 | 34
38880.5958 | 1 | 0 | 34
38880.596 | 1 | 0 | 34
38880.5962 | 1 | 0 | 34
38880.5965 | 2 | 0 | 34
38880.5967 | 185 | 0 | 34
38880.597 | 1577 | 0 | 34
38880.5972 | 1457 | 0 | 34
38880.5975 | 2459 | 0 | 34
38880.5977 | 2062 | 0 | 34
38880.5979 | 2199 | 0 | 34
38880.5982 | 2027 | 0 | 34
38880.5984 | 1886 | 0 | 34
38880.5987 | 1990 | 0 | 34
38880.5989 | 2224 | 0 | 34
38880.5992 | 1671 | 0 | 34
38880.5994 | 1705 | 0 | 34
38880.5996 | 1739 | 0 | 34
38880.5999 | 2120 | 0 | 34
38880.6001 | 1865 | 0 | 34
38880.5936 | 1 | 1 | 35
38880.5938 | 1 | 0 | 35
38880.5941 | 1 | 0 | 35
38880.5943 | 1 | 0 | 35
38880.5945 | 1 | 0 | 35
38880.5948 | 1 | 0 | 35
38880.5953 | 1 | 0 | 35
38880.5955 | 1 | 0 | 35
38880.5958 | 1 | 0 | 35
38880.596 | 1 | 0 | 35
38880.5962 | 1 | 0 | 35
38880.5965 | 1 | 0 | 35
38880.5967 | 2 | 0 | 35
38880.597 | 2099 | 0 | 35
38880.5972 | 2115 | 0 | 35
38880.5975 | 1992 | 0 | 35
38880.5977 | 2457 | 0 | 35
38880.5979 | 1967 | 0 | 35
38880.5982 | 1946 | 0 | 35
38880.5984 | 2444 | 0 | 35
38880.5987 | 1933 | 0 | 35
38880.5989 | 2274 | 0 | 35
38880.5992 | 2040 | 0 | 35
38880.5994 | 2040 | 0 | 35
38880.5996 | 2196 | 0 | 35
38880.5999 | 1740 | 0 | 35
38880.6001 | 1801 | 0 | 35
38880.5936 | 1 | 0 | 36
38880.5938 | 1 | 0 | 36
38880.5941 | 1 | 0 | 36
38880.5943 | 1 | 0 | 36
38880.5945 | 1 | 0 | 36
38880.5948 | 1 | 0 | 36
38880.5953 | 1 | 0 | 36
38880.5955 | 1 | 0 | 36
38880.5958 | 1 | 0 | 36
38880.596 | 1 | 0 | 36
38880.5965 | 1 | 0 | 36
38880.5967 | 4 | 0 | 36
38880.597 | 563 | 0 | 36
38880.5972 | 1301 | 1 | 36
38880.5975 | 2032 | 0 | 36
38880.5977 | 1857 | 0 | 36
38880.598 | 2377 | 0 | 36
38880.5982 | 2536 | 0 | 36
38880.5984 | 2417 | 0 | 36
38880.5987 | 1946 | 0 | 36
38880.5989 | 2098 | 0 | 36
38880.5992 | 2465 | 0 | 36
38880.5994 | 2070 | 0 | 36
38880.5997 | 1999 | 0 | 36
38880.5999 | 2070 | 0 | 36
38880.6001 | 1854 | 0 | 36
38880.5936 | 1 | 0 | 37
38880.5938 | 1 | 0 | 37
38880.5941 | 1 | 0 | 37
38880.5943 | 1 | 0 | 37
38880.5945 | 1 | 0 | 37
38880.5948 | 1 | 0 | 37
38880.5953 | 1 | 0 | 37
38880.5955 | 1 | 0 | 37
38880.5958 | 2 | 0 | 37
38880.596 | 1 | 1 | 37
38880.5963 | 1 | 0 | 37
38880.5965 | 1 | 0 | 37
38880.5967 | 1 | 0 | 37
38880.597 | 2061 | 0 | 37
38880.5972 | 2540 | 0 | 37
38880.5975 | 1977 | 0 | 37
38880.5977 | 2111 | 0 | 37
38880.598 | 2210 | 0 | 37
38880.5982 | 2385 | 0 | 37
38880.5984 | 2464 | 0 | 37
38880.5987 | 1979 | 0 | 37
38880.5989 | 1981 | 0 | 37
38880.5992 | 2359 | 0 | 37
38880.5994 | 2436 | 0 | 37
38880.5997 | 1881 | 0 | 37
38880.5999 | 1820 | 1 | 37
38880.6001 | 1965 | 0 | 37
38880.5936 | 1 | 0 | 38
38880.5938 | 1 | 0 | 38
38880.5941 | 1 | 0 | 38
38880.5943 | 1 | 0 | 38
38880.5946 | 1 | 0 | 38
38880.5948 | 1 | 1 | 38
38880.5953 | 1 | 0 | 38
38880.5955 | 1 | 0 | 38
38880.5958 | 1 | 0 | 38
38880.596 | 1 | 0 | 38
38880.5963 | 1 | 0 | 38
38880.5965 | 1 | 0 | 38
38880.5967 | 576 | 0 | 38
38880.597 | 1718 | 0 | 38
38880.5972 | 1438 | 0 | 38
38880.5975 | 2517 | 0 | 38
38880.5977 | 2094 | 0 | 38
38880.598 | 2383 | 0 | 38
38880.5982 | 2092 | 0 | 38
38880.5984 | 2130 | 0 | 38
38880.5987 | 2448 | 0 | 38
38880.5989 | 2004 | 0 | 38
38880.5992 | 1864 | 0 | 38
38880.5994 | 1747 | 0 | 38
38880.5997 | 2234 | 0 | 38
38880.5999 | 2198 | 0 | 38
38880.6002 | 1743 | 2 | 38
38880.5936 | 1 | 0 | 39
38880.5938 | 1 | 0 | 39
38880.5941 | 1 | 0 | 39
38880.5943 | 1 | 0 | 39
38880.5946 | 1 | 0 | 39
38880.5948 | 1 | 0 | 39
38880.5953 | 1 | 0 | 39
38880.5955 | 1 | 0 | 39
38880.5958 | 1 | 0 | 39
38880.596 | 1 | 0 | 39
38880.5963 | 1 | 0 | 39
38880.5965 | 1 | 1 | 39
38880.5967 | 3 | 0 | 39
38880.597 | 2407 | 0 | 39
38880.5972 | 2152 | 0 | 39
38880.5975 | 2375 | 0 | 39
38880.5977 | 2055 | 0 | 39
38880.598 | 2369 | 0 | 39
38880.5982 | 1994 | 0 | 39
38880.5984 | 2128 | 0 | 39
38880.5987 | 2048 | 0 | 39
38880.5989 | 2393 | 0 | 39
38880.5992 | 1941 | 0 | 39
38880.5994 | 2078 | 0 | 39
38880.5997 | 2237 | 0 | 39
38880.5999 | 1676 | 0 | 39
38880.6002 | 2233 | 0 | 39
38880.5936 | 1 | 0 | 40
38880.5938 | 1 | 0 | 40
38880.5941 | 1 | 0 | 40
38880.5943 | 1 | 0 | 40
38880.5946 | 1 | 0 | 40
38880.5948 | 1 | 0 | 40
38880.5953 | 1 | 0 | 40
38880.5955 | 1 | 0 | 40
38880.5958 | 1 | 0 | 40
38880.596 | 1 | 0 | 40
38880.5963 | 1 | 0 | 40
38880.5965 | 1 | 0 | 40
38880.5968 | 35 | 0 | 40
38880.597 | 598 | 0 | 40
38880.5972 | 1298 | 0 | 40
38880.5975 | 2021 | 0 | 40
38880.5977 | 1833 | 0 | 40
38880.598 | 2088 | 0 | 40
38880.5982 | 2342 | 0 | 40
38880.5985 | 2217 | 0 | 40
38880.5987 | 1936 | 0 | 40
38880.5989 | 2091 | 0 | 40
38880.5992 | 2394 | 0 | 40
38880.5994 | 1918 | 0 | 40
38880.5997 | 2052 | 0 | 40
38880.5999 | 2260 | 0 | 40
38880.6002 | 2184 | 0 | 40
38880.5936 | 1 | 0 | 41
38880.5938 | 1 | 0 | 41
38880.5941 | 1 | 0 | 41
38880.5943 | 1 | 0 | 41
38880.5946 | 1 | 0 | 41
38880.5948 | 1 | 0 | 41
38880.5953 | 1 | 0 | 41
38880.5955 | 1 | 0 | 41
38880.5958 | 1 | 0 | 41
38880.596 | 1 | 0 | 41
38880.5963 | 1 | 0 | 41
38880.5965 | 1 | 0 | 41
38880.5968 | 693 | 0 | 41
38880.597 | 1739 | 0 | 41
38880.5972 | 1386 | 283 | 41
38880.5975 | 2518 | 0 | 41
38880.5977 | 2170 | 0 | 41
38880.598 | 2322 | 0 | 41
38880.5982 | 2057 | 0 | 41
38880.5985 | 2062 | 0 | 41
38880.5987 | 2442 | 0 | 41
38880.5989 | 1900 | 0 | 41
38880.5992 | 2048 | 0 | 41
38880.5994 | 1232 | 0 | 41
38880.5997 | 2240 | 0 | 41
38880.5999 | 2132 | 0 | 41
38880.6002 | 1797 | 0 | 41
38880.5936 | 1 | 0 | 42
38880.5939 | 1 | 0 | 42
38880.5941 | 1 | 0 | 42
38880.5943 | 1 | 0 | 42
38880.5946 | 1 | 0 | 42
38880.5948 | 1 | 0 | 42
38880.5951 | 1 | 0 | 42
38880.5953 | 1 | 0 | 42
38880.5958 | 1 | 0 | 42
38880.596 | 1 | 0 | 42
38880.5963 | 1 | 0 | 42
38880.5965 | 1 | 0 | 42
38880.5968 | 207 | 26 | 42
38880.597 | 532 | 1 | 42
38880.5973 | 2129 | 15 | 42
38880.5975 | 1964 | 0 | 42
38880.5977 | 1654 | 3 | 42
38880.598 | 2411 | 0 | 42
38880.5982 | 1988 | 0 | 42
38880.5985 | 2400 | 0 | 42
38880.5987 | 1972 | 0 | 42
38880.599 | 1915 | 0 | 42
38880.5992 | 2338 | 0 | 42
38880.5994 | 2338 | 0 | 42
38880.5997 | 2321 | 0 | 42
38880.5999 | 2069 | 0 | 42
38880.6002 | 1831 | 0 | 42

## C-G
Average Conductor to Ground Resistances
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15
EPR | 7-C | Tray
650 C | 41 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-79 | 228351.5 |  | -74.8333 | 102254821.4067 | -72 | 229276.5 | -70.1667 | 108683643.5733 | -69 | 251404.6667 | -68.1667 | 252921.3333 | -67.3333 | #DIV/0! | -79 | #DIV/0!
-58 | 52243590.0367 |  | -53.8333 | 109555223.4067 | -51 | 250054.6667 | -49.1667 | 254854.6667 | -48 | 230568.1667 | -47.1667 | 252921.3333 | -46.3333 | 227484.8333 | -58 | 227484.8333
-37 | 100652462.1474 |  | -32.8333 | 253454.6667 | -30 | 229834.8333 | -28.1667 | 254854.6667 | -27 | 251404.6667 | -26.1667 | 252921.3333 | -25.3333 | 247704.6667 | -37 | 229834.8333
-16 | 102414930.0733 |  | -11.8333 | 253454.6667 | -9 | 250054.6667 | -7.1667 | 254854.6667 | -6 | 251404.6667 | -5.1667 | 252921.3333 | -4.3333 | 247704.6667 | -16 | 247704.6667
5 | 248571.3333 |  | 9.1667 | 253454.6667 | 12 | 250054.6667 | 13.8333 | 254854.6667 | 15 | 251404.6667 | 15.8333 | 252921.3333 | 16.6667 | 247704.6667 | 5 | 247704.6667
26 | 248571.3333 |  | 30.1667 | 231993.1667 | 33 | 250054.6667 | 34.8333 | 233718.1667 | 36 | 251404.6667 | 36.8333 | 252921.3333 | 37.6667 | 247704.6667 | 26 | 231993.1667
68 | 104321921.4067 |  | 72.1667 | 253454.6667 | 75 | 250054.6667 | 76.8333 | 233376.5 | 78 | 251404.6667 | 77.0833 | 252921.3333 | 77.9167 | 247704.6667 | 68 | 233376.5
89 | 227434.8333 |  | 93.1667 | 253454.6667 | 96 | 250054.6667 | 97.8333 | 254854.6667 | 99 | 251404.6667 | 98.0833 | 252921.3333 | 98.9167 | 247704.6667 | 89 | 227434.8333
110 | 165350.3333 |  | 114.1667 | 253454.6667 | 117 | 208356.6667 | 118.8333 | 233718.1667 | 120 | 209265 | 120.8333 | 252921.3333 | 121.6667 | 247704.6667 | 110 | 165350.3333
131 | 248571.3333 |  | 135.1667 | 211556590.1467 | 138 | 105158031.4067 | 139.8333 | 254854.6667 | 141 | 109041597.4067 | 141.8333 | 252921.3333 | 142.6667 | 247704.6667 | 131 | 247704.6667
152 | 228351.5 |  | 156.1667 | 232101.5 | 159 | 250054.6667 | 160.75 | 254854.6667 | 162 | 251404.6667 | 162.8333 | 252921.3333 | 163.5833 | 247704.6667 | 152 | 228351.5
173 | 206598.3333 |  | 177.1667 | 253454.6667 | 180 | 229276.5 | 181.8333 | 233718.1667 | 183 | 97988426.24 | 183.8333 | 210873.3333 | 184.6667 | 247704.6667 | 173 | 206598.3333
194 | 227543.1667 |  | 198.1667 | 253454.6667 | 201 | 250054.6667 | 202.8333 | 233584.8333 | 204 | 224478.2222 | 204.8333 | 77432.1071 | 205.6667 | 134557.9421 | 194 | 77432.1071
215 | 7285831.6474 |  | 219.1667 | 1825.0653 | 221.9167 | 1600.599 | 223.8333 | 42268.6911 | 225 | 41856.6153 | 225.8333 | 42485.3271 | 226.5833 | 3306.664 | 215 | 1600.599
236 | 12692.1978 |  | 240.1667 | 344.983 | 243 | 16.4322 | 244.8333 | 8.6697 | 246 | 15.1741 | 246.8333 | 94.1097 | 247.6667 | 130.0869 | 236 | 8.6697
257 | 13.9282 |  | 261.1667 | 15.2043 | 264 | 47.1333 | 265.8333 | 13.6978 | 267 | 15.6144 | 267.8333 | 6.3915 | 268.6667 | 17.9757 | 257 | 6.3915
278 | 10.4477 |  | 282.1667 | 14.3438 | 286.75 | 38.0294 | 288.5833 | 11.9681 | 288 | 14.625 | 288.8333 | 13.9383 | 289.6667 | 32.342 | 278 | 10.4477
299 | 27.7284 |  | 303.1667 | 14.7305 | 307.75 | 17.0024 | 309.5833 | 16.6325 | 309 | 16.7699 | 309.8333 | 17.6312 | 310.6667 | 17.5884 | 299 | 14.7305
320 | 42.5232 |  | 324.1667 | 12.5129 | 328.75 | 19.3797 | 330.5833 | 18.3476 | 330 | 14.0705 | 330.8333 | 15.0058 | 331.6667 | 13.4247 | 320 | 12.5129
341 | 11.9408 |  | 345.0833 | 9.4564 | 349.75 | 51.0897 | 351.5833 | 13.6441 | 350.9167 | 15.5235 | 351.8333 | 25.396 | 352.6667 | 9.053 | 341 | 9.053
362 | 23.7681 |  | 366.1667 | 11.3311 | 370.75 | 45.6476 | 372.5833 | 22.7532 | 372 | 17.5742 | 372.8333 | 19.7764 | 373.6667 | 20.2947 | 362 | 11.3311
383 | 11.8495 |  | 387.1667 | 10.6678 | 391.75 | 44.3762 | 393.5833 | 17.8521 | 393 | 12.584 | 393.8333 | 22.8394 | 394.6667 | 19.4922 | 383 | 10.6678
403.9167 | 9.2303 |  | 408.1667 | 12.0253 | 412.75 | 55.9672 | 414.5833 | 23.4809 | 414 | 9.5738 | 414.8333 | 24.0633 | 415.5833 | 11.0581 | 403.9167 | 9.2303
425 | 14.6786 |  | 429.1667 | 15.0139 | 433.75 | 18.3984 | 435.5833 | 22.6227 | 435 | 10.4015 | 435.8333 | 43.6414 | 436.6667 | 17.4433 | 425 | 10.4015
446 | 19.2393 |  | 450.1667 | 12.8769 | 454.75 | 67.274 | 456.5833 | 23.4952 | 456 | 19.2396 | 456.8333 | 35.0099 | 457.6667 | 16.7236 | 446 | 12.8769
467 | 49.7001 |  | 471.1667 | 19.4926 | 475.75 | 75.0993 | 477.5833 | 30.9347 | 477 | 35.4832 | 477.8333 | 32.7036 | 478.6667 | 15.1611 | 467 | 15.1611
488 | 354.4081 |  | 492.1667 | 10.3688 | #REF! | 256.7272 | #REF! | #DIV/0! | 498 | 35.7828 | 498.8333 | 39.2395 | 499.6667 | 21.2775 | 488 | #DIV/0!

## C-C
Conductor to Conductor Resistances
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15
EPR | 7-C | Tray
650 C | 41 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-81.5 | 247637.9994 | -80.5 | 121218.9988 | -79.5 | 253537.9994 | -78.5 | 249937.9994 | -77.5 | 252237.9994 | -76.5 | 245537.9994 | -75.5 | 257437.9994 | -74.5 | 257037.9994 | -73.5 | 256137.9994 | -72.5 | 255037.9994 | -71.5 | 247238.0808 | -70.5 | 257637.9994 | -69.5 | 250937.9994 | -68.5 | 124568.9988 | -67.5 | 242537.9994 | -66.5 | 253637.9994 | -65.5 | 126018.9988 | -64.5 | 254938.0784 | -63.5 | 255537.9994 | -62.5 | 242237.9994 | -61.5 | 253337.9994 | -81.5 | 121218.9988
-60.5 | 247637.9994 | -59.5 | 242537.9994 | -58.5 | 253537.9994 | -57.5 | 249638.16 | -56.5 | 252237.9994 | -55.5 | 245537.9994 | -54.5 | 257437.9994 | -53.5 | 257037.9994 | -52.5 | 255938.0781 | -51.5 | 255037.9994 | -50.5 | 247437.9994 | -49.5 | 257637.9994 | -48.5 | 250937.9994 | -47.5 | 249237.9994 | -46.5 | 242537.9994 | -45.5 | 253637.9994 | -44.5 | 252137.9994 | -43.5 | 255137.9994 | -42.5 | 255537.9994 | -41.5 | 242237.9994 | -40.5 | 253337.9994 | -60.5 | 242237.9994
-39.5 | 27426.4389 | -38.5 | 242537.9994 | -37.5 | 253537.9994 | -36.5 | 249937.9994 | -35.5 | 252237.9994 | -34.5 | 245338.0814 | -33.5 | 257437.9994 | -32.5 | 257037.9994 | -31.5 | 256137.9994 | -30.5 | 255037.9994 | -29.5 | 247437.9994 | -28.5 | 257637.9994 | -27.5 | 250937.9994 | -26.5 | 249237.9994 | -25.5 | 121218.9988 | -24.5 | 253637.9994 | -23.5 | 252137.9994 | -22.5 | 255137.9994 | -21.5 | 255537.9994 | -20.5 | 242237.9994 | -19.5 | 253337.9994 | -39.5 | 27426.4389
-18.5 | 247438.0807 | -17.5 | 242537.9994 | -16.5 | 253537.9994 | -15.5 | 249937.9994 | -14.5 | 252237.9994 | -13.5 | 245537.9994 | -12.5 | 257437.9994 | -11.5 | 257037.9994 | -10.5 | 256137.9994 | -9.5 | 255037.9994 | -8.5 | 247437.9994 | -7.5 | 257637.9994 | -6.5 | 250937.9994 | -5.5 | 249237.9994 | -4.5 | 242537.9994 | -3.5 | 253637.9994 | -2.5 | 252137.9994 | -1.5 | 255137.9994 | -0.5 | 255537.9994 | 0.5 | 242237.9994 | 1.5 | 253337.9994 | -18.5 | 242237.9994
2.5 | 247637.9994 | 3.5 | 242537.9994 | 4.5 | 253537.9994 | 5.5 | 249937.9994 | 6.5 | 252237.9994 | 7.5 | 245537.9994 | 8.5 | 257437.9994 | 9.5 | 257037.9994 | 10.5 | 256137.9994 | 11.5 | 255037.9994 | 12.5 | 247437.9994 | 13.5 | 257637.9994 | 14.5 | 250937.9994 | 15.5 | 249237.9994 | 16.5 | 242537.9994 | 17.5 | 253637.9994 | 18.5 | 252137.9994 | 19.5 | 255137.9994 | 20.5 | 255537.9994 | 21.5 | 242237.9994 | 22.5 | 253337.9994 | 2.5 | 242237.9994
23.5 | 247637.9994 | 24.5 | 242537.9994 | 25.5 | 253537.9994 | 26.5 | 249937.9994 | 27.5 | 252237.9994 | 28.5 | 245537.9994 | 29.5 | 128668.9988 | 30.5 | 257037.9994 | 31.5 | 256137.9994 | 32.5 | 255037.9994 | 33.5 | 247437.9994 | 34.5 | 257637.9994 | 35.5 | 250937.9994 | 36.5 | 249237.9994 | 37.5 | 242537.9994 | 38.5 | 253637.9994 | 39.5 | 252137.9994 | 40.5 | 255137.9994 | 41.5 | 255537.9994 | 42.5 | 242237.9994 | 43.5 | 253337.9994 | 23.5 | 128668.9988
65.5 | 247637.9994 | 66.5 | 242537.9994 | 67.5 | 253537.9994 | 68.5 | 249738.08 | 69.5 | 252237.9994 | 70.5 | 245537.9994 | 71.5 | 257437.9994 | 72.5 | 257037.9994 | 73.5 | 256137.9994 | 74.5 | 255037.9994 | 75.5 | 247437.9994 | 76.5 | 257637.9994 | 77.5 | 250937.9994 | 78.5 | 249237.9994 | 79.5 | 242537.9994 | 80.5 | 253637.9994 | 81.5 | 252137.9994 | 82.5 | 255137.9994 | 83.5 | 255537.9994 | 84.5 | 242237.9994 | 75 | 253337.9994 | 65.5 | 242237.9994
86.5 | 247637.9994 | 87.5 | 242537.9994 | 88.5 | 126718.9988 | 89.5 | 249937.9994 | 90.5 | 252237.9994 | 91.5 | 245537.9994 | 92.5 | 257437.9994 | 93.5 | 257037.9994 | 94.5 | 256137.9994 | 95.5 | 255037.9994 | 96.5 | 247437.9994 | 97.5 | 257637.9994 | 98.5 | 250937.9994 | 99.5 | 249237.9994 | 100.5 | 242537.9994 | 101.5 | 253637.9994 | 102.5 | 252137.9994 | 103.5 | 255137.9994 | 104.5 | 255537.9994 | 105.5 | 242237.9994 | 96 | 253337.9994 | 86.5 | 126718.9988
107.5 | 247637.9994 | 108.5 | 121218.9988 | 109.5 | 126718.9988 | 110.5 | 124918.9988 | 111.5 | 126068.9988 | 112.5 | 245537.9994 | 113.5 | 257437.9994 | 114.5 | 257037.9994 | 115.5 | 256137.9994 | 116.5 | 255037.9994 | 117.5 | 247437.9994 | 118.5 | 128768.9988 | 119.5 | 250937.9994 | 120.5 | 249237.9994 | 121.5 | 242537.9994 | 122.5 | 253637.9994 | 123.5 | 252137.9994 | 124.5 | 255137.9994 | 125.5 | 127718.9988 | 126.5 | 242237.9994 | 127.5 | 253337.9994 | 107.5 | 121218.9988
128.5 | 247637.9994 | 129.5 | 242537.9994 | 130.5 | 253537.9994 | 131.5 | 249937.9994 | 132.5 | 252237.9994 | 133.5 | 245537.9994 | 134.5 | 257437.9994 | 135.5 | 257037.9994 | 136.5 | 255938.0781 | 137.5 | 255037.9994 | 138.5 | 247238.0808 | 139.5 | 257637.9994 | 140.5 | 250738.0797 | 141.5 | 249237.9994 | 142.5 | 242537.9994 | 143.5 | 253637.9994 | 144.5 | 252137.9994 | 145.5 | 255137.9994 | 146.5 | 255338.0782 | 147.5 | 242237.9994 | 148.5 | 253337.9994 | 128.5 | 242237.9994
149.5 | 247637.9994 | 150.5 | 121218.9988 | 151.5 | 253537.9994 | 152.5 | 249937.9994 | 153.5 | 252237.9994 | 154.5 | 245537.9994 | 155.5 | 257437.9994 | 156.5 | 257037.9994 | 157.5 | 128018.9988 | 158.5 | 255037.9994 | 159.5 | 247437.9994 | 160.5 | 257637.9994 | 161.5 | 250937.9994 | 162.5 | 249237.9994 | 163.5 | 242537.9994 | 164.5 | 253637.9994 | 165.5 | 252137.9994 | 166 | 255137.9994 | 167.5 | 255537.9994 | 168.5 | 242237.9994 | 169.5 | 253337.9994 | 149.5 | 121218.9988
170.5 | 247637.9994 | 171.5 | 242537.9994 | 172.5 | 126718.9988 | 173.5 | 124918.9988 | 174.5 | 252237.9994 | 175.5 | 245537.9994 | 176.5 | 257437.9994 | 177.5 | 257037.9994 | 178.5 | 256137.9994 | 179.5 | 255037.9994 | 180.5 | 247437.9994 | 181.5 | 257637.9994 | 182.5 | 250937.9994 | 183.5 | 124568.9988 | 184.5 | 242537.9994 | 185.5 | 253637.9994 | 186.5 | 252137.9994 | 187.5 | 255137.9994 | 188.5 | 255537.9994 | 189.5 | 242038.0825 | 190.5 | 253337.9994 | 170.5 | 124568.9988
191.5 | 247637.9994 | 192.5 | 242537.9994 | 193.5 | 253537.9994 | 194.5 | 249937.9994 | 195.5 | 126068.9988 | 196.5 | 245537.9994 | 197.5 | 257437.9994 | 198.5 | 257037.9994 | 199.5 | 256137.9994 | 200.5 | 255037.9994 | 201.5 | 247437.9994 | 202.5 | 257637.9994 | 203.5 | 250937.9994 | 204.5 | 249237.9994 | 205.5 | 242537.9994 | 206.5 | 253637.9994 | 207.5 | 252137.9994 | 208.5 | 127518.9988 | 209.5 | 255537.9994 | 210.5 | 80679.3315 | 211.5 | 265.2883 | 191.5 | 265.2883
212.5 | 227470.1307 | 213.5 | 121218.9988 | 214.5 | 126718.9988 | 215.5 | 249937.9994 | 216.5 | 252237.9994 | 217.5 | 244039.1399 | 218.5 | 44630.5772 | 219.5 | 2155.5269 | 220.5 | 1585.6835 | 221.5 | 3651.9879 | 222.5 | 700.6068 | 223.5 | 1045.3649 | 224.5 | 1745.7846 | 225.5 | 485.0404 | 226 | 15991.6818 | 227.5 | 30.5677 | 228.5 | 10058.797 | 229.5 | 20.3184 | 230.5 | 22.7777 | 231.5 | 0.78896 | 232.5 | 44.6761 | 212.5 | 0.78896
233.5 | 754.3244 | 234.5 | 60559.4976 | 235.5 | 9655.2918 | 236.5 | 531.1673 | 237.5 | 307.2764 | 238.5 | 111.626 | 239.5 | 43870.0349 | 240.5 | 397.0499 | 241.5 | 407.0937 | 242.5 | 189.7228 | 243.5 | 3786.9689 | 244.5 | 5.1152 | 245.5 | 12.9754 | 246.5 | 0.85093 | 247.5 | 11.0664 | 248.5 | 19.837 | 249.5 | 0.65468 | 250.5 | 19.3887 | 251.5 | 0.90579 | 252.5 | 11.2968 | 253.5 | 85.7012 | 233.5 | 0.65468
254.5 | 2053.9531 | 255.5 | 22.8539 | 256.5 | 7.246 | 257.5 | 18.0133 | 258.5 | 0.87715 | 259.5 | 24 | 260.5 | 11.0143 | 261.5 | 13.53 | 262.5 | 26.8334 | 263.5 | 1.1122 | 264.5 | 13.5512 | 265.5 | 54.8173 | 266.5 | 30.8952 | 267.5 | 45.7185 | 268.5 | 659.8094 | 269.5 | 12.3708 | 270.5 | 10.4805 | 271.5 | 26.9154 | 272.5 | 28.0991 | 273.5 | 0.58711 | 274.5 | 0.88672 | 254.5 | 0.58711
275.5 | 0.29434 | 276.5 | 10.5421 | 277.5 | 3.4196 | 278.5 | 6.077 | 279.5 | 22.2052 | 280.5 | 12.4559 | 281.5 | 19.3804 | 282.5 | 5.0457 | 283.5 | 23.0688 | 284.5 | 2.47 | 285.5 | 10.9675 | 297 | 41.8488 | 287.5 | 5.9922 | 288.5 | 5.6827 | 289.5 | 27.915 | 290.5 | 10.7431 | 291.5 | 13.3633 | 292.5 | 2.382 | 293.5 | 19.8093 | 294.5 | 16.6715 | 295.5 | 15.4669 | 275.5 | 0.29434
296.5 | 31.1958 | 297.5 | 20.7757 | 298.5 | 34.6401 | 299.5 | 18.4753 | 300.5 | 39.2581 | 301.5 | 6784.762 | 302.5 | 1853.9774 | 303.5 | 11.0882 | 304.5 | 0.96895 | 305.5 | 16.5249 | 306.5 | 20.0367 | 318 | 23.2474 | 308.5 | 27.0822 | 309.5 | 7.2429 | 310.5 | 24.5409 | 311.5 | 0.84878 | 312.5 | 0.87628 | 313.5 | 28.5592 | 314.5 | 14.3241 | 315.5 | 0.84921 | 316.5 | 7.7288 | 296.5 | 0.84878
317.5 | 45.0365 | 318.5 | 51.9221 | 319.5 | 33.4772 | 320.5 | 84.3892 | 321.5 | 21.7022 | 322.5 | 11.9252 | 323.5 | 4.632 | 324.5 | 15.4304 | 325.5 | 27.3523 | 326.5 | 7.4633 | 327.5 | 0.8351 | 339 | 39.9563 | 329.5 | 15.8903 | 330.5 | 4.9419 | 331.5 | 23.6918 | 332.5 | 22.0976 | 333.5 | 3.7228 | 334.5 | 29.9723 | 335.5 | 5.7297 | 336.5 | 20.3163 | 337.5 | 21.9518 | 317.5 | 0.8351
338.5 | 1.759 | 339.5 | 11.6486 | 340.5 | 28.813 | 341.5 | 7.3559 | 342.5 | 4146.2397 | 343.5 | 0.81831 | 344.5 | 22.0076 | 345.5 | 0.23424 | 346 | 3.3081 | 347.5 | 12.8429 | 348.5 | 8.0523 | 360 | 45.8722 | 350.5 | 94.5758 | 351.5 | 24.6553 | 352.5 | 31.253 | 353.5 | 27.5983 | 354.5 | 12.6812 | 355.5 | 2.9425 | 356.5 | 2.2449 | 357.5 | 12.5815 | 358.5 | 21.65 | 338.5 | 0.23424
359.5 | 29.2285 | 360.5 | 24.6045 | 361.5 | 33.4052 | 362.5 | 10.8651 | 363.5 | 48.785 | 364.5 | 37.2254 | 365.5 | 28.9272 | 366.5 | 2.6393 | 367.5 | 0.71989 | 368.5 | 0.90147 | 369.5 | 12.0082 | 381 | 62.3687 | 371.5 | 17246.3836 | 372.5 | 13188.2282 | 373.5 | 3084.6764 | 374.5 | 27.5983 | 375.5 | 8.2645 | 376.5 | 30.8623 | 377.5 | 27.9672 | 378.5 | 17.0788 | 379.5 | 2.2921 | 359.5 | 0.71989
380.5 | 3.5329 | 381.5 | 140.5969 | 382.5 | 5.8947 | 383.5 | 6.3586 | 384.5 | 26.4951 | 385.5 | 11.9781 | 386.5 | 7.7793 | 387.5 | 19.1359 | 388.5 | 0.91097 | 389.5 | 17.5239 | 390.5 | 1.1983 | 402 | 30.4379 | 392.5 | 66.107 | 393.5 | 59.293 | 394.5 | 93.3473 | 395.5 | 9.0626 | 396.5 | 25.7956 | 397.5 | 10.8536 | 398.5 | 27.8355 | 399.5 | 0.19139 | 400.5 | 32.2285 | 380.5 | 0.19139
401.5 | 0.83686 | 402.5 | 4.8866 | 403.5 | 19.3818 | 404.5 | 0.013998 | 405.5 | 24.1882 | 406 | 0.65056 | 407.5 | 12.7796 | 408.5 | 0.91873 | 409.5 | 15.2896 | 410.5 | 0.21159 | 411.5 | 12.377 | 423 | 55.3883 | 413.5 | 46.2825 | 414.5 | 17.8517 | 415.5 | 44.4481 | 416.5 | 27.2036 | 417.5 | 18.5429 | 418.5 | 23.8712 | 419.5 | 6.9269 | 420.5 | 23.6672 | 421.5 | 22.4987 | 401.5 | 0.013998
422.5 | 10.6981 | 423.5 | 12.6142 | 424.5 | 7.3877 | 425.5 | 2603.9028 | 426.5 | 10.8271 | 427.5 | 11.5042 | 428.5 | 0.92218 | 429.5 | 12.6535 | 430.5 | 26.0627 | 431.5 | 5.2479 | 432.5 | 23.1761 | 444 | 11.8522 | 434.5 | 31.3875 | 435.5 | 11.8362 | 436.5 | 18.4059 | 437.5 | 36.6268 | 438.5 | 16.7291 | 439.5 | 23.8712 | 440.5 | 3.4545 | 441.5 | 15.3522 | 442.5 | 104.9605 | 422.5 | 0.92218
443.5 | 4.1223 | 444.5 | 907.334 | 445.5 | 1477.2711 | 446.5 | 9.3558 | 447.5 | 40.5159 | 448.5 | 14.7387 | 449.5 | 26.0699 | 450.5 | 11.5383 | 451.5 | 0.30535 | 452.5 | 9.6232 | 453.5 | 7.2256 | 465 | 22274.5588 | 455.5 | 74.5547 | 456.5 | 84.8376 | 457.5 | 5881.0246 | 458.5 | 11.5512 | 459.5 | 24.2014 | 460.5 | 14.8879 | 461.5 | 34.757 | 462.5 | 6.966 | 463.5 | 11.7744 | 443.5 | 0.30535
464.5 | 20.6172 | 465.5 | 772.5923 | 466.5 | 2941.7266 | 467.5 | 74.3482 | 468.5 | 67.8753 | 469.5 | 15706.4072 | 470.5 | 26.0699 | 471.5 | 26.7665 | 472.5 | 8.8866 | 473.5 | 27.9781 | 474.5 | 0.89685 | 486 | 16.1346 | 476.5 | 45.2449 | 477.5 | 17090.6184 | 478.5 | 216.2921 | 479.5 | 295.1906 | 480.5 | 9816.7843 | 481.5 | 45.6262 | 482.5 | 10309.3235 | 483.5 | 43.5699 | 484.5 | 17.5718 | 464.5 | 0.89685
485.5 | 49.5042 | 486.5 | 6203.6751 | 487.5 | 118.3327 | 488.5 | 149.1932 | 489.5 | 34997.6557 | 490.5 | 64.6183 | 491.5 | 8.6304 | 492.5 | 0.45934 | 493.5 | 13.0244 | 494.5 | 23.2674 | 495.5 | 6.316 | #REF! | #DIV/0! | 497.5 | 405.8222 | 498.5 | 215.1354 | 499.5 | 349.8342 | 500.5 | 487.6558 | 501.5 | 49.2061 | 502.5 | 40.6206 | 503.5 | 28.896 | 504.5 | 7.1625 | 505.5 | 39.9369 | 485.5 | #DIV/0!

## PenTemps
Penlight Time (s) | DAQ Time (s) | Shroud Temp | Cable Temp.
-82 | 0 | 23.6395 | 23.5824
-81.1788 | 0.8212 | 23.6406 | 23.5791
-80.1574 | 1.8426 | 23.6368 | 23.5777
-79.1759 | 2.8241 | 23.6335 | 23.5809
-78.1745 | 3.8255 | 23.6332 | 23.5788
-77.1731 | 4.8269 | 23.6349 | 23.582
-76.1716 | 5.8284 | 23.6401 | 23.5757
-75.1802 | 6.8198 | 23.6393 | 23.5778
-74.1788 | 7.8212 | 23.6384 | 23.5746
-73.1773 | 8.8227 | 23.6423 | 23.5695
-72.1759 | 9.8241 | 23.644 | 23.5739
-71.1744 | 10.8256 | 23.6408 | 23.5763
-70.173 | 11.827 | 23.6467 | 23.5753
-69.1716 | 12.8284 | 23.6423 | 23.577
-68.1701 | 13.8299 | 23.6424 | 23.5783
-67.1787 | 14.8213 | 23.6451 | 23.5793
-66.1772 | 15.8228 | 23.6464 | 23.5786
-65.1758 | 16.8242 | 23.6447 | 23.5736
-64.1343 | 17.8657 | 23.6457 | 23.5792
-63.1729 | 18.8271 | 23.643 | 23.5767
-62.1715 | 19.8285 | 23.6425 | 23.5687
-61.14 | 20.86 | 23.6425 | 23.5681
-60.1786 | 21.8214 | 23.6396 | 23.5791
-59.1772 | 22.8228 | 23.6408 | 23.5726
-58.1657 | 23.8343 | 23.6394 | 23.5767
-57.1743 | 24.8257 | 23.6416 | 23.5783
-56.1729 | 25.8271 | 23.644 | 23.5722
-55.1714 | 26.8286 | 23.6405 | 23.581
-54.17 | 27.83 | 23.639 | 23.5721
-53.1786 | 28.8214 | 23.6427 | 23.5748
-52.1671 | 29.8329 | 23.6422 | 23.5751
-51.1757 | 30.8243 | 23.6419 | 23.577
-50.1742 | 31.8258 | 23.64 | 23.5738
-49.1728 | 32.8272 | 23.64 | 23.577
-48.1714 | 33.8286 | 23.645 | 23.5758
-47.1699 | 34.8301 | 23.6393 | 23.5759
-46.1785 | 35.8215 | 23.6419 | 23.5767
-45.1771 | 36.8229 | 23.6476 | 23.5737
-44.1756 | 37.8244 | 23.6499 | 23.5734
-43.1742 | 38.8258 | 23.6511 | 23.5756
-42.1727 | 39.8273 | 23.6513 | 23.5725
-41.1713 | 40.8287 | 23.6465 | 23.5779
-40.1799 | 41.8201 | 23.6511 | 23.5741
-39.1784 | 42.8216 | 23.6544 | 23.5797
-38.177 | 43.823 | 23.6477 | 23.5763
-37.1755 | 44.8245 | 23.6545 | 23.5829
-36.1741 | 45.8259 | 23.654 | 23.5743
-35.1727 | 46.8273 | 23.6518 | 23.5787
-34.1712 | 47.8288 | 23.6496 | 23.5806
-33.1698 | 48.8302 | 23.6513 | 23.5775
-32.1784 | 49.8216 | 23.6478 | 23.5774
-31.1769 | 50.8231 | 23.6525 | 23.5778
-30.1755 | 51.8245 | 23.6492 | 23.5766
-29.174 | 52.826 | 23.6499 | 23.5806
-28.1726 | 53.8274 | 23.6425 | 23.5786
-27.1712 | 54.8288 | 23.6466 | 23.576
-26.1697 | 55.8303 | 23.6471 | 23.5807
-25.1783 | 56.8217 | 23.6483 | 23.5762
-24.1769 | 57.8231 | 23.652 | 23.5777
-23.1754 | 58.8246 | 23.646 | 23.5839
-22.174 | 59.826 | 23.6495 | 23.5745
-21.1725 | 60.8275 | 23.6452 | 23.5735
-20.1711 | 61.8289 | 23.642 | 23.5765
-19.1797 | 62.8203 | 23.6498 | 23.5813
-18.1782 | 63.8218 | 23.6498 | 23.5742
-17.1768 | 64.8232 | 23.6509 | 23.5787
-16.1753 | 65.8247 | 23.6442 | 23.5777
-15.1739 | 66.8261 | 23.6472 | 23.5811
-14.1725 | 67.8275 | 23.6489 | 23.5814
-13.171 | 68.829 | 23.6535 | 23.5752
-12.1696 | 69.8304 | 23.6501 | 23.5794
-11.1782 | 70.8218 | 23.6485 | 23.5792
-10.1767 | 71.8233 | 23.6496 | 23.5782
-9.1753 | 72.8247 | 23.6442 | 23.5801
-8.1738 | 73.8262 | 23.6523 | 23.5773
-7.1724 | 74.8276 | 23.6523 | 23.5764
-6.171 | 75.829 | 23.6454 | 23.5751
-5.1695 | 76.8305 | 23.6538 | 23.5754
-4.1781 | 77.8219 | 23.6535 | 23.5761
-3.1767 | 78.8233 | 23.6477 | 23.5717
-2.1752 | 79.8248 | 23.7445 | 23.5752
-1.1738 | 80.8262 | 24.2327 | 23.5772
-0.1723 | 81.8277 | 25.2594 | 23.5714
0.8291 | 82.8291 | 26.842 | 23.5768
1.8205 | 83.8205 | 28.8984 | 23.5826
2.822 | 84.822 | 31.3907 | 23.5815
3.8234 | 85.8234 | 34.192 | 23.59
4.8248 | 86.8248 | 37.1912 | 23.6006
5.8263 | 87.8263 | 40.3834 | 23.6148
6.8277 | 88.8277 | 43.7491 | 23.6355
7.8292 | 89.8292 | 47.2926 | 23.6575
8.8306 | 90.8306 | 50.9799 | 23.6834
9.822 | 91.822 | 54.8277 | 23.7264
10.8235 | 92.8235 | 58.8665 | 23.7714
11.8249 | 93.8249 | 63.0259 | 23.8203
12.8264 | 94.8264 | 67.2338 | 23.8779
13.8278 | 95.8278 | 71.5531 | 23.9335
14.8292 | 96.8292 | 76.0404 | 24.002
15.8207 | 97.8207 | 80.68 | 24.0822
16.8221 | 98.8221 | 85.4593 | 24.1728
17.8235 | 99.8235 | 90.4077 | 24.2753
18.825 | 100.825 | 95.4983 | 24.3782
19.8264 | 101.8264 | 100.6792 | 24.4944
20.8279 | 102.8279 | 105.9811 | 24.6089
21.8293 | 103.8293 | 111.3205 | 24.7381
22.8207 | 104.8207 | 116.6974 | 24.887
23.8222 | 105.8222 | 122.1047 | 25.0338
24.8236 | 106.8236 | 127.5533 | 25.1942
25.825 | 107.825 | 133.0912 | 25.3683
26.8265 | 108.8265 | 138.648 | 25.55
27.8279 | 109.8279 | 144.2495 | 25.7377
28.8294 | 110.8294 | 149.8018 | 25.9414
29.8308 | 111.8308 | 155.265 | 26.1711
30.8222 | 112.8222 | 160.7823 | 26.4021
31.8237 | 113.8237 | 166.2598 | 26.6521
32.8251 | 114.8251 | 171.6821 | 26.9154
33.8266 | 115.8266 | 177.1649 | 27.1931
34.828 | 116.828 | 182.7782 | 27.4777
35.8194 | 117.8194 | 188.4158 | 27.7737
36.8209 | 118.8209 | 194.0738 | 28.0963
37.8423 | 119.8423 | 199.8383 | 28.4428
38.8237 | 120.8237 | 205.2749 | 28.7857
39.8252 | 121.8252 | 210.822 | 29.1459
40.8266 | 122.8266 | 216.3364 | 29.5175
41.8281 | 123.8281 | 221.7093 | 29.9173
42.8295 | 124.8295 | 227.1402 | 30.3304
43.8209 | 125.8209 | 232.569 | 30.7494
44.8224 | 126.8224 | 237.988 | 31.182
45.8238 | 127.8238 | 243.3177 | 31.6318
46.8252 | 128.8252 | 248.7728 | 32.0965
47.8267 | 129.8267 | 254.268 | 32.5712
48.8281 | 130.8281 | 259.7868 | 33.0777
49.8296 | 131.8296 | 265.2463 | 33.5903
50.821 | 132.821 | 270.6729 | 34.1304
51.8224 | 133.8224 | 276.0755 | 34.6759
52.8239 | 134.8239 | 281.5564 | 35.2424
53.8253 | 135.8253 | 286.8737 | 35.8169
54.8267 | 136.8267 | 292.1683 | 36.4036
55.8282 | 137.8282 | 297.5628 | 37.0089
56.8196 | 138.8196 | 303.0736 | 37.6283
57.8211 | 139.8211 | 308.2973 | 38.274
58.8225 | 140.8225 | 313.5913 | 38.927
59.8239 | 141.8239 | 318.8483 | 39.6052
60.8254 | 142.8254 | 324.0899 | 40.2936
61.8268 | 143.8268 | 329.3317 | 40.9991
62.8283 | 144.8283 | 334.5269 | 41.7351
63.8297 | 145.8297 | 339.7195 | 42.4837
64.8211 | 146.8211 | 344.8556 | 43.2653
65.8226 | 147.8226 | 349.9787 | 44.0564
66.824 | 148.824 | 355.0452 | 44.8804
67.8254 | 149.8254 | 360.0661 | 45.7226
68.8269 | 150.8269 | 365.0602 | 46.5975
69.8283 | 151.8283 | 370.1671 | 47.4967
70.8298 | 152.8298 | 375.2059 | 48.4371
71.8312 | 153.8312 | 380.0732 | 49.3899
72.8226 | 154.8226 | 384.9214 | 50.3715
73.8241 | 155.8241 | 390.0318 | 51.3831
74.8255 | 156.8255 | 394.9109 | 52.4264
75.8269 | 157.8269 | 399.6834 | 53.4949
76.8284 | 158.8284 | 404.5314 | 54.5851
77.8198 | 159.8198 | 409.169 | 55.6979
78.8212 | 160.8212 | 413.8442 | 56.8419
79.8227 | 161.8227 | 418.4542 | 58.0198
80.8241 | 162.8241 | 423.09 | 59.2188
81.8256 | 163.8256 | 427.8333 | 60.4424 | Time of cable ignition
82.827 | 164.827 | 432.5247 | 61.6913 | 164 | 0
83.8284 | 165.8284 | 436.9015 | 62.9712 | 164 | 900
84.8299 | 166.8299 | 441.2659 | 64.2762
85.8213 | 167.8213 | 445.6838 | 65.6045
86.8228 | 168.8228 | 450.0118 | 66.9624
87.8242 | 169.8242 | 454.4094 | 68.3416
88.8256 | 170.8256 | 458.8128 | 69.738
89.8271 | 171.8271 | 463.0924 | 71.1653
90.8285 | 172.8285 | 467.3564 | 72.6109
91.83 | 173.83 | 471.6215 | 74.0799
92.8214 | 174.8214 | 476.0126 | 75.5655
93.8228 | 175.8228 | 480.3237 | 77.0674
94.8243 | 176.8243 | 484.4793 | 78.5894
95.8257 | 177.8257 | 488.5378 | 80.1022
96.8271 | 178.8271 | 492.5174 | 81.6325
97.8286 | 179.8286 | 496.7005 | 83.1842
98.82 | 180.82 | 500.5263 | 84.7437
99.8315 | 181.8315 | 504.6598 | 86.3341
100.8229 | 182.8229 | 508.8024 | 87.9392
101.8243 | 183.8243 | 512.8649 | 89.5989
102.8258 | 184.8258 | 516.9386 | 91.3058
103.8272 | 185.8272 | 520.8417 | 93.0481
104.8286 | 186.8286 | 524.567 | 94.856
105.8301 | 187.8301 | 528.411 | 96.713
106.8215 | 188.8215 | 532.0976 | 98.6419
107.823 | 189.823 | 535.7461 | 100.6076
108.8244 | 190.8244 | 539.4783 | 102.738
109.8258 | 191.8258 | 543.2217 | 105.0593
110.8273 | 192.8273 | 546.883 | 107.5421
111.8287 | 193.8287 | 550.3337 | 110.152
112.8201 | 194.8201 | 553.8747 | 112.9035
113.8216 | 195.8216 | 557.443 | 115.8405
114.823 | 196.823 | 560.9922 | 118.8559
115.8245 | 197.8245 | 564.6532 | 121.9272
116.8259 | 198.8259 | 568.0777 | 124.9934
117.8273 | 199.8273 | 571.556 | 128.0744
118.8288 | 200.8288 | 575.0531 | 131.0817
119.8202 | 201.8202 | 578.3438 | 134.0526
120.8216 | 202.8216 | 581.5669 | 136.934
121.8231 | 203.8231 | 584.7979 | 139.7616
122.8245 | 204.8245 | 588.0282 | 142.5168
123.826 | 205.826 | 591.1272 | 145.2004
124.8274 | 206.8274 | 594.101 | 147.8231
125.8288 | 207.8288 | 597.2048 | 150.3657
126.8303 | 208.8303 | 600.1196 | 152.8447
127.8317 | 209.8317 | 602.9669 | 155.25
128.8231 | 210.8231 | 605.7066 | 157.5287
129.8246 | 211.8246 | 608.0504 | 159.7247
130.826 | 212.826 | 610.3413 | 161.8404
131.8275 | 213.8275 | 612.3961 | 163.8631
132.8289 | 214.8289 | 614.6167 | 165.7755
133.8203 | 215.8203 | 616.6684 | 167.5629
134.8218 | 216.8218 | 618.2579 | 169.1341
135.8232 | 217.8232 | 620.0936 | 170.4911
136.8247 | 218.8247 | 621.9297 | 171.757
137.8261 | 219.8261 | 623.6405 | 172.9585
138.8275 | 220.8275 | 625.5619 | 174.1854
139.829 | 221.829 | 627.2832 | 175.2436
140.8204 | 222.8204 | 629.076 | 176.1979
141.8218 | 223.8218 | 631.0854 | 177.1149
142.8233 | 224.8233 | 632.9639 | 178.0905
143.8247 | 225.8247 | 635.1571 | 179.1929
144.8262 | 226.8262 | 637.0484 | 180.4937
145.8276 | 227.8276 | 638.6034 | 181.9673
146.829 | 228.829 | 639.9748 | 183.4083
147.8305 | 229.8305 | 641.2121 | 184.7016
148.8219 | 230.8219 | 642.5212 | 185.7774
149.8233 | 231.8233 | 643.6894 | 186.7759
150.8248 | 232.8248 | 644.6745 | 187.7946
151.8262 | 233.8262 | 645.4789 | 188.7893
152.8277 | 234.8277 | 646.4497 | 189.8356
153.8291 | 235.8291 | 647.2741 | 190.8103
154.8205 | 236.8205 | 647.8526 | 191.8793
155.822 | 237.822 | 648.2241 | 192.925
156.8234 | 238.8234 | 648.423 | 193.9555
157.8249 | 239.8249 | 648.9111 | 194.9829
158.8263 | 240.8263 | 649.4978 | 202.6225
159.8277 | 241.8277 | 649.9543 | 206.1192
160.8292 | 242.8292 | 650.2017 | 206.7545
161.8306 | 243.8306 | 650.4812 | 207.8523
162.822 | 244.822 | 650.9533 | 210.047
163.8235 | 245.8235 | 651.3064 | 203.8123
164.8249 | 246.8249 | 651.8616 | 202.2522
165.8264 | 247.8264 | 652.356 | 209.1617
166.8278 | 248.8278 | 652.4435 | 214.7427
167.8292 | 249.8292 | 652.5429 | 220.1585
168.8207 | 250.8207 | 652.5026 | 226.7813
169.8221 | 251.8221 | 652.423 | 234.6883
170.8235 | 252.8235 | 652.7674 | 246.7129
171.825 | 253.825 | 653.2441 | 249.8953
172.8264 | 254.8264 | 653.4201 | 257.4029
173.8279 | 255.8279 | 653.7373 | 267.5205
174.8293 | 256.8293 | 654.2274 | 284.1187
175.8207 | 257.8207 | 654.541 | 282.0457
176.8222 | 258.8222 | 654.9506 | 305.063
177.8236 | 259.8236 | 655.3974 | 306.9074
178.825 | 260.825 | 655.5342 | 319.8111
179.8265 | 261.8265 | 655.8277 | 334.0822
180.8279 | 262.8279 | 655.8226 | 347.1721
181.8294 | 263.8294 | 655.7391 | 407.8233
182.8308 | 264.8308 | 655.8035 | 427.8896
183.8222 | 265.8222 | 655.9077 | 447.5264
184.8237 | 266.8237 | 655.9833 | 466.0097
185.8251 | 267.8251 | 656.0413 | 482.2515
186.8266 | 268.8266 | 656.1044 | 495.5406
187.828 | 269.828 | 655.9204 | 506.56
188.8194 | 270.8194 | 655.6399 | 516.2095
189.8209 | 271.8209 | 655.5555 | 525.6536
190.8223 | 272.8223 | 655.3958 | 534.3406
191.8237 | 273.8237 | 655.5318 | 543.0786
192.8252 | 274.8252 | 655.608 | 552.1504
193.8266 | 275.8266 | 655.8402 | 562.5098
194.8281 | 276.8281 | 655.804 | 573.8997
195.8295 | 277.8295 | 656.0169 | 584.8416
196.8209 | 278.8209 | 656.2399 | 595.8927
197.8224 | 279.8224 | 656.6276 | 607.2077
198.8238 | 280.8238 | 656.7694 | 618.4041
199.8252 | 281.8252 | 656.9292 | 629.1004
200.8267 | 282.8267 | 657.17 | 639.3778
201.8281 | 283.8281 | 657.3558 | 648.8088
202.8296 | 284.8296 | 657.6906 | 657.5897
203.821 | 285.821 | 658.1761 | 666.21
204.8224 | 286.8224 | 658.3954 | 673.7885
205.8239 | 287.8239 | 658.75 | 680.2715
206.8253 | 288.8253 | 658.9087 | 685.3358
207.8268 | 289.8268 | 659.06 | 690.0011
208.8282 | 290.8282 | 659.2222 | 694.0018
209.8196 | 291.8196 | 659.2278 | 697.6723
210.8211 | 292.8211 | 659.0963 | 700.6109
211.8225 | 293.8225 | 658.9475 | 705.0237 | Time of first failure
212.8239 | 294.8239 | 658.9166 | 707.4336 | 211 | 0
213.8254 | 295.8254 | 658.9018 | 709.0337 | 211 | 900
214.8268 | 296.8268 | 658.9739 | 711.9428
215.8283 | 297.8283 | 658.9672 | 714.5951
216.8297 | 298.8297 | 658.9912 | 717.331
217.8211 | 299.8211 | 658.6228 | 721.0958
218.8226 | 300.8226 | 658.4858 | 722.9967
219.824 | 301.824 | 658.4035 | 726.3832
220.8254 | 302.8254 | 658.3544 | 728.0036
221.8269 | 303.8269 | 658.3459 | 728.4761
222.8283 | 304.8283 | 658.1876 | 729.1348
223.8298 | 305.8298 | 658.0084 | 729.571
224.8312 | 306.8312 | 657.9389 | 729.9473
225.8226 | 307.8226 | 657.7847 | 730.8275
226.8241 | 308.8241 | 657.7979 | 734.2315
227.8255 | 309.8255 | 657.6247 | 734.7047
228.8269 | 310.8269 | 657.5327 | 737.9733
229.8284 | 311.8284 | 657.374 | 742.7062
230.8198 | 312.8198 | 657.1597 | 741.817
231.8213 | 313.8213 | 657.2379 | 744.7104
232.8227 | 314.8227 | 657.3786 | 751.2768
233.8241 | 315.8241 | 657.4565 | 759.0938
234.8256 | 316.8256 | 657.4847 | 765.4105
235.827 | 317.827 | 657.6013 | 770.9498
236.8285 | 318.8285 | 658.0574 | 779.4062
237.8299 | 319.8299 | 658.3964 | 776.8358
238.8213 | 320.8213 | 658.4192 | 775.0242
239.8228 | 321.8228 | 658.2963 | 774.9
240.8242 | 322.8242 | 657.7943 | 772.9778
241.8256 | 323.8256 | 657.4671 | 773.2537
242.8271 | 324.8271 | 657.4272 | 775.2058
243.8285 | 325.8285 | 657.665 | 775.961
244.83 | 326.83 | 657.8662 | 779.1373
245.8214 | 327.8214 | 658.0853 | 779.7329
246.8228 | 328.8228 | 657.9216 | 781.0753
247.8243 | 329.8243 | 657.7549 | 784.4975
248.8257 | 330.8257 | 657.5554 | 785.6148
249.8271 | 331.8271 | 657.7859 | 790.7678
250.8286 | 332.8286 | 657.9456 | 791.9222
251.82 | 333.82 | 657.6659 | 790.2529
252.8315 | 334.8315 | 657.621 | 789.7861
253.8229 | 335.8229 | 657.7802 | 783.1443
254.8243 | 336.8243 | 657.7787 | 778.1798
255.8258 | 337.8258 | 657.6412 | 771.2358
256.8272 | 338.8272 | 657.4959 | 764.3101
257.8286 | 339.8286 | 657.2693 | 756.2527
258.8301 | 340.8301 | 657.0581 | 748.5143
259.8215 | 341.8215 | 656.7777 | 742.8858
260.823 | 342.823 | 656.7736 | 739.0542
261.8244 | 343.8244 | 657.1021 | 735.287
262.8258 | 344.8258 | 657.243 | 732.5605
263.8273 | 345.8273 | 657.3163 | 731.1229
264.8287 | 346.8287 | 657.1761 | 729.4203
265.8302 | 347.8302 | 657.0655 | 728.2725
266.8216 | 348.8216 | 657.1429 | 727.4225
267.823 | 349.823 | 657.206 | 726.2542
268.8245 | 350.8245 | 657.0047 | 725.9669
269.8259 | 351.8259 | 656.7351 | 725.4787
270.8273 | 352.8273 | 656.4132 | 724.524
271.8288 | 353.8288 | 656.1114 | 724.4151
272.8202 | 354.8202 | 655.8641 | 723.8055
273.8216 | 355.8216 | 655.9533 | 722.6906
274.8231 | 356.8231 | 655.8583 | 722.0407
275.8245 | 357.8245 | 655.9211 | 721.7118
276.826 | 358.826 | 655.7605 | 721.9397
277.8274 | 359.8274 | 655.3952 | 724.0346
278.8288 | 360.8288 | 654.9281 | 725.8763
279.8303 | 361.8303 | 654.7269 | 727.3308
280.8217 | 362.8217 | 654.6957 | 729.033
281.8232 | 363.8232 | 654.4449 | 729.2828
282.8246 | 364.8246 | 654.2882 | 730.3195
283.826 | 365.826 | 654.1274 | 730.8744
284.8275 | 366.8275 | 654.1598 | 731.5022
285.8289 | 367.8289 | 654.0595 | 732.7751
286.8203 | 368.8203 | 653.8092 | 732.9435
287.8218 | 369.8218 | 653.7941 | 731.486
288.8232 | 370.8232 | 653.7993 | 730.1347
289.8247 | 371.8247 | 653.9848 | 730.6256
290.8261 | 372.8261 | 653.9258 | 731.5313
291.8275 | 373.8275 | 653.7782 | 732.3769
292.829 | 374.829 | 653.5003 | 732.3324
293.8204 | 375.8204 | 653.3013 | 731.6977
294.8218 | 376.8218 | 653.4081 | 731.0738
295.8233 | 377.8233 | 653.4445 | 730.1051
296.8247 | 378.8247 | 653.6303 | 729.3952
297.8262 | 379.8262 | 653.8152 | 728.7098
298.8276 | 380.8276 | 654.0046 | 728.151
299.829 | 381.829 | 654.0716 | 729.4379
300.8305 | 382.8305 | 654.2024 | 730.9431
301.8219 | 383.8219 | 654.3024 | 732.0536
302.8233 | 384.8233 | 654.261 | 733.0523
303.8248 | 385.8248 | 654.2347 | 734.6112
304.8262 | 386.8262 | 654.216 | 736.8443
305.8277 | 387.8277 | 654.2743 | 738.1114
306.8291 | 388.8291 | 654.4305 | 738.3823
307.8305 | 389.8305 | 654.5601 | 739.8291
308.822 | 390.822 | 654.525 | 740.2345
309.8234 | 391.8234 | 654.5601 | 741.0792
310.8249 | 392.8249 | 654.4073 | 741.9031
311.8263 | 393.8263 | 654.3591 | 743.8683
312.8277 | 394.8277 | 654.4351 | 743.9686
313.8292 | 395.8292 | 654.6293 | 744.3905
314.8206 | 396.8206 | 654.6777 | 744.0013
315.822 | 397.822 | 654.7511 | 744.0525
316.8235 | 398.8235 | 654.7438 | 743.3147
317.8249 | 399.8249 | 654.5698 | 741.4241
318.8264 | 400.8264 | 654.5808 | 739.8144
319.8278 | 401.8278 | 654.4832 | 737.2362
320.8292 | 402.8292 | 654.309 | 736.0902
321.8307 | 403.8307 | 654.1343 | 734.992
322.8221 | 404.8221 | 653.7253 | 733.3201
323.8235 | 405.8235 | 653.1339 | 732.396
324.825 | 406.825 | 652.4946 | 732.2046
325.8264 | 407.8264 | 651.6502 | 731.5053
326.8279 | 408.8279 | 650.8959 | 730.6776
327.8293 | 409.8293 | 650.0156 | 730.8041
328.8207 | 410.8207 | 649.0852 | 730.0771
329.8222 | 411.8222 | 648.0938 | 730.2093
330.8236 | 412.8236 | 647.0621 | 730.349
331.8251 | 413.8251 | 646.0105 | 732.5594
332.8265 | 414.8265 | 644.9789 | 733.4364
333.8279 | 415.8279 | 643.7707 | 733.7198
334.8294 | 416.8294 | 642.5502 | 733.4613
335.8208 | 417.8208 | 641.4197 | 734.2079
336.8222 | 418.8222 | 640.2684 | 733.7913
337.8237 | 419.8237 | 638.9652 | 734.2569
338.8251 | 420.8251 | 637.5575 | 735.6888
339.8266 | 421.8266 | 636.2537 | 737.1115
340.828 | 422.828 | 634.9414 | 739.4744
341.8294 | 423.8294 | 633.8082 | 741.0532
342.8309 | 424.8309 | 632.6946 | 741.0884
343.8223 | 425.8223 | 631.3911 | 740.6715
344.8237 | 426.8237 | 630.4776 | 740.6268
345.8252 | 427.8252 | 629.1955 | 741.1215
346.8266 | 428.8266 | 627.9188 | 741.5034
347.8281 | 429.8281 | 626.7703 | 742.0591
348.8295 | 430.8295 | 625.6908 | 742.696
349.8209 | 431.8209 | 624.4251 | 741.8966
350.8224 | 432.8224 | 623.3223 | 741.6889
351.8238 | 433.8238 | 622.3297 | 743.2336
352.8252 | 434.8252 | 621.1131 | 744.7138
353.8267 | 435.8267 | 620.0262 | 744.3698
354.8281 | 436.8281 | 619.0092 | 745.0941
355.8296 | 437.8296 | 618.0821 | 745.0359
356.821 | 438.821 | 616.958 | 744.7956
357.8224 | 439.8224 | 615.8714 | 744.3306
358.8239 | 440.8239 | 614.79 | 742.6499
359.8253 | 441.8253 | 613.724 | 740.9716
360.8268 | 442.8268 | 612.4858 | 740.5777
361.8282 | 443.8282 | 611.3633 | 740.3773
362.8196 | 444.8196 | 610.1884 | 741.3677
363.8211 | 445.8211 | 608.9452 | 742.9386
364.8225 | 446.8225 | 607.8194 | 743.3943
365.8239 | 447.8239 | 606.4008 | 742.4043
366.8254 | 448.8254 | 605.0389 | 742.9172
367.8268 | 449.8268 | 603.7682 | 742.5474
368.8283 | 450.8283 | 602.5106 | 742.7386
369.8297 | 451.8297 | 601.3262 | 742.6474
370.8211 | 452.8211 | 600.0717 | 742.6405
371.8226 | 453.8226 | 598.8103 | 741.742
372.824 | 454.824 | 597.7236 | 740.403
373.8254 | 455.8254 | 596.5737 | 737.6255
374.8269 | 456.8269 | 595.5453 | 738.1906
375.8283 | 457.8283 | 594.5838 | 737.9259
376.8298 | 458.8298 | 593.5683 | 736.4505
377.8312 | 459.8312 | 592.4381 | 737.1561
378.8226 | 460.8226 | 591.171 | 737.2881
379.8241 | 461.8241 | 590.0199 | 737.0211
380.8255 | 462.8255 | 588.8146 | 736.8799
381.827 | 463.827 | 587.5065 | 734.9045
382.8284 | 464.8284 | 586.4992 | 733.9978
383.8298 | 465.8298 | 585.5276 | 732.8976
384.8213 | 466.8213 | 584.1755 | 731.001
385.8227 | 467.8227 | 582.6913 | 730.6154
386.8241 | 468.8241 | 581.3146 | 729.5012
387.8256 | 469.8256 | 580.0278 | 729.8923
388.827 | 470.827 | 578.7475 | 729.924
389.8285 | 471.8285 | 577.7694 | 730.2317
390.8299 | 472.8299 | 576.796 | 730.5694
391.8213 | 473.8213 | 575.746 | 730.6441
392.8228 | 474.8228 | 574.5791 | 729.9509
393.8242 | 475.8242 | 573.3904 | 728.0819
394.8256 | 476.8256 | 572.3437 | 725.3388
395.8271 | 477.8271 | 571.3597 | 723.8047
396.8285 | 478.8285 | 570.2636 | 722.9592
397.83 | 479.83 | 569.1137 | 723.3037
398.8414 | 480.8414 | 567.974 | 723.0387
399.8228 | 481.8228 | 566.707 | 721.4148
400.8243 | 482.8243 | 565.5625 | 720.5719
401.8257 | 483.8257 | 564.3428 | 720.6199
402.8271 | 484.8271 | 563.4133 | 720.9986
403.8286 | 485.8286 | 562.3914 | 722.2162
404.82 | 486.82 | 561.2718 | 722.2984
405.8215 | 487.8215 | 560.1855 | 720.9914
406.8229 | 488.8229 | 558.9747 | 721.5211
407.8243 | 489.8243 | 557.7915 | 719.647
408.8258 | 490.8258 | 556.5496 | 716.6378
409.8272 | 491.8272 | 555.4395 | 715.4007
410.8287 | 492.8287 | 554.1959 | 715.0924
411.8301 | 493.8301 | 552.8988 | 714.6741
412.8215 | 494.8215 | 551.6685 | 711.7115
413.823 | 495.823 | 550.4704 | 710.1654
414.8244 | 496.8244 | 549.4266 | 709.5309
415.8258 | 497.8258 | 548.3332 | 709.1046
416.8273 | 498.8273 | 547.3518 | 708.8825
417.8287 | 499.8287 | 546.3705 | 707.5636
418.8302 | 500.8302 | 545.4484 | 706.5427
419.8216 | 501.8216 | 544.6196 | 706.4626
420.823 | 502.823 | 543.7066 | 705.7562
421.8245 | 503.8245 | 542.7536 | 706.5516
422.8259 | 504.8259 | 541.7808 | 706.4598
423.8273 | 505.8273 | 540.6875 | 704.0899
424.8288 | 506.8288 | 539.5695 | 703.3267
425.8202 | 507.8202 | 538.3882 | 701.6976
426.8216 | 508.8216 | 537.1941 | 702.8641
427.8231 | 509.8231 | 536.2023 | 701.0967
428.8245 | 510.8245 | 535.1693 | 699.2303
429.826 | 511.826 | 534.3665 | 698.6935
430.8274 | 512.8274 | 533.534 | 697.1729
431.8288 | 513.8288 | 532.5995 | 694.4607
432.8303 | 514.8303 | 531.6407 | 693.5659
433.8217 | 515.8217 | 530.5682 | 693.804
434.8232 | 516.8232 | 529.6208 | 691.905
435.8246 | 517.8246 | 528.5452 | 690.4482
436.826 | 518.826 | 527.2829 | 688.0352
437.8275 | 519.8275 | 526.2757 | 687.4039
438.8289 | 520.8289 | 525.3115 | 685.747
439.8304 | 521.8304 | 524.2776 | 683.1977
440.8218 | 522.8218 | 523.3193 | 681.0973
441.8232 | 523.8232 | 522.3586 | 679.1405
442.8247 | 524.8247 | 521.2465 | 676.1119
443.8261 | 525.8261 | 520.181 | 672.9581
444.8275 | 526.8275 | 519.2744 | 669.7773
445.829 | 527.829 | 518.281 | 667.8001
446.8204 | 528.8204 | 517.1547 | 664.3743
447.8218 | 529.8218 | 516.1985 | 659.7971
448.8233 | 530.8233 | 515.2475 | 656.1441
449.8247 | 531.8247 | 514.1655 | 653.7636
450.8262 | 532.8262 | 513.0869 | 650.1149
451.8276 | 533.8276 | 512.0876 | 647.2734
452.829 | 534.829 | 511.2063 | 643.859
453.8305 | 535.8305 | 510.217 | 639.6685
454.8219 | 536.8219 | 509.2151 | 635.2616
455.8234 | 537.8234 | 508.2542 | 630.558
456.8248 | 538.8248 | 507.2399 | 624.4913
457.8262 | 539.8262 | 506.2293 | 617.5006
458.8277 | 540.8277 | 505.1532 | 606.7262
459.8291 | 541.8291 | 504.1785 | 595.9536
460.8306 | 542.8306 | 503.1872 | 587.4298
461.822 | 543.822 | 502.1702 | 578.7993
462.8234 | 544.8234 | 501.2953 | 569.2649
463.8249 | 545.8249 | 500.4284 | 561.211
464.8263 | 546.8263 | 499.4766 | 555.3675
465.8277 | 547.8277 | 498.5995 | 550.3794
466.8292 | 548.8292 | 497.5881 | 545.1011
467.8306 | 549.8306 | 496.6116 | 540.9028
468.822 | 550.822 | 495.5048 | 537.8267
469.8235 | 551.8235 | 494.4888 | 535.4943
470.8249 | 552.8249 | 493.4971 | 533.5918
471.8264 | 553.8264 | 492.4732 | 531.653
472.8278 | 554.8278 | 491.4881 | 530.0674
473.8292 | 555.8292 | 490.6151 | 528.8983
474.8307 | 556.8307 | 489.584 | 527.7813
475.8221 | 557.8221 | 488.6311 | 525.6364
476.8235 | 558.8235 | 487.8826 | 522.2315
477.825 | 559.825 | 487.0099 | 519.7153
478.8264 | 560.8264 | 486.0842 | 517.5199
479.8279 | 561.8279 | 485.2981 | 514.7895
480.8293 | 562.8293 | 484.4876 | 513.7469
481.8207 | 563.8207 | 483.715 | 512.6707
482.8222 | 564.8222 | 482.9119 | 511.5725
483.8236 | 565.8236 | 482.0067 | 508.0688
484.8251 | 566.8251 | 481.2001 | 506.3767
485.8265 | 567.8265 | 480.3681 | 505.5947
486.8279 | 568.8279 | 479.6004 | 504.0171
487.8294 | 569.8294 | 478.6882 | 501.2646
488.8208 | 570.8208 | 477.7064 | 500.1662
489.8222 | 571.8222 | 476.6401 | 500.0142
490.8237 | 572.8237 | 475.6748 | 499.533
491.8251 | 573.8251 | 474.8015 | 498.5134
492.8266 | 574.8266 | 474.0594 | 497.2807
493.828 | 575.828 | 473.3174 | 496.1116
494.8294 | 576.8294 | 472.4311 | 495.457
495.8209 | 577.8209 | 471.4148 | 493.3552
496.8223 | 578.8223 | 470.4703 | 492.6786
497.8237 | 579.8237 | 469.72 | 492.4068
498.8252 | 580.8252 | 468.925 | 491.6004
499.8266 | 581.8266 | 467.9723 | 491.1328
500.8281 | 582.8281 | 467.0597 | 489.6404
501.8295 | 583.8295 | 466.1623 | 487.71
502.8309 | 584.8309 | 465.314 | 486.9587
503.8224 | 585.8224 | 464.3851 | 486.8481
504.8238 | 586.8238 | 463.5757 | 485.7834
505.8253 | 587.8253 | 462.7501 | 485.0904
506.8267 | 588.8267 | 461.9538 | 483.8108
507.8281 | 589.8281 | 461.0474 | 483.1249
508.8296 | 590.8296 | 460.327 | 482.2599
509.821 | 591.821 | 459.5605 | 480.8032
510.8224 | 592.8224 | 458.7243 | 480.2191
511.8239 | 593.8239 | 457.9522 | 479.053
512.8253 | 594.8253 | 457.3497 | 477.1347
513.8268 | 595.8268 | 456.5443 | 474.9709
514.8282 | 596.8282 | 455.5878 | 473.627
515.8296 | 597.8296 | 454.6495 | 471.6182
516.8211 | 598.8211 | 453.7327 | 470.9863
517.8225 | 599.8225 | 452.9736 | 470.4576
518.8239 | 600.8239 | 452.2681 | 469.4063
519.8254 | 601.8254 | 451.6793 | 467.8566
520.8268 | 602.8268 | 450.946 | 466.0598
521.8283 | 603.8283 | 450.1386 | 463.9021
522.8297 | 604.8297 | 449.2901 | 462.2453
523.8211 | 605.8211 | 448.4207 | 460.5678
524.8226 | 606.8226 | 447.5123 | 459.24
525.824 | 607.824 | 446.7951 | 457.5786
526.8254 | 608.8254 | 446.0886 | 455.9315
527.8269 | 609.8269 | 445.3048 | 452.0093
528.8283 | 610.8283 | 444.5516 | 451.0896
529.8298 | 611.8298 | 443.6943 | 450.618
530.8212 | 612.8212 | 442.93 | 448.9902
531.8226 | 613.8226 | 442.241 | 447.0117
532.8241 | 614.8241 | 441.4796 | 443.8735
533.8255 | 615.8255 | 440.7538 | 440.2554

## C6-7
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 154.7241 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38880.5936 | 1 | 0 | 38880.5936 | 1 | 0 | -61.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5938 | 1 | 0 | 38880.5939 | 1 | 0 | -40.5 | 41.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5941 | 1 | 0 | 38880.5941 | 1 | 0 | -19.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5943 | 1 | 0 | 38880.5943 | 1 | 0 | 1.5 | 83.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5946 | 1 | 0 | 38880.5946 | 1 | 0 | 22.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5948 | 1 | 0 | 38880.5948 | 1 | 0 | 43.5 | 125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5953 | 1 | 0 | 38880.5951 | 1 | 0 | 75 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5955 | 1 | 0 | 38880.5953 | 1 | 0 | 96 | 178 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5958 | 1 | 0 | 38880.5958 | 1 | 0 | 127.5 | 209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.596 | 1 | 0 | 38880.596 | 1 | 0 | 148.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5963 | 1 | 0 | 38880.5963 | 1 | 0 | 169.5 | 251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5965 | 1 | 0 | 38880.5965 | 1 | 0 | 190.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38880.5968 | 693 | 0 | 38880.5968 | 207 | 26 | 211.5 | 293.5 | 42.3077 | 0 | 12.6374 | 1.5873 | 0.42308 | 0 | 0.12637 | 0.015873 | 0.42308 | 0.1105 | 265.7114 | 1300.2099 | 265.2883
38880.597 | 1739 | 0 | 38880.597 | 532 | 1 | 232.5 | 314.5 | 106.1661 | 0 | 32.4786 | 0.06105 | 1.0617 | 0 | 0.32479 | 0.0006105 | 1.0617 | 0.32418 | 45.7378 | 377.2844 | 44.6761
38880.5972 | 1386 | 283 | 38880.5973 | 2129 | 15 | 253.5 | 335.5 | 84.6154 | 17.2772 | 129.9756 | 0.91575 | 0.84615 | 0.17277 | 1.2998 | 0.0091575 | 0.67338 | 1.2906 | 305.2285 | 38.9397 | 85.7012
38880.5975 | 2518 | 0 | 38880.5975 | 1964 | 0 | 274.5 | 356.5 | 153.7241 | 0 | 119.9023 | 0 | 1.5372 | 0 | 1.199 | 0 | 1.5372 | 1.199 | 0.65052 | 29.0418 | 0.88672
38880.5977 | 2170 | 0 | 38880.5977 | 1654 | 3 | 295.5 | 377.5 | 132.4786 | 0 | 100.9768 | 0.18315 | 1.3248 | 0 | 1.0098 | 0.0018315 | 1.3248 | 1.0079 | 16.7917 | 53.5058 | 15.4669
38880.598 | 2322 | 0 | 38880.598 | 2411 | 0 | 316.5 | 398.5 | 141.7582 | 0 | 147.1917 | 0 | 1.4176 | 0 | 1.4719 | 0 | 1.4176 | 1.4719 | 9.1464 | 5.1174 | 7.7288
38880.5982 | 2057 | 0 | 38880.5982 | 1988 | 0 | 337.5 | 419.5 | 125.58 | 0 | 121.3675 | 0 | 1.2558 | 0 | 1.2137 | 0 | 1.2558 | 1.2137 | 23.2076 | 27.4839 | 21.9518
38880.5985 | 2062 | 0 | 38880.5985 | 2400 | 0 | 358.5 | 440.5 | 125.8852 | 0 | 146.5201 | 0 | 1.2589 | 0 | 1.4652 | 0 | 1.2589 | 1.4652 | 22.9088 | 5.5992 | 21.65
38880.5987 | 2442 | 0 | 38880.5987 | 1972 | 0 | 379.5 | 461.5 | 149.0842 | 0 | 120.3907 | 0 | 1.4908 | 0 | 1.2039 | 0 | 1.4908 | 1.2039 | 3.783 | 28.5183 | 2.2921
38880.5989 | 1900 | 0 | 38880.599 | 1915 | 0 | 400.5 | 482.5 | 115.9951 | 0 | 116.9109 | 0 | 1.16 | 0 | 1.1691 | 0 | 1.16 | 1.1691 | 33.3884 | 32.3436 | 32.2285
38880.5992 | 2048 | 0 | 38880.5992 | 2338 | 0 | 421.5 | 503.5 | 125.0305 | 0 | 142.735 | 0 | 1.2503 | 0 | 1.4274 | 0 | 1.2503 | 1.4274 | 23.749 | 8.3995 | 22.4987
38880.5994 | 1232 | 0 | 38880.5994 | 2338 | 0 | 442.5 | 524.5 | 75.2137 | 0 | 142.735 | 0 | 0.75214 | 0 | 1.4274 | 0 | 0.75214 | 1.4274 | 105.7127 | 8.3995 | 104.9605
38880.5997 | 2240 | 0 | 38880.5997 | 2321 | 0 | 463.5 | 545.5 | 136.7521 | 0 | 141.6972 | 0 | 1.3675 | 0 | 1.417 | 0 | 1.3675 | 1.417 | 13.142 | 9.1935 | 11.7744
38880.5999 | 2132 | 0 | 38880.5999 | 2069 | 0 | 484.5 | 566.5 | 130.1587 | 0 | 126.3126 | 0 | 1.3016 | 0 | 1.2631 | 0 | 1.3016 | 1.2631 | 18.8734 | 22.493 | 17.5718
38880.6002 | 1797 | 0 | 38880.6002 | 1831 | 0 | 505.5 | 587.5 | 109.707 | 0 | 111.7827 | 0 | 1.0971 | 0 | 1.1178 | 0 | 1.0971 | 1.1178 | 41.0339 | 38.4151 | 39.9369

## C5-7
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 147.9475 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38880.5936 | 1 | 0 | 38880.5936 | 1 | 0 | -62.5 | 19.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5938 | 1 | 0 | 38880.5938 | 1 | 0 | -41.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5941 | 1 | 0 | 38880.5941 | 1 | 0 | -20.5 | 61.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5943 | 1 | 0 | 38880.5943 | 1 | 0 | 0.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5946 | 1 | 0 | 38880.5946 | 1 | 0 | 21.5 | 103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5948 | 1 | 0 | 38880.5948 | 1 | 0 | 42.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5953 | 1 | 0 | 38880.5953 | 1 | 0 | 84.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 105.5 | 187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5958 | 1 | 0 | 38880.5958 | 1 | 0 | 126.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.596 | 1 | 0 | 38880.596 | 1 | 0 | 147.5 | 229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5963 | 1 | 0 | 38880.5963 | 1 | 0 | 168.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242238 | 242238 | 242237.9994
38880.5965 | 1 | 1 | 38880.5965 | 1 | 0 | 189.5 | 271.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 586792486.44 | 242238 | 242038.0825
38880.5967 | 3 | 0 | 38880.5968 | 35 | 0 | 210.5 | 292.5 | 0.18315 | 0 | 2.1368 | 0 | 0.0018315 | 0 | 0.021368 | 0 | 0.0018315 | 0.021368 | 80679.3333 | 6823.9429 | 80679.3315
38880.597 | 2407 | 0 | 38880.597 | 598 | 0 | 231.5 | 313.5 | 146.9475 | 0 | 36.5079 | 0 | 1.4695 | 0 | 0.36508 | 0 | 1.4695 | 0.36508 | 0.68052 | 305.2475 | 0.78896
38880.5972 | 2152 | 0 | 38880.5972 | 1298 | 0 | 252.5 | 334.5 | 131.3797 | 0 | 79.243 | 0 | 1.3138 | 0 | 0.79243 | 0 | 1.3138 | 0.79243 | 12.6106 | 86.7011 | 11.2968
38880.5975 | 2375 | 0 | 38880.5975 | 2021 | 0 | 273.5 | 355.5 | 144.9939 | 0 | 123.3822 | 0 | 1.4499 | 0 | 1.2338 | 0 | 1.4499 | 1.2338 | 2.0371 | 19.9099 | 0.58711
38880.5977 | 2055 | 0 | 38880.5977 | 1833 | 0 | 294.5 | 376.5 | 125.4579 | 0 | 111.9048 | 0 | 1.2546 | 0 | 1.119 | 0 | 1.2546 | 1.119 | 17.926 | 32.2084 | 16.6715
38880.598 | 2369 | 0 | 38880.598 | 2088 | 0 | 315.5 | 397.5 | 144.6276 | 0 | 127.4725 | 0 | 1.4463 | 0 | 1.2747 | 0 | 1.4463 | 1.2747 | 2.2955 | 16.0623 | 0.84921
38880.5982 | 1994 | 0 | 38880.5982 | 2342 | 0 | 336.5 | 418.5 | 121.7338 | 0 | 142.9792 | 0 | 1.2173 | 0 | 1.4298 | 0 | 1.2173 | 1.4298 | 21.5336 | 3.4748 | 20.3163
38880.5984 | 2128 | 0 | 38880.5985 | 2217 | 0 | 357.5 | 439.5 | 129.9145 | 0 | 135.348 | 0 | 1.2991 | 0 | 1.3535 | 0 | 1.2991 | 1.3535 | 13.8806 | 9.309 | 12.5815
38880.5987 | 2048 | 0 | 38880.5987 | 1936 | 0 | 378.5 | 460.5 | 125.0305 | 0 | 118.1929 | 0 | 1.2503 | 0 | 1.1819 | 0 | 1.2503 | 1.1819 | 18.3291 | 25.1746 | 17.0788
38880.5989 | 2393 | 0 | 38880.5989 | 2091 | 0 | 399.5 | 481.5 | 146.0928 | 0 | 127.6557 | 0 | 1.4609 | 0 | 1.2766 | 0 | 1.4609 | 1.2766 | 1.2695 | 15.8957 | 0.19139
38880.5992 | 1941 | 0 | 38880.5992 | 2394 | 0 | 420.5 | 502.5 | 118.4982 | 0 | 146.1538 | 0 | 1.185 | 0 | 1.4615 | 0 | 1.185 | 1.4615 | 24.8521 | 1.2272 | 23.6672
38880.5994 | 2078 | 0 | 38880.5994 | 1918 | 0 | 441.5 | 523.5 | 126.862 | 0 | 117.094 | 0 | 1.2686 | 0 | 1.1709 | 0 | 1.2686 | 1.1709 | 16.6208 | 26.3493 | 15.3522
38880.5997 | 2237 | 0 | 38880.5997 | 2052 | 0 | 462.5 | 544.5 | 136.569 | 0 | 125.2747 | 0 | 1.3657 | 0 | 1.2527 | 0 | 1.3657 | 1.2527 | 8.3317 | 18.0984 | 6.966
38880.5999 | 1676 | 0 | 38880.5999 | 2260 | 0 | 483.5 | 565.5 | 102.3199 | 0 | 137.9731 | 0 | 1.0232 | 0 | 1.3797 | 0 | 1.0232 | 1.3797 | 44.5931 | 7.2292 | 43.5699
38880.6002 | 2233 | 0 | 38880.6002 | 2184 | 0 | 504.5 | 586.5 | 136.3248 | 0 | 133.3333 | 0 | 1.3632 | 0 | 1.3333 | 0 | 1.3632 | 1.3333 | 8.5258 | 10.9606 | 7.1625

## C5-6
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 156.0672 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38880.5936 | 1 | 0 | 38880.5936 | 1 | 0 | -63.5 | 18.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5938 | 1 | 0 | 38880.5938 | 1 | 0 | -42.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5941 | 1 | 0 | 38880.5941 | 1 | 0 | -21.5 | 60.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5943 | 1 | 0 | 38880.5943 | 1 | 0 | -0.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5945 | 1 | 0 | 38880.5946 | 1 | 0 | 20.5 | 102.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5948 | 1 | 0 | 38880.5948 | 1 | 1 | 41.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 255538 | 255538 | 255537.9994
38880.5953 | 1 | 0 | 38880.5953 | 1 | 0 | 83.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 104.5 | 186.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5958 | 2 | 0 | 38880.5958 | 1 | 0 | 125.5 | 207.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127719 | 255538 | 127718.9988
38880.596 | 1 | 1 | 38880.596 | 1 | 0 | 146.5 | 228.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 652996694.44 | 255538 | 255338.0782
38880.5963 | 1 | 0 | 38880.5963 | 1 | 0 | 167.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5965 | 1 | 0 | 38880.5965 | 1 | 0 | 188.5 | 270.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38880.5967 | 1 | 0 | 38880.5967 | 576 | 0 | 209.5 | 291.5 | 0.06105 | 0 | 35.1648 | 0 | 0.0006105 | 0 | 0.35165 | 0 | 0.0006105 | 0.35165 | 255538 | 343.816 | 255537.9994
38880.597 | 2061 | 0 | 38880.597 | 1718 | 0 | 230.5 | 312.5 | 125.8242 | 0 | 104.884 | 0 | 1.2582 | 0 | 1.0488 | 0 | 1.2582 | 1.0488 | 24.0359 | 48.7998 | 22.7777
38880.5972 | 2540 | 0 | 38880.5972 | 1438 | 0 | 251.5 | 333.5 | 155.0672 | 0 | 87.79 | 0 | 1.5507 | 0 | 0.8779 | 0 | 1.5507 | 0.8779 | 0.64488 | 77.7733 | 0.90579
38880.5975 | 1977 | 0 | 38880.5975 | 2517 | 0 | 272.5 | 354.5 | 120.696 | 0 | 153.663 | 0 | 1.207 | 0 | 1.5366 | 0 | 1.207 | 1.5366 | 29.306 | 1.5646 | 28.0991
38880.5977 | 2111 | 0 | 38880.5977 | 2094 | 0 | 293.5 | 375.5 | 128.8767 | 0 | 127.8388 | 0 | 1.2888 | 0 | 1.2784 | 0 | 1.2888 | 1.2784 | 21.0981 | 22.0812 | 19.8093
38880.598 | 2210 | 0 | 38880.598 | 2383 | 0 | 314.5 | 396.5 | 134.9206 | 0 | 145.4823 | 0 | 1.3492 | 0 | 1.4548 | 0 | 1.3492 | 1.4548 | 15.6733 | 7.2757 | 14.3241
38880.5982 | 2385 | 0 | 38880.5982 | 2092 | 0 | 335.5 | 417.5 | 145.6044 | 0 | 127.7167 | 0 | 1.456 | 0 | 1.2772 | 0 | 1.456 | 1.2772 | 7.1857 | 22.1979 | 5.7297
38880.5984 | 2464 | 0 | 38880.5984 | 2130 | 0 | 356.5 | 438.5 | 150.4274 | 0 | 130.0366 | 0 | 1.5043 | 0 | 1.3004 | 0 | 1.5043 | 1.3004 | 3.7492 | 20.0178 | 2.2449
38880.5987 | 1979 | 0 | 38880.5987 | 2448 | 0 | 377.5 | 459.5 | 120.8181 | 0 | 149.4505 | 0 | 1.2082 | 0 | 1.4945 | 0 | 1.2082 | 1.4945 | 29.1753 | 4.4273 | 27.9672
38880.5989 | 1981 | 0 | 38880.5989 | 2004 | 0 | 398.5 | 480.5 | 120.9402 | 0 | 122.3443 | 0 | 1.2094 | 0 | 1.2234 | 0 | 1.2094 | 1.2234 | 29.0449 | 27.5639 | 27.8355
38880.5992 | 2359 | 0 | 38880.5992 | 1864 | 0 | 419.5 | 501.5 | 144.0171 | 0 | 113.7973 | 0 | 1.4402 | 0 | 1.138 | 0 | 1.4402 | 1.138 | 8.3671 | 37.1448 | 6.9269
38880.5994 | 2436 | 0 | 38880.5994 | 1747 | 0 | 440.5 | 522.5 | 148.7179 | 0 | 106.6545 | 0 | 1.4872 | 0 | 1.0665 | 0 | 1.4872 | 1.0665 | 4.9417 | 46.3297 | 3.4545
38880.5997 | 1881 | 0 | 38880.5997 | 2234 | 0 | 461.5 | 543.5 | 114.8352 | 0 | 136.3858 | 0 | 1.1484 | 0 | 1.3639 | 0 | 1.1484 | 1.3639 | 35.9054 | 14.4306 | 34.757
38880.5999 | 1820 | 1 | 38880.5999 | 2198 | 0 | 482.5 | 564.5 | 111.1111 | 0.06105 | 134.188 | 0 | 1.1111 | 0.0006105 | 1.3419 | 0 | 1.1105 | 1.3419 | 40.6196 | 16.3048 | 10309.3235
38880.6001 | 1965 | 0 | 38880.6002 | 1743 | 2 | 503.5 | 585.5 | 119.9634 | 0 | 106.4103 | 0.1221 | 1.1996 | 0 | 1.0641 | 0.001221 | 1.1996 | 1.0629 | 30.0957 | 46.834 | 28.896

## C4-7
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 155.823 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38880.5936 | 1 | 1 | 38880.5936 | 1 | 0 | -64.5 | 17.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 650953990.44 | 255138 | 254938.0784
38880.5938 | 1 | 0 | 38880.5938 | 1 | 0 | -43.5 | 38.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5941 | 1 | 0 | 38880.5941 | 1 | 0 | -22.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5943 | 1 | 0 | 38880.5943 | 1 | 0 | -1.5 | 80.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 19.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5948 | 1 | 0 | 38880.5948 | 1 | 0 | 40.5 | 122.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5953 | 1 | 0 | 38880.5953 | 1 | 0 | 82.5 | 164.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 103.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5958 | 1 | 0 | 38880.5958 | 1 | 0 | 124.5 | 206.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.596 | 1 | 0 | 38880.596 | 1 | 0 | 145.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5962 | 1 | 0 |  | 1 | 0 | 166 | 248 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5965 | 1 | 0 | 38880.5965 | 1 | 0 | 187.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38880.5967 | 2 | 0 | 38880.5967 | 4 | 0 | 208.5 | 290.5 | 0.1221 | 0 | 0.2442 | 0 | 0.001221 | 0 | 0.002442 | 0 | 0.001221 | 0.002442 | 127519 | 63709.5 | 127518.9988
38880.597 | 2099 | 0 | 38880.597 | 563 | 0 | 229.5 | 311.5 | 128.1441 | 0 | 34.3712 | 0 | 1.2814 | 0 | 0.34371 | 0 | 1.2814 | 0.34371 | 21.5998 | 353.3535 | 20.3184
38880.5972 | 2115 | 0 | 38880.5972 | 1301 | 1 | 250.5 | 332.5 | 129.1209 | 0 | 79.4261 | 0.06105 | 1.2912 | 0 | 0.79426 | 0.0006105 | 1.2912 | 0.79365 | 20.6799 | 96.186 | 19.3887
38880.5975 | 1992 | 0 | 38880.5975 | 2032 | 0 | 271.5 | 353.5 | 121.6117 | 0 | 124.0537 | 0 | 1.2161 | 0 | 1.2405 | 0 | 1.2161 | 1.2405 | 28.1315 | 25.6093 | 26.9154
38880.5977 | 2457 | 0 | 38880.5977 | 1857 | 0 | 292.5 | 374.5 | 150 | 0 | 113.37 | 0 | 1.5 | 0 | 1.1337 | 0 | 1.5 | 1.1337 | 3.882 | 37.4464 | 2.382
38880.5979 | 1967 | 0 | 38880.598 | 2377 | 0 | 313.5 | 395.5 | 120.0855 | 0 | 145.116 | 0 | 1.2009 | 0 | 1.4512 | 0 | 1.2009 | 1.4512 | 29.76 | 7.3782 | 28.5592
38880.5982 | 1946 | 0 | 38880.5982 | 2536 | 0 | 334.5 | 416.5 | 118.8034 | 0 | 154.823 | 0 | 1.188 | 0 | 1.5482 | 0 | 1.188 | 1.5482 | 31.1603 | 0.6459 | 29.9723
38880.5984 | 2444 | 0 | 38880.5984 | 2417 | 0 | 355.5 | 437.5 | 149.2063 | 0 | 147.558 | 0 | 1.4921 | 0 | 1.4756 | 0 | 1.4921 | 1.4756 | 4.4345 | 5.6012 | 2.9425
38880.5987 | 1933 | 0 | 38880.5987 | 1946 | 0 | 376.5 | 458.5 | 118.0098 | 0 | 118.8034 | 0 | 1.1801 | 0 | 1.188 | 0 | 1.1801 | 1.188 | 32.0424 | 31.1603 | 30.8623
38880.5989 | 2274 | 0 | 38880.5989 | 2098 | 0 | 397.5 | 479.5 | 138.8278 | 0 | 128.083 | 0 | 1.3883 | 0 | 1.2808 | 0 | 1.3883 | 1.2808 | 12.2419 | 21.6578 | 10.8536
38880.5992 | 2040 | 0 | 38880.5992 | 2465 | 0 | 418.5 | 500.5 | 124.5421 | 0 | 150.4884 | 0 | 1.2454 | 0 | 1.5049 | 0 | 1.2454 | 1.5049 | 25.1167 | 3.5448 | 23.8712
38880.5994 | 2040 | 0 | 38880.5994 | 2070 | 0 | 439.5 | 521.5 | 124.5421 | 0 | 126.3736 | 0 | 1.2454 | 0 | 1.2637 | 0 | 1.2454 | 1.2637 | 25.1167 | 23.3034 | 23.8712
38880.5996 | 2196 | 0 | 38880.5997 | 1999 | 0 | 460.5 | 542.5 | 134.0659 | 0 | 122.0391 | 0 | 1.3407 | 0 | 1.2204 | 0 | 1.3407 | 1.2204 | 16.2286 | 27.6828 | 14.8879
38880.5999 | 1740 | 0 | 38880.5999 | 2070 | 0 | 481.5 | 563.5 | 106.2271 | 0 | 126.3736 | 0 | 1.0623 | 0 | 1.2637 | 0 | 1.0623 | 1.2637 | 46.6885 | 23.3034 | 45.6262
38880.6001 | 1801 | 0 | 38880.6001 | 1854 | 0 | 502.5 | 584.5 | 109.9512 | 0 | 113.1868 | 0 | 1.0995 | 0 | 1.1319 | 0 | 1.0995 | 1.1319 | 41.7202 | 37.6688 | 40.6206

## C4-6
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 153.9915 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38880.5936 | 2 | 0 | 38880.5936 | 1 | 0 | -65.5 | 16.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126019 | 252138 | 126018.9988
38880.5938 | 1 | 0 | 38880.5938 | 1 | 0 | -44.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.594 | 1 | 0 | 38880.5941 | 1 | 0 | -23.5 | 58.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5943 | 1 | 0 | 38880.5943 | 1 | 0 | -2.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 18.5 | 100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5948 | 1 | 0 | 38880.5948 | 1 | 0 | 39.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5953 | 1 | 0 | 38880.5953 | 1 | 0 | 81.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 102.5 | 184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5957 | 1 | 0 | 38880.5958 | 1 | 0 | 123.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.596 | 1 | 0 | 38880.596 | 1 | 0 | 144.5 | 226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5962 | 1 | 0 | 38880.5962 | 1 | 0 | 165.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38880.5965 | 1 | 0 | 38880.5965 | 2 | 0 | 186.5 | 268.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252138 | 126019 | 252137.9994
38880.5967 | 1 | 0 | 38880.5967 | 185 | 0 | 207.5 | 289.5 | 0.06105 | 0 | 11.2943 | 0 | 0.0006105 | 0 | 0.11294 | 0 | 0.0006105 | 0.11294 | 252138 | 1263.4486 | 252137.9994
38880.597 | 2253 | 1 | 38880.597 | 1577 | 0 | 228.5 | 310.5 | 137.5458 | 0.06105 | 96.2759 | 0 | 1.3755 | 0.0006105 | 0.96276 | 0 | 1.3748 | 0.96276 | 11.9707 | 59.948 | 10058.797
38880.5972 | 2469 | 0 | 38880.5972 | 1457 | 0 | 249.5 | 331.5 | 150.7326 | 0 | 88.9499 | 0 | 1.5073 | 0 | 0.8895 | 0 | 1.5073 | 0.8895 | 2.162 | 73.1215 | 0.65468
38880.5974 | 2255 | 0 | 38880.5975 | 2459 | 0 | 270.5 | 352.5 | 137.6679 | 0 | 150.1221 | 0 | 1.3767 | 0 | 1.5012 | 0 | 1.3767 | 1.5012 | 11.8572 | 2.5775 | 10.4805
38880.5977 | 2199 | 0 | 38880.5977 | 2062 | 0 | 291.5 | 373.5 | 134.2491 | 0 | 125.8852 | 0 | 1.3425 | 0 | 1.2589 | 0 | 1.3425 | 1.2589 | 14.7058 | 22.3269 | 13.3633
38880.5979 | 2506 | 0 | 38880.5979 | 2199 | 0 | 312.5 | 394.5 | 152.9915 | 0 | 134.2491 | 0 | 1.5299 | 0 | 1.3425 | 0 | 1.5299 | 1.3425 | 0.65363 | 14.7058 | 0.87628
38880.5982 | 2398 | 0 | 38880.5982 | 2027 | 0 | 333.5 | 415.5 | 146.398 | 0 | 123.7485 | 0 | 1.464 | 0 | 1.2375 | 0 | 1.464 | 1.2375 | 5.1868 | 24.4391 | 3.7228
38880.5984 | 2212 | 0 | 38880.5984 | 1886 | 0 | 354.5 | 436.5 | 135.0427 | 0 | 115.1404 | 0 | 1.3504 | 0 | 1.1514 | 0 | 1.3504 | 1.1514 | 14.0316 | 33.7423 | 12.6812
38880.5987 | 2300 | 0 | 38880.5987 | 1990 | 0 | 375.5 | 457.5 | 140.4151 | 0 | 121.4896 | 0 | 1.4042 | 0 | 1.2149 | 0 | 1.4042 | 1.2149 | 9.6687 | 26.7528 | 8.2645
38880.5989 | 1986 | 0 | 38880.5989 | 2224 | 0 | 396.5 | 478.5 | 121.2454 | 0 | 135.7753 | 0 | 1.2125 | 0 | 1.3578 | 0 | 1.2125 | 1.3578 | 27.0081 | 13.4164 | 25.7956
38880.5991 | 2105 | 0 | 38880.5992 | 1671 | 0 | 417.5 | 499.5 | 128.5104 | 0 | 102.0147 | 0 | 1.2851 | 0 | 1.0201 | 0 | 1.2851 | 1.0201 | 19.828 | 50.9503 | 18.5429
38880.5994 | 2137 | 0 | 38880.5994 | 1705 | 0 | 438.5 | 520.5 | 130.464 | 0 | 104.0904 | 0 | 1.3046 | 0 | 1.0409 | 0 | 1.3046 | 1.0409 | 18.0337 | 47.9402 | 16.7291
38880.5996 | 2011 | 0 | 38880.5996 | 1739 | 0 | 459.5 | 541.5 | 122.7717 | 0 | 106.1661 | 0 | 1.2277 | 0 | 1.0617 | 0 | 1.2277 | 1.0617 | 25.4291 | 45.0477 | 24.2014
38880.5999 | 1906 | 1 | 38880.5999 | 2120 | 0 | 480.5 | 562.5 | 116.3614 | 0.06105 | 129.4261 | 0 | 1.1636 | 0.0006105 | 1.2943 | 0 | 1.163 | 1.2943 | 32.4456 | 18.9802 | 9816.7843
38880.6001 | 1679 | 0 | 38880.6001 | 1865 | 0 | 501.5 | 583.5 | 102.5031 | 0 | 113.8584 | 0 | 1.025 | 0 | 1.1386 | 0 | 1.025 | 1.1386 | 50.2311 | 35.2483 | 49.2061

## C4-5
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 154.9072 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38880.5935 | 1 | 0 | 38880.5936 | 1 | 0 | -66.5 | 15.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5938 | 1 | 0 | 38880.5938 | 1 | 0 | -45.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.594 | 1 | 0 | 38880.594 | 1 | 0 | -24.5 | 57.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5943 | 1 | 0 | 38880.5943 | 1 | 0 | -3.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 17.5 | 99.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5948 | 1 | 0 | 38880.5948 | 1 | 0 | 38.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5952 | 1 | 0 | 38880.5953 | 1 | 0 | 80.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 101.5 | 183.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5957 | 1 | 0 | 38880.5957 | 1 | 0 | 122.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.596 | 1 | 0 | 38880.596 | 1 | 0 | 143.5 | 225.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5962 | 1 | 0 | 38880.5962 | 1 | 0 | 164.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5965 | 1 | 0 | 38880.5965 | 1 | 0 | 185.5 | 267.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5967 | 1 | 0 | 38880.5967 | 1 | 0 | 206.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38880.5969 | 1926 | 0 | 38880.597 | 2377 | 1 | 227.5 | 309.5 | 117.5824 | 0 | 145.116 | 0.06105 | 1.1758 | 0 | 1.4512 | 0.0006105 | 1.1758 | 1.4505 | 31.7435 | 6.7921 | 30.5677
38880.5972 | 2095 | 0 | 38880.5972 | 2521 | 0 | 248.5 | 330.5 | 127.8999 | 0 | 153.9072 | 0 | 1.279 | 0 | 1.5391 | 0 | 1.279 | 1.5391 | 21.116 | 0.64974 | 19.837
38880.5974 | 2231 | 0 | 38880.5974 | 2037 | 0 | 269.5 | 351.5 | 136.2027 | 0 | 124.359 | 0 | 1.362 | 0 | 1.2436 | 0 | 1.362 | 1.2436 | 13.7329 | 24.5646 | 12.3708
38880.5977 | 2263 | 0 | 38880.5977 | 2385 | 0 | 290.5 | 372.5 | 138.1563 | 0 | 145.6044 | 0 | 1.3816 | 0 | 1.456 | 0 | 1.3816 | 1.456 | 12.1246 | 6.3891 | 10.7431
38880.5979 | 2520 | 0 | 38880.5979 | 2046 | 0 | 311.5 | 393.5 | 153.8462 | 0 | 124.9084 | 0 | 1.5385 | 0 | 1.2491 | 0 | 1.5385 | 1.2491 | 0.68968 | 24.0166 | 0.84878
38880.5982 | 2057 | 0 | 38880.5982 | 2397 | 0 | 332.5 | 414.5 | 125.58 | 0 | 146.337 | 0 | 1.2558 | 0 | 1.4634 | 0 | 1.2558 | 1.4634 | 23.3534 | 5.8565 | 22.0976
38880.5984 | 1970 | 0 | 38880.5984 | 2338 | 0 | 353.5 | 435.5 | 120.2686 | 0 | 142.735 | 0 | 1.2027 | 0 | 1.4274 | 0 | 1.2027 | 1.4274 | 28.801 | 8.5278 | 27.5983
38880.5986 | 1970 | 0 | 38880.5987 | 2486 | 0 | 374.5 | 456.5 | 120.2686 | 0 | 151.7705 | 0 | 1.2027 | 0 | 1.5177 | 0 | 1.2027 | 1.5177 | 28.801 | 2.0668 | 27.5983
38880.5989 | 2297 | 0 | 38880.5989 | 2300 | 0 | 395.5 | 477.5 | 140.232 | 0 | 140.4151 | 0 | 1.4023 | 0 | 1.4042 | 0 | 1.4023 | 1.4042 | 10.465 | 10.3209 | 9.0626
38880.5991 | 1976 | 0 | 38880.5991 | 2342 | 0 | 416.5 | 498.5 | 120.6349 | 0 | 142.9792 | 0 | 1.2063 | 0 | 1.4298 | 0 | 1.2063 | 1.4298 | 28.4099 | 8.3424 | 27.2036
38880.5994 | 1842 | 0 | 38880.5994 | 2402 | 0 | 437.5 | 519.5 | 112.4542 | 0 | 146.6422 | 0 | 1.1245 | 0 | 1.4664 | 0 | 1.1245 | 1.4664 | 37.7514 | 5.6361 | 36.6268
38880.5996 | 2247 | 0 | 38880.5996 | 2296 | 0 | 458.5 | 540.5 | 137.1795 | 0 | 140.1709 | 0 | 1.3718 | 0 | 1.4017 | 0 | 1.3718 | 1.4017 | 12.923 | 10.5131 | 11.5512
38880.5999 | 1936 | 62 | 38880.5999 | 1792 | 87 | 479.5 | 561.5 | 118.1929 | 3.7851 | 109.4017 | 5.3114 | 1.1819 | 0.037851 | 1.094 | 0.053114 | 1.1441 | 1.0409 | 34.3003 | 51.3574 | 295.1906
38880.6001 | 1946 | 42 | 38880.6001 | 1703 | 73 | 500.5 | 582.5 | 118.8034 | 2.5641 | 103.9683 | 4.4567 | 1.188 | 0.025641 | 1.0397 | 0.044567 | 1.1624 | 0.99512 | 32.2569 | 59.4418 | 487.6558

## C3-7
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 148.1306 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38880.5935 | 1 | 0 | 38880.5935 | 1 | 0 | -67.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5938 | 1 | 0 | 38880.5938 | 2 | 0 | -46.5 | 35.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 242538 | 121219 | 242537.9994
38880.594 | 2 | 0 | 38880.594 | 1 | 0 | -25.5 | 56.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121219 | 242538 | 121218.9988
38880.5943 | 1 | 0 | 38880.5943 | 1 | 0 | -4.5 | 77.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 16.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5947 | 1 | 0 | 38880.5948 | 1 | 1 | 37.5 | 119.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 242538 | 242538 | 242537.9994
38880.5952 | 1 | 0 | 38880.5952 | 1 | 0 | 79.5 | 161.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 100.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5957 | 1 | 0 | 38880.5957 | 1 | 0 | 121.5 | 203.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.596 | 1 | 0 | 38880.596 | 1 | 0 | 142.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5962 | 1 | 0 | 38880.5962 | 1 | 0 | 163.5 | 245.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5964 | 1 | 0 | 38880.5965 | 1 | 0 | 184.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5967 | 1 | 0 | 38880.5967 | 1 | 0 | 205.5 | 287.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5969 | 551 | 10 |  | 354 | 7 | 226 | 308 | 33.6386 | 0.6105 | 21.6117 | 0.42735 | 0.33639 | 0.006105 | 0.21612 | 0.0042735 | 0.33028 | 0.21184 | 347.7206 | 600.7127 | 15991.6818
38880.5972 | 2159 | 0 | 38880.5972 | 1146 | 0 | 247.5 | 329.5 | 131.8071 | 0 | 69.9634 | 0 | 1.3181 | 0 | 0.69963 | 0 | 1.3181 | 0.69963 | 12.3844 | 111.726 | 11.0664
38880.5974 | 1448 | 1 | 38880.5974 | 2410 | 0 | 268.5 | 350.5 | 88.4005 | 0.06105 | 147.1306 | 0 | 0.884 | 0.0006105 | 1.4713 | 0 | 0.88339 | 1.4713 | 75.2676 | 0.67967 | 659.8094
38880.5977 | 1880 | 0 | 38880.5977 | 1988 | 0 | 289.5 | 371.5 | 114.7741 | 0 | 121.3675 | 0 | 1.1477 | 0 | 1.2137 | 0 | 1.1477 | 1.2137 | 29.0628 | 22.0513 | 27.915
38880.5979 | 1930 | 0 | 38880.5979 | 1877 | 0 | 310.5 | 392.5 | 117.8266 | 0 | 114.591 | 0 | 1.1783 | 0 | 1.1459 | 0 | 1.1783 | 1.1459 | 25.7192 | 29.269 | 24.5409
38880.5981 | 1943 | 0 | 38880.5982 | 1979 | 0 | 331.5 | 413.5 | 118.6203 | 0 | 120.8181 | 0 | 1.1862 | 0 | 1.2082 | 0 | 1.1862 | 1.2082 | 24.878 | 22.6064 | 23.6918
38880.5984 | 1833 | 0 | 38880.5984 | 1926 | 0 | 352.5 | 434.5 | 111.9048 | 0 | 117.5824 | 0 | 1.119 | 0 | 1.1758 | 0 | 1.119 | 1.1758 | 32.3721 | 25.9803 | 31.253
38880.5986 | 1898 | 2 | 38880.5986 | 2142 | 0 | 373.5 | 455.5 | 115.873 | 0.1221 | 130.7692 | 0 | 1.1587 | 0.001221 | 1.3077 | 0 | 1.1575 | 1.3077 | 28.0913 | 13.2764 | 3084.6764
38880.5989 | 1250 | 0 | 38880.5989 | 2206 | 0 | 394.5 | 476.5 | 76.3126 | 0 | 134.6764 | 0 | 0.76313 | 0 | 1.3468 | 0 | 0.76313 | 1.3468 | 94.1104 | 9.99 | 93.3473
38880.5991 | 1668 | 0 | 38880.5991 | 1962 | 0 | 415.5 | 497.5 | 101.8315 | 0 | 119.7802 | 0 | 1.0183 | 0 | 1.1978 | 0 | 1.0183 | 1.1978 | 45.4664 | 23.6687 | 44.4481
38880.5994 | 2028 | 0 | 38880.5994 | 2089 | 0 | 436.5 | 518.5 | 123.8095 | 0 | 127.5336 | 0 | 1.2381 | 0 | 1.2753 | 0 | 1.2381 | 1.2753 | 19.644 | 16.1503 | 18.4059
38880.5996 | 1084 | 1 | 38880.5996 | 2320 | 0 | 457.5 | 539.5 | 66.1783 | 0.06105 | 141.6361 | 0 | 0.66178 | 0.0006105 | 1.4164 | 0 | 0.66117 | 1.4164 | 126.4974 | 4.5853 | 5881.0246
38880.5998 | 766 | 0 | 38880.5999 | 2376 | 0 | 478.5 | 560.5 | 46.7643 | 0 | 145.0549 | 0 | 0.46764 | 0 | 1.4505 | 0 | 0.46764 | 1.4505 | 216.7598 | 2.1204 | 216.2921
38880.6001 | 539 | 0 | 38880.6001 | 2016 | 0 | 499.5 | 581.5 | 32.906 | 0 | 123.0769 | 0 | 0.32906 | 0 | 1.2308 | 0 | 0.32906 | 1.2308 | 350.1633 | 20.3562 | 349.8342

## C3-6
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 152.221 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38880.5935 | 2 | 0 | 38880.5935 | 1 | 0 | -68.5 | 13.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124569 | 249238 | 124568.9988
38880.5938 | 1 | 0 | 38880.5938 | 1 | 0 | -47.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.594 | 1 | 0 | 38880.594 | 1 | 0 | -26.5 | 55.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5942 | 1 | 0 | 38880.5943 | 1 | 0 | -5.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 15.5 | 97.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5947 | 1 | 0 | 38880.5947 | 1 | 0 | 36.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5952 | 1 | 0 | 38880.5952 | 1 | 0 | 78.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 99.5 | 181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5957 | 1 | 0 | 38880.5957 | 1 | 0 | 120.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5959 | 1 | 0 | 38880.596 | 1 | 0 | 141.5 | 223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5962 | 1 | 0 | 38880.5962 | 1 | 0 | 162.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38880.5964 | 2 | 0 | 38880.5964 | 1 | 0 | 183.5 | 265.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124569 | 249238 | 124568.9988
38880.5967 | 1 | 0 | 38880.5967 | 3 | 0 | 204.5 | 286.5 | 0.06105 | 0 | 0.18315 | 0 | 0.0006105 | 0 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 249238 | 83012.6667 | 249237.9994
38880.5969 | 426 | 0 | 38880.5969 | 861 | 0 | 225.5 | 307.5 | 26.0073 | 0 | 52.5641 | 0 | 0.26007 | 0 | 0.52564 | 0 | 0.26007 | 0.52564 | 485.3005 | 189.5912 | 485.0404
38880.5972 | 2477 | 0 | 38880.5972 | 1621 | 0 | 246.5 | 328.5 | 151.221 | 0 | 98.9621 | 0 | 1.5122 | 0 | 0.98962 | 0 | 1.5122 | 0.98962 | 0.66128 | 53.8174 | 0.85093
38880.5974 | 1699 | 0 | 38880.5974 | 2454 | 0 | 267.5 | 349.5 | 103.7241 | 0 | 149.8168 | 0 | 1.0372 | 0 | 1.4982 | 0 | 1.0372 | 1.4982 | 46.7557 | 1.6047 | 45.7185
38880.5977 | 2328 | 0 | 38880.5977 | 2195 | 0 | 288.5 | 370.5 | 142.1245 | 0 | 134.0049 | 0 | 1.4212 | 0 | 1.34 | 0 | 1.4212 | 1.34 | 7.104 | 13.5936 | 5.6827
38880.5979 | 2295 | 0 | 38880.5979 | 2164 | 0 | 309.5 | 391.5 | 140.1099 | 0 | 132.1123 | 0 | 1.4011 | 0 | 1.3211 | 0 | 1.4011 | 1.3211 | 8.644 | 15.2209 | 7.2429
38880.5981 | 2344 | 0 | 38880.5981 | 2397 | 0 | 330.5 | 412.5 | 143.1013 | 0 | 146.337 | 0 | 1.431 | 0 | 1.4634 | 0 | 1.431 | 1.4634 | 6.3729 | 4.0209 | 4.9419
38880.5984 | 1981 | 0 | 38880.5984 | 2172 | 0 | 351.5 | 433.5 | 120.9402 | 0 | 132.6007 | 0 | 1.2094 | 0 | 1.326 | 0 | 1.2094 | 1.326 | 25.8647 | 14.7965 | 24.6553
38880.5986 | 1775 | 1 | 38880.5986 | 2035 | 0 | 372.5 | 454.5 | 108.3639 | 0.06105 | 124.2369 | 0 | 1.0836 | 0.0006105 | 1.2424 | 0 | 1.083 | 1.2424 | 40.5965 | 22.5248 | 13188.2282
38880.5989 | 1556 | 0 | 38880.5989 | 2008 | 0 | 393.5 | 475.5 | 94.9939 | 0 | 122.5885 | 0 | 0.94994 | 0 | 1.2259 | 0 | 0.94994 | 1.2259 | 60.2429 | 24.1723 | 59.293
38880.5991 | 2093 | 0 | 38880.5991 | 2289 | 0 | 414.5 | 496.5 | 127.7778 | 0 | 139.7436 | 0 | 1.2778 | 0 | 1.3974 | 0 | 1.2778 | 1.3974 | 19.1295 | 8.9288 | 17.8517
38880.5994 | 2203 | 0 | 38880.5994 | 2170 | 0 | 435.5 | 517.5 | 134.4933 | 0 | 132.4786 | 0 | 1.3449 | 0 | 1.3248 | 0 | 1.3449 | 1.3248 | 13.1811 | 14.9023 | 11.8362
38880.5996 | 1343 | 0 | 38880.5996 | 1915 | 0 | 456.5 | 538.5 | 81.9902 | 0 | 116.9109 | 0 | 0.8199 | 0 | 1.1691 | 0 | 0.8199 | 1.1691 | 85.6575 | 30.2026 | 84.8376
38880.5998 | 1797 | 2 | 38880.5998 | 1266 | 0 | 477.5 | 559.5 | 109.707 | 0.1221 | 77.2894 | 0 | 1.0971 | 0.001221 | 0.77289 | 0 | 1.0958 | 0.77289 | 38.8402 | 96.9494 | 17090.6184
38880.6001 | 790 | 0 | 38880.6001 | 1796 | 0 | 498.5 | 580.5 | 48.2295 | 0 | 109.6459 | 0 | 0.4823 | 0 | 1.0965 | 0 | 0.4823 | 1.0965 | 215.6177 | 38.8296 | 215.1354

## C3-5
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 153.2589 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38880.5935 | 1 | 0 | 38880.5935 | 1 | 0 | -69.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5938 | 1 | 0 | 38880.5938 | 1 | 0 | -48.5 | 33.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.594 | 1 | 0 | 38880.594 | 1 | 0 | -27.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -6.5 | 75.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 14.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5947 | 1 | 0 | 38880.5947 | 1 | 0 | 35.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5952 | 1 | 0 | 38880.5952 | 1 | 0 | 77.5 | 159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5955 | 1 | 0 | 38880.5955 | 1 | 0 | 98.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5957 | 1 | 0 | 38880.5957 | 1 | 0 | 119.5 | 201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5959 | 1 | 1 | 38880.5959 | 1 | 0 | 140.5 | 222.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 629698798.44 | 250938 | 250738.0797
38880.5962 | 1 | 0 | 38880.5962 | 1 | 0 | 161.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5964 | 1 | 0 | 38880.5964 | 1 | 0 | 182.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5967 | 1 | 0 | 38880.5967 | 1 | 0 | 203.5 | 285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38880.5969 | 136 | 0 | 38880.5969 | 2326 | 0 | 224.5 | 306.5 | 8.3028 | 0 | 142.0024 | 0 | 0.083028 | 0 | 1.42 | 0 | 0.083028 | 1.42 | 1745.8676 | 7.9269 | 1745.7846
38880.5972 | 2196 | 0 | 38880.5972 | 2106 | 0 | 245.5 | 327.5 | 134.0659 | 0 | 128.5714 | 0 | 1.3407 | 0 | 1.2857 | 0 | 1.3407 | 1.2857 | 14.316 | 19.2013 | 12.9754
38880.5974 | 1901 | 0 | 38880.5974 | 2164 | 0 | 266.5 | 348.5 | 116.0562 | 0 | 132.1123 | 0 | 1.1606 | 0 | 1.3211 | 0 | 1.1606 | 1.3211 | 32.0558 | 16.0065 | 30.8952
38880.5976 | 2337 | 0 | 38880.5977 | 2494 | 0 | 287.5 | 369.5 | 142.674 | 0 | 152.2589 | 0 | 1.4267 | 0 | 1.5226 | 0 | 1.4267 | 1.5226 | 7.4189 | 0.65678 | 5.9922
38880.5979 | 1957 | 0 | 38880.5979 | 2082 | 0 | 308.5 | 390.5 | 119.475 | 0 | 127.1062 | 0 | 1.1947 | 0 | 1.2711 | 0 | 1.1947 | 1.2711 | 28.277 | 20.5754 | 27.0822
38880.5981 | 2142 | 0 | 38880.5981 | 2079 | 0 | 329.5 | 411.5 | 130.7692 | 0 | 126.9231 | 0 | 1.3077 | 0 | 1.2692 | 0 | 1.3077 | 1.2692 | 17.1979 | 20.7494 | 15.8903
38880.5984 | 1285 | 0 | 38880.5984 | 1928 | 0 | 350.5 | 432.5 | 78.4493 | 0 | 117.7045 | 0 | 0.78449 | 0 | 1.177 | 0 | 0.78449 | 1.177 | 95.3603 | 30.2064 | 94.5758
38880.5986 | 1571 | 1 | 38880.5986 | 2049 | 0 | 371.5 | 453.5 | 95.9096 | 0.06105 | 125.0916 | 0 | 0.9591 | 0.0006105 | 1.2509 | 0 | 0.95849 | 1.2509 | 60.0028 | 22.5173 | 17246.3836
38880.5989 | 1503 | 0 | 38880.5989 | 2424 | 0 | 392.5 | 474.5 | 91.7582 | 0 | 147.9853 | 0 | 0.91758 | 0 | 1.4799 | 0 | 0.91758 | 1.4799 | 67.0246 | 3.5635 | 66.107
38880.5991 | 1704 | 0 | 38880.5991 | 2444 | 0 | 413.5 | 495.5 | 104.0293 | 0 | 149.2063 | 0 | 1.0403 | 0 | 1.4921 | 0 | 1.0403 | 1.4921 | 47.3228 | 2.716 | 46.2825
38880.5993 | 1894 | 0 | 38880.5994 | 2039 | 0 | 434.5 | 516.5 | 115.6288 | 0 | 124.4811 | 0 | 1.1563 | 0 | 1.2448 | 0 | 1.1563 | 1.2448 | 32.5438 | 23.1182 | 31.3875
38880.5996 | 1431 | 0 | 38880.5996 | 1962 | 0 | 455.5 | 537.5 | 87.3626 | 0 | 119.7802 | 0 | 0.87363 | 0 | 1.1978 | 0 | 0.87363 | 1.1978 | 75.4284 | 27.9501 | 74.5547
38880.5998 | 1716 | 0 | 38880.5998 | 2344 | 0 | 476.5 | 558.5 | 104.7619 | 0 | 143.1013 | 0 | 1.0476 | 0 | 1.431 | 0 | 1.0476 | 1.431 | 46.2925 | 7.0981 | 45.2449
38880.6001 | 496 | 0 | 38880.6001 | 1985 | 2 | 497.5 | 579.5 | 30.2808 | 0 | 121.1844 | 0.1221 | 0.30281 | 0 | 1.2118 | 0.001221 | 0.30281 | 1.2106 | 406.125 | 26.5951 | 405.8222

## C3-4
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 157.3492 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38880.5935 | 1 | 0 | 38880.5935 | 1 | 0 | -70.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5937 | 1 | 0 | 38880.5938 | 1 | 0 | -49.5 | 32.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.594 | 1 | 0 | 38880.594 | 1 | 0 | -28.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -7.5 | 74.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 13.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5947 | 1 | 0 | 38880.5947 | 1 | 0 | 34.5 | 116.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5952 | 1 | 0 | 38880.5952 | 2 | 0 | 76.5 | 158.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 257638 | 128769 | 257637.9994
38880.5954 | 1 | 0 | 38880.5955 | 1 | 0 | 97.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5957 | 2 | 0 | 38880.5957 | 1 | 0 | 118.5 | 200.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128769 | 257638 | 128768.9988
38880.5959 | 1 | 0 | 38880.5959 | 1 | 0 | 139.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5962 | 1 | 0 | 38880.5962 | 1 | 0 | 160.5 | 242.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5964 | 1 | 0 | 38880.5964 | 1 | 0 | 181.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5967 | 1 | 0 | 38880.5967 | 1 | 0 | 202.5 | 284.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38880.5969 | 225 | 0 | 38880.5969 | 2470 | 0 | 223.5 | 305.5 | 13.7363 | 0 | 150.7937 | 0 | 0.13736 | 0 | 1.5079 | 0 | 0.13736 | 1.5079 | 1045.5022 | 4.3474 | 1045.3649
38880.5971 | 2418 | 0 | 38880.5972 | 2495 | 0 | 244.5 | 326.5 | 147.619 | 0 | 152.3199 | 0 | 1.4762 | 0 | 1.5232 | 0 | 1.4762 | 1.5232 | 6.5914 | 3.3018 | 5.1152
38880.5974 | 1654 | 0 | 38880.5974 | 2561 | 0 | 265.5 | 347.5 | 100.9768 | 0 | 156.3492 | 0 | 1.0098 | 0 | 1.5635 | 0 | 1.0098 | 1.5635 | 55.8271 | 0.63959 | 54.8173
38880.5976 | 1803 | 0 | 38880.5979 | 2124 | 0 | 297 | 379 | 110.0733 | 0 | 129.6703 | 0 | 1.1007 | 0 | 1.2967 | 0 | 1.1007 | 1.2967 | 42.9495 | 21.3456 | 41.8488
38880.5979 | 2070 | 0 | 38880.5981 | 2346 | 0 | 318 | 400 | 126.3736 | 0 | 143.2234 | 0 | 1.2637 | 0 | 1.4322 | 0 | 1.2637 | 1.4322 | 24.5111 | 9.8627 | 23.2474
38880.5981 | 1827 | 0 | 38880.5984 | 2294 | 0 | 339 | 421 | 111.5385 | 0 | 140.0488 | 0 | 1.1154 | 0 | 1.4005 | 0 | 1.1154 | 1.4005 | 41.0717 | 12.3531 | 39.9563
38880.5984 | 1754 | 0 | 38880.5986 | 2412 | 0 | 360 | 442 | 107.0818 | 0 | 147.2527 | 0 | 1.0708 | 0 | 1.4725 | 0 | 1.0708 | 1.4725 | 46.943 | 6.8566 | 45.8722
38880.5986 | 1578 | 0 | 38880.5989 | 2336 | 0 | 381 | 463 | 96.337 | 0 | 142.6129 | 0 | 0.96337 | 0 | 1.4261 | 0 | 0.96337 | 1.4261 | 63.3321 | 10.333 | 62.3687
38880.5988 | 1958 | 0 | 38880.5991 | 2105 | 0 | 402 | 484 | 119.536 | 0 | 128.5104 | 0 | 1.1954 | 0 | 1.2851 | 0 | 1.1954 | 1.2851 | 31.6333 | 22.4409 | 30.4379
38880.5991 | 1648 | 0 | 38880.5993 | 2012 | 0 | 423 | 505 | 100.6105 | 0 | 122.8327 | 0 | 1.0061 | 0 | 1.2283 | 0 | 1.0061 | 1.2283 | 56.3944 | 28.1004 | 55.3883
38880.5993 | 2276 | 0 | 38880.5996 | 2266 | 1 | 444 | 526 | 138.9499 | 0 | 138.3394 | 0.06105 | 1.3895 | 0 | 1.3834 | 0.0006105 | 1.3895 | 1.3828 | 13.2417 | 13.7916 | 11.8522
38880.5996 | 1720 | 1 | 38880.5998 | 1907 | 0 | 465 | 547 | 105.0061 | 0.06105 | 116.4225 | 0 | 1.0501 | 0.0006105 | 1.1642 | 0 | 1.0495 | 1.1642 | 49.9593 | 35.1536 | 22274.5588
38880.5998 | 2194 | 0 | 38880.6001 | 1822 | 0 | 486 | 568 | 133.9438 | 0 | 111.2332 | 0 | 1.3394 | 0 | 1.1123 | 0 | 1.3394 | 1.1123 | 17.474 | 41.4588 | 16.1346
38880.6001 | 935 | 397 | [5 empty] | 57.0818 | 24.2369 | 0 | 0 | 0.57082 | 0.24237 | 0 | 0 | 0.32845 | 0 | 305.2751 | #DIV/0! | #DIV/0!

## C2-7
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 151.1221 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38880.5935 | 1 | 1 | 38880.5935 | 1 | 0 | -71.5 | 10.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 612255638.44 | 247438 | 247238.0808
38880.5937 | 1 | 0 | 38880.5937 | 1 | 0 | -50.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.594 | 1 | 0 | 38880.594 | 1 | 0 | -29.5 | 52.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -8.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5945 | 1 | 0 | 38880.5945 | 1 | 0 | 12.5 | 94.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5947 | 1 | 0 | 38880.5947 | 1 | 0 | 33.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5952 | 1 | 0 | 38880.5952 | 1 | 0 | 75.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5954 | 1 | 0 | 38880.5954 | 1 | 0 | 96.5 | 178.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5957 | 1 | 0 | 38880.5957 | 1 | 0 | 117.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5959 | 1 | 1 | 38880.5959 | 1 | 0 | 138.5 | 220.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 612255638.44 | 247438 | 247238.0808
38880.5962 | 1 | 0 | 38880.5962 | 1 | 0 | 159.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5964 | 1 | 0 | 38880.5964 | 1 | 0 | 180.5 | 262.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5966 | 1 | 0 | 38880.5967 | 1 | 0 | 201.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38880.5969 | 466 | 225 | 38880.5969 | 312 | 24 | 222.5 | 304.5 | 28.4493 | 13.7363 | 19.0476 | 1.4652 | 0.28449 | 0.13736 | 0.19048 | 0.014652 | 0.14713 | 0.17582 | 950.9186 | 757.8147 | 700.6068
38880.5971 | 609 | 31 | 38880.5971 | 922 | 36 | 243.5 | 325.5 | 37.1795 | 1.8926 | 56.2882 | 2.1978 | 0.37179 | 0.018926 | 0.56288 | 0.021978 | 0.35287 | 0.5409 | 332.9644 | 177.491 | 3786.9689
38880.5974 | 2155 | 0 | 38880.5974 | 1983 | 0 | 264.5 | 346.5 | 131.5629 | 0 | 121.0623 | 0 | 1.3156 | 0 | 1.2106 | 0 | 1.3156 | 1.2106 | 14.8668 | 24.8301 | 13.5512
38880.5976 | 2204 | 0 | 38880.5976 | 1857 | 0 | 285.5 | 367.5 | 134.5543 | 0 | 113.37 | 0 | 1.3455 | 0 | 1.1337 | 0 | 1.3455 | 1.1337 | 12.3131 | 33.2999 | 10.9675
38880.5979 | 2041 | 0 | 38880.5979 | 2396 | 0 | 306.5 | 388.5 | 124.6032 | 0 | 146.2759 | 0 | 1.246 | 0 | 1.4628 | 0 | 1.246 | 1.4628 | 21.2827 | 3.313 | 20.0367
38880.5981 | 2459 | 0 | 38880.5981 | 2048 | 0 | 327.5 | 409.5 | 150.1221 | 0 | 125.0305 | 0 | 1.5012 | 0 | 1.2503 | 0 | 1.5012 | 1.2503 | 0.66612 | 20.8682 | 0.8351
38880.5983 | 2262 | 0 | 38880.5984 | 2413 | 0 | 348.5 | 430.5 | 138.0952 | 0 | 147.3138 | 0 | 1.381 | 0 | 1.4731 | 0 | 1.381 | 1.4731 | 9.4332 | 2.5852 | 8.0523
38880.5986 | 2184 | 0 | 38880.5986 | 2426 | 0 | 369.5 | 451.5 | 133.3333 | 0 | 148.1074 | 0 | 1.3333 | 0 | 1.4811 | 0 | 1.3333 | 1.4811 | 13.3416 | 2.0354 | 12.0082
38880.5988 | 2411 | 0 | 38880.5988 | 2135 | 0 | 390.5 | 472.5 | 147.1917 | 0 | 130.3419 | 0 | 1.4719 | 0 | 1.3034 | 0 | 1.4719 | 1.3034 | 2.6703 | 15.9429 | 1.1983
38880.5991 | 2177 | 0 | 38880.5991 | 2363 | 0 | 411.5 | 493.5 | 132.906 | 0 | 144.2613 | 0 | 1.3291 | 0 | 1.4426 | 0 | 1.3291 | 1.4426 | 13.706 | 4.7558 | 12.377
38880.5993 | 1990 | 0 | 38880.5993 | 2432 | 0 | 432.5 | 514.5 | 121.4896 | 0 | 148.4737 | 0 | 1.2149 | 0 | 1.4847 | 0 | 1.2149 | 1.4847 | 24.391 | 1.7837 | 23.1761
38880.5996 | 2279 | 0 | 38880.5996 | 2013 | 0 | 453.5 | 535.5 | 139.1331 | 0 | 122.8938 | 0 | 1.3913 | 0 | 1.2289 | 0 | 1.3913 | 1.2289 | 8.6169 | 22.9697 | 7.2256
38880.5998 | 2418 | 0 | 38880.5998 | 2134 | 0 | 474.5 | 556.5 | 147.619 | 0 | 130.2808 | 0 | 1.4762 | 0 | 1.3028 | 0 | 1.4762 | 1.3028 | 2.373 | 15.9972 | 0.89685
38880.6 | 2298 | 0 | 38880.6001 | 2125 | 0 | 495.5 | 577.5 | 140.293 | 0 | 129.7314 | 0 | 1.4029 | 0 | 1.2973 | 0 | 1.4029 | 1.2973 | 7.7189 | 16.4885 | 6.316

## C2-6
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 155.7619 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38880.5935 | 1 | 0 | 38880.5935 | 1 | 0 | -72.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5937 | 1 | 0 | 38880.5937 | 1 | 0 | -51.5 | 30.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.594 | 1 | 0 | 38880.594 | 1 | 0 | -30.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -9.5 | 72.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5944 | 1 | 0 | 38880.5945 | 1 | 0 | 11.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5947 | 1 | 0 | 38880.5947 | 1 | 0 | 32.5 | 114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5952 | 1 | 0 | 38880.5952 | 1 | 0 | 74.5 | 156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5954 | 1 | 0 | 38880.5954 | 1 | 0 | 95.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5957 | 1 | 0 | 38880.5957 | 1 | 0 | 116.5 | 198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5959 | 1 | 0 | 38880.5959 | 1 | 0 | 137.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5961 | 1 | 0 | 38880.5962 | 1 | 0 | 158.5 | 240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5964 | 1 | 0 | 38880.5964 | 1 | 0 | 179.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38880.5966 | 1 | 0 | 38880.5966 | 2 | 0 | 200.5 | 282.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255038 | 127469 | 255037.9994
38880.5969 | 68 | 0 | 38880.5969 | 105 | 0 | 221.5 | 303.5 | 4.1514 | 0 | 6.4103 | 0 | 0.041514 | 0 | 0.064103 | 0 | 0.041514 | 0.064103 | 3652.0294 | 2329.8857 | 3651.9879
38880.5971 | 879 | 0 | 38880.5971 | 1901 | 0 | 242.5 | 324.5 | 53.663 | 0 | 116.0562 | 0 | 0.53663 | 0 | 1.1606 | 0 | 0.53663 | 1.1606 | 190.2594 | 34.2125 | 189.7228
38880.5974 | 2486 | 0 | 38880.5974 | 2311 | 0 | 263.5 | 345.5 | 151.7705 | 0 | 141.0867 | 0 | 1.5177 | 0 | 1.4109 | 0 | 1.5177 | 1.4109 | 2.6299 | 10.4016 | 1.1122
38880.5976 | 2454 | 0 | 38880.5976 | 2487 | 0 | 284.5 | 366.5 | 149.8168 | 0 | 151.8315 | 0 | 1.4982 | 0 | 1.5183 | 0 | 1.4982 | 1.5183 | 3.9682 | 2.5887 | 2.47
38880.5978 | 2165 | 0 | 38880.5979 | 2162 | 0 | 305.5 | 387.5 | 132.1734 | 0 | 131.9902 | 0 | 1.3217 | 0 | 1.3199 | 0 | 1.3217 | 1.3199 | 17.8467 | 18.0102 | 16.5249
38880.5981 | 2343 | 0 | 38880.5981 | 2437 | 0 | 326.5 | 408.5 | 143.0403 | 0 | 148.779 | 0 | 1.4304 | 0 | 1.4878 | 0 | 1.4304 | 1.4878 | 8.8937 | 4.6935 | 7.4633
38880.5983 | 2234 | 0 | 38880.5983 | 1973 | 0 | 347.5 | 429.5 | 136.3858 | 0 | 120.4518 | 0 | 1.3639 | 0 | 1.2045 | 0 | 1.3639 | 1.2045 | 14.2068 | 29.3147 | 12.8429
38880.5986 | 2535 | 0 | 38880.5986 | 2207 | 0 | 368.5 | 450.5 | 154.7619 | 0 | 134.7375 | 0 | 1.5476 | 0 | 1.3474 | 0 | 1.5476 | 1.3474 | 0.64615 | 15.604 | 0.90147
38880.5988 | 2147 | 0 | 38880.5988 | 1890 | 0 | 389.5 | 471.5 | 131.0745 | 0 | 115.3846 | 0 | 1.3107 | 0 | 1.1538 | 0 | 1.3107 | 1.1538 | 18.8347 | 34.9937 | 17.5239
38880.5991 | 2518 | 0 | 38880.5991 | 2282 | 0 | 410.5 | 492.5 | 153.7241 | 0 | 139.3162 | 0 | 1.5372 | 0 | 1.3932 | 0 | 1.5372 | 1.3932 | 1.3257 | 11.8046 | 0.21159
38880.5993 | 2391 | 0 | 38880.5993 | 2043 | 0 | 431.5 | 513.5 | 145.9707 | 0 | 124.7253 | 0 | 1.4597 | 0 | 1.2473 | 0 | 1.4597 | 1.2473 | 6.7077 | 24.884 | 5.2479
38880.5995 | 2298 | 0 | 38880.5996 | 1755 | 0 | 452.5 | 534.5 | 140.293 | 0 | 107.1429 | 0 | 1.4029 | 0 | 1.0714 | 0 | 1.4029 | 1.0714 | 11.0261 | 45.3778 | 9.6232
38880.5998 | 1975 | 0 | 38880.5998 | 2190 | 0 | 473.5 | 555.5 | 120.5739 | 0 | 133.6996 | 0 | 1.2057 | 0 | 1.337 | 0 | 1.2057 | 1.337 | 29.1838 | 16.5014 | 27.9781
38880.6 | 2049 | 0 | 38880.6 | 1972 | 0 | 494.5 | 576.5 | 125.0916 | 0 | 120.3907 | 0 | 1.2509 | 0 | 1.2039 | 0 | 1.2509 | 1.2039 | 24.5183 | 29.3803 | 23.2674

## C2-5
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 156.4335 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38880.5935 | 1 | 0 | 38880.5935 | 1 | 0 | -73.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5937 | 1 | 1 | 38880.5937 | 1 | 0 | -52.5 | 29.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38880.5939 | 1 | 0 | 38880.594 | 1 | 0 | -31.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -10.5 | 71.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 10.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5947 | 1 | 0 | 38880.5947 | 1 | 0 | 31.5 | 113.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5952 | 1 | 0 | 38880.5952 | 1 | 0 | 73.5 | 155.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5954 | 1 | 0 | 38880.5954 | 1 | 0 | 94.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5956 | 1 | 0 | 38880.5957 | 1 | 0 | 115.5 | 197.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5959 | 1 | 1 | 38880.5959 | 1 | 0 | 136.5 | 218.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38880.5961 | 2 | 0 | 38880.5961 | 1 | 0 | 157.5 | 239.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128019 | 256138 | 128018.9988
38880.5964 | 1 | 0 | 38880.5964 | 2 | 0 | 178.5 | 260.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 256138 | 128019 | 256137.9994
38880.5966 | 1 | 0 | 38880.5966 | 1 | 0 | 199.5 | 281.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38880.5969 | 152 | 0 | 38880.5969 | 203 | 0 | 220.5 | 302.5 | 9.2796 | 0 | 12.3932 | 0 | 0.092796 | 0 | 0.12393 | 0 | 0.092796 | 0.12393 | 1585.7763 | 1162.2562 | 1585.6835
38880.5971 | 505 | 0 | 38880.5971 | 1999 | 0 | 241.5 | 323.5 | 30.8303 | 0 | 122.0391 | 0 | 0.3083 | 0 | 1.2204 | 0 | 0.3083 | 1.2204 | 407.402 | 28.1831 | 407.0937
38880.5973 | 2001 | 0 | 38880.5974 | 2499 | 0 | 262.5 | 344.5 | 122.1612 | 0 | 152.5641 | 0 | 1.2216 | 0 | 1.5256 | 0 | 1.2216 | 1.5256 | 28.055 | 2.5362 | 26.8334
38880.5976 | 2061 | 0 | 38880.5976 | 2041 | 0 | 283.5 | 365.5 | 125.8242 | 0 | 124.6032 | 0 | 1.2582 | 0 | 1.246 | 0 | 1.2582 | 1.246 | 24.327 | 25.5453 | 23.0688
38880.5978 | 2500 | 0 | 38880.5978 | 2311 | 0 | 304.5 | 386.5 | 152.6252 | 0 | 141.0867 | 0 | 1.5263 | 0 | 1.4109 | 0 | 1.5263 | 1.4109 | 2.4952 | 10.8775 | 0.96895
38880.5981 | 1993 | 0 | 38880.5981 | 2519 | 0 | 325.5 | 407.5 | 121.6728 | 0 | 153.7851 | 0 | 1.2167 | 0 | 1.5379 | 0 | 1.2167 | 1.5379 | 28.569 | 1.7221 | 27.3523
38880.5983 | 2445 | 0 |  | 2225 | 0 | 346 | 428 | 149.2674 | 0 | 135.8364 | 0 | 1.4927 | 0 | 1.3584 | 0 | 1.4927 | 1.3584 | 4.8008 | 15.1631 | 3.3081
38880.5986 | 2506 | 0 | 38880.5986 | 1931 | 0 | 367.5 | 449.5 | 152.9915 | 0 | 117.8877 | 0 | 1.5299 | 0 | 1.1789 | 0 | 1.5299 | 1.1789 | 2.2498 | 32.697 | 0.71989
38880.5988 | 2546 | 0 | 38880.5988 | 2326 | 0 | 388.5 | 470.5 | 155.4335 | 0 | 142.0024 | 0 | 1.5543 | 0 | 1.42 | 0 | 1.5543 | 1.42 | 0.64336 | 10.1625 | 0.91097
38880.5991 | 2197 | 0 | 38880.5991 | 2290 | 0 | 409.5 | 491.5 | 134.127 | 0 | 139.8046 | 0 | 1.3413 | 0 | 1.398 | 0 | 1.3413 | 1.398 | 16.6309 | 11.8943 | 15.2896
38880.5993 | 2013 | 0 | 38880.5993 | 2393 | 0 | 430.5 | 512.5 | 122.8938 | 0 | 146.0928 | 0 | 1.2289 | 0 | 1.4609 | 0 | 1.2289 | 1.4609 | 27.2916 | 7.0781 | 26.0627
38880.5995 | 2531 | 0 | 38880.5995 | 2269 | 0 | 451.5 | 533.5 | 154.5177 | 0 | 138.5226 | 0 | 1.5452 | 0 | 1.3852 | 0 | 1.5452 | 1.3852 | 1.2398 | 12.9299 | 0.30535
38880.5998 | 2323 | 0 | 38880.5998 | 1877 | 0 | 472.5 | 554.5 | 141.8193 | 0 | 114.591 | 0 | 1.4182 | 0 | 1.1459 | 0 | 1.4182 | 1.1459 | 10.3048 | 36.5147 | 8.8866
38880.6 | 2240 | 0 | 38880.6 | 2122 | 0 | 493.5 | 575.5 | 136.7521 | 0 | 129.5482 | 0 | 1.3675 | 0 | 1.2955 | 0 | 1.3675 | 1.2955 | 14.392 | 20.7531 | 13.0244

## C2-4
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 156.9829 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38880.5934 | 1 | 0 | 38880.5935 | 1 | 0 | -74.5 | 7.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5937 | 1 | 0 | 38880.5937 | 1 | 0 | -53.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5939 | 1 | 0 | 38880.5939 | 1 | 0 | -32.5 | 49.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -11.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 9.5 | 91.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5947 | 1 | 0 | 38880.5947 | 1 | 0 | 30.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5952 | 1 | 0 | 38880.5952 | 1 | 0 | 72.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5954 | 1 | 0 | 38880.5954 | 1 | 0 | 93.5 | 175.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5956 | 1 | 0 | 38880.5956 | 1 | 0 | 114.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5959 | 1 | 0 | 38880.5959 | 1 | 0 | 135.5 | 217.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5961 | 1 | 0 | 38880.5961 | 1 | 0 | 156.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5964 | 1 | 0 | 38880.5964 | 1 | 0 | 177.5 | 259.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5966 | 1 | 0 | 38880.5966 | 1 | 0 | 198.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38880.5969 | 114 | 0 | 38880.5969 | 2461 | 0 | 219.5 | 301.5 | 6.9597 | 0 | 150.2442 | 0 | 0.069597 | 0 | 1.5024 | 0 | 0.069597 | 1.5024 | 2155.5965 | 4.4852 | 2155.5269
38880.5971 | 517 | 0 | 38880.5971 | 2507 | 1 | 240.5 | 322.5 | 31.5629 | 0 | 153.0525 | 0.06105 | 0.31563 | 0 | 1.5305 | 0.0006105 | 0.31563 | 1.5299 | 397.3656 | 2.6089 | 397.0499
38880.5973 | 2238 | 0 | 38880.5973 | 2148 | 0 | 261.5 | 343.5 | 136.63 | 0 | 131.1355 | 0 | 1.3663 | 0 | 1.3114 | 0 | 1.3663 | 1.3114 | 14.8963 | 19.7104 | 13.53
38880.5976 | 2414 | 0 | 38880.5976 | 2159 | 0 | 282.5 | 364.5 | 147.3748 | 0 | 131.8071 | 0 | 1.4737 | 0 | 1.3181 | 0 | 1.4737 | 1.3181 | 6.5195 | 19.1005 | 5.0457
38880.5978 | 2286 | 0 | 38880.5978 | 1995 | 0 | 303.5 | 385.5 | 139.5604 | 0 | 121.7949 | 0 | 1.3956 | 0 | 1.2179 | 0 | 1.3956 | 1.2179 | 12.4838 | 28.8912 | 11.0882
38880.5981 | 2202 | 0 | 38880.5981 | 2133 | 0 | 324.5 | 406.5 | 134.4322 | 0 | 130.2198 | 0 | 1.3443 | 0 | 1.3022 | 0 | 1.3443 | 1.3022 | 16.7748 | 20.5523 | 15.4304
38880.5983 | 2538 | 0 | 38880.5983 | 2512 | 0 | 345.5 | 427.5 | 154.9451 | 0 | 153.3578 | 0 | 1.5495 | 0 | 1.5336 | 0 | 1.5495 | 1.5336 | 1.3152 | 2.3639 | 0.23424
38880.5986 | 2469 | 0 | 38880.5986 | 1933 | 0 | 366.5 | 448.5 | 150.7326 | 0 | 118.0098 | 0 | 1.5073 | 0 | 1.1801 | 0 | 1.5073 | 1.1801 | 4.1466 | 33.0253 | 2.6393
38880.5988 | 2135 | 0 | 38880.5988 | 2477 | 0 | 387.5 | 469.5 | 130.3419 | 0 | 151.221 | 0 | 1.3034 | 0 | 1.5122 | 0 | 1.3034 | 1.5122 | 20.4393 | 3.8103 | 19.1359
38880.599 | 2555 | 0 | 38880.5991 | 2257 | 0 | 408.5 | 490.5 | 155.9829 | 0 | 137.79 | 0 | 1.5598 | 0 | 1.3779 | 0 | 1.5598 | 1.3779 | 0.6411 | 13.9291 | 0.91873
38880.5993 | 2255 | 0 | 38880.5993 | 2127 | 0 | 429.5 | 511.5 | 137.6679 | 0 | 129.8535 | 0 | 1.3767 | 0 | 1.2985 | 0 | 1.3767 | 1.2985 | 14.0302 | 20.8923 | 12.6535
38880.5995 | 2277 | 0 | 38880.5995 | 1932 | 0 | 450.5 | 532.5 | 139.011 | 0 | 117.9487 | 0 | 1.3901 | 0 | 1.1795 | 0 | 1.3901 | 1.1795 | 12.9284 | 33.0942 | 11.5383
38880.5998 | 2009 | 0 | 38880.5998 | 2341 | 0 | 471.5 | 553.5 | 122.6496 | 0 | 142.9182 | 0 | 1.2265 | 0 | 1.4292 | 0 | 1.2265 | 1.4292 | 27.993 | 9.8411 | 26.7665
38880.6 | 2521 | 0 | 38880.6 | 2045 | 0 | 492.5 | 574.5 | 153.9072 | 0 | 124.8474 | 0 | 1.5391 | 0 | 1.2485 | 0 | 1.5391 | 1.2485 | 1.9984 | 25.7399 | 0.45934

## C2-3
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 157.2271 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38880.5934 | 1 | 0 | 38880.5934 | 1 | 0 | -75.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5937 | 1 | 0 | 38880.5937 | 1 | 0 | -54.5 | 27.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5939 | 1 | 0 | 38880.5939 | 1 | 0 | -33.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -12.5 | 69.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 8.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5947 | 2 | 0 | 38880.5947 | 1 | 1 | 29.5 | 111.5 | 0.1221 | 0 | 0.06105 | 0.06105 | 0.001221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 128669 | 257438 | 128668.9988
38880.5951 | 1 | 0 | 38880.5952 | 1 | 0 | 71.5 | 153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5954 | 1 | 0 | 38880.5954 | 1 | 0 | 92.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5956 | 1 | 0 | 38880.5956 | 1 | 0 | 113.5 | 195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5959 | 1 | 0 | 38880.5959 | 1 | 0 | 134.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5961 | 1 | 0 | 38880.5961 | 1 | 0 | 155.5 | 237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5964 | 1 | 0 | 38880.5964 | 1 | 0 | 176.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5966 | 1 | 0 | 38880.5966 | 1 | 0 | 197.5 | 279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38880.5968 | 170 | 5 | 38880.5969 | 205 | 24 | 218.5 | 300.5 | 10.3785 | 0.30525 | 12.5153 | 1.4652 | 0.10379 | 0.0030525 | 0.12515 | 0.014652 | 0.10073 | 0.1105 | 1461.1564 | 1321.5954 | 44630.5772
38880.5971 | 468 | 1 | 38880.5971 | 2039 | 0 | 239.5 | 321.5 | 28.5714 | 0.06105 | 124.4811 | 0 | 0.28571 | 0.0006105 | 1.2448 | 0 | 0.2851 | 1.2448 | 454.9625 | 26.306 | 43870.0349
38880.5973 | 2291 | 0 | 38880.5973 | 1950 | 0 | 260.5 | 342.5 | 139.8657 | 0 | 119.0476 | 0 | 1.3987 | 0 | 1.1905 | 0 | 1.3987 | 1.1905 | 12.4129 | 32.0708 | 11.0143
38880.5976 | 2134 | 0 | 38880.5976 | 1341 | 0 | 281.5 | 363.5 | 130.2808 | 0 | 81.8681 | 0 | 1.3028 | 0 | 0.81868 | 0 | 1.3028 | 0.81868 | 20.6832 | 92.0492 | 19.3804
38880.5978 | 2330 | 1 | 38880.5978 | 2380 | 0 | 302.5 | 384.5 | 142.2466 | 0.06105 | 145.2991 | 0 | 1.4225 | 0.0006105 | 1.453 | 0 | 1.4219 | 1.453 | 10.5912 | 8.2092 | 1853.9774
38880.5981 | 2427 | 0 | 38880.5981 | 2136 | 0 | 323.5 | 405.5 | 148.1685 | 0 | 130.4029 | 0 | 1.4817 | 0 | 1.304 | 0 | 1.4817 | 1.304 | 6.1137 | 20.5702 | 4.632
38880.5983 | 2089 | 0 | 38880.5983 | 1637 | 0 | 344.5 | 426.5 | 127.5336 | 0 | 99.9389 | 0 | 1.2753 | 0 | 0.99939 | 0 | 1.2753 | 0.99939 | 23.2829 | 57.3232 | 22.0076
38880.5985 | 1979 | 0 | 38880.5986 | 1586 | 0 | 365.5 | 447.5 | 120.8181 | 0 | 96.8254 | 0 | 1.2082 | 0 | 0.96825 | 0 | 1.2082 | 0.96825 | 30.1354 | 62.3821 | 28.9272
38880.5988 | 2358 | 0 | 38880.5988 | 2288 | 0 | 386.5 | 468.5 | 143.956 | 0 | 139.6825 | 0 | 1.4396 | 0 | 1.3968 | 0 | 1.4396 | 1.3968 | 9.2188 | 12.5603 | 7.7793
38880.599 | 2256 | 0 | 38880.599 | 1328 | 0 | 407.5 | 489.5 | 137.7289 | 0 | 81.0745 | 0 | 1.3773 | 0 | 0.81074 | 0 | 1.3773 | 0.81074 | 14.1569 | 93.9292 | 12.7796
38880.5993 | 2559 | 0 | 38880.5993 | 2191 | 0 | 428.5 | 510.5 | 156.2271 | 0 | 133.7607 | 0 | 1.5623 | 0 | 1.3376 | 0 | 1.5623 | 1.3376 | 0.64009 | 17.5436 | 0.92218
38880.5995 | 2023 | 0 | 38880.5995 | 2118 | 0 | 449.5 | 531.5 | 123.5043 | 0 | 129.304 | 0 | 1.235 | 0 | 1.293 | 0 | 1.235 | 1.293 | 27.305 | 21.5949 | 26.0699
38880.5998 | 2023 | 0 | 38880.5998 | 1720 | 0 | 470.5 | 552.5 | 123.5043 | 0 | 105.0061 | 0 | 1.235 | 0 | 1.0501 | 0 | 1.235 | 1.0501 | 27.305 | 49.7314 | 26.0699
38880.6 | 2340 | 0 | 38880.6 | 2213 | 0 | 491.5 | 573.5 | 142.8571 | 0 | 135.1038 | 0 | 1.4286 | 0 | 1.351 | 0 | 1.4286 | 1.351 | 10.059 | 16.3751 | 8.6304

## C1-7
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 149.9621 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38880.5934 | 1 | 0 | 38880.5934 | 1 | 1 | -76.5 | 5.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 245538 | #DIV/0! | 245537.9994
38880.5937 | 1 | 0 | 38880.5937 | 1 | 0 | -55.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5939 | 1 | 1 | 38880.5939 | 1 | 0 | -34.5 | 47.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 602889094.44 | 245538 | 245338.0814
38880.5942 | 1 | 0 | 38880.5942 | 1 | 0 | -13.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 7.5 | 89.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5946 | 1 | 0 | 38880.5947 | 1 | 0 | 28.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5951 | 1 | 0 | 38880.5951 | 1 | 0 | 70.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5954 | 1 | 0 | 38880.5954 | 1 | 0 | 91.5 | 173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5956 | 1 | 0 | 38880.5956 | 1 | 0 | 112.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5959 | 1 | 0 | 38880.5959 | 1 | 0 | 133.5 | 215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5961 | 1 | 0 | 38880.5961 | 1 | 0 | 154.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5963 | 1 | 0 | 38880.5964 | 1 | 0 | 175.5 | 257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5966 | 1 | 0 | 38880.5966 | 1 | 0 | 196.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38880.5968 | 1 | 1 | 38880.5968 | 14 | 0 | 217.5 | 299.5 | 0.06105 | 0.06105 | 0.8547 | 0 | 0.0006105 | 0.0006105 | 0.008547 | 0 | 0 | 0.008547 | 42835507.1743 | 17445.5714 | 244039.1399
38880.5971 | 1014 | 570 | 38880.5971 | 863 | 234 | 238.5 | 320.5 | 61.9048 | 34.7985 | 52.6862 | 14.2857 | 0.61905 | 0.34799 | 0.52686 | 0.14286 | 0.27106 | 0.384 | 620.4325 | 269.4778 | 111.626
38880.5973 | 1962 | 0 | 38880.5973 | 2279 | 0 | 259.5 | 341.5 | 119.7802 | 0 | 139.1331 | 0 | 1.1978 | 0 | 1.3913 | 0 | 1.1978 | 1.3913 | 25.1978 | 7.7832 | 24
38880.5976 | 2159 | 0 | 38880.5976 | 2126 | 0 | 280.5 | 362.5 | 131.8071 | 0 | 129.7924 | 0 | 1.3181 | 0 | 1.2979 | 0 | 1.3181 | 1.2979 | 13.774 | 15.54 | 12.4559
38880.5978 | 2013 | 2 | 38880.5978 | 1708 | 4 | 301.5 | 383.5 | 122.8938 | 0.1221 | 104.2735 | 0.2442 | 1.2289 | 0.001221 | 1.0427 | 0.002442 | 1.2277 | 1.0403 | 22.0972 | 44.3906 | 6784.762
38880.598 | 2169 | 0 | 38880.5981 | 2329 | 0 | 322.5 | 404.5 | 132.4176 | 0 | 142.1856 | 0 | 1.3242 | 0 | 1.4219 | 0 | 1.3242 | 1.4219 | 13.2494 | 5.4693 | 11.9252
38880.5983 | 2440 | 0 | 38880.5983 | 2334 | 0 | 343.5 | 425.5 | 148.9621 | 0 | 142.4908 | 0 | 1.4896 | 0 | 1.4249 | 0 | 1.4896 | 1.4249 | 0.67131 | 5.2434 | 0.81831
38880.5985 | 1776 | 0 | 38880.5985 | 2020 | 0 | 364.5 | 446.5 | 108.4249 | 0 | 123.3211 | 0 | 1.0842 | 0 | 1.2332 | 0 | 1.0842 | 1.2332 | 38.3097 | 21.603 | 37.2254
38880.5988 | 2168 | 0 | 38880.5988 | 2028 | 0 | 385.5 | 467.5 | 132.3565 | 0 | 123.8095 | 0 | 1.3236 | 0 | 1.2381 | 0 | 1.3236 | 1.2381 | 13.3017 | 21.1233 | 11.9781
38880.599 | 2436 | 0 |  | 1969 | 0 | 406 | 488 | 148.7179 | 0 | 120.2076 | 0 | 1.4872 | 0 | 1.2021 | 0 | 1.4872 | 1.2021 | 0.83662 | 24.7527 | 0.65056
38880.5993 | 2177 | 0 | 38880.5993 | 1909 | 0 | 427.5 | 509.5 | 132.906 | 0 | 116.5446 | 0 | 1.3291 | 0 | 1.1654 | 0 | 1.3291 | 1.1654 | 12.8333 | 28.6737 | 11.5042
38880.5995 | 2117 | 0 | 38880.5995 | 2085 | 0 | 448.5 | 530.5 | 129.243 | 0 | 127.2894 | 0 | 1.2924 | 0 | 1.2729 | 0 | 1.2924 | 1.2729 | 16.0312 | 17.812 | 14.7387
38880.5997 | 1506 | 1 | 38880.5998 | 2050 | 0 | 469.5 | 551.5 | 91.9414 | 0.06105 | 125.1526 | 0 | 0.91941 | 0.0006105 | 1.2515 | 0 | 0.9188 | 1.2515 | 63.3605 | 19.8234 | 15706.4072
38880.6 | 1484 | 0 | 38880.6 | 2367 | 0 | 490.5 | 572.5 | 90.5983 | 0 | 144.5055 | 0 | 0.90598 | 0 | 1.4451 | 0 | 0.90598 | 1.4451 | 65.5243 | 3.7761 | 64.6183

## C1-6
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 154.0525 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38880.5934 | 1 | 0 | 38880.5934 | 1 | 0 | -77.5 | 4.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5937 | 1 | 0 | 38880.5937 | 1 | 1 | -56.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 252238 | 252238 | 252237.9994
38880.5939 | 1 | 0 | 38880.5939 | 1 | 0 | -35.5 | 46.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5941 | 1 | 0 | 38880.5942 | 1 | 0 | -14.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 6.5 | 88.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5946 | 1 | 0 | 38880.5946 | 1 | 0 | 27.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5951 | 1 | 0 | 38880.5951 | 1 | 0 | 69.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5954 | 1 | 0 | 38880.5954 | 1 | 0 | 90.5 | 172.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5956 | 2 | 0 | 38880.5956 | 1 | 0 | 111.5 | 193.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126069 | 252238 | 126068.9988
38880.5958 | 1 | 0 | 38880.5959 | 1 | 0 | 132.5 | 214.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5961 | 1 | 0 | 38880.5961 | 1 | 0 | 153.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5963 | 1 | 0 | 38880.5963 | 2 | 0 | 174.5 | 256.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252238 | 126069 | 252237.9994
38880.5966 | 2 | 0 | 38880.5966 | 1 | 0 | 195.5 | 277.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126069 | 252238 | 126068.9988
38880.5968 | 1 | 0 | 38880.5968 | 1 | 0 | 216.5 | 298.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38880.5971 | 619 | 0 | 38880.5971 | 2094 | 0 | 237.5 | 319.5 | 37.79 | 0 | 127.8388 | 0 | 0.3779 | 0 | 1.2784 | 0 | 0.3779 | 1.2784 | 307.6543 | 20.5053 | 307.2764
38880.5973 | 2507 | 0 | 38880.5973 | 2076 | 0 | 258.5 | 340.5 | 153.0525 | 0 | 126.7399 | 0 | 1.5305 | 0 | 1.2674 | 0 | 1.5305 | 1.2674 | 0.65337 | 21.5501 | 0.87715
38880.5975 | 2044 | 0 | 38880.5976 | 2375 | 0 | 279.5 | 361.5 | 124.7863 | 0 | 144.9939 | 0 | 1.2479 | 0 | 1.4499 | 0 | 1.2479 | 1.4499 | 23.453 | 6.2476 | 22.2052
38880.5978 | 2053 | 201 | 38880.5978 | 1981 | 172 | 300.5 | 382.5 | 125.3358 | 12.2711 | 120.9402 | 10.5006 | 1.2534 | 0.12271 | 1.2094 | 0.10501 | 1.1306 | 1.1044 | 34.4141 | 41.4282 | 39.2581
38880.598 | 2225 | 96 | 38880.598 | 2268 | 8 | 321.5 | 403.5 | 135.8364 | 5.8608 | 138.4615 | 0.4884 | 1.3584 | 0.058608 | 1.3846 | 0.004884 | 1.2998 | 1.3797 | 23.086 | 11.476 | 21.7022
38880.5983 | 2176 | 2 | 38880.5983 | 1921 | 2 | 342.5 | 424.5 | 132.8449 | 0.1221 | 117.2772 | 0.1221 | 1.3284 | 0.001221 | 1.1728 | 0.001221 | 1.3272 | 1.1716 | 16.0255 | 31.5958 | 4146.2397
38880.5985 | 2288 | 92 | 38880.5985 | 1944 | 71 | 363.5 | 445.5 | 139.6825 | 5.6166 | 118.6813 | 4.3346 | 1.3968 | 0.056166 | 1.1868 | 0.043346 | 1.3407 | 1.1435 | 11.8038 | 45.5666 | 48.785
38880.5988 | 1976 | 0 | 38880.5988 | 2438 | 0 | 384.5 | 466.5 | 120.6349 | 0 | 148.84 | 0 | 1.2063 | 0 | 1.4884 | 0 | 1.2063 | 1.4884 | 27.7014 | 3.5021 | 26.4951
38880.599 | 2012 | 0 | 38880.599 | 2257 | 0 | 405.5 | 487.5 | 122.8327 | 0 | 137.79 | 0 | 1.2283 | 0 | 1.3779 | 0 | 1.2283 | 1.3779 | 25.4165 | 11.8024 | 24.1882
38880.5992 | 2249 | 0 | 38880.5993 | 2067 | 0 | 426.5 | 508.5 | 137.3016 | 0 | 126.1905 | 0 | 1.373 | 0 | 1.2619 | 0 | 1.373 | 1.2619 | 12.2001 | 22.0793 | 10.8271
38880.5995 | 1782 | 0 | 38880.5995 | 1559 | 0 | 447.5 | 529.5 | 108.7912 | 0 | 95.177 | 0 | 1.0879 | 0 | 0.95177 | 0 | 1.0879 | 0.95177 | 41.6038 | 61.8589 | 40.5159
38880.5997 | 1495 | 0 | 38880.5997 | 1963 | 1 | 468.5 | 550.5 | 91.2698 | 0 | 119.8413 | 0.06105 | 0.9127 | 0 | 1.1984 | 0.0006105 | 0.9127 | 1.1978 | 68.788 | 28.6126 | 67.8753
38880.6 | 1379 | 1 | 38880.6 | 1751 | 0 | 489.5 | 571.5 | 84.188 | 0.06105 | 106.8987 | 0 | 0.84188 | 0.0006105 | 1.069 | 0 | 0.84127 | 1.069 | 83.1833 | 44.1108 | 34997.6557

## C1-5
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 152.6484 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38880.5934 | 1 | 0 | 38880.5934 | 1 | 1 | -78.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 249938 | 249938 | 249937.9994
38880.5936 | 1 | 1 | 38880.5937 | 2 | 0 | -57.5 | 24.5 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 312220050.22 | 124919 | 249638.16
38880.5939 | 1 | 0 | 38880.5939 | 1 | 1 | -36.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 249938 | 249938 | 249937.9994
38880.5941 | 1 | 0 | 38880.5941 | 1 | 0 | -15.5 | 66.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 5.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.5946 | 1 | 0 | 38880.5946 | 1 | 0 | 26.5 | 108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.5951 | 1 | 1 | 38880.5951 | 1 | 0 | 68.5 | 150.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 624690038.44 | 249938 | 249738.08
38880.5953 | 1 | 0 | 38880.5954 | 1 | 0 | 89.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.5956 | 2 | 0 | 38880.5956 | 2 | 0 | 110.5 | 192.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124919 | 124919 | 124918.9988
38880.5958 | 1 | 0 | 38880.5958 | 1 | 0 | 131.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.5961 | 1 | 0 | 38880.5961 | 1 | 0 | 152.5 | 234.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.5963 | 2 | 0 | 38880.5963 | 1 | 0 | 173.5 | 255.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124919 | 249938 | 124918.9988
38880.5966 | 1 | 0 | 38880.5966 | 1 | 0 | 194.5 | 276.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.5968 | 1 | 0 | 38880.5968 | 1 | 0 | 215.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38880.597 | 396 | 0 | 38880.5971 | 1927 | 0 | 236.5 | 318.5 | 24.1758 | 0 | 117.6435 | 0 | 0.24176 | 0 | 1.1764 | 0 | 0.24176 | 1.1764 | 531.4091 | 29.7551 | 531.1673
38880.5973 | 2096 | 0 | 38880.5973 | 2097 | 0 | 257.5 | 339.5 | 127.9609 | 0 | 128.022 | 0 | 1.2796 | 0 | 1.2802 | 0 | 1.2796 | 1.2802 | 19.2929 | 19.2361 | 18.0133
38880.5975 | 2326 | 0 | 38880.5975 | 2153 | 0 | 278.5 | 360.5 | 142.0024 | 0 | 131.4408 | 0 | 1.42 | 0 | 1.3144 | 0 | 1.42 | 1.3144 | 7.497 | 16.1347 | 6.077
38880.5978 | 2088 | 0 | 38880.5978 | 1966 | 0 | 299.5 | 381.5 | 127.4725 | 0 | 120.0244 | 0 | 1.2747 | 0 | 1.2002 | 0 | 1.2747 | 1.2002 | 19.75 | 27.1811 | 18.4753
38880.598 | 1350 | 0 | 38880.598 | 1963 | 0 | 320.5 | 402.5 | 82.4176 | 0 | 119.8413 | 0 | 0.82418 | 0 | 1.1984 | 0 | 0.82418 | 1.1984 | 85.2133 | 27.3754 | 84.3892
38880.5983 | 2299 | 0 | 38880.5983 | 2056 | 0 | 341.5 | 423.5 | 140.3541 | 0 | 125.5189 | 0 | 1.4035 | 0 | 1.2552 | 0 | 1.4035 | 1.2552 | 8.7595 | 21.6138 | 7.3559
38880.5985 | 2228 | 0 | 38880.5985 | 2484 | 0 | 362.5 | 444.5 | 136.0195 | 0 | 151.6484 | 0 | 1.3602 | 0 | 1.5165 | 0 | 1.3602 | 1.5165 | 12.2253 | 0.65942 | 10.8651
38880.5987 | 2320 | 0 | 38880.5988 | 2064 | 0 | 383.5 | 465.5 | 141.6361 | 0 | 126.0073 | 0 | 1.4164 | 0 | 1.2601 | 0 | 1.4164 | 1.2601 | 7.775 | 21.1424 | 6.3586
38880.599 | 2463 | 0 | 38880.599 | 2469 | 0 | 404.5 | 486.5 | 150.3663 | 0 | 150.7326 | 0 | 1.5037 | 0 | 1.5073 | 0 | 1.5037 | 1.5073 | 1.5177 | 1.271 | 0.013998
38880.5992 | 1954 | 1 | 38880.5992 | 2381 | 0 | 425.5 | 507.5 | 119.2918 | 0.06105 | 145.3602 | 0 | 1.1929 | 0.0006105 | 1.4536 | 0 | 1.1923 | 1.4536 | 28.2651 | 5.0139 | 2603.9028
38880.5995 | 2258 | 0 | 38880.5995 | 2087 | 0 | 446.5 | 528.5 | 137.851 | 0 | 127.4115 | 0 | 1.3785 | 0 | 1.2741 | 0 | 1.3785 | 1.2741 | 10.7343 | 19.8074 | 9.3558
38880.5997 | 1427 | 0 | 38880.5997 | 1884 | 0 | 467.5 | 549.5 | 87.1184 | 0 | 115.0183 | 0 | 0.87118 | 0 | 1.1502 | 0 | 0.87118 | 1.1502 | 75.2193 | 32.7166 | 74.3482
38880.6 | 921 | 340 | 38880.6 | 1661 | 4 | 488.5 | 570.5 | 56.2271 | 20.757 | 101.4042 | 0.2442 | 0.56227 | 0.20757 | 1.014 | 0.002442 | 0.3547 | 1.0116 | 1749.4533 | 69.2857 | 149.1932

## C1-4
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 154.8462 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38880.5934 | 1 | 0 | 38880.5934 | 1 | 0 | -79.5 | 2.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5936 | 1 | 0 | 38880.5936 | 1 | 0 | -58.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5939 | 1 | 0 | 38880.5939 | 1 | 0 | -37.5 | 44.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5941 | 1 | 0 | 38880.5941 | 1 | 0 | -16.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 4.5 | 86.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5946 | 1 | 0 | 38880.5946 | 2 | 0 | 25.5 | 107.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253538 | 126719 | 253537.9994
38880.5951 | 1 | 0 | 38880.5951 | 1 | 0 | 67.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5953 | 2 | 0 | 38880.5953 | 1 | 0 | 88.5 | 170.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126719 | 253538 | 126718.9988
38880.5956 | 2 | 0 | 38880.5956 | 2 | 0 | 109.5 | 191.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 126719 | 126719 | 126718.9988
38880.5958 | 1 | 0 | 38880.5958 | 1 | 0 | 130.5 | 212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5961 | 1 | 0 | 38880.5961 | 1 | 0 | 151.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5963 | 2 | 0 | 38880.5963 | 2 | 0 | 172.5 | 254.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 126719 | 126719 | 126718.9988
38880.5966 | 1 | 0 | 38880.5966 | 1 | 0 | 193.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38880.5968 | 2 | 0 | 38880.5968 | 1 | 0 | 214.5 | 296.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126719 | 253538 | 126718.9988
38880.597 | 26 | 0 | 38880.597 | 2483 | 0 | 235.5 | 317.5 | 1.5873 | 0 | 151.5873 | 0 | 0.015873 | 0 | 1.5159 | 0 | 0.015873 | 1.5159 | 9655.3077 | 2.1498 | 9655.2918
38880.5973 | 2334 | 0 | 38880.5973 | 2346 | 0 | 256.5 | 338.5 | 142.4908 | 0 | 143.2234 | 0 | 1.4249 | 0 | 1.4322 | 0 | 1.4249 | 1.4322 | 8.671 | 8.1151 | 7.246
38880.5975 | 2418 | 0 | 38880.5975 | 2520 | 0 | 277.5 | 359.5 | 147.619 | 0 | 153.8462 | 0 | 1.4762 | 0 | 1.5385 | 0 | 1.4762 | 1.5385 | 4.8958 | 0.65 | 3.4196
38880.5978 | 1868 | 0 | 38880.5978 | 1952 | 0 | 298.5 | 380.5 | 114.0415 | 0 | 119.1697 | 0 | 1.1404 | 0 | 1.1917 | 0 | 1.1404 | 1.1917 | 35.7805 | 29.9375 | 34.6401
38880.598 | 1884 | 0 | 38880.598 | 2159 | 0 | 319.5 | 401.5 | 115.0183 | 0 | 131.8071 | 0 | 1.1502 | 0 | 1.3181 | 0 | 1.1502 | 1.3181 | 34.6274 | 17.4794 | 33.4772
38880.5983 | 1951 | 0 | 38880.5983 | 2023 | 0 | 340.5 | 422.5 | 119.1087 | 0 | 123.5043 | 0 | 1.1911 | 0 | 1.235 | 0 | 1.1911 | 1.235 | 30.0041 | 25.3772 | 28.813
38880.5985 | 1885 | 0 | 38880.5985 | 2068 | 0 | 361.5 | 443.5 | 115.0794 | 0 | 126.2515 | 0 | 1.1508 | 0 | 1.2625 | 0 | 1.1508 | 1.2625 | 34.556 | 22.6489 | 33.4052
38880.5987 | 2363 | 0 | 38880.5987 | 1934 | 0 | 382.5 | 464.5 | 144.2613 | 0 | 118.0708 | 0 | 1.4426 | 0 | 1.1807 | 0 | 1.4426 | 1.1807 | 7.3373 | 31.1468 | 5.8947
38880.599 | 2102 | 0 | 38880.599 | 2021 | 0 | 403.5 | 485.5 | 128.3272 | 0 | 123.3822 | 0 | 1.2833 | 0 | 1.2338 | 0 | 1.2833 | 1.2338 | 20.6651 | 25.5012 | 19.3818
38880.5992 | 2331 | 0 | 38880.5992 | 2111 | 0 | 424.5 | 506.5 | 142.3077 | 0 | 128.8767 | 0 | 1.4231 | 0 | 1.2888 | 0 | 1.4231 | 1.2888 | 8.8108 | 20.1506 | 7.3877
38880.5995 | 1856 | 7 | 38880.5995 | 2148 | 2 | 445.5 | 527.5 | 113.3089 | 0.42735 | 131.1355 | 0.1221 | 1.1331 | 0.0042735 | 1.3114 | 0.001221 | 1.1288 | 1.3101 | 37.5814 | 18.1428 | 1477.2711
38880.5997 | 1851 | 4 | 38880.5997 | 2099 | 1 | 466.5 | 548.5 | 113.0037 | 0.2442 | 128.1441 | 0.06105 | 1.13 | 0.002442 | 1.2814 | 0.0006105 | 1.1276 | 1.2808 | 37.4968 | 20.874 | 2941.7266
38880.6 | 1432 | 366 | 38880.6 | 2122 | 1 | 487.5 | 569.5 | 87.4237 | 22.3443 | 129.5482 | 0.06105 | 0.87424 | 0.22344 | 1.2955 | 0.0006105 | 0.65079 | 1.2949 | 136.6784 | 141.868 | 118.3327

## C1-3
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 148.1306 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38880.5934 | 2 | 0 | 38880.5934 | 1 | 0 | -80.5 | 1.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121219 | 242538 | 121218.9988
38880.5936 | 1 | 0 | 38880.5936 | 1 | 0 | -59.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5939 | 1 | 0 | 38880.5939 | 1 | 0 | -38.5 | 43.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5941 | 1 | 0 | 38880.5941 | 1 | 0 | -17.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5944 | 1 | 0 | 38880.5944 | 1 | 0 | 3.5 | 85.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5946 | 1 | 0 | 38880.5946 | 1 | 0 | 24.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5951 | 1 | 0 | 38880.5951 | 1 | 0 | 66.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5953 | 1 | 0 | 38880.5953 | 1 | 0 | 87.5 | 169.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5956 | 2 | 0 | 38880.5956 | 2 | 0 | 108.5 | 190.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121219 | 121219 | 121218.9988
38880.5958 | 1 | 0 | 38880.5958 | 1 | 0 | 129.5 | 211.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5961 | 2 | 0 | 38880.5961 | 1 | 0 | 150.5 | 232.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121219 | 242538 | 121218.9988
38880.5963 | 1 | 0 | 38880.5963 | 1 | 0 | 171.5 | 253.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5965 | 1 | 0 | 38880.5966 | 1 | 0 | 192.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38880.5968 | 2 | 0 | 38880.5968 | 51 | 0 | 213.5 | 295.5 | 0.1221 | 0 | 3.1136 | 0 | 0.001221 | 0 | 0.031136 | 0 | 0.001221 | 0.031136 | 121219 | 4657.6078 | 121218.9988
38880.597 | 4 | 0 | 38880.597 | 1754 | 0 | 234.5 | 316.5 | 0.2442 | 0 | 107.0818 | 0 | 0.002442 | 0 | 1.0708 | 0 | 0.002442 | 1.0708 | 60559.5 | 38.3341 | 60559.4976
38880.5973 | 1956 | 0 | 38880.5973 | 1723 | 0 | 255.5 | 337.5 | 119.4139 | 0 | 105.1893 | 0 | 1.1941 | 0 | 1.0519 | 0 | 1.1941 | 1.0519 | 24.0481 | 40.823 | 22.8539
38880.5975 | 2169 | 0 | 38880.5975 | 1622 | 0 | 276.5 | 358.5 | 132.4176 | 0 | 99.0232 | 0 | 1.3242 | 0 | 0.99023 | 0 | 1.3242 | 0.99023 | 11.8663 | 49.5919 | 10.5421
38880.5978 | 1989 | 0 | 38880.5978 | 2275 | 0 | 297.5 | 379.5 | 121.4286 | 0 | 138.8889 | 0 | 1.2143 | 0 | 1.3889 | 0 | 1.2143 | 1.3889 | 21.9899 | 6.6541 | 20.7757
38880.598 | 1587 | 0 | 38880.598 | 2285 | 0 | 318.5 | 400.5 | 96.8864 | 0 | 139.4994 | 0 | 0.96886 | 0 | 1.395 | 0 | 0.96886 | 1.395 | 52.891 | 6.1873 | 51.9221
38880.5982 | 2148 | 0 | 38880.5983 | 1632 | 0 | 339.5 | 421.5 | 131.1355 | 0 | 99.6337 | 0 | 1.3114 | 0 | 0.99634 | 0 | 1.3114 | 0.99634 | 12.96 | 48.6752 | 11.6486
38880.5985 | 2183 | 97 | 38880.5985 | 2032 | 1 | 360.5 | 442.5 | 133.2723 | 5.9219 | 124.0537 | 0.06105 | 1.3327 | 0.059219 | 1.2405 | 0.0006105 | 1.2735 | 1.2399 | 15.3255 | 19.4806 | 24.6045
38880.5987 | 2219 | 1 | 38880.5987 | 2410 | 2 | 381.5 | 463.5 | 135.4701 | 0.06105 | 147.1306 | 0.1221 | 1.3547 | 0.0006105 | 1.4713 | 0.001221 | 1.3541 | 1.4701 | 10.0077 | 0.68593 | 140.5969
38880.599 | 2283 | 0 | 38880.599 | 1398 | 0 | 402.5 | 484.5 | 139.3773 | 0 | 85.348 | 0 | 1.3938 | 0 | 0.85348 | 0 | 1.3938 | 0.85348 | 6.2803 | 73.5608 | 4.8866
38880.5992 | 2130 | 0 | 38880.5992 | 2124 | 0 | 423.5 | 505.5 | 130.0366 | 0 | 129.6703 | 0 | 1.3004 | 0 | 1.2967 | 0 | 1.3004 | 1.2967 | 13.9146 | 14.2363 | 12.6142
38880.5995 | 2335 | 3 | 38880.5995 | 1899 | 27 | 444.5 | 526.5 | 142.5519 | 0.18315 | 115.9341 | 1.6484 | 1.4255 | 0.0018315 | 1.1593 | 0.016484 | 1.4237 | 1.1429 | 3.9299 | 44.5063 | 907.334
38880.5997 | 1862 | 31 | 38880.5997 | 1380 | 23 | 465.5 | 547.5 | 113.6752 | 1.8926 | 84.2491 | 1.4042 | 1.1368 | 0.018926 | 0.84249 | 0.014042 | 1.1178 | 0.82845 | 31.4775 | 81.4981 | 772.5923
38880.5999 | 1721 | 8 | 38880.6 | 627 | 395 | 486.5 | 568.5 | 105.0672 | 0.4884 | 38.2784 | 24.1148 | 1.0507 | 0.004884 | 0.38278 | 0.24115 | 1.0458 | 0.14164 | 41.1003 | 246.8069 | 6203.6751

## C1-2
Penlight Shakedown Test 11 |  |  | 2006-06-12 | 14:15 |  | Vs = |  | 151.2442 |  | R = | 100
EPR | 7-C | Tray
650 C | 41 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38880.5934 | 1 | 0 | 38880.5934 | 1 | 0 | -81.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5936 | 1 | 0 | 38880.5936 | 1 | 0 | -60.5 | 21.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5939 | 9 | 0 | 38880.5939 | 1 | 0 | -39.5 | 42.5 | 0.54945 | 0 | 0.06105 | 0 | 0.0054945 | 0 | 0.0006105 | 0 | 0.0054945 | 0.0006105 | 27426.4444 | 247638 | 27426.4389
38880.5941 | 1 | 1 | 38880.5941 | 1 | 0 | -18.5 | 63.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 613245790.44 | 247638 | 247438.0807
38880.5943 | 1 | 0 | 38880.5944 | 1 | 0 | 2.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5946 | 1 | 0 | 38880.5946 | 1 | 0 | 23.5 | 105.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5951 | 1 | 0 | 38880.5951 | 1 | 0 | 65.5 | 147.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5953 | 1 | 0 | 38880.5953 | 1 | 0 | 86.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5956 | 1 | 0 | 38880.5956 | 1 | 0 | 107.5 | 189.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5958 | 1 | 0 | 38880.5958 | 1 | 0 | 128.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.596 | 1 | 0 | 38880.5961 | 1 | 0 | 149.5 | 231.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5963 | 1 | 0 | 38880.5963 | 1 | 0 | 170.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5965 | 1 | 0 | 38880.5965 | 1 | 0 | 191.5 | 273.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38880.5968 | 3 | 1 | 38880.5968 | 199 | 0 | 212.5 | 294.5 | 0.18315 | 0.06105 | 12.149 | 0 | 0.0018315 | 0.0006105 | 0.12149 | 0 | 0.001221 | 0.12149 | 129368.7102 | 1144.9146 | 227470.1307
38880.597 | 310 | 194 | 38880.597 | 641 | 1 | 233.5 | 315.5 | 18.9255 | 11.8437 | 39.1331 | 0.06105 | 0.18926 | 0.11844 | 0.39133 | 0.0006105 | 0.070818 | 0.39072 | 4478.8833 | 286.9444 | 754.3244
38880.5973 | 2344 | 1 | 38880.5973 | 2093 | 0 | 254.5 | 336.5 | 143.1013 | 0.06105 | 127.7778 | 0 | 1.431 | 0.0006105 | 1.2778 | 0 | 1.4304 | 1.2778 | 5.706 | 18.365 | 2053.9531
38880.5975 | 2448 | 0 | 38880.5975 | 2095 | 0 | 275.5 | 357.5 | 149.4505 | 0 | 127.8999 | 0 | 1.4945 | 0 | 1.279 | 0 | 1.4945 | 1.279 | 1.2002 | 18.252 | 0.29434
38880.5977 | 1872 | 0 | 38880.5978 | 2003 | 0 | 296.5 | 378.5 | 114.2857 | 0 | 122.2833 | 0 | 1.1429 | 0 | 1.2228 | 0 | 1.1429 | 1.2228 | 32.3387 | 23.6835 | 31.1958
38880.598 | 1696 | 0 | 38880.598 | 2172 | 0 | 317.5 | 399.5 | 103.5409 | 0 | 132.6007 | 0 | 1.0354 | 0 | 1.326 | 0 | 1.0354 | 1.326 | 46.0719 | 14.0599 | 45.0365
38880.5982 | 2400 | 0 | 38880.5982 | 2389 | 0 | 338.5 | 420.5 | 146.5201 | 0 | 145.8486 | 0 | 1.4652 | 0 | 1.4585 | 0 | 1.4652 | 1.4585 | 3.2242 | 3.6995 | 1.759
38880.5985 | 1900 | 0 | 38880.5985 | 2109 | 0 | 359.5 | 441.5 | 115.9951 | 0 | 128.7546 | 0 | 1.16 | 0 | 1.2875 | 0 | 1.16 | 1.2875 | 30.3884 | 17.467 | 29.2285
38880.5987 | 2360 | 0 | 38880.5987 | 2208 | 0 | 380.5 | 462.5 | 144.0781 | 0 | 134.7985 | 0 | 1.4408 | 0 | 1.348 | 0 | 1.4408 | 1.348 | 4.9737 | 12.2002 | 3.5329
38880.599 | 2461 | 0 | 38880.599 | 1971 | 0 | 401.5 | 483.5 | 150.2442 | 0 | 120.3297 | 0 | 1.5024 | 0 | 1.2033 | 0 | 1.5024 | 1.2033 | 0.66558 | 25.6915 | 0.83686
38880.5992 | 2211 | 0 | 38880.5992 | 2117 | 0 | 422.5 | 504.5 | 134.9817 | 0 | 129.243 | 0 | 1.3498 | 0 | 1.2924 | 0 | 1.3498 | 1.2924 | 12.0479 | 17.0231 | 10.6981
38880.5994 | 2347 | 0 | 38880.5995 | 2133 | 0 | 443.5 | 525.5 | 143.2845 | 0 | 130.2198 | 0 | 1.4328 | 0 | 1.3022 | 0 | 1.4328 | 1.3022 | 5.5552 | 16.1453 | 4.1223
38880.5997 | 2033 | 0 | 38880.5997 | 2068 | 0 | 464.5 | 546.5 | 124.1148 | 0 | 126.2515 | 0 | 1.2411 | 0 | 1.2625 | 0 | 1.2411 | 1.2625 | 21.8583 | 19.7959 | 20.6172
38880.5999 | 1646 | 0 | 38880.5999 | 2393 | 0 | 485.5 | 567.5 | 100.4884 | 0 | 146.0928 | 0 | 1.0049 | 0 | 1.4609 | 0 | 1.0049 | 1.4609 | 50.5091 | 3.5261 | 49.5042