## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 48
Test conditions: Cable: 7-conductor, 12 AWG, one EPR insulated control cable and two PE insulated, industrial control cables (cable items #2 & #15). Cable specimens present: Three lengths of cable were monitored for electrical performance, a fourth length of cable (EPR) was monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using six channels - two for each cable (see electrical connection map), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures and six cable temperatures (see thermocouple map). Shroud power: Initiated after 139 seconds of baseline data monitoring. Special Note: Test setup included three thermocouples on the outer surface of the conduit.
DAQ Time | Penlight Time | Event | Interpretation
139 | 0 | Initated Penlight Heating
1596 | 1457 | Conductors A1 & A2 short together at less than 100 ohms (6) | Cable A is shorted internally
1653-1728 | 1514-1589 | Conductors A1 & A2 short to ground at less than 1000 ohms (880 & 154) | Cable A shorts to ground (NOTE: This early ground fault may have been caused by an interaction through the Cable 4 thermocouple sheath.)
2126-2212 | 1987-2073 | Conductors C5 & C6 both short to ground (28 & 789) | Cable C shorts to ground
2207-2708 | 2068-2569 | Conductors B3 & B4 both short to ground at less than 1000 ohms (501 & 931) | Cable B shorts to ground
2224 | 2085 | Conductors C5 & C6 short together at less than 100 ohms (17) | Cable C is shorted internally
2492-2526 | 2353-2387 | The existing ground faults on conductors A1 & A2 decrease to less than 100 ohms (24 & 58)
2506 | 2367 | The existing short to ground on conductor C6 decreases to less than 100 ohms (17)
2543-2876 | 2404-2737 | The existing ground faults on conductors B3 & B4 decrease to less than 100 ohms (54 & 33)
2839 | 2700 | Conductors B3 & B4 short together at less than 1000 ohms (318) | Cable B is shorted internally
2881 | 2742 | The existing short between conductors B3 & B4 decreases to less than 100 ohms (60)
2914 | 2775 | Power to Penlight shutoff
Additional Observations
Observation 1 | Cable failures did not progress as expected during this test: the top cable (A) shorted to ground before the two lower cables (B & C). However, this may have been the result of an interaction between Cable A and the Inconel sheath on one of the thermocouples embedded in the temperature monitoring cable (note the behavior of "Cable 4" in the Temperature Plot).
Observation 2 | It took 1457 seconds (24.3 min.) from the start of Penlight heating for the first internal short to occur, and it took 1514 s (25.2 min.) for the first short to ground failure.
Observation 3 | No cable to cable interations occurred prior to one or both cables shorting to ground or internally.
Observation 4 | A post-test operational check of the thermocouples and temperature data acquisition system showed that all of the thermocouples behaved normally as long as the IRMS system was turned off. Once the IRMS was turned on, the Cable 4 thermocouple again responded with divergently cyclic readings. Turning the IRMS system off again allowed the Cable 4 thermocouple to respond normally.
Observation 5 | After removing the cables from the conduit, a post-test visual inspection of the cable bundle revealed that the "Cable 4" thermocouple sheath could have been touching the conductors on Cable A, but then the sheath on the "Cable 3" thermocouple was also found to be close enough to have touched the Cable A conductors as well.

## Thermocouple Map
Thermocouple map for TC's on and within the cable and conduit
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Outer surface of conduit
| TC2 | = | Conduit 2 | Outer surface of conduit at mid-point
| TC3 | = | Conduit 3 | Outer surface of conduit
| TC4 | = | Cable 1 | Within cable just below cable jacket, center position
| TC5 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC6 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC7 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC8 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC9 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
Cable A = EPR (item #2)
Cable B = PE (item #15)
Cable C = PE (item #15)
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 48 |  |  | 2006-08-31 | 8:30
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | C5-C6 | Penlight Time | Minimums
-138.5 | 227537.9994 | -136 | 116668.9988 | -133 | 217437.9994 | -130.5 | 237937.9994 | -127.5 | 238437.9994 | -124.5 | 234037.9994 | -122 | 223537.9994 | -119 | 238837.9994 | -116.5 | 238737.9994 | -113.5 | 229137.9994 | -110.5 | 236837.9994 | -108 | 239337.9994 | -105 | 236237.9994 | -102.5 | 235037.9994 | -99.5 | 240037.9994 | -138.5 | #REF!
-96.5 | 227537.9994 | -94 | 233437.9994 | -91 | 217437.9994 | -88.5 | 118918.9988 | -85.5 | 238437.9994 | -82.5 | 234037.9994 | -80 | 223537.9994 | -77 | 238837.9994 | -74.5 | 238737.9994 | -71.5 | 229137.9994 | -68.5 | 236837.9994 | -66 | 239337.9994 | -63 | 236237.9994 | -60.5 | 235037.9994 | -57.5 | 240037.9994 | -96.5 | #REF!
-54.5 | 227537.9994 | -52 | 233437.9994 | -49 | 217437.9994 | -46.5 | 237937.9994 | -43.5 | 238437.9994 | -40.5 | 234037.9994 | -38 | 223537.9994 | -35 | 238837.9994 | -32.5 | 238737.9994 | -29.5 | 229137.9994 | -26.5 | 236837.9994 | -24 | 239337.9994 | -21 | 236237.9994 | -18.5 | 235037.9994 | -15.5 | 240037.9994 | -54.5 | #REF!
-12.5 | 227537.9994 | -10 | 233437.9994 | -7 | 217437.9994 | -4.5 | 237937.9994 | -1.5 | 238437.9994 | 1.5 | 234037.9994 | 4 | 223537.9994 | 7 | 238837.9994 | 9.5 | 238737.9994 | 12.5 | 229137.9994 | 15.5 | 236837.9994 | 18 | 239337.9994 | 21 | 236237.9994 | 23.5 | 235037.9994 | 26.5 | 240037.9994 | -12.5 | #REF!
29.5 | 227537.9994 | 32 | 233437.9994 | 35 | 217437.9994 | 37.5 | 237937.9994 | 40.5 | 238437.9994 | 43.5 | 234037.9994 | 46 | 223537.9994 | 49 | 238837.9994 | 51.5 | 238737.9994 | 54.5 | 229137.9994 | 57.5 | 236837.9994 | 60 | 239337.9994 | 63 | 118068.9988 | 65.5 | 235037.9994 | 68.5 | 240037.9994 | 29.5 | #REF!
71.5 | 227537.9994 | 74 | 116668.9988 | 77 | 217437.9994 | 79.5 | 237937.9994 | 82.5 | 238437.9994 | 85.5 | 234037.9994 | 88 | 111718.9988 | 91 | 238837.9994 | 93.5 | 238737.9994 | 96.5 | 229137.9994 | 99.5 | 236837.9994 | 102 | 239337.9994 | 105 | 236237.9994 | 107.5 | 235037.9994 | 110.5 | 240037.9994 | 71.5 | #REF!
113.5 | 227537.9994 | 116 | 233437.9994 | 119 | 217437.9994 | 121.5 | 237937.9994 | 124.5 | 238437.9994 | 127.5 | 234037.9994 | 130 | 223537.9994 | 133 | 238837.9994 | 135.5 | 119318.9988 | 138.5 | 229137.9994 | 141.5 | 236837.9994 | 144 | 239337.9994 | 147 | 236237.9994 | 149.5 | 235037.9994 | 152.5 | 119968.9988 | 113.5 | #REF!
155.5 | 227537.9994 | 158 | 233437.9994 | 161 | 217437.9994 | 163.5 | 237937.9994 | 166.5 | 238437.9994 | 169.5 | 234037.9994 | 172 | 223537.9994 | 175 | 238837.9994 | 177.5 | 238737.9994 | 180.5 | 229137.9994 | 183.5 | 236837.9994 | 186 | 239337.9994 | 189 | 118068.9988 | 191.5 | 235037.9994 | 194.5 | 240037.9994 | 155.5 | #REF!
197.5 | 227537.9994 | 200 | 233437.9994 | 203 | 217437.9994 | 205.5 | 237937.9994 | 208.5 | 238437.9994 | 211.5 | 234037.9994 | 214 | 223537.9994 | 217 | 238837.9994 | 219.5 | 238737.9994 | 222.5 | 229137.9994 | 225.5 | 236837.9994 | 228 | 239337.9994 | 231 | 236237.9994 | 233.5 | 235037.9994 | 236.5 | 240037.9994 | 197.5 | #REF!
239.5 | 227537.9994 | 242 | 233437.9994 | 245 | 217437.9994 | 247.5 | 237937.9994 | 250.5 | 238437.9994 | 253.5 | 234037.9994 | 256 | 223537.9994 | 259 | 119368.9988 | 261.5 | 119318.9988 | 264.5 | 229137.9994 | 267.5 | 236837.9994 | 270 | 239337.9994 | 273 | 236237.9994 | 275.5 | 235037.9994 | 278.5 | 240037.9994 | 239.5 | #REF!
281.5 | 227537.9994 | 284 | 233437.9994 | 287 | 217437.9994 | 289.5 | 237937.9994 | 292.5 | 238437.9994 | 295.5 | 234037.9994 | 298 | 223537.9994 | 301 | 238837.9994 | 303.5 | 238737.9994 | 306.5 | 229137.9994 | 309.5 | 236837.9994 | 312 | 239337.9994 | 315 | 236237.9994 | 317.5 | 235037.9994 | 320.5 | 240037.9994 | 281.5 | #REF!
323.5 | 227537.9994 | 326 | 233437.9994 | 329 | 217437.9994 | 331.5 | 237937.9994 | 334.5 | 238437.9994 | 337.5 | 234037.9994 | 340 | 223537.9994 | 343 | 238837.9994 | 345.5 | 238737.9994 | 348.5 | 229137.9994 | 351.5 | 236837.9994 | 354 | 239337.9994 | 357 | 236237.9994 | 359.5 | 235037.9994 | 362.5 | 240037.9994 | 323.5 | #REF!
365.5 | 227537.9994 | 368 | 233437.9994 | 370.5 | 217437.9994 | 373.5 | 237937.9994 | 376.5 | 238437.9994 | 379.5 | 234037.9994 | 382 | 223537.9994 | 384.5 | 238837.9994 | 387.5 | 238737.9994 | 390.5 | 229137.9994 | 393.5 | 236837.9994 | 396 | 239337.9994 | 399 | 236237.9994 | 401.5 | 235037.9994 | 404.5 | 240037.9994 | 365.5 | #REF!
407.5 | 227537.9994 | 410 | 233437.9994 | 413 | 217437.9994 | 415.5 | 237937.9994 | 418.5 | 238437.9994 | 421.5 | 116968.9988 | 424 | 223537.9994 | 426.5 | 238837.9994 | 429.5 | 119318.9988 | 432.5 | 229137.9994 | 435 | 236837.9994 | 438 | 239337.9994 | 440.5 | 236237.9994 | 443.5 | 235037.9994 | 446.5 | 240037.9994 | 407.5 | #REF!
449 | 227537.9994 | 452 | 233437.9994 | 455 | 217437.9994 | 457.5 | 237937.9994 | 460.5 | 238437.9994 | 463.5 | 234037.9994 | 466 | 223537.9994 | 469 | 238837.9994 | 471.5 | 238737.9994 | 474.5 | 229137.9994 | 477 | 236837.9994 | 480 | 239337.9994 | 482.5 | 236237.9994 | 485.5 | 235037.9994 | 488.5 | 240037.9994 | 449 | #REF!
491.5 | 227537.9994 | 494 | 233437.9994 | 497 | 217437.9994 | 499.5 | 237937.9994 | 502.5 | 238437.9994 | 505.5 | 234037.9994 | 508 | 223537.9994 | 511 | 238837.9994 | 513.5 | 238737.9994 | 516.5 | 229137.9994 | 519.5 | 236837.9994 | 522 | 239337.9994 | 525 | 236237.9994 | 527.5 | 235037.9994 | 530.5 | 240037.9994 | 491.5 | #REF!
533.5 | 227537.9994 | 536 | 233437.9994 | 539 | 217437.9994 | 541.5 | 237937.9994 | 544.5 | 238437.9994 | 547 | 234037.9994 | 550 | 223537.9994 | 552 | 238837.9994 | 555.5 | 238737.9994 | 558.5 | 229137.9994 | 561.5 | 236837.9994 | 564 | 239337.9994 | 566.5 | 236237.9994 | 569.5 | 235037.9994 | 572.5 | 240037.9994 | 533.5 | #REF!
575 | 227537.9994 | 578 | 233437.9994 | 580.5 | 217437.9994 | 583.5 | 237937.9994 | 586.5 | 238437.9994 | 589.5 | 234037.9994 | 592 | 111718.9988 | 595 | 238837.9994 | 597.5 | 238737.9994 | 600.5 | 229137.9994 | 603 | 236837.9994 | 606 | 239337.9994 | 609 | 236237.9994 | 611.5 | 235037.9994 | 614.5 | 240037.9994 | 575 | #REF!
617 | 227537.9994 | 620 | 233437.9994 | 622.5 | 217437.9994 | 625.5 | 237937.9994 | 628.5 | 238437.9994 | 631 | 234037.9994 | 634 | 223537.9994 | 637 | 238837.9994 | 639.5 | 238737.9994 | 642.5 | 229137.9994 | 645.5 | 236837.9994 | 648 | 239337.9994 | 650.5 | 236237.9994 | 653.5 | 235037.9994 | 656.5 | 240037.9994 | 617 | #REF!
659 | 227537.9994 | 662 | 233437.9994 | 664.5 | 217437.9994 | 667.5 | 237937.9994 | 670.5 | 238437.9994 | 673 | 234037.9994 | 676 | 223537.9994 | 678.5 | 238837.9994 | 681.5 | 238737.9994 | 684.5 | 229137.9994 | 687 | 236837.9994 | 690 | 239337.9994 | 692.5 | 236237.9994 | 695.5 | 235037.9994 | 698.5 | 240037.9994 | 659 | #REF!
701 | 227537.9994 | 704 | 233437.9994 | 707 | 217437.9994 | 709.5 | 237937.9994 | 712.5 | 238437.9994 | 715.5 | 234037.9994 | 718 | 223537.9994 | 720.5 | 238837.9994 | 723.5 | 238737.9994 | 726.5 | 229137.9994 | 729 | 236837.9994 | 732 | 239337.9994 | 735 | 236237.9994 | 737.5 | 235037.9994 | 740.5 | 240037.9994 | 701 | #REF!
743.5 | 227537.9994 | 746 | 233437.9994 | 749 | 217437.9994 | 751.5 | 237937.9994 | 754.5 | 238437.9994 | 757.5 | 234037.9994 | 760 | 223537.9994 | 762.5 | 238837.9994 | 765.5 | 238737.9994 | 768.5 | 229137.9994 | 771 | 236837.9994 | 774 | 239337.9994 | 777 | 236237.9994 | 779.5 | 235037.9994 | 782.5 | 240037.9994 | 743.5 | #REF!
785.5 | 227537.9994 | 788 | 233437.9994 | 790.5 | 217437.9994 | 793.5 | 237937.9994 | 796.5 | 238437.9994 | 799 | 234037.9994 | 802 | 223537.9994 | 804.5 | 238837.9994 | 807.5 | 238737.9994 | 810.5 | 229137.9994 | 813 | 236837.9994 | 816 | 239337.9994 | 818.5 | 236237.9994 | 821.5 | 235037.9994 | 824.5 | 240037.9994 | 785.5 | #REF!
827 | 227537.9994 | 830 | 233437.9994 | 832.5 | 217437.9994 | 835.5 | 237937.9994 | 838.5 | 238437.9994 | 841 | 234037.9994 | 844 | 223537.9994 | 846.5 | 238837.9994 | 849.5 | 238737.9994 | 852.5 | 229137.9994 | 855 | 236837.9994 | 858 | 239337.9994 | 861 | 236237.9994 | 863.5 | 235037.9994 | 866.5 | 240037.9994 | 827 | #REF!
869.5 | 227537.9994 | 872 | 233437.9994 | 874.5 | 217437.9994 | 877.5 | 237937.9994 | 880.5 | 238437.9994 | 883 | 234037.9994 | 886 | 223537.9994 | 888.5 | 238837.9994 | 891.5 | 238737.9994 | 894.5 | 229137.9994 | 897.5 | 236837.9994 | 900 | 239337.9994 | 902.5 | 236237.9994 | 905.5 | 235037.9994 | 908.5 | 240037.9994 | 869.5 | #REF!
911 | 227537.9994 | 914 | 233437.9994 | 916.5 | 217437.9994 | 919.5 | 237937.9994 | 922.5 | 238437.9994 | 925 | 234037.9994 | 928 | 223537.9994 | 930.5 | 238837.9994 | 933.5 | 238737.9994 | 936.5 | 229137.9994 | 939 | 236837.9994 | 942 | 239337.9994 | 945 | 236237.9994 | 947.5 | 235037.9994 | 950.5 | 240037.9994 | 911 | #REF!
953 | 227537.9994 | 956 | 233437.9994 | 959 | 217437.9994 | 961.5 | 237937.9994 | 964.5 | 238437.9994 | 967 | 234037.9994 | 970 | 223537.9994 | 972 | 238638.0837 | 975.5 | 238737.9994 | 978.5 | 229137.9994 | 981 | 236837.9994 | 984 | 239337.9994 | 986.5 | 236237.9994 | 989.5 | 235037.9994 | 992.5 | 240037.9994 | 953 | #REF!
995 | 227537.9994 | 998 | 233437.9994 | 1001 | 217437.9994 | 1003.5 | 237937.9994 | 1006.5 | 238437.9994 | 1009.5 | 234037.9994 | 1012 | 223537.9994 | 1014.5 | 238837.9994 | 1017.5 | 238737.9994 | 1020.5 | 229137.9994 | 1023 | 236837.9994 | 1026 | 239337.9994 | 1028.5 | 236237.9994 | 1031.5 | 235037.9994 | 1034.5 | 240037.9994 | 995 | #REF!
1037 | 227537.9994 | 1040 | 233238.0856 | 1042.5 | 217437.9994 | 1045.5 | 237937.9994 | 1048.5 | 238437.9994 | 1051 | 234037.9994 | 1054 | 223537.9994 | 1056.5 | 238837.9994 | 1059.5 | 238737.9994 | 1062.5 | 229137.9994 | 1065 | 236837.9994 | 1068 | 239337.9994 | 1070.5 | 236237.9994 | 1073.5 | 235037.9994 | 1076.5 | 240037.9994 | 1037 | #REF!
1079 | 227537.9994 | 1082 | 233437.9994 | 1084.5 | 217238.0919 | 1087.5 | 237937.9994 | 1090.5 | 238437.9994 | 1093 | 234037.9994 | 1096 | 223537.9994 | 1098.5 | 238837.9994 | 1101.5 | 238737.9994 | 1104.5 | 228938.0872 | 1107 | 236837.9994 | 1110 | 239337.9994 | 1113 | 236237.9994 | 1115.5 | 235037.9994 | 1118.5 | 240037.9994 | 1079 | #REF!
1121 | 227537.9994 | 1124 | 233437.9994 | 1126.5 | 217437.9994 | 1129.5 | 237937.9994 | 1132.5 | 238437.9994 | 1135 | 234037.9994 | 1138 | 223338.0894 | 1140.5 | 238837.9994 | 1143.5 | 238737.9994 | 1146.5 | 229137.9994 | 1149 | 236837.9994 | 1152 | 239337.9994 | 1154.5 | 236237.9994 | 1157.5 | 234838.0851 | 1160.5 | 240037.9994 | 1121 | #REF!
1163 | 227537.9994 | 1166 | 233437.9994 | 1168.5 | 217437.9994 | 1171.5 | 237937.9994 | 1174.5 | 238437.9994 | 1177 | 234037.9994 | 1180 | 223537.9994 | 1182.5 | 238837.9994 | 1185.5 | 238737.9994 | 1188.5 | 229137.9994 | 1191 | 236837.9994 | 1194 | 239337.9994 | 1196.5 | 236237.9994 | 1199.5 | 235037.9994 | 1202.5 | 240037.9994 | 1163 | #REF!
1205 | 227537.9994 | 1208 | 233437.9994 | 1210.5 | 217437.9994 | 1213.5 | 237937.9994 | 1216.5 | 238437.9994 | 1219 | 234037.9994 | 1222 | 223537.9994 | 1224.5 | 238837.9994 | 1227.5 | 238737.9994 | 1230.5 | 229137.9994 | 1233 | 236837.9994 | 1236 | 239337.9994 | 1238.5 | 236237.9994 | 1241.5 | 235037.9994 | 1244.5 | 240037.9994 | 1205 | #REF!
1247 | 227537.9994 | 1250 | 233437.9994 | 1252.5 | 217437.9994 | 1255.5 | 237937.9994 | 1258.5 | 238437.9994 | 1261 | 234037.9994 | 1264 | 223537.9994 | 1266.5 | 238837.9994 | 1269.5 | 238737.9994 | 1272.5 | 229137.9994 | 1275 | 236837.9994 | 1278 | 239337.9994 | 1280.5 | 236237.9994 | 1283.5 | 235037.9994 | 1286.5 | 239838.0833 | 1247 | #REF!
1289 | 227537.9994 | 1292 | 233437.9994 | 1294.5 | 217437.9994 | 1297.5 | 237937.9994 | 1300.5 | 238437.9994 | 1303 | 234037.9994 | 1306 | 223537.9994 | 1308.5 | 238837.9994 | 1311.5 | 238737.9994 | 1314.5 | 229137.9994 | 1317 | 236837.9994 | 1320 | 239337.9994 | 1322.5 | 236237.9994 | 1325.5 | 235037.9994 | 1328.5 | 240037.9994 | 1289 | #REF!
1331 | 227537.9994 | 1334 | 233437.9994 | 1336.5 | 217437.9994 | 1339.5 | 237937.9994 | 1342.5 | 238437.9994 | 1345 | 234037.9994 | 1348 | 223537.9994 | 1350.5 | 238837.9994 | 1353.5 | 238737.9994 | 1356.5 | 229137.9994 | 1359 | 236837.9994 | 1362 | 239337.9994 | 1364.5 | 236237.9994 | 1367.5 | 235037.9994 | 1370.5 | 240037.9994 | 1331 | #REF!
1373 | 227537.9994 | 1376 | 233437.9994 | 1378.5 | 217437.9994 | 1381.5 | 237937.9994 | 1384.5 | 238437.9994 | 1387 | 234037.9994 | 1390 | 223338.0894 | 1392.5 | 238837.9994 | 1395.5 | 238737.9994 | 1398.5 | 229137.9994 | 1401 | 236837.9994 | 1404 | 239337.9994 | 1406.5 | 236237.9994 | 1409.5 | 235037.9994 | 1412.5 | 240037.9994 | 1373 | #REF!
1415 | 227537.9994 | 1418 | 233437.9994 | 1420.5 | 217437.9994 | 1423.5 | 237937.9994 | 1426.5 | 238437.9994 | 1429 | 234037.9994 | 1432 | 223537.9994 | 1434.5 | 238837.9994 | 1437.5 | 238737.9994 | 1440.5 | 229137.9994 | 1443 | 236837.9994 | 1446 | 239337.9994 | 1448.5 | 236237.9994 | 1451.5 | 235037.9994 | 1455 | 240037.9994 | 1415 | #REF!
1457 | 6.0161 | 1460 | 233138.1285 | 1462.5 | 217238.0919 | 1465.5 | 237937.9994 | 1468.5 | 238437.9994 | 1471 | 234037.9994 | 1474 | 223537.9994 | 1476.5 | 238837.9994 | 1479.5 | 119318.9988 | 1482.5 | 229137.9994 | 1485 | 236837.9994 | 1488 | 239337.9994 | 1490.5 | 236237.9994 | 1493.5 | 235037.9994 | 1496.5 | 240037.9994 | 1457 | #REF!
1499 | 30.7936 | 1502 | 233138.1285 | 1504.5 | 217437.9994 | 1507.5 | 237937.9994 | 1510.5 | 238437.9994 | 1513 | 234037.9994 | 1516 | 111718.9988 | 1518.5 | 59634.4976 | 1521.5 | 59609.4976 | 1524 | 229137.9994 | 1527 | 236837.9994 | 1530 | 239337.9994 | 1532.5 | 236237.9994 | 1535.5 | 235037.9994 | 1538.5 | 240037.9994 | 1499 | #REF!
1541 | 46.5156 | 1544 | 233238.0856 | 1546.5 | 108668.9988 | 1549.5 | 237937.9994 | 1552.5 | 238437.9994 | 1555 | 116968.9988 | 1558 | 55809.4976 | 1560.5 | 59634.4976 | 1563.5 | 59609.4976 | 1566.5 | 229137.9994 | 1569 | 236837.9994 | 1572 | 239337.9994 | 1574.5 | 236237.9994 | 1577.5 | 235037.9994 | 1580.5 | 240037.9994 | 1541 | #REF!
1583 | 6.9375 | 1585.5 | 233237.9572 | 1588.5 | 108668.9988 | 1591.5 | 237937.9994 | 1594.5 | 119168.9988 | 1597 | 234037.9994 | 1600 | 223537.9994 | 1602.5 | 119368.9988 | 1605.5 | 119318.9988 | 1608.5 | 229137.9994 | 1611 | 236837.9994 | 1614 | 239337.9994 | 1616.5 | 236237.9994 | 1619.5 | 235037.9994 | 1622.5 | 240037.9994 | 1583 | #REF!
1625 | 1.987 | 1628 | 233138.1285 | 1630.5 | 217138.1379 | 1633.5 | 118918.9988 | 1636 | 119168.9988 | 1639 | 116968.9988 | 1642 | 111718.9988 | 1644.5 | 79545.9982 | 1647.5 | 119318.9988 | 1650 | 229137.9994 | 1653 | 236837.9994 | 1656 | 239337.9994 | 1658.5 | 236237.9994 | 1661.5 | 235037.9994 | 1664.5 | 240037.9994 | 1625 | #REF!
1667 | 5.6102 | 1669.5 | 233038.1713 | 1672.5 | 108668.9988 | 1675.5 | 118918.9988 | 1678 | 119168.9988 | 1681 | 116968.9988 | 1684 | 111718.9988 | 1686.5 | 119368.9988 | 1689.5 | 119318.9988 | 1692.5 | 229137.9994 | 1695 | 236837.9994 | 1698 | 239337.9994 | 1700.5 | 236237.9994 | 1703.5 | 235037.9994 | 1706.5 | 240037.9994 | 1667 | #REF!
1709 | 17.9732 | 1712 | 233137.9144 | 1714.5 | 72412.6648 | 1717.5 | 79245.9982 | 1720.5 | 59534.4976 | 1723 | 58434.4976 | 1726 | 44627.5969 | 1728.5 | 39722.9963 | 1731.5 | 39706.3297 | 1734.5 | 229137.9994 | 1737 | 236837.9994 | 1740 | 239337.9994 | 1742.5 | 236237.9994 | 1745.5 | 235037.9994 | 1748.5 | 240037.9994 | 1709 | #REF!
1751 | 3.8558 | 1754 | 116319.2355 | 1756.5 | 30976.8529 | 1759.5 | 33905.4243 | 1762.5 | 33976.8529 | 1765 | 25915.3278 | 1768 | 27854.7451 | 1770.5 | 21621.6296 | 1773.5 | 21612.5387 | 1776.5 | 229137.9994 | 1779 | 236837.9994 | 1782 | 239337.9994 | 1784.5 | 236237.9994 | 1787.5 | 235037.9994 | 1790.5 | 240037.9994 | 1751 | #REF!
1793 | 5.4496 | 1796 | 116469.107 | 1798.5 | 72412.6648 | 1801.5 | 237638.126 | 1804 | 79412.6648 | 1807 | 77945.9982 | 1809.5 | 55809.4976 | 1812.5 | 59634.4976 | 1815.5 | 59609.4976 | 1818.5 | 229137.9994 | 1821 | 236837.9994 | 1824 | 239337.9994 | 1826.5 | 236237.9994 | 1829.5 | 235037.9994 | 1832.5 | 240037.9994 | 1793 | #REF!
1835 | 1.8318 | 1838 | 116268.8716 | 1840.5 | 213839.6549 | 1843.5 | 234139.5964 | 1846.5 | 234239.7607 | 1849 | 229639.8792 | 1852 | 4372.7295 | 1854.5 | 233740.1344 | 1857.5 | 232640.554 | 1860 | 229137.9994 | 1863 | 236837.9994 | 1866 | 239337.9994 | 1868.5 | 236237.9994 | 1871.5 | 235037.9994 | 1874 | 240037.9994 | 1835 | #REF!
1877 | 15.8287 | 1880 | 226134.9171 | 1882.5 | 209941.4477 | 1885.5 | 229341.6129 | 1888 | 229841.6053 | 1891 | 225941.4595 | 1894 | 2530.9834 | 1896.5 | 230841.3481 | 1899.5 | 230141.6008 | 1902.5 | 229137.9994 | 1905 | 236837.9994 | 1908 | 239337.9994 | 1910.5 | 236237.9994 | 1913.5 | 235037.9994 | 1916.5 | 218347.0365 | 1877 | #REF!
1919 | 3.4897 | 1922 | 223433.761 | 1924.5 | 205843.3324 | 1927.5 | 226442.8312 | 1930.5 | 227642.5276 | 1933 | 223142.6554 | 1935.5 | 1763.5767 | 1938.5 | 225948.7141 | 1941.5 | 225743.443 | 1944.5 | 229137.9994 | 1947 | 236837.9994 | 1949.5 | 239337.9994 | 1952.5 | 236237.9994 | 1955.5 | 235037.9994 | 1958 | 236039.6657 | 1919 | #REF!
1961 | 17.3912 | 1964 | 221043.3096 | 1966.5 | 204344.0219 | 1969.5 | 103042.7161 | 1972.5 | 225548.732 | 1975 | 220243.894 | 1977.5 | 2279.0703 | 1980.5 | 2554.8117 | 1983.5 | 229345.7877 | 1986 | 229137.9994 | 1989 | 236837.9994 | 1992 | 239337.9994 | 1994.5 | 236237.9994 | 1997.5 | 235037.9994 | 2000.5 | 129530.0304 | 1961 | #REF!
2003 | 4.8083 | 2005.5 | 222333.29 | 2008.5 | 204349.9519 | 2011.5 | 1676.3212 | 2014 | 226742.9049 | 2017 | 219244.3211 | 2020 | 1520.481 | 2022.5 | 1891.0767 | 2025.5 | 224344.0292 | 2028.5 | 229137.9994 | 2031 | 236837.9994 | 2033.5 | 119618.9988 | 2036.5 | 236237.9994 | 2039.5 | 117468.9988 | 2042 | 35308.5686 | 2003 | #REF!
2045 | 14.4958 | 2047.5 | 212955.4276 | 2050.5 | 196047.8374 | 2053.5 | 991.7843 | 2056 | 218462.9017 | 2059 | 214746.243 | 2061.5 | 1076.9261 | 2064.5 | 903.7959 | 2067.5 | 197309.8805 | 2070 | 114518.9988 | 2073 | 236837.9994 | 2075.5 | 119618.9988 | 2078.5 | 236237.9994 | 2081.5 | 117468.9988 | 2084.5 | 16.8202 | 2045 | #REF!
2087 | 0.04044 | 2089.5 | 209548.2339 | 2092.5 | 190150.5495 | 2095.5 | 953.1275 | 2098 | 215712.1182 | 2101 | 208548.891 | 2104 | 692.8704 | 2106.5 | 883.1356 | 2109.5 | 212901.8089 | 2112.5 | 114518.9988 | 2115 | 236837.9994 | 2117.5 | 119618.9988 | 2120.5 | 236237.9994 | 2123.5 | 117468.9988 | 2126 | 11.3335 | 2087 | #REF!
2129 | 15.9335 | 2131.5 | 207660.0093 | 2134.5 | 191261.9958 | 2137.5 | 749.9648 | 2140.5 | 98376.3696 | 2143 | 199652.6922 | 2146 | 579.5499 | 2148.5 | 781.5246 | 2151.5 | 602.2571 | 2154 | 114518.9988 | 2157 | 236837.9994 | 2159.5 | 119618.9988 | 2162.5 | 118068.9988 | 2165.5 | 117468.9988 | 2168 | 5.6917 | 2129 | #REF!
2171 | 4.2067 | 2173.5 | 201964.8479 | 2176.5 | 180671.7412 | 2179.5 | 564.6921 | 2182 | 558.7238 | 2185 | 204163.4551 | 2187.5 | 486.7438 | 2190.5 | 626.0545 | 2193.5 | 598.1479 | 2196 | 114518.9988 | 2199 | 236837.9994 | 2201.5 | 119618.9988 | 2204.5 | 118068.9988 | 2207.5 | 78279.3315 | 2210 | 32.0128 | 2171 | #REF!
2213 | 41.6055 | 2215.5 | 193871.8275 | 2218.5 | 181471.0057 | 2221.5 | 543.1201 | 2224 | 462.3308 | 2227 | 198867.9823 | 2229.5 | 450.5846 | 2232.5 | 582.4663 | 2235.5 | 461.7123 | 2238 | 114518.9988 | 2241 | 236837.9994 | 2243.5 | 119618.9988 | 2246.5 | 118068.9988 | 2249.5 | 117468.9988 | 2252 | 3.373 | 2213 | #REF!
2255 | 10.8279 | 2258 | 195570.3288 | 2260.5 | 177075.051 | 2263.5 | 499.3496 | 2266 | 443.0987 | 2269 | 195071.2283 | 2271.5 | 377.5733 | 2274.5 | 515.5827 | 2277.5 | 450.053 | 2280 | 114518.9988 | 2283 | 236837.9994 | 2285.5 | 119618.9988 | 2288.5 | 118068.9988 | 2291.5 | 117468.9988 | 2294 | 15.0289 | 2255 | #REF!
2297 | 9.0332 | 2299.5 | 186677.9935 | 2302.5 | 168360.5708 | 2305.5 | 377.6839 | 2308 | 335.7502 | 2311 | 188776.6097 | 2313.5 | 297.5893 | 2316.5 | 345.4526 | 2319.5 | 343.6084 | 2322 | 114518.9988 | 2325 | 236837.9994 | 2327.5 | 119618.9988 | 2330.5 | 118068.9988 | 2333.5 | 117468.9988 | 2336 | 7.8105 | 2297 | #REF!
2339 | 16.6431 | 2341.5 | 183880.3914 | 2344.5 | 162388.5659 | 2347.5 | 341.2999 | 2350 | 321.8462 | 2352 | 171990.9602 | 2355.5 | 270.5075 | 2358.5 | 170.0589 | 2361.5 | 56.7239 | 2364 | 114518.9988 | 2367 | 118368.9988 | 2369.5 | 119618.9988 | 2372.5 | 118068.9988 | 2375.5 | 117468.9988 | 2378 | 4.6858 | 2339 | #REF!
2381 | 93.1095 | 2383.5 | 61185.5563 | 2386.5 | 53488.7783 | 2389.5 | 23.0672 | 2392 | 27.1107 | 2395 | 30711.7437 | 2397.5 | 19.4927 | 2400.5 | 21.0254 | 2403.5 | 33.2441 | 2406 | 114518.9988 | 2409 | 118368.9988 | 2411.5 | 119618.9988 | 2414.5 | 118068.9988 | 2417.5 | 117468.9988 | 2420 | 13.4561 | 2381 | #REF!
2423 | 14.6924 | 2425.5 | 28213.8172 | 2428.5 | 28012.2224 | 2431.5 | 28.3161 | 2434 | 26.2126 | 2437 | 23018.321 | 2439.5 | 27.3909 | 2442.5 | 9.3008 | 2445.5 | 30.7762 | 2448 | 114518.9988 | 2451 | 118368.9988 | 2453.5 | 119618.9988 | 2456.5 | 118068.9988 | 2459.5 | 117468.9988 | 2462 | 2.6369 | 2423 | #REF!
2465 | 15.3103 | 2467.5 | 49795.3192 | 2470.5 | 35105.6948 | 2473.5 | 13.3945 | 2476 | 29.6639 | 2479 | 32510.2061 | 2481.5 | 12.3774 | 2484.5 | 16.2302 | 2487.5 | 11.851 | 2490 | 114518.9988 | 2493 | 118368.9988 | 2495.5 | 119618.9988 | 2498.5 | 118068.9988 | 2501.5 | 117468.9988 | 2504 | 1.5514 | 2465 | #REF!
2507 | 4.7492 | 2509.5 | 39104.4825 | 2512.5 | 13225.8293 | 2515.5 | 32.1144 | 2518 | 37.2298 | 2521 | 60985.8615 | 2523.5 | 25.9198 | 2526.5 | 31.0522 | 2529.5 | 34.9405 | 2532 | 114518.9988 | 2535 | 118368.9988 | 2537.5 | 119618.9988 | 2540.5 | 118068.9988 | 2543.5 | 117468.9988 | 2546 | 16.411
2549 | 8 | 2551.5 | 49674.1072 | 2554.5 | 26213.8773 | 2557.5 | 24.5238 | 2560 | 35.6327 | 2563 | 23314.9358 | 2565.5 | 32.2521 | 2568.5 | 23.6027 | 2571.5 | 38.8747 | 2574 | 212752.221 | 2577 | 501.1249 | 2579.5 | 512.1347 | 2582.5 | 118068.9988 | 2585.5 | 117468.9988 | 2588 | 23.2456
2591 | 50.9967 | 2593.5 | 17269.3011 | 2596.5 | 18021.4162 | 2599.5 | 38.0776 | 2602 | 18.5926 | 2605 | 12.0678 | 2607.5 | 25.7745 | 2610.5 | 6.5698 | 2613.5 | 7.2196 | 2616 | 145810.6756 | 2619 | 190.9403 | 2621.5 | 401.6752 | 2624.5 | 118068.9988 | 2627.5 | 117468.9988 | 2630 | 1.1501
2633 | 1.7781 | 2635.5 | 42136.2067 | 2638.5 | 31109.3724 | 2641.5 | 38.4884 | 2644 | 8.0394 | 2647 | 7.6401 | 2649.5 | 8.7081 | 2652.5 | 31.4217 | 2655.5 | 30.8497 | 2658 | 171887.9045 | 2661 | 313.1545 | 2663.5 | 250.1511 | 2666.5 | 58984.4976 | 2669.5 | 78279.3315 | 2672 | 4.7809
2675 | 6.9817 | 2677.5 | 21007.676 | 2680.5 | 46053.1633 | 2683.5 | 7.6584 | 2686 | 22.4812 | 2689 | 10.4275 | 2691.5 | 10.4851 | 2694.5 | 32.1669 | 2697.5 | 33.8561 | 2700 | 317.983 | 2703 | 243.4662 | 2705.5 | 389.3497 | 2708.5 | 613.81 | 2711.5 | 646.2775 | 2714 | 28.8166
2717 | 2.1174 | 2719.5 | 30026.4824 | 2722.5 | 21706.9682 | 2725.5 | 24.5238 | 2728 | 18.4712 | 2731 | 30.6007 | 2733.5 | 10.0356 | 2736.5 | 17.2901 | 2739.5 | 6.1313 | 2742 | 59.659 | 2745 | 53.2178 | 2747.5 | 63.9017 | 2750.5 | 440.5524 | 2753.5 | 931.1678 | 2756 | 8.773
2759 | 30.0558 | 2761.5 | 16.6795 | 2764.5 | 26081.2026 | 2767.5 | 37.3441 | 2770 | 16.6191 | 2773 | 33.3441 | 2775.5 | 12.3191 | 2778.5 | 36.2584 | 2781.5 | 10.8302 | 2784 | 39.036 | 2787 | 14.5564 | 2789.5 | 14.6332 | 2792.5 | 47.4816 | 2795.5 | 22.4 | 2798 | 4.1193
2801 | 0.95878 | 2803.5 | 7.4121 | 2806.5 | 4976.2379 | 2809.5 | 7.5071 | 2812 | 22.7406 | 2815 | 22.9939 | 2817.5 | 20.5525 | 2820.5 | 6.718 | 2823.5 | 11.7968 | 2826 | 47.2168 | 2829 | 9.991 | 2831.5 | 10.6334 | 2834.5 | 19.3219 | 2837.5 | 39.2739 | 2840 | 23.3759
2843 | 5.1752 | 2845.5 | 27.4916 | 2848.5 | 17.2988 | 2851.5 | 7.5071 | 2854 | 31.4222 | 2857 | 34.8378 | 2859.5 | 7.1448 | 2862.5 | 17.2901 | 2865.5 | 26.3728 | 2868 | 51.1391 | 2871 | 7.4573 | 2873.5 | 17.0047 | 2876.5 | 48.8072 | 2879.5 | 21.8128 | 2882 | 9.9606
2885 | 2.6283 | 2887.5 | 5.7966 | 2890.5 | 10.0791 | 2893.5 | 8.8841 | 2896 | 32.8476 | 2899 | 2.9225 | 2901.5 | 1.927 | 2904.5 | 25.1335 | 2907.5 | 28.3959 | 2910 | 6.145 | 2913 | 4.8888 | 2915.5 | 5.4279 | 2918.5 | 12.965 | 2921.5 | 40.2075 | 2924 | 29.458
2927 | 2.8127 | 2929.5 | 24.5589 | 2932.5 | 2.9101 | 2935.5 | 33.4808 | 2938 | 6.4877 | 2941 | 27.1098 | 2943.5 | 1.9753 | 2946.5 | 16.5814 | 2949.5 | 4.5858 | 2952 | 36.5069 | 2955 | 4.5041 | 2957.5 | 25.8041 | 2960.5 | 28.2431 | 2963.5 | 18.4635 | 2966 | 28.6042
2969 | 37.0953 | 2971.5 | 4.7129 | 2974.5 | 16.3945 | 2977.5 | 9.9789 | 2980 | 27.6696 | 2983 | 20.9674 | 2985.5 | 0.47933 | 2988.5 | 18.7327 | 2991.5 | 35.9629 | 2994 | 183.4224 | 2997 | 22.4931 | 2999.5 | 25.5329 | 3002.5 | 22.0501 | 3005.5 | 16.5264 | 3008 | 12.0324
3011 | 3.145 | 3013.5 | 4.3725 | 3016.5 | 25.7228 | 3019.5 | 28.0327 | 3022 | 13.7473 | 3025 | 10.5894 | 3027.5 | 24.6952 | 3030.5 | 5.737 | 3033.5 | 25.4859 | 3036 | 126.2909 | 3038.5 | 29.8729 | 3041.5 | 23.9957 | 3044.5 | 15.4156 | 3047.5 | 29.9739 | 3050 | 0.2689
3053 | 0.0080629 | 3055.5 | 32.8447 | 3058.5 | 17.4943 | 3061.5 | 32.1144 | 3064 | 9.2191 | 3067 | 10.6976 | 3069.5 | 5.4179 | 3072.5 | 18.0071 | 3075.5 | 17.0626 | 3078 | 0.36799 | 3081 | 23.0822 | 3083.5 | 18.9837 | 3086.5 | 13.0209 | 3089.5 | 35.8988 | 3092 | 23.5064
3094.5 | 6.8929 | 3097.5 | 29.3754 | 3100.5 | 15.0007 | 3103 | 36.458 | 3106 | 7.6852 | 3109 | 9.5183 | 3111.5 | 6.458 | 3114.5 | 20.3973 | 3117.5 | 7.7719 | 3120 | 57.801 | 3122.5 | 26.5275 | 3125.5 | 16.1843 | 3128.5 | 36.8404 | 3131 | 16.6457 | 3134 | 0.76925
3137 | 55.1094 | 3139.5 | 3.3166 | 3142.5 | 0.49134 | 3145.5 | 35.662 | 3148 | 33.9173 | 3151 | 15.848 | 3153.5 | 8.7628 | 3156.5 | 19.2212 | 3159 | 22.2492 | 3162 | 55.8661 | 3164.5 | 10.7362 | 3167.5 | 12.6812 | 3170.5 | 7.8924 | 3173 | 34.467 | 3176 | 0.050906
3178.5 | 17.8998 | 3181.5 | 3.89 | 3184.5 | 8.9401 | 3187.5 | 18.0993 | 3190 | 14.4807 | 3193 | 18.1386 | 3195.5 | 15.0614 | 3198.5 | 21.2151 | 3201 | 4.1589 | 3204 | 35.6897 | 3207 | 0.17923 | 3209.5 | 21.5982 | 3212.5 | 10.6667 | 3215.5 | 7.2363 | 3218 | 6.7164
3221 | 43.3171 | 3223.5 | 20.6544 | 3226.5 | 7.0552 | 3229 | 18.5237 | 3232 | 12.9676 | 3234.5 | 11.736 | 3237.5 | 5.7797 | 3240.5 | 8.4266 | 3243.5 | 22.572 | 3246 | 37.8085 | 3249 | 27.5768 | 3251.5 | 4.5663 | 3255 | 12.299 | 3257.5 | 25.8337 | 3260 | 7.7102
3262.5 | 5.57 | 3265.5 | 6.4472 | 3268.5 | 16.845 | 3271 | 31.4414 | 3274 | 36.5865 | 3277 | 10.3197 | 3279.5 | 3.894 | 3282.5 | 11.8441 | 3285.5 | 5.1121 | 3288 | 29.0293 | 3290.5 | 11.9272 | 3293.5 | 26.4183 | 3296.5 | 14.0353 | 3299 | 19.0196 | 3302 | 3.3267

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 48 |  |  | 2006-08-31 | 8:30
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | Minimums Overall
-133.1 | 116669 |  | -124.1 | 223538 | -118.5 | 229138 | -115.2 | 217438 | -112.9 | 236238 | -110.8 | 235038 | -133.1 | 116669
-91.1 | 118919 |  | -82.1 | 223538 | -76.5 | 229138 | -73.2 | 217438 | -70.9 | 236238 | -68.8 | 235038 | -91.1 | 118919
-49.1 | 217438 |  | -40.1 | 223538 | -34.5 | 229138 | -31.2 | 217438 | -28.9 | 236238 | -26.8 | 119619 | -49.1 | 119619
-7.1 | 217438 |  | 1.9 | 223538 | 7.5 | 229138 | 10.8 | 217438 | 13.1 | 236238 | 15.2 | 235038 | -7.1 | 217438
34.9 | 217438 |  | 43.9 | 223538 | 49.5 | 229138 | 52.8 | 118069 | 55.1 | 236238 | 57.2 | 235038 | 34.9 | 118069
76.9 | 116669 |  | 85.9 | 111719 | 91.5 | 229138 | 94.8 | 217438 | 97.1 | 236238 | 99.2 | 235038 | 76.9 | 111719
118.9 | 217438 |  | 127.9 | 119319 | 133.5 | 229138 | 136.8 | 217438 | 139.1 | 118369 | 141.2 | 235038 | 118.9 | 118369
160.9 | 217438 |  | 169.9 | 223538 | 175.5 | 229138 | 178.8 | 118069 | 181.1 | 236238 | 183.2 | 119169 | 160.9 | 118069
202.9 | 217438 |  | 211.9 | 223538 | 217.5 | 229138 | 220.8 | 217438 | 223.1 | 236238 | 225.2 | 235038 | 202.9 | 217438
244.9 | 217438 |  | 253.9 | 119319 | 259.5 | 229138 | 262.8 | 217438 | 265.1 | 236238 | 267.2 | 119319 | 244.9 | 119319
286.9 | 217438 |  | 295.9 | 223538 | 301.5 | 229138 | 304.8 | 217438 | 307.1 | 236238 | 309.2 | 119319 | 286.9 | 119319
328.9 | 217438 |  | 337.9 | 223538 | 343.5 | 229138 | 346.8 | 217438 | 349.1 | 236238 | 351.2 | 117469 | 328.9 | 117469
370.8 | 217438 |  | 379.8 | 223538 | 385.5 | 229138 | 388.7 | 217438 | 391 | 236238 | 393.2 | 235038 | 370.8 | 217438
412.9 | 217438 |  | 421.8 | 116969 | 427.4 | 229138 | 430.7 | 217438 | 432.8 | 236238 | 435.2 | 235038 | 412.9 | 116969
454.8 | 217438 |  | 463.8 | 223538 | 469.4 | 229138 | 472.7 | 217438 | 474.9 | 236238 | 477.2 | 235038 | 454.8 | 217438
496.9 | 217438 |  | 505.9 | 223538 | 511.5 | 229138 | 514.8 | 217438 | 517.1 | 236238 | 519.2 | 235038 | 496.9 | 217438
538.9 | 217438 |  | 547.6 | 223538 | 553.4 | 229138 | 556.7 | 217438 | 558.8 | 236238 | 561.2 | 235038 | 538.9 | 217438
580.7 | 217438 |  | 589.8 | 111719 | 595.4 | 229138 | 598.7 | 217438 | 601 | 236238 | 603.2 | 117469 | 580.7 | 111719
622.7 | 217438 |  | 631.7 | 223538 | 637.4 | 229138 | 640.6 | 111719 | 643 | 236238 | 645.2 | 235038 | 622.7 | 111719
664.7 | 217438 |  | 673.6 | 223538 | 679.3 | 229138 | 682.6 | 217438 | 684.8 | 236238 | 687.2 | 235038 | 664.7 | 217438
706.8 | 217438 |  | 715.7 | 223538 | 721.4 | 229138 | 724.8 | 217438 | 726.9 | 236238 | 729.2 | 235038 | 706.8 | 217438
748.9 | 217438 |  | 757.8 | 223538 | 763.4 | 229138 | 766.8 | 217438 | 768.9 | 236238 | 771.2 | 235038 | 748.9 | 217438
790.8 | 217438 |  | 799.7 | 223538 | 805.3 | 229138 | 808.6 | 217438 | 810.8 | 236238 | 813.2 | 235038 | 790.8 | 217438
832.7 | 217438 |  | 841.6 | 223538 | 847.3 | 229138 | 850.7 | 217438 | 852.9 | 236238 | 855.2 | 235038 | 832.7 | 217438
874.8 | 217438 |  | 883.7 | 223538 | 889.4 | 229138 | 892.6 | 217438 | 894.9 | #DIV/0! | 897.2 | 235038 | 874.8 | #DIV/0!
916.7 | 217438 |  | 925.6 | 223538 | 931.3 | 229138 | 934.7 | 217438 | 936.9 | 236238 | 939.2 | 235038 | 916.7 | 217438
958.8 | 217438 |  | 967.5 | 223538 | 973.3 | 229138 | 976.7 | 217438 | 978.7 | 236238 | 981.2 | 235038 | 958.8 | 217438
1000.8 | 217438 |  | 1009.7 | 223538 | 1015.4 | 229138 | 1018.7 | 217438 | 1020.8 | 236238 | 1023.2 | 235038 | 1000.8 | 217438
1042.7 | 217438 |  | 1051.6 | 223538 | 1057.3 | 229138 | 1060.6 | 114519 | 1062.8 | 236238 | 1065.2 | 119319 | 1042.7 | 114519
1084.7 | 227538 |  | 1093.6 | 223538 | 1099.3 | 233438 | 1102.7 | 217438 | 1104.9 | 236238 | 1107.2 | 235038 | 1084.7 | 217438
1126.7 | 217438 |  | 1135.6 | 227538 | 1141.3 | 229138 | 1144.6 | 217438 | 1146.8 | 236238 | 1149.2 | 235038 | 1126.7 | 217438
1168.7 | 217438 |  | 1177.6 | 223538 | 1183.3 | 229138 | 1186.6 | 217438 | 1188.8 | 118919 | 1191.2 | 235038 | 1168.7 | 118919
1210.7 | 217438 |  | 1219.6 | 223538 | 1225.3 | 229138 | 1228.6 | 217438 | 1230.8 | 236238 | 1233.2 | 235038 | 1210.7 | 217438
1252.7 | 217438 |  | 1261.6 | 223538 | 1267.3 | 229138 | 1270.6 | 217438 | 1272.8 | 236238 | 1275.2 | 235038 | 1252.7 | 217438
1294.7 | 217438 |  | 1303.6 | 223538 | 1309.3 | 229138 | 1312.6 | 217438 | 1314.8 | 236238 | 1317.2 | 235038 | 1294.7 | 217438
1336.7 | 217438 |  | 1345.6 | 223538 | 1351.3 | 229138 | 1354.6 | 217438 | 1356.8 | 236238 | 1359.2 | 119619 | 1336.7 | 119619
1378.7 | 217438 |  | 1387.6 | 227538 | 1393.3 | 229138 | 1396.6 | 217438 | 1398.8 | 236238 | 1401.2 | 235038 | 1378.7 | 217438
1420.7 | 217438 |  | 1429.6 | 223538 | 1435.3 | 229138 | 1438.6 | 217438 | 1440.9 | 236238 | 1443.3 | 235038 | 1420.7 | 217438
1462.7 | 2639.9349 |  | 1471.6 | 5125.8149 | 1477.3 | 229138 | 1480.6 | 217438 | 1482.8 | 236238 | 1485.2 | 235038 | 1462.7 | 2639.9349
1504.7 | 1041.3638 |  | 1513.6 | 880.1205 | 1519.2 | 229138 | 1522.5 | 74446 | 1524.8 | 236238 | 1527.2 | 235038 | 1504.7 | 880.1205
1546.7 | 7559.6792 |  | 1555.6 | 3286.062 | 1561.3 | 229138 | 1564.6 | 55809.5 | 1566.8 | 236238 | 1569.2 | 235038 | 1546.7 | 3286.062
1588.6 | 154.2815 |  | 1597.6 | 140.7888 | 1603.2 | 229138 | 1606.6 | 108669 | 1608.8 | 236238 | 1611.2 | 235038 | 1588.6 | 140.7888
1630.6 | 104.8424 |  | 1639.6 | 108.1466 | 1645.2 | 229138 | 1648.5 | 111719 | 1650.8 | 236238 | 1653.1 | 235038 | 1630.6 | 104.8424
1672.5 | 130.8008 |  | 1681.6 | 129.5419 | 1687.2 | 229138 | 1690.6 | 111719 | 1692.8 | 236238 | 1695.1 | 235038 | 1672.5 | 129.5419
1714.7 | 708.3104 |  | 1723.6 | 1006.4833 | 1729.3 | 229138 | 1732.6 | 44627.6 | 1734.8 | 236238 | 1737.2 | 235038 | 1714.7 | 708.3104
1756.7 | 492.188 |  | 1765.6 | 601.8148 | 1771.3 | 229138 | 1774.6 | 22263.8 | 1776.8 | 236238 | 1779.2 | 235038 | 1756.7 | 492.188
1798.6 | 336.4876 |  | 1807.5 | 462.6589 | 1813.3 | 229138 | 1816.5 | 74446 | 1818.8 | 236238 | 1821.1 | 235038 | 1798.6 | 336.4876
1840.7 | 124.2167 |  | 1849.6 | 132.972 | 1855.2 | 229138 | 1858.5 | 4869.7333 | 1860.7 | 236238 | 1863.1 | 235038 | 1840.7 | 124.2167
1882.6 | 2732.6089 |  | 1891.6 | 828.3402 | 1897.3 | 229138 | 1900.6 | 2842.6053 | 1902.8 | 1016.4578 | 1905.1 | 235038 | 1882.6 | 828.3402
1924.7 | 83.7532 |  | 1933.5 | 86.9024 | 1939.2 | 229138 | 1942.5 | 2071.2427 | 1944.7 | 6216.8576 | 1947 | 235038 | 1924.7 | 83.7532
1966.7 | 316.2052 |  | 1975.5 | 492.6579 | 1981.2 | 229138 | 1984.4 | 2531.0353 | 1986.8 | 27.8672 | 1989.2 | 119169 | 1966.7 | 27.8672
2008.5 | 1598.7459 |  | 2017.6 | 1082.5316 | 2023.1 | 119619 | 2026.6 | 1660.9291 | 2028.7 | 10.364 | 2030.9 | 119969 | 2008.5 | 10.364
2050.5 | 925.653 |  | 2059.5 | 537.1319 | 2065 | 114519 | 2068.4 | 930.5899 | 2070.8 | 7.622 | 2073 | 789.4 | 2050.5 | 7.622
2092.5 | 156.3785 |  | 2101.6 | 215.3731 | 2107.1 | 114519 | 2110.6 | 824.124 | 2112.7 | 12.6351 | 2114.9 | 119.104 | 2092.5 | 12.6351
2134.6 | 622.399 |  | 2143.6 | 579.7508 | 2149 | 114519 | 2152.5 | 728.2889 | 2154.7 | 3.1143 | 2157 | 83.272 | 2134.6 | 3.1143
2176.5 | 106.968 |  | 2185.5 | 143.5161 | 2191 | 114519 | 2194.4 | 633.2393 | 2196.7 | 4.9458 | 2198.9 | 93.2346 | 2176.5 | 4.9458
2218.5 | 462.5896 |  | 2227.5 | 397.1551 | 2233 | 114519 | 2236.4 | 428.695 | 2238.7 | 2.2666 | 2240.9 | 119.104 | 2218.5 | 2.2666
2260.6 | 442.2404 |  | 2269.5 | 339.7105 | 2275.1 | 114519 | 2278.4 | 440.1884 | 2280.7 | 16.2896 | 2282.9 | 123.5922 | 2260.6 | 16.2896
2302.5 | 206.1441 |  | 2311.5 | 297.9324 | 2317 | 114519 | 2320.4 | 339.3674 | 2322.7 | 4.0218 | 2324.9 | 170.4257 | 2302.5 | 4.0218
2344.5 | 296.7852 |  | 2353.3 | 57.6488 | 2358.8 | 114519 | 2362.4 | 217.217 | 2364.7 | 5.9592 | 2366.9 | 16.9702 | 2344.5 | 5.9592
2386.5 | 24.237 |  | 2395.5 | 15.1762 | 2401 | 114519 | 2404.4 | 33.4356 | 2406.7 | 7.6013 | 2408.9 | 10.7996 | 2386.5 | 7.6013
2428.5 | 13.8167 |  | 2437.5 | 7.7607 | 2443 | 114519 | 2446.4 | 13.8107 | 2448.7 | 1.7691 | 2450.9 | 9.2207 | 2428.5 | 1.7691
2470.5 | 14.6618 |  | 2479.5 | 13.1397 | 2485 | 114519 | 2488.4 | 23.0132 | 2490.7 | 1.2988 | 2492.9 | 2.1007 | 2470.5 | 1.2988
2512.5 | 6.535 |  | 2521.5 | 26.9949 | 2527 | 114519 | 2530.4 | 14.8629 | 2532.7 | 0.69791 | 2534.9 | 3.3483 | 2512.5 | 0.69791
2554.5 | 13.7823 |  | 2563.5 | 8.9908 | 2569 | 501.3655 | 2572.4 | 17.3953 | 2574.7 | 15.0743 | 2576.9 | 13.3742 | 2554.5 | 8.9908
2596.5 | 9.1009 |  | 2605.5 | 7.9214 | 2611 | 175.7379 | 2614.4 | 5.2414 | 2616.7 | 2.5792 | 2618.9 | 9.1829 | 2596.5 | 2.5792
2638.5 | 1.9469 |  | 2647.5 | 5.3214 | 2653 | 250.5681 | 2656.4 | 15.3963 | 2658.7 | 4.667 | 2660.9 | 2.1139 | 2638.5 | 1.9469
2680.5 | 8.9918 |  | 2689.5 | 11.7071 | 2695 | 243.8868 | 2698.4 | 20.3002 | 2700.7 | 3.1684 | 2702.9 | 0.7015 | 2680.5 | 0.7015
2722.5 | 1.6754 |  | 2731.5 | 5.0412 | 2737 | 54.1561 | 2740.4 | 2.6333 | 2742.7 | 5.0257 | 2744.9 | 5.5851 | 2722.5 | 1.6754
2764.5 | 13.7824 |  | 2773.5 | 9.9368 | 2779 | 15.8055 | 2782.4 | 0.73784 | 2784.7 | 2.7798 | 2786.9 | 3.7524 | 2764.5 | 0.73784
2806.5 | 8.7235 |  | 2815.5 | 8.0678 | 2821 | 11.2907 | 2824.4 | 15.2825 | 2826.7 | 2.6911 | 2828.9 | 13.0471 | 2806.5 | 2.6911
2848.5 | 6.6945 |  | 2857.5 | 8.4043 | 2863 | 8.787 | 2866.4 | 21.7336 | 2868.7 | 0.69613 | 2870.9 | 3.8426 | 2848.5 | 0.69613
2890.5 | 7.1275 |  | 2899.5 | 3.2493 | 2905 | 1.2158 | 2908.4 | 10.5974 | 2910.7 | 0.91289 | 2912.9 | 1.0713 | 2890.5 | 0.91289
2932.5 | 1.5634 |  | 2941.5 | 3.297 | 2947 | 5.5151 | 2950.4 | 14.0294 | 2952.7 | 2.6026 | 2954.9 | 2.9031 | 2932.5 | 1.5634
2974.5 | 6.0572 |  | 2983.5 | 0.87415 | 2989 | 11.3677 | 2992.4 | 12.3647 | 2994.7 | 0.69027 | 2996.9 | 1.8795 | 2974.5 | 0.69027
3016.5 | 3.9629 |  | 3025.5 | 1.7262 | 3030.9 | 16.1975 | 3034.4 | 7.209 | 3036.6 | 1.7103 | 3038.9 | 7.3713 | 3016.5 | 1.7103
3058.5 | 1.4381 |  | 3067.5 | 1.8274 | 3073 | 0.10665 | 3076.4 | 0.49439 | 3078.7 | 1.6325 | 3080.9 | 10.9842 | 3058.5 | 0.10665
3100.3 | 3.2067 |  | 3109.4 | 7.7254 | 3114.9 | 1.406 | 3118.3 | 11.2627 | 3120.5 | 0.68679 | 3122.8 | 0.69143 | 3100.3 | 0.68679
3142.5 | 1.796 |  | 3151.4 | 10.0039 | 3156.9 | 3.6565 | 3160.3 | 5.3406 | 3162.6 | 1.4954 | 3164.7 | 5.2012 | 3142.5 | 1.4954
3184.4 | 5.2447 |  | 3193.3 | 5.5404 | 3199 | 1.6029 | 3202.4 | 5.5068 | 3204.7 | 4.332 | 3206.8 | 8.9555 | 3184.4 | 1.6029
3226.4 | 8.2817 |  | 3235.4 | 7.0551 | 3240.9 | 0.70452 | 3244.5 | 0.75868 | 3246.7 | 7.6502 | 3248.9 | 0.68881 | 3226.4 | 0.68881
3268.3 | 6.1486 |  | 3277.4 | 5.1919 | 3282.9 | 0.70634 | 3286.3 | 7.8813 | 3288.5 | 0.69289 | 3290.8 | 0.69056 | 3268.3 | 0.69056

## TempPlot
Data truncated: "Cable 4" T/C failure (due to interaction with Cable A?)

## C5-C6
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 146.6044 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38960.3532 | 1 | 0 | 38960.3532 | 1 | 0 |  | -99.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3537 | 1 | 0 | 38960.3537 | 1 | 0 |  | -57.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3542 | 1 | 0 | 38960.3542 | 2 | 0 |  | -15.5 | 123.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 240038 | 119969 | 240037.9994
38960.3547 | 1 | 0 | 38960.3547 | 1 | 0 |  | 26.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3551 | 1 | 0 | 38960.3552 | 1 | 0 |  | 68.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3556 | 1 | 0 | 38960.3556 | 1 | 0 |  | 110.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3561 | 2 | 0 | 38960.3561 | 1 | 0 |  | 152.5 | 291.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119969 | 240038 | 119968.9988
38960.3566 | 1 | 0 | 38960.3566 | 1 | 0 |  | 194.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3571 | 1 | 0 | 38960.3571 | 1 | 0 |  | 236.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3576 | 1 | 0 | 38960.3576 | 1 | 0 |  | 278.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3581 | 1 | 0 | 38960.3581 | 1 | 0 |  | 320.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3585 | 1 | 0 | 38960.3586 | 1 | 0 |  | 362.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.359 | 1 | 0 | 38960.359 | 1 | 0 |  | 404.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3595 | 1 | 0 | 38960.3595 | 1 | 0 |  | 446.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.36 | 1 | 0 | 38960.36 | 1 | 0 |  | 488.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3605 | 1 | 0 | 38960.3605 | 1 | 0 |  | 530.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.361 | 1 | 0 | 38960.361 | 1 | 0 |  | 572.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3615 | 1 | 0 | 38960.3615 | 1 | 0 |  | 614.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3619 | 1 | 0 | 38960.362 | 1 | 0 |  | 656.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3624 | 1 | 0 | 38960.3624 | 1 | 0 |  | 698.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3629 | 1 | 0 | 38960.3629 | 1 | 0 |  | 740.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3634 | 1 | 0 | 38960.3634 | 1 | 0 |  | 782.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3639 | 1 | 0 | 38960.3639 | 1 | 0 |  | 824.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3644 | 1 | 0 | 38960.3644 | 1 | 0 |  | 866.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3649 | 1 | 0 | 38960.3649 | 1 | 0 |  | 908.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3653 | 1 | 0 | 38960.3654 | 1 | 0 |  | 950.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3658 | 1 | 0 | 38960.3658 | 1 | 0 |  | 992.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3663 | 1 | 0 | 38960.3663 | 1 | 0 |  | 1034.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3668 | 1 | 0 | 38960.3668 | 1 | 0 |  | 1076.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3673 | 1 | 0 | 38960.3673 | 1 | 0 |  | 1118.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3678 | 1 | 0 | 38960.3678 | 1 | 0 |  | 1160.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3683 | 1 | 0 | 38960.3683 | 1 | 0 |  | 1202.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3688 | 1 | 0 | 38960.3688 | 1 | 0 |  | 1244.5 | 1383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3692 | 1 | 1 | 38960.3692 | 1 | 0 |  | 1286.5 | 1425.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 576182414.44 | 240038 | 239838.0833
38960.3697 | 1 | 0 | 38960.3697 | 1 | 0 |  | 1328.5 | 1467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3702 | 1 | 0 | 38960.3702 | 1 | 0 |  | 1370.5 | 1509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3707 | 1 | 0 | 38960.3707 | 1 | 0 |  | 1412.5 | 1551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
| 1 | 0 | 38960.3712 | 1 | 0 |  | 1455 | 1594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3717 | 1 | 0 | 38960.3717 | 1 | 0 |  | 1496.5 | 1635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3722 | 1 | 0 | 38960.3722 | 1 | 0 |  | 1538.5 | 1677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3726 | 1 | 0 | 38960.3727 | 1 | 0 |  | 1580.5 | 1719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3731 | 1 | 0 | 38960.3731 | 1 | 0 |  | 1622.5 | 1761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3736 | 1 | 0 | 38960.3736 | 1 | 0 |  | 1664.5 | 1803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3741 | 1 | 0 | 38960.3741 | 1 | 0 |  | 1706.5 | 1845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3746 | 1 | 0 | 38960.3746 | 1 | 0 |  | 1748.5 | 1887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3751 | 1 | 0 | 38960.3751 | 1 | 0 |  | 1790.5 | 1929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3756 | 1 | 0 | 38960.3756 | 1 | 0 |  | 1832.5 | 1971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.376 | 1 | 0 | 38960.3761 | 1 | 0 |  | 1874 | 2013 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38960.3765 | 216 | 1 | 38960.3765 | 1 | 0 |  | 1916.5 | 2055.5 | 13.1868 | 0.06105 | 0.06105 | 0 | 0.13187 | 0.0006105 | 0.0006105 | 0 | 0.13126 | 0.0006105 | 1016.4578 | 240038 | 218347.0365
38960.377 | 39 | 1 | 38960.377 | 1 | 0 |  | 1958 | 2097 | 2.381 | 0.06105 | 0.06105 | 0 | 0.02381 | 0.0006105 | 0.0006105 | 0 | 0.023199 | 0.0006105 | 6216.8576 | 240038 | 236039.6657
38960.3775 | 1104 | 1 | 38960.3775 | 2 | 0 |  | 2000.5 | 2139.5 | 67.3993 | 0.06105 | 0.1221 | 0 | 0.67399 | 0.0006105 | 0.001221 | 0 | 0.67338 | 0.001221 | 117.6229 | 119969 | 129530.0304
38960.378 | 2047 | 1 | 38960.378 | 2 | 0 |  | 2042 | 2181 | 124.9695 | 0.06105 | 0.1221 | 0 | 1.2497 | 0.0006105 | 0.001221 | 0 | 1.2491 | 0.001221 | 17.3206 | 119969 | 35308.5686
38960.3785 | 2034 | 0 | 38960.3785 | 270 | 0 |  | 2084.5 | 2223.5 | 124.1758 | 0 | 16.4835 | 0 | 1.2418 | 0 | 0.16484 | 0 | 1.2418 | 0.16484 | 18.0619 | 789.4 | 16.8202
38960.3789 | 2132 | 0 | 38960.379 | 1096 | 0 |  | 2126 | 2265 | 130.1587 | 0 | 66.9109 | 0 | 1.3016 | 0 | 0.66911 | 0 | 1.3016 | 0.66911 | 12.6351 | 119.104 | 11.3335
38960.3794 | 2243 | 0 | 38960.3795 | 593 | 0 |  | 2168 | 2307 | 136.9353 | 0 | 36.2027 | 0 | 1.3694 | 0 | 0.36203 | 0 | 1.3694 | 0.36203 | 7.0611 | 304.9545 | 5.6917
38960.3799 | 1804 | 0 | 38960.3799 | 740 | 0 |  | 2210 | 2349 | 110.1343 | 0 | 45.177 | 0 | 1.1013 | 0 | 0.45177 | 0 | 1.1013 | 0.45177 | 33.1142 | 224.5108 | 32.0128
38960.3804 | 2292 | 0 | 38960.3804 | 1096 | 0 |  | 2252 | 2391 | 139.9267 | 0 | 66.9109 | 0 | 1.3993 | 0 | 0.66911 | 0 | 1.3993 | 0.66911 | 4.7723 | 119.104 | 3.373
38960.3809 | 2065 | 0 | 38960.3809 | 1074 | 0 |  | 2294 | 2433 | 126.0684 | 0 | 65.5678 | 0 | 1.2607 | 0 | 0.65568 | 0 | 1.2607 | 0.65568 | 16.2896 | 123.5922 | 15.0289
38960.3814 | 2200 | 0 | 38960.3814 | 888 | 0 |  | 2336 | 2475 | 134.3101 | 0 | 54.2125 | 0 | 1.3431 | 0 | 0.54212 | 0 | 1.3431 | 0.54212 | 9.1536 | 170.4257 | 7.8105
38960.3819 | 2264 | 0 | 38960.3819 | 2043 | 0 |  | 2378 | 2517 | 138.2173 | 0 | 124.7253 | 0 | 1.3822 | 0 | 1.2473 | 0 | 1.3822 | 1.2473 | 6.068 | 17.5419 | 4.6858
38960.3823 | 2093 | 0 | 38960.3824 | 1962 | 0 |  | 2420 | 2559 | 127.7778 | 0 | 119.7802 | 0 | 1.2778 | 0 | 1.1978 | 0 | 1.2778 | 1.1978 | 14.7339 | 22.3945 | 13.4561
38960.3828 | 2308 | 0 | 38960.3829 | 1841 | 0 |  | 2462 | 2601 | 140.9035 | 0 | 112.3932 | 0 | 1.409 | 0 | 1.1239 | 0 | 1.409 | 1.1239 | 4.0459 | 30.4389 | 2.6369
38960.3833 | 2332 | 0 | 38960.3833 | 2021 | 0 |  | 2504 | 2643 | 142.3687 | 0 | 123.3822 | 0 | 1.4237 | 0 | 1.2338 | 0 | 1.4237 | 1.2338 | 2.9751 | 18.8214 | 1.5514
38960.3838 | 2041 | 0 | 38960.3838 | 2224 | 0 |  | 2546 | 2685 | 124.6032 | 0 | 135.7753 | 0 | 1.246 | 0 | 1.3578 | 0 | 1.246 | 1.3578 | 17.657 | 7.9757 | 16.411
38960.3843 | 1930 | 0 | 38960.3843 | 1897 | 0 |  | 2588 | 2727 | 117.8266 | 0 | 115.812 | 0 | 1.1783 | 0 | 1.1581 | 0 | 1.1783 | 1.1581 | 24.4238 | 26.5883 | 23.2456
38960.3848 | 2341 | 0 | 38960.3848 | 2143 | 0 |  | 2630 | 2769 | 142.9182 | 0 | 130.8303 | 0 | 1.4292 | 0 | 1.3083 | 0 | 1.4292 | 1.3083 | 2.5792 | 12.0569 | 1.1501
38960.3853 | 2262 | 0 | 38960.3853 | 2012 | 0 |  | 2672 | 2811 | 138.0952 | 0 | 122.8327 | 0 | 1.381 | 0 | 1.2283 | 0 | 1.381 | 1.2283 | 6.1618 | 19.3529 | 4.7809
38960.3858 | 1848 | 0 | 38960.3858 | 1826 | 0 |  | 2714 | 2853 | 112.8205 | 0 | 111.4774 | 0 | 1.1282 | 0 | 1.1148 | 0 | 1.1282 | 1.1148 | 29.9448 | 31.5104 | 28.8166
38960.3862 | 2181 | 0 | 38960.3863 | 1944 | 0 |  | 2756 | 2895 | 133.1502 | 0 | 118.6813 | 0 | 1.3315 | 0 | 1.1868 | 0 | 1.3315 | 1.1868 | 10.1045 | 23.5278 | 8.773
38960.3867 | 2276 | 0 | 38960.3867 | 2176 | 0 |  | 2798 | 2937 | 138.9499 | 0 | 132.8449 | 0 | 1.3895 | 0 | 1.3284 | 0 | 1.3895 | 1.3284 | 5.5088 | 10.3575 | 4.1193
38960.3872 | 1928 | 0 | 38960.3872 | 2068 | 0 |  | 2840 | 2979 | 117.7045 | 0 | 126.2515 | 0 | 1.177 | 0 | 1.2625 | 0 | 1.177 | 1.2625 | 24.5529 | 16.1209 | 23.3759
38960.3877 | 2158 | 0 | 38960.3877 | 2276 | 0 |  | 2882 | 3021 | 131.746 | 0 | 138.9499 | 0 | 1.3175 | 0 | 1.3895 | 0 | 1.3175 | 1.3895 | 11.278 | 5.5088 | 9.9606
38960.3882 | 1839 | 0 | 38960.3882 | 2132 | 0 |  | 2924 | 3063 | 112.2711 | 0 | 130.1587 | 0 | 1.1227 | 0 | 1.3016 | 0 | 1.1227 | 1.3016 | 30.5808 | 12.6351 | 29.458
38960.3887 | 1851 | 0 | 38960.3887 | 2140 | 0 |  | 2966 | 3105 | 113.0037 | 0 | 130.6471 | 0 | 1.13 | 0 | 1.3065 | 0 | 1.13 | 1.3065 | 29.7342 | 12.214 | 28.6042
38960.3892 | 2119 | 0 | 38960.3892 | 1972 | 0 |  | 3008 | 3147 | 129.3651 | 0 | 120.3907 | 0 | 1.2937 | 0 | 1.2039 | 0 | 1.2937 | 1.2039 | 13.3261 | 21.7738 | 12.0324
38960.3896 | 2361 | 0 | 38960.3897 | 2085 | 0 |  | 3050 | 3189 | 144.1392 | 0 | 127.2894 | 0 | 1.4414 | 0 | 1.2729 | 0 | 1.4414 | 1.2729 | 1.7103 | 15.1741 | 0.2689
38960.3901 | 1926 | 0 | 38960.3902 | 2067 | 0 |  | 3092 | 3231 | 117.5824 | 0 | 126.1905 | 0 | 1.1758 | 0 | 1.2619 | 0 | 1.1758 | 1.2619 | 24.6822 | 16.1771 | 23.5064
38960.3906 | 2385 | 0 | 38960.3906 | 1850 | 0 |  | 3134 | 3273 | 145.6044 | 0 | 112.9426 | 0 | 1.456 | 0 | 1.1294 | 0 | 1.456 | 1.1294 | 0.68679 | 29.8043 | 0.76925
38960.3911 | 2366 | 0 | 38960.3911 | 2239 | 0 |  | 3176 | 3315 | 144.4444 | 0 | 136.6911 | 0 | 1.4444 | 0 | 1.3669 | 0 | 1.4444 | 1.3669 | 1.4954 | 7.2523 | 0.050906
38960.3916 | 2222 | 0 | 38960.3916 | 2204 | 0 |  | 3218 | 3357 | 135.6532 | 0 | 134.5543 | 0 | 1.3565 | 0 | 1.3455 | 0 | 1.3565 | 1.3455 | 8.0729 | 8.9555 | 6.7164
38960.3921 | 2202 | 0 | 38960.3921 | 2043 | 0 |  | 3260 | 3399 | 134.4322 | 0 | 124.7253 | 0 | 1.3443 | 0 | 1.2473 | 0 | 1.3443 | 1.2473 | 9.0545 | 17.5419 | 7.7102
38960.3926 | 2293 | 0 | 38960.3926 | 1999 | 0 |  | 3302 | 3441 | 139.9878 | 0 | 122.0391 | 0 | 1.3999 | 0 | 1.2204 | 0 | 1.3999 | 1.2204 | 4.7266 | 20.1291 | 3.3267

## B4-C6
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 143.5519 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38960.3532 | 1 | 0 | 38960.3532 | 1 | 0 |  | -102.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3536 | 1 | 0 | 38960.3537 | 1 | 0 |  | -60.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3541 | 1 | 0 | 38960.3541 | 1 | 0 |  | -18.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3546 | 1 | 0 | 38960.3546 | 1 | 0 |  | 23.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3551 | 1 | 0 | 38960.3551 | 1 | 0 |  | 65.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3556 | 1 | 0 | 38960.3556 | 1 | 0 |  | 107.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3561 | 1 | 0 | 38960.3561 | 1 | 0 |  | 149.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3566 | 1 | 0 | 38960.3566 | 1 | 0 |  | 191.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.357 | 1 | 0 | 38960.3571 | 1 | 0 |  | 233.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3575 | 1 | 0 | 38960.3575 | 1 | 0 |  | 275.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.358 | 1 | 0 | 38960.358 | 1 | 0 |  | 317.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3585 | 1 | 0 | 38960.3585 | 2 | 0 |  | 359.5 | 498.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235038 | 117469 | 235037.9994
38960.359 | 1 | 0 | 38960.359 | 1 | 0 |  | 401.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3595 | 1 | 0 | 38960.3595 | 1 | 0 |  | 443.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.36 | 1 | 0 | 38960.36 | 1 | 0 |  | 485.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3605 | 1 | 0 | 38960.3605 | 1 | 0 |  | 527.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3609 | 1 | 0 | 38960.3609 | 1 | 0 |  | 569.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3614 | 1 | 0 | 38960.3614 | 2 | 0 |  | 611.5 | 750.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235038 | 117469 | 235037.9994
38960.3619 | 1 | 0 | 38960.3619 | 1 | 0 |  | 653.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3624 | 1 | 0 | 38960.3624 | 1 | 0 |  | 695.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3629 | 1 | 0 | 38960.3629 | 1 | 0 |  | 737.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3634 | 1 | 0 | 38960.3634 | 1 | 0 |  | 779.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3639 | 1 | 0 | 38960.3639 | 1 | 0 |  | 821.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3643 | 1 | 0 | 38960.3644 | 1 | 0 |  | 863.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3648 | 1 | 0 | 38960.3648 | 1 | 0 |  | 905.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3653 | 1 | 0 | 38960.3653 | 1 | 0 |  | 947.5 | 1086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3658 | 1 | 0 | 38960.3658 | 1 | 0 |  | 989.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3663 | 1 | 0 | 38960.3663 | 1 | 0 |  | 1031.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3668 | 1 | 0 | 38960.3668 | 1 | 0 |  | 1073.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3673 | 1 | 0 | 38960.3673 | 1 | 0 |  | 1115.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3677 | 1 | 1 | 38960.3678 | 1 | 0 |  | 1157.5 | 1296.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 552428614.44 | 235038 | 234838.0851
38960.3682 | 1 | 0 | 38960.3682 | 1 | 0 |  | 1199.5 | 1338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3687 | 1 | 0 | 38960.3687 | 1 | 0 |  | 1241.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3692 | 1 | 0 | 38960.3692 | 1 | 0 |  | 1283.5 | 1422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3697 | 1 | 0 | 38960.3697 | 1 | 0 |  | 1325.5 | 1464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3702 | 1 | 0 | 38960.3702 | 1 | 0 |  | 1367.5 | 1506.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3707 | 1 | 0 | 38960.3707 | 1 | 0 |  | 1409.5 | 1548.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3711 | 1 | 0 | 38960.3712 | 1 | 0 |  | 1451.5 | 1590.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3716 | 1 | 0 | 38960.3716 | 1 | 0 |  | 1493.5 | 1632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3721 | 1 | 0 | 38960.3721 | 1 | 0 |  | 1535.5 | 1674.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3726 | 1 | 0 | 38960.3726 | 1 | 0 |  | 1577.5 | 1716.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3731 | 1 | 0 | 38960.3731 | 1 | 0 |  | 1619.5 | 1758.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3736 | 1 | 0 | 38960.3736 | 1 | 0 |  | 1661.5 | 1800.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3741 | 1 | 0 | 38960.3741 | 1 | 0 |  | 1703.5 | 1842.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3745 | 1 | 0 | 38960.3746 | 1 | 0 |  | 1745.5 | 1884.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.375 | 1 | 0 | 38960.375 | 1 | 0 |  | 1787.5 | 1926.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3755 | 1 | 0 | 38960.3755 | 1 | 0 |  | 1829.5 | 1968.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.376 | 1 | 0 | 38960.376 | 1 | 0 |  | 1871.5 | 2010.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3765 | 1 | 0 | 38960.3765 | 1 | 0 |  | 1913.5 | 2052.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.377 | 1 | 0 | 38960.377 | 1 | 0 |  | 1955.5 | 2094.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.3775 | 1 | 0 | 38960.3775 | 1 | 0 |  | 1997.5 | 2136.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235038 | 235038 | 235037.9994
38960.378 | 2 | 0 | 38960.378 | 1 | 0 |  | 2039.5 | 2178.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117469 | 235038 | 117468.9988
38960.3784 | 2 | 0 | 38960.3784 | 2 | 0 |  | 2081.5 | 2220.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117469 | 117469 | 117468.9988
38960.3789 | 2 | 0 | 38960.3789 | 718 | 0 |  | 2123.5 | 2262.5 | 0.1221 | 0 | 43.8339 | 0 | 0.001221 | 0 | 0.43834 | 0 | 0.001221 | 0.43834 | 117469 | 227.4903 | 117468.9988
38960.3794 | 2 | 0 | 38960.3794 | 1283 | 0 |  | 2165.5 | 2304.5 | 0.1221 | 0 | 78.3272 | 0 | 0.001221 | 0 | 0.78327 | 0 | 0.001221 | 0.78327 | 117469 | 83.272 | 117468.9988
38960.3799 | 3 | 0 | 38960.3799 | 601 | 0 |  | 2207.5 | 2346.5 | 0.18315 | 0 | 36.6911 | 0 | 0.0018315 | 0 | 0.36691 | 0 | 0.0018315 | 0.36691 | 78279.3333 | 291.2446 | 78279.3315
38960.3804 | 2 | 0 | 38960.3804 | 812 | 0 |  | 2249.5 | 2388.5 | 0.1221 | 0 | 49.5726 | 0 | 0.001221 | 0 | 0.49573 | 0 | 0.001221 | 0.49573 | 117469 | 189.5788 | 117468.9988
38960.3809 | 2 | 0 | 38960.3809 | 967 | 0 |  | 2291.5 | 2430.5 | 0.1221 | 0 | 59.0354 | 0 | 0.001221 | 0 | 0.59035 | 0 | 0.001221 | 0.59035 | 117469 | 143.1624 | 117468.9988
38960.3814 | 2 | 0 | 38960.3814 | 505 | 0 |  | 2333.5 | 2472.5 | 0.1221 | 0 | 30.8303 | 0 | 0.001221 | 0 | 0.3083 | 0 | 0.001221 | 0.3083 | 117469 | 365.6198 | 117468.9988
38960.3818 | 2 | 0 | 38960.3819 | 1872 | 0 |  | 2375.5 | 2514.5 | 0.1221 | 0 | 114.2857 | 0 | 0.001221 | 0 | 1.1429 | 0 | 0.001221 | 1.1429 | 117469 | 25.6079 | 117468.9988
38960.3823 | 2 | 0 | 38960.3823 | 2070 | 0 |  | 2417.5 | 2556.5 | 0.1221 | 0 | 126.3736 | 0 | 0.001221 | 0 | 1.2637 | 0 | 0.001221 | 1.2637 | 117469 | 13.5932 | 117468.9988
38960.3828 | 2 | 0 | 38960.3828 | 2043 | 0 |  | 2459.5 | 2598.5 | 0.1221 | 0 | 124.7253 | 0 | 0.001221 | 0 | 1.2473 | 0 | 0.001221 | 1.2473 | 117469 | 15.0945 | 117468.9988
38960.3833 | 2 | 0 | 38960.3833 | 2303 | 0 |  | 2501.5 | 2640.5 | 0.1221 | 0 | 140.5983 | 0 | 0.001221 | 0 | 1.406 | 0 | 0.001221 | 1.406 | 117469 | 2.1007 | 117468.9988
38960.3838 | 2 | 0 | 38960.3838 | 1903 | 0 |  | 2543.5 | 2682.5 | 0.1221 | 0 | 116.1783 | 0 | 0.001221 | 0 | 1.1618 | 0 | 0.001221 | 1.1618 | 117469 | 23.5617 | 117468.9988
38960.3843 | 2 | 0 | 38960.3843 | 2074 | 0 |  | 2585.5 | 2724.5 | 0.1221 | 0 | 126.6178 | 0 | 0.001221 | 0 | 1.2662 | 0 | 0.001221 | 1.2662 | 117469 | 13.3742 | 117468.9988
38960.3848 | 2 | 0 | 38960.3848 | 1862 | 0 |  | 2627.5 | 2766.5 | 0.1221 | 0 | 113.6752 | 0 | 0.001221 | 0 | 1.1368 | 0 | 0.001221 | 1.1368 | 117469 | 26.2825 | 117468.9988
38960.3852 | 3 | 0 | 38960.3853 | 2246 | 0 |  | 2669.5 | 2808.5 | 0.18315 | 0 | 137.1184 | 0 | 0.0018315 | 0 | 1.3712 | 0 | 0.0018315 | 1.3712 | 78279.3333 | 4.6919 | 78279.3315
38960.3857 | 315 | 0 | 38960.3857 | 2335 | 0 |  | 2711.5 | 2850.5 | 19.2308 | 0 | 142.5519 | 0 | 0.19231 | 0 | 1.4255 | 0 | 0.19231 | 1.4255 | 646.4698 | 0.7015 | 646.2775
38960.3862 | 228 | 0 | 38960.3862 | 2227 | 0 |  | 2753.5 | 2892.5 | 13.9194 | 0 | 135.9585 | 0 | 0.13919 | 0 | 1.3596 | 0 | 0.13919 | 1.3596 | 931.307 | 5.5851 | 931.1678
38960.3867 | 1903 | 0 | 38960.3867 | 2060 | 0 |  | 2795.5 | 2934.5 | 116.1783 | 0 | 125.7631 | 0 | 1.1618 | 0 | 1.2576 | 0 | 1.1618 | 1.2576 | 23.5617 | 14.1447 | 22.4
38960.3872 | 1676 | 0 | 38960.3872 | 2080 | 0 |  | 2837.5 | 2976.5 | 102.3199 | 0 | 126.9841 | 0 | 1.0232 | 0 | 1.2698 | 0 | 1.0232 | 1.2698 | 40.2971 | 13.0471 | 39.2739
38960.3877 | 1912 | 0 | 38960.3877 | 1977 | 0 |  | 2879.5 | 3018.5 | 116.7277 | 0 | 120.696 | 0 | 1.1673 | 0 | 1.207 | 0 | 1.1673 | 1.207 | 22.9801 | 18.9368 | 21.8128
38960.3882 | 1665 | 0 | 38960.3882 | 1852 | 0 |  | 2921.5 | 3060.5 | 101.6484 | 0 | 113.0647 | 0 | 1.0165 | 0 | 1.1306 | 0 | 1.0165 | 1.1306 | 41.224 | 26.9644 | 40.2075
38960.3886 | 1965 | 0 | 38960.3887 | 2260 | 0 |  | 2963.5 | 3102.5 | 119.9634 | 0 | 137.9731 | 0 | 1.1996 | 0 | 1.3797 | 0 | 1.1996 | 1.3797 | 19.6631 | 4.0434 | 18.4635
38960.3891 | 1997 | 0 | 38960.3891 | 2308 | 0 |  | 3005.5 | 3144.5 | 121.917 | 0 | 140.9035 | 0 | 1.2192 | 0 | 1.409 | 0 | 1.2192 | 1.409 | 17.7456 | 1.8795 | 16.5264
38960.3896 | 1794 | 0 | 38960.3896 | 1836 | 0 |  | 3047.5 | 3186.5 | 109.5238 | 0 | 112.0879 | 0 | 1.0952 | 0 | 1.1209 | 0 | 1.0952 | 1.1209 | 31.0691 | 28.0708 | 29.9739
38960.3901 | 1717 | 0 | 38960.3901 | 2011 | 0 |  | 3089.5 | 3228.5 | 104.823 | 0 | 122.7717 | 0 | 1.0482 | 0 | 1.2277 | 0 | 1.0482 | 1.2277 | 36.947 | 16.9259 | 35.8988
38960.3906 | 1995 | 0 | 38960.3906 | 1977 | 0 |  | 3131 | 3270 | 121.7949 | 0 | 120.696 | 0 | 1.2179 | 0 | 1.207 | 0 | 1.2179 | 1.207 | 17.8637 | 18.9368 | 16.6457
38960.3911 | 1735 | 0 | 38960.3911 | 2106 | 0 |  | 3173 | 3312 | 105.9219 | 0 | 128.5714 | 0 | 1.0592 | 0 | 1.2857 | 0 | 1.0592 | 1.2857 | 35.5262 | 11.6515 | 34.467
38960.3916 | 2166 | 0 | 38960.3916 | 1979 | 0 |  | 3215.5 | 3354.5 | 132.2344 | 0 | 120.8181 | 0 | 1.3223 | 0 | 1.2082 | 0 | 1.3223 | 1.2082 | 8.5586 | 18.8166 | 7.2363
38960.392 | 1852 | 0 | 38960.3921 | 1916 | 0 |  | 3257.5 | 3396.5 | 113.0647 | 0 | 116.9719 | 0 | 1.1306 | 0 | 1.1697 | 0 | 1.1306 | 1.1697 | 26.9644 | 22.7234 | 25.8337
38960.3925 | 1956 | 0 | 38960.3925 | 2225 | 0 |  | 3299 | 3438 | 119.4139 | 0 | 135.8364 | 0 | 1.1941 | 0 | 1.3584 | 0 | 1.1941 | 1.3584 | 20.2137 | 5.68 | 19.0196

## B4-C5
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 144.2845 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38960.3531 | 1 | 0 | 38960.3531 | 1 | 0 |  | -105 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3536 | 1 | 0 | 38960.3536 | 1 | 0 |  | -63 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3541 | 1 | 0 | 38960.3541 | 1 | 0 |  | -21 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3546 | 1 | 0 | 38960.3546 | 1 | 0 |  | 21 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3551 | 2 | 0 | 38960.3551 | 1 | 0 |  | 63 | 202 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118069 | 236238 | 118068.9988
38960.3556 | 1 | 0 | 38960.3556 | 1 | 0 |  | 105 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.356 | 1 | 0 | 38960.3561 | 1 | 0 |  | 147 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3565 | 2 | 0 | 38960.3566 | 1 | 0 |  | 189 | 328 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118069 | 236238 | 118068.9988
38960.357 | 1 | 0 | 38960.357 | 1 | 0 |  | 231 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3575 | 1 | 0 | 38960.3575 | 1 | 0 |  | 273 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.358 | 1 | 0 | 38960.358 | 1 | 0 |  | 315 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3585 | 1 | 0 | 38960.3585 | 1 | 0 |  | 357 | 496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.359 | 1 | 0 | 38960.359 | 1 | 0 |  | 399 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3594 | 1 | 0 | 38960.3595 | 1 | 0 |  | 440.5 | 579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3599 | 1 | 0 | 38960.3599 | 1 | 0 |  | 482.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3604 | 1 | 0 | 38960.3604 | 1 | 0 |  | 525 | 664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3609 | 1 | 0 | 38960.3609 | 1 | 0 |  | 566.5 | 705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3614 | 1 | 0 | 38960.3614 | 1 | 0 |  | 609 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3619 | 1 | 0 | 38960.3619 | 1 | 0 |  | 650.5 | 789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3624 | 1 | 0 | 38960.3624 | 1 | 0 |  | 692.5 | 831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3628 | 1 | 0 | 38960.3629 | 1 | 0 |  | 735 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3633 | 1 | 0 | 38960.3634 | 1 | 0 |  | 777 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3638 | 1 | 0 | 38960.3638 | 1 | 0 |  | 818.5 | 957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3643 | 1 | 0 | 38960.3643 | 1 | 0 |  | 861 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3648 | 1 | 0 | 38960.3648 | 1 | 0 |  | 902.5 | 1041.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3653 | 1 | 0 | 38960.3653 | 1 | 0 |  | 945 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3658 | 1 | 0 | 38960.3658 | 1 | 0 |  | 986.5 | 1125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3662 | 1 | 0 | 38960.3663 | 1 | 0 |  | 1028.5 | 1167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3667 | 1 | 0 | 38960.3667 | 1 | 0 |  | 1070.5 | 1209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3672 | 1 | 0 | 38960.3672 | 1 | 0 |  | 1113 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3677 | 1 | 0 | 38960.3677 | 1 | 0 |  | 1154.5 | 1293.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3682 | 1 | 0 | 38960.3682 | 1 | 0 |  | 1196.5 | 1335.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3687 | 1 | 0 | 38960.3687 | 1 | 0 |  | 1238.5 | 1377.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3692 | 1 | 0 | 38960.3692 | 1 | 0 |  | 1280.5 | 1419.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3697 | 1 | 0 | 38960.3697 | 1 | 0 |  | 1322.5 | 1461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3701 | 1 | 0 | 38960.3702 | 1 | 0 |  | 1364.5 | 1503.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3706 | 1 | 0 | 38960.3706 | 1 | 0 |  | 1406.5 | 1545.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3711 | 1 | 0 | 38960.3711 | 1 | 0 |  | 1448.5 | 1587.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3716 | 1 | 0 | 38960.3716 | 1 | 0 |  | 1490.5 | 1629.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3721 | 1 | 0 | 38960.3721 | 1 | 0 |  | 1532.5 | 1671.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3726 | 1 | 0 | 38960.3726 | 1 | 0 |  | 1574.5 | 1713.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3731 | 1 | 0 | 38960.3731 | 1 | 0 |  | 1616.5 | 1755.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3735 | 1 | 0 | 38960.3736 | 1 | 0 |  | 1658.5 | 1797.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.374 | 1 | 0 | 38960.374 | 1 | 0 |  | 1700.5 | 1839.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3745 | 1 | 0 | 38960.3745 | 1 | 0 |  | 1742.5 | 1881.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.375 | 1 | 0 | 38960.375 | 1 | 0 |  | 1784.5 | 1923.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3755 | 1 | 0 | 38960.3755 | 1 | 0 |  | 1826.5 | 1965.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.376 | 1 | 0 | 38960.376 | 1 | 0 |  | 1868.5 | 2007.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38960.3765 | 1 | 0 | 38960.3765 | 206 | 0 |  | 1910.5 | 2049.5 | 0.06105 | 0 | 12.5763 | 0 | 0.0006105 | 0 | 0.12576 | 0 | 0.0006105 | 0.12576 | 236238 | 1047.2718 | 236237.9994
38960.3769 | 1 | 0 | 38960.377 | 5 | 0 |  | 1952.5 | 2091.5 | 0.06105 | 0 | 0.30525 | 0 | 0.0006105 | 0 | 0.0030525 | 0 | 0.0006105 | 0.0030525 | 236238 | 47167.6 | 236237.9994
38960.3774 | 1 | 0 | 38960.3774 | 487 | 0 |  | 1994.5 | 2133.5 | 0.06105 | 0 | 29.7314 | 0 | 0.0006105 | 0 | 0.29731 | 0 | 0.0006105 | 0.29731 | 236238 | 385.2936 | 236237.9994
38960.3779 | 1 | 0 | 38960.3779 | 1804 | 0 |  | 2036.5 | 2175.5 | 0.06105 | 0 | 110.1343 | 0 | 0.0006105 | 0 | 1.1013 | 0 | 0.0006105 | 1.1013 | 236238 | 31.0078 | 236237.9994
38960.3784 | 1 | 0 | 38960.3784 | 2196 | 0 |  | 2078.5 | 2217.5 | 0.06105 | 0 | 134.0659 | 0 | 0.0006105 | 0 | 1.3407 | 0 | 0.0006105 | 1.3407 | 236238 | 7.622 | 236237.9994
38960.3789 | 1 | 0 | 38960.3789 | 1934 | 0 |  | 2120.5 | 2259.5 | 0.06105 | 0 | 118.0708 | 0 | 0.0006105 | 0 | 1.1807 | 0 | 0.0006105 | 1.1807 | 236238 | 22.2017 | 236237.9994
38960.3794 | 2 | 0 | 38960.3794 | 2292 | 0 |  | 2162.5 | 2301.5 | 0.1221 | 0 | 139.9267 | 0 | 0.001221 | 0 | 1.3993 | 0 | 0.001221 | 1.3993 | 118069 | 3.1143 | 118068.9988
38960.3799 | 2 | 0 | 38960.3799 | 2252 | 0 |  | 2204.5 | 2343.5 | 0.1221 | 0 | 137.4847 | 0 | 0.001221 | 0 | 1.3748 | 0 | 0.001221 | 1.3748 | 118069 | 4.9458 | 118068.9988
38960.3803 | 2 | 0 | 38960.3804 | 2311 | 0 |  | 2246.5 | 2385.5 | 0.1221 | 0 | 141.0867 | 0 | 0.001221 | 0 | 1.4109 | 0 | 0.001221 | 1.4109 | 118069 | 2.2666 | 118068.9988
38960.3808 | 2 | 0 | 38960.3808 | 1939 | 0 |  | 2288.5 | 2427.5 | 0.1221 | 0 | 118.3761 | 0 | 0.001221 | 0 | 1.1838 | 0 | 0.001221 | 1.1838 | 118069 | 21.8865 | 118068.9988
38960.3813 | 2 | 0 | 38960.3813 | 2002 | 0 |  | 2330.5 | 2469.5 | 0.1221 | 0 | 122.2222 | 0 | 0.001221 | 0 | 1.2222 | 0 | 0.001221 | 1.2222 | 118069 | 18.0509 | 118068.9988
38960.3818 | 2 | 0 | 38960.3818 | 2089 | 0 |  | 2372.5 | 2511.5 | 0.1221 | 0 | 127.5336 | 0 | 0.001221 | 0 | 1.2753 | 0 | 0.001221 | 1.2753 | 118069 | 13.1345 | 118068.9988
38960.3823 | 2 | 0 | 38960.3823 | 1970 | 0 |  | 2414.5 | 2553.5 | 0.1221 | 0 | 120.2686 | 0 | 0.001221 | 0 | 1.2027 | 0 | 0.001221 | 1.2027 | 118069 | 19.9685 | 118068.9988
38960.3828 | 2 | 0 | 38960.3828 | 2113 | 0 |  | 2456.5 | 2595.5 | 0.1221 | 0 | 128.9988 | 0 | 0.001221 | 0 | 1.29 | 0 | 0.001221 | 1.29 | 118069 | 11.8495 | 118068.9988
38960.3833 | 2 | 0 | 38960.3833 | 1908 | 0 |  | 2498.5 | 2637.5 | 0.1221 | 0 | 116.4835 | 0 | 0.001221 | 0 | 1.1648 | 0 | 0.001221 | 1.1648 | 118069 | 23.8669 | 118068.9988
38960.3838 | 2 | 0 | 38960.3838 | 2347 | 0 |  | 2540.5 | 2679.5 | 0.1221 | 0 | 143.2845 | 0 | 0.001221 | 0 | 1.4328 | 0 | 0.001221 | 1.4328 | 118069 | 0.69791 | 118068.9988
38960.3842 | 2 | 0 | 38960.3842 | 1870 | 0 |  | 2582.5 | 2721.5 | 0.1221 | 0 | 114.1636 | 0 | 0.001221 | 0 | 1.1416 | 0 | 0.001221 | 1.1416 | 118069 | 26.384 | 118068.9988
38960.3847 | 2 | 0 | 38960.3847 | 2095 | 0 |  | 2624.5 | 2763.5 | 0.1221 | 0 | 127.8999 | 0 | 0.001221 | 0 | 1.279 | 0 | 0.001221 | 1.279 | 118069 | 12.8105 | 118068.9988
38960.3852 | 4 | 0 | 38960.3852 | 2258 | 0 |  | 2666.5 | 2805.5 | 0.2442 | 0 | 137.851 | 0 | 0.002442 | 0 | 1.3785 | 0 | 0.002442 | 1.3785 | 58984.5 | 4.667 | 58984.4976
38960.3857 | 331 | 0 | 38960.3857 | 1978 | 0 |  | 2708.5 | 2847.5 | 20.2076 | 0 | 120.757 | 0 | 0.20208 | 0 | 1.2076 | 0 | 0.20208 | 1.2076 | 614.0121 | 19.4833 | 613.81
38960.3862 | 437 | 0 | 38960.3862 | 1856 | 0 |  | 2750.5 | 2889.5 | 26.6789 | 0 | 113.3089 | 0 | 0.26679 | 0 | 1.1331 | 0 | 0.26679 | 1.1331 | 440.8192 | 27.3373 | 440.5524
38960.3867 | 1592 | 0 | 38960.3867 | 2081 | 0 |  | 2792.5 | 2931.5 | 97.1917 | 0 | 127.0452 | 0 | 0.97192 | 0 | 1.2705 | 0 | 0.97192 | 1.2705 | 48.4535 | 13.5694 | 47.4816
38960.3872 | 1961 | 0 | 38960.3872 | 1824 | 0 |  | 2834.5 | 2973.5 | 119.7192 | 0 | 111.3553 | 0 | 1.1972 | 0 | 1.1136 | 0 | 1.1972 | 1.1136 | 20.5191 | 29.5713 | 19.3219
38960.3876 | 1578 | 0 | 38960.3877 | 1987 | 0 |  | 2876.5 | 3015.5 | 96.337 | 0 | 121.3065 | 0 | 0.96337 | 0 | 1.2131 | 0 | 0.96337 | 1.2131 | 49.7706 | 18.9421 | 48.8072
38960.3881 | 2069 | 0 | 38960.3881 | 2342 | 0 |  | 2918.5 | 3057.5 | 126.3126 | 0 | 142.9792 | 0 | 1.2631 | 0 | 1.4298 | 0 | 1.2631 | 1.4298 | 14.2281 | 0.91289 | 12.965
38960.3886 | 1827 | 0 | 38960.3886 | 2035 | 0 |  | 2960.5 | 3099.5 | 111.5385 | 0 | 124.2369 | 0 | 1.1154 | 0 | 1.2424 | 0 | 1.1154 | 1.2424 | 29.3585 | 16.1366 | 28.2431
38960.3891 | 1918 | 0 | 38960.3891 | 1849 | 0 |  | 3002.5 | 3141.5 | 117.094 | 0 | 112.8816 | 0 | 1.1709 | 0 | 1.1288 | 0 | 1.1709 | 1.1288 | 23.2211 | 27.8194 | 22.0501
38960.3896 | 2026 | 0 | 38960.3896 | 1841 | 0 |  | 3044.5 | 3183.5 | 123.6874 | 0 | 112.3932 | 0 | 1.2369 | 0 | 1.1239 | 0 | 1.2369 | 1.1239 | 16.6525 | 28.3748 | 15.4156
38960.3901 | 2068 | 0 | 38960.3901 | 2125 | 0 |  | 3086.5 | 3225.5 | 126.2515 | 0 | 129.7314 | 0 | 1.2625 | 0 | 1.2973 | 0 | 1.2625 | 1.2973 | 14.2834 | 11.2179 | 13.0209
38960.3906 | 1714 | 0 | 38960.3906 | 2172 | 0 |  | 3128.5 | 3267.5 | 104.6398 | 0 | 132.6007 | 0 | 1.0464 | 0 | 1.326 | 0 | 1.0464 | 1.326 | 37.8868 | 8.8112 | 36.8404
38960.391 | 2164 | 0 | 38960.3911 | 2164 | 0 |  | 3170.5 | 3309.5 | 132.1123 | 0 | 132.1123 | 0 | 1.3211 | 0 | 1.3211 | 0 | 1.3211 | 1.3211 | 9.2135 | 9.2135 | 7.8924
38960.3915 | 2111 | 0 | 38960.3915 | 1886 | 0 |  | 3212.5 | 3351.5 | 128.8767 | 0 | 115.1404 | 0 | 1.2888 | 0 | 1.1514 | 0 | 1.2888 | 1.1514 | 11.9555 | 25.3118 | 10.6667
| 2081 | 0 | 38960.392 | 1887 | 0 |  | 3255 | 3394 | 127.0452 | 0 | 115.2015 | 0 | 1.2705 | 0 | 1.152 | 0 | 1.2705 | 1.152 | 13.5694 | 25.2454 | 12.299
38960.3925 | 2050 | 0 | 38960.3925 | 2222 | 0 |  | 3296.5 | 3435.5 | 125.1526 | 0 | 135.6532 | 0 | 1.2515 | 0 | 1.3565 | 0 | 1.2515 | 1.3565 | 15.2868 | 6.3627 | 14.0353

## B3-C6
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 146.177 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38960.3531 | 1 | 0 | 38960.3531 | 1 | 0 |  | -108 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3536 | 1 | 0 | 38960.3536 | 1 | 0 |  | -66 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3541 | 1 | 0 | 38960.3541 | 2 | 0 |  | -24 | 115 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 239338 | 119619 | 239337.9994
38960.3545 | 1 | 0 | 38960.3546 | 1 | 0 |  | 18 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.355 | 1 | 0 | 38960.3551 | 1 | 0 |  | 60 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3555 | 1 | 0 | 38960.3555 | 1 | 0 |  | 102 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.356 | 1 | 0 | 38960.356 | 1 | 0 |  | 144 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3565 | 1 | 0 | 38960.3565 | 1 | 0 |  | 186 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.357 | 1 | 0 | 38960.357 | 1 | 0 |  | 228 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3575 | 1 | 0 | 38960.3575 | 1 | 0 |  | 270 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.358 | 1 | 0 | 38960.358 | 1 | 0 |  | 312 | 451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3584 | 1 | 0 | 38960.3585 | 1 | 0 |  | 354 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3589 | 1 | 0 | 38960.3589 | 1 | 0 |  | 396 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3594 | 1 | 0 | 38960.3594 | 1 | 0 |  | 438 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3599 | 1 | 0 | 38960.3599 | 1 | 0 |  | 480 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3604 | 1 | 0 | 38960.3604 | 1 | 0 |  | 522 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3609 | 1 | 0 | 38960.3609 | 1 | 0 |  | 564 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3614 | 1 | 0 | 38960.3614 | 1 | 0 |  | 606 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3618 | 1 | 0 | 38960.3619 | 1 | 0 |  | 648 | 787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3623 | 1 | 0 | 38960.3623 | 1 | 0 |  | 690 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3628 | 1 | 0 | 38960.3628 | 1 | 0 |  | 732 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3633 | 1 | 0 | 38960.3633 | 1 | 0 |  | 774 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3638 | 1 | 0 | 38960.3638 | 1 | 0 |  | 816 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3643 | 1 | 0 | 38960.3643 | 1 | 0 |  | 858 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3648 | 1 | 0 | 38960.3648 | 1 | 0 |  | 900 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3652 | 1 | 0 | 38960.3653 | 1 | 0 |  | 942 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3657 | 1 | 0 | 38960.3658 | 1 | 0 |  | 984 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3662 | 1 | 0 | 38960.3662 | 1 | 0 |  | 1026 | 1165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3667 | 1 | 0 | 38960.3667 | 1 | 0 |  | 1068 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3672 | 1 | 0 | 38960.3672 | 1 | 0 |  | 1110 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3677 | 1 | 0 | 38960.3677 | 1 | 0 |  | 1152 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3682 | 1 | 0 | 38960.3682 | 1 | 0 |  | 1194 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3686 | 1 | 0 | 38960.3687 | 1 | 0 |  | 1236 | 1375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3691 | 1 | 0 | 38960.3692 | 1 | 0 |  | 1278 | 1417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3696 | 1 | 0 | 38960.3696 | 1 | 0 |  | 1320 | 1459 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3701 | 1 | 0 | 38960.3701 | 2 | 0 |  | 1362 | 1501 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 239338 | 119619 | 239337.9994
38960.3706 | 1 | 0 | 38960.3706 | 1 | 0 |  | 1404 | 1543 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3711 | 1 | 0 | 38960.3711 | 1 | 0 |  | 1446 | 1585 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3716 | 1 | 0 | 38960.3716 | 1 | 0 |  | 1488 | 1627 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.372 | 1 | 0 | 38960.3721 | 1 | 0 |  | 1530 | 1669 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3725 | 1 | 0 | 38960.3726 | 1 | 0 |  | 1572 | 1711 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.373 | 1 | 0 | 38960.373 | 1 | 0 |  | 1614 | 1753 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3735 | 1 | 0 | 38960.3735 | 1 | 0 |  | 1656 | 1795 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.374 | 1 | 0 | 38960.374 | 1 | 0 |  | 1698 | 1837 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3745 | 1 | 0 | 38960.3745 | 1 | 0 |  | 1740 | 1879 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.375 | 1 | 0 | 38960.375 | 1 | 0 |  | 1782 | 1921 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3755 | 1 | 0 | 38960.3755 | 1 | 0 |  | 1824 | 1963 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3759 | 1 | 0 | 38960.376 | 1 | 0 |  | 1866 | 2005 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3764 | 1 | 0 | 38960.3764 | 1 | 0 |  | 1908 | 2047 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3769 | 1 | 0 | 38960.3769 | 1 | 0 |  | 1949.5 | 2088.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3774 | 1 | 0 | 38960.3774 | 1 | 0 |  | 1992 | 2131 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239338 | 239338 | 239337.9994
38960.3779 | 2 | 0 | 38960.3779 | 1 | 0 |  | 2033.5 | 2172.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119619 | 239338 | 119618.9988
38960.3784 | 2 | 0 | 38960.3784 | 2 | 0 |  | 2075.5 | 2214.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119619 | 119619 | 119618.9988
38960.3789 | 2 | 0 | 38960.3789 | 3 | 0 |  | 2117.5 | 2256.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 119619 | 79712.6667 | 119618.9988
38960.3793 | 2 | 0 | 38960.3794 | 734 | 0 |  | 2159.5 | 2298.5 | 0.1221 | 0 | 44.8107 | 0 | 0.001221 | 0 | 0.44811 | 0 | 0.001221 | 0.44811 | 119619 | 226.2098 | 119618.9988
38960.3798 | 2 | 0 | 38960.3798 | 613 | 0 |  | 2201.5 | 2340.5 | 0.1221 | 0 | 37.4237 | 0 | 0.001221 | 0 | 0.37424 | 0 | 0.001221 | 0.37424 | 119619 | 290.6003 | 119618.9988
38960.3803 | 2 | 0 | 38960.3803 | 807 | 0 |  | 2243.5 | 2382.5 | 0.1221 | 0 | 49.2674 | 0 | 0.001221 | 0 | 0.49267 | 0 | 0.001221 | 0.49267 | 119619 | 196.7014 | 119618.9988
38960.3808 | 2 | 0 | 38960.3808 | 900 | 0 |  | 2285.5 | 2424.5 | 0.1221 | 0 | 54.9451 | 0 | 0.001221 | 0 | 0.54945 | 0 | 0.001221 | 0.54945 | 119619 | 166.0422 | 119618.9988
38960.3813 | 2 | 0 | 38960.3813 | 187 | 0 |  | 2327.5 | 2466.5 | 0.1221 | 0 | 11.4164 | 0 | 0.001221 | 0 | 0.11416 | 0 | 0.001221 | 0.11416 | 119619 | 1180.4171 | 119618.9988
38960.3818 | 2 | 0 | 38960.3818 | 2047 | 0 |  | 2369.5 | 2508.5 | 0.1221 | 0 | 124.9695 | 0 | 0.001221 | 0 | 1.2497 | 0 | 0.001221 | 1.2497 | 119619 | 16.9702 | 119618.9988
38960.3823 | 2 | 0 | 38960.3823 | 2161 | 0 |  | 2411.5 | 2550.5 | 0.1221 | 0 | 131.9292 | 0 | 0.001221 | 0 | 1.3193 | 0 | 0.001221 | 1.3193 | 119619 | 10.7996 | 119618.9988
38960.3827 | 2 | 0 | 38960.3828 | 1805 | 0 |  | 2453.5 | 2592.5 | 0.1221 | 0 | 110.1954 | 0 | 0.001221 | 0 | 1.102 | 0 | 0.001221 | 1.102 | 119619 | 32.6526 | 119618.9988
38960.3832 | 2 | 0 | 38960.3832 | 2036 | 0 |  | 2495.5 | 2634.5 | 0.1221 | 0 | 124.2979 | 0 | 0.001221 | 0 | 1.243 | 0 | 0.001221 | 1.243 | 119619 | 17.6022 | 119618.9988
38960.3837 | 2 | 0 | 38960.3837 | 2298 | 0 |  | 2537.5 | 2676.5 | 0.1221 | 0 | 140.293 | 0 | 0.001221 | 0 | 1.4029 | 0 | 0.001221 | 1.4029 | 119619 | 4.1941 | 119618.9988
38960.3842 | 391 | 0 | 38960.3842 | 1803 | 0 |  | 2579.5 | 2718.5 | 23.8706 | 0 | 110.0733 | 0 | 0.23871 | 0 | 1.1007 | 0 | 0.23871 | 1.1007 | 512.3734 | 32.7998 | 512.1347
38960.3847 | 477 | 0 | 38960.3847 | 2193 | 0 |  | 2621.5 | 2760.5 | 29.1209 | 0 | 133.8828 | 0 | 0.29121 | 0 | 1.3388 | 0 | 0.29121 | 1.3388 | 401.9665 | 9.1829 | 401.6752
38960.3852 | 683 | 0 | 38960.3852 | 2337 | 0 |  | 2663.5 | 2802.5 | 41.6972 | 0 | 142.674 | 0 | 0.41697 | 0 | 1.4267 | 0 | 0.41697 | 1.4267 | 250.5681 | 2.4553 | 250.1511
38960.3857 | 489 | 0 | 38960.3857 | 2224 | 0 |  | 2705.5 | 2844.5 | 29.8535 | 0 | 135.7753 | 0 | 0.29853 | 0 | 1.3578 | 0 | 0.29853 | 1.3578 | 389.6483 | 7.661 | 389.3497
38960.3861 | 1453 | 0 | 38960.3862 | 1937 | 0 |  | 2747.5 | 2886.5 | 88.7057 | 0 | 118.254 | 0 | 0.88706 | 0 | 1.1825 | 0 | 0.88706 | 1.1825 | 64.7887 | 23.6128 | 63.9017
38960.3866 | 2066 | 0 | 38960.3866 | 1866 | 0 |  | 2789.5 | 2928.5 | 126.1294 | 0 | 113.9194 | 0 | 1.2613 | 0 | 1.1392 | 0 | 1.2613 | 1.1392 | 15.8945 | 28.3162 | 14.6332
38960.3871 | 2139 | 0 | 38960.3871 | 1860 | 0 |  | 2831.5 | 2970.5 | 130.5861 | 0 | 113.5531 | 0 | 1.3059 | 0 | 1.1355 | 0 | 1.3059 | 1.1355 | 11.9392 | 28.7301 | 10.6334
38960.3876 | 2025 | 0 | 38960.3876 | 2064 | 0 |  | 2873.5 | 3012.5 | 123.6264 | 0 | 126.0073 | 0 | 1.2363 | 0 | 1.2601 | 0 | 1.2363 | 1.2601 | 18.241 | 16.0068 | 17.0047
38960.3881 | 2242 | 0 | 38960.3881 | 2369 | 0 |  | 2915.5 | 3054.5 | 136.8742 | 0 | 144.6276 | 0 | 1.3687 | 0 | 1.4463 | 0 | 1.3687 | 1.4463 | 6.7966 | 1.0713 | 5.4279
38960.3886 | 1886 | 0 | 38960.3886 | 1944 | 0 |  | 2957.5 | 3096.5 | 115.1404 | 0 | 118.6813 | 0 | 1.1514 | 0 | 1.1868 | 0 | 1.1514 | 1.1868 | 26.9555 | 23.1677 | 25.8041
38960.3891 | 1890 | 0 | 38960.3891 | 1851 | 0 |  | 2999.5 | 3138.5 | 115.3846 | 0 | 113.0037 | 0 | 1.1538 | 0 | 1.13 | 0 | 1.1538 | 1.13 | 26.6868 | 29.356 | 25.5329
38960.3895 | 1913 | 0 | 38960.3896 | 2230 | 0 |  | 3041.5 | 3180.5 | 116.7888 | 0 | 136.1416 | 0 | 1.1679 | 0 | 1.3614 | 0 | 1.1679 | 1.3614 | 25.1636 | 7.3713 | 23.9957
38960.39 | 1992 | 0 | 38960.39 | 1920 | 0 |  | 3083.5 | 3222.5 | 121.6117 | 0 | 117.2161 | 0 | 1.2161 | 0 | 1.1722 | 0 | 1.2161 | 1.1722 | 20.1998 | 24.7073 | 18.9837
38960.3905 | 2039 | 0 | 38960.3905 | 2096 | 0 |  | 3125.5 | 3264.5 | 124.4811 | 0 | 127.9609 | 0 | 1.2448 | 0 | 1.2796 | 0 | 1.2448 | 1.2796 | 17.4291 | 14.2357 | 16.1843
38960.391 | 2101 | 0 | 38960.391 | 2276 | 0 |  | 3167.5 | 3306.5 | 128.2662 | 0 | 138.9499 | 0 | 1.2827 | 0 | 1.3895 | 0 | 1.2827 | 1.3895 | 13.9638 | 5.2012 | 12.6812
38960.3915 | 1950 | 0 | 38960.3915 | 1894 | 0 |  | 3209.5 | 3348.5 | 119.0476 | 0 | 115.6288 | 0 | 1.1905 | 0 | 1.1563 | 0 | 1.1905 | 1.1563 | 22.7887 | 26.4192 | 21.5982
38960.392 | 2260 | 0 | 38960.392 | 2378 | 0 |  | 3251.5 | 3390.5 | 137.9731 | 0 | 145.177 | 0 | 1.3797 | 0 | 1.4518 | 0 | 1.3797 | 1.4518 | 5.946 | 0.68881 | 4.5663
38960.3925 | 1877 | 0 | 38960.3925 | 2358 | 0 |  | 3293.5 | 3432.5 | 114.591 | 0 | 143.956 | 0 | 1.1459 | 0 | 1.4396 | 0 | 1.1459 | 1.4396 | 27.5642 | 1.5428 | 26.4183

## B3-C5
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 144.6508 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38960.3531 | 1 | 0 | 38960.3531 | 1 | 0 |  | -110.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3536 | 1 | 0 | 38960.3536 | 1 | 0 |  | -68.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.354 | 1 | 0 | 38960.3541 | 1 | 0 |  | -26.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3545 | 1 | 0 | 38960.3545 | 1 | 0 |  | 15.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.355 | 1 | 0 | 38960.355 | 1 | 0 |  | 57.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3555 | 1 | 0 | 38960.3555 | 1 | 0 |  | 99.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.356 | 1 | 0 | 38960.356 | 2 | 0 |  | 141.5 | 280.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 236838 | 118369 | 236837.9994
38960.3565 | 1 | 0 | 38960.3565 | 1 | 0 |  | 183.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.357 | 1 | 0 | 38960.357 | 1 | 0 |  | 225.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3574 | 1 | 0 | 38960.3575 | 1 | 0 |  | 267.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3579 | 1 | 0 | 38960.3579 | 1 | 0 |  | 309.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3584 | 1 | 0 | 38960.3584 | 1 | 0 |  | 351.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3589 | 1 | 0 | 38960.3589 | 1 | 0 |  | 393.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3594 | 1 | 0 | 38960.3594 | 1 | 0 |  | 435 | 574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3599 | 1 | 0 | 38960.3599 | 1 | 0 |  | 477 | 616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3604 | 1 | 0 | 38960.3604 | 1 | 0 |  | 519.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3608 | 1 | 0 | 38960.3609 | 1 | 0 |  | 561.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3613 | 1 | 0 | 38960.3613 | 1 | 0 |  | 603 | 742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3618 | 1 | 0 | 38960.3618 | 1 | 0 |  | 645.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3623 | 1 | 0 | 38960.3623 | 1 | 0 |  | 687 | 826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3628 | 1 | 0 | 38960.3628 | 1 | 0 |  | 729 | 868 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3633 | 1 | 0 | 38960.3633 | 1 | 0 |  | 771 | 910 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3637 | 1 | 0 | 38960.3638 | 1 | 0 |  | 813 | 952 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3642 | 1 | 0 | 38960.3643 | 1 | 0 |  | 855 | 994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3647 | 1 | 0 | 38960.3647 | 1 | 1 |  | 897.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 236838 | #DIV/0! | 236837.9994
38960.3652 | 1 | 0 | 38960.3652 | 1 | 0 |  | 939 | 1078 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3657 | 1 | 0 | 38960.3657 | 1 | 0 |  | 981 | 1120 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3662 | 1 | 0 | 38960.3662 | 1 | 0 |  | 1023 | 1162 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3667 | 1 | 0 | 38960.3667 | 1 | 0 |  | 1065 | 1204 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3672 | 1 | 0 | 38960.3672 | 1 | 0 |  | 1107 | 1246 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3676 | 1 | 0 | 38960.3677 | 1 | 0 |  | 1149 | 1288 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3681 | 1 | 0 | 38960.3681 | 1 | 0 |  | 1191 | 1330 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3686 | 1 | 0 | 38960.3686 | 1 | 0 |  | 1233 | 1372 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3691 | 1 | 0 | 38960.3691 | 1 | 0 |  | 1275 | 1414 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3696 | 1 | 0 | 38960.3696 | 1 | 0 |  | 1317 | 1456 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3701 | 1 | 0 | 38960.3701 | 1 | 0 |  | 1359 | 1498 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3706 | 1 | 0 | 38960.3706 | 1 | 0 |  | 1401 | 1540 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.371 | 1 | 0 | 38960.3711 | 1 | 0 |  | 1443 | 1582 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3715 | 1 | 0 | 38960.3716 | 1 | 0 |  | 1485 | 1624 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.372 | 1 | 0 | 38960.372 | 1 | 0 |  | 1527 | 1666 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3725 | 1 | 0 | 38960.3725 | 1 | 0 |  | 1569 | 1708 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.373 | 1 | 0 | 38960.373 | 1 | 0 |  | 1611 | 1750 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3735 | 1 | 0 | 38960.3735 | 1 | 0 |  | 1653 | 1792 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.374 | 1 | 0 | 38960.374 | 1 | 0 |  | 1695 | 1834 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3744 | 1 | 0 | 38960.3745 | 1 | 0 |  | 1737 | 1876 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3749 | 1 | 0 | 38960.375 | 1 | 0 |  | 1779 | 1918 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3754 | 1 | 0 | 38960.3754 | 1 | 0 |  | 1821 | 1960 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3759 | 1 | 0 | 38960.3759 | 1 | 0 |  | 1863 | 2002 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3764 | 1 | 0 | 38960.3764 | 1 | 0 |  | 1905 | 2044 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3769 | 1 | 0 | 38960.3769 | 1 | 0 |  | 1947 | 2086 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38960.3774 | 1 | 0 | 38960.3774 | 1853 | 0 |  | 1989 | 2128 | 0.06105 | 0 | 113.1258 | 0 | 0.0006105 | 0 | 1.1313 | 0 | 0.0006105 | 1.1313 | 236838 | 27.8672 | 236837.9994
38960.3778 | 1 | 0 | 38960.3779 | 1963 | 0 |  | 2031 | 2170 | 0.06105 | 0 | 119.8413 | 0 | 0.0006105 | 0 | 1.1984 | 0 | 0.0006105 | 1.1984 | 236838 | 20.702 | 236837.9994
38960.3783 | 1 | 0 | 38960.3784 | 2183 | 0 |  | 2073 | 2212 | 0.06105 | 0 | 133.2723 | 0 | 0.0006105 | 0 | 1.3327 | 0 | 0.0006105 | 1.3327 | 236838 | 8.5378 | 236837.9994
38960.3788 | 1 | 0 | 38960.3788 | 1979 | 0 |  | 2115 | 2254 | 0.06105 | 0 | 120.8181 | 0 | 0.0006105 | 0 | 1.2082 | 0 | 0.0006105 | 1.2082 | 236838 | 19.7261 | 236837.9994
38960.3793 | 1 | 0 | 38960.3793 | 1943 | 0 |  | 2157 | 2296 | 0.06105 | 0 | 118.6203 | 0 | 0.0006105 | 0 | 1.1862 | 0 | 0.0006105 | 1.1862 | 236838 | 21.9444 | 236837.9994
38960.3798 | 1 | 0 | 38960.3798 | 1794 | 0 |  | 2199 | 2338 | 0.06105 | 0 | 109.5238 | 0 | 0.0006105 | 0 | 1.0952 | 0 | 0.0006105 | 1.0952 | 236838 | 32.0725 | 236837.9994
38960.3803 | 1 | 0 | 38960.3803 | 1975 | 0 |  | 2241 | 2380 | 0.06105 | 0 | 120.5739 | 0 | 0.0006105 | 0 | 1.2057 | 0 | 0.0006105 | 1.2057 | 236838 | 19.9686 | 236837.9994
38960.3808 | 1 | 0 | 38960.3808 | 1798 | 0 |  | 2283 | 2422 | 0.06105 | 0 | 109.768 | 0 | 0.0006105 | 0 | 1.0977 | 0 | 0.0006105 | 1.0977 | 236838 | 31.7786 | 236837.9994
38960.3812 | 1 | 0 | 38960.3813 | 1875 | 0 |  | 2325 | 2464 | 0.06105 | 0 | 114.4689 | 0 | 0.0006105 | 0 | 1.1447 | 0 | 0.0006105 | 1.1447 | 236838 | 26.3669 | 236837.9994
38960.3817 | 2 | 0 | 38960.3818 | 2043 | 0 |  | 2367 | 2506 | 0.1221 | 0 | 124.7253 | 0 | 0.001221 | 0 | 1.2473 | 0 | 0.001221 | 1.2473 | 118369 | 15.9755 | 118368.9988
38960.3822 | 2 | 0 | 38960.3822 | 2202 | 0 |  | 2409 | 2548 | 0.1221 | 0 | 134.4322 | 0 | 0.001221 | 0 | 1.3443 | 0 | 0.001221 | 1.3443 | 118369 | 7.6013 | 118368.9988
38960.3827 | 2 | 0 | 38960.3827 | 2152 | 0 |  | 2451 | 2590 | 0.1221 | 0 | 131.3797 | 0 | 0.001221 | 0 | 1.3138 | 0 | 0.001221 | 1.3138 | 118369 | 10.1013 | 118368.9988
38960.3832 | 2 | 0 | 38960.3832 | 2339 | 0 |  | 2493 | 2632 | 0.1221 | 0 | 142.7961 | 0 | 0.001221 | 0 | 1.428 | 0 | 0.001221 | 1.428 | 118369 | 1.2988 | 118368.9988
38960.3837 | 2 | 0 | 38960.3837 | 1910 | 0 |  | 2535 | 2674 | 0.1221 | 0 | 116.6056 | 0 | 0.001221 | 0 | 1.1661 | 0 | 0.001221 | 1.1661 | 118369 | 24.0513 | 118368.9988
38960.3842 | 394 | 0 | 38960.3842 | 2059 | 0 |  | 2577 | 2716 | 24.0537 | 0 | 125.7021 | 0 | 0.24054 | 0 | 1.257 | 0 | 0.24054 | 1.257 | 501.3655 | 15.0743 | 501.1249
38960.3847 | 813 | 0 | 38960.3847 | 1925 | 0 |  | 2619 | 2758 | 49.6337 | 0 | 117.5214 | 0 | 0.49634 | 0 | 1.1752 | 0 | 0.49634 | 1.1752 | 191.4367 | 23.0847 | 190.9403
38960.3851 | 573 | 0 | 38960.3852 | 2006 | 0 |  | 2661 | 2800 | 34.9817 | 0 | 122.4664 | 0 | 0.34982 | 0 | 1.2247 | 0 | 0.34982 | 1.2247 | 313.5044 | 18.1147 | 313.1545
38960.3856 | 689 | 0 | 38960.3856 | 2057 | 0 |  | 2703 | 2842 | 42.0635 | 0 | 125.58 | 0 | 0.42063 | 0 | 1.2558 | 0 | 0.42063 | 1.2558 | 243.8868 | 15.1862 | 243.4662
38960.3861 | 1537 | 0 | 38960.3861 | 2256 | 0 |  | 2745 | 2884 | 93.8339 | 0 | 137.7289 | 0 | 0.93834 | 0 | 1.3773 | 0 | 0.93834 | 1.3773 | 54.1561 | 5.0257 | 53.2178
38960.3866 | 2046 | 0 | 38960.3866 | 1885 | 0 |  | 2787 | 2926 | 124.9084 | 0 | 115.0794 | 0 | 1.2491 | 0 | 1.1508 | 0 | 1.2491 | 1.1508 | 15.8055 | 25.6966 | 14.5564
38960.3871 | 2129 | 0 | 38960.3871 | 2281 | 0 |  | 2829 | 2968 | 129.9756 | 0 | 139.2552 | 0 | 1.2998 | 0 | 1.3926 | 0 | 1.2998 | 1.3926 | 11.2907 | 3.8746 | 9.991
38960.3876 | 2178 | 0 | 38960.3876 | 2353 | 0 |  | 2871 | 3010 | 132.967 | 0 | 143.6508 | 0 | 1.3297 | 0 | 1.4365 | 0 | 1.3297 | 1.4365 | 8.787 | 0.69613 | 7.4573
38960.3881 | 2230 | 0 | 38960.3881 | 2129 | 0 |  | 2913 | 3052 | 136.1416 | 0 | 129.9756 | 0 | 1.3614 | 0 | 1.2998 | 0 | 1.3614 | 1.2998 | 6.2502 | 11.2907 | 4.8888
38960.3885 | 2238 | 0 | 38960.3886 | 2215 | 0 |  | 2955 | 3094 | 136.63 | 0 | 135.2259 | 0 | 1.3663 | 0 | 1.3523 | 0 | 1.3663 | 1.3523 | 5.8704 | 6.9698 | 4.5041
38960.389 | 1916 | 0 | 38960.3891 | 1927 | 0 |  | 2997 | 3136 | 116.9719 | 0 | 117.6435 | 0 | 1.1697 | 0 | 1.1764 | 0 | 1.1697 | 1.1764 | 23.6628 | 22.9569 | 22.4931
38960.3895 | 1809 | 0 | 38960.3895 | 2112 | 0 |  | 3038.5 | 3177.5 | 110.4396 | 0 | 128.9377 | 0 | 1.1044 | 0 | 1.2894 | 0 | 1.1044 | 1.2894 | 30.9773 | 12.1866 | 29.8729
38960.39 | 1907 | 0 | 38960.39 | 2172 | 0 |  | 3081 | 3220 | 116.4225 | 0 | 132.6007 | 0 | 1.1642 | 0 | 1.326 | 0 | 1.1642 | 1.326 | 24.2465 | 9.0875 | 23.0822
38960.3905 | 1856 | 0 | 38960.3905 | 2038 | 0 |  | 3122.5 | 3261.5 | 113.3089 | 0 | 124.42 | 0 | 1.1331 | 0 | 1.2442 | 0 | 1.1331 | 1.2442 | 27.6606 | 16.2601 | 26.5275
38960.391 | 2115 | 0 | 38960.391 | 1922 | 0 |  | 3164.5 | 3303.5 | 129.1209 | 0 | 117.3382 | 0 | 1.2912 | 0 | 1.1734 | 0 | 1.2912 | 1.1734 | 12.0274 | 23.2768 | 10.7362
38960.3915 | 2332 | 0 | 38960.3915 | 2271 | 0 |  | 3207 | 3346 | 142.3687 | 0 | 138.6447 | 0 | 1.4237 | 0 | 1.3864 | 0 | 1.4237 | 1.3864 | 1.6029 | 4.332 | 0.17923
38960.3919 | 1841 | 0 | 38960.392 | 2201 | 0 |  | 3249 | 3388 | 112.3932 | 0 | 134.3712 | 0 | 1.1239 | 0 | 1.3437 | 0 | 1.1239 | 1.3437 | 28.7007 | 7.6502 | 27.5768
38960.3924 | 2093 | 0 | 38960.3924 | 1962 | 0 |  | 3290.5 | 3429.5 | 127.7778 | 0 | 119.7802 | 0 | 1.2778 | 0 | 1.1978 | 0 | 1.2778 | 1.1978 | 13.205 | 20.7635 | 11.9272

## B3-B4
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 139.9499 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38960.353 | 1 | 0 | 38960.353 | 1 | 0 |  | -113.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3535 | 1 | 0 | 38960.3535 | 1 | 0 |  | -71.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.354 | 1 | 0 | 38960.354 | 1 | 0 |  | -29.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3545 | 1 | 0 | 38960.3545 | 1 | 0 |  | 12.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.355 | 1 | 0 | 38960.355 | 1 | 0 |  | 54.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3555 | 1 | 0 | 38960.3555 | 1 | 0 |  | 96.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3559 | 1 | 0 | 38960.356 | 1 | 0 |  | 138.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3564 | 1 | 0 | 38960.3564 | 1 | 0 |  | 180.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3569 | 1 | 0 | 38960.3569 | 1 | 0 |  | 222.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3574 | 1 | 0 | 38960.3574 | 1 | 0 |  | 264.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3579 | 1 | 0 | 38960.3579 | 1 | 0 |  | 306.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3584 | 1 | 0 | 38960.3584 | 1 | 0 |  | 348.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3589 | 1 | 0 | 38960.3589 | 1 | 0 |  | 390.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3594 | 1 | 0 | 38960.3594 | 1 | 0 |  | 432.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3598 | 1 | 0 | 38960.3598 | 1 | 0 |  | 474.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3603 | 1 | 0 | 38960.3603 | 1 | 0 |  | 516.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3608 | 1 | 0 | 38960.3608 | 1 | 0 |  | 558.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3613 | 1 | 0 | 38960.3613 | 1 | 0 |  | 600.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3618 | 1 | 0 | 38960.3618 | 1 | 0 |  | 642.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3623 | 1 | 0 | 38960.3623 | 1 | 0 |  | 684.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3628 | 1 | 0 | 38960.3628 | 1 | 0 |  | 726.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3632 | 1 | 0 | 38960.3633 | 1 | 0 |  | 768.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3637 | 1 | 0 | 38960.3637 | 1 | 0 |  | 810.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3642 | 1 | 0 | 38960.3642 | 1 | 0 |  | 852.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3647 | 1 | 0 | 38960.3647 | 1 | 0 |  | 894.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3652 | 1 | 0 | 38960.3652 | 1 | 0 |  | 936.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3657 | 1 | 0 | 38960.3657 | 1 | 0 |  | 978.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3662 | 1 | 0 | 38960.3662 | 1 | 0 |  | 1020.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3666 | 1 | 0 | 38960.3667 | 2 | 0 |  | 1062.5 | 1201.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229138 | 114519 | 229137.9994
38960.3671 | 1 | 1 | 38960.3671 | 1 | 0 |  | 1104.5 | 1243.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 525042230.44 | 229138 | 228938.0872
38960.3676 | 1 | 0 | 38960.3676 | 1 | 0 |  | 1146.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3681 | 1 | 0 | 38960.3681 | 1 | 0 |  | 1188.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3686 | 1 | 0 | 38960.3686 | 1 | 0 |  | 1230.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3691 | 1 | 0 | 38960.3691 | 1 | 0 |  | 1272.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3696 | 1 | 0 | 38960.3696 | 1 | 0 |  | 1314.5 | 1453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.37 | 1 | 0 | 38960.3701 | 1 | 0 |  | 1356.5 | 1495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3705 | 1 | 0 | 38960.3705 | 1 | 0 |  | 1398.5 | 1537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.371 | 1 | 0 | 38960.371 | 1 | 0 |  | 1440.5 | 1579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3715 | 1 | 0 | 38960.3715 | 1 | 0 |  | 1482.5 | 1621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.372 | 1 | 0 | 38960.372 | 1 | 0 |  | 1524 | 1663 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3725 | 1 | 0 | 38960.3725 | 1 | 0 |  | 1566.5 | 1705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.373 | 1 | 0 | 38960.373 | 1 | 0 |  | 1608.5 | 1747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3734 | 1 | 0 | 38960.3735 | 1 | 0 |  | 1650 | 1789 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3739 | 1 | 0 | 38960.3739 | 1 | 0 |  | 1692.5 | 1831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3744 | 1 | 0 | 38960.3744 | 1 | 0 |  | 1734.5 | 1873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3749 | 1 | 0 | 38960.3749 | 1 | 0 |  | 1776.5 | 1915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3754 | 1 | 0 | 38960.3754 | 1 | 0 |  | 1818.5 | 1957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3759 | 1 | 0 | 38960.3759 | 1 | 0 |  | 1860 | 1999 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3764 | 1 | 0 | 38960.3764 | 1 | 0 |  | 1902.5 | 2041.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3769 | 1 | 0 | 38960.3769 | 1 | 0 |  | 1944.5 | 2083.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3773 | 1 | 0 | 38960.3773 | 1 | 0 |  | 1986 | 2125 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38960.3778 | 1 | 0 | 38960.3778 | 2 | 0 |  | 2028.5 | 2167.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229138 | 114519 | 229137.9994
38960.3783 | 2 | 0 | 38960.3783 | 2 | 0 |  | 2070 | 2209 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114519 | 114519 | 114518.9988
38960.3788 | 2 | 0 | 38960.3788 | 1 | 0 |  | 2112.5 | 2251.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114519 | 229138 | 114518.9988
38960.3793 | 2 | 0 | 38960.3793 | 1 | 0 |  | 2154 | 2293 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114519 | 229138 | 114518.9988
38960.3798 | 2 | 0 | 38960.3798 | 2 | 0 |  | 2196 | 2335 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114519 | 114519 | 114518.9988
38960.3802 | 2 | 0 | 38960.3803 | 1 | 0 |  | 2238 | 2377 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114519 | 229138 | 114518.9988
38960.3807 | 2 | 0 | 38960.3808 | 2 | 0 |  | 2280 | 2419 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114519 | 114519 | 114518.9988
38960.3812 | 2 | 0 | 38960.3812 | 1 | 0 |  | 2322 | 2461 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114519 | 229138 | 114518.9988
38960.3817 | 2 | 0 | 38960.3817 | 2 | 0 |  | 2364 | 2503 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114519 | 114519 | 114518.9988
38960.3822 | 2 | 0 | 38960.3822 | 2 | 0 |  | 2406 | 2545 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114519 | 114519 | 114518.9988
38960.3827 | 2 | 0 | 38960.3827 | 2 | 0 |  | 2448 | 2587 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114519 | 114519 | 114518.9988
38960.3832 | 2 | 0 | 38960.3832 | 1 | 0 |  | 2490 | 2629 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114519 | 229138 | 114518.9988
38960.3836 | 2 | 0 | 38960.3837 | 2 | 0 |  | 2532 | 2671 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114519 | 114519 | 114518.9988
38960.3841 | 162 | 1 | 38960.3842 | 2 | 0 |  | 2574 | 2713 | 9.8901 | 0.06105 | 0.1221 | 0 | 0.098901 | 0.0006105 | 0.001221 | 0 | 0.098291 | 0.001221 | 1323.2246 | 114519 | 212752.221
38960.3846 | 832 | 1 | 38960.3846 | 2 | 0 |  | 2616 | 2755 | 50.7937 | 0.06105 | 0.1221 | 0 | 0.50794 | 0.0006105 | 0.001221 | 0 | 0.50733 | 0.001221 | 175.7379 | 114519 | 145810.6756
38960.3851 | 571 | 1 | 38960.3851 | 2 | 0 |  | 2658 | 2797 | 34.8596 | 0.06105 | 0.1221 | 0 | 0.3486 | 0.0006105 | 0.001221 | 0 | 0.34799 | 0.001221 | 301.997 | 114519 | 171887.9045
38960.3856 | 548 | 0 | 38960.3856 | 483 | 1 |  | 2700 | 2839 | 33.4554 | 0 | 29.4872 | 0.06105 | 0.33455 | 0 | 0.29487 | 0.0006105 | 0.33455 | 0.29426 | 318.3175 | 375.5975 | 317.983
38960.3861 | 1428 | 0 | 38960.3861 | 504 | 55 |  | 2742 | 2881 | 87.1795 | 0 | 30.7692 | 3.3578 | 0.87179 | 0 | 0.30769 | 0.033578 | 0.87179 | 0.27411 | 60.5308 | 410.5523 | 59.659
38960.3866 | 1637 | 0 | 38960.3866 | 1266 | 156 |  | 2784 | 2923 | 99.9389 | 0 | 77.2894 | 9.5238 | 0.99939 | 0 | 0.77289 | 0.095238 | 0.99939 | 0.67766 | 40.0354 | 106.5207 | 39.036
38960.387 | 1839 | 120 | 38960.3871 | 1989 | 145 |  | 2826 | 2965 | 112.2711 | 7.326 | 121.4286 | 8.8523 | 1.1227 | 0.07326 | 1.2143 | 0.088523 | 1.0495 | 1.1258 | 40.0181 | 20.4756 | 47.2168
38960.3875 | 1950 | 103 | 38960.3876 | 1931 | 122 |  | 2868 | 3007 | 119.0476 | 6.2882 | 117.8877 | 7.4481 | 1.1905 | 0.062882 | 1.1789 | 0.074481 | 1.1276 | 1.1044 | 23.1041 | 28.2118 | 51.1391
38960.388 | 2254 | 107 | 38960.388 | 1676 | 90 |  | 2910 | 3049 | 137.6068 | 6.5324 | 102.3199 | 5.4945 | 1.3761 | 0.065324 | 1.0232 | 0.054945 | 1.3107 | 0.96825 | 1.2158 | 10.5974 | 6.145
38960.3885 | 1975 | 80 | 38960.3885 | 2074 | 100 |  | 2952 | 3091 | 120.5739 | 4.884 | 126.6178 | 6.105 | 1.2057 | 0.04884 | 1.2662 | 0.06105 | 1.1569 | 1.2051 | 23.9574 | 14.0294 | 36.5069
38960.389 | 1769 | 67 | 38960.389 | 1755 | 76 |  | 2994 | 3133 | 107.9976 | 4.0904 | 107.1429 | 4.6398 | 1.08 | 0.040904 | 1.0714 | 0.046398 | 1.0391 | 1.025 | 34.4287 | 36.8509 | 183.4224
38960.3895 | 1841 | 64 | 38960.3895 | 1882 | 74 |  | 3036 | 3175 | 112.3932 | 3.9072 | 114.8962 | 4.5177 | 1.1239 | 0.039072 | 1.149 | 0.045177 | 1.0849 | 1.1038 | 29.42 | 26.3661 | 126.2909
38960.39 | 2276 | 65 | 38960.39 | 1954 | 75 |  | 3078 | 3217 | 138.9499 | 3.9683 | 119.2918 | 4.5788 | 1.3895 | 0.039683 | 1.1929 | 0.045788 | 1.3498 | 1.1471 | 0.10665 | 0.49439 | 0.36799
38960.3905 | 2090 | 63 | 38960.3905 | 1855 | 61 |  | 3120 | 3259 | 127.5946 | 3.8462 | 113.2479 | 3.7241 | 1.2759 | 0.038462 | 1.1325 | 0.037241 | 1.2375 | 1.0952 | 10.9462 | 35.3659 | 57.801
38960.3909 | 1959 | 54 | 38960.391 | 2082 | 64 |  | 3162 | 3301 | 119.5971 | 3.2967 | 127.1062 | 3.9072 | 1.196 | 0.032967 | 1.2711 | 0.039072 | 1.163 | 1.232 | 22.8513 | 12.1052 | 55.8661
38960.3914 | 1924 | 47 | 38960.3914 | 2182 | 47 |  | 3204 | 3343 | 117.4603 | 2.8694 | 133.2112 | 2.8694 | 1.1746 | 0.028694 | 1.3321 | 0.028694 | 1.1459 | 1.3034 | 35.9916 | 5.5068 | 35.6897
38960.3919 | 2154 | 54 | 38960.3919 | 1915 | 49 |  | 3246 | 3385 | 131.5018 | 3.2967 | 116.9109 | 2.9915 | 1.315 | 0.032967 | 1.1691 | 0.029915 | 1.2821 | 1.1392 | 7.1669 | 31.9191 | 37.8085
38960.3924 | 2189 | 48 | 38960.3924 | 1956 | 47 |  | 3288 | 3427 | 133.6386 | 2.9304 | 119.4139 | 2.8694 | 1.3364 | 0.029304 | 1.1941 | 0.028694 | 1.3071 | 1.1654 | 5.1736 | 33.6199 | 29.0293

## A2-C6
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 145.8107 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38960.353 | 1 | 0 | 38960.353 | 1 | 0 |  | -116.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3535 | 1 | 0 | 38960.3535 | 1 | 0 |  | -74.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.354 | 1 | 0 | 38960.354 | 1 | 0 |  | -32.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3545 | 1 | 0 | 38960.3545 | 1 | 0 |  | 9.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3549 | 1 | 0 | 38960.355 | 1 | 0 |  | 51.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3554 | 1 | 0 | 38960.3554 | 1 | 0 |  | 93.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3559 | 2 | 0 | 38960.3559 | 1 | 0 |  | 135.5 | 274.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119319 | 238738 | 119318.9988
38960.3564 | 1 | 0 | 38960.3564 | 1 | 0 |  | 177.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3569 | 1 | 0 | 38960.3569 | 1 | 0 |  | 219.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3574 | 2 | 0 | 38960.3574 | 2 | 0 |  | 261.5 | 400.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119319 | 119319 | 119318.9988
38960.3579 | 1 | 0 | 38960.3579 | 2 | 0 |  | 303.5 | 442.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 238738 | 119319 | 238737.9994
38960.3583 | 1 | 0 | 38960.3584 | 1 | 0 |  | 345.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3588 | 1 | 0 | 38960.3588 | 1 | 0 |  | 387.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3593 | 2 | 0 | 38960.3593 | 1 | 0 |  | 429.5 | 568.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119319 | 238738 | 119318.9988
38960.3598 | 1 | 0 | 38960.3598 | 1 | 0 |  | 471.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3603 | 1 | 0 | 38960.3603 | 1 | 0 |  | 513.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3608 | 1 | 0 | 38960.3608 | 1 | 0 |  | 555.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3613 | 1 | 0 | 38960.3613 | 1 | 0 |  | 597.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3617 | 1 | 0 | 38960.3618 | 1 | 0 |  | 639.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3622 | 1 | 0 | 38960.3622 | 1 | 0 |  | 681.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3627 | 1 | 0 | 38960.3627 | 1 | 0 |  | 723.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3632 | 1 | 0 | 38960.3632 | 1 | 0 |  | 765.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3637 | 1 | 0 | 38960.3637 | 1 | 0 |  | 807.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3642 | 1 | 0 | 38960.3642 | 1 | 0 |  | 849.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3647 | 1 | 0 | 38960.3647 | 1 | 0 |  | 891.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3652 | 1 | 0 | 38960.3652 | 1 | 0 |  | 933.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3656 | 1 | 0 | 38960.3656 | 1 | 0 |  | 975.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3661 | 1 | 0 | 38960.3661 | 1 | 0 |  | 1017.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3666 | 1 | 0 | 38960.3666 | 2 | 0 |  | 1059.5 | 1198.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 238738 | 119319 | 238737.9994
38960.3671 | 1 | 0 | 38960.3671 | 1 | 0 |  | 1101.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3676 | 1 | 0 | 38960.3676 | 1 | 0 |  | 1143.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3681 | 1 | 0 | 38960.3681 | 1 | 0 |  | 1185.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3686 | 1 | 0 | 38960.3686 | 1 | 0 |  | 1227.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.369 | 1 | 0 | 38960.3691 | 1 | 0 |  | 1269.5 | 1408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3695 | 1 | 0 | 38960.3695 | 1 | 0 |  | 1311.5 | 1450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.37 | 1 | 0 | 38960.37 | 1 | 0 |  | 1353.5 | 1492.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3705 | 1 | 0 | 38960.3705 | 1 | 0 |  | 1395.5 | 1534.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.371 | 1 | 0 | 38960.371 | 1 | 0 |  | 1437.5 | 1576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238738 | 238738 | 238737.9994
38960.3715 | 2 | 0 | 38960.3715 | 1 | 0 |  | 1479.5 | 1618.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119319 | 238738 | 119318.9988
38960.372 | 4 | 0 | 38960.372 | 1 | 0 |  | 1521.5 | 1660.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 59609.5 | 238738 | 59609.4976
38960.3724 | 4 | 0 | 38960.3725 | 1 | 0 |  | 1563.5 | 1702.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 59609.5 | 238738 | 59609.4976
38960.3729 | 2 | 0 | 38960.3729 | 1 | 0 |  | 1605.5 | 1744.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119319 | 238738 | 119318.9988
38960.3734 | 2 | 0 | 38960.3734 | 1 | 0 |  | 1647.5 | 1786.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119319 | 238738 | 119318.9988
38960.3739 | 2 | 0 | 38960.3739 | 1 | 0 |  | 1689.5 | 1828.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119319 | 238738 | 119318.9988
38960.3744 | 6 | 0 | 38960.3744 | 1 | 0 |  | 1731.5 | 1870.5 | 0.3663 | 0 | 0.06105 | 0 | 0.003663 | 0 | 0.0006105 | 0 | 0.003663 | 0.0006105 | 39706.3333 | 238738 | 39706.3297
38960.3749 | 11 | 0 | 38960.3749 | 1 | 0 |  | 1773.5 | 1912.5 | 0.67155 | 0 | 0.06105 | 0 | 0.0067155 | 0 | 0.0006105 | 0 | 0.0067155 | 0.0006105 | 21612.5455 | 238738 | 21612.5387
38960.3754 | 4 | 0 | 38960.3754 | 1 | 0 |  | 1815.5 | 1954.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 59609.5 | 238738 | 59609.4976
38960.3758 | 60 | 1 | 38960.3759 | 1 | 0 |  | 1857.5 | 1996.5 | 3.663 | 0.06105 | 0.06105 | 0 | 0.03663 | 0.0006105 | 0.0006105 | 0 | 0.03602 | 0.0006105 | 3946.4348 | 238738 | 232640.554
38960.3763 | 85 | 1 | 38960.3763 | 1 | 0 |  | 1899.5 | 2038.5 | 5.1893 | 0.06105 | 0.06105 | 0 | 0.051893 | 0.0006105 | 0.0006105 | 0 | 0.051282 | 0.0006105 | 2742.1327 | 238738 | 230141.6008
38960.3768 | 129 | 1 | 38960.3768 | 1 | 0 |  | 1941.5 | 2080.5 | 7.8755 | 0.06105 | 0.06105 | 0 | 0.078755 | 0.0006105 | 0.0006105 | 0 | 0.078144 | 0.0006105 | 1765.1464 | 238738 | 225743.443
38960.3773 | 92 | 1 | 38960.3773 | 2 | 0 |  | 1983.5 | 2122.5 | 5.6166 | 0.06105 | 0.1221 | 0 | 0.056166 | 0.0006105 | 0.001221 | 0 | 0.055556 | 0.001221 | 2523.5177 | 119319 | 229345.7877
38960.3778 | 143 | 1 | 38960.3778 | 1 | 0 |  | 2025.5 | 2164.5 | 8.7302 | 0.06105 | 0.06105 | 0 | 0.087302 | 0.0006105 | 0.0006105 | 0 | 0.086691 | 0.0006105 | 1581.2582 | 238738 | 224344.0292
38960.3783 | 202 | 1 | 38960.3783 | 232 | 0 |  | 2067.5 | 2206.5 | 12.3321 | 0.06105 | 14.1636 | 0 | 0.12332 | 0.0006105 | 0.14164 | 0 | 0.12271 | 0.14164 | 1088.3338 | 929.4741 | 197309.8805
38960.3788 | 253 | 1 | 38960.3788 | 6 | 0 |  | 2109.5 | 2248.5 | 15.4457 | 0.06105 | 0.3663 | 0 | 0.15446 | 0.0006105 | 0.003663 | 0 | 0.15385 | 0.003663 | 847.3815 | 39706.3333 | 212901.8089
38960.3792 | 340 | 0 | 38960.3793 | 917 | 1 |  | 2151.5 | 2290.5 | 20.757 | 0 | 55.9829 | 0.06105 | 0.20757 | 0 | 0.55983 | 0.0006105 | 0.20757 | 0.55922 | 602.4647 | 160.7402 | 602.2571
38960.3797 | 342 | 0 | 38960.3797 | 1236 | 0 |  | 2193.5 | 2332.5 | 20.8791 | 0 | 75.4579 | 0 | 0.20879 | 0 | 0.75458 | 0 | 0.20879 | 0.75458 | 598.3567 | 93.2346 | 598.1479
38960.3802 | 425 | 0 | 38960.3802 | 287 | 0 |  | 2235.5 | 2374.5 | 25.9463 | 0 | 17.5214 | 0 | 0.25946 | 0 | 0.17521 | 0 | 0.25946 | 0.17521 | 461.9718 | 732.1882 | 461.7123
38960.3807 | 434 | 0 | 38960.3807 | 295 | 0 |  | 2277.5 | 2416.5 | 26.4957 | 0 | 18.0098 | 0 | 0.26496 | 0 | 0.1801 | 0 | 0.26496 | 0.1801 | 450.318 | 709.6203 | 450.053
38960.3812 | 538 | 0 | 38960.3812 | 646 | 0 |  | 2319.5 | 2458.5 | 32.8449 | 0 | 39.4383 | 0 | 0.32845 | 0 | 0.39438 | 0 | 0.32845 | 0.39438 | 343.9368 | 269.7183 | 343.6084
38960.3817 | 1515 | 0 | 38960.3817 | 1703 | 0 |  | 2361.5 | 2500.5 | 92.4908 | 0 | 103.9683 | 0 | 0.92491 | 0 | 1.0397 | 0 | 0.92491 | 1.0397 | 57.6488 | 40.2454 | 56.7239
38960.3822 | 1778 | 0 | 38960.3822 | 1978 | 0 |  | 2403.5 | 2542.5 | 108.547 | 0 | 120.757 | 0 | 1.0855 | 0 | 1.2076 | 0 | 1.0855 | 1.2076 | 34.3296 | 20.7472 | 33.2441
38960.3827 | 1811 | 0 | 38960.3827 | 2045 | 0 |  | 2445.5 | 2584.5 | 110.5617 | 0 | 124.8474 | 0 | 1.1056 | 0 | 1.2485 | 0 | 1.1056 | 1.2485 | 31.8818 | 16.7912 | 30.7762
38960.3831 | 2111 | 0 | 38960.3831 | 2304 | 0 |  | 2487.5 | 2626.5 | 128.8767 | 0 | 140.6593 | 0 | 1.2888 | 0 | 1.4066 | 0 | 1.2888 | 1.4066 | 13.1397 | 3.6623 | 11.851
38960.3836 | 1756 | 0 | 38960.3836 | 2311 | 0 |  | 2529.5 | 2668.5 | 107.2039 | 0 | 141.0867 | 0 | 1.072 | 0 | 1.4109 | 0 | 1.072 | 1.4109 | 36.0125 | 3.3483 | 34.9405
38960.3841 | 1707 | 0 | 38960.3841 | 1812 | 0 |  | 2571.5 | 2710.5 | 104.2125 | 0 | 110.6227 | 0 | 1.0421 | 0 | 1.1062 | 0 | 1.0421 | 1.1062 | 39.9168 | 31.8091 | 38.8747
38960.3846 | 2200 | 0 | 38960.3846 | 1857 | 0 |  | 2613.5 | 2752.5 | 134.3101 | 0 | 113.37 | 0 | 1.3431 | 0 | 1.1337 | 0 | 1.3431 | 1.1337 | 8.5627 | 28.615 | 7.2196
38960.3851 | 1810 | 0 | 38960.3851 | 2297 | 0 |  | 2655.5 | 2794.5 | 110.5006 | 0 | 140.232 | 0 | 1.105 | 0 | 1.4023 | 0 | 1.105 | 1.4023 | 31.9547 | 3.9782 | 30.8497
38960.3856 | 1770 | 0 | 38960.3856 | 1912 | 0 |  | 2697.5 | 2836.5 | 108.0586 | 0 | 116.7277 | 0 | 1.0806 | 0 | 1.1673 | 0 | 1.0806 | 1.1673 | 34.9367 | 24.9153 | 33.8561
38960.3861 | 2222 | 0 | 38960.3861 | 2258 | 0 |  | 2739.5 | 2878.5 | 135.6532 | 0 | 137.851 | 0 | 1.3565 | 0 | 1.3785 | 0 | 1.3565 | 1.3785 | 7.4878 | 5.7741 | 6.1313
38960.3865 | 2130 | 0 | 38960.3866 | 2302 | 0 |  | 2781.5 | 2920.5 | 130.0366 | 0 | 140.5372 | 0 | 1.3004 | 0 | 1.4054 | 0 | 1.3004 | 1.4054 | 12.1305 | 3.7524 | 10.8302
38960.387 | 2112 | 0 | 38960.387 | 2058 | 0 |  | 2823.5 | 2962.5 | 128.9377 | 0 | 125.641 | 0 | 1.2894 | 0 | 1.2564 | 0 | 1.2894 | 1.2564 | 13.0862 | 16.0534 | 11.7968
38960.3875 | 1873 | 0 | 38960.3875 | 2300 | 0 |  | 2865.5 | 3004.5 | 114.3468 | 0 | 140.4151 | 0 | 1.1435 | 0 | 1.4042 | 0 | 1.1435 | 1.4042 | 27.5163 | 3.8426 | 26.3728
38960.388 | 1844 | 0 | 38960.388 | 2354 | 0 |  | 2907.5 | 3046.5 | 112.5763 | 0 | 143.7118 | 0 | 1.1258 | 0 | 1.4371 | 0 | 1.1258 | 1.4371 | 29.5217 | 1.4605 | 28.3959
38960.3885 | 2254 | 0 | 38960.3885 | 2321 | 0 |  | 2949.5 | 3088.5 | 137.6068 | 0 | 141.6972 | 0 | 1.3761 | 0 | 1.417 | 0 | 1.3761 | 1.417 | 5.9618 | 2.9031 | 4.5858
38960.389 | 1743 | 0 | 38960.389 | 2319 | 0 |  | 2991.5 | 3130.5 | 106.4103 | 0 | 141.5751 | 0 | 1.0641 | 0 | 1.4158 | 0 | 1.0641 | 1.4158 | 37.027 | 2.9918 | 35.9629
38960.3895 | 1886 | 0 | 38960.3895 | 1895 | 0 |  | 3033.5 | 3172.5 | 115.1404 | 0 | 115.6899 | 0 | 1.1514 | 0 | 1.1569 | 0 | 1.1514 | 1.1569 | 26.6373 | 26.0359 | 25.4859
38960.3899 | 2019 | 0 | 38960.39 | 2152 | 0 |  | 3075.5 | 3214.5 | 123.2601 | 0 | 131.3797 | 0 | 1.2326 | 0 | 1.3138 | 0 | 1.2326 | 1.3138 | 18.2952 | 10.9842 | 17.0626
38960.3904 | 2189 | 0 | 38960.3904 | 2234 | 0 |  | 3117.5 | 3256.5 | 133.6386 | 0 | 136.3858 | 0 | 1.3364 | 0 | 1.3639 | 0 | 1.3364 | 1.3639 | 9.1083 | 6.9105 | 7.7719
38960.3909 | 1935 | 0 | 38960.3909 | 2198 | 0 |  | 3159 | 3298 | 118.1319 | 0 | 134.188 | 0 | 1.1813 | 0 | 1.3419 | 0 | 1.1813 | 1.3419 | 23.4305 | 8.6615 | 22.2492
38960.3914 | 2263 | 0 | 38960.3914 | 2190 | 0 |  | 3201 | 3340 | 138.1563 | 0 | 133.6996 | 0 | 1.3816 | 0 | 1.337 | 0 | 1.3816 | 1.337 | 5.5404 | 9.0584 | 4.1589
38960.3919 | 1930 | 0 | 38960.3919 | 2055 | 0 |  | 3243.5 | 3382.5 | 117.8266 | 0 | 125.4579 | 0 | 1.1783 | 0 | 1.2546 | 0 | 1.1783 | 1.2546 | 23.7503 | 16.2229 | 22.572
38960.3924 | 2243 | 0 | 38960.3924 | 2372 | 0 |  | 3285.5 | 3424.5 | 136.9353 | 0 | 144.8107 | 0 | 1.3694 | 0 | 1.4481 | 0 | 1.3694 | 1.4481 | 6.4815 | 0.69056 | 5.1121

## A2-C5
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 145.8718 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38960.353 | 1 | 0 | 38960.353 | 1 | 0 |  | -119 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3534 | 1 | 0 | 38960.3535 | 1 | 0 |  | -77 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3539 | 1 | 0 | 38960.354 | 1 | 0 |  | -35 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3544 | 1 | 0 | 38960.3544 | 1 | 0 |  | 7 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3549 | 1 | 0 | 38960.3549 | 1 | 0 |  | 49 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3554 | 1 | 0 | 38960.3554 | 1 | 0 |  | 91 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3559 | 1 | 0 | 38960.3559 | 1 | 0 |  | 133 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3564 | 1 | 0 | 38960.3564 | 1 | 0 |  | 175 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3569 | 1 | 0 | 38960.3569 | 1 | 0 |  | 217 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3573 | 2 | 0 | 38960.3574 | 1 | 0 |  | 259 | 398 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119369 | 238838 | 119368.9988
38960.3578 | 1 | 0 | 38960.3578 | 1 | 0 |  | 301 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3583 | 1 | 0 | 38960.3583 | 1 | 0 |  | 343 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3588 | 1 | 0 | 38960.3588 | 1 | 0 |  | 384.5 | 523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3593 | 1 | 0 | 38960.3593 | 1 | 0 |  | 426.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3598 | 1 | 0 | 38960.3598 | 1 | 0 |  | 469 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3603 | 1 | 0 | 38960.3603 | 1 | 0 |  | 511 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3607 | 1 | 0 |  | 1 | 0 |  | 552 | 691 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3612 | 1 | 0 | 38960.3613 | 1 | 0 |  | 595 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3617 | 1 | 0 | 38960.3617 | 1 | 0 |  | 637 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3622 | 1 | 0 | 38960.3622 | 1 | 0 |  | 678.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3627 | 1 | 0 | 38960.3627 | 1 | 0 |  | 720.5 | 859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3632 | 1 | 0 | 38960.3632 | 1 | 0 |  | 762.5 | 901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3637 | 1 | 0 | 38960.3637 | 1 | 0 |  | 804.5 | 943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3641 | 1 | 0 | 38960.3642 | 1 | 0 |  | 846.5 | 985.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3646 | 1 | 0 | 38960.3646 | 1 | 0 |  | 888.5 | 1027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3651 | 1 | 0 | 38960.3651 | 1 | 0 |  | 930.5 | 1069.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3656 | 1 | 1 |  | 1 | 0 |  | 972 | 1111 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 570435902.44 | 238838 | 238638.0837
38960.3661 | 1 | 0 | 38960.3661 | 1 | 0 |  | 1014.5 | 1153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3666 | 1 | 0 | 38960.3666 | 1 | 0 |  | 1056.5 | 1195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3671 | 1 | 0 | 38960.3671 | 1 | 0 |  | 1098.5 | 1237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3675 | 1 | 0 | 38960.3676 | 1 | 0 |  | 1140.5 | 1279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.368 | 1 | 0 | 38960.368 | 1 | 0 |  | 1182.5 | 1321.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3685 | 1 | 0 | 38960.3685 | 1 | 0 |  | 1224.5 | 1363.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.369 | 1 | 0 | 38960.369 | 1 | 0 |  | 1266.5 | 1405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3695 | 1 | 0 | 38960.3695 | 1 | 0 |  | 1308.5 | 1447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.37 | 1 | 0 | 38960.37 | 1 | 0 |  | 1350.5 | 1489.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3705 | 1 | 0 | 38960.3705 | 1 | 0 |  | 1392.5 | 1531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3709 | 1 | 0 | 38960.371 | 1 | 0 |  | 1434.5 | 1573.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3714 | 1 | 0 | 38960.3714 | 1 | 0 |  | 1476.5 | 1615.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38960.3719 | 4 | 0 | 38960.3719 | 1 | 0 |  | 1518.5 | 1657.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 59634.5 | 238838 | 59634.4976
38960.3724 | 4 | 0 | 38960.3724 | 1 | 0 |  | 1560.5 | 1699.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 59634.5 | 238838 | 59634.4976
38960.3729 | 2 | 0 | 38960.3729 | 1 | 0 |  | 1602.5 | 1741.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119369 | 238838 | 119368.9988
38960.3734 | 3 | 0 | 38960.3734 | 1 | 0 |  | 1644.5 | 1783.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 79546 | 238838 | 79545.9982
38960.3739 | 2 | 0 | 38960.3739 | 1 | 0 |  | 1686.5 | 1825.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119369 | 238838 | 119368.9988
38960.3744 | 6 | 0 | 38960.3744 | 1 | 0 |  | 1728.5 | 1867.5 | 0.3663 | 0 | 0.06105 | 0 | 0.003663 | 0 | 0.0006105 | 0 | 0.003663 | 0.0006105 | 39723 | 238838 | 39722.9963
38960.3748 | 11 | 0 | 38960.3748 | 1 | 0 |  | 1770.5 | 1909.5 | 0.67155 | 0 | 0.06105 | 0 | 0.0067155 | 0 | 0.0006105 | 0 | 0.0067155 | 0.0006105 | 21621.6364 | 238838 | 21621.6296
38960.3753 | 4 | 0 | 38960.3753 | 1 | 0 |  | 1812.5 | 1951.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 59634.5 | 238838 | 59634.4976
38960.3758 | 50 | 1 | 38960.3758 | 1 | 0 |  | 1854.5 | 1993.5 | 3.0525 | 0.06105 | 0.06105 | 0 | 0.030525 | 0.0006105 | 0.0006105 | 0 | 0.029915 | 0.0006105 | 4774.2857 | 238838 | 233740.1344
38960.3763 | 79 | 1 | 38960.3763 | 1 | 0 |  | 1896.5 | 2035.5 | 4.823 | 0.06105 | 0.06105 | 0 | 0.04823 | 0.0006105 | 0.0006105 | 0 | 0.047619 | 0.0006105 | 2962.0415 | 238838 | 230841.3481
38960.3768 | 127 | 1 | 38960.3768 | 2 | 0 |  | 1938.5 | 2077.5 | 7.7534 | 0.06105 | 0.1221 | 0 | 0.077534 | 0.0006105 | 0.001221 | 0 | 0.076923 | 0.001221 | 1795.5516 | 119369 | 225948.7141
38960.3773 | 90 | 0 | 38960.3773 | 1314 | 0 |  | 1980.5 | 2119.5 | 5.4945 | 0 | 80.2198 | 0 | 0.054945 | 0 | 0.8022 | 0 | 0.054945 | 0.8022 | 2554.8667 | 81.8402 | 2554.8117
38960.3778 | 120 | 0 | 38960.3778 | 2165 | 0 |  | 2022.5 | 2161.5 | 7.326 | 0 | 132.1734 | 0 | 0.07326 | 0 | 1.3217 | 0 | 0.07326 | 1.3217 | 1891.15 | 10.364 | 1891.0767
38960.3782 | 238 | 0 | 38960.3783 | 2200 | 0 |  | 2064.5 | 2203.5 | 14.5299 | 0 | 134.3101 | 0 | 0.1453 | 0 | 1.3431 | 0 | 0.1453 | 1.3431 | 903.9412 | 8.6082 | 903.7959
38960.3787 | 243 | 0 | 38960.3787 | 1827 | 0 |  | 2106.5 | 2245.5 | 14.8352 | 0 | 111.5385 | 0 | 0.14835 | 0 | 1.1154 | 0 | 0.14835 | 1.1154 | 883.284 | 30.7816 | 883.1356
38960.3792 | 271 | 0 | 38960.3792 | 1924 | 0 |  | 2148.5 | 2287.5 | 16.5446 | 0 | 117.4603 | 0 | 0.16545 | 0 | 1.1746 | 0 | 0.16545 | 1.1746 | 781.69 | 24.1881 | 781.5246
38960.3797 | 329 | 0 | 38960.3797 | 2076 | 0 |  | 2190.5 | 2329.5 | 20.0855 | 0 | 126.7399 | 0 | 0.20085 | 0 | 1.2674 | 0 | 0.20085 | 1.2674 | 626.2553 | 15.0954 | 626.0545
38960.3802 | 350 | 0 | 38960.3802 | 1870 | 0 |  | 2232.5 | 2371.5 | 21.3675 | 0 | 114.1636 | 0 | 0.21368 | 0 | 1.1416 | 0 | 0.21368 | 1.1416 | 582.68 | 27.7743 | 582.4663
38960.3807 | 388 | 0 | 38960.3807 | 1946 | 0 |  | 2274.5 | 2413.5 | 23.6874 | 0 | 118.8034 | 0 | 0.23687 | 0 | 1.188 | 0 | 0.23687 | 1.188 | 515.8196 | 22.7842 | 515.5827
38960.3812 | 536 | 0 | 38960.3812 | 2297 | 0 |  | 2316.5 | 2455.5 | 32.7228 | 0 | 140.232 | 0 | 0.32723 | 0 | 1.4023 | 0 | 0.32723 | 1.4023 | 345.7799 | 4.0218 | 345.4526
38960.3816 | 883 | 0 | 38960.3817 | 2255 | 0 |  | 2358.5 | 2497.5 | 53.9072 | 0 | 137.6679 | 0 | 0.53907 | 0 | 1.3767 | 0 | 0.53907 | 1.3767 | 170.598 | 5.9592 | 170.0589
38960.3821 | 1955 | 0 | 38960.3821 | 2096 | 0 |  | 2400.5 | 2539.5 | 119.3529 | 0 | 127.9609 | 0 | 1.1935 | 0 | 1.2796 | 0 | 1.1935 | 1.2796 | 22.2189 | 13.9971 | 21.0254
38960.3826 | 2160 | 0 | 38960.3826 | 1899 | 0 |  | 2442.5 | 2581.5 | 131.8681 | 0 | 115.9341 | 0 | 1.3187 | 0 | 1.1593 | 0 | 1.3187 | 1.1593 | 10.6194 | 25.8231 | 9.3008
38960.3831 | 2034 | 0 | 38960.3831 | 2288 | 0 |  | 2484.5 | 2623.5 | 124.1758 | 0 | 139.6825 | 0 | 1.2418 | 0 | 1.3968 | 0 | 1.2418 | 1.3968 | 17.472 | 4.4309 | 16.2302
38960.3836 | 1808 | 0 | 38960.3836 | 2044 | 0 |  | 2526.5 | 2665.5 | 110.3785 | 0 | 124.7863 | 0 | 1.1038 | 0 | 1.2479 | 0 | 1.1038 | 1.2479 | 32.156 | 16.8973 | 31.0522
38960.3841 | 1915 | 0 | 38960.3841 | 1921 | 0 |  | 2568.5 | 2707.5 | 116.9109 | 0 | 117.2772 | 0 | 1.1691 | 0 | 1.1728 | 0 | 1.1691 | 1.1728 | 24.7718 | 24.3821 | 23.6027
38960.3846 | 2214 | 0 | 38960.3846 | 2005 | 0 |  | 2610.5 | 2749.5 | 135.1648 | 0 | 122.4054 | 0 | 1.3516 | 0 | 1.2241 | 0 | 1.3516 | 1.2241 | 7.9214 | 19.1711 | 6.5698
38960.385 | 1803 | 0 | 38960.3851 | 2045 | 0 |  | 2652.5 | 2791.5 | 110.0733 | 0 | 124.8474 | 0 | 1.1007 | 0 | 1.2485 | 0 | 1.1007 | 1.2485 | 32.5225 | 16.8401 | 31.4217
38960.3855 | 1793 | 0 | 38960.3855 | 2316 | 0 |  | 2694.5 | 2833.5 | 109.4628 | 0 | 141.3919 | 0 | 1.0946 | 0 | 1.4139 | 0 | 1.0946 | 1.4139 | 33.2616 | 3.1684 | 32.1669
38960.386 | 2016 | 0 | 38960.386 | 2030 | 0 |  | 2736.5 | 2875.5 | 123.0769 | 0 | 123.9316 | 0 | 1.2308 | 0 | 1.2393 | 0 | 1.2308 | 1.2393 | 18.5208 | 17.7034 | 17.2901
38960.3865 | 1740 | 0 | 38960.3865 | 1972 | 0 |  | 2778.5 | 2917.5 | 106.2271 | 0 | 120.3907 | 0 | 1.0623 | 0 | 1.2039 | 0 | 1.0623 | 1.2039 | 37.3207 | 21.1653 | 36.2584
38960.387 | 2211 | 0 | 38960.387 | 1837 | 0 |  | 2820.5 | 2959.5 | 134.9817 | 0 | 112.149 | 0 | 1.3498 | 0 | 1.1215 | 0 | 1.3498 | 1.1215 | 8.0678 | 30.0697 | 6.718
38960.3875 | 2016 | 0 | 38960.3875 | 1986 | 0 |  | 2862.5 | 3001.5 | 123.0769 | 0 | 121.2454 | 0 | 1.2308 | 0 | 1.2125 | 0 | 1.2308 | 1.2125 | 18.5208 | 20.3112 | 17.2901
38960.388 | 1892 | 0 | 38960.388 | 1920 | 0 |  | 2904.5 | 3043.5 | 115.5067 | 0 | 117.2161 | 0 | 1.1551 | 0 | 1.1722 | 0 | 1.1551 | 1.1722 | 26.2886 | 24.4469 | 25.1335
38960.3884 | 2028 | 0 | 38960.3885 | 2034 | 0 |  | 2946.5 | 3085.5 | 123.8095 | 0 | 124.1758 | 0 | 1.2381 | 0 | 1.2418 | 0 | 1.2381 | 1.2418 | 17.8195 | 17.472 | 16.5814
38960.3889 | 1992 | 0 | 38960.3889 | 2373 | 0 |  | 2988.5 | 3127.5 | 121.6117 | 0 | 144.8718 | 0 | 1.2161 | 0 | 1.4487 | 0 | 1.2161 | 1.4487 | 19.9488 | 0.69027 | 18.7327
38960.3894 | 2231 | 0 | 38960.3894 | 2336 | 0 |  | 3030.5 | 3169.5 | 136.2027 | 0 | 142.6129 | 0 | 1.362 | 0 | 1.4261 | 0 | 1.362 | 1.4261 | 7.0991 | 2.2851 | 5.737
38960.3899 | 2004 | 0 | 38960.3899 | 2351 | 0 |  | 3072.5 | 3211.5 | 122.3443 | 0 | 143.5287 | 0 | 1.2234 | 0 | 1.4353 | 0 | 1.2234 | 1.4353 | 19.2305 | 1.6325 | 18.0071
38960.3904 | 1965 | 0 | 38960.3904 | 2098 | 0 |  | 3114.5 | 3253.5 | 119.9634 | 0 | 128.083 | 0 | 1.1996 | 0 | 1.2808 | 0 | 1.1996 | 1.2808 | 21.5969 | 13.8885 | 20.3973
38960.3909 | 1984 | 0 | 38960.3909 | 1988 | 0 |  | 3156.5 | 3295.5 | 121.1233 | 0 | 121.3675 | 0 | 1.2112 | 0 | 1.2137 | 0 | 1.2112 | 1.2137 | 20.4325 | 20.1901 | 19.2212
38960.3914 | 1952 | 0 | 38960.3914 | 2280 | 0 |  | 3198.5 | 3337.5 | 119.1697 | 0 | 139.1941 | 0 | 1.1917 | 0 | 1.3919 | 0 | 1.1917 | 1.3919 | 22.4068 | 4.7974 | 21.2151
38960.3919 | 2177 | 0 | 38960.3919 | 2116 | 0 |  | 3240.5 | 3379.5 | 132.906 | 0 | 129.1819 | 0 | 1.3291 | 0 | 1.2918 | 0 | 1.3291 | 1.2918 | 9.7556 | 12.9197 | 8.4266
38960.3923 | 2112 | 0 | 38960.3923 | 2042 | 0 |  | 3282.5 | 3421.5 | 128.9377 | 0 | 124.6642 | 0 | 1.2894 | 0 | 1.2466 | 0 | 1.2894 | 1.2466 | 13.1335 | 17.0118 | 11.8441

## A2-B4
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 136.5311 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38960.3529 | 1 | 0 | 38960.353 | 1 | 0 |  | -122 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3534 | 1 | 0 | 38960.3534 | 1 | 0 |  | -80 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3539 | 1 | 0 | 38960.3539 | 1 | 0 |  | -38 | 101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3544 | 1 | 0 | 38960.3544 | 1 | 0 |  | 4 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3549 | 1 | 0 | 38960.3549 | 1 | 0 |  | 46 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3554 | 2 | 0 | 38960.3554 | 1 | 0 |  | 88 | 227 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 111719 | 223538 | 111718.9988
38960.3558 | 1 | 0 | 38960.3559 | 1 | 0 |  | 130 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3563 | 1 | 0 | 38960.3564 | 1 | 0 |  | 172 | 311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3568 | 1 | 0 | 38960.3568 | 1 | 0 |  | 214 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3573 | 1 | 0 | 38960.3573 | 1 | 0 |  | 256 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3578 | 1 | 0 | 38960.3578 | 1 | 0 |  | 298 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3583 | 1 | 0 | 38960.3583 | 1 | 0 |  | 340 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3588 | 1 | 0 | 38960.3588 | 1 | 0 |  | 382 | 521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3592 | 1 | 0 | 38960.3593 | 1 | 0 |  | 424 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3597 | 1 | 0 | 38960.3598 | 1 | 0 |  | 466 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3602 | 1 | 0 | 38960.3602 | 1 | 0 |  | 508 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3607 | 1 | 0 | 38960.3607 | 1 | 0 |  | 550 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3612 | 2 | 0 | 38960.3612 | 1 | 0 |  | 592 | 731 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 111719 | 223538 | 111718.9988
38960.3617 | 1 | 0 | 38960.3617 | 2 | 0 |  | 634 | 773 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 223538 | 111719 | 223537.9994
38960.3622 | 1 | 0 | 38960.3622 | 1 | 0 |  | 676 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3627 | 1 | 0 | 38960.3627 | 1 | 0 |  | 718 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3631 | 1 | 0 | 38960.3632 | 1 | 0 |  | 760 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3636 | 1 | 0 | 38960.3636 | 1 | 0 |  | 802 | 941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3641 | 1 | 0 | 38960.3641 | 1 | 0 |  | 844 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3646 | 1 | 0 | 38960.3646 | 1 | 0 |  | 886 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3651 | 1 | 0 | 38960.3651 | 1 | 0 |  | 928 | 1067 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3656 | 1 | 0 | 38960.3656 | 1 | 0 |  | 970 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3661 | 1 | 0 | 38960.3661 | 1 | 0 |  | 1012 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3665 | 1 | 0 | 38960.3666 | 1 | 0 |  | 1054 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.367 | 1 | 0 | 38960.367 | 1 | 0 |  | 1096 | 1235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3675 | 1 | 1 | 38960.3675 | 1 | 0 |  | 1138 | 1277 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 499692374.44 | 223538 | 223338.0894
38960.368 | 1 | 0 | 38960.368 | 1 | 0 |  | 1180 | 1319 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3685 | 1 | 0 | 38960.3685 | 1 | 0 |  | 1222 | 1361 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.369 | 1 | 0 | 38960.369 | 1 | 0 |  | 1264 | 1403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3695 | 1 | 0 | 38960.3695 | 1 | 0 |  | 1306 | 1445 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3699 | 1 | 0 | 38960.37 | 1 | 0 |  | 1348 | 1487 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3704 | 1 | 1 | 38960.3705 | 1 | 0 |  | 1390 | 1529 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 499692374.44 | 223538 | 223338.0894
38960.3709 | 1 | 0 | 38960.3709 | 1 | 0 |  | 1432 | 1571 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3714 | 1 | 0 | 38960.3714 | 1 | 0 |  | 1474 | 1613 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223538 | 223538 | 223537.9994
38960.3719 | 2 | 0 | 38960.3719 | 3 | 0 |  | 1516 | 1655 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 111719 | 74446 | 111718.9988
38960.3724 | 4 | 0 | 38960.3724 | 4 | 0 |  | 1558 | 1697 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 55809.5 | 55809.5 | 55809.4976
38960.3729 | 1 | 0 | 38960.3729 | 2 | 0 |  | 1600 | 1739 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 223538 | 111719 | 223537.9994
38960.3733 | 2 | 0 | 38960.3734 | 2 | 0 |  | 1642 | 1781 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 111719 | 111719 | 111718.9988
38960.3738 | 2 | 0 | 38960.3739 | 2 | 0 |  | 1684 | 1823 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 111719 | 111719 | 111718.9988
38960.3743 | 5 | 0 | 38960.3743 | 5 | 0 |  | 1726 | 1865 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 44627.6 | 44627.6 | 44627.5969
38960.3748 | 8 | 0 | 38960.3748 | 10 | 0 |  | 1768 | 1907 | 0.4884 | 0 | 0.6105 | 0 | 0.004884 | 0 | 0.006105 | 0 | 0.004884 | 0.006105 | 27854.75 | 22263.8 | 27854.7451
38960.3753 | 4 | 0 | 38960.3753 | 3 | 0 |  | 1809.5 | 1948.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 55809.5 | 74446 | 55809.4976
38960.3758 | 50 | 0 | 38960.3758 | 45 | 0 |  | 1852 | 1991 | 3.0525 | 0 | 2.7473 | 0 | 0.030525 | 0 | 0.027473 | 0 | 0.030525 | 0.027473 | 4372.76 | 4869.7333 | 4372.7295
38960.3763 | 85 | 0 | 38960.3763 | 76 | 0 |  | 1894 | 2033 | 5.1893 | 0 | 4.6398 | 0 | 0.051893 | 0 | 0.046398 | 0 | 0.051893 | 0.046398 | 2531.0353 | 2842.6053 | 2530.9834
38960.3767 | 120 | 0 | 38960.3768 | 103 | 0 |  | 1935.5 | 2074.5 | 7.326 | 0 | 6.2882 | 0 | 0.07326 | 0 | 0.062882 | 0 | 0.07326 | 0.062882 | 1763.65 | 2071.2427 | 1763.5767
38960.3772 | 94 | 0 | 38960.3772 | 85 | 0 |  | 1977.5 | 2116.5 | 5.7387 | 0 | 5.1893 | 0 | 0.057387 | 0 | 0.051893 | 0 | 0.057387 | 0.051893 | 2279.1277 | 2531.0353 | 2279.0703
38960.3777 | 138 | 0 | 38960.3777 | 127 | 0 |  | 2020 | 2159 | 8.4249 | 0 | 7.7534 | 0 | 0.084249 | 0 | 0.077534 | 0 | 0.084249 | 0.077534 | 1520.5652 | 1660.9291 | 1520.481
38960.3782 | 190 | 0 | 38960.3782 | 217 | 0 |  | 2061.5 | 2200.5 | 11.5995 | 0 | 13.2479 | 0 | 0.116 | 0 | 0.13248 | 0 | 0.116 | 0.13248 | 1077.0421 | 930.5899 | 1076.9261
38960.3787 | 282 | 0 | 38960.3787 | 242 | 0 |  | 2104 | 2243 | 17.2161 | 0 | 14.7741 | 0 | 0.17216 | 0 | 0.14774 | 0 | 0.17216 | 0.14774 | 693.0426 | 824.124 | 692.8704
38960.3792 | 329 | 0 | 38960.3792 | 270 | 0 |  | 2146 | 2285 | 20.0855 | 0 | 16.4835 | 0 | 0.20085 | 0 | 0.16484 | 0 | 0.20085 | 0.16484 | 579.7508 | 728.2889 | 579.5499
38960.3797 | 381 | 0 | 38960.3797 | 305 | 0 |  | 2187.5 | 2326.5 | 23.2601 | 0 | 18.6203 | 0 | 0.2326 | 0 | 0.1862 | 0 | 0.2326 | 0.1862 | 486.9764 | 633.2393 | 486.7438
38960.3802 | 406 | 0 | 38960.3802 | 423 | 0 |  | 2229.5 | 2368.5 | 24.7863 | 0 | 25.8242 | 0 | 0.24786 | 0 | 0.25824 | 0 | 0.24786 | 0.25824 | 450.8325 | 428.695 | 450.5846
38960.3806 | 468 | 0 | 38960.3806 | 414 | 0 |  | 2271.5 | 2410.5 | 28.5714 | 0 | 25.2747 | 0 | 0.28571 | 0 | 0.25275 | 0 | 0.28571 | 0.25275 | 377.859 | 440.1884 | 377.5733
38960.3811 | 562 | 0 | 38960.3811 | 509 | 0 |  | 2313.5 | 2452.5 | 34.3101 | 0 | 31.0745 | 0 | 0.3431 | 0 | 0.31074 | 0 | 0.3431 | 0.31074 | 297.9324 | 339.3674 | 297.5893
38960.3816 | 603 | 0 | 38960.3816 | 705 | 0 |  | 2355.5 | 2494.5 | 36.8132 | 0 | 43.0403 | 0 | 0.36813 | 0 | 0.4304 | 0 | 0.36813 | 0.4304 | 270.8756 | 217.217 | 270.5075
38960.3821 | 1854 | 0 | 38960.3821 | 1676 | 0 |  | 2397.5 | 2536.5 | 113.1868 | 0 | 102.3199 | 0 | 1.1319 | 0 | 1.0232 | 0 | 1.1319 | 1.0232 | 20.6246 | 33.4356 | 19.4927
38960.3826 | 1741 | 0 | 38960.3826 | 1965 | 0 |  | 2439.5 | 2578.5 | 106.2882 | 0 | 119.9634 | 0 | 1.0629 | 0 | 1.1996 | 0 | 1.0629 | 1.1996 | 28.4538 | 13.8107 | 27.3909
38960.3831 | 1969 | 0 | 38960.3831 | 1818 | 0 |  | 2481.5 | 2620.5 | 120.2076 | 0 | 110.989 | 0 | 1.2021 | 0 | 1.1099 | 0 | 1.2021 | 1.1099 | 13.5795 | 23.0132 | 12.3774
38960.3836 | 1761 | 0 | 38960.3836 | 1947 | 0 |  | 2523.5 | 2662.5 | 107.5092 | 0 | 118.8645 | 0 | 1.0751 | 0 | 1.1886 | 0 | 1.0751 | 1.1886 | 26.9949 | 14.8629 | 25.9198
38960.384 | 1678 | 0 | 38960.3841 | 1905 | 0 |  | 2565.5 | 2704.5 | 102.442 | 0 | 116.3004 | 0 | 1.0244 | 0 | 1.163 | 0 | 1.0244 | 1.163 | 33.2765 | 17.3953 | 32.2521
38960.3845 | 1763 | 0 | 38960.3845 | 2125 | 0 |  | 2607.5 | 2746.5 | 107.6313 | 0 | 129.7314 | 0 | 1.0763 | 0 | 1.2973 | 0 | 1.0763 | 1.2973 | 26.8508 | 5.2414 | 25.7745
38960.385 | 2034 | 0 | 38960.385 | 1938 | 0 |  | 2649.5 | 2788.5 | 124.1758 | 0 | 118.315 | 0 | 1.2418 | 0 | 1.1832 | 0 | 1.2418 | 1.1832 | 9.9499 | 15.3963 | 8.7081
38960.3855 | 2002 | 0 | 38960.3855 | 1859 | 0 |  | 2691.5 | 2830.5 | 122.2222 | 0 | 113.4921 | 0 | 1.2222 | 0 | 1.1349 | 0 | 1.2222 | 1.1349 | 11.7073 | 20.3002 | 10.4851
38960.386 | 2010 | 0 | 38960.386 | 2179 | 0 |  | 2733.5 | 2872.5 | 122.7106 | 0 | 133.0281 | 0 | 1.2271 | 0 | 1.3303 | 0 | 1.2271 | 1.3303 | 11.2627 | 2.6333 | 10.0356
38960.3865 | 1970 | 0 | 38960.3865 | 2220 | 0 |  | 2775.5 | 2914.5 | 120.2686 | 0 | 135.5311 | 0 | 1.2027 | 0 | 1.3553 | 0 | 1.2027 | 1.3553 | 13.5218 | 0.73784 | 12.3191
38960.387 | 1838 | 0 | 38960.387 | 1897 | 0 |  | 2817.5 | 2956.5 | 112.21 | 0 | 115.812 | 0 | 1.1221 | 0 | 1.1581 | 0 | 1.1221 | 1.1581 | 21.6746 | 17.8904 | 20.5525
38960.3874 | 2063 | 0 | 38960.3875 | 1806 | 0 |  | 2859.5 | 2998.5 | 125.9463 | 0 | 110.2564 | 0 | 1.2595 | 0 | 1.1026 | 0 | 1.2595 | 1.1026 | 8.4043 | 23.8306 | 7.1448
38960.3879 | 2166 | 0 | 38960.3879 | 1775 | 0 |  | 2901.5 | 3040.5 | 132.2344 | 0 | 108.3639 | 0 | 1.3223 | 0 | 1.0836 | 0 | 1.3223 | 1.0836 | 3.2493 | 25.9932 | 1.927
38960.3884 | 2165 | 0 | 38960.3884 | 1884 | 0 |  | 2943.5 | 3082.5 | 132.1734 | 0 | 115.0183 | 0 | 1.3217 | 0 | 1.1502 | 0 | 1.3217 | 1.1502 | 3.297 | 18.7038 | 1.9753
38960.3889 | 2217 | 0 | 38960.3889 | 1989 | 0 |  | 2985.5 | 3124.5 | 135.348 | 0 | 121.4286 | 0 | 1.3535 | 0 | 1.2143 | 0 | 1.3535 | 1.2143 | 0.87415 | 12.4374 | 0.47933
38960.3894 | 1778 | 0 | 38960.3894 | 2086 | 0 |  | 3027.5 | 3166.5 | 108.547 | 0 | 127.3504 | 0 | 1.0855 | 0 | 1.2735 | 0 | 1.0855 | 1.2735 | 25.7807 | 7.209 | 24.6952
38960.3899 | 2096 | 0 | 38960.3899 | 2009 | 0 |  | 3069.5 | 3208.5 | 127.9609 | 0 | 122.6496 | 0 | 1.2796 | 0 | 1.2265 | 0 | 1.2796 | 1.2265 | 6.6975 | 11.3181 | 5.4179
38960.3904 | 2076 | 0 | 38960.3904 | 2010 | 0 |  | 3111.5 | 3250.5 | 126.7399 | 0 | 122.7106 | 0 | 1.2674 | 0 | 1.2271 | 0 | 1.2674 | 1.2271 | 7.7254 | 11.2627 | 6.458
38960.3908 | 2033 | 0 | 38960.3909 | 2123 | 0 |  | 3153.5 | 3292.5 | 124.1148 | 0 | 129.6093 | 0 | 1.2411 | 0 | 1.2961 | 0 | 1.2411 | 1.2961 | 10.0039 | 5.3406 | 8.7628
38960.3913 | 1924 | 0 | 38960.3913 | 2033 | 0 |  | 3195.5 | 3334.5 | 117.4603 | 0 | 124.1148 | 0 | 1.1746 | 0 | 1.2411 | 0 | 1.1746 | 1.2411 | 16.236 | 10.0039 | 15.0614
38960.3918 | 2089 | 0 | 38960.3918 | 1961 | 0 |  | 3237.5 | 3376.5 | 127.5336 | 0 | 119.7192 | 0 | 1.2753 | 0 | 1.1972 | 0 | 1.2753 | 1.1972 | 7.0551 | 14.0428 | 5.7797
38960.3923 | 2126 | 0 | 38960.3923 | 2073 | 0 |  | 3279.5 | 3418.5 | 129.7924 | 0 | 126.5568 | 0 | 1.2979 | 0 | 1.2656 | 0 | 1.2979 | 1.2656 | 5.1919 | 7.8813 | 3.894

## A2-B3
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 142.9414 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38960.3529 | 1 | 0 | 38960.3529 | 1 | 0 |  | -124.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3534 | 1 | 0 | 38960.3534 | 1 | 0 |  | -82.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3539 | 1 | 0 | 38960.3539 | 1 | 0 |  | -40.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3544 | 1 | 0 | 38960.3544 | 1 | 0 |  | 1.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3548 | 1 | 0 | 38960.3549 | 1 | 0 |  | 43.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3553 | 1 | 0 | 38960.3553 | 1 | 0 |  | 85.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3558 | 1 | 0 | 38960.3558 | 1 | 0 |  | 127.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3563 | 1 | 0 | 38960.3563 | 1 | 0 |  | 169.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3568 | 1 | 0 | 38960.3568 | 1 | 0 |  | 211.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3573 | 1 | 0 | 38960.3573 | 1 | 0 |  | 253.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3578 | 1 | 0 | 38960.3578 | 1 | 0 |  | 295.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3583 | 1 | 0 | 38960.3583 | 1 | 0 |  | 337.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3587 | 1 | 0 | 38960.3587 | 1 | 0 |  | 379.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3592 | 2 | 0 | 38960.3592 | 1 | 0 |  | 421.5 | 560.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116969 | 234038 | 116968.9988
38960.3597 | 1 | 0 | 38960.3597 | 1 | 0 |  | 463.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3602 | 1 | 0 | 38960.3602 | 1 | 0 |  | 505.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3607 | 1 | 0 | 38960.3607 | 1 | 0 |  | 547 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3612 | 1 | 0 | 38960.3612 | 1 | 0 |  | 589.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3616 | 1 | 0 | 38960.3617 | 1 | 0 |  | 631 | 770 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3621 | 1 | 0 | 38960.3622 | 1 | 0 |  | 673 | 812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3626 | 1 | 0 | 38960.3626 | 1 | 0 |  | 715.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3631 | 1 | 0 | 38960.3631 | 1 | 0 |  | 757.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3636 | 1 | 0 | 38960.3636 | 1 | 0 |  | 799 | 938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3641 | 1 | 0 | 38960.3641 | 1 | 0 |  | 841 | 980 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3646 | 1 | 0 | 38960.3646 | 1 | 0 |  | 883 | 1022 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.365 | 1 | 0 | 38960.3651 | 1 | 0 |  | 925 | 1064 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3655 | 1 | 0 | 38960.3656 | 1 | 0 |  | 967 | 1106 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.366 | 1 | 0 | 38960.366 | 1 | 0 |  | 1009.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3665 | 1 | 0 | 38960.3665 | 1 | 0 |  | 1051 | 1190 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.367 | 1 | 0 | 38960.367 | 1 | 0 |  | 1093 | 1232 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3675 | 1 | 0 | 38960.3675 | 1 | 0 |  | 1135 | 1274 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.368 | 1 | 0 | 38960.368 | 1 | 0 |  | 1177 | 1316 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3684 | 1 | 0 | 38960.3685 | 1 | 0 |  | 1219 | 1358 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3689 | 1 | 0 | 38960.369 | 1 | 0 |  | 1261 | 1400 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3694 | 1 | 0 | 38960.3694 | 1 | 0 |  | 1303 | 1442 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3699 | 1 | 0 | 38960.3699 | 1 | 0 |  | 1345 | 1484 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3704 | 1 | 0 | 38960.3704 | 1 | 0 |  | 1387 | 1526 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3709 | 1 | 0 | 38960.3709 | 1 | 0 |  | 1429 | 1568 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3714 | 1 | 0 | 38960.3714 | 1 | 0 |  | 1471 | 1610 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3719 | 1 | 0 | 38960.3719 | 1 | 0 |  | 1513 | 1652 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3723 | 2 | 0 | 38960.3724 | 1 | 0 |  | 1555 | 1694 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116969 | 234038 | 116968.9988
38960.3728 | 1 | 0 | 38960.3728 | 1 | 0 |  | 1597 | 1736 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234038 | 234038 | 234037.9994
38960.3733 | 2 | 0 | 38960.3733 | 1 | 0 |  | 1639 | 1778 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116969 | 234038 | 116968.9988
38960.3738 | 2 | 0 | 38960.3738 | 1 | 0 |  | 1681 | 1820 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116969 | 234038 | 116968.9988
38960.3743 | 4 | 0 | 38960.3743 | 1 | 0 |  | 1723 | 1862 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 58434.5 | 234038 | 58434.4976
38960.3748 | 9 | 0 | 38960.3748 | 1 | 0 |  | 1765 | 1904 | 0.54945 | 0 | 0.06105 | 0 | 0.0054945 | 0 | 0.0006105 | 0 | 0.0054945 | 0.0006105 | 25915.3333 | 234038 | 25915.3278
38960.3753 | 3 | 0 | 38960.3753 | 1 | 0 |  | 1807 | 1946 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 77946 | 234038 | 77945.9982
38960.3757 | 43 | 1 | 38960.3758 | 1 | 0 |  | 1849 | 1988 | 2.6252 | 0.06105 | 0.06105 | 0 | 0.026252 | 0.0006105 | 0.0006105 | 0 | 0.025641 | 0.0006105 | 5472.389 | 234038 | 229639.8792
38960.3762 | 80 | 1 | 38960.3763 | 1 | 0 |  | 1891 | 2030 | 4.884 | 0.06105 | 0.06105 | 0 | 0.04884 | 0.0006105 | 0.0006105 | 0 | 0.04823 | 0.0006105 | 2862.5218 | 234038 | 225941.4595
38960.3767 | 108 | 1 | 38960.3767 | 1 | 0 |  | 1933 | 2072 | 6.5934 | 0.06105 | 0.06105 | 0 | 0.065934 | 0.0006105 | 0.0006105 | 0 | 0.065324 | 0.0006105 | 2087.2794 | 234038 | 223142.6554
38960.3772 | 137 | 1 | 38960.3772 | 1 | 0 |  | 1975 | 2114 | 8.3639 | 0.06105 | 0.06105 | 0 | 0.083639 | 0.0006105 | 0.0006105 | 0 | 0.083028 | 0.0006105 | 1620.8727 | 234038 | 220243.894
38960.3777 | 147 | 1 | 38960.3777 | 1 | 0 |  | 2017 | 2156 | 8.9744 | 0.06105 | 0.06105 | 0 | 0.089744 | 0.0006105 | 0.0006105 | 0 | 0.089133 | 0.0006105 | 1503.0044 | 234038 | 219244.3211
38960.3782 | 192 | 1 | 38960.3782 | 1 | 0 |  | 2059 | 2198 | 11.7216 | 0.06105 | 0.06105 | 0 | 0.11722 | 0.0006105 | 0.0006105 | 0 | 0.11661 | 0.0006105 | 1125.3324 | 234038 | 214746.243
38960.3787 | 254 | 1 | 38960.3787 | 1 | 0 |  | 2101 | 2240 | 15.5067 | 0.06105 | 0.06105 | 0 | 0.15507 | 0.0006105 | 0.0006105 | 0 | 0.15446 | 0.0006105 | 825.0528 | 234038 | 208548.891
38960.3791 | 343 | 1 | 38960.3792 | 1 | 0 |  | 2143 | 2282 | 20.9402 | 0.06105 | 0.06105 | 0 | 0.2094 | 0.0006105 | 0.0006105 | 0 | 0.20879 | 0.0006105 | 584.3224 | 234038 | 199652.6922
38960.3796 | 297 | 1 | 38960.3797 | 2 | 0 |  | 2185 | 2324 | 18.1319 | 0.06105 | 0.1221 | 0 | 0.18132 | 0.0006105 | 0.001221 | 0 | 0.18071 | 0.001221 | 690.6709 | 116969 | 204163.4551
38960.3801 | 350 | 1 | 38960.3801 | 2 | 0 |  | 2227 | 2366 | 21.3675 | 0.06105 | 0.1221 | 0 | 0.21368 | 0.0006105 | 0.001221 | 0 | 0.21306 | 0.001221 | 570.5974 | 116969 | 198867.9823
38960.3806 | 388 | 1 | 38960.3806 | 2 | 0 |  | 2269 | 2408 | 23.6874 | 0.06105 | 0.1221 | 0 | 0.23687 | 0.0006105 | 0.001221 | 0 | 0.23626 | 0.001221 | 504.7505 | 116969 | 195071.2283
38960.3811 | 451 | 1 | 38960.3811 | 2 | 0 |  | 2311 | 2450 | 27.5336 | 0.06105 | 0.1221 | 0 | 0.27534 | 0.0006105 | 0.001221 | 0 | 0.27473 | 0.001221 | 420.0852 | 116969 | 188776.6097
38960.3816 | 619 | 1 |  | 2 | 0 |  | 2352 | 2491 | 37.79 | 0.06105 | 0.1221 | 0 | 0.3779 | 0.0006105 | 0.001221 | 0 | 0.37729 | 0.001221 | 278.7027 | 116969 | 171990.9602
38960.3821 | 2033 | 1 | 38960.3821 | 2 | 0 |  | 2395 | 2534 | 124.1148 | 0.06105 | 0.1221 | 0 | 1.2411 | 0.0006105 | 0.001221 | 0 | 1.2405 | 0.001221 | 15.1762 | 116969 | 30711.7437
38960.3825 | 2110 | 1 | 38960.3826 | 2 | 0 |  | 2437 | 2576 | 128.8156 | 0.06105 | 0.1221 | 0 | 1.2882 | 0.0006105 | 0.001221 | 0 | 1.2875 | 0.001221 | 10.9711 | 116969 | 23018.321
38960.383 | 2015 | 1 | 38960.3831 | 2 | 0 |  | 2479 | 2618 | 123.0159 | 0.06105 | 0.1221 | 0 | 1.2302 | 0.0006105 | 0.001221 | 0 | 1.2295 | 0.001221 | 16.2056 | 116969 | 32510.2061
38960.3835 | 1730 | 1 | 38960.3835 | 2 | 0 |  | 2521 | 2660 | 105.6166 | 0.06105 | 0.1221 | 0 | 1.0562 | 0.0006105 | 0.001221 | 0 | 1.0556 | 0.001221 | 35.3603 | 116969 | 60985.8615
38960.384 | 2104 | 1 | 38960.384 | 32 | 0 |  | 2563 | 2702 | 128.4493 | 0.06105 | 1.9536 | 0 | 1.2845 | 0.0006105 | 0.019536 | 0 | 1.2839 | 0.019536 | 11.2878 | 7216.8125 | 23314.9358
38960.3845 | 2066 | 0 | 38960.3845 | 514 | 0 |  | 2605 | 2744 | 126.1294 | 0 | 31.3797 | 0 | 1.2613 | 0 | 0.3138 | 0 | 1.2613 | 0.3138 | 13.3291 | 355.5214 | 12.0678
38960.385 | 2149 | 0 | 38960.385 | 656 | 0 |  | 2647 | 2786 | 131.1966 | 0 | 40.0488 | 0 | 1.312 | 0 | 0.40049 | 0 | 1.312 | 0.40049 | 8.9521 | 256.9177 | 7.6401
38960.3855 | 2096 | 0 | 38960.3855 | 447 | 0 |  | 2689 | 2828 | 127.9609 | 0 | 27.2894 | 0 | 1.2796 | 0 | 0.27289 | 0 | 1.2796 | 0.27289 | 11.7071 | 423.7987 | 10.4275
38960.3859 | 1778 | 0 | 38960.386 | 1271 | 0 |  | 2731 | 2870 | 108.547 | 0 | 77.5946 | 0 | 1.0855 | 0 | 0.77595 | 0 | 1.0855 | 0.77595 | 31.6862 | 84.2156 | 30.6007
38960.3864 | 1742 | 0 | 38960.3865 | 1870 | 0 |  | 2773 | 2912 | 106.3492 | 0 | 114.1636 | 0 | 1.0635 | 0 | 1.1416 | 0 | 1.0635 | 1.1416 | 34.4076 | 25.2075 | 33.3441
38960.3869 | 1886 | 0 | 38960.3869 | 1833 | 0 |  | 2815 | 2954 | 115.1404 | 0 | 111.9048 | 0 | 1.1514 | 0 | 1.119 | 0 | 1.1514 | 1.119 | 24.1453 | 27.7349 | 22.9939
38960.3874 | 1723 | 0 | 38960.3874 | 1936 | 0 |  | 2857 | 2996 | 105.1893 | 0 | 118.1929 | 0 | 1.0519 | 0 | 1.1819 | 0 | 1.0519 | 1.1819 | 35.8897 | 20.939 | 34.8378
38960.3879 | 2245 | 0 | 38960.3879 | 1770 | 0 |  | 2899 | 3038 | 137.0574 | 0 | 108.0586 | 0 | 1.3706 | 0 | 1.0806 | 0 | 1.3706 | 1.0806 | 4.2931 | 32.2814 | 2.9225
38960.3884 | 1826 | 0 | 38960.3884 | 2219 | 0 |  | 2941 | 3080 | 111.4774 | 0 | 135.4701 | 0 | 1.1148 | 0 | 1.3547 | 0 | 1.1148 | 1.3547 | 28.2245 | 5.5151 | 27.1098
38960.3889 | 1917 | 0 | 38960.3889 | 1995 | 0 |  | 2983 | 3122 | 117.033 | 0 | 121.7949 | 0 | 1.1703 | 0 | 1.2179 | 0 | 1.1703 | 1.2179 | 22.1377 | 17.3624 | 20.9674
38960.3894 | 2093 | 0 | 38960.3894 | 2015 | 0 |  | 3025 | 3164 | 127.7778 | 0 | 123.0159 | 0 | 1.2778 | 0 | 1.2302 | 0 | 1.2778 | 1.2302 | 11.8672 | 16.1975 | 10.5894
38960.3898 | 2091 | 0 | 38960.3899 | 1964 | 0 |  | 3067 | 3206 | 127.6557 | 0 | 119.9023 | 0 | 1.2766 | 0 | 1.199 | 0 | 1.2766 | 1.199 | 11.9742 | 19.2149 | 10.6976
38960.3903 | 2113 | 0 | 38960.3903 | 1901 | 0 |  | 3109 | 3248 | 128.9988 | 0 | 116.0562 | 0 | 1.29 | 0 | 1.1606 | 0 | 1.29 | 1.1606 | 10.8083 | 23.1657 | 9.5183
38960.3908 | 2000 | 0 | 38960.3908 | 1905 | 0 |  | 3151 | 3290 | 122.1001 | 0 | 116.3004 | 0 | 1.221 | 0 | 1.163 | 0 | 1.221 | 1.163 | 17.069 | 22.9071 | 15.848
38960.3913 | 1962 | 0 | 38960.3913 | 1941 | 0 |  | 3193 | 3332 | 119.7802 | 0 | 118.4982 | 0 | 1.1978 | 0 | 1.185 | 0 | 1.1978 | 1.185 | 19.3364 | 20.6275 | 18.1386
38960.3918 | 2072 | 0 | 38960.3918 | 2325 | 0 |  | 3234.5 | 3373.5 | 126.4957 | 0 | 141.9414 | 0 | 1.265 | 0 | 1.4194 | 0 | 1.265 | 1.4194 | 13.001 | 0.70452 | 11.736
38960.3923 | 2098 | 0 | 38960.3923 | 1807 | 0 |  | 3277 | 3416 | 128.083 | 0 | 110.3175 | 0 | 1.2808 | 0 | 1.1032 | 0 | 1.2808 | 1.1032 | 11.6006 | 29.5728 | 10.3197

## A1-C6
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 145.6276 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38960.3529 | 1 | 0 | 38960.3529 | 1 | 0 |  | -127.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3534 | 1 | 0 | 38960.3534 | 1 | 0 |  | -85.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3538 | 1 | 0 | 38960.3539 | 1 | 0 |  | -43.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3543 | 1 | 0 | 38960.3543 | 1 | 0 |  | -1.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3548 | 1 | 0 | 38960.3548 | 1 | 0 |  | 40.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3553 | 1 | 0 | 38960.3553 | 1 | 0 |  | 82.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3558 | 1 | 0 | 38960.3558 | 1 | 0 |  | 124.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3563 | 1 | 0 | 38960.3563 | 2 | 0 |  | 166.5 | 305.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 238438 | 119169 | 238437.9994
38960.3568 | 1 | 0 | 38960.3568 | 1 | 0 |  | 208.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3572 | 1 | 0 | 38960.3573 | 1 | 0 |  | 250.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3577 | 1 | 0 | 38960.3577 | 1 | 0 |  | 292.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3582 | 1 | 0 | 38960.3582 | 1 | 0 |  | 334.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3587 | 1 | 0 | 38960.3587 | 1 | 0 |  | 376.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3592 | 1 | 0 | 38960.3592 | 1 | 0 |  | 418.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3597 | 1 | 0 | 38960.3597 | 1 | 0 |  | 460.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3602 | 1 | 0 | 38960.3602 | 1 | 0 |  | 502.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3606 | 1 | 0 | 38960.3607 | 1 | 0 |  | 544.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3611 | 1 | 0 | 38960.3611 | 1 | 0 |  | 586.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3616 | 1 | 0 | 38960.3616 | 1 | 0 |  | 628.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3621 | 1 | 0 | 38960.3621 | 1 | 0 |  | 670.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3626 | 1 | 0 | 38960.3626 | 1 | 0 |  | 712.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3631 | 1 | 0 | 38960.3631 | 1 | 0 |  | 754.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3636 | 1 | 0 | 38960.3636 | 1 | 0 |  | 796.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3641 | 1 | 0 | 38960.3641 | 1 | 0 |  | 838.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3645 | 1 | 0 | 38960.3645 | 1 | 0 |  | 880.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.365 | 1 | 0 | 38960.365 | 1 | 0 |  | 922.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3655 | 1 | 0 | 38960.3655 | 1 | 0 |  | 964.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.366 | 1 | 0 | 38960.366 | 1 | 0 |  | 1006.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3665 | 1 | 0 | 38960.3665 | 1 | 0 |  | 1048.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.367 | 1 | 0 | 38960.367 | 1 | 0 |  | 1090.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3675 | 1 | 0 | 38960.3675 | 1 | 0 |  | 1132.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3679 | 1 | 0 | 38960.368 | 1 | 0 |  | 1174.5 | 1313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3684 | 1 | 0 | 38960.3684 | 1 | 0 |  | 1216.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3689 | 1 | 0 | 38960.3689 | 1 | 0 |  | 1258.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3694 | 1 | 0 | 38960.3694 | 1 | 0 |  | 1300.5 | 1439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3699 | 1 | 0 | 38960.3699 | 1 | 0 |  | 1342.5 | 1481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3704 | 1 | 0 | 38960.3704 | 1 | 0 |  | 1384.5 | 1523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3709 | 1 | 0 | 38960.3709 | 1 | 0 |  | 1426.5 | 1565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3713 | 1 | 0 | 38960.3714 | 1 | 0 |  | 1468.5 | 1607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3718 | 1 | 0 | 38960.3718 | 1 | 0 |  | 1510.5 | 1649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3723 | 1 | 0 | 38960.3723 | 1 | 0 |  | 1552.5 | 1691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38960.3728 | 2 | 0 | 38960.3728 | 1 | 0 |  | 1594.5 | 1733.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119169 | 238438 | 119168.9988
38960.3733 | 2 | 0 | 38960.3733 | 1 | 0 |  | 1636 | 1775 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119169 | 238438 | 119168.9988
38960.3738 | 2 | 0 | 38960.3738 | 1 | 0 |  | 1678 | 1817 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119169 | 238438 | 119168.9988
38960.3743 | 4 | 0 | 38960.3743 | 1 | 0 |  | 1720.5 | 1859.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 59534.5 | 238438 | 59534.4976
38960.3747 | 7 | 0 | 38960.3748 | 1 | 0 |  | 1762.5 | 1901.5 | 0.42735 | 0 | 0.06105 | 0 | 0.0042735 | 0 | 0.0006105 | 0 | 0.0042735 | 0.0006105 | 33976.8571 | 238438 | 33976.8529
38960.3752 | 3 | 0 | 38960.3752 | 1 | 0 |  | 1804 | 1943 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 79412.6667 | 238438 | 79412.6648
38960.3757 | 41 | 1 | 38960.3757 | 1 | 0 |  | 1846.5 | 1985.5 | 2.5031 | 0.06105 | 0.06105 | 0 | 0.025031 | 0.0006105 | 0.0006105 | 0 | 0.02442 | 0.0006105 | 5861.0115 | 238438 | 234239.7607
38960.3762 | 85 | 1 | 38960.3762 | 1 | 0 |  | 1888 | 2027 | 5.1893 | 0.06105 | 0.06105 | 0 | 0.051893 | 0.0006105 | 0.0006105 | 0 | 0.051282 | 0.0006105 | 2738.5613 | 238438 | 229841.6053
38960.3767 | 107 | 1 | 38960.3767 | 1 | 0 |  | 1930.5 | 2069.5 | 6.5324 | 0.06105 | 0.06105 | 0 | 0.065324 | 0.0006105 | 0.0006105 | 0 | 0.064713 | 0.0006105 | 2149.4236 | 238438 | 227642.5276
38960.3772 | 127 | 1 | 38960.3772 | 2 | 0 |  | 1972.5 | 2111.5 | 7.7534 | 0.06105 | 0.1221 | 0 | 0.077534 | 0.0006105 | 0.001221 | 0 | 0.076923 | 0.001221 | 1792.377 | 119169 | 225548.732
38960.3777 | 116 | 1 | 38960.3777 | 1 | 0 |  | 2014 | 2153 | 7.0818 | 0.06105 | 0.06105 | 0 | 0.070818 | 0.0006105 | 0.0006105 | 0 | 0.070208 | 0.0006105 | 1973.3811 | 238438 | 226742.9049
38960.3781 | 197 | 1 | 38960.3782 | 3 | 0 |  | 2056 | 2195 | 12.0269 | 0.06105 | 0.18315 | 0 | 0.12027 | 0.0006105 | 0.0018315 | 0 | 0.11966 | 0.0018315 | 1116.5276 | 79412.6667 | 218462.9017
38960.3786 | 220 | 1 | 38960.3786 | 8 | 0 |  | 2098 | 2237 | 13.431 | 0.06105 | 0.4884 | 0 | 0.13431 | 0.0006105 | 0.004884 | 0 | 0.1337 | 0.004884 | 988.7732 | 29717.25 | 215712.1182
38960.3791 | 332 | 1 | 38960.3791 | 1242 | 0 |  | 2140.5 | 2279.5 | 20.2686 | 0.06105 | 75.8242 | 0 | 0.20269 | 0.0006105 | 0.75824 | 0 | 0.20208 | 0.75824 | 622.399 | 92.0596 | 98376.3696
38960.3796 | 362 | 0 | 38960.3796 | 991 | 0 |  | 2182 | 2321 | 22.1001 | 0 | 60.5006 | 0 | 0.221 | 0 | 0.60501 | 0 | 0.221 | 0.60501 | 558.9448 | 140.7043 | 558.7238
38960.3801 | 424 | 0 | 38960.3801 | 964 | 0 |  | 2224 | 2363 | 25.8852 | 0 | 58.8523 | 0 | 0.25885 | 0 | 0.58852 | 0 | 0.25885 | 0.58852 | 462.5896 | 147.4461 | 462.3308
38960.3806 | 439 | 0 | 38960.3806 | 553 | 0 |  | 2266 | 2405 | 26.801 | 0 | 33.7607 | 0 | 0.26801 | 0 | 0.33761 | 0 | 0.26801 | 0.33761 | 443.3667 | 331.3526 | 443.0987
38960.3811 | 547 | 0 | 38960.3811 | 364 | 0 |  | 2308 | 2447 | 33.3944 | 0 | 22.2222 | 0 | 0.33394 | 0 | 0.22222 | 0 | 0.33394 | 0.22222 | 336.0841 | 555.3242 | 335.7502
38960.3815 | 565 | 0 | 38960.3816 | 1889 | 0 |  | 2350 | 2489 | 34.4933 | 0 | 115.3236 | 0 | 0.34493 | 0 | 1.1532 | 0 | 0.34493 | 1.1532 | 322.1912 | 26.2774 | 321.8462
38960.382 | 1860 | 0 | 38960.382 | 1818 | 0 |  | 2392 | 2531 | 113.5531 | 0 | 110.989 | 0 | 1.1355 | 0 | 1.1099 | 0 | 1.1355 | 1.1099 | 28.2462 | 31.209 | 27.1107
38960.3825 | 1873 | 0 | 38960.3825 | 2184 | 0 |  | 2434 | 2573 | 114.3468 | 0 | 133.3333 | 0 | 1.1435 | 0 | 1.3333 | 0 | 1.1435 | 1.3333 | 27.3561 | 9.2207 | 26.2126
38960.383 | 1824 | 0 | 38960.383 | 2307 | 0 |  | 2476 | 2615 | 111.3553 | 0 | 140.8425 | 0 | 1.1136 | 0 | 1.4084 | 0 | 1.1136 | 1.4084 | 30.7774 | 3.3975 | 29.6639
38960.3835 | 1725 | 0 | 38960.3835 | 2030 | 0 |  | 2518 | 2657 | 105.3114 | 0 | 123.9316 | 0 | 1.0531 | 0 | 1.2393 | 0 | 1.0531 | 1.2393 | 38.2829 | 17.5064 | 37.2298
38960.384 | 1745 | 0 | 38960.384 | 1959 | 0 |  | 2560 | 2699 | 106.5324 | 0 | 119.5971 | 0 | 1.0653 | 0 | 1.196 | 0 | 1.0653 | 1.196 | 36.698 | 21.7652 | 35.6327
38960.3845 | 1991 | 0 | 38960.3845 | 2050 | 0 |  | 2602 | 2741 | 121.5507 | 0 | 125.1526 | 0 | 1.2155 | 0 | 1.2515 | 0 | 1.2155 | 1.2515 | 19.8081 | 16.36 | 18.5926
38960.3849 | 2181 | 0 | 38960.385 | 2336 | 0 |  | 2644 | 2783 | 133.1502 | 0 | 142.6129 | 0 | 1.3315 | 0 | 1.4261 | 0 | 1.3315 | 1.4261 | 9.3709 | 2.1139 | 8.0394
38960.3854 | 1929 | 0 | 38960.3855 | 2190 | 0 |  | 2686 | 2825 | 117.7656 | 0 | 133.6996 | 0 | 1.1777 | 0 | 1.337 | 0 | 1.1777 | 1.337 | 23.6589 | 8.9215 | 22.4812
38960.3859 | 1993 | 0 | 38960.3859 | 2009 | 0 |  | 2728 | 2867 | 121.6728 | 0 | 122.6496 | 0 | 1.2167 | 0 | 1.2265 | 0 | 1.2167 | 1.2265 | 19.6879 | 18.7347 | 18.4712
38960.3864 | 2024 | 0 | 38960.3864 | 2130 | 0 |  | 2770 | 2909 | 123.5653 | 0 | 130.0366 | 0 | 1.2357 | 0 | 1.3004 | 0 | 1.2357 | 1.3004 | 17.8547 | 11.9897 | 16.6191
38960.3869 | 1925 | 0 | 38960.3869 | 1801 | 0 |  | 2812 | 2951 | 117.5214 | 0 | 109.9512 | 0 | 1.1752 | 0 | 1.0995 | 0 | 1.1752 | 1.0995 | 23.9158 | 32.4475 | 22.7406
38960.3874 | 1800 | 0 | 38960.3874 | 1809 | 0 |  | 2854 | 2993 | 109.8901 | 0 | 110.4396 | 0 | 1.0989 | 0 | 1.1044 | 0 | 1.0989 | 1.1044 | 32.5211 | 31.8618 | 31.4222
38960.3879 | 1781 | 0 | 38960.3879 | 1841 | 0 |  | 2896 | 3035 | 108.7302 | 0 | 112.3932 | 0 | 1.0873 | 0 | 1.1239 | 0 | 1.0873 | 1.1239 | 33.9349 | 29.5698 | 32.8476
38960.3883 | 2212 | 0 | 38960.3884 | 1877 | 0 |  | 2938 | 3077 | 135.0427 | 0 | 114.591 | 0 | 1.3504 | 0 | 1.1459 | 0 | 1.3504 | 1.1459 | 7.8382 | 27.0847 | 6.4877
38960.3888 | 1852 | 0 | 38960.3889 | 1887 | 0 |  | 2980 | 3119 | 113.0647 | 0 | 115.2015 | 0 | 1.1306 | 0 | 1.152 | 0 | 1.1306 | 1.152 | 28.8002 | 26.4112 | 27.6696
38960.3893 | 2074 | 0 | 38960.3893 | 2030 | 0 |  | 3022 | 3161 | 126.6178 | 0 | 123.9316 | 0 | 1.2662 | 0 | 1.2393 | 0 | 1.2662 | 1.2393 | 15.0135 | 17.5064 | 13.7473
38960.3898 | 2158 | 0 | 38960.3898 | 1841 | 0 |  | 3064 | 3203 | 131.746 | 0 | 112.3932 | 0 | 1.3175 | 0 | 1.1239 | 0 | 1.3175 | 1.1239 | 10.5366 | 29.5698 | 9.2191
38960.3903 | 2188 | 0 | 38960.3903 | 2369 | 0 |  | 3106 | 3245 | 133.5775 | 0 | 144.6276 | 0 | 1.3358 | 0 | 1.4463 | 0 | 1.3358 | 1.4463 | 9.021 | 0.69143 | 7.6852
38960.3908 | 1767 | 0 | 38960.3908 | 2056 | 0 |  | 3148 | 3287 | 107.8755 | 0 | 125.5189 | 0 | 1.0788 | 0 | 1.2552 | 0 | 1.0788 | 1.2552 | 34.996 | 16.0204 | 33.9173
38960.3913 | 2061 | 0 | 38960.3913 | 1911 | 0 |  | 3190 | 3329 | 125.8242 | 0 | 116.6667 | 0 | 1.2582 | 0 | 1.1667 | 0 | 1.2582 | 1.1667 | 15.739 | 24.8237 | 14.4807
38960.3917 | 2088 | 0 | 38960.3918 | 2142 | 0 |  | 3232 | 3371 | 127.4725 | 0 | 130.7692 | 0 | 1.2747 | 0 | 1.3077 | 0 | 1.2747 | 1.3077 | 14.2423 | 11.3623 | 12.9676
38960.3922 | 1733 | 0 | 38960.3923 | 2255 | 0 |  | 3274 | 3413 | 105.7998 | 0 | 137.6679 | 0 | 1.058 | 0 | 1.3767 | 0 | 1.058 | 1.3767 | 37.6445 | 5.7818 | 36.5865

## A1-C5
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 145.3223 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38960.3528 | 1 | 0 | 38960.3528 | 1 | 0 |  | -130.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3533 | 2 | 0 | 38960.3533 | 1 | 0 |  | -88.5 | 50.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118919 | 237938 | 118918.9988
38960.3538 | 1 | 0 | 38960.3538 | 1 | 0 |  | -46.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3543 | 1 | 0 | 38960.3543 | 1 | 0 |  | -4.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3548 | 1 | 0 | 38960.3548 | 1 | 0 |  | 37.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3553 | 1 | 0 | 38960.3553 | 1 | 0 |  | 79.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3558 | 1 | 0 | 38960.3558 | 1 | 0 |  | 121.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3562 | 1 | 0 | 38960.3562 | 1 | 0 |  | 163.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3567 | 1 | 0 | 38960.3567 | 1 | 0 |  | 205.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3572 | 1 | 0 | 38960.3572 | 1 | 0 |  | 247.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3577 | 1 | 0 | 38960.3577 | 1 | 0 |  | 289.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3582 | 1 | 0 | 38960.3582 | 1 | 0 |  | 331.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3587 | 1 | 0 | 38960.3587 | 1 | 0 |  | 373.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3592 | 1 | 0 | 38960.3592 | 1 | 0 |  | 415.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3596 | 1 | 0 | 38960.3597 | 1 | 0 |  | 457.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3601 | 1 | 0 | 38960.3601 | 1 | 0 |  | 499.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3606 | 1 | 0 | 38960.3606 | 1 | 0 |  | 541.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3611 | 1 | 0 | 38960.3611 | 1 | 0 |  | 583.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3616 | 1 | 0 | 38960.3616 | 1 | 0 |  | 625.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3621 | 1 | 0 | 38960.3621 | 1 | 0 |  | 667.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3626 | 1 | 0 | 38960.3626 | 1 | 0 |  | 709.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.363 | 1 | 0 | 38960.3631 | 1 | 0 |  | 751.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3635 | 1 | 0 | 38960.3635 | 1 | 0 |  | 793.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.364 | 1 | 0 | 38960.364 | 1 | 0 |  | 835.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3645 | 1 | 0 | 38960.3645 | 1 | 0 |  | 877.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.365 | 1 | 0 | 38960.365 | 1 | 0 |  | 919.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3655 | 1 | 0 | 38960.3655 | 1 | 0 |  | 961.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.366 | 1 | 0 | 38960.366 | 1 | 0 |  | 1003.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3664 | 1 | 0 | 38960.3665 | 1 | 0 |  | 1045.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3669 | 1 | 0 | 38960.3669 | 1 | 0 |  | 1087.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3674 | 1 | 0 | 38960.3674 | 1 | 0 |  | 1129.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3679 | 1 | 0 | 38960.3679 | 2 | 0 |  | 1171.5 | 1310.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 237938 | 118919 | 237937.9994
38960.3684 | 1 | 0 | 38960.3684 | 1 | 0 |  | 1213.5 | 1352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3689 | 1 | 0 | 38960.3689 | 1 | 0 |  | 1255.5 | 1394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3694 | 1 | 0 | 38960.3694 | 1 | 0 |  | 1297.5 | 1436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3698 | 1 | 0 | 38960.3699 | 1 | 0 |  | 1339.5 | 1478.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3703 | 1 | 0 | 38960.3703 | 1 | 0 |  | 1381.5 | 1520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3708 | 1 | 0 | 38960.3708 | 1 | 0 |  | 1423.5 | 1562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3713 | 1 | 0 | 38960.3713 | 1 | 0 |  | 1465.5 | 1604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3718 | 1 | 0 | 38960.3718 | 1 | 0 |  | 1507.5 | 1646.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3723 | 1 | 0 | 38960.3723 | 1 | 0 |  | 1549.5 | 1688.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3728 | 1 | 0 | 38960.3728 | 1 | 0 |  | 1591.5 | 1730.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38960.3733 | 2 | 0 | 38960.3733 | 1 | 0 |  | 1633.5 | 1772.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118919 | 237938 | 118918.9988
38960.3737 | 2 | 0 | 38960.3737 | 1 | 0 |  | 1675.5 | 1814.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118919 | 237938 | 118918.9988
38960.3742 | 3 | 0 | 38960.3742 | 1 | 0 |  | 1717.5 | 1856.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 79246 | 237938 | 79245.9982
38960.3747 | 7 | 0 | 38960.3747 | 1 | 0 |  | 1759.5 | 1898.5 | 0.42735 | 0 | 0.06105 | 0 | 0.0042735 | 0 | 0.0006105 | 0 | 0.0042735 | 0.0006105 | 33905.4286 | 237938 | 33905.4243
38960.3752 | 2 | 1 | 38960.3752 | 1 | 0 |  | 1801.5 | 1940.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237638.126
38960.3757 | 37 | 1 | 38960.3757 | 1 | 0 |  | 1843.5 | 1982.5 | 2.2589 | 0.06105 | 0.06105 | 0 | 0.022589 | 0.0006105 | 0.0006105 | 0 | 0.021978 | 0.0006105 | 6509.4649 | 237938 | 234139.5964
38960.3762 | 85 | 1 | 38960.3762 | 1 | 0 |  | 1885.5 | 2024.5 | 5.1893 | 0.06105 | 0.06105 | 0 | 0.051893 | 0.0006105 | 0.0006105 | 0 | 0.051282 | 0.0006105 | 2732.6089 | 237938 | 229341.6129
38960.3767 | 114 | 1 | 38960.3767 | 1 | 0 |  | 1927.5 | 2066.5 | 6.9597 | 0.06105 | 0.06105 | 0 | 0.069597 | 0.0006105 | 0.0006105 | 0 | 0.068987 | 0.0006105 | 2005.6535 | 237938 | 226442.8312
38960.3771 | 134 | 1 | 38960.3772 | 1288 | 0 |  | 1969.5 | 2108.5 | 8.1807 | 0.06105 | 78.6325 | 0 | 0.081807 | 0.0006105 | 0.78632 | 0 | 0.081197 | 0.78632 | 1704.1149 | 84.8121 | 103042.7161
38960.3776 | 134 | 0 | 38960.3776 | 1750 | 0 |  | 2011.5 | 2150.5 | 8.1807 | 0 | 106.8376 | 0 | 0.081807 | 0 | 1.0684 | 0 | 0.081807 | 1.0684 | 1676.403 | 36.0217 | 1676.3212
38960.3781 | 218 | 0 | 38960.3781 | 1803 | 0 |  | 2053.5 | 2192.5 | 13.3089 | 0 | 110.0733 | 0 | 0.13309 | 0 | 1.1007 | 0 | 0.13309 | 1.1007 | 991.9174 | 32.0233 | 991.7843
38960.3786 | 226 | 0 | 38960.3786 | 1949 | 0 |  | 2095.5 | 2234.5 | 13.7973 | 0 | 118.9866 | 0 | 0.13797 | 0 | 1.1899 | 0 | 0.13797 | 1.1899 | 953.2655 | 22.1334 | 953.1275
38960.3791 | 280 | 0 | 38960.3791 | 2133 | 0 |  | 2137.5 | 2276.5 | 17.094 | 0 | 130.2198 | 0 | 0.17094 | 0 | 1.3022 | 0 | 0.17094 | 1.3022 | 750.1357 | 11.5977 | 749.9648
38960.3796 | 358 | 0 | 38960.3796 | 2116 | 0 |  | 2179.5 | 2318.5 | 21.8559 | 0 | 129.1819 | 0 | 0.21856 | 0 | 1.2918 | 0 | 0.21856 | 1.2918 | 564.9106 | 12.4943 | 564.6921
38960.3801 | 370 | 0 | 38960.3801 | 1791 | 0 |  | 2221.5 | 2360.5 | 22.5885 | 0 | 109.3407 | 0 | 0.22589 | 0 | 1.0934 | 0 | 0.22589 | 1.0934 | 543.3459 | 32.9079 | 543.1201
38960.3805 | 397 | 0 | 38960.3806 | 2015 | 0 |  | 2263.5 | 2402.5 | 24.2369 | 0 | 123.0159 | 0 | 0.24237 | 0 | 1.2302 | 0 | 0.24237 | 1.2302 | 499.5919 | 18.133 | 499.3496
38960.381 | 498 | 0 | 38960.381 | 1804 | 0 |  | 2305.5 | 2444.5 | 30.4029 | 0 | 110.1343 | 0 | 0.30403 | 0 | 1.1013 | 0 | 0.30403 | 1.1013 | 377.988 | 31.9501 | 377.6839
38960.3815 | 539 | 0 | 38960.3815 | 1919 | 0 |  | 2347.5 | 2486.5 | 32.906 | 0 | 117.1551 | 0 | 0.32906 | 0 | 1.1716 | 0 | 0.32906 | 1.1716 | 341.6289 | 24.0427 | 341.2999
38960.382 | 1916 | 0 | 38960.382 | 2181 | 0 |  | 2389.5 | 2528.5 | 116.9719 | 0 | 133.1502 | 0 | 1.1697 | 0 | 1.3315 | 0 | 1.1697 | 1.3315 | 24.237 | 9.1417 | 23.0672
38960.3825 | 1839 | 0 | 38960.3825 | 2339 | 0 |  | 2431.5 | 2570.5 | 112.2711 | 0 | 142.7961 | 0 | 1.1227 | 0 | 1.428 | 0 | 1.1227 | 1.428 | 29.4388 | 1.7691 | 28.3161
38960.383 | 2076 | 0 | 38960.383 | 2076 | 0 |  | 2473.5 | 2612.5 | 126.7399 | 0 | 126.7399 | 0 | 1.2674 | 0 | 1.2674 | 0 | 1.2674 | 1.2674 | 14.6618 | 14.6618 | 13.3945
38960.3835 | 1787 | 0 | 38960.3835 | 2294 | 0 |  | 2515.5 | 2654.5 | 109.0965 | 0 | 140.0488 | 0 | 1.091 | 0 | 1.4005 | 0 | 1.091 | 1.4005 | 33.2054 | 3.7655 | 32.1144
38960.3839 | 1894 | 0 | 38960.384 | 1936 | 0 |  | 2557.5 | 2696.5 | 115.6288 | 0 | 118.1929 | 0 | 1.1563 | 0 | 1.1819 | 0 | 1.1563 | 1.1819 | 25.68 | 22.9535 | 24.5238
38960.3844 | 1711 | 0 | 38960.3844 | 2206 | 0 |  | 2599.5 | 2738.5 | 104.4567 | 0 | 134.6764 | 0 | 1.0446 | 0 | 1.3468 | 0 | 1.0446 | 1.3468 | 39.1222 | 7.9048 | 38.0776
38960.3849 | 1706 | 0 | 38960.3849 | 2098 | 0 |  | 2641.5 | 2780.5 | 104.1514 | 0 | 128.083 | 0 | 1.0415 | 0 | 1.2808 | 0 | 1.0415 | 1.2808 | 39.5299 | 13.4595 | 38.4884
38960.3854 | 2184 | 0 | 38960.3854 | 1897 | 0 |  | 2683.5 | 2822.5 | 133.3333 | 0 | 115.812 | 0 | 1.3333 | 0 | 1.1581 | 0 | 1.3333 | 1.1581 | 8.9918 | 25.4813 | 7.6584
38960.3859 | 1894 | 0 | 38960.3859 | 1927 | 0 |  | 2725.5 | 2864.5 | 115.6288 | 0 | 117.6435 | 0 | 1.1563 | 0 | 1.1764 | 0 | 1.1563 | 1.1764 | 25.68 | 23.5278 | 24.5238
38960.3864 | 1720 | 0 | 38960.3864 | 2316 | 0 |  | 2767.5 | 2906.5 | 105.0061 | 0 | 141.3919 | 0 | 1.0501 | 0 | 1.4139 | 0 | 1.0501 | 1.4139 | 38.3942 | 2.7798 | 37.3441
38960.3869 | 2187 | 0 | 38960.3869 | 2318 | 0 |  | 2809.5 | 2948.5 | 133.5165 | 0 | 141.514 | 0 | 1.3352 | 0 | 1.4151 | 0 | 1.3352 | 1.4151 | 8.8422 | 2.6911 | 7.5071
38960.3873 | 2187 | 0 | 38960.3874 | 2086 | 0 |  | 2851.5 | 2990.5 | 133.5165 | 0 | 127.3504 | 0 | 1.3352 | 0 | 1.2735 | 0 | 1.3352 | 1.2735 | 8.8422 | 14.1122 | 7.5071
38960.3878 | 2160 | 0 | 38960.3878 | 1894 | 0 |  | 2893.5 | 3032.5 | 131.8681 | 0 | 115.6288 | 0 | 1.3187 | 0 | 1.1563 | 0 | 1.3187 | 1.1563 | 10.2028 | 25.68 | 8.8841
38960.3883 | 1769 | 0 | 38960.3883 | 2320 | 0 |  | 2935.5 | 3074.5 | 107.9976 | 0 | 141.6361 | 0 | 1.08 | 0 | 1.4164 | 0 | 1.08 | 1.4164 | 34.5608 | 2.6026 | 33.4808
38960.3888 | 2139 | 0 | 38960.3888 | 1973 | 0 |  | 2977.5 | 3116.5 | 130.5861 | 0 | 120.4518 | 0 | 1.3059 | 0 | 1.2045 | 0 | 1.3059 | 1.2045 | 11.2847 | 20.6477 | 9.9789
38960.3893 | 1843 | 0 | 38960.3893 | 1999 | 0 |  | 3019.5 | 3158.5 | 112.5153 | 0 | 122.0391 | 0 | 1.1252 | 0 | 1.2204 | 0 | 1.1252 | 1.2204 | 29.1579 | 19.0785 | 28.0327
38960.3898 | 1787 | 0 | 38960.3898 | 2202 | 0 |  | 3061.5 | 3200.5 | 109.0965 | 0 | 134.4322 | 0 | 1.091 | 0 | 1.3443 | 0 | 1.091 | 1.3443 | 33.2054 | 8.1008 | 32.1144
38960.3903 | 1731 | 0 | 38960.3903 | 2313 | 0 |  | 3103 | 3242 | 105.6777 | 0 | 141.2088 | 0 | 1.0568 | 0 | 1.4121 | 0 | 1.0568 | 1.4121 | 37.5147 | 2.9131 | 36.458
38960.3908 | 1741 | 0 | 38960.3908 | 1972 | 0 |  | 3145.5 | 3284.5 | 106.2882 | 0 | 120.3907 | 0 | 1.0629 | 0 | 1.2039 | 0 | 1.0629 | 1.2039 | 36.7249 | 20.7089 | 35.662
38960.3912 | 1995 | 0 | 38960.3913 | 1859 | 0 |  | 3187.5 | 3326.5 | 121.7949 | 0 | 113.4921 | 0 | 1.2179 | 0 | 1.1349 | 0 | 1.2179 | 1.1349 | 19.3173 | 28.0463 | 18.0993
38960.3917 | 1988 | 0 | 38960.3917 | 2156 | 0 |  | 3229 | 3368 | 121.3675 | 0 | 131.6239 | 0 | 1.2137 | 0 | 1.3162 | 0 | 1.2137 | 1.3162 | 19.7374 | 10.4072 | 18.5237
38960.3922 | 1796 | 0 | 38960.3922 | 2364 | 0 |  | 3271 | 3410 | 109.6459 | 0 | 144.3223 | 0 | 1.0965 | 0 | 1.4432 | 0 | 1.0965 | 1.4432 | 32.5379 | 0.69289 | 31.4414

## A1-B4
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 132.8071 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38960.3528 | 1 | 0 | 38960.3528 | 1 | 0 |  | -133 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3533 | 1 | 0 | 38960.3533 | 1 | 0 |  | -91 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3538 | 1 | 0 | 38960.3538 | 1 | 0 |  | -49 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3543 | 1 | 0 | 38960.3543 | 1 | 0 |  | -7 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3547 | 1 | 0 | 38960.3548 | 1 | 0 |  | 35 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3552 | 1 | 0 | 38960.3553 | 1 | 0 |  | 77 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3557 | 1 | 0 | 38960.3557 | 1 | 0 |  | 119 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3562 | 1 | 0 | 38960.3562 | 1 | 0 |  | 161 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3567 | 1 | 0 | 38960.3567 | 1 | 0 |  | 203 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3572 | 1 | 0 | 38960.3572 | 1 | 0 |  | 245 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3577 | 1 | 0 | 38960.3577 | 1 | 0 |  | 287 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3581 | 1 | 0 | 38960.3582 | 1 | 0 |  | 329 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3586 | 1 | 0 | 38960.3586 | 1 | 0 |  | 370.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3591 | 1 | 0 | 38960.3591 | 1 | 0 |  | 413 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3596 | 1 | 0 | 38960.3596 | 1 | 0 |  | 455 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3601 | 1 | 0 | 38960.3601 | 1 | 0 |  | 497 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3606 | 1 | 0 | 38960.3606 | 1 | 0 |  | 539 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3611 | 1 | 0 | 38960.3611 | 1 | 0 |  | 580.5 | 719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3616 | 1 | 0 | 38960.3616 | 1 | 0 |  | 622.5 | 761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.362 | 1 | 0 | 38960.362 | 1 | 0 |  | 664.5 | 803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3625 | 1 | 0 | 38960.3625 | 1 | 0 |  | 707 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.363 | 1 | 0 | 38960.363 | 1 | 0 |  | 749 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3635 | 1 | 0 | 38960.3635 | 1 | 0 |  | 790.5 | 929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.364 | 1 | 0 | 38960.364 | 1 | 0 |  | 832.5 | 971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3645 | 1 | 0 | 38960.3645 | 1 | 0 |  | 874.5 | 1013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.365 | 1 | 0 | 38960.365 | 1 | 0 |  | 916.5 | 1055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3654 | 1 | 0 | 38960.3655 | 1 | 0 |  | 959 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3659 | 1 | 0 | 38960.3659 | 1 | 0 |  | 1001 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3664 | 1 | 0 | 38960.3664 | 1 | 0 |  | 1042.5 | 1181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3669 | 1 | 1 | 38960.3669 | 1 | 0 |  | 1084.5 | 1223.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 472792838.44 | 217438 | 217238.0919
38960.3674 | 1 | 0 | 38960.3674 | 1 | 0 |  | 1126.5 | 1265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3679 | 1 | 0 | 38960.3679 | 1 | 0 |  | 1168.5 | 1307.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3684 | 1 | 0 | 38960.3684 | 1 | 0 |  | 1210.5 | 1349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3688 | 1 | 0 | 38960.3689 | 1 | 0 |  | 1252.5 | 1391.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3693 | 1 | 0 | 38960.3693 | 1 | 0 |  | 1294.5 | 1433.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3698 | 1 | 0 | 38960.3698 | 1 | 0 |  | 1336.5 | 1475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3703 | 1 | 0 | 38960.3703 | 1 | 0 |  | 1378.5 | 1517.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3708 | 1 | 0 | 38960.3708 | 1 | 0 |  | 1420.5 | 1559.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3713 | 1 | 1 | 38960.3713 | 1 | 0 |  | 1462.5 | 1601.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 472792838.44 | 217438 | 217238.0919
38960.3718 | 1 | 0 | 38960.3718 | 1 | 0 |  | 1504.5 | 1643.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217437.9994
38960.3722 | 2 | 0 | 38960.3723 | 1 | 0 |  | 1546.5 | 1685.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 108669 | 217438 | 108668.9988
38960.3727 | 2 | 0 | 38960.3727 | 2 | 0 |  | 1588.5 | 1727.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 108669 | 108669 | 108668.9988
38960.3732 | 2 | 1 | 38960.3732 | 1 | 0 |  | 1630.5 | 1769.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217438 | 217438 | 217138.1379
38960.3737 | 2 | 0 | 38960.3737 | 1 | 0 |  | 1672.5 | 1811.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 108669 | 217438 | 108668.9988
38960.3742 | 3 | 0 | 38960.3742 | 1 | 0 |  | 1714.5 | 1853.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 72412.6667 | 217438 | 72412.6648
38960.3747 | 7 | 0 | 38960.3747 | 1 | 0 |  | 1756.5 | 1895.5 | 0.42735 | 0 | 0.06105 | 0 | 0.0042735 | 0 | 0.0006105 | 0 | 0.0042735 | 0.0006105 | 30976.8571 | 217438 | 30976.8529
38960.3752 | 3 | 0 | 38960.3752 | 1 | 0 |  | 1798.5 | 1937.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 72412.6667 | 217438 | 72412.6648
38960.3756 | 35 | 1 | 38960.3757 | 1 | 0 |  | 1840.5 | 1979.5 | 2.1368 | 0.06105 | 0.06105 | 0 | 0.021368 | 0.0006105 | 0.0006105 | 0 | 0.020757 | 0.0006105 | 6295.3204 | 217438 | 213839.6549
38960.3761 | 74 | 1 | 38960.3761 | 1 | 0 |  | 1882.5 | 2021.5 | 4.5177 | 0.06105 | 0.06105 | 0 | 0.045177 | 0.0006105 | 0.0006105 | 0 | 0.044567 | 0.0006105 | 2878.6209 | 217438 | 209941.4477
38960.3766 | 115 | 1 | 38960.3766 | 1 | 0 |  | 1924.5 | 2063.5 | 7.0208 | 0.06105 | 0.06105 | 0 | 0.070208 | 0.0006105 | 0.0006105 | 0 | 0.069597 | 0.0006105 | 1807.3582 | 217438 | 205843.3324
38960.3771 | 130 | 1 | 38960.3771 | 1 | 0 |  | 1966.5 | 2105.5 | 7.9365 | 0.06105 | 0.06105 | 0 | 0.079365 | 0.0006105 | 0.0006105 | 0 | 0.078755 | 0.0006105 | 1585.5715 | 217438 | 204344.0219
38960.3776 | 129 | 1 | 38960.3776 | 2 | 0 |  | 2008.5 | 2147.5 | 7.8755 | 0.06105 | 0.1221 | 0 | 0.078755 | 0.0006105 | 0.001221 | 0 | 0.078144 | 0.001221 | 1598.7459 | 108669 | 204349.9519
38960.3781 | 213 | 1 | 38960.3781 | 1 | 0 |  | 2050.5 | 2189.5 | 13.0037 | 0.06105 | 0.06105 | 0 | 0.13004 | 0.0006105 | 0.0006105 | 0 | 0.12943 | 0.0006105 | 925.653 | 217438 | 196047.8374
38960.3786 | 272 | 1 | 38960.3786 | 1 | 0 |  | 2092.5 | 2231.5 | 16.6056 | 0.06105 | 0.06105 | 0 | 0.16606 | 0.0006105 | 0.0006105 | 0 | 0.16545 | 0.0006105 | 702.3554 | 217438 | 190150.5495
38960.3791 | 260 | 1 | 38960.3791 | 2 | 0 |  | 2134.5 | 2273.5 | 15.873 | 0.06105 | 0.1221 | 0 | 0.15873 | 0.0006105 | 0.001221 | 0 | 0.15812 | 0.001221 | 739.5316 | 108669 | 191261.9958
38960.3795 | 366 | 1 | 38960.3795 | 2 | 0 |  | 2176.5 | 2315.5 | 22.3443 | 0.06105 | 0.1221 | 0 | 0.22344 | 0.0006105 | 0.001221 | 0 | 0.22283 | 0.001221 | 495.7218 | 108669 | 180671.7412
38960.38 | 358 | 1 | 38960.38 | 2 | 0 |  | 2218.5 | 2357.5 | 21.8559 | 0.06105 | 0.1221 | 0 | 0.21856 | 0.0006105 | 0.001221 | 0 | 0.21795 | 0.001221 | 509.0713 | 108669 | 181471.0057
38960.3805 | 402 | 1 | 38960.3805 | 2 | 0 |  | 2260.5 | 2399.5 | 24.5421 | 0.06105 | 0.1221 | 0 | 0.24542 | 0.0006105 | 0.001221 | 0 | 0.24481 | 0.001221 | 442.2404 | 108669 | 177075.051
38960.381 | 490 | 1 | 38960.381 | 1 | 0 |  | 2302.5 | 2441.5 | 29.9145 | 0.06105 | 0.06105 | 0 | 0.29915 | 0.0006105 | 0.0006105 | 0 | 0.29853 | 0.0006105 | 344.6588 | 217438 | 168360.5708
38960.3815 | 549 | 1 | 38960.3815 | 2 | 0 |  | 2344.5 | 2483.5 | 33.5165 | 0.06105 | 0.1221 | 0 | 0.33516 | 0.0006105 | 0.001221 | 0 | 0.33455 | 0.001221 | 296.7852 | 108669 | 162388.5659
38960.382 | 1639 | 1 | 38960.382 | 2 | 0 |  | 2386.5 | 2525.5 | 100.0611 | 0.06105 | 0.1221 | 0 | 1.0006 | 0.0006105 | 0.001221 | 0 | 1 | 0.001221 | 32.7461 | 108669 | 53488.7783
38960.3825 | 1894 | 1 | 38960.3825 | 2 | 0 |  | 2428.5 | 2567.5 | 115.6288 | 0.06105 | 0.1221 | 0 | 1.1563 | 0.0006105 | 0.001221 | 0 | 1.1557 | 0.001221 | 14.8642 | 108669 | 28012.2224
38960.3829 | 1823 | 1 | 38960.383 | 2 | 0 |  | 2470.5 | 2609.5 | 111.2943 | 0.06105 | 0.1221 | 0 | 1.1129 | 0.0006105 | 0.001221 | 0 | 1.1123 | 0.001221 | 19.3403 | 108669 | 35105.6948
38960.3834 | 2042 | 1 | 38960.3834 | 2 | 0 |  | 2512.5 | 2651.5 | 124.6642 | 0.06105 | 0.1221 | 0 | 1.2466 | 0.0006105 | 0.001221 | 0 | 1.246 | 0.001221 | 6.535 | 108669 | 13225.8293
38960.3839 | 1912 | 1 | 38960.3839 | 2 | 0 |  | 2554.5 | 2693.5 | 116.7277 | 0.06105 | 0.1221 | 0 | 1.1673 | 0.0006105 | 0.001221 | 0 | 1.1667 | 0.001221 | 13.7823 | 108669.0001 | 26213.8773
38960.3844 | 1994 | 1 | 38960.3844 | 2 | 0 |  | 2596.5 | 2735.5 | 121.7338 | 0.06105 | 0.1221 | 0 | 1.2173 | 0.0006105 | 0.001221 | 0 | 1.2167 | 0.001221 | 9.1009 | 108669 | 18021.4162
38960.3849 | 1863 | 1 | 38960.3849 | 2 | 0 |  | 2638.5 | 2777.5 | 113.7363 | 0.06105 | 0.1221 | 0 | 1.1374 | 0.0006105 | 0.001221 | 0 | 1.1368 | 0.001221 | 16.7766 | 108669 | 31109.3724
38960.3854 | 1713 | 1 | 38960.3854 | 4 | 0 |  | 2680.5 | 2819.5 | 104.5788 | 0.06105 | 0.2442 | 0 | 1.0458 | 0.0006105 | 0.002442 | 0 | 1.0452 | 0.002442 | 27.0082 | 54284.5 | 46053.1633
38960.3859 | 1870 | 1 | 38960.3859 | 624 | 0 |  | 2722.5 | 2861.5 | 114.1636 | 0.06105 | 38.0952 | 0 | 1.1416 | 0.0006105 | 0.38095 | 0 | 1.141 | 0.38095 | 16.3427 | 248.6186 | 21706.9682
38960.3863 | 1912 | 1 | 38960.3864 | 13 | 0 |  | 2764.5 | 2903.5 | 116.7277 | 0.06105 | 0.79365 | 0 | 1.1673 | 0.0006105 | 0.0079365 | 0 | 1.1667 | 0.0079365 | 13.7824 | 16633.6923 | 26081.2026
38960.3868 | 1799 | 1 | 38960.3868 | 1887 | 0 |  | 2806.5 | 2945.5 | 109.8291 | 0.06105 | 115.2015 | 0 | 1.0983 | 0.0006105 | 1.152 | 0 | 1.0977 | 1.152 | 21.0097 | 15.2825 | 4976.2379
38960.3873 | 1837 | 0 | 38960.3873 | 1787 | 0 |  | 2848.5 | 2987.5 | 112.149 | 0 | 109.0965 | 0 | 1.1215 | 0 | 1.091 | 0 | 1.1215 | 1.091 | 18.4203 | 21.7336 | 17.2988
38960.3878 | 1955 | 0 | 38960.3878 | 1584 | 0 |  | 2890.5 | 3029.5 | 119.3529 | 0 | 96.7033 | 0 | 1.1935 | 0 | 0.96703 | 0 | 1.1935 | 0.96703 | 11.2726 | 37.3346 | 10.0791
38960.3883 | 2088 | 0 | 38960.3883 | 1799 | 0 |  | 2932.5 | 3071.5 | 127.4725 | 0 | 109.8291 | 0 | 1.2747 | 0 | 1.0983 | 0 | 1.2747 | 1.0983 | 4.1849 | 20.9216 | 2.9101
38960.3888 | 1851 | 0 | 38960.3888 | 1936 | 0 |  | 2974.5 | 3113.5 | 113.0037 | 0 | 118.1929 | 0 | 1.13 | 0 | 1.1819 | 0 | 1.13 | 1.1819 | 17.5246 | 12.3647 | 16.3945
38960.3893 | 1716 | 0 | 38960.3893 | 1792 | 0 |  | 3016.5 | 3155.5 | 104.7619 | 0 | 109.4017 | 0 | 1.0476 | 0 | 1.094 | 0 | 1.0476 | 1.094 | 26.7704 | 21.394 | 25.7228
38960.3897 | 1834 | 0 | 38960.3898 | 1800 | 0 |  | 3058.5 | 3197.5 | 111.9658 | 0 | 109.8901 | 0 | 1.1197 | 0 | 1.0989 | 0 | 1.1197 | 1.0989 | 18.614 | 20.8544 | 17.4943
38960.3902 | 1873 | 0 | 38960.3902 | 1940 | 0 |  | 3100.5 | 3239.5 | 114.3468 | 0 | 118.4371 | 0 | 1.1435 | 0 | 1.1844 | 0 | 1.1435 | 1.1844 | 16.1442 | 12.133 | 15.0007
38960.3907 | 2137 | 0 | 38960.3907 | 2030 | 0 |  | 3142.5 | 3281.5 | 130.464 | 0 | 123.9316 | 0 | 1.3046 | 0 | 1.2393 | 0 | 1.3046 | 1.2393 | 1.796 | 7.1616 | 0.49134
38960.3912 | 1975 | 0 | 38960.3912 | 1866 | 0 |  | 3184.5 | 3323.5 | 120.5739 | 0 | 113.9194 | 0 | 1.2057 | 0 | 1.1392 | 0 | 1.2057 | 1.1392 | 10.1458 | 16.5798 | 8.9401
38960.3917 | 2009 | 0 | 38960.3917 | 2159 | 0 |  | 3226.5 | 3365.5 | 122.6496 | 0 | 131.8071 | 0 | 1.2265 | 0 | 1.3181 | 0 | 1.2265 | 1.3181 | 8.2817 | 0.75868 | 7.0552
38960.3922 | 1844 | 0 | 38960.3922 | 1867 | 0 |  | 3268.5 | 3407.5 | 112.5763 | 0 | 113.9805 | 0 | 1.1258 | 0 | 1.1398 | 0 | 1.1258 | 1.1398 | 17.9707 | 16.5174 | 16.845

## A1-B3
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 142.5751 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38960.3528 | 2 | 0 | 38960.3528 | 1 | 0 |  | -136 | 3 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116669 | 233438 | 116668.9988
38960.3533 | 1 | 0 | 38960.3533 | 1 | 0 |  | -94 | 45 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3537 | 1 | 0 | 38960.3538 | 1 | 0 |  | -52 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3542 | 1 | 0 | 38960.3542 | 1 | 0 |  | -10 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3547 | 1 | 0 | 38960.3547 | 1 | 0 |  | 32 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3552 | 2 | 0 | 38960.3552 | 1 | 0 |  | 74 | 213 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116669 | 233438 | 116668.9988
38960.3557 | 1 | 0 | 38960.3557 | 1 | 0 |  | 116 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3562 | 1 | 0 | 38960.3562 | 1 | 0 |  | 158 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3567 | 1 | 0 | 38960.3567 | 1 | 0 |  | 200 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3571 | 1 | 0 | 38960.3572 | 1 | 0 |  | 242 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3576 | 1 | 0 | 38960.3577 | 1 | 0 |  | 284 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3581 | 1 | 0 | 38960.3581 | 1 | 0 |  | 326 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3586 | 1 | 0 | 38960.3586 | 1 | 0 |  | 368 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3591 | 1 | 0 | 38960.3591 | 1 | 0 |  | 410 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3596 | 1 | 0 | 38960.3596 | 1 | 0 |  | 452 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3601 | 1 | 0 | 38960.3601 | 1 | 0 |  | 494 | 633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3605 | 1 | 0 | 38960.3606 | 1 | 0 |  | 536 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.361 | 1 | 0 | 38960.3611 | 1 | 0 |  | 578 | 717 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3615 | 1 | 0 | 38960.3615 | 1 | 0 |  | 620 | 759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.362 | 1 | 0 | 38960.362 | 1 | 0 |  | 662 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3625 | 1 | 0 | 38960.3625 | 1 | 0 |  | 704 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.363 | 1 | 0 | 38960.363 | 1 | 0 |  | 746 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3635 | 1 | 0 | 38960.3635 | 1 | 0 |  | 788 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3639 | 1 | 0 | 38960.364 | 1 | 0 |  | 830 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3644 | 1 | 0 | 38960.3645 | 1 | 0 |  | 872 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3649 | 1 | 0 | 38960.3649 | 1 | 0 |  | 914 | 1053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3654 | 1 | 0 | 38960.3654 | 1 | 0 |  | 956 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3659 | 1 | 0 | 38960.3659 | 1 | 0 |  | 998 | 1137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3664 | 1 | 1 | 38960.3664 | 1 | 0 |  | 1040 | 1179 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 544932998.44 | 233438 | 233238.0856
38960.3669 | 1 | 0 | 38960.3669 | 1 | 0 |  | 1082 | 1221 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3673 | 1 | 0 | 38960.3674 | 1 | 0 |  | 1124 | 1263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3678 | 1 | 0 | 38960.3679 | 1 | 0 |  | 1166 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3683 | 1 | 0 | 38960.3683 | 1 | 0 |  | 1208 | 1347 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3688 | 1 | 0 | 38960.3688 | 1 | 0 |  | 1250 | 1389 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3693 | 1 | 0 | 38960.3693 | 1 | 0 |  | 1292 | 1431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3698 | 1 | 0 | 38960.3698 | 1 | 0 |  | 1334 | 1473 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3703 | 1 | 0 | 38960.3703 | 1 | 0 |  | 1376 | 1515 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3708 | 1 | 0 | 38960.3708 | 1 | 0 |  | 1418 | 1557 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233437.9994
38960.3712 | 2 | 1 | 38960.3713 | 1 | 0 |  | 1460 | 1599 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233138.1285
38960.3717 | 2 | 1 | 38960.3717 | 1 | 0 |  | 1502 | 1641 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233138.1285
38960.3722 | 1 | 1 | 38960.3722 | 1 | 0 |  | 1544 | 1683 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 544932998.44 | 233438 | 233238.0856
38960.3727 | 2 | 1 | 38960.3727 | 1 | 1 |  | 1585.5 | 1724.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 233337.9572 | 544699460.9887 | 233237.9572
38960.3732 | 2 | 1 | 38960.3732 | 1 | 0 |  | 1628 | 1767 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 233138.1285
38960.3737 | 3 | 1 | 38960.3737 | 1 | 0 |  | 1669.5 | 1808.5 | 0.18315 | 0.06105 | 0.06105 | 0 | 0.0018315 | 0.0006105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116643.9839 | 233438 | 233038.1713
38960.3742 | 3 | 1 | 38960.3742 | 1 | 1 |  | 1712 | 1851 | 0.18315 | 0.06105 | 0.06105 | 0.06105 | 0.0018315 | 0.0006105 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 116618.9786 | 272233011.3131 | 233137.9144
38960.3746 | 6 | 2 | 38960.3747 | 2 | 1 |  | 1754 | 1893 | 0.3663 | 0.1221 | 0.1221 | 0.06105 | 0.003663 | 0.001221 | 0.001221 | 0.0006105 | 0.002442 | 0.0006105 | 58246.9598 | 233739.2901 | 116319.2355
38960.3751 | 3 | 2 | 38960.3752 | 1 | 0 |  | 1796 | 1935 | 0.18315 | 0.1221 | 0.06105 | 0 | 0.0018315 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233438 | 233438 | 116469.107
38960.3756 | 8 | 2 | 38960.3756 | 1 | 1 |  | 1838 | 1977 | 0.4884 | 0.1221 | 0.06105 | 0.06105 | 0.004884 | 0.001221 | 0.0006105 | 0.0006105 | 0.003663 | 0 | 38789.6524 | 90549788.8103 | 116268.8716
38960.3761 | 73 | 1 | 38960.3761 | 1 | 1 |  | 1880 | 2019 | 4.4567 | 0.06105 | 0.06105 | 0.06105 | 0.044567 | 0.0006105 | 0.0006105 | 0.0006105 | 0.043956 | 0 | 3142.1938 | 7335074.4809 | 226134.9171
38960.3766 | 100 | 1 | 38960.3766 | 1 | 1 |  | 1922 | 2061 | 6.105 | 0.06105 | 0.06105 | 0.06105 | 0.06105 | 0.0006105 | 0.0006105 | 0.0006105 | 0.06044 | 0 | 2257.9592 | 5270934.7108 | 223433.761
38960.3771 | 123 | 1 | 38960.3771 | 1 | 0 |  | 1964 | 2103 | 7.5092 | 0.06105 | 0.06105 | 0 | 0.075092 | 0.0006105 | 0.0006105 | 0 | 0.074481 | 0.0006105 | 1813.4326 | 233438 | 221043.3096
38960.3776 | 111 | 1 | 38960.3776 | 1 | 1 |  | 2005.5 | 2144.5 | 6.7766 | 0.06105 | 0.06105 | 0.06105 | 0.067766 | 0.0006105 | 0.0006105 | 0.0006105 | 0.067155 | 0 | 2022.1632 | 4720497.4426 | 222333.29
38960.378 | 204 | 1 | 38960.3781 | 2 | 1 |  | 2047.5 | 2186.5 | 12.4542 | 0.06105 | 0.1221 | 0.06105 | 0.12454 | 0.0006105 | 0.001221 | 0.0006105 | 0.12393 | 0.0006105 | 1049.9429 | 257901.3713 | 212955.4276
38960.3785 | 238 | 1 | 38960.3785 | 1 | 0 |  | 2089.5 | 2228.5 | 14.5299 | 0.06105 | 0.06105 | 0 | 0.1453 | 0.0006105 | 0.0006105 | 0 | 0.14469 | 0.0006105 | 884.9721 | 233438 | 209548.2339
38960.379 | 256 | 1 | 38960.379 | 2 | 0 |  | 2131.5 | 2270.5 | 15.6288 | 0.06105 | 0.1221 | 0 | 0.15629 | 0.0006105 | 0.001221 | 0 | 0.15568 | 0.001221 | 815.4459 | 116669 | 207660.0093
38960.3795 | 314 | 1 | 38960.3795 | 2 | 1 |  | 2173.5 | 2312.5 | 19.1697 | 0.06105 | 0.1221 | 0.06105 | 0.1917 | 0.0006105 | 0.001221 | 0.0006105 | 0.19109 | 0.0006105 | 645.8091 | 276088.8482 | 201964.8479
38960.38 | 394 | 1 | 38960.38 | 2 | 0 |  | 2215.5 | 2354.5 | 24.0537 | 0.06105 | 0.1221 | 0 | 0.24054 | 0.0006105 | 0.001221 | 0 | 0.23993 | 0.001221 | 493.9909 | 116669 | 193871.8275
38960.3805 | 378 | 1 | 38960.3805 | 2 | 1 |  | 2258 | 2397 | 23.0769 | 0.06105 | 0.1221 | 0.06105 | 0.23077 | 0.0006105 | 0.001221 | 0.0006105 | 0.23016 | 0.0006105 | 519.1994 | 289000.7684 | 195570.3288
38960.381 | 466 | 1 | 38960.381 | 2 | 0 |  | 2299.5 | 2438.5 | 28.4493 | 0.06105 | 0.1221 | 0 | 0.28449 | 0.0006105 | 0.001221 | 0 | 0.28388 | 0.001221 | 402.0179 | 116669 | 186677.9935
38960.3814 | 494 | 1 | 38960.3815 | 2 | 0 |  | 2341.5 | 2480.5 | 30.1587 | 0.06105 | 0.1221 | 0 | 0.30159 | 0.0006105 | 0.001221 | 0 | 0.30098 | 0.001221 | 373.5057 | 116669 | 183880.3914
38960.3819 | 1722 | 1 | 38960.3819 | 2 | 0 |  | 2383.5 | 2522.5 | 105.1282 | 0.06105 | 0.1221 | 0 | 1.0513 | 0.0006105 | 0.001221 | 0 | 1.0507 | 0.001221 | 35.6409 | 116669 | 61185.5563
38960.3824 | 2052 | 1 | 38960.3824 | 2 | 0 |  | 2425.5 | 2564.5 | 125.2747 | 0.06105 | 0.1221 | 0 | 1.2527 | 0.0006105 | 0.001221 | 0 | 1.2521 | 0.001221 | 13.8167 | 116669 | 28213.8172
38960.3829 | 1836 | 1 | 38960.3829 | 2 | 0 |  | 2467.5 | 2606.5 | 112.0879 | 0.06105 | 0.1221 | 0 | 1.1209 | 0.0006105 | 0.001221 | 0 | 1.1203 | 0.001221 | 27.2142 | 116669.0001 | 49795.3192
38960.3834 | 1943 | 1 | 38960.3834 | 2 | 0 |  | 2509.5 | 2648.5 | 118.6203 | 0.06105 | 0.1221 | 0 | 1.1862 | 0.0006105 | 0.001221 | 0 | 1.1856 | 0.001221 | 20.205 | 116669 | 39104.4825
38960.3839 | 1837 | 1 | 38960.3839 | 3 | 0 |  | 2551.5 | 2690.5 | 112.149 | 0.06105 | 0.18315 | 0 | 1.1215 | 0.0006105 | 0.0018315 | 0 | 1.1209 | 0.0018315 | 27.1449 | 77746 | 49674.1072
38960.3844 | 2115 | 1 | 38960.3844 | 497 | 0 |  | 2593.5 | 2732.5 | 129.1209 | 0.06105 | 30.3419 | 0 | 1.2912 | 0.0006105 | 0.30342 | 0 | 1.2906 | 0.30342 | 10.4261 | 369.8954 | 17269.3011
38960.3848 | 1802 | 1 | 38960.3849 | 487 | 0 |  | 2635.5 | 2774.5 | 110.0122 | 0.06105 | 29.7314 | 0 | 1.1001 | 0.0006105 | 0.29731 | 0 | 1.0995 | 0.29731 | 29.6201 | 379.5441 | 42136.2067
38960.3853 | 2045 | 1 | 38960.3853 | 640 | 0 |  | 2677.5 | 2816.5 | 124.8474 | 0.06105 | 39.072 | 0 | 1.2485 | 0.0006105 | 0.39072 | 0 | 1.2479 | 0.39072 | 14.2091 | 264.9031 | 21007.676
38960.3858 | 1812 | 1 | 38960.3858 | 993 | 0 |  | 2719.5 | 2858.5 | 110.6227 | 0.06105 | 60.6227 | 0 | 1.1062 | 0.0006105 | 0.60623 | 0 | 1.1056 | 0.60623 | 28.9119 | 135.1843 | 30026.4824
38960.3863 | 1981 | 0 | 38960.3863 | 1596 | 0 |  | 2761.5 | 2900.5 | 120.9402 | 0 | 97.4359 | 0 | 1.2094 | 0 | 0.97436 | 0 | 1.2094 | 0.97436 | 17.8889 | 46.3271 | 16.6795
38960.3868 | 2148 | 0 | 38960.3868 | 2025 | 0 |  | 2803.5 | 2942.5 | 131.1355 | 0 | 123.6264 | 0 | 1.3114 | 0 | 1.2363 | 0 | 1.3114 | 1.2363 | 8.7235 | 15.3274 | 7.4121
38960.3873 | 1816 | 0 | 38960.3873 | 1992 | 0 |  | 2845.5 | 2984.5 | 110.8669 | 0 | 121.6117 | 0 | 1.1087 | 0 | 1.2161 | 0 | 1.1087 | 1.2161 | 28.6002 | 17.238 | 27.4916
38960.3878 | 2180 | 0 | 38960.3878 | 1770 | 0 |  | 2887.5 | 3026.5 | 133.0891 | 0 | 108.0586 | 0 | 1.3309 | 0 | 1.0806 | 0 | 1.3309 | 1.0806 | 7.1275 | 31.9424 | 5.7966
38960.3883 | 1858 | 0 | 38960.3883 | 1976 | 0 |  | 2929.5 | 3068.5 | 113.431 | 0 | 120.6349 | 0 | 1.1343 | 0 | 1.2063 | 0 | 1.1343 | 1.2063 | 25.6932 | 18.1872 | 24.5589
38960.3887 | 2202 | 0 | 38960.3887 | 2097 | 0 |  | 2971.5 | 3110.5 | 134.4322 | 0 | 128.022 | 0 | 1.3443 | 0 | 1.2802 | 0 | 1.3443 | 1.2802 | 6.0572 | 11.3677 | 4.7129
38960.3892 | 2209 | 0 | 38960.3892 | 1911 | 0 |  | 3013.5 | 3152.5 | 134.8596 | 0 | 116.6667 | 0 | 1.3486 | 0 | 1.1667 | 0 | 1.3486 | 1.1667 | 5.7211 | 22.2072 | 4.3725
38960.3897 | 1744 | 0 | 38960.3897 | 1962 | 0 |  | 3055.5 | 3194.5 | 106.4713 | 0 | 119.7802 | 0 | 1.0647 | 0 | 1.1978 | 0 | 1.0647 | 1.1978 | 33.9094 | 19.0306 | 32.8447
38960.3902 | 1790 | 0 | 38960.3902 | 2303 | 0 |  | 3097.5 | 3236.5 | 109.2796 | 0 | 140.5983 | 0 | 1.0928 | 0 | 1.406 | 0 | 1.0928 | 1.406 | 30.4682 | 1.406 | 29.3754
38960.3907 | 2231 | 0 | 38960.3907 | 2253 | 0 |  | 3139.5 | 3278.5 | 136.2027 | 0 | 137.5458 | 0 | 1.362 | 0 | 1.3755 | 0 | 1.362 | 1.3755 | 4.6786 | 3.6565 | 3.3166
38960.3912 | 2219 | 0 | 38960.3912 | 2289 | 0 |  | 3181.5 | 3320.5 | 135.4701 | 0 | 139.7436 | 0 | 1.3547 | 0 | 1.3974 | 0 | 1.3547 | 1.3974 | 5.2447 | 2.0262 | 3.89
38960.3917 | 1917 | 0 | 38960.3917 | 2287 | 0 |  | 3223.5 | 3362.5 | 117.033 | 0 | 139.6215 | 0 | 1.1703 | 0 | 1.3962 | 0 | 1.1703 | 1.3962 | 21.8247 | 2.1154 | 20.6544
38960.3921 | 2167 | 0 | 38960.3922 | 2319 | 0 |  | 3265.5 | 3404.5 | 132.2955 | 0 | 141.5751 | 0 | 1.323 | 0 | 1.4158 | 0 | 1.323 | 1.4158 | 7.7702 | 0.70634 | 6.4472

## A1-A2
Penlight Test 48 |  |  | 2006-08-31 | 8:30 |  |  | Vs = |  | 138.9731 |  | R = | 100
EPR & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38960.3527 | 1 | 0 | 38960.3528 | 1 | 0 |  | -138.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3532 | 1 | 0 | 38960.3532 | 1 | 0 |  | -96.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3537 | 1 | 0 | 38960.3537 | 1 | 0 |  | -54.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3542 | 1 | 0 | 38960.3542 | 1 | 0 |  | -12.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3547 | 1 | 0 | 38960.3547 | 1 | 0 |  | 29.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3552 | 1 | 0 | 38960.3552 | 1 | 0 |  | 71.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3557 | 1 | 0 | 38960.3557 | 1 | 0 |  | 113.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3561 | 1 | 0 | 38960.3562 | 1 | 0 |  | 155.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3566 | 1 | 0 | 38960.3566 | 1 | 0 |  | 197.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3571 | 1 | 0 | 38960.3571 | 1 | 0 |  | 239.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3576 | 1 | 0 | 38960.3576 | 1 | 0 |  | 281.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3581 | 1 | 0 | 38960.3581 | 1 | 0 |  | 323.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3586 | 1 | 0 | 38960.3586 | 1 | 0 |  | 365.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3591 | 1 | 0 | 38960.3591 | 1 | 0 |  | 407.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3595 | 1 | 0 | 38960.3596 | 1 | 0 |  | 449 | 588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.36 | 1 | 0 | 38960.36 | 1 | 0 |  | 491.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3605 | 1 | 0 | 38960.3605 | 1 | 0 |  | 533.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.361 | 1 | 0 | 38960.361 | 1 | 0 |  | 575 | 714 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3615 | 1 | 0 | 38960.3615 | 1 | 0 |  | 617 | 756 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.362 | 1 | 0 | 38960.362 | 1 | 0 |  | 659 | 798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3625 | 1 | 0 | 38960.3625 | 1 | 0 |  | 701 | 840 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.363 | 1 | 0 | 38960.363 | 1 | 0 |  | 743.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3634 | 1 | 0 | 38960.3634 | 1 | 0 |  | 785.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3639 | 1 | 0 | 38960.3639 | 1 | 0 |  | 827 | 966 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3644 | 1 | 0 | 38960.3644 | 1 | 0 |  | 869.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3649 | 1 | 0 | 38960.3649 | 1 | 0 |  | 911 | 1050 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3654 | 1 | 0 | 38960.3654 | 1 | 0 |  | 953 | 1092 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3659 | 1 | 0 | 38960.3659 | 1 | 0 |  | 995 | 1134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3663 | 1 | 0 | 38960.3664 | 1 | 0 |  | 1037 | 1176 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3668 | 1 | 0 | 38960.3669 | 1 | 0 |  | 1079 | 1218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3673 | 1 | 0 | 38960.3673 | 1 | 0 |  | 1121 | 1260 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3678 | 1 | 0 | 38960.3678 | 1 | 0 |  | 1163 | 1302 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3683 | 1 | 0 | 38960.3683 | 1 | 0 |  | 1205 | 1344 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3688 | 1 | 0 | 38960.3688 | 1 | 0 |  | 1247 | 1386 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3693 | 1 | 0 | 38960.3693 | 1 | 0 |  | 1289 | 1428 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3697 | 1 | 0 | 38960.3698 | 1 | 0 |  | 1331 | 1470 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3702 | 1 | 0 | 38960.3703 | 1 | 0 |  | 1373 | 1512 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3707 | 1 | 0 | 38960.3707 | 1 | 0 |  | 1415 | 1554 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38960.3712 | 1165 | 1184 | 38960.3712 | 930 | 963 |  | 1457 | 1596 | 71.1233 | 72.2833 | 56.7766 | 58.7912 | 0.71123 | 0.72283 | 0.56777 | 0.58791 | 0.0116 | 0.020147 | 2639.9349 | 5125.8149 | 6.0161
38960.3717 | 963 | 978 | 38960.3717 | 1190 | 1143 |  | 1499 | 1638 | 58.7912 | 59.707 | 72.6496 | 69.7802 | 0.58791 | 0.59707 | 0.7265 | 0.6978 | 0.0091575 | 0.028694 | 1041.3638 | 880.1205 | 30.7936
38960.3722 | 945 | 900 | 38960.3722 | 1023 | 972 |  | 1541 | 1680 | 57.6923 | 54.9451 | 62.4542 | 59.3407 | 0.57692 | 0.54945 | 0.62454 | 0.59341 | 0.027473 | 0.031136 | 7559.6792 | 3286.062 | 46.5156
38960.3727 | 1066 | 1082 | 38960.3727 | 1204 | 1167 |  | 1583 | 1722 | 65.0794 | 66.0562 | 73.5043 | 71.2454 | 0.65079 | 0.66056 | 0.73504 | 0.71245 | 0.009768 | 0.022589 | 154.2815 | 140.7888 | 6.9375
38960.3731 | 1153 | 1082 | 38960.3732 | 1121 | 1140 |  | 1625 | 1764 | 70.3907 | 66.0562 | 68.4371 | 69.5971 | 0.70391 | 0.66056 | 0.68437 | 0.69597 | 0.043346 | 0.0116 | 104.8424 | 108.1466 | 1.987
38960.3736 | 1122 | 1050 | 38960.3737 | 1144 | 1146 |  | 1667 | 1806 | 68.4982 | 64.1026 | 69.8413 | 69.9634 | 0.68498 | 0.64103 | 0.69841 | 0.69963 | 0.043956 | 0.001221 | 130.8008 | 129.5419 | 5.6102
38960.3741 | 1074 | 1004 | 38960.3741 | 964 | 959 |  | 1709 | 1848 | 65.5678 | 61.2943 | 58.8523 | 58.547 | 0.65568 | 0.61294 | 0.58852 | 0.58547 | 0.042735 | 0.0030525 | 708.3104 | 1006.4833 | 17.9732
38960.3746 | 1180 | 1148 | 38960.3746 | 1073 | 1058 |  | 1751 | 1890 | 72.0391 | 70.0855 | 65.5067 | 64.591 | 0.72039 | 0.70085 | 0.65507 | 0.64591 | 0.019536 | 0.0091575 | 492.188 | 601.8148 | 3.8558
38960.3751 | 1211 | 1141 | 38960.3751 | 1184 | 1158 |  | 1793 | 1932 | 73.9316 | 69.6581 | 72.2833 | 70.696 | 0.73932 | 0.69658 | 0.72283 | 0.70696 | 0.042735 | 0.015873 | 336.4876 | 462.6589 | 5.4496
38960.3756 | 1172 | 1141 | 38960.3756 | 1128 | 1036 |  | 1835 | 1974 | 71.5507 | 69.6581 | 68.8645 | 63.2479 | 0.71551 | 0.69658 | 0.68864 | 0.63248 | 0.018926 | 0.056166 | 124.2167 | 132.972 | 1.8318
38960.3761 | 1119 | 983 | 38960.3761 | 1207 | 1062 |  | 1877 | 2016 | 68.315 | 60.0122 | 73.6874 | 64.8352 | 0.68315 | 0.60012 | 0.73687 | 0.64835 | 0.083028 | 0.088523 | 6678.883 | 828.3402 | 15.8287
38960.3766 | 1168 | 1031 | 38960.3766 | 1254 | 1001 |  | 1919 | 2058 | 71.3065 | 62.9426 | 76.5568 | 61.1111 | 0.71306 | 0.62943 | 0.76557 | 0.61111 | 0.083639 | 0.15446 | 83.7532 | 86.9024 | 3.4897
38960.377 | 1124 | 953 | 38960.3771 | 1151 | 1048 |  | 1961 | 2100 | 68.6203 | 58.1807 | 70.2686 | 63.9805 | 0.6862 | 0.58181 | 0.70269 | 0.6398 | 0.1044 | 0.062882 | 316.2052 | 492.6579 | 17.3912
38960.3775 | 1237 | 1097 | 38960.3775 | 1029 | 881 |  | 2003 | 2142 | 75.5189 | 66.9719 | 62.8205 | 53.7851 | 0.75519 | 0.66972 | 0.62821 | 0.53785 | 0.08547 | 0.090354 | 2688.2744 | 1082.5316 | 4.8083
38960.378 | 1156 | 956 | 38960.378 | 1262 | 1047 |  | 2045 | 2184 | 70.5739 | 58.3639 | 77.0452 | 63.9194 | 0.70574 | 0.58364 | 0.77045 | 0.63919 | 0.1221 | 0.13126 | 5088.5535 | 537.1319 | 14.4958
38960.3785 | 1230 | 1047 | 38960.3785 | 1214 | 969 |  | 2087 | 2226 | 75.0916 | 63.9194 | 74.1148 | 59.1575 | 0.75092 | 0.63919 | 0.74115 | 0.59158 | 0.11172 | 0.14957 | 156.3785 | 215.3731 | 0.04044
38960.379 | 1190 | 921 | 38960.379 | 1180 | 913 |  | 2129 | 2268 | 72.6496 | 56.2271 | 72.0391 | 55.7387 | 0.7265 | 0.56227 | 0.72039 | 0.55739 | 0.16422 | 0.163 | 714.4388 | 787.5876 | 15.9335
38960.3795 | 1250 | 958 | 38960.3795 | 1233 | 1013 |  | 2171 | 2310 | 76.3126 | 58.486 | 75.2747 | 61.8437 | 0.76313 | 0.58486 | 0.75275 | 0.61844 | 0.17827 | 0.13431 | 106.968 | 143.5161 | 4.2067
38960.38 | 1043 | 811 | 38960.38 | 1171 | 873 |  | 2213 | 2352 | 63.6752 | 49.5116 | 71.4896 | 53.2967 | 0.63675 | 0.49512 | 0.7149 | 0.53297 | 0.14164 | 0.18193 | 4436.9904 | 397.1551 | 41.6055
38960.3804 | 1232 | 916 | 38960.3805 | 1281 | 946 |  | 2255 | 2394 | 75.2137 | 55.9219 | 78.2051 | 57.7534 | 0.75214 | 0.55922 | 0.78205 | 0.57753 | 0.19292 | 0.20452 | 2252.8276 | 339.7105 | 10.8279
38960.3809 | 1273 | 910 | 38960.3809 | 1144 | 874 |  | 2297 | 2436 | 77.7167 | 55.5556 | 69.8413 | 53.3578 | 0.77717 | 0.55556 | 0.69841 | 0.53358 | 0.22161 | 0.16484 | 206.1441 | 735.4301 | 9.0332
38960.3814 | 1215 | 866 | 38960.3814 | 1217 | 809 |  | 2339 | 2478 | 74.1758 | 52.8694 | 74.2979 | 49.3895 | 0.74176 | 0.52869 | 0.74298 | 0.49389 | 0.21306 | 0.24908 | 2584.9022 | 281.2243 | 16.6431
38960.3819 | 1490 | 353 | 38960.3819 | 1939 | 419 |  | 2381 | 2520 | 90.9646 | 21.5507 | 118.3761 | 25.58 | 0.90965 | 0.21551 | 1.1838 | 0.2558 | 0.69414 | 0.92796 | 76.7539 | 313.9114 | 93.1095
38960.3824 | 1717 | 184 | 38960.3824 | 2159 | 219 |  | 2423 | 2562 | 104.823 | 11.2332 | 131.8071 | 13.37 | 1.0482 | 0.11233 | 1.3181 | 0.1337 | 0.9359 | 1.1844 | 14.3286 | 7.7607 | 14.6924
38960.3829 | 2022 | 185 | 38960.3829 | 1824 | 163 |  | 2465 | 2604 | 123.4432 | 11.2943 | 111.3553 | 9.9512 | 1.2344 | 0.11294 | 1.1136 | 0.099512 | 1.1215 | 1.014 | 16.2145 | 68.989 | 15.3103
38960.3834 | 2131 | 179 | 38960.3834 | 2170 | 172 |  | 2507 | 2646 | 130.0977 | 10.928 | 132.4786 | 10.5006 | 1.301 | 0.10928 | 1.3248 | 0.10501 | 1.1917 | 1.2198 | 10.2158 | 33.8433 | 4.7492
38960.3838 | 1975 | 153 | 38960.3839 | 2117 | 156 |  | 2549 | 2688 | 120.5739 | 9.3407 | 129.243 | 9.5238 | 1.2057 | 0.093407 | 1.2924 | 0.095238 | 1.1123 | 1.1972 | 250.6154 | 8.9908 | 8
38960.3843 | 1841 | 138 | 38960.3844 | 1861 | 134 |  | 2591 | 2730 | 112.3932 | 8.4249 | 113.6142 | 8.1807 | 1.1239 | 0.084249 | 1.1361 | 0.081807 | 1.0397 | 1.0543 | 34.6126 | 31.0018 | 50.9967
38960.3848 | 2185 | 141 | 38960.3848 | 2007 | 135 |  | 2633 | 2772 | 133.3944 | 8.6081 | 122.5275 | 8.2418 | 1.3339 | 0.086081 | 1.2253 | 0.082418 | 1.2479 | 1.1429 | 1.9469 | 5.3214 | 1.7781
38960.3853 | 2089 | 148 | 38960.3853 | 1986 | 128 |  | 2675 | 2814 | 127.5336 | 9.0354 | 121.2454 | 7.8144 | 1.2753 | 0.090354 | 1.2125 | 0.078144 | 1.185 | 1.1343 | 12.2876 | 35.5727 | 6.9817
38960.3858 | 2192 | 151 | 38960.3858 | 2067 | 132 |  | 2717 | 2856 | 133.8217 | 9.2186 | 126.1905 | 8.0586 | 1.3382 | 0.092186 | 1.2619 | 0.080586 | 1.246 | 1.1813 | 1.6754 | 5.0412 | 2.1174
38960.3863 | 1766 | 118 | 38960.3863 | 2202 | 137 |  | 2759 | 2898 | 107.8144 | 7.2039 | 134.4322 | 8.3639 | 1.0781 | 0.072039 | 1.3443 | 0.083639 | 1.0061 | 1.2607 | 17.9996 | 9.9368 | 30.0558
38960.3868 | 2114 | 146 | 38960.3868 | 2121 | 131 |  | 2801 | 2940 | 129.0598 | 8.9133 | 129.4872 | 7.9976 | 1.2906 | 0.089133 | 1.2949 | 0.079976 | 1.2015 | 1.2149 | 40.0359 | 9.3445 | 0.95878
38960.3872 | 2144 | 141 | 38960.3873 | 1739 | 103 |  | 2843 | 2982 | 130.8913 | 8.6081 | 106.1661 | 6.2882 | 1.3089 | 0.086081 | 1.0617 | 0.062882 | 1.2228 | 0.99878 | 6.6945 | 551.5551 | 5.1752
38960.3877 | 2172 | 140 | 38960.3878 | 2157 | 127 |  | 2885 | 3024 | 132.6007 | 8.547 | 131.685 | 7.7534 | 1.326 | 0.08547 | 1.3168 | 0.077534 | 1.2405 | 1.2393 | 12.7802 | 11.5201 | 2.6283
38960.3882 | 2207 | 140 | 38960.3882 | 1930 | 120 |  | 2927 | 3066 | 134.7375 | 8.547 | 117.8266 | 7.326 | 1.3474 | 0.08547 | 1.1783 | 0.07326 | 1.2619 | 1.105 | 1.5634 | 5.9054 | 2.8127
38960.3887 | 1983 | 122 | 38960.3887 | 1850 | 107 |  | 2969 | 3108 | 121.0623 | 7.4481 | 112.9426 | 6.5324 | 1.2106 | 0.074481 | 1.1294 | 0.065324 | 1.1361 | 1.0641 | 19.2886 | 35.8825 | 37.0953
38960.3892 | 1914 | 127 | 38960.3892 | 2256 | 131 |  | 3011 | 3150 | 116.8498 | 7.7534 | 137.7289 | 7.9976 | 1.1685 | 0.077534 | 1.3773 | 0.079976 | 1.091 | 1.2973 | 3.9629 | 1.7262 | 3.145
38960.3897 | 2139 | 138 | 38960.3897 | 2167 | 102 |  | 3053 | 3192 | 130.5861 | 8.4249 | 132.2955 | 6.2271 | 1.3059 | 0.084249 | 1.323 | 0.062271 | 1.2216 | 1.2607 | 1.4381 | 1.8274 | 0.0080629
38960.3902 | 2192 | 133 | 38960.3902 | 1923 | 107 |  | 3094.5 | 3233.5 | 133.8217 | 8.1197 | 117.3993 | 6.5324 | 1.3382 | 0.081197 | 1.174 | 0.065324 | 1.257 | 1.1087 | 3.2067 | 23.2371 | 6.8929
38960.3906 | 1919 | 113 | 38960.3907 | 1827 | 100 |  | 3137 | 3276 | 117.1551 | 6.8987 | 111.5385 | 6.105 | 1.1716 | 0.068987 | 1.1154 | 0.06105 | 1.1026 | 1.0543 | 24.22 | 34.1963 | 55.1094
38960.3911 | 2083 | 123 | 38960.3911 | 1875 | 102 |  | 3178.5 | 3317.5 | 127.1673 | 7.5092 | 114.4689 | 6.2271 | 1.2717 | 0.075092 | 1.1447 | 0.062271 | 1.1966 | 1.0824 | 11.4439 | 45.5237 | 17.8998
38960.3916 | 1965 | 115 | 38960.3916 | 1843 | 97 |  | 3221 | 3360 | 119.9634 | 7.0208 | 112.5153 | 5.9219 | 1.1996 | 0.070208 | 1.1252 | 0.059219 | 1.1294 | 1.0659 | 20.5987 | 33.988 | 43.3171
38960.3921 | 2245 | 128 | 38960.3921 | 2260 | 119 |  | 3262.5 | 3401.5 | 137.0574 | 7.8144 | 137.9731 | 7.265 | 1.3706 | 0.078144 | 1.3797 | 0.07265 | 1.2924 | 1.3071 | 6.1486 | 7.9669 | 5.57

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -139 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.1
1 | -138 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.1
2 | -137 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.1
3 | -136 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.1
4 | -135 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.1
5 | -134 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.1
6 | -133 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.6 | 23 | 23.1
7 | -132 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
8 | -131 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.2
9 | -130 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
10 | -129 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.8 | 24.5 | 27.5 | 23 | 23.1
11 | -128 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
12 | -127 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
13 | -126 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
14 | -125 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
15 | -124 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
16 | -123 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
17 | -122 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
18 | -121 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
19 | -120 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
20 | -119 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
21 | -118 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
22 | -117 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
23 | -116 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
24 | -115 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
25 | -114 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
26 | -113 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
27 | -112 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
28 | -111 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
29 | -110 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
30 | -109 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
31 | -108 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
32 | -107 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
33 | -106 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
34 | -105 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
35 | -104 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
36 | -103 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
37 | -102 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
38 | -101 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
39 | -100 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
40 | -99 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
41 | -98 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
42 | -97 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
43 | -96 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
44 | -95 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
45 | -94 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
46 | -93 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
47 | -92 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
48 | -91 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
49 | -90 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
50 | -89 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
51 | -88 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
52 | -87 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
53 | -86 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
54 | -85 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
55 | -84 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
56 | -83 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
57 | -82 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
58 | -81 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
59 | -80 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
60 | -79 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
61 | -78 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
62 | -77 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
63 | -76 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
64 | -75 | 18.5 | 25.9 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
65 | -74 | 18.5 | 25.9 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
66 | -73 | 18.5 | 25.9 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
67 | -72 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
68 | -71 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
69 | -70 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
70 | -69 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
71 | -68 | 18.5 | 25.9 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
72 | -67 | 18.5 | 26 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
73 | -66 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
74 | -65 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
75 | -64 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
76 | -63 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
77 | -62 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
78 | -61 | 18.5 | 26 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
79 | -60 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
80 | -59 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
81 | -58 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.7 | 23 | 23.1
82 | -57 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.7 | 23 | 23.1
83 | -56 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
84 | -55 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
85 | -54 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
86 | -53 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
87 | -52 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
88 | -51 | 18.5 | 25.9 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
89 | -50 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
90 | -49 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
91 | -48 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
92 | -47 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.6 | 23 | 23.1
93 | -46 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
94 | -45 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
95 | -44 | 18.5 | 25.9 | 21.6 | 25.9 | 27.7 | 25.7 | 24.5 | 27.7 | 23 | 23.1
96 | -43 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
97 | -42 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
98 | -41 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
99 | -40 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.5 | 23 | 23.1
100 | -39 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
101 | -38 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
102 | -37 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
103 | -36 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
104 | -35 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
105 | -34 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
106 | -33 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
107 | -32 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
108 | -31 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
109 | -30 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
110 | -29 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
111 | -28 | 18.5 | 26 | 21.6 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
112 | -27 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
113 | -26 | 18.5 | 26 | 21.5 | 25.9 | 27.8 | 25.7 | 24.5 | 27.6 | 23 | 23.1
114 | -25 | 18.5 | 26 | 21.4 | 25.9 | 28 | 25.8 | 24.5 | 27.6 | 23 | 23.1
115 | -24 | 18.5 | 26.3 | 20.8 | 26.2 | 28.9 | 26 | 24.4 | 27.6 | 22.9 | 23.1
116 | -23 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26.1 | 24.4 | 27.6 | 22.9 | 23.1
117 | -22 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26.1 | 24.4 | 27.6 | 22.9 | 23.1
118 | -21 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.5 | 22.9 | 23.1
119 | -20 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.5 | 22.9 | 23.1
120 | -19 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.5 | 22.9 | 23.1
121 | -18 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.6 | 22.9 | 23.1
122 | -17 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.6 | 22.9 | 23.1
123 | -16 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26.1 | 24.4 | 27.6 | 22.9 | 23.1
124 | -15 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.6 | 22.9 | 23.1
125 | -14 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
126 | -13 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.6 | 22.9 | 23.1
127 | -12 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
128 | -11 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
129 | -10 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
130 | -9 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
131 | -8 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
132 | -7 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
133 | -6 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.7 | 22.9 | 23.1
134 | -5 | 18.5 | 26.4 | 20.7 | 26.2 | 29 | 26 | 24.4 | 27.6 | 22.9 | 23.1
135 | -4 | 18.5 | 26.7 | 19.9 | 26.4 | 29.7 | 26.3 | 24.3 | 27.6 | 22.9 | 23.1
136 | -3 | 18.5 | 27.1 | 19.3 | 26.6 | 30.5 | 26.6 | 24.3 | 27.5 | 22.8 | 23
137 | -2 | 18.5 | 27.3 | 19.1 | 26.7 | 30.9 | 26.7 | 24.2 | 27.5 | 22.8 | 23
138 | -1 | 19 | 27.2 | 19.1 | 26.7 | 30.9 | 26.7 | 24.2 | 27.6 | 22.8 | 23
139 | 0 | 20 | 27.2 | 19.1 | 26.7 | 30.8 | 26.7 | 24.2 | 27.6 | 22.8 | 23
140 | 1 | 21.5 | 27.2 | 19.1 | 26.7 | 30.8 | 26.7 | 24.2 | 27.7 | 22.8 | 23
141 | 2 | 23.7 | 27.2 | 19.2 | 26.7 | 30.8 | 26.7 | 24.2 | 27.7 | 22.8 | 23
142 | 3 | 26.2 | 27.2 | 19.2 | 26.7 | 30.8 | 26.7 | 24.2 | 27.6 | 22.8 | 23
143 | 4 | 29.1 | 27.6 | 18.6 | 26.9 | 31.3 | 26.9 | 24.1 | 27.6 | 22.8 | 23
144 | 5 | 32.4 | 28 | 17.9 | 27.2 | 32 | 27.2 | 24.1 | 27.5 | 22.8 | 23
145 | 6 | 36 | 28 | 17.9 | 27.2 | 32 | 27.3 | 24.1 | 27.5 | 22.8 | 23
146 | 7 | 39.8 | 28 | 18 | 27.2 | 32 | 27.2 | 24.1 | 27.5 | 22.8 | 23
147 | 8 | 43.9 | 28.1 | 18 | 27.2 | 32 | 27.2 | 24.1 | 27.5 | 22.8 | 23
148 | 9 | 48.2 | 28.1 | 18 | 27.2 | 32 | 27.3 | 24.1 | 27.5 | 22.8 | 23
149 | 10 | 52.7 | 28.1 | 18.1 | 27.3 | 32 | 27.2 | 24.1 | 27.5 | 22.8 | 23
150 | 11 | 57.3 | 28.2 | 18.2 | 27.3 | 32 | 27.2 | 24.1 | 27.6 | 22.8 | 23
151 | 12 | 62.1 | 28.2 | 18.3 | 27.3 | 32 | 27.2 | 24.1 | 27.6 | 22.8 | 23
152 | 13 | 67.1 | 28.3 | 18.3 | 27.4 | 32 | 27.3 | 24.1 | 27.5 | 22.8 | 23
153 | 14 | 72.1 | 28.3 | 18.5 | 27.4 | 32 | 27.2 | 24.1 | 27.5 | 22.8 | 23
154 | 15 | 77.3 | 28.3 | 18.6 | 27.5 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
155 | 16 | 82.7 | 28.4 | 18.8 | 27.5 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
156 | 17 | 88.2 | 28.4 | 19 | 27.6 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
157 | 18 | 93.7 | 28.5 | 19.2 | 27.6 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
158 | 19 | 99.3 | 28.6 | 19.3 | 27.7 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
159 | 20 | 105 | 28.7 | 19.4 | 27.8 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
160 | 21 | 110.8 | 28.7 | 19.5 | 27.8 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
161 | 22 | 116.7 | 28.8 | 19.7 | 27.9 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
162 | 23 | 122.6 | 28.9 | 19.9 | 28 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
163 | 24 | 128.4 | 29 | 20.1 | 28.1 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
164 | 25 | 134.4 | 29.1 | 20.4 | 28.2 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
165 | 26 | 140.3 | 29.3 | 20.5 | 28.3 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
166 | 27 | 146.3 | 29.4 | 20.8 | 28.4 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
167 | 28 | 152.3 | 29.5 | 21 | 28.6 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
168 | 29 | 158.4 | 29.7 | 21.2 | 28.7 | 31.9 | 27.2 | 24.1 | 27.5 | 22.8 | 23
169 | 30 | 164.4 | 29.8 | 21.4 | 28.9 | 32 | 27.2 | 24.1 | 27.5 | 22.8 | 23
170 | 31 | 170.5 | 30 | 21.7 | 29 | 32 | 27.2 | 24.1 | 27.6 | 22.8 | 23
171 | 32 | 176.5 | 30.1 | 22.2 | 29.1 | 31.9 | 27.2 | 24.1 | 27.6 | 22.8 | 23
172 | 33 | 182.6 | 30.4 | 22.6 | 29.3 | 32 | 27.2 | 24.1 | 27.6 | 22.8 | 23
173 | 34 | 188.8 | 30.5 | 22.9 | 29.5 | 32 | 27.2 | 24.1 | 27.6 | 22.8 | 23
174 | 35 | 194.9 | 30.7 | 23.1 | 29.7 | 32 | 27.2 | 24.1 | 27.6 | 22.8 | 23
175 | 36 | 201.1 | 30.9 | 23.5 | 29.9 | 32 | 27.2 | 24.1 | 27.7 | 22.9 | 23
176 | 37 | 207.2 | 31.2 | 24 | 30 | 32 | 27.3 | 24.1 | 27.7 | 22.9 | 23
177 | 38 | 213.3 | 31.3 | 24.4 | 30.3 | 32 | 27.2 | 24.1 | 27.6 | 22.9 | 23
178 | 39 | 219.3 | 31.5 | 24.8 | 30.5 | 32 | 27.2 | 24.1 | 27.6 | 22.9 | 23
179 | 40 | 225.5 | 31.8 | 25.1 | 30.7 | 32 | 27.3 | 24.1 | 27.6 | 22.9 | 23
180 | 41 | 231.7 | 32 | 25.7 | 30.9 | 32 | 27.2 | 24.1 | 27.7 | 22.9 | 23
181 | 42 | 237.7 | 32.3 | 26 | 31.2 | 32 | 27.3 | 24.1 | 27.6 | 22.9 | 23
182 | 43 | 243.8 | 32.6 | 26.6 | 31.4 | 32 | 27.2 | 24.1 | 27.6 | 22.9 | 23
183 | 44 | 249.9 | 32.9 | 26.9 | 31.7 | 32 | 27.3 | 24.1 | 27.7 | 22.9 | 23
184 | 45 | 256 | 33.2 | 27.5 | 32 | 32 | 27.2 | 24.1 | 27.7 | 22.9 | 23
185 | 46 | 262.1 | 33.4 | 28 | 32.3 | 32 | 27.3 | 24.1 | 27.6 | 22.9 | 23
186 | 47 | 268.2 | 33.8 | 28.4 | 32.6 | 32 | 27.2 | 24.1 | 27.6 | 22.9 | 23
187 | 48 | 274.2 | 34.1 | 29 | 32.9 | 32 | 27.3 | 24.1 | 27.7 | 23 | 23.1
188 | 49 | 280.3 | 34.4 | 29.7 | 33.2 | 32 | 27.3 | 24.1 | 27.6 | 23 | 23
189 | 50 | 286.3 | 34.8 | 30.3 | 33.5 | 32 | 27.3 | 24.1 | 27.6 | 23 | 23.1
190 | 51 | 292.2 | 35.1 | 30.9 | 33.9 | 32 | 27.3 | 24.1 | 27.6 | 23 | 23.1
191 | 52 | 298.2 | 35.5 | 31.6 | 34.3 | 32 | 27.3 | 24.1 | 27.6 | 23 | 23.1
192 | 53 | 304.2 | 35.9 | 32.1 | 34.6 | 32 | 27.3 | 24.1 | 27.6 | 23 | 23.1
193 | 54 | 310.2 | 36.3 | 32.8 | 35 | 32 | 27.3 | 24.1 | 27.5 | 23 | 23.1
194 | 55 | 316.1 | 36.7 | 33.5 | 35.4 | 32 | 27.3 | 24.1 | 27.5 | 23.1 | 23.1
195 | 56 | 322 | 37.1 | 34.4 | 35.8 | 32 | 27.3 | 24.1 | 27.6 | 23.1 | 23.1
196 | 57 | 327.9 | 37.6 | 35.1 | 36.2 | 32.1 | 27.3 | 24.1 | 27.6 | 23.1 | 23.1
197 | 58 | 333.7 | 38 | 35.8 | 36.7 | 32 | 27.2 | 24.1 | 27.6 | 23.1 | 23.2
198 | 59 | 339.6 | 38.4 | 36.8 | 37.1 | 32 | 27.2 | 24.1 | 27.6 | 23.1 | 23.2
199 | 60 | 345.4 | 39 | 37.5 | 37.5 | 32 | 27.3 | 24.1 | 27.5 | 23.1 | 23.2
200 | 61 | 351.1 | 39.4 | 38.2 | 38 | 32.1 | 27.3 | 24.1 | 27.6 | 23.2 | 23.2
201 | 62 | 356.8 | 40 | 39 | 38.6 | 32.1 | 27.3 | 24.1 | 27.6 | 23.2 | 23.2
202 | 63 | 362.5 | 40.5 | 40.4 | 39 | 32.1 | 27.3 | 24.1 | 27.6 | 23.2 | 23.2
203 | 64 | 368.2 | 41 | 41 | 39.6 | 32.2 | 27.3 | 24.1 | 27.7 | 23.2 | 23.2
204 | 65 | 373.9 | 41.6 | 41.9 | 40.1 | 32.2 | 27.3 | 24.1 | 27.7 | 23.3 | 23.3
205 | 66 | 379.5 | 42.1 | 42.7 | 40.6 | 32.2 | 27.3 | 24.1 | 27.7 | 23.3 | 23.3
206 | 67 | 385 | 42.7 | 43.6 | 41.2 | 32.1 | 27.3 | 24.1 | 27.7 | 23.3 | 23.3
207 | 68 | 390.5 | 43.3 | 44.5 | 41.8 | 32.1 | 27.3 | 24.1 | 27.7 | 23.4 | 23.3
208 | 69 | 396.1 | 43.9 | 45.6 | 42.3 | 32.1 | 27.3 | 24.1 | 27.7 | 23.4 | 23.4
209 | 70 | 401.6 | 44.5 | 46.7 | 42.9 | 32.2 | 27.3 | 24.1 | 27.8 | 23.4 | 23.4
210 | 71 | 407 | 45.1 | 47.9 | 43.5 | 32.2 | 27.3 | 24.2 | 27.8 | 23.5 | 23.4
211 | 72 | 412.5 | 45.8 | 48.8 | 44.2 | 32.2 | 27.3 | 24.2 | 27.8 | 23.5 | 23.4
212 | 73 | 417.9 | 46.5 | 49.7 | 44.9 | 32.2 | 27.3 | 24.2 | 27.8 | 23.5 | 23.5
213 | 74 | 423.2 | 47.1 | 50.9 | 45.5 | 32.2 | 27.3 | 24.2 | 27.8 | 23.6 | 23.5
214 | 75 | 428.5 | 47.9 | 52.2 | 46.2 | 32.3 | 27.3 | 24.2 | 27.8 | 23.6 | 23.5
215 | 76 | 433.7 | 48.7 | 53.5 | 46.9 | 32.2 | 27.3 | 24.2 | 27.8 | 23.6 | 23.5
216 | 77 | 438.9 | 49.4 | 54.5 | 47.6 | 32.3 | 27.4 | 24.2 | 27.8 | 23.7 | 23.6
217 | 78 | 443.9 | 50.2 | 55.7 | 48.3 | 32.3 | 27.4 | 24.2 | 27.8 | 23.7 | 23.6
218 | 79 | 449 | 51 | 56.9 | 49.1 | 32.3 | 27.4 | 24.2 | 27.8 | 23.7 | 23.6
219 | 80 | 454.1 | 51.7 | 58.2 | 49.9 | 32.4 | 27.4 | 24.2 | 27.8 | 23.8 | 23.7
220 | 81 | 459.2 | 52.5 | 59.5 | 50.6 | 32.4 | 27.4 | 24.2 | 27.8 | 23.8 | 23.7
221 | 82 | 464.2 | 53.4 | 60.6 | 51.5 | 32.5 | 27.5 | 24.2 | 27.8 | 23.9 | 23.7
222 | 83 | 469.3 | 54.2 | 61.9 | 52.3 | 32.5 | 27.5 | 24.3 | 27.8 | 23.9 | 23.8
223 | 84 | 474.3 | 55.1 | 63.6 | 53.1 | 32.5 | 27.5 | 24.3 | 27.8 | 24 | 23.8
224 | 85 | 479.2 | 56 | 65.1 | 54 | 32.5 | 27.5 | 24.3 | 27.8 | 24 | 23.9
225 | 86 | 484.1 | 56.6 | 66.8 | 54.8 | 32.2 | 27.3 | 24.3 | 27.8 | 24.1 | 23.9
226 | 87 | 488.9 | 57.6 | 68.1 | 55.6 | 32.4 | 27.4 | 24.3 | 27.8 | 24.1 | 23.9
227 | 88 | 493.4 | 58.5 | 69.4 | 56.5 | 32.3 | 27.4 | 24.4 | 27.8 | 24.2 | 24
228 | 89 | 497.5 | 59.5 | 70.9 | 57.4 | 32.3 | 27.3 | 24.4 | 27.8 | 24.2 | 24
229 | 90 | 501 | 60.4 | 72.6 | 58.3 | 32.4 | 27.4 | 24.4 | 27.8 | 24.3 | 24.1
230 | 91 | 504.4 | 61.3 | 74 | 59.2 | 32.4 | 27.4 | 24.4 | 27.9 | 24.4 | 24.1
231 | 92 | 507.5 | 62.2 | 75.2 | 60.1 | 32.4 | 27.4 | 24.4 | 28 | 24.4 | 24.2
232 | 93 | 510.6 | 63.2 | 76.6 | 61 | 32.5 | 27.4 | 24.5 | 28 | 24.5 | 24.3
233 | 94 | 513.4 | 64.2 | 78 | 62 | 32.5 | 27.5 | 24.5 | 28 | 24.6 | 24.3
234 | 95 | 516.1 | 65.2 | 79.4 | 62.9 | 32.6 | 27.5 | 24.5 | 28 | 24.6 | 24.4
235 | 96 | 518.6 | 66.1 | 81.2 | 63.8 | 32.5 | 27.4 | 24.5 | 28 | 24.7 | 24.4
236 | 97 | 521 | 67 | 82.9 | 64.7 | 32.4 | 27.4 | 24.6 | 28.1 | 24.8 | 24.5
237 | 98 | 523.1 | 67.8 | 84.4 | 65.6 | 32.1 | 27.3 | 24.6 | 28.1 | 24.9 | 24.6
238 | 99 | 524.8 | 68.7 | 85.9 | 66.4 | 31.8 | 27.2 | 24.6 | 28.2 | 24.9 | 24.7
239 | 100 | 526.3 | 69.5 | 87.5 | 67.2 | 31.5 | 27.1 | 24.7 | 28.2 | 25 | 24.8
240 | 101 | 527.6 | 70.3 | 89.1 | 68.1 | 31.2 | 27 | 24.7 | 28.3 | 25.1 | 24.9
241 | 102 | 528.6 | 71.2 | 90.5 | 69 | 31.2 | 27 | 24.8 | 28.4 | 25.1 | 24.9
242 | 103 | 529.4 | 72.2 | 91.8 | 69.9 | 31.3 | 27 | 24.8 | 28.4 | 25.2 | 25
243 | 104 | 529.8 | 73.2 | 93.1 | 70.8 | 31.4 | 27.1 | 24.8 | 28.4 | 25.3 | 25.1
244 | 105 | 530.2 | 74.1 | 94.4 | 71.8 | 31.5 | 27.1 | 24.9 | 28.4 | 25.4 | 25.2
245 | 106 | 530.3 | 75.1 | 95.7 | 72.6 | 31.5 | 27.1 | 24.9 | 28.5 | 25.5 | 25.2
246 | 107 | 530.4 | 76 | 96.9 | 73.6 | 31.6 | 27.1 | 24.9 | 28.5 | 25.5 | 25.3
247 | 108 | 530.4 | 76.9 | 98.2 | 74.4 | 31.6 | 27.2 | 25 | 28.5 | 25.6 | 25.4
248 | 109 | 530.1 | 77.9 | 99.4 | 75.4 | 31.6 | 27.2 | 25 | 28.6 | 25.7 | 25.5
249 | 110 | 529.8 | 78.8 | 100.5 | 76.3 | 31.6 | 27.2 | 25 | 28.6 | 25.8 | 25.6
250 | 111 | 529.5 | 79.7 | 101.7 | 77.2 | 31.7 | 27.2 | 25.1 | 28.7 | 25.9 | 25.7
251 | 112 | 529.1 | 80.6 | 102.9 | 78 | 31.7 | 27.3 | 25.1 | 28.7 | 26 | 25.8
252 | 113 | 528.6 | 81.6 | 104 | 78.9 | 31.8 | 27.3 | 25.1 | 28.8 | 26.1 | 25.9
253 | 114 | 528 | 82.5 | 105 | 79.9 | 32 | 27.4 | 25.2 | 28.8 | 26.2 | 26
254 | 115 | 527.6 | 83.5 | 106.1 | 80.8 | 32.1 | 27.5 | 25.2 | 28.8 | 26.2 | 26.1
255 | 116 | 527.1 | 84.4 | 107 | 81.7 | 32.3 | 27.5 | 25.2 | 28.8 | 26.3 | 26.2
256 | 117 | 526.6 | 85.4 | 108.1 | 82.6 | 32.6 | 27.7 | 25.2 | 28.8 | 26.4 | 26.3
257 | 118 | 526.1 | 86.4 | 109.3 | 83.5 | 32.8 | 27.7 | 25.3 | 28.8 | 26.5 | 26.4
258 | 119 | 525.6 | 87.4 | 110.3 | 84.3 | 33 | 27.8 | 25.3 | 28.8 | 26.6 | 26.4
259 | 120 | 525.1 | 88.3 | 111.4 | 85.4 | 33.2 | 27.9 | 25.3 | 28.8 | 26.7 | 26.5
260 | 121 | 524.7 | 89.3 | 112.4 | 86.3 | 33.5 | 28.1 | 25.4 | 28.9 | 26.8 | 26.6
261 | 122 | 524.3 | 90.2 | 113.4 | 87.1 | 33.8 | 28.2 | 25.4 | 28.9 | 26.9 | 26.7
262 | 123 | 524 | 91.2 | 114.3 | 87.9 | 34 | 28.2 | 25.4 | 28.9 | 27 | 26.8
263 | 124 | 523.8 | 92.1 | 115.3 | 88.8 | 34.1 | 28.3 | 25.5 | 28.9 | 27.1 | 26.9
264 | 125 | 523.5 | 93 | 116.4 | 89.7 | 34.3 | 28.4 | 25.5 | 29 | 27.3 | 27
265 | 126 | 523.4 | 93.9 | 117.4 | 90.6 | 34.4 | 28.4 | 25.6 | 29 | 27.4 | 27.1
266 | 127 | 523.3 | 94.8 | 118.7 | 91.4 | 34.5 | 28.5 | 25.6 | 29.1 | 27.5 | 27.2
267 | 128 | 523.3 | 95.7 | 119.8 | 92.3 | 34.7 | 28.6 | 25.7 | 29.1 | 27.6 | 27.3
268 | 129 | 523.3 | 96.5 | 120.9 | 93.2 | 34.8 | 28.6 | 25.8 | 29.1 | 27.7 | 27.4
269 | 130 | 523.4 | 97.4 | 121.9 | 94 | 34.9 | 28.7 | 25.8 | 29.2 | 27.8 | 27.5
270 | 131 | 523.4 | 98.4 | 122.9 | 94.9 | 35 | 28.8 | 25.9 | 29.3 | 27.9 | 27.6
271 | 132 | 523.6 | 99.2 | 124 | 95.8 | 35.1 | 28.8 | 25.9 | 29.3 | 28 | 27.7
272 | 133 | 523.8 | 100.1 | 125.3 | 96.6 | 35.2 | 28.9 | 26 | 29.4 | 28.2 | 27.8
273 | 134 | 524.1 | 100.9 | 126.5 | 97.4 | 35.3 | 28.9 | 26.1 | 29.4 | 28.3 | 28
274 | 135 | 524.4 | 101.8 | 127.7 | 98.3 | 35.4 | 29 | 26.1 | 29.4 | 28.4 | 28.1
275 | 136 | 524.6 | 102.7 | 128.8 | 99.1 | 35.5 | 29.1 | 26.2 | 29.5 | 28.5 | 28.3
276 | 137 | 524.8 | 103.6 | 130 | 99.9 | 35.6 | 29.1 | 26.3 | 29.6 | 28.6 | 28.4
277 | 138 | 525.1 | 104.5 | 131.1 | 100.8 | 35.7 | 29.2 | 26.4 | 29.7 | 28.8 | 28.5
278 | 139 | 525.3 | 105.3 | 132.4 | 101.7 | 35.8 | 29.3 | 26.4 | 29.7 | 28.9 | 28.6
279 | 140 | 525.6 | 106.2 | 133.6 | 102.5 | 35.9 | 29.3 | 26.5 | 29.8 | 29 | 28.7
280 | 141 | 525.9 | 107.1 | 134.6 | 103.4 | 36 | 29.4 | 26.6 | 29.9 | 29.1 | 28.8
281 | 142 | 526.2 | 107.9 | 135.6 | 104.3 | 36.1 | 29.5 | 26.7 | 30 | 29.2 | 28.9
282 | 143 | 526.4 | 108.7 | 136.6 | 105.1 | 36.2 | 29.5 | 26.8 | 30.1 | 29.4 | 29
283 | 144 | 526.6 | 109.6 | 137.8 | 105.9 | 36.3 | 29.6 | 26.9 | 30.2 | 29.5 | 29.1
284 | 145 | 526.7 | 110.5 | 139.2 | 106.7 | 36.4 | 29.7 | 26.9 | 30.2 | 29.6 | 29.3
285 | 146 | 526.9 | 111.3 | 140.3 | 107.6 | 36.5 | 29.7 | 27 | 30.3 | 29.8 | 29.4
286 | 147 | 527 | 112.2 | 141.4 | 108.5 | 36.6 | 29.8 | 27.1 | 30.4 | 29.9 | 29.6
287 | 148 | 527.2 | 113.1 | 142.5 | 109.3 | 36.8 | 29.9 | 27.2 | 30.5 | 30 | 29.7
288 | 149 | 527.4 | 113.9 | 143.6 | 110.1 | 36.9 | 30 | 27.3 | 30.6 | 30.1 | 29.8
289 | 150 | 527.5 | 114.8 | 144.7 | 111 | 37 | 30 | 27.4 | 30.6 | 30.3 | 30
290 | 151 | 527.6 | 115.6 | 145.7 | 111.8 | 37.1 | 30.1 | 27.5 | 30.7 | 30.4 | 30.1
291 | 152 | 527.7 | 116.5 | 146.7 | 112.7 | 37.2 | 30.2 | 27.6 | 30.9 | 30.5 | 30.3
292 | 153 | 527.8 | 117.3 | 147.8 | 113.5 | 37.4 | 30.3 | 27.7 | 31 | 30.7 | 30.5
293 | 154 | 527.8 | 118.2 | 148.9 | 114.3 | 37.5 | 30.4 | 27.8 | 31.1 | 30.8 | 30.7
294 | 155 | 527.9 | 119 | 150.1 | 115.1 | 37.7 | 30.5 | 27.9 | 31.2 | 30.9 | 30.9
295 | 156 | 528 | 119.9 | 151.1 | 115.9 | 37.9 | 30.6 | 28 | 31.3 | 31.1 | 31
296 | 157 | 528 | 120.8 | 152.1 | 116.8 | 38.1 | 30.7 | 28.1 | 31.4 | 31.2 | 31.2
297 | 158 | 528 | 121.6 | 153.2 | 117.7 | 38.3 | 30.8 | 28.2 | 31.5 | 31.3 | 31.4
298 | 159 | 528.1 | 122.5 | 154.2 | 118.5 | 38.4 | 30.9 | 28.4 | 31.6 | 31.5 | 31.6
299 | 160 | 528.1 | 123.3 | 155.2 | 119.4 | 38.6 | 31.1 | 28.5 | 31.7 | 31.6 | 31.8
300 | 161 | 528.1 | 124.2 | 156.3 | 120.2 | 38.7 | 31.2 | 28.6 | 31.8 | 31.7 | 31.9
301 | 162 | 528.1 | 125 | 157.4 | 121 | 38.9 | 31.3 | 28.7 | 31.9 | 31.9 | 32.1
302 | 163 | 528.2 | 125.8 | 158.5 | 121.9 | 39 | 31.4 | 28.8 | 32 | 32 | 32.2
303 | 164 | 528.2 | 126.6 | 159.6 | 122.7 | 39.2 | 31.5 | 28.9 | 32.1 | 32.2 | 32.3
304 | 165 | 528.1 | 127.4 | 160.6 | 123.5 | 39.3 | 31.6 | 29.1 | 32.2 | 32.3 | 32.5
305 | 166 | 528.2 | 128.3 | 161.6 | 124.3 | 39.6 | 31.7 | 29.2 | 32.3 | 32.4 | 32.7
306 | 167 | 528.2 | 129.1 | 162.7 | 125.1 | 39.7 | 31.8 | 29.3 | 32.3 | 32.6 | 32.9
307 | 168 | 528.3 | 129.9 | 163.8 | 125.9 | 39.9 | 31.9 | 29.4 | 32.4 | 32.7 | 33.2
308 | 169 | 528.3 | 130.8 | 164.8 | 126.8 | 40.1 | 32.1 | 29.6 | 32.6 | 32.9 | 33.4
309 | 170 | 528.3 | 131.6 | 165.8 | 127.6 | 40.2 | 32.2 | 29.7 | 32.7 | 33 | 33.6
310 | 171 | 528.3 | 132.4 | 166.7 | 128.3 | 40.4 | 32.3 | 29.8 | 32.9 | 33.2 | 33.9
311 | 172 | 528.3 | 133.2 | 167.7 | 129.2 | 40.5 | 32.4 | 30 | 33 | 33.3 | 34.1
312 | 173 | 528.4 | 134 | 168.8 | 130.1 | 40.8 | 32.5 | 30.1 | 33.1 | 33.5 | 34.3
313 | 174 | 528.5 | 134.8 | 169.8 | 130.8 | 40.9 | 32.7 | 30.3 | 33.2 | 33.6 | 34.4
314 | 175 | 528.5 | 135.6 | 170.9 | 131.6 | 41.1 | 32.8 | 30.4 | 33.4 | 33.8 | 34.6
315 | 176 | 528.6 | 136.4 | 171.8 | 132.5 | 41.2 | 32.9 | 30.5 | 33.5 | 34 | 34.7
316 | 177 | 528.6 | 137.2 | 172.9 | 133.3 | 41.4 | 33 | 30.7 | 33.6 | 34.1 | 34.9
317 | 178 | 528.7 | 138 | 173.9 | 134.1 | 41.6 | 33.2 | 30.8 | 33.8 | 34.3 | 35
318 | 179 | 528.8 | 138.8 | 175.1 | 134.8 | 41.7 | 33.2 | 31 | 33.9 | 34.4 | 35.1
319 | 180 | 528.8 | 139.6 | 176.2 | 135.6 | 41.9 | 33.4 | 31.1 | 34 | 34.6 | 35.3
320 | 181 | 528.8 | 140.4 | 177.1 | 136.4 | 42.1 | 33.6 | 31.3 | 34.2 | 34.8 | 35.4
321 | 182 | 528.8 | 141.2 | 178.2 | 137.2 | 42.3 | 33.7 | 31.4 | 34.3 | 34.9 | 35.6
322 | 183 | 528.8 | 142 | 179.2 | 138 | 42.5 | 33.8 | 31.6 | 34.5 | 35.1 | 35.8
323 | 184 | 528.8 | 142.8 | 180.1 | 138.8 | 42.7 | 33.9 | 31.7 | 34.6 | 35.3 | 36
324 | 185 | 528.8 | 143.5 | 181.1 | 139.6 | 42.9 | 34.1 | 31.9 | 34.7 | 35.4 | 36.2
325 | 186 | 528.8 | 144.3 | 182 | 140.4 | 43.1 | 34.2 | 32.1 | 34.8 | 35.6 | 36.4
326 | 187 | 528.8 | 145.1 | 183 | 141.2 | 43.3 | 34.4 | 32.2 | 35 | 35.8 | 36.6
327 | 188 | 528.7 | 145.8 | 184 | 141.9 | 43.5 | 34.5 | 32.4 | 35.1 | 35.9 | 36.7
328 | 189 | 528.7 | 146.7 | 185 | 142.7 | 43.8 | 34.7 | 32.5 | 35.3 | 36.1 | 36.8
329 | 190 | 528.7 | 147.5 | 185.9 | 143.5 | 44 | 34.9 | 32.7 | 35.4 | 36.3 | 36.9
330 | 191 | 528.7 | 148.2 | 186.8 | 144.3 | 44.3 | 35 | 32.9 | 35.6 | 36.4 | 37.1
331 | 192 | 528.8 | 149 | 187.9 | 145 | 44.5 | 35.2 | 33 | 35.7 | 36.6 | 37.2
332 | 193 | 528.9 | 149.8 | 188.9 | 145.8 | 44.7 | 35.4 | 33.2 | 35.9 | 36.8 | 37.4
333 | 194 | 528.9 | 150.5 | 189.9 | 146.5 | 44.9 | 35.5 | 33.4 | 36.1 | 37 | 37.6
334 | 195 | 529 | 151.3 | 191 | 147.3 | 45 | 35.7 | 33.6 | 36.3 | 37.2 | 38
335 | 196 | 529.1 | 152 | 192 | 148.1 | 45.2 | 35.8 | 33.7 | 36.4 | 37.3 | 38.3
336 | 197 | 529.1 | 152.7 | 192.9 | 148.9 | 45.4 | 35.9 | 33.9 | 36.5 | 37.5 | 38.5
337 | 198 | 529.2 | 153.5 | 193.8 | 149.6 | 45.6 | 36.1 | 34.1 | 36.7 | 37.7 | 38.7
338 | 199 | 529.1 | 154.3 | 194.8 | 150.3 | 45.8 | 36.3 | 34.3 | 36.9 | 37.9 | 38.8
339 | 200 | 529.2 | 155 | 195.9 | 151.1 | 46 | 36.4 | 34.5 | 37 | 38.1 | 38.9
340 | 201 | 529.2 | 155.8 | 196.7 | 151.8 | 46.3 | 36.6 | 34.7 | 37.1 | 38.3 | 39
341 | 202 | 529.2 | 156.5 | 197.7 | 152.6 | 46.6 | 36.8 | 34.8 | 37.3 | 38.4 | 39.2
342 | 203 | 529.1 | 157.3 | 198.7 | 153.4 | 46.8 | 36.9 | 35 | 37.5 | 38.6 | 39.5
343 | 204 | 529.1 | 158 | 199.7 | 154.1 | 46.9 | 37.1 | 35.2 | 37.7 | 38.8 | 39.7
344 | 205 | 529.1 | 158.7 | 200.7 | 154.9 | 47.1 | 37.3 | 35.4 | 37.9 | 39 | 39.9
345 | 206 | 529.1 | 159.5 | 201.5 | 155.6 | 47.4 | 37.5 | 35.6 | 38.1 | 39.2 | 40.2
346 | 207 | 529.1 | 160.3 | 202.4 | 156.4 | 47.7 | 37.6 | 35.8 | 38.2 | 39.4 | 40.5
347 | 208 | 529.2 | 161 | 203.3 | 157.2 | 47.9 | 37.8 | 36 | 38.4 | 39.6 | 40.7
348 | 209 | 529.2 | 161.8 | 204.2 | 157.9 | 48.2 | 38 | 36.2 | 38.6 | 39.8 | 40.9
349 | 210 | 529.2 | 162.5 | 205.1 | 158.6 | 48.4 | 38.2 | 36.4 | 38.8 | 40 | 41.1
350 | 211 | 529.2 | 163.2 | 206.2 | 159.4 | 48.6 | 38.3 | 36.6 | 39 | 40.2 | 41.4
351 | 212 | 529.2 | 164 | 207.1 | 160.1 | 48.8 | 38.5 | 36.7 | 39.2 | 40.4 | 41.6
352 | 213 | 529.1 | 164.7 | 208 | 160.8 | 49.1 | 38.7 | 36.9 | 39.4 | 40.6 | 41.9
353 | 214 | 529.1 | 165.4 | 208.9 | 161.5 | 49.3 | 38.9 | 37.1 | 39.5 | 40.8 | 42.2
354 | 215 | 529.1 | 166.2 | 209.8 | 162.2 | 49.6 | 39.1 | 37.3 | 39.8 | 41 | 42.4
355 | 216 | 529.1 | 166.9 | 210.7 | 163 | 49.8 | 39.3 | 37.5 | 39.9 | 41.2 | 42.6
356 | 217 | 529.1 | 167.6 | 211.6 | 163.8 | 50.1 | 39.5 | 37.7 | 40.1 | 41.4 | 42.9
357 | 218 | 529.1 | 168.4 | 212.5 | 164.5 | 50.3 | 39.7 | 37.9 | 40.3 | 41.6 | 43.1
358 | 219 | 529.1 | 169.1 | 213.3 | 165.2 | 50.5 | 39.9 | 38.1 | 40.6 | 41.8 | 43.3
359 | 220 | 529.1 | 169.8 | 214.2 | 166 | 50.8 | 40.1 | 38.3 | 40.7 | 42 | 43.5
360 | 221 | 529.2 | 170.5 | 215.1 | 166.7 | 51 | 40.2 | 38.6 | 40.9 | 42.2 | 43.7
361 | 222 | 529.2 | 171.2 | 216.1 | 167.4 | 51.2 | 40.4 | 38.8 | 41.1 | 42.4 | 43.9
362 | 223 | 529.3 | 172 | 217 | 168.2 | 51.5 | 40.7 | 39 | 41.3 | 42.7 | 44.1
363 | 224 | 529.3 | 172.7 | 217.9 | 168.9 | 51.7 | 40.8 | 39.2 | 41.5 | 42.9 | 44.3
364 | 225 | 529.4 | 173.4 | 218.9 | 169.7 | 52 | 41 | 39.4 | 41.7 | 43.1 | 44.5
365 | 226 | 529.5 | 174.1 | 219.7 | 170.4 | 52.2 | 41.2 | 39.6 | 42 | 43.3 | 44.7
366 | 227 | 529.5 | 174.9 | 220.6 | 171.1 | 52.4 | 41.4 | 39.8 | 42.2 | 43.5 | 44.8
367 | 228 | 529.6 | 175.5 | 221.6 | 171.7 | 52.6 | 41.6 | 40 | 42.4 | 43.8 | 45.1
368 | 229 | 529.5 | 176.2 | 222.6 | 172.4 | 52.8 | 41.8 | 40.2 | 42.6 | 44 | 45.4
369 | 230 | 529.5 | 177 | 223.4 | 173.2 | 53.1 | 42 | 40.4 | 42.8 | 44.2 | 45.6
370 | 231 | 529.6 | 177.6 | 224.3 | 174 | 53.2 | 42.2 | 40.7 | 43 | 44.4 | 45.8
371 | 232 | 529.7 | 178.3 | 225.2 | 174.7 | 53.5 | 42.4 | 40.9 | 43.2 | 44.6 | 46
372 | 233 | 529.7 | 179.1 | 226.1 | 175.3 | 53.7 | 42.6 | 41.1 | 43.4 | 44.9 | 46.2
373 | 234 | 529.7 | 179.8 | 226.9 | 176.1 | 53.9 | 42.8 | 41.3 | 43.6 | 45.1 | 46.2
374 | 235 | 529.7 | 180.5 | 227.8 | 176.8 | 54.2 | 43 | 41.5 | 43.9 | 45.3 | 46.3
375 | 236 | 529.7 | 181.1 | 228.7 | 177.4 | 54.4 | 43.2 | 41.7 | 44.1 | 45.6 | 46.3
376 | 237 | 529.8 | 181.8 | 229.6 | 178.1 | 54.6 | 43.4 | 42 | 44.3 | 45.8 | 46.4
377 | 238 | 529.8 | 182.5 | 230.5 | 178.8 | 54.8 | 43.6 | 42.2 | 44.5 | 46.1 | 46.5
378 | 239 | 529.8 | 183.2 | 231.4 | 179.6 | 55 | 43.8 | 42.4 | 44.7 | 46.3 | 46.5
379 | 240 | 529.8 | 183.9 | 232.3 | 180.3 | 55.3 | 44.1 | 42.6 | 44.9 | 46.5 | 46.6
380 | 241 | 529.8 | 184.6 | 233.2 | 181 | 55.5 | 44.3 | 42.8 | 45.1 | 46.8 | 46.8
381 | 242 | 529.8 | 185.3 | 234.1 | 181.7 | 55.8 | 44.5 | 43.1 | 45.3 | 47 | 47
382 | 243 | 529.7 | 186 | 234.9 | 182.4 | 56 | 44.7 | 43.3 | 45.5 | 47.3 | 47.2
383 | 244 | 529.7 | 186.7 | 235.7 | 183.1 | 56.3 | 44.9 | 43.5 | 45.7 | 47.5 | 47.4
384 | 245 | 529.7 | 187.3 | 236.6 | 183.8 | 56.6 | 45.2 | 43.7 | 45.9 | 47.7 | 47.6
385 | 246 | 529.6 | 188.1 | 237.5 | 184.5 | 56.8 | 45.4 | 43.9 | 46.1 | 48 | 47.7
386 | 247 | 529.5 | 188.8 | 238.2 | 185.2 | 57.1 | 45.6 | 44.2 | 46.3 | 48.2 | 48
387 | 248 | 529.5 | 189.4 | 239.1 | 185.9 | 57.3 | 45.8 | 44.4 | 46.5 | 48.5 | 48.2
388 | 249 | 529.5 | 190.1 | 240 | 186.6 | 57.6 | 46.1 | 44.6 | 46.8 | 48.7 | 48.4
389 | 250 | 529.4 | 190.8 | 240.8 | 187.3 | 57.9 | 46.3 | 44.8 | 47 | 49 | 48.6
390 | 251 | 529.3 | 191.5 | 241.6 | 188 | 58.2 | 46.5 | 45 | 47.1 | 49.2 | 48.7
391 | 252 | 529.3 | 192.2 | 242.4 | 188.7 | 58.5 | 46.8 | 45.3 | 47.4 | 49.5 | 48.9
392 | 253 | 529.3 | 192.9 | 243.3 | 189.4 | 58.7 | 47 | 45.5 | 47.6 | 49.7 | 49.2
393 | 254 | 529.3 | 193.5 | 244.1 | 190 | 59 | 47.2 | 45.7 | 47.8 | 50 | 49.3
394 | 255 | 529.3 | 194.2 | 244.9 | 190.8 | 59.2 | 47.5 | 45.9 | 48.1 | 50.2 | 49.5
395 | 256 | 529.3 | 194.9 | 245.7 | 191.5 | 59.5 | 47.7 | 46.1 | 48.3 | 50.5 | 49.7
396 | 257 | 529.3 | 195.6 | 246.5 | 192.1 | 59.8 | 47.9 | 46.4 | 48.5 | 50.7 | 49.9
397 | 258 | 529.3 | 196.2 | 247.4 | 192.8 | 60.1 | 48.2 | 46.6 | 48.7 | 51 | 50.1
398 | 259 | 529.3 | 196.9 | 248.2 | 193.5 | 60.4 | 48.4 | 46.8 | 48.9 | 51.3 | 50.3
399 | 260 | 529.3 | 197.5 | 249 | 194.1 | 60.6 | 48.6 | 47 | 49.1 | 51.5 | 50.5
400 | 261 | 529.4 | 198.2 | 249.8 | 194.8 | 60.9 | 48.8 | 47.3 | 49.3 | 51.8 | 50.7
401 | 262 | 529.3 | 198.8 | 250.7 | 195.5 | 61.2 | 49.1 | 47.5 | 49.5 | 52 | 50.9
402 | 263 | 529.3 | 199.5 | 251.5 | 196.2 | 61.4 | 49.3 | 47.7 | 49.7 | 52.3 | 51.1
403 | 264 | 529.3 | 200.2 | 252.2 | 196.9 | 61.8 | 49.6 | 47.9 | 50 | 52.6 | 51.3
404 | 265 | 529.3 | 200.8 | 253.1 | 197.5 | 62 | 49.8 | 48.1 | 50.2 | 52.8 | 51.5
405 | 266 | 529.4 | 201.4 | 254 | 198.2 | 62.3 | 50 | 48.3 | 50.4 | 53.1 | 51.7
406 | 267 | 529.4 | 202.1 | 254.7 | 198.9 | 62.6 | 50.3 | 48.6 | 50.7 | 53.4 | 51.9
407 | 268 | 529.4 | 202.8 | 255.5 | 199.6 | 62.9 | 50.5 | 48.8 | 50.9 | 53.6 | 52.1
408 | 269 | 529.3 | 203.4 | 256.3 | 200.2 | 63.2 | 50.7 | 49 | 51.1 | 53.9 | 52.3
409 | 270 | 529.3 | 204 | 257.1 | 200.8 | 63.5 | 51 | 49.2 | 51.3 | 54.2 | 52.5
410 | 271 | 529.2 | 204.7 | 257.9 | 201.5 | 63.8 | 51.2 | 49.4 | 51.5 | 54.4 | 52.6
411 | 272 | 529.3 | 205.4 | 258.7 | 202.2 | 64.1 | 51.5 | 49.6 | 51.7 | 54.7 | 52.7
412 | 273 | 529.4 | 206 | 259.5 | 202.8 | 64.4 | 51.8 | 49.8 | 51.9 | 55 | 52.9
413 | 274 | 529.4 | 206.6 | 260.4 | 203.5 | 64.6 | 52 | 50 | 52.2 | 55.3 | 53
414 | 275 | 529.4 | 207.3 | 261.2 | 204.2 | 64.9 | 52.2 | 50.2 | 52.4 | 55.5 | 53.1
415 | 276 | 529.4 | 207.9 | 262 | 204.8 | 65.2 | 52.5 | 50.4 | 52.6 | 55.8 | 53.2
416 | 277 | 529.4 | 208.5 | 262.8 | 205.5 | 65.5 | 52.7 | 50.7 | 52.8 | 56.1 | 53.3
417 | 278 | 529.4 | 209.2 | 263.6 | 206.2 | 65.8 | 53 | 50.9 | 53 | 56.4 | 53.4
418 | 279 | 529.4 | 209.8 | 264.3 | 206.9 | 66.2 | 53.3 | 51.1 | 53.2 | 56.7 | 53.6
419 | 280 | 529.4 | 210.5 | 265.2 | 207.5 | 66.4 | 53.5 | 51.3 | 53.4 | 56.9 | 53.8
420 | 281 | 529.4 | 211.1 | 266 | 208.1 | 66.7 | 53.7 | 51.5 | 53.7 | 57.2 | 54
421 | 282 | 529.3 | 211.7 | 266.7 | 208.7 | 67 | 54 | 51.7 | 53.9 | 57.5 | 54.2
422 | 283 | 529.4 | 212.3 | 267.5 | 209.4 | 67.3 | 54.2 | 52 | 54 | 57.8 | 54.4
423 | 284 | 529.4 | 212.9 | 268.4 | 210 | 67.6 | 54.5 | 52.2 | 54.2 | 58.1 | 54.7
424 | 285 | 529.3 | 213.6 | 269.1 | 210.7 | 67.9 | 54.8 | 52.4 | 54.5 | 58.3 | 54.9
425 | 286 | 529.3 | 214.2 | 269.8 | 211.3 | 68.2 | 55 | 52.6 | 54.7 | 58.6 | 55.1
426 | 287 | 529.3 | 214.8 | 270.5 | 211.9 | 68.6 | 55.3 | 52.8 | 55 | 58.9 | 55.2
427 | 288 | 529.3 | 215.5 | 271.2 | 212.5 | 69 | 55.6 | 53 | 55.2 | 59.2 | 55.4
428 | 289 | 529.3 | 216.1 | 272 | 213.2 | 69.3 | 55.9 | 53.3 | 55.4 | 59.5 | 55.6
429 | 290 | 529.2 | 216.7 | 272.8 | 213.9 | 69.6 | 56.1 | 53.5 | 55.7 | 59.8 | 55.7
430 | 291 | 529.1 | 217.4 | 273.6 | 214.5 | 69.9 | 56.4 | 53.7 | 55.9 | 60.1 | 55.9
431 | 292 | 529.1 | 218 | 274.3 | 215.2 | 70.3 | 56.6 | 53.9 | 56.1 | 60.3 | 56.2
432 | 293 | 529 | 218.6 | 275 | 215.8 | 70.6 | 56.9 | 54.1 | 56.3 | 60.6 | 56.4
433 | 294 | 529.1 | 219.2 | 275.8 | 216.5 | 71 | 57.2 | 54.4 | 56.5 | 60.9 | 56.7
434 | 295 | 529.1 | 219.8 | 276.6 | 217.1 | 71.3 | 57.4 | 54.6 | 56.7 | 61.2 | 57
435 | 296 | 529.1 | 220.5 | 277.3 | 217.7 | 71.6 | 57.7 | 54.8 | 57 | 61.5 | 57.3
436 | 297 | 529.1 | 221.1 | 278 | 218.3 | 71.9 | 58 | 55 | 57.3 | 61.8 | 57.6
437 | 298 | 529.1 | 221.7 | 278.8 | 219 | 72.2 | 58.3 | 55.2 | 57.5 | 62.1 | 57.9
438 | 299 | 529.1 | 222.3 | 279.5 | 219.6 | 72.5 | 58.5 | 55.4 | 57.7 | 62.4 | 58.2
439 | 300 | 529 | 222.8 | 280.3 | 220.2 | 72.8 | 58.8 | 55.7 | 57.9 | 62.7 | 58.4
440 | 301 | 529 | 223.5 | 280.9 | 220.8 | 73.2 | 59.1 | 55.9 | 58.1 | 63 | 58.5
441 | 302 | 529 | 224.1 | 281.6 | 221.6 | 73.6 | 59.4 | 56.1 | 58.4 | 63.3 | 58.7
442 | 303 | 529 | 224.8 | 282.3 | 222.2 | 73.9 | 59.7 | 56.3 | 58.6 | 63.5 | 58.9
443 | 304 | 528.9 | 225.3 | 283 | 222.8 | 74.3 | 59.9 | 56.5 | 58.8 | 63.8 | 59
444 | 305 | 528.9 | 225.9 | 283.8 | 223.4 | 74.6 | 60.2 | 56.7 | 59 | 64.1 | 59.2
445 | 306 | 528.9 | 226.6 | 284.5 | 224 | 75 | 60.5 | 56.9 | 59.2 | 64.4 | 59.5
446 | 307 | 528.9 | 227.2 | 285.2 | 224.6 | 75.3 | 60.8 | 57.1 | 59.4 | 64.7 | 59.7
447 | 308 | 528.9 | 227.8 | 286 | 225.2 | 75.6 | 61.1 | 57.3 | 59.6 | 65.1 | 59.8
448 | 309 | 529 | 228.4 | 286.8 | 225.8 | 75.9 | 61.3 | 57.5 | 59.9 | 65.4 | 59.9
449 | 310 | 529 | 229 | 287.4 | 226.5 | 76.2 | 61.6 | 57.8 | 60.2 | 65.7 | 60
450 | 311 | 529 | 229.6 | 288.1 | 227 | 76.6 | 61.9 | 58 | 60.4 | 66 | 60.2
451 | 312 | 529.1 | 230.2 | 288.9 | 227.7 | 76.9 | 62.2 | 58.2 | 60.6 | 66.3 | 60.5
452 | 313 | 529.1 | 230.7 | 289.6 | 228.3 | 77.2 | 62.4 | 58.4 | 60.8 | 66.6 | 60.7
453 | 314 | 529.2 | 231.3 | 290.3 | 228.9 | 77.5 | 62.7 | 58.7 | 61 | 66.9 | 60.9
454 | 315 | 529.2 | 231.9 | 291 | 229.5 | 77.8 | 63 | 58.9 | 61.2 | 67.2 | 61.1
455 | 316 | 529.2 | 232.5 | 291.7 | 230.1 | 78.2 | 63.3 | 59.1 | 61.4 | 67.5 | 61.3
456 | 317 | 529.2 | 233.1 | 292.5 | 230.8 | 78.5 | 63.6 | 59.4 | 61.6 | 67.8 | 61.5
457 | 318 | 529.3 | 233.7 | 293.1 | 231.5 | 78.8 | 63.9 | 59.6 | 61.9 | 68.1 | 61.6
458 | 319 | 529.3 | 234.2 | 293.9 | 232 | 79.1 | 64.1 | 59.9 | 62.1 | 68.4 | 61.8
459 | 320 | 529.3 | 234.8 | 294.5 | 232.5 | 79.5 | 64.4 | 60.1 | 62.3 | 68.8 | 62
460 | 321 | 529.4 | 235.4 | 295.2 | 233.1 | 79.8 | 64.7 | 60.3 | 62.6 | 69.1 | 62.2
461 | 322 | 529.4 | 236 | 295.9 | 233.7 | 80.2 | 65 | 60.6 | 62.8 | 69.4 | 62.3
462 | 323 | 529.3 | 236.7 | 296.6 | 234.3 | 80.6 | 65.3 | 60.8 | 63.1 | 69.7 | 62.5
463 | 324 | 529.3 | 237.3 | 297.2 | 235 | 80.9 | 65.6 | 61.1 | 63.3 | 70 | 62.7
464 | 325 | 529.3 | 237.8 | 297.9 | 235.5 | 81.3 | 65.9 | 61.3 | 63.6 | 70.4 | 62.8
465 | 326 | 529.3 | 238.4 | 298.7 | 236.1 | 81.6 | 66.2 | 61.6 | 63.7 | 70.7 | 63
466 | 327 | 529.3 | 239 | 299.3 | 236.7 | 82 | 66.5 | 61.8 | 63.9 | 71 | 63.2
467 | 328 | 529.3 | 239.6 | 300 | 237.3 | 82.3 | 66.8 | 62.1 | 64.2 | 71.3 | 63.4
468 | 329 | 529.3 | 240.2 | 300.7 | 237.9 | 82.6 | 67.1 | 62.3 | 64.4 | 71.6 | 63.6
469 | 330 | 529.4 | 240.7 | 301.4 | 238.5 | 83 | 67.4 | 62.6 | 64.7 | 72 | 63.7
470 | 331 | 529.3 | 241.3 | 302.1 | 239 | 83.3 | 67.7 | 62.9 | 64.9 | 72.3 | 63.9
471 | 332 | 529.4 | 241.9 | 302.8 | 239.6 | 83.6 | 68 | 63.1 | 65.1 | 72.6 | 64.1
472 | 333 | 529.4 | 242.4 | 303.5 | 240.2 | 83.9 | 68.3 | 63.4 | 65.3 | 73 | 64.3
473 | 334 | 529.4 | 243 | 304.1 | 240.7 | 84.3 | 68.6 | 63.7 | 65.6 | 73.3 | 64.4
474 | 335 | 529.4 | 243.6 | 304.8 | 241.3 | 84.6 | 68.9 | 64 | 65.8 | 73.6 | 64.6
475 | 336 | 529.4 | 244.2 | 305.4 | 241.9 | 84.9 | 69.2 | 64.2 | 66 | 73.9 | 64.8
476 | 337 | 529.4 | 244.8 | 306.1 | 242.5 | 85.3 | 69.5 | 64.5 | 66.3 | 74.3 | 65
477 | 338 | 529.4 | 245.4 | 306.8 | 243.1 | 85.6 | 69.8 | 64.8 | 66.5 | 74.6 | 65.2
478 | 339 | 529.4 | 245.9 | 307.5 | 243.7 | 86 | 70.1 | 65.1 | 66.7 | 74.9 | 65.4
479 | 340 | 529.4 | 246.5 | 308.1 | 244.2 | 86.3 | 70.4 | 65.3 | 66.9 | 75.3 | 65.6
480 | 341 | 529.3 | 247.1 | 308.8 | 244.8 | 86.7 | 70.7 | 65.6 | 67.3 | 75.6 | 65.9
481 | 342 | 529.3 | 247.6 | 309.4 | 245.3 | 87 | 71 | 65.9 | 67.5 | 75.9 | 66.1
482 | 343 | 529.3 | 248.2 | 310 | 246 | 87.4 | 71.4 | 66.2 | 67.8 | 76.2 | 66.3
483 | 344 | 529.3 | 248.8 | 310.7 | 246.5 | 87.8 | 71.7 | 66.5 | 68 | 76.6 | 66.6
484 | 345 | 529.2 | 249.4 | 311.3 | 247.1 | 88.1 | 72 | 66.7 | 68.3 | 76.9 | 66.8
485 | 346 | 529.1 | 250 | 311.9 | 247.6 | 88.5 | 72.3 | 67 | 68.5 | 77.2 | 67.1
486 | 347 | 529.1 | 250.5 | 312.5 | 248.2 | 88.8 | 72.6 | 67.3 | 68.8 | 77.6 | 67.3
487 | 348 | 529 | 251.1 | 313.1 | 248.8 | 89.2 | 73 | 67.6 | 69 | 77.9 | 67.6
488 | 349 | 529 | 251.6 | 313.8 | 249.4 | 89.6 | 73.3 | 67.9 | 69.3 | 78.2 | 67.8
489 | 350 | 528.9 | 252.2 | 314.4 | 249.9 | 89.9 | 73.6 | 68.2 | 69.5 | 78.6 | 68.1
490 | 351 | 528.9 | 252.8 | 314.9 | 250.5 | 90.3 | 73.9 | 68.5 | 69.8 | 78.9 | 68.3
491 | 352 | 528.9 | 253.4 | 315.5 | 251 | 90.7 | 74.2 | 68.7 | 70.1 | 79.2 | 68.6
492 | 353 | 528.9 | 254 | 316.1 | 251.5 | 91.1 | 74.5 | 69 | 70.4 | 79.6 | 68.8
493 | 354 | 528.8 | 254.5 | 316.8 | 252.1 | 91.4 | 74.8 | 69.3 | 70.6 | 79.9 | 69.1
494 | 355 | 528.8 | 255.1 | 317.5 | 252.7 | 91.7 | 75.2 | 69.6 | 70.9 | 80.3 | 69.3
495 | 356 | 528.8 | 255.6 | 318.2 | 253.2 | 92 | 75.4 | 69.9 | 71.2 | 80.6 | 69.5
496 | 357 | 528.8 | 256.2 | 318.8 | 253.7 | 92.4 | 75.8 | 70.2 | 71.5 | 81 | 69.8
497 | 358 | 528.8 | 256.7 | 319.4 | 254.3 | 92.7 | 76.1 | 70.5 | 71.7 | 81.3 | 70
498 | 359 | 528.7 | 257.3 | 320 | 254.8 | 93.1 | 76.4 | 70.8 | 72 | 81.7 | 70.2
499 | 360 | 528.7 | 257.9 | 320.6 | 255.4 | 93.5 | 76.8 | 71.1 | 72.3 | 82 | 70.5
500 | 361 | 528.7 | 258.5 | 321.2 | 255.9 | 93.9 | 77.1 | 71.4 | 72.6 | 82.4 | 70.7
501 | 362 | 528.6 | 259 | 321.8 | 256.5 | 94.2 | 77.4 | 71.7 | 72.8 | 82.8 | 70.9
502 | 363 | 528.5 | 259.6 | 322.3 | 257 | 94.6 | 77.7 | 72 | 73.1 | 83.1 | 71.2
503 | 364 | 528.6 | 260.2 | 322.9 | 257.6 | 95 | 78.1 | 72.3 | 73.4 | 83.5 | 71.5
504 | 365 | 528.5 | 260.7 | 323.5 | 258.1 | 95.4 | 78.4 | 72.6 | 73.6 | 83.8 | 71.8
505 | 366 | 528.5 | 261.3 | 324.1 | 258.7 | 95.7 | 78.7 | 72.9 | 73.8 | 84.2 | 72.1
506 | 367 | 528.4 | 261.8 | 324.7 | 259.2 | 96.1 | 79 | 73.2 | 74.1 | 84.5 | 72.4
507 | 368 | 528.4 | 262.4 | 325.3 | 259.7 | 96.5 | 79.4 | 73.5 | 74.3 | 84.9 | 72.7
508 | 369 | 528.4 | 262.9 | 325.9 | 260.3 | 96.8 | 79.7 | 73.9 | 74.5 | 85.2 | 72.9
509 | 370 | 528.4 | 263.5 | 326.5 | 260.8 | 97.2 | 80 | 74.2 | 74.7 | 85.6 | 73.2
510 | 371 | 528.4 | 264 | 327.1 | 261.4 | 97.5 | 80.3 | 74.5 | 75 | 85.9 | 73.5
511 | 372 | 528.4 | 264.6 | 327.7 | 261.9 | 97.8 | 80.6 | 74.8 | 75.3 | 86.3 | 73.8
512 | 373 | 528.4 | 265.1 | 328.3 | 262.4 | 98.2 | 80.9 | 75.1 | 75.6 | 86.7 | 74.1
513 | 374 | 528.4 | 265.7 | 328.8 | 263 | 98.6 | 81.3 | 75.4 | 75.9 | 87 | 74.4
514 | 375 | 528.4 | 266.2 | 329.4 | 263.5 | 98.9 | 81.6 | 75.7 | 76.2 | 87.4 | 74.7
515 | 376 | 528.4 | 266.8 | 329.9 | 264 | 99.3 | 81.9 | 76 | 76.5 | 87.7 | 75
516 | 377 | 528.4 | 267.4 | 330.5 | 264.5 | 99.6 | 82.2 | 76.4 | 76.8 | 88.1 | 75.2
517 | 378 | 528.4 | 267.9 | 331.1 | 265.1 | 100 | 82.6 | 76.7 | 77 | 88.5 | 75.5
518 | 379 | 528.4 | 268.5 | 331.6 | 265.7 | 100.4 | 82.9 | 77 | 77.3 | 88.9 | 75.8
519 | 380 | 528.4 | 269 | 332.2 | 266.2 | 100.7 | 83.2 | 77.3 | 77.6 | 89.2 | 76.1
520 | 381 | 528.3 | 269.6 | 332.7 | 266.7 | 101.1 | 83.5 | 77.6 | 77.9 | 89.6 | 76.4
521 | 382 | 528.3 | 270.1 | 333.3 | 267.2 | 101.4 | 83.9 | 77.9 | 78.2 | 90 | 76.7
522 | 383 | 528.3 | 270.7 | 333.9 | 267.7 | 101.8 | 84.2 | 78.3 | 78.5 | 90.3 | 77.1
523 | 384 | 528.3 | 271.2 | 334.5 | 268.2 | 102.1 | 84.5 | 78.6 | 78.8 | 90.7 | 77.4
524 | 385 | 528.3 | 271.7 | 335.1 | 268.7 | 102.4 | 84.8 | 78.9 | 79.1 | 91.1 | 77.7
525 | 386 | 528.4 | 272.3 | 335.7 | 269.2 | 102.8 | 85.1 | 79.2 | 79.4 | 91.4 | 78.1
526 | 387 | 528.4 | 272.8 | 336.2 | 269.7 | 103.1 | 85.4 | 79.6 | 79.7 | 91.8 | 78.4
527 | 388 | 528.4 | 273.3 | 336.8 | 270.2 | 103.4 | 85.7 | 79.9 | 80 | 92.2 | 78.7
528 | 389 | 528.4 | 273.9 | 337.3 | 270.7 | 103.8 | 86 | 80.2 | 80.3 | 92.6 | 79
529 | 390 | 528.4 | 274.4 | 337.8 | 271.3 | 104.2 | 86.4 | 80.5 | 80.6 | 92.9 | 79.3
530 | 391 | 528.4 | 275 | 338.3 | 271.9 | 104.6 | 86.7 | 80.8 | 80.8 | 93.3 | 79.6
531 | 392 | 528.3 | 275.5 | 339 | 272.4 | 104.9 | 87 | 81.1 | 81.2 | 93.7 | 79.9
532 | 393 | 528.3 | 276 | 339.4 | 272.9 | 105.3 | 87.4 | 81.5 | 81.5 | 94.1 | 80.2
533 | 394 | 528.3 | 276.6 | 340 | 273.5 | 105.6 | 87.7 | 81.8 | 81.7 | 94.5 | 80.5
534 | 395 | 528.2 | 277.1 | 340.5 | 274 | 106 | 88 | 82.1 | 82 | 94.8 | 80.8
535 | 396 | 528.2 | 277.7 | 341 | 274.4 | 106.4 | 88.3 | 82.4 | 82.3 | 95.2 | 81.2
536 | 397 | 528.2 | 278.2 | 341.5 | 275 | 106.8 | 88.6 | 82.7 | 82.6 | 95.6 | 81.5
537 | 398 | 528.2 | 278.8 | 342 | 275.5 | 107.1 | 89 | 83 | 82.9 | 96 | 81.9
538 | 399 | 528.2 | 279.3 | 342.6 | 276 | 107.5 | 89.3 | 83.4 | 83.3 | 96.4 | 82.2
539 | 400 | 528.2 | 279.8 | 343 | 276.5 | 107.8 | 89.6 | 83.7 | 83.6 | 96.7 | 82.6
540 | 401 | 528.1 | 280.3 | 343.6 | 277 | 108.2 | 89.9 | 84 | 83.9 | 97.1 | 82.9
541 | 402 | 528.1 | 280.9 | 344.1 | 277.5 | 108.6 | 90.2 | 84.3 | 84.2 | 97.5 | 83.3
542 | 403 | 528.2 | 281.4 | 344.7 | 278 | 108.9 | 90.5 | 84.6 | 84.6 | 97.9 | 83.6
543 | 404 | 528.2 | 281.9 | 345.2 | 278.5 | 109.3 | 90.8 | 85 | 84.9 | 98.3 | 84
544 | 405 | 528.2 | 282.4 | 345.7 | 279 | 109.6 | 91.2 | 85.3 | 85.2 | 98.7 | 84.3
545 | 406 | 528.2 | 282.9 | 346.2 | 279.5 | 110 | 91.5 | 85.6 | 85.5 | 99.1 | 84.7
546 | 407 | 528.2 | 283.5 | 346.7 | 280 | 110.4 | 91.8 | 85.9 | 85.8 | 99.5 | 85
547 | 408 | 528.2 | 284 | 347.3 | 280.5 | 110.7 | 92.1 | 86.3 | 86.2 | 99.9 | 85.3
548 | 409 | 528.3 | 284.5 | 347.8 | 281 | 111 | 92.4 | 86.6 | 86.4 | 100.3 | 85.7
549 | 410 | 528.3 | 285 | 348.3 | 281.5 | 111.4 | 92.7 | 86.9 | 86.7 | 100.6 | 86
550 | 411 | 528.3 | 285.5 | 348.8 | 281.9 | 111.7 | 93 | 87.2 | 87 | 101 | 86.4
551 | 412 | 528.4 | 286 | 349.3 | 282.4 | 112.1 | 93.3 | 87.6 | 87.3 | 101.4 | 86.7
552 | 413 | 528.4 | 286.5 | 349.8 | 282.9 | 112.5 | 93.6 | 87.9 | 87.7 | 101.8 | 87
553 | 414 | 528.4 | 287 | 350.4 | 283.4 | 112.8 | 93.9 | 88.3 | 88 | 102.2 | 87.4
554 | 415 | 528.4 | 287.6 | 350.9 | 283.9 | 113.2 | 94.2 | 88.6 | 88.3 | 102.6 | 87.7
555 | 416 | 528.4 | 288.1 | 351.4 | 284.4 | 113.6 | 94.5 | 88.9 | 88.6 | 103 | 88
556 | 417 | 528.4 | 288.6 | 351.9 | 284.9 | 114 | 94.8 | 89.3 | 88.9 | 103.4 | 88.4
557 | 418 | 528.4 | 289.1 | 352.3 | 285.4 | 114.4 | 95.2 | 89.6 | 89.2 | 103.8 | 88.7
558 | 419 | 528.4 | 289.6 | 352.8 | 285.8 | 114.8 | 95.5 | 90 | 89.5 | 104.2 | 89.1
559 | 420 | 528.4 | 290.1 | 353.3 | 286.3 | 115.2 | 95.8 | 90.3 | 89.8 | 104.6 | 89.4
560 | 421 | 528.4 | 290.6 | 353.8 | 286.8 | 115.6 | 96.1 | 90.7 | 90.1 | 105.1 | 89.7
561 | 422 | 528.4 | 291.1 | 354.3 | 287.3 | 116.1 | 96.4 | 91 | 90.4 | 105.5 | 90
562 | 423 | 528.4 | 291.7 | 354.7 | 287.7 | 116.5 | 96.8 | 91.4 | 90.7 | 105.9 | 90.4
563 | 424 | 528.4 | 292.1 | 355.4 | 288.2 | 116.9 | 97.1 | 91.8 | 90.9 | 106.3 | 90.7
564 | 425 | 528.4 | 292.6 | 355.8 | 288.7 | 117.3 | 97.4 | 92.1 | 91.2 | 106.7 | 91.1
565 | 426 | 528.4 | 293.1 | 356.2 | 289.2 | 117.7 | 97.7 | 92.5 | 91.5 | 107.1 | 91.4
566 | 427 | 528.4 | 293.6 | 356.7 | 289.6 | 118.1 | 98 | 92.9 | 91.7 | 107.5 | 91.7
567 | 428 | 528.4 | 294.1 | 357.2 | 290.1 | 118.6 | 98.3 | 93.2 | 92 | 107.9 | 92.1
568 | 429 | 528.4 | 294.6 | 357.6 | 290.6 | 119 | 98.7 | 93.6 | 92.3 | 108.3 | 92.4
569 | 430 | 528.4 | 295.1 | 358 | 291.1 | 119.5 | 99 | 94 | 92.5 | 108.7 | 92.8
570 | 431 | 528.4 | 295.6 | 358.6 | 291.5 | 119.9 | 99.3 | 94.3 | 92.8 | 109.1 | 93.1
571 | 432 | 528.5 | 296.1 | 359.1 | 292 | 120.4 | 99.7 | 94.7 | 93.1 | 109.5 | 93.5
572 | 433 | 528.5 | 296.6 | 359.5 | 292.5 | 120.8 | 100 | 95.1 | 93.4 | 109.9 | 93.9
573 | 434 | 528.5 | 297.1 | 360 | 292.9 | 121.3 | 100.3 | 95.4 | 93.7 | 110.3 | 94.2
574 | 435 | 528.5 | 297.5 | 360.4 | 293.4 | 121.8 | 100.7 | 95.8 | 94 | 110.7 | 94.6
575 | 436 | 528.5 | 298 | 360.9 | 293.9 | 122.3 | 101 | 96.2 | 94.3 | 111.1 | 94.9
576 | 437 | 528.5 | 298.5 | 361.4 | 294.3 | 122.7 | 101.4 | 96.5 | 94.6 | 111.6 | 95.2
577 | 438 | 528.5 | 299 | 361.9 | 294.8 | 123.2 | 101.7 | 96.9 | 94.9 | 112 | 95.6
578 | 439 | 528.5 | 299.5 | 362.3 | 295.3 | 123.8 | 102.1 | 97.2 | 95.1 | 112.4 | 95.9
579 | 440 | 528.5 | 299.9 | 362.8 | 295.7 | 124.2 | 102.4 | 97.6 | 95.4 | 112.8 | 96.2
580 | 441 | 528.5 | 300.4 | 363.3 | 296.1 | 124.7 | 102.8 | 97.9 | 95.6 | 113.2 | 96.6
581 | 442 | 528.5 | 300.9 | 363.8 | 296.6 | 125.2 | 103.1 | 98.2 | 95.9 | 113.6 | 96.9
582 | 443 | 528.5 | 301.4 | 364.3 | 297 | 125.8 | 103.5 | 98.6 | 96.2 | 114 | 97.3
583 | 444 | 528.5 | 301.8 | 364.7 | 297.5 | 126.3 | 103.9 | 99 | 96.5 | 114.4 | 97.6
584 | 445 | 528.5 | 302.3 | 365.2 | 297.9 | 126.8 | 104.3 | 99.3 | 96.8 | 114.8 | 98
585 | 446 | 528.5 | 302.8 | 365.7 | 298.4 | 127.4 | 104.7 | 99.6 | 97.1 | 115.2 | 98.3
586 | 447 | 528.5 | 303.3 | 366.1 | 298.8 | 128 | 105.1 | 100 | 97.3 | 115.6 | 98.7
587 | 448 | 528.5 | 303.7 | 366.5 | 299.3 | 128.5 | 105.5 | 100.3 | 97.6 | 116 | 99
588 | 449 | 528.5 | 304.2 | 367 | 299.7 | 129.1 | 105.9 | 100.7 | 97.9 | 116.4 | 99.4
589 | 450 | 528.5 | 304.7 | 367.4 | 300.2 | 129.7 | 106.3 | 101 | 98.1 | 116.8 | 99.7
590 | 451 | 528.5 | 305.1 | 367.9 | 300.6 | 130.2 | 106.7 | 101.3 | 98.4 | 117.2 | 100
591 | 452 | 528.5 | 305.6 | 368.4 | 301.1 | 130.8 | 107.2 | 101.7 | 98.6 | 117.6 | 100.3
592 | 453 | 528.5 | 306 | 368.8 | 301.5 | 131.4 | 107.6 | 102 | 98.9 | 118 | 100.6
593 | 454 | 528.5 | 306.5 | 369.2 | 302 | 131.9 | 108 | 102.4 | 99.2 | 118.4 | 101
594 | 455 | 528.5 | 307 | 369.6 | 302.4 | 132.5 | 108.5 | 102.7 | 99.4 | 118.8 | 101.3
595 | 456 | 528.5 | 307.5 | 370 | 302.9 | 133.1 | 108.9 | 103 | 99.7 | 119.2 | 101.7
596 | 457 | 528.5 | 307.9 | 370.5 | 303.3 | 133.7 | 109.4 | 103.4 | 100 | 119.6 | 102
597 | 458 | 528.5 | 308.4 | 371 | 303.7 | 134.2 | 109.8 | 103.8 | 100.3 | 120 | 102.4
598 | 459 | 528.5 | 308.8 | 371.4 | 304.2 | 134.8 | 110.3 | 104.1 | 100.5 | 120.4 | 102.8
599 | 460 | 528.4 | 309.3 | 371.8 | 304.6 | 135.3 | 110.7 | 104.5 | 100.8 | 120.8 | 103.1
600 | 461 | 528.4 | 309.7 | 372.2 | 305 | 135.9 | 111.2 | 104.8 | 101.1 | 121.2 | 103.4
601 | 462 | 528.4 | 310.2 | 372.6 | 305.5 | 136.4 | 111.6 | 105.2 | 101.4 | 121.6 | 103.8
602 | 463 | 528.4 | 310.6 | 373 | 305.9 | 137 | 112 | 105.6 | 101.6 | 122 | 104.2
603 | 464 | 528.4 | 311.1 | 373.5 | 306.4 | 137.5 | 112.5 | 106 | 101.9 | 122.4 | 104.5
604 | 465 | 528.3 | 311.5 | 373.9 | 306.8 | 138 | 112.9 | 106.3 | 102.2 | 122.8 | 104.8
605 | 466 | 528.3 | 312 | 374.2 | 307.2 | 138.6 | 113.4 | 106.7 | 102.5 | 123.2 | 105.2
606 | 467 | 528.3 | 312.4 | 374.7 | 307.6 | 139.1 | 113.8 | 107.1 | 102.7 | 123.6 | 105.5
607 | 468 | 528.3 | 312.9 | 375.1 | 308.1 | 139.6 | 114.3 | 107.5 | 103 | 124 | 105.8
608 | 469 | 528.3 | 313.3 | 375.6 | 308.5 | 140.1 | 114.7 | 107.9 | 103.3 | 124.4 | 106.2
609 | 470 | 528.3 | 313.7 | 376 | 308.9 | 140.6 | 115.1 | 108.3 | 103.6 | 124.8 | 106.5
610 | 471 | 528.2 | 314.2 | 376.4 | 309.4 | 141.1 | 115.6 | 108.7 | 103.9 | 125.1 | 106.9
611 | 472 | 528.2 | 314.6 | 376.7 | 309.8 | 141.6 | 116 | 109.1 | 104.2 | 125.5 | 107.2
612 | 473 | 528.2 | 315.1 | 377.2 | 310.2 | 142.1 | 116.5 | 109.5 | 104.5 | 125.9 | 107.5
613 | 474 | 528.2 | 315.5 | 377.5 | 310.6 | 142.6 | 116.9 | 109.9 | 104.8 | 126.3 | 107.9
614 | 475 | 528.2 | 316 | 377.9 | 311 | 143.1 | 117.4 | 110.3 | 105.1 | 126.7 | 108.2
615 | 476 | 528.2 | 316.4 | 378.4 | 311.4 | 143.6 | 117.8 | 110.7 | 105.4 | 127.1 | 108.5
616 | 477 | 528.2 | 316.8 | 378.8 | 311.9 | 144.1 | 118.2 | 111.2 | 105.7 | 127.5 | 108.9
617 | 478 | 528.1 | 317.2 | 379.2 | 312.3 | 144.6 | 118.7 | 111.6 | 106 | 127.9 | 109.2
618 | 479 | 528.1 | 317.7 | 379.6 | 312.7 | 145.1 | 119.2 | 112 | 106.3 | 128.3 | 109.5
619 | 480 | 528.2 | 318.1 | 380 | 313.1 | 145.5 | 119.6 | 112.4 | 106.6 | 128.7 | 109.9
620 | 481 | 528.2 | 318.5 | 380.4 | 313.5 | 146 | 120.1 | 112.9 | 106.9 | 129 | 110.2
621 | 482 | 528.2 | 318.9 | 380.8 | 313.9 | 146.4 | 120.5 | 113.3 | 107.2 | 129.4 | 110.6
622 | 483 | 528.2 | 319.3 | 381.3 | 314.3 | 146.7 | 120.9 | 113.7 | 107.6 | 129.8 | 110.9
623 | 484 | 528.2 | 319.7 | 381.7 | 314.7 | 147.2 | 121.4 | 114.2 | 107.9 | 130.2 | 111.2
624 | 485 | 528.2 | 320.2 | 382.1 | 315.1 | 147.7 | 121.8 | 114.6 | 108.2 | 130.6 | 111.6
625 | 486 | 528.1 | 320.6 | 382.4 | 315.5 | 148.2 | 122.3 | 115 | 108.5 | 131 | 111.9
626 | 487 | 528.1 | 321 | 382.8 | 315.9 | 148.7 | 122.7 | 115.5 | 108.9 | 131.3 | 112.3
627 | 488 | 528 | 321.5 | 383.2 | 316.4 | 149.2 | 123.2 | 115.9 | 109.3 | 131.7 | 112.6
628 | 489 | 528 | 321.9 | 383.5 | 316.8 | 149.8 | 123.7 | 116.3 | 109.6 | 132.1 | 112.9
629 | 490 | 528 | 322.4 | 383.8 | 317.2 | 150.4 | 124.2 | 116.8 | 110 | 132.5 | 113.3
630 | 491 | 528 | 322.8 | 384.2 | 317.6 | 150.9 | 124.7 | 117.2 | 110.4 | 132.8 | 113.6
631 | 492 | 528 | 323.2 | 384.5 | 318 | 151.3 | 125.1 | 117.7 | 110.8 | 133.2 | 113.9
632 | 493 | 528 | 323.6 | 384.9 | 318.5 | 151.8 | 125.6 | 118.1 | 111.1 | 133.6 | 114.3
633 | 494 | 528 | 324 | 385.3 | 318.9 | 152.3 | 126 | 118.6 | 111.5 | 134 | 114.7
634 | 495 | 527.9 | 324.5 | 385.7 | 319.2 | 152.8 | 126.5 | 119 | 111.9 | 134.3 | 115
635 | 496 | 527.9 | 324.9 | 386 | 319.6 | 153.3 | 127 | 119.5 | 112.3 | 134.7 | 115.4
636 | 497 | 527.9 | 325.3 | 386.4 | 320 | 153.7 | 127.4 | 119.9 | 112.7 | 135.1 | 115.8
637 | 498 | 527.9 | 325.7 | 386.8 | 320.4 | 154.2 | 127.9 | 120.4 | 113 | 135.4 | 116.1
638 | 499 | 528 | 326.1 | 387.2 | 320.8 | 154.7 | 128.3 | 120.8 | 113.4 | 135.8 | 116.4
639 | 500 | 527.9 | 326.5 | 387.6 | 321.2 | 155.1 | 128.8 | 121.3 | 113.8 | 136.2 | 116.7
640 | 501 | 527.9 | 326.9 | 387.9 | 321.6 | 155.6 | 129.3 | 121.7 | 114.2 | 136.5 | 117.1
641 | 502 | 527.9 | 327.3 | 388.3 | 322 | 156.2 | 129.7 | 122.2 | 114.6 | 136.9 | 117.4
642 | 503 | 527.8 | 327.7 | 388.6 | 322.4 | 156.7 | 130.2 | 122.7 | 115 | 137.3 | 117.8
643 | 504 | 527.8 | 328.1 | 389 | 322.7 | 157.2 | 130.7 | 123.1 | 115.4 | 137.6 | 118.1
644 | 505 | 527.8 | 328.5 | 389.3 | 323.1 | 157.7 | 131.1 | 123.6 | 115.8 | 138 | 118.4
645 | 506 | 527.8 | 328.9 | 389.7 | 323.5 | 158.2 | 131.6 | 124.1 | 116.2 | 138.4 | 118.8
646 | 507 | 527.8 | 329.3 | 390.1 | 323.9 | 158.7 | 132.1 | 124.6 | 116.5 | 138.7 | 119.1
647 | 508 | 527.8 | 329.7 | 390.4 | 324.3 | 159.2 | 132.5 | 125 | 116.8 | 139.1 | 119.5
648 | 509 | 527.8 | 330.2 | 390.7 | 324.7 | 159.7 | 133 | 125.5 | 117.2 | 139.4 | 119.8
649 | 510 | 527.7 | 330.5 | 391 | 325.1 | 160.2 | 133.5 | 126 | 117.6 | 139.8 | 120.2
650 | 511 | 527.7 | 330.9 | 391.5 | 325.5 | 160.7 | 133.9 | 126.5 | 118 | 140.2 | 120.5
651 | 512 | 527.7 | 331.3 | 391.8 | 325.9 | 161.1 | 134.4 | 127 | 118.4 | 140.5 | 120.9
652 | 513 | 527.7 | 331.7 | 392.2 | 326.3 | 161.6 | 134.8 | 127.5 | 118.8 | 140.9 | 121.3
653 | 514 | 527.7 | 332.1 | 392.6 | 326.6 | 162.1 | 135.3 | 127.9 | 119.1 | 141.3 | 121.6
654 | 515 | 527.7 | 332.5 | 392.9 | 327 | 162.6 | 135.7 | 128.4 | 119.6 | 141.6 | 121.9
655 | 516 | 527.8 | 332.9 | 393.3 | 327.4 | 163.1 | 136.2 | 128.9 | 120 | 142 | 122.2
656 | 517 | 527.8 | 333.3 | 393.5 | 327.7 | 163.6 | 136.7 | 129.4 | 120.4 | 142.4 | 122.6
657 | 518 | 527.8 | 333.6 | 393.9 | 328.1 | 164 | 137.1 | 129.9 | 120.8 | 142.7 | 123
658 | 519 | 527.8 | 334 | 394.2 | 328.5 | 164.5 | 137.6 | 130.4 | 121.1 | 143.1 | 123.3
659 | 520 | 527.8 | 334.4 | 394.5 | 328.9 | 165 | 138.1 | 130.9 | 121.5 | 143.4 | 123.7
660 | 521 | 527.8 | 334.8 | 394.9 | 329.3 | 165.5 | 138.5 | 131.4 | 121.9 | 143.8 | 124
661 | 522 | 527.7 | 335.2 | 395.3 | 329.6 | 165.9 | 139 | 131.9 | 122.3 | 144.2 | 124.4
662 | 523 | 527.7 | 335.6 | 395.6 | 330 | 166.4 | 139.5 | 132.4 | 122.7 | 144.5 | 124.7
663 | 524 | 527.7 | 335.9 | 395.9 | 330.4 | 166.9 | 139.9 | 132.9 | 123.1 | 144.9 | 125.1
664 | 525 | 527.7 | 336.3 | 396.3 | 330.7 | 167.4 | 140.4 | 133.4 | 123.5 | 145.2 | 125.4
665 | 526 | 527.7 | 336.7 | 396.5 | 331.1 | 167.8 | 140.8 | 133.9 | 123.8 | 145.6 | 125.8
666 | 527 | 527.6 | 337.1 | 396.9 | 331.4 | 168.3 | 141.3 | 134.4 | 124.2 | 145.9 | 126.2
667 | 528 | 527.6 | 337.5 | 397.3 | 331.8 | 168.8 | 141.8 | 134.9 | 124.6 | 146.3 | 126.6
668 | 529 | 527.6 | 337.8 | 397.6 | 332.2 | 169.3 | 142.2 | 135.4 | 125 | 146.6 | 127
669 | 530 | 527.6 | 338.2 | 397.9 | 332.5 | 169.8 | 142.7 | 135.9 | 125.4 | 146.9 | 127.4
670 | 531 | 527.5 | 338.6 | 398.2 | 332.9 | 170.3 | 143.1 | 136.4 | 125.8 | 147.3 | 127.8
671 | 532 | 527.5 | 339 | 398.5 | 333.3 | 170.8 | 143.6 | 136.9 | 126.2 | 147.6 | 128.2
672 | 533 | 527.5 | 339.4 | 398.8 | 333.7 | 171.3 | 144.1 | 137.4 | 126.6 | 148 | 128.6
673 | 534 | 527.5 | 339.8 | 399.1 | 334 | 171.8 | 144.5 | 137.9 | 127 | 148.4 | 129
674 | 535 | 527.5 | 340.1 | 399.5 | 334.4 | 172.3 | 145 | 138.4 | 127.4 | 148.7 | 129.3
675 | 536 | 527.5 | 340.5 | 399.8 | 334.7 | 172.8 | 145.4 | 138.9 | 127.8 | 149.1 | 129.7
676 | 537 | 527.5 | 340.8 | 400.2 | 335.1 | 173.3 | 145.9 | 139.3 | 128.2 | 149.5 | 130.1
677 | 538 | 527.5 | 341.2 | 400.5 | 335.4 | 173.7 | 146.3 | 139.8 | 128.6 | 149.9 | 130.4
678 | 539 | 527.5 | 341.6 | 400.8 | 335.8 | 174.2 | 146.8 | 140.3 | 129 | 150.3 | 130.8
679 | 540 | 527.5 | 341.9 | 401.1 | 336.2 | 174.7 | 147.2 | 140.8 | 129.4 | 150.7 | 131.2
680 | 541 | 527.5 | 342.3 | 401.4 | 336.5 | 175.2 | 147.7 | 141.3 | 129.8 | 151.1 | 131.6
681 | 542 | 527.5 | 342.7 | 401.7 | 336.9 | 175.7 | 148.1 | 141.8 | 130.3 | 151.5 | 131.9
682 | 543 | 527.5 | 343 | 402 | 337.2 | 176.2 | 148.5 | 142.3 | 130.7 | 151.9 | 132.3
683 | 544 | 527.6 | 343.4 | 402.3 | 337.5 | 176.6 | 149 | 142.8 | 131 | 152.3 | 132.6
684 | 545 | 527.6 | 343.7 | 402.7 | 337.9 | 177.1 | 149.4 | 143.2 | 131.4 | 152.8 | 133
685 | 546 | 527.6 | 344.1 | 403 | 338.3 | 177.6 | 149.8 | 143.7 | 131.8 | 153.2 | 133.4
686 | 547 | 527.7 | 344.5 | 403.4 | 338.6 | 178 | 150.2 | 144.2 | 132.3 | 153.6 | 133.8
687 | 548 | 527.6 | 344.8 | 403.6 | 339 | 178.5 | 150.7 | 144.7 | 132.6 | 154.1 | 134.2
688 | 549 | 527.7 | 345.2 | 403.9 | 339.3 | 179 | 151.1 | 145.1 | 133 | 154.5 | 134.6
689 | 550 | 527.7 | 345.6 | 404.2 | 339.6 | 179.5 | 151.6 | 145.6 | 133.4 | 155 | 134.9
690 | 551 | 527.7 | 345.9 | 404.5 | 340 | 180 | 152 | 146.1 | 133.9 | 155.4 | 135.3
691 | 552 | 527.7 | 346.2 | 404.8 | 340.3 | 180.5 | 152.5 | 146.5 | 134.3 | 155.9 | 135.6
692 | 553 | 527.7 | 346.6 | 405.1 | 340.7 | 181 | 152.9 | 147 | 134.7 | 156.4 | 136
693 | 554 | 527.7 | 347 | 405.4 | 341.1 | 181.4 | 153.3 | 147.5 | 135.1 | 156.8 | 136.3
694 | 555 | 527.7 | 347.3 | 405.7 | 341.4 | 181.9 | 153.8 | 147.9 | 135.5 | 157.3 | 136.7
695 | 556 | 527.7 | 347.6 | 406 | 341.7 | 182.4 | 154.2 | 148.4 | 136 | 157.8 | 137
696 | 557 | 527.7 | 348 | 406.4 | 342 | 182.9 | 154.6 | 148.8 | 136.5 | 158.2 | 137.4
697 | 558 | 527.7 | 348.3 | 406.6 | 342.4 | 183.3 | 155.1 | 149.3 | 136.9 | 158.7 | 137.7
698 | 559 | 527.7 | 348.7 | 406.9 | 342.8 | 183.9 | 155.5 | 149.7 | 137.4 | 159.2 | 138.1
699 | 560 | 527.7 | 349 | 407.2 | 343.1 | 184.3 | 155.9 | 150.1 | 137.9 | 159.7 | 138.4
700 | 561 | 527.6 | 349.4 | 407.5 | 343.4 | 184.8 | 156.4 | 150.6 | 138.3 | 160.2 | 138.8
701 | 562 | 527.6 | 349.7 | 407.8 | 343.8 | 185.3 | 156.8 | 151 | 138.7 | 160.6 | 139.1
702 | 563 | 527.6 | 350.1 | 408.1 | 344.1 | 185.8 | 157.3 | 151.5 | 139.2 | 161.1 | 139.5
703 | 564 | 527.6 | 350.4 | 408.4 | 344.4 | 186.2 | 157.7 | 151.9 | 139.6 | 161.6 | 139.9
704 | 565 | 527.6 | 350.8 | 408.7 | 344.8 | 186.7 | 158.1 | 152.3 | 140 | 162.1 | 140.2
705 | 566 | 527.5 | 351.1 | 409 | 345.1 | 187.1 | 158.6 | 152.8 | 140.5 | 162.6 | 140.6
706 | 567 | 527.5 | 351.4 | 409.3 | 345.4 | 187.6 | 159 | 153.2 | 140.9 | 163.1 | 141
707 | 568 | 527.5 | 351.8 | 409.6 | 345.7 | 188.1 | 159.5 | 153.6 | 141.3 | 163.5 | 141.4
708 | 569 | 527.5 | 352.1 | 409.8 | 346.1 | 188.6 | 159.9 | 154 | 141.7 | 164 | 141.8
709 | 570 | 527.5 | 352.5 | 410.1 | 346.4 | 189 | 160.4 | 154.5 | 142.1 | 164.5 | 142.1
710 | 571 | 527.6 | 352.8 | 410.4 | 346.7 | 189.5 | 160.8 | 154.9 | 142.6 | 165 | 142.4
711 | 572 | 527.5 | 353.1 | 410.7 | 347.1 | 189.9 | 161.3 | 155.3 | 143 | 165.5 | 142.7
712 | 573 | 527.5 | 353.5 | 411 | 347.4 | 190.4 | 161.7 | 155.7 | 143.4 | 166 | 143.1
713 | 574 | 527.5 | 353.8 | 411.3 | 347.8 | 190.9 | 162.2 | 156.2 | 143.9 | 166.5 | 143.4
714 | 575 | 527.5 | 354.1 | 411.5 | 348.1 | 191.3 | 162.6 | 156.6 | 144.3 | 166.9 | 143.7
715 | 576 | 527.5 | 354.5 | 411.8 | 348.4 | 191.8 | 163 | 157 | 144.8 | 167.4 | 144.1
716 | 577 | 527.5 | 354.8 | 412.1 | 348.7 | 192.3 | 163.5 | 157.4 | 145.3 | 167.9 | 144.4
717 | 578 | 527.5 | 355.1 | 412.4 | 349 | 192.7 | 163.9 | 157.9 | 145.7 | 168.4 | 144.8
718 | 579 | 527.5 | 355.5 | 412.7 | 349.4 | 193.2 | 164.4 | 158.3 | 146.1 | 168.9 | 145.1
719 | 580 | 527.5 | 355.8 | 412.9 | 349.7 | 193.7 | 164.8 | 158.7 | 146.6 | 169.4 | 145.4
720 | 581 | 527.5 | 356.1 | 413.2 | 350 | 194.2 | 165.3 | 159.1 | 147 | 169.9 | 145.7
721 | 582 | 527.5 | 356.5 | 413.5 | 350.3 | 194.6 | 165.7 | 159.6 | 147.4 | 170.4 | 146.1
722 | 583 | 527.5 | 356.8 | 413.7 | 350.6 | 195.1 | 166.2 | 160 | 147.9 | 170.9 | 146.4
723 | 584 | 527.5 | 357.1 | 414 | 350.9 | 195.6 | 166.6 | 160.4 | 148.3 | 171.3 | 146.7
724 | 585 | 527.6 | 357.4 | 414.3 | 351.2 | 196 | 167 | 160.8 | 148.7 | 171.8 | 147
725 | 586 | 527.6 | 357.7 | 414.6 | 351.6 | 196.5 | 167.5 | 161.2 | 149.2 | 172.3 | 147.4
726 | 587 | 527.6 | 358.1 | 414.9 | 351.9 | 197 | 167.9 | 161.7 | 149.7 | 172.7 | 147.7
727 | 588 | 527.7 | 358.4 | 415.2 | 352.2 | 197.5 | 168.4 | 162.1 | 150.1 | 173.2 | 148
728 | 589 | 527.7 | 358.7 | 415.4 | 352.5 | 198 | 168.9 | 162.5 | 150.6 | 173.6 | 148.3
729 | 590 | 527.8 | 359 | 415.7 | 352.8 | 198.4 | 169.3 | 162.9 | 151.1 | 174.1 | 148.6
730 | 591 | 527.8 | 359.4 | 416 | 353.2 | 198.9 | 169.7 | 163.3 | 151.6 | 174.6 | 148.8
731 | 592 | 527.8 | 359.6 | 416.3 | 353.5 | 199.3 | 170.2 | 163.7 | 152 | 175 | 149.1
732 | 593 | 527.7 | 360 | 416.6 | 353.8 | 199.8 | 170.6 | 164.1 | 152.5 | 175.5 | 149.5
733 | 594 | 527.7 | 360.3 | 416.8 | 354.1 | 200.2 | 171.1 | 164.5 | 153 | 175.9 | 149.8
734 | 595 | 527.8 | 360.6 | 417.1 | 354.4 | 200.7 | 171.5 | 164.9 | 153.5 | 176.3 | 150.2
735 | 596 | 527.8 | 360.9 | 417.4 | 354.7 | 201.1 | 171.9 | 165.4 | 153.9 | 176.8 | 150.6
736 | 597 | 527.8 | 361.2 | 417.7 | 355 | 201.6 | 172.4 | 165.8 | 154.4 | 177.2 | 151
737 | 598 | 527.8 | 361.5 | 418 | 355.3 | 202 | 172.8 | 166.2 | 154.9 | 177.7 | 151.4
738 | 599 | 527.8 | 361.8 | 418.2 | 355.6 | 202.5 | 173.3 | 166.6 | 155.4 | 178.1 | 151.8
739 | 600 | 527.8 | 362.1 | 418.5 | 355.9 | 203 | 173.7 | 167 | 155.8 | 178.5 | 152.2
740 | 601 | 527.9 | 362.4 | 418.7 | 356.2 | 203.5 | 174.2 | 167.4 | 156.3 | 178.9 | 152.7
741 | 602 | 527.9 | 362.7 | 419 | 356.5 | 203.9 | 174.6 | 167.8 | 156.8 | 179.3 | 153.1
742 | 603 | 527.9 | 363.1 | 419.3 | 356.8 | 204.4 | 175.1 | 168.2 | 157.2 | 179.7 | 153.5
743 | 604 | 527.9 | 363.4 | 419.5 | 357.1 | 204.9 | 175.5 | 168.6 | 157.7 | 180.2 | 153.9
744 | 605 | 527.9 | 363.6 | 419.8 | 357.4 | 205.4 | 176 | 169 | 158.1 | 180.6 | 154.2
745 | 606 | 527.9 | 364 | 420 | 357.7 | 205.9 | 176.4 | 169.4 | 158.6 | 181 | 154.5
746 | 607 | 527.9 | 364.2 | 420.3 | 358 | 206.3 | 176.9 | 169.8 | 159 | 181.4 | 154.8
747 | 608 | 527.8 | 364.6 | 420.6 | 358.3 | 206.8 | 177.3 | 170.2 | 159.4 | 181.8 | 155.2
748 | 609 | 527.8 | 364.8 | 420.9 | 358.6 | 207.2 | 177.8 | 170.6 | 159.8 | 182.3 | 155.6
749 | 610 | 527.8 | 365.1 | 421.1 | 358.9 | 207.6 | 178.2 | 171.1 | 160.3 | 182.7 | 156
750 | 611 | 527.8 | 365.4 | 421.4 | 359.2 | 208.1 | 178.6 | 171.4 | 160.7 | 183.1 | 156.4
751 | 612 | 527.9 | 365.7 | 421.7 | 359.5 | 208.6 | 179.1 | 171.8 | 161.1 | 183.5 | 156.7
752 | 613 | 527.9 | 366 | 422 | 359.8 | 209 | 179.5 | 172.3 | 161.6 | 184 | 157.1
753 | 614 | 527.9 | 366.3 | 422.2 | 360.1 | 209.5 | 180 | 172.6 | 162 | 184.4 | 157.5
754 | 615 | 527.8 | 366.6 | 422.5 | 360.4 | 209.9 | 180.5 | 173.1 | 162.5 | 184.8 | 157.9
755 | 616 | 527.8 | 366.9 | 422.8 | 360.7 | 210.3 | 180.9 | 173.4 | 162.9 | 185.2 | 158.3
756 | 617 | 527.8 | 367.2 | 423 | 360.9 | 210.8 | 181.3 | 173.8 | 163.3 | 185.7 | 158.7
757 | 618 | 527.8 | 367.5 | 423.2 | 361.2 | 211.3 | 181.8 | 174.2 | 163.7 | 186.1 | 159.1
758 | 619 | 527.8 | 367.8 | 423.5 | 361.5 | 211.8 | 182.3 | 174.6 | 164.1 | 186.5 | 159.5
759 | 620 | 527.7 | 368 | 423.7 | 361.8 | 212.2 | 182.7 | 175 | 164.5 | 187 | 159.9
760 | 621 | 527.7 | 368.3 | 424 | 362.1 | 212.7 | 183.2 | 175.4 | 164.9 | 187.4 | 160.3
761 | 622 | 527.7 | 368.7 | 424.2 | 362.4 | 213.1 | 183.6 | 175.8 | 165.3 | 187.8 | 160.7
762 | 623 | 527.7 | 368.9 | 424.5 | 362.7 | 213.5 | 184.1 | 176.2 | 165.7 | 188.3 | 161.1
763 | 624 | 527.7 | 369.2 | 424.7 | 363 | 214 | 184.6 | 176.6 | 166.1 | 188.7 | 161.4
764 | 625 | 527.6 | 369.5 | 425 | 363.2 | 214.4 | 185 | 177 | 166.4 | 189.2 | 161.8
765 | 626 | 527.6 | 369.8 | 425.2 | 363.6 | 214.9 | 185.5 | 177.4 | 166.8 | 189.6 | 162.1
766 | 627 | 527.6 | 370.1 | 425.5 | 363.8 | 215.2 | 185.9 | 177.8 | 167.2 | 190.1 | 162.5
767 | 628 | 527.6 | 370.4 | 425.7 | 364.1 | 215.7 | 186.4 | 178.2 | 167.6 | 190.5 | 162.9
768 | 629 | 527.6 | 370.6 | 425.9 | 364.4 | 216.1 | 186.8 | 178.6 | 168 | 191 | 163.2
769 | 630 | 527.6 | 370.9 | 426.2 | 364.7 | 216.5 | 187.3 | 179 | 168.4 | 191.4 | 163.6
770 | 631 | 527.7 | 371.2 | 426.4 | 364.9 | 216.9 | 187.8 | 179.5 | 168.8 | 191.9 | 164
771 | 632 | 527.7 | 371.5 | 426.7 | 365.2 | 217.4 | 188.2 | 179.9 | 169.1 | 192.3 | 164.4
772 | 633 | 527.7 | 371.7 | 426.9 | 365.5 | 217.7 | 188.7 | 180.3 | 169.5 | 192.8 | 164.7
773 | 634 | 527.7 | 372 | 427.1 | 365.8 | 218.1 | 189.1 | 180.7 | 169.9 | 193.2 | 165.1
774 | 635 | 527.7 | 372.3 | 427.4 | 366 | 218.5 | 189.6 | 181.1 | 170.3 | 193.7 | 165.5
775 | 636 | 527.6 | 372.6 | 427.6 | 366.3 | 218.9 | 190 | 181.5 | 170.6 | 194.2 | 165.9
776 | 637 | 527.6 | 372.9 | 427.8 | 366.6 | 219.3 | 190.5 | 181.9 | 171 | 194.6 | 166.3
777 | 638 | 527.6 | 373.1 | 428.1 | 366.9 | 219.7 | 190.9 | 182.3 | 171.4 | 195.1 | 166.8
778 | 639 | 527.6 | 373.4 | 428.3 | 367.1 | 220.1 | 191.4 | 182.7 | 171.8 | 195.6 | 167.3
779 | 640 | 527.5 | 373.7 | 428.6 | 367.4 | 220.5 | 191.8 | 183.1 | 172.2 | 196.1 | 167.8
780 | 641 | 527.5 | 373.9 | 428.8 | 367.7 | 220.9 | 192.3 | 183.5 | 172.6 | 196.5 | 168.1
781 | 642 | 527.4 | 374.2 | 429 | 368 | 221.3 | 192.7 | 183.8 | 173 | 197 | 168.3
782 | 643 | 527.4 | 374.5 | 429.2 | 368.2 | 221.8 | 193.2 | 184.2 | 173.4 | 197.5 | 168.6
783 | 644 | 527.4 | 374.8 | 429.5 | 368.5 | 222.2 | 193.6 | 184.6 | 173.8 | 198 | 168.8
784 | 645 | 527.4 | 375 | 429.7 | 368.8 | 222.6 | 194.1 | 185 | 174.2 | 198.4 | 169.1
785 | 646 | 527.4 | 375.3 | 429.9 | 369 | 223 | 194.5 | 185.3 | 174.6 | 198.9 | 169.4
786 | 647 | 527.3 | 375.6 | 430.1 | 369.3 | 223.4 | 195 | 185.7 | 174.9 | 199.4 | 169.7
787 | 648 | 527.3 | 375.9 | 430.4 | 369.5 | 223.8 | 195.4 | 186.1 | 175.3 | 199.9 | 170.1
788 | 649 | 527.2 | 376.1 | 430.6 | 369.8 | 224.2 | 195.9 | 186.5 | 175.7 | 200.4 | 170.4
789 | 650 | 527.2 | 376.4 | 430.8 | 370.1 | 224.6 | 196.3 | 186.8 | 176.2 | 200.9 | 170.7
790 | 651 | 527.1 | 376.7 | 431.1 | 370.3 | 224.9 | 196.8 | 187.2 | 176.6 | 201.3 | 171
791 | 652 | 527 | 376.9 | 431.3 | 370.6 | 225.3 | 197.2 | 187.6 | 176.9 | 201.8 | 171.4
792 | 653 | 527 | 377.2 | 431.5 | 370.9 | 225.8 | 197.7 | 188 | 177.3 | 202.3 | 171.8
793 | 654 | 526.9 | 377.5 | 431.7 | 371.1 | 226.1 | 198.1 | 188.3 | 177.7 | 202.8 | 172.3
794 | 655 | 526.9 | 377.7 | 431.9 | 371.4 | 226.5 | 198.6 | 188.7 | 178.1 | 203.3 | 172.7
795 | 656 | 526.8 | 378 | 432.1 | 371.7 | 226.9 | 199 | 189.1 | 178.5 | 203.8 | 173
796 | 657 | 526.8 | 378.3 | 432.3 | 371.9 | 227.3 | 199.5 | 189.4 | 178.9 | 204.3 | 173.3
797 | 658 | 526.8 | 378.6 | 432.5 | 372.2 | 227.7 | 199.9 | 189.8 | 179.4 | 204.8 | 173.6
798 | 659 | 526.8 | 378.8 | 432.8 | 372.4 | 228 | 200.3 | 190.2 | 179.7 | 205.3 | 174
799 | 660 | 526.8 | 379.1 | 433 | 372.7 | 228.5 | 200.8 | 190.5 | 180.1 | 205.8 | 174.6
800 | 661 | 526.8 | 379.3 | 433.2 | 372.9 | 228.8 | 201.2 | 190.9 | 180.5 | 206.3 | 175.4
801 | 662 | 526.8 | 379.6 | 433.4 | 373.2 | 229.2 | 201.6 | 191.3 | 180.8 | 206.8 | 175.8
802 | 663 | 526.9 | 379.9 | 433.6 | 373.4 | 229.6 | 202.1 | 191.6 | 181.2 | 207.3 | 176.2
803 | 664 | 526.9 | 380.1 | 433.8 | 373.7 | 229.9 | 202.5 | 192 | 181.6 | 207.8 | 176.8
804 | 665 | 526.9 | 380.4 | 434 | 373.9 | 230.3 | 202.9 | 192.4 | 181.9 | 208.3 | 177.5
805 | 666 | 527 | 380.6 | 434.3 | 374.2 | 230.7 | 203.4 | 192.7 | 182.3 | 208.8 | 178.1
806 | 667 | 527.1 | 380.9 | 434.5 | 374.4 | 231 | 203.8 | 193.1 | 182.6 | 209.3 | 178.6
807 | 668 | 527.1 | 381.1 | 434.7 | 374.7 | 231.4 | 204.2 | 193.5 | 183 | 209.8 | 179.2
808 | 669 | 527.1 | 381.4 | 434.9 | 374.9 | 231.7 | 204.6 | 193.8 | 183.4 | 210.2 | 179.9
809 | 670 | 527.2 | 381.6 | 435.1 | 375.1 | 232.1 | 205 | 194.2 | 183.8 | 210.7 | 180.6
810 | 671 | 527.2 | 381.9 | 435.3 | 375.4 | 232.4 | 205.4 | 194.5 | 184.1 | 211.2 | 181.1
811 | 672 | 527.3 | 382.1 | 435.5 | 375.6 | 232.8 | 205.9 | 194.9 | 184.5 | 211.7 | 181.5
812 | 673 | 527.3 | 382.4 | 435.7 | 375.9 | 233.2 | 206.3 | 195.2 | 185 | 212.2 | 181.9
813 | 674 | 527.3 | 382.6 | 436 | 376.1 | 233.6 | 206.7 | 195.6 | 185.4 | 212.7 | 182.5
814 | 675 | 527.3 | 382.9 | 436.1 | 376.4 | 234 | 207.2 | 195.9 | 185.7 | 213.2 | 183.1
815 | 676 | 527.3 | 383.2 | 436.3 | 376.7 | 234.3 | 207.6 | 196.3 | 186 | 213.7 | 183.8
816 | 677 | 527.3 | 383.4 | 436.5 | 376.9 | 234.7 | 208 | 196.6 | 186.4 | 214.2 | 184.4
817 | 678 | 527.3 | 383.7 | 436.7 | 377.2 | 235 | 208.4 | 196.9 | 186.7 | 214.7 | 184.9
818 | 679 | 527.3 | 383.9 | 437 | 377.4 | 235.4 | 208.9 | 197.3 | 187.1 | 215.2 | 185.3
819 | 680 | 527.3 | 384.2 | 437.1 | 377.7 | 235.8 | 209.3 | 197.6 | 187.5 | 215.6 | 185.8
820 | 681 | 527.3 | 384.4 | 437.3 | 377.9 | 236.1 | 209.7 | 198 | 187.9 | 216.1 | 186.4
821 | 682 | 527.3 | 384.6 | 437.5 | 378.2 | 236.5 | 210.1 | 198.3 | 188.2 | 216.6 | 186.9
822 | 683 | 527.3 | 384.9 | 437.7 | 378.4 | 236.8 | 210.5 | 198.6 | 188.5 | 217 | 187.5
823 | 684 | 527.3 | 385.2 | 437.9 | 378.7 | 237.2 | 211 | 199 | 188.9 | 217.5 | 188.1
824 | 685 | 527.3 | 385.4 | 438.2 | 379 | 237.5 | 211.4 | 199.3 | 189.3 | 218 | 188.6
825 | 686 | 527.3 | 385.6 | 438.3 | 379.2 | 237.8 | 211.8 | 199.6 | 189.7 | 218.4 | 189.2
826 | 687 | 527.3 | 385.9 | 438.5 | 379.5 | 238.1 | 212.2 | 200 | 190 | 218.9 | 189.8
827 | 688 | 527.3 | 386.1 | 438.7 | 379.7 | 238.4 | 212.6 | 200.3 | 190.3 | 219.4 | 190.4
828 | 689 | 527.3 | 386.4 | 438.9 | 380 | 238.8 | 213 | 200.7 | 190.7 | 219.8 | 190.9
829 | 690 | 527.3 | 386.6 | 439.1 | 380.2 | 239 | 213.4 | 201 | 191 | 220.3 | 191.5
830 | 691 | 527.3 | 386.9 | 439.3 | 380.5 | 239.4 | 213.8 | 201.3 | 191.4 | 220.7 | 192
831 | 692 | 527.3 | 387.1 | 439.5 | 380.7 | 239.7 | 214.2 | 201.7 | 191.7 | 221.1 | 192.6
832 | 693 | 527.3 | 387.3 | 439.7 | 381 | 240 | 214.6 | 202 | 192 | 221.5 | 193.2
833 | 694 | 527.2 | 387.6 | 439.9 | 381.2 | 240.2 | 215 | 202.3 | 192.3 | 222 | 193.7
834 | 695 | 527.2 | 387.8 | 440.1 | 381.5 | 240.5 | 215.5 | 202.6 | 192.7 | 222.4 | 194.2
835 | 696 | 527.2 | 388.1 | 440.3 | 381.7 | 240.8 | 215.8 | 203 | 193 | 222.8 | 194.8
836 | 697 | 527.2 | 388.3 | 440.4 | 381.9 | 241.1 | 216.3 | 203.3 | 193.4 | 223.2 | 195.3
837 | 698 | 527.2 | 388.6 | 440.6 | 382.2 | 241.4 | 216.7 | 203.6 | 193.8 | 223.6 | 195.8
838 | 699 | 527.3 | 388.8 | 440.8 | 382.4 | 241.7 | 217.1 | 203.9 | 194.1 | 223.9 | 196.3
839 | 700 | 527.2 | 389.1 | 441 | 382.7 | 242 | 217.5 | 204.2 | 194.5 | 224.3 | 196.8
840 | 701 | 527.2 | 389.3 | 441.2 | 382.9 | 242.3 | 217.8 | 204.5 | 194.8 | 224.7 | 197.3
841 | 702 | 527.2 | 389.5 | 441.3 | 383.2 | 242.6 | 218.3 | 204.9 | 195.1 | 225.1 | 197.9
842 | 703 | 527.2 | 389.8 | 441.5 | 383.4 | 243 | 218.7 | 205.2 | 195.4 | 225.4 | 198.3
843 | 704 | 527.2 | 390 | 441.7 | 383.6 | 243.3 | 219.1 | 205.5 | 195.8 | 225.8 | 198.8
844 | 705 | 527.2 | 390.2 | 441.9 | 383.9 | 243.7 | 219.4 | 205.8 | 196.1 | 226.2 | 199.2
845 | 706 | 527.2 | 390.5 | 442 | 384.1 | 244 | 219.8 | 206.1 | 196.5 | 226.5 | 199.7
846 | 707 | 527.2 | 390.7 | 442.2 | 384.3 | 244.4 | 220.2 | 206.4 | 196.9 | 226.9 | 200.1
847 | 708 | 527.2 | 390.9 | 442.4 | 384.5 | 244.7 | 220.6 | 206.8 | 197.2 | 227.3 | 200.5
848 | 709 | 527.2 | 391.2 | 442.6 | 384.8 | 245.1 | 221 | 207.1 | 197.5 | 227.8 | 200.9
849 | 710 | 527.2 | 391.4 | 442.7 | 385 | 245.5 | 221.4 | 207.4 | 197.9 | 228.2 | 201.3
850 | 711 | 527.2 | 391.6 | 442.9 | 385.3 | 245.8 | 221.8 | 207.7 | 198.3 | 228.7 | 201.8
851 | 712 | 527.2 | 391.8 | 443.1 | 385.5 | 246.2 | 222.2 | 208 | 198.6 | 229.2 | 202.2
852 | 713 | 527.2 | 392 | 443.3 | 385.7 | 246.5 | 222.6 | 208.3 | 198.9 | 229.6 | 202.7
853 | 714 | 527.2 | 392.3 | 443.5 | 386 | 246.9 | 222.9 | 208.6 | 199.2 | 230.1 | 203.1
854 | 715 | 527.2 | 392.5 | 443.6 | 386.2 | 247.2 | 223.3 | 208.9 | 199.5 | 230.6 | 203.5
855 | 716 | 527.2 | 392.7 | 443.8 | 386.4 | 247.5 | 223.7 | 209.2 | 199.9 | 231 | 204
856 | 717 | 527.2 | 392.9 | 443.9 | 386.6 | 247.9 | 224.1 | 209.5 | 200.2 | 231.5 | 204.4
857 | 718 | 527.2 | 393.2 | 444.2 | 386.8 | 248.2 | 224.5 | 209.8 | 200.5 | 232 | 204.7
858 | 719 | 527.1 | 393.4 | 444.3 | 387 | 248.6 | 224.8 | 210.1 | 200.9 | 232.4 | 205.1
859 | 720 | 527.1 | 393.6 | 444.5 | 387.3 | 249 | 225.2 | 210.4 | 201.2 | 232.9 | 205.5
860 | 721 | 527 | 393.8 | 444.6 | 387.5 | 249.3 | 225.6 | 210.7 | 201.5 | 233.4 | 205.9
861 | 722 | 527 | 394 | 444.8 | 387.7 | 249.6 | 226 | 211 | 201.8 | 233.9 | 206.2
862 | 723 | 527 | 394.2 | 445 | 388 | 249.9 | 226.3 | 211.3 | 202.1 | 234.4 | 206.6
863 | 724 | 527 | 394.5 | 445.1 | 388.2 | 250.3 | 226.7 | 211.6 | 202.3 | 234.8 | 207
864 | 725 | 527 | 394.7 | 445.3 | 388.4 | 250.5 | 227.1 | 211.9 | 202.6 | 235.3 | 207.3
865 | 726 | 527 | 394.9 | 445.5 | 388.6 | 250.9 | 227.4 | 212.2 | 202.9 | 235.7 | 207.7
866 | 727 | 527 | 395.1 | 445.7 | 388.8 | 251.2 | 227.8 | 212.5 | 203.2 | 236.1 | 208.1
867 | 728 | 527 | 395.3 | 445.8 | 389 | 251.5 | 228.2 | 212.8 | 203.5 | 236.6 | 208.5
868 | 729 | 527 | 395.5 | 446 | 389.2 | 251.8 | 228.5 | 213.1 | 203.8 | 236.9 | 208.9
869 | 730 | 527 | 395.8 | 446.1 | 389.4 | 252.1 | 228.9 | 213.4 | 204.1 | 237.3 | 209.3
870 | 731 | 527 | 396 | 446.3 | 389.7 | 252.4 | 229.3 | 213.7 | 204.4 | 237.7 | 209.7
871 | 732 | 527 | 396.2 | 446.5 | 389.9 | 252.7 | 229.6 | 214 | 204.7 | 238 | 210.1
872 | 733 | 526.9 | 396.4 | 446.7 | 390.1 | 253 | 230 | 214.2 | 205.1 | 238.3 | 210.6
873 | 734 | 526.9 | 396.6 | 446.8 | 390.3 | 253.3 | 230.4 | 214.4 | 205.3 | 238.6 | 211
874 | 735 | 526.9 | 396.8 | 447 | 390.5 | 253.6 | 230.7 | 214.6 | 205.6 | 238.9 | 211.5
875 | 736 | 526.9 | 397 | 447.1 | 390.7 | 253.9 | 231.1 | 214.8 | 205.9 | 239.2 | 211.9
876 | 737 | 526.8 | 397.2 | 447.3 | 390.9 | 254.2 | 231.4 | 215.1 | 206.2 | 239.5 | 212.3
877 | 738 | 526.8 | 397.5 | 447.4 | 391.1 | 254.6 | 231.8 | 215.3 | 206.5 | 239.8 | 212.7
878 | 739 | 526.8 | 397.7 | 447.6 | 391.3 | 254.9 | 232.1 | 215.5 | 206.7 | 240.1 | 213.1
879 | 740 | 526.7 | 397.9 | 447.7 | 391.5 | 255.2 | 232.5 | 215.7 | 207 | 240.4 | 213.4
880 | 741 | 526.7 | 398.1 | 447.9 | 391.8 | 255.5 | 232.8 | 216 | 207.2 | 240.6 | 213.8
881 | 742 | 526.6 | 398.3 | 448.1 | 391.9 | 255.8 | 233.1 | 216.2 | 207.5 | 240.9 | 214.2
882 | 743 | 526.6 | 398.5 | 448.3 | 392.1 | 256.1 | 233.5 | 216.5 | 207.8 | 241.2 | 214.5
883 | 744 | 526.5 | 398.7 | 448.4 | 392.4 | 256.4 | 233.9 | 216.7 | 208 | 241.5 | 214.9
884 | 745 | 526.5 | 398.9 | 448.6 | 392.5 | 256.7 | 234.2 | 216.9 | 208.2 | 241.7 | 215.2
885 | 746 | 526.5 | 399.1 | 448.7 | 392.8 | 257.1 | 234.6 | 217.2 | 208.4 | 242 | 215.5
886 | 747 | 526.5 | 399.3 | 448.8 | 393 | 257.4 | 234.9 | 217.4 | 208.6 | 242.2 | 215.9
887 | 748 | 526.5 | 399.5 | 449 | 393.2 | 257.7 | 235.3 | 217.6 | 208.9 | 242.5 | 216.2
888 | 749 | 526.5 | 399.7 | 449.2 | 393.4 | 258 | 235.6 | 217.9 | 209.2 | 242.7 | 216.6
889 | 750 | 526.5 | 399.9 | 449.3 | 393.6 | 258.3 | 236 | 218.1 | 209.4 | 243 | 216.9
890 | 751 | 526.6 | 400.1 | 449.5 | 393.8 | 258.6 | 236.3 | 218.4 | 209.7 | 243.3 | 217.2
891 | 752 | 526.6 | 400.4 | 449.6 | 394 | 258.9 | 236.7 | 218.6 | 209.9 | 243.5 | 217.5
892 | 753 | 526.6 | 400.5 | 449.8 | 394.2 | 259.2 | 237 | 218.9 | 210.2 | 243.9 | 217.8
893 | 754 | 526.6 | 400.8 | 449.9 | 394.4 | 259.6 | 237.4 | 219.1 | 210.5 | 244.2 | 218.1
894 | 755 | 526.7 | 401 | 450.1 | 394.6 | 259.9 | 237.7 | 219.3 | 210.7 | 244.5 | 218.3
895 | 756 | 526.7 | 401.2 | 450.2 | 394.8 | 260.2 | 238 | 219.6 | 211 | 244.8 | 218.6
896 | 757 | 526.7 | 401.4 | 450.4 | 394.9 | 260.5 | 238.3 | 219.9 | 211.3 | 245.1 | 218.9
897 | 758 | 526.7 | 401.6 | 450.5 | 395.1 | 260.9 | 238.7 | 220.1 | 211.5 | 245.4 | 219.1
898 | 759 | 526.7 | 401.8 | 450.7 | 395.4 | 261.2 | 239 | 220.4 | 211.8 | 245.7 | 219.4
899 | 760 | 526.7 | 402 | 450.9 | 395.5 | 261.5 | 239.3 | 220.6 | 212.1 | 246 | 219.6
900 | 761 | 526.7 | 402.1 | 451 | 395.7 | 261.8 | 239.6 | 220.9 | 212.3 | 246.3 | 219.8
901 | 762 | 526.6 | 402.4 | 451.1 | 395.9 | 262.1 | 240 | 221.2 | 212.6 | 246.7 | 220.1
902 | 763 | 526.6 | 402.5 | 451.3 | 396.1 | 262.4 | 240.3 | 221.5 | 212.9 | 247 | 220.3
903 | 764 | 526.6 | 402.7 | 451.4 | 396.3 | 262.7 | 240.6 | 221.7 | 213.2 | 247.3 | 220.5
904 | 765 | 526.6 | 402.9 | 451.6 | 396.5 | 263 | 240.9 | 222 | 213.4 | 247.6 | 220.8
905 | 766 | 526.6 | 403.1 | 451.7 | 396.7 | 263.4 | 241.3 | 222.3 | 213.7 | 247.8 | 221
906 | 767 | 526.5 | 403.3 | 451.9 | 396.9 | 263.7 | 241.6 | 222.6 | 214 | 248.1 | 221.2
907 | 768 | 526.5 | 403.5 | 452 | 397.1 | 264 | 241.9 | 222.9 | 214.2 | 248.4 | 221.4
908 | 769 | 526.6 | 403.7 | 452.2 | 397.3 | 264.3 | 242.2 | 223.2 | 214.5 | 248.7 | 221.6
909 | 770 | 526.6 | 403.9 | 452.4 | 397.5 | 264.5 | 242.6 | 223.5 | 214.7 | 249 | 221.8
910 | 771 | 526.6 | 404.1 | 452.5 | 397.7 | 264.8 | 242.9 | 223.8 | 214.9 | 249.3 | 222
911 | 772 | 526.6 | 404.3 | 452.6 | 397.9 | 265.2 | 243.2 | 224.1 | 215.2 | 249.6 | 222.2
912 | 773 | 526.6 | 404.5 | 452.7 | 398.1 | 265.5 | 243.6 | 224.4 | 215.4 | 249.8 | 222.4
913 | 774 | 526.6 | 404.7 | 452.9 | 398.2 | 265.9 | 243.9 | 224.7 | 215.7 | 250.1 | 222.6
914 | 775 | 526.6 | 404.9 | 453 | 398.4 | 266.2 | 244.2 | 225 | 216 | 250.4 | 222.8
915 | 776 | 526.7 | 405.1 | 453.1 | 398.6 | 266.5 | 244.5 | 225.3 | 216.3 | 250.6 | 222.9
916 | 777 | 526.7 | 405.3 | 453.3 | 398.8 | 266.8 | 244.9 | 225.6 | 216.5 | 250.9 | 223.1
917 | 778 | 526.7 | 405.5 | 453.4 | 399 | 267.1 | 245.2 | 225.9 | 216.8 | 251.2 | 223.3
918 | 779 | 526.7 | 405.6 | 453.6 | 399.2 | 267.4 | 245.5 | 226.2 | 217 | 251.4 | 223.4
919 | 780 | 526.7 | 405.8 | 453.8 | 399.4 | 267.7 | 245.8 | 226.5 | 217.3 | 251.7 | 223.6
920 | 781 | 526.7 | 406 | 453.9 | 399.6 | 268.1 | 246.2 | 226.8 | 217.6 | 252 | 223.7
921 | 782 | 526.6 | 406.2 | 454.1 | 399.7 | 268.4 | 246.5 | 227.1 | 217.9 | 252.3 | 223.9
922 | 783 | 526.6 | 406.4 | 454.2 | 399.9 | 268.7 | 246.9 | 227.4 | 218.1 | 252.7 | 224.1
923 | 784 | 526.6 | 406.6 | 454.3 | 400.1 | 269.1 | 247.2 | 227.7 | 218.4 | 253 | 224.2
924 | 785 | 526.5 | 406.7 | 454.5 | 400.3 | 269.4 | 247.5 | 228 | 218.6 | 253.3 | 224.4
925 | 786 | 526.5 | 406.9 | 454.6 | 400.5 | 269.7 | 247.8 | 228.3 | 218.9 | 253.6 | 224.5
926 | 787 | 526.5 | 407.1 | 454.7 | 400.7 | 270 | 248.2 | 228.6 | 219.1 | 253.9 | 224.7
927 | 788 | 526.5 | 407.3 | 454.9 | 400.9 | 270.4 | 248.5 | 228.8 | 219.3 | 254.3 | 224.8
928 | 789 | 526.5 | 407.5 | 455 | 401 | 270.7 | 248.8 | 229.1 | 219.6 | 254.6 | 225
929 | 790 | 526.4 | 407.7 | 455.1 | 401.2 | 271 | 249.2 | 229.4 | 219.8 | 254.9 | 225.1
930 | 791 | 526.4 | 407.9 | 455.3 | 401.4 | 271.4 | 249.5 | 229.7 | 220.1 | 255.2 | 225.3
931 | 792 | 526.4 | 408.1 | 455.4 | 401.6 | 271.7 | 249.8 | 230 | 220.3 | 255.5 | 225.5
932 | 793 | 526.4 | 408.3 | 455.5 | 401.8 | 272 | 250.2 | 230.3 | 220.5 | 255.8 | 225.6
933 | 794 | 526.4 | 408.4 | 455.7 | 401.9 | 272.3 | 250.5 | 230.6 | 220.8 | 256.2 | 225.8
934 | 795 | 526.4 | 408.6 | 455.8 | 402.1 | 272.7 | 250.8 | 230.9 | 221.1 | 256.5 | 226.1
935 | 796 | 526.5 | 408.8 | 455.9 | 402.3 | 273 | 251.2 | 231.2 | 221.3 | 256.8 | 226.3
936 | 797 | 526.4 | 409 | 456.1 | 402.5 | 273.3 | 251.5 | 231.5 | 221.6 | 257.1 | 226.6
937 | 798 | 526.4 | 409.2 | 456.2 | 402.7 | 273.7 | 251.8 | 231.8 | 221.8 | 257.4 | 226.9
938 | 799 | 526.4 | 409.3 | 456.3 | 402.9 | 273.9 | 252.1 | 232.1 | 222.1 | 257.7 | 227.1
939 | 800 | 526.4 | 409.5 | 456.5 | 403 | 274.3 | 252.5 | 232.5 | 222.3 | 258.1 | 227.4
940 | 801 | 526.4 | 409.7 | 456.6 | 403.2 | 274.6 | 252.8 | 232.8 | 222.6 | 258.4 | 227.7
941 | 802 | 526.4 | 409.8 | 456.7 | 403.4 | 274.9 | 253.1 | 233.1 | 222.9 | 258.7 | 227.9
942 | 803 | 526.4 | 410 | 456.8 | 403.6 | 275.3 | 253.4 | 233.4 | 223.2 | 259 | 228.2
943 | 804 | 526.5 | 410.2 | 457 | 403.8 | 275.6 | 253.8 | 233.7 | 223.5 | 259.3 | 228.5
944 | 805 | 526.5 | 410.4 | 457.1 | 403.9 | 275.9 | 254.1 | 234 | 223.8 | 259.6 | 228.7
945 | 806 | 526.6 | 410.6 | 457.3 | 404.1 | 276.2 | 254.4 | 234.3 | 224 | 259.9 | 229
946 | 807 | 526.6 | 410.8 | 457.4 | 404.3 | 276.6 | 254.7 | 234.6 | 224.3 | 260.1 | 229.2
947 | 808 | 526.6 | 410.9 | 457.5 | 404.4 | 276.9 | 255.1 | 234.9 | 224.6 | 260.4 | 229.5
948 | 809 | 526.7 | 411.1 | 457.7 | 404.6 | 277.2 | 255.4 | 235.2 | 224.9 | 260.7 | 229.8
949 | 810 | 526.7 | 411.2 | 457.8 | 404.8 | 277.5 | 255.7 | 235.5 | 225.2 | 261 | 230
950 | 811 | 526.7 | 411.4 | 457.9 | 404.9 | 277.8 | 256 | 235.8 | 225.5 | 261.3 | 230.3
951 | 812 | 526.7 | 411.6 | 458 | 405.1 | 278.2 | 256.4 | 236.1 | 225.7 | 261.6 | 230.5
952 | 813 | 526.7 | 411.8 | 458.2 | 405.3 | 278.5 | 256.7 | 236.4 | 226 | 261.9 | 230.8
953 | 814 | 526.7 | 411.9 | 458.3 | 405.5 | 278.8 | 257.1 | 236.7 | 226.2 | 262.2 | 231
954 | 815 | 526.7 | 412.1 | 458.4 | 405.7 | 279.2 | 257.4 | 237 | 226.5 | 262.4 | 231.2
955 | 816 | 526.7 | 412.3 | 458.6 | 405.8 | 279.5 | 257.7 | 237.3 | 226.7 | 262.6 | 231.5
956 | 817 | 526.6 | 412.4 | 458.7 | 406 | 279.8 | 258.1 | 237.6 | 227 | 262.9 | 231.7
957 | 818 | 526.6 | 412.6 | 458.8 | 406.2 | 280.2 | 258.4 | 237.9 | 227.3 | 263.2 | 232
958 | 819 | 526.6 | 412.8 | 458.9 | 406.3 | 280.5 | 258.8 | 238.2 | 227.6 | 263.5 | 232.2
959 | 820 | 526.6 | 413 | 459 | 406.5 | 280.8 | 259.1 | 238.4 | 227.8 | 263.7 | 232.4
960 | 821 | 526.5 | 413.1 | 459.1 | 406.7 | 281.2 | 259.5 | 238.8 | 228.1 | 264 | 232.7
961 | 822 | 526.5 | 413.3 | 459.3 | 406.9 | 281.5 | 259.8 | 239.1 | 228.3 | 264.3 | 232.9
962 | 823 | 526.5 | 413.5 | 459.4 | 407.1 | 281.8 | 260.2 | 239.4 | 228.6 | 264.5 | 233.1
963 | 824 | 526.5 | 413.6 | 459.5 | 407.2 | 282.2 | 260.5 | 239.7 | 228.9 | 264.8 | 233.4
964 | 825 | 526.5 | 413.8 | 459.6 | 407.4 | 282.5 | 260.8 | 240 | 229.2 | 265.1 | 233.6
965 | 826 | 526.5 | 413.9 | 459.8 | 407.6 | 282.8 | 261.2 | 240.3 | 229.5 | 265.4 | 233.8
966 | 827 | 526.5 | 414.1 | 459.9 | 407.7 | 283.1 | 261.5 | 240.7 | 229.8 | 265.7 | 234.1
967 | 828 | 526.5 | 414.3 | 460 | 407.9 | 283.4 | 261.8 | 241 | 230 | 266 | 234.3
968 | 829 | 526.5 | 414.4 | 460.2 | 408 | 283.8 | 262.2 | 241.3 | 230.3 | 266.3 | 234.6
969 | 830 | 526.5 | 414.6 | 460.3 | 408.2 | 284.1 | 262.5 | 241.6 | 230.7 | 266.6 | 234.8
970 | 831 | 526.5 | 414.7 | 460.4 | 408.4 | 284.4 | 262.8 | 241.9 | 231 | 266.9 | 235
971 | 832 | 526.4 | 414.9 | 460.5 | 408.6 | 284.8 | 263.1 | 242.3 | 231.3 | 267.2 | 235.2
972 | 833 | 526.4 | 415.1 | 460.6 | 408.7 | 285.1 | 263.5 | 242.6 | 231.5 | 267.4 | 235.5
973 | 834 | 526.4 | 415.3 | 460.7 | 408.9 | 285.5 | 263.8 | 242.9 | 231.8 | 267.7 | 235.7
974 | 835 | 526.4 | 415.4 | 460.8 | 409.1 | 285.8 | 264.1 | 243.2 | 232.1 | 268 | 236
975 | 836 | 526.4 | 415.6 | 461 | 409.3 | 286.2 | 264.4 | 243.6 | 232.4 | 268.3 | 236.2
976 | 837 | 526.5 | 415.7 | 461.1 | 409.4 | 286.5 | 264.7 | 243.9 | 232.7 | 268.5 | 236.5
977 | 838 | 526.5 | 415.9 | 461.2 | 409.6 | 286.9 | 265 | 244.2 | 233 | 268.8 | 236.7
978 | 839 | 526.5 | 416 | 461.3 | 409.7 | 287.2 | 265.4 | 244.6 | 233.3 | 269 | 236.9
979 | 840 | 526.6 | 416.2 | 461.4 | 409.9 | 287.6 | 265.7 | 244.9 | 233.6 | 269.3 | 237.1
980 | 841 | 526.6 | 416.4 | 461.5 | 410 | 287.9 | 266 | 245.2 | 233.9 | 269.5 | 237.3
981 | 842 | 526.6 | 416.5 | 461.6 | 410.2 | 288.3 | 266.3 | 245.5 | 234.2 | 269.8 | 237.6
982 | 843 | 526.6 | 416.7 | 461.8 | 410.4 | 288.6 | 266.7 | 245.9 | 234.5 | 270 | 237.8
983 | 844 | 526.6 | 416.8 | 461.9 | 410.5 | 288.9 | 267 | 246.2 | 234.8 | 270.3 | 238
984 | 845 | 526.6 | 417 | 462 | 410.7 | 289.3 | 267.3 | 246.5 | 235.1 | 270.5 | 238.3
985 | 846 | 526.7 | 417.1 | 462.1 | 410.9 | 289.6 | 267.7 | 246.8 | 235.4 | 270.8 | 238.5
986 | 847 | 526.7 | 417.3 | 462.3 | 411 | 289.9 | 268 | 247.2 | 235.8 | 271 | 238.7
987 | 848 | 526.6 | 417.4 | 462.4 | 411.2 | 290.3 | 268.3 | 247.5 | 236 | 271.3 | 238.9
988 | 849 | 526.6 | 417.6 | 462.5 | 411.3 | 290.6 | 268.7 | 247.9 | 236.3 | 271.6 | 239.2
989 | 850 | 526.6 | 417.7 | 462.6 | 411.5 | 291 | 269 | 248.2 | 236.6 | 271.8 | 239.4
990 | 851 | 526.7 | 417.9 | 462.8 | 411.6 | 291.3 | 269.3 | 248.5 | 236.9 | 272.1 | 239.6
991 | 852 | 526.7 | 418 | 462.9 | 411.8 | 291.6 | 269.6 | 248.9 | 237.2 | 272.4 | 239.9
992 | 853 | 526.7 | 418.2 | 462.9 | 412 | 292 | 269.9 | 249.2 | 237.5 | 272.7 | 240.1
993 | 854 | 526.7 | 418.3 | 463.1 | 412.1 | 292.3 | 270.3 | 249.6 | 237.7 | 273 | 240.3
994 | 855 | 526.7 | 418.5 | 463.2 | 412.3 | 292.6 | 270.6 | 249.9 | 238 | 273.2 | 240.6
995 | 856 | 526.7 | 418.6 | 463.3 | 412.4 | 293 | 270.9 | 250.3 | 238.3 | 273.5 | 240.8
996 | 857 | 526.7 | 418.8 | 463.3 | 412.6 | 293.3 | 271.2 | 250.6 | 238.6 | 273.9 | 241.1
997 | 858 | 526.7 | 419 | 463.5 | 412.8 | 293.7 | 271.5 | 251 | 238.9 | 274.2 | 241.3
998 | 859 | 526.7 | 419.1 | 463.5 | 412.9 | 294.1 | 271.9 | 251.4 | 239.1 | 274.5 | 241.6
999 | 860 | 526.7 | 419.3 | 463.6 | 413.1 | 294.4 | 272.3 | 251.8 | 239.5 | 274.8 | 241.8
1000 | 861 | 526.7 | 419.4 | 463.7 | 413.2 | 294.7 | 272.6 | 252.1 | 239.8 | 275.1 | 242.1
1001 | 862 | 526.6 | 419.6 | 463.8 | 413.4 | 295.1 | 272.9 | 252.5 | 240 | 275.4 | 242.3
1002 | 863 | 526.6 | 419.7 | 463.9 | 413.6 | 295.5 | 273.3 | 252.8 | 240.3 | 275.7 | 242.6
1003 | 864 | 526.6 | 419.9 | 464 | 413.7 | 295.8 | 273.6 | 253.2 | 240.6 | 276.1 | 242.8
1004 | 865 | 526.6 | 420 | 464.2 | 413.9 | 296.2 | 273.9 | 253.5 | 240.9 | 276.4 | 243.1
1005 | 866 | 526.6 | 420.2 | 464.3 | 414 | 296.5 | 274.2 | 253.8 | 241.2 | 276.7 | 243.3
1006 | 867 | 526.6 | 420.3 | 464.4 | 414.2 | 296.9 | 274.6 | 254.1 | 241.5 | 277 | 243.6
1007 | 868 | 526.6 | 420.5 | 464.4 | 414.3 | 297.3 | 274.9 | 254.4 | 241.8 | 277.3 | 243.8
1008 | 869 | 526.7 | 420.6 | 464.6 | 414.5 | 297.6 | 275.2 | 254.7 | 242 | 277.6 | 244
1009 | 870 | 526.7 | 420.8 | 464.7 | 414.6 | 298 | 275.6 | 255 | 242.4 | 277.9 | 244.3
1010 | 871 | 526.7 | 420.9 | 464.8 | 414.8 | 298.3 | 275.9 | 255.3 | 242.6 | 278.3 | 244.5
1011 | 872 | 526.7 | 421.1 | 464.9 | 414.9 | 298.6 | 276.2 | 255.6 | 242.9 | 278.6 | 244.8
1012 | 873 | 526.7 | 421.2 | 465 | 415.1 | 299 | 276.6 | 255.9 | 243.2 | 278.9 | 245
1013 | 874 | 526.7 | 421.4 | 465.1 | 415.3 | 299.4 | 276.9 | 256.2 | 243.5 | 279.2 | 245.3
1014 | 875 | 526.7 | 421.5 | 465.1 | 415.4 | 299.7 | 277.3 | 256.5 | 243.8 | 279.5 | 245.5
1015 | 876 | 526.7 | 421.6 | 465.3 | 415.6 | 300.1 | 277.6 | 256.8 | 244.1 | 279.8 | 245.8
1016 | 877 | 526.7 | 421.8 | 465.3 | 415.7 | 300.4 | 277.9 | 257.1 | 244.3 | 280.1 | 246
1017 | 878 | 526.7 | 421.9 | 465.5 | 415.9 | 300.8 | 278.3 | 257.5 | 244.6 | 280.4 | 246.3
1018 | 879 | 526.7 | 422 | 465.6 | 416 | 301.1 | 278.6 | 257.8 | 244.9 | 280.7 | 246.5
1019 | 880 | 526.7 | 422.2 | 465.7 | 416.2 | 301.5 | 278.9 | 258.1 | 245.2 | 281 | 246.8
1020 | 881 | 526.7 | 422.3 | 465.8 | 416.3 | 301.8 | 279.2 | 258.5 | 245.5 | 281.3 | 247
1021 | 882 | 526.7 | 422.5 | 465.9 | 416.5 | 302.2 | 279.6 | 258.8 | 245.9 | 281.6 | 247.3
1022 | 883 | 526.7 | 422.6 | 465.9 | 416.6 | 302.5 | 279.9 | 259.1 | 246.2 | 281.9 | 247.5
1023 | 884 | 526.7 | 422.8 | 466 | 416.7 | 302.9 | 280.3 | 259.4 | 246.5 | 282.2 | 247.7
1024 | 885 | 526.6 | 422.9 | 466.1 | 416.9 | 303.3 | 280.6 | 259.8 | 246.8 | 282.5 | 248
1025 | 886 | 526.6 | 423 | 466.2 | 417.1 | 303.6 | 280.9 | 260.1 | 247.1 | 282.8 | 248.2
1026 | 887 | 526.6 | 423.2 | 466.3 | 417.2 | 304 | 281.3 | 260.4 | 247.4 | 283.2 | 248.5
1027 | 888 | 526.6 | 423.3 | 466.4 | 417.4 | 304.3 | 281.6 | 260.8 | 247.7 | 283.5 | 248.7
1028 | 889 | 526.6 | 423.4 | 466.5 | 417.5 | 304.7 | 282 | 261.1 | 248 | 283.8 | 249
1029 | 890 | 526.7 | 423.6 | 466.7 | 417.6 | 305 | 282.3 | 261.5 | 248.3 | 284.2 | 249.2
1030 | 891 | 526.7 | 423.7 | 466.8 | 417.8 | 305.3 | 282.7 | 261.8 | 248.6 | 284.5 | 249.5
1031 | 892 | 526.7 | 423.8 | 466.8 | 417.9 | 305.7 | 283 | 262.1 | 249 | 284.8 | 249.7
1032 | 893 | 526.7 | 423.9 | 467 | 418.1 | 306 | 283.3 | 262.4 | 249.3 | 285.1 | 250
1033 | 894 | 526.7 | 424.1 | 467.1 | 418.2 | 306.3 | 283.6 | 262.7 | 249.6 | 285.5 | 250.2
1034 | 895 | 526.7 | 424.2 | 467.2 | 418.4 | 306.7 | 284 | 263 | 249.9 | 285.8 | 250.5
1035 | 896 | 526.7 | 424.4 | 467.2 | 418.5 | 307.1 | 284.3 | 263.4 | 250.2 | 286.1 | 250.8
1036 | 897 | 526.7 | 424.5 | 467.3 | 418.7 | 307.4 | 284.6 | 263.7 | 250.5 | 286.4 | 251
1037 | 898 | 526.7 | 424.7 | 467.4 | 418.8 | 307.8 | 285 | 264 | 250.8 | 286.7 | 251.3
1038 | 899 | 526.6 | 424.8 | 467.5 | 418.9 | 308.1 | 285.4 | 264.4 | 251.1 | 287 | 251.6
1039 | 900 | 526.6 | 424.9 | 467.6 | 419.1 | 308.5 | 285.7 | 264.7 | 251.4 | 287.3 | 251.8
1040 | 901 | 526.6 | 425 | 467.7 | 419.2 | 308.8 | 286 | 265 | 251.8 | 287.6 | 252.1
1041 | 902 | 526.6 | 425.2 | 467.8 | 419.3 | 309.2 | 286.3 | 265.4 | 252.1 | 287.9 | 252.3
1042 | 903 | 526.7 | 425.3 | 467.9 | 419.5 | 309.5 | 286.7 | 265.7 | 252.3 | 288.2 | 252.6
1043 | 904 | 526.7 | 425.5 | 467.9 | 419.7 | 309.9 | 287.1 | 266.1 | 252.6 | 288.5 | 252.8
1044 | 905 | 526.7 | 425.6 | 468.1 | 419.8 | 310.2 | 287.4 | 266.4 | 252.9 | 288.9 | 253.1
1045 | 906 | 526.7 | 425.7 | 468.2 | 419.9 | 310.6 | 287.8 | 266.7 | 253.2 | 289.2 | 253.3
1046 | 907 | 526.7 | 425.8 | 468.3 | 420.1 | 311 | 288.1 | 267.1 | 253.5 | 289.5 | 253.6
1047 | 908 | 526.7 | 425.9 | 468.4 | 420.2 | 311.3 | 288.4 | 267.4 | 253.8 | 289.8 | 253.9
1048 | 909 | 526.7 | 426.1 | 468.5 | 420.3 | 311.7 | 288.7 | 267.8 | 254.2 | 290.1 | 254.1
1049 | 910 | 526.7 | 426.2 | 468.5 | 420.5 | 312 | 289.1 | 268.1 | 254.5 | 290.4 | 254.4
1050 | 911 | 526.8 | 426.3 | 468.6 | 420.6 | 312.3 | 289.4 | 268.4 | 254.9 | 290.7 | 254.7
1051 | 912 | 526.8 | 426.5 | 468.8 | 420.8 | 312.7 | 289.8 | 268.7 | 255.2 | 291 | 254.9
1052 | 913 | 526.8 | 426.6 | 468.8 | 420.9 | 313.1 | 290.1 | 269 | 255.4 | 291.3 | 255.2
1053 | 914 | 526.8 | 426.7 | 468.9 | 421 | 313.4 | 290.4 | 269.3 | 255.8 | 291.6 | 255.4
1054 | 915 | 526.8 | 426.8 | 469 | 421.1 | 313.7 | 290.8 | 269.7 | 256 | 291.9 | 255.7
1055 | 916 | 526.7 | 427 | 469.1 | 421.3 | 314.1 | 291.1 | 269.9 | 256.3 | 292.2 | 255.9
1056 | 917 | 526.7 | 427.1 | 469.2 | 421.4 | 314.4 | 291.4 | 270.3 | 256.6 | 292.5 | 256.2
1057 | 918 | 526.7 | 427.2 | 469.3 | 421.5 | 314.8 | 291.8 | 270.6 | 257 | 292.8 | 256.4
1058 | 919 | 526.7 | 427.3 | 469.4 | 421.7 | 315.1 | 292.1 | 270.9 | 257.3 | 293.1 | 256.7
1059 | 920 | 526.6 | 427.5 | 469.5 | 421.8 | 315.5 | 292.5 | 271.2 | 257.6 | 293.5 | 256.9
1060 | 921 | 526.6 | 427.6 | 469.5 | 421.9 | 315.9 | 292.8 | 271.6 | 257.9 | 293.8 | 257.2
1061 | 922 | 526.6 | 427.7 | 469.6 | 422.1 | 316.3 | 293.1 | 271.9 | 258.1 | 294.1 | 257.4
1062 | 923 | 526.5 | 427.8 | 469.7 | 422.2 | 316.6 | 293.5 | 272.2 | 258.5 | 294.4 | 257.7
1063 | 924 | 526.5 | 428 | 469.8 | 422.3 | 317 | 293.8 | 272.5 | 258.8 | 294.8 | 258
1064 | 925 | 526.5 | 428.1 | 469.9 | 422.4 | 317.3 | 294.2 | 272.9 | 259.1 | 295.1 | 258.2
1065 | 926 | 526.4 | 428.2 | 470 | 422.6 | 317.7 | 294.5 | 273.2 | 259.4 | 295.4 | 258.5
1066 | 927 | 526.4 | 428.4 | 470.1 | 422.7 | 318.1 | 294.8 | 273.5 | 259.7 | 295.7 | 258.7
1067 | 928 | 526.4 | 428.5 | 470.2 | 422.8 | 318.4 | 295.2 | 273.9 | 259.9 | 296 | 258.9
1068 | 929 | 526.5 | 428.6 | 470.2 | 423 | 318.8 | 295.5 | 274.2 | 260.2 | 296.4 | 259.2
1069 | 930 | 526.5 | 428.7 | 470.3 | 423.1 | 319.2 | 295.8 | 274.5 | 260.5 | 296.7 | 259.4
1070 | 931 | 526.5 | 428.8 | 470.5 | 423.2 | 319.5 | 296.1 | 274.9 | 260.7 | 297 | 259.7
1071 | 932 | 526.6 | 429 | 470.5 | 423.3 | 319.9 | 296.5 | 275.2 | 261 | 297.3 | 259.9
1072 | 933 | 526.6 | 429.1 | 470.6 | 423.5 | 320.3 | 296.9 | 275.5 | 261.3 | 297.7 | 260.2
1073 | 934 | 526.6 | 429.2 | 470.7 | 423.6 | 320.7 | 297.2 | 275.9 | 261.6 | 298 | 260.4
1074 | 935 | 526.6 | 429.3 | 470.8 | 423.7 | 321.1 | 297.5 | 276.2 | 261.9 | 298.3 | 260.7
1075 | 936 | 526.6 | 429.4 | 470.9 | 423.8 | 321.4 | 297.9 | 276.5 | 262.2 | 298.6 | 260.9
1076 | 937 | 526.6 | 429.6 | 471 | 424 | 321.8 | 298.2 | 276.9 | 262.5 | 299 | 261.2
1077 | 938 | 526.6 | 429.7 | 471.1 | 424.1 | 322.2 | 298.5 | 277.3 | 262.8 | 299.3 | 261.4
1078 | 939 | 526.6 | 429.8 | 471.2 | 424.2 | 322.5 | 298.9 | 277.6 | 263 | 299.6 | 261.7
1079 | 940 | 526.6 | 429.9 | 471.2 | 424.4 | 322.9 | 299.2 | 278 | 263.3 | 299.9 | 261.9
1080 | 941 | 526.6 | 430 | 471.4 | 424.5 | 323.3 | 299.5 | 278.4 | 263.6 | 300.2 | 262.2
1081 | 942 | 526.6 | 430.2 | 471.4 | 424.6 | 323.6 | 299.8 | 278.7 | 263.9 | 300.6 | 262.4
1082 | 943 | 526.6 | 430.3 | 471.5 | 424.7 | 323.9 | 300.2 | 279.1 | 264.2 | 300.9 | 262.7
1083 | 944 | 526.6 | 430.4 | 471.6 | 424.8 | 324.3 | 300.5 | 279.5 | 264.5 | 301.2 | 262.9
1084 | 945 | 526.6 | 430.5 | 471.6 | 425 | 324.7 | 300.8 | 279.8 | 264.9 | 301.5 | 263.2
1085 | 946 | 526.6 | 430.6 | 471.7 | 425.1 | 325 | 301.1 | 280.2 | 265.2 | 301.8 | 263.4
1086 | 947 | 526.6 | 430.8 | 471.8 | 425.2 | 325.4 | 301.4 | 280.6 | 265.5 | 302.2 | 263.7
1087 | 948 | 526.6 | 430.9 | 471.9 | 425.3 | 325.7 | 301.8 | 281 | 265.8 | 302.5 | 263.9
1088 | 949 | 526.6 | 431 | 472 | 425.4 | 326.1 | 302.1 | 281.4 | 266.1 | 302.8 | 264.1
1089 | 950 | 526.6 | 431.1 | 472.1 | 425.5 | 326.4 | 302.4 | 281.8 | 266.4 | 303 | 264.4
1090 | 951 | 526.5 | 431.2 | 472.2 | 425.6 | 326.8 | 302.7 | 282.2 | 266.7 | 303.3 | 264.6
1091 | 952 | 526.5 | 431.3 | 472.2 | 425.8 | 327.1 | 303.1 | 282.6 | 267 | 303.6 | 264.8
1092 | 953 | 526.5 | 431.4 | 472.3 | 425.9 | 327.5 | 303.4 | 283 | 267.3 | 303.9 | 265.1
1093 | 954 | 526.5 | 431.5 | 472.5 | 426 | 327.8 | 303.7 | 283.3 | 267.6 | 304.1 | 265.3
1094 | 955 | 526.5 | 431.6 | 472.6 | 426.1 | 328.1 | 304 | 283.7 | 267.9 | 304.4 | 265.6
1095 | 956 | 526.4 | 431.7 | 472.7 | 426.2 | 328.4 | 304.3 | 284.1 | 268.3 | 304.6 | 265.8
1096 | 957 | 526.4 | 431.8 | 472.8 | 426.3 | 328.7 | 304.6 | 284.5 | 268.6 | 304.7 | 266
1097 | 958 | 526.4 | 431.9 | 472.8 | 426.5 | 329.1 | 305 | 284.9 | 268.9 | 304.8 | 266.3
1098 | 959 | 526.4 | 432 | 472.9 | 426.6 | 329.4 | 305.3 | 285.3 | 269.2 | 304.9 | 266.5
1099 | 960 | 526.3 | 432.2 | 473 | 426.7 | 329.8 | 305.6 | 285.8 | 269.4 | 305.1 | 266.7
1100 | 961 | 526.3 | 432.3 | 473.1 | 426.8 | 330.1 | 305.9 | 286.2 | 269.7 | 305.3 | 267
1101 | 962 | 526.3 | 432.4 | 473.2 | 426.9 | 330.5 | 306.2 | 286.5 | 270 | 305.5 | 267.2
1102 | 963 | 526.3 | 432.5 | 473.2 | 427 | 330.8 | 306.5 | 286.9 | 270.3 | 305.8 | 267.4
1103 | 964 | 526.3 | 432.6 | 473.3 | 427.1 | 331.2 | 306.9 | 287.3 | 270.6 | 306.1 | 267.7
1104 | 965 | 526.3 | 432.7 | 473.4 | 427.2 | 331.5 | 307.2 | 287.7 | 270.8 | 306.4 | 267.8
1105 | 966 | 526.3 | 432.8 | 473.5 | 427.4 | 331.8 | 307.5 | 288.1 | 271.1 | 306.8 | 268.1
1106 | 967 | 526.3 | 432.9 | 473.6 | 427.5 | 332.1 | 307.8 | 288.5 | 271.4 | 307.1 | 268.3
1107 | 968 | 526.3 | 433 | 473.7 | 427.6 | 332.5 | 308.1 | 288.9 | 271.7 | 307.5 | 268.5
1108 | 969 | 526.3 | 433.1 | 473.8 | 427.7 | 332.8 | 308.5 | 289.3 | 272.1 | 307.8 | 268.7
1109 | 970 | 526.2 | 433.2 | 473.9 | 427.8 | 333.1 | 308.8 | 289.7 | 272.4 | 308.2 | 268.9
1110 | 971 | 526.2 | 433.3 | 473.9 | 427.9 | 333.5 | 309.1 | 290.1 | 272.8 | 308.5 | 269.1
1111 | 972 | 526.2 | 433.4 | 474 | 428 | 333.8 | 309.4 | 290.5 | 273.1 | 308.8 | 269.4
1112 | 973 | 526.2 | 433.5 | 474.1 | 428.1 | 334.1 | 309.7 | 290.9 | 273.5 | 309.1 | 269.6
1113 | 974 | 526.2 | 433.6 | 474.2 | 428.2 | 334.4 | 310 | 291.2 | 273.7 | 309.4 | 269.8
1114 | 975 | 526.1 | 433.7 | 474.2 | 428.4 | 334.8 | 310.3 | 291.6 | 274 | 309.7 | 270.1
1115 | 976 | 526.1 | 433.9 | 474.3 | 428.5 | 335.2 | 310.6 | 292 | 274.3 | 310 | 270.3
1116 | 977 | 526 | 434 | 474.4 | 428.6 | 335.5 | 310.9 | 292.4 | 274.7 | 310.3 | 270.6
1117 | 978 | 526 | 434.1 | 474.4 | 428.7 | 335.8 | 311.3 | 292.8 | 275.1 | 310.5 | 270.8
1118 | 979 | 526 | 434.2 | 474.5 | 428.8 | 336.1 | 311.6 | 293.2 | 275.3 | 310.8 | 271.1
1119 | 980 | 525.9 | 434.3 | 474.6 | 428.9 | 336.5 | 311.9 | 293.5 | 275.6 | 311.1 | 271.3
1120 | 981 | 525.9 | 434.4 | 474.7 | 429.1 | 336.8 | 312.2 | 293.9 | 275.9 | 311.4 | 271.5
1121 | 982 | 525.9 | 434.5 | 474.8 | 429.1 | 337.1 | 312.5 | 294.4 | 276.3 | 311.6 | 271.8
1122 | 983 | 525.9 | 434.6 | 474.8 | 429.3 | 337.4 | 312.8 | 294.8 | 276.5 | 311.9 | 272
1123 | 984 | 525.8 | 434.7 | 474.9 | 429.4 | 337.7 | 313.1 | 295.2 | 276.9 | 312.2 | 272.2
1124 | 985 | 525.8 | 434.8 | 475 | 429.5 | 338.1 | 313.4 | 295.6 | 277.2 | 312.4 | 272.5
1125 | 986 | 525.8 | 434.9 | 475 | 429.6 | 338.4 | 313.7 | 295.9 | 277.5 | 312.7 | 272.7
1126 | 987 | 525.8 | 435 | 475.1 | 429.7 | 338.7 | 314.1 | 296.3 | 277.8 | 313.1 | 272.9
1127 | 988 | 525.8 | 435.1 | 475.2 | 429.8 | 339 | 314.4 | 296.7 | 278.1 | 313.4 | 273.1
1128 | 989 | 525.8 | 435.3 | 475.2 | 429.9 | 339.3 | 314.7 | 297 | 278.5 | 313.7 | 273.4
1129 | 990 | 525.8 | 435.3 | 475.3 | 430 | 339.6 | 315 | 297.4 | 278.8 | 314 | 273.6
1130 | 991 | 525.8 | 435.4 | 475.4 | 430.1 | 339.9 | 315.3 | 297.8 | 279.2 | 314.4 | 273.8
1131 | 992 | 525.8 | 435.6 | 475.4 | 430.2 | 340.3 | 315.6 | 298.1 | 279.5 | 314.7 | 274
1132 | 993 | 525.8 | 435.7 | 475.5 | 430.3 | 340.6 | 315.9 | 298.5 | 279.8 | 315 | 274.3
1133 | 994 | 525.8 | 435.8 | 475.5 | 430.4 | 340.9 | 316.2 | 298.9 | 280.2 | 315.3 | 274.4
1134 | 995 | 525.8 | 435.9 | 475.6 | 430.5 | 341.2 | 316.5 | 299.2 | 280.5 | 315.6 | 274.7
1135 | 996 | 525.8 | 436 | 475.7 | 430.7 | 341.5 | 316.8 | 299.6 | 280.9 | 315.9 | 275
1136 | 997 | 525.8 | 436.1 | 475.7 | 430.8 | 341.8 | 317.1 | 300 | 281.2 | 316.2 | 275.2
1137 | 998 | 525.8 | 436.2 | 475.8 | 430.9 | 342.1 | 317.4 | 300.4 | 281.5 | 316.5 | 275.5
1138 | 999 | 525.8 | 436.3 | 475.9 | 431 | 342.4 | 317.7 | 300.7 | 281.9 | 316.8 | 275.7
1139 | 1000 | 525.8 | 436.4 | 475.9 | 431.1 | 342.8 | 318 | 301.1 | 282.2 | 317.1 | 275.9
1140 | 1001 | 525.8 | 436.5 | 476 | 431.2 | 343.1 | 318.3 | 301.5 | 282.6 | 317.3 | 276.2
1141 | 1002 | 525.9 | 436.6 | 476 | 431.3 | 343.4 | 318.7 | 301.8 | 282.9 | 317.6 | 276.4
1142 | 1003 | 525.9 | 436.7 | 476.1 | 431.4 | 343.7 | 319 | 302.2 | 283.3 | 317.9 | 276.7
1143 | 1004 | 525.9 | 436.8 | 476.2 | 431.5 | 344 | 319.3 | 302.6 | 283.6 | 318.1 | 276.9
1144 | 1005 | 525.9 | 436.9 | 476.3 | 431.6 | 344.3 | 319.6 | 303 | 284 | 318.3 | 277.2
1145 | 1006 | 525.9 | 437 | 476.3 | 431.7 | 344.6 | 319.9 | 303.3 | 284.3 | 318.6 | 277.4
1146 | 1007 | 525.9 | 437.1 | 476.4 | 431.8 | 344.9 | 320.2 | 303.7 | 284.6 | 318.9 | 277.6
1147 | 1008 | 525.9 | 437.2 | 476.5 | 431.9 | 345.2 | 320.5 | 304.1 | 284.9 | 319.2 | 277.8
1148 | 1009 | 525.9 | 437.3 | 476.5 | 432 | 345.5 | 320.8 | 304.5 | 285.3 | 319.5 | 278.1
1149 | 1010 | 525.9 | 437.4 | 476.6 | 432.2 | 345.9 | 321.1 | 304.9 | 285.7 | 319.7 | 278.3
1150 | 1011 | 525.9 | 437.5 | 476.6 | 432.3 | 346.2 | 321.3 | 305.2 | 286 | 320 | 278.6
1151 | 1012 | 526 | 437.6 | 476.7 | 432.3 | 346.5 | 321.7 | 305.6 | 286.4 | 320.3 | 278.8
1152 | 1013 | 526 | 437.7 | 476.8 | 432.4 | 346.8 | 322 | 305.9 | 286.7 | 320.5 | 279.1
1153 | 1014 | 526 | 437.8 | 476.8 | 432.6 | 347.1 | 322.3 | 306.3 | 287.1 | 320.8 | 279.3
1154 | 1015 | 526 | 437.9 | 476.9 | 432.7 | 347.4 | 322.6 | 306.6 | 287.5 | 321 | 279.6
1155 | 1016 | 526 | 438 | 477 | 432.8 | 347.7 | 322.9 | 307 | 287.9 | 321.3 | 279.8
1156 | 1017 | 526 | 438.1 | 477.1 | 432.8 | 348 | 323.2 | 307.4 | 288.2 | 321.6 | 280
1157 | 1018 | 526 | 438.2 | 477.2 | 433 | 348.3 | 323.5 | 307.8 | 288.5 | 321.8 | 280.3
1158 | 1019 | 526 | 438.3 | 477.2 | 433.1 | 348.6 | 323.7 | 308.2 | 288.8 | 322.1 | 280.5
1159 | 1020 | 526 | 438.4 | 477.3 | 433.2 | 348.9 | 324.1 | 308.6 | 289.1 | 322.3 | 280.8
1160 | 1021 | 526 | 438.5 | 477.3 | 433.3 | 349.2 | 324.3 | 308.9 | 289.4 | 322.5 | 281
1161 | 1022 | 526 | 438.6 | 477.4 | 433.4 | 349.5 | 324.6 | 309.3 | 289.7 | 322.7 | 281.2
1162 | 1023 | 526 | 438.7 | 477.5 | 433.5 | 349.7 | 324.9 | 309.7 | 290 | 323 | 281.5
1163 | 1024 | 526 | 438.8 | 477.5 | 433.6 | 350 | 325.2 | 310.1 | 290.3 | 323.2 | 281.7
1164 | 1025 | 526 | 438.9 | 477.6 | 433.7 | 350.3 | 325.5 | 310.4 | 290.7 | 323.4 | 281.9
1165 | 1026 | 526.1 | 439 | 477.7 | 433.8 | 350.6 | 325.8 | 310.8 | 291 | 323.6 | 282.2
1166 | 1027 | 526.1 | 439 | 477.8 | 433.9 | 350.9 | 326.1 | 311.2 | 291.3 | 323.7 | 282.4
1167 | 1028 | 526.1 | 439.2 | 477.8 | 434 | 351.2 | 326.4 | 311.5 | 291.7 | 323.9 | 282.7
1168 | 1029 | 526.1 | 439.2 | 477.9 | 434.1 | 351.5 | 326.7 | 311.9 | 292 | 324 | 282.9
1169 | 1030 | 526.1 | 439.3 | 477.9 | 434.2 | 351.8 | 327 | 312.3 | 292.3 | 324.2 | 283.2
1170 | 1031 | 526.2 | 439.4 | 478 | 434.3 | 352.1 | 327.3 | 312.7 | 292.6 | 324.3 | 283.4
1171 | 1032 | 526.2 | 439.5 | 478.1 | 434.4 | 352.4 | 327.6 | 313.1 | 293 | 324.4 | 283.7
1172 | 1033 | 526.2 | 439.6 | 478.1 | 434.5 | 352.6 | 327.9 | 313.5 | 293.2 | 324.5 | 283.9
1173 | 1034 | 526.2 | 439.7 | 478.2 | 434.6 | 352.9 | 328.2 | 313.8 | 293.6 | 324.6 | 284.1
1174 | 1035 | 526.2 | 439.8 | 478.3 | 434.7 | 353.2 | 328.5 | 314.1 | 293.9 | 324.6 | 284.3
1175 | 1036 | 526.3 | 439.9 | 478.3 | 434.8 | 353.5 | 328.8 | 314.3 | 294.2 | 324.8 | 284.6
1176 | 1037 | 526.3 | 440 | 478.4 | 434.9 | 353.8 | 329 | 314.7 | 294.6 | 324.9 | 284.8
1177 | 1038 | 526.3 | 440.1 | 478.4 | 435 | 354.1 | 329.4 | 315 | 294.9 | 325.2 | 285.1
1178 | 1039 | 526.3 | 440.2 | 478.5 | 435 | 354.3 | 329.6 | 315.4 | 295.3 | 325.4 | 285.3
1179 | 1040 | 526.3 | 440.3 | 478.6 | 435.1 | 354.6 | 329.9 | 315.8 | 295.6 | 325.6 | 285.6
1180 | 1041 | 526.3 | 440.4 | 478.6 | 435.2 | 354.9 | 330.2 | 316.2 | 296 | 325.8 | 285.8
1181 | 1042 | 526.3 | 440.5 | 478.7 | 435.3 | 355.2 | 330.5 | 316.6 | 296.3 | 326 | 286.1
1182 | 1043 | 526.3 | 440.6 | 478.7 | 435.4 | 355.5 | 330.8 | 317 | 296.6 | 326.1 | 286.3
1183 | 1044 | 526.3 | 440.6 | 478.8 | 435.5 | 355.8 | 331.1 | 317.3 | 297 | 326.2 | 286.5
1184 | 1045 | 526.3 | 440.8 | 478.8 | 435.6 | 356.1 | 331.4 | 317.6 | 297.4 | 326.3 | 286.7
1185 | 1046 | 526.3 | 440.8 | 478.9 | 435.7 | 356.4 | 331.7 | 318 | 297.7 | 326.4 | 286.9
1186 | 1047 | 526.3 | 440.9 | 478.9 | 435.8 | 356.6 | 332 | 318.4 | 298.1 | 326.5 | 287.2
1187 | 1048 | 526.2 | 441 | 479 | 435.9 | 356.9 | 332.3 | 318.8 | 298.4 | 326.7 | 287.4
1188 | 1049 | 526.2 | 441.1 | 479 | 436 | 357.2 | 332.6 | 319.1 | 298.8 | 326.8 | 287.7
1189 | 1050 | 526.2 | 441.2 | 479.1 | 436.1 | 357.5 | 332.9 | 319.4 | 299.1 | 326.9 | 287.9
1190 | 1051 | 526.2 | 441.3 | 479.1 | 436.2 | 357.8 | 333.2 | 319.6 | 299.4 | 327 | 288.1
1191 | 1052 | 526.3 | 441.4 | 479.2 | 436.3 | 358.1 | 333.5 | 320 | 299.8 | 327.1 | 288.4
1192 | 1053 | 526.3 | 441.5 | 479.3 | 436.4 | 358.4 | 333.7 | 320.4 | 300.2 | 327.2 | 288.6
1193 | 1054 | 526.4 | 441.5 | 479.4 | 436.4 | 358.6 | 334 | 320.8 | 300.6 | 327.2 | 288.9
1194 | 1055 | 526.4 | 441.6 | 479.5 | 436.5 | 358.8 | 334.3 | 321 | 300.9 | 327.3 | 289.1
1195 | 1056 | 526.4 | 441.7 | 479.5 | 436.6 | 359.1 | 334.6 | 321.4 | 301.2 | 327.4 | 289.4
1196 | 1057 | 526.4 | 441.8 | 479.6 | 436.7 | 359.4 | 334.8 | 321.8 | 301.5 | 327.5 | 289.6
1197 | 1058 | 526.4 | 441.9 | 479.6 | 436.8 | 359.7 | 335.1 | 322.1 | 301.8 | 327.6 | 289.9
1198 | 1059 | 526.4 | 442 | 479.6 | 436.9 | 360 | 335.4 | 322.5 | 302.2 | 327.7 | 290.2
1199 | 1060 | 526.4 | 442.1 | 479.7 | 437 | 360.3 | 335.7 | 322.9 | 302.5 | 327.9 | 290.4
1200 | 1061 | 526.4 | 442.1 | 479.7 | 437.1 | 360.6 | 336 | 323.2 | 302.8 | 328 | 290.6
1201 | 1062 | 526.4 | 442.2 | 479.7 | 437.2 | 360.9 | 336.3 | 323.5 | 303.1 | 328.2 | 290.9
1202 | 1063 | 526.3 | 442.3 | 479.8 | 437.3 | 361.1 | 336.6 | 323.9 | 303.4 | 328.4 | 291.2
1203 | 1064 | 526.3 | 442.4 | 479.9 | 437.4 | 361.4 | 336.9 | 324.2 | 303.7 | 328.5 | 291.4
1204 | 1065 | 526.3 | 442.5 | 480 | 437.5 | 361.7 | 337.1 | 324.5 | 304 | 328.7 | 291.7
1205 | 1066 | 526.3 | 442.6 | 480 | 437.6 | 361.9 | 337.4 | 324.8 | 304.4 | 328.8 | 292
1206 | 1067 | 526.3 | 442.7 | 480.1 | 437.6 | 362.2 | 337.7 | 325.1 | 304.8 | 328.9 | 292.3
1207 | 1068 | 526.2 | 442.7 | 480.1 | 437.7 | 362.4 | 338 | 325.5 | 305.1 | 329 | 292.5
1208 | 1069 | 526.2 | 442.8 | 480.2 | 437.8 | 362.7 | 338.3 | 325.8 | 305.5 | 329.2 | 292.8
1209 | 1070 | 526.2 | 442.9 | 480.2 | 437.9 | 363 | 338.5 | 326.2 | 305.8 | 329.3 | 293.1
1210 | 1071 | 526.2 | 443 | 480.3 | 438 | 363.3 | 338.8 | 326.5 | 306.1 | 329.5 | 293.4
1211 | 1072 | 526.2 | 443.1 | 480.4 | 438.1 | 363.4 | 339.1 | 326.9 | 306.4 | 329.6 | 293.6
1212 | 1073 | 526.1 | 443.2 | 480.4 | 438.2 | 363.7 | 339.4 | 327.1 | 306.8 | 329.8 | 293.9
1213 | 1074 | 526.1 | 443.2 | 480.5 | 438.3 | 363.9 | 339.7 | 327.5 | 307.1 | 329.9 | 294.1
1214 | 1075 | 526.1 | 443.3 | 480.5 | 438.4 | 364.1 | 339.9 | 327.8 | 307.4 | 330 | 294.4
1215 | 1076 | 526.1 | 443.4 | 480.5 | 438.4 | 364.4 | 340.2 | 328.2 | 307.7 | 330.1 | 294.7
1216 | 1077 | 526.1 | 443.5 | 480.6 | 438.5 | 364.6 | 340.5 | 328.5 | 308.1 | 330.2 | 295
1217 | 1078 | 526.1 | 443.6 | 480.6 | 438.6 | 364.8 | 340.8 | 328.8 | 308.4 | 330.2 | 295.2
1218 | 1079 | 526 | 443.7 | 480.7 | 438.7 | 365 | 341.1 | 329.1 | 308.8 | 330.3 | 295.5
1219 | 1080 | 526 | 443.8 | 480.7 | 438.8 | 365.2 | 341.3 | 329.4 | 309.2 | 330.1 | 295.8
1220 | 1081 | 526 | 443.9 | 480.8 | 438.9 | 365.5 | 341.6 | 329.8 | 309.5 | 330.1 | 296
1221 | 1082 | 526 | 443.9 | 480.8 | 439 | 365.7 | 341.9 | 330.1 | 309.9 | 330.2 | 296.3
1222 | 1083 | 526 | 444 | 480.8 | 439.1 | 365.9 | 342.2 | 330.4 | 310.2 | 330.3 | 296.6
1223 | 1084 | 525.9 | 444.1 | 480.9 | 439.2 | 366.2 | 342.4 | 330.7 | 310.5 | 330.4 | 296.8
1224 | 1085 | 525.9 | 444.2 | 480.9 | 439.3 | 366.5 | 342.7 | 331.1 | 310.8 | 330.5 | 297.1
1225 | 1086 | 525.9 | 444.3 | 480.9 | 439.3 | 366.7 | 343 | 331.4 | 311.1 | 330.7 | 297.4
1226 | 1087 | 525.9 | 444.4 | 480.9 | 439.4 | 366.9 | 343.3 | 331.7 | 311.5 | 330.8 | 297.6
1227 | 1088 | 525.9 | 444.5 | 481 | 439.5 | 367.1 | 343.6 | 332 | 311.8 | 331 | 297.8
1228 | 1089 | 525.9 | 444.5 | 481.1 | 439.6 | 367.2 | 343.8 | 332.2 | 312.1 | 331.1 | 298.1
1229 | 1090 | 526 | 444.6 | 481.2 | 439.7 | 367.4 | 344.1 | 332.5 | 312.4 | 331.2 | 298.3
1230 | 1091 | 526 | 444.7 | 481.2 | 439.7 | 367.6 | 344.4 | 332.8 | 312.8 | 331.2 | 298.6
1231 | 1092 | 526 | 444.8 | 481.2 | 439.8 | 367.7 | 344.7 | 333.1 | 313.1 | 331.3 | 298.8
1232 | 1093 | 526 | 444.8 | 481.3 | 439.9 | 367.8 | 344.9 | 333.4 | 313.5 | 331.4 | 299
1233 | 1094 | 526 | 444.9 | 481.3 | 440 | 368 | 345.2 | 333.7 | 313.9 | 331.5 | 299.3
1234 | 1095 | 526.1 | 445 | 481.4 | 440.1 | 368.2 | 345.5 | 333.9 | 314.2 | 331.5 | 299.5
1235 | 1096 | 526.1 | 445.1 | 481.4 | 440.2 | 368.3 | 345.7 | 334.2 | 314.6 | 331.6 | 299.8
1236 | 1097 | 526.1 | 445.2 | 481.5 | 440.3 | 368.5 | 346 | 334.4 | 314.9 | 331.7 | 300.1
1237 | 1098 | 526.1 | 445.3 | 481.5 | 440.3 | 368.7 | 346.3 | 334.7 | 315.2 | 331.8 | 300.4
1238 | 1099 | 526.1 | 445.3 | 481.6 | 440.4 | 368.8 | 346.5 | 335 | 315.5 | 331.9 | 300.7
1239 | 1100 | 526.1 | 445.4 | 481.7 | 440.5 | 369 | 346.8 | 335.3 | 315.8 | 331.9 | 300.9
1240 | 1101 | 526.1 | 445.5 | 481.7 | 440.5 | 369.2 | 347 | 335.6 | 316.2 | 332 | 301.2
1241 | 1102 | 526.1 | 445.6 | 481.8 | 440.6 | 369.4 | 347.3 | 335.9 | 316.6 | 332.2 | 301.5
1242 | 1103 | 526.1 | 445.6 | 481.8 | 440.7 | 369.6 | 347.6 | 336.2 | 316.9 | 332.3 | 301.8
1243 | 1104 | 526.1 | 445.7 | 481.8 | 440.8 | 369.8 | 347.9 | 336.5 | 317.1 | 332.4 | 302
1244 | 1105 | 526.1 | 445.8 | 481.8 | 440.9 | 370 | 348.1 | 336.7 | 317.4 | 332.5 | 302.3
1245 | 1106 | 526.1 | 445.9 | 481.9 | 441 | 370.2 | 348.4 | 336.9 | 317.7 | 332.6 | 302.6
1246 | 1107 | 526.1 | 446 | 481.9 | 441.1 | 370.5 | 348.7 | 337.2 | 317.9 | 332.7 | 302.9
1247 | 1108 | 526.1 | 446.1 | 482 | 441.1 | 370.7 | 348.9 | 337.5 | 318.3 | 332.8 | 303.2
1248 | 1109 | 526.1 | 446.1 | 482 | 441.2 | 370.9 | 349.2 | 337.8 | 318.6 | 332.8 | 303.5
1249 | 1110 | 526.1 | 446.2 | 482.1 | 441.3 | 371.1 | 349.4 | 338.1 | 318.9 | 332.8 | 303.8
1250 | 1111 | 526.1 | 446.3 | 482.1 | 441.4 | 371.3 | 349.7 | 338.4 | 319.3 | 332.9 | 304
1251 | 1112 | 526 | 446.4 | 482.2 | 441.5 | 371.5 | 349.9 | 338.6 | 319.7 | 333.1 | 304.3
1252 | 1113 | 526 | 446.4 | 482.2 | 441.5 | 371.7 | 350.2 | 338.9 | 320 | 333.2 | 304.6
1253 | 1114 | 526 | 446.5 | 482.3 | 441.6 | 371.9 | 350.5 | 339.2 | 320.3 | 333.3 | 304.8
1254 | 1115 | 526 | 446.6 | 482.4 | 441.7 | 372.1 | 350.7 | 339.5 | 320.6 | 333.4 | 305.1
1255 | 1116 | 526 | 446.6 | 482.4 | 441.8 | 372.3 | 351 | 339.7 | 320.9 | 333.6 | 305.4
1256 | 1117 | 526.1 | 446.7 | 482.5 | 441.8 | 372.5 | 351.2 | 340 | 321.2 | 333.8 | 305.7
1257 | 1118 | 526.1 | 446.8 | 482.5 | 441.9 | 372.7 | 351.5 | 340.2 | 321.5 | 333.9 | 306
1258 | 1119 | 526.1 | 446.9 | 482.6 | 442 | 372.9 | 351.7 | 340.5 | 321.8 | 334 | 306.2
1259 | 1120 | 526.1 | 446.9 | 482.6 | 442.1 | 373.1 | 352 | 340.7 | 322 | 334.2 | 306.5
1260 | 1121 | 526.2 | 447 | 482.6 | 442.2 | 373.3 | 352.2 | 341 | 322.3 | 334.4 | 306.8
1261 | 1122 | 526.2 | 447.1 | 482.7 | 442.2 | 373.5 | 352.5 | 341.2 | 322.6 | 334.6 | 307.1
1262 | 1123 | 526.2 | 447.2 | 482.8 | 442.3 | 373.7 | 352.7 | 341.5 | 322.8 | 334.8 | 307.3
1263 | 1124 | 526.2 | 447.2 | 482.8 | 442.4 | 373.9 | 353 | 341.7 | 323.1 | 335 | 307.6
1264 | 1125 | 526.2 | 447.3 | 482.9 | 442.5 | 374.2 | 353.2 | 341.9 | 323.4 | 335 | 307.9
1265 | 1126 | 526.2 | 447.4 | 482.9 | 442.6 | 374.4 | 353.5 | 342.2 | 323.7 | 335.1 | 308.2
1266 | 1127 | 526.2 | 447.5 | 482.9 | 442.7 | 374.6 | 353.7 | 342.4 | 324 | 335.2 | 308.5
1267 | 1128 | 526.1 | 447.5 | 483 | 442.7 | 374.8 | 354 | 342.6 | 324.3 | 335.2 | 308.8
1268 | 1129 | 526.1 | 447.6 | 483 | 442.8 | 375.1 | 354.2 | 342.8 | 324.5 | 335.3 | 309.1
1269 | 1130 | 526.1 | 447.7 | 483.1 | 442.9 | 375.3 | 354.5 | 343.1 | 324.8 | 335.3 | 309.4
1270 | 1131 | 526.2 | 447.7 | 483.2 | 442.9 | 375.5 | 354.7 | 343.3 | 325.1 | 335.3 | 309.7
1271 | 1132 | 526.2 | 447.8 | 483.2 | 443 | 375.7 | 355 | 343.5 | 325.4 | 335.3 | 310
1272 | 1133 | 526.1 | 447.9 | 483.2 | 443.1 | 375.9 | 355.2 | 343.7 | 325.7 | 335.2 | 310.3
1273 | 1134 | 526.2 | 448 | 483.3 | 443.2 | 376.1 | 355.5 | 344 | 326.1 | 335.2 | 310.6
1274 | 1135 | 526.2 | 448 | 483.3 | 443.2 | 376.3 | 355.7 | 344.2 | 326.5 | 335.3 | 310.8
1275 | 1136 | 526.2 | 448.1 | 483.4 | 443.3 | 376.5 | 355.9 | 344.4 | 326.8 | 335.4 | 311.1
1276 | 1137 | 526.1 | 448.2 | 483.4 | 443.4 | 376.7 | 356.2 | 344.6 | 327.1 | 335.5 | 311.4
1277 | 1138 | 526.1 | 448.2 | 483.5 | 443.5 | 377 | 356.4 | 344.9 | 327.4 | 335.6 | 311.6
1278 | 1139 | 526.1 | 448.3 | 483.5 | 443.5 | 377.2 | 356.7 | 345.1 | 327.6 | 335.6 | 311.8
1279 | 1140 | 526 | 448.4 | 483.6 | 443.6 | 377.4 | 356.9 | 345.3 | 327.9 | 335.7 | 312
1280 | 1141 | 526 | 448.5 | 483.6 | 443.7 | 377.7 | 357.2 | 345.5 | 328.3 | 335.6 | 312.2
1281 | 1142 | 525.9 | 448.6 | 483.6 | 443.8 | 377.9 | 357.4 | 345.8 | 328.6 | 335.7 | 312.5
1282 | 1143 | 525.9 | 448.6 | 483.7 | 443.9 | 378.1 | 357.6 | 346 | 328.9 | 335.8 | 312.7
1283 | 1144 | 526 | 448.7 | 483.7 | 443.9 | 378.3 | 357.9 | 346.2 | 329.2 | 335.8 | 313
1284 | 1145 | 526 | 448.8 | 483.8 | 444 | 378.6 | 358.1 | 346.4 | 329.4 | 335.9 | 313.3
1285 | 1146 | 526 | 448.9 | 483.8 | 444.1 | 378.8 | 358.4 | 346.7 | 329.8 | 336.1 | 313.6
1286 | 1147 | 526 | 448.9 | 483.9 | 444.1 | 379 | 358.6 | 346.9 | 330.1 | 336.3 | 314
1287 | 1148 | 526 | 449 | 483.9 | 444.2 | 379.2 | 358.8 | 347.1 | 330.4 | 335.8 | 314.3
1288 | 1149 | 526 | 449 | 484 | 444.3 | 379.4 | 359.1 | 347.3 | 330.6 | 335.5 | 314.6
1289 | 1150 | 525.9 | 449.1 | 484 | 444.4 | 379.6 | 359.3 | 347.5 | 330.9 | 335.8 | 315
1290 | 1151 | 525.9 | 449.2 | 484.1 | 444.4 | 379.9 | 359.6 | 347.7 | 331.2 | 336 | 315.3
1291 | 1152 | 525.8 | 449.3 | 484.1 | 444.5 | 380 | 359.8 | 348 | 331.5 | 336.1 | 315.6
1292 | 1153 | 525.8 | 449.3 | 484.1 | 444.6 | 380.3 | 360 | 348.2 | 331.8 | 336.3 | 316
1293 | 1154 | 525.8 | 449.4 | 484.2 | 444.7 | 380.5 | 360.3 | 348.4 | 332 | 336.4 | 316.4
1294 | 1155 | 525.7 | 449.5 | 484.2 | 444.7 | 380.8 | 360.6 | 348.6 | 332.3 | 336.1 | 316.7
1295 | 1156 | 525.7 | 449.5 | 484.3 | 444.8 | 380.9 | 360.8 | 348.8 | 332.6 | 336.1 | 317.1
1296 | 1157 | 525.6 | 449.6 | 484.3 | 444.9 | 381.2 | 361 | 349 | 332.9 | 336.5 | 317.5
1297 | 1158 | 525.6 | 449.7 | 484.3 | 445 | 381.4 | 361.3 | 349.2 | 333.2 | 336.4 | 317.8
1298 | 1159 | 525.6 | 449.8 | 484.3 | 445.1 | 381.6 | 361.5 | 349.4 | 333.5 | 335.7 | 318.1
1299 | 1160 | 525.6 | 449.9 | 484.4 | 445.1 | 381.8 | 361.7 | 349.6 | 333.8 | 336 | 318.3
1300 | 1161 | 525.6 | 449.9 | 484.4 | 445.2 | 382 | 362 | 349.9 | 334 | 336.1 | 318.4
1301 | 1162 | 525.6 | 450 | 484.5 | 445.3 | 382.2 | 362.2 | 350.1 | 334.3 | 336.3 | 318.5
1302 | 1163 | 525.6 | 450 | 484.5 | 445.3 | 382.4 | 362.5 | 350.3 | 334.6 | 336.2 | 318.6
1303 | 1164 | 525.7 | 450.1 | 484.6 | 445.4 | 382.6 | 362.7 | 350.5 | 334.9 | 335.7 | 318.8
1304 | 1165 | 525.7 | 450.2 | 484.6 | 445.5 | 382.8 | 362.9 | 350.7 | 335.2 | 335.2 | 319
1305 | 1166 | 525.8 | 450.3 | 484.6 | 445.5 | 383 | 363.2 | 350.9 | 335.5 | 336.4 | 319.1
1306 | 1167 | 525.8 | 450.3 | 484.7 | 445.6 | 383.2 | 363.4 | 351.1 | 335.8 | 336.7 | 319.3
1307 | 1168 | 525.8 | 450.4 | 484.7 | 445.7 | 383.4 | 363.7 | 351.3 | 336.1 | 337.1 | 319.6
1308 | 1169 | 525.9 | 450.5 | 484.8 | 445.8 | 383.6 | 363.9 | 351.5 | 336.3 | 337.1 | 319.8
1309 | 1170 | 525.9 | 450.6 | 484.8 | 445.9 | 383.8 | 364.2 | 351.7 | 336.6 | 338.1 | 320.1
1310 | 1171 | 525.9 | 450.7 | 484.8 | 445.9 | 384 | 364.4 | 351.9 | 336.9 | 338.6 | 320.4
1311 | 1172 | 525.9 | 450.7 | 484.8 | 446 | 384.2 | 364.6 | 352.1 | 337.2 | 339 | 320.7
1312 | 1173 | 526 | 450.8 | 484.9 | 446.1 | 384.3 | 364.9 | 352.3 | 337.4 | 339.1 | 321
1313 | 1174 | 526 | 450.8 | 484.9 | 446.1 | 384.5 | 365.1 | 352.5 | 337.7 | 339.5 | 321.3
1314 | 1175 | 526.1 | 450.9 | 485 | 446.2 | 384.6 | 365.3 | 352.7 | 338 | 339.8 | 321.5
1315 | 1176 | 526.1 | 451 | 485 | 446.3 | 384.8 | 365.6 | 352.9 | 338.3 | 339.9 | 321.8
1316 | 1177 | 526.1 | 451 | 485.1 | 446.3 | 385 | 365.8 | 353.1 | 338.4 | 340 | 322.1
1317 | 1178 | 526.2 | 451.1 | 485.1 | 446.4 | 385.2 | 366.1 | 353.3 | 338.6 | 340.4 | 322.4
1318 | 1179 | 526.2 | 451.2 | 485.2 | 446.5 | 385.3 | 366.3 | 353.5 | 338.9 | 340.9 | 322.7
1319 | 1180 | 526.2 | 451.2 | 485.3 | 446.5 | 385.5 | 366.5 | 353.7 | 339.1 | 341.1 | 323
1320 | 1181 | 526.2 | 451.3 | 485.3 | 446.6 | 385.7 | 366.8 | 353.9 | 339.4 | 341.2 | 323.2
1321 | 1182 | 526.2 | 451.4 | 485.3 | 446.7 | 385.8 | 367 | 354.1 | 339.7 | 341.2 | 323.5
1322 | 1183 | 526.2 | 451.4 | 485.4 | 446.8 | 386 | 367.3 | 354.3 | 339.9 | 341.5 | 323.8
1323 | 1184 | 526.2 | 451.5 | 485.4 | 446.8 | 386.2 | 367.5 | 354.5 | 340.2 | 341.8 | 324.1
1324 | 1185 | 526.2 | 451.5 | 485.5 | 446.9 | 386.3 | 367.8 | 354.7 | 340.4 | 341.8 | 324.3
1325 | 1186 | 526.3 | 451.6 | 485.6 | 447 | 386.5 | 368 | 354.9 | 340.7 | 342 | 324.6
1326 | 1187 | 526.2 | 451.7 | 485.6 | 447 | 386.6 | 368.3 | 355.1 | 341 | 342.2 | 324.9
1327 | 1188 | 526.2 | 451.7 | 485.6 | 447.1 | 386.8 | 368.5 | 355.2 | 341.3 | 342.4 | 325.1
1328 | 1189 | 526.2 | 451.8 | 485.6 | 447.2 | 387 | 368.8 | 355.4 | 341.6 | 342.5 | 325.4
1329 | 1190 | 526.2 | 451.9 | 485.7 | 447.2 | 387.1 | 369 | 355.6 | 341.8 | 342.4 | 325.7
1330 | 1191 | 526.2 | 451.9 | 485.8 | 447.3 | 387.3 | 369.2 | 355.8 | 342 | 342.8 | 325.7
1331 | 1192 | 526.2 | 452 | 485.8 | 447.4 | 387.5 | 369.5 | 356 | 342.2 | 342.8 | 325.7
1332 | 1193 | 526.2 | 452.1 | 485.9 | 447.4 | 387.6 | 369.7 | 356.2 | 342.4 | 342.8 | 325.8
1333 | 1194 | 526.2 | 452.1 | 485.9 | 447.5 | 387.8 | 370 | 356.4 | 342.6 | 342.9 | 325.9
1334 | 1195 | 526.1 | 452.2 | 485.9 | 447.6 | 388 | 370.2 | 356.6 | 342.9 | 342.9 | 326
1335 | 1196 | 526.1 | 452.3 | 486 | 447.6 | 388.1 | 370.5 | 356.8 | 343.1 | 343 | 326.1
1336 | 1197 | 526 | 452.3 | 486 | 447.7 | 388.3 | 370.8 | 357 | 343.4 | 343.1 | 326.3
1337 | 1198 | 526 | 452.4 | 486 | 447.8 | 388.5 | 371 | 357.2 | 343.6 | 343.2 | 326.6
1338 | 1199 | 526 | 452.5 | 486.1 | 447.8 | 388.7 | 371.3 | 357.4 | 343.9 | 343.2 | 326.9
1339 | 1200 | 526 | 452.6 | 486.1 | 447.9 | 388.9 | 371.5 | 357.5 | 344.2 | 343.1 | 327.2
1340 | 1201 | 526 | 452.6 | 486.2 | 448 | 389 | 371.7 | 357.7 | 344.5 | 342.9 | 327.5
1341 | 1202 | 526 | 452.7 | 486.2 | 448 | 389.2 | 372 | 357.9 | 344.7 | 342.8 | 327.8
1342 | 1203 | 526 | 452.7 | 486.2 | 448.1 | 389.3 | 372.3 | 358.1 | 344.9 | 343 | 328.1
1343 | 1204 | 526 | 452.8 | 486.3 | 448.2 | 389.5 | 372.5 | 358.3 | 345.2 | 343.2 | 328.4
1344 | 1205 | 526 | 452.9 | 486.3 | 448.2 | 389.7 | 372.8 | 358.4 | 345.4 | 343.1 | 328.7
1345 | 1206 | 526 | 452.9 | 486.3 | 448.3 | 389.8 | 373 | 358.6 | 345.7 | 343.2 | 329
1346 | 1207 | 526 | 453 | 486.3 | 448.4 | 390 | 373.3 | 358.8 | 346 | 343.3 | 329.3
1347 | 1208 | 526 | 453.1 | 486.4 | 448.4 | 390.1 | 373.5 | 359 | 346.3 | 343.4 | 329.5
1348 | 1209 | 526 | 453.1 | 486.5 | 448.5 | 390.2 | 373.8 | 359.1 | 346.5 | 343.3 | 329.7
1349 | 1210 | 525.9 | 453.2 | 486.5 | 448.6 | 390.3 | 374 | 359.3 | 346.8 | 343.4 | 329.8
1350 | 1211 | 525.9 | 453.3 | 486.5 | 448.7 | 390.4 | 374.2 | 359.5 | 347 | 343.2 | 330.1
1351 | 1212 | 525.9 | 453.3 | 486.6 | 448.7 | 390.5 | 374.5 | 359.7 | 347.2 | 343.1 | 330.3
1352 | 1213 | 525.9 | 453.4 | 486.6 | 448.8 | 390.7 | 374.8 | 359.8 | 347.5 | 343.1 | 330.4
1353 | 1214 | 525.9 | 453.5 | 486.6 | 448.9 | 390.9 | 375 | 360 | 347.8 | 343.3 | 330.3
1354 | 1215 | 525.9 | 453.5 | 486.7 | 448.9 | 391 | 375.3 | 360.2 | 348.1 | 343.3 | 330.2
1355 | 1216 | 525.8 | 453.6 | 486.8 | 449 | 391.1 | 375.5 | 360.4 | 348.3 | 343.9 | 330.1
1356 | 1217 | 525.8 | 453.6 | 486.8 | 449 | 391.2 | 375.8 | 360.6 | 348.6 | 343.9 | 330.1
1357 | 1218 | 525.7 | 453.7 | 486.8 | 449.1 | 391.2 | 376.1 | 360.8 | 348.8 | 343.7 | 330.1
1358 | 1219 | 525.7 | 453.7 | 486.9 | 449.1 | 391.1 | 376.3 | 361 | 349.1 | 343.6 | 330.3
1359 | 1220 | 525.7 | 453.8 | 486.9 | 449.2 | 391.1 | 376.6 | 361.2 | 349.4 | 343.4 | 330.6
1360 | 1221 | 525.6 | 453.8 | 486.9 | 449.3 | 391.1 | 376.8 | 361.4 | 349.7 | 343.3 | 330.8
1361 | 1222 | 525.6 | 453.9 | 487 | 449.3 | 391.2 | 377.1 | 361.6 | 350.1 | 343 | 331.1
1362 | 1223 | 525.5 | 454 | 487 | 449.4 | 391.3 | 377.3 | 361.7 | 350.4 | 342.7 | 331.3
1363 | 1224 | 525.5 | 454 | 487 | 449.5 | 391.5 | 377.6 | 361.9 | 350.6 | 342.6 | 331.6
1364 | 1225 | 525.5 | 454.1 | 487.1 | 449.5 | 391.6 | 377.8 | 362.1 | 350.9 | 342.6 | 331.8
1365 | 1226 | 525.5 | 454.1 | 487.1 | 449.6 | 391.8 | 378.1 | 362.2 | 351.2 | 342.9 | 332.1
1366 | 1227 | 525.5 | 454.2 | 487.2 | 449.7 | 392.1 | 378.3 | 362.4 | 351.5 | 343 | 332.3
1367 | 1228 | 525.4 | 454.3 | 487.2 | 449.7 | 392.4 | 378.5 | 362.5 | 351.8 | 342.9 | 332.4
1368 | 1229 | 525.4 | 454.3 | 487.3 | 449.8 | 392.6 | 378.7 | 362.7 | 352.1 | 343 | 332.4
1369 | 1230 | 525.4 | 454.4 | 487.3 | 449.8 | 392.9 | 379 | 362.8 | 352.4 | 342.8 | 332.3
1370 | 1231 | 525.3 | 454.5 | 487.3 | 449.9 | 393.2 | 379.2 | 362.9 | 352.7 | 342.9 | 332.2
1371 | 1232 | 525.3 | 454.5 | 487.3 | 450 | 393.4 | 379.4 | 363.1 | 352.9 | 343.2 | 332.2
1372 | 1233 | 525.3 | 454.6 | 487.4 | 450 | 393.7 | 379.6 | 363.2 | 353.2 | 343.6 | 332.4
1373 | 1234 | 525.3 | 454.7 | 487.4 | 450.1 | 394 | 379.9 | 363.3 | 353.4 | 343.6 | 332.6
1374 | 1235 | 525.3 | 454.7 | 487.5 | 450.2 | 394.4 | 380.1 | 363.4 | 353.7 | 343.4 | 332.8
1375 | 1236 | 525.4 | 454.8 | 487.5 | 450.2 | 394.7 | 380.3 | 363.6 | 354 | 343.8 | 333.1
1376 | 1237 | 525.4 | 454.8 | 487.5 | 450.3 | 395.1 | 380.5 | 363.7 | 354.3 | 343.9 | 333.3
1377 | 1238 | 525.4 | 454.9 | 487.6 | 450.3 | 395.5 | 380.8 | 363.8 | 354.5 | 343.4 | 333.4
1378 | 1239 | 525.4 | 454.9 | 487.6 | 450.4 | 395.8 | 381 | 363.9 | 354.8 | 343.3 | 333.6
1379 | 1240 | 525.4 | 455 | 487.6 | 450.5 | 396.1 | 381.2 | 364 | 355 | 343.3 | 333.8
1380 | 1241 | 525.4 | 455.1 | 487.7 | 450.5 | 396.5 | 381.4 | 364.1 | 355.3 | 343.5 | 334
1381 | 1242 | 525.4 | 455.1 | 487.7 | 450.6 | 396.8 | 381.7 | 364.2 | 355.5 | 343.5 | 334.2
1382 | 1243 | 525.4 | 455.2 | 487.7 | 450.7 | 397.1 | 381.9 | 364.3 | 355.7 | 343.4 | 334.3
1383 | 1244 | 525.4 | 455.3 | 487.7 | 450.7 | 397.4 | 382.2 | 364.4 | 355.9 | 343.5 | 334.4
1384 | 1245 | 525.4 | 455.3 | 487.8 | 450.8 | 397.6 | 382.4 | 364.5 | 356.2 | 343.7 | 334.3
1385 | 1246 | 525.4 | 455.4 | 487.8 | 450.8 | 397.8 | 382.7 | 364.6 | 356.4 | 343.5 | 334
1386 | 1247 | 525.4 | 455.4 | 487.9 | 450.9 | 398 | 382.9 | 364.7 | 356.7 | 343.6 | 333.8
1387 | 1248 | 525.4 | 455.5 | 487.9 | 451 | 398.3 | 383.2 | 364.9 | 356.9 | 343.6 | 333.7
1388 | 1249 | 525.5 | 455.5 | 488 | 451 | 398.4 | 383.4 | 365 | 357.1 | 343.6 | 333.6
1389 | 1250 | 525.5 | 455.6 | 488 | 451.1 | 398.6 | 383.6 | 365.1 | 357.4 | 343.6 | 333.7
1390 | 1251 | 525.6 | 455.6 | 488.1 | 451.1 | 398.8 | 383.9 | 365.2 | 357.6 | 343.6 | 333.9
1391 | 1252 | 525.7 | 455.7 | 488.1 | 451.2 | 399 | 384.1 | 365.4 | 357.9 | 343.6 | 334.1
1392 | 1253 | 525.8 | 455.7 | 488.1 | 451.3 | 399.2 | 384.4 | 365.5 | 358.1 | 343.8 | 334.3
1393 | 1254 | 525.8 | 455.8 | 488.2 | 451.3 | 399.4 | 384.6 | 365.7 | 358.2 | 343.8 | 334.6
1394 | 1255 | 525.9 | 455.9 | 488.2 | 451.4 | 399.6 | 384.8 | 365.8 | 358.4 | 343.6 | 334.8
1395 | 1256 | 525.9 | 455.9 | 488.3 | 451.4 | 399.8 | 385.1 | 366 | 358.5 | 343.7 | 335
1396 | 1257 | 525.9 | 456 | 488.3 | 451.5 | 400 | 385.3 | 366.2 | 358.7 | 343.7 | 335.2
1397 | 1258 | 525.9 | 456 | 488.4 | 451.5 | 400.2 | 385.6 | 366.4 | 358.9 | 343.6 | 335.4
1398 | 1259 | 525.9 | 456.1 | 488.4 | 451.6 | 400.4 | 385.8 | 366.6 | 359.1 | 343.7 | 335.4
1399 | 1260 | 526 | 456.1 | 488.5 | 451.6 | 400.5 | 386 | 366.8 | 359.3 | 343.6 | 335.3
1400 | 1261 | 526 | 456.2 | 488.5 | 451.7 | 400.7 | 386.2 | 367 | 359.5 | 343.5 | 335.3
1401 | 1262 | 526 | 456.3 | 488.5 | 451.8 | 400.9 | 386.5 | 367.1 | 359.5 | 343.7 | 335.2
1402 | 1263 | 526 | 456.3 | 488.6 | 451.8 | 401.1 | 386.7 | 367.3 | 359.7 | 343.7 | 335.2
1403 | 1264 | 526 | 456.3 | 488.6 | 451.9 | 401.3 | 386.9 | 367.5 | 359.9 | 343.7 | 335.5
1404 | 1265 | 526 | 456.4 | 488.7 | 451.9 | 401.5 | 387.1 | 367.7 | 360 | 343.8 | 335.7
1405 | 1266 | 526 | 456.5 | 488.7 | 452 | 401.7 | 387.4 | 367.9 | 360.1 | 343.7 | 335.8
1406 | 1267 | 525.9 | 456.5 | 488.7 | 452.1 | 401.9 | 387.6 | 368.1 | 360.2 | 343.6 | 335.9
1407 | 1268 | 525.9 | 456.6 | 488.7 | 452.1 | 402 | 387.8 | 368.2 | 360.3 | 343.5 | 335.9
1408 | 1269 | 525.9 | 456.7 | 488.7 | 452.2 | 402.2 | 388.1 | 368.4 | 360.4 | 343.3 | 335.9
1409 | 1270 | 525.8 | 456.7 | 488.8 | 452.3 | 402.4 | 388.3 | 368.6 | 360.6 | 343.2 | 336.2
1410 | 1271 | 525.8 | 456.8 | 488.8 | 452.3 | 402.6 | 388.5 | 368.7 | 360.8 | 343.2 | 336.4
1411 | 1272 | 525.8 | 456.8 | 488.9 | 452.4 | 402.7 | 388.8 | 368.9 | 360.9 | 343.1 | 336.7
1412 | 1273 | 525.8 | 456.9 | 488.9 | 452.4 | 402.9 | 389 | 369.1 | 361 | 343.1 | 336.9
1413 | 1274 | 525.7 | 456.9 | 489 | 452.4 | 403.1 | 389.3 | 369.3 | 361.2 | 342.9 | 337.1
1414 | 1275 | 525.7 | 457 | 489 | 452.5 | 403.2 | 389.5 | 369.6 | 361.4 | 342.7 | 337.2
1415 | 1276 | 525.7 | 457 | 489 | 452.6 | 403.4 | 389.8 | 369.8 | 361.5 | 342.6 | 337.3
1416 | 1277 | 525.7 | 457.1 | 489 | 452.6 | 403.6 | 390 | 370 | 361.6 | 342.3 | 337.4
1417 | 1278 | 525.7 | 457.1 | 489.1 | 452.7 | 403.7 | 390.3 | 370.2 | 361.7 | 342 | 337.4
1418 | 1279 | 525.7 | 457.2 | 489.1 | 452.7 | 403.9 | 390.5 | 370.4 | 361.8 | 341.8 | 337.5
1419 | 1280 | 525.7 | 457.3 | 489.1 | 452.8 | 404.1 | 390.7 | 370.8 | 362 | 341.7 | 337.6
1420 | 1281 | 525.7 | 457.3 | 489.2 | 452.9 | 404.3 | 391 | 371.1 | 362.2 | 341.5 | 337.8
1421 | 1282 | 525.7 | 457.3 | 489.2 | 452.9 | 404.4 | 391.2 | 371.3 | 362.4 | 341.3 | 338.1
1422 | 1283 | 525.7 | 457.4 | 489.2 | 453 | 404.6 | 391.4 | 371.6 | 362.6 | 341.2 | 338.4
1423 | 1284 | 525.6 | 457.5 | 489.3 | 453 | 404.7 | 391.7 | 371.8 | 362.7 | 341.1 | 338.5
1424 | 1285 | 525.6 | 457.5 | 489.3 | 453.1 | 404.9 | 391.9 | 372.1 | 362.9 | 341 | 338.6
1425 | 1286 | 525.6 | 457.6 | 489.3 | 453.1 | 405 | 392.2 | 372.3 | 363 | 340.8 | 338.6
1426 | 1287 | 525.5 | 457.6 | 489.4 | 453.2 | 405.2 | 392.4 | 372.5 | 363.2 | 340.7 | 338.7
1427 | 1288 | 525.5 | 457.7 | 489.4 | 453.2 | 405.4 | 392.6 | 372.7 | 363.4 | 340.6 | 338.8
1428 | 1289 | 525.5 | 457.7 | 489.5 | 453.3 | 405.5 | 392.9 | 373 | 363.5 | 340.5 | 338.9
1429 | 1290 | 525.5 | 457.8 | 489.5 | 453.4 | 405.7 | 393.1 | 373.2 | 363.7 | 340.4 | 339.1
1430 | 1291 | 525.5 | 457.9 | 489.5 | 453.4 | 405.9 | 393.4 | 373.4 | 363.8 | 340.3 | 339.2
1431 | 1292 | 525.5 | 457.9 | 489.5 | 453.5 | 406 | 393.6 | 373.7 | 364 | 340.2 | 339.4
1432 | 1293 | 525.5 | 458 | 489.5 | 453.5 | 406.2 | 393.8 | 374 | 364.1 | 340.1 | 339.7
1433 | 1294 | 525.5 | 458 | 489.6 | 453.6 | 406.3 | 394.1 | 374.2 | 364.3 | 340 | 339.9
1434 | 1295 | 525.5 | 458.1 | 489.6 | 453.6 | 406.4 | 394.3 | 374.5 | 364.4 | 340 | 340.2
1435 | 1296 | 525.5 | 458.1 | 489.6 | 453.7 | 406.6 | 394.6 | 374.8 | 364.6 | 339.9 | 340.4
1436 | 1297 | 525.6 | 458.2 | 489.7 | 453.7 | 406.7 | 394.8 | 375 | 364.8 | 339.8 | 340.5
1437 | 1298 | 525.6 | 458.2 | 489.7 | 453.8 | 406.9 | 395 | 375.2 | 364.9 | 339.8 | 340.7
1438 | 1299 | 525.6 | 458.3 | 489.8 | 453.8 | 407 | 395.2 | 375.5 | 365 | 339.7 | 340.8
1439 | 1300 | 525.7 | 458.3 | 489.8 | 453.9 | 407.2 | 395.4 | 375.7 | 365.2 | 339.7 | 340.9
1440 | 1301 | 525.7 | 458.4 | 489.8 | 453.9 | 407.4 | 395.7 | 375.9 | 365.3 | 339.6 | 341.1
1441 | 1302 | 525.7 | 458.4 | 489.9 | 454 | 407.5 | 395.9 | 376.1 | 365.5 | 339.5 | 341.2
1442 | 1303 | 525.7 | 458.5 | 489.9 | 454 | 407.7 | 396.1 | 376.5 | 365.7 | 339.5 | 341.4
1443 | 1304 | 525.8 | 458.5 | 489.9 | 454.1 | 407.8 | 396.3 | 377 | 365.9 | 339.4 | 341.6
1444 | 1305 | 525.9 | 458.6 | 490 | 454.1 | 408 | 396.6 | 377.4 | 366.1 | 339.3 | 341.8
1445 | 1306 | 525.9 | 458.7 | 490 | 454.2 | 408.1 | 396.8 | 377.8 | 366.3 | 339.1 | 342
1446 | 1307 | 526 | 458.7 | 490.1 | 454.2 | 408.3 | 397 | 378.9 | 366.5 | 339.1 | 342.2
1447 | 1308 | 526 | 458.8 | 490.1 | 454.3 | 408.5 | 397.2 | 381.2 | 366.7 | 339 | 342.4
1448 | 1309 | 526 | 458.8 | 490.1 | 454.3 | 408.7 | 397.4 | 383.1 | 366.9 | 339 | 342.6
1449 | 1310 | 526 | 458.9 | 490.1 | 454.4 | 408.8 | 397.7 | 384.6 | 367.1 | 338.9 | 342.8
1450 | 1311 | 526 | 458.9 | 490.2 | 454.4 | 409 | 397.9 | 385.8 | 367.3 | 338.8 | 343
1451 | 1312 | 526 | 459 | 490.2 | 454.5 | 409.2 | 398.1 | 386.9 | 367.6 | 338.7 | 343.2
1452 | 1313 | 526 | 459 | 490.2 | 454.5 | 409.4 | 398.3 | 387.8 | 367.8 | 338.7 | 343.4
1453 | 1314 | 526 | 459.1 | 490.2 | 454.6 | 409.6 | 398.5 | 388.6 | 368 | 338.7 | 343.6
1454 | 1315 | 525.9 | 459.1 | 490.3 | 454.6 | 409.8 | 398.7 | 389.3 | 368.1 | 338.6 | 343.7
1455 | 1316 | 525.9 | 459.2 | 490.3 | 454.7 | 409.9 | 398.9 | 389.9 | 368.3 | 338.5 | 343.8
1456 | 1317 | 525.9 | 459.2 | 490.3 | 454.7 | 410.1 | 399.2 | 390.4 | 368.5 | 338.4 | 343.9
1457 | 1318 | 525.9 | 459.3 | 490.4 | 454.8 | 410.3 | 399.4 | 390.9 | 368.7 | 338.3 | 344
1458 | 1319 | 525.9 | 459.3 | 490.4 | 454.8 | 410.5 | 399.6 | 391.4 | 368.9 | 338.2 | 344.2
1459 | 1320 | 525.9 | 459.4 | 490.5 | 454.9 | 410.7 | 399.8 | 391.8 | 369.1 | 338.1 | 344.3
1460 | 1321 | 525.9 | 459.4 | 490.5 | 454.9 | 410.9 | 400 | 392.1 | 369.3 | 337.9 | 344.5
1461 | 1322 | 526 | 459.5 | 490.5 | 455 | 411.1 | 400.2 | 392.4 | 369.6 | 337.8 | 344.6
1462 | 1323 | 526 | 459.5 | 490.5 | 455 | 411.3 | 400.4 | 392.8 | 369.8 | 337.9 | 344.8
1463 | 1324 | 526 | 459.6 | 490.6 | 455.1 | 411.4 | 400.6 | 393 | 370 | 337.9 | 345
1464 | 1325 | 526 | 459.6 | 490.6 | 455.1 | 411.7 | 400.8 | 393.3 | 370.1 | 337.9 | 345.1
1465 | 1326 | 526 | 459.7 | 490.6 | 455.2 | 411.9 | 401 | 393.6 | 370.3 | 337.9 | 345.3
1466 | 1327 | 526.1 | 459.7 | 490.7 | 455.2 | 412 | 401.2 | 393.8 | 370.4 | 338 | 345.5
1467 | 1328 | 526.1 | 459.8 | 490.7 | 455.3 | 412.3 | 401.4 | 394 | 370.7 | 338.1 | 345.7
1468 | 1329 | 526.1 | 459.8 | 490.7 | 455.3 | 412.5 | 401.6 | 394.2 | 370.9 | 338.1 | 345.9
1469 | 1330 | 526 | 459.9 | 490.7 | 455.4 | 412.7 | 401.8 | 394.4 | 371 | 338.3 | 346.1
1470 | 1331 | 526 | 459.9 | 490.8 | 455.4 | 413 | 402 | 394.6 | 371.1 | 338.3 | 346.3
1471 | 1332 | 526 | 460 | 490.8 | 455.5 | 413.2 | 402.3 | 394.8 | 371.3 | 338.3 | 346.5
1472 | 1333 | 526 | 460 | 490.9 | 455.5 | 413.5 | 402.5 | 394.9 | 371.6 | 338.2 | 346.7
1473 | 1334 | 526 | 460.1 | 490.9 | 455.6 | 413.7 | 402.7 | 395.1 | 371.8 | 338.3 | 346.9
1474 | 1335 | 526.1 | 460.2 | 490.9 | 455.6 | 413.9 | 402.9 | 395.3 | 372 | 338.3 | 347.1
1475 | 1336 | 526 | 460.2 | 490.9 | 455.7 | 414.1 | 403.1 | 395.4 | 372.1 | 338.4 | 347.3
1476 | 1337 | 526.1 | 460.3 | 490.9 | 455.8 | 414.3 | 403.3 | 395.6 | 372.3 | 338.3 | 347.5
1477 | 1338 | 526.1 | 460.3 | 490.9 | 455.8 | 414.6 | 403.5 | 395.7 | 372.5 | 338.3 | 347.7
1478 | 1339 | 526.1 | 460.4 | 491 | 455.8 | 414.8 | 403.7 | 395.9 | 372.8 | 338.4 | 347.9
1479 | 1340 | 526.1 | 460.4 | 491 | 455.9 | 415 | 403.9 | 396 | 373 | 338.3 | 348.1
1480 | 1341 | 526.1 | 460.5 | 491 | 455.9 | 415.2 | 404.1 | 396.2 | 373.3 | 338.3 | 348.3
1481 | 1342 | 526.1 | 460.5 | 491.1 | 456 | 415.4 | 404.3 | 396.3 | 373.5 | 338.2 | 348.5
1482 | 1343 | 526.1 | 460.6 | 491.1 | 456 | 415.6 | 404.5 | 396.5 | 373.7 | 338.2 | 348.6
1483 | 1344 | 526.1 | 460.6 | 491.1 | 456.1 | 415.8 | 404.8 | 396.6 | 373.9 | 338.3 | 348.8
1484 | 1345 | 526.1 | 460.7 | 491.2 | 456.1 | 416 | 405 | 396.7 | 374.1 | 338.3 | 349
1485 | 1346 | 526.1 | 460.7 | 491.2 | 456.2 | 416.2 | 405.2 | 396.9 | 374.3 | 338.4 | 349.1
1486 | 1347 | 526.1 | 460.8 | 491.2 | 456.3 | 416.4 | 405.4 | 397 | 374.5 | 338.3 | 349.4
1487 | 1348 | 526 | 460.8 | 491.3 | 456.3 | 416.6 | 405.6 | 397.1 | 374.7 | 338.2 | 349.6
1488 | 1349 | 526 | 460.8 | 491.3 | 456.3 | 416.8 | 405.8 | 397.3 | 374.9 | 338.3 | 349.9
1489 | 1350 | 526 | 460.9 | 491.3 | 456.4 | 417 | 406 | 397.4 | 375.1 | 338.3 | 350.1
1490 | 1351 | 526 | 460.9 | 491.4 | 456.4 | 417.2 | 406.2 | 397.5 | 375.2 | 338.1 | 350.4
1491 | 1352 | 525.9 | 461 | 491.4 | 456.5 | 417.4 | 406.4 | 397.7 | 375.4 | 338.2 | 350.7
1492 | 1353 | 525.8 | 461 | 491.4 | 456.5 | 417.6 | 406.6 | 397.8 | 375.6 | 338.2 | 350.9
1493 | 1354 | 525.8 | 461.1 | 491.4 | 456.6 | 417.8 | 406.8 | 397.9 | 375.9 | 338.3 | 351.2
1494 | 1355 | 525.8 | 461.1 | 491.4 | 456.6 | 418 | 407 | 398.1 | 376.1 | 338.3 | 351.4
1495 | 1356 | 525.8 | 461.2 | 491.5 | 456.7 | 418.2 | 407.2 | 398.2 | 376.2 | 338.4 | 351.6
1496 | 1357 | 525.8 | 461.2 | 491.5 | 456.7 | 418.3 | 407.4 | 398.4 | 376.4 | 338.4 | 351.8
1497 | 1358 | 525.8 | 461.3 | 491.6 | 456.8 | 418.5 | 407.6 | 398.5 | 376.7 | 338.5 | 352
1498 | 1359 | 525.8 | 461.3 | 491.6 | 456.8 | 418.7 | 407.8 | 398.6 | 376.9 | 338.6 | 352.3
1499 | 1360 | 525.8 | 461.4 | 491.6 | 456.9 | 418.9 | 408.1 | 398.8 | 377.1 | 338.7 | 352.5
1500 | 1361 | 525.8 | 461.4 | 491.6 | 456.9 | 419.2 | 408.3 | 398.9 | 377.3 | 338.8 | 352.7
1501 | 1362 | 525.8 | 461.5 | 491.6 | 457 | 419.3 | 408.5 | 399 | 377.5 | 338.9 | 352.9
1502 | 1363 | 525.8 | 461.5 | 491.6 | 457 | 419.5 | 408.7 | 399.2 | 377.7 | 339 | 353.1
1503 | 1364 | 525.8 | 461.6 | 491.7 | 457.1 | 419.7 | 408.9 | 399.3 | 377.8 | 339.1 | 353.3
1504 | 1365 | 525.8 | 461.6 | 491.7 | 457.1 | 419.9 | 409.1 | 399.4 | 378 | 339.3 | 353.5
1505 | 1366 | 525.7 | 461.7 | 491.7 | 457.2 | 420.1 | 409.3 | 399.6 | 378.1 | 339.3 | 353.7
1506 | 1367 | 525.7 | 461.7 | 491.8 | 457.2 | 420.2 | 409.5 | 399.7 | 378.3 | 339.4 | 353.9
1507 | 1368 | 525.7 | 461.8 | 491.8 | 457.3 | 420.4 | 409.8 | 399.8 | 378.5 | 339.6 | 354.1
1508 | 1369 | 525.8 | 461.8 | 491.9 | 457.3 | 420.5 | 410 | 399.9 | 378.6 | 339.7 | 354.4
1509 | 1370 | 525.7 | 461.9 | 491.9 | 457.3 | 420.6 | 410.2 | 400.1 | 378.8 | 339.7 | 354.6
1510 | 1371 | 525.7 | 461.9 | 491.9 | 457.4 | 420.8 | 410.4 | 400.2 | 378.9 | 339.8 | 354.8
1511 | 1372 | 525.7 | 461.9 | 491.9 | 457.4 | 420.9 | 410.6 | 400.3 | 379.1 | 339.9 | 354.9
1512 | 1373 | 525.7 | 462 | 491.9 | 457.5 | 421.1 | 410.8 | 400.5 | 379.3 | 340 | 355.1
1513 | 1374 | 525.7 | 462 | 492 | 457.5 | 421.3 | 411 | 400.6 | 379.5 | 340.2 | 355.2
1514 | 1375 | 525.7 | 462.1 | 492 | 457.6 | 421.4 | 411.2 | 400.7 | 379.7 | 340.5 | 355.3
1515 | 1376 | 525.7 | 462.1 | 492 | 457.6 | 421.6 | 411.4 | 400.8 | 379.9 | 340.6 | 355.5
1516 | 1377 | 525.7 | 462.2 | 492 | 457.7 | 421.7 | 411.6 | 401 | 380.1 | 340.7 | 355.7
1517 | 1378 | 525.7 | 462.2 | 492.1 | 457.7 | 421.9 | 411.9 | 401.1 | 380.3 | 340.8 | 355.9
1518 | 1379 | 525.7 | 462.3 | 492.1 | 457.8 | 422 | 412.1 | 401.2 | 380.5 | 341 | 356.1
1519 | 1380 | 525.7 | 462.3 | 492.1 | 457.8 | 422.1 | 412.3 | 401.4 | 380.6 | 341.2 | 356.3
1520 | 1381 | 525.6 | 462.4 | 492.2 | 457.9 | 422.3 | 412.5 | 401.5 | 380.8 | 341.4 | 356.5
1521 | 1382 | 525.6 | 462.4 | 492.2 | 457.9 | 422.5 | 412.7 | 401.6 | 380.9 | 341.6 | 356.6
1522 | 1383 | 525.6 | 462.4 | 492.2 | 457.9 | 422.7 | 412.9 | 401.8 | 381.1 | 341.8 | 356.7
1523 | 1384 | 525.6 | 462.5 | 492.2 | 458 | 422.8 | 413.1 | 401.9 | 381.4 | 342 | 356.7
1524 | 1385 | 525.6 | 462.5 | 492.3 | 458 | 423 | 413.4 | 402 | 381.5 | 342.2 | 356.7
1525 | 1386 | 525.7 | 462.6 | 492.3 | 458.1 | 423.2 | 413.6 | 402.2 | 381.7 | 342.4 | 356.8
1526 | 1387 | 525.7 | 462.6 | 492.3 | 458.1 | 423.3 | 413.8 | 402.3 | 381.8 | 342.6 | 356.8
1527 | 1388 | 525.7 | 462.7 | 492.3 | 458.2 | 423.5 | 414 | 402.4 | 382 | 342.8 | 356.9
1528 | 1389 | 525.8 | 462.7 | 492.3 | 458.2 | 423.6 | 414.2 | 402.6 | 382.1 | 342.9 | 357
1529 | 1390 | 525.8 | 462.8 | 492.4 | 458.3 | 423.7 | 414.4 | 402.7 | 382.3 | 343.1 | 357.1
1530 | 1391 | 525.8 | 462.8 | 492.4 | 458.3 | 423.8 | 414.6 | 402.9 | 382.5 | 343.4 | 357.2
1531 | 1392 | 525.8 | 462.9 | 492.4 | 458.4 | 424 | 414.8 | 403 | 382.6 | 343.6 | 357.3
1532 | 1393 | 525.7 | 462.9 | 492.4 | 458.4 | 424.1 | 415 | 403.1 | 382.7 | 343.9 | 357.5
1533 | 1394 | 525.7 | 463 | 492.4 | 458.5 | 424.2 | 415.3 | 403.3 | 382.9 | 344 | 357.7
1534 | 1395 | 525.8 | 463 | 492.5 | 458.5 | 424.3 | 415.5 | 403.4 | 383.1 | 344.2 | 358
1535 | 1396 | 525.8 | 463 | 492.5 | 458.6 | 424.4 | 415.7 | 403.6 | 383.3 | 344.4 | 358.2
1536 | 1397 | 525.8 | 463.1 | 492.5 | 458.6 | 424.4 | 415.9 | 403.7 | 383.4 | 344.6 | 358.5
1537 | 1398 | 525.8 | 463.1 | 492.5 | 458.7 | 424.5 | 416.1 | 403.8 | 383.7 | 344.8 | 358.7
1538 | 1399 | 525.8 | 463.2 | 492.5 | 458.7 | 424.7 | 416.3 | 404 | 383.9 | 345.1 | 358.9
1539 | 1400 | 525.8 | 463.2 | 492.6 | 458.7 | 424.7 | 416.6 | 404.1 | 384 | 345.2 | 359.1
1540 | 1401 | 525.8 | 463.3 | 492.6 | 458.8 | 424.7 | 416.8 | 404.2 | 384.2 | 345.3 | 359.3
1541 | 1402 | 525.9 | 463.3 | 492.7 | 458.8 | 424.8 | 417 | 404.4 | 384.3 | 345.6 | 359.5
1542 | 1403 | 525.9 | 463.3 | 492.7 | 458.9 | 424.8 | 417.2 | 404.5 | 384.4 | 345.8 | 359.7
1543 | 1404 | 525.9 | 463.4 | 492.7 | 458.9 | 424.9 | 417.4 | 404.6 | 384.6 | 346.1 | 359.9
1544 | 1405 | 525.9 | 463.4 | 492.8 | 459 | 425 | 417.6 | 404.7 | 384.7 | 346.5 | 360.1
1545 | 1406 | 525.9 | 463.5 | 492.8 | 459 | 425 | 417.8 | 404.9 | 384.9 | 346.8 | 360.2
1546 | 1407 | 525.9 | 463.5 | 492.8 | 459.1 | 425 | 418.1 | 405 | 385.1 | 347.1 | 360.3
1547 | 1408 | 525.9 | 463.5 | 492.8 | 459.1 | 425 | 418.3 | 405.2 | 385.3 | 347.3 | 360.4
1548 | 1409 | 525.9 | 463.6 | 492.9 | 459.1 | 425.1 | 418.5 | 405.3 | 385.4 | 347.5 | 360.4
1549 | 1410 | 525.9 | 463.7 | 492.9 | 459.2 | 425.1 | 418.7 | 405.4 | 385.6 | 347.7 | 360.5
1550 | 1411 | 525.9 | 463.7 | 492.9 | 459.2 | 425.1 | 418.9 | 405.6 | 385.7 | 348.1 | 360.7
1551 | 1412 | 525.9 | 463.7 | 492.9 | 459.3 | 425.1 | 419.1 | 405.7 | 385.9 | 348.4 | 360.9
1552 | 1413 | 525.9 | 463.8 | 492.9 | 459.3 | 425.2 | 419.3 | 405.8 | 386 | 348.7 | 361.1
1553 | 1414 | 525.9 | 463.8 | 493 | 459.4 | 425.1 | 419.5 | 406 | 386.2 | 349 | 361.3
1554 | 1415 | 526 | 463.9 | 493 | 459.4 | 425.1 | 419.7 | 406.1 | 386.4 | 349.1 | 361.5
1555 | 1416 | 526 | 463.9 | 493 | 459.5 | 425.1 | 420 | 406.2 | 386.5 | 349.5 | 361.7
1556 | 1417 | 526 | 463.9 | 493 | 459.5 | 425.1 | 420.2 | 406.4 | 386.7 | 349.9 | 361.9
1557 | 1418 | 526 | 464 | 493.1 | 459.6 | 425.1 | 420.4 | 406.5 | 386.8 | 350.2 | 362
1558 | 1419 | 526 | 464 | 493.1 | 459.6 | 425 | 420.6 | 406.7 | 387.1 | 350.4 | 362.2
1559 | 1420 | 526 | 464 | 493.2 | 459.6 | 425 | 420.8 | 406.8 | 387.2 | 350.7 | 362.3
1560 | 1421 | 526 | 464.1 | 493.2 | 459.7 | 425 | 421 | 407 | 387.4 | 351 | 362.5
1561 | 1422 | 526 | 464.1 | 493.2 | 459.7 | 424.9 | 421.2 | 407.1 | 387.6 | 351.2 | 362.7
1562 | 1423 | 526 | 464.2 | 493.2 | 459.8 | 424.9 | 421.4 | 407.3 | 387.8 | 351.3 | 362.8
1563 | 1424 | 526 | 464.2 | 493.2 | 459.8 | 424.9 | 421.6 | 407.4 | 387.9 | 351.5 | 363
1564 | 1425 | 525.9 | 464.2 | 493.3 | 459.9 | 424.9 | 421.8 | 407.6 | 388.1 | 352 | 363
1565 | 1426 | 525.9 | 464.3 | 493.3 | 459.9 | 424.9 | 422 | 407.8 | 388.2 | 352.2 | 363.1
1566 | 1427 | 525.9 | 464.3 | 493.3 | 460 | 424.9 | 422.2 | 407.9 | 388.3 | 352.4 | 363.2
1567 | 1428 | 525.9 | 464.4 | 493.4 | 460 | 424.9 | 422.4 | 408.1 | 388.5 | 352.7 | 363.2
1568 | 1429 | 525.9 | 464.4 | 493.4 | 460.1 | 425 | 422.6 | 408.2 | 388.7 | 353 | 363.3
1569 | 1430 | 525.9 | 464.5 | 493.4 | 460.1 | 425 | 422.8 | 408.4 | 389 | 353.2 | 363.5
1570 | 1431 | 525.8 | 464.5 | 493.4 | 460.1 | 425 | 423 | 408.5 | 389.2 | 353.5 | 363.6
1571 | 1432 | 525.8 | 464.5 | 493.4 | 460.2 | 425.1 | 423.2 | 408.7 | 389.4 | 353.8 | 363.7
1572 | 1433 | 525.8 | 464.6 | 493.4 | 460.2 | 425.1 | 423.4 | 408.9 | 389.5 | 354 | 363.9
1573 | 1434 | 525.8 | 464.6 | 493.5 | 460.3 | 425.1 | 423.6 | 409 | 389.7 | 354.3 | 364.1
1574 | 1435 | 525.7 | 464.6 | 493.5 | 460.3 | 425.2 | 423.8 | 409.2 | 389.8 | 354.6 | 364.4
1575 | 1436 | 525.7 | 464.7 | 493.5 | 460.4 | 425.2 | 424 | 409.4 | 390 | 355 | 364.6
1576 | 1437 | 525.7 | 464.7 | 493.5 | 460.4 | 425.2 | 424.1 | 409.6 | 390.1 | 355.4 | 364.8
1577 | 1438 | 525.6 | 464.8 | 493.5 | 460.5 | 425.3 | 424.3 | 409.7 | 390.3 | 355.6 | 364.9
1578 | 1439 | 525.6 | 464.8 | 493.5 | 460.5 | 425.3 | 424.5 | 409.9 | 390.5 | 356 | 365.1
1579 | 1440 | 525.6 | 464.8 | 493.5 | 460.5 | 425.4 | 424.7 | 410.1 | 390.6 | 356.2 | 365.3
1580 | 1441 | 525.6 | 464.9 | 493.6 | 460.6 | 425.4 | 424.9 | 410.3 | 390.7 | 356.5 | 365.4
1581 | 1442 | 525.6 | 464.9 | 493.6 | 460.6 | 425.5 | 425.1 | 410.4 | 390.9 | 356.8 | 365.6
1582 | 1443 | 525.6 | 465 | 493.6 | 460.7 | 425.6 | 425.3 | 410.6 | 391 | 357.1 | 365.7
1583 | 1444 | 525.6 | 465 | 493.6 | 460.7 | 425.7 | 425.4 | 410.8 | 391.2 | 357.3 | 365.9
1584 | 1445 | 525.6 | 465.1 | 493.6 | 460.8 | 425.7 | 425.6 | 411 | 391.3 | 357.6 | 366.1
1585 | 1446 | 525.6 | 465.1 | 493.6 | 460.8 | 425.8 | 425.8 | 411.2 | 391.5 | 358 | 366.2
1586 | 1447 | 525.6 | 465.1 | 493.6 | 460.9 | 425.9 | 426 | 411.3 | 391.7 | 358.6 | 366.4
1587 | 1448 | 525.6 | 465.2 | 493.6 | 460.9 | 425.9 | 426.2 | 411.5 | 391.7 | 358.8 | 366.5
1588 | 1449 | 525.6 | 465.2 | 493.6 | 460.9 | 426 | 426.3 | 411.7 | 391.9 | 358.9 | 366.6
1589 | 1450 | 525.6 | 465.3 | 493.6 | 461 | 426.1 | 426.4 | 411.9 | 392 | 359.4 | 366.7
1590 | 1451 | 525.6 | 465.3 | 493.7 | 461 | 426.1 | 426.5 | 412.1 | 392.1 | 359.6 | 366.8
1591 | 1452 | 525.7 | 465.3 | 493.6 | 461.1 | 426.2 | 426.6 | 412.2 | 392.2 | 359.8 | 366.9
1592 | 1453 | 525.7 | 465.4 | 493.7 | 461.1 | 426.3 | 426.7 | 412.4 | 392.4 | 360 | 367.1
1593 | 1454 | 525.8 | 465.4 | 493.7 | 461.2 | 426.4 | 426.8 | 412.6 | 392.6 | 360.4 | 367.3
1594 | 1455 | 525.8 | 465.4 | 493.7 | 461.2 | 426.4 | 426.9 | 412.8 | 392.7 | 360.7 | 367.5
1595 | 1456 | 525.8 | 465.5 | 493.8 | 461.2 | 426.5 | 427 | 413 | 392.9 | 360.9 | 367.7
1596 | 1457 | 525.9 | 465.5 | 493.8 | 461.3 | 426.5 | 427.2 | 413.2 | 393 | 361.4 | 367.8
1597 | 1458 | 525.9 | 465.5 | 493.8 | 461.3 | 426.6 | 427.3 | 413.4 | 393.2 | 361.7 | 367.9
1598 | 1459 | 525.9 | 465.6 | 493.8 | 461.4 | 426.7 | 427.5 | 413.6 | 393.3 | 362.1 | 368
1599 | 1460 | 525.9 | 465.6 | 493.8 | 461.4 | 426.8 | 427.6 | 413.8 | 393.4 | 362.2 | 368.1
1600 | 1461 | 525.9 | 465.7 | 493.8 | 461.5 | 426.9 | 427.8 | 414 | 393.6 | 362.6 | 368.2
1601 | 1462 | 525.9 | 465.7 | 493.9 | 461.5 | 427 | 427.9 | 414.2 | 393.8 | 363 | 368.4
1602 | 1463 | 525.9 | 465.7 | 493.9 | 461.5 | 427.1 | 428.1 | 414.4 | 393.9 | 363.3 | 368.5
1603 | 1464 | 525.9 | 465.8 | 493.9 | 461.6 | 427.2 | 428.3 | 414.6 | 394.1 | 363.4 | 368.7
1604 | 1465 | 526 | 465.8 | 493.9 | 461.6 | 427.3 | 428.4 | 414.8 | 394.2 | 363.7 | 368.9
1605 | 1466 | 525.9 | 465.8 | 494 | 461.7 | 427.4 | 428.6 | 415 | 394.4 | 364 | 368.9
1606 | 1467 | 526 | 465.9 | 494 | 461.7 | 427.6 | 428.7 | 415.2 | 394.6 | 364.3 | 369
1607 | 1468 | 526 | 465.9 | 494 | 461.7 | 427.7 | 428.8 | 415.4 | 394.8 | 364.5 | 369.1
1608 | 1469 | 526 | 466 | 494 | 461.8 | 427.8 | 429 | 415.5 | 394.9 | 364.8 | 369.2
1609 | 1470 | 526 | 466 | 494.1 | 461.8 | 427.9 | 429.1 | 415.7 | 395.1 | 365.1 | 369.4
1610 | 1471 | 526 | 466 | 494.1 | 461.9 | 428 | 429.2 | 415.9 | 395.2 | 365.4 | 369.6
1611 | 1472 | 526 | 466.1 | 494.1 | 461.9 | 428.1 | 429.3 | 416.1 | 395.4 | 365.7 | 369.7
1612 | 1473 | 526 | 466.1 | 494.1 | 462 | 428.2 | 429.4 | 416.3 | 395.5 | 366 | 369.9
1613 | 1474 | 526 | 466.1 | 494.2 | 462 | 428.3 | 429.6 | 416.5 | 395.8 | 366.3 | 369.9
1614 | 1475 | 526 | 466.2 | 494.2 | 462 | 428.5 | 429.7 | 416.7 | 395.9 | 366.7 | 370
1615 | 1476 | 526 | 466.2 | 494.2 | 462.1 | 428.6 | 429.8 | 416.9 | 396 | 366.9 | 370.1
1616 | 1477 | 526 | 466.3 | 494.2 | 462.1 | 428.7 | 430 | 417.1 | 396.2 | 367.2 | 370.2
1617 | 1478 | 526 | 466.3 | 494.2 | 462.2 | 428.9 | 430.1 | 417.3 | 396.3 | 367.3 | 370.4
1618 | 1479 | 526 | 466.3 | 494.3 | 462.2 | 429 | 430.2 | 417.5 | 396.5 | 367.7 | 370.6
1619 | 1480 | 526 | 466.4 | 494.3 | 462.3 | 429.2 | 430.4 | 417.6 | 396.7 | 367.9 | 370.7
1620 | 1481 | 526 | 466.4 | 494.3 | 462.3 | 429.3 | 430.5 | 417.8 | 396.8 | 368.2 | 370.9
1621 | 1482 | 526 | 466.5 | 494.3 | 462.3 | 429.4 | 430.7 | 418 | 396.9 | 368.5 | 371
1622 | 1483 | 526 | 466.5 | 494.3 | 462.4 | 429.6 | 430.8 | 418.2 | 397.1 | 368.9 | 371.1
1623 | 1484 | 526 | 466.5 | 494.3 | 462.4 | 429.7 | 430.9 | 418.4 | 397.3 | 369.2 | 371.3
1624 | 1485 | 526 | 466.6 | 494.4 | 462.5 | 429.8 | 431.1 | 418.6 | 397.5 | 369.5 | 371.4
1625 | 1486 | 526 | 466.6 | 494.4 | 462.5 | 429.9 | 431.2 | 418.7 | 397.7 | 369.8 | 371.4
1626 | 1487 | 526 | 466.6 | 494.5 | 462.5 | 430.1 | 431.3 | 418.9 | 397.9 | 370.3 | 371.5
1627 | 1488 | 526 | 466.7 | 494.5 | 462.6 | 430.2 | 431.5 | 419.1 | 398.1 | 370.6 | 371.5
1628 | 1489 | 526 | 466.7 | 494.5 | 462.6 | 430.3 | 431.6 | 419.3 | 398.2 | 370.8 | 371.6
1629 | 1490 | 526 | 466.7 | 494.5 | 462.7 | 430.5 | 431.7 | 419.5 | 398.4 | 371.1 | 371.8
1630 | 1491 | 526 | 466.8 | 494.6 | 462.7 | 430.6 | 431.9 | 419.7 | 398.6 | 371.3 | 371.9
1631 | 1492 | 526 | 466.8 | 494.6 | 462.7 | 430.7 | 432 | 419.9 | 398.8 | 371.6 | 372.1
1632 | 1493 | 526 | 466.8 | 494.6 | 462.8 | 430.8 | 432.1 | 420.1 | 398.9 | 371.8 | 372.3
1633 | 1494 | 526 | 466.8 | 494.6 | 462.8 | 431 | 432.3 | 420.3 | 399.1 | 372.1 | 372.4
1634 | 1495 | 526.1 | 466.9 | 494.7 | 462.9 | 431.1 | 432.4 | 420.5 | 399.2 | 372.3 | 372.6
1635 | 1496 | 526.1 | 466.9 | 494.7 | 462.9 | 431.2 | 432.6 | 420.7 | 399.4 | 372.6 | 372.7
1636 | 1497 | 526.1 | 467 | 494.7 | 463 | 431.4 | 432.7 | 420.9 | 399.5 | 372.7 | 372.9
1637 | 1498 | 526.1 | 467 | 494.7 | 463 | 431.5 | 432.8 | 421 | 399.7 | 372.9 | 373
1638 | 1499 | 526 | 467 | 494.7 | 463 | 431.6 | 433 | 421.2 | 399.8 | 373.2 | 373.1
1639 | 1500 | 526 | 467.1 | 494.7 | 463.1 | 431.8 | 433.1 | 421.4 | 400 | 373.3 | 373.2
1640 | 1501 | 526 | 467.1 | 494.7 | 463.1 | 431.9 | 433.2 | 421.6 | 400.2 | 373.6 | 373.3
1641 | 1502 | 526 | 467.2 | 494.8 | 463.1 | 432 | 433.3 | 421.8 | 400.4 | 373.8 | 373.5
1642 | 1503 | 526 | 467.2 | 494.8 | 463.2 | 432.2 | 433.5 | 422 | 400.6 | 374.1 | 373.7
1643 | 1504 | 526 | 467.2 | 494.8 | 463.2 | 432.3 | 433.6 | 422.2 | 400.8 | 374.3 | 373.8
1644 | 1505 | 526 | 467.3 | 494.8 | 463.3 | 432.4 | 433.8 | 422.3 | 400.9 | 374.6 | 374
1645 | 1506 | 525.9 | 467.3 | 494.8 | 463.3 | 432.5 | 433.9 | 422.5 | 401 | 374.9 | 374.1
1646 | 1507 | 525.9 | 467.3 | 494.9 | 463.4 | 432.7 | 434.1 | 422.7 | 401.2 | 375.1 | 374.2
1647 | 1508 | 525.9 | 467.3 | 494.9 | 463.4 | 432.8 | 434.2 | 422.8 | 401.4 | 375.3 | 374.4
1648 | 1509 | 525.9 | 467.4 | 494.9 | 463.4 | 432.9 | 434.3 | 423 | 401.6 | 375.5 | 374.5
1649 | 1510 | 525.9 | 467.4 | 494.9 | 463.5 | 433.1 | 434.4 | 423.2 | 401.8 | 375.8 | 374.6
1650 | 1511 | 525.9 | 467.5 | 495 | 463.5 | 433.2 | 434.6 | 423.3 | 401.9 | 376.1 | 374.7
1651 | 1512 | 525.9 | 467.5 | 495 | 463.6 | 433.3 | 434.7 | 423.5 | 402 | 376.3 | 374.9
1652 | 1513 | 525.9 | 467.5 | 495 | 463.6 | 433.4 | 434.9 | 423.6 | 402.2 | 376.6 | 375
1653 | 1514 | 525.9 | 467.6 | 495 | 463.6 | 433.6 | 435.1 | 423.8 | 402.3 | 376.8 | 375.2
1654 | 1515 | 525.9 | 467.6 | 495.1 | 463.7 | 433.7 | 435.2 | 424 | 402.5 | 377 | 375.3
1655 | 1516 | 525.9 | 467.6 | 495.1 | 463.7 | 433.8 | 435.4 | 424.1 | 402.7 | 377.2 | 375.4
1656 | 1517 | 525.9 | 467.7 | 495.1 | 463.8 | 434 | 435.6 | 424.3 | 402.8 | 377.5 | 375.6
1657 | 1518 | 525.9 | 467.7 | 495.1 | 463.8 | 434.1 | 435.7 | 424.4 | 402.9 | 377.7 | 375.7
1658 | 1519 | 525.8 | 467.7 | 495.1 | 463.8 | 434.2 | 435.9 | 424.6 | 403.1 | 377.8 | 375.8
1659 | 1520 | 525.8 | 467.8 | 495.1 | 463.9 | 434.4 | 436.1 | 424.8 | 403.2 | 378.1 | 376
1660 | 1521 | 525.8 | 467.8 | 495.2 | 463.9 | 434.5 | 436.2 | 424.9 | 403.4 | 378.4 | 376.1
1661 | 1522 | 525.8 | 467.8 | 495.2 | 464 | 434.7 | 436.4 | 425.1 | 403.5 | 378.6 | 376.2
1662 | 1523 | 525.8 | 467.8 | 495.2 | 464 | 434.8 | 436.5 | 425.2 | 403.7 | 378.8 | 376.4
1663 | 1524 | 525.8 | 467.9 | 495.2 | 464.1 | 434.9 | 436.4 | 425.4 | 403.9 | 379 | 376.4
1664 | 1525 | 525.8 | 467.9 | 495.3 | 464.1 | 435.1 | 436.3 | 425.6 | 404 | 379.3 | 376.6
1665 | 1526 | 525.8 | 468 | 495.3 | 464.1 | 435.2 | 436.3 | 425.8 | 404.2 | 379.6 | 376.7
1666 | 1527 | 525.8 | 468 | 495.3 | 464.2 | 435.4 | 436.3 | 426 | 404.3 | 379.8 | 376.8
1667 | 1528 | 525.8 | 468 | 495.4 | 464.2 | 435.5 | 436.4 | 426.1 | 404.5 | 380 | 377
1668 | 1529 | 525.8 | 468.1 | 495.4 | 464.2 | 435.6 | 436.5 | 426.3 | 404.6 | 380.2 | 377.1
1669 | 1530 | 525.8 | 468.1 | 495.4 | 464.3 | 435.8 | 436.6 | 426.5 | 404.7 | 380.5 | 377.3
1670 | 1531 | 525.8 | 468.1 | 495.4 | 464.3 | 436 | 436.7 | 426.7 | 404.9 | 380.8 | 377.4
1671 | 1532 | 525.8 | 468.1 | 495.4 | 464.3 | 436.1 | 436.8 | 426.9 | 405.1 | 381 | 377.5
1672 | 1533 | 525.8 | 468.2 | 495.4 | 464.4 | 436.3 | 436.9 | 427.1 | 405.3 | 381.2 | 377.6
1673 | 1534 | 525.8 | 468.2 | 495.5 | 464.4 | 436.4 | 436.9 | 427.4 | 405.5 | 381.4 | 377.7
1674 | 1535 | 525.7 | 468.3 | 495.5 | 464.5 | 436.5 | 437 | 427.6 | 405.7 | 381.6 | 377.8
1675 | 1536 | 525.7 | 468.3 | 495.5 | 464.5 | 436.6 | 437 | 427.9 | 405.9 | 381.9 | 377.9
1676 | 1537 | 525.6 | 468.3 | 495.5 | 464.5 | 436.6 | 437.1 | 428.1 | 406.1 | 382.1 | 378
1677 | 1538 | 525.6 | 468.4 | 495.5 | 464.6 | 436.7 | 437.1 | 428.4 | 406.2 | 382.3 | 378.1
1678 | 1539 | 525.6 | 468.4 | 495.5 | 464.6 | 436.7 | 437.2 | 428.6 | 406.4 | 382.5 | 378.2
1679 | 1540 | 525.6 | 468.4 | 495.5 | 464.6 | 436.8 | 437.2 | 428.9 | 406.6 | 382.8 | 378.3
1680 | 1541 | 525.5 | 468.4 | 495.6 | 464.7 | 436.9 | 437.3 | 429.1 | 406.7 | 383 | 378.4
1681 | 1542 | 525.5 | 468.5 | 495.6 | 464.7 | 437.1 | 437.4 | 429.4 | 406.9 | 383.1 | 378.6
1682 | 1543 | 525.5 | 468.5 | 495.6 | 464.8 | 437.2 | 437.5 | 429.6 | 406.9 | 383.3 | 378.7
1683 | 1544 | 525.4 | 468.6 | 495.6 | 464.8 | 437.3 | 437.5 | 429.9 | 407.1 | 383.5 | 378.8
1684 | 1545 | 525.4 | 468.6 | 495.6 | 464.8 | 437.4 | 437.6 | 430.2 | 407.3 | 383.7 | 378.9
1685 | 1546 | 525.5 | 468.6 | 495.6 | 464.9 | 437.5 | 437.8 | 430.4 | 407.4 | 383.9 | 379.1
1686 | 1547 | 525.4 | 468.7 | 495.6 | 464.9 | 437.6 | 437.9 | 430.7 | 407.6 | 384.1 | 379.2
1687 | 1548 | 525.4 | 468.7 | 495.7 | 464.9 | 437.6 | 438 | 431 | 407.8 | 384.3 | 379.2
1688 | 1549 | 525.4 | 468.7 | 495.7 | 465 | 437.7 | 438.1 | 431.2 | 407.9 | 384.5 | 379.3
1689 | 1550 | 525.4 | 468.8 | 495.7 | 465 | 437.8 | 438.4 | 431.5 | 408 | 384.7 | 379.4
1690 | 1551 | 525.4 | 468.8 | 495.8 | 465.1 | 437.9 | 438.4 | 431.8 | 408.1 | 384.9 | 379.4
1691 | 1552 | 525.4 | 468.8 | 495.8 | 465.1 | 438 | 438.5 | 432 | 408.2 | 385.2 | 379.5
1692 | 1553 | 525.4 | 468.9 | 495.8 | 465.1 | 438 | 438.7 | 432.2 | 408.3 | 385.2 | 379.6
1693 | 1554 | 525.4 | 468.9 | 495.8 | 465.2 | 438.1 | 438.8 | 432.4 | 408.5 | 385.3 | 379.7
1694 | 1555 | 525.5 | 468.9 | 495.8 | 465.2 | 438.1 | 438.8 | 432.7 | 408.6 | 385.6 | 379.9
1695 | 1556 | 525.5 | 469 | 495.8 | 465.2 | 438.2 | 439 | 432.9 | 408.7 | 385.7 | 380
1696 | 1557 | 525.5 | 469 | 495.9 | 465.3 | 438.3 | 439.1 | 433.1 | 408.9 | 385.9 | 380.1
1697 | 1558 | 525.5 | 469 | 495.9 | 465.3 | 438.3 | 439.3 | 433.4 | 409 | 386.1 | 380.2
1698 | 1559 | 525.6 | 469.1 | 496 | 465.3 | 438.4 | 439.4 | 433.6 | 409.1 | 386.3 | 380.3
1699 | 1560 | 525.6 | 469.1 | 496 | 465.4 | 438.5 | 439.5 | 433.8 | 409.4 | 386.4 | 380.4
1700 | 1561 | 525.6 | 469.1 | 496 | 465.4 | 438.5 | 439.6 | 434.1 | 409.6 | 386.6 | 380.5
1701 | 1562 | 525.6 | 469.2 | 496 | 465.4 | 438.5 | 439.8 | 434.3 | 409.8 | 386.8 | 380.6
1702 | 1563 | 525.7 | 469.2 | 496 | 465.5 | 438.4 | 440 | 434.6 | 410 | 387 | 380.7
1703 | 1564 | 525.7 | 469.2 | 496 | 465.5 | 438 | 440.1 | 434.9 | 410.2 | 387.1 | 380.8
1704 | 1565 | 525.7 | 469.2 | 496.1 | 465.5 | 437.7 | 440.1 | 435.1 | 410.3 | 387.2 | 380.8
1705 | 1566 | 525.8 | 469.3 | 496.1 | 465.6 | 437.8 | 440.1 | 435.4 | 410.5 | 387.4 | 380.9
1706 | 1567 | 525.8 | 469.3 | 496.1 | 465.6 | 438 | 440.1 | 435.7 | 410.6 | 387.6 | 381.1
1707 | 1568 | 525.8 | 469.4 | 496.1 | 465.7 | 438 | 440.2 | 435.9 | 410.7 | 387.8 | 381.2
1708 | 1569 | 525.9 | 469.4 | 496.2 | 465.7 | 438.1 | 440.3 | 436.3 | 410.9 | 388 | 381.3
1709 | 1570 | 525.9 | 469.4 | 496.2 | 465.7 | 438.3 | 440.4 | 436.7 | 411 | 388.1 | 381.3
1710 | 1571 | 525.9 | 469.4 | 496.2 | 465.7 | 438.3 | 440.4 | 436.9 | 411.2 | 388.4 | 381.4
1711 | 1572 | 526 | 469.5 | 496.2 | 465.8 | 438.2 | 440.5 | 437.2 | 411.4 | 388.5 | 381.5
1712 | 1573 | 526 | 469.5 | 496.2 | 465.8 | 438.3 | 440.7 | 437.5 | 411.5 | 388.6 | 381.6
1713 | 1574 | 525.9 | 469.5 | 496.3 | 465.8 | 438.4 | 440.7 | 437.8 | 411.6 | 388.8 | 381.7
1714 | 1575 | 525.9 | 469.6 | 496.3 | 465.9 | 438.6 | 440.8 | 438.1 | 411.8 | 389 | 381.8
1715 | 1576 | 525.9 | 469.6 | 496.3 | 465.9 | 438.7 | 440.9 | 438.4 | 411.9 | 389.1 | 382
1716 | 1577 | 525.9 | 469.6 | 496.3 | 466 | 438.8 | 440.9 | 438.7 | 412.1 | 389.3 | 382.1
1717 | 1578 | 525.8 | 469.7 | 496.3 | 466 | 438.8 | 441 | 439 | 412.2 | 389.4 | 382.2
1718 | 1579 | 525.8 | 469.7 | 496.4 | 466 | 438.9 | 441.1 | 439.2 | 412.4 | 389.6 | 382.3
1719 | 1580 | 525.8 | 469.7 | 496.4 | 466.1 | 439 | 441.2 | 439.4 | 412.6 | 389.7 | 382.4
1720 | 1581 | 525.7 | 469.7 | 496.4 | 466.1 | 439 | 441.3 | 439.6 | 412.8 | 389.9 | 382.5
1721 | 1582 | 525.7 | 469.8 | 496.4 | 466.1 | 439.2 | 441.4 | 439.8 | 413 | 390 | 382.6
1722 | 1583 | 525.7 | 469.8 | 496.4 | 466.2 | 439.3 | 441.5 | 440 | 413 | 390.2 | 382.7
1723 | 1584 | 525.7 | 469.9 | 496.4 | 466.2 | 439.5 | 441.6 | 440.2 | 413.2 | 390.4 | 382.7
1724 | 1585 | 525.6 | 469.9 | 496.5 | 466.2 | 439.7 | 441.7 | 440.3 | 413.3 | 390.5 | 382.8
1725 | 1586 | 525.6 | 469.9 | 496.5 | 466.3 | 439.9 | 441.8 | 440.4 | 413.4 | 390.7 | 382.9
1726 | 1587 | 525.6 | 470 | 496.5 | 466.3 | 440 | 441.9 | 440.5 | 413.6 | 390.8 | 383
1727 | 1588 | 525.6 | 470 | 496.5 | 466.4 | 440.2 | 442 | 440.6 | 413.7 | 391 | 383.1
1728 | 1589 | 525.6 | 470 | 496.5 | 466.4 | 440.4 | 442 | 440.7 | 413.8 | 391.1 | 383.2
1729 | 1590 | 525.6 | 470 | 496.6 | 466.4 | 440.5 | 442.1 | 440.8 | 414 | 391.3 | 383.3
1730 | 1591 | 525.6 | 470.1 | 496.6 | 466.5 | 440.7 | 442.1 | 440.9 | 414.2 | 391.4 | 383.4
1731 | 1592 | 525.6 | 470.1 | 496.6 | 466.5 | 440.9 | 442.2 | 441 | 414.4 | 391.6 | 383.6
1732 | 1593 | 525.6 | 470.1 | 496.6 | 466.5 | 441.1 | 442.3 | 441.1 | 414.6 | 391.8 | 383.7
1733 | 1594 | 525.6 | 470.2 | 496.6 | 466.5 | 441.2 | 442.4 | 441.2 | 414.7 | 391.9 | 383.8
1734 | 1595 | 525.6 | 470.2 | 496.6 | 466.6 | 441.1 | 442.5 | 441.3 | 414.9 | 392 | 383.9
1735 | 1596 | 525.5 | 470.2 | 496.7 | 466.6 | 441 | 442.5 | 441.4 | 415 | 392.2 | 384.1
1736 | 1597 | 525.5 | 470.2 | 496.7 | 466.6 | 441 | 442.7 | 441.5 | 415.1 | 392.3 | 384.2
1737 | 1598 | 525.5 | 470.3 | 496.7 | 466.7 | 441.1 | 442.8 | 441.6 | 415.3 | 392.5 | 384.3
1738 | 1599 | 525.5 | 470.3 | 496.7 | 466.7 | 441.1 | 442.9 | 441.7 | 415.4 | 392.7 | 384.4
1739 | 1600 | 525.5 | 470.3 | 496.7 | 466.8 | 441.2 | 443 | 441.8 | 415.6 | 392.8 | 384.5
1740 | 1601 | 525.5 | 470.4 | 496.8 | 466.8 | 441.3 | 443.1 | 441.9 | 415.7 | 393 | 384.6
1741 | 1602 | 525.6 | 470.4 | 496.8 | 466.8 | 441.4 | 443.2 | 442 | 415.8 | 393.1 | 384.7
1742 | 1603 | 525.6 | 470.4 | 496.8 | 466.9 | 441.5 | 443.3 | 442.1 | 416.1 | 393.2 | 384.9
1743 | 1604 | 525.6 | 470.5 | 496.8 | 466.9 | 441.6 | 443.4 | 442.2 | 416.2 | 393.3 | 385
1744 | 1605 | 525.6 | 470.5 | 496.8 | 466.9 | 441.7 | 443.5 | 442.3 | 416.4 | 393.5 | 385.1
1745 | 1606 | 525.6 | 470.5 | 496.9 | 467 | 441.9 | 443.5 | 442.4 | 416.6 | 393.6 | 385.2
1746 | 1607 | 525.6 | 470.6 | 496.8 | 467 | 442 | 443.7 | 442.5 | 416.8 | 393.8 | 385.4
1747 | 1608 | 525.6 | 470.6 | 496.9 | 467 | 442.2 | 443.8 | 442.6 | 417 | 393.9 | 385.5
1748 | 1609 | 525.6 | 470.6 | 496.9 | 467.1 | 442.4 | 443.9 | 442.7 | 417.2 | 394.2 | 385.6
1749 | 1610 | 525.6 | 470.7 | 496.9 | 467.1 | 442.6 | 443.9 | 442.8 | 417.4 | 394.3 | 385.8
1750 | 1611 | 525.6 | 470.7 | 496.9 | 467.1 | 442.7 | 444.1 | 442.9 | 417.7 | 394.3 | 385.9
1751 | 1612 | 525.6 | 470.7 | 496.9 | 467.2 | 442.7 | 444.2 | 443 | 417.9 | 394.4 | 386
1752 | 1613 | 525.6 | 470.7 | 497 | 467.2 | 442.7 | 444.3 | 443 | 418.1 | 394.6 | 386.2
1753 | 1614 | 525.6 | 470.8 | 497 | 467.2 | 442.9 | 444.2 | 443.1 | 418.3 | 394.7 | 386.3
1754 | 1615 | 525.6 | 470.8 | 497.1 | 467.3 | 443 | 444.3 | 443.2 | 418.5 | 394.8 | 386.5
1755 | 1616 | 525.7 | 470.8 | 497.1 | 467.3 | 443 | 444.4 | 443.3 | 418.6 | 394.9 | 386.6
1756 | 1617 | 525.7 | 470.8 | 497.1 | 467.3 | 443.1 | 444.6 | 443.3 | 418.8 | 395 | 386.8
1757 | 1618 | 525.7 | 470.9 | 497.1 | 467.4 | 443.2 | 444.7 | 443.4 | 418.9 | 395.1 | 386.9
1758 | 1619 | 525.7 | 470.9 | 497.1 | 467.4 | 443.2 | 444.8 | 443.4 | 419.1 | 395.2 | 387
1759 | 1620 | 525.7 | 470.9 | 497.1 | 467.4 | 443.3 | 444.8 | 443.5 | 419.2 | 395.4 | 387.1
1760 | 1621 | 525.7 | 471 | 497.2 | 467.5 | 443.4 | 444.8 | 443.5 | 419.4 | 395.5 | 387.3
1761 | 1622 | 525.7 | 471 | 497.2 | 467.5 | 443.4 | 444.9 | 443.6 | 419.6 | 395.6 | 387.5
1762 | 1623 | 525.7 | 471 | 497.2 | 467.5 | 443.4 | 445 | 443.6 | 419.8 | 395.7 | 387.6
1763 | 1624 | 525.7 | 471 | 497.3 | 467.6 | 443.4 | 445.2 | 443.7 | 419.9 | 395.7 | 387.8
1764 | 1625 | 525.7 | 471.1 | 497.3 | 467.6 | 443.4 | 445.4 | 443.8 | 420.1 | 395.9 | 388
1765 | 1626 | 525.7 | 471.1 | 497.3 | 467.6 | 443.4 | 445.4 | 443.8 | 420.3 | 396 | 388.1
1766 | 1627 | 525.7 | 471.1 | 497.2 | 467.6 | 443.6 | 445.4 | 443.8 | 420.5 | 396.1 | 388.3
1767 | 1628 | 525.7 | 471.2 | 497.3 | 467.7 | 443.7 | 445.4 | 443.9 | 420.7 | 396.2 | 388.5
1768 | 1629 | 525.7 | 471.2 | 497.3 | 467.7 | 443.7 | 445.3 | 444 | 420.9 | 396.3 | 388.7
1769 | 1630 | 525.7 | 471.2 | 497.4 | 467.7 | 443.9 | 445.5 | 444 | 421.2 | 396.4 | 388.9
1770 | 1631 | 525.7 | 471.2 | 497.4 | 467.8 | 444.2 | 445.7 | 444.1 | 421.3 | 396.5 | 389.1
1771 | 1632 | 525.7 | 471.3 | 497.4 | 467.8 | 444.3 | 445.8 | 444.2 | 421.5 | 396.6 | 389.2
1772 | 1633 | 525.6 | 471.3 | 497.4 | 467.8 | 444.3 | 445.8 | 444.2 | 421.7 | 396.7 | 389.4
1773 | 1634 | 525.6 | 471.3 | 497.4 | 467.8 | 444.3 | 445.8 | 444.3 | 421.8 | 396.8 | 389.6
1774 | 1635 | 525.6 | 471.4 | 497.4 | 467.9 | 444.3 | 445.8 | 444.4 | 422 | 397 | 389.8
1775 | 1636 | 525.6 | 471.4 | 497.4 | 467.9 | 444.1 | 446 | 444.4 | 422.1 | 397.1 | 389.9
1776 | 1637 | 525.6 | 471.4 | 497.4 | 468 | 444.1 | 446.1 | 444.5 | 422.3 | 397.3 | 390.1
1777 | 1638 | 525.6 | 471.5 | 497.4 | 468 | 444.3 | 446.1 | 444.6 | 422.5 | 397.4 | 390.2
1778 | 1639 | 525.6 | 471.5 | 497.5 | 468 | 444.5 | 446.2 | 444.6 | 422.6 | 397.5 | 390.4
1779 | 1640 | 525.6 | 471.5 | 497.5 | 468 | 444.6 | 446.3 | 444.7 | 422.8 | 397.7 | 390.5
1780 | 1641 | 525.6 | 471.6 | 497.5 | 468.1 | 444.6 | 446.4 | 444.8 | 423 | 397.9 | 390.7
1781 | 1642 | 525.6 | 471.6 | 497.5 | 468.1 | 444.6 | 446.4 | 444.9 | 423.2 | 397.9 | 390.8
1782 | 1643 | 525.6 | 471.6 | 497.5 | 468.1 | 444.7 | 446.4 | 444.9 | 423.3 | 398.1 | 391
1783 | 1644 | 525.6 | 471.6 | 497.6 | 468.2 | 444.9 | 446.6 | 445 | 423.5 | 398.3 | 391.1
1784 | 1645 | 525.6 | 471.7 | 497.6 | 468.2 | 445 | 446.7 | 445.1 | 423.7 | 398.3 | 391.3
1785 | 1646 | 525.6 | 471.7 | 497.6 | 468.2 | 445.1 | 446.7 | 445.2 | 423.9 | 398.4 | 391.4
1786 | 1647 | 525.6 | 471.7 | 497.6 | 468.2 | 445.2 | 446.7 | 445.3 | 424 | 398.6 | 391.6
1787 | 1648 | 525.6 | 471.7 | 497.6 | 468.3 | 445.3 | 446.7 | 445.4 | 424.2 | 398.8 | 391.7
1788 | 1649 | 525.7 | 471.8 | 497.6 | 468.3 | 445.3 | 446.8 | 445.5 | 424.4 | 398.9 | 391.9
1789 | 1650 | 525.7 | 471.8 | 497.6 | 468.3 | 445.4 | 446.9 | 445.5 | 424.5 | 399 | 392
1790 | 1651 | 525.7 | 471.8 | 497.7 | 468.4 | 445.5 | 447.1 | 445.6 | 424.7 | 399.2 | 392.1
1791 | 1652 | 525.7 | 471.9 | 497.7 | 468.4 | 445.7 | 447.1 | 445.7 | 424.9 | 399.4 | 392.2
1792 | 1653 | 525.7 | 471.9 | 497.7 | 468.4 | 445.9 | 447.1 | 445.7 | 425 | 399.5 | 392.4
1793 | 1654 | 525.7 | 471.9 | 497.7 | 468.4 | 446.2 | 447.1 | 445.8 | 425.3 | 399.6 | 392.5
1794 | 1655 | 525.7 | 471.9 | 497.8 | 468.5 | 446.3 | 447.2 | 445.9 | 425.5 | 399.8 | 392.6
1795 | 1656 | 525.7 | 472 | 497.8 | 468.5 | 446.3 | 447.3 | 445.9 | 425.7 | 399.9 | 392.8
1796 | 1657 | 525.7 | 472 | 497.8 | 468.5 | 446.2 | 447.3 | 446 | 425.9 | 400 | 392.9
1797 | 1658 | 525.7 | 472 | 497.8 | 468.6 | 446.2 | 447.3 | 446 | 426.1 | 400.2 | 393
1798 | 1659 | 525.7 | 472 | 497.8 | 468.6 | 446.3 | 447.4 | 446.1 | 426.4 | 400.3 | 393.1
1799 | 1660 | 525.7 | 472.1 | 497.9 | 468.6 | 446.3 | 447.5 | 446.1 | 426.7 | 400.5 | 393.2
1800 | 1661 | 525.7 | 472.1 | 497.9 | 468.7 | 446.3 | 447.7 | 446.2 | 426.9 | 400.7 | 393.3
1801 | 1662 | 525.7 | 472.1 | 497.9 | 468.7 | 446.4 | 447.7 | 446.2 | 427 | 400.8 | 393.4
1802 | 1663 | 525.7 | 472.1 | 497.9 | 468.7 | 446.3 | 447.7 | 446.2 | 427.1 | 401 | 393.6
1803 | 1664 | 525.7 | 472.2 | 497.9 | 468.7 | 446.2 | 447.6 | 446.3 | 427.3 | 401.2 | 393.7
1804 | 1665 | 525.8 | 472.2 | 498 | 468.8 | 446.3 | 447.6 | 446.3 | 427.5 | 401.4 | 393.8
1805 | 1666 | 525.8 | 472.2 | 498 | 468.8 | 446.4 | 447.6 | 446.4 | 427.7 | 401.5 | 393.9
1806 | 1667 | 525.8 | 472.2 | 498 | 468.8 | 446.4 | 447.6 | 446.4 | 427.9 | 401.7 | 394
1807 | 1668 | 525.7 | 472.3 | 498 | 468.9 | 446.6 | 447.7 | 446.5 | 428 | 401.8 | 394.1
1808 | 1669 | 525.7 | 472.3 | 498 | 468.9 | 446.7 | 447.8 | 446.6 | 428.2 | 402 | 394.2
1809 | 1670 | 525.7 | 472.3 | 498 | 468.9 | 446.8 | 447.8 | 446.6 | 428.3 | 402.1 | 394.3
1810 | 1671 | 525.7 | 472.3 | 498.1 | 468.9 | 447 | 448 | 446.7 | 428.5 | 402.3 | 394.4
1811 | 1672 | 525.7 | 472.4 | 498.1 | 469 | 447.1 | 448.1 | 446.7 | 428.7 | 402.4 | 394.5
1812 | 1673 | 525.7 | 472.4 | 498.1 | 469 | 447.2 | 448.2 | 446.8 | 429 | 402.4 | 394.7
1813 | 1674 | 525.6 | 472.4 | 498.1 | 469 | 447.2 | 448.3 | 446.9 | 429.2 | 402.6 | 394.8
1814 | 1675 | 525.6 | 472.4 | 498.1 | 469.1 | 447.3 | 448.4 | 446.9 | 429.4 | 402.7 | 394.9
1815 | 1676 | 525.6 | 472.5 | 498.2 | 469.1 | 447.3 | 448.5 | 447 | 429.6 | 402.8 | 395
1816 | 1677 | 525.6 | 472.5 | 498.2 | 469.1 | 447.2 | 448.6 | 447 | 429.7 | 403 | 395.2
1817 | 1678 | 525.6 | 472.5 | 498.2 | 469.1 | 447.3 | 448.6 | 447.1 | 429.8 | 403.1 | 395.3
1818 | 1679 | 525.6 | 472.6 | 498.2 | 469.2 | 447.4 | 448.7 | 447.1 | 430 | 403.2 | 395.4
1819 | 1680 | 525.6 | 472.6 | 498.2 | 469.2 | 447.5 | 448.8 | 447.2 | 430.2 | 403.4 | 395.6
1820 | 1681 | 525.6 | 472.6 | 498.2 | 469.2 | 447.6 | 448.8 | 447.2 | 430.4 | 403.5 | 395.6
1821 | 1682 | 525.6 | 472.6 | 498.2 | 469.2 | 447.7 | 448.8 | 447.3 | 430.7 | 403.6 | 395.8
1822 | 1683 | 525.6 | 472.7 | 498.3 | 469.3 | 448 | 448.9 | 447.3 | 430.9 | 403.8 | 395.9
1823 | 1684 | 525.6 | 472.7 | 498.3 | 469.3 | 448 | 448.9 | 447.3 | 431 | 403.8 | 396.1
1824 | 1685 | 525.6 | 472.7 | 498.3 | 469.3 | 447.9 | 448.9 | 447.4 | 431.2 | 404 | 396.2
1825 | 1686 | 525.6 | 472.8 | 498.3 | 469.4 | 447.9 | 448.9 | 447.4 | 431.3 | 404.1 | 396.3
1826 | 1687 | 525.6 | 472.8 | 498.3 | 469.4 | 448 | 449 | 447.5 | 431.5 | 404.1 | 396.4
1827 | 1688 | 525.6 | 472.8 | 498.3 | 469.4 | 448.2 | 448.9 | 447.5 | 431.7 | 404.2 | 396.5
1828 | 1689 | 525.6 | 472.8 | 498.4 | 469.5 | 448.3 | 448.9 | 447.6 | 431.9 | 404.4 | 396.7
1829 | 1690 | 525.6 | 472.9 | 498.4 | 469.5 | 448.5 | 448.9 | 447.6 | 432.1 | 404.5 | 396.8
1830 | 1691 | 525.6 | 472.9 | 498.3 | 469.5 | 448.6 | 449 | 447.6 | 432.2 | 404.6 | 396.9
1831 | 1692 | 525.6 | 472.9 | 498.4 | 469.5 | 448.5 | 449 | 447.7 | 432.4 | 404.7 | 397.1
1832 | 1693 | 525.6 | 473 | 498.4 | 469.6 | 448.6 | 449.1 | 447.7 | 432.6 | 404.8 | 397.2
1833 | 1694 | 525.7 | 473 | 498.4 | 469.6 | 448.7 | 449.1 | 447.7 | 432.8 | 405 | 397.3
1834 | 1695 | 525.7 | 473 | 498.4 | 469.6 | 448.7 | 449.2 | 447.7 | 432.9 | 405.1 | 397.4
1835 | 1696 | 525.7 | 473 | 498.5 | 469.6 | 448.9 | 449.2 | 447.8 | 433.1 | 405.2 | 397.5
1836 | 1697 | 525.7 | 473.1 | 498.5 | 469.7 | 449 | 449.3 | 447.8 | 433.2 | 405.3 | 397.6
1837 | 1698 | 525.8 | 473.1 | 498.5 | 469.7 | 449 | 449.3 | 447.8 | 433.4 | 405.4 | 397.7
1838 | 1699 | 525.8 | 473.1 | 498.5 | 469.7 | 449.1 | 449.3 | 447.9 | 433.6 | 405.5 | 397.8
1839 | 1700 | 525.8 | 473.1 | 498.5 | 469.7 | 449.3 | 449.4 | 447.9 | 433.8 | 405.6 | 397.9
1840 | 1701 | 525.8 | 473.1 | 498.6 | 469.8 | 449.4 | 449.4 | 448 | 434 | 405.8 | 398
1841 | 1702 | 525.8 | 473.2 | 498.6 | 469.8 | 449.5 | 449.5 | 448 | 434.2 | 405.9 | 398.1
1842 | 1703 | 525.8 | 473.2 | 498.6 | 469.8 | 449.6 | 449.5 | 448 | 434.4 | 406.1 | 398.2
1843 | 1704 | 525.9 | 473.2 | 498.7 | 469.8 | 449.6 | 449.5 | 448.1 | 434.5 | 406.2 | 398.3
1844 | 1705 | 525.9 | 473.2 | 498.7 | 469.9 | 449.6 | 449.5 | 448.1 | 434.7 | 406.3 | 398.4
1845 | 1706 | 525.9 | 473.2 | 498.7 | 469.9 | 449.6 | 449.6 | 448.2 | 434.9 | 406.4 | 398.6
1846 | 1707 | 525.9 | 473.3 | 498.7 | 469.9 | 449.7 | 449.6 | 448.3 | 435.2 | 406.5 | 398.7
1847 | 1708 | 525.9 | 473.3 | 498.7 | 469.9 | 449.9 | 449.6 | 448.3 | 435.4 | 406.7 | 398.8
1848 | 1709 | 525.9 | 473.3 | 498.7 | 470 | 450.1 | 449.6 | 448.4 | 435.5 | 406.8 | 398.8
1849 | 1710 | 525.9 | 473.4 | 498.7 | 470 | 450.2 | 449.6 | 448.4 | 435.6 | 406.9 | 398.9
1850 | 1711 | 525.9 | 473.4 | 498.7 | 470 | 450.3 | 449.7 | 448.5 | 435.8 | 407.1 | 399
1851 | 1712 | 525.9 | 473.4 | 498.7 | 470.1 | 450.4 | 449.8 | 448.6 | 436 | 407.2 | 399.1
1852 | 1713 | 525.9 | 473.4 | 498.7 | 470.1 | 450.5 | 449.8 | 448.6 | 436.2 | 407.3 | 399.2
1853 | 1714 | 525.9 | 473.5 | 498.7 | 470.1 | 450.6 | 449.9 | 448.7 | 436.4 | 407.5 | 399.2
1854 | 1715 | 525.9 | 473.5 | 498.7 | 470.2 | 450.7 | 450 | 448.8 | 436.6 | 407.6 | 399.3
1855 | 1716 | 525.9 | 473.5 | 498.7 | 470.2 | 450.8 | 450 | 448.8 | 436.8 | 407.7 | 399.4
1856 | 1717 | 525.8 | 473.5 | 498.7 | 470.2 | 450.9 | 450.1 | 448.9 | 436.9 | 407.9 | 399.5
1857 | 1718 | 525.8 | 473.6 | 498.8 | 470.2 | 451.1 | 450.2 | 449 | 437.1 | 408 | 399.6
1858 | 1719 | 525.8 | 473.6 | 498.8 | 470.3 | 451.1 | 450.2 | 449.1 | 437.2 | 408.2 | 399.7
1859 | 1720 | 525.8 | 473.6 | 498.8 | 470.3 | 451.2 | 450.3 | 449.1 | 437.4 | 408.2 | 399.7
1860 | 1721 | 525.9 | 473.6 | 498.9 | 470.3 | 451.2 | 450.3 | 449.2 | 437.5 | 408.4 | 399.8
1861 | 1722 | 525.9 | 473.7 | 498.9 | 470.4 | 451.3 | 450.3 | 449.3 | 437.7 | 408.5 | 399.9
1862 | 1723 | 525.9 | 473.7 | 498.9 | 470.4 | 451.3 | 450.4 | 449.4 | 437.8 | 408.6 | 400
1863 | 1724 | 525.9 | 473.7 | 498.9 | 470.4 | 451.5 | 450.5 | 449.4 | 438.1 | 408.7 | 400.1
1864 | 1725 | 525.9 | 473.7 | 498.9 | 470.4 | 451.5 | 450.5 | 449.5 | 438.2 | 408.9 | 400.3
1865 | 1726 | 525.9 | 473.7 | 498.9 | 470.4 | 451.6 | 450.5 | 449.6 | 438.4 | 408.9 | 400.4
1866 | 1727 | 525.9 | 473.8 | 498.9 | 470.5 | 451.7 | 450.6 | 449.7 | 438.6 | 409.1 | 400.5
1867 | 1728 | 525.8 | 473.8 | 498.9 | 470.5 | 451.8 | 450.6 | 449.7 | 438.8 | 409.2 | 400.6
1868 | 1729 | 525.8 | 473.8 | 498.9 | 470.5 | 451.9 | 450.7 | 449.8 | 438.9 | 409.3 | 400.7
1869 | 1730 | 525.8 | 473.9 | 498.9 | 470.6 | 451.9 | 450.8 | 449.9 | 438.9 | 409.4 | 400.7
1870 | 1731 | 525.8 | 473.9 | 499 | 470.6 | 452 | 450.8 | 450 | 439 | 409.5 | 400.8
1871 | 1732 | 525.8 | 473.9 | 499 | 470.6 | 452.1 | 450.9 | 450.1 | 439.3 | 409.7 | 400.9
1872 | 1733 | 525.7 | 473.9 | 499 | 470.7 | 452.1 | 450.9 | 450.2 | 439.6 | 409.9 | 401
1873 | 1734 | 525.7 | 474 | 499 | 470.7 | 452.2 | 451 | 450.2 | 439.8 | 409.9 | 401
1874 | 1735 | 525.8 | 474 | 499.1 | 470.7 | 452.3 | 451 | 450.3 | 440 | 410.1 | 401.1
1875 | 1736 | 525.8 | 474 | 499.1 | 470.7 | 452.3 | 451 | 450.4 | 440.1 | 410.2 | 401.1
1876 | 1737 | 525.8 | 474 | 499.1 | 470.8 | 452.4 | 451.1 | 450.4 | 440.3 | 410.3 | 401.2
1877 | 1738 | 525.8 | 474 | 499.2 | 470.8 | 452.4 | 451.1 | 450.5 | 440.4 | 410.4 | 401.3
1878 | 1739 | 525.8 | 474.1 | 499.2 | 470.8 | 452.5 | 451.2 | 450.6 | 440.6 | 410.5 | 401.3
1879 | 1740 | 525.8 | 474.1 | 499.2 | 470.8 | 452.5 | 451.2 | 450.6 | 440.8 | 410.6 | 401.4
1880 | 1741 | 525.7 | 474.1 | 499.2 | 470.9 | 452.6 | 451.3 | 450.7 | 441 | 410.7 | 401.5
1881 | 1742 | 525.7 | 474.1 | 499.2 | 470.9 | 452.7 | 451.3 | 450.7 | 441.2 | 410.8 | 401.6
1882 | 1743 | 525.7 | 474.2 | 499.2 | 470.9 | 452.7 | 451.4 | 450.8 | 441.4 | 410.9 | 401.7
1883 | 1744 | 525.6 | 474.2 | 499.2 | 470.9 | 452.8 | 451.4 | 450.9 | 441.6 | 411 | 401.7
1884 | 1745 | 525.6 | 474.2 | 499.2 | 471 | 452.9 | 451.4 | 450.9 | 441.7 | 411 | 401.8
1885 | 1746 | 525.5 | 474.3 | 499.2 | 471 | 453 | 451.5 | 451 | 441.9 | 411.1 | 401.9
1886 | 1747 | 525.5 | 474.3 | 499.2 | 471 | 453 | 451.5 | 451.1 | 442.2 | 411.2 | 402
1887 | 1748 | 525.4 | 474.3 | 499.2 | 471.1 | 453 | 451.6 | 451.1 | 442.3 | 411.3 | 402.1
1888 | 1749 | 525.4 | 474.3 | 499.2 | 471.1 | 453 | 451.6 | 451.2 | 442.5 | 411.4 | 402.1
1889 | 1750 | 525.4 | 474.3 | 499.3 | 471.1 | 453.1 | 451.6 | 451.2 | 442.6 | 411.5 | 402.2
1890 | 1751 | 525.4 | 474.3 | 499.3 | 471.2 | 453.1 | 451.7 | 451.3 | 442.8 | 411.6 | 402.3
1891 | 1752 | 525.3 | 474.4 | 499.3 | 471.2 | 453.2 | 451.7 | 451.4 | 442.9 | 411.7 | 402.3
1892 | 1753 | 525.3 | 474.4 | 499.3 | 471.2 | 453.3 | 451.8 | 451.4 | 443.1 | 411.8 | 402.4
1893 | 1754 | 525.3 | 474.4 | 499.3 | 471.2 | 453.3 | 451.8 | 451.5 | 443.2 | 411.9 | 402.5
1894 | 1755 | 525.3 | 474.5 | 499.3 | 471.3 | 453.4 | 451.9 | 451.6 | 443.3 | 412 | 402.5
1895 | 1756 | 525.3 | 474.5 | 499.3 | 471.3 | 453.4 | 451.9 | 451.6 | 443.4 | 412 | 402.6
1896 | 1757 | 525.4 | 474.5 | 499.3 | 471.3 | 453.5 | 451.9 | 451.7 | 443.4 | 412.1 | 402.7
1897 | 1758 | 525.4 | 474.5 | 499.3 | 471.3 | 453.5 | 452 | 451.8 | 443.5 | 412.3 | 402.7
1898 | 1759 | 525.4 | 474.5 | 499.3 | 471.4 | 453.6 | 452 | 451.9 | 443.6 | 412.3 | 402.8
1899 | 1760 | 525.4 | 474.6 | 499.3 | 471.4 | 453.6 | 452.1 | 451.9 | 443.8 | 412.3 | 402.9
1900 | 1761 | 525.5 | 474.6 | 499.3 | 471.4 | 453.6 | 452.1 | 452 | 443.9 | 412.6 | 403
1901 | 1762 | 525.5 | 474.6 | 499.4 | 471.4 | 453.7 | 452.1 | 452.1 | 444 | 412.5 | 403
1902 | 1763 | 525.5 | 474.6 | 499.4 | 471.5 | 453.7 | 452.2 | 452.2 | 444.1 | 412.6 | 403.1
1903 | 1764 | 525.5 | 474.6 | 499.4 | 471.5 | 453.8 | 452.2 | 452.2 | 444.3 | 412.8 | 403.2
1904 | 1765 | 525.5 | 474.7 | 499.4 | 471.5 | 453.9 | 452.3 | 452.3 | 444.4 | 412.6 | 403.2
1905 | 1766 | 525.5 | 474.7 | 499.4 | 471.5 | 453.9 | 452.3 | 452.4 | 444.5 | 413 | 403.3
1906 | 1767 | 525.5 | 474.7 | 499.4 | 471.6 | 454 | 452.4 | 452.5 | 444.6 | 413.1 | 403.4
1907 | 1768 | 525.6 | 474.7 | 499.4 | 471.6 | 454 | 452.4 | 452.6 | 444.7 | 412.9 | 403.5
1908 | 1769 | 525.6 | 474.8 | 499.4 | 471.6 | 454.1 | 452.5 | 452.6 | 444.7 | 413.2 | 403.5
1909 | 1770 | 525.6 | 474.8 | 499.4 | 471.7 | 454.1 | 452.5 | 452.7 | 444.8 | 413.2 | 403.6
1910 | 1771 | 525.6 | 474.8 | 499.4 | 471.7 | 454.2 | 452.5 | 452.8 | 444.9 | 413.2 | 403.7
1911 | 1772 | 525.6 | 474.8 | 499.4 | 471.7 | 454.3 | 452.6 | 452.9 | 445 | 413.2 | 403.8
1912 | 1773 | 525.7 | 474.8 | 499.5 | 471.7 | 454.3 | 452.7 | 453 | 445.1 | 413.3 | 403.8
1913 | 1774 | 525.7 | 474.9 | 499.5 | 471.7 | 454.3 | 452.7 | 453 | 445.2 | 413.4 | 403.9
1914 | 1775 | 525.7 | 474.9 | 499.5 | 471.8 | 454.4 | 452.7 | 453.1 | 445.3 | 413.7 | 404
1915 | 1776 | 525.7 | 474.9 | 499.5 | 471.8 | 454.4 | 452.8 | 453.1 | 445.5 | 413.5 | 404.1
1916 | 1777 | 525.8 | 474.9 | 499.6 | 471.8 | 454.5 | 452.8 | 453.2 | 445.5 | 413.7 | 404.1
1917 | 1778 | 525.8 | 474.9 | 499.5 | 471.9 | 454.6 | 452.9 | 453.3 | 445.6 | 413.9 | 404.2
1918 | 1779 | 525.8 | 475 | 499.6 | 471.9 | 454.6 | 452.9 | 453.3 | 445.7 | 414 | 404.3
1919 | 1780 | 525.8 | 475 | 499.6 | 471.9 | 454.6 | 452.9 | 453.4 | 445.8 | 414.1 | 404.3
1920 | 1781 | 525.8 | 475 | 499.6 | 471.9 | 454.7 | 453 | 453.4 | 445.9 | 414.2 | 404.4
1921 | 1782 | 525.8 | 475 | 499.6 | 472 | 454.7 | 453 | 453.5 | 446 | 414.3 | 404.4
1922 | 1783 | 525.8 | 475 | 499.6 | 472 | 454.7 | 453 | 453.5 | 446.1 | 414.4 | 404.5
1923 | 1784 | 525.8 | 475.1 | 499.7 | 472 | 454.8 | 453.1 | 453.6 | 446.2 | 414.4 | 404.5
1924 | 1785 | 525.8 | 475.1 | 499.6 | 472 | 454.8 | 453.1 | 453.6 | 446.2 | 414.5 | 404.6
1925 | 1786 | 525.8 | 475.1 | 499.7 | 472 | 454.9 | 453.1 | 453.7 | 446.3 | 414.6 | 404.6
1926 | 1787 | 525.9 | 475.1 | 499.7 | 472.1 | 454.9 | 453.2 | 453.7 | 446.4 | 414.7 | 404.7
1927 | 1788 | 525.9 | 475.1 | 499.8 | 472.1 | 454.9 | 453.2 | 453.8 | 446.5 | 414.8 | 404.7
1928 | 1789 | 525.9 | 475.1 | 499.8 | 472.1 | 455 | 453.2 | 453.8 | 446.6 | 414.9 | 404.8
1929 | 1790 | 525.9 | 475.2 | 499.8 | 472.1 | 455 | 453.3 | 453.9 | 446.7 | 415 | 404.8
1930 | 1791 | 526 | 475.2 | 499.8 | 472.2 | 455 | 453.3 | 453.9 | 446.8 | 415.1 | 404.8
1931 | 1792 | 526 | 475.2 | 499.8 | 472.2 | 455.1 | 453.3 | 454 | 446.9 | 415.2 | 404.9
1932 | 1793 | 526 | 475.2 | 499.8 | 472.2 | 455.2 | 453.4 | 454.1 | 447 | 415.2 | 404.9
1933 | 1794 | 525.9 | 475.2 | 499.8 | 472.3 | 455.2 | 453.4 | 454.1 | 447.2 | 415.3 | 405
1934 | 1795 | 525.9 | 475.2 | 499.9 | 472.3 | 455.2 | 453.5 | 454.2 | 447.3 | 415.4 | 405
1935 | 1796 | 525.9 | 475.3 | 499.9 | 472.3 | 455.3 | 453.5 | 454.3 | 447.4 | 415.3 | 405
1936 | 1797 | 525.9 | 475.3 | 499.9 | 472.3 | 455.3 | 453.5 | 454.3 | 447.5 | 415.4 | 405.1
1937 | 1798 | 525.9 | 475.3 | 499.9 | 472.4 | 455.3 | 453.6 | 454.4 | 447.5 | 415.4 | 405.1
1938 | 1799 | 525.9 | 475.3 | 499.9 | 472.4 | 455.3 | 453.6 | 454.5 | 447.6 | 415.3 | 405.2
1939 | 1800 | 525.9 | 475.3 | 499.8 | 472.4 | 455.4 | 453.7 | 454.6 | 447.7 | 415.8 | 405.2
1940 | 1801 | 525.9 | 475.3 | 499.9 | 472.5 | 455.3 | 453.7 | 454.6 | 447.8 | 415.6 | 405.3
1941 | 1802 | 525.9 | 475.4 | 499.9 | 472.5 | 455.3 | 453.7 | 454.7 | 447.8 | 415.6 | 405.4
1942 | 1803 | 525.9 | 475.4 | 499.9 | 472.5 | 455.3 | 453.8 | 454.8 | 447.8 | 416.1 | 405.4
1943 | 1804 | 525.9 | 475.4 | 499.9 | 472.5 | 455.3 | 453.8 | 454.9 | 447.8 | 415.7 | 405.5
1944 | 1805 | 525.8 | 475.5 | 499.9 | 472.6 | 455.3 | 453.9 | 454.9 | 447.8 | 416 | 405.5
1945 | 1806 | 525.8 | 475.5 | 499.9 | 472.6 | 455.3 | 453.9 | 455 | 447.9 | 416.3 | 405.6
1946 | 1807 | 525.8 | 475.5 | 499.9 | 472.6 | 455.3 | 454 | 455.1 | 448 | 415.8 | 405.6
1947 | 1808 | 525.8 | 475.5 | 499.9 | 472.7 | 455.3 | 454 | 455.2 | 448.1 | 416.5 | 405.7
1948 | 1809 | 525.7 | 475.5 | 499.9 | 472.7 | 455.3 | 454.1 | 455.3 | 448.2 | 416.5 | 405.7
1949 | 1810 | 525.7 | 475.5 | 499.9 | 472.7 | 455.3 | 454.1 | 455.4 | 448.3 | 416.1 | 405.8
1950 | 1811 | 525.7 | 475.6 | 500 | 472.7 | 455.4 | 454.2 | 455.4 | 448.4 | 416.8 | 405.9
1951 | 1812 | 525.6 | 475.6 | 500 | 472.8 | 455.5 | 454.2 | 455.5 | 448.5 | 416.7 | 406
1952 | 1813 | 525.6 | 475.6 | 500 | 472.8 | 455.5 | 454.2 | 455.6 | 448.6 | 416.5 | 406
1953 | 1814 | 525.6 | 475.6 | 500 | 472.8 | 455.5 | 454.3 | 455.7 | 448.7 | 416.4 | 406.1
1954 | 1815 | 525.6 | 475.7 | 500 | 472.9 | 455.5 | 454.3 | 455.8 | 448.7 | 416.7 | 406.2
1955 | 1816 | 525.6 | 475.7 | 500 | 472.9 | 455.5 | 454.4 | 455.8 | 448.8 | 417 | 406.2
1956 | 1817 | 525.6 | 475.7 | 500 | 472.9 | 455.6 | 454.4 | 455.9 | 448.9 | 417.3 | 406.3
1957 | 1818 | 525.6 | 475.7 | 500 | 472.9 | 455.6 | 454.4 | 456 | 448.9 | 417 | 406.4
1958 | 1819 | 525.6 | 475.7 | 500.1 | 473 | 455.7 | 454.5 | 456.1 | 449 | 417.2 | 406.4
1959 | 1820 | 525.6 | 475.7 | 500 | 473 | 455.7 | 454.5 | 456.1 | 449.1 | 417.6 | 406.4
1960 | 1821 | 525.6 | 475.7 | 500.1 | 473 | 455.8 | 454.6 | 456.2 | 449.2 | 417.6 | 406.5
1961 | 1822 | 525.6 | 475.8 | 500 | 473 | 455.8 | 454.6 | 456.3 | 449.2 | 417.7 | 406.5
1962 | 1823 | 525.6 | 475.8 | 500 | 473.1 | 455.9 | 454.6 | 456.3 | 449.3 | 417.8 | 406.6
1963 | 1824 | 525.6 | 475.8 | 500 | 473.1 | 455.9 | 454.7 | 456.4 | 449.3 | 417.8 | 406.7
1964 | 1825 | 525.6 | 475.8 | 500 | 473.1 | 455.9 | 454.7 | 456.4 | 449.4 | 417.9 | 406.7
1965 | 1826 | 525.6 | 475.8 | 500 | 473.2 | 455.9 | 454.7 | 456.5 | 449.4 | 417.9 | 406.8
1966 | 1827 | 525.6 | 475.8 | 500.1 | 473.2 | 455.9 | 454.8 | 456.6 | 449.5 | 418 | 406.9
1967 | 1828 | 525.6 | 475.9 | 500.1 | 473.2 | 455.9 | 454.8 | 456.6 | 449.6 | 418 | 406.9
1968 | 1829 | 525.6 | 475.9 | 500.1 | 473.2 | 455.9 | 454.8 | 456.7 | 449.6 | 418.1 | 406.9
1969 | 1830 | 525.7 | 475.9 | 500.1 | 473.3 | 456 | 454.9 | 456.7 | 449.6 | 418.2 | 407
1970 | 1831 | 525.6 | 475.9 | 500.1 | 473.3 | 456 | 454.9 | 456.8 | 449.7 | 418.2 | 407
1971 | 1832 | 525.6 | 475.9 | 500.1 | 473.3 | 456.1 | 455 | 456.8 | 449.7 | 418.3 | 407.1
1972 | 1833 | 525.7 | 476 | 500.1 | 473.3 | 456.1 | 455 | 456.9 | 449.8 | 418.4 | 407.1
1973 | 1834 | 525.7 | 476 | 500.1 | 473.4 | 456.1 | 455 | 456.9 | 449.9 | 418.5 | 407.2
1974 | 1835 | 525.7 | 476 | 500.2 | 473.4 | 456.1 | 455.1 | 457 | 450 | 418.6 | 407.2
1975 | 1836 | 525.7 | 476 | 500.2 | 473.4 | 456.1 | 455.1 | 457 | 450 | 418.6 | 407.2
1976 | 1837 | 525.7 | 476 | 500.2 | 473.4 | 456.1 | 455.1 | 457.1 | 450.1 | 418.7 | 407.3
1977 | 1838 | 525.7 | 476 | 500.2 | 473.5 | 456.1 | 455.2 | 457.1 | 450.2 | 418.5 | 407.3
1978 | 1839 | 525.7 | 476 | 500.3 | 473.5 | 456.1 | 455.2 | 457.2 | 450.2 | 418.6 | 407.3
1979 | 1840 | 525.7 | 476.1 | 500.3 | 473.5 | 456.1 | 455.2 | 457.3 | 450.3 | 418.5 | 407.4
1980 | 1841 | 525.7 | 476.1 | 500.3 | 473.6 | 456.1 | 455.3 | 457.4 | 450.4 | 418.3 | 407.4
1981 | 1842 | 525.7 | 476.1 | 500.3 | 473.6 | 456.1 | 455.3 | 457.4 | 450.5 | 419.1 | 407.5
1982 | 1843 | 525.7 | 476.1 | 500.2 | 473.6 | 456.1 | 455.3 | 457.5 | 450.5 | 418.7 | 407.5
1983 | 1844 | 525.7 | 476.1 | 500.3 | 473.6 | 456.1 | 455.4 | 457.6 | 450.6 | 418.8 | 407.5
1984 | 1845 | 525.7 | 476.2 | 500.3 | 473.7 | 456.1 | 455.4 | 457.7 | 450.6 | 419.4 | 407.6
1985 | 1846 | 525.7 | 476.2 | 500.3 | 473.7 | 456.2 | 455.5 | 457.7 | 450.6 | 418.7 | 407.6
1986 | 1847 | 525.7 | 476.2 | 500.3 | 473.7 | 456.2 | 455.5 | 457.8 | 450.7 | 419.4 | 407.6
1987 | 1848 | 525.7 | 476.2 | 500.3 | 473.8 | 456.3 | 455.5 | 457.9 | 450.8 | 419.7 | 407.7
1988 | 1849 | 525.7 | 476.2 | 500.4 | 473.8 | 456.3 | 455.6 | 458 | 450.9 | 418.8 | 407.7
1989 | 1850 | 525.7 | 476.3 | 500.3 | 473.8 | 456.4 | 455.6 | 458 | 451 | 419.8 | 407.8
1990 | 1851 | 525.7 | 476.3 | 500.3 | 473.8 | 456.4 | 455.6 | 458.1 | 451.1 | 419.9 | 407.8
1991 | 1852 | 525.7 | 476.3 | 500.3 | 473.8 | 456.4 | 455.7 | 458.2 | 451.2 | 419.1 | 407.9
1992 | 1853 | 525.7 | 476.3 | 500.4 | 473.9 | 456.4 | 455.7 | 458.3 | 451.3 | 420.2 | 407.9
1993 | 1854 | 525.8 | 476.4 | 500.4 | 473.9 | 456.4 | 455.8 | 458.3 | 451.3 | 419.7 | 407.9
1994 | 1855 | 525.8 | 476.3 | 500.4 | 473.9 | 456.4 | 455.8 | 458.4 | 451.5 | 419.5 | 408
1995 | 1856 | 525.8 | 476.4 | 500.4 | 474 | 456.5 | 455.8 | 458.5 | 451.6 | 419.2 | 408.1
1996 | 1857 | 525.8 | 476.4 | 500.5 | 474 | 456.5 | 455.9 | 458.6 | 451.7 | 419.6 | 408.1
1997 | 1858 | 525.8 | 476.4 | 500.5 | 474 | 456.6 | 455.9 | 458.7 | 451.7 | 420 | 408.2
1998 | 1859 | 525.8 | 476.4 | 500.5 | 474 | 456.6 | 456 | 458.8 | 451.8 | 420.8 | 408.2
1999 | 1860 | 525.8 | 476.4 | 500.5 | 474.1 | 456.7 | 456 | 458.8 | 451.9 | 419.6 | 408.3
2000 | 1861 | 525.8 | 476.5 | 500.5 | 474.1 | 456.8 | 456.1 | 458.9 | 452 | 420.5 | 408.3
2001 | 1862 | 525.9 | 476.5 | 500.5 | 474.1 | 456.8 | 456.1 | 459 | 452 | 421.1 | 408.4
2002 | 1863 | 525.9 | 476.5 | 500.5 | 474.1 | 456.8 | 456.1 | 459 | 452 | 421.1 | 408.4
2003 | 1864 | 525.9 | 476.5 | 500.5 | 474.2 | 456.8 | 456.2 | 459.1 | 452 | 421.2 | 408.5
2004 | 1865 | 525.9 | 476.5 | 500.5 | 474.2 | 456.8 | 456.2 | 459.1 | 452.1 | 421.3 | 408.5
2005 | 1866 | 525.9 | 476.6 | 500.5 | 474.2 | 456.8 | 456.3 | 459.1 | 452.1 | 421.3 | 408.6
2006 | 1867 | 525.9 | 476.6 | 500.6 | 474.2 | 456.9 | 456.3 | 459.2 | 452.2 | 421.4 | 408.6
2007 | 1868 | 526 | 476.6 | 500.6 | 474.3 | 456.9 | 456.3 | 459.2 | 452.2 | 421.4 | 408.7
2008 | 1869 | 526 | 476.6 | 500.6 | 474.3 | 456.9 | 456.3 | 459.2 | 452.3 | 421.5 | 408.7
2009 | 1870 | 526 | 476.6 | 500.6 | 474.3 | 456.9 | 456.4 | 459.3 | 452.3 | 421.5 | 408.8
2010 | 1871 | 526 | 476.6 | 500.6 | 474.3 | 457 | 456.4 | 459.3 | 452.4 | 421.5 | 408.8
2011 | 1872 | 526 | 476.6 | 500.6 | 474.3 | 457 | 456.4 | 459.3 | 452.5 | 421.5 | 408.9
2012 | 1873 | 526 | 476.7 | 500.7 | 474.4 | 457 | 456.5 | 459.4 | 452.5 | 421.5 | 408.9
2013 | 1874 | 526 | 476.7 | 500.7 | 474.4 | 457 | 456.5 | 459.4 | 452.5 | 421.6 | 409
2014 | 1875 | 526 | 476.7 | 500.7 | 474.4 | 457.1 | 456.5 | 459.4 | 452.5 | 421.6 | 409.1
2015 | 1876 | 526 | 476.7 | 500.7 | 474.4 | 457.1 | 456.6 | 459.5 | 452.5 | 421.6 | 409.1
2016 | 1877 | 526 | 476.7 | 500.7 | 474.5 | 457.2 | 456.6 | 459.5 | 452.5 | 421.7 | 409.2
2017 | 1878 | 526 | 476.7 | 500.8 | 474.5 | 457.2 | 456.6 | 459.5 | 452.6 | 421.7 | 409.2
2018 | 1879 | 526 | 476.7 | 500.8 | 474.5 | 457.2 | 456.7 | 459.6 | 452.6 | 421.8 | 409.3
2019 | 1880 | 526 | 476.8 | 500.8 | 474.5 | 457.2 | 456.7 | 459.6 | 452.7 | 421.4 | 409.4
2020 | 1881 | 525.9 | 476.8 | 500.8 | 474.6 | 457.3 | 456.7 | 459.6 | 452.9 | 421.3 | 409.4
2021 | 1882 | 525.9 | 476.8 | 500.8 | 474.6 | 457.3 | 456.8 | 459.7 | 453 | 421.4 | 409.5
2022 | 1883 | 525.8 | 476.8 | 500.8 | 474.6 | 457.3 | 456.8 | 459.8 | 453.3 | 420.8 | 409.6
2023 | 1884 | 525.8 | 476.8 | 500.8 | 474.6 | 457.4 | 456.8 | 459.8 | 453.4 | 421.9 | 409.6
2024 | 1885 | 525.8 | 476.8 | 500.8 | 474.6 | 457.4 | 456.9 | 459.9 | 453.4 | 421.1 | 409.7
2025 | 1886 | 525.8 | 476.8 | 500.8 | 474.7 | 457.4 | 456.9 | 459.9 | 453.8 | 421.2 | 409.7
2026 | 1887 | 525.8 | 476.9 | 500.8 | 474.7 | 457.5 | 457 | 460 | 453.8 | 421.9 | 409.8
2027 | 1888 | 525.7 | 476.9 | 500.8 | 474.7 | 457.5 | 457 | 460.1 | 453.8 | 420.6 | 409.9
2028 | 1889 | 525.6 | 476.9 | 500.8 | 474.7 | 457.6 | 457 | 460.1 | 454.1 | 421.6 | 409.9
2029 | 1890 | 525.6 | 477 | 500.8 | 474.8 | 457.6 | 457.1 | 460.2 | 454.1 | 421.8 | 410
2030 | 1891 | 525.5 | 477 | 500.8 | 474.8 | 457.6 | 457.1 | 460.3 | 454.2 | 420.3 | 410.1
2031 | 1892 | 525.5 | 477 | 500.9 | 474.8 | 457.6 | 457.2 | 460.4 | 454.6 | 421.8 | 410.2
2032 | 1893 | 525.5 | 477 | 500.9 | 474.8 | 457.7 | 457.2 | 460.4 | 454.5 | 421.8 | 410.2
2033 | 1894 | 525.5 | 477 | 500.8 | 474.9 | 457.7 | 457.2 | 460.5 | 454.7 | 420.2 | 410.3
2034 | 1895 | 525.5 | 477 | 500.9 | 474.9 | 457.8 | 457.3 | 460.5 | 455 | 421.8 | 410.4
2035 | 1896 | 525.5 | 477 | 500.9 | 474.9 | 457.9 | 457.3 | 460.6 | 454.9 | 421.3 | 410.4
2036 | 1897 | 525.4 | 477.1 | 500.9 | 474.9 | 457.9 | 457.3 | 460.6 | 455.2 | 420.4 | 410.5
2037 | 1898 | 525.4 | 477.1 | 500.9 | 474.9 | 457.9 | 457.4 | 460.7 | 455.6 | 420 | 410.6
2038 | 1899 | 525.4 | 477.1 | 500.9 | 475 | 458 | 457.4 | 460.8 | 455.9 | 420.7 | 410.7
2039 | 1900 | 525.4 | 477.1 | 500.9 | 475 | 458.1 | 457.4 | 460.9 | 456.2 | 420.8 | 410.7
2040 | 1901 | 525.4 | 477.1 | 500.9 | 475 | 458.1 | 457.5 | 461 | 456 | 421.6 | 410.8
2041 | 1902 | 525.4 | 477.1 | 500.9 | 475 | 458.1 | 457.5 | 461 | 455.9 | 420.2 | 410.9
2042 | 1903 | 525.4 | 477.2 | 501 | 475 | 458.2 | 457.6 | 461.1 | 456.3 | 421.1 | 411
2043 | 1904 | 525.4 | 477.2 | 501 | 475.1 | 458.2 | 457.6 | 461.2 | 456.1 | 421.5 | 411
2044 | 1905 | 525.5 | 477.2 | 501 | 475.1 | 458.2 | 457.6 | 461.2 | 455.9 | 421.4 | 411.1
2045 | 1906 | 525.5 | 477.2 | 501 | 475.1 | 458.3 | 457.6 | 461.3 | 455.6 | 421.4 | 411.2
2046 | 1907 | 525.5 | 477.2 | 501 | 475.1 | 458.3 | 457.7 | 461.3 | 455.5 | 421.5 | 411.3
2047 | 1908 | 525.5 | 477.3 | 501 | 475.1 | 458.4 | 457.7 | 461.3 | 455.4 | 421.5 | 411.3
2048 | 1909 | 525.5 | 477.3 | 501 | 475.1 | 458.4 | 457.8 | 461.4 | 455.3 | 421.6 | 411.4
2049 | 1910 | 525.5 | 477.3 | 501 | 475.2 | 458.4 | 457.8 | 461.4 | 455.2 | 421.6 | 411.4
2050 | 1911 | 525.6 | 477.3 | 501 | 475.2 | 458.4 | 457.9 | 461.4 | 455.2 | 421.6 | 411.5
2051 | 1912 | 525.6 | 477.4 | 501 | 475.2 | 458.5 | 457.9 | 461.4 | 455.1 | 421.6 | 411.5
2052 | 1913 | 525.6 | 477.4 | 501 | 475.2 | 458.5 | 457.9 | 461.5 | 455 | 421.5 | 411.6
2053 | 1914 | 525.7 | 477.4 | 501.1 | 475.3 | 458.5 | 458 | 461.5 | 455 | 421.5 | 411.7
2054 | 1915 | 525.7 | 477.4 | 501.1 | 475.3 | 458.5 | 458 | 461.5 | 455 | 421.5 | 411.7
2055 | 1916 | 525.7 | 477.4 | 501.1 | 475.3 | 458.6 | 458 | 461.6 | 455 | 421.5 | 411.8
2056 | 1917 | 525.8 | 477.4 | 501.1 | 475.3 | 458.6 | 458.1 | 461.6 | 455 | 421.6 | 411.9
2057 | 1918 | 525.8 | 477.4 | 501.2 | 475.3 | 458.7 | 458.1 | 461.6 | 455.1 | 421.6 | 411.9
2058 | 1919 | 525.8 | 477.5 | 501.1 | 475.4 | 458.8 | 458.2 | 461.6 | 455.1 | 421.6 | 412
2059 | 1920 | 525.9 | 477.5 | 501.1 | 475.4 | 458.8 | 458.2 | 461.7 | 455.1 | 421.7 | 412
2060 | 1921 | 525.9 | 477.5 | 501.2 | 475.4 | 458.8 | 458.2 | 461.7 | 455.1 | 421.5 | 412.1
2061 | 1922 | 525.9 | 477.5 | 501.2 | 475.4 | 458.9 | 458.3 | 461.7 | 455.4 | 420.9 | 412.1
2062 | 1923 | 526 | 477.5 | 501.2 | 475.4 | 458.9 | 458.3 | 461.7 | 455.7 | 420.9 | 412.2
2063 | 1924 | 526 | 477.5 | 501.2 | 475.4 | 458.9 | 458.3 | 461.8 | 456 | 420.9 | 412.3
2064 | 1925 | 526 | 477.5 | 501.3 | 475.5 | 459 | 458.4 | 461.9 | 456.9 | 420.3 | 412.3
2065 | 1926 | 526 | 477.5 | 501.3 | 475.5 | 459.1 | 458.4 | 461.9 | 457.2 | 421.9 | 412.4
2066 | 1927 | 526 | 477.5 | 501.3 | 475.5 | 459.1 | 458.4 | 462 | 457 | 420.6 | 412.5
2067 | 1928 | 526 | 477.6 | 501.3 | 475.5 | 459.1 | 458.5 | 462 | 457.8 | 421 | 412.6
2068 | 1929 | 526 | 477.6 | 501.4 | 475.5 | 459.2 | 458.5 | 462.1 | 457.7 | 422 | 412.6
2069 | 1930 | 525.9 | 477.6 | 501.4 | 475.5 | 459.2 | 458.5 | 462.2 | 457.7 | 420.3 | 412.7
2070 | 1931 | 525.9 | 477.6 | 501.4 | 475.6 | 459.3 | 458.6 | 462.3 | 458.5 | 421.7 | 412.8
2071 | 1932 | 525.8 | 477.6 | 501.4 | 475.6 | 459.4 | 458.6 | 462.3 | 458.2 | 422.1 | 412.8
2072 | 1933 | 525.8 | 477.6 | 501.4 | 475.6 | 459.4 | 458.6 | 462.4 | 458.3 | 420.1 | 412.9
2073 | 1934 | 525.7 | 477.6 | 501.4 | 475.6 | 459.5 | 458.7 | 462.4 | 459 | 422.1 | 413
2074 | 1935 | 525.7 | 477.6 | 501.4 | 475.7 | 459.5 | 458.7 | 462.5 | 458.6 | 422.3 | 413
2075 | 1936 | 525.7 | 477.7 | 501.4 | 475.7 | 459.6 | 458.8 | 462.6 | 459.1 | 420.2 | 413.1
2076 | 1937 | 525.6 | 477.7 | 501.4 | 475.7 | 459.7 | 458.8 | 462.6 | 459.5 | 422.4 | 413.2
2077 | 1938 | 525.5 | 477.7 | 501.4 | 475.7 | 459.7 | 458.9 | 462.7 | 459 | 421.8 | 413.2
2078 | 1939 | 525.5 | 477.7 | 501.4 | 475.8 | 459.8 | 458.9 | 462.8 | 459.7 | 420.9 | 413.3
2079 | 1940 | 525.4 | 477.7 | 501.4 | 475.8 | 459.9 | 459 | 462.8 | 460.3 | 419.5 | 413.4
2080 | 1941 | 525.4 | 477.8 | 501.4 | 475.8 | 459.9 | 459 | 462.9 | 461 | 421.3 | 413.4
2081 | 1942 | 525.3 | 477.8 | 501.4 | 475.8 | 459.9 | 459 | 463 | 461.8 | 421.6 | 413.5
2082 | 1943 | 525.2 | 477.8 | 501.3 | 475.9 | 460.1 | 459.1 | 463.1 | 461.4 | 422.7 | 413.6
2083 | 1944 | 525.2 | 477.8 | 501.4 | 475.8 | 460.1 | 459.1 | 463.2 | 461 | 420.6 | 413.7
2084 | 1945 | 525.1 | 477.8 | 501.5 | 475.8 | 460.2 | 459.2 | 463.2 | 461.8 | 422.4 | 413.7
2085 | 1946 | 525.1 | 477.9 | 501.5 | 475.9 | 460.3 | 459.2 | 463.3 | 461.1 | 422.9 | 413.8
2086 | 1947 | 525.1 | 477.9 | 501.5 | 475.9 | 460.3 | 459.3 | 463.3 | 460.4 | 422.9 | 413.8
2087 | 1948 | 525.1 | 477.9 | 501.5 | 475.9 | 460.4 | 459.3 | 463.4 | 459.9 | 423 | 413.9
2088 | 1949 | 525.1 | 477.9 | 501.5 | 475.9 | 460.4 | 459.3 | 463.4 | 459.6 | 423 | 413.9
2089 | 1950 | 525.1 | 477.9 | 501.5 | 476 | 460.5 | 459.4 | 463.4 | 459.4 | 423 | 414
2090 | 1951 | 525.1 | 477.9 | 501.5 | 476 | 460.6 | 459.4 | 463.4 | 459.1 | 423.1 | 414.1
2091 | 1952 | 525.1 | 478 | 501.5 | 476 | 460.6 | 459.5 | 463.4 | 458.9 | 423.1 | 414.2
2092 | 1953 | 525.1 | 478 | 501.5 | 476 | 460.7 | 459.5 | 463.4 | 458.7 | 423.2 | 414.3
2093 | 1954 | 525.2 | 478 | 501.5 | 476 | 460.7 | 459.5 | 463.5 | 458.5 | 423.2 | 414.4
2094 | 1955 | 525.2 | 478 | 501.5 | 476 | 460.8 | 459.6 | 463.5 | 458.4 | 423.3 | 414.4
2095 | 1956 | 525.3 | 478 | 501.5 | 476.1 | 460.8 | 459.6 | 463.5 | 458.4 | 423.4 | 414.5
2096 | 1957 | 525.3 | 478.1 | 501.5 | 476.1 | 460.9 | 459.6 | 463.5 | 458.3 | 423.4 | 414.6
2097 | 1958 | 525.4 | 478.1 | 501.5 | 476.1 | 460.9 | 459.7 | 463.5 | 458.2 | 423.4 | 414.7
2098 | 1959 | 525.4 | 478.1 | 501.6 | 476.1 | 460.9 | 459.7 | 463.5 | 458.2 | 423.5 | 414.8
2099 | 1960 | 525.5 | 478.1 | 501.6 | 476.1 | 460.9 | 459.7 | 463.5 | 458.2 | 423.5 | 414.9
2100 | 1961 | 525.5 | 478.1 | 501.6 | 476.1 | 461 | 459.7 | 463.5 | 458.2 | 423.5 | 415
2101 | 1962 | 525.6 | 478.1 | 501.6 | 476.1 | 461 | 459.8 | 463.6 | 458.1 | 423.6 | 415.1
2102 | 1963 | 525.6 | 478.1 | 501.6 | 476.2 | 461 | 459.8 | 463.6 | 458.2 | 423.5 | 415.2
2103 | 1964 | 525.7 | 478.1 | 501.6 | 476.2 | 461.1 | 459.8 | 463.6 | 458.5 | 422.9 | 415.3
2104 | 1965 | 525.7 | 478.1 | 501.6 | 476.2 | 461.1 | 459.9 | 463.6 | 459 | 422.8 | 415.4
2105 | 1966 | 525.7 | 478.2 | 501.6 | 476.2 | 461.1 | 459.9 | 463.6 | 459.4 | 422.8 | 415.5
2106 | 1967 | 525.7 | 478.2 | 501.7 | 476.2 | 461.2 | 459.9 | 463.7 | 461 | 422 | 415.5
2107 | 1968 | 525.7 | 478.2 | 501.7 | 476.3 | 461.2 | 460 | 463.7 | 461.4 | 424.1 | 415.6
2108 | 1969 | 525.7 | 478.2 | 501.7 | 476.3 | 461.2 | 460 | 463.8 | 461.1 | 422.7 | 415.7
2109 | 1970 | 525.7 | 478.2 | 501.8 | 476.3 | 461.2 | 460 | 463.8 | 462.6 | 422.7 | 415.8
2110 | 1971 | 525.7 | 478.2 | 501.8 | 476.3 | 461.3 | 460.1 | 463.9 | 462.5 | 424.4 | 415.9
2111 | 1972 | 525.7 | 478.3 | 501.6 | 476.3 | 461.4 | 460.1 | 463.9 | 462.3 | 420.7 | 416
2112 | 1973 | 525.7 | 478.3 | 501.6 | 476.4 | 461.5 | 460.2 | 463.9 | 463.9 | 424.2 | 416
2113 | 1974 | 525.7 | 478.3 | 501.6 | 476.4 | 461.5 | 460.2 | 464 | 463.3 | 424.8 | 416.1
2114 | 1975 | 525.7 | 478.4 | 501.7 | 476.4 | 461.6 | 460.3 | 464 | 463.5 | 419.9 | 416.2
2115 | 1976 | 525.7 | 478.3 | 501.7 | 476.4 | 461.6 | 460.3 | 464.1 | 464.7 | 424.8 | 416.3
2116 | 1977 | 525.6 | 478.3 | 501.7 | 476.4 | 461.6 | 460.3 | 464.1 | 463.8 | 423.9 | 416.4
2117 | 1978 | 525.6 | 478.4 | 501.7 | 476.5 | 461.7 | 460.4 | 464.2 | 464.5 | 421.2 | 416.4
2118 | 1979 | 525.6 | 478.4 | 501.7 | 476.5 | 461.7 | 460.4 | 464.3 | 465.2 | 425.2 | 416.5
2119 | 1980 | 525.6 | 478.4 | 501.7 | 476.5 | 461.7 | 460.4 | 464.3 | 464.4 | 423.1 | 416.6
2120 | 1981 | 525.6 | 478.4 | 501.8 | 476.5 | 461.7 | 460.4 | 464.4 | 465.7 | 421.8 | 416.7
2121 | 1982 | 525.6 | 478.4 | 501.7 | 476.5 | 461.8 | 460.5 | 464.4 | 466.9 | 421.5 | 416.7
2122 | 1983 | 525.6 | 478.4 | 501.8 | 476.5 | 461.8 | 460.5 | 464.5 | 468.3 | 422 | 416.8
2123 | 1984 | 525.6 | 478.4 | 501.8 | 476.5 | 461.9 | 460.6 | 464.6 | 469.5 | 423 | 416.9
2124 | 1985 | 525.6 | 478.5 | 501.7 | 476.6 | 462 | 460.7 | 464.7 | 468.5 | 425.5 | 416.9
2125 | 1986 | 525.7 | 478.5 | 501.8 | 476.6 | 462 | 460.7 | 464.7 | 467.7 | 421.4 | 417
2126 | 1987 | 525.7 | 478.5 | 501.8 | 476.6 | 462 | 460.7 | 464.8 | 469.2 | 424.1 | 417.1
2127 | 1988 | 525.7 | 478.5 | 501.8 | 476.6 | 462 | 460.7 | 464.8 | 468 | 425.7 | 417.2
2128 | 1989 | 525.7 | 478.6 | 501.8 | 476.6 | 462.1 | 460.8 | 464.8 | 466.7 | 425.7 | 417.2
2129 | 1990 | 525.7 | 478.5 | 501.9 | 476.6 | 462.1 | 460.8 | 464.9 | 465.7 | 425.8 | 417.3
2130 | 1991 | 525.7 | 478.5 | 501.9 | 476.7 | 462.1 | 460.8 | 464.9 | 464.9 | 425.9 | 417.4
2131 | 1992 | 525.7 | 478.6 | 501.8 | 476.7 | 462.2 | 460.9 | 464.9 | 464.2 | 425.9 | 417.4
2132 | 1993 | 525.7 | 478.6 | 501.9 | 476.7 | 462.3 | 460.9 | 464.9 | 463.7 | 426 | 417.5
2133 | 1994 | 525.7 | 478.7 | 501.8 | 476.8 | 462.4 | 461 | 464.9 | 463.2 | 426 | 417.6
2134 | 1995 | 525.7 | 478.7 | 501.8 | 476.8 | 462.4 | 461 | 465 | 462.9 | 426 | 417.6
2135 | 1996 | 525.7 | 478.7 | 501.9 | 476.8 | 462.4 | 461 | 465 | 462.6 | 426.1 | 417.7
2136 | 1997 | 525.7 | 478.7 | 501.8 | 476.8 | 462.5 | 461.1 | 465 | 462.3 | 426.2 | 417.8
2137 | 1998 | 525.6 | 478.7 | 501.8 | 476.8 | 462.6 | 461.1 | 465 | 462.2 | 426.3 | 417.8
2138 | 1999 | 525.6 | 478.8 | 501.7 | 476.9 | 462.7 | 461.2 | 465 | 461.9 | 426.4 | 417.9
2139 | 2000 | 525.7 | 478.7 | 501.9 | 476.8 | 462.6 | 461.2 | 465.1 | 461.8 | 426.5 | 418
2140 | 2001 | 525.7 | 478.7 | 501.9 | 476.9 | 462.6 | 461.2 | 465.1 | 461.6 | 426.6 | 418.1
2141 | 2002 | 525.7 | 478.7 | 502 | 476.9 | 462.6 | 461.2 | 465.1 | 461.4 | 426.6 | 418.1
2142 | 2003 | 525.7 | 478.8 | 501.8 | 477 | 462.8 | 461.3 | 465.1 | 461.4 | 426.7 | 418.2
2143 | 2004 | 525.8 | 478.7 | 502 | 476.9 | 462.7 | 461.3 | 465.1 | 461.3 | 426.8 | 418.3
2144 | 2005 | 525.8 | 478.7 | 502 | 476.9 | 462.7 | 461.3 | 465.1 | 461.2 | 426.8 | 418.4
2145 | 2006 | 525.8 | 478.8 | 502 | 476.9 | 462.8 | 461.3 | 465.2 | 461.7 | 425.3 | 418.4
2146 | 2007 | 525.8 | 478.8 | 502 | 476.9 | 462.8 | 461.3 | 465.2 | 462.3 | 425.3 | 418.5
2147 | 2008 | 525.8 | 478.8 | 502 | 477 | 462.9 | 461.4 | 465.2 | 463 | 425.4 | 418.6
2148 | 2009 | 525.8 | 478.8 | 502 | 477 | 462.9 | 461.4 | 465.2 | 465.6 | 424.3 | 418.6
2149 | 2010 | 525.8 | 478.9 | 502 | 477 | 463 | 461.5 | 465.3 | 466.2 | 427 | 418.7
2150 | 2011 | 525.8 | 478.9 | 502 | 477 | 463 | 461.5 | 465.3 | 465.6 | 425.2 | 418.8
2151 | 2012 | 525.7 | 478.9 | 502 | 477 | 463 | 461.5 | 465.4 | 468.1 | 425.5 | 418.8
2152 | 2013 | 525.7 | 478.9 | 502 | 477.1 | 463.1 | 461.6 | 465.4 | 467.7 | 427.2 | 418.9
2153 | 2014 | 525.7 | 478.9 | 502.1 | 477.1 | 463.1 | 461.6 | 465.4 | 467.4 | 424.3 | 419
2154 | 2015 | 525.7 | 478.9 | 502.1 | 477.1 | 463.2 | 461.6 | 465.5 | 469.7 | 426.6 | 419
2155 | 2016 | 525.7 | 479 | 502 | 477.1 | 463.3 | 461.7 | 465.5 | 468.6 | 427.5 | 419.1
2156 | 2017 | 525.7 | 479 | 502.1 | 477.1 | 463.3 | 461.7 | 465.5 | 468.9 | 423.4 | 419.2
2157 | 2018 | 525.6 | 479 | 502 | 477.2 | 463.4 | 461.8 | 465.6 | 470.7 | 427.3 | 419.2
2158 | 2019 | 525.6 | 479 | 502 | 477.2 | 463.4 | 461.8 | 465.6 | 469.3 | 427.3 | 419.3
2159 | 2020 | 525.6 | 479 | 502.1 | 477.2 | 463.4 | 461.8 | 465.7 | 470.5 | 422.9 | 419.4
2160 | 2021 | 525.6 | 479 | 502.2 | 477.2 | 463.4 | 461.8 | 465.7 | 471.4 | 427.5 | 419.5
2161 | 2022 | 525.6 | 479 | 502.2 | 477.2 | 463.5 | 461.9 | 465.7 | 469.9 | 426.3 | 419.5
2162 | 2023 | 525.6 | 479 | 502.2 | 477.2 | 463.5 | 461.9 | 465.8 | 471.9 | 424.1 | 419.6
2163 | 2024 | 525.6 | 479 | 502.2 | 477.2 | 463.5 | 461.9 | 465.8 | 473.6 | 422.3 | 419.7
2164 | 2025 | 525.5 | 479.1 | 502.2 | 477.3 | 463.7 | 462 | 465.9 | 475.4 | 424.7 | 419.7
2165 | 2026 | 525.5 | 479.1 | 502.2 | 477.3 | 463.7 | 462 | 465.9 | 477.1 | 424.8 | 419.8
2166 | 2027 | 525.5 | 479.1 | 502.2 | 477.3 | 463.7 | 462.1 | 466 | 475.5 | 427.4 | 419.9
2167 | 2028 | 525.4 | 479.1 | 502.2 | 477.3 | 463.8 | 462.1 | 466 | 474.3 | 423.4 | 420
2168 | 2029 | 525.4 | 479.1 | 502.2 | 477.4 | 463.8 | 462.2 | 466.1 | 476.3 | 425.6 | 420
2169 | 2030 | 525.4 | 479.2 | 502.2 | 477.4 | 463.9 | 462.2 | 466.1 | 474.5 | 427.5 | 420.1
2170 | 2031 | 525.3 | 479.1 | 502.3 | 477.4 | 463.8 | 462.2 | 466.1 | 472.6 | 427.5 | 420.2
2171 | 2032 | 525.3 | 479.2 | 502.3 | 477.4 | 463.9 | 462.3 | 466.1 | 471.1 | 427.5 | 420.3
2172 | 2033 | 525.4 | 479.2 | 502.3 | 477.4 | 464 | 462.3 | 466.2 | 469.9 | 427.6 | 420.3
2173 | 2034 | 525.3 | 479.2 | 502.3 | 477.4 | 464 | 462.3 | 466.2 | 468.9 | 427.6 | 420.4
2174 | 2035 | 525.3 | 479.2 | 502.3 | 477.4 | 464 | 462.4 | 466.2 | 468.2 | 427.7 | 420.5
2175 | 2036 | 525.4 | 479.2 | 502.3 | 477.5 | 464.1 | 462.4 | 466.2 | 467.5 | 427.7 | 420.5
2176 | 2037 | 525.4 | 479.2 | 502.3 | 477.5 | 464.1 | 462.5 | 466.2 | 466.9 | 427.7 | 420.6
2177 | 2038 | 525.4 | 479.2 | 502.4 | 477.5 | 464.1 | 462.5 | 466.2 | 466.4 | 427.8 | 420.7
2178 | 2039 | 525.4 | 479.3 | 502.4 | 477.5 | 464.2 | 462.5 | 466.3 | 465.9 | 427.8 | 420.8
2179 | 2040 | 525.4 | 479.3 | 502.3 | 477.5 | 464.3 | 462.6 | 466.3 | 465.5 | 427.9 | 420.8
2180 | 2041 | 525.4 | 479.3 | 502.4 | 477.5 | 464.3 | 462.6 | 466.3 | 465.3 | 427.9 | 420.9
2181 | 2042 | 525.5 | 479.3 | 502.4 | 477.5 | 464.3 | 462.6 | 466.3 | 465.1 | 428 | 421
2182 | 2043 | 525.5 | 479.3 | 502.4 | 477.6 | 464.4 | 462.7 | 466.3 | 464.8 | 428 | 421.1
2183 | 2044 | 525.5 | 479.4 | 502.4 | 477.6 | 464.5 | 462.7 | 466.4 | 464.6 | 428.1 | 421.1
2184 | 2045 | 525.5 | 479.3 | 502.4 | 477.6 | 464.4 | 462.7 | 466.4 | 464.4 | 428.2 | 421.2
2185 | 2046 | 525.5 | 479.4 | 502.3 | 477.6 | 464.6 | 462.8 | 466.4 | 464.2 | 428.3 | 421.3
2186 | 2047 | 525.5 | 479.4 | 502.4 | 477.6 | 464.6 | 462.8 | 466.4 | 464.1 | 428.1 | 421.3
2187 | 2048 | 525.5 | 479.4 | 502.4 | 477.6 | 464.6 | 462.8 | 466.5 | 464.8 | 426.5 | 421.4
2188 | 2049 | 525.5 | 479.4 | 502.4 | 477.6 | 464.6 | 462.9 | 466.5 | 465.7 | 426 | 421.5
2189 | 2050 | 525.5 | 479.5 | 502.4 | 477.7 | 464.7 | 462.9 | 466.5 | 466.7 | 424.7 | 421.5
2190 | 2051 | 525.5 | 479.5 | 502.4 | 477.7 | 464.7 | 463 | 466.6 | 470.2 | 423.7 | 421.6
2191 | 2052 | 525.5 | 479.5 | 502.5 | 477.7 | 464.7 | 463 | 466.6 | 470.8 | 428.5 | 421.6
2192 | 2053 | 525.5 | 479.5 | 502.5 | 477.7 | 464.8 | 463 | 466.6 | 469.8 | 424 | 421.7
2193 | 2054 | 525.5 | 479.5 | 502.5 | 477.7 | 464.8 | 463.1 | 466.7 | 473.1 | 426.2 | 421.7
2194 | 2055 | 525.5 | 479.5 | 502.5 | 477.7 | 464.9 | 463.1 | 466.7 | 472.5 | 428.6 | 421.8
2195 | 2056 | 525.4 | 479.5 | 502.5 | 477.7 | 464.9 | 463.2 | 466.8 | 472 | 422.6 | 421.8
2196 | 2057 | 525.4 | 479.6 | 502.5 | 477.8 | 465 | 463.2 | 466.8 | 475.1 | 427.6 | 421.8
2197 | 2058 | 525.4 | 479.6 | 502.5 | 477.8 | 465.1 | 463.3 | 466.9 | 473.5 | 428.9 | 421.9
2198 | 2059 | 525.4 | 479.6 | 502.6 | 477.8 | 465 | 463.3 | 466.9 | 473.9 | 424.2 | 421.9
2199 | 2060 | 525.4 | 479.6 | 502.5 | 477.8 | 465.2 | 463.4 | 467 | 476.2 | 428.5 | 421.9
2200 | 2061 | 525.4 | 479.6 | 502.6 | 477.8 | 465.2 | 463.4 | 467 | 474.2 | 429.2 | 422
2201 | 2062 | 525.4 | 479.6 | 502.6 | 477.8 | 465.2 | 463.4 | 467 | 475.7 | 423.1 | 422
2202 | 2063 | 525.4 | 479.6 | 502.6 | 477.8 | 465.2 | 463.5 | 467.1 | 477 | 429.1 | 422
2203 | 2064 | 525.5 | 479.7 | 502.6 | 477.9 | 465.3 | 463.6 | 467.1 | 474.9 | 427.9 | 422
2204 | 2065 | 525.5 | 479.7 | 502.6 | 477.9 | 465.3 | 463.6 | 467.2 | 477.6 | 424.9 | 422.1
2205 | 2066 | 525.5 | 479.7 | 502.6 | 477.9 | 465.3 | 463.6 | 467.2 | 479.7 | 421.5 | 422.1
2206 | 2067 | 525.5 | 479.7 | 502.6 | 477.9 | 465.4 | 463.7 | 467.3 | 481.8 | 426.4 | 422.1
2207 | 2068 | 525.5 | 479.7 | 502.6 | 477.9 | 465.5 | 463.8 | 467.3 | 484 | 426 | 422.2
2208 | 2069 | 525.5 | 479.7 | 502.6 | 477.9 | 465.5 | 463.8 | 467.4 | 481.8 | 429.5 | 422.2
2209 | 2070 | 525.5 | 479.7 | 502.7 | 477.9 | 465.5 | 463.9 | 467.4 | 480.2 | 424.5 | 422.3
2210 | 2071 | 525.5 | 479.8 | 502.6 | 478 | 465.6 | 464 | 467.5 | 482.9 | 427.5 | 422.3
2211 | 2072 | 525.5 | 479.8 | 502.7 | 478 | 465.7 | 464 | 467.5 | 480.4 | 429.7 | 422.3
2212 | 2073 | 525.5 | 479.8 | 502.7 | 478 | 465.6 | 464 | 467.6 | 477.9 | 429.7 | 422.4
2213 | 2074 | 525.6 | 479.8 | 502.7 | 478 | 465.7 | 464.1 | 467.6 | 475.9 | 429.7 | 422.4
2214 | 2075 | 525.6 | 479.8 | 502.7 | 478 | 465.8 | 464.1 | 467.6 | 474.3 | 429.8 | 422.5
2215 | 2076 | 525.6 | 479.8 | 502.8 | 478 | 465.8 | 464.2 | 467.6 | 473.1 | 429.8 | 422.5
2216 | 2077 | 525.6 | 479.8 | 502.7 | 478 | 465.8 | 464.2 | 467.7 | 472 | 429.9 | 422.6
2217 | 2078 | 525.6 | 479.9 | 502.7 | 478.1 | 465.9 | 464.3 | 467.7 | 471.1 | 429.9 | 422.6
2218 | 2079 | 525.6 | 479.9 | 502.8 | 478.1 | 465.9 | 464.3 | 467.7 | 470.4 | 429.9 | 422.6
2219 | 2080 | 525.6 | 479.8 | 502.9 | 478.1 | 465.9 | 464.3 | 467.7 | 469.8 | 430 | 422.7
2220 | 2081 | 525.6 | 479.9 | 502.8 | 478.1 | 466 | 464.4 | 467.7 | 469.3 | 430.1 | 422.7
2221 | 2082 | 525.6 | 479.9 | 502.8 | 478.1 | 466 | 464.4 | 467.8 | 468.9 | 430.1 | 422.8
2222 | 2083 | 525.6 | 479.9 | 502.9 | 478.1 | 466 | 464.4 | 467.8 | 468.5 | 430.2 | 422.8
2223 | 2084 | 525.7 | 479.9 | 502.9 | 478.1 | 466.1 | 464.5 | 467.8 | 468.1 | 430.2 | 422.9
2224 | 2085 | 525.7 | 479.9 | 502.8 | 478.2 | 466.2 | 464.5 | 467.9 | 467.8 | 430.2 | 422.9
2225 | 2086 | 525.7 | 480 | 502.8 | 478.2 | 466.2 | 464.6 | 467.9 | 467.5 | 430.3 | 423
2226 | 2087 | 525.7 | 479.9 | 502.9 | 478.2 | 466.2 | 464.6 | 467.9 | 467.3 | 430.3 | 423
2227 | 2088 | 525.7 | 480 | 502.8 | 478.2 | 466.3 | 464.6 | 468 | 467.1 | 430.4 | 423.1
2228 | 2089 | 525.8 | 480 | 502.9 | 478.2 | 466.3 | 464.6 | 468 | 466.9 | 429.2 | 423.1
2229 | 2090 | 525.8 | 480 | 502.9 | 478.2 | 466.3 | 464.7 | 468 | 468 | 427.9 | 423.2
2230 | 2091 | 525.8 | 480 | 502.9 | 478.2 | 466.3 | 464.7 | 468.1 | 469.3 | 428 | 423.2
2231 | 2092 | 525.8 | 480 | 502.9 | 478.3 | 466.4 | 464.8 | 468.1 | 470.6 | 426.1 | 423.2
2232 | 2093 | 525.7 | 480.1 | 502.9 | 478.3 | 466.5 | 464.8 | 468.2 | 475.3 | 426.2 | 423.3
2233 | 2094 | 525.7 | 480 | 503 | 478.3 | 466.4 | 464.8 | 468.3 | 475.9 | 430.5 | 423.4
2234 | 2095 | 525.7 | 480.1 | 502.9 | 478.3 | 466.5 | 464.9 | 468.3 | 474.6 | 425 | 423.4
2235 | 2096 | 525.7 | 480.1 | 503 | 478.3 | 466.6 | 464.9 | 468.4 | 479.1 | 427.9 | 423.4
2236 | 2097 | 525.7 | 480.1 | 503 | 478.3 | 466.6 | 464.9 | 468.4 | 478 | 430.7 | 423.5
2237 | 2098 | 525.7 | 480.1 | 503 | 478.4 | 466.6 | 465 | 468.5 | 477.3 | 423.6 | 423.5
2238 | 2099 | 525.7 | 480.1 | 503 | 478.4 | 466.7 | 465.1 | 468.5 | 481.5 | 429.5 | 423.6
2239 | 2100 | 525.7 | 480.1 | 503 | 478.4 | 466.7 | 465.1 | 468.6 | 479.3 | 430.7 | 423.6
2240 | 2101 | 525.7 | 480.1 | 503.1 | 478.4 | 466.7 | 465.1 | 468.6 | 479.9 | 424.7 | 423.7
2241 | 2102 | 525.7 | 480.1 | 503 | 478.4 | 466.8 | 465.2 | 468.7 | 483 | 430.3 | 423.7
2242 | 2103 | 525.8 | 480.2 | 503.1 | 478.4 | 466.8 | 465.3 | 468.7 | 480.2 | 431 | 423.8
2243 | 2104 | 525.8 | 480.1 | 503.1 | 478.5 | 466.8 | 465.3 | 468.8 | 482.4 | 426.1 | 423.9
2244 | 2105 | 525.8 | 480.2 | 503.1 | 478.5 | 466.9 | 465.3 | 468.8 | 483.9 | 430.7 | 423.9
2245 | 2106 | 525.8 | 480.2 | 503.1 | 478.5 | 467 | 465.4 | 468.9 | 481 | 429.7 | 423.9
2246 | 2107 | 525.8 | 480.2 | 503.1 | 478.5 | 467 | 465.5 | 468.9 | 484.6 | 427.5 | 424
2247 | 2108 | 525.8 | 480.2 | 503.2 | 478.5 | 467 | 465.5 | 469 | 487.4 | 425.2 | 424.1
2248 | 2109 | 525.8 | 480.2 | 503.1 | 478.5 | 467.1 | 465.6 | 469.1 | 490.3 | 428.2 | 424.1
2249 | 2110 | 525.8 | 480.2 | 503.2 | 478.5 | 467.1 | 465.6 | 469.1 | 493.2 | 428.1 | 424.1
2250 | 2111 | 525.8 | 480.2 | 503.2 | 478.6 | 467.2 | 465.7 | 469.2 | 490 | 431.3 | 424.1
2251 | 2112 | 525.8 | 480.2 | 503.2 | 478.6 | 467.2 | 465.7 | 469.2 | 487.8 | 426.9 | 424.2
2252 | 2113 | 525.8 | 480.3 | 503.2 | 478.6 | 467.3 | 465.8 | 469.3 | 491.3 | 429.5 | 424.2
2253 | 2114 | 525.7 | 480.3 | 503.2 | 478.6 | 467.3 | 465.9 | 469.3 | 487.9 | 431.3 | 424.2
2254 | 2115 | 525.7 | 480.2 | 503.2 | 478.6 | 467.3 | 465.9 | 469.4 | 484.5 | 431.3 | 424.3
2255 | 2116 | 525.6 | 480.3 | 503.2 | 478.7 | 467.4 | 466 | 469.4 | 481.9 | 431.3 | 424.3
2256 | 2117 | 525.6 | 480.3 | 503.2 | 478.7 | 467.5 | 466 | 469.4 | 479.8 | 431.3 | 424.3
2257 | 2118 | 525.6 | 480.3 | 503.2 | 478.7 | 467.5 | 466 | 469.4 | 478.1 | 431.3 | 424.4
2258 | 2119 | 525.5 | 480.3 | 503.3 | 478.7 | 467.5 | 466.1 | 469.5 | 476.7 | 431.3 | 424.4
2259 | 2120 | 525.5 | 480.4 | 503.2 | 478.7 | 467.6 | 466.1 | 469.5 | 475.5 | 431.3 | 424.4
2260 | 2121 | 525.5 | 480.4 | 503.3 | 478.7 | 467.6 | 466.2 | 469.5 | 474.6 | 431.3 | 424.5
2261 | 2122 | 525.4 | 480.3 | 503.3 | 478.7 | 467.6 | 466.2 | 469.5 | 473.8 | 431.3 | 424.5
2262 | 2123 | 525.4 | 480.4 | 503.3 | 478.8 | 467.7 | 466.2 | 469.6 | 473.1 | 431.3 | 424.5
2263 | 2124 | 525.4 | 480.4 | 503.3 | 478.8 | 467.7 | 466.3 | 469.6 | 472.4 | 431.4 | 424.6
2264 | 2125 | 525.4 | 480.4 | 503.3 | 478.8 | 467.7 | 466.3 | 469.6 | 471.7 | 431.4 | 424.6
2265 | 2126 | 525.4 | 480.4 | 503.3 | 478.8 | 467.7 | 466.3 | 469.7 | 471.2 | 431.4 | 424.6
2266 | 2127 | 525.4 | 480.4 | 503.3 | 478.8 | 467.8 | 466.3 | 469.7 | 470.9 | 431.5 | 424.7
2267 | 2128 | 525.4 | 480.4 | 503.3 | 478.9 | 467.8 | 466.4 | 469.7 | 470.6 | 431.5 | 424.7
2268 | 2129 | 525.4 | 480.4 | 503.4 | 478.9 | 467.8 | 466.4 | 469.7 | 470.3 | 431.5 | 424.8
2269 | 2130 | 525.4 | 480.5 | 503.3 | 478.9 | 467.9 | 466.4 | 469.8 | 470 | 431.6 | 424.8
2270 | 2131 | 525.3 | 480.5 | 503.3 | 478.9 | 467.9 | 466.4 | 469.8 | 469.7 | 430.4 | 424.8
2271 | 2132 | 525.3 | 480.5 | 503.4 | 478.9 | 467.9 | 466.4 | 469.8 | 471.3 | 428.8 | 424.9
2272 | 2133 | 525.3 | 480.5 | 503.4 | 478.9 | 467.9 | 466.5 | 469.9 | 472.9 | 428.6 | 424.9
2273 | 2134 | 525.3 | 480.5 | 503.4 | 478.9 | 468 | 466.5 | 469.9 | 474.7 | 426.3 | 424.9
2274 | 2135 | 525.3 | 480.5 | 503.4 | 478.9 | 468.1 | 466.6 | 470 | 481.1 | 424.8 | 424.9
2275 | 2136 | 525.2 | 480.5 | 503.5 | 478.9 | 468 | 466.6 | 470 | 481.8 | 431.9 | 425
2276 | 2137 | 525.3 | 480.6 | 503.3 | 479 | 468.2 | 466.7 | 470 | 479.9 | 428.6 | 425
2277 | 2138 | 525.3 | 480.6 | 503.4 | 479 | 468.2 | 466.7 | 470.1 | 486 | 429.7 | 425
2278 | 2139 | 525.3 | 480.6 | 503.4 | 479 | 468.2 | 466.7 | 470.2 | 484.4 | 432 | 425
2279 | 2140 | 525.4 | 480.6 | 503.4 | 479 | 468.3 | 466.8 | 470.2 | 483.4 | 427.4 | 425.1
2280 | 2141 | 525.4 | 480.6 | 503.4 | 479.1 | 468.3 | 466.9 | 470.3 | 489 | 430.8 | 425.1
2281 | 2142 | 525.4 | 480.6 | 503.4 | 479.1 | 468.4 | 466.9 | 470.3 | 485.8 | 431.7 | 425.1
2282 | 2143 | 525.4 | 480.6 | 503.5 | 479.1 | 468.3 | 466.9 | 470.4 | 486.6 | 422.3 | 425.2
2283 | 2144 | 525.4 | 480.7 | 503.4 | 479.1 | 468.5 | 467 | 470.4 | 490.6 | 431.9 | 425.2
2284 | 2145 | 525.4 | 480.7 | 503.4 | 479.1 | 468.5 | 467.1 | 470.5 | 486.7 | 429.7 | 425.2
2285 | 2146 | 525.4 | 480.7 | 503.5 | 479.1 | 468.5 | 467.1 | 470.5 | 489.7 | 426.1 | 425.3
2286 | 2147 | 525.5 | 480.7 | 503.5 | 479.1 | 468.5 | 467.1 | 470.6 | 491.5 | 432.1 | 425.3
2287 | 2148 | 525.5 | 480.7 | 503.5 | 479.2 | 468.6 | 467.2 | 470.6 | 487.7 | 428.3 | 425.3
2288 | 2149 | 525.5 | 480.7 | 503.5 | 479.2 | 468.6 | 467.2 | 470.7 | 492.5 | 428.1 | 425.4
2289 | 2150 | 525.6 | 480.7 | 503.6 | 479.1 | 468.6 | 467.3 | 470.7 | 496.1 | 424.8 | 425.5
2290 | 2151 | 525.6 | 480.7 | 503.6 | 479.2 | 468.7 | 467.4 | 470.8 | 499.7 | 426.5 | 425.4
2291 | 2152 | 525.7 | 480.8 | 503.6 | 479.2 | 468.8 | 467.4 | 470.9 | 503.1 | 429.9 | 425.5
2292 | 2153 | 525.7 | 480.8 | 503.6 | 479.2 | 468.8 | 467.5 | 470.9 | 498.9 | 432.7 | 425.5
2293 | 2154 | 525.7 | 480.7 | 503.7 | 479.2 | 468.8 | 467.5 | 471 | 496.1 | 425.4 | 425.6
2294 | 2155 | 525.7 | 480.8 | 503.6 | 479.2 | 468.9 | 467.6 | 471 | 500.6 | 430 | 425.6
2295 | 2156 | 525.7 | 480.8 | 503.6 | 479.3 | 468.9 | 467.7 | 471 | 496.1 | 432.9 | 425.6
2296 | 2157 | 525.7 | 480.8 | 503.7 | 479.2 | 468.9 | 467.7 | 471.1 | 491.6 | 432.9 | 425.7
2297 | 2158 | 525.7 | 480.8 | 503.6 | 479.3 | 469 | 467.8 | 471.1 | 488.1 | 432.9 | 425.7
2298 | 2159 | 525.7 | 480.8 | 503.6 | 479.3 | 469.1 | 467.8 | 471.1 | 485.3 | 432.9 | 425.7
2299 | 2160 | 525.7 | 480.9 | 503.6 | 479.3 | 469.1 | 467.9 | 471.1 | 483 | 432.9 | 425.7
2300 | 2161 | 525.7 | 480.8 | 503.7 | 479.3 | 469.1 | 467.9 | 471.1 | 481.1 | 432.9 | 425.8
2301 | 2162 | 525.7 | 480.9 | 503.7 | 479.3 | 469.1 | 467.9 | 471.2 | 479.6 | 432.9 | 425.8
2302 | 2163 | 525.7 | 480.9 | 503.7 | 479.4 | 469.1 | 467.9 | 471.2 | 478.4 | 432.9 | 425.8
2303 | 2164 | 525.7 | 480.9 | 503.8 | 479.4 | 469.1 | 467.9 | 471.2 | 477.3 | 432.9 | 425.9
2304 | 2165 | 525.7 | 480.9 | 503.7 | 479.4 | 469.2 | 468 | 471.3 | 476.4 | 432.9 | 425.9
2305 | 2166 | 525.6 | 480.9 | 503.7 | 479.4 | 469.3 | 468 | 471.3 | 475.6 | 432.9 | 425.9
2306 | 2167 | 525.6 | 480.9 | 503.8 | 479.4 | 469.2 | 468 | 471.3 | 474.9 | 433 | 426
2307 | 2168 | 525.6 | 480.9 | 503.8 | 479.4 | 469.2 | 468 | 471.4 | 474.2 | 433 | 426
2308 | 2169 | 525.5 | 480.9 | 503.7 | 479.4 | 469.3 | 468.1 | 471.4 | 473.7 | 433 | 426
2309 | 2170 | 525.5 | 481 | 503.8 | 479.5 | 469.3 | 468.1 | 471.4 | 473.2 | 433 | 426
2310 | 2171 | 525.5 | 480.9 | 503.9 | 479.5 | 469.3 | 468.1 | 471.4 | 472.9 | 433.1 | 426.1
2311 | 2172 | 525.5 | 481 | 503.8 | 479.5 | 469.4 | 468.2 | 471.5 | 472.5 | 433.1 | 426.1
2312 | 2173 | 525.4 | 481 | 503.8 | 479.5 | 469.5 | 468.2 | 471.5 | 472.2 | 431.7 | 426.1
2313 | 2174 | 525.4 | 481 | 503.8 | 479.5 | 469.4 | 468.2 | 471.5 | 474.3 | 428.2 | 426.1
2314 | 2175 | 525.4 | 481 | 503.8 | 479.5 | 469.5 | 468.2 | 471.6 | 476.4 | 430.2 | 426.2
2315 | 2176 | 525.4 | 481 | 503.8 | 479.6 | 469.6 | 468.3 | 471.6 | 478.7 | 425.8 | 426.1
2316 | 2177 | 525.4 | 481 | 503.8 | 479.6 | 469.6 | 468.3 | 471.7 | 486.7 | 426.3 | 426.2
2317 | 2178 | 525.4 | 481 | 503.9 | 479.6 | 469.6 | 468.3 | 471.7 | 487.2 | 433.3 | 426.2
2318 | 2179 | 525.4 | 481.1 | 503.8 | 479.6 | 469.7 | 468.4 | 471.8 | 485 | 429.8 | 426.2
2319 | 2180 | 525.4 | 481.1 | 503.8 | 479.6 | 469.7 | 468.4 | 471.8 | 492.5 | 428.6 | 426.2
2320 | 2181 | 525.3 | 481.1 | 503.9 | 479.6 | 469.8 | 468.5 | 471.9 | 490.3 | 433.5 | 426.3
2321 | 2182 | 525.3 | 481.1 | 503.9 | 479.6 | 469.8 | 468.5 | 472 | 489.2 | 427.8 | 426.3
2322 | 2183 | 525.3 | 481.1 | 503.9 | 479.7 | 469.9 | 468.6 | 472 | 496 | 431.8 | 426.3
2323 | 2184 | 525.3 | 481.1 | 503.8 | 479.7 | 469.9 | 468.7 | 472.1 | 492 | 433 | 426.3
2324 | 2185 | 525.3 | 481.1 | 503.9 | 479.7 | 469.8 | 468.7 | 472.2 | 493 | 423 | 426.4
2325 | 2186 | 525.3 | 481.1 | 503.9 | 479.7 | 470 | 468.8 | 472.2 | 497.7 | 433 | 426.3
2326 | 2187 | 525.3 | 481.2 | 503.9 | 479.7 | 470 | 468.8 | 472.3 | 492.9 | 430.4 | 426.4
2327 | 2188 | 525.4 | 481.1 | 504 | 479.7 | 470 | 468.9 | 472.4 | 496.5 | 424.4 | 426.4
2328 | 2189 | 525.4 | 481.1 | 503.9 | 479.7 | 470 | 468.9 | 472.4 | 498.3 | 433.7 | 426.4
2329 | 2190 | 525.4 | 481.2 | 503.9 | 479.8 | 470.1 | 469 | 472.5 | 493.6 | 427.8 | 426.4
2330 | 2191 | 525.4 | 481.2 | 504 | 479.8 | 470.2 | 469.1 | 472.6 | 499.5 | 427.8 | 426.5
2331 | 2192 | 525.4 | 481.2 | 504 | 479.8 | 470.2 | 469.1 | 472.6 | 503.7 | 426.2 | 426.5
2332 | 2193 | 525.4 | 481.2 | 504 | 479.8 | 470.3 | 469.2 | 472.7 | 507.8 | 425.6 | 426.5
2333 | 2194 | 525.4 | 481.2 | 504 | 479.8 | 470.4 | 469.3 | 472.8 | 511.8 | 429.3 | 426.5
2334 | 2195 | 525.5 | 481.2 | 504.1 | 479.8 | 470.4 | 469.3 | 472.9 | 506.4 | 434 | 426.5
2335 | 2196 | 525.5 | 481.2 | 504.1 | 479.8 | 470.4 | 469.4 | 472.9 | 503 | 424 | 426.6
2336 | 2197 | 525.5 | 481.3 | 504.1 | 479.9 | 470.5 | 469.5 | 473 | 508.2 | 431 | 426.6
2337 | 2198 | 525.5 | 481.3 | 504.1 | 479.9 | 470.5 | 469.5 | 473 | 502.5 | 434.1 | 426.6
2338 | 2199 | 525.6 | 481.2 | 504.2 | 479.9 | 470.4 | 469.5 | 473.1 | 497.2 | 434.1 | 426.6
2339 | 2200 | 525.6 | 481.3 | 504.1 | 479.9 | 470.5 | 469.6 | 473.1 | 493.1 | 434.1 | 426.6
2340 | 2201 | 525.7 | 481.3 | 504.1 | 479.9 | 470.6 | 469.7 | 473.1 | 489.9 | 434.1 | 426.7
2341 | 2202 | 525.7 | 481.3 | 504.2 | 479.9 | 470.6 | 469.7 | 473.2 | 487.3 | 434.1 | 426.7
2342 | 2203 | 525.7 | 481.3 | 504.2 | 479.9 | 470.6 | 469.7 | 473.2 | 485.2 | 434.1 | 426.7
2343 | 2204 | 525.7 | 481.3 | 504.2 | 479.9 | 470.6 | 469.7 | 473.2 | 483.4 | 434.1 | 426.7
2344 | 2205 | 525.7 | 481.3 | 504.2 | 480 | 470.6 | 469.8 | 473.2 | 481.9 | 434.1 | 426.7
2345 | 2206 | 525.6 | 481.3 | 504.3 | 480 | 470.6 | 469.8 | 473.3 | 480.6 | 434.2 | 426.8
2346 | 2207 | 525.6 | 481.3 | 504.3 | 480 | 470.7 | 469.8 | 473.3 | 479.5 | 434.2 | 426.8
2347 | 2208 | 525.6 | 481.4 | 504.2 | 480 | 470.8 | 469.8 | 473.3 | 478.7 | 434.2 | 426.8
2348 | 2209 | 525.6 | 481.4 | 504.3 | 480 | 470.8 | 469.8 | 473.4 | 477.9 | 434.2 | 426.8
2349 | 2210 | 525.6 | 481.4 | 504.3 | 480 | 470.8 | 469.9 | 473.4 | 477.2 | 434.2 | 426.8
2350 | 2211 | 525.6 | 481.4 | 504.3 | 480.1 | 470.9 | 469.9 | 473.4 | 476.6 | 434.2 | 426.8
2351 | 2212 | 525.6 | 481.4 | 504.3 | 480.1 | 470.9 | 469.9 | 473.5 | 476.1 | 434.2 | 426.9
2352 | 2213 | 525.5 | 481.4 | 504.4 | 480.1 | 470.9 | 469.9 | 473.5 | 475.6 | 434.2 | 426.9
2353 | 2214 | 525.5 | 481.4 | 504.3 | 480.1 | 470.9 | 469.9 | 473.5 | 475.2 | 434.3 | 426.9
2354 | 2215 | 525.4 | 481.5 | 504.3 | 480.1 | 471 | 470 | 473.6 | 474.7 | 433.2 | 426.9
2355 | 2216 | 525.4 | 481.4 | 504.4 | 480.1 | 470.9 | 470 | 473.6 | 477.1 | 430.6 | 427
2356 | 2217 | 525.3 | 481.4 | 504.3 | 480.1 | 471 | 470 | 473.6 | 479.5 | 431.2 | 427
2357 | 2218 | 525.3 | 481.5 | 504.3 | 480.2 | 471.1 | 470 | 473.7 | 482.2 | 428.9 | 427
2358 | 2219 | 525.2 | 481.5 | 504.3 | 480.2 | 471.2 | 470.1 | 473.7 | 491.3 | 429.8 | 427
2359 | 2220 | 525.2 | 481.5 | 504.4 | 480.2 | 471.1 | 470.1 | 473.8 | 491.9 | 434.1 | 427
2360 | 2221 | 525.2 | 481.5 | 504.3 | 480.2 | 471.3 | 470.2 | 473.8 | 489.4 | 431.1 | 427.1
2361 | 2222 | 525.2 | 481.5 | 504.3 | 480.2 | 471.3 | 470.3 | 473.8 | 497.9 | 430.1 | 427
2362 | 2223 | 525.2 | 481.5 | 504.4 | 480.2 | 471.3 | 470.3 | 473.9 | 495.3 | 434.6 | 427.1
2363 | 2224 | 525.2 | 481.5 | 504.4 | 480.2 | 471.4 | 470.3 | 473.9 | 494.1 | 429.1 | 427.1
2364 | 2225 | 525.2 | 481.6 | 504.3 | 480.2 | 471.5 | 470.4 | 474 | 501.5 | 432.1 | 427.1
2365 | 2226 | 525.2 | 481.6 | 504.3 | 480.3 | 471.6 | 470.5 | 474 | 497 | 435.5 | 427.1
2366 | 2227 | 525.2 | 481.5 | 504.4 | 480.3 | 471.5 | 470.5 | 474 | 498.3 | 426 | 427.2
2367 | 2228 | 525.3 | 481.6 | 504.3 | 480.3 | 471.7 | 470.6 | 474.1 | 503.4 | 434.4 | 427.1
2368 | 2229 | 525.3 | 481.6 | 504.3 | 480.3 | 471.7 | 470.7 | 474.1 | 497.9 | 434.7 | 427.2
2369 | 2230 | 525.3 | 481.6 | 504.4 | 480.3 | 471.7 | 470.7 | 474.2 | 502.1 | 425.6 | 427.2
2370 | 2231 | 525.3 | 481.6 | 504.4 | 480.3 | 471.8 | 470.8 | 474.2 | 504 | 434.9 | 427.2
2371 | 2232 | 525.3 | 481.7 | 504.4 | 480.4 | 471.9 | 470.9 | 474.3 | 498.8 | 432.3 | 427.2
2372 | 2233 | 525.4 | 481.7 | 504.4 | 480.4 | 471.9 | 470.9 | 474.3 | 505.4 | 426.7 | 427.2
2373 | 2234 | 525.4 | 481.6 | 504.5 | 480.3 | 471.9 | 471 | 474.4 | 510.1 | 424.2 | 427.2
2374 | 2235 | 525.4 | 481.7 | 504.4 | 480.4 | 472 | 471.1 | 474.4 | 514.8 | 429.2 | 427.2
2375 | 2236 | 525.4 | 481.7 | 504.4 | 480.4 | 472.1 | 471.2 | 474.4 | 519.5 | 429.3 | 427.2
2376 | 2237 | 525.5 | 481.7 | 504.5 | 480.4 | 472.1 | 471.2 | 474.5 | 513 | 435.2 | 427.3
2377 | 2238 | 525.5 | 481.7 | 504.5 | 480.4 | 472.1 | 471.3 | 474.6 | 509.2 | 425.7 | 427.3
2378 | 2239 | 525.5 | 481.7 | 504.5 | 480.4 | 472.3 | 471.4 | 474.6 | 515.1 | 433.8 | 427.3
2379 | 2240 | 525.6 | 481.7 | 504.5 | 480.5 | 472.3 | 471.5 | 474.7 | 508.4 | 435.1 | 427.3
2380 | 2241 | 525.6 | 481.7 | 504.6 | 480.4 | 472.2 | 471.5 | 474.8 | 502.2 | 435.2 | 427.3
2381 | 2242 | 525.6 | 481.7 | 504.6 | 480.5 | 472.3 | 471.6 | 474.8 | 497.6 | 435.2 | 427.4
2382 | 2243 | 525.6 | 481.8 | 504.6 | 480.5 | 472.3 | 471.6 | 474.9 | 493.8 | 435.2 | 427.4
2383 | 2244 | 525.6 | 481.7 | 504.6 | 480.5 | 472.3 | 471.6 | 474.9 | 490.9 | 435.2 | 427.4
2384 | 2245 | 525.6 | 481.7 | 504.6 | 480.5 | 472.3 | 471.7 | 475 | 488.5 | 435.2 | 427.4
2385 | 2246 | 525.6 | 481.8 | 504.6 | 480.5 | 472.4 | 471.7 | 475 | 486.5 | 435.1 | 427.4
2386 | 2247 | 525.6 | 481.8 | 504.6 | 480.5 | 472.4 | 471.7 | 475 | 484.9 | 435.1 | 427.4
2387 | 2248 | 525.6 | 481.8 | 504.7 | 480.5 | 472.4 | 471.7 | 475.1 | 483.5 | 435.2 | 427.5
2388 | 2249 | 525.6 | 481.8 | 504.7 | 480.6 | 472.4 | 471.8 | 475.1 | 482.3 | 435.2 | 427.5
2389 | 2250 | 525.6 | 481.8 | 504.7 | 480.6 | 472.5 | 471.8 | 475.1 | 481.2 | 435.2 | 427.5
2390 | 2251 | 525.6 | 481.8 | 504.8 | 480.6 | 472.4 | 471.8 | 475.2 | 480.4 | 435.2 | 427.5
2391 | 2252 | 525.6 | 481.8 | 504.8 | 480.6 | 472.4 | 471.8 | 475.2 | 479.7 | 435.2 | 427.5
2392 | 2253 | 525.6 | 481.9 | 504.7 | 480.6 | 472.6 | 471.8 | 475.2 | 479 | 435.2 | 427.5
2393 | 2254 | 525.5 | 481.8 | 504.8 | 480.6 | 472.6 | 471.8 | 475.3 | 478.4 | 435.2 | 427.6
2394 | 2255 | 525.5 | 481.8 | 504.8 | 480.6 | 472.5 | 471.8 | 475.3 | 477.9 | 435.2 | 427.6
2395 | 2256 | 525.5 | 481.9 | 504.8 | 480.7 | 472.6 | 471.9 | 475.4 | 477.4 | 435.3 | 427.6
2396 | 2257 | 525.5 | 481.9 | 504.8 | 480.7 | 472.7 | 471.9 | 475.4 | 476.9 | 435.3 | 427.6
2397 | 2258 | 525.5 | 481.9 | 504.8 | 480.7 | 472.6 | 471.9 | 475.4 | 479.8 | 429.9 | 427.6
2398 | 2259 | 525.5 | 481.9 | 504.8 | 480.7 | 472.7 | 471.9 | 475.5 | 482.5 | 430.7 | 427.7
2399 | 2260 | 525.5 | 481.9 | 504.9 | 480.7 | 472.8 | 471.9 | 475.5 | 485.7 | 433.3 | 427.7
2400 | 2261 | 525.5 | 481.9 | 504.8 | 480.7 | 472.8 | 472 | 475.6 | 496.6 | 431 | 427.7
2401 | 2262 | 525.5 | 481.9 | 504.9 | 480.7 | 472.8 | 472 | 475.6 | 496.8 | 435.2 | 427.7
2402 | 2263 | 525.5 | 481.9 | 504.9 | 480.7 | 472.9 | 472.1 | 475.7 | 493.9 | 431.3 | 427.7
2403 | 2264 | 525.5 | 482 | 504.8 | 480.8 | 473 | 472.2 | 475.7 | 503.7 | 432.9 | 427.7
2404 | 2265 | 525.5 | 481.9 | 504.9 | 480.8 | 473 | 472.2 | 475.8 | 500.2 | 435.5 | 427.7
2405 | 2266 | 525.4 | 481.9 | 504.9 | 480.8 | 473.1 | 472.3 | 475.8 | 499.2 | 430.2 | 427.8
2406 | 2267 | 525.4 | 482 | 504.8 | 480.8 | 473.2 | 472.4 | 475.9 | 507.4 | 433.2 | 427.7
2407 | 2268 | 525.4 | 482 | 504.9 | 480.8 | 473.2 | 472.5 | 475.9 | 501.6 | 436.4 | 427.7
2408 | 2269 | 525.3 | 482 | 505 | 480.8 | 473.2 | 472.5 | 476 | 500.9 | 427.5 | 427.8
2409 | 2270 | 525.3 | 482 | 504.9 | 480.8 | 473.3 | 472.6 | 476 | 502.8 | 435.4 | 427.7
2410 | 2271 | 525.2 | 482 | 504.9 | 480.9 | 473.3 | 472.7 | 476.1 | 498 | 435.8 | 427.8
2411 | 2272 | 525.2 | 482 | 504.9 | 480.9 | 473.3 | 472.8 | 476.1 | 500 | 427.2 | 427.8
2412 | 2273 | 525.1 | 482 | 505 | 480.9 | 473.4 | 472.8 | 476.2 | 500.7 | 435.9 | 427.8
2413 | 2274 | 525.1 | 482.1 | 504.9 | 480.9 | 473.4 | 472.9 | 476.2 | 496.7 | 433.3 | 427.8
2414 | 2275 | 525.1 | 482.1 | 504.9 | 480.9 | 473.5 | 473 | 476.3 | 500.5 | 429.7 | 427.8
2415 | 2276 | 525.1 | 482.1 | 505 | 480.9 | 473.5 | 473.1 | 476.4 | 503.5 | 429.2 | 427.9
2416 | 2277 | 525.1 | 482.1 | 504.9 | 480.9 | 473.6 | 473.2 | 476.4 | 506.2 | 430 | 427.8
2417 | 2278 | 525.1 | 482.1 | 504.9 | 480.9 | 473.7 | 473.3 | 476.5 | 508.8 | 430.8 | 427.8
2418 | 2279 | 525.1 | 482.1 | 504.9 | 480.9 | 473.7 | 473.4 | 476.6 | 504.8 | 436.3 | 427.8
2419 | 2280 | 525.1 | 482.1 | 505 | 480.9 | 473.7 | 473.5 | 476.6 | 502 | 427.9 | 427.9
2420 | 2281 | 525.1 | 482.2 | 504.9 | 481 | 473.9 | 473.7 | 476.7 | 505 | 432.6 | 427.8
2421 | 2282 | 525.1 | 482.2 | 505 | 481 | 473.9 | 473.7 | 476.7 | 501 | 436.3 | 427.9
2422 | 2283 | 525.1 | 482.1 | 505.1 | 481 | 473.8 | 473.8 | 476.8 | 497.1 | 436.3 | 427.9
2423 | 2284 | 525.1 | 482.2 | 505 | 481 | 473.9 | 473.8 | 476.8 | 493.7 | 436.3 | 427.9
2424 | 2285 | 525.1 | 482.2 | 505 | 481 | 474 | 473.9 | 476.9 | 491.1 | 436.3 | 427.9
2425 | 2286 | 525.1 | 482.2 | 505 | 481 | 474 | 473.9 | 476.9 | 489 | 436.3 | 428
2426 | 2287 | 525.1 | 482.2 | 505.1 | 481 | 474 | 473.9 | 476.9 | 487.1 | 436.3 | 428
2427 | 2288 | 525.2 | 482.2 | 505 | 481.1 | 474.1 | 474 | 477 | 485.6 | 436.3 | 428
2428 | 2289 | 525.2 | 482.2 | 505 | 481.1 | 474.1 | 474 | 477 | 484.3 | 436.3 | 428
2429 | 2290 | 525.3 | 482.2 | 505.1 | 481.1 | 474 | 473.9 | 477 | 483.2 | 436.4 | 428.1
2430 | 2291 | 525.3 | 482.2 | 505.1 | 481.1 | 474.1 | 474 | 477 | 482.2 | 436.3 | 428.1
2431 | 2292 | 525.4 | 482.3 | 505.1 | 481.1 | 474.2 | 474 | 477.1 | 481.4 | 436.3 | 428.1
2432 | 2293 | 525.5 | 482.2 | 505.2 | 481.1 | 474.1 | 473.9 | 477.1 | 480.8 | 436.4 | 428.1
2433 | 2294 | 525.5 | 482.2 | 505.2 | 481.1 | 474.1 | 473.9 | 477.1 | 480.2 | 436.4 | 428.2
2434 | 2295 | 525.5 | 482.3 | 505.1 | 481.1 | 474.3 | 474 | 477.1 | 479.6 | 436.4 | 428.2
2435 | 2296 | 525.5 | 482.3 | 505.1 | 481.1 | 474.3 | 474 | 477.2 | 479.1 | 436.4 | 428.2
2436 | 2297 | 525.5 | 482.3 | 505.2 | 481.1 | 474.2 | 473.9 | 477.2 | 478.7 | 436.4 | 428.2
2437 | 2298 | 525.5 | 482.3 | 505.1 | 481.2 | 474.4 | 474 | 477.2 | 478.3 | 436.4 | 428.2
2438 | 2299 | 525.6 | 482.4 | 505.1 | 481.1 | 474.4 | 474 | 477.2 | 477.9 | 434.9 | 428.2
2439 | 2300 | 525.6 | 482.3 | 505.2 | 481.1 | 474.4 | 474 | 477.3 | 479 | 432.7 | 428.3
2440 | 2301 | 525.6 | 482.3 | 505.3 | 481.2 | 474.4 | 474 | 477.3 | 480.4 | 430.8 | 428.3
2441 | 2302 | 525.6 | 482.4 | 505.2 | 481.2 | 474.5 | 474 | 477.3 | 482 | 432.4 | 428.4
2442 | 2303 | 525.5 | 482.4 | 505.2 | 481.2 | 474.6 | 474.1 | 477.4 | 487.4 | 431.4 | 428.4
2443 | 2304 | 525.5 | 482.4 | 505.3 | 481.2 | 474.6 | 474.1 | 477.4 | 488 | 436.2 | 428.4
2444 | 2305 | 525.5 | 482.4 | 505.2 | 481.2 | 474.7 | 474.2 | 477.5 | 486.8 | 431.5 | 428.4
2445 | 2306 | 525.5 | 482.4 | 505.2 | 481.2 | 474.8 | 474.3 | 477.5 | 491.9 | 433.9 | 428.4
2446 | 2307 | 525.5 | 482.4 | 505.3 | 481.2 | 474.8 | 474.3 | 477.6 | 490.6 | 436.5 | 428.4
2447 | 2308 | 525.6 | 482.4 | 505.3 | 481.2 | 474.8 | 474.4 | 477.7 | 490.1 | 430.5 | 428.5
2448 | 2309 | 525.5 | 482.5 | 505.3 | 481.3 | 474.9 | 474.5 | 477.7 | 495.5 | 435.9 | 428.5
2449 | 2310 | 525.5 | 482.5 | 505.2 | 481.3 | 475 | 474.6 | 477.8 | 493.1 | 437.7 | 428.5
2450 | 2311 | 525.5 | 482.4 | 505.3 | 481.3 | 474.9 | 474.6 | 477.9 | 495.1 | 428.3 | 428.6
2451 | 2312 | 525.5 | 482.5 | 505.2 | 481.3 | 475.1 | 474.7 | 477.9 | 499.9 | 436.5 | 428.5
2452 | 2313 | 525.5 | 482.5 | 505.2 | 481.3 | 475.1 | 474.8 | 478 | 496.3 | 436.4 | 428.6
2453 | 2314 | 525.5 | 482.5 | 505.3 | 481.3 | 475.1 | 474.9 | 478 | 500 | 427.8 | 428.6
2454 | 2315 | 525.5 | 482.5 | 505.4 | 481.3 | 475.2 | 474.9 | 478.1 | 502 | 436.9 | 428.6
2455 | 2316 | 525.5 | 482.5 | 505.3 | 481.3 | 475.3 | 475 | 478.1 | 498.7 | 434.1 | 428.7
2456 | 2317 | 525.5 | 482.5 | 505.4 | 481.3 | 475.3 | 475.1 | 478.2 | 503.5 | 430.7 | 428.7
2457 | 2318 | 525.5 | 482.5 | 505.4 | 481.3 | 475.3 | 475.2 | 478.2 | 507.9 | 429.7 | 428.8
2458 | 2319 | 525.6 | 482.6 | 505.4 | 481.3 | 475.5 | 475.3 | 478.3 | 512.1 | 430.2 | 428.7
2459 | 2320 | 525.6 | 482.6 | 505.4 | 481.4 | 475.6 | 475.4 | 478.4 | 516.4 | 431.5 | 428.7
2460 | 2321 | 525.6 | 482.6 | 505.4 | 481.4 | 475.5 | 475.5 | 478.4 | 512.7 | 437.2 | 428.8
2461 | 2322 | 525.6 | 482.6 | 505.5 | 481.4 | 475.6 | 475.6 | 478.5 | 509.7 | 427.9 | 428.8
2462 | 2323 | 525.6 | 482.6 | 505.4 | 481.4 | 475.7 | 475.7 | 478.5 | 513.7 | 433.5 | 428.8
2463 | 2324 | 525.6 | 482.6 | 505.4 | 481.4 | 475.7 | 475.8 | 478.6 | 509.7 | 437.2 | 428.8
2464 | 2325 | 525.6 | 482.6 | 505.5 | 481.4 | 475.6 | 475.8 | 478.6 | 505 | 437.3 | 428.9
2465 | 2326 | 525.6 | 482.7 | 505.4 | 481.4 | 475.8 | 475.9 | 478.7 | 501 | 437.2 | 428.9
2466 | 2327 | 525.6 | 482.7 | 505.4 | 481.4 | 475.8 | 475.9 | 478.7 | 497.9 | 437.2 | 428.9
2467 | 2328 | 525.6 | 482.6 | 505.5 | 481.4 | 475.8 | 475.9 | 478.7 | 495.3 | 437.2 | 428.9
2468 | 2329 | 525.5 | 482.7 | 505.5 | 481.4 | 475.8 | 475.9 | 478.7 | 493.1 | 437.2 | 429
2469 | 2330 | 525.5 | 482.7 | 505.5 | 481.5 | 476 | 476 | 478.7 | 491.2 | 437.2 | 429
2470 | 2331 | 525.5 | 482.7 | 505.5 | 481.4 | 476 | 476 | 478.8 | 489.6 | 437.2 | 429
2471 | 2332 | 525.5 | 482.7 | 505.6 | 481.4 | 475.9 | 475.9 | 478.8 | 488.2 | 437.2 | 429
2472 | 2333 | 525.5 | 482.7 | 505.6 | 481.5 | 476 | 476 | 478.8 | 487.1 | 437.2 | 429.1
2473 | 2334 | 525.5 | 482.7 | 505.6 | 481.5 | 476.1 | 476 | 478.8 | 486.1 | 437.2 | 429.1
2474 | 2335 | 525.5 | 482.7 | 505.6 | 481.5 | 476.1 | 476 | 478.8 | 485.2 | 437.2 | 429.1
2475 | 2336 | 525.5 | 482.7 | 505.6 | 481.5 | 476.1 | 475.9 | 478.9 | 484.4 | 437.2 | 429.1
2476 | 2337 | 525.5 | 482.8 | 505.5 | 481.5 | 476.2 | 476 | 478.9 | 483.7 | 437.2 | 429.1
2477 | 2338 | 525.6 | 482.8 | 505.6 | 481.5 | 476.2 | 476 | 478.9 | 483 | 437.2 | 429.2
2478 | 2339 | 525.6 | 482.7 | 505.7 | 481.5 | 476.2 | 475.9 | 478.9 | 482.5 | 437.3 | 429.2
2479 | 2340 | 525.7 | 482.8 | 505.7 | 481.5 | 476.3 | 475.9 | 478.9 | 482 | 437.2 | 429.2
2480 | 2341 | 525.7 | 482.8 | 505.6 | 481.5 | 476.4 | 476 | 479 | 481.5 | 437.2 | 429.2
2481 | 2342 | 525.7 | 482.8 | 505.7 | 481.5 | 476.4 | 475.9 | 479 | 483.8 | 433.5 | 429.3
2482 | 2343 | 525.7 | 482.8 | 505.7 | 481.5 | 476.4 | 476 | 479 | 486.5 | 433.6 | 429.3
2483 | 2344 | 525.7 | 482.9 | 505.6 | 481.6 | 476.5 | 476 | 479.1 | 489.7 | 431.7 | 429.3
2484 | 2345 | 525.7 | 482.9 | 505.6 | 481.6 | 476.6 | 476.1 | 479.1 | 498.7 | 432.4 | 429.3
2485 | 2346 | 525.7 | 482.8 | 505.7 | 481.6 | 476.6 | 476.1 | 479.2 | 500.5 | 436.9 | 429.3
2486 | 2347 | 525.7 | 482.9 | 505.7 | 481.6 | 476.7 | 476.2 | 479.2 | 499 | 432.7 | 429.4
2487 | 2348 | 525.7 | 482.9 | 505.7 | 481.6 | 476.8 | 476.2 | 479.3 | 507.9 | 434.7 | 429.4
2488 | 2349 | 525.7 | 482.9 | 505.8 | 481.6 | 476.8 | 476.3 | 479.3 | 507.1 | 437.1 | 429.4
2489 | 2350 | 525.7 | 482.9 | 505.8 | 481.6 | 476.8 | 476.3 | 479.4 | 506.8 | 429.1 | 429.4
2490 | 2351 | 525.7 | 482.9 | 505.8 | 481.6 | 476.9 | 476.4 | 479.4 | 515.8 | 434 | 429.4
2491 | 2352 | 525.7 | 482.9 | 505.8 | 481.6 | 476.9 | 476.5 | 479.5 | 512.7 | 436.7 | 429.4
2492.1 | 2353.1 | 525.7 | 482.9 | 505.8 | 481.6 | 476.9 | 476.5 | 479.6 | 515.3 | 426.3 | 429.5
2493.1 | 2354.1 | 525.6 | 482.9 | 505.8 | 481.7 | 477 | 476.6 | 479.6 | 522.3 | 437 | 429.5
2494.1 | 2355.1 | 525.6 | 483 | 505.8 | 481.7 | 477.1 | 476.7 | 479.6 | 518 | 434 | 429.5
2495.1 | 2356.1 | 525.6 | 482.9 | 505.8 | 481.7 | 477.1 | 476.8 | 479.7 | 523.5 | 428.8 | 429.5
2496.1 | 2357.1 | 525.6 | 483 | 505.8 | 481.7 | 477.2 | 476.8 | 479.7 | 526.9 | 437.2 | 429.5
2497.1 | 2358.1 | 525.6 | 483 | 505.8 | 481.7 | 477.2 | 476.9 | 479.8 | 522.5 | 433.3 | 429.5
2498.1 | 2359.1 | 525.6 | 483 | 505.8 | 481.7 | 477.3 | 477 | 479.8 | 530.4 | 429.7 | 429.5
2499.1 | 2360.1 | 525.6 | 483 | 505.9 | 481.7 | 477.3 | 477 | 479.9 | 538.7 | 427.3 | 429.6
2500.1 | 2361.1 | 525.5 | 483 | 505.9 | 481.7 | 477.5 | 477.1 | 479.9 | 547.8 | 430.7 | 429.6
2501.1 | 2362.1 | 525.5 | 483 | 505.9 | 481.7 | 477.5 | 477.2 | 480 | 561.7 | 433.2 | 429.6
2502.1 | 2363.1 | 525.5 | 483 | 505.9 | 481.7 | 477.5 | 477.3 | 480 | 557.1 | 437.4 | 429.6
2503.1 | 2364.1 | 525.5 | 483 | 505.9 | 481.7 | 477.5 | 477.3 | 480.1 | 558 | 430.4 | 429.7
2504.1 | 2365.1 | 525.5 | 483.1 | 505.8 | 481.8 | 477.7 | 477.4 | 480.1 | 587.5 | 436.7 | 429.7
2505.1 | 2366.1 | 525.5 | 483.1 | 505.8 | 481.8 | 477.7 | 477.5 | 480.2 | 575 | 437.4 | 429.7
2506.1 | 2367.1 | 525.5 | 483 | 506 | 481.7 | 477.6 | 477.4 | 480.2 | 562.6 | 437.4 | 429.7
2507.1 | 2368.1 | 525.4 | 483.1 | 505.9 | 481.8 | 477.7 | 477.5 | 480.2 | 552.5 | 437.4 | 429.7
2508.1 | 2369.1 | 525.4 | 483.1 | 505.9 | 481.8 | 477.8 | 477.5 | 480.3 | 544.1 | 437.5 | 429.7
2509.1 | 2370.1 | 525.3 | 483.1 | 505.9 | 481.8 | 477.8 | 477.5 | 480.3 | 537.2 | 437.5 | 429.8
2510.1 | 2371.1 | 525.3 | 483.1 | 506 | 481.8 | 477.8 | 477.5 | 480.3 | 531.3 | 437.5 | 429.8
2511.1 | 2372.1 | 525.3 | 483.1 | 505.9 | 481.8 | 477.9 | 477.6 | 480.3 | 526.2 | 437.5 | 429.8
2512.1 | 2373.1 | 525.2 | 483.2 | 505.9 | 481.8 | 478 | 477.6 | 480.3 | 521.8 | 437.5 | 429.8
2513.1 | 2374.1 | 525.2 | 483.1 | 506 | 481.8 | 477.9 | 477.5 | 480.3 | 518 | 437.5 | 429.9
2514.1 | 2375.1 | 525.2 | 483.2 | 505.9 | 481.9 | 478 | 477.6 | 480.4 | 514.7 | 437.5 | 429.9
2515.1 | 2376.1 | 525.2 | 483.2 | 505.9 | 481.9 | 478.1 | 477.6 | 480.4 | 511.7 | 437.5 | 429.9
2516.1 | 2377.1 | 525.2 | 483.2 | 506 | 481.9 | 478 | 477.5 | 480.4 | 509 | 437.5 | 429.9
2517.1 | 2378.1 | 525.1 | 483.2 | 506 | 481.9 | 478.1 | 477.6 | 480.4 | 506.5 | 437.6 | 429.9
2518.1 | 2379.1 | 525.1 | 483.2 | 506 | 481.9 | 478.2 | 477.6 | 480.4 | 504.4 | 437.6 | 429.9
2519.1 | 2380.1 | 525.1 | 483.2 | 506 | 481.9 | 478.3 | 477.6 | 480.5 | 502.5 | 437.6 | 429.9
2520.1 | 2381.1 | 525.2 | 483.2 | 506 | 481.9 | 478.2 | 477.6 | 480.5 | 500.7 | 437.6 | 430
2521.1 | 2382.1 | 525.2 | 483.3 | 506 | 481.9 | 478.3 | 477.6 | 480.5 | 499.3 | 437.6 | 430
2522.1 | 2383.1 | 525.2 | 483.3 | 506 | 481.9 | 478.4 | 477.6 | 480.5 | 498.1 | 437.3 | 430
2523.1 | 2384.1 | 525.2 | 483.3 | 506 | 481.9 | 478.4 | 477.6 | 480.6 | 523.6 | 435.7 | 430
2524.1 | 2385.1 | 525.2 | 483.3 | 506 | 482 | 478.4 | 477.6 | 480.6 | 544.8 | 435.9 | 430.1
2525.1 | 2386.1 | 525.2 | 483.3 | 506 | 482 | 478.5 | 477.7 | 480.6 | 569.3 | 435.6 | 430
2526.1 | 2387.1 | 525.2 | 483.3 | 506 | 482 | 478.6 | 477.7 | 480.7 | 607.2 | 436 | 430.1
2527.1 | 2388.1 | 525.2 | 483.3 | 506.1 | 482 | 478.5 | 477.7 | 480.7 | 597.5 | 437.4 | 430.1
2528.1 | 2389.1 | 525.2 | 483.4 | 506 | 482 | 478.6 | 477.7 | 480.7 | 588.6 | 436.4 | 430.1
2529.1 | 2390.1 | 525.3 | 483.4 | 506 | 482 | 478.7 | 477.8 | 480.8 | 626.1 | 436.3 | 430.1
2530.1 | 2391.1 | 525.2 | 483.3 | 506.1 | 482 | 478.7 | 477.8 | 480.8 | 606.6 | 437.5 | 430.1
2531.1 | 2392.1 | 525.2 | 483.4 | 506.1 | 482 | 478.7 | 477.8 | 480.8 | 607.5 | 435.7 | 430.2
2532.1 | 2393.1 | 525.2 | 483.4 | 506.1 | 482 | 478.8 | 477.8 | 480.9 | 635.9 | 437.4 | 430.2
2533.1 | 2394.1 | 525.2 | 483.4 | 506 | 482 | 478.8 | 477.9 | 480.9 | 610.7 | 437.5 | 430.2
2534.1 | 2395.1 | 525.3 | 483.4 | 506.1 | 482 | 478.8 | 477.8 | 480.9 | 624.5 | 435.3 | 430.2
2535.1 | 2396.1 | 525.3 | 483.4 | 506.1 | 482 | 478.9 | 477.9 | 481 | 638.4 | 437.5 | 430.2
2536.1 | 2397.1 | 525.3 | 483.4 | 506.1 | 482 | 478.9 | 477.9 | 481 | 613 | 436.9 | 430.2
2537.1 | 2398.1 | 525.3 | 483.4 | 506.2 | 482 | 478.9 | 477.9 | 481 | 639.8 | 436 | 430.3
2538.1 | 2399.1 | 525.2 | 483.4 | 506.2 | 482 | 478.9 | 478 | 481.1 | 637.3 | 437.6 | 430.3
2539.1 | 2400.1 | 525.2 | 483.5 | 506.1 | 482.1 | 479 | 478 | 481.1 | 616.4 | 436.7 | 430.3
2540.1 | 2401.1 | 525.2 | 483.5 | 506.1 | 482.1 | 479.1 | 478 | 481.1 | 648.8 | 436.7 | 430.3
2541.1 | 2402.1 | 525.2 | 483.4 | 506.2 | 482 | 479 | 478 | 481.2 | 666.1 | 436.4 | 430.4
2542.1 | 2403.1 | 525.2 | 483.5 | 506.2 | 482.1 | 479.1 | 478.1 | 481.2 | 679.3 | 436.4 | 430.4
2543.1 | 2404.1 | 525.2 | 483.5 | 506.2 | 482.1 | 479.2 | 478.2 | 481.2 | 695.5 | 437.2 | 430.4
2544.1 | 2405.1 | 525.2 | 483.5 | 506.2 | 482.1 | 479.2 | 478.2 | 481.3 | 663.2 | 437.8 | 430.4
2545.1 | 2406.1 | 525.2 | 483.5 | 506.2 | 482.1 | 479.2 | 478.2 | 481.3 | 655.6 | 436.6 | 430.4
2546.1 | 2407.1 | 525.2 | 483.6 | 506.2 | 482.1 | 479.3 | 478.3 | 481.3 | 676.5 | 437.6 | 430.5
2547.1 | 2408.1 | 525.3 | 483.6 | 506.2 | 482.1 | 479.4 | 478.3 | 481.4 | 645.5 | 437.8 | 430.5
2548.1 | 2409.1 | 525.3 | 483.5 | 506.3 | 482.1 | 479.3 | 478.3 | 481.4 | 621.7 | 437.9 | 430.5
2549.1 | 2410.1 | 525.4 | 483.6 | 506.2 | 482.1 | 479.4 | 478.4 | 481.4 | 603.7 | 438 | 430.5
2550.1 | 2411.1 | 525.4 | 483.6 | 506.2 | 482.2 | 479.5 | 478.4 | 481.5 | 589.4 | 438 | 430.5
2551.1 | 2412.1 | 525.4 | 483.6 | 506.2 | 482.2 | 479.5 | 478.4 | 481.5 | 577.9 | 438 | 430.5
2552.1 | 2413.1 | 525.5 | 483.6 | 506.3 | 482.2 | 479.5 | 478.4 | 481.6 | 568.3 | 438.1 | 430.6
2553.1 | 2414.1 | 525.5 | 483.6 | 506.2 | 482.2 | 479.6 | 478.5 | 481.6 | 560.2 | 438.1 | 430.6
2554.1 | 2415.1 | 525.5 | 483.6 | 506.2 | 482.2 | 479.6 | 478.5 | 481.6 | 553.2 | 438.1 | 430.6
2555.1 | 2416.1 | 525.6 | 483.6 | 506.3 | 482.2 | 479.6 | 478.5 | 481.7 | 547.1 | 438.1 | 430.6
2556.1 | 2417.1 | 525.6 | 483.7 | 506.2 | 482.2 | 479.7 | 478.6 | 481.7 | 541.7 | 438.1 | 430.6
2557.1 | 2418.1 | 525.6 | 483.7 | 506.2 | 482.2 | 479.8 | 478.6 | 481.7 | 536.9 | 438.1 | 430.7
2558.1 | 2419.1 | 525.7 | 483.7 | 506.3 | 482.2 | 479.7 | 478.6 | 481.8 | 532.7 | 438.2 | 430.7
2559.1 | 2420.1 | 525.7 | 483.7 | 506.4 | 482.2 | 479.7 | 478.7 | 481.8 | 528.9 | 438.2 | 430.7
2560.1 | 2421.1 | 525.7 | 483.7 | 506.3 | 482.3 | 479.8 | 478.7 | 481.8 | 525.4 | 438.2 | 430.7
2561.1 | 2422.1 | 525.7 | 483.7 | 506.3 | 482.3 | 479.9 | 478.7 | 481.8 | 522.4 | 438.2 | 430.7
2562.1 | 2423.1 | 525.7 | 483.7 | 506.4 | 482.2 | 479.8 | 478.7 | 481.9 | 519.5 | 438.3 | 430.8
2563.1 | 2424.1 | 525.7 | 483.7 | 506.4 | 482.3 | 479.9 | 478.8 | 481.9 | 517 | 438.3 | 430.8
2564.1 | 2425.1 | 525.7 | 483.7 | 506.4 | 482.3 | 480 | 478.9 | 482 | 515.3 | 438 | 430.8
2565.1 | 2426.1 | 525.7 | 483.7 | 506.5 | 482.3 | 479.9 | 478.9 | 482 | 553 | 437.5 | 430.9
2566.1 | 2427.1 | 525.8 | 483.7 | 506.5 | 482.3 | 479.9 | 478.9 | 482.1 | 577 | 437.5 | 430.9
2567.1 | 2428.1 | 525.8 | 483.8 | 506.4 | 482.3 | 480.1 | 479 | 482.1 | 602.9 | 437.1 | 430.9
2568.1 | 2429.1 | 525.8 | 483.8 | 506.4 | 482.3 | 480.1 | 479 | 482.1 | 634.2 | 437.4 | 430.9
2569.1 | 2430.1 | 525.9 | 483.7 | 506.5 | 482.3 | 480.1 | 479 | 482.2 | 616.7 | 438.1 | 430.9
2570.1 | 2431.1 | 525.8 | 483.8 | 506.5 | 482.4 | 480.2 | 479.1 | 482.2 | 605.1 | 437.3 | 430.9
2571.1 | 2432.1 | 525.8 | 483.8 | 506.4 | 482.4 | 480.3 | 479.1 | 482.3 | 637.8 | 437.8 | 431
2572.1 | 2433.1 | 525.7 | 483.8 | 506.5 | 482.4 | 480.2 | 479.2 | 482.3 | 615.2 | 438.1 | 431
2573.1 | 2434.1 | 525.7 | 483.8 | 506.5 | 482.4 | 480.3 | 479.2 | 482.4 | 615.5 | 437.3 | 431
2574.1 | 2435.1 | 525.7 | 483.9 | 506.5 | 482.4 | 480.4 | 479.3 | 482.4 | 639.9 | 438.1 | 431
2575.1 | 2436.1 | 525.6 | 483.9 | 506.5 | 482.4 | 480.4 | 479.3 | 482.4 | 614.3 | 438.2 | 431
2576.1 | 2437.1 | 525.6 | 483.8 | 506.6 | 482.4 | 480.3 | 479.3 | 482.5 | 627.4 | 436.8 | 431.1
2577.1 | 2438.1 | 525.6 | 483.9 | 506.6 | 482.4 | 480.5 | 479.4 | 482.5 | 638.5 | 438.2 | 431.1
2578.1 | 2439.1 | 525.6 | 483.9 | 506.5 | 482.4 | 480.5 | 479.4 | 482.5 | 613.7 | 437.9 | 431.1
2579.1 | 2440.1 | 525.6 | 483.8 | 506.6 | 482.4 | 480.5 | 479.4 | 482.6 | 639.4 | 437.3 | 431.1
2580.1 | 2441.1 | 525.6 | 483.8 | 506.6 | 482.4 | 480.5 | 479.5 | 482.6 | 635.5 | 438.3 | 431.1
2581.1 | 2442.1 | 525.6 | 483.9 | 506.6 | 482.5 | 480.6 | 479.6 | 482.6 | 615.7 | 437.7 | 431.1
2582.1 | 2443.1 | 525.6 | 483.9 | 506.5 | 482.5 | 480.7 | 479.6 | 482.7 | 646.2 | 437.4 | 431.1
2583.1 | 2444.1 | 525.6 | 483.9 | 506.7 | 482.5 | 480.6 | 479.6 | 482.7 | 661.7 | 437.4 | 431.2
2584.1 | 2445.1 | 525.6 | 483.9 | 506.6 | 482.5 | 480.8 | 479.7 | 482.8 | 672.6 | 437.4 | 431.2
2585.1 | 2446.1 | 525.6 | 484 | 506.6 | 482.5 | 480.9 | 479.7 | 482.8 | 685.7 | 437.7 | 431.2
2586.1 | 2447.1 | 525.6 | 483.9 | 506.6 | 482.5 | 480.8 | 479.7 | 482.8 | 655.9 | 438.3 | 431.2
2587.1 | 2448.1 | 525.6 | 483.9 | 506.7 | 482.5 | 480.8 | 479.8 | 482.9 | 648.4 | 437.3 | 431.2
2588.1 | 2449.1 | 525.6 | 484 | 506.6 | 482.5 | 481 | 479.8 | 482.9 | 664.9 | 438 | 431.2
2589.1 | 2450.1 | 525.6 | 484 | 506.6 | 482.5 | 481 | 479.9 | 482.9 | 637.6 | 438.4 | 431.2
2590.1 | 2451.1 | 525.6 | 484 | 506.7 | 482.5 | 480.9 | 479.9 | 483 | 616.3 | 438.4 | 431.3
2591.1 | 2452.1 | 525.5 | 484 | 506.7 | 482.6 | 481.1 | 479.9 | 483 | 599.9 | 438.5 | 431.3
2592.1 | 2453.1 | 525.5 | 484.1 | 506.7 | 482.6 | 481.1 | 480 | 483 | 586.8 | 438.5 | 431.3
2593.1 | 2454.1 | 525.5 | 484 | 506.7 | 482.6 | 481.1 | 480 | 483.1 | 576.1 | 438.6 | 431.3
2594.1 | 2455.1 | 525.5 | 484 | 506.7 | 482.6 | 481.1 | 480 | 483.1 | 567.1 | 438.6 | 431.3
2595.1 | 2456.1 | 525.5 | 484.1 | 506.7 | 482.6 | 481.3 | 480.1 | 483.1 | 559.5 | 438.6 | 431.3
2596.1 | 2457.1 | 525.5 | 484.1 | 506.7 | 482.6 | 481.3 | 480.2 | 483.1 | 552.9 | 438.6 | 431.3
2597.1 | 2458.1 | 525.5 | 484 | 506.8 | 482.6 | 481.3 | 480.2 | 483.2 | 547.1 | 438.7 | 431.4
2598.1 | 2459.1 | 525.5 | 484.1 | 506.7 | 482.6 | 481.4 | 480.2 | 483.2 | 542 | 438.7 | 431.4
2599.1 | 2460.1 | 525.5 | 484.1 | 506.7 | 482.6 | 481.5 | 480.3 | 483.2 | 537.4 | 438.7 | 431.4
2600.1 | 2461.1 | 525.5 | 484.1 | 506.8 | 482.6 | 481.4 | 480.3 | 483.3 | 533.3 | 438.8 | 431.4
2601.1 | 2462.1 | 525.5 | 484.1 | 506.8 | 482.6 | 481.5 | 480.3 | 483.3 | 529.7 | 438.8 | 431.4
2602.1 | 2463.1 | 525.5 | 484.1 | 506.7 | 482.6 | 481.6 | 480.4 | 483.3 | 526.5 | 438.8 | 431.4
2603.1 | 2464.1 | 525.5 | 484.1 | 506.7 | 482.6 | 481.6 | 480.5 | 483.4 | 523.6 | 438.9 | 431.5
2604.1 | 2465.1 | 525.6 | 484.1 | 506.8 | 482.6 | 481.5 | 480.4 | 483.4 | 520.9 | 438.9 | 431.5
2605.1 | 2466.1 | 525.6 | 484.1 | 506.8 | 482.6 | 481.6 | 480.5 | 483.4 | 518.3 | 438.9 | 431.5
2606.1 | 2467.1 | 525.6 | 484.2 | 506.8 | 482.6 | 481.7 | 480.6 | 483.5 | 516.7 | 438.7 | 431.5
2607.1 | 2468.1 | 525.5 | 484.2 | 506.9 | 482.6 | 481.7 | 480.6 | 483.5 | 549.4 | 438 | 431.6
2608.1 | 2469.1 | 525.5 | 484.2 | 506.9 | 482.6 | 481.7 | 480.6 | 483.5 | 571.3 | 438 | 431.6
2609.1 | 2470.1 | 525.5 | 484.2 | 506.8 | 482.7 | 481.9 | 480.7 | 483.5 | 595.1 | 438.2 | 431.6
2610.1 | 2471.1 | 525.5 | 484.2 | 506.8 | 482.7 | 481.9 | 480.8 | 483.6 | 623.6 | 437.9 | 431.6
2611.1 | 2472.1 | 525.5 | 484.2 | 506.9 | 482.6 | 481.8 | 480.8 | 483.6 | 608.5 | 438.8 | 431.6
2612.1 | 2473.1 | 525.4 | 484.2 | 506.9 | 482.7 | 482 | 480.8 | 483.7 | 598.6 | 438 | 431.6
2613.1 | 2474.1 | 525.4 | 484.2 | 506.8 | 482.7 | 482 | 480.9 | 483.7 | 628.7 | 438.4 | 431.7
2614.1 | 2475.1 | 525.4 | 484.2 | 506.9 | 482.7 | 482 | 480.9 | 483.7 | 608.5 | 438.8 | 431.7
2615.1 | 2476.1 | 525.4 | 484.2 | 506.9 | 482.7 | 482 | 480.9 | 483.8 | 609.3 | 437.7 | 431.7
2616.1 | 2477.1 | 525.3 | 484.3 | 506.9 | 482.7 | 482.1 | 481 | 483.8 | 631.9 | 438.7 | 431.7
2617.1 | 2478.1 | 525.3 | 484.3 | 506.9 | 482.7 | 482.2 | 481.1 | 483.8 | 608.6 | 438.7 | 431.7
2618.1 | 2479.1 | 525.3 | 484.2 | 507 | 482.7 | 482.1 | 481.1 | 483.9 | 621.4 | 437.9 | 431.8
2619.1 | 2480.1 | 525.3 | 484.3 | 506.9 | 482.7 | 482.3 | 481.1 | 483.9 | 631.4 | 438.8 | 431.8
2620.1 | 2481.1 | 525.2 | 484.3 | 506.9 | 482.7 | 482.3 | 481.2 | 483.9 | 608.8 | 438.6 | 431.8
2621.1 | 2482.1 | 525.2 | 484.3 | 506.9 | 482.7 | 482.3 | 481.2 | 483.9 | 633.2 | 438.2 | 431.8
2622.1 | 2483.1 | 525.2 | 484.3 | 506.9 | 482.7 | 482.4 | 481.3 | 484 | 629.5 | 438.9 | 431.8
2623.1 | 2484.1 | 525.1 | 484.4 | 506.9 | 482.7 | 482.5 | 481.3 | 484 | 611.2 | 438.4 | 431.8
2624.1 | 2485.1 | 525.1 | 484.4 | 506.9 | 482.7 | 482.5 | 481.4 | 484 | 640 | 438.2 | 431.9
2625.1 | 2486.1 | 525.1 | 484.3 | 507 | 482.7 | 482.5 | 481.4 | 484.1 | 654.6 | 437.9 | 431.9
2626.1 | 2487.1 | 525.1 | 484.4 | 506.9 | 482.8 | 482.6 | 481.5 | 484.1 | 665 | 438.4 | 431.9
2627.1 | 2488.1 | 525.1 | 484.4 | 506.9 | 482.8 | 482.7 | 481.5 | 484.1 | 677.8 | 438.7 | 431.9
2628.1 | 2489.1 | 525.1 | 484.4 | 507 | 482.8 | 482.6 | 481.5 | 484.2 | 649.8 | 439 | 431.9
2629.1 | 2490.1 | 525.2 | 484.4 | 507 | 482.8 | 482.7 | 481.6 | 484.2 | 643.4 | 438.3 | 432
2630.1 | 2491.1 | 525.2 | 484.4 | 506.9 | 482.8 | 482.8 | 481.6 | 484.2 | 659.3 | 439 | 431.9
2631.1 | 2492.1 | 525.3 | 484.5 | 506.9 | 482.8 | 482.8 | 481.7 | 484.2 | 633.3 | 439.1 | 432
2632.1 | 2493.1 | 525.3 | 484.4 | 507.1 | 482.8 | 482.7 | 481.7 | 484.3 | 612.9 | 439.2 | 432
2633.1 | 2494.1 | 525.3 | 484.5 | 507 | 482.8 | 482.8 | 481.7 | 484.3 | 597.3 | 439.2 | 432
2634.1 | 2495.1 | 525.4 | 484.5 | 507 | 482.8 | 482.9 | 481.8 | 484.4 | 584.8 | 439.2 | 432
2635.1 | 2496.1 | 525.4 | 484.5 | 507.1 | 482.8 | 482.9 | 481.8 | 484.4 | 574.5 | 439.3 | 432.1
2636.1 | 2497.1 | 525.4 | 484.5 | 507 | 482.8 | 482.9 | 481.9 | 484.4 | 565.9 | 439.3 | 432.1
2637.1 | 2498.1 | 525.4 | 484.5 | 506.9 | 482.8 | 483.1 | 482 | 484.5 | 558.5 | 439.3 | 432.1
2638.1 | 2499.1 | 525.4 | 484.5 | 507 | 482.8 | 483.1 | 482 | 484.5 | 552.1 | 439.4 | 432.1
2639.1 | 2500.1 | 525.4 | 484.5 | 507.1 | 482.8 | 483 | 482 | 484.5 | 546.6 | 439.4 | 432.1
2640.1 | 2501.1 | 525.4 | 484.5 | 507 | 482.8 | 483.2 | 482.1 | 484.6 | 541.8 | 439.4 | 432.1
2641.1 | 2502.1 | 525.4 | 484.6 | 507 | 482.8 | 483.2 | 482.1 | 484.6 | 537.5 | 439.5 | 432.1
2642.1 | 2503.1 | 525.4 | 484.5 | 507.1 | 482.8 | 483.2 | 482.1 | 484.7 | 533.6 | 439.5 | 432.2
2643.1 | 2504.1 | 525.4 | 484.6 | 507 | 482.8 | 483.2 | 482.2 | 484.7 | 530.1 | 439.5 | 432.2
2644.1 | 2505.1 | 525.4 | 484.6 | 507 | 482.9 | 483.4 | 482.2 | 484.7 | 527 | 439.5 | 432.2
2645.1 | 2506.1 | 525.4 | 484.6 | 507 | 482.8 | 483.4 | 482.3 | 484.7 | 524.1 | 439.6 | 432.2
2646.1 | 2507.1 | 525.3 | 484.6 | 507.1 | 482.8 | 483.3 | 482.3 | 484.8 | 521.5 | 439.6 | 432.3
2647.1 | 2508.1 | 525.3 | 484.6 | 507.1 | 482.9 | 483.5 | 482.4 | 484.8 | 519.1 | 439.6 | 432.3
2648.1 | 2509.1 | 525.3 | 484.7 | 507 | 482.9 | 483.6 | 482.4 | 484.9 | 517.6 | 439.4 | 432.3
2649.1 | 2510.1 | 525.3 | 484.6 | 507.1 | 482.8 | 483.5 | 482.4 | 484.9 | 549.5 | 439.1 | 432.3
2650.1 | 2511.1 | 525.3 | 484.6 | 507.1 | 482.8 | 483.5 | 482.5 | 485 | 570.4 | 439 | 432.4
2651.1 | 2512.1 | 525.3 | 484.7 | 507.1 | 482.9 | 483.6 | 482.5 | 485 | 593.2 | 438.8 | 432.3
2652.1 | 2513.1 | 525.3 | 484.7 | 507.1 | 482.9 | 483.7 | 482.6 | 485 | 620.4 | 439 | 432.4
2653.1 | 2514.1 | 525.4 | 484.6 | 507.2 | 482.8 | 483.6 | 482.6 | 485.1 | 605.9 | 439.5 | 432.4
2654.1 | 2515.1 | 525.4 | 484.7 | 507.1 | 482.9 | 483.8 | 482.7 | 485.1 | 596.7 | 438.8 | 432.4
2655.1 | 2516.1 | 525.3 | 484.7 | 507.1 | 482.9 | 483.8 | 482.7 | 485.2 | 625.1 | 439.2 | 432.4
2656.1 | 2517.1 | 525.3 | 484.7 | 507.1 | 482.9 | 483.8 | 482.7 | 485.2 | 605.8 | 439.6 | 432.4
2657.1 | 2518.1 | 525.3 | 484.7 | 507.2 | 482.9 | 483.8 | 482.8 | 485.3 | 606.9 | 438.7 | 432.5
2658.1 | 2519.1 | 525.3 | 484.8 | 507.1 | 482.9 | 484 | 482.9 | 485.3 | 628.1 | 439.5 | 432.5
2659.1 | 2520.1 | 525.3 | 484.8 | 507.1 | 482.9 | 484 | 482.9 | 485.3 | 605.8 | 439.5 | 432.5
2660.1 | 2521.1 | 525.3 | 484.7 | 507.2 | 482.9 | 483.9 | 482.9 | 485.4 | 618.6 | 438.9 | 432.5
2661.1 | 2522.1 | 525.4 | 484.8 | 507.1 | 482.9 | 484.1 | 483 | 485.4 | 627.5 | 439.6 | 432.5
2662.1 | 2523.1 | 525.4 | 484.8 | 507.1 | 482.9 | 484.1 | 483 | 485.5 | 606 | 439.5 | 432.6
2663.1 | 2524.1 | 525.4 | 484.8 | 507.2 | 482.9 | 484.1 | 483.1 | 485.5 | 629.7 | 439.1 | 432.6
2664.1 | 2525.1 | 525.4 | 484.8 | 507.2 | 482.9 | 484.1 | 483.1 | 485.6 | 625.7 | 439.7 | 432.6
2665.1 | 2526.1 | 525.4 | 484.8 | 507.2 | 482.9 | 484.2 | 483.2 | 485.6 | 608.6 | 439.3 | 432.6
2666.1 | 2527.1 | 525.5 | 484.8 | 507.2 | 483 | 484.3 | 483.2 | 485.6 | 636.3 | 439.4 | 432.6
2667.1 | 2528.1 | 525.5 | 484.8 | 507.3 | 482.9 | 484.2 | 483.2 | 485.7 | 650.2 | 439 | 432.7
2668.1 | 2529.1 | 525.5 | 484.8 | 507.2 | 483 | 484.3 | 483.3 | 485.7 | 660.7 | 439.1 | 432.7
2669.1 | 2530.1 | 525.5 | 484.9 | 507.1 | 483 | 484.4 | 483.3 | 485.7 | 673.2 | 439.5 | 432.7
2670.1 | 2531.1 | 525.5 | 484.8 | 507.3 | 483 | 484.4 | 483.3 | 485.8 | 646.2 | 439.8 | 432.7
2671.1 | 2532.1 | 525.5 | 484.8 | 507.3 | 482.9 | 484.4 | 483.4 | 485.8 | 640.6 | 439.1 | 432.7
2672.1 | 2533.1 | 525.5 | 484.9 | 507.2 | 483 | 484.5 | 483.5 | 485.8 | 655.6 | 439.8 | 432.7
2673.1 | 2534.1 | 525.5 | 484.9 | 507.3 | 483 | 484.5 | 483.5 | 485.9 | 630.5 | 439.9 | 432.7
2674.1 | 2535.1 | 525.5 | 484.8 | 507.4 | 483 | 484.4 | 483.5 | 485.9 | 611 | 440 | 432.8
2675.1 | 2536.1 | 525.5 | 484.9 | 507.3 | 483 | 484.6 | 483.6 | 486 | 596 | 440 | 432.8
2676.1 | 2537.1 | 525.5 | 484.9 | 507.3 | 483 | 484.7 | 483.6 | 486 | 583.9 | 440.1 | 432.8
2677.1 | 2538.1 | 525.6 | 484.9 | 507.4 | 483 | 484.6 | 483.6 | 486 | 573.9 | 440.1 | 432.8
2678.1 | 2539.1 | 525.5 | 484.9 | 507.4 | 483 | 484.6 | 483.7 | 486.1 | 565.6 | 440.1 | 432.9
2679.1 | 2540.1 | 525.5 | 485 | 507.3 | 483 | 484.8 | 483.8 | 486.1 | 558.4 | 440.2 | 432.9
2680.1 | 2541.1 | 525.5 | 485 | 507.3 | 483 | 484.8 | 483.8 | 486.2 | 552.2 | 440.2 | 432.9
2681.1 | 2542.1 | 525.5 | 484.9 | 507.4 | 483 | 484.7 | 483.8 | 486.2 | 546.8 | 440.2 | 432.9
2682.1 | 2543.1 | 525.5 | 485 | 507.3 | 483 | 484.9 | 483.9 | 486.2 | 542 | 440.2 | 432.9
2683.1 | 2544.1 | 525.5 | 485 | 507.3 | 483.1 | 485 | 483.9 | 486.3 | 537.7 | 440.3 | 432.9
2684.1 | 2545.1 | 525.5 | 485 | 507.4 | 483 | 484.9 | 483.9 | 486.3 | 534 | 440.3 | 433
2685.1 | 2546.1 | 525.5 | 485 | 507.5 | 483 | 484.9 | 484 | 486.3 | 530.7 | 440.3 | 433
2686.1 | 2547.1 | 525.5 | 485 | 507.3 | 483.1 | 485.1 | 484.1 | 486.4 | 527.6 | 440.3 | 433
2687.1 | 2548.1 | 525.5 | 485 | 507.3 | 483.1 | 485.1 | 484.1 | 486.4 | 524.8 | 440.4 | 433
2688.1 | 2549.1 | 525.5 | 485 | 507.4 | 483.1 | 485 | 484.1 | 486.5 | 522.2 | 440.4 | 433
2689.1 | 2550.1 | 525.5 | 485 | 507.4 | 483.1 | 485.2 | 484.2 | 486.5 | 519.9 | 440.4 | 433
2690.1 | 2551.1 | 525.5 | 485.1 | 507.4 | 483.1 | 485.2 | 484.2 | 486.5 | 518.6 | 440.3 | 433
2691.1 | 2552.1 | 525.4 | 485 | 507.5 | 483.1 | 485.2 | 484.2 | 486.5 | 549.5 | 439.9 | 433.1
2692.1 | 2553.1 | 525.5 | 485 | 507.5 | 483.1 | 485.2 | 484.3 | 486.6 | 569.8 | 439.7 | 433.1
2693.1 | 2554.1 | 525.5 | 485.1 | 507.4 | 483.1 | 485.3 | 484.3 | 486.6 | 591.5 | 440 | 433.1
2694.1 | 2555.1 | 525.5 | 485.1 | 507.5 | 483.1 | 485.4 | 484.4 | 486.7 | 617.9 | 439.6 | 433.1
2695.1 | 2556.1 | 525.5 | 485.1 | 507.5 | 483.1 | 485.3 | 484.4 | 486.7 | 603.8 | 440.3 | 433.1
2696.1 | 2557.1 | 525.5 | 485.1 | 507.5 | 483.1 | 485.4 | 484.5 | 486.7 | 595.2 | 439.9 | 433.2
2697.1 | 2558.1 | 525.5 | 485.1 | 507.4 | 483.1 | 485.5 | 484.5 | 486.8 | 622.7 | 439.8 | 433.2
2698.1 | 2559.1 | 525.5 | 485.1 | 507.5 | 483.1 | 485.5 | 484.5 | 486.8 | 603.8 | 440.3 | 433.2
2699.1 | 2560.1 | 525.6 | 485.1 | 507.6 | 483.1 | 485.5 | 484.6 | 486.8 | 605.1 | 439.7 | 433.2
2700.1 | 2561.1 | 525.6 | 485.2 | 507.5 | 483.1 | 485.6 | 484.6 | 486.9 | 625.4 | 440.3 | 433.2
2701.1 | 2562.1 | 525.6 | 485.2 | 507.5 | 483.2 | 485.7 | 484.7 | 486.9 | 603.7 | 440.4 | 433.2
2702.1 | 2563.1 | 525.6 | 485.1 | 507.6 | 483.1 | 485.6 | 484.7 | 486.9 | 616.2 | 439.7 | 433.3
2703.1 | 2564.1 | 525.6 | 485.2 | 507.5 | 483.2 | 485.7 | 484.7 | 486.9 | 624.5 | 440.3 | 433.3
2704.1 | 2565.1 | 525.6 | 485.2 | 507.5 | 483.2 | 485.7 | 484.8 | 487 | 603.7 | 440.3 | 433.3
2705.1 | 2566.1 | 525.7 | 485.2 | 507.6 | 483.2 | 485.7 | 484.8 | 487 | 626.9 | 439.6 | 433.3
2706.1 | 2567.1 | 525.7 | 485.2 | 507.6 | 483.2 | 485.7 | 484.8 | 487 | 622.9 | 440.4 | 433.3
2707.1 | 2568.1 | 525.7 | 485.2 | 507.6 | 483.2 | 485.8 | 484.9 | 487 | 606.4 | 440.2 | 433.4
2708.1 | 2569.1 | 525.7 | 485.2 | 507.6 | 483.2 | 485.8 | 484.9 | 487.1 | 633.4 | 439.9 | 433.4
2709.1 | 2570.1 | 525.8 | 485.2 | 507.7 | 483.2 | 485.8 | 484.9 | 487.1 | 647.4 | 439.8 | 433.4
2710.1 | 2571.1 | 525.8 | 485.2 | 507.6 | 483.2 | 485.9 | 485 | 487.1 | 657.1 | 439.9 | 433.4
2711.1 | 2572.1 | 525.8 | 485.2 | 507.6 | 483.2 | 486 | 485 | 487.2 | 669.4 | 440 | 433.4
2712.1 | 2573.1 | 525.8 | 485.2 | 507.7 | 483.2 | 485.9 | 485.1 | 487.2 | 643.1 | 440.6 | 433.5
2713.1 | 2574.1 | 525.8 | 485.2 | 507.7 | 483.2 | 485.9 | 485.1 | 487.2 | 637.8 | 439.8 | 433.5
2714.1 | 2575.1 | 525.8 | 485.3 | 507.6 | 483.2 | 486.1 | 485.2 | 487.2 | 652.4 | 440.3 | 433.5
2715.1 | 2576.1 | 525.8 | 485.3 | 507.7 | 483.2 | 486.1 | 485.2 | 487.3 | 628 | 440.6 | 433.5
2716.1 | 2577.1 | 525.8 | 485.2 | 507.8 | 483.2 | 486 | 485.2 | 487.3 | 609.1 | 440.7 | 433.5
2717.1 | 2578.1 | 525.8 | 485.3 | 507.7 | 483.2 | 486.2 | 485.3 | 487.3 | 594.5 | 440.7 | 433.5
2718.1 | 2579.1 | 525.8 | 485.3 | 507.7 | 483.2 | 486.3 | 485.3 | 487.3 | 582.8 | 440.7 | 433.6
2719.1 | 2580.1 | 525.8 | 485.3 | 507.7 | 483.2 | 486.2 | 485.4 | 487.4 | 573.2 | 440.8 | 433.6
2720.1 | 2581.1 | 525.8 | 485.3 | 507.7 | 483.2 | 486.2 | 485.4 | 487.4 | 565 | 440.8 | 433.6
2721.1 | 2582.1 | 525.8 | 485.4 | 507.7 | 483.2 | 486.3 | 485.5 | 487.4 | 558 | 440.9 | 433.6
2722.1 | 2583.1 | 525.8 | 485.4 | 507.7 | 483.2 | 486.4 | 485.5 | 487.5 | 552 | 440.9 | 433.6
2723.1 | 2584.1 | 525.8 | 485.3 | 507.8 | 483.2 | 486.3 | 485.5 | 487.5 | 546.8 | 440.9 | 433.7
2724.1 | 2585.1 | 525.8 | 485.4 | 507.7 | 483.3 | 486.5 | 485.6 | 487.6 | 542.2 | 440.9 | 433.7
2725.1 | 2586.1 | 525.8 | 485.4 | 507.7 | 483.2 | 486.5 | 485.6 | 487.6 | 538 | 440.9 | 433.7
2726.1 | 2587.1 | 525.7 | 485.4 | 507.8 | 483.2 | 486.5 | 485.6 | 487.6 | 534.4 | 441 | 433.7
2727.1 | 2588.1 | 525.7 | 485.4 | 507.8 | 483.2 | 486.5 | 485.7 | 487.7 | 531.1 | 441 | 433.8
2728.1 | 2589.1 | 525.7 | 485.4 | 507.8 | 483.3 | 486.6 | 485.7 | 487.7 | 528 | 441 | 433.8
2729.1 | 2590.1 | 525.7 | 485.5 | 507.8 | 483.3 | 486.7 | 485.8 | 487.7 | 525.3 | 441 | 433.8
2730.1 | 2591.1 | 525.7 | 485.4 | 507.9 | 483.2 | 486.6 | 485.8 | 487.8 | 522.9 | 441 | 433.8
2731.1 | 2592.1 | 525.6 | 485.5 | 507.8 | 483.3 | 486.7 | 485.9 | 487.8 | 520.6 | 441 | 433.8
2732.1 | 2593.1 | 525.6 | 485.5 | 507.7 | 483.3 | 486.8 | 485.9 | 487.8 | 519.3 | 440.7 | 433.8
2733.1 | 2594.1 | 525.6 | 485.5 | 507.8 | 483.3 | 486.8 | 485.9 | 487.9 | 549.8 | 440.4 | 433.9
2734.1 | 2595.1 | 525.6 | 485.5 | 507.8 | 483.2 | 486.8 | 485.9 | 487.9 | 570.2 | 440.2 | 433.9
2735.1 | 2596.1 | 525.6 | 485.5 | 507.8 | 483.3 | 486.9 | 486 | 487.9 | 591.3 | 440 | 433.9
2736.1 | 2597.1 | 525.6 | 485.5 | 507.8 | 483.3 | 486.9 | 486.1 | 488 | 616.9 | 440.3 | 433.9
2737.1 | 2598.1 | 525.7 | 485.5 | 507.9 | 483.3 | 486.8 | 486.1 | 488 | 602.8 | 440.8 | 434
2738.1 | 2599.1 | 525.7 | 485.5 | 507.9 | 483.3 | 487 | 486.1 | 488 | 594.3 | 440.2 | 434
2739.1 | 2600.1 | 525.7 | 485.5 | 507.9 | 483.3 | 487 | 486.2 | 488.1 | 621.2 | 440.5 | 434
2740.1 | 2601.1 | 525.7 | 485.5 | 507.9 | 483.3 | 487 | 486.2 | 488.1 | 602.7 | 440.9 | 434
2741.1 | 2602.1 | 525.7 | 485.5 | 507.9 | 483.3 | 487 | 486.2 | 488.2 | 604.2 | 440 | 434
2742.1 | 2603.1 | 525.7 | 485.6 | 507.9 | 483.3 | 487.2 | 486.3 | 488.2 | 624.1 | 440.8 | 434.1
2743.1 | 2604.1 | 525.7 | 485.6 | 507.9 | 483.3 | 487.2 | 486.4 | 488.2 | 603 | 441 | 434.1
2744.1 | 2605.1 | 525.7 | 485.5 | 508 | 483.3 | 487.1 | 486.4 | 488.3 | 615.3 | 440.2 | 434.1
2745.1 | 2606.1 | 525.7 | 485.6 | 507.9 | 483.3 | 487.2 | 486.4 | 488.3 | 623.3 | 440.9 | 434.1
2746.1 | 2607.1 | 525.7 | 485.6 | 507.9 | 483.3 | 487.3 | 486.5 | 488.4 | 603 | 441 | 434.1
2747.1 | 2608.1 | 525.7 | 485.6 | 508 | 483.3 | 487.3 | 486.5 | 488.4 | 625.7 | 440.4 | 434.2
2748.1 | 2609.1 | 525.7 | 485.6 | 508 | 483.3 | 487.3 | 486.5 | 488.4 | 621.4 | 441 | 434.2
2749.1 | 2610.1 | 525.7 | 485.6 | 507.9 | 483.3 | 487.4 | 486.6 | 488.5 | 605.3 | 440.8 | 434.2
2750.1 | 2611.1 | 525.7 | 485.6 | 507.9 | 483.4 | 487.5 | 486.7 | 488.5 | 631.5 | 440.3 | 434.2
2751.1 | 2612.1 | 525.8 | 485.6 | 508.1 | 483.3 | 487.4 | 486.6 | 488.6 | 645.4 | 440.2 | 434.2
2752.1 | 2613.1 | 525.8 | 485.7 | 508 | 483.4 | 487.5 | 486.7 | 488.6 | 654.9 | 440.7 | 434.2
2753.1 | 2614.1 | 525.8 | 485.7 | 507.9 | 483.4 | 487.6 | 486.8 | 488.6 | 667.1 | 440.9 | 434.2
2754.1 | 2615.1 | 525.8 | 485.7 | 508 | 483.4 | 487.6 | 486.8 | 488.6 | 641.3 | 441.2 | 434.3
2755.1 | 2616.1 | 525.8 | 485.6 | 508 | 483.3 | 487.6 | 486.8 | 488.7 | 636.5 | 440.6 | 434.3
2756.1 | 2617.1 | 525.8 | 485.7 | 507.9 | 483.4 | 487.7 | 486.9 | 488.7 | 650.7 | 441.1 | 434.3
2757.1 | 2618.1 | 525.7 | 485.7 | 507.9 | 483.4 | 487.8 | 487 | 488.7 | 626.7 | 441.2 | 434.3
2758.1 | 2619.1 | 525.7 | 485.7 | 508.1 | 483.3 | 487.7 | 486.9 | 488.8 | 608.2 | 441.3 | 434.3
2759.1 | 2620.1 | 525.6 | 485.7 | 508 | 483.4 | 487.8 | 487 | 488.8 | 593.8 | 441.4 | 434.3
2760.1 | 2621.1 | 525.6 | 485.8 | 508 | 483.4 | 487.9 | 487.1 | 488.8 | 582.3 | 441.4 | 434.3
2761.1 | 2622.1 | 525.6 | 485.7 | 508 | 483.4 | 487.9 | 487.1 | 488.9 | 572.9 | 441.4 | 434.4
2762.1 | 2623.1 | 525.5 | 485.7 | 508 | 483.4 | 487.9 | 487.1 | 488.9 | 564.9 | 441.5 | 434.4
2763.1 | 2624.1 | 525.5 | 485.8 | 508 | 483.4 | 488 | 487.2 | 488.9 | 558.1 | 441.5 | 434.4
2764.1 | 2625.1 | 525.5 | 485.8 | 508 | 483.4 | 488.1 | 487.3 | 488.9 | 552.2 | 441.5 | 434.4
2765.1 | 2626.1 | 525.5 | 485.7 | 508.1 | 483.4 | 488 | 487.2 | 489 | 547.1 | 441.5 | 434.5
2766.1 | 2627.1 | 525.5 | 485.8 | 508 | 483.4 | 488.1 | 487.3 | 489 | 542.5 | 441.5 | 434.5
2767.1 | 2628.1 | 525.5 | 485.8 | 508 | 483.4 | 488.2 | 487.4 | 489.1 | 538.5 | 441.5 | 434.5
2768.1 | 2629.1 | 525.5 | 485.8 | 508.1 | 483.4 | 488.1 | 487.4 | 489.1 | 534.9 | 441.6 | 434.5
2769.1 | 2630.1 | 525.6 | 485.8 | 508.1 | 483.4 | 488.1 | 487.4 | 489.2 | 531.6 | 441.6 | 434.5
2770.1 | 2631.1 | 525.6 | 485.8 | 508.1 | 483.4 | 488.2 | 487.5 | 489.2 | 528.7 | 441.6 | 434.5
2771.1 | 2632.1 | 525.6 | 485.8 | 508.1 | 483.4 | 488.3 | 487.5 | 489.2 | 526.1 | 441.7 | 434.6
2772.1 | 2633.1 | 525.6 | 485.8 | 508.1 | 483.4 | 488.2 | 487.5 | 489.3 | 523.6 | 441.7 | 434.6
2773.1 | 2634.1 | 525.6 | 485.8 | 508 | 483.5 | 488.3 | 487.6 | 489.3 | 521.4 | 441.7 | 434.6
2774.1 | 2635.1 | 525.6 | 485.9 | 508 | 483.5 | 488.4 | 487.7 | 489.3 | 520.1 | 441.4 | 434.6
2775.1 | 2636.1 | 525.6 | 485.8 | 508.1 | 483.4 | 488.4 | 487.7 | 489.4 | 550.5 | 441.2 | 434.6
2776.1 | 2637.1 | 525.6 | 485.8 | 508.2 | 483.4 | 488.4 | 487.7 | 489.4 | 569.9 | 441.1 | 434.7
2777.1 | 2638.1 | 525.6 | 485.9 | 508.1 | 483.5 | 488.5 | 487.8 | 489.4 | 590.7 | 441 | 434.6
2778.1 | 2639.1 | 525.6 | 485.9 | 508.1 | 483.5 | 488.5 | 487.8 | 489.4 | 615.4 | 441.1 | 434.7
2779.1 | 2640.1 | 525.6 | 485.9 | 508.2 | 483.5 | 488.5 | 487.8 | 489.5 | 601.3 | 441.6 | 434.7
2780.1 | 2641.1 | 525.6 | 485.9 | 508.1 | 483.5 | 488.6 | 487.9 | 489.5 | 593.1 | 441.2 | 434.7
2781.1 | 2642.1 | 525.6 | 485.9 | 508.1 | 483.5 | 488.7 | 487.9 | 489.5 | 618.5 | 441.3 | 434.7
2782.1 | 2643.1 | 525.6 | 485.9 | 508.2 | 483.5 | 488.6 | 487.9 | 489.5 | 600.5 | 441.6 | 434.8
2783.1 | 2644.1 | 525.6 | 485.9 | 508.2 | 483.5 | 488.6 | 488 | 489.5 | 602 | 441 | 434.8
2784.1 | 2645.1 | 525.7 | 485.9 | 508.2 | 483.5 | 488.7 | 488 | 489.6 | 620.8 | 441.5 | 434.8
2785.1 | 2646.1 | 525.7 | 486 | 508.2 | 483.5 | 488.8 | 488.1 | 489.6 | 600.6 | 441.5 | 434.8
2786.1 | 2647.1 | 525.7 | 485.9 | 508.3 | 483.5 | 488.7 | 488.1 | 489.6 | 613.1 | 440.9 | 434.9
2787.1 | 2648.1 | 525.7 | 486 | 508.2 | 483.5 | 488.8 | 488.1 | 489.6 | 620.3 | 441.6 | 434.8
2788.1 | 2649.1 | 525.7 | 486 | 508.3 | 483.5 | 488.9 | 488.2 | 489.7 | 601 | 441.5 | 434.9
2789.1 | 2650.1 | 525.7 | 486 | 508.3 | 483.5 | 488.8 | 488.2 | 489.7 | 623.4 | 441.1 | 434.9
2790.1 | 2651.1 | 525.7 | 486 | 508.3 | 483.5 | 488.8 | 488.2 | 489.7 | 619 | 441.7 | 434.9
2791.1 | 2652.1 | 525.7 | 486 | 508.3 | 483.5 | 489 | 488.3 | 489.7 | 604 | 441.2 | 434.9
2792.1 | 2653.1 | 525.7 | 486 | 508.3 | 483.5 | 489 | 488.3 | 489.8 | 629.5 | 441.3 | 435
2793.1 | 2654.1 | 525.7 | 486 | 508.4 | 483.5 | 488.9 | 488.3 | 489.8 | 642.8 | 440.9 | 435
2794.1 | 2655.1 | 525.7 | 486 | 508.3 | 483.5 | 489 | 488.4 | 489.8 | 652.1 | 441.1 | 435
2795.1 | 2656.1 | 525.6 | 486 | 508.2 | 483.5 | 489.1 | 488.5 | 489.9 | 663.8 | 441.4 | 435
2796.1 | 2657.1 | 525.6 | 485.8 | 508.6 | 483.4 | 488.7 | 488.3 | 490 | 638.8 | 441.9 | 435.1
2797.1 | 2658.1 | 525.6 | 485.6 | 509 | 483.3 | 488.3 | 488.2 | 490.1 | 634.8 | 441.2 | 435.2
2798.1 | 2659.1 | 525.6 | 485.6 | 508.9 | 483.3 | 488.4 | 488.3 | 490.1 | 648.3 | 441.9 | 435.2
2799.1 | 2660.1 | 525.6 | 485.6 | 509 | 483.3 | 488.4 | 488.3 | 490.1 | 625 | 442 | 435.2
2800.1 | 2661.1 | 525.6 | 485.6 | 509.1 | 483.3 | 488.3 | 488.3 | 490.2 | 607.1 | 442.1 | 435.3
2801.1 | 2662.1 | 525.6 | 485.6 | 509 | 483.3 | 488.4 | 488.4 | 490.2 | 593.1 | 442.2 | 435.3
2802.1 | 2663.1 | 525.6 | 485.7 | 509 | 483.3 | 488.5 | 488.4 | 490.3 | 582 | 442.2 | 435.3
2803.1 | 2664.1 | 525.6 | 485.7 | 509 | 483.3 | 488.6 | 488.5 | 490.3 | 572.7 | 442.3 | 435.3
2804.1 | 2665.1 | 525.6 | 485.7 | 509 | 483.3 | 488.5 | 488.5 | 490.4 | 565 | 442.3 | 435.3
2805.1 | 2666.1 | 525.6 | 485.7 | 509 | 483.4 | 488.6 | 488.6 | 490.4 | 558.3 | 442.4 | 435.3
2806.1 | 2667.1 | 525.5 | 485.7 | 509 | 483.4 | 488.7 | 488.6 | 490.4 | 552.5 | 442.4 | 435.3
2807.1 | 2668.1 | 525.5 | 485.7 | 509.1 | 483.4 | 488.6 | 488.6 | 490.5 | 547.4 | 442.5 | 435.4
2808.1 | 2669.1 | 525.5 | 485.7 | 509 | 483.4 | 488.8 | 488.7 | 490.5 | 542.9 | 442.5 | 435.4
2809.1 | 2670.1 | 525.5 | 485.7 | 509 | 483.4 | 488.8 | 488.7 | 490.5 | 539 | 442.5 | 435.4
2810.1 | 2671.1 | 525.5 | 485.7 | 509 | 483.4 | 488.8 | 488.8 | 490.6 | 535.4 | 442.6 | 435.4
2811.1 | 2672.1 | 525.5 | 485.7 | 509 | 483.4 | 488.8 | 488.8 | 490.6 | 532.3 | 442.6 | 435.4
2812.1 | 2673.1 | 525.5 | 485.7 | 509 | 483.4 | 488.9 | 488.8 | 490.6 | 529.5 | 442.6 | 435.4
2813.1 | 2674.1 | 525.5 | 485.7 | 509 | 483.4 | 488.9 | 488.9 | 490.6 | 526.8 | 442.6 | 435.5
2814.1 | 2675.1 | 525.6 | 485.7 | 509.1 | 483.4 | 488.9 | 488.9 | 490.7 | 524.5 | 442.7 | 435.5
2815.1 | 2676.1 | 525.6 | 485.7 | 509.1 | 483.4 | 489 | 488.9 | 490.7 | 522.3 | 442.7 | 435.5
2816.1 | 2677.1 | 525.6 | 485.8 | 509 | 483.4 | 489.1 | 489 | 490.7 | 521 | 442.6 | 435.5
2817.1 | 2678.1 | 525.6 | 485.8 | 509 | 483.4 | 489.1 | 489 | 490.7 | 550 | 441.8 | 435.6
2818.1 | 2679.1 | 525.6 | 485.8 | 509.1 | 483.4 | 489.1 | 489 | 490.7 | 569.2 | 442 | 435.6
2819.1 | 2680.1 | 525.6 | 485.8 | 509 | 483.4 | 489.2 | 489.1 | 490.8 | 589.3 | 441.9 | 435.6
2820.1 | 2681.1 | 525.5 | 485.8 | 509 | 483.4 | 489.2 | 489.1 | 490.8 | 613.4 | 441.7 | 435.6
2821.1 | 2682.1 | 525.5 | 485.8 | 509.1 | 483.4 | 489.2 | 489.1 | 490.8 | 599.8 | 442.5 | 435.6
2822.1 | 2683.1 | 525.5 | 485.8 | 509.1 | 483.4 | 489.3 | 489.2 | 490.8 | 592.2 | 442 | 435.7
2823.1 | 2684.1 | 525.5 | 485.8 | 509.1 | 483.4 | 489.3 | 489.2 | 490.9 | 617.2 | 442 | 435.6
2824.1 | 2685.1 | 525.5 | 485.8 | 509.1 | 483.4 | 489.3 | 489.3 | 490.9 | 599.6 | 442.6 | 435.7
2825.1 | 2686.1 | 525.4 | 485.8 | 509.2 | 483.4 | 489.3 | 489.3 | 490.9 | 601.5 | 441.9 | 435.7
2826.1 | 2687.1 | 525.5 | 485.9 | 509.1 | 483.4 | 489.4 | 489.4 | 490.9 | 619.7 | 442.3 | 435.7
2827.1 | 2688.1 | 525.5 | 485.9 | 509.1 | 483.4 | 489.5 | 489.4 | 491 | 599.8 | 442.7 | 435.7
2828.1 | 2689.1 | 525.5 | 485.8 | 509.2 | 483.4 | 489.4 | 489.4 | 491 | 612.2 | 441.8 | 435.8
2829.1 | 2690.1 | 525.5 | 485.9 | 509.1 | 483.4 | 489.5 | 489.5 | 491 | 618.8 | 442.5 | 435.8
2830.1 | 2691.1 | 525.5 | 485.9 | 509.1 | 483.5 | 489.6 | 489.5 | 491.1 | 599.9 | 442.4 | 435.8
2831.1 | 2692.1 | 525.5 | 485.9 | 509.2 | 483.4 | 489.5 | 489.6 | 491.1 | 621.8 | 442 | 435.8
2832.1 | 2693.1 | 525.5 | 485.9 | 509.2 | 483.4 | 489.6 | 489.6 | 491.1 | 617.1 | 442.6 | 435.8
2833.1 | 2694.1 | 525.5 | 485.9 | 509.2 | 483.5 | 489.7 | 489.7 | 491.2 | 602.3 | 442.2 | 435.8
2834.1 | 2695.1 | 525.5 | 485.9 | 509.2 | 483.4 | 489.7 | 489.7 | 491.2 | 627.2 | 442.3 | 435.9
2835.1 | 2696.1 | 525.5 | 485.9 | 509.3 | 483.4 | 489.7 | 489.7 | 491.2 | 640.6 | 441.9 | 435.9
2836.1 | 2697.1 | 525.5 | 485.9 | 509.2 | 483.4 | 489.8 | 489.8 | 491.3 | 649.9 | 442.1 | 435.9
2837.1 | 2698.1 | 525.4 | 486 | 509.2 | 483.5 | 489.9 | 489.8 | 491.3 | 661.4 | 442.4 | 435.9
2838.1 | 2699.1 | 525.4 | 485.9 | 509.2 | 483.5 | 489.8 | 489.9 | 491.3 | 636.6 | 442.7 | 435.9
2839.1 | 2700.1 | 525.5 | 485.9 | 509.2 | 483.5 | 489.8 | 489.9 | 491.4 | 633 | 442 | 436
2840.1 | 2701.1 | 525.5 | 486 | 509.2 | 483.5 | 490 | 490 | 491.4 | 646 | 442.7 | 436
2841.1 | 2702.1 | 525.4 | 486 | 509.2 | 483.5 | 490 | 490 | 491.4 | 623.1 | 442.8 | 436
2842.1 | 2703.1 | 525.4 | 485.9 | 509.3 | 483.5 | 489.9 | 490 | 491.5 | 605.6 | 443 | 436
2843.1 | 2704.1 | 525.4 | 486 | 509.2 | 483.5 | 490 | 490.1 | 491.5 | 592 | 443 | 436
2844.1 | 2705.1 | 525.3 | 486 | 509.2 | 483.5 | 490.1 | 490.1 | 491.5 | 581.2 | 443.1 | 436
2845.1 | 2706.1 | 525.3 | 486 | 509.3 | 483.5 | 490.1 | 490.1 | 491.6 | 572.1 | 443.1 | 436.1
2846.1 | 2707.1 | 525.3 | 485.9 | 509.3 | 483.5 | 490 | 490.2 | 491.6 | 564.6 | 443.2 | 436.1
2847.1 | 2708.1 | 525.3 | 486 | 509.3 | 483.5 | 490.2 | 490.2 | 491.7 | 558 | 443.2 | 436.1
2848.1 | 2709.1 | 525.3 | 486 | 509.3 | 483.5 | 490.2 | 490.3 | 491.7 | 552.4 | 443.2 | 436.1
2849.1 | 2710.1 | 525.3 | 486 | 509.4 | 483.5 | 490.1 | 490.3 | 491.7 | 547.5 | 443.3 | 436.2
2850.1 | 2711.1 | 525.3 | 486 | 509.3 | 483.5 | 490.3 | 490.3 | 491.8 | 543.1 | 443.3 | 436.2
2851.1 | 2712.1 | 525.3 | 486 | 509.3 | 483.5 | 490.3 | 490.4 | 491.8 | 539.2 | 443.3 | 436.2
2852.1 | 2713.1 | 525.3 | 486 | 509.3 | 483.5 | 490.3 | 490.4 | 491.8 | 535.8 | 443.3 | 436.2
2853.1 | 2714.1 | 525.3 | 486 | 509.4 | 483.5 | 490.3 | 490.5 | 491.9 | 532.7 | 443.4 | 436.2
2854.1 | 2715.1 | 525.4 | 486 | 509.3 | 483.5 | 490.4 | 490.5 | 491.9 | 529.9 | 443.4 | 436.2
2855.1 | 2716.1 | 525.4 | 486 | 509.3 | 483.6 | 490.5 | 490.6 | 491.9 | 527.4 | 443.4 | 436.3
2856.1 | 2717.1 | 525.4 | 486 | 509.4 | 483.5 | 490.4 | 490.6 | 492 | 525.1 | 443.4 | 436.3
2857.1 | 2718.1 | 525.4 | 486 | 509.4 | 483.6 | 490.5 | 490.6 | 492 | 523.1 | 443.4 | 436.3
2858.1 | 2719.1 | 525.4 | 486.1 | 509.3 | 483.6 | 490.6 | 490.7 | 492 | 521.9 | 443.4 | 436.3
2859.1 | 2720.1 | 525.4 | 486.1 | 509.4 | 483.6 | 490.6 | 490.7 | 492 | 550.7 | 442.5 | 436.3
2860.1 | 2721.1 | 525.5 | 486 | 509.4 | 483.6 | 490.6 | 490.7 | 492.1 | 569.7 | 442.6 | 436.4
2861.1 | 2722.1 | 525.5 | 486.1 | 509.3 | 483.6 | 490.7 | 490.8 | 492.1 | 589.6 | 442.9 | 436.4
2862.1 | 2723.1 | 525.5 | 486.1 | 509.4 | 483.6 | 490.7 | 490.8 | 492.1 | 613.4 | 442.5 | 436.4
2863.1 | 2724.1 | 525.5 | 486 | 509.4 | 483.6 | 490.6 | 490.8 | 492.2 | 599.7 | 443.2 | 436.4
2864.1 | 2725.1 | 525.5 | 486.1 | 509.4 | 483.6 | 490.7 | 490.9 | 492.2 | 592.4 | 442.7 | 436.5
2865.1 | 2726.1 | 525.4 | 486.1 | 509.4 | 483.6 | 490.8 | 491 | 492.2 | 617.1 | 442.8 | 436.4
2866.1 | 2727.1 | 525.4 | 486.1 | 509.4 | 483.6 | 490.8 | 491 | 492.3 | 599.4 | 443.3 | 436.5
2867.1 | 2728.1 | 525.4 | 486.1 | 509.5 | 483.6 | 490.8 | 491 | 492.3 | 601.5 | 442.5 | 436.5
2868.1 | 2729.1 | 525.4 | 486.1 | 509.4 | 483.6 | 490.9 | 491.1 | 492.3 | 619.1 | 443.3 | 436.5
2869.1 | 2730.1 | 525.4 | 486.1 | 509.4 | 483.6 | 491 | 491.1 | 492.4 | 599.3 | 443.3 | 436.5
2870.1 | 2731.1 | 525.4 | 486.1 | 509.5 | 483.6 | 490.9 | 491.1 | 492.4 | 612.2 | 442.5 | 436.6
2871.1 | 2732.1 | 525.3 | 486.1 | 509.4 | 483.6 | 491 | 491.2 | 492.4 | 618.5 | 443.3 | 436.5
2872.1 | 2733.1 | 525.3 | 486.1 | 509.4 | 483.6 | 491.1 | 491.2 | 492.4 | 599.8 | 443.3 | 436.6
2873.1 | 2734.1 | 525.3 | 486.1 | 509.5 | 483.6 | 491.1 | 491.3 | 492.5 | 622.1 | 442.7 | 436.6
2874.1 | 2735.1 | 525.3 | 486.1 | 509.5 | 483.6 | 491.1 | 491.3 | 492.5 | 617.2 | 443.4 | 436.6
2875.1 | 2736.1 | 525.3 | 486.2 | 509.5 | 483.6 | 491.2 | 491.4 | 492.5 | 602.7 | 443 | 436.6
2876.1 | 2737.1 | 525.4 | 486.2 | 509.5 | 483.6 | 491.2 | 491.4 | 492.5 | 627.7 | 443 | 436.7
2877.1 | 2738.1 | 525.4 | 486.2 | 509.5 | 483.6 | 491.2 | 491.4 | 492.5 | 640.9 | 442.5 | 436.7
2878.1 | 2739.1 | 525.4 | 486.2 | 509.5 | 483.7 | 491.3 | 491.5 | 492.6 | 650 | 442.7 | 436.7
2879.1 | 2740.1 | 525.4 | 486.2 | 509.5 | 483.6 | 491.4 | 491.5 | 492.6 | 661.3 | 443.2 | 436.7
2880.1 | 2741.1 | 525.4 | 486.2 | 509.5 | 483.6 | 491.3 | 491.5 | 492.6 | 636.5 | 443.5 | 436.7
2881.1 | 2742.1 | 525.4 | 486.2 | 509.5 | 483.6 | 491.3 | 491.6 | 492.6 | 633 | 442.8 | 436.8
2882.1 | 2743.1 | 525.4 | 486.2 | 509.5 | 483.7 | 491.5 | 491.6 | 492.7 | 646.1 | 443.3 | 436.7
2883.1 | 2744.1 | 525.4 | 486.2 | 509.5 | 483.7 | 491.5 | 491.7 | 492.7 | 623.2 | 443.6 | 436.8
2884.1 | 2745.1 | 525.4 | 486.2 | 509.6 | 483.6 | 491.4 | 491.7 | 492.7 | 605.7 | 443.7 | 436.8
2885.1 | 2746.1 | 525.3 | 486.2 | 509.5 | 483.7 | 491.5 | 491.7 | 492.7 | 592.2 | 443.8 | 436.8
2886.1 | 2747.1 | 525.3 | 486.3 | 509.5 | 483.7 | 491.6 | 491.8 | 492.8 | 581.4 | 443.8 | 436.8
2887.1 | 2748.1 | 525.3 | 486.3 | 509.5 | 483.6 | 491.6 | 491.8 | 492.8 | 572.5 | 443.9 | 436.9
2888.1 | 2749.1 | 525.3 | 486.2 | 509.6 | 483.6 | 491.5 | 491.8 | 492.8 | 565 | 443.9 | 436.9
2889.1 | 2750.1 | 525.3 | 486.3 | 509.5 | 483.7 | 491.7 | 491.9 | 492.8 | 558.6 | 444 | 436.9
2890.1 | 2751.1 | 525.3 | 486.3 | 509.6 | 483.7 | 491.7 | 491.9 | 492.9 | 553.1 | 444 | 436.9
2891.1 | 2752.1 | 525.3 | 486.3 | 509.7 | 483.6 | 491.6 | 492 | 492.9 | 548.2 | 444 | 436.9
2892.1 | 2753.1 | 525.3 | 486.3 | 509.7 | 483.6 | 491.7 | 492 | 492.9 | 543.9 | 444.1 | 437
2893.1 | 2754.1 | 525.3 | 486.3 | 509.6 | 483.7 | 491.8 | 492.1 | 493 | 540.1 | 444.1 | 437
2894.1 | 2755.1 | 525.3 | 486.3 | 509.7 | 483.6 | 491.8 | 492.1 | 493 | 536.7 | 444.1 | 437
2895.1 | 2756.1 | 525.3 | 486.3 | 509.7 | 483.6 | 491.8 | 492.1 | 493 | 533.7 | 444.2 | 437
2896.1 | 2757.1 | 525.3 | 486.3 | 509.6 | 483.7 | 491.9 | 492.2 | 493.1 | 530.9 | 444.2 | 437
2897.1 | 2758.1 | 525.3 | 486.3 | 509.6 | 483.7 | 491.9 | 492.2 | 493.1 | 528.4 | 444.2 | 437
2898.1 | 2759.1 | 525.3 | 486.3 | 509.7 | 483.7 | 491.9 | 492.2 | 493.1 | 526.1 | 444.2 | 437.1
2899.1 | 2760.1 | 525.3 | 486.3 | 509.6 | 483.7 | 492 | 492.3 | 493.2 | 524 | 444.2 | 437.1
2900.1 | 2761.1 | 525.3 | 486.3 | 509.6 | 483.7 | 492 | 492.3 | 493.2 | 522.8 | 444 | 437.1
2901.1 | 2762.1 | 525.3 | 486.3 | 509.7 | 483.7 | 492 | 492.3 | 493.2 | 551.6 | 443.6 | 437.2
2902.1 | 2763.1 | 525.3 | 486.3 | 509.7 | 483.7 | 492 | 492.4 | 493.2 | 570.1 | 443.4 | 437.2
2903.1 | 2764.1 | 525.3 | 486.4 | 509.6 | 483.7 | 492.2 | 492.4 | 493.3 | 589.7 | 443.3 | 437.2
2904.1 | 2765.1 | 525.3 | 486.4 | 509.6 | 483.7 | 492.2 | 492.5 | 493.3 | 612.9 | 443.5 | 437.2
2905.1 | 2766.1 | 525.3 | 486.4 | 509.7 | 483.7 | 492.1 | 492.5 | 493.3 | 598.9 | 444 | 437.2
2906.1 | 2767.1 | 525.2 | 486.4 | 509.7 | 483.7 | 492.2 | 492.6 | 493.4 | 592.1 | 443.3 | 437.2
2907.1 | 2768.1 | 525.2 | 486.4 | 509.7 | 483.7 | 492.3 | 492.6 | 493.4 | 616.3 | 443.7 | 437.2
2908.1 | 2769.1 | 525.2 | 486.4 | 509.7 | 483.7 | 492.3 | 492.6 | 493.4 | 598.6 | 444.1 | 437.3
2909.1 | 2770.1 | 525.3 | 486.4 | 509.7 | 483.7 | 492.3 | 492.7 | 493.5 | 600.9 | 443.1 | 437.3
2910.1 | 2771.1 | 525.3 | 486.4 | 509.8 | 483.7 | 492.3 | 492.7 | 493.5 | 618 | 444 | 437.3
2911.1 | 2772.1 | 525.3 | 486.2 | 510.2 | 483.5 | 491.8 | 492.6 | 493.6 | 598.5 | 444.2 | 437.4
2912.1 | 2773.1 | 525.3 | 486.1 | 510.5 | 483.4 | 491.6 | 492.5 | 493.6 | 611.3 | 443 | 437.5
2913.1 | 2774.1 | 525.2 | 486 | 510.6 | 483.4 | 491.6 | 492.5 | 493.7 | 617.7 | 444.2 | 437.5
2914.1 | 2775.1 | 525 | 486 | 510.5 | 483.4 | 491.7 | 492.6 | 493.7 | 599.3 | 444.1 | 437.5
2915.1 | 2776.1 | 524.7 | 486 | 510.5 | 483.4 | 491.7 | 492.6 | 493.7 | 621.5 | 443.6 | 437.5
2916.1 | 2777.1 | 524.3 | 486 | 510.5 | 483.4 | 491.7 | 492.6 | 493.8 | 616.3 | 444.3 | 437.5
2917.1 | 2778.1 | 523.9 | 486 | 510.4 | 483.4 | 491.8 | 492.7 | 493.8 | 602.3 | 444 | 437.6
2918.1 | 2779.1 | 523.4 | 486 | 510.4 | 483.4 | 491.8 | 492.7 | 493.8 | 626.9 | 443.9 | 437.6
2919.1 | 2780.1 | 522.9 | 485.9 | 510.4 | 483.3 | 491.8 | 492.8 | 493.9 | 640.3 | 443.4 | 437.6
2920.1 | 2781.1 | 522.3 | 486 | 510.3 | 483.3 | 491.9 | 492.8 | 493.9 | 648.9 | 443.5 | 437.6
2921.1 | 2782.1 | 521.7 | 485.9 | 510.3 | 483.3 | 492 | 492.9 | 493.9 | 660.2 | 443.8 | 437.6
2922.1 | 2783.1 | 521 | 485.9 | 510.2 | 483.3 | 491.9 | 492.9 | 494 | 635.7 | 444.4 | 437.6
2923.1 | 2784.1 | 520.4 | 485.9 | 510.2 | 483.3 | 491.9 | 492.9 | 494 | 632.6 | 443.6 | 437.7
2924.1 | 2785.1 | 519.7 | 485.9 | 510.1 | 483.3 | 492 | 493 | 494 | 645.3 | 444.2 | 437.6
2925.1 | 2786.1 | 519 | 485.9 | 510 | 483.2 | 492.1 | 493 | 494.1 | 622.6 | 444.5 | 437.7
2926.1 | 2787.1 | 518.3 | 485.8 | 510.1 | 483.2 | 492 | 493 | 494.1 | 605.4 | 444.6 | 437.7
2927.1 | 2788.1 | 517.6 | 485.8 | 509.9 | 483.2 | 492.1 | 493.1 | 494.1 | 592.1 | 444.7 | 437.7
2928.1 | 2789.1 | 517 | 485.7 | 509.8 | 483.1 | 492.2 | 493.1 | 494.2 | 581.5 | 444.7 | 437.7
2929.1 | 2790.1 | 516.2 | 485.7 | 509.8 | 483.1 | 492.2 | 493.2 | 494.2 | 572.7 | 444.8 | 437.7
2930.1 | 2791.1 | 515.4 | 485.6 | 509.7 | 483 | 492.2 | 493.2 | 494.2 | 565.3 | 444.8 | 437.8
2931.1 | 2792.1 | 514.7 | 485.6 | 509.6 | 483 | 492.3 | 493.3 | 494.3 | 559 | 444.8 | 437.7
2932.1 | 2793.1 | 513.9 | 485.6 | 509.5 | 483 | 492.3 | 493.3 | 494.3 | 553.6 | 444.9 | 437.8
2933.1 | 2794.1 | 513.2 | 485.5 | 509.5 | 482.9 | 492.3 | 493.3 | 494.3 | 548.8 | 444.9 | 437.8
2934.1 | 2795.1 | 512.4 | 485.5 | 509.3 | 482.9 | 492.4 | 493.3 | 494.3 | 544.6 | 444.9 | 437.8
2935.1 | 2796.1 | 511.6 | 485.4 | 509.2 | 482.8 | 492.4 | 493.4 | 494.3 | 540.8 | 444.9 | 437.8
2936.1 | 2797.1 | 510.8 | 485.4 | 509.2 | 482.8 | 492.4 | 493.4 | 494.4 | 537.4 | 445 | 437.8
2937.1 | 2798.1 | 510 | 485.3 | 509.1 | 482.7 | 492.4 | 493.4 | 494.4 | 534.4 | 445 | 437.9
2938.1 | 2799.1 | 509.1 | 485.3 | 509 | 482.7 | 492.5 | 493.5 | 494.4 | 531.6 | 445 | 437.9
2939.1 | 2800.1 | 508.3 | 485.2 | 508.8 | 482.6 | 492.5 | 493.5 | 494.4 | 529.1 | 445 | 437.9
2940.1 | 2801.1 | 507.5 | 485.1 | 508.8 | 482.5 | 492.5 | 493.5 | 494.4 | 526.9 | 445.1 | 437.9
2941.1 | 2802.1 | 506.8 | 485.1 | 508.6 | 482.5 | 492.6 | 493.6 | 494.4 | 524.8 | 445.1 | 437.9
2942.1 | 2803.1 | 506 | 485 | 508.5 | 482.4 | 492.6 | 493.6 | 494.4 | 523.9 | 445 | 438
2943.1 | 2804.1 | 505.2 | 484.9 | 508.4 | 482.3 | 492.6 | 493.6 | 494.5 | 552.6 | 444.1 | 438
2944.1 | 2805.1 | 504.4 | 484.9 | 508.3 | 482.3 | 492.6 | 493.6 | 494.5 | 570.8 | 444 | 438
2945.1 | 2806.1 | 503.6 | 484.8 | 508.1 | 482.2 | 492.7 | 493.7 | 494.5 | 590.1 | 444.2 | 438
2946.1 | 2807.1 | 502.8 | 484.7 | 508 | 482.1 | 492.7 | 493.7 | 494.5 | 613 | 444 | 438
2947.1 | 2808.1 | 502 | 484.6 | 507.9 | 482 | 492.7 | 493.7 | 494.5 | 599 | 444.8 | 438
2948.1 | 2809.1 | 501.2 | 484.6 | 507.8 | 482 | 492.7 | 493.8 | 494.5 | 592.4 | 444.3 | 438.1
2949.1 | 2810.1 | 500.4 | 484.5 | 507.6 | 481.9 | 492.8 | 493.8 | 494.5 | 616 | 444.3 | 438
2950.1 | 2811.1 | 499.7 | 484.4 | 507.6 | 481.8 | 492.8 | 493.8 | 494.6 | 598.5 | 444.9 | 438.1
2951.1 | 2812.1 | 499 | 484.3 | 507.4 | 481.7 | 492.8 | 493.8 | 494.6 | 600.9 | 443.8 | 438.1
2952.1 | 2813.1 | 498.2 | 484.3 | 507.3 | 481.6 | 492.9 | 493.9 | 494.6 | 617.5 | 444.6 | 438.1
2953.1 | 2814.1 | 497.4 | 484.2 | 507.1 | 481.6 | 492.9 | 493.9 | 494.6 | 598.3 | 444.8 | 438.1
2954.1 | 2815.1 | 496.6 | 484 | 507 | 481.4 | 492.8 | 493.9 | 494.6 | 610.9 | 443.8 | 438.1
2955.1 | 2816.1 | 495.8 | 484 | 506.8 | 481.4 | 492.9 | 493.9 | 494.6 | 616.4 | 444.9 | 438.1
2956.1 | 2817.1 | 495 | 483.9 | 506.6 | 481.3 | 492.9 | 494 | 494.6 | 598.5 | 444.9 | 438.1
2957.1 | 2818.1 | 494.2 | 483.8 | 506.6 | 481.2 | 492.9 | 494 | 494.6 | 620.9 | 444 | 438.1
2958.1 | 2819.1 | 493.4 | 483.7 | 506.4 | 481.1 | 492.9 | 494 | 494.6 | 615.6 | 445 | 438.2
2959.1 | 2820.1 | 492.7 | 483.6 | 506.2 | 481 | 493 | 494 | 494.6 | 601.7 | 444.3 | 438.1
2960.1 | 2821.1 | 491.9 | 483.5 | 506.1 | 480.9 | 493 | 494 | 494.6 | 625.9 | 444.2 | 438.1
2961.1 | 2822.1 | 491.2 | 483.3 | 506 | 480.7 | 492.9 | 494 | 494.6 | 639.4 | 444 | 438.2
2962.1 | 2823.1 | 490.4 | 483.3 | 505.8 | 480.7 | 493 | 494.1 | 494.6 | 647.6 | 444 | 438.2
2963.1 | 2824.1 | 489.7 | 483.2 | 505.6 | 480.6 | 493 | 494.1 | 494.6 | 658.6 | 444.4 | 438.2
2964.1 | 2825.1 | 489 | 483.1 | 505.5 | 480.4 | 493 | 494.1 | 494.6 | 634.2 | 445 | 438.2
2965.1 | 2826.1 | 488.2 | 482.9 | 505.3 | 480.3 | 492.9 | 494.1 | 494.5 | 631.3 | 443.8 | 438.2
2966.1 | 2827.1 | 487.4 | 482.8 | 505.1 | 480.2 | 493 | 494.1 | 494.5 | 643.4 | 444.7 | 438.2
2967.1 | 2828.1 | 486.6 | 482.7 | 505 | 480.1 | 493 | 494.1 | 494.5 | 621.2 | 445 | 438.2
2968.1 | 2829.1 | 485.9 | 482.6 | 504.9 | 480 | 492.9 | 494.1 | 494.5 | 604.3 | 445.1 | 438.2
2969.1 | 2830.1 | 485.1 | 482.5 | 504.6 | 479.9 | 493 | 494.1 | 494.5 | 591.2 | 445.1 | 438.2
2970.1 | 2831.1 | 484.4 | 482.4 | 504.5 | 479.8 | 493.1 | 494.1 | 494.5 | 580.7 | 445.1 | 438.2
2971.1 | 2832.1 | 483.6 | 482.2 | 504.3 | 479.6 | 493 | 494.1 | 494.5 | 572.1 | 445.2 | 438.3
2972.1 | 2833.1 | 482.9 | 482.1 | 504.1 | 479.5 | 493 | 494.1 | 494.5 | 564.8 | 445.2 | 438.3
2973.1 | 2834.1 | 482.1 | 482 | 503.9 | 479.4 | 493.1 | 494.2 | 494.5 | 558.6 | 445.2 | 438.3
2974.1 | 2835.1 | 481.4 | 481.9 | 503.7 | 479.3 | 493.1 | 494.2 | 494.5 | 553.2 | 445.2 | 438.3
2975.1 | 2836.1 | 480.6 | 481.7 | 503.6 | 479.1 | 493 | 494.1 | 494.5 | 548.5 | 445.2 | 438.3
2976.1 | 2837.1 | 479.9 | 481.6 | 503.4 | 479 | 493 | 494.2 | 494.4 | 544.3 | 445.2 | 438.3
2977.1 | 2838.1 | 479.1 | 481.5 | 503.1 | 478.9 | 493.1 | 494.2 | 494.4 | 540.6 | 445.2 | 438.3
2978.1 | 2839.1 | 478.4 | 481.3 | 503 | 478.8 | 493 | 494.1 | 494.4 | 537.3 | 445.2 | 438.3
2979.1 | 2840.1 | 477.7 | 481.2 | 502.8 | 478.6 | 493 | 494.1 | 494.4 | 534.3 | 445.2 | 438.3
2980.1 | 2841.1 | 476.9 | 481.1 | 502.6 | 478.5 | 493 | 494.2 | 494.4 | 531.6 | 445.2 | 438.3
2981.1 | 2842.1 | 476.2 | 480.9 | 502.4 | 478.4 | 493 | 494.1 | 494.3 | 529.2 | 445.2 | 438.3
2982.1 | 2843.1 | 475.5 | 480.8 | 502.3 | 478.2 | 493 | 494.1 | 494.3 | 526.9 | 445.2 | 438.3
2983.1 | 2844.1 | 474.7 | 480.6 | 502 | 478.1 | 493 | 494.1 | 494.3 | 525 | 445.2 | 438.3
2984.1 | 2845.1 | 474 | 480.5 | 501.8 | 478 | 493 | 494.1 | 494.2 | 524 | 444.7 | 438.3
2985.1 | 2846.1 | 473.2 | 480.4 | 501.6 | 477.8 | 493 | 494.1 | 494.2 | 552.4 | 444.1 | 438.3
2986.1 | 2847.1 | 472.5 | 480.2 | 501.4 | 477.7 | 492.9 | 494.1 | 494.2 | 570.4 | 444 | 438.3
2987.1 | 2848.1 | 471.8 | 480.1 | 501.2 | 477.6 | 493 | 494.1 | 494.1 | 589.7 | 444.4 | 438.3
2988.1 | 2849.1 | 471.1 | 479.9 | 501 | 477.4 | 492.9 | 494 | 494.1 | 612.2 | 443.9 | 438.3
2989.1 | 2850.1 | 470.4 | 479.7 | 500.8 | 477.3 | 492.8 | 494 | 494.1 | 597.9 | 444.8 | 438.3
2990.1 | 2851.1 | 469.6 | 479.6 | 500.6 | 477.1 | 492.9 | 494 | 494 | 591.6 | 444.2 | 438.3
2991.1 | 2852.1 | 468.9 | 479.5 | 500.3 | 477 | 492.9 | 494 | 494 | 614.9 | 444.1 | 438.3
2992.1 | 2853.1 | 468.2 | 479.3 | 500.2 | 476.8 | 492.8 | 494 | 493.9 | 597.3 | 444.7 | 438.3
2993.1 | 2854.1 | 467.5 | 479.1 | 500 | 476.6 | 492.8 | 493.9 | 493.9 | 600.3 | 443.8 | 438.3
2994.1 | 2855.1 | 466.8 | 479 | 499.9 | 476.5 | 492.8 | 493.9 | 493.9 | 616.6 | 444.4 | 438.3
2995.1 | 2856.1 | 466.1 | 478.9 | 499.6 | 476.4 | 492.8 | 493.9 | 493.8 | 597.2 | 444.8 | 438.3
2996.1 | 2857.1 | 465.4 | 478.7 | 499.5 | 476.2 | 492.7 | 493.9 | 493.8 | 610.5 | 443.4 | 438.3
2997.1 | 2858.1 | 464.7 | 478.5 | 499.2 | 476.1 | 492.7 | 493.9 | 493.8 | 615.6 | 444.5 | 438.3
2998.1 | 2859.1 | 464 | 478.4 | 499 | 475.9 | 492.7 | 493.9 | 493.7 | 597.7 | 444.5 | 438.3
2999.1 | 2860.1 | 463.3 | 478.2 | 498.8 | 475.8 | 492.7 | 493.8 | 493.7 | 620.1 | 443.6 | 438.2
3000.1 | 2861.1 | 462.7 | 478 | 498.6 | 475.6 | 492.6 | 493.8 | 493.6 | 614.5 | 444.5 | 438.3
3001.1 | 2862.1 | 462 | 477.9 | 498.3 | 475.4 | 492.6 | 493.8 | 493.6 | 600.9 | 444.1 | 438.2
3002.1 | 2863.1 | 461.3 | 477.7 | 498.1 | 475.3 | 492.6 | 493.7 | 493.5 | 625.1 | 443.5 | 438.2
3003.1 | 2864.1 | 460.6 | 477.5 | 497.9 | 475.1 | 492.5 | 493.7 | 493.5 | 638.1 | 443.5 | 438.2
3004.1 | 2865.1 | 459.9 | 477.3 | 497.7 | 474.9 | 492.4 | 493.6 | 493.4 | 646.2 | 443.6 | 438.2
3005.1 | 2866.1 | 459.2 | 477.1 | 497.7 | 474.7 | 492.1 | 493.5 | 493.4 | 656.9 | 443.9 | 438.2
3006.1 | 2867.1 | 458.6 | 476.9 | 497.5 | 474.5 | 492 | 493.5 | 493.3 | 632.5 | 444.6 | 438.2
3007.1 | 2868.1 | 457.9 | 476.7 | 497.3 | 474.4 | 492 | 493.4 | 493.3 | 630 | 443.5 | 438.2
3008.1 | 2869.1 | 457.2 | 476.6 | 497 | 474.2 | 492 | 493.4 | 493.2 | 641.9 | 444.2 | 438.2
3009.1 | 2870.1 | 456.6 | 476.4 | 496.8 | 474 | 491.9 | 493.4 | 493.1 | 619.6 | 444.5 | 438.2
3010.1 | 2871.1 | 455.9 | 476.2 | 496.7 | 473.8 | 491.8 | 493.3 | 493.1 | 602.8 | 444.6 | 438.2
3011.1 | 2872.1 | 455.2 | 476 | 496.3 | 473.7 | 491.8 | 493.3 | 493 | 589.8 | 444.6 | 438.2
3012.1 | 2873.1 | 454.6 | 475.9 | 496.1 | 473.5 | 491.8 | 493.2 | 492.9 | 579.3 | 444.6 | 438.1
3013.1 | 2874.1 | 453.9 | 475.7 | 495.8 | 473.3 | 491.7 | 493.2 | 492.9 | 570.7 | 444.6 | 438.1
3014.1 | 2875.1 | 453.3 | 475.5 | 495.7 | 473.1 | 491.6 | 493.1 | 492.8 | 563.5 | 444.6 | 438.1
3015.1 | 2876.1 | 452.6 | 475.3 | 495.4 | 473 | 491.7 | 493.1 | 492.7 | 557.3 | 444.5 | 438.1
3016.1 | 2877.1 | 452 | 475.2 | 495.1 | 472.8 | 491.6 | 493 | 492.6 | 552 | 444.5 | 438.1
3017.1 | 2878.1 | 451.4 | 474.9 | 495 | 472.6 | 491.4 | 492.9 | 492.6 | 547.2 | 444.5 | 438.1
3018.1 | 2879.1 | 450.7 | 474.7 | 494.8 | 472.4 | 491.2 | 492.8 | 492.5 | 543 | 444.5 | 438.1
3019.1 | 2880.1 | 450.1 | 474.6 | 494.5 | 472.3 | 491.4 | 492.8 | 492.4 | 539.2 | 444.4 | 438
3020.1 | 2881.1 | 449.5 | 474.4 | 494.3 | 472.1 | 491.3 | 492.8 | 492.3 | 535.9 | 444.4 | 438
3021.1 | 2882.1 | 448.8 | 474.2 | 494.1 | 471.9 | 491.2 | 492.7 | 492.3 | 533 | 444.4 | 438
3022.1 | 2883.1 | 448.2 | 474 | 493.8 | 471.7 | 491.2 | 492.7 | 492.2 | 530.2 | 444.3 | 438
3023.1 | 2884.1 | 447.5 | 473.8 | 493.5 | 471.5 | 491.1 | 492.6 | 492.1 | 527.8 | 444.3 | 438
3024.1 | 2885.1 | 446.9 | 473.6 | 493.3 | 471.3 | 491 | 492.5 | 492 | 525.6 | 444.3 | 438
3025.1 | 2886.1 | 446.2 | 473.5 | 493 | 471.1 | 491 | 492.5 | 491.9 | 523.6 | 444.2 | 437.9
3026.1 | 2887.1 | 445.6 | 473.3 | 492.8 | 470.9 | 491 | 492.4 | 491.9 | 522.7 | 444.1 | 437.9
3027.1 | 2888.1 | 445 | 473.1 | 492.6 | 470.7 | 490.9 | 492.3 | 491.8 | 551.1 | 443.4 | 437.9
3028.1 | 2889.1 | 444.4 | 472.9 | 492.4 | 470.5 | 490.8 | 492.2 | 491.7 | 569 | 442.9 | 437.9
3029.1 | 2890.1 | 443.8 | 472.7 | 492 | 470.4 | 490.8 | 492.2 | 491.6 | 587.6 | 443.4 | 437.9
3030.1 | 2891.1 | 443.2 | 472.6 | 491.7 | 470.2 | 490.8 | 492.2 | 491.5 | 610.9 | 442.9 | 437.8
3031.1 | 2892.1 | 442.5 | 472.3 | 491.5 | 470 | 490.7 | 492.1 | 491.4 | 596.6 | 443.7 | 437.8
3032.1 | 2893.1 | 441.9 | 472.2 | 491.2 | 469.8 | 490.6 | 492 | 491.3 | 590.4 | 443 | 437.8
3033.1 | 2894.1 | 441.2 | 472 | 491 | 469.6 | 490.6 | 492 | 491.2 | 614 | 443 | 437.7
3034.1 | 2895.1 | 440.6 | 471.8 | 490.7 | 469.4 | 490.5 | 491.9 | 491.1 | 596.3 | 443.6 | 437.7
3035.1 | 2896.1 | 440 | 471.6 | 490.5 | 469.2 | 490.3 | 491.8 | 491.1 | 599.5 | 442.5 | 437.7
3036.1 | 2897.1 | 439.4 | 471.4 | 490.2 | 469.1 | 490.4 | 491.7 | 491 | 615.9 | 443.2 | 437.6
3037.1 | 2898.1 | 438.8 | 471.2 | 489.9 | 468.9 | 490.3 | 491.7 | 490.9 | 596.3 | 443.5 | 437.6
3038.1 | 2899.1 | 438.2 | 471 | 489.7 | 468.6 | 490.1 | 491.6 | 490.8 | 609.9 | 442.1 | 437.6
3039.1 | 2900.1 | 437.6 | 470.8 | 489.5 | 468.4 | 490.1 | 491.5 | 490.7 | 614.8 | 443.2 | 437.6
3040.1 | 2901.1 | 437 | 470.6 | 489.2 | 468.2 | 490 | 491.4 | 490.6 | 596.7 | 443.1 | 437.5
3041.1 | 2902.1 | 436.4 | 470.4 | 489 | 468 | 489.9 | 491.3 | 490.5 | 619.5 | 442.1 | 437.5
3042.1 | 2903.1 | 435.8 | 470.2 | 488.7 | 467.9 | 489.8 | 491.2 | 490.4 | 613.5 | 443.1 | 437.5
3043.1 | 2904.1 | 435.1 | 470 | 488.4 | 467.7 | 489.8 | 491.2 | 490.3 | 599.8 | 442.7 | 437.5
3044.1 | 2905.1 | 434.5 | 469.8 | 488.1 | 467.5 | 489.7 | 491.1 | 490.2 | 624.3 | 442.2 | 437.4
3045.1 | 2906.1 | 433.9 | 469.6 | 487.9 | 467.2 | 489.6 | 491 | 490.1 | 637.6 | 441.9 | 437.4
3046.1 | 2907.1 | 433.3 | 469.4 | 487.6 | 467 | 489.5 | 490.9 | 490 | 645.9 | 442 | 437.3
3047.1 | 2908.1 | 432.7 | 469.2 | 487.3 | 466.9 | 489.5 | 490.8 | 489.9 | 656.7 | 442.2 | 437.3
3048.1 | 2909.1 | 432.1 | 469 | 487.1 | 466.6 | 489.3 | 490.7 | 489.8 | 631.9 | 442.7 | 437.3
3049.1 | 2910.1 | 431.5 | 468.7 | 487 | 466.4 | 489.1 | 490.6 | 489.7 | 629.6 | 441.8 | 437.3
3050.1 | 2911.1 | 430.9 | 468.4 | 486.8 | 466.2 | 488.9 | 490.5 | 489.6 | 641.4 | 442.4 | 437.2
3051.1 | 2912.1 | 430.3 | 468.2 | 486.5 | 465.9 | 488.8 | 490.4 | 489.5 | 618.7 | 442.6 | 437.2
3052.1 | 2913.1 | 429.8 | 468 | 486.3 | 465.7 | 488.6 | 490.3 | 489.4 | 601.6 | 442.6 | 437.2
3053.1 | 2914.1 | 429.2 | 467.8 | 486.1 | 465.5 | 488.6 | 490.2 | 489.2 | 588.4 | 442.6 | 437.1
3054.1 | 2915.1 | 428.6 | 467.6 | 485.8 | 465.3 | 488.5 | 490.1 | 489.1 | 577.9 | 442.6 | 437.1
3055.1 | 2916.1 | 428.1 | 467.4 | 485.6 | 465.1 | 488.4 | 490 | 489 | 569.1 | 442.5 | 437
3056.1 | 2917.1 | 427.5 | 467.2 | 485.3 | 464.9 | 488.3 | 489.9 | 488.9 | 561.8 | 442.5 | 437
3057.1 | 2918.1 | 427 | 467 | 485 | 464.7 | 488.2 | 489.8 | 488.8 | 555.5 | 442.5 | 437
3058.1 | 2919.1 | 426.5 | 466.8 | 484.7 | 464.5 | 488.1 | 489.7 | 488.7 | 550 | 442.4 | 436.9
3059.1 | 2920.1 | 425.9 | 466.5 | 484.5 | 464.2 | 487.9 | 489.6 | 488.6 | 545.3 | 442.3 | 436.9
3060.1 | 2921.1 | 425.4 | 466.4 | 484.2 | 464 | 487.9 | 489.5 | 488.4 | 541 | 442.3 | 436.8
3061.1 | 2922.1 | 424.8 | 466.1 | 483.9 | 463.8 | 487.8 | 489.4 | 488.3 | 537.2 | 442.2 | 436.8
3062.1 | 2923.1 | 424.3 | 465.9 | 483.7 | 463.6 | 487.7 | 489.3 | 488.2 | 533.8 | 442.1 | 436.7
3063.1 | 2924.1 | 423.7 | 465.7 | 483.4 | 463.4 | 487.6 | 489.1 | 488.1 | 530.8 | 442.1 | 436.7
3064.1 | 2925.1 | 423.2 | 465.5 | 483.1 | 463.2 | 487.5 | 489.1 | 488 | 528 | 442 | 436.6
3065.1 | 2926.1 | 422.6 | 465.3 | 482.9 | 463 | 487.4 | 489 | 487.8 | 525.5 | 441.9 | 436.6
3066.1 | 2927.1 | 422.1 | 465.1 | 482.6 | 462.8 | 487.2 | 488.8 | 487.7 | 523.2 | 441.9 | 436.6
3067.1 | 2928.1 | 421.5 | 464.9 | 482.3 | 462.5 | 487.2 | 488.7 | 487.6 | 521 | 441.8 | 436.5
3068.1 | 2929.1 | 421 | 464.7 | 482.1 | 462.4 | 487.1 | 488.6 | 487.5 | 520.2 | 441.5 | 436.5
3069.1 | 2930.1 | 420.5 | 464.4 | 481.8 | 462.2 | 486.9 | 488.5 | 487.3 | 549.7 | 440.6 | 436.4
3070.1 | 2931.1 | 419.9 | 464.2 | 481.6 | 461.9 | 486.8 | 488.4 | 487.2 | 567.8 | 440.3 | 436.4
3071.1 | 2932.1 | 419.4 | 464 | 481.2 | 461.7 | 486.8 | 488.3 | 487.1 | 586.8 | 440.4 | 436.3
3072.1 | 2933.1 | 418.8 | 463.8 | 481 | 461.5 | 486.6 | 488.2 | 487 | 609.3 | 440.3 | 436.2
3073.1 | 2934.1 | 418.3 | 463.5 | 480.7 | 461.3 | 486.5 | 488.1 | 486.9 | 594.4 | 441 | 436.2
3074.1 | 2935.1 | 417.8 | 463.3 | 480.4 | 461.1 | 486.4 | 487.9 | 486.7 | 588.4 | 440.3 | 436.2
3075.1 | 2936.1 | 417.2 | 463.1 | 480.2 | 460.8 | 486.3 | 487.8 | 486.6 | 611.8 | 440.3 | 436.1
3076.1 | 2937.1 | 416.7 | 462.9 | 479.9 | 460.6 | 486.2 | 487.7 | 486.5 | 593.7 | 440.8 | 436
3077.1 | 2938.1 | 416.2 | 462.7 | 479.7 | 460.4 | 486 | 487.6 | 486.4 | 597.3 | 439.7 | 436
3078.1 | 2939.1 | 415.7 | 462.5 | 479.3 | 460.2 | 486 | 487.5 | 486.2 | 613.1 | 440.4 | 435.9
3079.1 | 2940.1 | 415.1 | 462.2 | 479.1 | 460 | 485.8 | 487.4 | 486.1 | 593.4 | 440.6 | 435.9
3080.1 | 2941.1 | 414.6 | 462 | 478.8 | 459.7 | 485.6 | 487.2 | 485.9 | 607.6 | 439.2 | 435.8
3081.1 | 2942.1 | 414.1 | 461.8 | 478.5 | 459.5 | 485.6 | 487.1 | 485.8 | 611.9 | 440.3 | 435.7
3082.1 | 2943.1 | 413.5 | 461.6 | 478.2 | 459.3 | 485.5 | 487 | 485.6 | 593.8 | 439.9 | 435.7
3083.1 | 2944.1 | 413 | 461.4 | 477.9 | 459.1 | 485.3 | 486.9 | 485.5 | 616.5 | 439.2 | 435.6
3084.1 | 2945.1 | 412.4 | 461.1 | 477.7 | 458.9 | 485.2 | 486.7 | 485.4 | 610.1 | 440.1 | 435.6
3085.1 | 2946.1 | 411.9 | 460.9 | 477.4 | 458.6 | 485.1 | 486.6 | 485.2 | 596.6 | 439.4 | 435.5
3086.1 | 2947.1 | 411.3 | 460.7 | 477.1 | 458.4 | 485 | 486.5 | 485.1 | 621.1 | 438.9 | 435.4
3087.1 | 2948.1 | 410.8 | 460.4 | 476.9 | 458.2 | 484.8 | 486.4 | 484.9 | 634.6 | 438.7 | 435.3
3088.1 | 2949.1 | 410.2 | 460.2 | 476.6 | 458 | 484.7 | 486.2 | 484.8 | 642.9 | 438.9 | 435.3
3089.1 | 2950.1 | 409.7 | 460 | 476.3 | 457.7 | 484.6 | 486.1 | 484.6 | 653.7 | 439.3 | 435.2
3090.1 | 2951.1 | 409.2 | 459.8 | 476.1 | 457.5 | 484.4 | 486 | 484.5 | 628.6 | 439.6 | 435.2
3091.1 | 2952.1 | 408.7 | 459.5 | 475.8 | 457.3 | 484.3 | 485.8 | 484.4 | 626.6 | 438.4 | 435.1
3092.1 | 2953.1 | 408.1 | 459.3 | 475.5 | 457 | 484.2 | 485.7 | 484.2 | 638.2 | 439.3 | 435.1
3093.1 | 2954.1 | 407.6 | 459.1 | 475.2 | 456.8 | 484.1 | 485.6 | 484.1 | 615.4 | 439.3 | 435
3094.1 | 2955.1 | 407 | 458.8 | 475 | 456.6 | 483.9 | 485.4 | 483.9 | 598.2 | 439.3 | 434.9
3095.1 | 2956.1 | 406.5 | 458.6 | 474.7 | 456.4 | 483.8 | 485.3 | 483.8 | 584.9 | 439.3 | 434.9
3096.1 | 2957.1 | 406 | 458.4 | 474.4 | 456.1 | 483.7 | 485.2 | 483.6 | 574.2 | 439.2 | 434.8
3097.1 | 2958.1 | 405.4 | 458.2 | 474.1 | 455.9 | 483.5 | 485 | 483.5 | 565.4 | 439.1 | 434.7
3098.1 | 2959.1 | 404.9 | 458 | 473.9 | 455.7 | 483.3 | 484.9 | 483.3 | 558 | 439.1 | 434.7
3099.1 | 2960.1 | 404.4 | 457.8 | 473.6 | 455.5 | 483.3 | 484.8 | 483.2 | 551.6 | 439 | 434.6
3100.1 | 2961.1 | 403.9 | 457.5 | 473.3 | 455.3 | 483.1 | 484.6 | 483 | 546 | 438.9 | 434.5
3101.1 | 2962.1 | 403.4 | 457.3 | 473 | 455 | 482.9 | 484.5 | 482.9 | 541.2 | 438.9 | 434.5
3102.1 | 2963.1 | 402.8 | 457.1 | 472.7 | 454.8 | 482.8 | 484.3 | 482.7 | 536.8 | 438.8 | 434.4
3103.1 | 2964.1 | 402.3 | 456.9 | 472.4 | 454.6 | 482.7 | 484.2 | 482.6 | 533 | 438.7 | 434.3
3104.1 | 2965.1 | 401.8 | 456.6 | 472.2 | 454.4 | 482.6 | 484.1 | 482.4 | 529.5 | 438.6 | 434.3
3105.1 | 2966.1 | 401.3 | 456.4 | 471.9 | 454.1 | 482.4 | 483.9 | 482.3 | 526.5 | 438.6 | 434.2
3106.1 | 2967.1 | 400.8 | 456.2 | 471.6 | 453.9 | 482.3 | 483.8 | 482.1 | 523.7 | 438.5 | 434.1
3107.1 | 2968.1 | 400.3 | 455.9 | 471.3 | 453.7 | 482.2 | 483.6 | 482 | 521.2 | 438.4 | 434.1
3108.1 | 2969.1 | 399.8 | 455.7 | 471.1 | 453.4 | 482 | 483.5 | 481.8 | 518.8 | 438.4 | 434
3109.1 | 2970.1 | 399.3 | 455.5 | 470.8 | 453.2 | 481.9 | 483.3 | 481.7 | 516.7 | 438.3 | 433.9
3110.1 | 2971.1 | 398.8 | 455.2 | 470.5 | 453 | 481.8 | 483.2 | 481.5 | 515.8 | 437.8 | 433.9
3111.1 | 2972.1 | 398.3 | 455 | 470.2 | 452.7 | 481.6 | 483.1 | 481.4 | 545.6 | 437.1 | 433.8
3112.1 | 2973.1 | 397.8 | 454.7 | 470 | 452.5 | 481.4 | 482.9 | 481.2 | 563.6 | 436.8 | 433.7
3113.1 | 2974.1 | 397.3 | 454.5 | 469.6 | 452.3 | 481.4 | 482.8 | 481.1 | 582.4 | 436.7 | 433.6
3114.1 | 2975.1 | 396.8 | 454.3 | 469.3 | 452.1 | 481.2 | 482.6 | 480.9 | 605.3 | 437 | 433.6
3115.1 | 2976.1 | 396.4 | 454 | 469.1 | 451.8 | 481 | 482.5 | 480.8 | 590.2 | 437.5 | 433.5
3116.1 | 2977.1 | 395.9 | 453.8 | 468.8 | 451.6 | 480.9 | 482.3 | 480.6 | 584.2 | 436.4 | 433.4
3117.1 | 2978.1 | 395.4 | 453.6 | 468.5 | 451.4 | 480.8 | 482.2 | 480.4 | 607.4 | 437 | 433.3
3118.1 | 2979.1 | 394.9 | 453.4 | 468.3 | 451.2 | 480.6 | 482.1 | 480.3 | 589.2 | 437.3 | 433.3
3119.1 | 2980.1 | 394.4 | 453.1 | 468 | 450.9 | 480.5 | 481.9 | 480.1 | 593 | 436 | 433.2
3120.1 | 2981.1 | 393.9 | 452.9 | 467.7 | 450.7 | 480.4 | 481.8 | 480 | 608.8 | 437 | 433.1
3121.1 | 2982.1 | 393.5 | 452.7 | 467.4 | 450.5 | 480.2 | 481.6 | 479.8 | 589 | 436.7 | 433
3122.1 | 2983.1 | 393 | 452.4 | 467.2 | 450.2 | 480 | 481.5 | 479.6 | 603.3 | 435.8 | 432.9
3123.1 | 2984.1 | 392.5 | 452.2 | 466.8 | 450 | 479.9 | 481.3 | 479.5 | 607.5 | 436.7 | 432.9
3124.1 | 2985.1 | 392.1 | 452 | 466.5 | 449.8 | 479.8 | 481.2 | 479.3 | 589.5 | 436.2 | 432.8
3125.1 | 2986.1 | 391.6 | 451.7 | 466.3 | 449.6 | 479.6 | 481 | 479.2 | 612.7 | 435.8 | 432.7
3126.1 | 2987.1 | 391.2 | 451.5 | 466 | 449.3 | 479.4 | 480.9 | 479 | 606.1 | 436.4 | 432.6
3127.1 | 2988.1 | 390.7 | 451.3 | 465.7 | 449.1 | 479.4 | 480.7 | 478.8 | 592.6 | 435.6 | 432.5
3128.1 | 2989.1 | 390.3 | 451 | 465.4 | 448.9 | 479.2 | 480.6 | 478.7 | 617.3 | 435.6 | 432.5
3129.1 | 2990.1 | 389.8 | 450.8 | 465.2 | 448.7 | 479 | 480.4 | 478.5 | 630.8 | 434.8 | 432.4
3130.1 | 2991.1 | 389.3 | 450.6 | 464.8 | 448.4 | 478.9 | 480.3 | 478.3 | 639 | 434.9 | 432.3
3131.1 | 2992.1 | 388.9 | 450.3 | 464.6 | 448.2 | 478.8 | 480.1 | 478.1 | 649.5 | 435.2 | 432.2
3132.1 | 2993.1 | 388.4 | 450.1 | 464.3 | 448 | 478.6 | 480 | 478 | 624.2 | 435.7 | 432.1
3133.1 | 2994.1 | 388 | 449.8 | 464.1 | 447.7 | 478.4 | 479.8 | 477.8 | 622.7 | 434.4 | 432
3134.1 | 2995.1 | 387.5 | 449.6 | 463.7 | 447.5 | 478.3 | 479.7 | 477.6 | 634.1 | 435.4 | 432
3135.1 | 2996.1 | 387 | 449.4 | 463.4 | 447.3 | 478.2 | 479.5 | 477.5 | 611.3 | 435.4 | 431.9
3136.1 | 2997.1 | 386.6 | 449.1 | 463.2 | 447.1 | 477.9 | 479.3 | 477.3 | 594.1 | 435.4 | 431.8
3137.1 | 2998.1 | 386.2 | 448.9 | 462.9 | 446.8 | 477.8 | 479.2 | 477.1 | 580.9 | 435.3 | 431.7
3138.1 | 2999.1 | 385.7 | 448.7 | 462.6 | 446.6 | 477.7 | 479 | 476.9 | 570.2 | 435.1 | 431.6
3139.1 | 3000.1 | 385.3 | 448.5 | 462.4 | 446.4 | 477.5 | 478.9 | 476.8 | 561.4 | 435.1 | 431.6
3140.1 | 3001.1 | 384.8 | 448.2 | 462.1 | 446.1 | 477.3 | 478.7 | 476.6 | 553.9 | 435 | 431.5
3141.1 | 3002.1 | 384.4 | 448 | 461.8 | 445.9 | 477.2 | 478.6 | 476.4 | 547.6 | 434.9 | 431.4
3142.1 | 3003.1 | 383.9 | 447.8 | 461.5 | 445.7 | 477 | 478.4 | 476.2 | 542 | 434.7 | 431.3
3143.1 | 3004.1 | 383.5 | 447.5 | 461.2 | 445.4 | 476.8 | 478.2 | 476.1 | 537.1 | 434.6 | 431.2
3144.1 | 3005.1 | 383 | 447.3 | 460.9 | 445.2 | 476.7 | 478.1 | 475.9 | 532.8 | 434.5 | 431.1
3145.1 | 3006.1 | 382.6 | 447 | 460.6 | 445 | 476.6 | 477.9 | 475.7 | 528.8 | 434.4 | 431
3146.1 | 3007.1 | 382.1 | 446.8 | 460.4 | 444.7 | 476.4 | 477.8 | 475.5 | 525.3 | 434.3 | 431
3147.1 | 3008.1 | 381.7 | 446.5 | 460.1 | 444.5 | 476.2 | 477.6 | 475.4 | 522.2 | 434.1 | 430.9
3148.1 | 3009.1 | 381.2 | 446.3 | 459.8 | 444.3 | 476.1 | 477.4 | 475.2 | 519.3 | 434 | 430.8
3149.1 | 3010.1 | 380.8 | 446.1 | 459.5 | 444 | 475.9 | 477.3 | 475 | 516.7 | 433.9 | 430.7
3150.1 | 3011.1 | 380.3 | 445.8 | 459.2 | 443.8 | 475.7 | 477.1 | 474.8 | 514.3 | 433.8 | 430.6
3151.1 | 3012.1 | 379.8 | 445.6 | 458.9 | 443.6 | 475.5 | 476.9 | 474.6 | 512.1 | 433.7 | 430.5
3152.1 | 3013.1 | 379.4 | 445.3 | 458.8 | 443.3 | 475.2 | 476.7 | 474.5 | 511.3 | 433.2 | 430.4
3153.1 | 3014.1 | 378.9 | 445 | 458.6 | 443 | 474.9 | 476.5 | 474.3 | 541.6 | 432.7 | 430.4
3154.1 | 3015.1 | 378.5 | 444.8 | 458.4 | 442.8 | 474.7 | 476.3 | 474.1 | 560.1 | 432.1 | 430.2
3155.1 | 3016.1 | 378.1 | 444.5 | 458 | 442.6 | 474.6 | 476.2 | 473.9 | 579.1 | 432.2 | 430.1
3156.1 | 3017.1 | 377.7 | 444.3 | 457.7 | 442.3 | 474.4 | 476 | 473.7 | 602.1 | 432.2 | 430.1
3157.1 | 3018.1 | 377.2 | 444 | 457.5 | 442.1 | 474.2 | 475.8 | 473.6 | 586.7 | 432.6 | 430
3158.1 | 3019.1 | 376.8 | 443.8 | 457.2 | 441.8 | 474.1 | 475.6 | 473.4 | 581 | 431.6 | 429.8
3159.1 | 3020.1 | 376.4 | 443.6 | 456.9 | 441.6 | 473.9 | 475.5 | 473.2 | 604.4 | 432.1 | 429.8
3160.1 | 3021.1 | 375.9 | 443.4 | 456.6 | 441.4 | 473.7 | 475.3 | 473 | 585.9 | 432.3 | 429.6
3161.1 | 3022.1 | 375.5 | 443.1 | 456.4 | 441.1 | 473.5 | 475.1 | 472.8 | 589.8 | 431.1 | 429.5
3162.1 | 3023.1 | 375.1 | 442.9 | 456 | 440.9 | 473.4 | 474.9 | 472.6 | 605.5 | 432 | 429.5
3163.1 | 3024.1 | 374.7 | 442.7 | 455.8 | 440.7 | 473.2 | 474.8 | 472.4 | 585.5 | 431.8 | 429.3
3164.1 | 3025.1 | 374.3 | 442.4 | 455.5 | 440.4 | 473 | 474.6 | 472.3 | 600 | 430.9 | 429.2
3165.1 | 3026.1 | 373.9 | 442.2 | 455.2 | 440.2 | 472.9 | 474.4 | 472.1 | 604 | 431.6 | 429.1
3166.1 | 3027.1 | 373.5 | 441.9 | 454.9 | 440 | 472.7 | 474.3 | 471.9 | 586 | 431.2 | 429
3167.1 | 3028.1 | 373 | 441.7 | 454.7 | 439.7 | 472.5 | 474.1 | 471.7 | 609.3 | 430.8 | 428.9
3168.1 | 3029.1 | 372.6 | 441.4 | 454.4 | 439.5 | 472.3 | 473.9 | 471.5 | 602.5 | 431.3 | 428.8
3169.1 | 3030.1 | 372.2 | 441.2 | 454.1 | 439.3 | 472.2 | 473.7 | 471.3 | 589.2 | 430.5 | 428.7
3170.1 | 3031.1 | 371.8 | 441 | 453.8 | 439 | 472.1 | 473.6 | 471.2 | 614.1 | 430.6 | 428.6
3171.1 | 3032.1 | 371.4 | 440.7 | 453.6 | 438.8 | 471.8 | 473.4 | 471 | 627.8 | 429.8 | 428.5
3172.1 | 3033.1 | 371 | 440.5 | 453.3 | 438.6 | 471.7 | 473.2 | 470.8 | 636.1 | 429.9 | 428.4
3173.1 | 3034.1 | 370.6 | 440.3 | 453 | 438.3 | 471.6 | 473.1 | 470.6 | 646.9 | 430.5 | 428.3
3174.1 | 3035.1 | 370.2 | 440 | 452.7 | 438.1 | 471.4 | 472.9 | 470.5 | 621.8 | 430.7 | 428.2
3175.1 | 3036.1 | 369.8 | 439.8 | 452.5 | 437.8 | 471.2 | 472.7 | 470.3 | 620.4 | 429.5 | 428.1
3176.1 | 3037.1 | 369.4 | 439.6 | 452.1 | 437.7 | 471.1 | 472.5 | 470.1 | 631.7 | 430.4 | 428
3177.1 | 3038.1 | 369 | 439.3 | 451.9 | 437.4 | 470.9 | 472.4 | 470 | 609 | 430.4 | 427.9
3178.1 | 3039.1 | 368.6 | 439.1 | 451.6 | 437.2 | 470.7 | 472.2 | 469.8 | 591.9 | 430.4 | 427.8
3179.1 | 3040.1 | 368.2 | 438.8 | 451.3 | 437 | 470.5 | 472 | 469.6 | 578.5 | 430.3 | 427.7
3180.1 | 3041.1 | 367.8 | 438.6 | 451 | 436.7 | 470.4 | 471.8 | 469.4 | 567.7 | 430.2 | 427.6
3181.1 | 3042.1 | 367.4 | 438.4 | 450.8 | 436.5 | 470.2 | 471.7 | 469.3 | 558.8 | 430.1 | 427.5
3182.1 | 3043.1 | 367 | 438.1 | 450.5 | 436.3 | 470 | 471.5 | 469.1 | 551.3 | 430 | 427.3
3183.1 | 3044.1 | 366.6 | 437.9 | 450.2 | 436.1 | 469.9 | 471.3 | 468.9 | 544.8 | 429.9 | 427.2
3184.1 | 3045.1 | 366.2 | 437.7 | 449.9 | 435.8 | 469.7 | 471.1 | 468.7 | 539.2 | 429.8 | 427.1
3185.1 | 3046.1 | 365.8 | 437.4 | 449.7 | 435.6 | 469.5 | 470.9 | 468.5 | 534.1 | 429.6 | 427
3186.1 | 3047.1 | 365.4 | 437.2 | 449.4 | 435.4 | 469.3 | 470.8 | 468.4 | 529.7 | 429.5 | 426.9
3187.1 | 3048.1 | 365 | 436.9 | 449.1 | 435.2 | 469.2 | 470.6 | 468.2 | 525.6 | 429.4 | 426.8
3188.1 | 3049.1 | 364.6 | 436.7 | 448.8 | 434.9 | 469 | 470.4 | 468 | 522 | 429.3 | 426.7
3189.1 | 3050.1 | 364.2 | 436.4 | 448.6 | 434.7 | 468.8 | 470.2 | 467.8 | 518.7 | 429.1 | 426.6
3190.1 | 3051.1 | 363.8 | 436.2 | 448.2 | 434.5 | 468.7 | 470.1 | 467.6 | 515.7 | 429 | 426.5
3191.1 | 3052.1 | 363.4 | 436 | 447.9 | 434.2 | 468.5 | 469.9 | 467.4 | 513 | 428.9 | 426.3
3192.1 | 3053.1 | 363 | 435.7 | 447.7 | 434 | 468.2 | 469.7 | 467.2 | 510.5 | 428.7 | 426.2
3193.1 | 3054.1 | 362.6 | 435.5 | 447.4 | 433.7 | 468.1 | 469.5 | 467 | 508.2 | 428.6 | 426.1
3194.1 | 3055.1 | 362.2 | 435.3 | 447.1 | 433.5 | 467.9 | 469.4 | 466.8 | 507.4 | 428.1 | 426
3195.1 | 3056.1 | 361.8 | 435 | 446.9 | 433.3 | 467.7 | 469.2 | 466.7 | 537.5 | 427.6 | 425.9
3196.1 | 3057.1 | 361.5 | 434.8 | 446.6 | 433 | 467.5 | 469 | 466.5 | 556 | 427.2 | 425.8
3197.1 | 3058.1 | 361.1 | 434.5 | 446.3 | 432.8 | 467.4 | 468.8 | 466.3 | 575.3 | 427 | 425.6
3198.1 | 3059.1 | 360.7 | 434.3 | 446 | 432.6 | 467.2 | 468.6 | 466.1 | 598.7 | 427.1 | 425.5
3199.1 | 3060.1 | 360.3 | 434 | 445.8 | 432.3 | 467 | 468.4 | 465.9 | 583.7 | 427.4 | 425.4
3200.1 | 3061.1 | 359.9 | 433.8 | 445.5 | 432.1 | 466.8 | 468.3 | 465.7 | 578.4 | 426.4 | 425.3
3201.1 | 3062.1 | 359.5 | 433.6 | 445.2 | 431.9 | 466.7 | 468.1 | 465.5 | 601.7 | 426.9 | 425.2
3202.1 | 3063.1 | 359.1 | 433.3 | 444.9 | 431.6 | 466.5 | 467.9 | 465.3 | 583.6 | 427 | 425.1
3203.1 | 3064.1 | 358.7 | 433.1 | 444.7 | 431.4 | 466.3 | 467.7 | 465.1 | 588 | 425.8 | 424.9
3204.1 | 3065.1 | 358.3 | 432.9 | 444.3 | 431.2 | 466.2 | 467.5 | 464.9 | 603.7 | 426.7 | 424.9
3205.1 | 3066.1 | 357.9 | 432.6 | 444 | 431 | 466 | 467.4 | 464.7 | 583.9 | 426.4 | 424.7
3206.1 | 3067.1 | 357.6 | 432.4 | 443.8 | 430.7 | 465.7 | 467.2 | 464.5 | 598.8 | 425.6 | 424.6
3207.1 | 3068.1 | 357.2 | 432.1 | 443.5 | 430.5 | 465.6 | 467 | 464.3 | 602.6 | 426.3 | 424.5
3208.1 | 3069.1 | 356.8 | 431.9 | 443.2 | 430.3 | 465.4 | 466.8 | 464.1 | 585 | 425.8 | 424.4
3209.1 | 3070.1 | 356.4 | 431.6 | 443 | 430 | 465.2 | 466.6 | 463.9 | 608.4 | 425.3 | 424.3
3210.1 | 3071.1 | 356.1 | 431.4 | 442.7 | 429.8 | 465 | 466.4 | 463.7 | 601.5 | 425.8 | 424.2
3211.1 | 3072.1 | 355.7 | 431.2 | 442.4 | 429.6 | 464.9 | 466.3 | 463.5 | 588.4 | 425.2 | 424
3212.1 | 3073.1 | 355.3 | 431 | 442.1 | 429.4 | 464.7 | 466.1 | 463.3 | 613.2 | 424.8 | 423.9
3213.1 | 3074.1 | 354.9 | 430.7 | 441.9 | 429.1 | 464.5 | 465.9 | 463.1 | 627.4 | 424.2 | 423.7
3214.1 | 3075.1 | 354.6 | 430.4 | 441.6 | 428.9 | 464.3 | 465.7 | 462.9 | 635.2 | 424.4 | 423.6
3215.1 | 3076.1 | 354.2 | 430.2 | 441.3 | 428.7 | 464.1 | 465.5 | 462.7 | 646 | 424.8 | 423.5
3216.1 | 3077.1 | 353.8 | 430 | 441 | 428.4 | 463.9 | 465.3 | 462.5 | 621.1 | 424.9 | 423.4
3217.1 | 3078.1 | 353.4 | 429.7 | 440.8 | 428.2 | 463.7 | 465.1 | 462.3 | 619.9 | 423.6 | 423.2
3218.1 | 3079.1 | 353 | 429.5 | 440.5 | 427.9 | 463.6 | 465 | 462.1 | 631.1 | 424.4 | 423.1
3219.1 | 3080.1 | 352.6 | 429.3 | 440.2 | 427.7 | 463.4 | 464.8 | 461.9 | 608.3 | 424.5 | 423
3220.1 | 3081.1 | 352.2 | 429 | 440 | 427.4 | 463.1 | 464.6 | 461.7 | 591 | 424.4 | 422.9
3221.1 | 3082.1 | 351.8 | 428.8 | 439.6 | 427.2 | 462.9 | 464.4 | 461.5 | 577.3 | 424.3 | 422.8
3222.1 | 3083.1 | 351.4 | 428.6 | 439.3 | 427 | 462.8 | 464.2 | 461.3 | 566.2 | 424.1 | 422.6
3223.1 | 3084.1 | 351 | 428.3 | 439.1 | 426.8 | 462.6 | 464 | 461.1 | 557 | 424 | 422.5
3224.1 | 3085.1 | 350.7 | 428 | 438.9 | 426.5 | 462.3 | 463.8 | 460.9 | 549.1 | 423.9 | 422.4
3225.1 | 3086.1 | 350.3 | 427.8 | 438.5 | 426.3 | 462.2 | 463.6 | 460.7 | 542.3 | 423.8 | 422.3
3226.1 | 3087.1 | 349.9 | 427.6 | 438.3 | 426.1 | 462 | 463.4 | 460.5 | 536.3 | 423.6 | 422.1
3227.1 | 3088.1 | 349.6 | 427.3 | 438 | 425.8 | 461.8 | 463.2 | 460.3 | 531.1 | 423.5 | 422
3228.1 | 3089.1 | 349.2 | 427.1 | 437.7 | 425.6 | 461.6 | 463 | 460 | 526.5 | 423.4 | 421.9
3229.1 | 3090.1 | 348.8 | 426.9 | 437.4 | 425.4 | 461.5 | 462.8 | 459.8 | 522.4 | 423.2 | 421.7
3230.1 | 3091.1 | 348.5 | 426.6 | 437.2 | 425.1 | 461.2 | 462.7 | 459.6 | 518.5 | 423.1 | 421.6
3231.1 | 3092.1 | 348.1 | 426.4 | 437 | 424.9 | 461 | 462.4 | 459.4 | 515.1 | 423 | 421.5
3232.1 | 3093.1 | 347.7 | 426.2 | 436.6 | 424.7 | 460.9 | 462.3 | 459.2 | 512 | 422.8 | 421.4
3233.1 | 3094.1 | 347.4 | 425.9 | 436.3 | 424.5 | 460.7 | 462.1 | 459 | 509.1 | 422.7 | 421.2
3234.1 | 3095.1 | 347 | 425.7 | 436.1 | 424.3 | 460.5 | 461.9 | 458.8 | 506.5 | 422.6 | 421.1
3235.1 | 3096.1 | 346.7 | 425.5 | 435.8 | 424 | 460.3 | 461.7 | 458.6 | 504 | 422.4 | 421
3236.1 | 3097.1 | 346.3 | 425.2 | 435.5 | 423.8 | 460.1 | 461.5 | 458.4 | 503.1 | 421.9 | 420.8
3237.1 | 3098.1 | 345.9 | 425 | 435.3 | 423.6 | 459.9 | 461.3 | 458.2 | 533.6 | 421.4 | 420.7
3238.1 | 3099.1 | 345.6 | 424.7 | 435 | 423.3 | 459.7 | 461.1 | 458 | 552.3 | 421 | 420.6
3239.1 | 3100.1 | 345.2 | 424.5 | 434.7 | 423.1 | 459.6 | 460.9 | 457.8 | 572.2 | 420.7 | 420.4
3240.1 | 3101.1 | 344.9 | 424.3 | 434.5 | 422.9 | 459.4 | 460.7 | 457.6 | 595.7 | 420.9 | 420.3
3241.1 | 3102.1 | 344.5 | 424 | 434.2 | 422.6 | 459.1 | 460.5 | 457.4 | 580.8 | 421.2 | 420.2
3242.1 | 3103.1 | 344.2 | 423.8 | 433.9 | 422.4 | 459 | 460.3 | 457.2 | 575.5 | 420.2 | 420
3243.1 | 3104.1 | 343.9 | 423.6 | 433.6 | 422.2 | 458.8 | 460.2 | 457 | 598.9 | 420.7 | 419.9
3244.1 | 3105.1 | 343.5 | 423.3 | 433.4 | 422 | 458.6 | 460 | 456.8 | 580.8 | 420.8 | 419.8
3245.1 | 3106.1 | 343.2 | 423.1 | 433.1 | 421.8 | 458.3 | 459.7 | 456.6 | 585.4 | 419.5 | 419.6
3246.1 | 3107.1 | 342.8 | 422.9 | 432.8 | 421.6 | 458.2 | 459.6 | 456.4 | 600.9 | 420.3 | 419.5
3247.1 | 3108.1 | 342.5 | 422.6 | 432.6 | 421.3 | 458 | 459.4 | 456.1 | 581.4 | 420.1 | 419.4
3248.1 | 3109.1 | 342.1 | 422.4 | 432.3 | 421.1 | 457.8 | 459.2 | 455.9 | 596.5 | 419.2 | 419.3
3249.1 | 3110.1 | 341.8 | 422.1 | 432 | 420.9 | 457.6 | 459 | 455.7 | 600.3 | 419.9 | 419.1
3250.1 | 3111.1 | 341.4 | 421.9 | 431.7 | 420.7 | 457.4 | 458.8 | 455.5 | 582.5 | 419.5 | 419
3251.1 | 3112.1 | 341 | 421.7 | 431.5 | 420.4 | 457.2 | 458.6 | 455.3 | 605.9 | 419 | 418.9
3252.1 | 3113.1 | 340.7 | 421.4 | 431.3 | 420.2 | 457 | 458.4 | 455.1 | 599.1 | 419.4 | 418.7
3253.1 | 3114.1 | 340.3 | 421.2 | 430.9 | 420 | 456.8 | 458.2 | 454.9 | 586.1 | 418.7 | 418.6
3254.1 | 3115.1 | 340 | 421 | 430.7 | 419.7 | 456.6 | 458 | 454.7 | 610.9 | 418.7 | 418.5
3255.1 | 3116.1 | 339.6 | 420.7 | 430.4 | 419.5 | 456.4 | 457.8 | 454.5 | 625 | 418 | 418.3
3256.1 | 3117.1 | 339.3 | 420.5 | 430.2 | 419.2 | 456.2 | 457.6 | 454.3 | 633.6 | 417.9 | 418.2
3257.1 | 3118.1 | 338.9 | 420.3 | 429.9 | 419 | 456 | 457.4 | 454 | 644.5 | 418.3 | 418.1
3258.1 | 3119.1 | 338.6 | 420 | 429.6 | 418.8 | 455.8 | 457.2 | 453.8 | 619.6 | 418.4 | 417.9
3259.1 | 3120.1 | 338.3 | 419.8 | 429.4 | 418.5 | 455.6 | 457 | 453.6 | 618.6 | 417.3 | 417.8
3260.1 | 3121.1 | 337.9 | 419.5 | 429.1 | 418.3 | 455.4 | 456.8 | 453.4 | 629.3 | 418 | 417.7
3261.1 | 3122.1 | 337.6 | 419.3 | 428.8 | 418.1 | 455.2 | 456.6 | 453.2 | 606.5 | 418 | 417.5
3262.1 | 3123.1 | 337.2 | 419.1 | 428.6 | 417.8 | 455 | 456.4 | 453 | 589.1 | 417.9 | 417.4
3263.1 | 3124.1 | 336.9 | 418.8 | 428.3 | 417.6 | 454.8 | 456.2 | 452.8 | 575.3 | 417.8 | 417.2
3264.1 | 3125.1 | 336.5 | 418.6 | 428 | 417.4 | 454.6 | 456 | 452.6 | 564.1 | 417.6 | 417.1
3265.1 | 3126.1 | 336.2 | 418.4 | 427.7 | 417.2 | 454.4 | 455.8 | 452.4 | 554.7 | 417.5 | 417
3266.1 | 3127.1 | 335.9 | 418.1 | 427.5 | 416.9 | 454.2 | 455.6 | 452.2 | 546.6 | 417.4 | 416.8
3267.1 | 3128.1 | 335.5 | 417.9 | 427.2 | 416.7 | 454 | 455.4 | 451.9 | 539.6 | 417.2 | 416.7
3268.1 | 3129.1 | 335.2 | 417.7 | 426.9 | 416.5 | 453.8 | 455.2 | 451.7 | 533.4 | 417.1 | 416.6
3269.1 | 3130.1 | 334.8 | 417.4 | 426.7 | 416.3 | 453.6 | 455 | 451.5 | 528 | 416.9 | 416.4
3270.1 | 3131.1 | 334.5 | 417.2 | 426.4 | 416.1 | 453.4 | 454.8 | 451.3 | 523.1 | 416.8 | 416.3
3271.1 | 3132.1 | 334.1 | 417 | 426.1 | 415.8 | 453.2 | 454.6 | 451.1 | 518.7 | 416.7 | 416.1
3272.1 | 3133.1 | 333.8 | 416.7 | 425.9 | 415.6 | 453 | 454.4 | 450.9 | 514.7 | 416.5 | 416
3273.1 | 3134.1 | 333.4 | 416.4 | 425.6 | 415.4 | 452.7 | 454.2 | 450.7 | 511.1 | 416.4 | 415.8
3274.1 | 3135.1 | 333.1 | 416.2 | 425.3 | 415.2 | 452.6 | 454 | 450.5 | 507.8 | 416.2 | 415.7
3275.1 | 3136.1 | 332.8 | 416 | 425 | 415 | 452.4 | 453.8 | 450.3 | 504.8 | 416.1 | 415.5
3276.1 | 3137.1 | 332.4 | 415.7 | 424.8 | 414.7 | 452.2 | 453.6 | 450.1 | 502.1 | 415.9 | 415.4
3277.1 | 3138.1 | 332.1 | 415.5 | 424.5 | 414.5 | 452 | 453.4 | 449.8 | 499.7 | 415.8 | 415.3
3278.1 | 3139.1 | 331.8 | 415.3 | 424.3 | 414.3 | 451.8 | 453.2 | 449.6 | 498.5 | 415.5 | 415.1
3279.1 | 3140.1 | 331.4 | 415.1 | 424 | 414.1 | 451.6 | 453 | 449.4 | 529.1 | 414.6 | 415
3280.1 | 3141.1 | 331.1 | 414.8 | 423.7 | 413.9 | 451.4 | 452.8 | 449.2 | 548.4 | 414.5 | 414.9
3281.1 | 3142.1 | 330.8 | 414.6 | 423.4 | 413.7 | 451.2 | 452.6 | 449 | 567.9 | 414.5 | 414.7
3282.1 | 3143.1 | 330.4 | 414.4 | 423.2 | 413.5 | 451 | 452.4 | 448.8 | 591.7 | 414 | 414.5
3283.1 | 3144.1 | 330.1 | 414.1 | 423 | 413.2 | 450.8 | 452.2 | 448.6 | 576.9 | 414.5 | 414.4
3284.1 | 3145.1 | 329.8 | 413.9 | 422.7 | 413 | 450.6 | 452 | 448.4 | 571.8 | 413.7 | 414.3
3285.1 | 3146.1 | 329.4 | 413.7 | 422.4 | 412.8 | 450.4 | 451.8 | 448.2 | 595.2 | 414 | 414.1
3286.1 | 3147.1 | 329.1 | 413.4 | 422.1 | 412.6 | 450.2 | 451.6 | 447.9 | 577.2 | 414.1 | 414
3287.1 | 3148.1 | 328.8 | 413.2 | 421.9 | 412.4 | 450 | 451.4 | 447.8 | 582 | 413.2 | 413.8
3288.1 | 3149.1 | 328.5 | 413 | 421.6 | 412.3 | 449.9 | 451.2 | 447.5 | 597.4 | 413.7 | 413.7
3289.1 | 3150.1 | 328.1 | 412.7 | 421.3 | 412 | 449.6 | 451 | 447.3 | 577.9 | 413.6 | 413.6
3290.1 | 3151.1 | 327.8 | 412.5 | 421.1 | 411.8 | 449.4 | 450.8 | 447.1 | 593.4 | 412.7 | 413.4
3291.1 | 3152.1 | 327.5 | 412.3 | 420.8 | 411.6 | 449.2 | 450.6 | 446.9 | 597.1 | 413.3 | 413.3
3292.1 | 3153.1 | 327.2 | 412 | 420.5 | 411.4 | 449 | 450.4 | 446.7 | 579.5 | 412.8 | 413.1
3293.1 | 3154.1 | 326.9 | 411.8 | 420.3 | 411.2 | 448.8 | 450.2 | 446.5 | 602.8 | 412.4 | 413
3294.1 | 3155.1 | 326.6 | 411.6 | 420 | 411 | 448.6 | 450 | 446.3 | 596 | 412.8 | 412.9
3295.1 | 3156.1 | 326.3 | 411.3 | 419.7 | 410.8 | 448.4 | 449.8 | 446.1 | 583.1 | 412.1 | 412.7
3296.1 | 3157.1 | 326 | 411.1 | 419.5 | 410.6 | 448.3 | 449.6 | 445.9 | 607.9 | 412.2 | 412.6
3297.1 | 3158.1 | 325.6 | 410.9 | 419.3 | 410.4 | 448 | 449.4 | 445.7 | 622.6 | 411.6 | 412.5
3298.1 | 3159.1 | 325.3 | 410.6 | 419 | 410.2 | 447.8 | 449.2 | 445.4 | 631.4 | 411.6 | 412.3
3299.1 | 3160.1 | 325 | 410.4 | 418.7 | 410 | 447.6 | 449 | 445.2 | 642.7 | 411.6 | 412.2
3300.1 | 3161.1 | 324.7 | 410.2 | 418.5 | 409.8 | 447.4 | 448.8 | 445 | 618.1 | 411.8 | 412
3301.1 | 3162.1 | 324.4 | 409.9 | 418.3 | 409.6 | 447.2 | 448.6 | 444.8 | 616.9 | 410.7 | 411.9
3302.1 | 3163.1 | 324.1 | 409.7 | 417.9 | 409.4 | 447 | 448.4 | 444.6 | 627.9 | 411.4 | 411.7
3303.1 | 3164.1 | 323.8 | 409.5 | 417.7 | 409.2 | 446.8 | 448.2 | 444.4 | 605.4 | 411.4 | 411.6
3304.1 | 3165.1 | 323.5 | 409.2 | 417.5 | 409 | 446.6 | 448 | 444.2 | 587.9 | 411.3 | 411.5
3305.1 | 3166.1 | 323.1 | 409 | 417.2 | 408.8 | 446.4 | 447.8 | 444 | 574.1 | 411.2 | 411.3
3306.1 | 3167.1 | 322.8 | 408.8 | 416.9 | 408.6 | 446.2 | 447.6 | 443.8 | 562.7 | 411 | 411.2
3307.1 | 3168.1 | 322.5 | 408.6 | 416.7 | 408.4 | 446 | 447.4 | 443.6 | 553.1 | 410.9 | 411
3308.1 | 3169.1 | 322.2 | 408.3 | 416.5 | 408.2 | 445.8 | 447.1 | 443.4 | 544.8 | 410.8 | 410.9
3309.1 | 3170.1 | 321.9 | 408.1 | 416.1 | 408 | 445.6 | 447 | 443.1 | 537.6 | 410.6 | 410.7
3310.1 | 3171.1 | 321.6 | 407.9 | 415.9 | 407.8 | 445.4 | 446.8 | 442.9 | 531.2 | 410.5 | 410.6
3311.1 | 3172.1 | 321.3 | 407.6 | 415.7 | 407.6 | 445.2 | 446.5 | 442.7 | 525.5 | 410.3 | 410.5
3312.1 | 3173.1 | 321 | 407.4 | 415.4 | 407.4 | 445 | 446.3 | 442.5 | 520.5 | 410.2 | 410.3
3313.1 | 3174.1 | 320.6 | 407.2 | 415.1 | 407.2 | 444.8 | 446.2 | 442.3 | 515.9 | 410 | 410.2
3314.1 | 3175.1 | 320.3 | 407 | 414.8 | 407 | 444.6 | 445.9 | 442.1 | 511.8 | 409.9 | 410
3315.1 | 3176.1 | 320 | 406.7 | 414.6 | 406.8 | 444.3 | 445.7 | 441.9 | 508 | 409.7 | 409.9
3316.1 | 3177.1 | 319.7 | 406.5 | 414.3 | 406.6 | 444.2 | 445.5 | 441.7 | 504.6 | 409.5 | 409.7
3317.1 | 3178.1 | 319.4 | 406.3 | 414.1 | 406.4 | 444 | 445.3 | 441.4 | 501.4 | 409.4 | 409.6
3318.1 | 3179.1 | 319.1 | 406 | 413.9 | 406.2 | 443.7 | 445.1 | 441.2 | 498.6 | 409.2 | 409.4
3319.1 | 3180.1 | 318.8 | 405.8 | 413.6 | 406 | 443.6 | 444.9 | 441 | 496 | 409.1 | 409.3
3320.1 | 3181.1 | 318.5 | 405.6 | 413.3 | 405.8 | 443.4 | 444.7 | 440.8 | 494.8 | 408.6 | 409.1
3321.1 | 3182.1 | 318.2 | 405.3 | 413.1 | 405.6 | 443.2 | 444.5 | 440.6 | 525.4 | 408 | 409
3322.1 | 3183.1 | 317.9 | 405.1 | 412.9 | 405.4 | 442.9 | 444.3 | 440.4 | 544.6 | 407.6 | 408.9
3323.1 | 3184.1 | 317.6 | 404.9 | 412.5 | 405.3 | 442.8 | 444.1 | 440.2 | 564.5 | 407.8 | 408.7
3324.1 | 3185.1 | 317.3 | 404.7 | 412.2 | 405.1 | 442.6 | 443.9 | 440 | 588.2 | 407.4 | 408.5
3325.1 | 3186.1 | 317 | 404.4 | 412.1 | 404.8 | 442.3 | 443.7 | 439.8 | 573.6 | 407.9 | 408.4
3326.1 | 3187.1 | 316.7 | 404.2 | 411.8 | 404.7 | 442.2 | 443.5 | 439.5 | 568.7 | 407.2 | 408.3
3327.1 | 3188.1 | 316.4 | 404 | 411.5 | 404.5 | 442 | 443.3 | 439.3 | 592.2 | 407.5 | 408.1
3328.1 | 3189.1 | 316.1 | 403.7 | 411.3 | 404.3 | 441.8 | 443.1 | 439.1 | 574.5 | 407.5 | 408
3329.1 | 3190.1 | 315.8 | 403.5 | 411.1 | 404 | 441.5 | 442.9 | 438.9 | 579.2 | 406.6 | 407.8
3330.1 | 3191.1 | 315.5 | 403.3 | 410.8 | 403.9 | 441.4 | 442.7 | 438.7 | 594.9 | 407.1 | 407.7
3331.1 | 3192.1 | 315.2 | 403.1 | 410.5 | 403.7 | 441.2 | 442.5 | 438.5 | 575.6 | 407 | 407.5
3332.1 | 3193.1 | 314.9 | 402.8 | 410.3 | 403.4 | 440.9 | 442.3 | 438.3 | 590.7 | 405.9 | 407.4
3333.1 | 3194.1 | 314.6 | 402.6 | 410 | 403.2 | 440.7 | 442.1 | 438.1 | 594.8 | 406.6 | 407.2
3334.1 | 3195.1 | 314.3 | 402.4 | 409.7 | 403 | 440.6 | 441.9 | 437.9 | 577.3 | 406.4 | 407.1
3335.1 | 3196.1 | 314 | 402.1 | 409.5 | 402.8 | 440.3 | 441.7 | 437.7 | 600.6 | 405.9 | 407
3336.1 | 3197.1 | 313.7 | 401.9 | 409.3 | 402.6 | 440.1 | 441.4 | 437.4 | 593.9 | 406.2 | 406.8
3337.1 | 3198.1 | 313.4 | 401.7 | 409 | 402.4 | 440 | 441.3 | 437.2 | 581 | 405.7 | 406.7
3338.1 | 3199.1 | 313.1 | 401.5 | 408.7 | 402.2 | 439.8 | 441.1 | 437 | 605.7 | 405.3 | 406.5
3339.1 | 3200.1 | 312.8 | 401.2 | 408.5 | 402 | 439.5 | 440.9 | 436.8 | 620.5 | 404.8 | 406.3
3340.1 | 3201.1 | 312.6 | 401 | 408.2 | 401.8 | 439.3 | 440.6 | 436.6 | 629 | 405 | 406.2
3341.1 | 3202.1 | 312.3 | 400.8 | 408 | 401.6 | 439.1 | 440.5 | 436.4 | 640.2 | 405.2 | 406
3342.1 | 3203.1 | 312 | 400.5 | 407.8 | 401.4 | 438.9 | 440.2 | 436.2 | 615.8 | 405.2 | 405.9
3343.1 | 3204.1 | 311.7 | 400.3 | 407.5 | 401.2 | 438.7 | 440 | 436 | 614.7 | 404.5 | 405.8
3344.1 | 3205.1 | 311.4 | 400.1 | 407.2 | 401.1 | 438.6 | 439.8 | 435.7 | 625.5 | 404.9 | 405.6
3345.1 | 3206.1 | 311.1 | 399.9 | 407 | 400.9 | 438.3 | 439.6 | 435.5 | 602.9 | 404.8 | 405.5
3346.1 | 3207.1 | 310.8 | 399.6 | 406.8 | 400.6 | 438.1 | 439.4 | 435.3 | 585.4 | 404.7 | 405.3
3347.1 | 3208.1 | 310.5 | 399.4 | 406.5 | 400.4 | 437.9 | 439.2 | 435.1 | 571.5 | 404.6 | 405.1
3348.1 | 3209.1 | 310.2 | 399.2 | 406.2 | 400.2 | 437.7 | 439 | 434.9 | 560 | 404.5 | 405
3349.1 | 3210.1 | 309.9 | 398.9 | 406 | 400 | 437.5 | 438.8 | 434.7 | 550.2 | 404.3 | 404.9
3350.1 | 3211.1 | 309.6 | 398.7 | 405.8 | 399.8 | 437.3 | 438.6 | 434.5 | 541.8 | 404.2 | 404.7
3351.1 | 3212.1 | 309.3 | 398.5 | 405.5 | 399.6 | 437.1 | 438.4 | 434.3 | 534.3 | 404 | 404.5
3352.1 | 3213.1 | 309.1 | 398.3 | 405.2 | 399.5 | 436.9 | 438.2 | 434.1 | 527.8 | 403.9 | 404.4
3353.1 | 3214.1 | 308.8 | 398 | 405 | 399.3 | 436.7 | 438 | 433.9 | 522 | 403.8 | 404.3
3354.1 | 3215.1 | 308.5 | 397.8 | 404.7 | 399.1 | 436.5 | 437.8 | 433.6 | 516.7 | 403.6 | 404.1
3355.1 | 3216.1 | 308.2 | 397.6 | 404.5 | 398.9 | 436.3 | 437.6 | 433.4 | 512 | 403.5 | 404
3356.1 | 3217.1 | 308 | 397.4 | 404.2 | 398.7 | 436.1 | 437.4 | 433.2 | 507.7 | 403.3 | 403.8
3357.1 | 3218.1 | 307.7 | 397.1 | 404 | 398.5 | 435.8 | 437.2 | 433 | 503.8 | 403.2 | 403.7
3358.1 | 3219.1 | 307.4 | 396.9 | 403.7 | 398.3 | 435.7 | 437 | 432.8 | 500.2 | 403 | 403.5
3359.1 | 3220.1 | 307.1 | 396.7 | 403.5 | 398.1 | 435.5 | 436.8 | 432.6 | 496.9 | 402.9 | 403.4
3360.1 | 3221.1 | 306.8 | 396.5 | 403.3 | 397.8 | 435.2 | 436.6 | 432.4 | 493.8 | 402.7 | 403.2
3361.1 | 3222.1 | 306.5 | 396.2 | 403 | 397.6 | 435.1 | 436.3 | 432.2 | 490.9 | 402.6 | 403.1
3362.1 | 3223.1 | 306.3 | 396 | 402.7 | 397.4 | 434.9 | 436.2 | 432 | 489.6 | 402.2 | 402.9
3363.1 | 3224.1 | 306 | 395.8 | 402.5 | 397.2 | 434.7 | 435.9 | 431.7 | 520.4 | 401.8 | 402.8
3364.1 | 3225.1 | 305.7 | 395.6 | 402.3 | 397 | 434.4 | 435.7 | 431.5 | 539.9 | 401.4 | 402.6
3365.1 | 3226.1 | 305.4 | 395.4 | 402 | 396.8 | 434.3 | 435.5 | 431.3 | 559.9 | 401.4 | 402.4
3366.1 | 3227.1 | 305.1 | 395.1 | 401.7 | 396.6 | 434.1 | 435.3 | 431.1 | 584.2 | 401 | 402.3
3367.1 | 3228.1 | 304.9 | 394.9 | 401.5 | 396.4 | 433.9 | 435.1 | 430.9 | 569.6 | 401.4 | 402.1
3368.1 | 3229.1 | 304.6 | 394.7 | 401.3 | 396.2 | 433.7 | 434.9 | 430.7 | 564.8 | 400.8 | 402
3369.1 | 3230.1 | 304.3 | 394.5 | 401 | 396 | 433.5 | 434.7 | 430.5 | 588.5 | 401 | 401.8
3370.1 | 3231.1 | 304 | 394.2 | 400.8 | 395.8 | 433.3 | 434.5 | 430.3 | 570.5 | 401 | 401.6
3371.1 | 3232.1 | 303.7 | 394 | 400.6 | 395.6 | 433 | 434.3 | 430.1 | 575.7 | 400.1 | 401.5
3372.1 | 3233.1 | 303.4 | 393.8 | 400.3 | 395.4 | 432.9 | 434.1 | 429.9 | 591.1 | 400.6 | 401.3
3373.1 | 3234.1 | 303.2 | 393.6 | 400 | 395.2 | 432.7 | 433.9 | 429.6 | 571.6 | 400.5 | 401.2
3374.1 | 3235.1 | 302.9 | 393.3 | 399.8 | 395 | 432.4 | 433.7 | 429.4 | 587 | 399.7 | 401
3375.1 | 3236.1 | 302.6 | 393.1 | 399.6 | 394.8 | 432.3 | 433.5 | 429.2 | 590.6 | 400.1 | 400.9
3376.1 | 3237.1 | 302.3 | 392.9 | 399.3 | 394.6 | 432.1 | 433.3 | 429 | 573.1 | 399.8 | 400.7
3377.1 | 3238.1 | 302 | 392.7 | 399.1 | 394.4 | 431.9 | 433.1 | 428.8 | 597 | 399.1 | 400.5
3378.1 | 3239.1 | 301.8 | 392.4 | 398.9 | 394.2 | 431.6 | 432.9 | 428.6 | 590.3 | 399.7 | 400.4
3379.1 | 3240.1 | 301.5 | 392.2 | 398.6 | 394 | 431.5 | 432.7 | 428.4 | 577.3 | 399.2 | 400.2
3380.1 | 3241.1 | 301.2 | 392 | 398.3 | 393.8 | 431.3 | 432.5 | 428.2 | 602.6 | 398.9 | 400.1
3381.1 | 3242.1 | 300.9 | 391.8 | 398.1 | 393.6 | 431 | 432.3 | 428 | 617.6 | 398.5 | 399.9
3382.1 | 3243.1 | 300.7 | 391.6 | 397.8 | 393.4 | 430.9 | 432.1 | 427.8 | 626.2 | 398.4 | 399.8
3383.1 | 3244.1 | 300.4 | 391.4 | 397.6 | 393.2 | 430.7 | 431.9 | 427.5 | 637.6 | 398.5 | 399.6
3384.1 | 3245.1 | 300.1 | 391.1 | 397.4 | 393 | 430.5 | 431.7 | 427.3 | 613 | 398.7 | 399.4
3385.1 | 3246.1 | 299.9 | 390.9 | 397.2 | 392.8 | 430.2 | 431.4 | 427.1 | 612.2 | 397.9 | 399.3
3386.1 | 3247.1 | 299.6 | 390.7 | 396.9 | 392.7 | 430.1 | 431.3 | 426.9 | 623.1 | 398.3 | 399.1
3387.1 | 3248.1 | 299.3 | 390.5 | 396.6 | 392.5 | 429.9 | 431.1 | 426.7 | 600.4 | 398.3 | 399
3388.1 | 3249.1 | 299.1 | 390.2 | 396.4 | 392.3 | 429.6 | 430.8 | 426.5 | 582.8 | 398.2 | 398.8
3389.1 | 3250.1 | 298.8 | 390 | 396.2 | 392.1 | 429.5 | 430.6 | 426.3 | 568.6 | 398.1 | 398.7
3390.1 | 3251.1 | 298.5 | 389.8 | 395.9 | 391.9 | 429.3 | 430.4 | 426.1 | 556.8 | 398 | 398.5
3391.1 | 3252.1 | 298.2 | 389.6 | 395.7 | 391.7 | 429.1 | 430.2 | 425.9 | 546.7 | 397.8 | 398.4
3392.1 | 3253.1 | 297.9 | 389.4 | 395.5 | 391.5 | 428.8 | 430 | 425.7 | 538.1 | 397.7 | 398.2
3393.1 | 3254.1 | 297.7 | 389.2 | 395.2 | 391.3 | 428.7 | 429.8 | 425.5 | 530.3 | 397.6 | 398
3394.1 | 3255.1 | 297.4 | 389 | 394.9 | 391.1 | 428.5 | 429.6 | 425.3 | 523.6 | 397.4 | 397.9
3395.1 | 3256.1 | 297.1 | 388.7 | 394.8 | 390.9 | 428.2 | 429.4 | 425.1 | 517.5 | 397.3 | 397.8
3396.1 | 3257.1 | 296.9 | 388.5 | 394.5 | 390.7 | 428.1 | 429.2 | 424.9 | 512.1 | 397.2 | 397.6
3397.1 | 3258.1 | 296.6 | 388.3 | 394.2 | 390.5 | 427.9 | 429 | 424.7 | 507.2 | 397 | 397.4
3398.1 | 3259.1 | 296.4 | 388.1 | 394 | 390.3 | 427.7 | 428.8 | 424.4 | 502.7 | 396.9 | 397.3
3399.1 | 3260.1 | 296.1 | 387.8 | 393.8 | 390.1 | 427.4 | 428.6 | 424.2 | 498.8 | 396.7 | 397.1
3400.1 | 3261.1 | 295.8 | 387.6 | 393.5 | 390 | 427.3 | 428.4 | 424 | 495 | 396.5 | 397
3401.1 | 3262.1 | 295.6 | 387.4 | 393.2 | 389.7 | 427.1 | 428.2 | 423.8 | 491.6 | 396.4 | 396.8
3402.1 | 3263.1 | 295.3 | 387.2 | 393.1 | 389.5 | 426.8 | 428 | 423.6 | 488.3 | 396.2 | 396.7
3403.1 | 3264.1 | 295.1 | 387 | 392.8 | 389.3 | 426.7 | 427.8 | 423.4 | 485.4 | 396.1 | 396.5
3404.1 | 3265.1 | 294.8 | 386.8 | 392.5 | 389.1 | 426.5 | 427.6 | 423.2 | 484.1 | 395.7 | 396.3
3405.1 | 3266.1 | 294.6 | 386.5 | 392.3 | 388.9 | 426.3 | 427.4 | 423 | 515.5 | 395 | 396.2
3406.1 | 3267.1 | 294.3 | 386.3 | 392.1 | 388.6 | 426 | 427.2 | 422.8 | 535.1 | 394.6 | 396
3407.1 | 3268.1 | 294 | 386.1 | 391.8 | 388.5 | 425.9 | 427 | 422.6 | 555.4 | 394.7 | 395.8
3408.1 | 3269.1 | 293.8 | 385.9 | 391.6 | 388.3 | 425.7 | 426.8 | 422.3 | 579.9 | 394.5 | 395.6
3409.1 | 3270.1 | 293.5 | 385.7 | 391.4 | 388.1 | 425.4 | 426.5 | 422.1 | 565 | 394.9 | 395.5
3410.1 | 3271.1 | 293.2 | 385.4 | 391.2 | 387.9 | 425.2 | 426.3 | 421.9 | 560.4 | 394.3 | 395.3
3411.1 | 3272.1 | 293 | 385.2 | 390.9 | 387.7 | 425.1 | 426.2 | 421.7 | 584.2 | 394.2 | 395.2
3412.1 | 3273.1 | 292.7 | 385 | 390.7 | 387.5 | 424.9 | 425.9 | 421.5 | 566 | 394.5 | 395
3413.1 | 3274.1 | 292.4 | 384.8 | 390.5 | 387.2 | 424.6 | 425.7 | 421.3 | 571.3 | 393.5 | 394.9
3414.1 | 3275.1 | 292.2 | 384.6 | 390.2 | 387.1 | 424.5 | 425.5 | 421.1 | 586.8 | 394 | 394.7
3415.1 | 3276.1 | 291.9 | 384.4 | 390 | 386.9 | 424.3 | 425.3 | 420.9 | 567.1 | 394 | 394.5
3416.1 | 3277.1 | 291.7 | 384.1 | 389.8 | 386.7 | 424 | 425.1 | 420.7 | 582.9 | 393 | 394.4
3417.1 | 3278.1 | 291.4 | 383.9 | 389.5 | 386.5 | 423.8 | 424.9 | 420.5 | 586.4 | 393.7 | 394.2
3418.1 | 3279.1 | 291.1 | 383.7 | 389.3 | 386.3 | 423.7 | 424.7 | 420.3 | 568.8 | 393.3 | 394.1
3419.1 | 3280.1 | 290.9 | 383.5 | 389 | 386.1 | 423.5 | 424.5 | 420.1 | 592.9 | 392.7 | 393.9
3420.1 | 3281.1 | 290.6 | 383.3 | 388.9 | 385.9 | 423.2 | 424.3 | 419.9 | 585.8 | 393.2 | 393.7
3421.1 | 3282.1 | 290.4 | 383.1 | 388.6 | 385.7 | 423.1 | 424.1 | 419.6 | 573.1 | 392.7 | 393.6
3422.1 | 3283.1 | 290.1 | 382.9 | 388.3 | 385.6 | 422.9 | 423.9 | 419.4 | 598.3 | 392.2 | 393.4
3423.1 | 3284.1 | 289.8 | 382.6 | 388.1 | 385.3 | 422.6 | 423.7 | 419.2 | 613.2 | 392 | 393.2
3424.1 | 3285.1 | 289.6 | 382.4 | 387.9 | 385.2 | 422.4 | 423.5 | 419 | 622 | 391.9 | 393.1
3425.1 | 3286.1 | 289.3 | 382.2 | 387.6 | 385 | 422.3 | 423.3 | 418.8 | 633.1 | 392.1 | 392.9
3426.1 | 3287.1 | 289.1 | 382 | 387.4 | 384.8 | 422.1 | 423.1 | 418.6 | 608.5 | 392.3 | 392.8
3427.1 | 3288.1 | 288.8 | 381.8 | 387.2 | 384.6 | 421.8 | 422.9 | 418.4 | 607.8 | 391.3 | 392.6
3428.1 | 3289.1 | 288.6 | 381.6 | 387 | 384.4 | 421.7 | 422.7 | 418.2 | 618.3 | 391.9 | 392.4
3429.1 | 3290.1 | 288.3 | 381.4 | 386.7 | 384.2 | 421.5 | 422.5 | 418 | 595.6 | 391.9 | 392.3
3430.1 | 3291.1 | 288.1 | 381.1 | 386.5 | 384 | 421.2 | 422.3 | 417.8 | 577.9 | 391.8 | 392.1
3431.1 | 3292.1 | 287.8 | 380.9 | 386.2 | 383.8 | 421.1 | 422.1 | 417.6 | 563.6 | 391.6 | 392
3432.1 | 3293.1 | 287.5 | 380.7 | 386 | 383.7 | 420.9 | 421.9 | 417.4 | 551.9 | 391.5 | 391.8
3433.1 | 3294.1 | 287.3 | 380.5 | 385.8 | 383.5 | 420.7 | 421.7 | 417.2 | 541.8 | 391.4 | 391.6
3434.1 | 3295.1 | 287 | 380.3 | 385.6 | 383.3 | 420.4 | 421.5 | 417 | 533.1 | 391.3 | 391.5
3435.1 | 3296.1 | 286.8 | 380.1 | 385.3 | 383.1 | 420.3 | 421.3 | 416.8 | 525.4 | 391.1 | 391.3
3436.1 | 3297.1 | 286.5 | 379.9 | 385.1 | 382.9 | 420.1 | 421.1 | 416.6 | 518.7 | 391 | 391.1
3437.1 | 3298.1 | 286.3 | 379.6 | 384.9 | 382.7 | 419.9 | 420.9 | 416.4 | 512.7 | 390.8 | 391
3438.1 | 3299.1 | 286 | 379.4 | 384.6 | 382.5 | 419.7 | 420.7 | 416.2 | 507.2 | 390.7 | 390.8
3439.1 | 3300.1 | 285.7 | 379.2 | 384.4 | 382.4 | 419.5 | 420.5 | 416 | 502.2 | 390.6 | 390.7
3440.1 | 3301.1 | 285.5 | 379 | 384.2 | 382.2 | 419.3 | 420.3 | 415.8 | 497.8 | 390.4 | 390.5
3441.1 | 3302.1 | 285.2 | 378.8 | 384 | 381.9 | 419.1 | 420.1 | 415.6 | 493.7 | 390.3 | 390.3
3442.1 | 3303.1 | 285 | 378.6 | 383.7 | 381.8 | 418.9 | 419.9 | 415.4 | 489.8 | 390.1 | 390.2
3443.1 | 3304.1 | 284.7 | 378.4 | 383.5 | 381.6 | 418.8 | 419.7 | 415.2 | 486.3 | 390 | 390
3444.1 | 3305.1 | 284.5 | 378.1 | 383.3 | 381.4 | 418.5 | 419.5 | 415 | 483 | 389.8 | 389.9
3445.1 | 3306.1 | 284.2 | 377.9 | 383.1 | 381.2 | 418.3 | 419.3 | 414.8 | 479.9 | 389.7 | 389.7
3446.1 | 3307.1 | 284 | 377.8 | 382.8 | 381 | 418.2 | 419.1 | 414.6 | 477.1 | 389.5 | 389.5
3447.1 | 3308.1 | 283.7 | 377.5 | 382.6 | 380.8 | 418 | 418.9 | 414.4 | 474.4 | 389.4 | 389.4
3448.1 | 3309.1 | 283.5 | 377.3 | 382.5 | 380.6 | 417.7 | 418.7 | 414.2 | 471.9 | 389.3 | 389.2

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 48 |  |  | 2006-08-31 | 8:30
38960.3527 | 1 | 0 | 1 | EPR & PE | 7-C | Conduit
38960.3532 | 1 | 0 | 1 | 525 C | 23 kW/m2 |  | Bundle
38960.3537 | 1 | 0 | 1
38960.3542 | 1 | 0 | 1
38960.3547 | 1 | 0 | 1
38960.3552 | 1 | 0 | 1
38960.3557 | 1 | 0 | 1
38960.3561 | 1 | 0 | 1
38960.3566 | 1 | 0 | 1
38960.3571 | 1 | 0 | 1
38960.3576 | 1 | 0 | 1
38960.3581 | 1 | 0 | 1
38960.3586 | 1 | 0 | 1
38960.3591 | 1 | 0 | 1
38960.3595 | 1 | 0 | 1
38960.36 | 1 | 0 | 1
38960.3605 | 1 | 0 | 1
38960.361 | 1 | 0 | 1
38960.3615 | 1 | 0 | 1
38960.362 | 1 | 0 | 1
38960.3625 | 1 | 0 | 1
38960.363 | 1 | 0 | 1
38960.3634 | 1 | 0 | 1
38960.3639 | 1 | 0 | 1
38960.3644 | 1 | 0 | 1
38960.3649 | 1 | 0 | 1
38960.3654 | 1 | 0 | 1
38960.3659 | 1 | 0 | 1
38960.3663 | 1 | 0 | 1
38960.3668 | 1 | 0 | 1
38960.3673 | 1 | 0 | 1
38960.3678 | 1 | 0 | 1
38960.3683 | 1 | 0 | 1
38960.3688 | 1 | 0 | 1
38960.3693 | 1 | 0 | 1
38960.3697 | 1 | 0 | 1
38960.3702 | 1 | 0 | 1
38960.3707 | 1 | 0 | 1
38960.3712 | 1165 | 1184 | 1
38960.3717 | 963 | 978 | 1
38960.3722 | 945 | 900 | 1
38960.3727 | 1066 | 1082 | 1
38960.3731 | 1153 | 1082 | 1
38960.3736 | 1122 | 1050 | 1
38960.3741 | 1074 | 1004 | 1
38960.3746 | 1180 | 1148 | 1
38960.3751 | 1211 | 1141 | 1
38960.3756 | 1172 | 1141 | 1
38960.3761 | 1119 | 983 | 1
38960.3766 | 1168 | 1031 | 1
38960.377 | 1124 | 953 | 1
38960.3775 | 1237 | 1097 | 1
38960.378 | 1156 | 956 | 1
38960.3785 | 1230 | 1047 | 1
38960.379 | 1190 | 921 | 1
38960.3795 | 1250 | 958 | 1
38960.38 | 1043 | 811 | 1
38960.3804 | 1232 | 916 | 1
38960.3809 | 1273 | 910 | 1
38960.3814 | 1215 | 866 | 1
38960.3819 | 1490 | 353 | 1
38960.3824 | 1717 | 184 | 1
38960.3829 | 2022 | 185 | 1
38960.3834 | 2131 | 179 | 1
38960.3838 | 1975 | 153 | 1
38960.3843 | 1841 | 138 | 1
38960.3848 | 2185 | 141 | 1
38960.3853 | 2089 | 148 | 1
38960.3858 | 2192 | 151 | 1
38960.3863 | 1766 | 118 | 1
38960.3868 | 2114 | 146 | 1
38960.3872 | 2144 | 141 | 1
38960.3877 | 2172 | 140 | 1
38960.3882 | 2207 | 140 | 1
38960.3887 | 1983 | 122 | 1
38960.3892 | 1914 | 127 | 1
38960.3897 | 2139 | 138 | 1
38960.3902 | 2192 | 133 | 1
38960.3906 | 1919 | 113 | 1
38960.3911 | 2083 | 123 | 1
38960.3916 | 1965 | 115 | 1
38960.3921 | 2245 | 128 | 1
1
38960.3528 | 1 | 0 | 2
38960.3532 | 1 | 0 | 2
38960.3537 | 1 | 0 | 2
38960.3542 | 1 | 0 | 2
38960.3547 | 1 | 0 | 2
38960.3552 | 1 | 0 | 2
38960.3557 | 1 | 0 | 2
38960.3562 | 1 | 0 | 2
38960.3566 | 1 | 0 | 2
38960.3571 | 1 | 0 | 2
38960.3576 | 1 | 0 | 2
38960.3581 | 1 | 0 | 2
38960.3586 | 1 | 0 | 2
38960.3591 | 1 | 0 | 2
38960.3596 | 1 | 0 | 2
38960.36 | 1 | 0 | 2
38960.3605 | 1 | 0 | 2
38960.361 | 1 | 0 | 2
38960.3615 | 1 | 0 | 2
38960.362 | 1 | 0 | 2
38960.3625 | 1 | 0 | 2
38960.363 | 1 | 0 | 2
38960.3634 | 1 | 0 | 2
38960.3639 | 1 | 0 | 2
38960.3644 | 1 | 1 | 2
38960.3649 | 1 | 0 | 2
38960.3654 | 1 | 0 | 2
38960.3659 | 1 | 0 | 2
38960.3664 | 1 | 0 | 2
38960.3669 | 1 | 0 | 2
38960.3673 | 1 | 0 | 2
38960.3678 | 1 | 0 | 2
38960.3683 | 1 | 0 | 2
38960.3688 | 1 | 0 | 2
38960.3693 | 1 | 0 | 2
38960.3698 | 1 | 0 | 2
38960.3703 | 1 | 0 | 2
38960.3707 | 1 | 1 | 2
38960.3712 | 930 | 963 | 2
38960.3717 | 1190 | 1143 | 2
38960.3722 | 1023 | 972 | 2
38960.3727 | 1204 | 1167 | 2
38960.3732 | 1121 | 1140 | 2
38960.3737 | 1144 | 1146 | 2
38960.3741 | 964 | 959 | 2
38960.3746 | 1073 | 1058 | 2
38960.3751 | 1184 | 1158 | 2
38960.3756 | 1128 | 1036 | 2
38960.3761 | 1207 | 1062 | 2
38960.3766 | 1254 | 1001 | 2
38960.3771 | 1151 | 1048 | 2
38960.3775 | 1029 | 881 | 2
38960.378 | 1262 | 1047 | 2
38960.3785 | 1214 | 969 | 2
38960.379 | 1180 | 913 | 2
38960.3795 | 1233 | 1013 | 2
38960.38 | 1171 | 873 | 2
38960.3805 | 1281 | 946 | 2
38960.3809 | 1144 | 874 | 2
38960.3814 | 1217 | 809 | 2
38960.3819 | 1939 | 419 | 2
38960.3824 | 2159 | 219 | 2
38960.3829 | 1824 | 163 | 2
38960.3834 | 2170 | 172 | 2
38960.3839 | 2117 | 156 | 2
38960.3844 | 1861 | 134 | 2
38960.3848 | 2007 | 135 | 2
38960.3853 | 1986 | 128 | 2
38960.3858 | 2067 | 132 | 2
38960.3863 | 2202 | 137 | 2
38960.3868 | 2121 | 131 | 2
38960.3873 | 1739 | 103 | 2
38960.3878 | 2157 | 127 | 2
38960.3882 | 1930 | 120 | 2
38960.3887 | 1850 | 107 | 2
38960.3892 | 2256 | 131 | 2
38960.3897 | 2167 | 102 | 2
38960.3902 | 1923 | 107 | 2
38960.3907 | 1827 | 100 | 2
38960.3911 | 1875 | 102 | 2
38960.3916 | 1843 | 97 | 2
38960.3921 | 2260 | 119 | 2
2
38960.3528 | 2 | 0 | 3
38960.3533 | 1 | 0 | 3
38960.3537 | 1 | 0 | 3
38960.3542 | 1 | 0 | 3
38960.3547 | 1 | 0 | 3
38960.3552 | 2 | 0 | 3
38960.3557 | 1 | 0 | 3
38960.3562 | 1 | 0 | 3
38960.3567 | 1 | 0 | 3
38960.3571 | 1 | 0 | 3
38960.3576 | 1 | 0 | 3
38960.3581 | 1 | 0 | 3
38960.3586 | 1 | 0 | 3
38960.3591 | 1 | 0 | 3
38960.3596 | 1 | 0 | 3
38960.3601 | 1 | 0 | 3
38960.3605 | 1 | 0 | 3
38960.361 | 1 | 0 | 3
38960.3615 | 1 | 0 | 3
38960.362 | 1 | 0 | 3
38960.3625 | 1 | 0 | 3
38960.363 | 1 | 0 | 3
38960.3635 | 1 | 0 | 3
38960.3639 | 1 | 0 | 3
38960.3644 | 1 | 0 | 3
38960.3649 | 1 | 0 | 3
38960.3654 | 1 | 0 | 3
38960.3659 | 1 | 0 | 3
38960.3664 | 1 | 1 | 3
38960.3669 | 1 | 0 | 3
38960.3673 | 1 | 0 | 3
38960.3678 | 1 | 0 | 3
38960.3683 | 1 | 0 | 3
38960.3688 | 1 | 0 | 3
38960.3693 | 1 | 0 | 3
38960.3698 | 1 | 0 | 3
38960.3703 | 1 | 0 | 3
38960.3708 | 1 | 0 | 3
38960.3712 | 2 | 1 | 3
38960.3717 | 2 | 1 | 3
38960.3722 | 1 | 1 | 3
38960.3727 | 2 | 1 | 3
38960.3732 | 2 | 1 | 3
38960.3737 | 3 | 1 | 3
38960.3742 | 3 | 1 | 3
38960.3746 | 6 | 2 | 3
38960.3751 | 3 | 2 | 3
38960.3756 | 8 | 2 | 3
38960.3761 | 73 | 1 | 3
38960.3766 | 100 | 1 | 3
38960.3771 | 123 | 1 | 3
38960.3776 | 111 | 1 | 3
38960.378 | 204 | 1 | 3
38960.3785 | 238 | 1 | 3
38960.379 | 256 | 1 | 3
38960.3795 | 314 | 1 | 3
38960.38 | 394 | 1 | 3
38960.3805 | 378 | 1 | 3
38960.381 | 466 | 1 | 3
38960.3814 | 494 | 1 | 3
38960.3819 | 1722 | 0 | 3
38960.3824 | 2052 | 0 | 3
38960.3829 | 1836 | 0 | 3
38960.3834 | 1943 | 0 | 3
38960.3839 | 1837 | 0 | 3
38960.3844 | 2115 | 0 | 3
38960.3848 | 1802 | 0 | 3
38960.3853 | 2045 | 0 | 3
38960.3858 | 1812 | 1 | 3
38960.3863 | 1981 | 0 | 3
38960.3868 | 2148 | 0 | 3
38960.3873 | 1816 | 0 | 3
38960.3878 | 2180 | 0 | 3
38960.3883 | 1858 | 0 | 3
38960.3887 | 2202 | 0 | 3
38960.3892 | 2209 | 0 | 3
38960.3897 | 1744 | 0 | 3
38960.3902 | 1790 | 0 | 3
38960.3907 | 2231 | 0 | 3
38960.3912 | 2219 | 0 | 3
38960.3917 | 1917 | 0 | 3
38960.3921 | 2167 | 0 | 3
3
38960.3528 | 1 | 0 | 4
38960.3533 | 1 | 0 | 4
38960.3538 | 1 | 0 | 4
38960.3542 | 1 | 0 | 4
38960.3547 | 1 | 0 | 4
38960.3552 | 1 | 0 | 4
38960.3557 | 1 | 0 | 4
38960.3562 | 1 | 0 | 4
38960.3567 | 1 | 0 | 4
38960.3572 | 1 | 0 | 4
38960.3577 | 1 | 0 | 4
38960.3581 | 1 | 0 | 4
38960.3586 | 1 | 0 | 4
38960.3591 | 1 | 0 | 4
38960.3596 | 1 | 0 | 4
38960.3601 | 1 | 0 | 4
38960.3606 | 1 | 0 | 4
38960.3611 | 1 | 0 | 4
38960.3615 | 1 | 0 | 4
38960.362 | 1 | 0 | 4
38960.3625 | 1 | 0 | 4
38960.363 | 1 | 0 | 4
38960.3635 | 1 | 0 | 4
38960.364 | 1 | 0 | 4
38960.3645 | 1 | 0 | 4
38960.3649 | 1 | 0 | 4
38960.3654 | 1 | 0 | 4
38960.3659 | 1 | 0 | 4
38960.3664 | 1 | 0 | 4
38960.3669 | 1 | 0 | 4
38960.3674 | 1 | 0 | 4
38960.3679 | 1 | 0 | 4
38960.3683 | 1 | 0 | 4
38960.3688 | 1 | 0 | 4
38960.3693 | 1 | 0 | 4
38960.3698 | 1 | 0 | 4
38960.3703 | 1 | 0 | 4
38960.3708 | 1 | 0 | 4
38960.3713 | 1 | 0 | 4
38960.3717 | 1 | 0 | 4
38960.3722 | 1 | 0 | 4
38960.3727 | 1 | 1 | 4
38960.3732 | 1 | 0 | 4
38960.3737 | 1 | 0 | 4
38960.3742 | 1 | 1 | 4
38960.3747 | 2 | 1 | 4
38960.3752 | 1 | 0 | 4
38960.3756 | 1 | 1 | 4
38960.3761 | 1 | 1 | 4
38960.3766 | 1 | 1 | 4
38960.3771 | 1 | 0 | 4
38960.3776 | 1 | 1 | 4
38960.3781 | 2 | 1 | 4
38960.3785 | 1 | 0 | 4
38960.379 | 2 | 0 | 4
38960.3795 | 2 | 1 | 4
38960.38 | 2 | 0 | 4
38960.3805 | 2 | 1 | 4
38960.381 | 2 | 0 | 4
38960.3815 | 2 | 0 | 4
38960.3819 | 2 | 0 | 4
38960.3824 | 2 | 0 | 4
38960.3829 | 2 | 0 | 4
38960.3834 | 2 | 0 | 4
38960.3839 | 3 | 0 | 4
38960.3844 | 497 | 0 | 4
38960.3849 | 487 | 0 | 4
38960.3853 | 640 | 0 | 4
38960.3858 | 993 | 0 | 4
38960.3863 | 1596 | 0 | 4
38960.3868 | 2025 | 0 | 4
38960.3873 | 1992 | 0 | 4
38960.3878 | 1770 | 0 | 4
38960.3883 | 1976 | 0 | 4
38960.3887 | 2097 | 0 | 4
38960.3892 | 1911 | 0 | 4
38960.3897 | 1962 | 0 | 4
38960.3902 | 2303 | 0 | 4
38960.3907 | 2253 | 0 | 4
38960.3912 | 2289 | 0 | 4
38960.3917 | 2287 | 0 | 4
38960.3922 | 2319 | 0 | 4
4
38960.3528 | 1 | 0 | 5
38960.3533 | 1 | 0 | 5
38960.3538 | 1 | 0 | 5
38960.3543 | 1 | 0 | 5
38960.3547 | 1 | 0 | 5
38960.3552 | 1 | 0 | 5
38960.3557 | 1 | 0 | 5
38960.3562 | 1 | 0 | 5
38960.3567 | 1 | 0 | 5
38960.3572 | 1 | 0 | 5
38960.3577 | 1 | 0 | 5
38960.3581 | 1 | 0 | 5
38960.3586 | 1 | 0 | 5
38960.3591 | 1 | 0 | 5
38960.3596 | 1 | 0 | 5
38960.3601 | 1 | 0 | 5
38960.3606 | 1 | 0 | 5
38960.3611 | 1 | 0 | 5
38960.3616 | 1 | 0 | 5
38960.362 | 1 | 0 | 5
38960.3625 | 1 | 0 | 5
38960.363 | 1 | 0 | 5
38960.3635 | 1 | 0 | 5
38960.364 | 1 | 0 | 5
38960.3645 | 1 | 0 | 5
38960.365 | 1 | 0 | 5
38960.3654 | 1 | 0 | 5
38960.3659 | 1 | 0 | 5
38960.3664 | 1 | 0 | 5
38960.3669 | 1 | 1 | 5
38960.3674 | 1 | 0 | 5
38960.3679 | 1 | 0 | 5
38960.3684 | 1 | 0 | 5
38960.3688 | 1 | 0 | 5
38960.3693 | 1 | 0 | 5
38960.3698 | 1 | 0 | 5
38960.3703 | 1 | 0 | 5
38960.3708 | 1 | 0 | 5
38960.3713 | 1 | 1 | 5
38960.3718 | 1 | 0 | 5
38960.3722 | 2 | 0 | 5
38960.3727 | 2 | 0 | 5
38960.3732 | 2 | 1 | 5
38960.3737 | 2 | 0 | 5
38960.3742 | 3 | 0 | 5
38960.3747 | 7 | 0 | 5
38960.3752 | 3 | 0 | 5
38960.3756 | 35 | 1 | 5
38960.3761 | 74 | 0 | 5
38960.3766 | 115 | 0 | 5
38960.3771 | 130 | 0 | 5
38960.3776 | 129 | 0 | 5
38960.3781 | 213 | 0 | 5
38960.3786 | 272 | 0 | 5
38960.3791 | 260 | 0 | 5
38960.3795 | 366 | 0 | 5
38960.38 | 358 | 0 | 5
38960.3805 | 402 | 0 | 5
38960.381 | 490 | 0 | 5
38960.3815 | 549 | 0 | 5
38960.382 | 1639 | 0 | 5
38960.3825 | 1894 | 0 | 5
38960.3829 | 1823 | 0 | 5
38960.3834 | 2042 | 0 | 5
38960.3839 | 1912 | 0 | 5
38960.3844 | 1994 | 0 | 5
38960.3849 | 1863 | 0 | 5
38960.3854 | 1713 | 0 | 5
38960.3859 | 1870 | 0 | 5
38960.3863 | 1912 | 0 | 5
38960.3868 | 1799 | 0 | 5
38960.3873 | 1837 | 0 | 5
38960.3878 | 1955 | 0 | 5
38960.3883 | 2088 | 0 | 5
38960.3888 | 1851 | 0 | 5
38960.3893 | 1716 | 0 | 5
38960.3897 | 1834 | 0 | 5
38960.3902 | 1873 | 0 | 5
38960.3907 | 2137 | 0 | 5
38960.3912 | 1975 | 0 | 5
38960.3917 | 2009 | 0 | 5
38960.3922 | 1844 | 0 | 5
5
38960.3528 | 1 | 0 | 6
38960.3533 | 1 | 0 | 6
38960.3538 | 1 | 0 | 6
38960.3543 | 1 | 0 | 6
38960.3548 | 1 | 0 | 6
38960.3553 | 1 | 0 | 6
38960.3557 | 1 | 0 | 6
38960.3562 | 1 | 0 | 6
38960.3567 | 1 | 0 | 6
38960.3572 | 1 | 0 | 6
38960.3577 | 1 | 0 | 6
38960.3582 | 1 | 0 | 6
38960.3586 | 1 | 0 | 6
38960.3591 | 1 | 0 | 6
38960.3596 | 1 | 0 | 6
38960.3601 | 1 | 0 | 6
38960.3606 | 1 | 0 | 6
38960.3611 | 1 | 0 | 6
38960.3616 | 1 | 0 | 6
38960.362 | 1 | 0 | 6
38960.3625 | 1 | 0 | 6
38960.363 | 1 | 0 | 6
38960.3635 | 1 | 0 | 6
38960.364 | 1 | 0 | 6
38960.3645 | 1 | 0 | 6
38960.365 | 1 | 0 | 6
38960.3655 | 1 | 0 | 6
38960.3659 | 1 | 0 | 6
38960.3664 | 1 | 0 | 6
38960.3669 | 1 | 0 | 6
38960.3674 | 1 | 0 | 6
38960.3679 | 1 | 0 | 6
38960.3684 | 1 | 0 | 6
38960.3689 | 1 | 0 | 6
38960.3693 | 1 | 0 | 6
38960.3698 | 1 | 0 | 6
38960.3703 | 1 | 0 | 6
38960.3708 | 1 | 0 | 6
38960.3713 | 1 | 0 | 6
38960.3718 | 1 | 0 | 6
38960.3723 | 1 | 0 | 6
38960.3727 | 2 | 0 | 6
38960.3732 | 1 | 0 | 6
38960.3737 | 1 | 0 | 6
38960.3742 | 1 | 0 | 6
38960.3747 | 1 | 0 | 6
38960.3752 | 1 | 0 | 6
38960.3757 | 1 | 0 | 6
38960.3761 | 1 | 0 | 6
38960.3766 | 1 | 0 | 6
38960.3771 | 1 | 0 | 6
38960.3776 | 2 | 0 | 6
38960.3781 | 1 | 0 | 6
38960.3786 | 1 | 0 | 6
38960.3791 | 2 | 0 | 6
38960.3795 | 2 | 0 | 6
38960.38 | 2 | 0 | 6
38960.3805 | 2 | 0 | 6
38960.381 | 1 | 0 | 6
38960.3815 | 2 | 0 | 6
38960.382 | 2 | 0 | 6
38960.3825 | 2 | 0 | 6
38960.383 | 2 | 0 | 6
38960.3834 | 2 | 0 | 6
38960.3839 | 2 | 0 | 6
38960.3844 | 2 | 0 | 6
38960.3849 | 2 | 0 | 6
38960.3854 | 4 | 0 | 6
38960.3859 | 624 | 0 | 6
38960.3864 | 13 | 0 | 6
38960.3868 | 1887 | 0 | 6
38960.3873 | 1787 | 0 | 6
38960.3878 | 1584 | 0 | 6
38960.3883 | 1799 | 0 | 6
38960.3888 | 1936 | 0 | 6
38960.3893 | 1792 | 0 | 6
38960.3898 | 1800 | 0 | 6
38960.3902 | 1940 | 0 | 6
38960.3907 | 2030 | 0 | 6
38960.3912 | 1866 | 0 | 6
38960.3917 | 2159 | 0 | 6
38960.3922 | 1867 | 0 | 6
6
38960.3528 | 1 | 0 | 7
38960.3533 | 2 | 0 | 7
38960.3538 | 1 | 0 | 7
38960.3543 | 1 | 0 | 7
38960.3548 | 1 | 0 | 7
38960.3553 | 1 | 0 | 7
38960.3558 | 1 | 0 | 7
38960.3562 | 1 | 0 | 7
38960.3567 | 1 | 0 | 7
38960.3572 | 1 | 0 | 7
38960.3577 | 1 | 0 | 7
38960.3582 | 1 | 0 | 7
38960.3587 | 1 | 0 | 7
38960.3592 | 1 | 0 | 7
38960.3596 | 1 | 0 | 7
38960.3601 | 1 | 0 | 7
38960.3606 | 1 | 0 | 7
38960.3611 | 1 | 0 | 7
38960.3616 | 1 | 0 | 7
38960.3621 | 1 | 0 | 7
38960.3626 | 1 | 0 | 7
38960.363 | 1 | 0 | 7
38960.3635 | 1 | 0 | 7
38960.364 | 1 | 0 | 7
38960.3645 | 1 | 0 | 7
38960.365 | 1 | 0 | 7
38960.3655 | 1 | 0 | 7
38960.366 | 1 | 0 | 7
38960.3664 | 1 | 0 | 7
38960.3669 | 1 | 0 | 7
38960.3674 | 1 | 0 | 7
38960.3679 | 1 | 0 | 7
38960.3684 | 1 | 0 | 7
38960.3689 | 1 | 0 | 7
38960.3694 | 1 | 0 | 7
38960.3698 | 1 | 0 | 7
38960.3703 | 1 | 0 | 7
38960.3708 | 1 | 0 | 7
38960.3713 | 1 | 0 | 7
38960.3718 | 1 | 0 | 7
38960.3723 | 1 | 0 | 7
38960.3728 | 1 | 0 | 7
38960.3733 | 2 | 0 | 7
38960.3737 | 2 | 0 | 7
38960.3742 | 3 | 0 | 7
38960.3747 | 7 | 0 | 7
38960.3752 | 2 | 1 | 7
38960.3757 | 37 | 0 | 7
38960.3762 | 85 | 0 | 7
38960.3767 | 114 | 0 | 7
38960.3771 | 134 | 0 | 7
38960.3776 | 134 | 0 | 7
38960.3781 | 218 | 0 | 7
38960.3786 | 226 | 0 | 7
38960.3791 | 280 | 0 | 7
38960.3796 | 358 | 0 | 7
38960.3801 | 370 | 0 | 7
38960.3805 | 397 | 0 | 7
38960.381 | 498 | 0 | 7
38960.3815 | 539 | 0 | 7
38960.382 | 1916 | 0 | 7
38960.3825 | 1839 | 0 | 7
38960.383 | 2076 | 0 | 7
38960.3835 | 1787 | 0 | 7
38960.3839 | 1894 | 0 | 7
38960.3844 | 1711 | 0 | 7
38960.3849 | 1706 | 0 | 7
38960.3854 | 2184 | 0 | 7
38960.3859 | 1894 | 0 | 7
38960.3864 | 1720 | 0 | 7
38960.3869 | 2187 | 0 | 7
38960.3873 | 2187 | 0 | 7
38960.3878 | 2160 | 0 | 7
38960.3883 | 1769 | 0 | 7
38960.3888 | 2139 | 0 | 7
38960.3893 | 1843 | 0 | 7
38960.3898 | 1787 | 0 | 7
38960.3903 | 1731 | 0 | 7
38960.3908 | 1741 | 0 | 7
38960.3912 | 1995 | 0 | 7
38960.3917 | 1988 | 0 | 7
38960.3922 | 1796 | 0 | 7
7
38960.3528 | 1 | 0 | 8
38960.3533 | 1 | 0 | 8
38960.3538 | 1 | 0 | 8
38960.3543 | 1 | 0 | 8
38960.3548 | 1 | 0 | 8
38960.3553 | 1 | 0 | 8
38960.3558 | 1 | 0 | 8
38960.3562 | 1 | 0 | 8
38960.3567 | 1 | 0 | 8
38960.3572 | 1 | 0 | 8
38960.3577 | 1 | 0 | 8
38960.3582 | 1 | 0 | 8
38960.3587 | 1 | 0 | 8
38960.3592 | 1 | 0 | 8
38960.3597 | 1 | 0 | 8
38960.3601 | 1 | 0 | 8
38960.3606 | 1 | 0 | 8
38960.3611 | 1 | 0 | 8
38960.3616 | 1 | 0 | 8
38960.3621 | 1 | 0 | 8
38960.3626 | 1 | 0 | 8
38960.3631 | 1 | 0 | 8
38960.3635 | 1 | 0 | 8
38960.364 | 1 | 0 | 8
38960.3645 | 1 | 0 | 8
38960.365 | 1 | 0 | 8
38960.3655 | 1 | 0 | 8
38960.366 | 1 | 0 | 8
38960.3665 | 1 | 0 | 8
38960.3669 | 1 | 0 | 8
38960.3674 | 1 | 1 | 8
38960.3679 | 2 | 0 | 8
38960.3684 | 1 | 0 | 8
38960.3689 | 1 | 0 | 8
38960.3694 | 1 | 0 | 8
38960.3699 | 1 | 0 | 8
38960.3703 | 1 | 0 | 8
38960.3708 | 1 | 0 | 8
38960.3713 | 1 | 0 | 8
38960.3718 | 1 | 0 | 8
38960.3723 | 1 | 0 | 8
38960.3728 | 1 | 0 | 8
38960.3733 | 1 | 0 | 8
38960.3737 | 1 | 0 | 8
38960.3742 | 1 | 0 | 8
38960.3747 | 1 | 0 | 8
38960.3752 | 1 | 0 | 8
38960.3757 | 1 | 0 | 8
38960.3762 | 1 | 0 | 8
38960.3767 | 1 | 0 | 8
38960.3772 | 1288 | 0 | 8
38960.3776 | 1750 | 0 | 8
38960.3781 | 1803 | 0 | 8
38960.3786 | 1949 | 0 | 8
38960.3791 | 2133 | 0 | 8
38960.3796 | 2116 | 0 | 8
38960.3801 | 1791 | 0 | 8
38960.3806 | 2015 | 0 | 8
38960.381 | 1804 | 0 | 8
38960.3815 | 1919 | 0 | 8
38960.382 | 2181 | 0 | 8
38960.3825 | 2339 | 0 | 8
38960.383 | 2076 | 0 | 8
38960.3835 | 2294 | 0 | 8
38960.384 | 1936 | 0 | 8
38960.3844 | 2206 | 0 | 8
38960.3849 | 2098 | 0 | 8
38960.3854 | 1897 | 0 | 8
38960.3859 | 1927 | 0 | 8
38960.3864 | 2316 | 0 | 8
38960.3869 | 2318 | 0 | 8
38960.3874 | 2086 | 0 | 8
38960.3878 | 1894 | 0 | 8
38960.3883 | 2320 | 0 | 8
38960.3888 | 1973 | 0 | 8
38960.3893 | 1999 | 0 | 8
38960.3898 | 2202 | 0 | 8
38960.3903 | 2313 | 0 | 8
38960.3908 | 1972 | 0 | 8
38960.3913 | 1859 | 0 | 8
38960.3917 | 2156 | 0 | 8
38960.3922 | 2364 | 0 | 8
8
38960.3529 | 1 | 0 | 9
38960.3534 | 1 | 0 | 9
38960.3538 | 1 | 0 | 9
38960.3543 | 1 | 0 | 9
38960.3548 | 1 | 0 | 9
38960.3553 | 1 | 0 | 9
38960.3558 | 1 | 0 | 9
38960.3563 | 1 | 0 | 9
38960.3568 | 1 | 0 | 9
38960.3572 | 1 | 0 | 9
38960.3577 | 1 | 0 | 9
38960.3582 | 1 | 0 | 9
38960.3587 | 1 | 0 | 9
38960.3592 | 1 | 0 | 9
38960.3597 | 1 | 0 | 9
38960.3602 | 1 | 0 | 9
38960.3606 | 1 | 0 | 9
38960.3611 | 1 | 0 | 9
38960.3616 | 1 | 0 | 9
38960.3621 | 1 | 0 | 9
38960.3626 | 1 | 0 | 9
38960.3631 | 1 | 0 | 9
38960.3636 | 1 | 0 | 9
38960.3641 | 1 | 0 | 9
38960.3645 | 1 | 0 | 9
38960.365 | 1 | 0 | 9
38960.3655 | 1 | 0 | 9
38960.366 | 1 | 0 | 9
38960.3665 | 1 | 0 | 9
38960.367 | 1 | 0 | 9
38960.3675 | 1 | 0 | 9
38960.3679 | 1 | 0 | 9
38960.3684 | 1 | 0 | 9
38960.3689 | 1 | 0 | 9
38960.3694 | 1 | 0 | 9
38960.3699 | 1 | 0 | 9
38960.3704 | 1 | 0 | 9
38960.3709 | 1 | 0 | 9
38960.3713 | 1 | 0 | 9
38960.3718 | 1 | 0 | 9
38960.3723 | 1 | 0 | 9
38960.3728 | 2 | 0 | 9
38960.3733 | 2 | 0 | 9
38960.3738 | 2 | 0 | 9
38960.3743 | 4 | 0 | 9
38960.3747 | 7 | 0 | 9
38960.3752 | 3 | 0 | 9
38960.3757 | 41 | 0 | 9
38960.3762 | 85 | 0 | 9
38960.3767 | 107 | 0 | 9
38960.3772 | 127 | 0 | 9
38960.3777 | 116 | 0 | 9
38960.3781 | 197 | 0 | 9
38960.3786 | 220 | 0 | 9
38960.3791 | 332 | 0 | 9
38960.3796 | 362 | 0 | 9
38960.3801 | 424 | 0 | 9
38960.3806 | 439 | 0 | 9
38960.3811 | 547 | 0 | 9
38960.3815 | 565 | 0 | 9
38960.382 | 1860 | 0 | 9
38960.3825 | 1873 | 0 | 9
38960.383 | 1824 | 0 | 9
38960.3835 | 1725 | 0 | 9
38960.384 | 1745 | 0 | 9
38960.3845 | 1991 | 0 | 9
38960.3849 | 2181 | 0 | 9
38960.3854 | 1929 | 0 | 9
38960.3859 | 1993 | 0 | 9
38960.3864 | 2024 | 0 | 9
38960.3869 | 1925 | 0 | 9
38960.3874 | 1800 | 0 | 9
38960.3879 | 1781 | 0 | 9
38960.3883 | 2212 | 0 | 9
38960.3888 | 1852 | 0 | 9
38960.3893 | 2074 | 0 | 9
38960.3898 | 2158 | 0 | 9
38960.3903 | 2188 | 0 | 9
38960.3908 | 1767 | 0 | 9
38960.3913 | 2061 | 0 | 9
38960.3917 | 2088 | 0 | 9
38960.3922 | 1733 | 0 | 9
9
38960.3529 | 1 | 0 | 10
38960.3534 | 1 | 0 | 10
38960.3539 | 1 | 0 | 10
38960.3543 | 1 | 0 | 10
38960.3548 | 1 | 0 | 10
38960.3553 | 1 | 0 | 10
38960.3558 | 1 | 0 | 10
38960.3563 | 2 | 0 | 10
38960.3568 | 1 | 0 | 10
38960.3573 | 1 | 0 | 10
38960.3577 | 1 | 0 | 10
38960.3582 | 1 | 0 | 10
38960.3587 | 1 | 0 | 10
38960.3592 | 1 | 0 | 10
38960.3597 | 1 | 0 | 10
38960.3602 | 1 | 0 | 10
38960.3607 | 1 | 0 | 10
38960.3611 | 1 | 0 | 10
38960.3616 | 1 | 0 | 10
38960.3621 | 1 | 0 | 10
38960.3626 | 1 | 0 | 10
38960.3631 | 1 | 0 | 10
38960.3636 | 1 | 0 | 10
38960.3641 | 1 | 0 | 10
38960.3645 | 1 | 0 | 10
38960.365 | 1 | 0 | 10
38960.3655 | 1 | 0 | 10
38960.366 | 1 | 0 | 10
38960.3665 | 1 | 0 | 10
38960.367 | 1 | 0 | 10
38960.3675 | 1 | 0 | 10
38960.368 | 1 | 0 | 10
38960.3684 | 1 | 0 | 10
38960.3689 | 1 | 0 | 10
38960.3694 | 1 | 0 | 10
38960.3699 | 1 | 0 | 10
38960.3704 | 1 | 0 | 10
38960.3709 | 1 | 0 | 10
38960.3714 | 1 | 0 | 10
38960.3718 | 1 | 0 | 10
38960.3723 | 1 | 0 | 10
38960.3728 | 1 | 0 | 10
38960.3733 | 1 | 0 | 10
38960.3738 | 1 | 0 | 10
38960.3743 | 1 | 0 | 10
38960.3748 | 1 | 0 | 10
38960.3752 | 1 | 0 | 10
38960.3757 | 1 | 0 | 10
38960.3762 | 1 | 0 | 10
38960.3767 | 1 | 0 | 10
38960.3772 | 2 | 0 | 10
38960.3777 | 1 | 0 | 10
38960.3782 | 3 | 0 | 10
38960.3786 | 8 | 0 | 10
38960.3791 | 1242 | 0 | 10
38960.3796 | 991 | 0 | 10
38960.3801 | 964 | 0 | 10
38960.3806 | 553 | 0 | 10
38960.3811 | 364 | 0 | 10
38960.3816 | 1889 | 0 | 10
38960.382 | 1818 | 0 | 10
38960.3825 | 2184 | 0 | 10
38960.383 | 2307 | 0 | 10
38960.3835 | 2030 | 0 | 10
38960.384 | 1959 | 0 | 10
38960.3845 | 2050 | 0 | 10
38960.385 | 2336 | 0 | 10
38960.3855 | 2190 | 0 | 10
38960.3859 | 2009 | 0 | 10
38960.3864 | 2130 | 0 | 10
38960.3869 | 1801 | 0 | 10
38960.3874 | 1809 | 0 | 10
38960.3879 | 1841 | 0 | 10
38960.3884 | 1877 | 0 | 10
38960.3889 | 1887 | 0 | 10
38960.3893 | 2030 | 0 | 10
38960.3898 | 1841 | 0 | 10
38960.3903 | 2369 | 0 | 10
38960.3908 | 2056 | 0 | 10
38960.3913 | 1911 | 0 | 10
38960.3918 | 2142 | 0 | 10
38960.3923 | 2255 | 0 | 10
10
38960.3529 | 1 | 0 | 11
38960.3534 | 1 | 0 | 11
38960.3539 | 1 | 0 | 11
38960.3544 | 1 | 0 | 11
38960.3548 | 1 | 0 | 11
38960.3553 | 1 | 0 | 11
38960.3558 | 1 | 0 | 11
38960.3563 | 1 | 0 | 11
38960.3568 | 1 | 0 | 11
38960.3573 | 1 | 0 | 11
38960.3578 | 1 | 0 | 11
38960.3583 | 1 | 0 | 11
38960.3587 | 1 | 0 | 11
38960.3592 | 2 | 0 | 11
38960.3597 | 1 | 0 | 11
38960.3602 | 1 | 0 | 11
38960.3607 | 1 | 0 | 11
38960.3612 | 1 | 0 | 11
38960.3616 | 1 | 0 | 11
38960.3621 | 1 | 0 | 11
38960.3626 | 1 | 0 | 11
38960.3631 | 1 | 0 | 11
38960.3636 | 1 | 0 | 11
38960.3641 | 1 | 0 | 11
38960.3646 | 1 | 0 | 11
38960.365 | 1 | 0 | 11
38960.3655 | 1 | 0 | 11
38960.366 | 1 | 0 | 11
38960.3665 | 1 | 0 | 11
38960.367 | 1 | 0 | 11
38960.3675 | 1 | 0 | 11
38960.368 | 1 | 0 | 11
38960.3684 | 1 | 0 | 11
38960.3689 | 1 | 0 | 11
38960.3694 | 1 | 0 | 11
38960.3699 | 1 | 0 | 11
38960.3704 | 1 | 0 | 11
38960.3709 | 1 | 0 | 11
38960.3714 | 1 | 0 | 11
38960.3719 | 1 | 0 | 11
38960.3723 | 2 | 0 | 11
38960.3728 | 1 | 0 | 11
38960.3733 | 2 | 0 | 11
38960.3738 | 2 | 0 | 11
38960.3743 | 4 | 0 | 11
38960.3748 | 9 | 0 | 11
38960.3753 | 3 | 0 | 11
38960.3757 | 43 | 0 | 11
38960.3762 | 80 | 0 | 11
38960.3767 | 108 | 0 | 11
38960.3772 | 137 | 0 | 11
38960.3777 | 147 | 0 | 11
38960.3782 | 192 | 0 | 11
38960.3787 | 254 | 0 | 11
38960.3791 | 343 | 0 | 11
38960.3796 | 297 | 0 | 11
38960.3801 | 350 | 0 | 11
38960.3806 | 388 | 0 | 11
38960.3811 | 451 | 0 | 11
38960.3816 | 619 | 0 | 11
38960.3821 | 2033 | 0 | 11
38960.3825 | 2110 | 0 | 11
38960.383 | 2015 | 0 | 11
38960.3835 | 1730 | 0 | 11
38960.384 | 2104 | 0 | 11
38960.3845 | 2066 | 0 | 11
38960.385 | 2149 | 0 | 11
38960.3855 | 2096 | 0 | 11
38960.3859 | 1778 | 0 | 11
38960.3864 | 1742 | 0 | 11
38960.3869 | 1886 | 0 | 11
38960.3874 | 1723 | 0 | 11
38960.3879 | 2245 | 0 | 11
38960.3884 | 1826 | 0 | 11
38960.3889 | 1917 | 0 | 11
38960.3894 | 2093 | 0 | 11
38960.3898 | 2091 | 0 | 11
38960.3903 | 2113 | 0 | 11
38960.3908 | 2000 | 0 | 11
38960.3913 | 1962 | 0 | 11
38960.3918 | 2072 | 0 | 11
38960.3923 | 2098 | 0 | 11
11
38960.3529 | 1 | 0 | 12
38960.3534 | 1 | 0 | 12
38960.3539 | 1 | 0 | 12
38960.3544 | 1 | 0 | 12
38960.3549 | 1 | 0 | 12
38960.3553 | 1 | 0 | 12
38960.3558 | 1 | 0 | 12
38960.3563 | 1 | 0 | 12
38960.3568 | 1 | 0 | 12
38960.3573 | 1 | 0 | 12
38960.3578 | 1 | 0 | 12
38960.3583 | 1 | 0 | 12
38960.3587 | 1 | 0 | 12
38960.3592 | 1 | 0 | 12
38960.3597 | 1 | 0 | 12
38960.3602 | 1 | 0 | 12
38960.3607 | 1 | 0 | 12
38960.3612 | 1 | 0 | 12
38960.3617 | 1 | 0 | 12
38960.3622 | 1 | 0 | 12
38960.3626 | 1 | 0 | 12
38960.3631 | 1 | 0 | 12
38960.3636 | 1 | 0 | 12
38960.3641 | 1 | 0 | 12
38960.3646 | 1 | 0 | 12
38960.3651 | 1 | 0 | 12
38960.3656 | 1 | 0 | 12
38960.366 | 1 | 0 | 12
38960.3665 | 1 | 0 | 12
38960.367 | 1 | 0 | 12
38960.3675 | 1 | 0 | 12
38960.368 | 1 | 0 | 12
38960.3685 | 1 | 0 | 12
38960.369 | 1 | 0 | 12
38960.3694 | 1 | 0 | 12
38960.3699 | 1 | 0 | 12
38960.3704 | 1 | 0 | 12
38960.3709 | 1 | 0 | 12
38960.3714 | 1 | 0 | 12
38960.3719 | 1 | 0 | 12
38960.3724 | 1 | 0 | 12
38960.3728 | 1 | 0 | 12
38960.3733 | 1 | 0 | 12
38960.3738 | 1 | 0 | 12
38960.3743 | 1 | 0 | 12
38960.3748 | 1 | 0 | 12
38960.3753 | 1 | 0 | 12
38960.3758 | 1 | 0 | 12
38960.3763 | 1 | 0 | 12
38960.3767 | 1 | 0 | 12
38960.3772 | 1 | 0 | 12
38960.3777 | 1 | 0 | 12
38960.3782 | 1 | 0 | 12
38960.3787 | 1 | 0 | 12
38960.3792 | 1 | 0 | 12
38960.3797 | 2 | 0 | 12
38960.3801 | 2 | 0 | 12
38960.3806 | 2 | 0 | 12
38960.3811 | 2 | 0 | 12
38960.3821 | 2 | 0 | 12
38960.3826 | 2 | 0 | 12
38960.3831 | 2 | 0 | 12
38960.3835 | 2 | 0 | 12
38960.384 | 32 | 0 | 12
38960.3845 | 514 | 0 | 12
38960.385 | 656 | 0 | 12
38960.3855 | 447 | 0 | 12
38960.386 | 1271 | 0 | 12
38960.3865 | 1870 | 0 | 12
38960.3869 | 1833 | 0 | 12
38960.3874 | 1936 | 0 | 12
38960.3879 | 1770 | 0 | 12
38960.3884 | 2219 | 0 | 12
38960.3889 | 1995 | 0 | 12
38960.3894 | 2015 | 0 | 12
38960.3899 | 1964 | 0 | 12
38960.3903 | 1901 | 0 | 12
38960.3908 | 1905 | 0 | 12
38960.3913 | 1941 | 0 | 12
38960.3918 | 2325 | 0 | 12
38960.3923 | 1807 | 0 | 12
12
38960.3529 | 1 | 0 | 13
38960.3534 | 1 | 0 | 13
38960.3539 | 1 | 0 | 13
38960.3544 | 1 | 0 | 13
38960.3549 | 1 | 0 | 13
38960.3554 | 2 | 0 | 13
38960.3558 | 1 | 0 | 13
38960.3563 | 1 | 0 | 13
38960.3568 | 1 | 0 | 13
38960.3573 | 1 | 0 | 13
38960.3578 | 1 | 0 | 13
38960.3583 | 1 | 0 | 13
38960.3588 | 1 | 0 | 13
38960.3592 | 1 | 0 | 13
38960.3597 | 1 | 0 | 13
38960.3602 | 1 | 0 | 13
38960.3607 | 1 | 0 | 13
38960.3612 | 2 | 0 | 13
38960.3617 | 1 | 0 | 13
38960.3622 | 1 | 0 | 13
38960.3627 | 1 | 0 | 13
38960.3631 | 1 | 0 | 13
38960.3636 | 1 | 0 | 13
38960.3641 | 1 | 0 | 13
38960.3646 | 1 | 0 | 13
38960.3651 | 1 | 0 | 13
38960.3656 | 1 | 0 | 13
38960.3661 | 1 | 0 | 13
38960.3665 | 1 | 0 | 13
38960.367 | 1 | 0 | 13
38960.3675 | 1 | 1 | 13
38960.368 | 1 | 0 | 13
38960.3685 | 1 | 0 | 13
38960.369 | 1 | 0 | 13
38960.3695 | 1 | 0 | 13
38960.3699 | 1 | 0 | 13
38960.3704 | 1 | 1 | 13
38960.3709 | 1 | 0 | 13
38960.3714 | 1 | 0 | 13
38960.3719 | 2 | 0 | 13
38960.3724 | 4 | 0 | 13
38960.3729 | 1 | 0 | 13
38960.3733 | 2 | 0 | 13
38960.3738 | 2 | 0 | 13
38960.3743 | 5 | 0 | 13
38960.3748 | 8 | 0 | 13
38960.3753 | 4 | 0 | 13
38960.3758 | 50 | 0 | 13
38960.3763 | 85 | 0 | 13
38960.3767 | 120 | 0 | 13
38960.3772 | 94 | 0 | 13
38960.3777 | 138 | 0 | 13
38960.3782 | 190 | 0 | 13
38960.3787 | 282 | 0 | 13
38960.3792 | 329 | 0 | 13
38960.3797 | 381 | 0 | 13
38960.3802 | 406 | 0 | 13
38960.3806 | 468 | 0 | 13
38960.3811 | 562 | 0 | 13
38960.3816 | 603 | 0 | 13
38960.3821 | 1854 | 0 | 13
38960.3826 | 1741 | 0 | 13
38960.3831 | 1969 | 0 | 13
38960.3836 | 1761 | 0 | 13
38960.384 | 1678 | 0 | 13
38960.3845 | 1763 | 0 | 13
38960.385 | 2034 | 0 | 13
38960.3855 | 2002 | 0 | 13
38960.386 | 2010 | 0 | 13
38960.3865 | 1970 | 0 | 13
38960.387 | 1838 | 0 | 13
38960.3874 | 2063 | 0 | 13
38960.3879 | 2166 | 0 | 13
38960.3884 | 2165 | 0 | 13
38960.3889 | 2217 | 0 | 13
38960.3894 | 1778 | 0 | 13
38960.3899 | 2096 | 0 | 13
38960.3904 | 2076 | 0 | 13
38960.3908 | 2033 | 0 | 13
38960.3913 | 1924 | 0 | 13
38960.3918 | 2089 | 0 | 13
38960.3923 | 2126 | 0 | 13
13
38960.353 | 1 | 0 | 14
38960.3534 | 1 | 0 | 14
38960.3539 | 1 | 0 | 14
38960.3544 | 1 | 0 | 14
38960.3549 | 1 | 0 | 14
38960.3554 | 1 | 0 | 14
38960.3559 | 1 | 0 | 14
38960.3564 | 1 | 0 | 14
38960.3568 | 1 | 0 | 14
38960.3573 | 1 | 0 | 14
38960.3578 | 1 | 0 | 14
38960.3583 | 1 | 0 | 14
38960.3588 | 1 | 0 | 14
38960.3593 | 1 | 0 | 14
38960.3598 | 1 | 0 | 14
38960.3602 | 1 | 0 | 14
38960.3607 | 1 | 0 | 14
38960.3612 | 1 | 0 | 14
38960.3617 | 2 | 0 | 14
38960.3622 | 1 | 0 | 14
38960.3627 | 1 | 0 | 14
38960.3632 | 1 | 0 | 14
38960.3636 | 1 | 0 | 14
38960.3641 | 1 | 0 | 14
38960.3646 | 1 | 0 | 14
38960.3651 | 1 | 0 | 14
38960.3656 | 1 | 0 | 14
38960.3661 | 1 | 0 | 14
38960.3666 | 1 | 0 | 14
38960.367 | 1 | 0 | 14
38960.3675 | 1 | 0 | 14
38960.368 | 1 | 0 | 14
38960.3685 | 1 | 0 | 14
38960.369 | 1 | 1 | 14
38960.3695 | 1 | 0 | 14
38960.37 | 1 | 0 | 14
38960.3705 | 1 | 0 | 14
38960.3709 | 1 | 0 | 14
38960.3714 | 1 | 0 | 14
38960.3719 | 3 | 0 | 14
38960.3724 | 4 | 0 | 14
38960.3729 | 2 | 0 | 14
38960.3734 | 2 | 0 | 14
38960.3739 | 2 | 0 | 14
38960.3743 | 5 | 0 | 14
38960.3748 | 10 | 0 | 14
38960.3753 | 3 | 0 | 14
38960.3758 | 45 | 0 | 14
38960.3763 | 76 | 0 | 14
38960.3768 | 103 | 0 | 14
38960.3772 | 85 | 0 | 14
38960.3777 | 127 | 0 | 14
38960.3782 | 217 | 0 | 14
38960.3787 | 242 | 0 | 14
38960.3792 | 270 | 0 | 14
38960.3797 | 305 | 0 | 14
38960.3802 | 423 | 0 | 14
38960.3806 | 414 | 0 | 14
38960.3811 | 509 | 0 | 14
38960.3816 | 705 | 0 | 14
38960.3821 | 1676 | 0 | 14
38960.3826 | 1965 | 0 | 14
38960.3831 | 1818 | 0 | 14
38960.3836 | 1947 | 0 | 14
38960.3841 | 1905 | 0 | 14
38960.3845 | 2125 | 0 | 14
38960.385 | 1938 | 0 | 14
38960.3855 | 1859 | 0 | 14
38960.386 | 2179 | 0 | 14
38960.3865 | 2220 | 0 | 14
38960.387 | 1897 | 0 | 14
38960.3875 | 1806 | 0 | 14
38960.3879 | 1775 | 0 | 14
38960.3884 | 1884 | 0 | 14
38960.3889 | 1989 | 0 | 14
38960.3894 | 2086 | 0 | 14
38960.3899 | 2009 | 0 | 14
38960.3904 | 2010 | 0 | 14
38960.3909 | 2123 | 0 | 14
38960.3913 | 2033 | 0 | 14
38960.3918 | 1961 | 0 | 14
38960.3923 | 2073 | 0 | 14
14
38960.353 | 1 | 0 | 15
38960.3534 | 1 | 0 | 15
38960.3539 | 1 | 0 | 15
38960.3544 | 1 | 0 | 15
38960.3549 | 1 | 0 | 15
38960.3554 | 1 | 0 | 15
38960.3559 | 1 | 0 | 15
38960.3564 | 1 | 0 | 15
38960.3569 | 1 | 0 | 15
38960.3573 | 2 | 0 | 15
38960.3578 | 1 | 0 | 15
38960.3583 | 1 | 0 | 15
38960.3588 | 1 | 0 | 15
38960.3593 | 1 | 0 | 15
38960.3598 | 1 | 0 | 15
38960.3603 | 1 | 0 | 15
38960.3607 | 1 | 0 | 15
38960.3612 | 1 | 0 | 15
38960.3617 | 1 | 0 | 15
38960.3622 | 1 | 0 | 15
38960.3627 | 1 | 0 | 15
38960.3632 | 1 | 0 | 15
38960.3637 | 1 | 0 | 15
38960.3641 | 1 | 0 | 15
38960.3646 | 1 | 0 | 15
38960.3651 | 1 | 0 | 15
38960.3656 | 1 | 1 | 15
38960.3661 | 1 | 0 | 15
38960.3666 | 1 | 0 | 15
38960.3671 | 1 | 0 | 15
38960.3675 | 1 | 0 | 15
38960.368 | 1 | 0 | 15
38960.3685 | 1 | 0 | 15
38960.369 | 1 | 0 | 15
38960.3695 | 1 | 0 | 15
38960.37 | 1 | 0 | 15
38960.3705 | 1 | 0 | 15
38960.3709 | 1 | 0 | 15
38960.3714 | 1 | 0 | 15
38960.3719 | 4 | 0 | 15
38960.3724 | 4 | 0 | 15
38960.3729 | 2 | 0 | 15
38960.3734 | 3 | 0 | 15
38960.3739 | 2 | 0 | 15
38960.3744 | 6 | 0 | 15
38960.3748 | 11 | 0 | 15
38960.3753 | 4 | 0 | 15
38960.3758 | 50 | 0 | 15
38960.3763 | 79 | 0 | 15
38960.3768 | 127 | 0 | 15
38960.3773 | 90 | 0 | 15
38960.3778 | 120 | 0 | 15
38960.3782 | 238 | 0 | 15
38960.3787 | 243 | 0 | 15
38960.3792 | 271 | 0 | 15
38960.3797 | 329 | 0 | 15
38960.3802 | 350 | 0 | 15
38960.3807 | 388 | 0 | 15
38960.3812 | 536 | 0 | 15
38960.3816 | 883 | 0 | 15
38960.3821 | 1955 | 0 | 15
38960.3826 | 2160 | 0 | 15
38960.3831 | 2034 | 0 | 15
38960.3836 | 1808 | 0 | 15
38960.3841 | 1915 | 0 | 15
38960.3846 | 2214 | 0 | 15
38960.385 | 1803 | 0 | 15
38960.3855 | 1793 | 0 | 15
38960.386 | 2016 | 0 | 15
38960.3865 | 1740 | 0 | 15
38960.387 | 2211 | 0 | 15
38960.3875 | 2016 | 0 | 15
38960.388 | 1892 | 0 | 15
38960.3884 | 2028 | 0 | 15
38960.3889 | 1992 | 0 | 15
38960.3894 | 2231 | 0 | 15
38960.3899 | 2004 | 0 | 15
38960.3904 | 1965 | 0 | 15
38960.3909 | 1984 | 0 | 15
38960.3914 | 1952 | 0 | 15
38960.3919 | 2177 | 0 | 15
38960.3923 | 2112 | 0 | 15
15
38960.353 | 1 | 0 | 16
38960.3535 | 1 | 0 | 16
38960.354 | 1 | 0 | 16
38960.3544 | 1 | 0 | 16
38960.3549 | 1 | 0 | 16
38960.3554 | 1 | 0 | 16
38960.3559 | 1 | 0 | 16
38960.3564 | 1 | 0 | 16
38960.3569 | 1 | 0 | 16
38960.3574 | 1 | 0 | 16
38960.3578 | 1 | 0 | 16
38960.3583 | 1 | 0 | 16
38960.3588 | 1 | 0 | 16
38960.3593 | 1 | 0 | 16
38960.3598 | 1 | 0 | 16
38960.3603 | 1 | 0 | 16
38960.3613 | 1 | 0 | 16
38960.3617 | 1 | 0 | 16
38960.3622 | 1 | 0 | 16
38960.3627 | 1 | 0 | 16
38960.3632 | 1 | 0 | 16
38960.3637 | 1 | 0 | 16
38960.3642 | 1 | 0 | 16
38960.3646 | 1 | 0 | 16
38960.3651 | 1 | 0 | 16
38960.3661 | 1 | 0 | 16
38960.3666 | 1 | 0 | 16
38960.3671 | 1 | 0 | 16
38960.3676 | 1 | 0 | 16
38960.368 | 1 | 0 | 16
38960.3685 | 1 | 0 | 16
38960.369 | 1 | 0 | 16
38960.3695 | 1 | 0 | 16
38960.37 | 1 | 0 | 16
38960.3705 | 1 | 0 | 16
38960.371 | 1 | 0 | 16
38960.3714 | 1 | 0 | 16
38960.3719 | 1 | 0 | 16
38960.3724 | 1 | 0 | 16
38960.3729 | 1 | 0 | 16
38960.3734 | 1 | 0 | 16
38960.3739 | 1 | 0 | 16
38960.3744 | 1 | 0 | 16
38960.3748 | 1 | 0 | 16
38960.3753 | 1 | 0 | 16
38960.3758 | 1 | 0 | 16
38960.3763 | 1 | 0 | 16
38960.3768 | 2 | 0 | 16
38960.3773 | 1314 | 0 | 16
38960.3778 | 2165 | 0 | 16
38960.3783 | 2200 | 0 | 16
38960.3787 | 1827 | 0 | 16
38960.3792 | 1924 | 0 | 16
38960.3797 | 2076 | 0 | 16
38960.3802 | 1870 | 0 | 16
38960.3807 | 1946 | 0 | 16
38960.3812 | 2297 | 0 | 16
38960.3817 | 2255 | 0 | 16
38960.3821 | 2096 | 0 | 16
38960.3826 | 1899 | 0 | 16
38960.3831 | 2288 | 0 | 16
38960.3836 | 2044 | 0 | 16
38960.3841 | 1921 | 0 | 16
38960.3846 | 2005 | 0 | 16
38960.3851 | 2045 | 0 | 16
38960.3855 | 2316 | 0 | 16
38960.386 | 2030 | 0 | 16
38960.3865 | 1972 | 0 | 16
38960.387 | 1837 | 0 | 16
38960.3875 | 1986 | 0 | 16
38960.388 | 1920 | 0 | 16
38960.3885 | 2034 | 0 | 16
38960.3889 | 2373 | 0 | 16
38960.3894 | 2336 | 0 | 16
38960.3899 | 2351 | 0 | 16
38960.3904 | 2098 | 0 | 16
38960.3909 | 1988 | 0 | 16
38960.3914 | 2280 | 0 | 16
38960.3919 | 2116 | 0 | 16
38960.3923 | 2042 | 0 | 16
16
38960.353 | 1 | 0 | 17
38960.3535 | 1 | 0 | 17
38960.354 | 1 | 0 | 17
38960.3545 | 1 | 0 | 17
38960.3549 | 1 | 0 | 17
38960.3554 | 1 | 0 | 17
38960.3559 | 2 | 0 | 17
38960.3564 | 1 | 0 | 17
38960.3569 | 1 | 0 | 17
38960.3574 | 2 | 0 | 17
38960.3579 | 1 | 0 | 17
38960.3583 | 1 | 0 | 17
38960.3588 | 1 | 0 | 17
38960.3593 | 2 | 0 | 17
38960.3598 | 1 | 0 | 17
38960.3603 | 1 | 0 | 17
38960.3608 | 1 | 0 | 17
38960.3613 | 1 | 0 | 17
38960.3617 | 1 | 0 | 17
38960.3622 | 1 | 0 | 17
38960.3627 | 1 | 0 | 17
38960.3632 | 1 | 0 | 17
38960.3637 | 1 | 0 | 17
38960.3642 | 1 | 0 | 17
38960.3647 | 1 | 0 | 17
38960.3652 | 1 | 0 | 17
38960.3656 | 1 | 0 | 17
38960.3661 | 1 | 0 | 17
38960.3666 | 1 | 0 | 17
38960.3671 | 1 | 0 | 17
38960.3676 | 1 | 0 | 17
38960.3681 | 1 | 0 | 17
38960.3686 | 1 | 0 | 17
38960.369 | 1 | 0 | 17
38960.3695 | 1 | 0 | 17
38960.37 | 1 | 0 | 17
38960.3705 | 1 | 0 | 17
38960.371 | 1 | 0 | 17
38960.3715 | 2 | 0 | 17
38960.372 | 4 | 0 | 17
38960.3724 | 4 | 0 | 17
38960.3729 | 2 | 0 | 17
38960.3734 | 2 | 0 | 17
38960.3739 | 2 | 0 | 17
38960.3744 | 6 | 0 | 17
38960.3749 | 11 | 0 | 17
38960.3754 | 4 | 0 | 17
38960.3758 | 60 | 0 | 17
38960.3763 | 85 | 0 | 17
38960.3768 | 129 | 0 | 17
38960.3773 | 92 | 0 | 17
38960.3778 | 143 | 0 | 17
38960.3783 | 202 | 0 | 17
38960.3788 | 253 | 0 | 17
38960.3792 | 340 | 0 | 17
38960.3797 | 342 | 0 | 17
38960.3802 | 425 | 0 | 17
38960.3807 | 434 | 0 | 17
38960.3812 | 538 | 0 | 17
38960.3817 | 1515 | 0 | 17
38960.3822 | 1778 | 0 | 17
38960.3827 | 1811 | 0 | 17
38960.3831 | 2111 | 0 | 17
38960.3836 | 1756 | 0 | 17
38960.3841 | 1707 | 0 | 17
38960.3846 | 2200 | 0 | 17
38960.3851 | 1810 | 0 | 17
38960.3856 | 1770 | 0 | 17
38960.3861 | 2222 | 0 | 17
38960.3865 | 2130 | 0 | 17
38960.387 | 2112 | 0 | 17
38960.3875 | 1873 | 0 | 17
38960.388 | 1844 | 0 | 17
38960.3885 | 2254 | 0 | 17
38960.389 | 1743 | 0 | 17
38960.3895 | 1886 | 0 | 17
38960.3899 | 2019 | 0 | 17
38960.3904 | 2189 | 0 | 17
38960.3909 | 1935 | 0 | 17
38960.3914 | 2263 | 0 | 17
38960.3919 | 1930 | 0 | 17
38960.3924 | 2243 | 0 | 17
17
38960.353 | 1 | 0 | 18
38960.3535 | 1 | 0 | 18
38960.354 | 1 | 0 | 18
38960.3545 | 1 | 0 | 18
38960.355 | 1 | 0 | 18
38960.3554 | 1 | 0 | 18
38960.3559 | 1 | 0 | 18
38960.3564 | 1 | 0 | 18
38960.3569 | 1 | 0 | 18
38960.3574 | 2 | 0 | 18
38960.3579 | 2 | 0 | 18
38960.3584 | 1 | 0 | 18
38960.3588 | 1 | 0 | 18
38960.3593 | 1 | 0 | 18
38960.3598 | 1 | 0 | 18
38960.3603 | 1 | 0 | 18
38960.3608 | 1 | 0 | 18
38960.3613 | 1 | 0 | 18
38960.3618 | 1 | 0 | 18
38960.3622 | 1 | 0 | 18
38960.3627 | 1 | 0 | 18
38960.3632 | 1 | 0 | 18
38960.3637 | 1 | 0 | 18
38960.3642 | 1 | 0 | 18
38960.3647 | 1 | 0 | 18
38960.3652 | 1 | 0 | 18
38960.3656 | 1 | 0 | 18
38960.3661 | 1 | 0 | 18
38960.3666 | 2 | 0 | 18
38960.3671 | 1 | 0 | 18
38960.3676 | 1 | 0 | 18
38960.3681 | 1 | 0 | 18
38960.3686 | 1 | 0 | 18
38960.3691 | 1 | 0 | 18
38960.3695 | 1 | 0 | 18
38960.37 | 1 | 0 | 18
38960.3705 | 1 | 1 | 18
38960.371 | 1 | 0 | 18
38960.3715 | 1 | 0 | 18
38960.372 | 1 | 0 | 18
38960.3725 | 1 | 0 | 18
38960.3729 | 1 | 0 | 18
38960.3734 | 1 | 0 | 18
38960.3739 | 1 | 0 | 18
38960.3744 | 1 | 0 | 18
38960.3749 | 1 | 0 | 18
38960.3754 | 1 | 0 | 18
38960.3759 | 1 | 0 | 18
38960.3763 | 1 | 0 | 18
38960.3768 | 1 | 0 | 18
38960.3773 | 2 | 0 | 18
38960.3778 | 1 | 0 | 18
38960.3783 | 232 | 0 | 18
38960.3788 | 6 | 0 | 18
38960.3793 | 917 | 1 | 18
38960.3797 | 1236 | 0 | 18
38960.3802 | 287 | 0 | 18
38960.3807 | 295 | 0 | 18
38960.3812 | 646 | 0 | 18
38960.3817 | 1703 | 0 | 18
38960.3822 | 1978 | 0 | 18
38960.3827 | 2045 | 0 | 18
38960.3831 | 2304 | 0 | 18
38960.3836 | 2311 | 0 | 18
38960.3841 | 1812 | 0 | 18
38960.3846 | 1857 | 0 | 18
38960.3851 | 2297 | 0 | 18
38960.3856 | 1912 | 0 | 18
38960.3861 | 2258 | 0 | 18
38960.3866 | 2302 | 0 | 18
38960.387 | 2058 | 0 | 18
38960.3875 | 2300 | 0 | 18
38960.388 | 2354 | 0 | 18
38960.3885 | 2321 | 0 | 18
38960.389 | 2319 | 0 | 18
38960.3895 | 1895 | 0 | 18
38960.39 | 2152 | 0 | 18
38960.3904 | 2234 | 0 | 18
38960.3909 | 2198 | 0 | 18
38960.3914 | 2190 | 0 | 18
38960.3919 | 2055 | 0 | 18
38960.3924 | 2372 | 0 | 18
18
38960.353 | 1 | 0 | 19
38960.3535 | 1 | 0 | 19
38960.354 | 1 | 0 | 19
38960.3545 | 1 | 0 | 19
38960.355 | 1 | 0 | 19
38960.3555 | 1 | 0 | 19
38960.3559 | 1 | 0 | 19
38960.3564 | 1 | 0 | 19
38960.3569 | 1 | 0 | 19
38960.3574 | 1 | 0 | 19
38960.3579 | 1 | 0 | 19
38960.3584 | 1 | 0 | 19
38960.3589 | 1 | 0 | 19
38960.3594 | 1 | 0 | 19
38960.3598 | 1 | 0 | 19
38960.3603 | 1 | 0 | 19
38960.3608 | 1 | 0 | 19
38960.3613 | 1 | 0 | 19
38960.3618 | 1 | 0 | 19
38960.3623 | 1 | 0 | 19
38960.3628 | 1 | 0 | 19
38960.3632 | 1 | 0 | 19
38960.3637 | 1 | 0 | 19
38960.3642 | 1 | 0 | 19
38960.3647 | 1 | 0 | 19
38960.3652 | 1 | 0 | 19
38960.3657 | 1 | 0 | 19
38960.3662 | 1 | 0 | 19
38960.3666 | 1 | 0 | 19
38960.3671 | 1 | 1 | 19
38960.3676 | 1 | 0 | 19
38960.3681 | 1 | 0 | 19
38960.3686 | 1 | 0 | 19
38960.3691 | 1 | 0 | 19
38960.3696 | 1 | 0 | 19
38960.37 | 1 | 0 | 19
38960.3705 | 1 | 0 | 19
38960.371 | 1 | 0 | 19
38960.3715 | 1 | 0 | 19
38960.372 | 1 | 0 | 19
38960.3725 | 1 | 0 | 19
38960.373 | 1 | 0 | 19
38960.3734 | 1 | 0 | 19
38960.3739 | 1 | 0 | 19
38960.3744 | 1 | 0 | 19
38960.3749 | 1 | 0 | 19
38960.3754 | 1 | 0 | 19
38960.3759 | 1 | 0 | 19
38960.3764 | 1 | 0 | 19
38960.3769 | 1 | 0 | 19
38960.3773 | 1 | 0 | 19
38960.3778 | 1 | 0 | 19
38960.3783 | 2 | 0 | 19
38960.3788 | 2 | 0 | 19
38960.3793 | 2 | 0 | 19
38960.3798 | 2 | 0 | 19
38960.3802 | 2 | 0 | 19
38960.3807 | 2 | 0 | 19
38960.3812 | 2 | 0 | 19
38960.3817 | 2 | 0 | 19
38960.3822 | 2 | 0 | 19
38960.3827 | 2 | 0 | 19
38960.3832 | 2 | 0 | 19
38960.3836 | 2 | 0 | 19
38960.3841 | 162 | 0 | 19
38960.3846 | 832 | 0 | 19
38960.3851 | 571 | 0 | 19
38960.3856 | 548 | 0 | 19
38960.3861 | 1428 | 0 | 19
38960.3866 | 1637 | 0 | 19
38960.387 | 1839 | 120 | 19
38960.3875 | 1950 | 103 | 19
38960.388 | 2254 | 107 | 19
38960.3885 | 1975 | 80 | 19
38960.389 | 1769 | 67 | 19
38960.3895 | 1841 | 64 | 19
38960.39 | 2276 | 65 | 19
38960.3905 | 2090 | 63 | 19
38960.3909 | 1959 | 54 | 19
38960.3914 | 1924 | 47 | 19
38960.3919 | 2154 | 54 | 19
38960.3924 | 2189 | 48 | 19
19
38960.353 | 1 | 0 | 20
38960.3535 | 1 | 0 | 20
38960.354 | 1 | 0 | 20
38960.3545 | 1 | 0 | 20
38960.355 | 1 | 0 | 20
38960.3555 | 1 | 0 | 20
38960.356 | 1 | 0 | 20
38960.3564 | 1 | 0 | 20
38960.3569 | 1 | 0 | 20
38960.3574 | 1 | 0 | 20
38960.3579 | 1 | 0 | 20
38960.3584 | 1 | 0 | 20
38960.3589 | 1 | 0 | 20
38960.3594 | 1 | 0 | 20
38960.3598 | 1 | 0 | 20
38960.3603 | 1 | 0 | 20
38960.3608 | 1 | 0 | 20
38960.3613 | 1 | 0 | 20
38960.3618 | 1 | 0 | 20
38960.3623 | 1 | 0 | 20
38960.3628 | 1 | 0 | 20
38960.3633 | 1 | 0 | 20
38960.3637 | 1 | 0 | 20
38960.3642 | 1 | 0 | 20
38960.3647 | 1 | 0 | 20
38960.3652 | 1 | 1 | 20
38960.3657 | 1 | 0 | 20
38960.3662 | 1 | 0 | 20
38960.3667 | 2 | 0 | 20
38960.3671 | 1 | 0 | 20
38960.3676 | 1 | 0 | 20
38960.3681 | 1 | 0 | 20
38960.3686 | 1 | 0 | 20
38960.3691 | 1 | 0 | 20
38960.3696 | 1 | 0 | 20
38960.3701 | 1 | 0 | 20
38960.3705 | 1 | 0 | 20
38960.371 | 1 | 0 | 20
38960.3715 | 1 | 0 | 20
38960.372 | 1 | 0 | 20
38960.3725 | 1 | 0 | 20
38960.373 | 1 | 0 | 20
38960.3735 | 1 | 0 | 20
38960.3739 | 1 | 0 | 20
38960.3744 | 1 | 0 | 20
38960.3749 | 1 | 0 | 20
38960.3754 | 1 | 0 | 20
38960.3759 | 1 | 0 | 20
38960.3764 | 1 | 0 | 20
38960.3769 | 1 | 0 | 20
38960.3773 | 1 | 0 | 20
38960.3778 | 2 | 0 | 20
38960.3783 | 2 | 0 | 20
38960.3788 | 1 | 0 | 20
38960.3793 | 1 | 0 | 20
38960.3798 | 2 | 0 | 20
38960.3803 | 1 | 0 | 20
38960.3808 | 2 | 0 | 20
38960.3812 | 1 | 0 | 20
38960.3817 | 2 | 0 | 20
38960.3822 | 2 | 0 | 20
38960.3827 | 2 | 0 | 20
38960.3832 | 1 | 0 | 20
38960.3837 | 2 | 0 | 20
38960.3842 | 2 | 0 | 20
38960.3846 | 2 | 0 | 20
38960.3851 | 2 | 0 | 20
38960.3856 | 483 | 1 | 20
38960.3861 | 504 | 55 | 20
38960.3866 | 1266 | 156 | 20
38960.3871 | 1989 | 145 | 20
38960.3876 | 1931 | 122 | 20
38960.388 | 1676 | 90 | 20
38960.3885 | 2074 | 100 | 20
38960.389 | 1755 | 76 | 20
38960.3895 | 1882 | 74 | 20
38960.39 | 1954 | 75 | 20
38960.3905 | 1855 | 61 | 20
38960.391 | 2082 | 64 | 20
38960.3914 | 2182 | 47 | 20
38960.3919 | 1915 | 49 | 20
38960.3924 | 1956 | 47 | 20
20
38960.3531 | 1 | 0 | 21
38960.3536 | 1 | 0 | 21
38960.354 | 1 | 0 | 21
38960.3545 | 1 | 0 | 21
38960.355 | 1 | 0 | 21
38960.3555 | 1 | 0 | 21
38960.356 | 1 | 0 | 21
38960.3565 | 1 | 0 | 21
38960.357 | 1 | 0 | 21
38960.3574 | 1 | 0 | 21
38960.3579 | 1 | 0 | 21
38960.3584 | 1 | 0 | 21
38960.3589 | 1 | 0 | 21
38960.3594 | 1 | 0 | 21
38960.3599 | 1 | 0 | 21
38960.3604 | 1 | 0 | 21
38960.3608 | 1 | 0 | 21
38960.3613 | 1 | 0 | 21
38960.3618 | 1 | 0 | 21
38960.3623 | 1 | 0 | 21
38960.3628 | 1 | 0 | 21
38960.3633 | 1 | 0 | 21
38960.3637 | 1 | 0 | 21
38960.3642 | 1 | 0 | 21
38960.3647 | 1 | 0 | 21
38960.3652 | 1 | 0 | 21
38960.3657 | 1 | 0 | 21
38960.3662 | 1 | 0 | 21
38960.3667 | 1 | 0 | 21
38960.3672 | 1 | 0 | 21
38960.3676 | 1 | 0 | 21
38960.3681 | 1 | 0 | 21
38960.3686 | 1 | 0 | 21
38960.3691 | 1 | 0 | 21
38960.3696 | 1 | 0 | 21
38960.3701 | 1 | 0 | 21
38960.3706 | 1 | 0 | 21
38960.371 | 1 | 0 | 21
38960.3715 | 1 | 0 | 21
38960.372 | 1 | 0 | 21
38960.3725 | 1 | 0 | 21
38960.373 | 1 | 0 | 21
38960.3735 | 1 | 0 | 21
38960.374 | 1 | 0 | 21
38960.3744 | 1 | 0 | 21
38960.3749 | 1 | 0 | 21
38960.3754 | 1 | 0 | 21
38960.3759 | 1 | 0 | 21
38960.3764 | 1 | 0 | 21
38960.3769 | 1 | 0 | 21
38960.3774 | 1 | 0 | 21
38960.3778 | 1 | 0 | 21
38960.3783 | 1 | 0 | 21
38960.3788 | 1 | 0 | 21
38960.3793 | 1 | 0 | 21
38960.3798 | 1 | 0 | 21
38960.3803 | 1 | 0 | 21
38960.3808 | 1 | 0 | 21
38960.3812 | 1 | 0 | 21
38960.3817 | 2 | 0 | 21
38960.3822 | 2 | 0 | 21
38960.3827 | 2 | 0 | 21
38960.3832 | 2 | 0 | 21
38960.3837 | 2 | 0 | 21
38960.3842 | 394 | 0 | 21
38960.3847 | 813 | 0 | 21
38960.3851 | 573 | 0 | 21
38960.3856 | 689 | 0 | 21
38960.3861 | 1537 | 0 | 21
38960.3866 | 2046 | 0 | 21
38960.3871 | 2129 | 0 | 21
38960.3876 | 2178 | 0 | 21
38960.3881 | 2230 | 0 | 21
38960.3885 | 2238 | 0 | 21
38960.389 | 1916 | 0 | 21
38960.3895 | 1809 | 0 | 21
38960.39 | 1907 | 0 | 21
38960.3905 | 1856 | 0 | 21
38960.391 | 2115 | 0 | 21
38960.3915 | 2332 | 0 | 21
38960.3919 | 1841 | 0 | 21
38960.3924 | 2093 | 0 | 21
21
38960.3531 | 1 | 0 | 22
38960.3536 | 1 | 0 | 22
38960.3541 | 1 | 0 | 22
38960.3545 | 1 | 0 | 22
38960.355 | 1 | 0 | 22
38960.3555 | 1 | 0 | 22
38960.356 | 2 | 0 | 22
38960.3565 | 1 | 0 | 22
38960.357 | 1 | 0 | 22
38960.3575 | 1 | 0 | 22
38960.3579 | 1 | 0 | 22
38960.3584 | 1 | 0 | 22
38960.3589 | 1 | 0 | 22
38960.3594 | 1 | 0 | 22
38960.3599 | 1 | 0 | 22
38960.3604 | 1 | 0 | 22
38960.3609 | 1 | 0 | 22
38960.3613 | 1 | 0 | 22
38960.3618 | 1 | 0 | 22
38960.3623 | 1 | 0 | 22
38960.3628 | 1 | 0 | 22
38960.3633 | 1 | 0 | 22
38960.3638 | 1 | 0 | 22
38960.3643 | 1 | 0 | 22
38960.3647 | 1 | 1 | 22
38960.3652 | 1 | 0 | 22
38960.3657 | 1 | 0 | 22
38960.3662 | 1 | 0 | 22
38960.3667 | 1 | 0 | 22
38960.3672 | 1 | 0 | 22
38960.3677 | 1 | 0 | 22
38960.3681 | 1 | 0 | 22
38960.3686 | 1 | 0 | 22
38960.3691 | 1 | 0 | 22
38960.3696 | 1 | 0 | 22
38960.3701 | 1 | 0 | 22
38960.3706 | 1 | 0 | 22
38960.3711 | 1 | 0 | 22
38960.3716 | 1 | 0 | 22
38960.372 | 1 | 0 | 22
38960.3725 | 1 | 0 | 22
38960.373 | 1 | 0 | 22
38960.3735 | 1 | 0 | 22
38960.374 | 1 | 0 | 22
38960.3745 | 1 | 0 | 22
38960.375 | 1 | 0 | 22
38960.3754 | 1 | 0 | 22
38960.3759 | 1 | 0 | 22
38960.3764 | 1 | 0 | 22
38960.3769 | 1 | 0 | 22
38960.3774 | 1853 | 0 | 22
38960.3779 | 1963 | 0 | 22
38960.3784 | 2183 | 0 | 22
38960.3788 | 1979 | 0 | 22
38960.3793 | 1943 | 0 | 22
38960.3798 | 1794 | 0 | 22
38960.3803 | 1975 | 0 | 22
38960.3808 | 1798 | 0 | 22
38960.3813 | 1875 | 0 | 22
38960.3818 | 2043 | 0 | 22
38960.3822 | 2202 | 0 | 22
38960.3827 | 2152 | 0 | 22
38960.3832 | 2339 | 0 | 22
38960.3837 | 1910 | 0 | 22
38960.3842 | 2059 | 0 | 22
38960.3847 | 1925 | 0 | 22
38960.3852 | 2006 | 0 | 22
38960.3856 | 2057 | 0 | 22
38960.3861 | 2256 | 0 | 22
38960.3866 | 1885 | 0 | 22
38960.3871 | 2281 | 0 | 22
38960.3876 | 2353 | 0 | 22
38960.3881 | 2129 | 0 | 22
38960.3886 | 2215 | 0 | 22
38960.3891 | 1927 | 0 | 22
38960.3895 | 2112 | 0 | 22
38960.39 | 2172 | 0 | 22
38960.3905 | 2038 | 0 | 22
38960.391 | 1922 | 0 | 22
38960.3915 | 2271 | 0 | 22
38960.392 | 2201 | 0 | 22
38960.3924 | 1962 | 0 | 22
22
38960.3531 | 1 | 0 | 23
38960.3536 | 1 | 0 | 23
38960.3541 | 1 | 0 | 23
38960.3545 | 1 | 0 | 23
38960.355 | 1 | 0 | 23
38960.3555 | 1 | 0 | 23
38960.356 | 1 | 0 | 23
38960.3565 | 1 | 0 | 23
38960.357 | 1 | 0 | 23
38960.3575 | 1 | 0 | 23
38960.358 | 1 | 0 | 23
38960.3584 | 1 | 0 | 23
38960.3589 | 1 | 0 | 23
38960.3594 | 1 | 0 | 23
38960.3599 | 1 | 0 | 23
38960.3604 | 1 | 0 | 23
38960.3609 | 1 | 0 | 23
38960.3614 | 1 | 0 | 23
38960.3618 | 1 | 0 | 23
38960.3623 | 1 | 0 | 23
38960.3628 | 1 | 0 | 23
38960.3633 | 1 | 0 | 23
38960.3638 | 1 | 0 | 23
38960.3643 | 1 | 0 | 23
38960.3648 | 1 | 0 | 23
38960.3652 | 1 | 0 | 23
38960.3657 | 1 | 0 | 23
38960.3662 | 1 | 0 | 23
38960.3667 | 1 | 0 | 23
38960.3672 | 1 | 0 | 23
38960.3677 | 1 | 0 | 23
38960.3682 | 1 | 0 | 23
38960.3686 | 1 | 0 | 23
38960.3691 | 1 | 0 | 23
38960.3696 | 1 | 0 | 23
38960.3701 | 1 | 0 | 23
38960.3706 | 1 | 0 | 23
38960.3711 | 1 | 0 | 23
38960.3716 | 1 | 0 | 23
38960.372 | 1 | 0 | 23
38960.3725 | 1 | 0 | 23
38960.373 | 1 | 0 | 23
38960.3735 | 1 | 0 | 23
38960.374 | 1 | 0 | 23
38960.3745 | 1 | 0 | 23
38960.375 | 1 | 0 | 23
38960.3755 | 1 | 0 | 23
38960.3759 | 1 | 0 | 23
38960.3764 | 1 | 0 | 23
38960.3769 | 1 | 0 | 23
38960.3774 | 1 | 0 | 23
38960.3779 | 2 | 0 | 23
38960.3784 | 2 | 0 | 23
38960.3789 | 2 | 0 | 23
38960.3793 | 2 | 0 | 23
38960.3798 | 2 | 0 | 23
38960.3803 | 2 | 0 | 23
38960.3808 | 2 | 0 | 23
38960.3813 | 2 | 0 | 23
38960.3818 | 2 | 0 | 23
38960.3823 | 2 | 0 | 23
38960.3827 | 2 | 0 | 23
38960.3832 | 2 | 0 | 23
38960.3837 | 2 | 0 | 23
38960.3842 | 391 | 0 | 23
38960.3847 | 477 | 0 | 23
38960.3852 | 683 | 0 | 23
38960.3857 | 489 | 0 | 23
38960.3861 | 1453 | 0 | 23
38960.3866 | 2066 | 0 | 23
38960.3871 | 2139 | 0 | 23
38960.3876 | 2025 | 0 | 23
38960.3881 | 2242 | 0 | 23
38960.3886 | 1886 | 0 | 23
38960.3891 | 1890 | 0 | 23
38960.3895 | 1913 | 0 | 23
38960.39 | 1992 | 0 | 23
38960.3905 | 2039 | 0 | 23
38960.391 | 2101 | 0 | 23
38960.3915 | 1950 | 0 | 23
38960.392 | 2260 | 0 | 23
38960.3925 | 1877 | 0 | 23
23
38960.3531 | 1 | 0 | 24
38960.3536 | 1 | 0 | 24
38960.3541 | 2 | 0 | 24
38960.3546 | 1 | 0 | 24
38960.3551 | 1 | 0 | 24
38960.3555 | 1 | 0 | 24
38960.356 | 1 | 0 | 24
38960.3565 | 1 | 0 | 24
38960.357 | 1 | 0 | 24
38960.3575 | 1 | 0 | 24
38960.358 | 1 | 0 | 24
38960.3585 | 1 | 0 | 24
38960.3589 | 1 | 0 | 24
38960.3594 | 1 | 0 | 24
38960.3599 | 1 | 0 | 24
38960.3604 | 1 | 0 | 24
38960.3609 | 1 | 0 | 24
38960.3614 | 1 | 0 | 24
38960.3619 | 1 | 0 | 24
38960.3623 | 1 | 0 | 24
38960.3628 | 1 | 0 | 24
38960.3633 | 1 | 0 | 24
38960.3638 | 1 | 0 | 24
38960.3643 | 1 | 0 | 24
38960.3648 | 1 | 0 | 24
38960.3653 | 1 | 0 | 24
38960.3658 | 1 | 0 | 24
38960.3662 | 1 | 0 | 24
38960.3667 | 1 | 0 | 24
38960.3672 | 1 | 0 | 24
38960.3677 | 1 | 0 | 24
38960.3682 | 1 | 0 | 24
38960.3687 | 1 | 0 | 24
38960.3692 | 1 | 0 | 24
38960.3696 | 1 | 0 | 24
38960.3701 | 2 | 0 | 24
38960.3706 | 1 | 0 | 24
38960.3711 | 1 | 0 | 24
38960.3716 | 1 | 0 | 24
38960.3721 | 1 | 0 | 24
38960.3726 | 1 | 0 | 24
38960.373 | 1 | 0 | 24
38960.3735 | 1 | 0 | 24
38960.374 | 1 | 0 | 24
38960.3745 | 1 | 0 | 24
38960.375 | 1 | 0 | 24
38960.3755 | 1 | 0 | 24
38960.376 | 1 | 0 | 24
38960.3764 | 1 | 0 | 24
38960.3769 | 1 | 0 | 24
38960.3774 | 1 | 0 | 24
38960.3779 | 1 | 0 | 24
38960.3784 | 2 | 0 | 24
38960.3789 | 3 | 0 | 24
38960.3794 | 734 | 0 | 24
38960.3798 | 613 | 0 | 24
38960.3803 | 807 | 0 | 24
38960.3808 | 900 | 0 | 24
38960.3813 | 187 | 0 | 24
38960.3818 | 2047 | 0 | 24
38960.3823 | 2161 | 0 | 24
38960.3828 | 1805 | 0 | 24
38960.3832 | 2036 | 0 | 24
38960.3837 | 2298 | 0 | 24
38960.3842 | 1803 | 0 | 24
38960.3847 | 2193 | 0 | 24
38960.3852 | 2337 | 0 | 24
38960.3857 | 2224 | 0 | 24
38960.3862 | 1937 | 0 | 24
38960.3866 | 1866 | 0 | 24
38960.3871 | 1860 | 0 | 24
38960.3876 | 2064 | 0 | 24
38960.3881 | 2369 | 0 | 24
38960.3886 | 1944 | 0 | 24
38960.3891 | 1851 | 0 | 24
38960.3896 | 2230 | 0 | 24
38960.39 | 1920 | 0 | 24
38960.3905 | 2096 | 0 | 24
38960.391 | 2276 | 0 | 24
38960.3915 | 1894 | 0 | 24
38960.392 | 2378 | 0 | 24
38960.3925 | 2358 | 0 | 24
24
38960.3531 | 1 | 0 | 25
38960.3536 | 1 | 0 | 25
38960.3541 | 1 | 0 | 25
38960.3546 | 1 | 0 | 25
38960.3551 | 2 | 0 | 25
38960.3556 | 1 | 0 | 25
38960.356 | 1 | 0 | 25
38960.3565 | 2 | 0 | 25
38960.357 | 1 | 0 | 25
38960.3575 | 1 | 0 | 25
38960.358 | 1 | 0 | 25
38960.3585 | 1 | 0 | 25
38960.359 | 1 | 0 | 25
38960.3594 | 1 | 0 | 25
38960.3599 | 1 | 0 | 25
38960.3604 | 1 | 0 | 25
38960.3609 | 1 | 0 | 25
38960.3614 | 1 | 0 | 25
38960.3619 | 1 | 0 | 25
38960.3624 | 1 | 0 | 25
38960.3628 | 1 | 0 | 25
38960.3633 | 1 | 0 | 25
38960.3638 | 1 | 0 | 25
38960.3643 | 1 | 0 | 25
38960.3648 | 1 | 0 | 25
38960.3653 | 1 | 0 | 25
38960.3658 | 1 | 0 | 25
38960.3662 | 1 | 0 | 25
38960.3667 | 1 | 0 | 25
38960.3672 | 1 | 0 | 25
38960.3677 | 1 | 0 | 25
38960.3682 | 1 | 0 | 25
38960.3687 | 1 | 0 | 25
38960.3692 | 1 | 0 | 25
38960.3697 | 1 | 0 | 25
38960.3701 | 1 | 0 | 25
38960.3706 | 1 | 0 | 25
38960.3711 | 1 | 0 | 25
38960.3716 | 1 | 0 | 25
38960.3721 | 1 | 0 | 25
38960.3726 | 1 | 0 | 25
38960.3731 | 1 | 0 | 25
38960.3735 | 1 | 0 | 25
38960.374 | 1 | 0 | 25
38960.3745 | 1 | 0 | 25
38960.375 | 1 | 0 | 25
38960.3755 | 1 | 0 | 25
38960.376 | 1 | 0 | 25
38960.3765 | 1 | 0 | 25
38960.3769 | 1 | 0 | 25
38960.3774 | 1 | 0 | 25
38960.3779 | 1 | 0 | 25
38960.3784 | 1 | 0 | 25
38960.3789 | 1 | 0 | 25
38960.3794 | 2 | 0 | 25
38960.3799 | 2 | 0 | 25
38960.3803 | 2 | 0 | 25
38960.3808 | 2 | 0 | 25
38960.3813 | 2 | 0 | 25
38960.3818 | 2 | 0 | 25
38960.3823 | 2 | 0 | 25
38960.3828 | 2 | 0 | 25
38960.3833 | 2 | 0 | 25
38960.3838 | 2 | 0 | 25
38960.3842 | 2 | 0 | 25
38960.3847 | 2 | 0 | 25
38960.3852 | 4 | 0 | 25
38960.3857 | 331 | 0 | 25
38960.3862 | 437 | 0 | 25
38960.3867 | 1592 | 0 | 25
38960.3872 | 1961 | 0 | 25
38960.3876 | 1578 | 0 | 25
38960.3881 | 2069 | 0 | 25
38960.3886 | 1827 | 0 | 25
38960.3891 | 1918 | 0 | 25
38960.3896 | 2026 | 0 | 25
38960.3901 | 2068 | 0 | 25
38960.3906 | 1714 | 0 | 25
38960.391 | 2164 | 0 | 25
38960.3915 | 2111 | 0 | 25
38960.3925 | 2050 | 0 | 25
25
38960.3531 | 1 | 0 | 26
38960.3536 | 1 | 0 | 26
38960.3541 | 1 | 0 | 26
38960.3546 | 1 | 0 | 26
38960.3551 | 1 | 0 | 26
38960.3556 | 1 | 0 | 26
38960.3561 | 1 | 0 | 26
38960.3566 | 1 | 0 | 26
38960.357 | 1 | 0 | 26
38960.3575 | 1 | 0 | 26
38960.358 | 1 | 0 | 26
38960.3585 | 1 | 0 | 26
38960.359 | 1 | 0 | 26
38960.3595 | 1 | 0 | 26
38960.3599 | 1 | 0 | 26
38960.3604 | 1 | 0 | 26
38960.3609 | 1 | 0 | 26
38960.3614 | 1 | 0 | 26
38960.3619 | 1 | 0 | 26
38960.3624 | 1 | 0 | 26
38960.3629 | 1 | 0 | 26
38960.3634 | 1 | 0 | 26
38960.3638 | 1 | 0 | 26
38960.3643 | 1 | 0 | 26
38960.3648 | 1 | 0 | 26
38960.3653 | 1 | 0 | 26
38960.3658 | 1 | 0 | 26
38960.3663 | 1 | 0 | 26
38960.3667 | 1 | 0 | 26
38960.3672 | 1 | 0 | 26
38960.3677 | 1 | 0 | 26
38960.3682 | 1 | 0 | 26
38960.3687 | 1 | 0 | 26
38960.3692 | 1 | 0 | 26
38960.3697 | 1 | 0 | 26
38960.3702 | 1 | 0 | 26
38960.3706 | 1 | 0 | 26
38960.3711 | 1 | 0 | 26
38960.3716 | 1 | 0 | 26
38960.3721 | 1 | 0 | 26
38960.3726 | 1 | 0 | 26
38960.3731 | 1 | 0 | 26
38960.3736 | 1 | 0 | 26
38960.374 | 1 | 0 | 26
38960.3745 | 1 | 0 | 26
38960.375 | 1 | 0 | 26
38960.3755 | 1 | 0 | 26
38960.376 | 1 | 0 | 26
38960.3765 | 206 | 0 | 26
38960.377 | 5 | 0 | 26
38960.3774 | 487 | 0 | 26
38960.3779 | 1804 | 0 | 26
38960.3784 | 2196 | 0 | 26
38960.3789 | 1934 | 0 | 26
38960.3794 | 2292 | 0 | 26
38960.3799 | 2252 | 0 | 26
38960.3804 | 2311 | 0 | 26
38960.3808 | 1939 | 0 | 26
38960.3813 | 2002 | 0 | 26
38960.3818 | 2089 | 0 | 26
38960.3823 | 1970 | 0 | 26
38960.3828 | 2113 | 0 | 26
38960.3833 | 1908 | 0 | 26
38960.3838 | 2347 | 0 | 26
38960.3842 | 1870 | 0 | 26
38960.3847 | 2095 | 0 | 26
38960.3852 | 2258 | 0 | 26
38960.3857 | 1978 | 0 | 26
38960.3862 | 1856 | 0 | 26
38960.3867 | 2081 | 0 | 26
38960.3872 | 1824 | 0 | 26
38960.3877 | 1987 | 0 | 26
38960.3881 | 2342 | 0 | 26
38960.3886 | 2035 | 0 | 26
38960.3891 | 1849 | 0 | 26
38960.3896 | 1841 | 0 | 26
38960.3901 | 2125 | 0 | 26
38960.3906 | 2172 | 0 | 26
38960.3911 | 2164 | 0 | 26
38960.3915 | 1886 | 0 | 26
38960.392 | 1887 | 0 | 26
38960.3925 | 2222 | 0 | 26
26
38960.3532 | 1 | 0 | 27
38960.3536 | 1 | 0 | 27
38960.3541 | 1 | 0 | 27
38960.3546 | 1 | 0 | 27
38960.3551 | 1 | 0 | 27
38960.3556 | 1 | 0 | 27
38960.3561 | 1 | 0 | 27
38960.3566 | 1 | 0 | 27
38960.357 | 1 | 0 | 27
38960.3575 | 1 | 0 | 27
38960.358 | 1 | 0 | 27
38960.3585 | 1 | 0 | 27
38960.359 | 1 | 0 | 27
38960.3595 | 1 | 0 | 27
38960.36 | 1 | 0 | 27
38960.3605 | 1 | 0 | 27
38960.3609 | 1 | 0 | 27
38960.3614 | 1 | 0 | 27
38960.3619 | 1 | 0 | 27
38960.3624 | 1 | 0 | 27
38960.3629 | 1 | 0 | 27
38960.3634 | 1 | 0 | 27
38960.3639 | 1 | 0 | 27
38960.3643 | 1 | 0 | 27
38960.3648 | 1 | 0 | 27
38960.3653 | 1 | 0 | 27
38960.3658 | 1 | 0 | 27
38960.3663 | 1 | 0 | 27
38960.3668 | 1 | 0 | 27
38960.3673 | 1 | 0 | 27
38960.3677 | 1 | 1 | 27
38960.3682 | 1 | 0 | 27
38960.3687 | 1 | 0 | 27
38960.3692 | 1 | 0 | 27
38960.3697 | 1 | 0 | 27
38960.3702 | 1 | 0 | 27
38960.3707 | 1 | 0 | 27
38960.3711 | 1 | 0 | 27
38960.3716 | 1 | 0 | 27
38960.3721 | 1 | 0 | 27
38960.3726 | 1 | 0 | 27
38960.3731 | 1 | 0 | 27
38960.3736 | 1 | 0 | 27
38960.3741 | 1 | 0 | 27
38960.3745 | 1 | 0 | 27
38960.375 | 1 | 0 | 27
38960.3755 | 1 | 0 | 27
38960.376 | 1 | 0 | 27
38960.3765 | 1 | 0 | 27
38960.377 | 1 | 0 | 27
38960.3775 | 1 | 0 | 27
38960.378 | 2 | 0 | 27
38960.3784 | 2 | 0 | 27
38960.3789 | 2 | 0 | 27
38960.3794 | 2 | 0 | 27
38960.3799 | 3 | 0 | 27
38960.3804 | 2 | 0 | 27
38960.3809 | 2 | 0 | 27
38960.3814 | 2 | 0 | 27
38960.3818 | 2 | 0 | 27
38960.3823 | 2 | 0 | 27
38960.3828 | 2 | 0 | 27
38960.3833 | 2 | 0 | 27
38960.3838 | 2 | 0 | 27
38960.3843 | 2 | 0 | 27
38960.3848 | 2 | 0 | 27
38960.3852 | 3 | 0 | 27
38960.3857 | 315 | 0 | 27
38960.3862 | 228 | 0 | 27
38960.3867 | 1903 | 0 | 27
38960.3872 | 1676 | 0 | 27
38960.3877 | 1912 | 0 | 27
38960.3882 | 1665 | 0 | 27
38960.3886 | 1965 | 0 | 27
38960.3891 | 1997 | 0 | 27
38960.3896 | 1794 | 0 | 27
38960.3901 | 1717 | 0 | 27
38960.3906 | 1995 | 0 | 27
38960.3911 | 1735 | 0 | 27
38960.3916 | 2166 | 0 | 27
38960.392 | 1852 | 0 | 27
38960.3925 | 1956 | 0 | 27
27
38960.3532 | 1 | 0 | 28
38960.3537 | 1 | 0 | 28
38960.3541 | 1 | 0 | 28
38960.3546 | 1 | 0 | 28
38960.3551 | 1 | 0 | 28
38960.3556 | 1 | 0 | 28
38960.3561 | 1 | 0 | 28
38960.3566 | 1 | 0 | 28
38960.3571 | 1 | 0 | 28
38960.3575 | 1 | 0 | 28
38960.358 | 1 | 0 | 28
38960.3585 | 2 | 0 | 28
38960.359 | 1 | 0 | 28
38960.3595 | 1 | 0 | 28
38960.36 | 1 | 0 | 28
38960.3605 | 1 | 0 | 28
38960.3609 | 1 | 0 | 28
38960.3614 | 2 | 0 | 28
38960.3619 | 1 | 0 | 28
38960.3624 | 1 | 0 | 28
38960.3629 | 1 | 0 | 28
38960.3634 | 1 | 0 | 28
38960.3639 | 1 | 0 | 28
38960.3644 | 1 | 0 | 28
38960.3648 | 1 | 0 | 28
38960.3653 | 1 | 0 | 28
38960.3658 | 1 | 0 | 28
38960.3663 | 1 | 0 | 28
38960.3668 | 1 | 0 | 28
38960.3673 | 1 | 0 | 28
38960.3678 | 1 | 0 | 28
38960.3682 | 1 | 0 | 28
38960.3687 | 1 | 0 | 28
38960.3692 | 1 | 0 | 28
38960.3697 | 1 | 0 | 28
38960.3702 | 1 | 0 | 28
38960.3707 | 1 | 0 | 28
38960.3712 | 1 | 0 | 28
38960.3716 | 1 | 0 | 28
38960.3721 | 1 | 0 | 28
38960.3726 | 1 | 0 | 28
38960.3731 | 1 | 0 | 28
38960.3736 | 1 | 0 | 28
38960.3741 | 1 | 0 | 28
38960.3746 | 1 | 0 | 28
38960.375 | 1 | 0 | 28
38960.3755 | 1 | 0 | 28
38960.376 | 1 | 0 | 28
38960.3765 | 1 | 0 | 28
38960.377 | 1 | 0 | 28
38960.3775 | 1 | 0 | 28
38960.378 | 1 | 0 | 28
38960.3784 | 2 | 0 | 28
38960.3789 | 718 | 0 | 28
38960.3794 | 1283 | 0 | 28
38960.3799 | 601 | 0 | 28
38960.3804 | 812 | 0 | 28
38960.3809 | 967 | 0 | 28
38960.3814 | 505 | 0 | 28
38960.3819 | 1872 | 0 | 28
38960.3823 | 2070 | 0 | 28
38960.3828 | 2043 | 0 | 28
38960.3833 | 2303 | 0 | 28
38960.3838 | 1903 | 0 | 28
38960.3843 | 2074 | 0 | 28
38960.3848 | 1862 | 0 | 28
38960.3853 | 2246 | 0 | 28
38960.3857 | 2335 | 0 | 28
38960.3862 | 2227 | 0 | 28
38960.3867 | 2060 | 0 | 28
38960.3872 | 2080 | 0 | 28
38960.3877 | 1977 | 0 | 28
38960.3882 | 1852 | 0 | 28
38960.3887 | 2260 | 0 | 28
38960.3891 | 2308 | 0 | 28
38960.3896 | 1836 | 0 | 28
38960.3901 | 2011 | 0 | 28
38960.3906 | 1977 | 0 | 28
38960.3911 | 2106 | 0 | 28
38960.3916 | 1979 | 0 | 28
38960.3921 | 1916 | 0 | 28
38960.3925 | 2225 | 0 | 28
28
38960.3532 | 1 | 0 | 29
38960.3537 | 1 | 0 | 29
38960.3542 | 1 | 0 | 29
38960.3547 | 1 | 0 | 29
38960.3551 | 1 | 0 | 29
38960.3556 | 1 | 0 | 29
38960.3561 | 2 | 0 | 29
38960.3566 | 1 | 0 | 29
38960.3571 | 1 | 0 | 29
38960.3576 | 1 | 0 | 29
38960.3581 | 1 | 0 | 29
38960.3585 | 1 | 0 | 29
38960.359 | 1 | 0 | 29
38960.3595 | 1 | 0 | 29
38960.36 | 1 | 0 | 29
38960.3605 | 1 | 0 | 29
38960.361 | 1 | 0 | 29
38960.3615 | 1 | 0 | 29
38960.3619 | 1 | 0 | 29
38960.3624 | 1 | 0 | 29
38960.3629 | 1 | 0 | 29
38960.3634 | 1 | 0 | 29
38960.3639 | 1 | 0 | 29
38960.3644 | 1 | 0 | 29
38960.3649 | 1 | 0 | 29
38960.3653 | 1 | 0 | 29
38960.3658 | 1 | 0 | 29
38960.3663 | 1 | 0 | 29
38960.3668 | 1 | 0 | 29
38960.3673 | 1 | 0 | 29
38960.3678 | 1 | 0 | 29
38960.3683 | 1 | 0 | 29
38960.3688 | 1 | 0 | 29
38960.3692 | 1 | 1 | 29
38960.3697 | 1 | 0 | 29
38960.3702 | 1 | 0 | 29
38960.3707 | 1 | 0 | 29
38960.3717 | 1 | 0 | 29
38960.3722 | 1 | 0 | 29
38960.3726 | 1 | 0 | 29
38960.3731 | 1 | 0 | 29
38960.3736 | 1 | 0 | 29
38960.3741 | 1 | 0 | 29
38960.3746 | 1 | 0 | 29
38960.3751 | 1 | 0 | 29
38960.3756 | 1 | 0 | 29
38960.376 | 1 | 0 | 29
38960.3765 | 216 | 0 | 29
38960.377 | 39 | 0 | 29
38960.3775 | 1104 | 0 | 29
38960.378 | 2047 | 0 | 29
38960.3785 | 2034 | 0 | 29
38960.3789 | 2132 | 0 | 29
38960.3794 | 2243 | 0 | 29
38960.3799 | 1804 | 0 | 29
38960.3804 | 2292 | 0 | 29
38960.3809 | 2065 | 0 | 29
38960.3814 | 2200 | 0 | 29
38960.3819 | 2264 | 0 | 29
38960.3823 | 2093 | 0 | 29
38960.3828 | 2308 | 0 | 29
38960.3833 | 2332 | 0 | 29
38960.3838 | 2041 | 0 | 29
38960.3843 | 1930 | 0 | 29
38960.3848 | 2341 | 0 | 29
38960.3853 | 2262 | 0 | 29
38960.3858 | 1848 | 0 | 29
38960.3862 | 2181 | 0 | 29
38960.3867 | 2276 | 0 | 29
38960.3872 | 1928 | 0 | 29
38960.3877 | 2158 | 0 | 29
38960.3882 | 1839 | 0 | 29
38960.3887 | 1851 | 0 | 29
38960.3892 | 2119 | 0 | 29
38960.3896 | 2361 | 0 | 29
38960.3901 | 1926 | 0 | 29
38960.3906 | 2385 | 0 | 29
38960.3911 | 2366 | 0 | 29
38960.3916 | 2222 | 0 | 29
38960.3921 | 2202 | 0 | 29
38960.3926 | 2293 | 0 | 29
29
38960.3532 | 1 | 0 | 30
38960.3537 | 1 | 0 | 30
38960.3542 | 2 | 0 | 30
38960.3547 | 1 | 0 | 30
38960.3552 | 1 | 0 | 30
38960.3556 | 1 | 0 | 30
38960.3561 | 1 | 0 | 30
38960.3566 | 1 | 0 | 30
38960.3571 | 1 | 0 | 30
38960.3576 | 1 | 0 | 30
38960.3581 | 1 | 0 | 30
38960.3586 | 1 | 0 | 30
38960.359 | 1 | 0 | 30
38960.3595 | 1 | 0 | 30
38960.36 | 1 | 0 | 30
38960.3605 | 1 | 0 | 30
38960.361 | 1 | 0 | 30
38960.3615 | 1 | 0 | 30
38960.362 | 1 | 0 | 30
38960.3624 | 1 | 0 | 30
38960.3629 | 1 | 0 | 30
38960.3634 | 1 | 0 | 30
38960.3639 | 1 | 0 | 30
38960.3644 | 1 | 0 | 30
38960.3649 | 1 | 0 | 30
38960.3654 | 1 | 0 | 30
38960.3658 | 1 | 0 | 30
38960.3663 | 1 | 0 | 30
38960.3668 | 1 | 0 | 30
38960.3673 | 1 | 0 | 30
38960.3678 | 1 | 0 | 30
38960.3683 | 1 | 0 | 30
38960.3688 | 1 | 0 | 30
38960.3692 | 1 | 0 | 30
38960.3697 | 1 | 0 | 30
38960.3702 | 1 | 0 | 30
38960.3707 | 1 | 1 | 30
38960.3712 | 1 | 0 | 30
38960.3717 | 1 | 0 | 30
38960.3722 | 1 | 0 | 30
38960.3727 | 1 | 0 | 30
38960.3731 | 1 | 0 | 30
38960.3736 | 1 | 0 | 30
38960.3741 | 1 | 0 | 30
38960.3746 | 1 | 0 | 30
38960.3751 | 1 | 0 | 30
38960.3756 | 1 | 0 | 30
38960.3761 | 1 | 0 | 30
38960.3765 | 1 | 0 | 30
38960.377 | 1 | 0 | 30
38960.3775 | 2 | 0 | 30
38960.378 | 2 | 0 | 30
38960.3785 | 270 | 0 | 30
38960.379 | 1096 | 0 | 30
38960.3795 | 593 | 0 | 30
38960.3799 | 740 | 0 | 30
38960.3804 | 1096 | 0 | 30
38960.3809 | 1074 | 0 | 30
38960.3814 | 888 | 0 | 30
38960.3819 | 2043 | 0 | 30
38960.3824 | 1962 | 0 | 30
38960.3829 | 1841 | 0 | 30
38960.3833 | 2021 | 0 | 30
38960.3838 | 2224 | 0 | 30
38960.3843 | 1897 | 0 | 30
38960.3848 | 2143 | 0 | 30
38960.3853 | 2012 | 0 | 30
38960.3858 | 1826 | 0 | 30
38960.3863 | 1944 | 0 | 30
38960.3867 | 2176 | 0 | 30
38960.3872 | 2068 | 0 | 30
38960.3877 | 2276 | 0 | 30
38960.3882 | 2132 | 0 | 30
38960.3887 | 2140 | 0 | 30
38960.3892 | 1972 | 0 | 30
38960.3897 | 2085 | 0 | 30
38960.3902 | 2067 | 0 | 30
38960.3906 | 1850 | 0 | 30
38960.3911 | 2239 | 0 | 30
38960.3916 | 2204 | 0 | 30
38960.3921 | 2043 | 0 | 30
38960.3926 | 1999 | 0 | 30
30

## Test Facts
Last row in IRMS data sheets: | 87
Time when Penlight power was initiated: | 139