## Test Facts
Last row in IRMS data sheets: | 44
Time when Penlight power was initiated: | 121

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 27
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, CSPE ("Hypalon") jacketed, Rockbestos Firewall III, control cable (Cable Item #10). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: None. Cables were run horizontally through the Penlight chamber ("air drop" configuration) and secured to the raceway support brackets outside of the chamber; chamber end walls were closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 121 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
121 | 0 | Initated Penlight Heating
1477-1479 | 1356-1358 | Conductor 1 shorts to conductors 4 & 5 at less than 100 ohms (24 & 2)
1478 | 1357 | Conductor 1 shorts to ground (77) | Uncertain of the path to ground; unstable ground fault condition
1488-1496 | 1367-1375 | Conductor 2 shorts to conductors 3, 4, 5 & 6 (436, 16, 94 & 2)
1489 | 1368 | Conductor 2 shorts to ground (134) | Uncertain of the path to ground; unstable ground fault condition
1497-1505 | 1376-1384 | Conductors 3 & 5 both short to ground (352 & 75) | Uncertain of the paths to ground; unstable ground fault conditions
1505-1510 | 1384-1389 | Conductor 3 shorts to conductors 5, 6 & 7 (578, 7 & 5)
1508-1510 | 1387-1389 | Conductors 6 & 7 both short to ground (144 & 626) | Uncertain of the paths to ground; unstable ground fault conditions
1519 | 1398 | Conductors 4 & 7 short together at less than 1000 ohms (830)
1521-1524 | 1400-1403 | Conductor 5 shorts to conductors 6 & 7 at less than 100 ohms (22 & 26)
1527 | 1406 | Conductors 6 & 7 short together at less than 100 ohms (17)
1530-1544 | 1409-1423 | Conductor 1 shorts to conductors 2, 3, 6 & 7 at less than 100 ohms (18, 17, 23 & 2) | Conductor 1 is shorted to all other conductors
1547 | 1426 | The existing short between conductors 2 & 3 decreases to less than 100 ohms (33)
1558 | 1437 | Conductors 2 & 7 short together at less than 100 ohms (11) | Conductors 2 & 7 are shorted to all other conductors
1561-1563 | 1440-1442 | Conductors 3 & 4 short together at less than 1000 ohms (456); the existing short between conductors 3 & 5 decreases to less than 100 ohms (38) | Conductor 3 is shorted to all other conductors
1572 | 1451 | Conductors 4 & 5 short together at less than 1000 ohms (795) | Conductor 5 is shorted to all other conductors
1575 | 1454 | Cables ignite and burn
1593 | 1472 | Power to Penlight is shutoff
1619 | 1498 | The existing short between conductors 3 & 4 decreases to less than 100 ohms (13)
1620 | 1499 | Conductor 4 shorts to ground (74) | Uncertain of the path to ground; unstable ground fault condition
1631-1636 | 1510-1515 | Conductors 4 & 6 short together at less than 100 ohms (17); the existing shorts between conductor 4 and conductors 5 & 7 decrease to less than 100 ohms (3 & 27) | Conductors 4 & 6 are shorted to all other conductors
Additional Observations
Observation 1 | It took 1356 seconds (22.6 min.) from the start of Penlight heating for the first shorting failure to occur, and it took 1454 seconds (24.2 min.) for the cables to ignite.
Observation 2 | Although short to ground failures are indicated, it is uncertain what the paths to ground could have been.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 27 |  |  | 2006-08-01 | 9:51
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-120 | 211201.9994 | -117.5 | 211201.9994 | -114.5 | 211201.9994 | -111.5 | 211201.9994 | -108.5 | 211201.9994 | -106 | 211201.9994 | -103 | 211201.9994 | -100.5 | 211201.9994 | -97.5 | 211201.9994 | -95 | 211201.9994 | -92 | 211201.9994 | -89.5 | 211201.9994 | -86.5 | 211201.9994 | -83.5 | 211201.9994 | -81 | 211201.9994 | -78 | 211201.9994 | -75.5 | 211201.9994 | -72.5 | 211201.9994 | -69.5 | 211201.9994 | -66.5 | 211201.9994 | -64 | 211201.9994 | -120 | 211201.9994
-61.5 | 211201.9994 | -58.5 | 211201.9994 | -55.5 | 211201.9994 | -53 | 211201.9994 | -50 | 211201.9994 | -47.5 | 211201.9994 | -44.5 | 211201.9994 | -41.5 | 211201.9994 | -39 | 211201.9994 | -36 | 211201.9994 | -33.5 | 211201.9994 | -30.5 | 211201.9994 | -27.5 | 211201.9994 | -25 | 211201.9994 | -22 | 211201.9994 | -19.5 | 211201.9994 | -16.5 | 211201.9994 | -13.5 | 211201.9994 | -11 | 211201.9994 | -8 | 211201.9994 | -5.5 | 211201.9994 | -61.5 | 211201.9994
-3 | 211201.9994 | 0.5 | 211201.9994 | 3 | 211201.9994 | 6 | 211201.9994 | 8.5 | 211201.9994 | 11.5 | 211201.9994 | 14.5 | 211201.9994 | 17 | 211201.9994 | 20 | 211201.9994 | 22.5 | 211201.9994 | 25.5 | 211002.0947 | 28.5 | 211201.9994 | 31 | 211201.9994 | 34 | 211201.9994 | 36.5 | 211201.9994 | 39.5 | 211201.9994 | 42.5 | 211201.9994 | 45 | 211201.9994 | 48 | 211201.9994 | 50.5 | 211201.9994 | 53.5 | 211201.9994 | -3 | 211002.0947
56.5 | 211201.9994 | 59.5 | 211201.9994 | 62 | 211201.9994 | 64.5 | 211201.9994 | 67.5 | 211201.9994 | 70.5 | 211201.9994 | 73 | 211201.9994 | 76 | 211201.9994 | 78.5 | 211201.9994 | 81.5 | 211201.9994 | 84.5 | 211201.9994 | 87 | 211201.9994 | 90 | 211201.9994 | 92.5 | 211201.9994 | 95.5 | 211201.9994 | 98.5 | 211201.9994 | 101 | 211201.9994 | 104 | 211201.9994 | 106.5 | 211201.9994 | 109.5 | 211201.9994 | 112.5 | 211201.9994 | 56.5 | 211201.9994
115 | 211201.9994 | 118 | 211201.9994 | 120.5 | 211201.9994 | 123.5 | 211201.9994 | 126.5 | 211201.9994 | 129 | 211201.9994 | 132 | 211201.9994 | 134.5 | 211201.9994 | 137.5 | 211201.9994 | 140.5 | 211201.9994 | 143 | 211201.9994 | 146 | 211201.9994 | 148.5 | 211201.9994 | 151.5 | 211201.9994 | 154.5 | 211201.9994 | 157 | 211201.9994 | 160 | 211201.9994 | 162.5 | 211201.9994 | 165.5 | 211201.9994 | 168.5 | 211201.9994 | 171 | 211201.9994 | 115 | 211201.9994
174 | 211201.9994 | 176.5 | 211201.9994 | 179.5 | 211201.9994 | 182.5 | 211201.9994 | 185 | 211201.9994 | 188 | 211201.9994 | 190.5 | 211201.9994 | 193.5 | 211201.9994 | 196.5 | 211201.9994 | 199 | 211201.9994 | 202 | 211201.9994 | 204.5 | 211201.9994 | 207.5 | 211201.9994 | 210.5 | 211201.9994 | 213 | 211201.9994 | 216 | 211201.9994 | 218.5 | 211201.9994 | 221.5 | 211201.9994 | 224.5 | 211201.9994 | 227 | 211201.9994 | 230 | 211201.9994 | 174 | 211201.9994
232.5 | 211201.9994 | 235.5 | 211201.9994 | 238.5 | 211201.9994 | 241 | 211201.9994 | 244 | 211201.9994 | 246.5 | 211201.9994 | 249.5 | 211201.9994 | 252.5 | 211201.9994 | 255 | 211201.9994 | 258 | 211201.9994 | 260.5 | 211201.9994 | 263.5 | 211201.9994 | 266.5 | 211201.9994 | 269 | 211201.9994 | 272 | 211201.9994 | 274.5 | 211201.9994 | 277.5 | 211201.9994 | 280.5 | 211201.9994 | 283 | 211201.9994 | 286 | 105550.9988 | 288.5 | 211201.9994 | 232.5 | 105550.9988
291.5 | 211201.9994 | 294.5 | 211201.9994 | 297 | 211201.9994 | 300 | 211201.9994 | 302.5 | 211201.9994 | 305.5 | 211201.9994 | 308.5 | 211201.9994 | 311 | 211201.9994 | 314 | 211201.9994 | 316.5 | 211201.9994 | 319.5 | 211201.9994 | 322.5 | 211201.9994 | 325 | 211201.9994 | 328 | 211201.9994 | 330.5 | 211201.9994 | 333.5 | 211201.9994 | 336.5 | 211201.9994 | 339 | 211201.9994 | 342 | 211201.9994 | 344.5 | 211201.9994 | 347.5 | 211201.9994 | 291.5 | 211201.9994
350.5 | 211201.9994 | 353 | 211201.9994 | 356 | 211201.9994 | 358.5 | 211201.9994 | 361.5 | 211201.9994 | 364.5 | 211201.9994 | 367 | 211201.9994 | 370 | 211201.9994 | 372.5 | 211201.9994 | 375.5 | 211201.9994 | 378.5 | 211201.9994 | 381 | 211201.9994 | 384 | 211201.9994 | 386.5 | 211201.9994 | 389.5 | 211201.9994 | 392.5 | 211201.9994 | 395 | 211201.9994 | 398 | 211201.9994 | 400.5 | 211201.9994 | 403.5 | 211201.9994 | 406.5 | 211201.9994 | 350.5 | 211201.9994
409 | 211201.9994 | 412 | 211201.9994 | 414.5 | 211201.9994 | 417.5 | 211201.9994 | 420.5 | 211201.9994 | 423 | 211201.9994 | 426 | 211201.9994 | 428.5 | 211201.9994 | 431.5 | 211201.9994 | 434.5 | 211201.9994 | 437 | 211201.9994 | 440 | 211201.9994 | 442.5 | 211201.9994 | 445.5 | 211201.9994 | 448.5 | 211201.9994 | 451 | 211201.9994 | 454 | 211201.9994 | 456.5 | 211201.9994 | 459.5 | 211201.9994 | 462.5 | 211201.9994 | 465 | 211201.9994 | 409 | 211201.9994
468 | 211201.9994 | 470.5 | 211201.9994 | 473.5 | 211201.9994 | 476.5 | 211201.9994 | 480 | 211201.9994 | 482 | 211201.9994 | 484.5 | 211201.9994 | 487.5 | 211201.9994 | 490.5 | 211201.9994 | 493 | 211201.9994 | 496 | 211201.9994 | 498.5 | 211201.9994 | 501.5 | 211201.9994 | 504.5 | 211201.9994 | 507 | 211201.9994 | 510 | 211201.9994 | 512.5 | 211201.9994 | 515.5 | 211201.9994 | 518.5 | 211201.9994 | 521 | 211201.9994 | 524 | 211201.9994 | 468 | 211201.9994
526.5 | 211201.9994 | 529.5 | 211201.9994 | 532.5 | 211201.9994 | 535 | 211201.9994 | 538 | 211201.9994 | 540.5 | 211201.9994 | 543.5 | 211201.9994 | 546.5 | 211201.9994 | 549 | 211201.9994 | 552 | 211201.9994 | 554.5 | 211201.9994 | 557.5 | 211201.9994 | 560.5 | 211201.9994 | 563 | 211201.9994 | 566 | 211201.9994 | 568.5 | 211201.9994 | 571.5 | 211201.9994 | 574.5 | 211201.9994 | 577 | 211201.9994 | 580 | 211201.9994 | 582.5 | 211201.9994 | 526.5 | 211201.9994
585.5 | 211201.9994 | 588.5 | 211201.9994 | 591 | 211201.9994 | 594 | 211201.9994 | 596.5 | 211201.9994 | 599.5 | 211201.9994 | 602.5 | 211201.9994 | 605 | 211201.9994 | 608 | 211201.9994 | 610.5 | 211201.9994 | 613.5 | 211201.9994 | 616.5 | 211201.9994 | 619 | 211201.9994 | 622 | 211201.9994 | 624.5 | 211201.9994 | 627.5 | 211201.9994 | 630.5 | 211201.9994 | 633 | 211201.9994 | 636 | 211201.9994 | 638.5 | 211201.9994 | 641.5 | 211201.9994 | 585.5 | 211201.9994
644.5 | 211201.9994 | 647 | 211002.0947 | 650 | 211201.9994 | 652.5 | 211201.9994 | 655.5 | 211201.9994 | 658.5 | 211201.9994 | 661 | 211201.9994 | 664 | 211201.9994 | 666.5 | 211201.9994 | 669.5 | 211201.9994 | 672.5 | 211201.9994 | 675 | 211201.9994 | 678 | 211201.9994 | 680.5 | 211201.9994 | 683.5 | 211201.9994 | 686.5 | 211201.9994 | 689 | 211201.9994 | 692 | 211201.9994 | 694.5 | 211201.9994 | 697.5 | 105550.9988 | 700.5 | 211201.9994 | 644.5 | 105550.9988
703 | 211201.9994 | 706 | 211201.9994 | 708.5 | 211201.9994 | 711.5 | 211201.9994 | 714.5 | 211201.9994 | 717 | 211201.9994 | 720 | 211201.9994 | 722.5 | 211201.9994 | 725.5 | 211201.9994 | 728.5 | 211201.9994 | 731 | 211201.9994 | 734 | 211201.9994 | 736.5 | 211002.0947 | 739.5 | 211201.9994 | 742.5 | 211201.9994 | 745 | 211201.9994 | 747.5 | 211201.9994 | 750.5 | 211201.9994 | 753.5 | 211201.9994 | 756.5 | 211201.9994 | 759 | 211201.9994 | 703 | 211002.0947
761.5 | 211201.9994 | 764.5 | 211201.9994 | 767.5 | 211201.9994 | 770.5 | 211201.9994 | 773 | 211201.9994 | 775.5 | 211201.9994 | 778.5 | 211201.9994 | 781.5 | 211201.9994 | 784.5 | 211201.9994 | 787 | 211201.9994 | 790 | 211201.9994 | 792.5 | 211201.9994 | 795.5 | 211201.9994 | 798 | 211201.9994 | 801 | 211201.9994 | 804 | 211201.9994 | 806.5 | 211201.9994 | 809.5 | 211201.9994 | 812.5 | 211201.9994 | 815 | 211201.9994 | 817.5 | 211201.9994 | 761.5 | 211201.9994
820.5 | 211201.9994 | 823.5 | 211201.9994 | 826 | 211201.9994 | 829 | 211201.9994 | 831.5 | 211201.9994 | 834.5 | 211201.9994 | 837.5 | 211201.9994 | 840.5 | 211201.9994 | 843 | 211201.9994 | 846 | 211201.9994 | 848.5 | 211201.9994 | 851.5 | 211201.9994 | 854.5 | 211201.9994 | 858 | 211201.9994 | 860 | 211201.9994 | 862.5 | 211201.9994 | 865.5 | 211201.9994 | 868.5 | 211201.9994 | 871 | 211201.9994 | 874 | 211201.9994 | 876.5 | 211201.9994 | 820.5 | 211201.9994
879.5 | 211201.9994 | 882.5 | 211201.9994 | 885 | 211201.9994 | 888 | 211201.9994 | 890.5 | 211201.9994 | 893.5 | 211201.9994 | 896.5 | 211201.9994 | 899 | 211201.9994 | 902 | 211201.9994 | 904.5 | 211201.9994 | 907.5 | 211201.9994 | 910.5 | 211201.9994 | 913 | 211201.9994 | 915.5 | 211201.9994 | 918.5 | 211201.9994 | 921.5 | 211201.9994 | 924 | 211201.9994 | 927 | 211201.9994 | 929.5 | 211201.9994 | 932.5 | 211201.9994 | 935.5 | 211201.9994 | 879.5 | 211201.9994
938.5 | 211201.9994 | 941 | 211201.9994 | 943.5 | 211201.9994 | 946.5 | 211201.9994 | 949.5 | 211201.9994 | 952.5 | 211201.9994 | 955 | 211201.9994 | 958 | 211201.9994 | 960.5 | 211201.9994 | 963.5 | 211201.9994 | 966.5 | 211201.9994 | 969 | 211201.9994 | 972 | 211201.9994 | 974.5 | 211201.9994 | 977.5 | 211201.9994 | 980 | 211201.9994 | 983 | 211201.9994 | 986 | 105550.9988 | 988.5 | 211201.9994 | 991.5 | 211201.9994 | 994.5 | 211201.9994 | 938.5 | 105550.9988
997 | 211201.9994 | 1000 | 211201.9994 | 1002.5 | 211201.9994 | 1005.5 | 211201.9994 | 1008.5 | 211201.9994 | 1011 | 211201.9994 | 1014 | 211201.9994 | 1016.5 | 211201.9994 | 1019.5 | 105550.9988 | 1022.5 | 211201.9994 | 1025 | 211201.9994 | 1027.5 | 211201.9994 | 1030.5 | 211201.9994 | 1033.5 | 211201.9994 | 1036 | 211201.9994 | 1039 | 211002.0947 | 1041.5 | 211201.9994 | 1044.5 | 211201.9994 | 1047.5 | 211201.9994 | 1050.5 | 211201.9994 | 1053 | 211201.9994 | 997 | 105550.9988
1055.5 | 211201.9994 | 1058.5 | 211201.9994 | 1061.5 | 211201.9994 | 1064 | 211201.9994 | 1067 | 211201.9994 | 1069.5 | 211201.9994 | 1072.5 | 211201.9994 | 1075.5 | 211201.9994 | 1078.5 | 211002.0947 | 1081 | 211201.9994 | 1084 | 211201.9994 | 1086.5 | 211201.9994 | 1089.5 | 211201.9994 | 1092.5 | 211201.9994 | 1095 | 211201.9994 | 1098 | 211201.9994 | 1100.5 | 211201.9994 | 1103.5 | 211201.9994 | 1106 | 211201.9994 | 1109 | 211201.9994 | 1111.5 | 211201.9994 | 1055.5 | 211002.0947
1114.5 | 211201.9994 | 1117.5 | 211201.9994 | 1120 | 211201.9994 | 1123 | 211201.9994 | 1125.5 | 211201.9994 | 1128.5 | 211201.9994 | 1131.5 | 211201.9994 | 1134.5 | 211201.9994 | 1137 | 211201.9994 | 1139.5 | 211201.9994 | 1142.5 | 211201.9994 | 1145.5 | 211201.9994 | 1148 | 211201.9994 | 1151 | 211201.9994 | 1153.5 | 211201.9994 | 1156.5 | 211201.9994 | 1159.5 | 211201.9994 | 1162 | 211201.9994 | 1165 | 211201.9994 | 1167.5 | 211201.9994 | 1170.5 | 211201.9994 | 1114.5 | 211201.9994
1173.5 | 211201.9994 | 1176 | 211201.9994 | 1179 | 211201.9994 | 1181.5 | 211201.9994 | 1184.5 | 211201.9994 | 1187.5 | 211201.9994 | 1190.5 | 211201.9994 | 1193 | 211201.9994 | 1196 | 211201.9994 | 1198.5 | 211201.9994 | 1201.5 | 211201.9994 | 1204 | 211201.9994 | 1207 | 211201.9994 | 1209.5 | 211201.9994 | 1212.5 | 211201.9994 | 1215.5 | 211201.9994 | 1218 | 211201.9994 | 1221 | 211201.9994 | 1223.5 | 211201.9994 | 1226.5 | 211201.9994 | 1229.5 | 211201.9994 | 1173.5 | 211201.9994
1232 | 211201.9994 | 1235 | 211201.9994 | 1237.5 | 211201.9994 | 1240.5 | 211201.9994 | 1243.5 | 211201.9994 | 1246 | 211201.9994 | 1249 | 211201.9994 | 1251.5 | 211201.9994 | 1254.5 | 211201.9994 | 1257.5 | 211201.9994 | 1260 | 211201.9994 | 1263 | 211201.9994 | 1265.5 | 211201.9994 | 1268.5 | 211201.9994 | 1271.5 | 211201.9994 | 1274 | 211201.9994 | 1277 | 211201.9994 | 1279.5 | 211201.9994 | 1282.5 | 211201.9994 | 1285.5 | 211201.9994 | 1288 | 211201.9994 | 1232 | 211201.9994
1291 | 211201.9994 | 1293.5 | 211201.9994 | 1296.5 | 211201.9994 | 1299.5 | 211201.9994 | 1302 | 211201.9994 | 1305 | 211201.9994 | 1307.5 | 211201.9994 | 1310.5 | 211201.9994 | 1313.5 | 211201.9994 | 1316 | 211201.9994 | 1319 | 211201.9994 | 1321.5 | 211201.9994 | 1324.5 | 211201.9994 | 1327.5 | 211201.9994 | 1330 | 211201.9994 | 1333 | 211201.9994 | 1335.5 | 211201.9994 | 1338.5 | 211201.9994 | 1341.5 | 211201.9994 | 1344 | 211201.9994 | 1347 | 211201.9994 | 1291 | 211201.9994
1349.5 | 211201.9994 | 1352.5 | 211201.9994 | 1355.5 | 24.4604 | 1358 | 1.6437 | 1361 | 6245.9266 | 1363.5 | 23289.8442 | 1366.5 | 436.4537 | 1369.5 | 16.0198 | 1372 | 94.4002 | 1375 | 2.2175 | 1378 | 2513.0187 | 1380.5 | 9868.0707 | 1383.5 | 577.6474 | 1386 | 7.444 | 1389 | 5.2566 | 1391.5 | 7928.8037 | 1394.5 | 1145.9669 | 1397.5 | 829.7883 | 1400 | 21.6005 | 1403 | 26.033 | 1405.5 | 17.3165 | 1349.5 | 1.6437
1408.5 | 18.0502 | 1411.5 | 17.0415 | 1414 | 1735.2179 | 1417 | 19.1556 | 1419.5 | 22.7247 | 1422.5 | 1.7162 | 1425.5 | 33.0491 | 1428.5 | 269.2234 | 1431 | 0.98517 | 1433.5 | 21.9884 | 1436.5 | 11.2885 | 1439.5 | 456.3298 | 1442 | 37.8562 | 1445 | 19.4902 | 1447.5 | 0.89826 | 1450.5 | 795.283 | 1453.5 | 4217.6292 | 1456 | 882.6354 | 1459 | 4.1472 | 1461.5 | 22.9961 | 1464.5 | 19.5256 | 1408.5 | 0.89826
1467.5 | 6.3903 | 1470 | 7.1168 | 1473 | 12.8065 | 1475.5 | 1.0432 | 1478.5 | 2.5801 | 1481.5 | 20.4765 | 1484 | 4.2289 | 1487 | 13.6263 | 1489.5 | 22.5254 | 1492.5 | 12.8936 | 1495.5 | 14.6519 | 1498 | 13.4462 | 1501 | 5.2971 | 1503.5 | 8.8919 | 1506.5 | 3.483 | 1509.5 | 2.8099 | 1512 | 16.7479 | 1515 | 26.5658 | 1517.5 | 7.4335 | 1520.5 | 10.0876 | 1523.5 | 5.9491 | 1467.5 | 1.0432
1526 | 12.5608 | 1529 | 9.8663 | 1531.5 | 1.9524 | 1534.5 | 16.2853 | 1537.5 | 0.18746 | 1540 | 6.8068 | 1543 | 14.8533 | 1545.5 | 17.6868 | 1548.5 | 12.194 | 1551.5 | 34.7599 | 1554 | 35.151 | 1557 | 37.9143 | 1559.5 | 40.6214 | 1562.5 | 6.2971 | 1565.5 | 35.0473 | 1568 | 42.3217 | 1571 | 1.5685 | 1573.5 | 25.5991 | 1576.5 | 17.6733 | 1579.5 | 41.3009 | 1582 | 15.2287 | 1526 | 0.18746
1585 | 0.23628 | 1587.5 | 2.3547 | 1590.5 | 1.7428 | 1593.5 | 20.9375 | 1596 | 7.9124 | 1599 | 9.0066 | 1601.5 | 10.083 | 1604.5 | 1.6454 | 1607.5 | 4.2458 | 1610 | 14.329 | 1613 | 0.25866 | 1615.5 | 30.746 | 1618.5 | 15.9326 | 1621.5 | 20.1131 | 1624 | 17.2666 | 1627 | 15.7557 | 1629.5 | 1.1697 | 1632.5 | 9.1472 | 1635.5 | 14.2254 | 1638 | 25.6284 | 1641 | 16.6524 | 1585 | 0.23628
1643.5 | 7.8443 | 1646.5 | 14.868 | 1649.5 | 22.2232 | 1652 | 19.3595 | 1655 | 16.9836 | 1657.5 | 30.1205 | 1660.5 | 5.863 | 1663.5 | 3.7455 | 1666 | 2.3788 | 1669 | 0.95082 | 1671.5 | 28.1942 | 1674.5 | 19.0539 | 1677.5 | 11.4677 | 1680 | 14.7613 | 1683 | 28.7639 | 1685.5 | 36.8195 | 1688.5 | 13.0624 | 1691.5 | 11.0087 | 1694 | 12.606 | 1697 | 10.0914 | 1699.5 | 9.565 | 1643.5 | 0.95082
1702.5 | 15.5886 | 1705.5 | 17.4775 | 1708 | 33.4536 | 1711 | 3.8053 | 1713.5 | 26.2797 | 1716.5 | 14.7015 | 1719.5 | 23.797 | 1722 | 11.6305 | 1725 | 32.3061 | 1727.5 | 20.8571 | 1730.5 | 9.4927 | 1733.5 | 34.3486 | 1736 | 37.9794 | 1739 | 18.8312 | 1741.5 | 10.7177 | 1744.5 | 18.192 | 1747.5 | 8.1552 | 1750 | 17.2998 | 1753 | 10.1244 | 1755.5 | 0.93308 | 1758.5 | 6.8509 | 1702.5 | 0.93308
1761.5 | 2.0874 | 1764 | 6.8471 | 1767 | 20.2412 | 1769.5 | 18.884 | 1772.5 | 10.1471 | 1775.5 | 19.2386 | 1778 | 17.893 | 1781 | 16.1404 | 1783.5 | 15.7834 | 1786.5 | 26.7972 | 1789.5 | 17.0095 | 1792 | 10.6876 | 1795 | 14.7383 | 1797 | 19.5386 | 1800.5 | 44.1165 | 1803.5 | 25.7203 | 1806 | 31.9395 | 1809 | 1.432 | 1811.5 | 3.3812 | 1814.5 | 16.6596 | 1817.5 | 24.7522 | 1761.5 | 1.432
1820 | 9.7097 | 1823 | 8.854 | 1825.5 | 16.311 | 1828.5 | 21.8979 | 1831.5 | 27.0254 | 1834 | 10.2782 | 1837 | 2.0534 | 1839.5 | 10.3625 | 1842.5 | 12.2045 | 1845.5 | 6.0788 | 1848 | 11.2055 | 1851 | 16.8027 | 1853.5 | 15.0054 | 1856.5 | 10.3932 | 1859.5 | 13.5434 | 1862 | 2.5512 | 1865 | 24.5704 | 1867.5 | 5.6886 | 1870.5 | 26.5805 | 1873.5 | 20.0425 | 1876 | 0.13077 | 1820 | 0.13077
1879 | 17.048 | 1881.5 | 29.6145 | 1884.5 | 27.2893 | 1887.5 | 38.0986 | 1890 | 11.0337 | 1893 | 9.4726 | 1895.5 | 4.1603 | 1898.5 | 7.2647 | 1901.5 | 6.0913 | 1904 | 8.0888 | 1907 | 5.6594 | 1909.5 | 12.7014 | 1912.5 | 16.014 | 1915.5 | 7.9871 | 1918 | 15.4563 | 1921 | 14.2085 | 1923.5 | 3.5382 | 1926.5 | 3.5653 | 1929.5 | 5.706 | 1932 | 1.4457 | 1935 | 10.0898 | 1879 | 1.4457
1937.5 | 19.7121 | 1940.5 | 15.2378 | 1943.5 | 1.3687 | 1946 | 0.84563 | 1949 | 1.8475 | 1951.5 | 21.1515 | 1954.5 | 6.4025 | 1957.5 | 38.8524 | 1960 | 4.4831 | 1963 | 23.0535 | 1965.5 | 25.559 | 1968.5 | 20.482 | 1971.5 | 22.2496 | 1974 | 15.7367 | 1977 | 16.2257 | 1979.5 | 0.23557 | 1982.5 | 21.049 | 1985.5 | 10.2931 | 1988 | 17.4865 | 1991 | 19.0025 | 1993.5 | 9.6042 | 1937.5 | 0.23557
1996.5 | 1.2162 | 1999.5 | 1.139 | 2002 | 4.3314 | 2005 | 4.8338 | 2007.5 | 5.1448 | 2010.5 | 2.6771 | 2013.5 | 6.8824 | 2016 | 9.9653 | 2018.5 | 34.6971 | 2021.5 | 6.4391 | 2024.5 | 27.3044 | 2027.5 | 4.3799 | 2030 | 6.9371 | 2033 | 1.8765 | 2035.5 | 11.8365 | 2038.5 | 22.2517 | 2041.5 | 16.349 | 2044 | 15.6896 | 2046.5 | 1.0265 | 2049.5 | 26.5116 | 2052.5 | 34.9022 | 1996.5 | 1.0265
2055.5 | 38.8843 | 2058 | 21.9086 | 2061 | 9.9764 | 2063.5 | 25.3314 | 2066.5 | 4.2433 | 2069.5 | 20.2144 | 2072 | 2.4983 | 2074.5 | 8.7839 | 2077.5 | 32.2989 | 2080.5 | 5.0436 | 2083.5 | 2.6466 | 2086 | 29.855 | 2089 | 5.3129 | 2091.5 | 9.8567 | 2094.5 | 37.3322 | 2097.5 | 6.5305 | 2100 | 2.2206 | 2103 | 16.071 | 2105.5 | 6.3812 | 2108.5 | 1.1374 | 2111 | 0.95328 | 2055.5 | 0.95328
2114 | 6.0923 | 2117 | 1.7447 | 2119.5 | 2.1988 | 2122.5 | 10.4315 | 2125.5 | 25.6639 | 2128 | 8.5654 | 2131 | 9.4455 | 2133.5 | 2.3946 | 2136.5 | 39.0999 | 2139.5 | 11.5501 | 2142 | 34.6094 | 2145 | 8.0084 | 2147.5 | 36.0888 | 2150.5 | 23.2682 | 2153.5 | 28.2075 | 2156 | 3.898 | 2159 | 9.212 | 2161.5 | 4.0733 | 2164.5 | 14.4518 | 2167.5 | 0.63502 | 2170 | 8.8036 | 2114 | 0.63502

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 27 |  |  | 2006-08-01 | 9:51
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2
Penlight Penlight Penlight Time | C1-G |  | Penlight Penlight Penlight Time | C2-G | Penlight Penlight Penlight Time | C3-G | Penlight Penlight Penlight Time | C4-G | Penlight Penlight Penlight Time | C5-G | Penlight Penlight Penlight Time | C6-G | Penlight Penlight Penlight Time | C7-G | Penlight Penlight Penlight Time | Minimums Overall
-113 | 211202 |  | -101.3333 | 211202 | -93.5 | 211202 | -88.4167 | 211202 | -84.9167 | 211202 | -82.6667 | 211202 | -80.3333 | 211202 | -113 | 211202
-54.3333 | 211202 |  | -42.6667 | 211202 | -34.6667 | 211202 | -29.5 | 211202 | -26.3333 | 211202 | -24 | 211202 | -21.6667 | 211202 | -54.3333 | 211202
4.4167 | 211202 |  | 16.0833 | 211202 | 24.1667 | 211202 | 29.25 | 211202 | 32.5 | 211202 | 34.8333 | 211202 | 37.0833 | 211202 | 4.4167 | 211202
63.4167 | 211202 |  | 75 | 211202 | 82.9167 | 211202 | 88.0833 | 211202 | 91.25 | 211202 | 93.5833 | 211202 | 96.0833 | 211202 | 63.4167 | 211202
122.0833 | 211202 |  | 133.75 | 211202 | 141.75 | 211202 | 146.75 | 211202 | 150.0833 | 211202 | 152.5 | 211202 | 154.75 | 211202 | 122.0833 | 211202
180.9167 | 211202 |  | 192.5833 | 211202 | 200.4167 | 211202 | 205.5833 | 211202 | 209 | 211202 | 211.25 | 211202 | 213.5833 | 211202 | 180.9167 | 211202
239.6667 | 211202 |  | 251.3333 | 211202 | 259.3333 | 211202 | 264.5 | 211202 | 267.6667 | 105551 | 270 | 211202 | 272.3333 | 211202 | 239.6667 | 105551
298.5 | 211202 |  | 310.1667 | 211202 | 318.1667 | 211202 | 323.25 | 211202 | 326.5 | 211202 | 328.8333 | 211202 | 331.0833 | 211202 | 298.5 | 211202
357.3333 | 211202 |  | 369 | 211202 | 376.8333 | 211202 | 382.0833 | 211202 | 385.25 | 211202 | 387.5833 | 211202 | 390.0833 | 211202 | 357.3333 | 211202
416.0833 | 211202 |  | 427.75 | 211202 | 435.75 | 211202 | 440.75 | 211202 | 444.0833 | 211202 | 446.5 | 211202 | 448.75 | 105551 | 416.0833 | 105551
475.0833 | 211202 |  | 486.5833 | 211202 | 494.4167 | 211202 | 499.5833 | 211202 | 503 | 211202 | 505.4167 | 105551 | 507.5833 | 211202 | 475.0833 | 105551
533.6667 | 211202 |  | 545.3333 | 211202 | 553.3333 | 211202 | 558.5 | 211202 | 561.6667 | 211202 | 564 | 211202 | 566.3333 | 211202 | 533.6667 | 211202
592.5 | 211202 |  | 604.1667 | 211202 | 612.1667 | 211202 | 617.25 | 105551 | 620.5 | 211202 | 622.8333 | 211202 | 625.0833 | 211202 | 592.5 | 105551
651.3333 | 211202 |  | 663 | 211202 | 670.8333 | 211202 | 676.0833 | 211202 | 679.25 | 105551 | 681.5833 | 211202 | 684.0833 | 211202 | 651.3333 | 105551
710.0833 | 211202 |  | 721.75 | 211202 | 729.75 | 211202 | 734.6667 | 211202 | 738.0833 | 211202 | 740.4167 | 211202 | 742.75 | 211202 | 710.0833 | 211202
768.75 | 211202 |  | 780.5 | 211202 | 788.3333 | 211202 | 793.5833 | 211202 | 797 | 211202 | 799.0833 | 211202 | 801.4167 | 211202 | 768.75 | 211202
827.5 | 211202 |  | 839.3333 | 211202 | 847.5 | 211202 | 852.4167 | 211202 | 855.6667 | 211202 | 858.0833 | 211202 | 860.3333 | 211202 | 827.5 | 211202
886.5 | 211202 |  | 898.1667 | 211202 | 906.0833 | 211202 | 911.1667 | 211202 | 914.4167 | 211202 | 916.5833 | 211202 | 919.0833 | 211202 | 886.5 | 211202
945.25 | 211202 |  | 957 | 211202 | 964.8333 | 211202 | 969.9167 | 105551 | 973.1667 | 211202 | 975.5833 | 211202 | 978.0833 | 105551 | 945.25 | 105551
1004.0833 | 211202 |  | 1015.75 | 105551 | 1023.5833 | 211202 | 1028.5833 | 211202 | 1032.0833 | 211202 | 1034.4167 | 211202 | 1036.6667 | 211202 | 1004.0833 | 105551
1062.6667 | 211202 |  | 1074.5 | 211202 | 1082.4167 | 211202 | 1087.5833 | 211202 | 1090.8333 | 211202 | 1093.0833 | 211202 | 1095.4167 | 211202 | 1062.6667 | 211202
1121.5 | 211202 |  | 1133.25 | 211202 | 1141.1667 | 211202 | 1146.3333 | 105551 | 1149.5 | 211202 | 1151.8333 | 211202 | 1154.0833 | 211202 | 1121.5 | 105551
1180.3333 | 211202 |  | 1192.1667 | 211202 | 1199.9167 | 211202 | 1205.0833 | 211202 | 1208.3333 | 105551 | 1210.5833 | 211202 | 1213.0833 | 211202 | 1180.3333 | 105551
1239.0833 | 211202 |  | 1250.75 | 211202 | 1258.75 | 211202 | 1263.75 | 105551 | 1267.0833 | 211202 | 1269.5 | 211202 | 1271.75 | 211202 | 1239.0833 | 105551
1297.9167 | 211202 |  | 1309.5833 | 211202 | 1317.4167 | 211202 | 1322.5833 | 211202 | 1326 | 211202 | 1328.25 | 211202 | 1330.5833 | 211202 | 1297.9167 | 211202
1356.6667 | 76.5441 |  | 1368.4167 | 134.0392 | 1376.3333 | 352.1761 | 1381.5 | 4235.4063 | 1384.6667 | 75.4704 | 1387 | 143.984 | 1389.4167 | 625.8491 | 1356.6667 | 75.4704
1415.5 | 522.2633 |  | 1427.25 | 108.0052 | 1435.1667 | 157.8673 | 1440.3333 | 2717.3266 | 1443.5 | 324.2315 | 1445.8333 | 442.2074 | 1448.0833 | 137.507 | 1415.5 | 108.0052
1474.3333 | 35.1668 |  | 1486 | 148.3428 | 1493.8333 | 65.3888 | 1499.0833 | 73.7231 | 1502.25 | 82.9243 | 1504.5833 | 41.6712 | 1507.0833 | 64.2349 | 1474.3333 | 35.1668
1533.0833 | 128.0096 |  | 1544.75 | 131.3506 | 1552.75 | 875.7488 | 1557.75 | 10.9834 | 1561.0833 | 103.7509 | 1563.5 | 12.8165 | 1565.75 | 230.9466 | 1533.0833 | 10.9834
1591.9167 | 15.9105 |  | 1603.5833 | 1.9567 | 1611.4167 | 55.4422 | 1616.5833 | 18.1143 | 1620 | 26.4046 | 1622.25 | 129.88 | 1624.5833 | 2.2225 | 1591.9167 | 1.9567
1650.6667 | 188.0707 |  | 1662.3333 | 5.5656 | 1670.3333 | 81.8004 | 1675.5 | 193.2208 | 1678.6667 | 18.3506 | 1681 | 6.5946 | 1683.3333 | 47.7541 | 1650.6667 | 5.5656
1709.5 | 191.1474 |  | 1721.1667 | 126.5639 | 1729.1667 | 86.8891 | 1734.25 | 66.5155 | 1737.5 | 388.1965 | 1739.8333 | 83.4792 | 1742.0833 | 112.1488 | 1709.5 | 66.5155
1768.3333 | 98.7428 |  | 1780 | 559.799 | 1787.75 | 91.9992 | 1793.0833 | 117.826 | 1796.25 | 56.6127 | 1798.5 | 63.1822 | 1801.0833 | 123.5898 | 1768.3333 | 56.6127
1827.0833 | 86.0721 |  | 1838.75 | 67.79 | 1846.75 | 70.4998 | 1851.75 | 87.8052 | 1855.0833 | 210.6346 | 1857.5 | 0.84879 | 1859.75 | 0.9812 | 1827.0833 | 0.84879
1885.9167 | 156.3352 |  | 1897.5833 | 84.4823 | 1905.4167 | 46.6419 | 1910.5833 | 109.7424 | 1914 | 78.6509 | 1916.25 | 59.8629 | 1918.5833 | 108.6674 | 1885.9167 | 46.6419
1944.6667 | 38.7691 |  | 1956.3333 | 63.9063 | 1964.3333 | 70.8222 | 1969.5 | 185.4339 | 1972.6667 | 91.8533 | 1975 | 36.3598 | 1977.3333 | 394.5978 | 1944.6667 | 36.3598
2003.5 | 288.968 |  | 2015.0833 | 94.3641 | 2023.1667 | 93.7752 | 2028.25 | 117.559 | 2031.3333 | 6.767 | 2033.75 | 7.8962 | 2036.0833 | 95.1097 | 2003.5 | 6.767
2062.3333 | 147.1648 |  | 2073.9167 | 338.5457 | 2081.8333 | 61.6944 | 2087 | 122.324 | 2090.25 | 56.1465 | 2092.5 | 5.5279 | 2095 | 4.597 | 2062.3333 | 4.597
2121.0833 | 42.9428 |  | 2132.75 | 107.036 | 2140.75 | 211.1891 | 2145.75 | 47.2474 | 2149.0833 | 119.7302 | 2151.5 | 88.4428 | 2153.75 | 153.1102 | 2121.0833 | 42.9428

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -121 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
1 | -120 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
2 | -119 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
3 | -118 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
4 | -117 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
5 | -116 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
6 | -115 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
7 | -114 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
8 | -113 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
9 | -112 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
10 | -111 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
11 | -110 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
12 | -109 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
13 | -108 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
14 | -107 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
15 | -106 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
16 | -105 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
17 | -104 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
18 | -103 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
19 | -102 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
20 | -101 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
21 | -100 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
22 | -99 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
23 | -98 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
24 | -97 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
25 | -96 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
26 | -95 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
27 | -94 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
28 | -93 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
29 | -92 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
30 | -91 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
31 | -90 | 19.4 | 26.5 | 22 | 26.3 | 29 | 23.9 | 24.1
32 | -89 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
33 | -88 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
34 | -87 | 19.4 | 26.4 | 22.1 | 26.2 | 29 | 23.9 | 24.1
35 | -86 | 19.4 | 26.4 | 22.1 | 26.2 | 28.9 | 23.9 | 24.1
36 | -85 | 19.4 | 26.4 | 22.1 | 26.2 | 28.9 | 23.9 | 24.1
37 | -84 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
38 | -83 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
39 | -82 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
40 | -81 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
41 | -80 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
42 | -79 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
43 | -78 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
44 | -77 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
45 | -76 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
46 | -75 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
47 | -74 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
48 | -73 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
49 | -72 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
50 | -71 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
51 | -70 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
52 | -69 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
53 | -68 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
54 | -67 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
55 | -66 | 19.4 | 26.4 | 22.2 | 26.2 | 28.9 | 23.9 | 24.1
56 | -65 | 19.4 | 26.4 | 22.1 | 26.2 | 29 | 23.9 | 24.1
57 | -64 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
58 | -63 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
59 | -62 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
60 | -61 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
61 | -60 | 19.4 | 26.5 | 22 | 26.3 | 29 | 23.9 | 24.1
62 | -59 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
63 | -58 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
64 | -57 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
65 | -56 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
66 | -55 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
67 | -54 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
68 | -53 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
69 | -52 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
70 | -51 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
71 | -50 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
72 | -49 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
73 | -48 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
74 | -47 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
75 | -46 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
76 | -45 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
77 | -44 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
78 | -43 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
79 | -42 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
80 | -41 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
81 | -40 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
82 | -39 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
83 | -38 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
84 | -37 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
85 | -36 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
86 | -35 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
87 | -34 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
88 | -33 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
89 | -32 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
90 | -31 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
91 | -30 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
92 | -29 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
93 | -28 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
94 | -27 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
95 | -26 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
96 | -25 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
97 | -24 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
98 | -23 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
99 | -22 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
100 | -21 | 19.4 | 26.5 | 22 | 26.3 | 29.2 | 23.9 | 24.1
101 | -20 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
102 | -19 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
103 | -18 | 19.4 | 26.5 | 22 | 26.3 | 29.1 | 23.9 | 24.1
104 | -17 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
105 | -16 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
106 | -15 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
107 | -14 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
108 | -13 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
109 | -12 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
110 | -11 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
111 | -10 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
112 | -9 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
113 | -8 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
114 | -7 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
115 | -6 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
116 | -5 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
117 | -4 | 19.4 | 26.5 | 22.1 | 26.3 | 29.1 | 23.9 | 24.1
118 | -3 | 19.4 | 26.5 | 22.1 | 26.3 | 29 | 23.9 | 24.1
119 | -2 | 19.4 | 26.4 | 22.2 | 26.2 | 28.7 | 24 | 24.1
120 | -1 | 19.4 | 26.4 | 22.1 | 26.3 | 28.9 | 24 | 24.1
121 | 0 | 19.6 | 26.5 | 21.9 | 26.3 | 29.2 | 24 | 24.1
122 | 1 | 20.4 | 26.5 | 21.9 | 26.3 | 29.2 | 24 | 24.1
123 | 2 | 22 | 26.6 | 21.9 | 26.3 | 29.2 | 24 | 24.1
124 | 3 | 24.3 | 26.5 | 21.9 | 26.3 | 29.2 | 24 | 24.1
125 | 4 | 27.1 | 26.5 | 22 | 26.3 | 29.2 | 24 | 24.2
126 | 5 | 30.4 | 26.6 | 21.9 | 26.3 | 29.2 | 24.1 | 24.2
127 | 6 | 34.1 | 26.6 | 21.9 | 26.3 | 29.2 | 24.1 | 24.2
128 | 7 | 38.1 | 26.6 | 21.9 | 26.3 | 29.3 | 24.2 | 24.3
129 | 8 | 42.4 | 26.6 | 21.9 | 26.3 | 29.3 | 24.2 | 24.4
130 | 9 | 46.8 | 26.6 | 21.9 | 26.3 | 29.3 | 24.3 | 24.4
131 | 10 | 51.3 | 26.6 | 21.9 | 26.3 | 29.4 | 24.4 | 24.5
132 | 11 | 56.1 | 26.7 | 21.9 | 26.3 | 29.4 | 24.5 | 24.6
133 | 12 | 61 | 26.7 | 21.9 | 26.3 | 29.4 | 24.6 | 24.7
134 | 13 | 66 | 26.7 | 21.9 | 26.4 | 29.5 | 24.7 | 24.8
135 | 14 | 71.1 | 26.8 | 21.9 | 26.3 | 29.5 | 24.8 | 25
136 | 15 | 76.3 | 26.8 | 21.9 | 26.4 | 29.6 | 25 | 25.1
137 | 16 | 81.6 | 26.9 | 21.9 | 26.4 | 29.7 | 25.1 | 25.3
138 | 17 | 87 | 26.9 | 21.9 | 26.4 | 29.8 | 25.3 | 25.4
139 | 18 | 92.5 | 27 | 21.9 | 26.4 | 29.9 | 25.5 | 25.7
140 | 19 | 97.9 | 27.1 | 21.9 | 26.4 | 30 | 25.7 | 25.9
141 | 20 | 103.5 | 27.2 | 21.9 | 26.4 | 30.1 | 25.9 | 26.1
142 | 21 | 109 | 27.3 | 21.9 | 26.4 | 30.2 | 26.1 | 26.3
143 | 22 | 114.6 | 27.4 | 21.9 | 26.4 | 30.4 | 26.3 | 26.6
144 | 23 | 120.2 | 27.5 | 22 | 26.4 | 30.5 | 26.6 | 26.9
145 | 24 | 125.9 | 27.7 | 22 | 26.5 | 30.7 | 26.9 | 27.1
146 | 25 | 131.6 | 27.8 | 22 | 26.5 | 30.9 | 27.2 | 27.4
147 | 26 | 137.3 | 28 | 22 | 26.5 | 31.1 | 27.5 | 27.8
148 | 27 | 143.1 | 28.1 | 22 | 26.5 | 31.3 | 27.9 | 28.1
149 | 28 | 148.8 | 28.3 | 22.1 | 26.6 | 31.5 | 28.2 | 28.5
150 | 29 | 154.5 | 28.5 | 22.1 | 26.6 | 31.8 | 28.6 | 28.9
151 | 30 | 160.2 | 28.7 | 22.1 | 26.7 | 32.1 | 29 | 29.3
152 | 31 | 165.9 | 29 | 22.2 | 26.7 | 32.3 | 29.4 | 29.7
153 | 32 | 171.7 | 29.2 | 22.3 | 26.7 | 32.6 | 29.8 | 30.2
154 | 33 | 177.5 | 29.5 | 22.3 | 26.8 | 32.9 | 30.3 | 30.7
155 | 34 | 183.2 | 29.7 | 22.4 | 26.8 | 33.3 | 30.8 | 31.2
156 | 35 | 189 | 30 | 22.4 | 26.9 | 33.6 | 31.3 | 31.7
157 | 36 | 194.8 | 30.3 | 22.5 | 27 | 34 | 31.8 | 32.2
158 | 37 | 200.5 | 30.7 | 22.5 | 27 | 34.4 | 32.4 | 32.8
159 | 38 | 206.1 | 31 | 22.6 | 27.1 | 34.8 | 33 | 33.4
160 | 39 | 211.8 | 31.4 | 22.7 | 27.2 | 35.2 | 33.5 | 34.1
161 | 40 | 217.5 | 31.7 | 22.8 | 27.3 | 35.7 | 34.1 | 34.7
162 | 41 | 223.2 | 32.1 | 22.9 | 27.4 | 36.2 | 34.8 | 35.3
163 | 42 | 229 | 32.6 | 23 | 27.5 | 36.7 | 35.4 | 36
164 | 43 | 234.7 | 33 | 23.1 | 27.6 | 37.2 | 36.2 | 36.8
165 | 44 | 240.3 | 33.5 | 23.1 | 27.7 | 37.8 | 36.9 | 37.5
166 | 45 | 246 | 33.9 | 23.3 | 27.8 | 38.3 | 37.6 | 38.2
167 | 46 | 251.6 | 34.5 | 23.4 | 28 | 39 | 38.3 | 39
168 | 47 | 257.2 | 35 | 23.5 | 28.1 | 39.6 | 39.1 | 39.8
169 | 48 | 262.7 | 35.5 | 23.7 | 28.3 | 40.2 | 39.9 | 40.6
170 | 49 | 268.4 | 36.1 | 23.8 | 28.4 | 40.9 | 40.8 | 41.5
171 | 50 | 274 | 36.7 | 24 | 28.6 | 41.6 | 41.6 | 42.4
172 | 51 | 279.6 | 37.4 | 24.1 | 28.8 | 42.4 | 42.5 | 43.3
173 | 52 | 285.1 | 38 | 24.3 | 29 | 43.1 | 43.4 | 44.2
174 | 53 | 290.5 | 38.7 | 24.5 | 29.2 | 43.9 | 44.3 | 45.3
175 | 54 | 295.9 | 39.4 | 24.6 | 29.4 | 44.7 | 45.3 | 46.3
176 | 55 | 301.3 | 40.1 | 24.8 | 29.6 | 45.5 | 46.3 | 47.3
177 | 56 | 306.8 | 40.8 | 25.1 | 29.8 | 46.3 | 47.4 | 48.4
178 | 57 | 312.2 | 41.6 | 25.3 | 30 | 47.2 | 48.5 | 49.4
179 | 58 | 317.7 | 42.3 | 25.5 | 30.3 | 48.1 | 49.7 | 50.5
180 | 59 | 322.9 | 43.2 | 25.7 | 30.5 | 49 | 50.8 | 51.7
181 | 60 | 328.2 | 44 | 26 | 30.8 | 50 | 51.9 | 52.8
182 | 61 | 333.5 | 44.9 | 26.2 | 31.1 | 51 | 53.1 | 54
183 | 62 | 338.8 | 45.8 | 26.4 | 31.4 | 52 | 54.3 | 55.3
184 | 63 | 344.1 | 46.7 | 26.7 | 31.7 | 53.1 | 55.6 | 56.6
185 | 64 | 349.3 | 47.6 | 27 | 32 | 54.2 | 56.9 | 57.8
186 | 65 | 354.5 | 48.6 | 27.3 | 32.3 | 55.3 | 58.2 | 59.2
187 | 66 | 359.7 | 49.6 | 27.6 | 32.7 | 56.4 | 59.5 | 60.6
188 | 67 | 364.9 | 50.6 | 27.9 | 33 | 57.5 | 60.8 | 62
189 | 68 | 370.2 | 51.6 | 28.3 | 33.4 | 58.7 | 62.2 | 63.5
190 | 69 | 375.4 | 52.7 | 28.6 | 33.8 | 59.9 | 63.6 | 64.9
191 | 70 | 380.4 | 53.8 | 29 | 34.2 | 61.2 | 65.1 | 66.4
192 | 71 | 385.3 | 54.9 | 29.4 | 34.6 | 62.4 | 66.7 | 68
193 | 72 | 390.5 | 56 | 29.7 | 35 | 63.8 | 68.3 | 69.5
194 | 73 | 395.5 | 57.2 | 30.1 | 35.4 | 65.1 | 69.8 | 71.1
195 | 74 | 400.5 | 58.5 | 30.6 | 35.9 | 66.6 | 71.5 | 72.7
196 | 75 | 405.4 | 59.8 | 31 | 36.3 | 68 | 73.1 | 74.4
197 | 76 | 410.4 | 61.1 | 31.4 | 36.8 | 69.5 | 74.8 | 76.1
198 | 77 | 415.5 | 62.5 | 31.9 | 37.3 | 71.1 | 76.5 | 77.8
199 | 78 | 420.4 | 63.9 | 32.3 | 37.8 | 72.7 | 78.3 | 79.6
200 | 79 | 425.3 | 65.3 | 32.8 | 38.3 | 74.3 | 80 | 81.5
201 | 80 | 430.1 | 66.8 | 33.3 | 38.8 | 75.9 | 81.8 | 83.3
202 | 81 | 434.9 | 68.2 | 33.9 | 39.3 | 77.3 | 83.7 | 85.3
203 | 82 | 439.6 | 69.8 | 34.4 | 39.9 | 79 | 85.6 | 87.2
204 | 83 | 443.8 | 71.3 | 34.9 | 40.5 | 80.7 | 87.5 | 89.2
205 | 84 | 447.4 | 72.9 | 35.5 | 41.1 | 82.5 | 89.4 | 91.1
206 | 85 | 450.8 | 74.6 | 36 | 41.7 | 84.2 | 91.4 | 93.1
207 | 86 | 454.1 | 76.2 | 36.6 | 42.3 | 86 | 93.3 | 95.1
208 | 87 | 457.1 | 77.9 | 37.2 | 43 | 87.8 | 95.3 | 97
209 | 88 | 459.9 | 79.6 | 37.9 | 43.6 | 89.6 | 97.1 | 98.9
210 | 89 | 462.4 | 81.3 | 38.4 | 44.3 | 91.5 | 99 | 100.8
211 | 90 | 464.9 | 83.1 | 39 | 45 | 93.3 | 101 | 102.7
212 | 91 | 467.4 | 84.8 | 39.7 | 45.7 | 95.2 | 102.9 | 104.7
213 | 92 | 469.8 | 86.6 | 40.5 | 46.4 | 96.9 | 104.8 | 106.7
214 | 93 | 471.8 | 88.3 | 41.3 | 47.1 | 98.6 | 106.8 | 108.7
215 | 94 | 473.4 | 90 | 42.1 | 47.8 | 100.3 | 108.6 | 110.6
216 | 95 | 474.8 | 91.7 | 43 | 48.5 | 101.9 | 110.4 | 112.5
217 | 96 | 476 | 93.4 | 43.9 | 49.2 | 103.4 | 112.2 | 114.4
218 | 97 | 477 | 95.2 | 44.7 | 49.9 | 105.2 | 114 | 116.3
219 | 98 | 477.7 | 97.1 | 45.4 | 50.7 | 107.1 | 115.8 | 118.1
220 | 99 | 478.3 | 98.8 | 46.2 | 51.5 | 108.8 | 117.5 | 119.8
221 | 100 | 478.5 | 100.6 | 47 | 52.3 | 110.6 | 119.1 | 121.6
222 | 101 | 478.3 | 102.4 | 47.8 | 53.2 | 112.3 | 120.8 | 123.3
223 | 102 | 478.1 | 104.2 | 48.6 | 54 | 114.1 | 122.5 | 125
224 | 103 | 477.9 | 106 | 49.4 | 54.8 | 115.8 | 124.1 | 126.7
225 | 104 | 477.5 | 107.8 | 50.2 | 55.7 | 117.5 | 125.6 | 128.3
226 | 105 | 477.1 | 109.5 | 51 | 56.5 | 119.2 | 127.1 | 129.9
227 | 106 | 477 | 111.2 | 51.8 | 57.4 | 120.8 | 128.6 | 131.4
228 | 107 | 476.7 | 112.9 | 52.7 | 58.3 | 122.5 | 130.1 | 133
229 | 108 | 476.1 | 114.6 | 53.5 | 59.1 | 124.2 | 131.4 | 134.5
230 | 109 | 475.5 | 116.2 | 54.3 | 60 | 125.8 | 132.8 | 135.9
231 | 110 | 474.7 | 117.9 | 55.2 | 60.9 | 127.4 | 134.1 | 137.3
232 | 111 | 474.1 | 119.5 | 56 | 61.8 | 129.1 | 135.5 | 138.8
233 | 112 | 473.4 | 121.1 | 56.8 | 62.7 | 130.7 | 136.7 | 140.2
234 | 113 | 472.7 | 122.6 | 57.6 | 63.6 | 132.3 | 138 | 141.6
235 | 114 | 471.9 | 124.1 | 58.5 | 64.5 | 133.8 | 139.2 | 142.9
236 | 115 | 471.1 | 125.6 | 59.4 | 65.4 | 135.2 | 140.3 | 144.3
237 | 116 | 470.2 | 127.1 | 60.3 | 66.3 | 136.6 | 141.5 | 145.5
238 | 117 | 469.5 | 128.5 | 61.1 | 67.2 | 138.1 | 142.7 | 146.7
239 | 118 | 468.9 | 130 | 62 | 68.1 | 139.5 | 143.8 | 147.9
240 | 119 | 468.4 | 131.4 | 62.8 | 69 | 140.9 | 145 | 149.1
241 | 120 | 467.9 | 132.8 | 63.6 | 69.9 | 142.4 | 146.1 | 150.2
242 | 121 | 467.4 | 134.3 | 64.4 | 70.8 | 143.8 | 147.2 | 151.3
243 | 122 | 466.8 | 135.7 | 65.2 | 71.8 | 145.3 | 148.2 | 152.5
244 | 123 | 466.2 | 137.2 | 66 | 72.7 | 146.7 | 149.3 | 153.6
245 | 124 | 465.8 | 138.6 | 66.8 | 73.6 | 148 | 150.3 | 154.6
246 | 125 | 465.6 | 140 | 67.6 | 74.5 | 149.4 | 151.3 | 155.7
247 | 126 | 465.3 | 141.4 | 68.4 | 75.4 | 150.6 | 152.3 | 156.8
248 | 127 | 465.2 | 142.8 | 69.3 | 76.3 | 151.8 | 153.3 | 157.8
249 | 128 | 465.1 | 144.2 | 70.1 | 77.2 | 153 | 154.3 | 158.8
250 | 129 | 465 | 145.5 | 71 | 78.1 | 154.1 | 155.3 | 159.8
251 | 130 | 464.9 | 146.9 | 71.8 | 79 | 155.2 | 156.2 | 160.8
252 | 131 | 464.9 | 148.3 | 72.6 | 79.9 | 156.3 | 157.2 | 161.9
253 | 132 | 465.1 | 149.7 | 73.5 | 80.8 | 157.3 | 158.2 | 162.9
254 | 133 | 465.3 | 151.1 | 74.3 | 81.6 | 158.3 | 159.1 | 163.9
255 | 134 | 465.4 | 152.5 | 75.2 | 82.5 | 159.4 | 160.1 | 164.8
256 | 135 | 465.7 | 153.9 | 76 | 83.3 | 160.3 | 161 | 165.8
257 | 136 | 465.9 | 155.4 | 76.8 | 84.2 | 161.3 | 161.9 | 166.8
258 | 137 | 466 | 156.8 | 77.7 | 85 | 162.2 | 162.8 | 167.7
259 | 138 | 466.1 | 158.2 | 78.5 | 85.9 | 163.1 | 163.8 | 168.7
260 | 139 | 466.3 | 159.6 | 79.3 | 86.7 | 164.1 | 164.7 | 169.6
261 | 140 | 466.5 | 161 | 80.2 | 87.6 | 165 | 165.6 | 170.6
262 | 141 | 466.7 | 162.3 | 80.9 | 88.4 | 165.9 | 166.5 | 171.5
263 | 142 | 467 | 163.7 | 81.8 | 89.3 | 166.9 | 167.3 | 172.5
264 | 143 | 467.2 | 165 | 82.6 | 90.1 | 167.8 | 168.2 | 173.4
265 | 144 | 467.4 | 166.4 | 83.3 | 90.9 | 168.7 | 169.1 | 174.3
266 | 145 | 467.6 | 167.7 | 84.1 | 91.7 | 169.6 | 170 | 175.1
267 | 146 | 467.8 | 169 | 84.9 | 92.6 | 170.6 | 170.9 | 176
268 | 147 | 468 | 170.3 | 85.7 | 93.4 | 171.5 | 171.8 | 176.9
269 | 148 | 468.3 | 171.6 | 86.5 | 94.2 | 172.4 | 172.6 | 177.7
270 | 149 | 468.7 | 172.9 | 87.4 | 95 | 173.3 | 173.4 | 178.6
271 | 150 | 469 | 174.1 | 88.2 | 95.8 | 174.2 | 174.3 | 179.4
272 | 151 | 469.1 | 175.4 | 88.9 | 96.6 | 175.2 | 175.1 | 180.3
273 | 152 | 468.9 | 176.7 | 89.7 | 97.4 | 176.2 | 176 | 181.2
274 | 153 | 468.9 | 178 | 90.4 | 98.2 | 177.1 | 176.8 | 182
275 | 154 | 468.9 | 179.2 | 91.2 | 99.1 | 178.1 | 177.6 | 182.9
276 | 155 | 468.9 | 180.5 | 92 | 99.9 | 179 | 178.5 | 183.7
277 | 156 | 469 | 181.7 | 92.8 | 100.7 | 179.9 | 179.3 | 184.5
278 | 157 | 469.1 | 182.9 | 93.6 | 101.5 | 180.7 | 180.1 | 185.4
279 | 158 | 469.4 | 184.1 | 94.4 | 102.3 | 181.6 | 181 | 186.2
280 | 159 | 469.5 | 185.3 | 95.2 | 103.1 | 182.6 | 181.8 | 187
281 | 160 | 469.6 | 186.4 | 96 | 103.9 | 183.4 | 182.6 | 187.8
282 | 161 | 469.6 | 187.6 | 96.8 | 104.8 | 184.3 | 183.3 | 188.6
283 | 162 | 469.5 | 188.8 | 97.5 | 105.6 | 185.2 | 184 | 189.4
284 | 163 | 469.5 | 189.9 | 98.4 | 106.4 | 186.1 | 184.8 | 190.2
285 | 164 | 469.6 | 191 | 99.1 | 107.2 | 187 | 185.6 | 190.9
286 | 165 | 469.5 | 192.1 | 99.9 | 108.1 | 187.9 | 186.4 | 191.7
287 | 166 | 469.4 | 193.1 | 100.7 | 108.8 | 188.8 | 187.2 | 192.5
288 | 167 | 469.3 | 194.2 | 101.5 | 109.6 | 189.7 | 187.9 | 193.2
289 | 168 | 469.4 | 195.2 | 102.3 | 110.4 | 190.6 | 188.7 | 194
290 | 169 | 469.5 | 196.2 | 103.1 | 111.2 | 191.5 | 189.3 | 194.7
291 | 170 | 469.6 | 197.2 | 103.9 | 112 | 192.3 | 190.1 | 195.5
292 | 171 | 469.7 | 198.1 | 104.7 | 112.8 | 193.2 | 190.8 | 196.3
293 | 172 | 469.7 | 199.1 | 105.4 | 113.6 | 194.1 | 191.6 | 196.9
294 | 173 | 469.8 | 200.1 | 106.2 | 114.3 | 195 | 192.4 | 197.7
295 | 174 | 469.7 | 201 | 107 | 115.1 | 195.8 | 193.1 | 198.4
296 | 175 | 469.7 | 201.8 | 107.7 | 115.9 | 196.6 | 193.7 | 199.2
297 | 176 | 469.7 | 202.7 | 108.5 | 116.7 | 197.4 | 194.4 | 199.9
298 | 177 | 469.8 | 203.5 | 109.3 | 117.5 | 198.3 | 195.1 | 200.6
299 | 178 | 469.8 | 204.4 | 110 | 118.3 | 199.1 | 195.9 | 201.4
300 | 179 | 469.9 | 205.2 | 110.9 | 119.2 | 199.9 | 196.6 | 202.1
301 | 180 | 470.1 | 206.1 | 111.6 | 120 | 200.7 | 197.2 | 202.8
302 | 181 | 470.2 | 206.9 | 112.4 | 120.9 | 201.5 | 197.9 | 203.5
303 | 182 | 470.1 | 207.8 | 113.2 | 121.7 | 202.3 | 198.6 | 204.2
304 | 183 | 469.9 | 208.7 | 114 | 122.6 | 203.1 | 199.3 | 204.9
305 | 184 | 470 | 209.6 | 114.9 | 123.5 | 203.9 | 200.1 | 205.6
306 | 185 | 470 | 210.5 | 115.8 | 124.4 | 204.7 | 200.7 | 206.3
307 | 186 | 469.8 | 211.3 | 116.6 | 125.2 | 205.5 | 201.4 | 207
308 | 187 | 469.7 | 212.2 | 117.5 | 126.1 | 206.3 | 202 | 207.7
309 | 188 | 469.6 | 213.1 | 118.4 | 127 | 207.1 | 202.7 | 208.3
310 | 189 | 469.5 | 214 | 119.3 | 127.9 | 207.9 | 203.4 | 209
311 | 190 | 469.6 | 214.9 | 120.3 | 128.8 | 208.8 | 204.1 | 209.7
312 | 191 | 469.5 | 215.8 | 121.2 | 129.7 | 209.6 | 204.7 | 210.3
313 | 192 | 469.6 | 216.7 | 122.2 | 130.6 | 210.5 | 205.4 | 211
314 | 193 | 469.5 | 217.5 | 123.1 | 131.5 | 211.3 | 206 | 211.7
315 | 194 | 469.3 | 218.4 | 124.1 | 132.4 | 212.2 | 206.4 | 212.3
316 | 195 | 469.1 | 219.2 | 125 | 133.3 | 213.1 | 207.1 | 213
317 | 196 | 469 | 220.1 | 126 | 134.2 | 214 | 207.8 | 213.6
318 | 197 | 468.9 | 221 | 126.9 | 135.1 | 214.8 | 208.5 | 214.2
319 | 198 | 468.9 | 221.9 | 127.9 | 136 | 215.7 | 209.2 | 214.9
320 | 199 | 468.9 | 222.8 | 128.9 | 136.9 | 216.6 | 209.9 | 215.5
321 | 200 | 468.8 | 223.8 | 129.8 | 137.7 | 217.4 | 210.4 | 216.2
322 | 201 | 468.7 | 224.7 | 130.8 | 138.6 | 218.3 | 211.1 | 216.9
323 | 202 | 468.8 | 225.7 | 131.7 | 139.5 | 219.2 | 211.6 | 217.5
324 | 203 | 468.9 | 226.6 | 132.7 | 140.3 | 220.1 | 212.2 | 218
325 | 204 | 469 | 227.6 | 133.6 | 141.2 | 220.9 | 212.8 | 218.6
326 | 205 | 469 | 228.6 | 134.6 | 142.1 | 221.7 | 213.5 | 219.2
327 | 206 | 469.1 | 229.5 | 135.6 | 142.9 | 222.5 | 214.1 | 219.8
328 | 207 | 469.3 | 230.5 | 136.5 | 143.8 | 223.3 | 214.8 | 220.4
329 | 208 | 469.6 | 231.5 | 137.5 | 144.7 | 224.1 | 215.4 | 221
330 | 209 | 469.8 | 232.4 | 138.5 | 145.6 | 224.9 | 216 | 221.6
331 | 210 | 470 | 233.4 | 139.5 | 146.4 | 225.5 | 216.5 | 222.2
332 | 211 | 470.3 | 234.3 | 140.5 | 147.3 | 225.9 | 217.1 | 222.9
333 | 212 | 470.3 | 235.3 | 141.5 | 148.2 | 225.9 | 217.7 | 223.5
334 | 213 | 470.1 | 236.3 | 142.6 | 149.2 | 225.7 | 218.3 | 224.1
335 | 214 | 470.1 | 237.4 | 143.6 | 150.1 | 225.7 | 218.9 | 224.7
336 | 215 | 470 | 238.6 | 144.6 | 151.1 | 225.8 | 219.5 | 225.3
337 | 216 | 470 | 239.5 | 145.7 | 152.1 | 225.9 | 220.1 | 225.9
338 | 217 | 470.2 | 240.5 | 146.8 | 153.1 | 226.1 | 220.8 | 226.5
339 | 218 | 470.2 | 241.4 | 147.8 | 154.2 | 226.5 | 221.3 | 227.1
340 | 219 | 470.2 | 242.2 | 148.8 | 155.2 | 227 | 222 | 227.7
341 | 220 | 470.2 | 243 | 149.9 | 156.2 | 227.5 | 222.6 | 228.3
342 | 221 | 470.2 | 243.7 | 151 | 157.2 | 228 | 223.1 | 228.9
343 | 222 | 470.4 | 244.4 | 152 | 158.3 | 228.5 | 223.8 | 229.5
344 | 223 | 470.6 | 245.1 | 153.1 | 159.3 | 229.1 | 224.4 | 230.1
345 | 224 | 470.7 | 245.6 | 154.1 | 160.3 | 229.7 | 225 | 230.6
346 | 225 | 470.7 | 246.1 | 155.1 | 161.3 | 230.3 | 225.7 | 231.2
347 | 226 | 470.6 | 246.5 | 156.2 | 162.3 | 230.8 | 226.3 | 231.7
348 | 227 | 470.6 | 246.9 | 157.1 | 163.3 | 231.4 | 227 | 232.2
349 | 228 | 470.6 | 247.3 | 158.1 | 164.3 | 232 | 227.6 | 232.8
350 | 229 | 470.8 | 247.8 | 159.1 | 165.3 | 232.7 | 228.1 | 233.5
351 | 230 | 470.8 | 248.2 | 160.2 | 166.2 | 233.4 | 228.7 | 234.1
352 | 231 | 470.9 | 248.5 | 161.2 | 167.2 | 234 | 229.3 | 234.7
353 | 232 | 471 | 248.8 | 162.1 | 168.2 | 234.6 | 229.9 | 235.2
354 | 233 | 471 | 249.2 | 163.1 | 169.1 | 235.2 | 230.4 | 235.8
355 | 234 | 471.1 | 249.5 | 164 | 170.1 | 235.7 | 231 | 236.3
356 | 235 | 471.1 | 249.8 | 165 | 171 | 236.1 | 231.6 | 236.9
357 | 236 | 471.1 | 250.1 | 165.9 | 172 | 236.4 | 232.1 | 237.5
358 | 237 | 471 | 250.3 | 166.9 | 172.9 | 236.7 | 232.6 | 238
359 | 238 | 471.1 | 250.5 | 167.8 | 173.8 | 236.7 | 233.2 | 238.6
360 | 239 | 471.1 | 250.8 | 168.8 | 174.7 | 236.8 | 233.8 | 239.1
361 | 240 | 471.1 | 251.1 | 169.7 | 175.6 | 237 | 234.3 | 239.7
362 | 241 | 471.1 | 251.3 | 170.6 | 176.5 | 237.2 | 234.9 | 240.2
363 | 242 | 471.2 | 251.5 | 171.5 | 177.4 | 237.6 | 235.4 | 240.8
364 | 243 | 471 | 251.7 | 172.4 | 178.3 | 237.9 | 236 | 241.4
365 | 244 | 470.8 | 251.9 | 173.3 | 179.2 | 238.4 | 236.6 | 242
366 | 245 | 470.8 | 252.1 | 174.2 | 180.1 | 238.8 | 237 | 242.5
367 | 246 | 470.8 | 252.2 | 175.1 | 180.9 | 239.2 | 237.5 | 243
368 | 247 | 470.7 | 252.4 | 175.9 | 181.8 | 239.6 | 238.1 | 243.5
369 | 248 | 470.6 | 252.4 | 176.8 | 182.6 | 240 | 238.6 | 244
370 | 249 | 470.5 | 252.6 | 177.7 | 183.5 | 240.5 | 239.1 | 244.6
371 | 250 | 470.3 | 252.6 | 178.5 | 184.3 | 240.9 | 239.6 | 245.2
372 | 251 | 470.3 | 252.7 | 179.4 | 185.1 | 241.3 | 240.1 | 245.7
373 | 252 | 470.5 | 252.8 | 180.2 | 186 | 241.7 | 240.6 | 246.2
374 | 253 | 470.7 | 252.8 | 181 | 186.8 | 242.2 | 241.3 | 246.7
375 | 254 | 470.7 | 252.9 | 181.9 | 187.6 | 242.7 | 241.8 | 247.2
376 | 255 | 470.9 | 252.9 | 182.7 | 188.4 | 243.1 | 242.3 | 247.7
377 | 256 | 471.1 | 252.9 | 183.6 | 189.2 | 243.6 | 243 | 248.2
378 | 257 | 471.1 | 252.9 | 184.4 | 190 | 244 | 243.5 | 248.8
379 | 258 | 471.3 | 252.9 | 185.3 | 190.8 | 244.4 | 243.9 | 249.3
380 | 259 | 471.5 | 252.8 | 186.1 | 191.6 | 244.8 | 244.5 | 249.8
381 | 260 | 471.5 | 252.9 | 187 | 192.3 | 245.1 | 245 | 250.2
382 | 261 | 471.6 | 253.1 | 187.8 | 193.1 | 245.3 | 245.4 | 250.7
383 | 262 | 471.5 | 253.3 | 188.6 | 193.9 | 245.5 | 246 | 251.3
384 | 263 | 471.4 | 253.5 | 189.4 | 194.6 | 245.6 | 246.5 | 251.7
385 | 264 | 471.3 | 253.7 | 190.2 | 195.4 | 245.8 | 247 | 252.2
386 | 265 | 471.2 | 253.9 | 190.9 | 196.2 | 246 | 247.4 | 252.7
387 | 266 | 471.2 | 254.2 | 191.7 | 196.9 | 246.2 | 248 | 253.2
388 | 267 | 471.3 | 254.4 | 192.5 | 197.6 | 246.3 | 248.5 | 253.7
389 | 268 | 471.4 | 254.7 | 193.3 | 198.4 | 246.6 | 249 | 254.1
390 | 269 | 471.5 | 255 | 194.1 | 199.1 | 246.8 | 249.6 | 254.6
391 | 270 | 471.5 | 255.3 | 194.8 | 199.8 | 247.2 | 250 | 255.1
392 | 271 | 471.5 | 255.5 | 195.6 | 200.5 | 247.5 | 250.5 | 255.6
393 | 272 | 471.5 | 255.8 | 196.4 | 201.2 | 247.9 | 251 | 256
394 | 273 | 471.4 | 256.1 | 197.1 | 202 | 248.4 | 251.5 | 256.4
395 | 274 | 471.4 | 256.3 | 197.8 | 202.7 | 248.8 | 251.9 | 256.9
396 | 275 | 471.5 | 256.6 | 198.6 | 203.4 | 249.2 | 252.4 | 257.3
397 | 276 | 471.7 | 256.9 | 199.3 | 204.1 | 249.6 | 253.1 | 257.8
398 | 277 | 471.5 | 257.2 | 200 | 204.8 | 250.1 | 253.6 | 258.3
399 | 278 | 471.4 | 257.5 | 200.8 | 205.5 | 250.5 | 254.1 | 258.8
400 | 279 | 471.5 | 257.8 | 201.5 | 206.2 | 250.9 | 254.6 | 259.3
401 | 280 | 471.6 | 258.2 | 202.3 | 206.9 | 251.4 | 255.1 | 259.7
402 | 281 | 471.5 | 258.5 | 203 | 207.5 | 251.8 | 255.5 | 260.1
403 | 282 | 471.6 | 258.8 | 203.8 | 208.2 | 252.3 | 255.8 | 260.6
404 | 283 | 471.5 | 259.2 | 204.5 | 208.9 | 252.8 | 256.3 | 261.1
405 | 284 | 471.4 | 259.5 | 205.2 | 209.6 | 253.2 | 256.7 | 261.5
406 | 285 | 471.3 | 259.9 | 205.9 | 210.3 | 253.7 | 257.2 | 262
407 | 286 | 471.2 | 260.2 | 206.6 | 211 | 254.2 | 257.6 | 262.4
408 | 287 | 471.2 | 260.6 | 207.4 | 211.6 | 254.5 | 258 | 262.9
409 | 288 | 471.2 | 260.9 | 208.1 | 212.3 | 254.8 | 258.6 | 263.3
410 | 289 | 471.1 | 261.2 | 208.8 | 213 | 255 | 259.1 | 263.8
411 | 290 | 471.2 | 261.5 | 209.6 | 213.6 | 255.2 | 259.6 | 264.3
412 | 291 | 471.1 | 261.8 | 210.3 | 214.3 | 255.4 | 260.1 | 264.8
413 | 292 | 470.9 | 262.1 | 211 | 214.9 | 255.6 | 260.5 | 265.3
414 | 293 | 470.9 | 262.3 | 211.6 | 215.6 | 255.9 | 261 | 265.8
415 | 294 | 470.9 | 262.5 | 212.3 | 216.3 | 256.2 | 261.5 | 266.3
416 | 295 | 470.7 | 262.7 | 213 | 216.9 | 256.5 | 261.8 | 266.7
417 | 296 | 470.6 | 263 | 213.6 | 217.6 | 256.9 | 262.3 | 267.1
418 | 297 | 470.5 | 263.2 | 214.3 | 218.2 | 257.3 | 262.8 | 267.6
419 | 298 | 470.4 | 263.5 | 214.9 | 218.9 | 257.8 | 263.3 | 268
420 | 299 | 470.2 | 263.7 | 215.5 | 219.5 | 258.3 | 263.8 | 268.4
421 | 300 | 469.9 | 263.9 | 216.1 | 220.1 | 258.8 | 264.1 | 268.9
422 | 301 | 469.6 | 264.1 | 216.7 | 220.7 | 259.1 | 264.6 | 269.4
423 | 302 | 469.4 | 264.3 | 217.2 | 221.3 | 259.4 | 265 | 269.9
424 | 303 | 469.5 | 264.4 | 217.8 | 221.9 | 259.6 | 265.5 | 270.3
425 | 304 | 469.5 | 264.4 | 218.4 | 222.5 | 259.8 | 265.9 | 270.8
426 | 305 | 469.5 | 264.3 | 219 | 223.1 | 259.9 | 266.3 | 271.3
427 | 306 | 469.5 | 263.7 | 219.5 | 223.7 | 260.1 | 266.8 | 271.7
428 | 307 | 469.6 | 262.6 | 220.1 | 224.2 | 260.2 | 267.3 | 272.2
429 | 308 | 469.7 | 261.3 | 220.7 | 224.8 | 260.4 | 267.7 | 272.6
430 | 309 | 469.8 | 260.1 | 221.2 | 225.3 | 260.9 | 268.1 | 273.1
431 | 310 | 469.9 | 259.2 | 221.7 | 225.9 | 261.5 | 268.7 | 273.4
432 | 311 | 469.8 | 257.2 | 222.3 | 226.4 | 262.2 | 269.1 | 273.9
433 | 312 | 469.8 | 255.6 | 222.8 | 227 | 262.7 | 269.5 | 274.4
434 | 313 | 469.9 | 254.6 | 223.4 | 227.5 | 263.2 | 269.9 | 274.9
435 | 314 | 470.2 | 253.7 | 223.9 | 228.1 | 263.7 | 270.4 | 275.3
436 | 315 | 470.3 | 253 | 224.5 | 228.6 | 264.2 | 270.8 | 275.7
437 | 316 | 470.4 | 252.5 | 225 | 229.2 | 264.6 | 271.3 | 276.2
438 | 317 | 470.5 | 252.1 | 225.6 | 229.7 | 265.1 | 271.8 | 276.6
439 | 318 | 470.6 | 251.8 | 226.1 | 230.3 | 265.5 | 271.9 | 277
440 | 319 | 470.5 | 251.7 | 226.7 | 230.9 | 266.1 | 272.4 | 277.4
441 | 320 | 470.5 | 251.6 | 227.2 | 231.4 | 266.6 | 272.8 | 277.8
442 | 321 | 470.6 | 251.6 | 227.7 | 232 | 267.3 | 273.2 | 278.2
443 | 322 | 470.8 | 251.6 | 228.1 | 232.6 | 268 | 273.6 | 278.6
444 | 323 | 471.1 | 251.7 | 228.6 | 233.1 | 268.6 | 274.1 | 279
445 | 324 | 471.3 | 251.8 | 229.1 | 233.6 | 269.2 | 274.6 | 279.3
446 | 325 | 471.4 | 251.9 | 229.5 | 234.1 | 269.8 | 275.1 | 279.7
447 | 326 | 471.4 | 252 | 230 | 234.6 | 270.4 | 275.6 | 280
448 | 327 | 471.5 | 252.2 | 230.6 | 235.1 | 271 | 276 | 280.3
449 | 328 | 471.7 | 252.4 | 231.1 | 235.6 | 271.5 | 276.5 | 280.7
450 | 329 | 471.8 | 252.6 | 231.6 | 236.1 | 272.1 | 277 | 281.1
451 | 330 | 471.9 | 252.9 | 232.1 | 236.6 | 272.7 | 277.4 | 281.5
452 | 331 | 471.9 | 253.1 | 232.5 | 237.1 | 273.2 | 277.8 | 281.9
453 | 332 | 471.9 | 253.4 | 233.1 | 237.6 | 273.7 | 278.2 | 282.3
454 | 333 | 472 | 253.7 | 233.6 | 238.1 | 274.3 | 278.6 | 282.7
455 | 334 | 472 | 253.9 | 234.1 | 238.5 | 274.9 | 279 | 283.1
456 | 335 | 472 | 254.2 | 234.6 | 239 | 275.4 | 279.4 | 283.5
457 | 336 | 471.9 | 254.5 | 235.2 | 239.5 | 276 | 279.8 | 283.9
458 | 337 | 471.9 | 254.9 | 235.6 | 239.9 | 276.6 | 280.2 | 284.2
459 | 338 | 472.1 | 255.2 | 236.1 | 240.4 | 277 | 280.6 | 284.6
460 | 339 | 472.3 | 255.6 | 236.6 | 240.9 | 277.5 | 281 | 285
461 | 340 | 472.4 | 255.9 | 237.1 | 241.3 | 278 | 281.2 | 285.4
462 | 341 | 472.5 | 256.3 | 237.6 | 241.8 | 278.4 | 281.5 | 285.7
463 | 342 | 472.6 | 256.6 | 238.1 | 242.2 | 278.7 | 282 | 286.1
464 | 343 | 472.5 | 257 | 238.6 | 242.7 | 279 | 282.4 | 286.4
465 | 344 | 472.3 | 257.3 | 239 | 243.1 | 279.5 | 282.8 | 286.7
466 | 345 | 472.2 | 257.7 | 239.5 | 243.6 | 280.1 | 283.2 | 287
467 | 346 | 472 | 258.1 | 239.9 | 244 | 280.7 | 283.6 | 287.4
468 | 347 | 471.6 | 258.5 | 240.3 | 244.4 | 281.3 | 283.9 | 287.8
469 | 348 | 471.4 | 258.9 | 240.8 | 244.9 | 282.1 | 284.4 | 288.1
470 | 349 | 471.4 | 259.4 | 241.2 | 245.3 | 282.9 | 284.9 | 288.5
471 | 350 | 471.3 | 259.8 | 241.7 | 245.8 | 283.8 | 285.2 | 288.8
472 | 351 | 471.2 | 260.2 | 242.1 | 246.2 | 284.8 | 285.5 | 289.2
473 | 352 | 471.2 | 260.6 | 242.6 | 246.7 | 285.7 | 285.9 | 289.5
474 | 353 | 471.4 | 261 | 243.1 | 247.1 | 286.6 | 286.4 | 289.8
475 | 354 | 471.4 | 261.4 | 243.5 | 247.6 | 287.5 | 286.8 | 290.1
476 | 355 | 471.2 | 261.9 | 244 | 248 | 288.3 | 287.2 | 290.5
477 | 356 | 471.2 | 262.3 | 244.4 | 248.5 | 289.1 | 287.5 | 290.8
478 | 357 | 471.1 | 262.8 | 244.9 | 249 | 289.9 | 287.8 | 291.1
479 | 358 | 470.9 | 263.2 | 245.3 | 249.4 | 290.8 | 288.3 | 291.5
480 | 359 | 470.7 | 263.7 | 245.7 | 249.9 | 291.7 | 288.7 | 291.8
481 | 360 | 470.5 | 264.2 | 246.1 | 250.3 | 292.5 | 289 | 292.1
482 | 361 | 470.4 | 264.7 | 246.5 | 250.7 | 293.2 | 289.4 | 292.5
483 | 362 | 470.4 | 265.1 | 246.9 | 251.2 | 294 | 289.8 | 292.8
484 | 363 | 470.4 | 265.6 | 247.3 | 251.6 | 294.7 | 290 | 293.1
485 | 364 | 470.3 | 266.1 | 247.7 | 252.1 | 295.3 | 290.4 | 293.5
486 | 365 | 470.1 | 266.6 | 248.1 | 252.5 | 296 | 290.6 | 293.7
487 | 366 | 470.1 | 267 | 248.5 | 252.9 | 296.6 | 290.9 | 294
488 | 367 | 470.1 | 267.5 | 248.9 | 253.3 | 297.2 | 291.3 | 294.3
489 | 368 | 470.1 | 268 | 249.3 | 253.8 | 297.9 | 291.8 | 294.6
490 | 369 | 470 | 268.5 | 249.6 | 254.2 | 298.6 | 292 | 294.8
491 | 370 | 470.1 | 269 | 250 | 254.6 | 299.4 | 292.5 | 295.1
492 | 371 | 470.1 | 269.5 | 250.3 | 255.1 | 300 | 292.9 | 295.5
493 | 372 | 469.9 | 269.9 | 250.8 | 255.4 | 300.6 | 293.3 | 295.8
494 | 373 | 469.8 | 270.4 | 251.2 | 255.8 | 301.1 | 293.7 | 296.1
495 | 374 | 469.8 | 270.8 | 251.6 | 256.2 | 301.7 | 294.2 | 296.4
496 | 375 | 470.1 | 271.3 | 252.1 | 256.5 | 302.4 | 294.5 | 296.7
497 | 376 | 470.3 | 271.7 | 252.5 | 256.9 | 303 | 294.9 | 297
498 | 377 | 470.4 | 272.2 | 252.9 | 257.3 | 303.8 | 295.3 | 297.4
499 | 378 | 470.6 | 272.7 | 253.4 | 257.7 | 304.5 | 295.7 | 297.6
500 | 379 | 470.5 | 273.2 | 253.7 | 258.1 | 305.3 | 296.1 | 297.9
501 | 380 | 470.3 | 273.6 | 254.2 | 258.4 | 306 | 296.5 | 298.2
502 | 381 | 470.1 | 274.1 | 254.6 | 258.8 | 306.7 | 296.9 | 298.6
503 | 382 | 469.9 | 274.6 | 255 | 259.2 | 307.4 | 297.4 | 298.8
504 | 383 | 469.8 | 275.1 | 255.3 | 259.6 | 308.1 | 297.9 | 299.1
505 | 384 | 469.8 | 275.6 | 255.7 | 260 | 308.7 | 298.3 | 299.4
506 | 385 | 469.7 | 276.1 | 256.1 | 260.4 | 309.4 | 298.8 | 299.8
507 | 386 | 469.5 | 276.6 | 256.5 | 260.7 | 310.2 | 299.2 | 300
508 | 387 | 469.5 | 277.1 | 256.8 | 261.1 | 310.9 | 299.5 | 300.3
509 | 388 | 469.5 | 277.5 | 257.3 | 261.4 | 311.6 | 299.9 | 300.6
510 | 389 | 469.4 | 278 | 257.7 | 261.8 | 312.2 | 300.4 | 300.8
511 | 390 | 469.4 | 278.5 | 258 | 262.1 | 312.8 | 300.9 | 301.1
512 | 391 | 469.6 | 278.9 | 258.5 | 262.5 | 313.4 | 301.2 | 301.4
513 | 392 | 469.6 | 279.4 | 258.9 | 262.8 | 313.9 | 301.5 | 301.7
514 | 393 | 469.7 | 279.9 | 259.2 | 263.2 | 314.5 | 301.8 | 302
515 | 394 | 469.8 | 280.4 | 259.6 | 263.6 | 315.1 | 302.2 | 302.2
516 | 395 | 469.9 | 280.8 | 260 | 264 | 315.6 | 302.5 | 302.5
517 | 396 | 469.9 | 281.3 | 260.4 | 264.4 | 316.2 | 302.9 | 302.7
518 | 397 | 469.9 | 281.8 | 260.8 | 264.8 | 316.8 | 303.2 | 303
519 | 398 | 469.7 | 282.3 | 261.2 | 265.1 | 317.4 | 303.6 | 303.3
520 | 399 | 469.6 | 282.8 | 261.6 | 265.5 | 317.9 | 303.9 | 303.6
521 | 400 | 469.5 | 283.3 | 262 | 265.9 | 318.4 | 304.1 | 303.9
522 | 401 | 469.6 | 283.8 | 262.3 | 266.3 | 319 | 304.5 | 304.2
523 | 402 | 469.6 | 284.3 | 262.7 | 266.7 | 319.5 | 304.9 | 304.5
524 | 403 | 469.7 | 284.7 | 263.1 | 267.1 | 320 | 305.2 | 304.8
525 | 404 | 470 | 285.2 | 263.5 | 267.5 | 320.5 | 305.6 | 305.1
526 | 405 | 470.2 | 285.7 | 263.8 | 267.9 | 321 | 305.9 | 305.4
527 | 406 | 470.3 | 286.2 | 264.3 | 268.3 | 321.5 | 306.2 | 305.7
528 | 407 | 470.3 | 286.7 | 264.6 | 268.7 | 321.9 | 306.5 | 306
529 | 408 | 470.3 | 287.2 | 265 | 269 | 322.4 | 306.8 | 306.4
530 | 409 | 470.3 | 287.7 | 265.3 | 269.4 | 322.8 | 307.2 | 306.8
531 | 410 | 470.4 | 288.2 | 265.7 | 269.8 | 323.2 | 307.5 | 307
532 | 411 | 470.4 | 288.6 | 266 | 270.2 | 323.6 | 307.8 | 307.3
533 | 412 | 470.5 | 289.1 | 266.5 | 270.6 | 323.9 | 308.1 | 307.6
534 | 413 | 470.5 | 289.6 | 266.9 | 270.9 | 324.2 | 308.5 | 307.9
535 | 414 | 470.6 | 290 | 267.3 | 271.3 | 324.6 | 308.7 | 308.2
536 | 415 | 470.5 | 290.5 | 267.7 | 271.7 | 324.9 | 309 | 308.5
537 | 416 | 470.5 | 291 | 268.1 | 272 | 325.2 | 309.2 | 308.7
538 | 417 | 470.6 | 291.5 | 268.4 | 272.4 | 325.6 | 309.5 | 308.9
539 | 418 | 470.6 | 292 | 268.8 | 272.8 | 326 | 309.7 | 309.2
540 | 419 | 470.7 | 292.5 | 269.2 | 273.2 | 326.3 | 310 | 309.4
541 | 420 | 470.8 | 293 | 269.6 | 273.6 | 326.6 | 310.3 | 309.8
542 | 421 | 470.9 | 293.5 | 269.9 | 274 | 327 | 310.6 | 310.2
543 | 422 | 470.7 | 294 | 270.3 | 274.4 | 327.3 | 310.8 | 310.5
544 | 423 | 470.6 | 294.5 | 270.6 | 274.8 | 327.6 | 311 | 310.9
545 | 424 | 470.6 | 295 | 270.9 | 275.2 | 328 | 311.2 | 311.1
546 | 425 | 470.3 | 295.4 | 271.3 | 275.6 | 328.3 | 311.4 | 311.4
547 | 426 | 470.2 | 295.9 | 271.7 | 276 | 328.6 | 311.6 | 311.7
548 | 427 | 470.2 | 296.3 | 272.1 | 276.4 | 328.9 | 311.8 | 312
549 | 428 | 470.2 | 296.8 | 272.5 | 276.8 | 329.1 | 312 | 312.2
550 | 429 | 470.1 | 297.3 | 272.8 | 277.2 | 329.4 | 312.3 | 312.5
551 | 430 | 469.8 | 297.8 | 273.2 | 277.6 | 329.8 | 312.5 | 312.7
552 | 431 | 469.7 | 298.2 | 273.5 | 278 | 330.1 | 312.8 | 312.9
553 | 432 | 469.6 | 298.7 | 273.9 | 278.4 | 330.4 | 313.1 | 313.2
554 | 433 | 469.7 | 299.1 | 274.3 | 278.8 | 330.7 | 313.3 | 313.5
555 | 434 | 469.6 | 299.6 | 274.6 | 279.2 | 331 | 313.5 | 313.8
556 | 435 | 469.5 | 300.1 | 275 | 279.7 | 331.4 | 313.8 | 314.1
557 | 436 | 469.3 | 300.5 | 275.4 | 280.1 | 331.7 | 314 | 314.4
558 | 437 | 469.2 | 301 | 275.8 | 280.5 | 332 | 314.2 | 314.6
559 | 438 | 469.2 | 301.4 | 276.2 | 280.9 | 332.2 | 314.4 | 314.9
560 | 439 | 469.3 | 301.9 | 276.5 | 281.3 | 332.5 | 314.7 | 315.2
561 | 440 | 469.3 | 302.3 | 276.9 | 281.7 | 332.8 | 314.9 | 315.4
562 | 441 | 469.4 | 302.7 | 277.3 | 282.2 | 333 | 315.2 | 315.7
563 | 442 | 469.6 | 303.2 | 277.7 | 282.6 | 333.3 | 315.4 | 316
564 | 443 | 469.6 | 303.6 | 278 | 283 | 333.6 | 315.7 | 316.4
565 | 444 | 469.6 | 304.1 | 278.4 | 283.5 | 333.9 | 316 | 316.7
566 | 445 | 469.6 | 304.5 | 278.8 | 283.9 | 334.1 | 316.3 | 317
567 | 446 | 469.5 | 304.9 | 279.3 | 284.3 | 334.3 | 316.6 | 317.3
568 | 447 | 469.5 | 305.3 | 279.7 | 284.7 | 334.5 | 316.9 | 317.6
569 | 448 | 469.5 | 305.7 | 280.1 | 285.1 | 334.7 | 317.1 | 318
570 | 449 | 469.7 | 306.1 | 280.6 | 285.6 | 334.9 | 317.4 | 318.4
571 | 450 | 470.1 | 306.5 | 281 | 286 | 335.1 | 317.7 | 318.7
572 | 451 | 470.3 | 307 | 281.4 | 286.4 | 335.3 | 317.8 | 319
573 | 452 | 470.3 | 307.4 | 281.9 | 286.8 | 335.5 | 318 | 319.3
574 | 453 | 470.5 | 307.8 | 282.3 | 287.2 | 335.7 | 318.3 | 319.6
575 | 454 | 470.5 | 308.2 | 282.7 | 287.7 | 336 | 318.6 | 319.8
576 | 455 | 470.4 | 308.7 | 283.1 | 288.1 | 336.2 | 318.9 | 320.1
577 | 456 | 470.5 | 309.1 | 283.5 | 288.5 | 336.5 | 319.2 | 320.4
578 | 457 | 470.5 | 309.5 | 284 | 289 | 336.7 | 319.4 | 320.8
579 | 458 | 470.5 | 309.9 | 284.4 | 289.4 | 336.9 | 319.6 | 321.1
580 | 459 | 470.4 | 310.3 | 284.8 | 289.8 | 337.1 | 319.9 | 321.4
581 | 460 | 470.6 | 310.8 | 285.3 | 290.3 | 337.3 | 320.1 | 321.7
582 | 461 | 470.5 | 311.2 | 285.7 | 290.7 | 337.5 | 320.4 | 322.1
583 | 462 | 470.5 | 311.6 | 286.1 | 291.1 | 337.7 | 320.6 | 322.4
584 | 463 | 470.4 | 312 | 286.6 | 291.5 | 337.9 | 320.8 | 322.6
585 | 464 | 470.4 | 312.5 | 287 | 291.9 | 338.1 | 321.1 | 322.9
586 | 465 | 470.4 | 312.9 | 287.4 | 292.4 | 338.3 | 321.3 | 323.2
587 | 466 | 470.5 | 313.3 | 287.8 | 292.8 | 338.4 | 321.5 | 323.4
588 | 467 | 470.5 | 313.7 | 288.2 | 293.2 | 338.6 | 321.7 | 323.7
589 | 468 | 470.6 | 314.1 | 288.7 | 293.6 | 338.9 | 321.9 | 324
590 | 469 | 470.6 | 314.5 | 289.1 | 294.1 | 339.1 | 322.2 | 324.3
591 | 470 | 470.8 | 314.9 | 289.6 | 294.5 | 339.5 | 322.4 | 324.5
592 | 471 | 470.8 | 315.3 | 290 | 294.9 | 340 | 322.6 | 324.8
593 | 472 | 470.9 | 315.7 | 290.4 | 295.3 | 340.5 | 322.8 | 325.1
594 | 473 | 471 | 316.1 | 290.9 | 295.7 | 340.8 | 323.1 | 325.3
595 | 474 | 471 | 316.5 | 291.3 | 296.1 | 341.2 | 323.3 | 325.6
596 | 475 | 470.9 | 317 | 291.7 | 296.6 | 341.6 | 323.5 | 325.9
597 | 476 | 470.9 | 317.4 | 292.1 | 297 | 341.9 | 323.7 | 326.2
598 | 477 | 470.7 | 317.8 | 292.5 | 297.4 | 342.2 | 323.9 | 326.5
599 | 478 | 470.6 | 318.2 | 292.9 | 297.8 | 342.5 | 324.2 | 326.8
600 | 479 | 470.4 | 318.6 | 293.3 | 298.2 | 342.8 | 324.5 | 327
601 | 480 | 470.4 | 319 | 293.7 | 298.6 | 343.1 | 324.7 | 327.3
602 | 481 | 470.4 | 319.4 | 294.1 | 299 | 343.5 | 324.8 | 327.6
603 | 482 | 470.3 | 319.8 | 294.6 | 299.4 | 343.8 | 325 | 327.9
604 | 483 | 470.3 | 320.2 | 295 | 299.8 | 344 | 325.3 | 328.1
605 | 484 | 470.3 | 320.5 | 295.5 | 300.2 | 344.2 | 325.6 | 328.2
606 | 485 | 470.5 | 320.9 | 295.9 | 300.6 | 344.5 | 325.7 | 328.4
607 | 486 | 470.5 | 321.3 | 296.3 | 301 | 344.7 | 325.9 | 328.6
608 | 487 | 470.5 | 321.7 | 296.7 | 301.4 | 345 | 325.9 | 328.9
609 | 488 | 470.5 | 322.1 | 297.1 | 301.8 | 345.3 | 326.2 | 329.1
610 | 489 | 470.6 | 322.5 | 297.6 | 302.2 | 345.5 | 326.4 | 329.4
611 | 490 | 470.6 | 322.8 | 298.1 | 302.6 | 345.4 | 326.7 | 329.6
612 | 491 | 470.6 | 323.2 | 298.5 | 303 | 345.5 | 327.1 | 329.9
613 | 492 | 470.6 | 323.6 | 298.9 | 303.4 | 345.8 | 327.4 | 330.1
614 | 493 | 470.5 | 323.9 | 299.3 | 303.8 | 346 | 327.8 | 330.4
615 | 494 | 470.5 | 324.3 | 299.7 | 304.2 | 345.9 | 328.1 | 330.6
616 | 495 | 470.4 | 324.7 | 300.1 | 304.6 | 346 | 328.4 | 330.8
617 | 496 | 470.4 | 325.1 | 300.5 | 305 | 346.2 | 328.6 | 331
618 | 497 | 470.5 | 325.5 | 300.9 | 305.4 | 346.2 | 328.8 | 331.2
619 | 498 | 470.5 | 325.9 | 301.3 | 305.8 | 346.4 | 329.1 | 331.4
620 | 499 | 470.5 | 326.3 | 301.7 | 306.2 | 346.7 | 329.4 | 331.6
621 | 500 | 470.5 | 326.7 | 302.2 | 306.6 | 346.8 | 329.7 | 331.9
622 | 501 | 470.3 | 327 | 302.6 | 307 | 347 | 329.9 | 332.1
623 | 502 | 470.2 | 327.5 | 303 | 307.4 | 347.2 | 330.2 | 332.4
624 | 503 | 470.1 | 327.9 | 303.3 | 307.9 | 347.7 | 330.5 | 332.7
625 | 504 | 470.1 | 328.3 | 303.7 | 308.3 | 348 | 330.7 | 333
626 | 505 | 470.1 | 328.6 | 304.1 | 308.7 | 348.2 | 331 | 333.3
627 | 506 | 470 | 329 | 304.5 | 309.1 | 348.4 | 331.2 | 333.5
628 | 507 | 470.1 | 329.4 | 304.9 | 309.5 | 348.5 | 331.4 | 333.8
629 | 508 | 470 | 329.8 | 305.3 | 309.9 | 348.7 | 331.6 | 334.2
630 | 509 | 470 | 330.2 | 305.7 | 310.4 | 349 | 331.8 | 334.5
631 | 510 | 470.1 | 330.5 | 306.1 | 310.8 | 349.2 | 331.9 | 334.8
632 | 511 | 470.1 | 330.9 | 306.5 | 311.2 | 349.3 | 332.1 | 335.1
633 | 512 | 470.1 | 331.3 | 307 | 311.6 | 349.4 | 332.3 | 335.4
634 | 513 | 470.2 | 331.6 | 307.4 | 312 | 349.5 | 332.5 | 335.7
635 | 514 | 470.3 | 332 | 307.8 | 312.4 | 349.5 | 332.6 | 336
636 | 515 | 470.3 | 332.3 | 308.3 | 312.8 | 349.7 | 332.8 | 336.4
637 | 516 | 470.3 | 332.7 | 308.7 | 313.2 | 349.9 | 332.8 | 336.7
638 | 517 | 470.4 | 333.1 | 309 | 313.6 | 350.1 | 333.1 | 337
639 | 518 | 470.5 | 333.4 | 309.4 | 314 | 350.3 | 333.4 | 337.3
640 | 519 | 470.6 | 333.8 | 309.8 | 314.4 | 350.6 | 333.6 | 337.7
641 | 520 | 470.7 | 334.2 | 310.3 | 314.8 | 350.7 | 333.9 | 338
642 | 521 | 470.8 | 334.5 | 310.7 | 315.2 | 350.8 | 334.1 | 338.3
643 | 522 | 470.9 | 334.8 | 311.1 | 315.6 | 351.1 | 334.4 | 338.6
644 | 523 | 471.1 | 335.1 | 311.5 | 316 | 351.3 | 334.5 | 338.9
645 | 524 | 471.3 | 335.5 | 311.9 | 316.4 | 351.5 | 334.7 | 339.2
646 | 525 | 471.4 | 335.8 | 312.4 | 316.8 | 351.7 | 335 | 339.5
647 | 526 | 471.4 | 336.2 | 312.8 | 317.2 | 351.9 | 335.2 | 339.8
648 | 527 | 471.4 | 336.5 | 313.2 | 317.6 | 352 | 335.5 | 340.1
649 | 528 | 471.3 | 336.8 | 313.6 | 318.1 | 352.2 | 335.8 | 340.4
650 | 529 | 471.3 | 337.2 | 314 | 318.5 | 352.5 | 336 | 340.7
651 | 530 | 471 | 337.5 | 314.4 | 318.9 | 352.2 | 336.2 | 340.9
652 | 531 | 470.9 | 337.8 | 314.8 | 319.3 | 352.3 | 336.3 | 341.2
653 | 532 | 471 | 338.1 | 315.2 | 319.7 | 352.6 | 336.6 | 341.5
654 | 533 | 471 | 338.5 | 315.6 | 320.1 | 352.9 | 336.8 | 341.8
655 | 534 | 471 | 338.8 | 316 | 320.5 | 352.9 | 337 | 342
656 | 535 | 471.1 | 339.1 | 316.4 | 320.9 | 353.1 | 337.1 | 342.3
657 | 536 | 471.2 | 339.4 | 316.9 | 321.3 | 353.2 | 337.2 | 342.6
658 | 537 | 471.2 | 339.7 | 317.3 | 321.7 | 353.3 | 337.3 | 342.9
659 | 538 | 471.1 | 340.1 | 317.7 | 322.1 | 353.3 | 337.6 | 343.1
660 | 539 | 470.9 | 340.4 | 318.1 | 322.5 | 353.6 | 337.9 | 343.4
661 | 540 | 470.8 | 340.7 | 318.5 | 322.9 | 353.8 | 338.1 | 343.7
662 | 541 | 470.8 | 341.1 | 318.9 | 323.3 | 354 | 338.4 | 343.9
663 | 542 | 470.9 | 341.4 | 319.3 | 323.7 | 354.2 | 338.6 | 344.2
664 | 543 | 470.9 | 341.7 | 319.7 | 324.1 | 354.4 | 338.7 | 344.5
665 | 544 | 470.9 | 342.1 | 320 | 324.5 | 354.7 | 338.9 | 344.8
666 | 545 | 470.8 | 342.4 | 320.4 | 324.9 | 354.9 | 339.1 | 345.1
667 | 546 | 470.7 | 342.8 | 320.8 | 325.3 | 355.1 | 339.3 | 345.4
668 | 547 | 470.5 | 343.1 | 321.2 | 325.7 | 355.4 | 339.4 | 345.6
669 | 548 | 470.4 | 343.5 | 321.6 | 326.1 | 355.6 | 339.6 | 345.8
670 | 549 | 470.4 | 343.8 | 322 | 326.6 | 355.8 | 339.8 | 346
671 | 550 | 470.3 | 344.1 | 322.4 | 326.9 | 356 | 340 | 346.2
672 | 551 | 470.3 | 344.4 | 322.8 | 327.3 | 356.2 | 340.2 | 346.4
673 | 552 | 470.3 | 344.8 | 323.2 | 327.7 | 356.3 | 340.3 | 346.6
674 | 553 | 470.1 | 345.1 | 323.5 | 328.1 | 356.5 | 340.5 | 346.7
675 | 554 | 470.1 | 345.5 | 323.9 | 328.5 | 356.8 | 340.7 | 347
676 | 555 | 470.1 | 345.8 | 324.3 | 328.9 | 357.1 | 340.9 | 347.2
677 | 556 | 470.1 | 346.1 | 324.7 | 329.2 | 357.3 | 341.1 | 347.5
678 | 557 | 470 | 346.4 | 325 | 329.6 | 357.4 | 341.3 | 347.7
679 | 558 | 469.8 | 346.8 | 325.4 | 330 | 357.6 | 341.5 | 348
680 | 559 | 469.7 | 347.1 | 325.7 | 330.4 | 357.8 | 341.7 | 348.2
681 | 560 | 469.6 | 347.4 | 326.1 | 330.8 | 358 | 342 | 348.3
682 | 561 | 469.6 | 347.7 | 326.5 | 331.2 | 358.3 | 342.2 | 348.5
683 | 562 | 469.7 | 348 | 326.9 | 331.6 | 358.5 | 342.4 | 348.7
684 | 563 | 469.7 | 348.4 | 327.2 | 332 | 358.6 | 342.4 | 348.9
685 | 564 | 469.6 | 348.7 | 327.6 | 332.3 | 358.8 | 342.7 | 349.1
686 | 565 | 469.7 | 349.1 | 328 | 332.7 | 359.2 | 342.9 | 349.4
687 | 566 | 469.9 | 349.4 | 328.3 | 333 | 359.4 | 343.1 | 349.5
688 | 567 | 470 | 349.8 | 328.7 | 333.4 | 359.6 | 343.3 | 349.7
689 | 568 | 470 | 350.1 | 329 | 333.8 | 359.8 | 343.5 | 349.9
690 | 569 | 470 | 350.5 | 329.3 | 334.2 | 360.1 | 343.7 | 350.2
691 | 570 | 470 | 350.9 | 329.4 | 334.6 | 360.6 | 343.9 | 350.6
692 | 571 | 470 | 351.2 | 330 | 334.9 | 360.5 | 344.1 | 350.8
693 | 572 | 470.2 | 351.3 | 330.5 | 335.2 | 360.4 | 344.2 | 351
694 | 573 | 470.3 | 351.7 | 330.9 | 335.6 | 360.6 | 344.3 | 351.1
695 | 574 | 470.4 | 352 | 331.2 | 335.9 | 360.8 | 344.6 | 351.3
696 | 575 | 470.5 | 352.3 | 331.6 | 336.3 | 361 | 344.6 | 351.5
697 | 576 | 470.7 | 352.6 | 332 | 336.6 | 361.2 | 344.7 | 351.8
698 | 577 | 470.8 | 352.9 | 332.4 | 336.9 | 361.3 | 344.9 | 352.1
699 | 578 | 470.9 | 353.2 | 332.7 | 337.3 | 361.5 | 345.1 | 352.3
700 | 579 | 470.9 | 353.5 | 333.1 | 337.7 | 361.7 | 345.2 | 352.5
701 | 580 | 471 | 353.8 | 333.4 | 338 | 361.9 | 345.4 | 352.6
702 | 581 | 471.2 | 354.1 | 333.7 | 338.4 | 362.1 | 345.5 | 352.8
703 | 582 | 471.4 | 354.5 | 334.1 | 338.8 | 362.3 | 345.7 | 353
704 | 583 | 471.5 | 354.8 | 334.4 | 339.1 | 362.4 | 345.8 | 353.3
705 | 584 | 471.6 | 355.1 | 334.8 | 339.4 | 362.6 | 345.9 | 353.5
706 | 585 | 471.6 | 355.4 | 335.1 | 339.8 | 362.7 | 346.1 | 353.7
707 | 586 | 471.6 | 355.7 | 335.5 | 340.1 | 362.9 | 346.3 | 353.9
708 | 587 | 471.7 | 356 | 335.8 | 340.5 | 363.1 | 346.5 | 354.1
709 | 588 | 471.7 | 356.2 | 336.2 | 340.8 | 363.3 | 346.8 | 354.3
710 | 589 | 471.5 | 356.5 | 336.6 | 341.1 | 363.4 | 346.9 | 354.4
711 | 590 | 471.5 | 356.8 | 336.9 | 341.5 | 363.6 | 347.1 | 354.6
712 | 591 | 471.6 | 357.1 | 337.3 | 341.8 | 363.8 | 347.2 | 354.7
713 | 592 | 471.5 | 357.4 | 337.7 | 342.2 | 364 | 347.2 | 354.9
714 | 593 | 471.3 | 357.7 | 338 | 342.5 | 364.2 | 347.3 | 355.1
715 | 594 | 471.1 | 358 | 338.3 | 342.8 | 364.4 | 347.5 | 355.3
716 | 595 | 471.1 | 358.2 | 338.6 | 343.2 | 364.6 | 347.6 | 355.5
717 | 596 | 471.1 | 358.5 | 338.9 | 343.5 | 364.8 | 347.8 | 355.8
718 | 597 | 471.2 | 358.8 | 339.3 | 343.8 | 365 | 348 | 356
719 | 598 | 471.2 | 359.1 | 339.7 | 344.2 | 365.1 | 348.1 | 356
720 | 599 | 471 | 359.4 | 340 | 344.5 | 365.4 | 348.4 | 356
721 | 600 | 471 | 359.6 | 340.3 | 344.9 | 365.6 | 348.6 | 356.1
722 | 601 | 471.1 | 359.9 | 340.6 | 345.2 | 365.8 | 348.5 | 356.2
723 | 602 | 471 | 360.1 | 341 | 345.5 | 366 | 348.7 | 356.3
724 | 603 | 470.8 | 360.4 | 341.3 | 345.9 | 366.2 | 348.9 | 356.4
725 | 604 | 470.7 | 360.6 | 341.6 | 346.2 | 366.5 | 349.1 | 356.4
726 | 605 | 470.6 | 360.9 | 341.9 | 346.6 | 366.7 | 349.2 | 356.4
727 | 606 | 470.5 | 361.2 | 342.2 | 346.9 | 367 | 349.4 | 356.4
728 | 607 | 470.5 | 361.5 | 342.6 | 347.2 | 367.2 | 349.6 | 356.5
729 | 608 | 470.6 | 361.7 | 342.9 | 347.5 | 367.4 | 349.8 | 356.5
730 | 609 | 470.6 | 362 | 343.2 | 347.8 | 367.7 | 350 | 356.4
731 | 610 | 470.5 | 362.3 | 343.5 | 348.2 | 367.9 | 350.2 | 356.4
732 | 611 | 470.6 | 362.6 | 343.8 | 348.5 | 368.1 | 350.4 | 356.5
733 | 612 | 470.5 | 362.9 | 344.1 | 348.8 | 368.3 | 350.5 | 356.6
734 | 613 | 470.4 | 363.2 | 344.4 | 349.1 | 368.5 | 350.7 | 356.8
735 | 614 | 470.5 | 363.4 | 344.8 | 349.4 | 368.7 | 350.8 | 356.9
736 | 615 | 470.4 | 363.7 | 345.1 | 349.7 | 368.9 | 350.8 | 357.1
737 | 616 | 470.5 | 363.9 | 345.5 | 350.1 | 369.1 | 351.1 | 357.3
738 | 617 | 470.4 | 364.2 | 345.8 | 350.4 | 369.3 | 351.1 | 357.4
739 | 618 | 470.2 | 364.5 | 346.1 | 350.7 | 369.5 | 351.3 | 357.5
740 | 619 | 470.3 | 364.8 | 346.4 | 351 | 369.7 | 351.5 | 357.5
741 | 620 | 470.6 | 365 | 346.7 | 351.3 | 369.9 | 351.7 | 357.6
742 | 621 | 470.7 | 365.3 | 347 | 351.6 | 370.1 | 352 | 357.7
743 | 622 | 470.7 | 365.6 | 347.4 | 351.9 | 370.3 | 352.1 | 357.9
744 | 623 | 470.8 | 365.9 | 347.8 | 352.2 | 370.5 | 352.3 | 357.8
745 | 624 | 470.9 | 366.1 | 348.1 | 352.5 | 370.6 | 352.4 | 357.8
746 | 625 | 471.1 | 366.4 | 348.4 | 352.8 | 370.8 | 352.6 | 357.9
747 | 626 | 471.2 | 366.6 | 348.8 | 353.1 | 370.9 | 352.7 | 357.9
748 | 627 | 471.2 | 366.9 | 349 | 353.4 | 371.2 | 352.7 | 357.9
749 | 628 | 471.2 | 367.2 | 349.3 | 353.7 | 371.5 | 352.9 | 357.9
750 | 629 | 471.2 | 367.4 | 349.6 | 354 | 371.7 | 353.1 | 358
751 | 630 | 471.1 | 367.7 | 349.9 | 354.3 | 371.9 | 353.4 | 358
752 | 631 | 471.2 | 368 | 350.2 | 354.6 | 372.1 | 353.5 | 358
753 | 632 | 471.2 | 368.2 | 350.5 | 354.8 | 372.3 | 353.5 | 358.2
754 | 633 | 471.3 | 368.5 | 350.8 | 355.1 | 372.4 | 353.7 | 358.3
755 | 634 | 471.4 | 368.8 | 351.2 | 355.4 | 372.6 | 353.8 | 358.3
756 | 635 | 471.3 | 369 | 351.5 | 355.6 | 372.8 | 354 | 358.4
757 | 636 | 471.3 | 369.4 | 351.8 | 355.9 | 373 | 354.2 | 358.5
758 | 637 | 471.5 | 369.6 | 352.1 | 356.2 | 373.2 | 354.3 | 358.5
759 | 638 | 471.5 | 369.9 | 352.3 | 356.5 | 373.4 | 354.4 | 358.6
760 | 639 | 471.5 | 370.3 | 352.6 | 356.8 | 373.6 | 354.4 | 358.6
761 | 640 | 471.5 | 370.6 | 353 | 357 | 373.8 | 354.5 | 358.6
762 | 641 | 471.5 | 370.8 | 353.2 | 357.3 | 374 | 354.6 | 358.6
763 | 642 | 471.4 | 371.1 | 353.6 | 357.6 | 374.2 | 354.6 | 358.7
764 | 643 | 471.4 | 371.4 | 353.9 | 357.8 | 374.4 | 354.7 | 358.7
765 | 644 | 471.5 | 371.6 | 354.2 | 358.1 | 374.6 | 354.9 | 358.8
766 | 645 | 471.5 | 371.9 | 354.5 | 358.4 | 374.9 | 355.1 | 358.9
767 | 646 | 471.5 | 372.2 | 354.7 | 358.7 | 375.1 | 355.3 | 358.9
768 | 647 | 471.4 | 372.5 | 355 | 359 | 375.4 | 355.4 | 358.9
769 | 648 | 471.3 | 372.7 | 355.3 | 359.3 | 375.7 | 355.6 | 358.9
770 | 649 | 471.3 | 373 | 355.6 | 359.6 | 375.9 | 355.7 | 358.9
771 | 650 | 471.1 | 373.2 | 355.9 | 359.9 | 376.1 | 355.8 | 358.8
772 | 651 | 471.1 | 373.4 | 356.2 | 360.2 | 376.3 | 355.9 | 358.9
773 | 652 | 471.1 | 373.7 | 356.5 | 360.5 | 376.6 | 356 | 358.9
774 | 653 | 471 | 373.9 | 356.8 | 360.8 | 376.9 | 356 | 359
775 | 654 | 471.1 | 374 | 357.1 | 361.1 | 377.1 | 356 | 359
776 | 655 | 471.2 | 374.2 | 357.5 | 361.3 | 377.2 | 356.2 | 359
777 | 656 | 471.3 | 374.4 | 357.8 | 361.6 | 377.4 | 356.3 | 359.1
778 | 657 | 471.4 | 374.6 | 358.1 | 361.9 | 377.4 | 356.4 | 359.1
779 | 658 | 471.4 | 374.8 | 358.5 | 362.2 | 377.5 | 356.6 | 359.1
780 | 659 | 471.3 | 374.9 | 358.8 | 362.5 | 377.6 | 356.8 | 359.2
781 | 660 | 471.2 | 375.1 | 359.1 | 362.8 | 377.8 | 356.9 | 359.4
782 | 661 | 471.1 | 375.3 | 359.5 | 363.1 | 378 | 357 | 359.5
783 | 662 | 471.1 | 375.5 | 359.7 | 363.4 | 378.2 | 357.1 | 359.6
784 | 663 | 471 | 375.7 | 360 | 363.7 | 378.5 | 357.3 | 359.7
785 | 664 | 471.1 | 375.9 | 360.3 | 364 | 378.6 | 357.4 | 359.8
786 | 665 | 471.1 | 376.1 | 360.6 | 364.3 | 378.9 | 357.5 | 360
787 | 666 | 471 | 376.3 | 360.9 | 364.7 | 379.1 | 357.5 | 360
788 | 667 | 470.8 | 376.5 | 361.2 | 365 | 379.3 | 357.6 | 360
789 | 668 | 470.6 | 376.6 | 361.5 | 365.3 | 379.6 | 357.6 | 360.1
790 | 669 | 470.5 | 376.8 | 361.8 | 365.5 | 379.8 | 357.5 | 360.3
791 | 670 | 470.5 | 377 | 362.1 | 365.8 | 380 | 357.6 | 360.4
792 | 671 | 470.4 | 377.2 | 362.4 | 366.1 | 380.2 | 357.6 | 360.7
793 | 672 | 470.3 | 377.2 | 362.7 | 366.4 | 380.4 | 357.7 | 361.1
794 | 673 | 470.3 | 377.3 | 363 | 366.7 | 380.7 | 357.8 | 361.5
795 | 674 | 470.2 | 377.4 | 363.3 | 367 | 380.9 | 357.9 | 361.8
796 | 675 | 470 | 377.5 | 363.6 | 367.2 | 381.1 | 358.1 | 362
797 | 676 | 469.9 | 377.5 | 363.9 | 367.5 | 381.3 | 358.1 | 362.4
798 | 677 | 469.9 | 377.7 | 364.2 | 367.8 | 381.5 | 358.1 | 362.6
799 | 678 | 469.9 | 377.8 | 364.5 | 368 | 381.7 | 358.2 | 362.8
800 | 679 | 469.8 | 377.9 | 364.8 | 368.3 | 381.8 | 358.2 | 363
801 | 680 | 469.7 | 378.1 | 365.1 | 368.5 | 382 | 358.3 | 363.2
802 | 681 | 469.6 | 378.2 | 365.3 | 368.8 | 382.3 | 358.3 | 363.4
803 | 682 | 469.6 | 378.4 | 365.6 | 369.1 | 382.5 | 358.4 | 363.6
804 | 683 | 469.6 | 378.6 | 365.9 | 369.3 | 382.7 | 358.5 | 363.6
805 | 684 | 469.6 | 378.7 | 366.1 | 369.6 | 382.9 | 358.4 | 363.7
806 | 685 | 469.6 | 378.9 | 366.4 | 369.8 | 383.1 | 358.5 | 363.9
807 | 686 | 469.6 | 379 | 366.7 | 370 | 383.3 | 358.6 | 364
808 | 687 | 469.7 | 379.2 | 367 | 370.3 | 383.4 | 358.7 | 364.1
809 | 688 | 469.8 | 379.4 | 367.3 | 370.5 | 383.6 | 358.8 | 364.3
810 | 689 | 470.2 | 379.5 | 367.6 | 370.7 | 383.7 | 358.9 | 364.4
811 | 690 | 470.4 | 379.7 | 367.9 | 371 | 383.8 | 358.9 | 364.5
812 | 691 | 470.7 | 379.8 | 368.2 | 371.2 | 383.9 | 359 | 364.8
813 | 692 | 470.9 | 380 | 368.5 | 371.4 | 384.1 | 359 | 365
814 | 693 | 471 | 380.2 | 368.7 | 371.6 | 384.2 | 359 | 365.2
815 | 694 | 471 | 380.3 | 369 | 371.8 | 384.4 | 359.1 | 365.4
816 | 695 | 471.2 | 380.5 | 369.3 | 372 | 384.5 | 359.2 | 365.5
817 | 696 | 471.2 | 380.6 | 369.6 | 372.2 | 384.6 | 359.2 | 365.5
818 | 697 | 471.4 | 380.7 | 369.8 | 372.4 | 384.7 | 359.3 | 365.7
819 | 698 | 471.5 | 380.9 | 370.1 | 372.6 | 384.8 | 359.5 | 365.9
820 | 699 | 471.6 | 381 | 370.3 | 372.7 | 384.9 | 359.7 | 366.2
821 | 700 | 471.7 | 381.2 | 370.6 | 372.9 | 385.1 | 359.8 | 366.4
822 | 701 | 471.4 | 381.4 | 370.8 | 373.1 | 385.2 | 359.9 | 366.6
823 | 702 | 471.1 | 381.5 | 371 | 373.3 | 385.4 | 360.1 | 366.8
824 | 703 | 471.1 | 381.7 | 371.1 | 373.5 | 385.6 | 360.2 | 367.1
825 | 704 | 471.1 | 381.9 | 371.3 | 373.7 | 385.8 | 360.3 | 367.4
826 | 705 | 471 | 382.1 | 371.5 | 373.9 | 385.9 | 360.4 | 367.7
827 | 706 | 471 | 382.2 | 371.6 | 374 | 386.1 | 360.5 | 367.8
828 | 707 | 470.9 | 382.4 | 371.8 | 374.2 | 386.2 | 360.6 | 367.9
829 | 708 | 470.8 | 382.5 | 371.9 | 374.4 | 386.4 | 360.7 | 368
830 | 709 | 470.8 | 382.7 | 372 | 374.5 | 386.5 | 360.7 | 368.3
831 | 710 | 470.8 | 382.9 | 372.1 | 374.7 | 386.7 | 360.7 | 368.5
832 | 711 | 470.7 | 383 | 372.3 | 374.8 | 386.8 | 360.8 | 368.6
833 | 712 | 470.7 | 383.2 | 372.4 | 375 | 387 | 360.9 | 368.6
834 | 713 | 470.8 | 383.4 | 372.5 | 375.1 | 387.1 | 360.8 | 368.7
835 | 714 | 470.9 | 383.5 | 372.6 | 375.3 | 387.2 | 360.8 | 369
836 | 715 | 471.1 | 383.7 | 372.6 | 375.4 | 387.4 | 360.8 | 369.2
837 | 716 | 471.3 | 383.8 | 372.7 | 375.5 | 387.5 | 361 | 369.5
838 | 717 | 471.4 | 383.9 | 372.9 | 375.7 | 387.6 | 361.1 | 369.5
839 | 718 | 471.5 | 384.1 | 373 | 375.8 | 387.7 | 361.1 | 369.6
840 | 719 | 471.7 | 384.2 | 373 | 375.9 | 387.8 | 361.1 | 369.7
841 | 720 | 471.7 | 384.3 | 373.1 | 376 | 387.9 | 361.2 | 369.8
842 | 721 | 471.7 | 384.5 | 373.2 | 376.2 | 388.1 | 361.3 | 370
843 | 722 | 471.8 | 384.6 | 373.2 | 376.3 | 388.3 | 361.3 | 370
844 | 723 | 471.8 | 384.8 | 373.3 | 376.4 | 388.4 | 361.5 | 370.1
845 | 724 | 471.8 | 384.9 | 373.3 | 376.5 | 388.5 | 361.6 | 370.1
846 | 725 | 471.9 | 385 | 373.4 | 376.6 | 388.6 | 361.8 | 370.1
847 | 726 | 471.9 | 385.1 | 373.5 | 376.7 | 388.7 | 361.7 | 370.3
848 | 727 | 471.9 | 385.2 | 373.5 | 376.8 | 388.8 | 361.9 | 370.4
849 | 728 | 472 | 385.4 | 373.5 | 377 | 389 | 362.1 | 370.4
850 | 729 | 471.9 | 385.5 | 373.6 | 377.1 | 389.1 | 362.3 | 370.5
851 | 730 | 472 | 385.6 | 373.6 | 377.2 | 389.3 | 362.4 | 370.5
852 | 731 | 471.9 | 385.7 | 373.6 | 377.3 | 389.4 | 362.6 | 370.7
853 | 732 | 472 | 385.8 | 373.6 | 377.4 | 389.6 | 362.7 | 370.7
854 | 733 | 472 | 385.9 | 373.7 | 377.5 | 389.7 | 362.7 | 370.7
855 | 734 | 472.1 | 386 | 373.7 | 377.6 | 389.8 | 362.8 | 370.9
856 | 735 | 472.2 | 386.1 | 373.7 | 377.6 | 390 | 363 | 371
857 | 736 | 472.2 | 386.2 | 373.8 | 377.7 | 390.1 | 363.1 | 371.2
858 | 737 | 472.2 | 386.3 | 373.8 | 377.8 | 390.2 | 363.3 | 371.4
859 | 738 | 472.2 | 386.4 | 373.9 | 377.9 | 390.3 | 363.4 | 371.5
860 | 739 | 472.2 | 386.5 | 374 | 377.9 | 390.4 | 363.5 | 371.8
861 | 740 | 472.1 | 386.6 | 374 | 378 | 390.5 | 363.7 | 372.1
862 | 741 | 471.9 | 386.7 | 374 | 378.1 | 390.7 | 363.9 | 372.2
863 | 742 | 471.7 | 386.8 | 374.1 | 378.2 | 390.8 | 364 | 372.3
864 | 743 | 471.6 | 386.8 | 374.2 | 378.3 | 390.9 | 364 | 372.5
865 | 744 | 471.4 | 386.9 | 374.2 | 378.3 | 391 | 364.1 | 372.7
866 | 745 | 471.3 | 387 | 374.3 | 378.4 | 391.2 | 364.2 | 372.9
867 | 746 | 471.2 | 387.1 | 374.3 | 378.5 | 391.3 | 364.3 | 373.1
868 | 747 | 471.2 | 387.2 | 374.3 | 378.6 | 391.4 | 364.4 | 373.4
869 | 748 | 471.2 | 387.3 | 374.4 | 378.6 | 391.6 | 364.3 | 373.4
870 | 749 | 471 | 387.4 | 374.4 | 378.7 | 391.7 | 364.4 | 373.4
871 | 750 | 470.9 | 387.5 | 374.5 | 378.8 | 391.8 | 364.6 | 373.5
872 | 751 | 470.9 | 387.6 | 374.5 | 378.8 | 391.9 | 364.7 | 373.6
873 | 752 | 470.9 | 387.7 | 374.5 | 378.9 | 392 | 364.8 | 373.6
874 | 753 | 470.8 | 387.8 | 374.6 | 379 | 392.2 | 364.9 | 373.6
875 | 754 | 470.6 | 387.9 | 374.6 | 379 | 392.2 | 365 | 373.3
876 | 755 | 470.7 | 387.9 | 374.7 | 379.1 | 392.3 | 365 | 373.3
877 | 756 | 470.7 | 388 | 374.7 | 379.1 | 392.4 | 365.1 | 373.6
878 | 757 | 470.7 | 388.1 | 374.8 | 379.2 | 392.5 | 365.2 | 373.6
879 | 758 | 470.7 | 388.2 | 374.9 | 379.2 | 392.6 | 365.4 | 373.7
880 | 759 | 470.7 | 388.3 | 374.9 | 379.3 | 392.7 | 365.4 | 373.9
881 | 760 | 470.7 | 388.4 | 374.9 | 379.4 | 392.8 | 365.6 | 373.9
882 | 761 | 470.5 | 388.5 | 375 | 379.4 | 392.9 | 365.7 | 374
883 | 762 | 470.4 | 388.6 | 375 | 379.5 | 393 | 365.7 | 374.3
884 | 763 | 470.5 | 388.7 | 375.1 | 379.5 | 393 | 365.7 | 374.6
885 | 764 | 470.6 | 388.8 | 375.2 | 379.6 | 393 | 365.8 | 374.7
886 | 765 | 470.7 | 388.8 | 375.3 | 379.6 | 393.1 | 365.9 | 374.9
887 | 766 | 470.6 | 388.9 | 375.4 | 379.7 | 393.2 | 366 | 374.9
888 | 767 | 470.5 | 389 | 375.4 | 379.7 | 393.2 | 366.1 | 375.1
889 | 768 | 470.5 | 389.1 | 375.5 | 379.8 | 393.4 | 366.1 | 375.5
890 | 769 | 470.6 | 389.2 | 375.5 | 379.9 | 393.4 | 366.1 | 375.5
891 | 770 | 470.8 | 389.3 | 375.6 | 379.9 | 393.6 | 366.2 | 375.6
892 | 771 | 470.9 | 389.4 | 375.6 | 380 | 393.7 | 366.2 | 375.7
893 | 772 | 471.1 | 389.5 | 375.7 | 380.1 | 393.8 | 366.2 | 375.9
894 | 773 | 471 | 389.6 | 375.7 | 380.1 | 393.9 | 366.3 | 375.8
895 | 774 | 470.9 | 389.7 | 375.8 | 380.2 | 394 | 366.4 | 375.8
896 | 775 | 470.9 | 389.8 | 375.9 | 380.3 | 394.1 | 366.6 | 376.1
897 | 776 | 470.8 | 389.9 | 375.9 | 380.3 | 394.1 | 366.6 | 376.2
898 | 777 | 470.7 | 390 | 376 | 380.4 | 394.2 | 366.6 | 376.3
899 | 778 | 470.7 | 390 | 376.1 | 380.4 | 394.2 | 366.7 | 376.6
900 | 779 | 470.7 | 390.2 | 376.2 | 380.5 | 394.3 | 366.9 | 376.8
901 | 780 | 470.8 | 390.3 | 376.2 | 380.6 | 394.5 | 367 | 376.9
902 | 781 | 470.8 | 390.4 | 376.2 | 380.7 | 394.6 | 366.9 | 376.9
903 | 782 | 470.9 | 390.5 | 376.3 | 380.7 | 394.7 | 367.1 | 376.8
904 | 783 | 470.9 | 390.6 | 376.4 | 380.8 | 394.7 | 367.2 | 376.9
905 | 784 | 471 | 390.6 | 376.4 | 380.8 | 394.8 | 367.3 | 377.2
906 | 785 | 471.3 | 390.7 | 376.5 | 380.9 | 394.8 | 367.4 | 377.4
907 | 786 | 471.4 | 390.8 | 376.6 | 381 | 394.9 | 367.5 | 377.6
908 | 787 | 471.5 | 390.9 | 376.7 | 381 | 394.9 | 367.4 | 377.5
909 | 788 | 471.6 | 391 | 376.8 | 381.1 | 394.9 | 367.6 | 377.4
910 | 789 | 471.7 | 391.1 | 376.9 | 381.2 | 395 | 367.7 | 377.3
911 | 790 | 471.6 | 391.2 | 377 | 381.2 | 395.1 | 367.9 | 377.3
912 | 791 | 471.6 | 391.3 | 377 | 381.3 | 395.2 | 368 | 377.3
913 | 792 | 471.6 | 391.4 | 377.1 | 381.4 | 395.3 | 368.1 | 377.3
914 | 793 | 471.5 | 391.5 | 377.1 | 381.5 | 395.3 | 368.2 | 377.3
915 | 794 | 471.6 | 391.6 | 377.2 | 381.5 | 395.4 | 368.4 | 377.4
916 | 795 | 471.6 | 391.7 | 377.3 | 381.6 | 395.5 | 368.5 | 377.4
917 | 796 | 471.4 | 391.8 | 377.4 | 381.7 | 395.6 | 368.5 | 377.5
918 | 797 | 471.3 | 391.9 | 377.4 | 381.8 | 395.7 | 368.5 | 377.6
919 | 798 | 471.2 | 392 | 377.5 | 381.8 | 395.7 | 368.7 | 377.9
920 | 799 | 471 | 392.1 | 377.6 | 381.9 | 395.8 | 368.8 | 378.2
921 | 800 | 471 | 392.2 | 377.6 | 382 | 395.9 | 368.8 | 378.3
922 | 801 | 471 | 392.4 | 377.7 | 382.1 | 396 | 368.7 | 378.2
923 | 802 | 471 | 392.5 | 377.8 | 382.2 | 396.1 | 368.8 | 378.2
924 | 803 | 471 | 392.6 | 377.8 | 382.2 | 396.1 | 368.9 | 378.4
925 | 804 | 470.8 | 392.7 | 377.9 | 382.3 | 396.2 | 369 | 378.5
926 | 805 | 470.7 | 392.8 | 377.9 | 382.4 | 396.3 | 369.1 | 378.7
927 | 806 | 470.7 | 392.9 | 378 | 382.5 | 396.4 | 369.2 | 378.9
928 | 807 | 470.6 | 393 | 378.1 | 382.6 | 396.4 | 369.3 | 378.8
929 | 808 | 470.5 | 393.1 | 378.2 | 382.7 | 396.5 | 369.4 | 378.8
930 | 809 | 470.5 | 393.2 | 378.2 | 382.8 | 396.6 | 369.4 | 378.7
931 | 810 | 470.4 | 393.4 | 378.3 | 382.8 | 396.7 | 369.5 | 378.7
932 | 811 | 470.3 | 393.5 | 378.4 | 382.9 | 396.8 | 369.4 | 378.6
933 | 812 | 470.3 | 393.6 | 378.4 | 383 | 396.8 | 369.4 | 378.5
934 | 813 | 470.2 | 393.7 | 378.5 | 383.1 | 396.9 | 369.3 | 378.5
935 | 814 | 470.2 | 393.8 | 378.6 | 383.2 | 396.9 | 369.5 | 378.5
936 | 815 | 470.2 | 393.9 | 378.7 | 383.3 | 397 | 369.5 | 378.3
937 | 816 | 470.4 | 394 | 378.8 | 383.4 | 397.1 | 369.6 | 378.3
938 | 817 | 470.5 | 394 | 378.9 | 383.4 | 397.1 | 369.6 | 378.2
939 | 818 | 470.6 | 394.1 | 379 | 383.5 | 397.2 | 369.7 | 378.2
940 | 819 | 470.6 | 394.3 | 379 | 383.6 | 397.3 | 369.6 | 378
941 | 820 | 470.5 | 394.3 | 379.1 | 383.7 | 397.4 | 369.6 | 378
942 | 821 | 470.4 | 394.5 | 379.1 | 383.8 | 397.5 | 369.3 | 378.1
943 | 822 | 470.5 | 394.5 | 379.3 | 383.9 | 397.5 | 369.4 | 378.1
944 | 823 | 470.5 | 394.6 | 379.4 | 384 | 397.5 | 369.6 | 378.2
945 | 824 | 470.5 | 394.7 | 379.5 | 384.1 | 397.5 | 369.6 | 378.3
946 | 825 | 470.7 | 394.8 | 379.6 | 384.1 | 397.6 | 369.8 | 378.3
947 | 826 | 470.6 | 394.9 | 379.6 | 384.3 | 397.7 | 369.9 | 378.2
948 | 827 | 470.5 | 394.9 | 379.7 | 384.3 | 397.8 | 370 | 378.3
949 | 828 | 470.5 | 395 | 379.8 | 384.4 | 397.9 | 370.1 | 378.5
950 | 829 | 470.6 | 395.1 | 379.8 | 384.5 | 398 | 370.1 | 378.5
951 | 830 | 470.7 | 395.2 | 379.9 | 384.6 | 398 | 370.1 | 378.6
952 | 831 | 470.8 | 395.3 | 380 | 384.7 | 398.1 | 370 | 378.7
953 | 832 | 470.7 | 395.4 | 380 | 384.8 | 398.2 | 370.2 | 378.9
954 | 833 | 470.7 | 395.5 | 380.1 | 384.9 | 398.3 | 370.3 | 378.9
955 | 834 | 470.8 | 395.6 | 380.2 | 385 | 398.4 | 370.4 | 378.9
956 | 835 | 470.7 | 395.7 | 380.3 | 385.1 | 398.4 | 370.5 | 379
957 | 836 | 470.7 | 395.8 | 380.4 | 385.2 | 398.5 | 370.6 | 379.3
958 | 837 | 470.9 | 395.9 | 380.5 | 385.3 | 398.5 | 370.7 | 379.5
959 | 838 | 470.8 | 395.9 | 380.6 | 385.4 | 398.5 | 370.6 | 379.6
960 | 839 | 470.8 | 396 | 380.7 | 385.4 | 398.6 | 370.6 | 379.6
961 | 840 | 470.7 | 396.1 | 380.7 | 385.5 | 398.7 | 370.6 | 379.6
962 | 841 | 470.7 | 396.2 | 380.8 | 385.7 | 398.8 | 370.7 | 379.7
963 | 842 | 470.8 | 396.3 | 380.9 | 385.8 | 398.9 | 370.9 | 379.7
964 | 843 | 470.9 | 396.4 | 380.9 | 385.9 | 399 | 371.1 | 379.8
965 | 844 | 470.9 | 396.5 | 381 | 386 | 399 | 371.2 | 379.9
966 | 845 | 471 | 396.5 | 381.1 | 386 | 399.1 | 371.3 | 380
967 | 846 | 471.2 | 396.6 | 381.2 | 386.1 | 399.2 | 371.4 | 380
968 | 847 | 471.1 | 396.7 | 381.3 | 386.2 | 399.2 | 371.6 | 379.9
969 | 848 | 471.1 | 396.8 | 381.4 | 386.3 | 399.3 | 371.7 | 380
970 | 849 | 471.1 | 396.9 | 381.5 | 386.4 | 399.4 | 371.8 | 380
971 | 850 | 471.1 | 396.9 | 381.6 | 386.5 | 399.4 | 371.8 | 380.1
972 | 851 | 471.2 | 397 | 381.7 | 386.6 | 399.5 | 371.7 | 380.2
973 | 852 | 471.4 | 397.1 | 381.7 | 386.7 | 399.6 | 371.6 | 380.3
974 | 853 | 471.6 | 397.2 | 381.8 | 386.8 | 399.7 | 371.7 | 380.5
975 | 854 | 471.7 | 397.2 | 381.9 | 386.9 | 399.7 | 371.7 | 380.6
976 | 855 | 471.7 | 397.3 | 382 | 387 | 399.8 | 371.7 | 380.7
977 | 856 | 471.7 | 397.4 | 382.1 | 387.1 | 399.9 | 371.7 | 380.7
978 | 857 | 471.8 | 397.5 | 382.2 | 387.2 | 400 | 371.7 | 380.7
979 | 858 | 471.7 | 397.6 | 382.3 | 387.3 | 400 | 371.8 | 380.8
980 | 859 | 471.7 | 397.7 | 382.4 | 387.3 | 400.1 | 371.6 | 380.8
981 | 860 | 471.7 | 397.8 | 382.5 | 387.4 | 400.1 | 371.6 | 380.9
982 | 861 | 471.9 | 397.9 | 382.6 | 387.5 | 400.2 | 371.6 | 381.2
983 | 862 | 471.9 | 398 | 382.7 | 387.7 | 400.3 | 371.7 | 381.2
984 | 863 | 471.8 | 398.1 | 382.8 | 387.8 | 400.4 | 371.6 | 381.2
985 | 864 | 471.8 | 398.2 | 382.8 | 387.9 | 400.5 | 371.6 | 381.2
986 | 865 | 471.8 | 398.3 | 383 | 387.9 | 400.5 | 371.6 | 381.2
987 | 866 | 471.7 | 398.4 | 383 | 388.1 | 400.6 | 371.7 | 381.3
988 | 867 | 471.7 | 398.5 | 383.1 | 388.2 | 400.7 | 371.7 | 381.3
989 | 868 | 471.7 | 398.6 | 383.2 | 388.3 | 400.8 | 371.8 | 381.1
990 | 869 | 471.7 | 398.7 | 383.3 | 388.4 | 400.9 | 371.8 | 381.1
991 | 870 | 471.7 | 398.8 | 383.4 | 388.5 | 400.9 | 371.8 | 381.2
992 | 871 | 471.6 | 398.8 | 383.5 | 388.6 | 400.9 | 371.9 | 381.1
993 | 872 | 471.4 | 398.9 | 383.7 | 388.7 | 401 | 372 | 381.2
994 | 873 | 471.3 | 399 | 383.8 | 388.8 | 401.1 | 372 | 381.2
995 | 874 | 471.3 | 399.1 | 383.8 | 388.9 | 401.2 | 371.9 | 381.2
996 | 875 | 471.4 | 399.2 | 384 | 389 | 401.2 | 371.8 | 381.2
997 | 876 | 471.5 | 399.3 | 384.1 | 389.1 | 401.3 | 371.9 | 381.3
998 | 877 | 471.5 | 399.4 | 384.2 | 389.2 | 401.4 | 371.9 | 381.3
999 | 878 | 471.5 | 399.5 | 384.3 | 389.3 | 401.4 | 371.9 | 381.3
1000 | 879 | 471.6 | 399.5 | 384.5 | 389.4 | 401.4 | 372 | 381.3
1001 | 880 | 471.7 | 399.6 | 384.6 | 389.5 | 401.5 | 372 | 381.3
1002 | 881 | 471.7 | 399.7 | 384.7 | 389.6 | 401.6 | 372 | 381.3
1003 | 882 | 471.6 | 399.8 | 384.8 | 389.7 | 401.6 | 372 | 381.3
1004 | 883 | 471.7 | 399.9 | 385 | 389.8 | 401.7 | 372.1 | 381.4
1005 | 884 | 471.7 | 400 | 385.1 | 389.9 | 401.7 | 372.1 | 381.6
1006 | 885 | 471.8 | 400.1 | 385.2 | 390 | 401.8 | 372 | 381.7
1007 | 886 | 471.8 | 400.1 | 385.3 | 390.1 | 402 | 371.9 | 381.7
1008 | 887 | 471.6 | 400.3 | 385.3 | 390.2 | 402.2 | 371.8 | 381.7
1009 | 888 | 471.5 | 400.4 | 385.5 | 390.3 | 402.3 | 371.9 | 381.7
1010 | 889 | 471.5 | 400.5 | 385.6 | 390.4 | 402.4 | 371.9 | 381.7
1011 | 890 | 471.3 | 400.6 | 385.7 | 390.6 | 402.5 | 371.9 | 381.6
1012 | 891 | 471.1 | 400.7 | 385.8 | 390.7 | 402.6 | 372.1 | 381.4
1013 | 892 | 471.1 | 400.7 | 385.9 | 390.8 | 402.7 | 372.1 | 381.4
1014 | 893 | 471 | 400.8 | 386.1 | 390.9 | 402.7 | 372.1 | 381.4
1015 | 894 | 471 | 400.9 | 386.2 | 391 | 402.8 | 372.1 | 381.5
1016 | 895 | 470.9 | 401 | 386.3 | 391.1 | 402.9 | 372.1 | 381.5
1017 | 896 | 470.8 | 401 | 386.5 | 391.2 | 402.9 | 372 | 381.6
1018 | 897 | 470.9 | 401.1 | 386.6 | 391.3 | 403 | 372.1 | 381.6
1019 | 898 | 471 | 401.2 | 386.7 | 391.5 | 403.2 | 372.1 | 381.6
1020 | 899 | 470.9 | 401.3 | 386.8 | 391.6 | 403.2 | 372 | 381.6
1021 | 900 | 470.9 | 401.4 | 387 | 391.7 | 403.3 | 372 | 381.6
1022 | 901 | 470.9 | 401.5 | 387.1 | 391.8 | 403.4 | 372 | 381.6
1023 | 902 | 470.9 | 401.5 | 387.3 | 391.9 | 403.5 | 371.9 | 381.7
1024 | 903 | 470.8 | 401.6 | 387.4 | 392.1 | 403.6 | 371.8 | 381.7
1025 | 904 | 470.9 | 401.7 | 387.5 | 392.2 | 403.7 | 371.9 | 381.8
1026 | 905 | 470.9 | 401.8 | 387.6 | 392.3 | 403.8 | 371.9 | 381.9
1027 | 906 | 470.9 | 401.8 | 387.8 | 392.4 | 403.9 | 372 | 381.8
1028 | 907 | 470.9 | 401.9 | 387.9 | 392.5 | 403.9 | 371.9 | 381.7
1029 | 908 | 470.8 | 402 | 388 | 392.7 | 404.1 | 371.9 | 381.8
1030 | 909 | 470.7 | 402.1 | 388.1 | 392.8 | 404.2 | 371.9 | 381.7
1031 | 910 | 470.6 | 402.2 | 388.2 | 392.9 | 404.3 | 371.9 | 381.7
1032 | 911 | 470.6 | 402.3 | 388.4 | 393 | 404.4 | 371.9 | 381.9
1033 | 912 | 470.5 | 402.4 | 388.4 | 393.2 | 404.5 | 371.9 | 382
1034 | 913 | 470.4 | 402.4 | 388.6 | 393.3 | 404.6 | 372 | 382.1
1035 | 914 | 470.4 | 402.5 | 388.7 | 393.4 | 404.7 | 372 | 382.1
1036 | 915 | 470.4 | 402.6 | 388.8 | 393.5 | 404.8 | 372.2 | 382.1
1037 | 916 | 470.4 | 402.7 | 389 | 393.6 | 404.9 | 372.2 | 382.1
1038 | 917 | 470.5 | 402.7 | 389.1 | 393.8 | 405 | 372.2 | 382.2
1039 | 918 | 470.6 | 402.8 | 389.2 | 393.9 | 405.1 | 372.4 | 382.3
1040 | 919 | 470.7 | 402.9 | 389.3 | 394 | 405.2 | 372.3 | 382.4
1041 | 920 | 470.9 | 403 | 389.5 | 394.1 | 405.2 | 372.4 | 382.5
1042 | 921 | 470.9 | 403 | 389.7 | 394.2 | 405.3 | 372.4 | 382.5
1043 | 922 | 471 | 403.1 | 389.8 | 394.3 | 405.4 | 372.4 | 382.5
1044 | 923 | 470.9 | 403.2 | 389.9 | 394.4 | 405.4 | 372.4 | 382.6
1045 | 924 | 470.9 | 403.2 | 390.1 | 394.5 | 405.5 | 372.5 | 382.6
1046 | 925 | 470.9 | 403.3 | 390.2 | 394.7 | 405.6 | 372.5 | 382.6
1047 | 926 | 471 | 403.4 | 390.3 | 394.8 | 405.7 | 372.5 | 382.7
1048 | 927 | 471.2 | 403.5 | 390.4 | 394.9 | 405.8 | 372.5 | 382.7
1049 | 928 | 471.1 | 403.6 | 390.5 | 395 | 405.9 | 372.5 | 382.7
1050 | 929 | 471 | 403.6 | 390.6 | 395.1 | 406 | 372.6 | 382.8
1051 | 930 | 471 | 403.7 | 390.7 | 395.3 | 406.1 | 372.6 | 382.9
1052 | 931 | 470.9 | 403.8 | 390.8 | 395.4 | 406.2 | 372.6 | 383
1053 | 932 | 470.8 | 403.9 | 390.9 | 395.5 | 406.3 | 372.7 | 383
1054 | 933 | 470.8 | 404 | 391 | 395.6 | 406.4 | 372.7 | 383
1055 | 934 | 470.8 | 404.1 | 391.2 | 395.7 | 406.5 | 372.7 | 383.1
1056 | 935 | 470.7 | 404.1 | 391.3 | 395.8 | 406.6 | 372.7 | 383
1057 | 936 | 470.6 | 404.2 | 391.3 | 395.9 | 406.7 | 372.8 | 383.1
1058 | 937 | 470.7 | 404.3 | 391.4 | 396.1 | 406.8 | 372.7 | 383.1
1059 | 938 | 470.9 | 404.4 | 391.6 | 396.1 | 406.9 | 372.8 | 383.2
1060 | 939 | 471.1 | 404.5 | 391.7 | 396.3 | 406.9 | 372.9 | 383.3
1061 | 940 | 471.1 | 404.6 | 391.8 | 396.4 | 407 | 372.9 | 383.4
1062 | 941 | 471.2 | 404.6 | 391.9 | 396.5 | 407 | 373 | 383.4
1063 | 942 | 471.3 | 404.7 | 392.1 | 396.6 | 407.1 | 373 | 383.3
1064 | 943 | 471.4 | 404.8 | 392.2 | 396.6 | 407.1 | 373.1 | 383.3
1065 | 944 | 471.5 | 404.8 | 392.3 | 396.7 | 407.2 | 373.2 | 383.4
1066 | 945 | 471.4 | 404.9 | 392.4 | 396.9 | 407.3 | 373.2 | 383.6
1067 | 946 | 471.4 | 405 | 392.5 | 397 | 407.4 | 373.3 | 383.7
1068 | 947 | 471.4 | 405.1 | 392.6 | 397.1 | 407.5 | 373.3 | 383.7
1069 | 948 | 471.3 | 405.2 | 392.7 | 397.2 | 407.6 | 373.3 | 383.7
1070 | 949 | 471.2 | 405.3 | 392.7 | 397.3 | 407.7 | 373.3 | 383.6
1071 | 950 | 471.1 | 405.4 | 392.8 | 397.4 | 407.8 | 373.4 | 383.6
1072 | 951 | 471 | 405.4 | 392.9 | 397.5 | 408 | 373.5 | 383.6
1073 | 952 | 471 | 405.5 | 393 | 397.6 | 408.1 | 373.5 | 383.7
1074 | 953 | 471 | 405.6 | 393.1 | 397.7 | 408.1 | 373.5 | 383.7
1075 | 954 | 471.1 | 405.7 | 393.2 | 397.8 | 408.1 | 373.4 | 383.7
1076 | 955 | 471.3 | 405.7 | 393.3 | 397.9 | 408.2 | 373.4 | 383.8
1077 | 956 | 471.4 | 405.8 | 393.5 | 398 | 408.2 | 373.3 | 383.8
1078 | 957 | 471.5 | 405.9 | 393.5 | 398.1 | 408.3 | 373.4 | 383.8
1079 | 958 | 471.5 | 406 | 393.7 | 398.2 | 408.4 | 373.4 | 383.9
1080 | 959 | 471.5 | 406 | 393.8 | 398.3 | 408.4 | 373.2 | 383.9
1081 | 960 | 471.5 | 406.1 | 393.9 | 398.4 | 408.5 | 373.1 | 383.8
1082 | 961 | 471.4 | 406.2 | 394 | 398.5 | 408.5 | 373.2 | 383.8
1083 | 962 | 471.4 | 406.3 | 394.1 | 398.5 | 408.6 | 373.1 | 383.9
1084 | 963 | 471.2 | 406.3 | 394.2 | 398.7 | 408.6 | 373.1 | 383.9
1085 | 964 | 471.2 | 406.4 | 394.3 | 398.7 | 408.7 | 373.1 | 383.9
1086 | 965 | 471.2 | 406.5 | 394.4 | 398.8 | 408.8 | 373.1 | 383.9
1087 | 966 | 471.1 | 406.6 | 394.4 | 399 | 408.9 | 373 | 384.1
1088 | 967 | 470.9 | 406.7 | 394.5 | 399 | 409 | 373 | 384.2
1089 | 968 | 470.8 | 406.7 | 394.6 | 399.1 | 409.1 | 373.1 | 384.2
1090 | 969 | 470.6 | 406.8 | 394.7 | 399.2 | 409.2 | 373 | 384.2
1091 | 970 | 470.7 | 406.9 | 394.8 | 399.3 | 409.2 | 373 | 384.2
1092 | 971 | 470.6 | 407 | 394.8 | 399.4 | 409.3 | 373 | 384.2
1093 | 972 | 470.6 | 407.1 | 394.9 | 399.5 | 409.4 | 373 | 384.1
1094 | 973 | 470.6 | 407.1 | 395 | 399.6 | 409.5 | 373 | 384.1
1095 | 974 | 470.7 | 407.2 | 395 | 399.7 | 409.6 | 372.9 | 384.1
1096 | 975 | 470.6 | 407.3 | 395.1 | 399.8 | 409.7 | 372.9 | 384.2
1097 | 976 | 470.5 | 407.4 | 395.2 | 399.9 | 409.8 | 372.8 | 384.2
1098 | 977 | 470.5 | 407.4 | 395.3 | 400 | 409.9 | 372.8 | 384.3
1099 | 978 | 470.4 | 407.5 | 395.4 | 400.1 | 409.9 | 372.8 | 384.3
1100 | 979 | 470.3 | 407.6 | 395.5 | 400.2 | 410 | 372.8 | 384.2
1101 | 980 | 470.4 | 407.6 | 395.6 | 400.3 | 410 | 372.7 | 384.3
1102 | 981 | 470.5 | 407.7 | 395.7 | 400.4 | 410.1 | 372.7 | 384.4
1103 | 982 | 470.6 | 407.8 | 395.7 | 400.5 | 410.2 | 372.7 | 384.4
1104 | 983 | 470.6 | 407.9 | 395.9 | 400.6 | 410.2 | 372.8 | 384.4
1105 | 984 | 470.7 | 407.9 | 396 | 400.6 | 410.3 | 372.8 | 384.4
1106 | 985 | 470.8 | 408 | 396.1 | 400.7 | 410.4 | 372.9 | 384.5
1107 | 986 | 470.9 | 408.1 | 396.1 | 400.8 | 410.4 | 373 | 384.5
1108 | 987 | 471 | 408.2 | 396.2 | 400.9 | 410.5 | 372.9 | 384.5
1109 | 988 | 471 | 408.2 | 396.3 | 401 | 410.6 | 372.9 | 384.4
1110 | 989 | 471.1 | 408.3 | 396.4 | 401.1 | 410.7 | 373.1 | 384.5
1111 | 990 | 471.2 | 408.4 | 396.5 | 401.2 | 410.7 | 372.9 | 384.6
1112 | 991 | 471.3 | 408.4 | 396.6 | 401.3 | 410.8 | 372.9 | 384.6
1113 | 992 | 471.3 | 408.5 | 396.7 | 401.4 | 410.8 | 372.9 | 384.6
1114 | 993 | 471.3 | 408.6 | 396.8 | 401.4 | 410.9 | 372.9 | 384.7
1115 | 994 | 471.2 | 408.6 | 396.9 | 401.5 | 410.9 | 372.8 | 384.7
1116 | 995 | 471.3 | 408.7 | 397 | 401.6 | 411 | 372.9 | 384.7
1117 | 996 | 471.2 | 408.8 | 397.1 | 401.7 | 411.1 | 372.9 | 384.7
1118 | 997 | 471.2 | 408.9 | 397.1 | 401.8 | 411.2 | 372.9 | 384.7
1119 | 998 | 471.3 | 408.9 | 397.2 | 401.8 | 411.2 | 372.9 | 384.8
1120 | 999 | 471.3 | 409 | 397.3 | 401.9 | 411.3 | 372.8 | 384.7
1121 | 1000 | 471.5 | 409 | 397.4 | 402 | 411.3 | 372.9 | 384.6
1122 | 1001 | 471.4 | 409.1 | 397.6 | 402 | 411.2 | 372.9 | 384.6
1123 | 1002 | 471.3 | 409.2 | 397.7 | 402.1 | 411.3 | 372.9 | 384.7
1124 | 1003 | 471.2 | 409.2 | 397.7 | 402.2 | 411.4 | 373 | 384.7
1125 | 1004 | 471.1 | 409.3 | 397.8 | 402.3 | 411.5 | 373 | 384.8
1126 | 1005 | 470.8 | 409.4 | 397.9 | 402.4 | 411.5 | 372.9 | 384.8
1127 | 1006 | 470.6 | 409.5 | 397.9 | 402.5 | 411.6 | 372.9 | 384.8
1128 | 1007 | 470.6 | 409.5 | 398 | 402.6 | 411.7 | 372.8 | 384.8
1129 | 1008 | 470.5 | 409.6 | 398.1 | 402.6 | 411.8 | 372.8 | 384.8
1130 | 1009 | 470.6 | 409.7 | 398.1 | 402.7 | 411.8 | 372.7 | 384.8
1131 | 1010 | 470.6 | 409.7 | 398.2 | 402.8 | 411.9 | 372.5 | 384.9
1132 | 1011 | 470.5 | 409.8 | 398.3 | 402.9 | 412 | 372.5 | 384.9
1133 | 1012 | 470.4 | 409.9 | 398.3 | 402.9 | 412.1 | 372.5 | 384.9
1134 | 1013 | 470.4 | 410 | 398.4 | 403 | 412.1 | 372.5 | 384.9
1135 | 1014 | 470.5 | 410 | 398.5 | 403.1 | 412.1 | 372.5 | 385
1136 | 1015 | 470.7 | 410.1 | 398.6 | 403.2 | 412.1 | 372.5 | 384.9
1137 | 1016 | 470.9 | 410.2 | 398.7 | 403.2 | 412.2 | 372.5 | 384.9
1138 | 1017 | 471 | 410.2 | 398.8 | 403.3 | 412.2 | 372.5 | 384.9
1139 | 1018 | 471 | 410.3 | 398.9 | 403.4 | 412.3 | 372.6 | 385
1140 | 1019 | 471 | 410.4 | 398.9 | 403.5 | 412.3 | 372.6 | 385
1141 | 1020 | 471 | 410.4 | 399 | 403.5 | 412.4 | 372.6 | 385.1
1142 | 1021 | 470.8 | 410.5 | 399.1 | 403.6 | 412.5 | 372.4 | 385.2
1143 | 1022 | 470.8 | 410.6 | 399.1 | 403.7 | 412.6 | 372.5 | 385.1
1144 | 1023 | 470.7 | 410.6 | 399.2 | 403.8 | 412.6 | 372.5 | 384.9
1145 | 1024 | 470.7 | 410.7 | 399.3 | 403.8 | 412.6 | 372.6 | 384.9
1146 | 1025 | 470.7 | 410.8 | 399.4 | 403.9 | 412.7 | 372.5 | 384.8
1147 | 1026 | 470.7 | 410.9 | 399.5 | 404 | 412.7 | 372.4 | 384.8
1148 | 1027 | 470.7 | 410.9 | 399.5 | 404.1 | 412.8 | 372.4 | 384.8
1149 | 1028 | 470.8 | 411 | 399.6 | 404.1 | 412.8 | 372.3 | 384.7
1150 | 1029 | 470.8 | 411 | 399.7 | 404.2 | 412.9 | 372.2 | 384.7
1151 | 1030 | 470.7 | 411.1 | 399.8 | 404.2 | 412.9 | 372.2 | 384.8
1152 | 1031 | 470.7 | 411.2 | 399.9 | 404.3 | 412.9 | 372.2 | 384.8
1153 | 1032 | 470.5 | 411.2 | 399.9 | 404.4 | 413 | 372.1 | 384.8
1154 | 1033 | 470.2 | 411.3 | 400 | 404.4 | 413.1 | 372.1 | 384.8
1155 | 1034 | 470.2 | 411.4 | 400 | 404.5 | 413.2 | 372 | 384.8
1156 | 1035 | 470.2 | 411.5 | 400.1 | 404.6 | 413.3 | 372 | 384.8
1157 | 1036 | 470.2 | 411.5 | 400.1 | 404.7 | 413.4 | 372 | 384.9
1158 | 1037 | 470.4 | 411.6 | 400.2 | 404.8 | 413.5 | 371.9 | 385
1159 | 1038 | 470.5 | 411.6 | 400.2 | 404.8 | 413.5 | 371.9 | 385.1
1160 | 1039 | 470.5 | 411.7 | 400.3 | 404.9 | 413.5 | 372 | 385
1161 | 1040 | 470.6 | 411.7 | 400.4 | 404.9 | 413.5 | 372.1 | 384.9
1162 | 1041 | 470.7 | 411.8 | 400.5 | 405 | 413.6 | 372.4 | 385
1163 | 1042 | 470.7 | 411.8 | 400.5 | 405.1 | 413.6 | 372.4 | 385
1164 | 1043 | 470.7 | 411.9 | 400.7 | 405.1 | 413.6 | 372.5 | 385
1165 | 1044 | 470.8 | 411.9 | 400.7 | 405.2 | 413.7 | 372.5 | 385
1166 | 1045 | 470.8 | 412 | 400.8 | 405.2 | 413.7 | 372.4 | 385.1
1167 | 1046 | 470.7 | 412 | 400.8 | 405.3 | 413.8 | 372.4 | 385.1
1168 | 1047 | 470.7 | 412.1 | 400.9 | 405.4 | 413.9 | 372.4 | 385.1
1169 | 1048 | 470.8 | 412.1 | 400.9 | 405.4 | 413.9 | 372.4 | 385.1
1170 | 1049 | 470.8 | 412.2 | 401 | 405.5 | 414 | 372.5 | 385
1171 | 1050 | 470.8 | 412.2 | 401 | 405.6 | 414 | 372.5 | 385
1172 | 1051 | 470.8 | 412.3 | 401.1 | 405.6 | 414.1 | 372.4 | 384.9
1173 | 1052 | 470.8 | 412.3 | 401.2 | 405.7 | 414.2 | 372.4 | 385
1174 | 1053 | 470.8 | 412.4 | 401.2 | 405.8 | 414.2 | 372.4 | 385
1175 | 1054 | 470.8 | 412.5 | 401.3 | 405.8 | 414.2 | 372.4 | 385.1
1176 | 1055 | 471 | 412.5 | 401.4 | 405.9 | 414.2 | 372.3 | 385.1
1177 | 1056 | 471.2 | 412.6 | 401.4 | 405.9 | 414.3 | 372.5 | 385.2
1178 | 1057 | 471.2 | 412.6 | 401.5 | 406 | 414.3 | 372.3 | 385.3
1179 | 1058 | 471.1 | 412.7 | 401.6 | 406 | 414.4 | 372.4 | 385.3
1180 | 1059 | 471 | 412.7 | 401.7 | 406.1 | 414.4 | 372.4 | 385.4
1181 | 1060 | 471 | 412.8 | 401.7 | 406.2 | 414.5 | 372.5 | 385.3
1182 | 1061 | 470.9 | 412.9 | 401.7 | 406.2 | 414.7 | 372.7 | 385.3
1183 | 1062 | 470.8 | 412.9 | 401.7 | 406.3 | 414.8 | 372.7 | 385.3
1184 | 1063 | 470.8 | 413 | 401.8 | 406.4 | 414.9 | 372.8 | 385.1
1185 | 1064 | 470.7 | 413 | 401.8 | 406.4 | 414.9 | 372.8 | 385.1
1186 | 1065 | 470.6 | 413 | 401.9 | 406.5 | 415 | 372.9 | 385
1187 | 1066 | 470.6 | 413.1 | 402 | 406.6 | 415.1 | 373 | 384.9
1188 | 1067 | 470.7 | 413.1 | 402 | 406.6 | 415.1 | 373 | 384.9
1189 | 1068 | 470.8 | 413.2 | 402.1 | 406.7 | 415.2 | 373 | 385
1190 | 1069 | 470.9 | 413.2 | 402.1 | 406.8 | 415.3 | 373 | 385.1
1191 | 1070 | 471 | 413.3 | 402.2 | 406.8 | 415.4 | 373 | 385.2
1192 | 1071 | 471.1 | 413.3 | 402.2 | 406.9 | 415.5 | 373 | 385.4
1193 | 1072 | 471.1 | 413.4 | 402.3 | 407 | 415.6 | 373.1 | 385.5
1194 | 1073 | 471 | 413.4 | 402.4 | 407 | 415.7 | 373.1 | 385.6
1195 | 1074 | 471.2 | 413.4 | 402.4 | 407.1 | 415.7 | 373 | 385.7
1196 | 1075 | 471.2 | 413.5 | 402.5 | 407.1 | 415.7 | 373 | 385.8
1197 | 1076 | 471.3 | 413.5 | 402.6 | 407.2 | 415.8 | 373.1 | 385.9
1198 | 1077 | 471.2 | 413.5 | 402.7 | 407.2 | 415.8 | 373.1 | 385.9
1199 | 1078 | 471.2 | 413.5 | 402.8 | 407.3 | 415.9 | 373.1 | 385.9
1200 | 1079 | 471.2 | 413.6 | 402.8 | 407.4 | 416 | 373.1 | 386
1201 | 1080 | 471.3 | 413.6 | 402.9 | 407.4 | 416.1 | 373.2 | 386.1
1202 | 1081 | 471.3 | 413.7 | 402.9 | 407.5 | 416.2 | 373.2 | 386.1
1203 | 1082 | 471.3 | 413.8 | 402.9 | 407.6 | 416.4 | 373.3 | 386.1
1204 | 1083 | 471.4 | 413.8 | 402.9 | 407.7 | 416.5 | 373.2 | 386.1
1205 | 1084 | 471.3 | 413.8 | 403 | 407.7 | 416.6 | 373.3 | 386.1
1206 | 1085 | 471.3 | 413.9 | 403.1 | 407.8 | 416.6 | 373.3 | 386.1
1207 | 1086 | 471.3 | 413.9 | 403.1 | 407.8 | 416.7 | 373.4 | 386.2
1208 | 1087 | 471.2 | 414 | 403.2 | 407.9 | 416.8 | 373.5 | 386.2
1209 | 1088 | 471.1 | 414 | 403.2 | 408 | 416.9 | 373.6 | 386.3
1210 | 1089 | 471 | 414.1 | 403.3 | 408 | 416.9 | 373.6 | 386.3
1211 | 1090 | 471.1 | 414.1 | 403.3 | 408.1 | 417 | 373.6 | 386.4
1212 | 1091 | 471.1 | 414.1 | 403.4 | 408.1 | 417.1 | 373.6 | 386.4
1213 | 1092 | 471.1 | 414.1 | 403.5 | 408.2 | 417.1 | 373.6 | 386.4
1214 | 1093 | 471.1 | 414.2 | 403.5 | 408.3 | 417.2 | 373.7 | 386.2
1215 | 1094 | 471.2 | 414.2 | 403.6 | 408.3 | 417.3 | 373.7 | 386.2
1216 | 1095 | 471.2 | 414.2 | 403.7 | 408.4 | 417.3 | 373.8 | 386.2
1217 | 1096 | 471.4 | 414.3 | 403.7 | 408.4 | 417.4 | 373.9 | 386.2
1218 | 1097 | 471.6 | 414.3 | 403.8 | 408.5 | 417.5 | 373.9 | 386.2
1219 | 1098 | 471.6 | 414.4 | 403.9 | 408.5 | 417.5 | 374 | 386.2
1220 | 1099 | 471.5 | 414.4 | 404 | 408.6 | 417.5 | 373.9 | 386.2
1221 | 1100 | 471.5 | 414.4 | 404.1 | 408.6 | 417.5 | 374 | 386.3
1222 | 1101 | 471.6 | 414.5 | 404.2 | 408.7 | 417.5 | 374.1 | 386.3
1223 | 1102 | 471.5 | 414.5 | 404.2 | 408.7 | 417.6 | 374.1 | 386.3
1224 | 1103 | 471.5 | 414.6 | 404.3 | 408.8 | 417.7 | 374.3 | 386.3
1225 | 1104 | 471.5 | 414.6 | 404.3 | 408.8 | 417.8 | 374.4 | 386.3
1226 | 1105 | 471.4 | 414.7 | 404.3 | 408.9 | 417.9 | 374.4 | 386.3
1227 | 1106 | 471.1 | 414.7 | 404.4 | 409 | 417.9 | 374.3 | 386.4
1228 | 1107 | 470.9 | 414.7 | 404.4 | 409 | 418 | 374.2 | 386.4
1229 | 1108 | 470.8 | 414.8 | 404.4 | 409.1 | 418.1 | 374.2 | 386.4
1230 | 1109 | 470.7 | 414.9 | 404.4 | 409.2 | 418.2 | 374.3 | 386.4
1231 | 1110 | 470.8 | 414.9 | 404.5 | 409.2 | 418.3 | 374.3 | 386.4
1232 | 1111 | 470.8 | 415 | 404.5 | 409.3 | 418.4 | 374.4 | 386.4
1233 | 1112 | 470.6 | 415 | 404.6 | 409.3 | 418.4 | 374.4 | 386.4
1234 | 1113 | 470.7 | 415.1 | 404.6 | 409.4 | 418.5 | 374.3 | 386.4
1235 | 1114 | 470.7 | 415.1 | 404.7 | 409.4 | 418.5 | 374.3 | 386.4
1236 | 1115 | 470.6 | 415.1 | 404.8 | 409.5 | 418.6 | 374.3 | 386.3
1237 | 1116 | 470.5 | 415.2 | 404.8 | 409.5 | 418.7 | 374.3 | 386.2
1238 | 1117 | 470.5 | 415.2 | 404.8 | 409.6 | 418.7 | 374.3 | 386.1
1239 | 1118 | 470.7 | 415.3 | 404.8 | 409.7 | 418.8 | 374.3 | 386.1
1240 | 1119 | 470.8 | 415.3 | 404.9 | 409.7 | 418.8 | 374.4 | 386
1241 | 1120 | 470.9 | 415.3 | 405 | 409.7 | 418.8 | 374.4 | 385.9
1242 | 1121 | 471 | 415.4 | 405.1 | 409.8 | 418.8 | 374.3 | 385.9
1243 | 1122 | 471.2 | 415.4 | 405.2 | 409.8 | 418.8 | 374.1 | 386
1244 | 1123 | 471.1 | 415.4 | 405.3 | 409.8 | 418.8 | 374.1 | 385.9
1245 | 1124 | 471.1 | 415.5 | 405.4 | 409.9 | 418.9 | 374.2 | 385.9
1246 | 1125 | 471.1 | 415.6 | 405.4 | 410 | 418.9 | 374.3 | 385.7
1247 | 1126 | 471 | 415.6 | 405.4 | 410 | 419 | 374.4 | 385.4
1248 | 1127 | 471 | 415.6 | 405.5 | 410.1 | 419.1 | 374.4 | 385.5
1249 | 1128 | 471.1 | 415.7 | 405.5 | 410.1 | 419.1 | 374.5 | 385.4
1250 | 1129 | 471.2 | 415.7 | 405.6 | 410.2 | 419.2 | 374.5 | 385.5
1251 | 1130 | 471.4 | 415.8 | 405.6 | 410.2 | 419.2 | 374.5 | 385.6
1252 | 1131 | 471.5 | 415.8 | 405.7 | 410.3 | 419.2 | 374.5 | 385.7
1253 | 1132 | 471.5 | 415.9 | 405.7 | 410.3 | 419.3 | 374.4 | 385.8
1254 | 1133 | 471.5 | 415.9 | 405.8 | 410.4 | 419.3 | 374.4 | 385.8
1255 | 1134 | 471.3 | 416 | 405.8 | 410.4 | 419.4 | 374.5 | 385.9
1256 | 1135 | 471.3 | 416 | 405.9 | 410.5 | 419.4 | 374.4 | 386
1257 | 1136 | 471.3 | 416 | 406 | 410.5 | 419.4 | 374.4 | 386.1
1258 | 1137 | 471.3 | 416 | 406.1 | 410.5 | 419.4 | 374.6 | 386.2
1259 | 1138 | 471.3 | 416.1 | 406.1 | 410.6 | 419.4 | 374.6 | 386.2
1260 | 1139 | 471.1 | 416.1 | 406.2 | 410.6 | 419.5 | 374.6 | 386.2
1261 | 1140 | 471.1 | 416.2 | 406.2 | 410.7 | 419.6 | 374.6 | 386.2
1262 | 1141 | 471.1 | 416.2 | 406.2 | 410.7 | 419.6 | 374.6 | 386.1
1263 | 1142 | 471.1 | 416.3 | 406.2 | 410.8 | 419.7 | 374.6 | 386
1264 | 1143 | 471.1 | 416.3 | 406.3 | 410.8 | 419.8 | 374.6 | 385.9
1265 | 1144 | 471.2 | 416.4 | 406.3 | 410.9 | 419.8 | 374.6 | 385.9
1266 | 1145 | 471.1 | 416.4 | 406.3 | 410.9 | 419.9 | 374.6 | 386
1267 | 1146 | 470.9 | 416.5 | 406.4 | 411 | 419.9 | 374.6 | 385.9
1268 | 1147 | 470.7 | 416.5 | 406.4 | 411 | 420 | 374.5 | 385.9
1269 | 1148 | 470.7 | 416.6 | 406.5 | 411 | 420 | 374.5 | 385.9
1270 | 1149 | 470.9 | 416.7 | 406.5 | 411.1 | 420.1 | 374.6 | 385.9
1271 | 1150 | 470.9 | 416.7 | 406.6 | 411.1 | 420.1 | 374.5 | 385.9
1272 | 1151 | 470.9 | 416.7 | 406.7 | 411.2 | 420.1 | 374.6 | 385.8
1273 | 1152 | 471 | 416.8 | 406.7 | 411.2 | 420.1 | 374.6 | 385.8
1274 | 1153 | 471.1 | 416.8 | 406.8 | 411.2 | 420.2 | 374.6 | 385.8
1275 | 1154 | 471.3 | 416.9 | 406.8 | 411.3 | 420.2 | 374.7 | 385.8
1276 | 1155 | 471.4 | 416.9 | 406.9 | 411.3 | 420.3 | 374.8 | 385.6
1277 | 1156 | 471.3 | 417 | 406.9 | 411.4 | 420.3 | 374.8 | 385.4
1278 | 1157 | 471.4 | 417 | 407 | 411.4 | 420.3 | 374.9 | 385.4
1279 | 1158 | 471.4 | 417 | 407.1 | 411.5 | 420.3 | 375 | 385.4
1280 | 1159 | 471.4 | 417.1 | 407.1 | 411.5 | 420.3 | 375.1 | 385.5
1281 | 1160 | 471.7 | 417.1 | 407.2 | 411.5 | 420.3 | 375 | 385.5
1282 | 1161 | 471.8 | 417.1 | 407.3 | 411.6 | 420.3 | 375 | 385.4
1283 | 1162 | 472.1 | 417.2 | 407.3 | 411.6 | 420.3 | 375.1 | 385.4
1284 | 1163 | 472.1 | 417.2 | 407.4 | 411.7 | 420.4 | 375.2 | 385.4
1285 | 1164 | 472 | 417.3 | 407.4 | 411.7 | 420.5 | 375.2 | 385.4
1286 | 1165 | 471.8 | 417.3 | 407.5 | 411.7 | 420.5 | 375.2 | 385.5
1287 | 1166 | 471.8 | 417.4 | 407.5 | 411.8 | 420.6 | 375.2 | 385.6
1288 | 1167 | 471.8 | 417.4 | 407.5 | 411.8 | 420.7 | 375.3 | 385.6
1289 | 1168 | 471.7 | 417.5 | 407.5 | 411.9 | 420.8 | 375.1 | 385.7
1290 | 1169 | 471.5 | 417.6 | 407.5 | 411.9 | 420.8 | 375.2 | 385.7
1291 | 1170 | 471.5 | 417.6 | 407.5 | 412 | 420.9 | 375.2 | 385.7
1292 | 1171 | 471.6 | 417.7 | 407.6 | 412 | 421 | 375.3 | 385.8
1293 | 1172 | 471.5 | 417.8 | 407.6 | 412.1 | 421.1 | 375.2 | 385.9
1294 | 1173 | 471.4 | 417.8 | 407.7 | 412.1 | 421.1 | 375.2 | 385.9
1295 | 1174 | 471.6 | 417.8 | 407.8 | 412.2 | 421 | 375.1 | 386
1296 | 1175 | 471.8 | 417.8 | 407.8 | 412.2 | 421 | 374.9 | 386.2
1297 | 1176 | 472 | 417.8 | 407.9 | 412.2 | 420.9 | 374.9 | 386.3
1298 | 1177 | 472.1 | 417.9 | 408 | 412.2 | 420.9 | 375 | 386.3
1299 | 1178 | 472.1 | 417.9 | 408.1 | 412.3 | 421 | 375.1 | 386.2
1300 | 1179 | 472.2 | 417.9 | 408.1 | 412.3 | 421.1 | 375 | 386.3
1301 | 1180 | 472.2 | 418 | 408.1 | 412.4 | 421.1 | 375 | 386.3
1302 | 1181 | 472.1 | 418 | 408.1 | 412.4 | 421.2 | 375.1 | 386.3
1303 | 1182 | 471.9 | 418.1 | 408.2 | 412.5 | 421.2 | 375 | 386.4
1304 | 1183 | 471.7 | 418.2 | 408.2 | 412.5 | 421.3 | 374.8 | 386.4
1305 | 1184 | 471.6 | 418.2 | 408.2 | 412.6 | 421.4 | 374.9 | 386.3
1306 | 1185 | 471.5 | 418.2 | 408.3 | 412.6 | 421.4 | 374.9 | 386.2
1307 | 1186 | 471.2 | 418.2 | 408.3 | 412.6 | 421.4 | 375 | 386.2
1308 | 1187 | 471.2 | 418.3 | 408.4 | 412.7 | 421.4 | 374.9 | 386.3
1309 | 1188 | 471.3 | 418.3 | 408.4 | 412.7 | 421.4 | 375 | 386.2
1310 | 1189 | 471.4 | 418.4 | 408.5 | 412.7 | 421.5 | 375 | 386.2
1311 | 1190 | 471.4 | 418.4 | 408.6 | 412.8 | 421.5 | 375 | 386.3
1312 | 1191 | 471.3 | 418.4 | 408.6 | 412.8 | 421.5 | 374.9 | 386.3
1313 | 1192 | 471.1 | 418.5 | 408.7 | 412.9 | 421.5 | 375 | 386.3
1314 | 1193 | 471.1 | 418.5 | 408.7 | 412.9 | 421.6 | 375.1 | 386.3
1315 | 1194 | 471.1 | 418.5 | 408.7 | 413 | 421.6 | 375.3 | 386.3
1316 | 1195 | 471.1 | 418.6 | 408.8 | 413 | 421.7 | 375.3 | 386.3
1317 | 1196 | 471.1 | 418.6 | 408.7 | 413.1 | 421.8 | 375.4 | 386.3
1318 | 1197 | 471.3 | 418.7 | 408.8 | 413.1 | 421.9 | 375.4 | 386.3
1319 | 1198 | 471.4 | 418.7 | 408.8 | 413.2 | 421.9 | 375.2 | 386.3
1320 | 1199 | 471.3 | 418.8 | 408.9 | 413.2 | 421.9 | 375.3 | 386.3
1321 | 1200 | 471.3 | 418.8 | 409 | 413.2 | 421.9 | 375.3 | 386.4
1322 | 1201 | 471.2 | 418.8 | 409.1 | 413.2 | 421.8 | 375.4 | 386.5
1323 | 1202 | 471.1 | 418.8 | 409.1 | 413.3 | 421.9 | 375.4 | 386.6
1324 | 1203 | 471 | 418.8 | 409.1 | 413.3 | 421.9 | 375.4 | 386.6
1325 | 1204 | 470.9 | 418.9 | 409.2 | 413.4 | 422 | 375.5 | 386.6
1326 | 1205 | 471 | 418.9 | 409.2 | 413.4 | 422.1 | 375.5 | 386.5
1327 | 1206 | 471 | 418.9 | 409.2 | 413.5 | 422.1 | 375.4 | 386.5
1328 | 1207 | 471 | 419 | 409.3 | 413.5 | 422.1 | 375.5 | 386.5
1329 | 1208 | 471 | 419 | 409.3 | 413.5 | 422.2 | 375.5 | 386.5
1330 | 1209 | 471.1 | 419 | 409.4 | 413.6 | 422.2 | 375.5 | 386.5
1331 | 1210 | 471 | 419.1 | 409.5 | 413.6 | 422.2 | 375.5 | 386.6
1332 | 1211 | 470.9 | 419.1 | 409.5 | 413.7 | 422.2 | 375.6 | 386.5
1333 | 1212 | 470.9 | 419.2 | 409.6 | 413.7 | 422.3 | 375.6 | 386.6
1334 | 1213 | 470.9 | 419.2 | 409.6 | 413.7 | 422.3 | 375.7 | 386.6
1335 | 1214 | 470.9 | 419.3 | 409.6 | 413.8 | 422.4 | 375.6 | 386.5
1336 | 1215 | 470.8 | 419.3 | 409.7 | 413.8 | 422.4 | 375.6 | 386.5
1337 | 1216 | 470.9 | 419.3 | 409.7 | 413.8 | 422.4 | 375.7 | 386.3
1338 | 1217 | 471 | 419.3 | 409.8 | 413.9 | 422.4 | 375.7 | 386.2
1339 | 1218 | 471.1 | 419.4 | 409.8 | 413.9 | 422.4 | 375.7 | 386.2
1340 | 1219 | 471.1 | 419.4 | 409.9 | 413.9 | 422.4 | 375.8 | 386.2
1341 | 1220 | 471.1 | 419.4 | 410 | 414 | 422.4 | 375.7 | 386.3
1342 | 1221 | 471.1 | 419.4 | 410 | 414 | 422.4 | 375.6 | 386.3
1343 | 1222 | 471.1 | 419.4 | 410.1 | 414 | 422.4 | 375.7 | 386.3
1344 | 1223 | 471.1 | 419.4 | 410.1 | 414 | 422.4 | 375.7 | 386.2
1345 | 1224 | 471 | 419.4 | 410.1 | 414.1 | 422.5 | 375.9 | 386.2
1346 | 1225 | 471.1 | 419.5 | 410.1 | 414.1 | 422.5 | 375.9 | 386.2
1347 | 1226 | 471.1 | 419.5 | 410.2 | 414.2 | 422.6 | 375.7 | 386.2
1348 | 1227 | 471 | 419.6 | 410.2 | 414.2 | 422.7 | 375.6 | 386.2
1349 | 1228 | 470.8 | 419.6 | 410.3 | 414.2 | 422.7 | 375.6 | 386.3
1350 | 1229 | 470.7 | 419.6 | 410.3 | 414.3 | 422.7 | 375.6 | 386.4
1351 | 1230 | 470.8 | 419.7 | 410.3 | 414.3 | 422.8 | 375.6 | 386.5
1352 | 1231 | 470.7 | 419.7 | 410.3 | 414.3 | 422.8 | 375.6 | 386.6
1353 | 1232 | 470.6 | 419.7 | 410.4 | 414.4 | 422.9 | 375.5 | 386.6
1354 | 1233 | 470.6 | 419.7 | 410.4 | 414.4 | 422.9 | 375.5 | 386.6
1355 | 1234 | 470.5 | 419.8 | 410.4 | 414.5 | 423 | 375.6 | 386.6
1356 | 1235 | 470.5 | 419.8 | 410.4 | 414.5 | 423.1 | 375.7 | 386.5
1357 | 1236 | 470.4 | 419.8 | 410.4 | 414.5 | 423.2 | 375.8 | 386.2
1358 | 1237 | 470.4 | 419.8 | 410.4 | 414.6 | 423.2 | 375.7 | 386
1359 | 1238 | 470.4 | 419.8 | 410.5 | 414.6 | 423.2 | 375.9 | 386
1360 | 1239 | 470.4 | 419.8 | 410.6 | 414.6 | 423.2 | 375.8 | 386
1361 | 1240 | 470.5 | 419.8 | 410.6 | 414.6 | 423.2 | 375.9 | 386
1362 | 1241 | 470.7 | 419.9 | 410.6 | 414.7 | 423.3 | 375.9 | 386.1
1363 | 1242 | 470.7 | 419.9 | 410.6 | 414.7 | 423.3 | 375.8 | 386.2
1364 | 1243 | 470.8 | 419.9 | 410.7 | 414.7 | 423.4 | 375.8 | 386.3
1365 | 1244 | 470.8 | 420 | 410.7 | 414.8 | 423.4 | 375.8 | 386.4
1366 | 1245 | 470.9 | 420 | 410.8 | 414.8 | 423.4 | 375.8 | 386.4
1367 | 1246 | 471.1 | 420 | 410.8 | 414.8 | 423.4 | 375.8 | 386.5
1368 | 1247 | 471.2 | 420 | 410.9 | 414.8 | 423.4 | 375.9 | 386.5
1369 | 1248 | 471.4 | 420 | 410.9 | 414.9 | 423.4 | 376 | 386.5
1370 | 1249 | 471.5 | 420.1 | 410.9 | 414.9 | 423.5 | 376 | 386.6
1371 | 1250 | 471.5 | 420.1 | 411 | 414.9 | 423.5 | 375.9 | 386.6
1372 | 1251 | 471.7 | 420.1 | 411.1 | 414.9 | 423.5 | 376 | 386.6
1373 | 1252 | 471.9 | 420.1 | 411.1 | 415 | 423.5 | 376 | 386.6
1374 | 1253 | 472 | 420.1 | 411.2 | 415 | 423.6 | 376.1 | 386.7
1375 | 1254 | 471.9 | 420.1 | 411.2 | 415 | 423.6 | 376 | 386.7
1376 | 1255 | 471.9 | 420.2 | 411.3 | 415.1 | 423.6 | 376 | 386.7
1377 | 1256 | 472.1 | 420.2 | 411.3 | 415.1 | 423.7 | 376.2 | 386.8
1378 | 1257 | 472.2 | 420.2 | 411.3 | 415.1 | 423.7 | 376.3 | 386.7
1379 | 1258 | 472.1 | 420.2 | 411.4 | 415.1 | 423.8 | 376.4 | 386.5
1380 | 1259 | 472.1 | 420.2 | 411.4 | 415.1 | 423.8 | 376.3 | 386.5
1381 | 1260 | 472 | 420.3 | 411.4 | 415.2 | 423.8 | 376.3 | 386.6
1382 | 1261 | 471.9 | 420.3 | 411.5 | 415.2 | 423.9 | 376.2 | 386.7
1383 | 1262 | 471.9 | 420.3 | 411.5 | 415.2 | 423.9 | 376.2 | 386.8
1384 | 1263 | 471.8 | 420.3 | 411.6 | 415.2 | 423.8 | 376.3 | 386.9
1385 | 1264 | 471.8 | 420.3 | 411.7 | 415.2 | 423.8 | 376.2 | 386.9
1386 | 1265 | 471.8 | 420.4 | 411.7 | 415.3 | 423.9 | 376.3 | 387
1387 | 1266 | 471.8 | 420.4 | 411.7 | 415.3 | 424 | 376 | 387
1388 | 1267 | 471.7 | 420.5 | 411.7 | 415.4 | 424 | 376 | 387
1389 | 1268 | 471.5 | 420.5 | 411.7 | 415.4 | 424.1 | 376 | 387
1390 | 1269 | 471.5 | 420.5 | 411.8 | 415.4 | 424.1 | 376.1 | 387
1391 | 1270 | 471.4 | 420.6 | 411.8 | 415.4 | 424.1 | 376.2 | 387
1392 | 1271 | 471.4 | 420.6 | 411.8 | 415.4 | 424.2 | 376.2 | 387
1393 | 1272 | 471.4 | 420.6 | 411.9 | 415.5 | 424.2 | 376.3 | 387.1
1394 | 1273 | 471.2 | 420.7 | 411.9 | 415.5 | 424.3 | 376.3 | 387.1
1395 | 1274 | 471.1 | 420.7 | 411.9 | 415.5 | 424.3 | 376.1 | 387.1
1396 | 1275 | 471 | 420.7 | 412 | 415.6 | 424.4 | 376.2 | 387.1
1397 | 1276 | 471 | 420.8 | 412 | 415.6 | 424.4 | 376.1 | 387.1
1398 | 1277 | 470.9 | 420.8 | 412 | 415.6 | 424.5 | 376 | 387.1
1399 | 1278 | 470.7 | 420.8 | 412.1 | 415.6 | 424.5 | 376 | 387.1
1400 | 1279 | 470.7 | 420.8 | 412.1 | 415.7 | 424.5 | 376.1 | 387
1401 | 1280 | 470.7 | 420.9 | 412.2 | 415.7 | 424.5 | 376.1 | 387
1402 | 1281 | 470.6 | 420.9 | 412.2 | 415.7 | 424.6 | 376.1 | 387
1403 | 1282 | 470.5 | 420.9 | 412.2 | 415.8 | 424.6 | 376.2 | 386.9
1404 | 1283 | 470.3 | 421 | 412.3 | 415.8 | 424.6 | 376.1 | 386.9
1405 | 1284 | 470.2 | 421 | 412.3 | 415.8 | 424.7 | 376 | 386.8
1406 | 1285 | 470.1 | 421.1 | 412.3 | 415.9 | 424.7 | 375.9 | 386.7
1407 | 1286 | 470.1 | 421.1 | 412.3 | 415.9 | 424.8 | 375.8 | 386.6
1408 | 1287 | 469.9 | 421.1 | 412.3 | 415.9 | 424.8 | 375.8 | 386.5
1409 | 1288 | 469.9 | 421.2 | 412.3 | 416 | 424.8 | 375.7 | 386.4
1410 | 1289 | 469.8 | 421.2 | 412.3 | 416 | 424.9 | 375.6 | 386.3
1411 | 1290 | 469.8 | 421.2 | 412.4 | 416 | 424.9 | 375.6 | 386.3
1412 | 1291 | 469.9 | 421.3 | 412.4 | 416 | 424.9 | 375.7 | 386.3
1413 | 1292 | 469.9 | 421.3 | 412.5 | 416.1 | 424.9 | 375.7 | 386.4
1414 | 1293 | 470.1 | 421.3 | 412.5 | 416.1 | 424.9 | 375.7 | 386.4
1415 | 1294 | 470.1 | 421.4 | 412.6 | 416.1 | 424.9 | 375.6 | 386.2
1416 | 1295 | 470.2 | 421.4 | 412.6 | 416.1 | 424.9 | 375.6 | 385.9
1417 | 1296 | 470.2 | 421.4 | 412.6 | 416.1 | 424.9 | 375.7 | 385.9
1418 | 1297 | 470.3 | 421.5 | 412.6 | 416.2 | 424.9 | 375.7 | 386
1419 | 1298 | 470.4 | 421.5 | 412.7 | 416.2 | 424.9 | 375.8 | 385.9
1420 | 1299 | 470.4 | 421.5 | 412.7 | 416.2 | 424.9 | 375.8 | 386
1421 | 1300 | 470.4 | 421.6 | 412.8 | 416.2 | 424.9 | 375.7 | 385.9
1422 | 1301 | 470.5 | 421.7 | 412.7 | 416.3 | 425 | 375.8 | 385.9
1423 | 1302 | 470.6 | 421.7 | 412.8 | 416.3 | 425 | 375.8 | 385.9
1424 | 1303 | 470.7 | 421.8 | 412.8 | 416.3 | 425 | 375.9 | 385.9
1425 | 1304 | 470.6 | 421.8 | 412.8 | 416.3 | 425 | 375.7 | 386
1426 | 1305 | 470.6 | 421.8 | 412.9 | 416.3 | 425 | 375.8 | 386
1427 | 1306 | 470.6 | 421.9 | 412.9 | 416.4 | 425 | 375.9 | 386
1428 | 1307 | 470.7 | 421.9 | 412.9 | 416.4 | 425.1 | 376 | 386
1429 | 1308 | 470.7 | 421.9 | 412.9 | 416.4 | 425.1 | 376 | 385.9
1430 | 1309 | 470.9 | 422 | 412.9 | 416.4 | 425.1 | 376.1 | 385.9
1431 | 1310 | 471 | 422 | 413 | 416.5 | 425.1 | 376.2 | 385.9
1432 | 1311 | 471.3 | 422 | 413 | 416.5 | 425.1 | 376.2 | 385.9
1433 | 1312 | 471.3 | 422.1 | 413 | 416.5 | 425.1 | 376 | 385.8
1434 | 1313 | 471.3 | 422.1 | 413.1 | 416.5 | 425.1 | 375.8 | 385.9
1435 | 1314 | 471.2 | 422.1 | 413.1 | 416.5 | 425.2 | 375.8 | 385.9
1436 | 1315 | 471.1 | 422.1 | 413.1 | 416.5 | 425.2 | 375.8 | 385.9
1437 | 1316 | 471.2 | 422.2 | 413.1 | 416.6 | 425.2 | 375.9 | 385.9
1438 | 1317 | 471.1 | 422.2 | 413.1 | 416.6 | 425.2 | 375.9 | 386
1439 | 1318 | 471.1 | 422.2 | 413.1 | 416.6 | 425.2 | 375.9 | 385.9
1440 | 1319 | 471.2 | 422.2 | 413.2 | 416.6 | 425.2 | 375.9 | 385.9
1441 | 1320 | 471.3 | 422.3 | 413.1 | 416.6 | 425.3 | 375.9 | 385.9
1442 | 1321 | 471.3 | 422.3 | 413.1 | 416.7 | 425.3 | 375.9 | 385.9
1443 | 1322 | 471.3 | 422.3 | 413.1 | 416.7 | 425.3 | 376 | 386
1444 | 1323 | 471.4 | 422.3 | 413.1 | 416.7 | 425.3 | 376.1 | 386
1445 | 1324 | 471.4 | 422.4 | 413.1 | 416.7 | 425.4 | 376.2 | 386
1446 | 1325 | 471.3 | 422.4 | 413.1 | 416.8 | 425.5 | 376.3 | 385.8
1447 | 1326 | 471.4 | 422.4 | 413.1 | 416.8 | 425.5 | 376.3 | 385.8
1448 | 1327 | 471.4 | 422.5 | 413.1 | 416.8 | 425.5 | 376.4 | 385.7
1449 | 1328 | 471.3 | 422.5 | 413.1 | 416.9 | 425.5 | 376.4 | 385.7
1450 | 1329 | 471.4 | 422.5 | 413.1 | 416.9 | 425.6 | 376.3 | 385.7
1451 | 1330 | 471.5 | 422.5 | 413.1 | 416.9 | 425.6 | 376.4 | 385.8
1452 | 1331 | 471.6 | 422.5 | 413.1 | 416.9 | 425.6 | 376.5 | 385.8
1453 | 1332 | 471.6 | 422.5 | 413.1 | 417 | 425.6 | 376.5 | 385.8
1454 | 1333 | 471.5 | 422.5 | 413.1 | 417 | 425.6 | 376.5 | 385.8
1455 | 1334 | 471.5 | 422.6 | 413.1 | 417 | 425.6 | 376.6 | 385.8
1456 | 1335 | 471.4 | 422.6 | 413.1 | 417 | 425.7 | 376.5 | 385.8
1457 | 1336 | 471.3 | 422.6 | 413.1 | 417.1 | 425.7 | 376.4 | 385.7
1458 | 1337 | 471.3 | 422.6 | 413.1 | 417.1 | 425.7 | 376.4 | 385.8
1459 | 1338 | 471.4 | 422.7 | 413.1 | 417.1 | 425.7 | 376.4 | 385.7
1460 | 1339 | 471.4 | 422.7 | 413 | 417.2 | 425.8 | 376.5 | 385.7
1461 | 1340 | 471.5 | 422.7 | 413.1 | 417.2 | 425.8 | 376.5 | 385.7
1462 | 1341 | 471.6 | 422.7 | 413.1 | 417.2 | 425.8 | 376.3 | 385.7
1463 | 1342 | 471.7 | 422.8 | 413.1 | 417.2 | 425.8 | 376.3 | 385.8
1464 | 1343 | 471.7 | 422.8 | 413 | 417.3 | 425.9 | 376.3 | 385.8
1465 | 1344 | 471.7 | 422.8 | 413 | 417.3 | 425.9 | 376.3 | 385.8
1466 | 1345 | 471.5 | 422.8 | 413 | 417.3 | 425.9 | 376.3 | 385.6
1467 | 1346 | 471.4 | 422.9 | 412.9 | 417.4 | 426 | 376.3 | 385.6
1468 | 1347 | 471.4 | 422.9 | 412.9 | 417.4 | 426 | 376.4 | 385.7
1469 | 1348 | 471.4 | 423 | 412.9 | 417.4 | 426 | 376.5 | 385.8
1470 | 1349 | 471.3 | 423 | 412.9 | 417.5 | 426.1 | 376.6 | 385.9
1471 | 1350 | 471.1 | 423 | 412.8 | 417.5 | 426.1 | 376.6 | 385.9
1472 | 1351 | 471.2 | 423.1 | 412.8 | 417.5 | 426.2 | 376.6 | 385.9
1473 | 1352 | 471.3 | 423.1 | 412.7 | 417.6 | 426.3 | 376.7 | 386
1474 | 1353 | 471.2 | 423.1 | 412.7 | 417.6 | 426.3 | 376.6 | 386
1475 | 1354 | 471.2 | 423.2 | 412.7 | 417.6 | 426.3 | 376.6 | 386
1476 | 1355 | 471 | 423.2 | 412.6 | 417.7 | 426.4 | 376.6 | 386
1477 | 1356 | 470.8 | 423.3 | 412.6 | 417.7 | 426.4 | 376.6 | 386.1 | Time of first failure
1478 | 1357 | 470.9 | 423.3 | 412.5 | 417.7 | 426.5 | 376.7 | 386.1 | 1356 | 0
1479 | 1358 | 470.9 | 423.3 | 412.5 | 417.8 | 426.6 | 376.7 | 386 | 1356 | 900
1480 | 1359 | 470.8 | 423.4 | 412.4 | 417.8 | 426.6 | 376.7 | 386
1481 | 1360 | 470.8 | 423.4 | 412.4 | 417.8 | 426.6 | 376.6 | 386
1482 | 1361 | 470.9 | 423.4 | 412.4 | 417.9 | 426.6 | 376.7 | 386
1483 | 1362 | 471 | 423.5 | 412.4 | 417.9 | 426.6 | 376.8 | 386
1484 | 1363 | 470.9 | 423.5 | 412.4 | 417.9 | 426.6 | 376.8 | 385.9
1485 | 1364 | 470.7 | 423.5 | 412.4 | 417.9 | 426.6 | 376.7 | 385.8
1486 | 1365 | 470.7 | 423.5 | 412.4 | 418 | 426.6 | 376.8 | 385.8
1487 | 1366 | 470.7 | 423.6 | 412.4 | 418 | 426.6 | 376.7 | 385.7
1488 | 1367 | 470.8 | 423.7 | 412.4 | 418 | 426.7 | 376.6 | 385.7
1489 | 1368 | 470.9 | 423.7 | 412.3 | 418.1 | 426.7 | 376.7 | 385.8
1490 | 1369 | 470.8 | 423.8 | 412.3 | 418.1 | 426.7 | 376.8 | 385.9
1491 | 1370 | 470.9 | 423.9 | 412.2 | 418.2 | 426.7 | 376.7 | 385.9
1492 | 1371 | 470.9 | 423.9 | 412.2 | 418.2 | 426.7 | 376.7 | 385.9
1493 | 1372 | 470.9 | 423.9 | 412.3 | 418.2 | 426.7 | 376.8 | 386
1494 | 1373 | 471 | 423.9 | 412.3 | 418.2 | 426.6 | 376.8 | 386.1
1495 | 1374 | 471 | 423.9 | 412.2 | 418.3 | 426.7 | 376.7 | 386.1
1496 | 1375 | 471.2 | 424 | 412.2 | 418.3 | 426.7 | 376.8 | 386.2
1497 | 1376 | 471.3 | 424 | 412.2 | 418.3 | 426.7 | 376.9 | 386.2
1498 | 1377 | 471.3 | 424 | 412.2 | 418.3 | 426.6 | 376.9 | 386.2
1499 | 1378 | 471.1 | 424 | 412.2 | 418.3 | 426.6 | 376.9 | 386.2
1500 | 1379 | 471.1 | 424.1 | 412.2 | 418.4 | 426.6 | 377 | 386.3
1501 | 1380 | 471.2 | 424.1 | 412.1 | 418.4 | 426.6 | 377 | 386.3
1502 | 1381 | 471.2 | 424.1 | 412.1 | 418.4 | 426.6 | 376.9 | 386.3
1503 | 1382 | 471.1 | 424.1 | 412.1 | 418.4 | 426.7 | 376.9 | 386.3
1504 | 1383 | 471.1 | 424.1 | 412.1 | 418.5 | 426.6 | 377.1 | 386.3
1505 | 1384 | 471.3 | 424.2 | 412.1 | 418.5 | 426.7 | 377.2 | 386.4
1506 | 1385 | 471.4 | 424.2 | 412.1 | 418.5 | 426.6 | 377.3 | 386.4
1507 | 1386 | 471.3 | 424.2 | 412.1 | 418.5 | 426.7 | 377.3 | 386.5
1508 | 1387 | 471.1 | 424.3 | 412.1 | 418.6 | 426.7 | 377.3 | 386.5
1509 | 1388 | 471 | 424.3 | 412.1 | 418.6 | 426.7 | 377.3 | 386.5
1510 | 1389 | 470.9 | 424.3 | 412.1 | 418.6 | 426.7 | 377.5 | 386.5
1511 | 1390 | 470.8 | 424.4 | 412.1 | 418.6 | 426.8 | 377.2 | 386.6
1512 | 1391 | 470.9 | 424.4 | 412 | 418.7 | 426.9 | 377.1 | 386.5
1513 | 1392 | 470.8 | 424.5 | 412 | 418.7 | 427 | 377.2 | 386.5
1514 | 1393 | 470.7 | 424.5 | 412 | 418.7 | 427 | 377.3 | 386.5
1515 | 1394 | 470.4 | 424.5 | 412 | 418.8 | 427 | 377.3 | 386.5
1516 | 1395 | 470.5 | 424.5 | 412 | 418.8 | 427.1 | 377.4 | 386.5
1517 | 1396 | 470.5 | 424.5 | 412 | 418.8 | 427.1 | 377.5 | 386.5
1518 | 1397 | 470.5 | 424.5 | 412 | 418.8 | 427.1 | 377.5 | 386.5
1519 | 1398 | 470.5 | 424.5 | 412 | 418.9 | 427.1 | 377.6 | 386.6
1520 | 1399 | 470.6 | 424.5 | 412 | 418.9 | 427.1 | 377.5 | 386.6
1521 | 1400 | 470.7 | 424.6 | 412 | 418.9 | 427.1 | 377.5 | 386.7
1522 | 1401 | 470.8 | 424.6 | 412 | 418.9 | 427.2 | 377.6 | 386.7
1523 | 1402 | 470.9 | 424.7 | 411.9 | 419 | 427.2 | 377.6 | 386.7
1524 | 1403 | 470.8 | 424.7 | 412 | 419 | 427.2 | 377.7 | 386.8
1525 | 1404 | 470.9 | 424.7 | 412 | 419 | 427.2 | 377.7 | 386.8
1526 | 1405 | 470.8 | 424.7 | 412.1 | 419 | 427.3 | 377.7 | 386.8
1527 | 1406 | 470.8 | 424.7 | 412.1 | 419.1 | 427.3 | 377.6 | 386.9
1528 | 1407 | 470.8 | 424.7 | 412.2 | 419.1 | 427.3 | 377.7 | 386.9
1529 | 1408 | 470.8 | 424.8 | 412.3 | 419.1 | 427.4 | 377.7 | 387
1530 | 1409 | 470.9 | 424.8 | 412.4 | 419.1 | 427.4 | 377.6 | 387
1531 | 1410 | 471.1 | 424.8 | 412.5 | 419.1 | 427.5 | 377.4 | 387
1532 | 1411 | 471.4 | 424.8 | 412.6 | 419.2 | 427.5 | 377.5 | 387
1533 | 1412 | 471.5 | 424.8 | 412.7 | 419.2 | 427.5 | 377.5 | 387
1534 | 1413 | 471.6 | 424.9 | 412.8 | 419.2 | 427.5 | 377.6 | 387
1535 | 1414 | 471.6 | 424.8 | 412.9 | 419.2 | 427.5 | 377.8 | 387.1
1536 | 1415 | 471.6 | 424.8 | 412.9 | 419.3 | 427.6 | 377.8 | 387.1
1537 | 1416 | 471.6 | 424.9 | 413 | 419.3 | 427.7 | 377.8 | 387.1
1538 | 1417 | 471.6 | 424.8 | 413.1 | 419.3 | 427.7 | 377.9 | 387
1539 | 1418 | 471.7 | 424.8 | 413.1 | 419.3 | 427.8 | 377.9 | 387
1540 | 1419 | 471.6 | 424.8 | 413.1 | 419.4 | 427.9 | 377.9 | 387.1
1541 | 1420 | 471.6 | 424.9 | 413.2 | 419.4 | 427.9 | 377.9 | 387
1542 | 1421 | 471.5 | 424.9 | 413.2 | 419.4 | 427.9 | 377.9 | 387
1543 | 1422 | 471.4 | 424.9 | 413.2 | 419.5 | 428 | 377.9 | 387
1544 | 1423 | 471.3 | 424.9 | 413.2 | 419.5 | 428.1 | 377.9 | 387
1545 | 1424 | 471.2 | 425 | 413.3 | 419.5 | 428.1 | 378 | 387
1546 | 1425 | 471.3 | 424.9 | 413.3 | 419.5 | 428.1 | 378.1 | 387
1547 | 1426 | 471.4 | 424.9 | 413.4 | 419.5 | 428.1 | 378.1 | 387.1
1548 | 1427 | 471.3 | 424.9 | 413.5 | 419.6 | 428.1 | 378.1 | 387.1
1549 | 1428 | 471.3 | 424.9 | 413.7 | 419.6 | 428.1 | 378.1 | 387
1550 | 1429 | 471.2 | 424.9 | 413.8 | 419.6 | 428.1 | 378.1 | 387
1551 | 1430 | 471.2 | 425 | 414 | 419.7 | 428.1 | 378.1 | 387
1552 | 1431 | 471.3 | 425 | 414.1 | 419.7 | 428.1 | 378.1 | 387
1553 | 1432 | 471.4 | 425 | 414.1 | 419.7 | 428.2 | 378.2 | 387
1554 | 1433 | 471.5 | 425 | 414.2 | 419.8 | 428.2 | 378.2 | 386.9
1555 | 1434 | 471.6 | 425 | 414.2 | 419.8 | 428.2 | 378.2 | 386.8
1556 | 1435 | 471.5 | 425 | 414.2 | 419.8 | 428.2 | 378.3 | 386.9
1557 | 1436 | 471.5 | 425 | 414.3 | 419.8 | 428.2 | 378.2 | 386.9
1558 | 1437 | 471.5 | 425 | 414.3 | 419.8 | 428.3 | 378.3 | 386.9
1559 | 1438 | 471.5 | 425 | 414.3 | 419.9 | 428.4 | 378.4 | 386.9
1560 | 1439 | 471.3 | 425 | 414.4 | 419.9 | 428.4 | 378.4 | 386.9
1561 | 1440 | 471.4 | 425 | 414.4 | 419.9 | 428.4 | 378.3 | 387
1562 | 1441 | 471.6 | 425.1 | 414.5 | 419.9 | 428.4 | 378.3 | 387
1563 | 1442 | 471.6 | 425.1 | 414.5 | 419.9 | 428.4 | 378.5 | 387
1564 | 1443 | 471.5 | 425.1 | 414.5 | 419.9 | 428.4 | 378.4 | 387
1565 | 1444 | 471.4 | 425.1 | 414.5 | 420 | 428.4 | 378.3 | 387.1
1566 | 1445 | 471.2 | 425.1 | 414.5 | 420 | 428.5 | 378.4 | 387.1
1567 | 1446 | 471 | 425.2 | 414.5 | 420.1 | 428.6 | 378.4 | 387.2
1568 | 1447 | 470.9 | 425.2 | 414.4 | 420.1 | 428.7 | 378.4 | 387.3
1569 | 1448 | 470.8 | 425.2 | 414.4 | 420.2 | 428.8 | 378.3 | 387.3
1570 | 1449 | 470.8 | 425.2 | 414.5 | 420.2 | 428.8 | 378.2 | 387.2
1571 | 1450 | 471 | 425.1 | 414.5 | 420.2 | 428.9 | 378.4 | 387.3
1572 | 1451 | 471.3 | 425 | 414.6 | 420.2 | 428.9 | 378.8 | 387.5
1573 | 1452 | 471.8 | 424.9 | 414.8 | 420.2 | 428.7 | 379.1 | 387.6
1574 | 1453 | 472.4 | 424.8 | 415 | 420.2 | 428.6 | 379.6 | 387.9
1575 | 1454 | 473.2 | 424.8 | 415 | 420.2 | 428.6 | 380.2 | 388.3
1576 | 1455 | 474.1 | 424.6 | 415 | 420.2 | 428.5 | 380.8 | 388.8
1577 | 1456 | 475.4 | 424.5 | 414.9 | 420.1 | 428.3 | 381.3 | 389.5
1578 | 1457 | 476.7 | 424.6 | 414.8 | 419.9 | 428.3 | 382.1 | 390.4
1579 | 1458 | 478.4 | 424.5 | 414.9 | 419.8 | 428.2 | 382.9 | 391.5
1580 | 1459 | 480.1 | 424.5 | 414.8 | 419.8 | 428.2 | 383.7 | 392.7
1581 | 1460 | 481.8 | 424.6 | 414.7 | 419.9 | 428.3 | 384.7 | 394.1
1582 | 1461 | 483.4 | 424.7 | 414.8 | 420 | 428.6 | 385.4 | 395.6
1583 | 1462 | 484.9 | 424.9 | 414.8 | 420.1 | 429 | 386.5 | 397.3
1584 | 1463 | 486.3 | 425.2 | 415 | 420.3 | 429.6 | 387.4 | 398.9
1585 | 1464 | 487.6 | 425.6 | 415.2 | 420.4 | 430.4 | 388.5 | 400.9
1586 | 1465 | 488.8 | 426 | 415.5 | 420.5 | 431.4 | 390.1 | 402.7
1587 | 1466 | 489.7 | 426.8 | 415.9 | 420.7 | 432.5 | 392.7 | 404.4
1588 | 1467 | 490.3 | 427.7 | 416.5 | 421 | 433.7 | 402.1 | 406.1
1589 | 1468 | 491 | 428.7 | 417.4 | 421.3 | 435.1 | 416.3 | 407.9
1590 | 1469 | 491.2 | 429.6 | 418.4 | 421.6 | 436.5 | 427.9 | 409.7
1591 | 1470 | 491.5 | 430.2 | 419.6 | 422 | 438 | 439.6 | 411.8
1592 | 1471 | 491.8 | 430.6 | 420.8 | 422.4 | 439.5 | 449.6 | 413.9
1593 | 1472 | 491.9 | 431.3 | 422.3 | 422.8 | 441.1 | 460 | 415.9
1594 | 1473 | 491.7 | 432.1 | 423.9 | 423.2 | 442.7 | 469.8 | 417.7
1595 | 1474 | 491.4 | 433 | 425.4 | 423.6 | 444.4 | 477.9 | 419.1
1596 | 1475 | 491.2 | 433.9 | 426.8 | 424.1 | 446.1 | 484.3 | 421
1597 | 1476 | 490.9 | 435.1 | 428.2 | 424.7 | 447.8 | 492.2 | 424.3
1598 | 1477 | 490.5 | 435.9 | 429.5 | 425.3 | 449.3 | 499.1 | 427.6
1599 | 1478 | 490.1 | 436.5 | 430.8 | 425.9 | 450.7 | 506.5 | 432.8
1600 | 1479 | 489.6 | 437.1 | 431.9 | 426.5 | 452.1 | 511.9 | 436.5
1601 | 1480 | 489.1 | 437.8 | 432.8 | 427.2 | 453.6 | 517.7 | 443
1602 | 1481 | 488.6 | 438.4 | 434 | 427.8 | 455.1 | 522.6 | 449.9
1603 | 1482 | 488 | 439.1 | 435.6 | 428.5 | 456.7 | 527.5 | 456.6
1604 | 1483 | 487.3 | 439.7 | 437.1 | 429.2 | 458.3 | 532.7 | 460.8
1605 | 1484 | 486.8 | 440.4 | 438.2 | 430 | 459.7 | 537.1 | 465.7
1606 | 1485 | 486.2 | 441.2 | 439.6 | 430.9 | 461.1 | 539 | 471.2
1607 | 1486 | 485.6 | 442.2 | 441.4 | 431.8 | 462.3 | 540 | 474.5
1608 | 1487 | 485 | 443 | 443.3 | 432.6 | 463.4 | 543.2 | 478
1609 | 1488 | 484.5 | 444 | 445.5 | 433.2 | 464.4 | 545.3 | 481
1610 | 1489 | 484 | 444.9 | 447.4 | 434 | 465.8 | 549.2 | 484.7
1611 | 1490 | 483.5 | 445.8 | 449.4 | 434.9 | 466.8 | 549.9 | 487.3
1612 | 1491 | 482.9 | 446.6 | 451.6 | 435.7 | 467.9 | 550.6 | 490.5
1613 | 1492 | 482.5 | 447.5 | 453.8 | 436.6 | 469 | 551.8 | 493.1
1614 | 1493 | 482 | 448.4 | 455.8 | 437.5 | 470.2 | 553.6 | 494.4
1615 | 1494 | 481.4 | 449.2 | 457.7 | 438.4 | 471.5 | 554.6 | 495.6
1616 | 1495 | 481 | 450.1 | 459.6 | 439.3 | 472.6 | 555.8 | 497.1
1617 | 1496 | 480.6 | 450.8 | 461.4 | 440.1 | 473.5 | 558.1 | 497.3
1618 | 1497 | 480.2 | 451.5 | 462.7 | 440.9 | 474.1 | 559.4 | 499.1
1619 | 1498 | 479.6 | 452.3 | 464.4 | 441.9 | 474.6 | 559.3 | 500
1620 | 1499 | 479.2 | 453.2 | 466 | 443 | 475.6 | 559.3 | 499.7
1621 | 1500 | 478.7 | 453.8 | 467.8 | 444 | 476.6 | 560.1 | 500
1622 | 1501 | 478.3 | 454.4 | 470 | 445 | 477.6 | 562 | 501.3
1623 | 1502 | 478 | 455.2 | 472.1 | 445.8 | 478.7 | 563.7 | 502
1624 | 1503 | 477.6 | 455.9 | 473.6 | 446.5 | 479.7 | 565 | 502.7
1625 | 1504 | 477.2 | 456.7 | 474 | 447.3 | 480.5 | 566.3 | 504.3
1626 | 1505 | 476.8 | 457.4 | 473.9 | 448.2 | 481 | 566.9 | 505.7
1627 | 1506 | 476.3 | 458 | 474.7 | 449 | 481.8 | 568 | 506.3
1628 | 1507 | 475.8 | 458.8 | 475.7 | 449.9 | 482.5 | 568.9 | 506.9
1629 | 1508 | 475.4 | 459.6 | 477.1 | 450.8 | 483.2 | 572 | 508.2
1630 | 1509 | 475.1 | 460.4 | 478.1 | 451.7 | 483.8 | 573.6 | 509.9
1631 | 1510 | 474.7 | 461.2 | 478.9 | 452.7 | 484.3 | 574.5 | 511.3
1632 | 1511 | 474.3 | 462.1 | 480.1 | 453.7 | 485 | 575.9 | 514
1633 | 1512 | 474 | 462.8 | 481.3 | 454.3 | 485.8 | 576.3 | 517.7
1634 | 1513 | 473.6 | 463.5 | 481.8 | 455.1 | 486.2 | 576.9 | 519.8
1635 | 1514 | 473.3 | 464.1 | 482.7 | 455.9 | 486.7 | 577 | 521.6
1636 | 1515 | 472.9 | 464.9 | 483.8 | 456.7 | 487.5 | 576.7 | 522.8
1637 | 1516 | 472.5 | 465.7 | 484.6 | 457.5 | 488 | 576.1 | 524.4
1638 | 1517 | 472.2 | 466.4 | 484.2 | 458.5 | 488.5 | 575.5 | 526.7
1639 | 1518 | 471.6 | 467.2 | 483.5 | 459.4 | 488.9 | 575.8 | 528.9
1640 | 1519 | 471.1 | 467.8 | 484.2 | 460.3 | 489.6 | 575.6 | 530.9
1641 | 1520 | 470.7 | 468.5 | 485.4 | 461.1 | 489.9 | 576.6 | 532.5
1642 | 1521 | 470.3 | 469.1 | 486.6 | 461.8 | 490.1 | 577.7 | 533.6
1643 | 1522 | 469.7 | 469.8 | 487.7 | 462.6 | 490.6 | 579.1 | 535.2
1644 | 1523 | 469.2 | 470.5 | 488.6 | 463.3 | 490.7 | 579.4 | 536.4
1645 | 1524 | 468.8 | 471.2 | 487.5 | 464 | 491.1 | 579.3 | 538.2
1646 | 1525 | 468.4 | 471.9 | 486.1 | 464.6 | 491.9 | 578.6 | 540
1647 | 1526 | 468 | 472.5 | 486.2 | 465.2 | 492.7 | 578.5 | 540.7
1648 | 1527 | 467.6 | 473.1 | 485.3 | 465.6 | 493.3 | 580.3 | 541.5
1649 | 1528 | 467.2 | 473.7 | 486.6 | 466.3 | 493.8 | 581.1 | 541.9
1650 | 1529 | 466.7 | 474.3 | 488.2 | 467.1 | 494.3 | 581.7 | 542.1
1651 | 1530 | 466.2 | 474.9 | 489.6 | 467.6 | 494.9 | 581.8 | 543.1
1652 | 1531 | 465.7 | 475.7 | 489.7 | 468.3 | 495.3 | 581.3 | 544
1653 | 1532 | 465.2 | 476.4 | 489.6 | 469 | 495.5 | 581.2 | 544.3
1654 | 1533 | 464.6 | 477.1 | 489.6 | 469.5 | 495.8 | 581 | 544.6
1655 | 1534 | 464.1 | 477.8 | 489.1 | 470.1 | 496 | 580.8 | 544.9
1656 | 1535 | 463.5 | 478.5 | 488.2 | 470.7 | 496.4 | 580.9 | 545.5
1657 | 1536 | 462.9 | 479.2 | 487.6 | 471.2 | 496.8 | 580.9 | 546.8
1658 | 1537 | 462.4 | 480.1 | 487.5 | 471.9 | 497.3 | 580 | 547.3
1659 | 1538 | 461.8 | 481.6 | 488.3 | 472.8 | 497.7 | 578.9 | 548.2
1660 | 1539 | 461.2 | 482.7 | 489.5 | 473.6 | 498 | 577.6 | 548.8
1661 | 1540 | 460.8 | 483.5 | 489.9 | 473.9 | 498.4 | 576.9 | 549.9
1662 | 1541 | 460.3 | 484.1 | 490.6 | 474.4 | 498.8 | 576.7 | 550.5
1663 | 1542 | 459.6 | 484.7 | 491.3 | 474.8 | 499.2 | 577.6 | 550.9
1664 | 1543 | 459 | 485.2 | 492.3 | 475.4 | 499.6 | 577.1 | 551.8
1665 | 1544 | 458.4 | 485.7 | 493.8 | 476.2 | 499.9 | 576.4 | 552
1666 | 1545 | 458 | 486 | 494.5 | 477.1 | 500 | 576 | 552.1
1667 | 1546 | 457.7 | 486.2 | 494.9 | 477.8 | 500.2 | 575 | 552
1668 | 1547 | 457.2 | 486.3 | 495.6 | 478.5 | 500.3 | 573 | 551.7
1669 | 1548 | 456.6 | 486.5 | 496.2 | 479.2 | 500.6 | 572 | 551.8
1670 | 1549 | 455.9 | 486.7 | 496.5 | 479.8 | 500.9 | 569.6 | 552.2
1671 | 1550 | 455.5 | 486.9 | 496.5 | 480.5 | 501.3 | 565.8 | 553
1672 | 1551 | 455 | 487.1 | 496.2 | 481.2 | 501.7 | 560.8 | 553.5
1673 | 1552 | 454.5 | 487.3 | 496.3 | 481.7 | 502 | 557.1 | 553.4
1674 | 1553 | 453.9 | 487.6 | 496.7 | 482.3 | 502.2 | 553.8 | 554.4
1675 | 1554 | 453.2 | 487.9 | 496.9 | 482.8 | 502.5 | 549.9 | 555.7
1676 | 1555 | 452.8 | 488.2 | 497.3 | 483.4 | 502.6 | 546.1 | 556.8
1677 | 1556 | 452.4 | 488.6 | 497.5 | 484 | 502.9 | 542.2 | 557.9
1678 | 1557 | 452 | 488.9 | 497.6 | 484.5 | 503.2 | 537.5 | 558.8
1679 | 1558 | 451.4 | 489.3 | 498 | 485 | 503.4 | 533.3 | 560
1680 | 1559 | 450.9 | 489.5 | 498.5 | 485.4 | 503.7 | 530 | 561
1681 | 1560 | 450.5 | 489.8 | 499.1 | 485.9 | 503.9 | 526.7 | 561.4
1682 | 1561 | 449.8 | 490.2 | 499.4 | 486.4 | 504 | 523.7 | 562
1683 | 1562 | 449.3 | 490.5 | 499.6 | 487.1 | 504.1 | 521.8 | 561.8
1684 | 1563 | 448.8 | 490.9 | 500 | 487.5 | 504.2 | 520.2 | 561.7
1685 | 1564 | 448.3 | 491.2 | 500.3 | 487.9 | 504.4 | 519.1 | 562.4
1686 | 1565 | 447.9 | 491.4 | 500.7 | 488.3 | 504.6 | 517.9 | 562.4
1687 | 1566 | 447.3 | 491.8 | 501.1 | 488.6 | 504.9 | 517.2 | 562.2
1688 | 1567 | 446.7 | 492.1 | 501.4 | 489 | 505.1 | 516.4 | 561.8
1689 | 1568 | 446.2 | 492.4 | 501.5 | 489.3 | 505.4 | 516.3 | 561.4
1690 | 1569 | 445.8 | 492.7 | 501.7 | 489.7 | 505.7 | 515.7 | 561.1
1691 | 1570 | 445.2 | 493 | 501.7 | 490 | 506 | 514.6 | 561.1
1692 | 1571 | 444.7 | 493.3 | 501.9 | 490.3 | 506.3 | 514.6 | 561.7
1693 | 1572 | 444.3 | 493.6 | 502.1 | 490.6 | 506.7 | 514.6 | 561.5
1694 | 1573 | 443.8 | 494 | 502.3 | 490.8 | 507 | 514.3 | 561.6
1695 | 1574 | 443.2 | 494.3 | 502.3 | 491.2 | 507.3 | 513.4 | 561.7
1696 | 1575 | 442.6 | 494.6 | 502.4 | 491.4 | 507.6 | 513.2 | 561.9
1697 | 1576 | 441.9 | 495 | 502.7 | 491.8 | 507.9 | 512.7 | 562.2
1698 | 1577 | 441.2 | 495.4 | 503 | 492.1 | 508.2 | 512.6 | 561.5
1699 | 1578 | 440.5 | 495.7 | 503.4 | 492.5 | 508.6 | 512.2 | 560.9
1700 | 1579 | 439.9 | 496 | 503.8 | 492.9 | 509 | 511.7 | 560.2
1701 | 1580 | 439.4 | 496.4 | 504.2 | 493.3 | 509.4 | 511.8 | 559.6
1702 | 1581 | 438.9 | 496.7 | 504.6 | 493.6 | 509.9 | 511.3 | 559.5
1703 | 1582 | 438.2 | 497.1 | 504.9 | 493.9 | 510.4 | 510.9 | 559.4
1704 | 1583 | 437.7 | 497.4 | 505.4 | 494.2 | 510.8 | 511.1 | 559.3
1705 | 1584 | 437 | 497.8 | 505.9 | 494.5 | 511.2 | 509.6 | 559.4
1706 | 1585 | 436.3 | 498.2 | 506.4 | 494.8 | 511.5 | 508.7 | 559.7
1707 | 1586 | 435.9 | 498.5 | 506.9 | 495.1 | 511.8 | 508.2 | 559.1
1708 | 1587 | 435.3 | 498.9 | 507.6 | 495.4 | 512.2 | 508.4 | 558.1
1709 | 1588 | 434.7 | 499.2 | 508 | 495.7 | 512.6 | 507.5 | 557
1710 | 1589 | 434.2 | 499.5 | 508.6 | 495.9 | 513 | 506.9 | 555.9
1711 | 1590 | 433.7 | 499.9 | 509.2 | 496.1 | 513.5 | 505.8 | 554.8
1712 | 1591 | 433.1 | 500.2 | 509.7 | 496.4 | 513.9 | 506.1 | 553.8
1713 | 1592 | 432.7 | 500.5 | 510.3 | 496.7 | 514.2 | 506.4 | 553.2
1714 | 1593 | 432.2 | 500.9 | 510.9 | 497 | 514.6 | 506.3 | 553.6
1715 | 1594 | 431.7 | 501.3 | 511.4 | 497.3 | 515 | 507 | 553.5
1716 | 1595 | 431.3 | 501.7 | 512.1 | 497.6 | 515.4 | 507 | 552.6
1717 | 1596 | 430.9 | 502.1 | 512.7 | 497.9 | 515.7 | 506.7 | 551.6
1718 | 1597 | 430.4 | 502.5 | 513.3 | 498.2 | 516 | 507.5 | 550.8
1719 | 1598 | 429.8 | 502.9 | 514.2 | 498.5 | 516.4 | 507.8 | 549.4
1720 | 1599 | 429.2 | 503.3 | 515 | 498.9 | 516.8 | 508.1 | 548.3
1721 | 1600 | 428.6 | 503.7 | 515.8 | 499.2 | 517.2 | 508.2 | 548
1722 | 1601 | 427.9 | 504.2 | 516.6 | 499.4 | 517.6 | 507.8 | 547.3
1723 | 1602 | 427.2 | 504.6 | 517.3 | 499.7 | 518 | 508.3 | 547.2
1724 | 1603 | 426.4 | 505 | 518.1 | 500.1 | 518.5 | 508.7 | 547.5
1725 | 1604 | 425.8 | 505.5 | 519 | 500.2 | 519.1 | 508.3 | 547
1726 | 1605 | 425.1 | 505.9 | 519.8 | 500.5 | 519.7 | 507.8 | 546.3
1727 | 1606 | 424.5 | 506.4 | 520.5 | 500.9 | 520.3 | 507.3 | 545.9
1728 | 1607 | 423.9 | 506.8 | 521.3 | 501.2 | 520.9 | 506.8 | 545.2
1729 | 1608 | 423.4 | 507.2 | 522.1 | 501.5 | 521.6 | 506.5 | 544.7
1730 | 1609 | 423 | 507.5 | 522.9 | 501.9 | 522.1 | 506.9 | 544.1
1731 | 1610 | 422.5 | 508 | 523.7 | 502.2 | 522.6 | 507.1 | 543.6
1732 | 1611 | 421.9 | 508.4 | 524.5 | 502.5 | 523.1 | 507.6 | 543
1733 | 1612 | 421.2 | 509 | 525.3 | 502.8 | 523.6 | 507.9 | 542.9
1734 | 1613 | 420.7 | 509.5 | 526.1 | 503.1 | 524.1 | 507.4 | 542.9
1735 | 1614 | 420.1 | 510 | 526.9 | 503.4 | 524.6 | 508.1 | 543.1
1736 | 1615 | 419.6 | 510.4 | 527.5 | 503.7 | 525.1 | 508.1 | 543.4
1737 | 1616 | 419 | 511 | 528.2 | 504 | 525.7 | 507.9 | 542.6
1738 | 1617 | 418.3 | 511.6 | 528.8 | 504.4 | 526.2 | 507.8 | 542.6
1739 | 1618 | 417.7 | 512.1 | 529.4 | 504.8 | 526.8 | 507.7 | 542.4
1740 | 1619 | 417.2 | 512.7 | 530 | 505.2 | 527.4 | 507.8 | 542.5
1741 | 1620 | 416.6 | 513.2 | 530.6 | 505.5 | 527.9 | 508.5 | 542.9
1742 | 1621 | 416.1 | 513.7 | 531.1 | 505.8 | 528.3 | 508.4 | 543.4
1743 | 1622 | 415.6 | 514.3 | 531.8 | 506.2 | 528.8 | 507.7 | 543.5
1744 | 1623 | 415.2 | 514.9 | 532.5 | 506.5 | 529.2 | 508 | 543.6
1745 | 1624 | 414.8 | 515.5 | 533.2 | 506.9 | 529.6 | 508.8 | 543.2
1746 | 1625 | 414.4 | 516 | 534 | 507.3 | 529.9 | 508.5 | 542.4
1747 | 1626 | 413.9 | 516.5 | 534.8 | 507.8 | 530.1 | 507 | 541.4
1748 | 1627 | 413.4 | 517.2 | 535.6 | 508.2 | 530.3 | 507.2 | 540.3
1749 | 1628 | 413 | 517.8 | 536.4 | 508.7 | 530.6 | 507.4 | 540
1750 | 1629 | 412.6 | 518.3 | 537.2 | 509 | 530.7 | 507.3 | 539.8
1751 | 1630 | 412.2 | 518.8 | 538 | 509.3 | 530.9 | 507.4 | 539
1752 | 1631 | 411.5 | 519.3 | 538.8 | 509.7 | 531.3 | 507.7 | 538.1
1753 | 1632 | 411 | 519.8 | 539.7 | 510.1 | 531.6 | 506.8 | 537.3
1754 | 1633 | 410.6 | 520.3 | 540.4 | 510.4 | 531.8 | 507.6 | 536.1
1755 | 1634 | 410.1 | 520.8 | 541.1 | 510.7 | 532.2 | 507.2 | 535.3
1756 | 1635 | 409.6 | 521.3 | 541.9 | 511.1 | 532.6 | 505.8 | 534.2
1757 | 1636 | 409 | 521.7 | 542.7 | 511.5 | 532.8 | 505 | 533.4
1758 | 1637 | 408.5 | 522.2 | 543.5 | 512 | 533.2 | 505.3 | 532.7
1759 | 1638 | 408.1 | 522.7 | 544.4 | 512.4 | 533.6 | 505.7 | 531.5
1760 | 1639 | 407.6 | 523.3 | 545.1 | 512.7 | 534 | 506.7 | 530.3
1761 | 1640 | 407 | 523.7 | 545.7 | 513.1 | 534.4 | 506.3 | 529.6
1762 | 1641 | 406.5 | 524.1 | 546.4 | 513.3 | 534.7 | 506.4 | 528.1
1763 | 1642 | 405.8 | 524.6 | 547 | 513.5 | 535.1 | 506.7 | 527
1764 | 1643 | 405.3 | 525 | 547.7 | 514 | 535.4 | 506.6 | 526.7
1765 | 1644 | 404.8 | 525.5 | 548.6 | 514.5 | 535.7 | 506.1 | 526.1
1766 | 1645 | 404.4 | 525.9 | 549.2 | 514.8 | 536.1 | 505.8 | 525.4
1767 | 1646 | 403.8 | 526.3 | 550 | 515.1 | 536.4 | 505.8 | 524.9
1768 | 1647 | 403.3 | 526.8 | 550.6 | 515.3 | 536.7 | 505.6 | 524.1
1769 | 1648 | 402.8 | 527.3 | 551.3 | 515.6 | 537 | 505.5 | 523.8
1770 | 1649 | 402.2 | 527.7 | 551.9 | 516 | 537.4 | 505.4 | 524
1771 | 1650 | 401.7 | 528.1 | 552.6 | 516.4 | 537.8 | 505 | 524.8
1772 | 1651 | 401.1 | 528.5 | 553.4 | 516.7 | 538.3 | 505 | 524.6
1773 | 1652 | 400.6 | 528.9 | 554 | 517.1 | 538.8 | 505.1 | 524.7
1774 | 1653 | 400 | 529.4 | 554.7 | 517.4 | 539.3 | 504.6 | 524.4
1775 | 1654 | 399.5 | 529.8 | 555.3 | 517.9 | 539.6 | 504.3 | 524.7
1776 | 1655 | 399 | 530.3 | 555.8 | 518.1 | 540 | 504.7 | 525.3
1777 | 1656 | 398.5 | 530.7 | 556.3 | 518.4 | 540.4 | 504.3 | 526.4
1778 | 1657 | 398 | 531.1 | 556.9 | 518.8 | 540.9 | 504.1 | 527.3
1779 | 1658 | 397.4 | 531.5 | 557.4 | 519 | 541.4 | 504.1 | 528
1780 | 1659 | 396.9 | 531.8 | 558.1 | 519.3 | 541.8 | 503.6 | 529.1
1781 | 1660 | 396.2 | 532.2 | 558.7 | 519.6 | 542.2 | 502.9 | 530.2
1782 | 1661 | 395.7 | 532.7 | 559.3 | 519.8 | 542.6 | 502.8 | 530.1
1783 | 1662 | 395.1 | 533 | 559.8 | 520.2 | 543 | 502.7 | 531
1784 | 1663 | 394.6 | 533.4 | 560.2 | 520.4 | 543.4 | 502.2 | 531.3
1785 | 1664 | 394.2 | 533.8 | 560.6 | 520.6 | 543.9 | 501.2 | 531.5
1786 | 1665 | 393.8 | 534.1 | 561 | 520.8 | 544.2 | 500.7 | 532.2
1787 | 1666 | 393.3 | 534.5 | 561.5 | 521.1 | 544.6 | 500.3 | 532.1
1788 | 1667 | 392.7 | 535 | 562 | 521.3 | 545 | 500.2 | 532
1789 | 1668 | 392.1 | 535.4 | 562.7 | 521.7 | 545.5 | 500.3 | 532.1
1790 | 1669 | 391.6 | 535.8 | 563.1 | 521.9 | 546.1 | 500.4 | 531.3
1791 | 1670 | 391 | 536.2 | 563.7 | 522.3 | 546.7 | 500.4 | 531
1792 | 1671 | 390.6 | 536.5 | 564.2 | 522.6 | 547.3 | 500.4 | 530.5
1793 | 1672 | 389.9 | 537 | 564.8 | 522.9 | 547.8 | 500.1 | 529.8
1794 | 1673 | 389.3 | 537.3 | 565.3 | 523.2 | 548.3 | 499.8 | 529.7
1795 | 1674 | 388.8 | 537.6 | 565.8 | 523.4 | 548.8 | 499.5 | 529.6
1796 | 1675 | 388.2 | 538.1 | 566.2 | 523.6 | 549.4 | 499.4 | 529.6
1797 | 1676 | 387.7 | 538.5 | 566.7 | 523.9 | 550 | 499.2 | 529
1798 | 1677 | 387.2 | 538.8 | 567.4 | 524.2 | 550.5 | 499.1 | 528.4
1799 | 1678 | 386.6 | 539.1 | 567.8 | 524.4 | 551 | 499.1 | 528.2
1800 | 1679 | 386.1 | 539.4 | 568 | 524.7 | 551.4 | 499.2 | 528.2
1801 | 1680 | 385.5 | 539.7 | 568.8 | 525 | 551.9 | 499.4 | 527.2
1802 | 1681 | 385 | 540.1 | 569.3 | 525.3 | 552.3 | 499.5 | 527.2
1803 | 1682 | 384.5 | 540.4 | 569.8 | 525.6 | 552.9 | 500 | 527.6
1804 | 1683 | 384 | 540.7 | 570.3 | 525.9 | 553.4 | 500.1 | 527.8
1805 | 1684 | 383.5 | 541.1 | 571.1 | 526.1 | 553.9 | 500.2 | 526.9
1806 | 1685 | 383 | 541.4 | 571.7 | 526.4 | 554.4 | 500.3 | 526.6
1807 | 1686 | 382.6 | 541.9 | 572.5 | 526.7 | 555 | 500.3 | 525.6
1808 | 1687 | 382 | 542.3 | 573.1 | 527 | 555.5 | 500.3 | 524.9
1809 | 1688 | 381.4 | 542.7 | 573.6 | 527.3 | 556 | 500.3 | 524.1
1810 | 1689 | 380.9 | 543.1 | 574 | 527.6 | 556.6 | 500.3 | 523.7
1811 | 1690 | 380.3 | 543.5 | 574.3 | 527.9 | 557.3 | 500.3 | 523.5
1812 | 1691 | 379.8 | 543.9 | 574.7 | 528.1 | 557.8 | 500.4 | 523.7
1813 | 1692 | 379.3 | 544.3 | 575.1 | 528.4 | 558.3 | 500.4 | 523.2
1814 | 1693 | 378.7 | 544.7 | 575.4 | 528.7 | 558.9 | 500.4 | 522.8
1815 | 1694 | 378.3 | 545 | 575.9 | 529 | 559.5 | 500.6 | 522.3
1816 | 1695 | 377.8 | 545.4 | 576.4 | 529.3 | 560 | 500.7 | 521.6
1817 | 1696 | 377.2 | 545.6 | 576.6 | 529.6 | 560.5 | 500.9 | 520.9
1818 | 1697 | 376.8 | 546 | 577.2 | 529.9 | 561.1 | 501.2 | 519.7
1819 | 1698 | 376.3 | 546.3 | 577.6 | 530.1 | 561.7 | 501.3 | 518
1820 | 1699 | 375.8 | 546.7 | 578.2 | 530.4 | 562.2 | 501.5 | 516.8
1821 | 1700 | 375.2 | 547.2 | 578.8 | 530.7 | 562.9 | 501.6 | 515.9
1822 | 1701 | 374.7 | 547.6 | 579.1 | 531 | 563.5 | 501.7 | 514.9
1823 | 1702 | 374.2 | 547.9 | 579.5 | 531.3 | 564.1 | 501.9 | 513.8
1824 | 1703 | 373.7 | 548.3 | 579.8 | 531.5 | 564.7 | 502.3 | 512.6
1825 | 1704 | 373.2 | 548.7 | 580.1 | 531.8 | 565.2 | 502.8 | 512.1
1826 | 1705 | 372.7 | 549.1 | 580.5 | 532.1 | 565.9 | 503.4 | 511.9
1827 | 1706 | 372.2 | 549.4 | 580.7 | 532.4 | 566.5 | 504.1 | 511.8
1828 | 1707 | 371.7 | 549.6 | 580.9 | 532.7 | 567.2 | 504.7 | 511.4
1829 | 1708 | 371.1 | 550 | 581.3 | 533 | 568 | 505.3 | 511.4
1830 | 1709 | 370.4 | 550.3 | 581.5 | 533.3 | 568.8 | 506 | 510.9
1831 | 1710 | 369.8 | 550.6 | 581.8 | 533.6 | 569.6 | 506.8 | 510.5
1832 | 1711 | 369.3 | 551 | 582.2 | 533.9 | 570.6 | 507.6 | 510.2
1833 | 1712 | 368.8 | 551.5 | 582.8 | 534.2 | 571.5 | 508.5 | 510.2
1834 | 1713 | 368.4 | 551.8 | 583.1 | 534.5 | 572.2 | 509.5 | 510.4
1835 | 1714 | 367.9 | 552.1 | 583.5 | 534.7 | 573 | 510.5 | 510.2
1836 | 1715 | 367.5 | 552.3 | 583.7 | 535 | 573.7 | 511.7 | 509.7
1837 | 1716 | 367 | 552.7 | 584.2 | 535.3 | 574.5 | 512.9 | 509.2
1838 | 1717 | 366.5 | 553 | 584.5 | 535.6 | 575.1 | 514.1 | 508.6
1839 | 1718 | 366 | 553.2 | 584.6 | 535.9 | 575.6 | 515.3 | 507.7
1840 | 1719 | 365.6 | 553.4 | 584.9 | 536.2 | 576.2 | 516.6 | 507.3
1841 | 1720 | 365.1 | 553.8 | 585.2 | 536.5 | 576.8 | 517.9 | 506.9
1842 | 1721 | 364.5 | 554.2 | 585.5 | 536.7 | 577.4 | 519.5 | 506.5
1843 | 1722 | 364 | 554.6 | 585.9 | 537 | 577.9 | 521.2 | 506.5
1844 | 1723 | 363.5 | 554.8 | 586 | 537.3 | 578.4 | 522.9 | 506.3
1845 | 1724 | 363 | 555 | 586.1 | 537.6 | 578.7 | 524.7 | 505.9
1846 | 1725 | 362.5 | 555.2 | 586.3 | 537.8 | 579.2 | 526.5 | 505.5
1847 | 1726 | 362.1 | 555.6 | 586.6 | 538.1 | 579.6 | 528.3 | 505
1848 | 1727 | 361.7 | 556 | 586.8 | 538.4 | 580 | 530.3 | 504.8
1849 | 1728 | 361.2 | 556.3 | 586.8 | 538.6 | 580.4 | 532.4 | 504.5
1850 | 1729 | 360.8 | 556.6 | 587 | 538.9 | 580.9 | 534.3 | 504.4
1851 | 1730 | 360.2 | 557 | 587.1 | 539.1 | 581.5 | 535.8 | 504.8
1852 | 1731 | 359.7 | 557.3 | 587.2 | 539.4 | 582 | 537.4 | 505.3
1853 | 1732 | 359.2 | 557.6 | 587.3 | 539.6 | 582.5 | 538.9 | 505.3
1854 | 1733 | 358.7 | 558.1 | 587.6 | 539.9 | 583.1 | 540.2 | 505.3
1855 | 1734 | 358.2 | 558.4 | 587.8 | 540.1 | 583.6 | 541.6 | 505.5
1856 | 1735 | 357.6 | 558.7 | 588.1 | 540.3 | 584.1 | 543 | 505.6
1857 | 1736 | 357.2 | 559.1 | 588.3 | 540.6 | 584.6 | 544.1 | 505.6
1858 | 1737 | 356.7 | 559.4 | 588.4 | 540.8 | 585.1 | 545 | 505.8
1859 | 1738 | 356.2 | 559.7 | 588.4 | 541.1 | 585.7 | 546 | 505.9
1860 | 1739 | 355.7 | 559.9 | 588.5 | 541.3 | 586.3 | 546.6 | 505.6
1861 | 1740 | 355.4 | 560.2 | 588.7 | 541.6 | 587 | 547.1 | 505.2
1862 | 1741 | 354.9 | 560.6 | 589.1 | 541.8 | 587.7 | 548 | 505.1
1863 | 1742 | 354.4 | 560.8 | 589.3 | 542.1 | 588.4 | 548.8 | 505.7
1864 | 1743 | 353.9 | 561.1 | 589.5 | 542.4 | 589.1 | 548.7 | 506.1
1865 | 1744 | 353.4 | 561.4 | 589.7 | 542.6 | 589.8 | 548.7 | 506.4
1866 | 1745 | 352.9 | 561.6 | 589.8 | 542.9 | 590.3 | 549.1 | 506.7
1867 | 1746 | 352.4 | 561.8 | 589.8 | 543.2 | 590.8 | 549.8 | 507.2
1868 | 1747 | 351.8 | 562.1 | 589.9 | 543.4 | 591.2 | 550.3 | 507.2
1869 | 1748 | 351.2 | 562.4 | 590.2 | 543.7 | 591.9 | 551 | 507.3
1870 | 1749 | 350.8 | 562.7 | 590.4 | 543.9 | 592.5 | 551.8 | 507.5
1871 | 1750 | 350.3 | 563 | 590.6 | 544.2 | 593.1 | 552.6 | 507.5
1872 | 1751 | 349.9 | 563.2 | 590.8 | 544.4 | 593.7 | 552.8 | 507.6
1873 | 1752 | 349.4 | 563.5 | 590.8 | 544.7 | 594.2 | 552.9 | 508.1
1874 | 1753 | 348.9 | 563.7 | 591 | 545 | 594.6 | 553.5 | 508.4
1875 | 1754 | 348.4 | 563.9 | 591.2 | 545.2 | 595.1 | 554.2 | 508.4
1876 | 1755 | 348 | 564.2 | 591.5 | 545.5 | 595.5 | 554.8 | 508.4
1877 | 1756 | 347.4 | 564.6 | 591.8 | 545.7 | 596.1 | 555 | 508.5
1878 | 1757 | 346.9 | 564.8 | 592.2 | 546 | 596.4 | 555.3 | 508.9
1879 | 1758 | 346.4 | 565 | 592.5 | 546.2 | 596.8 | 556.1 | 509.4
1880 | 1759 | 345.9 | 565.3 | 592.9 | 546.5 | 597.3 | 556.5 | 509.6
1881 | 1760 | 345.6 | 565.5 | 593.2 | 546.7 | 597.8 | 556.6 | 509.7
1882 | 1761 | 345.2 | 565.7 | 593.3 | 546.9 | 598.2 | 556.8 | 510
1883 | 1762 | 344.9 | 566 | 593.4 | 547.2 | 598.7 | 557.1 | 510
1884 | 1763 | 344.4 | 566.3 | 593.3 | 547.4 | 599 | 557.7 | 510.1
1885 | 1764 | 343.8 | 566.5 | 593.1 | 547.6 | 599.2 | 558.2 | 510.3
1886 | 1765 | 343.4 | 566.8 | 593.1 | 547.8 | 599.4 | 558.9 | 510.3
1887 | 1766 | 343 | 567 | 593.2 | 548 | 599.7 | 559.6 | 510.6
1888 | 1767 | 342.6 | 567.3 | 593.4 | 548.2 | 599.9 | 560.3 | 510.8
1889 | 1768 | 342.1 | 567.6 | 593.7 | 548.4 | 600.1 | 560.8 | 510.4
1890 | 1769 | 341.7 | 568 | 593.9 | 548.6 | 600.4 | 561.3 | 510.3
1891 | 1770 | 341.3 | 568.2 | 593.9 | 548.7 | 600.7 | 561.7 | 510.5
1892 | 1771 | 340.9 | 568.5 | 594 | 548.9 | 601 | 562.4 | 510.8
1893 | 1772 | 340.4 | 568.8 | 594.1 | 549.1 | 601.3 | 562.9 | 510.8
1894 | 1773 | 340 | 569 | 594.2 | 549.4 | 601.6 | 563.3 | 510.8
1895 | 1774 | 339.5 | 569.3 | 594.5 | 549.6 | 601.9 | 564.3 | 510.4
1896 | 1775 | 339 | 569.5 | 594.7 | 549.7 | 602.1 | 565 | 510.4
1897 | 1776 | 338.6 | 569.7 | 594.5 | 549.9 | 602.4 | 565.4 | 510.5
1898 | 1777 | 338.2 | 569.9 | 594.4 | 550.1 | 602.6 | 565.8 | 510.3
1899 | 1778 | 337.7 | 570.2 | 594.5 | 550.3 | 602.9 | 566.4 | 510.2
1900 | 1779 | 337.3 | 570.5 | 594.4 | 550.5 | 603.1 | 566.7 | 510.2
1901 | 1780 | 336.8 | 570.7 | 594.4 | 550.7 | 603.3 | 567.1 | 510.5
1902 | 1781 | 336.3 | 570.9 | 594.6 | 550.9 | 603.6 | 567.2 | 510.8
1903 | 1782 | 335.8 | 571.1 | 594.7 | 551.1 | 603.9 | 567.4 | 511.3
1904 | 1783 | 335.3 | 571.3 | 594.7 | 551.4 | 604.4 | 567.2 | 511.8
1905 | 1784 | 334.9 | 571.4 | 594.9 | 551.6 | 604.9 | 567.2 | 511.8
1906 | 1785 | 334.5 | 571.6 | 595 | 551.8 | 605.4 | 567.2 | 512.1
1907 | 1786 | 334.1 | 571.8 | 595.1 | 552.1 | 605.8 | 567.3 | 512.1
1908 | 1787 | 333.6 | 571.9 | 595.2 | 552.3 | 606.3 | 567.2 | 512.4
1909 | 1788 | 333.1 | 572 | 595.3 | 552.5 | 606.6 | 567.3 | 512.8
1910 | 1789 | 332.6 | 572.2 | 595.5 | 552.8 | 606.9 | 567.4 | 513.1
1911 | 1790 | 332.2 | 572.4 | 595.7 | 553.1 | 607.1 | 567.3 | 513.5
1912 | 1791 | 331.8 | 572.6 | 595.8 | 553.3 | 607.4 | 567.1 | 513.6
1913 | 1792 | 331.2 | 572.7 | 596 | 553.6 | 607.8 | 566.8 | 513.7
1914 | 1793 | 330.6 | 572.8 | 595.9 | 553.8 | 608.2 | 566.8 | 514
1915 | 1794 | 330.2 | 573 | 595.8 | 554.1 | 608.7 | 567 | 514.3
1916 | 1795 | 329.8 | 573.1 | 595.8 | 554.3 | 609.3 | 567.2 | 515
1917 | 1796 | 329.4 | 573.2 | 595.7 | 554.5 | 609.9 | 567.6 | 515.5
1918 | 1797 | 329 | 573.3 | 595.8 | 554.8 | 610.4 | 567.5 | 516
1919 | 1798 | 328.4 | 573.5 | 596 | 555.1 | 610.9 | 567.1 | 516.1
1920 | 1799 | 328 | 573.7 | 596.2 | 555.3 | 611.4 | 566.9 | 516.4
1921 | 1800 | 327.5 | 573.8 | 596.2 | 555.6 | 611.8 | 566.9 | 516.4
1922 | 1801 | 327 | 574 | 596.5 | 555.8 | 612.1 | 566.8 | 516.1
1923 | 1802 | 326.6 | 574.2 | 596.7 | 556.1 | 612.3 | 566.6 | 515.7
1924 | 1803 | 326.2 | 574.4 | 596.7 | 556.3 | 612.5 | 567 | 515.8
1925 | 1804 | 325.9 | 574.5 | 596.6 | 556.5 | 612.6 | 567.4 | 516
1926 | 1805 | 325.5 | 574.7 | 596.6 | 556.7 | 612.8 | 567.9 | 515.7
1927 | 1806 | 325.1 | 574.9 | 596.7 | 557 | 612.9 | 568.6 | 515
1928 | 1807 | 324.7 | 575.1 | 596.8 | 557.2 | 612.9 | 569.1 | 514.6
1929 | 1808 | 324.3 | 575.3 | 596.9 | 557.4 | 613.1 | 569.6 | 514.1
1930 | 1809 | 323.9 | 575.4 | 596.9 | 557.6 | 613.2 | 569.9 | 514
1931 | 1810 | 323.6 | 575.6 | 596.8 | 557.8 | 613.4 | 570.2 | 513.9
1932 | 1811 | 323.2 | 575.8 | 596.7 | 558 | 613.5 | 570.2 | 514.1
1933 | 1812 | 322.8 | 576 | 596.8 | 558.2 | 613.6 | 570.2 | 513.5
1934 | 1813 | 322.4 | 576.1 | 596.6 | 558.4 | 613.7 | 570.5 | 512.9
1935 | 1814 | 321.9 | 576.3 | 596.4 | 558.5 | 613.8 | 571 | 511.9
1936 | 1815 | 321.5 | 576.5 | 596.4 | 558.7 | 614 | 571.4 | 511.3
1937 | 1816 | 321.1 | 576.7 | 596.1 | 558.9 | 614.2 | 571.6 | 510.9
1938 | 1817 | 320.6 | 576.9 | 595.8 | 559.1 | 614.4 | 571.5 | 510.3
1939 | 1818 | 320.1 | 577.2 | 595.7 | 559.2 | 614.5 | 571.4 | 509.7
1940 | 1819 | 319.6 | 577.4 | 595.7 | 559.4 | 614.6 | 572.1 | 509.3
1941 | 1820 | 319.1 | 577.6 | 595.8 | 559.6 | 614.7 | 572.7 | 508.9
1942 | 1821 | 318.7 | 577.8 | 596 | 559.8 | 614.9 | 572.8 | 508.3
1943 | 1822 | 318.2 | 577.9 | 596.1 | 559.9 | 615.1 | 572.3 | 507.7
1944 | 1823 | 317.7 | 578.1 | 596.2 | 560.1 | 615.3 | 572.1 | 507.1
1945 | 1824 | 317.3 | 578.3 | 596.4 | 560.3 | 615.5 | 571.5 | 506.1
1946 | 1825 | 316.8 | 578.4 | 596.6 | 560.5 | 615.8 | 570.7 | 505.3
1947 | 1826 | 316.4 | 578.6 | 596.7 | 560.7 | 616.2 | 570.6 | 504.6
1948 | 1827 | 316 | 578.7 | 596.8 | 560.9 | 616.5 | 570.9 | 504
1949 | 1828 | 315.5 | 578.8 | 596.9 | 561.1 | 616.9 | 571 | 503.3
1950 | 1829 | 315 | 578.9 | 596.8 | 561.3 | 617.4 | 571 | 502.5
1951 | 1830 | 314.6 | 579 | 596.8 | 561.5 | 617.8 | 570.9 | 502
1952 | 1831 | 314.1 | 579.1 | 596.6 | 561.8 | 618.2 | 571.4 | 501.7
1953 | 1832 | 313.6 | 579.2 | 596.4 | 562 | 618.6 | 571.6 | 501.3
1954 | 1833 | 313 | 579.3 | 596.2 | 562.2 | 619 | 571.5 | 500.9
1955 | 1834 | 312.5 | 579.4 | 596.1 | 562.4 | 619.5 | 571.5 | 500.2
1956 | 1835 | 312.1 | 579.5 | 596.1 | 562.6 | 620 | 571.7 | 499.7
1957 | 1836 | 311.8 | 579.6 | 596 | 562.8 | 620.4 | 572.2 | 499.2
1958 | 1837 | 311.3 | 579.7 | 595.9 | 563 | 620.9 | 573 | 498.8
1959 | 1838 | 310.8 | 579.9 | 595.7 | 563.1 | 621.3 | 573.5 | 498.4
1960 | 1839 | 310.3 | 580 | 595.7 | 563.3 | 621.8 | 573.5 | 497.9
1961 | 1840 | 309.9 | 580.1 | 595.5 | 563.5 | 622.2 | 573.5 | 497.4
1962 | 1841 | 309.4 | 580.2 | 595.4 | 563.7 | 622.6 | 573.5 | 496.8
1963 | 1842 | 308.9 | 580.3 | 595.3 | 563.9 | 622.8 | 573.8 | 496.1
1964 | 1843 | 308.6 | 580.4 | 595.3 | 564.1 | 623 | 574.3 | 495.4
1965 | 1844 | 308.2 | 580.5 | 595.3 | 564.3 | 623.1 | 574.9 | 494.8
1966 | 1845 | 307.9 | 580.6 | 595.4 | 564.4 | 623.1 | 575.8 | 494.2
1967 | 1846 | 307.5 | 580.7 | 595.4 | 564.6 | 623.2 | 576.5 | 493.7
1968 | 1847 | 307.1 | 580.9 | 595.4 | 564.8 | 623.4 | 577 | 493
1969 | 1848 | 306.8 | 581 | 595.5 | 564.9 | 623.4 | 576.9 | 492.5
1970 | 1849 | 306.5 | 581.1 | 595.5 | 565.1 | 623.6 | 577 | 492.1
1971 | 1850 | 306.1 | 581.2 | 595.4 | 565.3 | 623.7 | 576.9 | 491.8
1972 | 1851 | 305.7 | 581.3 | 595.4 | 565.4 | 623.9 | 577.4 | 491.5
1973 | 1852 | 305.3 | 581.4 | 595.3 | 565.6 | 624 | 577.7 | 491.2
1974 | 1853 | 304.9 | 581.5 | 595.3 | 565.8 | 624.1 | 578.2 | 490.9
1975 | 1854 | 304.5 | 581.6 | 595.2 | 565.9 | 624.2 | 578.9 | 490.6
1976 | 1855 | 304.2 | 581.7 | 595.1 | 566.1 | 624.3 | 579.7 | 490.1
1977 | 1856 | 303.8 | 581.8 | 595 | 566.3 | 624.4 | 580.4 | 489.7
1978 | 1857 | 303.3 | 581.9 | 594.9 | 566.4 | 624.5 | 581.4 | 489.1
1979 | 1858 | 303 | 582.1 | 594.8 | 566.6 | 624.7 | 581.9 | 488.6
1980 | 1859 | 302.6 | 582.2 | 594.7 | 566.7 | 624.8 | 582.5 | 488.1
1981 | 1860 | 302.2 | 582.3 | 594.6 | 566.9 | 624.9 | 582.9 | 487.6
1982 | 1861 | 301.9 | 582.5 | 594.4 | 567 | 625 | 583.3 | 487
1983 | 1862 | 301.5 | 582.6 | 594.2 | 567.1 | 625.1 | 583.7 | 486.5
1984 | 1863 | 301.1 | 582.8 | 593.8 | 567.3 | 625.2 | 583.9 | 486
1985 | 1864 | 300.7 | 582.9 | 593.4 | 567.4 | 625.3 | 584.2 | 485.5
1986 | 1865 | 300.3 | 583 | 593.1 | 567.5 | 625.3 | 584.4 | 484.9
1987 | 1866 | 299.9 | 583.1 | 592.8 | 567.6 | 625.2 | 585 | 484.3
1988 | 1867 | 299.6 | 583.2 | 592.5 | 567.7 | 625.2 | 585.4 | 483.7
1989 | 1868 | 299.2 | 583.3 | 592.2 | 567.9 | 625.3 | 585.5 | 483.1
1990 | 1869 | 298.8 | 583.4 | 592 | 568 | 625.3 | 585.5 | 482.5
1991 | 1870 | 298.4 | 583.5 | 591.6 | 568.1 | 625.3 | 585.8 | 481.7
1992 | 1871 | 297.9 | 583.6 | 591.3 | 568.2 | 625.5 | 586 | 481.1
1993 | 1872 | 297.5 | 583.7 | 590.9 | 568.4 | 625.6 | 586.2 | 480.6
1994 | 1873 | 297.2 | 583.7 | 590.6 | 568.5 | 625.8 | 586 | 480.2
1995 | 1874 | 296.8 | 583.8 | 590.2 | 568.6 | 626 | 586.1 | 479.7
1996 | 1875 | 296.4 | 583.9 | 589.9 | 568.7 | 626.1 | 586.3 | 479.2
1997 | 1876 | 296.1 | 583.9 | 589.6 | 568.9 | 626.2 | 586.7 | 478.6
1998 | 1877 | 295.9 | 584 | 589.3 | 569 | 626.3 | 586.8 | 478.2
1999 | 1878 | 295.5 | 584 | 588.8 | 569.1 | 626.5 | 587.2 | 477.7
2000 | 1879 | 294.8 | 584 | 588.3 | 569.2 | 626.7 | 587.5 | 477.3
2001 | 1880 | 294.3 | 584.1 | 587.7 | 569.3 | 627 | 587.7 | 476.9
2002 | 1881 | 293.8 | 584.1 | 587 | 569.3 | 627.4 | 587.9 | 476.6
2003 | 1882 | 293.4 | 584.1 | 586.4 | 569.4 | 627.9 | 587.5 | 476.4
2004 | 1883 | 293 | 584.2 | 586 | 569.5 | 628.2 | 586.9 | 476.2
2005 | 1884 | 292.7 | 584.2 | 585.6 | 569.6 | 628.6 | 585.9 | 476
2006 | 1885 | 292.3 | 584.3 | 585.3 | 569.7 | 629 | 585.4 | 475.7
2007 | 1886 | 292 | 584.3 | 585 | 569.8 | 629.3 | 585.5 | 475.8
2008 | 1887 | 291.7 | 584.4 | 584.8 | 569.9 | 629.4 | 585.9 | 475.9
2009 | 1888 | 291.3 | 584.4 | 584.5 | 570 | 629.5 | 586.3 | 476
2010 | 1889 | 291 | 584.4 | 584.2 | 570.1 | 629.6 | 586.8 | 476
2011 | 1890 | 290.6 | 584.4 | 583.9 | 570.2 | 629.7 | 587.1 | 476
2012 | 1891 | 290.1 | 584.4 | 583.6 | 570.3 | 629.8 | 586.6 | 476
2013 | 1892 | 289.7 | 584.5 | 583.2 | 570.4 | 629.9 | 586.5 | 475.8
2014 | 1893 | 289.4 | 584.5 | 582.7 | 570.5 | 630.1 | 586.6 | 475.6
2015 | 1894 | 289 | 584.5 | 582.1 | 570.6 | 630.4 | 586.7 | 475.5
2016 | 1895 | 288.7 | 584.6 | 581.6 | 570.7 | 630.5 | 587.2 | 475.2
2017 | 1896 | 288.4 | 584.6 | 581.2 | 570.8 | 630.5 | 587 | 474.9
2018 | 1897 | 288.1 | 584.6 | 580.8 | 570.9 | 630.4 | 586.8 | 474.6
2019 | 1898 | 287.7 | 584.7 | 580.5 | 571 | 630.4 | 586.7 | 474.3
2020 | 1899 | 287.3 | 584.7 | 580.2 | 571 | 630.4 | 586.8 | 474
2021 | 1900 | 286.8 | 584.8 | 579.8 | 571.1 | 630.4 | 587.2 | 473.7
2022 | 1901 | 286.4 | 584.8 | 579.4 | 571.1 | 630.4 | 587.7 | 473.2
2023 | 1902 | 286.1 | 584.9 | 579 | 571.2 | 630.5 | 587.7 | 472.9
2024 | 1903 | 285.7 | 584.9 | 578.6 | 571.3 | 630.7 | 588.2 | 472.5
2025 | 1904 | 285.4 | 585 | 578.2 | 571.3 | 630.8 | 588.6 | 472.2
2026 | 1905 | 285 | 585 | 577.8 | 571.4 | 631.1 | 588.4 | 471.7
2027 | 1906 | 284.6 | 585 | 577.3 | 571.5 | 631.3 | 588.1 | 471.3
2028 | 1907 | 284.2 | 585 | 576.8 | 571.5 | 631.4 | 588 | 471
2029 | 1908 | 283.9 | 585.1 | 576.4 | 571.5 | 631.3 | 587.4 | 470.7
2030 | 1909 | 283.6 | 585.1 | 576 | 571.6 | 631.3 | 586.4 | 470.3
2031 | 1910 | 283.3 | 585.2 | 575.6 | 571.6 | 631.3 | 586.2 | 470.1
2032 | 1911 | 282.9 | 585.2 | 575.2 | 571.6 | 631.4 | 585.9 | 469.7
2033 | 1912 | 282.6 | 585.2 | 574.8 | 571.7 | 631.5 | 585.3 | 469.5
2034 | 1913 | 282.3 | 585.2 | 574.3 | 571.7 | 631.8 | 585.7 | 469.3
2035 | 1914 | 281.9 | 585.2 | 573.8 | 571.8 | 632 | 586 | 469.2
2036 | 1915 | 281.5 | 585.2 | 573.5 | 571.8 | 632.2 | 586.5 | 469
2037 | 1916 | 281.2 | 585.2 | 573.2 | 571.8 | 632.4 | 585.7 | 468.9
2038 | 1917 | 280.9 | 585.2 | 572.9 | 571.9 | 632.6 | 584.7 | 468.6
2039 | 1918 | 280.6 | 585.2 | 572.6 | 571.9 | 632.6 | 583.5 | 468.4
2040 | 1919 | 280.3 | 585.2 | 572.4 | 571.9 | 632.4 | 583.4 | 468.2
2041 | 1920 | 280 | 585.3 | 572.2 | 572 | 632.3 | 583.6 | 468
2042 | 1921 | 279.6 | 585.3 | 571.9 | 572 | 632.3 | 582.9 | 467.8
2043 | 1922 | 279.2 | 585.3 | 571.6 | 572 | 632.3 | 582.6 | 467.5
2044 | 1923 | 278.8 | 585.3 | 571.4 | 572 | 632.2 | 582.5 | 467.3
2045 | 1924 | 278.4 | 585.3 | 571.2 | 572 | 632.1 | 582.2 | 467.1
2046 | 1925 | 278.1 | 585.3 | 571 | 572.1 | 632 | 581.7 | 466.8
2047 | 1926 | 277.7 | 585.3 | 570.7 | 572.1 | 632 | 581.5 | 466.4
2048 | 1927 | 277.3 | 585.3 | 570.5 | 572.1 | 631.9 | 580.8 | 466.1
2049 | 1928 | 277 | 585.3 | 570.4 | 572.1 | 631.8 | 580 | 465.8
2050 | 1929 | 276.7 | 585.3 | 570.2 | 572.1 | 631.8 | 579.7 | 465.5
2051 | 1930 | 276.4 | 585.3 | 570 | 572.1 | 631.8 | 579.2 | 465.2
2052 | 1931 | 275.9 | 585.3 | 569.8 | 572.2 | 631.9 | 578.6 | 465
2053 | 1932 | 275.5 | 585.3 | 569.6 | 572.2 | 632 | 578.1 | 464.8
2054 | 1933 | 275.1 | 585.3 | 569.4 | 572.2 | 632.1 | 577.7 | 464.6
2055 | 1934 | 274.8 | 585.3 | 569.1 | 572.2 | 632.1 | 576.4 | 464.4
2056 | 1935 | 274.5 | 585.3 | 568.9 | 572.2 | 632.3 | 575.5 | 464.3
2057 | 1936 | 274.1 | 585.3 | 568.8 | 572.2 | 632.4 | 574.8 | 464
2058 | 1937 | 273.6 | 585.3 | 568.6 | 572.3 | 632.6 | 573.5 | 463.6
2059 | 1938 | 273.3 | 585.3 | 568.4 | 572.3 | 632.6 | 571.7 | 463.4
2060 | 1939 | 273 | 585.3 | 568.2 | 572.3 | 632.6 | 570.4 | 463
2061 | 1940 | 272.7 | 585.3 | 568.2 | 572.2 | 632.5 | 570.3 | 462.8
2062 | 1941 | 272.4 | 585.4 | 568.2 | 572.2 | 632.4 | 569.6 | 462.5
2063 | 1942 | 272.1 | 585.4 | 568.2 | 572.2 | 632.5 | 568.9 | 462.2
2064 | 1943 | 271.8 | 585.4 | 568.2 | 572.2 | 632.6 | 567.8 | 462
2065 | 1944 | 271.4 | 585.4 | 568.2 | 572.2 | 632.6 | 566.8 | 461.8
2066 | 1945 | 271.1 | 585.4 | 568.1 | 572.2 | 632.7 | 566 | 461.6
2067 | 1946 | 270.8 | 585.4 | 568 | 572.2 | 632.9 | 564.9 | 461.3
2068 | 1947 | 270.4 | 585.4 | 567.9 | 572.2 | 633 | 563.4 | 461.1
2069 | 1948 | 270.1 | 585.4 | 567.9 | 572.1 | 633.3 | 561.9 | 460.9
2070 | 1949 | 269.7 | 585.4 | 568 | 572.1 | 633.3 | 560.7 | 460.7
2071 | 1950 | 269.3 | 585.4 | 568.1 | 572.2 | 633.4 | 559.3 | 460.4
2072 | 1951 | 269 | 585.4 | 568.3 | 572.2 | 633.4 | 557.6 | 460.2
2073 | 1952 | 268.8 | 585.4 | 568.4 | 572.2 | 633.2 | 556.5 | 460.1
2074 | 1953 | 268.6 | 585.4 | 568.6 | 572.2 | 632.9 | 555.7 | 459.7
2075 | 1954 | 268.2 | 585.4 | 568.8 | 572.2 | 632.6 | 554.3 | 459.6
2076 | 1955 | 267.8 | 585.4 | 569 | 572.2 | 632.4 | 552.7 | 459.3
2077 | 1956 | 267.5 | 585.4 | 569.1 | 572.2 | 632.2 | 551.1 | 459
2078 | 1957 | 267.1 | 585.5 | 569.4 | 572.2 | 632.1 | 550 | 458.7
2079 | 1958 | 266.7 | 585.5 | 569.6 | 572.2 | 632 | 549.1 | 458.4
2080 | 1959 | 266.5 | 585.5 | 569.8 | 572.2 | 631.9 | 548.1 | 458.3
2081 | 1960 | 266.2 | 585.4 | 569.9 | 572.1 | 631.9 | 547.1 | 457.9
2082 | 1961 | 265.8 | 585.5 | 570.2 | 572.1 | 631.8 | 545.4 | 457.7
2083 | 1962 | 265.5 | 585.4 | 570.5 | 572.1 | 631.8 | 543.9 | 457.3
2084 | 1963 | 265.1 | 585.4 | 570.9 | 572.1 | 631.9 | 542.2 | 457
2085 | 1964 | 264.8 | 585.5 | 571.2 | 572.1 | 631.9 | 540.7 | 456.9
2086 | 1965 | 264.5 | 585.5 | 571.7 | 572.1 | 631.8 | 539.4 | 456.7
2087 | 1966 | 264.2 | 585.5 | 572.2 | 572.1 | 631.6 | 538 | 456.5
2088 | 1967 | 263.8 | 585.5 | 572.7 | 572.1 | 631.5 | 536.9 | 456.3
2089 | 1968 | 263.4 | 585.6 | 573.3 | 572.1 | 631.4 | 535.9 | 456.1
2090 | 1969 | 263 | 585.6 | 573.9 | 572.1 | 631.3 | 535 | 455.8
2091 | 1970 | 262.7 | 585.6 | 574.4 | 572 | 631.2 | 534.2 | 455.6
2092 | 1971 | 262.4 | 585.7 | 574.9 | 572 | 631.1 | 533.2 | 455.4
2093 | 1972 | 262.1 | 585.7 | 575.4 | 572 | 631 | 532.3 | 455
2094 | 1973 | 261.8 | 585.7 | 575.9 | 571.9 | 630.7 | 531.1 | 454.8
2095 | 1974 | 261.5 | 585.8 | 576.5 | 571.9 | 630.5 | 529.5 | 454.7
2096 | 1975 | 261.2 | 585.8 | 577.1 | 571.8 | 630.3 | 528 | 454.3
2097 | 1976 | 260.9 | 585.8 | 577.5 | 571.8 | 630 | 526.8 | 453.9
2098 | 1977 | 260.6 | 585.8 | 578 | 571.8 | 629.7 | 525.6 | 453.5
2099 | 1978 | 260.4 | 585.9 | 578.4 | 571.8 | 629.6 | 524.4 | 453.2
2100 | 1979 | 260.1 | 585.9 | 578.9 | 571.7 | 629.4 | 523.4 | 452.9
2101 | 1980 | 259.9 | 585.9 | 579.3 | 571.7 | 629.3 | 522.2 | 452.4
2102 | 1981 | 259.6 | 585.9 | 579.5 | 571.7 | 629.3 | 520.8 | 452.1
2103 | 1982 | 259.2 | 585.9 | 579.8 | 571.6 | 629.4 | 519.3 | 451.9
2104 | 1983 | 258.8 | 585.9 | 580.2 | 571.6 | 629.4 | 517.8 | 451.4
2105 | 1984 | 258.5 | 585.9 | 580.5 | 571.6 | 629.4 | 516.5 | 451.1
2106 | 1985 | 258.1 | 585.9 | 580.8 | 571.6 | 629.5 | 515.3 | 450.9
2107 | 1986 | 257.8 | 585.8 | 581 | 571.5 | 629.6 | 514.2 | 450.7
2108 | 1987 | 257.4 | 585.8 | 581.1 | 571.5 | 629.6 | 512.7 | 450.3
2109 | 1988 | 257 | 585.8 | 581.3 | 571.4 | 629.5 | 511.1 | 450.2
2110 | 1989 | 256.7 | 585.8 | 581.5 | 571.4 | 629.5 | 509.9 | 450
2111 | 1990 | 256.3 | 585.8 | 581.9 | 571.4 | 629.4 | 508.7 | 449.8
2112 | 1991 | 256.1 | 585.8 | 582.4 | 571.3 | 629.2 | 507.3 | 449.5
2113 | 1992 | 255.9 | 585.8 | 582.8 | 571.3 | 629 | 505.8 | 449.4
2114 | 1993 | 255.5 | 585.8 | 583.1 | 571.3 | 628.9 | 504.4 | 449
2115 | 1994 | 255.1 | 585.8 | 583.4 | 571.3 | 628.8 | 502.9 | 448.7
2116 | 1995 | 254.8 | 585.8 | 583.8 | 571.3 | 628.5 | 501.6 | 448.4
2117 | 1996 | 254.5 | 585.8 | 584.3 | 571.3 | 628.2 | 500.4 | 448
2118 | 1997 | 254.2 | 585.8 | 584.5 | 571.3 | 627.8 | 499.4 | 447.7
2119 | 1998 | 253.9 | 585.8 | 584.8 | 571.3 | 627.6 | 498.1 | 447.5
2120 | 1999 | 253.6 | 585.7 | 585 | 571.2 | 627.4 | 496.5 | 447.2
2121 | 2000 | 253.4 | 585.7 | 585.2 | 571.2 | 627.4 | 495.1 | 447
2122 | 2001 | 253.1 | 585.7 | 585.4 | 571.2 | 627.4 | 493.8 | 446.5
2123 | 2002 | 252.8 | 585.6 | 585.4 | 571.2 | 627.4 | 492.5 | 446
2124 | 2003 | 252.4 | 585.6 | 585.4 | 571.2 | 627.3 | 491.2 | 445.7
2125 | 2004 | 252.1 | 585.5 | 585.4 | 571.2 | 627.2 | 489.9 | 445.4
2126 | 2005 | 251.8 | 585.4 | 585.6 | 571.1 | 627.1 | 488.5 | 445.2
2127 | 2006 | 251.5 | 585.4 | 585.7 | 571.1 | 626.9 | 487.3 | 445
2128 | 2007 | 251.2 | 585.3 | 585.8 | 571.1 | 626.9 | 485.9 | 444.7
2129 | 2008 | 250.9 | 585.3 | 585.8 | 571.1 | 627 | 484.5 | 444.3
2130 | 2009 | 250.6 | 585.2 | 585.8 | 571.1 | 627 | 483.2 | 443.9
2131 | 2010 | 250.3 | 585.2 | 586.1 | 571.1 | 626.9 | 482 | 443.5
2132 | 2011 | 249.9 | 585.2 | 586.3 | 571.1 | 626.7 | 480.8 | 443.1
2133 | 2012 | 249.5 | 585.2 | 586.5 | 571.1 | 626.5 | 479.6 | 442.8
2134 | 2013 | 249.2 | 585.2 | 586.7 | 571.1 | 626.3 | 478.5 | 442.4
2135 | 2014 | 248.9 | 585.1 | 586.9 | 571.1 | 626 | 477.3 | 442
2136 | 2015 | 248.6 | 585.1 | 586.8 | 571 | 625.9 | 476.2 | 441.7
2137 | 2016 | 248.4 | 585.1 | 587 | 571 | 625.8 | 475.2 | 441.5
2138 | 2017 | 248.1 | 585.1 | 587 | 571 | 625.8 | 474.1 | 441.1
2139 | 2018 | 247.9 | 585 | 587 | 570.9 | 625.8 | 473.1 | 440.8
2140 | 2019 | 247.6 | 585 | 587 | 570.8 | 625.7 | 472.2 | 440.5
2141 | 2020 | 247.3 | 585 | 587 | 570.8 | 625.6 | 471.2 | 440.1
2142 | 2021 | 247.1 | 585 | 586.8 | 570.7 | 625.5 | 470.2 | 439.8
2143 | 2022 | 246.8 | 584.9 | 586.7 | 570.7 | 625.5 | 469.2 | 439.5
2144 | 2023 | 246.5 | 584.9 | 586.7 | 570.7 | 625.4 | 468.3 | 439.3
2145 | 2024 | 246.1 | 584.9 | 586.7 | 570.6 | 625.2 | 467.3 | 439.1
2146 | 2025 | 245.7 | 584.9 | 586.8 | 570.6 | 625.1 | 466.4 | 438.8
2147 | 2026 | 245.4 | 584.9 | 586.8 | 570.6 | 625 | 465.5 | 438.6
2148 | 2027 | 245 | 584.9 | 586.7 | 570.6 | 624.9 | 464.6 | 438.4
2149 | 2028 | 244.7 | 584.9 | 586.9 | 570.6 | 624.5 | 463.7 | 438
2150 | 2029 | 244.5 | 584.9 | 587 | 570.5 | 624.2 | 462.8 | 437.3
2151 | 2030 | 244.2 | 584.9 | 587.1 | 570.5 | 623.8 | 462 | 437.1
2152 | 2031 | 244 | 584.9 | 587.2 | 570.4 | 623.4 | 461.2 | 436.8
2153 | 2032 | 243.7 | 584.9 | 587.1 | 570.4 | 623 | 460.3 | 436.5
2154 | 2033 | 243.4 | 584.9 | 587.2 | 570.3 | 622.7 | 459.5 | 436.3
2155 | 2034 | 243.2 | 584.9 | 587.3 | 570.3 | 622.4 | 458.7 | 436
2156 | 2035 | 242.9 | 584.9 | 587.5 | 570.3 | 622.2 | 457.8 | 435.7
2157 | 2036 | 242.6 | 584.8 | 587.6 | 570.2 | 621.9 | 457 | 435.4
2158 | 2037 | 242.2 | 584.8 | 587.4 | 570.2 | 621.6 | 456.2 | 435.1
2159 | 2038 | 241.9 | 584.7 | 587.4 | 570.2 | 621.3 | 455.5 | 434.7
2160 | 2039 | 241.7 | 584.7 | 587.6 | 570.1 | 621 | 454.7 | 434.2
2161 | 2040 | 241.5 | 584.6 | 587.8 | 570 | 620.7 | 453.9 | 433.6
2162 | 2041 | 241.3 | 584.6 | 587.8 | 570 | 620.7 | 453.1 | 433.2
2163 | 2042 | 241 | 584.5 | 587.5 | 569.9 | 620.7 | 452.1 | 432.8
2164 | 2043 | 240.7 | 584.5 | 587.3 | 569.9 | 621 | 451.2 | 432.4
2165 | 2044 | 240.3 | 584.4 | 587.2 | 569.8 | 621.1 | 450.5 | 432
2166 | 2045 | 239.8 | 584.3 | 587 | 569.8 | 621.3 | 449.8 | 431.4
2167 | 2046 | 239.5 | 584.3 | 586.8 | 569.7 | 621.5 | 449.1 | 431.3
2168 | 2047 | 239.1 | 584.3 | 586.8 | 569.7 | 621.5 | 448.5 | 430.8
2169 | 2048 | 238.9 | 584.2 | 586.7 | 569.6 | 621.5 | 447.9 | 430.5
2170 | 2049 | 238.7 | 584.1 | 586.4 | 569.6 | 621.5 | 447.1 | 430.3
2171 | 2050 | 238.4 | 584.1 | 586.3 | 569.5 | 621.6 | 446.5 | 430.1
2172 | 2051 | 238.1 | 584 | 586.4 | 569.5 | 621.6 | 445.9 | 429.7
2173 | 2052 | 237.8 | 584 | 586.3 | 569.5 | 621.5 | 445.3 | 429.4
2174 | 2053 | 237.7 | 583.9 | 586.1 | 569.5 | 621.4 | 444.7 | 429.1
2175 | 2054 | 237.4 | 583.9 | 585.9 | 569.5 | 621.4 | 444.2 | 428.8
2176 | 2055 | 237.2 | 583.8 | 585.9 | 569.4 | 621.3 | 443.7 | 428.4
2177 | 2056 | 237 | 583.7 | 586 | 569.4 | 621.2 | 443 | 428
2178 | 2057 | 236.7 | 583.7 | 586.1 | 569.4 | 620.9 | 442.4 | 427.6
2179 | 2058 | 236.5 | 583.6 | 586.2 | 569.3 | 620.5 | 442 | 427.3
2180 | 2059 | 236.1 | 583.6 | 586.3 | 569.2 | 620.2 | 441.5 | 427.1
2181 | 2060 | 235.9 | 583.5 | 586.4 | 569.1 | 620 | 440.9 | 426.8
2182 | 2061 | 235.6 | 583.5 | 586.5 | 569.1 | 619.9 | 440.2 | 426.5
2183 | 2062 | 235.4 | 583.5 | 586.6 | 569 | 619.7 | 439.6 | 426.1
2184 | 2063 | 235.1 | 583.4 | 586.7 | 568.9 | 619.5 | 439 | 425.7
2185 | 2064 | 234.8 | 583.4 | 586.8 | 568.8 | 619.3 | 438.6 | 425.4
2186 | 2065 | 234.6 | 583.4 | 586.8 | 568.8 | 619 | 438.2 | 425.1
2187 | 2066 | 234.4 | 583.4 | 586.8 | 568.7 | 618.9 | 437.6 | 424.7
2188 | 2067 | 234 | 583.3 | 586.8 | 568.6 | 618.6 | 437.1 | 424.2
2189 | 2068 | 233.7 | 583.3 | 586.6 | 568.6 | 618.6 | 436.6 | 423.6
2190 | 2069 | 233.4 | 583.2 | 586.4 | 568.5 | 618.5 | 436.1 | 423.1
2191 | 2070 | 233.1 | 583.1 | 586.1 | 568.4 | 618.3 | 435.7 | 422.7
2192 | 2071 | 232.9 | 582.9 | 585.8 | 568.4 | 618.2 | 435.1 | 422.3
2193 | 2072 | 232.6 | 582.8 | 585.8 | 568.3 | 618 | 434.6 | 422.1
2194 | 2073 | 232.4 | 582.8 | 585.9 | 568.3 | 617.9 | 434.1 | 422
2195 | 2074 | 232.1 | 582.7 | 586 | 568.1 | 617.7 | 433.6 | 421.7
2196 | 2075 | 231.8 | 582.6 | 586 | 568.1 | 617.6 | 433.1 | 421.5
2197 | 2076 | 231.5 | 582.5 | 586.1 | 567.9 | 617.4 | 432.6 | 421.2
2198 | 2077 | 231.2 | 582.5 | 586.1 | 567.8 | 617.2 | 432.1 | 421.1
2199 | 2078 | 230.9 | 582.4 | 585.9 | 567.7 | 616.9 | 431.6 | 420.6
2200 | 2079 | 230.6 | 582.3 | 585.6 | 567.6 | 616.9 | 431.2 | 420.2
2201 | 2080 | 230.3 | 582.2 | 585.6 | 567.5 | 616.8 | 430.8 | 419.6
2202 | 2081 | 230.1 | 582.1 | 585.5 | 567.4 | 616.6 | 430.4 | 419.3
2203 | 2082 | 229.8 | 582 | 585.5 | 567.3 | 616.5 | 429.9 | 419
2204 | 2083 | 229.6 | 581.9 | 585.4 | 567.2 | 616.4 | 429.4 | 418.7
2205 | 2084 | 229.4 | 581.8 | 585.1 | 567.1 | 616.3 | 428.9 | 418.3
2206 | 2085 | 229.1 | 581.7 | 584.9 | 567 | 616.4 | 428.6 | 417.9
2207 | 2086 | 228.8 | 581.6 | 585 | 566.9 | 616.3 | 428.2 | 417.5
2208 | 2087 | 228.6 | 581.6 | 585 | 566.8 | 616.1 | 427.7 | 417.3
2209 | 2088 | 228.3 | 581.5 | 584.9 | 566.7 | 615.9 | 427.2 | 417
2210 | 2089 | 228 | 581.4 | 585 | 566.6 | 615.5 | 426.6 | 416.7
2211 | 2090 | 227.8 | 581.4 | 585.1 | 566.5 | 615.3 | 426.2 | 416.2
2212 | 2091 | 227.6 | 581.3 | 585.2 | 566.4 | 615.3 | 425.9 | 415.8
2213 | 2092 | 227.3 | 581.2 | 585.1 | 566.3 | 615.3 | 425.4 | 415.4
2214 | 2093 | 227.1 | 581.2 | 585.1 | 566.3 | 615.1 | 424.8 | 414.9
2215 | 2094 | 226.9 | 581.1 | 585.1 | 566.2 | 615 | 424.3 | 414.5
2216 | 2095 | 226.6 | 581.1 | 584.9 | 566.1 | 614.6 | 423.7 | 414.2
2217 | 2096 | 226.3 | 581 | 584.5 | 566 | 614.4 | 423.2 | 413.9
2218 | 2097 | 226.1 | 580.9 | 584.3 | 566 | 614.2 | 422.7 | 413.7
2219 | 2098 | 225.9 | 580.8 | 584.2 | 565.9 | 613.9 | 422.2 | 413.4
2220 | 2099 | 225.6 | 580.8 | 583.8 | 565.8 | 613.6 | 421.9 | 413.1
2221 | 2100 | 225.3 | 580.7 | 583.4 | 565.7 | 613.2 | 421.6 | 412.9
2222 | 2101 | 225.1 | 580.7 | 583.1 | 565.6 | 612.5 | 421.2 | 412.5
2223 | 2102 | 224.9 | 580.6 | 582.9 | 565.4 | 611.8 | 420.8 | 411.9
2224 | 2103 | 224.7 | 580.5 | 582.9 | 565.3 | 611.2 | 420.5 | 411.3
2225 | 2104 | 224.4 | 580.5 | 582.7 | 565.2 | 610.6 | 420 | 411
2226 | 2105 | 224 | 580.4 | 582.7 | 565.1 | 610.1 | 419.6 | 410.8
2227 | 2106 | 223.7 | 580.3 | 582.5 | 565 | 609.3 | 419.2 | 410.2
2228 | 2107 | 223.4 | 580.2 | 582.3 | 564.9 | 608.6 | 418.6 | 410
2229 | 2108 | 223 | 580.1 | 581.9 | 564.8 | 608 | 418 | 409.6
2230 | 2109 | 222.7 | 580 | 581.6 | 564.6 | 607.1 | 417.5 | 409.2
2231 | 2110 | 222.5 | 579.9 | 581.6 | 564.5 | 606 | 417 | 408.6
2232 | 2111 | 222.3 | 579.8 | 581.6 | 564.3 | 605.1 | 416.5 | 408.3
2233 | 2112 | 222 | 579.7 | 581.3 | 564.2 | 604.3 | 415.9 | 407.9
2234 | 2113 | 221.8 | 579.5 | 581.2 | 564.1 | 603.5 | 415.6 | 407.4
2235 | 2114 | 221.6 | 579.3 | 580.8 | 564 | 602.6 | 415.2 | 407.2
2236 | 2115 | 221.3 | 579.1 | 580.4 | 563.9 | 601.8 | 414.7 | 406.8
2237 | 2116 | 221.1 | 579 | 579.9 | 563.8 | 601 | 414.1 | 406.6
2238 | 2117 | 220.8 | 578.8 | 579.7 | 563.7 | 600.1 | 413.7 | 406.2
2239 | 2118 | 220.5 | 578.7 | 579.5 | 563.7 | 599.2 | 413.3 | 405.9
2240 | 2119 | 220.2 | 578.6 | 579.3 | 563.6 | 598.1 | 413 | 405.6
2241 | 2120 | 220 | 578.5 | 579.2 | 563.5 | 596.9 | 412.6 | 405.3
2242 | 2121 | 219.7 | 578.3 | 579 | 563.4 | 595.6 | 412 | 405.1
2243 | 2122 | 219.5 | 578.2 | 578.8 | 563.3 | 594.3 | 411.6 | 404.8
2244 | 2123 | 219.3 | 578.2 | 578.4 | 563.2 | 593.1 | 411.1 | 404.5
2245 | 2124 | 219.1 | 578 | 578.1 | 563.1 | 591.9 | 410.7 | 404.3
2246 | 2125 | 218.8 | 577.9 | 577.8 | 562.9 | 590.8 | 410.3 | 404.2
2247 | 2126 | 218.6 | 577.8 | 577.4 | 562.8 | 589.6 | 409.8 | 403.9
2248 | 2127 | 218.4 | 577.7 | 577.1 | 562.7 | 588.4 | 409.4 | 403.5
2249 | 2128 | 218.1 | 577.6 | 576.7 | 562.6 | 587.3 | 408.9 | 403.1
2250 | 2129 | 217.9 | 577.4 | 576.1 | 562.5 | 586.2 | 408.5 | 402.7
2251 | 2130 | 217.7 | 577.3 | 575.4 | 562.3 | 585.1 | 408 | 402.3
2252 | 2131 | 217.4 | 577.2 | 574.6 | 562.2 | 584 | 407.6 | 402
2253 | 2132 | 217.2 | 577 | 573.7 | 562.1 | 583 | 407.1 | 401.5
2254 | 2133 | 217 | 576.8 | 573.1 | 561.9 | 581.9 | 406.6 | 401.2
2255 | 2134 | 216.7 | 576.6 | 572.5 | 561.7 | 580.8 | 406 | 400.9
2256 | 2135 | 216.5 | 576.4 | 571.8 | 561.6 | 579.8 | 405.5 | 400.5
2257 | 2136 | 216.2 | 576.3 | 571.1 | 561.4 | 578.7 | 404.9 | 400.2
2258 | 2137 | 215.9 | 576.2 | 570.3 | 561.2 | 577.7 | 404.3 | 399.7
2259 | 2138 | 215.6 | 576.1 | 569.4 | 561 | 576.7 | 403.6 | 399.4
2260 | 2139 | 215.3 | 576 | 568.3 | 560.8 | 575.7 | 403 | 399.1
2261 | 2140 | 215 | 575.8 | 567.8 | 560.6 | 574.5 | 402.3 | 398.8
2262 | 2141 | 214.7 | 575.7 | 567.1 | 560.5 | 573.6 | 401.6 | 398.2
2263 | 2142 | 214.5 | 575.5 | 566.4 | 560.3 | 572.8 | 401.1 | 397.5
2264 | 2143 | 214.2 | 575.4 | 565.6 | 560.2 | 571.9 | 400.6 | 397.1
2265 | 2144 | 213.9 | 575.2 | 564.8 | 560 | 571 | 400.3 | 396.7
2266 | 2145 | 213.7 | 575.1 | 563.7 | 559.9 | 570.1 | 400.1 | 396.3
2267 | 2146 | 213.6 | 575 | 562.7 | 559.7 | 569.1 | 399.9 | 396
2268 | 2147 | 213.4 | 574.9 | 561.9 | 559.6 | 568.2 | 399.6 | 395.6
2269 | 2148 | 213.2 | 574.7 | 560.8 | 559.5 | 567.2 | 399 | 395.2
2270 | 2149 | 212.9 | 574.5 | 559.9 | 559.3 | 566.3 | 398.2 | 394.8

## C6-7
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38930.4095 | 1 | 0 | 38930.4096 | 1 | 0 | -64 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4102 | 1 | 0 | 38930.4102 | 1 | 0 | -5.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4109 | 1 | 0 | 38930.4109 | 1 | 0 | 53.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4116 | 1 | 0 | 38930.4116 | 1 | 0 | 112.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4123 | 1 | 0 | 38930.4123 | 1 | 0 | 171 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4129 | 1 | 0 | 38930.413 | 1 | 0 | 230 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4136 | 1 | 0 | 38930.4136 | 1 | 0 | 288.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4143 | 1 | 0 | 38930.4143 | 1 | 0 | 347.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.415 | 1 | 0 | 38930.415 | 1 | 0 | 406.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4157 | 1 | 0 | 38930.4157 | 1 | 0 | 465 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4163 | 1 | 0 | 38930.4164 | 1 | 0 | 524 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.417 | 1 | 0 | 38930.417 | 1 | 0 | 582.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4177 | 1 | 0 | 38930.4177 | 1 | 0 | 641.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4184 | 1 | 0 | 38930.4184 | 1 | 0 | 700.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4191 | 1 | 0 | 38930.4191 | 1 | 0 | 759 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4197 | 1 | 0 | 38930.4198 | 1 | 0 | 817.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4204 | 1 | 0 | 38930.4204 | 1 | 0 | 876.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4211 | 1 | 0 | 38930.4211 | 1 | 0 | 935.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4218 | 1 | 0 | 38930.4218 | 1 | 0 | 994.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4225 | 1 | 0 | 38930.4225 | 1 | 0 | 1053 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4231 | 1 | 0 | 38930.4232 | 1 | 0 | 1111.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4238 | 1 | 0 | 38930.4238 | 1 | 0 | 1170.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4245 | 1 | 0 | 38930.4245 | 1 | 0 | 1229.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4252 | 1 | 0 | 38930.4252 | 1 | 0 | 1288 | 1409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4259 | 1 | 0 | 38930.4259 | 1 | 0 | 1347 | 1468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4266 | 1174 | 1175 | 38930.4266 | 1039 | 1008 | 1405.5 | 1526.5 | 71.6728 | 71.7338 | 63.431 | 61.5385 | 0.71673 | 0.71734 | 0.63431 | 0.61538 | 0.0006105 | 0.018926 | 497.5074 | 625.8491 | 17.3165
38930.4272 | 1168 | 1187 | 38930.4272 | 1058 | 1027 | 1464.5 | 1585.5 | 71.3065 | 72.4664 | 64.591 | 62.6984 | 0.71306 | 0.72466 | 0.64591 | 0.62698 | 0.0116 | 0.018926 | 1325.4479 | 2269.6783 | 19.5256
38930.4279 | 1070 | 975 | 38930.4279 | 976 | 936 | 1523.5 | 1644.5 | 65.3236 | 59.5238 | 59.5849 | 57.1429 | 0.65324 | 0.59524 | 0.59585 | 0.57143 | 0.057998 | 0.02442 | 396.0401 | 579.1085 | 5.9491
38930.4286 | 1196 | 1173 | 38930.4286 | 1043 | 954 | 1582 | 1703 | 73.0159 | 71.6117 | 63.6752 | 58.2418 | 0.73016 | 0.71612 | 0.63675 | 0.58242 | 0.014042 | 0.054335 | 172.7262 | 230.9466 | 15.2287
38930.4293 | 1171 | 1188 | 38930.4293 | 1082 | 1006 | 1641 | 1762 | 71.4896 | 72.5275 | 66.0562 | 61.4164 | 0.7149 | 0.72527 | 0.66056 | 0.61416 | 0.010379 | 0.046398 | 307.7027 | 410.8649 | 16.6524
38930.43 | 930 | 1017 | 38930.43 | 1082 | 1108 | 1699.5 | 1820.5 | 56.7766 | 62.0879 | 66.0562 | 67.6435 | 0.56777 | 0.62088 | 0.66056 | 0.67643 | 0.053114 | 0.015873 | 146.8322 | 141.5065 | 9.565
38930.4306 | 952 | 1053 | 38930.4306 | 1091 | 837 | 1758.5 | 1879.5 | 58.1197 | 64.2857 | 66.6056 | 51.0989 | 0.5812 | 0.64286 | 0.66606 | 0.51099 | 0.061661 | 0.15507 | 185.8429 | 201.0571 | 6.8509
38930.4313 | 983 | 879 | 38930.4313 | 1108 | 1042 | 1817.5 | 1938.5 | 60.0122 | 53.663 | 67.6435 | 63.6142 | 0.60012 | 0.53663 | 0.67643 | 0.63614 | 0.063492 | 0.040293 | 472.5517 | 650.4773 | 24.7522
38930.432 | 1155 | 1107 | 38930.432 | 1141 | 839 | 1876 | 1997 | 70.5128 | 67.5824 | 69.6581 | 51.221 | 0.70513 | 0.67582 | 0.69658 | 0.51221 | 0.029304 | 0.18437 | 0.84879 | 0.9812 | 0.13077
38930.4327 | 1156 | 1187 | 38930.4327 | 966 | 860 | 1935 | 2056 | 70.5739 | 72.4664 | 58.9744 | 52.5031 | 0.70574 | 0.72466 | 0.58974 | 0.52503 | 0.018926 | 0.064713 | 85.1954 | 108.6674 | 10.0898
38930.4334 | 996 | 997 | 38930.4334 | 976 | 887 | 1993.5 | 2114.5 | 60.8059 | 60.8669 | 59.5849 | 54.1514 | 0.60806 | 0.60867 | 0.59585 | 0.54151 | 0.0006105 | 0.054335 | 440.3571 | 394.5978 | 9.6042
38930.434 | 948 | 845 | 38930.4341 | 1092 | 1025 | 2052.5 | 2173.5 | 57.8755 | 51.5873 | 66.6667 | 62.5763 | 0.57875 | 0.51587 | 0.66667 | 0.62576 | 0.062882 | 0.040904 | 666.083 | 1175.1434 | 34.9022
38930.4347 | 1075 | 853 | 38930.4347 | 1149 | 1185 | 2111 | 2232 | 65.6288 | 52.0757 | 70.1465 | 72.3443 | 0.65629 | 0.52076 | 0.70147 | 0.72344 | 0.13553 | 0.021978 | 5.5279 | 4.597 | 0.95328
38930.4354 | 1048 | 974 | 38930.4354 | 1034 | 955 | 2170 | 2291 | 63.9805 | 59.4628 | 63.1258 | 58.3028 | 0.6398 | 0.59463 | 0.63126 | 0.58303 | 0.045177 | 0.04823 | 7548.1437 | 1626.3066 | 8.8036

## C5-7
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38930.4095 | 1 | 0 | 38930.4095 | 1 | 0 | -66.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4102 | 1 | 0 | 38930.4102 | 1 | 0 | -8 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4109 | 1 | 0 | 38930.4109 | 1 | 0 | 50.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4116 | 1 | 0 | 38930.4116 | 1 | 0 | 109.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4122 | 1 | 0 | 38930.4122 | 1 | 0 | 168.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4129 | 1 | 0 | 38930.4129 | 1 | 0 | 227 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4136 | 2 | 0 | 38930.4136 | 1 | 0 | 286 | 407 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38930.4143 | 1 | 0 | 38930.4143 | 1 | 0 | 344.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.415 | 1 | 0 | 38930.415 | 1 | 0 | 403.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4156 | 1 | 0 | 38930.4156 | 1 | 0 | 462.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4163 | 1 | 0 | 38930.4163 | 1 | 0 | 521 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.417 | 1 | 0 | 38930.417 | 1 | 0 | 580 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4177 | 1 | 0 | 38930.4177 | 1 | 0 | 638.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4184 | 2 | 0 | 38930.4184 | 1 | 0 | 697.5 | 818.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38930.419 | 1 | 0 | 38930.4191 | 1 | 0 | 756.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4197 | 1 | 0 | 38930.4197 | 1 | 0 | 815 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4204 | 1 | 0 | 38930.4204 | 1 | 0 | 874 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4211 | 1 | 0 | 38930.4211 | 1 | 0 | 932.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4218 | 1 | 0 | 38930.4218 | 1 | 0 | 991.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4224 | 1 | 0 | 38930.4225 | 1 | 0 | 1050.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4231 | 1 | 0 | 38930.4231 | 1 | 0 | 1109 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4238 | 1 | 0 | 38930.4238 | 1 | 0 | 1167.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4245 | 1 | 0 | 38930.4245 | 1 | 0 | 1226.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4252 | 1 | 0 | 38930.4252 | 1 | 0 | 1285.5 | 1406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4258 | 1 | 0 | 38930.4259 | 1 | 0 | 1344 | 1465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4265 | 945 | 910 | 38930.4265 | 1065 | 1127 | 1403 | 1524 | 57.6923 | 55.5556 | 65.0183 | 68.8034 | 0.57692 | 0.55556 | 0.65018 | 0.68803 | 0.021368 | 0.037851 | 1005.8022 | 1121.6815 | 26.033
38930.4272 | 966 | 931 | 38930.4272 | 1049 | 1020 | 1461.5 | 1582.5 | 58.9744 | 56.8376 | 64.0415 | 62.2711 | 0.58974 | 0.56838 | 0.64042 | 0.62271 | 0.021368 | 0.017705 | 2644.4069 | 11115.9907 | 22.9961
38930.4279 | 1132 | 1093 | 38930.4279 | 1172 | 1132 | 1520.5 | 1641.5 | 69.1087 | 66.7277 | 71.5507 | 69.1087 | 0.69109 | 0.66728 | 0.71551 | 0.69109 | 0.02381 | 0.02442 | 4474.4546 | 6401.1363 | 10.0876
38930.4286 | 935 | 830 | 38930.4286 | 964 | 1065 | 1579.5 | 1700.5 | 57.0818 | 50.6716 | 58.8523 | 65.0183 | 0.57082 | 0.50672 | 0.58852 | 0.65018 | 0.064103 | 0.061661 | 1275.5446 | 6563.4833 | 41.3009
38930.4292 | 980 | 871 | 38930.4293 | 1111 | 1045 | 1638 | 1759 | 59.8291 | 53.1746 | 67.8266 | 63.7973 | 0.59829 | 0.53175 | 0.67827 | 0.63797 | 0.066545 | 0.040293 | 435.1353 | 575.3605 | 25.6284
38930.4299 | 974 | 868 | 38930.4299 | 1191 | 1161 | 1697 | 1818 | 59.4628 | 52.9915 | 72.7106 | 70.8791 | 0.59463 | 0.52991 | 0.72711 | 0.70879 | 0.064713 | 0.018315 | 59.2116 | 47.7541 | 10.0914
38930.4306 | 1002 | 1099 | 38930.4306 | 1154 | 1104 | 1755.5 | 1876.5 | 61.1722 | 67.094 | 70.4518 | 67.3993 | 0.61172 | 0.67094 | 0.70452 | 0.67399 | 0.059219 | 0.030525 | 388.1965 | 580.8656 | 0.93308
38930.4313 | 1171 | 1131 | 38930.4313 | 1121 | 1172 | 1814.5 | 1935.5 | 71.4896 | 69.0476 | 68.4371 | 71.5507 | 0.7149 | 0.69048 | 0.68437 | 0.71551 | 0.02442 | 0.031136 | 2172.361 | 33621.8912 | 16.6596
38930.432 | 1188 | 1162 | 38930.432 | 1137 | 1179 | 1873.5 | 1994.5 | 72.5275 | 70.9402 | 69.4139 | 71.978 | 0.72527 | 0.7094 | 0.69414 | 0.71978 | 0.015873 | 0.025641 | 1994.0684 | 5699.2692 | 20.0425
38930.4326 | 997 | 1096 | 38930.4327 | 1038 | 859 | 1932 | 2053 | 60.8669 | 66.9109 | 63.37 | 52.442 | 0.60867 | 0.66911 | 0.6337 | 0.52442 | 0.06044 | 0.10928 | 287.7545 | 379.452 | 1.4457
38930.4333 | 1180 | 1152 | 38930.4333 | 1172 | 1138 | 1991 | 2112 | 72.0391 | 70.3297 | 71.5507 | 69.475 | 0.72039 | 0.7033 | 0.71551 | 0.69475 | 0.017094 | 0.020757 | 3377.5697 | 306386.5834 | 19.0025
38930.434 | 984 | 889 | 38930.434 | 1055 | 978 | 2049.5 | 2170.5 | 60.0733 | 54.2735 | 64.4078 | 59.707 | 0.60073 | 0.54274 | 0.64408 | 0.59707 | 0.057998 | 0.047009 | 1014.0203 | 5440.3132 | 26.5116
38930.4347 | 1053 | 1077 | 38930.4347 | 1074 | 1150 | 2108.5 | 2229.5 | 64.2857 | 65.7509 | 65.5678 | 70.2076 | 0.64286 | 0.65751 | 0.65568 | 0.70208 | 0.014652 | 0.046398 | 241.0028 | 258.9956 | 1.1374
38930.4354 | 1187 | 917 | 38930.4354 | 964 | 869 | 2167.5 | 2288.5 | 72.4664 | 55.9829 | 58.8523 | 53.0525 | 0.72466 | 0.55983 | 0.58852 | 0.53053 | 0.16484 | 0.057998 | 119.7302 | 182.1533 | 0.63502

## C5-6
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38930.4095 | 1 | 0 | 38930.4095 | 1 | 0 | -69.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4102 | 1 | 0 | 38930.4102 | 1 | 0 | -11 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4108 | 1 | 0 | 38930.4109 | 1 | 0 | 48 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4115 | 1 | 0 | 38930.4115 | 1 | 0 | 106.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4122 | 1 | 0 | 38930.4122 | 1 | 0 | 165.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4129 | 1 | 0 | 38930.4129 | 1 | 0 | 224.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4136 | 1 | 0 | 38930.4136 | 1 | 0 | 283 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4142 | 1 | 0 | 38930.4143 | 1 | 0 | 342 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4149 | 1 | 0 | 38930.4149 | 1 | 0 | 400.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4156 | 1 | 0 | 38930.4156 | 1 | 0 | 459.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4163 | 1 | 0 | 38930.4163 | 1 | 0 | 518.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.417 | 1 | 0 | 38930.417 | 1 | 0 | 577 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4176 | 1 | 0 | 38930.4177 | 1 | 0 | 636 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4183 | 1 | 0 | 38930.4183 | 1 | 0 | 694.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.419 | 1 | 0 | 38930.419 | 1 | 0 | 753.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4197 | 1 | 0 | 38930.4197 | 1 | 0 | 812.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4204 | 1 | 0 | 38930.4204 | 1 | 0 | 871 | 992 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.421 | 1 | 0 | 38930.4211 | 1 | 0 | 929.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4217 | 1 | 0 | 38930.4217 | 1 | 0 | 988.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4224 | 1 | 0 | 38930.4224 | 1 | 0 | 1047.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4231 | 1 | 0 | 38930.4231 | 1 | 0 | 1106 | 1227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4238 | 1 | 0 | 38930.4238 | 1 | 0 | 1165 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4244 | 1 | 0 | 38930.4245 | 1 | 0 | 1223.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4251 | 1 | 0 | 38930.4251 | 1 | 0 | 1282.5 | 1403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4258 | 1 | 0 | 38930.4258 | 1 | 0 | 1341.5 | 1462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4265 | 971 | 936 | 38930.4265 | 917 | 881 | 1400 | 1521 | 59.2796 | 57.1429 | 55.9829 | 53.7851 | 0.5928 | 0.57143 | 0.55983 | 0.53785 | 0.021368 | 0.021978 | 6629.3037 | 5266.37 | 21.6005
38930.4272 | 976 | 1082 | 38930.4272 | 982 | 946 | 1459 | 1580 | 59.5849 | 66.0562 | 59.9512 | 57.7534 | 0.59585 | 0.66056 | 0.59951 | 0.57753 | 0.064713 | 0.021978 | 324.2315 | 442.2074 | 4.1472
38930.4278 | 1110 | 1085 | 38930.4279 | 1163 | 1143 | 1517.5 | 1638.5 | 67.7656 | 66.2393 | 71.0012 | 69.7802 | 0.67766 | 0.66239 | 0.71001 | 0.6978 | 0.015263 | 0.01221 | 14009.5557 | 6081.6824 | 7.4335
38930.4285 | 952 | 836 | 38930.4285 | 1172 | 1188 | 1576.5 | 1697.5 | 58.1197 | 51.0379 | 71.5507 | 72.5275 | 0.5812 | 0.51038 | 0.71551 | 0.72527 | 0.070818 | 0.009768 | 103.7509 | 83.3462 | 17.6733
38930.4292 | 1031 | 936 | 38930.4292 | 949 | 833 | 1635.5 | 1756.5 | 62.9426 | 57.1429 | 57.9365 | 50.8547 | 0.62943 | 0.57143 | 0.57937 | 0.50855 | 0.057998 | 0.070818 | 23919.683 | 1034.5234 | 14.2254
38930.4299 | 1152 | 1100 | 38930.4299 | 1105 | 1169 | 1694 | 1815 | 70.3297 | 67.1551 | 67.4603 | 71.3675 | 0.7033 | 0.67155 | 0.6746 | 0.71368 | 0.031746 | 0.039072 | 1763.7398 | 44218.8015 | 12.606
38930.4306 | 1049 | 960 | 38930.4306 | 1010 | 914 | 1753 | 1874 | 64.0415 | 58.6081 | 61.6606 | 55.7998 | 0.64042 | 0.58608 | 0.61661 | 0.558 | 0.054335 | 0.058608 | 4929.3757 | 1424.0215 | 10.1244
38930.4313 | 1089 | 1122 | 38930.4313 | 1063 | 985 | 1811.5 | 1932.5 | 66.4835 | 68.4982 | 64.8962 | 60.1343 | 0.66484 | 0.68498 | 0.64896 | 0.60134 | 0.020147 | 0.047619 | 56.6127 | 63.1822 | 3.3812
38930.4319 | 965 | 877 | 38930.4319 | 1127 | 1072 | 1870.5 | 1991.5 | 58.9133 | 53.5409 | 68.8034 | 65.4457 | 0.58913 | 0.53541 | 0.68803 | 0.65446 | 0.053724 | 0.033578 | 497.8017 | 614.9296 | 26.5805
38930.4326 | 992 | 984 | 38930.4326 | 1133 | 1085 | 1929.5 | 2050.5 | 60.5617 | 60.0733 | 69.1697 | 66.2393 | 0.60562 | 0.60073 | 0.6917 | 0.66239 | 0.004884 | 0.029304 | 78.6509 | 69.4272 | 5.706
38930.4333 | 1176 | 1144 | 38930.4333 | 1124 | 1076 | 1988 | 2109 | 71.7949 | 69.8413 | 68.6203 | 65.6899 | 0.71795 | 0.69841 | 0.6862 | 0.6569 | 0.019536 | 0.029304 | 1307.6893 | 2884.9088 | 17.4865
38930.434 | 1157 | 1112 | 38930.434 | 984 | 973 | 2046.5 | 2167.5 | 70.6349 | 67.8877 | 60.0733 | 59.4017 | 0.70635 | 0.67888 | 0.60073 | 0.59402 | 0.027473 | 0.0067155 | 6.767 | 7.8962 | 1.0265
38930.4347 | 1165 | 1125 | 38930.4347 | 1024 | 942 | 2105.5 | 2226.5 | 71.1233 | 68.6813 | 62.5153 | 57.5092 | 0.71123 | 0.68681 | 0.62515 | 0.57509 | 0.02442 | 0.050061 | 56.1465 | 68.2448 | 6.3812
38930.4353 | 1178 | 1143 | 38930.4353 | 997 | 1096 | 2164.5 | 2285.5 | 71.917 | 69.7802 | 60.8669 | 66.9109 | 0.71917 | 0.6978 | 0.60867 | 0.66911 | 0.021368 | 0.06044 | 282.3717 | 385.9779 | 14.4518

## C4-7
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38930.4094 | 1 | 0 | 38930.4095 | 1 | 0 | -72.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4101 | 1 | 0 | 38930.4101 | 1 | 0 | -13.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4108 | 1 | 0 | 38930.4108 | 1 | 0 | 45 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4115 | 1 | 0 | 38930.4115 | 1 | 0 | 104 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4122 | 1 | 0 | 38930.4122 | 1 | 0 | 162.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4128 | 1 | 0 | 38930.4129 | 1 | 0 | 221.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4135 | 1 | 0 | 38930.4135 | 1 | 0 | 280.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4142 | 1 | 0 | 38930.4142 | 1 | 0 | 339 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4149 | 1 | 0 | 38930.4149 | 1 | 0 | 398 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4156 | 1 | 0 | 38930.4156 | 1 | 0 | 456.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4163 | 1 | 0 | 38930.4163 | 1 | 0 | 515.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4169 | 1 | 0 | 38930.4169 | 1 | 0 | 574.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4176 | 1 | 0 | 38930.4176 | 1 | 0 | 633 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4183 | 1 | 0 | 38930.4183 | 1 | 0 | 692 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.419 | 1 | 0 | 38930.419 | 1 | 0 | 750.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4197 | 1 | 0 | 38930.4197 | 1 | 0 | 809.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4203 | 1 | 0 | 38930.4203 | 1 | 0 | 868.5 | 989.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.421 | 1 | 0 | 38930.421 | 1 | 0 | 927 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4217 | 2 | 0 | 38930.4217 | 1 | 0 | 986 | 1107 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38930.4224 | 1 | 0 | 38930.4224 | 1 | 0 | 1044.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4231 | 1 | 0 | 38930.4231 | 1 | 0 | 1103.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4237 | 1 | 0 | 38930.4238 | 1 | 0 | 1162 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4244 | 1 | 0 | 38930.4244 | 1 | 0 | 1221 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4251 | 1 | 0 | 38930.4251 | 1 | 0 | 1279.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4258 | 1 | 0 | 38930.4258 | 1 | 0 | 1338.5 | 1459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4265 | 162 | 209 | 38930.4265 | 16 | 26 | 1397.5 | 1518.5 | 9.8901 | 12.7595 | 0.9768 | 1.5873 | 0.098901 | 0.12759 | 0.009768 | 0.015873 | 0.028694 | 0.006105 | 4235.4063 | 22341.6955 | 829.7883
38930.4271 | 203 | 194 | 38930.4272 | 173 | 178 | 1456 | 1577 | 12.3932 | 11.8437 | 10.5617 | 10.8669 | 0.12393 | 0.11844 | 0.10562 | 0.10867 | 0.0054945 | 0.0030525 | 22261.4004 | 46186.4471 | 882.6354
38930.4278 | 945 | 913 | 38930.4278 | 913 | 913 | 1515 | 1636 | 57.6923 | 55.7387 | 55.7387 | 55.7387 | 0.57692 | 0.55739 | 0.55739 | 0.55739 | 0.019536 | 0 | 1479.3461 | 1944.4084 | 26.5658
38930.4285 | 954 | 921 | 38930.4285 | 929 | 864 | 1573.5 | 1694.5 | 58.2418 | 56.2271 | 56.7155 | 52.7473 | 0.58242 | 0.56227 | 0.56716 | 0.52747 | 0.020147 | 0.039683 | 2772.9388 | 10468.8441 | 25.5991
38930.4292 | 1092 | 1150 | 38930.4292 | 1004 | 1094 | 1632.5 | 1753.5 | 66.6667 | 70.2076 | 61.2943 | 66.7888 | 0.66667 | 0.70208 | 0.61294 | 0.66789 | 0.035409 | 0.054945 | 321.0274 | 442.2267 | 9.1472
38930.4299 | 1122 | 1171 | 38930.4299 | 1054 | 971 | 1691.5 | 1812.5 | 68.4982 | 71.4896 | 64.3468 | 59.2796 | 0.68498 | 0.7149 | 0.64347 | 0.5928 | 0.029915 | 0.050672 | 193.2208 | 252.4278 | 11.0087
38930.4305 | 1138 | 1179 | 38930.4306 | 1164 | 1117 | 1750 | 1871 | 69.475 | 71.978 | 71.0623 | 68.1929 | 0.69475 | 0.71978 | 0.71062 | 0.68193 | 0.025031 | 0.028694 | 2373.0549 | 1353246.4395 | 17.2998
38930.4312 | 1061 | 1080 | 38930.4312 | 1106 | 1039 | 1809 | 1930 | 64.7741 | 65.9341 | 67.5214 | 63.431 | 0.64774 | 0.65934 | 0.67521 | 0.63431 | 0.0116 | 0.040904 | 117.826 | 123.5898 | 1.432
38930.4319 | 1060 | 996 | 38930.4319 | 946 | 850 | 1867.5 | 1988.5 | 64.7131 | 60.8059 | 57.7534 | 51.8926 | 0.64713 | 0.60806 | 0.57753 | 0.51893 | 0.039072 | 0.058608 | 1826.8291 | 15665.1954 | 5.6886
38930.4326 | 1028 | 1037 | 38930.4326 | 984 | 888 | 1926.5 | 2047.5 | 62.7595 | 63.3089 | 60.0733 | 54.2125 | 0.62759 | 0.63309 | 0.60073 | 0.54212 | 0.0054945 | 0.058608 | 340.2511 | 334.637 | 3.5653
38930.4333 | 1097 | 1139 | 38930.4333 | 924 | 896 | 1985.5 | 2106.5 | 66.9719 | 69.536 | 56.4103 | 54.7009 | 0.66972 | 0.69536 | 0.5641 | 0.54701 | 0.025641 | 0.017094 | 1039.0966 | 2041.981 | 10.2931
38930.4339 | 1190 | 1161 | 38930.434 | 1048 | 970 | 2044 | 2165 | 72.6496 | 70.8791 | 63.9805 | 59.2186 | 0.7265 | 0.70879 | 0.6398 | 0.59219 | 0.017705 | 0.047619 | 239.8683 | 326.3044 | 15.6896
38930.4346 | 965 | 872 | 38930.4346 | 1180 | 1147 | 2103 | 2224 | 58.9133 | 53.2357 | 72.0391 | 70.0244 | 0.58913 | 0.53236 | 0.72039 | 0.70024 | 0.056777 | 0.020147 | 122.324 | 103.1333 | 16.071
38930.4353 | 1019 | 1025 | 38930.4353 | 1075 | 1006 | 2161.5 | 2282.5 | 62.21 | 62.5763 | 65.6288 | 61.4164 | 0.6221 | 0.62576 | 0.65629 | 0.61416 | 0.003663 | 0.042125 | 161.9685 | 153.1102 | 4.0733

## C4-6
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38930.4094 | 1 | 0 | 38930.4094 | 1 | 0 | -75.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4101 | 1 | 0 | 38930.4101 | 1 | 0 | -16.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4108 | 1 | 0 | 38930.4108 | 1 | 0 | 42.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4114 | 1 | 0 | 38930.4115 | 0 | 0 | 101 | 222 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
38930.4121 | 1 | 0 | 38930.4122 | 1 | 0 | 160 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4128 | 1 | 0 | 38930.4128 | 1 | 0 | 218.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4135 | 1 | 0 | 38930.4135 | 1 | 0 | 277.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4142 | 1 | 0 | 38930.4142 | 1 | 0 | 336.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4148 | 1 | 0 | 38930.4149 | 1 | 0 | 395 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4155 | 1 | 0 | 38930.4156 | 1 | 0 | 454 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4162 | 1 | 0 | 38930.4162 | 1 | 0 | 512.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4169 | 1 | 0 | 38930.4169 | 1 | 0 | 571.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4176 | 1 | 0 | 38930.4176 | 1 | 0 | 630.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4183 | 1 | 0 | 38930.4183 | 1 | 0 | 689 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4189 | 1 | 0 | 38930.4189 | 1 | 0 | 747.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4196 | 1 | 0 | 38930.4196 | 1 | 0 | 806.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4203 | 1 | 0 | 38930.4203 | 1 | 0 | 865.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.421 | 1 | 0 | 38930.421 | 1 | 0 | 924 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4217 | 1 | 0 | 38930.4217 | 1 | 0 | 983 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4223 | 1 | 0 | 38930.4223 | 1 | 0 | 1041.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.423 | 1 | 0 | 38930.423 | 1 | 0 | 1100.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4237 | 1 | 0 | 38930.4237 | 1 | 0 | 1159.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4244 | 1 | 0 | 38930.4244 | 1 | 0 | 1218 | 1339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4251 | 1 | 0 | 38930.4251 | 1 | 0 | 1277 | 1398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4257 | 1 | 0 | 38930.4258 | 1 | 0 | 1335.5 | 1456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4264 | 156 | 157 | 38930.4264 | 281 | 280 | 1394.5 | 1515.5 | 9.5238 | 9.5849 | 17.1551 | 17.094 | 0.095238 | 0.095849 | 0.17155 | 0.17094 | 0.0006105 | 0.0006105 | 211420.746 | 211168.6074 | 1145.9669
38930.4271 | 37 | 48 | 38930.4271 | 375 | 370 | 1453.5 | 1574.5 | 2.2589 | 2.9304 | 22.8938 | 22.5885 | 0.022589 | 0.029304 | 0.22894 | 0.22589 | 0.0067155 | 0.0030525 | 19018.7649 | 56899.3246 | 4217.6292
38930.4278 | 991 | 960 | 38930.4278 | 908 | 937 | 1512 | 1633 | 60.5006 | 58.6081 | 55.4335 | 57.2039 | 0.60501 | 0.58608 | 0.55433 | 0.57204 | 0.018926 | 0.017705 | 4755.7231 | 12960.7954 | 16.7479
38930.4285 | 1158 | 1108 | 38930.4285 | 1026 | 932 | 1571 | 1692 | 70.696 | 67.6435 | 62.6374 | 56.8987 | 0.70696 | 0.67643 | 0.62637 | 0.56899 | 0.030525 | 0.057387 | 10.9834 | 12.8165 | 1.5685
38930.4291 | 1026 | 1110 | 38930.4292 | 1077 | 1006 | 1629.5 | 1750.5 | 62.6374 | 67.7656 | 65.7509 | 61.4164 | 0.62637 | 0.67766 | 0.65751 | 0.61416 | 0.051282 | 0.043346 | 115.8086 | 129.88 | 1.1697
38930.4298 | 974 | 954 | 38930.4298 | 1139 | 1086 | 1688.5 | 1809.5 | 59.4628 | 58.2418 | 69.536 | 66.3004 | 0.59463 | 0.58242 | 0.69536 | 0.663 | 0.01221 | 0.032357 | 236.1019 | 206.3027 | 13.0624
38930.4305 | 1179 | 1138 | 38930.4305 | 987 | 880 | 1747.5 | 1868.5 | 71.978 | 69.475 | 60.2564 | 53.7241 | 0.71978 | 0.69475 | 0.60256 | 0.53724 | 0.025031 | 0.065324 | 66.5155 | 83.4792 | 8.1552
38930.4312 | 931 | 888 | 38930.4312 | 1097 | 1027 | 1806 | 1927 | 56.8376 | 54.2125 | 66.9719 | 62.6984 | 0.56838 | 0.54212 | 0.66972 | 0.62698 | 0.026252 | 0.042735 | 1564.4945 | 2727.8725 | 31.9395
38930.4319 | 972 | 884 | 38930.4319 | 1123 | 1070 | 1865 | 1986 | 59.3407 | 53.9683 | 68.5592 | 65.3236 | 0.59341 | 0.53968 | 0.68559 | 0.65324 | 0.053724 | 0.032357 | 456.3042 | 545.4876 | 24.5704
38930.4325 | 1073 | 1004 | 38930.4326 | 1086 | 1019 | 1923.5 | 2044.5 | 65.5067 | 61.2943 | 66.3004 | 62.21 | 0.65507 | 0.61294 | 0.663 | 0.6221 | 0.042125 | 0.040904 | 1252.5189 | 7153.9149 | 3.5382
38930.4332 | 959 | 862 | 38930.4332 | 1180 | 1136 | 1982.5 | 2103.5 | 58.547 | 52.6252 | 72.0391 | 69.3529 | 0.58547 | 0.52625 | 0.72039 | 0.69353 | 0.059219 | 0.026862 | 185.4339 | 164.0857 | 21.049
38930.4339 | 1170 | 1130 | 38930.4339 | 1122 | 1177 | 2041.5 | 2162.5 | 71.4286 | 68.9866 | 68.4982 | 71.8559 | 0.71429 | 0.68987 | 0.68498 | 0.71856 | 0.02442 | 0.033578 | 1756.8742 | 8262.6422 | 16.349
38930.4346 | 1058 | 1080 | 38930.4346 | 1149 | 1184 | 2100 | 2221 | 64.591 | 65.9341 | 70.1465 | 72.2833 | 0.64591 | 0.65934 | 0.70147 | 0.72283 | 0.013431 | 0.021368 | 1577.0646 | 2405.4682 | 2.2206
38930.4353 | 1050 | 973 | 38930.4353 | 1060 | 989 | 2159 | 2280 | 64.1026 | 59.4017 | 64.7131 | 60.3785 | 0.64103 | 0.59402 | 0.64713 | 0.60379 | 0.047009 | 0.043346 | 1309.0862 | 23148.9759 | 9.212

## C4-5
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38930.4094 | 1 | 0 | 38930.4094 | 1 | 0 | -78 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4101 | 1 | 0 | 38930.4101 | 1 | 0 | -19.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4107 | 1 | 0 | 38930.4108 | 1 | 0 | 39.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4114 | 1 | 0 | 38930.4114 | 1 | 0 | 98.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4121 | 1 | 0 | 38930.4121 | 1 | 0 | 157 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4128 | 1 | 0 | 38930.4128 | 1 | 0 | 216 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4135 | 1 | 0 | 38930.4135 | 1 | 0 | 274.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4141 | 1 | 0 | 38930.4142 | 1 | 0 | 333.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4148 | 1 | 0 | 38930.4148 | 1 | 0 | 392.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4155 | 1 | 0 | 38930.4155 | 1 | 0 | 451 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4162 | 1 | 0 | 38930.4162 | 1 | 0 | 510 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4169 | 1 | 0 | 38930.4169 | 1 | 0 | 568.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4175 | 1 | 0 | 38930.4176 | 1 | 0 | 627.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4182 | 1 | 0 | 38930.4182 | 1 | 0 | 686.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4189 | 1 | 0 | 38930.4189 | 1 | 0 | 745 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4196 | 1 | 0 | 38930.4196 | 1 | 0 | 804 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4203 | 1 | 0 | 38930.4203 | 1 | 0 | 862.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4209 | 1 | 0 | 38930.421 | 1 | 0 | 921.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4216 | 1 | 0 | 38930.4216 | 1 | 0 | 980 | 1101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4223 | 1 | 1 | 38930.4223 | 1 | 0 | 1039 | 1160 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.423 | 1 | 0 | 38930.423 | 1 | 0 | 1098 | 1219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4237 | 1 | 0 | 38930.4237 | 1 | 0 | 1156.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4244 | 1 | 0 | 38930.4244 | 1 | 0 | 1215.5 | 1336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.425 | 1 | 0 | 38930.425 | 1 | 0 | 1274 | 1395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4257 | 1 | 0 | 38930.4257 | 1 | 0 | 1333 | 1454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4264 | 11 | 26 | 38930.4264 | 5 | 20 | 1391.5 | 1512.5 | 0.67155 | 1.5873 | 0.30525 | 1.221 | 0.0067155 | 0.015873 | 0.0030525 | 0.01221 | 0.0091575 | 0.0091575 | 14186.8 | 14186.8 | 7928.8037
38930.4271 | 209 | 211 | 38930.4271 | 20 | 41 | 1450.5 | 1571.5 | 12.7595 | 12.8816 | 1.221 | 2.5031 | 0.12759 | 0.12882 | 0.01221 | 0.025031 | 0.001221 | 0.012821 | 1623326.6412 | 11207.2565 | 795.283
38930.4278 | 1054 | 1129 | 38930.4278 | 1073 | 896 | 1509.5 | 1630.5 | 64.3468 | 68.9255 | 65.5067 | 54.7009 | 0.64347 | 0.68926 | 0.65507 | 0.54701 | 0.045788 | 0.10806 | 73.7231 | 82.9243 | 2.8099
38930.4284 | 940 | 821 | 38930.4284 | 1016 | 917 | 1568 | 1689 | 57.3871 | 50.1221 | 62.0269 | 55.9829 | 0.57387 | 0.50122 | 0.62027 | 0.55983 | 0.07265 | 0.06044 | 1083.8414 | 7621.6232 | 42.3217
38930.4291 | 1005 | 908 | 38930.4291 | 1052 | 1074 | 1627 | 1748 | 61.3553 | 55.4335 | 64.2247 | 65.5678 | 0.61355 | 0.55433 | 0.64225 | 0.65568 | 0.059219 | 0.013431 | 241.6594 | 251.1723 | 15.7557
38930.4298 | 924 | 806 | 38930.4298 | 1148 | 1102 | 1685.5 | 1806.5 | 56.4103 | 49.2063 | 70.0855 | 67.2772 | 0.5641 | 0.49206 | 0.70085 | 0.67277 | 0.072039 | 0.028083 | 337.5369 | 344.0568 | 36.8195
38930.4305 | 1015 | 919 | 38930.4305 | 1001 | 897 | 1744.5 | 1865.5 | 61.9658 | 56.105 | 61.1111 | 54.7619 | 0.61966 | 0.56105 | 0.61111 | 0.54762 | 0.058608 | 0.063492 | 3548.7568 | 1412.5635 | 18.192
38930.4312 | 974 | 869 | 38930.4312 | 1077 | 1150 | 1803.5 | 1924.5 | 59.4628 | 53.0525 | 65.7509 | 70.2076 | 0.59463 | 0.53053 | 0.65751 | 0.70208 | 0.064103 | 0.044567 | 398.494 | 480.5588 | 25.7203
38930.4318 | 1073 | 1012 | 38930.4319 | 1185 | 1158 | 1862 | 1983 | 65.5067 | 61.7827 | 72.3443 | 70.696 | 0.65507 | 0.61783 | 0.72344 | 0.70696 | 0.037241 | 0.016484 | 705.9419 | 1172.3311 | 2.5512
38930.4325 | 1115 | 1170 | 38930.4325 | 1121 | 1163 | 1921 | 2042 | 68.0708 | 71.4286 | 68.4371 | 71.0012 | 0.68071 | 0.71429 | 0.68437 | 0.71001 | 0.033578 | 0.025641 | 6837.2507 | 2895.8104 | 14.2085
38930.4332 | 1087 | 1023 | 38930.4332 | 956 | 1060 | 1979.5 | 2100.5 | 66.3614 | 62.4542 | 58.3639 | 64.7131 | 0.66361 | 0.62454 | 0.58364 | 0.64713 | 0.039072 | 0.063492 | 317.6779 | 395.0189 | 0.23557
38930.4339 | 997 | 910 | 38930.4339 | 924 | 865 | 2038.5 | 2159.5 | 60.8669 | 55.5556 | 56.4103 | 52.8083 | 0.60867 | 0.55556 | 0.5641 | 0.52808 | 0.053114 | 0.03602 | 1084.9622 | 5736.7739 | 22.2517
38930.4346 | 1007 | 1009 | 38930.4346 | 1061 | 987 | 2097.5 | 2218.5 | 61.4774 | 61.5995 | 64.7741 | 60.2564 | 0.61477 | 0.616 | 0.64774 | 0.60256 | 0.001221 | 0.045177 | 231.0745 | 211.6892 | 6.5305
38930.4352 | 1191 | 983 | 38930.4353 | 980 | 889 | 2156 | 2277 | 72.7106 | 60.0122 | 59.8291 | 54.2735 | 0.72711 | 0.60012 | 0.59829 | 0.54274 | 0.12698 | 0.055556 | 116.8005 | 169.0755 | 3.898

## C3-7
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38930.4093 | 1 | 0 | 38930.4094 | 1 | 0 | -81 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.41 | 1 | 0 | 38930.41 | 1 | 0 | -22 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4107 | 1 | 0 | 38930.4107 | 1 | 0 | 36.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4114 | 1 | 0 | 38930.4114 | 1 | 0 | 95.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4121 | 1 | 0 | 38930.4121 | 1 | 0 | 154.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4127 | 1 | 0 | 38930.4128 | 1 | 0 | 213 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4134 | 1 | 0 | 38930.4134 | 1 | 0 | 272 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4141 | 1 | 0 | 38930.4141 | 1 | 0 | 330.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4148 | 1 | 0 | 38930.4148 | 1 | 0 | 389.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4155 | 1 | 0 | 38930.4155 | 1 | 0 | 448.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4161 | 1 | 0 | 38930.4162 | 1 | 0 | 507 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4168 | 1 | 0 | 38930.4169 | 1 | 0 | 566 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4175 | 1 | 0 | 38930.4175 | 1 | 0 | 624.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4182 | 1 | 0 | 38930.4182 | 1 | 0 | 683.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4189 | 1 | 0 | 38930.4189 | 1 | 0 | 742.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4195 | 1 | 0 | 38930.4196 | 1 | 0 | 801 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4202 | 1 | 0 | 38930.4203 | 1 | 0 | 860 | 981 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4209 | 1 | 0 | 38930.4209 | 1 | 0 | 918.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4216 | 1 | 0 | 38930.4216 | 2 | 0 | 977.5 | 1098.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.4223 | 1 | 0 | 38930.4223 | 1 | 0 | 1036 | 1157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.423 | 1 | 0 | 38930.423 | 1 | 0 | 1095 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4236 | 1 | 0 | 38930.4236 | 1 | 0 | 1153.5 | 1274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4243 | 1 | 0 | 38930.4243 | 1 | 0 | 1212.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.425 | 1 | 0 | 38930.425 | 1 | 0 | 1271.5 | 1392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4257 | 1 | 0 | 38930.4257 | 1 | 0 | 1330 | 1451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4264 | 1062 | 1116 | 38930.4264 | 1122 | 1102 | 1389 | 1510 | 64.8352 | 68.1319 | 68.4982 | 67.2772 | 0.64835 | 0.68132 | 0.68498 | 0.67277 | 0.032967 | 0.01221 | 603.4611 | 928.7204 | 5.2566
38930.427 | 1063 | 1035 | 38930.427 | 943 | 1057 | 1447.5 | 1568.5 | 64.8962 | 63.1868 | 57.5702 | 64.5299 | 0.64896 | 0.63187 | 0.5757 | 0.6453 | 0.017094 | 0.069597 | 157.8673 | 162.4477 | 0.89826
38930.4277 | 951 | 1067 | 38930.4277 | 1139 | 1113 | 1506.5 | 1627.5 | 58.0586 | 65.1404 | 69.536 | 67.9487 | 0.58059 | 0.6514 | 0.69536 | 0.67949 | 0.070818 | 0.015873 | 65.3888 | 64.2349 | 3.483
38930.4284 | 955 | 846 | 38930.4284 | 969 | 861 | 1565.5 | 1686.5 | 58.3028 | 51.6484 | 59.1575 | 52.5641 | 0.58303 | 0.51648 | 0.59158 | 0.52564 | 0.066545 | 0.065934 | 1789.3454 | 1910.4622 | 35.0473
38930.4291 | 1016 | 916 | 38930.4291 | 1095 | 1025 | 1624 | 1745 | 62.0269 | 55.9219 | 66.8498 | 62.5763 | 0.62027 | 0.55922 | 0.6685 | 0.62576 | 0.06105 | 0.042735 | 472.0777 | 691.9408 | 17.2666
38930.4298 | 957 | 841 | 38930.4298 | 1185 | 954 | 1683 | 1804 | 58.4249 | 51.3431 | 72.3443 | 58.2418 | 0.58425 | 0.51343 | 0.72344 | 0.58242 | 0.070818 | 0.14103 | 312.2761 | 330.8527 | 28.7639
38930.4304 | 1189 | 1159 | 38930.4305 | 960 | 847 | 1741.5 | 1862.5 | 72.5885 | 70.757 | 58.6081 | 51.7094 | 0.72589 | 0.70757 | 0.58608 | 0.51709 | 0.018315 | 0.068987 | 86.8891 | 112.1488 | 10.7177
38930.4311 | 931 | 818 | 38930.4311 | 1012 | 920 | 1800.5 | 1921.5 | 56.8376 | 49.9389 | 61.7827 | 56.1661 | 0.56838 | 0.49939 | 0.61783 | 0.56166 | 0.068987 | 0.056166 | 1116.5092 | 11468.5752 | 44.1165
38930.4318 | 967 | 874 | 38930.4318 | 1157 | 1181 | 1859.5 | 1980.5 | 59.0354 | 53.3578 | 70.6349 | 72.1001 | 0.59035 | 0.53358 | 0.70635 | 0.721 | 0.056777 | 0.014652 | 93.3615 | 77.0378 | 13.5434
38930.4325 | 974 | 957 | 38930.4325 | 1046 | 963 | 1918 | 2039 | 59.4628 | 58.4249 | 63.8584 | 58.7912 | 0.59463 | 0.58425 | 0.63858 | 0.58791 | 0.010379 | 0.050672 | 479.2922 | 433.7259 | 15.4563
38930.4332 | 1181 | 1149 | 38930.4332 | 1035 | 1124 | 1977 | 2098 | 72.1001 | 70.1465 | 63.1868 | 68.6203 | 0.721 | 0.70147 | 0.63187 | 0.6862 | 0.019536 | 0.054335 | 423.1425 | 610.3213 | 16.2257
38930.4338 | 992 | 902 | 38930.4339 | 1125 | 1169 | 2035.5 | 2156.5 | 60.5617 | 55.0672 | 68.6813 | 71.3675 | 0.60562 | 0.55067 | 0.68681 | 0.71368 | 0.054945 | 0.026862 | 107.9587 | 95.1097 | 11.8365
38930.4345 | 943 | 843 | 38930.4345 | 1040 | 1126 | 2094.5 | 2215.5 | 57.5702 | 51.4652 | 63.4921 | 68.7424 | 0.5757 | 0.51465 | 0.63492 | 0.68742 | 0.06105 | 0.052503 | 879.8898 | 2556.6013 | 37.3322
38930.4352 | 946 | 847 | 38930.4352 | 1127 | 840 | 2153.5 | 2274.5 | 57.7534 | 51.7094 | 68.8034 | 51.2821 | 0.57753 | 0.51709 | 0.68803 | 0.51282 | 0.06044 | 0.17521 | 301.9289 | 294.5867 | 28.2075

## C3-6
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38930.4093 | 1 | 0 | 38930.4093 | 1 | 0 | -83.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.41 | 1 | 0 | 38930.41 | 1 | 0 | -25 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4107 | 1 | 0 | 38930.4107 | 1 | 0 | 34 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4114 | 1 | 0 | 38930.4114 | 1 | 0 | 92.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.412 | 1 | 0 | 38930.412 | 1 | 0 | 151.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4127 | 1 | 0 | 38930.4127 | 1 | 0 | 210.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4134 | 1 | 0 | 38930.4134 | 1 | 0 | 269 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4141 | 1 | 0 | 38930.4141 | 1 | 0 | 328 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4148 | 1 | 0 | 38930.4148 | 1 | 0 | 386.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4154 | 1 | 0 | 38930.4155 | 1 | 0 | 445.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4161 | 1 | 0 | 38930.4161 | 1 | 0 | 504.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4168 | 1 | 0 | 38930.4168 | 1 | 0 | 563 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4175 | 1 | 0 | 38930.4175 | 1 | 0 | 622 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4182 | 1 | 0 | 38930.4182 | 1 | 0 | 680.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4188 | 1 | 0 | 38930.4189 | 1 | 0 | 739.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4195 | 1 | 0 | 38930.4195 | 1 | 0 | 798 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38930.4202 | 1 | 0 | 858 | 979 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4209 | 1 | 0 | 38930.4209 | 1 | 0 | 915.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4216 | 1 | 0 | 38930.4216 | 1 | 0 | 974.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4222 | 1 | 0 | 38930.4223 | 1 | 0 | 1033.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4229 | 1 | 0 | 38930.4229 | 1 | 0 | 1092.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4236 | 1 | 0 | 38930.4236 | 1 | 0 | 1151 | 1272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4243 | 1 | 0 | 38930.4243 | 1 | 0 | 1209.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.425 | 1 | 0 | 38930.425 | 1 | 0 | 1268.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4256 | 1 | 0 | 38930.4257 | 1 | 0 | 1327.5 | 1448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4263 | 1118 | 1096 | 38930.4263 | 1003 | 970 | 1386 | 1507 | 68.254 | 66.9109 | 61.2332 | 59.2186 | 0.68254 | 0.66911 | 0.61233 | 0.59219 | 0.013431 | 0.020147 | 352.1761 | 420.6732 | 7.444
38930.427 | 979 | 946 | 38930.427 | 1071 | 1044 | 1445 | 1566 | 59.768 | 57.7534 | 65.3846 | 63.7363 | 0.59768 | 0.57753 | 0.65385 | 0.63736 | 0.020147 | 0.016484 | 2193.9512 | 5061.942 | 19.4902
38930.4277 | 1026 | 997 | 38930.4277 | 1159 | 1181 | 1503.5 | 1624.5 | 62.6374 | 60.8669 | 70.757 | 72.1001 | 0.62637 | 0.60867 | 0.70757 | 0.721 | 0.017705 | 0.013431 | 2449.4761 | 6483.4345 | 8.8919
38930.4284 | 1021 | 1020 | 38930.4284 | 1164 | 1148 | 1562.5 | 1683.5 | 62.3321 | 62.2711 | 71.0623 | 70.0855 | 0.62332 | 0.62271 | 0.71062 | 0.70085 | 0.0006105 | 0.009768 | 875.7488 | 824.6051 | 6.2971
38930.4291 | 918 | 987 | 38930.4291 | 1110 | 1043 | 1621.5 | 1742.5 | 56.044 | 60.2564 | 67.7656 | 63.6752 | 0.56044 | 0.60256 | 0.67766 | 0.63675 | 0.042125 | 0.040904 | 5494.2216 | 2088.9105 | 20.1131
38930.4297 | 980 | 961 | 38930.4297 | 1018 | 924 | 1680 | 1801 | 59.8291 | 58.6691 | 62.149 | 56.4103 | 0.59829 | 0.58669 | 0.62149 | 0.5641 | 0.0116 | 0.057387 | 507.2955 | 470.2827 | 14.7613
38930.4304 | 974 | 863 | 38930.4304 | 1169 | 1124 | 1739 | 1860 | 59.4628 | 52.6862 | 71.3675 | 68.6203 | 0.59463 | 0.52686 | 0.71368 | 0.6862 | 0.067766 | 0.027473 | 159.5811 | 143.1756 | 18.8312
38930.4311 | 971 | 866 |  | 1166 | 1123 | 1797 | 1918 | 59.2796 | 52.8694 | 71.1844 | 68.5592 | 0.5928 | 0.52869 | 0.71184 | 0.68559 | 0.064103 | 0.026252 | 175.2401 | 158.4083 | 19.5386
38930.4318 | 1014 | 863 | 38930.4318 | 1162 | 1122 | 1856.5 | 1977.5 | 61.9048 | 52.6862 | 70.9402 | 68.4982 | 0.61905 | 0.52686 | 0.7094 | 0.68498 | 0.092186 | 0.02442 | 70.4998 | 61.297 | 10.3932
38930.4325 | 1191 | 1172 | 38930.4325 | 966 | 863 | 1915.5 | 2036.5 | 72.7106 | 71.5507 | 58.9744 | 52.6862 | 0.72711 | 0.71551 | 0.58974 | 0.52686 | 0.0116 | 0.062882 | 46.6419 | 59.8629 | 7.9871
38930.4331 | 1168 | 1129 | 38930.4331 | 1106 | 1168 | 1974 | 2095 | 71.3065 | 68.9255 | 67.5214 | 71.3065 | 0.71306 | 0.68926 | 0.67521 | 0.71306 | 0.02381 | 0.037851 | 1194.5558 | 2814.719 | 15.7367
38930.4338 | 1081 | 1013 | 38930.4338 | 998 | 908 | 2033 | 2154 | 65.9951 | 61.8437 | 60.928 | 55.4335 | 0.65995 | 0.61844 | 0.60928 | 0.55433 | 0.041514 | 0.054945 | 1504.4912 | 169981.4898 | 1.8765
38930.4345 | 1133 | 839 | 38930.4345 | 1022 | 941 | 2091.5 | 2212.5 | 69.1697 | 51.221 | 62.3932 | 57.4481 | 0.6917 | 0.51221 | 0.62393 | 0.57448 | 0.17949 | 0.049451 | 110.6493 | 141.795 | 9.8567
38930.4352 | 991 | 900 | 38930.4352 | 949 | 851 | 2150.5 | 2271.5 | 60.5006 | 54.9451 | 57.9365 | 51.9536 | 0.60501 | 0.54945 | 0.57937 | 0.51954 | 0.055556 | 0.059829 | 3047.2707 | 1661.1446 | 23.2682

## C3-5
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38930.4093 | 1 | 0 | 38930.4093 | 1 | 0 | -86.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.41 | 1 | 0 | 38930.41 | 1 | 0 | -27.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4106 | 1 | 0 | 38930.4107 | 1 | 0 | 31 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4113 | 1 | 0 | 38930.4113 | 1 | 0 | 90 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.412 | 1 | 0 | 38930.412 | 1 | 0 | 148.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4127 | 1 | 0 | 38930.4127 | 1 | 0 | 207.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4134 | 1 | 0 | 38930.4134 | 1 | 0 | 266.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.414 | 1 | 0 | 38930.4141 | 1 | 0 | 325 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4147 | 1 | 0 | 38930.4147 | 1 | 0 | 384 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4154 | 1 | 0 | 38930.4154 | 1 | 0 | 442.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4161 | 1 | 0 | 38930.4161 | 1 | 0 | 501.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4168 | 1 | 0 | 38930.4168 | 1 | 0 | 560.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4174 | 1 | 0 | 38930.4175 | 1 | 0 | 619 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4181 | 1 | 0 | 38930.4181 | 1 | 0 | 678 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4188 | 1 | 1 | 38930.4188 | 1 | 0 | 736.5 | 857.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.4195 | 1 | 0 | 38930.4195 | 1 | 0 | 795.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4202 | 1 | 0 | 38930.4202 | 1 | 0 | 854.5 | 975.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4208 | 1 | 0 | 38930.4209 | 1 | 0 | 913 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4215 | 1 | 0 | 38930.4216 | 1 | 0 | 972 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4222 | 1 | 0 | 38930.4222 | 1 | 0 | 1030.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4229 | 1 | 0 | 38930.4229 | 1 | 0 | 1089.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4236 | 1 | 0 | 38930.4236 | 1 | 0 | 1148 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4242 | 1 | 0 | 38930.4243 | 1 | 0 | 1207 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4249 | 1 | 0 | 38930.4249 | 1 | 0 | 1265.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4256 | 1 | 0 | 38930.4256 | 1 | 0 | 1324.5 | 1445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4263 | 241 | 273 | 38930.4263 | 926 | 957 | 1383.5 | 1504.5 | 14.7131 | 16.6667 | 56.5324 | 58.4249 | 0.14713 | 0.16667 | 0.56532 | 0.58425 | 0.019536 | 0.018926 | 6642.1248 | 7154.1879 | 577.6474
38930.427 | 908 | 873 | 38930.427 | 1045 | 1017 | 1442 | 1563 | 55.4335 | 53.2967 | 63.7973 | 62.0879 | 0.55433 | 0.53297 | 0.63797 | 0.62088 | 0.021368 | 0.017094 | 3085.3654 | 21523.7193 | 37.8562
38930.4277 | 1042 | 1016 | 38930.4277 | 941 | 910 | 1501 | 1622 | 63.6142 | 62.0269 | 57.4481 | 55.5556 | 0.63614 | 0.62027 | 0.57448 | 0.55556 | 0.015873 | 0.018926 | 32311.0232 | 4478.6752 | 5.2971
38930.4283 | 909 | 851 | 38930.4283 | 947 | 914 | 1559.5 | 1680.5 | 55.4945 | 51.9536 | 57.8144 | 55.7998 | 0.55495 | 0.51954 | 0.57814 | 0.558 | 0.035409 | 0.020147 | 1583.2066 | 4714.8232 | 40.6214
38930.429 | 1002 | 846 | 38930.429 | 1155 | 1109 | 1618.5 | 1739.5 | 61.1722 | 51.6484 | 70.5128 | 67.7045 | 0.61172 | 0.51648 | 0.70513 | 0.67705 | 0.095238 | 0.028083 | 114.1405 | 103.5016 | 15.9326
38930.4297 | 1126 | 1169 | 38930.4297 | 946 | 831 | 1677.5 | 1798.5 | 68.7424 | 71.3675 | 57.7534 | 50.7326 | 0.68742 | 0.71368 | 0.57753 | 0.50733 | 0.026252 | 0.070208 | 214.1559 | 279.7397 | 11.4677
38930.4304 | 930 | 818 | 38930.4304 | 990 | 976 | 1736 | 1857 | 56.7766 | 49.9389 | 60.4396 | 59.5849 | 0.56777 | 0.49939 | 0.6044 | 0.59585 | 0.068376 | 0.008547 | 463.7493 | 571.632 | 37.9794
38930.4311 | 964 | 855 | 38930.4311 | 1183 | 1161 | 1795 | 1916 | 58.8523 | 52.1978 | 72.2222 | 70.8791 | 0.58852 | 0.52198 | 0.72222 | 0.70879 | 0.066545 | 0.013431 | 91.9992 | 75.0036 | 14.7383
38930.4317 | 1125 | 1168 | 38930.4317 | 1145 | 1106 | 1853.5 | 1974.5 | 68.6813 | 71.3065 | 69.9023 | 67.5214 | 0.68681 | 0.71306 | 0.69902 | 0.67521 | 0.026252 | 0.02381 | 8540.1814 | 3716.0854 | 15.0054
38930.4324 | 927 | 1017 | 38930.4324 | 927 | 1016 | 1912.5 | 2033.5 | 56.5934 | 62.0879 | 56.5934 | 62.0269 | 0.56593 | 0.62088 | 0.56593 | 0.62027 | 0.054945 | 0.054335 | 2300.6719 | 2645.0642 | 16.014
38930.4331 | 991 | 907 | 38930.4331 | 948 | 853 | 1971.5 | 2092.5 | 60.5006 | 55.3724 | 57.8755 | 52.0757 | 0.60501 | 0.55372 | 0.57875 | 0.52076 | 0.051282 | 0.057998 | 4561.1639 | 1526.9212 | 22.2496
38930.4338 | 932 | 1029 | 38930.4338 | 1134 | 1084 | 2030 | 2151 | 56.8987 | 62.8205 | 69.2308 | 66.1783 | 0.56899 | 0.62821 | 0.69231 | 0.66178 | 0.059219 | 0.030525 | 93.7752 | 88.5225 | 6.9371
38930.4345 | 1169 | 836 | 38930.4345 | 992 | 991 | 2089 | 2210 | 71.3675 | 51.0379 | 60.5617 | 60.5006 | 0.71368 | 0.51038 | 0.60562 | 0.60501 | 0.2033 | 0.0006105 | 61.6944 | 69.8323 | 5.3129
38930.4351 | 945 | 846 | 38930.4352 | 1016 | 858 | 2147.5 | 2268.5 | 57.6923 | 51.6484 | 62.0269 | 52.381 | 0.57692 | 0.51648 | 0.62027 | 0.52381 | 0.06044 | 0.096459 | 2216.3063 | 1827.2611 | 36.0888

## C3-4
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38930.4092 | 1 | 0 | 38930.4093 | 1 | 0 | -89.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4099 | 1 | 0 | 38930.4099 | 1 | 0 | -30.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4106 | 1 | 0 | 38930.4106 | 1 | 0 | 28.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4113 | 1 | 0 | 38930.4113 | 1 | 0 | 87 | 208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.412 | 1 | 0 | 38930.412 | 1 | 0 | 146 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4127 | 1 | 0 | 38930.4127 | 1 | 0 | 204.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4133 | 1 | 0 | 38930.4133 | 1 | 0 | 263.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.414 | 1 | 0 | 38930.414 | 1 | 0 | 322.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4147 | 1 | 0 | 38930.4147 | 1 | 0 | 381 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4154 | 1 | 0 | 38930.4154 | 1 | 0 | 440 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4161 | 1 | 0 | 38930.4161 | 1 | 0 | 498.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4167 | 1 | 0 | 38930.4167 | 1 | 0 | 557.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4174 | 1 | 0 | 38930.4174 | 1 | 0 | 616.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4181 | 1 | 0 | 38930.4181 | 1 | 0 | 675 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4188 | 1 | 0 | 38930.4188 | 1 | 0 | 734 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4195 | 1 | 0 | 38930.4195 | 1 | 0 | 792.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4201 | 1 | 0 | 38930.4202 | 1 | 0 | 851.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4208 | 1 | 0 | 38930.4208 | 1 | 0 | 910.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4215 | 1 | 0 | 38930.4215 | 1 | 0 | 969 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4222 | 1 | 0 | 38930.4222 | 1 | 0 | 1027.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4229 | 1 | 0 | 38930.4229 | 1 | 0 | 1086.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4235 | 1 | 0 | 38930.4236 | 1 | 0 | 1145.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4242 | 1 | 0 | 38930.4242 | 1 | 0 | 1204 | 1325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4249 | 1 | 0 | 38930.4249 | 2 | 0 | 1263 | 1384 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.4256 | 1 | 0 | 38930.4256 | 1 | 0 | 1321.5 | 1442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4263 | 9 | 21 | 38930.4263 | 4 | 15 | 1380.5 | 1501.5 | 0.54945 | 1.2821 | 0.2442 | 0.91575 | 0.0054945 | 0.012821 | 0.002442 | 0.0091575 | 0.007326 | 0.0067155 | 17693.7544 | 19321.82 | 9868.0707
38930.4269 | 327 | 321 | 38930.427 | 223 | 222 | 1439.5 | 1560.5 | 19.9634 | 19.5971 | 13.6142 | 13.5531 | 0.19963 | 0.19597 | 0.13614 | 0.13553 | 0.003663 | 0.0006105 | 29987.4357 | 727798.6698 | 456.3298
38930.4276 | 1114 | 1156 | 38930.4276 | 1150 | 1131 | 1498 | 1619 | 68.0098 | 70.5739 | 70.2076 | 69.0476 | 0.6801 | 0.70574 | 0.70208 | 0.69048 | 0.025641 | 0.0116 | 1868.5427 | 10082.6896 | 13.4462
38930.4283 | 914 | 865 | 38930.4283 | 1009 | 913 | 1557 | 1678 | 55.7998 | 52.8083 | 61.5995 | 55.7387 | 0.558 | 0.52808 | 0.616 | 0.55739 | 0.029915 | 0.058608 | 1844.9943 | 5410.3972 | 37.9143
38930.429 | 939 | 824 | 38930.429 | 1150 | 810 | 1615.5 | 1736.5 | 57.326 | 50.3053 | 70.2076 | 49.4505 | 0.57326 | 0.50305 | 0.70208 | 0.49451 | 0.070208 | 0.20757 | 273.3943 | 262.0668 | 30.746
38930.4297 | 998 | 907 | 38930.4297 | 982 | 972 | 1674.5 | 1795.5 | 60.928 | 55.3724 | 59.9512 | 59.3407 | 0.60928 | 0.55372 | 0.59951 | 0.59341 | 0.055556 | 0.006105 | 404.3628 | 490.9406 | 19.0539
38930.4303 | 963 | 854 | 38930.4304 | 986 | 1086 | 1733.5 | 1854.5 | 58.7912 | 52.1368 | 60.1954 | 66.3004 | 0.58791 | 0.52137 | 0.60195 | 0.663 | 0.066545 | 0.06105 | 984.51 | 10932.7266 | 34.3486
38930.431 | 1106 | 1144 | 38930.431 | 917 | 971 | 1792 | 1913 | 67.5214 | 69.8413 | 55.9829 | 59.2796 | 0.67521 | 0.69841 | 0.55983 | 0.5928 | 0.023199 | 0.032967 | 573.2265 | 830.9378 | 10.6876
38930.4317 | 1159 | 1168 | 38930.4317 | 1147 | 1102 | 1851 | 1972 | 70.757 | 71.3065 | 70.0244 | 67.2772 | 0.70757 | 0.71306 | 0.70024 | 0.67277 | 0.0054945 | 0.027473 | 833.2994 | 1107.2447 | 16.8027
38930.4324 | 1034 | 949 | 38930.4324 | 948 | 839 | 1909.5 | 2030.5 | 63.1258 | 57.9365 | 57.8755 | 51.221 | 0.63126 | 0.57937 | 0.57875 | 0.51221 | 0.051893 | 0.066545 | 10440.3616 | 1271.0119 | 12.7014
38930.4331 | 995 | 924 | 38930.4331 | 1090 | 1029 | 1968.5 | 2089.5 | 60.7448 | 56.4103 | 66.5446 | 62.8205 | 0.60745 | 0.5641 | 0.66545 | 0.62821 | 0.043346 | 0.037241 | 1185.9609 | 3970.567 | 20.482
38930.4337 | 1058 | 1139 | 38930.4338 | 953 | 1053 | 2027.5 | 2148.5 | 64.591 | 69.536 | 58.1807 | 64.2857 | 0.64591 | 0.69536 | 0.58181 | 0.64286 | 0.049451 | 0.06105 | 122.7647 | 146.3289 | 4.3799
38930.4344 | 937 | 873 | 38930.4344 | 1160 | 1119 | 2086 | 2207 | 57.2039 | 53.2967 | 70.8181 | 68.315 | 0.57204 | 0.53297 | 0.70818 | 0.68315 | 0.039072 | 0.025031 | 570.9602 | 614.9086 | 29.855
38930.4351 | 1077 | 1152 | 38930.4351 | 938 | 913 | 2145 | 2266 | 65.7509 | 70.3297 | 57.265 | 55.7387 | 0.65751 | 0.7033 | 0.57265 | 0.55739 | 0.045788 | 0.015263 | 279.0797 | 388.8906 | 8.0084

## C2-7
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38930.4092 | 1 | 0 | 38930.4092 | 1 | 0 | -92 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4099 | 1 | 0 | 38930.4099 | 1 | 0 | -33.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4106 | 1 | 1 | 38930.4106 | 1 | 0 | 25.5 | 146.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.4113 | 1 | 0 | 38930.4113 | 1 | 0 | 84.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4119 | 1 | 0 | 38930.412 | 1 | 0 | 143 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4126 | 1 | 0 | 38930.4126 | 1 | 0 | 202 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4133 | 1 | 0 | 38930.4133 | 1 | 0 | 260.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.414 | 1 | 0 | 38930.414 | 1 | 0 | 319.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4147 | 1 | 0 | 38930.4147 | 1 | 0 | 378.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4153 | 1 | 0 | 38930.4154 | 2 | 0 | 437 | 558 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.416 | 1 | 0 | 38930.416 | 1 | 0 | 496 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4167 | 1 | 0 | 38930.4167 | 1 | 0 | 554.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4174 | 1 | 0 | 38930.4174 | 1 | 0 | 613.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4181 | 1 | 0 | 38930.4181 | 1 | 0 | 672.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4187 | 1 | 0 | 38930.4188 | 1 | 0 | 731 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4194 | 1 | 0 | 38930.4194 | 1 | 0 | 790 | 911 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4201 | 1 | 0 | 38930.4201 | 1 | 0 | 848.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4208 | 1 | 0 | 38930.4208 | 1 | 0 | 907.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4215 | 1 | 0 | 38930.4215 | 2 | 0 | 966.5 | 1087.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.4221 | 1 | 0 | 38930.4222 | 1 | 0 | 1025 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4228 | 1 | 0 | 38930.4228 | 1 | 0 | 1084 | 1205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4235 | 1 | 0 | 38930.4235 | 1 | 0 | 1142.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4242 | 1 | 0 | 38930.4242 | 1 | 0 | 1201.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4249 | 1 | 0 | 38930.4249 | 1 | 0 | 1260 | 1381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4255 | 1 | 0 | 38930.4256 | 1 | 0 | 1319 | 1440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4262 | 73 | 76 | 38930.4262 | 998 | 966 | 1378 | 1499 | 4.4567 | 4.6398 | 60.928 | 58.9744 | 0.044567 | 0.046398 | 0.60928 | 0.58974 | 0.0018315 | 0.019536 | 241084.6057 | 3528.6213 | 2513.0187
38930.4269 | 1180 | 1159 | 38930.4269 | 968 | 935 | 1436.5 | 1557.5 | 72.0391 | 70.757 | 59.0965 | 57.0818 | 0.72039 | 0.70757 | 0.59096 | 0.57082 | 0.012821 | 0.020147 | 108.0052 | 137.507 | 11.2885
38930.4276 | 1151 | 1128 | 38930.4276 | 1109 | 1082 | 1495.5 | 1616.5 | 70.2686 | 68.8645 | 67.7045 | 66.0562 | 0.70269 | 0.68864 | 0.67705 | 0.66056 | 0.014042 | 0.016484 | 3457.694 | 23389.9241 | 14.6519
38930.4283 | 924 | 872 | 38930.4283 | 994 | 883 | 1554 | 1675 | 56.4103 | 53.2357 | 60.6838 | 53.9072 | 0.5641 | 0.53236 | 0.60684 | 0.53907 | 0.031746 | 0.067766 | 1452.1196 | 2918.1756 | 35.151
38930.4289 | 1106 | 1143 | 38930.429 | 1178 | 830 | 1613 | 1734 | 67.5214 | 69.7802 | 71.917 | 50.6716 | 0.67521 | 0.6978 | 0.71917 | 0.50672 | 0.022589 | 0.21245 | 1.9567 | 2.2225 | 0.25866
38930.4296 | 974 | 862 | 38930.4296 | 1104 | 1034 | 1671.5 | 1792.5 | 59.4628 | 52.6252 | 67.3993 | 63.1258 | 0.59463 | 0.52625 | 0.67399 | 0.63126 | 0.068376 | 0.042735 | 489.8135 | 715.1061 | 28.1942
38930.4303 | 1050 | 964 | 38930.4303 | 962 | 1066 | 1730.5 | 1851.5 | 64.1026 | 58.8523 | 58.7302 | 65.0794 | 0.64103 | 0.58852 | 0.5873 | 0.65079 | 0.052503 | 0.063492 | 15448.7401 | 1218.417 | 9.4927
38930.431 | 1145 | 1184 | 38930.431 | 921 | 868 | 1789.5 | 1910.5 | 69.9023 | 72.2833 | 56.2271 | 52.9915 | 0.69902 | 0.72283 | 0.56227 | 0.52991 | 0.02381 | 0.032357 | 775.9054 | 1380.5961 | 17.0095
38930.4317 | 1039 | 964 | 38930.4317 | 1058 | 986 | 1848 | 1969 | 63.431 | 58.8523 | 64.591 | 60.1954 | 0.63431 | 0.58852 | 0.64591 | 0.60195 | 0.045788 | 0.043956 | 1878.9791 | 5403.516 | 11.2055
38930.4323 | 1016 | 1014 | 38930.4324 | 1168 | 1124 | 1907 | 2028 | 62.0269 | 61.9048 | 71.3065 | 68.6203 | 0.62027 | 0.61905 | 0.71306 | 0.6862 | 0.001221 | 0.026862 | 241.1418 | 223.877 | 5.6594
38930.433 | 927 | 915 | 38930.433 | 1037 | 966 | 1965.5 | 2086.5 | 56.5934 | 55.8608 | 63.3089 | 58.9744 | 0.56593 | 0.55861 | 0.63309 | 0.58974 | 0.007326 | 0.043346 | 753.6416 | 629.4202 | 25.559
38930.4337 | 978 | 881 | 38930.4337 | 934 | 833 | 2024.5 | 2145.5 | 59.707 | 53.7851 | 57.0208 | 50.8547 | 0.59707 | 0.53785 | 0.57021 | 0.50855 | 0.059219 | 0.061661 | 2380.7899 | 1786.0797 | 27.3044
38930.4344 | 1101 | 1041 | 38930.4344 | 961 | 866 | 2083.5 | 2204.5 | 67.2161 | 63.5531 | 58.6691 | 52.8694 | 0.67216 | 0.63553 | 0.58669 | 0.52869 | 0.03663 | 0.057998 | 887.899 | 1928.5214 | 2.6466
38930.4351 | 953 | 852 | 38930.4351 | 936 | 838 | 2142 | 2263 | 58.1807 | 52.0147 | 57.1429 | 51.16 | 0.58181 | 0.52015 | 0.57143 | 0.5116 | 0.061661 | 0.059829 | 1840.9699 | 2242.7752 | 34.6094

## C2-6
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38930.4092 | 1 | 0 | 38930.4092 | 1 | 0 | -95 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4099 | 1 | 0 | 38930.4099 | 1 | 0 | -36 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4105 | 1 | 0 | 38930.4106 | 1 | 0 | 22.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4112 | 1 | 0 | 38930.4112 | 1 | 0 | 81.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4119 | 1 | 0 | 38930.4119 | 1 | 0 | 140.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4126 | 1 | 0 | 38930.4126 | 1 | 0 | 199 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4133 | 1 | 0 | 38930.4133 | 1 | 0 | 258 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4139 | 1 | 0 | 38930.414 | 1 | 0 | 316.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4146 | 1 | 0 | 38930.4146 | 1 | 0 | 375.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4153 | 1 | 0 | 38930.4153 | 1 | 0 | 434.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.416 | 1 | 0 | 38930.416 | 2 | 0 | 493 | 614 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.4167 | 1 | 0 | 38930.4167 | 1 | 0 | 552 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4173 | 1 | 0 | 38930.4174 | 1 | 0 | 610.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.418 | 1 | 0 | 38930.418 | 1 | 0 | 669.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4187 | 1 | 0 | 38930.4187 | 1 | 0 | 728.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4194 | 1 | 0 | 38930.4194 | 1 | 0 | 787 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4201 | 1 | 0 | 38930.4201 | 1 | 0 | 846 | 967 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4208 | 1 | 0 | 38930.4208 | 1 | 0 | 904.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4214 | 1 | 0 | 38930.4214 | 1 | 0 | 963.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4221 | 1 | 0 | 38930.4221 | 1 | 0 | 1022.5 | 1143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4228 | 1 | 0 | 38930.4228 | 1 | 0 | 1081 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4235 | 1 | 0 | 38930.4235 | 1 | 0 | 1139.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4242 | 1 | 0 | 38930.4242 | 1 | 0 | 1198.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4248 | 1 | 0 | 38930.4248 | 1 | 0 | 1257.5 | 1378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4255 | 1 | 0 | 38930.4255 | 1 | 0 | 1316 | 1437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4262 | 1089 | 1064 | 38930.4262 | 923 | 1034 | 1375 | 1496 | 66.4835 | 64.9573 | 56.3492 | 63.1258 | 0.66484 | 0.64957 | 0.56349 | 0.63126 | 0.015263 | 0.067766 | 134.0392 | 143.984 | 2.2175
38930.4269 | 1191 | 1195 | 38930.4269 | 1148 | 1124 | 1433.5 | 1554.5 | 72.7106 | 72.9548 | 70.0855 | 68.6203 | 0.72711 | 0.72955 | 0.70085 | 0.6862 | 0.002442 | 0.014652 | 1826.8079 | 2571.4605 | 21.9884
38930.4276 | 1150 | 1195 | 38930.4276 | 951 | 919 | 1492.5 | 1613.5 | 70.2076 | 72.9548 | 58.0586 | 56.105 | 0.70208 | 0.72955 | 0.58059 | 0.56105 | 0.027473 | 0.019536 | 148.3428 | 197.7869 | 12.8936
38930.4282 | 926 | 874 | 38930.4283 | 979 | 867 | 1551.5 | 1672.5 | 56.5324 | 53.3578 | 59.768 | 52.9304 | 0.56532 | 0.53358 | 0.59768 | 0.5293 | 0.031746 | 0.068376 | 1511.7218 | 3295.4944 | 34.7599
38930.4289 | 1120 | 1160 | 38930.4289 | 1195 | 1177 | 1610 | 1731 | 68.3761 | 70.8181 | 72.9548 | 71.8559 | 0.68376 | 0.70818 | 0.72955 | 0.71856 | 0.02442 | 0.010989 | 2864.1721 | 21765.2448 | 14.329
38930.4296 | 1166 | 1119 | 38930.4296 | 1111 | 835 | 1669 | 1790 | 71.1844 | 68.315 | 67.8266 | 50.9768 | 0.71184 | 0.68315 | 0.67827 | 0.50977 | 0.028694 | 0.1685 | 5.5656 | 6.5946 | 0.95082
38930.4303 | 1187 | 1187 | 38930.4303 | 1177 | 1148 | 1727.5 | 1848.5 | 72.4664 | 72.4664 | 71.8559 | 70.0855 | 0.72466 | 0.72466 | 0.71856 | 0.70085 | 0 | 0.017705 | 1440.6146 | 1846.6227 | 20.8571
38930.431 | 983 | 872 | 38930.431 | 1091 | 1016 | 1786.5 | 1907.5 | 60.0122 | 53.2357 | 66.6056 | 62.0269 | 0.60012 | 0.53236 | 0.66606 | 0.62027 | 0.067766 | 0.045788 | 559.799 | 959.6997 | 26.7972
38930.4316 | 1012 | 1016 | 38930.4317 | 995 | 871 | 1845.5 | 1966.5 | 61.7827 | 62.0269 | 60.7448 | 53.1746 | 0.61783 | 0.62027 | 0.60745 | 0.53175 | 0.002442 | 0.075702 | 284.7674 | 265.5249 | 6.0788
38930.4323 | 1054 | 975 | 38930.4323 | 1005 | 911 | 1904 | 2025 | 64.3468 | 59.5238 | 61.3553 | 55.6166 | 0.64347 | 0.59524 | 0.61355 | 0.55617 | 0.04823 | 0.057387 | 6928.1157 | 1530.2718 | 8.0888
38930.433 | 934 | 912 | 38930.433 | 1014 | 1111 | 1963 | 2084 | 57.0208 | 55.6777 | 61.9048 | 67.8266 | 0.57021 | 0.55678 | 0.61905 | 0.67827 | 0.013431 | 0.059219 | 439.4993 | 370.3337 | 23.0535
38930.4337 | 1051 | 971 | 38930.4337 | 1158 | 1113 | 2021.5 | 2142.5 | 64.1636 | 59.2796 | 70.696 | 67.9487 | 0.64164 | 0.5928 | 0.70696 | 0.67949 | 0.04884 | 0.027473 | 203.2393 | 219.4119 | 6.4391
38930.4344 | 1112 | 1057 | 38930.4344 | 1163 | 1182 | 2080.5 | 2201.5 | 67.8877 | 64.5299 | 71.0012 | 72.1612 | 0.67888 | 0.6453 | 0.71001 | 0.72161 | 0.033578 | 0.0116 | 927.5804 | 1997.4551 | 5.0436
38930.435 | 923 | 955 | 38930.4351 | 1168 | 1189 | 2139.5 | 2260.5 | 56.3492 | 58.3028 | 71.3065 | 72.5885 | 0.56349 | 0.58303 | 0.71306 | 0.72589 | 0.019536 | 0.012821 | 107.036 | 88.4428 | 11.5501

## C2-5
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38930.4092 | 1 | 0 | 38930.4092 | 1 | 0 | -97.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4098 | 1 | 0 | 38930.4098 | 1 | 0 | -39 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4105 | 1 | 0 | 38930.4105 | 1 | 0 | 20 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4112 | 1 | 0 | 38930.4112 | 1 | 0 | 78.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4119 | 1 | 0 | 38930.4119 | 1 | 0 | 137.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4126 | 1 | 0 | 38930.4126 | 1 | 0 | 196.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4132 | 1 | 0 | 38930.4133 | 1 | 0 | 255 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4139 | 1 | 0 | 38930.4139 | 1 | 0 | 314 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4146 | 1 | 0 | 38930.4146 | 1 | 0 | 372.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4153 | 1 | 0 | 38930.4153 | 1 | 0 | 431.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.416 | 1 | 0 | 38930.416 | 1 | 0 | 490.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4166 | 1 | 0 | 38930.4167 | 1 | 0 | 549 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4173 | 1 | 0 | 38930.4173 | 1 | 0 | 608 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.418 | 1 | 0 | 38930.418 | 1 | 0 | 666.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4187 | 1 | 0 | 38930.4187 | 1 | 0 | 725.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4194 | 1 | 0 | 38930.4194 | 1 | 0 | 784.5 | 905.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.42 | 1 | 0 | 38930.4201 | 1 | 0 | 843 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4207 | 1 | 0 | 38930.4207 | 1 | 0 | 902 | 1023 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4214 | 1 | 0 | 38930.4214 | 1 | 0 | 960.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4221 | 2 | 0 | 38930.4221 | 1 | 0 | 1019.5 | 1140.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38930.4228 | 1 | 1 | 38930.4228 | 1 | 0 | 1078.5 | 1199.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.4234 | 1 | 0 | 38930.4235 | 1 | 0 | 1137 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4241 | 1 | 0 | 38930.4241 | 2 | 0 | 1196 | 1317 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.4248 | 1 | 0 | 38930.4248 | 1 | 0 | 1254.5 | 1375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4255 | 1 | 0 | 38930.4255 | 1 | 0 | 1313.5 | 1434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4262 | 694 | 726 | 38930.4262 | 1036 | 1007 | 1372 | 1493 | 42.3687 | 44.3223 | 63.2479 | 61.4774 | 0.42369 | 0.44322 | 0.63248 | 0.61477 | 0.019536 | 0.017705 | 5944.7642 | 8929.9779 | 94.4002
38930.4268 | 1077 | 1049 | 38930.4269 | 1070 | 1125 | 1431 | 1552 | 65.7509 | 64.0415 | 65.3236 | 68.6813 | 0.65751 | 0.64042 | 0.65324 | 0.68681 | 0.017094 | 0.033578 | 349.3643 | 390.6245 | 0.98517
38930.4275 | 930 | 961 | 38930.4275 | 916 | 929 | 1489.5 | 1610.5 | 56.7766 | 58.6691 | 55.9219 | 56.7155 | 0.56777 | 0.58669 | 0.55922 | 0.56716 | 0.018926 | 0.0079365 | 2126.0925 | 3899.7 | 22.5254
38930.4282 | 1182 | 1155 | 38930.4282 | 943 | 828 | 1548.5 | 1669.5 | 72.1612 | 70.5128 | 57.5702 | 50.5495 | 0.72161 | 0.70513 | 0.5757 | 0.50549 | 0.016484 | 0.070208 | 131.3506 | 169.4031 | 12.194
38930.4289 | 923 | 989 | 38930.4289 | 1137 | 1181 | 1607.5 | 1728.5 | 56.3492 | 60.3785 | 69.4139 | 72.1001 | 0.56349 | 0.60379 | 0.69414 | 0.721 | 0.040293 | 0.026862 | 31.2214 | 26.4046 | 4.2458
38930.4296 | 1164 | 1121 | 38930.4296 | 926 | 1011 | 1666 | 1787 | 71.0623 | 68.4371 | 56.5324 | 61.7216 | 0.71062 | 0.68437 | 0.56532 | 0.61722 | 0.026252 | 0.051893 | 15.4268 | 18.3506 | 2.3788
38930.4302 | 971 | 861 | 38930.4303 | 946 | 858 | 1725 | 1846 | 59.2796 | 52.5641 | 57.7534 | 52.381 | 0.5928 | 0.52564 | 0.57753 | 0.52381 | 0.067155 | 0.053724 | 1129.2296 | 9709.7987 | 32.3061
38930.4309 | 1026 | 932 | 38930.4309 | 1027 | 931 | 1783.5 | 1904.5 | 62.6374 | 56.8987 | 62.6984 | 56.8376 | 0.62637 | 0.56899 | 0.62698 | 0.56838 | 0.057387 | 0.058608 | 2480.0732 | 1857.6897 | 15.7834
38930.4316 | 1145 | 1106 | 38930.4316 | 1146 | 1108 | 1842.5 | 1963.5 | 69.9023 | 67.5214 | 69.9634 | 67.6435 | 0.69902 | 0.67521 | 0.69963 | 0.67643 | 0.02381 | 0.023199 | 6706.9667 | 4501.9837 | 12.2045
38930.4323 | 1045 | 965 | 38930.4323 | 1153 | 1107 | 1901.5 | 2022.5 | 63.7973 | 58.9133 | 70.3907 | 67.5824 | 0.63797 | 0.58913 | 0.70391 | 0.67582 | 0.04884 | 0.028083 | 132.4663 | 132.8729 | 6.0913
38930.433 | 1106 | 1055 | 38930.433 | 1115 | 1171 | 1960 | 2081 | 67.5214 | 64.4078 | 68.0708 | 71.4896 | 0.67521 | 0.64408 | 0.68071 | 0.7149 | 0.031136 | 0.034188 | 2816.0306 | 6922.6925 | 4.4831
38930.4336 | 919 | 884 | 38930.4337 | 940 | 908 | 2018.5 | 2139.5 | 56.105 | 53.9683 | 57.3871 | 55.4335 | 0.56105 | 0.53968 | 0.57387 | 0.55433 | 0.021368 | 0.019536 | 4683.2032 | 9301.1483 | 34.6971
38930.4343 | 929 | 872 | 38930.4343 | 1031 | 1048 | 2077.5 | 2198.5 | 56.7155 | 53.2357 | 62.9426 | 63.9805 | 0.56716 | 0.53236 | 0.62943 | 0.6398 | 0.034799 | 0.010379 | 783.924 | 927.2886 | 32.2989
38930.435 | 931 | 838 | 38930.435 | 962 | 867 | 2136.5 | 2257.5 | 56.8376 | 51.16 | 58.7302 | 52.9304 | 0.56838 | 0.5116 | 0.5873 | 0.5293 | 0.056777 | 0.057998 | 2310.8653 | 2002.4152 | 39.0999

## C2-4
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38930.4091 | 1 | 0 | 38930.4091 | 1 | 0 | -100.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4098 | 1 | 0 | 38930.4098 | 1 | 0 | -41.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4105 | 1 | 0 | 38930.4105 | 1 | 0 | 17 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4112 | 1 | 0 | 38930.4112 | 1 | 0 | 76 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4118 | 1 | 0 | 38930.4119 | 1 | 0 | 134.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4125 | 1 | 0 | 38930.4125 | 1 | 0 | 193.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4132 | 1 | 0 | 38930.4132 | 1 | 0 | 252.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4139 | 1 | 0 | 38930.4139 | 1 | 0 | 311 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4146 | 1 | 0 | 38930.4146 | 1 | 0 | 370 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4152 | 1 | 0 | 38930.4153 | 1 | 0 | 428.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4159 | 1 | 0 | 38930.4159 | 1 | 0 | 487.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4166 | 1 | 0 | 38930.4166 | 1 | 0 | 546.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4173 | 1 | 0 | 38930.4173 | 2 | 0 | 605 | 726 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.418 | 1 | 0 | 38930.418 | 1 | 0 | 664 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4186 | 1 | 0 | 38930.4187 | 1 | 0 | 722.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4193 | 1 | 0 | 38930.4193 | 1 | 0 | 781.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.42 | 1 | 0 | 38930.42 | 1 | 0 | 840.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4207 | 1 | 0 | 38930.4207 | 1 | 0 | 899 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4214 | 1 | 0 | 38930.4214 | 1 | 0 | 958 | 1079 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.422 | 1 | 0 | 38930.4221 | 1 | 0 | 1016.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4227 | 1 | 0 | 38930.4227 | 1 | 0 | 1075.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4234 | 1 | 0 | 38930.4234 | 1 | 0 | 1134.5 | 1255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4241 | 1 | 0 | 38930.4241 | 1 | 0 | 1193 | 1314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4248 | 1 | 0 | 38930.4248 | 1 | 0 | 1251.5 | 1372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4255 | 1 | 0 | 38930.4255 | 1 | 0 | 1310.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4261 | 997 | 960 | 38930.4261 | 988 | 952 | 1369.5 | 1490.5 | 60.8669 | 58.6081 | 60.3175 | 58.1197 | 0.60867 | 0.58608 | 0.60317 | 0.5812 | 0.022589 | 0.021978 | 4834.9475 | 6897.7213 | 16.0198
38930.4268 | 453 | 448 | 38930.4268 | 1160 | 1139 | 1428.5 | 1549.5 | 27.6557 | 27.3504 | 70.8181 | 69.536 | 0.27656 | 0.2735 | 0.70818 | 0.69536 | 0.0030525 | 0.012821 | 23083.8541 | 20444.8567 | 269.2234
38930.4275 | 1144 | 1123 | 38930.4275 | 1157 | 1180 | 1487 | 1608 | 69.8413 | 68.5592 | 70.6349 | 72.0391 | 0.69841 | 0.68559 | 0.70635 | 0.72039 | 0.012821 | 0.014042 | 6931.4551 | 15997.2357 | 13.6263
38930.4282 | 1177 | 1166 | 38930.4282 | 1135 | 1080 | 1545.5 | 1666.5 | 71.8559 | 71.1844 | 69.2918 | 65.9341 | 0.71856 | 0.71184 | 0.69292 | 0.65934 | 0.0067155 | 0.033578 | 644.2238 | 868.2429 | 17.6868
38930.4289 | 983 | 1082 | 38930.4289 | 1175 | 826 | 1604.5 | 1725.5 | 60.0122 | 66.0562 | 71.7338 | 50.4274 | 0.60012 | 0.66056 | 0.71734 | 0.50427 | 0.06044 | 0.21306 | 58.3835 | 58.916 | 1.6454
38930.4295 | 1110 | 1052 | 38930.4295 | 1087 | 1018 | 1663.5 | 1784.5 | 67.7656 | 64.2247 | 66.3614 | 62.149 | 0.67766 | 0.64225 | 0.66361 | 0.62149 | 0.035409 | 0.042125 | 319.7334 | 411.4114 | 3.7455
38930.4302 | 1183 | 1144 | 38930.4302 | 958 | 842 | 1722 | 1843 | 72.2222 | 69.8413 | 58.486 | 51.4042 | 0.72222 | 0.69841 | 0.58486 | 0.51404 | 0.02381 | 0.070818 | 126.5639 | 164.4098 | 11.6305
38930.4309 | 1170 | 1126 | 38930.4309 | 917 | 865 | 1781 | 1902 | 71.4286 | 68.7424 | 55.9829 | 52.8083 | 0.71429 | 0.68742 | 0.55983 | 0.52808 | 0.026862 | 0.031746 | 2596.215 | 14666.9532 | 16.1404
38930.4316 | 1193 | 1182 | 38930.4316 | 946 | 852 | 1839.5 | 1960.5 | 72.8327 | 72.1612 | 57.7534 | 52.0147 | 0.72833 | 0.72161 | 0.57753 | 0.52015 | 0.0067155 | 0.057387 | 67.79 | 87.8052 | 10.3625
38930.4323 | 1189 | 1073 | 38930.4323 | 917 | 941 | 1898.5 | 2019.5 | 72.5885 | 65.5067 | 55.9829 | 57.4481 | 0.72589 | 0.65507 | 0.55983 | 0.57448 | 0.070818 | 0.014652 | 84.4823 | 109.7424 | 7.2647
38930.4329 | 935 | 834 | 38930.433 | 1084 | 1016 | 1957.5 | 2078.5 | 57.0818 | 50.9158 | 66.1783 | 62.0269 | 0.57082 | 0.50916 | 0.66178 | 0.62027 | 0.061661 | 0.041514 | 772.7016 | 1620.843 | 38.8524
38930.4336 | 1111 | 846 | 38930.4336 | 988 | 981 | 2016 | 2137 | 67.8266 | 51.6484 | 60.3175 | 59.8901 | 0.67827 | 0.51648 | 0.60317 | 0.5989 | 0.16178 | 0.0042735 | 101.7653 | 117.559 | 9.9653
38930.4343 | 1133 | 1081 | 38930.4343 | 1184 | 1181 | 2074.5 | 2195.5 | 69.1697 | 65.9951 | 72.2833 | 72.1001 | 0.6917 | 0.65995 | 0.72283 | 0.721 | 0.031746 | 0.0018315 | 812.5915 | 1575.7039 | 8.7839
38930.435 | 1026 | 1118 | 38930.435 | 922 | 890 | 2133.5 | 2254.5 | 62.6374 | 68.254 | 56.2882 | 54.3346 | 0.62637 | 0.68254 | 0.56288 | 0.54335 | 0.056166 | 0.019536 | 406.0316 | 636.2465 | 2.3946

## C2-3
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38930.4091 | 1 | 0 | 38930.4091 | 1 | 0 | -103 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4098 | 1 | 0 | 38930.4098 | 1 | 0 | -44.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4105 | 1 | 0 | 38930.4105 | 1 | 0 | 14.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4111 | 1 | 0 | 38930.4111 | 1 | 0 | 73 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4118 | 1 | 0 | 38930.4118 | 1 | 0 | 132 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4125 | 1 | 0 | 38930.4125 | 1 | 0 | 190.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4132 | 1 | 0 | 38930.4132 | 1 | 0 | 249.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4139 | 1 | 0 | 38930.4139 | 1 | 0 | 308.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4145 | 1 | 0 | 38930.4145 | 1 | 0 | 367 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4152 | 1 | 0 | 38930.4152 | 1 | 0 | 426 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4159 | 1 | 0 | 38930.4159 | 1 | 0 | 484.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4166 | 1 | 0 | 38930.4166 | 1 | 0 | 543.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4173 | 1 | 0 | 38930.4173 | 1 | 0 | 602.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4179 | 1 | 0 | 38930.418 | 1 | 0 | 661 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4186 | 1 | 0 | 38930.4186 | 1 | 0 | 720 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4193 | 1 | 0 | 38930.4193 | 1 | 0 | 778.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.42 | 1 | 0 | 38930.42 | 1 | 0 | 837.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4207 | 1 | 0 | 38930.4207 | 1 | 0 | 896.5 | 1017.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4213 | 1 | 0 | 38930.4214 | 1 | 0 | 955 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.422 | 1 | 0 | 38930.422 | 1 | 0 | 1014 | 1135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4227 | 1 | 0 | 38930.4227 | 1 | 0 | 1072.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4234 | 1 | 0 | 38930.4234 | 1 | 0 | 1131.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4241 | 1 | 0 | 38930.4241 | 1 | 0 | 1190.5 | 1311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4247 | 1 | 0 | 38930.4248 | 1 | 0 | 1249 | 1370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4254 | 1 | 0 | 38930.4254 | 1 | 0 | 1307.5 | 1428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4261 | 313 | 328 | 38930.4261 | 1021 | 987 | 1366.5 | 1487.5 | 19.1087 | 20.0244 | 62.3321 | 60.2564 | 0.19109 | 0.20024 | 0.62332 | 0.60256 | 0.0091575 | 0.020757 | 31404.507 | 3538.9541 | 436.4537
38930.4268 | 927 | 891 | 38930.4268 | 1038 | 1008 | 1425.5 | 1546.5 | 56.5934 | 54.3956 | 63.37 | 61.5385 | 0.56593 | 0.54396 | 0.6337 | 0.61538 | 0.021978 | 0.018315 | 3148.2419 | 53274.9817 | 33.0491
38930.4275 | 1047 | 1133 | 38930.4275 | 1091 | 1066 | 1484 | 1605 | 63.9194 | 69.1697 | 66.6056 | 65.0794 | 0.63919 | 0.6917 | 0.66606 | 0.65079 | 0.052503 | 0.015263 | 198.5677 | 251.3005 | 4.2289
38930.4281 | 1174 | 1103 | 38930.4282 | 1117 | 1158 | 1543 | 1664 | 71.6728 | 67.3382 | 68.1929 | 70.696 | 0.71673 | 0.67338 | 0.68193 | 0.70696 | 0.043346 | 0.025031 | 1341.4359 | 110422.4676 | 14.8533
38930.4288 | 934 | 1026 | 38930.4288 | 1194 | 1166 | 1601.5 | 1722.5 | 57.0208 | 62.6374 | 72.8938 | 71.1844 | 0.57021 | 0.62637 | 0.72894 | 0.71184 | 0.056166 | 0.017094 | 202.0232 | 208.7036 | 10.083
38930.4295 | 1112 | 1151 | 38930.4295 | 1012 | 919 | 1660.5 | 1781.5 | 67.8877 | 70.2686 | 61.7827 | 56.105 | 0.67888 | 0.70269 | 0.61783 | 0.56105 | 0.02381 | 0.056777 | 69.2228 | 81.8004 | 5.863
38930.4302 | 1001 | 897 | 38930.4302 | 955 | 1056 | 1719.5 | 1840.5 | 61.1111 | 54.7619 | 58.3028 | 64.4689 | 0.61111 | 0.54762 | 0.58303 | 0.64469 | 0.063492 | 0.061661 | 1141.229 | 13674.9665 | 23.797
38930.4309 | 1179 | 1142 | 38930.4309 | 946 | 909 | 1778 | 1899 | 71.978 | 69.7192 | 57.7534 | 55.4945 | 0.71978 | 0.69719 | 0.57753 | 0.55495 | 0.022589 | 0.022589 | 5610.8649 | 5610.8649 | 17.893
38930.4315 | 1070 | 995 | 38930.4316 | 1115 | 1064 | 1837 | 1958 | 65.3236 | 60.7448 | 68.0708 | 64.9573 | 0.65324 | 0.60745 | 0.68071 | 0.64957 | 0.045788 | 0.031136 | 73.5286 | 74.0591 | 2.0534
38930.4322 | 983 | 1083 | 38930.4322 | 1005 | 914 | 1895.5 | 2016.5 | 60.0122 | 66.1172 | 61.3553 | 55.7998 | 0.60012 | 0.66117 | 0.61355 | 0.558 | 0.06105 | 0.055556 | 2140.7687 | 2293.7971 | 4.1603
38930.4329 | 1156 | 829 | 38930.4329 | 1004 | 1002 | 1954.5 | 2075.5 | 70.5739 | 50.6105 | 61.2943 | 61.1722 | 0.70574 | 0.50611 | 0.61294 | 0.61172 | 0.19963 | 0.001221 | 63.9063 | 70.8222 | 6.4025
38930.4336 | 1169 | 840 | 38930.4336 | 1006 | 918 | 2013.5 | 2134.5 | 71.3675 | 51.2821 | 61.4164 | 56.044 | 0.71368 | 0.51282 | 0.61416 | 0.56044 | 0.20085 | 0.053724 | 94.3641 | 125.1113 | 6.8824
38930.4343 | 990 | 1090 | 38930.4343 | 1191 | 1172 | 2072 | 2193 | 60.4396 | 66.5446 | 72.7106 | 71.5507 | 0.6044 | 0.66545 | 0.72711 | 0.71551 | 0.06105 | 0.0116 | 338.5457 | 470.3976 | 2.4983
38930.4349 | 999 | 997 | 38930.435 | 960 | 865 | 2131 | 2252 | 60.989 | 60.8669 | 58.6081 | 52.8083 | 0.60989 | 0.60867 | 0.58608 | 0.52808 | 0.001221 | 0.057998 | 456.7548 | 412.1556 | 9.4455

## C1-7
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38930.4091 | 1 | 0 | 38930.4091 | 1 | 0 | -106 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4097 | 1 | 0 | 38930.4097 | 1 | 0 | -47.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4104 | 1 | 0 | 38930.4104 | 1 | 0 | 11.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4111 | 1 | 0 | 38930.4111 | 1 | 0 | 70.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4118 | 1 | 0 | 38930.4118 | 1 | 0 | 129 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4125 | 1 | 0 | 38930.4125 | 1 | 0 | 188 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4131 | 1 | 0 | 38930.4131 | 1 | 0 | 246.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4138 | 1 | 0 | 38930.4138 | 1 | 0 | 305.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4145 | 1 | 0 | 38930.4145 | 1 | 0 | 364.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4152 | 1 | 0 | 38930.4152 | 1 | 0 | 423 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4159 | 1 | 0 | 38930.4159 | 1 | 0 | 482 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4165 | 1 | 0 | 38930.4166 | 1 | 0 | 540.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4172 | 1 | 0 | 38930.4172 | 1 | 0 | 599.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4179 | 1 | 0 | 38930.4179 | 1 | 0 | 658.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4186 | 1 | 0 | 38930.4186 | 1 | 0 | 717 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4193 | 1 | 0 | 38930.4193 | 1 | 0 | 775.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4199 | 1 | 0 | 38930.42 | 1 | 0 | 834.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4206 | 1 | 0 | 38930.4206 | 1 | 0 | 893.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4213 | 1 | 0 | 38930.4213 | 1 | 0 | 952.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.422 | 1 | 0 | 38930.422 | 1 | 0 | 1011 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4227 | 1 | 0 | 38930.4227 | 1 | 0 | 1069.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4233 | 1 | 0 | 38930.4234 | 1 | 0 | 1128.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.424 | 1 | 0 | 38930.424 | 1 | 0 | 1187.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4247 | 1 | 0 | 38930.4247 | 1 | 0 | 1246 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4254 | 1 | 0 | 38930.4254 | 1 | 0 | 1305 | 1426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4261 | 3 | 9 | 38930.4261 | 84 | 79 | 1363.5 | 1484.5 | 0.18315 | 0.54945 | 5.1282 | 4.823 | 0.0018315 | 0.0054945 | 0.051282 | 0.04823 | 0.003663 | 0.0030525 | 35291.6104 | 42482.3273 | 23289.8442
38930.4267 | 1080 | 1052 | 38930.4268 | 1051 | 1021 | 1422.5 | 1543.5 | 65.9341 | 64.2247 | 64.1636 | 62.3321 | 0.65934 | 0.64225 | 0.64164 | 0.62332 | 0.017094 | 0.018315 | 1261.1273 | 1951.3127 | 1.7162
38930.4274 | 1186 | 1168 | 38930.4274 | 1142 | 1117 | 1481.5 | 1602.5 | 72.4054 | 71.3065 | 69.7192 | 68.1929 | 0.72405 | 0.71306 | 0.69719 | 0.68193 | 0.010989 | 0.015263 | 3450.8912 | 13178.0759 | 20.4765
38930.4281 | 1065 | 977 | 38930.4281 | 937 | 822 | 1540 | 1661 | 65.0183 | 59.6459 | 57.2039 | 50.1832 | 0.65018 | 0.59646 | 0.57204 | 0.50183 | 0.053724 | 0.070208 | 4843.6194 | 1472.2087 | 6.8068
38930.4288 | 968 | 857 | 38930.4288 | 1198 | 1177 | 1599 | 1720 | 59.0965 | 52.3199 | 73.138 | 71.8559 | 0.59096 | 0.5232 | 0.73138 | 0.71856 | 0.067766 | 0.012821 | 46.6999 | 36.6103 | 9.0066
38930.4295 | 959 | 848 | 38930.4295 | 994 | 979 | 1657.5 | 1778.5 | 58.547 | 51.7705 | 60.6838 | 59.768 | 0.58547 | 0.5177 | 0.60684 | 0.59768 | 0.067766 | 0.0091575 | 413.6464 | 504.8008 | 30.1205
38930.4302 | 1024 | 929 | 38930.4302 | 974 | 948 | 1716.5 | 1837.5 | 62.5153 | 56.7155 | 59.4628 | 57.8755 | 0.62515 | 0.56716 | 0.59463 | 0.57875 | 0.057998 | 0.015873 | 427.9728 | 582.5909 | 14.7015
38930.4308 | 1012 | 913 | 38930.4308 | 935 | 826 | 1775.5 | 1896.5 | 61.7827 | 55.7387 | 57.0818 | 50.4274 | 0.61783 | 0.55739 | 0.57082 | 0.50427 | 0.06044 | 0.066545 | 3173.4741 | 1419.7846 | 19.2386
38930.4315 | 1163 | 1183 | 38930.4315 | 959 | 848 | 1834 | 1955 | 71.0012 | 72.2222 | 58.547 | 51.7705 | 0.71001 | 0.72222 | 0.58547 | 0.5177 | 0.01221 | 0.067766 | 86.0721 | 109.1581 | 10.2782
38930.4322 | 1135 | 1082 | 38930.4322 | 1166 | 1189 | 1893 | 2014 | 69.2918 | 66.0562 | 71.1844 | 72.5885 | 0.69292 | 0.66056 | 0.71184 | 0.72589 | 0.032357 | 0.014042 | 1423.744 | 6894.5604 | 9.4726
38930.4329 | 1194 | 1180 | 38930.4329 | 1094 | 1131 | 1951.5 | 2072.5 | 72.8938 | 72.0391 | 66.7888 | 69.0476 | 0.72894 | 0.72039 | 0.66789 | 0.69048 | 0.008547 | 0.022589 | 1354.3037 | 2190.8967 | 21.1515
38930.4336 | 1078 | 1008 | 38930.4336 | 1077 | 1155 | 2010.5 | 2131.5 | 65.812 | 61.5385 | 65.7509 | 70.5128 | 0.65812 | 0.61538 | 0.65751 | 0.70513 | 0.042735 | 0.047619 | 1506.5477 | 77624.6028 | 2.6771
38930.4342 | 927 | 862 | 38930.4342 | 1191 | 1181 | 2069.5 | 2190.5 | 56.5934 | 52.6252 | 72.7106 | 72.1001 | 0.56593 | 0.52625 | 0.72711 | 0.721 | 0.039683 | 0.006105 | 147.1648 | 116.343 | 20.2144
38930.4349 | 1131 | 1078 | 38930.4349 | 1085 | 1157 | 2128 | 2249 | 69.0476 | 65.812 | 66.2393 | 70.6349 | 0.69048 | 0.65812 | 0.66239 | 0.70635 | 0.032357 | 0.043956 | 1027.6703 | 2533.0206 | 8.5654

## C1-6
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38930.409 | 1 | 0 | 38930.409 | 1 | 0 | -108.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4097 | 1 | 0 | 38930.4097 | 1 | 0 | -50 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4104 | 1 | 0 | 38930.4104 | 1 | 0 | 8.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4111 | 1 | 0 | 38930.4111 | 1 | 0 | 67.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4117 | 1 | 0 | 38930.4118 | 1 | 0 | 126.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4124 | 1 | 0 | 38930.4124 | 1 | 0 | 185 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4131 | 1 | 0 | 38930.4131 | 1 | 0 | 244 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4138 | 1 | 0 | 38930.4138 | 1 | 0 | 302.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4145 | 1 | 0 | 38930.4145 | 1 | 0 | 361.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4152 | 1 | 0 | 38930.4152 | 1 | 0 | 420.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38930.4158 | 1 | 0 | 480 | 601 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4165 | 1 | 0 | 38930.4165 | 1 | 0 | 538 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4172 | 1 | 0 | 38930.4172 | 1 | 0 | 596.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4179 | 1 | 0 | 38930.4179 | 1 | 0 | 655.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4186 | 1 | 0 | 38930.4186 | 1 | 0 | 714.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4192 | 1 | 0 | 38930.4192 | 1 | 0 | 773 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4199 | 1 | 0 | 38930.4199 | 1 | 0 | 831.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4206 | 1 | 0 | 38930.4206 | 1 | 0 | 890.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4213 | 1 | 0 | 38930.4213 | 1 | 0 | 949.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.422 | 1 | 0 | 38930.422 | 1 | 0 | 1008.5 | 1129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4226 | 1 | 0 | 38930.4227 | 1 | 0 | 1067 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4233 | 1 | 0 | 38930.4233 | 1 | 0 | 1125.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.424 | 1 | 0 | 38930.424 | 1 | 0 | 1184.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4247 | 1 | 0 | 38930.4247 | 1 | 0 | 1243.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4253 | 1 | 0 | 38930.4254 | 1 | 0 | 1302 | 1423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.426 | 27 | 32 | 38930.4261 | 872 | 836 | 1361 | 1482 | 1.6484 | 1.9536 | 53.2357 | 51.0379 | 0.016484 | 0.019536 | 0.53236 | 0.51038 | 0.0030525 | 0.021978 | 50702.3518 | 3612.7454 | 6245.9266
38930.4267 | 967 | 930 | 38930.4267 | 1041 | 1087 | 1419.5 | 1540.5 | 59.0354 | 56.7766 | 63.5531 | 66.3614 | 0.59035 | 0.56777 | 0.63553 | 0.66361 | 0.022589 | 0.028083 | 6986.4589 | 4515.3184 | 22.7247
38930.4274 | 1198 | 1003 | 38930.4274 | 992 | 958 | 1478.5 | 1599.5 | 73.138 | 61.2332 | 60.5617 | 58.486 | 0.73138 | 0.61233 | 0.60562 | 0.58486 | 0.11905 | 0.020757 | 35.1668 | 41.6712 | 2.5801
38930.4281 | 1094 | 1017 | 38930.4281 | 976 | 851 | 1537.5 | 1658.5 | 66.7888 | 62.0879 | 59.5849 | 51.9536 | 0.66789 | 0.62088 | 0.59585 | 0.51954 | 0.047009 | 0.076313 | 740.8291 | 1679.5678 | 0.18746
38930.4287 | 1143 | 1084 | 38930.4288 | 998 | 892 | 1596 | 1717 | 69.7802 | 66.1783 | 60.928 | 54.4567 | 0.6978 | 0.66178 | 0.60928 | 0.54457 | 0.03602 | 0.064713 | 233.4462 | 304.0487 | 7.9124
38930.4294 | 1018 | 921 | 38930.4295 | 1092 | 1020 | 1655 | 1776 | 62.149 | 56.2271 | 66.6667 | 62.2711 | 0.62149 | 0.56227 | 0.66667 | 0.62271 | 0.059219 | 0.043956 | 545.7807 | 888.7071 | 16.9836
38930.4301 | 988 | 879 | 38930.4301 | 958 | 844 | 1713.5 | 1834.5 | 60.3175 | 53.663 | 58.486 | 51.5263 | 0.60317 | 0.53663 | 0.58486 | 0.51526 | 0.066545 | 0.069597 | 2170.179 | 1537.7877 | 26.2797
38930.4308 | 1087 | 1160 | 38930.4308 | 953 | 837 | 1772.5 | 1893.5 | 66.3614 | 70.8181 | 58.1807 | 51.0989 | 0.66361 | 0.70818 | 0.58181 | 0.51099 | 0.044567 | 0.070818 | 439.6354 | 723.2833 | 10.1471
38930.4315 | 984 | 880 | 38930.4315 | 980 | 878 | 1831.5 | 1952.5 | 60.0733 | 53.7241 | 59.8291 | 53.602 | 0.60073 | 0.53724 | 0.59829 | 0.53602 | 0.063492 | 0.062271 | 1804.377 | 2124.1253 | 27.0254
38930.4322 | 1128 | 1179 | 38930.4322 | 974 | 877 | 1890 | 2011 | 68.8645 | 71.978 | 59.4628 | 53.5409 | 0.68864 | 0.71978 | 0.59463 | 0.53541 | 0.031136 | 0.059219 | 156.3352 | 203.6026 | 11.0337
38930.4328 | 1017 | 1025 | 38930.4329 | 1128 | 1072 | 1949 | 2070 | 62.0879 | 62.5763 | 68.8645 | 65.4457 | 0.62088 | 0.62576 | 0.68864 | 0.65446 | 0.004884 | 0.034188 | 38.7691 | 36.3598 | 1.8475
38930.4335 | 970 | 1076 | 38930.4335 | 949 | 925 | 2007.5 | 2128.5 | 59.2186 | 65.6899 | 57.9365 | 56.4713 | 0.59219 | 0.6569 | 0.57937 | 0.56471 | 0.064713 | 0.014652 | 343.5741 | 474.6671 | 5.1448
38930.4342 | 1110 | 1048 | 38930.4342 | 1156 | 1109 | 2066.5 | 2187.5 | 67.7656 | 63.9805 | 70.5739 | 67.7045 | 0.67766 | 0.6398 | 0.70574 | 0.67705 | 0.037851 | 0.028694 | 2007.3121 | 8710.334 | 4.2433
38930.4349 | 980 | 888 | 38930.4349 | 1082 | 1017 | 2125.5 | 2246.5 | 59.8291 | 54.2125 | 66.0562 | 62.0879 | 0.59829 | 0.54212 | 0.66056 | 0.62088 | 0.056166 | 0.039683 | 713.824 | 1330.8278 | 25.6639

## C1-5
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38930.409 | 1 | 0 | 38930.409 | 1 | 0 | -111.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4097 | 1 | 0 | 38930.4097 | 1 | 0 | -53 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4103 | 1 | 0 | 38930.4104 | 1 | 0 | 6 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.411 | 1 | 0 | 38930.411 | 1 | 0 | 64.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4117 | 1 | 0 | 38930.4117 | 1 | 0 | 123.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4124 | 1 | 0 | 38930.4124 | 1 | 0 | 182.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4131 | 1 | 0 | 38930.4131 | 1 | 0 | 241 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4137 | 1 | 0 | 38930.4138 | 1 | 0 | 300 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4144 | 1 | 0 | 38930.4144 | 1 | 0 | 358.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4151 | 1 | 0 | 38930.4151 | 1 | 0 | 417.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4158 | 1 | 0 | 38930.4158 | 1 | 0 | 476.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4165 | 1 | 0 | 38930.4165 | 1 | 0 | 535 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4172 | 1 | 0 | 38930.4172 | 1 | 0 | 594 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4178 | 1 | 0 | 38930.4178 | 1 | 0 | 652.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4185 | 1 | 0 | 38930.4185 | 1 | 0 | 711.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4192 | 1 | 0 | 38930.4192 | 1 | 0 | 770.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4199 | 1 | 0 | 38930.4199 | 1 | 0 | 829 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4206 | 1 | 0 | 38930.4206 | 1 | 0 | 888 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4212 | 1 | 0 | 38930.4212 | 1 | 0 | 946.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4219 | 1 | 0 | 38930.4219 | 1 | 0 | 1005.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4226 | 1 | 0 | 38930.4226 | 1 | 0 | 1064 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4233 | 1 | 0 | 38930.4233 | 1 | 0 | 1123 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.424 | 1 | 0 | 38930.424 | 1 | 0 | 1181.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4246 | 1 | 0 | 38930.4247 | 1 | 0 | 1240.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4253 | 1 | 0 | 38930.4253 | 1 | 0 | 1299.5 | 1420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.426 | 1053 | 1021 | 38930.426 | 1049 | 1095 | 1358 | 1479 | 64.2857 | 62.3321 | 64.0415 | 66.8498 | 0.64286 | 0.62332 | 0.64042 | 0.6685 | 0.019536 | 0.028083 | 76.5441 | 75.4704 | 1.6437
38930.4267 | 969 | 931 | 38930.4267 | 1077 | 1144 | 1417 | 1538 | 59.1575 | 56.8376 | 65.7509 | 69.8413 | 0.59158 | 0.56838 | 0.65751 | 0.69841 | 0.023199 | 0.040904 | 522.2633 | 514.2214 | 19.1556
38930.4274 | 1075 | 1049 | 38930.4274 | 1165 | 1146 | 1475.5 | 1596.5 | 65.6288 | 64.0415 | 71.1233 | 69.9634 | 0.65629 | 0.64042 | 0.71123 | 0.69963 | 0.015873 | 0.0116 | 4622.9858 | 29578.0759 | 1.0432
38930.428 | 1183 | 1160 | 38930.4281 | 911 | 855 | 1534.5 | 1655.5 | 72.2222 | 70.8181 | 55.6166 | 52.1978 | 0.72222 | 0.70818 | 0.55617 | 0.52198 | 0.014042 | 0.034188 | 337.9541 | 459.9684 | 16.2853
38930.4287 | 922 | 980 | 38930.4287 | 1061 | 977 | 1593.5 | 1714.5 | 56.2882 | 59.8291 | 64.7741 | 59.6459 | 0.56288 | 0.59829 | 0.64774 | 0.59646 | 0.035409 | 0.051282 | 1387.2181 | 3518.0021 | 20.9375
38930.4294 | 1011 | 914 | 38930.4294 | 1031 | 1120 | 1652 | 1773 | 61.7216 | 55.7998 | 62.9426 | 68.3761 | 0.61722 | 0.558 | 0.62943 | 0.68376 | 0.059219 | 0.054335 | 714.6468 | 1597.7667 | 19.3595
38930.4301 | 1076 | 999 | 38930.4301 | 951 | 1052 | 1711 | 1832 | 65.6899 | 60.989 | 58.0586 | 64.2247 | 0.6569 | 0.60989 | 0.58059 | 0.64225 | 0.047009 | 0.061661 | 1348.8906 | 828859.989 | 3.8053
38930.4308 | 1183 | 1179 | 38930.4308 | 1150 | 1095 | 1769.5 | 1890.5 | 72.2222 | 71.978 | 70.2076 | 66.8498 | 0.72222 | 0.71978 | 0.70208 | 0.6685 | 0.002442 | 0.033578 | 648.2345 | 845.345 | 18.884
38930.4314 | 970 | 864 | 38930.4315 | 1155 | 1109 | 1828.5 | 1949.5 | 59.2186 | 52.7473 | 70.5128 | 67.7045 | 0.59219 | 0.52747 | 0.70513 | 0.67705 | 0.064713 | 0.028083 | 221.4344 | 210.6346 | 21.8979
38930.4321 | 928 | 849 | 38930.4321 | 1042 | 963 | 1887.5 | 2008.5 | 56.6545 | 51.8315 | 63.6142 | 58.7912 | 0.56654 | 0.51832 | 0.63614 | 0.58791 | 0.04823 | 0.04823 | 2574.7089 | 2574.7089 | 38.0986
38930.4328 | 1190 | 907 | 38930.4328 | 1019 | 930 | 1946 | 2067 | 72.6496 | 55.3724 | 62.21 | 56.7766 | 0.7265 | 0.55372 | 0.6221 | 0.56777 | 0.17277 | 0.054335 | 72.6533 | 91.8533 | 0.84563
38930.4335 | 1061 | 990 | 38930.4335 | 1143 | 1096 | 2005 | 2126 | 64.7741 | 60.4396 | 69.7802 | 66.9109 | 0.64774 | 0.6044 | 0.6978 | 0.66911 | 0.043346 | 0.028694 | 288.968 | 337.8136 | 4.8338
38930.4342 | 1013 | 860 | 38930.4342 | 1002 | 915 | 2063.5 | 2184.5 | 61.8437 | 52.5031 | 61.1722 | 55.8608 | 0.61844 | 0.52503 | 0.61172 | 0.55861 | 0.093407 | 0.053114 | 457.3524 | 982.6421 | 25.3314
38930.4348 | 990 | 989 | 38930.4349 | 1016 | 932 | 2122.5 | 2243.5 | 60.4396 | 60.3785 | 62.0269 | 56.8987 | 0.6044 | 0.60379 | 0.62027 | 0.56899 | 0.0006105 | 0.051282 | 378.4231 | 334.3893 | 10.4315

## C1-4
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38930.409 | 1 | 0 | 38930.409 | 1 | 0 | -114.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4096 | 1 | 0 | 38930.4097 | 1 | 0 | -55.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4103 | 1 | 0 | 38930.4103 | 1 | 0 | 3 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.411 | 1 | 0 | 38930.411 | 1 | 0 | 62 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4117 | 1 | 0 | 38930.4117 | 1 | 0 | 120.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4124 | 1 | 0 | 38930.4124 | 1 | 0 | 179.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.413 | 1 | 0 | 38930.4131 | 1 | 0 | 238.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4137 | 1 | 0 | 38930.4137 | 1 | 0 | 297 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4144 | 1 | 0 | 38930.4144 | 1 | 0 | 356 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4151 | 1 | 0 | 38930.4151 | 1 | 0 | 414.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4158 | 1 | 0 | 38930.4158 | 1 | 0 | 473.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4164 | 1 | 0 | 38930.4165 | 1 | 0 | 532.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4171 | 1 | 0 | 38930.4171 | 1 | 0 | 591 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4178 | 1 | 0 | 38930.4178 | 1 | 0 | 650 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4185 | 1 | 0 | 38930.4185 | 1 | 0 | 708.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4192 | 1 | 0 | 38930.4192 | 1 | 0 | 767.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4198 | 1 | 0 | 38930.4199 | 1 | 0 | 826 | 947 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4205 | 1 | 0 | 38930.4205 | 1 | 0 | 885 | 1006 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4212 | 1 | 0 | 38930.4212 | 1 | 0 | 943.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4219 | 1 | 0 | 38930.4219 | 1 | 0 | 1002.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4226 | 1 | 0 | 38930.4226 | 1 | 0 | 1061.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4232 | 1 | 0 | 38930.4233 | 2 | 0 | 1120 | 1241 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.4239 | 1 | 0 | 38930.4239 | 1 | 0 | 1179 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4246 | 1 | 0 | 38930.4246 | 1 | 0 | 1237.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4253 | 1 | 0 | 38930.4253 | 1 | 0 | 1296.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.426 | 960 | 924 | 38930.426 | 926 | 950 | 1355.5 | 1476.5 | 58.6081 | 56.4103 | 56.5324 | 57.9976 | 0.58608 | 0.5641 | 0.56532 | 0.57998 | 0.021978 | 0.014652 | 2387.8216 | 7519.8207 | 24.4604
38930.4266 | 100 | 106 | 38930.4267 | 215 | 145 | 1414 | 1535 | 6.105 | 6.4713 | 13.1258 | 8.8523 | 0.06105 | 0.064713 | 0.13126 | 0.088523 | 0.003663 | 0.042735 | 95898.8695 | 2717.3266 | 1735.2179
38930.4273 | 923 | 1034 | 38930.4273 | 945 | 980 | 1473 | 1594 | 56.3492 | 63.1258 | 57.6923 | 59.8291 | 0.56349 | 0.63126 | 0.57692 | 0.59829 | 0.067766 | 0.021368 | 403.0026 | 561.0771 | 12.8065
38930.428 | 1102 | 1032 | 38930.428 | 1155 | 1109 | 1531.5 | 1652.5 | 67.2772 | 63.0037 | 70.5128 | 67.7045 | 0.67277 | 0.63004 | 0.70513 | 0.67705 | 0.042735 | 0.028083 | 897.9888 | 2423.2662 | 1.9524
38930.4287 | 1146 | 1091 | 38930.4287 | 1038 | 947 | 1590.5 | 1711.5 | 69.9634 | 66.6056 | 63.37 | 57.8144 | 0.69963 | 0.66606 | 0.6337 | 0.57814 | 0.033578 | 0.055556 | 15.9105 | 18.1143 | 1.7428
38930.4294 | 978 | 877 | 38930.4294 | 1131 | 1082 | 1649.5 | 1770.5 | 59.707 | 53.5409 | 69.0476 | 66.0562 | 0.59707 | 0.53541 | 0.69048 | 0.66056 | 0.061661 | 0.029915 | 294.7791 | 308.7584 | 22.2232
38930.43 | 962 | 848 | 38930.4301 | 1080 | 1001 | 1708 | 1829 | 58.7302 | 51.7705 | 65.9341 | 61.1111 | 0.5873 | 0.5177 | 0.65934 | 0.61111 | 0.069597 | 0.04823 | 670.0087 | 1467.3361 | 33.4536
38930.4307 | 997 | 889 | 38930.4308 | 1125 | 1060 | 1767 | 1888 | 60.8669 | 54.2735 | 68.6813 | 64.7131 | 0.60867 | 0.54274 | 0.68681 | 0.64713 | 0.065934 | 0.039683 | 327.6907 | 382.2486 | 20.2412
38930.4314 | 973 | 953 | 38930.4314 | 1036 | 950 | 1825.5 | 1946.5 | 59.4017 | 58.1807 | 63.2479 | 57.9976 | 0.59402 | 0.58181 | 0.63248 | 0.57998 | 0.01221 | 0.052503 | 533.7424 | 492.2777 | 16.311
38930.4321 | 982 | 887 | 38930.4321 | 1040 | 957 | 1884.5 | 2005.5 | 59.9512 | 54.1514 | 63.4921 | 58.4249 | 0.59951 | 0.54151 | 0.63492 | 0.58425 | 0.057998 | 0.050672 | 1288.1388 | 12323.9859 | 27.2893
38930.4328 | 1041 | 1057 | 38930.4328 | 929 | 895 | 1943.5 | 2064.5 | 63.5531 | 64.5299 | 56.7155 | 54.6398 | 0.63553 | 0.6453 | 0.56716 | 0.5464 | 0.009768 | 0.020757 | 1902.3432 | 2619.4095 | 1.3687
38930.4334 | 1066 | 996 | 38930.4335 | 1148 | 1101 | 2002 | 2123 | 65.0794 | 60.8059 | 70.0855 | 67.2161 | 0.65079 | 0.60806 | 0.70085 | 0.67216 | 0.042735 | 0.028694 | 415.6377 | 547.5328 | 4.3314
38930.4341 | 1108 | 1149 | 38930.4342 | 1076 | 1006 | 2061 | 2182 | 67.6435 | 70.1465 | 65.6899 | 61.4164 | 0.67643 | 0.70147 | 0.6569 | 0.61416 | 0.025031 | 0.042735 | 299.8196 | 390.5398 | 9.9764
38930.4348 | 1121 | 1065 | 38930.4348 | 975 | 1079 | 2119.5 | 2240.5 | 68.4371 | 65.0183 | 59.5238 | 65.873 | 0.68437 | 0.65018 | 0.59524 | 0.65873 | 0.034188 | 0.063492 | 42.9428 | 47.2474 | 2.1988

## C1-3
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38930.4089 | 1 | 0 | 38930.4089 | 1 | 0 | -117.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4096 | 1 | 0 | 38930.4096 | 1 | 0 | -58.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4103 | 1 | 0 | 38930.4103 | 1 | 0 | 0.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.411 | 1 | 0 | 38930.411 | 1 | 0 | 59.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4116 | 1 | 0 | 38930.4117 | 1 | 0 | 118 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4123 | 1 | 0 | 38930.4123 | 1 | 0 | 176.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.413 | 1 | 0 | 38930.413 | 1 | 0 | 235.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4137 | 1 | 0 | 38930.4137 | 1 | 0 | 294.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4144 | 1 | 0 | 38930.4144 | 1 | 0 | 353 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.415 | 1 | 0 | 38930.4151 | 1 | 0 | 412 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4157 | 1 | 0 | 38930.4157 | 1 | 0 | 470.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4164 | 1 | 0 | 38930.4164 | 1 | 0 | 529.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4171 | 1 | 0 | 38930.4171 | 1 | 0 | 588.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4178 | 1 | 1 | 38930.4178 | 1 | 0 | 647 | 768 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.4184 | 1 | 0 | 38930.4185 | 1 | 0 | 706 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4191 | 1 | 0 | 38930.4191 | 1 | 0 | 764.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4198 | 1 | 0 | 38930.4198 | 1 | 0 | 823.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4205 | 1 | 0 | 38930.4205 | 1 | 0 | 882.5 | 1003.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4212 | 1 | 0 | 38930.4212 | 1 | 0 | 941 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4219 | 1 | 0 | 38930.4219 | 1 | 0 | 1000 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4225 | 1 | 0 | 38930.4225 | 1 | 0 | 1058.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4232 | 1 | 0 | 38930.4232 | 1 | 0 | 1117.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4239 | 1 | 0 | 38930.4239 | 1 | 0 | 1176 | 1297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4246 | 1 | 0 | 38930.4246 | 1 | 0 | 1235 | 1356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4253 | 1 | 0 | 38930.4253 | 1 | 0 | 1293.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4259 | 1 | 0 | 38930.4259 | 1 | 0 | 1352.5 | 1473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4266 | 956 | 988 | 38930.4266 | 945 | 921 | 1411.5 | 1532.5 | 58.3639 | 60.3175 | 57.6923 | 56.2271 | 0.58364 | 0.60317 | 0.57692 | 0.56227 | 0.019536 | 0.014652 | 3230.7803 | 25915.4281 | 17.0415
38930.4273 | 1102 | 1160 | 38930.4273 | 989 | 956 | 1470 | 1591 | 67.2772 | 70.8181 | 60.3785 | 58.3639 | 0.67277 | 0.70818 | 0.60379 | 0.58364 | 0.035409 | 0.020147 | 101.9825 | 124.2813 | 7.1168
38930.428 | 1138 | 1082 | 38930.428 | 1182 | 1151 | 1529 | 1650 | 69.475 | 66.0562 | 72.1612 | 70.2686 | 0.69475 | 0.66056 | 0.72161 | 0.70269 | 0.034188 | 0.018926 | 1815.6316 | 47072.5798 | 9.8663
38930.4287 | 1123 | 1060 | 38930.4287 | 1068 | 986 | 1587.5 | 1708.5 | 68.5592 | 64.7131 | 65.2015 | 60.1954 | 0.68559 | 0.64713 | 0.65201 | 0.60195 | 0.038462 | 0.050061 | 50.1301 | 55.4422 | 2.3547
38930.4293 | 1026 | 936 | 38930.4294 | 1086 | 1015 | 1646.5 | 1767.5 | 62.6374 | 57.1429 | 66.3004 | 61.9658 | 0.62637 | 0.57143 | 0.663 | 0.61966 | 0.054945 | 0.043346 | 640.4087 | 1173.8372 | 14.868
38930.43 | 1182 | 1143 | 38930.43 | 927 | 876 | 1705.5 | 1826.5 | 72.1612 | 69.7802 | 56.5934 | 53.4799 | 0.72161 | 0.6978 | 0.56593 | 0.5348 | 0.02381 | 0.031136 | 855.1126 | 1635.7341 | 17.4775
38930.4307 | 1036 | 944 | 38930.4307 | 1135 | 1078 | 1764 | 1885 | 63.2479 | 57.6313 | 69.2918 | 65.812 | 0.63248 | 0.57631 | 0.69292 | 0.65812 | 0.056166 | 0.034799 | 98.7428 | 94.5197 | 6.8471
38930.4314 | 1124 | 1165 | 38930.4314 | 953 | 1056 | 1823 | 1944 | 68.6203 | 71.1233 | 58.1807 | 64.4689 | 0.6862 | 0.71123 | 0.58181 | 0.64469 | 0.025031 | 0.062882 | 114.5275 | 141.63 | 8.854
38930.4321 | 972 | 877 | 38930.4321 | 1051 | 975 | 1881.5 | 2002.5 | 59.3407 | 53.5409 | 64.1636 | 59.5238 | 0.59341 | 0.53541 | 0.64164 | 0.59524 | 0.057998 | 0.046398 | 1041.7994 | 6038.2948 | 29.6145
38930.4327 | 1000 | 906 | 38930.4328 | 1083 | 1117 | 1940.5 | 2061.5 | 61.0501 | 55.3114 | 66.1172 | 68.1929 | 0.6105 | 0.55311 | 0.66117 | 0.68193 | 0.057387 | 0.020757 | 203.628 | 200.179 | 15.2378
38930.4334 | 1079 | 1022 | 38930.4334 | 957 | 866 | 1999.5 | 2120.5 | 65.873 | 62.3932 | 58.4249 | 52.8694 | 0.65873 | 0.62393 | 0.58425 | 0.52869 | 0.034799 | 0.055556 | 1144.6287 | 3065.6889 | 1.139
38930.4341 | 1001 | 912 | 38930.4341 | 1049 | 971 | 2058 | 2179 | 61.1111 | 55.6777 | 64.0415 | 59.2796 | 0.61111 | 0.55678 | 0.64042 | 0.5928 | 0.054335 | 0.047619 | 1263.3151 | 93439.076 | 21.9086
38930.4348 | 1035 | 1051 | 38930.4348 | 1045 | 968 | 2117 | 2238 | 63.1868 | 64.1636 | 63.7973 | 59.0965 | 0.63187 | 0.64164 | 0.63797 | 0.59096 | 0.009768 | 0.047009 | 209.8711 | 211.1891 | 1.7447

## C1-2
Penlight Test 27 |  |  | 2006-08-01 | 9:51 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38930.4089 | 1 | 0 | 38930.4089 | 1 | 0 | -120 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4096 | 1 | 0 | 38930.4096 | 1 | 0 | -61.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4103 | 1 | 0 |  | 1 | 0 | -3 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4109 | 1 | 0 | 38930.4109 | 1 | 0 | 56.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4116 | 1 | 0 | 38930.4116 | 1 | 0 | 115 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4123 | 1 | 0 | 38930.4123 | 1 | 0 | 174 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.413 | 1 | 0 | 38930.413 | 1 | 0 | 232.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4137 | 1 | 0 | 38930.4137 | 1 | 0 | 291.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4143 | 1 | 0 | 38930.4144 | 1 | 0 | 350.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.415 | 1 | 0 | 38930.415 | 1 | 0 | 409 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4157 | 1 | 0 | 38930.4157 | 1 | 0 | 468 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4164 | 1 | 0 | 38930.4164 | 1 | 0 | 526.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4171 | 1 | 0 | 38930.4171 | 1 | 0 | 585.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4177 | 1 | 0 | 38930.4178 | 1 | 0 | 644.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4184 | 1 | 0 | 38930.4184 | 1 | 0 | 703 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4191 | 1 | 0 | 38930.4191 | 1 | 0 | 761.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4198 | 1 | 0 | 38930.4198 | 1 | 0 | 820.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4205 | 1 | 0 | 38930.4205 | 1 | 0 | 879.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4211 | 1 | 0 | 38930.4212 | 1 | 0 | 938.5 | 1059.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4218 | 1 | 0 | 38930.4218 | 1 | 0 | 997 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4225 | 1 | 0 | 38930.4225 | 1 | 0 | 1055.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4232 | 1 | 0 | 38930.4232 | 1 | 0 | 1114.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4239 | 1 | 0 | 38930.4239 | 1 | 0 | 1173.5 | 1294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4245 | 1 | 0 | 38930.4246 | 1 | 0 | 1232 | 1353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4252 | 1 | 0 | 38930.4252 | 1 | 0 | 1291 | 1412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4259 | 1 | 0 | 38930.4259 | 1 | 0 | 1349.5 | 1470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.4266 | 986 | 950 | 38930.4266 | 1082 | 1053 | 1408.5 | 1529.5 | 60.1954 | 57.9976 | 66.0562 | 64.2857 | 0.60195 | 0.57998 | 0.66056 | 0.64286 | 0.021978 | 0.017705 | 1689.5045 | 3093.7436 | 18.0502
38930.4273 | 1110 | 1083 | 38930.4273 | 1101 | 1172 | 1467.5 | 1588.5 | 67.7656 | 66.1172 | 67.2161 | 71.5507 | 0.67766 | 0.66117 | 0.67216 | 0.71551 | 0.016484 | 0.043346 | 512.8255 | 642.3983 | 6.3903
38930.4279 | 1130 | 822 | 38930.428 | 927 | 893 | 1526 | 1647 | 68.9866 | 50.1832 | 56.5934 | 54.5177 | 0.68987 | 0.50183 | 0.56593 | 0.54518 | 0.18803 | 0.020757 | 128.0096 | 178.724 | 12.5608
38930.4286 | 1091 | 1017 | 38930.4286 | 1001 | 1101 | 1585 | 1706 | 66.6056 | 62.0879 | 61.1111 | 67.2161 | 0.66606 | 0.62088 | 0.61111 | 0.67216 | 0.045177 | 0.06105 | 86.4978 | 91.8238 | 0.23628
38930.4293 | 1001 | 989 | 38930.4293 | 1099 | 1026 | 1643.5 | 1764.5 | 61.1111 | 60.3785 | 67.094 | 62.6374 | 0.61111 | 0.60379 | 0.67094 | 0.62637 | 0.007326 | 0.044567 | 188.0707 | 170.7299 | 7.8443
38930.43 | 1195 | 1172 | 38930.43 | 924 | 867 | 1702.5 | 1823.5 | 72.9548 | 71.5507 | 56.4103 | 52.9304 | 0.72955 | 0.71551 | 0.5641 | 0.5293 | 0.014042 | 0.034799 | 191.1474 | 256.3047 | 15.5886
38930.4307 | 994 | 1093 | 38930.4307 | 1132 | 1181 | 1761.5 | 1882.5 | 60.6838 | 66.7277 | 69.1087 | 72.1001 | 0.60684 | 0.66728 | 0.69109 | 0.721 | 0.06044 | 0.029915 | 443.1459 | 711.972 | 2.0874
38930.4313 | 1140 | 1083 | 38930.4314 | 1187 | 1108 | 1820 | 1941 | 69.5971 | 66.1172 | 72.4664 | 67.6435 | 0.69597 | 0.66117 | 0.72466 | 0.67643 | 0.034799 | 0.04823 | 912.0928 | 2179.9546 | 9.7097
38930.432 | 926 | 1004 | 38930.432 | 1055 | 1138 | 1879 | 2000 | 56.5324 | 61.2943 | 64.4078 | 69.475 | 0.56532 | 0.61294 | 0.64408 | 0.69475 | 0.047619 | 0.050672 | 14054.226 | 1443.4828 | 17.048
38930.4327 | 1186 | 1186 | 38930.4327 | 1154 | 1105 | 1937.5 | 2058.5 | 72.4054 | 72.4054 | 70.4518 | 67.4603 | 0.72405 | 0.72405 | 0.70452 | 0.6746 | 0 | 0.029915 | 725.2973 | 927.9224 | 19.7121
38930.4334 | 1041 | 1059 | 38930.4334 | 925 | 903 | 1996.5 | 2117.5 | 63.5531 | 64.652 | 56.4713 | 55.1282 | 0.63553 | 0.64652 | 0.56471 | 0.55128 | 0.010989 | 0.013431 | 16581.1856 | 9180.9767 | 1.2162
38930.4341 | 931 | 847 | 38930.4341 | 1062 | 986 | 2055.5 | 2176.5 | 56.8376 | 51.7094 | 64.8352 | 60.1954 | 0.56838 | 0.51709 | 0.64835 | 0.60195 | 0.051282 | 0.046398 | 1702.7269 | 5809.0234 | 38.8843
38930.4347 | 1178 | 841 | 38930.4348 | 1003 | 914 | 2114 | 2235 | 71.917 | 51.3431 | 61.2332 | 55.7998 | 0.71917 | 0.51343 | 0.61233 | 0.558 | 0.20574 | 0.054335 | 89.9706 | 119.7578 | 6.0923

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 27 |  |  | 2006-08-01 | 9:51
38930.4089 | 1 | 0 | 1 | XLPE | 7-C | Air Drop
38930.4096 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38930.4103 | 1 | 0 | 1
38930.4109 | 1 | 0 | 1
38930.4116 | 1 | 0 | 1
38930.4123 | 1 | 0 | 1
38930.413 | 1 | 0 | 1
38930.4137 | 1 | 0 | 1
38930.4143 | 1 | 0 | 1
38930.415 | 1 | 0 | 1
38930.4157 | 1 | 0 | 1
38930.4164 | 1 | 0 | 1
38930.4171 | 1 | 0 | 1
38930.4177 | 1 | 0 | 1
38930.4184 | 1 | 0 | 1
38930.4191 | 1 | 0 | 1
38930.4198 | 1 | 0 | 1
38930.4205 | 1 | 0 | 1
38930.4211 | 1 | 0 | 1
38930.4218 | 1 | 0 | 1
38930.4225 | 1 | 0 | 1
38930.4232 | 1 | 0 | 1
38930.4239 | 1 | 0 | 1
38930.4245 | 1 | 0 | 1
38930.4252 | 1 | 0 | 1
38930.4259 | 1 | 0 | 1
38930.4266 | 986 | 950 | 1
38930.4273 | 1110 | 1083 | 1
38930.4279 | 1130 | 822 | 1
38930.4286 | 1091 | 1017 | 1
38930.4293 | 1001 | 989 | 1
38930.43 | 1195 | 1172 | 1
38930.4307 | 994 | 1093 | 1
38930.4313 | 1140 | 1083 | 1
38930.432 | 926 | 1004 | 1
38930.4327 | 1186 | 1186 | 1
38930.4334 | 1041 | 1059 | 1
38930.4341 | 931 | 847 | 1
38930.4347 | 1178 | 841 | 1
1
38930.4089 | 1 | 0 | 2
38930.4096 | 1 | 0 | 2
38930.4109 | 1 | 0 | 2
38930.4116 | 1 | 0 | 2
38930.4123 | 1 | 0 | 2
38930.413 | 1 | 0 | 2
38930.4137 | 1 | 0 | 2
38930.4144 | 1 | 0 | 2
38930.415 | 1 | 0 | 2
38930.4157 | 1 | 0 | 2
38930.4164 | 1 | 0 | 2
38930.4171 | 1 | 0 | 2
38930.4178 | 1 | 0 | 2
38930.4184 | 1 | 0 | 2
38930.4191 | 1 | 0 | 2
38930.4198 | 1 | 0 | 2
38930.4205 | 1 | 0 | 2
38930.4212 | 1 | 0 | 2
38930.4218 | 1 | 0 | 2
38930.4225 | 1 | 0 | 2
38930.4232 | 1 | 0 | 2
38930.4239 | 1 | 0 | 2
38930.4246 | 1 | 0 | 2
38930.4252 | 1 | 0 | 2
38930.4259 | 1 | 0 | 2
38930.4266 | 1082 | 1053 | 2
38930.4273 | 1101 | 1172 | 2
38930.428 | 927 | 893 | 2
38930.4286 | 1001 | 1101 | 2
38930.4293 | 1099 | 1026 | 2
38930.43 | 924 | 867 | 2
38930.4307 | 1132 | 1181 | 2
38930.4314 | 1187 | 1108 | 2
38930.432 | 1055 | 1138 | 2
38930.4327 | 1154 | 1105 | 2
38930.4334 | 925 | 903 | 2
38930.4341 | 1062 | 986 | 2
38930.4348 | 1003 | 914 | 2
2
38930.4089 | 1 | 0 | 3
38930.4096 | 1 | 0 | 3
38930.4103 | 1 | 0 | 3
38930.411 | 1 | 0 | 3
38930.4116 | 1 | 0 | 3
38930.4123 | 1 | 0 | 3
38930.413 | 1 | 0 | 3
38930.4137 | 1 | 0 | 3
38930.4144 | 1 | 0 | 3
38930.415 | 1 | 0 | 3
38930.4157 | 1 | 0 | 3
38930.4164 | 1 | 0 | 3
38930.4171 | 1 | 0 | 3
38930.4178 | 1 | 1 | 3
38930.4184 | 1 | 0 | 3
38930.4191 | 1 | 0 | 3
38930.4198 | 1 | 0 | 3
38930.4205 | 1 | 0 | 3
38930.4212 | 1 | 0 | 3
38930.4219 | 1 | 0 | 3
38930.4225 | 1 | 0 | 3
38930.4232 | 1 | 0 | 3
38930.4239 | 1 | 0 | 3
38930.4246 | 1 | 0 | 3
38930.4253 | 1 | 0 | 3
38930.4259 | 1 | 0 | 3
38930.4266 | 956 | 988 | 3
38930.4273 | 1102 | 1160 | 3
38930.428 | 1138 | 1082 | 3
38930.4287 | 1123 | 1060 | 3
38930.4293 | 1026 | 936 | 3
38930.43 | 1182 | 1143 | 3
38930.4307 | 1036 | 944 | 3
38930.4314 | 1124 | 1165 | 3
38930.4321 | 972 | 877 | 3
38930.4327 | 1000 | 906 | 3
38930.4334 | 1079 | 1022 | 3
38930.4341 | 1001 | 912 | 3
38930.4348 | 1035 | 1051 | 3
3
38930.4089 | 1 | 0 | 4
38930.4096 | 1 | 0 | 4
38930.4103 | 1 | 0 | 4
38930.411 | 1 | 0 | 4
38930.4117 | 1 | 0 | 4
38930.4123 | 1 | 0 | 4
38930.413 | 1 | 0 | 4
38930.4137 | 1 | 0 | 4
38930.4144 | 1 | 0 | 4
38930.4151 | 1 | 0 | 4
38930.4157 | 1 | 0 | 4
38930.4164 | 1 | 0 | 4
38930.4171 | 1 | 0 | 4
38930.4178 | 1 | 0 | 4
38930.4185 | 1 | 0 | 4
38930.4191 | 1 | 0 | 4
38930.4198 | 1 | 0 | 4
38930.4205 | 1 | 0 | 4
38930.4212 | 1 | 0 | 4
38930.4219 | 1 | 0 | 4
38930.4225 | 1 | 0 | 4
38930.4232 | 1 | 0 | 4
38930.4239 | 1 | 0 | 4
38930.4246 | 1 | 0 | 4
38930.4253 | 1 | 0 | 4
38930.4259 | 1 | 0 | 4
38930.4266 | 945 | 921 | 4
38930.4273 | 989 | 956 | 4
38930.428 | 1182 | 1151 | 4
38930.4287 | 1068 | 986 | 4
38930.4294 | 1086 | 1015 | 4
38930.43 | 927 | 876 | 4
38930.4307 | 1135 | 1078 | 4
38930.4314 | 953 | 1056 | 4
38930.4321 | 1051 | 975 | 4
38930.4328 | 1083 | 1117 | 4
38930.4334 | 957 | 866 | 4
38930.4341 | 1049 | 971 | 4
38930.4348 | 1045 | 968 | 4
4
38930.409 | 1 | 0 | 5
38930.4096 | 1 | 0 | 5
38930.4103 | 1 | 0 | 5
38930.411 | 1 | 0 | 5
38930.4117 | 1 | 0 | 5
38930.4124 | 1 | 0 | 5
38930.413 | 1 | 0 | 5
38930.4137 | 1 | 0 | 5
38930.4144 | 1 | 0 | 5
38930.4151 | 1 | 0 | 5
38930.4158 | 1 | 0 | 5
38930.4164 | 1 | 0 | 5
38930.4171 | 1 | 0 | 5
38930.4178 | 1 | 0 | 5
38930.4185 | 1 | 0 | 5
38930.4192 | 1 | 0 | 5
38930.4198 | 1 | 0 | 5
38930.4205 | 1 | 0 | 5
38930.4212 | 1 | 0 | 5
38930.4219 | 1 | 0 | 5
38930.4226 | 1 | 0 | 5
38930.4232 | 1 | 0 | 5
38930.4239 | 1 | 0 | 5
38930.4246 | 1 | 0 | 5
38930.4253 | 1 | 0 | 5
38930.426 | 960 | 924 | 5
38930.4266 | 100 | 106 | 5
38930.4273 | 923 | 1034 | 5
38930.428 | 1102 | 1032 | 5
38930.4287 | 1146 | 1091 | 5
38930.4294 | 978 | 877 | 5
38930.43 | 962 | 848 | 5
38930.4307 | 997 | 889 | 5
38930.4314 | 973 | 953 | 5
38930.4321 | 982 | 887 | 5
38930.4328 | 1041 | 1057 | 5
38930.4334 | 1066 | 996 | 5
38930.4341 | 1108 | 1149 | 5
38930.4348 | 1121 | 1065 | 5
5
38930.409 | 1 | 0 | 6
38930.4097 | 1 | 0 | 6
38930.4103 | 1 | 0 | 6
38930.411 | 1 | 0 | 6
38930.4117 | 1 | 0 | 6
38930.4124 | 1 | 0 | 6
38930.4131 | 1 | 0 | 6
38930.4137 | 1 | 0 | 6
38930.4144 | 1 | 0 | 6
38930.4151 | 1 | 0 | 6
38930.4158 | 1 | 0 | 6
38930.4165 | 1 | 0 | 6
38930.4171 | 1 | 0 | 6
38930.4178 | 1 | 0 | 6
38930.4185 | 1 | 0 | 6
38930.4192 | 1 | 0 | 6
38930.4199 | 1 | 0 | 6
38930.4205 | 1 | 0 | 6
38930.4212 | 1 | 0 | 6
38930.4219 | 1 | 0 | 6
38930.4226 | 1 | 0 | 6
38930.4233 | 2 | 0 | 6
38930.4239 | 1 | 0 | 6
38930.4246 | 1 | 0 | 6
38930.4253 | 1 | 0 | 6
38930.426 | 926 | 950 | 6
38930.4267 | 215 | 145 | 6
38930.4273 | 945 | 980 | 6
38930.428 | 1155 | 1109 | 6
38930.4287 | 1038 | 947 | 6
38930.4294 | 1131 | 1082 | 6
38930.4301 | 1080 | 1001 | 6
38930.4308 | 1125 | 1060 | 6
38930.4314 | 1036 | 950 | 6
38930.4321 | 1040 | 957 | 6
38930.4328 | 929 | 895 | 6
38930.4335 | 1148 | 1101 | 6
38930.4342 | 1076 | 1006 | 6
38930.4348 | 975 | 1079 | 6
6
38930.409 | 1 | 0 | 7
38930.4097 | 1 | 0 | 7
38930.4103 | 1 | 0 | 7
38930.411 | 1 | 0 | 7
38930.4117 | 1 | 0 | 7
38930.4124 | 1 | 0 | 7
38930.4131 | 1 | 0 | 7
38930.4137 | 1 | 0 | 7
38930.4144 | 1 | 0 | 7
38930.4151 | 1 | 0 | 7
38930.4158 | 1 | 0 | 7
38930.4165 | 1 | 0 | 7
38930.4172 | 1 | 0 | 7
38930.4178 | 1 | 0 | 7
38930.4185 | 1 | 0 | 7
38930.4192 | 1 | 0 | 7
38930.4199 | 1 | 0 | 7
38930.4206 | 1 | 0 | 7
38930.4212 | 1 | 0 | 7
38930.4219 | 1 | 0 | 7
38930.4226 | 1 | 0 | 7
38930.4233 | 1 | 0 | 7
38930.424 | 1 | 0 | 7
38930.4246 | 1 | 0 | 7
38930.4253 | 1 | 0 | 7
38930.426 | 1053 | 1021 | 7
38930.4267 | 969 | 931 | 7
38930.4274 | 1075 | 1049 | 7
38930.428 | 1183 | 1160 | 7
38930.4287 | 922 | 980 | 7
38930.4294 | 1011 | 914 | 7
38930.4301 | 1076 | 999 | 7
38930.4308 | 1183 | 1179 | 7
38930.4314 | 970 | 864 | 7
38930.4321 | 928 | 849 | 7
38930.4328 | 1190 | 907 | 7
38930.4335 | 1061 | 990 | 7
38930.4342 | 1013 | 860 | 7
38930.4348 | 990 | 989 | 7
7
38930.409 | 1 | 0 | 8
38930.4097 | 1 | 0 | 8
38930.4104 | 1 | 0 | 8
38930.411 | 1 | 0 | 8
38930.4117 | 1 | 0 | 8
38930.4124 | 1 | 0 | 8
38930.4131 | 1 | 0 | 8
38930.4138 | 1 | 0 | 8
38930.4144 | 1 | 0 | 8
38930.4151 | 1 | 1 | 8
38930.4158 | 1 | 0 | 8
38930.4165 | 1 | 0 | 8
38930.4172 | 1 | 0 | 8
38930.4178 | 1 | 0 | 8
38930.4185 | 1 | 0 | 8
38930.4192 | 1 | 0 | 8
38930.4199 | 1 | 0 | 8
38930.4206 | 1 | 0 | 8
38930.4212 | 1 | 0 | 8
38930.4219 | 1 | 0 | 8
38930.4226 | 1 | 0 | 8
38930.4233 | 1 | 0 | 8
38930.424 | 1 | 0 | 8
38930.4247 | 1 | 0 | 8
38930.4253 | 1 | 0 | 8
38930.426 | 1049 | 1095 | 8
38930.4267 | 1077 | 1144 | 8
38930.4274 | 1165 | 1146 | 8
38930.4281 | 911 | 855 | 8
38930.4287 | 1061 | 977 | 8
38930.4294 | 1031 | 1120 | 8
38930.4301 | 951 | 1052 | 8
38930.4308 | 1150 | 1095 | 8
38930.4315 | 1155 | 1109 | 8
38930.4321 | 1042 | 963 | 8
38930.4328 | 1019 | 930 | 8
38930.4335 | 1143 | 1096 | 8
38930.4342 | 1002 | 915 | 8
38930.4349 | 1016 | 932 | 8
8
38930.409 | 1 | 0 | 9
38930.4097 | 1 | 0 | 9
38930.4104 | 1 | 0 | 9
38930.4111 | 1 | 0 | 9
38930.4117 | 1 | 0 | 9
38930.4124 | 1 | 0 | 9
38930.4131 | 1 | 0 | 9
38930.4138 | 1 | 0 | 9
38930.4145 | 1 | 0 | 9
38930.4152 | 1 | 0 | 9
38930.4165 | 1 | 0 | 9
38930.4172 | 1 | 0 | 9
38930.4179 | 1 | 0 | 9
38930.4186 | 1 | 0 | 9
38930.4192 | 1 | 0 | 9
38930.4199 | 1 | 0 | 9
38930.4206 | 1 | 0 | 9
38930.4213 | 1 | 0 | 9
38930.422 | 1 | 0 | 9
38930.4226 | 1 | 0 | 9
38930.4233 | 1 | 0 | 9
38930.424 | 1 | 0 | 9
38930.4247 | 1 | 0 | 9
38930.4253 | 1 | 0 | 9
38930.426 | 27 | 32 | 9
38930.4267 | 967 | 930 | 9
38930.4274 | 1198 | 1003 | 9
38930.4281 | 1094 | 1017 | 9
38930.4287 | 1143 | 1084 | 9
38930.4294 | 1018 | 921 | 9
38930.4301 | 988 | 879 | 9
38930.4308 | 1087 | 1160 | 9
38930.4315 | 984 | 880 | 9
38930.4322 | 1128 | 1179 | 9
38930.4328 | 1017 | 1025 | 9
38930.4335 | 970 | 1076 | 9
38930.4342 | 1110 | 1048 | 9
38930.4349 | 980 | 888 | 9
9
38930.409 | 1 | 0 | 10
38930.4097 | 1 | 0 | 10
38930.4104 | 1 | 0 | 10
38930.4111 | 1 | 0 | 10
38930.4118 | 1 | 0 | 10
38930.4124 | 1 | 0 | 10
38930.4131 | 1 | 0 | 10
38930.4138 | 1 | 0 | 10
38930.4145 | 1 | 0 | 10
38930.4152 | 1 | 0 | 10
38930.4158 | 1 | 0 | 10
38930.4165 | 1 | 0 | 10
38930.4172 | 1 | 0 | 10
38930.4179 | 1 | 0 | 10
38930.4186 | 1 | 0 | 10
38930.4192 | 1 | 0 | 10
38930.4199 | 1 | 0 | 10
38930.4206 | 1 | 0 | 10
38930.4213 | 1 | 0 | 10
38930.422 | 1 | 0 | 10
38930.4227 | 1 | 0 | 10
38930.4233 | 1 | 0 | 10
38930.424 | 1 | 0 | 10
38930.4247 | 1 | 0 | 10
38930.4254 | 1 | 0 | 10
38930.4261 | 872 | 836 | 10
38930.4267 | 1041 | 1087 | 10
38930.4274 | 992 | 958 | 10
38930.4281 | 976 | 851 | 10
38930.4288 | 998 | 892 | 10
38930.4295 | 1092 | 1020 | 10
38930.4301 | 958 | 844 | 10
38930.4308 | 953 | 837 | 10
38930.4315 | 980 | 878 | 10
38930.4322 | 974 | 877 | 10
38930.4329 | 1128 | 1072 | 10
38930.4335 | 949 | 925 | 10
38930.4342 | 1156 | 1109 | 10
38930.4349 | 1082 | 1017 | 10
10
38930.4091 | 1 | 0 | 11
38930.4097 | 1 | 0 | 11
38930.4104 | 1 | 0 | 11
38930.4111 | 1 | 0 | 11
38930.4118 | 1 | 0 | 11
38930.4125 | 1 | 0 | 11
38930.4131 | 1 | 0 | 11
38930.4138 | 1 | 0 | 11
38930.4145 | 1 | 0 | 11
38930.4152 | 1 | 0 | 11
38930.4159 | 1 | 0 | 11
38930.4165 | 1 | 0 | 11
38930.4172 | 1 | 0 | 11
38930.4179 | 1 | 0 | 11
38930.4186 | 1 | 0 | 11
38930.4193 | 1 | 0 | 11
38930.4199 | 1 | 0 | 11
38930.4206 | 1 | 0 | 11
38930.4213 | 1 | 0 | 11
38930.422 | 1 | 0 | 11
38930.4227 | 1 | 0 | 11
38930.4233 | 1 | 0 | 11
38930.424 | 1 | 0 | 11
38930.4247 | 1 | 0 | 11
38930.4254 | 1 | 0 | 11
38930.4261 | 3 | 9 | 11
38930.4267 | 1080 | 1052 | 11
38930.4274 | 1186 | 1168 | 11
38930.4281 | 1065 | 977 | 11
38930.4288 | 968 | 857 | 11
38930.4295 | 959 | 848 | 11
38930.4302 | 1024 | 929 | 11
38930.4308 | 1012 | 913 | 11
38930.4315 | 1163 | 1183 | 11
38930.4322 | 1135 | 1082 | 11
38930.4329 | 1194 | 1180 | 11
38930.4336 | 1078 | 1008 | 11
38930.4342 | 927 | 862 | 11
38930.4349 | 1131 | 1078 | 11
11
38930.4091 | 1 | 0 | 12
38930.4097 | 1 | 0 | 12
38930.4104 | 1 | 0 | 12
38930.4111 | 1 | 0 | 12
38930.4118 | 1 | 0 | 12
38930.4125 | 1 | 0 | 12
38930.4131 | 1 | 0 | 12
38930.4138 | 1 | 0 | 12
38930.4145 | 1 | 0 | 12
38930.4152 | 1 | 0 | 12
38930.4159 | 1 | 0 | 12
38930.4166 | 1 | 0 | 12
38930.4172 | 1 | 0 | 12
38930.4179 | 1 | 0 | 12
38930.4186 | 1 | 0 | 12
38930.4193 | 1 | 0 | 12
38930.42 | 1 | 0 | 12
38930.4206 | 1 | 0 | 12
38930.4213 | 1 | 0 | 12
38930.422 | 1 | 0 | 12
38930.4227 | 1 | 0 | 12
38930.4234 | 1 | 0 | 12
38930.424 | 1 | 0 | 12
38930.4247 | 1 | 0 | 12
38930.4254 | 1 | 0 | 12
38930.4261 | 84 | 79 | 12
38930.4268 | 1051 | 1021 | 12
38930.4274 | 1142 | 1117 | 12
38930.4281 | 937 | 822 | 12
38930.4288 | 1198 | 1177 | 12
38930.4295 | 994 | 979 | 12
38930.4302 | 974 | 948 | 12
38930.4308 | 935 | 826 | 12
38930.4315 | 959 | 848 | 12
38930.4322 | 1166 | 1189 | 12
38930.4329 | 1094 | 1131 | 12
38930.4336 | 1077 | 1155 | 12
38930.4342 | 1191 | 1181 | 12
38930.4349 | 1085 | 1157 | 12
12
38930.4091 | 1 | 0 | 13
38930.4098 | 1 | 0 | 13
38930.4105 | 1 | 0 | 13
38930.4111 | 1 | 0 | 13
38930.4118 | 1 | 0 | 13
38930.4125 | 1 | 0 | 13
38930.4132 | 1 | 0 | 13
38930.4139 | 1 | 0 | 13
38930.4145 | 1 | 0 | 13
38930.4152 | 1 | 0 | 13
38930.4159 | 1 | 0 | 13
38930.4166 | 1 | 0 | 13
38930.4173 | 1 | 0 | 13
38930.4179 | 1 | 0 | 13
38930.4186 | 1 | 0 | 13
38930.4193 | 1 | 0 | 13
38930.42 | 1 | 0 | 13
38930.4207 | 1 | 0 | 13
38930.4213 | 1 | 0 | 13
38930.422 | 1 | 0 | 13
38930.4227 | 1 | 0 | 13
38930.4234 | 1 | 0 | 13
38930.4241 | 1 | 0 | 13
38930.4247 | 1 | 0 | 13
38930.4254 | 1 | 0 | 13
38930.4261 | 313 | 328 | 13
38930.4268 | 927 | 891 | 13
38930.4275 | 1047 | 1133 | 13
38930.4281 | 1174 | 1103 | 13
38930.4288 | 934 | 1026 | 13
38930.4295 | 1112 | 1151 | 13
38930.4302 | 1001 | 897 | 13
38930.4309 | 1179 | 1142 | 13
38930.4315 | 1070 | 995 | 13
38930.4322 | 983 | 1083 | 13
38930.4329 | 1156 | 829 | 13
38930.4336 | 1169 | 840 | 13
38930.4343 | 990 | 1090 | 13
38930.4349 | 999 | 997 | 13
13
38930.4091 | 1 | 0 | 14
38930.4098 | 1 | 0 | 14
38930.4105 | 1 | 0 | 14
38930.4111 | 1 | 0 | 14
38930.4118 | 1 | 0 | 14
38930.4125 | 1 | 0 | 14
38930.4132 | 1 | 0 | 14
38930.4139 | 1 | 0 | 14
38930.4145 | 1 | 1 | 14
38930.4152 | 1 | 0 | 14
38930.4159 | 1 | 0 | 14
38930.4166 | 1 | 0 | 14
38930.4173 | 1 | 0 | 14
38930.418 | 1 | 0 | 14
38930.4186 | 1 | 0 | 14
38930.4193 | 1 | 0 | 14
38930.42 | 1 | 0 | 14
38930.4207 | 1 | 0 | 14
38930.4214 | 1 | 0 | 14
38930.422 | 1 | 0 | 14
38930.4227 | 1 | 0 | 14
38930.4234 | 1 | 0 | 14
38930.4241 | 1 | 0 | 14
38930.4248 | 1 | 0 | 14
38930.4254 | 1 | 0 | 14
38930.4261 | 1021 | 987 | 14
38930.4268 | 1038 | 1008 | 14
38930.4275 | 1091 | 1066 | 14
38930.4282 | 1117 | 1158 | 14
38930.4288 | 1194 | 1166 | 14
38930.4295 | 1012 | 919 | 14
38930.4302 | 955 | 1056 | 14
38930.4309 | 946 | 909 | 14
38930.4316 | 1115 | 1064 | 14
38930.4322 | 1005 | 914 | 14
38930.4329 | 1004 | 1002 | 14
38930.4336 | 1006 | 918 | 14
38930.4343 | 1191 | 1172 | 14
38930.435 | 960 | 865 | 14
14
38930.4091 | 1 | 0 | 15
38930.4098 | 1 | 0 | 15
38930.4105 | 1 | 0 | 15
38930.4112 | 1 | 0 | 15
38930.4118 | 1 | 0 | 15
38930.4125 | 1 | 0 | 15
38930.4132 | 1 | 0 | 15
38930.4139 | 1 | 0 | 15
38930.4146 | 1 | 0 | 15
38930.4152 | 1 | 0 | 15
38930.4159 | 1 | 0 | 15
38930.4166 | 1 | 0 | 15
38930.4173 | 1 | 0 | 15
38930.418 | 1 | 0 | 15
38930.4186 | 1 | 0 | 15
38930.4193 | 1 | 0 | 15
38930.42 | 1 | 0 | 15
38930.4207 | 1 | 0 | 15
38930.4214 | 1 | 0 | 15
38930.422 | 1 | 0 | 15
38930.4227 | 1 | 0 | 15
38930.4234 | 1 | 0 | 15
38930.4241 | 1 | 0 | 15
38930.4248 | 1 | 0 | 15
38930.4255 | 1 | 0 | 15
38930.4261 | 997 | 960 | 15
38930.4268 | 453 | 448 | 15
38930.4275 | 1144 | 1123 | 15
38930.4282 | 1177 | 1166 | 15
38930.4289 | 983 | 1082 | 15
38930.4295 | 1110 | 1052 | 15
38930.4302 | 1183 | 1144 | 15
38930.4309 | 1170 | 1126 | 15
38930.4316 | 1193 | 1182 | 15
38930.4323 | 1189 | 1073 | 15
38930.4329 | 935 | 834 | 15
38930.4336 | 1111 | 846 | 15
38930.4343 | 1133 | 1081 | 15
38930.435 | 1026 | 1118 | 15
15
38930.4091 | 1 | 0 | 16
38930.4098 | 1 | 0 | 16
38930.4105 | 1 | 0 | 16
38930.4112 | 1 | 0 | 16
38930.4119 | 1 | 0 | 16
38930.4125 | 1 | 0 | 16
38930.4132 | 1 | 0 | 16
38930.4139 | 1 | 0 | 16
38930.4146 | 1 | 0 | 16
38930.4153 | 1 | 0 | 16
38930.4159 | 1 | 0 | 16
38930.4166 | 1 | 0 | 16
38930.4173 | 2 | 0 | 16
38930.418 | 1 | 0 | 16
38930.4187 | 1 | 0 | 16
38930.4193 | 1 | 0 | 16
38930.42 | 1 | 0 | 16
38930.4207 | 1 | 0 | 16
38930.4214 | 1 | 0 | 16
38930.4221 | 1 | 0 | 16
38930.4227 | 1 | 0 | 16
38930.4234 | 1 | 0 | 16
38930.4241 | 1 | 0 | 16
38930.4248 | 1 | 0 | 16
38930.4255 | 1 | 0 | 16
38930.4261 | 988 | 952 | 16
38930.4268 | 1160 | 1139 | 16
38930.4275 | 1157 | 1180 | 16
38930.4282 | 1135 | 1080 | 16
38930.4289 | 1175 | 826 | 16
38930.4295 | 1087 | 1018 | 16
38930.4302 | 958 | 842 | 16
38930.4309 | 917 | 865 | 16
38930.4316 | 946 | 852 | 16
38930.4323 | 917 | 941 | 16
38930.433 | 1084 | 1016 | 16
38930.4336 | 988 | 981 | 16
38930.4343 | 1184 | 1181 | 16
38930.435 | 922 | 890 | 16
16
38930.4092 | 1 | 0 | 17
38930.4098 | 1 | 0 | 17
38930.4105 | 1 | 0 | 17
38930.4112 | 1 | 0 | 17
38930.4119 | 1 | 0 | 17
38930.4126 | 1 | 0 | 17
38930.4132 | 1 | 0 | 17
38930.4139 | 1 | 0 | 17
38930.4146 | 1 | 0 | 17
38930.4153 | 1 | 0 | 17
38930.416 | 1 | 0 | 17
38930.4166 | 1 | 0 | 17
38930.4173 | 1 | 0 | 17
38930.418 | 1 | 0 | 17
38930.4187 | 1 | 0 | 17
38930.4194 | 1 | 0 | 17
38930.42 | 1 | 0 | 17
38930.4207 | 1 | 0 | 17
38930.4214 | 1 | 0 | 17
38930.4221 | 2 | 0 | 17
38930.4228 | 1 | 1 | 17
38930.4234 | 1 | 0 | 17
38930.4241 | 1 | 0 | 17
38930.4248 | 1 | 0 | 17
38930.4255 | 1 | 0 | 17
38930.4262 | 694 | 726 | 17
38930.4268 | 1077 | 1049 | 17
38930.4275 | 930 | 961 | 17
38930.4282 | 1182 | 1155 | 17
38930.4289 | 923 | 989 | 17
38930.4296 | 1164 | 1121 | 17
38930.4302 | 971 | 861 | 17
38930.4309 | 1026 | 932 | 17
38930.4316 | 1145 | 1106 | 17
38930.4323 | 1045 | 965 | 17
38930.433 | 1106 | 1055 | 17
38930.4336 | 919 | 884 | 17
38930.4343 | 929 | 872 | 17
38930.435 | 931 | 838 | 17
17
38930.4092 | 1 | 0 | 18
38930.4098 | 1 | 0 | 18
38930.4105 | 1 | 0 | 18
38930.4112 | 1 | 0 | 18
38930.4119 | 1 | 0 | 18
38930.4126 | 1 | 0 | 18
38930.4133 | 1 | 0 | 18
38930.4139 | 1 | 0 | 18
38930.4146 | 1 | 0 | 18
38930.4153 | 1 | 0 | 18
38930.416 | 1 | 0 | 18
38930.4167 | 1 | 0 | 18
38930.4173 | 1 | 0 | 18
38930.418 | 1 | 0 | 18
38930.4187 | 1 | 0 | 18
38930.4194 | 1 | 0 | 18
38930.4201 | 1 | 0 | 18
38930.4207 | 1 | 0 | 18
38930.4214 | 1 | 0 | 18
38930.4221 | 1 | 0 | 18
38930.4228 | 1 | 0 | 18
38930.4235 | 1 | 0 | 18
38930.4241 | 2 | 0 | 18
38930.4248 | 1 | 0 | 18
38930.4255 | 1 | 0 | 18
38930.4262 | 1036 | 1007 | 18
38930.4269 | 1070 | 1125 | 18
38930.4275 | 916 | 929 | 18
38930.4282 | 943 | 828 | 18
38930.4289 | 1137 | 1181 | 18
38930.4296 | 926 | 1011 | 18
38930.4303 | 946 | 858 | 18
38930.4309 | 1027 | 931 | 18
38930.4316 | 1146 | 1108 | 18
38930.4323 | 1153 | 1107 | 18
38930.433 | 1115 | 1171 | 18
38930.4337 | 940 | 908 | 18
38930.4343 | 1031 | 1048 | 18
38930.435 | 962 | 867 | 18
18
38930.4092 | 1 | 0 | 19
38930.4099 | 1 | 0 | 19
38930.4105 | 1 | 0 | 19
38930.4112 | 1 | 0 | 19
38930.4119 | 1 | 0 | 19
38930.4126 | 1 | 0 | 19
38930.4133 | 1 | 0 | 19
38930.4139 | 1 | 0 | 19
38930.4146 | 1 | 0 | 19
38930.4153 | 1 | 0 | 19
38930.416 | 1 | 0 | 19
38930.4167 | 1 | 0 | 19
38930.4173 | 1 | 0 | 19
38930.418 | 1 | 0 | 19
38930.4187 | 1 | 0 | 19
38930.4194 | 1 | 0 | 19
38930.4201 | 1 | 0 | 19
38930.4208 | 1 | 0 | 19
38930.4214 | 1 | 0 | 19
38930.4221 | 1 | 0 | 19
38930.4228 | 1 | 0 | 19
38930.4235 | 1 | 0 | 19
38930.4242 | 1 | 0 | 19
38930.4248 | 1 | 0 | 19
38930.4255 | 1 | 0 | 19
38930.4262 | 1089 | 1064 | 19
38930.4269 | 1191 | 1195 | 19
38930.4276 | 1150 | 1195 | 19
38930.4282 | 926 | 874 | 19
38930.4289 | 1120 | 1160 | 19
38930.4296 | 1166 | 1119 | 19
38930.4303 | 1187 | 1187 | 19
38930.431 | 983 | 872 | 19
38930.4316 | 1012 | 1016 | 19
38930.4323 | 1054 | 975 | 19
38930.433 | 934 | 912 | 19
38930.4337 | 1051 | 971 | 19
38930.4344 | 1112 | 1057 | 19
38930.435 | 923 | 955 | 19
19
38930.4092 | 1 | 0 | 20
38930.4099 | 1 | 0 | 20
38930.4106 | 1 | 0 | 20
38930.4112 | 1 | 0 | 20
38930.4119 | 1 | 0 | 20
38930.4126 | 1 | 0 | 20
38930.4133 | 1 | 0 | 20
38930.414 | 1 | 0 | 20
38930.4146 | 1 | 0 | 20
38930.4153 | 1 | 0 | 20
38930.416 | 2 | 0 | 20
38930.4167 | 1 | 0 | 20
38930.4174 | 1 | 0 | 20
38930.418 | 1 | 0 | 20
38930.4187 | 1 | 1 | 20
38930.4194 | 1 | 0 | 20
38930.4201 | 1 | 0 | 20
38930.4208 | 1 | 0 | 20
38930.4214 | 1 | 0 | 20
38930.4221 | 1 | 0 | 20
38930.4228 | 1 | 0 | 20
38930.4235 | 1 | 0 | 20
38930.4242 | 1 | 0 | 20
38930.4248 | 1 | 0 | 20
38930.4255 | 1 | 0 | 20
38930.4262 | 923 | 1034 | 20
38930.4269 | 1148 | 1124 | 20
38930.4276 | 951 | 919 | 20
38930.4283 | 979 | 867 | 20
38930.4289 | 1195 | 1177 | 20
38930.4296 | 1111 | 835 | 20
38930.4303 | 1177 | 1148 | 20
38930.431 | 1091 | 1016 | 20
38930.4317 | 995 | 871 | 20
38930.4323 | 1005 | 911 | 20
38930.433 | 1014 | 1111 | 20
38930.4337 | 1158 | 1113 | 20
38930.4344 | 1163 | 1182 | 20
38930.4351 | 1168 | 1189 | 20
20
38930.4092 | 1 | 0 | 21
38930.4099 | 1 | 0 | 21
38930.4106 | 1 | 1 | 21
38930.4113 | 1 | 0 | 21
38930.4119 | 1 | 0 | 21
38930.4126 | 1 | 0 | 21
38930.4133 | 1 | 0 | 21
38930.414 | 1 | 0 | 21
38930.4147 | 1 | 0 | 21
38930.4153 | 1 | 0 | 21
38930.416 | 1 | 0 | 21
38930.4167 | 1 | 0 | 21
38930.4174 | 1 | 0 | 21
38930.4181 | 1 | 0 | 21
38930.4187 | 1 | 0 | 21
38930.4194 | 1 | 0 | 21
38930.4201 | 1 | 0 | 21
38930.4208 | 1 | 0 | 21
38930.4215 | 1 | 0 | 21
38930.4221 | 1 | 0 | 21
38930.4228 | 1 | 0 | 21
38930.4235 | 1 | 0 | 21
38930.4242 | 1 | 0 | 21
38930.4249 | 1 | 0 | 21
38930.4255 | 1 | 0 | 21
38930.4262 | 73 | 76 | 21
38930.4269 | 1180 | 1159 | 21
38930.4276 | 1151 | 1128 | 21
38930.4283 | 924 | 872 | 21
38930.4289 | 1106 | 1143 | 21
38930.4296 | 974 | 862 | 21
38930.4303 | 1050 | 964 | 21
38930.431 | 1145 | 1184 | 21
38930.4317 | 1039 | 964 | 21
38930.4323 | 1016 | 1014 | 21
38930.433 | 927 | 915 | 21
38930.4337 | 978 | 881 | 21
38930.4344 | 1101 | 1041 | 21
38930.4351 | 953 | 852 | 21
21
38930.4092 | 1 | 0 | 22
38930.4099 | 1 | 0 | 22
38930.4106 | 1 | 0 | 22
38930.4113 | 1 | 0 | 22
38930.412 | 1 | 0 | 22
38930.4126 | 1 | 0 | 22
38930.4133 | 1 | 0 | 22
38930.414 | 1 | 0 | 22
38930.4147 | 1 | 0 | 22
38930.4154 | 2 | 0 | 22
38930.416 | 1 | 0 | 22
38930.4167 | 1 | 0 | 22
38930.4174 | 1 | 0 | 22
38930.4181 | 1 | 1 | 22
38930.4188 | 1 | 0 | 22
38930.4194 | 1 | 0 | 22
38930.4201 | 1 | 0 | 22
38930.4208 | 1 | 0 | 22
38930.4215 | 2 | 0 | 22
38930.4222 | 1 | 0 | 22
38930.4228 | 1 | 0 | 22
38930.4235 | 1 | 0 | 22
38930.4242 | 1 | 0 | 22
38930.4249 | 1 | 0 | 22
38930.4256 | 1 | 0 | 22
38930.4262 | 998 | 966 | 22
38930.4269 | 968 | 935 | 22
38930.4276 | 1109 | 1082 | 22
38930.4283 | 994 | 883 | 22
38930.429 | 1178 | 830 | 22
38930.4296 | 1104 | 1034 | 22
38930.4303 | 962 | 1066 | 22
38930.431 | 921 | 868 | 22
38930.4317 | 1058 | 986 | 22
38930.4324 | 1168 | 1124 | 22
38930.433 | 1037 | 966 | 22
38930.4337 | 934 | 833 | 22
38930.4344 | 961 | 866 | 22
38930.4351 | 936 | 838 | 22
22
38930.4092 | 1 | 0 | 23
38930.4099 | 1 | 0 | 23
38930.4106 | 1 | 0 | 23
38930.4113 | 1 | 0 | 23
38930.412 | 1 | 0 | 23
38930.4127 | 1 | 0 | 23
38930.4133 | 1 | 0 | 23
38930.414 | 1 | 0 | 23
38930.4147 | 1 | 0 | 23
38930.4154 | 1 | 0 | 23
38930.4161 | 1 | 0 | 23
38930.4167 | 1 | 0 | 23
38930.4174 | 1 | 0 | 23
38930.4181 | 1 | 0 | 23
38930.4188 | 1 | 0 | 23
38930.4195 | 1 | 0 | 23
38930.4201 | 1 | 0 | 23
38930.4208 | 1 | 0 | 23
38930.4215 | 1 | 0 | 23
38930.4222 | 1 | 0 | 23
38930.4229 | 1 | 0 | 23
38930.4235 | 1 | 0 | 23
38930.4242 | 1 | 0 | 23
38930.4249 | 1 | 0 | 23
38930.4256 | 1 | 0 | 23
38930.4263 | 9 | 21 | 23
38930.4269 | 327 | 321 | 23
38930.4276 | 1114 | 1156 | 23
38930.4283 | 914 | 865 | 23
38930.429 | 939 | 824 | 23
38930.4297 | 998 | 907 | 23
38930.4303 | 963 | 854 | 23
38930.431 | 1106 | 1144 | 23
38930.4317 | 1159 | 1168 | 23
38930.4324 | 1034 | 949 | 23
38930.4331 | 995 | 924 | 23
38930.4337 | 1058 | 1139 | 23
38930.4344 | 937 | 873 | 23
38930.4351 | 1077 | 1152 | 23
23
38930.4093 | 1 | 0 | 24
38930.4099 | 1 | 0 | 24
38930.4106 | 1 | 0 | 24
38930.4113 | 1 | 0 | 24
38930.412 | 1 | 0 | 24
38930.4127 | 1 | 0 | 24
38930.4133 | 1 | 1 | 24
38930.414 | 1 | 0 | 24
38930.4147 | 1 | 0 | 24
38930.4154 | 1 | 0 | 24
38930.4161 | 1 | 0 | 24
38930.4167 | 1 | 0 | 24
38930.4174 | 1 | 0 | 24
38930.4181 | 1 | 0 | 24
38930.4188 | 1 | 0 | 24
38930.4195 | 1 | 0 | 24
38930.4202 | 1 | 0 | 24
38930.4208 | 1 | 0 | 24
38930.4215 | 1 | 0 | 24
38930.4222 | 1 | 0 | 24
38930.4229 | 1 | 0 | 24
38930.4236 | 1 | 0 | 24
38930.4242 | 1 | 0 | 24
38930.4249 | 2 | 0 | 24
38930.4256 | 1 | 0 | 24
38930.4263 | 4 | 15 | 24
38930.427 | 223 | 222 | 24
38930.4276 | 1150 | 1131 | 24
38930.4283 | 1009 | 913 | 24
38930.429 | 1150 | 810 | 24
38930.4297 | 982 | 972 | 24
38930.4304 | 986 | 1086 | 24
38930.431 | 917 | 971 | 24
38930.4317 | 1147 | 1102 | 24
38930.4324 | 948 | 839 | 24
38930.4331 | 1090 | 1029 | 24
38930.4338 | 953 | 1053 | 24
38930.4344 | 1160 | 1119 | 24
38930.4351 | 938 | 913 | 24
24
38930.4093 | 1 | 0 | 25
38930.41 | 1 | 0 | 25
38930.4106 | 1 | 0 | 25
38930.4113 | 1 | 0 | 25
38930.412 | 1 | 0 | 25
38930.4127 | 1 | 0 | 25
38930.4134 | 1 | 0 | 25
38930.414 | 1 | 0 | 25
38930.4147 | 1 | 0 | 25
38930.4154 | 1 | 0 | 25
38930.4161 | 1 | 0 | 25
38930.4168 | 1 | 0 | 25
38930.4174 | 1 | 0 | 25
38930.4181 | 1 | 0 | 25
38930.4188 | 1 | 1 | 25
38930.4195 | 1 | 0 | 25
38930.4202 | 1 | 0 | 25
38930.4208 | 1 | 0 | 25
38930.4215 | 1 | 0 | 25
38930.4222 | 1 | 0 | 25
38930.4229 | 1 | 0 | 25
38930.4236 | 1 | 0 | 25
38930.4242 | 1 | 0 | 25
38930.4249 | 1 | 0 | 25
38930.4256 | 1 | 0 | 25
38930.4263 | 241 | 273 | 25
38930.427 | 908 | 873 | 25
38930.4277 | 1042 | 1016 | 25
38930.4283 | 909 | 851 | 25
38930.429 | 1002 | 846 | 25
38930.4297 | 1126 | 1169 | 25
38930.4304 | 930 | 818 | 25
38930.4311 | 964 | 855 | 25
38930.4317 | 1125 | 1168 | 25
38930.4324 | 927 | 1017 | 25
38930.4331 | 991 | 907 | 25
38930.4338 | 932 | 1029 | 25
38930.4345 | 1169 | 836 | 25
38930.4351 | 945 | 846 | 25
25
38930.4093 | 1 | 0 | 26
38930.41 | 1 | 0 | 26
38930.4107 | 1 | 0 | 26
38930.4113 | 1 | 0 | 26
38930.412 | 1 | 0 | 26
38930.4127 | 1 | 0 | 26
38930.4134 | 1 | 0 | 26
38930.4141 | 1 | 0 | 26
38930.4147 | 1 | 0 | 26
38930.4154 | 1 | 0 | 26
38930.4161 | 1 | 0 | 26
38930.4168 | 1 | 0 | 26
38930.4175 | 1 | 0 | 26
38930.4181 | 1 | 0 | 26
38930.4188 | 1 | 0 | 26
38930.4195 | 1 | 0 | 26
38930.4202 | 1 | 0 | 26
38930.4209 | 1 | 0 | 26
38930.4216 | 1 | 0 | 26
38930.4222 | 1 | 0 | 26
38930.4229 | 1 | 0 | 26
38930.4236 | 1 | 0 | 26
38930.4243 | 1 | 0 | 26
38930.4249 | 1 | 0 | 26
38930.4256 | 1 | 0 | 26
38930.4263 | 926 | 957 | 26
38930.427 | 1045 | 1017 | 26
38930.4277 | 941 | 910 | 26
38930.4283 | 947 | 914 | 26
38930.429 | 1155 | 1109 | 26
38930.4297 | 946 | 831 | 26
38930.4304 | 990 | 976 | 26
38930.4311 | 1183 | 1161 | 26
38930.4317 | 1145 | 1106 | 26
38930.4324 | 927 | 1016 | 26
38930.4331 | 948 | 853 | 26
38930.4338 | 1134 | 1084 | 26
38930.4345 | 992 | 991 | 26
38930.4352 | 1016 | 858 | 26
26
38930.4093 | 1 | 0 | 27
38930.41 | 1 | 0 | 27
38930.4107 | 1 | 0 | 27
38930.4114 | 1 | 0 | 27
38930.412 | 1 | 0 | 27
38930.4127 | 1 | 0 | 27
38930.4134 | 1 | 0 | 27
38930.4141 | 1 | 0 | 27
38930.4148 | 1 | 0 | 27
38930.4154 | 1 | 0 | 27
38930.4161 | 1 | 0 | 27
38930.4168 | 1 | 0 | 27
38930.4175 | 1 | 0 | 27
38930.4182 | 1 | 0 | 27
38930.4188 | 1 | 0 | 27
38930.4195 | 1 | 0 | 27
38930.4209 | 1 | 0 | 27
38930.4216 | 1 | 0 | 27
38930.4222 | 1 | 0 | 27
38930.4229 | 1 | 0 | 27
38930.4236 | 1 | 0 | 27
38930.4243 | 1 | 0 | 27
38930.425 | 1 | 0 | 27
38930.4256 | 1 | 0 | 27
38930.4263 | 1118 | 1096 | 27
38930.427 | 979 | 946 | 27
38930.4277 | 1026 | 997 | 27
38930.4284 | 1021 | 1020 | 27
38930.4291 | 918 | 987 | 27
38930.4297 | 980 | 961 | 27
38930.4304 | 974 | 863 | 27
38930.4311 | 971 | 866 | 27
38930.4318 | 1014 | 863 | 27
38930.4325 | 1191 | 1172 | 27
38930.4331 | 1168 | 1129 | 27
38930.4338 | 1081 | 1013 | 27
38930.4345 | 1133 | 839 | 27
38930.4352 | 991 | 900 | 27
27
38930.4093 | 1 | 0 | 28
38930.41 | 1 | 0 | 28
38930.4107 | 1 | 0 | 28
38930.4114 | 1 | 0 | 28
38930.412 | 1 | 0 | 28
38930.4127 | 1 | 0 | 28
38930.4134 | 1 | 0 | 28
38930.4141 | 1 | 0 | 28
38930.4148 | 1 | 0 | 28
38930.4155 | 1 | 0 | 28
38930.4161 | 1 | 0 | 28
38930.4168 | 1 | 0 | 28
38930.4175 | 1 | 0 | 28
38930.4182 | 1 | 0 | 28
38930.4189 | 1 | 1 | 28
38930.4195 | 1 | 0 | 28
38930.4202 | 1 | 0 | 28
38930.4209 | 1 | 0 | 28
38930.4216 | 1 | 0 | 28
38930.4223 | 1 | 0 | 28
38930.4229 | 1 | 0 | 28
38930.4236 | 1 | 0 | 28
38930.4243 | 1 | 0 | 28
38930.425 | 1 | 0 | 28
38930.4257 | 1 | 0 | 28
38930.4263 | 1003 | 970 | 28
38930.427 | 1071 | 1044 | 28
38930.4277 | 1159 | 1181 | 28
38930.4284 | 1164 | 1148 | 28
38930.4291 | 1110 | 1043 | 28
38930.4297 | 1018 | 924 | 28
38930.4304 | 1169 | 1124 | 28
38930.4318 | 1162 | 1122 | 28
38930.4325 | 966 | 863 | 28
38930.4331 | 1106 | 1168 | 28
38930.4338 | 998 | 908 | 28
38930.4345 | 1022 | 941 | 28
38930.4352 | 949 | 851 | 28
28
38930.4093 | 1 | 0 | 29
38930.41 | 1 | 0 | 29
38930.4107 | 1 | 0 | 29
38930.4114 | 1 | 0 | 29
38930.4121 | 1 | 0 | 29
38930.4127 | 1 | 0 | 29
38930.4134 | 1 | 0 | 29
38930.4141 | 1 | 0 | 29
38930.4148 | 1 | 0 | 29
38930.4155 | 1 | 0 | 29
38930.4161 | 1 | 0 | 29
38930.4168 | 1 | 0 | 29
38930.4175 | 1 | 0 | 29
38930.4182 | 1 | 0 | 29
38930.4189 | 1 | 0 | 29
38930.4195 | 1 | 0 | 29
38930.4202 | 1 | 0 | 29
38930.4209 | 1 | 0 | 29
38930.4216 | 1 | 0 | 29
38930.4223 | 1 | 0 | 29
38930.423 | 1 | 0 | 29
38930.4236 | 1 | 0 | 29
38930.4243 | 1 | 0 | 29
38930.425 | 1 | 0 | 29
38930.4257 | 1 | 0 | 29
38930.4264 | 1062 | 1116 | 29
38930.427 | 1063 | 1035 | 29
38930.4277 | 951 | 1067 | 29
38930.4284 | 955 | 846 | 29
38930.4291 | 1016 | 916 | 29
38930.4298 | 957 | 841 | 29
38930.4304 | 1189 | 1159 | 29
38930.4311 | 931 | 818 | 29
38930.4318 | 967 | 874 | 29
38930.4325 | 974 | 957 | 29
38930.4332 | 1181 | 1149 | 29
38930.4338 | 992 | 902 | 29
38930.4345 | 943 | 843 | 29
38930.4352 | 946 | 847 | 29
29
38930.4094 | 1 | 0 | 30
38930.41 | 1 | 0 | 30
38930.4107 | 1 | 0 | 30
38930.4114 | 1 | 0 | 30
38930.4121 | 1 | 0 | 30
38930.4128 | 1 | 0 | 30
38930.4134 | 1 | 0 | 30
38930.4141 | 1 | 0 | 30
38930.4148 | 1 | 0 | 30
38930.4155 | 1 | 0 | 30
38930.4162 | 1 | 0 | 30
38930.4169 | 1 | 0 | 30
38930.4175 | 1 | 0 | 30
38930.4182 | 1 | 0 | 30
38930.4189 | 1 | 0 | 30
38930.4196 | 1 | 0 | 30
38930.4203 | 1 | 0 | 30
38930.4209 | 1 | 0 | 30
38930.4216 | 2 | 0 | 30
38930.4223 | 1 | 0 | 30
38930.423 | 1 | 0 | 30
38930.4236 | 1 | 0 | 30
38930.4243 | 1 | 0 | 30
38930.425 | 1 | 0 | 30
38930.4257 | 1 | 0 | 30
38930.4264 | 1122 | 1102 | 30
38930.427 | 943 | 1057 | 30
38930.4277 | 1139 | 1113 | 30
38930.4284 | 969 | 861 | 30
38930.4291 | 1095 | 1025 | 30
38930.4298 | 1185 | 954 | 30
38930.4305 | 960 | 847 | 30
38930.4311 | 1012 | 920 | 30
38930.4318 | 1157 | 1181 | 30
38930.4325 | 1046 | 963 | 30
38930.4332 | 1035 | 1124 | 30
38930.4339 | 1125 | 1169 | 30
38930.4345 | 1040 | 1126 | 30
38930.4352 | 1127 | 840 | 30
30
38930.4094 | 1 | 0 | 31
38930.4101 | 1 | 0 | 31
38930.4107 | 1 | 0 | 31
38930.4114 | 1 | 0 | 31
38930.4121 | 1 | 0 | 31
38930.4128 | 1 | 0 | 31
38930.4135 | 1 | 0 | 31
38930.4141 | 1 | 0 | 31
38930.4148 | 1 | 0 | 31
38930.4155 | 1 | 0 | 31
38930.4162 | 1 | 0 | 31
38930.4169 | 1 | 0 | 31
38930.4175 | 1 | 0 | 31
38930.4182 | 1 | 0 | 31
38930.4189 | 1 | 0 | 31
38930.4196 | 1 | 0 | 31
38930.4203 | 1 | 0 | 31
38930.4209 | 1 | 0 | 31
38930.4216 | 1 | 0 | 31
38930.4223 | 1 | 1 | 31
38930.423 | 1 | 0 | 31
38930.4237 | 1 | 0 | 31
38930.4244 | 1 | 0 | 31
38930.425 | 1 | 0 | 31
38930.4257 | 1 | 0 | 31
38930.4264 | 11 | 26 | 31
38930.4271 | 209 | 211 | 31
38930.4278 | 1054 | 1129 | 31
38930.4284 | 940 | 821 | 31
38930.4291 | 1005 | 908 | 31
38930.4298 | 924 | 806 | 31
38930.4305 | 1015 | 919 | 31
38930.4312 | 974 | 869 | 31
38930.4318 | 1073 | 1012 | 31
38930.4325 | 1115 | 1170 | 31
38930.4332 | 1087 | 1023 | 31
38930.4339 | 997 | 910 | 31
38930.4346 | 1007 | 1009 | 31
38930.4352 | 1191 | 983 | 31
31
38930.4094 | 1 | 0 | 32
38930.4101 | 1 | 0 | 32
38930.4108 | 1 | 0 | 32
38930.4114 | 1 | 0 | 32
38930.4121 | 1 | 0 | 32
38930.4128 | 1 | 0 | 32
38930.4135 | 1 | 0 | 32
38930.4142 | 1 | 0 | 32
38930.4148 | 1 | 0 | 32
38930.4155 | 1 | 0 | 32
38930.4162 | 1 | 0 | 32
38930.4169 | 1 | 0 | 32
38930.4176 | 1 | 0 | 32
38930.4182 | 1 | 0 | 32
38930.4189 | 1 | 0 | 32
38930.4196 | 1 | 0 | 32
38930.4203 | 1 | 0 | 32
38930.421 | 1 | 0 | 32
38930.4216 | 1 | 0 | 32
38930.4223 | 1 | 0 | 32
38930.423 | 1 | 0 | 32
38930.4237 | 1 | 0 | 32
38930.4244 | 1 | 0 | 32
38930.425 | 1 | 0 | 32
38930.4257 | 1 | 0 | 32
38930.4264 | 5 | 20 | 32
38930.4271 | 20 | 41 | 32
38930.4278 | 1073 | 896 | 32
38930.4284 | 1016 | 917 | 32
38930.4291 | 1052 | 1074 | 32
38930.4298 | 1148 | 1102 | 32
38930.4305 | 1001 | 897 | 32
38930.4312 | 1077 | 1150 | 32
38930.4319 | 1185 | 1158 | 32
38930.4325 | 1121 | 1163 | 32
38930.4332 | 956 | 1060 | 32
38930.4339 | 924 | 865 | 32
38930.4346 | 1061 | 987 | 32
38930.4353 | 980 | 889 | 32
32
38930.4094 | 1 | 0 | 33
38930.4101 | 1 | 0 | 33
38930.4108 | 1 | 0 | 33
38930.4114 | 1 | 0 | 33
38930.4121 | 1 | 0 | 33
38930.4128 | 1 | 0 | 33
38930.4135 | 1 | 0 | 33
38930.4142 | 1 | 0 | 33
38930.4148 | 1 | 0 | 33
38930.4155 | 1 | 0 | 33
38930.4162 | 1 | 0 | 33
38930.4169 | 1 | 0 | 33
38930.4176 | 1 | 0 | 33
38930.4183 | 1 | 0 | 33
38930.4189 | 1 | 0 | 33
38930.4196 | 1 | 0 | 33
38930.4203 | 1 | 0 | 33
38930.421 | 1 | 0 | 33
38930.4217 | 1 | 0 | 33
38930.4223 | 1 | 0 | 33
38930.423 | 1 | 0 | 33
38930.4237 | 1 | 0 | 33
38930.4244 | 1 | 0 | 33
38930.4251 | 1 | 0 | 33
38930.4257 | 1 | 0 | 33
38930.4264 | 156 | 157 | 33
38930.4271 | 37 | 48 | 33
38930.4278 | 991 | 960 | 33
38930.4285 | 1158 | 1108 | 33
38930.4291 | 1026 | 1110 | 33
38930.4298 | 974 | 954 | 33
38930.4305 | 1179 | 1138 | 33
38930.4312 | 931 | 888 | 33
38930.4319 | 972 | 884 | 33
38930.4325 | 1073 | 1004 | 33
38930.4332 | 959 | 862 | 33
38930.4339 | 1170 | 1130 | 33
38930.4346 | 1058 | 1080 | 33
38930.4353 | 1050 | 973 | 33
33
38930.4094 | 1 | 0 | 34
38930.4101 | 1 | 0 | 34
38930.4108 | 1 | 0 | 34
38930.4115 | 0 | 0 | 34
38930.4122 | 1 | 0 | 34
38930.4128 | 1 | 0 | 34
38930.4135 | 1 | 1 | 34
38930.4142 | 1 | 0 | 34
38930.4149 | 1 | 0 | 34
38930.4156 | 1 | 0 | 34
38930.4162 | 1 | 0 | 34
38930.4169 | 1 | 0 | 34
38930.4176 | 1 | 0 | 34
38930.4183 | 1 | 0 | 34
38930.4189 | 1 | 0 | 34
38930.4196 | 1 | 0 | 34
38930.4203 | 1 | 0 | 34
38930.421 | 1 | 0 | 34
38930.4217 | 1 | 0 | 34
38930.4223 | 1 | 0 | 34
38930.423 | 1 | 0 | 34
38930.4237 | 1 | 0 | 34
38930.4244 | 1 | 0 | 34
38930.4251 | 1 | 0 | 34
38930.4258 | 1 | 0 | 34
38930.4264 | 281 | 280 | 34
38930.4271 | 375 | 370 | 34
38930.4278 | 908 | 937 | 34
38930.4285 | 1026 | 932 | 34
38930.4292 | 1077 | 1006 | 34
38930.4298 | 1139 | 1086 | 34
38930.4305 | 987 | 880 | 34
38930.4312 | 1097 | 1027 | 34
38930.4319 | 1123 | 1070 | 34
38930.4326 | 1086 | 1019 | 34
38930.4332 | 1180 | 1136 | 34
38930.4339 | 1122 | 1177 | 34
38930.4346 | 1149 | 1184 | 34
38930.4353 | 1060 | 989 | 34
34
38930.4094 | 1 | 0 | 35
38930.4101 | 1 | 0 | 35
38930.4108 | 1 | 0 | 35
38930.4115 | 1 | 0 | 35
38930.4122 | 1 | 0 | 35
38930.4128 | 1 | 0 | 35
38930.4135 | 1 | 0 | 35
38930.4142 | 1 | 0 | 35
38930.4149 | 1 | 0 | 35
38930.4156 | 1 | 0 | 35
38930.4163 | 1 | 0 | 35
38930.4169 | 1 | 0 | 35
38930.4176 | 1 | 0 | 35
38930.4183 | 1 | 0 | 35
38930.419 | 1 | 0 | 35
38930.4197 | 1 | 0 | 35
38930.4203 | 1 | 0 | 35
38930.421 | 1 | 0 | 35
38930.4217 | 2 | 0 | 35
38930.4224 | 1 | 0 | 35
38930.4231 | 1 | 0 | 35
38930.4237 | 1 | 0 | 35
38930.4244 | 1 | 0 | 35
38930.4251 | 1 | 0 | 35
38930.4258 | 1 | 0 | 35
38930.4265 | 162 | 209 | 35
38930.4271 | 203 | 194 | 35
38930.4278 | 945 | 913 | 35
38930.4285 | 954 | 921 | 35
38930.4292 | 1092 | 1150 | 35
38930.4299 | 1122 | 1171 | 35
38930.4305 | 1138 | 1179 | 35
38930.4312 | 1061 | 1080 | 35
38930.4319 | 1060 | 996 | 35
38930.4326 | 1028 | 1037 | 35
38930.4333 | 1097 | 1139 | 35
38930.4339 | 1190 | 1161 | 35
38930.4346 | 965 | 872 | 35
38930.4353 | 1019 | 1025 | 35
35
38930.4095 | 1 | 0 | 36
38930.4101 | 1 | 0 | 36
38930.4108 | 1 | 0 | 36
38930.4115 | 1 | 0 | 36
38930.4122 | 1 | 0 | 36
38930.4129 | 1 | 0 | 36
38930.4135 | 1 | 0 | 36
38930.4142 | 1 | 0 | 36
38930.4149 | 1 | 0 | 36
38930.4156 | 1 | 0 | 36
38930.4163 | 1 | 0 | 36
38930.4169 | 1 | 0 | 36
38930.4176 | 1 | 0 | 36
38930.4183 | 1 | 0 | 36
38930.419 | 1 | 0 | 36
38930.4197 | 1 | 0 | 36
38930.4203 | 1 | 0 | 36
38930.421 | 1 | 0 | 36
38930.4217 | 1 | 0 | 36
38930.4224 | 1 | 0 | 36
38930.4231 | 1 | 0 | 36
38930.4238 | 1 | 0 | 36
38930.4244 | 1 | 0 | 36
38930.4251 | 1 | 0 | 36
38930.4258 | 1 | 0 | 36
38930.4265 | 16 | 26 | 36
38930.4272 | 173 | 178 | 36
38930.4278 | 913 | 913 | 36
38930.4285 | 929 | 864 | 36
38930.4292 | 1004 | 1094 | 36
38930.4299 | 1054 | 971 | 36
38930.4306 | 1164 | 1117 | 36
38930.4312 | 1106 | 1039 | 36
38930.4319 | 946 | 850 | 36
38930.4326 | 984 | 888 | 36
38930.4333 | 924 | 896 | 36
38930.434 | 1048 | 970 | 36
38930.4346 | 1180 | 1147 | 36
38930.4353 | 1075 | 1006 | 36
36
38930.4095 | 1 | 0 | 37
38930.4102 | 1 | 0 | 37
38930.4108 | 1 | 0 | 37
38930.4115 | 1 | 0 | 37
38930.4122 | 1 | 0 | 37
38930.4129 | 1 | 0 | 37
38930.4136 | 1 | 0 | 37
38930.4142 | 1 | 0 | 37
38930.4149 | 1 | 0 | 37
38930.4156 | 1 | 0 | 37
38930.4163 | 1 | 0 | 37
38930.417 | 1 | 0 | 37
38930.4176 | 1 | 0 | 37
38930.4183 | 1 | 0 | 37
38930.419 | 1 | 0 | 37
38930.4197 | 1 | 0 | 37
38930.4204 | 1 | 0 | 37
38930.421 | 1 | 0 | 37
38930.4217 | 1 | 0 | 37
38930.4224 | 1 | 0 | 37
38930.4231 | 1 | 0 | 37
38930.4238 | 1 | 0 | 37
38930.4244 | 1 | 0 | 37
38930.4251 | 1 | 0 | 37
38930.4258 | 1 | 0 | 37
38930.4265 | 971 | 936 | 37
38930.4272 | 976 | 1082 | 37
38930.4278 | 1110 | 1085 | 37
38930.4285 | 952 | 836 | 37
38930.4292 | 1031 | 936 | 37
38930.4299 | 1152 | 1100 | 37
38930.4306 | 1049 | 960 | 37
38930.4313 | 1089 | 1122 | 37
38930.4319 | 965 | 877 | 37
38930.4326 | 992 | 984 | 37
38930.4333 | 1176 | 1144 | 37
38930.434 | 1157 | 1112 | 37
38930.4347 | 1165 | 1125 | 37
38930.4353 | 1178 | 1143 | 37
37
38930.4095 | 1 | 0 | 38
38930.4102 | 1 | 0 | 38
38930.4109 | 1 | 0 | 38
38930.4115 | 1 | 0 | 38
38930.4122 | 1 | 0 | 38
38930.4129 | 1 | 0 | 38
38930.4136 | 1 | 0 | 38
38930.4143 | 1 | 0 | 38
38930.4149 | 1 | 0 | 38
38930.4156 | 1 | 0 | 38
38930.4163 | 1 | 0 | 38
38930.417 | 1 | 0 | 38
38930.4177 | 1 | 0 | 38
38930.4183 | 1 | 0 | 38
38930.419 | 1 | 0 | 38
38930.4197 | 1 | 0 | 38
38930.4204 | 1 | 0 | 38
38930.4211 | 1 | 0 | 38
38930.4217 | 1 | 0 | 38
38930.4224 | 1 | 0 | 38
38930.4231 | 1 | 0 | 38
38930.4238 | 1 | 0 | 38
38930.4245 | 1 | 0 | 38
38930.4251 | 1 | 0 | 38
38930.4258 | 1 | 0 | 38
38930.4265 | 917 | 881 | 38
38930.4272 | 982 | 946 | 38
38930.4279 | 1163 | 1143 | 38
38930.4285 | 1172 | 1188 | 38
38930.4292 | 949 | 833 | 38
38930.4299 | 1105 | 1169 | 38
38930.4306 | 1010 | 914 | 38
38930.4313 | 1063 | 985 | 38
38930.4319 | 1127 | 1072 | 38
38930.4326 | 1133 | 1085 | 38
38930.4333 | 1124 | 1076 | 38
38930.434 | 984 | 973 | 38
38930.4347 | 1024 | 942 | 38
38930.4353 | 997 | 1096 | 38
38
38930.4095 | 1 | 0 | 39
38930.4102 | 1 | 0 | 39
38930.4109 | 1 | 0 | 39
38930.4116 | 1 | 0 | 39
38930.4122 | 1 | 0 | 39
38930.4129 | 1 | 0 | 39
38930.4136 | 2 | 0 | 39
38930.4143 | 1 | 0 | 39
38930.415 | 1 | 0 | 39
38930.4156 | 1 | 0 | 39
38930.4163 | 1 | 0 | 39
38930.417 | 1 | 0 | 39
38930.4177 | 1 | 0 | 39
38930.4184 | 2 | 0 | 39
38930.419 | 1 | 0 | 39
38930.4197 | 1 | 0 | 39
38930.4204 | 1 | 0 | 39
38930.4211 | 1 | 0 | 39
38930.4218 | 1 | 0 | 39
38930.4224 | 1 | 0 | 39
38930.4231 | 1 | 0 | 39
38930.4238 | 1 | 0 | 39
38930.4245 | 1 | 0 | 39
38930.4252 | 1 | 0 | 39
38930.4258 | 1 | 0 | 39
38930.4265 | 945 | 910 | 39
38930.4272 | 966 | 931 | 39
38930.4279 | 1132 | 1093 | 39
38930.4286 | 935 | 830 | 39
38930.4292 | 980 | 871 | 39
38930.4299 | 974 | 868 | 39
38930.4306 | 1002 | 1099 | 39
38930.4313 | 1171 | 1131 | 39
38930.432 | 1188 | 1162 | 39
38930.4326 | 997 | 1096 | 39
38930.4333 | 1180 | 1152 | 39
38930.434 | 984 | 889 | 39
38930.4347 | 1053 | 1077 | 39
38930.4354 | 1187 | 917 | 39
39
38930.4095 | 1 | 0 | 40
38930.4102 | 1 | 0 | 40
38930.4109 | 1 | 0 | 40
38930.4116 | 1 | 0 | 40
38930.4122 | 1 | 0 | 40
38930.4129 | 1 | 0 | 40
38930.4136 | 1 | 0 | 40
38930.4143 | 1 | 0 | 40
38930.415 | 1 | 0 | 40
38930.4156 | 1 | 0 | 40
38930.4163 | 1 | 0 | 40
38930.417 | 1 | 0 | 40
38930.4177 | 1 | 0 | 40
38930.4184 | 1 | 1 | 40
38930.4191 | 1 | 0 | 40
38930.4197 | 1 | 0 | 40
38930.4204 | 1 | 0 | 40
38930.4211 | 1 | 0 | 40
38930.4218 | 1 | 0 | 40
38930.4225 | 1 | 0 | 40
38930.4231 | 1 | 0 | 40
38930.4238 | 1 | 0 | 40
38930.4245 | 1 | 0 | 40
38930.4252 | 1 | 0 | 40
38930.4259 | 1 | 0 | 40
38930.4265 | 1065 | 1127 | 40
38930.4272 | 1049 | 1020 | 40
38930.4279 | 1172 | 1132 | 40
38930.4286 | 964 | 1065 | 40
38930.4293 | 1111 | 1045 | 40
38930.4299 | 1191 | 1161 | 40
38930.4306 | 1154 | 1104 | 40
38930.4313 | 1121 | 1172 | 40
38930.432 | 1137 | 1179 | 40
38930.4327 | 1038 | 859 | 40
38930.4333 | 1172 | 1138 | 40
38930.434 | 1055 | 978 | 40
38930.4347 | 1074 | 1150 | 40
38930.4354 | 964 | 869 | 40
40
38930.4095 | 1 | 0 | 41
38930.4102 | 1 | 0 | 41
38930.4109 | 1 | 0 | 41
38930.4116 | 1 | 0 | 41
38930.4123 | 1 | 0 | 41
38930.4129 | 1 | 0 | 41
38930.4136 | 1 | 0 | 41
38930.4143 | 1 | 0 | 41
38930.415 | 1 | 0 | 41
38930.4157 | 1 | 0 | 41
38930.4163 | 1 | 0 | 41
38930.417 | 1 | 0 | 41
38930.4177 | 1 | 0 | 41
38930.4184 | 1 | 0 | 41
38930.4191 | 1 | 0 | 41
38930.4197 | 1 | 0 | 41
38930.4204 | 1 | 0 | 41
38930.4211 | 1 | 0 | 41
38930.4218 | 1 | 0 | 41
38930.4225 | 1 | 0 | 41
38930.4231 | 1 | 0 | 41
38930.4238 | 1 | 0 | 41
38930.4245 | 1 | 0 | 41
38930.4252 | 1 | 0 | 41
38930.4259 | 1 | 0 | 41
38930.4266 | 1174 | 1175 | 41
38930.4272 | 1168 | 1187 | 41
38930.4279 | 1070 | 975 | 41
38930.4286 | 1196 | 1173 | 41
38930.4293 | 1171 | 1188 | 41
38930.43 | 930 | 1017 | 41
38930.4306 | 952 | 1053 | 41
38930.4313 | 983 | 879 | 41
38930.432 | 1155 | 1107 | 41
38930.4327 | 1156 | 1187 | 41
38930.4334 | 996 | 997 | 41
38930.434 | 948 | 845 | 41
38930.4347 | 1075 | 853 | 41
38930.4354 | 1048 | 974 | 41
41
38930.4096 | 1 | 0 | 42
38930.4102 | 1 | 0 | 42
38930.4109 | 1 | 0 | 42
38930.4116 | 1 | 0 | 42
38930.4123 | 1 | 0 | 42
38930.413 | 1 | 0 | 42
38930.4136 | 1 | 0 | 42
38930.4143 | 1 | 0 | 42
38930.415 | 1 | 0 | 42
38930.4157 | 1 | 0 | 42
38930.4164 | 1 | 0 | 42
38930.417 | 1 | 0 | 42
38930.4177 | 1 | 0 | 42
38930.4184 | 1 | 0 | 42
38930.4191 | 1 | 0 | 42
38930.4198 | 1 | 0 | 42
38930.4204 | 1 | 0 | 42
38930.4211 | 1 | 0 | 42
38930.4218 | 1 | 0 | 42
38930.4225 | 1 | 0 | 42
38930.4232 | 1 | 0 | 42
38930.4238 | 1 | 0 | 42
38930.4245 | 1 | 0 | 42
38930.4252 | 1 | 0 | 42
38930.4259 | 1 | 0 | 42
38930.4266 | 1039 | 1008 | 42
38930.4272 | 1058 | 1027 | 42
38930.4279 | 976 | 936 | 42
38930.4286 | 1043 | 954 | 42
38930.4293 | 1082 | 1006 | 42
38930.43 | 1082 | 1108 | 42
38930.4306 | 1091 | 837 | 42
38930.4313 | 1108 | 1042 | 42
38930.432 | 1141 | 839 | 42
38930.4327 | 966 | 860 | 42
38930.4334 | 976 | 887 | 42
38930.4341 | 1092 | 1025 | 42
38930.4347 | 1149 | 1185 | 42
38930.4354 | 1034 | 955 | 42
42