## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Test 31
Test conditions: Cable: 7-conductor, 14 AWG, Fire resistant silicone insulated, Rockbestos VitaLink (VL) control cable (Cable Item #11). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 700C, nominal 50.8 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and one cable temperature (see thermocouple map). One thermocouple was attached to the inside of the center tray rung. Shroud power: Initiated after 75 seconds of baseline data monitoring. Special Note: Based on the results of a preliminary test of this cable, it was expected that conduct of Test 31 would not lead to cable failure under normal conditions. Hence, as a part of this test, it was decided to assess the potential that disturbing the cable during the exposure might induce failure. The cable tray was struck with a hammer several times after the flames had extinguished. The cable was subsequently physically shaken using a pair of insulated pliers.
DAQ Time | Penlight Time | Event | Interpretation
75 | 0 | Initated Penlight Heating
~283 | ~208 | Cables ignite and burn | No electrical failures detected
340 | 265 | Power to Penlight is shutoff
~1455 | ~1380 | Flames extinguished; struck cable tray 3 times with hammer | No electrical failures detected
~1575 | ~1500 | Struck cable tray 3 more times with hammer | No electrical failures detected
~1695 | ~1620 | Physically shook test cable by hand with insulated pliers | Conductor 6 shorts to ground at less than 100 ohms
Additional Observations
Observation 1 | Electrical failure was detected during this test only after the application of physical shock and rough handling. Even so, only one conductor shorted to ground and no conductor-to-conductor shorting was evident.
Observation 2 | It took 208 s (3.5 min.) from the start of Penlight heating for the cables to ignite and burn.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | "Cable" | Within cable just below cable jacket, center position

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 31 |  |  | 2006-07-27 | 13:16
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-74 | 211201.9994 | -71 | 211201.9994 | -68.5 | 211201.9994 | -65.5 | 211201.9994 | -63 | 252037.9994 | -60 | 211201.9994 | -57 | 211201.9994 | -54.5 | 211201.9994 | -51.5 | 211201.9994 | -48.5 | 232237.9994 | -46 | 211201.9994 | -43 | 211201.9994 | -40.5 | 211201.9994 | -37.5 | 252438.0791 | -35 | 211201.9994 | -32 | 211201.9994 | -29 | 252737.9994 | -26.5 | 211201.9994 | -23.5 | 252637.9994 | -21 | 211201.9994 | -18 | 241537.9994 | -74 | 211201.9994
-15.5 | 211201.9994 | -12.5 | 211201.9994 | -9.5 | 105550.9988 | -7 | 211201.9994 | -4 | 252037.9994 | -1.5 | 211201.9994 | 1.5 | 211201.9994 | 4.5 | 211201.9994 | 7.5 | 211201.9994 | 10 | 232237.9994 | 13 | 211201.9994 | 15.5 | 211201.9994 | 18.5 | 211201.9994 | 21.5 | 252637.9994 | 24 | 211201.9994 | 27 | 211201.9994 | 29.5 | 252737.9994 | 32.5 | 211201.9994 | 35.5 | 252637.9994 | 38 | 211201.9994 | 41 | 241537.9994 | -15.5 | 105550.9988
43.5 | 211201.9994 | 46.5 | 211201.9994 | 49.5 | 211201.9994 | 52 | 211201.9994 | 55 | 252037.9994 | 57.5 | 211201.9994 | 60.5 | 211201.9994 | 63.5 | 210902.1893 | 66 | 211201.9994 | 69 | 232237.9994 | 71.5 | 211201.9994 | 74.5 | 211201.9994 | 77.5 | 211201.9994 | 80 | 252438.0791 | 83 | 211201.9994 | 85.5 | 211201.9994 | 88.5 | 252737.9994 | 91 | 211201.9994 | 94 | 252637.9994 | 98 | 211201.9994 | 99.5 | 241537.9994 | 43.5 | 210902.1893
102.5 | 211201.9994 | 105.5 | 211201.9994 | 108 | 211201.9994 | 111 | 211201.9994 | 113.5 | 251838.0793 | 116.5 | 211201.9994 | 119 | 211201.9994 | 122 | 211201.9994 | 124.5 | 211201.9994 | 127.5 | 232237.9994 | 130.5 | 211201.9994 | 133.5 | 211201.9994 | 136 | 211201.9994 | 138.5 | 252637.9994 | 141.5 | 211002.0947 | 144.5 | 211002.0947 | 147 | 252737.9994 | 150 | 211201.9994 | 152.5 | 252637.9994 | 155.5 | 211201.9994 | 158.5 | 241537.9994 | 102.5 | 211002.0947
161 | 211201.9994 | 164 | 211201.9994 | 167 | 211201.9994 | 169.5 | 211201.9994 | 172.5 | 252037.9994 | 175.5 | 211201.9994 | 178 | 211201.9994 | 181 | 211201.9994 | 183.5 | 211201.9994 | 186.5 | 232237.9994 | 189.5 | 211201.9994 | 192 | 211201.9994 | 194.5 | 211201.9994 | 197.5 | 252637.9994 | 200.5 | 211201.9994 | 203 | 211201.9994 | 206 | 252737.9994 | 208.5 | 211201.9994 | 211.5 | 252637.9994 | 214.5 | 211201.9994 | 217 | 241537.9994 | 161 | 211201.9994
220 | 211201.9994 | 222.5 | 211201.9994 | 225.5 | 211201.9994 | 228.5 | 211201.9994 | 231 | 252037.9994 | 234 | 211201.9994 | 237 | 211201.9994 | 239.5 | 211002.0947 | 242.5 | 211201.9994 | 245.5 | 232237.9994 | 248 | 211201.9994 | 251 | 211201.9994 | 253.5 | 211201.9994 | 256.5 | 252637.9994 | 259 | 105550.9988 | 262 | 211201.9994 | 264.5 | 252737.9994 | 267.5 | 211201.9994 | 270.5 | 126268.9988 | 273 | 211201.9994 | 276 | 241537.9994 | 220 | 105550.9988
279 | 211201.9994 | 281.5 | 211201.9994 | 284.5 | 211201.9994 | 287 | 211201.9994 | 290 | 252037.9994 | 293 | 211002.0947 | 295.5 | 211201.9994 | 298.5 | 211002.0947 | 301 | 105451.071 | 304 | 232237.9994 | 306.5 | 211201.9994 | 309.5 | 211201.9994 | 312.5 | 211201.9994 | 315 | 252637.9994 | 318 | 211201.9994 | 320.5 | 211201.9994 | 323.5 | 252538.0791 | 326.5 | 211201.9994 | 329 | 252637.9994 | 332 | 211201.9994 | 334.5 | 241537.9994 | 279 | 105451.071
337.5 | 211201.9994 | 340.5 | 211201.9994 | 343 | 105550.9988 | 346 | 211201.9994 | 348.5 | 252037.9994 | 351.5 | 211201.9994 | 354.5 | 211201.9994 | 357 | 211201.9994 | 360 | 211201.9994 | 362.5 | 232237.9994 | 365.5 | 211201.9994 | 368.5 | 211201.9994 | 371 | 211201.9994 | 374 | 252637.9994 | 376.5 | 211201.9994 | 379.5 | 211201.9994 | 382.5 | 252737.9994 | 385 | 211201.9994 | 388 | 252637.9994 | 391 | 211201.9994 | 393.5 | 241537.9994 | 337.5 | 105550.9988
396.5 | 211201.9994 | 399 | 211201.9994 | 402 | 211201.9994 | 404.5 | 211201.9994 | 407.5 | 252037.9994 | 410.5 | 211201.9994 | 413 | 211201.9994 | 416 | 211201.9994 | 418.5 | 211201.9994 | 421.5 | 232237.9994 | 424.5 | 211201.9994 | 427.5 | 211201.9994 | 430 | 211201.9994 | 432.5 | 252637.9994 | 435.5 | 211201.9994 | 438.5 | 211201.9994 | 441 | 252737.9994 | 444 | 211201.9994 | 447 | 252637.9994 | 449.5 | 211201.9994 | 452.5 | 241537.9994 | 396.5 | 211201.9994
455 | 211201.9994 | 458 | 211201.9994 | 460.5 | 211201.9994 | 463.5 | 211201.9994 | 466.5 | 252037.9994 | 469 | 211201.9994 | 472 | 105550.9988 | 474.5 | 211201.9994 | 477.5 | 211201.9994 | 480.5 | 232237.9994 | 483 | 211201.9994 | 486 | 211201.9994 | 488.5 | 211201.9994 | 491.5 | 252637.9994 | 494.5 | 211201.9994 | 497 | 211201.9994 | 500 | 252737.9994 | 502.5 | 211201.9994 | 505.5 | 252637.9994 | 508.5 | 211201.9994 | 511 | 241537.9994 | 455 | 105550.9988
514 | 211201.9994 | 517 | 211201.9994 | 519.5 | 211201.9994 | 522.5 | 211201.9994 | 525 | 252037.9994 | 528 | 211201.9994 | 530.5 | 211201.9994 | 533.5 | 211201.9994 | 536.5 | 211201.9994 | 539 | 232237.9994 | 542 | 211201.9994 | 544.5 | 211201.9994 | 547.5 | 211201.9994 | 550.5 | 252637.9994 | 553 | 211201.9994 | 556 | 211201.9994 | 558.5 | 252737.9994 | 561.5 | 211201.9994 | 564.5 | 252438.0791 | 567 | 211201.9994 | 570 | 241537.9994 | 514 | 211201.9994
572.5 | 211201.9994 | 575.5 | 211201.9994 | 578.5 | 211201.9994 | 581 | 211002.0947 | 584 | 252037.9994 | 586.5 | 211201.9994 | 589.5 | 211201.9994 | 592.5 | 211201.9994 | 595 | 211201.9994 | 598 | 232237.9994 | 600.5 | 211002.0947 | 603.5 | 211201.9994 | 606.5 | 211201.9994 | 609 | 252637.9994 | 612 | 211201.9994 | 614.5 | 211201.9994 | 617.5 | 252737.9994 | 620.5 | 211201.9994 | 623 | 252637.9994 | 626 | 211201.9994 | 628.5 | 241537.9994 | 572.5 | 211002.0947
631.5 | 211201.9994 | 634.5 | 211201.9994 | 637 | 211201.9994 | 640 | 211201.9994 | 642.5 | 252037.9994 | 645.5 | 211201.9994 | 648.5 | 211201.9994 | 651 | 211201.9994 | 654 | 211201.9994 | 656.5 | 232237.9994 | 659.5 | 211201.9994 | 662.5 | 211201.9994 | 665 | 211201.9994 | 668 | 252637.9994 | 670.5 | 211201.9994 | 673.5 | 211201.9994 | 676.5 | 252737.9994 | 679 | 211201.9994 | 682 | 252637.9994 | 684.5 | 211201.9994 | 687.5 | 241537.9994 | 631.5 | 211201.9994
690.5 | 211201.9994 | 693 | 211201.9994 | 696 | 211201.9994 | 698.5 | 211201.9994 | 701.5 | 252037.9994 | 704.5 | 211201.9994 | 707 | 211201.9994 | 710 | 211201.9994 | 712.5 | 211201.9994 | 715.5 | 232237.9994 | 718.5 | 211201.9994 | 721 | 211201.9994 | 724 | 211201.9994 | 726.5 | 252637.9994 | 729.5 | 211201.9994 | 732.5 | 211201.9994 | 735 | 252737.9994 | 738 | 211201.9994 | 740.5 | 252637.9994 | 743.5 | 211201.9994 | 746.5 | 241537.9994 | 690.5 | 211201.9994
749 | 211201.9994 | 752 | 211201.9994 | 754.5 | 211201.9994 | 757.5 | 211201.9994 | 760.5 | 252037.9994 | 763 | 211201.9994 | 766 | 211201.9994 | 768.5 | 105550.9988 | 771.5 | 211201.9994 | 774.5 | 232237.9994 | 777 | 211201.9994 | 780 | 211201.9994 | 782.5 | 211201.9994 | 785.5 | 252637.9994 | 788.5 | 211201.9994 | 791 | 211201.9994 | 794 | 252737.9994 | 796.5 | 211201.9994 | 799.5 | 252637.9994 | 802.5 | 211201.9994 | 805 | 241537.9994 | 749 | 105550.9988
808 | 211201.9994 | 810.5 | 211201.9994 | 813.5 | 211201.9994 | 816.5 | 211201.9994 | 819 | 252037.9994 | 822 | 211201.9994 | 824.5 | 211201.9994 | 827.5 | 211201.9994 | 830.5 | 211201.9994 | 833 | 232237.9994 | 836 | 211201.9994 | 838.5 | 211201.9994 | 841.5 | 211201.9994 | 844.5 | 252637.9994 | 847 | 211201.9994 | 850 | 211201.9994 | 852.5 | 252737.9994 | 855.5 | 211201.9994 | 858.5 | 252637.9994 | 861 | 211201.9994 | 864 | 241537.9994 | 808 | 211201.9994
866.5 | 211201.9994 | 869.5 | 211201.9994 | 872.5 | 211201.9994 | 875 | 211201.9994 | 878 | 252037.9994 | 880.5 | 211201.9994 | 883.5 | 211201.9994 | 886.5 | 211201.9994 | 889 | 211201.9994 | 892 | 232237.9994 | 894.5 | 211201.9994 | 897.5 | 211201.9994 | 900.5 | 211002.0947 | 903 | 252637.9994 | 906 | 211201.9994 | 908.5 | 211201.9994 | 911.5 | 252737.9994 | 914.5 | 211201.9994 | 917 | 252637.9994 | 920 | 211201.9994 | 922.5 | 241537.9994 | 866.5 | 211002.0947
925.5 | 211201.9994 | 928.5 | 211201.9994 | 931 | 211201.9994 | 934 | 211201.9994 | 936.5 | 252037.9994 | 939.5 | 211201.9994 | 942.5 | 211201.9994 | 945 | 211201.9994 | 948 | 211201.9994 | 950.5 | 232237.9994 | 953.5 | 211201.9994 | 956.5 | 211201.9994 | 959 | 211201.9994 | 962 | 252637.9994 | 964.5 | 211201.9994 | 967.5 | 211201.9994 | 970.5 | 252737.9994 | 973 | 211201.9994 | 976 | 252637.9994 | 978.5 | 211201.9994 | 981.5 | 241537.9994 | 925.5 | 211201.9994
984.5 | 211201.9994 | 987 | 211201.9994 | 990 | 211201.9994 | 992.5 | 211201.9994 | 995.5 | 252037.9994 | 998.5 | 211201.9994 | 1001 | 211201.9994 | 1004 | 211201.9994 | 1006.5 | 211201.9994 | 1009.5 | 232237.9994 | 1012.5 | 211201.9994 | 1015 | 211201.9994 | 1018 | 211201.9994 | 1020.5 | 252637.9994 | 1023.5 | 211201.9994 | 1026.5 | 211201.9994 | 1029 | 252737.9994 | 1032 | 211201.9994 | 1034.5 | 252637.9994 | 1037.5 | 211201.9994 | 1040.5 | 241537.9994 | 984.5 | 211201.9994
1043 | 211201.9994 | 1046 | 211201.9994 | 1048.5 | 211201.9994 | 1051.5 | 211201.9994 | 1054.5 | 252037.9994 | 1057 | 211201.9994 | 1060 | 211201.9994 | 1062.5 | 211201.9994 | 1065.5 | 211201.9994 | 1068 | 232237.9994 | 1071 | 211201.9994 | 1073.5 | 211201.9994 | 1076.5 | 211201.9994 | 1079.5 | 252637.9994 | 1082.5 | 211201.9994 | 1085 | 211201.9994 | 1088 | 252737.9994 | 1090.5 | 211201.9994 | 1093.5 | 252637.9994 | 1096.5 | 211201.9994 | 1099 | 241537.9994 | 1043 | 211201.9994
1102 | 211201.9994 | 1104.5 | 211201.9994 | 1107.5 | 211201.9994 | 1110.5 | 211201.9994 | 1113 | 252037.9994 | 1116 | 211201.9994 | 1118.5 | 211201.9994 | 1121.5 | 211201.9994 | 1124.5 | 211201.9994 | 1127 | 232237.9994 | 1129.5 | 211201.9994 | 1132.5 | 211201.9994 | 1135.5 | 211201.9994 | 1138.5 | 252637.9994 | 1141 | 211201.9994 | 1144 | 211201.9994 | 1146.5 | 252737.9994 | 1149.5 | 211201.9994 | 1152.5 | 252637.9994 | 1155 | 211201.9994 | 1158 | 241537.9994 | 1102 | 211201.9994
1160.5 | 211201.9994 | 1163.5 | 211201.9994 | 1166.5 | 211201.9994 | 1169 | 211201.9994 | 1172 | 252037.9994 | 1174.5 | 211201.9994 | 1177.5 | 211201.9994 | 1180.5 | 211201.9994 | 1183 | 211201.9994 | 1186 | 232237.9994 | 1188.5 | 211201.9994 | 1191.5 | 211201.9994 | 1194.5 | 211201.9994 | 1197 | 252637.9994 | 1200 | 211201.9994 | 1202.5 | 211201.9994 | 1205.5 | 252737.9994 | 1208 | 211201.9994 | 1211 | 252637.9994 | 1213.5 | 211201.9994 | 1216.5 | 241537.9994 | 1160.5 | 211201.9994
1219.5 | 211201.9994 | 1222.5 | 211201.9994 | 1225 | 211201.9994 | 1227.5 | 211201.9994 | 1230.5 | 252037.9994 | 1233.5 | 211201.9994 | 1236.5 | 211201.9994 | 1239 | 211201.9994 | 1242 | 211002.0947 | 1244.5 | 232237.9994 | 1247.5 | 211201.9994 | 1250.5 | 211201.9994 | 1253 | 211201.9994 | 1255.5 | 252637.9994 | 1258.5 | 211201.9994 | 1261.5 | 211201.9994 | 1264.5 | 252737.9994 | 1267 | 211201.9994 | 1270 | 252637.9994 | 1272.5 | 211201.9994 | 1275.5 | 241537.9994 | 1219.5 | 211002.0947
1278.5 | 211201.9994 | 1281 | 211201.9994 | 1284 | 211201.9994 | 1286.5 | 211201.9994 | 1289.5 | 252037.9994 | 1292.5 | 211201.9994 | 1295 | 211201.9994 | 1298 | 211201.9994 | 1300.5 | 211201.9994 | 1303.5 | 232237.9994 | 1306 | 211201.9994 | 1309 | 211201.9994 | 1312 | 211201.9994 | 1314.5 | 252637.9994 | 1317.5 | 211201.9994 | 1320.5 | 211201.9994 | 1323 | 252737.9994 | 1325.5 | 211201.9994 | 1328.5 | 252637.9994 | 1331.5 | 211201.9994 | 1334 | 241537.9994 | 1278.5 | 211201.9994
1337 | 211201.9994 | 1340 | 211201.9994 | 1342.5 | 211201.9994 | 1345.5 | 211201.9994 | 1348 | 252037.9994 | 1351 | 211201.9994 | 1354 | 211201.9994 | 1356.5 | 211201.9994 | 1359.5 | 211201.9994 | 1362.5 | 232237.9994 | 1365 | 211201.9994 | 1367.5 | 211201.9994 | 1370.5 | 211201.9994 | 1373.5 | 252637.9994 | 1376 | 211201.9994 | 1379 | 211201.9994 | 1382 | 252737.9994 | 1384.5 | 211201.9994 | 1387.5 | 252637.9994 | 1390.5 | 211201.9994 | 1393 | 241537.9994 | 1337 | 211201.9994
1396 | 211201.9994 | 1398.5 | 211201.9994 | 1401.5 | 211201.9994 | 1404.5 | 211201.9994 | 1407 | 252037.9994 | 1409.5 | 211201.9994 | 1412.5 | 211201.9994 | 1415.5 | 211201.9994 | 1418.5 | 211201.9994 | 1421 | 232237.9994 | 1423.5 | 211201.9994 | 1426.5 | 211201.9994 | 1429.5 | 211201.9994 | 1432.5 | 252637.9994 | 1435 | 211201.9994 | 1438 | 211201.9994 | 1440.5 | 252737.9994 | 1443.5 | 211201.9994 | 1446 | 252637.9994 | 1449 | 105550.9988 | 1451.5 | 241537.9994 | 1396 | 105550.9988
1454.5 | 211201.9994 | 1457.5 | 211201.9994 | 1460.5 | 211201.9994 | 1463 | 211201.9994 | 1465.5 | 252037.9994 | 1468.5 | 211201.9994 | 1471.5 | 211201.9994 | 1474 | 211201.9994 | 1478 | 211201.9994 | 1479.5 | 232237.9994 | 1482.5 | 211201.9994 | 1485.5 | 211201.9994 | 1488 | 211201.9994 | 1491 | 252637.9994 | 1493.5 | 211201.9994 | 1496.5 | 211201.9994 | 1499.5 | 252737.9994 | 1502 | 211201.9994 | 1505 | 252637.9994 | 1507.5 | 211201.9994 | 1510.5 | 241537.9994 | 1454.5 | 211201.9994
1513.5 | 211201.9994 | 1516 | 211201.9994 | 1519 | 211201.9994 | 1521.5 | 211201.9994 | 1524.5 | 252037.9994 | 1527.5 | 211201.9994 | 1530 | 211201.9994 | 1533 | 211201.9994 | 1535.5 | 211201.9994 | 1538.5 | 232237.9994 | 1541.5 | 211201.9994 | 1544.5 | 211201.9994 | 1547 | 211201.9994 | 1550 | 252637.9994 | 1552.5 | 211201.9994 | 1555.5 | 211201.9994 | 1558 | 252737.9994 | 1561 | 105550.9988 | 1563.5 | 252637.9994 | 1566.5 | 211201.9994 | 1569.5 | 241537.9994 | 1513.5 | 105550.9988
1572 | 211201.9994 | 1575 | 211201.9994 | 1578 | 211201.9994 | 1580.5 | 211201.9994 | 1583.5 | 252037.9994 | 1586.5 | 211201.9994 | 1589 | 211201.9994 | 1592 | 211201.9994 | 1594.5 | 211201.9994 | 1597.5 | 232237.9994 | 1600 | 211201.9994 | 1603 | 211201.9994 | 1605.5 | 211201.9994 | 1608.5 | 252637.9994 | 1611.5 | 211201.9994 | 1614 | 211201.9994 | 1617 | 252737.9994 | 1619.5 | 211201.9994 | 1622.5 | 252637.9994 | 1625.5 | 211201.9994 | 1628 | 241537.9994 | 1572 | 211201.9994
1631 | 211201.9994 | 1634 | 211201.9994 | 1636.5 | 211201.9994 | 1639.5 | 211201.9994 | 1642.5 | 252037.9994 | 1645 | 30085.9957 | 1647.5 | 35116.9963 | 1650.5 | 105550.9988 | 1653.5 | 105550.9988 | 1656 | 232237.9994 | 1659 | 30085.9957 | 1662 | 52725.4976 | 1664.5 | 105550.9988 | 1667.5 | 126268.9988 | 1670.5 | 30085.9957 | 1673 | 52725.4976 | 1675.5 | 84179.3315 | 1678.5 | 30085.9957 | 1681.5 | 63084.4976 | 1684 | 26312.7451 | 1687 | 19074.6391 | 1631 | 19074.6391
1689.5 | 35116.9963 | 1692.5 | 70333.9982 | 1695.5 | 70333.9982 | 1698 | 70333.9982 | 1701 | 125968.9988 | 1703.5 | 30085.9957 | 1706.5 | 52725.4976 | 1709.5 | 70333.9982 | 1712 | 70333.9982 | 1715 | 116068.9988 | 1717.5 | 30085.9957 | 1720.5 | 70333.9982 | 1723.5 | 105550.9988 | 1726 | 126268.9988 | 1729 | 26312.7451 | 1731.5 | 52725.4976 | 1734.5 | 126318.9988 | 1737.5 | 30085.9957 | 1740 | 63084.4976 | 1743 | 26312.7451 | 1745.5 | 8111.0572 | 1689.5 | 8111.0572
1748.5 | 30085.9957 | 1751.5 | 52725.4976 | 1754 | 70333.9982 | 1757 | 70333.9982 | 1759.5 | 83945.9982 | 1762.5 | 30085.9957 | 1765.5 | 52725.4976 | 1768 | 70333.9982 | 1771 | 70333.9982 | 1773.5 | 116068.9988 | 1776.5 | 30085.9957 | 1779.5 | 52725.4976 | 1782 | 70333.9982 | 1785 | 84145.9982 | 1787.5 | 30085.9957 | 1790.5 | 52725.4976 | 1793.5 | 84179.3315 | 1796 | 30085.9957 | 1799 | 84145.9982 | 1801.5 | 30085.9957 | 1804.5 | 2629.2663 | 1748.5 | 2629.2663
1807.5 | 35116.9963 | 1810 | 52725.4976 | 1813 | 70333.9982 | 1815.5 | 70333.9982 | 1818.5 | 83945.9982 | 1821.5 | 30085.9957 | 1824 | 52725.4976 | 1827 | 70333.9982 | 1829.5 | 70333.9982 | 1832.5 | 77345.9982 | 1835.5 | 26312.7451 | 1838 | 52725.4976 | 1841 | 70333.9982 | 1843.5 | 84145.9982 | 1846.5 | 30085.9957 | 1849.5 | 52725.4976 | 1852 | 84179.3315 | 1855 | 30085.9957 | 1857.5 | 63084.4976 | 1860.5 | 26312.7451 | 1863.5 | 1532.9081 | 1807.5 | 1532.9081
1866 | 30085.9957 | 1869 | 52725.4976 | 1871.5 | 70333.9982 | 1874.5 | 70333.9982 | 1877.5 | 83945.9982 | 1880 | 26312.7451 | 1883 | 52725.4976 | 1885.5 | 70333.9982 | 1888.5 | 105550.9988 | 1891.5 | 77345.9982 | 1894 | 30085.9957 | 1898 | 52725.4976 | 1899.5 | 70333.9982 | 1902.5 | 126268.9988 | 1905.5 | 30085.9957 | 1908 | 52725.4976 | 1911 | 126318.9988 | 1913.5 | 26312.7451 | 1916.5 | 63084.4976 | 1919.5 | 26312.7451 | 1922 | 45007.2399 | 1866 | 26312.7451
1925 | 30085.9957 | 1927.5 | 52725.4976 | 1930.5 | 70333.9982 | 1933.5 | 70333.9982 | 1936 | 125968.9988 | 1939 | 26312.7451 | 1941.5 | 42160.3969 | 1944.5 | 70333.9982 | 1947.5 | 70333.9982 | 1950 | 77345.9982 | 1953 | 30085.9957 | 1955.5 | 70333.9982 | 1958.5 | 70333.9982 | 1961.5 | 84145.9982 | 1964 | 30085.9957 | 1967 | 52725.4976 | 1969.5 | 84179.3315 | 1972.5 | 26312.7451 | 1975.5 | 63084.4976 | 1978 | 26312.7451 | 1981 | 44309.2678 | 1925 | 26312.7451
1983.5 | 30085.9957 | 1986.5 | 52725.4976 | 1989.5 | 52725.4976 | 1992 | 70333.9982 | 1995 | 83945.9982 | 1997.5 | 30085.9957 | 2000.5 | 52725.4976 | 2003.5 | 70333.9982 | 2006 | 105550.9988 | 2009 | 116068.9988 | 2011.5 | 30085.9957 | 2014.5 | 52725.4976 | 2017.5 | 70333.9982 | 2020 | 126268.9988 | 2023 | 30085.9957 | 2025.5 | 52725.4976 | 2028.5 | 84179.3315 | 2031.5 | 209804.5556 | 2034 | 63084.4976 | 2037 | 26312.7451 | 2039.5 | 24157.7543 | 1983.5 | 24157.7543

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 31 |  |  | 2006-07-27 | 13:16
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2
Penlight Penlight Penlight Time | C1-G |  | Penlight Penlight Penlight Time | C2-G | Penlight Penlight Penlight Time | C3-G | Penlight Penlight Penlight Time | C4-G | Penlight Penlight Penlight Time | C5-G | Penlight Penlight Penlight Time | C6-G | Penlight Penlight Penlight Time | C7-G | Penlight Penlight Penlight Time | Minimums Overall
-67 | 211202 |  | -55.25 | 211202 | -47.3333 | 211202 | -42.25 | 211202 | -39 | 211202 | -36.5833 | 232238 | -34.4167 | 105551 | -67 | 105551
-8.3333 | 105551 |  | 3.5 | 211202 | 11.4167 | 211202 | 16.5833 | 211202 | 19.9167 | 105551 | 22.25 | 232238 | 24.5 | 105551 | -8.3333 | 105551
50.6667 | 211202 |  | 62.3333 | 211202 | 70.3333 | 105551 | 75.4167 | 105551 | 78.8333 | 211202 | 81 | 232238 | 83.4167 | 105551 | 50.6667 | 105551
109.5 | 211202 |  | 121 | 211202 | 129 | 211202 | 134.1667 | 211202 | 137.3333 | 105551 | 139.5833 | 232238 | 142.0833 | 211202 | 109.5 | 105551
168.25 | 211202 |  | 179.9167 | 211202 | 187.75 | 211202 | 192.9167 | 211202 | 196.0833 | 211202 | 198.5 | 126269 | 200.9167 | 211202 | 168.25 | 126269
226.9167 | 211202 |  | 238.75 | 211202 | 246.5833 | 105551 | 251.6667 | 211202 | 255 | 126269 | 257.3333 | 125969 | 259.5833 | 211202 | 226.9167 | 105551
285.8333 | 211202 |  | 297.4167 | 211202 | 305.3333 | 105551 | 310.5 | 211202 | 313.6667 | 211202 | 316 | 232238 | 318.4167 | 211202 | 285.8333 | 105551
344.5 | 105551 |  | 356.1667 | 211202 | 364.1667 | 211202 | 369.25 | 211202 | 372.5833 | 211202 | 374.8333 | 125969 | 377.1667 | 105551 | 344.5 | 105551
403.3333 | 211202 |  | 415 | 211202 | 422.9167 | 211202 | 428.1667 | 211202 | 431.3333 | 211202 | 433.6667 | 126269 | 436.0833 | 105551 | 403.3333 | 105551
462.0833 | 211202 |  | 473.75 | 105551 | 481.75 | 211202 | 486.75 | 211202 | 490.0833 | 105551 | 492.5 | 232238 | 494.75 | 211202 | 462.0833 | 105551
521 | 211202 |  | 532.5833 | 211202 | 540.5 | 211202 | 545.5833 | 211202 | 549 | 211202 | 551.25 | 232238 | 553.5833 | 211202 | 521 | 211202
579.6667 | 211202 |  | 591.3333 | 211202 | 599.3333 | 211202 | 604.5 | 211202 | 607.6667 | 211202 | 610 | 232238 | 612.3333 | 211202 | 579.6667 | 211202
638.5 | 211202 |  | 650.1667 | 211202 | 658.1667 | 211202 | 663.25 | 211202 | 666.5 | 211202 | 668.8333 | 232238 | 671.0833 | 211202 | 638.5 | 211202
697.3333 | 211202 |  | 709 | 211202 | 716.8333 | 211202 | 722.0833 | 211202 | 725.25 | 105551 | 727.5833 | 232238 | 730.0833 | 105551 | 697.3333 | 105551
756.0833 | 211202 |  | 767.75 | 105551 | 775.75 | 211202 | 780.75 | 211202 | 784.0833 | 211202 | 786.5 | 126319 | 788.75 | 211202 | 756.0833 | 105551
814.9167 | 211202 |  | 826.5833 | 211202 | 834.4167 | 211202 | 839.5833 | 211202 | 843 | 211202 | 845.25 | 232238 | 847.5833 | 105551 | 814.9167 | 105551
873.6667 | 211202 |  | 885.3333 | 211202 | 893.3333 | 211202 | 898.5 | 211202 | 901.6667 | 211202 | 904 | 232238 | 906.3333 | 211202 | 873.6667 | 211202
932.5 | 211202 |  | 944.1667 | 211202 | 952.1667 | 105551 | 957.25 | 211202 | 960.5 | 211202 | 962.8333 | 232238 | 965.0833 | 211202 | 932.5 | 105551
991.3333 | 211202 |  | 1003 | 211202 | 1010.8333 | 211202 | 1016.0833 | 211202 | 1019.25 | 211202 | 1021.5833 | 232238 | 1024.0833 | 211202 | 991.3333 | 211202
1050.0833 | 211202 |  | 1061.6667 | 211202 | 1069.6667 | 211202 | 1074.6667 | 211202 | 1078.0833 | 211202 | 1080.4167 | 232238 | 1082.75 | 211202 | 1050.0833 | 211202
1108.9167 | 211202 |  | 1120.5 | 211202 | 1128.4167 | 211202 | 1133.5833 | 211202 | 1137 | 211202 | 1139.25 | 232238 | 1141.5 | 211202 | 1108.9167 | 211202
1167.6667 | 211202 |  | 1179.3333 | 211202 | 1187.3333 | 211202 | 1192.4167 | 211202 | 1195.5833 | 211202 | 1198 | 232238 | 1200.1667 | 211202 | 1167.6667 | 211202
1226.4167 | 211202 |  | 1238.1667 | 211202 | 1246.0833 | 211202 | 1251.25 | 211202 | 1254.4167 | 211202 | 1256.75 | 232238 | 1259.0833 | 211202 | 1226.4167 | 211202
1285.3333 | 211202 |  | 1296.9167 | 211202 | 1304.8333 | 211202 | 1310 | 211202 | 1313.25 | 211202 | 1315.5 | 126319 | 1317.8333 | 105551 | 1285.3333 | 105551
1344 | 211202 |  | 1355.75 | 211202 | 1363.5833 | 211202 | 1368.6667 | 211202 | 1372.0833 | 211202 | 1374.4167 | 232238 | 1376.6667 | 211202 | 1344 | 211202
1402.8333 | 211202 |  | 1414.5 | 211202 | 1422.4167 | 211202 | 1427.5833 | 211202 | 1430.9167 | 105551 | 1433.0833 | 232238 | 1435.3333 | 211202 | 1402.8333 | 105551
1461.5833 | 211202 |  | 1473.3333 | 211202 | 1481.1667 | 211202 | 1486.3333 | 211202 | 1489.6667 | 211202 | 1491.8333 | 232238 | 1494.0833 | 211202 | 1461.5833 | 211202
1520.3333 | 211202 |  | 1532 | 211202 | 1540 | 211202 | 1545.1667 | 105551 | 1548.25 | 211202 | 1550.6667 | 232238 | 1553.0833 | 211202 | 1520.3333 | 105551
1579.25 | 211202 |  | 1590.8333 | 211202 | 1598.75 | 211202 | 1603.9167 | 211202 | 1607.0833 | 211202 | 1609.5 | 232238 | 1611.8333 | 211202 | 1579.25 | 211202
1638.0833 | 30086 |  | 1649.5833 | 30086 | 1657.6667 | 30086 | 1662.6667 | 30086 | 1666 | 26312.75 | 1668.3333 | 0.71001 | 1670.6667 | 30104.75 | 1638.0833 | 0.71001
1696.6667 | 30086 |  | 1708.3333 | 30086 | 1716.3333 | 26312.75 | 1721.5 | 30086 | 1724.6667 | 26312.75 | 1727 | 2.1164 | 1729.3333 | 30104.75 | 1696.6667 | 2.1164
1755.5 | 30086 |  | 1767.1667 | 30086 | 1775.1667 | 30086 | 1780.25 | 30086 | 1783.5 | 30086 | 1785.8333 | 0.65389 | 1788.0833 | 30104.75 | 1755.5 | 0.65389
1814.3333 | 30086 |  | 1826 | 26312.75 | 1833.8333 | 30086 | 1839.0833 | 30086 | 1842.25 | 26312.75 | 1844.5833 | 0.68279 | 1847.0833 | 30104.75 | 1814.3333 | 0.68279
1873.0833 | 26312.75 |  | 1884.75 | 30086 | 1892.9167 | 30086 | 1897.9167 | 26312.75 | 1901.0833 | 26312.75 | 1903.5 | 0.69243 | 1905.75 | 34419.7143 | 1873.0833 | 0.69243
1931.9167 | 26312.75 |  | 1943.5833 | 30086 | 1951.4167 | 30086 | 1956.5833 | 26312.75 | 1960 | 26312.75 | 1962.25 | 0.65207 | 1964.5833 | 30086 | 1931.9167 | 0.65207
1990.6667 | 30086 |  | 2002.3333 | 30086 | 2010.3333 | 30086 | 2015.5 | 30083.9525 | 2018.6667 | 26312.75 | 2021 | 11.2054 | 2023.3333 | 30104.75 | 1990.6667 | 11.2054

## C6-7
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 147.5201 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38925.5526 | 1 | 0 | 38925.5526 | 1 | 0 | -18 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5533 | 1 | 0 | 38925.5533 | 1 | 0 | 41 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5539 | 1 | 0 | 38925.554 | 1 | 0 | 99.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5546 | 1 | 0 | 38925.5546 | 1 | 0 | 158.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5553 | 1 | 0 | 38925.5553 | 1 | 0 | 217 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.556 | 1 | 0 | 38925.556 | 1 | 0 | 276 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5567 | 1 | 0 | 38925.5567 | 1 | 0 | 334.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5573 | 1 | 0 | 38925.5574 | 1 | 0 | 393.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.558 | 1 | 0 | 38925.558 | 1 | 0 | 452.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5587 | 1 | 0 | 38925.5587 | 1 | 0 | 511 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5594 | 1 | 0 | 38925.5594 | 1 | 0 | 570 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5601 | 1 | 0 | 38925.5601 | 1 | 0 | 628.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5608 | 1 | 0 | 38925.5608 | 1 | 0 | 687.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5614 | 1 | 0 | 38925.5614 | 1 | 0 | 746.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5621 | 1 | 0 | 38925.5621 | 1 | 0 | 805 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5628 | 1 | 0 | 38925.5628 | 1 | 0 | 864 | 939 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5635 | 1 | 0 | 38925.5635 | 1 | 0 | 922.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5642 | 1 | 0 | 38925.5642 | 1 | 0 | 981.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5648 | 1 | 0 | 38925.5648 | 1 | 0 | 1040.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5655 | 1 | 0 | 38925.5655 | 1 | 0 | 1099 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5662 | 1 | 0 | 38925.5662 | 1 | 0 | 1158 | 1233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5669 | 1 | 0 | 38925.5669 | 1 | 0 | 1216.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5676 | 1 | 0 | 38925.5676 | 1 | 0 | 1275.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5682 | 1 | 0 | 38925.5683 | 1 | 0 | 1334 | 1409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5689 | 1 | 0 | 38925.5689 | 1 | 0 | 1393 | 1468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5696 | 1 | 0 | 38925.5696 | 1 | 0 | 1451.5 | 1526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5703 | 1 | 0 | 38925.5703 | 1 | 0 | 1510.5 | 1585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.571 | 1 | 0 | 38925.571 | 1 | 0 | 1569.5 | 1644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5716 | 1 | 0 | 38925.5717 | 1 | 0 | 1628 | 1703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
38925.5723 | 2224 | 1 | 38925.5723 | 8 | 0 | 1687 | 1762 | 135.7753 | 0.06105 | 0.4884 | 0 | 1.3578 | 0.0006105 | 0.004884 | 0 | 1.3571 | 0.004884 | 8.6541 | 30104.75 | 19074.6391
38925.573 | 2334 | 1 | 38925.573 | 8 | 0 | 1745.5 | 1820.5 | 142.4908 | 0.06105 | 0.4884 | 0 | 1.4249 | 0.0006105 | 0.004884 | 0 | 1.4243 | 0.004884 | 3.5311 | 30104.75 | 8111.0572
38925.5737 | 2389 | 1 | 38925.5737 | 8 | 0 | 1804.5 | 1879.5 | 145.8486 | 0.06105 | 0.4884 | 0 | 1.4585 | 0.0006105 | 0.004884 | 0 | 1.4579 | 0.004884 | 1.1466 | 30104.75 | 2629.2663
38925.5744 | 2400 | 1 | 38925.5744 | 8 | 0 | 1863.5 | 1938.5 | 146.5201 | 0.06105 | 0.4884 | 0 | 1.4652 | 0.0006105 | 0.004884 | 0 | 1.4646 | 0.004884 | 0.68279 | 30104.75 | 1532.9081
38925.575 | 1964 | 1 | 38925.5751 | 7 | 0 | 1922 | 1997 | 119.9023 | 0.06105 | 0.42735 | 0 | 1.199 | 0.0006105 | 0.0042735 | 0 | 1.1984 | 0.0042735 | 23.0454 | 34419.7143 | 45007.2399
38925.5757 | 1971 | 1 | 38925.5757 | 7 | 0 | 1981 | 2056 | 120.3297 | 0.06105 | 0.42735 | 0 | 1.2033 | 0.0006105 | 0.0042735 | 0 | 1.2027 | 0.0042735 | 22.6082 | 34419.7143 | 44309.2678
38925.5764 | 2173 | 1 | 38925.5764 | 8 | 0 | 2039.5 | 2114.5 | 132.6618 | 0.06105 | 0.4884 | 0 | 1.3266 | 0.0006105 | 0.004884 | 0 | 1.326 | 0.004884 | 11.2054 | 30104.75 | 24157.7543

## C5-7
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38925.5525 | 1 | 0 | 38925.5526 | 1 | 0 | -21 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5532 | 1 | 0 | 38925.5533 | 1 | 0 | 38 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38925.5539 | 1 | 0 | 98 | 173 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5546 | 1 | 0 | 38925.5546 | 1 | 0 | 155.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5553 | 1 | 0 | 38925.5553 | 1 | 0 | 214.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5559 | 1 | 0 | 38925.556 | 1 | 0 | 273 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5566 | 1 | 0 | 38925.5567 | 1 | 0 | 332 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5573 | 1 | 0 | 38925.5573 | 1 | 0 | 391 | 466 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.558 | 1 | 0 | 38925.558 | 1 | 0 | 449.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5587 | 1 | 0 | 38925.5587 | 1 | 0 | 508.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5594 | 1 | 0 | 38925.5594 | 1 | 0 | 567 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.56 | 1 | 0 | 38925.5601 | 1 | 0 | 626 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5607 | 1 | 0 | 38925.5607 | 1 | 0 | 684.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5614 | 1 | 0 | 38925.5614 | 2 | 0 | 743.5 | 818.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5621 | 1 | 0 | 38925.5621 | 1 | 0 | 802.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5628 | 1 | 0 | 38925.5628 | 1 | 0 | 861 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5634 | 1 | 0 | 38925.5635 | 1 | 0 | 920 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5641 | 1 | 0 | 38925.5641 | 1 | 0 | 978.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5648 | 1 | 0 | 38925.5648 | 1 | 0 | 1037.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5655 | 1 | 0 | 38925.5655 | 1 | 0 | 1096.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5662 | 1 | 0 | 38925.5662 | 1 | 0 | 1155 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5668 | 1 | 0 | 38925.5669 | 1 | 0 | 1213.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5675 | 1 | 0 | 38925.5675 | 1 | 0 | 1272.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5682 | 1 | 0 | 38925.5682 | 1 | 0 | 1331.5 | 1406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5689 | 1 | 0 | 38925.5689 | 1 | 0 | 1390.5 | 1465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5696 | 2 | 0 | 38925.5696 | 1 | 0 | 1449 | 1524 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5702 | 1 | 0 | 38925.5703 | 1 | 0 | 1507.5 | 1582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5709 | 1 | 0 | 38925.5709 | 1 | 0 | 1566.5 | 1641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5716 | 1 | 0 | 38925.5716 | 1 | 0 | 1625.5 | 1700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5723 | 8 | 0 | 38925.5723 | 6 | 0 | 1684 | 1759 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 26312.75 | 35117 | 26312.7451
38925.573 | 8 | 0 | 38925.573 | 5 | 0 | 1743 | 1818 | 0.4884 | 0 | 0.30525 | 0 | 0.004884 | 0 | 0.0030525 | 0 | 0.004884 | 0.0030525 | 26312.75 | 42160.4 | 26312.7451
38925.5736 | 7 | 0 | 38925.5737 | 6 | 0 | 1801.5 | 1876.5 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 30086 | 35117 | 30085.9957
38925.5743 | 8 | 0 | 38925.5743 | 6 | 0 | 1860.5 | 1935.5 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 26312.75 | 35117 | 26312.7451
38925.575 | 8 | 0 | 38925.575 | 6 | 0 | 1919.5 | 1994.5 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 26312.75 | 35117 | 26312.7451
38925.5757 | 8 | 0 | 38925.5757 | 7 | 0 | 1978 | 2053 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 26312.75 | 30086 | 26312.7451
38925.5764 | 8 | 0 | 38925.5764 | 6 | 0 | 2037 | 2112 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 26312.75 | 35117 | 26312.7451

## C5-6
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 154.2967 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38925.5525 | 1 | 0 | 38925.5525 | 1 | 0 | -23.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5532 | 1 | 0 | 38925.5532 | 1 | 0 | 35.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5539 | 1 | 0 | 38925.5539 | 1 | 0 | 94 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5546 | 1 | 0 | 38925.5546 | 1 | 0 | 152.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5552 | 1 | 0 | 38925.5553 | 2 | 0 | 211.5 | 286.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252638 | 126269 | 252637.9994
38925.5559 | 2 | 0 | 38925.5559 | 1 | 0 | 270.5 | 345.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126269 | 252638 | 126268.9988
38925.5566 | 1 | 0 | 38925.5566 | 1 | 0 | 329 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5573 | 1 | 0 | 38925.5573 | 1 | 0 | 388 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.558 | 1 | 0 | 38925.558 | 2 | 0 | 447 | 522 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252638 | 126269 | 252637.9994
38925.5586 | 1 | 0 | 38925.5587 | 1 | 0 | 505.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5593 | 1 | 1 | 38925.5593 | 1 | 0 | 564.5 | 639.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 638259590.44 | 252638 | 252438.0791
38925.56 | 1 | 0 | 38925.56 | 1 | 0 | 623 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5607 | 1 | 0 | 38925.5607 | 1 | 0 | 682 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5614 | 1 | 0 | 38925.5614 | 1 | 0 | 740.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.562 | 1 | 0 | 38925.5621 | 1 | 0 | 799.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5627 | 1 | 0 | 38925.5627 | 1 | 0 | 858.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5634 | 1 | 0 | 38925.5634 | 1 | 0 | 917 | 992 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5641 | 1 | 0 | 38925.5641 | 1 | 0 | 976 | 1051 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5648 | 1 | 0 | 38925.5648 | 1 | 0 | 1034.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5655 | 1 | 0 | 38925.5655 | 1 | 0 | 1093.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5661 | 1 | 0 | 38925.5661 | 1 | 0 | 1152.5 | 1227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5668 | 1 | 0 | 38925.5668 | 1 | 0 | 1211 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5675 | 1 | 0 | 38925.5675 | 1 | 0 | 1270 | 1345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5682 | 1 | 0 | 38925.5682 | 1 | 0 | 1328.5 | 1403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5689 | 1 | 0 | 38925.5689 | 1 | 0 | 1387.5 | 1462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5695 | 1 | 0 | 38925.5695 | 1 | 0 | 1446 | 1521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5702 | 1 | 0 | 38925.5702 | 1 | 0 | 1505 | 1580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5709 | 1 | 0 | 38925.5709 | 1 | 0 | 1563.5 | 1638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5716 | 1 | 0 | 38925.5716 | 1 | 0 | 1622.5 | 1697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5723 | 4 | 0 | 38925.5723 | 2477 | 0 | 1681.5 | 1756.5 | 0.2442 | 0 | 151.221 | 0 | 0.002442 | 0 | 1.5122 | 0 | 0.002442 | 1.5122 | 63084.5 | 2.0339 | 63084.4976
38925.5729 | 4 | 0 | 38925.573 | 2475 | 0 | 1740 | 1815 | 0.2442 | 0 | 151.0989 | 0 | 0.002442 | 0 | 1.511 | 0 | 0.002442 | 1.511 | 63084.5 | 2.1164 | 63084.4976
38925.5736 | 3 | 0 | 38925.5736 | 2173 | 0 | 1799 | 1874 | 0.18315 | 0 | 132.6618 | 0 | 0.0018315 | 0 | 1.3266 | 0 | 0.0018315 | 1.3266 | 84146 | 16.3083 | 84145.9982
38925.5743 | 4 | 0 | 38925.5743 | 2160 | 0 | 1857.5 | 1932.5 | 0.2442 | 0 | 131.8681 | 0 | 0.002442 | 0 | 1.3187 | 0 | 0.002442 | 1.3187 | 63084.5 | 17.0083 | 63084.4976
38925.575 | 4 | 0 | 38925.575 | 2452 | 0 | 1916.5 | 1991.5 | 0.2442 | 0 | 149.6947 | 0 | 0.002442 | 0 | 1.4969 | 0 | 0.002442 | 1.4969 | 63084.5 | 3.0742 | 63084.4976
38925.5757 | 4 | 0 | 38925.5757 | 2511 | 0 | 1975.5 | 2050.5 | 0.2442 | 0 | 153.2967 | 0 | 0.002442 | 0 | 1.533 | 0 | 0.002442 | 1.533 | 63084.5 | 0.65233 | 63084.4976
38925.5763 | 4 | 0 | 38925.5764 | 2118 | 0 | 2034 | 2109 | 0.2442 | 0 | 129.304 | 0 | 0.002442 | 0 | 1.293 | 0 | 0.002442 | 1.293 | 63084.5 | 19.3286 | 63084.4976

## C4-7
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38925.5525 | 1 | 0 | 38925.5525 | 1 | 0 | -26.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5532 | 1 | 0 | 38925.5532 | 1 | 0 | 32.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5538 | 1 | 0 | 38925.5539 | 1 | 0 | 91 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5545 | 1 | 0 | 38925.5545 | 1 | 0 | 150 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5552 | 1 | 0 | 38925.5552 | 1 | 0 | 208.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5559 | 1 | 0 | 38925.5559 | 1 | 0 | 267.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5566 | 1 | 0 | 38925.5566 | 1 | 0 | 326.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5572 | 1 | 0 | 38925.5573 | 2 | 0 | 385 | 460 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5579 | 1 | 0 | 38925.558 | 1 | 0 | 444 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5586 | 1 | 0 | 38925.5586 | 1 | 0 | 502.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5593 | 1 | 0 | 38925.5593 | 1 | 0 | 561.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.56 | 1 | 0 | 38925.56 | 1 | 0 | 620.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5606 | 1 | 0 | 38925.5607 | 1 | 0 | 679 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5613 | 1 | 0 | 38925.5614 | 1 | 0 | 738 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.562 | 1 | 0 | 38925.562 | 1 | 0 | 796.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5627 | 1 | 0 | 38925.5627 | 1 | 0 | 855.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5634 | 1 | 0 | 38925.5634 | 1 | 0 | 914.5 | 989.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5641 | 1 | 0 | 38925.5641 | 1 | 0 | 973 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5647 | 1 | 0 | 38925.5648 | 1 | 0 | 1032 | 1107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5654 | 1 | 0 | 38925.5654 | 1 | 0 | 1090.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5661 | 1 | 0 | 38925.5661 | 1 | 0 | 1149.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5668 | 1 | 0 | 38925.5668 | 1 | 0 | 1208 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5675 | 1 | 0 | 38925.5675 | 1 | 0 | 1267 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5681 | 1 | 0 | 38925.5681 | 1 | 0 | 1325.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5688 | 1 | 0 | 38925.5688 | 1 | 0 | 1384.5 | 1459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5695 | 1 | 0 | 38925.5695 | 1 | 0 | 1443.5 | 1518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5702 | 1 | 0 | 38925.5702 | 1 | 0 | 1502 | 1577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5709 | 2 | 0 | 38925.5709 | 1 | 0 | 1561 | 1636 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5715 | 1 | 0 | 38925.5716 | 1 | 0 | 1619.5 | 1694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5722 | 7 | 0 | 38925.5722 | 5 | 0 | 1678.5 | 1753.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5729 | 7 | 0 | 38925.5729 | 6 | 0 | 1737.5 | 1812.5 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 30086 | 35117 | 30085.9957
38925.5736 | 7 | 0 | 38925.5736 | 6 | 0 | 1796 | 1871 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 30086 | 35117 | 30085.9957
38925.5743 | 7 | 0 | 38925.5743 | 6 | 0 | 1855 | 1930 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 30086 | 35117 | 30085.9957
38925.5749 | 8 | 0 | 38925.575 | 6 | 0 | 1913.5 | 1988.5 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 26312.75 | 35117 | 26312.7451
38925.5756 | 8 | 0 | 38925.5756 | 6 | 1 | 1972.5 | 2047.5 | 0.4884 | 0 | 0.3663 | 0.06105 | 0.004884 | 0 | 0.003663 | 0.0006105 | 0.004884 | 0.0030525 | 26312.75 | 42160.4 | 26312.7451
38925.5763 | 8 | 1 | 38925.5763 | 6 | 0 | 2031.5 | 2106.5 | 0.4884 | 0.06105 | 0.3663 | 0 | 0.004884 | 0.0006105 | 0.003663 | 0 | 0.0042735 | 0.003663 | 30083.9525 | 35117 | 209804.5556

## C4-6
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 154.3578 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38925.5525 | 1 | 0 | 38925.5525 | 1 | 0 | -29 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5531 | 1 | 0 | 38925.5531 | 1 | 0 | 29.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5538 | 1 | 0 | 38925.5538 | 1 | 0 | 88.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5545 | 1 | 0 | 38925.5545 | 1 | 0 | 147 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5552 | 1 | 0 | 38925.5552 | 1 | 0 | 206 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5559 | 1 | 0 | 38925.5559 | 1 | 0 | 264.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5565 | 1 | 1 | 38925.5566 | 1 | 0 | 323.5 | 398.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 638764966.44 | 252738 | 252538.0791
38925.5572 | 1 | 0 | 38925.5572 | 1 | 0 | 382.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5579 | 1 | 0 | 38925.5579 | 1 | 0 | 441 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5586 | 1 | 0 | 38925.5586 | 1 | 0 | 500 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5593 | 1 | 0 | 38925.5593 | 1 | 0 | 558.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5599 | 1 | 0 | 38925.56 | 1 | 0 | 617.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5606 | 1 | 0 | 38925.5606 | 1 | 0 | 676.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5613 | 1 | 0 | 38925.5613 | 1 | 0 | 735 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.562 | 1 | 0 | 38925.562 | 2 | 0 | 794 | 869 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252738 | 126319 | 252737.9994
38925.5627 | 1 | 0 | 38925.5627 | 1 | 0 | 852.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5633 | 1 | 0 | 38925.5634 | 1 | 0 | 911.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.564 | 1 | 0 | 38925.564 | 1 | 0 | 970.5 | 1045.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5647 | 1 | 0 | 38925.5647 | 1 | 0 | 1029 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5654 | 1 | 0 | 38925.5654 | 1 | 0 | 1088 | 1163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5661 | 1 | 0 | 38925.5661 | 1 | 0 | 1146.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5667 | 1 | 0 | 38925.5668 | 1 | 0 | 1205.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5674 | 1 | 0 | 38925.5674 | 1 | 0 | 1264.5 | 1339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5681 | 1 | 0 | 38925.5681 | 2 | 0 | 1323 | 1398 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252738 | 126319 | 252737.9994
38925.5688 | 1 | 0 | 38925.5688 | 1 | 0 | 1382 | 1457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5695 | 1 | 0 | 38925.5695 | 1 | 0 | 1440.5 | 1515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5702 | 1 | 0 | 38925.5702 | 1 | 0 | 1499.5 | 1574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5708 | 1 | 0 | 38925.5708 | 1 | 0 | 1558 | 1633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5715 | 1 | 0 | 38925.5715 | 1 | 0 | 1617 | 1692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38925.5722 | 3 | 0 | 38925.5722 | 1983 | 0 | 1675.5 | 1750.5 | 0.18315 | 0 | 121.0623 | 0 | 0.0018315 | 0 | 1.2106 | 0 | 0.0018315 | 1.2106 | 84179.3333 | 27.5028 | 84179.3315
38925.5729 | 2 | 0 | 38925.5729 | 2377 | 0 | 1734.5 | 1809.5 | 0.1221 | 0 | 145.116 | 0 | 0.001221 | 0 | 1.4512 | 0 | 0.001221 | 1.4512 | 126319 | 6.3685 | 126318.9988
38925.5736 | 3 | 0 | 38925.5736 | 2081 | 0 | 1793.5 | 1868.5 | 0.18315 | 0 | 127.0452 | 0 | 0.0018315 | 0 | 1.2705 | 0 | 0.0018315 | 1.2705 | 84179.3333 | 21.4983 | 84179.3315
38925.5742 | 3 | 0 | 38925.5742 | 2353 | 0 | 1852 | 1927 | 0.18315 | 0 | 143.6508 | 0 | 0.0018315 | 0 | 1.4365 | 0 | 0.0018315 | 1.4365 | 84179.3333 | 7.4535 | 84179.3315
38925.5749 | 2 | 0 | 38925.5749 | 1961 | 0 | 1911 | 1986 | 0.1221 | 0 | 119.7192 | 0 | 0.001221 | 0 | 1.1972 | 0 | 0.001221 | 1.1972 | 126319 | 28.9332 | 126318.9988
38925.5756 | 3 | 0 | 38925.5756 | 2512 | 0 | 1969.5 | 2044.5 | 0.18315 | 0 | 153.3578 | 0 | 0.0018315 | 0 | 1.5336 | 0 | 0.0018315 | 1.5336 | 84179.3333 | 0.65207 | 84179.3315
38925.5763 | 3 | 0 | 38925.5763 | 2228 | 0 | 2028.5 | 2103.5 | 0.18315 | 0 | 136.0195 | 0 | 0.0018315 | 0 | 1.3602 | 0 | 0.0018315 | 1.3602 | 84179.3333 | 13.482 | 84179.3315

## C4-5
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38925.5524 | 1 | 0 | 38925.5524 | 1 | 0 | -32 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5531 | 1 | 0 | 38925.5531 | 1 | 0 | 27 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5538 | 1 | 0 | 38925.5538 | 1 | 0 | 85.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5545 | 1 | 1 | 38925.5545 | 1 | 0 | 144.5 | 219.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5551 | 1 | 0 | 38925.5552 | 1 | 0 | 203 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5558 | 1 | 0 | 38925.5558 | 1 | 0 | 262 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5565 | 1 | 0 | 38925.5565 | 1 | 0 | 320.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5572 | 1 | 0 | 38925.5572 | 1 | 0 | 379.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5579 | 1 | 0 | 38925.5579 | 1 | 0 | 438.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5585 | 1 | 0 | 38925.5586 | 1 | 0 | 497 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5592 | 1 | 0 | 38925.5592 | 1 | 0 | 556 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5599 | 1 | 0 | 38925.5599 | 1 | 0 | 614.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5606 | 1 | 0 | 38925.5606 | 1 | 0 | 673.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5613 | 1 | 0 | 38925.5613 | 1 | 0 | 732.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5619 | 1 | 0 | 38925.562 | 1 | 0 | 791 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5626 | 1 | 0 | 38925.5627 | 1 | 0 | 850 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5633 | 1 | 0 | 38925.5633 | 1 | 0 | 908.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.564 | 1 | 0 | 38925.564 | 1 | 0 | 967.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5647 | 1 | 0 | 38925.5647 | 1 | 0 | 1026.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5653 | 1 | 0 | 38925.5654 | 1 | 0 | 1085 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.566 | 1 | 0 | 38925.5661 | 1 | 0 | 1144 | 1219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5667 | 1 | 0 | 38925.5667 | 1 | 0 | 1202.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5674 | 1 | 0 | 38925.5674 | 1 | 0 | 1261.5 | 1336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5681 | 1 | 0 | 38925.5681 | 1 | 0 | 1320.5 | 1395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5687 | 1 | 0 | 38925.5688 | 1 | 0 | 1379 | 1454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5694 | 1 | 0 | 38925.5695 | 1 | 0 | 1438 | 1513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5701 | 1 | 0 | 38925.5701 | 1 | 0 | 1496.5 | 1571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5708 | 1 | 0 | 38925.5708 | 1 | 0 | 1555.5 | 1630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5715 | 1 | 0 | 38925.5715 | 1 | 0 | 1614 | 1689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5722 | 4 | 0 | 38925.5722 | 3 | 0 | 1673 | 1748 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5728 | 4 | 0 | 38925.5728 | 3 | 0 | 1731.5 | 1806.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5735 | 4 | 0 | 38925.5735 | 3 | 0 | 1790.5 | 1865.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5742 | 4 | 0 | 38925.5742 | 4 | 0 | 1849.5 | 1924.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38925.5749 | 4 | 0 | 38925.5749 | 3 | 0 | 1908 | 1983 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5756 | 4 | 0 | 38925.5756 | 3 | 0 | 1967 | 2042 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5762 | 4 | 0 | 38925.5762 | 4 | 0 | 2025.5 | 2100.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## C3-7
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38925.5524 | 1 | 0 | 38925.5524 | 1 | 0 | -35 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5531 | 1 | 0 | 38925.5531 | 2 | 0 | 24 | 99 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5537 | 1 | 0 | 38925.5538 | 2 | 0 | 83 | 158 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5544 | 1 | 1 | 38925.5544 | 1 | 0 | 141.5 | 216.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5551 | 1 | 0 | 38925.5551 | 1 | 0 | 200.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5558 | 2 | 0 | 38925.5558 | 1 | 0 | 259 | 334 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5565 | 1 | 0 | 38925.5565 | 1 | 0 | 318 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5572 | 1 | 0 | 38925.5572 | 1 | 0 | 376.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5578 | 1 | 0 | 38925.5578 | 1 | 0 | 435.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5585 | 1 | 0 | 38925.5585 | 1 | 0 | 494.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5592 | 1 | 0 | 38925.5592 | 1 | 0 | 553 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5599 | 1 | 0 | 38925.5599 | 1 | 0 | 612 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5606 | 1 | 0 | 38925.5606 | 1 | 0 | 670.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5612 | 1 | 0 | 38925.5612 | 1 | 0 | 729.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5619 | 1 | 0 | 38925.5619 | 1 | 0 | 788.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5626 | 1 | 0 | 38925.5626 | 1 | 0 | 847 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5633 | 1 | 0 | 38925.5633 | 1 | 0 | 906 | 981 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.564 | 1 | 0 | 38925.564 | 1 | 0 | 964.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5646 | 1 | 0 | 38925.5647 | 1 | 0 | 1023.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5653 | 1 | 0 | 38925.5653 | 1 | 0 | 1082.5 | 1157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.566 | 1 | 0 | 38925.566 | 1 | 0 | 1141 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5667 | 1 | 0 | 38925.5667 | 1 | 0 | 1200 | 1275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5674 | 1 | 0 | 38925.5674 | 1 | 0 | 1258.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.568 | 1 | 0 | 38925.5681 | 1 | 0 | 1317.5 | 1392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5687 | 1 | 0 | 38925.5687 | 1 | 0 | 1376 | 1451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5694 | 1 | 0 | 38925.5694 | 1 | 0 | 1435 | 1510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5701 | 1 | 0 | 38925.5701 | 1 | 0 | 1493.5 | 1568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5708 | 1 | 0 | 38925.5708 | 1 | 0 | 1552.5 | 1627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5714 | 1 | 0 | 38925.5715 | 1 | 0 | 1611.5 | 1686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5721 | 7 | 0 | 38925.5721 | 5 | 0 | 1670.5 | 1745.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5728 | 8 | 0 | 38925.5728 | 5 | 0 | 1729 | 1804 | 0.4884 | 0 | 0.30525 | 0 | 0.004884 | 0 | 0.0030525 | 0 | 0.004884 | 0.0030525 | 26312.75 | 42160.4 | 26312.7451
38925.5735 | 7 | 0 | 38925.5735 | 5 | 0 | 1787.5 | 1862.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5742 | 7 | 0 | 38925.5742 | 5 | 0 | 1846.5 | 1921.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5748 | 7 | 0 | 38925.5749 | 5 | 0 | 1905.5 | 1980.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5755 | 7 | 0 | 38925.5755 | 5 | 0 | 1964 | 2039 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5762 | 7 | 0 | 38925.5762 | 5 | 0 | 2023 | 2098 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957

## C3-6
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 154.2967 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38925.5524 | 1 | 1 | 38925.5524 | 1 | 0 | -37.5 | 37.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 638259590.44 | 252638 | 252438.0791
38925.553 | 1 | 0 | 38925.5531 | 1 | 0 | 21.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5537 | 1 | 1 | 38925.5537 | 1 | 0 | 80 | 155 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 638259590.44 | 252638 | 252438.0791
38925.5544 | 1 | 0 | 38925.5544 | 1 | 0 | 138.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5551 | 1 | 0 | 38925.5551 | 1 | 0 | 197.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5558 | 1 | 0 | 38925.5558 | 1 | 0 | 256.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5564 | 1 | 0 | 38925.5565 | 1 | 0 | 315 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5571 | 1 | 0 | 38925.5571 | 1 | 0 | 374 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5578 | 1 | 0 | 38925.5578 | 1 | 0 | 432.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5585 | 1 | 0 | 38925.5585 | 1 | 0 | 491.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5592 | 1 | 0 | 38925.5592 | 1 | 0 | 550.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5598 | 1 | 0 | 38925.5599 | 1 | 0 | 609 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5605 | 1 | 0 | 38925.5605 | 1 | 0 | 668 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5612 | 1 | 0 | 38925.5612 | 1 | 0 | 726.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5619 | 1 | 0 | 38925.5619 | 1 | 0 | 785.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5626 | 1 | 0 | 38925.5626 | 1 | 0 | 844.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5632 | 1 | 0 | 38925.5633 | 1 | 0 | 903 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5639 | 1 | 0 | 38925.5639 | 1 | 0 | 962 | 1037 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5646 | 1 | 0 | 38925.5646 | 1 | 0 | 1020.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5653 | 1 | 0 | 38925.5653 | 1 | 0 | 1079.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.566 | 1 | 0 | 38925.566 | 1 | 0 | 1138.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5666 | 1 | 0 | 38925.5667 | 1 | 0 | 1197 | 1272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5673 | 1 | 0 | 38925.5673 | 1 | 0 | 1255.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.568 | 1 | 0 | 38925.568 | 1 | 0 | 1314.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5687 | 1 | 0 | 38925.5687 | 1 | 0 | 1373.5 | 1448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5694 | 1 | 0 | 38925.5694 | 1 | 0 | 1432.5 | 1507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.57 | 1 | 0 | 38925.5701 | 1 | 0 | 1491 | 1566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5707 | 1 | 0 | 38925.5708 | 1 | 0 | 1550 | 1625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5714 | 1 | 0 | 38925.5714 | 1 | 0 | 1608.5 | 1683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38925.5721 | 2 | 0 | 38925.5721 | 2291 | 0 | 1667.5 | 1742.5 | 0.1221 | 0 | 139.8657 | 0 | 0.001221 | 0 | 1.3987 | 0 | 0.001221 | 1.3987 | 126269 | 10.3178 | 126268.9988
38925.5728 | 2 | 0 | 38925.5728 | 2262 | 0 | 1726 | 1801 | 0.1221 | 0 | 138.0952 | 0 | 0.001221 | 0 | 1.381 | 0 | 0.001221 | 1.381 | 126269 | 11.7321 | 126268.9988
38925.5734 | 3 | 0 | 38925.5735 | 2231 | 0 | 1785 | 1860 | 0.18315 | 0 | 136.2027 | 0 | 0.0018315 | 0 | 1.362 | 0 | 0.0018315 | 1.362 | 84146 | 13.2846 | 84145.9982
38925.5741 | 3 | 0 | 38925.5741 | 2353 | 0 | 1843.5 | 1918.5 | 0.18315 | 0 | 143.6508 | 0 | 0.0018315 | 0 | 1.4365 | 0 | 0.0018315 | 1.4365 | 84146 | 7.411 | 84145.9982
38925.5748 | 2 | 0 | 38925.5748 | 2511 | 1 | 1902.5 | 1977.5 | 0.1221 | 0 | 153.2967 | 0.06105 | 0.001221 | 0 | 1.533 | 0.0006105 | 0.001221 | 1.5324 | 126269 | 0.69243 | 126268.9988
38925.5755 | 3 | 0 | 38925.5755 | 2318 | 0 | 1961.5 | 2036.5 | 0.18315 | 0 | 141.514 | 0 | 0.0018315 | 0 | 1.4151 | 0 | 0.0018315 | 1.4151 | 84146 | 9.0328 | 84145.9982
38925.5762 | 2 | 0 | 38925.5762 | 1947 | 0 | 2020 | 2095 | 0.1221 | 0 | 118.8645 | 0 | 0.001221 | 0 | 1.1886 | 0 | 0.001221 | 1.1886 | 126269 | 29.8089 | 126268.9988

## C3-5
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38925.5523 | 1 | 0 | 38925.5523 | 1 | 0 | -40.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.553 | 1 | 0 | 38925.553 | 1 | 0 | 18.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5537 | 1 | 0 | 38925.5537 | 1 | 0 | 77.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5544 | 1 | 0 | 38925.5544 | 1 | 0 | 136 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.555 | 1 | 0 | 38925.5551 | 1 | 0 | 194.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5557 | 1 | 0 | 38925.5557 | 1 | 0 | 253.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5564 | 1 | 0 | 38925.5564 | 1 | 0 | 312.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5571 | 1 | 0 | 38925.5571 | 1 | 0 | 371 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5578 | 1 | 0 | 38925.5578 | 1 | 0 | 430 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5584 | 1 | 0 | 38925.5585 | 2 | 0 | 488.5 | 563.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5591 | 1 | 0 | 38925.5591 | 1 | 0 | 547.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5598 | 1 | 0 | 38925.5598 | 1 | 0 | 606.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5605 | 1 | 0 | 38925.5605 | 1 | 0 | 665 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5612 | 1 | 0 | 38925.5612 | 2 | 0 | 724 | 799 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5619 | 1 | 0 | 38925.5619 | 1 | 0 | 782.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5625 | 1 | 0 | 38925.5625 | 1 | 0 | 841.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5632 | 1 | 1 | 38925.5632 | 1 | 0 | 900.5 | 975.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5639 | 1 | 0 | 38925.5639 | 1 | 0 | 959 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5646 | 1 | 0 | 38925.5646 | 1 | 0 | 1018 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5653 | 1 | 0 | 38925.5653 | 1 | 0 | 1076.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5659 | 1 | 0 | 38925.5659 | 1 | 0 | 1135.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5666 | 1 | 0 | 38925.5666 | 1 | 0 | 1194.5 | 1269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5673 | 1 | 0 | 38925.5673 | 1 | 0 | 1253 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.568 | 1 | 0 | 38925.568 | 1 | 0 | 1312 | 1387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5687 | 1 | 0 | 38925.5687 | 1 | 0 | 1370.5 | 1445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5693 | 1 | 0 | 38925.5694 | 1 | 0 | 1429.5 | 1504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.57 | 1 | 0 | 38925.57 | 1 | 0 | 1488 | 1563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5707 | 1 | 0 | 38925.5707 | 1 | 0 | 1547 | 1622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5714 | 1 | 0 | 38925.5714 | 1 | 0 | 1605.5 | 1680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5721 | 2 | 0 | 38925.5721 | 2 | 0 | 1664.5 | 1739.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38925.5727 | 2 | 0 | 38925.5728 | 2 | 0 | 1723.5 | 1798.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38925.5734 | 3 | 0 | 38925.5734 | 2 | 0 | 1782 | 1857 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38925.5741 | 3 | 0 | 38925.5741 | 3 | 0 | 1841 | 1916 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5748 | 3 | 0 | 38925.5748 | 3 | 0 | 1899.5 | 1974.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5755 | 3 | 0 | 38925.5755 | 3 | 0 | 1958.5 | 2033.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5761 | 3 | 0 | 38925.5762 | 3 | 0 | 2017.5 | 2092.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## C3-4
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38925.5523 | 1 | 0 | 38925.5523 | 1 | 0 | -43 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.553 | 1 | 0 | 38925.553 | 1 | 0 | 15.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5537 | 1 | 0 | 38925.5537 | 1 | 0 | 74.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5543 | 1 | 0 | 38925.5544 | 1 | 0 | 133.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.555 | 1 | 0 | 38925.555 | 1 | 0 | 192 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5557 | 1 | 0 | 38925.5557 | 1 | 0 | 251 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5564 | 1 | 0 | 38925.5564 | 1 | 0 | 309.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5571 | 1 | 0 | 38925.5571 | 1 | 0 | 368.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5577 | 1 | 0 | 38925.5578 | 1 | 0 | 427.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5584 | 1 | 0 | 38925.5584 | 1 | 0 | 486 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5591 | 1 | 0 | 38925.5591 | 1 | 0 | 544.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5598 | 1 | 0 | 38925.5598 | 1 | 0 | 603.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5605 | 1 | 0 | 38925.5605 | 1 | 0 | 662.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5611 | 1 | 0 | 38925.5612 | 1 | 0 | 721 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5618 | 1 | 0 | 38925.5618 | 1 | 0 | 780 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5625 | 1 | 0 | 38925.5625 | 1 | 0 | 838.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5632 | 1 | 0 | 38925.5632 | 1 | 0 | 897.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5639 | 1 | 0 | 38925.5639 | 1 | 0 | 956.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5645 | 1 | 0 | 38925.5646 | 1 | 0 | 1015 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5652 | 1 | 0 | 38925.5652 | 1 | 0 | 1073.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5659 | 1 | 0 | 38925.5659 | 1 | 0 | 1132.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5666 | 1 | 0 | 38925.5666 | 1 | 0 | 1191.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5673 | 1 | 0 | 38925.5673 | 1 | 0 | 1250.5 | 1325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5679 | 1 | 0 | 38925.568 | 1 | 0 | 1309 | 1384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5686 | 1 | 0 | 38925.5686 | 1 | 0 | 1367.5 | 1442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5693 | 1 | 0 | 38925.5693 | 1 | 0 | 1426.5 | 1501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.57 | 1 | 0 | 38925.57 | 1 | 0 | 1485.5 | 1560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5707 | 1 | 0 | 38925.5707 | 1 | 0 | 1544.5 | 1619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5713 | 1 | 0 | 38925.5714 | 1 | 0 | 1603 | 1678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.572 | 4 | 0 | 38925.572 | 2 | 0 | 1662 | 1737 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 52725.5 | 105551 | 52725.4976
38925.5727 | 3 | 0 | 38925.5727 | 3 | 0 | 1720.5 | 1795.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5734 | 4 | 0 | 38925.5734 | 3 | 0 | 1779.5 | 1854.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5741 | 4 | 0 | 38925.5741 | 3 | 0 | 1838 | 1913 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
| 4 | 0 | 38925.5748 | 3 | 0 | 1898 | 1973 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5754 | 3 | 0 | 38925.5754 | 4 | 0 | 1955.5 | 2030.5 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 70334 | 52725.5 | 70333.9982
38925.5761 | 4 | 0 | 38925.5761 | 3 | 0 | 2014.5 | 2089.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976

## C2-7
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38925.5523 | 1 | 0 | 38925.5523 | 1 | 0 | -46 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5529 | 1 | 0 | 38925.553 | 1 | 0 | 13 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5536 | 1 | 0 | 38925.5536 | 1 | 0 | 71.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5543 | 1 | 0 | 38925.5543 | 1 | 0 | 130.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.555 | 1 | 0 | 38925.555 | 1 | 0 | 189.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5557 | 1 | 0 | 38925.5557 | 1 | 0 | 248 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5563 | 1 | 0 | 38925.5564 | 1 | 0 | 306.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.557 | 1 | 0 | 38925.557 | 1 | 0 | 365.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5577 | 1 | 0 | 38925.5577 | 2 | 0 | 424.5 | 499.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5584 | 1 | 0 | 38925.5584 | 1 | 0 | 483 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5591 | 1 | 0 | 38925.5591 | 1 | 0 | 542 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5597 | 1 | 1 | 38925.5598 | 1 | 0 | 600.5 | 675.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5604 | 1 | 0 | 38925.5604 | 1 | 0 | 659.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5611 | 1 | 0 | 38925.5611 | 1 | 0 | 718.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5618 | 1 | 0 | 38925.5618 | 1 | 0 | 777 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5625 | 1 | 0 | 38925.5625 | 2 | 0 | 836 | 911 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5631 | 1 | 0 | 38925.5632 | 1 | 0 | 894.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5638 | 1 | 0 | 38925.5638 | 1 | 0 | 953.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5645 | 1 | 0 | 38925.5645 | 1 | 0 | 1012.5 | 1087.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5652 | 1 | 0 | 38925.5652 | 1 | 0 | 1071 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5659 | 1 | 0 | 38925.5659 | 1 | 0 | 1129.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5666 | 1 | 0 | 38925.5666 | 1 | 0 | 1188.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5672 | 1 | 0 | 38925.5672 | 1 | 0 | 1247.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5679 | 1 | 0 | 38925.5679 | 2 | 0 | 1306 | 1381 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5686 | 1 | 0 | 38925.5686 | 1 | 0 | 1365 | 1440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5693 | 1 | 0 | 38925.5693 | 1 | 0 | 1423.5 | 1498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.57 | 1 | 0 | 38925.57 | 1 | 0 | 1482.5 | 1557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5706 | 1 | 0 | 38925.5706 | 1 | 0 | 1541.5 | 1616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5713 | 1 | 0 | 38925.5713 | 1 | 0 | 1600 | 1675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.572 | 7 | 0 | 38925.572 | 6 | 0 | 1659 | 1734 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 30086 | 35117 | 30085.9957
38925.5727 | 7 | 0 | 38925.5727 | 5 | 0 | 1717.5 | 1792.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5734 | 7 | 0 | 38925.5734 | 5 | 0 | 1776.5 | 1851.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.574 | 8 | 0 | 38925.5741 | 6 | 0 | 1835.5 | 1910.5 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 26312.75 | 35117 | 26312.7451
38925.5747 | 7 | 0 | 38925.5747 | 5 | 0 | 1894 | 1969 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5754 | 7 | 0 | 38925.5754 | 5 | 0 | 1953 | 2028 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5761 | 7 | 0 | 38925.5761 | 5 | 0 | 2011.5 | 2086.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957

## C2-6
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 141.8425 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38925.5522 | 1 | 0 | 38925.5522 | 1 | 0 | -48.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5529 | 1 | 0 | 38925.5529 | 1 | 0 | 10 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5536 | 1 | 0 | 38925.5536 | 1 | 0 | 69 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5543 | 1 | 0 | 38925.5543 | 1 | 0 | 127.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.555 | 1 | 0 | 38925.555 | 1 | 0 | 186.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5556 | 1 | 0 | 38925.5556 | 1 | 0 | 245.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5563 | 1 | 0 | 38925.5563 | 1 | 0 | 304 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.557 | 1 | 0 | 38925.557 | 1 | 0 | 362.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5577 | 1 | 0 | 38925.5577 | 1 | 0 | 421.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5584 | 1 | 0 | 38925.5584 | 1 | 0 | 480.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.559 | 1 | 0 | 38925.5591 | 1 | 0 | 539 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5597 | 1 | 0 | 38925.5597 | 1 | 0 | 598 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5604 | 1 | 0 | 38925.5604 | 1 | 0 | 656.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5611 | 1 | 0 | 38925.5611 | 1 | 0 | 715.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5618 | 1 | 0 | 38925.5618 | 1 | 0 | 774.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5624 | 1 | 0 | 38925.5625 | 1 | 0 | 833 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5631 | 1 | 0 | 38925.5631 | 1 | 0 | 892 | 967 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5638 | 1 | 0 | 38925.5638 | 1 | 0 | 950.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5645 | 1 | 0 | 38925.5645 | 1 | 0 | 1009.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5652 | 1 | 0 | 38925.5652 | 1 | 0 | 1068 | 1143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5658 | 1 | 0 | 38925.5659 | 1 | 0 | 1127 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5665 | 1 | 0 | 38925.5665 | 1 | 0 | 1186 | 1261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5672 | 1 | 0 | 38925.5672 | 1 | 0 | 1244.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5679 | 1 | 0 | 38925.5679 | 1 | 0 | 1303.5 | 1378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5686 | 1 | 0 | 38925.5686 | 1 | 0 | 1362.5 | 1437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5692 | 1 | 0 | 38925.5693 | 1 | 0 | 1421 | 1496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5699 | 1 | 0 | 38925.5699 | 1 | 0 | 1479.5 | 1554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5706 | 1 | 0 | 38925.5706 | 1 | 0 | 1538.5 | 1613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.5713 | 1 | 0 | 38925.5713 | 1 | 0 | 1597.5 | 1672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38925.572 | 1 | 0 | 38925.572 | 2307 | 0 | 1656 | 1731 | 0.06105 | 0 | 140.8425 | 0 | 0.0006105 | 0 | 1.4084 | 0 | 0.0006105 | 1.4084 | 232238 | 0.71001 | 232237.9994
38925.5726 | 2 | 0 | 38925.5727 | 2009 | 0 | 1715 | 1790 | 0.1221 | 0 | 122.6496 | 0 | 0.001221 | 0 | 1.2265 | 0 | 0.001221 | 1.2265 | 116069 | 15.6486 | 116068.9988
38925.5733 | 2 | 0 | 38925.5733 | 2258 | 0 | 1773.5 | 1848.5 | 0.1221 | 0 | 137.851 | 0 | 0.001221 | 0 | 1.3785 | 0 | 0.001221 | 1.3785 | 116069 | 2.8955 | 116068.9988
38925.574 | 3 | 0 | 38925.574 | 1943 | 0 | 1832.5 | 1907.5 | 0.18315 | 0 | 118.6203 | 0 | 0.0018315 | 0 | 1.1862 | 0 | 0.0018315 | 1.1862 | 77346 | 19.5769 | 77345.9982
38925.5747 | 3 | 0 | 38925.5747 | 2077 | 0 | 1891.5 | 1966.5 | 0.18315 | 0 | 126.801 | 0 | 0.0018315 | 0 | 1.268 | 0 | 0.0018315 | 1.268 | 77346 | 11.8623 | 77345.9982
38925.5754 | 3 | 0 | 38925.5754 | 2150 | 0 | 1950 | 2025 | 0.18315 | 0 | 131.2576 | 0 | 0.0018315 | 0 | 1.3126 | 0 | 0.0018315 | 1.3126 | 77346 | 8.0642 | 77345.9982
38925.576 | 2 | 0 | 38925.5761 | 2054 | 0 | 2009 | 2084 | 0.1221 | 0 | 125.3968 | 0 | 0.001221 | 0 | 1.254 | 0 | 0.001221 | 1.254 | 116069 | 13.1149 | 116068.9988

## C2-5
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38925.5522 | 1 | 0 | 38925.5522 | 1 | 0 | -51.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5529 | 1 | 0 | 38925.5529 | 1 | 0 | 7.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5536 | 1 | 0 | 38925.5536 | 1 | 0 | 66 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5542 | 1 | 0 | 38925.5542 | 1 | 0 | 124.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5549 | 1 | 0 | 38925.5549 | 1 | 0 | 183.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5556 | 1 | 0 | 38925.5556 | 1 | 0 | 242.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5563 | 1 | 2 | 38925.5563 | 1 | 0 | 301 | 376 | 0.06105 | 0.1221 | 0.06105 | 0 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211402.1896 | 211202 | 105451.071
38925.557 | 1 | 0 | 38925.557 | 1 | 0 | 360 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5576 | 1 | 0 | 38925.5577 | 1 | 0 | 418.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5583 | 1 | 0 | 38925.5583 | 1 | 0 | 477.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.559 | 1 | 0 | 38925.559 | 1 | 0 | 536.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5597 | 1 | 0 | 38925.5597 | 1 | 0 | 595 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5604 | 1 | 0 | 38925.5604 | 1 | 0 | 654 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.561 | 1 | 0 | 38925.5611 | 1 | 0 | 712.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5617 | 1 | 0 | 38925.5617 | 1 | 0 | 771.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5624 | 1 | 0 | 38925.5624 | 1 | 0 | 830.5 | 905.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5631 | 1 | 0 | 38925.5631 | 1 | 0 | 889 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5638 | 1 | 0 | 38925.5638 | 1 | 0 | 948 | 1023 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5644 | 1 | 0 | 38925.5645 | 1 | 0 | 1006.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5651 | 1 | 0 | 38925.5651 | 1 | 0 | 1065.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5658 | 1 | 0 | 38925.5658 | 1 | 0 | 1124.5 | 1199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5665 | 1 | 0 | 38925.5665 | 1 | 0 | 1183 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5672 | 1 | 1 | 38925.5672 | 1 | 0 | 1242 | 1317 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5678 | 1 | 0 | 38925.5679 | 1 | 0 | 1300.5 | 1375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5685 | 1 | 0 | 38925.5685 | 1 | 0 | 1359.5 | 1434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5692 | 1 | 0 | 38925.5692 | 1 | 0 | 1418.5 | 1493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38925.5699 | 1 | 0 | 1478 | 1553 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5706 | 1 | 0 | 38925.5706 | 1 | 0 | 1535.5 | 1610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5713 | 1 | 0 | 38925.5713 | 1 | 0 | 1594.5 | 1669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5719 | 2 | 0 | 38925.5719 | 1 | 0 | 1653.5 | 1728.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5726 | 3 | 0 | 38925.5726 | 2 | 0 | 1712 | 1787 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38925.5733 | 3 | 0 | 38925.5733 | 2 | 0 | 1771 | 1846 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38925.574 | 3 | 0 | 38925.574 | 2 | 0 | 1829.5 | 1904.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38925.5747 | 2 | 0 | 38925.5747 | 3 | 0 | 1888.5 | 1963.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38925.5753 | 3 | 0 | 38925.5753 | 3 | 0 | 1947.5 | 2022.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.576 | 2 | 0 | 38925.576 | 3 | 0 | 2006 | 2081 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988

## C2-4
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38925.5522 | 1 | 0 | 38925.5522 | 1 | 0 | -54.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5528 | 1 | 0 | 38925.5529 | 1 | 0 | 4.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5535 | 1 | 1 | 38925.5535 | 2 | 0 | 63.5 | 138.5 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 222925823.02 | 105551 | 210902.1893
38925.5542 | 1 | 0 | 38925.5542 | 1 | 0 | 122 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5549 | 1 | 0 | 38925.5549 | 1 | 0 | 181 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5556 | 1 | 1 | 38925.5556 | 1 | 0 | 239.5 | 314.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5563 | 1 | 1 | 38925.5563 | 1 | 0 | 298.5 | 373.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5569 | 1 | 0 | 38925.5569 | 1 | 0 | 357 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5576 | 1 | 0 | 38925.5576 | 1 | 0 | 416 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5583 | 1 | 0 | 38925.5583 | 1 | 0 | 474.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.559 | 1 | 0 | 38925.559 | 1 | 0 | 533.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5597 | 1 | 0 | 38925.5597 | 1 | 0 | 592.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5603 | 1 | 0 | 38925.5603 | 1 | 0 | 651 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.561 | 1 | 0 | 38925.561 | 1 | 0 | 710 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5617 | 2 | 0 | 38925.5617 | 1 | 0 | 768.5 | 843.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5624 | 1 | 0 | 38925.5624 | 1 | 0 | 827.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5631 | 1 | 0 | 38925.5631 | 1 | 0 | 886.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5637 | 1 | 0 | 38925.5638 | 1 | 0 | 945 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5644 | 1 | 0 | 38925.5644 | 1 | 0 | 1004 | 1079 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5651 | 1 | 0 | 38925.5651 | 1 | 0 | 1062.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5658 | 1 | 0 | 38925.5658 | 1 | 0 | 1121.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5665 | 1 | 0 | 38925.5665 | 1 | 0 | 1180.5 | 1255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5671 | 1 | 0 | 38925.5672 | 1 | 0 | 1239 | 1314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5678 | 1 | 0 | 38925.5678 | 1 | 0 | 1298 | 1373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5685 | 1 | 0 | 38925.5685 | 1 | 0 | 1356.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5692 | 1 | 0 | 38925.5692 | 1 | 0 | 1415.5 | 1490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5698 | 1 | 0 | 38925.5699 | 1 | 0 | 1474 | 1549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5705 | 1 | 0 | 38925.5706 | 1 | 0 | 1533 | 1608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5712 | 1 | 0 | 38925.5712 | 1 | 0 | 1592 | 1667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5719 | 2 | 0 | 38925.5719 | 2 | 0 | 1650.5 | 1725.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38925.5726 | 3 | 0 | 38925.5726 | 3 | 0 | 1709.5 | 1784.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5733 | 3 | 0 | 38925.5733 | 3 | 0 | 1768 | 1843 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5739 | 3 | 0 | 38925.574 | 3 | 0 | 1827 | 1902 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5746 | 3 | 0 | 38925.5746 | 3 | 0 | 1885.5 | 1960.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5753 | 3 | 0 | 38925.5753 | 3 | 0 | 1944.5 | 2019.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.576 | 3 | 0 | 38925.576 | 3 | 0 | 2003.5 | 2078.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## C2-3
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38925.5521 | 1 | 0 | 38925.5522 | 1 | 0 | -57 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5528 | 1 | 0 | 38925.5528 | 1 | 0 | 1.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5535 | 1 | 0 | 38925.5535 | 1 | 0 | 60.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5542 | 1 | 0 | 38925.5542 | 1 | 0 | 119 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5548 | 1 | 0 | 38925.5549 | 1 | 0 | 178 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5555 | 1 | 0 | 38925.5556 | 1 | 0 | 237 | 312 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5562 | 1 | 0 | 38925.5562 | 1 | 0 | 295.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5569 | 1 | 0 | 38925.5569 | 1 | 0 | 354.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5576 | 1 | 0 | 38925.5576 | 1 | 0 | 413 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5583 | 2 | 0 | 38925.5583 | 1 | 0 | 472 | 547 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5589 | 1 | 0 | 38925.5589 | 1 | 0 | 530.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5596 | 1 | 0 | 38925.5596 | 1 | 0 | 589.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5603 | 1 | 0 | 38925.5603 | 1 | 0 | 648.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.561 | 1 | 0 | 38925.561 | 1 | 0 | 707 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5617 | 1 | 0 | 38925.5617 | 1 | 0 | 766 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5623 | 1 | 0 | 38925.5623 | 1 | 0 | 824.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.563 | 1 | 0 | 38925.563 | 1 | 0 | 883.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5637 | 1 | 0 | 38925.5637 | 2 | 0 | 942.5 | 1017.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5644 | 1 | 0 | 38925.5644 | 1 | 0 | 1001 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5651 | 1 | 0 | 38925.5651 | 1 | 0 | 1060 | 1135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5657 | 1 | 0 | 38925.5658 | 1 | 0 | 1118.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5664 | 1 | 0 | 38925.5664 | 1 | 0 | 1177.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5671 | 1 | 0 | 38925.5671 | 1 | 0 | 1236.5 | 1311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5678 | 1 | 0 | 38925.5678 | 1 | 0 | 1295 | 1370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5685 | 1 | 0 | 38925.5685 | 1 | 0 | 1354 | 1429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5691 | 1 | 0 | 38925.5692 | 1 | 0 | 1412.5 | 1487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5698 | 1 | 0 | 38925.5698 | 1 | 0 | 1471.5 | 1546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5705 | 1 | 0 | 38925.5705 | 1 | 0 | 1530 | 1605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5712 | 1 | 0 | 38925.5712 | 1 | 0 | 1589 | 1664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5719 | 6 | 0 | 38925.5719 | 3 | 0 | 1647.5 | 1722.5 | 0.3663 | 0 | 0.18315 | 0 | 0.003663 | 0 | 0.0018315 | 0 | 0.003663 | 0.0018315 | 35117 | 70334 | 35116.9963
38925.5725 | 4 | 0 | 38925.5726 | 3 | 0 | 1706.5 | 1781.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5732 | 4 | 0 | 38925.5732 | 3 | 0 | 1765.5 | 1840.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5739 | 4 | 0 | 38925.5739 | 3 | 0 | 1824 | 1899 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5746 | 4 | 0 | 38925.5746 | 3 | 0 | 1883 | 1958 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5753 | 5 | 0 | 38925.5753 | 4 | 0 | 1941.5 | 2016.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38925.5759 | 4 | 0 | 38925.576 | 4 | 0 | 2000.5 | 2075.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## C1-7
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38925.5521 | 1 | 0 | 38925.5521 | 2 | 0 | -60 | 15 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5528 | 1 | 0 | 38925.5528 | 1 | 0 | -1.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5535 | 1 | 0 | 38925.5535 | 1 | 0 | 57.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5541 | 1 | 0 | 38925.5542 | 1 | 0 | 116.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5548 | 1 | 0 | 38925.5548 | 1 | 0 | 175.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5555 | 1 | 0 | 38925.5555 | 1 | 0 | 234 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5562 | 1 | 1 | 38925.5562 | 1 | 0 | 293 | 368 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5569 | 1 | 0 | 38925.5569 | 1 | 0 | 351.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5575 | 1 | 0 | 38925.5576 | 1 | 0 | 410.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5582 | 1 | 0 | 38925.5582 | 1 | 0 | 469 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5589 | 1 | 0 | 38925.5589 | 1 | 0 | 528 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5596 | 1 | 0 | 38925.5596 | 1 | 0 | 586.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5603 | 1 | 0 | 38925.5603 | 1 | 0 | 645.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5609 | 1 | 0 | 38925.561 | 1 | 0 | 704.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5616 | 1 | 0 | 38925.5616 | 1 | 0 | 763 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5623 | 1 | 0 | 38925.5623 | 1 | 0 | 822 | 897 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.563 | 1 | 0 | 38925.563 | 1 | 0 | 880.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5637 | 1 | 0 | 38925.5637 | 1 | 0 | 939.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5644 | 1 | 0 | 38925.5644 | 1 | 0 | 998.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.565 | 1 | 0 | 38925.565 | 1 | 0 | 1057 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5657 | 1 | 0 | 38925.5657 | 1 | 0 | 1116 | 1191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5664 | 1 | 0 | 38925.5664 | 1 | 0 | 1174.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5671 | 1 | 0 | 38925.5671 | 1 | 0 | 1233.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5678 | 1 | 0 | 38925.5678 | 1 | 0 | 1292.5 | 1367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5684 | 1 | 0 | 38925.5684 | 1 | 0 | 1351 | 1426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5691 | 1 | 0 | 38925.5691 | 1 | 0 | 1409.5 | 1484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5698 | 1 | 0 | 38925.5698 | 1 | 0 | 1468.5 | 1543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5705 | 1 | 0 | 38925.5705 | 1 | 0 | 1527.5 | 1602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5712 | 1 | 0 | 38925.5712 | 1 | 0 | 1586.5 | 1661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5718 | 7 | 0 | 38925.5719 | 5 | 0 | 1645 | 1720 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5725 | 7 | 0 | 38925.5725 | 5 | 0 | 1703.5 | 1778.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5732 | 7 | 0 | 38925.5732 | 5 | 0 | 1762.5 | 1837.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5739 | 7 | 0 | 38925.5739 | 5 | 0 | 1821.5 | 1896.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5745 | 8 | 0 | 38925.5746 | 5 | 0 | 1880 | 1955 | 0.4884 | 0 | 0.30525 | 0 | 0.004884 | 0 | 0.0030525 | 0 | 0.004884 | 0.0030525 | 26312.75 | 42160.4 | 26312.7451
38925.5752 | 8 | 0 | 38925.5753 | 5 | 0 | 1939 | 2014 | 0.4884 | 0 | 0.30525 | 0 | 0.004884 | 0 | 0.0030525 | 0 | 0.004884 | 0.0030525 | 26312.75 | 42160.4 | 26312.7451
38925.5759 | 7 | 0 | 38925.5759 | 5 | 0 | 1997.5 | 2072.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957

## C1-6
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 153.9304 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38925.5521 | 1 | 0 | 38925.5521 | 1 | 0 | -63 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5527 | 1 | 0 | 38925.5528 | 1 | 0 | -4 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5534 | 1 | 0 | 38925.5534 | 1 | 0 | 55 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5541 | 1 | 1 | 38925.5541 | 1 | 0 | 113.5 | 188.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 635231534.44 | 252038 | 251838.0793
38925.5548 | 1 | 0 | 38925.5548 | 1 | 0 | 172.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5555 | 1 | 0 | 38925.5555 | 2 | 0 | 231 | 306 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252038 | 125969 | 252037.9994
38925.5561 | 1 | 0 | 38925.5562 | 1 | 0 | 290 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5568 | 1 | 0 | 38925.5568 | 2 | 0 | 348.5 | 423.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252038 | 125969 | 252037.9994
38925.5575 | 1 | 0 | 38925.5575 | 1 | 0 | 407.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5582 | 1 | 0 | 38925.5582 | 1 | 0 | 466.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5589 | 1 | 0 | 38925.5589 | 1 | 0 | 525 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5595 | 1 | 0 | 38925.5596 | 1 | 0 | 584 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5602 | 1 | 0 | 38925.5602 | 1 | 0 | 642.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5609 | 1 | 0 | 38925.5609 | 1 | 0 | 701.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5616 | 1 | 0 | 38925.5616 | 1 | 0 | 760.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5623 | 1 | 0 | 38925.5623 | 1 | 0 | 819 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.563 | 1 | 0 | 38925.563 | 1 | 0 | 878 | 953 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5636 | 1 | 0 | 38925.5636 | 1 | 0 | 936.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5643 | 1 | 0 | 38925.5643 | 1 | 0 | 995.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.565 | 1 | 0 | 38925.565 | 1 | 0 | 1054.5 | 1129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5657 | 1 | 0 | 38925.5657 | 1 | 0 | 1113 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5664 | 1 | 0 | 38925.5664 | 1 | 0 | 1172 | 1247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.567 | 1 | 0 | 38925.567 | 1 | 0 | 1230.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5677 | 1 | 0 | 38925.5677 | 1 | 0 | 1289.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5684 | 1 | 0 | 38925.5684 | 1 | 0 | 1348 | 1423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5691 | 1 | 0 | 38925.5691 | 1 | 0 | 1407 | 1482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5698 | 1 | 0 | 38925.5698 | 1 | 0 | 1465.5 | 1540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5704 | 1 | 0 | 38925.5705 | 1 | 0 | 1524.5 | 1599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5711 | 1 | 0 | 38925.5711 | 1 | 0 | 1583.5 | 1658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38925.5718 | 1 | 0 | 38925.5718 | 2309 | 0 | 1642.5 | 1717.5 | 0.06105 | 0 | 140.9646 | 0 | 0.0006105 | 0 | 1.4096 | 0 | 0.0006105 | 1.4096 | 252038 | 9.1979 | 252037.9994
38925.5725 | 2 | 0 | 38925.5725 | 1964 | 0 | 1701 | 1776 | 0.1221 | 0 | 119.9023 | 0 | 0.001221 | 0 | 1.199 | 0 | 0.001221 | 1.199 | 125969 | 28.3798 | 125968.9988
38925.5732 | 3 | 0 | 38925.5732 | 2505 | 0 | 1759.5 | 1834.5 | 0.18315 | 0 | 152.9304 | 0 | 0.0018315 | 0 | 1.5293 | 0 | 0.0018315 | 1.5293 | 83946 | 0.65389 | 83945.9982
38925.5738 | 3 | 0 | 38925.5739 | 2163 | 0 | 1818.5 | 1893.5 | 0.18315 | 0 | 132.0513 | 0 | 0.0018315 | 0 | 1.3205 | 0 | 0.0018315 | 1.3205 | 83946 | 16.5687 | 83945.9982
38925.5745 | 3 | 0 | 38925.5745 | 2392 | 0 | 1877.5 | 1952.5 | 0.18315 | 0 | 146.0317 | 0 | 0.0018315 | 0 | 1.4603 | 0 | 0.0018315 | 1.4603 | 83946 | 5.4089 | 83945.9982
38925.5752 | 2 | 0 | 38925.5752 | 2085 | 0 | 1936 | 2011 | 0.1221 | 0 | 127.2894 | 0 | 0.001221 | 0 | 1.2729 | 0 | 0.001221 | 1.2729 | 125969 | 20.9295 | 125968.9988
38925.5759 | 3 | 0 | 38925.5759 | 2240 | 0 | 1995 | 2070 | 0.18315 | 0 | 136.7521 | 0 | 0.0018315 | 0 | 1.3675 | 0 | 0.0018315 | 1.3675 | 83946 | 12.5616 | 83945.9982

## C1-5
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38925.552 | 1 | 0 | 38925.552 | 1 | 0 | -65.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5527 | 1 | 0 | 38925.5527 | 2 | 0 | -7 | 68 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5534 | 1 | 0 | 38925.5534 | 1 | 0 | 52 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5541 | 1 | 0 | 38925.5541 | 2 | 0 | 111 | 186 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5548 | 1 | 0 | 38925.5548 | 1 | 0 | 169.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5554 | 1 | 0 | 38925.5555 | 1 | 0 | 228.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5561 | 1 | 0 | 38925.5561 | 1 | 0 | 287 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5568 | 1 | 0 | 38925.5568 | 1 | 0 | 346 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5575 | 1 | 0 | 38925.5575 | 1 | 0 | 404.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5582 | 1 | 0 | 38925.5582 | 1 | 0 | 463.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5588 | 1 | 0 | 38925.5589 | 1 | 0 | 522.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5595 | 1 | 1 | 38925.5595 | 1 | 0 | 581 | 656 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.5602 | 1 | 0 | 38925.5602 | 1 | 0 | 640 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5609 | 1 | 0 | 38925.5609 | 1 | 0 | 698.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5616 | 1 | 0 | 38925.5616 | 1 | 0 | 757.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5622 | 1 | 0 | 38925.5623 | 1 | 0 | 816.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5629 | 1 | 0 | 38925.5629 | 1 | 0 | 875 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5636 | 1 | 0 | 38925.5636 | 1 | 0 | 934 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5643 | 1 | 0 | 38925.5643 | 1 | 0 | 992.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.565 | 1 | 0 | 38925.565 | 1 | 0 | 1051.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5656 | 1 | 0 | 38925.5657 | 1 | 0 | 1110.5 | 1185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5663 | 1 | 0 | 38925.5663 | 1 | 0 | 1169 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.567 | 1 | 0 | 38925.567 | 1 | 0 | 1227.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5677 | 1 | 0 | 38925.5677 | 1 | 0 | 1286.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5684 | 1 | 0 | 38925.5684 | 1 | 0 | 1345.5 | 1420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5691 | 1 | 0 | 38925.5691 | 1 | 0 | 1404.5 | 1479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5697 | 1 | 0 | 38925.5697 | 1 | 0 | 1463 | 1538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5704 | 1 | 0 | 38925.5704 | 1 | 0 | 1521.5 | 1596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5711 | 1 | 0 | 38925.5711 | 1 | 0 | 1580.5 | 1655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5718 | 1 | 0 | 38925.5718 | 1 | 0 | 1639.5 | 1714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5724 | 3 | 0 | 38925.5725 | 2 | 0 | 1698 | 1773 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38925.5731 | 3 | 0 | 38925.5731 | 3 | 0 | 1757 | 1832 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5738 | 3 | 0 | 38925.5738 | 3 | 0 | 1815.5 | 1890.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5745 | 3 | 0 | 38925.5745 | 3 | 0 | 1874.5 | 1949.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5752 | 3 | 0 | 38925.5752 | 3 | 0 | 1933.5 | 2008.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5758 | 3 | 0 | 38925.5759 | 3 | 0 | 1992 | 2067 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## C1-4
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38925.552 | 1 | 0 | 38925.552 | 1 | 0 | -68.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5527 | 2 | 0 | 38925.5527 | 1 | 0 | -9.5 | 65.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5534 | 1 | 0 | 38925.5534 | 1 | 0 | 49.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.554 | 1 | 0 | 38925.5541 | 1 | 0 | 108 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5547 | 1 | 0 | 38925.5547 | 1 | 0 | 167 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5554 | 1 | 0 | 38925.5554 | 1 | 0 | 225.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5561 | 1 | 0 | 38925.5561 | 1 | 0 | 284.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5568 | 2 | 0 | 38925.5568 | 1 | 0 | 343 | 418 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.5574 | 1 | 0 | 38925.5575 | 1 | 0 | 402 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5581 | 1 | 0 | 38925.5581 | 1 | 0 | 460.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5588 | 1 | 0 | 38925.5588 | 1 | 0 | 519.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5595 | 1 | 0 | 38925.5595 | 1 | 0 | 578.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5602 | 1 | 0 | 38925.5602 | 1 | 0 | 637 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5608 | 1 | 0 | 38925.5609 | 1 | 0 | 696 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5615 | 1 | 0 | 38925.5615 | 1 | 0 | 754.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5622 | 1 | 0 | 38925.5622 | 1 | 0 | 813.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5629 | 1 | 0 | 38925.5629 | 1 | 0 | 872.5 | 947.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5636 | 1 | 0 | 38925.5636 | 1 | 0 | 931 | 1006 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5642 | 1 | 0 | 38925.5643 | 1 | 0 | 990 | 1065 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5649 | 1 | 0 | 38925.5649 | 1 | 0 | 1048.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5656 | 1 | 0 | 38925.5656 | 1 | 0 | 1107.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5663 | 1 | 0 | 38925.5663 | 1 | 0 | 1166.5 | 1241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.567 | 1 | 0 | 38925.567 | 1 | 0 | 1225 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5677 | 1 | 0 | 38925.5677 | 1 | 0 | 1284 | 1359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5683 | 1 | 0 | 38925.5683 | 1 | 0 | 1342.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.569 | 1 | 0 | 38925.569 | 1 | 0 | 1401.5 | 1476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5697 | 1 | 0 | 38925.5697 | 1 | 0 | 1460.5 | 1535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5704 | 1 | 0 | 38925.5704 | 1 | 0 | 1519 | 1594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5711 | 1 | 0 | 38925.5711 | 1 | 0 | 1578 | 1653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5717 | 1 | 0 | 38925.5717 | 1 | 0 | 1636.5 | 1711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5724 | 3 | 0 | 38925.5724 | 2 | 0 | 1695.5 | 1770.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38925.5731 | 3 | 0 | 38925.5731 | 3 | 0 | 1754 | 1829 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5738 | 3 | 0 | 38925.5738 | 3 | 0 | 1813 | 1888 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5745 | 3 | 0 | 38925.5745 | 3 | 0 | 1871.5 | 1946.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5751 | 3 | 0 | 38925.5752 | 3 | 0 | 1930.5 | 2005.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5758 | 4 | 0 | 38925.5758 | 3 | 0 | 1989.5 | 2064.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976

## C1-3
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38925.552 | 1 | 0 | 38925.552 | 1 | 0 | -71 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5527 | 1 | 0 | 38925.5527 | 1 | 0 | -12.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5533 | 1 | 0 | 38925.5533 | 2 | 0 | 46.5 | 121.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.554 | 1 | 0 | 38925.554 | 1 | 0 | 105.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5547 | 1 | 0 | 38925.5547 | 1 | 0 | 164 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5554 | 1 | 0 | 38925.5554 | 1 | 0 | 222.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5561 | 1 | 0 | 38925.5561 | 2 | 0 | 281.5 | 356.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.5567 | 1 | 0 | 38925.5567 | 1 | 0 | 340.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5574 | 1 | 0 | 38925.5574 | 1 | 0 | 399 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5581 | 1 | 0 | 38925.5581 | 1 | 0 | 458 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5588 | 1 | 0 | 38925.5588 | 1 | 0 | 517 | 592 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5595 | 1 | 0 | 38925.5595 | 1 | 0 | 575.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5601 | 1 | 0 | 38925.5602 | 1 | 0 | 634.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5608 | 1 | 0 | 38925.5608 | 1 | 0 | 693 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5615 | 1 | 0 | 38925.5615 | 1 | 0 | 752 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5622 | 1 | 0 | 38925.5622 | 1 | 0 | 810.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5629 | 1 | 0 | 38925.5629 | 1 | 0 | 869.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5635 | 1 | 0 | 38925.5636 | 1 | 0 | 928.5 | 1003.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5642 | 1 | 0 | 38925.5642 | 1 | 0 | 987 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5649 | 1 | 0 | 38925.5649 | 1 | 0 | 1046 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5656 | 1 | 0 | 38925.5656 | 1 | 0 | 1104.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5663 | 1 | 0 | 38925.5663 | 1 | 0 | 1163.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5669 | 1 | 0 | 38925.567 | 1 | 0 | 1222.5 | 1297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5676 | 1 | 0 | 38925.5676 | 1 | 0 | 1281 | 1356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5683 | 1 | 0 | 38925.5683 | 1 | 0 | 1340 | 1415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.569 | 1 | 0 | 38925.569 | 1 | 0 | 1398.5 | 1473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5697 | 1 | 0 | 38925.5697 | 1 | 0 | 1457.5 | 1532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5703 | 1 | 0 | 38925.5704 | 1 | 0 | 1516 | 1591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.571 | 1 | 0 | 38925.571 | 1 | 0 | 1575 | 1650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5717 | 1 | 0 | 38925.5717 | 1 | 0 | 1634 | 1709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5724 | 3 | 0 | 38925.5724 | 3 | 0 | 1692.5 | 1767.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38925.5731 | 4 | 0 | 38925.5731 | 3 | 0 | 1751.5 | 1826.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38925.5737 | 4 | 0 | 38925.5738 | 4 | 0 | 1810 | 1885 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38925.5744 | 4 | 0 | 38925.5744 | 4 | 0 | 1869 | 1944 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38925.5751 | 4 | 0 | 38925.5751 | 4 | 0 | 1927.5 | 2002.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38925.5758 | 4 | 0 | 38925.5758 | 4 | 0 | 1986.5 | 2061.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## C1-2
Penlight Test 31 |  |  | 2006-07-27 | 13:16 |  | Vs = |  | 129 |  | R = | 100
VitaLink | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38925.5519 | 1 | 0 | 38925.552 | 1 | 0 | -74 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5526 | 1 | 0 | 38925.5526 | 1 | 0 | -15.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5533 | 1 | 0 | 38925.5533 | 1 | 0 | 43.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.554 | 1 | 0 | 38925.554 | 1 | 0 | 102.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5547 | 1 | 0 | 38925.5547 | 1 | 0 | 161 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5553 | 1 | 0 | 38925.5554 | 1 | 0 | 220 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.556 | 1 | 0 | 38925.556 | 1 | 0 | 279 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5567 | 1 | 0 | 38925.5567 | 1 | 0 | 337.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5574 | 1 | 0 | 38925.5574 | 1 | 0 | 396.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5581 | 1 | 0 | 38925.5581 | 1 | 0 | 455 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5587 | 1 | 0 | 38925.5588 | 1 | 0 | 514 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5594 | 1 | 0 | 38925.5594 | 1 | 0 | 572.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5601 | 1 | 0 | 38925.5601 | 1 | 0 | 631.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5608 | 1 | 0 | 38925.5608 | 1 | 0 | 690.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5615 | 1 | 0 | 38925.5615 | 1 | 0 | 749 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5621 | 1 | 0 | 38925.5622 | 1 | 0 | 808 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5628 | 1 | 0 | 38925.5628 | 1 | 0 | 866.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5635 | 1 | 0 | 38925.5635 | 1 | 0 | 925.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5642 | 1 | 0 | 38925.5642 | 1 | 0 | 984.5 | 1059.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5649 | 1 | 0 | 38925.5649 | 1 | 0 | 1043 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5655 | 1 | 0 | 38925.5656 | 1 | 0 | 1102 | 1177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5662 | 1 | 0 | 38925.5662 | 1 | 0 | 1160.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5669 | 1 | 0 | 38925.5669 | 1 | 0 | 1219.5 | 1294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5676 | 1 | 0 | 38925.5676 | 1 | 0 | 1278.5 | 1353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5683 | 1 | 0 | 38925.5683 | 1 | 0 | 1337 | 1412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5689 | 1 | 0 | 38925.569 | 1 | 0 | 1396 | 1471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5696 | 1 | 0 | 38925.5696 | 1 | 0 | 1454.5 | 1529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5703 | 1 | 0 | 38925.5703 | 1 | 0 | 1513.5 | 1588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.571 | 1 | 0 | 38925.571 | 1 | 0 | 1572 | 1647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5717 | 1 | 0 | 38925.5717 | 1 | 0 | 1631 | 1706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.5723 | 6 | 0 | 38925.5724 | 5 | 0 | 1689.5 | 1764.5 | 0.3663 | 0 | 0.30525 | 0 | 0.003663 | 0 | 0.0030525 | 0 | 0.003663 | 0.0030525 | 35117 | 42160.4 | 35116.9963
38925.573 | 7 | 0 | 38925.573 | 5 | 0 | 1748.5 | 1823.5 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5737 | 6 | 0 | 38925.5737 | 4 | 0 | 1807.5 | 1882.5 | 0.3663 | 0 | 0.2442 | 0 | 0.003663 | 0 | 0.002442 | 0 | 0.003663 | 0.002442 | 35117 | 52725.5 | 35116.9963
38925.5744 | 7 | 0 | 38925.5744 | 5 | 0 | 1866 | 1941 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5751 | 7 | 0 | 38925.5751 | 5 | 0 | 1925 | 2000 | 0.42735 | 0 | 0.30525 | 0 | 0.0042735 | 0 | 0.0030525 | 0 | 0.0042735 | 0.0030525 | 30086 | 42160.4 | 30085.9957
38925.5758 | 7 | 0 | 38925.5758 | 6 | 0 | 1983.5 | 2058.5 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 30086 | 35117 | 30085.9957

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable | Tray Rung
0 | -75 | 23.7 | 31.9 | 24.9
1 | -74 | 23.7 | 31.9 | 24.8
2 | -73 | 23.7 | 31.9 | 24.8
3 | -72 | 23.7 | 32 | 24.8
4 | -71 | 23.7 | 32 | 24.8
5 | -70 | 23.7 | 32 | 24.8
6 | -69 | 23.7 | 32 | 24.8
7 | -68 | 23.7 | 32 | 24.8
8 | -67 | 23.7 | 32 | 24.8
9 | -66 | 23.7 | 32 | 24.8
10 | -65 | 23.7 | 32 | 24.8
11 | -64 | 23.7 | 32 | 24.8
12 | -63 | 23.7 | 32 | 24.8
13 | -62 | 23.7 | 32 | 24.8
14 | -61 | 23.7 | 32 | 24.8
15 | -60 | 23.7 | 31.9 | 24.8
16 | -59 | 23.7 | 32 | 24.8
17 | -58 | 23.7 | 32 | 24.8
18 | -57 | 23.7 | 32 | 24.8
19 | -56 | 23.7 | 31.9 | 24.8
20 | -55 | 23.7 | 31.9 | 24.8
21 | -54 | 23.7 | 31.9 | 24.8
22 | -53 | 23.7 | 31.9 | 24.8
23 | -52 | 23.7 | 32 | 24.8
24 | -51 | 23.7 | 32 | 24.8
25 | -50 | 23.7 | 32 | 24.8
26 | -49 | 23.7 | 32 | 24.8
27 | -48 | 23.7 | 32 | 24.8
28 | -47 | 23.7 | 32 | 24.8
29 | -46 | 23.7 | 32 | 24.8
30 | -45 | 23.7 | 32 | 24.8
31 | -44 | 23.7 | 32 | 24.8
32 | -43 | 23.7 | 32 | 24.8
33 | -42 | 23.7 | 32 | 24.7
34 | -41 | 23.7 | 32 | 24.8
35 | -40 | 23.7 | 32 | 24.8
36 | -39 | 23.7 | 32 | 24.8
37 | -38 | 23.7 | 32 | 24.8
38 | -37 | 23.7 | 32 | 24.8
39 | -36 | 23.7 | 32 | 24.7
40 | -35 | 23.7 | 32 | 24.7
41 | -34 | 23.7 | 32 | 24.7
42 | -33 | 23.7 | 32 | 24.8
43 | -32 | 23.7 | 32 | 24.7
44 | -31 | 23.7 | 32 | 24.7
45 | -30 | 23.7 | 32 | 24.7
46 | -29 | 23.7 | 32 | 24.8
47 | -28 | 23.7 | 32 | 24.7
48 | -27 | 23.7 | 32 | 24.7
49 | -26 | 23.6 | 32 | 24.7
50 | -25 | 23.7 | 32 | 24.8
51 | -24 | 23.7 | 32 | 24.7
52 | -23 | 23.6 | 32 | 24.7
53 | -22 | 23.6 | 32 | 24.7
54 | -21 | 23.6 | 32 | 24.7
55 | -20 | 23.6 | 32 | 24.7
56 | -19 | 23.6 | 32 | 24.7
57 | -18 | 23.6 | 32 | 24.8
58 | -17 | 23.6 | 32 | 24.7
59 | -16 | 23.6 | 32 | 24.7
60 | -15 | 23.6 | 32 | 24.7
61 | -14 | 23.6 | 32 | 24.7
62 | -13 | 23.6 | 32 | 24.7
63 | -12 | 23.6 | 31.9 | 24.7
64 | -11 | 23.6 | 32 | 24.7
65 | -10 | 23.6 | 31.9 | 24.7
66 | -9 | 23.6 | 31.9 | 24.7
67 | -8 | 23.6 | 32 | 24.7
68 | -7 | 23.6 | 31.9 | 24.7
69 | -6 | 23.6 | 31.9 | 24.7
70 | -5 | 23.6 | 32 | 24.7
71 | -4 | 23.6 | 31.9 | 24.7
72 | -3 | 23.6 | 32.5 | 23.5
73 | -2 | 23.6 | 33.5 | 21.4
74 | -1 | 23.7 | 33.9 | 20.7
75 | 0 | 24.2 | 33.9 | 20.7
76 | 1 | 25.4 | 33.9 | 20.7
77 | 2 | 27.4 | 33.9 | 20.8
78 | 3 | 29.8 | 33.7 | 21.1
79 | 4 | 32.8 | 33.9 | 20.7
80 | 5 | 36.1 | 33.9 | 20.7
81 | 6 | 39.8 | 33.9 | 20.8
82 | 7 | 43.7 | 33.9 | 20.8
83 | 8 | 47.8 | 33.9 | 20.9
84 | 9 | 52.2 | 34 | 20.8
85 | 10 | 56.6 | 34 | 20.9
86 | 11 | 61.2 | 34 | 21
87 | 12 | 66 | 34 | 21
88 | 13 | 70.9 | 34.1 | 21.1
89 | 14 | 75.9 | 34.1 | 21.1
90 | 15 | 81 | 34.2 | 21.2
91 | 16 | 86.2 | 34.2 | 21.3
92 | 17 | 91.5 | 34.3 | 21.4
93 | 18 | 96.9 | 34.4 | 21.5
94 | 19 | 102.2 | 34.4 | 21.7
95 | 20 | 107.6 | 34.5 | 21.8
96 | 21 | 113.1 | 34.6 | 21.9
97 | 22 | 118.6 | 34.6 | 22.1
98 | 23 | 124.2 | 34.7 | 22.3
99 | 24 | 129.8 | 34.9 | 22.4
100 | 25 | 135.3 | 35 | 22.6
101 | 26 | 140.9 | 35.1 | 22.9
102 | 27 | 146.5 | 35.3 | 23
103 | 28 | 152 | 35.4 | 23.3
104 | 29 | 157.7 | 35.6 | 23.5
105 | 30 | 163.5 | 35.7 | 23.8
106 | 31 | 169.1 | 35.9 | 24
107 | 32 | 174.7 | 36.1 | 24.4
108 | 33 | 180.3 | 36.3 | 24.7
109 | 34 | 185.8 | 36.5 | 25
110 | 35 | 191.3 | 36.7 | 25.4
111 | 36 | 196.9 | 36.9 | 25.7
112 | 37 | 202.5 | 37.1 | 26.1
113 | 38 | 208.2 | 37.4 | 26.5
114 | 39 | 213.9 | 37.7 | 26.8
115 | 40 | 219.7 | 38 | 27.3
116 | 41 | 225.4 | 38.2 | 27.8
117 | 42 | 231.1 | 38.5 | 28.2
118 | 43 | 236.9 | 38.8 | 28.7
119 | 44 | 242.6 | 39.2 | 29.2
120 | 45 | 248.2 | 39.5 | 29.8
121 | 46 | 253.9 | 39.8 | 30.3
122 | 47 | 259.5 | 40.2 | 30.9
123 | 48 | 265 | 40.6 | 31.5
124 | 49 | 270.6 | 41 | 32.1
125 | 50 | 276.1 | 41.4 | 32.8
126 | 51 | 281.5 | 41.8 | 33.5
127 | 52 | 287.2 | 42.2 | 34.2
128 | 53 | 292.7 | 42.6 | 34.9
129 | 54 | 298.2 | 43.1 | 35.7
130 | 55 | 303.7 | 43.6 | 36.5
131 | 56 | 309.2 | 44.1 | 37.4
132 | 57 | 314.6 | 44.6 | 38.2
133 | 58 | 319.9 | 45.1 | 39.1
134 | 59 | 325.2 | 45.7 | 39.9
135 | 60 | 330.5 | 46.3 | 40.9
136 | 61 | 335.8 | 46.8 | 41.9
137 | 62 | 341 | 47.4 | 42.9
138 | 63 | 346.1 | 48 | 43.9
139 | 64 | 351.2 | 48.7 | 44.9
140 | 65 | 356.5 | 49.3 | 46.1
141 | 66 | 361.9 | 49.9 | 47.2
142 | 67 | 367.2 | 50.6 | 48.4
143 | 68 | 372.1 | 51.3 | 49.6
144 | 69 | 377 | 52 | 50.8
145 | 70 | 381.8 | 52.7 | 52.1
146 | 71 | 386.7 | 53.5 | 53.4
147 | 72 | 391.5 | 54.2 | 54.8
148 | 73 | 396.4 | 55 | 56.2
149 | 74 | 401.2 | 55.8 | 57.5
150 | 75 | 405.9 | 56.6 | 59
151 | 76 | 410.7 | 57.5 | 60.5
152 | 77 | 415.7 | 58.3 | 62
153 | 78 | 420.6 | 59.3 | 63.6
154 | 79 | 425.4 | 60.2 | 65.2
155 | 80 | 430.1 | 61.3 | 66.8
156 | 81 | 434.6 | 62.4 | 68.5
157 | 82 | 439 | 63.5 | 70.2
158 | 83 | 443.5 | 64.7 | 72
159 | 84 | 448 | 65.9 | 73.7
160 | 85 | 452.7 | 67.2 | 75.6
161 | 86 | 457.2 | 68.5 | 77.5
162 | 87 | 461.6 | 69.9 | 79.5
163 | 88 | 466 | 71.3 | 81.4
164 | 89 | 470.3 | 72.8 | 83.5
165 | 90 | 474.6 | 74.3 | 85.5
166 | 91 | 478.9 | 75.8 | 87.6
167 | 92 | 483.3 | 77.4 | 89.7
168 | 93 | 487.4 | 79.1 | 91.9
169 | 94 | 491.4 | 80.8 | 94
170 | 95 | 495.4 | 82.5 | 96.3
171 | 96 | 499.5 | 84.2 | 98.6
172 | 97 | 503.4 | 86 | 100.9
173 | 98 | 507.4 | 87.7 | 103.3
174 | 99 | 511.4 | 89.5 | 105.6
175 | 100 | 515.3 | 91.3 | 108.1
176 | 101 | 518.9 | 93.1 | 110.6
177 | 102 | 522.7 | 94.8 | 113.1
178 | 103 | 526.5 | 96.6 | 115.7
179 | 104 | 530.1 | 98.4 | 118.3
180 | 105 | 533.9 | 100.2 | 120.9
181 | 106 | 537.5 | 102 | 123.6
182 | 107 | 541 | 103.8 | 126.3
183 | 108 | 544.6 | 105.6 | 129
184 | 109 | 548.1 | 107.4 | 131.8
185 | 110 | 551.6 | 109.3 | 134.6
186 | 111 | 554.9 | 111.2 | 137.4
187 | 112 | 558.3 | 113.1 | 140.3
188 | 113 | 561.6 | 115.1 | 143.1
189 | 114 | 565.1 | 117.1 | 146.1
190 | 115 | 568.4 | 119.2 | 149.1
191 | 116 | 571.6 | 121.3 | 152.1
192 | 117 | 574.6 | 123.5 | 155.2
193 | 118 | 577.6 | 125.6 | 158.2
194 | 119 | 580.6 | 127.8 | 161.3
195 | 120 | 583.5 | 130 | 164.5
196 | 121 | 586.4 | 132.2 | 167.7
197 | 122 | 589.3 | 134.5 | 170.9
198 | 123 | 592.3 | 136.7 | 174.2
199 | 124 | 595.3 | 138.9 | 177.5
200 | 125 | 598.1 | 141.2 | 180.8
201 | 126 | 601 | 143.5 | 184.2
202 | 127 | 603.9 | 145.7 | 187.6
203 | 128 | 606.7 | 147.9 | 191
204 | 129 | 609.6 | 150.2 | 194.5
205 | 130 | 612.3 | 152.4 | 197.9
206 | 131 | 615.1 | 154.6 | 201.5
207 | 132 | 617.8 | 156.8 | 205
208 | 133 | 620.6 | 159 | 208.5
209 | 134 | 623.2 | 161.2 | 212.2
210 | 135 | 625.8 | 163.3 | 215.8
211 | 136 | 628.3 | 165.5 | 219.5
212 | 137 | 630.8 | 167.6 | 223.1
213 | 138 | 633.4 | 169.8 | 226.9
214 | 139 | 636 | 172 | 230.6
215 | 140 | 638.5 | 174.2 | 234.4
216 | 141 | 640.9 | 176.5 | 238.1
217 | 142 | 643.2 | 178.8 | 242
218 | 143 | 645.8 | 181.1 | 245.8
219 | 144 | 648.5 | 183.5 | 249.6
220 | 145 | 650.9 | 185.9 | 253.5
221 | 146 | 653.3 | 187.5 | 258.7
222 | 147 | 655.8 | 190 | 262.6
223 | 148 | 658.1 | 192.4 | 266.4
224 | 149 | 660.1 | 194.9 | 270.2
225 | 150 | 661.9 | 197.3 | 274.1
226 | 151 | 663.6 | 200.1 | 277
227 | 152 | 665.3 | 203 | 279.9
228 | 153 | 666.8 | 205.5 | 283.4
229 | 154 | 668.3 | 207.9 | 287.2
230 | 155 | 670 | 210.3 | 291
231 | 156 | 671.6 | 212.8 | 294.7
232 | 157 | 673.1 | 215.1 | 298.4
233 | 158 | 674.4 | 217.4 | 302.1
234 | 159 | 675.7 | 219.6 | 305.7
235 | 160 | 677 | 221.7 | 309.4
236 | 161 | 678.5 | 223.8 | 313
237 | 162 | 680 | 225.7 | 316.9
238 | 163 | 681.6 | 226.8 | 322.2
239 | 164 | 683.2 | 228.8 | 325.8
240 | 165 | 684.7 | 230.8 | 329.2
241 | 166 | 686.3 | 232.7 | 332.8
242 | 167 | 687.7 | 234.5 | 336.4
243 | 168 | 689.1 | 236.7 | 339.1
244 | 169 | 690.4 | 238.9 | 342
245 | 170 | 691.5 | 240.3 | 346.4
246 | 171 | 692.4 | 242.1 | 349.8
247 | 172 | 693.1 | 243.7 | 353.1
248 | 173 | 693.7 | 244 | 356.6
249 | 174 | 694.2 | 243.8 | 360
250 | 175 | 694.7 | 243.4 | 363.5
251 | 176 | 695.1 | 242.1 | 367
252 | 177 | 695.2 | 240.5 | 370.5
253 | 178 | 695.4 | 239.6 | 372.8
254 | 179 | 695.7 | 238.7 | 376
255 | 180 | 696 | 238.3 | 379.6
256 | 181 | 696.4 | 238.6 | 383.2
257 | 182 | 696.9 | 239.1 | 387.4
258 | 183 | 697.2 | 240 | 391.9
259 | 184 | 697.5 | 241.5 | 395.6
260 | 185 | 697.8 | 243.2 | 399.3
261 | 186 | 698.2 | 245 | 402.8
262 | 187 | 698.7 | 247 | 406.5
263 | 188 | 699.1 | 249.3 | 410.1
264 | 189 | 699.7 | 252.1 | 413.6
265 | 190 | 700.3 | 255.2 | 417.3
266 | 191 | 700.7 | 258.2 | 420.9
267 | 192 | 701 | 260.8 | 424.5
268 | 193 | 701.2 | 263.3 | 428
269 | 194 | 701.3 | 265.3 | 431.4
270 | 195 | 701.4 | 266.8 | 434.9
271 | 196 | 701.3 | 268 | 438.2
272 | 197 | 701.3 | 268.7 | 441.6
273 | 198 | 701.3 | 269.2 | 444.9
274 | 199 | 701.1 | 269.7 | 448.3
275 | 200 | 701 | 270.2 | 451.7
276 | 201 | 700.7 | 270.8 | 455
277 | 202 | 700.5 | 271.5 | 458.3
278 | 203 | 700.3 | 272.1 | 461.6
279 | 204 | 700.2 | 273.5 | 465
280 | 205 | 700.2 | 275.3 | 468.2
281 | 206 | 700.3 | 277.2 | 471.5
282 | 207 | 700.5 | 279 | 474.9
283 | 208 | 700.5 | 281.1 | 478.2
284 | 209 | 700.5 | 283.4 | 481.5
285 | 210 | 700.5 | 285.7 | 484.7
286 | 211 | 700.5 | 288 | 487.9
287 | 212 | 700.4 | 290.2 | 491.1
288 | 213 | 700.4 | 292.3 | 494.3
289 | 214 | 700.6 | 294.4 | 497.5
290 | 215 | 700.8 | 296.5 | 500.4
291 | 216 | 700.8 | 298.7 | 503.5
292 | 217 | 700.7 | 300.9 | 506.4
293 | 218 | 700.9 | 303.1 | 509.3
294 | 219 | 701.1 | 305.3 | 512.2
295 | 220 | 701.2 | 307.3 | 515.1
296 | 221 | 701.3 | 309.2 | 517.5
297 | 222 | 701.3 | 311.7 | 518.7
298 | 223 | 701.3 | 313.3 | 521.6
299 | 224 | 701.5 | 314.3 | 525.5
300 | 225 | 701.5 | 316.7 | 526.6
301 | 226 | 701.5 | 318.4 | 529.1
302 | 227 | 701.6 | 319.7 | 532.1
303 | 228 | 701.5 | 321 | 535
304 | 229 | 701.5 | 323.1 | 536.2
305 | 230 | 701.6 | 323.8 | 539.9
306 | 231 | 701.6 | 325.5 | 541.5
307 | 232 | 701.6 | 326.8 | 543.9
308 | 233 | 701.2 | 327.8 | 546.8
309 | 234 | 701.1 | 329.1 | 549
310 | 235 | 700.9 | 330.3 | 550.9
311 | 236 | 700.6 | 331.6 | 552.9
312 | 237 | 700.6 | 333.4 | 553.8
313 | 238 | 700.5 | 334.4 | 556.2
314 | 239 | 700.1 | 335.3 | 558.6
315 | 240 | 699.8 | 336.6 | 560.4
316 | 241 | 699.5 | 337.8 | 562.1
317 | 242 | 699.2 | 339 | 563.8
318 | 243 | 698.9 | 340.1 | 565.5
319 | 244 | 698.9 | 341.1 | 567.1
320 | 245 | 699.1 | 342.2 | 568.7
321 | 246 | 699.3 | 343.3 | 570.2
322 | 247 | 699.5 | 344.9 | 570.3
323 | 248 | 699.6 | 345.7 | 572
324 | 249 | 699.6 | 346.2 | 574.5
325 | 250 | 699.8 | 347.3 | 575.6
326 | 251 | 699.7 | 348.5 | 576.2
327 | 252 | 699.8 | 348.9 | 578.4
328 | 253 | 699.9 | 349.8 | 579.7
329 | 254 | 700 | 350.9 | 580.4
330 | 255 | 700.1 | 352.2 | 580.7
331 | 256 | 700.2 | 352.9 | 582.2
332 | 257 | 700.3 | 353.2 | 584.5
333 | 258 | 700.7 | 353.9 | 585.8
334 | 259 | 701.1 | 353.9 | 588.4
335 | 260 | 701.3 | 353.9 | 591
336 | 261 | 701.2 | 354.7 | 592.3
337 | 262 | 700.7 | 355.4 | 593.4
338 | 263 | 699.8 | 356.3 | 594.4
339 | 264 | 698.9 | 357.1 | 595.4
340 | 265 | 697.7 | 357.8 | 596.3
341 | 266 | 695.9 | 358.6 | 597.2
342 | 267 | 694.1 | 359.4 | 598.2
343 | 268 | 692.5 | 360.1 | 599
344 | 269 | 691.1 | 360.9 | 599.9
345 | 270 | 689.5 | 361.8 | 600.8
346 | 271 | 687.9 | 362.5 | 601.6
347 | 272 | 686.4 | 363.3 | 602.5
348 | 273 | 684.8 | 364.1 | 603.2
349 | 274 | 683.3 | 365 | 604
350 | 275 | 681.9 | 365.7 | 604.8
351 | 276 | 680.5 | 366.4 | 605.5
352 | 277 | 679.1 | 367.2 | 606.2
353 | 278 | 677.3 | 367.9 | 606.8
354 | 279 | 675.7 | 368.6 | 607.4
355 | 280 | 673.9 | 369.3 | 608
356 | 281 | 672.2 | 370 | 608.6
357 | 282 | 670.8 | 370.7 | 609.2
358 | 283 | 669.4 | 371.3 | 609.7
359 | 284 | 667.9 | 372 | 610.3
360 | 285 | 666.4 | 372.6 | 610.9
361 | 286 | 664.8 | 373.2 | 611.4
362 | 287 | 663.4 | 373.9 | 611.9
363 | 288 | 662 | 374.6 | 612.4
364 | 289 | 660.6 | 375.3 | 612.9
365 | 290 | 659.1 | 376 | 613.3
366 | 291 | 657.7 | 376.6 | 613.7
367 | 292 | 656.5 | 377.3 | 614
368 | 293 | 655.2 | 378.4 | 613.3
369 | 294 | 653.7 | 378.7 | 614.1
370 | 295 | 652.2 | 379.4 | 614.3
371 | 296 | 650.7 | 380.1 | 614.6
372 | 297 | 649.2 | 380.3 | 615.5
373 | 298 | 647.8 | 380.8 | 616.3
374 | 299 | 646.4 | 381.4 | 616.7
375 | 300 | 645 | 382 | 617
376 | 301 | 643.4 | 382.7 | 617.4
377 | 302 | 642 | 383.3 | 617.7
378 | 303 | 640.8 | 383.9 | 617.9
379 | 304 | 639.3 | 385.2 | 617
380 | 305 | 637.9 | 385.5 | 617.8
381 | 306 | 636.7 | 385.8 | 618.7
382 | 307 | 635.3 | 386.4 | 619
383 | 308 | 634 | 387.1 | 619.2
384 | 309 | 632.8 | 387.7 | 619.4
385 | 310 | 631.4 | 388.4 | 619.7
386 | 311 | 630 | 389.2 | 619.9
387 | 312 | 628.6 | 390 | 620.1
388 | 313 | 627.4 | 390.8 | 620.3
389 | 314 | 626.4 | 391.6 | 620.5
390 | 315 | 625.3 | 392.5 | 620.6
391 | 316 | 624.1 | 393.3 | 620.8
392 | 317 | 622.9 | 394.2 | 620.9
393 | 318 | 621.7 | 395.7 | 619.9
394 | 319 | 620.5 | 396.4 | 620.3
395 | 320 | 619.5 | 397.1 | 621
396 | 321 | 618.3 | 398.5 | 620.2
397 | 322 | 617.1 | 399.1 | 620.9
398 | 323 | 615.5 | 399.7 | 621.7
399 | 324 | 614 | 400.8 | 621.5
400 | 325 | 612.5 | 402.1 | 621.1
401 | 326 | 611 | 402.6 | 621.9
402 | 327 | 609.6 | 403.6 | 622
403 | 328 | 608.3 | 404.6 | 621.8
404 | 329 | 607.1 | 405.6 | 621.6
405 | 330 | 605.9 | 406.7 | 621.4
406 | 331 | 604.5 | 407.8 | 621.3
407 | 332 | 603.2 | 408.9 | 621.2
408 | 333 | 602 | 410.5 | 620.2
409 | 334 | 601 | 411.3 | 620.7
410 | 335 | 599.8 | 412.5 | 620.6
411 | 336 | 598.5 | 414 | 619.8
412 | 337 | 597.4 | 415 | 619.8
413 | 338 | 596.2 | 415.9 | 620.1
414 | 339 | 594.8 | 416.9 | 620.2
415 | 340 | 593.5 | 417.6 | 620.8
416 | 341 | 592.2 | 418.7 | 620.8
417 | 342 | 591.2 | 419.8 | 620.8
418 | 343 | 590.2 | 420.9 | 620.8
419 | 344 | 589.1 | 422 | 620.7
420 | 345 | 587.8 | 423.2 | 620.6
421 | 346 | 586.8 | 424.3 | 620.5
422 | 347 | 585.8 | 425.3 | 620.5
423 | 348 | 584.9 | 426.4 | 620.4
424 | 349 | 583.9 | 427.7 | 620.3
425 | 350 | 583 | 428.9 | 620.2
426 | 351 | 582 | 430.1 | 620.2
427 | 352 | 580.8 | 431.4 | 620.1
428 | 353 | 579.9 | 432.7 | 620.1
429 | 354 | 579.1 | 434 | 620
430 | 355 | 578.1 | 435.4 | 619.8
431 | 356 | 577.3 | 436.9 | 619.6
432 | 357 | 576.4 | 438.3 | 619.5
433 | 358 | 575.4 | 439.8 | 619.3
434 | 359 | 574.4 | 441.3 | 619.1
435 | 360 | 573.4 | 442.9 | 618.9
436 | 361 | 572.6 | 444.5 | 618.7
437 | 362 | 571.5 | 446 | 618.5
438 | 363 | 570.3 | 447.5 | 618.2
439 | 364 | 569.2 | 448.9 | 618
440 | 365 | 568.2 | 450.3 | 617.8
441 | 366 | 567.4 | 451.5 | 617.6
442 | 367 | 566.6 | 452.6 | 617.4
443 | 368 | 565.7 | 453.5 | 617.2
444 | 369 | 564.8 | 454.4 | 616.9
445 | 370 | 563.8 | 455.2 | 616.6
446 | 371 | 562.9 | 455.6 | 616.4
447 | 372 | 561.9 | 455.9 | 616.2
448 | 373 | 560.9 | 455.9 | 615.9
449 | 374 | 559.9 | 455.9 | 615.6
450 | 375 | 558.9 | 456.1 | 615.3
451 | 376 | 557.9 | 456.3 | 615
452 | 377 | 556.9 | 456.7 | 614.8
453 | 378 | 556 | 457.1 | 614.5
454 | 379 | 554.9 | 457.7 | 614.3
455 | 380 | 554.1 | 458.5 | 614
456 | 381 | 553.1 | 459.4 | 613.6
457 | 382 | 551.9 | 460.4 | 613.3
458 | 383 | 550.7 | 461.6 | 612.9
459 | 384 | 549.6 | 462.8 | 612.6
460 | 385 | 548.5 | 464.2 | 612.3
461 | 386 | 547.4 | 465.7 | 612
462 | 387 | 546.2 | 467.3 | 611.6
463 | 388 | 545.1 | 469 | 611.3
464 | 389 | 544 | 470.9 | 610.9
465 | 390 | 542.8 | 472.9 | 610.5
466 | 391 | 541.8 | 475 | 610.1
467 | 392 | 541 | 477.2 | 609.6
468 | 393 | 540.2 | 479.4 | 609.1
469 | 394 | 539.3 | 481.7 | 608.6
470 | 395 | 538.2 | 484 | 608.1
471 | 396 | 537.1 | 486.4 | 607.6
472 | 397 | 536.1 | 488.7 | 607.1
473 | 398 | 535.2 | 491.1 | 606.6
474 | 399 | 534.3 | 493.5 | 606
475 | 400 | 533.4 | 495.9 | 605.5
476 | 401 | 532.4 | 498.4 | 605
477 | 402 | 531.4 | 500.9 | 604.4
478 | 403 | 530.5 | 503.6 | 603.9
479 | 404 | 529.6 | 506.4 | 603.3
480 | 405 | 528.8 | 509.4 | 602.7
481 | 406 | 528 | 512.6 | 602.1
482 | 407 | 527.2 | 515.8 | 601.5
483 | 408 | 526.4 | 519.1 | 600.9
484 | 409 | 525.8 | 522.4 | 600.3
485 | 410 | 525.1 | 525.6 | 599.7
486 | 411 | 524.2 | 528.7 | 599.1
487 | 412 | 523.3 | 531.5 | 598.5
488 | 413 | 522.4 | 534 | 597.9
489 | 414 | 521.6 | 536.1 | 597.2
490 | 415 | 520.8 | 540.2 | 596.6
491 | 416 | 520.2 | 553.2 | 595.8
492 | 417 | 519.7 | 562.9 | 594.9
493 | 418 | 519.3 | 559.8 | 593.9
494 | 419 | 518.6 | 547.4 | 593.2
495 | 420 | 517.9 | 534.6 | 592.5
496 | 421 | 517.3 | 526 | 591.9
497 | 422 | 516.7 | 523.4 | 591.2
498 | 423 | 516.1 | 519.6 | 590.5
499 | 424 | 515.4 | 516.2 | 589.9
500 | 425 | 514.6 | 512.5 | 589.3
501 | 426 | 513.8 | 508.3 | 588.8
502 | 427 | 512.9 | 504 | 588.2
503 | 428 | 512 | 502 | 587.7
504 | 429 | 511.1 | 499.5 | 587.2
505 | 430 | 510.1 | 495.3 | 586.7
506 | 431 | 509.2 | 490 | 586.3
507 | 432 | 508.2 | 488.5 | 585.8
508 | 433 | 507.1 | 487.2 | 585.4
509 | 434 | 506 | 484 | 584.9
510 | 435 | 505 | 482 | 584.5
511 | 436 | 504.1 | 477.2 | 584.1
512 | 437 | 503.3 | 473.9 | 583.6
513 | 438 | 502.5 | 471.9 | 583.1
514 | 439 | 502 | 468.6 | 582.7
515 | 440 | 501.4 | 463.6 | 582.2
516 | 441 | 500.5 | 461.5 | 581.8
517 | 442 | 499.8 | 460.4 | 581.4
518 | 443 | 498.7 | 459.3 | 581
519 | 444 | 497.9 | 457 | 580.5
520 | 445 | 497.2 | 453.7 | 580.1
521 | 446 | 496.3 | 451.5 | 579.6
522 | 447 | 495.7 | 449.9 | 579.2
523 | 448 | 495.1 | 448.6 | 578.7
524 | 449 | 494.3 | 446.1 | 578.3
525 | 450 | 493.6 | 446.2 | 577.8
526 | 451 | 493 | 446.1 | 577.3
527 | 452 | 492.3 | 444.9 | 576.9
528 | 453 | 491.4 | 446.7 | 576.4
529 | 454 | 490.7 | 447.5 | 575.9
530 | 455 | 490 | 447.4 | 575.5
531 | 456 | 489.4 | 446 | 575
532 | 457 | 488.8 | 444.3 | 574.5
533 | 458 | 488.1 | 443.8 | 574
534 | 459 | 487.4 | 443.2 | 573.6
535 | 460 | 486.8 | 440.5 | 573.6
536 | 461 | 486 | 436.5 | 573.4
537 | 462 | 485 | 435.6 | 572.9
538 | 463 | 484.2 | 433.4 | 572.4
539 | 464 | 483.1 | 431.9 | 572
540 | 465 | 482.1 | 430.6 | 571.6
541 | 466 | 481.2 | 428.5 | 571.1
542 | 467 | 480.4 | 426 | 570.6
543 | 468 | 479.7 | 425.6 | 570.1
544 | 469 | 479 | 425.8 | 569.6
545 | 470 | 478.2 | 426.1 | 569.1
546 | 471 | 477.4 | 426.4 | 568.7
547 | 472 | 476.6 | 426.8 | 568.2
548 | 473 | 475.8 | 426.6 | 567.7
549 | 474 | 475.2 | 424.2 | 567.2
550 | 475 | 474.4 | 421.9 | 566.8
551 | 476 | 473.6 | 421.4 | 566.3
552 | 477 | 472.8 | 420.2 | 565.8
553 | 478 | 472.2 | 418 | 565.4
554 | 479 | 471.5 | 417.4 | 564.9
555 | 480 | 470.6 | 417.3 | 564.4
556 | 481 | 469.7 | 415.3 | 563.9
557 | 482 | 468.9 | 412.1 | 563.4
558 | 483 | 468.2 | 412.2 | 562.8
559 | 484 | 467.4 | 412.5 | 562.3
560 | 485 | 466.6 | 411.7 | 561.8
561 | 486 | 465.9 | 409.5 | 561.3
562 | 487 | 465.2 | 407.7 | 560.7
563 | 488 | 464.7 | 407.2 | 560.2
564 | 489 | 464 | 407.7 | 559.7
565 | 490 | 463.2 | 407.7 | 559.1
566 | 491 | 462.5 | 406.2 | 558.6
567 | 492 | 461.8 | 405.6 | 558.1
568 | 493 | 461 | 405.3 | 557.5
569 | 494 | 460.3 | 402.4 | 557
570 | 495 | 459.6 | 398.9 | 556.5
571 | 496 | 459.1 | 397.3 | 556
572 | 497 | 458.7 | 395.7 | 555.4
573 | 498 | 458.3 | 395.1 | 554.9
574 | 499 | 457.7 | 396 | 554.4
575 | 500 | 457 | 395.4 | 553.9
576 | 501 | 456.4 | 392.5 | 553.3
577 | 502 | 456 | 393.2 | 552.8
578 | 503 | 455.4 | 394.1 | 552.3
579 | 504 | 454.8 | 393.5 | 551.7
580 | 505 | 454 | 394.1 | 551.2
581 | 506 | 453.2 | 391.8 | 550.6
582 | 507 | 452.6 | 388.1 | 550.1
583 | 508 | 452.1 | 384.9 | 549.5
584 | 509 | 451.7 | 384 | 548.9
585 | 510 | 451 | 382.8 | 548.3
586 | 511 | 450.2 | 381.6 | 547.8
587 | 512 | 449.6 | 380 | 547.2
588 | 513 | 449 | 379.6 | 546.6
589 | 514 | 448.3 | 380.5 | 546
590 | 515 | 447.4 | 380.8 | 545.4
591 | 516 | 446.6 | 378.8 | 544.9
592 | 517 | 445.9 | 378.5 | 544.3
593 | 518 | 445.3 | 377.5 | 543.7
594 | 519 | 444.6 | 376.5 | 543.1
595 | 520 | 444.1 | 375.1 | 542.6
596 | 521 | 443.5 | 374.2 | 542
597 | 522 | 442.9 | 373.2 | 541.4
598 | 523 | 442.4 | 373.8 | 540.8
599 | 524 | 441.9 | 375 | 540.3
600 | 525 | 441.3 | 372.4 | 539.7
601 | 526 | 440.7 | 369.1 | 539.2
602 | 527 | 440 | 367.6 | 538.6
603 | 528 | 439.3 | 366.6 | 538.1
604 | 529 | 438.5 | 362.8 | 537.5
605 | 530 | 437.8 | 362.7 | 537
606 | 531 | 437 | 364.7 | 536.4
607 | 532 | 436.4 | 366.1 | 535.9
608 | 533 | 435.6 | 366.8 | 535.3
609 | 534 | 435 | 366.3 | 534.8
610 | 535 | 434.5 | 368 | 534.2
611 | 536 | 433.7 | 367.5 | 533.6
612 | 537 | 433 | 366.5 | 532.9
613 | 538 | 432.4 | 369.1 | 531.7
614 | 539 | 431.8 | 370.2 | 531.2
615 | 540 | 431.3 | 367.7 | 530.7
616 | 541 | 430.7 | 366.9 | 530.1
617 | 542 | 430.1 | 366.6 | 529.6
618 | 543 | 429.6 | 365.7 | 529
619 | 544 | 429 | 364.6 | 528.5
620 | 545 | 428.4 | 366.2 | 528
621 | 546 | 427.9 | 367 | 527.4
622 | 547 | 427.4 | 367.5 | 526.9
623 | 548 | 427 | 368.6 | 526.5
624 | 549 | 426.5 | 368.3 | 526
625 | 550 | 426.2 | 367.2 | 525.5
626 | 551 | 425.6 | 368 | 525
627 | 552 | 425 | 368.1 | 524.5
628 | 553 | 424.3 | 366.7 | 523.9
629 | 554 | 423.6 | 367.5 | 523.3
630 | 555 | 423 | 367.3 | 522.8
631 | 556 | 422.6 | 366.6 | 522.2
632 | 557 | 421.9 | 367 | 521.6
633 | 558 | 421.2 | 364.7 | 521
634 | 559 | 420.4 | 363.5 | 520.5
635 | 560 | 419.7 | 364.6 | 519.9
636 | 561 | 419.2 | 363.9 | 519.4
637 | 562 | 418.8 | 363.5 | 518.9
638 | 563 | 418.3 | 366.1 | 518.4
639 | 564 | 417.8 | 367.4 | 517.8
640 | 565 | 417.3 | 368.5 | 517.3
641 | 566 | 416.7 | 368.7 | 516.8
642 | 567 | 416.2 | 369.7 | 516.3
643 | 568 | 415.7 | 370.7 | 515.7
644 | 569 | 415.2 | 370.9 | 515.3
645 | 570 | 414.8 | 370.9 | 514.8
646 | 571 | 414.2 | 370.7 | 514.3
647 | 572 | 413.7 | 370.6 | 513.8
648 | 573 | 413.1 | 371.5 | 513.3
649 | 574 | 412.6 | 372.9 | 512.9
650 | 575 | 412.1 | 373.1 | 512.4
651 | 576 | 411.5 | 369.8 | 511.9
652 | 577 | 410.9 | 366.2 | 511.5
653 | 578 | 410.5 | 364.3 | 511
654 | 579 | 410 | 360.8 | 510.6
655 | 580 | 409.2 | 357.4 | 510.1
656 | 581 | 408.6 | 354.7 | 509.6
657 | 582 | 408 | 352.7 | 509.2
658 | 583 | 407.4 | 350.8 | 508.7
659 | 584 | 406.9 | 350.2 | 508.3
660 | 585 | 406.6 | 351 | 507.8
661 | 586 | 406.1 | 350.8 | 507.4
662 | 587 | 405.6 | 351.5 | 506.9
663 | 588 | 405.2 | 352.6 | 506.4
664 | 589 | 404.6 | 354.1 | 506
665 | 590 | 404.2 | 354.3 | 505.5
666 | 591 | 403.7 | 355.4 | 505
667 | 592 | 403.1 | 354.2 | 504.6
668 | 593 | 402.6 | 349.9 | 504.1
669 | 594 | 402 | 349.7 | 503.7
670 | 595 | 401.4 | 349.8 | 503.3
671 | 596 | 400.7 | 347.2 | 502.8
672 | 597 | 400.2 | 346.8 | 502.4
673 | 598 | 399.9 | 346.9 | 502.1
674 | 599 | 399.7 | 347 | 501.6
675 | 600 | 399.3 | 348 | 501.3
676 | 601 | 398.7 | 345.6 | 500.9
677 | 602 | 397.9 | 343.3 | 500.5
678 | 603 | 397.2 | 341.9 | 500.1
679 | 604 | 396.6 | 340.4 | 499.8
680 | 605 | 396.1 | 339.1 | 499.5
681 | 606 | 395.6 | 338.5 | 499.1
682 | 607 | 395.1 | 338.7 | 498.7
683 | 608 | 394.6 | 339.2 | 498.4
684 | 609 | 394.3 | 339 | 498
685 | 610 | 393.9 | 339.9 | 497.6
686 | 611 | 393.5 | 340 | 497.3
687 | 612 | 393.1 | 340.5 | 497
688 | 613 | 392.7 | 340.4 | 496.5
689 | 614 | 392.2 | 342.2 | 496.2
690 | 615 | 391.7 | 342.2 | 495.8
691 | 616 | 391.4 | 342.3 | 495.4
692 | 617 | 391.1 | 342.1 | 495.1
693 | 618 | 390.7 | 343.4 | 494.6
694 | 619 | 390.1 | 343.1 | 494.3
695 | 620 | 389.6 | 342.6 | 493.9
696 | 621 | 389 | 341.3 | 493.5
697 | 622 | 388.4 | 341.2 | 493.1
698 | 623 | 387.9 | 343 | 492.7
699 | 624 | 387.5 | 343.3 | 492.3
700 | 625 | 386.9 | 343.5 | 491.9
701 | 626 | 386.3 | 342.2 | 491.6
702 | 627 | 385.7 | 342.3 | 491.2
703 | 628 | 385.1 | 342.8 | 490.8
704 | 629 | 384.6 | 342 | 490.4
705 | 630 | 384 | 341 | 490
706 | 631 | 383.5 | 340.7 | 489.6
707 | 632 | 383 | 339.4 | 489.3
708 | 633 | 382.5 | 337.8 | 488.9
709 | 634 | 382.1 | 336 | 488.5
710 | 635 | 381.5 | 334.5 | 488.1
711 | 636 | 381 | 334.1 | 487.8
712 | 637 | 380.5 | 335.2 | 487.4
713 | 638 | 380.1 | 336.7 | 487
714 | 639 | 379.7 | 336.8 | 486.6
715 | 640 | 379.3 | 335.3 | 486.3
716 | 641 | 379 | 333.3 | 485.9
717 | 642 | 378.6 | 331.8 | 485.6
718 | 643 | 378.2 | 333.2 | 485.2
719 | 644 | 377.9 | 333.8 | 484.8
720 | 645 | 377.4 | 334.4 | 484.5
721 | 646 | 376.9 | 332.7 | 484.1
722 | 647 | 376.4 | 330.5 | 483.8
723 | 648 | 376 | 328.4 | 483.5
724 | 649 | 375.5 | 327.4 | 483.1
725 | 650 | 374.9 | 327.8 | 482.8
726 | 651 | 374.3 | 327.5 | 482.5
727 | 652 | 373.8 | 327.4 | 482.2
728 | 653 | 373.2 | 326 | 481.9
729 | 654 | 372.7 | 323.1 | 481.6
730 | 655 | 372.3 | 323.4 | 481.3
731 | 656 | 371.8 | 322.9 | 481
732 | 657 | 371.3 | 321.8 | 480.7
733 | 658 | 370.9 | 320.5 | 480.4
734 | 659 | 370.5 | 319.4 | 480.1
735 | 660 | 370 | 319.6 | 479.8
736 | 661 | 369.5 | 320.8 | 479.5
737 | 662 | 369.1 | 321 | 479.3
738 | 663 | 368.6 | 323.3 | 479
739 | 664 | 368.3 | 324.8 | 478.7
740 | 665 | 367.9 | 328.1 | 478.5
741 | 666 | 367.6 | 329.2 | 478.2
742 | 667 | 367.4 | 330.4 | 478
743 | 668 | 367.2 | 331 | 477.8
744 | 669 | 367 | 332.3 | 477.5
745 | 670 | 366.7 | 334.6 | 477.3
746 | 671 | 366.4 | 335.7 | 477.1
747 | 672 | 366.1 | 335.3 | 476.9
748 | 673 | 365.8 | 335.8 | 476.6
749 | 674 | 365.3 | 337.5 | 476.4
750 | 675 | 364.7 | 336.6 | 476.1
751 | 676 | 364.1 | 333.6 | 475.9
752 | 677 | 363.5 | 331.8 | 475.7
753 | 678 | 363.1 | 329.9 | 475.5
754 | 679 | 362.7 | 328.4 | 475.2
755 | 680 | 362.3 | 327.8 | 475
756 | 681 | 361.9 | 327.8 | 474.8
757 | 682 | 361.4 | 327.6 | 474.5
758 | 683 | 360.9 | 328 | 474.2
759 | 684 | 360.5 | 328 | 474
760 | 685 | 360.1 | 327.2 | 473.9
761 | 686 | 359.7 | 327.4 | 473.6
762 | 687 | 359.3 | 325.5 | 473.5
763 | 688 | 358.9 | 325.5 | 473.3
764 | 689 | 358.5 | 327 | 473
765 | 690 | 358.1 | 326.5 | 472.9
766 | 691 | 357.7 | 324 | 472.7
767 | 692 | 357.3 | 322.1 | 472.5
768 | 693 | 356.9 | 321.4 | 472.2
769 | 694 | 356.6 | 321.3 | 472
770 | 695 | 356.2 | 319.8 | 471.9
771 | 696 | 355.8 | 319.1 | 471.7
772 | 697 | 355.4 | 320.4 | 471.5
773 | 698 | 355 | 320.9 | 471.3
774 | 699 | 354.6 | 321.1 | 471.2
775 | 700 | 354.2 | 321.5 | 471
776 | 701 | 353.8 | 321.4 | 470.8
777 | 702 | 353.5 | 321.1 | 470.7
778 | 703 | 353.2 | 321.7 | 470.5
779 | 704 | 352.9 | 321.3 | 470.3
780 | 705 | 352.6 | 320.9 | 470.2
781 | 706 | 352.3 | 320.5 | 470.1
782 | 707 | 352.1 | 320.6 | 469.9
783 | 708 | 351.7 | 320.5 | 469.8
784 | 709 | 351.2 | 321.8 | 469.6
785 | 710 | 350.8 | 323.9 | 469.5
786 | 711 | 350.2 | 325.1 | 469.4
787 | 712 | 349.8 | 328.1 | 469.2
788 | 713 | 349.4 | 327.4 | 469.1
789 | 714 | 349 | 326.9 | 468.9
790 | 715 | 348.6 | 325.4 | 468.8
791 | 716 | 348.1 | 326.6 | 468.7
792 | 717 | 347.8 | 327.1 | 468.6
793 | 718 | 347.5 | 327.4 | 468.4
794 | 719 | 347.2 | 325.7 | 468.4
795 | 720 | 347 | 324.7 | 468.3
796 | 721 | 346.6 | 324.2 | 468.1
797 | 722 | 346.3 | 323.8 | 468
798 | 723 | 345.8 | 324.5 | 467.9
799 | 724 | 345.4 | 325.3 | 467.8
800 | 725 | 344.9 | 326.1 | 467.7
801 | 726 | 344.5 | 324.5 | 467.6
802 | 727 | 344.2 | 323.7 | 467.5
803 | 728 | 343.9 | 322.1 | 467.4
804 | 729 | 343.5 | 322 | 467.3
805 | 730 | 343.2 | 322.4 | 467.2
806 | 731 | 342.9 | 321.3 | 467.1
807 | 732 | 342.5 | 321.6 | 467
808 | 733 | 342.1 | 322.4 | 467
809 | 734 | 341.8 | 320.5 | 466.9
810 | 735 | 341.5 | 320.2 | 466.8
811 | 736 | 341.2 | 319.7 | 466.7
812 | 737 | 340.8 | 320 | 466.6
813 | 738 | 340.4 | 319.6 | 466.6
814 | 739 | 340 | 317.9 | 466.5
815 | 740 | 339.6 | 316.1 | 466.4
816 | 741 | 339.3 | 316 | 466.3
817 | 742 | 338.9 | 316.4 | 466.2
818 | 743 | 338.6 | 314.1 | 466.2
819 | 744 | 338.2 | 313.4 | 466.1
820 | 745 | 337.9 | 314.6 | 466.1
821 | 746 | 337.5 | 314.9 | 466
822 | 747 | 337.2 | 316 | 465.9
823 | 748 | 336.9 | 316.5 | 465.9
824 | 749 | 336.6 | 315.7 | 465.8
825 | 750 | 336.3 | 316.4 | 465.7
826 | 751 | 336.1 | 316.6 | 465.7
827 | 752 | 335.9 | 317 | 465.6
828 | 753 | 335.6 | 316.5 | 465.6
829 | 754 | 335.2 | 314.7 | 465.5
830 | 755 | 334.9 | 315.1 | 465.4
831 | 756 | 334.8 | 315.2 | 465.4
832 | 757 | 334.7 | 316.6 | 465.4
833 | 758 | 334.5 | 317.3 | 465.3
834 | 759 | 334.3 | 316.7 | 465.3
835 | 760 | 334 | 317.4 | 465.2
836 | 761 | 333.6 | 319.4 | 465.2
837 | 762 | 333.3 | 320.1 | 465.1
838 | 763 | 333.1 | 318.6 | 465.1
839 | 764 | 332.9 | 318.2 | 465
840 | 765 | 332.6 | 317.4 | 464.9
841 | 766 | 332.2 | 317.1 | 464.9
842 | 767 | 331.8 | 317 | 464.8
843 | 768 | 331.4 | 313.8 | 464.8
844 | 769 | 331.1 | 311.8 | 464.8
845 | 770 | 331 | 311.6 | 464.7
846 | 771 | 330.7 | 308.8 | 464.7
847 | 772 | 330.5 | 308 | 464.6
848 | 773 | 330.2 | 307.6 | 464.6
849 | 774 | 329.7 | 306.7 | 464.6
850 | 775 | 329.3 | 306.9 | 464.5
851 | 776 | 328.9 | 308.4 | 464.5
852 | 777 | 328.6 | 309.3 | 464.5
853 | 778 | 328.3 | 309.7 | 464.4
854 | 779 | 328.1 | 310.9 | 464.4
855 | 780 | 327.8 | 311.3 | 464.4
856 | 781 | 327.4 | 310.6 | 464.3
857 | 782 | 327 | 311.3 | 464.3
858 | 783 | 326.7 | 312.7 | 464.3
859 | 784 | 326.4 | 311.9 | 464.2
860 | 785 | 326.3 | 311.1 | 464.2
861 | 786 | 326.1 | 310.5 | 464.2
862 | 787 | 325.8 | 308.6 | 464.1
863 | 788 | 325.5 | 306.7 | 464.1
864 | 789 | 325 | 303.8 | 464.1
865 | 790 | 324.7 | 302.7 | 464.1
866 | 791 | 324.3 | 303.9 | 464
867 | 792 | 324 | 304.2 | 464
868 | 793 | 323.7 | 303.3 | 464
869 | 794 | 323.5 | 303.5 | 463.9
870 | 795 | 323.3 | 302.1 | 463.9
871 | 796 | 323 | 300.6 | 463.9
872 | 797 | 322.6 | 300 | 463.9
873 | 798 | 322.2 | 297.8 | 463.9
874 | 799 | 321.9 | 297.6 | 463.9
875 | 800 | 321.7 | 297.1 | 463.9
876 | 801 | 321.6 | 298 | 463.9
877 | 802 | 321.3 | 299.4 | 463.8
878 | 803 | 321 | 297.5 | 463.8
879 | 804 | 320.8 | 295.1 | 463.8
880 | 805 | 320.5 | 293.4 | 463.8
881 | 806 | 320.2 | 293.3 | 463.9
882 | 807 | 319.8 | 291.4 | 463.8
883 | 808 | 319.5 | 290.1 | 463.9
884 | 809 | 319.2 | 289.2 | 463.8
885 | 810 | 318.9 | 289.4 | 463.8
886 | 811 | 318.8 | 288.4 | 463.9
887 | 812 | 318.7 | 287.8 | 463.9
888 | 813 | 318.5 | 289 | 463.9
889 | 814 | 318.2 | 291 | 463.9
890 | 815 | 318 | 291.6 | 463.9
891 | 816 | 317.8 | 292.5 | 463.8
892 | 817 | 317.7 | 293.8 | 463.8
893 | 818 | 317.5 | 295 | 463.8
894 | 819 | 317.4 | 296.6 | 463.8
895 | 820 | 317.3 | 298.6 | 463.9
896 | 821 | 317.1 | 299.6 | 463.9
897 | 822 | 316.9 | 300.9 | 463.8
898 | 823 | 316.6 | 301.6 | 463.8
899 | 824 | 316.1 | 300.6 | 463.8
900 | 825 | 315.8 | 301.3 | 463.8
901 | 826 | 315.4 | 300.9 | 463.8
902 | 827 | 315.1 | 298.5 | 463.7
903 | 828 | 314.8 | 296.2 | 463.7
904 | 829 | 314.5 | 294.4 | 463.6
905 | 830 | 314.2 | 294 | 463.6
906 | 831 | 313.8 | 293.8 | 463.6
907 | 832 | 313.5 | 294 | 463.5
908 | 833 | 313.2 | 294.2 | 463.5
909 | 834 | 312.8 | 293.5 | 463.5
910 | 835 | 312.6 | 291.7 | 463.5
911 | 836 | 312.4 | 288.9 | 463.4
912 | 837 | 312.1 | 288 | 463.4
913 | 838 | 311.9 | 287.4 | 463.4
914 | 839 | 311.7 | 287.6 | 463.4
915 | 840 | 311.4 | 288 | 463.3
916 | 841 | 311.2 | 286.6 | 463.3
917 | 842 | 311 | 285.5 | 463.2
918 | 843 | 310.7 | 284.3 | 463.2
919 | 844 | 310.4 | 282.1 | 463.1
920 | 845 | 310.2 | 281.3 | 463
921 | 846 | 310 | 280.8 | 463
922 | 847 | 309.8 | 279.7 | 462.9
923 | 848 | 309.5 | 280.3 | 462.8
924 | 849 | 309.3 | 280.2 | 462.8
925 | 850 | 309.1 | 278.6 | 462.7
926 | 851 | 308.8 | 277.3 | 462.6
927 | 852 | 308.5 | 276.6 | 462.5
928 | 853 | 308.3 | 275.3 | 462.3
929 | 854 | 308 | 273.8 | 462.2
930 | 855 | 307.6 | 274 | 462.1
931 | 856 | 307.3 | 274.1 | 462
932 | 857 | 306.9 | 274.7 | 461.8
933 | 858 | 306.7 | 275.7 | 461.7
934 | 859 | 306.5 | 276.8 | 461.5
935 | 860 | 306.4 | 277.2 | 461.4
936 | 861 | 306.3 | 277.7 | 461.2
937 | 862 | 306.1 | 276.5 | 461
938 | 863 | 305.9 | 275.6 | 460.9
939 | 864 | 305.6 | 274.3 | 460.7
940 | 865 | 305.3 | 273.2 | 460.5
941 | 866 | 304.9 | 270.7 | 460.4
942 | 867 | 304.5 | 270 | 460.2
943 | 868 | 304.2 | 271.4 | 460
944 | 869 | 303.8 | 271.9 | 459.8
945 | 870 | 303.4 | 270.8 | 459.6
946 | 871 | 303.2 | 267.8 | 459.4
947 | 872 | 303 | 267.1 | 459.1
948 | 873 | 302.7 | 268.1 | 458.9
949 | 874 | 302.5 | 268.3 | 458.7
950 | 875 | 302.2 | 267.5 | 458.4
951 | 876 | 301.9 | 266.1 | 458.2
952 | 877 | 301.5 | 265.5 | 457.9
953 | 878 | 301.3 | 264.6 | 457.6
954 | 879 | 301.1 | 263.6 | 457.3
955 | 880 | 300.9 | 262.5 | 457.1
956 | 881 | 300.6 | 262.2 | 456.8
957 | 882 | 300.2 | 261.8 | 456.5
958 | 883 | 300 | 261.3 | 456.2
959 | 884 | 299.7 | 259.7 | 455.9
960 | 885 | 299.4 | 259.8 | 455.6
961 | 886 | 299.1 | 260.8 | 455.2
962 | 887 | 298.8 | 262.2 | 455
963 | 888 | 298.6 | 263.4 | 454.6
964 | 889 | 298.4 | 262.8 | 454.3
965 | 890 | 298.3 | 262.1 | 453.9
966 | 891 | 298.1 | 262 | 453.6
967 | 892 | 298 | 260.8 | 453.3
968 | 893 | 297.9 | 260.7 | 452.9
969 | 894 | 297.8 | 260.5 | 452.6
970 | 895 | 297.7 | 260 | 452.2
971 | 896 | 297.6 | 259.8 | 451.9
972 | 897 | 297.4 | 260 | 451.5
973 | 898 | 297.2 | 259.8 | 451.1
974 | 899 | 297 | 259.1 | 450.7
975 | 900 | 296.7 | 259 | 450.3
976 | 901 | 296.5 | 259.2 | 450
977 | 902 | 296.4 | 259 | 449.5
978 | 903 | 296.1 | 259 | 449.1
979 | 904 | 295.9 | 259.7 | 448.7
980 | 905 | 295.7 | 259.1 | 448.3
981 | 906 | 295.4 | 259.2 | 447.9
982 | 907 | 295 | 259.2 | 447.5
983 | 908 | 294.6 | 258.9 | 447.1
984 | 909 | 294.3 | 258.5 | 446.7
985 | 910 | 293.9 | 257.3 | 446.7
986 | 911 | 293.6 | 256.8 | 446.6
987 | 912 | 293.3 | 256.1 | 446.2
988 | 913 | 293.1 | 255.6 | 445.8
989 | 914 | 292.8 | 254.2 | 445.4
990 | 915 | 292.5 | 252.5 | 444.9
991 | 916 | 292.1 | 249.7 | 444.5
992 | 917 | 291.8 | 248.2 | 444.1
993 | 918 | 291.4 | 247.6 | 443.7
994 | 919 | 291.2 | 247.4 | 443.3
995 | 920 | 290.8 | 245.2 | 442.9
996 | 921 | 290.5 | 243.8 | 442.5
997 | 922 | 290.2 | 241.2 | 442
998 | 923 | 290 | 238.3 | 441.6
999 | 924 | 289.8 | 235.1 | 441.2
1000 | 925 | 289.6 | 233.7 | 440.8
1001 | 926 | 289.4 | 234 | 440.4
1002 | 927 | 289.2 | 232.5 | 439.9
1003 | 928 | 289 | 232.4 | 439.5
1004 | 929 | 288.8 | 231.5 | 439.1
1005 | 930 | 288.6 | 232.3 | 438.6
1006 | 931 | 288.4 | 233.2 | 438.2
1007 | 932 | 288.3 | 233.4 | 437.8
1008 | 933 | 288.2 | 234.3 | 437.3
1009 | 934 | 287.9 | 235.2 | 436.9
1010 | 935 | 287.7 | 235 | 436.4
1011 | 936 | 287.4 | 233.3 | 436
1012 | 937 | 287.1 | 231.8 | 435.5
1013 | 938 | 286.8 | 231.4 | 435.1
1014 | 939 | 286.3 | 230.6 | 434.7
1015 | 940 | 285.9 | 230.9 | 434.3
1016 | 941 | 285.5 | 230.9 | 433.8
1017 | 942 | 285.2 | 229.6 | 433.4
1018 | 943 | 284.9 | 228.1 | 433
1019 | 944 | 284.7 | 227.6 | 432.5
1020 | 945 | 284.5 | 226.3 | 432.1
1021 | 946 | 284.3 | 226.4 | 431.6
1022 | 947 | 284 | 225.6 | 431.2
1023 | 948 | 283.8 | 225.4 | 430.7
1024 | 949 | 283.6 | 226.1 | 430.3
1025 | 950 | 283.3 | 225.8 | 429.8
1026 | 951 | 283 | 224.9 | 429.3
1027 | 952 | 282.7 | 224.2 | 428.9
1028 | 953 | 282.4 | 223.7 | 428.4
1029 | 954 | 282.1 | 222.4 | 427.9
1030 | 955 | 281.9 | 221.6 | 427.5
1031 | 956 | 281.7 | 222.1 | 426.9
1032 | 957 | 281.3 | 221.2 | 426.5
1033 | 958 | 281 | 220.4 | 426
1034 | 959 | 280.6 | 219.4 | 425.5
1035 | 960 | 280.3 | 218.2 | 425
1036 | 961 | 280 | 216.1 | 424.5
1037 | 962 | 279.8 | 214.2 | 424
1038 | 963 | 279.6 | 212.5 | 423.5
1039 | 964 | 279.4 | 211 | 423
1040 | 965 | 279.1 | 209.9 | 422.5
1041 | 966 | 278.8 | 209.7 | 422
1042 | 967 | 278.6 | 208.8 | 421.5
1043 | 968 | 278.4 | 208.5 | 421
1044 | 969 | 278.2 | 208.4 | 420.4
1045 | 970 | 278 | 208.4 | 419.9
1046 | 971 | 277.8 | 208.1 | 419.4
1047 | 972 | 277.5 | 207.6 | 418.9
1048 | 973 | 277.2 | 208.3 | 418.3
1049 | 974 | 276.9 | 209.5 | 417.8
1050 | 975 | 276.6 | 210.4 | 417.3
1051 | 976 | 276.2 | 211.1 | 416.7
1052 | 977 | 275.9 | 211 | 416.2
1053 | 978 | 275.6 | 210.5 | 415.6
1054 | 979 | 275.3 | 210.1 | 415.1
1055 | 980 | 275.1 | 210.4 | 414.5
1056 | 981 | 274.8 | 210.2 | 413.9
1057 | 982 | 274.5 | 210.4 | 413.4
1058 | 983 | 274.2 | 210 | 412.8
1059 | 984 | 274 | 210.5 | 412.2
1060 | 985 | 273.6 | 210.9 | 411.6
1061 | 986 | 273.3 | 212.3 | 411
1062 | 987 | 273 | 213.7 | 410.5
1063 | 988 | 272.8 | 214.4 | 409.9
1064 | 989 | 272.4 | 213.7 | 409.2
1065 | 990 | 272.1 | 213.2 | 408.7
1066 | 991 | 271.9 | 213.6 | 408
1067 | 992 | 271.7 | 213.5 | 407.5
1068 | 993 | 271.5 | 213.7 | 406.8
1069 | 994 | 271.3 | 214.1 | 406.2
1070 | 995 | 271.1 | 214.7 | 405.6
1071 | 996 | 270.8 | 215.2 | 405
1072 | 997 | 270.5 | 213.3 | 404.3
1073 | 998 | 270.2 | 211.9 | 403.7
1074 | 999 | 269.9 | 209.4 | 403.1
1075 | 1000 | 269.7 | 207.7 | 402.4
1076 | 1001 | 269.5 | 207.2 | 401.8
1077 | 1002 | 269.2 | 206.3 | 401.1
1078 | 1003 | 269 | 204.4 | 400.5
1079 | 1004 | 268.7 | 203.1 | 399.9
1080 | 1005 | 268.6 | 202.7 | 399.2
1081 | 1006 | 268.5 | 203 | 398.5
1082 | 1007 | 268.3 | 203.5 | 397.9
1083 | 1008 | 268 | 203.2 | 397.2
1084 | 1009 | 267.6 | 201.6 | 396.6
1085 | 1010 | 267.3 | 201 | 395.9
1086 | 1011 | 267.1 | 200.1 | 395.2
1087 | 1012 | 266.8 | 200.7 | 394.6
1088 | 1013 | 266.6 | 199.8 | 393.9
1089 | 1014 | 266.4 | 198.8 | 393.2
1090 | 1015 | 266.2 | 199.5 | 392.5
1091 | 1016 | 266 | 199.6 | 391.8
1092 | 1017 | 265.8 | 198.3 | 391.2
1093 | 1018 | 265.6 | 198.2 | 390.5
1094 | 1019 | 265.4 | 199.5 | 389.8
1095 | 1020 | 265.2 | 200.9 | 389
1096 | 1021 | 265 | 202.2 | 388.4
1097 | 1022 | 264.7 | 202.2 | 387.7
1098 | 1023 | 264.5 | 200.8 | 386.9
1099 | 1024 | 264.4 | 199.2 | 386.2
1100 | 1025 | 264.1 | 197.8 | 385.5
1101 | 1026 | 263.9 | 197.7 | 384.8
1102 | 1027 | 263.6 | 197 | 384.1
1103 | 1028 | 263.3 | 197.4 | 383.4
1104 | 1029 | 263 | 196.8 | 382.7
1105 | 1030 | 262.7 | 196.2 | 382
1106 | 1031 | 262.3 | 196.9 | 381.3
1107 | 1032 | 262 | 197.6 | 380.6
1108 | 1033 | 261.6 | 196.2 | 379.8
1109 | 1034 | 261.4 | 196 | 379.1
1110 | 1035 | 261.2 | 195.9 | 378.4
1111 | 1036 | 261 | 195.3 | 377.7
1112 | 1037 | 260.7 | 194.1 | 376.9
1113 | 1038 | 260.5 | 193.1 | 376.2
1114 | 1039 | 260.1 | 193 | 375.5
1115 | 1040 | 259.8 | 192.9 | 374.8
1116 | 1041 | 259.5 | 192.9 | 374.1
1117 | 1042 | 259.2 | 192.2 | 373.3
1118 | 1043 | 258.9 | 191.5 | 372.6
1119 | 1044 | 258.6 | 191.2 | 371.9
1120 | 1045 | 258.4 | 191.2 | 371.2
1121 | 1046 | 258.1 | 192 | 370.5
1122 | 1047 | 257.8 | 192.6 | 369.7
1123 | 1048 | 257.5 | 192.5 | 369
1124 | 1049 | 257.2 | 191.8 | 368.3
1125 | 1050 | 256.9 | 192.5 | 367.6
1126 | 1051 | 256.6 | 192.5 | 367
1127 | 1052 | 256.3 | 193 | 366.3
1128 | 1053 | 255.9 | 193.1 | 365.6
1129 | 1054 | 255.6 | 193 | 364.9
1130 | 1055 | 255.3 | 192.9 | 364.2
1131 | 1056 | 255.2 | 192.9 | 363.5
1132 | 1057 | 255 | 193.7 | 362.8
1133 | 1058 | 254.7 | 193.6 | 362
1134 | 1059 | 254.4 | 192.9 | 361.4
1135 | 1060 | 254.2 | 193.4 | 360.7
1136 | 1061 | 254 | 193.3 | 360
1137 | 1062 | 253.7 | 191.7 | 359.3
1138 | 1063 | 253.4 | 190.3 | 358.6
1139 | 1064 | 253.2 | 190.3 | 358
1140 | 1065 | 252.9 | 189.3 | 357.3
1141 | 1066 | 252.6 | 188.8 | 356.6
1142 | 1067 | 252.3 | 188.5 | 356
1143 | 1068 | 252.2 | 188.8 | 355.3
1144 | 1069 | 252 | 189.2 | 354.6
1145 | 1070 | 251.8 | 190 | 354
1146 | 1071 | 251.7 | 190.1 | 353.3
1147 | 1072 | 251.5 | 189.8 | 352.7
1148 | 1073 | 251.3 | 188.7 | 352.1
1149 | 1074 | 251.1 | 188.8 | 351.4
1150 | 1075 | 250.8 | 189.3 | 350.8
1151 | 1076 | 250.6 | 189.1 | 350.1
1152 | 1077 | 250.3 | 188.3 | 349.5
1153 | 1078 | 250 | 187.3 | 348.9
1154 | 1079 | 249.8 | 186.8 | 348.3
1155 | 1080 | 249.7 | 186.8 | 347.7
1156 | 1081 | 249.5 | 185.9 | 347
1157 | 1082 | 249.4 | 185.2 | 346.4
1158 | 1083 | 249.2 | 186.3 | 345.8
1159 | 1084 | 249.1 | 187.6 | 345.2
1160 | 1085 | 248.9 | 187.9 | 344.6
1161 | 1086 | 248.7 | 187.7 | 344
1162 | 1087 | 248.5 | 187.6 | 343.4
1163 | 1088 | 248.3 | 188.6 | 342.8
1164 | 1089 | 248.1 | 189.2 | 342.2
1165 | 1090 | 247.9 | 189.7 | 341.6
1166 | 1091 | 247.6 | 190.1 | 341
1167 | 1092 | 247.4 | 189.9 | 340.4
1168 | 1093 | 247.1 | 190.3 | 339.9
1169 | 1094 | 246.8 | 190.2 | 339.3
1170 | 1095 | 246.5 | 189.7 | 338.8
1171 | 1096 | 246.2 | 188.9 | 338.2
1172 | 1097 | 246 | 189.5 | 337.6
1173 | 1098 | 245.7 | 190.3 | 337
1174 | 1099 | 245.5 | 190.7 | 336.5
1175 | 1100 | 245.2 | 190.7 | 335.9
1176 | 1101 | 244.9 | 190.6 | 335.4
1177 | 1102 | 244.7 | 189.6 | 334.9
1178 | 1103 | 244.4 | 188.9 | 334.3
1179 | 1104 | 244.3 | 188.5 | 333.8
1180 | 1105 | 244 | 188.2 | 333.2
1181 | 1106 | 243.8 | 187.8 | 332.7
1182 | 1107 | 243.4 | 187.7 | 332.2
1183 | 1108 | 243 | 187.8 | 331.7
1184 | 1109 | 242.7 | 188.1 | 331.1
1185 | 1110 | 242.4 | 188.5 | 330.6
1186 | 1111 | 242.3 | 188.8 | 330
1187 | 1112 | 242.1 | 189.1 | 329.5
1188 | 1113 | 241.9 | 189.4 | 329
1189 | 1114 | 241.6 | 189.2 | 328.5
1190 | 1115 | 241.3 | 188.6 | 328
1191 | 1116 | 241 | 188.4 | 327.5
1192 | 1117 | 240.8 | 188.2 | 327
1193 | 1118 | 240.6 | 187.9 | 326.6
1194 | 1119 | 240.3 | 186.9 | 326.4
1195 | 1120 | 240 | 187.1 | 326.1
1196 | 1121 | 239.7 | 187.4 | 325.6
1197 | 1122 | 239.4 | 187 | 325.1
1198 | 1123 | 239.1 | 186.8 | 324.5
1199 | 1124 | 238.8 | 187.1 | 324
1200 | 1125 | 238.6 | 187 | 323.5
1201 | 1126 | 238.3 | 186.1 | 323
1202 | 1127 | 238 | 186.1 | 322.6
1203 | 1128 | 237.8 | 185.7 | 322.1
1204 | 1129 | 237.5 | 185.7 | 321.6
1205 | 1130 | 237.2 | 184.7 | 321.1
1206 | 1131 | 237 | 183.7 | 320.6
1207 | 1132 | 236.7 | 181.9 | 320.1
1208 | 1133 | 236.5 | 180.2 | 319.6
1209 | 1134 | 236.3 | 180 | 319.1
1210 | 1135 | 236.1 | 179 | 318.6
1211 | 1136 | 235.9 | 177.2 | 318.1
1212 | 1137 | 235.7 | 176.7 | 317.7
1213 | 1138 | 235.5 | 176.9 | 317.2
1214 | 1139 | 235.3 | 176.7 | 316.7
1215 | 1140 | 234.9 | 175.8 | 316.2
1216 | 1141 | 234.7 | 174.7 | 315.7
1217 | 1142 | 234.4 | 174.7 | 315.3
1218 | 1143 | 234.3 | 174.7 | 314.8
1219 | 1144 | 233.9 | 174.7 | 314.3
1220 | 1145 | 233.6 | 174.9 | 313.8
1221 | 1146 | 233.3 | 174.8 | 313.4
1222 | 1147 | 233.1 | 174.2 | 312.9
1223 | 1148 | 232.8 | 173.6 | 312.4
1224 | 1149 | 232.6 | 172.7 | 312
1225 | 1150 | 232.5 | 172 | 311.5
1226 | 1151 | 232.2 | 171 | 311
1227 | 1152 | 232 | 170.4 | 310.5
1228 | 1153 | 231.8 | 169.5 | 310.1
1229 | 1154 | 231.5 | 168.6 | 309.6
1230 | 1155 | 231.2 | 167.6 | 309.1
1231 | 1156 | 231 | 167.4 | 308.7
1232 | 1157 | 230.7 | 167.5 | 308.2
1233 | 1158 | 230.4 | 166.7 | 307.8
1234 | 1159 | 230.1 | 165.7 | 307.3
1235 | 1160 | 229.8 | 165.2 | 306.8
1236 | 1161 | 229.6 | 165.9 | 306.4
1237 | 1162 | 229.4 | 166.2 | 305.9
1238 | 1163 | 229.2 | 165.2 | 305.4
1239 | 1164 | 229 | 165.4 | 305
1240 | 1165 | 228.7 | 165.4 | 304.5
1241 | 1166 | 228.5 | 164 | 304.1
1242 | 1167 | 228.2 | 162.9 | 303.6
1243 | 1168 | 228 | 163.4 | 303.2
1244 | 1169 | 227.7 | 164.1 | 302.7
1245 | 1170 | 227.5 | 163.7 | 302.2
1246 | 1171 | 227.3 | 164 | 301.8
1247 | 1172 | 227.1 | 164.1 | 301.3
1248 | 1173 | 226.8 | 163.7 | 300.9
1249 | 1174 | 226.6 | 163.2 | 300.4
1250 | 1175 | 226.4 | 162.9 | 300
1251 | 1176 | 226.2 | 161.5 | 299.5
1252 | 1177 | 226 | 161.3 | 299.1
1253 | 1178 | 225.7 | 161.4 | 298.6
1254 | 1179 | 225.5 | 161.3 | 298.2
1255 | 1180 | 225.3 | 161 | 297.7
1256 | 1181 | 225.1 | 160.5 | 297.3
1257 | 1182 | 224.9 | 160.4 | 296.8
1258 | 1183 | 224.7 | 160.8 | 296.4
1259 | 1184 | 224.5 | 161.1 | 295.9
1260 | 1185 | 224.3 | 161.5 | 295.5
1261 | 1186 | 224 | 161.8 | 295
1262 | 1187 | 223.8 | 161.9 | 294.6
1263 | 1188 | 223.5 | 162.3 | 294.1
1264 | 1189 | 223.3 | 161.8 | 293.7
1265 | 1190 | 223 | 160.7 | 293.2
1266 | 1191 | 222.7 | 159.6 | 292.8
1267 | 1192 | 222.4 | 158.6 | 292.4
1268 | 1193 | 222.2 | 158.5 | 291.9
1269 | 1194 | 222 | 158.1 | 291.4
1270 | 1195 | 221.7 | 158.1 | 291
1271 | 1196 | 221.4 | 158.4 | 290.5
1272 | 1197 | 221.1 | 158.2 | 290.1
1273 | 1198 | 221 | 158.2 | 289.6
1274 | 1199 | 220.8 | 158.3 | 289.2
1275 | 1200 | 220.6 | 157.8 | 288.8
1276 | 1201 | 220.4 | 156.6 | 288.3
1277 | 1202 | 220.1 | 156.7 | 287.9
1278 | 1203 | 220 | 156.3 | 287.4
1279 | 1204 | 219.8 | 156.2 | 287
1280 | 1205 | 219.6 | 156.9 | 286.5
1281 | 1206 | 219.3 | 157 | 286.1
1282 | 1207 | 219.1 | 155.9 | 285.6
1283 | 1208 | 218.9 | 155 | 285.2
1284 | 1209 | 218.6 | 154.1 | 284.7
1285 | 1210 | 218.4 | 153.6 | 284.3
1286 | 1211 | 218.2 | 153 | 283.9
1287 | 1212 | 218 | 152.9 | 283.4
1288 | 1213 | 217.8 | 153.3 | 283
1289 | 1214 | 217.6 | 153.6 | 282.5
1290 | 1215 | 217.4 | 154.4 | 282.1
1291 | 1216 | 217.3 | 154.5 | 281.6
1292 | 1217 | 217.1 | 154.7 | 281.2
1293 | 1218 | 216.9 | 155 | 280.8
1294 | 1219 | 216.7 | 154.7 | 280.3
1295 | 1220 | 216.5 | 155 | 279.9
1296 | 1221 | 216.3 | 155.2 | 279.5
1297 | 1222 | 216.1 | 154.9 | 279
1298 | 1223 | 215.9 | 153.8 | 278.6
1299 | 1224 | 215.6 | 153.3 | 278.2
1300 | 1225 | 215.3 | 153.2 | 277.7
1301 | 1226 | 215 | 152.6 | 277.3
1302 | 1227 | 214.9 | 152.6 | 276.9
1303 | 1228 | 214.7 | 152.3 | 276.5
1304 | 1229 | 214.5 | 152.6 | 276
1305 | 1230 | 214.2 | 152.9 | 275.6
1306 | 1231 | 213.9 | 153.6 | 275.2
1307 | 1232 | 213.6 | 153.8 | 274.7
1308 | 1233 | 213.4 | 154.2 | 274.3
1309 | 1234 | 213.2 | 154.2 | 273.9
1310 | 1235 | 212.9 | 154.5 | 273.5
1311 | 1236 | 212.7 | 154.4 | 273
1312 | 1237 | 212.5 | 154.1 | 272.6
1313 | 1238 | 212.3 | 154.6 | 272.2
1314 | 1239 | 212.1 | 154.3 | 271.8
1315 | 1240 | 211.9 | 154.1 | 271.3
1316 | 1241 | 211.8 | 153.1 | 270.9
1317 | 1242 | 211.6 | 153 | 270.5
1318 | 1243 | 211.4 | 152.9 | 270.1
1319 | 1244 | 211.2 | 153.4 | 269.7
1320 | 1245 | 211 | 153.4 | 269.3
1321 | 1246 | 210.8 | 153.4 | 268.9
1322 | 1247 | 210.5 | 153.5 | 268.4
1323 | 1248 | 210.4 | 153.2 | 268
1324 | 1249 | 210.2 | 151.7 | 267.6
1325 | 1250 | 210.1 | 150.8 | 267.2
1326 | 1251 | 209.9 | 150.4 | 266.8
1327 | 1252 | 209.7 | 150.3 | 266.4
1328 | 1253 | 209.4 | 149.4 | 266
1329 | 1254 | 209.2 | 149 | 265.6
1330 | 1255 | 209 | 148.8 | 265.2
1331 | 1256 | 208.7 | 147.7 | 264.8
1332 | 1257 | 208.4 | 147.4 | 264.4
1333 | 1258 | 208.2 | 147 | 264
1334 | 1259 | 207.9 | 147.3 | 263.6
1335 | 1260 | 207.7 | 147.1 | 263.2
1336 | 1261 | 207.3 | 147 | 262.8
1337 | 1262 | 207.1 | 147.1 | 262.4
1338 | 1263 | 206.9 | 146.1 | 262
1339 | 1264 | 206.7 | 144.8 | 261.6
1340 | 1265 | 206.4 | 144.7 | 261.2
1341 | 1266 | 206.2 | 144.7 | 261
1342 | 1267 | 205.9 | 144.7 | 260.7
1343 | 1268 | 205.7 | 144.8 | 260.3
1344 | 1269 | 205.4 | 144.5 | 259.9
1345 | 1270 | 205.2 | 144.4 | 259.5
1346 | 1271 | 205.1 | 143.8 | 259.1
1347 | 1272 | 204.9 | 142.7 | 258.7
1348 | 1273 | 204.8 | 142.6 | 258.3
1349 | 1274 | 204.6 | 142.9 | 257.9
1350 | 1275 | 204.4 | 143.1 | 257.6
1351 | 1276 | 204.2 | 142.5 | 257.2
1352 | 1277 | 204.1 | 142.5 | 256.8
1353 | 1278 | 203.9 | 142.9 | 256.4
1354 | 1279 | 203.7 | 143.4 | 256
1355 | 1280 | 203.4 | 143.4 | 255.6
1356 | 1281 | 203.1 | 142.7 | 255.3
1357 | 1282 | 202.9 | 141.5 | 254.8
1358 | 1283 | 202.8 | 141.7 | 254.5
1359 | 1284 | 202.6 | 142.1 | 254.1
1360 | 1285 | 202.5 | 142.4 | 253.7
1361 | 1286 | 202.3 | 142.8 | 253.4
1362 | 1287 | 202.2 | 143.3 | 253
1363 | 1288 | 202 | 143.5 | 252.6
1364 | 1289 | 201.7 | 143.3 | 252.2
1365 | 1290 | 201.3 | 143 | 251.9
1366 | 1291 | 201.1 | 141.3 | 251.5
1367 | 1292 | 200.8 | 140.3 | 251.1
1368 | 1293 | 200.6 | 140.2 | 250.7
1369 | 1294 | 200.3 | 139.9 | 250.4
1370 | 1295 | 200.1 | 139.2 | 250
1371 | 1296 | 199.8 | 138.4 | 249.6
1372 | 1297 | 199.7 | 137.5 | 249.2
1373 | 1298 | 199.5 | 136.5 | 248.9
1374 | 1299 | 199.3 | 135.9 | 248.5
1375 | 1300 | 199.2 | 134.6 | 248.1
1376 | 1301 | 199 | 134 | 247.8
1377 | 1302 | 198.8 | 133.7 | 247.4
1378 | 1303 | 198.6 | 132.6 | 247
1379 | 1304 | 198.3 | 131.5 | 246.7
1380 | 1305 | 198.1 | 131.3 | 246.3
1381 | 1306 | 197.9 | 131.9 | 246
1382 | 1307 | 197.6 | 132 | 245.6
1383 | 1308 | 197.4 | 132.5 | 245.3
1384 | 1309 | 197.1 | 132.5 | 244.9
1385 | 1310 | 196.9 | 132.9 | 244.5
1386 | 1311 | 196.7 | 133.1 | 244.2
1387 | 1312 | 196.5 | 132.6 | 243.9
1388 | 1313 | 196.2 | 132.5 | 243.5
1389 | 1314 | 195.9 | 132.3 | 243.1
1390 | 1315 | 195.7 | 133 | 242.8
1391 | 1316 | 195.6 | 133.8 | 242.4
1392 | 1317 | 195.5 | 134 | 242.1
1393 | 1318 | 195.3 | 134.4 | 241.8
1394 | 1319 | 195 | 134.9 | 241.4
1395 | 1320 | 194.9 | 135.1 | 241.1
1396 | 1321 | 194.7 | 135.1 | 240.7
1397 | 1322 | 194.6 | 134.6 | 240.4
1398 | 1323 | 194.4 | 134.1 | 240
1399 | 1324 | 194.3 | 133.5 | 239.7
1400 | 1325 | 194.1 | 133.4 | 239.4
1401 | 1326 | 193.9 | 133.6 | 239
1402 | 1327 | 193.8 | 133 | 238.7
1403 | 1328 | 193.6 | 133 | 238.3
1404 | 1329 | 193.4 | 132.8 | 238
1405 | 1330 | 193.2 | 132.1 | 237.7
1406 | 1331 | 192.9 | 132.2 | 237.3
1407 | 1332 | 192.7 | 132.6 | 237
1408 | 1333 | 192.5 | 133 | 236.7
1409 | 1334 | 192.3 | 132.6 | 236.3
1410 | 1335 | 192.1 | 132.9 | 236
1411 | 1336 | 192 | 133.4 | 235.6
1412 | 1337 | 191.8 | 133.3 | 235.3
1413 | 1338 | 191.6 | 133.3 | 235
1414 | 1339 | 191.5 | 133.3 | 234.6
1415 | 1340 | 191.3 | 133.3 | 234.3
1416 | 1341 | 191 | 133.2 | 234
1417 | 1342 | 190.8 | 132.3 | 233.7
1418 | 1343 | 190.5 | 132.2 | 233.4
1419 | 1344 | 190.3 | 132.4 | 233.1
1420 | 1345 | 190.1 | 132.2 | 232.7
1421 | 1346 | 189.9 | 132.2 | 232.4
1422 | 1347 | 189.7 | 132 | 232.1
1423 | 1348 | 189.5 | 131.5 | 231.7
1424 | 1349 | 189.3 | 131 | 231.4
1425 | 1350 | 189.1 | 130.7 | 231.1
1426 | 1351 | 188.9 | 130.9 | 230.8
1427 | 1352 | 188.6 | 130.3 | 230.5
1428 | 1353 | 188.4 | 130.2 | 230.2
1429 | 1354 | 188.2 | 130.5 | 229.8
1430 | 1355 | 188 | 130.6 | 229.5
1431 | 1356 | 187.9 | 130.5 | 229.2
1432 | 1357 | 187.7 | 130.5 | 228.9
1433 | 1358 | 187.5 | 130.5 | 228.6
1434 | 1359 | 187.4 | 130.7 | 228.2
1435 | 1360 | 187.2 | 130.9 | 227.9
1436 | 1361 | 186.9 | 131.3 | 227.6
1437 | 1362 | 186.7 | 131.3 | 227.3
1438 | 1363 | 186.5 | 130.8 | 227
1439 | 1364 | 186.2 | 130.7 | 226.7
1440 | 1365 | 186 | 131.1 | 226.4
1441 | 1366 | 185.8 | 131.1 | 226.1
1442 | 1367 | 185.6 | 131.3 | 225.8
1443 | 1368 | 185.3 | 131.5 | 225.5
1444 | 1369 | 185.1 | 132 | 225.1
1445 | 1370 | 184.9 | 132 | 224.9
1446 | 1371 | 184.7 | 132 | 224.6
1447 | 1372 | 184.6 | 132 | 224.3
1448 | 1373 | 184.4 | 131.6 | 223.9
1449 | 1374 | 184.3 | 131.7 | 223.7
1450 | 1375 | 184.1 | 131.7 | 223.4
1451 | 1376 | 183.9 | 131.8 | 223
1452 | 1377 | 183.6 | 131.8 | 222.8
1453 | 1378 | 183.4 | 131.9 | 222.5
1454 | 1379 | 183.2 | 131.8 | 222.2
1455 | 1380 | 183.1 | 131.8 | 221.8
1456 | 1381 | 182.8 | 131.7 | 221.6
1457 | 1382 | 182.7 | 131.7 | 221.3
1458 | 1383 | 182.5 | 131.9 | 221
1459 | 1384 | 182.3 | 131.8 | 220.7
1460 | 1385 | 182.1 | 131.6 | 220.4
1461 | 1386 | 181.9 | 131.6 | 220.1
1462 | 1387 | 181.8 | 131.6 | 219.8
1463 | 1388 | 181.6 | 131.4 | 219.5
1464 | 1389 | 181.3 | 131.4 | 219.2
1465 | 1390 | 181.2 | 131.8 | 219
1466 | 1391 | 181.1 | 130.9 | 218.7
1467 | 1392 | 181 | 129.9 | 218.4
1468 | 1393 | 180.8 | 129.3 | 218.1
1469 | 1394 | 180.6 | 130.4 | 217.9
1470 | 1395 | 180.4 | 131.4 | 217.6
1471 | 1396 | 180.3 | 131.6 | 217.4
1472 | 1397 | 180.2 | 131.9 | 217.1
1473 | 1398 | 180.1 | 132.7 | 216.8
1474 | 1399 | 180 | 134 | 216.6
1475 | 1400 | 179.9 | 135.1 | 216.3
1476 | 1401 | 179.7 | 136 | 216
1477 | 1402 | 179.6 | 137.2 | 215.8
1478 | 1403 | 179.5 | 138.4 | 215.5
1479 | 1404 | 179.3 | 139.6 | 215.2
1480 | 1405 | 179.2 | 140.6 | 215
1481 | 1406 | 179 | 140.8 | 214.7
1482 | 1407 | 178.9 | 141 | 214.4
1483 | 1408 | 178.7 | 141.4 | 214.1
1484 | 1409 | 178.6 | 142 | 213.9
1485 | 1410 | 178.5 | 142.7 | 213.6
1486 | 1411 | 178.3 | 143.3 | 213.4
1487 | 1412 | 178.2 | 143.5 | 213.1
1488 | 1413 | 178 | 143.3 | 212.8
1489 | 1414 | 177.7 | 142.9 | 212.6
1490 | 1415 | 177.6 | 142.8 | 212.3
1491 | 1416 | 177.4 | 142.4 | 212
1492 | 1417 | 177.2 | 142.2 | 211.8
1493 | 1418 | 176.9 | 142.3 | 211.5
1494 | 1419 | 176.8 | 142.5 | 211.2
1495 | 1420 | 176.6 | 142.8 | 211
1496 | 1421 | 176.4 | 143.1 | 210.7
1497 | 1422 | 176.2 | 142.9 | 210.4
1498 | 1423 | 176.1 | 142.8 | 210.1
1499 | 1424 | 175.9 | 142.7 | 209.9
1500 | 1425 | 175.7 | 142.8 | 209.6
1501 | 1426 | 175.6 | 142.9 | 209.3
1502 | 1427 | 175.4 | 142.9 | 209.1
1503 | 1428 | 175.3 | 143.2 | 208.8
1504 | 1429 | 175.2 | 143.4 | 208.5
1505 | 1430 | 175 | 143.6 | 208.3
1506 | 1431 | 174.9 | 143.5 | 208
1507 | 1432 | 174.8 | 143.6 | 207.7
1508 | 1433 | 174.6 | 143.5 | 207.5
1509 | 1434 | 174.5 | 143.2 | 207.2
1510 | 1435 | 174.4 | 143.5 | 206.9
1511 | 1436 | 174.2 | 143.7 | 206.6
1512 | 1437 | 174 | 143.7 | 206.4
1513 | 1438 | 173.9 | 143.7 | 206.1
1514 | 1439 | 173.7 | 143.7 | 205.8
1515 | 1440 | 173.6 | 143.6 | 205.6
1516 | 1441 | 173.4 | 143.3 | 205.3
1517 | 1442 | 173.3 | 143.3 | 205
1518 | 1443 | 173.1 | 143 | 204.8
1519 | 1444 | 172.9 | 143 | 204.6
1520 | 1445 | 172.7 | 142.9 | 204.3
1521 | 1446 | 172.6 | 142.8 | 204
1522 | 1447 | 172.5 | 142.8 | 203.8
1523 | 1448 | 172.3 | 142.8 | 203.5
1524 | 1449 | 172.1 | 142.7 | 203.3
1525 | 1450 | 172 | 142.5 | 203
1526 | 1451 | 171.8 | 142.2 | 202.7
1527 | 1452 | 171.7 | 142 | 202.5
1528 | 1453 | 171.5 | 141.9 | 202.2
1529 | 1454 | 171.4 | 141.7 | 201.9
1530 | 1455 | 171.2 | 141.7 | 201.7
1531 | 1456 | 171.1 | 141.5 | 201.4
1532 | 1457 | 171 | 141.2 | 201.2
1533 | 1458 | 170.8 | 141.2 | 200.9
1534 | 1459 | 170.5 | 141.2 | 200.7
1535 | 1460 | 170.3 | 140.9 | 200.4
1536 | 1461 | 170.1 | 140.7 | 200.2
1537.1 | 1462.1 | 169.9 | 140.8 | 199.9
1538.1 | 1463.1 | 169.8 | 140.8 | 199.6
1539.1 | 1464.1 | 169.5 | 140.8 | 199.4
1540.1 | 1465.1 | 169.3 | 140.8 | 199.1
1541.1 | 1466.1 | 169.1 | 140.8 | 198.9
1542.1 | 1467.1 | 168.9 | 140.7 | 198.6
1543.1 | 1468.1 | 168.7 | 140.7 | 198.4
1544.1 | 1469.1 | 168.5 | 140.6 | 198.2
1545.1 | 1470.1 | 168.4 | 140.3 | 197.9
1546.1 | 1471.1 | 168.2 | 139.9 | 197.6
1547.1 | 1472.1 | 168 | 139.2 | 197.4
1548.1 | 1473.1 | 167.8 | 138.7 | 197.1
1549.1 | 1474.1 | 167.5 | 138.4 | 196.9
1550.1 | 1475.1 | 167.3 | 138.3 | 196.6
1551.1 | 1476.1 | 167.1 | 138.1 | 196.4
1552.1 | 1477.1 | 167 | 138.1 | 196.1
1553.1 | 1478.1 | 166.8 | 137.9 | 195.9
1554.1 | 1479.1 | 166.6 | 137.5 | 195.7
1555.1 | 1480.1 | 166.5 | 136.9 | 195.4
1556.1 | 1481.1 | 166.4 | 136 | 195.2
1557.1 | 1482.1 | 166.2 | 135.1 | 194.9
1558.1 | 1483.1 | 166.1 | 134.5 | 194.7
1559.1 | 1484.1 | 165.9 | 133.5 | 194.4
1560.1 | 1485.1 | 165.7 | 132.8 | 194.2
1561.1 | 1486.1 | 165.5 | 132.7 | 193.9
1562.1 | 1487.1 | 165.3 | 132.5 | 193.7
1563.1 | 1488.1 | 165.1 | 132.6 | 193.4
1564.1 | 1489.1 | 165 | 132.8 | 193.2
1565.1 | 1490.1 | 164.8 | 132.9 | 193
1566.1 | 1491.1 | 164.7 | 133.3 | 192.7
1567.1 | 1492.1 | 164.6 | 133.4 | 192.5
1568.1 | 1493.1 | 164.4 | 132.7 | 192.3
1569.1 | 1494.1 | 164.3 | 131.9 | 192
1570.1 | 1495.1 | 164.2 | 131.5 | 191.8
1571.1 | 1496.1 | 164 | 131.3 | 191.5
1572.1 | 1497.1 | 163.8 | 131.5 | 191.3
1573.1 | 1498.1 | 163.6 | 131.9 | 191.1
1574.1 | 1499.1 | 163.5 | 132 | 190.8
1575.1 | 1500.1 | 163.4 | 131.7 | 190.6
1576.1 | 1501.1 | 163.3 | 131.4 | 190.4
1577.1 | 1502.1 | 163.1 | 131.1 | 190.1
1578.1 | 1503.1 | 162.9 | 130.7 | 189.9
1579.1 | 1504.1 | 162.6 | 130.5 | 189.7
1580.1 | 1505.1 | 162.4 | 130.6 | 189.4
1581.1 | 1506.1 | 162.3 | 130.5 | 189.2
1582.1 | 1507.1 | 162.2 | 130.4 | 189
1583.1 | 1508.1 | 162 | 130.1 | 188.7
1584.1 | 1509.1 | 162 | 129.8 | 188.5
1585.1 | 1510.1 | 161.8 | 128.7 | 188.3
1586.1 | 1511.1 | 161.7 | 127.7 | 188
1587.1 | 1512.1 | 161.5 | 127.4 | 187.8
1588.1 | 1513.1 | 161.3 | 127.6 | 187.6
1589.1 | 1514.1 | 161.1 | 127.4 | 187.3
1590.1 | 1515.1 | 160.9 | 127.6 | 187.1
1591.1 | 1516.1 | 160.7 | 128.1 | 186.9
1592.1 | 1517.1 | 160.6 | 128.4 | 186.6
1593.1 | 1518.1 | 160.4 | 128.8 | 186.4
1594.1 | 1519.1 | 160.3 | 129.2 | 186.2
1595.1 | 1520.1 | 160.1 | 129.5 | 186
1596.1 | 1521.1 | 159.9 | 129.7 | 185.8
1597.1 | 1522.1 | 159.7 | 130 | 185.5
1598.1 | 1523.1 | 159.5 | 130.4 | 185.3
1599.1 | 1524.1 | 159.4 | 130.7 | 185.1
1600.1 | 1525.1 | 159.2 | 131.1 | 184.8
1601.1 | 1526.1 | 159.1 | 131.5 | 184.6
1602.1 | 1527.1 | 158.9 | 132 | 184.4
1603.1 | 1528.1 | 158.7 | 132.1 | 184.3
1604.1 | 1529.1 | 158.5 | 132 | 184
1605.1 | 1530.1 | 158.3 | 132 | 183.8
1606.1 | 1531.1 | 158.1 | 132 | 183.6
1607.1 | 1532.1 | 157.9 | 132.1 | 183.4
1608.1 | 1533.1 | 157.7 | 132.1 | 183.2
1609.1 | 1534.1 | 157.6 | 132.1 | 182.9
1610.1 | 1535.1 | 157.4 | 132.1 | 182.7
1611.1 | 1536.1 | 157.3 | 131.9 | 182.6
1612.1 | 1537.1 | 157.2 | 131.6 | 182.3
1613.1 | 1538.1 | 157 | 131.4 | 182.1
1614.1 | 1539.1 | 156.9 | 131 | 181.9
1615.1 | 1540.1 | 156.8 | 130.8 | 181.7
1616.1 | 1541.1 | 156.7 | 130.6 | 181.5
1617.1 | 1542.1 | 156.5 | 130.3 | 181.3
1618.1 | 1543.1 | 156.4 | 130 | 181.1
1619.1 | 1544.1 | 156.3 | 129.7 | 180.8
1620.1 | 1545.1 | 156.2 | 129.6 | 180.6
1621.1 | 1546.1 | 156.1 | 129.4 | 180.4
1622.1 | 1547.1 | 156 | 129.3 | 180.2
1623.1 | 1548.1 | 155.8 | 129.2 | 180
1624.1 | 1549.1 | 155.6 | 129.1 | 179.8
1625.1 | 1550.1 | 155.4 | 129 | 179.5
1626.1 | 1551.1 | 155.3 | 129 | 179.3
1627.1 | 1552.1 | 155.1 | 129 | 179.1
1628.1 | 1553.1 | 155 | 128.9 | 178.9
1629.1 | 1554.1 | 154.8 | 128.8 | 178.7
1630.1 | 1555.1 | 154.7 | 128.5 | 178.5
1631.1 | 1556.1 | 154.5 | 128.3 | 178.3
1632.1 | 1557.1 | 154.5 | 128 | 178.1
1633.1 | 1558.1 | 154.4 | 127.8 | 177.9
1634.1 | 1559.1 | 154.2 | 127.4 | 177.6
1635.1 | 1560.1 | 154.1 | 127 | 177.4
1636.1 | 1561.1 | 154 | 126.7 | 177.2
1637.1 | 1562.1 | 153.9 | 126.3 | 177
1638.1 | 1563.1 | 153.8 | 125.8 | 176.8
1639.1 | 1564.1 | 153.7 | 125.3 | 176.6
1640.1 | 1565.1 | 153.6 | 124.8 | 176.4
1641.1 | 1566.1 | 153.5 | 124.4 | 176.2
1642.1 | 1567.1 | 153.3 | 124.2 | 176
1643.1 | 1568.1 | 153.2 | 124.1 | 175.8
1644.1 | 1569.1 | 153.1 | 124 | 175.6
1645.1 | 1570.1 | 153 | 123.9 | 175.3
1646.1 | 1571.1 | 152.8 | 123.9 | 175.1
1647.1 | 1572.1 | 152.7 | 124 | 174.9
1648.1 | 1573.1 | 152.6 | 124.1 | 174.7
1649.1 | 1574.1 | 152.5 | 124.1 | 174.5
1650.1 | 1575.1 | 152.3 | 124.1 | 174.3
1651.1 | 1576.1 | 152.2 | 124.1 | 174.1
1652.1 | 1577.1 | 152 | 124 | 173.9
1653.1 | 1578.1 | 151.9 | 123.9 | 173.7
1654.1 | 1579.1 | 151.8 | 123.9 | 173.5
1655.1 | 1580.1 | 151.6 | 123.8 | 173.3
1656.1 | 1581.1 | 151.4 | 123.6 | 173.1
1657.1 | 1582.1 | 151.2 | 123.4 | 172.9
1658.1 | 1583.1 | 151 | 123.3 | 172.6
1659.1 | 1584.1 | 150.8 | 123.2 | 172.5
1660.1 | 1585.1 | 150.6 | 123 | 172.2
1661.1 | 1586.1 | 150.4 | 122.9 | 172
1662.1 | 1587.1 | 150.3 | 122.7 | 171.8
1663.1 | 1588.1 | 150.2 | 122.6 | 171.6
1664.1 | 1589.1 | 150 | 122.6 | 171.5
1665.1 | 1590.1 | 149.8 | 122.5 | 171.3
1666.1 | 1591.1 | 149.6 | 122.5 | 171
1667.1 | 1592.1 | 149.4 | 122.5 | 170.9
1668.1 | 1593.1 | 149.3 | 122.4 | 170.7
1669.1 | 1594.1 | 149.1 | 122.3 | 170.5
1670.1 | 1595.1 | 148.9 | 122.3 | 170.3
1671.1 | 1596.1 | 148.8 | 122.2 | 170.1
1672.1 | 1597.1 | 148.6 | 122.2 | 169.9
1673.1 | 1598.1 | 148.5 | 122 | 169.7
1674.1 | 1599.1 | 148.4 | 121.7 | 169.5
1675.1 | 1600.1 | 148.3 | 121.5 | 169.3
1676.1 | 1601.1 | 148.2 | 121.3 | 169.1
1677.1 | 1602.1 | 148.2 | 121.1 | 168.9
1678.1 | 1603.1 | 148.1 | 120.8 | 168.7
1679.1 | 1604.1 | 147.9 | 120.7 | 168.6
1680.1 | 1605.1 | 147.8 | 120.5 | 168.4
1681.1 | 1606.1 | 147.7 | 120.4 | 168.2
1682.1 | 1607.1 | 147.7 | 120.3 | 168
1683.1 | 1608.1 | 147.5 | 120.2 | 167.8
1684.1 | 1609.1 | 147.3 | 120.1 | 167.6
1685.1 | 1610.1 | 147.2 | 119.9 | 167.4
1686.1 | 1611.1 | 147.1 | 119.6 | 167.2
1687.1 | 1612.1 | 146.9 | 119.2 | 167
1688.1 | 1613.1 | 146.7 | 118.9 | 166.8
1689.1 | 1614.1 | 146.5 | 118.7 | 166.7
1690.1 | 1615.1 | 146.4 | 118.5 | 166.5
1691.1 | 1616.1 | 146.3 | 118.4 | 166.3
1692.1 | 1617.1 | 146.2 | 118.3 | 166.1
1693.1 | 1618.1 | 146 | 118.2 | 165.9
1694.1 | 1619.1 | 145.7 | 118.1 | 165.7
1695.1 | 1620.1 | 145.6 | 118 | 165.5
1696.1 | 1621.1 | 145.5 | 117.9 | 165.4
1697.1 | 1622.1 | 145.3 | 117.7 | 165.2
1698.1 | 1623.1 | 145.2 | 117.7 | 165
1699.1 | 1624.1 | 145.2 | 117.7 | 164.8
1700.1 | 1625.1 | 145.1 | 117.6 | 164.6
1701.1 | 1626.1 | 145 | 117.5 | 164.4
1702.1 | 1627.1 | 144.9 | 117.4 | 164.3
1703.1 | 1628.1 | 144.7 | 117.3 | 164.1
1704.1 | 1629.1 | 144.6 | 117.1 | 163.9
1705.1 | 1630.1 | 144.5 | 117 | 163.7
1706.1 | 1631.1 | 144.4 | 117 | 163.5
1707.1 | 1632.1 | 144.3 | 116.8 | 163.3
1708.1 | 1633.1 | 144.2 | 116.7 | 163.1
1709.1 | 1634.1 | 144.1 | 116.7 | 163
1710.1 | 1635.1 | 144 | 116.6 | 162.8
1711.1 | 1636.1 | 143.8 | 116.4 | 162.6
1712.1 | 1637.1 | 143.7 | 116.1 | 162.4
1713.1 | 1638.1 | 143.6 | 115.8 | 162.2
1714.1 | 1639.1 | 143.5 | 115.3 | 162
1715.1 | 1640.1 | 143.4 | 114.1 | 161.9
1716.1 | 1641.1 | 143.4 | 112.4 | 161.8
1717.1 | 1642.1 | 143.3 | 110.6 | 161.6
1718.1 | 1643.1 | 143.2 | 108.7 | 161.4
1719.1 | 1644.1 | 143.1 | 108.5 | 161.3
1720.1 | 1645.1 | 143 | 108 | 161.1
1721.1 | 1646.1 | 142.9 | 107.3 | 160.9
1722.1 | 1647.1 | 142.8 | 106.9 | 160.6
1723.1 | 1648.1 | 142.7 | 106.1 | 160.4
1724.1 | 1649.1 | 142.6 | 105.4 | 160.3
1725.1 | 1650.1 | 142.4 | 104.9 | 160
1726.1 | 1651.1 | 142.3 | 104 | 159.8
1727.1 | 1652.1 | 142.2 | 103.1 | 159.6
1728.1 | 1653.1 | 142 | 102.7 | 159.6
1729.1 | 1654.1 | 141.9 | 102.6 | 159.2
1730.1 | 1655.1 | 141.7 | 102 | 159
1731.1 | 1656.1 | 141.6 | 101.2 | 158.9
1732.1 | 1657.1 | 141.5 | 100.9 | 158.7
1733.1 | 1658.1 | 141.4 | 100.6 | 158.4
1734.1 | 1659.1 | 141.3 | 99.6 | 158.3
1735.1 | 1660.1 | 141.1 | 98.4 | 158.2
1736.1 | 1661.1 | 141 | 97.9 | 158.1
1737.1 | 1662.1 | 140.9 | 97.8 | 157.9
1738.1 | 1663.1 | 140.8 | 97.3 | 157.7
1739.1 | 1664.1 | 140.6 | 97 | 157.5
1740.1 | 1665.1 | 140.5 | 97 | 157.4
1741.1 | 1666.1 | 140.4 | 96.7 | 157.2
1742.1 | 1667.1 | 140.3 | 96.1 | 157
1743.1 | 1668.1 | 140.1 | 95.4 | 156.8
1744.1 | 1669.1 | 140 | 95.1 | 156.6
1745.1 | 1670.1 | 139.9 | 94.3 | 156.4
1746.1 | 1671.1 | 139.7 | 93.3 | 156.2
1747.1 | 1672.1 | 139.6 | 92.5 | 155.9
1748.1 | 1673.1 | 139.4 | 92 | 155.7
1749.1 | 1674.1 | 139.3 | 91.4 | 155.6
1750.1 | 1675.1 | 139.1 | 90.7 | 155.4
1751.1 | 1676.1 | 138.9 | 90.2 | 155.2
1752.1 | 1677.1 | 138.8 | 89.6 | 155.1
1753.1 | 1678.1 | 138.6 | 90 | 154.9
1754.1 | 1679.1 | 138.5 | 90.3 | 154.7
1755.1 | 1680.1 | 138.4 | 90.6 | 154.6
1756.1 | 1681.1 | 138.3 | 90.7 | 154.4
1757.1 | 1682.1 | 138.2 | 90.9 | 154.3
1758.1 | 1683.1 | 138 | 90.6 | 154
1759.1 | 1684.1 | 137.9 | 90.2 | 153.9
1760.1 | 1685.1 | 137.8 | 90.3 | 153.7
1761.1 | 1686.1 | 137.6 | 90.5 | 153.6
1762.1 | 1687.1 | 137.4 | 90.7 | 153.4
1763.1 | 1688.1 | 137.3 | 90.8 | 153.2
1764.1 | 1689.1 | 137.2 | 90.7 | 153.1
1765.1 | 1690.1 | 137 | 90.1 | 152.9
1766.1 | 1691.1 | 136.9 | 90 | 152.7
1767.1 | 1692.1 | 136.7 | 89.4 | 152.5
1768.1 | 1693.1 | 136.6 | 88.7 | 152.4
1769.1 | 1694.1 | 136.4 | 88 | 152.2
1770.1 | 1695.1 | 136.2 | 87.8 | 152
1771.1 | 1696.1 | 136.1 | 88 | 151.9
1772.1 | 1697.1 | 136 | 87.6 | 151.7
1773.1 | 1698.1 | 135.9 | 87.3 | 151.5
1774.1 | 1699.1 | 135.8 | 87.4 | 151.3
1775.1 | 1700.1 | 135.7 | 87.5 | 151.2
1776.1 | 1701.1 | 135.7 | 87.6 | 151
1777.1 | 1702.1 | 135.6 | 87.5 | 150.8
1778.1 | 1703.1 | 135.5 | 87.5 | 150.7
1779.1 | 1704.1 | 135.4 | 87.5 | 150.5
1780.1 | 1705.1 | 135.3 | 87.8 | 150.4
1781.1 | 1706.1 | 135.2 | 87.9 | 150.2
1782.1 | 1707.1 | 135.1 | 87.7 | 150.1
1783.1 | 1708.1 | 135 | 87.6 | 149.9
1784.1 | 1709.1 | 134.9 | 88.1 | 149.7
1785.1 | 1710.1 | 134.7 | 88.3 | 149.6
1786.1 | 1711.1 | 134.6 | 88.1 | 149.4
1787.1 | 1712.1 | 134.5 | 88 | 149.2
1788.1 | 1713.1 | 134.4 | 88.2 | 149.1
1789.1 | 1714.1 | 134.3 | 88.3 | 148.9
1790.1 | 1715.1 | 134.1 | 88.2 | 148.8
1791.1 | 1716.1 | 133.9 | 87.7 | 148.6
1792.1 | 1717.1 | 133.8 | 87.9 | 148.4
1793.1 | 1718.1 | 133.6 | 88.1 | 148.3
1794.1 | 1719.1 | 133.5 | 88.3 | 148.1
1795.1 | 1720.1 | 133.3 | 88.4 | 147.9
1796.1 | 1721.1 | 133.2 | 88.6 | 147.8
1797.1 | 1722.1 | 133 | 88.8 | 147.6
1798.1 | 1723.1 | 132.9 | 88.7 | 147.4
1799.1 | 1724.1 | 132.8 | 88.4 | 147.3
1800.1 | 1725.1 | 132.7 | 88.6 | 147.1
1801.1 | 1726.1 | 132.6 | 88.8 | 146.9
1802.1 | 1727.1 | 132.5 | 88.8 | 146.8
1803.1 | 1728.1 | 132.4 | 88.9 | 146.6
1804.1 | 1729.1 | 132.3 | 89 | 146.5
1805.1 | 1730.1 | 132.1 | 88.7 | 146.3
1806.1 | 1731.1 | 132 | 88.7 | 146.2
1807.1 | 1732.1 | 131.8 | 88.6 | 146.1
1808.1 | 1733.1 | 131.7 | 88.5 | 145.9
1809.1 | 1734.1 | 131.6 | 87.8 | 145.7
1810.1 | 1735.1 | 131.5 | 87.3 | 145.6
1811.1 | 1736.1 | 131.3 | 87 | 145.4
1812.1 | 1737.1 | 131.3 | 86.3 | 145.2
1813.1 | 1738.1 | 131.1 | 85.4 | 145.1
1814.1 | 1739.1 | 131 | 84.8 | 145
1815.1 | 1740.1 | 130.9 | 84.5 | 144.8
1816.1 | 1741.1 | 130.7 | 84.4 | 144.6
1817.1 | 1742.1 | 130.6 | 84.4 | 144.5
1818.1 | 1743.1 | 130.4 | 84 | 144.3
1819.1 | 1744.1 | 130.3 | 83.7 | 144.2
1820.1 | 1745.1 | 130.2 | 83.4 | 144
1821.1 | 1746.1 | 130 | 83.7 | 143.9
1822.1 | 1747.1 | 129.9 | 84.1 | 143.7
1823.1 | 1748.1 | 129.8 | 84.1 | 143.5
1824.1 | 1749.1 | 129.7 | 84.2 | 143.4
1825.1 | 1750.1 | 129.6 | 84.2 | 143.3
1826.1 | 1751.1 | 129.5 | 84.2 | 143.1
1827.1 | 1752.1 | 129.4 | 84.1 | 143
1828.1 | 1753.1 | 129.3 | 84.1 | 142.8
1829.1 | 1754.1 | 129.2 | 84.4 | 142.7
1830.1 | 1755.1 | 129 | 84.7 | 142.5
1831.1 | 1756.1 | 128.9 | 84.9 | 142.4
1832.1 | 1757.1 | 128.7 | 85.1 | 142.2
1833.1 | 1758.1 | 128.6 | 85.1 | 142
1834.1 | 1759.1 | 128.5 | 85.2 | 141.9
1835.1 | 1760.1 | 128.3 | 85.4 | 141.8
1836.1 | 1761.1 | 128.2 | 85.5 | 141.6
1837.1 | 1762.1 | 128.1 | 84.1 | 144.5
1838.1 | 1763.1 | 128 | 84 | 144.6
1839.1 | 1764.1 | 127.9 | 83.8 | 144.5
1840.1 | 1765.1 | 127.8 | 83.7 | 144.4
1841.1 | 1766.1 | 127.6 | 83.6 | 144.2
1842.1 | 1767.1 | 127.5 | 83.7 | 144.1
1843.1 | 1768.1 | 127.5 | 83.8 | 143.9
1844.1 | 1769.1 | 127.4 | 83.5 | 143.8
1845.1 | 1770.1 | 127.3 | 83.6 | 143.6
1846.1 | 1771.1 | 127.1 | 83.9 | 143.5
1847.1 | 1772.1 | 127 | 84 | 143.3
1848.1 | 1773.1 | 126.9 | 83.9 | 143.2
1849.1 | 1774.1 | 126.8 | 84.1 | 143.1
1850.1 | 1775.1 | 126.7 | 84.1 | 142.9
1851.1 | 1776.1 | 126.6 | 83.8 | 142.8
1852.1 | 1777.1 | 126.5 | 83.1 | 142.6
1853.1 | 1778.1 | 126.4 | 82.5 | 142.5
1854.1 | 1779.1 | 126.3 | 81.9 | 142.3
1855.1 | 1780.1 | 126.2 | 81.4 | 142.2
1856.1 | 1781.1 | 126.1 | 81.1 | 142
1857.1 | 1782.1 | 126 | 81 | 141.9
1858.1 | 1783.1 | 126 | 81.4 | 141.7
1859.1 | 1784.1 | 125.8 | 81.7 | 141.6
1860.1 | 1785.1 | 125.7 | 81.4 | 141.5
1861.1 | 1786.1 | 125.6 | 80.9 | 141.3
1862.1 | 1787.1 | 125.5 | 80.4 | 141.2
1863.1 | 1788.1 | 125.4 | 79.8 | 141
1864.1 | 1789.1 | 125.3 | 79.6 | 140.9
1865.1 | 1790.1 | 125.2 | 79.7 | 140.8
1866.1 | 1791.1 | 125.1 | 79.9 | 140.7
1867.1 | 1792.1 | 125 | 79.5 | 140.5
1868.1 | 1793.1 | 124.8 | 78.9 | 140.4
1869.1 | 1794.1 | 124.7 | 78.4 | 140.2
1870.1 | 1795.1 | 124.6 | 78.7 | 140.1
1871.1 | 1796.1 | 124.5 | 78.8 | 140
1872.1 | 1797.1 | 124.4 | 79.1 | 139.8
1873.1 | 1798.1 | 124.2 | 79.4 | 139.7
1874.1 | 1799.1 | 124.1 | 79.6 | 139.5
1875.1 | 1800.1 | 124 | 79.7 | 139.4
1876.1 | 1801.1 | 123.9 | 79.8 | 139.2
1877.1 | 1802.1 | 123.8 | 79.5 | 139.1
1878.1 | 1803.1 | 123.7 | 79.8 | 138.9
1879.1 | 1804.1 | 123.6 | 80 | 138.8
1880.1 | 1805.1 | 123.5 | 79.9 | 138.7
1881.1 | 1806.1 | 123.4 | 80 | 138.6
1882.1 | 1807.1 | 123.3 | 80 | 138.4
1883.1 | 1808.1 | 123.2 | 79.8 | 138.3
1884.1 | 1809.1 | 123.1 | 79.5 | 138.1
1885.1 | 1810.1 | 123.1 | 79.2 | 138
1886.1 | 1811.1 | 123 | 79.1 | 137.9
1887.1 | 1812.1 | 122.9 | 79.2 | 137.7
1888.1 | 1813.1 | 122.8 | 79.1 | 137.6
1889.1 | 1814.1 | 122.7 | 79.1 | 137.5
1890.1 | 1815.1 | 122.6 | 79.4 | 137.3
1891.1 | 1816.1 | 122.6 | 79.3 | 137.2
1892.1 | 1817.1 | 122.5 | 79.6 | 137.1
1893.1 | 1818.1 | 122.4 | 79.6 | 136.9
1894.1 | 1819.1 | 122.3 | 79.5 | 136.8
1895.1 | 1820.1 | 122.2 | 79.4 | 136.7
1896.1 | 1821.1 | 122.1 | 79.5 | 136.5
1897.1 | 1822.1 | 122 | 79.5 | 136.4
1898.1 | 1823.1 | 121.9 | 79.4 | 136.3
1899.1 | 1824.1 | 121.8 | 79.7 | 136.2
1900.1 | 1825.1 | 121.7 | 79.8 | 136
1901.1 | 1826.1 | 121.6 | 79.6 | 135.9
1902.1 | 1827.1 | 121.5 | 79.3 | 135.8
1903.1 | 1828.1 | 121.4 | 79.2 | 135.6
1904.1 | 1829.1 | 121.3 | 79.2 | 135.5
1905.1 | 1830.1 | 121.1 | 79.3 | 135.4
1906.1 | 1831.1 | 121 | 79 | 135.3
1907.1 | 1832.1 | 120.9 | 79 | 135.1
1908.1 | 1833.1 | 120.8 | 79.1 | 135
1909.1 | 1834.1 | 120.8 | 78.8 | 134.9
1910.1 | 1835.1 | 120.7 | 79 | 134.7
1911.1 | 1836.1 | 120.6 | 78.8 | 134.6
1912.1 | 1837.1 | 120.6 | 78.6 | 134.5
1913.1 | 1838.1 | 120.5 | 78.5 | 134.3
1914.1 | 1839.1 | 120.3 | 78.5 | 134.2
1915.1 | 1840.1 | 120.3 | 78.7 | 134.1
1916.1 | 1841.1 | 120.2 | 78.7 | 134
1917.1 | 1842.1 | 120.1 | 78.9 | 133.8
1918.1 | 1843.1 | 120 | 79.1 | 133.7
1919.1 | 1844.1 | 119.9 | 79.2 | 133.6
1920.1 | 1845.1 | 119.8 | 79.2 | 133.4
1921.1 | 1846.1 | 119.6 | 79.2 | 133.3
1922.1 | 1847.1 | 119.5 | 79.2 | 133.2
1923.1 | 1848.1 | 119.4 | 79.2 | 133.1
1924.1 | 1849.1 | 119.3 | 78.8 | 132.9
1925.1 | 1850.1 | 119.2 | 78.8 | 132.8
1926.1 | 1851.1 | 119.1 | 78.7 | 132.7
1927.1 | 1852.1 | 119 | 78.8 | 132.6
1928.1 | 1853.1 | 118.8 | 78.9 | 132.5
1929.1 | 1854.1 | 118.6 | 78.8 | 132.3
1930.1 | 1855.1 | 118.5 | 78.7 | 132.2
1931.1 | 1856.1 | 118.4 | 78.6 | 132
1932.1 | 1857.1 | 118.3 | 78.2 | 131.9
1933.1 | 1858.1 | 118.2 | 78.1 | 131.8
1934.1 | 1859.1 | 118 | 77.9 | 131.7
1935.1 | 1860.1 | 117.9 | 77.9 | 131.6
1936.1 | 1861.1 | 117.7 | 77.9 | 131.5
1937.1 | 1862.1 | 117.6 | 78.1 | 131.3
1938.1 | 1863.1 | 117.5 | 77.7 | 131.2
1939.1 | 1864.1 | 117.4 | 77.4 | 131.1
1940.1 | 1865.1 | 117.3 | 77.6 | 131
1941.1 | 1866.1 | 117.2 | 77.8 | 130.8
1942.1 | 1867.1 | 117.1 | 78 | 130.7
1943.1 | 1868.1 | 116.9 | 77.9 | 130.6
1944.1 | 1869.1 | 116.8 | 77.9 | 130.5
1945.1 | 1870.1 | 116.8 | 77.9 | 130.4
1946.1 | 1871.1 | 116.7 | 78 | 130.3
1947.1 | 1872.1 | 116.6 | 77.9 | 130.1
1948.1 | 1873.1 | 116.5 | 78 | 130
1949.1 | 1874.1 | 116.4 | 77.9 | 129.9
1950.1 | 1875.1 | 116.3 | 77.7 | 129.8
1951.1 | 1876.1 | 116.3 | 77.7 | 129.7
1952.1 | 1877.1 | 116.2 | 77.8 | 129.5
1953.1 | 1878.1 | 116.2 | 77.9 | 129.4
1954.1 | 1879.1 | 116.1 | 77.8 | 129.3
1955.1 | 1880.1 | 116 | 77.4 | 129.2
1956.1 | 1881.1 | 116 | 77.1 | 129
1957.1 | 1882.1 | 115.9 | 76.7 | 128.9
1958.1 | 1883.1 | 115.8 | 76.2 | 128.8
1959.1 | 1884.1 | 115.7 | 76.3 | 128.7
1960.1 | 1885.1 | 115.6 | 75.9 | 128.6
1961.1 | 1886.1 | 115.5 | 75.8 | 128.4
1962.1 | 1887.1 | 115.4 | 75.8 | 128.3
1963.1 | 1888.1 | 115.3 | 75.7 | 128.2
1964.1 | 1889.1 | 115.2 | 75.8 | 128.1
1965.1 | 1890.1 | 115.1 | 75.9 | 128
1966.1 | 1891.1 | 115 | 76 | 127.9
1967.1 | 1892.1 | 114.9 | 76.1 | 127.7
1968.1 | 1893.1 | 114.7 | 76.2 | 127.6
1969.1 | 1894.1 | 114.6 | 76.3 | 127.5
1970.1 | 1895.1 | 114.5 | 76.3 | 127.4
1971.1 | 1896.1 | 114.4 | 76.3 | 127.3
1972.1 | 1897.1 | 114.3 | 76.4 | 127.2
1973.1 | 1898.1 | 114.3 | 76.3 | 127
1974.1 | 1899.1 | 114.2 | 76.3 | 126.9
1975.1 | 1900.1 | 114.1 | 76.3 | 126.8
1976.1 | 1901.1 | 114 | 76.3 | 126.7
1977.1 | 1902.1 | 113.9 | 76.3 | 126.6
1978.1 | 1903.1 | 113.8 | 76.2 | 126.5
1979.1 | 1904.1 | 113.7 | 76.1 | 126.4
1980.1 | 1905.1 | 113.7 | 75.9 | 126.2
1981.1 | 1906.1 | 113.6 | 75.8 | 126.1
1982.1 | 1907.1 | 113.5 | 75.4 | 126
1983.1 | 1908.1 | 113.4 | 75 | 125.9
1984.1 | 1909.1 | 113.2 | 74.7 | 125.8
1985.1 | 1910.1 | 113.1 | 74.1 | 125.7
1986.1 | 1911.1 | 113 | 73.4 | 125.5
1987.1 | 1912.1 | 112.9 | 73.2 | 125.4
1988.1 | 1913.1 | 112.8 | 73.1 | 125.3
1989.1 | 1914.1 | 112.7 | 73.1 | 125.2
1990.1 | 1915.1 | 112.7 | 73.4 | 125
1991.1 | 1916.1 | 112.6 | 73.5 | 125
1992.1 | 1917.1 | 112.5 | 73.6 | 124.8
1993.1 | 1918.1 | 112.4 | 73.6 | 124.7
1994.1 | 1919.1 | 112.3 | 73.3 | 124.6
1995.1 | 1920.1 | 112.2 | 73.3 | 124.5
1996.1 | 1921.1 | 112.1 | 73.1 | 124.4
1997.1 | 1922.1 | 112 | 72.8 | 124.3
1998.1 | 1923.1 | 111.9 | 72.4 | 124.1
1999.1 | 1924.1 | 111.9 | 72.2 | 124
2000.1 | 1925.1 | 111.8 | 72.2 | 123.9
2001.1 | 1926.1 | 111.7 | 72.2 | 123.8
2002.1 | 1927.1 | 111.6 | 72.1 | 123.7
2003.1 | 1928.1 | 111.5 | 72.1 | 123.6
2004.1 | 1929.1 | 111.5 | 71.8 | 123.5
2005.1 | 1930.1 | 111.4 | 71.5 | 123.3
2006.1 | 1931.1 | 111.3 | 71.5 | 123.2
2007.1 | 1932.1 | 111.2 | 71.3 | 123.1
2008.1 | 1933.1 | 111.2 | 70.9 | 123
2009.1 | 1934.1 | 111.1 | 70.4 | 122.9
2010.1 | 1935.1 | 111 | 70 | 122.8
2011.1 | 1936.1 | 110.9 | 69.8 | 122.7
2012.1 | 1937.1 | 110.8 | 69.5 | 122.6
2013.1 | 1938.1 | 110.8 | 69.2 | 122.5
2014.1 | 1939.1 | 110.7 | 69 | 122.3
2015.1 | 1940.1 | 110.6 | 68.8 | 122.2
2016.1 | 1941.1 | 110.5 | 68.4 | 122.1
2017.1 | 1942.1 | 110.4 | 68.1 | 122
2018.1 | 1943.1 | 110.3 | 68 | 121.9
2019.1 | 1944.1 | 110.2 | 68 | 121.8
2020.1 | 1945.1 | 110.1 | 68.6 | 121.7
2021.1 | 1946.1 | 109.9 | 68.9 | 121.6
2022.1 | 1947.1 | 109.8 | 69.1 | 121.5
2023.1 | 1948.1 | 109.7 | 69.5 | 121.4
2024.1 | 1949.1 | 109.6 | 69.6 | 121.3
2025.1 | 1950.1 | 109.5 | 69.3 | 121.1
2026.1 | 1951.1 | 109.4 | 68.8 | 121
2027.1 | 1952.1 | 109.4 | 68.4 | 120.9
2028.1 | 1953.1 | 109.3 | 68.4 | 120.8
2029.1 | 1954.1 | 109.2 | 68.5 | 120.7
2030.1 | 1955.1 | 109.1 | 68.5 | 120.6
2031.1 | 1956.1 | 109 | 68.1 | 120.5
2032.1 | 1957.1 | 108.9 | 67.8 | 120.4
2033.1 | 1958.1 | 108.8 | 67.7 | 120.3
2034.1 | 1959.1 | 108.7 | 67.9 | 120.2
2035.1 | 1960.1 | 108.7 | 67.6 | 120.1
2036.1 | 1961.1 | 108.5 | 67.5 | 119.9
2037.1 | 1962.1 | 108.4 | 67.4 | 119.8
2038.1 | 1963.1 | 108.3 | 67.7 | 119.7
2039.1 | 1964.1 | 108.3 | 67.8 | 119.6
2040.1 | 1965.1 | 108.2 | 68 | 119.5
2041.1 | 1966.1 | 108.1 | 68.3 | 119.4
2042.1 | 1967.1 | 108 | 68.4 | 119.3
2043.1 | 1968.1 | 107.8 | 68.4 | 119.2
2044.1 | 1969.1 | 107.7 | 68.6 | 119.1
2045.1 | 1970.1 | 107.6 | 68.7 | 119
2046.1 | 1971.1 | 107.5 | 68.8 | 118.9
2047.1 | 1972.1 | 107.5 | 68.8 | 118.8
2048.1 | 1973.1 | 107.4 | 68.6 | 118.7
2049.1 | 1974.1 | 107.2 | 68.7 | 118.6
2050.1 | 1975.1 | 107.1 | 69 | 118.5
2051.1 | 1976.1 | 107 | 69.2 | 118.4
2052.1 | 1977.1 | 106.9 | 69.3 | 118.3
2053.1 | 1978.1 | 106.8 | 69.4 | 118.2
2054.1 | 1979.1 | 106.7 | 69.3 | 118
2055.1 | 1980.1 | 106.7 | 68.9 | 118
2056.1 | 1981.1 | 106.6 | 68.6 | 117.9
2057.1 | 1982.1 | 106.4 | 68.5 | 117.8
2058.1 | 1983.1 | 106.3 | 68.6 | 117.6
2059.1 | 1984.1 | 106.3 | 69 | 117.5
2060.1 | 1985.1 | 106.2 | 69.2 | 117.4
2061.1 | 1986.1 | 106.2 | 69.3 | 117.3
2062.1 | 1987.1 | 106.1 | 69.1 | 117.3
2063.1 | 1988.1 | 106.1 | 68.7 | 117.2
2064.1 | 1989.1 | 106 | 68.8 | 117
2065.1 | 1990.1 | 105.9 | 68.9 | 116.9
2066.1 | 1991.1 | 105.9 | 69.2 | 116.9
2067.1 | 1992.1 | 105.8 | 69.1 | 116.7
2068.1 | 1993.1 | 105.7 | 69 | 116.7
2069.1 | 1994.1 | 105.6 | 69 | 116.6
2070.1 | 1995.1 | 105.6 | 69 | 116.5
2071.1 | 1996.1 | 105.5 | 69.2 | 116.3
2072.1 | 1997.1 | 105.4 | 69.1 | 116.3

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 31 |  |  | 2006-07-27 | 13:16
38925.5519 | 1 | 0 | 1 | VitaLink | 7-C | Tray
38925.5526 | 1 | 0 | 1 | 700 C | 50.8 kW/m2 |  | Conductors
38925.5533 | 1 | 0 | 1
38925.554 | 1 | 0 | 1
38925.5547 | 1 | 0 | 1
38925.5553 | 1 | 0 | 1
38925.556 | 1 | 0 | 1
38925.5567 | 1 | 0 | 1
38925.5574 | 1 | 0 | 1
38925.5581 | 1 | 0 | 1
38925.5587 | 1 | 0 | 1
38925.5594 | 1 | 0 | 1
38925.5601 | 1 | 0 | 1
38925.5608 | 1 | 0 | 1
38925.5615 | 1 | 0 | 1
38925.5621 | 1 | 0 | 1
38925.5628 | 1 | 0 | 1
38925.5635 | 1 | 0 | 1
38925.5642 | 1 | 0 | 1
38925.5649 | 1 | 0 | 1
38925.5655 | 1 | 0 | 1
38925.5662 | 1 | 0 | 1
38925.5669 | 1 | 0 | 1
38925.5676 | 1 | 0 | 1
38925.5683 | 1 | 0 | 1
38925.5689 | 1 | 0 | 1
38925.5696 | 1 | 0 | 1
38925.5703 | 1 | 0 | 1
38925.571 | 1 | 0 | 1
38925.5717 | 1 | 0 | 1
38925.5723 | 6 | 0 | 1
38925.573 | 7 | 0 | 1
38925.5737 | 6 | 0 | 1
38925.5744 | 7 | 0 | 1
38925.5751 | 7 | 0 | 1
38925.5758 | 7 | 0 | 1
1
38925.552 | 1 | 0 | 2
38925.5526 | 1 | 0 | 2
38925.5533 | 1 | 0 | 2
38925.554 | 1 | 0 | 2
38925.5547 | 1 | 0 | 2
38925.5554 | 1 | 0 | 2
38925.556 | 1 | 0 | 2
38925.5567 | 1 | 0 | 2
38925.5574 | 1 | 0 | 2
38925.5581 | 1 | 0 | 2
38925.5588 | 1 | 0 | 2
38925.5594 | 1 | 0 | 2
38925.5601 | 1 | 0 | 2
38925.5608 | 1 | 0 | 2
38925.5615 | 1 | 0 | 2
38925.5622 | 1 | 0 | 2
38925.5628 | 1 | 0 | 2
38925.5635 | 1 | 0 | 2
38925.5642 | 1 | 0 | 2
38925.5649 | 1 | 0 | 2
38925.5656 | 1 | 0 | 2
38925.5662 | 1 | 0 | 2
38925.5669 | 1 | 0 | 2
38925.5676 | 1 | 0 | 2
38925.5683 | 1 | 0 | 2
38925.569 | 1 | 0 | 2
38925.5696 | 1 | 0 | 2
38925.5703 | 1 | 0 | 2
38925.571 | 1 | 0 | 2
38925.5717 | 1 | 0 | 2
38925.5724 | 5 | 0 | 2
38925.573 | 5 | 0 | 2
38925.5737 | 4 | 0 | 2
38925.5744 | 5 | 0 | 2
38925.5751 | 5 | 0 | 2
38925.5758 | 6 | 0 | 2
2
38925.552 | 1 | 0 | 3
38925.5527 | 1 | 0 | 3
38925.5533 | 1 | 0 | 3
38925.554 | 1 | 0 | 3
38925.5547 | 1 | 0 | 3
38925.5554 | 1 | 0 | 3
38925.5561 | 1 | 0 | 3
38925.5567 | 1 | 0 | 3
38925.5574 | 1 | 0 | 3
38925.5581 | 1 | 0 | 3
38925.5588 | 1 | 0 | 3
38925.5595 | 1 | 0 | 3
38925.5601 | 1 | 0 | 3
38925.5608 | 1 | 0 | 3
38925.5615 | 1 | 0 | 3
38925.5622 | 1 | 0 | 3
38925.5629 | 1 | 0 | 3
38925.5635 | 1 | 0 | 3
38925.5642 | 1 | 0 | 3
38925.5649 | 1 | 0 | 3
38925.5656 | 1 | 0 | 3
38925.5663 | 1 | 0 | 3
38925.5669 | 1 | 0 | 3
38925.5676 | 1 | 0 | 3
38925.5683 | 1 | 0 | 3
38925.569 | 1 | 0 | 3
38925.5697 | 1 | 0 | 3
38925.5703 | 1 | 0 | 3
38925.571 | 1 | 0 | 3
38925.5717 | 1 | 0 | 3
38925.5724 | 3 | 0 | 3
38925.5731 | 4 | 0 | 3
38925.5737 | 4 | 0 | 3
38925.5744 | 4 | 0 | 3
38925.5751 | 4 | 0 | 3
38925.5758 | 4 | 0 | 3
3
38925.552 | 1 | 0 | 4
38925.5527 | 1 | 0 | 4
38925.5533 | 2 | 0 | 4
38925.554 | 1 | 0 | 4
38925.5547 | 1 | 0 | 4
38925.5554 | 1 | 0 | 4
38925.5561 | 2 | 0 | 4
38925.5567 | 1 | 0 | 4
38925.5574 | 1 | 0 | 4
38925.5581 | 1 | 0 | 4
38925.5588 | 1 | 0 | 4
38925.5595 | 1 | 0 | 4
38925.5602 | 1 | 0 | 4
38925.5608 | 1 | 1 | 4
38925.5615 | 1 | 0 | 4
38925.5622 | 1 | 0 | 4
38925.5629 | 1 | 0 | 4
38925.5636 | 1 | 0 | 4
38925.5642 | 1 | 0 | 4
38925.5649 | 1 | 0 | 4
38925.5656 | 1 | 0 | 4
38925.5663 | 1 | 0 | 4
38925.567 | 1 | 0 | 4
38925.5676 | 1 | 0 | 4
38925.5683 | 1 | 0 | 4
38925.569 | 1 | 0 | 4
38925.5697 | 1 | 0 | 4
38925.5704 | 1 | 0 | 4
38925.571 | 1 | 0 | 4
38925.5717 | 1 | 0 | 4
38925.5724 | 3 | 0 | 4
38925.5731 | 3 | 0 | 4
38925.5738 | 4 | 0 | 4
38925.5744 | 4 | 0 | 4
38925.5751 | 4 | 0 | 4
38925.5758 | 4 | 0 | 4
4
38925.552 | 1 | 0 | 5
38925.5527 | 2 | 0 | 5
38925.5534 | 1 | 0 | 5
38925.554 | 1 | 0 | 5
38925.5547 | 1 | 0 | 5
38925.5554 | 1 | 0 | 5
38925.5561 | 1 | 0 | 5
38925.5568 | 2 | 0 | 5
38925.5574 | 1 | 0 | 5
38925.5581 | 1 | 0 | 5
38925.5588 | 1 | 0 | 5
38925.5595 | 1 | 0 | 5
38925.5602 | 1 | 0 | 5
38925.5608 | 1 | 0 | 5
38925.5615 | 1 | 0 | 5
38925.5622 | 1 | 0 | 5
38925.5629 | 1 | 0 | 5
38925.5636 | 1 | 0 | 5
38925.5642 | 1 | 0 | 5
38925.5649 | 1 | 0 | 5
38925.5656 | 1 | 0 | 5
38925.5663 | 1 | 0 | 5
38925.567 | 1 | 0 | 5
38925.5677 | 1 | 0 | 5
38925.5683 | 1 | 0 | 5
38925.569 | 1 | 0 | 5
38925.5697 | 1 | 0 | 5
38925.5704 | 1 | 0 | 5
38925.5711 | 1 | 0 | 5
38925.5717 | 1 | 0 | 5
38925.5724 | 3 | 0 | 5
38925.5731 | 3 | 0 | 5
38925.5738 | 3 | 0 | 5
38925.5745 | 3 | 0 | 5
38925.5751 | 3 | 0 | 5
38925.5758 | 4 | 0 | 5
5
38925.552 | 1 | 0 | 6
38925.5527 | 1 | 0 | 6
38925.5534 | 1 | 0 | 6
38925.5541 | 1 | 0 | 6
38925.5547 | 1 | 0 | 6
38925.5554 | 1 | 1 | 6
38925.5561 | 1 | 0 | 6
38925.5568 | 1 | 0 | 6
38925.5575 | 1 | 0 | 6
38925.5581 | 1 | 0 | 6
38925.5588 | 1 | 0 | 6
38925.5595 | 1 | 0 | 6
38925.5602 | 1 | 0 | 6
38925.5609 | 1 | 0 | 6
38925.5615 | 1 | 0 | 6
38925.5622 | 1 | 0 | 6
38925.5629 | 1 | 0 | 6
38925.5636 | 1 | 0 | 6
38925.5643 | 1 | 0 | 6
38925.5649 | 1 | 0 | 6
38925.5656 | 1 | 0 | 6
38925.5663 | 1 | 0 | 6
38925.567 | 1 | 0 | 6
38925.5677 | 1 | 0 | 6
38925.5683 | 1 | 0 | 6
38925.569 | 1 | 0 | 6
38925.5697 | 1 | 0 | 6
38925.5704 | 1 | 0 | 6
38925.5711 | 1 | 0 | 6
38925.5717 | 1 | 0 | 6
38925.5724 | 2 | 0 | 6
38925.5731 | 3 | 0 | 6
38925.5738 | 3 | 0 | 6
38925.5745 | 3 | 0 | 6
38925.5752 | 3 | 0 | 6
38925.5758 | 3 | 0 | 6
6
38925.552 | 1 | 0 | 7
38925.5527 | 1 | 0 | 7
38925.5534 | 1 | 0 | 7
38925.5541 | 1 | 0 | 7
38925.5548 | 1 | 0 | 7
38925.5554 | 1 | 0 | 7
38925.5561 | 1 | 0 | 7
38925.5568 | 1 | 0 | 7
38925.5575 | 1 | 0 | 7
38925.5582 | 1 | 0 | 7
38925.5588 | 1 | 0 | 7
38925.5595 | 1 | 1 | 7
38925.5602 | 1 | 0 | 7
38925.5609 | 1 | 0 | 7
38925.5616 | 1 | 0 | 7
38925.5622 | 1 | 0 | 7
38925.5629 | 1 | 0 | 7
38925.5636 | 1 | 0 | 7
38925.5643 | 1 | 0 | 7
38925.565 | 1 | 0 | 7
38925.5656 | 1 | 0 | 7
38925.5663 | 1 | 0 | 7
38925.567 | 1 | 0 | 7
38925.5677 | 1 | 0 | 7
38925.5684 | 1 | 0 | 7
38925.5691 | 1 | 0 | 7
38925.5697 | 1 | 0 | 7
38925.5704 | 1 | 0 | 7
38925.5711 | 1 | 0 | 7
38925.5718 | 1 | 0 | 7
38925.5724 | 3 | 0 | 7
38925.5731 | 3 | 0 | 7
38925.5738 | 3 | 0 | 7
38925.5745 | 3 | 0 | 7
38925.5752 | 3 | 0 | 7
38925.5758 | 3 | 0 | 7
7
38925.552 | 1 | 0 | 8
38925.5527 | 2 | 0 | 8
38925.5534 | 1 | 0 | 8
38925.5541 | 2 | 0 | 8
38925.5548 | 1 | 0 | 8
38925.5555 | 1 | 0 | 8
38925.5561 | 1 | 1 | 8
38925.5568 | 1 | 0 | 8
38925.5575 | 1 | 1 | 8
38925.5582 | 1 | 0 | 8
38925.5589 | 1 | 0 | 8
38925.5595 | 1 | 0 | 8
38925.5602 | 1 | 0 | 8
38925.5609 | 1 | 0 | 8
38925.5616 | 1 | 0 | 8
38925.5623 | 1 | 0 | 8
38925.5629 | 1 | 0 | 8
38925.5636 | 1 | 0 | 8
38925.5643 | 1 | 0 | 8
38925.565 | 1 | 0 | 8
38925.5657 | 1 | 0 | 8
38925.5663 | 1 | 0 | 8
38925.567 | 1 | 0 | 8
38925.5677 | 1 | 0 | 8
38925.5684 | 1 | 0 | 8
38925.5691 | 1 | 0 | 8
38925.5697 | 1 | 0 | 8
38925.5704 | 1 | 0 | 8
38925.5711 | 1 | 0 | 8
38925.5718 | 1 | 0 | 8
38925.5725 | 2 | 0 | 8
38925.5731 | 3 | 0 | 8
38925.5738 | 3 | 0 | 8
38925.5745 | 3 | 0 | 8
38925.5752 | 3 | 0 | 8
38925.5759 | 3 | 0 | 8
8
38925.5521 | 1 | 0 | 9
38925.5527 | 1 | 0 | 9
38925.5534 | 1 | 0 | 9
38925.5541 | 1 | 1 | 9
38925.5548 | 1 | 0 | 9
38925.5555 | 1 | 0 | 9
38925.5561 | 1 | 0 | 9
38925.5568 | 1 | 0 | 9
38925.5575 | 1 | 0 | 9
38925.5582 | 1 | 0 | 9
38925.5589 | 1 | 0 | 9
38925.5595 | 1 | 0 | 9
38925.5602 | 1 | 0 | 9
38925.5609 | 1 | 0 | 9
38925.5616 | 1 | 0 | 9
38925.5623 | 1 | 0 | 9
38925.563 | 1 | 0 | 9
38925.5636 | 1 | 0 | 9
38925.5643 | 1 | 0 | 9
38925.565 | 1 | 0 | 9
38925.5657 | 1 | 0 | 9
38925.5664 | 1 | 0 | 9
38925.567 | 1 | 0 | 9
38925.5677 | 1 | 0 | 9
38925.5684 | 1 | 0 | 9
38925.5691 | 1 | 0 | 9
38925.5698 | 1 | 0 | 9
38925.5704 | 1 | 0 | 9
38925.5711 | 1 | 0 | 9
38925.5718 | 1 | 0 | 9
38925.5725 | 2 | 0 | 9
38925.5732 | 3 | 0 | 9
38925.5738 | 3 | 0 | 9
38925.5745 | 3 | 0 | 9
38925.5752 | 2 | 0 | 9
38925.5759 | 3 | 0 | 9
9
38925.5521 | 1 | 0 | 10
38925.5528 | 1 | 0 | 10
38925.5534 | 1 | 0 | 10
38925.5541 | 1 | 0 | 10
38925.5548 | 1 | 0 | 10
38925.5555 | 2 | 0 | 10
38925.5562 | 1 | 0 | 10
38925.5568 | 2 | 0 | 10
38925.5575 | 1 | 0 | 10
38925.5582 | 1 | 1 | 10
38925.5589 | 1 | 0 | 10
38925.5596 | 1 | 0 | 10
38925.5602 | 1 | 0 | 10
38925.5609 | 1 | 1 | 10
38925.5616 | 1 | 0 | 10
38925.5623 | 1 | 0 | 10
38925.563 | 1 | 0 | 10
38925.5636 | 1 | 0 | 10
38925.5643 | 1 | 0 | 10
38925.565 | 1 | 0 | 10
38925.5657 | 1 | 0 | 10
38925.5664 | 1 | 0 | 10
38925.567 | 1 | 0 | 10
38925.5677 | 1 | 0 | 10
38925.5684 | 1 | 0 | 10
38925.5691 | 1 | 0 | 10
38925.5698 | 1 | 0 | 10
38925.5705 | 1 | 0 | 10
38925.5711 | 1 | 0 | 10
38925.5718 | 2309 | 0 | 10
38925.5725 | 1964 | 0 | 10
38925.5732 | 2505 | 0 | 10
38925.5739 | 2163 | 0 | 10
38925.5745 | 2392 | 0 | 10
38925.5752 | 2085 | 0 | 10
38925.5759 | 2240 | 0 | 10
10
38925.5521 | 1 | 0 | 11
38925.5528 | 1 | 0 | 11
38925.5535 | 1 | 0 | 11
38925.5541 | 1 | 0 | 11
38925.5548 | 1 | 0 | 11
38925.5555 | 1 | 0 | 11
38925.5562 | 1 | 1 | 11
38925.5569 | 1 | 0 | 11
38925.5575 | 1 | 0 | 11
38925.5582 | 1 | 0 | 11
38925.5589 | 1 | 0 | 11
38925.5596 | 1 | 0 | 11
38925.5603 | 1 | 0 | 11
38925.5609 | 1 | 0 | 11
38925.5616 | 1 | 0 | 11
38925.5623 | 1 | 0 | 11
38925.563 | 1 | 0 | 11
38925.5637 | 1 | 0 | 11
38925.5644 | 1 | 0 | 11
38925.565 | 1 | 0 | 11
38925.5657 | 1 | 0 | 11
38925.5664 | 1 | 0 | 11
38925.5671 | 1 | 0 | 11
38925.5678 | 1 | 0 | 11
38925.5684 | 1 | 0 | 11
38925.5691 | 1 | 0 | 11
38925.5698 | 1 | 0 | 11
38925.5705 | 1 | 0 | 11
38925.5712 | 1 | 0 | 11
38925.5718 | 7 | 0 | 11
38925.5725 | 7 | 0 | 11
38925.5732 | 7 | 0 | 11
38925.5739 | 7 | 0 | 11
38925.5745 | 8 | 0 | 11
38925.5752 | 8 | 0 | 11
38925.5759 | 7 | 0 | 11
11
38925.5521 | 2 | 0 | 12
38925.5528 | 1 | 0 | 12
38925.5535 | 1 | 0 | 12
38925.5542 | 1 | 0 | 12
38925.5548 | 1 | 0 | 12
38925.5555 | 1 | 0 | 12
38925.5562 | 1 | 0 | 12
38925.5569 | 1 | 0 | 12
38925.5576 | 1 | 0 | 12
38925.5582 | 1 | 0 | 12
38925.5589 | 1 | 0 | 12
38925.5596 | 1 | 0 | 12
38925.5603 | 1 | 0 | 12
38925.561 | 1 | 0 | 12
38925.5616 | 1 | 0 | 12
38925.5623 | 1 | 0 | 12
38925.563 | 1 | 0 | 12
38925.5637 | 1 | 0 | 12
38925.5644 | 1 | 0 | 12
38925.565 | 1 | 0 | 12
38925.5657 | 1 | 1 | 12
38925.5664 | 1 | 0 | 12
38925.5671 | 1 | 0 | 12
38925.5678 | 1 | 0 | 12
38925.5684 | 1 | 0 | 12
38925.5691 | 1 | 0 | 12
38925.5698 | 1 | 0 | 12
38925.5705 | 1 | 0 | 12
38925.5712 | 1 | 0 | 12
38925.5719 | 5 | 0 | 12
38925.5725 | 5 | 0 | 12
38925.5732 | 5 | 0 | 12
38925.5739 | 5 | 0 | 12
38925.5746 | 5 | 0 | 12
38925.5753 | 5 | 0 | 12
38925.5759 | 5 | 0 | 12
12
38925.5521 | 1 | 0 | 13
38925.5528 | 1 | 0 | 13
38925.5535 | 1 | 0 | 13
38925.5542 | 1 | 0 | 13
38925.5548 | 1 | 0 | 13
38925.5555 | 1 | 0 | 13
38925.5562 | 1 | 0 | 13
38925.5569 | 1 | 0 | 13
38925.5576 | 1 | 0 | 13
38925.5583 | 2 | 0 | 13
38925.5589 | 1 | 0 | 13
38925.5596 | 1 | 0 | 13
38925.5603 | 1 | 0 | 13
38925.561 | 1 | 0 | 13
38925.5617 | 1 | 0 | 13
38925.5623 | 1 | 0 | 13
38925.563 | 1 | 0 | 13
38925.5637 | 1 | 0 | 13
38925.5644 | 1 | 0 | 13
38925.5651 | 1 | 0 | 13
38925.5657 | 1 | 0 | 13
38925.5664 | 1 | 0 | 13
38925.5671 | 1 | 0 | 13
38925.5678 | 1 | 0 | 13
38925.5685 | 1 | 0 | 13
38925.5691 | 1 | 0 | 13
38925.5698 | 1 | 0 | 13
38925.5705 | 1 | 0 | 13
38925.5712 | 1 | 0 | 13
38925.5719 | 6 | 0 | 13
38925.5725 | 4 | 0 | 13
38925.5732 | 4 | 0 | 13
38925.5739 | 4 | 0 | 13
38925.5746 | 4 | 0 | 13
38925.5753 | 5 | 0 | 13
38925.5759 | 4 | 0 | 13
13
38925.5522 | 1 | 0 | 14
38925.5528 | 1 | 0 | 14
38925.5535 | 1 | 0 | 14
38925.5542 | 1 | 0 | 14
38925.5549 | 1 | 0 | 14
38925.5556 | 1 | 0 | 14
38925.5562 | 1 | 0 | 14
38925.5569 | 1 | 0 | 14
38925.5576 | 1 | 0 | 14
38925.5583 | 1 | 0 | 14
38925.5589 | 1 | 0 | 14
38925.5596 | 1 | 0 | 14
38925.5603 | 1 | 0 | 14
38925.561 | 1 | 0 | 14
38925.5617 | 1 | 0 | 14
38925.5623 | 1 | 0 | 14
38925.563 | 1 | 0 | 14
38925.5637 | 2 | 0 | 14
38925.5644 | 1 | 0 | 14
38925.5651 | 1 | 0 | 14
38925.5658 | 1 | 0 | 14
38925.5664 | 1 | 0 | 14
38925.5671 | 1 | 0 | 14
38925.5678 | 1 | 0 | 14
38925.5685 | 1 | 0 | 14
38925.5692 | 1 | 0 | 14
38925.5698 | 1 | 0 | 14
38925.5705 | 1 | 0 | 14
38925.5712 | 1 | 0 | 14
38925.5719 | 3 | 0 | 14
38925.5726 | 3 | 0 | 14
38925.5732 | 3 | 0 | 14
38925.5739 | 3 | 0 | 14
38925.5746 | 3 | 0 | 14
38925.5753 | 4 | 0 | 14
38925.576 | 4 | 0 | 14
14
38925.5522 | 1 | 0 | 15
38925.5528 | 1 | 0 | 15
38925.5535 | 1 | 1 | 15
38925.5542 | 1 | 0 | 15
38925.5549 | 1 | 0 | 15
38925.5556 | 1 | 1 | 15
38925.5563 | 1 | 1 | 15
38925.5569 | 1 | 0 | 15
38925.5576 | 1 | 0 | 15
38925.5583 | 1 | 0 | 15
38925.559 | 1 | 0 | 15
38925.5597 | 1 | 0 | 15
38925.5603 | 1 | 0 | 15
38925.561 | 1 | 0 | 15
38925.5617 | 2 | 0 | 15
38925.5624 | 1 | 0 | 15
38925.5631 | 1 | 0 | 15
38925.5637 | 1 | 0 | 15
38925.5644 | 1 | 0 | 15
38925.5651 | 1 | 0 | 15
38925.5658 | 1 | 0 | 15
38925.5665 | 1 | 0 | 15
38925.5671 | 1 | 0 | 15
38925.5678 | 1 | 0 | 15
38925.5685 | 1 | 0 | 15
38925.5692 | 1 | 0 | 15
38925.5698 | 1 | 0 | 15
38925.5705 | 1 | 0 | 15
38925.5712 | 1 | 0 | 15
38925.5719 | 2 | 0 | 15
38925.5726 | 3 | 0 | 15
38925.5733 | 3 | 0 | 15
38925.5739 | 3 | 0 | 15
38925.5746 | 3 | 0 | 15
38925.5753 | 3 | 0 | 15
38925.576 | 3 | 0 | 15
15
38925.5522 | 1 | 0 | 16
38925.5529 | 1 | 0 | 16
38925.5535 | 2 | 0 | 16
38925.5542 | 1 | 0 | 16
38925.5549 | 1 | 0 | 16
38925.5556 | 1 | 0 | 16
38925.5563 | 1 | 0 | 16
38925.5569 | 1 | 0 | 16
38925.5576 | 1 | 0 | 16
38925.5583 | 1 | 0 | 16
38925.559 | 1 | 0 | 16
38925.5597 | 1 | 0 | 16
38925.5603 | 1 | 0 | 16
38925.561 | 1 | 0 | 16
38925.5617 | 1 | 0 | 16
38925.5624 | 1 | 0 | 16
38925.5631 | 1 | 0 | 16
38925.5638 | 1 | 0 | 16
38925.5644 | 1 | 0 | 16
38925.5651 | 1 | 1 | 16
38925.5658 | 1 | 0 | 16
38925.5665 | 1 | 0 | 16
38925.5672 | 1 | 0 | 16
38925.5678 | 1 | 0 | 16
38925.5685 | 1 | 0 | 16
38925.5692 | 1 | 0 | 16
38925.5699 | 1 | 0 | 16
38925.5706 | 1 | 0 | 16
38925.5712 | 1 | 0 | 16
38925.5719 | 2 | 0 | 16
38925.5726 | 3 | 0 | 16
38925.5733 | 3 | 0 | 16
38925.574 | 3 | 0 | 16
38925.5746 | 3 | 0 | 16
38925.5753 | 3 | 0 | 16
38925.576 | 3 | 0 | 16
16
38925.5522 | 1 | 0 | 17
38925.5529 | 1 | 0 | 17
38925.5536 | 1 | 0 | 17
38925.5542 | 1 | 0 | 17
38925.5549 | 1 | 0 | 17
38925.5556 | 1 | 0 | 17
38925.5563 | 1 | 2 | 17
38925.557 | 1 | 0 | 17
38925.5576 | 1 | 0 | 17
38925.5583 | 1 | 0 | 17
38925.559 | 1 | 0 | 17
38925.5597 | 1 | 0 | 17
38925.5604 | 1 | 0 | 17
38925.561 | 1 | 0 | 17
38925.5617 | 1 | 0 | 17
38925.5624 | 1 | 0 | 17
38925.5631 | 1 | 0 | 17
38925.5638 | 1 | 0 | 17
38925.5644 | 1 | 0 | 17
38925.5651 | 1 | 0 | 17
38925.5658 | 1 | 0 | 17
38925.5665 | 1 | 0 | 17
38925.5672 | 1 | 1 | 17
38925.5678 | 1 | 0 | 17
38925.5685 | 1 | 0 | 17
38925.5692 | 1 | 0 | 17
38925.5706 | 1 | 0 | 17
38925.5713 | 1 | 0 | 17
38925.5719 | 2 | 0 | 17
38925.5726 | 3 | 0 | 17
38925.5733 | 3 | 0 | 17
38925.574 | 3 | 0 | 17
38925.5747 | 2 | 0 | 17
38925.5753 | 3 | 0 | 17
38925.576 | 2 | 0 | 17
17
38925.5522 | 1 | 0 | 18
38925.5529 | 1 | 0 | 18
38925.5536 | 1 | 0 | 18
38925.5542 | 1 | 0 | 18
38925.5549 | 1 | 0 | 18
38925.5556 | 1 | 0 | 18
38925.5563 | 1 | 0 | 18
38925.557 | 1 | 0 | 18
38925.5577 | 1 | 0 | 18
38925.5583 | 1 | 0 | 18
38925.559 | 1 | 0 | 18
38925.5597 | 1 | 0 | 18
38925.5604 | 1 | 0 | 18
38925.5611 | 1 | 0 | 18
38925.5617 | 1 | 0 | 18
38925.5624 | 1 | 0 | 18
38925.5631 | 1 | 0 | 18
38925.5638 | 1 | 0 | 18
38925.5645 | 1 | 0 | 18
38925.5651 | 1 | 1 | 18
38925.5658 | 1 | 0 | 18
38925.5665 | 1 | 0 | 18
38925.5672 | 1 | 0 | 18
38925.5679 | 1 | 0 | 18
38925.5685 | 1 | 0 | 18
38925.5692 | 1 | 0 | 18
38925.5699 | 1 | 0 | 18
38925.5706 | 1 | 0 | 18
38925.5713 | 1 | 0 | 18
38925.5719 | 1 | 0 | 18
38925.5726 | 2 | 0 | 18
38925.5733 | 2 | 0 | 18
38925.574 | 2 | 0 | 18
38925.5747 | 3 | 0 | 18
38925.5753 | 3 | 0 | 18
38925.576 | 3 | 0 | 18
18
38925.5522 | 1 | 0 | 19
38925.5529 | 1 | 0 | 19
38925.5536 | 1 | 0 | 19
38925.5543 | 1 | 0 | 19
38925.555 | 1 | 0 | 19
38925.5556 | 1 | 0 | 19
38925.5563 | 1 | 0 | 19
38925.557 | 1 | 0 | 19
38925.5577 | 1 | 0 | 19
38925.5584 | 1 | 0 | 19
38925.559 | 1 | 0 | 19
38925.5597 | 1 | 0 | 19
38925.5604 | 1 | 0 | 19
38925.5611 | 1 | 0 | 19
38925.5618 | 1 | 0 | 19
38925.5624 | 1 | 0 | 19
38925.5631 | 1 | 0 | 19
38925.5638 | 1 | 0 | 19
38925.5645 | 1 | 0 | 19
38925.5652 | 1 | 0 | 19
38925.5658 | 1 | 0 | 19
38925.5665 | 1 | 0 | 19
38925.5672 | 1 | 0 | 19
38925.5679 | 1 | 0 | 19
38925.5686 | 1 | 0 | 19
38925.5692 | 1 | 0 | 19
38925.5699 | 1 | 0 | 19
38925.5706 | 1 | 0 | 19
38925.5713 | 1 | 0 | 19
38925.572 | 1 | 0 | 19
38925.5726 | 2 | 0 | 19
38925.5733 | 2 | 0 | 19
38925.574 | 3 | 0 | 19
38925.5747 | 3 | 0 | 19
38925.5754 | 3 | 0 | 19
38925.576 | 2 | 0 | 19
19
38925.5522 | 1 | 0 | 20
38925.5529 | 1 | 0 | 20
38925.5536 | 1 | 1 | 20
38925.5543 | 1 | 0 | 20
38925.555 | 1 | 0 | 20
38925.5556 | 1 | 0 | 20
38925.5563 | 1 | 0 | 20
38925.557 | 1 | 0 | 20
38925.5577 | 1 | 0 | 20
38925.5584 | 1 | 0 | 20
38925.5591 | 1 | 0 | 20
38925.5597 | 1 | 0 | 20
38925.5604 | 1 | 0 | 20
38925.5611 | 1 | 0 | 20
38925.5618 | 1 | 0 | 20
38925.5625 | 1 | 0 | 20
38925.5631 | 1 | 0 | 20
38925.5638 | 1 | 0 | 20
38925.5645 | 1 | 0 | 20
38925.5652 | 1 | 0 | 20
38925.5659 | 1 | 0 | 20
38925.5665 | 1 | 0 | 20
38925.5672 | 1 | 0 | 20
38925.5679 | 1 | 0 | 20
38925.5686 | 1 | 0 | 20
38925.5693 | 1 | 0 | 20
38925.5699 | 1 | 0 | 20
38925.5706 | 1 | 0 | 20
38925.5713 | 1 | 0 | 20
38925.572 | 2307 | 0 | 20
38925.5727 | 2009 | 0 | 20
38925.5733 | 2258 | 0 | 20
38925.574 | 1943 | 0 | 20
38925.5747 | 2077 | 0 | 20
38925.5754 | 2150 | 0 | 20
38925.5761 | 2054 | 0 | 20
20
38925.5523 | 1 | 0 | 21
38925.5529 | 1 | 0 | 21
38925.5536 | 1 | 0 | 21
38925.5543 | 1 | 0 | 21
38925.555 | 1 | 0 | 21
38925.5557 | 1 | 0 | 21
38925.5563 | 1 | 0 | 21
38925.557 | 1 | 0 | 21
38925.5577 | 1 | 0 | 21
38925.5584 | 1 | 0 | 21
38925.5591 | 1 | 0 | 21
38925.5597 | 1 | 1 | 21
38925.5604 | 1 | 0 | 21
38925.5611 | 1 | 0 | 21
38925.5618 | 1 | 0 | 21
38925.5625 | 1 | 0 | 21
38925.5631 | 1 | 0 | 21
38925.5638 | 1 | 0 | 21
38925.5645 | 1 | 0 | 21
38925.5652 | 1 | 0 | 21
38925.5659 | 1 | 0 | 21
38925.5666 | 1 | 0 | 21
38925.5672 | 1 | 0 | 21
38925.5679 | 1 | 0 | 21
38925.5686 | 1 | 0 | 21
38925.5693 | 1 | 0 | 21
38925.57 | 1 | 0 | 21
38925.5706 | 1 | 0 | 21
38925.5713 | 1 | 0 | 21
38925.572 | 7 | 0 | 21
38925.5727 | 7 | 0 | 21
38925.5734 | 7 | 0 | 21
38925.574 | 8 | 0 | 21
38925.5747 | 7 | 0 | 21
38925.5754 | 7 | 0 | 21
38925.5761 | 7 | 0 | 21
21
38925.5523 | 1 | 0 | 22
38925.553 | 1 | 0 | 22
38925.5536 | 1 | 0 | 22
38925.5543 | 1 | 0 | 22
38925.555 | 1 | 0 | 22
38925.5557 | 1 | 0 | 22
38925.5564 | 1 | 0 | 22
38925.557 | 1 | 1 | 22
38925.5577 | 2 | 0 | 22
38925.5584 | 1 | 0 | 22
38925.5591 | 1 | 0 | 22
38925.5598 | 1 | 0 | 22
38925.5604 | 1 | 0 | 22
38925.5611 | 1 | 0 | 22
38925.5618 | 1 | 0 | 22
38925.5625 | 2 | 0 | 22
38925.5632 | 1 | 0 | 22
38925.5638 | 1 | 0 | 22
38925.5645 | 1 | 0 | 22
38925.5652 | 1 | 0 | 22
38925.5659 | 1 | 0 | 22
38925.5666 | 1 | 0 | 22
38925.5672 | 1 | 0 | 22
38925.5679 | 2 | 0 | 22
38925.5686 | 1 | 0 | 22
38925.5693 | 1 | 0 | 22
38925.57 | 1 | 0 | 22
38925.5706 | 1 | 0 | 22
38925.5713 | 1 | 0 | 22
38925.572 | 6 | 0 | 22
38925.5727 | 5 | 0 | 22
38925.5734 | 5 | 0 | 22
38925.5741 | 6 | 0 | 22
38925.5747 | 5 | 0 | 22
38925.5754 | 5 | 0 | 22
38925.5761 | 5 | 0 | 22
22
38925.5523 | 1 | 0 | 23
38925.553 | 1 | 0 | 23
38925.5537 | 1 | 0 | 23
38925.5543 | 1 | 0 | 23
38925.555 | 1 | 0 | 23
38925.5557 | 1 | 0 | 23
38925.5564 | 1 | 0 | 23
38925.5571 | 1 | 0 | 23
38925.5577 | 1 | 0 | 23
38925.5584 | 1 | 0 | 23
38925.5591 | 1 | 0 | 23
38925.5598 | 1 | 0 | 23
38925.5605 | 1 | 0 | 23
38925.5611 | 1 | 0 | 23
38925.5618 | 1 | 0 | 23
38925.5625 | 1 | 0 | 23
38925.5632 | 1 | 0 | 23
38925.5639 | 1 | 0 | 23
38925.5645 | 1 | 0 | 23
38925.5652 | 1 | 0 | 23
38925.5659 | 1 | 0 | 23
38925.5666 | 1 | 0 | 23
38925.5673 | 1 | 0 | 23
38925.5679 | 1 | 0 | 23
38925.5686 | 1 | 0 | 23
38925.5693 | 1 | 0 | 23
38925.57 | 1 | 0 | 23
38925.5707 | 1 | 0 | 23
38925.5713 | 1 | 0 | 23
38925.572 | 4 | 0 | 23
38925.5727 | 3 | 0 | 23
38925.5734 | 4 | 0 | 23
38925.5741 | 4 | 0 | 23
38925.5754 | 3 | 0 | 23
38925.5761 | 4 | 0 | 23
23
38925.5523 | 1 | 0 | 24
38925.553 | 1 | 0 | 24
38925.5537 | 1 | 0 | 24
38925.5544 | 1 | 0 | 24
38925.555 | 1 | 0 | 24
38925.5557 | 1 | 0 | 24
38925.5564 | 1 | 0 | 24
38925.5571 | 1 | 0 | 24
38925.5578 | 1 | 0 | 24
38925.5584 | 1 | 0 | 24
38925.5591 | 1 | 0 | 24
38925.5598 | 1 | 0 | 24
38925.5605 | 1 | 0 | 24
38925.5612 | 1 | 0 | 24
38925.5618 | 1 | 0 | 24
38925.5625 | 1 | 0 | 24
38925.5632 | 1 | 0 | 24
38925.5639 | 1 | 0 | 24
38925.5646 | 1 | 0 | 24
38925.5652 | 1 | 0 | 24
38925.5659 | 1 | 0 | 24
38925.5666 | 1 | 0 | 24
38925.5673 | 1 | 0 | 24
38925.568 | 1 | 0 | 24
38925.5686 | 1 | 0 | 24
38925.5693 | 1 | 0 | 24
38925.57 | 1 | 0 | 24
38925.5707 | 1 | 0 | 24
38925.5714 | 1 | 0 | 24
38925.572 | 2 | 0 | 24
38925.5727 | 3 | 0 | 24
38925.5734 | 3 | 0 | 24
38925.5741 | 3 | 0 | 24
38925.5748 | 3 | 0 | 24
38925.5754 | 4 | 0 | 24
38925.5761 | 3 | 0 | 24
24
38925.5523 | 1 | 0 | 25
38925.553 | 1 | 0 | 25
38925.5537 | 1 | 0 | 25
38925.5544 | 1 | 0 | 25
38925.555 | 1 | 0 | 25
38925.5557 | 1 | 0 | 25
38925.5564 | 1 | 0 | 25
38925.5571 | 1 | 0 | 25
38925.5578 | 1 | 0 | 25
38925.5584 | 1 | 0 | 25
38925.5591 | 1 | 0 | 25
38925.5598 | 1 | 0 | 25
38925.5605 | 1 | 0 | 25
38925.5612 | 1 | 0 | 25
38925.5619 | 1 | 0 | 25
38925.5625 | 1 | 0 | 25
38925.5632 | 1 | 1 | 25
38925.5639 | 1 | 0 | 25
38925.5646 | 1 | 0 | 25
38925.5653 | 1 | 0 | 25
38925.5659 | 1 | 0 | 25
38925.5666 | 1 | 0 | 25
38925.5673 | 1 | 0 | 25
38925.568 | 1 | 0 | 25
38925.5687 | 1 | 0 | 25
38925.5693 | 1 | 0 | 25
38925.57 | 1 | 0 | 25
38925.5707 | 1 | 0 | 25
38925.5714 | 1 | 0 | 25
38925.5721 | 2 | 0 | 25
38925.5727 | 2 | 0 | 25
38925.5734 | 3 | 0 | 25
38925.5741 | 3 | 0 | 25
38925.5748 | 3 | 0 | 25
38925.5755 | 3 | 0 | 25
38925.5761 | 3 | 0 | 25
25
38925.5523 | 1 | 0 | 26
38925.553 | 1 | 0 | 26
38925.5537 | 1 | 0 | 26
38925.5544 | 1 | 0 | 26
38925.5551 | 1 | 0 | 26
38925.5557 | 1 | 0 | 26
38925.5564 | 1 | 0 | 26
38925.5571 | 1 | 0 | 26
38925.5578 | 1 | 0 | 26
38925.5585 | 2 | 0 | 26
38925.5591 | 1 | 0 | 26
38925.5598 | 1 | 0 | 26
38925.5605 | 1 | 0 | 26
38925.5612 | 2 | 0 | 26
38925.5619 | 1 | 0 | 26
38925.5625 | 1 | 0 | 26
38925.5632 | 1 | 0 | 26
38925.5639 | 1 | 0 | 26
38925.5646 | 1 | 0 | 26
38925.5653 | 1 | 0 | 26
38925.5659 | 1 | 0 | 26
38925.5666 | 1 | 0 | 26
38925.5673 | 1 | 0 | 26
38925.568 | 1 | 0 | 26
38925.5687 | 1 | 0 | 26
38925.5694 | 1 | 0 | 26
38925.57 | 1 | 0 | 26
38925.5707 | 1 | 0 | 26
38925.5714 | 1 | 0 | 26
38925.5721 | 2 | 0 | 26
38925.5728 | 2 | 0 | 26
38925.5734 | 2 | 0 | 26
38925.5741 | 3 | 0 | 26
38925.5748 | 3 | 0 | 26
38925.5755 | 3 | 0 | 26
38925.5762 | 3 | 0 | 26
26
38925.5524 | 1 | 1 | 27
38925.553 | 1 | 0 | 27
38925.5537 | 1 | 1 | 27
38925.5544 | 1 | 0 | 27
38925.5551 | 1 | 0 | 27
38925.5558 | 1 | 0 | 27
38925.5564 | 1 | 0 | 27
38925.5571 | 1 | 0 | 27
38925.5578 | 1 | 0 | 27
38925.5585 | 1 | 0 | 27
38925.5592 | 1 | 0 | 27
38925.5598 | 1 | 0 | 27
38925.5605 | 1 | 0 | 27
38925.5612 | 1 | 0 | 27
38925.5619 | 1 | 0 | 27
38925.5626 | 1 | 0 | 27
38925.5632 | 1 | 0 | 27
38925.5639 | 1 | 0 | 27
38925.5646 | 1 | 0 | 27
38925.5653 | 1 | 0 | 27
38925.566 | 1 | 0 | 27
38925.5666 | 1 | 0 | 27
38925.5673 | 1 | 0 | 27
38925.568 | 1 | 0 | 27
38925.5687 | 1 | 0 | 27
38925.5694 | 1 | 0 | 27
38925.57 | 1 | 0 | 27
38925.5707 | 1 | 0 | 27
38925.5714 | 1 | 0 | 27
38925.5721 | 2 | 0 | 27
38925.5728 | 2 | 0 | 27
38925.5734 | 3 | 0 | 27
38925.5741 | 3 | 0 | 27
38925.5748 | 2 | 0 | 27
38925.5755 | 3 | 0 | 27
38925.5762 | 2 | 0 | 27
27
38925.5524 | 1 | 0 | 28
38925.5531 | 1 | 0 | 28
38925.5537 | 1 | 0 | 28
38925.5544 | 1 | 0 | 28
38925.5551 | 1 | 0 | 28
38925.5558 | 1 | 0 | 28
38925.5565 | 1 | 0 | 28
38925.5571 | 1 | 1 | 28
38925.5578 | 1 | 1 | 28
38925.5585 | 1 | 0 | 28
38925.5592 | 1 | 0 | 28
38925.5599 | 1 | 0 | 28
38925.5605 | 1 | 0 | 28
38925.5612 | 1 | 0 | 28
38925.5619 | 1 | 0 | 28
38925.5626 | 1 | 0 | 28
38925.5633 | 1 | 0 | 28
38925.5639 | 1 | 0 | 28
38925.5646 | 1 | 0 | 28
38925.5653 | 1 | 0 | 28
38925.566 | 1 | 0 | 28
38925.5667 | 1 | 0 | 28
38925.5673 | 1 | 0 | 28
38925.568 | 1 | 0 | 28
38925.5687 | 1 | 0 | 28
38925.5694 | 1 | 0 | 28
38925.5701 | 1 | 0 | 28
38925.5708 | 1 | 0 | 28
38925.5714 | 1 | 0 | 28
38925.5721 | 2291 | 0 | 28
38925.5728 | 2262 | 0 | 28
38925.5735 | 2231 | 0 | 28
38925.5741 | 2353 | 0 | 28
38925.5748 | 2511 | 1 | 28
38925.5755 | 2318 | 0 | 28
38925.5762 | 1947 | 0 | 28
28
38925.5524 | 1 | 0 | 29
38925.5531 | 1 | 0 | 29
38925.5537 | 1 | 0 | 29
38925.5544 | 1 | 1 | 29
38925.5551 | 1 | 0 | 29
38925.5558 | 2 | 0 | 29
38925.5565 | 1 | 0 | 29
38925.5572 | 1 | 0 | 29
38925.5578 | 1 | 0 | 29
38925.5585 | 1 | 0 | 29
38925.5592 | 1 | 0 | 29
38925.5599 | 1 | 0 | 29
38925.5606 | 1 | 0 | 29
38925.5612 | 1 | 0 | 29
38925.5619 | 1 | 0 | 29
38925.5626 | 1 | 0 | 29
38925.5633 | 1 | 0 | 29
38925.564 | 1 | 0 | 29
38925.5646 | 1 | 0 | 29
38925.5653 | 1 | 0 | 29
38925.566 | 1 | 0 | 29
38925.5667 | 1 | 0 | 29
38925.5674 | 1 | 0 | 29
38925.568 | 1 | 0 | 29
38925.5687 | 1 | 0 | 29
38925.5694 | 1 | 0 | 29
38925.5701 | 1 | 0 | 29
38925.5708 | 1 | 0 | 29
38925.5714 | 1 | 0 | 29
38925.5721 | 7 | 0 | 29
38925.5728 | 8 | 0 | 29
38925.5735 | 7 | 0 | 29
38925.5742 | 7 | 0 | 29
38925.5748 | 7 | 0 | 29
38925.5755 | 7 | 0 | 29
38925.5762 | 7 | 0 | 29
29
38925.5524 | 1 | 0 | 30
38925.5531 | 2 | 0 | 30
38925.5538 | 2 | 0 | 30
38925.5544 | 1 | 0 | 30
38925.5551 | 1 | 0 | 30
38925.5558 | 1 | 0 | 30
38925.5565 | 1 | 0 | 30
38925.5572 | 1 | 0 | 30
38925.5578 | 1 | 0 | 30
38925.5585 | 1 | 0 | 30
38925.5592 | 1 | 0 | 30
38925.5599 | 1 | 0 | 30
38925.5606 | 1 | 0 | 30
38925.5612 | 1 | 0 | 30
38925.5619 | 1 | 0 | 30
38925.5626 | 1 | 0 | 30
38925.5633 | 1 | 0 | 30
38925.564 | 1 | 0 | 30
38925.5647 | 1 | 0 | 30
38925.5653 | 1 | 0 | 30
38925.566 | 1 | 0 | 30
38925.5667 | 1 | 0 | 30
38925.5674 | 1 | 0 | 30
38925.5681 | 1 | 0 | 30
38925.5687 | 1 | 0 | 30
38925.5694 | 1 | 0 | 30
38925.5701 | 1 | 0 | 30
38925.5708 | 1 | 0 | 30
38925.5715 | 1 | 0 | 30
38925.5721 | 5 | 0 | 30
38925.5728 | 5 | 0 | 30
38925.5735 | 5 | 0 | 30
38925.5742 | 5 | 0 | 30
38925.5749 | 5 | 0 | 30
38925.5755 | 5 | 0 | 30
38925.5762 | 5 | 0 | 30
30
38925.5524 | 1 | 0 | 31
38925.5531 | 1 | 0 | 31
38925.5538 | 1 | 0 | 31
38925.5545 | 1 | 1 | 31
38925.5551 | 1 | 0 | 31
38925.5558 | 1 | 0 | 31
38925.5565 | 1 | 0 | 31
38925.5572 | 1 | 0 | 31
38925.5579 | 1 | 0 | 31
38925.5585 | 1 | 0 | 31
38925.5592 | 1 | 0 | 31
38925.5599 | 1 | 0 | 31
38925.5606 | 1 | 0 | 31
38925.5613 | 1 | 0 | 31
38925.5619 | 1 | 0 | 31
38925.5626 | 1 | 0 | 31
38925.5633 | 1 | 0 | 31
38925.564 | 1 | 0 | 31
38925.5647 | 1 | 0 | 31
38925.5653 | 1 | 0 | 31
38925.566 | 1 | 0 | 31
38925.5667 | 1 | 0 | 31
38925.5674 | 1 | 0 | 31
38925.5681 | 1 | 0 | 31
38925.5687 | 1 | 0 | 31
38925.5694 | 1 | 0 | 31
38925.5701 | 1 | 0 | 31
38925.5708 | 1 | 0 | 31
38925.5715 | 1 | 0 | 31
38925.5722 | 4 | 0 | 31
38925.5728 | 4 | 0 | 31
38925.5735 | 4 | 0 | 31
38925.5742 | 4 | 0 | 31
38925.5749 | 4 | 0 | 31
38925.5756 | 4 | 0 | 31
38925.5762 | 4 | 0 | 31
31
38925.5524 | 1 | 0 | 32
38925.5531 | 1 | 0 | 32
38925.5538 | 1 | 0 | 32
38925.5545 | 1 | 0 | 32
38925.5552 | 1 | 0 | 32
38925.5558 | 1 | 0 | 32
38925.5565 | 1 | 0 | 32
38925.5572 | 1 | 0 | 32
38925.5579 | 1 | 0 | 32
38925.5586 | 1 | 0 | 32
38925.5592 | 1 | 0 | 32
38925.5599 | 1 | 0 | 32
38925.5606 | 1 | 0 | 32
38925.5613 | 1 | 0 | 32
38925.562 | 1 | 0 | 32
38925.5627 | 1 | 0 | 32
38925.5633 | 1 | 0 | 32
38925.564 | 1 | 0 | 32
38925.5647 | 1 | 0 | 32
38925.5654 | 1 | 0 | 32
38925.5661 | 1 | 0 | 32
38925.5667 | 1 | 0 | 32
38925.5674 | 1 | 0 | 32
38925.5681 | 1 | 0 | 32
38925.5688 | 1 | 0 | 32
38925.5695 | 1 | 0 | 32
38925.5701 | 1 | 0 | 32
38925.5708 | 1 | 0 | 32
38925.5715 | 1 | 0 | 32
38925.5722 | 3 | 0 | 32
38925.5728 | 3 | 0 | 32
38925.5735 | 3 | 0 | 32
38925.5742 | 4 | 0 | 32
38925.5749 | 3 | 0 | 32
38925.5756 | 3 | 0 | 32
38925.5762 | 4 | 0 | 32
32
38925.5525 | 1 | 0 | 33
38925.5531 | 1 | 0 | 33
38925.5538 | 1 | 0 | 33
38925.5545 | 1 | 0 | 33
38925.5552 | 1 | 0 | 33
38925.5559 | 1 | 0 | 33
38925.5565 | 1 | 1 | 33
38925.5572 | 1 | 0 | 33
38925.5579 | 1 | 0 | 33
38925.5586 | 1 | 0 | 33
38925.5593 | 1 | 0 | 33
38925.5599 | 1 | 0 | 33
38925.5606 | 1 | 0 | 33
38925.5613 | 1 | 0 | 33
38925.562 | 1 | 0 | 33
38925.5627 | 1 | 0 | 33
38925.5633 | 1 | 0 | 33
38925.564 | 1 | 0 | 33
38925.5647 | 1 | 0 | 33
38925.5654 | 1 | 0 | 33
38925.5661 | 1 | 0 | 33
38925.5667 | 1 | 0 | 33
38925.5674 | 1 | 0 | 33
38925.5681 | 1 | 0 | 33
38925.5688 | 1 | 0 | 33
38925.5695 | 1 | 0 | 33
38925.5702 | 1 | 0 | 33
38925.5708 | 1 | 0 | 33
38925.5715 | 1 | 0 | 33
38925.5722 | 3 | 0 | 33
38925.5729 | 2 | 0 | 33
38925.5736 | 3 | 0 | 33
38925.5742 | 3 | 0 | 33
38925.5749 | 2 | 0 | 33
38925.5756 | 3 | 0 | 33
38925.5763 | 3 | 0 | 33
33
38925.5525 | 1 | 0 | 34
38925.5531 | 1 | 0 | 34
38925.5538 | 1 | 0 | 34
38925.5545 | 1 | 0 | 34
38925.5552 | 1 | 0 | 34
38925.5559 | 1 | 0 | 34
38925.5566 | 1 | 0 | 34
38925.5572 | 1 | 0 | 34
38925.5579 | 1 | 0 | 34
38925.5586 | 1 | 1 | 34
38925.5593 | 1 | 0 | 34
38925.56 | 1 | 0 | 34
38925.5606 | 1 | 0 | 34
38925.5613 | 1 | 0 | 34
38925.562 | 2 | 0 | 34
38925.5627 | 1 | 0 | 34
38925.5634 | 1 | 0 | 34
38925.564 | 1 | 0 | 34
38925.5647 | 1 | 0 | 34
38925.5654 | 1 | 0 | 34
38925.5661 | 1 | 0 | 34
38925.5668 | 1 | 0 | 34
38925.5674 | 1 | 0 | 34
38925.5681 | 2 | 0 | 34
38925.5688 | 1 | 0 | 34
38925.5695 | 1 | 0 | 34
38925.5702 | 1 | 0 | 34
38925.5708 | 1 | 0 | 34
38925.5715 | 1 | 0 | 34
38925.5722 | 1983 | 0 | 34
38925.5729 | 2377 | 0 | 34
38925.5736 | 2081 | 0 | 34
38925.5742 | 2353 | 0 | 34
38925.5749 | 1961 | 0 | 34
38925.5756 | 2512 | 0 | 34
38925.5763 | 2228 | 0 | 34
34
38925.5525 | 1 | 0 | 35
38925.5532 | 1 | 0 | 35
38925.5538 | 1 | 0 | 35
38925.5545 | 1 | 0 | 35
38925.5552 | 1 | 0 | 35
38925.5559 | 1 | 0 | 35
38925.5566 | 1 | 0 | 35
38925.5572 | 1 | 0 | 35
38925.5579 | 1 | 0 | 35
38925.5586 | 1 | 0 | 35
38925.5593 | 1 | 0 | 35
38925.56 | 1 | 0 | 35
38925.5606 | 1 | 0 | 35
38925.5613 | 1 | 0 | 35
38925.562 | 1 | 0 | 35
38925.5627 | 1 | 0 | 35
38925.5634 | 1 | 0 | 35
38925.5641 | 1 | 0 | 35
38925.5647 | 1 | 0 | 35
38925.5654 | 1 | 0 | 35
38925.5661 | 1 | 0 | 35
38925.5668 | 1 | 0 | 35
38925.5675 | 1 | 0 | 35
38925.5681 | 1 | 0 | 35
38925.5688 | 1 | 0 | 35
38925.5695 | 1 | 0 | 35
38925.5702 | 1 | 0 | 35
38925.5709 | 2 | 0 | 35
38925.5715 | 1 | 0 | 35
38925.5722 | 7 | 0 | 35
38925.5729 | 7 | 0 | 35
38925.5736 | 7 | 0 | 35
38925.5743 | 7 | 0 | 35
38925.5749 | 8 | 0 | 35
38925.5756 | 8 | 0 | 35
38925.5763 | 8 | 1 | 35
35
38925.5525 | 1 | 0 | 36
38925.5532 | 1 | 0 | 36
38925.5539 | 1 | 0 | 36
38925.5545 | 1 | 0 | 36
38925.5552 | 1 | 0 | 36
38925.5559 | 1 | 0 | 36
38925.5566 | 1 | 0 | 36
38925.5573 | 2 | 0 | 36
38925.558 | 1 | 0 | 36
38925.5586 | 1 | 0 | 36
38925.5593 | 1 | 0 | 36
38925.56 | 1 | 0 | 36
38925.5607 | 1 | 0 | 36
38925.5614 | 1 | 0 | 36
38925.562 | 1 | 0 | 36
38925.5627 | 1 | 0 | 36
38925.5634 | 1 | 0 | 36
38925.5641 | 1 | 0 | 36
38925.5648 | 1 | 0 | 36
38925.5654 | 1 | 0 | 36
38925.5661 | 1 | 0 | 36
38925.5668 | 1 | 0 | 36
38925.5675 | 1 | 0 | 36
38925.5681 | 1 | 0 | 36
38925.5688 | 1 | 0 | 36
38925.5695 | 1 | 0 | 36
38925.5702 | 1 | 0 | 36
38925.5709 | 1 | 0 | 36
38925.5716 | 1 | 0 | 36
38925.5722 | 5 | 0 | 36
38925.5729 | 6 | 0 | 36
38925.5736 | 6 | 0 | 36
38925.5743 | 6 | 0 | 36
38925.575 | 6 | 0 | 36
38925.5756 | 6 | 1 | 36
38925.5763 | 6 | 0 | 36
36
38925.5525 | 1 | 0 | 37
38925.5532 | 1 | 0 | 37
38925.5539 | 1 | 0 | 37
38925.5546 | 1 | 0 | 37
38925.5552 | 1 | 0 | 37
38925.5559 | 2 | 0 | 37
38925.5566 | 1 | 0 | 37
38925.5573 | 1 | 0 | 37
38925.558 | 1 | 0 | 37
38925.5586 | 1 | 0 | 37
38925.5593 | 1 | 1 | 37
38925.56 | 1 | 0 | 37
38925.5607 | 1 | 0 | 37
38925.5614 | 1 | 0 | 37
38925.562 | 1 | 0 | 37
38925.5627 | 1 | 0 | 37
38925.5634 | 1 | 0 | 37
38925.5641 | 1 | 0 | 37
38925.5648 | 1 | 0 | 37
38925.5655 | 1 | 0 | 37
38925.5661 | 1 | 0 | 37
38925.5668 | 1 | 0 | 37
38925.5675 | 1 | 0 | 37
38925.5682 | 1 | 0 | 37
38925.5689 | 1 | 0 | 37
38925.5695 | 1 | 0 | 37
38925.5702 | 1 | 0 | 37
38925.5709 | 1 | 0 | 37
38925.5716 | 1 | 0 | 37
38925.5723 | 4 | 0 | 37
38925.5729 | 4 | 0 | 37
38925.5736 | 3 | 0 | 37
38925.5743 | 4 | 0 | 37
38925.575 | 4 | 0 | 37
38925.5757 | 4 | 0 | 37
38925.5763 | 4 | 0 | 37
37
38925.5525 | 1 | 0 | 38
38925.5532 | 1 | 0 | 38
38925.5539 | 1 | 0 | 38
38925.5546 | 1 | 0 | 38
38925.5553 | 2 | 0 | 38
38925.5559 | 1 | 0 | 38
38925.5566 | 1 | 0 | 38
38925.5573 | 1 | 0 | 38
38925.558 | 2 | 0 | 38
38925.5587 | 1 | 0 | 38
38925.5593 | 1 | 0 | 38
38925.56 | 1 | 0 | 38
38925.5607 | 1 | 0 | 38
38925.5614 | 1 | 0 | 38
38925.5621 | 1 | 0 | 38
38925.5627 | 1 | 0 | 38
38925.5634 | 1 | 0 | 38
38925.5641 | 1 | 0 | 38
38925.5648 | 1 | 0 | 38
38925.5655 | 1 | 0 | 38
38925.5661 | 1 | 0 | 38
38925.5668 | 1 | 0 | 38
38925.5675 | 1 | 0 | 38
38925.5682 | 1 | 0 | 38
38925.5689 | 1 | 0 | 38
38925.5695 | 1 | 0 | 38
38925.5702 | 1 | 0 | 38
38925.5709 | 1 | 0 | 38
38925.5716 | 1 | 0 | 38
38925.5723 | 2477 | 0 | 38
38925.573 | 2475 | 0 | 38
38925.5736 | 2173 | 0 | 38
38925.5743 | 2160 | 0 | 38
38925.575 | 2452 | 0 | 38
38925.5757 | 2511 | 0 | 38
38925.5764 | 2118 | 0 | 38
38
38925.5525 | 1 | 0 | 39
38925.5532 | 1 | 0 | 39
38925.5546 | 1 | 0 | 39
38925.5553 | 1 | 0 | 39
38925.5559 | 1 | 0 | 39
38925.5566 | 1 | 0 | 39
38925.5573 | 1 | 0 | 39
38925.558 | 1 | 0 | 39
38925.5587 | 1 | 0 | 39
38925.5594 | 1 | 0 | 39
38925.56 | 1 | 0 | 39
38925.5607 | 1 | 0 | 39
38925.5614 | 1 | 0 | 39
38925.5621 | 1 | 0 | 39
38925.5628 | 1 | 0 | 39
38925.5634 | 1 | 0 | 39
38925.5641 | 1 | 0 | 39
38925.5648 | 1 | 0 | 39
38925.5655 | 1 | 0 | 39
38925.5662 | 1 | 0 | 39
38925.5668 | 1 | 0 | 39
38925.5675 | 1 | 0 | 39
38925.5682 | 1 | 0 | 39
38925.5689 | 1 | 0 | 39
38925.5696 | 2 | 0 | 39
38925.5702 | 1 | 0 | 39
38925.5709 | 1 | 0 | 39
38925.5716 | 1 | 0 | 39
38925.5723 | 8 | 0 | 39
38925.573 | 8 | 0 | 39
38925.5736 | 7 | 0 | 39
38925.5743 | 8 | 0 | 39
38925.575 | 8 | 0 | 39
38925.5757 | 8 | 0 | 39
38925.5764 | 8 | 0 | 39
39
38925.5526 | 1 | 0 | 40
38925.5533 | 1 | 0 | 40
38925.5539 | 1 | 0 | 40
38925.5546 | 1 | 0 | 40
38925.5553 | 1 | 0 | 40
38925.556 | 1 | 0 | 40
38925.5567 | 1 | 0 | 40
38925.5573 | 1 | 0 | 40
38925.558 | 1 | 0 | 40
38925.5587 | 1 | 0 | 40
38925.5594 | 1 | 0 | 40
38925.5601 | 1 | 0 | 40
38925.5607 | 1 | 0 | 40
38925.5614 | 2 | 0 | 40
38925.5621 | 1 | 0 | 40
38925.5628 | 1 | 0 | 40
38925.5635 | 1 | 0 | 40
38925.5641 | 1 | 0 | 40
38925.5648 | 1 | 0 | 40
38925.5655 | 1 | 0 | 40
38925.5662 | 1 | 0 | 40
38925.5669 | 1 | 0 | 40
38925.5675 | 1 | 0 | 40
38925.5682 | 1 | 0 | 40
38925.5689 | 1 | 0 | 40
38925.5696 | 1 | 0 | 40
38925.5703 | 1 | 0 | 40
38925.5709 | 1 | 0 | 40
38925.5716 | 1 | 0 | 40
38925.5723 | 6 | 0 | 40
38925.573 | 5 | 0 | 40
38925.5737 | 6 | 0 | 40
38925.5743 | 6 | 0 | 40
38925.575 | 6 | 0 | 40
38925.5757 | 7 | 0 | 40
38925.5764 | 6 | 0 | 40
40
38925.5526 | 1 | 0 | 41
38925.5533 | 1 | 0 | 41
38925.5539 | 1 | 0 | 41
38925.5546 | 1 | 0 | 41
38925.5553 | 1 | 0 | 41
38925.556 | 1 | 0 | 41
38925.5567 | 1 | 0 | 41
38925.5573 | 1 | 0 | 41
38925.558 | 1 | 0 | 41
38925.5587 | 1 | 0 | 41
38925.5594 | 1 | 0 | 41
38925.5601 | 1 | 0 | 41
38925.5608 | 1 | 0 | 41
38925.5614 | 1 | 0 | 41
38925.5621 | 1 | 0 | 41
38925.5628 | 1 | 0 | 41
38925.5635 | 1 | 0 | 41
38925.5642 | 1 | 0 | 41
38925.5648 | 1 | 0 | 41
38925.5655 | 1 | 0 | 41
38925.5662 | 1 | 0 | 41
38925.5669 | 1 | 0 | 41
38925.5676 | 1 | 0 | 41
38925.5682 | 1 | 0 | 41
38925.5689 | 1 | 0 | 41
38925.5696 | 1 | 0 | 41
38925.5703 | 1 | 0 | 41
38925.571 | 1 | 0 | 41
38925.5716 | 1 | 0 | 41
38925.5723 | 2224 | 0 | 41
38925.573 | 2334 | 0 | 41
38925.5737 | 2389 | 0 | 41
38925.5744 | 2400 | 0 | 41
38925.575 | 1964 | 0 | 41
38925.5757 | 1971 | 0 | 41
38925.5764 | 2173 | 0 | 41
41
38925.5526 | 1 | 0 | 42
38925.5533 | 1 | 0 | 42
38925.554 | 1 | 0 | 42
38925.5546 | 1 | 0 | 42
38925.5553 | 1 | 1 | 42
38925.556 | 1 | 0 | 42
38925.5567 | 1 | 0 | 42
38925.5574 | 1 | 0 | 42
38925.558 | 1 | 0 | 42
38925.5587 | 1 | 0 | 42
38925.5594 | 1 | 0 | 42
38925.5601 | 1 | 0 | 42
38925.5608 | 1 | 0 | 42
38925.5614 | 1 | 0 | 42
38925.5621 | 1 | 0 | 42
38925.5628 | 1 | 0 | 42
38925.5635 | 1 | 0 | 42
38925.5642 | 1 | 0 | 42
38925.5648 | 1 | 0 | 42
38925.5655 | 1 | 0 | 42
38925.5662 | 1 | 0 | 42
38925.5669 | 1 | 0 | 42
38925.5676 | 1 | 0 | 42
38925.5683 | 1 | 0 | 42
38925.5689 | 1 | 0 | 42
38925.5696 | 1 | 0 | 42
38925.5703 | 1 | 0 | 42
38925.571 | 1 | 0 | 42
38925.5717 | 1 | 0 | 42
38925.5723 | 8 | 0 | 42
38925.573 | 8 | 0 | 42
38925.5737 | 8 | 0 | 42
38925.5744 | 8 | 0 | 42
38925.5751 | 7 | 0 | 42
38925.5757 | 7 | 0 | 42
38925.5764 | 8 | 0 | 42
42

## Test Facts
Last row in IRMS data sheets: | 41
Time when Penlight power was initiated: | 75