## Test Facts
Last row in IRMS data sheets: | 47
Time when Penlight power was initiated: | 133

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 28
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, CSPE ("Hypalon") jacketed, Rockbestos Firewall III, control cable (Cable Item #10). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: None. Cables were run horizontally through the Penlight chamber ("air drop" configuration) and secured to the raceway support brackets outside of the chamber; chamber end walls were closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 133 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
133 | 0 | Initated Penlight Heating
1447-1452 | 1314-1319 | Conductors 5 & 7 both short to ground (916 & 900) | Uncertain of the paths to ground; unstable ground fault conditions
1454 | 1321 | Conductor 4 shorts to conductor 5 briefly | Unsustained conductor-to-conductor short
1463-1465 | 1330-1332 | Conductor 5 shorts to conductors 6 & 7 at less than 100 ohms (13 & 35)
1468 | 1335 | Conductor 6 shorts to conductor 7 at less than 100 ohms (37)
1471-1482 | 1338-1349 | Conductor 1 shorts to conductors 2, 3, 5 & 6 (199, <1, 3 & 27)
1478 | 1345 | Conductor 1 shorts to ground (76) | Uncertain of the path to ground; unstable ground fault condition
1488 | 1355 | Conductor 2 shorts to conductor 3 at less than 100 ohms (9)
1489 | 1356 | Conductor 2 shorts to ground at less than 1000 ohms (314) | Uncertain of the path to ground; unstable ground fault condition
1490 | 1357 | Conductor 4 shorts to conductor 2 briefly | Unsustained conductor-to-conductor short
1493-1496 | 1360-1629 | Conductor 2 shorts to conductors 5 & 6 at less than 100 ohms (29 & 10)
1497 | 1364 | Conductor 3 shorts to ground (97) | Uncertain of the path to ground; unstable ground fault condition
1502 | 1369 | Conductor 4 shorts to conductor 3 briefly | Unsustained conductor-to-conductor short
1502 | 1369 | Conductor 4 shorts to ground briefly | Uncertain of the path to ground; unstable ground fault condition. Unsustained conductor-to-ground fault condition
1504-1507 | 1371-1374 | Conductor 3 shorts to conductors 5 & 6 at less than 100 ohms (14 & 18)
1516-1519 | 1383-1386 | Conductor 4 shorts to conductors 6 & 7 briefly | Unsustained conductor-to-conductor shorts
1530 | 1397 | The existing short between conductors 1 & 2 decreases to less than 100 ohms (15)
1558 | 1425 | Conductor 2 shorts to conductor 7 at much less than 100 ohms (<1)
1567 | 1434 | Conductor 6 shorts to ground (35) | Uncertain of the path to ground; unstable ground fault condition
1569 | 1436 | Conductor 3 shorts to conductor 7 at less than 100 ohms (17)
1796 | 1663 | Conductor 4 shorts to ground (somewhat sustained) | Uncertain of the path to ground; unstable ground fault condition
1810-1812 | 1677-1945 | Conductor 4 again shorts to conductors 6 & 7 at less than 1000 ohms (172 & 132) | Sustained conductor-to-conductor shorts
1829-1866 | 1696-1733 | Conductor 4 again shorts to conductors 1, 2, 3 & 5 (142, 6, 42 & 4) | Sustained conductor-to-conductor shorts
1869-1871 | 1736-1738 | The existing shorts between conductor 4 and conductors 1, 6 & 7 decrease to less than 100 ohms (25, 5 & 7)
1966 | 1833 | Power to Penlight is shutoff
Additional Observations
Observation 1 | It took 1330 seconds (22.2 min.) from the start of Penlight heating for the first sustained shorting failure to occur.
Observation 2 | Although short to ground failures are indicated, it is uncertain what the paths to ground could have been.
Observation 3 | Conductor 4 shorted to all of the other conductors and to ground briefly in the period of 1454-1519 seconds. Later, in the period of 1796-1866, conductor 4 established sustained shorts to all of the other conductors and somewhat to ground.
Observation 4 | The cables did not ignite or burn during this test run. Nevertheless, damage to the cables was observed.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 28 |  |  | 2006-08-01 | 12:06
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-132 | 211201.9994 | -129.5 | 211201.9994 | -126.5 | 211201.9994 | -123.5 | 211201.9994 | -121 | 211201.9994 | -118 | 211201.9994 | -115.5 | 211201.9994 | -112.5 | 211201.9994 | -110 | 211201.9994 | -107 | 211201.9994 | -104 | 211201.9994 | -101.5 | 211201.9994 | -98.5 | 211201.9994 | -95.5 | 211201.9994 | -93 | 211201.9994 | -90 | 211201.9994 | -87.5 | 211201.9994 | -84.5 | 211201.9994 | -81.5 | 211201.9994 | -79 | 211201.9994 | -76 | 211201.9994 | -132 | 211201.9994
-73.5 | 211201.9994 | -70.5 | 211201.9994 | -67.5 | 211201.9994 | -65 | 211201.9994 | -62 | 211201.9994 | -59.5 | 211201.9994 | -56.5 | 211201.9994 | -53.5 | 211201.9994 | -51 | 211201.9994 | -48 | 211201.9994 | -45.5 | 211201.9994 | -42.5 | 211201.9994 | -40 | 211201.9994 | -37 | 211201.9994 | -34 | 211201.9994 | -31.5 | 211201.9994 | -28.5 | 211201.9994 | -25.5 | 211201.9994 | -23 | 211201.9994 | -20.5 | 211201.9994 | -17.5 | 211201.9994 | -73.5 | 211201.9994
-14.5 | 211201.9994 | -11.5 | 211201.9994 | -9 | 211201.9994 | -6 | 211201.9994 | -3.5 | 211201.9994 | -0.5 | 211201.9994 | 2.5 | 211201.9994 | 5 | 211201.9994 | 8 | 211201.9994 | 10.5 | 211201.9994 | 13.5 | 211201.9994 | 16.5 | 211201.9994 | 19 | 211201.9994 | 22 | 211201.9994 | 24.5 | 211201.9994 | 27.5 | 211201.9994 | 30.5 | 211201.9994 | 33 | 211201.9994 | 36 | 211201.9994 | 38.5 | 211201.9994 | 41.5 | 211201.9994 | -14.5 | 211201.9994
44.5 | 211201.9994 | 47 | 211201.9994 | 49.5 | 211201.9994 | 52.5 | 211201.9994 | 55.5 | 211201.9994 | 58 | 211201.9994 | 61 | 211201.9994 | 64 | 211201.9994 | 66.5 | 211201.9994 | 69.5 | 211201.9994 | 72.5 | 211201.9994 | 75 | 211201.9994 | 77.5 | 211201.9994 | 80.5 | 211201.9994 | 83.5 | 211201.9994 | 86.5 | 211201.9994 | 89 | 211201.9994 | 91.5 | 211201.9994 | 94.5 | 211201.9994 | 97.5 | 211201.9994 | 100.5 | 211002.0947 | 44.5 | 211002.0947
103 | 211201.9994 | 105.5 | 211201.9994 | 108.5 | 211201.9994 | 111.5 | 211201.9994 | 114 | 211201.9994 | 117 | 211201.9994 | 120 | 211201.9994 | 122.5 | 211201.9994 | 125.5 | 211201.9994 | 128.5 | 211201.9994 | 131 | 211201.9994 | 134 | 211201.9994 | 136.5 | 211201.9994 | 139.5 | 211201.9994 | 142.5 | 211201.9994 | 145 | 211201.9994 | 147.5 | 211201.9994 | 150.5 | 211201.9994 | 153.5 | 211201.9994 | 156 | 211201.9994 | 159 | 211201.9994 | 103 | 211201.9994
161.5 | 211201.9994 | 164.5 | 211201.9994 | 167.5 | 211201.9994 | 170 | 211201.9994 | 173 | 211201.9994 | 175.5 | 211201.9994 | 178.5 | 211201.9994 | 181.5 | 211201.9994 | 184 | 211201.9994 | 187 | 211201.9994 | 189.5 | 211201.9994 | 192.5 | 211201.9994 | 195.5 | 211201.9994 | 198.5 | 211201.9994 | 201 | 211201.9994 | 204 | 211201.9994 | 206.5 | 211201.9994 | 209.5 | 211201.9994 | 212.5 | 211201.9994 | 215 | 211201.9994 | 217.5 | 211201.9994 | 161.5 | 211201.9994
220.5 | 211201.9994 | 223.5 | 211201.9994 | 226.5 | 211201.9994 | 229 | 211201.9994 | 232 | 211201.9994 | 234.5 | 211201.9994 | 237.5 | 211201.9994 | 240 | 211201.9994 | 243 | 211201.9994 | 245.5 | 211201.9994 | 248.5 | 211201.9994 | 251.5 | 211201.9994 | 254 | 211201.9994 | 257 | 211201.9994 | 259.5 | 211201.9994 | 262.5 | 211201.9994 | 265.5 | 211201.9994 | 268.5 | 211002.0947 | 271 | 211201.9994 | 274 | 211201.9994 | 276.5 | 211201.9994 | 220.5 | 211002.0947
279.5 | 211201.9994 | 282.5 | 211201.9994 | 285 | 211201.9994 | 288 | 211201.9994 | 290.5 | 211201.9994 | 293.5 | 211201.9994 | 296 | 211201.9994 | 299 | 211201.9994 | 302 | 211201.9994 | 304.5 | 211201.9994 | 307.5 | 211201.9994 | 310.5 | 211201.9994 | 313 | 211201.9994 | 315.5 | 211201.9994 | 318.5 | 211201.9994 | 321.5 | 211201.9994 | 324 | 211201.9994 | 327 | 211201.9994 | 330 | 211201.9994 | 332.5 | 211201.9994 | 335.5 | 211201.9994 | 279.5 | 211201.9994
338 | 211201.9994 | 341 | 211201.9994 | 343.5 | 211201.9994 | 346.5 | 211201.9994 | 349.5 | 211201.9994 | 352 | 211201.9994 | 355 | 211201.9994 | 358 | 211201.9994 | 360.5 | 211201.9994 | 363.5 | 211201.9994 | 366 | 211201.9994 | 369 | 211201.9994 | 371.5 | 211201.9994 | 374.5 | 211201.9994 | 377.5 | 211201.9994 | 380 | 211201.9994 | 383 | 211201.9994 | 385.5 | 211201.9994 | 388.5 | 211201.9994 | 391.5 | 211002.0947 | 394 | 211201.9994 | 338 | 211002.0947
397 | 211201.9994 | 399.5 | 211201.9994 | 402.5 | 211201.9994 | 405.5 | 211201.9994 | 408 | 211201.9994 | 411 | 211201.9994 | 414 | 211201.9994 | 416.5 | 211201.9994 | 419.5 | 211201.9994 | 422 | 211201.9994 | 425 | 211201.9994 | 427.5 | 211201.9994 | 430.5 | 211201.9994 | 433.5 | 211201.9994 | 436 | 211201.9994 | 439 | 211201.9994 | 441.5 | 211201.9994 | 444.5 | 211201.9994 | 447.5 | 211201.9994 | 450 | 211201.9994 | 453 | 211201.9994 | 397 | 211201.9994
455.5 | 211201.9994 | 458.5 | 211201.9994 | 461.5 | 211201.9994 | 464 | 211201.9994 | 467 | 211201.9994 | 470 | 211201.9994 | 472.5 | 211201.9994 | 475.5 | 211201.9994 | 478 | 211201.9994 | 481 | 211201.9994 | 483.5 | 211201.9994 | 486.5 | 211201.9994 | 489.5 | 211201.9994 | 492 | 211201.9994 | 495 | 211201.9994 | 497.5 | 211201.9994 | 500.5 | 211201.9994 | 503.5 | 211201.9994 | 506 | 211201.9994 | 509 | 211201.9994 | 511.5 | 211201.9994 | 455.5 | 211201.9994
514.5 | 211201.9994 | 517.5 | 211201.9994 | 520 | 211201.9994 | 523 | 211201.9994 | 525.5 | 211201.9994 | 528.5 | 211201.9994 | 531.5 | 211201.9994 | 534 | 211201.9994 | 537 | 211201.9994 | 539.5 | 211201.9994 | 542.5 | 211201.9994 | 545.5 | 211201.9994 | 548 | 211201.9994 | 551 | 211201.9994 | 553.5 | 211201.9994 | 556.5 | 211201.9994 | 559.5 | 211201.9994 | 562 | 211201.9994 | 565 | 211201.9994 | 567.5 | 211201.9994 | 570.5 | 211201.9994 | 514.5 | 211201.9994
573.5 | 211201.9994 | 576 | 211201.9994 | 579 | 211201.9994 | 581.5 | 211201.9994 | 584.5 | 211201.9994 | 587.5 | 211201.9994 | 590 | 211201.9994 | 593 | 211201.9994 | 595.5 | 211201.9994 | 598.5 | 211201.9994 | 601.5 | 211201.9994 | 604 | 211201.9994 | 607 | 211201.9994 | 609.5 | 211201.9994 | 612.5 | 211201.9994 | 615.5 | 211201.9994 | 618 | 211201.9994 | 621 | 211201.9994 | 623.5 | 211201.9994 | 626.5 | 211201.9994 | 629.5 | 211201.9994 | 573.5 | 211201.9994
632 | 211201.9994 | 635 | 211201.9994 | 637.5 | 211201.9994 | 640.5 | 211201.9994 | 643.5 | 211201.9994 | 646 | 211201.9994 | 649 | 211201.9994 | 651.5 | 211201.9994 | 654.5 | 211201.9994 | 657.5 | 211201.9994 | 660 | 211201.9994 | 663 | 211201.9994 | 665.5 | 211201.9994 | 668.5 | 211201.9994 | 671.5 | 211201.9994 | 674 | 211201.9994 | 677 | 211201.9994 | 679.5 | 211201.9994 | 682.5 | 211201.9994 | 685.5 | 211201.9994 | 688 | 211201.9994 | 632 | 211201.9994
691 | 211201.9994 | 693.5 | 211201.9994 | 696.5 | 211201.9994 | 699.5 | 211201.9994 | 702 | 211201.9994 | 705 | 211201.9994 | 707.5 | 211201.9994 | 710.5 | 211201.9994 | 713.5 | 211201.9994 | 716 | 211201.9994 | 719 | 211201.9994 | 721.5 | 211201.9994 | 724.5 | 211201.9994 | 727.5 | 211201.9994 | 730 | 211201.9994 | 733 | 211201.9994 | 735.5 | 211201.9994 | 738.5 | 211201.9994 | 741.5 | 211201.9994 | 744 | 211201.9994 | 747 | 211201.9994 | 691 | 211201.9994
749.5 | 211201.9994 | 752.5 | 211201.9994 | 755.5 | 211201.9994 | 758 | 211201.9994 | 761 | 211201.9994 | 763.5 | 211201.9994 | 766.5 | 211201.9994 | 769.5 | 211201.9994 | 772 | 211201.9994 | 775 | 211201.9994 | 777.5 | 211201.9994 | 780.5 | 211201.9994 | 783.5 | 211201.9994 | 786 | 211201.9994 | 789 | 211201.9994 | 791.5 | 211201.9994 | 794.5 | 211201.9994 | 797.5 | 211201.9994 | 800 | 211201.9994 | 803 | 211201.9994 | 805.5 | 211201.9994 | 749.5 | 211201.9994
808.5 | 211201.9994 | 811.5 | 211201.9994 | 814 | 211201.9994 | 817 | 211201.9994 | 819.5 | 211201.9994 | 822.5 | 211201.9994 | 825.5 | 211201.9994 | 828 | 211201.9994 | 831 | 211201.9994 | 833.5 | 211201.9994 | 836.5 | 211201.9994 | 839.5 | 211002.0947 | 842 | 211201.9994 | 845 | 211201.9994 | 847.5 | 211201.9994 | 850.5 | 211201.9994 | 853.5 | 211201.9994 | 856 | 211201.9994 | 859 | 211201.9994 | 861.5 | 211201.9994 | 864.5 | 211201.9994 | 808.5 | 211002.0947
867.5 | 211201.9994 | 870 | 211201.9994 | 873 | 211201.9994 | 875.5 | 211201.9994 | 878.5 | 211201.9994 | 881.5 | 211201.9994 | 884 | 211201.9994 | 887 | 211201.9994 | 889.5 | 211201.9994 | 892.5 | 211201.9994 | 895.5 | 211201.9994 | 898 | 211201.9994 | 901 | 211201.9994 | 903.5 | 211201.9994 | 906.5 | 211201.9994 | 909.5 | 211201.9994 | 912 | 211201.9994 | 915 | 211201.9994 | 917.5 | 211201.9994 | 920.5 | 211201.9994 | 923.5 | 211201.9994 | 867.5 | 211201.9994
926 | 211201.9994 | 929 | 211201.9994 | 931.5 | 211201.9994 | 934.5 | 211201.9994 | 937.5 | 211201.9994 | 940 | 211201.9994 | 943 | 211201.9994 | 945.5 | 211201.9994 | 948.5 | 211201.9994 | 951.5 | 211201.9994 | 954 | 211201.9994 | 957 | 211201.9994 | 959.5 | 211201.9994 | 962.5 | 211201.9994 | 965.5 | 211201.9994 | 968 | 211201.9994 | 971 | 211201.9994 | 973.5 | 211201.9994 | 976.5 | 211201.9994 | 979.5 | 211201.9994 | 982 | 211201.9994 | 926 | 211201.9994
985 | 211201.9994 | 987.5 | 211201.9994 | 990.5 | 211201.9994 | 993.5 | 211201.9994 | 996 | 211201.9994 | 999 | 211201.9994 | 1001.5 | 211201.9994 | 1004.5 | 211201.9994 | 1007.5 | 211201.9994 | 1010 | 211201.9994 | 1013 | 211201.9994 | 1015.5 | 211201.9994 | 1018.5 | 211201.9994 | 1021.5 | 211201.9994 | 1024 | 211201.9994 | 1027 | 211201.9994 | 1029.5 | 211201.9994 | 1032.5 | 211201.9994 | 1035.5 | 211201.9994 | 1038 | 211201.9994 | 1041 | 211201.9994 | 985 | 211201.9994
1043.5 | 211201.9994 | 1046.5 | 211201.9994 | 1049.5 | 211002.0947 | 1052 | 211201.9994 | 1055 | 211201.9994 | 1057.5 | 211201.9994 | 1060.5 | 211201.9994 | 1063.5 | 211201.9994 | 1066 | 211201.9994 | 1069 | 211201.9994 | 1071.5 | 211201.9994 | 1074.5 | 211201.9994 | 1077.5 | 211201.9994 | 1080 | 211201.9994 | 1083 | 211201.9994 | 1085.5 | 211201.9994 | 1088.5 | 211201.9994 | 1091.5 | 211201.9994 | 1093 | 211201.9994 | 1097 | 211201.9994 | 1099.5 | 211201.9994 | 1043.5 | 211002.0947
1102.5 | 211201.9994 | 1105.5 | 211201.9994 | 1108 | 211201.9994 | 1111 | 211201.9994 | 1113.5 | 211201.9994 | 1116.5 | 211201.9994 | 1119.5 | 211201.9994 | 1122 | 211201.9994 | 1125 | 211201.9994 | 1127.5 | 211201.9994 | 1130.5 | 211201.9994 | 1133.5 | 211201.9994 | 1136 | 211201.9994 | 1139 | 211201.9994 | 1141.5 | 211201.9994 | 1144.5 | 211201.9994 | 1147.5 | 211201.9994 | 1150 | 211201.9994 | 1153 | 211201.9994 | 1155.5 | 211201.9994 | 1158.5 | 211201.9994 | 1102.5 | 211201.9994
1161.5 | 211201.9994 | 1164 | 211201.9994 | 1167 | 211201.9994 | 1169.5 | 211201.9994 | 1172.5 | 211201.9994 | 1175.5 | 211201.9994 | 1178 | 211201.9994 | 1181 | 211201.9994 | 1183.5 | 211201.9994 | 1186.5 | 211201.9994 | 1189 | 211201.9994 | 1192 | 211201.9994 | 1195 | 211201.9994 | 1197.5 | 211201.9994 | 1200.5 | 211201.9994 | 1203 | 211201.9994 | 1206 | 211201.9994 | 1209 | 211201.9994 | 1211.5 | 211201.9994 | 1214.5 | 211201.9994 | 1217.5 | 211201.9994 | 1161.5 | 211201.9994
1220 | 211201.9994 | 1223 | 211201.9994 | 1225.5 | 211201.9994 | 1228.5 | 211201.9994 | 1231 | 211201.9994 | 1234 | 211201.9994 | 1236.5 | 211201.9994 | 1239.5 | 211201.9994 | 1242.5 | 211201.9994 | 1245.5 | 211201.9994 | 1248 | 211002.0947 | 1251 | 211201.9994 | 1253.5 | 211201.9994 | 1256.5 | 211201.9994 | 1259.5 | 211201.9994 | 1262 | 211201.9994 | 1265 | 211201.9994 | 1267.5 | 211201.9994 | 1270.5 | 211201.9994 | 1273.5 | 211201.9994 | 1276 | 211201.9994 | 1220 | 211002.0947
1279 | 211201.9994 | 1281.5 | 211201.9994 | 1284.5 | 211201.9994 | 1287.5 | 211201.9994 | 1290 | 211201.9994 | 1293 | 211201.9994 | 1295.5 | 29640.5821 | 1298.5 | 102815.1371 | 1301.5 | 105400.9527 | 1304 | 211001.9527 | 1307 | 211201.9994 | 1309.5 | 211201.9994 | 1312.5 | 211002.0947 | 1315.5 | 211002.0947 | 1318 | 211201.9994 | 1321 | 8.5957 | 1323.5 | 1070.6844 | 1326.5 | 2840.1708 | 1329.5 | 13.1896 | 1332 | 34.721 | 1335 | 35.6689 | 1279 | 8.5957
1337.5 | 198.854 | 1340.5 | 0.43192 | 1343.5 | 1050.2984 | 1346 | 2.5697 | 1349 | 27.4 | 1351.5 | 3941.8074 | 1354.5 | 9.3101 | 1357 | 4.3524 | 1360 | 29.4899 | 1362.5 | 10.0201 | 1365.5 | 5371.8477 | 1368.5 | 4.0111 | 1371 | 13.6228 | 1374 | 18.2165 | 1377 | 1416.2066 | 1379.5 | 467.9176 | 1382.5 | 40.9407 | 1385.5 | 2.6946 | 1388 | 17.744 | 1391 | 7.0115 | 1393.5 | 6.8336 | 1337.5 | 0.43192
1396.5 | 15.0764 | 1399 | 21.9997 | 1402 | 2737.9455 | 1405 | 19.7371 | 1407.5 | 10.3033 | 1410.5 | 8.7488 | 1413.5 | 7.2192 | 1416 | 3563.292 | 1419 | 16.8855 | 1421.5 | 12.9862 | 1424.5 | 0.057059 | 1427.5 | 8597.7281 | 1430 | 18.8824 | 1432.5 | 3.8564 | 1435.5 | 17.4627 | 1438.5 | 8617.8164 | 1441 | 13887.3495 | 1444 | 16054.4352 | 1447 | 20.864 | 1449.5 | 14.5264 | 1452.5 | 32.735 | 1396.5 | 0.057059
1455 | 30.9494 | 1458 | 8.0028 | 1461 | 6018.5538 | 1463.5 | 38.2355 | 1466.5 | 21.8353 | 1469.5 | 15.0965 | 1472 | 5.8431 | 1475 | 6843.8785 | 1477.5 | 34.518 | 1480.5 | 1.8978 | 1483.5 | 9.1581 | 1486 | 9896.3196 | 1488.5 | 0.95551 | 1491.5 | 5.9215 | 1494.5 | 11.6235 | 1497.5 | 6218.1096 | 1500 | 8270.0839 | 1502.5 | 18965.2601 | 1505.5 | 5.9331 | 1508.5 | 23.3742 | 1511 | 7.111 | 1455 | 0.95551
1514 | 10.9344 | 1516.5 | 18.6776 | 1519.5 | 10396.2169 | 1522.5 | 11.4434 | 1525 | 6.7976 | 1528 | 22.1591 | 1531 | 4.831 | 1533.5 | 9928.4982 | 1536.5 | 1.8857 | 1539.5 | 17.5203 | 1542 | 1.2224 | 1544.5 | 9031.3997 | 1547.5 | 18.9151 | 1550.5 | 7.7296 | 1553 | 20.7942 | 1556 | 10400.9536 | 1559 | 20920.7655 | 1561.5 | 23278.461 | 1564.5 | 25.0683 | 1567.5 | 23.768 | 1570 | 7.875 | 1514 | 1.2224
1572.5 | 14.8798 | 1576 | 1.3405 | 1578.5 | 9891.6619 | 1581.5 | 2.8695 | 1584 | 7.2936 | 1586.5 | 9.6919 | 1589.5 | 1.6111 | 1592.5 | 9461.6309 | 1595 | 11.5023 | 1598 | 0.088193 | 1601 | 0.50889 | 1603.5 | 10396.0843 | 1606.5 | 6.5156 | 1609 | 4.8152 | 1612 | 28.9043 | 1614.5 | 11562.1916 | 1617.5 | 20950.582 | 1620.5 | 23289.3577 | 1623 | 10.533 | 1626 | 2.8077 | 1628.5 | 4.9622 | 1572.5 | 0.088193
1631.5 | 20.1805 | 1634.5 | 24.4017 | 1637 | 10400.97 | 1640 | 29.988 | 1642.5 | 28.4672 | 1645.5 | 5.0524 | 1648.5 | 4.3917 | 1651.5 | 10016.0299 | 1654 | 1.3656 | 1657 | 4.0993 | 1659.5 | 30.5388 | 1662.5 | 10953.6036 | 1665 | 5.8737 | 1668 | 6.7427 | 1670.5 | 7.8394 | 1673.5 | 11590.1631 | 1676.5 | 171.8123 | 1679 | 132.3326 | 1682 | 4.9899 | 1684.5 | 3.4526 | 1687.5 | 3.8535 | 1631.5 | 1.3656
1690.5 | 15.464 | 1693 | 29.3 | 1696 | 142.311 | 1698.5 | 11.7593 | 1701.5 | 1.927 | 1704.5 | 13.8129 | 1707 | 15.4854 | 1710 | 5.8679 | 1713 | 1.7242 | 1715.5 | 35.8036 | 1718.5 | 5.8751 | 1721 | 42.2044 | 1724 | 8.9292 | 1726.5 | 4.9492 | 1729.5 | 9.575 | 1732.5 | 4.2043 | 1735.5 | 5.4486 | 1738 | 6.8288 | 1740.5 | 11.8462 | 1743.5 | 19.9596 | 1746.5 | 9.4292 | 1690.5 | 1.7242
1749 | 6.311 | 1752 | 28.5897 | 1755 | 25.4459 | 1757.5 | 1.0459 | 1760.5 | 28.1804 | 1763 | 7.4578 | 1766 | 17.841 | 1768.5 | 30.2899 | 1771.5 | 24.0287 | 1774.5 | 17.2023 | 1777 | 2.2433 | 1780 | 4.3932 | 1782.5 | 19.2202 | 1785.5 | 10.5481 | 1788.5 | 15.1919 | 1791 | 16.9449 | 1794 | 44.8327 | 1796.5 | 15.232 | 1799.5 | 7.2315 | 1802.5 | 35.5068 | 1805 | 7.819 | 1749 | 1.0459
1808 | 18.7229 | 1810.5 | 7.2917 | 1813.5 | 5.6704 | 1816.5 | 31.2658 | 1819 | 16.1902 | 1822 | 8.665 | 1824.5 | 12.066 | 1827.5 | 7.1432 | 1830.5 | 19.0902 | 1833 | 38.4163 | 1836 | 7.1244 | 1838.5 | 0.55894 | 1841.5 | 13.0596 | 1844.5 | 31.9927 | 1847 | 10.4401 | 1850 | 18.114 | 1852.5 | 41.736 | 1855.5 | 9.7685 | 1858.5 | 8.2363 | 1861 | 2.3579 | 1864 | 4.9103 | 1808 | 0.55894
1866.5 | 23.1152 | 1869.5 | 16.031 | 1872.5 | 0.59704 | 1875 | 39.8773 | 1878 | 1.7009 | 1880.5 | 1.5671 | 1883.5 | 3.0481 | 1886.5 | 1.406 | 1889 | 39.8752 | 1892 | 3.3842 | 1894.5 | 5.1914 | 1897.5 | 0.65068 | 1900.5 | 6.9085 | 1903 | 31.4773 | 1906 | 2.3544 | 1908.5 | 8.9902 | 1911.5 | 16.2218 | 1914.5 | 4.0891 | 1917 | 6.1805 | 1920 | 23.4607 | 1922.5 | 0.12857 | 1866.5 | 0.12857
1925.5 | 35.9781 | 1928.5 | 2.0592 | 1931 | 5.7627 | 1934 | 7.5966 | 1936.5 | 1.2826 | 1939.5 | 12.0307 | 1942.5 | 7.7938 | 1945 | 22.4149 | 1948 | 7.7466 | 1950.5 | 9.6438 | 1953.5 | 16.1828 | 1956.5 | 11.9008 | 1959 | 7.8117 | 1962 | 3.9739 | 1964.5 | 18.3888 | 1967.5 | 24.9622 | 1970.5 | 10.6402 | 1973 | 42.484 | 1976 | 21.6679 | 1978.5 | 20.1438 | 1981.5 | 16.7322 | 1925.5 | 1.2826
1984.5 | 33.5515 | 1987 | 17.4686 | 1990 | 34.573 | 1992.5 | 11.4952 | 1996 | 8.3632 | 1998.5 | 8.4888 | 2001 | 6.4529 | 2004 | 1.3382 | 2006.5 | 4.4709 | 2009.5 | 2.382 | 2012.5 | 5.7227 | 2015 | 43.1799 | 2018 | 27.8898 | 2020.5 | 13.6123 | 2023.5 | 9.5375 | 2026.5 | 39.7423 | 2029 | 46.6223 | 2032 | 6.7382 | 2035 | 6.3129 | 2037.5 | 3.5357 | 2040.5 | 15.982 | 1984.5 | 1.3382
2043 | 28.4664 | 2046 | 28.02 | 2048.5 | 50.2551 | 2051.5 | 9.5571 | 2054.5 | 20.1173 | 2057 | 39.8037 | 2060 | 1.76 | 2062.5 | 0.68848 | 2065.5 | 24.3601 | 2068.5 | 11.1538 | 2071 | 15.5402 | 2074 | 47.601 | 2076.5 | 0.089332 | 2079.5 | 34.9674 | 2082.5 | 3.0525 | 2085 | 33.9433 | 2088 | 2.8124 | 2090.5 | 2.1329 | 2093.5 | 3.6675 | 2096.5 | 17.9618 | 2099 | 25.4268 | 2043 | 0.089332
2102 | 27.6744 | 2104.5 | 6.584 | 2107.5 | 22.7605 | 2110.5 | 19.8971 | 2113 | 0.074303 | 2116 | 24.6882 | 2118.5 | 16.2814 | 2121.5 | 6.2416 | 2124.5 | 3.0016 | 2127 | 2.7146 | 2130 | 7.6276 | 2132.5 | 4.9616 | 2135.5 | 8.8329 | 2138.5 | 28.9827 | 2141 | 7.028 | 2144 | 7.3899 | 2146.5 | 19.9889 | 2149.5 | 26.2529 | 2152.5 | 16.4018 | 2155 | 11.2112 | 2158 | 1.4034 | 2102 | 0.074303
2160.5 | 11.248 | 2163.5 | 8.1356 | 2166.5 | 1.3334 | 2169 | 1.531 | 2172 | 17.602 | 2174.5 | 9.2333 | 2177.5 | 33.6381 | 2180.5 | 9.6595 | 2183 | 13.6787 | 2186 | 17.1016 | 2188.5 | 1.1278 | 2191.5 | 3.6132 | 2194.5 | 0.91229 | 2197 | 4.1662 | 2200 | 33.101 | 2202.5 | 130.4356 | 2205.5 | 6.2327 | 2208.5 | 30.5281 | 2211 | 5.4298 | 2214 | 34.1237 | 2216.5 | 15.783 | 2160.5 | 0.91229
2219.5 | 24.9506 | 2222.5 | 36.0788 | 2225 | 18.5557 | 2228 | 14.6464 | 2230.5 | 4.3514 | 2233.5 | 10.4389 | 2236.5 | 3.4793 | 2239 | 5.3192 | 2242 | 20.9092 | 2244.5 | 11.5605 | 2247.5 | 33.3836 | 2250.5 | 40.8858 | 2253 | 10.7151 | 2256 | 9.4419 | 2258.5 | 4.7738 | 2261.5 | 4.6004 | 2264.5 | 2.6759 | 2266 | 0.97068 | 2270 | 0.086471 | 2272.5 | 24.0944 | 2275.5 | 11.8538 | 2219.5 | 0.086471
2278.5 | 26.7888 | 2281 | 4.2627 | 2284 | 23.3479 | 2286.5 | 2.2851 | 2289.5 | 18.3838 | 2292.5 | 8.2484 | 2295 | 1.9814 | 2298 | 6.2112 | 2300.5 | 10.471 | 2303.5 | 5.4668 | 2306.5 | 32.9277 | 2309 | 10.6041 | 2312 | 2.168 | 2314.5 | 13.0562 | 2317.5 | 19.4533 | 2320.5 | 52.2624 | 2323 | 46.1762 | 2326 | 43.6944 | 2328.5 | 15.3998 | 2331.5 | 4.9549 | 2334.5 | 22.8354 | 2278.5 | 1.9814

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 28 |  |  | 2006-08-01 | 12:06
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2
Penlight Penlight Penlight Time | C1-G |  | Penlight Penlight Penlight Time | C2-G | Penlight Penlight Penlight Time | C3-G | Penlight Penlight Penlight Time | C4-G | Penlight Penlight Penlight Time | C5-G | Penlight Penlight Penlight Time | C6-G | Penlight Penlight Penlight Time | C7-G | Penlight Penlight Penlight Time | Minimums Overall
-125.0833 | 211202 |  | -113.5 | 211202 | -105.5833 | 211202 | -100.4167 | 211202 | -97.0833 | 211202 | -94.75 | 211202 | -92.4167 | 211202 | -125.0833 | 211202
-66.3333 | 211202 |  | -54.6667 | 211202 | -46.75 | 211202 | -41.5 | 211202 | -38.5 | 105551 | -36 | 211202 | -33.75 | 211202 | -66.3333 | 105551
-7.5 | 211202 |  | 4.1667 | 211202 | 12.1667 | 211202 | 17.25 | 211202 | 20.5 | 211202 | 22.8333 | 211202 | 25.0833 | 211202 | -7.5 | 211202
51.1667 | 211202 |  | 63 | 211202 | 70.75 | 211202 | 75.9167 | 211202 | 79.1667 | 211202 | 81.5833 | 211202 | 83.9167 | 211202 | 51.1667 | 211202
109.9167 | 211202 |  | 121.75 | 211202 | 129.6667 | 211202 | 134.6667 | 211202 | 138 | 211202 | 140.3333 | 211202 | 142.6667 | 211202 | 109.9167 | 211202
168.6667 | 211202 |  | 180.3333 | 211202 | 188.4167 | 211202 | 193.5833 | 211202 | 196.8333 | 211202 | 199.1667 | 211202 | 201.3333 | 211202 | 168.6667 | 211202
227.6667 | 211202 |  | 239.1667 | 211202 | 247.1667 | 211202 | 252.4167 | 211202 | 255.5833 | 211202 | 257.9167 | 211202 | 260.25 | 211202 | 227.6667 | 211202
286.5 | 211202 |  | 298.0833 | 211202 | 306 | 211202 | 311.1667 | 211202 | 314.5 | 211202 | 316.6667 | 211202 | 319.0833 | 211202 | 286.5 | 211202
345.0833 | 211202 |  | 356.8333 | 211202 | 364.75 | 211202 | 369.8333 | 211202 | 373.0833 | 211202 | 375.5 | 211202 | 377.75 | 211202 | 345.0833 | 211202
403.9167 | 211202 |  | 415.6667 | 211202 | 423.5 | 211202 | 428.5833 | 211202 | 432 | 211202 | 434.25 | 211202 | 436.5833 | 211202 | 403.9167 | 211202
462.75 | 211202 |  | 474.3333 | 211202 | 482.3333 | 211202 | 487.5 | 211202 | 490.6667 | 211202 | 493 | 211202 | 495.4167 | 211202 | 462.75 | 211202
521.5 | 211202 |  | 533.1667 | 211202 | 541.1667 | 211202 | 546.25 | 211202 | 549.5 | 211202 | 551.8333 | 211202 | 554.0833 | 211202 | 521.5 | 211202
580.3333 | 211202 |  | 592 | 211202 | 599.8333 | 211202 | 605.0833 | 211202 | 608.25 | 211202 | 610.5833 | 211202 | 613.0833 | 211202 | 580.3333 | 211202
639.0833 | 211202 |  | 650.75 | 211202 | 658.75 | 211202 | 663.75 | 211202 | 667.0833 | 211202 | 669.5 | 211202 | 671.75 | 211202 | 639.0833 | 211202
697.9167 | 211202 |  | 709.5833 | 211202 | 717.4167 | 211202 | 722.5833 | 211202 | 726 | 211202 | 728.25 | 211202 | 730.5833 | 211202 | 697.9167 | 211202
756.6667 | 211202 |  | 768.3333 | 211202 | 776.3333 | 211202 | 781.5 | 211202 | 784.6667 | 211202 | 787 | 211202 | 789.3333 | 211202 | 756.6667 | 211202
815.5 | 211202 |  | 827.1667 | 211202 | 835.1667 | 211202 | 840.25 | 211202 | 843.5 | 211202 | 845.8333 | 211202 | 848.0833 | 211202 | 815.5 | 211202
874.3333 | 211202 |  | 886 | 211202 | 893.8333 | 211202 | 899.0833 | 211202 | 902.25 | 211202 | 904.5833 | 211202 | 907.0833 | 211202 | 874.3333 | 211202
933.0833 | 211202 |  | 944.75 | 211202 | 952.75 | 211202 | 957.75 | 211202 | 961.0833 | 211202 | 963.5 | 211202 | 965.75 | 211202 | 933.0833 | 211202
991.9167 | 211202 |  | 1003.5833 | 211202 | 1011.4167 | 211202 | 1016.5833 | 211202 | 1020 | 211202 | 1022.25 | 211202 | 1024.5833 | 211202 | 991.9167 | 211202
1050.6667 | 211202 |  | 1062.3333 | 211202 | 1070.3333 | 211202 | 1075.5 | 211202 | 1078.5 | 211202 | 1080.8333 | 211202 | 1083.3333 | 211202 | 1050.6667 | 211202
1109.5 | 211202 |  | 1121.1667 | 211202 | 1129.1667 | 211202 | 1134.25 | 211202 | 1137.5 | 211202 | 1139.8333 | 211202 | 1142.0833 | 211202 | 1109.5 | 211202
1168.3333 | 211202 |  | 1179.9167 | 211202 | 1187.8333 | 211202 | 1193 | 211202 | 1196.1667 | 211202 | 1198.5833 | 211202 | 1201 | 211202 | 1168.3333 | 211202
1227 | 211202 |  | 1238.6667 | 211202 | 1246.6667 | 211202 | 1251.75 | 211202 | 1255.0833 | 211202 | 1257.4167 | 211202 | 1259.75 | 211202 | 1227 | 211202
1285.9167 | 211202 |  | 1297.5833 | 109289.9368 | 1305.4167 | 9354.8714 | 1310.5833 | 3900.6254 | 1314 | 915.9844 | 1316.25 | 1400.1845 | 1318.5833 | 900.0445 | 1285.9167 | 900.0445
1344.6667 | 76.1238 |  | 1356.1667 | 313.673 | 1364.25 | 97.36 | 1369.4167 | 415.6339 | 1372.5833 | 269.2262 | 1374.9167 | 2782.8659 | 1377.3333 | 317.1949 | 1344.6667 | 76.1238
1403.4167 | 114.3209 |  | 1415.1667 | 2.5718 | 1423 | 39.5973 | 1428.1667 | 3753.7504 | 1431.5 | 321.5768 | 1433.6667 | 34.8662 | 1436.0833 | 2.5328 | 1403.4167 | 2.5328
1462.25 | 63.162 |  | 1473.9167 | 123.4584 | 1481.75 | 79.0665 | 1487 | 7907.6047 | 1490.1667 | 209.9922 | 1492.5 | 195.364 | 1494.9167 | 82.0426 | 1462.25 | 63.162
1520.9167 | 157.5077 |  | 1532.75 | 293.2103 | 1540.5 | 355.8432 | 1545.6667 | 15121.0607 | 1549.0833 | 203.7006 | 1551.4167 | 498.513 | 1553.6667 | 524.7045 | 1520.9167 | 157.5077
1579.8333 | 26.5963 |  | 1591.4167 | 40.3146 | 1599.4167 | 38.1633 | 1604.5 | 2005.4423 | 1607.75 | 25.7918 | 1610 | 1053.6179 | 1612.4167 | 36.1105 | 1579.8333 | 25.7918
1638.5 | 243.8439 |  | 1650.3333 | 342.7109 | 1658.1667 | 71.6409 | 1663.3333 | 762.1934 | 1666.5 | 36.6608 | 1668.9167 | 86.4514 | 1671.0833 | 42.4821 | 1638.5 | 36.6608
1697.3333 | 87.0353 |  | 1709.0833 | 7.607 | 1716.8333 | 39.1697 | 1722.1667 | 257.3167 | 1725.3333 | 9.5167 | 1727.6667 | 47.346 | 1730.0833 | 71.3199 | 1697.3333 | 7.607
1756.1667 | 229.3679 |  | 1767.75 | 10.9877 | 1775.75 | 83.284 | 1780.8333 | 141.1739 | 1784.0833 | 137.1387 | 1786.5 | 116.5369 | 1788.75 | 13.5826 | 1756.1667 | 10.9877
1814.9167 | 67.2297 |  | 1826.5833 | 67.8655 | 1834.4167 | 73.3448 | 1839.5833 | 59.6358 | 1843 | 328.2877 | 1845.25 | 196.3986 | 1847.5833 | 183.881 | 1814.9167 | 59.6358
1873.6667 | 170.3249 |  | 1885.3333 | 488.4282 | 1893.3333 | 78.5121 | 1898.5 | 185.7894 | 1901.6667 | 96.0525 | 1904 | 3.6208 | 1906.3333 | 3.7626 | 1873.6667 | 3.6208
1932.5 | 368.5907 |  | 1944.1667 | 141.9373 | 1952.1667 | 157.0042 | 1957.25 | 122.6133 | 1960.5 | 139.4554 | 1962.8333 | 436.8989 | 1965.0833 | 190.0826 | 1932.5 | 122.6133
1991.4167 | 94.1975 |  | 2003 | 89.6844 | 2010.8333 | 116.3478 | 2016.0833 | 104.4008 | 2019.3333 | 76.336 | 2021.75 | 708.3257 | 2024.0833 | 97.0695 | 1991.4167 | 76.336
2050.0833 | 348.191 |  | 2061.75 | 7.1459 | 2069.75 | 9.0791 | 2074.75 | 294.5488 | 2078.0833 | 29.6158 | 2080.5 | 27.9504 | 2082.75 | 213.4411 | 2050.0833 | 7.1459
2108.9167 | 301.8451 |  | 2120.5833 | 263.6766 | 2128.4167 | 90.7782 | 2133.5833 | 173.59 | 2137 | 254.1596 | 2139.25 | 81.8255 | 2141.5833 | 80.1742 | 2108.9167 | 80.1742
2167.6667 | 160.6428 |  | 2179.3333 | 380.8372 | 2187.3333 | 39.0623 | 2192.5 | 35.1262 | 2195.6667 | 635.4772 | 2198 | 160.4713 | 2200.3333 | 141.3239 | 2167.6667 | 35.1262
2226.5 | 202.4554 |  | 2238.1667 | 216.2663 | 2246.1667 | 81.6935 | 2251.0833 | 56.3637 | 2254.5 | 51.0875 | 2256.8333 | 161.1239 | 2258.9167 | 175.1424 | 2226.5 | 51.0875
2285.3333 | 20.054 |  | 2297 | 11.0263 | 2304.8333 | 11.0566 | 2310.0833 | 1071.4277 | 2313.25 | 13.572 | 2315.5833 | 148.6186 | 2318.0833 | 139.0279 | 2285.3333 | 11.0263

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -133 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
1 | -132 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
2 | -131 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
3 | -130 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
4 | -129 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
5 | -128 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
6 | -127 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
7 | -126 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
8 | -125 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
9 | -124 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
10 | -123 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
11 | -122 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
12 | -121 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
13 | -120 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
14 | -119 | 22.5 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
15 | -118 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27.1 | 27.2
16 | -117 | 22.5 | 28.6 | 28.7 | 28.9 | 28.5 | 27 | 27.2
17 | -116 | 22.5 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
18 | -115 | 22.5 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
19 | -114 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
20 | -113 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
21 | -112 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
22 | -111 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
23 | -110 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
24 | -109 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
25 | -108 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
26 | -107 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
27 | -106 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
28 | -105 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
29 | -104 | 22.4 | 28.5 | 28.7 | 28.9 | 28.4 | 27 | 27.1
30 | -103 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
31 | -102 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
32 | -101 | 22.4 | 28.5 | 28.7 | 28.9 | 28.4 | 27 | 27.2
33 | -100 | 22.4 | 28.5 | 28.7 | 28.9 | 28.4 | 27 | 27.2
34 | -99 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.1
35 | -98 | 22.4 | 28.5 | 28.7 | 28.9 | 28.5 | 27 | 27.2
36 | -97 | 22.4 | 29.1 | 27.6 | 29.2 | 29.9 | 27.1 | 27.1
37 | -96 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
38 | -95 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
39 | -94 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
40 | -93 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
41 | -92 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
42 | -91 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
43 | -90 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
44 | -89 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
45 | -88 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
46 | -87 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
47 | -86 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
48 | -85 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
49 | -84 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
50 | -83 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
51 | -82 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
52 | -81 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
53 | -80 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
54 | -79 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
55 | -78 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
56 | -77 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
57 | -76 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
58 | -75 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
59 | -74 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
60 | -73 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
61 | -72 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
62 | -71 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.2 | 27.1
63 | -70 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
64 | -69 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
65 | -68 | 22.3 | 29.9 | 26.1 | 29.7 | 31.9 | 27.1 | 27.1
66 | -67 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
67 | -66 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
68 | -65 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
69 | -64 | 22.3 | 29.9 | 26.1 | 29.7 | 31.9 | 27.1 | 27.1
70 | -63 | 22.3 | 29.9 | 26.1 | 29.7 | 31.9 | 27.1 | 27.1
71 | -62 | 22.3 | 29.9 | 26.1 | 29.7 | 31.9 | 27.1 | 27.1
72 | -61 | 22.3 | 29.9 | 26.2 | 29.7 | 31.9 | 27.1 | 27.1
73 | -60 | 22.3 | 29.9 | 26.1 | 29.7 | 31.9 | 27.1 | 27.1
74 | -59 | 22.3 | 29.9 | 26.1 | 29.7 | 31.9 | 27.1 | 27.1
75 | -58 | 22.3 | 29.9 | 26.1 | 29.7 | 31.9 | 27.1 | 27.1
76 | -57 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
77 | -56 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
78 | -55 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
79 | -54 | 22.3 | 29.9 | 26.2 | 29.6 | 31.9 | 27.1 | 27.1
80 | -53 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
81 | -52 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
82 | -51 | 22.3 | 29.9 | 26.2 | 29.6 | 31.8 | 27.1 | 27.1
83 | -50 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
84 | -49 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
85 | -48 | 22.3 | 29.9 | 26.1 | 29.6 | 31.8 | 27.1 | 27.1
86 | -47 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
87 | -46 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
88 | -45 | 22.3 | 29.9 | 26.1 | 29.6 | 31.8 | 27.1 | 27.1
89 | -44 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
90 | -43 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
91 | -42 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
92 | -41 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
93 | -40 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
94 | -39 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
95 | -38 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
96 | -37 | 22.3 | 29.9 | 26.2 | 29.6 | 31.8 | 27.1 | 27.1
97 | -36 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27.1
98 | -35 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
99 | -34 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
100 | -33 | 22.3 | 29.9 | 26.1 | 29.6 | 31.8 | 27.1 | 27
101 | -32 | 22.3 | 29.9 | 26.1 | 29.6 | 31.8 | 27.1 | 27
102 | -31 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
103 | -30 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
104 | -29 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
105 | -28 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
106 | -27 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
107 | -26 | 22.3 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
108 | -25 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
109 | -24 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
110 | -23 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
111 | -22 | 22.2 | 29.9 | 26.1 | 29.6 | 31.8 | 27.1 | 27
112 | -21 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
113 | -20 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
114 | -19 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
115 | -18 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
116 | -17 | 22.2 | 29.9 | 26.1 | 29.6 | 31.8 | 27.1 | 27
117 | -16 | 22.2 | 29.8 | 26.1 | 29.6 | 31.8 | 27.1 | 27
118 | -15 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
119 | -14 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
120 | -13 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
121 | -12 | 22.2 | 29.8 | 26.1 | 29.6 | 31.9 | 27.1 | 27
122 | -11 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
123 | -10 | 22.2 | 29.8 | 26.1 | 29.6 | 31.8 | 27.1 | 27
124 | -9 | 22.2 | 29.8 | 26.1 | 29.6 | 31.8 | 27.1 | 27
125 | -8 | 22.2 | 29.8 | 26.1 | 29.6 | 31.9 | 27.1 | 27
126 | -7 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
127 | -6 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
128 | -5 | 22.2 | 29.9 | 26.1 | 29.6 | 31.9 | 27.1 | 27
129 | -4 | 22.2 | 30 | 25.6 | 29.7 | 32.2 | 27.2 | 27
130 | -3 | 22.2 | 30.2 | 25.4 | 29.8 | 32.6 | 27.2 | 27
131 | -2 | 22.4 | 30.2 | 25.3 | 29.9 | 32.7 | 27.2 | 27
132 | -1 | 23.3 | 30.3 | 25.3 | 29.9 | 32.7 | 27.2 | 27
133 | 0 | 25 | 30.2 | 25.3 | 29.9 | 32.7 | 27.2 | 27
134 | 1 | 27.3 | 30.2 | 25.3 | 29.9 | 32.6 | 27.2 | 27
135 | 2 | 30.3 | 30.3 | 25.3 | 29.9 | 32.8 | 27.2 | 27.1
136 | 3 | 33.6 | 30.3 | 25.3 | 29.9 | 32.8 | 27.2 | 27.1
137 | 4 | 37.4 | 30.3 | 25.3 | 29.9 | 32.8 | 27.3 | 27.1
138 | 5 | 41.4 | 30.3 | 25.3 | 29.9 | 32.8 | 27.3 | 27.2
139 | 6 | 45.6 | 30.3 | 25.2 | 29.9 | 32.8 | 27.4 | 27.2
140 | 7 | 50.1 | 30.3 | 25.2 | 29.9 | 32.9 | 27.5 | 27.3
141 | 8 | 54.7 | 30.3 | 25.2 | 29.9 | 32.9 | 27.5 | 27.4
142 | 9 | 59.4 | 30.4 | 25.2 | 29.9 | 33 | 27.6 | 27.5
143 | 10 | 64.3 | 30.4 | 25.2 | 29.9 | 33 | 27.7 | 27.6
144 | 11 | 69.3 | 30.4 | 25.2 | 29.9 | 33.1 | 27.9 | 27.7
145 | 12 | 74.3 | 30.5 | 25.2 | 29.9 | 33.1 | 28 | 27.8
146 | 13 | 79.5 | 30.5 | 25.2 | 29.9 | 33.2 | 28.1 | 27.9
147 | 14 | 84.9 | 30.6 | 25.2 | 29.9 | 33.3 | 28.3 | 28
148 | 15 | 90.2 | 30.6 | 25.2 | 29.9 | 33.4 | 28.5 | 28.2
149 | 16 | 95.6 | 30.7 | 25.2 | 29.9 | 33.6 | 28.7 | 28.4
150 | 17 | 101.1 | 30.8 | 25.3 | 29.9 | 33.7 | 28.9 | 28.5
151 | 18 | 106.7 | 30.8 | 25.3 | 29.9 | 33.8 | 29.2 | 28.7
152 | 19 | 112.3 | 30.9 | 25.3 | 29.9 | 34 | 29.4 | 29
153 | 20 | 117.9 | 31 | 25.3 | 30 | 34.2 | 29.7 | 29.2
154 | 21 | 123.6 | 31.2 | 25.3 | 30 | 34.3 | 30 | 29.4
155 | 22 | 129.4 | 31.3 | 25.3 | 30 | 34.5 | 30.2 | 29.6
156 | 23 | 135.2 | 31.4 | 25.3 | 30 | 34.7 | 30.5 | 29.9
157 | 24 | 140.9 | 31.6 | 25.3 | 30 | 35 | 30.9 | 30.2
158 | 25 | 146.6 | 31.7 | 25.4 | 30 | 35.2 | 31.2 | 30.5
159 | 26 | 152.3 | 31.9 | 25.4 | 30.1 | 35.5 | 31.6 | 30.8
160 | 27 | 158 | 32.1 | 25.4 | 30.1 | 35.8 | 32.1 | 31.2
161 | 28 | 163.7 | 32.3 | 25.4 | 30.2 | 36.2 | 32.5 | 31.5
162 | 29 | 169.4 | 32.5 | 25.4 | 30.2 | 36.5 | 32.9 | 31.9
163 | 30 | 175.1 | 32.8 | 25.5 | 30.2 | 36.8 | 33.4 | 32.3
164 | 31 | 180.8 | 33 | 25.5 | 30.3 | 37.2 | 33.8 | 32.7
165 | 32 | 186.6 | 33.3 | 25.6 | 30.3 | 37.6 | 34.3 | 33.1
166 | 33 | 192.3 | 33.5 | 25.6 | 30.4 | 38 | 34.8 | 33.6
167 | 34 | 197.9 | 33.8 | 25.7 | 30.4 | 38.4 | 35.4 | 34
168 | 35 | 203.6 | 34.1 | 25.8 | 30.5 | 38.8 | 35.9 | 34.5
169 | 36 | 209.3 | 34.5 | 25.8 | 30.6 | 39.3 | 36.5 | 35
170 | 37 | 215.1 | 34.8 | 25.9 | 30.6 | 39.8 | 37.1 | 35.6
171 | 38 | 220.7 | 35.2 | 26 | 30.7 | 40.3 | 37.7 | 36.1
172 | 39 | 226.4 | 35.6 | 26.1 | 30.8 | 40.8 | 38.4 | 36.7
173 | 40 | 232.1 | 36 | 26.1 | 30.9 | 41.4 | 39.1 | 37.3
174 | 41 | 237.7 | 36.4 | 26.2 | 31 | 42 | 39.8 | 37.9
175 | 42 | 243.3 | 36.9 | 26.3 | 31.1 | 42.7 | 40.5 | 38.6
176 | 43 | 249 | 37.3 | 26.5 | 31.2 | 43.3 | 41.3 | 39.2
177 | 44 | 254.5 | 37.8 | 26.5 | 31.3 | 44 | 42.1 | 39.9
178 | 45 | 260.1 | 38.3 | 26.6 | 31.5 | 44.7 | 42.8 | 40.7
179 | 46 | 265.7 | 38.9 | 26.7 | 31.6 | 45.4 | 43.6 | 41.4
180 | 47 | 271.3 | 39.4 | 26.9 | 31.7 | 46.1 | 44.5 | 42.2
181 | 48 | 277 | 40 | 27 | 31.9 | 46.9 | 45.3 | 43
182 | 49 | 282.4 | 40.6 | 27.2 | 32.1 | 47.7 | 46.3 | 43.8
183 | 50 | 287.8 | 41.2 | 27.3 | 32.2 | 48.5 | 47.3 | 44.7
184 | 51 | 293.3 | 41.9 | 27.5 | 32.4 | 49.3 | 48.2 | 45.5
185 | 52 | 298.8 | 42.5 | 27.7 | 32.6 | 50.2 | 49.2 | 46.4
186 | 53 | 304.3 | 43.2 | 27.9 | 32.8 | 51.1 | 50.3 | 47.4
187 | 54 | 309.6 | 43.9 | 28.1 | 33 | 52 | 51.3 | 48.3
188 | 55 | 314.9 | 44.7 | 28.3 | 33.2 | 53 | 52.3 | 49.3
189 | 56 | 320.2 | 45.4 | 28.5 | 33.4 | 54 | 53.4 | 50.3
190 | 57 | 325.5 | 46.2 | 28.8 | 33.7 | 55 | 54.5 | 51.4
191 | 58 | 330.7 | 47.1 | 29 | 33.9 | 56.1 | 55.7 | 52.4
192 | 59 | 336 | 47.9 | 29.2 | 34.2 | 57.1 | 57 | 53.5
193 | 60 | 341.3 | 48.7 | 29.5 | 34.4 | 58.2 | 58.2 | 54.7
194 | 61 | 346.6 | 49.6 | 29.7 | 34.7 | 59.3 | 59.4 | 55.9
195 | 62 | 351.8 | 50.5 | 30 | 35 | 60.5 | 60.7 | 57.1
196 | 63 | 357 | 51.5 | 30.3 | 35.3 | 61.7 | 62.1 | 58.3
197 | 64 | 362.3 | 52.4 | 30.6 | 35.6 | 62.9 | 63.4 | 59.5
198 | 65 | 367.4 | 53.4 | 30.9 | 35.9 | 64.2 | 64.8 | 60.8
199 | 66 | 372.5 | 54.4 | 31.3 | 36.3 | 65.6 | 66.2 | 62.1
200 | 67 | 377.6 | 55.5 | 31.6 | 36.6 | 66.9 | 67.7 | 63.5
201 | 68 | 382.7 | 56.5 | 32 | 37 | 68.3 | 69.2 | 64.8
202 | 69 | 387.7 | 57.6 | 32.3 | 37.4 | 69.8 | 70.7 | 66.2
203 | 70 | 392.6 | 58.7 | 32.7 | 37.8 | 71.3 | 72.2 | 67.6
204 | 71 | 397.5 | 59.9 | 33.1 | 38.2 | 72.8 | 73.8 | 69.1
205 | 72 | 402.6 | 61.1 | 33.5 | 38.6 | 74.4 | 75.5 | 70.6
206 | 73 | 407.5 | 62.3 | 33.9 | 39 | 76 | 77.1 | 72.2
207 | 74 | 412.3 | 63.6 | 34.3 | 39.4 | 77.6 | 78.9 | 73.7
208 | 75 | 417.2 | 64.9 | 34.8 | 39.9 | 79.2 | 80.6 | 75.3
209 | 76 | 422.1 | 66.3 | 35.3 | 40.4 | 80.9 | 82.3 | 77
210 | 77 | 426.9 | 67.7 | 35.7 | 40.8 | 82.6 | 84 | 78.6
211 | 78 | 431.8 | 69.1 | 36.2 | 41.3 | 84.3 | 85.8 | 80.4
212 | 79 | 436.7 | 70.5 | 36.9 | 41.8 | 85.8 | 87.7 | 82.1
213 | 80 | 441.3 | 72 | 37.3 | 42.3 | 87.7 | 89.5 | 83.9
214 | 81 | 445.6 | 73.5 | 37.9 | 42.9 | 89.5 | 91.4 | 85.6
215 | 82 | 449.4 | 75.1 | 38.4 | 43.4 | 91.4 | 93.4 | 87.4
216 | 83 | 452.6 | 76.6 | 39 | 44 | 93.3 | 95.2 | 89.2
217 | 84 | 455.5 | 78.2 | 39.6 | 44.6 | 95.2 | 97.1 | 90.9
218 | 85 | 458.4 | 79.8 | 40.2 | 45.2 | 97.1 | 99 | 92.7
219 | 86 | 461.1 | 81.5 | 40.7 | 45.8 | 99 | 100.9 | 94.4
220 | 87 | 463.8 | 83.1 | 41.3 | 46.4 | 101 | 102.8 | 96.1
221 | 88 | 466.3 | 84.8 | 41.9 | 47 | 102.9 | 104.7 | 97.9
222 | 89 | 468.7 | 86.4 | 42.6 | 47.7 | 104.8 | 106.6 | 99.6
223 | 90 | 470.8 | 88.1 | 43.4 | 48.3 | 106.6 | 108.5 | 101.3
224 | 91 | 472.7 | 89.7 | 44.3 | 48.9 | 108.4 | 110.3 | 103
225 | 92 | 474.3 | 91.3 | 45.1 | 49.5 | 110.1 | 112.2 | 104.7
226 | 93 | 475.6 | 92.9 | 46 | 50.1 | 111.7 | 114 | 106.4
227 | 94 | 476.5 | 94.6 | 46.8 | 50.8 | 113.6 | 115.8 | 108
228 | 95 | 477.3 | 96.4 | 47.5 | 51.6 | 115.6 | 117.6 | 109.7
229 | 96 | 477.8 | 98.1 | 48.2 | 52.3 | 117.4 | 119.3 | 111.3
230 | 97 | 478 | 99.8 | 49 | 53 | 119.2 | 121 | 113
231 | 98 | 478 | 101.5 | 49.8 | 53.7 | 120.9 | 122.6 | 114.6
232 | 99 | 478 | 103.2 | 50.6 | 54.5 | 122.8 | 124.2 | 116.1
233 | 100 | 477.9 | 104.9 | 51.4 | 55.2 | 124.6 | 125.8 | 117.7
234 | 101 | 477.7 | 106.6 | 52.2 | 56 | 126.3 | 127.4 | 119.2
235 | 102 | 477.3 | 108.2 | 53 | 56.8 | 128.1 | 128.9 | 120.7
236 | 103 | 476.8 | 109.9 | 53.8 | 57.6 | 129.8 | 130.3 | 122.2
237 | 104 | 476.3 | 111.6 | 54.6 | 58.4 | 131.5 | 131.8 | 123.6
238 | 105 | 475.7 | 113.2 | 55.4 | 59.2 | 133.2 | 133.2 | 125
239 | 106 | 475.1 | 114.9 | 56.2 | 60 | 134.9 | 134.6 | 126.4
240 | 107 | 474.5 | 116.5 | 57 | 60.8 | 136.5 | 135.9 | 127.8
241 | 108 | 473.9 | 118.1 | 57.8 | 61.7 | 138.1 | 137.3 | 129.1
242 | 109 | 473.3 | 119.7 | 58.6 | 62.5 | 139.7 | 138.6 | 130.4
243 | 110 | 472.6 | 121.3 | 59.4 | 63.3 | 141.3 | 139.9 | 131.7
244 | 111 | 472 | 122.9 | 60.3 | 64.2 | 142.9 | 141.1 | 133
245 | 112 | 471.4 | 124.5 | 61.1 | 65 | 144.4 | 142.4 | 134.2
246 | 113 | 470.7 | 126 | 61.9 | 65.8 | 145.9 | 143.6 | 135.4
247 | 114 | 469.9 | 127.5 | 62.8 | 66.7 | 147.3 | 144.8 | 136.6
248 | 115 | 469.2 | 128.9 | 63.7 | 67.5 | 148.7 | 145.9 | 137.7
249 | 116 | 468.5 | 130.4 | 64.5 | 68.4 | 150.1 | 147.1 | 138.9
250 | 117 | 467.7 | 131.9 | 65.4 | 69.2 | 151.5 | 148.2 | 140
251 | 118 | 467 | 133.3 | 66.2 | 70.1 | 153 | 149.3 | 141.1
252 | 119 | 466.4 | 134.8 | 67 | 71 | 154.4 | 150.4 | 142.2
253 | 120 | 465.9 | 136.2 | 67.9 | 71.8 | 155.8 | 151.5 | 143.2
254 | 121 | 465.4 | 137.6 | 68.7 | 72.7 | 157.3 | 152.6 | 144.3
255 | 122 | 465.1 | 139 | 69.5 | 73.6 | 158.7 | 153.6 | 145.3
256 | 123 | 464.6 | 140.4 | 70.3 | 74.5 | 160.1 | 154.6 | 146.4
257 | 124 | 464.3 | 141.8 | 71.1 | 75.4 | 161.6 | 155.7 | 147.4
258 | 125 | 464 | 143.2 | 71.8 | 76.2 | 163 | 156.7 | 148.4
259 | 126 | 463.8 | 144.6 | 72.6 | 77.1 | 164.4 | 157.7 | 149.4
260 | 127 | 463.6 | 145.9 | 73.5 | 78 | 165.7 | 158.7 | 150.4
261 | 128 | 463.6 | 147.2 | 74.3 | 78.8 | 167 | 159.7 | 151.4
262 | 129 | 463.6 | 148.5 | 75.2 | 79.7 | 168.3 | 160.7 | 152.3
263 | 130 | 463.7 | 149.8 | 76 | 80.5 | 169.5 | 161.7 | 153.3
264 | 131 | 463.8 | 151.1 | 76.8 | 81.4 | 170.8 | 162.7 | 154.3
265 | 132 | 464 | 152.4 | 77.7 | 82.2 | 172 | 163.6 | 155.2
266 | 133 | 464.1 | 153.6 | 78.5 | 83.1 | 173.2 | 164.6 | 156.2
267 | 134 | 464.5 | 154.9 | 79.4 | 83.9 | 174.4 | 165.6 | 157.2
268 | 135 | 464.9 | 156.2 | 80.1 | 84.7 | 175.7 | 166.5 | 158.1
269 | 136 | 465.1 | 157.4 | 81 | 85.6 | 176.9 | 167.5 | 159.1
270 | 137 | 465.3 | 158.6 | 81.8 | 86.4 | 178 | 168.4 | 160
271 | 138 | 465.5 | 159.8 | 82.6 | 87.2 | 179.1 | 169.4 | 160.9
272 | 139 | 465.6 | 161.1 | 83.5 | 88.1 | 180.3 | 170.4 | 161.9
273 | 140 | 465.7 | 162.3 | 84.2 | 88.9 | 181.5 | 171.3 | 162.8
274 | 141 | 465.8 | 163.5 | 85.1 | 89.7 | 182.6 | 172.3 | 163.7
275 | 142 | 465.9 | 164.7 | 85.9 | 90.5 | 183.7 | 173.2 | 164.6
276 | 143 | 466 | 165.9 | 86.7 | 91.3 | 184.9 | 174.2 | 165.5
277 | 144 | 466.2 | 167.1 | 87.4 | 92.2 | 186 | 175.1 | 166.4
278 | 145 | 466.3 | 168.2 | 88.2 | 93 | 187.1 | 176.1 | 167.3
279 | 146 | 466.5 | 169.4 | 89 | 93.8 | 188.2 | 177 | 168.2
280 | 147 | 466.7 | 170.6 | 89.8 | 94.6 | 189.3 | 177.9 | 169.1
281 | 148 | 467 | 171.7 | 90.6 | 95.4 | 190.2 | 178.8 | 170
282 | 149 | 467.3 | 172.8 | 91.4 | 96.3 | 191.3 | 179.8 | 170.9
283 | 150 | 467.6 | 174 | 92.2 | 97.1 | 192.4 | 180.7 | 171.7
284 | 151 | 467.6 | 175.1 | 93 | 97.9 | 193.4 | 181.6 | 172.6
285 | 152 | 467.8 | 176.2 | 93.9 | 98.8 | 194.4 | 182.5 | 173.5
286 | 153 | 467.9 | 177.3 | 94.7 | 99.6 | 195.4 | 183.4 | 174.3
287 | 154 | 468.1 | 178.4 | 95.5 | 100.5 | 196.4 | 184.3 | 175.2
288 | 155 | 468.4 | 179.5 | 96.4 | 101.3 | 197.3 | 185.1 | 176
289 | 156 | 468.4 | 180.6 | 97.3 | 102.1 | 198.3 | 186 | 176.8
290 | 157 | 468.5 | 181.7 | 98.1 | 103 | 199.3 | 186.9 | 177.6
291 | 158 | 468.5 | 182.8 | 99 | 103.8 | 200.2 | 187.8 | 178.4
292 | 159 | 468.6 | 183.8 | 99.9 | 104.6 | 201.2 | 188.7 | 179.2
293 | 160 | 468.5 | 184.9 | 100.7 | 105.4 | 202.1 | 189.6 | 180
294 | 161 | 468.4 | 185.9 | 101.6 | 106.2 | 203 | 190.4 | 180.8
295 | 162 | 468.4 | 186.9 | 102.4 | 107 | 203.9 | 191.3 | 181.6
296 | 163 | 468.4 | 187.9 | 103.2 | 107.8 | 204.9 | 192.1 | 182.4
297 | 164 | 468.4 | 188.9 | 104 | 108.6 | 205.8 | 193 | 183.2
298 | 165 | 468.4 | 189.9 | 104.8 | 109.3 | 206.7 | 193.8 | 183.9
299 | 166 | 468.4 | 190.8 | 105.6 | 110.1 | 207.6 | 194.6 | 184.7
300 | 167 | 468.2 | 191.8 | 106.3 | 110.8 | 208.5 | 195.4 | 185.4
301 | 168 | 468 | 192.7 | 107.1 | 111.6 | 209.4 | 196.2 | 186.2
302 | 169 | 467.9 | 193.6 | 107.8 | 112.4 | 210.3 | 197.1 | 186.9
303 | 170 | 467.8 | 194.6 | 108.5 | 113.2 | 211.2 | 197.9 | 187.7
304 | 171 | 467.8 | 195.5 | 109.3 | 114 | 212.1 | 198.7 | 188.4
305 | 172 | 467.7 | 196.4 | 110 | 114.8 | 213 | 199.5 | 189.1
306 | 173 | 467.6 | 197.3 | 110.8 | 115.6 | 214 | 200.3 | 189.8
307 | 174 | 467.7 | 198.2 | 111.6 | 116.4 | 214.9 | 201.1 | 190.6
308 | 175 | 467.6 | 199.1 | 112.5 | 117.3 | 215.8 | 201.8 | 191.3
309 | 176 | 467.5 | 200 | 113.3 | 118.1 | 216.7 | 202.6 | 192
310 | 177 | 467.6 | 200.9 | 114.2 | 119 | 217.7 | 203.4 | 192.7
311 | 178 | 467.6 | 201.8 | 115.1 | 120 | 218.7 | 204.2 | 193.4
312 | 179 | 467.5 | 202.7 | 116.1 | 120.9 | 219.6 | 205 | 194.1
313 | 180 | 467.5 | 203.6 | 117.1 | 121.9 | 220.5 | 205.7 | 194.8
314 | 181 | 467.7 | 204.5 | 118.1 | 122.9 | 221.5 | 206.5 | 195.4
315 | 182 | 468 | 205.3 | 119.2 | 123.9 | 222.4 | 207.3 | 196.1
316 | 183 | 468.1 | 206.2 | 120.3 | 124.9 | 223.3 | 208 | 196.8
317 | 184 | 468.3 | 207.1 | 121.4 | 125.8 | 224.2 | 208.8 | 197.5
318 | 185 | 468.4 | 207.9 | 122.5 | 126.7 | 225.1 | 209.6 | 198.2
319 | 186 | 468.4 | 208.8 | 123.6 | 127.5 | 226.1 | 210.4 | 198.8
320 | 187 | 468.5 | 209.7 | 124.5 | 128.4 | 227 | 211.1 | 199.5
321 | 188 | 468.6 | 210.6 | 125.5 | 129.2 | 227.9 | 211.9 | 200.1
322 | 189 | 468.9 | 211.5 | 126.5 | 130 | 228.9 | 212.7 | 200.8
323 | 190 | 469 | 212.4 | 127.4 | 130.8 | 229.8 | 213.4 | 201.5
324 | 191 | 469.2 | 213.2 | 128.3 | 131.6 | 230.8 | 214.2 | 202.1
325 | 192 | 469.2 | 214.1 | 129.3 | 132.4 | 231.8 | 214.9 | 202.8
326 | 193 | 469.3 | 215 | 130.2 | 133.1 | 232.7 | 215.6 | 203.4
327 | 194 | 469.4 | 215.9 | 131.1 | 133.9 | 233.8 | 216.4 | 204.1
328 | 195 | 469.5 | 216.8 | 132 | 134.7 | 234.8 | 217.2 | 204.7
329 | 196 | 469.6 | 217.6 | 132.9 | 135.4 | 235.8 | 217.9 | 205.3
330 | 197 | 469.7 | 218.5 | 133.8 | 136.2 | 236.9 | 218.6 | 206
331 | 198 | 469.9 | 219.4 | 134.7 | 136.9 | 237.8 | 219.4 | 206.6
332 | 199 | 470.1 | 220.3 | 135.6 | 137.7 | 238.4 | 220.1 | 207.2
333 | 200 | 470 | 221.2 | 136.5 | 138.5 | 239 | 220.8 | 207.8
334 | 201 | 470 | 222 | 137.4 | 139.3 | 239.5 | 221.5 | 208.4
335 | 202 | 469.8 | 222.9 | 138.4 | 140.1 | 239.9 | 222.2 | 209.1
336 | 203 | 469.8 | 223.8 | 139.3 | 140.9 | 240.4 | 223 | 209.7
337 | 204 | 469.9 | 224.7 | 140.2 | 141.8 | 240.6 | 223.7 | 210.3
338 | 205 | 469.9 | 225.5 | 141.2 | 142.6 | 240.9 | 224.4 | 210.9
339 | 206 | 469.8 | 226.4 | 142.2 | 143.5 | 241.2 | 225.1 | 211.5
340 | 207 | 469.9 | 227.3 | 143.2 | 144.4 | 241.6 | 225.8 | 212.1
341 | 208 | 469.9 | 228.1 | 144.3 | 145.4 | 242 | 226.5 | 212.7
342 | 209 | 470 | 229 | 145.3 | 146.4 | 242.2 | 227.2 | 213.3
343 | 210 | 470.1 | 229.8 | 146.4 | 147.4 | 242.3 | 228 | 213.9
344 | 211 | 470.1 | 230.7 | 147.4 | 148.5 | 242.4 | 228.7 | 214.5
345 | 212 | 469.9 | 231.6 | 148.4 | 149.5 | 242.6 | 229.4 | 215.1
346 | 213 | 469.8 | 232.5 | 149.5 | 150.6 | 242.7 | 230.1 | 215.7
347 | 214 | 469.7 | 233.3 | 150.6 | 151.7 | 242.6 | 230.8 | 216.3
348 | 215 | 469.7 | 234.2 | 151.6 | 152.7 | 242.6 | 231.4 | 216.9
349 | 216 | 469.7 | 235 | 152.7 | 153.8 | 242.7 | 232.1 | 217.5
350 | 217 | 469.7 | 235.9 | 153.7 | 154.8 | 242.8 | 232.8 | 218.1
351 | 218 | 469.7 | 236.7 | 154.8 | 155.8 | 243 | 233.5 | 218.7
352 | 219 | 469.5 | 237.5 | 155.8 | 156.9 | 243.2 | 234.2 | 219.2
353 | 220 | 469.5 | 238.3 | 156.8 | 157.9 | 243.7 | 234.8 | 219.9
354 | 221 | 469.4 | 239.1 | 157.8 | 158.9 | 244.2 | 235.5 | 220.4
355 | 222 | 469.2 | 239.8 | 158.8 | 159.9 | 244.8 | 236.2 | 221
356 | 223 | 469.1 | 240.3 | 159.8 | 161 | 245.5 | 236.8 | 221.6
357 | 224 | 469.1 | 240.8 | 160.8 | 162 | 246.1 | 237.5 | 222.2
358 | 225 | 469.1 | 241.3 | 161.8 | 162.9 | 246.7 | 238.2 | 222.7
359 | 226 | 469.1 | 241.7 | 162.8 | 163.9 | 247.4 | 238.8 | 223.3
360 | 227 | 469.1 | 242.1 | 163.7 | 164.9 | 248.1 | 239.5 | 223.8
361 | 228 | 468.9 | 242.8 | 164.7 | 165.8 | 248.8 | 240.1 | 224.4
362 | 229 | 468.9 | 243.3 | 165.6 | 166.8 | 249.6 | 240.8 | 225
363 | 230 | 469 | 243.7 | 166.5 | 167.7 | 250.4 | 241.4 | 225.6
364 | 231 | 469 | 244.1 | 167.5 | 168.7 | 251.3 | 242.1 | 226.1
365 | 232 | 469 | 244.3 | 168.4 | 169.6 | 252 | 242.7 | 226.7
366 | 233 | 469 | 244.6 | 169.4 | 170.5 | 252.8 | 243.3 | 227.3
367 | 234 | 469 | 244.8 | 170.3 | 171.4 | 253.6 | 244 | 227.9
368 | 235 | 469 | 245.1 | 171.3 | 172.3 | 254.4 | 244.6 | 228.4
369 | 236 | 469 | 245.3 | 172.2 | 173.2 | 255.3 | 245.2 | 229
370 | 237 | 468.9 | 245.5 | 173.1 | 174 | 256.2 | 245.8 | 229.6
371 | 238 | 468.9 | 245.7 | 174.1 | 174.9 | 257.1 | 246.5 | 230.1
372 | 239 | 469 | 245.8 | 174.9 | 175.8 | 258 | 247.1 | 230.7
373 | 240 | 469.1 | 246 | 175.8 | 176.6 | 258.9 | 247.7 | 231.2
374 | 241 | 469.3 | 246.2 | 176.6 | 177.5 | 259.2 | 248.3 | 231.8
375 | 242 | 469.2 | 246.3 | 177.5 | 178.4 | 258.3 | 248.9 | 232.3
376 | 243 | 469.1 | 246.5 | 178.3 | 179.2 | 257.8 | 249.5 | 232.9
377 | 244 | 469.2 | 246.7 | 179.2 | 180 | 257.7 | 250.1 | 233.4
378 | 245 | 469.3 | 247 | 180 | 180.9 | 257.6 | 250.7 | 234
379 | 246 | 469.3 | 247.2 | 180.8 | 181.7 | 257.7 | 251.3 | 234.5
380 | 247 | 469.3 | 247.4 | 181.6 | 182.5 | 257.6 | 251.9 | 235.1
381 | 248 | 469.5 | 247.7 | 182.4 | 183.3 | 257.7 | 252.5 | 235.6
382 | 249 | 469.6 | 248 | 183.2 | 184.1 | 257.8 | 253.1 | 236.2
383 | 250 | 469.7 | 248.4 | 184 | 184.9 | 257.9 | 253.7 | 236.7
384 | 251 | 469.6 | 249 | 184.8 | 185.7 | 258 | 254.3 | 237.2
385 | 252 | 469.6 | 249.7 | 185.5 | 186.5 | 258.2 | 254.9 | 237.8
386 | 253 | 469.6 | 250.3 | 186.3 | 187.3 | 258.3 | 255.4 | 238.4
387 | 254 | 469.6 | 250.9 | 187.1 | 188.1 | 258.4 | 256 | 238.9
388 | 255 | 469.7 | 251.6 | 187.9 | 188.9 | 258.8 | 256.6 | 239.5
389 | 256 | 469.8 | 252.3 | 188.7 | 189.6 | 259.1 | 257.2 | 240.1
390 | 257 | 469.8 | 253 | 189.5 | 190.4 | 259.7 | 257.8 | 240.6
391 | 258 | 469.9 | 253.6 | 190.2 | 191.2 | 260.2 | 258.4 | 241.2
392 | 259 | 469.9 | 254.1 | 191 | 191.9 | 260.4 | 259 | 241.7
393 | 260 | 469.9 | 255.1 | 191.7 | 192.7 | 260.6 | 259.5 | 242.2
394 | 261 | 469.9 | 256.4 | 192.4 | 193.4 | 260.8 | 260.1 | 242.8
395 | 262 | 469.9 | 257.5 | 193.1 | 194.2 | 261.1 | 260.7 | 243.3
396 | 263 | 469.9 | 258.3 | 193.8 | 194.9 | 261.3 | 261.3 | 243.8
397 | 264 | 469.8 | 259.2 | 194.5 | 195.7 | 261.4 | 261.9 | 244.4
398 | 265 | 469.7 | 260 | 195.1 | 196.5 | 261.6 | 262.4 | 244.9
399 | 266 | 469.7 | 260.6 | 195.8 | 197.2 | 261.7 | 263 | 245.4
400 | 267 | 469.7 | 261.2 | 196.5 | 198 | 262 | 263.6 | 245.9
401 | 268 | 469.6 | 261.7 | 197.1 | 198.7 | 262.1 | 264.2 | 246.4
402 | 269 | 469.7 | 262.2 | 197.8 | 199.4 | 262 | 264.8 | 247
403 | 270 | 469.7 | 262.5 | 198.5 | 200.2 | 262 | 265.3 | 247.4
404 | 271 | 469.7 | 262.8 | 199.2 | 200.9 | 262 | 265.9 | 247.9
405 | 272 | 469.8 | 262.4 | 199.9 | 201.6 | 262 | 266.4 | 248.4
406 | 273 | 469.9 | 260.3 | 200.6 | 202.2 | 262 | 267 | 249
407 | 274 | 469.9 | 256.6 | 201.2 | 202.9 | 262 | 267.6 | 249.5
408 | 275 | 469.8 | 254.6 | 201.9 | 203.5 | 262.1 | 268.2 | 250
409 | 276 | 469.9 | 253.4 | 202.6 | 204.2 | 262.2 | 268.7 | 250.5
410 | 277 | 469.9 | 252.9 | 203.3 | 204.8 | 262.4 | 269.3 | 251.1
411 | 278 | 469.9 | 252.7 | 203.9 | 205.5 | 262.5 | 269.9 | 251.5
412 | 279 | 469.9 | 252.6 | 204.5 | 206.2 | 262.6 | 270.4 | 252
413 | 280 | 469.9 | 252.6 | 205.1 | 206.8 | 262.9 | 271 | 252.5
414 | 281 | 469.9 | 252.6 | 205.7 | 207.4 | 263 | 271.5 | 253
415 | 282 | 469.8 | 252.5 | 206.3 | 208.1 | 263.2 | 272.1 | 253.5
416 | 283 | 469.8 | 252.3 | 206.9 | 208.7 | 263.4 | 272.6 | 253.9
417 | 284 | 469.7 | 252.2 | 207.5 | 209.4 | 263.6 | 273.2 | 254.4
418 | 285 | 469.6 | 252.2 | 208.1 | 210 | 263.9 | 273.7 | 254.9
419 | 286 | 469.5 | 252.4 | 208.7 | 210.6 | 264.1 | 274.3 | 255.4
420 | 287 | 469.4 | 252.6 | 209.3 | 211.2 | 264.4 | 274.8 | 255.8
421 | 288 | 469.3 | 253 | 209.9 | 211.8 | 264.7 | 275.4 | 256.3
422 | 289 | 469.4 | 253.2 | 210.4 | 212.4 | 265.2 | 275.9 | 256.8
423 | 290 | 469.4 | 253.5 | 211 | 213 | 265.9 | 276.5 | 257.3
424 | 291 | 469.4 | 253.9 | 211.6 | 213.6 | 266.5 | 277 | 257.7
425 | 292 | 469.4 | 254.3 | 212.1 | 214.2 | 267.1 | 277.5 | 258.2
426 | 293 | 469.3 | 254.7 | 212.6 | 214.8 | 267.7 | 278.1 | 258.7
427 | 294 | 469.2 | 255 | 213.2 | 215.4 | 268.3 | 278.6 | 259.1
428 | 295 | 469.2 | 255.4 | 213.7 | 216 | 269 | 279.1 | 259.6
429 | 296 | 469.1 | 255.8 | 214.2 | 216.6 | 269.7 | 279.6 | 260.1
430 | 297 | 469 | 256.2 | 214.7 | 217.2 | 270.4 | 280.2 | 260.6
431 | 298 | 469 | 256.6 | 215.3 | 217.7 | 270.9 | 280.7 | 261
432 | 299 | 469 | 256.9 | 215.9 | 218.3 | 271.3 | 281.2 | 261.5
433 | 300 | 469.1 | 257.3 | 216.4 | 218.8 | 271.9 | 281.7 | 262
434 | 301 | 469.2 | 257.8 | 217 | 219.4 | 272.5 | 282.3 | 262.4
435 | 302 | 469.3 | 258.2 | 217.6 | 220 | 273.2 | 282.8 | 262.9
436 | 303 | 469.3 | 258.6 | 218.1 | 220.5 | 274 | 283.4 | 263.3
437 | 304 | 469.3 | 259.1 | 218.6 | 221.1 | 274.9 | 284 | 263.9
438 | 305 | 469.4 | 259.4 | 219.2 | 221.7 | 275.7 | 284.5 | 264.3
439 | 306 | 469.5 | 259.7 | 219.7 | 222.2 | 276.3 | 285.1 | 264.8
440 | 307 | 469.6 | 260.1 | 220.2 | 222.8 | 276.9 | 285.6 | 265.3
441 | 308 | 469.7 | 260.4 | 220.7 | 223.3 | 277.6 | 286.1 | 265.8
442 | 309 | 469.8 | 260.7 | 221.2 | 223.9 | 278.2 | 286.7 | 266.3
443 | 310 | 470 | 260.9 | 221.7 | 224.4 | 278.9 | 287.2 | 266.7
444 | 311 | 470.1 | 261.2 | 222.3 | 225 | 279.6 | 287.7 | 267.2
445 | 312 | 470.1 | 261.4 | 222.8 | 225.5 | 280.3 | 288.3 | 267.7
446 | 313 | 470.1 | 261.6 | 223.4 | 226.1 | 281.1 | 288.8 | 268.2
447 | 314 | 470 | 261.8 | 223.9 | 226.6 | 281.8 | 289.4 | 268.7
448 | 315 | 470.1 | 262 | 224.5 | 227.1 | 282.4 | 289.9 | 269.2
449 | 316 | 470.3 | 262.2 | 225 | 227.7 | 283.2 | 290.5 | 269.6
450 | 317 | 470.5 | 262.3 | 225.5 | 228.2 | 283.9 | 291 | 270.1
451 | 318 | 470.6 | 262.3 | 226 | 228.8 | 284.6 | 291.6 | 270.5
452 | 319 | 470.5 | 262.4 | 226.5 | 229.3 | 285.3 | 292.1 | 271
453 | 320 | 470.5 | 262.5 | 227 | 229.9 | 285.9 | 292.7 | 271.4
454 | 321 | 470.6 | 262.7 | 227.4 | 230.4 | 286.5 | 293.2 | 271.9
455 | 322 | 470.6 | 262.9 | 227.9 | 231 | 287.1 | 293.7 | 272.3
456 | 323 | 470.6 | 263.1 | 228.4 | 231.5 | 287.6 | 294.2 | 272.8
457 | 324 | 470.6 | 263.4 | 228.9 | 232.1 | 288.1 | 294.8 | 273.2
458 | 325 | 470.7 | 263.7 | 229.4 | 232.6 | 288.7 | 295.3 | 273.7
459 | 326 | 470.7 | 264 | 229.9 | 233.1 | 289.1 | 295.8 | 274.1
460 | 327 | 470.8 | 264.2 | 230.5 | 233.7 | 289.6 | 296.4 | 274.5
461 | 328 | 470.9 | 264.5 | 231 | 234.2 | 290 | 296.9 | 275
462 | 329 | 471 | 264.6 | 231.5 | 234.7 | 290.4 | 297.4 | 275.4
463 | 330 | 471 | 264.9 | 232 | 235.2 | 290.9 | 298 | 275.8
464 | 331 | 471 | 265.1 | 232.5 | 235.7 | 291.3 | 298.5 | 276.2
465 | 332 | 471.1 | 265.4 | 233.1 | 236.2 | 291.7 | 299 | 276.7
466 | 333 | 471.1 | 265.7 | 233.6 | 236.7 | 292.1 | 299.6 | 277.1
467 | 334 | 471 | 266 | 234 | 237.2 | 292.6 | 300.1 | 277.5
468 | 335 | 470.9 | 266.3 | 234.5 | 237.7 | 293 | 300.6 | 277.9
469 | 336 | 470.8 | 266.6 | 234.9 | 238.2 | 293.4 | 301.1 | 278.3
470 | 337 | 470.8 | 266.9 | 235.4 | 238.7 | 293.8 | 301.6 | 278.6
471 | 338 | 470.7 | 267.3 | 235.9 | 239.2 | 294.3 | 302.1 | 279
472 | 339 | 470.5 | 267.6 | 236.3 | 239.7 | 294.8 | 302.6 | 279.4
473 | 340 | 470.2 | 268 | 236.8 | 240.2 | 295.2 | 303.1 | 279.8
474 | 341 | 470 | 268.4 | 237.2 | 240.7 | 295.7 | 303.5 | 280.1
475 | 342 | 469.9 | 268.8 | 237.6 | 241.2 | 296.2 | 303.9 | 280.5
476 | 343 | 469.7 | 269.5 | 238 | 241.7 | 296.7 | 304.4 | 280.8
477 | 344 | 469.6 | 270.2 | 238.4 | 242.2 | 297.2 | 304.9 | 281.1
478 | 345 | 469.6 | 270.7 | 238.8 | 242.7 | 297.7 | 305.4 | 281.5
479 | 346 | 469.7 | 271.2 | 239.3 | 243.2 | 298 | 305.8 | 281.8
480 | 347 | 469.8 | 271.7 | 239.8 | 243.7 | 298.3 | 306.3 | 282.2
481 | 348 | 469.8 | 272.2 | 240.2 | 244.1 | 298.7 | 306.7 | 282.5
482 | 349 | 469.8 | 272.7 | 240.7 | 244.6 | 299 | 307.2 | 282.9
483 | 350 | 470.1 | 273.2 | 241.2 | 245.1 | 299.4 | 307.7 | 283.3
484 | 351 | 470.3 | 273.6 | 241.7 | 245.5 | 299.8 | 308.1 | 283.6
485 | 352 | 470.3 | 274 | 242.1 | 246 | 300.2 | 308.6 | 283.9
486 | 353 | 470.3 | 274.5 | 242.6 | 246.5 | 300.7 | 309 | 284.3
487 | 354 | 470.3 | 274.8 | 243.1 | 246.9 | 301.1 | 309.5 | 284.7
488 | 355 | 470.1 | 275.2 | 243.6 | 247.4 | 301.5 | 309.9 | 285
489 | 356 | 470.2 | 275.6 | 244 | 247.9 | 302 | 310.4 | 285.4
490 | 357 | 470.3 | 276 | 244.4 | 248.3 | 302.5 | 310.8 | 285.7
491 | 358 | 470.2 | 276.4 | 244.9 | 248.8 | 302.9 | 311.3 | 286
492 | 359 | 470 | 276.7 | 245.3 | 249.3 | 303.3 | 311.8 | 286.3
493 | 360 | 470 | 277.1 | 245.8 | 249.7 | 303.7 | 312.2 | 286.6
494 | 361 | 470.1 | 277.4 | 246.2 | 250.2 | 303.8 | 312.6 | 286.9
495 | 362 | 470 | 277.7 | 246.7 | 250.6 | 303.9 | 313 | 287.2
496 | 363 | 469.9 | 278.1 | 247.1 | 251.1 | 304.1 | 313.5 | 287.5
497 | 364 | 469.9 | 278.3 | 247.6 | 251.5 | 304.4 | 313.9 | 287.8
498 | 365 | 470 | 278.6 | 248 | 251.9 | 304.8 | 314.4 | 288.1
499 | 366 | 469.9 | 278.9 | 248.5 | 252.4 | 305.1 | 314.8 | 288.4
500 | 367 | 469.9 | 279.2 | 248.9 | 252.8 | 305.4 | 315.2 | 288.7
501 | 368 | 469.8 | 279.5 | 249.4 | 253.2 | 305.8 | 315.6 | 289
502 | 369 | 469.8 | 279.8 | 249.8 | 253.7 | 306.1 | 316 | 289.3
503 | 370 | 469.7 | 280.1 | 250.2 | 254.1 | 306.5 | 316.4 | 289.5
504 | 371 | 469.4 | 280.4 | 250.7 | 254.6 | 306.8 | 316.9 | 289.8
505 | 372 | 469.2 | 280.7 | 251.1 | 255 | 307.1 | 317.3 | 290
506 | 373 | 469.2 | 281.1 | 251.5 | 255.4 | 307.4 | 317.7 | 290.3
507 | 374 | 469.2 | 281.4 | 251.9 | 255.9 | 307.8 | 318.2 | 290.6
508 | 375 | 469.3 | 281.8 | 252.3 | 256.3 | 308.1 | 318.5 | 290.8
509 | 376 | 469.3 | 282.1 | 252.8 | 256.7 | 308.5 | 318.9 | 291
510 | 377 | 469.5 | 282.5 | 253.2 | 257.1 | 308.8 | 319.3 | 291.3
511 | 378 | 469.5 | 282.9 | 253.6 | 257.6 | 309.2 | 319.7 | 291.6
512 | 379 | 469.6 | 283.2 | 254.1 | 257.9 | 309.4 | 320.1 | 291.8
513 | 380 | 469.5 | 283.2 | 255.3 | 258.1 | 308.7 | 320.5 | 292.1
514 | 381 | 469.3 | 283.6 | 255.7 | 258.6 | 309.1 | 320.9 | 292.4
515 | 382 | 469.2 | 283.9 | 256.1 | 259 | 309.5 | 321.3 | 292.7
516 | 383 | 469.3 | 284.4 | 256.5 | 259.4 | 309.8 | 321.7 | 292.9
517 | 384 | 469.4 | 284.8 | 256.9 | 259.8 | 310.2 | 322.2 | 293.2
518 | 385 | 469.3 | 285.2 | 257.4 | 260.2 | 310.5 | 322.7 | 293.4
519 | 386 | 469.2 | 285.6 | 257.8 | 260.7 | 310.9 | 323 | 293.6
520 | 387 | 469.2 | 286.1 | 258.2 | 261.1 | 311.3 | 323.4 | 293.9
521 | 388 | 469.2 | 286.5 | 258.6 | 261.5 | 311.7 | 323.7 | 294.1
522 | 389 | 469.1 | 287 | 259 | 261.9 | 312 | 324.1 | 294.3
523 | 390 | 469 | 287.4 | 259.4 | 262.3 | 312.4 | 324.4 | 294.6
524 | 391 | 469 | 287.9 | 259.8 | 262.7 | 312.8 | 324.7 | 294.8
525 | 392 | 469.1 | 288.4 | 260.2 | 263.2 | 313.1 | 325.2 | 295.1
526 | 393 | 468.9 | 289 | 260.6 | 263.6 | 313.4 | 325.8 | 295.3
527 | 394 | 468.8 | 289.6 | 261.1 | 264 | 313.7 | 326.2 | 295.6
528 | 395 | 468.8 | 290.1 | 261.5 | 264.4 | 314 | 326.7 | 295.8
529 | 396 | 468.7 | 290.5 | 262 | 264.8 | 314.2 | 327.1 | 296
530 | 397 | 468.7 | 290.9 | 262.4 | 265.2 | 314.5 | 327.6 | 296.3
531 | 398 | 468.9 | 291.4 | 262.8 | 265.6 | 314.8 | 328.2 | 296.5
532 | 399 | 469 | 291.9 | 263.2 | 266 | 315.1 | 328.6 | 296.7
533 | 400 | 469.2 | 292.4 | 263.6 | 266.4 | 315.5 | 329.3 | 296.9
534 | 401 | 469.1 | 293 | 264 | 266.8 | 315.8 | 329.7 | 297.1
535 | 402 | 469.1 | 293.6 | 264.4 | 267.2 | 316.1 | 330.1 | 297.3
536 | 403 | 469.2 | 294.1 | 264.8 | 267.6 | 316.4 | 330.7 | 297.5
537 | 404 | 469.3 | 294.5 | 265.2 | 268 | 316.7 | 331.3 | 297.8
538 | 405 | 469.3 | 294.9 | 265.6 | 268.4 | 317 | 331.9 | 298
539 | 406 | 469.2 | 295.4 | 266 | 268.9 | 317.4 | 332.4 | 298.3
540 | 407 | 469.1 | 296.3 | 266.4 | 269.3 | 317.7 | 332.9 | 298.5
541 | 408 | 468.9 | 296.8 | 266.8 | 269.7 | 318 | 333.4 | 298.8
542 | 409 | 468.9 | 297.3 | 267.2 | 270.1 | 318.3 | 333.8 | 299
543 | 410 | 468.9 | 297.7 | 267.6 | 270.5 | 318.7 | 334.2 | 299.2
544 | 411 | 468.9 | 298.2 | 268 | 270.9 | 318.9 | 334.8 | 299.5
545 | 412 | 469.1 | 298.7 | 268.4 | 271.3 | 319.3 | 335.4 | 299.7
546 | 413 | 469.4 | 299.3 | 268.8 | 271.7 | 319.5 | 335.8 | 300
547 | 414 | 469.6 | 300.1 | 269.2 | 272.1 | 319.8 | 336.2 | 300.2
548 | 415 | 469.7 | 300.5 | 269.7 | 272.5 | 320 | 336.8 | 300.5
549 | 416 | 469.8 | 300.8 | 270.1 | 272.9 | 320.3 | 337.5 | 300.8
550 | 417 | 469.8 | 301.2 | 270.5 | 273.3 | 320.6 | 338.1 | 301
551 | 418 | 469.9 | 301.6 | 270.9 | 273.7 | 320.8 | 338.7 | 301.3
552 | 419 | 469.9 | 302 | 271.3 | 274.1 | 321.1 | 339.2 | 301.6
553 | 420 | 469.8 | 302.3 | 271.7 | 274.6 | 321.5 | 339.8 | 301.8
554 | 421 | 469.8 | 302.9 | 272.1 | 275 | 321.8 | 340.4 | 302.1
555 | 422 | 469.8 | 303.6 | 272.5 | 275.4 | 322.1 | 341 | 302.3
556 | 423 | 469.9 | 304.3 | 272.9 | 275.8 | 322.4 | 341.6 | 302.6
557 | 424 | 470 | 304.9 | 273.4 | 276.2 | 322.7 | 342.2 | 302.8
558 | 425 | 470 | 305.3 | 273.8 | 276.7 | 323 | 342.7 | 303.1
559 | 426 | 470.2 | 305.7 | 274.2 | 277.1 | 323.3 | 343.2 | 303.3
560 | 427 | 470.2 | 305.9 | 274.7 | 277.5 | 323.6 | 343.9 | 303.6
561 | 428 | 470.1 | 306.2 | 275.1 | 277.9 | 324 | 344.6 | 303.8
562 | 429 | 470.1 | 306.5 | 275.5 | 278.3 | 324.3 | 345.3 | 304
563 | 430 | 470.2 | 307.1 | 276 | 278.7 | 324.7 | 345.9 | 304.3
564 | 431 | 470.1 | 307.7 | 276.4 | 279.2 | 325.2 | 346.6 | 304.5
565 | 432 | 470 | 308.2 | 276.8 | 279.6 | 325.8 | 347.3 | 304.8
566 | 433 | 470.1 | 308.6 | 277.2 | 280 | 326.2 | 347.9 | 305.1
567 | 434 | 469.9 | 309 | 277.7 | 280.4 | 326.6 | 348.5 | 305.3
568 | 435 | 469.7 | 309.4 | 278.1 | 280.9 | 327.1 | 349.2 | 305.6
569 | 436 | 469.6 | 309.9 | 278.6 | 281.3 | 327.5 | 349.9 | 305.9
570 | 437 | 469.5 | 310.4 | 279 | 281.7 | 327.8 | 350.6 | 306.1
571 | 438 | 469.5 | 310.9 | 279.5 | 282.2 | 328.1 | 351.3 | 306.4
572 | 439 | 469.5 | 311.3 | 279.9 | 282.6 | 328.4 | 351.9 | 306.7
573 | 440 | 469.5 | 311.6 | 280.3 | 283 | 328.7 | 352.6 | 306.9
574 | 441 | 469.5 | 311.9 | 280.8 | 283.4 | 329.1 | 353.2 | 307.2
575 | 442 | 469.4 | 312.1 | 281.2 | 283.9 | 329.5 | 353.7 | 307.4
576 | 443 | 469.5 | 312.6 | 281.7 | 284.3 | 329.9 | 354.2 | 307.7
577 | 444 | 469.6 | 313 | 282.1 | 284.8 | 330.3 | 354.7 | 308
578 | 445 | 469.5 | 313.5 | 282.5 | 285.2 | 330.7 | 355.1 | 308.3
579 | 446 | 469.3 | 313.8 | 283 | 285.6 | 331 | 355.6 | 308.5
580 | 447 | 469.3 | 314.3 | 283.4 | 286.1 | 331.4 | 356.1 | 308.7
581 | 448 | 469.4 | 314.7 | 283.9 | 286.5 | 331.7 | 356.6 | 308.9
582 | 449 | 469.3 | 314.9 | 284.3 | 286.9 | 331.9 | 356.8 | 309.1
583 | 450 | 469.1 | 315.3 | 284.7 | 287.4 | 332.1 | 357.1 | 309.4
584 | 451 | 469 | 315.9 | 285.1 | 287.8 | 332.4 | 357.4 | 309.7
585 | 452 | 468.9 | 316.4 | 285.6 | 288.2 | 332.8 | 357.9 | 310
586 | 453 | 468.9 | 316.9 | 286.1 | 288.7 | 333.1 | 358.2 | 310.4
587 | 454 | 468.9 | 317.5 | 286.5 | 289.1 | 333.3 | 358.6 | 310.7
588 | 455 | 468.8 | 317.8 | 287 | 289.6 | 333.6 | 359 | 311
589 | 456 | 468.8 | 318.2 | 287.4 | 290 | 333.9 | 359.5 | 311.2
590 | 457 | 468.9 | 318.7 | 287.8 | 290.4 | 334.2 | 360 | 311.5
591 | 458 | 468.9 | 319 | 288 | 290.9 | 334.8 | 360.3 | 311.8
592 | 459 | 469.1 | 319.6 | 288 | 291.5 | 335.8 | 360.7 | 312
593 | 460 | 469.2 | 320.3 | 288.4 | 292 | 336.1 | 361.2 | 312.3
594 | 461 | 469.1 | 320.7 | 288.8 | 292.4 | 336.5 | 361.5 | 312.6
595 | 462 | 469.2 | 320.9 | 289.3 | 292.8 | 336.7 | 361.8 | 312.8
596 | 463 | 469.5 | 321.5 | 289.7 | 293.2 | 336.9 | 362.3 | 313.1
597 | 464 | 469.6 | 322 | 290.2 | 293.7 | 337.2 | 362.6 | 313.4
598 | 465 | 469.7 | 322.4 | 290.6 | 294.1 | 337.4 | 362.9 | 313.6
599 | 466 | 469.9 | 322.9 | 291 | 294.5 | 337.6 | 363.2 | 313.9
600 | 467 | 470 | 323.2 | 291.5 | 294.9 | 337.8 | 363.6 | 314.1
601 | 468 | 470.1 | 323.5 | 292 | 295.3 | 338.2 | 363.9 | 314.4
602 | 469 | 470.2 | 323.9 | 292.5 | 295.7 | 338.5 | 364.4 | 314.7
603 | 470 | 470.2 | 324.5 | 292.9 | 296.2 | 338.7 | 364.8 | 315
604 | 471 | 470.3 | 324.9 | 293.3 | 296.6 | 339 | 365.3 | 315.3
605 | 472 | 470.4 | 325.4 | 293.8 | 297 | 339.2 | 365.7 | 315.6
606 | 473 | 470.5 | 325.8 | 294.2 | 297.4 | 339.4 | 366.1 | 315.9
607 | 474 | 470.6 | 326.2 | 294.7 | 297.9 | 339.7 | 366.5 | 316.2
608 | 475 | 470.6 | 326.7 | 295.1 | 298.3 | 340 | 366.9 | 316.5
609 | 476 | 470.5 | 327.1 | 295.6 | 298.7 | 340.2 | 367.3 | 316.7
610 | 477 | 470.7 | 327.5 | 296.1 | 299.1 | 340.4 | 367.6 | 317
611 | 478 | 470.6 | 327.7 | 296.5 | 299.5 | 340.7 | 368.1 | 317.3
612 | 479 | 470.6 | 328.2 | 296.9 | 299.9 | 341 | 368.5 | 317.5
613 | 480 | 470.6 | 328.8 | 297.3 | 300.4 | 341.2 | 369 | 317.9
614 | 481 | 470.6 | 329.3 | 297.8 | 300.8 | 341.6 | 369.4 | 318.1
615 | 482 | 470.5 | 329.7 | 298.2 | 301.2 | 341.9 | 369.7 | 318.4
616 | 483 | 470.5 | 330.2 | 298.6 | 301.6 | 342.1 | 370.1 | 318.7
617 | 484 | 470.5 | 330.8 | 299 | 302 | 342.4 | 370.4 | 319
618 | 485 | 470.4 | 331.2 | 299.4 | 302.4 | 342.7 | 370.7 | 319.4
619 | 486 | 470.2 | 331.6 | 299.9 | 302.9 | 343.1 | 371 | 319.6
620 | 487 | 470.1 | 332 | 300.3 | 303.3 | 343.4 | 371.3 | 319.9
621 | 488 | 470.1 | 332.5 | 300.8 | 303.7 | 343.6 | 371.7 | 320.2
622 | 489 | 470.2 | 333 | 301.2 | 304.1 | 343.9 | 372 | 320.5
623 | 490 | 470.2 | 333.5 | 301.6 | 304.5 | 344.3 | 372.3 | 320.8
624 | 491 | 470.2 | 333.8 | 302.1 | 304.9 | 344.5 | 372.5 | 321.1
625 | 492 | 470.2 | 334.2 | 302.5 | 305.3 | 344.8 | 372.8 | 321.4
626 | 493 | 470.2 | 334.6 | 302.9 | 305.7 | 345.1 | 373 | 321.7
627 | 494 | 470.3 | 335.2 | 303.3 | 306.1 | 345.4 | 373.2 | 321.9
628 | 495 | 470.3 | 335.6 | 303.8 | 306.5 | 345.7 | 373.4 | 322.2
629 | 496 | 470.2 | 336.1 | 304.2 | 307 | 346.1 | 373.7 | 322.5
630 | 497 | 470.2 | 336.6 | 304.6 | 307.4 | 346.5 | 374 | 322.8
631 | 498 | 470.2 | 337 | 305 | 307.8 | 346.9 | 374.3 | 323.1
632 | 499 | 470.3 | 337.3 | 305.4 | 308.2 | 347.1 | 374.6 | 323.3
633 | 500 | 470.3 | 337.8 | 305.8 | 308.6 | 347.4 | 374.9 | 323.5
634 | 501 | 470.4 | 338.1 | 306.3 | 309 | 347.7 | 375.3 | 323.8
635 | 502 | 470.3 | 338.5 | 306.7 | 309.4 | 348 | 375.5 | 324.1
636 | 503 | 470.2 | 339 | 307.1 | 309.8 | 348.2 | 375.8 | 324.4
637 | 504 | 470.2 | 339.5 | 307.6 | 310.2 | 348.5 | 376.1 | 324.6
638 | 505 | 470.3 | 339.8 | 308 | 310.6 | 348.7 | 376.3 | 324.8
639 | 506 | 470.2 | 340.2 | 308.5 | 311 | 349 | 376.6 | 325.1
640 | 507 | 470.2 | 340.6 | 308.9 | 311.4 | 349.2 | 376.8 | 325.4
641 | 508 | 470.3 | 341 | 309.3 | 311.8 | 349.5 | 377 | 325.6
642 | 509 | 470.3 | 341.4 | 309.7 | 312.3 | 349.8 | 377.1 | 326
643 | 510 | 470.4 | 341.8 | 310.1 | 312.7 | 350.2 | 377.4 | 326.2
644 | 511 | 470.5 | 342.1 | 310.5 | 313.1 | 350.5 | 377.7 | 326.6
645 | 512 | 470.6 | 342.4 | 311 | 313.5 | 350.8 | 377.9 | 326.9
646 | 513 | 470.7 | 342.8 | 311.4 | 313.9 | 351 | 378.2 | 327.1
647 | 514 | 470.6 | 343.2 | 311.8 | 314.3 | 351.3 | 378.4 | 327.4
648 | 515 | 470.6 | 343.6 | 312.2 | 314.7 | 351.6 | 378.7 | 327.7
649 | 516 | 470.4 | 343.9 | 312.6 | 315.1 | 351.9 | 378.9 | 328
650 | 517 | 470.5 | 344.4 | 313 | 315.5 | 352.2 | 379.2 | 328.2
651 | 518 | 470.6 | 344.8 | 313.4 | 315.9 | 352.5 | 379.5 | 328.5
652 | 519 | 470.6 | 345.2 | 313.8 | 316.3 | 352.8 | 379.7 | 328.8
653 | 520 | 470.6 | 345.5 | 314.3 | 316.7 | 353.1 | 379.9 | 329
654 | 521 | 470.9 | 345.9 | 314.7 | 317.1 | 353.3 | 380.2 | 329.3
655 | 522 | 471.1 | 346.2 | 315.1 | 317.5 | 353.5 | 380.4 | 329.6
656 | 523 | 471.1 | 346.5 | 315.6 | 317.9 | 353.7 | 380.6 | 329.8
657 | 524 | 471.1 | 346.8 | 316.1 | 318.3 | 354 | 380.8 | 330.1
658 | 525 | 471 | 347.2 | 316.5 | 318.7 | 354.3 | 381 | 330.3
659 | 526 | 471 | 347.5 | 316.9 | 319.1 | 354.5 | 381.1 | 330.5
660 | 527 | 471 | 347.8 | 317.2 | 319.5 | 354.8 | 381.2 | 330.7
661 | 528 | 471 | 348.1 | 317.6 | 319.9 | 355 | 381.3 | 331
662 | 529 | 471 | 348.5 | 318 | 320.3 | 355.3 | 381.4 | 331.2
663 | 530 | 471 | 348.9 | 318.4 | 320.7 | 355.6 | 381.6 | 331.4
664 | 531 | 470.9 | 349.2 | 318.9 | 321.1 | 355.8 | 381.7 | 331.7
665 | 532 | 470.8 | 349.5 | 319.3 | 321.5 | 356.1 | 381.8 | 331.9
666 | 533 | 470.8 | 349.8 | 319.7 | 321.9 | 356.2 | 381.8 | 332.1
667 | 534 | 470.7 | 350.2 | 320.1 | 322.3 | 356.5 | 381.9 | 332.3
668 | 535 | 470.7 | 350.4 | 320.6 | 322.7 | 356.8 | 381.9 | 332.5
669 | 536 | 470.7 | 350.8 | 321 | 323.1 | 357 | 382 | 332.7
670 | 537 | 470.8 | 351.1 | 321.4 | 323.4 | 357.3 | 382.1 | 332.9
671 | 538 | 470.7 | 351.4 | 321.8 | 323.8 | 357.5 | 382.3 | 333.1
672 | 539 | 470.4 | 351.7 | 322.2 | 324.2 | 357.7 | 382.4 | 333.3
673 | 540 | 470.2 | 352 | 322.6 | 324.6 | 358 | 382.5 | 333.5
674 | 541 | 470.2 | 352.3 | 323 | 325 | 358.3 | 382.5 | 333.8
675 | 542 | 470.2 | 352.6 | 323.4 | 325.4 | 358.5 | 382.6 | 334
676 | 543 | 470.2 | 352.9 | 323.8 | 325.8 | 358.7 | 382.8 | 334.1
677 | 544 | 470.2 | 353.1 | 324.2 | 326.2 | 358.9 | 382.9 | 334.3
678 | 545 | 470.1 | 353.4 | 324.6 | 326.5 | 359.2 | 383 | 334.6
679 | 546 | 469.9 | 353.7 | 325 | 326.9 | 359.4 | 383.1 | 334.8
680 | 547 | 469.8 | 354 | 325.4 | 327.3 | 359.7 | 383.1 | 335
681 | 548 | 469.7 | 354.3 | 325.7 | 327.7 | 359.9 | 383.1 | 335.1
682 | 549 | 469.7 | 354.6 | 326.1 | 328.1 | 360.1 | 383.1 | 335.3
683 | 550 | 469.7 | 354.9 | 326.5 | 328.5 | 360.4 | 383.2 | 335.5
684 | 551 | 469.6 | 355.2 | 326.9 | 328.8 | 360.6 | 383.3 | 335.6
685 | 552 | 469.5 | 355.5 | 327.3 | 329.2 | 360.8 | 383.4 | 335.8
686 | 553 | 469.5 | 355.8 | 327.6 | 329.6 | 361 | 383.3 | 335.9
687 | 554 | 469.4 | 356.1 | 328 | 330 | 361.3 | 383.3 | 336.1
688 | 555 | 469.4 | 356.3 | 328.4 | 330.3 | 361.5 | 383.4 | 336.3
689 | 556 | 469.5 | 356.7 | 328.8 | 330.7 | 361.6 | 383.4 | 336.5
690 | 557 | 469.4 | 357 | 329.1 | 331.1 | 361.9 | 383.4 | 336.7
691 | 558 | 469.4 | 357.3 | 329.5 | 331.5 | 362.1 | 383.4 | 336.8
692 | 559 | 469.3 | 357.7 | 329.9 | 331.8 | 362.3 | 383.5 | 337.1
693 | 560 | 469.2 | 358 | 330.3 | 332.2 | 362.5 | 383.4 | 337.3
694 | 561 | 469.2 | 358.3 | 330.6 | 332.6 | 362.7 | 383.4 | 337.5
695 | 562 | 469.2 | 358.6 | 331 | 332.9 | 362.9 | 383.4 | 337.7
696 | 563 | 469.2 | 358.8 | 331.4 | 333.3 | 363.1 | 383.4 | 338
697 | 564 | 469.1 | 359.1 | 331.8 | 333.7 | 363.3 | 383.5 | 338.2
698 | 565 | 469.2 | 359.4 | 332.1 | 334 | 363.5 | 383.5 | 338.4
699 | 566 | 469.2 | 359.7 | 332.5 | 334.4 | 363.7 | 383.6 | 338.6
700 | 567 | 469.1 | 359.9 | 332.9 | 334.7 | 364 | 383.6 | 338.7
701 | 568 | 469.1 | 360.2 | 333.3 | 335.1 | 364.1 | 383.6 | 338.9
702 | 569 | 469.1 | 360.5 | 333.6 | 335.4 | 364.3 | 383.6 | 339.1
703 | 570 | 469.1 | 360.7 | 334 | 335.8 | 364.5 | 383.6 | 339.2
704 | 571 | 469.2 | 361 | 334.3 | 336.1 | 364.8 | 383.6 | 339.4
705 | 572 | 469.2 | 361.2 | 334.6 | 336.5 | 365.1 | 383.6 | 339.6
706 | 573 | 469.1 | 361.5 | 335 | 336.9 | 365.3 | 383.6 | 339.8
707 | 574 | 469.1 | 361.8 | 335.4 | 337.2 | 365.5 | 383.6 | 340
708 | 575 | 469.1 | 362 | 335.7 | 337.6 | 365.7 | 383.6 | 340.1
709 | 576 | 469.1 | 362.3 | 336.1 | 337.9 | 365.9 | 383.6 | 340.3
710 | 577 | 469.2 | 362.4 | 336.5 | 338.3 | 366.1 | 383.7 | 340.4
711 | 578 | 469.3 | 362.7 | 336.8 | 338.6 | 366.3 | 383.7 | 340.6
712 | 579 | 469.5 | 363 | 337.2 | 339 | 366.5 | 383.7 | 340.7
713 | 580 | 469.7 | 363.2 | 337.6 | 339.3 | 366.6 | 383.7 | 340.8
714 | 581 | 469.6 | 363.5 | 337.9 | 339.6 | 366.8 | 383.7 | 341
715 | 582 | 469.6 | 363.8 | 338.2 | 340 | 367.1 | 383.7 | 341.2
716 | 583 | 469.7 | 364.2 | 338.6 | 340.3 | 367.3 | 383.8 | 341.3
717 | 584 | 470 | 364.5 | 338.9 | 340.7 | 367.5 | 383.8 | 341.4
718 | 585 | 470 | 364.8 | 339.3 | 341 | 367.8 | 383.8 | 341.6
719 | 586 | 469.9 | 365 | 339.6 | 341.4 | 368 | 383.8 | 341.8
720 | 587 | 470 | 365.3 | 340 | 341.7 | 368.2 | 383.9 | 342.1
721 | 588 | 470 | 365.4 | 340.4 | 342.1 | 368.4 | 383.9 | 342.3
722 | 589 | 470.1 | 365.6 | 340.7 | 342.4 | 368.5 | 384 | 342.5
723 | 590 | 470.1 | 365.7 | 341.1 | 342.7 | 368.7 | 384 | 342.6
724 | 591 | 470.3 | 365.9 | 341.5 | 343.1 | 368.9 | 384.1 | 342.8
725 | 592 | 470.4 | 366.1 | 341.9 | 343.4 | 369.1 | 384.2 | 342.9
726 | 593 | 470.4 | 366.5 | 342.3 | 343.7 | 369.3 | 384.2 | 343.1
727 | 594 | 470.5 | 366.8 | 342.6 | 344.1 | 369.5 | 384.2 | 343.2
728 | 595 | 470.4 | 367.2 | 343 | 344.4 | 369.7 | 384.3 | 343.4
729 | 596 | 470.4 | 367.6 | 343.3 | 344.8 | 370 | 384.3 | 343.6
730 | 597 | 470.4 | 367.8 | 343.7 | 345.1 | 370.3 | 384.3 | 343.8
731 | 598 | 470.3 | 368 | 344 | 345.5 | 370.6 | 384.4 | 343.9
732 | 599 | 470.1 | 368.3 | 344.3 | 345.8 | 370.8 | 384.4 | 344.1
733 | 600 | 470.1 | 368.5 | 344.6 | 346.2 | 371 | 384.4 | 344.3
734 | 601 | 470 | 368.7 | 344.9 | 346.5 | 371.3 | 384.4 | 344.4
735 | 602 | 470 | 369 | 345.2 | 346.9 | 371.5 | 384.5 | 344.6
736 | 603 | 470 | 369.3 | 345.6 | 347.2 | 371.8 | 384.5 | 344.8
737 | 604 | 470 | 369.6 | 346 | 347.5 | 372.1 | 384.5 | 345
738 | 605 | 470.1 | 370 | 346.3 | 347.9 | 372.3 | 384.6 | 345.1
739 | 606 | 470.1 | 370.3 | 346.6 | 348.2 | 372.6 | 384.7 | 345.3
740 | 607 | 470.2 | 370.6 | 346.9 | 348.5 | 372.8 | 384.8 | 345.5
741 | 608 | 470.2 | 370.8 | 347.2 | 348.9 | 373.1 | 384.8 | 345.6
742 | 609 | 470.1 | 371 | 347.6 | 349.2 | 373.4 | 384.9 | 345.8
743 | 610 | 470.3 | 371.2 | 347.9 | 349.5 | 373.7 | 384.9 | 346
744 | 611 | 470.3 | 371.7 | 348.2 | 349.9 | 373.9 | 385 | 346.1
745 | 612 | 470.2 | 372.2 | 348.5 | 350.2 | 374.2 | 385 | 346.2
746 | 613 | 470.2 | 372.6 | 348.8 | 350.5 | 374.4 | 385.1 | 346.4
747 | 614 | 470.2 | 373 | 349.2 | 350.9 | 374.5 | 385.2 | 346.6
748 | 615 | 470 | 373.5 | 349.5 | 351.2 | 374.8 | 385.2 | 346.7
749 | 616 | 470 | 373.9 | 349.8 | 351.6 | 375.1 | 385.3 | 346.9
750 | 617 | 470.1 | 374.2 | 350.1 | 351.9 | 375.3 | 385.3 | 347.1
751 | 618 | 470.2 | 374.4 | 350.4 | 352.2 | 375.5 | 385.4 | 347.3
752 | 619 | 470.2 | 374.6 | 350.8 | 352.5 | 375.7 | 385.4 | 347.5
753 | 620 | 470.2 | 374.8 | 351.1 | 352.8 | 375.9 | 385.5 | 347.7
754 | 621 | 470.2 | 375 | 351.5 | 353.2 | 376 | 385.6 | 347.9
755 | 622 | 470.3 | 375.2 | 351.8 | 353.4 | 376.2 | 385.7 | 348.1
756 | 623 | 470.2 | 375.4 | 352.1 | 353.8 | 376.4 | 385.8 | 348.3
757 | 624 | 470.1 | 375.6 | 352.4 | 354.1 | 376.6 | 385.8 | 348.5
758 | 625 | 470.1 | 375.8 | 352.8 | 354.4 | 376.8 | 385.9 | 348.7
759 | 626 | 470.1 | 375.9 | 353.1 | 354.7 | 377 | 386 | 348.8
760 | 627 | 470 | 376.1 | 353.4 | 355 | 377.1 | 386.1 | 348.9
761 | 628 | 469.9 | 376.3 | 353.7 | 355.3 | 377.3 | 386.1 | 349
762 | 629 | 469.8 | 376.5 | 354 | 355.7 | 377.6 | 386.2 | 349.1
763 | 630 | 469.7 | 376.7 | 354.3 | 356 | 377.8 | 386.3 | 349.2
764 | 631 | 469.6 | 376.9 | 354.6 | 356.3 | 378 | 386.3 | 349.4
765 | 632 | 469.4 | 377.1 | 354.8 | 356.6 | 378.2 | 386.4 | 349.5
766 | 633 | 469.3 | 377.3 | 355.2 | 356.9 | 378.4 | 386.5 | 349.7
767 | 634 | 469.3 | 377.6 | 355.4 | 357.2 | 378.6 | 386.5 | 349.8
768 | 635 | 469.3 | 377.9 | 355.7 | 357.5 | 378.8 | 386.6 | 349.9
769 | 636 | 469.3 | 378.1 | 356 | 357.8 | 379 | 386.6 | 350.1
770 | 637 | 469.2 | 378.4 | 356.2 | 358.1 | 379.2 | 386.7 | 350.2
771 | 638 | 469.2 | 378.7 | 356.5 | 358.4 | 379.5 | 386.7 | 350.3
772 | 639 | 469.3 | 379 | 356.8 | 358.7 | 379.6 | 386.8 | 350.4
773 | 640 | 469.4 | 379.2 | 357.1 | 359 | 379.8 | 386.9 | 350.5
774 | 641 | 469.3 | 379.5 | 357.3 | 359.3 | 380 | 387 | 350.6
775 | 642 | 469.3 | 379.7 | 357.6 | 359.6 | 380.1 | 387 | 350.8
776 | 643 | 469.4 | 379.9 | 358 | 359.9 | 380.2 | 387.1 | 351
777 | 644 | 469.6 | 380.1 | 358.3 | 360.2 | 380.3 | 387.2 | 351.1
778 | 645 | 469.6 | 380.3 | 358.6 | 360.5 | 380.5 | 387.3 | 351.2
779 | 646 | 469.6 | 380.6 | 358.8 | 360.8 | 380.6 | 387.4 | 351.3
780 | 647 | 469.5 | 380.8 | 359.2 | 361 | 380.8 | 387.5 | 351.4
781 | 648 | 469.5 | 381.1 | 359.5 | 361.3 | 380.9 | 387.5 | 351.5
782 | 649 | 469.5 | 381.3 | 359.8 | 361.6 | 381.1 | 387.6 | 351.6
783 | 650 | 469.4 | 381.5 | 360.1 | 361.9 | 381.3 | 387.7 | 351.7
784 | 651 | 469.4 | 381.8 | 360.4 | 362.2 | 381.5 | 387.8 | 351.8
785 | 652 | 469.4 | 382 | 360.7 | 362.5 | 381.6 | 387.9 | 351.9
786 | 653 | 469.6 | 382.2 | 360.9 | 362.7 | 381.8 | 388 | 352.1
787 | 654 | 469.5 | 382.3 | 361.2 | 363 | 381.9 | 388 | 352.2
788 | 655 | 469.4 | 382.4 | 361.5 | 363.3 | 382.1 | 388.1 | 352.4
789 | 656 | 469.3 | 382.5 | 361.8 | 363.6 | 382.3 | 388.1 | 352.5
790 | 657 | 469.4 | 382.7 | 362.1 | 363.9 | 382.4 | 388.2 | 352.6
791 | 658 | 469.6 | 382.8 | 362.4 | 364.1 | 382.5 | 388.3 | 352.8
792 | 659 | 469.8 | 383 | 362.7 | 364.4 | 382.7 | 388.4 | 352.9
793 | 660 | 469.9 | 383.1 | 363 | 364.7 | 382.8 | 388.4 | 353
794 | 661 | 469.7 | 383.3 | 363.3 | 365 | 383 | 388.5 | 353.1
795 | 662 | 469.7 | 383.4 | 363.6 | 365.3 | 383.1 | 388.6 | 353.2
796 | 663 | 469.8 | 383.6 | 363.9 | 365.5 | 383.3 | 388.6 | 353.3
797 | 664 | 469.7 | 383.8 | 364.1 | 365.8 | 383.5 | 388.7 | 353.4
798 | 665 | 469.7 | 384 | 364.3 | 366.1 | 383.7 | 388.8 | 353.6
799 | 666 | 469.8 | 384.1 | 364.6 | 366.4 | 383.9 | 388.9 | 353.6
800 | 667 | 469.9 | 384.3 | 364.9 | 366.6 | 384 | 389 | 353.7
801 | 668 | 470 | 384.4 | 365.2 | 366.9 | 384.2 | 389.1 | 353.8
802 | 669 | 470.1 | 384.6 | 365.4 | 367.2 | 384.3 | 389.2 | 353.9
803 | 670 | 470.2 | 384.7 | 365.7 | 367.5 | 384.5 | 389.3 | 354
804 | 671 | 470.1 | 384.9 | 366 | 367.7 | 384.6 | 389.3 | 354.2
805 | 672 | 470 | 385 | 366.3 | 368 | 384.7 | 389.4 | 354.3
806 | 673 | 470 | 385.1 | 366.6 | 368.3 | 384.9 | 389.5 | 354.4
807 | 674 | 470 | 385.3 | 366.9 | 368.5 | 385.1 | 389.6 | 354.5
808 | 675 | 470.2 | 385.5 | 367.1 | 368.8 | 385.2 | 389.7 | 354.6
809 | 676 | 470.3 | 385.6 | 367.3 | 369.1 | 385.4 | 389.8 | 354.7
810 | 677 | 470.4 | 385.8 | 367.6 | 369.4 | 385.5 | 389.9 | 354.9
811 | 678 | 470.4 | 385.9 | 367.9 | 369.6 | 385.6 | 390 | 355
812 | 679 | 470.5 | 386.1 | 368.2 | 369.9 | 385.8 | 390.1 | 355.1
813 | 680 | 470.6 | 386.2 | 368.5 | 370.1 | 385.9 | 390.2 | 355.2
814 | 681 | 470.8 | 386.4 | 368.7 | 370.4 | 386.1 | 390.3 | 355.3
815 | 682 | 470.9 | 386.5 | 369 | 370.6 | 386.2 | 390.4 | 355.3
816 | 683 | 470.9 | 386.7 | 369.2 | 370.9 | 386.3 | 390.5 | 355.4
817 | 684 | 470.9 | 386.9 | 369.4 | 371.1 | 386.5 | 390.6 | 355.5
818 | 685 | 470.8 | 387 | 369.6 | 371.4 | 386.7 | 390.7 | 355.6
819 | 686 | 470.8 | 387.2 | 369.8 | 371.6 | 386.9 | 390.8 | 355.7
820 | 687 | 470.8 | 387.4 | 369.9 | 371.9 | 387 | 390.9 | 355.9
821 | 688 | 470.9 | 387.6 | 370.1 | 372.1 | 387.2 | 391.1 | 356
822 | 689 | 470.9 | 387.7 | 370.3 | 372.4 | 387.4 | 391.2 | 356.1
823 | 690 | 470.9 | 387.9 | 370.5 | 372.6 | 387.5 | 391.2 | 356.2
824 | 691 | 470.9 | 388 | 370.8 | 372.8 | 387.5 | 391.3 | 356.3
825 | 692 | 470.9 | 388.1 | 371 | 373.1 | 387.7 | 391.4 | 356.3
826 | 693 | 471.1 | 388.3 | 371.2 | 373.3 | 387.8 | 391.5 | 356.4
827 | 694 | 471.2 | 388.4 | 371.4 | 373.5 | 387.9 | 391.6 | 356.5
828 | 695 | 471.2 | 388.6 | 371.5 | 373.7 | 388.1 | 391.7 | 356.6
829 | 696 | 471.1 | 388.7 | 371.7 | 374 | 388.3 | 391.8 | 356.7
830 | 697 | 471 | 388.9 | 371.8 | 374.2 | 388.4 | 391.9 | 356.9
831 | 698 | 471 | 389 | 372 | 374.4 | 388.6 | 392 | 357
832 | 699 | 471 | 389.2 | 372.1 | 374.6 | 388.8 | 392.1 | 357.1
833 | 700 | 470.9 | 389.3 | 372.2 | 374.8 | 389 | 392.2 | 357.3
834 | 701 | 470.9 | 389.4 | 372.3 | 375 | 389.1 | 392.3 | 357.3
835 | 702 | 470.8 | 389.6 | 372.5 | 375.2 | 389.3 | 392.4 | 357.4
836 | 703 | 470.7 | 389.7 | 372.6 | 375.4 | 389.4 | 392.5 | 357.5
837 | 704 | 470.6 | 389.8 | 372.6 | 375.5 | 389.6 | 392.5 | 357.6
838 | 705 | 470.3 | 390 | 372.7 | 375.7 | 389.7 | 392.6 | 357.7
839 | 706 | 470.3 | 390.1 | 372.7 | 375.8 | 389.9 | 392.7 | 357.7
840 | 707 | 470.2 | 390.3 | 372.8 | 376 | 390.1 | 392.7 | 357.8
841 | 708 | 470.2 | 390.4 | 372.8 | 376.1 | 390.2 | 392.8 | 357.9
842 | 709 | 470.2 | 390.6 | 372.9 | 376.2 | 390.3 | 392.9 | 358
843 | 710 | 470.1 | 390.7 | 372.9 | 376.4 | 390.4 | 392.9 | 358.1
844 | 711 | 470 | 390.8 | 373 | 376.5 | 390.5 | 393 | 358.2
845 | 712 | 469.9 | 390.9 | 373 | 376.6 | 390.7 | 393.1 | 358.3
846 | 713 | 470 | 391 | 373.1 | 376.7 | 390.8 | 393.2 | 358.3
847 | 714 | 470.1 | 391.2 | 373.1 | 376.8 | 391 | 393.3 | 358.4
848 | 715 | 470.1 | 391.3 | 373.2 | 376.9 | 391.1 | 393.4 | 358.5
849 | 716 | 470.1 | 391.4 | 373.2 | 377 | 391.2 | 393.5 | 358.6
850 | 717 | 470.1 | 391.5 | 373.2 | 377.1 | 391.4 | 393.6 | 358.7
851 | 718 | 470.2 | 391.6 | 373.3 | 377.2 | 391.5 | 393.6 | 358.7
852 | 719 | 470.3 | 391.7 | 373.4 | 377.3 | 391.6 | 393.7 | 358.9
853 | 720 | 470.3 | 391.8 | 373.5 | 377.4 | 391.7 | 393.8 | 359
854 | 721 | 470.5 | 392 | 373.5 | 377.4 | 391.8 | 393.9 | 359.1
855 | 722 | 470.6 | 392.1 | 373.6 | 377.5 | 391.9 | 394 | 359.2
856 | 723 | 470.6 | 392.2 | 373.7 | 377.6 | 392 | 394.1 | 359.3
857 | 724 | 470.7 | 392.3 | 373.7 | 377.6 | 392.1 | 394.2 | 359.4
858 | 725 | 470.8 | 392.4 | 373.8 | 377.7 | 392.3 | 394.3 | 359.4
859 | 726 | 470.8 | 392.6 | 373.8 | 377.7 | 392.5 | 394.5 | 359.5
860 | 727 | 470.7 | 392.8 | 373.8 | 377.8 | 392.6 | 394.6 | 359.6
861 | 728 | 470.7 | 392.9 | 373.9 | 377.8 | 392.8 | 394.7 | 359.7
862 | 729 | 470.8 | 393.1 | 373.9 | 377.8 | 392.9 | 394.8 | 359.8
863 | 730 | 470.8 | 393.3 | 374 | 377.8 | 393 | 394.9 | 359.8
864 | 731 | 470.8 | 393.4 | 374 | 377.8 | 393.2 | 395 | 359.9
865 | 732 | 470.8 | 393.6 | 374.1 | 377.9 | 393.3 | 395.1 | 360
866 | 733 | 470.6 | 393.7 | 374.1 | 377.9 | 393.4 | 395.2 | 360.1
867 | 734 | 470.5 | 393.9 | 374.2 | 377.9 | 393.6 | 395.3 | 360.1
868 | 735 | 470.5 | 394 | 374.2 | 378 | 393.7 | 395.4 | 360.2
869 | 736 | 470.5 | 394.2 | 374.2 | 378 | 393.8 | 395.5 | 360.3
870 | 737 | 470.5 | 394.3 | 374.3 | 378 | 394 | 395.6 | 360.3
871 | 738 | 470.5 | 394.4 | 374.4 | 378 | 394.1 | 395.7 | 360.5
872 | 739 | 470.5 | 394.6 | 374.4 | 378 | 394.2 | 395.8 | 360.5
873 | 740 | 470.4 | 394.7 | 374.5 | 378.1 | 394.3 | 395.8 | 360.6
874 | 741 | 470.4 | 394.8 | 374.5 | 378.1 | 394.4 | 395.9 | 360.6
875 | 742 | 470.4 | 395 | 374.6 | 378.1 | 394.5 | 396 | 360.7
876 | 743 | 470.4 | 395.1 | 374.6 | 378.1 | 394.6 | 396.1 | 360.8
877 | 744 | 470.2 | 395.2 | 374.7 | 378.2 | 394.6 | 396.1 | 360.8
878 | 745 | 470.1 | 395.4 | 374.7 | 378.2 | 394.7 | 396.2 | 360.9
879 | 746 | 470 | 395.5 | 374.8 | 378.2 | 394.9 | 396.3 | 361
880 | 747 | 470 | 395.7 | 374.8 | 378.3 | 395 | 396.4 | 361.1
881 | 748 | 470 | 395.8 | 374.8 | 378.3 | 395.1 | 396.5 | 361.2
882 | 749 | 469.8 | 395.9 | 374.9 | 378.4 | 395.2 | 396.6 | 361.2
883 | 750 | 469.8 | 396.1 | 374.9 | 378.4 | 395.3 | 396.6 | 361.3
884 | 751 | 469.7 | 396.2 | 374.9 | 378.5 | 395.4 | 396.7 | 361.4
885 | 752 | 469.7 | 396.3 | 375 | 378.5 | 395.4 | 396.8 | 361.5
886 | 753 | 469.6 | 396.1 | 375.7 | 378.3 | 394.6 | 396.8 | 361.6
887 | 754 | 469.6 | 396.3 | 375.7 | 378.4 | 394.7 | 396.9 | 361.7
888 | 755 | 469.5 | 396.4 | 375.8 | 378.4 | 394.8 | 397 | 361.8
889 | 756 | 469.5 | 396.5 | 375.8 | 378.5 | 394.8 | 397.1 | 362
890 | 757 | 469.5 | 396.7 | 375.9 | 378.5 | 394.9 | 397.2 | 362
891 | 758 | 469.5 | 396.8 | 375.9 | 378.6 | 395 | 397.3 | 362.1
892 | 759 | 469.6 | 397 | 376 | 378.6 | 395.1 | 397.4 | 362.1
893 | 760 | 469.7 | 397.1 | 376.1 | 378.7 | 395.1 | 397.5 | 362.2
894 | 761 | 469.9 | 397.2 | 376.1 | 378.7 | 395.2 | 397.6 | 362.3
895 | 762 | 470 | 397.3 | 376.2 | 378.8 | 395.2 | 397.7 | 362.3
896 | 763 | 470 | 397.5 | 376.3 | 378.8 | 395.3 | 397.8 | 362.3
897 | 764 | 469.9 | 397.6 | 376.4 | 378.9 | 395.3 | 397.9 | 362.4
898 | 765 | 469.8 | 397.7 | 376.4 | 379 | 395.4 | 398 | 362.5
899 | 766 | 469.7 | 397.8 | 376.5 | 379 | 395.4 | 398.1 | 362.6
900 | 767 | 469.5 | 397.9 | 376.6 | 379.1 | 395.5 | 398.2 | 362.7
901 | 768 | 469.5 | 398.1 | 376.6 | 379.1 | 395.5 | 398.3 | 362.8
902 | 769 | 469.5 | 398.2 | 376.7 | 379.2 | 395.6 | 398.4 | 362.9
903 | 770 | 469.4 | 398.3 | 376.8 | 379.3 | 395.6 | 398.5 | 363
904 | 771 | 469.3 | 398.4 | 376.9 | 379.3 | 395.6 | 398.5 | 363.1
905 | 772 | 469.4 | 398.6 | 376.9 | 379.4 | 395.7 | 398.6 | 363.2
906 | 773 | 469.4 | 398.7 | 377 | 379.5 | 395.7 | 398.7 | 363.3
907 | 774 | 469.5 | 398.8 | 377 | 379.5 | 395.8 | 398.8 | 363.5
908 | 775 | 469.6 | 398.9 | 377.1 | 379.6 | 395.8 | 398.9 | 363.6
909 | 776 | 469.6 | 399 | 377.2 | 379.7 | 395.8 | 398.9 | 363.7
910 | 777 | 469.5 | 399.2 | 377.2 | 379.7 | 395.9 | 399 | 363.7
911 | 778 | 469.5 | 399.3 | 377.3 | 379.8 | 395.9 | 399.1 | 363.8
912 | 779 | 469.4 | 399.4 | 377.4 | 379.9 | 395.9 | 399.1 | 363.8
913 | 780 | 469.3 | 399.5 | 377.4 | 380 | 396 | 399.2 | 363.8
914 | 781 | 469.2 | 399.7 | 377.5 | 380 | 396.1 | 399.3 | 363.9
915 | 782 | 469.2 | 399.8 | 377.5 | 380.1 | 396.2 | 399.4 | 363.9
916 | 783 | 469.2 | 400 | 377.5 | 380.2 | 396.2 | 399.5 | 364
917 | 784 | 469.2 | 400.1 | 377.6 | 380.3 | 396.3 | 399.6 | 364.1
918 | 785 | 469.1 | 400.2 | 377.7 | 380.4 | 396.4 | 399.7 | 364.1
919 | 786 | 469 | 400.4 | 377.8 | 380.5 | 396.4 | 399.8 | 364.1
920 | 787 | 469 | 400.5 | 377.8 | 380.5 | 396.5 | 399.9 | 364.3
921 | 788 | 469 | 400.6 | 377.9 | 380.6 | 396.5 | 400 | 364.3
922 | 789 | 469.1 | 400.7 | 378 | 380.7 | 396.6 | 400.1 | 364.4
923 | 790 | 469.3 | 400.8 | 378.1 | 380.8 | 396.7 | 400.2 | 364.5
924 | 791 | 469.6 | 400.9 | 378.2 | 380.8 | 396.7 | 400.3 | 364.5
925 | 792 | 469.7 | 401 | 378.3 | 380.9 | 396.7 | 400.4 | 364.6
926 | 793 | 469.8 | 401.1 | 378.4 | 381 | 396.8 | 400.5 | 364.7
927 | 794 | 470.1 | 401.2 | 378.4 | 381.1 | 396.9 | 400.5 | 364.8
928 | 795 | 470.3 | 401.3 | 378.6 | 381.1 | 396.9 | 400.6 | 364.9
929 | 796 | 470.4 | 401.4 | 378.6 | 381.2 | 397 | 400.7 | 365
930 | 797 | 470.4 | 401.5 | 378.7 | 381.3 | 397.1 | 400.7 | 365.2
931 | 798 | 470.4 | 401.6 | 378.9 | 381.4 | 397.1 | 400.8 | 365.2
932 | 799 | 470.5 | 401.7 | 379 | 381.5 | 397.2 | 400.9 | 365.4
933 | 800 | 470.6 | 401.8 | 379.1 | 381.5 | 397.3 | 401 | 365.5
934 | 801 | 470.5 | 402 | 379.2 | 381.6 | 397.4 | 401.1 | 365.6
935 | 802 | 470.5 | 402.1 | 379.3 | 381.7 | 397.4 | 401.2 | 365.7
936 | 803 | 470.5 | 402.2 | 379.3 | 381.8 | 397.5 | 401.3 | 365.8
937 | 804 | 470.5 | 402.3 | 379.4 | 381.9 | 397.7 | 401.3 | 365.9
938 | 805 | 470.6 | 402.4 | 379.5 | 382 | 397.8 | 401.4 | 366
939 | 806 | 470.8 | 402.5 | 379.6 | 382 | 397.8 | 401.4 | 366.2
940 | 807 | 470.7 | 402.6 | 379.8 | 382.1 | 397.9 | 401.5 | 366.3
941 | 808 | 470.6 | 402.7 | 379.9 | 382.2 | 398 | 401.6 | 366.4
942 | 809 | 470.5 | 402.8 | 380 | 382.3 | 398.1 | 401.7 | 366.4
943 | 810 | 470.6 | 402.9 | 380.1 | 382.4 | 398.2 | 401.8 | 366.4
944 | 811 | 470.6 | 403 | 380.2 | 382.5 | 398.3 | 402 | 366.5
945 | 812 | 470.7 | 403.1 | 380.3 | 382.5 | 398.3 | 402.1 | 366.6
946 | 813 | 470.7 | 403.2 | 380.4 | 382.6 | 398.4 | 402.2 | 366.7
947 | 814 | 470.7 | 403.3 | 380.5 | 382.7 | 398.5 | 402.3 | 366.8
948 | 815 | 470.7 | 403.4 | 380.7 | 382.8 | 398.5 | 402.4 | 366.9
949 | 816 | 470.6 | 403.5 | 380.8 | 382.9 | 398.6 | 402.5 | 367
950 | 817 | 470.5 | 403.6 | 380.9 | 383 | 398.7 | 402.6 | 367.1
951 | 818 | 470.4 | 403.7 | 381 | 383 | 398.7 | 402.6 | 367.2
952 | 819 | 470.3 | 403.8 | 381.1 | 383.1 | 398.8 | 402.7 | 367.3
953 | 820 | 470.1 | 403.9 | 381.2 | 383.3 | 398.9 | 402.8 | 367.5
954 | 821 | 469.9 | 404.1 | 381.2 | 383.4 | 399 | 402.8 | 367.6
955 | 822 | 469.9 | 404.2 | 381.4 | 383.4 | 399 | 402.9 | 367.8
956 | 823 | 469.9 | 404.3 | 381.5 | 383.5 | 399.1 | 402.9 | 367.9
957 | 824 | 469.8 | 404.4 | 381.6 | 383.6 | 399.2 | 403 | 368.1
958 | 825 | 469.6 | 404.5 | 381.7 | 383.7 | 399.3 | 403 | 368.1
959 | 826 | 469.4 | 404.5 | 381.8 | 383.8 | 399.3 | 403.1 | 368.2
960 | 827 | 469.3 | 404.6 | 381.9 | 383.9 | 399.4 | 403.1 | 368.4
961 | 828 | 469.4 | 404.7 | 382 | 384 | 399.4 | 403.2 | 368.5
962 | 829 | 469.3 | 404.8 | 382.1 | 384.1 | 399.5 | 403.2 | 368.6
963 | 830 | 469.4 | 404.9 | 382.2 | 384.2 | 399.6 | 403.2 | 368.7
964 | 831 | 469.4 | 405 | 382.3 | 384.3 | 399.6 | 403.2 | 368.8
965 | 832 | 469.3 | 405.1 | 382.5 | 384.4 | 399.7 | 403.3 | 369
966 | 833 | 469.2 | 405.2 | 382.5 | 384.5 | 399.8 | 403.3 | 369.2
967 | 834 | 469.2 | 405.3 | 382.6 | 384.6 | 399.9 | 403.3 | 369.2
968 | 835 | 469.3 | 405.4 | 382.7 | 384.7 | 400 | 403.3 | 369.3
969 | 836 | 469.1 | 405.5 | 382.8 | 384.8 | 400.1 | 403.3 | 369.4
970 | 837 | 469.1 | 405.6 | 382.9 | 384.9 | 400.2 | 403.4 | 369.4
971 | 838 | 469.1 | 405.7 | 383 | 385 | 400.2 | 403.4 | 369.4
972 | 839 | 469.1 | 405.7 | 383.1 | 385.1 | 400.3 | 403.4 | 369.4
973 | 840 | 469.3 | 405.8 | 383.3 | 385.2 | 400.4 | 403.3 | 369.5
974 | 841 | 469.3 | 405.9 | 383.4 | 385.3 | 400.4 | 403.3 | 369.5
975 | 842 | 469.3 | 406 | 383.5 | 385.4 | 400.4 | 403.4 | 369.7
976 | 843 | 469.4 | 406 | 383.7 | 385.5 | 400.5 | 403.4 | 369.8
977 | 844 | 469.6 | 406.1 | 383.8 | 385.6 | 400.5 | 403.4 | 369.8
978 | 845 | 469.8 | 406.2 | 384 | 385.7 | 400.6 | 403.5 | 369.9
979 | 846 | 469.9 | 406.3 | 384.1 | 385.8 | 400.7 | 403.5 | 369.9
980 | 847 | 469.9 | 406.4 | 384.2 | 385.9 | 400.8 | 403.6 | 369.9
981 | 848 | 469.9 | 406.4 | 384.3 | 386 | 400.8 | 403.6 | 370
982 | 849 | 469.8 | 406.5 | 384.5 | 386.1 | 400.9 | 403.7 | 370
983 | 850 | 469.9 | 406.6 | 384.6 | 386.2 | 400.9 | 403.7 | 370
984 | 851 | 470 | 406.7 | 384.7 | 386.3 | 401 | 403.7 | 370.1
985 | 852 | 470.1 | 406.8 | 384.8 | 386.4 | 401 | 403.8 | 370.2
986 | 853 | 470.1 | 406.8 | 385 | 386.5 | 401.1 | 403.8 | 370.3
987 | 854 | 470.1 | 406.9 | 385.1 | 386.6 | 401.2 | 403.8 | 370.3
988 | 855 | 470.1 | 407 | 385.2 | 386.7 | 401.2 | 403.8 | 370.4
989 | 856 | 470.1 | 407.1 | 385.4 | 386.9 | 401.3 | 403.9 | 370.5
990 | 857 | 470.1 | 407.2 | 385.5 | 387 | 401.4 | 403.9 | 370.5
991 | 858 | 470 | 407.3 | 385.6 | 387.1 | 401.5 | 403.9 | 370.5
992 | 859 | 469.9 | 407.4 | 385.7 | 387.2 | 401.5 | 403.9 | 370.5
993 | 860 | 469.9 | 407.5 | 385.8 | 387.3 | 401.6 | 403.9 | 370.6
994 | 861 | 469.8 | 407.6 | 385.9 | 387.5 | 401.7 | 404 | 370.6
995 | 862 | 469.8 | 407.7 | 386 | 387.6 | 401.8 | 404 | 370.7
996 | 863 | 469.8 | 407.8 | 386.1 | 387.7 | 401.9 | 404.1 | 370.8
997 | 864 | 469.7 | 407.9 | 386.3 | 387.8 | 401.9 | 404.1 | 370.8
998 | 865 | 469.6 | 407.9 | 386.4 | 387.9 | 402 | 404.2 | 370.9
999 | 866 | 469.6 | 408 | 386.6 | 388.1 | 402.1 | 404.2 | 371
1000 | 867 | 469.6 | 408.1 | 386.7 | 388.2 | 402.2 | 404.2 | 371.1
1001 | 868 | 469.5 | 408.2 | 386.8 | 388.3 | 402.2 | 404.3 | 371.2
1002 | 869 | 469.4 | 408.3 | 387 | 388.4 | 402.3 | 404.3 | 371.2
1003 | 870 | 469.4 | 408.4 | 387.1 | 388.6 | 402.4 | 404.4 | 371.2
1004 | 871 | 469.5 | 408.5 | 387.2 | 388.7 | 402.5 | 404.4 | 371.3
1005 | 872 | 469.6 | 408.6 | 387.4 | 388.8 | 402.5 | 404.5 | 371.3
1006 | 873 | 469.7 | 408.7 | 387.5 | 389 | 402.7 | 404.5 | 371.4
1007 | 874 | 469.5 | 408.8 | 387.6 | 389.1 | 402.8 | 404.5 | 371.4
1008 | 875 | 469.4 | 408.9 | 387.8 | 389.2 | 402.8 | 404.5 | 371.4
1009 | 876 | 469.4 | 409 | 387.9 | 389.4 | 402.9 | 404.6 | 371.5
1010 | 877 | 469.5 | 409.1 | 388 | 389.5 | 403 | 404.6 | 371.5
1011 | 878 | 469.5 | 409.2 | 388.2 | 389.7 | 403.1 | 404.6 | 371.5
1012 | 879 | 469.6 | 409.3 | 388.3 | 389.8 | 403.1 | 404.7 | 371.6
1013 | 880 | 469.7 | 409.4 | 388.5 | 390 | 403.2 | 404.7 | 371.6
1014 | 881 | 469.7 | 409.5 | 388.6 | 390.1 | 403.3 | 404.7 | 371.6
1015 | 882 | 469.6 | 409.6 | 388.7 | 390.3 | 403.4 | 404.8 | 371.6
1016 | 883 | 469.5 | 409.7 | 388.8 | 390.4 | 403.5 | 404.8 | 371.6
1017 | 884 | 469.4 | 409.8 | 388.9 | 390.5 | 403.6 | 404.9 | 371.6
1018 | 885 | 469.4 | 409.8 | 389.1 | 390.7 | 403.7 | 404.9 | 371.7
1019 | 886 | 469.6 | 409.9 | 389.2 | 390.8 | 403.7 | 404.9 | 371.7
1020 | 887 | 469.7 | 410 | 389.4 | 391 | 403.8 | 404.9 | 371.7
1021 | 888 | 469.7 | 410.1 | 389.5 | 391.1 | 403.9 | 404.9 | 371.8
1022 | 889 | 469.8 | 410.2 | 389.7 | 391.2 | 403.9 | 405 | 371.9
1023 | 890 | 469.9 | 410.3 | 389.8 | 391.3 | 404 | 405 | 371.9
1024 | 891 | 470 | 410.4 | 390 | 391.5 | 404.1 | 405 | 371.8
1025 | 892 | 470 | 410.5 | 390.1 | 391.6 | 404.2 | 405 | 371.8
1026 | 893 | 470.1 | 410.6 | 390.2 | 391.8 | 404.3 | 405.1 | 371.9
1027 | 894 | 470.2 | 410.7 | 390.4 | 391.9 | 404.4 | 405.1 | 372
1028 | 895 | 470.3 | 410.8 | 390.5 | 392.1 | 404.6 | 405.2 | 372
1029 | 896 | 470.3 | 410.9 | 390.7 | 392.2 | 404.7 | 405.2 | 372
1030 | 897 | 470.5 | 411 | 390.8 | 392.3 | 404.8 | 405.2 | 372.1
1031 | 898 | 470.6 | 411 | 390.9 | 392.5 | 404.9 | 405.2 | 372.1
1032 | 899 | 470.8 | 411.1 | 391.1 | 392.6 | 404.9 | 405.3 | 372.1
1033 | 900 | 470.9 | 411.2 | 391.2 | 392.7 | 405 | 405.3 | 372
1034 | 901 | 470.9 | 411.3 | 391.4 | 392.9 | 405.1 | 405.4 | 372
1035 | 902 | 471 | 411.4 | 391.5 | 393 | 405.3 | 405.4 | 372
1036 | 903 | 471 | 411.5 | 391.6 | 393.1 | 405.4 | 405.4 | 372
1037 | 904 | 471 | 411.6 | 391.8 | 393.3 | 405.5 | 405.4 | 371.9
1038 | 905 | 471.1 | 411.7 | 391.9 | 393.4 | 405.6 | 405.4 | 372
1039 | 906 | 471.2 | 411.8 | 392.1 | 393.5 | 405.6 | 405.5 | 372
1040 | 907 | 471.2 | 411.8 | 392.2 | 393.6 | 405.7 | 405.5 | 372
1041 | 908 | 471.1 | 411.9 | 392.4 | 393.8 | 405.8 | 405.6 | 372.1
1042 | 909 | 471.1 | 412 | 392.5 | 393.9 | 405.9 | 405.6 | 372.2
1043 | 910 | 471.1 | 412.1 | 392.6 | 394 | 406 | 405.7 | 372.3
1044 | 911 | 471.1 | 412.2 | 392.8 | 394.2 | 406.1 | 405.7 | 372.3
1045 | 912 | 471 | 412.3 | 392.9 | 394.3 | 406.2 | 405.8 | 372.2
1046 | 913 | 470.9 | 412.3 | 393.1 | 394.4 | 406.2 | 405.8 | 372.3
1047 | 914 | 470.8 | 412.4 | 393.2 | 394.6 | 406.3 | 405.9 | 372.3
1048 | 915 | 470.7 | 412.5 | 393.4 | 394.7 | 406.4 | 405.9 | 372.3
1049 | 916 | 470.6 | 412.6 | 393.5 | 394.8 | 406.5 | 406 | 372.3
1050 | 917 | 470.5 | 412.7 | 393.6 | 395 | 406.6 | 406 | 372.3
1051 | 918 | 470.5 | 412.8 | 393.7 | 395.1 | 406.7 | 406 | 372.3
1052 | 919 | 470.5 | 412.9 | 393.8 | 395.2 | 406.8 | 406.1 | 372.3
1053 | 920 | 470.2 | 413 | 393.9 | 395.4 | 406.8 | 406.1 | 372.3
1054 | 921 | 470.1 | 413.1 | 394 | 395.5 | 406.9 | 406.1 | 372.3
1055 | 922 | 470 | 413.2 | 394.1 | 395.6 | 407 | 406.2 | 372.2
1056 | 923 | 469.8 | 413.3 | 394.3 | 395.8 | 407.1 | 406.2 | 372.2
1057 | 924 | 469.9 | 413.3 | 394.4 | 395.9 | 407.1 | 406.2 | 372.3
1058 | 925 | 470 | 413.4 | 394.6 | 396 | 407.2 | 406.3 | 372.3
1059 | 926 | 470 | 413.5 | 394.7 | 396.1 | 407.2 | 406.3 | 372.4
1060 | 927 | 469.8 | 413.5 | 394.8 | 396.2 | 407.3 | 406.3 | 372.4
1061 | 928 | 469.8 | 413.6 | 394.9 | 396.4 | 407.3 | 406.3 | 372.5
1062 | 929 | 469.8 | 413.7 | 395.1 | 396.5 | 407.4 | 406.4 | 372.4
1063 | 930 | 469.9 | 413.8 | 395.2 | 396.6 | 407.5 | 406.4 | 372.4
1064 | 931 | 470 | 413.9 | 395.3 | 396.7 | 407.6 | 406.4 | 372.4
1065 | 932 | 469.8 | 414 | 395.4 | 396.9 | 407.7 | 406.4 | 372.3
1066 | 933 | 469.6 | 414.1 | 395.5 | 397 | 407.7 | 406.4 | 372.4
1067 | 934 | 469.4 | 414.2 | 395.6 | 397.1 | 407.8 | 406.4 | 372.3
1068 | 935 | 469.4 | 414.3 | 395.7 | 397.3 | 407.9 | 406.4 | 372.3
1069 | 936 | 469.4 | 414.3 | 395.9 | 397.4 | 408 | 406.4 | 372.2
1070 | 937 | 469.3 | 414.5 | 396 | 397.5 | 408.1 | 406.4 | 372.2
1071 | 938 | 469.1 | 414.5 | 396 | 397.6 | 408.1 | 406.4 | 372.2
1072 | 939 | 469.1 | 414.6 | 396.2 | 397.8 | 408.2 | 406.4 | 372.2
1073 | 940 | 469.2 | 414.7 | 396.3 | 397.9 | 408.3 | 406.4 | 372.2
1074 | 941 | 469.3 | 414.8 | 396.4 | 398 | 408.3 | 406.4 | 372.2
1075 | 942 | 469.3 | 414.8 | 396.6 | 398.1 | 408.4 | 406.4 | 372.2
1076 | 943 | 469.4 | 414.9 | 396.7 | 398.2 | 408.4 | 406.4 | 372.2
1077 | 944 | 469.5 | 415 | 396.8 | 398.3 | 408.5 | 406.4 | 372.1
1078 | 945 | 469.7 | 415.1 | 396.9 | 398.4 | 408.5 | 406.4 | 372.2
1079 | 946 | 469.7 | 415.1 | 397 | 398.6 | 408.6 | 406.4 | 372.1
1080 | 947 | 469.8 | 415.2 | 397.2 | 398.7 | 408.6 | 406.5 | 372
1081 | 948 | 469.7 | 415.3 | 397.3 | 398.8 | 408.7 | 406.5 | 372
1082 | 949 | 469.7 | 415.4 | 397.4 | 398.9 | 408.8 | 406.5 | 372
1083 | 950 | 469.5 | 415.4 | 397.5 | 399 | 408.9 | 406.6 | 372
1084 | 951 | 469.6 | 415.5 | 397.6 | 399.2 | 409 | 406.6 | 372.1
1085 | 952 | 469.6 | 415.6 | 397.7 | 399.3 | 409.1 | 406.6 | 372.1
1086 | 953 | 469.6 | 415.7 | 397.8 | 399.4 | 409.2 | 406.6 | 372.1
1087 | 954 | 469.6 | 415.8 | 397.8 | 399.5 | 409.3 | 406.7 | 372.2
1088 | 955 | 469.7 | 415.9 | 398 | 399.6 | 409.3 | 406.7 | 372.2
1089 | 956 | 469.9 | 416 | 398.1 | 399.7 | 409.4 | 406.7 | 372.2
1090 | 957 | 470 | 416 | 398.2 | 399.8 | 409.4 | 406.7 | 372.3
1091 | 958 | 470.1 | 416.1 | 398.3 | 399.9 | 409.5 | 406.7 | 372.3
1092 | 959 | 470.1 | 416.2 | 398.5 | 400 | 409.5 | 406.8 | 372.4
1093 | 960 | 470.2 | 416.2 | 398.6 | 400.1 | 409.5 | 406.8 | 372.4
1094 | 961 | 470.2 | 416.3 | 398.7 | 400.2 | 409.6 | 406.8 | 372.4
1095 | 962 | 470.2 | 416.4 | 398.8 | 400.3 | 409.6 | 406.8 | 372.4
1096 | 963 | 470.2 | 416.5 | 398.9 | 400.4 | 409.7 | 406.8 | 372.5
1097 | 964 | 470.3 | 416.6 | 399 | 400.5 | 409.8 | 406.8 | 372.6
1098 | 965 | 470.3 | 416.7 | 399.1 | 400.6 | 409.8 | 406.8 | 372.6
1099 | 966 | 470.2 | 416.8 | 399.2 | 400.7 | 409.9 | 406.8 | 372.6
1100 | 967 | 470.4 | 416.8 | 399.3 | 400.8 | 409.9 | 406.8 | 372.6
1101 | 968 | 470.5 | 416.9 | 399.4 | 400.9 | 410 | 406.8 | 372.6
1102 | 969 | 470.4 | 417 | 399.5 | 401 | 410 | 406.8 | 372.7
1103 | 970 | 470.3 | 417 | 399.6 | 401.1 | 410 | 406.8 | 372.7
1104 | 971 | 470.3 | 417.1 | 399.7 | 401.2 | 410.1 | 406.8 | 372.7
1105 | 972 | 470.2 | 417.2 | 399.8 | 401.3 | 410.1 | 406.9 | 372.8
1106 | 973 | 470.1 | 417.3 | 399.9 | 401.4 | 410.2 | 406.9 | 372.8
1107 | 974 | 470.1 | 417.4 | 400 | 401.5 | 410.2 | 407 | 372.9
1108 | 975 | 470.2 | 417.4 | 400.1 | 401.6 | 410.3 | 407 | 373
1109 | 976 | 470 | 417.5 | 400.2 | 401.7 | 410.4 | 407 | 373
1110 | 977 | 469.9 | 417.6 | 400.3 | 401.8 | 410.4 | 407.1 | 373
1111 | 978 | 469.9 | 417.7 | 400.4 | 401.9 | 410.5 | 407.1 | 373
1112 | 979 | 469.8 | 417.8 | 400.4 | 402 | 410.5 | 407.1 | 372.9
1113 | 980 | 469.8 | 417.8 | 400.5 | 402.1 | 410.6 | 407.1 | 372.9
1114 | 981 | 469.8 | 417.9 | 400.6 | 402.2 | 410.7 | 407.1 | 373
1115 | 982 | 469.8 | 418 | 400.7 | 402.3 | 410.7 | 407.1 | 373
1116 | 983 | 469.7 | 418.1 | 400.8 | 402.4 | 410.8 | 407.2 | 373
1117 | 984 | 469.7 | 418.2 | 400.9 | 402.5 | 410.9 | 407.2 | 373.1
1118 | 985 | 469.7 | 418.3 | 401 | 402.6 | 410.9 | 407.2 | 373.1
1119 | 986 | 469.8 | 418.4 | 401.1 | 402.7 | 411 | 407.2 | 373.1
1120 | 987 | 469.8 | 418.5 | 401.2 | 402.8 | 411 | 407.2 | 373.1
1121 | 988 | 470 | 418.5 | 401.3 | 402.9 | 411 | 407.3 | 373
1122 | 989 | 470.1 | 418.5 | 401.4 | 403 | 411.1 | 407.3 | 373
1123 | 990 | 470 | 418.6 | 401.5 | 403 | 411.1 | 407.4 | 373
1124 | 991 | 470.1 | 418.5 | 401.8 | 403 | 410.8 | 407.4 | 373
1125 | 992 | 470.2 | 418.6 | 401.9 | 403.1 | 410.9 | 407.4 | 372.9
1126 | 993 | 470.3 | 418.6 | 402.1 | 403.2 | 410.9 | 407.4 | 372.9
1127 | 994 | 470.3 | 418.7 | 402.1 | 403.3 | 411 | 407.5 | 372.8
1128 | 995 | 470.2 | 418.7 | 402.2 | 403.4 | 411 | 407.5 | 372.8
1129 | 996 | 470.2 | 418.8 | 402.3 | 403.5 | 411 | 407.5 | 372.8
1130 | 997 | 470.3 | 418.8 | 402.4 | 403.6 | 411.1 | 407.5 | 372.8
1131 | 998 | 470.2 | 418.9 | 402.5 | 403.6 | 411.1 | 407.6 | 372.7
1132 | 999 | 470.1 | 418.9 | 402.6 | 403.7 | 411.2 | 407.6 | 372.8
1133 | 1000 | 469.9 | 419 | 402.7 | 403.8 | 411.2 | 407.6 | 372.8
1134 | 1001 | 469.8 | 419.1 | 402.8 | 403.9 | 411.3 | 407.6 | 372.8
1135 | 1002 | 469.7 | 419.2 | 402.9 | 404 | 411.3 | 407.6 | 372.8
1136 | 1003 | 469.8 | 419.2 | 403 | 404.1 | 411.4 | 407.6 | 372.8
1137 | 1004 | 469.8 | 419.3 | 403 | 404.2 | 411.5 | 407.6 | 372.8
1138 | 1005 | 469.7 | 419.3 | 403.1 | 404.3 | 411.5 | 407.6 | 372.7
1139 | 1006 | 469.7 | 419.3 | 403.2 | 404.3 | 411.6 | 407.7 | 372.7
1140 | 1007 | 469.6 | 419.4 | 403.2 | 404.4 | 411.7 | 407.7 | 372.7
1141 | 1008 | 469.4 | 419.5 | 403.3 | 404.5 | 411.7 | 407.7 | 372.7
1142 | 1009 | 469.2 | 419.5 | 403.3 | 404.6 | 411.9 | 407.7 | 372.7
1143 | 1010 | 469.2 | 419.8 | 403 | 404.9 | 412.6 | 407.8 | 372.7
1144 | 1011 | 469.2 | 419.9 | 403 | 404.9 | 412.7 | 407.8 | 372.7
1145 | 1012 | 469.1 | 419.9 | 403.1 | 405 | 412.7 | 407.8 | 372.7
1146 | 1013 | 469.2 | 420 | 403.2 | 405.1 | 412.7 | 407.9 | 372.7
1147 | 1014 | 469.3 | 420 | 403.3 | 405.2 | 412.8 | 407.9 | 372.7
1148 | 1015 | 469.3 | 420.1 | 403.4 | 405.3 | 412.9 | 407.9 | 372.7
1149 | 1016 | 469.2 | 420.1 | 403.5 | 405.3 | 412.9 | 408 | 372.8
1150 | 1017 | 469.1 | 420.2 | 403.5 | 405.4 | 413 | 408 | 372.8
1151 | 1018 | 469 | 420.2 | 403.6 | 405.5 | 413.1 | 408 | 372.8
1152 | 1019 | 468.9 | 420.2 | 403.7 | 405.6 | 413.1 | 408 | 372.8
1153 | 1020 | 468.9 | 420.2 | 403.8 | 405.6 | 413.1 | 408 | 372.8
1154 | 1021 | 469 | 420.3 | 403.8 | 405.7 | 413.2 | 408 | 372.8
1155 | 1022 | 469.1 | 420.3 | 403.9 | 405.8 | 413.2 | 408 | 372.8
1156 | 1023 | 468.8 | 420.3 | 404 | 405.9 | 413.3 | 408.1 | 372.8
1157 | 1024 | 468.9 | 420.4 | 404 | 405.9 | 413.3 | 408.1 | 372.9
1158 | 1025 | 469 | 420.4 | 404.1 | 406 | 413.3 | 408.1 | 373
1159 | 1026 | 469.1 | 420.5 | 404.2 | 406.1 | 413.3 | 408.2 | 373
1160 | 1027 | 469 | 420.5 | 404.3 | 406.2 | 413.3 | 408.2 | 373.1
1161 | 1028 | 469.1 | 420.6 | 404.4 | 406.3 | 413.4 | 408.2 | 373
1162 | 1029 | 469.2 | 420.6 | 404.5 | 406.3 | 413.4 | 408.2 | 373
1163 | 1030 | 469 | 420.7 | 404.6 | 406.4 | 413.4 | 408.3 | 373.1
1164 | 1031 | 468.9 | 420.7 | 404.6 | 406.5 | 413.4 | 408.3 | 373
1165 | 1032 | 468.8 | 420.7 | 404.7 | 406.5 | 413.4 | 408.3 | 373
1166 | 1033 | 468.9 | 420.7 | 404.8 | 406.6 | 413.4 | 408.3 | 373
1167 | 1034 | 469 | 420.7 | 404.9 | 406.7 | 413.4 | 408.3 | 373
1168 | 1035 | 469 | 420.8 | 404.9 | 406.8 | 413.4 | 408.3 | 373
1169 | 1036 | 469 | 420.8 | 405 | 406.8 | 413.4 | 408.3 | 373
1170 | 1037 | 469.1 | 420.9 | 405.1 | 406.9 | 413.4 | 408.3 | 373
1171 | 1038 | 469.1 | 420.9 | 405.2 | 407 | 413.4 | 408.3 | 373.1
1172 | 1039 | 468.9 | 421 | 405.3 | 407 | 413.4 | 408.4 | 373.2
1173 | 1040 | 468.9 | 421 | 405.3 | 407.1 | 413.5 | 408.4 | 373.3
1174 | 1041 | 468.8 | 421 | 405.4 | 407.2 | 413.5 | 408.4 | 373.3
1175 | 1042 | 468.9 | 421.1 | 405.5 | 407.3 | 413.5 | 408.4 | 373.3
1176 | 1043 | 469.1 | 421.1 | 405.6 | 407.3 | 413.5 | 408.4 | 373.2
1177 | 1044 | 469 | 421.1 | 405.6 | 407.4 | 413.5 | 408.4 | 373.2
1178 | 1045 | 469.1 | 421.2 | 405.7 | 407.5 | 413.5 | 408.5 | 373.3
1179 | 1046 | 469.2 | 421.2 | 405.8 | 407.6 | 413.6 | 408.5 | 373.3
1180 | 1047 | 469.2 | 421.3 | 405.8 | 407.6 | 413.6 | 408.4 | 373.3
1181 | 1048 | 469.2 | 421.4 | 405.9 | 407.7 | 413.7 | 408.4 | 373.3
1182 | 1049 | 469.1 | 421.4 | 405.9 | 407.8 | 413.7 | 408.5 | 373.3
1183 | 1050 | 469.2 | 421.5 | 406 | 407.9 | 413.8 | 408.5 | 373.3
1184 | 1051 | 469.2 | 421.5 | 406.1 | 407.9 | 413.8 | 408.5 | 373.4
1185 | 1052 | 469.1 | 421.5 | 406.1 | 408 | 413.8 | 408.5 | 373.4
1186 | 1053 | 469.1 | 421.5 | 406.2 | 408.1 | 413.8 | 408.6 | 373.4
1187 | 1054 | 469.1 | 421.5 | 406.3 | 408.1 | 413.8 | 408.6 | 373.5
1188 | 1055 | 469.2 | 421.6 | 406.4 | 408.2 | 413.8 | 408.6 | 373.5
1189 | 1056 | 469.3 | 421.6 | 406.5 | 408.2 | 413.8 | 408.6 | 373.4
1190 | 1057 | 469.5 | 421.7 | 406.6 | 408.3 | 413.8 | 408.7 | 373.4
1191 | 1058 | 469.4 | 421.7 | 406.6 | 408.4 | 413.8 | 408.7 | 373.3
1192 | 1059 | 469.3 | 421.7 | 406.7 | 408.4 | 413.8 | 408.7 | 373.4
1193 | 1060 | 469.3 | 421.7 | 406.8 | 408.5 | 413.9 | 408.7 | 373.4
1194 | 1061 | 469.4 | 421.8 | 406.8 | 408.6 | 413.9 | 408.7 | 373.3
1195 | 1062 | 469.3 | 421.8 | 406.9 | 408.6 | 413.9 | 408.7 | 373.4
1196 | 1063 | 469.3 | 421.9 | 406.9 | 408.7 | 413.9 | 408.7 | 373.5
1197 | 1064 | 469.3 | 421.9 | 407 | 408.8 | 413.9 | 408.7 | 373.6
1198 | 1065 | 469.4 | 421.9 | 407 | 408.8 | 414 | 408.7 | 373.6
1199 | 1066 | 469.4 | 422 | 407.1 | 408.9 | 414 | 408.8 | 373.6
1200 | 1067 | 469.5 | 422 | 407.2 | 409 | 414 | 408.8 | 373.6
1201 | 1068 | 469.4 | 422.1 | 407.2 | 409.1 | 414.1 | 408.8 | 373.6
1202 | 1069 | 469.3 | 422.1 | 407.3 | 409.1 | 414.1 | 408.8 | 373.6
1203 | 1070 | 469.3 | 422.2 | 407.4 | 409.2 | 414.1 | 408.9 | 373.6
1204 | 1071 | 469.3 | 422.2 | 407.4 | 409.3 | 414.2 | 408.9 | 373.7
1205 | 1072 | 469.4 | 422.3 | 407.5 | 409.3 | 414.2 | 408.9 | 373.7
1206 | 1073 | 469.3 | 422.3 | 407.5 | 409.4 | 414.3 | 408.8 | 373.7
1207 | 1074 | 469.3 | 422.3 | 407.6 | 409.5 | 414.3 | 408.9 | 373.8
1208 | 1075 | 469.3 | 422.4 | 407.6 | 409.5 | 414.4 | 408.9 | 373.7
1209 | 1076 | 469.4 | 422.4 | 407.7 | 409.6 | 414.5 | 408.9 | 373.7
1210 | 1077 | 469.5 | 422.4 | 407.7 | 409.7 | 414.6 | 408.9 | 373.7
1211 | 1078 | 469.6 | 422.5 | 407.8 | 409.7 | 414.7 | 409 | 373.8
1212 | 1079 | 469.7 | 422.5 | 407.9 | 409.8 | 414.7 | 409 | 373.8
1213 | 1080 | 469.8 | 422.5 | 407.9 | 409.9 | 414.8 | 409 | 373.8
1214 | 1081 | 470 | 422.5 | 408 | 409.9 | 414.8 | 409.1 | 373.9
1215 | 1082 | 470 | 422.6 | 408.1 | 410 | 414.9 | 409.1 | 374
1216 | 1083 | 470.2 | 422.6 | 408.1 | 410 | 415 | 409.2 | 374.2
1217 | 1084 | 470.5 | 422.7 | 408.2 | 410.1 | 415.1 | 409.2 | 374.3
1218 | 1085 | 470.7 | 422.7 | 408.3 | 410.1 | 415.1 | 409.2 | 374.4
1219 | 1086 | 471 | 422.7 | 408.5 | 410.2 | 415.1 | 409.3 | 374.4
1220 | 1087 | 471.1 | 422.7 | 408.6 | 410.2 | 415.1 | 409.3 | 374.5
1221 | 1088 | 471.2 | 422.7 | 408.6 | 410.3 | 415.2 | 409.4 | 374.6
1222 | 1089 | 471.2 | 422.7 | 408.7 | 410.3 | 415.3 | 409.4 | 374.6
1223 | 1090 | 471.4 | 422.7 | 408.8 | 410.4 | 415.4 | 409.5 | 374.6
1224 | 1091 | 471.5 | 422.8 | 408.8 | 410.4 | 415.5 | 409.5 | 374.6
1225 | 1092 | 471.4 | 422.8 | 408.9 | 410.5 | 415.6 | 409.6 | 374.7
1226 | 1093 | 471.3 | 422.9 | 408.9 | 410.6 | 415.6 | 409.6 | 374.8
1227 | 1094 | 471.2 | 422.9 | 409 | 410.6 | 415.7 | 409.7 | 374.8
1228 | 1095 | 471.2 | 422.9 | 409 | 410.7 | 415.8 | 409.7 | 374.9
1229 | 1096 | 471.2 | 423 | 409.1 | 410.8 | 415.9 | 409.8 | 374.9
1230 | 1097 | 471.2 | 423 | 409.1 | 410.8 | 416 | 409.8 | 375
1231 | 1098 | 471.2 | 423 | 409.2 | 410.9 | 416 | 409.8 | 375
1232 | 1099 | 471.2 | 423.1 | 409.3 | 410.9 | 416.1 | 409.9 | 375
1233 | 1100 | 471.1 | 423.1 | 409.3 | 411 | 416.1 | 409.9 | 375.1
1234 | 1101 | 470.8 | 423.1 | 409.4 | 411 | 416.2 | 409.9 | 375.1
1235 | 1102 | 470.8 | 423.1 | 409.5 | 411.1 | 416.2 | 409.9 | 375.2
1236 | 1103 | 470.7 | 423.2 | 409.6 | 411.1 | 416.2 | 410 | 375.2
1237 | 1104 | 470.6 | 423.2 | 409.6 | 411.2 | 416.3 | 410 | 375.3
1238 | 1105 | 470.6 | 423.3 | 409.7 | 411.2 | 416.4 | 410 | 375.3
1239 | 1106 | 470.5 | 423.4 | 409.8 | 411.3 | 416.5 | 410 | 375.2
1240 | 1107 | 470.2 | 423.4 | 409.8 | 411.4 | 416.6 | 410 | 375.2
1241 | 1108 | 470 | 423.5 | 409.8 | 411.4 | 416.7 | 410 | 375.2
1242 | 1109 | 469.9 | 423.6 | 409.8 | 411.5 | 416.8 | 410 | 375.2
1243 | 1110 | 469.7 | 423.6 | 409.8 | 411.6 | 416.9 | 410 | 375.1
1244 | 1111 | 469.5 | 423.6 | 409.9 | 411.6 | 417 | 410 | 375.1
1245 | 1112 | 469.5 | 423.7 | 409.9 | 411.7 | 417 | 410 | 375.1
1246 | 1113 | 469.4 | 423.7 | 410 | 411.8 | 417.1 | 410 | 375.1
1247 | 1114 | 469.4 | 423.8 | 410 | 411.8 | 417.2 | 410 | 375.1
1248 | 1115 | 469.5 | 423.8 | 410.1 | 411.9 | 417.2 | 410 | 375.1
1249 | 1116 | 469.5 | 423.9 | 410.2 | 411.9 | 417.3 | 410 | 375.1
1250 | 1117 | 469.5 | 423.9 | 410.3 | 412 | 417.3 | 410 | 375.1
1251 | 1118 | 469.5 | 423.9 | 410.3 | 412 | 417.3 | 410 | 375.1
1252 | 1119 | 469.4 | 424 | 410.4 | 412.1 | 417.4 | 410 | 375.2
1253 | 1120 | 469.5 | 424 | 410.4 | 412.1 | 417.4 | 410 | 375.2
1254 | 1121 | 469.6 | 424.1 | 410.5 | 412.2 | 417.5 | 410.1 | 375.2
1255 | 1122 | 469.7 | 424.1 | 410.6 | 412.2 | 417.5 | 410.1 | 375.2
1256 | 1123 | 469.9 | 424.2 | 410.6 | 412.3 | 417.6 | 410.1 | 375.2
1257 | 1124 | 469.9 | 424.2 | 410.7 | 412.4 | 417.7 | 410.1 | 375.2
1258 | 1125 | 469.8 | 424.2 | 410.7 | 412.4 | 417.8 | 410.2 | 375.1
1259 | 1126 | 469.9 | 424.2 | 410.8 | 412.5 | 417.8 | 410.2 | 375.2
1260 | 1127 | 469.8 | 424.2 | 410.8 | 412.5 | 417.8 | 410.2 | 375.1
1261 | 1128 | 469.9 | 424.3 | 410.9 | 412.6 | 417.9 | 410.2 | 375
1262 | 1129 | 469.9 | 424.3 | 410.9 | 412.6 | 417.9 | 410.2 | 375
1263 | 1130 | 470 | 424.4 | 411 | 412.7 | 418 | 410.2 | 374.9
1264 | 1131 | 469.9 | 424.4 | 411 | 412.8 | 418 | 410.2 | 374.9
1265 | 1132 | 469.7 | 424.4 | 411.1 | 412.8 | 418 | 410.3 | 374.9
1266 | 1133 | 469.7 | 424.5 | 411.1 | 412.9 | 418 | 410.3 | 374.7
1267 | 1134 | 469.7 | 424.5 | 411.2 | 412.9 | 418 | 410.3 | 374.7
1268 | 1135 | 469.7 | 424.5 | 411.3 | 413 | 418 | 410.3 | 374.7
1269 | 1136 | 469.6 | 424.6 | 411.3 | 413.1 | 418 | 410.3 | 374.6
1270 | 1137 | 469.6 | 424.6 | 411.4 | 413.1 | 418 | 410.4 | 374.6
1271 | 1138 | 469.5 | 424.7 | 411.4 | 413.2 | 418 | 410.4 | 374.7
1272 | 1139 | 469.4 | 424.7 | 411.5 | 413.2 | 418 | 410.4 | 374.7
1273 | 1140 | 469.3 | 424.8 | 411.5 | 413.3 | 418 | 410.4 | 374.6
1274 | 1141 | 469.3 | 424.8 | 411.5 | 413.4 | 418.1 | 410.4 | 374.6
1275 | 1142 | 469.2 | 424.8 | 411.6 | 413.4 | 418.1 | 410.4 | 374.5
1276 | 1143 | 469.1 | 424.9 | 411.6 | 413.5 | 418.1 | 410.4 | 374.5
1277 | 1144 | 469.1 | 425 | 411.6 | 413.6 | 418.1 | 410.5 | 374.4
1278 | 1145 | 469 | 425 | 411.7 | 413.6 | 418.1 | 410.5 | 374.4
1279 | 1146 | 469.1 | 425.1 | 411.7 | 413.7 | 418.2 | 410.5 | 374.4
1280 | 1147 | 469.2 | 425.1 | 411.8 | 413.7 | 418.2 | 410.5 | 374.3
1281 | 1148 | 469.3 | 425.1 | 411.9 | 413.8 | 418.2 | 410.5 | 374.3
1282 | 1149 | 469.4 | 425.2 | 411.9 | 413.9 | 418.2 | 410.5 | 374.3
1283 | 1150 | 469.4 | 425.1 | 411.9 | 413.9 | 418.2 | 410.5 | 374.4
1284 | 1151 | 469.5 | 425.1 | 411.9 | 414 | 418.3 | 410.5 | 374.5
1285 | 1152 | 469.4 | 425.1 | 412 | 414 | 418.3 | 410.6 | 374.5
1286 | 1153 | 469.4 | 425.1 | 412.1 | 414.1 | 418.3 | 410.6 | 374.5
1287 | 1154 | 469.5 | 425.1 | 412.1 | 414.1 | 418.3 | 410.6 | 374.5
1288 | 1155 | 469.6 | 425.1 | 412.2 | 414.2 | 418.3 | 410.6 | 374.6
1289 | 1156 | 469.8 | 425.2 | 412.2 | 414.2 | 418.3 | 410.7 | 374.6
1290 | 1157 | 469.8 | 425.2 | 412.3 | 414.3 | 418.3 | 410.7 | 374.6
1291 | 1158 | 469.8 | 425.2 | 412.4 | 414.3 | 418.2 | 410.7 | 374.6
1292 | 1159 | 469.9 | 425.3 | 412.4 | 414.4 | 418.2 | 410.8 | 374.6
1293 | 1160 | 470 | 425.3 | 412.5 | 414.4 | 418.2 | 410.8 | 374.6
1294 | 1161 | 470.1 | 425.4 | 412.5 | 414.5 | 418.2 | 410.8 | 374.6
1295 | 1162 | 470.2 | 425.5 | 412.6 | 414.5 | 418.2 | 410.9 | 374.6
1296 | 1163 | 470.2 | 425.5 | 412.6 | 414.6 | 418.2 | 410.9 | 374.7
1297 | 1164 | 470.1 | 425.5 | 412.7 | 414.6 | 418.2 | 411 | 374.7
1298 | 1165 | 470.1 | 425.6 | 412.7 | 414.7 | 418.2 | 411 | 374.7
1299 | 1166 | 470 | 425.6 | 412.7 | 414.7 | 418.2 | 411 | 374.7
1300 | 1167 | 470.1 | 425.7 | 412.8 | 414.8 | 418.2 | 411 | 374.7
1301 | 1168 | 470.1 | 425.8 | 412.9 | 414.8 | 418.2 | 411 | 374.7
1302 | 1169 | 470 | 425.7 | 412.9 | 414.8 | 418.2 | 411 | 374.7
1303 | 1170 | 470 | 425.6 | 413 | 414.9 | 418.2 | 411 | 374.7
1304 | 1171 | 469.9 | 425.6 | 413 | 415 | 418.3 | 411.1 | 374.8
1305 | 1172 | 469.9 | 425.6 | 413.1 | 415 | 418.3 | 411.1 | 374.7
1306 | 1173 | 469.9 | 425.6 | 413.1 | 415.1 | 418.3 | 411.1 | 374.7
1307 | 1174 | 469.9 | 425.7 | 413.2 | 415.1 | 418.3 | 411.1 | 374.7
1308 | 1175 | 469.8 | 425.7 | 413.2 | 415.2 | 418.3 | 411.1 | 374.6
1309 | 1176 | 469.7 | 425.7 | 413.3 | 415.2 | 418.4 | 411.1 | 374.5
1310 | 1177 | 469.6 | 425.8 | 413.3 | 415.3 | 418.4 | 411.1 | 374.5
1311 | 1178 | 469.5 | 425.8 | 413.4 | 415.3 | 418.4 | 411.1 | 374.4
1312 | 1179 | 469.4 | 425.9 | 413.4 | 415.4 | 418.4 | 411.2 | 374.4
1313 | 1180 | 469.4 | 425.9 | 413.5 | 415.4 | 418.4 | 411.2 | 374.4
1314 | 1181 | 469.3 | 425.9 | 413.5 | 415.5 | 418.5 | 411.2 | 374.4
1315 | 1182 | 469.3 | 426 | 413.5 | 415.5 | 418.5 | 411.2 | 374.5
1316 | 1183 | 469.2 | 426 | 413.6 | 415.6 | 418.5 | 411.3 | 374.4
1317 | 1184 | 469.2 | 426 | 413.6 | 415.7 | 418.5 | 411.3 | 374.5
1318 | 1185 | 469.2 | 426.1 | 413.7 | 415.7 | 418.5 | 411.3 | 374.5
1319 | 1186 | 469.3 | 426.1 | 413.7 | 415.8 | 418.5 | 411.3 | 374.5
1320 | 1187 | 469.3 | 426.1 | 413.8 | 415.8 | 418.5 | 411.3 | 374.5
1321 | 1188 | 469.3 | 426.2 | 413.8 | 415.9 | 418.6 | 411.3 | 374.6
1322 | 1189 | 469.5 | 426.2 | 413.9 | 415.9 | 418.6 | 411.3 | 374.5
1323 | 1190 | 469.5 | 426.3 | 413.9 | 416 | 418.6 | 411.3 | 374.5
1324 | 1191 | 469.5 | 426.3 | 414 | 416 | 418.6 | 411.4 | 374.5
1325 | 1192 | 469.5 | 426.4 | 414 | 416.1 | 418.7 | 411.4 | 374.6
1326 | 1193 | 469.4 | 426.4 | 414 | 416.1 | 418.7 | 411.4 | 374.5
1327 | 1194 | 469.3 | 426.5 | 414.1 | 416.2 | 418.7 | 411.4 | 374.5
1328 | 1195 | 469.3 | 426.6 | 414.1 | 416.2 | 418.8 | 411.4 | 374.5
1329 | 1196 | 469.4 | 426.6 | 414.2 | 416.3 | 418.8 | 411.4 | 374.4
1330 | 1197 | 469.3 | 426.7 | 414.2 | 416.4 | 418.8 | 411.4 | 374.4
1331 | 1198 | 469.2 | 426.7 | 414.3 | 416.4 | 418.8 | 411.4 | 374.4
1332 | 1199 | 469.3 | 426.7 | 414.5 | 416.4 | 418.5 | 411.4 | 374.5
1333 | 1200 | 469.3 | 426.8 | 414.6 | 416.4 | 418.5 | 411.4 | 374.5
1334 | 1201 | 469.4 | 426.8 | 414.6 | 416.5 | 418.6 | 411.4 | 374.5
1335 | 1202 | 469.4 | 426.9 | 414.6 | 416.5 | 418.6 | 411.4 | 374.5
1336 | 1203 | 469.4 | 426.9 | 414.7 | 416.6 | 418.7 | 411.4 | 374.5
1337 | 1204 | 469.5 | 427 | 414.7 | 416.6 | 418.8 | 411.4 | 374.5
1338 | 1205 | 469.6 | 427.1 | 414.7 | 416.7 | 418.8 | 411.4 | 374.5
1339 | 1206 | 469.6 | 427.1 | 414.8 | 416.7 | 418.9 | 411.4 | 374.6
1340 | 1207 | 469.7 | 427.1 | 414.8 | 416.8 | 418.9 | 411.5 | 374.6
1341 | 1208 | 469.8 | 427.1 | 414.9 | 416.8 | 419 | 411.5 | 374.6
1342 | 1209 | 470 | 427.2 | 414.9 | 416.9 | 419.1 | 411.5 | 374.6
1343 | 1210 | 470.1 | 427.2 | 415 | 417 | 419.2 | 411.5 | 374.5
1344 | 1211 | 470.2 | 427.3 | 415 | 417 | 419.3 | 411.5 | 374.5
1345 | 1212 | 470.2 | 427.4 | 415 | 417.1 | 419.3 | 411.5 | 374.6
1346 | 1213 | 470.3 | 427.4 | 415.1 | 417.1 | 419.4 | 411.5 | 374.7
1347 | 1214 | 470.5 | 427.5 | 415.1 | 417.2 | 419.5 | 411.6 | 374.7
1348 | 1215 | 470.7 | 427.5 | 415.2 | 417.2 | 419.6 | 411.6 | 374.8
1349 | 1216 | 470.9 | 427.6 | 415.3 | 417.3 | 419.6 | 411.6 | 374.8
1350 | 1217 | 471.1 | 427.6 | 415.3 | 417.3 | 419.6 | 411.7 | 374.8
1351 | 1218 | 471.3 | 427.6 | 415.4 | 417.4 | 419.7 | 411.7 | 374.9
1352 | 1219 | 471.5 | 427.6 | 415.5 | 417.4 | 419.7 | 411.8 | 374.9
1353 | 1220 | 471.6 | 427.6 | 415.6 | 417.4 | 419.7 | 411.8 | 374.9
1354 | 1221 | 471.7 | 427.6 | 415.6 | 417.5 | 419.8 | 411.8 | 375
1355 | 1222 | 471.8 | 427.7 | 415.7 | 417.5 | 419.8 | 411.8 | 375
1356 | 1223 | 471.8 | 427.7 | 415.7 | 417.6 | 419.8 | 411.8 | 375.1
1357 | 1224 | 471.8 | 427.8 | 415.7 | 417.6 | 419.9 | 411.8 | 375.1
1358 | 1225 | 471.7 | 427.9 | 415.8 | 417.7 | 419.9 | 411.9 | 375.3
1359 | 1226 | 471.6 | 427.9 | 415.8 | 417.7 | 420 | 411.9 | 375.3
1360 | 1227 | 471.5 | 428 | 415.9 | 417.8 | 420 | 412 | 375.4
1361 | 1228 | 471.3 | 428 | 415.9 | 417.8 | 420 | 412 | 375.4
1362 | 1229 | 471.4 | 428.1 | 416 | 417.9 | 420.1 | 412 | 375.5
1363 | 1230 | 471.4 | 428.1 | 416 | 418 | 420.1 | 412 | 375.6
1364 | 1231 | 471.3 | 428.2 | 416 | 418 | 420.1 | 412.1 | 375.6
1365 | 1232 | 471.5 | 428.2 | 416.1 | 418.1 | 420.2 | 412.1 | 375.7
1366 | 1233 | 471.6 | 428.3 | 416.1 | 418.1 | 420.2 | 412.2 | 375.8
1367 | 1234 | 471.5 | 428.3 | 416.2 | 418.2 | 420.3 | 412.2 | 375.8
1368 | 1235 | 471.6 | 428.3 | 416.4 | 418.2 | 420.2 | 412.2 | 375.8
1369 | 1236 | 471.5 | 428.3 | 416.4 | 418.2 | 420.2 | 412.3 | 375.8
1370 | 1237 | 471.5 | 428.3 | 416.5 | 418.3 | 420.2 | 412.3 | 375.8
1371 | 1238 | 471.3 | 428.4 | 416.5 | 418.3 | 420.3 | 412.4 | 375.8
1372 | 1239 | 471.1 | 428.4 | 416.6 | 418.4 | 420.3 | 412.4 | 375.8
1373 | 1240 | 471 | 428.4 | 416.6 | 418.4 | 420.4 | 412.4 | 375.9
1374 | 1241 | 471.2 | 428.4 | 416.6 | 418.5 | 420.4 | 412.4 | 375.8
1375 | 1242 | 471.2 | 428.4 | 416.7 | 418.6 | 420.4 | 412.5 | 375.8
1376 | 1243 | 471.3 | 428.4 | 416.7 | 418.6 | 420.4 | 412.5 | 375.8
1377 | 1244 | 471.2 | 428.4 | 416.7 | 418.7 | 420.5 | 412.5 | 375.8
1378 | 1245 | 471.1 | 428.5 | 416.8 | 418.7 | 420.5 | 412.5 | 375.8
1379 | 1246 | 470.9 | 428.6 | 416.8 | 418.8 | 420.6 | 412.5 | 375.9
1380 | 1247 | 470.8 | 428.6 | 416.8 | 418.8 | 420.6 | 412.5 | 375.9
1381 | 1248 | 470.6 | 428.6 | 416.9 | 418.9 | 420.6 | 412.5 | 375.9
1382 | 1249 | 470.5 | 428.7 | 416.9 | 418.9 | 420.6 | 412.5 | 375.8
1383 | 1250 | 470.5 | 428.7 | 417 | 419 | 420.6 | 412.5 | 375.8
1384 | 1251 | 470.5 | 428.7 | 417 | 419 | 420.6 | 412.6 | 375.7
1385 | 1252 | 470.6 | 428.7 | 417 | 419.1 | 420.6 | 412.6 | 375.7
1386 | 1253 | 470.6 | 428.8 | 417.1 | 419.1 | 420.6 | 412.6 | 375.7
1387 | 1254 | 470.6 | 428.9 | 417.1 | 419.2 | 420.6 | 412.6 | 375.7
1388 | 1255 | 470.7 | 428.9 | 417.1 | 419.2 | 420.6 | 412.6 | 375.7
1389 | 1256 | 470.8 | 428.9 | 417.2 | 419.3 | 420.6 | 412.6 | 375.8
1390 | 1257 | 470.9 | 428.9 | 417.2 | 419.3 | 420.6 | 412.6 | 375.8
1391 | 1258 | 470.9 | 429 | 417.3 | 419.4 | 420.6 | 412.6 | 375.9
1392 | 1259 | 471 | 428.9 | 417.3 | 419.4 | 420.6 | 412.7 | 375.9
1393 | 1260 | 471 | 429 | 417.4 | 419.5 | 420.6 | 412.7 | 375.9
1394 | 1261 | 470.9 | 429 | 417.4 | 419.5 | 420.6 | 412.7 | 376
1395 | 1262 | 470.8 | 429.1 | 417.5 | 419.5 | 420.6 | 412.7 | 376
1396 | 1263 | 470.8 | 429.1 | 417.5 | 419.6 | 420.6 | 412.7 | 376.1
1397 | 1264 | 470.7 | 429.1 | 417.6 | 419.6 | 420.6 | 412.7 | 376.1
1398 | 1265 | 470.6 | 429.1 | 417.6 | 419.7 | 420.6 | 412.7 | 376.1
1399 | 1266 | 470.6 | 429.2 | 417.6 | 419.7 | 420.6 | 412.7 | 376.2
1400 | 1267 | 470.6 | 429.3 | 417.6 | 419.8 | 420.6 | 412.8 | 376.1
1401 | 1268 | 470.5 | 429.3 | 417.7 | 419.8 | 420.6 | 412.8 | 376.1
1402 | 1269 | 470.5 | 429.3 | 417.7 | 419.9 | 420.6 | 412.8 | 376.1
1403 | 1270 | 470.7 | 429.3 | 417.8 | 419.9 | 420.6 | 412.8 | 376.1
1404 | 1271 | 470.7 | 429.3 | 417.8 | 419.9 | 420.6 | 412.8 | 376.2
1405 | 1272 | 470.6 | 429.3 | 417.9 | 420 | 420.7 | 412.9 | 376.2
1406 | 1273 | 470.8 | 429.3 | 417.9 | 420 | 420.7 | 412.9 | 376.2
1407 | 1274 | 470.9 | 429.3 | 418 | 420 | 420.7 | 412.9 | 376.2
1408 | 1275 | 470.9 | 429.3 | 418.1 | 420.1 | 420.7 | 412.9 | 376.3
1409 | 1276 | 470.9 | 429.3 | 418.1 | 420.1 | 420.7 | 413 | 376.2
1410 | 1277 | 471 | 429.3 | 418.2 | 420.1 | 420.7 | 413 | 376.3
1411 | 1278 | 471.2 | 429.3 | 418.3 | 420.2 | 420.7 | 413 | 376.2
1412 | 1279 | 471.1 | 429.3 | 418.3 | 420.2 | 420.7 | 413 | 376.1
1413 | 1280 | 471 | 429.3 | 418.3 | 420.3 | 420.8 | 413 | 376.1
1414 | 1281 | 470.8 | 429.4 | 418.4 | 420.3 | 420.8 | 413.1 | 376.1
1415 | 1282 | 470.8 | 429.5 | 418.5 | 420.3 | 420.8 | 413.1 | 376
1416 | 1283 | 470.8 | 429.5 | 418.5 | 420.4 | 420.8 | 413.1 | 376
1417 | 1284 | 470.8 | 429.5 | 418.5 | 420.4 | 420.8 | 413.1 | 376
1418 | 1285 | 470.7 | 429.5 | 418.6 | 420.5 | 420.9 | 413.1 | 376
1419 | 1286 | 470.6 | 429.6 | 418.6 | 420.5 | 420.9 | 413.2 | 376
1420 | 1287 | 470.4 | 429.6 | 418.6 | 420.6 | 421 | 413.2 | 376
1421 | 1288 | 470.4 | 429.6 | 418.7 | 420.6 | 421 | 413.2 | 376
1422 | 1289 | 470.4 | 429.7 | 418.7 | 420.6 | 421 | 413.2 | 376
1423 | 1290 | 470.4 | 429.7 | 418.8 | 420.7 | 421.1 | 413.3 | 376
1424 | 1291 | 470.4 | 429.7 | 418.8 | 420.7 | 421.2 | 413.3 | 376
1425 | 1292 | 470.5 | 429.7 | 418.9 | 420.8 | 421.2 | 413.3 | 375.9
1426 | 1293 | 470.7 | 429.7 | 419 | 420.8 | 421.2 | 413.3 | 375.9
1427 | 1294 | 470.8 | 429.7 | 419 | 420.8 | 421.2 | 413.4 | 376
1428 | 1295 | 470.8 | 429.8 | 419.1 | 420.9 | 421.2 | 413.4 | 376
1429 | 1296 | 470.9 | 429.8 | 419.2 | 420.9 | 421.2 | 413.4 | 376
1430 | 1297 | 470.9 | 429.8 | 419.2 | 420.9 | 421.2 | 413.4 | 376
1431 | 1298 | 470.9 | 429.8 | 419.2 | 421 | 421.2 | 413.4 | 376
1432 | 1299 | 470.7 | 429.8 | 419.3 | 421 | 421.2 | 413.4 | 376.1
1433 | 1300 | 470.6 | 429.8 | 419.4 | 421 | 421.2 | 413.4 | 376.1
1434 | 1301 | 470.6 | 429.9 | 419.4 | 421 | 421.2 | 413.4 | 376.1
1435 | 1302 | 470.6 | 429.9 | 419.5 | 421.1 | 421.2 | 413.4 | 376
1436 | 1303 | 470.6 | 430 | 419.5 | 421.1 | 421.2 | 413.5 | 376.1
1437 | 1304 | 470.6 | 430 | 419.6 | 421.2 | 421.2 | 413.5 | 376.1
1438 | 1305 | 470.6 | 430 | 419.6 | 421.2 | 421.2 | 413.5 | 376.1
1439 | 1306 | 470.6 | 430 | 419.7 | 421.2 | 421.2 | 413.5 | 376.1
1440 | 1307 | 470.5 | 430 | 419.7 | 421.3 | 421.2 | 413.5 | 376.1
1441 | 1308 | 470.3 | 430.1 | 419.7 | 421.3 | 421.3 | 413.5 | 376.1
1442 | 1309 | 470.2 | 430.2 | 419.8 | 421.4 | 421.3 | 413.5 | 376.1
1443 | 1310 | 470.1 | 430.2 | 419.8 | 421.4 | 421.3 | 413.6 | 376.1
1444 | 1311 | 470.1 | 430.3 | 419.9 | 421.5 | 421.4 | 413.6 | 376.1
1445 | 1312 | 470.1 | 430.3 | 419.9 | 421.5 | 421.4 | 413.6 | 376.1
1446 | 1313 | 470.1 | 430.3 | 420 | 421.5 | 421.4 | 413.6 | 376.2
1447 | 1314 | 470.4 | 430.4 | 420.1 | 421.5 | 421.4 | 413.6 | 376.4 | Time of first failure
1448 | 1315 | 470.4 | 430.4 | 420.1 | 421.5 | 421.4 | 413.7 | 376.4 | 1314 | 0
1449 | 1316 | 470.4 | 430.5 | 420.2 | 421.6 | 421.4 | 413.7 | 376.5 | 1314 | 900
1450 | 1317 | 470.4 | 430.4 | 420.2 | 421.6 | 421.4 | 413.7 | 376.5
1451 | 1318 | 470.5 | 430.5 | 420.3 | 421.6 | 421.5 | 413.7 | 376.5
1452 | 1319 | 470.6 | 430.6 | 420.3 | 421.6 | 421.5 | 413.7 | 376.6
1453 | 1320 | 470.7 | 430.6 | 420.4 | 421.6 | 421.5 | 413.7 | 376.6
1454 | 1321 | 470.8 | 430.6 | 420.4 | 421.6 | 421.6 | 413.7 | 376.6
1455 | 1322 | 470.8 | 430.6 | 420.5 | 421.6 | 421.6 | 413.7 | 376.7
1456 | 1323 | 470.8 | 430.5 | 420.6 | 421.6 | 421.6 | 413.8 | 376.7
1457 | 1324 | 470.9 | 430.6 | 420.6 | 421.6 | 421.6 | 413.8 | 376.8
1458 | 1325 | 471 | 430.7 | 420.7 | 421.6 | 421.7 | 413.8 | 376.8
1459 | 1326 | 471.1 | 430.8 | 420.8 | 421.6 | 421.7 | 413.9 | 376.8
1460 | 1327 | 471 | 430.9 | 420.8 | 421.6 | 421.8 | 413.9 | 376.9
1461 | 1328 | 471.1 | 431 | 420.9 | 421.6 | 421.8 | 413.9 | 377
1462 | 1329 | 471 | 430.9 | 421 | 421.6 | 421.9 | 414 | 376.9
1463 | 1330 | 471 | 430.9 | 421 | 421.6 | 422 | 414 | 376.9
1464 | 1331 | 471 | 431 | 421.1 | 421.6 | 422.1 | 414 | 377
1465 | 1332 | 470.9 | 431 | 421.1 | 421.7 | 422.1 | 414.1 | 377
1466 | 1333 | 470.8 | 431.1 | 421.2 | 421.7 | 422.2 | 414.1 | 377
1467 | 1334 | 470.8 | 431.1 | 421.3 | 421.7 | 422.3 | 414.2 | 377
1468 | 1335 | 470.9 | 431.1 | 421.4 | 421.7 | 422.3 | 414.2 | 377
1469 | 1336 | 471 | 431.2 | 421.4 | 421.7 | 422.4 | 414.2 | 377
1470 | 1337 | 471.2 | 431.2 | 421.5 | 421.7 | 422.4 | 414.2 | 377
1471 | 1338 | 471.3 | 431.2 | 421.6 | 421.7 | 422.5 | 414.2 | 377
1472 | 1339 | 471.3 | 431.2 | 421.7 | 421.7 | 422.6 | 414.2 | 377.1
1473 | 1340 | 471.3 | 431.2 | 421.8 | 421.7 | 422.6 | 414.2 | 377.1
1474 | 1341 | 471.4 | 431.2 | 421.8 | 421.7 | 422.7 | 414.2 | 377
1475 | 1342 | 471.4 | 431.3 | 421.9 | 421.7 | 422.7 | 414.3 | 377.1
1476 | 1343 | 471.6 | 431.3 | 422 | 421.8 | 422.8 | 414.3 | 377.1
1477 | 1344 | 471.8 | 431.4 | 422 | 421.8 | 422.8 | 414.3 | 377.1
1478 | 1345 | 471.9 | 431.4 | 422.1 | 421.8 | 422.8 | 414.4 | 377.2
1479 | 1346 | 472 | 431.4 | 422.2 | 421.8 | 422.8 | 414.4 | 377.2
1480 | 1347 | 472.1 | 431.4 | 422.4 | 421.8 | 422.6 | 414.4 | 377.2
1481 | 1348 | 472.1 | 431.4 | 422.5 | 421.8 | 422.6 | 414.5 | 377.2
1482 | 1349 | 472.1 | 431.4 | 422.6 | 421.8 | 422.6 | 414.5 | 377.2
1483 | 1350 | 472.1 | 431.2 | 422.9 | 421.7 | 422.4 | 414.6 | 377.2
1484 | 1351 | 472.2 | 431.2 | 423.1 | 421.7 | 422.3 | 414.6 | 377.2
1485 | 1352 | 472.2 | 431.2 | 423.2 | 421.7 | 422.4 | 414.6 | 377.2
1486 | 1353 | 472.3 | 431.4 | 423.2 | 421.8 | 422.5 | 414.7 | 377.3
1487 | 1354 | 472.3 | 431.4 | 423.3 | 421.8 | 422.5 | 414.7 | 377.3
1488 | 1355 | 472.4 | 431.4 | 423.3 | 421.8 | 422.6 | 414.7 | 377.3
1489 | 1356 | 472.4 | 431.4 | 423.4 | 421.8 | 422.6 | 414.8 | 377.3
1490 | 1357 | 472.2 | 431.5 | 423.5 | 421.8 | 422.7 | 414.8 | 377.4
1491 | 1358 | 472.3 | 431.5 | 423.5 | 421.9 | 422.7 | 414.8 | 377.4
1492 | 1359 | 472.4 | 431.4 | 423.6 | 421.9 | 422.8 | 414.9 | 377.5
1493 | 1360 | 472.5 | 431.4 | 423.6 | 421.9 | 422.9 | 414.9 | 377.5
1494 | 1361 | 472.5 | 431.4 | 423.7 | 422 | 423 | 414.9 | 377.5
1495 | 1362 | 472.4 | 431.4 | 423.7 | 422 | 423 | 414.9 | 377.6
1496 | 1363 | 472.4 | 431.4 | 423.7 | 422.1 | 423.1 | 415 | 377.5
1497 | 1364 | 472.4 | 431.4 | 423.8 | 422.1 | 423.2 | 415 | 377.6
1498 | 1365 | 472.4 | 431.5 | 423.8 | 422.1 | 423.3 | 415 | 377.7
1499 | 1366 | 472.4 | 431.7 | 423.8 | 422.2 | 423.4 | 415.1 | 377.7
1500 | 1367 | 472.4 | 431.8 | 423.9 | 422.2 | 423.4 | 415.1 | 377.7
1501 | 1368 | 472.4 | 431.8 | 424 | 422.3 | 423.5 | 415.1 | 377.7
1502 | 1369 | 472.4 | 431.8 | 424 | 422.3 | 423.6 | 415.2 | 377.7
1503 | 1370 | 472.3 | 431.8 | 424 | 422.4 | 423.7 | 415.2 | 377.7
1504 | 1371 | 472.4 | 431.9 | 424.1 | 422.5 | 423.8 | 415.2 | 377.8
1505 | 1372 | 472.5 | 432 | 424.1 | 422.6 | 423.9 | 415.2 | 377.7
1506 | 1373 | 472.5 | 432 | 424.1 | 422.7 | 423.9 | 415.3 | 377.7
1507 | 1374 | 472.5 | 432.1 | 424.2 | 422.9 | 424 | 415.3 | 377.8
1508 | 1375 | 472.5 | 432.2 | 424.2 | 422.9 | 424.1 | 415.3 | 377.8
1509 | 1376 | 472.4 | 432.3 | 424.3 | 423 | 424.1 | 415.3 | 377.8
1510 | 1377 | 472.3 | 432.3 | 424.3 | 423.1 | 424.2 | 415.3 | 377.8
1511 | 1378 | 472.3 | 432.3 | 424.3 | 423.1 | 424.3 | 415.4 | 377.7
1512 | 1379 | 472.2 | 432.3 | 424.3 | 423.2 | 424.3 | 415.4 | 377.7
1513 | 1380 | 472 | 432.3 | 424.4 | 423.3 | 424.4 | 415.4 | 377.7
1514 | 1381 | 471.9 | 432.4 | 424.4 | 423.4 | 424.4 | 415.4 | 377.7
1515 | 1382 | 471.8 | 432.4 | 424.4 | 423.4 | 424.5 | 415.4 | 377.8
1516 | 1383 | 471.8 | 432.4 | 424.5 | 423.5 | 424.5 | 415.4 | 377.7
1517 | 1384 | 471.6 | 432.4 | 424.5 | 423.6 | 424.6 | 415.4 | 377.7
1518 | 1385 | 471.5 | 432.5 | 424.5 | 423.6 | 424.6 | 415.4 | 377.7
1519 | 1386 | 471.2 | 432.5 | 424.5 | 423.7 | 424.7 | 415.4 | 377.7
1520 | 1387 | 471 | 432.5 | 424.6 | 423.8 | 424.7 | 415.4 | 377.7
1521 | 1388 | 471 | 432.5 | 424.6 | 423.9 | 424.8 | 415.5 | 377.7
1522 | 1389 | 471.1 | 432.5 | 424.7 | 423.9 | 424.8 | 415.5 | 377.7
1523 | 1390 | 471 | 432.6 | 424.7 | 424 | 424.8 | 415.5 | 377.7
1524 | 1391 | 471 | 432.7 | 424.7 | 424 | 424.9 | 415.5 | 377.7
1525 | 1392 | 470.9 | 432.7 | 424.7 | 424.1 | 424.9 | 415.5 | 377.8
1526 | 1393 | 471 | 432.8 | 424.8 | 424.1 | 424.9 | 415.5 | 377.7
1527 | 1394 | 471 | 432.9 | 424.8 | 424.2 | 424.9 | 415.5 | 377.7
1528 | 1395 | 471.1 | 433 | 424.9 | 424.2 | 424.9 | 415.5 | 377.7
1529 | 1396 | 471.1 | 433 | 424.9 | 424.3 | 424.9 | 415.5 | 377.8
1530 | 1397 | 471 | 433.1 | 425 | 424.3 | 424.9 | 415.6 | 377.8
1531 | 1398 | 471 | 433.1 | 425 | 424.3 | 424.9 | 415.6 | 377.8
1532 | 1399 | 470.9 | 433 | 425 | 424.4 | 424.9 | 415.6 | 377.9
1533 | 1400 | 470.7 | 433.1 | 425 | 424.4 | 424.9 | 415.6 | 377.9
1534 | 1401 | 470.7 | 433.1 | 425 | 424.5 | 424.8 | 415.6 | 377.9
1535 | 1402 | 470.7 | 433.2 | 425 | 424.5 | 424.8 | 415.6 | 378
1536 | 1403 | 470.6 | 433.2 | 425 | 424.5 | 424.7 | 415.6 | 378
1537 | 1404 | 470.5 | 433.2 | 425 | 424.5 | 424.7 | 415.6 | 378
1538 | 1405 | 470.4 | 433.3 | 425.1 | 424.5 | 424.6 | 415.6 | 378
1539 | 1406 | 470.4 | 433.3 | 425.2 | 424.5 | 424.6 | 415.6 | 378
1540 | 1407 | 470.3 | 433.4 | 425.2 | 424.6 | 424.5 | 415.6 | 378.1
1541 | 1408 | 470.2 | 433.5 | 425.3 | 424.6 | 424.4 | 415.6 | 378.1
1542 | 1409 | 470.2 | 433.5 | 425.4 | 424.7 | 424.3 | 415.6 | 378.2
1543 | 1410 | 470.2 | 433.7 | 425.1 | 424.9 | 424.6 | 415.6 | 378.1
1544 | 1411 | 470.2 | 433.8 | 425.1 | 425.1 | 424.6 | 415.6 | 378.1
1545 | 1412 | 470.1 | 433.8 | 425.1 | 425.1 | 424.5 | 415.6 | 378
1546 | 1413 | 470 | 433.9 | 425.1 | 425.2 | 424.3 | 415.5 | 377.9
1547 | 1414 | 469.9 | 433.9 | 425.1 | 425.2 | 424.2 | 415.5 | 377.9
1548 | 1415 | 469.9 | 434 | 425.1 | 425.2 | 424.1 | 415.5 | 377.9
1549 | 1416 | 469.8 | 434 | 425.2 | 425.2 | 424 | 415.5 | 377.8
1550 | 1417 | 469.8 | 434 | 425.2 | 425.3 | 423.9 | 415.5 | 377.8
1551 | 1418 | 469.7 | 434 | 425.2 | 425.3 | 423.8 | 415.5 | 377.8
1552 | 1419 | 469.6 | 434.1 | 425.3 | 425.3 | 423.8 | 415.5 | 377.8
1553 | 1420 | 469.7 | 434.1 | 425.3 | 425.3 | 423.7 | 415.6 | 377.8
1554 | 1421 | 469.7 | 434.2 | 425.3 | 425.4 | 423.6 | 415.6 | 377.8
1555 | 1422 | 469.9 | 434.1 | 425.4 | 425.4 | 423.5 | 415.6 | 377.8
1556 | 1423 | 469.9 | 434.2 | 425.5 | 425.4 | 423.4 | 415.6 | 377.7
1557 | 1424 | 469.9 | 434.2 | 425.5 | 425.5 | 423.3 | 415.6 | 377.7
1558 | 1425 | 470.1 | 434.3 | 425.5 | 425.5 | 423.3 | 415.6 | 377.7
1559 | 1426 | 470 | 434.4 | 425.6 | 425.5 | 423.2 | 415.6 | 377.7
1560 | 1427 | 469.9 | 434.4 | 425.6 | 425.5 | 423.2 | 415.6 | 377.8
1561 | 1428 | 470 | 434.5 | 425.7 | 425.6 | 423.2 | 415.6 | 377.8
1562 | 1429 | 470 | 434.6 | 425.7 | 425.6 | 423.1 | 415.7 | 377.8
1563 | 1430 | 470.1 | 434.7 | 425.7 | 425.7 | 423 | 415.6 | 377.7
1564 | 1431 | 470.2 | 434.7 | 425.7 | 425.7 | 423 | 415.7 | 377.7
1565 | 1432 | 470.3 | 434.8 | 425.7 | 425.7 | 422.9 | 415.7 | 377.7
1566 | 1433 | 470.3 | 434.8 | 425.8 | 425.7 | 422.9 | 415.7 | 377.7
1567 | 1434 | 470.2 | 434.9 | 425.8 | 425.7 | 422.9 | 415.7 | 377.7
1568 | 1435 | 470.2 | 434.9 | 425.9 | 425.8 | 422.9 | 415.7 | 377.7
1569 | 1436 | 470.2 | 435 | 425.9 | 425.8 | 422.9 | 415.8 | 377.7
1570 | 1437 | 470.3 | 435 | 426 | 425.8 | 422.9 | 415.8 | 377.7
1571 | 1438 | 470.4 | 435.1 | 426 | 425.8 | 423 | 415.8 | 377.7
1572 | 1439 | 470.3 | 435.2 | 426 | 425.8 | 423.1 | 415.8 | 377.8
1573 | 1440 | 470.3 | 435.2 | 426 | 425.8 | 423.2 | 415.8 | 377.8
1574 | 1441 | 470.3 | 435.3 | 426.1 | 425.8 | 423.3 | 415.8 | 377.7
1575 | 1442 | 470.4 | 435.4 | 426.1 | 425.8 | 423.4 | 415.8 | 377.7
1576 | 1443 | 470.5 | 435.4 | 426.1 | 425.8 | 423.5 | 415.8 | 377.7
1577 | 1444 | 470.4 | 435.5 | 426.1 | 425.8 | 423.6 | 415.8 | 377.6
1578 | 1445 | 470.4 | 435.5 | 426.2 | 425.7 | 423.6 | 415.8 | 377.6
1579 | 1446 | 470.3 | 435.6 | 426.2 | 425.6 | 423.6 | 415.8 | 377.6
1580 | 1447 | 470.4 | 435.6 | 426.3 | 425.6 | 423.7 | 415.8 | 377.6
1581 | 1448 | 470.4 | 435.7 | 426.3 | 425.6 | 423.8 | 415.8 | 377.6
1582 | 1449 | 470.5 | 435.7 | 426.4 | 425.6 | 423.9 | 415.8 | 377.6
1583 | 1450 | 470.7 | 435.8 | 426.4 | 425.7 | 424 | 415.9 | 377.6
1584 | 1451 | 470.8 | 435.9 | 426.4 | 425.7 | 424 | 415.9 | 377.6
1585 | 1452 | 470.9 | 435.9 | 426.5 | 425.8 | 424 | 416 | 377.7
1586 | 1453 | 470.9 | 436 | 426.5 | 425.8 | 424.1 | 416 | 377.7
1587 | 1454 | 470.9 | 436 | 426.5 | 425.8 | 424.2 | 416 | 377.8
1588 | 1455 | 470.9 | 436.1 | 426.6 | 425.8 | 424.3 | 416 | 377.8
1589 | 1456 | 471 | 436.1 | 426.6 | 425.9 | 424.3 | 416 | 377.8
1590 | 1457 | 471 | 436.2 | 426.6 | 425.9 | 424.3 | 416.1 | 377.8
1591 | 1458 | 470.9 | 436.2 | 426.7 | 425.9 | 424.4 | 416.1 | 377.9
1592 | 1459 | 470.9 | 436.2 | 426.7 | 425.9 | 424.6 | 416.1 | 378
1593 | 1460 | 470.9 | 436.2 | 426.7 | 426 | 424.6 | 416.1 | 377.9
1594 | 1461 | 470.9 | 436.3 | 426.8 | 426 | 424.7 | 416.2 | 377.9
1595 | 1462 | 470.9 | 436.3 | 426.8 | 426.1 | 424.7 | 416.2 | 377.9
1596 | 1463 | 471 | 436.4 | 426.9 | 426.2 | 424.7 | 416.2 | 377.8
1597 | 1464 | 471 | 436.4 | 426.9 | 426.2 | 424.8 | 416.2 | 377.8
1598 | 1465 | 471 | 436.4 | 426.9 | 426.2 | 424.9 | 416.2 | 378
1599 | 1466 | 471 | 436.5 | 426.9 | 426.2 | 425 | 416.2 | 378.1
1600 | 1467 | 471 | 436.5 | 426.9 | 426.2 | 425.1 | 416.2 | 378.2
1601 | 1468 | 471 | 436.6 | 427 | 426.2 | 425.1 | 416.3 | 378.2
1602 | 1469 | 471 | 436.7 | 427 | 426.1 | 425.1 | 416.3 | 378.3
1603 | 1470 | 470.8 | 436.7 | 427.1 | 426.1 | 425.2 | 416.3 | 378.3
1604 | 1471 | 470.6 | 436.8 | 427.1 | 426 | 425.2 | 416.4 | 378.3
1605 | 1472 | 470.6 | 436.8 | 427.2 | 426.1 | 425.3 | 416.4 | 378.4
1606 | 1473 | 470.6 | 436.9 | 427.2 | 426.1 | 425.5 | 416.4 | 378.4
1607 | 1474 | 470.5 | 437 | 427.2 | 426.1 | 425.6 | 416.4 | 378.4
1608 | 1475 | 470.7 | 437 | 427.2 | 426.2 | 425.7 | 416.4 | 378.4
1609 | 1476 | 470.8 | 437.1 | 427.3 | 426.2 | 425.7 | 416.4 | 378.4
1610 | 1477 | 470.9 | 437.1 | 427.3 | 426.2 | 425.7 | 416.4 | 378.4
1611 | 1478 | 470.9 | 437.1 | 427.4 | 426.2 | 425.7 | 416.4 | 378.5
1612 | 1479 | 470.8 | 437.1 | 427.4 | 426.2 | 425.7 | 416.5 | 378.6
1613 | 1480 | 470.8 | 437.2 | 427.5 | 426.3 | 425.7 | 416.5 | 378.6
1614 | 1481 | 470.9 | 437.2 | 427.5 | 426.3 | 425.7 | 416.5 | 378.6
1615 | 1482 | 471 | 437.2 | 427.5 | 426.4 | 425.9 | 416.6 | 378.6
1616 | 1483 | 470.9 | 437.3 | 427.5 | 426.4 | 426 | 416.6 | 378.6
1617 | 1484 | 470.9 | 437.3 | 427.5 | 426.4 | 426.1 | 416.6 | 378.6
1618 | 1485 | 470.8 | 437.4 | 427.5 | 426.4 | 426.2 | 416.6 | 378.6
1619 | 1486 | 470.8 | 437.4 | 427.4 | 426.4 | 426.3 | 416.6 | 378.6
1620 | 1487 | 470.9 | 437.4 | 427.4 | 426.4 | 426.4 | 416.6 | 378.6
1621 | 1488 | 471.1 | 437.4 | 427.4 | 426.4 | 426.4 | 416.6 | 378.5
1622 | 1489 | 471.2 | 437.5 | 427.4 | 426.5 | 426.5 | 416.7 | 378.6
1623 | 1490 | 471 | 437.5 | 427.5 | 426.5 | 426.6 | 416.7 | 378.6
1624 | 1491 | 471 | 437.6 | 427.5 | 426.6 | 426.7 | 416.7 | 378.6
1625 | 1492 | 471 | 437.6 | 427.5 | 426.6 | 426.7 | 416.7 | 378.6
1626 | 1493 | 470.9 | 437.6 | 427.6 | 426.7 | 426.8 | 416.8 | 378.7
1627 | 1494 | 470.8 | 437.7 | 427.6 | 426.7 | 426.8 | 416.8 | 378.6
1628 | 1495 | 470.8 | 437.7 | 427.6 | 426.7 | 426.9 | 416.8 | 378.6
1629 | 1496 | 470.8 | 437.7 | 427.6 | 426.7 | 427.1 | 416.8 | 378.6
1630 | 1497 | 470.8 | 437.7 | 427.6 | 426.8 | 427.2 | 416.8 | 378.6
1631 | 1498 | 470.8 | 437.7 | 427.6 | 426.8 | 427.2 | 416.8 | 378.6
1632 | 1499 | 470.8 | 437.7 | 427.7 | 426.9 | 427.2 | 416.8 | 378.6
1633 | 1500 | 470.9 | 437.8 | 427.7 | 426.9 | 427.2 | 416.8 | 378.6
1634 | 1501 | 471 | 437.8 | 427.7 | 426.9 | 427.2 | 416.8 | 378.6
1635 | 1502 | 471.1 | 437.8 | 427.8 | 426.9 | 427.1 | 416.8 | 378.5
1636 | 1503 | 471.1 | 437.8 | 427.8 | 426.9 | 426.9 | 416.8 | 378.5
1637 | 1504 | 470.9 | 437.9 | 427.8 | 426.9 | 426.8 | 416.9 | 378.5
1638 | 1505 | 470.8 | 437.9 | 427.8 | 427 | 426.8 | 416.9 | 378.4
1639 | 1506 | 470.9 | 438 | 427.9 | 427 | 426.9 | 416.9 | 378.4
1640 | 1507 | 470.9 | 438 | 427.9 | 427 | 426.9 | 416.9 | 378.4
1641 | 1508 | 471 | 438.1 | 427.9 | 427.1 | 426.9 | 417 | 378.3
1642 | 1509 | 471.1 | 438.1 | 427.9 | 427.1 | 426.8 | 417 | 378.3
1643 | 1510 | 471.2 | 438.2 | 427.9 | 427.2 | 426.7 | 417 | 378.3
1644 | 1511 | 471.2 | 438.3 | 428 | 427.2 | 426.6 | 417 | 378.3
1645 | 1512 | 471.2 | 438.3 | 428 | 427.2 | 426.5 | 417 | 378.3
1646 | 1513 | 471.1 | 438.4 | 428 | 427.3 | 426.5 | 417 | 378.3
1647 | 1514 | 471.2 | 438.5 | 428.1 | 427.3 | 426.4 | 417 | 378.2
1648 | 1515 | 471.2 | 438.5 | 428.1 | 427.3 | 426.4 | 417 | 378.3
1649 | 1516 | 471.3 | 438.6 | 428.2 | 427.4 | 426.3 | 417 | 378.3
1650 | 1517 | 471.2 | 438.6 | 428.2 | 427.4 | 426.3 | 417 | 378.4
1651 | 1518 | 471.1 | 438.7 | 428.3 | 427.4 | 426.3 | 417.1 | 378.5
1652 | 1519 | 471 | 438.7 | 428.3 | 427.4 | 426.3 | 417.1 | 378.5
1653 | 1520 | 471 | 438.7 | 428.3 | 427.4 | 426.3 | 417.1 | 378.6
1654 | 1521 | 471 | 438.8 | 428.3 | 427.4 | 426.3 | 417.1 | 378.6
1655 | 1522 | 471.3 | 438.8 | 428.4 | 427.4 | 426.3 | 417.1 | 378.5
1656 | 1523 | 471.3 | 438.8 | 428.4 | 427.5 | 426.3 | 417.1 | 378.5
1657 | 1524 | 471.1 | 438.8 | 428.4 | 427.5 | 426.3 | 417.1 | 378.5
1658 | 1525 | 471 | 438.9 | 428.5 | 427.6 | 426.4 | 417.1 | 378.5
1659 | 1526 | 470.9 | 438.9 | 428.5 | 427.6 | 426.4 | 417.1 | 378.5
1660 | 1527 | 470.7 | 438.9 | 428.5 | 427.6 | 426.4 | 417.2 | 378.5
1661 | 1528 | 470.6 | 439 | 428.5 | 427.6 | 426.4 | 417.2 | 378.4
1662 | 1529 | 470.6 | 439 | 428.5 | 427.7 | 426.4 | 417.2 | 378.3
1663 | 1530 | 470.4 | 439.1 | 428.5 | 427.7 | 426.4 | 417.2 | 378.3
1664 | 1531 | 470.4 | 439.1 | 428.5 | 427.8 | 426.5 | 417.2 | 378.3
1665 | 1532 | 470.3 | 439.2 | 428.6 | 427.8 | 426.6 | 417.2 | 378.3
1666 | 1533 | 470.2 | 439.2 | 428.6 | 427.9 | 426.7 | 417.2 | 378.3
1667 | 1534 | 470.3 | 439.2 | 428.6 | 427.9 | 426.7 | 417.2 | 378.2
1668 | 1535 | 470.5 | 439.3 | 428.6 | 427.9 | 426.7 | 417.2 | 378.3
1669 | 1536 | 470.5 | 439.3 | 428.7 | 427.9 | 426.5 | 417.2 | 378.3
1670 | 1537 | 470.6 | 439.4 | 428.7 | 427.9 | 426.4 | 417.2 | 378.4
1671 | 1538 | 470.7 | 439.4 | 428.7 | 428 | 426.3 | 417.2 | 378.4
1672 | 1539 | 470.9 | 439.4 | 428.7 | 428 | 426.2 | 417.2 | 378.4
1673 | 1540 | 471 | 439.4 | 428.7 | 428 | 426.1 | 417.2 | 378.4
1674 | 1541 | 471 | 439.5 | 428.8 | 428 | 426.1 | 417.2 | 378.3
1675 | 1542 | 471 | 439.5 | 428.8 | 428 | 426.1 | 417.2 | 378.3
1676 | 1543 | 471.1 | 439.5 | 428.9 | 428 | 426.1 | 417.2 | 378.3
1677 | 1544 | 471.1 | 439.6 | 428.9 | 427.9 | 426.1 | 417.2 | 378.3
1678 | 1545 | 471 | 439.6 | 428.9 | 427.9 | 426.1 | 417.2 | 378.3
1679 | 1546 | 470.8 | 439.6 | 428.9 | 427.9 | 426.2 | 417.3 | 378.3
1680 | 1547 | 470.9 | 439.6 | 429 | 427.9 | 426.2 | 417.3 | 378.3
1681 | 1548 | 470.9 | 439.7 | 429 | 427.9 | 426.2 | 417.3 | 378.3
1682 | 1549 | 471 | 439.7 | 429 | 427.9 | 426.2 | 417.3 | 378.3
1683 | 1550 | 471.1 | 439.7 | 429 | 427.9 | 426.2 | 417.3 | 378.2
1684 | 1551 | 471.1 | 439.8 | 429 | 427.9 | 426.2 | 417.3 | 378.2
1685 | 1552 | 471.1 | 439.8 | 429.1 | 428 | 426.1 | 417.3 | 378.2
1686 | 1553 | 471.1 | 439.6 | 429.4 | 427.9 | 425.7 | 417.3 | 378.3
1687 | 1554 | 471.2 | 439.7 | 429.5 | 427.9 | 425.6 | 417.3 | 378.2
1688 | 1555 | 471.3 | 439.7 | 429.5 | 427.9 | 425.5 | 417.4 | 378.2
1689 | 1556 | 471.4 | 439.8 | 429.5 | 427.9 | 425.4 | 417.4 | 378.2
1690 | 1557 | 471.4 | 439.8 | 429.6 | 427.9 | 425.4 | 417.4 | 378.2
1691 | 1558 | 471.4 | 439.9 | 429.6 | 427.9 | 425.3 | 417.4 | 378.2
1692 | 1559 | 471.3 | 439.9 | 429.6 | 427.8 | 425.3 | 417.4 | 378.3
1693 | 1560 | 471.3 | 439.9 | 429.7 | 427.8 | 425.3 | 417.4 | 378.3
1694 | 1561 | 471.2 | 439.9 | 429.7 | 427.9 | 425.3 | 417.4 | 378.2
1695 | 1562 | 471.2 | 440 | 429.7 | 427.9 | 425.2 | 417.4 | 378.2
1696 | 1563 | 471.2 | 440.1 | 429.7 | 427.9 | 425.2 | 417.4 | 378.2
1697 | 1564 | 471.2 | 440.1 | 429.7 | 427.9 | 425.1 | 417.5 | 378.2
1698 | 1565 | 471.2 | 440.2 | 429.8 | 427.9 | 425.1 | 417.5 | 378.1
1699 | 1566 | 471.1 | 440.2 | 429.8 | 427.9 | 425 | 417.5 | 378.1
1700 | 1567 | 471 | 440.2 | 429.8 | 427.9 | 425 | 417.5 | 378.1
1701 | 1568 | 471 | 440.3 | 429.8 | 427.9 | 425 | 417.5 | 378.1
1702 | 1569 | 471 | 440.3 | 429.8 | 427.9 | 425 | 417.5 | 378.1
1703 | 1570 | 471.1 | 440.4 | 429.8 | 427.9 | 425 | 417.5 | 378
1704 | 1571 | 471.1 | 440.4 | 429.8 | 427.9 | 424.9 | 417.5 | 378.1
1705 | 1572 | 471.1 | 440.5 | 429.8 | 427.9 | 424.9 | 417.5 | 378.1
1706 | 1573 | 471.2 | 440.5 | 429.9 | 427.9 | 424.9 | 417.5 | 378.2
1707 | 1574 | 471.2 | 440.6 | 429.9 | 427.9 | 424.9 | 417.5 | 378.2
1708 | 1575 | 471.1 | 440.6 | 429.9 | 427.9 | 424.9 | 417.5 | 378.2
1709 | 1576 | 471.2 | 440.6 | 429.9 | 427.9 | 424.9 | 417.5 | 378.2
1710 | 1577 | 471.1 | 440.7 | 429.9 | 427.8 | 424.9 | 417.5 | 378.2
1711 | 1578 | 471.1 | 440.7 | 429.9 | 427.8 | 424.9 | 417.5 | 378.2
1712 | 1579 | 471 | 440.7 | 429.9 | 427.7 | 425 | 417.5 | 378.2
1713 | 1580 | 471 | 440.7 | 429.9 | 427.7 | 425 | 417.5 | 378.3
1714 | 1581 | 470.9 | 440.8 | 429.9 | 427.7 | 425 | 417.5 | 378.3
1715 | 1582 | 470.8 | 440.8 | 429.9 | 427.6 | 425 | 417.5 | 378.3
1716 | 1583 | 470.9 | 440.8 | 430 | 427.6 | 425 | 417.5 | 378.2
1717 | 1584 | 471 | 440.8 | 430 | 427.6 | 425.1 | 417.5 | 378.2
1718 | 1585 | 470.9 | 440.9 | 430 | 427.6 | 425.1 | 417.5 | 378.2
1719 | 1586 | 470.9 | 440.9 | 430.1 | 427.7 | 425.2 | 417.5 | 378.2
1720 | 1587 | 470.9 | 440.9 | 430.1 | 427.7 | 425.2 | 417.6 | 378.2
1721 | 1588 | 470.9 | 441 | 430.1 | 427.6 | 425.3 | 417.6 | 378.3
1722 | 1589 | 470.9 | 441 | 430.1 | 427.6 | 425.3 | 417.6 | 378.3
1723 | 1590 | 471.1 | 441 | 430.1 | 427.5 | 425.3 | 417.6 | 378.3
1724 | 1591 | 471.2 | 441 | 430.1 | 427.5 | 425.3 | 417.7 | 378.3
1725 | 1592 | 471.3 | 441.1 | 430.1 | 427.5 | 425.3 | 417.7 | 378.3
1726 | 1593 | 471.3 | 441.1 | 430.2 | 427.5 | 425.3 | 417.7 | 378.3
1727 | 1594 | 471.3 | 441.1 | 430.2 | 427.6 | 425.4 | 417.7 | 378.3
1728 | 1595 | 471.3 | 441.1 | 430.2 | 427.6 | 425.4 | 417.7 | 378.2
1729 | 1596 | 471.2 | 441.2 | 430.2 | 427.5 | 425.4 | 417.7 | 378.3
1730 | 1597 | 471.3 | 441.2 | 430.2 | 427.5 | 425.4 | 417.8 | 378.3
1731 | 1598 | 471.3 | 441.2 | 430.2 | 427.4 | 425.4 | 417.8 | 378.3
1732 | 1599 | 471.3 | 441.2 | 430.2 | 427.4 | 425.4 | 417.8 | 378.3
1733 | 1600 | 471.3 | 441.2 | 430.2 | 427.3 | 425.4 | 417.8 | 378.3
1734 | 1601 | 471.3 | 441.2 | 430.2 | 427.3 | 425.4 | 417.8 | 378.3
1735 | 1602 | 471.3 | 441.2 | 430.1 | 427.3 | 425.3 | 417.9 | 378.2
1736 | 1603 | 471.2 | 441.2 | 430.1 | 427.4 | 425.3 | 417.9 | 378.2
1737 | 1604 | 471.3 | 441.2 | 430.1 | 427.4 | 425.3 | 417.9 | 378.1
1738 | 1605 | 471.2 | 441.2 | 430.2 | 427.4 | 425.3 | 417.9 | 378.1
1739 | 1606 | 471.1 | 441.4 | 429.9 | 427.4 | 425.6 | 417.9 | 378
1740 | 1607 | 471.1 | 441.5 | 429.8 | 427.3 | 425.8 | 417.9 | 378
1741 | 1608 | 471.1 | 441.5 | 429.9 | 427.3 | 425.8 | 417.9 | 377.9
1742 | 1609 | 471.1 | 441.5 | 429.9 | 427.3 | 425.8 | 417.9 | 377.9
1743 | 1610 | 471.2 | 441.5 | 429.9 | 427.3 | 425.8 | 417.9 | 378
1744 | 1611 | 471.2 | 441.5 | 429.9 | 427.3 | 425.8 | 418 | 378.1
1745 | 1612 | 471.2 | 441.4 | 429.9 | 427.3 | 425.8 | 418 | 378.2
1746 | 1613 | 471.1 | 441.5 | 429.9 | 427.2 | 425.8 | 418 | 378.2
1747 | 1614 | 471.2 | 441.5 | 429.9 | 427.2 | 425.8 | 418 | 378.1
1748 | 1615 | 471.1 | 441.5 | 429.9 | 427.2 | 425.7 | 418 | 378.2
1749 | 1616 | 471.1 | 441.5 | 429.9 | 427.2 | 425.7 | 418 | 378.2
1750 | 1617 | 471.1 | 441.6 | 429.9 | 427.3 | 425.7 | 418 | 378.1
1751 | 1618 | 471.1 | 441.6 | 429.9 | 427.2 | 425.8 | 418 | 378.2
1752 | 1619 | 471 | 441.6 | 429.9 | 427.2 | 425.8 | 418 | 378.2
1753 | 1620 | 471 | 441.6 | 429.9 | 427.2 | 425.8 | 418.1 | 378.2
1754 | 1621 | 471 | 441.6 | 429.9 | 427.2 | 425.8 | 418 | 378.2
1755 | 1622 | 471 | 441.6 | 430 | 427.2 | 425.8 | 418.1 | 378.2
1756 | 1623 | 471 | 441.7 | 430 | 427.1 | 425.8 | 418.1 | 378.3
1757 | 1624 | 470.9 | 441.7 | 430 | 427 | 425.8 | 418.1 | 378.3
1758 | 1625 | 470.7 | 441.7 | 430 | 427 | 425.8 | 418.1 | 378.3
1759 | 1626 | 470.5 | 441.7 | 430 | 427 | 425.9 | 418.1 | 378.3
1760 | 1627 | 470.3 | 441.8 | 430 | 427 | 425.9 | 418.2 | 378.3
1761 | 1628 | 470.2 | 441.8 | 430 | 427 | 426 | 418.2 | 378.3
1762 | 1629 | 470.2 | 441.8 | 430 | 427 | 426 | 418.2 | 378.4
1763 | 1630 | 470.2 | 441.9 | 430 | 426.9 | 426.1 | 418.2 | 378.4
1764 | 1631 | 470.3 | 441.9 | 430 | 426.9 | 426.2 | 418.2 | 378.4
1765 | 1632 | 470.5 | 441.9 | 430 | 426.9 | 426.3 | 418.2 | 378.3
1766 | 1633 | 470.5 | 441.9 | 429.9 | 426.9 | 426.4 | 418.2 | 378.3
1767 | 1634 | 470.6 | 441.9 | 430 | 427 | 426.4 | 418.3 | 378.4
1768 | 1635 | 470.7 | 441.9 | 430 | 426.9 | 426.4 | 418.3 | 378.4
1769 | 1636 | 470.8 | 441.9 | 430 | 426.8 | 426.4 | 418.3 | 378.3
1770 | 1637 | 470.9 | 442 | 430 | 426.7 | 426.4 | 418.3 | 378.4
1771 | 1638 | 471 | 442 | 430 | 426.6 | 426.5 | 418.3 | 378.5
1772 | 1639 | 471.1 | 441.9 | 430 | 426.6 | 426.5 | 418.3 | 378.5
1773 | 1640 | 471.1 | 442 | 430 | 426.6 | 426.6 | 418.3 | 378.5
1774 | 1641 | 471.2 | 442 | 430 | 426.7 | 426.6 | 418.3 | 378.6
1775 | 1642 | 471.3 | 442 | 430 | 426.7 | 426.6 | 418.3 | 378.6
1776 | 1643 | 471.4 | 442 | 430 | 426.7 | 426.6 | 418.3 | 378.7
1777 | 1644 | 471.6 | 442 | 430 | 426.7 | 426.7 | 418.3 | 378.7
1778 | 1645 | 471.7 | 442 | 429.9 | 426.7 | 426.7 | 418.3 | 378.7
1779 | 1646 | 471.8 | 442 | 429.9 | 426.6 | 426.8 | 418.3 | 378.8
1780 | 1647 | 471.7 | 442 | 429.9 | 426.6 | 426.8 | 418.3 | 378.8
1781 | 1648 | 471.8 | 442.1 | 429.9 | 426.6 | 426.8 | 418.3 | 378.8
1782 | 1649 | 471.8 | 442 | 429.9 | 426.6 | 426.7 | 418.4 | 378.8
1783 | 1650 | 471.8 | 442.1 | 430 | 426.6 | 426.7 | 418.4 | 378.9
1784 | 1651 | 471.7 | 442.1 | 430 | 426.7 | 426.7 | 418.4 | 378.9
1785 | 1652 | 471.7 | 442.1 | 430 | 426.7 | 426.7 | 418.5 | 378.9
1786 | 1653 | 471.8 | 442.1 | 430 | 426.6 | 426.6 | 418.5 | 378.9
1787 | 1654 | 471.9 | 442.1 | 430 | 426.6 | 426.6 | 418.5 | 379
1788 | 1655 | 472 | 442.1 | 430.1 | 426.6 | 426.6 | 418.5 | 379.1
1789 | 1656 | 472 | 442.1 | 430.1 | 426.6 | 426.5 | 418.5 | 379.1
1790 | 1657 | 472 | 442.1 | 430.1 | 426.6 | 426.5 | 418.5 | 379.1
1791 | 1658 | 472 | 442.2 | 430.1 | 426.5 | 426.5 | 418.5 | 379.1
1792 | 1659 | 471.9 | 442.2 | 430.1 | 426.5 | 426.5 | 418.6 | 379.1
1793 | 1660 | 471.8 | 442.2 | 430.1 | 426.5 | 426.5 | 418.6 | 379.1
1794 | 1661 | 471.8 | 442.2 | 430 | 426.4 | 426.5 | 418.6 | 379.1
1795 | 1662 | 471.7 | 442.3 | 430 | 426.3 | 426.5 | 418.6 | 379.1
1796 | 1663 | 471.7 | 442.3 | 430 | 426.3 | 426.6 | 418.7 | 379.2
1797 | 1664 | 471.8 | 442.3 | 430.1 | 426.3 | 426.6 | 418.7 | 379.2
1798 | 1665 | 471.8 | 442.3 | 430.1 | 426.3 | 426.6 | 418.7 | 379.2
1799 | 1666 | 471.6 | 442.3 | 430.1 | 426.4 | 426.6 | 418.7 | 379.2
1800 | 1667 | 471.4 | 442.3 | 430.1 | 426.4 | 426.7 | 418.7 | 379.2
1801 | 1668 | 471.3 | 442.3 | 430.1 | 426.4 | 426.7 | 418.7 | 379.2
1802 | 1669 | 471.2 | 442.3 | 430.2 | 426.2 | 426.7 | 418.7 | 379.2
1803 | 1670 | 471 | 442.3 | 430.2 | 426.1 | 426.7 | 418.8 | 379.2
1804 | 1671 | 470.9 | 442.4 | 430.2 | 426 | 426.7 | 418.8 | 379.3
1805 | 1672 | 470.9 | 442.4 | 430.2 | 426 | 426.6 | 418.8 | 379.3
1806 | 1673 | 471 | 442.4 | 430.3 | 426 | 426.6 | 418.8 | 379.3
1807 | 1674 | 471.1 | 442.4 | 430.3 | 426 | 426.6 | 418.8 | 379.2
1808 | 1675 | 471 | 442.4 | 430.3 | 426 | 426.6 | 418.8 | 379.2
1809 | 1676 | 470.8 | 442.4 | 430.3 | 426.1 | 426.6 | 418.8 | 379.2
1810 | 1677 | 470.7 | 442.5 | 430.3 | 426.1 | 426.6 | 418.8 | 379.1
1811 | 1678 | 470.6 | 442.5 | 430.3 | 426.1 | 426.6 | 418.8 | 379.1
1812 | 1679 | 470.4 | 442.5 | 430.3 | 426 | 426.6 | 418.8 | 379.1
1813 | 1680 | 470.4 | 442.6 | 430.3 | 425.9 | 426.6 | 418.9 | 379
1814 | 1681 | 470.4 | 442.6 | 430.3 | 425.9 | 426.6 | 418.9 | 379
1815 | 1682 | 470.4 | 442.6 | 430.4 | 425.9 | 426.6 | 418.8 | 379
1816 | 1683 | 470.2 | 442.6 | 430.4 | 425.9 | 426.6 | 418.8 | 379
1817 | 1684 | 470 | 442.6 | 430.4 | 426 | 426.6 | 418.8 | 379
1818 | 1685 | 470 | 442.6 | 430.3 | 426 | 426.6 | 418.8 | 379
1819 | 1686 | 470 | 442.7 | 430.3 | 426 | 426.6 | 418.8 | 379
1820 | 1687 | 470.1 | 442.6 | 430.4 | 426 | 426.6 | 418.8 | 379
1821 | 1688 | 470.1 | 442.6 | 430.4 | 426 | 426.6 | 418.8 | 379
1822 | 1689 | 470.2 | 442.6 | 430.5 | 425.9 | 426.5 | 418.8 | 379
1823 | 1690 | 470.1 | 442.6 | 430.5 | 425.9 | 426.5 | 418.7 | 379
1824 | 1691 | 470 | 442.6 | 430.5 | 425.9 | 426.5 | 418.7 | 379
1825 | 1692 | 469.9 | 442.6 | 430.5 | 425.9 | 426.4 | 418.7 | 379
1826 | 1693 | 470 | 442.7 | 430.5 | 425.9 | 426.3 | 418.7 | 379
1827 | 1694 | 470 | 442.7 | 430.5 | 425.8 | 426.3 | 418.7 | 379
1828 | 1695 | 469.9 | 442.7 | 430.5 | 425.8 | 426.2 | 418.7 | 379
1829 | 1696 | 469.8 | 442.7 | 430.5 | 425.8 | 426.1 | 418.6 | 379
1830 | 1697 | 469.8 | 442.7 | 430.4 | 425.7 | 426.1 | 418.6 | 378.9
1831 | 1698 | 469.8 | 442.7 | 430.3 | 425.7 | 426 | 418.6 | 379
1832 | 1699 | 469.8 | 442.7 | 430.4 | 425.7 | 425.9 | 418.6 | 379
1833 | 1700 | 470 | 442.8 | 430.4 | 425.8 | 425.8 | 418.7 | 379.1
1834 | 1701 | 470.1 | 442.8 | 430.5 | 425.7 | 425.8 | 418.7 | 379
1835 | 1702 | 470.2 | 442.8 | 430.5 | 425.6 | 425.7 | 418.7 | 379
1836 | 1703 | 470.2 | 442.8 | 430.6 | 425.6 | 425.6 | 418.6 | 378.9
1837 | 1704 | 470.2 | 442.8 | 430.6 | 425.6 | 425.5 | 418.6 | 378.9
1838 | 1705 | 470.2 | 442.8 | 430.6 | 425.7 | 425.5 | 418.6 | 378.9
1839 | 1706 | 470.1 | 442.8 | 430.7 | 425.6 | 425.4 | 418.6 | 379
1840 | 1707 | 470 | 442.8 | 430.7 | 425.4 | 425.4 | 418.6 | 379
1841 | 1708 | 469.8 | 442.8 | 430.7 | 425.4 | 425.4 | 418.6 | 379
1842 | 1709 | 469.7 | 442.8 | 430.7 | 425.3 | 425.3 | 418.6 | 379
1843 | 1710 | 469.6 | 442.8 | 430.7 | 425.3 | 425.2 | 418.6 | 378.9
1844 | 1711 | 469.6 | 442.8 | 430.7 | 425.4 | 425.2 | 418.6 | 378.9
1845 | 1712 | 469.6 | 442.8 | 430.7 | 425.4 | 425.1 | 418.6 | 378.9
1846 | 1713 | 469.6 | 442.8 | 430.7 | 425.4 | 425.1 | 418.6 | 378.8
1847 | 1714 | 469.7 | 442.8 | 430.7 | 425.4 | 425 | 418.6 | 378.8
1848 | 1715 | 469.8 | 442.7 | 430.9 | 425.2 | 424.6 | 418.6 | 378.8
1849 | 1716 | 469.6 | 442.6 | 431 | 425.1 | 424.4 | 418.6 | 378.9
1850 | 1717 | 469.6 | 442.6 | 431 | 425.1 | 424.3 | 418.6 | 378.8
1851 | 1718 | 469.5 | 442.6 | 431.1 | 425 | 424.2 | 418.6 | 378.8
1852 | 1719 | 469.5 | 442.6 | 431.1 | 425.1 | 424.1 | 418.6 | 378.7
1853 | 1720 | 469.5 | 442.7 | 431.1 | 425.1 | 424 | 418.6 | 378.7
1854 | 1721 | 469.3 | 442.7 | 431.1 | 425.2 | 423.8 | 418.6 | 378.6
1855 | 1722 | 469.2 | 442.7 | 431.1 | 425.1 | 423.7 | 418.6 | 378.7
1856 | 1723 | 469.4 | 442.8 | 431.1 | 424.9 | 423.5 | 418.6 | 378.6
1857 | 1724 | 469.4 | 442.8 | 431.1 | 424.8 | 423.3 | 418.5 | 378.7
1858 | 1725 | 469.4 | 442.8 | 431.1 | 424.8 | 423.2 | 418.6 | 378.6
1859 | 1726 | 469.4 | 442.8 | 431.1 | 424.9 | 423.1 | 418.5 | 378.7
1860 | 1727 | 469.6 | 442.8 | 431.1 | 425 | 423 | 418.5 | 378.6
1861 | 1728 | 469.6 | 442.8 | 431.1 | 425 | 422.8 | 418.5 | 378.6
1862 | 1729 | 469.6 | 442.8 | 431.1 | 424.9 | 422.7 | 418.5 | 378.7
1863 | 1730 | 469.8 | 442.8 | 431.1 | 424.9 | 422.6 | 418.5 | 378.7
1864 | 1731 | 470 | 442.8 | 431.1 | 424.9 | 422.5 | 418.5 | 378.7
1865 | 1732 | 469.9 | 442.8 | 431.1 | 424.9 | 422.4 | 418.5 | 378.7
1866 | 1733 | 469.9 | 442.8 | 431.1 | 424.8 | 422.2 | 418.5 | 378.8
1867 | 1734 | 469.9 | 442.8 | 431.1 | 424.8 | 422.1 | 418.5 | 378.8
1868 | 1735 | 470 | 442.9 | 431.1 | 424.8 | 422 | 418.5 | 378.8
1869 | 1736 | 470 | 442.9 | 431.1 | 424.7 | 421.9 | 418.5 | 378.8
1870 | 1737 | 470.1 | 442.9 | 431.1 | 424.6 | 421.8 | 418.5 | 378.8
1871 | 1738 | 470.2 | 443 | 431.1 | 424.5 | 421.7 | 418.5 | 378.8
1872 | 1739 | 470.1 | 443 | 431.2 | 424.5 | 421.7 | 418.5 | 378.7
1873 | 1740 | 470.1 | 443 | 431.2 | 424.5 | 421.6 | 418.5 | 378.7
1874 | 1741 | 470 | 443 | 431.2 | 424.5 | 421.6 | 418.5 | 378.8
1875 | 1742 | 469.9 | 443.1 | 431.2 | 424.5 | 421.6 | 418.5 | 378.8
1876 | 1743 | 469.9 | 443.1 | 431.2 | 424.5 | 421.5 | 418.4 | 378.8
1877 | 1744 | 470 | 443.1 | 431.2 | 424.5 | 421.4 | 418.5 | 378.8
1878 | 1745 | 470 | 443.2 | 431.2 | 424.5 | 421.4 | 418.5 | 378.8
1879 | 1746 | 470 | 443.2 | 431.2 | 424.4 | 421.3 | 418.5 | 378.8
1880 | 1747 | 470 | 443.2 | 431.3 | 424.5 | 421.3 | 418.5 | 378.8
1881 | 1748 | 470.1 | 443.2 | 431.3 | 424.5 | 421.3 | 418.5 | 378.8
1882 | 1749 | 470 | 443.4 | 431.2 | 424.7 | 421.5 | 418.5 | 378.9
1883 | 1750 | 470.1 | 443.5 | 431 | 424.7 | 421.7 | 418.5 | 378.9
1884 | 1751 | 470 | 443.5 | 431.1 | 424.5 | 421.6 | 418.5 | 378.9
1885 | 1752 | 470 | 443.5 | 431.1 | 424.4 | 421.6 | 418.4 | 378.8
1886 | 1753 | 469.9 | 443.6 | 431.1 | 424.2 | 421.6 | 418.4 | 378.8
1887 | 1754 | 469.6 | 443.6 | 431.1 | 424 | 421.7 | 418.5 | 378.8
1888 | 1755 | 469.5 | 443.6 | 431.1 | 424 | 421.7 | 418.5 | 378.8
1889 | 1756 | 469.4 | 443.7 | 431.1 | 424 | 421.7 | 418.5 | 378.7
1890 | 1757 | 469.2 | 443.7 | 431.1 | 423.9 | 421.7 | 418.5 | 378.6
1891 | 1758 | 469.2 | 443.6 | 431.2 | 424 | 421.7 | 418.5 | 378.7
1892 | 1759 | 469.2 | 443.6 | 431.2 | 424.1 | 421.7 | 418.5 | 378.7
1893 | 1760 | 469.2 | 443.6 | 431.2 | 424.2 | 421.7 | 418.5 | 378.6
1894 | 1761 | 469 | 443.6 | 431.2 | 424.3 | 421.6 | 418.5 | 378.6
1895 | 1762 | 468.8 | 443.6 | 431.2 | 424.2 | 421.6 | 418.5 | 378.6
1896 | 1763 | 468.7 | 443.6 | 431.2 | 424.1 | 421.6 | 418.4 | 378.6
1897 | 1764 | 468.5 | 443.6 | 431.2 | 424 | 421.6 | 418.4 | 378.6
1898 | 1765 | 468.3 | 443.6 | 431.2 | 424 | 421.6 | 418.4 | 378.5
1899 | 1766 | 468.3 | 443.6 | 431.2 | 424 | 421.5 | 418.4 | 378.4
1900 | 1767 | 468.4 | 443.6 | 431.2 | 423.9 | 421.5 | 418.4 | 378.5
1901 | 1768 | 468.6 | 443.6 | 431.2 | 423.8 | 421.4 | 418.4 | 378.5
1902 | 1769 | 468.5 | 443.6 | 431.2 | 423.8 | 421.4 | 418.4 | 378.5
1903 | 1770 | 468.5 | 443.6 | 431.2 | 423.9 | 421.4 | 418.4 | 378.5
1904 | 1771 | 468.4 | 443.6 | 431.2 | 423.9 | 421.3 | 418.4 | 378.4
1905 | 1772 | 468.2 | 443.6 | 431.2 | 423.9 | 421.2 | 418.4 | 378.5
1906 | 1773 | 468.2 | 443.6 | 431.2 | 423.9 | 421.1 | 418.4 | 378.4
1907 | 1774 | 468.3 | 443.6 | 431.2 | 423.8 | 421 | 418.4 | 378.4
1908 | 1775 | 468.2 | 443.6 | 431.1 | 423.8 | 420.9 | 418.4 | 378.4
1909 | 1776 | 468.3 | 443.7 | 431.1 | 423.8 | 420.8 | 418.4 | 378.3
1910 | 1777 | 468.4 | 443.7 | 431.1 | 423.8 | 420.7 | 418.4 | 378.3
1911 | 1778 | 468.4 | 443.7 | 431.2 | 423.8 | 420.7 | 418.4 | 378.2
1912 | 1779 | 468.5 | 443.6 | 431.2 | 423.8 | 420.6 | 418.3 | 378.1
1913 | 1780 | 468.6 | 443.6 | 431.2 | 423.8 | 420.6 | 418.3 | 378.1
1914 | 1781 | 468.6 | 443.6 | 431.3 | 423.8 | 420.5 | 418.3 | 378
1915 | 1782 | 468.8 | 443.6 | 431.3 | 423.7 | 420.5 | 418.3 | 377.9
1916 | 1783 | 468.9 | 443.7 | 431.3 | 423.6 | 420.4 | 418.3 | 377.9
1917 | 1784 | 468.8 | 443.7 | 431.3 | 423.5 | 420.3 | 418.3 | 377.9
1918 | 1785 | 468.8 | 443.7 | 431.3 | 423.5 | 420.3 | 418.3 | 377.9
1919 | 1786 | 469 | 443.7 | 431.3 | 423.5 | 420.3 | 418.3 | 378
1920 | 1787 | 469 | 443.7 | 431.3 | 423.4 | 420.2 | 418.3 | 378
1921 | 1788 | 469 | 443.7 | 431.3 | 423.5 | 420.2 | 418.3 | 378.1
1922 | 1789 | 469.1 | 443.7 | 431.3 | 423.4 | 420.2 | 418.3 | 378.2
1923 | 1790 | 469.2 | 443.7 | 431.3 | 423.4 | 420.2 | 418.3 | 378.2
1924 | 1791 | 469.1 | 443.7 | 431.3 | 423.4 | 420.2 | 418.3 | 378.2
1925 | 1792 | 469 | 443.8 | 431.3 | 423.4 | 420.2 | 418.3 | 378.2
1926 | 1793 | 469 | 443.8 | 431.3 | 423.4 | 420.1 | 418.4 | 378.2
1927 | 1794 | 469.1 | 443.8 | 431.3 | 423.4 | 420.1 | 418.4 | 378.3
1928 | 1795 | 469.2 | 443.8 | 431.4 | 423.4 | 420 | 418.4 | 378.3
1929 | 1796 | 469.2 | 443.8 | 431.4 | 423.4 | 420 | 418.4 | 378.2
1930 | 1797 | 469.3 | 443.9 | 431.4 | 423.5 | 419.9 | 418.4 | 378.1
1931 | 1798 | 469.5 | 443.9 | 431.4 | 423.6 | 419.9 | 418.4 | 378
1932 | 1799 | 469.5 | 443.9 | 431.4 | 423.5 | 419.9 | 418.4 | 377.9
1933 | 1800 | 469.5 | 443.9 | 431.4 | 423.3 | 419.8 | 418.4 | 377.8
1934 | 1801 | 469.5 | 444 | 431.4 | 423.1 | 419.8 | 418.4 | 377.8
1935 | 1802 | 469.7 | 444 | 431.4 | 422.8 | 419.8 | 418.4 | 377.8
1936 | 1803 | 469.7 | 444 | 431.5 | 422.7 | 419.7 | 418.4 | 377.7
1937 | 1804 | 469.6 | 444 | 431.5 | 422.7 | 419.7 | 418.4 | 377.7
1938 | 1805 | 469.4 | 444 | 431.5 | 422.7 | 419.7 | 418.5 | 377.6
1939 | 1806 | 469.4 | 444.1 | 431.5 | 422.8 | 419.7 | 418.5 | 377.6
1940 | 1807 | 469.4 | 444.1 | 431.5 | 422.8 | 419.7 | 418.5 | 377.6
1941 | 1808 | 469.4 | 444.1 | 431.4 | 422.9 | 419.8 | 418.5 | 377.6
1942 | 1809 | 469.4 | 444.2 | 431.4 | 423 | 419.8 | 418.5 | 377.7
1943 | 1810 | 469.5 | 444.2 | 431.4 | 423 | 419.9 | 418.5 | 377.7
1944 | 1811 | 469.5 | 444.2 | 431.5 | 423 | 420 | 418.5 | 377.6
1945 | 1812 | 469.6 | 444.2 | 431.5 | 423 | 420.1 | 418.5 | 377.5
1946 | 1813 | 469.6 | 444.2 | 431.5 | 423 | 420.2 | 418.5 | 377.5
1947 | 1814 | 469.7 | 444.2 | 431.5 | 423.2 | 420.2 | 418.6 | 377.6
1948 | 1815 | 469.9 | 444.2 | 431.6 | 423.2 | 420.2 | 418.6 | 377.6
1949 | 1816 | 470.1 | 444.3 | 431.6 | 423.3 | 420.3 | 418.6 | 377.6
1950 | 1817 | 470.1 | 444.3 | 431.6 | 423.3 | 420.3 | 418.6 | 377.5
1951 | 1818 | 470.2 | 444.3 | 431.6 | 423.4 | 420.3 | 418.7 | 377.6
1952 | 1819 | 470.2 | 444.3 | 431.6 | 423.2 | 420.4 | 418.7 | 377.5
1953 | 1820 | 470.2 | 444.4 | 431.6 | 423.1 | 420.4 | 418.7 | 377.4
1954 | 1821 | 470.3 | 444.4 | 431.6 | 423 | 420.3 | 418.8 | 377.4
1955 | 1822 | 470.5 | 444.4 | 431.6 | 423 | 420.3 | 418.8 | 377.5
1956 | 1823 | 470.6 | 444.4 | 431.6 | 422.9 | 420.3 | 418.8 | 377.5
1957 | 1824 | 470.6 | 444.4 | 431.6 | 422.9 | 420.3 | 418.8 | 377.5
1958 | 1825 | 470.6 | 444.5 | 431.6 | 422.9 | 420.3 | 418.8 | 377.5
1959 | 1826 | 470.5 | 444.5 | 431.7 | 422.9 | 420.3 | 418.9 | 377.4
1960 | 1827 | 470.6 | 444.4 | 432 | 422.8 | 420 | 418.9 | 377.4
1961 | 1828 | 470.7 | 444.3 | 432.1 | 422.7 | 419.8 | 418.9 | 377.4
1962 | 1829 | 470.7 | 444.3 | 432.2 | 422.8 | 419.8 | 418.9 | 377.5
1963 | 1830 | 470.4 | 444.3 | 432.2 | 422.7 | 419.8 | 418.9 | 377.5
1964 | 1831 | 470 | 444.3 | 432.2 | 422.7 | 419.8 | 418.8 | 377.5
1965 | 1832 | 469.5 | 444.3 | 432.2 | 422.6 | 419.8 | 418.8 | 377.5
1966 | 1833 | 469 | 444.4 | 432.2 | 422.6 | 419.8 | 418.8 | 377.5
1967 | 1834 | 468.4 | 444.4 | 432.3 | 422.5 | 419.8 | 418.8 | 377.5
1968 | 1835 | 467.9 | 444.4 | 432.3 | 422.6 | 419.8 | 418.7 | 377.4
1969 | 1836 | 467.2 | 444.4 | 432.3 | 422.6 | 419.8 | 418.6 | 377.4
1970 | 1837 | 466.5 | 444.5 | 432.3 | 422.7 | 419.8 | 418.5 | 377.3
1971 | 1838 | 465.9 | 444.5 | 432.3 | 422.7 | 419.8 | 418.5 | 377.3
1972 | 1839 | 464.9 | 444.5 | 432.3 | 422.6 | 419.7 | 418.4 | 377.2
1973 | 1840 | 463.9 | 444.5 | 432.3 | 422.6 | 419.6 | 418.3 | 377.1
1974 | 1841 | 463.1 | 444.5 | 432.3 | 422.6 | 419.5 | 418.2 | 376.9
1975 | 1842 | 462.3 | 444.5 | 432.3 | 422.6 | 419.5 | 418.1 | 376.9
1976 | 1843 | 461.6 | 444.5 | 432.3 | 422.6 | 419.4 | 418 | 376.7
1977 | 1844 | 460.9 | 444.5 | 432.3 | 422.6 | 419.3 | 417.8 | 376.6
1978 | 1845 | 460.1 | 444.5 | 432.4 | 422.7 | 419.2 | 417.7 | 376.5
1979 | 1846 | 459.3 | 444.5 | 432.3 | 422.5 | 419.1 | 417.6 | 376.3
1980 | 1847 | 458.5 | 444.5 | 432.3 | 422.4 | 418.9 | 417.4 | 376.2
1981 | 1848 | 457.5 | 444.5 | 432.3 | 422.3 | 418.8 | 417.3 | 376
1982 | 1849 | 456.6 | 444.5 | 432.4 | 422.1 | 418.6 | 417.1 | 375.9
1983 | 1850 | 455.8 | 444.4 | 432.4 | 422 | 418.4 | 416.9 | 375.6
1984 | 1851 | 454.9 | 444.4 | 432.4 | 422 | 418.2 | 416.7 | 375.4
1985 | 1852 | 454.1 | 444.4 | 432.4 | 421.9 | 418 | 416.4 | 375.2
1986 | 1853 | 453.5 | 444.4 | 432.4 | 421.8 | 417.8 | 416.2 | 374.9
1987 | 1854 | 452.8 | 444.4 | 432.3 | 421.8 | 417.6 | 415.9 | 374.7
1988 | 1855 | 451.9 | 444.3 | 432.3 | 421.8 | 417.5 | 415.7 | 374.5
1989 | 1856 | 451.1 | 444.3 | 432.3 | 421.8 | 417.3 | 415.4 | 374.2
1990 | 1857 | 450.3 | 444.3 | 432.3 | 421.8 | 417.1 | 415.1 | 373.9
1991 | 1858 | 449.3 | 444.2 | 432.3 | 421.8 | 416.9 | 414.8 | 373.7
1992 | 1859 | 448.4 | 444.2 | 432.3 | 421.8 | 416.6 | 414.5 | 373.4
1993 | 1860 | 447.6 | 444.1 | 432.3 | 421.7 | 416.3 | 414.3 | 373.2
1994 | 1861 | 446.7 | 444.1 | 432.3 | 421.7 | 416.1 | 414 | 372.9
1995 | 1862 | 445.8 | 444 | 432.3 | 421.6 | 415.8 | 413.7 | 372.6
1996 | 1863 | 445 | 444 | 432.3 | 421.6 | 415.5 | 413.4 | 372.3
1997 | 1864 | 444.3 | 443.9 | 432.2 | 421.6 | 415.3 | 413 | 372.1
1998 | 1865 | 443.7 | 443.8 | 432.1 | 421.5 | 415.1 | 412.7 | 371.9
1999 | 1866 | 442.9 | 443.8 | 432.1 | 421.5 | 414.9 | 412.4 | 371.6
2000 | 1867 | 441.9 | 443.8 | 432.1 | 421.4 | 414.7 | 412.1 | 371.3
2001 | 1868 | 440.9 | 443.7 | 432.1 | 421.5 | 414.5 | 411.7 | 371
2002 | 1869 | 440.1 | 443.6 | 432 | 421.4 | 414.3 | 411.4 | 370.6
2003 | 1870 | 439.3 | 443.5 | 432 | 421.3 | 414.2 | 411 | 370.3
2004 | 1871 | 438.5 | 443.5 | 432 | 421.2 | 413.9 | 410.7 | 369.9
2005 | 1872 | 437.7 | 443.4 | 431.9 | 421.1 | 413.7 | 410.3 | 369.6
2006 | 1873 | 436.8 | 443.3 | 431.9 | 420.9 | 413.4 | 410 | 369.3
2007 | 1874 | 435.9 | 443.2 | 431.8 | 420.8 | 413.2 | 409.6 | 368.9
2008 | 1875 | 435 | 443 | 431.8 | 420.6 | 412.9 | 409.2 | 368.5
2009 | 1876 | 434.1 | 442.9 | 431.7 | 420.4 | 412.6 | 408.9 | 368.2
2010 | 1877 | 433.3 | 442.8 | 431.6 | 420.3 | 412.3 | 408.5 | 368
2011 | 1878 | 432.6 | 442.7 | 431.5 | 420.1 | 412 | 408.1 | 367.7
2012 | 1879 | 431.9 | 442.6 | 431.4 | 420 | 411.7 | 407.7 | 367.3
2013 | 1880 | 431.1 | 442.4 | 431.3 | 419.9 | 411.4 | 407.4 | 367
2014 | 1881 | 430.2 | 442.3 | 431.2 | 419.9 | 411.1 | 407 | 366.6
2015 | 1882 | 429.2 | 442.1 | 431.1 | 419.8 | 410.7 | 406.7 | 366.3
2016 | 1883 | 428.4 | 442 | 431.1 | 419.6 | 410.3 | 406.3 | 366
2017 | 1884 | 427.6 | 441.9 | 431 | 419.5 | 410 | 405.9 | 365.7
2018 | 1885 | 426.8 | 441.7 | 430.9 | 419.4 | 409.6 | 405.7 | 365.4
2019 | 1886 | 425.9 | 441.5 | 430.8 | 419.2 | 409.2 | 405.5 | 365.1
2020 | 1887 | 425.2 | 441.3 | 430.7 | 419 | 408.9 | 405.4 | 364.7
2021 | 1888 | 424.4 | 441.1 | 430.6 | 418.8 | 408.5 | 405.2 | 364.4
2022 | 1889 | 423.7 | 440.9 | 430.5 | 418.7 | 408.1 | 405 | 364.1
2023 | 1890 | 422.9 | 440.7 | 430.4 | 418.6 | 407.7 | 404.8 | 363.8
2024 | 1891 | 422.1 | 440.6 | 430.3 | 418.4 | 407.3 | 404.5 | 363.6
2025 | 1892 | 421.3 | 440.4 | 430.1 | 418.3 | 406.9 | 404.3 | 363.2
2026 | 1893 | 420.6 | 440.2 | 430 | 418.2 | 406.5 | 404.1 | 362.9
2027 | 1894 | 419.9 | 440 | 429.9 | 418.1 | 406.1 | 403.9 | 362.5
2028 | 1895 | 419.2 | 439.8 | 429.7 | 418 | 405.7 | 403.6 | 362.2
2029 | 1896 | 418.5 | 439.6 | 429.6 | 417.8 | 405.3 | 403.3 | 361.8
2030 | 1897 | 417.7 | 439.4 | 429.5 | 417.6 | 404.9 | 403 | 361.5
2031 | 1898 | 416.8 | 439.2 | 429.3 | 417.5 | 404.5 | 402.8 | 361.1
2032 | 1899 | 416 | 439 | 429.2 | 417.3 | 404.1 | 402.5 | 360.7
2033 | 1900 | 415.3 | 438.8 | 429 | 417.2 | 403.8 | 402.2 | 360.3
2034 | 1901 | 414.5 | 438.6 | 428.9 | 417 | 403.4 | 401.8 | 360
2035 | 1902 | 413.7 | 438.4 | 428.7 | 416.8 | 403 | 401.5 | 359.6
2036 | 1903 | 412.9 | 438.2 | 428.6 | 416.6 | 402.7 | 401.2 | 359.3
2037 | 1904 | 412 | 438 | 428.4 | 416.5 | 402.3 | 400.8 | 358.9
2038 | 1905 | 411.3 | 437.8 | 428.2 | 416.3 | 401.9 | 400.5 | 358.6
2039 | 1906 | 410.4 | 437.5 | 428 | 416.1 | 401.5 | 400.2 | 358.2
2040 | 1907 | 409.8 | 437.3 | 427.9 | 416 | 401 | 399.8 | 357.9
2041 | 1908 | 409.1 | 437 | 427.7 | 415.8 | 400.6 | 399.4 | 357.5
2042 | 1909 | 408.3 | 436.8 | 427.5 | 415.6 | 400.2 | 399.1 | 357.1
2043 | 1910 | 407.5 | 436.6 | 427.3 | 415.5 | 399.7 | 398.7 | 356.7
2044 | 1911 | 406.7 | 436.4 | 427.2 | 415.2 | 399.3 | 398.4 | 356.2
2045 | 1912 | 405.9 | 436.1 | 427 | 415 | 398.8 | 398 | 355.8
2046 | 1913 | 405 | 435.9 | 426.9 | 414.8 | 398.4 | 397.6 | 355.5
2047 | 1914 | 404.2 | 435.7 | 426.7 | 414.6 | 397.9 | 397.2 | 355.1
2048 | 1915 | 403.5 | 435.4 | 426.5 | 414.4 | 397.5 | 396.8 | 354.8
2049 | 1916 | 402.7 | 435.2 | 426.3 | 414.2 | 397.1 | 396.4 | 354.4
2050 | 1917 | 402 | 434.9 | 426.1 | 414 | 396.7 | 396 | 354
2051 | 1918 | 401.3 | 434.6 | 425.9 | 413.7 | 396.4 | 395.6 | 353.6
2052 | 1919 | 400.6 | 434.4 | 425.7 | 413.5 | 396 | 395.2 | 353.1
2053 | 1920 | 399.8 | 434.1 | 425.4 | 413.2 | 395.6 | 394.9 | 352.7
2054 | 1921 | 399.2 | 433.8 | 425.2 | 413 | 395.2 | 394.5 | 352.3
2055 | 1922 | 398.5 | 433.6 | 425 | 412.8 | 394.9 | 394 | 352
2056 | 1923 | 397.7 | 433.3 | 424.8 | 412.5 | 394.5 | 393.6 | 351.6
2057 | 1924 | 396.9 | 433 | 424.6 | 412.3 | 394.2 | 393.2 | 351.2
2058 | 1925 | 396.2 | 432.8 | 424.4 | 412 | 393.9 | 392.8 | 350.7
2059 | 1926 | 395.6 | 432.5 | 424.1 | 411.8 | 393.6 | 392.4 | 350.4
2060 | 1927 | 394.9 | 432.2 | 423.9 | 411.5 | 393.3 | 392 | 350
2061 | 1928 | 394.1 | 431.9 | 423.6 | 411.3 | 393 | 391.6 | 349.7
2062 | 1929 | 393.4 | 431.6 | 423.4 | 411 | 392.7 | 391.2 | 349.3
2063 | 1930 | 392.7 | 431.3 | 423.1 | 410.7 | 392.4 | 390.7 | 349
2064 | 1931 | 392 | 431 | 422.9 | 410.5 | 392 | 390.3 | 348.7
2065 | 1932 | 391.3 | 430.8 | 422.6 | 410.2 | 391.6 | 389.9 | 348.3
2066 | 1933 | 390.6 | 430.5 | 422.4 | 409.9 | 391.2 | 389.5 | 347.9
2067 | 1934 | 389.9 | 430.2 | 422.2 | 409.7 | 390.8 | 389.1 | 347.5
2068 | 1935 | 389.1 | 429.9 | 421.9 | 409.4 | 390.4 | 388.6 | 347.1
2069 | 1936 | 388.5 | 429.6 | 421.7 | 409.1 | 389.9 | 388.2 | 346.6
2070 | 1937 | 387.9 | 429.3 | 421.4 | 408.8 | 389.5 | 387.8 | 346.2
2071 | 1938 | 387.2 | 429 | 421.2 | 408.5 | 389 | 387.4 | 345.8
2072 | 1939 | 386.5 | 428.7 | 420.9 | 408.3 | 388.6 | 387 | 345.3
2073 | 1940 | 385.9 | 428.4 | 420.6 | 408 | 388.1 | 386.5 | 344.9
2074 | 1941 | 385.2 | 428 | 420.4 | 407.7 | 387.6 | 386.1 | 344.6
2075 | 1942 | 384.6 | 427.7 | 420.1 | 407.4 | 387.2 | 385.7 | 344.3
2076 | 1943 | 383.9 | 427.4 | 419.9 | 407.2 | 386.7 | 385.3 | 343.9
2077 | 1944 | 382.9 | 427.1 | 419.7 | 406.9 | 386.3 | 384.9 | 343.5
2078 | 1945 | 382.1 | 426.8 | 419.4 | 406.6 | 385.8 | 384.4 | 343
2079 | 1946 | 381.4 | 426.5 | 419.2 | 406.3 | 385.3 | 384 | 342.7
2080 | 1947 | 380.8 | 426.1 | 418.9 | 406 | 384.9 | 383.6 | 342.3
2081 | 1948 | 380.2 | 425.8 | 418.6 | 405.7 | 384.4 | 383.2 | 341.9
2082 | 1949 | 379.6 | 425.5 | 418.3 | 405.5 | 384 | 382.7 | 341.5
2083 | 1950 | 379 | 425.2 | 418.1 | 405.2 | 383.5 | 382.3 | 341.1
2084 | 1951 | 378.4 | 424.8 | 417.8 | 404.9 | 383.1 | 381.8 | 340.7
2085 | 1952 | 377.7 | 424.5 | 417.5 | 404.6 | 382.7 | 381.4 | 340.4
2086 | 1953 | 377.1 | 424.2 | 417.2 | 404.3 | 382.3 | 381 | 340
2087 | 1954 | 376.5 | 423.8 | 416.9 | 404 | 381.9 | 380.5 | 339.7
2088 | 1955 | 375.8 | 423.5 | 416.7 | 403.5 | 381.4 | 380.1 | 339.3
2089 | 1956 | 375.2 | 423.2 | 416.4 | 403.1 | 381 | 379.7 | 338.9
2090 | 1957 | 374.5 | 422.8 | 416 | 402.9 | 380.5 | 379.3 | 338.5
2091 | 1958 | 373.8 | 422.5 | 415.7 | 402.6 | 380.1 | 378.8 | 338.1
2092 | 1959 | 373.1 | 422.2 | 415.4 | 402.3 | 379.6 | 378.4 | 337.7
2093 | 1960 | 372.4 | 421.8 | 415.2 | 402 | 379.2 | 378 | 337.3
2094 | 1961 | 371.7 | 421.5 | 414.8 | 401.7 | 378.8 | 377.5 | 336.8
2095 | 1962 | 371 | 421.1 | 414.5 | 401.5 | 378.3 | 377.1 | 336.4
2096 | 1963 | 370.4 | 420.8 | 414.2 | 401.2 | 377.9 | 376.7 | 335.9
2097 | 1964 | 369.8 | 420.4 | 413.9 | 400.8 | 377.5 | 376.2 | 335.5
2098 | 1965 | 369.2 | 420 | 413.6 | 400.5 | 377 | 375.8 | 335.2
2099 | 1966 | 368.5 | 419.6 | 413.3 | 400.2 | 376.6 | 375.4 | 334.7
2100 | 1967 | 367.9 | 419.3 | 413 | 399.8 | 376.1 | 374.9 | 334.3
2101 | 1968 | 367.3 | 418.9 | 412.7 | 399.5 | 375.6 | 374.5 | 333.9
2102 | 1969 | 366.6 | 418.5 | 412.4 | 399.2 | 375.1 | 374 | 333.6
2103 | 1970 | 366 | 418.2 | 412.1 | 398.9 | 374.7 | 373.6 | 333.2
2104 | 1971 | 365.3 | 417.8 | 411.7 | 398.6 | 374.2 | 373.2 | 332.8
2105 | 1972 | 364.6 | 417.5 | 411.4 | 398.2 | 373.7 | 372.7 | 332.5
2106 | 1973 | 363.9 | 417.1 | 411.1 | 397.9 | 373.3 | 372.3 | 332.1
2107 | 1974 | 363.3 | 416.7 | 410.8 | 397.6 | 372.8 | 371.9 | 331.8
2108 | 1975 | 362.7 | 416.4 | 410.4 | 397.2 | 372.3 | 371.4 | 331.4
2109 | 1976 | 362.2 | 416 | 410.1 | 396.9 | 371.8 | 371 | 331.1
2110 | 1977 | 361.6 | 415.7 | 409.8 | 396.7 | 371.2 | 370.6 | 330.6
2111 | 1978 | 361 | 415.3 | 409.5 | 396.4 | 370.7 | 370.1 | 330.2
2112 | 1979 | 360.4 | 414.9 | 409.1 | 396.1 | 370.2 | 369.7 | 329.9
2113 | 1980 | 359.8 | 414.6 | 408.8 | 395.7 | 369.8 | 369.3 | 329.5
2114 | 1981 | 359.2 | 414.2 | 408.5 | 395.4 | 369.3 | 368.8 | 329.2
2115 | 1982 | 358.6 | 413.8 | 408.2 | 395.1 | 368.9 | 368.4 | 328.9
2116 | 1983 | 358 | 413.5 | 407.8 | 394.7 | 368.4 | 368 | 328.6
2117 | 1984 | 357.3 | 413.1 | 407.4 | 394.4 | 368 | 367.6 | 328.2
2118 | 1985 | 356.6 | 412.7 | 407.1 | 394 | 367.5 | 367.1 | 327.8
2119 | 1986 | 355.9 | 412.3 | 406.8 | 393.6 | 367.1 | 366.7 | 327.5
2120 | 1987 | 355.3 | 411.9 | 406.4 | 393.3 | 366.6 | 366.3 | 327.2
2121 | 1988 | 354.6 | 411.5 | 406.1 | 392.9 | 366.2 | 365.8 | 326.8
2122 | 1989 | 354 | 411.1 | 405.7 | 392.6 | 365.8 | 365.4 | 326.4
2123 | 1990 | 353.5 | 410.8 | 405.3 | 392.2 | 365.3 | 364.9 | 326.1
2124 | 1991 | 352.9 | 410.4 | 405 | 391.8 | 364.8 | 364.5 | 325.8
2125 | 1992 | 352.3 | 410 | 404.6 | 391.4 | 364.2 | 364.1 | 325.4
2126 | 1993 | 351.8 | 409.6 | 404.3 | 391 | 363.7 | 363.6 | 325
2127 | 1994 | 351.1 | 409.2 | 403.9 | 390.7 | 363.2 | 363.2 | 324.7
2128 | 1995 | 350.6 | 408.8 | 403.6 | 390.4 | 362.7 | 362.8 | 324.4
2129 | 1996 | 350 | 408.4 | 403.2 | 390 | 362.2 | 362.4 | 324
2130 | 1997 | 349.4 | 408 | 402.8 | 389.6 | 361.7 | 361.9 | 323.6
2131 | 1998 | 348.8 | 407.7 | 402.5 | 389.3 | 361.2 | 361.5 | 323.3
2132 | 1999 | 348.3 | 407.3 | 402.1 | 388.9 | 360.7 | 361.1 | 322.9
2133 | 2000 | 347.8 | 406.9 | 401.7 | 388.6 | 360.2 | 360.7 | 322.5
2134 | 2001 | 347.3 | 406.5 | 401.4 | 388.2 | 359.8 | 360.2 | 322.1
2135 | 2002 | 346.7 | 406.1 | 401 | 387.9 | 359.4 | 359.8 | 321.8
2136 | 2003 | 346.2 | 405.7 | 400.6 | 387.6 | 359 | 359.3 | 321.5
2137 | 2004 | 345.6 | 405.3 | 400.2 | 387.2 | 358.6 | 358.9 | 321.1
2138 | 2005 | 345.1 | 405 | 399.8 | 386.8 | 358.2 | 358.5 | 320.8
2139 | 2006 | 344.6 | 404.6 | 399.5 | 386.5 | 357.8 | 358.1 | 320.5
2140 | 2007 | 344.2 | 404.2 | 399.1 | 386.1 | 357.4 | 357.7 | 320.2
2141 | 2008 | 343.7 | 403.8 | 398.7 | 385.7 | 357 | 357.3 | 319.9
2142 | 2009 | 343.1 | 403.4 | 398.3 | 385.3 | 356.6 | 356.9 | 319.5
2143 | 2010 | 342.6 | 403 | 398 | 384.9 | 356.2 | 356.5 | 319.1
2144 | 2011 | 342.1 | 402.6 | 397.6 | 384.5 | 355.8 | 356.1 | 318.8
2145 | 2012 | 341.5 | 402.2 | 397.2 | 384.2 | 355.3 | 355.7 | 318.5
2146 | 2013 | 340.9 | 401.8 | 396.8 | 383.8 | 354.9 | 355.2 | 318.2
2147 | 2014 | 340.3 | 401.4 | 396.4 | 383.4 | 354.5 | 354.8 | 317.8
2148 | 2015 | 339.6 | 400.9 | 396 | 383.1 | 354 | 354.4 | 317.5
2149 | 2016 | 339.1 | 400.5 | 395.6 | 382.8 | 353.5 | 353.9 | 317.1
2150 | 2017 | 338.6 | 400.1 | 395.2 | 382.4 | 353 | 353.6 | 316.7
2151 | 2018 | 338 | 399.7 | 394.8 | 382 | 352.5 | 353.1 | 316.3
2152 | 2019 | 337.5 | 399.3 | 394.4 | 381.6 | 352 | 352.7 | 316
2153 | 2020 | 336.9 | 398.9 | 394 | 381.2 | 351.5 | 352.3 | 315.6
2154 | 2021 | 336.3 | 398.5 | 393.6 | 380.8 | 351 | 351.9 | 315.2
2155 | 2022 | 335.7 | 398.1 | 393.2 | 380.4 | 350.5 | 351.5 | 314.8
2156 | 2023 | 335.2 | 397.7 | 392.8 | 380.1 | 350 | 351.1 | 314.5
2157 | 2024 | 334.7 | 397.3 | 392.4 | 379.7 | 349.5 | 350.7 | 314.2
2158 | 2025 | 334.3 | 396.9 | 392 | 379.3 | 349 | 350.3 | 313.8
2159 | 2026 | 333.8 | 396.5 | 391.6 | 378.9 | 348.5 | 349.9 | 313.4
2160 | 2027 | 333.2 | 396.1 | 391.2 | 378.5 | 348.1 | 349.4 | 313
2161 | 2028 | 332.5 | 395.7 | 390.9 | 378.1 | 347.6 | 349 | 312.7
2162 | 2029 | 331.9 | 395.3 | 390.4 | 377.7 | 347.1 | 348.6 | 312.5
2163 | 2030 | 331.3 | 394.9 | 390 | 377.3 | 346.7 | 348.2 | 312.1
2164 | 2031 | 330.6 | 394.5 | 389.6 | 376.9 | 346.2 | 347.8 | 311.8
2165 | 2032 | 330 | 394.1 | 389.3 | 376.5 | 345.6 | 347.4 | 311.4
2166 | 2033 | 329.5 | 393.7 | 388.8 | 376.2 | 345.1 | 347 | 311.1
2167 | 2034 | 329.1 | 393.2 | 388.4 | 375.8 | 344.6 | 346.6 | 310.7
2168 | 2035 | 328.5 | 392.8 | 388 | 375.4 | 344.1 | 346.2 | 310.3
2169 | 2036 | 328 | 392.4 | 387.7 | 375 | 343.5 | 345.8 | 310
2170 | 2037 | 327.6 | 392 | 387.3 | 374.6 | 343 | 345.4 | 309.6
2171 | 2038 | 327.2 | 391.6 | 386.9 | 374.1 | 342.5 | 344.9 | 309.3
2172 | 2039 | 326.6 | 391.1 | 386.5 | 373.7 | 342 | 344.5 | 309
2173 | 2040 | 326.1 | 390.7 | 386.1 | 373.3 | 341.5 | 344.1 | 308.6
2174 | 2041 | 325.7 | 390.3 | 385.7 | 372.9 | 341 | 343.7 | 308.3
2175 | 2042 | 325 | 389.9 | 385.3 | 372.5 | 340.5 | 343.4 | 308
2176 | 2043 | 324.4 | 389.5 | 384.9 | 372 | 339.9 | 343 | 307.6
2177 | 2044 | 323.9 | 389.1 | 384.4 | 371.6 | 339.4 | 342.6 | 307.2
2178 | 2045 | 323.3 | 388.7 | 384 | 371.2 | 338.9 | 342.2 | 306.9
2179 | 2046 | 322.8 | 388.3 | 383.6 | 370.8 | 338.4 | 341.8 | 306.5
2180 | 2047 | 322.3 | 387.8 | 383.2 | 370.5 | 337.9 | 341.4 | 306.2
2181 | 2048 | 321.9 | 387.4 | 382.8 | 370.1 | 337.4 | 341 | 305.8
2182 | 2049 | 321.5 | 387 | 382.4 | 369.6 | 336.9 | 340.6 | 305.4
2183 | 2050 | 321.1 | 386.6 | 382 | 369.2 | 336.4 | 340.2 | 305.1
2184 | 2051 | 320.5 | 386.2 | 381.6 | 368.8 | 336 | 339.8 | 304.9
2185 | 2052 | 320 | 385.7 | 381.2 | 368.4 | 335.5 | 339.4 | 304.5
2186 | 2053 | 319.5 | 385.3 | 380.8 | 368 | 335 | 339 | 304.1
2187 | 2054 | 319 | 384.9 | 380.4 | 367.5 | 334.5 | 338.6 | 303.8
2188 | 2055 | 318.5 | 384.5 | 380 | 367.1 | 334 | 338.2 | 303.4
2189 | 2056 | 318 | 384.1 | 379.6 | 366.7 | 333.5 | 337.8 | 303
2190 | 2057 | 317.5 | 383.6 | 379.2 | 366.3 | 333 | 337.4 | 302.6
2191 | 2058 | 317 | 383.2 | 378.8 | 366 | 332.5 | 337 | 302.3
2192 | 2059 | 316.4 | 382.8 | 378.4 | 365.6 | 332 | 336.6 | 301.9
2193 | 2060 | 315.9 | 382.4 | 378 | 365.1 | 331.5 | 336.2 | 301.6
2194 | 2061 | 315.3 | 382 | 377.6 | 364.7 | 331 | 335.8 | 301.2
2195 | 2062 | 314.7 | 381.5 | 377.2 | 364.4 | 330.5 | 335.4 | 300.8
2196 | 2063 | 314.3 | 381.1 | 376.8 | 364 | 330.1 | 335 | 300.4
2197 | 2064 | 313.9 | 380.7 | 376.4 | 363.6 | 329.6 | 334.6 | 300.1
2198 | 2065 | 313.5 | 380.2 | 376 | 363.2 | 329.2 | 334.2 | 299.8
2199 | 2066 | 312.9 | 379.8 | 375.6 | 362.8 | 328.7 | 333.8 | 299.5
2200 | 2067 | 312.4 | 379.4 | 375.2 | 362.4 | 328.2 | 333.4 | 299.1
2201 | 2068 | 311.9 | 379 | 374.8 | 362 | 327.7 | 333 | 298.8
2202 | 2069 | 311.4 | 378.5 | 374.4 | 361.6 | 327.2 | 332.7 | 298.5
2203 | 2070 | 311 | 378.1 | 374 | 361.2 | 326.7 | 332.3 | 298.1
2204 | 2071 | 310.6 | 377.7 | 373.6 | 360.8 | 326.2 | 331.9 | 297.7
2205 | 2072 | 310.2 | 377.2 | 373.2 | 360.4 | 325.7 | 331.5 | 297.4
2206 | 2073 | 309.7 | 376.8 | 372.8 | 360 | 325.3 | 331.1 | 297.1
2207 | 2074 | 309.2 | 376.4 | 372.4 | 359.6 | 324.8 | 330.7 | 296.8
2208 | 2075 | 308.8 | 375.9 | 372 | 359.2 | 324.4 | 330.3 | 296.5
2209 | 2076 | 308.4 | 375.5 | 371.6 | 358.8 | 323.9 | 330 | 296.2
2210 | 2077 | 308 | 375.1 | 371.2 | 358.4 | 323.5 | 329.6 | 295.8
2211 | 2078 | 307.5 | 374.6 | 370.8 | 357.9 | 323 | 329.2 | 295.4
2212 | 2079 | 306.9 | 374.2 | 370.4 | 357.5 | 322.6 | 328.8 | 295.1
2213 | 2080 | 306.4 | 373.7 | 370 | 357.1 | 322.1 | 328.4 | 294.7
2214 | 2081 | 305.9 | 373.3 | 369.6 | 356.7 | 321.7 | 328 | 294.4
2215 | 2082 | 305.5 | 372.8 | 369.2 | 356.3 | 321.2 | 327.6 | 294
2216 | 2083 | 305 | 372.4 | 368.8 | 355.9 | 320.7 | 327.2 | 293.6
2217 | 2084 | 304.5 | 372 | 368.4 | 355.5 | 320.3 | 326.8 | 293.3
2218 | 2085 | 304 | 371.5 | 368 | 355.1 | 319.9 | 326.5 | 293
2219 | 2086 | 303.6 | 371.1 | 367.5 | 354.7 | 319.5 | 326.1 | 292.7
2220 | 2087 | 303.2 | 370.6 | 367.1 | 354.2 | 319 | 325.7 | 292.3
2221 | 2088 | 302.6 | 370.2 | 366.7 | 353.8 | 318.5 | 325.3 | 292.1
2222 | 2089 | 302.1 | 369.8 | 366.3 | 353.4 | 318 | 324.9 | 291.7
2223 | 2090 | 301.6 | 369.4 | 365.9 | 352.9 | 317.5 | 324.6 | 291.4
2224 | 2091 | 301.1 | 368.9 | 365.5 | 352.5 | 317 | 324.2 | 291.1
2225 | 2092 | 300.6 | 368.5 | 365.1 | 352.1 | 316.5 | 323.8 | 290.7
2226 | 2093 | 300.2 | 368.1 | 364.7 | 351.7 | 316 | 323.4 | 290.4
2227 | 2094 | 299.9 | 367.6 | 364.3 | 351.2 | 315.5 | 323 | 290
2228 | 2095 | 299.5 | 367.2 | 363.9 | 350.8 | 315 | 322.7 | 289.7
2229 | 2096 | 299 | 366.8 | 363.5 | 350.4 | 314.6 | 322.3 | 289.4
2230 | 2097 | 298.6 | 366.3 | 363 | 350 | 314.1 | 321.9 | 289.1
2231 | 2098 | 298.1 | 365.9 | 362.6 | 349.6 | 313.6 | 321.5 | 288.7
2232 | 2099 | 297.8 | 365.5 | 362.2 | 349.2 | 313.2 | 321.1 | 288.4
2233 | 2100 | 297.4 | 365 | 361.8 | 348.8 | 312.8 | 320.7 | 288.1
2234 | 2101 | 297.1 | 364.6 | 361.5 | 348.3 | 312.4 | 320.4 | 287.8
2235 | 2102 | 296.6 | 364.2 | 361.1 | 347.9 | 312 | 320 | 287.4
2236 | 2103 | 296.2 | 363.7 | 360.7 | 347.5 | 311.6 | 319.6 | 287.2
2237 | 2104 | 295.7 | 363.3 | 360.3 | 347 | 311.2 | 319.2 | 286.9
2238 | 2105 | 295.3 | 362.8 | 359.9 | 346.6 | 310.8 | 318.8 | 286.5
2239 | 2106 | 294.7 | 362.4 | 359.5 | 346.2 | 310.3 | 318.5 | 286.2
2240 | 2107 | 294.2 | 362 | 359.1 | 345.7 | 309.9 | 318.1 | 286
2241 | 2108 | 293.9 | 361.5 | 358.7 | 345.3 | 309.4 | 317.7 | 285.6
2242 | 2109 | 293.5 | 361.1 | 358.3 | 344.9 | 309 | 317.3 | 285.2
2243 | 2110 | 293 | 360.7 | 357.8 | 344.5 | 308.5 | 317 | 284.9
2244 | 2111 | 292.6 | 360.3 | 357.5 | 344 | 308.1 | 316.6 | 284.6
2245 | 2112 | 292.2 | 359.8 | 357.1 | 343.6 | 307.7 | 316.2 | 284.2
2246 | 2113 | 291.8 | 359.4 | 356.7 | 343.2 | 307.3 | 315.8 | 283.9
2247 | 2114 | 291.3 | 359 | 356.3 | 342.8 | 306.9 | 315.5 | 283.6
2248 | 2115 | 290.9 | 358.6 | 355.9 | 342.4 | 306.5 | 315.1 | 283.2
2249 | 2116 | 290.5 | 358.1 | 355.5 | 342 | 306 | 314.7 | 282.9
2250 | 2117 | 290.1 | 357.7 | 355.1 | 341.7 | 305.6 | 314.3 | 282.6
2251 | 2118 | 289.7 | 357.3 | 354.7 | 341.3 | 305.2 | 313.9 | 282.2
2252 | 2119 | 289.1 | 356.8 | 354.3 | 340.9 | 304.7 | 313.6 | 281.9
2253 | 2120 | 288.6 | 356.4 | 353.8 | 340.5 | 304.3 | 313.2 | 281.6
2254 | 2121 | 288.1 | 356 | 353.4 | 340.1 | 303.8 | 312.8 | 281.3
2255 | 2122 | 287.6 | 355.6 | 353 | 339.7 | 303.3 | 312.4 | 280.9
2256 | 2123 | 287.2 | 355.1 | 352.6 | 339.2 | 302.9 | 312.1 | 280.6
2257 | 2124 | 286.8 | 354.7 | 352.2 | 338.8 | 302.4 | 311.7 | 280.4
2258 | 2125 | 286.4 | 354.3 | 351.8 | 338.4 | 302 | 311.4 | 280.1
2259 | 2126 | 286 | 353.8 | 351.4 | 338 | 301.6 | 311 | 279.8
2260 | 2127 | 285.7 | 353.4 | 351 | 337.6 | 301.2 | 310.6 | 279.5
2261 | 2128 | 285.4 | 353 | 350.6 | 337.2 | 300.8 | 310.2 | 279.2
2262 | 2129 | 285 | 352.5 | 350.2 | 336.8 | 300.4 | 309.9 | 278.9
2263 | 2130 | 284.6 | 352.1 | 349.8 | 336.4 | 300.1 | 309.5 | 278.6
2264 | 2131 | 284.2 | 351.7 | 349.4 | 336 | 299.7 | 309.1 | 278.3
2265 | 2132 | 283.9 | 351.3 | 349 | 335.5 | 299.4 | 308.8 | 278
2266 | 2133 | 283.4 | 350.8 | 348.6 | 335.1 | 299 | 308.4 | 277.6
2267 | 2134 | 282.9 | 350.4 | 348.2 | 334.7 | 298.7 | 308 | 277.4
2268 | 2135 | 282.4 | 350 | 347.8 | 334.3 | 298.4 | 307.6 | 277.1
2269 | 2136 | 282 | 349.6 | 347.4 | 333.9 | 298 | 307.3 | 276.8
2270 | 2137 | 281.6 | 349.1 | 347 | 333.5 | 297.7 | 306.9 | 276.5
2271 | 2138 | 281.3 | 348.7 | 346.6 | 333.1 | 297.3 | 306.6 | 276.3
2272 | 2139 | 280.8 | 348.3 | 346.2 | 332.7 | 296.8 | 306.2 | 275.9
2273 | 2140 | 280.5 | 347.9 | 345.8 | 332.3 | 296.4 | 305.8 | 275.6
2274 | 2141 | 280.1 | 347.4 | 345.5 | 331.9 | 296 | 305.5 | 275.3
2275 | 2142 | 279.8 | 347 | 345 | 331.5 | 295.7 | 305.1 | 275
2276 | 2143 | 279.5 | 346.6 | 344.6 | 331.1 | 295.3 | 304.7 | 274.7
2277 | 2144 | 279.1 | 346.2 | 344.2 | 330.7 | 294.9 | 304.3 | 274.3
2278 | 2145 | 278.6 | 345.8 | 343.8 | 330.3 | 294.5 | 304 | 274
2279 | 2146 | 278.3 | 345.3 | 343.4 | 329.9 | 294.2 | 303.6 | 273.6
2280 | 2147 | 277.9 | 344.9 | 343 | 329.5 | 293.8 | 303.3 | 273.2
2281 | 2148 | 277.5 | 344.5 | 342.6 | 329.1 | 293.4 | 302.9 | 272.9
2282 | 2149 | 277.2 | 344 | 342.2 | 328.7 | 293.1 | 302.5 | 272.6
2283 | 2150 | 276.8 | 343.6 | 341.8 | 328.3 | 292.6 | 302.2 | 272.2
2284 | 2151 | 276.3 | 343.2 | 341.4 | 327.9 | 292.2 | 301.8 | 271.9
2285 | 2152 | 275.9 | 342.8 | 341 | 327.4 | 291.8 | 301.5 | 271.5
2286 | 2153 | 275.4 | 342.4 | 340.6 | 327 | 291.4 | 301.1 | 271.2
2287 | 2154 | 275 | 341.9 | 340.2 | 326.6 | 291 | 300.7 | 270.8
2288 | 2155 | 274.6 | 341.5 | 339.8 | 326.2 | 290.5 | 300.4 | 270.5
2289 | 2156 | 274.3 | 341.1 | 339.4 | 325.8 | 290.1 | 300 | 270.1
2290 | 2157 | 273.9 | 340.7 | 339 | 325.4 | 289.7 | 299.7 | 269.8
2291 | 2158 | 273.6 | 340.3 | 338.6 | 325 | 289.3 | 299.3 | 269.5
2292 | 2159 | 273.1 | 339.8 | 338.2 | 324.6 | 288.8 | 298.9 | 269.2
2293 | 2160 | 272.8 | 339.4 | 337.8 | 324.2 | 288.4 | 298.6 | 268.9
2294 | 2161 | 272.4 | 339 | 337.4 | 323.8 | 288 | 298.2 | 268.6
2295 | 2162 | 272 | 338.6 | 337 | 323.4 | 287.5 | 297.9 | 268.3
2296 | 2163 | 271.7 | 338.2 | 336.6 | 323 | 287.1 | 297.5 | 268
2297 | 2164 | 271.3 | 337.8 | 336.2 | 322.6 | 286.7 | 297.2 | 267.7
2298 | 2165 | 270.9 | 337.4 | 335.8 | 322.2 | 286.3 | 296.8 | 267.4
2299 | 2166 | 270.5 | 336.9 | 335.4 | 321.8 | 286 | 296.5 | 267
2300 | 2167 | 270.2 | 336.5 | 335 | 321.4 | 285.6 | 296.1 | 266.7
2301 | 2168 | 269.8 | 336.1 | 334.6 | 321 | 285.2 | 295.8 | 266.4
2302 | 2169 | 269.4 | 335.2 | 335.1 | 320.3 | 283.6 | 295.4 | 266.1
2303 | 2170 | 269 | 334.5 | 335.2 | 319.8 | 282.5 | 295 | 265.8
2304 | 2171 | 268.6 | 334.1 | 334.8 | 319.4 | 282.1 | 294.6 | 265.5
2305 | 2172 | 268.2 | 333.7 | 334.4 | 319 | 281.7 | 294.3 | 265.2
2306 | 2173 | 267.7 | 333.3 | 334 | 318.6 | 281.3 | 293.9 | 265
2307 | 2174 | 267.3 | 332.9 | 333.6 | 318.2 | 280.8 | 293.6 | 264.7
2308 | 2175 | 267 | 332.5 | 333.2 | 317.8 | 280.4 | 293.2 | 264.4
2309 | 2176 | 266.6 | 332 | 332.8 | 317.4 | 280 | 292.9 | 264.1
2310 | 2177 | 266.3 | 331.6 | 332.4 | 317 | 279.6 | 292.5 | 263.8
2311 | 2178 | 266 | 331.2 | 332 | 316.6 | 279.2 | 292.2 | 263.5
2312 | 2179 | 265.5 | 330.8 | 331.6 | 316.2 | 278.8 | 291.8 | 263.2
2313 | 2180 | 265.2 | 330.4 | 331.3 | 315.8 | 278.3 | 291.5 | 262.9
2314 | 2181 | 264.8 | 330 | 330.8 | 315.5 | 277.9 | 291.1 | 262.6
2315 | 2182 | 264.4 | 329.5 | 330.5 | 315.1 | 277.5 | 290.8 | 262.3
2316 | 2183 | 264 | 329.1 | 330 | 314.7 | 277.1 | 290.5 | 262
2317 | 2184 | 263.5 | 328.7 | 329.7 | 314.3 | 276.7 | 290.1 | 261.8
2318 | 2185 | 263.1 | 328.3 | 329.3 | 314 | 276.2 | 289.8 | 261.5
2319 | 2186 | 262.7 | 327.8 | 328.9 | 313.6 | 275.8 | 289.4 | 261.2
2320 | 2187 | 262.4 | 327.4 | 328.5 | 313.2 | 275.3 | 289.1 | 261
2321 | 2188 | 262.1 | 327 | 328.1 | 312.8 | 274.8 | 288.7 | 260.7
2322 | 2189 | 261.7 | 326.6 | 327.7 | 312.5 | 274.3 | 288.4 | 260.5
2323 | 2190 | 261.4 | 326.2 | 327.3 | 312.1 | 273.9 | 288 | 260.2
2324 | 2191 | 260.9 | 325.8 | 326.9 | 311.7 | 273.4 | 287.7 | 259.9
2325 | 2192 | 260.6 | 325.4 | 326.5 | 311.4 | 273 | 287.3 | 259.7
2326 | 2193 | 260.3 | 325 | 326.1 | 311 | 272.6 | 287 | 259.4
2327 | 2194 | 259.9 | 324.6 | 325.7 | 310.6 | 272.2 | 286.7 | 259.2
2328 | 2195 | 259.6 | 324.1 | 325.4 | 310.3 | 271.8 | 286.3 | 258.9
2329 | 2196 | 259.2 | 323.7 | 325 | 309.9 | 271.4 | 286 | 258.6
2330 | 2197 | 259 | 323.3 | 324.6 | 309.5 | 271 | 285.6 | 258.3
2331 | 2198 | 258.6 | 322.9 | 324.2 | 309.2 | 270.5 | 285.3 | 258
2332 | 2199 | 258.3 | 322.5 | 323.8 | 308.8 | 270.1 | 285 | 257.7
2333 | 2200 | 258 | 322.1 | 323.4 | 308.5 | 269.8 | 284.6 | 257.4
2334 | 2201 | 257.7 | 321.7 | 323.1 | 308.1 | 269.4 | 284.3 | 257.1
2335 | 2202 | 257.3 | 321.4 | 322.7 | 307.7 | 269 | 284 | 256.8
2336 | 2203 | 257 | 321 | 322.3 | 307.4 | 268.6 | 283.6 | 256.5
2337 | 2204 | 256.6 | 320.6 | 321.9 | 307 | 268.2 | 283.3 | 256.2
2338 | 2205 | 256.3 | 320.2 | 321.5 | 306.6 | 267.9 | 283 | 255.9
2339 | 2206 | 256 | 319.8 | 321.1 | 306.3 | 267.5 | 282.6 | 255.6
2340 | 2207 | 255.6 | 319.4 | 320.7 | 305.9 | 267.1 | 282.3 | 255.3
2341 | 2208 | 255.4 | 319 | 320.4 | 305.6 | 266.8 | 282 | 255
2342 | 2209 | 254.9 | 318.6 | 320 | 305.2 | 266.4 | 281.6 | 254.7
2343 | 2210 | 254.6 | 318.2 | 319.6 | 304.8 | 266 | 281.3 | 254.4
2344 | 2211 | 254.3 | 317.8 | 319.3 | 304.5 | 265.7 | 281 | 254.1
2345 | 2212 | 253.9 | 317.4 | 318.9 | 304.1 | 265.3 | 280.7 | 253.8
2346 | 2213 | 253.6 | 317 | 318.5 | 303.7 | 265 | 280.3 | 253.4
2347 | 2214 | 253.2 | 316.6 | 318.1 | 303.4 | 264.6 | 280 | 253.2
2348 | 2215 | 252.9 | 316.2 | 317.7 | 303 | 264.3 | 279.6 | 252.9
2349 | 2216 | 252.6 | 315.8 | 317.4 | 302.6 | 263.9 | 279.3 | 252.7
2350 | 2217 | 252.4 | 315.4 | 317 | 302.2 | 263.5 | 279 | 252.4
2351 | 2218 | 252.2 | 315 | 316.6 | 301.9 | 263.1 | 278.7 | 252.1
2352 | 2219 | 251.9 | 314.7 | 316.2 | 301.5 | 262.8 | 278.3 | 251.8
2353 | 2220 | 251.6 | 314.3 | 315.9 | 301.2 | 262.4 | 278 | 251.6
2354 | 2221 | 251.2 | 313.9 | 315.5 | 300.8 | 262 | 277.7 | 251.3
2355 | 2222 | 250.9 | 313.5 | 315.1 | 300.4 | 261.7 | 277.3 | 251
2356 | 2223 | 250.6 | 313.1 | 314.7 | 300.1 | 261.3 | 277 | 250.8
2357 | 2224 | 250.2 | 312.7 | 314.4 | 299.7 | 261 | 276.6 | 250.5
2358 | 2225 | 249.7 | 312.3 | 314 | 299.4 | 260.6 | 276.3 | 250.3
2359 | 2226 | 249.4 | 311.9 | 313.6 | 299 | 260.2 | 276 | 250
2360 | 2227 | 249 | 311.5 | 313.2 | 298.7 | 259.8 | 275.6 | 249.7
2361 | 2228 | 248.6 | 311.2 | 312.9 | 298.3 | 259.5 | 275.3 | 249.4
2362 | 2229 | 248.4 | 310.8 | 312.5 | 297.9 | 259.1 | 275 | 249.1
2363 | 2230 | 248.1 | 310.4 | 312.1 | 297.6 | 258.7 | 274.7 | 248.8
2364 | 2231 | 247.8 | 310 | 311.7 | 297.2 | 258.4 | 274.4 | 248.6
2365 | 2232 | 247.5 | 309.6 | 311.4 | 296.9 | 258 | 274 | 248.3
2366 | 2233 | 247.2 | 309.2 | 311 | 296.5 | 257.7 | 273.7 | 248
2367 | 2234 | 246.9 | 308.8 | 310.6 | 296.1 | 257.3 | 273.4 | 247.7
2368 | 2235 | 246.6 | 308.5 | 310.3 | 295.8 | 257 | 273.1 | 247.4
2369 | 2236 | 246.2 | 308.1 | 309.9 | 295.4 | 256.6 | 272.7 | 247
2370 | 2237 | 245.9 | 307.7 | 309.5 | 295.1 | 256.2 | 272.3 | 246.7
2371 | 2238 | 245.7 | 307.3 | 309.1 | 294.7 | 255.8 | 272 | 246.4
2372 | 2239 | 245.4 | 306.9 | 308.8 | 294.3 | 255.5 | 271.7 | 246.2
2373 | 2240 | 245 | 306.5 | 308.4 | 294 | 255.1 | 271.4 | 245.9
2374 | 2241 | 244.7 | 306.2 | 308.1 | 293.6 | 254.7 | 271 | 245.6
2375 | 2242 | 244.4 | 305.8 | 307.7 | 293.3 | 254.3 | 270.7 | 245.2
2376 | 2243 | 244 | 305.4 | 307.3 | 292.9 | 254 | 270.4 | 244.9
2377 | 2244 | 243.7 | 305 | 306.9 | 292.5 | 253.6 | 270 | 244.7
2378 | 2245 | 243.3 | 304.6 | 306.6 | 292.2 | 253.2 | 269.7 | 244.4
2379 | 2246 | 242.9 | 304.2 | 306.2 | 291.8 | 252.9 | 269.4 | 244.1
2380 | 2247 | 242.6 | 303.9 | 305.8 | 291.4 | 252.5 | 269.1 | 243.9
2381 | 2248 | 242.2 | 303.5 | 305.5 | 291.1 | 252.1 | 268.7 | 243.6
2382 | 2249 | 241.9 | 303.1 | 305.1 | 290.7 | 251.7 | 268.4 | 243.3
2383 | 2250 | 241.6 | 302.7 | 304.7 | 290.3 | 251.4 | 268.1 | 243
2384 | 2251 | 241.3 | 302.3 | 304.4 | 289.9 | 251 | 267.8 | 242.8
2385 | 2252 | 241 | 302 | 304 | 289.6 | 250.6 | 267.5 | 242.5
2386 | 2253 | 240.7 | 301.6 | 303.6 | 289.2 | 250.2 | 267.1 | 242.2
2387 | 2254 | 240.4 | 301.2 | 303.3 | 288.9 | 249.8 | 266.8 | 242
2388 | 2255 | 240.1 | 300.8 | 302.9 | 288.5 | 249.5 | 266.5 | 241.8
2389 | 2256 | 239.9 | 300.5 | 302.5 | 288.1 | 249.2 | 266.2 | 241.6
2390 | 2257 | 239.6 | 300.1 | 302.2 | 287.8 | 248.9 | 265.9 | 241.3
2391 | 2258 | 239.3 | 299.7 | 301.8 | 287.4 | 248.5 | 265.5 | 241.1
2392 | 2259 | 238.9 | 299.3 | 301.5 | 287.1 | 248.2 | 265.2 | 240.8
2393 | 2260 | 238.6 | 299 | 301.1 | 286.7 | 247.9 | 264.9 | 240.6
2394 | 2261 | 238.2 | 298.6 | 300.7 | 286.4 | 247.5 | 264.5 | 240.3
2395 | 2262 | 238 | 298.2 | 300.4 | 286 | 247.1 | 264.2 | 240.1
2396 | 2263 | 237.7 | 297.8 | 300 | 285.7 | 246.8 | 263.9 | 239.8
2397 | 2264 | 237.4 | 297.5 | 299.6 | 285.3 | 246.4 | 263.5 | 239.5
2398 | 2265 | 237.1 | 297.1 | 299.3 | 285 | 246.1 | 263.2 | 239.3
2399 | 2266 | 236.8 | 296.7 | 298.9 | 284.6 | 245.8 | 262.9 | 239.1
2400 | 2267 | 236.6 | 296.3 | 298.5 | 284.3 | 245.5 | 262.6 | 238.8
2401 | 2268 | 236.3 | 295.9 | 298.2 | 284 | 245.2 | 262.3 | 238.6
2402 | 2269 | 236 | 295.6 | 297.8 | 283.6 | 244.8 | 262 | 238.3
2403 | 2270 | 235.7 | 295.2 | 297.4 | 283.3 | 244.5 | 261.7 | 238.1
2404 | 2271 | 235.4 | 294.8 | 297.1 | 283 | 244.2 | 261.3 | 237.9
2405 | 2272 | 235.1 | 294.4 | 296.7 | 282.6 | 243.9 | 261 | 237.6
2406 | 2273 | 234.8 | 294.1 | 296.4 | 282.3 | 243.6 | 260.7 | 237.3
2407 | 2274 | 234.4 | 293.7 | 296 | 282 | 243.4 | 260.4 | 237.1
2408 | 2275 | 234.1 | 293.3 | 295.6 | 281.6 | 243.1 | 260.1 | 236.8
2409 | 2276 | 233.9 | 292.9 | 295.3 | 281.3 | 242.8 | 259.7 | 236.6
2410 | 2277 | 233.6 | 292.5 | 294.9 | 281 | 242.6 | 259.4 | 236.4
2411 | 2278 | 233.4 | 292.2 | 294.6 | 280.6 | 242.3 | 259.1 | 236.1
2412 | 2279 | 233.1 | 291.8 | 294.2 | 280.3 | 242.1 | 258.8 | 235.8
2413 | 2280 | 232.8 | 291.4 | 293.9 | 279.9 | 241.8 | 258.5 | 235.6
2414 | 2281 | 232.4 | 291 | 293.5 | 279.6 | 241.5 | 258.2 | 235.3
2415 | 2282 | 232.2 | 290.6 | 293.1 | 279.3 | 241.2 | 257.9 | 235.1
2416 | 2283 | 231.8 | 290.3 | 292.8 | 278.9 | 240.9 | 257.6 | 234.9
2417 | 2284 | 231.5 | 289.9 | 292.4 | 278.6 | 240.7 | 257.3 | 234.6
2418 | 2285 | 231.2 | 289.5 | 292 | 278.3 | 240.4 | 257 | 234.3
2419 | 2286 | 231 | 289.1 | 291.7 | 277.9 | 240.1 | 256.7 | 234.1
2420 | 2287 | 230.7 | 288.8 | 291.3 | 277.6 | 239.9 | 256.4 | 233.9
2421 | 2288 | 230.4 | 288.4 | 291 | 277.2 | 239.7 | 256.1 | 233.7
2422 | 2289 | 230 | 288 | 290.6 | 276.9 | 239.4 | 255.8 | 233.4
2423 | 2290 | 229.7 | 287.6 | 290.2 | 276.6 | 239.1 | 255.5 | 233.1
2424 | 2291 | 229.4 | 287.3 | 289.9 | 276.2 | 238.8 | 255.2 | 232.9
2425 | 2292 | 229 | 286.9 | 289.5 | 275.9 | 238.5 | 254.9 | 232.6
2426 | 2293 | 228.7 | 286.5 | 289.2 | 275.5 | 238.2 | 254.6 | 232.4
2427 | 2294 | 228.5 | 286.1 | 288.8 | 275.2 | 237.9 | 254.2 | 232.1
2428 | 2295 | 228.2 | 285.8 | 288.5 | 274.8 | 237.7 | 253.9 | 231.8
2429 | 2296 | 227.9 | 285.4 | 288.1 | 274.5 | 237.4 | 253.6 | 231.6
2430 | 2297 | 227.7 | 285 | 287.7 | 274.2 | 237.1 | 253.3 | 231.3
2431 | 2298 | 227.4 | 284.7 | 287.4 | 273.8 | 236.8 | 253 | 231.1
2432 | 2299 | 227.2 | 284.3 | 287 | 273.5 | 236.5 | 252.7 | 230.8
2433 | 2300 | 227 | 284 | 286.7 | 273.2 | 236.2 | 252.4 | 230.5
2434 | 2301 | 226.7 | 283.6 | 286.3 | 272.8 | 235.9 | 252.1 | 230.2
2435 | 2302 | 226.4 | 283.2 | 285.9 | 272.5 | 235.6 | 251.8 | 229.9
2436 | 2303 | 226.1 | 282.9 | 285.6 | 272.2 | 235.3 | 251.5 | 229.7
2437 | 2304 | 225.8 | 282.5 | 285.2 | 271.8 | 235 | 251.2 | 229.4
2438 | 2305 | 225.5 | 282.2 | 284.9 | 271.5 | 234.8 | 250.8 | 229.1
2439 | 2306 | 225.3 | 281.8 | 284.5 | 271.2 | 234.5 | 250.5 | 228.9
2440 | 2307 | 224.9 | 281.4 | 284.2 | 270.8 | 234.2 | 250.2 | 228.7
2441 | 2308 | 224.7 | 281.1 | 283.8 | 270.5 | 234 | 249.9 | 228.4
2442 | 2309 | 224.5 | 280.7 | 283.5 | 270.2 | 233.7 | 249.6 | 228.1
2443 | 2310 | 224.3 | 280.4 | 283.1 | 269.8 | 233.5 | 249.4 | 227.9
2444 | 2311 | 224 | 280 | 282.8 | 269.5 | 233.3 | 249.1 | 227.7
2445 | 2312 | 223.7 | 279.6 | 282.4 | 269.2 | 233 | 248.8 | 227.5
2446 | 2313 | 223.4 | 279.3 | 282.1 | 268.9 | 232.7 | 248.5 | 227.3
2447 | 2314 | 223.1 | 278.9 | 281.7 | 268.5 | 232.5 | 248.2 | 227.1
2448 | 2315 | 222.9 | 278.5 | 281.4 | 268.2 | 232.2 | 247.9 | 226.9
2449 | 2316 | 222.7 | 278.2 | 281 | 267.9 | 232 | 247.6 | 226.7
2450 | 2317 | 222.4 | 277.8 | 280.7 | 267.6 | 231.7 | 247.3 | 226.4
2451 | 2318 | 222.1 | 277.4 | 280.3 | 267.3 | 231.5 | 247.1 | 226.2
2452 | 2319 | 221.8 | 277.1 | 280 | 266.9 | 231.2 | 246.8 | 225.9
2453 | 2320 | 221.6 | 276.7 | 279.6 | 266.6 | 231 | 246.5 | 225.8

## C6-7
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38930.5037 | 1 | 0 | 38930.5037 | 1 | 0 | -76 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5043 | 1 | 0 | 38930.5044 | 1 | 0 | -17.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.505 | 1 | 0 | 38930.505 | 1 | 0 | 41.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5057 | 1 | 1 | 38930.5057 | 1 | 0 | 100.5 | 233.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5064 | 1 | 0 | 38930.5064 | 1 | 0 | 159 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5071 | 1 | 0 | 38930.5071 | 1 | 0 | 217.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5077 | 1 | 0 | 38930.5078 | 1 | 0 | 276.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5084 | 1 | 0 | 38930.5084 | 1 | 0 | 335.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5091 | 1 | 0 | 38930.5091 | 1 | 0 | 394 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5098 | 1 | 0 | 38930.5098 | 1 | 0 | 453 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5105 | 1 | 0 | 38930.5105 | 1 | 0 | 511.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5111 | 1 | 0 | 38930.5112 | 1 | 0 | 570.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5118 | 1 | 0 | 38930.5118 | 1 | 0 | 629.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5125 | 1 | 0 | 38930.5125 | 1 | 0 | 688 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5132 | 1 | 0 | 38930.5132 | 1 | 0 | 747 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5139 | 1 | 0 | 38930.5139 | 1 | 0 | 805.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5145 | 1 | 0 | 38930.5146 | 1 | 0 | 864.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5152 | 1 | 0 | 38930.5152 | 1 | 0 | 923.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5159 | 1 | 0 | 38930.5159 | 1 | 0 | 982 | 1115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5166 | 1 | 0 | 38930.5166 | 1 | 0 | 1041 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5173 | 1 | 0 | 38930.5173 | 1 | 0 | 1099.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.518 | 1 | 0 | 38930.518 | 1 | 0 | 1158.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5186 | 1 | 0 | 38930.5186 | 1 | 0 | 1217.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5193 | 1 | 0 | 38930.5193 | 1 | 0 | 1276 | 1409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.52 | 914 | 880 | 38930.52 | 965 | 931 | 1335 | 1468 | 55.7998 | 53.7241 | 58.9133 | 56.8376 | 0.558 | 0.53724 | 0.58913 | 0.56838 | 0.020757 | 0.020757 | 6114.7647 | 6114.7647 | 35.6689
38930.5207 | 1105 | 1083 | 38930.5207 | 1159 | 1149 | 1393.5 | 1526.5 | 67.4603 | 66.1172 | 70.757 | 70.1465 | 0.6746 | 0.66117 | 0.70757 | 0.70147 | 0.013431 | 0.006105 | 2782.8659 | 7614.7641 | 6.8336
38930.5214 | 922 | 884 | 38930.5214 | 1019 | 930 | 1452.5 | 1585.5 | 56.2882 | 53.9683 | 62.21 | 56.7766 | 0.56288 | 0.53968 | 0.6221 | 0.56777 | 0.023199 | 0.054335 | 1296.0585 | 1640.2099 | 32.735
38930.522 | 1051 | 977 | 38930.522 | 1140 | 1180 | 1511 | 1644 | 64.1636 | 59.6459 | 69.5971 | 72.0391 | 0.64164 | 0.59646 | 0.69597 | 0.72039 | 0.045177 | 0.02442 | 362.9425 | 446.9067 | 7.111
38930.5227 | 1132 | 1077 | 38930.5227 | 924 | 900 | 1570 | 1703 | 69.1087 | 65.7509 | 56.4103 | 54.9451 | 0.69109 | 0.65751 | 0.5641 | 0.54945 | 0.033578 | 0.014652 | 498.513 | 759.5779 | 7.875
38930.5234 | 1069 | 992 | 38930.5234 | 1063 | 979 | 1628.5 | 1761.5 | 65.2625 | 60.5617 | 64.8962 | 59.768 | 0.65263 | 0.60562 | 0.64896 | 0.59768 | 0.047009 | 0.051282 | 5050.5108 | 1761.1001 | 4.9622
38930.5241 | 1075 | 995 | 38930.5241 | 948 | 913 | 1687.5 | 1820.5 | 65.6288 | 60.7448 | 57.8755 | 55.7387 | 0.65629 | 0.60745 | 0.57875 | 0.55739 | 0.04884 | 0.021368 | 515.4104 | 819.6263 | 3.8535
38930.5248 | 1142 | 1091 | 38930.5248 | 1187 | 1082 | 1746.5 | 1879.5 | 69.7192 | 66.6056 | 72.4664 | 66.0562 | 0.69719 | 0.66606 | 0.72466 | 0.66056 | 0.031136 | 0.064103 | 417.7729 | 601.3414 | 9.4292
38930.5254 | 1060 | 1145 | 38930.5255 | 1074 | 1002 | 1805 | 1938 | 64.7131 | 69.9023 | 65.5678 | 61.1722 | 0.64713 | 0.69902 | 0.65568 | 0.61172 | 0.051893 | 0.043956 | 904.9494 | 3650.8789 | 7.819
38930.5261 | 1020 | 1016 | 38930.5261 | 1109 | 1147 | 1864 | 1997 | 62.2711 | 62.0269 | 67.7045 | 70.0244 | 0.62271 | 0.62027 | 0.67705 | 0.70024 | 0.002442 | 0.023199 | 196.3986 | 183.881 | 4.9103
38930.5268 | 1107 | 1043 | 38930.5268 | 1192 | 897 | 1922.5 | 2055.5 | 67.5824 | 63.6752 | 72.7717 | 54.7619 | 0.67582 | 0.63675 | 0.72772 | 0.54762 | 0.039072 | 0.1801 | 3.6208 | 3.7626 | 0.12857
38930.5275 | 1184 | 1152 | 38930.5275 | 1037 | 1126 | 1981.5 | 2114.5 | 72.2833 | 70.3297 | 63.3089 | 68.7424 | 0.72283 | 0.7033 | 0.63309 | 0.68742 | 0.019536 | 0.054335 | 436.8989 | 637.734 | 16.7322
38930.5282 | 1170 | 1129 | 38930.5282 | 1097 | 1132 | 2040.5 | 2173.5 | 71.4286 | 68.9255 | 66.9719 | 69.1087 | 0.71429 | 0.68926 | 0.66972 | 0.69109 | 0.025031 | 0.021368 | 14935.9339 | 3254.8936 | 15.982
38930.5288 | 922 | 911 | 38930.5289 | 1109 | 1053 | 2099 | 2232 | 56.2882 | 55.6166 | 67.7045 | 64.2857 | 0.56288 | 0.55617 | 0.67705 | 0.64286 | 0.0067155 | 0.034188 | 591.7297 | 478.7739 | 25.4268
38930.5295 | 1033 | 1047 | 38930.5295 | 1084 | 1022 | 2158 | 2291 | 63.0647 | 63.9194 | 66.1783 | 62.3932 | 0.63065 | 0.63919 | 0.66178 | 0.62393 | 0.008547 | 0.037851 | 81.8255 | 80.1742 | 1.4034
38930.5302 | 973 | 898 | 38930.5302 | 1136 | 1180 | 2216.5 | 2349.5 | 59.4017 | 54.823 | 69.3529 | 72.0391 | 0.59402 | 0.54823 | 0.69353 | 0.72039 | 0.045788 | 0.026862 | 160.4713 | 141.3239 | 15.783
38930.5309 | 1097 | 866 | 38930.5309 | 928 | 910 | 2275.5 | 2408.5 | 66.9719 | 52.8694 | 56.6545 | 55.5556 | 0.66972 | 0.52869 | 0.56654 | 0.55556 | 0.14103 | 0.010989 | 161.1239 | 216.726 | 11.8538
38930.5316 | 977 | 879 | 38930.5316 | 1020 | 1024 | 2334.5 | 2467.5 | 59.6459 | 53.663 | 62.2711 | 62.5153 | 0.59646 | 0.53663 | 0.62271 | 0.62515 | 0.059829 | 0.002442 | 329.7266 | 356.5432 | 22.8354

## C5-7
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38930.5036 | 1 | 0 | 38930.5036 | 1 | 0 | -79 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5043 | 1 | 0 | 38930.5043 | 1 | 0 | -20.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.505 | 1 | 0 | 38930.505 | 1 | 0 | 38.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5057 | 1 | 0 | 38930.5057 | 1 | 0 | 97.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5063 | 1 | 0 | 38930.5064 | 1 | 0 | 156 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.507 | 1 | 0 | 38930.507 | 1 | 0 | 215 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5077 | 1 | 0 | 38930.5077 | 1 | 0 | 274 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5084 | 1 | 0 | 38930.5084 | 1 | 0 | 332.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5091 | 1 | 1 | 38930.5091 | 1 | 0 | 391.5 | 524.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5097 | 1 | 0 | 38930.5098 | 1 | 0 | 450 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5104 | 1 | 0 | 38930.5105 | 1 | 0 | 509 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5111 | 1 | 0 | 38930.5111 | 1 | 0 | 567.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5118 | 1 | 0 | 38930.5118 | 1 | 0 | 626.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5125 | 1 | 0 | 38930.5125 | 1 | 0 | 685.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5131 | 1 | 0 | 38930.5132 | 1 | 0 | 744 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5138 | 1 | 0 | 38930.5139 | 1 | 0 | 803 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5145 | 1 | 0 | 38930.5145 | 1 | 0 | 861.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5152 | 1 | 0 | 38930.5152 | 1 | 0 | 920.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5159 | 1 | 0 | 38930.5159 | 1 | 0 | 979.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5166 | 1 | 0 | 38930.5166 | 1 | 0 | 1038 | 1171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5172 | 1 | 0 | 38930.5173 | 1 | 0 | 1097 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5179 | 1 | 0 | 38930.5179 | 1 | 0 | 1155.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5186 | 1 | 0 | 38930.5186 | 1 | 0 | 1214.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5193 | 1 | 0 | 38930.5193 | 1 | 0 | 1273.5 | 1406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.52 | 906 | 871 | 38930.52 | 1010 | 1101 | 1332 | 1465 | 55.3114 | 53.1746 | 61.6606 | 67.2161 | 0.55311 | 0.53175 | 0.61661 | 0.67216 | 0.021368 | 0.055556 | 915.9844 | 900.0445 | 34.721
38930.5206 | 1119 | 1095 | 38930.5207 | 1032 | 1001 | 1391 | 1524 | 68.315 | 66.8498 | 63.0037 | 61.1111 | 0.68315 | 0.6685 | 0.63004 | 0.61111 | 0.014652 | 0.018926 | 269.2262 | 317.1949 | 7.0115
38930.5213 | 1030 | 945 | 38930.5213 | 1058 | 980 | 1449.5 | 1582.5 | 62.8816 | 57.6923 | 64.591 | 59.8291 | 0.62882 | 0.57692 | 0.64591 | 0.59829 | 0.051893 | 0.047619 | 1355.9957 | 18417.4147 | 14.5264
38930.522 | 929 | 865 | 38930.522 | 1192 | 1168 | 1508.5 | 1641.5 | 56.7155 | 52.8083 | 72.7717 | 71.3065 | 0.56716 | 0.52808 | 0.72772 | 0.71306 | 0.039072 | 0.014652 | 209.9922 | 173.0554 | 23.3742
38930.5227 | 973 | 889 | 38930.5227 | 1099 | 1165 | 1567.5 | 1700.5 | 59.4017 | 54.2735 | 67.094 | 71.1233 | 0.59402 | 0.54274 | 0.67094 | 0.71123 | 0.051282 | 0.040293 | 453.9675 | 531.9412 | 23.768
38930.5234 | 1047 | 964 | 38930.5234 | 1141 | 1086 | 1626 | 1759 | 63.9194 | 58.8523 | 69.6581 | 66.3004 | 0.63919 | 0.58852 | 0.69658 | 0.663 | 0.050672 | 0.033578 | 38.7279 | 36.1105 | 2.8077
38930.524 | 1090 | 1157 | 38930.5241 | 1193 | 901 | 1684.5 | 1817.5 | 66.5446 | 70.6349 | 72.8327 | 55.0061 | 0.66545 | 0.70635 | 0.72833 | 0.55006 | 0.040904 | 0.17827 | 36.6608 | 42.4821 | 3.4526
38930.5247 | 1168 | 1185 | 38930.5247 | 1155 | 1184 | 1743.5 | 1876.5 | 71.3065 | 72.3443 | 70.5128 | 72.2833 | 0.71306 | 0.72344 | 0.70513 | 0.72283 | 0.010379 | 0.017705 | 2752.9249 | 6838.701 | 19.9596
38930.5254 | 945 | 838 | 38930.5254 | 948 | 919 | 1802.5 | 1935.5 | 57.6923 | 51.16 | 57.8755 | 56.105 | 0.57692 | 0.5116 | 0.57875 | 0.56105 | 0.065324 | 0.017705 | 588.5545 | 916.2904 | 35.5068
38930.5261 | 1107 | 1036 | 38930.5261 | 974 | 945 | 1861 | 1994 | 67.5824 | 63.2479 | 59.4628 | 57.6923 | 0.67582 | 0.63248 | 0.59463 | 0.57692 | 0.043346 | 0.017705 | 328.2877 | 440.0186 | 2.3579
38930.5268 | 999 | 896 | 38930.5268 | 1015 | 1110 | 1920 | 2053 | 60.989 | 54.7009 | 61.9658 | 67.7656 | 0.60989 | 0.54701 | 0.61966 | 0.67766 | 0.062882 | 0.057998 | 817.3282 | 2690.6749 | 23.4607
38930.5274 | 1190 | 1160 | 38930.5275 | 1156 | 1187 | 1978.5 | 2111.5 | 72.6496 | 70.8181 | 70.5739 | 72.4664 | 0.7265 | 0.70818 | 0.70574 | 0.72466 | 0.018315 | 0.018926 | 6808.4448 | 7054.6683 | 20.1438
38930.5281 | 1187 | 864 | 38930.5281 | 1021 | 929 | 2037.5 | 2170.5 | 72.4664 | 52.7473 | 62.3321 | 56.7155 | 0.72466 | 0.52747 | 0.62332 | 0.56716 | 0.19719 | 0.056166 | 76.336 | 97.0695 | 3.5357
38930.5288 | 987 | 891 | 38930.5288 | 1148 | 1099 | 2096.5 | 2229.5 | 60.2564 | 54.3956 | 70.0855 | 67.094 | 0.60256 | 0.54396 | 0.70085 | 0.67094 | 0.058608 | 0.029915 | 219.3067 | 213.4411 | 17.9618
38930.5295 | 994 | 993 | 38930.5295 | 1172 | 1188 | 2155 | 2288 | 60.6838 | 60.6227 | 71.5507 | 72.5275 | 0.60684 | 0.60623 | 0.71551 | 0.72527 | 0.0006105 | 0.009768 | 847.4207 | 757.7254 | 11.2112
38930.5302 | 928 | 870 | 38930.5302 | 995 | 918 | 2214 | 2347 | 56.6545 | 53.1136 | 60.7448 | 56.044 | 0.56654 | 0.53114 | 0.60745 | 0.56044 | 0.035409 | 0.047009 | 24534.0473 | 1636.2642 | 34.1237
38930.5308 | 988 | 904 | 38930.5309 | 1048 | 979 | 2272.5 | 2405.5 | 60.3175 | 55.1893 | 63.9805 | 59.768 | 0.60317 | 0.55189 | 0.6398 | 0.59768 | 0.051282 | 0.042125 | 1156.1563 | 6793.4624 | 24.0944
38930.5315 | 1063 | 985 | 38930.5315 | 991 | 984 | 2331.5 | 2464.5 | 64.8962 | 60.1343 | 60.5006 | 60.0733 | 0.64896 | 0.60134 | 0.60501 | 0.60073 | 0.047619 | 0.0042735 | 259.1129 | 301.0055 | 4.9549

## C5-6
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38930.5036 | 1 | 0 | 38930.5036 | 1 | 0 | -81.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5043 | 1 | 0 | 38930.5043 | 1 | 0 | -23 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.505 | 1 | 0 | 38930.505 | 1 | 0 | 36 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5056 | 1 | 0 | 38930.5056 | 1 | 0 | 94.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5063 | 1 | 0 | 38930.5063 | 1 | 0 | 153.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.507 | 1 | 0 | 38930.507 | 1 | 0 | 212.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5077 | 1 | 0 | 38930.5077 | 1 | 0 | 271 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5084 | 1 | 0 | 38930.5084 | 1 | 0 | 330 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.509 | 1 | 0 | 38930.5091 | 1 | 0 | 388.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5097 | 1 | 0 | 38930.5097 | 1 | 0 | 447.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5104 | 1 | 0 | 38930.5104 | 1 | 0 | 506 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5111 | 1 | 0 | 38930.5111 | 1 | 0 | 565 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5118 | 1 | 0 | 38930.5118 | 1 | 0 | 623.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5124 | 1 | 0 | 38930.5125 | 1 | 0 | 682.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5131 | 1 | 0 | 38930.5131 | 1 | 0 | 741.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5138 | 1 | 0 | 38930.5138 | 1 | 0 | 800 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5145 | 1 | 0 | 38930.5145 | 1 | 0 | 859 | 992 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5152 | 1 | 0 | 38930.5152 | 1 | 0 | 917.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5158 | 1 | 0 | 38930.5159 | 1 | 0 | 976.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5165 | 1 | 0 | 38930.5165 | 1 | 0 | 1035.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5172 | 1 | 0 |  | 1 | 0 | 1093 | 1226 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5179 | 1 | 0 | 38930.5179 | 1 | 0 | 1153 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5186 | 1 | 0 | 38930.5186 | 1 | 0 | 1211.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5192 | 1 | 0 | 38930.5193 | 1 | 0 | 1270.5 | 1403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5199 | 1147 | 1125 | 38930.5199 | 1118 | 1171 | 1329.5 | 1462.5 | 70.0244 | 68.6813 | 68.254 | 71.4896 | 0.70024 | 0.68681 | 0.68254 | 0.7149 | 0.013431 | 0.032357 | 943.8716 | 1400.1845 | 13.1896
38930.5206 | 1168 | 1151 | 38930.5206 | 1129 | 1106 | 1388 | 1521 | 71.3065 | 70.2686 | 68.9255 | 67.5214 | 0.71306 | 0.70269 | 0.68926 | 0.67521 | 0.010379 | 0.014042 | 3520.7736 | 11695.657 | 17.744
38930.5213 | 967 | 947 | 38930.5213 | 1056 | 1076 | 1447 | 1580 | 59.0354 | 57.8144 | 64.4689 | 65.6899 | 0.59035 | 0.57814 | 0.64469 | 0.6569 | 0.01221 | 0.01221 | 8743.5948 | 13738.5076 | 20.864
38930.522 | 1104 | 1073 | 38930.522 | 1141 | 1106 | 1505.5 | 1638.5 | 67.3993 | 65.5067 | 69.6581 | 67.5214 | 0.67399 | 0.65507 | 0.69658 | 0.67521 | 0.018926 | 0.021368 | 2774.7216 | 20001.008 | 5.9331
38930.5227 | 958 | 917 | 38930.5227 | 1011 | 1038 | 1564.5 | 1697.5 | 58.486 | 55.9829 | 61.7216 | 63.37 | 0.58486 | 0.55983 | 0.61722 | 0.6337 | 0.025031 | 0.016484 | 1571.739 | 2822.6887 | 25.0683
38930.5233 | 1020 | 980 | 38930.5233 | 1027 | 951 | 1623 | 1756 | 62.2711 | 59.8291 | 62.6984 | 58.0586 | 0.62271 | 0.59829 | 0.62698 | 0.58059 | 0.02442 | 0.046398 | 821.7402 | 1053.6179 | 10.533
38930.524 | 1054 | 968 | 38930.524 | 1147 | 1096 | 1682 | 1815 | 64.3468 | 59.0965 | 70.0244 | 66.9109 | 0.64347 | 0.59096 | 0.70024 | 0.66911 | 0.052503 | 0.031136 | 112.4112 | 113.0716 | 4.9899
38930.5247 | 1194 | 1174 | 38930.5247 | 943 | 833 | 1740.5 | 1873.5 | 72.8938 | 71.6728 | 57.5702 | 50.8547 | 0.72894 | 0.71673 | 0.5757 | 0.50855 | 0.01221 | 0.067155 | 92.0467 | 119.9884 | 11.8462
38930.5254 | 1018 | 1018 | 38930.5254 | 977 | 966 | 1799.5 | 1932.5 | 62.149 | 62.149 | 59.6459 | 58.9744 | 0.62149 | 0.62149 | 0.59646 | 0.58974 | 0 | 0.0067155 | 2326.9925 | 2163.3197 | 7.2315
38930.5261 | 1009 | 1001 | 38930.5261 | 940 | 820 | 1858.5 | 1991.5 | 61.5995 | 61.1111 | 57.3871 | 50.0611 | 0.616 | 0.61111 | 0.57387 | 0.50061 | 0.004884 | 0.07326 | 428.2421 | 400.7162 | 8.2363
38930.5267 | 1127 | 1065 | 38930.5267 | 1021 | 1113 | 1917 | 2050 | 68.8034 | 65.0183 | 62.3321 | 67.9487 | 0.68803 | 0.65018 | 0.62332 | 0.67949 | 0.037851 | 0.056166 | 358.6864 | 500.2406 | 6.1805
38930.5274 | 1195 | 1176 | 38930.5274 | 1174 | 1187 | 1976 | 2109 | 72.9548 | 71.7949 | 71.6728 | 72.4664 | 0.72955 | 0.71795 | 0.71673 | 0.72466 | 0.0116 | 0.0079365 | 20908.4766 | 8049.6446 | 21.6679
38930.5281 | 1123 | 1062 | 38930.5281 | 1089 | 1124 | 2035 | 2168 | 68.5592 | 64.8352 | 66.4835 | 68.6203 | 0.68559 | 0.64835 | 0.66484 | 0.6862 | 0.037241 | 0.021368 | 711.153 | 1357.8243 | 6.3129
38930.5288 | 1139 | 834 | 38930.5288 | 1183 | 1186 | 2093.5 | 2226.5 | 69.536 | 50.9158 | 72.2222 | 72.4054 | 0.69536 | 0.50916 | 0.72222 | 0.72405 | 0.1862 | 0.0018315 | 29.6158 | 27.9504 | 3.6675
38930.5295 | 1134 | 1179 | 38930.5295 | 1176 | 1142 | 2152.5 | 2285.5 | 69.2308 | 71.978 | 71.7949 | 69.7192 | 0.69231 | 0.71978 | 0.71795 | 0.69719 | 0.027473 | 0.020757 | 20628.7167 | 2928.8948 | 16.4018
38930.5301 | 1111 | 1062 | 38930.5302 | 1136 | 1092 | 2211 | 2344 | 67.8266 | 64.8352 | 69.3529 | 66.6667 | 0.67827 | 0.64835 | 0.69353 | 0.66667 | 0.029915 | 0.026862 | 15769.0727 | 2490.2884 | 5.4298
38930.5308 | 1088 | 1026 | 38930.5308 | 1196 | 1185 | 2270 | 2403 | 66.4225 | 62.6374 | 73.0159 | 72.3443 | 0.66422 | 0.62637 | 0.73016 | 0.72344 | 0.037851 | 0.0067155 | 605.3341 | 955.9189 | 0.086471
38930.5315 | 1020 | 937 | 38930.5315 | 1001 | 900 | 2328.5 | 2461.5 | 62.2711 | 57.2039 | 61.1111 | 54.9451 | 0.62271 | 0.57204 | 0.61111 | 0.54945 | 0.050672 | 0.061661 | 15908.7649 | 1230.7984 | 15.3998

## C4-7
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38930.5036 | 1 | 0 | 38930.5036 | 1 | 0 | -84.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5042 | 1 | 0 | 38930.5043 | 1 | 0 | -25.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5049 | 1 | 0 | 38930.5049 | 1 | 0 | 33 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5056 | 1 | 0 | 38930.5056 | 1 | 0 | 91.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5063 | 1 | 0 | 38930.5063 | 1 | 0 | 150.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.507 | 1 | 0 | 38930.507 | 1 | 0 | 209.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5077 | 1 | 1 | 38930.5077 | 1 | 0 | 268.5 | 401.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5083 | 1 | 0 | 38930.5083 | 1 | 0 | 327 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.509 | 1 | 0 | 38930.509 | 1 | 0 | 385.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5097 | 1 | 0 | 38930.5097 | 1 | 0 | 444.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5104 | 1 | 0 | 38930.5104 | 1 | 0 | 503.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.511 | 1 | 0 | 38930.5111 | 1 | 0 | 562 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5117 | 1 | 0 | 38930.5117 | 1 | 0 | 621 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5124 | 1 | 0 | 38930.5124 | 1 | 0 | 679.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5131 | 1 | 0 | 38930.5131 | 1 | 0 | 738.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5138 | 1 | 0 | 38930.5138 | 1 | 0 | 797.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5144 | 1 | 0 | 38930.5145 | 1 | 0 | 856 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5151 | 1 | 0 | 38930.5152 | 1 | 0 | 915 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5158 | 1 | 0 | 38930.5158 | 1 | 0 | 973.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5165 | 1 | 0 | 38930.5165 | 1 | 0 | 1032.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5172 | 1 | 0 | 38930.5172 | 1 | 0 | 1091.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5178 | 1 | 0 | 38930.5179 | 1 | 0 | 1150 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5185 | 1 | 0 | 38930.5186 | 1 | 0 | 1209 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5192 | 1 | 0 | 38930.5192 | 1 | 0 | 1267.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5199 | 71 | 69 | 38930.5199 | 224 | 237 | 1326.5 | 1459.5 | 4.3346 | 4.2125 | 13.6752 | 14.4689 | 0.043346 | 0.042125 | 0.13675 | 0.14469 | 0.001221 | 0.0079365 | 133322.1205 | 14732.3769 | 2840.1708
38930.5206 | 1040 | 1108 | 38930.5206 | 1140 | 1124 | 1385.5 | 1518.5 | 63.4921 | 67.6435 | 69.5971 | 68.6203 | 0.63492 | 0.67643 | 0.69597 | 0.6862 | 0.041514 | 0.009768 | 415.6339 | 582.6528 | 2.6946
38930.5212 | 9 | 13 | 38930.5213 | 7 | 11 | 1444 | 1577 | 0.54945 | 0.79365 | 0.42735 | 0.67155 | 0.0054945 | 0.0079365 | 0.0042735 | 0.0067155 | 0.002442 | 0.002442 | 52925.5 | 52925.5 | 16054.4352
38930.5219 | 5 | 11 | 38930.5219 | 5 | 16 | 1502.5 | 1635.5 | 0.30525 | 0.67155 | 0.30525 | 0.9768 | 0.0030525 | 0.0067155 | 0.0030525 | 0.009768 | 0.003663 | 0.0067155 | 35471.6193 | 19242.7247 | 18965.2601
38930.5226 | 5 | 9 | 38930.5226 | 5 | 9 | 1561.5 | 1694.5 | 0.30525 | 0.54945 | 0.30525 | 0.54945 | 0.0030525 | 0.0054945 | 0.0030525 | 0.0054945 | 0.002442 | 0.002442 | 52925.5 | 52925.5 | 23278.461
38930.5233 | 6 | 9 | 38930.5233 | 7 | 9 | 1620.5 | 1753.5 | 0.3663 | 0.54945 | 0.42735 | 0.54945 | 0.003663 | 0.0054945 | 0.0042735 | 0.0054945 | 0.0018315 | 0.001221 | 70433.381 | 105978.0958 | 23289.3577
38930.524 | 735 | 579 | 38930.524 | 637 | 619 | 1679 | 1812 | 44.8718 | 35.348 | 38.8889 | 37.79 | 0.44872 | 0.35348 | 0.38889 | 0.3779 | 0.095238 | 0.010989 | 762.1934 | 2334.9951 | 132.3326
38930.5247 | 1116 | 1090 | 38930.5247 | 937 | 838 | 1738 | 1871 | 68.1319 | 66.5446 | 57.2039 | 51.16 | 0.68132 | 0.66545 | 0.57204 | 0.5116 | 0.015873 | 0.06044 | 335.0366 | 401.3471 | 6.8288
38930.5253 | 922 | 1022 | 38930.5253 | 897 | 865 | 1796.5 | 1929.5 | 56.2882 | 62.3932 | 54.7619 | 52.8083 | 0.56288 | 0.62393 | 0.54762 | 0.52808 | 0.06105 | 0.019536 | 634.7433 | 1166.1602 | 15.232
38930.526 | 953 | 1046 | 38930.526 | 1067 | 1003 | 1855.5 | 1988.5 | 58.1807 | 63.8584 | 65.1404 | 61.2332 | 0.58181 | 0.63858 | 0.6514 | 0.61233 | 0.056777 | 0.039072 | 541.4916 | 862.8456 | 9.7685
38930.5267 | 1060 | 1116 | 38930.5267 | 1039 | 1068 | 1914.5 | 2047.5 | 64.7131 | 68.1319 | 63.431 | 65.2015 | 0.64713 | 0.68132 | 0.63431 | 0.65201 | 0.034188 | 0.017705 | 219.2981 | 263.0974 | 4.0891
38930.5274 | 924 | 828 | 38930.5274 | 1022 | 956 | 1973 | 2106 | 56.4103 | 50.5495 | 62.3932 | 58.3639 | 0.5641 | 0.50549 | 0.62393 | 0.58364 | 0.058608 | 0.040293 | 1009.5376 | 3801.8853 | 42.484
38930.5281 | 1106 | 1129 | 38930.5281 | 997 | 925 | 2032 | 2165 | 67.5214 | 68.9255 | 60.8669 | 56.4713 | 0.67521 | 0.68926 | 0.60867 | 0.56471 | 0.014042 | 0.043956 | 142.9883 | 165.7206 | 6.7382
38930.5287 | 1028 | 1058 | 38930.5287 | 999 | 918 | 2090.5 | 2223.5 | 62.7595 | 64.591 | 60.989 | 56.044 | 0.62759 | 0.64591 | 0.60989 | 0.56044 | 0.018315 | 0.049451 | 454.288 | 506.6088 | 2.1329
38930.5294 | 928 | 916 | 38930.5294 | 1066 | 1018 | 2149.5 | 2282.5 | 56.6545 | 55.9219 | 65.0794 | 62.149 | 0.56654 | 0.55922 | 0.65079 | 0.62149 | 0.007326 | 0.029304 | 981.5756 | 842.4824 | 26.2529
38930.5301 | 1047 | 775 | 38930.5301 | 902 | 830 | 2208.5 | 2341.5 | 63.9194 | 47.3138 | 55.0672 | 50.6716 | 0.63919 | 0.47314 | 0.55067 | 0.50672 | 0.16606 | 0.043956 | 236.7425 | 434.6933 | 30.5281
38930.5308 | 1081 | 1043 |  | 979 | 912 | 2266 | 2399 | 65.9951 | 63.6752 | 59.768 | 55.6777 | 0.65995 | 0.63675 | 0.59768 | 0.55678 | 0.023199 | 0.040904 | 817.9534 | 1182.9286 | 0.97068
38930.5315 | 915 | 827 | 38930.5315 | 1056 | 993 | 2326 | 2459 | 55.8608 | 50.4884 | 64.4689 | 60.6227 | 0.55861 | 0.50488 | 0.64469 | 0.60623 | 0.053724 | 0.038462 | 1087.8674 | 3737.7598 | 43.6944

## C4-6
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38930.5035 | 1 | 0 | 38930.5035 | 1 | 0 | -87.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5042 | 1 | 0 | 38930.5042 | 1 | 0 | -28.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5049 | 1 | 0 | 38930.5049 | 1 | 0 | 30.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5056 | 1 | 0 | 38930.5056 | 1 | 0 | 89 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5062 | 1 | 0 | 38930.5063 | 1 | 0 | 147.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5069 | 1 | 0 | 38930.5069 | 1 | 0 | 206.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5076 | 1 | 0 | 38930.5076 | 1 | 0 | 265.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5083 | 1 | 0 | 38930.5083 | 1 | 0 | 324 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.509 | 1 | 0 | 38930.509 | 1 | 0 | 383 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5097 | 1 | 0 | 38930.5097 | 1 | 0 | 441.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5103 | 1 | 0 | 38930.5103 | 1 | 0 | 500.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.511 | 1 | 0 | 38930.511 | 1 | 0 | 559.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5117 | 1 | 0 | 38930.5117 | 1 | 0 | 618 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5124 | 1 | 0 | 38930.5124 | 1 | 0 | 677 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5131 | 1 | 0 | 38930.5131 | 1 | 0 | 735.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5137 | 1 | 0 | 38930.5137 | 1 | 0 | 794.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5144 | 1 | 0 | 38930.5144 | 1 | 0 | 853.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5151 | 1 | 0 | 38930.5151 | 1 | 0 | 912 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5158 | 1 | 0 | 38930.5158 | 1 | 0 | 971 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5165 | 1 | 0 | 38930.5165 | 1 | 0 | 1029.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5171 | 1 | 0 | 38930.5172 | 1 | 0 | 1088.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5178 | 1 | 0 | 38930.5178 | 1 | 0 | 1147.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5185 | 1 | 0 | 38930.5185 | 1 | 0 | 1206 | 1339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5192 | 1 | 0 | 38930.5192 | 1 | 0 | 1265 | 1398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5199 | 168 | 166 | 38930.5199 | 162 | 160 | 1323.5 | 1456.5 | 10.2564 | 10.1343 | 9.8901 | 9.768 | 0.10256 | 0.10134 | 0.098901 | 0.09768 | 0.001221 | 0.001221 | 105551 | 105551 | 1070.6844
38930.5205 | 895 | 860 | 38930.5206 | 928 | 893 | 1382.5 | 1515.5 | 54.6398 | 52.5031 | 56.6545 | 54.5177 | 0.5464 | 0.52503 | 0.56654 | 0.54518 | 0.021368 | 0.021368 | 5937.2 | 5937.2 | 40.9407
38930.5212 | 10 | 15 | 38930.5212 | 36 | 41 | 1441 | 1574 | 0.6105 | 0.91575 | 2.1978 | 2.5031 | 0.006105 | 0.0091575 | 0.021978 | 0.025031 | 0.0030525 | 0.0030525 | 42360.4 | 42360.4 | 13887.3495
38930.5219 | 5 | 25 | 38930.5219 | 5 | 21 | 1500 | 1633 | 0.30525 | 1.5263 | 0.30525 | 1.2821 | 0.0030525 | 0.015263 | 0.0030525 | 0.012821 | 0.01221 | 0.009768 | 10639.8007 | 13339.6801 | 8270.0839
38930.5226 | 6 | 10 | 38930.5226 | 5 | 10 | 1559 | 1692 | 0.3663 | 0.6105 | 0.30525 | 0.6105 | 0.003663 | 0.006105 | 0.0030525 | 0.006105 | 0.002442 | 0.0030525 | 52988.5219 | 42320.1332 | 20920.7655
38930.5233 | 5 | 10 | 38930.5233 | 6 | 9 | 1617.5 | 1750.5 | 0.30525 | 0.6105 | 0.3663 | 0.54945 | 0.0030525 | 0.006105 | 0.003663 | 0.0054945 | 0.0030525 | 0.0018315 | 42279.9431 | 70735.9111 | 20950.582
38930.5239 | 564 | 569 | 38930.524 | 687 | 667 | 1676.5 | 1809.5 | 34.4322 | 34.7375 | 41.9414 | 40.7204 | 0.34432 | 0.34737 | 0.41941 | 0.4072 | 0.0030525 | 0.01221 | 43045.9658 | 40600.0928 | 171.8123
38930.5246 | 1058 | 1000 | 38930.5246 | 921 | 824 | 1735.5 | 1868.5 | 64.591 | 61.0501 | 56.2271 | 50.3053 | 0.64591 | 0.6105 | 0.56227 | 0.50305 | 0.035409 | 0.059219 | 1556.2123 | 10210.2364 | 5.4486
38930.5253 | 882 | 843 | 38930.5253 | 1046 | 989 | 1794 | 1927 | 53.8462 | 51.4652 | 63.8584 | 60.3785 | 0.53846 | 0.51465 | 0.63858 | 0.60379 | 0.02381 | 0.034799 | 7453.4653 | 3749.3455 | 44.8327
38930.526 | 927 | 824 | 38930.526 | 1053 | 987 | 1852.5 | 1985.5 | 56.5934 | 50.3053 | 64.2857 | 60.2564 | 0.56593 | 0.50305 | 0.64286 | 0.60256 | 0.062882 | 0.040293 | 810.0961 | 1898.4049 | 41.736
38930.5267 | 964 | 955 | 38930.5267 | 1078 | 1019 | 1911.5 | 2044.5 | 58.8523 | 58.3028 | 65.812 | 62.21 | 0.58852 | 0.58303 | 0.65812 | 0.6221 | 0.0054945 | 0.03602 | 459.5248 | 396.1911 | 16.2218
38930.5273 | 1136 | 1115 | 38930.5274 | 1086 | 1038 | 1970.5 | 2103.5 | 69.3529 | 68.0708 | 66.3004 | 63.37 | 0.69353 | 0.68071 | 0.663 | 0.6337 | 0.012821 | 0.029304 | 481.8106 | 613.3757 | 10.6402
38930.528 | 899 | 801 | 38930.528 | 968 | 818 | 2029 | 2162 | 54.884 | 48.9011 | 59.0965 | 49.9389 | 0.54884 | 0.48901 | 0.59096 | 0.49939 | 0.059829 | 0.091575 | 9257.4386 | 943.6184 | 46.6223
38930.5287 | 1096 | 1051 | 38930.5287 | 1134 | 1128 | 2088 | 2221 | 66.9109 | 64.1636 | 69.2308 | 68.8645 | 0.66911 | 0.64164 | 0.69231 | 0.68864 | 0.027473 | 0.003663 | 502.9022 | 668.4468 | 2.8124
38930.5294 | 1105 | 795 | 38930.5294 | 938 | 849 | 2146.5 | 2279.5 | 67.4603 | 48.5348 | 57.265 | 51.8315 | 0.6746 | 0.48535 | 0.57265 | 0.51832 | 0.18926 | 0.054335 | 173.59 | 293.6937 | 19.9889
38930.5301 | 1010 | 1034 | 38930.5301 | 878 | 804 | 2205.5 | 2338.5 | 61.6606 | 63.1258 | 53.602 | 49.0842 | 0.61661 | 0.63126 | 0.53602 | 0.49084 | 0.014652 | 0.045177 | 1132.6077 | 1408.9565 | 6.2327
38930.5308 | 1122 | 1028 | 38930.5308 | 1062 | 1113 | 2264.5 | 2397.5 | 68.4982 | 62.7595 | 64.8352 | 67.9487 | 0.68498 | 0.62759 | 0.64835 | 0.67949 | 0.057387 | 0.031136 | 221.2354 | 290.438 | 2.6759
38930.5314 | 909 | 818 | 38930.5314 | 966 | 887 | 2323 | 2456 | 55.4945 | 49.9389 | 58.9744 | 54.1514 | 0.55495 | 0.49939 | 0.58974 | 0.54151 | 0.055556 | 0.04823 | 1648.6958 | 4551.6849 | 46.1762

## C4-5
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38930.5035 | 1 | 0 | 38930.5035 | 1 | 0 | -90 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5042 | 1 | 0 | 38930.5042 | 1 | 0 | -31.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5049 | 1 | 0 | 38930.5049 | 1 | 0 | 27.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5055 | 1 | 0 | 38930.5056 | 1 | 0 | 86.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5062 | 1 | 0 | 38930.5062 | 1 | 0 | 145 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5069 | 1 | 0 | 38930.5069 | 1 | 0 | 204 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5076 | 1 | 0 | 38930.5076 | 1 | 0 | 262.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5083 | 1 | 0 | 38930.5083 | 1 | 0 | 321.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5089 | 1 | 0 | 38930.509 | 1 | 0 | 380 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5096 | 1 | 0 | 38930.5096 | 1 | 0 | 439 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5103 | 1 | 0 | 38930.5103 | 1 | 0 | 497.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.511 | 1 | 0 | 38930.511 | 1 | 0 | 556.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5117 | 1 | 0 | 38930.5117 | 1 | 0 | 615.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5123 | 1 | 0 | 38930.5124 | 1 | 0 | 674 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.513 | 1 | 0 | 38930.513 | 1 | 0 | 733 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5137 | 1 | 0 | 38930.5137 | 1 | 0 | 791.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5144 | 1 | 0 | 38930.5144 | 1 | 0 | 850.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5151 | 1 | 0 | 38930.5151 | 1 | 0 | 909.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5157 | 1 | 0 | 38930.5158 | 1 | 0 | 968 | 1101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5164 | 1 | 0 | 38930.5164 | 1 | 0 | 1027 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5171 | 1 | 0 | 38930.5171 | 1 | 0 | 1085.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5178 | 1 | 0 | 38930.5178 | 1 | 0 | 1144.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5185 | 1 | 0 | 38930.5185 | 1 | 0 | 1203 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5191 | 1 | 0 | 38930.5192 | 1 | 0 | 1262 | 1395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5198 | 1029 | 996 | 38930.5198 | 946 | 909 | 1321 | 1454 | 62.8205 | 60.8059 | 57.7534 | 55.4945 | 0.62821 | 0.60806 | 0.57753 | 0.55495 | 0.020147 | 0.022589 | 21673.6573 | 3557.3405 | 8.5957
38930.5205 | 309 | 316 | 38930.5205 | 390 | 378 | 1379.5 | 1512.5 | 18.8645 | 19.2918 | 23.8095 | 23.0769 | 0.18864 | 0.19292 | 0.2381 | 0.23077 | 0.0042735 | 0.007326 | 36145.4098 | 15729.2748 | 467.9176
38930.5212 | 12 | 24 | 38930.5212 | 11 | 20 | 1438.5 | 1571.5 | 0.7326 | 1.4652 | 0.67155 | 1.221 | 0.007326 | 0.014652 | 0.0067155 | 0.01221 | 0.007326 | 0.0054945 | 17657.8042 | 23653.4548 | 8617.8164
38930.5219 | 6 | 33 | 38930.5219 | 5 | 28 | 1497.5 | 1630.5 | 0.3663 | 2.0147 | 0.30525 | 1.7094 | 0.003663 | 0.020147 | 0.0030525 | 0.017094 | 0.016484 | 0.014042 | 7907.6047 | 9308.6123 | 6218.1096
38930.5225 | 6 | 20 | 38930.5226 | 5 | 12 | 1556 | 1689 | 0.3663 | 1.221 | 0.30525 | 0.7326 | 0.003663 | 0.01221 | 0.0030525 | 0.007326 | 0.008547 | 0.0042735 | 15121.0607 | 30459.8975 | 10400.9536
38930.5232 | 6 | 18 | 38930.5232 | 5 | 13 | 1614.5 | 1747.5 | 0.3663 | 1.0989 | 0.30525 | 0.79365 | 0.003663 | 0.010989 | 0.0030525 | 0.0079365 | 0.007326 | 0.004884 | 17658.0945 | 26594.9925 | 11562.1916
38930.5239 | 6 | 18 | 38930.5239 | 36 | 39 | 1673.5 | 1806.5 | 0.3663 | 1.0989 | 2.1978 | 2.381 | 0.003663 | 0.010989 | 0.021978 | 0.02381 | 0.007326 | 0.0018315 | 17593.8016 | 74757.8306 | 11590.1631
38930.5246 | 1102 | 1063 | 38930.5246 | 943 | 937 | 1732.5 | 1865.5 | 67.2772 | 64.8962 | 57.5702 | 57.2039 | 0.67277 | 0.64896 | 0.5757 | 0.57204 | 0.02381 | 0.003663 | 476.1003 | 613.1947 | 4.2043
38930.5253 | 970 | 884 | 38930.5253 | 1126 | 1126 | 1791 | 1924 | 59.2186 | 53.9683 | 68.7424 | 68.7424 | 0.59219 | 0.53968 | 0.68742 | 0.68742 | 0.052503 | 0 | 156.4488 | 137.1387 | 16.9449
38930.5259 | 1010 | 932 | 38930.526 | 1044 | 978 | 1850 | 1983 | 61.6606 | 56.8987 | 63.7363 | 59.707 | 0.61661 | 0.56899 | 0.63736 | 0.59707 | 0.047619 | 0.040293 | 1223.7556 | 7680.8901 | 18.114
38930.5266 | 1133 | 1108 | 38930.5266 | 927 | 821 | 1908.5 | 2041.5 | 69.1697 | 67.6435 | 56.5934 | 50.1221 | 0.6917 | 0.67643 | 0.56593 | 0.50122 | 0.015263 | 0.064713 | 287.7705 | 351.1262 | 8.9902
38930.5273 | 978 | 900 | 38930.5273 | 1128 | 1036 | 1967.5 | 2100.5 | 59.707 | 54.9451 | 68.8645 | 63.2479 | 0.59707 | 0.54945 | 0.68864 | 0.63248 | 0.047619 | 0.056166 | 3109.9818 | 2168.4674 | 24.9622
38930.528 | 930 | 837 | 38930.528 | 1043 | 981 | 2026.5 | 2159.5 | 56.7766 | 51.0989 | 63.6752 | 59.8901 | 0.56777 | 0.51099 | 0.63675 | 0.5989 | 0.056777 | 0.037851 | 934.0152 | 2486.6601 | 39.7423
38930.5287 | 913 | 817 | 38930.5287 | 1124 | 1131 | 2085 | 2218 | 55.7387 | 49.8779 | 68.6203 | 69.0476 | 0.55739 | 0.49878 | 0.6862 | 0.69048 | 0.058608 | 0.0042735 | 294.5488 | 262.3554 | 33.9433
38930.5294 | 956 | 1049 | 38930.5294 | 1022 | 1053 | 2144 | 2277 | 58.3639 | 64.0415 | 62.3932 | 64.2857 | 0.58364 | 0.64042 | 0.62393 | 0.64286 | 0.056777 | 0.018926 | 228.7809 | 254.1596 | 7.3899
38930.53 | 663 | 622 | 38930.53 | 610 | 568 | 2202.5 | 2335.5 | 40.4762 | 37.9731 | 37.2405 | 34.6764 | 0.40476 | 0.37973 | 0.37241 | 0.34676 | 0.025031 | 0.025641 | 5144.0065 | 4855.0257 | 130.4356
38930.5307 | 1019 | 963 | 38930.5307 | 1124 | 1103 | 2261.5 | 2394.5 | 62.21 | 58.7912 | 68.6203 | 67.3382 | 0.6221 | 0.58791 | 0.6862 | 0.67338 | 0.034188 | 0.012821 | 56.3637 | 51.0875 | 4.6004
38930.5314 | 880 | 800 | 38930.5314 | 968 | 890 | 2320.5 | 2453.5 | 53.7241 | 48.84 | 59.0965 | 54.3346 | 0.53724 | 0.4884 | 0.59096 | 0.54335 | 0.04884 | 0.047619 | 2396.5555 | 2802.0695 | 52.2624

## C3-7
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38930.5035 | 1 | 0 | 38930.5035 | 1 | 0 | -93 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5041 | 1 | 0 | 38930.5042 | 1 | 0 | -34 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5048 | 1 | 0 | 38930.5048 | 1 | 0 | 24.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5055 | 1 | 0 | 38930.5055 | 1 | 0 | 83.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5062 | 1 | 0 | 38930.5062 | 1 | 0 | 142.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5069 | 1 | 0 | 38930.5069 | 1 | 0 | 201 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5075 | 1 | 0 | 38930.5076 | 1 | 0 | 259.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5082 | 1 | 0 | 38930.5082 | 1 | 0 | 318.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5089 | 1 | 0 | 38930.5089 | 1 | 0 | 377.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5096 | 1 | 0 | 38930.5096 | 1 | 0 | 436 | 569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5103 | 1 | 0 | 38930.5103 | 1 | 0 | 495 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5109 | 1 | 0 | 38930.511 | 1 | 0 | 553.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5116 | 1 | 0 | 38930.5116 | 1 | 0 | 612.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5123 | 1 | 0 | 38930.5123 | 1 | 0 | 671.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.513 | 1 | 0 | 38930.513 | 1 | 0 | 730 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5137 | 1 | 0 | 38930.5137 | 1 | 0 | 789 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5144 | 1 | 0 | 38930.5144 | 1 | 0 | 847.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.515 | 1 | 0 | 38930.515 | 1 | 0 | 906.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5157 | 1 | 0 | 38930.5157 | 1 | 0 | 965.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5164 | 1 | 0 | 38930.5164 | 1 | 0 | 1024 | 1157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5171 | 1 | 0 | 38930.5171 | 1 | 0 | 1083 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5178 | 1 | 0 | 38930.5178 | 1 | 0 | 1141.5 | 1274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5184 | 1 | 0 | 38930.5184 | 1 | 0 | 1200.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5191 | 1 | 0 | 38930.5191 | 1 | 0 | 1259.5 | 1392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5198 | 1 | 0 | 38930.5198 | 1 | 0 | 1318 | 1451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5205 | 121 | 130 | 38930.5205 | 149 | 172 | 1377 | 1510 | 7.3871 | 7.9365 | 9.0965 | 10.5006 | 0.073871 | 0.079365 | 0.090965 | 0.10501 | 0.0054945 | 0.014042 | 26487.5354 | 8787.3107 | 1416.2066
38930.5212 | 989 | 955 | 38930.5212 | 1014 | 961 | 1435.5 | 1568.5 | 60.3785 | 58.3028 | 61.9048 | 58.6691 | 0.60379 | 0.58303 | 0.61905 | 0.58669 | 0.020757 | 0.032357 | 2397.0244 | 7407.519 | 17.4627
38930.5218 | 957 | 919 | 38930.5219 | 1194 | 1181 | 1494.5 | 1627.5 | 58.4249 | 56.105 | 72.8938 | 72.1001 | 0.58425 | 0.56105 | 0.72894 | 0.721 | 0.023199 | 0.0079365 | 99.8161 | 82.0426 | 11.6235
38930.5225 | 994 | 900 | 38930.5225 | 1073 | 1150 | 1553 | 1686 | 60.6838 | 54.9451 | 65.5067 | 70.2076 | 0.60684 | 0.54945 | 0.65507 | 0.70208 | 0.057387 | 0.047009 | 452.5463 | 587.1916 | 20.7942
38930.5232 | 984 | 875 | 38930.5232 | 1041 | 948 | 1612 | 1745 | 60.0733 | 53.4188 | 63.5531 | 57.8755 | 0.60073 | 0.53419 | 0.63553 | 0.57875 | 0.066545 | 0.056777 | 1073.5168 | 22847.2709 | 28.9043
38930.5239 | 1049 | 959 | 38930.5239 | 1179 | 1135 | 1670.5 | 1803.5 | 64.0415 | 58.547 | 71.978 | 69.2918 | 0.64042 | 0.58547 | 0.71978 | 0.69292 | 0.054945 | 0.026862 | 226.0772 | 251.9411 | 7.8394
38930.5246 | 1126 | 1168 | 38930.5246 | 922 | 983 | 1729.5 | 1862.5 | 68.7424 | 71.3065 | 56.2882 | 60.0122 | 0.68742 | 0.71306 | 0.56288 | 0.60012 | 0.025641 | 0.037241 | 129.1701 | 161.745 | 9.575
38930.5252 | 948 | 841 | 38930.5253 | 1190 | 1185 | 1788.5 | 1921.5 | 57.8755 | 51.3431 | 72.6496 | 72.3443 | 0.57875 | 0.51343 | 0.7265 | 0.72344 | 0.065324 | 0.0030525 | 83.284 | 65.1003 | 15.1919
38930.5259 | 1141 | 1087 | 38930.5259 | 1139 | 1082 | 1847 | 1980 | 69.6581 | 66.3614 | 69.536 | 66.0562 | 0.69658 | 0.66361 | 0.69536 | 0.66056 | 0.032967 | 0.034799 | 2450.0004 | 7587.7507 | 10.4401
38930.5266 | 1084 | 1005 | 38930.5266 | 991 | 878 | 1906 | 2039 | 66.1783 | 61.3553 | 60.5006 | 53.602 | 0.66178 | 0.61355 | 0.60501 | 0.53602 | 0.04823 | 0.068987 | 1092.0218 | 6598.5064 | 2.3544
38930.5273 | 1163 | 1179 | 38930.5273 | 1159 | 1116 | 1964.5 | 2097.5 | 71.0012 | 71.978 | 70.757 | 68.1319 | 0.71001 | 0.71978 | 0.70757 | 0.68132 | 0.009768 | 0.026252 | 1155.5037 | 1780.5106 | 18.3888
38930.528 | 1050 | 965 | 38930.528 | 1009 | 918 | 2023.5 | 2156.5 | 64.1026 | 58.9133 | 61.5995 | 56.044 | 0.64103 | 0.58913 | 0.616 | 0.56044 | 0.051893 | 0.055556 | 4774.1773 | 1538.2417 | 9.5375
38930.5286 | 1106 | 1042 | 38930.5287 | 1175 | 1186 | 2082.5 | 2215.5 | 67.5214 | 63.6142 | 71.7338 | 72.4054 | 0.67521 | 0.63614 | 0.71734 | 0.72405 | 0.039072 | 0.0067155 | 599.5459 | 1002.272 | 3.0525
38930.5293 | 1028 | 941 | 38930.5293 | 1170 | 1132 | 2141 | 2274 | 62.7595 | 57.4481 | 71.4286 | 69.1087 | 0.62759 | 0.57448 | 0.71429 | 0.69109 | 0.053114 | 0.023199 | 90.7782 | 84.9092 | 7.028
38930.53 | 952 | 862 | 38930.53 | 1010 | 869 | 2200 | 2333 | 58.1197 | 52.6252 | 61.6606 | 53.0525 | 0.5812 | 0.52625 | 0.61661 | 0.53053 | 0.054945 | 0.086081 | 2386.8231 | 2084.2855 | 33.101
38930.5307 | 1052 | 987 | 38930.5307 | 1132 | 1086 | 2258.5 | 2391.5 | 64.2247 | 60.2564 | 69.1087 | 66.3004 | 0.64225 | 0.60256 | 0.69109 | 0.663 | 0.039683 | 0.028083 | 168.8066 | 175.1424 | 4.7738
38930.5314 | 990 | 894 | 38930.5314 | 1037 | 1051 | 2317.5 | 2450.5 | 60.4396 | 54.5788 | 63.3089 | 64.1636 | 0.6044 | 0.54579 | 0.63309 | 0.64164 | 0.058608 | 0.008547 | 296.092 | 315.5879 | 19.4533

## C3-6
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38930.5034 | 1 | 0 | 38930.5034 | 1 | 0 | -95.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5041 | 1 | 0 | 38930.5041 | 1 | 0 | -37 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5048 | 1 | 0 | 38930.5048 | 1 | 0 | 22 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5055 | 1 | 0 | 38930.5055 | 1 | 0 | 80.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5062 | 1 | 0 | 38930.5062 | 1 | 0 | 139.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5068 | 1 | 0 | 38930.5069 | 1 | 0 | 198.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5075 | 1 | 0 | 38930.5075 | 1 | 0 | 257 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5082 | 1 | 0 | 38930.5082 | 1 | 0 | 315.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5089 | 1 | 0 | 38930.5089 | 1 | 0 | 374.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5096 | 1 | 0 | 38930.5096 | 1 | 0 | 433.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5102 | 1 | 0 | 38930.5103 | 1 | 0 | 492 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5109 | 1 | 0 | 38930.5109 | 1 | 0 | 551 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5116 | 1 | 0 | 38930.5116 | 1 | 0 | 609.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5123 | 1 | 0 | 38930.5123 | 1 | 0 | 668.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.513 | 1 | 0 | 38930.513 | 1 | 0 | 727.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5136 | 1 | 0 | 38930.5137 | 1 | 0 | 786 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5143 | 1 | 0 | 38930.5143 | 1 | 0 | 845 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.515 | 1 | 0 | 38930.515 | 1 | 0 | 903.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5157 | 1 | 0 | 38930.5157 | 1 | 0 | 962.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5164 | 1 | 0 | 38930.5164 | 1 | 0 | 1021.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.517 | 1 | 0 | 38930.5171 | 1 | 0 | 1080 | 1213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5177 | 1 | 0 | 38930.5177 | 1 | 0 | 1139 | 1272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5184 | 1 | 0 | 38930.5184 | 1 | 0 | 1197.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5191 | 1 | 0 | 38930.5191 | 1 | 0 | 1256.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5198 | 1 | 1 | 38930.5198 | 1 | 0 | 1315.5 | 1448.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5204 | 987 | 952 | 38930.5205 | 1023 | 993 | 1374 | 1507 | 60.2564 | 58.1197 | 62.4542 | 60.6227 | 0.60256 | 0.5812 | 0.62454 | 0.60623 | 0.021368 | 0.018315 | 2940.8523 | 28945.8457 | 18.2165
38930.5211 | 965 | 999 | 38930.5211 | 1189 | 1089 | 1432.5 | 1565.5 | 58.9133 | 60.989 | 72.5885 | 66.4835 | 0.58913 | 0.60989 | 0.72589 | 0.66484 | 0.020757 | 0.06105 | 39.5973 | 34.8662 | 3.8564
38930.5218 | 1127 | 905 | 38930.5218 | 951 | 912 | 1491.5 | 1624.5 | 68.8034 | 55.2503 | 58.0586 | 55.6777 | 0.68803 | 0.5525 | 0.58059 | 0.55678 | 0.13553 | 0.02381 | 143.8946 | 195.364 | 5.9215
38930.5225 | 1053 | 974 | 38930.5225 | 1094 | 1028 | 1550.5 | 1683.5 | 64.2857 | 59.4628 | 66.7888 | 62.7595 | 0.64286 | 0.59463 | 0.66789 | 0.62759 | 0.04823 | 0.040293 | 486.5382 | 701.3761 | 7.7296
38930.5232 | 1071 | 1096 | 38930.5232 | 1184 | 1150 | 1609 | 1742 | 65.3846 | 66.9109 | 72.2833 | 70.2076 | 0.65385 | 0.66911 | 0.72283 | 0.70208 | 0.015263 | 0.020757 | 2082.4346 | 4377.2509 | 4.8152
38930.5238 | 1120 | 1162 | 38930.5239 | 1195 | 942 | 1668 | 1801 | 68.3761 | 70.9402 | 72.9548 | 57.5092 | 0.68376 | 0.7094 | 0.72955 | 0.57509 | 0.025641 | 0.15446 | 71.6409 | 86.4514 | 6.7427
38930.5245 | 1119 | 1175 | 38930.5245 | 1192 | 883 | 1726.5 | 1859.5 | 68.315 | 71.7338 | 72.7717 | 53.9072 | 0.68315 | 0.71734 | 0.72772 | 0.53907 | 0.034188 | 0.18864 | 39.1697 | 47.346 | 4.9492
38930.5252 | 1186 | 1153 | 38930.5252 | 1019 | 931 | 1785.5 | 1918.5 | 72.4054 | 70.3907 | 62.21 | 56.8376 | 0.72405 | 0.70391 | 0.6221 | 0.56838 | 0.020147 | 0.053724 | 90.6722 | 116.5369 | 10.5481
38930.5259 | 967 | 861 | 38930.5259 | 1055 | 976 | 1844.5 | 1977.5 | 59.0354 | 52.5641 | 64.4078 | 59.5849 | 0.59035 | 0.52564 | 0.64408 | 0.59585 | 0.064713 | 0.04823 | 843.3416 | 2880.5262 | 31.9927
38930.5266 | 925 | 886 | 38930.5266 | 1043 | 950 | 1903 | 2036 | 56.4713 | 54.0904 | 63.6752 | 57.9976 | 0.56471 | 0.5409 | 0.63675 | 0.57998 | 0.02381 | 0.056777 | 1056.1459 | 1205.666 | 31.4773
38930.5272 | 1113 | 1049 | 38930.5273 | 1035 | 950 | 1962 | 2095 | 67.9487 | 64.0415 | 63.1868 | 57.9976 | 0.67949 | 0.64042 | 0.63187 | 0.57998 | 0.039072 | 0.051893 | 403.9892 | 571.5489 | 3.9739
38930.5279 | 1027 | 940 | 38930.5279 | 963 | 936 | 2020.5 | 2153.5 | 62.6984 | 57.3871 | 58.7912 | 57.1429 | 0.62698 | 0.57387 | 0.58791 | 0.57143 | 0.053114 | 0.016484 | 494.3031 | 708.3257 | 13.6123
38930.5286 | 924 | 877 | 38930.5286 | 1038 | 954 | 2079.5 | 2212.5 | 56.4103 | 53.5409 | 63.37 | 58.2418 | 0.5641 | 0.53541 | 0.6337 | 0.58242 | 0.028694 | 0.051282 | 1908.0509 | 5726.0575 | 34.9674
38930.5293 | 951 | 842 | 38930.5293 | 1070 | 1095 | 2138.5 | 2271.5 | 58.0586 | 51.4042 | 65.3236 | 66.8498 | 0.58059 | 0.51404 | 0.65324 | 0.6685 | 0.066545 | 0.015263 | 313.0642 | 321.158 | 28.9827
38930.53 | 1109 | 1053 | 38930.53 | 1019 | 943 | 2197 | 2330 | 67.7045 | 64.2857 | 62.21 | 57.5702 | 0.67705 | 0.64286 | 0.6221 | 0.5757 | 0.034188 | 0.046398 | 561.9551 | 858.4319 | 4.1662
38930.5306 | 1042 | 974 | 38930.5307 | 968 | 893 | 2256 | 2389 | 63.6142 | 59.4628 | 59.0965 | 54.5177 | 0.63614 | 0.59463 | 0.59096 | 0.54518 | 0.041514 | 0.045788 | 7410.7388 | 1818.938 | 9.4419
38930.5313 | 1197 | 1172 | 38930.5313 | 936 | 839 | 2314.5 | 2447.5 | 73.0769 | 71.5507 | 57.1429 | 51.221 | 0.73077 | 0.71551 | 0.57143 | 0.51221 | 0.015263 | 0.059219 | 112.5891 | 148.6186 | 13.0562

## C3-5
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38930.5034 | 1 | 0 | 38930.5034 | 1 | 0 | -98.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5041 | 1 | 0 | 38930.5041 | 2 | 0 | -40 | 93 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.5048 | 1 | 0 | 38930.5048 | 1 | 0 | 19 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5054 | 1 | 0 | 38930.5055 | 1 | 0 | 77.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5061 | 1 | 0 | 38930.5061 | 1 | 0 | 136.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5068 | 1 | 0 | 38930.5068 | 1 | 0 | 195.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5075 | 1 | 0 |  | 1 | 0 | 254 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5082 | 1 | 0 | 38930.5082 | 1 | 0 | 313 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5088 | 1 | 0 | 38930.5089 | 1 | 0 | 371.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5095 | 1 | 0 | 38930.5095 | 1 | 0 | 430.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5102 | 1 | 0 | 38930.5102 | 1 | 0 | 489.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5109 | 1 | 0 | 38930.5109 | 1 | 0 | 548 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5116 | 1 | 0 | 38930.5116 | 1 | 0 | 607 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5122 | 1 | 0 | 38930.5123 | 1 | 0 | 665.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5129 | 1 | 0 | 38930.5129 | 1 | 0 | 724.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5136 | 1 | 0 | 38930.5136 | 1 | 0 | 783.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5143 | 1 | 0 | 38930.5143 | 1 | 0 | 842 | 975 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.515 | 1 | 0 | 38930.515 | 1 | 0 | 901 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5156 | 1 | 0 | 38930.5157 | 1 | 0 | 959.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5163 | 1 | 0 | 38930.5163 | 1 | 0 | 1018.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.517 | 1 | 0 | 38930.517 | 1 | 0 | 1077.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5177 | 1 | 0 | 38930.5177 | 1 | 0 | 1136 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5184 | 1 | 0 | 38930.5184 | 1 | 0 | 1195 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5191 | 1 | 0 | 38930.5191 | 1 | 0 | 1253.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5197 | 1 | 1 | 38930.5197 | 1 | 0 | 1312.5 | 1445.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5204 | 1184 | 1096 | 38930.5204 | 1108 | 1081 | 1371 | 1504 | 72.2833 | 66.9109 | 67.6435 | 65.9951 | 0.72283 | 0.66911 | 0.67643 | 0.65995 | 0.053724 | 0.016484 | 426.6667 | 844.7726 | 13.6228
38930.5211 | 983 | 948 | 38930.5211 | 952 | 917 | 1430 | 1563 | 60.0122 | 57.8755 | 58.1197 | 55.9829 | 0.60012 | 0.57875 | 0.5812 | 0.55983 | 0.021368 | 0.021368 | 5937.2 | 5937.2 | 18.8824
38930.5218 | 1068 | 1035 | 38930.5218 | 1188 | 1169 | 1488.5 | 1621.5 | 65.2015 | 63.1868 | 72.5275 | 71.3675 | 0.65201 | 0.63187 | 0.72527 | 0.71368 | 0.020147 | 0.0116 | 2239.7405 | 7577.9297 | 0.95551
38930.5225 | 957 | 934 | 38930.5225 | 1137 | 1085 | 1547.5 | 1680.5 | 58.4249 | 57.0208 | 69.4139 | 66.2393 | 0.58425 | 0.57021 | 0.69414 | 0.66239 | 0.014042 | 0.031746 | 439.9336 | 389.5376 | 18.9151
38930.5231 | 1051 | 967 | 38930.5231 | 1161 | 1117 | 1606.5 | 1739.5 | 64.1636 | 59.0354 | 70.8791 | 68.1929 | 0.64164 | 0.59035 | 0.70879 | 0.68193 | 0.051282 | 0.026862 | 184.5848 | 196.8022 | 6.5156
38930.5238 | 1126 | 1065 | 38930.5238 | 1009 | 908 | 1665 | 1798 | 68.7424 | 65.0183 | 61.5995 | 55.4335 | 0.68742 | 0.65018 | 0.616 | 0.55433 | 0.037241 | 0.061661 | 304.9987 | 405.5375 | 5.8737
38930.5245 | 1163 | 1120 | 38930.5245 | 986 | 854 | 1724 | 1857 | 71.0012 | 68.3761 | 60.1954 | 52.1368 | 0.71001 | 0.68376 | 0.60195 | 0.52137 | 0.026252 | 0.080586 | 114.9262 | 142.9237 | 8.9292
38930.5252 | 1185 | 1150 | 38930.5252 | 1193 | 1184 | 1782.5 | 1915.5 | 72.3443 | 70.2076 | 72.8327 | 72.2833 | 0.72344 | 0.70208 | 0.72833 | 0.72283 | 0.021368 | 0.0054945 | 2323.9669 | 23314.3606 | 19.2202
38930.5259 | 1159 | 1112 | 38930.5259 | 1102 | 1034 | 1841.5 | 1974.5 | 70.757 | 67.8877 | 67.2772 | 63.1258 | 0.70757 | 0.67888 | 0.67277 | 0.63126 | 0.028694 | 0.041514 | 659.3861 | 1138.3754 | 13.0596
38930.5265 | 1108 | 1170 | 38930.5266 | 939 | 1035 | 1900.5 | 2033.5 | 67.6435 | 71.4286 | 57.326 | 63.1868 | 0.67643 | 0.71429 | 0.57326 | 0.63187 | 0.037851 | 0.058608 | 78.5121 | 96.0525 | 6.9085
38930.5272 | 1146 | 1097 | 38930.5272 | 1002 | 905 | 1959 | 2092 | 69.9634 | 66.9719 | 61.1722 | 55.2503 | 0.69963 | 0.66972 | 0.61172 | 0.5525 | 0.029915 | 0.059219 | 157.0042 | 193.5018 | 7.8117
38930.5279 | 961 | 859 | 38930.5279 | 1128 | 1074 | 2018 | 2151 | 58.6691 | 52.442 | 68.8645 | 65.5678 | 0.58669 | 0.52442 | 0.68864 | 0.65568 | 0.062271 | 0.032967 | 392.3318 | 448.2501 | 27.8898
38930.5286 | 1091 | 1023 | 38930.5286 | 1040 | 952 | 2076.5 | 2209.5 | 66.6056 | 62.4542 | 63.4921 | 58.1197 | 0.66606 | 0.62454 | 0.63492 | 0.5812 | 0.041514 | 0.053724 | 719.5878 | 1381.8998 | 0.089332
38930.5293 | 1139 | 1088 | 38930.5293 | 1186 | 1078 | 2135.5 | 2268.5 | 69.536 | 66.4225 | 72.4054 | 65.812 | 0.69536 | 0.66422 | 0.72405 | 0.65812 | 0.031136 | 0.065934 | 384.3705 | 537.5321 | 8.8329
38930.5299 | 1043 | 1060 | 38930.53 | 1167 | 1171 | 2194.5 | 2327.5 | 63.6752 | 64.7131 | 71.2454 | 71.4896 | 0.63675 | 0.64713 | 0.71245 | 0.7149 | 0.010379 | 0.002442 | 1933.7367 | 2765.1465 | 0.91229
38930.5306 | 1191 | 1165 | 38930.5306 | 955 | 860 | 2253 | 2386 | 72.7106 | 71.1233 | 58.3028 | 52.5031 | 0.72711 | 0.71123 | 0.58303 | 0.52503 | 0.015873 | 0.057998 | 81.6935 | 105.6562 | 10.7151
38930.5313 | 1143 | 1185 | 38930.5313 | 999 | 906 | 2312 | 2445 | 69.7802 | 72.3443 | 60.989 | 55.3114 | 0.6978 | 0.72344 | 0.60989 | 0.55311 | 0.025641 | 0.056777 | 11.0566 | 13.572 | 2.168

## C3-4
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38930.5034 | 1 | 0 | 38930.5034 | 1 | 0 | -101.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5041 | 1 | 0 | 38930.5041 | 1 | 0 | -42.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5047 | 1 | 0 | 38930.5047 | 1 | 0 | 16.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5054 | 1 | 0 | 38930.5054 | 1 | 0 | 75 | 208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5061 | 1 | 0 | 38930.5061 | 1 | 0 | 134 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5068 | 1 | 0 | 38930.5068 | 1 | 0 | 192.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5075 | 1 | 0 | 38930.5075 | 1 | 0 | 251.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5081 | 1 | 0 | 38930.5081 | 1 | 0 | 310.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5088 | 1 | 0 | 38930.5088 | 1 | 0 | 369 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5095 | 1 | 0 | 38930.5095 | 1 | 0 | 427.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5102 | 1 | 0 | 38930.5102 | 1 | 0 | 486.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5109 | 1 | 0 | 38930.5109 | 1 | 0 | 545.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5115 | 1 | 0 | 38930.5116 | 1 | 0 | 604 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5122 | 1 | 0 | 38930.5122 | 1 | 0 | 663 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5129 | 1 | 0 | 38930.5129 | 1 | 0 | 721.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5136 | 1 | 0 | 38930.5136 | 1 | 0 | 780.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5143 | 1 | 1 | 38930.5143 | 1 | 0 | 839.5 | 972.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5149 | 1 | 0 | 38930.515 | 1 | 0 | 898 | 1031 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5156 | 1 | 0 | 38930.5156 | 1 | 0 | 957 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5163 | 1 | 0 | 38930.5163 | 1 | 0 | 1015.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.517 | 1 | 0 | 38930.517 | 1 | 0 | 1074.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5177 | 1 | 0 | 38930.5177 | 1 | 0 | 1133.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5183 | 1 | 0 | 38930.5184 | 1 | 0 | 1192 | 1325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.519 | 1 | 0 | 38930.519 | 1 | 0 | 1251 | 1384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5197 | 1 | 0 | 38930.5197 | 1 | 0 | 1309.5 | 1442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5204 | 1050 | 1021 | 38930.5204 | 941 | 907 | 1368.5 | 1501.5 | 64.1026 | 62.3321 | 57.4481 | 55.3724 | 0.64103 | 0.62332 | 0.57448 | 0.55372 | 0.017705 | 0.020757 | 44089.4517 | 3839.9414 | 4.0111
38930.5211 | 11 | 24 | 38930.5211 | 7 | 22 | 1427.5 | 1560.5 | 0.67155 | 1.4652 | 0.42735 | 1.3431 | 0.0067155 | 0.014652 | 0.0042735 | 0.013431 | 0.0079365 | 0.0091575 | 16382.8765 | 14166.9622 | 8597.7281
38930.5217 | 6 | 21 | 38930.5218 | 6 | 14 | 1486 | 1619 | 0.3663 | 1.2821 | 0.3663 | 0.8547 | 0.003663 | 0.012821 | 0.003663 | 0.008547 | 0.0091575 | 0.004884 | 14120.9305 | 26668.2483 | 9896.3196
38930.5224 | 6 | 23 | 38930.5224 | 6 | 13 | 1544.5 | 1677.5 | 0.3663 | 1.4042 | 0.3663 | 0.79365 | 0.003663 | 0.014042 | 0.003663 | 0.0079365 | 0.010379 | 0.0042735 | 12449.3577 | 30556.1089 | 9031.3997
38930.5231 | 6 | 20 | 38930.5231 | 6 | 14 | 1603.5 | 1736.5 | 0.3663 | 1.221 | 0.3663 | 0.8547 | 0.003663 | 0.01221 | 0.003663 | 0.008547 | 0.008547 | 0.004884 | 15131.2663 | 26645.9223 | 10396.0843
38930.5238 | 6 | 19 | 38930.5238 | 6 | 13 | 1662.5 | 1795.5 | 0.3663 | 1.16 | 0.3663 | 0.79365 | 0.003663 | 0.0116 | 0.003663 | 0.0079365 | 0.0079365 | 0.0042735 | 16286.0222 | 30447.4873 | 10953.6036
38930.5245 | 922 | 826 | 38930.5245 | 1044 | 983 | 1721 | 1854 | 56.2882 | 50.4274 | 63.7363 | 60.0122 | 0.56288 | 0.50427 | 0.63736 | 0.60012 | 0.058608 | 0.037241 | 882.9765 | 2124.1061 | 42.2044
38930.5251 | 1115 | 1079 | 38930.5252 | 1030 | 962 | 1780 | 1913 | 68.0708 | 65.873 | 62.8816 | 58.7302 | 0.68071 | 0.65873 | 0.62882 | 0.5873 | 0.021978 | 0.041514 | 124.7049 | 141.1739 | 4.3932
38930.5258 | 1045 | 1082 | 38930.5258 | 1135 | 1023 | 1838.5 | 1971.5 | 63.7973 | 66.0562 | 69.2918 | 62.4542 | 0.63797 | 0.66056 | 0.69292 | 0.62454 | 0.022589 | 0.068376 | 73.3448 | 76.2421 | 0.55894
38930.5265 | 1027 | 1097 | 38930.5265 | 1089 | 1039 | 1897.5 | 2030.5 | 62.6984 | 66.9719 | 66.4835 | 63.431 | 0.62698 | 0.66972 | 0.66484 | 0.63431 | 0.042735 | 0.030525 | 164.4355 | 185.7894 | 0.65068
38930.5272 | 990 | 1001 | 38930.5272 | 909 | 881 | 1956.5 | 2089.5 | 60.4396 | 61.1111 | 55.4945 | 53.7851 | 0.6044 | 0.61111 | 0.55495 | 0.53785 | 0.0067155 | 0.017094 | 3180.9019 | 4118.4804 | 11.9008
38930.5279 | 893 | 790 | 38930.5279 | 1108 | 782 | 2015 | 2148 | 54.5177 | 48.2295 | 67.6435 | 47.7411 | 0.54518 | 0.4823 | 0.67643 | 0.47741 | 0.062882 | 0.19902 | 394.983 | 383.7204 | 43.1799
38930.5285 | 886 | 796 | 38930.5286 | 1080 | 1120 | 2074 | 2207 | 54.0904 | 48.5958 | 65.9341 | 68.3761 | 0.5409 | 0.48596 | 0.65934 | 0.68376 | 0.054945 | 0.02442 | 615.091 | 727.0341 | 47.601
38930.5292 | 1015 | 1039 | 38930.5292 | 906 | 803 | 2132.5 | 2265.5 | 61.9658 | 63.431 | 55.3114 | 49.0232 | 0.61966 | 0.63431 | 0.55311 | 0.49023 | 0.014652 | 0.062882 | 629.1152 | 690.2095 | 4.9616
38930.5299 | 1023 | 957 | 38930.5299 | 1131 | 1103 | 2191.5 | 2324.5 | 62.4542 | 58.4249 | 69.0476 | 67.3382 | 0.62454 | 0.58425 | 0.69048 | 0.67338 | 0.040293 | 0.017094 | 39.0623 | 35.1262 | 3.6132
38930.5306 | 895 | 807 | 38930.5306 | 1107 | 1124 | 2250.5 | 2383.5 | 54.6398 | 49.2674 | 67.5824 | 68.6203 | 0.5464 | 0.49267 | 0.67582 | 0.6862 | 0.053724 | 0.010379 | 425.4528 | 406.9839 | 40.8858
38930.5313 | 1129 | 1113 | 38930.5313 | 1110 | 1073 | 2309 | 2442 | 68.9255 | 67.9487 | 67.7656 | 65.5067 | 0.68926 | 0.67949 | 0.67766 | 0.65507 | 0.009768 | 0.022589 | 824.6524 | 1077.1793 | 10.6041

## C2-7
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38930.5033 | 1 | 0 | 38930.5034 | 1 | 0 | -104 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.504 | 1 | 0 | 38930.504 | 1 | 0 | -45.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5047 | 1 | 0 | 38930.5047 | 1 | 0 | 13.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5054 | 1 | 0 | 38930.5054 | 1 | 0 | 72.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5061 | 1 | 0 | 38930.5061 | 1 | 0 | 131 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5067 | 1 | 0 | 38930.5067 | 1 | 0 | 189.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5074 | 1 | 0 | 38930.5074 | 1 | 0 | 248.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5081 | 1 | 0 | 38930.5081 | 1 | 0 | 307.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5088 | 1 | 0 | 38930.5088 | 1 | 0 | 366 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5095 | 1 | 0 | 38930.5095 | 1 | 0 | 425 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5101 | 1 | 0 | 38930.5102 | 1 | 0 | 483.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5108 | 1 | 0 | 38930.5108 | 1 | 0 | 542.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5115 | 1 | 0 | 38930.5115 | 1 | 0 | 601.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5122 | 1 | 0 | 38930.5122 | 1 | 0 | 660 | 793 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5129 | 1 | 0 | 38930.5129 | 1 | 0 | 719 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5135 | 1 | 0 | 38930.5136 | 1 | 0 | 777.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5142 | 1 | 0 | 38930.5142 | 1 | 0 | 836.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5149 | 1 | 0 | 38930.5149 | 1 | 0 | 895.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5156 | 1 | 0 | 38930.5156 | 1 | 0 | 954 | 1087 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5163 | 1 | 0 | 38930.5163 | 1 | 0 | 1013 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5169 | 1 | 0 | 38930.517 | 1 | 0 | 1071.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5176 | 1 | 0 | 38930.5176 | 1 | 0 | 1130.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5183 | 1 | 0 | 38930.5183 | 1 | 0 | 1189 | 1322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.519 | 1 | 1 | 38930.519 | 1 | 0 | 1248 | 1381 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5197 | 1 | 0 | 38930.5197 | 1 | 0 | 1307 | 1440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5203 | 27 | 38 | 38930.5204 | 5 | 12 | 1365.5 | 1498.5 | 1.6484 | 2.3199 | 0.30525 | 0.7326 | 0.016484 | 0.023199 | 0.0030525 | 0.007326 | 0.0067155 | 0.0042735 | 19181.8937 | 30386.1323 | 5371.8477
38930.521 | 1182 | 910 | 38930.521 | 1085 | 1059 | 1424.5 | 1557.5 | 72.1612 | 55.5556 | 66.2393 | 64.652 | 0.72161 | 0.55556 | 0.66239 | 0.64652 | 0.16606 | 0.015873 | 2.5718 | 2.5328 | 0.057059
38930.5217 | 1084 | 1155 | 38930.5217 | 1059 | 1083 | 1483.5 | 1616.5 | 66.1783 | 70.5128 | 64.652 | 66.1172 | 0.66178 | 0.70513 | 0.64652 | 0.66117 | 0.043346 | 0.014652 | 352.8725 | 523.5425 | 9.1581
38930.5224 | 1066 | 1032 | 38930.5224 | 978 | 881 | 1542 | 1675 | 65.0794 | 63.0037 | 59.707 | 53.7851 | 0.65079 | 0.63004 | 0.59707 | 0.53785 | 0.020757 | 0.059219 | 453.88 | 524.7045 | 1.2224
38930.5231 | 1045 | 1058 | 38930.5231 | 1053 | 847 | 1601 | 1734 | 63.7973 | 64.591 | 64.2857 | 51.7094 | 0.63797 | 0.64591 | 0.64286 | 0.51709 | 0.0079365 | 0.12576 | 115.5895 | 116.1391 | 0.50889
38930.5238 | 964 | 852 | 38930.5238 | 1055 | 1135 | 1659.5 | 1792.5 | 58.8523 | 52.0147 | 64.4078 | 69.2918 | 0.58852 | 0.52015 | 0.64408 | 0.69292 | 0.068376 | 0.04884 | 493.9905 | 706.47 | 30.5388
38930.5244 | 1022 | 1024 | 38930.5244 | 1165 | 1186 | 1718.5 | 1851.5 | 62.3932 | 62.5153 | 71.1233 | 72.4054 | 0.62393 | 0.62515 | 0.71123 | 0.72405 | 0.001221 | 0.012821 | 918.7861 | 877.1193 | 5.8751
38930.5251 | 1182 | 1146 | 38930.5251 | 1043 | 852 | 1777 | 1910 | 72.1612 | 69.9634 | 63.6752 | 52.0147 | 0.72161 | 0.69963 | 0.63675 | 0.52015 | 0.021978 | 0.11661 | 10.9877 | 13.5826 | 2.2433
38930.5258 | 1125 | 1067 | 38930.5258 | 1137 | 1081 | 1836 | 1969 | 68.6813 | 65.1404 | 69.4139 | 65.9951 | 0.68681 | 0.6514 | 0.69414 | 0.65995 | 0.035409 | 0.034188 | 6016.8421 | 2566.1935 | 7.1244
38930.5265 | 1116 | 1052 | 38930.5265 | 1168 | 1127 | 1894.5 | 2027.5 | 68.1319 | 64.2247 | 71.3065 | 68.8034 | 0.68132 | 0.64225 | 0.71306 | 0.68803 | 0.039072 | 0.025031 | 1402.941 | 14887.3019 | 5.1914
38930.5272 | 992 | 899 | 38930.5272 | 1097 | 1136 | 1953.5 | 2086.5 | 60.5617 | 54.884 | 66.9719 | 69.3529 | 0.60562 | 0.54884 | 0.66972 | 0.69353 | 0.056777 | 0.02381 | 198.0767 | 190.0826 | 16.1828
38930.5278 | 1118 | 1057 | 38930.5278 | 1148 | 1099 | 2012.5 | 2145.5 | 68.254 | 64.5299 | 70.0855 | 67.094 | 0.68254 | 0.6453 | 0.70085 | 0.67094 | 0.037241 | 0.029915 | 2847.7666 | 4056.081 | 5.7227
38930.5285 | 1182 | 1114 | 38930.5285 | 1127 | 1068 | 2071 | 2204 | 72.1612 | 68.0098 | 68.8034 | 65.2015 | 0.72161 | 0.6801 | 0.68803 | 0.65201 | 0.041514 | 0.03602 | 20534.6738 | 1755.2676 | 15.5402
38930.5292 | 1136 | 1084 | 38930.5292 | 1011 | 1107 | 2130 | 2263 | 69.3529 | 66.1783 | 61.7216 | 67.5824 | 0.69353 | 0.66178 | 0.61722 | 0.67582 | 0.031746 | 0.058608 | 263.6766 | 340.3055 | 7.6276
38930.5299 | 1094 | 1033 | 38930.5299 | 949 | 936 | 2188.5 | 2321.5 | 66.7888 | 63.0647 | 57.9365 | 57.1429 | 0.66789 | 0.63065 | 0.57937 | 0.57143 | 0.037241 | 0.0079365 | 380.8372 | 500.0638 | 1.1278
38930.5306 | 954 | 862 | 38930.5306 | 934 | 849 | 2247.5 | 2380.5 | 58.2418 | 52.6252 | 57.0208 | 51.8315 | 0.58242 | 0.52625 | 0.57021 | 0.51832 | 0.056166 | 0.051893 | 1803.0473 | 3109.8 | 33.3836
38930.5312 | 928 | 885 | 38930.5312 | 938 | 838 | 2306.5 | 2439.5 | 56.6545 | 54.0293 | 57.265 | 51.16 | 0.56654 | 0.54029 | 0.57265 | 0.5116 | 0.026252 | 0.06105 | 1713.7773 | 3384.7519 | 32.9277

## C2-6
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38930.5033 | 1 | 0 | 38930.5033 | 1 | 0 | -107 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.504 | 1 | 0 | 38930.504 | 1 | 0 | -48 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5047 | 1 | 0 | 38930.5047 | 1 | 0 | 10.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5053 | 1 | 0 | 38930.5054 | 1 | 0 | 69.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.506 | 1 | 0 | 38930.506 | 1 | 0 | 128.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5067 | 1 | 0 | 38930.5067 | 1 | 0 | 187 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5074 | 1 | 0 | 38930.5074 | 1 | 0 | 245.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5081 | 1 | 0 | 38930.5081 | 1 | 0 | 304.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5088 | 1 | 0 | 38930.5088 | 1 | 0 | 363.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5094 | 1 | 0 | 38930.5094 | 1 | 0 | 422 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5101 | 1 | 0 | 38930.5101 | 1 | 0 | 481 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5108 | 1 | 0 | 38930.5108 | 1 | 0 | 539.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5115 | 1 | 0 | 38930.5115 | 1 | 0 | 598.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5122 | 1 | 0 | 38930.5122 | 1 | 0 | 657.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5128 | 1 | 0 | 38930.5128 | 1 | 0 | 716 | 849 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5135 | 1 | 0 | 38930.5135 | 1 | 0 | 775 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5142 | 1 | 0 | 38930.5142 | 1 | 0 | 833.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5149 | 1 | 0 | 38930.5149 | 1 | 0 | 892.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5156 | 1 | 0 | 38930.5156 | 1 | 0 | 951.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5162 | 1 | 0 | 38930.5163 | 1 | 0 | 1010 | 1143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5169 | 1 | 0 | 38930.5169 | 1 | 0 | 1069 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5176 | 1 | 0 | 38930.5176 | 1 | 0 | 1127.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5183 | 1 | 0 | 38930.5183 | 1 | 0 | 1186.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.519 | 1 | 0 | 38930.519 | 1 | 0 | 1245.5 | 1378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5196 | 2 | 1 | 38930.5197 | 1 | 1 | 1304 | 1437 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211101.9527 | 445851546.4873 | 211001.9527
38930.5203 | 1021 | 990 | 38930.5203 | 929 | 893 | 1362.5 | 1495.5 | 62.3321 | 60.4396 | 56.7155 | 54.5177 | 0.62332 | 0.6044 | 0.56716 | 0.54518 | 0.018926 | 0.021978 | 38408.4012 | 3516.0221 | 10.0201
38930.521 | 928 | 1031 | 38930.521 | 969 | 937 | 1421.5 | 1554.5 | 56.6545 | 62.9426 | 59.1575 | 57.2039 | 0.56654 | 0.62943 | 0.59158 | 0.57204 | 0.062882 | 0.019536 | 459.2529 | 665.0234 | 12.9862
38930.5217 | 1099 | 1035 | 38930.5217 | 920 | 884 | 1480.5 | 1613.5 | 67.094 | 63.1868 | 56.1661 | 53.9683 | 0.67094 | 0.63187 | 0.56166 | 0.53968 | 0.039072 | 0.021978 | 754.1095 | 1468.7959 | 1.8978
38930.5224 | 1140 | 1183 | 38930.5224 | 1158 | 1114 | 1539.5 | 1672.5 | 69.5971 | 72.2222 | 70.696 | 68.0098 | 0.69597 | 0.72222 | 0.70696 | 0.6801 | 0.026252 | 0.026862 | 3537.2609 | 7636.0636 | 17.5203
38930.523 | 1009 | 1103 | 38930.5231 | 1041 | 954 | 1598 | 1731 | 61.5995 | 67.3382 | 63.5531 | 58.2418 | 0.616 | 0.67338 | 0.63553 | 0.58242 | 0.057387 | 0.053114 | 2729.7317 | 2059.5368 | 0.088193
38930.5237 | 1113 | 1047 | 38930.5237 | 1040 | 1124 | 1657 | 1790 | 67.9487 | 63.9194 | 63.4921 | 68.6203 | 0.67949 | 0.63919 | 0.63492 | 0.6862 | 0.040293 | 0.051282 | 605.9226 | 1057.1392 | 4.0993
38930.5244 | 957 | 844 | 38930.5244 | 932 | 832 | 1715.5 | 1848.5 | 58.4249 | 51.5263 | 56.8987 | 50.7937 | 0.58425 | 0.51526 | 0.56899 | 0.50794 | 0.068987 | 0.06105 | 1351.6894 | 3071.7814 | 35.8036
38930.5251 | 1143 | 1185 | 38930.5251 | 1119 | 1057 | 1774.5 | 1907.5 | 69.7802 | 72.3443 | 68.315 | 64.5299 | 0.6978 | 0.72344 | 0.68315 | 0.6453 | 0.025641 | 0.037851 | 908.9381 | 1830.9603 | 17.2023
38930.5258 | 943 | 837 | 38930.5258 | 986 | 888 | 1833 | 1966 | 57.5702 | 51.0989 | 60.1954 | 54.2125 | 0.5757 | 0.51099 | 0.60195 | 0.54212 | 0.064713 | 0.059829 | 1536.8826 | 2802.0895 | 38.4163
38930.5264 | 1110 | 1043 | 38930.5265 | 1041 | 957 | 1892 | 2025 | 67.7656 | 63.6752 | 63.5531 | 58.4249 | 0.67766 | 0.63675 | 0.63553 | 0.58425 | 0.040904 | 0.051282 | 488.4282 | 753.8486 | 3.3842
38930.5271 | 1087 | 1159 | 38930.5271 | 989 | 889 | 1950.5 | 2083.5 | 66.3614 | 70.757 | 60.3785 | 54.2735 | 0.66361 | 0.70757 | 0.60379 | 0.54274 | 0.043956 | 0.06105 | 351.4842 | 527.0321 | 9.6438
38930.5278 | 1101 | 1038 | 38930.5278 | 1157 | 1186 | 2009.5 | 2142.5 | 67.2161 | 63.37 | 70.6349 | 72.4054 | 0.67216 | 0.6337 | 0.70635 | 0.72405 | 0.038462 | 0.017705 | 874.8112 | 1970.223 | 2.382
38930.5285 | 1097 | 1164 | 38930.5285 | 938 | 825 | 2068.5 | 2201.5 | 66.9719 | 71.0623 | 57.265 | 50.3663 | 0.66972 | 0.71062 | 0.57265 | 0.50366 | 0.040904 | 0.068987 | 442.2704 | 715.3031 | 11.1538
38930.5292 | 1076 | 1004 | 38930.5292 | 970 | 951 | 2127 | 2260 | 65.6899 | 61.2943 | 59.2186 | 58.0586 | 0.6569 | 0.61294 | 0.59219 | 0.58059 | 0.043956 | 0.0116 | 364.6399 | 472.7027 | 2.7146
38930.5298 | 1014 | 930 | 38930.5299 | 975 | 883 | 2186 | 2319 | 61.9048 | 56.7766 | 59.5238 | 53.9072 | 0.61905 | 0.56777 | 0.59524 | 0.53907 | 0.051282 | 0.056166 | 4280.7498 | 1594.4736 | 17.1016
38930.5305 | 1160 | 1121 | 38930.5305 | 921 | 930 | 2244.5 | 2377.5 | 70.8181 | 68.4371 | 56.2271 | 56.7766 | 0.70818 | 0.68437 | 0.56227 | 0.56777 | 0.02381 | 0.0054945 | 256.8392 | 337.5926 | 11.5605
38930.5312 | 1078 | 1111 | 38930.5312 | 958 | 858 | 2303.5 | 2436.5 | 65.812 | 67.8266 | 58.486 | 52.381 | 0.65812 | 0.67827 | 0.58486 | 0.52381 | 0.020147 | 0.06105 | 331.8942 | 398.4187 | 5.4668

## C2-5
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38930.5033 | 1 | 0 | 38930.5033 | 1 | 0 | -110 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5039 | 1 | 0 | 38930.504 | 1 | 0 | -51 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5046 | 1 | 0 | 38930.5047 | 1 | 0 | 8 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5053 | 1 | 0 | 38930.5053 | 1 | 0 | 66.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.506 | 1 | 0 | 38930.506 | 1 | 0 | 125.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5067 | 1 | 0 | 38930.5067 | 1 | 0 | 184 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5073 | 1 | 0 | 38930.5074 | 1 | 0 | 243 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.508 | 1 | 0 | 38930.5081 | 1 | 0 | 302 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5087 | 1 | 0 | 38930.5087 | 1 | 0 | 360.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5094 | 1 | 0 | 38930.5094 | 1 | 0 | 419.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5101 | 1 | 0 | 38930.5101 | 1 | 0 | 478 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5108 | 1 | 0 | 38930.5108 | 1 | 0 | 537 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5114 | 1 | 0 | 38930.5114 | 1 | 0 | 595.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5121 | 1 | 0 | 38930.5121 | 1 | 0 | 654.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5128 | 1 | 0 | 38930.5128 | 1 | 0 | 713.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5135 | 1 | 0 | 38930.5135 | 1 | 0 | 772 | 905 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5142 | 1 | 0 | 38930.5142 | 1 | 0 | 831 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5148 | 1 | 0 | 38930.5148 | 1 | 0 | 889.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5155 | 1 | 0 | 38930.5155 | 1 | 0 | 948.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5162 | 1 | 0 | 38930.5162 | 1 | 0 | 1007.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5169 | 1 | 0 | 38930.5169 | 1 | 0 | 1066 | 1199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5176 | 1 | 0 | 38930.5176 | 1 | 0 | 1125 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5182 | 1 | 0 | 38930.5183 | 1 | 0 | 1183.5 | 1316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5189 | 1 | 0 | 38930.5189 | 1 | 0 | 1242.5 | 1375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5196 | 3 | 2 | 38930.5196 | 2 | 2 | 1301.5 | 1434.5 | 0.18315 | 0.1221 | 0.1221 | 0.1221 | 0.0018315 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 211001.8105 | 222714521.0092 | 105400.9527
38930.5203 | 940 | 905 | 38930.5203 | 950 | 981 | 1360 | 1493 | 57.3871 | 55.2503 | 57.9976 | 59.8901 | 0.57387 | 0.5525 | 0.57998 | 0.5989 | 0.021368 | 0.018926 | 3766.1214 | 23485.952 | 29.4899
38930.521 | 1188 | 1188 | 38930.521 | 992 | 958 | 1419 | 1552 | 72.5275 | 72.5275 | 60.5617 | 58.486 | 0.72527 | 0.72527 | 0.60562 | 0.58486 | 0 | 0.020757 | 250.3914 | 321.5768 | 16.8855
38930.5216 | 941 | 835 | 38930.5217 | 1122 | 1065 | 1477.5 | 1610.5 | 57.4481 | 50.9768 | 68.4982 | 65.0183 | 0.57448 | 0.50977 | 0.68498 | 0.65018 | 0.064713 | 0.034799 | 473.8128 | 590.6935 | 34.518
38930.5223 | 1060 | 1076 | 38930.5223 | 1103 | 1141 | 1536.5 | 1669.5 | 64.7131 | 65.6899 | 67.3382 | 69.6581 | 0.64713 | 0.6569 | 0.67338 | 0.69658 | 0.009768 | 0.023199 | 663.8097 | 754.3846 | 1.8857
38930.523 | 1125 | 1177 | 38930.523 | 1040 | 961 | 1595 | 1728 | 68.6813 | 71.8559 | 63.4921 | 58.6691 | 0.68681 | 0.71856 | 0.63492 | 0.58669 | 0.031746 | 0.04823 | 190.7488 | 252.5918 | 11.5023
38930.5237 | 1086 | 1012 | 38930.5237 | 1170 | 1128 | 1654 | 1787 | 66.3004 | 61.7827 | 71.4286 | 68.8645 | 0.663 | 0.61783 | 0.71429 | 0.68864 | 0.045177 | 0.025641 | 634.3068 | 1151.1488 | 1.3656
38930.5244 | 1188 | 1154 | 38930.5244 | 1087 | 839 | 1713 | 1846 | 72.5275 | 70.4518 | 66.3614 | 51.221 | 0.72527 | 0.70452 | 0.66361 | 0.51221 | 0.020757 | 0.1514 | 7.607 | 9.5167 | 1.7242
38930.525 | 960 | 855 | 38930.5251 | 1196 | 970 | 1771.5 | 1904.5 | 58.6081 | 52.1978 | 73.0159 | 59.2186 | 0.58608 | 0.52198 | 0.73016 | 0.59219 | 0.064103 | 0.13797 | 235.1822 | 221.9241 | 24.0287
38930.5257 | 1012 | 921 | 38930.5257 | 1070 | 993 | 1830.5 | 1963.5 | 61.7827 | 56.2271 | 65.3236 | 60.6227 | 0.61783 | 0.56227 | 0.65324 | 0.60623 | 0.055556 | 0.047009 | 974.3922 | 4187.2066 | 19.0902
38930.5264 | 944 | 827 | 38930.5264 | 993 | 886 | 1889 | 2022 | 57.6313 | 50.4884 | 60.6227 | 54.0904 | 0.57631 | 0.50488 | 0.60623 | 0.5409 | 0.071429 | 0.065324 | 1355.0142 | 2691.4998 | 39.8752
38930.5271 | 997 | 985 | 38930.5271 | 1016 | 1113 | 1948 | 2081 | 60.8669 | 60.1343 | 62.0269 | 67.9487 | 0.60867 | 0.60134 | 0.62027 | 0.67949 | 0.007326 | 0.059219 | 155.3655 | 139.4554 | 7.7466
38930.5278 | 1116 | 1054 | 38930.5278 | 960 | 936 | 2006.5 | 2139.5 | 68.1319 | 64.3468 | 58.6081 | 57.1429 | 0.68132 | 0.64347 | 0.58608 | 0.57143 | 0.037851 | 0.014652 | 352.9674 | 478.0738 | 4.4709
38930.5284 | 1000 | 894 | 38930.5285 | 950 | 1052 | 2065.5 | 2198.5 | 61.0501 | 54.5788 | 57.9976 | 64.2247 | 0.6105 | 0.54579 | 0.57998 | 0.64225 | 0.064713 | 0.062271 | 1103.0014 | 17558.0108 | 24.3601
38930.5291 | 1027 | 1121 | 38930.5291 | 1029 | 943 | 2124.5 | 2257.5 | 62.6984 | 68.4371 | 62.8205 | 57.5702 | 0.62698 | 0.68437 | 0.62821 | 0.5757 | 0.057387 | 0.052503 | 2188.0376 | 2526.7341 | 3.0016
38930.5298 | 1109 | 1172 | 38930.5298 | 1133 | 1082 | 2183 | 2316 | 67.7045 | 71.5507 | 69.1697 | 66.0562 | 0.67705 | 0.71551 | 0.6917 | 0.66056 | 0.038462 | 0.031136 | 14428.9895 | 2091.3018 | 13.6787
38930.5305 | 954 | 940 | 38930.5305 | 1191 | 1182 | 2242 | 2375 | 58.2418 | 57.3871 | 72.7106 | 72.1612 | 0.58242 | 0.57387 | 0.72711 | 0.72161 | 0.008547 | 0.0054945 | 954.0852 | 874.5836 | 20.9092
38930.5312 | 949 | 1048 | 38930.5312 | 960 | 865 | 2300.5 | 2433.5 | 57.9365 | 63.9805 | 58.6081 | 52.8083 | 0.57937 | 0.6398 | 0.58608 | 0.52808 | 0.06044 | 0.057998 | 2985.941 | 1746.1823 | 10.471

## C2-4
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38930.5032 | 1 | 0 | 38930.5033 | 1 | 0 | -112.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5039 | 1 | 0 | 38930.5039 | 1 | 0 | -53.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5046 | 1 | 0 | 38930.5046 | 1 | 0 | 5 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5053 | 1 | 0 | 38930.5053 | 1 | 0 | 64 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.506 | 1 | 0 | 38930.506 | 1 | 0 | 122.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5066 | 1 | 0 | 38930.5067 | 1 | 0 | 181.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5073 | 1 | 0 | 38930.5073 | 1 | 0 | 240 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.508 | 1 | 0 | 38930.508 | 1 | 0 | 299 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5087 | 1 | 0 | 38930.5087 | 1 | 0 | 358 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5094 | 1 | 0 | 38930.5094 | 1 | 0 | 416.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.51 | 1 | 0 | 38930.5101 | 1 | 0 | 475.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5107 | 1 | 0 | 38930.5107 | 1 | 0 | 534 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5114 | 1 | 0 | 38930.5114 | 1 | 0 | 593 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5121 | 1 | 0 | 38930.5121 | 1 | 0 | 651.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5128 | 1 | 0 | 38930.5128 | 1 | 0 | 710.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5134 | 1 | 0 | 38930.5135 | 1 | 0 | 769.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5141 | 1 | 0 | 38930.5141 | 1 | 0 | 828 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5148 | 1 | 0 | 38930.5148 | 1 | 0 | 887 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5155 | 1 | 0 | 38930.5155 | 1 | 0 | 945.5 | 1078.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5162 | 1 | 0 | 38930.5162 | 1 | 0 | 1004.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5169 | 1 | 0 | 38930.5169 | 1 | 0 | 1063.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5175 | 1 | 0 | 38930.5175 | 1 | 0 | 1122 | 1255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5182 | 1 | 0 | 38930.5182 | 1 | 0 | 1181 | 1314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5189 | 1 | 0 | 38930.5189 | 1 | 0 | 1239.5 | 1372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5196 | 2 | 2 | 38930.5196 | 903 | 872 | 1298.5 | 1431.5 | 0.1221 | 0.1221 | 55.1282 | 53.2357 | 0.001221 | 0.001221 | 0.55128 | 0.53236 | 0 | 0.018926 | 4117149.0652 | 3900.6254 | 102815.1371
38930.5202 | 978 | 1077 | 38930.5203 | 1154 | 1187 | 1357 | 1490 | 59.707 | 65.7509 | 70.4518 | 72.4664 | 0.59707 | 0.65751 | 0.70452 | 0.72466 | 0.06044 | 0.020147 | 319.673 | 420.6103 | 4.3524
38930.5209 | 46 | 55 | 38930.5209 | 964 | 930 | 1416 | 1549 | 2.8083 | 3.3578 | 58.8523 | 56.7766 | 0.028083 | 0.033578 | 0.58852 | 0.56777 | 0.0054945 | 0.020757 | 27432.9824 | 3753.7504 | 3563.292
38930.5216 | 15 | 30 | 38930.5216 | 969 | 954 | 1475 | 1608 | 0.91575 | 1.8315 | 59.1575 | 58.2418 | 0.0091575 | 0.018315 | 0.59158 | 0.58242 | 0.0091575 | 0.0091575 | 14192.1859 | 13820.0197 | 6843.8785
38930.5223 | 6 | 21 | 38930.5223 | 1180 | 1188 | 1533.5 | 1666.5 | 0.3663 | 1.2821 | 72.0391 | 72.5275 | 0.003663 | 0.012821 | 0.72039 | 0.72527 | 0.0091575 | 0.004884 | 14037.0412 | 201376.1413 | 9928.4982
38930.523 | 6 | 21 | 38930.523 | 1133 | 1077 | 1592.5 | 1725.5 | 0.3663 | 1.2821 | 69.1697 | 65.7509 | 0.003663 | 0.012821 | 0.6917 | 0.65751 | 0.0091575 | 0.034188 | 15101.0015 | 2005.4423 | 9461.6309
38930.5237 | 6 | 19 | 38930.5237 | 944 | 826 | 1651.5 | 1784.5 | 0.3663 | 1.16 | 57.6313 | 50.4274 | 0.003663 | 0.0116 | 0.57631 | 0.50427 | 0.0079365 | 0.072039 | 18891.5894 | 1028.8162 | 10016.0299
38930.5243 | 1110 | 1092 | 38930.5244 | 964 | 858 | 1710 | 1843 | 67.7656 | 66.6667 | 58.8523 | 52.381 | 0.67766 | 0.66667 | 0.58852 | 0.52381 | 0.010989 | 0.064713 | 226.7328 | 257.3167 | 5.8679
38930.525 | 962 | 876 | 38930.525 | 1037 | 953 | 1768.5 | 1901.5 | 58.7302 | 53.4799 | 63.3089 | 58.1807 | 0.5873 | 0.5348 | 0.63309 | 0.58181 | 0.052503 | 0.051282 | 2129.8855 | 2741.0464 | 30.2899
38930.5257 | 1004 | 931 | 38930.5257 | 1173 | 1163 | 1827.5 | 1960.5 | 61.2943 | 56.8376 | 71.6117 | 71.0012 | 0.61294 | 0.56838 | 0.71612 | 0.71001 | 0.044567 | 0.006105 | 67.8655 | 59.6358 | 7.1432
38930.5264 | 1091 | 1037 | 38930.5264 | 1136 | 1076 | 1886.5 | 2019.5 | 66.6056 | 63.3089 | 69.3529 | 65.6899 | 0.66606 | 0.63309 | 0.69353 | 0.6569 | 0.032967 | 0.03663 | 1239.6048 | 3645.3444 | 1.406
38930.527 | 896 | 865 | 38930.5271 | 1166 | 825 | 1945 | 2078 | 54.7009 | 52.8083 | 71.1844 | 50.3663 | 0.54701 | 0.52808 | 0.71184 | 0.50366 | 0.018926 | 0.20818 | 165.2504 | 122.6133 | 22.4149
38930.5277 | 1133 | 955 | 38930.5278 | 1152 | 1102 | 2004 | 2137 | 69.1697 | 58.3028 | 70.3297 | 67.2772 | 0.6917 | 0.58303 | 0.7033 | 0.67277 | 0.10867 | 0.030525 | 89.6844 | 104.4008 | 1.3382
38930.5284 | 1025 | 1096 | 38930.5284 | 983 | 880 | 2062.5 | 2195.5 | 62.5763 | 66.9109 | 60.0122 | 53.7241 | 0.62576 | 0.66911 | 0.60012 | 0.53724 | 0.043346 | 0.062882 | 811.4884 | 1737.5565 | 0.68848
38930.5291 | 1008 | 1027 | 38930.5291 | 960 | 854 | 2121.5 | 2254.5 | 61.5385 | 62.6984 | 58.6081 | 52.1368 | 0.61538 | 0.62698 | 0.58608 | 0.52137 | 0.0116 | 0.064713 | 456.62 | 460.5383 | 6.2416
38930.5298 | 1100 | 1122 | 38930.5298 | 925 | 899 | 2180.5 | 2313.5 | 67.1551 | 68.4982 | 56.4713 | 54.884 | 0.67155 | 0.68498 | 0.56471 | 0.54884 | 0.013431 | 0.015873 | 6417.5974 | 18053.199 | 9.6595
38930.5305 | 1051 | 1004 | 38930.5305 | 1166 | 1187 | 2239 | 2372 | 64.1636 | 61.2943 | 71.1844 | 72.4664 | 0.64164 | 0.61294 | 0.71184 | 0.72466 | 0.028694 | 0.012821 | 793.9652 | 1157.195 | 5.3192
38930.5311 | 1116 | 1065 | 38930.5312 | 1168 | 1128 | 2298 | 2431 | 68.1319 | 65.0183 | 71.3065 | 68.8645 | 0.68132 | 0.65018 | 0.71306 | 0.68864 | 0.031136 | 0.02442 | 4630.3651 | 3614.1158 | 6.2112

## C2-3
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38930.5032 | 1 | 0 | 38930.5032 | 1 | 0 | -115.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5039 | 1 | 0 | 38930.5039 | 1 | 0 | -56.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5046 | 1 | 0 | 38930.5046 | 1 | 0 | 2.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5052 | 1 | 0 | 38930.5053 | 1 | 0 | 61 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5059 | 1 | 0 | 38930.5059 | 1 | 0 | 120 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5066 | 1 | 0 | 38930.5066 | 1 | 0 | 178.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5073 | 1 | 0 | 38930.5073 | 1 | 0 | 237.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.508 | 1 | 0 | 38930.508 | 1 | 0 | 296 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5086 | 1 | 0 | 38930.5087 | 1 | 0 | 355 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5093 | 1 | 0 | 38930.5094 | 1 | 0 | 414 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.51 | 1 | 0 | 38930.51 | 1 | 0 | 472.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5107 | 1 | 0 | 38930.5107 | 1 | 0 | 531.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5114 | 1 | 0 | 38930.5114 | 1 | 0 | 590 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.512 | 1 | 0 | 38930.5121 | 1 | 0 | 649 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5127 | 1 | 0 | 38930.5127 | 1 | 0 | 707.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5134 | 1 | 0 | 38930.5134 | 1 | 0 | 766.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5141 | 1 | 0 | 38930.5141 | 1 | 0 | 825.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5148 | 1 | 0 | 38930.5148 | 1 | 0 | 884 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5155 | 1 | 0 | 38930.5155 | 1 | 0 | 943 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5161 | 1 | 0 | 38930.5161 | 1 | 0 | 1001.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5168 | 1 | 0 | 38930.5168 | 1 | 0 | 1060.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5175 | 1 | 0 | 38930.5175 | 1 | 0 | 1119.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5182 | 1 | 0 | 38930.5182 | 1 | 0 | 1178 | 1311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5189 | 1 | 0 | 38930.5189 | 1 | 0 | 1236.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5195 | 9 | 7 | 38930.5195 | 471 | 489 | 1295.5 | 1428.5 | 0.54945 | 0.42735 | 28.7546 | 29.8535 | 0.0054945 | 0.0042735 | 0.28755 | 0.29853 | 0.001221 | 0.010989 | 109289.9368 | 9354.8714 | 29640.5821
38930.5202 | 1134 | 1109 | 38930.5202 | 1020 | 988 | 1354.5 | 1487.5 | 69.2308 | 67.7045 | 62.2711 | 60.3175 | 0.69231 | 0.67705 | 0.62271 | 0.60317 | 0.015263 | 0.019536 | 313.673 | 386.2566 | 9.3101
38930.5209 | 952 | 982 | 38930.5209 | 1185 | 909 | 1413.5 | 1546.5 | 58.1197 | 59.9512 | 72.3443 | 55.4945 | 0.5812 | 0.59951 | 0.72344 | 0.55495 | 0.018315 | 0.1685 | 75.9944 | 65.5641 | 7.2192
38930.5216 | 1138 | 1081 | 38930.5216 | 1060 | 980 | 1472 | 1605 | 69.475 | 65.9951 | 64.7131 | 59.8291 | 0.69475 | 0.65995 | 0.64713 | 0.59829 | 0.034799 | 0.04884 | 123.4584 | 147.5252 | 5.8431
38930.5223 | 1066 | 986 | 38930.5223 | 1119 | 1163 | 1531 | 1664 | 65.0794 | 60.1954 | 68.315 | 71.0012 | 0.65079 | 0.60195 | 0.68315 | 0.71001 | 0.04884 | 0.026862 | 293.2103 | 355.8432 | 4.831
38930.5229 | 1024 | 1029 | 38930.523 | 1123 | 1068 | 1589.5 | 1722.5 | 62.5153 | 62.8205 | 68.5592 | 65.2015 | 0.62515 | 0.62821 | 0.68559 | 0.65201 | 0.0030525 | 0.033578 | 40.3146 | 38.1633 | 1.6111
38930.5236 | 1027 | 1027 | 38930.5236 | 948 | 831 | 1648.5 | 1781.5 | 62.6984 | 62.6984 | 57.8755 | 50.7326 | 0.62698 | 0.62698 | 0.57875 | 0.50733 | 0 | 0.071429 | 342.7109 | 324.0862 | 4.3917
38930.5243 | 1120 | 1175 | 38930.5243 | 1194 | 1173 | 1707 | 1840 | 68.3761 | 71.7338 | 72.8938 | 71.6117 | 0.68376 | 0.71734 | 0.72894 | 0.71612 | 0.033578 | 0.012821 | 1799.9612 | 695400.9849 | 15.4854
38930.525 | 1155 | 1188 | 38930.525 | 1113 | 1051 | 1766 | 1899 | 70.5128 | 72.5275 | 67.9487 | 64.1636 | 0.70513 | 0.72527 | 0.67949 | 0.64164 | 0.020147 | 0.037851 | 714.6634 | 1175.6333 | 17.841
38930.5257 | 1035 | 955 | 38930.5257 | 951 | 847 | 1824.5 | 1957.5 | 63.1868 | 58.3028 | 58.0586 | 51.7094 | 0.63187 | 0.58303 | 0.58059 | 0.51709 | 0.04884 | 0.063492 | 6979.6773 | 1479.3616 | 12.066
38930.5263 | 1037 | 1041 | 38930.5264 | 1193 | 1167 | 1883.5 | 2016.5 | 63.3089 | 63.5531 | 72.8327 | 71.2454 | 0.63309 | 0.63553 | 0.72833 | 0.71245 | 0.002442 | 0.015873 | 961.6345 | 964.8278 | 3.0481
38930.527 | 1148 | 1100 | 38930.527 | 1057 | 976 | 1942.5 | 2075.5 | 70.0855 | 67.1551 | 64.5299 | 59.5849 | 0.70085 | 0.67155 | 0.6453 | 0.59585 | 0.029304 | 0.049451 | 141.9373 | 174.0804 | 7.7938
38930.5277 | 1067 | 1148 | 38930.5277 | 957 | 934 | 2001 | 2134 | 65.1404 | 70.0855 | 58.4249 | 57.0208 | 0.6514 | 0.70085 | 0.58425 | 0.57021 | 0.049451 | 0.014042 | 203.7493 | 265.5036 | 6.4529
38930.5284 | 1192 | 1168 | 38930.5284 | 986 | 883 | 2060 | 2193 | 72.7717 | 71.3065 | 60.1954 | 53.9072 | 0.72772 | 0.71306 | 0.60195 | 0.53907 | 0.014652 | 0.062882 | 7.1459 | 9.0791 | 1.76
38930.5291 | 1020 | 932 | 38930.5291 | 918 | 875 | 2118.5 | 2251.5 | 62.2711 | 56.8987 | 56.044 | 53.4188 | 0.62271 | 0.56899 | 0.56044 | 0.53419 | 0.053724 | 0.026252 | 753.8988 | 1635.5949 | 16.2814
38930.5297 | 920 | 890 | 38930.5298 | 1033 | 1056 | 2177.5 | 2310.5 | 56.1661 | 54.3346 | 63.0647 | 64.4689 | 0.56166 | 0.54335 | 0.63065 | 0.64469 | 0.018315 | 0.014042 | 2922.2794 | 8221.7232 | 33.6381
38930.5304 | 1109 | 1055 | 38930.5304 | 1049 | 979 | 2236.5 | 2369.5 | 67.7045 | 64.4078 | 64.0415 | 59.768 | 0.67705 | 0.64408 | 0.64042 | 0.59768 | 0.032967 | 0.042735 | 216.2663 | 257.1592 | 3.4793
38930.5311 | 1171 | 1133 | 38930.5311 | 1011 | 922 | 2295 | 2428 | 71.4896 | 69.1697 | 61.7216 | 56.2882 | 0.7149 | 0.6917 | 0.61722 | 0.56288 | 0.023199 | 0.054335 | 11.0263 | 13.3209 | 1.9814

## C1-7
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38930.5032 | 1 | 0 | 38930.5032 | 1 | 0 | -118 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5039 | 1 | 0 | 38930.5039 | 1 | 0 | -59.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5045 | 1 | 0 | 38930.5045 | 1 | 0 | -0.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5052 | 1 | 0 | 38930.5052 | 1 | 0 | 58 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5059 | 1 | 0 | 38930.5059 | 1 | 0 | 117 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5066 | 1 | 0 | 38930.5066 | 1 | 0 | 175.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5073 | 1 | 0 | 38930.5073 | 1 | 0 | 234.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5079 | 1 | 0 | 38930.508 | 1 | 0 | 293.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5086 | 1 | 0 | 38930.5086 | 1 | 0 | 352 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5093 | 1 | 0 | 38930.5093 | 1 | 0 | 411 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.51 | 1 | 0 | 38930.51 | 1 | 0 | 470 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5107 | 1 | 0 | 38930.5107 | 1 | 0 | 528.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5113 | 1 | 0 | 38930.5114 | 1 | 0 | 587.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.512 | 1 | 0 | 38930.512 | 1 | 0 | 646 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5127 | 1 | 0 | 38930.5127 | 1 | 0 | 705 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5134 | 1 | 0 | 38930.5134 | 1 | 0 | 763.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5141 | 1 | 0 | 38930.5141 | 1 | 0 | 822.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5147 | 1 | 0 | 38930.5148 | 1 | 0 | 881.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5154 | 1 | 0 | 38930.5154 | 1 | 0 | 940 | 1073 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5161 | 1 | 0 | 38930.5161 | 1 | 0 | 999 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5168 | 1 | 0 | 38930.5168 | 1 | 0 | 1057.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5175 | 1 | 0 | 38930.5175 | 1 | 0 | 1116.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5181 | 1 | 0 | 38930.5182 | 1 | 0 | 1175.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5188 | 1 | 0 | 38930.5188 | 1 | 0 | 1234 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5195 | 1 | 0 | 38930.5195 | 1 | 0 | 1293 | 1426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5202 | 46 | 51 | 38930.5202 | 7 | 13 | 1351.5 | 1484.5 | 2.8083 | 3.1136 | 0.42735 | 0.79365 | 0.028083 | 0.031136 | 0.0042735 | 0.0079365 | 0.0030525 | 0.003663 | 42571.2039 | 35279.8908 | 3941.8074
38930.5209 | 1028 | 997 | 38930.5209 | 1024 | 994 | 1410.5 | 1543.5 | 62.7595 | 60.8669 | 62.5153 | 60.6838 | 0.62759 | 0.60867 | 0.62515 | 0.60684 | 0.018926 | 0.018315 | 4950.8907 | 10974.9211 | 8.7488
38930.5216 | 1159 | 1185 | 38930.5216 | 1066 | 987 | 1469.5 | 1602.5 | 70.757 | 72.3443 | 65.0794 | 60.2564 | 0.70757 | 0.72344 | 0.65079 | 0.60256 | 0.015873 | 0.04823 | 257.133 | 343.4564 | 15.0965
38930.5222 | 1005 | 902 | 38930.5222 | 929 | 1012 | 1528 | 1661 | 61.3553 | 55.0672 | 56.7155 | 61.7827 | 0.61355 | 0.55067 | 0.56716 | 0.61783 | 0.062882 | 0.050672 | 847.5479 | 3252.5084 | 22.1591
38930.5229 | 1010 | 924 | 38930.5229 | 1149 | 1103 | 1586.5 | 1719.5 | 61.6606 | 56.4103 | 70.1465 | 67.3382 | 0.61661 | 0.5641 | 0.70147 | 0.67338 | 0.052503 | 0.028083 | 109.3056 | 100.0958 | 9.6919
38930.5236 | 1070 | 992 | 38930.5236 | 1011 | 910 | 1645.5 | 1778.5 | 65.3236 | 60.5617 | 61.7216 | 55.5556 | 0.65324 | 0.60562 | 0.61722 | 0.55556 | 0.047619 | 0.061661 | 1733.183 | 5566.6067 | 5.0524
38930.5243 | 969 | 859 | 38930.5243 | 1190 | 1156 | 1704.5 | 1837.5 | 59.1575 | 52.442 | 72.6496 | 70.5739 | 0.59158 | 0.52442 | 0.7265 | 0.70574 | 0.067155 | 0.020757 | 87.0353 | 71.3199 | 13.8129
38930.5249 | 1057 | 979 | 38930.525 | 1019 | 926 | 1763 | 1896 | 64.5299 | 59.768 | 62.21 | 56.5324 | 0.6453 | 0.59768 | 0.6221 | 0.56532 | 0.047619 | 0.056777 | 4353.8219 | 1821.5652 | 7.4578
38930.5256 | 1036 | 950 | 38930.5256 | 1161 | 1187 | 1822 | 1955 | 63.2479 | 57.9976 | 70.8791 | 72.4664 | 0.63248 | 0.57998 | 0.70879 | 0.72466 | 0.052503 | 0.015873 | 178.9378 | 184.1456 | 8.665
38930.5263 | 1101 | 1029 | 38930.5263 | 1062 | 982 | 1880.5 | 2013.5 | 67.2161 | 62.8205 | 64.8352 | 59.9512 | 0.67216 | 0.62821 | 0.64835 | 0.59951 | 0.043956 | 0.04884 | 800.0418 | 1888.2159 | 1.5671
38930.527 | 1096 | 1165 | 38930.527 | 1189 | 1184 | 1939.5 | 2072.5 | 66.9109 | 71.1233 | 72.5885 | 72.2833 | 0.66911 | 0.71123 | 0.72589 | 0.72283 | 0.042125 | 0.0030525 | 758.8385 | 1791.6667 | 12.0307
38930.5277 | 1036 | 949 | 38930.5277 | 1125 | 1067 | 1998.5 | 2131.5 | 63.2479 | 57.9365 | 68.6813 | 65.1404 | 0.63248 | 0.57937 | 0.68681 | 0.6514 | 0.053114 | 0.035409 | 166.6928 | 169.7338 | 8.4888
38930.5283 | 942 | 827 | 38930.5284 | 935 | 827 | 2057 | 2190 | 57.5092 | 50.4884 | 57.0818 | 50.4884 | 0.57509 | 0.50488 | 0.57082 | 0.50488 | 0.070208 | 0.065934 | 1506.9578 | 2217.607 | 39.8037
38930.529 | 991 | 888 | 38930.5291 | 939 | 828 | 2116 | 2249 | 60.5006 | 54.2125 | 57.326 | 50.5495 | 0.60501 | 0.54212 | 0.57326 | 0.50549 | 0.062882 | 0.067766 | 2603.3654 | 1482.4418 | 24.6882
38930.5297 | 1026 | 951 | 38930.5297 | 1087 | 1162 | 2174.5 | 2307.5 | 62.6374 | 58.0586 | 66.3614 | 70.9402 | 0.62637 | 0.58059 | 0.66361 | 0.7094 | 0.045788 | 0.045788 | 182.0361 | 182.1332 | 9.2333
38930.5304 | 1021 | 945 | 38930.5304 | 1191 | 1167 | 2233.5 | 2366.5 | 62.3321 | 57.6923 | 72.7106 | 71.2454 | 0.62332 | 0.57692 | 0.72711 | 0.71245 | 0.046398 | 0.014652 | 202.4554 | 203.9328 | 10.4389
38930.5311 | 1157 | 1114 | 38930.5311 | 956 | 1059 | 2292.5 | 2425.5 | 70.6349 | 68.0098 | 58.3639 | 64.652 | 0.70635 | 0.6801 | 0.58364 | 0.64652 | 0.026252 | 0.062882 | 113.2352 | 139.0279 | 8.2484

## C1-6
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38930.5031 | 1 | 0 | 38930.5032 | 1 | 0 | -121 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5038 | 1 | 0 | 38930.5038 | 1 | 0 | -62 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5045 | 1 | 0 | 38930.5045 | 1 | 0 | -3.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5052 | 1 | 0 | 38930.5052 | 1 | 0 | 55.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5059 | 1 | 0 | 38930.5059 | 1 | 0 | 114 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5065 | 1 | 0 | 38930.5066 | 1 | 0 | 173 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5072 | 1 | 0 | 38930.5072 | 1 | 0 | 232 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5079 | 1 | 0 | 38930.5079 | 1 | 0 | 290.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5086 | 1 | 0 | 38930.5086 | 1 | 0 | 349.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5093 | 1 | 0 | 38930.5093 | 1 | 0 | 408 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5099 | 1 | 0 | 38930.51 | 1 | 0 | 467 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5106 | 1 | 0 | 38930.5106 | 1 | 0 | 525.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5113 | 1 | 0 | 38930.5113 | 1 | 0 | 584.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.512 | 1 | 0 | 38930.512 | 1 | 0 | 643.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5127 | 1 | 0 | 38930.5127 | 1 | 0 | 702 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5133 | 1 | 0 | 38930.5134 | 1 | 0 | 761 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.514 | 1 | 0 | 38930.514 | 1 | 0 | 819.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5147 | 1 | 0 | 38930.5147 | 1 | 0 | 878.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5154 | 1 | 0 | 38930.5154 | 1 | 0 | 937.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5161 | 1 | 0 | 38930.5161 | 1 | 0 | 996 | 1129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5167 | 1 | 0 | 38930.5168 | 1 | 0 | 1055 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5174 | 1 | 0 | 38930.5174 | 1 | 0 | 1113.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5181 | 1 | 0 | 38930.5181 | 1 | 0 | 1172.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5188 | 1 | 0 | 38930.5188 | 1 | 0 | 1231 | 1364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5195 | 1 | 0 | 38930.5195 | 1 | 0 | 1290 | 1423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5202 | 955 | 908 | 38930.5202 | 985 | 1025 | 1349 | 1482 | 58.3028 | 55.4335 | 60.1343 | 62.5763 | 0.58303 | 0.55433 | 0.60134 | 0.62576 | 0.028694 | 0.02442 | 2249.3326 | 20255.0815 | 27.4
38930.5208 | 1168 | 1146 | 38930.5208 | 950 | 1065 | 1407.5 | 1540.5 | 71.3065 | 69.9634 | 57.9976 | 65.0183 | 0.71306 | 0.69963 | 0.57998 | 0.65018 | 0.013431 | 0.070208 | 114.3209 | 142.4243 | 10.3033
38930.5215 | 1007 | 907 | 38930.5215 | 1046 | 958 | 1466.5 | 1599.5 | 61.4774 | 55.3724 | 63.8584 | 58.486 | 0.61477 | 0.55372 | 0.63858 | 0.58486 | 0.06105 | 0.053724 | 1157.6265 | 20345.6399 | 21.8353
38930.5222 | 1064 | 980 | 38930.5222 | 1081 | 1004 | 1525 | 1658 | 64.9573 | 59.8291 | 65.9951 | 61.2943 | 0.64957 | 0.59829 | 0.65995 | 0.61294 | 0.051282 | 0.047009 | 878.8284 | 2771.0439 | 6.7976
38930.5229 | 1059 | 978 | 38930.5229 | 982 | 883 | 1584 | 1717 | 64.652 | 59.707 | 59.9512 | 53.9072 | 0.64652 | 0.59707 | 0.59951 | 0.53907 | 0.049451 | 0.06044 | 6306.7716 | 1521.2914 | 7.2936
38930.5236 | 981 | 871 | 38930.5236 | 971 | 862 | 1642.5 | 1775.5 | 59.8901 | 53.1746 | 59.2796 | 52.6252 | 0.5989 | 0.53175 | 0.5928 | 0.52625 | 0.067155 | 0.066545 | 1766.3982 | 1897.0391 | 28.4672
38930.5242 | 1101 | 1032 | 38930.5242 | 1124 | 1177 | 1701.5 | 1834.5 | 67.2161 | 63.0037 | 68.6203 | 71.8559 | 0.67216 | 0.63004 | 0.6862 | 0.71856 | 0.042125 | 0.032357 | 1577.9565 | 21212.086 | 1.927
38930.5249 | 941 | 866 | 38930.5249 | 1125 | 1168 | 1760.5 | 1893.5 | 57.4481 | 52.8694 | 68.6813 | 71.3065 | 0.57448 | 0.52869 | 0.68681 | 0.71306 | 0.045788 | 0.026252 | 397.3882 | 393.7603 | 28.1804
38930.5256 | 974 | 957 | 38930.5256 | 942 | 830 | 1819 | 1952 | 59.4628 | 58.4249 | 57.5092 | 50.6716 | 0.59463 | 0.58425 | 0.57509 | 0.50672 | 0.010379 | 0.068376 | 618.1552 | 572.1591 | 16.1902
38930.5263 | 1083 | 1004 | 38930.5263 | 1009 | 1000 | 1878 | 2011 | 66.1172 | 61.2943 | 61.5995 | 61.0501 | 0.66117 | 0.61294 | 0.616 | 0.6105 | 0.04823 | 0.0054945 | 170.3249 | 190.9695 | 1.7009
38930.527 | 1096 | 1033 | 38930.527 | 1063 | 986 | 1936.5 | 2069.5 | 66.9109 | 63.0647 | 64.8962 | 60.1954 | 0.66911 | 0.63065 | 0.64896 | 0.60195 | 0.038462 | 0.047009 | 368.5907 | 485.156 | 1.2826
| 1034 | 990 | 38930.5277 | 973 | 954 | 1996 | 2129 | 63.1258 | 60.4396 | 59.4017 | 58.2418 | 0.63126 | 0.6044 | 0.59402 | 0.58242 | 0.026862 | 0.0116 | 911.1208 | 1330.1487 | 8.3632
38930.5283 | 972 | 946 | 38930.5283 | 952 | 919 | 2054.5 | 2187.5 | 59.3407 | 57.7534 | 58.1197 | 56.105 | 0.59341 | 0.57753 | 0.5812 | 0.56105 | 0.015873 | 0.020147 | 44147.5395 | 4040.0694 | 20.1173
38930.529 | 1006 | 1106 | 38930.529 | 953 | 926 | 2113 | 2246 | 61.4164 | 67.5214 | 58.1807 | 56.5324 | 0.61416 | 0.67521 | 0.58181 | 0.56532 | 0.06105 | 0.016484 | 301.8451 | 414.6188 | 0.074303
38930.5297 | 1010 | 930 | 38930.5297 | 1082 | 1018 | 2172 | 2305 | 61.6606 | 56.7766 | 66.0562 | 62.149 | 0.61661 | 0.56777 | 0.66056 | 0.62149 | 0.04884 | 0.039072 | 829.6272 | 1756.2515 | 17.602
38930.5304 | 1109 | 1057 | 38930.5304 | 998 | 912 | 2230.5 | 2363.5 | 67.7045 | 64.5299 | 60.928 | 55.6777 | 0.67705 | 0.6453 | 0.60928 | 0.55678 | 0.031746 | 0.052503 | 472.3993 | 658.418 | 4.3514
38930.531 | 1149 | 1188 | 38930.5311 | 1187 | 1153 | 2289.5 | 2422.5 | 70.1465 | 72.5275 | 72.4664 | 70.3907 | 0.70147 | 0.72527 | 0.72466 | 0.70391 | 0.02381 | 0.020757 | 11153.5577 | 3913.451 | 18.3838

## C1-5
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38930.5031 | 1 | 0 | 38930.5031 | 1 | 0 | -123.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5038 | 1 | 0 | 38930.5038 | 1 | 0 | -65 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5045 | 1 | 0 | 38930.5045 | 1 | 0 | -6 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5052 | 1 | 0 | 38930.5052 | 1 | 0 | 52.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5058 | 1 | 0 | 38930.5058 | 1 | 0 | 111.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5065 | 1 | 0 | 38930.5065 | 1 | 0 | 170 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5072 | 1 | 0 | 38930.5072 | 1 | 0 | 229 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5079 | 1 | 0 | 38930.5079 | 1 | 0 | 288 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5086 | 1 | 0 | 38930.5086 | 1 | 0 | 346.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5092 | 1 | 0 | 38930.5092 | 1 | 0 | 405.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5099 | 1 | 0 | 38930.5099 | 1 | 0 | 464 | 597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5106 | 1 | 0 | 38930.5106 | 1 | 0 | 523 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5113 | 1 | 0 | 38930.5113 | 1 | 0 | 581.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.512 | 1 | 0 | 38930.512 | 1 | 0 | 640.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5126 | 1 | 0 | 38930.5127 | 1 | 0 | 699.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5133 | 1 | 0 | 38930.5133 | 1 | 0 | 758 | 891 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.514 | 1 | 0 | 38930.514 | 1 | 0 | 817 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5147 | 1 | 0 | 38930.5147 | 1 | 0 | 875.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5154 | 1 | 0 | 38930.5154 | 1 | 0 | 934.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.516 | 1 | 0 | 38930.5161 | 1 | 0 | 993.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5167 | 1 | 0 | 38930.5167 | 1 | 0 | 1052 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5174 | 1 | 0 | 38930.5174 | 1 | 0 | 1111 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5181 | 1 | 0 | 38930.5181 | 1 | 0 | 1169.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5188 | 1 | 0 | 38930.5188 | 1 | 0 | 1228.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5194 | 1 | 0 | 38930.5195 | 1 | 0 | 1287.5 | 1420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5201 | 1049 | 1098 | 38930.5201 | 1026 | 993 | 1346 | 1479 | 64.0415 | 67.033 | 62.6374 | 60.6227 | 0.64042 | 0.67033 | 0.62637 | 0.60623 | 0.029915 | 0.020147 | 389.2959 | 489.4814 | 2.5697
38930.5208 | 1188 | 1172 | 38930.5208 | 1180 | 1127 | 1405 | 1538 | 72.5275 | 71.5507 | 72.0391 | 68.8034 | 0.72527 | 0.71551 | 0.72039 | 0.68803 | 0.009768 | 0.032357 | 970.13 | 1476.9986 | 19.7371
38930.5215 | 951 | 839 | 38930.5215 | 1030 | 942 | 1463.5 | 1596.5 | 58.0586 | 51.221 | 62.8816 | 57.5092 | 0.58059 | 0.51221 | 0.62882 | 0.57509 | 0.068376 | 0.053724 | 986.286 | 14421.3891 | 38.2355
38930.5222 | 1136 | 1178 | 38930.5222 | 957 | 841 | 1522.5 | 1655.5 | 69.3529 | 71.917 | 58.4249 | 51.3431 | 0.69353 | 0.71917 | 0.58425 | 0.51343 | 0.025641 | 0.070818 | 157.5077 | 203.7006 | 11.4434
38930.5228 | 1168 | 829 | 38930.5229 | 1112 | 1049 | 1581.5 | 1714.5 | 71.3065 | 50.6105 | 67.8877 | 64.0415 | 0.71306 | 0.50611 | 0.67888 | 0.64042 | 0.20696 | 0.038462 | 26.5963 | 25.7918 | 2.8695
38930.5235 | 938 | 820 | 38930.5235 | 1132 | 1181 | 1640 | 1773 | 57.265 | 50.0611 | 69.1087 | 72.1001 | 0.57265 | 0.50061 | 0.69109 | 0.721 | 0.072039 | 0.029915 | 243.8439 | 225.3529 | 29.988
38930.5242 | 1105 | 1144 | 38930.5242 | 1165 | 1188 | 1698.5 | 1831.5 | 67.4603 | 69.8413 | 71.1233 | 72.5275 | 0.6746 | 0.69841 | 0.71123 | 0.72527 | 0.02381 | 0.014042 | 3784.4218 | 9252.697 | 11.7593
38930.5249 | 1086 | 1016 | 38930.5249 | 1001 | 901 | 1757.5 | 1890.5 | 66.3004 | 62.0269 | 61.1111 | 55.0061 | 0.663 | 0.62027 | 0.61111 | 0.55006 | 0.042735 | 0.06105 | 953.9736 | 2698.033 | 1.0459
38930.5256 | 970 | 861 | 38930.5256 | 984 | 878 | 1816.5 | 1949.5 | 59.2186 | 52.5641 | 60.0733 | 53.602 | 0.59219 | 0.52564 | 0.60073 | 0.53602 | 0.066545 | 0.064713 | 1681.075 | 2099.6619 | 31.2658
38930.5262 | 947 | 826 | 38930.5263 | 998 | 890 | 1875 | 2008 | 57.8144 | 50.4274 | 60.928 | 54.3346 | 0.57814 | 0.50427 | 0.60928 | 0.54335 | 0.073871 | 0.065934 | 1236.0595 | 3097.5365 | 39.8773
38930.5269 | 1126 | 1071 | 38930.5269 | 1140 | 1184 | 1934 | 2067 | 68.7424 | 65.3846 | 69.5971 | 72.2833 | 0.68742 | 0.65385 | 0.69597 | 0.72283 | 0.033578 | 0.026862 | 4813.3446 | 3104.8795 | 7.5966
38930.5276 | 1192 | 1164 | 38930.5276 | 1016 | 927 | 1992.5 | 2125.5 | 72.7717 | 71.0623 | 62.0269 | 56.5934 | 0.72772 | 0.71062 | 0.62027 | 0.56593 | 0.017094 | 0.054335 | 94.1975 | 122.5581 | 11.4952
38930.5283 | 1086 | 1159 | 38930.5283 | 988 | 885 | 2051.5 | 2184.5 | 66.3004 | 70.757 | 60.3175 | 54.0293 | 0.663 | 0.70757 | 0.60317 | 0.54029 | 0.044567 | 0.062882 | 348.191 | 522.169 | 9.5571
38930.529 | 1194 | 1175 | 38930.529 | 1126 | 1068 | 2110.5 | 2243.5 | 72.8938 | 71.7338 | 68.7424 | 65.2015 | 0.72894 | 0.71734 | 0.68742 | 0.65201 | 0.0116 | 0.035409 | 704.1147 | 1053.61 | 19.8971
38930.5296 | 1078 | 1017 | 38930.5297 | 949 | 1048 | 2169 | 2302 | 65.812 | 62.0879 | 57.9365 | 63.9805 | 0.65812 | 0.62088 | 0.57937 | 0.6398 | 0.037241 | 0.06044 | 468.256 | 635.4772 | 1.531
38930.5303 | 1157 | 1124 | 38930.5303 | 1060 | 1093 | 2228 | 2361 | 70.6349 | 68.6203 | 64.7131 | 66.7277 | 0.70635 | 0.6862 | 0.64713 | 0.66728 | 0.020147 | 0.020147 | 9470.1802 | 4907.2375 | 14.6464
38930.531 | 1101 | 1041 | 38930.531 | 1073 | 1106 | 2286.5 | 2419.5 | 67.2161 | 63.5531 | 65.5067 | 67.5214 | 0.67216 | 0.63553 | 0.65507 | 0.67521 | 0.03663 | 0.020147 | 352.3398 | 458.1293 | 2.2851

## C1-4
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38930.5031 | 1 | 0 | 38930.5031 | 1 | 0 | -126.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5038 | 1 | 0 | 38930.5038 | 1 | 0 | -67.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5044 | 1 | 0 | 38930.5045 | 1 | 0 | -9 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5051 | 1 | 0 | 38930.5051 | 1 | 0 | 49.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5058 | 1 | 0 | 38930.5058 | 1 | 0 | 108.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5065 | 1 | 0 | 38930.5065 | 1 | 0 | 167.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5072 | 1 | 0 | 38930.5072 | 1 | 0 | 226.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5078 | 1 | 0 | 38930.5079 | 1 | 0 | 285 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5085 | 1 | 0 | 38930.5085 | 1 | 0 | 343.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5092 | 1 | 0 | 38930.5092 | 1 | 0 | 402.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5099 | 1 | 0 | 38930.5099 | 1 | 0 | 461.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5106 | 1 | 0 | 38930.5106 | 1 | 0 | 520 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5112 | 1 | 0 | 38930.5113 | 1 | 0 | 579 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5119 | 1 | 0 | 38930.5119 | 1 | 0 | 637.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5126 | 1 | 0 | 38930.5126 | 1 | 0 | 696.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5133 | 1 | 0 | 38930.5133 | 1 | 0 | 755.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.514 | 1 | 0 | 38930.514 | 1 | 0 | 814 | 947 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5146 | 1 | 0 | 38930.5147 | 1 | 0 | 873 | 1006 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5153 | 1 | 0 | 38930.5153 | 1 | 0 | 931.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.516 | 1 | 0 | 38930.516 | 1 | 0 | 990.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5167 | 1 | 1 | 38930.5167 | 1 | 0 | 1049.5 | 1182.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.5174 | 1 | 0 | 38930.5174 | 1 | 0 | 1108 | 1241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.518 | 1 | 0 | 38930.5181 | 1 | 0 | 1167 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5187 | 1 | 0 | 38930.5187 | 1 | 0 | 1225.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5194 | 1 | 0 | 38930.5194 | 1 | 0 | 1284.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5201 | 163 | 169 | 38930.5201 | 234 | 227 | 1343.5 | 1476.5 | 9.9512 | 10.3175 | 14.2857 | 13.8584 | 0.099512 | 0.10317 | 0.14286 | 0.13858 | 0.003663 | 0.0042735 | 35930.2395 | 29506.2034 | 1050.2984
38930.5208 | 67 | 72 | 38930.5208 | 97 | 100 | 1402 | 1535 | 4.0904 | 4.3956 | 5.9219 | 6.105 | 0.040904 | 0.043956 | 0.059219 | 0.06105 | 0.0030525 | 0.0018315 | 41743.4661 | 73032.519 | 2737.9455
38930.5214 | 25 | 34 | 38930.5215 | 6 | 14 | 1461 | 1594 | 1.5263 | 2.0757 | 0.3663 | 0.8547 | 0.015263 | 0.020757 | 0.003663 | 0.008547 | 0.0054945 | 0.004884 | 23535.2926 | 26535.0552 | 6018.5538
38930.5221 | 5 | 20 | 38930.5221 | 6 | 15 | 1519.5 | 1652.5 | 0.30525 | 1.221 | 0.3663 | 0.91575 | 0.0030525 | 0.01221 | 0.003663 | 0.0091575 | 0.0091575 | 0.0054945 | 14133.0084 | 23690.7114 | 10396.2169
38930.5228 | 6 | 21 | 38930.5228 | 5 | 14 | 1578.5 | 1711.5 | 0.3663 | 1.2821 | 0.30525 | 0.8547 | 0.003663 | 0.012821 | 0.0030525 | 0.008547 | 0.0091575 | 0.0054945 | 14130.3296 | 23683.1636 | 9891.6619
38930.5235 | 6 | 20 | 38930.5235 | 6 | 13 | 1637 | 1770 | 0.3663 | 1.221 | 0.3663 | 0.79365 | 0.003663 | 0.01221 | 0.003663 | 0.0079365 | 0.008547 | 0.0042735 | 15121.0264 | 30474.57 | 10400.97
38930.5242 | 665 | 595 | 38930.5242 | 749 | 722 | 1696 | 1829 | 40.5983 | 36.3248 | 45.7265 | 44.0781 | 0.40598 | 0.36325 | 0.45726 | 0.44078 | 0.042735 | 0.016484 | 1946.1197 | 13505.8648 | 142.311
38930.5248 | 968 | 880 | 38930.5249 | 1005 | 1025 | 1755 | 1888 | 59.0965 | 53.7241 | 61.3553 | 62.5763 | 0.59096 | 0.53724 | 0.61355 | 0.62576 | 0.053724 | 0.01221 | 458.9219 | 544.8845 | 25.4459
38930.5255 | 1137 | 1121 | 38930.5255 | 1003 | 924 | 1813.5 | 1946.5 | 69.4139 | 68.4371 | 61.2332 | 56.4103 | 0.69414 | 0.68437 | 0.61233 | 0.5641 | 0.009768 | 0.04823 | 67.2297 | 78.0766 | 5.6704
38930.5262 | 1043 | 1077 | 38930.5262 | 960 | 947 | 1872.5 | 2005.5 | 63.6752 | 65.7509 | 58.6081 | 57.8144 | 0.63675 | 0.65751 | 0.58608 | 0.57814 | 0.020757 | 0.0079365 | 848.4968 | 1169.2831 | 0.59704
38930.5269 | 1054 | 996 | 38930.5269 | 925 | 908 | 1931 | 2064 | 64.3468 | 60.8059 | 56.4713 | 55.4335 | 0.64347 | 0.60806 | 0.56471 | 0.55433 | 0.035409 | 0.010379 | 680.6762 | 1020.6642 | 5.7627
38930.5276 | 935 | 837 | 38930.5276 | 985 | 992 | 1990 | 2123 | 57.0818 | 51.0989 | 60.1343 | 60.5617 | 0.57082 | 0.51099 | 0.60134 | 0.60562 | 0.059829 | 0.0042735 | 476.2065 | 560.3315 | 34.573
38930.5283 | 905 | 800 | 38930.5283 | 984 | 898 | 2048.5 | 2181.5 | 55.2503 | 48.84 | 60.0733 | 54.823 | 0.5525 | 0.4884 | 0.60073 | 0.54823 | 0.064103 | 0.052503 | 1297.5203 | 6723.933 | 50.2551
38930.5289 | 977 | 894 | 38930.5289 | 999 | 1013 | 2107.5 | 2240.5 | 59.6459 | 54.5788 | 60.989 | 61.8437 | 0.59646 | 0.54579 | 0.60989 | 0.61844 | 0.050672 | 0.008547 | 450.2033 | 527.9479 | 22.7605
38930.5296 | 1073 | 1026 | 38930.5296 | 912 | 830 | 2166.5 | 2299.5 | 65.5067 | 62.6374 | 55.6777 | 50.6716 | 0.65507 | 0.62637 | 0.55678 | 0.50672 | 0.028694 | 0.050061 | 1435.8617 | 4034.3247 | 1.3334
38930.5303 | 989 | 930 | 38930.5303 | 1088 | 1052 | 2225 | 2358 | 60.3785 | 56.7766 | 66.4225 | 64.2247 | 0.60379 | 0.56777 | 0.66422 | 0.64225 | 0.03602 | 0.021978 | 643.7317 | 804.4287 | 18.5557
38930.531 | 977 | 905 | 38930.531 | 1080 | 1034 | 2284 | 2417 | 59.6459 | 55.2503 | 65.9341 | 63.1258 | 0.59646 | 0.5525 | 0.65934 | 0.63126 | 0.043956 | 0.028083 | 726.0457 | 1071.4277 | 23.3479

## C1-3
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38930.503 | 1 | 0 | 38930.5031 | 1 | 0 | -129.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5037 | 1 | 0 | 38930.5037 | 1 | 0 | -70.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5044 | 1 | 0 | 38930.5044 | 1 | 0 | -11.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5051 | 1 | 0 | 38930.5051 | 1 | 0 | 47 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5058 | 1 | 0 | 38930.5058 | 1 | 0 | 105.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5064 | 1 | 0 | 38930.5065 | 1 | 0 | 164.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5071 | 1 | 0 | 38930.5071 | 1 | 0 | 223.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5078 | 1 | 0 | 38930.5078 | 1 | 0 | 282.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5085 | 1 | 0 | 38930.5085 | 1 | 0 | 341 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5092 | 1 | 0 | 38930.5092 | 1 | 0 | 399.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5098 | 1 | 0 | 38930.5099 | 1 | 0 | 458.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5105 | 1 | 0 | 38930.5105 | 1 | 0 | 517.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5112 | 1 | 0 | 38930.5112 | 1 | 0 | 576 | 709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5119 | 1 | 0 | 38930.5119 | 1 | 0 | 635 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5126 | 1 | 0 | 38930.5126 | 1 | 0 | 693.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5133 | 1 | 0 | 38930.5133 | 1 | 0 | 752.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5139 | 1 | 0 | 38930.5139 | 1 | 0 | 811.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5146 | 1 | 0 | 38930.5146 | 1 | 0 | 870 | 1003 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5153 | 1 | 0 | 38930.5153 | 1 | 0 | 929 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.516 | 1 | 0 | 38930.516 | 1 | 0 | 987.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5167 | 1 | 0 | 38930.5167 | 1 | 0 | 1046.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5173 | 1 | 0 | 38930.5173 | 1 | 0 | 1105.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.518 | 1 | 0 | 38930.518 | 1 | 0 | 1164 | 1297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5187 | 1 | 0 | 38930.5187 | 1 | 0 | 1223 | 1356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5194 | 1 | 0 | 38930.5194 | 1 | 0 | 1281.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5201 | 1189 | 916 | 38930.5201 | 1170 | 1150 | 1340.5 | 1473.5 | 72.5885 | 55.9219 | 71.4286 | 70.2076 | 0.72589 | 0.55922 | 0.71429 | 0.70208 | 0.16667 | 0.01221 | 76.1238 | 97.36 | 0.43192
38930.5207 | 918 | 973 | 38930.5208 | 961 | 994 | 1399 | 1532 | 56.044 | 59.4017 | 58.6691 | 60.6838 | 0.56044 | 0.59402 | 0.58669 | 0.60684 | 0.033578 | 0.020147 | 1310.3918 | 2688.1699 | 21.9997
38930.5214 | 1178 | 1142 | 38930.5214 | 1020 | 930 | 1458 | 1591 | 71.917 | 69.7192 | 62.2711 | 56.7766 | 0.71917 | 0.69719 | 0.62271 | 0.56777 | 0.021978 | 0.054945 | 63.162 | 79.0665 | 8.0028
38930.5221 | 1182 | 1149 | 38930.5221 | 1127 | 1176 | 1516.5 | 1649.5 | 72.1612 | 70.1465 | 68.8034 | 71.7949 | 0.72161 | 0.70147 | 0.68803 | 0.71795 | 0.020147 | 0.029915 | 1823.1355 | 6359.6731 | 18.6776
| 1084 | 1014 | 38930.5228 | 1123 | 1065 | 1576 | 1709 | 66.1783 | 61.9048 | 68.5592 | 65.0183 | 0.66178 | 0.61905 | 0.68559 | 0.65018 | 0.042735 | 0.035409 | 583.0612 | 952.2399 | 1.3405
38930.5235 | 985 | 879 | 38930.5235 | 1109 | 1042 | 1634.5 | 1767.5 | 60.1343 | 53.663 | 67.7045 | 63.6142 | 0.60134 | 0.53663 | 0.67705 | 0.63614 | 0.064713 | 0.040904 | 455.7594 | 621.1864 | 24.4017
38930.5241 | 979 | 877 | 38930.5242 | 940 | 1033 | 1693 | 1826 | 59.768 | 53.5409 | 57.3871 | 63.0647 | 0.59768 | 0.53541 | 0.57387 | 0.63065 | 0.062271 | 0.056777 | 1113.9935 | 433565.4408 | 29.3
38930.5248 | 938 | 825 | 38930.5248 | 1138 | 1181 | 1752 | 1885 | 57.265 | 50.3663 | 69.475 | 72.1001 | 0.57265 | 0.50366 | 0.69475 | 0.721 | 0.068987 | 0.026252 | 229.3679 | 206.6187 | 28.5897
38930.5255 | 1132 | 1075 | 38930.5255 | 1081 | 1008 | 1810.5 | 1943.5 | 69.1087 | 65.6288 | 65.9951 | 61.5385 | 0.69109 | 0.65629 | 0.65995 | 0.61538 | 0.034799 | 0.044567 | 362.1794 | 502.6517 | 7.2917
38930.5262 | 1011 | 907 | 38930.5262 | 1016 | 1011 | 1869.5 | 2002.5 | 61.7216 | 55.3724 | 62.0269 | 61.7216 | 0.61722 | 0.55372 | 0.62027 | 0.61722 | 0.063492 | 0.0030525 | 266.497 | 293.0338 | 16.031
38930.5269 | 1081 | 1009 | 38930.5269 | 1135 | 1079 | 1928.5 | 2061.5 | 65.9951 | 61.5995 | 69.2918 | 65.873 | 0.65995 | 0.616 | 0.69292 | 0.65873 | 0.043956 | 0.034188 | 570.4901 | 926.5331 | 2.0592
38930.5275 | 922 | 899 | 38930.5276 | 1189 | 1047 | 1987 | 2120 | 56.2882 | 54.884 | 72.5885 | 63.9194 | 0.56288 | 0.54884 | 0.72589 | 0.63919 | 0.014042 | 0.086691 | 149.6852 | 116.3478 | 17.4686
38930.5282 | 945 | 911 | 38930.5282 | 959 | 929 | 2046 | 2179 | 57.6923 | 55.6166 | 58.547 | 56.7155 | 0.57692 | 0.55617 | 0.58547 | 0.56716 | 0.020757 | 0.018315 | 4212.7565 | 14519.7545 | 28.02
38930.5289 | 1121 | 1062 | 38930.5289 | 1106 | 1044 | 2104.5 | 2237.5 | 68.4371 | 64.8352 | 67.5214 | 63.7363 | 0.68437 | 0.64835 | 0.67521 | 0.63736 | 0.03602 | 0.037851 | 1706.7977 | 120916.725 | 6.584
38930.5296 | 1106 | 1148 | 38930.5296 | 994 | 906 | 2163.5 | 2296.5 | 67.5214 | 70.0855 | 60.6838 | 55.3114 | 0.67521 | 0.70085 | 0.60684 | 0.55311 | 0.025641 | 0.053724 | 160.6428 | 196.2832 | 8.1356
38930.5303 | 929 | 863 | 38930.5303 | 1112 | 1060 | 2222.5 | 2355.5 | 56.7155 | 52.6862 | 67.8877 | 64.7131 | 0.56716 | 0.52686 | 0.67888 | 0.64713 | 0.040293 | 0.031746 | 1276.2192 | 3223.0841 | 36.0788
38930.5309 | 1172 | 1191 | 38930.531 | 1079 | 858 | 2281 | 2414 | 71.5507 | 72.7106 | 65.873 | 52.381 | 0.71551 | 0.72711 | 0.65873 | 0.52381 | 0.0116 | 0.13492 | 20.054 | 25.4845 | 4.2627

## C1-2
Penlight Test 28 |  |  | 2006-08-01 | 12:06 |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Air Drop
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38930.503 | 1 | 0 | 38930.503 | 1 | 0 | -132 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5037 | 1 | 0 | 38930.5037 | 1 | 0 | -73.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5044 | 1 | 0 | 38930.5044 | 1 | 0 | -14.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5051 | 1 | 0 | 38930.5051 | 1 | 0 | 44.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5057 | 1 | 0 | 38930.5058 | 1 | 0 | 103 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5064 | 1 | 0 | 38930.5064 | 1 | 0 | 161.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5071 | 1 | 0 | 38930.5071 | 1 | 0 | 220.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5078 | 1 | 0 | 38930.5078 | 1 | 0 | 279.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5084 | 1 | 0 | 38930.5085 | 1 | 0 | 338 | 471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5091 | 1 | 0 | 38930.5092 | 1 | 0 | 397 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5098 | 1 | 0 | 38930.5098 | 1 | 0 | 455.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5105 | 1 | 0 | 38930.5105 | 1 | 0 | 514.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5112 | 1 | 0 | 38930.5112 | 1 | 0 | 573.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5119 | 1 | 0 | 38930.5119 | 1 | 0 | 632 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5125 | 1 | 0 | 38930.5126 | 1 | 0 | 691 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5132 | 1 | 0 | 38930.5132 | 1 | 0 | 749.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5139 | 1 | 0 | 38930.5139 | 1 | 0 | 808.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5146 | 1 | 0 | 38930.5146 | 1 | 0 | 867.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5153 | 1 | 0 | 38930.5153 | 1 | 0 | 926 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5159 | 1 | 0 | 38930.516 | 1 | 0 | 985 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5166 | 1 | 0 | 38930.5166 | 1 | 0 | 1043.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5173 | 1 | 0 | 38930.5173 | 1 | 0 | 1102.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.518 | 1 | 0 | 38930.518 | 1 | 0 | 1161.5 | 1294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5187 | 1 | 0 | 38930.5187 | 1 | 0 | 1220 | 1353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5193 | 1 | 0 | 38930.5194 | 1 | 0 | 1279 | 1412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.52 | 472 | 547 | 38930.52 | 621 | 601 | 1337.5 | 1470.5 | 28.8156 | 33.3944 | 37.9121 | 36.6911 | 0.28816 | 0.33394 | 0.37912 | 0.36691 | 0.045788 | 0.01221 | 2099.501 | 17297.0775 | 198.854
38930.5207 | 1164 | 1142 | 38930.5207 | 1089 | 1161 | 1396.5 | 1529.5 | 71.0623 | 69.7192 | 66.4835 | 70.8791 | 0.71062 | 0.69719 | 0.66484 | 0.70879 | 0.013431 | 0.043956 | 593.0869 | 827.4544 | 15.0764
38930.5214 | 927 | 892 | 38930.5214 | 976 | 882 | 1455 | 1588 | 56.5934 | 54.4567 | 59.5849 | 53.8462 | 0.56593 | 0.54457 | 0.59585 | 0.53846 | 0.021368 | 0.057387 | 1275.267 | 1537.886 | 30.9494
38930.5221 | 1113 | 1170 | 38930.5221 | 974 | 875 | 1514 | 1647 | 67.9487 | 71.4286 | 59.4628 | 53.4188 | 0.67949 | 0.71429 | 0.59463 | 0.53419 | 0.034799 | 0.06044 | 226.4823 | 304.2562 | 10.9344
38930.5227 | 1089 | 837 | 38930.5228 | 920 | 935 | 1572.5 | 1705.5 | 66.4835 | 51.0989 | 56.1661 | 57.0818 | 0.66484 | 0.51099 | 0.56166 | 0.57082 | 0.15385 | 0.0091575 | 152.4133 | 199.3471 | 14.8798
38930.5234 | 1196 | 1176 | 38930.5234 | 1135 | 1075 | 1631.5 | 1764.5 | 73.0159 | 71.7949 | 69.2918 | 65.6288 | 0.73016 | 0.71795 | 0.69292 | 0.65629 | 0.01221 | 0.03663 | 720.2725 | 1095.8322 | 20.1805
38930.5241 | 974 | 950 | 38930.5241 | 1111 | 1045 | 1690.5 | 1823.5 | 59.4628 | 57.9976 | 67.8266 | 63.7973 | 0.59463 | 0.57998 | 0.67827 | 0.63797 | 0.014652 | 0.040293 | 384.3855 | 348.8513 | 15.464
38930.5248 | 1062 | 984 | 38930.5248 | 1028 | 942 | 1749 | 1882 | 64.8352 | 60.0733 | 62.7595 | 57.5092 | 0.64835 | 0.60073 | 0.62759 | 0.57509 | 0.047619 | 0.052503 | 2823409 | 1262.1408 | 6.311
38930.5255 | 1150 | 1189 | 38930.5255 | 1143 | 1093 | 1808 | 1941 | 70.2076 | 72.5885 | 69.7802 | 66.7277 | 0.70208 | 0.72589 | 0.6978 | 0.66728 | 0.02381 | 0.030525 | 1690.2938 | 6615.2849 | 18.7229
38930.5261 | 1002 | 893 | 38930.5262 | 922 | 865 | 1866.5 | 1999.5 | 61.1722 | 54.5177 | 56.2882 | 52.8083 | 0.61172 | 0.54518 | 0.56288 | 0.52808 | 0.066545 | 0.034799 | 697.9229 | 1779.2568 | 23.1152
38930.5268 | 929 | 853 | 38930.5268 | 1019 | 926 | 1925.5 | 2058.5 | 56.7155 | 52.0757 | 62.21 | 56.5324 | 0.56716 | 0.52076 | 0.6221 | 0.56532 | 0.046398 | 0.056777 | 13244.0957 | 1271.9949 | 35.9781
38930.5275 | 960 | 854 | 38930.5275 | 995 | 893 | 1984.5 | 2117.5 | 58.6081 | 52.1368 | 60.7448 | 54.5177 | 0.58608 | 0.52137 | 0.60745 | 0.54518 | 0.064713 | 0.062271 | 1676.5665 | 2294.0153 | 33.5515
38930.5282 | 978 | 874 | 38930.5282 | 1013 | 910 | 2043 | 2176 | 59.707 | 53.3578 | 61.8437 | 55.5556 | 0.59707 | 0.53358 | 0.61844 | 0.55556 | 0.063492 | 0.062882 | 1858.9139 | 2035.3145 | 28.4664
38930.5289 | 980 | 880 | 38930.5289 | 1011 | 915 | 2102 | 2235 | 59.8291 | 53.7241 | 61.7216 | 55.8608 | 0.59829 | 0.53724 | 0.61722 | 0.55861 | 0.06105 | 0.058608 | 1723.8578 | 2567.5319 | 27.6744
38930.5295 | 1156 | 1111 | 38930.5296 | 1062 | 992 | 2160.5 | 2293.5 | 70.5739 | 67.8266 | 64.8352 | 60.5617 | 0.70574 | 0.67827 | 0.64835 | 0.60562 | 0.027473 | 0.042735 | 315.8907 | 430.6882 | 11.248
38930.5302 | 983 | 902 | 38930.5302 | 1012 | 940 | 2219.5 | 2352.5 | 60.0122 | 55.0672 | 61.7827 | 57.3871 | 0.60012 | 0.55067 | 0.61783 | 0.57387 | 0.049451 | 0.043956 | 1634.9719 | 7589.7572 | 24.9506
38930.5309 | 977 | 892 | 38930.5309 | 1066 | 997 | 2278.5 | 2411.5 | 59.6459 | 54.4567 | 65.0794 | 60.8669 | 0.59646 | 0.54457 | 0.65079 | 0.60867 | 0.051893 | 0.042125 | 1093.3547 | 4719.0188 | 26.7888

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 28 |  |  | 2006-08-01 | 12:06
38930.503 | 1 | 0 | 1 | XLPE | 7-C | Air Drop
38930.5037 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38930.5044 | 1 | 0 | 1
38930.5051 | 1 | 0 | 1
38930.5057 | 1 | 0 | 1
38930.5064 | 1 | 0 | 1
38930.5071 | 1 | 0 | 1
38930.5078 | 1 | 0 | 1
38930.5084 | 1 | 0 | 1
38930.5091 | 1 | 0 | 1
38930.5098 | 1 | 0 | 1
38930.5105 | 1 | 0 | 1
38930.5112 | 1 | 0 | 1
38930.5119 | 1 | 0 | 1
38930.5125 | 1 | 0 | 1
38930.5132 | 1 | 0 | 1
38930.5139 | 1 | 0 | 1
38930.5146 | 1 | 0 | 1
38930.5153 | 1 | 0 | 1
38930.5159 | 1 | 0 | 1
38930.5166 | 1 | 0 | 1
38930.5173 | 1 | 0 | 1
38930.518 | 1 | 0 | 1
38930.5187 | 1 | 0 | 1
38930.5193 | 1 | 0 | 1
38930.52 | 472 | 547 | 1
38930.5207 | 1164 | 1142 | 1
38930.5214 | 927 | 892 | 1
38930.5221 | 1113 | 1170 | 1
38930.5227 | 1089 | 837 | 1
38930.5234 | 1196 | 1176 | 1
38930.5241 | 974 | 950 | 1
38930.5248 | 1062 | 984 | 1
38930.5255 | 1150 | 1189 | 1
38930.5261 | 1002 | 893 | 1
38930.5268 | 929 | 853 | 1
38930.5275 | 960 | 854 | 1
38930.5282 | 978 | 874 | 1
38930.5289 | 980 | 880 | 1
38930.5295 | 1156 | 1111 | 1
38930.5302 | 983 | 902 | 1
38930.5309 | 977 | 892 | 1
1
38930.503 | 1 | 0 | 2
38930.5037 | 1 | 0 | 2
38930.5044 | 1 | 0 | 2
38930.5051 | 1 | 0 | 2
38930.5058 | 1 | 0 | 2
38930.5064 | 1 | 0 | 2
38930.5071 | 1 | 0 | 2
38930.5078 | 1 | 0 | 2
38930.5085 | 1 | 0 | 2
38930.5092 | 1 | 0 | 2
38930.5098 | 1 | 0 | 2
38930.5105 | 1 | 0 | 2
38930.5112 | 1 | 0 | 2
38930.5119 | 1 | 0 | 2
38930.5126 | 1 | 0 | 2
38930.5132 | 1 | 0 | 2
38930.5139 | 1 | 0 | 2
38930.5146 | 1 | 0 | 2
38930.5153 | 1 | 0 | 2
38930.516 | 1 | 0 | 2
38930.5166 | 1 | 0 | 2
38930.5173 | 1 | 0 | 2
38930.518 | 1 | 0 | 2
38930.5187 | 1 | 0 | 2
38930.5194 | 1 | 0 | 2
38930.52 | 621 | 601 | 2
38930.5207 | 1089 | 1161 | 2
38930.5214 | 976 | 882 | 2
38930.5221 | 974 | 875 | 2
38930.5228 | 920 | 935 | 2
38930.5234 | 1135 | 1075 | 2
38930.5241 | 1111 | 1045 | 2
38930.5248 | 1028 | 942 | 2
38930.5255 | 1143 | 1093 | 2
38930.5262 | 922 | 865 | 2
38930.5268 | 1019 | 926 | 2
38930.5275 | 995 | 893 | 2
38930.5282 | 1013 | 910 | 2
38930.5289 | 1011 | 915 | 2
38930.5296 | 1062 | 992 | 2
38930.5302 | 1012 | 940 | 2
38930.5309 | 1066 | 997 | 2
2
38930.503 | 1 | 0 | 3
38930.5037 | 1 | 0 | 3
38930.5044 | 1 | 0 | 3
38930.5051 | 1 | 0 | 3
38930.5058 | 1 | 0 | 3
38930.5064 | 1 | 0 | 3
38930.5071 | 1 | 0 | 3
38930.5078 | 1 | 0 | 3
38930.5085 | 1 | 0 | 3
38930.5092 | 1 | 0 | 3
38930.5098 | 1 | 0 | 3
38930.5105 | 1 | 0 | 3
38930.5112 | 1 | 0 | 3
38930.5119 | 1 | 0 | 3
38930.5126 | 1 | 0 | 3
38930.5133 | 1 | 0 | 3
38930.5139 | 1 | 0 | 3
38930.5146 | 1 | 0 | 3
38930.5153 | 1 | 0 | 3
38930.516 | 1 | 0 | 3
38930.5167 | 1 | 0 | 3
38930.5173 | 1 | 0 | 3
38930.518 | 1 | 0 | 3
38930.5187 | 1 | 0 | 3
38930.5194 | 1 | 0 | 3
38930.5201 | 1189 | 916 | 3
38930.5207 | 918 | 973 | 3
38930.5214 | 1178 | 1142 | 3
38930.5221 | 1182 | 1149 | 3
38930.5235 | 985 | 879 | 3
38930.5241 | 979 | 877 | 3
38930.5248 | 938 | 825 | 3
38930.5255 | 1132 | 1075 | 3
38930.5262 | 1011 | 907 | 3
38930.5269 | 1081 | 1009 | 3
38930.5275 | 922 | 899 | 3
38930.5282 | 945 | 911 | 3
38930.5289 | 1121 | 1062 | 3
38930.5296 | 1106 | 1148 | 3
38930.5303 | 929 | 863 | 3
38930.5309 | 1172 | 1191 | 3
3
38930.5031 | 1 | 0 | 4
38930.5037 | 1 | 0 | 4
38930.5044 | 1 | 0 | 4
38930.5051 | 1 | 0 | 4
38930.5058 | 1 | 0 | 4
38930.5065 | 1 | 0 | 4
38930.5071 | 1 | 0 | 4
38930.5078 | 1 | 0 | 4
38930.5085 | 1 | 0 | 4
38930.5092 | 1 | 0 | 4
38930.5099 | 1 | 0 | 4
38930.5105 | 1 | 0 | 4
38930.5112 | 1 | 0 | 4
38930.5119 | 1 | 0 | 4
38930.5126 | 1 | 0 | 4
38930.5133 | 1 | 0 | 4
38930.5139 | 1 | 0 | 4
38930.5146 | 1 | 0 | 4
38930.5153 | 1 | 0 | 4
38930.516 | 1 | 0 | 4
38930.5167 | 1 | 0 | 4
38930.5173 | 1 | 0 | 4
38930.518 | 1 | 0 | 4
38930.5187 | 1 | 0 | 4
38930.5194 | 1 | 0 | 4
38930.5201 | 1170 | 1150 | 4
38930.5208 | 961 | 994 | 4
38930.5214 | 1020 | 930 | 4
38930.5221 | 1127 | 1176 | 4
38930.5228 | 1123 | 1065 | 4
38930.5235 | 1109 | 1042 | 4
38930.5242 | 940 | 1033 | 4
38930.5248 | 1138 | 1181 | 4
38930.5255 | 1081 | 1008 | 4
38930.5262 | 1016 | 1011 | 4
38930.5269 | 1135 | 1079 | 4
38930.5276 | 1189 | 1047 | 4
38930.5282 | 959 | 929 | 4
38930.5289 | 1106 | 1044 | 4
38930.5296 | 994 | 906 | 4
38930.5303 | 1112 | 1060 | 4
38930.531 | 1079 | 858 | 4
4
38930.5031 | 1 | 0 | 5
38930.5038 | 1 | 0 | 5
38930.5044 | 1 | 0 | 5
38930.5051 | 1 | 0 | 5
38930.5058 | 1 | 0 | 5
38930.5065 | 1 | 0 | 5
38930.5072 | 1 | 0 | 5
38930.5078 | 1 | 0 | 5
38930.5085 | 1 | 0 | 5
38930.5092 | 1 | 0 | 5
38930.5099 | 1 | 0 | 5
38930.5106 | 1 | 0 | 5
38930.5112 | 1 | 0 | 5
38930.5119 | 1 | 0 | 5
38930.5126 | 1 | 0 | 5
38930.5133 | 1 | 0 | 5
38930.514 | 1 | 0 | 5
38930.5146 | 1 | 0 | 5
38930.5153 | 1 | 0 | 5
38930.516 | 1 | 0 | 5
38930.5167 | 1 | 1 | 5
38930.5174 | 1 | 0 | 5
38930.518 | 1 | 0 | 5
38930.5187 | 1 | 0 | 5
38930.5194 | 1 | 0 | 5
38930.5201 | 163 | 169 | 5
38930.5208 | 67 | 72 | 5
38930.5214 | 25 | 34 | 5
38930.5221 | 5 | 20 | 5
38930.5228 | 6 | 21 | 5
38930.5235 | 6 | 20 | 5
38930.5242 | 665 | 595 | 5
38930.5248 | 968 | 880 | 5
38930.5255 | 1137 | 1121 | 5
38930.5262 | 1043 | 1077 | 5
38930.5269 | 1054 | 996 | 5
38930.5276 | 935 | 837 | 5
38930.5283 | 905 | 800 | 5
38930.5289 | 977 | 894 | 5
38930.5296 | 1073 | 1026 | 5
38930.5303 | 989 | 930 | 5
38930.531 | 977 | 905 | 5
5
38930.5031 | 1 | 0 | 6
38930.5038 | 1 | 0 | 6
38930.5045 | 1 | 0 | 6
38930.5051 | 1 | 0 | 6
38930.5058 | 1 | 0 | 6
38930.5065 | 1 | 0 | 6
38930.5072 | 1 | 0 | 6
38930.5079 | 1 | 0 | 6
38930.5085 | 1 | 0 | 6
38930.5092 | 1 | 0 | 6
38930.5099 | 1 | 0 | 6
38930.5106 | 1 | 0 | 6
38930.5113 | 1 | 0 | 6
38930.5119 | 1 | 0 | 6
38930.5126 | 1 | 0 | 6
38930.5133 | 1 | 0 | 6
38930.514 | 1 | 0 | 6
38930.5147 | 1 | 0 | 6
38930.5153 | 1 | 0 | 6
38930.516 | 1 | 0 | 6
38930.5167 | 1 | 0 | 6
38930.5174 | 1 | 0 | 6
38930.5181 | 1 | 0 | 6
38930.5187 | 1 | 0 | 6
38930.5194 | 1 | 0 | 6
38930.5201 | 234 | 227 | 6
38930.5208 | 97 | 100 | 6
38930.5215 | 6 | 14 | 6
38930.5221 | 6 | 15 | 6
38930.5228 | 5 | 14 | 6
38930.5235 | 6 | 13 | 6
38930.5242 | 749 | 722 | 6
38930.5249 | 1005 | 1025 | 6
38930.5255 | 1003 | 924 | 6
38930.5262 | 960 | 947 | 6
38930.5269 | 925 | 908 | 6
38930.5276 | 985 | 992 | 6
38930.5283 | 984 | 898 | 6
38930.5289 | 999 | 1013 | 6
38930.5296 | 912 | 830 | 6
38930.5303 | 1088 | 1052 | 6
38930.531 | 1080 | 1034 | 6
6
38930.5031 | 1 | 0 | 7
38930.5038 | 1 | 0 | 7
38930.5045 | 1 | 0 | 7
38930.5052 | 1 | 0 | 7
38930.5058 | 1 | 0 | 7
38930.5065 | 1 | 0 | 7
38930.5072 | 1 | 0 | 7
38930.5079 | 1 | 0 | 7
38930.5086 | 1 | 0 | 7
38930.5092 | 1 | 0 | 7
38930.5099 | 1 | 0 | 7
38930.5106 | 1 | 0 | 7
38930.5113 | 1 | 0 | 7
38930.512 | 1 | 0 | 7
38930.5126 | 1 | 0 | 7
38930.5133 | 1 | 0 | 7
38930.514 | 1 | 0 | 7
38930.5147 | 1 | 0 | 7
38930.5154 | 1 | 0 | 7
38930.516 | 1 | 0 | 7
38930.5167 | 1 | 0 | 7
38930.5174 | 1 | 0 | 7
38930.5181 | 1 | 0 | 7
38930.5188 | 1 | 0 | 7
38930.5194 | 1 | 0 | 7
38930.5201 | 1049 | 1098 | 7
38930.5208 | 1188 | 1172 | 7
38930.5215 | 951 | 839 | 7
38930.5222 | 1136 | 1178 | 7
38930.5228 | 1168 | 829 | 7
38930.5235 | 938 | 820 | 7
38930.5242 | 1105 | 1144 | 7
38930.5249 | 1086 | 1016 | 7
38930.5256 | 970 | 861 | 7
38930.5262 | 947 | 826 | 7
38930.5269 | 1126 | 1071 | 7
38930.5276 | 1192 | 1164 | 7
38930.5283 | 1086 | 1159 | 7
38930.529 | 1194 | 1175 | 7
38930.5296 | 1078 | 1017 | 7
38930.5303 | 1157 | 1124 | 7
38930.531 | 1101 | 1041 | 7
7
38930.5031 | 1 | 0 | 8
38930.5038 | 1 | 0 | 8
38930.5045 | 1 | 0 | 8
38930.5052 | 1 | 0 | 8
38930.5058 | 1 | 0 | 8
38930.5065 | 1 | 0 | 8
38930.5072 | 1 | 0 | 8
38930.5079 | 1 | 0 | 8
38930.5086 | 1 | 0 | 8
38930.5092 | 1 | 0 | 8
38930.5099 | 1 | 0 | 8
38930.5106 | 1 | 0 | 8
38930.5113 | 1 | 0 | 8
38930.512 | 1 | 0 | 8
38930.5127 | 1 | 0 | 8
38930.5133 | 1 | 0 | 8
38930.514 | 1 | 0 | 8
38930.5147 | 1 | 0 | 8
38930.5154 | 1 | 0 | 8
38930.5161 | 1 | 0 | 8
38930.5167 | 1 | 0 | 8
38930.5174 | 1 | 0 | 8
38930.5181 | 1 | 0 | 8
38930.5188 | 1 | 0 | 8
38930.5195 | 1 | 0 | 8
38930.5201 | 1026 | 993 | 8
38930.5208 | 1180 | 1127 | 8
38930.5215 | 1030 | 942 | 8
38930.5222 | 957 | 841 | 8
38930.5229 | 1112 | 1049 | 8
38930.5235 | 1132 | 1181 | 8
38930.5242 | 1165 | 1188 | 8
38930.5249 | 1001 | 901 | 8
38930.5256 | 984 | 878 | 8
38930.5263 | 998 | 890 | 8
38930.5269 | 1140 | 1184 | 8
38930.5276 | 1016 | 927 | 8
38930.5283 | 988 | 885 | 8
38930.529 | 1126 | 1068 | 8
38930.5297 | 949 | 1048 | 8
38930.5303 | 1060 | 1093 | 8
38930.531 | 1073 | 1106 | 8
8
38930.5031 | 1 | 0 | 9
38930.5038 | 1 | 0 | 9
38930.5045 | 1 | 0 | 9
38930.5052 | 1 | 0 | 9
38930.5059 | 1 | 0 | 9
38930.5065 | 1 | 0 | 9
38930.5072 | 1 | 0 | 9
38930.5079 | 1 | 0 | 9
38930.5086 | 1 | 0 | 9
38930.5093 | 1 | 0 | 9
38930.5099 | 1 | 0 | 9
38930.5106 | 1 | 0 | 9
38930.5113 | 1 | 0 | 9
38930.512 | 1 | 0 | 9
38930.5127 | 1 | 0 | 9
38930.5133 | 1 | 0 | 9
38930.514 | 1 | 0 | 9
38930.5147 | 1 | 0 | 9
38930.5154 | 1 | 0 | 9
38930.5161 | 1 | 0 | 9
38930.5167 | 1 | 0 | 9
38930.5174 | 1 | 0 | 9
38930.5181 | 1 | 0 | 9
38930.5188 | 1 | 0 | 9
38930.5195 | 1 | 0 | 9
38930.5202 | 955 | 908 | 9
38930.5208 | 1168 | 1146 | 9
38930.5215 | 1007 | 907 | 9
38930.5222 | 1064 | 980 | 9
38930.5229 | 1059 | 978 | 9
38930.5236 | 981 | 871 | 9
38930.5242 | 1101 | 1032 | 9
38930.5249 | 941 | 866 | 9
38930.5256 | 974 | 957 | 9
38930.5263 | 1083 | 1004 | 9
38930.527 | 1096 | 1033 | 9
38930.5283 | 972 | 946 | 9
38930.529 | 1006 | 1106 | 9
38930.5297 | 1010 | 930 | 9
38930.5304 | 1109 | 1057 | 9
38930.531 | 1149 | 1188 | 9
9
38930.5032 | 1 | 0 | 10
38930.5038 | 1 | 0 | 10
38930.5045 | 1 | 0 | 10
38930.5052 | 1 | 0 | 10
38930.5059 | 1 | 0 | 10
38930.5066 | 1 | 0 | 10
38930.5072 | 1 | 0 | 10
38930.5079 | 1 | 0 | 10
38930.5086 | 1 | 0 | 10
38930.5093 | 1 | 0 | 10
38930.51 | 1 | 0 | 10
38930.5106 | 1 | 0 | 10
38930.5113 | 1 | 0 | 10
38930.512 | 1 | 0 | 10
38930.5127 | 1 | 0 | 10
38930.5134 | 1 | 0 | 10
38930.514 | 1 | 0 | 10
38930.5147 | 1 | 0 | 10
38930.5154 | 1 | 0 | 10
38930.5161 | 1 | 0 | 10
38930.5168 | 1 | 0 | 10
38930.5174 | 1 | 0 | 10
38930.5181 | 1 | 0 | 10
38930.5188 | 1 | 0 | 10
38930.5195 | 1 | 0 | 10
38930.5202 | 985 | 1025 | 10
38930.5208 | 950 | 1065 | 10
38930.5215 | 1046 | 958 | 10
38930.5222 | 1081 | 1004 | 10
38930.5229 | 982 | 883 | 10
38930.5236 | 971 | 862 | 10
38930.5242 | 1124 | 1177 | 10
38930.5249 | 1125 | 1168 | 10
38930.5256 | 942 | 830 | 10
38930.5263 | 1009 | 1000 | 10
38930.527 | 1063 | 986 | 10
38930.5277 | 973 | 954 | 10
38930.5283 | 952 | 919 | 10
38930.529 | 953 | 926 | 10
38930.5297 | 1082 | 1018 | 10
38930.5304 | 998 | 912 | 10
38930.5311 | 1187 | 1153 | 10
10
38930.5032 | 1 | 0 | 11
38930.5039 | 1 | 0 | 11
38930.5045 | 1 | 0 | 11
38930.5052 | 1 | 0 | 11
38930.5059 | 1 | 0 | 11
38930.5066 | 1 | 0 | 11
38930.5073 | 1 | 0 | 11
38930.5079 | 1 | 0 | 11
38930.5086 | 1 | 0 | 11
38930.5093 | 1 | 0 | 11
38930.51 | 1 | 0 | 11
38930.5107 | 1 | 0 | 11
38930.5113 | 1 | 0 | 11
38930.512 | 1 | 0 | 11
38930.5127 | 1 | 0 | 11
38930.5134 | 1 | 0 | 11
38930.5141 | 1 | 0 | 11
38930.5147 | 1 | 0 | 11
38930.5154 | 1 | 0 | 11
38930.5161 | 1 | 0 | 11
38930.5168 | 1 | 0 | 11
38930.5175 | 1 | 0 | 11
38930.5181 | 1 | 0 | 11
38930.5188 | 1 | 0 | 11
38930.5195 | 1 | 0 | 11
38930.5202 | 46 | 51 | 11
38930.5209 | 1028 | 997 | 11
38930.5216 | 1159 | 1185 | 11
38930.5222 | 1005 | 902 | 11
38930.5229 | 1010 | 924 | 11
38930.5236 | 1070 | 992 | 11
38930.5243 | 969 | 859 | 11
38930.5249 | 1057 | 979 | 11
38930.5256 | 1036 | 950 | 11
38930.5263 | 1101 | 1029 | 11
38930.527 | 1096 | 1165 | 11
38930.5277 | 1036 | 949 | 11
38930.5283 | 942 | 827 | 11
38930.529 | 991 | 888 | 11
38930.5297 | 1026 | 951 | 11
38930.5304 | 1021 | 945 | 11
38930.5311 | 1157 | 1114 | 11
11
38930.5032 | 1 | 0 | 12
38930.5039 | 1 | 0 | 12
38930.5045 | 1 | 0 | 12
38930.5052 | 1 | 0 | 12
38930.5059 | 1 | 0 | 12
38930.5066 | 1 | 0 | 12
38930.5073 | 1 | 0 | 12
38930.508 | 1 | 0 | 12
38930.5086 | 1 | 0 | 12
38930.5093 | 1 | 0 | 12
38930.51 | 1 | 0 | 12
38930.5107 | 1 | 0 | 12
38930.5114 | 1 | 0 | 12
38930.512 | 1 | 0 | 12
38930.5127 | 1 | 0 | 12
38930.5134 | 1 | 0 | 12
38930.5141 | 1 | 0 | 12
38930.5148 | 1 | 0 | 12
38930.5154 | 1 | 0 | 12
38930.5161 | 1 | 0 | 12
38930.5168 | 1 | 0 | 12
38930.5175 | 1 | 0 | 12
38930.5182 | 1 | 0 | 12
38930.5188 | 1 | 0 | 12
38930.5195 | 1 | 0 | 12
38930.5202 | 7 | 13 | 12
38930.5209 | 1024 | 994 | 12
38930.5216 | 1066 | 987 | 12
38930.5222 | 929 | 1012 | 12
38930.5229 | 1149 | 1103 | 12
38930.5236 | 1011 | 910 | 12
38930.5243 | 1190 | 1156 | 12
38930.525 | 1019 | 926 | 12
38930.5256 | 1161 | 1187 | 12
38930.5263 | 1062 | 982 | 12
38930.527 | 1189 | 1184 | 12
38930.5277 | 1125 | 1067 | 12
38930.5284 | 935 | 827 | 12
38930.5291 | 939 | 828 | 12
38930.5297 | 1087 | 1162 | 12
38930.5304 | 1191 | 1167 | 12
38930.5311 | 956 | 1059 | 12
12
38930.5032 | 1 | 0 | 13
38930.5039 | 1 | 0 | 13
38930.5046 | 1 | 0 | 13
38930.5052 | 1 | 0 | 13
38930.5059 | 1 | 0 | 13
38930.5066 | 1 | 0 | 13
38930.5073 | 1 | 0 | 13
38930.508 | 1 | 0 | 13
38930.5086 | 1 | 0 | 13
38930.5093 | 1 | 0 | 13
38930.51 | 1 | 0 | 13
38930.5107 | 1 | 0 | 13
38930.5114 | 1 | 0 | 13
38930.512 | 1 | 0 | 13
38930.5127 | 1 | 0 | 13
38930.5134 | 1 | 0 | 13
38930.5141 | 1 | 0 | 13
38930.5148 | 1 | 0 | 13
38930.5155 | 1 | 0 | 13
38930.5161 | 1 | 0 | 13
38930.5168 | 1 | 0 | 13
38930.5175 | 1 | 0 | 13
38930.5182 | 1 | 0 | 13
38930.5189 | 1 | 0 | 13
38930.5195 | 9 | 7 | 13
38930.5202 | 1134 | 1109 | 13
38930.5209 | 952 | 982 | 13
38930.5216 | 1138 | 1081 | 13
38930.5223 | 1066 | 986 | 13
38930.5229 | 1024 | 1029 | 13
38930.5236 | 1027 | 1027 | 13
38930.5243 | 1120 | 1175 | 13
38930.525 | 1155 | 1188 | 13
38930.5257 | 1035 | 955 | 13
38930.5263 | 1037 | 1041 | 13
38930.527 | 1148 | 1100 | 13
38930.5277 | 1067 | 1148 | 13
38930.5284 | 1192 | 1168 | 13
38930.5291 | 1020 | 932 | 13
38930.5297 | 920 | 890 | 13
38930.5304 | 1109 | 1055 | 13
38930.5311 | 1171 | 1133 | 13
13
38930.5032 | 1 | 0 | 14
38930.5039 | 1 | 0 | 14
38930.5046 | 1 | 0 | 14
38930.5053 | 1 | 0 | 14
38930.5059 | 1 | 0 | 14
38930.5066 | 1 | 0 | 14
38930.5073 | 1 | 0 | 14
38930.508 | 1 | 0 | 14
38930.5087 | 1 | 0 | 14
38930.5094 | 1 | 0 | 14
38930.51 | 1 | 0 | 14
38930.5107 | 1 | 0 | 14
38930.5114 | 1 | 0 | 14
38930.5121 | 1 | 0 | 14
38930.5127 | 1 | 0 | 14
38930.5134 | 1 | 0 | 14
38930.5141 | 1 | 0 | 14
38930.5148 | 1 | 0 | 14
38930.5155 | 1 | 0 | 14
38930.5161 | 1 | 0 | 14
38930.5168 | 1 | 0 | 14
38930.5175 | 1 | 0 | 14
38930.5182 | 1 | 0 | 14
38930.5189 | 1 | 0 | 14
38930.5195 | 471 | 489 | 14
38930.5202 | 1020 | 988 | 14
38930.5209 | 1185 | 909 | 14
38930.5216 | 1060 | 980 | 14
38930.5223 | 1119 | 1163 | 14
38930.523 | 1123 | 1068 | 14
38930.5236 | 948 | 831 | 14
38930.5243 | 1194 | 1173 | 14
38930.525 | 1113 | 1051 | 14
38930.5257 | 951 | 847 | 14
38930.5264 | 1193 | 1167 | 14
38930.527 | 1057 | 976 | 14
38930.5277 | 957 | 934 | 14
38930.5284 | 986 | 883 | 14
38930.5291 | 918 | 875 | 14
38930.5298 | 1033 | 1056 | 14
38930.5304 | 1049 | 979 | 14
38930.5311 | 1011 | 922 | 14
14
38930.5032 | 1 | 0 | 15
38930.5039 | 1 | 0 | 15
38930.5046 | 1 | 0 | 15
38930.5053 | 1 | 0 | 15
38930.506 | 1 | 0 | 15
38930.5066 | 1 | 0 | 15
38930.5073 | 1 | 0 | 15
38930.508 | 1 | 0 | 15
38930.5087 | 1 | 0 | 15
38930.5094 | 1 | 0 | 15
38930.51 | 1 | 0 | 15
38930.5107 | 1 | 0 | 15
38930.5114 | 1 | 0 | 15
38930.5121 | 1 | 0 | 15
38930.5128 | 1 | 0 | 15
38930.5134 | 1 | 0 | 15
38930.5141 | 1 | 0 | 15
38930.5148 | 1 | 0 | 15
38930.5155 | 1 | 0 | 15
38930.5162 | 1 | 0 | 15
38930.5169 | 1 | 0 | 15
38930.5175 | 1 | 0 | 15
38930.5182 | 1 | 0 | 15
38930.5189 | 1 | 0 | 15
38930.5196 | 2 | 2 | 15
38930.5202 | 978 | 1077 | 15
38930.5209 | 46 | 55 | 15
38930.5216 | 15 | 30 | 15
38930.5223 | 6 | 21 | 15
38930.523 | 6 | 21 | 15
38930.5237 | 6 | 19 | 15
38930.5243 | 1110 | 1092 | 15
38930.525 | 962 | 876 | 15
38930.5257 | 1004 | 931 | 15
38930.5264 | 1091 | 1037 | 15
38930.527 | 896 | 865 | 15
38930.5277 | 1133 | 955 | 15
38930.5284 | 1025 | 1096 | 15
38930.5291 | 1008 | 1027 | 15
38930.5298 | 1100 | 1122 | 15
38930.5305 | 1051 | 1004 | 15
38930.5311 | 1116 | 1065 | 15
15
38930.5033 | 1 | 0 | 16
38930.5039 | 1 | 0 | 16
38930.5046 | 1 | 0 | 16
38930.5053 | 1 | 0 | 16
38930.506 | 1 | 0 | 16
38930.5067 | 1 | 0 | 16
38930.5073 | 1 | 0 | 16
38930.508 | 1 | 0 | 16
38930.5087 | 1 | 0 | 16
38930.5094 | 1 | 0 | 16
38930.5101 | 1 | 0 | 16
38930.5107 | 1 | 0 | 16
38930.5114 | 1 | 0 | 16
38930.5121 | 1 | 0 | 16
38930.5128 | 1 | 0 | 16
38930.5135 | 1 | 0 | 16
38930.5141 | 1 | 0 | 16
38930.5148 | 1 | 0 | 16
38930.5155 | 1 | 0 | 16
38930.5162 | 1 | 0 | 16
38930.5169 | 1 | 0 | 16
38930.5175 | 1 | 0 | 16
38930.5182 | 1 | 0 | 16
38930.5189 | 1 | 0 | 16
38930.5196 | 903 | 872 | 16
38930.5203 | 1154 | 1187 | 16
38930.5209 | 964 | 930 | 16
38930.5216 | 969 | 954 | 16
38930.5223 | 1180 | 1188 | 16
38930.523 | 1133 | 1077 | 16
38930.5237 | 944 | 826 | 16
38930.5244 | 964 | 858 | 16
38930.525 | 1037 | 953 | 16
38930.5257 | 1173 | 1163 | 16
38930.5264 | 1136 | 1076 | 16
38930.5271 | 1166 | 825 | 16
38930.5278 | 1152 | 1102 | 16
38930.5284 | 983 | 880 | 16
38930.5291 | 960 | 854 | 16
38930.5298 | 925 | 899 | 16
38930.5305 | 1166 | 1187 | 16
38930.5312 | 1168 | 1128 | 16
16
38930.5033 | 1 | 0 | 17
38930.5039 | 1 | 0 | 17
38930.5046 | 1 | 0 | 17
38930.5053 | 1 | 0 | 17
38930.506 | 1 | 0 | 17
38930.5067 | 1 | 0 | 17
38930.5073 | 1 | 0 | 17
38930.508 | 1 | 0 | 17
38930.5087 | 1 | 0 | 17
38930.5094 | 1 | 0 | 17
38930.5101 | 1 | 0 | 17
38930.5108 | 1 | 0 | 17
38930.5114 | 1 | 0 | 17
38930.5121 | 1 | 0 | 17
38930.5128 | 1 | 0 | 17
38930.5135 | 1 | 0 | 17
38930.5142 | 1 | 0 | 17
38930.5148 | 1 | 0 | 17
38930.5155 | 1 | 0 | 17
38930.5162 | 1 | 0 | 17
38930.5169 | 1 | 0 | 17
38930.5176 | 1 | 0 | 17
38930.5182 | 1 | 0 | 17
38930.5189 | 1 | 0 | 17
38930.5196 | 3 | 3 | 17
38930.5203 | 940 | 905 | 17
38930.521 | 1188 | 1188 | 17
38930.5216 | 941 | 835 | 17
38930.5223 | 1060 | 1076 | 17
38930.523 | 1125 | 1177 | 17
38930.5237 | 1086 | 1012 | 17
38930.5244 | 1188 | 1154 | 17
38930.525 | 960 | 855 | 17
38930.5257 | 1012 | 921 | 17
38930.5264 | 944 | 827 | 17
38930.5271 | 997 | 985 | 17
38930.5278 | 1116 | 1054 | 17
38930.5284 | 1000 | 894 | 17
38930.5291 | 1027 | 1121 | 17
38930.5298 | 1109 | 1172 | 17
38930.5305 | 954 | 940 | 17
38930.5312 | 949 | 1048 | 17
17
38930.5033 | 1 | 0 | 18
38930.504 | 1 | 0 | 18
38930.5047 | 1 | 0 | 18
38930.5053 | 1 | 0 | 18
38930.506 | 1 | 0 | 18
38930.5067 | 1 | 0 | 18
38930.5074 | 1 | 0 | 18
38930.5081 | 1 | 0 | 18
38930.5087 | 1 | 0 | 18
38930.5094 | 1 | 0 | 18
38930.5101 | 1 | 0 | 18
38930.5108 | 1 | 0 | 18
38930.5114 | 1 | 0 | 18
38930.5121 | 1 | 0 | 18
38930.5128 | 1 | 0 | 18
38930.5135 | 1 | 0 | 18
38930.5142 | 1 | 0 | 18
38930.5148 | 1 | 0 | 18
38930.5155 | 1 | 0 | 18
38930.5162 | 1 | 0 | 18
38930.5169 | 1 | 0 | 18
38930.5176 | 1 | 0 | 18
38930.5183 | 1 | 0 | 18
38930.5189 | 1 | 0 | 18
38930.5196 | 2 | 2 | 18
38930.5203 | 950 | 981 | 18
38930.521 | 992 | 958 | 18
38930.5217 | 1122 | 1065 | 18
38930.5223 | 1103 | 1141 | 18
38930.523 | 1040 | 961 | 18
38930.5237 | 1170 | 1128 | 18
38930.5244 | 1087 | 839 | 18
38930.5251 | 1196 | 970 | 18
38930.5257 | 1070 | 993 | 18
38930.5264 | 993 | 886 | 18
38930.5271 | 1016 | 1113 | 18
38930.5278 | 960 | 936 | 18
38930.5285 | 950 | 1052 | 18
38930.5291 | 1029 | 943 | 18
38930.5298 | 1133 | 1082 | 18
38930.5305 | 1191 | 1182 | 18
38930.5312 | 960 | 865 | 18
18
38930.5033 | 1 | 0 | 19
38930.504 | 1 | 0 | 19
38930.5047 | 1 | 0 | 19
38930.5053 | 1 | 0 | 19
38930.506 | 1 | 0 | 19
38930.5067 | 1 | 0 | 19
38930.5074 | 1 | 0 | 19
38930.5081 | 1 | 0 | 19
38930.5088 | 1 | 0 | 19
38930.5094 | 1 | 0 | 19
38930.5101 | 1 | 0 | 19
38930.5108 | 1 | 0 | 19
38930.5115 | 1 | 0 | 19
38930.5122 | 1 | 0 | 19
38930.5128 | 1 | 0 | 19
38930.5135 | 1 | 0 | 19
38930.5142 | 1 | 0 | 19
38930.5149 | 1 | 0 | 19
38930.5156 | 1 | 0 | 19
38930.5162 | 1 | 0 | 19
38930.5169 | 1 | 0 | 19
38930.5176 | 1 | 0 | 19
38930.5183 | 1 | 0 | 19
38930.519 | 1 | 0 | 19
38930.5196 | 2 | 1 | 19
38930.5203 | 1021 | 990 | 19
38930.521 | 928 | 1031 | 19
38930.5217 | 1099 | 1035 | 19
38930.5224 | 1140 | 1183 | 19
38930.523 | 1009 | 1103 | 19
38930.5237 | 1113 | 1047 | 19
38930.5244 | 957 | 844 | 19
38930.5251 | 1143 | 1185 | 19
38930.5258 | 943 | 837 | 19
38930.5264 | 1110 | 1043 | 19
38930.5271 | 1087 | 1159 | 19
38930.5278 | 1101 | 1038 | 19
38930.5285 | 1097 | 1164 | 19
38930.5292 | 1076 | 1004 | 19
38930.5298 | 1014 | 930 | 19
38930.5305 | 1160 | 1121 | 19
38930.5312 | 1078 | 1111 | 19
19
38930.5033 | 1 | 0 | 20
38930.504 | 1 | 0 | 20
38930.5047 | 1 | 0 | 20
38930.5054 | 1 | 0 | 20
38930.506 | 1 | 0 | 20
38930.5067 | 1 | 0 | 20
38930.5074 | 1 | 0 | 20
38930.5081 | 1 | 0 | 20
38930.5088 | 1 | 0 | 20
38930.5094 | 1 | 0 | 20
38930.5101 | 1 | 0 | 20
38930.5108 | 1 | 0 | 20
38930.5115 | 1 | 0 | 20
38930.5122 | 1 | 0 | 20
38930.5128 | 1 | 0 | 20
38930.5135 | 1 | 0 | 20
38930.5142 | 1 | 0 | 20
38930.5149 | 1 | 0 | 20
38930.5156 | 1 | 0 | 20
38930.5163 | 1 | 0 | 20
38930.5169 | 1 | 0 | 20
38930.5176 | 1 | 0 | 20
38930.5183 | 1 | 0 | 20
38930.519 | 1 | 0 | 20
38930.5197 | 1 | 1 | 20
38930.5203 | 929 | 893 | 20
38930.521 | 969 | 937 | 20
38930.5217 | 920 | 884 | 20
38930.5224 | 1158 | 1114 | 20
38930.5231 | 1041 | 954 | 20
38930.5237 | 1040 | 1124 | 20
38930.5244 | 932 | 832 | 20
38930.5251 | 1119 | 1057 | 20
38930.5258 | 986 | 888 | 20
38930.5265 | 1041 | 957 | 20
38930.5271 | 989 | 889 | 20
38930.5278 | 1157 | 1186 | 20
38930.5285 | 938 | 825 | 20
38930.5292 | 970 | 951 | 20
38930.5299 | 975 | 883 | 20
38930.5305 | 921 | 930 | 20
38930.5312 | 958 | 858 | 20
20
38930.5033 | 1 | 0 | 21
38930.504 | 1 | 0 | 21
38930.5047 | 1 | 0 | 21
38930.5054 | 1 | 0 | 21
38930.5061 | 1 | 0 | 21
38930.5067 | 1 | 0 | 21
38930.5074 | 1 | 0 | 21
38930.5081 | 1 | 0 | 21
38930.5088 | 1 | 0 | 21
38930.5095 | 1 | 0 | 21
38930.5101 | 1 | 0 | 21
38930.5108 | 1 | 0 | 21
38930.5115 | 1 | 0 | 21
38930.5122 | 1 | 0 | 21
38930.5129 | 1 | 0 | 21
38930.5135 | 1 | 0 | 21
38930.5142 | 1 | 0 | 21
38930.5149 | 1 | 0 | 21
38930.5156 | 1 | 0 | 21
38930.5163 | 1 | 0 | 21
38930.5169 | 1 | 0 | 21
38930.5176 | 1 | 0 | 21
38930.5183 | 1 | 0 | 21
38930.519 | 1 | 1 | 21
38930.5197 | 1 | 0 | 21
38930.5203 | 27 | 38 | 21
38930.521 | 1182 | 910 | 21
38930.5217 | 1084 | 1155 | 21
38930.5224 | 1066 | 1032 | 21
38930.5231 | 1045 | 1058 | 21
38930.5238 | 964 | 852 | 21
38930.5244 | 1022 | 1024 | 21
38930.5251 | 1182 | 1146 | 21
38930.5258 | 1125 | 1067 | 21
38930.5265 | 1116 | 1052 | 21
38930.5272 | 992 | 899 | 21
38930.5278 | 1118 | 1057 | 21
38930.5285 | 1182 | 1114 | 21
38930.5292 | 1136 | 1084 | 21
38930.5299 | 1094 | 1033 | 21
38930.5306 | 954 | 862 | 21
38930.5312 | 928 | 885 | 21
21
38930.5034 | 1 | 0 | 22
38930.504 | 1 | 0 | 22
38930.5047 | 1 | 0 | 22
38930.5054 | 1 | 0 | 22
38930.5061 | 1 | 0 | 22
38930.5067 | 1 | 0 | 22
38930.5074 | 1 | 0 | 22
38930.5081 | 1 | 0 | 22
38930.5088 | 1 | 0 | 22
38930.5095 | 1 | 0 | 22
38930.5102 | 1 | 0 | 22
38930.5108 | 1 | 0 | 22
38930.5115 | 1 | 0 | 22
38930.5122 | 1 | 0 | 22
38930.5129 | 1 | 0 | 22
38930.5136 | 1 | 0 | 22
38930.5142 | 1 | 0 | 22
38930.5149 | 1 | 0 | 22
38930.5156 | 1 | 0 | 22
38930.5163 | 1 | 0 | 22
38930.517 | 1 | 0 | 22
38930.5176 | 1 | 0 | 22
38930.5183 | 1 | 0 | 22
38930.519 | 1 | 0 | 22
38930.5197 | 1 | 0 | 22
38930.5204 | 5 | 12 | 22
38930.521 | 1085 | 1059 | 22
38930.5217 | 1059 | 1083 | 22
38930.5224 | 978 | 881 | 22
38930.5231 | 1053 | 847 | 22
38930.5238 | 1055 | 1135 | 22
38930.5244 | 1165 | 1186 | 22
38930.5251 | 1043 | 852 | 22
38930.5258 | 1137 | 1081 | 22
38930.5265 | 1168 | 1127 | 22
38930.5272 | 1097 | 1136 | 22
38930.5278 | 1148 | 1099 | 22
38930.5285 | 1127 | 1068 | 22
38930.5292 | 1011 | 1107 | 22
38930.5299 | 949 | 936 | 22
38930.5306 | 934 | 849 | 22
38930.5312 | 938 | 838 | 22
22
38930.5034 | 1 | 0 | 23
38930.5041 | 1 | 0 | 23
38930.5047 | 1 | 0 | 23
38930.5054 | 1 | 0 | 23
38930.5061 | 1 | 0 | 23
38930.5068 | 1 | 0 | 23
38930.5075 | 1 | 0 | 23
38930.5081 | 1 | 0 | 23
38930.5088 | 1 | 0 | 23
38930.5095 | 1 | 0 | 23
38930.5102 | 1 | 0 | 23
38930.5109 | 1 | 0 | 23
38930.5115 | 1 | 0 | 23
38930.5122 | 1 | 0 | 23
38930.5129 | 1 | 0 | 23
38930.5136 | 1 | 0 | 23
38930.5143 | 1 | 1 | 23
38930.5149 | 1 | 0 | 23
38930.5156 | 1 | 0 | 23
38930.5163 | 1 | 0 | 23
38930.517 | 1 | 0 | 23
38930.5177 | 1 | 0 | 23
38930.5183 | 1 | 0 | 23
38930.519 | 1 | 0 | 23
38930.5197 | 1 | 0 | 23
38930.5204 | 1050 | 1021 | 23
38930.5211 | 11 | 24 | 23
38930.5217 | 6 | 21 | 23
38930.5224 | 6 | 23 | 23
38930.5231 | 6 | 20 | 23
38930.5238 | 6 | 19 | 23
38930.5245 | 922 | 826 | 23
38930.5251 | 1115 | 1079 | 23
38930.5258 | 1045 | 1082 | 23
38930.5265 | 1027 | 1097 | 23
38930.5272 | 990 | 1001 | 23
38930.5279 | 893 | 790 | 23
38930.5285 | 886 | 796 | 23
38930.5292 | 1015 | 1039 | 23
38930.5299 | 1023 | 957 | 23
38930.5306 | 895 | 807 | 23
38930.5313 | 1129 | 1113 | 23
23
38930.5034 | 1 | 0 | 24
38930.5041 | 1 | 0 | 24
38930.5047 | 1 | 0 | 24
38930.5054 | 1 | 0 | 24
38930.5061 | 1 | 0 | 24
38930.5068 | 1 | 0 | 24
38930.5075 | 1 | 0 | 24
38930.5081 | 1 | 0 | 24
38930.5088 | 1 | 0 | 24
38930.5095 | 1 | 0 | 24
38930.5102 | 1 | 0 | 24
38930.5109 | 1 | 0 | 24
38930.5116 | 1 | 0 | 24
38930.5122 | 1 | 0 | 24
38930.5129 | 1 | 0 | 24
38930.5136 | 1 | 0 | 24
38930.5143 | 1 | 0 | 24
38930.515 | 1 | 0 | 24
38930.5156 | 1 | 0 | 24
38930.5163 | 1 | 0 | 24
38930.517 | 1 | 0 | 24
38930.5177 | 1 | 0 | 24
38930.5184 | 1 | 0 | 24
38930.519 | 1 | 0 | 24
38930.5197 | 1 | 0 | 24
38930.5204 | 941 | 907 | 24
38930.5211 | 7 | 22 | 24
38930.5218 | 6 | 14 | 24
38930.5224 | 6 | 13 | 24
38930.5231 | 6 | 14 | 24
38930.5238 | 6 | 13 | 24
38930.5245 | 1044 | 983 | 24
38930.5252 | 1030 | 962 | 24
38930.5258 | 1135 | 1023 | 24
38930.5265 | 1089 | 1039 | 24
38930.5272 | 909 | 881 | 24
38930.5279 | 1108 | 782 | 24
38930.5286 | 1080 | 1120 | 24
38930.5292 | 906 | 803 | 24
38930.5299 | 1131 | 1103 | 24
38930.5306 | 1107 | 1124 | 24
38930.5313 | 1110 | 1073 | 24
24
38930.5034 | 1 | 0 | 25
38930.5041 | 1 | 0 | 25
38930.5048 | 1 | 0 | 25
38930.5054 | 1 | 0 | 25
38930.5061 | 1 | 0 | 25
38930.5068 | 1 | 0 | 25
38930.5075 | 1 | 0 | 25
38930.5082 | 1 | 0 | 25
38930.5088 | 1 | 0 | 25
38930.5095 | 1 | 0 | 25
38930.5102 | 1 | 0 | 25
38930.5109 | 1 | 0 | 25
38930.5116 | 1 | 0 | 25
38930.5122 | 1 | 0 | 25
38930.5129 | 1 | 0 | 25
38930.5136 | 1 | 0 | 25
38930.5143 | 1 | 0 | 25
38930.515 | 1 | 0 | 25
38930.5156 | 1 | 0 | 25
38930.5163 | 1 | 0 | 25
38930.517 | 1 | 0 | 25
38930.5177 | 1 | 0 | 25
38930.5184 | 1 | 0 | 25
38930.5191 | 1 | 0 | 25
38930.5197 | 1 | 1 | 25
38930.5204 | 1184 | 1096 | 25
38930.5211 | 983 | 948 | 25
38930.5218 | 1068 | 1035 | 25
38930.5225 | 957 | 934 | 25
38930.5231 | 1051 | 967 | 25
38930.5238 | 1126 | 1065 | 25
38930.5245 | 1163 | 1120 | 25
38930.5252 | 1185 | 1150 | 25
38930.5259 | 1159 | 1112 | 25
38930.5265 | 1108 | 1170 | 25
38930.5272 | 1146 | 1097 | 25
38930.5279 | 961 | 859 | 25
38930.5286 | 1091 | 1023 | 25
38930.5293 | 1139 | 1088 | 25
38930.5299 | 1043 | 1060 | 25
38930.5306 | 1191 | 1165 | 25
38930.5313 | 1143 | 1185 | 25
25
38930.5034 | 1 | 0 | 26
38930.5041 | 2 | 0 | 26
38930.5048 | 1 | 0 | 26
38930.5055 | 1 | 0 | 26
38930.5061 | 1 | 0 | 26
38930.5068 | 1 | 0 | 26
38930.5082 | 1 | 0 | 26
38930.5089 | 1 | 0 | 26
38930.5095 | 1 | 0 | 26
38930.5102 | 1 | 0 | 26
38930.5109 | 1 | 0 | 26
38930.5116 | 1 | 0 | 26
38930.5123 | 1 | 0 | 26
38930.5129 | 1 | 0 | 26
38930.5136 | 1 | 0 | 26
38930.5143 | 1 | 0 | 26
38930.515 | 1 | 0 | 26
38930.5157 | 1 | 0 | 26
38930.5163 | 1 | 0 | 26
38930.517 | 1 | 0 | 26
38930.5177 | 1 | 0 | 26
38930.5184 | 1 | 0 | 26
38930.5191 | 1 | 0 | 26
38930.5197 | 1 | 0 | 26
38930.5204 | 1108 | 1081 | 26
38930.5211 | 952 | 917 | 26
38930.5218 | 1188 | 1169 | 26
38930.5225 | 1137 | 1085 | 26
38930.5231 | 1161 | 1117 | 26
38930.5238 | 1009 | 908 | 26
38930.5245 | 986 | 854 | 26
38930.5252 | 1193 | 1184 | 26
38930.5259 | 1102 | 1034 | 26
38930.5266 | 939 | 1035 | 26
38930.5272 | 1002 | 905 | 26
38930.5279 | 1128 | 1074 | 26
38930.5286 | 1040 | 952 | 26
38930.5293 | 1186 | 1078 | 26
38930.53 | 1167 | 1171 | 26
38930.5306 | 955 | 860 | 26
38930.5313 | 999 | 906 | 26
26
38930.5034 | 1 | 0 | 27
38930.5041 | 1 | 0 | 27
38930.5048 | 1 | 0 | 27
38930.5055 | 1 | 0 | 27
38930.5062 | 1 | 0 | 27
38930.5068 | 1 | 0 | 27
38930.5075 | 1 | 0 | 27
38930.5082 | 1 | 0 | 27
38930.5089 | 1 | 0 | 27
38930.5096 | 1 | 0 | 27
38930.5102 | 1 | 0 | 27
38930.5109 | 1 | 0 | 27
38930.5116 | 1 | 0 | 27
38930.5123 | 1 | 0 | 27
38930.513 | 1 | 0 | 27
38930.5136 | 1 | 0 | 27
38930.5143 | 1 | 0 | 27
38930.515 | 1 | 0 | 27
38930.5157 | 1 | 0 | 27
38930.5164 | 1 | 0 | 27
38930.517 | 1 | 0 | 27
38930.5177 | 1 | 0 | 27
38930.5184 | 1 | 0 | 27
38930.5191 | 1 | 0 | 27
38930.5198 | 1 | 1 | 27
38930.5204 | 987 | 952 | 27
38930.5211 | 965 | 999 | 27
38930.5218 | 1127 | 905 | 27
38930.5225 | 1053 | 974 | 27
38930.5232 | 1071 | 1096 | 27
38930.5238 | 1120 | 1162 | 27
38930.5245 | 1119 | 1175 | 27
38930.5252 | 1186 | 1153 | 27
38930.5259 | 967 | 861 | 27
38930.5266 | 925 | 886 | 27
38930.5272 | 1113 | 1049 | 27
38930.5279 | 1027 | 940 | 27
38930.5286 | 924 | 877 | 27
38930.5293 | 951 | 842 | 27
38930.53 | 1109 | 1053 | 27
38930.5306 | 1042 | 974 | 27
38930.5313 | 1197 | 1172 | 27
27
38930.5034 | 1 | 0 | 28
38930.5041 | 1 | 0 | 28
38930.5048 | 1 | 0 | 28
38930.5055 | 1 | 0 | 28
38930.5062 | 1 | 0 | 28
38930.5069 | 1 | 0 | 28
38930.5075 | 1 | 0 | 28
38930.5082 | 1 | 0 | 28
38930.5089 | 1 | 0 | 28
38930.5096 | 1 | 0 | 28
38930.5103 | 1 | 0 | 28
38930.5109 | 1 | 0 | 28
38930.5116 | 1 | 0 | 28
38930.5123 | 1 | 0 | 28
38930.513 | 1 | 0 | 28
38930.5137 | 1 | 0 | 28
38930.5143 | 1 | 0 | 28
38930.515 | 1 | 0 | 28
38930.5157 | 1 | 0 | 28
38930.5164 | 1 | 0 | 28
38930.5171 | 1 | 0 | 28
38930.5177 | 1 | 0 | 28
38930.5184 | 1 | 0 | 28
38930.5191 | 1 | 0 | 28
38930.5198 | 1 | 0 | 28
38930.5205 | 1023 | 993 | 28
38930.5211 | 1189 | 1089 | 28
38930.5218 | 951 | 912 | 28
38930.5225 | 1094 | 1028 | 28
38930.5232 | 1184 | 1150 | 28
38930.5239 | 1195 | 942 | 28
38930.5245 | 1192 | 883 | 28
38930.5252 | 1019 | 931 | 28
38930.5259 | 1055 | 976 | 28
38930.5266 | 1043 | 950 | 28
38930.5273 | 1035 | 950 | 28
38930.5279 | 963 | 936 | 28
38930.5286 | 1038 | 954 | 28
38930.5293 | 1070 | 1095 | 28
38930.53 | 1019 | 943 | 28
38930.5307 | 968 | 893 | 28
38930.5313 | 936 | 839 | 28
28
38930.5035 | 1 | 0 | 29
38930.5041 | 1 | 0 | 29
38930.5048 | 1 | 0 | 29
38930.5055 | 1 | 0 | 29
38930.5062 | 1 | 0 | 29
38930.5069 | 1 | 0 | 29
38930.5075 | 1 | 0 | 29
38930.5082 | 1 | 0 | 29
38930.5089 | 1 | 0 | 29
38930.5096 | 1 | 0 | 29
38930.5103 | 1 | 0 | 29
38930.5109 | 1 | 0 | 29
38930.5116 | 1 | 0 | 29
38930.5123 | 1 | 0 | 29
38930.513 | 1 | 0 | 29
38930.5137 | 1 | 0 | 29
38930.5144 | 1 | 0 | 29
38930.515 | 1 | 0 | 29
38930.5157 | 1 | 0 | 29
38930.5164 | 1 | 0 | 29
38930.5171 | 1 | 0 | 29
38930.5178 | 1 | 0 | 29
38930.5184 | 1 | 0 | 29
38930.5191 | 1 | 0 | 29
38930.5198 | 1 | 0 | 29
38930.5205 | 121 | 130 | 29
38930.5212 | 989 | 955 | 29
38930.5218 | 957 | 919 | 29
38930.5225 | 994 | 900 | 29
38930.5232 | 984 | 875 | 29
38930.5239 | 1049 | 959 | 29
38930.5246 | 1126 | 1168 | 29
38930.5252 | 948 | 841 | 29
38930.5259 | 1141 | 1087 | 29
38930.5266 | 1084 | 1005 | 29
38930.5273 | 1163 | 1179 | 29
38930.528 | 1050 | 965 | 29
38930.5286 | 1106 | 1042 | 29
38930.5293 | 1028 | 941 | 29
38930.53 | 952 | 862 | 29
38930.5307 | 1052 | 987 | 29
38930.5314 | 990 | 894 | 29
29
38930.5035 | 1 | 0 | 30
38930.5042 | 1 | 0 | 30
38930.5048 | 1 | 0 | 30
38930.5055 | 1 | 0 | 30
38930.5062 | 1 | 0 | 30
38930.5069 | 1 | 0 | 30
38930.5076 | 1 | 0 | 30
38930.5082 | 1 | 0 | 30
38930.5089 | 1 | 0 | 30
38930.5096 | 1 | 0 | 30
38930.5103 | 1 | 0 | 30
38930.511 | 1 | 0 | 30
38930.5116 | 1 | 0 | 30
38930.5123 | 1 | 0 | 30
38930.513 | 1 | 0 | 30
38930.5137 | 1 | 0 | 30
38930.5144 | 1 | 0 | 30
38930.515 | 1 | 0 | 30
38930.5157 | 1 | 0 | 30
38930.5164 | 1 | 0 | 30
38930.5171 | 1 | 0 | 30
38930.5178 | 1 | 0 | 30
38930.5184 | 1 | 0 | 30
38930.5191 | 1 | 0 | 30
38930.5198 | 1 | 0 | 30
38930.5205 | 149 | 172 | 30
38930.5212 | 1014 | 961 | 30
38930.5219 | 1194 | 1181 | 30
38930.5225 | 1073 | 1150 | 30
38930.5232 | 1041 | 948 | 30
38930.5239 | 1179 | 1135 | 30
38930.5246 | 922 | 983 | 30
38930.5253 | 1190 | 1185 | 30
38930.5259 | 1139 | 1082 | 30
38930.5266 | 991 | 878 | 30
38930.5273 | 1159 | 1116 | 30
38930.528 | 1009 | 918 | 30
38930.5287 | 1175 | 1186 | 30
38930.5293 | 1170 | 1132 | 30
38930.53 | 1010 | 869 | 30
38930.5307 | 1132 | 1086 | 30
38930.5314 | 1037 | 1051 | 30
30
38930.5035 | 1 | 0 | 31
38930.5042 | 1 | 0 | 31
38930.5049 | 1 | 0 | 31
38930.5055 | 1 | 0 | 31
38930.5062 | 1 | 0 | 31
38930.5069 | 1 | 0 | 31
38930.5076 | 1 | 0 | 31
38930.5083 | 1 | 0 | 31
38930.5089 | 1 | 0 | 31
38930.5096 | 1 | 0 | 31
38930.5103 | 1 | 0 | 31
38930.511 | 1 | 0 | 31
38930.5117 | 1 | 0 | 31
38930.5123 | 1 | 0 | 31
38930.513 | 1 | 0 | 31
38930.5137 | 1 | 0 | 31
38930.5144 | 1 | 0 | 31
38930.5151 | 1 | 0 | 31
38930.5157 | 1 | 0 | 31
38930.5164 | 1 | 0 | 31
38930.5171 | 1 | 0 | 31
38930.5178 | 1 | 0 | 31
38930.5185 | 1 | 0 | 31
38930.5191 | 1 | 0 | 31
38930.5198 | 1029 | 996 | 31
38930.5205 | 309 | 316 | 31
38930.5212 | 12 | 24 | 31
38930.5219 | 6 | 33 | 31
38930.5225 | 6 | 20 | 31
38930.5232 | 6 | 18 | 31
38930.5239 | 6 | 18 | 31
38930.5246 | 1102 | 1063 | 31
38930.5253 | 970 | 884 | 31
38930.5259 | 1010 | 932 | 31
38930.5266 | 1133 | 1108 | 31
38930.5273 | 978 | 900 | 31
38930.528 | 930 | 837 | 31
38930.5287 | 913 | 817 | 31
38930.5294 | 956 | 1049 | 31
38930.53 | 663 | 622 | 31
38930.5307 | 1019 | 963 | 31
38930.5314 | 880 | 800 | 31
31
38930.5035 | 1 | 0 | 32
38930.5042 | 1 | 0 | 32
38930.5049 | 1 | 0 | 32
38930.5056 | 1 | 0 | 32
38930.5062 | 1 | 0 | 32
38930.5069 | 1 | 0 | 32
38930.5076 | 1 | 0 | 32
38930.5083 | 1 | 0 | 32
38930.509 | 1 | 0 | 32
38930.5096 | 1 | 0 | 32
38930.5103 | 1 | 0 | 32
38930.511 | 1 | 0 | 32
38930.5117 | 1 | 0 | 32
38930.5124 | 1 | 0 | 32
38930.513 | 1 | 0 | 32
38930.5137 | 1 | 0 | 32
38930.5144 | 1 | 0 | 32
38930.5151 | 1 | 0 | 32
38930.5158 | 1 | 0 | 32
38930.5164 | 1 | 0 | 32
38930.5171 | 1 | 0 | 32
38930.5178 | 1 | 0 | 32
38930.5185 | 1 | 0 | 32
38930.5192 | 1 | 0 | 32
38930.5198 | 946 | 909 | 32
38930.5205 | 390 | 378 | 32
38930.5212 | 11 | 20 | 32
38930.5219 | 5 | 28 | 32
38930.5226 | 5 | 12 | 32
38930.5232 | 5 | 13 | 32
38930.5239 | 36 | 39 | 32
38930.5246 | 943 | 937 | 32
38930.5253 | 1126 | 1126 | 32
38930.526 | 1044 | 978 | 32
38930.5266 | 927 | 821 | 32
38930.5273 | 1128 | 1036 | 32
38930.528 | 1043 | 981 | 32
38930.5287 | 1124 | 1131 | 32
38930.5294 | 1022 | 1053 | 32
38930.53 | 610 | 568 | 32
38930.5307 | 1124 | 1103 | 32
38930.5314 | 968 | 890 | 32
32
38930.5035 | 1 | 0 | 33
38930.5042 | 1 | 0 | 33
38930.5049 | 1 | 0 | 33
38930.5056 | 1 | 0 | 33
38930.5062 | 1 | 0 | 33
38930.5069 | 1 | 0 | 33
38930.5076 | 1 | 0 | 33
38930.5083 | 1 | 0 | 33
38930.509 | 1 | 0 | 33
38930.5097 | 1 | 0 | 33
38930.5103 | 1 | 0 | 33
38930.511 | 1 | 0 | 33
38930.5117 | 1 | 0 | 33
38930.5124 | 1 | 0 | 33
38930.5131 | 1 | 0 | 33
38930.5137 | 1 | 0 | 33
38930.5144 | 1 | 0 | 33
38930.5151 | 1 | 0 | 33
38930.5158 | 1 | 0 | 33
38930.5165 | 1 | 0 | 33
38930.5171 | 1 | 0 | 33
38930.5178 | 1 | 0 | 33
38930.5185 | 1 | 0 | 33
38930.5192 | 1 | 0 | 33
38930.5199 | 168 | 166 | 33
38930.5205 | 895 | 860 | 33
38930.5212 | 10 | 15 | 33
38930.5219 | 5 | 25 | 33
38930.5226 | 6 | 10 | 33
38930.5233 | 5 | 10 | 33
38930.5239 | 564 | 569 | 33
38930.5246 | 1058 | 1000 | 33
38930.5253 | 882 | 843 | 33
38930.526 | 927 | 824 | 33
38930.5267 | 964 | 955 | 33
38930.5273 | 1136 | 1115 | 33
38930.528 | 899 | 801 | 33
38930.5287 | 1096 | 1051 | 33
38930.5294 | 1105 | 795 | 33
38930.5301 | 1010 | 1034 | 33
38930.5308 | 1122 | 1028 | 33
38930.5314 | 909 | 818 | 33
33
38930.5035 | 1 | 0 | 34
38930.5042 | 1 | 0 | 34
38930.5049 | 1 | 0 | 34
38930.5056 | 1 | 0 | 34
38930.5063 | 1 | 0 | 34
38930.5069 | 1 | 0 | 34
38930.5076 | 1 | 0 | 34
38930.5083 | 1 | 0 | 34
38930.509 | 1 | 0 | 34
38930.5097 | 1 | 0 | 34
38930.5103 | 1 | 0 | 34
38930.511 | 1 | 0 | 34
38930.5117 | 1 | 0 | 34
38930.5124 | 1 | 0 | 34
38930.5131 | 1 | 0 | 34
38930.5137 | 1 | 0 | 34
38930.5144 | 1 | 0 | 34
38930.5151 | 1 | 0 | 34
38930.5158 | 1 | 0 | 34
38930.5165 | 1 | 0 | 34
38930.5172 | 1 | 0 | 34
38930.5178 | 1 | 0 | 34
38930.5185 | 1 | 0 | 34
38930.5192 | 1 | 0 | 34
38930.5199 | 162 | 160 | 34
38930.5206 | 928 | 893 | 34
38930.5212 | 36 | 41 | 34
38930.5219 | 5 | 21 | 34
38930.5226 | 5 | 10 | 34
38930.5233 | 6 | 9 | 34
38930.524 | 687 | 667 | 34
38930.5246 | 921 | 824 | 34
38930.5253 | 1046 | 989 | 34
38930.526 | 1053 | 987 | 34
38930.5267 | 1078 | 1019 | 34
38930.5274 | 1086 | 1038 | 34
38930.528 | 968 | 818 | 34
38930.5287 | 1134 | 1128 | 34
38930.5294 | 938 | 849 | 34
38930.5301 | 878 | 804 | 34
38930.5308 | 1062 | 1113 | 34
38930.5314 | 966 | 887 | 34
34
38930.5036 | 1 | 0 | 35
38930.5042 | 1 | 0 | 35
38930.5049 | 1 | 0 | 35
38930.5056 | 1 | 0 | 35
38930.5063 | 1 | 0 | 35
38930.507 | 1 | 0 | 35
38930.5077 | 1 | 1 | 35
38930.5083 | 1 | 0 | 35
38930.509 | 1 | 0 | 35
38930.5097 | 1 | 0 | 35
38930.5104 | 1 | 0 | 35
38930.511 | 1 | 0 | 35
38930.5117 | 1 | 0 | 35
38930.5124 | 1 | 0 | 35
38930.5131 | 1 | 0 | 35
38930.5138 | 1 | 0 | 35
38930.5144 | 1 | 0 | 35
38930.5151 | 1 | 0 | 35
38930.5158 | 1 | 0 | 35
38930.5165 | 1 | 0 | 35
38930.5172 | 1 | 0 | 35
38930.5178 | 1 | 0 | 35
38930.5185 | 1 | 0 | 35
38930.5192 | 1 | 0 | 35
38930.5199 | 71 | 69 | 35
38930.5206 | 1040 | 1108 | 35
38930.5212 | 9 | 13 | 35
38930.5219 | 5 | 11 | 35
38930.5226 | 5 | 9 | 35
38930.5233 | 6 | 9 | 35
38930.524 | 735 | 579 | 35
38930.5247 | 1116 | 1090 | 35
38930.5253 | 922 | 1022 | 35
38930.526 | 953 | 1046 | 35
38930.5267 | 1060 | 1116 | 35
38930.5274 | 924 | 828 | 35
38930.5281 | 1106 | 1129 | 35
38930.5287 | 1028 | 1058 | 35
38930.5294 | 928 | 916 | 35
38930.5301 | 1047 | 775 | 35
38930.5308 | 1081 | 1043 | 35
38930.5315 | 915 | 827 | 35
35
38930.5036 | 1 | 0 | 36
38930.5043 | 1 | 0 | 36
38930.5049 | 1 | 0 | 36
38930.5056 | 1 | 0 | 36
38930.5063 | 1 | 0 | 36
38930.507 | 1 | 0 | 36
38930.5077 | 1 | 0 | 36
38930.5083 | 1 | 0 | 36
38930.509 | 1 | 0 | 36
38930.5097 | 1 | 0 | 36
38930.5104 | 1 | 0 | 36
38930.5111 | 1 | 0 | 36
38930.5117 | 1 | 0 | 36
38930.5124 | 1 | 0 | 36
38930.5131 | 1 | 0 | 36
38930.5138 | 1 | 0 | 36
38930.5145 | 1 | 0 | 36
38930.5152 | 1 | 0 | 36
38930.5158 | 1 | 0 | 36
38930.5165 | 1 | 0 | 36
38930.5172 | 1 | 0 | 36
38930.5179 | 1 | 0 | 36
38930.5186 | 1 | 0 | 36
38930.5192 | 1 | 0 | 36
38930.5199 | 224 | 237 | 36
38930.5206 | 1140 | 1124 | 36
38930.5213 | 7 | 11 | 36
38930.5219 | 5 | 16 | 36
38930.5226 | 5 | 9 | 36
38930.5233 | 7 | 9 | 36
38930.524 | 637 | 619 | 36
38930.5247 | 937 | 838 | 36
38930.5253 | 897 | 865 | 36
38930.526 | 1067 | 1003 | 36
38930.5267 | 1039 | 1068 | 36
38930.5274 | 1022 | 956 | 36
38930.5281 | 997 | 925 | 36
38930.5287 | 999 | 918 | 36
38930.5294 | 1066 | 1018 | 36
38930.5301 | 902 | 830 | 36
38930.5315 | 1056 | 993 | 36
36
38930.5036 | 1 | 0 | 37
38930.5043 | 1 | 0 | 37
38930.505 | 1 | 0 | 37
38930.5056 | 1 | 0 | 37
38930.5063 | 1 | 0 | 37
38930.507 | 1 | 0 | 37
38930.5077 | 1 | 0 | 37
38930.5084 | 1 | 0 | 37
38930.509 | 1 | 0 | 37
38930.5097 | 1 | 0 | 37
38930.5104 | 1 | 0 | 37
38930.5111 | 1 | 0 | 37
38930.5118 | 1 | 0 | 37
38930.5124 | 1 | 0 | 37
38930.5131 | 1 | 0 | 37
38930.5138 | 1 | 0 | 37
38930.5145 | 1 | 0 | 37
38930.5152 | 1 | 0 | 37
38930.5158 | 1 | 0 | 37
38930.5165 | 1 | 0 | 37
38930.5172 | 1 | 0 | 37
38930.5179 | 1 | 0 | 37
38930.5186 | 1 | 0 | 37
38930.5192 | 1 | 0 | 37
38930.5199 | 1147 | 1125 | 37
38930.5206 | 1168 | 1151 | 37
38930.5213 | 967 | 947 | 37
38930.522 | 1104 | 1073 | 37
38930.5227 | 958 | 917 | 37
38930.5233 | 1020 | 980 | 37
38930.524 | 1054 | 968 | 37
38930.5247 | 1194 | 1174 | 37
38930.5254 | 1018 | 1018 | 37
38930.5261 | 1009 | 1001 | 37
38930.5267 | 1127 | 1065 | 37
38930.5274 | 1195 | 1176 | 37
38930.5281 | 1123 | 1062 | 37
38930.5288 | 1139 | 834 | 37
38930.5295 | 1134 | 1179 | 37
38930.5301 | 1111 | 1062 | 37
38930.5308 | 1088 | 1026 | 37
38930.5315 | 1020 | 937 | 37
37
38930.5036 | 1 | 0 | 38
38930.5043 | 1 | 0 | 38
38930.505 | 1 | 0 | 38
38930.5056 | 1 | 0 | 38
38930.5063 | 1 | 0 | 38
38930.507 | 1 | 0 | 38
38930.5077 | 1 | 0 | 38
38930.5084 | 1 | 0 | 38
38930.5091 | 1 | 0 | 38
38930.5097 | 1 | 0 | 38
38930.5104 | 1 | 0 | 38
38930.5111 | 1 | 0 | 38
38930.5118 | 1 | 0 | 38
38930.5125 | 1 | 0 | 38
38930.5131 | 1 | 0 | 38
38930.5138 | 1 | 0 | 38
38930.5145 | 1 | 0 | 38
38930.5152 | 1 | 0 | 38
38930.5159 | 1 | 0 | 38
38930.5165 | 1 | 0 | 38
38930.5179 | 1 | 0 | 38
38930.5186 | 1 | 0 | 38
38930.5193 | 1 | 0 | 38
38930.5199 | 1118 | 1171 | 38
38930.5206 | 1129 | 1106 | 38
38930.5213 | 1056 | 1076 | 38
38930.522 | 1141 | 1106 | 38
38930.5227 | 1011 | 1038 | 38
38930.5233 | 1027 | 951 | 38
38930.524 | 1147 | 1096 | 38
38930.5247 | 943 | 833 | 38
38930.5254 | 977 | 966 | 38
38930.5261 | 940 | 820 | 38
38930.5267 | 1021 | 1113 | 38
38930.5274 | 1174 | 1187 | 38
38930.5281 | 1089 | 1124 | 38
38930.5288 | 1183 | 1186 | 38
38930.5295 | 1176 | 1142 | 38
38930.5302 | 1136 | 1092 | 38
38930.5308 | 1196 | 1185 | 38
38930.5315 | 1001 | 900 | 38
38
38930.5036 | 1 | 0 | 39
38930.5043 | 1 | 0 | 39
38930.505 | 1 | 0 | 39
38930.5057 | 1 | 0 | 39
38930.5063 | 1 | 0 | 39
38930.507 | 1 | 0 | 39
38930.5077 | 1 | 0 | 39
38930.5084 | 1 | 0 | 39
38930.5091 | 1 | 1 | 39
38930.5097 | 1 | 0 | 39
38930.5104 | 1 | 0 | 39
38930.5111 | 1 | 0 | 39
38930.5118 | 1 | 0 | 39
38930.5125 | 1 | 0 | 39
38930.5131 | 1 | 0 | 39
38930.5138 | 1 | 0 | 39
38930.5145 | 1 | 0 | 39
38930.5152 | 1 | 0 | 39
38930.5159 | 1 | 0 | 39
38930.5166 | 1 | 0 | 39
38930.5172 | 1 | 0 | 39
38930.5179 | 1 | 0 | 39
38930.5186 | 1 | 0 | 39
38930.5193 | 1 | 0 | 39
38930.52 | 906 | 871 | 39
38930.5206 | 1119 | 1095 | 39
38930.5213 | 1030 | 945 | 39
38930.522 | 929 | 865 | 39
38930.5227 | 973 | 889 | 39
38930.5234 | 1047 | 964 | 39
38930.524 | 1090 | 1157 | 39
38930.5247 | 1168 | 1185 | 39
38930.5254 | 945 | 838 | 39
38930.5261 | 1107 | 1036 | 39
38930.5268 | 999 | 896 | 39
38930.5274 | 1190 | 1160 | 39
38930.5281 | 1187 | 864 | 39
38930.5288 | 987 | 891 | 39
38930.5295 | 994 | 993 | 39
38930.5302 | 928 | 870 | 39
38930.5308 | 988 | 904 | 39
38930.5315 | 1063 | 985 | 39
39
38930.5036 | 1 | 0 | 40
38930.5043 | 1 | 0 | 40
38930.505 | 1 | 0 | 40
38930.5057 | 1 | 0 | 40
38930.5064 | 1 | 0 | 40
38930.507 | 1 | 0 | 40
38930.5077 | 1 | 0 | 40
38930.5084 | 1 | 0 | 40
38930.5091 | 1 | 0 | 40
38930.5098 | 1 | 0 | 40
38930.5105 | 1 | 0 | 40
38930.5111 | 1 | 0 | 40
38930.5118 | 1 | 0 | 40
38930.5125 | 1 | 0 | 40
38930.5132 | 1 | 0 | 40
38930.5139 | 1 | 0 | 40
38930.5145 | 1 | 0 | 40
38930.5152 | 1 | 0 | 40
38930.5159 | 1 | 0 | 40
38930.5166 | 1 | 0 | 40
38930.5173 | 1 | 0 | 40
38930.5179 | 1 | 0 | 40
38930.5186 | 1 | 0 | 40
38930.5193 | 1 | 0 | 40
38930.52 | 1010 | 1101 | 40
38930.5207 | 1032 | 1001 | 40
38930.5213 | 1058 | 980 | 40
38930.522 | 1192 | 1168 | 40
38930.5227 | 1099 | 1165 | 40
38930.5234 | 1141 | 1086 | 40
38930.5241 | 1193 | 901 | 40
38930.5247 | 1155 | 1184 | 40
38930.5254 | 948 | 919 | 40
38930.5261 | 974 | 945 | 40
38930.5268 | 1015 | 1110 | 40
38930.5275 | 1156 | 1187 | 40
38930.5281 | 1021 | 929 | 40
38930.5288 | 1148 | 1099 | 40
38930.5295 | 1172 | 1188 | 40
38930.5302 | 995 | 918 | 40
38930.5309 | 1048 | 979 | 40
38930.5315 | 991 | 984 | 40
40
38930.5037 | 1 | 0 | 41
38930.5043 | 1 | 0 | 41
38930.505 | 1 | 0 | 41
38930.5057 | 1 | 1 | 41
38930.5064 | 1 | 0 | 41
38930.5071 | 1 | 0 | 41
38930.5077 | 1 | 0 | 41
38930.5084 | 1 | 0 | 41
38930.5091 | 1 | 0 | 41
38930.5098 | 1 | 0 | 41
38930.5105 | 1 | 0 | 41
38930.5111 | 1 | 0 | 41
38930.5118 | 1 | 0 | 41
38930.5125 | 1 | 0 | 41
38930.5132 | 1 | 0 | 41
38930.5139 | 1 | 0 | 41
38930.5145 | 1 | 0 | 41
38930.5152 | 1 | 0 | 41
38930.5159 | 1 | 0 | 41
38930.5166 | 1 | 0 | 41
38930.5173 | 1 | 0 | 41
38930.518 | 1 | 0 | 41
38930.5186 | 1 | 0 | 41
38930.5193 | 1 | 0 | 41
38930.52 | 914 | 880 | 41
38930.5207 | 1105 | 1083 | 41
38930.5214 | 922 | 884 | 41
38930.522 | 1051 | 977 | 41
38930.5227 | 1132 | 1077 | 41
38930.5234 | 1069 | 992 | 41
38930.5241 | 1075 | 995 | 41
38930.5248 | 1142 | 1091 | 41
38930.5254 | 1060 | 1145 | 41
38930.5261 | 1020 | 1016 | 41
38930.5268 | 1107 | 1043 | 41
38930.5275 | 1184 | 1152 | 41
38930.5282 | 1170 | 1129 | 41
38930.5288 | 922 | 911 | 41
38930.5295 | 1033 | 1047 | 41
38930.5302 | 973 | 898 | 41
38930.5309 | 1097 | 866 | 41
38930.5316 | 977 | 879 | 41
41
38930.5037 | 1 | 0 | 42
38930.5044 | 1 | 0 | 42
38930.505 | 1 | 0 | 42
38930.5057 | 1 | 0 | 42
38930.5064 | 1 | 0 | 42
38930.5071 | 1 | 0 | 42
38930.5078 | 1 | 0 | 42
38930.5084 | 1 | 0 | 42
38930.5091 | 1 | 0 | 42
38930.5098 | 1 | 0 | 42
38930.5105 | 1 | 0 | 42
38930.5112 | 1 | 0 | 42
38930.5118 | 1 | 0 | 42
38930.5125 | 1 | 0 | 42
38930.5132 | 1 | 0 | 42
38930.5139 | 1 | 0 | 42
38930.5146 | 1 | 0 | 42
38930.5152 | 1 | 0 | 42
38930.5159 | 1 | 0 | 42
38930.5166 | 1 | 0 | 42
38930.5173 | 1 | 0 | 42
38930.518 | 1 | 0 | 42
38930.5186 | 1 | 0 | 42
38930.5193 | 1 | 0 | 42
38930.52 | 965 | 931 | 42
38930.5207 | 1159 | 1149 | 42
38930.5214 | 1019 | 930 | 42
38930.522 | 1140 | 1180 | 42
38930.5227 | 924 | 900 | 42
38930.5234 | 1063 | 979 | 42
38930.5241 | 948 | 913 | 42
38930.5248 | 1187 | 1082 | 42
38930.5255 | 1074 | 1002 | 42
38930.5261 | 1109 | 1147 | 42
38930.5268 | 1192 | 897 | 42
38930.5275 | 1037 | 1126 | 42
38930.5282 | 1097 | 1132 | 42
38930.5289 | 1109 | 1053 | 42
38930.5295 | 1084 | 1022 | 42
38930.5302 | 1136 | 1180 | 42
38930.5309 | 928 | 910 | 42
38930.5316 | 1020 | 1024 | 42
42