## Test Facts
Last row in IRMS data sheets: | 24
Time when Penlight power was initiated: | 62

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 20
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, PVC jacketed, control cable (identified in the test matrix as "TS/TP"). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 62 seconds of baseline data monitoring. Special Note: Test setup included a thermocouple on the inner surface of one center tray rung.
DAQ Time | Penlight Time | Event | Interpretation
62 | 0 | Initated Penlight Heating
663 | 601 | Cables ignite
674-685 | 612-623 | Conductors 3, 4, 5 & 6 all short to ground (587, <1, <1 & 10) | Initial failures are by conductor to ground shorting
680 | 618 | Penlight power is shutoff
682-687 | 620-625 | Conductor 3 shorts to conductors 5, 6 & 7 (28, 40 & 397)
688 | 626 | Conductor 7 shorts to ground at less than 100 ohms (5)
693-696 | 631-634 | Conductor 4 shorts to conductors 6 & 7 at less than 100 ohms (61 & 10)
699-701 | 637-639 | Conductor 5 shorts to conductors 6 & 7 (142 & 56)
704 | 642 | Conductor 6 shorts to conductor 7 at less than 1000 ohms (873)
707-721 | 645-659 | Conductor 1 shorts to conductors 2, 4, 6 & 7 (20, 21, 179 & 750)
714 | 652 | Conductor 1 shorts to ground at much less than 100 ohms (<1)
724-735 | 662-673 | Conductor 2 shorts to conductors 3, 4 & 7 (256, <1 & 543)
725-733 | 663-671 | Conductor 2 shorts to ground at much less than 100 ohms (<1); the existing ground fault on conductor 3 degrades to less than 100 ohms (4) | All conductors are shorted to ground
746-763 | 684-701 | Conductor 4 shorts to conductor 5 at much less than 100 ohms (<1); the existing shorts between conductors 3 & 7, 5 & 6 and 6 & 7 all degrade to less than 100 ohms (16, 15 & 13)
769-780 | 707-718 | Conductor 1 shorts to conductors 3 & 5 at less than 100 ohms (<1 & 21); the existing short between conductor 1 and conductors 6 & 7 degrade to less than 100 ohms (15 & 13)
783-794 | 721-732 | Conductor 2 shorts to conductors 5 & 6 at less than 100 ohms (9 & 2); the existing shorts between conductor 2 and conductors 3 & 7 degrade to less than 100 ohms (<1 & 18)
797 | 735 | Conductor 3 shorts to conductor 4 at much less than 100 ohms (<1)
Additional Observations
Observation 1 | The progression of failure modes for this cable did not follow that expected for a typical thermoset-insulated cable: conductor-to-conductor shorts followed by shorting to ground.
Observation 2 | It took 601 s (10.0 min.) from the start of Penlight heating for ignition to occur. It took 612 s (10.2 min.) from the start of Penlight heating for the first conductor-to-ground short to occur, and it took 620 s (10.3 min.) for the first conductor-to-conductor short.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 20 |  |  | 2006-07-12 | 11:44
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-61 | 513375.9997 | -58 | 490375.9997 | -55 | 513775.9997 | -52.5 | 510375.9997 | -49.5 | 515375.9997 | -46.5 | 517175.9997 | -44 | 510175.9997 | -41.5 | 509375.9997 | -38.5 | 510975.9997 | -35.5 | 516575.9997 | -32.5 | 504775.9997 | -30 | 511375.9997 | -27 | 484175.9997 | -24.5 | 510775.9997 | -21.5 | 515975.9997 | -19 | 514575.9997 | -16 | 515975.9997 | -13 | 502975.9997 | -10.5 | 512575.9997 | -7.5 | 515175.9997 | -5 | 510575.9997 | -61 | 484175.9997
-2 | 513375.9997 | 1 | 490375.9997 | 3.5 | 513775.9997 | 6.5 | 510375.9997 | 9 | 515375.9997 | 12 | 517175.9997 | 15 | 510175.9997 | 17.5 | 509375.9997 | 20.5 | 510975.9997 | 23 | 516575.9997 | 26 | 504775.9997 | 29 | 511375.9997 | 31.5 | 484175.9997 | 34.5 | 510775.9997 | 37.5 | 515975.9997 | 40 | 514575.9997 | 42.5 | 515975.9997 | 45.5 | 502975.9997 | 48.5 | 512575.9997 | 51.5 | 515175.9997 | 54 | 510575.9997 | -2 | 484175.9997
56.5 | 513375.9997 | 59.5 | 490375.9997 | 62.5 | 513775.9997 | 65.5 | 510375.9997 | 68 | 515375.9997 | 70.5 | 517175.9997 | 73.5 | 510175.9997 | 76.5 | 509375.9997 | 79.5 | 510975.9997 | 82 | 516575.9997 | 84.5 | 504775.9997 | 87.5 | 511375.9997 | 90.5 | 484175.9997 | 93.5 | 510775.9997 | 96 | 515975.9997 | 98.5 | 514575.9997 | 101.5 | 515975.9997 | 104.5 | 502975.9997 | 107 | 512575.9997 | 110 | 515175.9997 | 113 | 510575.9997 | 56.5 | 484175.9997
115.5 | 513375.9997 | 118.5 | 490375.9997 | 121 | 513775.9997 | 124 | 510375.9997 | 127 | 515375.9997 | 129.5 | 517175.9997 | 132.5 | 510175.9997 | 135 | 509375.9997 | 138 | 510975.9997 | 141 | 516575.9997 | 143.5 | 504775.9997 | 146.5 | 511375.9997 | 149 | 484175.9997 | 152 | 510775.9997 | 155 | 515975.9997 | 157.5 | 514575.9997 | 160.5 | 515975.9997 | 163 | 502975.9997 | 166 | 512575.9997 | 168.5 | 515175.9997 | 171.5 | 510575.9997 | 115.5 | 484175.9997
174.5 | 513375.9997 | 177.5 | 490375.9997 | 180 | 513775.9997 | 182.5 | 510375.9997 | 185.5 | 515375.9997 | 188.5 | 517175.9997 | 191.5 | 510175.9997 | 194 | 509375.9997 | 196.5 | 510975.9997 | 199.5 | 516575.9997 | 202.5 | 504775.9997 | 205 | 511375.9997 | 208 | 484175.9997 | 210.5 | 510775.9997 | 213.5 | 515975.9997 | 216.5 | 514575.9997 | 219 | 515975.9997 | 222 | 502975.9997 | 225 | 512575.9997 | 227.5 | 515175.9997 | 230.5 | 510575.9997 | 174.5 | 484175.9997
233 | 513375.9997 | 236 | 490375.9997 | 239 | 513775.9997 | 241.5 | 510375.9997 | 244.5 | 515375.9997 | 247 | 517175.9997 | 250 | 255037.9994 | 252.5 | 509375.9997 | 255.5 | 510975.9997 | 258.5 | 516575.9997 | 261 | 504775.9997 | 264 | 511375.9997 | 267 | 484175.9997 | 269.5 | 510775.9997 | 272.5 | 515975.9997 | 275 | 514575.9997 | 278 | 515975.9997 | 280.5 | 502975.9997 | 283.5 | 512575.9997 | 286.5 | 515175.9997 | 289 | 510575.9997 | 233 | 255037.9994
292 | 513375.9997 | 294.5 | 490375.9997 | 297.5 | 513775.9997 | 300.5 | 510375.9997 | 303.5 | 515375.9997 | 306 | 517175.9997 | 308.5 | 510175.9997 | 311.5 | 509375.9997 | 314.5 | 510975.9997 | 317 | 516575.9997 | 320 | 504775.9997 | 322.5 | 511375.9997 | 325.5 | 484175.9997 | 328.5 | 510775.9997 | 331 | 515975.9997 | 334 | 514575.9997 | 336.5 | 515975.9997 | 339.5 | 502975.9997 | 342.5 | 512575.9997 | 345 | 515175.9997 | 348 | 510575.9997 | 292 | 484175.9997
350.5 | 513375.9997 | 353.5 | 490375.9997 | 356.5 | 513775.9997 | 359 | 510375.9997 | 362 | 515375.9997 | 364.5 | 517175.9997 | 367.5 | 510175.9997 | 370.5 | 509375.9997 | 373 | 510975.9997 | 376 | 516575.9997 | 378.5 | 504775.9997 | 381.5 | 511375.9997 | 384.5 | 484175.9997 | 387.5 | 510775.9997 | 390 | 515975.9997 | 392.5 | 514575.9997 | 395.5 | 515975.9997 | 398.5 | 502975.9997 | 401 | 512575.9997 | 404 | 515175.9997 | 406.5 | 510575.9997 | 350.5 | 484175.9997
409.5 | 513375.9997 | 412.5 | 490375.9997 | 415 | 513775.9997 | 418 | 510375.9997 | 421 | 515375.9997 | 423.5 | 517175.9997 | 426.5 | 510175.9997 | 429 | 509375.9997 | 432 | 510975.9997 | 434.5 | 516575.9997 | 437.5 | 504775.9997 | 440.5 | 511375.9997 | 443 | 484175.9997 | 446 | 510775.9997 | 449 | 515975.9997 | 451.5 | 514575.9997 | 454.5 | 515975.9997 | 457 | 502975.9997 | 460 | 512575.9997 | 462.5 | 515175.9997 | 465.5 | 510575.9997 | 409.5 | 484175.9997
468.5 | 513375.9997 | 471 | 490375.9997 | 474 | 513775.9997 | 476.5 | 510375.9997 | 479.5 | 515375.9997 | 482.5 | 517175.9997 | 485 | 510175.9997 | 488 | 509375.9997 | 490.5 | 510975.9997 | 493.5 | 516575.9997 | 496.5 | 504775.9997 | 499 | 511375.9997 | 502 | 484175.9997 | 504.5 | 510775.9997 | 507.5 | 515975.9997 | 510.5 | 514575.9997 | 513 | 515975.9997 | 516 | 502975.9997 | 518.5 | 512575.9997 | 521.5 | 515175.9997 | 524.5 | 510575.9997 | 468.5 | 484175.9997
527 | 513375.9997 | 530 | 490375.9997 | 532.5 | 513775.9997 | 535.5 | 510375.9997 | 538.5 | 515375.9997 | 541 | 517175.9997 | 544 | 510175.9997 | 546.5 | 509375.9997 | 549.5 | 510975.9997 | 552.5 | 516575.9997 | 555 | 504775.9997 | 558 | 511375.9997 | 560.5 | 484175.9997 | 563.5 | 510775.9997 | 566.5 | 515975.9997 | 569 | 514575.9997 | 572 | 515975.9997 | 574.5 | 502975.9997 | 577.5 | 512575.9997 | 580.5 | 515175.9997 | 583 | 510575.9997 | 527 | 484175.9997
586 | 513375.9997 | 588.5 | 490375.9997 | 591.5 | 513775.9997 | 594.5 | 510375.9997 | 597 | 515375.9997 | 600 | 517175.9997 | 602.5 | 510175.9997 | 605.5 | 509375.9997 | 608.5 | 510975.9997 | 611 | 516575.9997 | 614 | 504775.9997 | 616.5 | 511375.9997 | 619.5 | 27.6065 | 622.5 | 40.1903 | 625 | 396.8804 | 628 | 2016.0777 | 630.5 | 61.1748 | 633.5 | 9.9557 | 636.5 | 142.2479 | 639 | 55.7479 | 642 | 873.0398 | 586 | 9.9557
644.5 | 19.9816 | 647.5 | 1428.1051 | 650.5 | 20.6036 | 653 | 1647.5825 | 656 | 178.514 | 658.5 | 750.4313 | 661.5 | 256.3999 | 664.5 | 0.85761 | 667 | 3262.2957 | 670 | 17812.4095 | 672.5 | 543.1363 | 675.5 | 3919.9159 | 678.5 | 2.0941 | 681 | 42.0391 | 684 | 16.1089 | 686.5 | 0.92046 | 689.5 | 28.2554 | 692.5 | 12.8873 | 695 | 15.0137 | 698 | 8.1985 | 700.5 | 12.5198 | 644.5 | 0.85761
703.5 | 7.2066 | 706.5 | 0.81477 | 709 | 0.46215 | 712 | 21.1434 | 714.5 | 3.3995 | 717.5 | 29.8842 | 720.5 | 0.86146 | 723 | 29.1072 | 726 | 8.5853 | 728.5 | 1.5996 | 731.5 | 17.5536 | 734.5 | 0.90665 | 737 | 14.2442 | 740 | 3.4161 | 742.5 | 1.3132 | 745.5 | 25.2764 | 748.5 | 8.0854 | 751 | 21.0882 | 754 | 10.1945 | 756.5 | 13.442 | 759.5 | 22.9975 | 703.5 | 0.46215
762.5 | 1.1689 | 765 | 27.7757 | 768 | 9.7209 | 770.5 | 0.90233 | 773.5 | 6.7942 | 776.5 | 7.8232 | 779 | 7.6993 | 782 | 0.69573 | 784.5 | 1.7367 | 787.5 | 5.6328 | 790.5 | 0.87803 | 792 | 15.4923 | 796 | 0.617 | 798.5 | 17.3284 | 801.5 | 11.5319 | 804.5 | 32.297 | 807 | 9.5163 | 810 | 3.0332 | 812.5 | 19.8509 | 815.5 | 23.5645 | 818.5 | 28.0133 | 762.5 | 0.617
821 | 19.6356 | 824 | 20.6593 | 826.5 | 18.5316 | 829.5 | 30.8623 | 832.5 | 10.8535 | 835 | 32.6911 | 838 | 23.9462 | 840.5 | 14.8744 | 843.5 | 20.0524 | 846.5 | 2404.1908 | 849 | 29.2776 | 852 | 7419.3856 | 854.5 | 22.3432 | 857.5 | 4.743 | 860.5 | 14.2458 | 863 | 33.4948 | 866 | 11.9336 | 868.5 | 28.8125 | 871.5 | 3.9174 | 874.5 | 0.68295 | 877 | 17.5052 | 821 | 0.68295
880 | 5.9171 | 882.5 | 18.4979 | 885.5 | 427.731 | 888.5 | 3955.4481 | 891 | 7476.9163 | 894 | 1817.7432 | 896.5 | 7.8473 | 899.5 | 120.6445 | 902.5 | 68.1505 | 905 | 22.1517 | 908 | 6.4042 | 910.5 | 24.74 | 913.5 | 0.78717 | 916.5 | 20.0049 | 919 | 9.2753 | 922 | 21.7928 | 924.5 | 0.85757 | 927.5 | 27.1391 | 930.5 | 18.2517 | 933 | 30.7268 | 936 | 31.1212 | 880 | 0.78717
938.5 | 13.5591 | 941.5 | 6.6003 | 944.5 | 12.5137 | 947 | 6.4792 | 950 | 16.0805 | 952.5 | 17.8632 | 955.5 | 2.9883 | 958.5 | 11.4373 | 961 | 9.0186 | 964 | 28.2748 | 966.5 | 12.6152 | 969.5 | 18.7644 | 972.5 | 16.8646 | 975 | 15.9513 | 978 | 2.9609 | 980.5 | 24.5892 | 983.5 | 154.8239 | 986.5 | 29.9061 | 989 | 18.6476 | 992 | 7.8686 | 994.5 | 0.9032 | 938.5 | 0.9032
997.5 | 22.2819 | 1000.5 | 0.77281 | 1003 | 30.5045 | 1006 | 2.4249 | 1008.5 | 2.2852 | 1011.5 | 23.9877 | 1014.5 | 0.90147 | 1017 | 11.7415 | 1020 | 8.1076 | 1022.5 | 32.0488 | 1025.5 | 0.30447 | 1028.5 | 0.19074 | 1031 | 20.4625 | 1034 | 7.5914 | 1036.5 | 2.3211 | 1039.5 | 24.0939 | 1042.5 | 7.4299 | 1045 | 21.0281 | 1048 | 20.6077 | 1050.5 | 4.5404 | 1053.5 | 26.3836 | 997.5 | 0.19074

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 20 |  |  | 2006-07-12 | 11:44
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums Overall
-53.75 | 490376 |  | -42.1667 | 504776 | -34.1667 | 484176 | -29.0833 | 502976 | -25.8333 | 484176 | -23.5 | 510576 | -21 | 502976 | -53.75 | 484176
5 | 490376 |  | 16.6667 | 504776 | 24.75 | 484176 | 29.6667 | 502976 | 33.0833 | 484176 | 35.25 | 510576 | 37.75 | 502976 | 5 | 484176
63.75 | 490376 |  | 75.4167 | 504776 | 83.4167 | 484176 | 88.5 | 502976 | 91.8333 | 484176 | 94.1667 | 510576 | 96.4167 | 502976 | 63.75 | 484176
122.5833 | 490376 |  | 134.25 | 504776 | 142.25 | 484176 | 147.25 | 502976 | 150.5 | 484176 | 153 | 510576 | 155.1667 | 502976 | 122.5833 | 484176
181.4167 | 490376 |  | 193.0833 | 504776 | 201 | 484176 | 206.0833 | 502976 | 209.3333 | 484176 | 211.6667 | 510576 | 214.0833 | 502976 | 181.4167 | 484176
240.1667 | 490376 |  | 251.75 | 255038 | 259.8333 | 484176 | 264.8333 | 502976 | 268.1667 | 484176 | 270.5 | 510576 | 272.75 | 502976 | 240.1667 | 255038
299 | 490376 |  | 310.5833 | 504776 | 318.4167 | 484176 | 323.5833 | 254638 | 327 | 484176 | 329.3333 | 510576 | 331.5833 | 502976 | 299 | 254638
357.6667 | 490376 |  | 369.3333 | 504776 | 377.4167 | 484176 | 382.5 | 502976 | 385.6667 | 484176 | 388.0833 | 510576 | 390.3333 | 502976 | 357.6667 | 484176
416.5833 | 490376 |  | 428.1667 | 504776 | 436.25 | 484176 | 441.25 | 502976 | 444.5 | 484176 | 446.9167 | 510576 | 449.1667 | 502976 | 416.5833 | 484176
475.3333 | 490376 |  | 487 | 504776 | 494.8333 | 484176 | 500.0833 | 502976 | 503.25 | 484176 | 505.5833 | 510576 | 508.0833 | 502976 | 475.3333 | 484176
534.0833 | 490376 |  | 545.75 | 504776 | 553.75 | 484176 | 558.75 | 502976 | 562.0833 | 484176 | 564.5 | 510576 | 566.75 | 502976 | 534.0833 | 484176
592.9167 | 490376 |  | 604.5833 | 504776 | 612.4167 | 586.7472 | 617.5833 | 0.64228 | 621 | 0.64549 | 623.25 | 10.0303 | 625.5833 | 4.5743 | 592.9167 | 0.64228
651.6667 | 0.66092 |  | 663.3333 | 0.68696 | 671.3333 | 3.522 | 676.5 | 0.64059 | 679.6667 | 5.5942 | 682 | 0.72099 | 684.3333 | 1.9128 | 651.6667 | 0.64059
710.5 | 0.67241 |  | 722.1667 | 2.3828 | 730.1667 | 0.64463 | 735.25 | 9.5238 | 738.5 | 1.5671 | 740.8333 | 0.6381 | 743.0833 | 9.2693 | 710.5 | 0.6381
769.3333 | 0.6459 |  | 781 | 0.65311 | 788.6667 | 0.84881 | 793.9167 | 3.7207 | 797.25 | 3.2099 | 799.5833 | 0.63959 | 802.0833 | 12.6458 | 769.3333 | 0.63959
828.0833 | 12.2552 |  | 839.75 | 10.3508 | 847.75 | 6.2112 | 852.75 | 0.64718 | 856.0833 | 0.87627 | 858.5 | 0.64539 | 860.75 | 0.63984 | 828.0833 | 0.63984
886.9167 | 7.3768 |  | 898.5833 | 4.6366 | 906.4167 | 0.68108 | 911.5833 | 0.84809 | 915 | 0.65092 | 917.25 | 7.1586 | 919.5833 | 0.63885 | 886.9167 | 0.63885
945.6667 | 7.923 |  | 957.3333 | 4.4791 | 965.3333 | 2.096 | 970.5 | 5.2342 | 973.6667 | 3.7507 | 976 | 0.64564 | 978.3333 | 0.63735 | 945.6667 | 0.63735
1004.5 | 0.71376 |  | 1016.1667 | 0.64615 | 1024.1667 | 1.7255 | 1029.25 | 2.6648 | 1032.5 | 6.0239 | 1034.8333 | 4.303 | 1037.0833 | 4155.6333 | 1004.5 | 0.64615

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 20 |  |  | 2006-07-12 | 11:44
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-53.75 | 510076 |  | -42.1667 | 510876 | -34.1667 | 503809.3333 | -29.0833 | 511342.6667 | -25.8333 | 507976 | -23.5 | 513642.6667 | -21 | 511109.3333 | -53.75 | 503809.3333
5 | 510076 |  | 16.6667 | 510876 | 24.75 | 503809.3333 | 29.6667 | 511342.6667 | 33.0833 | 507976 | 35.25 | 513642.6667 | 37.75 | 511109.3333 | 5 | 503809.3333
63.75 | 510076 |  | 75.4167 | 510876 | 83.4167 | 503809.3333 | 88.5 | 511342.6667 | 91.8333 | 507976 | 94.1667 | 513642.6667 | 96.4167 | 511109.3333 | 63.75 | 503809.3333
122.5833 | 510076 |  | 134.25 | 510876 | 142.25 | 503809.3333 | 147.25 | 511342.6667 | 150.5 | 507976 | 153 | 513642.6667 | 155.1667 | 511109.3333 | 122.5833 | 503809.3333
181.4167 | 510076 |  | 193.0833 | 510876 | 201 | 503809.3333 | 206.0833 | 511342.6667 | 209.3333 | 507976 | 211.6667 | 513642.6667 | 214.0833 | 511109.3333 | 181.4167 | 503809.3333
240.1667 | 510076 |  | 251.75 | 468353 | 259.8333 | 503809.3333 | 264.8333 | 511342.6667 | 268.1667 | 507976 | 270.5 | 513642.6667 | 272.75 | 511109.3333 | 240.1667 | 468353
299 | 510076 |  | 310.5833 | 510876 | 318.4167 | 503809.3333 | 323.5833 | 468886.3333 | 327 | 507976 | 329.3333 | 513642.6667 | 331.5833 | 511109.3333 | 299 | 468886.3333
357.6667 | 510076 |  | 369.3333 | 510876 | 377.4167 | 503809.3333 | 382.5 | 511342.6667 | 385.6667 | 507976 | 388.0833 | 513642.6667 | 390.3333 | 511109.3333 | 357.6667 | 503809.3333
416.5833 | 510076 |  | 428.1667 | 510876 | 436.25 | 503809.3333 | 441.25 | 511342.6667 | 444.5 | 507976 | 446.9167 | 513642.6667 | 449.1667 | 511109.3333 | 416.5833 | 503809.3333
475.3333 | 510076 |  | 487 | 510876 | 494.8333 | 503809.3333 | 500.0833 | 511342.6667 | 503.25 | 507976 | 505.5833 | 513642.6667 | 508.0833 | 511109.3333 | 475.3333 | 503809.3333
534.0833 | 510076 |  | 545.75 | 510876 | 553.75 | 503809.3333 | 558.75 | 511342.6667 | 562.0833 | 507976 | 564.5 | 513642.6667 | 566.75 | 511109.3333 | 534.0833 | 503809.3333
592.9167 | 510076 |  | 604.5833 | 510876 | 612.4167 | 254455.3341 | 617.5833 | 170859.2029 | 621 | 171758.2383 | 623.25 | 172100.4848 | 625.5833 | 172131.8311 | 592.9167 | 170859.2029
651.6667 | 9.6773 |  | 663.3333 | 618.1153 | 671.3333 | 327.8828 | 676.5 | 18.0459 | 679.6667 | 16.3002 | 682 | 11.9289 | 684.3333 | 20.5533 | 651.6667 | 9.6773
710.5 | 11.621 |  | 722.1667 | 11.8293 | 730.1667 | 14.0331 | 735.25 | 19.286 | 738.5 | 10.7497 | 740.8333 | 19.5577 | 743.0833 | 48.4497 | 710.5 | 10.7497
769.3333 | 10.1544 |  | 781 | 5.0305 | 788.6667 | 14.0828 | 793.9167 | 12.6474 | 797.25 | 20.2528 | 799.5833 | 17.2938 | 802.0833 | 62.1013 | 769.3333 | 5.0305
828.0833 | 23.4714 |  | 839.75 | 21.6601 | 847.75 | 17.9273 | 852.75 | 21.724 | 856.0833 | 10.3856 | 858.5 | 8.9071 | 860.75 | 21.5438 | 828.0833 | 8.9071
886.9167 | 30.5672 |  | 898.5833 | 16.2004 | 906.4167 | 22.5059 | 911.5833 | 15.9289 | 915 | 16.538 | 917.25 | 16.7437 | 919.5833 | 15.9456 | 886.9167 | 15.9289
945.6667 | 13.5554 |  | 957.3333 | 12.6843 | 965.3333 | 12.6289 | 970.5 | 20.795 | 973.6667 | 17.5707 | 976 | 11.4509 | 978.3333 | 2847.7605 | 945.6667 | 11.4509
1004.5 | 14.8223 |  | 1016.1667 | 10.9818 | 1024.1667 | 14.3658 | 1029.25 | 16.2081 | 1032.5 | 15.4555 | 1034.8333 | 16.3592 | 1037.0833 | 6239.2854 | 1004.5 | 10.9818

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -62 | 33.8053 | 30.729 | 30.7386 | 30.6362 | 30.9409 | 29.1617 | 28.6256 | 31.6431
0.681 | -61.319 | 33.8038 | 30.7338 | 30.735 | 30.6347 | 30.9389 | 29.1623 | 28.6253 | 31.6536
1.6824 | -60.3176 | 33.8016 | 30.7357 | 30.735 | 30.6325 | 30.9309 | 29.1609 | 28.6128 | 31.6496
2.6839 | -59.3161 | 33.7944 | 30.7332 | 30.7325 | 30.6373 | 30.9296 | 29.1647 | 28.6169 | 31.6494
3.6853 | -58.3147 | 33.791 | 30.7314 | 30.7368 | 30.6393 | 30.9268 | 29.1601 | 28.604 | 31.6519
4.6867 | -57.3133 | 33.7857 | 30.7263 | 30.7305 | 30.6342 | 30.9342 | 29.1637 | 28.6097 | 31.6305
5.6882 | -56.3118 | 33.7845 | 30.7289 | 30.7427 | 30.6267 | 30.9337 | 29.1684 | 28.6095 | 31.6547
6.6796 | -55.3204 | 33.7888 | 30.7308 | 30.7282 | 30.6338 | 30.9345 | 29.1673 | 28.6136 | 31.6447
7.681 | -54.319 | 33.7803 | 30.7292 | 30.7338 | 30.634 | 30.9291 | 29.1715 | 28.6065 | 31.6414
8.6825 | -53.3175 | 33.7816 | 30.7268 | 30.7312 | 30.6368 | 30.9312 | 29.1668 | 28.6114 | 31.6381
9.6839 | -52.3161 | 33.7827 | 30.732 | 30.737 | 30.6369 | 30.9296 | 29.1596 | 28.6132 | 31.6405
10.6854 | -51.3146 | 33.7758 | 30.7337 | 30.737 | 30.6367 | 30.923 | 29.1542 | 28.6134 | 31.641
11.6868 | -50.3132 | 33.7778 | 30.7312 | 30.7321 | 30.6349 | 30.9292 | 29.1514 | 28.616 | 31.6314
12.6782 | -49.3218 | 33.7706 | 30.7291 | 30.7354 | 30.6417 | 30.9334 | 29.1575 | 28.6177 | 31.634
13.6797 | -48.3203 | 33.7685 | 30.7292 | 30.7381 | 30.6399 | 30.9308 | 29.1647 | 28.6157 | 31.6325
14.6811 | -47.3189 | 33.7636 | 30.7335 | 30.7281 | 30.6405 | 30.9271 | 29.1627 | 28.6198 | 31.6288
15.6825 | -46.3175 | 33.7711 | 30.7261 | 30.735 | 30.642 | 30.9284 | 29.172 | 28.6204 | 31.6313
16.684 | -45.316 | 33.7688 | 30.7315 | 30.7364 | 30.6373 | 30.9304 | 29.1651 | 28.625 | 31.6266
17.6854 | -44.3146 | 33.7651 | 30.726 | 30.7394 | 30.6393 | 30.9306 | 29.1693 | 28.6325 | 31.6471
18.6869 | -43.3131 | 33.7671 | 30.7269 | 30.7375 | 30.6374 | 30.9289 | 29.1688 | 28.6334 | 31.6396
19.6883 | -42.3117 | 33.7624 | 30.7311 | 30.7351 | 30.6414 | 30.9259 | 29.17 | 28.6306 | 31.6366
20.6797 | -41.3203 | 33.7539 | 30.7423 | 30.7338 | 30.6408 | 30.9225 | 29.1675 | 28.6281 | 31.6259
21.6812 | -40.3188 | 33.7537 | 30.7363 | 30.7382 | 30.6405 | 30.9266 | 29.1653 | 28.6339 | 31.6408
22.6826 | -39.3174 | 33.75 | 30.7315 | 30.7407 | 30.6378 | 30.9204 | 29.172 | 28.6298 | 31.6341
23.7441 | -38.2559 | 33.7441 | 30.7307 | 30.7382 | 30.6445 | 30.9285 | 29.1702 | 28.6269 | 31.6166
24.6855 | -37.3145 | 33.7394 | 30.7318 | 30.7431 | 30.6393 | 30.9275 | 29.1704 | 28.6348 | 31.6307
25.6869 | -36.3131 | 33.7414 | 30.7361 | 30.741 | 30.6428 | 30.9254 | 29.1697 | 28.6311 | 31.6265
26.6884 | -35.3116 | 33.7332 | 30.7342 | 30.7441 | 30.6433 | 30.9287 | 29.1707 | 28.629 | 31.6326
27.6798 | -34.3202 | 33.7324 | 30.7246 | 30.7403 | 30.6398 | 30.9266 | 29.1693 | 28.617 | 31.6321
28.6812 | -33.3188 | 33.7236 | 30.7338 | 30.7474 | 30.6422 | 30.9177 | 29.1754 | 28.6147 | 31.6336
29.6827 | -32.3173 | 33.7259 | 30.7338 | 30.7446 | 30.6429 | 30.9304 | 29.1778 | 28.6059 | 31.6298
30.6841 | -31.3159 | 33.7219 | 30.736 | 30.7392 | 30.6403 | 30.9293 | 29.1727 | 28.5985 | 31.62
31.6856 | -30.3144 | 33.7225 | 30.7352 | 30.7282 | 30.6399 | 30.9297 | 29.1807 | 28.6062 | 31.6287
32.687 | -29.313 | 33.7247 | 30.7327 | 30.7414 | 30.6387 | 30.9218 | 29.1784 | 28.6051 | 31.6334
33.6784 | -28.3216 | 33.7192 | 30.7313 | 30.7349 | 30.6425 | 30.9294 | 29.1744 | 28.6073 | 31.6175
34.6899 | -27.3101 | 33.7188 | 30.7281 | 30.7427 | 30.6414 | 30.9306 | 29.1759 | 28.6043 | 31.6305
35.6813 | -26.3187 | 33.7242 | 30.7382 | 30.7424 | 30.6423 | 30.9306 | 29.1761 | 28.6064 | 31.6173
36.6827 | -25.3173 | 33.7263 | 30.7361 | 30.7394 | 30.6459 | 30.9285 | 29.1787 | 28.612 | 31.615
37.6842 | -24.3158 | 33.7223 | 30.7358 | 30.7377 | 30.6421 | 30.9277 | 29.1758 | 28.6028 | 31.6164
38.6856 | -23.3144 | 33.7185 | 30.7396 | 30.7399 | 30.641 | 30.9325 | 29.1712 | 28.6071 | 31.615
39.6871 | -22.3129 | 33.7124 | 30.7364 | 30.7449 | 30.6425 | 30.9295 | 29.1623 | 28.6006 | 31.6177
40.6885 | -21.3115 | 33.7131 | 30.735 | 30.746 | 30.6478 | 30.9304 | 29.1705 | 28.6034 | 31.6221
41.6799 | -20.3201 | 33.715 | 30.7369 | 30.7451 | 30.646 | 30.934 | 29.1658 | 28.6083 | 31.6296
42.6814 | -19.3186 | 33.7084 | 30.733 | 30.7452 | 30.6482 | 30.9366 | 29.1676 | 28.6101 | 31.6142
43.6828 | -18.3172 | 33.7046 | 30.7417 | 30.7481 | 30.6409 | 30.9325 | 29.1693 | 28.6052 | 31.6152
44.6843 | -17.3157 | 33.6923 | 30.739 | 30.751 | 30.6486 | 30.9366 | 29.1699 | 28.6025 | 31.6128
45.6857 | -16.3143 | 33.6973 | 30.7316 | 30.752 | 30.6404 | 30.9287 | 29.1643 | 28.5981 | 31.6145
46.6871 | -15.3129 | 33.6951 | 30.7345 | 30.7528 | 30.6466 | 30.9254 | 29.1651 | 28.5934 | 31.615
47.6886 | -14.3114 | 33.6915 | 30.7314 | 30.7472 | 30.6497 | 30.9287 | 29.1627 | 28.5911 | 31.6113
48.68 | -13.32 | 33.6987 | 30.7305 | 30.7451 | 30.65 | 30.9281 | 29.1656 | 28.5801 | 31.6144
49.6814 | -12.3186 | 33.6967 | 30.7384 | 30.7415 | 30.6504 | 30.9327 | 29.166 | 28.5842 | 31.6206
50.6829 | -11.3171 | 33.6939 | 30.733 | 30.7511 | 30.6463 | 30.9324 | 29.1693 | 28.5903 | 31.6011
51.6843 | -10.3157 | 33.6923 | 30.737 | 30.7447 | 30.6498 | 30.934 | 29.1657 | 28.5875 | 31.5964
52.6858 | -9.3142 | 33.6928 | 30.7353 | 30.7398 | 30.6472 | 30.9298 | 29.1749 | 28.5924 | 31.6062
53.6872 | -8.3128 | 33.6965 | 30.7394 | 30.7462 | 30.6443 | 30.9327 | 29.1707 | 28.5925 | 31.607
54.6786 | -7.3214 | 33.6977 | 30.7393 | 30.745 | 30.6508 | 30.9315 | 29.1775 | 28.5997 | 31.6034
55.6801 | -6.3199 | 33.694 | 30.735 | 30.7476 | 30.6523 | 30.9368 | 29.1794 | 28.6024 | 31.6047
56.6815 | -5.3185 | 33.6922 | 30.7345 | 30.7444 | 30.6469 | 30.9314 | 29.1722 | 28.6003 | 31.6052
57.6829 | -4.3171 | 33.6913 | 30.7351 | 30.7419 | 30.6488 | 30.9319 | 29.1732 | 28.6023 | 31.6121
58.6844 | -3.3156 | 33.6904 | 30.736 | 30.7529 | 30.6486 | 30.9335 | 29.18 | 28.5982 | 31.6078
59.6858 | -2.3142 | 33.6844 | 30.6521 | 30.7277 | 30.6119 | 31.0305 | 29.2266 | 28.5959 | 31.574
60.6873 | -1.3127 | 33.6788 | 30.7017 | 30.7524 | 30.6349 | 30.9864 | 29.192 | 28.6067 | 31.5921
61.6787 | -0.3213 | 33.7382 | 30.708 | 30.7568 | 30.6417 | 30.9938 | 29.1891 | 28.6076 | 31.6012
62.6801 | 0.6801 | 34.1465 | 30.7148 | 30.7545 | 30.6417 | 30.9953 | 29.1959 | 28.6067 | 31.5998
63.6816 | 1.6816 | 35.1332 | 30.7145 | 30.7502 | 30.649 | 30.9722 | 29.1975 | 28.6118 | 31.5969
64.693 | 2.693 | 36.729 | 30.7112 | 30.7535 | 30.6461 | 30.9863 | 29.2147 | 28.6172 | 31.6122
65.6844 | 3.6844 | 38.8179 | 30.7221 | 30.7543 | 30.6514 | 30.98 | 29.2362 | 28.6413 | 31.6196
66.6859 | 4.6859 | 41.3748 | 30.7204 | 30.7526 | 30.6483 | 30.9725 | 29.2658 | 28.6792 | 31.6409
67.6873 | 5.6873 | 44.2967 | 30.7246 | 30.7477 | 30.6506 | 30.9753 | 29.3049 | 28.7362 | 31.6557
68.6888 | 6.6888 | 47.5759 | 30.7277 | 30.7508 | 30.6545 | 30.9723 | 29.3543 | 28.7899 | 31.6703
69.6802 | 7.6802 | 51.0941 | 30.7404 | 30.753 | 30.656 | 30.9896 | 29.4192 | 28.8578 | 31.716
70.6816 | 8.6816 | 54.8368 | 30.7444 | 30.7591 | 30.6563 | 30.9894 | 29.4815 | 28.9374 | 31.7439
71.6831 | 9.6831 | 58.8125 | 30.7598 | 30.7478 | 30.6602 | 31.0067 | 29.5575 | 29.0209 | 31.7924
72.6845 | 10.6845 | 62.9889 | 30.7702 | 30.7571 | 30.6556 | 31.0204 | 29.6524 | 29.1163 | 31.8279
73.686 | 11.686 | 67.3522 | 30.7825 | 30.7529 | 30.6575 | 31.0418 | 29.7535 | 29.234 | 31.8986
74.6874 | 12.6874 | 71.8618 | 30.8013 | 30.7578 | 30.6608 | 31.066 | 29.8786 | 29.3651 | 31.9584
75.6788 | 13.6788 | 76.4869 | 30.8173 | 30.7638 | 30.6604 | 31.0781 | 30.0259 | 29.5004 | 32.0291
76.6903 | 14.6903 | 81.2275 | 30.8475 | 30.7657 | 30.6633 | 31.1105 | 30.1687 | 29.6727 | 32.1068
77.6817 | 15.6817 | 86.0589 | 30.878 | 30.7643 | 30.6673 | 31.1612 | 30.361 | 29.8479 | 32.1856
78.6831 | 16.6831 | 90.9946 | 30.9108 | 30.7708 | 30.673 | 31.186 | 30.5197 | 30.0573 | 32.2904
79.6846 | 17.6846 | 96.0204 | 30.9527 | 30.7772 | 30.6762 | 31.2401 | 30.7088 | 30.2821 | 32.3888
80.686 | 18.686 | 101.1321 | 30.9938 | 30.7795 | 30.6823 | 31.2956 | 30.9146 | 30.5412 | 32.5194
81.6875 | 19.6875 | 106.3477 | 31.0402 | 30.7806 | 30.6879 | 31.3507 | 31.1492 | 30.7606 | 32.6387
82.6889 | 20.6889 | 111.617 | 31.0931 | 30.7952 | 30.6931 | 31.4305 | 31.4061 | 31.032 | 32.774
83.6803 | 21.6803 | 116.9652 | 31.1512 | 30.8036 | 30.7028 | 31.5011 | 31.7082 | 31.3315 | 32.93
84.6818 | 22.6818 | 122.4038 | 31.2189 | 30.8126 | 30.7095 | 31.5789 | 32.1045 | 31.6536 | 33.0892
85.6832 | 23.6832 | 127.8001 | 31.2938 | 30.8236 | 30.721 | 31.672 | 32.4163 | 32.0009 | 33.2774
86.6846 | 24.6846 | 133.213 | 31.3733 | 30.8364 | 30.7349 | 31.7609 | 32.7445 | 32.3699 | 33.4467
87.6861 | 25.6861 | 138.6496 | 31.4681 | 30.8462 | 30.737 | 31.8683 | 33.1347 | 32.7511 | 33.665
88.6875 | 26.6875 | 144.1553 | 31.5648 | 30.8707 | 30.7546 | 31.981 | 33.497 | 33.1171 | 33.8807
89.679 | 27.679 | 149.6647 | 31.6722 | 30.8868 | 30.7806 | 32.102 | 33.9562 | 33.5399 | 34.1232
90.6804 | 28.6804 | 155.1714 | 31.7838 | 30.9056 | 30.7926 | 32.2264 | 34.3551 | 33.9588 | 34.3733
91.6818 | 29.6818 | 160.7384 | 31.9104 | 30.9299 | 30.8116 | 32.3647 | 34.8281 | 34.4157 | 34.6466
92.6833 | 30.6833 | 166.3152 | 32.0333 | 30.9489 | 30.8324 | 32.5124 | 35.312 | 34.8392 | 34.9428
93.6847 | 31.6847 | 171.8407 | 32.1683 | 30.9825 | 30.855 | 32.6686 | 35.7336 | 35.3276 | 35.2519
94.6862 | 32.6862 | 177.317 | 32.3197 | 31.0024 | 30.8843 | 32.8362 | 36.2873 | 35.8645 | 35.5761
95.6876 | 33.6876 | 182.7825 | 32.4795 | 31.0349 | 30.9076 | 33.0133 | 36.7665 | 36.4114 | 35.9141
96.679 | 34.679 | 188.2627 | 32.6401 | 31.0717 | 30.9432 | 33.2061 | 37.2777 | 36.8707 | 36.261
97.6805 | 35.6805 | 193.732 | 32.8163 | 31.1066 | 30.983 | 33.4081 | 37.8191 | 37.4763 | 36.6451
98.6819 | 36.6819 | 199.202 | 33.0008 | 31.1476 | 31.0133 | 33.6177 | 38.3072 | 38.0724 | 37.0467
99.6833 | 37.6833 | 204.7359 | 33.1938 | 31.2011 | 31.0538 | 33.8259 | 38.8702 | 38.6598 | 37.4669
100.6848 | 38.6848 | 210.2342 | 33.4055 | 31.2439 | 31.1023 | 34.0846 | 39.4676 | 39.2953 | 37.9034
101.6862 | 39.6862 | 215.6034 | 33.6201 | 31.2774 | 31.1539 | 34.3229 | 40.1291 | 39.9346 | 38.3585
102.6877 | 40.6877 | 221.0727 | 33.842 | 31.3343 | 31.1991 | 34.5857 | 40.8175 | 40.5758 | 38.8431
103.6891 | 41.6891 | 226.5232 | 34.0858 | 31.3967 | 31.2551 | 34.872 | 41.4756 | 41.2615 | 39.3548
104.6805 | 42.6805 | 231.9499 | 34.3425 | 31.455 | 31.3141 | 35.1487 | 42.1642 | 41.9861 | 39.865
105.682 | 43.682 | 237.4025 | 34.6012 | 31.5181 | 31.3653 | 35.4421 | 42.8537 | 42.7752 | 40.4448
106.6834 | 44.6834 | 242.9138 | 34.8855 | 31.6043 | 31.4477 | 35.7421 | 43.6508 | 43.5506 | 41.0264
107.6848 | 45.6848 | 248.3989 | 35.1685 | 31.6759 | 31.5118 | 36.0639 | 44.4776 | 44.504 | 41.6694
108.6863 | 46.6863 | 253.9466 | 35.4712 | 31.7502 | 31.5892 | 36.3977 | 45.1631 | 45.2394 | 42.314
109.6877 | 47.6877 | 259.5097 | 35.7822 | 31.8314 | 31.6633 | 36.7393 | 46.006 | 46.0129 | 42.9851
110.6791 | 48.6791 | 264.9557 | 36.0989 | 31.9324 | 31.7569 | 37.1115 | 46.9027 | 46.852 | 43.6638
111.6806 | 49.6806 | 270.3111 | 36.4419 | 32.025 | 31.8429 | 37.4825 | 47.7998 | 47.7681 | 44.3849
112.682 | 50.682 | 275.6716 | 36.7883 | 32.1228 | 31.9433 | 37.8757 | 48.66 | 48.6985 | 45.1244
113.6835 | 51.6835 | 281.035 | 37.1449 | 32.2234 | 32.0345 | 38.2935 | 49.5922 | 49.5963 | 45.8977
114.6849 | 52.6849 | 286.4099 | 37.5052 | 32.3405 | 32.1422 | 38.7181 | 50.5293 | 50.5371 | 46.6886
115.6863 | 53.6863 | 291.7534 | 37.901 | 32.4591 | 32.259 | 39.1613 | 51.523 | 51.5419 | 47.514
116.6878 | 54.6878 | 297.0127 | 38.289 | 32.5803 | 32.3732 | 39.6248 | 52.514 | 52.5963 | 48.3443
117.6792 | 55.6792 | 302.2356 | 38.7079 | 32.7037 | 32.5039 | 40.107 | 53.5512 | 53.7269 | 49.2433
118.6807 | 56.6807 | 307.4912 | 39.1434 | 32.8406 | 32.6354 | 40.5883 | 54.6053 | 54.7369 | 50.1606
119.6821 | 57.6821 | 312.8308 | 39.5814 | 32.9919 | 32.7734 | 41.0903 | 55.6359 | 55.7972 | 51.102
120.6835 | 58.6835 | 318.075 | 40.0279 | 33.1358 | 32.9053 | 41.6069 | 56.6758 | 56.8653 | 52.0716
121.685 | 59.685 | 323.4958 | 40.4989 | 33.2789 | 33.064 | 42.1371 | 57.9087 | 58.0929 | 53.083
122.6864 | 60.6864 | 328.7843 | 40.9734 | 33.4504 | 33.2181 | 42.6814 | 59.1243 | 59.2295 | 54.1247
123.6879 | 61.6879 | 334.0331 | 41.4711 | 33.6213 | 33.3779 | 43.262 | 60.2191 | 60.3255 | 55.1883
124.6893 | 62.6893 | 339.2288 | 41.9827 | 33.7959 | 33.5449 | 43.8396 | 61.3791 | 61.5478 | 56.3263
125.6807 | 63.6807 | 344.2634 | 42.5109 | 33.9699 | 33.7258 | 44.428 | 62.6895 | 62.7371 | 57.4763
126.6822 | 64.6822 | 349.2693 | 43.0471 | 34.1662 | 33.9151 | 45.0585 | 63.9198 | 64.1956 | 58.6492
127.6836 | 65.6836 | 354.4733 | 43.6062 | 34.3762 | 34.111 | 45.69 | 65.1951 | 65.3838 | 59.8757
128.685 | 66.685 | 359.6272 | 44.1667 | 34.5852 | 34.3129 | 46.3582 | 66.4773 | 66.7245 | 61.1176
129.6865 | 67.6865 | 364.7999 | 44.7482 | 34.7954 | 34.5257 | 47.0264 | 67.8149 | 68.155 | 62.4057
130.6779 | 68.6779 | 369.8122 | 45.3414 | 35.0223 | 34.7477 | 47.7133 | 69.1922 | 69.4946 | 63.7182
131.6793 | 69.6793 | 374.697 | 45.9482 | 35.2591 | 34.9722 | 48.4544 | 70.6159 | 70.9556 | 65.0796
132.6808 | 70.6808 | 379.7075 | 46.5692 | 35.5045 | 35.2026 | 49.1989 | 72.0814 | 72.4246 | 66.4801
133.6822 | 71.6822 | 384.9797 | 47.2047 | 35.7413 | 35.4508 | 49.9719 | 73.6539 | 73.9834 | 67.9092
134.6837 | 72.6837 | 390.0552 | 47.8435 | 36.0021 | 35.692 | 50.7616 | 75.1829 | 75.4338 | 69.3827
135.6851 | 73.6851 | 394.9601 | 48.5091 | 36.2645 | 35.9561 | 51.575 | 76.6334 | 76.9794 | 70.8853
136.6865 | 74.6865 | 399.8379 | 49.2042 | 36.5426 | 36.2301 | 52.4235 | 78.1695 | 78.5741 | 72.4595
137.678 | 75.678 | 404.6817 | 49.8979 | 36.8222 | 36.5121 | 53.2789 | 79.761 | 80.2042 | 74.0542
138.6794 | 76.6794 | 409.4007 | 50.6138 | 37.121 | 36.8007 | 54.1895 | 81.2785 | 81.8324 | 75.7101
139.6809 | 77.6809 | 414.1179 | 51.3467 | 37.4198 | 37.1024 | 55.1048 | 82.8325 | 83.4692 | 77.4063
140.6823 | 78.6823 | 418.6798 | 52.0907 | 37.7382 | 37.4029 | 56.0526 | 84.5485 | 85.1856 | 79.1661
141.6837 | 79.6837 | 423.2994 | 52.8537 | 38.0511 | 37.7252 | 57.051 | 86.2001 | 86.7871 | 80.9582
142.6852 | 80.6852 | 428.0698 | 53.6526 | 38.3769 | 38.045 | 58.0603 | 87.9334 | 88.4952 | 82.7883
143.6866 | 81.6866 | 432.7212 | 54.4573 | 38.7304 | 38.3821 | 59.1246 | 89.589 | 90.3042 | 84.6455
144.6881 | 82.6881 | 437.3371 | 55.2522 | 39.0833 | 38.7062 | 60.2229 | 91.3386 | 91.9965 | 86.558
145.6795 | 83.6795 | 442.0009 | 56.1034 | 39.4404 | 39.0593 | 61.3194 | 93.1362 | 93.848 | 88.489
146.6809 | 84.6809 | 446.3036 | 56.9746 | 39.8195 | 39.4307 | 62.4413 | 94.9067 | 95.6483 | 90.4814
147.6824 | 85.6824 | 449.9331 | 57.8621 | 40.1959 | 39.7975 | 63.6028 | 96.6114 | 97.4554 | 92.4848
148.6838 | 86.6838 | 453.3954 | 58.7741 | 40.5887 | 40.1809 | 64.7816 | 98.3984 | 99.2959 | 94.5061
149.6852 | 87.6852 | 456.6669 | 59.6783 | 40.9919 | 40.5672 | 65.9957 | 100.2813 | 101.1098 | 96.5504
150.6867 | 88.6867 | 459.5999 | 60.6134 | 41.3951 | 40.9778 | 67.2192 | 102.0603 | 102.9552 | 98.6215
151.6781 | 89.6781 | 462.3201 | 61.5736 | 41.8198 | 41.3947 | 68.4557 | 103.8305 | 104.7433 | 100.7127
152.6795 | 90.6795 | 464.9906 | 62.5271 | 42.2602 | 41.8117 | 69.7115 | 105.6382 | 106.491 | 102.832
153.681 | 91.681 | 467.5737 | 63.4817 | 42.6935 | 42.2392 | 71.0338 | 107.4138 | 108.2169 | 104.9641
154.6824 | 92.6824 | 470.1188 | 64.448 | 43.1544 | 42.6775 | 72.3269 | 109.1867 | 109.9407 | 107.1314
155.6839 | 93.6839 | 472.5234 | 65.4464 | 43.5961 | 43.133 | 73.5969 | 110.9923 | 111.7267 | 109.313
156.6853 | 94.6853 | 474.8298 | 66.4685 | 44.073 | 43.608 | 74.8945 | 112.7399 | 113.4574 | 111.5137
157.6867 | 95.6867 | 476.9472 | 67.4725 | 44.5517 | 44.0892 | 76.2232 | 114.5329 | 115.2 | 113.7222
158.6782 | 96.6782 | 478.7186 | 68.4741 | 45.036 | 44.5637 | 77.5606 | 116.2607 | 116.922 | 115.9478
159.6796 | 97.6796 | 480.2931 | 69.4807 | 45.5533 | 45.0554 | 78.9048 | 117.9753 | 118.6781 | 118.1553
160.681 | 98.681 | 481.4964 | 70.494 | 46.0631 | 45.5636 | 80.2664 | 119.7529 | 120.38 | 120.3912
161.6825 | 99.6825 | 482.4399 | 71.496 | 46.5855 | 46.08 | 81.6434 | 121.4938 | 122.0129 | 122.6047
162.6839 | 100.6839 | 483.2117 | 72.4825 | 47.1147 | 46.5975 | 83.0011 | 123.2454 | 123.6535 | 124.8412
163.6854 | 101.6854 | 483.7563 | 73.4663 | 47.6431 | 47.1275 | 84.3897 | 124.8947 | 125.3095 | 127.0339
164.6868 | 102.6868 | 484.1598 | 74.4489 | 48.1872 | 47.6635 | 85.7974 | 126.445 | 126.8633 | 129.2749
165.6882 | 103.6882 | 484.3562 | 75.452 | 48.7329 | 48.2129 | 87.1564 | 128.0138 | 128.4327 | 131.4962
166.6797 | 104.6797 | 484.5092 | 76.428 | 49.3075 | 48.7835 | 88.5316 | 129.5165 | 129.9714 | 133.7048
167.6811 | 105.6811 | 484.616 | 77.3962 | 49.8777 | 49.3456 | 89.9092 | 131.073 | 131.382 | 135.888
168.6826 | 106.6826 | 484.699 | 78.3448 | 50.4553 | 49.9197 | 91.2698 | 132.4955 | 132.8208 | 138.0603
169.684 | 107.684 | 484.611 | 79.27 | 51.0363 | 50.502 | 92.6458 | 133.9918 | 134.2008 | 140.2192
170.6854 | 108.6854 | 484.3631 | 80.1928 | 51.6307 | 51.0909 | 94.0231 | 135.3916 | 135.5944 | 142.3539
171.6869 | 109.6869 | 484.0113 | 81.1169 | 52.2337 | 51.6934 | 95.3676 | 136.7637 | 136.9215 | 144.4819
172.6783 | 110.6783 | 483.7509 | 82.0139 | 52.8403 | 52.3011 | 96.755 | 138.1376 | 138.2411 | 146.5957
173.6797 | 111.6797 | 483.4235 | 82.9002 | 53.4636 | 52.9168 | 98.1183 | 139.4873 | 139.5252 | 148.6806
174.6812 | 112.6812 | 482.9981 | 83.7559 | 54.1017 | 53.5419 | 99.5149 | 140.8293 | 140.7521 | 150.7708
175.6826 | 113.6826 | 482.5237 | 84.6172 | 54.7374 | 54.1767 | 100.8891 | 142.1481 | 141.9913 | 152.8361
176.6841 | 114.6841 | 482.0563 | 85.4663 | 55.3849 | 54.8177 | 102.2672 | 143.5836 | 143.1394 | 154.9198
177.6855 | 115.6855 | 481.5365 | 86.3121 | 56.0296 | 55.4638 | 103.6229 | 144.7661 | 144.4681 | 156.9515
178.6869 | 116.6869 | 480.9169 | 87.1217 | 56.6825 | 56.1245 | 104.9866 | 146.0051 | 145.4623 | 158.994
179.6784 | 117.6784 | 480.6003 | 87.917 | 57.3481 | 56.7799 | 106.3599 | 147.2226 | 146.5224 | 161.0204
180.6798 | 118.6798 | 480.2814 | 88.7178 | 58.0187 | 57.4457 | 107.7056 | 148.3597 | 147.6107 | 163.0228
181.6812 | 119.6812 | 479.7269 | 89.5066 | 58.7025 | 58.1317 | 109.056 | 149.5372 | 148.6699 | 165.0256
182.6827 | 120.6827 | 479.2694 | 90.2988 | 59.3912 | 58.8109 | 110.3788 | 150.7374 | 149.6996 | 167.034
183.6841 | 121.6841 | 478.9133 | 91.0789 | 60.0906 | 59.5029 | 111.7111 | 151.8242 | 150.6872 | 169.0164
184.6856 | 122.6856 | 478.4717 | 91.8464 | 60.7808 | 60.193 | 113.0217 | 153.0044 | 151.6493 | 170.9786
185.687 | 123.687 | 478.1218 | 92.6012 | 61.4724 | 60.8932 | 114.3493 | 154.1585 | 152.6079 | 172.9433
186.6784 | 124.6784 | 477.9806 | 93.3499 | 62.192 | 61.608 | 115.6717 | 155.2809 | 153.5612 | 174.903
187.6799 | 125.6799 | 477.8343 | 94.0914 | 62.9022 | 62.3165 | 116.9656 | 156.3454 | 154.5268 | 176.8408
188.6813 | 126.6813 | 477.6858 | 94.8244 | 63.6221 | 63.0304 | 118.2623 | 157.4379 | 155.4534 | 178.7498
189.6828 | 127.6828 | 477.6937 | 95.5536 | 64.348 | 63.757 | 119.546 | 158.6388 | 156.3838 | 180.6863
190.6842 | 128.6842 | 477.6864 | 96.28 | 65.0803 | 64.4839 | 120.8261 | 159.7628 | 157.2692 | 182.5951
191.6856 | 129.6856 | 477.8215 | 97.0022 | 65.8166 | 65.2249 | 122.1014 | 160.8761 | 158.1892 | 184.4815
192.6871 | 130.6871 | 477.9991 | 97.699 | 66.5588 | 65.9652 | 123.3721 | 162.0667 | 159.0922 | 186.3902
193.6785 | 131.6785 | 478.0059 | 98.4045 | 67.3008 | 66.7037 | 124.6248 | 163.0601 | 160.0263 | 188.2628
194.6799 | 132.6799 | 478.0275 | 99.0959 | 68.0536 | 67.4625 | 125.8686 | 164.091 | 160.8963 | 190.1167
195.6814 | 133.6814 | 478.1256 | 99.7701 | 68.8059 | 68.2181 | 127.1249 | 165.1511 | 161.8108 | 191.9801
196.6828 | 134.6828 | 478.2043 | 100.4544 | 69.5608 | 68.9799 | 128.3712 | 166.1611 | 162.6946 | 193.8346
197.6843 | 135.6843 | 478.3196 | 101.1335 | 70.3131 | 69.7477 | 129.5974 | 167.104 | 163.6017 | 195.682
198.6857 | 136.6857 | 478.4331 | 101.805 | 71.0672 | 70.5172 | 130.8209 | 168.2565 | 164.4493 | 197.5116
199.6871 | 137.6871 | 478.3855 | 102.4758 | 71.8345 | 71.2839 | 132.0262 | 169.2404 | 165.3671 | 199.3144
200.6786 | 138.6786 | 478.4176 | 103.1153 | 72.5832 | 72.0592 | 133.2411 | 170.4037 | 166.2225 | 201.1274
201.68 | 139.68 | 478.543 | 103.7607 | 73.3556 | 72.8396 | 134.4591 | 171.5373 | 167.105 | 202.9285
202.6814 | 140.6814 | 478.7673 | 104.417 | 74.1159 | 73.6181 | 135.6456 | 172.5811 | 167.9116 | 204.7158
203.7129 | 141.7129 | 479.0393 | 105.0897 | 74.8982 | 74.41 | 136.8463 | 173.6157 | 168.7419 | 206.5318
204.6843 | 142.6843 | 479.084 | 105.7279 | 75.6421 | 75.172 | 138.0102 | 174.6502 | 169.553 | 208.2287
205.6858 | 143.6858 | 479.1353 | 106.3867 | 76.4074 | 75.949 | 139.1796 | 175.6739 | 170.3897 | 209.9842
206.6872 | 144.6872 | 479.147 | 107.0469 | 77.1777 | 76.7164 | 140.3348 | 176.6844 | 171.219 | 211.73
207.6886 | 145.6886 | 479.4382 | 107.7581 | 77.9451 | 77.5167 | 141.4463 | 177.6332 | 172.0331 | 213.4522
208.6801 | 146.6801 | 479.5999 | 108.4305 | 78.7228 | 78.2898 | 142.5887 | 178.5659 | 172.8575 | 215.1817
209.6815 | 147.6815 | 479.8389 | 109.1116 | 79.4882 | 79.06 | 143.7145 | 179.5209 | 173.6964 | 216.8757
210.6829 | 148.6829 | 480.055 | 109.8052 | 80.2417 | 79.8227 | 144.8473 | 180.5302 | 174.4755 | 218.5628
211.6844 | 149.6844 | 480.2323 | 110.503 | 81.013 | 80.5916 | 145.9688 | 181.3994 | 175.275 | 220.2536
212.6858 | 150.6858 | 480.5724 | 111.1829 | 81.7641 | 81.347 | 147.0978 | 182.556 | 176.1035 | 221.9068
213.6873 | 151.6873 | 480.694 | 111.8804 | 82.5502 | 82.1101 | 148.2152 | 183.5307 | 176.9108 | 223.5821
214.6787 | 152.6787 | 480.7187 | 112.5958 | 83.3096 | 82.8683 | 149.3025 | 184.5064 | 177.7613 | 225.208
215.7102 | 153.7102 | 480.7986 | 113.3335 | 84.1015 | 83.6658 | 150.4195 | 185.5296 | 178.614 | 226.9057
216.6816 | 154.6816 | 480.7504 | 114.0353 | 84.85 | 84.4047 | 151.4706 | 186.5093 | 179.4105 | 228.485
217.683 | 155.683 | 480.6618 | 114.7782 | 85.6153 | 85.1742 | 152.5262 | 187.4447 | 180.2576 | 230.0879
218.6845 | 156.6845 | 480.7097 | 115.4985 | 86.3779 | 85.943 | 153.59 | 188.3776 | 181.0642 | 231.6843
219.6859 | 157.6859 | 480.7049 | 116.2343 | 87.1808 | 86.7361 | 154.668 | 189.3168 | 181.9077 | 233.2977
220.6873 | 158.6873 | 480.6754 | 116.9874 | 87.9582 | 87.5254 | 155.69 | 190.1569 | 182.679 | 234.8676
221.6788 | 159.6788 | 480.7568 | 117.722 | 88.7542 | 88.3213 | 156.7728 | 191.1719 | 183.5069 | 236.4537
222.6802 | 160.6802 | 480.831 | 118.4677 | 89.5661 | 89.1124 | 157.8175 | 192.107 | 184.32 | 238.0071
223.6816 | 161.6816 | 480.8404 | 119.2388 | 90.3802 | 89.9375 | 158.8699 | 192.9384 | 185.191 | 239.5371
224.6831 | 162.6831 | 480.8377 | 120.0104 | 91.2215 | 90.7694 | 159.8887 | 193.7478 | 186.015 | 241.0292
225.6845 | 163.6845 | 480.8497 | 120.7956 | 92.079 | 91.6168 | 160.9104 | 194.5563 | 186.8023 | 242.5192
226.686 | 164.686 | 480.9422 | 121.5863 | 92.9427 | 92.4832 | 161.9342 | 195.4151 | 187.5902 | 243.9936
227.6874 | 165.6874 | 481.0639 | 122.3752 | 93.8152 | 93.3539 | 162.9549 | 196.2687 | 188.4073 | 245.4689
228.6888 | 166.6888 | 481.0872 | 123.1881 | 94.6931 | 94.2369 | 163.9728 | 196.9065 | 189.2746 | 246.92
229.6803 | 167.6803 | 481.1779 | 124.0114 | 95.5732 | 95.1231 | 164.9501 | 197.7971 | 190.1656 | 248.3824
230.6817 | 168.6817 | 481.2481 | 124.8331 | 96.4428 | 96.0188 | 165.9579 | 198.6189 | 190.9954 | 249.8234
231.6831 | 169.6831 | 481.1649 | 125.651 | 97.3197 | 96.91 | 166.9803 | 199.4412 | 191.8307 | 251.2799
232.6846 | 170.6846 | 481.119 | 126.4704 | 98.1463 | 97.8015 | 167.9987 | 200.2232 | 192.6079 | 252.713
233.686 | 171.686 | 481.0764 | 127.2941 | 99.0364 | 98.7039 | 169.0567 | 200.8799 | 193.2778 | 254.1163
234.6875 | 172.6875 | 481.1296 | 128.1227 | 99.8969 | 99.6148 | 170.1387 | 201.5251 | 194.1816 | 255.5239
235.6789 | 173.6789 | 481.2643 | 128.9674 | 100.7827 | 100.5425 | 171.24 | 202.2248 | 195.1161 | 256.9111
236.6803 | 174.6803 | 481.3511 | 129.8028 | 101.6631 | 101.478 | 172.3794 | 202.9325 | 195.9664 | 258.3088
237.6818 | 175.6818 | 481.3337 | 130.6344 | 102.5677 | 102.4277 | 173.5533 | 203.4733 | 196.8101 | 259.6513
238.6832 | 176.6832 | 481.2052 | 131.4876 | 103.4801 | 103.3835 | 174.7696 | 204.053 | 197.6456 | 260.9903
239.6846 | 177.6846 | 481.1956 | 132.3153 | 104.4118 | 104.339 | 176.0072 | 204.5523 | 198.4588 | 262.3152
240.6861 | 178.6861 | 481.1356 | 133.1546 | 105.37 | 105.3196 | 177.225 | 205.1126 | 199.3183 | 263.6171
241.6875 | 179.6875 | 481.2123 | 134.0068 | 106.3411 | 106.2913 | 178.4629 | 205.6704 | 200.0817 | 264.9309
242.679 | 180.679 | 481.2497 | 134.8399 | 107.3191 | 107.2668 | 179.721 | 206.2843 | 200.5828 | 266.2008
243.6804 | 181.6804 | 481.1306 | 135.6852 | 108.31 | 108.2549 | 180.9896 | 206.8384 | 201.1542 | 267.4714
244.6818 | 182.6818 | 481.095 | 136.5327 | 109.3214 | 109.257 | 182.2861 | 207.1886 | 201.8765 | 268.744
245.6833 | 183.6833 | 481.1616 | 137.3796 | 110.33 | 110.2679 | 183.6127 | 207.8128 | 202.779 | 269.982
246.6847 | 184.6847 | 481.2079 | 138.242 | 111.3577 | 111.278 | 184.9269 | 208.3433 | 203.5727 | 271.2054
247.6862 | 185.6862 | 481.3467 | 139.1223 | 112.3764 | 112.2857 | 186.2496 | 208.7198 | 204.2491 | 272.4327
248.6876 | 186.6876 | 481.502 | 140.0207 | 113.4127 | 113.3059 | 187.5908 | 209.2554 | 204.8722 | 273.6261
249.689 | 187.689 | 481.6996 | 140.9429 | 114.4255 | 114.3016 | 188.93 | 209.6272 | 205.2305 | 274.7982
250.6805 | 188.6805 | 481.6956 | 141.8918 | 115.4573 | 115.3184 | 190.2728 | 210.0547 | 205.9026 | 275.9584
251.6819 | 189.6819 | 481.693 | 142.8398 | 116.477 | 116.3262 | 191.5976 | 210.4087 | 206.5838 | 277.093
252.6833 | 190.6833 | 481.7429 | 143.7964 | 117.507 | 117.32 | 192.9161 | 210.7541 | 207.4474 | 278.1909
253.6848 | 191.6848 | 481.7845 | 144.7734 | 118.5123 | 118.3194 | 194.2 | 211.0614 | 208.3028 | 279.3086
254.6862 | 192.6862 | 481.728 | 146.7799 | 119.5334 | 119.3203 | 195.4809 | 211.494 | 208.9439 | 280.4184
255.6877 | 193.6877 | 481.7832 | 148.7946 | 120.5428 | 120.311 | 196.7561 | 211.81 | 209.804 | 281.5081
256.6791 | 194.6791 | 481.8939 | 151.0135 | 121.5496 | 121.3046 | 197.9898 | 212.1635 | 210.5397 | 282.6041
257.6805 | 195.6805 | 481.8199 | 152.9845 | 122.5487 | 122.2869 | 199.2199 | 212.4751 | 211.2927 | 283.6641
258.682 | 196.682 | 481.7723 | 154.7537 | 123.5521 | 123.2649 | 200.4072 | 212.8028 | 211.9563 | 284.7229
259.6834 | 197.6834 | 481.7395 | 156.0965 | 124.5453 | 124.2556 | 201.5993 | 213.1076 | 212.7433 | 285.7851
260.6848 | 198.6848 | 481.7416 | 157.269 | 125.5612 | 125.228 | 202.7676 | 213.335 | 213.5876 | 286.8036
261.6863 | 199.6863 | 481.541 | 158.4458 | 126.5487 | 126.2064 | 203.8929 | 213.5707 | 214.4183 | 287.8367
262.6777 | 200.6777 | 481.2745 | 159.3197 | 127.543 | 127.1666 | 204.993 | 213.8361 | 215.2263 | 288.8592
263.6792 | 201.6792 | 481.2195 | 160.0495 | 128.5273 | 128.1277 | 206.0354 | 214.1165 | 215.8168 | 289.8391
264.7006 | 202.7006 | 481.2849 | 160.7217 | 129.5278 | 129.094 | 207.0408 | 214.4117 | 216.5999 | 290.8535
265.682 | 203.682 | 481.3553 | 161.3656 | 130.4984 | 130.0362 | 207.9848 | 214.6898 | 217.3655 | 291.7914
266.6835 | 204.6835 | 481.3979 | 162.0117 | 131.4649 | 130.9813 | 208.933 | 214.9806 | 218.1699 | 292.7455
267.6849 | 205.6849 | 481.4752 | 162.6547 | 132.4212 | 131.9155 | 209.8726 | 215.2664 | 219.0134 | 293.714
268.6864 | 206.6864 | 481.5986 | 163.3304 | 133.3982 | 132.8552 | 210.8205 | 215.4976 | 219.6402 | 294.6519
269.6878 | 207.6878 | 481.7936 | 164.0182 | 134.3638 | 133.7918 | 211.8053 | 215.7561 | 220.4864 | 295.5997
270.6792 | 208.6792 | 481.9488 | 164.7668 | 135.3176 | 134.7276 | 212.8261 | 215.9719 | 221.2991 | 296.5247
271.6807 | 209.6807 | 481.9975 | 165.5265 | 136.2726 | 135.6457 | 213.8983 | 216.2986 | 221.8216 | 297.4284
272.6821 | 210.6821 | 481.8969 | 166.3261 | 137.2071 | 136.5638 | 215.0129 | 216.5431 | 222.6839 | 298.3582
273.6835 | 211.6835 | 481.813 | 167.1891 | 138.1524 | 137.4762 | 216.1338 | 216.8169 | 223.5017 | 299.2615
274.685 | 212.685 | 481.6452 | 168.0836 | 139.0978 | 138.3891 | 217.274 | 217.0982 | 224.3427 | 300.1627
275.6864 | 213.6864 | 481.5063 | 168.9941 | 140.0209 | 139.2956 | 218.4562 | 217.4092 | 225.1726 | 301.0519
276.6879 | 214.6879 | 481.3947 | 169.9227 | 140.9518 | 140.195 | 219.7017 | 217.7179 | 226.07 | 301.935
277.6893 | 215.6893 | 481.3879 | 170.9025 | 141.8698 | 141.0973 | 221.0058 | 218.0325 | 226.7456 | 302.7998
278.6807 | 216.6807 | 481.3118 | 171.8995 | 142.7877 | 141.9851 | 222.3501 | 218.3249 | 227.5411 | 303.6807
279.6822 | 217.6822 | 481.1396 | 172.9484 | 143.691 | 142.8609 | 223.6919 | 218.6049 | 228.2947 | 304.5275
280.6836 | 218.6836 | 481.0999 | 174.0292 | 144.6036 | 143.7599 | 225.0156 | 218.8622 | 229.1933 | 305.3539
281.685 | 219.685 | 481.0511 | 175.158 | 145.5018 | 144.6296 | 226.3324 | 219.1204 | 230.0984 | 306.1665
282.6865 | 220.6865 | 481.0721 | 176.3382 | 146.3884 | 145.5087 | 227.6049 | 219.4434 | 230.8113 | 307.0147
283.6879 | 221.6879 | 481.111 | 177.6251 | 147.2891 | 146.3795 | 228.8304 | 219.7668 | 231.7075 | 307.8542
284.6793 | 222.6793 | 481.1382 | 179.1004 | 148.1756 | 147.2309 | 230.0249 | 220.0827 | 232.6215 | 308.7088
285.6808 | 223.6808 | 481.14 | 180.6642 | 149.0555 | 148.0977 | 231.1756 | 220.4117 | 233.5495 | 309.5558
286.6822 | 224.6822 | 481.2373 | 182.0947 | 149.9316 | 148.9554 | 232.2261 | 220.7486 | 234.3136 | 310.3977
287.6837 | 225.6837 | 481.3473 | 183.3462 | 150.7978 | 149.8034 | 233.225 | 221.1194 | 235.1736 | 311.2341
288.6851 | 226.6851 | 481.4259 | 184.4307 | 151.6502 | 150.6511 | 234.1612 | 221.5086 | 235.8253 | 312.0893
289.6865 | 227.6865 | 481.4715 | 185.4251 | 152.5022 | 151.5006 | 235.0747 | 221.8579 | 236.6326 | 312.9124
290.678 | 228.678 | 481.7411 | 186.3056 | 153.3631 | 152.3388 | 235.9748 | 222.2318 | 237.3021 | 313.7649
291.6894 | 229.6894 | 481.9896 | 187.1169 | 154.1977 | 153.1734 | 236.8118 | 222.5743 | 238.249 | 314.6043
292.6809 | 230.6809 | 482.0761 | 187.8859 | 155.0428 | 154.0091 | 237.6185 | 222.9413 | 239.1267 | 315.422
293.6823 | 231.6823 | 482.3228 | 188.5981 | 155.881 | 154.837 | 238.3523 | 223.3561 | 239.6844 | 316.2157
294.6837 | 232.6837 | 482.3343 | 189.2649 | 156.7031 | 155.6742 | 239.0075 | 223.8072 | 240.5479 | 317.0244
295.6852 | 233.6852 | 482.5893 | 189.896 | 157.5237 | 156.4953 | 239.6533 | 224.2852 | 241.406 | 317.8002
296.6866 | 234.6866 | 482.8482 | 190.4894 | 158.3343 | 157.3175 | 240.2437 | 224.8022 | 242.2646 | 318.5668
297.6881 | 235.6881 | 482.8887 | 191.0496 | 159.1566 | 158.1335 | 240.7882 | 225.3905 | 243.0609 | 319.3371
298.6895 | 236.6895 | 482.8558 | 191.5817 | 159.974 | 158.9531 | 241.2793 | 226.0167 | 243.9711 | 320.0925
299.6809 | 237.6809 | 482.9213 | 192.1111 | 160.7751 | 159.7539 | 241.7102 | 226.6568 | 244.252 | 320.8674
300.6824 | 238.6824 | 482.9499 | 192.631 | 161.5832 | 160.5563 | 242.0681 | 227.3524 | 245.0758 | 321.6292
301.6838 | 239.6838 | 483.035 | 193.1631 | 162.3775 | 161.3575 | 242.3712 | 228.1048 | 245.6843 | 322.3759
302.6852 | 240.6852 | 482.9741 | 193.7134 | 163.1577 | 162.1494 | 242.5859 | 228.8741 | 246.6094 | 323.135
303.6867 | 241.6867 | 482.8848 | 194.2742 | 163.969 | 162.9402 | 242.7521 | 229.7139 | 247.508 | 323.8947
304.6781 | 242.6781 | 482.8698 | 194.8605 | 164.7494 | 163.7266 | 242.7564 | 230.554 | 248.1661 | 324.6462
305.6795 | 243.6795 | 482.7862 | 195.4854 | 165.5301 | 164.5033 | 242.7076 | 231.4221 | 248.9362 | 325.3686
306.681 | 244.681 | 482.655 | 196.1352 | 166.3138 | 165.2666 | 242.7415 | 232.2741 | 249.1873 | 326.1072
307.6824 | 245.6824 | 482.5206 | 196.8073 | 167.0865 | 166.0429 | 243.0176 | 233.0957 | 249.5526 | 326.8131
308.6839 | 246.6839 | 482.3845 | 197.4893 | 167.8715 | 166.7981 | 243.4766 | 233.9272 | 250.1199 | 327.5231
309.6853 | 247.6853 | 482.2922 | 198.1884 | 168.643 | 167.5695 | 244.0813 | 234.7036 | 251.0777 | 328.1986
310.6867 | 248.6867 | 482.1159 | 198.8954 | 169.402 | 168.3333 | 244.7898 | 235.4241 | 251.5129 | 328.9183
311.6782 | 249.6782 | 481.8809 | 199.5996 | 170.154 | 169.0949 | 245.6459 | 236.0129 | 252.4735 | 329.6339
312.6796 | 250.6796 | 481.867 | 200.2854 | 170.907 | 169.8549 | 246.5888 | 236.5221 | 252.8747 | 330.3367
313.6811 | 251.6811 | 482.0402 | 200.9671 | 171.6563 | 170.6049 | 247.482 | 237.0114 | 253.6768 | 331.0096
314.6825 | 252.6825 | 482.0936 | 201.6166 | 172.401 | 171.3623 | 248.2909 | 237.4292 | 254.1821 | 331.6863
315.6839 | 253.6839 | 482.1592 | 202.2475 | 173.1414 | 172.1178 | 249.1388 | 237.774 | 254.7447 | 332.3457
316.6854 | 254.6854 | 482.1023 | 202.8558 | 173.895 | 172.8875 | 250.0458 | 238.287 | 255.7631 | 332.9649
317.6868 | 255.6868 | 482.1769 | 203.42 | 174.6321 | 173.6364 | 251.0001 | 238.9586 | 256.8232 | 333.5968
318.6883 | 256.6883 | 482.138 | 203.967 | 175.377 | 174.3925 | 252.0407 | 239.7349 | 257.4851 | 334.2499
319.6797 | 257.6797 | 482.1007 | 204.4781 | 176.1234 | 175.1531 | 252.8985 | 240.6671 | 258.527 | 334.8826
320.6811 | 258.6811 | 482.0206 | 204.9503 | 176.8494 | 175.9007 | 253.4318 | 241.6654 | 259.3437 | 335.5414
321.6826 | 259.6826 | 482.003 | 205.4054 | 177.5822 | 176.6575 | 253.6014 | 242.7021 | 259.7796 | 336.1774
322.684 | 260.684 | 482.0209 | 205.8326 | 178.3023 | 177.406 | 253.6469 | 243.7304 | 260.0468 | 336.8115
323.7555 | 261.7555 | 481.9017 | 206.3137 | 179.0876 | 178.2043 | 254.0014 | 244.8658 | 260.957 | 337.4812
324.6869 | 262.6869 | 481.7318 | 206.7477 | 179.7768 | 178.9007 | 254.0603 | 245.8521 | 261.619 | 338.0591
325.6783 | 263.6783 | 481.6977 | 207.1954 | 180.4987 | 179.6502 | 253.8417 | 246.8967 | 262.3651 | 338.682
326.6797 | 264.6797 | 481.9399 | 207.6626 | 181.2171 | 180.3929 | 253.7766 | 247.8968 | 263.0225 | 339.3295
327.6812 | 265.6812 | 482.1823 | 208.0928 | 181.9356 | 181.1276 | 254.0806 | 248.8625 | 263.901 | 339.9627
328.6826 | 266.6826 | 482.2069 | 208.4837 | 182.6497 | 181.861 | 254.5755 | 249.8984 | 264.6718 | 340.5706
329.6841 | 267.6841 | 482.1084 | 208.8476 | 183.3687 | 182.6029 | 255.1091 | 250.9208 | 265.1372 | 341.2054
330.6855 | 268.6855 | 482.1059 | 209.2052 | 184.0739 | 183.3267 | 255.3515 | 251.9266 | 266.0267 | 341.806
331.6869 | 269.6869 | 482.0725 | 209.5811 | 184.7979 | 184.0536 | 255.7723 | 252.9439 | 266.7463 | 342.4215
332.6784 | 270.6784 | 482.1102 | 209.9984 | 185.5185 | 184.7887 | 256.1567 | 253.9674 | 267.5038 | 343.0274
333.6798 | 271.6798 | 482.176 | 210.4206 | 186.2314 | 185.5099 | 256.3728 | 254.9513 | 268.4388 | 343.5947
334.6812 | 272.6812 | 482.3585 | 210.882 | 186.9379 | 186.237 | 256.5478 | 255.8552 | 269.0927 | 344.1782
335.6827 | 273.6827 | 482.5253 | 211.3833 | 187.6509 | 186.955 | 256.6934 | 256.7942 | 269.5939 | 344.7855
336.6841 | 274.6841 | 482.5487 | 211.8849 | 188.3535 | 187.664 | 257.1028 | 257.7545 | 270.5974 | 345.3662
337.6856 | 275.6856 | 482.4905 | 212.4118 | 189.0741 | 188.3747 | 257.8286 | 258.6238 | 271.0146 | 345.9757
338.687 | 276.687 | 482.5147 | 212.9279 | 189.7728 | 189.0831 | 258.417 | 259.5504 | 271.9632 | 346.5434
339.6884 | 277.6884 | 482.4145 | 213.4519 | 190.4686 | 189.7945 | 258.9569 | 260.5625 | 272.5013 | 347.1217
340.6799 | 278.6799 | 482.2655 | 213.9912 | 191.1706 | 190.4886 | 259.5432 | 261.487 | 272.2814 | 347.6926
341.6813 | 279.6813 | 482.2 | 214.5434 | 191.8665 | 191.1982 | 260.0789 | 262.3828 | 272.5439 | 348.2349
342.6828 | 280.6828 | 482.2058 | 215.1014 | 192.5552 | 191.9 | 261.0891 | 263.3147 | 273.345 | 348.7698
343.6842 | 281.6842 | 482.1136 | 215.673 | 193.2552 | 192.6024 | 262.8048 | 264.3594 | 274.1672 | 349.2917
344.6856 | 282.6856 | 482.0594 | 216.2026 | 193.9287 | 193.2965 | 264.3405 | 265.5364 | 274.716 | 349.8067
345.6871 | 283.6871 | 481.9564 | 216.7879 | 194.6106 | 193.9789 | 265.7483 | 266.5963 | 275.543 | 350.329
346.6785 | 284.6785 | 481.7534 | 217.3857 | 195.302 | 194.6651 | 266.8686 | 267.6432 | 275.562 | 350.8556
347.6799 | 285.6799 | 481.6004 | 217.9524 | 195.984 | 195.3496 | 267.8569 | 268.7471 | 276.0533 | 351.3854
348.6814 | 286.6814 | 481.3507 | 218.4198 | 196.6567 | 196.0356 | 268.7394 | 269.897 | 277.1073 | 351.895
349.6828 | 287.6828 | 481.3309 | 218.7314 | 197.3415 | 196.711 | 269.4374 | 270.7849 | 277.7079 | 352.3881
350.6843 | 288.6843 | 481.2954 | 219.0092 | 198.007 | 197.3724 | 269.9024 | 271.6302 | 278.507 | 352.8748
351.6857 | 289.6857 | 481.1624 | 219.3197 | 198.681 | 198.0222 | 270.2827 | 272.516 | 279.4125 | 353.3478
352.6871 | 290.6871 | 481.0172 | 219.6493 | 199.3407 | 198.6805 | 270.7174 | 273.3121 | 279.9534 | 353.8014
353.6886 | 291.6886 | 480.8557 | 219.9244 | 199.9991 | 199.3232 | 271.247 | 273.9965 | 280.1071 | 354.2811
354.68 | 292.68 | 480.6805 | 220.2375 | 200.6566 | 199.9672 | 271.865 | 274.6607 | 280.7753 | 354.7435
355.6814 | 293.6814 | 480.631 | 220.6091 | 201.3076 | 200.6054 | 272.4543 | 275.4299 | 281.5506 | 355.2105
356.6829 | 294.6829 | 480.5823 | 221.0791 | 201.9547 | 201.2416 | 273.0668 | 276.2423 | 282.2798 | 355.6481
357.6843 | 295.6843 | 480.4113 | 221.57 | 202.6119 | 201.8784 | 273.8028 | 276.9794 | 283.0305 | 356.0947
358.6858 | 296.6858 | 480.3309 | 222.053 | 203.2404 | 202.5082 | 274.5635 | 277.722 | 283.7524 | 356.5259
359.6872 | 297.6872 | 480.1696 | 222.4942 | 203.8641 | 203.1236 | 275.3045 | 278.4901 | 284.2882 | 356.9628
360.6786 | 298.6786 | 480.1939 | 222.9071 | 204.491 | 203.737 | 276.0167 | 279.2607 | 284.9238 | 357.4194
361.6901 | 299.6901 | 480.1622 | 223.3228 | 205.1234 | 204.3455 | 276.6636 | 280.0345 | 285.447 | 357.8732
362.6815 | 300.6815 | 480.1826 | 223.8222 | 205.733 | 204.9732 | 277.2758 | 280.8268 | 286.1245 | 358.3576
363.683 | 301.683 | 480.2758 | 224.3189 | 206.3392 | 205.5974 | 277.8973 | 281.6522 | 286.4399 | 358.8354
364.6844 | 302.6844 | 480.3524 | 224.7924 | 206.9356 | 206.2063 | 278.4741 | 282.4932 | 286.855 | 359.2887
365.6858 | 303.6858 | 480.3803 | 225.2556 | 207.5562 | 206.804 | 278.9817 | 283.3575 | 287.6683 | 359.7754
366.6873 | 304.6873 | 480.2602 | 225.724 | 208.1619 | 207.4099 | 279.4515 | 284.1491 | 288.3183 | 360.2464
367.6787 | 305.6787 | 480.2498 | 226.2009 | 208.76 | 208.0134 | 279.9106 | 284.8888 | 288.6183 | 360.7143
368.6801 | 306.6801 | 480.4375 | 226.6801 | 209.3652 | 208.6669 | 280.409 | 285.6496 | 289.3947 | 361.1987
369.6816 | 307.6816 | 480.5515 | 227.169 | 209.9489 | 209.3265 | 280.9173 | 286.3416 | 290.0853 | 361.6758
370.683 | 308.683 | 480.7214 | 227.6696 | 210.5302 | 209.953 | 281.5841 | 286.9602 | 290.7638 | 362.128
371.6845 | 309.6845 | 480.8349 | 228.1841 | 211.1194 | 210.5759 | 282.2734 | 287.5798 | 291.2663 | 362.5692
372.6859 | 310.6859 | 480.9152 | 228.7418 | 211.7086 | 211.2 | 282.9403 | 288.1939 | 291.9395 | 363.0148
373.6873 | 311.6873 | 480.8714 | 229.269 | 212.3119 | 211.8214 | 283.5047 | 288.8016 | 292.4553 | 363.4601
374.6788 | 312.6788 | 480.8597 | 229.85 | 212.9369 | 212.4189 | 283.9582 | 289.4359 | 292.9355 | 363.9148
375.6802 | 313.6802 | 480.6941 | 230.4347 | 213.5617 | 213.0076 | 284.3467 | 290.0656 | 293.6465 | 364.3491
376.6816 | 314.6816 | 480.6125 | 231.0205 | 214.2189 | 213.5969 | 284.6854 | 290.6277 | 294.0005 | 364.7658
377.6831 | 315.6831 | 480.5267 | 231.5868 | 214.8361 | 214.165 | 284.9726 | 291.1708 | 294.3893 | 365.1909
378.6845 | 316.6845 | 480.4061 | 232.122 | 215.4351 | 214.7358 | 285.1274 | 291.7583 | 294.6649 | 365.618
379.686 | 317.686 | 480.3993 | 232.6014 | 216.0333 | 215.3014 | 285.1913 | 292.467 | 295.1541 | 366.0332
380.6874 | 318.6874 | 480.4028 | 233.0917 | 216.6199 | 215.8677 | 285.1635 | 293.2062 | 295.4545 | 366.4203
381.6888 | 319.6888 | 480.414 | 233.5565 | 217.1921 | 216.4236 | 285.176 | 293.9869 | 296.2893 | 366.8469
382.6803 | 320.6803 | 480.3721 | 234.0001 | 217.7622 | 217 | 285.1957 | 294.693 | 297.0934 | 367.2531
383.6817 | 321.6817 | 480.2585 | 234.4559 | 218.3066 | 217.5621 | 285.2799 | 295.3267 | 296.9003 | 367.6702
384.6932 | 322.6932 | 480.2821 | 234.9245 | 218.8684 | 218.1247 | 285.4051 | 295.9914 | 297.8851 | 368.0794
385.6846 | 323.6846 | 480.3824 | 235.3829 | 219.4231 | 218.6695 | 285.6361 | 296.6729 | 298.9584 | 368.4879
386.686 | 324.686 | 480.438 | 235.8864 | 219.9949 | 219.246 | 285.9511 | 297.3756 | 299.4329 | 368.8971
387.6875 | 325.6875 | 480.4998 | 236.3892 | 220.5544 | 219.7944 | 286.301 | 298.1013 | 300.1318 | 369.295
388.6789 | 326.6789 | 480.7858 | 236.9109 | 221.0954 | 220.3542 | 286.6655 | 298.9059 | 299.8529 | 369.6882
389.6803 | 327.6803 | 480.764 | 237.4152 | 221.64 | 220.9205 | 287.0347 | 299.7076 | 300.5203 | 370.0816
390.6818 | 328.6818 | 480.9769 | 237.9224 | 222.1886 | 221.4959 | 287.4231 | 300.5068 | 301.4389 | 370.4425
391.6832 | 329.6832 | 481.2321 | 238.4417 | 222.7289 | 222.0627 | 287.8579 | 301.1964 | 302.2124 | 370.8235
392.6847 | 330.6847 | 481.3509 | 238.9863 | 223.2802 | 222.6253 | 288.2745 | 301.7942 | 302.8055 | 371.2222
393.6861 | 331.6861 | 481.4836 | 239.5125 | 223.8256 | 223.1841 | 288.7184 | 302.4111 | 302.8194 | 371.6062
394.6875 | 332.6875 | 481.5948 | 240.073 | 224.3683 | 223.7502 | 289.1379 | 303.1014 | 303.8759 | 372.0079
395.679 | 333.679 | 481.7914 | 240.7443 | 224.9136 | 224.3053 | 289.5181 | 303.8209 | 304.3396 | 372.3897
396.6804 | 334.6804 | 481.9889 | 241.5792 | 225.4461 | 224.8727 | 289.9707 | 304.5428 | 304.3821 | 372.7686
397.6818 | 335.6818 | 482.1519 | 242.8605 | 226.0021 | 225.4238 | 290.4082 | 305.2377 | 304.4288 | 373.1195
398.6833 | 336.6833 | 482.2091 | 244.3052 | 226.545 | 225.9673 | 290.8787 | 305.9735 | 304.6629 | 373.4827
399.6847 | 337.6847 | 482.2739 | 245.5607 | 227.1066 | 226.54 | 291.3785 | 306.6435 | 305.0524 | 373.8517
400.6862 | 338.6862 | 482.2924 | 246.4382 | 227.6516 | 227.0825 | 291.9219 | 307.3184 | 305.2341 | 374.2035
401.6876 | 339.6876 | 482.4854 | 247.1698 | 228.1982 | 227.6375 | 292.4661 | 308.0325 | 305.8703 | 374.5353
402.679 | 340.679 | 482.5038 | 247.8761 | 228.753 | 228.1713 | 292.9999 | 308.7254 | 305.9861 | 374.8757
403.6805 | 341.6805 | 482.441 | 248.5572 | 229.2863 | 228.7294 | 293.6193 | 309.421 | 306.5163 | 375.2041
404.6819 | 342.6819 | 482.4267 | 249.1567 | 229.8318 | 229.2745 | 294.2295 | 310.0743 | 307.2383 | 375.5369
405.6833 | 343.6833 | 482.2865 | 249.8113 | 230.3842 | 229.8203 | 294.8899 | 310.6966 | 307.3031 | 375.8698
406.6848 | 344.6848 | 482.1553 | 250.3816 | 230.9349 | 230.3825 | 295.54 | 311.3539 | 306.9451 | 376.173
407.6862 | 345.6862 | 481.9505 | 250.8605 | 231.4837 | 230.9426 | 296.2349 | 311.9558 | 307.3226 | 376.5329
408.6877 | 346.6877 | 481.7775 | 251.2906 | 232.054 | 231.5002 | 296.9825 | 312.5896 | 307.6109 | 376.8699
409.6791 | 347.6791 | 481.6763 | 251.6691 | 232.6008 | 232.0446 | 297.6775 | 313.228 | 307.4924 | 377.1802
410.6805 | 348.6805 | 481.6593 | 252.0251 | 233.1427 | 232.5946 | 298.351 | 313.7618 | 307.8285 | 377.5202
411.682 | 349.682 | 481.6012 | 252.3678 | 233.6759 | 233.1527 | 299.0117 | 314.1899 | 309.012 | 377.8337
412.6834 | 350.6834 | 481.5103 | 252.7276 | 234.2164 | 233.6957 | 299.6745 | 314.5927 | 308.5904 | 378.1415
413.6848 | 351.6848 | 481.5502 | 253.0732 | 234.7559 | 234.241 | 300.353 | 315.0575 | 308.9621 | 378.445
414.6863 | 352.6863 | 481.4934 | 253.3509 | 235.2802 | 234.7793 | 300.9552 | 315.5135 | 308.5807 | 378.7572
415.6777 | 353.6777 | 481.5379 | 253.655 | 235.8224 | 235.3214 | 301.5743 | 316.0246 | 308.5334 | 379.0737
416.6792 | 354.6792 | 481.4684 | 253.9763 | 236.3508 | 235.8671 | 302.2219 | 316.6101 | 308.4121 | 379.3865
417.6806 | 355.6806 | 481.5302 | 254.2983 | 236.8796 | 236.4232 | 302.8824 | 317.1994 | 308.264 | 379.7057
418.682 | 356.682 | 481.5901 | 254.6655 | 237.4043 | 236.9626 | 303.5491 | 317.7293 | 307.3948 | 380.0303
419.6835 | 357.6835 | 481.4323 | 255.0927 | 237.9306 | 237.5076 | 304.1485 | 318.2153 | 307.4863 | 380.3366
420.6849 | 358.6849 | 481.1958 | 255.4726 | 238.4767 | 238.0508 | 304.7072 | 318.6748 | 307.357 | 380.6378
421.6864 | 359.6864 | 481.1651 | 255.8299 | 239.0093 | 238.6048 | 305.4037 | 319.2619 | 308.0839 | 380.9013
422.6878 | 360.6878 | 481.1848 | 256.1938 | 239.5481 | 239.1433 | 306.0596 | 319.9139 | 308.3273 | 381.2098
423.6892 | 361.6892 | 481.2086 | 256.6099 | 240.1004 | 239.6891 | 306.7261 | 320.5642 | 308.0042 | 381.5159
424.6807 | 362.6807 | 481.2434 | 257.0296 | 240.6629 | 240.2262 | 307.3144 | 321.197 | 307.9864 | 381.845
425.6821 | 363.6821 | 481.2392 | 257.4888 | 241.2187 | 240.7692 | 307.9775 | 321.7776 | 307.9502 | 382.1709
426.6835 | 364.6835 | 481.2078 | 257.9797 | 241.8023 | 241.3399 | 308.7005 | 322.3827 | 307.603 | 382.4899
427.685 | 365.685 | 481.0218 | 258.4735 | 242.3714 | 241.8932 | 309.3313 | 323.0264 | 307.7303 | 382.8212
428.6864 | 366.6864 | 480.8971 | 258.9537 | 242.9335 | 242.4433 | 309.9322 | 323.6362 | 308.3753 | 383.1352
429.6879 | 367.6879 | 480.9981 | 259.4249 | 243.4946 | 242.9999 | 310.4608 | 324.2185 | 307.992 | 383.4523
430.6793 | 368.6793 | 481.2555 | 259.9287 | 244.0592 | 243.573 | 311.0536 | 324.7946 | 308.3884 | 383.7572
431.6807 | 369.6807 | 481.1791 | 260.4585 | 244.6087 | 244.2424 | 311.6679 | 325.3366 | 308.5554 | 384.0463
432.6822 | 370.6822 | 480.9916 | 261.0017 | 245.1667 | 244.9756 | 312.2637 | 325.9169 | 308.283 | 384.3604
433.6836 | 371.6836 | 480.9642 | 261.5537 | 245.7087 | 245.5287 | 312.8381 | 326.5271 | 308.1001 | 384.6412
434.685 | 372.685 | 480.907 | 262.1057 | 246.2717 | 246.0647 | 313.4596 | 327.0681 | 308.158 | 384.9054
435.6865 | 373.6865 | 480.8803 | 262.6268 | 246.8146 | 246.6674 | 314.0386 | 327.5753 | 308.194 | 385.1739
436.6879 | 374.6879 | 480.8513 | 263.1855 | 247.3654 | 247.2381 | 314.5483 | 327.986 | 308.1494 | 385.4648
437.6794 | 375.6794 | 480.7887 | 263.7297 | 247.9113 | 247.7463 | 315.1379 | 328.4591 | 308.5215 | 385.7312
438.6808 | 376.6808 | 480.868 | 264.2801 | 248.438 | 248.2598 | 315.7379 | 328.9404 | 309.2625 | 385.9909
439.6822 | 377.6822 | 481.0132 | 264.8389 | 248.9848 | 248.7692 | 316.3355 | 329.5204 | 309.5606 | 386.2344
440.6837 | 378.6837 | 481.0274 | 265.389 | 249.5159 | 249.2937 | 316.9002 | 330.1418 | 310.2029 | 386.4895
441.6851 | 379.6851 | 480.9508 | 265.9586 | 250.062 | 249.7986 | 317.4581 | 330.7332 | 310.3526 | 386.7077
442.6866 | 380.6866 | 481.0279 | 266.5243 | 250.6037 | 250.3124 | 318.036 | 331.3664 | 310.6022 | 386.9257
443.688 | 381.688 | 481.3336 | 267.0983 | 251.1614 | 250.835 | 318.6703 | 331.8591 | 312.071 | 387.1444
444.6794 | 382.6794 | 481.4725 | 267.6682 | 251.7005 | 251.3502 | 319.3407 | 332.3507 | 312.2501 | 387.3898
445.6809 | 383.6809 | 481.5213 | 268.2537 | 252.2465 | 251.8924 | 320.0871 | 332.9137 | 311.7893 | 387.6316
446.6823 | 384.6823 | 481.4993 | 268.8372 | 252.7759 | 252.4335 | 320.6691 | 333.4281 | 311.8613 | 387.8618
447.6837 | 385.6837 | 481.5203 | 269.4264 | 253.3105 | 252.9875 | 321.2447 | 333.9258 | 312.2535 | 388.0838
448.6852 | 386.6852 | 481.6907 | 270.0192 | 253.8633 | 253.5383 | 321.8648 | 334.4486 | 312.3666 | 388.3135
449.6866 | 387.6866 | 481.7949 | 270.6114 | 254.3977 | 254.091 | 322.5194 | 334.9445 | 312.0437 | 388.545
450.6881 | 388.6881 | 481.8496 | 271.1938 | 254.9308 | 254.6639 | 323.1765 | 335.4602 | 312.5895 | 388.7626
451.6795 | 389.6795 | 482.1269 | 271.7813 | 255.453 | 255.2159 | 323.9116 | 336.0338 | 312.1353 | 388.9586
452.6809 | 390.6809 | 482.254 | 272.3812 | 255.9754 | 255.8046 | 324.6135 | 336.5879 | 312.418 | 389.1372
453.6824 | 391.6824 | 482.3786 | 272.9839 | 256.4963 | 256.3551 | 325.2664 | 337.133 | 313.2509 | 389.3495
454.6838 | 392.6838 | 482.3632 | 273.5932 | 257.0182 | 256.9086 | 325.9354 | 337.7059 | 313.3103 | 389.5647
455.6852 | 393.6852 | 482.3668 | 274.2122 | 257.5453 | 257.4511 | 326.642 | 338.2865 | 313.616 | 389.7837
456.6867 | 394.6867 | 482.3935 | 274.821 | 258.0789 | 257.9822 | 327.3649 | 338.8511 | 313.4771 | 390.015
457.6781 | 395.6781 | 482.4016 | 275.4254 | 258.6083 | 258.5001 | 328.0228 | 339.3891 | 313.5228 | 390.235
458.6795 | 396.6795 | 482.2626 | 276.0371 | 259.1334 | 259.0488 | 328.6745 | 339.9401 | 314.0785 | 390.4051
459.681 | 397.681 | 482.4371 | 276.6441 | 259.658 | 259.597 | 329.3033 | 340.5124 | 314.3948 | 390.6006
460.6824 | 398.6824 | 482.6383 | 277.242 | 260.1923 | 260.1592 | 329.896 | 341.0572 | 315.1706 | 390.7907
461.6839 | 399.6839 | 482.6243 | 277.8489 | 260.7406 | 260.7094 | 330.4842 | 341.529 | 314.9277 | 390.9667
462.6853 | 400.6853 | 482.4547 | 278.4515 | 261.2807 | 261.2413 | 331.0276 | 342.0275 | 314.8436 | 391.1452
463.6867 | 401.6867 | 482.2961 | 279.0675 | 261.8153 | 261.7972 | 331.6299 | 342.562 | 315.5175 | 391.3325
464.6882 | 402.6882 | 482.0915 | 279.6775 | 262.3652 | 262.3613 | 332.1564 | 343.0189 | 315.643 | 391.4792
465.6896 | 403.6896 | 481.8667 | 280.2912 | 262.9051 | 262.911 | 332.6181 | 343.4574 | 315.7061 | 391.6236
466.6811 | 404.6811 | 481.6677 | 280.8988 | 263.4587 | 263.4849 | 333.1266 | 343.8658 | 315.3472 | 391.794
467.6825 | 405.6825 | 481.5134 | 281.4983 | 263.9903 | 264.045 | 333.695 | 344.2669 | 315.6946 | 391.9547
468.6839 | 406.6839 | 481.4904 | 282.1193 | 264.5486 | 264.6053 | 334.1823 | 344.6761 | 316.0028 | 392.1357
469.6854 | 407.6854 | 481.5041 | 282.7283 | 265.1069 | 265.15 | 334.7203 | 345.057 | 315.7113 | 392.3491
470.6868 | 408.6868 | 481.5312 | 283.3325 | 265.6722 | 265.7158 | 335.3284 | 345.4899 | 315.8594 | 392.515
471.6883 | 409.6883 | 481.5417 | 283.9577 | 266.2077 | 266.238 | 335.9535 | 345.9177 | 316.9519 | 392.7039
472.6797 | 410.6797 | 481.6231 | 284.5641 | 266.7589 | 266.7967 | 336.5707 | 346.2996 | 316.4991 | 392.8911
473.6811 | 411.6811 | 481.6435 | 285.185 | 267.3222 | 267.3598 | 337.1552 | 346.7397 | 317.0032 | 393.0762
474.6826 | 412.6826 | 481.6083 | 285.8048 | 267.8649 | 267.905 | 337.7727 | 347.1831 | 316.4252 | 393.277
475.684 | 413.684 | 481.6006 | 286.4378 | 268.4197 | 268.4491 | 338.3997 | 347.6511 | 316.9268 | 393.4464
476.6854 | 414.6854 | 481.6685 | 287.0567 | 268.9732 | 268.9963 | 339.0379 | 348.0808 | 318.027 | 393.623
477.6869 | 415.6869 | 481.5739 | 287.67 | 269.5254 | 269.538 | 339.7123 | 348.5027 | 318.0943 | 393.7922
478.6783 | 416.6783 | 481.5908 | 288.2852 | 270.0579 | 270.0952 | 340.409 | 348.9048 | 317.7621 | 393.9654
479.6797 | 417.6797 | 481.6421 | 288.9051 | 270.6023 | 270.6461 | 341.095 | 349.3162 | 318.2112 | 394.1426
480.6812 | 418.6812 | 481.7314 | 289.5351 | 271.1473 | 271.2057 | 341.7664 | 349.6926 | 318.4653 | 394.2692
481.6826 | 419.6826 | 481.8426 | 290.1554 | 271.6657 | 271.7508 | 342.4512 | 350.0639 | 320.0098 | 394.3601
482.6841 | 420.6841 | 482.031 | 290.7652 | 272.2062 | 272.3357 | 343.1379 | 350.4956 | 320.3506 | 394.4938
483.6855 | 421.6855 | 482.2347 | 291.3796 | 272.7261 | 272.9316 | 343.8897 | 350.9275 | 320.1883 | 394.6483
484.6869 | 422.6869 | 482.2981 | 292.001 | 273.2559 | 273.4869 | 344.621 | 351.3393 | 320.7783 | 394.797
485.6784 | 423.6784 | 482.3532 | 292.628 | 273.8124 | 274.0061 | 345.2852 | 351.765 | 320.3532 | 394.9479
486.6798 | 424.6798 | 482.1598 | 293.249 | 274.3489 | 274.538 | 345.8675 | 352.1586 | 320.4525 | 395.1038
487.6813 | 425.6813 | 482.0585 | 293.867 | 274.9009 | 275.0804 | 346.3962 | 352.5314 | 320.7845 | 395.244
488.6827 | 426.6827 | 481.868 | 294.4977 | 275.4218 | 275.6314 | 346.938 | 352.873 | 320.472 | 395.3973
489.6841 | 427.6841 | 481.7059 | 295.1173 | 275.9475 | 276.1759 | 347.4372 | 353.1516 | 320.6059 | 395.4937
490.6856 | 428.6856 | 481.5377 | 295.7272 | 276.5013 | 276.6956 | 347.9438 | 353.4323 | 320.6438 | 395.6112
491.687 | 429.687 | 481.5012 | 296.3484 | 277.0329 | 277.202 | 348.4514 | 353.7514 | 320.9748 | 395.7515
492.6885 | 430.6885 | 481.3388 | 296.9606 | 277.5718 | 277.7771 | 348.8867 | 354.0737 | 321.1683 | 395.8701
493.6899 | 431.6899 | 481.3542 | 297.5771 | 278.1081 | 278.3808 | 349.3153 | 354.4445 | 321.4204 | 395.9944
494.6813 | 432.6813 | 481.2936 | 298.185 | 278.6467 | 278.9516 | 349.775 | 354.8254 | 322.1211 | 396.1303
495.6828 | 433.6828 | 481.2736 | 298.7859 | 279.1993 | 279.5215 | 350.1752 | 355.1962 | 322.7522 | 396.2452
496.6842 | 434.6842 | 481.224 | 299.3935 | 279.7628 | 280.1213 | 350.5357 | 355.5888 | 322.9397 | 396.3588
497.6856 | 435.6856 | 481.2939 | 299.99 | 280.2826 | 280.7098 | 350.9158 | 355.9994 | 323.123 | 396.4873
498.6871 | 436.6871 | 481.3154 | 300.5919 | 280.8304 | 281.2751 | 351.2961 | 356.4316 | 323.0747 | 396.6146
499.6785 | 437.6785 | 481.3189 | 301.1911 | 281.3767 | 281.8229 | 351.7474 | 356.8468 | 324.189 | 396.7341
500.6799 | 438.6799 | 481.3166 | 301.7963 | 281.9211 | 282.37 | 352.2403 | 357.2037 | 324.3651 | 396.8698
501.6814 | 439.6814 | 481.4275 | 302.4184 | 282.4746 | 282.9017 | 352.6921 | 357.6078 | 324.2293 | 396.9833
502.6828 | 440.6828 | 481.48 | 303.0462 | 283.0409 | 283.4387 | 353.1081 | 358.0322 | 324.1943 | 397.096
503.7143 | 441.7143 | 481.4841 | 303.6843 | 283.6219 | 283.993 | 353.5292 | 358.4826 | 324.4649 | 397.2374
504.6857 | 442.6857 | 481.4204 | 304.2924 | 284.1683 | 284.5009 | 354.0267 | 358.9091 | 324.116 | 397.3874
505.6871 | 443.6871 | 481.5962 | 304.9236 | 284.7296 | 285.0653 | 354.5482 | 359.2811 | 324.0058 | 397.5314
506.6886 | 444.6886 | 481.7019 | 305.5606 | 285.2718 | 285.6069 | 355.021 | 359.6029 | 324.3629 | 397.6314
507.69 | 445.69 | 481.7892 | 306.186 | 285.8019 | 286.1454 | 355.4526 | 359.9495 | 324.4524 | 397.7565
508.6814 | 446.6814 | 481.8404 | 306.8119 | 286.3426 | 286.681 | 355.8141 | 360.2864 | 324.5661 | 397.8667
509.6829 | 447.6829 | 481.6926 | 307.4605 | 286.8836 | 287.2379 | 356.2261 | 360.6394 | 324.679 | 397.9866
510.6843 | 448.6843 | 481.6137 | 308.1166 | 287.4328 | 287.787 | 356.6502 | 361.0209 | 325.0529 | 398.0837
511.6858 | 449.6858 | 481.5928 | 308.7826 | 287.9804 | 288.3782 | 356.9518 | 361.3992 | 325.958 | 398.1787
512.6872 | 450.6872 | 481.5829 | 309.4525 | 288.5313 | 288.9508 | 357.2554 | 361.7543 | 326.1347 | 398.2899
513.6886 | 451.6886 | 481.4838 | 310.1236 | 289.1018 | 289.493 | 357.5436 | 362.1521 | 326.4216 | 398.4396
514.6901 | 452.6901 | 481.3922 | 310.8096 | 289.6729 | 290.025 | 357.8091 | 362.5573 | 326.4375 | 398.583
515.6815 | 453.6815 | 481.2656 | 311.486 | 290.217 | 290.5808 | 358.1081 | 362.9875 | 327.1299 | 398.6975
516.683 | 454.683 | 481.1806 | 312.1738 | 290.7617 | 291.1044 | 358.4122 | 363.4389 | 326.7371 | 398.8344
517.6844 | 455.6844 | 481.038 | 312.8749 | 291.2997 | 291.6256 | 358.8301 | 363.9115 | 326.8184 | 398.9388
518.6858 | 456.6858 | 481.0024 | 313.5772 | 291.8572 | 292.1685 | 359.3039 | 364.3791 | 326.9702 | 399.0277
519.6873 | 457.6873 | 480.9447 | 314.2723 | 292.4404 | 292.6729 | 359.822 | 364.8755 | 326.7657 | 399.128
520.6787 | 458.6787 | 480.9733 | 314.9736 | 292.9988 | 293.2352 | 360.3278 | 365.358 | 326.8745 | 399.2433
521.6801 | 459.6801 | 481.0438 | 315.6832 | 293.5662 | 293.7772 | 360.8658 | 365.8448 | 327.2726 | 399.3621
522.6816 | 460.6816 | 481.0648 | 316.3933 | 294.1077 | 294.3154 | 361.3439 | 366.3026 | 327.2846 | 399.4567
523.683 | 461.683 | 481.1025 | 317.1002 | 294.6551 | 294.8674 | 361.8337 | 366.7857 | 327.3292 | 399.5462
524.6845 | 462.6845 | 481.0265 | 317.8017 | 295.2162 | 295.3861 | 362.2881 | 367.2342 | 327.5805 | 399.6562
525.6859 | 463.6859 | 481.0163 | 318.5046 | 295.7515 | 295.901 | 362.7468 | 367.7065 | 329.1059 | 399.7648
526.6873 | 464.6873 | 481.0816 | 319.2057 | 296.3092 | 296.4357 | 363.2212 | 368.2374 | 329.0814 | 399.8595
527.6788 | 465.6788 | 481.0323 | 319.917 | 296.8722 | 296.9906 | 363.7318 | 368.7444 | 328.8186 | 399.9743
528.6802 | 466.6802 | 481.1352 | 320.6339 | 297.4404 | 297.5325 | 364.1467 | 369.2358 | 328.8383 | 400.0631
529.6816 | 467.6816 | 481.1339 | 321.3528 | 298.026 | 298.0961 | 364.4563 | 369.6669 | 329.4196 | 400.1661
530.6831 | 468.6831 | 481.2178 | 322.0721 | 298.6024 | 298.6185 | 364.8126 | 370.1151 | 329.2614 | 400.2704
531.6845 | 469.6845 | 481.2283 | 322.8032 | 299.1662 | 299.196 | 365.2475 | 370.5334 | 330.0112 | 400.3496
532.686 | 470.686 | 481.4141 | 323.5383 | 299.7277 | 299.7264 | 365.7138 | 370.9973 | 329.9942 | 400.4562
533.6874 | 471.6874 | 481.5535 | 324.299 | 300.2981 | 300.2657 | 366.1862 | 371.4388 | 330.6695 | 400.5721
534.6888 | 472.6888 | 481.6576 | 325.0402 | 300.8665 | 300.7893 | 366.6663 | 371.8552 | 330.7839 | 400.6766
535.6803 | 473.6803 | 481.6221 | 325.7771 | 301.4256 | 301.3718 | 367.1424 | 372.3238 | 331.6287 | 400.773
536.6817 | 474.6817 | 481.5641 | 326.5483 | 301.989 | 301.9193 | 367.6144 | 372.7594 | 331.6394 | 400.8796
537.6832 | 475.6832 | 481.4922 | 327.3117 | 302.5493 | 302.4912 | 368.0129 | 373.1333 | 332.3069 | 401.0029
538.6846 | 476.6846 | 481.3563 | 328.078 | 303.1053 | 303.0269 | 368.4512 | 373.4751 | 332.5969 | 401.0683
539.686 | 477.686 | 481.2593 | 328.8614 | 303.6851 | 303.5665 | 368.7826 | 373.8573 | 332.8085 | 401.1461
540.6875 | 478.6875 | 481.228 | 329.635 | 304.2624 | 304.135 | 369.1139 | 374.3034 | 332.2077 | 401.2374
541.6789 | 479.6789 | 481.1086 | 330.3996 | 304.8374 | 304.7219 | 369.5017 | 374.7751 | 332.1537 | 401.3245
542.6803 | 480.6803 | 481.1892 | 331.2033 | 305.4176 | 305.2807 | 369.8424 | 375.2608 | 331.95 | 401.4216
543.6818 | 481.6818 | 481.3325 | 331.9873 | 305.9773 | 305.84 | 370.2549 | 375.7535 | 331.9188 | 401.4961
544.6832 | 482.6832 | 481.2495 | 332.779 | 306.5502 | 306.4095 | 370.6261 | 376.233 | 332.1515 | 401.5865
545.6847 | 483.6847 | 481.2855 | 333.5751 | 307.1269 | 306.9821 | 370.928 | 376.7169 | 333.4292 | 401.6537
546.6861 | 484.6861 | 481.2297 | 334.391 | 307.6992 | 307.5562 | 371.1203 | 377.1635 | 333.8757 | 401.7746
547.6875 | 485.6875 | 481.2123 | 335.2073 | 308.2723 | 308.1018 | 371.4144 | 377.6303 | 333.5854 | 401.8886
548.679 | 486.679 | 481.1522 | 336.042 | 308.8376 | 308.6376 | 371.6944 | 378.1077 | 333.4699 | 402.007
549.6804 | 487.6804 | 481.13 | 336.8907 | 309.4163 | 309.2046 | 372.0118 | 378.5647 | 332.7163 | 402.1146
550.6818 | 488.6818 | 481.2747 | 337.7294 | 309.9734 | 309.7706 | 372.2816 | 379.0241 | 332.4683 | 402.2326
551.6833 | 489.6833 | 481.304 | 338.5763 | 310.5439 | 310.3476 | 372.5629 | 379.4682 | 332.3873 | 402.3168
552.6847 | 490.6847 | 481.2878 | 339.4398 | 311.1179 | 310.9226 | 372.8156 | 379.8958 | 332.0814 | 402.4301
553.6862 | 491.6862 | 481.2278 | 340.3269 | 311.6966 | 311.4949 | 373.104 | 380.2873 | 332.0433 | 402.5331
554.6876 | 492.6876 | 481.14 | 341.2094 | 312.2564 | 312.0503 | 373.3759 | 380.6663 | 332.386 | 402.6412
555.689 | 493.689 | 481.2009 | 342.1002 | 312.8297 | 312.6058 | 373.6704 | 381.0914 | 332.6733 | 402.722
556.6805 | 494.6805 | 481.2249 | 342.9816 | 313.4049 | 313.1625 | 373.9598 | 381.5197 | 332.3058 | 402.8346
557.6819 | 495.6819 | 481.2486 | 343.8287 | 313.9839 | 313.7064 | 374.2867 | 381.9516 | 332.6765 | 402.9118
558.6833 | 496.6833 | 481.1429 | 344.6173 | 314.5589 | 314.2321 | 374.6117 | 382.395 | 332.6867 | 403.0364
559.6848 | 497.6848 | 481.0589 | 345.479 | 315.1198 | 314.7904 | 374.9383 | 382.8461 | 334.2816 | 403.1346
560.6862 | 498.6862 | 480.9842 | 346.3237 | 315.6988 | 315.347 | 375.2905 | 383.2836 | 333.4246 | 403.2348
561.6877 | 499.6877 | 480.8751 | 347.1812 | 316.2609 | 315.9164 | 375.6499 | 383.7282 | 333.6125 | 403.322
562.6791 | 500.6791 | 480.8684 | 348.0182 | 316.8233 | 316.469 | 376.0148 | 384.1695 | 333.5249 | 403.4112
563.6805 | 501.6805 | 480.828 | 348.8665 | 317.3928 | 317.0274 | 376.4185 | 384.5885 | 333.7992 | 403.5478
564.682 | 502.682 | 480.7905 | 349.6881 | 317.9645 | 317.5808 | 376.785 | 384.9492 | 334.3248 | 403.6639
565.6834 | 503.6834 | 480.9418 | 350.4525 | 318.5442 | 318.1479 | 377.0318 | 385.3409 | 334.1115 | 403.8056
566.6849 | 504.6849 | 481.1128 | 351.1732 | 319.1263 | 318.6833 | 377.3009 | 385.7431 | 334.8123 | 403.9014
567.6863 | 505.6863 | 481.2964 | 351.9101 | 319.7112 | 319.2037 | 377.5737 | 386.1568 | 334.8766 | 403.9755
568.6877 | 506.6877 | 481.3081 | 352.6447 | 320.2913 | 319.7312 | 377.8808 | 386.5827 | 335.1195 | 404.0699
569.6792 | 507.6792 | 481.2975 | 353.3086 | 320.8664 | 320.2703 | 378.1472 | 387.0161 | 335.8893 | 404.1614
570.6806 | 508.6806 | 481.2178 | 353.9447 | 321.4408 | 320.793 | 378.3891 | 387.4101 | 335.9427 | 404.2729
571.682 | 509.682 | 481.3431 | 354.5638 | 322.0198 | 321.3138 | 378.63 | 387.8103 | 335.586 | 404.3722
572.6835 | 510.6835 | 481.264 | 355.1434 | 322.6096 | 321.8572 | 378.8547 | 388.1954 | 335.6123 | 404.4654
573.6849 | 511.6849 | 481.013 | 355.6867 | 323.1762 | 322.3596 | 379.0573 | 388.5766 | 335.6031 | 404.5286
574.6864 | 512.6864 | 480.9756 | 356.2392 | 323.7446 | 322.8841 | 379.248 | 388.9477 | 335.3734 | 404.5968
575.6878 | 513.6878 | 481.0425 | 356.7761 | 324.3419 | 323.381 | 379.4273 | 389.345 | 335.4202 | 404.6808
576.7393 | 514.7393 | 480.9298 | 357.3085 | 324.9505 | 323.9327 | 379.6278 | 389.6343 | 335.95 | 404.779
577.6807 | 515.6807 | 480.8711 | 357.7802 | 325.4991 | 324.4385 | 379.8145 | 389.9174 | 336.6644 | 404.855
578.6821 | 516.6821 | 480.7594 | 358.2366 | 326.0666 | 324.9704 | 379.9709 | 390.2494 | 336.5931 | 404.9058
579.6835 | 517.6835 | 480.7198 | 358.6936 | 326.6536 | 325.5418 | 380.1185 | 390.612 | 336.4423 | 404.9643
580.685 | 518.685 | 480.7392 | 359.1226 | 327.2518 | 326.0992 | 380.2802 | 390.9206 | 336.3918 | 405.0398
581.6864 | 519.6864 | 480.6584 | 359.5887 | 327.8242 | 326.6068 | 380.5206 | 391.2165 | 337.3691 | 405.1271
582.6879 | 520.6879 | 480.5308 | 360.0671 | 328.4187 | 327.1155 | 380.6954 | 391.454 | 337.9269 | 405.1796
583.6793 | 521.6793 | 480.4684 | 360.5348 | 328.9919 | 327.6484 | 380.8679 | 391.7583 | 336.9306 | 405.2637
584.6807 | 522.6807 | 480.3476 | 360.9976 | 329.5777 | 328.1786 | 380.9742 | 392.0841 | 336.7048 | 405.34
585.6822 | 523.6822 | 480.3818 | 361.3549 | 330.1706 | 328.7159 | 381.0672 | 392.4154 | 337.7023 | 405.4297
586.6836 | 524.6836 | 480.4657 | 361.7172 | 330.7528 | 329.2535 | 381.1848 | 392.7796 | 338.7737 | 405.5168
587.685 | 525.685 | 480.6109 | 362.0553 | 331.3462 | 329.7778 | 381.2207 | 393.1668 | 338.319 | 405.602
588.6865 | 526.6865 | 480.6259 | 362.377 | 331.9426 | 330.3509 | 381.2562 | 393.5696 | 338.5956 | 405.6674
589.6779 | 527.6779 | 480.687 | 362.7103 | 332.5252 | 330.9341 | 381.3075 | 393.9567 | 339.0965 | 405.7203
590.6794 | 528.6794 | 480.721 | 363.0415 | 333.1165 | 331.5322 | 381.3254 | 394.3204 | 338.9642 | 405.7718
591.6808 | 529.6808 | 480.7788 | 363.3873 | 333.6867 | 332.0971 | 381.3133 | 394.6268 | 338.5587 | 405.8428
592.6822 | 530.6822 | 480.6644 | 363.7497 | 334.2743 | 332.6627 | 381.3839 | 395.0127 | 339.0098 | 405.8855
593.6837 | 531.6837 | 480.618 | 364.108 | 334.8357 | 333.2258 | 381.4248 | 395.3645 | 339.3873 | 405.9563
594.6851 | 532.6851 | 480.4795 | 364.4876 | 335.4161 | 333.7986 | 381.5011 | 395.6675 | 339.7841 | 406.0249
595.6866 | 533.6866 | 480.4284 | 364.878 | 335.97 | 334.3682 | 381.6533 | 395.8727 | 340.3496 | 406.1074
596.688 | 534.688 | 480.3171 | 365.2682 | 336.521 | 334.9269 | 381.7752 | 396.1103 | 340.0128 | 406.1401
597.6894 | 535.6894 | 480.1926 | 365.6794 | 337.0571 | 335.4823 | 381.9292 | 396.2941 | 340.1466 | 406.191
598.6809 | 536.6809 | 480.2133 | 366.1136 | 337.6164 | 336.047 | 382.0875 | 396.4331 | 340.1777 | 406.2484
599.6823 | 537.6823 | 480.237 | 366.5581 | 338.1413 | 336.6207 | 382.2999 | 396.6725 | 340.0018 | 406.3148
600.6837 | 538.6837 | 480.1967 | 367.0127 | 338.6762 | 337.1801 | 382.5912 | 396.9594 | 340.3807 | 406.3866
601.6852 | 539.6852 | 480.1956 | 367.4825 | 339.2156 | 337.7321 | 382.8797 | 397.3058 | 340.4684 | 406.459
602.6866 | 540.6866 | 480.2189 | 367.9775 | 339.7425 | 338.2703 | 383.1564 | 397.5961 | 340.9411 | 406.5439
603.6881 | 541.6881 | 480.3122 | 368.4856 | 340.2787 | 338.7757 | 383.5145 | 397.7481 | 341.8849 | 406.6025
604.6795 | 542.6795 | 480.5024 | 369.0121 | 340.8116 | 339.2875 | 383.8828 | 397.9338 | 341.7017 | 406.6913
605.6809 | 543.6809 | 480.5041 | 369.5879 | 341.3441 | 339.778 | 384.2436 | 398.1495 | 341.2375 | 406.7742
606.6824 | 544.6824 | 480.474 | 370.1922 | 341.872 | 340.2909 | 384.6172 | 398.3519 | 340.848 | 406.8544
607.6838 | 545.6838 | 480.4982 | 370.8263 | 342.3922 | 340.8076 | 384.9719 | 398.5599 | 340.8726 | 406.9429
608.6852 | 546.6852 | 480.5202 | 371.4853 | 342.9225 | 341.3289 | 385.3321 | 398.7311 | 341.493 | 407.012
609.6867 | 547.6867 | 480.6571 | 372.1384 | 343.4378 | 341.8553 | 385.7058 | 398.892 | 341.6553 | 407.096
610.6781 | 548.6781 | 480.7865 | 372.8426 | 343.9647 | 342.375 | 386.0862 | 399.098 | 342.364 | 407.1798
611.6796 | 549.6796 | 480.8282 | 373.5516 | 344.4841 | 342.8533 | 386.4764 | 399.2552 | 342.8006 | 407.244
612.681 | 550.681 | 480.8121 | 374.2587 | 344.9951 | 343.3457 | 386.8685 | 399.4711 | 343.2979 | 407.3073
613.6824 | 551.6824 | 480.8373 | 374.9808 | 345.4963 | 343.8409 | 387.2742 | 399.5953 | 343.7228 | 407.3695
614.6839 | 552.6839 | 480.9102 | 375.7385 | 346.0027 | 344.3665 | 387.6769 | 399.7853 | 343.5461 | 407.4109
615.6853 | 553.6853 | 480.8054 | 376.5018 | 346.5088 | 344.9066 | 388.0735 | 400.03 | 342.723 | 407.479
616.6868 | 554.6868 | 480.7323 | 377.2717 | 347.0219 | 345.4457 | 388.4783 | 400.3613 | 342.5038 | 407.5445
617.6882 | 555.6882 | 480.5801 | 378.0717 | 347.5229 | 345.9743 | 388.9114 | 400.5456 | 342.0966 | 407.6116
618.6896 | 556.6896 | 480.4797 | 378.8777 | 348.0195 | 346.5278 | 389.3117 | 400.6728 | 341.9139 | 407.6949
619.6811 | 557.6811 | 480.4809 | 379.6912 | 348.5122 | 347.0762 | 389.7552 | 400.8565 | 341.7636 | 407.7795
620.6825 | 558.6825 | 480.5088 | 380.5272 | 348.9968 | 347.6106 | 390.2042 | 401.125 | 342.4943 | 407.8173
621.6839 | 559.6839 | 480.6977 | 381.229 | 349.4887 | 348.1361 | 390.6584 | 401.3712 | 343.1584 | 407.858
622.6854 | 560.6854 | 480.8916 | 381.6244 | 349.9915 | 348.6898 | 391.123 | 401.5607 | 343.1485 | 407.9088
623.7369 | 561.7369 | 480.9948 | 382.1712 | 350.5417 | 349.2691 | 391.6206 | 401.7383 | 342.8889 | 407.9757
624.6883 | 562.6883 | 481.0357 | 382.7215 | 351.039 | 349.795 | 392.1402 | 401.9226 | 342.6696 | 408.0843
625.6797 | 563.6797 | 481.052 | 383.3529 | 351.5374 | 350.3443 | 392.6656 | 402.0003 | 342.6678 | 408.1777
626.6811 | 564.6811 | 481.1464 | 384.023 | 352.0384 | 350.8763 | 393.2196 | 402.1006 | 343.7127 | 408.2466
627.6826 | 565.6826 | 481.0269 | 384.7147 | 352.5388 | 351.4158 | 393.7884 | 402.1934 | 343.2297 | 408.3166
628.684 | 566.684 | 481.0173 | 385.4157 | 353.0444 | 351.9369 | 394.3758 | 402.3685 | 344.6133 | 408.388
629.6854 | 567.6854 | 481.0931 | 386.1329 | 353.516 | 352.4659 | 394.9858 | 402.5438 | 344.7883 | 408.4656
630.6869 | 568.6869 | 481.1975 | 386.8602 | 353.9907 | 352.9946 | 395.5909 | 402.7643 | 345.4749 | 408.5572
631.6883 | 569.6883 | 481.2156 | 387.5876 | 354.4592 | 353.5112 | 396.2153 | 402.9967 | 345.8471 | 408.6388
632.6797 | 570.6797 | 481.3348 | 388.3457 | 354.9308 | 354.0436 | 396.8679 | 403.1667 | 345.4042 | 408.7286
633.6812 | 571.6812 | 481.2444 | 389.1272 | 355.4471 | 354.573 | 397.5385 | 403.2853 | 345.125 | 408.8135
634.6826 | 572.6826 | 481.302 | 389.9067 | 355.9449 | 355.0916 | 398.2221 | 403.3585 | 345.2736 | 408.9103
635.6841 | 573.6841 | 481.2285 | 390.69 | 356.4312 | 355.6075 | 398.8917 | 403.5561 | 344.8325 | 409.0018
636.6855 | 574.6855 | 481.1138 | 391.4991 | 356.9343 | 356.1241 | 399.5829 | 403.7461 | 345.7787 | 409.107
637.6869 | 575.6869 | 481.2397 | 392.3059 | 357.439 | 356.6411 | 400.282 | 403.9101 | 346.095 | 409.2094
638.6784 | 576.6784 | 481.1824 | 393.1386 | 357.929 | 357.1601 | 401.0041 | 403.9946 | 347.3651 | 409.3095
639.6898 | 577.6898 | 481.166 | 393.9601 | 358.3991 | 357.6825 | 401.741 | 404.1181 | 348.6355 | 409.4085
640.6813 | 578.6813 | 481.2437 | 394.7828 | 358.8948 | 358.2278 | 402.4594 | 404.2617 | 349.3077 | 409.5248
641.6827 | 579.6827 | 481.5914 | 395.615 | 359.4177 | 358.736 | 403.2216 | 404.4158 | 349.7051 | 409.6198
642.6841 | 580.6841 | 481.7665 | 396.4481 | 359.9446 | 359.2575 | 403.9874 | 404.5049 | 350.5166 | 409.7178
643.6856 | 581.6856 | 481.7273 | 397.2963 | 360.4526 | 359.764 | 404.751 | 404.6156 | 349.76 | 409.8384
644.687 | 582.687 | 481.6498 | 398.146 | 360.9489 | 360.2597 | 405.4966 | 404.6592 | 350.4839 | 409.9417
645.6885 | 583.6885 | 481.5782 | 399.0035 | 361.4294 | 360.762 | 406.2534 | 404.7035 | 351.6182 | 410.0433
646.6799 | 584.6799 | 481.3872 | 399.8667 | 361.9154 | 361.2487 | 407.0089 | 404.7029 | 352.2076 | 410.1583
647.6813 | 585.6813 | 481.3114 | 400.7254 | 362.4292 | 361.741 | 407.7664 | 404.747 | 352.8356 | 410.27
648.6828 | 586.6828 | 481.2246 | 401.5729 | 362.9205 | 362.226 | 408.5281 | 404.8666 | 352.9873 | 410.3735
649.6842 | 587.6842 | 481.3101 | 402.4168 | 363.416 | 362.7026 | 409.2752 | 404.9763 | 354.0567 | 410.4646
650.6856 | 588.6856 | 481.3349 | 403.2471 | 363.9222 | 363.1968 | 410.0162 | 405.076 | 354.7641 | 410.5626
651.6871 | 589.6871 | 481.451 | 404.07 | 364.4428 | 363.6812 | 410.771 | 405.1149 | 354.8724 | 410.6754
652.6785 | 590.6785 | 481.3321 | 404.8819 | 364.9454 | 364.1613 | 411.5155 | 405.1309 | 354.0445 | 410.7761
653.6799 | 591.6799 | 481.2415 | 405.6711 | 365.4693 | 364.6364 | 412.2543 | 405.2164 | 353.0752 | 410.8844
654.6814 | 592.6814 | 481.2212 | 406.4525 | 365.9802 | 365.1212 | 413.0261 | 405.334 | 353.9402 | 410.9777
655.6828 | 593.6828 | 481.2861 | 407.2559 | 366.5015 | 365.591 | 413.8007 | 405.4321 | 354.9971 | 411.0789
656.6843 | 594.6843 | 481.2215 | 408.0378 | 367.0203 | 366.0644 | 414.6019 | 405.5145 | 354.8909 | 411.1652
657.6857 | 595.6857 | 481.119 | 408.8243 | 367.5435 | 366.5078 | 415.3988 | 405.6009 | 355.8789 | 411.2276
658.6871 | 596.6871 | 481.0467 | 409.6087 | 368.0908 | 366.9793 | 416.2228 | 405.6711 | 356.2801 | 411.3031
659.6786 | 597.6786 | 481.1209 | 410.3962 | 368.6557 | 367.4509 | 417.1355 | 405.8095 | 359.6248 | 411.5996
660.69 | 598.69 | 481.1673 | 411.222 | 369.2477 | 367.9333 | 418.1415 | 405.9824 | 359.2972 | 412.031
661.6815 | 599.6815 | 481.1717 | 412.0965 | 369.9155 | 368.4202 | 419.2625 | 406.3364 | 364.2212 | 412.8094
662.6829 | 600.6829 | 481.341 | 413.0622 | 370.6451 | 368.9179 | 420.5454 | 407.011 | 367.3839 | 414.0679 | Approximate time of cable ignition
663.6843 | 601.6843 | 481.5366 | 414.1168 | 371.3667 | 369.3772 | 422.2217 | 407.8119 | 372.6393 | 415.8366
664.6858 | 602.6858 | 481.7205 | 415.449 | 372.0259 | 369.8213 | 424.3669 | 409.125 | 378.9005 | 418.1375
665.6872 | 603.6872 | 481.9899 | 416.9867 | 372.5101 | 370.3257 | 426.4711 | 411.0587 | 383.6992 | 421.0812
666.6887 | 604.6887 | 482.448 | 418.8149 | 373.0182 | 370.8746 | 428.6716 | 413.9862 | 395.8794 | 424.63
667.6801 | 605.6801 | 482.9226 | 420.8154 | 373.6059 | 371.4121 | 431.3571 | 417.9433 | 403.2631 | 428.2267
668.6815 | 606.6815 | 483.5603 | 422.9869 | 374.2459 | 371.9979 | 434.0534 | 422.9206 | 415.8927 | 432.0281
669.683 | 607.683 | 483.9199 | 425.6417 | 375.0384 | 372.547 | 436.5167 | 430.0427 | 427.0185 | 435.817
670.6844 | 608.6844 | 484.5493 | 429.074 | 375.8159 | 373.0763 | 439.1401 | 437.8047 | 443.3486 | 439.5727
671.6858 | 609.6858 | 484.7862 | 432.5793 | 376.6829 | 373.6786 | 441.6096 | 446.1267 | 456.2409 | 443.3023
672.6873 | 610.6873 | 484.9573 | 436.2374 | 377.6131 | 374.2804 | 444.2636 | 454.8804 | 455.3059 | 447.0311
673.6787 | 611.6787 | 485.2408 | 440.0473 | 378.6195 | 374.9494 | 447.1031 | 463.9874 | 457.9438 | 450.5754 | Time of first failure
674.6801 | 612.6801 | 485.362 | 443.9882 | 379.5998 | 375.6669 | 450.2462 | 473.8903 | 456.226 | 454.1878 | 612 | 0
675.6816 | 613.6816 | 485.5527 | 448.0037 | 380.6446 | 376.465 | 453.2862 | 485.233 | 458.8557 | 457.728 | 612 | 900
676.683 | 614.683 | 485.5582 | 452.1032 | 381.8108 | 377.2897 | 456.9904 | 496.1805 | 462.129 | 460.8866
677.6845 | 615.6845 | 485.4897 | 456.1435 | 383.0296 | 378.1672 | 460.4567 | 509.8507 | 465.8982 | 464.0399
678.6859 | 616.6859 | 485.3068 | 459.9044 | 384.2982 | 379.1513 | 464.2465 | 522.5354 | 468.4827 | 467.2608
679.6873 | 617.6873 | 484.9226 | 462.9019 | 385.6169 | 380.0902 | 467.8308 | 534.8421 | 471.5887 | 470.5263
680.6788 | 618.6788 | 484.5673 | 465.2605 | 387.062 | 381.2108 | 471.4851 | 544.88 | 474.7312 | 473.6925
681.6802 | 619.6802 | 484.344 | 467.0236 | 388.6517 | 382.3175 | 474.774 | 554.7317 | 478.7385 | 476.5757
682.6816 | 620.6816 | 484.1091 | 468.3808 | 390.4302 | 383.5078 | 477.7637 | 564.5186 | 482.3745 | 479.3635
683.6831 | 621.6831 | 483.8173 | 469.2299 | 392.3807 | 384.837 | 480.9963 | 564.8193 | 489.3435 | 482.0357
684.6845 | 622.6845 | 483.2711 | 469.3196 | 394.5019 | 386.1896 | 484.6017 | 565.7766 | 497.8481 | 484.7287
685.686 | 623.686 | 482.6937 | 468.9863 | 396.9223 | 387.5338 | 487.856 | 569.2693 | 505.7733 | 487.4037
686.6874 | 624.6874 | 482.2244 | 468.5201 | 399.4938 | 388.8011 | 490.4885 | 569.8724 | 515.3656 | 490.2786
687.6888 | 625.6888 | 481.8335 | 468.0612 | 402.0705 | 390.1271 | 492.4888 | 572.9345 | 526.2872 | 493.0403
688.6803 | 626.6803 | 481.4325 | 467.3528 | 404.5394 | 391.4307 | 494.8138 | 575.6041 | 529.3984 | 495.6141
689.6817 | 627.6817 | 480.9095 | 466.231 | 406.8633 | 392.7952 | 498.4272 | 578.5771 | 537.81 | 498.2318
690.6832 | 628.6832 | 480.287 | 465.1138 | 408.9986 | 394.1056 | 500.7642 | 582.6848 | 544.6952 | 500.5212
691.6846 | 629.6846 | 479.8649 | 463.9697 | 410.9214 | 395.4213 | 502.8954 | 587.3074 | 550.8997 | 502.9903
692.686 | 630.686 | 479.3083 | 462.9785 | 412.441 | 397.1052 | 504.8703 | 593.5442 | 556.2758 | 505.396
693.6875 | 631.6875 | 478.7254 | 462.1634 | 413.5504 | 399.3111 | 506.6732 | 599.5004 | 563.6956 | 507.8099
694.6789 | 632.6789 | 478.1999 | 460.763 | 414.9331 | 401.5875 | 508.1038 | 604.9726 | 569.4536 | 510.0595
695.6803 | 633.6803 | 477.5568 | 460.1788 | 416.5997 | 403.9519 | 508.4964 | 608.9561 | 574.8526 | 512.4171
696.6818 | 634.6818 | 476.9761 | 460.2667 | 418.2921 | 406.4113 | 509.1452 | 614.1365 | 575.6572 | 514.6242
697.6832 | 635.6832 | 476.4342 | 461.0923 | 419.911 | 409.0227 | 508.2136 | 617.8143 | 582.5845 | 517.0583
698.6847 | 636.6847 | 475.8852 | 462.2341 | 421.8899 | 411.6738 | 508.5235 | 618.3315 | 587.5174 | 519.4241
699.6861 | 637.6861 | 475.3477 | 463.8098 | 424.2365 | 414.5583 | 509.748 | 620.304 | 589.9712 | 521.6607
700.6875 | 638.6875 | 474.837 | 465.5384 | 426.8356 | 417.5936 | 510.4786 | 622.8263 | 593.3579 | 523.7152
701.689 | 639.689 | 474.3389 | 467.0448 | 429.9681 | 420.7911 | 510.3736 | 624.709 | 594.4934 | 525.6877
702.6804 | 640.6804 | 473.8197 | 469.0934 | 433.5553 | 424.05 | 510.071 | 626.0215 | 591.2108 | 527.5436
703.6818 | 641.6818 | 473.4918 | 470.9993 | 437.5494 | 427.5041 | 510.3077 | 626.0731 | 593.8055 | 529.2151
704.6833 | 642.6833 | 473.0439 | 473.0024 | 441.9235 | 431.0237 | 510.4541 | 627.492 | 596.56 | 530.8304
705.6847 | 643.6847 | 472.5751 | 475.0427 | 446.6669 | 434.5002 | 510.0418 | 627.6824 | 599.5139 | 532.4083
706.6862 | 644.6862 | 472.0872 | 476.9757 | 451.9328 | 437.9102 | 509.479 | 627.5747 | 601.1442 | 533.9813
707.6876 | 645.6876 | 471.5655 | 478.5788 | 457.7836 | 441.2959 | 508.3391 | 627.4133 | 605.0752 | 535.5746
708.689 | 646.689 | 471.0783 | 479.9786 | 463.8819 | 444.669 | 506.8859 | 628.2079 | 607.0615 | 537.089
709.6805 | 647.6805 | 470.4868 | 481.2851 | 470.4213 | 448.1349 | 505.4843 | 630.0957 | 608.5273 | 538.7774
710.6819 | 648.6819 | 470.0133 | 482.376 | 476.6547 | 451.6427 | 504.5498 | 629.8568 | 610.0009 | 540.3709
711.6834 | 649.6834 | 469.4565 | 483.2435 | 482.6831 | 454.9754 | 503.4913 | 628.8048 | 612.2749 | 541.7619
712.6848 | 650.6848 | 468.8782 | 483.9122 | 489.2105 | 458.1032 | 502.3683 | 626.7794 | 613.5333 | 543.1745
713.6862 | 651.6862 | 468.4214 | 484.4276 | 495.102 | 460.9168 | 501.5121 | 623.9537 | 616.0038 | 544.5947
714.6877 | 652.6877 | 467.9336 | 484.7788 | 500.101 | 463.1153 | 500.6144 | 622.4554 | 615.6029 | 545.6821
715.6791 | 653.6791 | 467.3197 | 484.8895 | 504.2173 | 464.8007 | 499.9418 | 620.6338 | 617.5835 | 546.7428
716.6805 | 654.6805 | 466.7758 | 485.0784 | 507.3401 | 466.2509 | 498.8308 | 616.8583 | 618.9051 | 547.7873
717.682 | 655.682 | 466.1849 | 485.1118 | 509.8027 | 467.8324 | 497.8171 | 616.9941 | 620.0683 | 548.7432
718.6834 | 656.6834 | 465.6116 | 485.4283 | 512.5605 | 469.6672 | 495.9207 | 615.5121 | 620.7846 | 549.8386
719.6849 | 657.6849 | 464.9495 | 485.4694 | 514.3237 | 472.0601 | 494.5195 | 615.4167 | 621.1161 | 551.0367
720.6863 | 658.6863 | 464.3771 | 485.6316 | 515.6466 | 475.1882 | 493.2555 | 615.2915 | 619.0947 | 552.2303
721.6877 | 659.6877 | 463.7626 | 486.9678 | 516.8204 | 478.445 | 492.3096 | 613.8119 | 620.1617 | 553.4638
722.6792 | 660.6792 | 463.1278 | 489.1104 | 517.2752 | 481.3577 | 491.5597 | 614.0889 | 621.8416 | 554.359
723.6806 | 661.6806 | 462.4905 | 491.9257 | 517.2307 | 485.3493 | 491.0122 | 612.9258 | 623.4077 | 555.251
724.682 | 662.682 | 461.913 | 494.8155 | 517.0368 | 501.9359 | 491.3557 | 610.5754 | 627.6663 | 556.1941
725.6835 | 663.6835 | 461.4213 | 497.6767 | 517.1963 | 517.8268 | 492.0078 | 611.0251 | 627.8662 | 557.1425
726.6849 | 664.6849 | 460.8566 | 500.1617 | 517.6944 | 531.7412 | 492.6065 | 610.9195 | 624.0204 | 557.8271
727.6864 | 665.6864 | 460.3473 | 502.5412 | 518.3804 | 541.6451 | 493.8549 | 609.7222 | 624.9905 | 558.5132
728.6878 | 666.6878 | 459.8496 | 505.4139 | 518.5137 | 550.2328 | 493.9375 | 609.4272 | 630.0878 | 559.5276
729.6892 | 667.6892 | 459.3598 | 507.7281 | 518.5145 | 558.6001 | 494.5421 | 605.4731 | 631.9998 | 560.4999
730.6807 | 668.6807 | 458.9632 | 509.4459 | 519.0724 | 568.6527 | 495.9234 | 605.0285 | 628.592 | 561.6071
731.6821 | 669.6821 | 458.6315 | 511.1546 | 520.1683 | 578.8777 | 497.1382 | 603.4744 | 623.8614 | 562.6032
732.6835 | 670.6835 | 458.2142 | 512.9015 | 520.8843 | 588.3478 | 497.6566 | 602.058 | 622.2185 | 563.8692
733.685 | 671.685 | 457.7349 | 514.3973 | 521.5232 | 596.8959 | 498.2587 | 600.5102 | 617.1311 | 565.1197
734.6864 | 672.6864 | 457.391 | 515.7291 | 522.4551 | 601.9349 | 498.9995 | 599.1672 | 612.6764 | 566.1935
735.6879 | 673.6879 | 456.8932 | 517.3169 | 523.1334 | 607.0311 | 499.9245 | 598.4892 | 606.7587 | 567.6365
736.6793 | 674.6793 | 456.3427 | 519.076 | 524.0522 | 613.4943 | 501.4014 | 597.38 | 606.1765 | 568.8777
737.6807 | 675.6807 | 455.7345 | 520.9908 | 525.102 | 616.2646 | 503.3459 | 595.2507 | 603.4288 | 569.7695
738.6822 | 676.6822 | 455.3273 | 523.3573 | 526.35 | 618.4748 | 505.7686 | 594.9675 | 599.7778 | 570.6972
739.6836 | 677.6836 | 454.8861 | 525.7958 | 527.5938 | 623.2623 | 508.8099 | 595.2007 | 595.9481 | 571.5028
740.6851 | 678.6851 | 454.3123 | 528.2673 | 528.9195 | 626.4652 | 511.5508 | 593.8166 | 593.3193 | 572.4078
741.6865 | 679.6865 | 453.7105 | 530.8293 | 530.5758 | 627.7748 | 514.1461 | 592.5335 | 587.0703 | 572.8423
742.6879 | 680.6879 | 453.1841 | 533.3978 | 532.1449 | 629.4289 | 516.4679 | 591.0935 | 582.8663 | 573.192
743.6794 | 681.6794 | 452.7092 | 535.8176 | 533.6195 | 632.7538 | 518.2267 | 591.2811 | 580.8607 | 573.7327
744.6808 | 682.6808 | 452.1312 | 538.1628 | 535.2555 | 635.2664 | 520.2951 | 591.6965 | 577.5847 | 573.9958
745.6822 | 683.6822 | 451.6087 | 540.3669 | 536.8076 | 639.4788 | 522.2143 | 591.3715 | 573.8495 | 574.1636
746.6837 | 684.6837 | 451.0976 | 542.4985 | 538.2065 | 642.0497 | 524.1617 | 591.1485 | 570.8737 | 574.1773
747.6851 | 685.6851 | 450.5181 | 544.6982 | 540.5499 | 642.1111 | 525.7034 | 591.9346 | 568.6081 | 574.025
748.6866 | 686.6866 | 449.9478 | 546.9307 | 542.4245 | 645.8958 | 527.8369 | 590.7618 | 564.4111 | 573.7676
749.688 | 687.688 | 449.3336 | 549.3306 | 543.662 | 651.0252 | 530.1242 | 592.0513 | 561.5144 | 573.6374
750.6794 | 688.6794 | 448.7957 | 551.2812 | 544.9179 | 656.581 | 533.7379 | 592.5095 | 558.5006 | 573.5027
751.6809 | 689.6809 | 448.3372 | 553.0097 | 546.1778 | 660.3192 | 536.8028 | 593.9369 | 556.2552 | 573.3929
752.6823 | 690.6823 | 447.9534 | 554.7354 | 547.5766 | 661.539 | 542.0512 | 593.5826 | 553.965 | 573.3292
753.6837 | 691.6837 | 447.4802 | 556.3776 | 549.0732 | 661.2773 | 548.751 | 592.8084 | 551.177 | 573.2847
754.6852 | 692.6852 | 446.868 | 557.9014 | 550.5894 | 659.3219 | 553.8991 | 592.0527 | 549.7116 | 573.1815
755.6866 | 693.6866 | 446.1823 | 559.4291 | 552.0607 | 659.7561 | 558.3871 | 591.546 | 548.412 | 573.0439
756.6881 | 694.6881 | 445.4586 | 560.994 | 553.7674 | 658.9207 | 562.1871 | 589.6495 | 548.2738 | 572.8989
757.7496 | 695.7496 | 444.8043 | 562.6149 | 555.2082 | 656.2276 | 565.8902 | 588.9919 | 547.498 | 572.6942
758.6809 | 696.6809 | 444.1856 | 563.8937 | 556.3556 | 654.1456 | 568.7785 | 587.8575 | 546.0078 | 572.497
759.6824 | 697.6824 | 443.5534 | 565.2245 | 557.9087 | 651.1314 | 570.997 | 586.3246 | 546.1411 | 572.249
760.6838 | 698.6838 | 442.9505 | 566.5934 | 559.3658 | 648.2507 | 572.4457 | 585.1983 | 545.0892 | 571.9539
761.6852 | 699.6852 | 442.3451 | 567.9165 | 560.7235 | 647.1439 | 573.7655 | 583.1186 | 544.4455 | 571.6234
762.6867 | 700.6867 | 441.7546 | 569.131 | 561.9581 | 645.7105 | 574.9974 | 581.8821 | 542.3883 | 571.1453
763.6781 | 701.6781 | 441.1249 | 570.2693 | 563.22 | 645.3672 | 576.4633 | 580.8952 | 540.7919 | 570.6447
764.6796 | 702.6796 | 440.5309 | 571.3801 | 564.1991 | 645.0311 | 579.0854 | 579.7771 | 539.3505 | 570.1746
765.681 | 703.681 | 439.9536 | 572.4478 | 565.2248 | 643.2085 | 580.9832 | 579.3318 | 537.5944 | 569.7071
766.6824 | 704.6824 | 439.2803 | 573.4151 | 566.527 | 640.2259 | 582.4823 | 579.5455 | 535.4599 | 569.1435
767.6839 | 705.6839 | 438.6758 | 574.3287 | 567.6103 | 637.8195 | 584.39 | 579.2084 | 535.4936 | 568.5843
768.6853 | 706.6853 | 438.1205 | 575.2152 | 568.5696 | 636.4894 | 587.1802 | 578.2313 | 534.7798 | 567.9227
769.6868 | 707.6868 | 437.515 | 576.0842 | 569.6755 | 633.8546 | 588.6101 | 578.0839 | 532.0584 | 567.1934
770.6882 | 708.6882 | 436.8806 | 576.9651 | 570.6497 | 631.053 | 589.8337 | 577.7169 | 534.4565 | 566.4347
771.6796 | 709.6796 | 436.1888 | 577.7975 | 571.6203 | 629.3196 | 591.9585 | 577.0835 | 533.3568 | 565.6568
772.6811 | 710.6811 | 435.5846 | 578.506 | 572.5297 | 626.9674 | 593.7058 | 576.5553 | 531.6328 | 564.8238
773.6825 | 711.6825 | 435.0568 | 579.4167 | 573.4213 | 624.1626 | 593.9177 | 575.2033 | 530.8739 | 564.0469
774.6839 | 712.6839 | 434.5197 | 580.2257 | 574.3337 | 620.5159 | 593.6602 | 574.7737 | 531.0895 | 563.2281
775.6854 | 713.6854 | 433.8672 | 580.9747 | 575.2252 | 617.5163 | 593.5612 | 573.9094 | 533.7723 | 562.4317
776.6868 | 714.6868 | 433.2112 | 581.7401 | 576.1299 | 615.4485 | 593.8075 | 574.208 | 531.4802 | 561.6116
777.6883 | 715.6883 | 432.5739 | 582.4695 | 577.2855 | 613.069 | 596.0664 | 574.0641 | 529.3216 | 560.737
778.6797 | 716.6797 | 431.897 | 583.2823 | 578.1036 | 610.5822 | 597.4668 | 574.6035 | 526.7773 | 559.8264
779.6811 | 717.6811 | 431.4286 | 584.0415 | 578.8711 | 608.0943 | 597.8947 | 574.8852 | 525.8263 | 558.8742
780.6826 | 718.6826 | 430.8332 | 584.7633 | 579.8039 | 606.1305 | 598.4541 | 575.1467 | 524.582 | 557.9181
781.684 | 719.684 | 430.2199 | 585.5403 | 580.8358 | 603.4646 | 598.96 | 574.9249 | 523.9314 | 556.92
782.6854 | 720.6854 | 429.7843 | 586.2993 | 581.647 | 600.9596 | 599.3202 | 575.209 | 522.0092 | 555.9086
783.6869 | 721.6869 | 429.2581 | 586.9912 | 582.4632 | 598.9479 | 600.0072 | 575.4443 | 521.3414 | 554.8458
784.6783 | 722.6783 | 428.8086 | 587.7644 | 583.4341 | 596.5982 | 600.2473 | 574.7788 | 521.8077 | 553.791
785.6798 | 723.6798 | 428.2666 | 588.4642 | 584.4235 | 594.068 | 600.4305 | 574.6885 | 522.5546 | 552.6982
786.6812 | 724.6812 | 427.7584 | 589.1068 | 585.4343 | 591.4906 | 600.7402 | 575.1432 | 522.7659 | 551.5396
787.6826 | 725.6826 | 427.2423 | 589.9521 | 586.1523 | 589.6449 | 602.3133 | 575.5123 | 520.9813 | 550.4616
788.6841 | 726.6841 | 426.7505 | 590.701 | 587.0169 | 587.6334 | 604.1154 | 576.3256 | 518.5947 | 549.3242
789.6855 | 727.6855 | 426.1342 | 591.4354 | 587.6489 | 585.3401 | 605.7271 | 576.1884 | 518.0523 | 548.1439
790.687 | 728.687 | 425.4616 | 592.1528 | 588.3173 | 583.3666 | 607.2826 | 575.8117 | 519.233 | 546.9663
791.6884 | 729.6884 | 424.8475 | 592.9507 | 589.0318 | 581.216 | 609.0077 | 576.678 | 516.5992 | 545.7707
792.6898 | 730.6898 | 424.2121 | 593.7725 | 589.8361 | 578.4898 | 609.7544 | 577.7663 | 514.7953 | 544.6195
793.6813 | 731.6813 | 423.5053 | 594.6197 | 590.5901 | 576.098 | 610.6332 | 577.8375 | 515.6907 | 543.4555
794.6827 | 732.6827 | 422.7956 | 595.5471 | 591.6271 | 573.6851 | 611.7514 | 578.5559 | 515.6256 | 542.2507
795.6841 | 733.6841 | 422.1157 | 596.3595 | 592.7919 | 571.4582 | 613.4571 | 579.8195 | 513.7113 | 541.0311
796.6856 | 734.6856 | 421.3843 | 597.1906 | 593.4153 | 569.3446 | 614.7428 | 581.0334 | 511.5162 | 539.7943
797.687 | 735.687 | 420.7311 | 598.1277 | 594.2252 | 567.1496 | 615.4699 | 582.3976 | 509.5051 | 538.5804
798.6885 | 736.6885 | 420.0758 | 599.1191 | 594.9355 | 565.0473 | 616.1809 | 583.1857 | 508.0861 | 537.4105
799.6799 | 737.6799 | 419.5356 | 600.0169 | 595.7752 | 562.9292 | 617.6452 | 584.8421 | 507.3346 | 536.1991
800.6813 | 738.6813 | 419.1168 | 600.938 | 596.7387 | 561.2936 | 619.4399 | 586.1363 | 506.9432 | 534.9982
801.6828 | 739.6828 | 418.5244 | 601.7367 | 597.3863 | 559.5342 | 620.2337 | 587.6028 | 507.1886 | 533.8073
802.6842 | 740.6842 | 417.9311 | 602.6191 | 598.0513 | 557.8093 | 621.4021 | 588.8674 | 506.5001 | 532.5913
803.6957 | 741.6957 | 417.3332 | 603.4807 | 598.9339 | 555.9585 | 623.0904 | 590.2874 | 505.8226 | 531.3829
804.6871 | 742.6871 | 416.7025 | 604.1604 | 599.5267 | 554.5208 | 623.5752 | 591.3784 | 505.5245 | 530.2192
805.6885 | 743.6885 | 416.0177 | 604.995 | 600.3038 | 553.0514 | 624.1772 | 591.866 | 505.6785 | 529.0119
806.6799 | 744.6799 | 415.3587 | 605.817 | 601.1333 | 551.5268 | 625.4722 | 592.2132 | 507.8568 | 527.8275
807.6814 | 745.6814 | 414.7039 | 606.4989 | 601.6129 | 550.18 | 626.5279 | 593.6719 | 506.9552 | 526.665
808.6828 | 746.6828 | 414.0786 | 607.0913 | 602.3208 | 548.8255 | 627.2252 | 594.5088 | 506.9166 | 525.4952
809.6843 | 747.6843 | 413.3949 | 607.671 | 602.9303 | 547.5083 | 628.0554 | 594.9914 | 510.9537 | 524.3371
810.6857 | 748.6857 | 412.7895 | 608.4134 | 603.5531 | 546.2444 | 628.214 | 595.5121 | 514.2915 | 523.2021
811.6871 | 749.6871 | 412.2046 | 609.031 | 604.235 | 544.7211 | 629.3996 | 596.2752 | 514.3383 | 522.0717
812.6886 | 750.6886 | 411.5346 | 609.5948 | 604.797 | 543.4539 | 629.7913 | 596.3516 | 518.5021 | 520.934
813.69 | 751.69 | 410.8694 | 610.0989 | 605.4152 | 542.3087 | 630.7875 | 597.1035 | 516.6304 | 519.8215
814.6815 | 752.6815 | 410.227 | 610.5917 | 606.0385 | 541.136 | 631.264 | 597.2554 | 516.5767 | 518.7059
815.6829 | 753.6829 | 409.6535 | 611.0586 | 606.4867 | 540.0798 | 631.2914 | 598.0405 | 515.6023 | 517.5889
816.6843 | 754.6843 | 409.115 | 611.4486 | 606.9947 | 539.0021 | 632.6469 | 598.7965 | 515.9756 | 516.4768
817.6858 | 755.6858 | 408.5963 | 611.6059 | 608.0567 | 538.0026 | 632.7797 | 598.7056 | 519.0075 | 515.3247
818.6872 | 756.6872 | 407.9874 | 612.0315 | 608.3976 | 537.0143 | 632.6276 | 598.7757 | 520.368 | 514.2057
819.6887 | 757.6887 | 407.501 | 612.4797 | 608.7452 | 536.0329 | 632.5738 | 599.9052 | 521.6299 | 513.0735
820.6801 | 758.6801 | 406.9966 | 612.9681 | 609.0483 | 535.0461 | 632.8984 | 599.9985 | 522.5231 | 511.9511
821.6815 | 759.6815 | 406.4334 | 613.232 | 609.5825 | 534.1054 | 633.249 | 600.8634 | 523.5329 | 510.8151
822.683 | 760.683 | 405.8303 | 613.4679 | 609.9439 | 533.1019 | 633.5884 | 601.8799 | 523.4389 | 509.6717
823.6844 | 761.6844 | 405.1846 | 613.8414 | 610.6044 | 532.2137 | 634.4137 | 602.0069 | 526.0424 | 508.5698
824.6858 | 762.6858 | 404.5522 | 614.2217 | 610.9954 | 531.4251 | 633.9776 | 602.3293 | 527.9747 | 507.4454
825.6873 | 763.6873 | 403.959 | 614.5696 | 611.5003 | 530.5051 | 633.2561 | 601.9823 | 531.0013 | 506.3391
826.6787 | 764.6787 | 403.4164 | 614.9902 | 611.9429 | 529.3086 | 632.8109 | 602.3021 | 532.6382 | 505.2317
827.6801 | 765.6801 | 402.7996 | 615.2787 | 612.1784 | 528.2147 | 632.2352 | 601.9335 | 533.1169 | 504.1332
828.6816 | 766.6816 | 402.1916 | 615.5062 | 612.6128 | 527.2259 | 631.684 | 601.6172 | 533.854 | 503.0008
829.683 | 767.683 | 401.6578 | 615.761 | 612.9522 | 526.451 | 631.2061 | 601.1663 | 534.1397 | 501.8972
830.6845 | 768.6845 | 401.1196 | 615.9576 | 613.2519 | 525.498 | 630.2012 | 600.8253 | 537.0614 | 500.794
831.6859 | 769.6859 | 400.5832 | 615.9971 | 613.5895 | 524.3399 | 629.2225 | 600.871 | 538.1435 | 499.8146
832.6873 | 770.6873 | 399.9474 | 616.0964 | 613.9909 | 523.5072 | 628.0816 | 600.8923 | 539.4348 | 498.7265
833.6888 | 771.6888 | 399.3417 | 616.3 | 614.605 | 522.5274 | 626.9758 | 601.1807 | 540.3993 | 497.6248
834.6902 | 772.6902 | 398.6693 | 616.4398 | 614.6464 | 521.6772 | 625.2325 | 601.1127 | 540.9724 | 496.5377
835.6817 | 773.6817 | 398.0539 | 616.7337 | 614.4506 | 520.9648 | 623.646 | 601.1411 | 542.6825 | 495.4318
836.6831 | 774.6831 | 397.4541 | 616.9776 | 614.6801 | 519.8154 | 622.1772 | 601.3916 | 544.0309 | 494.3595
837.6845 | 775.6845 | 396.7696 | 617.1448 | 614.9641 | 518.9556 | 620.2522 | 601.0718 | 545.2274 | 493.2736
838.686 | 776.686 | 396.2092 | 617.2896 | 615.0132 | 518.2188 | 618.1824 | 600.8253 | 547.291 | 492.1662
839.6874 | 777.6874 | 395.6461 | 617.4452 | 614.8887 | 517.4811 | 616.2518 | 600.7141 | 547.9679 | 491.0933
840.6889 | 778.6889 | 395.094 | 617.6065 | 615.0383 | 516.7277 | 613.521 | 600.7059 | 549.149 | 490.0112
841.6803 | 779.6803 | 394.5398 | 617.7727 | 614.8646 | 515.9306 | 611.04 | 600.5693 | 550.8317 | 488.9185
842.6817 | 780.6817 | 393.8226 | 617.9028 | 614.6417 | 515.1103 | 608.6412 | 600.6646 | 551.9846 | 487.8528
843.6832 | 781.6832 | 393.1436 | 617.9689 | 614.6896 | 514.3654 | 606.0842 | 600.2959 | 553.9502 | 486.7788
844.6846 | 782.6846 | 392.6146 | 618.0681 | 614.7347 | 513.7196 | 603.5673 | 599.942 | 555.3282 | 485.7136
845.686 | 783.686 | 392.1069 | 618.2901 | 614.5352 | 512.9115 | 601.1741 | 599.8426 | 556.8301 | 484.6771
846.6875 | 784.6875 | 391.5619 | 618.5265 | 614.3274 | 512.1507 | 598.7533 | 599.6372 | 557.993 | 483.6348
847.6789 | 785.6789 | 391.0437 | 618.4791 | 614.2535 | 511.4411 | 596.4365 | 599.6408 | 558.948 | 482.5783
848.6904 | 786.6904 | 390.5758 | 618.5934 | 614.1737 | 510.6399 | 594.0912 | 599.8011 | 560.5906 | 481.5123
849.6818 | 787.6818 | 390.0995 | 618.7376 | 614.0576 | 509.8754 | 591.9255 | 599.8945 | 562.8665 | 480.4608
850.6832 | 788.6832 | 389.5516 | 618.783 | 613.6621 | 509.0794 | 589.7244 | 599.7934 | 565.1567 | 479.4119
851.6847 | 789.6847 | 388.9419 | 618.6079 | 613.1242 | 508.3284 | 587.572 | 599.9631 | 567.8321 | 478.3544
852.6861 | 790.6861 | 388.4145 | 618.5087 | 612.9018 | 507.5456 | 585.4611 | 599.7098 | 569.0976 | 477.3074
853.6875 | 791.6875 | 387.7922 | 618.5627 | 612.574 | 506.7585 | 583.3871 | 599.3044 | 570.0252 | 476.2889
854.689 | 792.689 | 387.1869 | 618.6511 | 612.2908 | 505.9595 | 581.433 | 599.2579 | 572.1748 | 475.2543
855.6804 | 793.6804 | 386.5814 | 618.811 | 611.795 | 505.103 | 579.626 | 599.3916 | 572.487 | 474.2205
856.6818 | 794.6818 | 385.9971 | 619.0257 | 611.3812 | 504.4103 | 577.9281 | 599.3296 | 573.9701 | 473.2234
857.6833 | 795.6833 | 385.4308 | 619.135 | 610.9018 | 503.6155 | 576.2569 | 599.2894 | 574.6096 | 472.2129
858.6847 | 796.6847 | 384.8427 | 619.0705 | 610.5605 | 502.7775 | 574.7272 | 598.6725 | 574.8817 | 471.1989
859.6862 | 797.6862 | 384.2118 | 618.7756 | 610.1774 | 501.9072 | 573.2372 | 598.4872 | 574.3586 | 470.1846
860.6876 | 798.6876 | 383.6439 | 618.9106 | 609.5119 | 501.1194 | 571.871 | 597.7531 | 574.5002 | 469.1873
861.679 | 799.679 | 383.1074 | 619.3128 | 608.9919 | 500.3586 | 570.5729 | 597.3702 | 573.4991 | 468.1865
862.6805 | 800.6805 | 382.476 | 619.5936 | 608.7073 | 499.7107 | 569.3338 | 597.1196 | 571.5649 | 467.2089
863.6819 | 801.6819 | 381.8725 | 619.6746 | 608.1509 | 498.9059 | 568.0833 | 597.415 | 569.7476 | 466.1946
864.6834 | 802.6834 | 381.3061 | 619.9572 | 607.665 | 498.1895 | 566.8759 | 596.7798 | 568.6942 | 465.1946
865.6848 | 803.6848 | 380.7787 | 619.9216 | 607.1721 | 497.3573 | 565.6809 | 596.0285 | 567.682 | 464.2069
866.6862 | 804.6862 | 380.1921 | 619.7961 | 606.6355 | 496.5411 | 564.5112 | 595.7964 | 566.6289 | 463.2375
867.6877 | 805.6877 | 379.5623 | 619.814 | 606.0797 | 495.7295 | 563.4504 | 595.6053 | 565.557 | 462.2395
868.6791 | 806.6791 | 378.9904 | 620.0415 | 605.6484 | 494.9028 | 562.2057 | 594.9499 | 564.8693 | 461.2783
869.6805 | 807.6805 | 378.4474 | 620.1476 | 605.1223 | 494.081 | 561.129 | 594.3388 | 564.2806 | 460.324
870.682 | 808.682 | 377.9435 | 620.2882 | 604.5555 | 493.2628 | 560.0728 | 594.3071 | 563.1911 | 459.3655
871.6834 | 809.6834 | 377.4162 | 620.4315 | 603.9924 | 492.4551 | 559.0717 | 593.9097 | 562.3886 | 458.3967
872.6849 | 810.6849 | 376.8918 | 620.7271 | 603.4121 | 491.6022 | 558.0137 | 593.9431 | 562.2395 | 457.4302
873.6863 | 811.6863 | 376.3676 | 621.2325 | 602.7791 | 490.7275 | 557.0428 | 593.4936 | 561.5565 | 456.4732
874.6877 | 812.6877 | 375.8754 | 621.7447 | 602.1588 | 489.9548 | 556.1032 | 593.2127 | 560.9999 | 455.5151
875.6892 | 813.6892 | 375.2441 | 622.0623 | 601.5643 | 489.0708 | 555.2166 | 592.9401 | 560.3158 | 454.5391
876.6806 | 814.6806 | 374.6035 | 622.2091 | 600.9348 | 488.2295 | 554.4169 | 592.675 | 559.4713 | 453.5662
877.682 | 815.682 | 374.042 | 622.4045 | 600.3152 | 487.3364 | 553.331 | 592.1708 | 558.5358 | 452.6419
878.6835 | 816.6835 | 373.5794 | 622.4677 | 599.7286 | 486.4441 | 552.4209 | 592.0195 | 557.6226 | 451.678
879.6849 | 817.6849 | 373.0398 | 622.7628 | 599.1023 | 485.5343 | 551.4552 | 591.5203 | 556.4765 | 450.7173
880.6864 | 818.6864 | 372.4826 | 622.9852 | 598.5386 | 484.6777 | 550.5162 | 591.1797 | 555.5376 | 449.7774
881.6878 | 819.6878 | 371.9779 | 623.0146 | 598.0277 | 483.6837 | 549.7409 | 591.0317 | 554.3783 | 448.825
882.6892 | 820.6892 | 371.4806 | 623.0354 | 597.5763 | 482.9025 | 548.6915 | 590.0824 | 552.9421 | 447.9045
883.6807 | 821.6807 | 370.9588 | 622.7629 | 597.0868 | 482.0682 | 547.7901 | 589.2183 | 552.541 | 446.9634
884.6821 | 822.6821 | 370.5365 | 622.3771 | 596.7698 | 481.179 | 547.4389 | 589.4249 | 551.5255 | 445.9573
885.6836 | 823.6836 | 370.0826 | 622.2811 | 596.2094 | 480.2774 | 545.8922 | 588.4204 | 550.2241 | 445.0854
886.685 | 824.685 | 369.6201 | 622.117 | 595.7574 | 479.3698 | 544.9746 | 588.0263 | 548.889 | 444.1469
887.6864 | 825.6864 | 369.1673 | 622.1722 | 595.4389 | 478.5345 | 544.138 | 587.3879 | 548.2405 | 443.209
888.6879 | 826.6879 | 368.7025 | 621.7616 | 595.0138 | 477.7175 | 543.3039 | 586.6417 | 547.6113 | 442.2875
889.6793 | 827.6793 | 368.2267 | 621.8174 | 594.5612 | 476.8125 | 542.4577 | 586.1373 | 546.0137 | 441.3503
890.6807 | 828.6807 | 367.795 | 621.6231 | 594.1071 | 475.7636 | 541.6612 | 585.6087 | 545.2568 | 440.407
891.6822 | 829.6822 | 367.3318 | 621.437 | 593.5629 | 474.7606 | 540.5679 | 584.7161 | 544.4473 | 439.528
892.6836 | 830.6836 | 366.8436 | 621.3191 | 593.0113 | 473.8353 | 539.6268 | 584.1232 | 543.1812 | 438.6071
893.6851 | 831.6851 | 366.2871 | 621.3891 | 592.5301 | 472.9418 | 538.6723 | 583.4857 | 542.1719 | 437.7081
894.6865 | 832.6865 | 365.7241 | 621.0631 | 592.0229 | 472.1351 | 537.7113 | 582.6856 | 541.0175 | 436.8072
895.6779 | 833.6779 | 365.0962 | 620.6729 | 591.4459 | 471.3111 | 536.8243 | 582.0711 | 540.2452 | 435.9059
896.6894 | 834.6894 | 364.5289 | 620.4811 | 590.8321 | 470.5031 | 535.9584 | 581.5304 | 539.6272 | 435.0217
897.6808 | 835.6808 | 364.034 | 620.7021 | 590.162 | 469.6735 | 535.0306 | 580.9066 | 538.6632 | 434.1527
898.6822 | 836.6822 | 363.5318 | 620.4531 | 589.4809 | 468.7819 | 534.0836 | 580.6205 | 537.1451 | 433.261
899.6837 | 837.6837 | 362.9767 | 620.4644 | 588.8305 | 467.6351 | 533.1384 | 580.3005 | 536.5836 | 432.3663
900.6851 | 838.6851 | 362.4083 | 620.427 | 588.0915 | 466.6788 | 532.1541 | 579.7996 | 535.5673 | 431.4878
901.6866 | 839.6866 | 361.8462 | 620.237 | 587.4058 | 465.6654 | 531.378 | 579.3397 | 534.3344 | 430.589
902.688 | 840.688 | 361.3108 | 620.024 | 586.7065 | 464.7026 | 530.1842 | 578.282 | 533.4487 | 429.7199
903.6794 | 841.6794 | 360.8809 | 619.4104 | 585.9413 | 463.5569 | 529.1314 | 577.5404 | 531.9361 | 428.8244
904.6809 | 842.6809 | 360.553 | 619.2144 | 585.0497 | 462.5498 | 528.1149 | 577.1268 | 531.2284 | 427.9055
905.6823 | 843.6823 | 360.1783 | 619.0247 | 584.1298 | 461.5031 | 527.0265 | 576.8884 | 530.5496 | 427.0237
906.6837 | 844.6837 | 359.8652 | 618.6798 | 583.2731 | 460.1571 | 525.9385 | 576.473 | 529.631 | 426.124
907.6852 | 845.6852 | 359.5581 | 618.2394 | 582.45 | 459.0873 | 524.6585 | 576.0609 | 528.5607 | 425.2237
908.6866 | 846.6866 | 359.1709 | 617.926 | 581.5162 | 458.0474 | 523.356 | 575.6521 | 527.6546 | 424.3284
909.6881 | 847.6881 | 358.7634 | 617.6931 | 580.6702 | 456.9348 | 521.9169 | 575.3117 | 526.4083 | 423.4433
910.6795 | 848.6795 | 358.2807 | 617.2872 | 579.6382 | 455.8153 | 520.5962 | 574.9349 | 525.5104 | 422.5668
911.6809 | 849.6809 | 357.8218 | 616.7721 | 578.6534 | 454.7368 | 519.2185 | 574.2827 | 524.0334 | 421.6874
912.6824 | 850.6824 | 357.3514 | 616.0971 | 577.643 | 453.569 | 517.8434 | 573.6053 | 522.8678 | 420.8217
913.6838 | 851.6838 | 356.8988 | 615.3564 | 576.5643 | 452.5075 | 516.4875 | 572.9994 | 521.9388 | 419.9571
914.6853 | 852.6853 | 356.3956 | 614.9011 | 575.418 | 451.5094 | 515.066 | 572.4273 | 521.5349 | 419.0741
915.6867 | 853.6867 | 355.923 | 613.4166 | 574.2469 | 450.1781 | 514.7901 | 572.8252 | 520.1362 | 418.0339
916.6881 | 854.6881 | 355.3997 | 613.69 | 572.8724 | 449.2626 | 512.0373 | 571.0222 | 519.2793 | 417.3728
917.6896 | 855.6896 | 354.8988 | 612.7832 | 571.4123 | 448.2156 | 510.5245 | 570.1334 | 518.4574 | 416.5223
918.681 | 856.681 | 354.321 | 611.7722 | 569.9295 | 447.1511 | 509.0507 | 569.2143 | 516.903 | 415.6626
919.6824 | 857.6824 | 353.7449 | 610.9787 | 568.4516 | 446.085 | 507.588 | 568.0776 | 515.9697 | 414.8246
920.6839 | 858.6839 | 353.1503 | 610.1014 | 566.8961 | 445.0759 | 506.0951 | 567.056 | 514.5917 | 413.9788
921.6853 | 859.6853 | 352.6206 | 609.4599 | 565.3612 | 444.03 | 504.5441 | 566.0308 | 513.7386 | 413.1358
922.6868 | 860.6868 | 352.1026 | 608.5427 | 563.7757 | 443.0338 | 503.0225 | 564.9527 | 512.8276 | 412.3158
923.7082 | 861.7082 | 351.4997 | 607.5235 | 562.1654 | 442.018 | 501.407 | 564.0218 | 511.7282 | 411.4801
924.6896 | 862.6896 | 350.9175 | 606.6115 | 560.5949 | 441.1223 | 499.9987 | 562.969 | 510.7735 | 410.6861
925.6811 | 863.6811 | 350.4075 | 605.5722 | 558.9896 | 440.1276 | 498.6762 | 561.7652 | 508.9036 | 409.8468
926.6825 | 864.6825 | 349.8786 | 604.3117 | 557.441 | 439.1645 | 497.1568 | 560.5599 | 507.1365 | 409.0573
927.6839 | 865.6839 | 349.2344 | 603.1521 | 555.9182 | 438.1745 | 495.5632 | 559.4339 | 506.5928 | 408.2325
928.6854 | 866.6854 | 348.7857 | 602.156 | 554.4405 | 437.1332 | 494.0173 | 558.5259 | 506.1747 | 407.4264
929.6868 | 867.6868 | 348.3235 | 601.3258 | 552.9452 | 436.095 | 492.4447 | 557.548 | 505.1949 | 406.6189
930.6883 | 868.6883 | 347.7986 | 600.4159 | 551.4328 | 435.1448 | 490.985 | 556.5201 | 504.1404 | 405.822
931.6797 | 869.6797 | 347.2451 | 599.5749 | 549.9093 | 434.1829 | 489.3921 | 555.5184 | 502.5461 | 405.0067
932.6811 | 870.6811 | 346.6965 | 598.4818 | 548.4237 | 433.2044 | 487.8448 | 554.3635 | 501.075 | 404.232
933.6826 | 871.6826 | 346.1785 | 597.1563 | 546.9536 | 432.2132 | 486.3123 | 553.3003 | 500.0786 | 403.4369
934.684 | 872.684 | 345.6057 | 595.7291 | 545.4842 | 431.2206 | 484.7933 | 552.1825 | 499.0415 | 402.6503
935.6854 | 873.6854 | 345.0655 | 594.5473 | 544.0346 | 430.2652 | 483.2596 | 551.1352 | 498.405 | 401.8607
936.6869 | 874.6869 | 344.5721 | 593.2593 | 542.5747 | 429.2984 | 481.7202 | 549.9715 | 497.4829 | 401.0774
937.6983 | 875.6983 | 344.1308 | 591.8446 | 541.1141 | 428.3342 | 480.172 | 548.8616 | 496.7738 | 400.3161
938.6798 | 876.6798 | 343.5832 | 590.4245 | 539.6459 | 427.3354 | 478.6607 | 547.8235 | 495.4953 | 399.5355
939.6812 | 877.6812 | 343.0983 | 588.9828 | 538.1641 | 426.3386 | 477.1323 | 546.663 | 494.3009 | 398.7801
940.6826 | 878.6826 | 342.6782 | 587.4535 | 536.6918 | 425.3291 | 475.5946 | 545.5748 | 493.4237 | 397.9912
941.6841 | 879.6841 | 342.1798 | 585.8232 | 535.2177 | 424.3577 | 474.0401 | 544.5548 | 492.1614 | 397.222
942.6855 | 880.6855 | 341.6763 | 584.2216 | 533.7455 | 423.2617 | 472.449 | 543.5337 | 490.7438 | 396.4684
943.687 | 881.687 | 341.1751 | 582.6728 | 532.2491 | 422.2349 | 470.862 | 542.5446 | 488.6991 | 395.6957
944.6884 | 882.6884 | 340.6594 | 581.1718 | 530.7816 | 421.341 | 469.2457 | 541.5473 | 486.7383 | 394.9371
945.6898 | 883.6898 | 340.2389 | 579.6383 | 529.3064 | 420.4235 | 467.5987 | 540.4808 | 485.9037 | 394.1887
946.6813 | 884.6813 | 339.7721 | 578.1102 | 527.8443 | 419.5334 | 465.9406 | 539.4715 | 485.171 | 393.4276
947.6827 | 885.6827 | 339.274 | 576.5949 | 526.4057 | 418.6674 | 464.4322 | 538.5029 | 484.2429 | 392.6649
948.6841 | 886.6841 | 338.7437 | 575.0018 | 524.9386 | 417.7381 | 462.814 | 537.4919 | 483.7343 | 391.9127
949.6856 | 887.6856 | 338.2059 | 573.4888 | 523.4402 | 416.869 | 460.8552 | 536.2954 | 482.7393 | 391.1757
950.687 | 888.687 | 337.715 | 571.3551 | 522.1117 | 415.8027 | 460.1335 | 536.0069 | 481.074 | 390.3047
951.6885 | 889.6885 | 337.2811 | 570.1883 | 520.4758 | 414.959 | 457.4465 | 534.0866 | 480.0157 | 389.7082
952.6799 | 890.6799 | 336.9028 | 568.4488 | 518.9717 | 414.0093 | 455.8099 | 533.0326 | 478.607 | 388.9681
953.6813 | 891.6813 | 336.4625 | 566.5965 | 517.5136 | 412.8661 | 454.2212 | 531.9579 | 477.6036 | 388.2375
954.6828 | 892.6828 | 335.9789 | 564.7694 | 516.0131 | 411.918 | 452.5236 | 530.6785 | 476.0532 | 387.5252
955.6842 | 893.6842 | 335.5492 | 560.6175 | 514.8779 | 410.3077 | 455.4134 | 533.1891 | 473.4951 | 386.0665
956.6856 | 894.6856 | 335.0946 | 561.0297 | 512.9561 | 410.0891 | 449.3049 | 528.3325 | 472.31 | 386.0623
957.6871 | 895.6871 | 334.7054 | 559.0565 | 511.4385 | 409.1862 | 447.7298 | 527.1777 | 472.1256 | 385.3366
958.6885 | 896.6885 | 334.2613 | 553.4513 | 510.2592 | 406.9928 | 452.1599 | 531.1845 | 469.2552 | 383.2626
959.68 | 897.68 | 333.8979 | 555.0482 | 508.3984 | 407.3798 | 444.6286 | 524.6332 | 470.3186 | 383.9165
960.6814 | 898.6814 | 333.5133 | 552.9784 | 506.8531 | 406.4783 | 443.0883 | 523.3892 | 469.8994 | 383.2039
961.6828 | 899.6828 | 333.0961 | 550.8859 | 505.2827 | 405.5675 | 441.5407 | 522.1802 | 468.4592 | 382.5018
962.6843 | 900.6843 | 332.6965 | 548.7169 | 503.6999 | 404.645 | 440.0203 | 520.937 | 467.9016 | 381.7901
963.6857 | 901.6857 | 332.2051 | 546.5157 | 502.1067 | 403.6822 | 438.5411 | 519.6453 | 467.1306 | 381.0853
964.6972 | 902.6972 | 331.775 | 544.2603 | 500.4824 | 402.7301 | 437.0804 | 518.2858 | 465.5192 | 380.368
965.6886 | 903.6886 | 331.4835 | 542.058 | 499.0368 | 401.8055 | 435.4612 | 516.8744 | 464.9351 | 379.6774
966.68 | 904.68 | 331.2399 | 539.7679 | 497.4733 | 400.713 | 433.6255 | 515.4379 | 463.6892 | 378.9704
967.6815 | 905.6815 | 330.9004 | 537.4014 | 495.8857 | 399.6787 | 431.9435 | 513.9843 | 462.496 | 378.2527
968.6829 | 906.6829 | 330.5661 | 534.9814 | 494.2449 | 398.5696 | 430.54 | 512.456 | 461.4281 | 377.5379
969.6843 | 907.6843 | 330.1516 | 532.4981 | 492.5838 | 397.5239 | 429.2563 | 510.9315 | 460.169 | 376.8239
970.6858 | 908.6858 | 329.6609 | 529.974 | 490.9152 | 396.3819 | 427.9755 | 509.4063 | 458.7494 | 376.1254
971.6872 | 909.6872 | 329.1907 | 527.4092 | 489.2091 | 395.3281 | 426.7847 | 507.8374 | 457.9089 | 375.4267
972.6887 | 910.6887 | 328.8566 | 524.8407 | 487.5303 | 394.2487 | 425.6359 | 506.2148 | 456.8959 | 374.7276
973.6801 | 911.6801 | 328.474 | 522.2545 | 485.8421 | 393.2019 | 424.4595 | 504.5114 | 455.5025 | 374.0386
974.6815 | 912.6815 | 327.9931 | 519.6609 | 484.2026 | 392.1604 | 423.2782 | 502.7885 | 453.7481 | 373.348
975.683 | 913.683 | 327.5286 | 517.0368 | 482.5163 | 391.1681 | 422.045 | 501.0359 | 452.7742 | 372.6667
976.6844 | 914.6844 | 327.0747 | 514.4294 | 480.8424 | 390.2224 | 420.9223 | 499.3684 | 451.7504 | 371.9859
977.6858 | 915.6858 | 326.498 | 511.8176 | 479.1709 | 389.2221 | 419.7705 | 497.4784 | 450.9058 | 371.3047
978.6873 | 916.6873 | 325.9421 | 509.1796 | 477.4602 | 388.243 | 418.6049 | 495.5049 | 449.5702 | 370.6361
979.6787 | 917.6787 | 325.5046 | 506.5482 | 475.7821 | 387.2432 | 417.5322 | 493.4877 | 448.6535 | 369.9774
980.6801 | 918.6801 | 325.0183 | 503.8297 | 474.0862 | 386.3058 | 416.4507 | 491.364 | 447.7738 | 369.3212
981.6816 | 919.6816 | 324.6697 | 501.0696 | 472.379 | 385.3405 | 415.3126 | 489.2171 | 446.5516 | 368.6444
982.683 | 920.683 | 324.3286 | 498.4194 | 470.6883 | 384.2731 | 414.1429 | 487.0515 | 445.8025 | 367.9791
983.6845 | 921.6845 | 323.8496 | 495.6309 | 468.9661 | 383.3406 | 413.0155 | 484.8674 | 444.6359 | 367.3045
984.6859 | 922.6859 | 323.3363 | 492.7895 | 467.268 | 382.3416 | 411.7991 | 482.6482 | 443.6652 | 366.6604
985.6873 | 923.6873 | 322.8568 | 489.9099 | 465.5089 | 381.4424 | 410.6617 | 480.468 | 441.6548 | 366.0126
986.6888 | 924.6888 | 322.3291 | 487.016 | 463.8053 | 380.5371 | 409.572 | 478.3477 | 439.9158 | 365.3553
987.6902 | 925.6902 | 321.8824 | 484.1485 | 462.0923 | 379.655 | 408.5349 | 476.1717 | 439.1341 | 364.7075
988.6817 | 926.6817 | 321.5215 | 481.2899 | 460.393 | 378.7908 | 407.5314 | 473.9718 | 438.5249 | 364.044
989.6831 | 927.6831 | 321.0662 | 478.5024 | 458.6764 | 377.958 | 406.5556 | 471.7209 | 437.1815 | 363.3946
990.6845 | 928.6845 | 320.5666 | 475.7757 | 456.987 | 377.0563 | 405.5207 | 469.4054 | 435.8605 | 362.7502
991.686 | 929.686 | 320.0944 | 473.0909 | 455.2651 | 376.1474 | 404.494 | 467.0882 | 435.094 | 362.1196
992.6874 | 930.6874 | 319.5999 | 470.5013 | 453.5622 | 375.299 | 403.4614 | 464.7785 | 433.9111 | 361.4947
993.6889 | 931.6889 | 319.1349 | 467.9717 | 451.8527 | 374.4275 | 402.4506 | 462.4956 | 433.2906 | 360.8708
994.6803 | 932.6803 | 318.7249 | 465.5176 | 450.1669 | 373.5672 | 401.439 | 460.1892 | 431.7874 | 360.2635
995.6817 | 933.6817 | 318.2666 | 463.1007 | 448.4797 | 372.741 | 400.4708 | 457.8804 | 429.791 | 359.6491
996.6832 | 934.6832 | 317.8412 | 460.7602 | 446.8021 | 371.9455 | 399.4929 | 455.5843 | 429.1126 | 359.0312
997.6846 | 935.6846 | 317.4987 | 458.4753 | 445.1665 | 371.0651 | 398.5043 | 453.261 | 428.7417 | 358.3924
998.686 | 936.686 | 317.0323 | 456.2564 | 443.5504 | 370.1613 | 397.5275 | 450.9493 | 427.4603 | 357.7635
999.6875 | 937.6875 | 316.6161 | 454.0663 | 441.9351 | 369.2716 | 396.5373 | 448.5724 | 425.0708 | 357.1628
1000.6789 | 938.6789 | 316.267 | 451.9436 | 440.3047 | 368.4051 | 395.4582 | 446.19 | 423.742 | 356.544
1001.6803 | 939.6803 | 315.9853 | 449.8786 | 438.6903 | 367.5338 | 394.4104 | 443.8235 | 422.9933 | 355.9382
1002.6818 | 940.6818 | 315.6105 | 447.8612 | 437.07 | 366.6906 | 393.3946 | 441.4893 | 421.2785 | 355.3233
1003.6832 | 941.6832 | 315.1792 | 445.8581 | 435.4949 | 365.81 | 392.3791 | 439.2019 | 420.8086 | 354.7284
1004.6847 | 942.6847 | 314.6903 | 443.9223 | 433.9505 | 364.9499 | 391.4026 | 436.9172 | 420.1151 | 354.1204
1005.6861 | 943.6861 | 314.1721 | 442.0388 | 432.3874 | 364.0851 | 390.4753 | 434.7005 | 419.1607 | 353.5373
1006.6875 | 944.6875 | 313.7302 | 440.164 | 430.8264 | 363.2812 | 389.558 | 432.4802 | 418.5849 | 352.9237
1007.689 | 945.689 | 313.2541 | 438.3293 | 429.2905 | 362.4352 | 388.6206 | 430.2686 | 417.7719 | 352.3383
1008.6804 | 946.6804 | 312.8826 | 436.5176 | 427.7254 | 361.5776 | 387.6707 | 428.0857 | 417.0271 | 351.744
1009.6819 | 947.6819 | 312.4885 | 434.7591 | 426.1867 | 360.7528 | 386.7229 | 425.9173 | 416.3913 | 351.137
1010.6833 | 948.6833 | 312.0159 | 433.0234 | 424.678 | 359.9185 | 385.7785 | 423.7846 | 416.0741 | 350.5232
1011.6847 | 949.6847 | 311.4794 | 431.3175 | 423.1682 | 359.0985 | 384.8569 | 421.6775 | 415.1528 | 349.9203
1012.6862 | 950.6862 | 311.0112 | 429.6417 | 421.63 | 358.2946 | 383.9967 | 419.609 | 414.373 | 349.3131
1013.6876 | 951.6876 | 310.5291 | 427.991 | 420.1236 | 357.4656 | 383.0957 | 417.5834 | 413.2657 | 348.6954
1014.6891 | 952.6891 | 310.0947 | 426.365 | 418.6494 | 356.6456 | 382.202 | 415.5714 | 412.231 | 348.1167
1015.6805 | 953.6805 | 309.5942 | 424.7705 | 417.1644 | 355.8247 | 381.2799 | 413.5307 | 411.4519 | 347.5184
1016.6819 | 954.6819 | 309.2336 | 423.192 | 415.6858 | 354.9907 | 380.3788 | 411.5151 | 410.2958 | 346.9235
1017.6834 | 955.6834 | 308.8727 | 421.6357 | 414.2166 | 354.1655 | 379.4873 | 409.5292 | 409.5849 | 346.3264
1018.6848 | 956.6848 | 308.5163 | 420.0769 | 412.7539 | 353.3769 | 378.6647 | 407.6241 | 408.7052 | 345.7358
1019.6862 | 957.6862 | 308.1677 | 418.5773 | 411.3114 | 352.566 | 377.6583 | 405.722 | 407.283 | 345.1618
1020.6877 | 958.6877 | 307.7552 | 417.0847 | 409.8401 | 351.7721 | 376.7466 | 403.8208 | 405.9923 | 344.5663
1021.6791 | 959.6791 | 307.3235 | 415.6001 | 408.4219 | 350.9626 | 375.8513 | 401.9419 | 405.5017 | 343.9832
1022.6805 | 960.6805 | 306.9578 | 414.1398 | 407.0304 | 350.1423 | 374.9405 | 400.1276 | 405.0108 | 343.4091
1023.682 | 961.682 | 306.5772 | 412.6965 | 405.6489 | 349.3192 | 374.0398 | 398.3642 | 404.3694 | 342.8132
1024.6834 | 962.6834 | 306.2081 | 411.271 | 404.3035 | 348.5132 | 373.1241 | 396.642 | 403.4488 | 342.2456
1025.6849 | 963.6849 | 305.8607 | 409.8553 | 402.9161 | 347.639 | 372.181 | 394.8834 | 402.7865 | 341.6506
1026.6863 | 964.6863 | 305.5799 | 408.4565 | 401.5756 | 346.752 | 371.2526 | 393.1917 | 401.9609 | 341.0474
1027.6877 | 965.6877 | 305.2236 | 407.0843 | 400.2197 | 345.7278 | 370.2665 | 391.5246 | 400.8123 | 340.4574
1028.6892 | 966.6892 | 304.8788 | 405.7184 | 398.8915 | 344.6888 | 369.2924 | 389.901 | 399.9234 | 339.8532
1029.6806 | 967.6806 | 304.4725 | 404.3501 | 397.5441 | 343.6827 | 368.3587 | 388.3161 | 399.2483 | 339.2654
1030.682 | 968.682 | 304.0707 | 403.02 | 396.2119 | 342.7144 | 367.4488 | 386.7549 | 398.3783 | 338.6799
1031.6835 | 969.6835 | 303.6504 | 401.6961 | 394.8705 | 341.7872 | 366.5796 | 385.2562 | 397.1561 | 338.1128
1032.6849 | 970.6849 | 303.2066 | 400.2892 | 393.56 | 340.878 | 365.9083 | 383.8298 | 396.5455 | 337.5216
1033.6864 | 971.6864 | 302.7458 | 399.0656 | 392.2466 | 339.9623 | 364.9182 | 382.2771 | 395.89 | 336.9689
1034.6878 | 972.6878 | 302.3212 | 397.788 | 390.9729 | 339.0802 | 364.0162 | 380.8129 | 394.7672 | 336.4029
1035.6892 | 973.6892 | 301.9834 | 396.5111 | 389.7004 | 338.24 | 363.1577 | 379.3838 | 393.7492 | 335.8128
1036.6807 | 974.6807 | 301.5639 | 395.2281 | 388.4427 | 337.4154 | 362.2684 | 377.9936 | 392.748 | 335.2453
1037.6821 | 975.6821 | 301.2061 | 393.9697 | 387.183 | 336.5935 | 361.3975 | 376.5812 | 392.0322 | 334.6842
1038.6836 | 976.6836 | 300.8431 | 392.7115 | 385.9464 | 335.8092 | 360.5442 | 375.2109 | 391.2257 | 334.1152
1039.685 | 977.685 | 300.3654 | 391.4602 | 384.7378 | 334.9993 | 359.6673 | 373.8493 | 390.5282 | 333.5521
1040.6864 | 978.6864 | 299.858 | 390.2206 | 383.5024 | 334.23 | 358.7972 | 372.4636 | 389.6671 | 332.9793
1041.6779 | 979.6779 | 299.4521 | 388.9912 | 382.2931 | 333.4578 | 357.9605 | 371.1563 | 388.4701 | 332.4193
1042.6793 | 980.6793 | 298.978 | 387.7688 | 381.099 | 332.7085 | 357.1226 | 369.9109 | 388.0929 | 331.8629
1043.6807 | 981.6807 | 298.5312 | 386.5167 | 379.9385 | 331.9422 | 356.3403 | 368.7528 | 387.0722 | 331.2911
1044.6822 | 982.6822 | 298.0585 | 385.3621 | 378.7626 | 331.2028 | 355.467 | 367.5712 | 385.7924 | 330.7467
1045.6836 | 983.6836 | 297.6219 | 384.1927 | 377.6098 | 330.3531 | 354.5851 | 366.4389 | 384.3983 | 330.2122
1046.6851 | 984.6851 | 297.2118 | 383.0234 | 376.4946 | 329.5293 | 353.7726 | 365.2933 | 383.5755 | 329.6664
1047.6865 | 985.6865 | 296.7633 | 381.855 | 375.3765 | 328.7174 | 352.9623 | 364.1934 | 381.8775 | 329.1189
1048.6779 | 986.6779 | 296.346 | 380.7051 | 374.2431 | 327.9482 | 352.1391 | 363.0705 | 380.7257 | 328.5566
1049.6894 | 987.6894 | 295.9477 | 379.5682 | 373.1367 | 327.2161 | 351.3576 | 361.9921 | 380.3616 | 328.0073
1050.6808 | 988.6808 | 295.5623 | 378.4321 | 372.0546 | 326.5232 | 350.5955 | 360.9443 | 379.5773 | 327.4795
1051.6822 | 989.6822 | 295.1328 | 377.3134 | 370.9808 | 325.8469 | 349.8071 | 359.8877 | 378.6668 | 326.9246
1052.6837 | 990.6837 | 294.6672 | 376.0723 | 369.9509 | 325.1217 | 349.2487 | 358.939 | 377.7709 | 326.3753
1053.6851 | 991.6851 | 294.2543 | 375.0921 | 368.8729 | 324.4598 | 348.2917 | 357.7974 | 376.7947 | 325.8686
1054.6866 | 992.6866 | 293.931 | 374.0094 | 367.8311 | 323.7646 | 347.5171 | 356.6552 | 376.1721 | 325.3248
1055.688 | 993.688 | 293.6411 | 372.93 | 366.8093 | 323.0615 | 346.7392 | 355.5132 | 374.8532 | 324.801
1056.6794 | 994.6794 | 293.3133 | 371.8596 | 365.8017 | 322.3503 | 345.9104 | 354.3801 | 373.942 | 324.2709
1057.6809 | 995.6809 | 292.9975 | 370.8012 | 364.8036 | 321.5143 | 345.0606 | 353.2755 | 372.9552 | 323.7676
1058.6823 | 996.6823 | 292.6958 | 369.7664 | 363.7976 | 320.7552 | 344.2044 | 352.1332 | 371.6553 | 323.2386
1059.6838 | 997.6838 | 292.3989 | 368.7213 | 362.8079 | 319.9963 | 343.4011 | 350.9837 | 371.3342 | 322.7251
1060.6852 | 998.6852 | 292.0164 | 367.6891 | 361.8345 | 319.282 | 342.5488 | 349.827 | 370.6572 | 322.203
1061.6866 | 999.6866 | 291.6641 | 366.6737 | 360.8796 | 318.5506 | 341.6066 | 348.6951 | 370.0324 | 321.6678
1062.6881 | 1000.6881 | 291.2908 | 365.669 | 359.9056 | 317.898 | 340.7689 | 347.6067 | 368.647 | 321.1508
1063.6795 | 1001.6795 | 290.9135 | 364.6577 | 358.9271 | 317.2505 | 339.9787 | 346.5363 | 368.0132 | 320.6382
1064.6809 | 1002.6809 | 290.6484 | 363.6633 | 357.98 | 316.6205 | 339.2157 | 345.4635 | 367.2594 | 320.1067
1065.6824 | 1003.6824 | 290.3828 | 362.6701 | 357.0464 | 315.9947 | 338.4059 | 344.4057 | 366.7315 | 319.5989
1066.6838 | 1004.6838 | 290.1393 | 361.6731 | 356.0907 | 315.3378 | 337.6435 | 343.3317 | 366.1241 | 319.07
1067.6853 | 1005.6853 | 289.8656 | 360.7173 | 355.1645 | 314.7037 | 336.827 | 342.2424 | 365.3874 | 318.5434
1068.6867 | 1006.6867 | 289.6205 | 359.7461 | 354.251 | 313.9814 | 336.0355 | 341.1688 | 364.7907 | 318.0226
1069.6781 | 1007.6781 | 289.3106 | 358.7869 | 353.3543 | 313.3268 | 335.2746 | 340.107 | 364.1933 | 317.4935
1070.6896 | 1008.6896 | 288.884 | 357.8285 | 352.4374 | 312.6849 | 334.5867 | 339.0925 | 363.2575 | 316.9886
1071.681 | 1009.681 | 288.4528 | 356.8967 | 351.5417 | 312.0723 | 333.876 | 338.1184 | 362.4866 | 316.4701
1072.6824 | 1010.6824 | 288.0972 | 355.964 | 350.6365 | 311.4493 | 333.1257 | 337.1779 | 361.4308 | 315.9479
1073.6839 | 1011.6839 | 287.688 | 355.0334 | 349.729 | 310.8333 | 332.3897 | 336.2579 | 360.7118 | 315.4452
1074.6853 | 1012.6853 | 287.1948 | 354.1064 | 348.8436 | 310.2166 | 331.6865 | 335.3344 | 358.9926 | 314.9508
1075.6868 | 1013.6868 | 286.8176 | 353.1904 | 347.9642 | 309.6234 | 331.0433 | 334.4274 | 358.2026 | 314.4333
1076.6882 | 1014.6882 | 286.3871 | 352.2784 | 347.1032 | 309.057 | 330.3736 | 333.5202 | 357.5186 | 313.9192
1077.6796 | 1015.6796 | 285.9428 | 351.3696 | 346.2225 | 308.4116 | 329.728 | 332.6316 | 356.7565 | 313.4117
1078.6811 | 1016.6811 | 285.4986 | 350.477 | 345.3629 | 307.7705 | 329.0536 | 331.7941 | 355.4847 | 312.9111
1079.6825 | 1017.6825 | 285.036 | 349.5846 | 344.514 | 307.1511 | 328.3951 | 330.9473 | 354.916 | 312.4187
1080.6839 | 1018.6839 | 284.5599 | 348.7041 | 343.6775 | 306.5732 | 327.7583 | 330.1079 | 354.1128 | 311.9154
1081.6854 | 1019.6854 | 284.1638 | 347.8288 | 342.8553 | 305.9992 | 327.131 | 329.3082 | 352.5707 | 311.4246
1082.6868 | 1020.6868 | 283.7528 | 346.9562 | 342.0244 | 305.4161 | 326.4788 | 328.4941 | 352.0995 | 310.9128
1083.6883 | 1021.6883 | 283.3872 | 346.0873 | 341.2063 | 304.7919 | 325.8482 | 327.6679 | 351.3241 | 310.448
1084.6797 | 1022.6797 | 283.033 | 345.231 | 340.3716 | 304.1949 | 325.211 | 326.7884 | 349.8614 | 309.9662
1085.6811 | 1023.6811 | 282.6804 | 344.3693 | 339.5831 | 303.6014 | 324.582 | 325.8657 | 348.7547 | 309.476
1086.6826 | 1024.6826 | 282.3078 | 343.518 | 338.804 | 302.9547 | 323.8968 | 324.8975 | 348.3805 | 309.0008
1087.684 | 1025.684 | 281.98 | 342.6797 | 337.9978 | 302.3074 | 323.1669 | 323.9569 | 347.7254 | 308.5204
1088.6855 | 1026.6855 | 281.702 | 341.839 | 337.2192 | 301.6842 | 322.5034 | 323.0164 | 347.0034 | 308.0274
1089.6869 | 1027.6869 | 281.3635 | 341.0061 | 336.4331 | 301.0615 | 321.8318 | 322.065 | 346.2437 | 307.53
1090.6883 | 1028.6883 | 281.0762 | 340.1768 | 335.6458 | 300.4719 | 321.1795 | 321.1204 | 345.3872 | 307.0489
1091.6898 | 1029.6898 | 280.7759 | 339.3605 | 334.874 | 299.842 | 320.5548 | 320.2137 | 344.7411 | 306.5576
1092.6812 | 1030.6812 | 280.3922 | 338.5423 | 334.1248 | 299.1697 | 319.9334 | 319.3018 | 344.0598 | 306.0834
1093.6826 | 1031.6826 | 279.9458 | 337.7443 | 333.3642 | 298.5728 | 319.2878 | 318.4136 | 343.1656 | 305.5921
1094.6841 | 1032.6841 | 279.5467 | 336.9392 | 332.5899 | 298.0246 | 318.6469 | 317.5585 | 342.1922 | 305.1222
1095.6855 | 1033.6855 | 279.197 | 336.1532 | 331.819 | 297.5017 | 318.0462 | 316.6897 | 341.2757 | 304.6198

## C6-7
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 155.884 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38910.4891 | 0 | 0 | 38910.4891 | 0 | 0 | -5 | 57 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4898 | 0 | 0 | 38910.4898 | 0 | 0 | 54 | 116 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4904 | 0 | 0 | 38910.4905 | 0 | 0 | 113 | 175 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4911 | 0 | 0 | 38910.4911 | 0 | 0 | 171.5 | 233.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4918 | 0 | 0 | 38910.4918 | 0 | 0 | 230.5 | 292.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4925 | 0 | 0 | 38910.4925 | 0 | 0 | 289 | 351 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4932 | 0 | 0 | 38910.4932 | 0 | 0 | 348 | 410 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4938 | 0 | 0 | 38910.4939 | 0 | 0 | 406.5 | 468.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4945 | 0 | 0 | 38910.4945 | 0 | 0 | 465.5 | 527.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4952 | 0 | 0 | 38910.4952 | 0 | 0 | 524.5 | 586.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4959 | 0 | 0 | 38910.4959 | 0 | 0 | 583 | 645 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510576 | 510576 | 510575.9997
38910.4966 | 2323 | 2 | 38910.4966 | 2359 | 1 | 642 | 704 | 141.8193 | 0.1221 | 144.0171 | 0.06105 | 1.4182 | 0.001221 | 1.4402 | 0.0006105 | 1.417 | 1.4396 | 10.0303 | 8.2784 | 873.0398
38910.4972 | 2242 | 0 | 38910.4973 | 1681 | 0 | 700.5 | 762.5 | 136.8742 | 0 | 102.6252 | 0 | 1.3687 | 0 | 1.0263 | 0 | 1.3687 | 1.0263 | 13.8885 | 51.8965 | 12.5198
38910.4979 | 2055 | 0 | 38910.4979 | 1717 | 0 | 759.5 | 821.5 | 125.4579 | 0 | 104.823 | 0 | 1.2546 | 0 | 1.0482 | 0 | 1.2546 | 1.0482 | 24.2521 | 48.7117 | 22.9975
38910.4986 | 1976 | 0 | 38910.4986 | 1722 | 0 | 818.5 | 880.5 | 120.6349 | 0 | 105.1282 | 0 | 1.2063 | 0 | 1.0513 | 0 | 1.2063 | 1.0513 | 29.2196 | 48.2799 | 28.0133
38910.4993 | 2149 | 0 | 38910.4993 | 2002 | 0 | 877 | 939 | 131.1966 | 0 | 122.2222 | 0 | 1.312 | 0 | 1.2222 | 0 | 1.312 | 1.2222 | 18.8171 | 27.5415 | 17.5052
38910.5 | 1930 | 0 | 38910.5 | 2143 | 0 | 936 | 998 | 117.8266 | 0 | 130.8303 | 0 | 1.1783 | 0 | 1.3083 | 0 | 1.1783 | 1.3083 | 32.2995 | 19.1498 | 31.1212
38910.5006 | 2537 | 0 | 38910.5007 | 32 | 0 | 994.5 | 1056.5 | 154.884 | 0 | 1.9536 | 0 | 1.5488 | 0 | 0.019536 | 0 | 1.5488 | 0.019536 | 0.64564 | 7879.3125 | 0.9032
38910.5013 | 2001 | 0 | 38910.5013 | 60 | 0 | 1053.5 | 1115.5 | 122.1612 | 0 | 3.663 | 0 | 1.2216 | 0 | 0.03663 | 0 | 1.2216 | 0.03663 | 27.6052 | 4155.6333 | 26.3836

## C5-7
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 157.2882 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38910.4891 | 0 | 0 | 38910.4891 | 0 | 0 | -7.5 | 54.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4897 | 0 | 0 | 38910.4897 | 0 | 0 | 51.5 | 113.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4904 | 0 | 0 | 38910.4904 | 0 | 0 | 110 | 172 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4911 | 0 | 0 | 38910.4911 | 0 | 0 | 168.5 | 230.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4918 | 0 | 0 | 38910.4918 | 0 | 0 | 227.5 | 289.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4925 | 0 | 0 | 38910.4925 | 0 | 0 | 286.5 | 348.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4931 | 0 | 0 | 38910.4931 | 0 | 0 | 345 | 407 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4938 | 0 | 0 | 38910.4938 | 0 | 0 | 404 | 466 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4945 | 0 | 0 | 38910.4945 | 0 | 0 | 462.5 | 524.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4952 | 0 | 0 | 38910.4952 | 0 | 0 | 521.5 | 583.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4959 | 0 | 0 | 38910.4959 | 0 | 0 | 580.5 | 642.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
38910.4965 | 2006 | 79 | 38910.4966 | 2346 | 2 | 639 | 701 | 122.4664 | 4.823 | 143.2234 | 0.1221 | 1.2247 | 0.04823 | 1.4322 | 0.001221 | 1.1764 | 1.431 | 50.72 | 9.8451 | 55.7479
38910.4972 | 2350 | 0 | 38910.4972 | 2256 | 0 | 698 | 760 | 143.4676 | 0 | 137.7289 | 0 | 1.4347 | 0 | 1.3773 | 0 | 1.4347 | 1.3773 | 9.6332 | 14.2012 | 8.1985
38910.4979 | 2244 | 0 | 38910.4979 | 2219 | 0 | 756.5 | 818.5 | 136.9963 | 0 | 135.4701 | 0 | 1.37 | 0 | 1.3547 | 0 | 1.37 | 1.3547 | 14.8119 | 16.1055 | 13.442
38910.4986 | 2064 | 0 | 38910.4986 | 1688 | 0 | 815.5 | 877.5 | 126.0073 | 0 | 103.0525 | 0 | 1.2601 | 0 | 1.0305 | 0 | 1.2601 | 1.0305 | 24.8246 | 52.6291 | 23.5645
38910.4993 | 2554 | 0 | 38910.4993 | 2560 | 0 | 874.5 | 936.5 | 155.9219 | 0 | 156.2882 | 0 | 1.5592 | 0 | 1.5629 | 0 | 1.5592 | 1.5629 | 0.87627 | 0.63984 | 0.68295
38910.4999 | 1953 | 0 | 38910.5 | 1936 | 0 | 933 | 995 | 119.2308 | 0 | 118.1929 | 0 | 1.1923 | 0 | 1.1819 | 0 | 1.1923 | 1.1819 | 31.9191 | 33.0775 | 30.7268
38910.5006 | 2357 | 0 | 38910.5006 | 28 | 0 | 992 | 1054 | 143.895 | 0 | 1.7094 | 0 | 1.4389 | 0 | 0.017094 | 0 | 1.4389 | 0.017094 | 9.3076 | 9101.3571 | 7.8686
38910.5013 | 2430 | 0 | 38910.5013 | 59 | 0 | 1050.5 | 1112.5 | 148.3516 | 0 | 3.602 | 0 | 1.4835 | 0 | 0.03602 | 0 | 1.4835 | 0.03602 | 6.0239 | 4266.7458 | 4.5404

## C5-6
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 156.4945 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38910.489 | 0 | 0 | 38910.489 | 0 | 0 | -10.5 | 51.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4897 | 0 | 0 | 38910.4897 | 0 | 0 | 48.5 | 110.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4904 | 0 | 0 | 38910.4904 | 0 | 0 | 107 | 169 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4911 | 0 | 0 | 38910.4911 | 0 | 0 | 166 | 228 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4917 | 0 | 0 | 38910.4918 | 0 | 0 | 225 | 287 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4924 | 0 | 0 | 38910.4924 | 0 | 0 | 283.5 | 345.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4931 | 0 | 0 | 38910.4931 | 0 | 0 | 342.5 | 404.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4938 | 0 | 0 | 38910.4938 | 0 | 0 | 401 | 463 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4945 | 0 | 0 | 38910.4945 | 0 | 0 | 460 | 522 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4951 | 0 | 0 | 38910.4952 | 0 | 0 | 518.5 | 580.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4958 | 0 | 0 | 38910.4958 | 0 | 0 | 577.5 | 639.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
38910.4965 | 2547 | 3 | 38910.4965 | 1895 | 3 | 636.5 | 698.5 | 155.4945 | 0.18315 | 115.6899 | 0.18315 | 1.5549 | 0.0018315 | 1.1569 | 0.0018315 | 1.5531 | 1.1551 | 0.64549 | 46.8303 | 142.2479
38910.4972 | 2203 | 0 | 38910.4972 | 2019 | 0 | 695 | 757 | 134.4933 | 0 | 123.2601 | 0 | 1.3449 | 0 | 1.2326 | 0 | 1.3449 | 1.2326 | 16.3586 | 26.9629 | 15.0137
38910.4979 | 2297 | 0 | 38910.4979 | 2294 | 0 | 754 | 816 | 140.232 | 0 | 140.0488 | 0 | 1.4023 | 0 | 1.4005 | 0 | 1.4023 | 1.4005 | 11.5969 | 11.7428 | 10.1945
38910.4985 | 2116 | 0 | 38910.4986 | 1972 | 0 | 812.5 | 874.5 | 129.1819 | 0 | 120.3907 | 0 | 1.2918 | 0 | 1.2039 | 0 | 1.2918 | 1.2039 | 21.1427 | 29.9888 | 19.8509
38910.4992 | 2432 | 0 | 38910.4992 | 2318 | 0 | 871.5 | 933.5 | 148.4737 | 0 | 141.514 | 0 | 1.4847 | 0 | 1.4151 | 0 | 1.4847 | 1.4151 | 5.4021 | 10.5858 | 3.9174
38910.4999 | 2144 | 0 | 38910.4999 | 2350 | 0 | 930.5 | 992.5 | 130.8913 | 0 | 143.4676 | 0 | 1.3089 | 0 | 1.4347 | 0 | 1.3089 | 1.4347 | 19.5606 | 9.08 | 18.2517
38910.5006 | 2137 | 0 | 38910.5006 | 2373 | 0 | 989 | 1051 | 130.464 | 0 | 144.8718 | 0 | 1.3046 | 0 | 1.4487 | 0 | 1.3046 | 1.4487 | 19.9523 | 8.0228 | 18.6476
38910.5013 | 2103 | 0 | 38910.5013 | 2251 | 0 | 1048 | 1110 | 128.3883 | 0 | 137.4237 | 0 | 1.2839 | 0 | 1.3742 | 0 | 1.2839 | 1.3742 | 21.8916 | 13.8774 | 20.6077

## C4-7
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 153.5641 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38910.489 | 0 | 0 | 38910.489 | 0 | 0 | -13 | 49 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4897 | 0 | 0 | 38910.4897 | 0 | 0 | 45.5 | 107.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4903 | 0 | 0 | 38910.4904 | 0 | 0 | 104.5 | 166.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.491 | 0 | 0 | 38910.491 | 0 | 0 | 163 | 225 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4917 | 0 | 0 | 38910.4917 | 0 | 0 | 222 | 284 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4924 | 0 | 0 | 38910.4924 | 0 | 0 | 280.5 | 342.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4931 | 0 | 0 | 38910.4931 | 0 | 0 | 339.5 | 401.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4938 | 0 | 0 | 38910.4938 | 0 | 0 | 398.5 | 460.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4944 | 0 | 0 | 38910.4944 | 0 | 0 | 457 | 519 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4951 | 0 | 0 | 38910.4951 | 0 | 0 | 516 | 578 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4958 | 0 | 0 | 38910.4958 | 0 | 0 | 574.5 | 636.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502976 | 502976 | 502975.9997
38910.4965 | 2499 | 5 | 38910.4965 | 2431 | 4 | 633.5 | 695.5 | 152.5641 | 0.30525 | 148.4127 | 0.2442 | 1.5256 | 0.0030525 | 1.4841 | 0.002442 | 1.5226 | 1.4817 | 0.68688 | 4.5743 | 9.9557
38910.4972 | 2202 | 0 | 38910.4972 | 1965 | 0 | 692.5 | 754.5 | 134.4322 | 0 | 119.9634 | 0 | 1.3443 | 0 | 1.1996 | 0 | 1.3443 | 1.1996 | 14.2316 | 28.0092 | 12.8873
38910.4978 | 2056 | 0 | 38910.4978 | 2302 | 0 | 751 | 813 | 125.5189 | 0 | 140.5372 | 0 | 1.2552 | 0 | 1.4054 | 0 | 1.2552 | 1.4054 | 22.3434 | 9.2693 | 21.0882
38910.4985 | 2407 | 0 | 38910.4985 | 2237 | 4 | 810 | 872 | 146.9475 | 0 | 136.569 | 0.2442 | 1.4695 | 0 | 1.3657 | 0.002442 | 1.4695 | 1.3632 | 4.5027 | 12.6458 | 3.0332
38910.4992 | 1935 | 0 | 38910.4992 | 2110 | 0 | 868.5 | 930.5 | 118.1319 | 0 | 128.8156 | 0 | 1.1813 | 0 | 1.2882 | 0 | 1.1813 | 1.2882 | 29.9938 | 19.2123 | 28.8125
38910.4999 | 1960 | 0 | 38910.4999 | 2127 | 0 | 927.5 | 989.5 | 119.6581 | 0 | 129.8535 | 0 | 1.1966 | 0 | 1.2985 | 0 | 1.1966 | 1.2985 | 28.3357 | 18.2595 | 27.1391
38910.5006 | 1919 | 0 | 38910.5006 | 1612 | 1 | 986.5 | 1048.5 | 117.1551 | 0 | 98.4127 | 0.06105 | 1.1716 | 0 | 0.98413 | 0.0006105 | 1.1716 | 0.98352 | 31.0776 | 56.1378 | 29.9061
38910.5012 | 2057 | 0 | 38910.5013 | 59 | 0 | 1045 | 1107 | 125.58 | 0 | 3.602 | 0 | 1.2558 | 0 | 0.03602 | 0 | 1.2558 | 0.03602 | 22.2839 | 4163.3559 | 21.0281

## C4-6
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 157.5324 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38910.4889 | 0 | 0 | 38910.489 | 0 | 0 | -16 | 46 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4896 | 0 | 0 | 38910.4896 | 0 | 0 | 42.5 | 104.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4903 | 0 | 0 | 38910.4903 | 0 | 0 | 101.5 | 163.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.491 | 0 | 0 | 38910.491 | 0 | 0 | 160.5 | 222.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4917 | 0 | 0 | 38910.4917 | 0 | 0 | 219 | 281 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4923 | 0 | 0 | 38910.4924 | 0 | 0 | 278 | 340 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.493 | 0 | 0 | 38910.493 | 0 | 0 | 336.5 | 398.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4937 | 0 | 0 | 38910.4937 | 0 | 0 | 395.5 | 457.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4944 | 0 | 0 | 38910.4944 | 0 | 0 | 454.5 | 516.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4951 | 0 | 0 | 38910.4951 | 0 | 0 | 513 | 575 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4958 | 0 | 0 | 38910.4958 | 0 | 0 | 572 | 634 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4964 | 2564 | 8 | 38910.4964 | 1714 | 7 | 630.5 | 692.5 | 156.5324 | 0.4884 | 104.6398 | 0.42735 | 1.5653 | 0.004884 | 1.0464 | 0.0042735 | 1.5604 | 1.0421 | 0.64228 | 140.3891 | 61.1748
38910.4971 | 1993 | 0 | 38910.4971 | 2460 | 0 | 689.5 | 751.5 | 121.6728 | 0 | 150.1832 | 0 | 1.2167 | 0 | 1.5018 | 0 | 1.2167 | 1.5018 | 29.4722 | 4.8935 | 28.2554
38910.4978 | 2356 | 0 | 38910.4978 | 1927 | 0 | 748.5 | 810.5 | 143.8339 | 0 | 117.6435 | 0 | 1.4383 | 0 | 1.1764 | 0 | 1.4383 | 1.1764 | 9.5238 | 33.9066 | 8.0854
38910.4985 | 2326 | 0 | 38910.4985 | 2291 | 0 | 807 | 869 | 142.0024 | 0 | 139.8657 | 0 | 1.42 | 0 | 1.3987 | 0 | 1.42 | 1.3987 | 10.9364 | 12.6312 | 9.5163
38910.4992 | 2277 | 0 | 38910.4992 | 2516 | 0 | 866 | 928 | 139.011 | 0 | 153.602 | 0 | 1.3901 | 0 | 1.536 | 0 | 1.3901 | 1.536 | 13.3237 | 2.5588 | 11.9336
38910.4998 | 2520 | 0 | 38910.4998 | 2408 | 0 | 924.5 | 986.5 | 153.8462 | 0 | 147.0085 | 0 | 1.5385 | 0 | 1.4701 | 0 | 1.5385 | 1.4701 | 2.396 | 7.1586 | 0.85757
38910.5005 | 2456 | 1 | 38910.5005 | 2548 | 0 | 983.5 | 1045.5 | 149.9389 | 0.06105 | 155.5556 | 0 | 1.4994 | 0.0006105 | 1.5556 | 0 | 1.4988 | 1.5556 | 5.2342 | 1.2708 | 154.8239
38910.5012 | 2370 | 0 | 38910.5012 | 2321 | 0 | 1042.5 | 1104.5 | 144.6886 | 0 | 141.6972 | 0 | 1.4469 | 0 | 1.417 | 0 | 1.4469 | 1.417 | 8.8768 | 11.1754 | 7.4299

## C4-5
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 157.105 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38910.4889 | 0 | 0 | 38910.4889 | 0 | 0 | -19 | 43 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4896 | 0 | 0 | 38910.4896 | 0 | 0 | 40 | 102 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4903 | 0 | 0 | 38910.4903 | 0 | 0 | 98.5 | 160.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.491 | 0 | 0 | 38910.491 | 0 | 0 | 157.5 | 219.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4916 | 0 | 0 | 38910.4917 | 0 | 0 | 216.5 | 278.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4923 | 0 | 0 | 38910.4923 | 0 | 0 | 275 | 337 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.493 | 0 | 0 | 38910.493 | 0 | 0 | 334 | 396 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4937 | 0 | 0 | 38910.4937 | 0 | 0 | 392.5 | 454.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4944 | 0 | 0 | 38910.4944 | 0 | 0 | 451.5 | 513.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.495 | 0 | 0 | 38910.4951 | 0 | 0 | 510.5 | 572.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4957 | 0 | 0 | 38910.4957 | 0 | 0 | 569 | 631 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514576 | 514576 | 514575.9997
38910.4964 | 2101 | 22 | 38910.4964 | 31 | 13 | 628 | 690 | 128.2662 | 1.3431 | 1.8926 | 0.79365 | 1.2827 | 0.013431 | 0.018926 | 0.0079365 | 1.2692 | 0.010989 | 22.7178 | 6481.7161 | 2016.0777
38910.4971 | 2557 | 0 | 38910.4971 | 2004 | 0 | 686.5 | 748.5 | 156.105 | 0 | 122.3443 | 0 | 1.5611 | 0 | 1.2234 | 0 | 1.5611 | 1.2234 | 0.64059 | 28.4122 | 0.92046
38910.4978 | 2034 | 0 | 38910.4978 | 2378 | 0 | 745.5 | 807.5 | 124.1758 | 0 | 145.177 | 0 | 1.2418 | 0 | 1.4518 | 0 | 1.2418 | 1.4518 | 26.5182 | 8.2161 | 25.2764
38910.4984 | 1928 | 0 | 38910.4985 | 1951 | 0 | 804.5 | 866.5 | 117.7045 | 0 | 119.1087 | 0 | 1.177 | 0 | 1.1911 | 0 | 1.177 | 1.1911 | 33.4741 | 31.9006 | 32.297
38910.4991 | 1911 | 0 | 38910.4991 | 2086 | 0 | 863 | 925 | 116.6667 | 0 | 127.3504 | 0 | 1.1667 | 0 | 1.2735 | 0 | 1.1667 | 1.2735 | 34.6614 | 23.3643 | 33.4948
38910.4998 | 2091 | 0 | 38910.4998 | 2197 | 0 | 922 | 984 | 127.6557 | 0 | 134.127 | 0 | 1.2766 | 0 | 1.3413 | 0 | 1.2766 | 1.3413 | 23.0693 | 17.1315 | 21.7928
38910.5005 | 2045 | 0 | 38910.5005 | 2080 | 1 | 980.5 | 1042.5 | 124.8474 | 0 | 126.9841 | 0.06105 | 1.2485 | 0 | 1.2698 | 0.0006105 | 1.2485 | 1.2692 | 25.8377 | 23.7797 | 24.5892
38910.5012 | 2053 | 0 | 38910.5012 | 2191 | 0 | 1039.5 | 1101.5 | 125.3358 | 0 | 133.7607 | 0 | 1.2534 | 0 | 1.3376 | 0 | 1.2534 | 1.3376 | 25.3473 | 17.4523 | 24.0939

## C3-7
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 157.5324 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38910.4889 | 0 | 0 | 38910.4889 | 0 | 0 | -21.5 | 40.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4896 | 0 | 0 | 38910.4896 | 0 | 0 | 37.5 | 99.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4902 | 0 | 0 | 38910.4903 | 0 | 0 | 96 | 158 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4909 | 0 | 0 | 38910.4909 | 0 | 0 | 155 | 217 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4916 | 0 | 0 | 38910.4916 | 0 | 0 | 213.5 | 275.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4923 | 0 | 0 | 38910.4923 | 0 | 0 | 272.5 | 334.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.493 | 0 | 0 | 38910.493 | 0 | 0 | 331 | 393 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4936 | 0 | 0 | 38910.4937 | 0 | 0 | 390 | 452 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4943 | 0 | 0 | 38910.4944 | 0 | 0 | 449 | 511 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.495 | 0 | 0 | 38910.495 | 0 | 0 | 507.5 | 569.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4957 | 0 | 0 | 38910.4957 | 0 | 0 | 566.5 | 628.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
38910.4964 | 413 | 433 | 38910.4964 | 18 | 42 | 625 | 687 | 25.2137 | 26.4347 | 1.0989 | 2.5641 | 0.25214 | 0.26435 | 0.010989 | 0.025641 | 0.01221 | 0.014652 | 13548.8529 | 10816.2889 | 396.8804
38910.497 | 2197 | 0 | 38910.4971 | 2171 | 0 | 684 | 746 | 134.127 | 0 | 132.5397 | 0 | 1.3413 | 0 | 1.3254 | 0 | 1.3413 | 1.3254 | 17.4502 | 18.8567 | 16.1089
38910.4977 | 2509 | 0 | 38910.4977 | 1102 | 0 | 742.5 | 804.5 | 153.1746 | 0 | 67.2772 | 0 | 1.5317 | 0 | 0.67277 | 0 | 1.5317 | 0.67277 | 2.845 | 134.1543 | 1.3132
38910.4984 | 2285 | 0 | 38910.4984 | 1761 | 2 | 801.5 | 863.5 | 139.4994 | 0 | 107.5092 | 0.1221 | 1.395 | 0 | 1.0751 | 0.001221 | 1.395 | 1.0739 | 12.9269 | 46.6958 | 11.5319
38910.4991 | 2232 | 0 | 38910.4991 | 2081 | 0 | 860.5 | 922.5 | 136.2637 | 0 | 127.0452 | 0 | 1.3626 | 0 | 1.2705 | 0 | 1.3626 | 1.2705 | 15.6084 | 23.9971 | 14.2458
38910.4998 | 2331 | 0 | 38910.4998 | 2564 | 0 | 919 | 981 | 142.3077 | 0 | 156.5324 | 0 | 1.4231 | 0 | 1.5653 | 0 | 1.4231 | 1.5653 | 10.6984 | 0.63885 | 9.2753
38910.5005 | 2470 | 0 | 38910.5005 | 2031 | 0 | 978 | 1040 | 150.7937 | 0 | 123.9927 | 0 | 1.5079 | 0 | 1.2399 | 0 | 1.5079 | 1.2399 | 4.4688 | 27.0497 | 2.9609
38910.5011 | 2485 | 0 | 38910.5011 | 29 | 0 | 1036.5 | 1098.5 | 151.7094 | 0 | 1.7705 | 0 | 1.5171 | 0 | 0.017705 | 0 | 1.5171 | 0.017705 | 3.8382 | 8797.8621 | 2.3211

## C3-6
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 155.9451 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38910.4889 | 0 | 0 | 38910.4889 | 0 | 0 | -24.5 | 37.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4895 | 0 | 0 | 38910.4895 | 0 | 0 | 34.5 | 96.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4902 | 0 | 0 | 38910.4902 | 0 | 0 | 93.5 | 155.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4909 | 0 | 0 | 38910.4909 | 0 | 0 | 152 | 214 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4916 | 0 | 0 | 38910.4916 | 0 | 0 | 210.5 | 272.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4923 | 0 | 0 | 38910.4923 | 0 | 0 | 269.5 | 331.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4929 | 0 | 0 | 38910.493 | 0 | 0 | 328.5 | 390.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4936 | 0 | 0 | 38910.4936 | 0 | 0 | 387.5 | 449.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4943 | 0 | 0 | 38910.4943 | 0 | 0 | 446 | 508 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.495 | 0 | 0 | 38910.495 | 0 | 0 | 504.5 | 566.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4957 | 0 | 0 | 38910.4957 | 0 | 0 | 563.5 | 625.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
38910.4963 | 1046 | 1012 | 38910.4964 | 1153 | 904 | 622.5 | 684.5 | 63.8584 | 61.7827 | 70.3907 | 55.1893 | 0.63858 | 0.61783 | 0.70391 | 0.55189 | 0.020757 | 0.15201 | 586.7472 | 453.6592 | 40.1903
38910.497 | 2292 | 56 | 38910.497 | 2263 | 0 | 681 | 743 | 139.9267 | 3.4188 | 138.1563 | 0 | 1.3993 | 0.034188 | 1.3816 | 0 | 1.3651 | 1.3816 | 14.568 | 12.8758 | 42.0391
38910.4977 | 2435 | 0 | 38910.4977 | 2195 | 0 | 740 | 802 | 148.6569 | 0 | 134.0049 | 0 | 1.4866 | 0 | 1.34 | 0 | 1.4866 | 1.34 | 4.9027 | 16.3727 | 3.4161
38910.4984 | 2153 | 0 | 38910.4984 | 2200 | 0 | 798.5 | 860.5 | 131.4408 | 0 | 134.3101 | 0 | 1.3144 | 0 | 1.3431 | 0 | 1.3144 | 1.3431 | 18.6428 | 16.1082 | 17.3284
38910.4991 | 2405 | 0 | 38910.4991 | 2538 | 0 | 857.5 | 919.5 | 146.8254 | 0 | 154.9451 | 0 | 1.4683 | 0 | 1.5495 | 0 | 1.4683 | 1.5495 | 6.2112 | 0.64539 | 4.743
38910.4997 | 2106 | 0 | 38910.4998 | 2317 | 0 | 916.5 | 978.5 | 128.5714 | 0 | 141.453 | 0 | 1.2857 | 0 | 1.4145 | 0 | 1.2857 | 1.4145 | 21.2906 | 10.2451 | 20.0049
38910.5004 | 2178 | 0 | 38910.5004 | 2221 | 0 | 975 | 1037 | 132.967 | 0 | 135.5922 | 0 | 1.3297 | 0 | 1.3559 | 0 | 1.3297 | 1.3559 | 17.281 | 15.0104 | 15.9513
38910.5011 | 2343 | 0 | 38910.5011 | 2449 | 0 | 1034 | 1096 | 143.0403 | 0 | 149.5116 | 0 | 1.4304 | 0 | 1.4951 | 0 | 1.4304 | 1.4951 | 9.0218 | 4.303 | 7.5914

## C3-5
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 147.8254 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38910.4888 | 0 | 0 | 38910.4888 | 0 | 0 | -27 | 35 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4895 | 0 | 0 | 38910.4895 | 0 | 0 | 31.5 | 93.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4902 | 0 | 0 | 38910.4902 | 0 | 0 | 90.5 | 152.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4909 | 0 | 0 | 38910.4909 | 0 | 0 | 149 | 211 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4915 | 0 | 0 | 38910.4916 | 0 | 0 | 208 | 270 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4922 | 0 | 0 | 38910.4922 | 0 | 0 | 267 | 329 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4929 | 0 | 0 | 38910.4929 | 0 | 0 | 325.5 | 387.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4936 | 0 | 0 | 38910.4936 | 0 | 0 | 384.5 | 446.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4943 | 0 | 0 | 38910.4943 | 0 | 0 | 443 | 505 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4949 | 0 | 0 | 38910.495 | 0 | 0 | 502 | 564 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4956 | 0 | 0 | 38910.4956 | 0 | 0 | 560.5 | 622.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 484176 | 484176 | 484175.9997
38910.4963 | 960 | 1136 | 38910.4963 | 1040 | 1162 | 619.5 | 681.5 | 58.6081 | 69.3529 | 63.4921 | 70.9402 | 0.58608 | 0.69353 | 0.63492 | 0.7094 | 0.10745 | 0.074481 | 668.4045 | 2664.3483 | 27.6065
38910.497 | 2339 | 0 | 38910.497 | 2168 | 0 | 678.5 | 740.5 | 142.7961 | 0 | 132.3565 | 0 | 1.428 | 0 | 1.3236 | 0 | 1.428 | 1.3236 | 3.522 | 11.6873 | 2.0941
38910.4977 | 2096 | 0 | 38910.4977 | 2142 | 0 | 737 | 799 | 127.9609 | 0 | 130.7692 | 0 | 1.2796 | 0 | 1.3077 | 0 | 1.2796 | 1.3077 | 15.5239 | 13.043 | 14.2442
38910.4983 | 2401 | 0 | 38910.4984 | 1972 | 0 | 796 | 858 | 146.5812 | 0 | 120.3907 | 0 | 1.4658 | 0 | 1.2039 | 0 | 1.4658 | 1.2039 | 0.84881 | 22.788 | 0.617
38910.499 | 1960 | 0 | 38910.499 | 2313 | 0 | 854.5 | 916.5 | 119.6581 | 0 | 141.2088 | 0 | 1.1966 | 0 | 1.4121 | 0 | 1.1966 | 1.4121 | 23.5398 | 4.6857 | 22.3432
38910.4997 | 2405 | 0 | 38910.4997 | 2357 | 0 | 913.5 | 975.5 | 146.8254 | 0 | 143.895 | 0 | 1.4683 | 0 | 1.4389 | 0 | 1.4683 | 1.4389 | 0.68108 | 2.7314 | 0.78717
38910.5004 | 2050 | 0 | 38910.5004 | 2053 | 0 | 972.5 | 1034.5 | 125.1526 | 0 | 125.3358 | 0 | 1.2515 | 0 | 1.2534 | 0 | 1.2515 | 1.2534 | 18.1161 | 17.9435 | 16.8646
38910.5011 | 1990 | 0 | 38910.5011 | 1999 | 0 | 1031 | 1093 | 121.4896 | 0 | 122.0391 | 0 | 1.2149 | 0 | 1.2204 | 0 | 1.2149 | 1.2204 | 21.6774 | 21.1296 | 20.4625

## C3-4
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 156.1282 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38910.4888 | 0 | 0 | 38910.4888 | 0 | 0 | -30 | 32 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4895 | 0 | 0 | 38910.4895 | 0 | 0 | 29 | 91 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4902 | 0 | 0 | 38910.4902 | 0 | 0 | 87.5 | 149.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4908 | 0 | 0 | 38910.4908 | 0 | 0 | 146.5 | 208.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4915 | 0 | 0 | 38910.4915 | 0 | 0 | 205 | 267 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4922 | 0 | 0 | 38910.4922 | 0 | 0 | 264 | 326 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4929 | 0 | 0 | 38910.4929 | 0 | 0 | 322.5 | 384.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4936 | 0 | 0 | 38910.4936 | 0 | 0 | 381.5 | 443.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4942 | 0 | 0 | 38910.4942 | 0 | 0 | 440.5 | 502.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4949 | 0 | 0 | 38910.4949 | 0 | 0 | 499 | 561 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4956 | 0 | 0 | 38910.4956 | 0 | 0 | 558 | 620 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511376 | 511376 | 511375.9997
38910.4963 | 0 | 0 | 38910.4963 | 237 | 114 | 616.5 | 678.5 | 0.030525 | 0 | 14.4689 | 6.9597 | 0.00030525 | 0 | 0.14469 | 0.069597 | 0.00030525 | 0.075092 | 511376 | 1979.1707 | 511375.9997
38910.497 | 2156 | 1 | 38910.497 | 2307 | 0 | 675.5 | 737.5 | 131.6239 | 0.06105 | 140.8425 | 0 | 1.3162 | 0.0006105 | 1.4084 | 0 | 1.3156 | 1.4084 | 18.7055 | 10.8531 | 3919.9159
38910.4976 | 2541 | 0 | 38910.4977 | 2141 | 0 | 734.5 | 796.5 | 155.1282 | 0 | 130.7082 | 0 | 1.5513 | 0 | 1.3071 | 0 | 1.5513 | 1.3071 | 0.64463 | 19.4479 | 0.90665
38910.4983 | 2189 | 0 |  | 2148 | 0 | 792 | 854 | 133.6386 | 0 | 131.1355 | 0 | 1.3364 | 0 | 1.3114 | 0 | 1.3364 | 1.3114 | 16.8287 | 19.0587 | 15.4923
38910.499 | 2086 | 1 | 38910.499 | 2154 | 0 | 852 | 914 | 127.3504 | 0.06105 | 131.5018 | 0 | 1.2735 | 0.0006105 | 1.315 | 0 | 1.2729 | 1.315 | 22.6662 | 18.727 | 7419.3856
38910.4997 | 2030 | 0 | 38910.4997 | 1936 | 0 | 910.5 | 972.5 | 123.9316 | 0 | 118.1929 | 0 | 1.2393 | 0 | 1.1819 | 0 | 1.2393 | 1.1819 | 25.9793 | 32.0961 | 24.74
38910.5004 | 2130 | 0 | 38910.5004 | 1985 | 0 | 969.5 | 1031.5 | 130.0366 | 0 | 121.1844 | 0 | 1.3004 | 0 | 1.2118 | 0 | 1.3004 | 1.2118 | 20.0648 | 28.8353 | 18.7644
38910.501 | 2514 | 0 | 38910.5011 | 2491 | 0 | 1028.5 | 1090.5 | 153.4799 | 0 | 152.0757 | 0 | 1.5348 | 0 | 1.5208 | 0 | 1.5348 | 1.5208 | 1.7255 | 2.6648 | 0.19074

## C2-7
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 154.1136 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38910.4888 | 0 | 0 | 38910.4888 | 0 | 0 | -32.5 | 29.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4894 | 0 | 0 | 38910.4895 | 0 | 0 | 26 | 88 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4901 | 0 | 0 | 38910.4901 | 0 | 0 | 84.5 | 146.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4908 | 0 | 0 | 38910.4908 | 0 | 0 | 143.5 | 205.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4915 | 0 | 0 | 38910.4915 | 0 | 0 | 202.5 | 264.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4922 | 0 | 0 | 38910.4922 | 0 | 0 | 261 | 323 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4928 | 0 | 0 | 38910.4929 | 0 | 0 | 320 | 382 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4935 | 0 | 0 | 38910.4935 | 0 | 0 | 378.5 | 440.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4942 | 0 | 0 | 38910.4942 | 0 | 0 | 437.5 | 499.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4949 | 0 | 0 | 38910.4949 | 0 | 0 | 496.5 | 558.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4956 | 0 | 0 | 38910.4956 | 0 | 0 | 555 | 617 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4962 | 0 | 0 | 38910.4963 | 0 | 0 | 614 | 676 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504776 | 504776 | 504775.9997
38910.4969 | 2234 | 1 | 38910.4969 | 2477 | 0 | 672.5 | 734.5 | 136.3858 | 0.06105 | 151.221 | 0 | 1.3639 | 0.0006105 | 1.5122 | 0 | 1.3632 | 1.5122 | 13.3158 | 1.9128 | 543.1363
38910.4976 | 2124 | 0 | 38910.4976 | 1834 | 0 | 731.5 | 793.5 | 129.6703 | 0 | 111.9658 | 0 | 1.2967 | 0 | 1.1197 | 0 | 1.2967 | 1.1197 | 18.8503 | 37.6434 | 17.5536
38910.4983 | 2508 | 0 | 38910.4983 | 961 | 0 | 790.5 | 852.5 | 153.1136 | 0 | 58.6691 | 0 | 1.5311 | 0 | 0.58669 | 0 | 1.5311 | 0.58669 | 0.65311 | 162.6826 | 0.87803
38910.499 | 1935 | 0 | 38910.499 | 1790 | 1 | 849 | 911 | 118.1319 | 0 | 109.2796 | 0.06105 | 1.1813 | 0 | 1.0928 | 0.0006105 | 1.1813 | 1.0922 | 30.4589 | 41.1056 | 29.2776
38910.4996 | 2341 | 0 | 38910.4997 | 2477 | 0 | 908 | 970 | 142.9182 | 0 | 151.221 | 0 | 1.4292 | 0 | 1.5122 | 0 | 1.4292 | 1.5122 | 7.8334 | 1.9128 | 6.4042
38910.5003 | 2215 | 0 | 38910.5003 | 2068 | 0 | 966.5 | 1028.5 | 135.2259 | 0 | 126.2515 | 0 | 1.3523 | 0 | 1.2625 | 0 | 1.3523 | 1.2625 | 13.9675 | 22.0687 | 12.6152
38910.501 | 2494 | 0 | 38910.501 | 30 | 0 | 1025.5 | 1087.5 | 152.2589 | 0 | 1.8315 | 0 | 1.5226 | 0 | 0.018315 | 0 | 1.5226 | 0.018315 | 1.2181 | 8314.6 | 0.30447

## C2-6
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 157.7155 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38910.4887 | 0 | 0 | 38910.4887 | 0 | 0 | -35.5 | 26.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4894 | 0 | 0 | 38910.4894 | 0 | 0 | 23 | 85 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4901 | 0 | 0 | 38910.4901 | 0 | 0 | 82 | 144 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4908 | 0 | 0 | 38910.4908 | 0 | 0 | 141 | 203 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4914 | 0 | 0 | 38910.4915 | 0 | 0 | 199.5 | 261.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4921 | 0 | 0 | 38910.4921 | 0 | 0 | 258.5 | 320.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4928 | 0 | 0 | 38910.4928 | 0 | 0 | 317 | 379 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4935 | 0 | 0 | 38910.4935 | 0 | 0 | 376 | 438 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4942 | 0 | 0 | 38910.4942 | 0 | 0 | 434.5 | 496.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4948 | 0 | 0 | 38910.4949 | 0 | 0 | 493.5 | 555.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4955 | 0 | 0 | 38910.4955 | 0 | 0 | 552.5 | 614.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4962 | 0 | 0 | 38910.4962 | 0 | 0 | 611 | 673 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
38910.4969 | 948 | 1 | 38910.4969 | 2302 | 1 | 670 | 732 | 57.8755 | 0.06105 | 140.5372 | 0.06105 | 0.57875 | 0.0006105 | 1.4054 | 0.0006105 | 0.57814 | 1.4048 | 174.1944 | 12.2316 | 17812.4095
38910.4976 | 2505 | 0 | 38910.4976 | 2567 | 0 | 728.5 | 790.5 | 152.9304 | 0 | 156.7155 | 0 | 1.5293 | 0 | 1.5672 | 0 | 1.5293 | 1.5672 | 3.1289 | 0.6381 | 1.5996
38910.4983 | 2412 | 0 | 38910.4983 | 2243 | 0 | 787.5 | 849.5 | 147.2527 | 0 | 136.9353 | 0 | 1.4725 | 0 | 1.3694 | 0 | 1.4725 | 1.3694 | 7.1053 | 15.1752 | 5.6328
38910.4989 | 2342 | 1 | 38910.4989 | 2325 | 0 | 846.5 | 908.5 | 142.9792 | 0.06105 | 141.9414 | 0 | 1.4298 | 0.0006105 | 1.4194 | 0 | 1.4292 | 1.4194 | 10.3508 | 11.1131 | 2404.1908
38910.4996 | 2093 | 0 | 38910.4996 | 2172 | 1 | 905 | 967 | 127.7778 | 0 | 132.6007 | 0.06105 | 1.2778 | 0 | 1.326 | 0.0006105 | 1.2778 | 1.3254 | 23.4295 | 18.9949 | 22.1517
38910.5003 | 1995 | 0 | 38910.5003 | 1966 | 0 | 964 | 1026 | 121.7949 | 0 | 120.0244 | 0 | 1.2179 | 0 | 1.2002 | 0 | 1.2179 | 1.2002 | 29.4927 | 31.4028 | 28.2748
38910.501 | 1939 | 0 | 38910.501 | 1972 | 0 | 1022.5 | 1084.5 | 118.3761 | 0 | 120.3907 | 0 | 1.1838 | 0 | 1.2039 | 0 | 1.1838 | 1.2039 | 33.2326 | 31.003 | 32.0488

## C2-5
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 156.0061 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38910.4887 | 0 | 0 | 38910.4887 | 0 | 0 | -38.5 | 23.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4894 | 0 | 0 | 38910.4894 | 0 | 0 | 20.5 | 82.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4901 | 0 | 0 | 38910.4901 | 0 | 0 | 79.5 | 141.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4907 | 0 | 0 | 38910.4908 | 0 | 0 | 138 | 200 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4914 | 0 | 0 | 38910.4914 | 0 | 0 | 196.5 | 258.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4921 | 0 | 0 | 38910.4921 | 0 | 0 | 255.5 | 317.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4928 | 0 | 0 | 38910.4928 | 0 | 0 | 314.5 | 376.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4934 | 0 | 0 | 38910.4935 | 0 | 0 | 373 | 435 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4941 | 0 | 0 | 38910.4942 | 0 | 0 | 432 | 494 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4948 | 0 | 0 | 38910.4948 | 0 | 0 | 490.5 | 552.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4955 | 0 | 0 | 38910.4955 | 0 | 0 | 549.5 | 611.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4962 | 0 | 0 | 38910.4962 | 0 | 0 | 608.5 | 670.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510976 | 510976 | 510975.9997
38910.4969 | 76 | 0 | 38910.4969 | 2420 | 0 | 667 | 729 | 4.6398 | 0 | 147.7411 | 0 | 0.046398 | 0 | 1.4774 | 0 | 0.046398 | 1.4774 | 3262.3421 | 5.5942 | 3262.2957
38910.4975 | 2323 | 0 | 38910.4976 | 2217 | 0 | 726 | 788 | 141.8193 | 0 | 135.348 | 0 | 1.4182 | 0 | 1.3535 | 0 | 1.4182 | 1.3535 | 10.0034 | 15.263 | 8.5853
38910.4982 | 2475 | 0 | 38910.4982 | 2172 | 0 | 784.5 | 846.5 | 151.0989 | 0 | 132.6007 | 0 | 1.511 | 0 | 1.326 | 0 | 1.511 | 1.326 | 3.2477 | 17.651 | 1.7367
38910.4989 | 2106 | 0 | 38910.4989 | 2088 | 0 | 843.5 | 905.5 | 128.5714 | 0 | 127.4725 | 0 | 1.2857 | 0 | 1.2747 | 0 | 1.2857 | 1.2747 | 21.3381 | 22.3841 | 20.0524
38910.4996 | 2449 | 1 | 38910.4996 | 2539 | 1 | 902.5 | 964.5 | 149.5116 | 0.06105 | 155.0061 | 0.06105 | 1.4951 | 0.0006105 | 1.5501 | 0.0006105 | 1.4945 | 1.5495 | 4.6366 | 0.65092 | 68.1505
38910.5003 | 2314 | 0 | 38910.5003 | 2463 | 0 | 961 | 1023 | 141.2698 | 0 | 150.3663 | 0 | 1.4127 | 0 | 1.5037 | 0 | 1.4127 | 1.5037 | 10.4313 | 3.7507 | 9.0186
38910.5009 | 2333 | 0 | 38910.501 | 2373 | 0 | 1020 | 1082 | 142.4298 | 0 | 144.8718 | 0 | 1.4243 | 0 | 1.4487 | 0 | 1.4243 | 1.4487 | 9.5319 | 7.6856 | 8.1076

## C2-4
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 155.5177 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38910.4887 | 0 | 0 | 38910.4887 | 0 | 0 | -41.5 | 20.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4893 | 0 | 0 | 38910.4894 | 0 | 0 | 17.5 | 79.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.49 | 0 | 0 | 38910.49 | 0 | 0 | 76.5 | 138.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4907 | 0 | 0 | 38910.4907 | 0 | 0 | 135 | 197 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4914 | 0 | 0 | 38910.4914 | 0 | 0 | 194 | 256 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4921 | 0 | 0 | 38910.4921 | 0 | 0 | 252.5 | 314.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4927 | 0 | 0 | 38910.4928 | 1 | 0 | 311.5 | 373.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 509376 | 254638 | 509375.9997
38910.4934 | 0 | 0 | 38910.4934 | 0 | 0 | 370.5 | 432.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4941 | 0 | 0 | 38910.4941 | 0 | 0 | 429 | 491 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4948 | 0 | 0 | 38910.4948 | 0 | 0 | 488 | 550 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4955 | 0 | 0 | 38910.4955 | 0 | 0 | 546.5 | 608.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4961 | 0 | 0 | 38910.4962 | 0 | 0 | 605.5 | 667.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509376 | 509376 | 509375.9997
38910.4968 | 2530 | 0 | 38910.4968 | 1680 | 1 | 664.5 | 726.5 | 154.4567 | 0 | 102.5641 | 0.06105 | 1.5446 | 0 | 1.0256 | 0.0006105 | 1.5446 | 1.025 | 0.68696 | 51.7201 | 0.85761
38910.4975 | 1955 | 0 | 38910.4975 | 2009 | 0 | 723 | 785 | 119.3529 | 0 | 122.6496 | 0 | 1.1935 | 0 | 1.2265 | 0 | 1.1935 | 1.2265 | 30.3008 | 26.7984 | 29.1072
38910.4982 | 2526 | 0 | 38910.4982 | 2456 | 0 | 782 | 844 | 154.2125 | 0 | 149.9389 | 0 | 1.5421 | 0 | 1.4994 | 0 | 1.5421 | 1.4994 | 0.8464 | 3.7207 | 0.69573
38910.4989 | 2192 | 0 | 38910.4989 | 2531 | 0 | 840.5 | 902.5 | 133.8217 | 0 | 154.5177 | 0 | 1.3382 | 0 | 1.5452 | 0 | 1.3382 | 1.5452 | 16.2126 | 0.64718 | 14.8744
38910.4995 | 2114 | 3 | 38910.4996 | 2526 | 1 | 899.5 | 961.5 | 129.0598 | 0.18315 | 154.2125 | 0.06105 | 1.2906 | 0.0018315 | 1.5421 | 0.0006105 | 1.2888 | 1.5415 | 24.6622 | 0.84809 | 120.6445
38910.5002 | 2258 | 0 | 38910.5002 | 2228 | 0 | 958.5 | 1020.5 | 137.851 | 0 | 136.0195 | 0 | 1.3785 | 0 | 1.3602 | 0 | 1.3785 | 1.3602 | 12.8158 | 14.3348 | 11.4373
38910.5009 | 2252 | 0 | 38910.5009 | 1983 | 0 | 1017 | 1079 | 137.4847 | 0 | 121.0623 | 0 | 1.3748 | 0 | 1.2106 | 0 | 1.3748 | 1.2106 | 13.1163 | 28.4609 | 11.7415

## C2-3
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 155.7619 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38910.4886 | 0 | 0 | 38910.4886 | 0 | 0 | -44 | 18 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4893 | 0 | 0 | 38910.4893 | 0 | 0 | 15 | 77 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.49 | 0 | 0 | 38910.49 | 0 | 0 | 73.5 | 135.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4907 | 0 | 0 | 38910.4907 | 0 | 0 | 132.5 | 194.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4914 | 0 | 0 | 38910.4914 | 0 | 0 | 191.5 | 253.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.492 | 1 | 0 | 38910.492 | 0 | 0 | 250 | 312 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 255038 | 510176 | 255037.9994
38910.4927 | 0 | 0 | 38910.4927 | 0 | 0 | 308.5 | 370.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4934 | 0 | 0 | 38910.4934 | 0 | 0 | 367.5 | 429.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4941 | 0 | 0 | 38910.4941 | 0 | 0 | 426.5 | 488.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4947 | 0 | 0 | 38910.4948 | 0 | 0 | 485 | 547 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4954 | 0 | 0 | 38910.4955 | 0 | 0 | 544 | 606 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4961 | 0 | 0 | 38910.4961 | 0 | 0 | 602.5 | 664.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
38910.4968 | 715 | 0 | 38910.4968 | 128 | 1 | 661.5 | 723.5 | 43.6508 | 0 | 7.8144 | 0.06105 | 0.43651 | 0 | 0.078144 | 0.0006105 | 0.43651 | 0.077534 | 256.8364 | 1908.9606 | 256.3999
38910.4975 | 2492 | 0 | 38910.4975 | 2181 | 1 | 720.5 | 782.5 | 152.1368 | 0 | 133.1502 | 0.06105 | 1.5214 | 0 | 1.3315 | 0.0006105 | 1.5214 | 1.3309 | 2.3828 | 17.0358 | 0.86146
38910.4981 | 2338 | 0 | 38910.4982 | 2340 | 0 | 779 | 841 | 142.735 | 0 | 142.8571 | 0 | 1.4274 | 0 | 1.4286 | 0 | 1.4274 | 1.4286 | 9.1266 | 9.0333 | 7.6993
38910.4988 | 2038 | 0 | 38910.4989 | 2134 | 0 | 838 | 900 | 124.42 | 0 | 130.2808 | 0 | 1.2442 | 0 | 1.3028 | 0 | 1.2442 | 1.3028 | 25.1904 | 19.5586 | 23.9462
38910.4995 | 1094 | 994 | 38910.4995 | 2132 | 10 | 896.5 | 958.5 | 66.7888 | 60.6838 | 130.1587 | 0.6105 | 0.66789 | 0.60684 | 1.3016 | 0.006105 | 0.06105 | 1.2955 | 29.0837 | 20.2403 | 7.8473
38910.5002 | 2442 | 0 | 38910.5002 | 2499 | 0 | 955.5 | 1017.5 | 149.0842 | 0 | 152.5641 | 0 | 1.4908 | 0 | 1.5256 | 0 | 1.4908 | 1.5256 | 4.4791 | 2.096 | 2.9883
38910.5009 | 2535 | 0 | 38910.5009 | 1909 | 0 | 1014.5 | 1076.5 | 154.7619 | 0 | 116.5446 | 0 | 1.5476 | 0 | 1.1654 | 0 | 1.5476 | 1.1654 | 0.64615 | 33.6501 | 0.90147

## C1-7
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 157.8987 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38910.4886 | 0 | 0 | 38910.4886 | 0 | 0 | -46.5 | 15.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4893 | 0 | 0 | 38910.4893 | 0 | 0 | 12 | 74 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.49 | 0 | 0 | 38910.49 | 0 | 0 | 70.5 | 132.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4906 | 0 | 0 | 38910.4906 | 0 | 0 | 129.5 | 191.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4913 | 0 | 0 | 38910.4913 | 0 | 0 | 188.5 | 250.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.492 | 0 | 0 | 38910.492 | 0 | 0 | 247 | 309 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4927 | 0 | 0 | 38910.4927 | 0 | 0 | 306 | 368 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4934 | 0 | 0 | 38910.4934 | 0 | 0 | 364.5 | 426.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.494 | 0 | 0 | 38910.4941 | 0 | 0 | 423.5 | 485.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4947 | 0 | 0 | 38910.4947 | 0 | 0 | 482.5 | 544.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4954 | 0 | 0 | 38910.4954 | 0 | 0 | 541 | 603 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4961 | 0 | 0 | 38910.4961 | 0 | 0 | 600 | 662 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517176 | 517176 | 517175.9997
38910.4968 | 2489 | 1 | 38910.4968 | 2385 | 0 | 658.5 | 720.5 | 151.9536 | 0.06105 | 145.6044 | 0 | 1.5195 | 0.0006105 | 1.456 | 0 | 1.5189 | 1.456 | 3.9327 | 8.4436 | 750.4313
38910.4974 | 1973 | 0 | 38910.4975 | 1786 | 0 | 717.5 | 779.5 | 120.4518 | 0 | 109.0354 | 0 | 1.2045 | 0 | 1.0904 | 0 | 1.2045 | 1.0904 | 31.0887 | 44.8141 | 29.8842
38910.4981 | 2367 | 0 | 38910.4981 | 1728 | 0 | 776.5 | 838.5 | 144.5055 | 0 | 105.4945 | 0 | 1.4451 | 0 | 1.0549 | 0 | 1.4451 | 1.0549 | 9.2683 | 49.6748 | 7.8232
38910.4988 | 1932 | 0 | 38910.4988 | 2215 | 0 | 835 | 897 | 117.9487 | 0 | 135.2259 | 0 | 1.1795 | 0 | 1.3523 | 0 | 1.1795 | 1.3523 | 33.8706 | 16.7666 | 32.6911
38910.4995 | 1890 | 7 | 38910.4995 | 2109 | 0 | 894 | 956 | 115.3846 | 0.42735 | 128.7546 | 0 | 1.1538 | 0.0042735 | 1.2875 | 0 | 1.1496 | 1.2875 | 37.6 | 22.6354 | 1817.7432
38910.5002 | 2170 | 0 | 38910.5002 | 2570 | 0 | 952.5 | 1014.5 | 132.4786 | 0 | 156.8987 | 0 | 1.3248 | 0 | 1.569 | 0 | 1.3248 | 1.569 | 19.188 | 0.63735 | 17.8632
38910.5008 | 2065 | 0 | 38910.5009 | 33 | 0 | 1011.5 | 1073.5 | 126.0684 | 0 | 2.0147 | 0 | 1.2607 | 0 | 0.020147 | 0 | 1.2607 | 0.020147 | 25.2484 | 7737.5152 | 23.9877

## C1-6
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 157.3492 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38910.4886 | 0 | 0 | 38910.4886 | 0 | 0 | -49.5 | 12.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4892 | 0 | 0 | 38910.4893 | 0 | 0 | 9 | 71 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4899 | 0 | 0 | 38910.4899 | 0 | 0 | 68 | 130 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4906 | 0 | 0 | 38910.4906 | 0 | 0 | 127 | 189 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4913 | 0 | 0 | 38910.4913 | 0 | 0 | 185.5 | 247.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.492 | 0 | 0 | 38910.492 | 0 | 0 | 244.5 | 306.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4927 | 0 | 0 | 38910.4927 | 0 | 0 | 303.5 | 365.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4933 | 0 | 0 | 38910.4933 | 0 | 0 | 362 | 424 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.494 | 0 | 0 | 38910.494 | 0 | 0 | 421 | 483 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4947 | 0 | 0 | 38910.4947 | 0 | 0 | 479.5 | 541.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4954 | 0 | 0 | 38910.4954 | 0 | 0 | 538.5 | 600.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.496 | 0 | 0 | 38910.4961 | 0 | 0 | 597 | 659 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515376 | 515376 | 515375.9997
38910.4967 | 2327 | 1 | 38910.4967 | 2559 | 1 | 656 | 718 | 142.0635 | 0.06105 | 156.2271 | 0.06105 | 1.4206 | 0.0006105 | 1.5623 | 0.0006105 | 1.42 | 1.5617 | 11.447 | 0.72099 | 178.514
38910.4974 | 2457 | 0 | 38910.4974 | 1976 | 0 | 714.5 | 776.5 | 150 | 0 | 120.6349 | 0 | 1.5 | 0 | 1.2063 | 0 | 1.5 | 1.2063 | 4.8995 | 30.4342 | 3.3995
38910.4981 | 2381 | 0 | 38910.4981 | 2561 | 0 | 773.5 | 835.5 | 145.3602 | 0 | 156.3492 | 0 | 1.4536 | 0 | 1.5635 | 0 | 1.4536 | 1.5635 | 8.2478 | 0.63959 | 6.7942
38910.4988 | 2296 | 0 | 38910.4988 | 2349 | 0 | 832.5 | 894.5 | 140.1709 | 0 | 143.4066 | 0 | 1.4017 | 0 | 1.4341 | 0 | 1.4017 | 1.4341 | 12.2552 | 9.7224 | 10.8535
38910.4994 | 2172 | 1 | 38910.4995 | 2102 | 1 | 891 | 953 | 132.6007 | 0.06105 | 128.3272 | 0.06105 | 1.326 | 0.0006105 | 1.2833 | 0.0006105 | 1.3254 | 1.2827 | 18.7105 | 22.6841 | 7476.9163
38910.5001 | 2195 | 0 | 38910.5002 | 2294 | 0 | 950 | 1012 | 134.0049 | 0 | 140.0488 | 0 | 1.34 | 0 | 1.4005 | 0 | 1.34 | 1.4005 | 17.4205 | 12.3531 | 16.0805
38910.5008 | 2483 | 0 | 38910.5008 | 2339 | 0 | 1008.5 | 1070.5 | 151.5873 | 0 | 142.7961 | 0 | 1.5159 | 0 | 1.428 | 0 | 1.5159 | 1.428 | 3.801 | 10.1915 | 2.2852

## C1-5
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 155.823 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38910.4885 | 0 | 0 | 38910.4885 | 0 | 0 | -52.5 | 9.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4892 | 0 | 0 | 38910.4892 | 0 | 0 | 6.5 | 68.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4899 | 0 | 0 | 38910.4899 | 0 | 0 | 65.5 | 127.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4906 | 0 | 0 | 38910.4906 | 0 | 0 | 124 | 186 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4912 | 0 | 0 | 38910.4913 | 0 | 0 | 182.5 | 244.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4919 | 0 | 0 | 38910.4919 | 0 | 0 | 241.5 | 303.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4926 | 0 | 0 | 38910.4926 | 0 | 0 | 300.5 | 362.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4933 | 0 | 0 | 38910.4933 | 0 | 0 | 359 | 421 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.494 | 0 | 0 | 38910.494 | 0 | 0 | 418 | 480 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4947 | 0 | 0 | 38910.4947 | 0 | 0 | 476.5 | 538.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4953 | 0 | 0 | 38910.4953 | 0 | 0 | 535.5 | 597.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.496 | 0 | 0 | 38910.496 | 0 | 0 | 594.5 | 656.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510376 | 510376 | 510375.9997
38910.4967 | 2069 | 6 | 38910.4967 | 2026 | 2 | 653 | 715 | 126.3126 | 0.3663 | 123.6874 | 0.1221 | 1.2631 | 0.003663 | 1.2369 | 0.001221 | 1.2595 | 1.2357 | 23.6948 | 26.1158 | 1647.5825
38910.4974 | 2085 | 0 | 38910.4974 | 2513 | 0 | 712 | 774 | 127.2894 | 0 | 153.4188 | 0 | 1.2729 | 0 | 1.5342 | 0 | 1.2729 | 1.5342 | 22.4163 | 1.5671 | 21.1434
38910.4981 | 2536 | 0 | 38910.4981 | 2473 | 0 | 770.5 | 832.5 | 154.823 | 0 | 150.9768 | 0 | 1.5482 | 0 | 1.5098 | 0 | 1.5482 | 1.5098 | 0.6459 | 3.2099 | 0.90233
38910.4987 | 1933 | 0 | 38910.4987 | 2417 | 0 | 829.5 | 891.5 | 118.0098 | 0 | 147.558 | 0 | 1.1801 | 0 | 1.4756 | 0 | 1.1801 | 1.4756 | 32.0424 | 5.6012 | 30.8623
38910.4994 | 1995 | 3 | 38910.4994 | 2008 | 2 | 888.5 | 950.5 | 121.7949 | 0.18315 | 122.5885 | 0.1221 | 1.2179 | 0.0018315 | 1.2259 | 0.001221 | 1.2161 | 1.2247 | 28.1365 | 27.2341 | 3955.4481
38910.5001 | 2365 | 0 | 38910.5001 | 1953 | 0 | 947 | 1009 | 144.3834 | 0 | 119.2308 | 0 | 1.4438 | 0 | 1.1923 | 0 | 1.4438 | 1.1923 | 7.923 | 30.6902 | 6.4792
38910.5008 | 2456 | 0 | 38910.5008 | 2153 | 0 | 1006 | 1068 | 149.9389 | 0 | 131.4408 | 0 | 1.4994 | 0 | 1.3144 | 0 | 1.4994 | 1.3144 | 3.9243 | 18.5499 | 2.4249

## C1-4
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 156.8608 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38910.4885 | 0 | 0 | 38910.4885 | 0 | 0 | -55 | 7 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4892 | 0 | 0 | 38910.4892 | 0 | 0 | 3.5 | 65.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4899 | 0 | 0 | 38910.4899 | 0 | 0 | 62.5 | 124.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4905 | 0 | 0 | 38910.4906 | 0 | 0 | 121 | 183 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4912 | 0 | 0 | 38910.4912 | 0 | 0 | 180 | 242 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4919 | 0 | 0 | 38910.4919 | 0 | 0 | 239 | 301 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4926 | 0 | 0 | 38910.4926 | 0 | 0 | 297.5 | 359.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4933 | 0 | 0 | 38910.4933 | 0 | 0 | 356.5 | 418.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4939 | 0 | 0 | 38910.494 | 0 | 0 | 415 | 477 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4946 | 0 | 0 | 38910.4946 | 0 | 0 | 474 | 536 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4953 | 0 | 0 | 38910.4953 | 0 | 0 | 532.5 | 594.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.496 | 0 | 0 | 38910.496 | 0 | 0 | 591.5 | 653.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513776 | 513776 | 513775.9997
38910.4967 | 2553 | 1 | 38910.4967 | 2537 | 1 | 650.5 | 712.5 | 155.8608 | 0.06105 | 154.884 | 0.06105 | 1.5586 | 0.0006105 | 1.5488 | 0.0006105 | 1.558 | 1.5482 | 0.66092 | 1.3578 | 20.6036
38910.4973 | 2519 | 0 | 38910.4974 | 2313 | 0 | 709 | 771 | 153.7851 | 0 | 141.2088 | 0 | 1.5379 | 0 | 1.4121 | 0 | 1.5379 | 1.4121 | 2 | 11.0843 | 0.46215
38910.498 | 2312 | 0 | 38910.498 | 2466 | 0 | 768 | 830 | 141.1477 | 0 | 150.5495 | 0 | 1.4115 | 0 | 1.5055 | 0 | 1.4115 | 1.5055 | 11.1324 | 4.1922 | 9.7209
38910.4987 | 2144 | 0 | 38910.4987 | 1932 | 0 | 826.5 | 888.5 | 130.8913 | 0 | 117.9487 | 0 | 1.3089 | 0 | 1.1795 | 0 | 1.3089 | 1.1795 | 19.8405 | 32.9907 | 18.5316
38910.4994 | 1656 | 17 | 38910.4994 | 2362 | 5 | 885.5 | 947.5 | 101.0989 | 1.0379 | 144.2002 | 0.30525 | 1.011 | 0.010379 | 1.442 | 0.0030525 | 1.0006 | 1.4389 | 63.147 | 8.8281 | 427.731
38910.5001 | 2256 | 0 | 38910.5001 | 2151 | 0 | 944.5 | 1006.5 | 137.7289 | 0 | 131.3187 | 0 | 1.3773 | 0 | 1.3132 | 0 | 1.3773 | 1.3132 | 13.891 | 19.4505 | 12.5137
38910.5007 | 1951 | 0 | 38910.5008 | 2344 | 0 | 1003 | 1065 | 119.1087 | 0 | 143.1013 | 0 | 1.1911 | 0 | 1.431 | 0 | 1.1911 | 1.431 | 31.6955 | 9.6152 | 30.5045

## C1-3
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 149.7179 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38910.4885 | 0 | 0 | 38910.4885 | 0 | 0 | -58 | 4 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4891 | 0 | 0 | 38910.4892 | 0 | 0 | 1 | 63 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4898 | 0 | 0 | 38910.4898 | 0 | 0 | 59.5 | 121.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4905 | 0 | 0 | 38910.4905 | 0 | 0 | 118.5 | 180.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4912 | 0 | 0 | 38910.4912 | 0 | 0 | 177.5 | 239.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4919 | 0 | 0 | 38910.4919 | 0 | 0 | 236 | 298 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4925 | 0 | 0 | 38910.4926 | 0 | 0 | 294.5 | 356.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4932 | 0 | 0 | 38910.4932 | 0 | 0 | 353.5 | 415.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4939 | 0 | 0 | 38910.4939 | 0 | 0 | 412.5 | 474.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4946 | 0 | 0 | 38910.4946 | 0 | 0 | 471 | 533 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4953 | 0 | 0 | 38910.4953 | 0 | 0 | 530 | 592 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4959 | 0 | 0 | 38910.496 | 0 | 0 | 588.5 | 650.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
38910.4966 | 2088 | 1 | 38910.4966 | 2356 | 0 | 647.5 | 709.5 | 127.4725 | 0.06105 | 143.8339 | 0 | 1.2747 | 0.0006105 | 1.4383 | 0 | 1.2741 | 1.4383 | 17.6664 | 4.0908 | 1428.1051
38910.4973 | 2436 | 0 | 38910.4973 | 1713 | 1 | 706.5 | 768.5 | 148.7179 | 0 | 104.5788 | 0.06105 | 1.4872 | 0 | 1.0458 | 0.0006105 | 1.4872 | 1.0452 | 0.67241 | 43.2465 | 0.81477
38910.498 | 1902 | 0 | 38910.498 | 1943 | 0 | 765 | 827 | 116.1172 | 0 | 118.6203 | 0 | 1.1612 | 0 | 1.1862 | 0 | 1.1612 | 1.1862 | 28.9369 | 26.2162 | 27.7757
38910.4987 | 2012 | 0 | 38910.4987 | 2047 | 3 | 824 | 886 | 122.8327 | 0 | 124.9695 | 0.18315 | 1.2283 | 0 | 1.2497 | 0.0018315 | 1.2283 | 1.2479 | 21.8877 | 19.9795 | 20.6593
38910.4994 | 2213 | 493 | 38910.4994 | 1676 | 937 | 882.5 | 944.5 | 135.1038 | 30.0977 | 102.3199 | 57.2039 | 1.351 | 0.30098 | 1.0232 | 0.57204 | 1.0501 | 0.45116 | 28.4323 | 56.1458 | 18.4979
38910.5 | 2271 | 0 | 38910.5 | 2156 | 0 | 941.5 | 1003.5 | 138.6447 | 0 | 131.6239 | 0 | 1.3864 | 0 | 1.3162 | 0 | 1.3864 | 1.3162 | 7.9868 | 13.7468 | 6.6003
38910.5007 | 2435 | 0 | 38910.5007 | 2109 | 0 | 1000.5 | 1062.5 | 148.6569 | 0 | 128.7546 | 0 | 1.4866 | 0 | 1.2875 | 0 | 1.4866 | 1.2875 | 0.71376 | 16.2817 | 0.77281

## C1-2
Penlight Test 20 |  |  | 2006-07-12 | 11:44 |  | Vs = |  | 156.7387 |  | R = | 100
TS/TP | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38910.4884 | 0 | 0 | 38910.4884 | 0 | 0 | -61 | 1 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4891 | 0 | 0 | 38910.4891 | 0 | 0 | -2 | 60 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4898 | 0 | 0 | 38910.4898 | 0 | 0 | 56.5 | 118.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4905 | 0 | 0 | 38910.4905 | 0 | 0 | 115.5 | 177.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4912 | 0 | 0 | 38910.4912 | 0 | 0 | 174.5 | 236.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4918 | 0 | 0 | 38910.4919 | 0 | 0 | 233 | 295 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4925 | 0 | 0 | 38910.4925 | 0 | 0 | 292 | 354 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4932 | 0 | 0 | 38910.4932 | 0 | 0 | 350.5 | 412.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4939 | 0 | 0 | 38910.4939 | 0 | 0 | 409.5 | 471.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4946 | 0 | 0 | 38910.4946 | 0 | 0 | 468.5 | 530.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4952 | 0 | 0 | 38910.4953 | 0 | 0 | 527 | 589 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4959 | 0 | 0 | 38910.4959 | 0 | 0 | 586 | 648 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513376 | 513376 | 513375.9997
38910.4966 | 2551 | 1 | 38910.4966 | 2536 | 1 | 644.5 | 706.5 | 155.7387 | 0.06105 | 154.823 | 0.06105 | 1.5574 | 0.0006105 | 1.5482 | 0.0006105 | 1.5568 | 1.5476 | 0.66208 | 1.3163 | 19.9816
38910.4973 | 2363 | 0 | 38910.4973 | 2415 | 0 | 703.5 | 765.5 | 144.2613 | 0 | 147.4359 | 0 | 1.4426 | 0 | 1.4744 | 0 | 1.4426 | 1.4744 | 8.6492 | 6.3097 | 7.2066
38910.498 | 2500 | 0 | 38910.498 | 2351 | 0 | 762.5 | 824.5 | 152.6252 | 0 | 143.5287 | 0 | 1.5263 | 0 | 1.4353 | 0 | 1.5263 | 1.4353 | 2.6952 | 9.2037 | 1.1689
38910.4986 | 2123 | 0 | 38910.4987 | 2031 | 0 | 821 | 883 | 129.6093 | 0 | 123.9927 | 0 | 1.2961 | 0 | 1.2399 | 0 | 1.2961 | 1.2399 | 20.9317 | 26.4097 | 19.6356
38910.4993 | 2391 | 0 | 38910.4993 | 2387 | 0 | 880 | 942 | 145.9707 | 0 | 145.7265 | 0 | 1.4597 | 0 | 1.4573 | 0 | 1.4597 | 1.4573 | 7.3768 | 7.5568 | 5.9171
38910.5 | 2234 | 0 | 38910.5 | 2447 | 0 | 938.5 | 1000.5 | 136.3858 | 0 | 149.3895 | 0 | 1.3639 | 0 | 1.4939 | 0 | 1.3639 | 1.4939 | 14.923 | 4.9195 | 13.5591
38910.5007 | 2078 | 0 | 38910.5007 | 2374 | 0 | 997.5 | 1059.5 | 126.862 | 0 | 144.9328 | 0 | 1.2686 | 0 | 1.4493 | 0 | 1.2686 | 1.4493 | 23.5505 | 8.1457 | 22.2819

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 20 |  |  | 2006-07-12 | 11:44
38910.4884 | 0 | 0 | 1 | TS/TP | 7-C | Tray
38910.4891 | 0 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38910.4898 | 0 | 0 | 1
38910.4905 | 0 | 0 | 1
38910.4912 | 0 | 0 | 1
38910.4918 | 0 | 0 | 1
38910.4925 | 0 | 0 | 1
38910.4932 | 0 | 0 | 1
38910.4939 | 0 | 0 | 1
38910.4946 | 0 | 0 | 1
38910.4952 | 0 | 0 | 1
38910.4959 | 0 | 0 | 1
38910.4966 | 2551 | 1 | 1
38910.4973 | 2363 | 0 | 1
38910.498 | 2500 | 0 | 1
38910.4986 | 2123 | 0 | 1
38910.4993 | 2391 | 0 | 1
38910.5 | 2234 | 0 | 1
38910.5007 | 2078 | 0 | 1
38910.4884 | 0 | 0 | 2
38910.4891 | 0 | 0 | 2
38910.4898 | 0 | 0 | 2
38910.4905 | 0 | 0 | 2
38910.4912 | 0 | 0 | 2
38910.4919 | 0 | 0 | 2
38910.4925 | 0 | 0 | 2
38910.4932 | 0 | 0 | 2
38910.4939 | 0 | 0 | 2
38910.4946 | 0 | 0 | 2
38910.4953 | 0 | 0 | 2
38910.4959 | 0 | 0 | 2
38910.4966 | 2536 | 1 | 2
38910.4973 | 2415 | 0 | 2
38910.498 | 2351 | 0 | 2
38910.4987 | 2031 | 0 | 2
38910.4993 | 2387 | 0 | 2
38910.5 | 2447 | 0 | 2
38910.5007 | 2374 | 0 | 2
38910.4885 | 0 | 0 | 3
38910.4891 | 0 | 0 | 3
38910.4898 | 0 | 0 | 3
38910.4905 | 0 | 0 | 3
38910.4912 | 0 | 0 | 3
38910.4919 | 0 | 0 | 3
38910.4925 | 0 | 0 | 3
38910.4932 | 0 | 0 | 3
38910.4939 | 0 | 0 | 3
38910.4946 | 0 | 0 | 3
38910.4953 | 0 | 0 | 3
38910.4959 | 0 | 0 | 3
38910.4966 | 2088 | 1 | 3
38910.4973 | 2436 | 0 | 3
38910.498 | 1902 | 0 | 3
38910.4987 | 2012 | 0 | 3
38910.4994 | 2213 | 493 | 3
38910.5 | 2271 | 0 | 3
38910.5007 | 2435 | 0 | 3
38910.4885 | 0 | 0 | 4
38910.4892 | 0 | 0 | 4
38910.4898 | 0 | 0 | 4
38910.4905 | 0 | 0 | 4
38910.4912 | 0 | 0 | 4
38910.4919 | 0 | 0 | 4
38910.4926 | 0 | 0 | 4
38910.4932 | 0 | 0 | 4
38910.4939 | 0 | 0 | 4
38910.4946 | 0 | 0 | 4
38910.4953 | 0 | 0 | 4
38910.496 | 0 | 0 | 4
38910.4966 | 2356 | 0 | 4
38910.4973 | 1713 | 1 | 4
38910.498 | 1943 | 0 | 4
38910.4987 | 2047 | 3 | 4
38910.4994 | 1676 | 937 | 4
38910.5 | 2156 | 0 | 4
38910.5007 | 2109 | 0 | 4
38910.4885 | 0 | 0 | 5
38910.4892 | 0 | 0 | 5
38910.4899 | 0 | 0 | 5
38910.4905 | 0 | 0 | 5
38910.4912 | 0 | 0 | 5
38910.4919 | 0 | 0 | 5
38910.4926 | 0 | 0 | 5
38910.4933 | 0 | 0 | 5
38910.4939 | 0 | 0 | 5
38910.4946 | 0 | 0 | 5
38910.4953 | 0 | 0 | 5
38910.496 | 0 | 0 | 5
38910.4967 | 2553 | 1 | 5
38910.4973 | 2519 | 0 | 5
38910.498 | 2312 | 0 | 5
38910.4987 | 2144 | 0 | 5
38910.4994 | 1656 | 17 | 5
38910.5001 | 2256 | 0 | 5
38910.5007 | 1951 | 0 | 5
38910.4885 | 0 | 0 | 6
38910.4892 | 0 | 0 | 6
38910.4899 | 0 | 0 | 6
38910.4906 | 0 | 0 | 6
38910.4912 | 0 | 0 | 6
38910.4919 | 0 | 0 | 6
38910.4926 | 0 | 0 | 6
38910.4933 | 0 | 0 | 6
38910.494 | 0 | 0 | 6
38910.4946 | 0 | 0 | 6
38910.4953 | 0 | 0 | 6
38910.496 | 0 | 0 | 6
38910.4967 | 2537 | 1 | 6
38910.4974 | 2313 | 0 | 6
38910.498 | 2466 | 0 | 6
38910.4987 | 1932 | 0 | 6
38910.4994 | 2362 | 5 | 6
38910.5001 | 2151 | 0 | 6
38910.5008 | 2344 | 0 | 6
38910.4885 | 0 | 0 | 7
38910.4892 | 0 | 0 | 7
38910.4899 | 0 | 0 | 7
38910.4906 | 0 | 0 | 7
38910.4912 | 0 | 0 | 7
38910.4919 | 0 | 0 | 7
38910.4926 | 0 | 0 | 7
38910.4933 | 0 | 0 | 7
38910.494 | 0 | 0 | 7
38910.4947 | 0 | 0 | 7
38910.4953 | 0 | 0 | 7
38910.496 | 0 | 0 | 7
38910.4967 | 2069 | 6 | 7
38910.4974 | 2085 | 0 | 7
38910.4981 | 2536 | 0 | 7
38910.4987 | 1933 | 0 | 7
38910.4994 | 1995 | 3 | 7
38910.5001 | 2365 | 0 | 7
38910.5008 | 2456 | 0 | 7
38910.4885 | 0 | 0 | 8
38910.4892 | 0 | 0 | 8
38910.4899 | 0 | 0 | 8
38910.4906 | 0 | 0 | 8
38910.4913 | 0 | 0 | 8
38910.4919 | 0 | 0 | 8
38910.4926 | 0 | 0 | 8
38910.4933 | 0 | 0 | 8
38910.494 | 0 | 0 | 8
38910.4947 | 0 | 0 | 8
38910.4953 | 0 | 0 | 8
38910.496 | 0 | 0 | 8
38910.4967 | 2026 | 2 | 8
38910.4974 | 2513 | 0 | 8
38910.4981 | 2473 | 0 | 8
38910.4987 | 2417 | 0 | 8
38910.4994 | 2008 | 2 | 8
38910.5001 | 1953 | 0 | 8
38910.5008 | 2153 | 0 | 8
38910.4886 | 0 | 0 | 9
38910.4892 | 0 | 0 | 9
38910.4899 | 0 | 0 | 9
38910.4906 | 0 | 0 | 9
38910.4913 | 0 | 0 | 9
38910.492 | 0 | 0 | 9
38910.4927 | 0 | 0 | 9
38910.4933 | 0 | 0 | 9
38910.494 | 0 | 0 | 9
38910.4947 | 0 | 0 | 9
38910.4954 | 0 | 0 | 9
38910.496 | 0 | 0 | 9
38910.4967 | 2327 | 1 | 9
38910.4974 | 2457 | 0 | 9
38910.4981 | 2381 | 0 | 9
38910.4988 | 2296 | 0 | 9
38910.4994 | 2172 | 1 | 9
38910.5001 | 2195 | 0 | 9
38910.5008 | 2483 | 0 | 9
38910.4886 | 0 | 0 | 10
38910.4893 | 0 | 0 | 10
38910.4899 | 0 | 0 | 10
38910.4906 | 0 | 0 | 10
38910.4913 | 0 | 0 | 10
38910.492 | 0 | 0 | 10
38910.4927 | 0 | 0 | 10
38910.4933 | 0 | 0 | 10
38910.494 | 0 | 0 | 10
38910.4947 | 0 | 0 | 10
38910.4954 | 0 | 0 | 10
38910.4961 | 0 | 0 | 10
38910.4967 | 2559 | 1 | 10
38910.4974 | 1976 | 0 | 10
38910.4981 | 2561 | 0 | 10
38910.4988 | 2349 | 0 | 10
38910.4995 | 2102 | 1 | 10
38910.5002 | 2294 | 0 | 10
38910.5008 | 2339 | 0 | 10
38910.4886 | 0 | 0 | 11
38910.4893 | 0 | 0 | 11
38910.49 | 0 | 0 | 11
38910.4906 | 0 | 0 | 11
38910.4913 | 0 | 0 | 11
38910.492 | 0 | 0 | 11
38910.4927 | 0 | 0 | 11
38910.4934 | 0 | 0 | 11
38910.494 | 0 | 0 | 11
38910.4947 | 0 | 0 | 11
38910.4954 | 0 | 0 | 11
38910.4961 | 0 | 0 | 11
38910.4968 | 2489 | 1 | 11
38910.4974 | 1973 | 0 | 11
38910.4981 | 2367 | 0 | 11
38910.4988 | 1932 | 0 | 11
38910.4995 | 1890 | 7 | 11
38910.5002 | 2170 | 0 | 11
38910.5008 | 2065 | 0 | 11
38910.4886 | 0 | 0 | 12
38910.4893 | 0 | 0 | 12
38910.49 | 0 | 0 | 12
38910.4906 | 0 | 0 | 12
38910.4913 | 0 | 0 | 12
38910.492 | 0 | 0 | 12
38910.4927 | 0 | 0 | 12
38910.4934 | 0 | 0 | 12
38910.4941 | 0 | 0 | 12
38910.4947 | 0 | 0 | 12
38910.4954 | 0 | 0 | 12
38910.4961 | 0 | 0 | 12
38910.4968 | 2385 | 0 | 12
38910.4975 | 1786 | 0 | 12
38910.4981 | 1728 | 0 | 12
38910.4988 | 2215 | 0 | 12
38910.4995 | 2109 | 0 | 12
38910.5002 | 2570 | 0 | 12
38910.5009 | 33 | 0 | 12
38910.4886 | 0 | 0 | 13
38910.4893 | 0 | 0 | 13
38910.49 | 0 | 0 | 13
38910.4907 | 0 | 0 | 13
38910.4914 | 0 | 0 | 13
38910.492 | 1 | 0 | 13
38910.4927 | 0 | 0 | 13
38910.4934 | 0 | 0 | 13
38910.4941 | 0 | 0 | 13
38910.4947 | 0 | 0 | 13
38910.4954 | 0 | 0 | 13
38910.4961 | 0 | 0 | 13
38910.4968 | 715 | 0 | 13
38910.4975 | 2492 | 0 | 13
38910.4981 | 2338 | 0 | 13
38910.4988 | 2038 | 0 | 13
38910.4995 | 1094 | 994 | 13
38910.5002 | 2442 | 0 | 13
38910.5009 | 2535 | 0 | 13
38910.4886 | 0 | 0 | 14
38910.4893 | 0 | 0 | 14
38910.49 | 0 | 0 | 14
38910.4907 | 0 | 0 | 14
38910.4914 | 0 | 0 | 14
38910.492 | 0 | 0 | 14
38910.4927 | 0 | 0 | 14
38910.4934 | 0 | 0 | 14
38910.4941 | 0 | 0 | 14
38910.4948 | 0 | 0 | 14
38910.4955 | 0 | 0 | 14
38910.4961 | 0 | 0 | 14
38910.4968 | 128 | 1 | 14
38910.4975 | 2181 | 1 | 14
38910.4982 | 2340 | 0 | 14
38910.4989 | 2134 | 0 | 14
38910.4995 | 2132 | 10 | 14
38910.5002 | 2499 | 0 | 14
38910.5009 | 1909 | 0 | 14
38910.4887 | 0 | 0 | 15
38910.4893 | 0 | 0 | 15
38910.49 | 0 | 0 | 15
38910.4907 | 0 | 0 | 15
38910.4914 | 0 | 0 | 15
38910.4921 | 0 | 0 | 15
38910.4927 | 0 | 0 | 15
38910.4934 | 0 | 0 | 15
38910.4941 | 0 | 0 | 15
38910.4948 | 0 | 0 | 15
38910.4955 | 0 | 0 | 15
38910.4961 | 0 | 0 | 15
38910.4968 | 2530 | 0 | 15
38910.4975 | 1955 | 0 | 15
38910.4982 | 2526 | 0 | 15
38910.4989 | 2192 | 0 | 15
38910.4995 | 2114 | 3 | 15
38910.5002 | 2258 | 0 | 15
38910.5009 | 2252 | 0 | 15
38910.4887 | 0 | 0 | 16
38910.4894 | 0 | 0 | 16
38910.49 | 0 | 0 | 16
38910.4907 | 0 | 0 | 16
38910.4914 | 0 | 0 | 16
38910.4921 | 0 | 0 | 16
38910.4928 | 1 | 0 | 16
38910.4934 | 0 | 0 | 16
38910.4941 | 0 | 0 | 16
38910.4948 | 0 | 0 | 16
38910.4955 | 0 | 0 | 16
38910.4962 | 0 | 0 | 16
38910.4968 | 1680 | 1 | 16
38910.4975 | 2009 | 0 | 16
38910.4982 | 2456 | 0 | 16
38910.4989 | 2531 | 0 | 16
38910.4996 | 2526 | 1 | 16
38910.5002 | 2228 | 0 | 16
38910.5009 | 1983 | 0 | 16
38910.4887 | 0 | 0 | 17
38910.4894 | 0 | 0 | 17
38910.4901 | 0 | 0 | 17
38910.4907 | 0 | 0 | 17
38910.4914 | 0 | 0 | 17
38910.4921 | 0 | 0 | 17
38910.4928 | 0 | 0 | 17
38910.4934 | 0 | 0 | 17
38910.4941 | 0 | 0 | 17
38910.4948 | 0 | 0 | 17
38910.4955 | 0 | 0 | 17
38910.4962 | 0 | 0 | 17
38910.4969 | 76 | 0 | 17
38910.4975 | 2323 | 0 | 17
38910.4982 | 2475 | 0 | 17
38910.4989 | 2106 | 0 | 17
38910.4996 | 2449 | 1 | 17
38910.5003 | 2314 | 0 | 17
38910.5009 | 2333 | 0 | 17
38910.4887 | 0 | 0 | 18
38910.4894 | 0 | 0 | 18
38910.4901 | 0 | 0 | 18
38910.4908 | 0 | 0 | 18
38910.4914 | 0 | 0 | 18
38910.4921 | 0 | 0 | 18
38910.4928 | 0 | 0 | 18
38910.4935 | 0 | 0 | 18
38910.4942 | 0 | 0 | 18
38910.4948 | 0 | 0 | 18
38910.4955 | 0 | 0 | 18
38910.4962 | 0 | 0 | 18
38910.4969 | 2420 | 0 | 18
38910.4976 | 2217 | 0 | 18
38910.4982 | 2172 | 0 | 18
38910.4989 | 2088 | 0 | 18
38910.4996 | 2539 | 1 | 18
38910.5003 | 2463 | 0 | 18
38910.501 | 2373 | 0 | 18
38910.4887 | 0 | 0 | 19
38910.4894 | 0 | 0 | 19
38910.4901 | 0 | 0 | 19
38910.4908 | 0 | 0 | 19
38910.4914 | 0 | 0 | 19
38910.4921 | 0 | 0 | 19
38910.4928 | 0 | 0 | 19
38910.4935 | 0 | 0 | 19
38910.4942 | 0 | 0 | 19
38910.4948 | 0 | 0 | 19
38910.4955 | 0 | 0 | 19
38910.4962 | 0 | 0 | 19
38910.4969 | 948 | 1 | 19
38910.4976 | 2505 | 0 | 19
38910.4983 | 2412 | 0 | 19
38910.4989 | 2342 | 1 | 19
38910.4996 | 2093 | 0 | 19
38910.5003 | 1995 | 0 | 19
38910.501 | 1939 | 0 | 19
38910.4887 | 0 | 0 | 20
38910.4894 | 0 | 0 | 20
38910.4901 | 0 | 0 | 20
38910.4908 | 0 | 0 | 20
38910.4915 | 0 | 0 | 20
38910.4921 | 0 | 0 | 20
38910.4928 | 0 | 0 | 20
38910.4935 | 0 | 0 | 20
38910.4942 | 0 | 0 | 20
38910.4949 | 0 | 0 | 20
38910.4955 | 0 | 0 | 20
38910.4962 | 0 | 0 | 20
38910.4969 | 2302 | 1 | 20
38910.4976 | 2567 | 0 | 20
38910.4983 | 2243 | 0 | 20
38910.4989 | 2325 | 0 | 20
38910.4996 | 2172 | 1 | 20
38910.5003 | 1966 | 0 | 20
38910.501 | 1972 | 0 | 20
38910.4888 | 0 | 0 | 21
38910.4894 | 0 | 0 | 21
38910.4901 | 0 | 0 | 21
38910.4908 | 0 | 0 | 21
38910.4915 | 0 | 0 | 21
38910.4922 | 0 | 0 | 21
38910.4928 | 0 | 0 | 21
38910.4935 | 0 | 0 | 21
38910.4942 | 0 | 0 | 21
38910.4949 | 0 | 0 | 21
38910.4956 | 0 | 0 | 21
38910.4962 | 0 | 0 | 21
38910.4969 | 2234 | 1 | 21
38910.4976 | 2124 | 0 | 21
38910.4983 | 2508 | 0 | 21
38910.499 | 1935 | 0 | 21
38910.4996 | 2341 | 0 | 21
38910.5003 | 2215 | 0 | 21
38910.501 | 2494 | 0 | 21
38910.4888 | 0 | 0 | 22
38910.4895 | 0 | 0 | 22
38910.4901 | 0 | 0 | 22
38910.4908 | 0 | 0 | 22
38910.4915 | 0 | 0 | 22
38910.4922 | 0 | 0 | 22
38910.4929 | 0 | 0 | 22
38910.4935 | 0 | 0 | 22
38910.4942 | 0 | 0 | 22
38910.4949 | 0 | 0 | 22
38910.4956 | 0 | 0 | 22
38910.4963 | 0 | 0 | 22
38910.4969 | 2477 | 0 | 22
38910.4976 | 1834 | 0 | 22
38910.4983 | 961 | 0 | 22
38910.499 | 1790 | 1 | 22
38910.4997 | 2477 | 0 | 22
38910.5003 | 2068 | 0 | 22
38910.501 | 30 | 0 | 22
38910.4888 | 0 | 0 | 23
38910.4895 | 0 | 0 | 23
38910.4902 | 0 | 0 | 23
38910.4908 | 0 | 0 | 23
38910.4915 | 0 | 0 | 23
38910.4922 | 0 | 0 | 23
38910.4929 | 0 | 0 | 23
38910.4936 | 0 | 0 | 23
38910.4942 | 0 | 0 | 23
38910.4949 | 0 | 0 | 23
38910.4956 | 0 | 0 | 23
38910.4963 | 0 | 0 | 23
38910.497 | 2156 | 1 | 23
38910.4976 | 2541 | 0 | 23
38910.4983 | 2189 | 0 | 23
38910.499 | 2086 | 1 | 23
38910.4997 | 2030 | 0 | 23
38910.5004 | 2130 | 0 | 23
38910.501 | 2514 | 0 | 23
38910.4888 | 0 | 0 | 24
38910.4895 | 0 | 0 | 24
38910.4902 | 0 | 0 | 24
38910.4908 | 0 | 0 | 24
38910.4915 | 0 | 0 | 24
38910.4922 | 0 | 0 | 24
38910.4929 | 0 | 0 | 24
38910.4936 | 0 | 0 | 24
38910.4942 | 0 | 0 | 24
38910.4949 | 0 | 0 | 24
38910.4956 | 0 | 0 | 24
38910.4963 | 237 | 114 | 24
38910.497 | 2307 | 0 | 24
38910.4977 | 2141 | 0 | 24
38910.499 | 2154 | 0 | 24
38910.4997 | 1936 | 0 | 24
38910.5004 | 1985 | 0 | 24
38910.5011 | 2491 | 0 | 24
38910.4888 | 0 | 0 | 25
38910.4895 | 0 | 0 | 25
38910.4902 | 0 | 0 | 25
38910.4909 | 0 | 0 | 25
38910.4915 | 0 | 0 | 25
38910.4922 | 0 | 0 | 25
38910.4929 | 0 | 0 | 25
38910.4936 | 0 | 0 | 25
38910.4943 | 0 | 0 | 25
38910.4949 | 0 | 0 | 25
38910.4956 | 0 | 0 | 25
38910.4963 | 960 | 1136 | 25
38910.497 | 2339 | 0 | 25
38910.4977 | 2096 | 0 | 25
38910.4983 | 2401 | 0 | 25
38910.499 | 1960 | 0 | 25
38910.4997 | 2405 | 0 | 25
38910.5004 | 2050 | 0 | 25
38910.5011 | 1990 | 0 | 25
38910.4888 | 0 | 0 | 26
38910.4895 | 0 | 0 | 26
38910.4902 | 0 | 0 | 26
38910.4909 | 0 | 0 | 26
38910.4916 | 0 | 0 | 26
38910.4922 | 0 | 0 | 26
38910.4929 | 0 | 0 | 26
38910.4936 | 0 | 0 | 26
38910.4943 | 0 | 0 | 26
38910.495 | 0 | 0 | 26
38910.4956 | 0 | 0 | 26
38910.4963 | 1040 | 1162 | 26
38910.497 | 2168 | 0 | 26
38910.4977 | 2142 | 0 | 26
38910.4984 | 1972 | 0 | 26
38910.499 | 2313 | 0 | 26
38910.4997 | 2357 | 0 | 26
38910.5004 | 2053 | 0 | 26
38910.5011 | 1999 | 0 | 26
38910.4889 | 0 | 0 | 27
38910.4895 | 0 | 0 | 27
38910.4902 | 0 | 0 | 27
38910.4909 | 0 | 0 | 27
38910.4916 | 0 | 0 | 27
38910.4923 | 0 | 0 | 27
38910.4929 | 0 | 0 | 27
38910.4936 | 0 | 0 | 27
38910.4943 | 0 | 0 | 27
38910.495 | 0 | 0 | 27
38910.4957 | 0 | 0 | 27
38910.4963 | 1046 | 1012 | 27
38910.497 | 2292 | 56 | 27
38910.4977 | 2435 | 0 | 27
38910.4984 | 2153 | 0 | 27
38910.4991 | 2405 | 0 | 27
38910.4997 | 2106 | 0 | 27
38910.5004 | 2178 | 0 | 27
38910.5011 | 2343 | 0 | 27
38910.4889 | 0 | 0 | 28
38910.4895 | 0 | 0 | 28
38910.4902 | 0 | 0 | 28
38910.4909 | 0 | 0 | 28
38910.4916 | 0 | 0 | 28
38910.4923 | 0 | 0 | 28
38910.493 | 0 | 0 | 28
38910.4936 | 0 | 0 | 28
38910.4943 | 0 | 0 | 28
38910.495 | 0 | 0 | 28
38910.4957 | 0 | 0 | 28
38910.4964 | 1153 | 904 | 28
38910.497 | 2263 | 0 | 28
38910.4977 | 2195 | 0 | 28
38910.4984 | 2200 | 0 | 28
38910.4991 | 2538 | 0 | 28
38910.4998 | 2317 | 0 | 28
38910.5004 | 2221 | 0 | 28
38910.5011 | 2449 | 0 | 28
38910.4889 | 0 | 0 | 29
38910.4896 | 0 | 0 | 29
38910.4902 | 0 | 0 | 29
38910.4909 | 0 | 0 | 29
38910.4916 | 0 | 0 | 29
38910.4923 | 0 | 0 | 29
38910.493 | 0 | 0 | 29
38910.4936 | 0 | 0 | 29
38910.4943 | 0 | 0 | 29
38910.495 | 0 | 0 | 29
38910.4957 | 0 | 0 | 29
38910.4964 | 413 | 433 | 29
38910.497 | 2197 | 0 | 29
38910.4977 | 2509 | 0 | 29
38910.4984 | 2285 | 0 | 29
38910.4991 | 2232 | 0 | 29
38910.4998 | 2331 | 0 | 29
38910.5005 | 2470 | 0 | 29
38910.5011 | 2485 | 0 | 29
38910.4889 | 0 | 0 | 30
38910.4896 | 0 | 0 | 30
38910.4903 | 0 | 0 | 30
38910.4909 | 0 | 0 | 30
38910.4916 | 0 | 0 | 30
38910.4923 | 0 | 0 | 30
38910.493 | 0 | 0 | 30
38910.4937 | 0 | 0 | 30
38910.4944 | 0 | 0 | 30
38910.495 | 0 | 0 | 30
38910.4957 | 0 | 0 | 30
38910.4964 | 18 | 42 | 30
38910.4971 | 2171 | 0 | 30
38910.4977 | 1102 | 0 | 30
38910.4984 | 1761 | 2 | 30
38910.4991 | 2081 | 0 | 30
38910.4998 | 2564 | 0 | 30
38910.5005 | 2031 | 0 | 30
38910.5011 | 29 | 0 | 30
38910.4889 | 0 | 0 | 31
38910.4896 | 0 | 0 | 31
38910.4903 | 0 | 0 | 31
38910.491 | 0 | 0 | 31
38910.4916 | 0 | 0 | 31
38910.4923 | 0 | 0 | 31
38910.493 | 0 | 0 | 31
38910.4937 | 0 | 0 | 31
38910.4944 | 0 | 0 | 31
38910.495 | 0 | 0 | 31
38910.4957 | 0 | 0 | 31
38910.4964 | 2101 | 22 | 31
38910.4971 | 2557 | 0 | 31
38910.4978 | 2034 | 0 | 31
38910.4984 | 1928 | 0 | 31
38910.4991 | 1911 | 0 | 31
38910.4998 | 2091 | 0 | 31
38910.5005 | 2045 | 0 | 31
38910.5012 | 2053 | 0 | 31
38910.4889 | 0 | 0 | 32
38910.4896 | 0 | 0 | 32
38910.4903 | 0 | 0 | 32
38910.491 | 0 | 0 | 32
38910.4917 | 0 | 0 | 32
38910.4923 | 0 | 0 | 32
38910.493 | 0 | 0 | 32
38910.4937 | 0 | 0 | 32
38910.4944 | 0 | 0 | 32
38910.4951 | 0 | 0 | 32
38910.4957 | 0 | 0 | 32
38910.4964 | 31 | 13 | 32
38910.4971 | 2004 | 0 | 32
38910.4978 | 2378 | 0 | 32
38910.4985 | 1951 | 0 | 32
38910.4991 | 2086 | 0 | 32
38910.4998 | 2197 | 0 | 32
38910.5005 | 2080 | 1 | 32
38910.5012 | 2191 | 0 | 32
38910.4889 | 0 | 0 | 33
38910.4896 | 0 | 0 | 33
38910.4903 | 0 | 0 | 33
38910.491 | 0 | 0 | 33
38910.4917 | 0 | 0 | 33
38910.4923 | 0 | 0 | 33
38910.493 | 0 | 0 | 33
38910.4937 | 0 | 0 | 33
38910.4944 | 0 | 0 | 33
38910.4951 | 0 | 0 | 33
38910.4958 | 0 | 0 | 33
38910.4964 | 2564 | 8 | 33
38910.4971 | 1993 | 0 | 33
38910.4978 | 2356 | 0 | 33
38910.4985 | 2326 | 0 | 33
38910.4992 | 2277 | 0 | 33
38910.4998 | 2520 | 0 | 33
38910.5005 | 2456 | 1 | 33
38910.5012 | 2370 | 0 | 33
38910.489 | 0 | 0 | 34
38910.4896 | 0 | 0 | 34
38910.4903 | 0 | 0 | 34
38910.491 | 0 | 0 | 34
38910.4917 | 0 | 0 | 34
38910.4924 | 0 | 0 | 34
38910.493 | 0 | 0 | 34
38910.4937 | 0 | 0 | 34
38910.4944 | 0 | 0 | 34
38910.4951 | 0 | 0 | 34
38910.4958 | 0 | 0 | 34
38910.4964 | 1714 | 7 | 34
38910.4971 | 2460 | 0 | 34
38910.4978 | 1927 | 0 | 34
38910.4985 | 2291 | 0 | 34
38910.4992 | 2516 | 0 | 34
38910.4998 | 2408 | 0 | 34
38910.5005 | 2548 | 0 | 34
38910.5012 | 2321 | 0 | 34
38910.489 | 0 | 0 | 35
38910.4897 | 0 | 0 | 35
38910.4903 | 0 | 0 | 35
38910.491 | 0 | 0 | 35
38910.4917 | 0 | 0 | 35
38910.4924 | 0 | 0 | 35
38910.4931 | 0 | 0 | 35
38910.4938 | 0 | 0 | 35
38910.4944 | 0 | 0 | 35
38910.4951 | 0 | 0 | 35
38910.4958 | 0 | 0 | 35
38910.4965 | 2499 | 5 | 35
38910.4972 | 2202 | 0 | 35
38910.4978 | 2056 | 0 | 35
38910.4985 | 2407 | 0 | 35
38910.4992 | 1935 | 0 | 35
38910.4999 | 1960 | 0 | 35
38910.5006 | 1919 | 0 | 35
38910.5012 | 2057 | 0 | 35
38910.489 | 0 | 0 | 36
38910.4897 | 0 | 0 | 36
38910.4904 | 0 | 0 | 36
38910.491 | 0 | 0 | 36
38910.4917 | 0 | 0 | 36
38910.4924 | 0 | 0 | 36
38910.4931 | 0 | 0 | 36
38910.4938 | 0 | 0 | 36
38910.4944 | 0 | 0 | 36
38910.4951 | 0 | 0 | 36
38910.4958 | 0 | 0 | 36
38910.4965 | 2431 | 4 | 36
38910.4972 | 1965 | 0 | 36
38910.4978 | 2302 | 0 | 36
38910.4985 | 2237 | 4 | 36
38910.4992 | 2110 | 0 | 36
38910.4999 | 2127 | 0 | 36
38910.5006 | 1612 | 1 | 36
38910.5013 | 59 | 0 | 36
38910.489 | 0 | 0 | 37
38910.4897 | 0 | 0 | 37
38910.4904 | 0 | 0 | 37
38910.4911 | 0 | 0 | 37
38910.4917 | 0 | 0 | 37
38910.4924 | 0 | 0 | 37
38910.4931 | 0 | 0 | 37
38910.4938 | 0 | 0 | 37
38910.4945 | 0 | 0 | 37
38910.4951 | 0 | 0 | 37
38910.4958 | 0 | 0 | 37
38910.4965 | 2547 | 3 | 37
38910.4972 | 2203 | 0 | 37
38910.4979 | 2297 | 0 | 37
38910.4985 | 2116 | 0 | 37
38910.4992 | 2432 | 0 | 37
38910.4999 | 2144 | 0 | 37
38910.5006 | 2137 | 0 | 37
38910.5013 | 2103 | 0 | 37
38910.489 | 0 | 0 | 38
38910.4897 | 0 | 0 | 38
38910.4904 | 0 | 0 | 38
38910.4911 | 0 | 0 | 38
38910.4918 | 0 | 0 | 38
38910.4924 | 0 | 0 | 38
38910.4931 | 0 | 0 | 38
38910.4938 | 0 | 0 | 38
38910.4945 | 0 | 0 | 38
38910.4952 | 0 | 0 | 38
38910.4958 | 0 | 0 | 38
38910.4965 | 1895 | 3 | 38
38910.4972 | 2019 | 0 | 38
38910.4979 | 2294 | 0 | 38
38910.4986 | 1972 | 0 | 38
38910.4992 | 2318 | 0 | 38
38910.4999 | 2350 | 0 | 38
38910.5006 | 2373 | 0 | 38
38910.5013 | 2251 | 0 | 38
38910.4891 | 0 | 0 | 39
38910.4897 | 0 | 0 | 39
38910.4904 | 0 | 0 | 39
38910.4911 | 0 | 0 | 39
38910.4918 | 0 | 0 | 39
38910.4925 | 0 | 0 | 39
38910.4931 | 0 | 0 | 39
38910.4938 | 0 | 0 | 39
38910.4945 | 0 | 0 | 39
38910.4952 | 0 | 0 | 39
38910.4959 | 0 | 0 | 39
38910.4965 | 2006 | 79 | 39
38910.4972 | 2350 | 0 | 39
38910.4979 | 2244 | 0 | 39
38910.4986 | 2064 | 0 | 39
38910.4993 | 2554 | 0 | 39
38910.4999 | 1953 | 0 | 39
38910.5006 | 2357 | 0 | 39
38910.5013 | 2430 | 0 | 39
38910.4891 | 0 | 0 | 40
38910.4897 | 0 | 0 | 40
38910.4904 | 0 | 0 | 40
38910.4911 | 0 | 0 | 40
38910.4918 | 0 | 0 | 40
38910.4925 | 0 | 0 | 40
38910.4931 | 0 | 0 | 40
38910.4938 | 0 | 0 | 40
38910.4945 | 0 | 0 | 40
38910.4952 | 0 | 0 | 40
38910.4959 | 0 | 0 | 40
38910.4966 | 2346 | 2 | 40
38910.4972 | 2256 | 0 | 40
38910.4979 | 2219 | 0 | 40
38910.4986 | 1688 | 0 | 40
38910.4993 | 2560 | 0 | 40
38910.5 | 1936 | 0 | 40
38910.5006 | 28 | 0 | 40
38910.5013 | 59 | 0 | 40
38910.4891 | 0 | 0 | 41
38910.4898 | 0 | 0 | 41
38910.4904 | 0 | 0 | 41
38910.4911 | 0 | 0 | 41
38910.4918 | 0 | 0 | 41
38910.4925 | 0 | 0 | 41
38910.4932 | 0 | 0 | 41
38910.4938 | 0 | 0 | 41
38910.4945 | 0 | 0 | 41
38910.4952 | 0 | 0 | 41
38910.4959 | 0 | 0 | 41
38910.4966 | 2323 | 2 | 41
38910.4972 | 2242 | 0 | 41
38910.4979 | 2055 | 0 | 41
38910.4986 | 1976 | 0 | 41
38910.4993 | 2149 | 0 | 41
38910.5 | 1930 | 0 | 41
38910.5006 | 2537 | 0 | 41
38910.5013 | 2001 | 0 | 41
38910.4891 | 0 | 0 | 42
38910.4898 | 0 | 0 | 42
38910.4905 | 0 | 0 | 42
38910.4911 | 0 | 0 | 42
38910.4918 | 0 | 0 | 42
38910.4925 | 0 | 0 | 42
38910.4932 | 0 | 0 | 42
38910.4939 | 0 | 0 | 42
38910.4945 | 0 | 0 | 42
38910.4952 | 0 | 0 | 42
38910.4959 | 0 | 0 | 42
38910.4966 | 2359 | 1 | 42
38910.4973 | 1681 | 0 | 42
38910.4979 | 1717 | 0 | 42
38910.4986 | 1722 | 0 | 42
38910.4993 | 2002 | 0 | 42
38910.5 | 2143 | 0 | 42
38910.5007 | 32 | 0 | 42
38910.5013 | 60 | 0 | 42