## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 35
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, mixture of XLPE (3) & PE (3) insulated control cables (Items 10 & 15). Cable specimens present: Six lengths of cable were monitored for electrical performance, 3 each of XLPE and PE, A seventh length of cable (PE cable Item #15) was monitored for temperature response, No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 186 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
186 | 0 | Initated Penlight Heating
692-695 | 506-509 | Conductors E9 & E10 both short to ground at less than 100 ohms (2 & 34) | Thermoplastic Cable E shorts to ground prior to any interaction with other cables
1598-1604 | 1412-1418 | Conductors D7 & D8 both short to ground at less than 1000 ohms (478 & 651) | Thermoset Cable D shorts to ground
1611 | 1425 | Cable bundle ignites into flame
1664 | 1478 | Conductor A1 shorts to A2 at less than 100 ohms (13) | Thermoset Cable A is shorted internally
1700 | 1514 | Power to Penlight is shutoff
1759-1788 | 1573-1602 | The existing ground faults on conductors D7 & D8 degrade to less than 100 ohms (35 & 21)
1821-1824 | 1635-1638 | Conductors F11 & F12 both short to ground at less than 100 ohms (3 & <1) | Thermoset Cable F shorts to ground
1905-1920 | 1719-1734 | Conductors B3 & B4 both short to ground at less than 100 ohms (<1 & 36) | Thermoplastic Cable B shorts to ground
1911-1914 | 1725-1728 | Conductor B3 shorts to Conductors C5 & C6 at less than 100 ohms (5 & <1) | Interaction between two thermoplastic cables
1933-1936 | 1747-1750 | Conductor B4 shorts to Conductors C5 & C6 (188 & 82) | Interaction between two thermoplastic cables
1935-1943 | 1749-1757 | Conductors C5 & C6 short to gound at less than 1000 ohms (663 & 518) | Thermoplastic Cable C shorts to ground
2039-2062 | 1863-1876 | Conductors A1 & A2 short to ground at less than 1000 ohms (782 & 710)
2224-2246 | 2038-2060 | The existing ground shorts on Conductors A1 & A2 degrade to less than 100 ohms (87 & 75) | All conductors have shorted to external ground.
Additional Observations
Observation 1 | The progression of failure modes for the cable bundle was by shorting to ground of the three cables on the bottom, followed by shorting of the cables in the middle row and finally the top cable shorted to ground.
Observation 2 | It took 506 s (8.4 min.) from the start of Penlight heating for the first short to ground to occur, and it took 1425 s (23.8 min.) for the cable bundle to ignite.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A, D, F = XLPE Cable Item #10
B, C, E = PE Cable Item #15
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 35 |  |  | 2006-08-14 | 12:49
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-185 | 211201.9994 | -182 | 240637.9994 | -179.5 | 247537.9994 | -176.5 | 211201.9994 | -173.5 | 211201.9994 | -154 | 255737.9994 | -151.5 | 211201.9994 | -148.5 | 211201.9994 | -145.5 | 211201.9994 | -126 | 228237.9994 | -123.5 | 211201.9994 | -120.5 | 256137.9994 | -117.5 | 251237.9994 | -115 | 255037.9994 | -112 | 259737.9994 | -109.5 | 259237.9994 | -101 | 257137.9994 | -98 | 241637.9994 | -95.5 | 249037.9994 | -92.5 | 249937.9994 | -89.5 | 258437.9994 | -87 | 258537.9994 | -78.5 | 211201.9994 | -70 | 262637.9994 | -67.5 | 259737.9994 | -64.5 | 251737.9994 | -61.5 | 231737.9994 | -53.5 | 257237.9994 | -50.5 | 253537.9994 | -47.5 | 251437.9994 | -45 | 243137.9994 | -42 | 221737.9994 | -39.5 | 259037.9994 | -36.5 | 262337.9994 | -28 | 259337.9994 | -25.5 | 262637.9994 | -17 | 259837.9994 | -14 | 255537.9994 | -11.5 | 262137.9994 | -8.5 | 253137.9994 | -5.5 | 260637.9994 | -3 | 250737.9994 | -182 | 211201.9994 | -176.5 | 211201.9994 | -123.5 | 211201.9994 | -117.5 | 249037.9994 | -112 | 258437.9994 | -70 | 253537.9994 | -64.5 | 231737.9994 | -39.5 | 259037.9994 | -14 | 253137.9994
1.0338e-07 | 211201.9994 | 2.5 | 240637.9994 | 5.5 | 247537.9994 | 8.5 | 211201.9994 | 11 | 211201.9994 | 30.5 | 255737.9994 | 33.5 | 211201.9994 | 36.5 | 211201.9994 | 39 | 211201.9994 | 58.5 | 228237.9994 | 61.5 | 211201.9994 | 64.5 | 256137.9994 | 67 | 251237.9994 | 70 | 255037.9994 | 72.5 | 259737.9994 | 75.5 | 259237.9994 | 84 | 257137.9994 | 86.5 | 241637.9994 | 89.5 | 249037.9994 | 92.5 | 249937.9994 | 95 | 258437.9994 | 98 | 258537.9994 | 106 | 211201.9994 | 114.5 | 262637.9994 | 117.5 | 259737.9994 | 120.5 | 251737.9994 | 123 | 231737.9994 | 131.5 | 257237.9994 | 134.5 | 253537.9994 | 137 | 251437.9994 | 140 | 243137.9994 | 142.5 | 221737.9994 | 145.5 | 259037.9994 | 148 | 262337.9994 | 156.5 | 259337.9994 | 159.5 | 262637.9994 | 168 | 259837.9994 | 170.5 | 255537.9994 | 173.5 | 262137.9994 | 176.5 | 253137.9994 | 179 | 260637.9994 | 182 | 250737.9994 | 2.5 | 211201.9994 | 8.5 | 211201.9994 | 61.5 | 211201.9994 | 67 | 249037.9994 | 72.5 | 258437.9994 | 114.5 | 253537.9994 | 120.5 | 231737.9994 | 145.5 | 259037.9994 | 170.5 | 253137.9994
184.5 | 211201.9994 | 187.5 | 240637.9994 | 190 | 247537.9994 | 193 | 211201.9994 | 196 | 211201.9994 | 215.5 | 255737.9994 | 218 | 211201.9994 | 221 | 211201.9994 | 223.5 | 211201.9994 | 243.5 | 228237.9994 | 246.5 | 211201.9994 | 249 | 256137.9994 | 251.5 | 251237.9994 | 254.5 | 255037.9994 | 257.5 | 129818.9988 | 260 | 259237.9994 | 268.5 | 257137.9994 | 271.5 | 241637.9994 | 274.5 | 249037.9994 | 277 | 249937.9994 | 280 | 258437.9994 | 282.5 | 258537.9994 | 291 | 211201.9994 | 299.5 | 262637.9994 | 302 | 259737.9994 | 305 | 251737.9994 | 308 | 231737.9994 | 316.5 | 257237.9994 | 319 | 253537.9994 | 321.5 | 251437.9994 | 324.5 | 243137.9994 | 327.5 | 221737.9994 | 330.5 | 259037.9994 | 333 | 262337.9994 | 341.5 | 259337.9994 | 344.5 | 262637.9994 | 352.5 | 259837.9994 | 355.5 | 255537.9994 | 358.5 | 262137.9994 | 361 | 253137.9994 | 363.5 | 260637.9994 | 366.5 | 250737.9994 | 187.5 | 211201.9994 | 193 | 211201.9994 | 246.5 | 211201.9994 | 251.5 | 249037.9994 | 257.5 | 129818.9988 | 299.5 | 253537.9994 | 305 | 231737.9994 | 330.5 | 259037.9994 | 355.5 | 253137.9994
369.5 | 211201.9994 | 372 | 240637.9994 | 375 | 247537.9994 | 377.5 | 211201.9994 | 380.5 | 211201.9994 | 400 | 255737.9994 | 403 | 211201.9994 | 405.5 | 211201.9994 | 408.5 | 211201.9994 | 428.5 | 228237.9994 | 431 | 211201.9994 | 434 | 256137.9994 | 436.5 | 251237.9994 | 439.5 | 255037.9994 | 442 | 259737.9994 | 445 | 64734.4976 | 453.5 | 128518.9988 | 456 | 120768.9988 | 459 | 124468.9988 | 461.5 | 249937.9994 | 464.5 | 258437.9994 | 467.5 | 64559.4976 | 475.5 | 211201.9994 | 484.5 | 262637.9994 | 487 | 86512.6648 | 490 | 251038.5956 | 492.5 | 115818.9988 | 501 | 128568.9988 | 503.5 | 63309.4976 | 506.5 | 62784.4976 | 509.5 | 121518.9988 | 512 | 110818.9988 | 515 | 129468.9988 | 517.5 | 65509.4976 | 526 | 129618.9988 | 529 | 52447.5969 | 537.5 | 14.6762 | 540 | 22.1125 | 543 | 9.9639 | 545.5 | 63209.4976 | 548.5 | 86812.6648 | 551.5 | 125318.9988 | 372 | 211201.9994 | 377.5 | 211201.9994 | 431 | 120768.9988 | 436.5 | 124468.9988 | 442 | 64559.4976 | 484.5 | 63309.4976 | 490 | 62784.4976 | 515 | 52447.5969 | 540 | 9.9639
554 | 105550.9988 | 557 | 80145.9982 | 559.5 | 123718.9988 | 562.5 | 105550.9988 | 565.5 | 105550.9988 | 585 | 127818.9988 | 587.5 | 105550.9988 | 590.5 | 105550.9988 | 593.5 | 105550.9988 | 613 | 114068.9988 | 615.5 | 211201.9994 | 618.5 | 256137.9994 | 621.5 | 251237.9994 | 624 | 255037.9994 | 627 | 129818.9988 | 629.5 | 64734.4976 | 638.5 | 128518.9988 | 641 | 120768.9988 | 643.5 | 124468.9988 | 646.5 | 249937.9994 | 649.5 | 258437.9994 | 652 | 64559.4976 | 660.5 | 211201.9994 | 669 | 131268.9988 | 671.5 | 86512.6648 | 674.5 | 125818.9988 | 677.5 | 115818.9988 | 685.5 | 257237.9994 | 688.5 | 63309.4976 | 691.5 | 125668.9988 | 694 | 243137.9994 | 697 | 221737.9994 | 699.5 | 129468.9988 | 702.5 | 262337.9994 | 711 | 259337.9994 | 713.5 | 131268.9988 | 722 | 36.2329 | 725 | 97.2273 | 727.5 | 37362.5672 | 730.5 | 1565.9467 | 733.5 | 130268.9988 | 736 | 125318.9988 | 557 | 80145.9982 | 562.5 | 105550.9988 | 615.5 | 120768.9988 | 621.5 | 124468.9988 | 627 | 64559.4976 | 669 | 63309.4976 | 674.5 | 115818.9988 | 699.5 | 129468.9988 | 725 | 97.2273
739 | 105550.9988 | 741.5 | 240637.9994 | 744.5 | 123718.9988 | 747.5 | 211201.9994 | 750 | 211201.9994 | 769.5 | 127818.9988 | 772.5 | 211201.9994 | 775.5 | 211201.9994 | 778 | 211201.9994 | 797.5 | 114068.9988 | 800.5 | 105550.9988 | 803.5 | 128018.9988 | 806 | 125568.9988 | 809 | 127468.9988 | 811.5 | 259737.9994 | 814.5 | 64734.4976 | 823 | 128518.9988 | 825.5 | 120768.9988 | 828.5 | 124468.9988 | 831.5 | 124918.9988 | 834 | 258437.9994 | 837 | 64559.4976 | 845.5 | 105550.9988 | 853.5 | 131268.9988 | 856.5 | 64859.4976 | 859.5 | 83845.9982 | 862 | 77179.3315 | 870.5 | 128568.9988 | 873.5 | 63309.4976 | 876 | 62784.4976 | 879 | 80979.3315 | 881.5 | 110818.9988 | 884.5 | 129468.9988 | 887.5 | 65509.4976 | 895.5 | 129618.9988 | 898.5 | 65584.4976 | 907 | 0.50567 | 909.5 | 12.1411 | 912.5 | 40675.861 | 915.5 | 22.6455 | 918 | 0.94962 | 921 | 62609.4976 | 741.5 | 123718.9988 | 747.5 | 211201.9994 | 800.5 | 105550.9988 | 806 | 124468.9988 | 811.5 | 64559.4976 | 853.5 | 63309.4976 | 859.5 | 62784.4976 | 884.5 | 65509.4976 | 909.5 | 0.94962
923.5 | 70333.9982 | 926.5 | 80145.9982 | 929.5 | 82445.9982 | 932 | 70333.9982 | 935 | 105550.9988 | 954.5 | 127818.9988 | 957.5 | 105550.9988 | 960 | 105550.9988 | 963 | 105550.9988 | 982.5 | 76012.6648 | 985.5 | 105550.9988 | 988 | 128018.9988 | 991 | 125568.9988 | 993.5 | 127468.9988 | 996.5 | 129818.9988 | 999.5 | 64734.4976 | 1007.5 | 128518.9988 | 1010.5 | 120768.9988 | 1013.5 | 124468.9988 | 1016 | 124918.9988 | 1019 | 258437.9994 | 1021.5 | 64559.4976 | 1030 | 105550.9988 | 1038.5 | 131268.9988 | 1041.5 | 64859.4976 | 1044 | 62859.4976 | 1047 | 115818.9988 | 1055.5 | 128568.9988 | 1058 | 63309.4976 | 1061 | 62784.4976 | 1063.5 | 80979.3315 | 1066.5 | 110818.9988 | 1069.5 | 129468.9988 | 1072 | 65509.4976 | 1080.5 | 129618.9988 | 1083.5 | 65584.4976 | 1091.5 | 728.1595 | 1094.5 | 16.4807 | 1097.5 | 18.2407 | 1099 | 14.8333 | 1103 | 24.5125 | 1105.5 | 62609.4976 | 926.5 | 80145.9982 | 932 | 70333.9982 | 985.5 | 105550.9988 | 991 | 124468.9988 | 996.5 | 64559.4976 | 1038.5 | 63309.4976 | 1044 | 62784.4976 | 1069.5 | 65509.4976 | 1094.5 | 14.8333
1108.5 | 52725.4976 | 1111.5 | 60084.4976 | 1114 | 123718.9988 | 1117 | 70333.9982 | 1119.5 | 105550.9988 | 1139.5 | 85179.3315 | 1142 | 105550.9988 | 1145 | 105550.9988 | 1147.5 | 105550.9988 | 1167.5 | 114068.9988 | 1170 | 105550.9988 | 1173 | 128018.9988 | 1175.5 | 125568.9988 | 1178.5 | 255037.9994 | 1181.5 | 129818.9988 | 1184 | 64734.4976 | 1192.5 | 128518.9988 | 1195.5 | 120768.9988 | 1198 | 249037.9994 | 1201 | 124918.9988 | 1203.5 | 129168.9988 | 1206.5 | 64559.4976 | 1215 | 105550.9988 | 1223.5 | 131268.9988 | 1226 | 86512.6648 | 1229 | 62859.4976 | 1231.5 | 77179.3315 | 1240 | 128568.9988 | 1243 | 84445.9982 | 1245.5 | 62784.4976 | 1248.5 | 121518.9988 | 1251.5 | 55060.0409 | 1254 | 129468.9988 | 1257 | 65509.4976 | 1265.5 | 129618.9988 | 1268 | 87479.3315 | 1276.5 | 16.1622 | 1279.5 | 0.13566 | 1282 | 26.7956 | 1285 | 0.88499 | 1287.5 | 15.7208 | 1290.5 | 62609.4976 | 1111.5 | 60084.4976 | 1117 | 70333.9982 | 1170 | 105550.9988 | 1175.5 | 124918.9988 | 1181.5 | 64559.4976 | 1223.5 | 84445.9982 | 1229 | 62784.4976 | 1254 | 65509.4976 | 1279.5 | 0.13566
1293 | 9364.1766 | 1296 | 80145.9982 | 1299 | 82445.9982 | 1301.5 | 105550.9988 | 1304.5 | 105550.9988 | 1324 | 127818.9988 | 1327 | 105550.9988 | 1329.5 | 105550.9988 | 1332.5 | 105550.9988 | 1352 | 114068.9988 | 1355 | 105550.9988 | 1357.5 | 128018.9988 | 1360.5 | 125568.9988 | 1363.5 | 127468.9988 | 1366 | 129818.9988 | 1368.5 | 64734.4976 | 1377.5 | 128518.9988 | 1380 | 120768.9988 | 1383 | 124468.9988 | 1385.5 | 124918.9988 | 1388.5 | 129168.9988 | 1391 | 64559.4976 | 1399.5 | 105550.9988 | 1408 | 131268.9988 | 1411 | 86512.6648 | 1413.5 | 62859.4976 | 1416.5 | 115818.9988 | 1425 | 128568.9988 | 1427.5 | 84445.9982 | 1430.5 | 62784.4976 | 1433.5 | 80979.3315 | 1436 | 18.2589 | 1439 | 4330.0519 | 1441.5 | 828.0185 | 1450 | 53957.7262 | 1453 | 65584.4976 | 1461.5 | 13.9469 | 1464 | 16.0431 | 1467 | 0.96242 | 1469.5 | 0.68169 | 1472.5 | 3.4077 | 1475.5 | 1499.8223 | 1296 | 80145.9982 | 1301.5 | 105550.9988 | 1355 | 105550.9988 | 1360.5 | 124468.9988 | 1366 | 64559.4976 | 1408 | 84445.9982 | 1413.5 | 62784.4976 | 1439 | 828.0185 | 1464 | 0.68169
1478 | 13.3841 | 1480.5 | 26593.2539 | 1483.5 | 123469.1615 | 1486.5 | 105301.213 | 1489 | 210702.3786 | 1509 | 85179.3315 | 1511.5 | 105550.9988 | 1514.5 | 105550.9988 | 1517.5 | 105550.9988 | 1537 | 114068.9988 | 1539.5 | 105550.9988 | 1542.5 | 128018.9988 | 1545 | 125568.9988 | 1548 | 127468.9988 | 1551 | 129818.9988 | 1553.5 | 64734.4976 | 1562 | 64209.4976 | 1565 | 120768.9988 | 1567.5 | 124468.9988 | 1570.5 | 124918.9988 | 1573.5 | 129168.9988 | 1576 | 64559.4976 | 1584.5 | 52725.4976 | 1592.5 | 131268.9988 | 1595.5 | 64859.4976 | 1598.5 | 62859.4976 | 1601 | 57859.4976 | 1609.5 | 64234.4976 | 1612.5 | 63309.4976 | 1615 | 62784.4976 | 1618 | 60709.4976 | 1620.5 | 13.7338 | 1623.5 | 16975.7868 | 1626.5 | 34.1633 | 1634.5 | 19.869 | 1637.5 | 21.0061 | 1646 | 25.2359 | 1649 | 22.6562 | 1651.5 | 2.5662 | 1654.5 | 2.8603 | 1657.5 | 17.2832 | 1660 | 1.0145 | 1480.5 | 26593.2539 | 1486.5 | 105301.213 | 1539.5 | 64209.4976 | 1545 | 124468.9988 | 1551 | 64559.4976 | 1592.5 | 63309.4976 | 1598.5 | 57859.4976 | 1623.5 | 19.869 | 1649 | 2.5662
1663 | 22.3104 | 1665.5 | 29137.1648 | 1668.5 | 66772.7445 | 1671 | 202886.8549 | 1674 | 206807.963 | 1693.5 | 183530.7939 | 1696.5 | 13539.5591 | 1699 | 3007.3408 | 1702 | 1299.2588 | 1721.5 | 2208.0854 | 1724.5 | 4.967 | 1727.5 | 0.91097 | 1730 | 0.86843 | 1733 | 0.90147 | 1735.5 | 4.1669 | 1738.5 | 26.4499 | 1747 | 188.4881 | 1749.5 | 81.9119 | 1752.5 | 1831.2236 | 1755.5 | 35.1402 | 1758 | 7504.0381 | 1760.5 | 1305.529 | 1769 | 140.9932 | 1777.5 | 87479.3315 | 1780.5 | 86512.6648 | 1783 | 9973.5047 | 1786 | 1969.9138 | 1794.5 | 51367.5969 | 1797 | 63309.4976 | 1800 | 62784.4976 | 1802.5 | 60709.4976 | 1805.5 | 17.9001 | 1808.5 | 3074.8938 | 1811 | 51.3517 | 1819.5 | 34.6654 | 1822.5 | 41.9041 | 1830.5 | 28.1603 | 1833.5 | 6.4634 | 1836.5 | 26.9853 | 1839.5 | 16.1411 | 1842 | 14.3538 | 1845 | 27.7781 | 1665.5 | 13539.5591 | 1671 | 1299.2588 | 1724.5 | 0.91097 | 1730 | 0.86843 | 1735.5 | 4.1669 | 1777.5 | 51367.5969 | 1783 | 1969.9138 | 1808.5 | 34.6654 | 1833.5 | 6.4634
1847.5 | 23.4642 | 1850.5 | 25089.4249 | 1853 | 17800.7653 | 1856 | 196275.4948 | 1858.5 | 2172.0077 | 1878.5 | 1268.0035 | 1881 | 873.6095 | 1884 | 709.4269 | 1886.5 | 887.2619 | 1906.5 | 67.5048 | 1909 | 0.27239 | 1912 | 22.1613 | 1914.5 | 13.0066 | 1917.5 | 0.82078 | 1920.5 | 24.2006 | 1923 | 30.239 | 1931.5 | 25.9852 | 1934.5 | 14.2205 | 1937.5 | 21.611 | 1940 | 7.7889 | 1942.5 | 16.4449 | 1945.5 | 29.5498 | 1954 | 2674.0779 | 1962.5 | 761.2499 | 1965 | 837.8742 | 1968 | 1116.4823 | 1970.5 | 710.4478 | 1979 | 809.1488 | 1982 | 279.8597 | 1984.5 | 279.5626 | 1987.5 | 140.6922 | 1990.5 | 0.36943 | 1993 | 29.2036 | 1996 | 21.6766 | 2004.5 | 7.9738 | 2007 | 11.734 | 2015.5 | 0.70539 | 2018.5 | 0.90579 | 2021 | 4.7922 | 2024 | 25.462 | 2026.5 | 9.5655 | 2029.5 | 15.0825 | 1850.5 | 873.6095 | 1856 | 709.4269 | 1909 | 0.27239 | 1914.5 | 0.82078 | 1920.5 | 16.4449 | 1962.5 | 279.8597 | 1968 | 140.6922 | 1993 | 7.9738 | 2018.5 | 0.90579
2032.5 | 13.1849 | 2035 | 5748.0385 | 2038 | 2631.4249 | 2040.5 | 170776.7575 | 2043.5 | 175777.3282 | 2063 | 3453.2616 | 2066 | 74.6187 | 2068.5 | 649.1257 | 2071.5 | 599.4911 | 2091 | 8.0826 | 2094 | 2.9542 | 2096.5 | 0.5545 | 2099.5 | 13.6949 | 2102.5 | 12.2766 | 2105 | 2.5357 | 2108 | 20.8022 | 2116.5 | 17.4949 | 2119 | 198.317 | 2122 | 69.2825 | 2124.5 | 614.1806 | 2127.5 | 5462.0424 | 2130.5 | 2881.6041 | 2138.5 | 82.0609 | 2147 | 43704.8993 | 2150 | 1218.8544 | 2152.5 | 1184.7681 | 2155.5 | 993.446 | 2164 | 1108.0296 | 2166.5 | 993.1256 | 2169.5 | 776.2638 | 2172.5 | 655.2009 | 2175 | 8.2251 | 2178 | 995.9445 | 2180.5 | 13511.6517 | 2189 | 62.4046 | 2192 | 91.6487 | 2200.5 | 3.8599 | 2203 | 15.4466 | 2206 | 2.7342 | 2208.5 | 10.8233 | 2211.5 | 24.4513 | 2214.5 | 87.7118 | 2035 | 74.6187 | 2040.5 | 599.4911 | 2094 | 0.5545 | 2099.5 | 12.2766 | 2105 | 2.5357 | 2147 | 993.1256 | 2152.5 | 655.2009 | 2178 | 62.4046 | 2203 | 2.7342
2217 | 19.7713 | 2220 | 895.8157 | 2222.5 | 6993.903 | 2225.5 | 101667.7249 | 2228.5 | 822.5764 | 2248 | 1767.347 | 2250.5 | 1377.5491 | 2253.5 | 994.7112 | 2256.5 | 1029.8431 | 2276 | 11.0188 | 2278.5 | 1.9755 | 2281.5 | 13.9621 | 2284.5 | 6.683 | 2287 | 26.4124 | 2290 | 1.7382 | 2292.5 | 22.0342 | 2301 | 0.91959 | 2304 | 0.7836 | 2306.5 | 0.84917 | 2309.5 | 0.85706 | 2312.5 | 4.03 | 2315 | 23.8653 | 2323.5 | 48.4691 | 2332 | 1133.3817 | 2334.5 | 1119.7667 | 2337.5 | 1514.2509 | 2340.5 | 1209.7112 | 2348.5 | 1337.5332 | 2351.5 | 997.859 | 2354.5 | 926.5361 | 2357 | 976.1364 | 2360 | 8.1523 | 2362.5 | 4132.0955 | 2365.5 | 12579.4696 | 2374 | 52.665 | 2376.5 | 126.1825 | 2385 | 16.6478 | 2388 | 2.0318 | 2390.5 | 15.4919 | 2393.5 | 24.6355 | 2396.5 | 26.6306 | 2399 | 68.2513 | 2220 | 895.8157 | 2225.5 | 822.5764 | 2278.5 | 0.7836 | 2284.5 | 0.84917 | 2290 | 1.7382 | 2332 | 997.859 | 2337.5 | 926.5361 | 2362.5 | 52.665 | 2388 | 2.0318
2402 | 3.0828 | 2404.5 | 241.0277 | 2407.5 | 1249.4385 | 2410.5 | 90896.2859 | 2413 | 184852.9621 | 2432.5 | 1898.6562 | 2435.5 | 1550.7187 | 2438.5 | 1006.1766 | 2441 | 3363.93 | 2460.5 | 8.2949 | 2463.5 | 0.070991 | 2466.5 | 15.4509 | 2469 | 13.4292 | 2472 | 14.4158 | 2474.5 | 11.6684 | 2477.5 | 16.7006 | 2486 | 7.2318 | 2488.5 | 6.7957 | 2491.5 | 6.0646 | 2494.5 | 13.5787 | 2497 | 11.1027 | 2500 | 17.3655 | 2508.5 | 17.5144 | 2516.5 | 7627.5675 | 2519.5 | 7542.2734 | 2522.5 | 6706.4098 | 2525 | 7627.915 | 2533.5 | 12766.8878 | 2536.5 | 13249.3568 | 2539 | 9574.5226 | 2542 | 9255.2918 | 2544.5 | 11.85 | 2547.5 | 218.7635 | 2550.5 | 7633.6028 | 2558.5 | 232.9929 | 2561.5 | 358.983 | 2570 | 14.7287 | 2572.5 | 11.4313 | 2575.5 | 21.933 | 2578.5 | 23.5706 | 2581 | 26.1888 | 2584 | 71.7116 | 2404.5 | 241.0277 | 2410.5 | 1006.1766 | 2463.5 | 0.070991 | 2469 | 6.0646 | 2474.5 | 11.1027 | 2516.5 | 7542.2734 | 2522.5 | 6706.4098 | 2547.5 | 218.7635 | 2572.5 | 11.4313

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 35 |  |  | 2006-08-14 | 12:49
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-179.3 | 211202 |  | -156.9 | 211202 | -128.8889 | 211202 | -113.3889 | 211202 | -99.0556 | 211202 | -90.2778 | 211202 | -66.2 | 221738 | -60.6 | 221738 | -48.3333 | 255538 | -45.2778 | 253138 | -27.5 | 63209.5 | -25.3 | 231738 | -179.3 | 211202 | -128.8889 | 211202 | -99.0556 | 63209.5 | -92.2694 | 211202 | -83.9722 | 211202 | -55.1028 | 221738 | -70.7361 | 211202 | -60.5333 | 63209.5 | -36.6028 | 63209.5 | -168.1 | 211202 | -121.1389 | 211202 | -94.6667 | 211202 | -63.4 | 221738 | -46.8056 | 253138 | -26.4 | 63209.5
5.5 | 211202 |  | 27.9 | 211202 | 55.8333 | 211202 | 71.4444 | 211202 | 85.7778 | 211202 | 94.4444 | 211202 | 118.5 | 221738 | 124.2 | 221738 | 136.3889 | 255538 | 139.6111 | 253138 | 157.3 | 126519 | 159.5 | 231738 | 5.5 | 211202 | 55.8333 | 211202 | 85.7778 | 126519 | 92.4944 | 211202 | 100.8194 | 211202 | 129.675 | 221738 | 114.0556 | 211202 | 124.2556 | 126519 | 148.2 | 126519 | 16.7 | 211202 | 63.6389 | 211202 | 90.1111 | 211202 | 121.35 | 221738 | 138 | 253138 | 158.4 | 126519
190.2 | 211202 |  | 212.5 | 211202 | 240.6111 | 129819 | 256.1667 | 211202 | 270.5 | 211202 | 279.1667 | 211202 | 303.4 | 221738 | 309 | 221738 | 321.3333 | 255538 | 324.2222 | 253138 | 341.9 | 250738 | 344.2 | 231738 | 190.2 | 129819 | 240.6111 | 129819 | 270.5 | 211202 | 277.2944 | 129819 | 285.5833 | 129819 | 314.4889 | 221738 | 298.8056 | 211202 | 308.9417 | 211202 | 332.9139 | 231738 | 201.35 | 211202 | 248.3889 | 129819 | 274.8333 | 211202 | 306.2 | 221738 | 322.7778 | 253138 | 343.05 | 231738
374.9 | 211202 |  | 397.3 | 211202 | 425.3889 | 64734.5 | 440.9444 | 64559.5 | 455.2222 | 83846 | 463.8889 | 62784.5 | 488 | 65509.5 | 493.6 | 52447.6 | 505.9444 | 1.7424 | 509 | 34.0753 | 526.7 | 63809.5 | 529 | 52347.6 | 374.9 | 62784.5 | 425.3889 | 1.7424 | 455.2222 | 1.7424 | 461.9833 | 52447.6 | 470.3194 | 1.7424 | 499.1361 | 1.7424 | 483.5139 | 1.7424 | 493.7028 | 52347.6 | 517.6611 | 1.7424 | 386.1 | 211202 | 433.1667 | 64559.5 | 459.5556 | 62784.5 | 490.8 | 52447.6 | 507.4722 | 1.7424 | 527.85 | 52347.6
559.7 | 80146 |  | 582.1 | 105551 | 610.1111 | 64734.5 | 625.6667 | 64559.5 | 640 | 86512.6667 | 648.7222 | 63309.5 | 672.8 | 125569 | 678.4 | 131269 | 690.6667 | 8.4471 | 693.7222 | 25.2326 | 711.5 | 84312.6667 | 713.7 | 121519 | 559.7 | 63309.5 | 610.1111 | 8.4471 | 640 | 8.4471 | 646.7444 | 64559.5 | 655.0417 | 8.4471 | 683.8972 | 8.4471 | 668.2778 | 8.4471 | 678.4806 | 63309.5 | 702.3972 | 8.4471 | 570.9 | 80146 | 617.8889 | 64559.5 | 644.3611 | 63309.5 | 675.6 | 125569 | 692.1944 | 8.4471 | 712.6 | 84312.6667
744.5 | 105551 |  | 766.9 | 105551 | 794.8333 | 64734.5 | 810.4444 | 64559.5 | 824.8333 | 64859.5 | 833.5 | 62784.5 | 857.6 | 65509.5 | 863.2 | 65584.5 | 875.3889 | 1.0645 | 878.6667 | 0.63219 | 896.3 | 62609.5 | 898.5 | 52047.6 | 744.5 | 62784.5 | 794.8333 | 0.63219 | 824.8333 | 0.63219 | 831.5194 | 64559.5 | 839.8333 | 0.63219 | 868.7139 | 0.63219 | 853.0972 | 0.63219 | 863.2833 | 52047.6 | 887.2139 | 0.63219 | 755.7 | 105551 | 802.6389 | 64559.5 | 829.1667 | 62784.5 | 860.4 | 65509.5 | 877.0278 | 0.63219 | 897.4 | 52047.6
929.3 | 70334 |  | 951.7 | 52725.5 | 979.7222 | 64734.5 | 995.2778 | 64559.5 | 1009.5556 | 62859.5 | 1018.2778 | 62784.5 | 1042.5 | 65509.5 | 1048 | 65584.5 | 1060.3333 | 0.62735 | 1063.2778 | 0.62735 | 1080.8 | 62609.5 | 1083.3 | 62609.5 | 929.3 | 52725.5 | 979.7222 | 0.62735 | 1009.5556 | 0.62735 | 1016.375 | 64559.5 | 1024.6528 | 0.62735 | 1053.5278 | 0.62735 | 1037.8611 | 0.62735 | 1047.9833 | 62609.5 | 1071.9278 | 0.62735 | 940.5 | 52725.5 | 987.5 | 64559.5 | 1013.9167 | 62784.5 | 1045.25 | 65509.5 | 1061.8056 | 0.62735 | 1082.05 | 62609.5
1114.1 | 52725.5 |  | 1136.5 | 70334 | 1164.5556 | 64734.5 | 1180.0556 | 64559.5 | 1194.3889 | 62859.5 | 1203.0556 | 62784.5 | 1227.2 | 55359.5 | 1232.9 | 55359.5 | 1245.1111 | 0.64059 | 1248.1667 | 0.63562 | 1265.9 | 51027.6 | 1268 | 65084.5 | 1114.1 | 52725.5 | 1164.5556 | 0.63562 | 1194.3889 | 0.63562 | 1201.1778 | 55359.5 | 1209.4722 | 0.63562 | 1238.3444 | 0.63562 | 1222.6806 | 0.63562 | 1232.8361 | 51027.6 | 1256.7944 | 0.63562 | 1125.3 | 52725.5 | 1172.3056 | 64559.5 | 1198.7222 | 62784.5 | 1230.05 | 55359.5 | 1246.6389 | 0.63562 | 1266.95 | 51027.6
1298.8 | 52867.2601 |  | 1321.2 | 42033.3454 | 1349.2222 | 64734.5 | 1364.8333 | 64559.5 | 1379.1111 | 62859.5 | 1387.8333 | 62784.5 | 1412 | 477.536 | 1417.6 | 650.9878 | 1429.8889 | 0.62855 | 1432.8889 | 0.63649 | 1450.6 | 26862.1681 | 1453 | 4440.6386 | 1298.8 | 42033.3454 | 1349.2222 | 0.62855 | 1379.1111 | 0.62855 | 1385.9139 | 477.536 | 1394.2083 | 0.62855 | 1423.0944 | 0.62855 | 1407.4306 | 0.62855 | 1417.6361 | 4440.6386 | 1441.5944 | 0.62855 | 1310 | 42033.3454 | 1357.0278 | 64559.5 | 1383.4722 | 62784.5 | 1414.8 | 477.536 | 1431.3889 | 0.62855 | 1451.8 | 4440.6386
1483.5 | 2714.9494 |  | 1506.1 | 24358.7779 | 1534 | 64734.5 | 1549.6111 | 64209.5 | 1563.8333 | 52725.5 | 1572.6111 | 60709.5 | 1596.6 | 35.3471 | 1602.2 | 21.1761 | 1614.5556 | 4.104 | 1617.7222 | 1.6414 | 1635.4 | 2.5084 | 1637.6 | 0.71156 | 1483.5 | 2714.9494 | 1534 | 1.6414 | 1563.8333 | 0.71156 | 1570.6028 | 21.1761 | 1578.9722 | 1.6414 | 1607.7694 | 1.6414 | 1592.1806 | 1.6414 | 1602.3611 | 0.71156 | 1626.3194 | 0.71156 | 1494.8 | 2714.9494 | 1541.8056 | 64209.5 | 1568.2222 | 52725.5 | 1599.4 | 21.1761 | 1616.1389 | 1.6414 | 1636.5 | 0.71156
1668.4 | 4595.2477 |  | 1690.8 | 1147.9076 | 1718.8333 | 0.64336 | 1734.3889 | 36.2605 | 1748.6111 | 663.3175 | 1757.3333 | 518.2558 | 1781.5 | 16.8565 | 1787.2 | 27.3054 | 1799.3333 | 5.5394 | 1802.4444 | 0.65 | 1820.2 | 3.9992 | 1822.4 | 5.8265 | 1668.4 | 0.64336 | 1718.8333 | 0.64336 | 1748.6111 | 0.65 | 1755.4806 | 0.64336 | 1763.75 | 0.64336 | 1792.6194 | 0.65 | 1776.9306 | 0.65 | 1787.1361 | 3.9992 | 1811.0944 | 0.65 | 1679.6 | 1147.9076 | 1726.6111 | 0.64336 | 1752.9722 | 518.2558 | 1784.35 | 16.8565 | 1800.8889 | 0.65 | 1821.3 | 3.9992
1853.1 | 782.3923 |  | 1875.5 | 709.5862 | 1903.5556 | 0.72562 | 1919.1111 | 9.1869 | 1933.3889 | 560.3188 | 1942.0556 | 141.3075 | 1966.3 | 0.56652 | 1971.9 | 0.25214 | 1984.1111 | 0.6376 | 1987.1667 | 2.854 | 2004.9 | 0.65546 | 2007 | 0.67798 | 1853.1 | 0.72562 | 1903.5556 | 0.25214 | 1933.3889 | 0.6376 | 1940.2167 | 0.25214 | 1948.4861 | 0.6376 | 1977.3694 | 0.25214 | 1961.6806 | 0.6376 | 1971.8361 | 0.65546 | 1995.7944 | 0.6376 | 1864.3 | 709.5862 | 1911.3333 | 0.72562 | 1937.7222 | 141.3075 | 1969.1 | 0.25214 | 1985.6389 | 0.6376 | 2005.95 | 0.65546
2037.9 | 86.615 |  | 2060.3 | 75.3544 | 2088.2778 | 0.68398 | 2103.8889 | 2.2884 | 2118.1111 | 643.8273 | 2126.8333 | 655.3975 | 2151 | 11.272 | 2156.6 | 36.7223 | 2168.8889 | 0.94864 | 2172 | 0.63415 | 2189.6 | 0.65468 | 2192 | 6.0479 | 2037.9 | 0.68398 | 2088.2778 | 0.63415 | 2118.1111 | 0.63415 | 2124.9417 | 0.68398 | 2133.2639 | 0.63415 | 2162.1222 | 0.63415 | 2146.4583 | 0.63415 | 2156.6361 | 0.65468 | 2180.6222 | 0.63415 | 2049.1 | 75.3544 | 2096.0833 | 0.68398 | 2122.4722 | 643.8273 | 2153.8 | 11.272 | 2170.4444 | 0.63415 | 2190.8 | 0.65468
2222.7 | 119.5609 |  | 2245.1 | 994.829 | 2273.1111 | 2.6198 | 2288.6111 | 0.64085 | 2302.9444 | 548.4869 | 2311.7222 | 602 | 2335.8 | 33.8328 | 2341.4 | 53.6955 | 2353.6667 | 0.63439 | 2356.7222 | 1.8965 | 2374.5 | 78.3555 | 2376.7 | 28.001 | 2222.7 | 0.64085 | 2273.1111 | 0.63439 | 2302.9444 | 0.63439 | 2309.7306 | 0.64085 | 2318.0278 | 0.63439 | 2346.8972 | 0.63439 | 2331.2639 | 0.63439 | 2341.4667 | 28.001 | 2365.3972 | 0.63439 | 2233.9 | 119.5609 | 2280.8611 | 0.64085 | 2307.3333 | 548.4869 | 2338.6 | 33.8328 | 2355.1944 | 0.63439 | 2375.6 | 28.001
2407.5 | 185.6038 |  | 2429.9 | 241.5885 | 2457.8333 | 0.85429 | 2473.4444 | 0.90057 | 2487.8333 | 1404.6552 | 2496.5 | 1806.2609 | 2520.6 | 110.1488 | 2526.2 | 117.6945 | 2538.3889 | 0.63538 | 2541.6667 | 0.63439 | 2559.3 | 53.2918 | 2561.5 | 36.6969 | 2407.5 | 0.85429 | 2457.8333 | 0.63439 | 2487.8333 | 0.63439 | 2494.5194 | 0.85429 | 2502.8333 | 0.63439 | 2531.7139 | 0.63439 | 2516.0972 | 0.63439 | 2526.2833 | 36.6969 | 2550.2139 | 0.63439 | 2418.7 | 185.6038 | 2465.6389 | 0.85429 | 2492.1667 | 1404.6552 | 2523.4 | 110.1488 | 2540.0278 | 0.63439 | 2560.4 | 36.6969
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0

## F11-F12
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 153.1368 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38943.5343 | 1 | 0 | 38943.5343 | 1 | 0 |  | -3 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38943.5364 | 1 | 0 | 38943.5364 | 1 | 0 |  | 182 | 368 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38943.5385 | 1 | 0 | 38943.5386 | 1 | 0 |  | 366.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38943.5407 | 2 | 0 | 38943.5407 | 2 | 0 |  | 551.5 | 737.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125319 | 125319 | 125318.9988
38943.5428 | 2 | 0 | 38943.5428 | 2 | 0 |  | 736 | 922 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125319 | 125319 | 125318.9988
38943.545 | 4 | 0 | 38943.545 | 4 | 0 |  | 921 | 1107 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 62609.5 | 62609.5 | 62609.4976
38943.5471 | 4 | 0 | 38943.5471 | 4 | 0 |  | 1105.5 | 1291.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 62609.5 | 62609.5 | 62609.4976
38943.5492 | 4 | 0 | 38943.5492 | 3 | 0 |  | 1290.5 | 1476.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62609.5 | 83512.6667 | 62609.4976
38943.5514 | 156 | 144 | 38943.5514 | 976 | 938 |  | 1475.5 | 1661.5 | 9.5238 | 8.7912 | 59.5849 | 57.265 | 0.095238 | 0.087912 | 0.59585 | 0.57265 | 0.007326 | 0.023199 | 26862.1681 | 4440.6386 | 1499.8223
38943.5535 | 2447 | 0 | 38943.5535 | 2342 | 0 |  | 1660 | 1846 | 149.3895 | 0 | 142.9792 | 0 | 1.4939 | 0 | 1.4298 | 0 | 1.4939 | 1.4298 | 2.5084 | 7.1042 | 1.0145
38943.5556 | 1945 | 0 | 38943.5557 | 2193 | 0 |  | 1845 | 2031 | 118.7424 | 0 | 133.8828 | 0 | 1.1874 | 0 | 1.3388 | 0 | 1.1874 | 1.3388 | 28.9656 | 14.3812 | 27.7781
38943.5578 | 2155 | 0 | 38943.5578 | 2407 | 1 |  | 2029.5 | 2215.5 | 131.5629 | 0 | 146.9475 | 0.06105 | 1.3156 | 0 | 1.4695 | 0.0006105 | 1.3156 | 1.4689 | 16.3981 | 4.2552 | 15.0825
38943.5599 | 2492 | 1 | 38943.5599 | 2374 | 1 |  | 2214.5 | 2400.5 | 152.1368 | 0.06105 | 144.9328 | 0.06105 | 1.5214 | 0.0006105 | 1.4493 | 0.0006105 | 1.5208 | 1.4487 | 0.66196 | 6.0479 | 87.7118
38943.5621 | 1034 | 845 | 38943.5621 | 1106 | 909 |  | 2399 | 2585 | 63.1258 | 51.5873 | 67.5214 | 55.4945 | 0.63126 | 0.51587 | 0.67521 | 0.55495 | 0.11538 | 0.12027 | 1318.1908 | 1095.2513 | 68.2513
38943.5642 | 972 | 883 | 38943.5642 | 1008 | 981 |  | 2584 | 2770 | 59.3407 | 53.9072 | 61.5385 | 59.8901 | 0.59341 | 0.53907 | 0.61538 | 0.5989 | 0.054335 | 0.016484 | 1311.7821 | 3139.9371 | 71.7116

## E10-F12
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 159.1807 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38943.5342 | 1 | 0 | 38943.5342 | 1 | 0 |  | -5.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
38943.5364 | 1 | 0 | 38943.5364 | 1 | 0 |  | 179 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
38943.5385 | 1 | 0 | 38943.5385 | 1 | 0 |  | 363.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
38943.5406 | 3 | 0 | 38943.5407 | 3 | 0 |  | 548.5 | 734.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 86812.6667 | 86812.6667 | 86812.6648
38943.5428 | 2 | 0 | 38943.5428 | 2 | 1 |  | 733.5 | 919.5 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 130269 | 260638 | 130268.9988
38943.5449 | 2591 | 0 | 38943.5449 | 5 | 0 |  | 918 | 1104 | 158.1807 | 0 | 0.30525 | 0 | 1.5818 | 0 | 0.0030525 | 0 | 1.5818 | 0.0030525 | 0.63219 | 52047.6 | 0.94962
38943.5471 | 2073 | 0 | 38943.5471 | 4 | 0 |  | 1103 | 1289 | 126.5568 | 0 | 0.2442 | 0 | 1.2656 | 0 | 0.002442 | 0 | 1.2656 | 0.002442 | 25.7781 | 65084.5 | 24.5125
38943.5492 | 2227 | 0 | 38943.5492 | 4 | 0 |  | 1287.5 | 1473.5 | 135.9585 | 0 | 0.2442 | 0 | 1.3596 | 0 | 0.002442 | 0 | 1.3596 | 0.002442 | 17.0804 | 65084.5 | 15.7208
38943.5513 | 2485 | 0 | 38943.5514 | 4 | 0 |  | 1472.5 | 1658.5 | 151.7094 | 0 | 0.2442 | 0 | 1.5171 | 0 | 0.002442 | 0 | 1.5171 | 0.002442 | 4.9247 | 65084.5 | 3.4077
38943.5535 | 2198 | 0 | 38943.5535 | 2088 | 0 |  | 1657.5 | 1843.5 | 134.188 | 0 | 127.4725 | 0 | 1.3419 | 0 | 1.2747 | 0 | 1.3419 | 1.2747 | 18.6251 | 24.8745 | 17.2832
38943.5556 | 2253 | 0 | 38943.5556 | 1984 | 0 |  | 1842 | 2028 | 137.5458 | 0 | 121.1233 | 0 | 1.3755 | 0 | 1.2112 | 0 | 1.3755 | 1.2112 | 15.7292 | 31.4204 | 14.3538
38943.5578 | 2349 | 0 | 38943.5578 | 2294 | 0 |  | 2026.5 | 2212.5 | 143.4066 | 0 | 140.0488 | 0 | 1.4341 | 0 | 1.4005 | 0 | 1.4341 | 1.4005 | 10.9996 | 13.6609 | 9.5655
38943.5599 | 2074 | 0 | 38943.5599 | 2216 | 0 |  | 2211.5 | 2397.5 | 126.6178 | 0 | 135.2869 | 0 | 1.2662 | 0 | 1.3529 | 0 | 1.2662 | 1.3529 | 25.7175 | 17.6616 | 24.4513
38943.562 | 2039 | 0 | 38943.562 | 2037 | 0 |  | 2396.5 | 2582.5 | 124.4811 | 0 | 124.359 | 0 | 1.2448 | 0 | 1.2436 | 0 | 1.2448 | 1.2436 | 27.8754 | 28.001 | 26.6306
38943.5642 | 2046 | 0 | 38943.5642 | 1570 | 0 |  | 2581 | 2767 | 124.9084 | 0 | 95.8486 | 0 | 1.2491 | 0 | 0.95849 | 0 | 1.2491 | 0.95849 | 27.4379 | 66.0752 | 26.1888

## E10-F11
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 154.602 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38943.5342 | 1 | 0 | 38943.5342 | 4 | 0 |  | -8.5 | 177.5 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 253138 | 63209.5 | 253137.9994
38943.5363 | 1 | 0 | 38943.5364 | 2 | 0 |  | 176.5 | 362.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253138 | 126519 | 253137.9994
38943.5385 | 1 | 0 | 38943.5385 | 1 | 0 |  | 361 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
38943.5406 | 4 | 0 | 38943.5406 | 3 | 0 |  | 545.5 | 731.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 63209.5 | 84312.6667 | 63209.4976
38943.5428 | 152 | 0 | 38943.5428 | 3 | 0 |  | 730.5 | 916.5 | 9.2796 | 0 | 0.18315 | 0 | 0.092796 | 0 | 0.0018315 | 0 | 0.092796 | 0.0018315 | 1566.0395 | 84312.6667 | 1565.9467
38943.5449 | 2044 | 0 | 38943.5449 | 4 | 0 |  | 915.5 | 1101.5 | 124.7863 | 0 | 0.2442 | 0 | 1.2479 | 0 | 0.002442 | 0 | 1.2479 | 0.002442 | 23.8933 | 63209.5 | 22.6455
38943.547 | 2180 | 0 |  | 4 | 0 |  | 1099 | 1285 | 133.0891 | 0 | 0.2442 | 0 | 1.3309 | 0 | 0.002442 | 0 | 1.3309 | 0.002442 | 16.1642 | 63209.5 | 14.8333
38943.5492 | 2516 | 0 | 38943.5492 | 4 | 0 |  | 1285 | 1471 | 153.602 | 0 | 0.2442 | 0 | 1.536 | 0 | 0.002442 | 0 | 1.536 | 0.002442 | 0.65103 | 63209.5 | 0.88499
38943.5513 | 2478 | 0 | 38943.5513 | 4 | 0 |  | 1469.5 | 1655.5 | 151.2821 | 0 | 0.2442 | 0 | 1.5128 | 0 | 0.002442 | 0 | 1.5128 | 0.002442 | 2.1945 | 63209.5 | 0.68169
38943.5534 | 2427 | 0 | 38943.5535 | 2004 | 0 |  | 1654.5 | 1840.5 | 148.1685 | 0 | 122.3443 | 0 | 1.4817 | 0 | 1.2234 | 0 | 1.4817 | 1.2234 | 4.342 | 26.3663 | 2.8603
38943.5556 | 2156 | 0 | 38943.5556 | 2435 | 0 |  | 1839.5 | 2025.5 | 131.6239 | 0 | 148.6569 | 0 | 1.3162 | 0 | 1.4866 | 0 | 1.3162 | 1.4866 | 17.4573 | 3.9992 | 16.1411
38943.5577 | 1999 | 0 | 38943.5577 | 2486 | 0 |  | 2024 | 2210 | 122.0391 | 0 | 151.7705 | 0 | 1.2204 | 0 | 1.5177 | 0 | 1.2204 | 1.5177 | 26.6823 | 1.8656 | 25.462
38943.5599 | 2257 | 0 | 38943.5599 | 2183 | 0 |  | 2208.5 | 2394.5 | 137.79 | 0 | 133.2723 | 0 | 1.3779 | 0 | 1.3327 | 0 | 1.3779 | 1.3327 | 12.2012 | 16.0046 | 10.8233
38943.562 | 2012 | 0 | 38943.562 | 1368 | 0 |  | 2393.5 | 2579.5 | 122.8327 | 0 | 83.5165 | 0 | 1.2283 | 0 | 0.83516 | 0 | 1.2283 | 0.83516 | 25.8638 | 85.1155 | 24.6355
38943.5641 | 2029 | 0 | 38943.5642 | 1652 | 0 |  | 2578.5 | 2764.5 | 123.8706 | 0 | 100.8547 | 0 | 1.2387 | 0 | 1.0085 | 0 | 1.2387 | 1.0085 | 24.8093 | 53.2918 | 23.5706

## E9-F12
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 160.0965 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38943.5342 | 1 | 0 | 38943.5342 | 1 | 0 |  | -11.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262138 | 262138 | 262137.9994
38943.5363 | 1 | 0 | 38943.5363 | 1 | 0 |  | 173.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262138 | 262138 | 262137.9994
38943.5384 | 1 | 0 | 38943.5385 | 1 | 0 |  | 358.5 | 544.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262138 | 262138 | 262137.9994
38943.5406 | 2354 | 0 | 38943.5406 | 5 | 0 |  | 543 | 729 | 143.7118 | 0 | 0.30525 | 0 | 1.4371 | 0 | 0.0030525 | 0 | 1.4371 | 0.0030525 | 11.401 | 52347.6 | 9.9639
38943.5427 | 7 | 0 | 38943.5427 | 2 | 0 |  | 727.5 | 913.5 | 0.42735 | 0 | 0.1221 | 0 | 0.0042735 | 0 | 0.001221 | 0 | 0.0042735 | 0.001221 | 37362.5714 | 131019 | 37362.5672
38943.5449 | 2214 | 1 | 38943.5449 | 4 | 0 |  | 912.5 | 1098.5 | 135.1648 | 0.06105 | 0.2442 | 0 | 1.3516 | 0.0006105 | 0.002442 | 0 | 1.351 | 0.002442 | 18.4537 | 65459.5 | 40675.861
38943.547 | 2193 | 0 | 38943.547 | 4 | 0 |  | 1097.5 | 1283.5 | 133.8828 | 0 | 0.2442 | 0 | 1.3388 | 0 | 0.002442 | 0 | 1.3388 | 0.002442 | 19.5796 | 65459.5 | 18.2407
38943.5491 | 2048 | 0 | 38943.5492 | 4 | 0 |  | 1282 | 1468 | 125.0305 | 0 | 0.2442 | 0 | 1.2503 | 0 | 0.002442 | 0 | 1.2503 | 0.002442 | 28.0459 | 65459.5 | 26.7956
38943.5513 | 2606 | 0 | 38943.5513 | 4 | 0 |  | 1467 | 1653 | 159.0965 | 0 | 0.2442 | 0 | 1.591 | 0 | 0.002442 | 0 | 1.591 | 0.002442 | 0.62855 | 65459.5 | 0.96242
38943.5534 | 2519 | 0 | 38943.5534 | 2284 | 0 |  | 1651.5 | 1837.5 | 153.7851 | 0 | 139.4383 | 0 | 1.5379 | 0 | 1.3944 | 0 | 1.5379 | 1.3944 | 4.104 | 14.8152 | 2.5662
38943.5556 | 2045 | 0 | 38943.5556 | 2478 | 0 |  | 1836.5 | 2022.5 | 124.8474 | 0 | 151.2821 | 0 | 1.2485 | 0 | 1.5128 | 0 | 1.2485 | 1.5128 | 28.2337 | 5.8265 | 26.9853
38943.5577 | 2467 | 0 | 38943.5577 | 2029 | 0 |  | 2021 | 2207 | 150.6105 | 0 | 123.8706 | 0 | 1.5061 | 0 | 1.2387 | 0 | 1.5061 | 1.2387 | 6.2983 | 29.2449 | 4.7922
38943.5598 | 2515 | 0 | 38943.5598 | 2181 | 0 |  | 2206 | 2392 | 153.5409 | 0 | 133.1502 | 0 | 1.5354 | 0 | 1.3315 | 0 | 1.5354 | 1.3315 | 4.2696 | 20.2375 | 2.7342
38943.562 | 2244 | 0 | 38943.562 | 1401 | 0 |  | 2390.5 | 2576.5 | 136.9963 | 0 | 85.5311 | 0 | 1.37 | 0 | 0.85531 | 0 | 1.37 | 0.85531 | 16.8619 | 87.1792 | 15.4919
38943.5641 | 2128 | 0 | 38943.5641 | 1725 | 1 |  | 2575.5 | 2761.5 | 129.9145 | 0 | 105.3114 | 0.06105 | 1.2991 | 0 | 1.0531 | 0.0006105 | 1.2991 | 1.0525 | 23.2321 | 52.1102 | 21.933

## E9-F11
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 156.0672 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38943.5341 | 1 | 0 | 38943.5342 | 1 | 0 |  | -14 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38943.5363 | 1 | 0 | 38943.5363 | 1 | 0 |  | 170.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38943.5384 | 1 | 0 | 38943.5384 | 1 | 0 |  | 355.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38943.5405 | 2072 | 0 | 38943.5406 | 4 | 0 |  | 540 | 726 | 126.4957 | 0 | 0.2442 | 0 | 1.265 | 0 | 0.002442 | 0 | 1.265 | 0.002442 | 23.3774 | 63809.5 | 22.1125
38943.5427 | 1291 | 0 | 38943.5427 | 3 | 0 |  | 725 | 911 | 78.8156 | 0 | 0.18315 | 0 | 0.78816 | 0 | 0.0018315 | 0 | 0.78816 | 0.0018315 | 98.0155 | 85112.6667 | 97.2273
38943.5448 | 2252 | 0 | 38943.5448 | 4 | 0 |  | 909.5 | 1095.5 | 137.4847 | 0 | 0.2442 | 0 | 1.3748 | 0 | 0.002442 | 0 | 1.3748 | 0.002442 | 13.516 | 63809.5 | 12.1411
38943.547 | 2170 | 0 | 38943.547 | 4 | 1 |  | 1094.5 | 1280.5 | 132.4786 | 0 | 0.2442 | 0.06105 | 1.3248 | 0 | 0.002442 | 0.0006105 | 1.3248 | 0.0018315 | 17.8055 | 85112.6667 | 16.4807
38943.5491 | 2521 | 0 | 38943.5491 | 5 | 0 |  | 1279.5 | 1465.5 | 153.9072 | 0 | 0.30525 | 0 | 1.5391 | 0 | 0.0030525 | 0 | 1.5391 | 0.0030525 | 1.4034 | 51027.6 | 0.13566
38943.5512 | 2178 | 0 | 38943.5513 | 4 | 0 |  | 1464 | 1650 | 132.967 | 0 | 0.2442 | 0 | 1.3297 | 0 | 0.002442 | 0 | 1.3297 | 0.002442 | 17.3728 | 63809.5 | 16.0431
38943.5534 | 2063 | 0 | 38943.5534 | 1945 | 0 |  | 1649 | 1835 | 125.9463 | 0 | 118.7424 | 0 | 1.2595 | 0 | 1.1874 | 0 | 1.2595 | 1.1874 | 23.9157 | 31.4334 | 22.6562
38943.5555 | 2369 | 0 | 38943.5555 | 2161 | 0 |  | 1833.5 | 2019.5 | 144.6276 | 0 | 131.9292 | 0 | 1.4463 | 0 | 1.3193 | 0 | 1.4463 | 1.3193 | 7.9097 | 18.2962 | 6.4634
38943.5577 | 2540 | 0 | 38943.5577 | 2434 | 0 |  | 2018.5 | 2204.5 | 155.0672 | 0 | 148.5958 | 0 | 1.5507 | 0 | 1.486 | 0 | 1.5507 | 1.486 | 0.64488 | 5.0279 | 0.90579
38943.5598 | 2189 | 0 | 38943.5598 | 2126 | 0 |  | 2203 | 2389 | 133.6386 | 0 | 129.7924 | 0 | 1.3364 | 0 | 1.2979 | 0 | 1.3364 | 1.2979 | 16.783 | 20.2437 | 15.4466
38943.5619 | 2469 | 0 | 38943.562 | 1124 | 0 |  | 2388 | 2574 | 150.7326 | 0 | 68.6203 | 0 | 1.5073 | 0 | 0.6862 | 0 | 1.5073 | 0.6862 | 3.5391 | 127.4359 | 2.0318
38943.5641 | 2266 | 0 | 38943.5641 | 1142 | 0 |  | 2572.5 | 2758.5 | 138.3394 | 0 | 69.7192 | 0 | 1.3834 | 0 | 0.69719 | 0 | 1.3834 | 0.69719 | 12.8147 | 123.8511 | 11.4313

## E9-E10
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 158.6923 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38943.5341 | 1 | 0 | 38943.5341 | 1 | 0 |  | -17 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
38943.5362 | 1 | 0 | 38943.5363 | 1 | 0 |  | 168 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
38943.5384 | 1 | 0 | 38943.5384 | 1 | 0 |  | 352.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
38943.5405 | 2240 | 0 | 38943.5405 | 4 | 0 |  | 537.5 | 723.5 | 136.7521 | 0 | 0.2442 | 0 | 1.3675 | 0 | 0.002442 | 0 | 1.3675 | 0.002442 | 16.0437 | 64884.5 | 14.6762
38943.5427 | 1892 | 0 | 38943.5427 | 3 | 0 |  | 722 | 908 | 115.5067 | 0 | 0.18315 | 0 | 1.1551 | 0 | 0.0018315 | 0 | 1.1551 | 0.0018315 | 37.3879 | 86546 | 36.2329
38943.5448 | 2572 | 0 | 38943.5448 | 2065 | 0 |  | 907 | 1093 | 157.0208 | 0 | 126.0684 | 0 | 1.5702 | 0 | 1.2607 | 0 | 1.5702 | 1.2607 | 1.0645 | 25.878 | 0.50567
38943.5469 | 2399 | 5 | 38943.5469 | 2115 | 0 |  | 1091.5 | 1277.5 | 146.4591 | 0.30525 | 129.1209 | 0 | 1.4646 | 0.0030525 | 1.2912 | 0 | 1.4615 | 1.2912 | 8.4471 | 22.9021 | 728.1595
38943.5491 | 2212 | 0 | 38943.5491 | 2527 | 0 |  | 1276.5 | 1462.5 | 135.0427 | 0 | 154.2735 | 0 | 1.3504 | 0 | 1.5427 | 0 | 1.3504 | 1.5427 | 17.5127 | 2.8643 | 16.1622
38943.5512 | 2254 | 0 | 38943.5512 | 2360 | 0 |  | 1461.5 | 1647.5 | 137.6068 | 0 | 144.0781 | 0 | 1.3761 | 0 | 1.4408 | 0 | 1.3761 | 1.4408 | 15.323 | 10.1432 | 13.9469
38943.5533 | 2055 | 0 | 38943.5534 | 2130 | 0 |  | 1646 | 1832 | 125.4579 | 0 | 130.0366 | 0 | 1.2546 | 0 | 1.3004 | 0 | 1.2546 | 1.3004 | 26.4905 | 22.0366 | 25.2359
38943.5555 | 2009 | 0 | 38943.5555 | 2246 | 0 |  | 1830.5 | 2016.5 | 122.6496 | 0 | 137.1184 | 0 | 1.2265 | 0 | 1.3712 | 0 | 1.2265 | 1.3712 | 29.3868 | 15.7337 | 28.1603
38943.5576 | 2542 | 0 | 38943.5576 | 2086 | 0 |  | 2015.5 | 2201.5 | 155.1893 | 0 | 127.3504 | 0 | 1.5519 | 0 | 1.2735 | 0 | 1.5519 | 1.2735 | 2.2573 | 24.6107 | 0.70539
38943.5598 | 2467 | 0 | 38943.5598 | 2583 | 0 |  | 2200.5 | 2386.5 | 150.6105 | 0 | 157.6923 | 0 | 1.5061 | 0 | 1.5769 | 0 | 1.5061 | 1.5769 | 5.366 | 0.63415 | 3.8599
38943.5619 | 2203 | 0 | 38943.5619 | 2551 | 0 |  | 2385 | 2571 | 134.4933 | 0 | 155.7387 | 0 | 1.3449 | 0 | 1.5574 | 0 | 1.3449 | 1.5574 | 17.9927 | 1.8965 | 16.6478
38943.564 | 2239 | 0 | 38943.5641 | 2305 | 0 |  | 2570 | 2756 | 136.6911 | 0 | 140.7204 | 0 | 1.3669 | 0 | 1.4072 | 0 | 1.3669 | 1.4072 | 16.0956 | 12.7714 | 14.7287

## D8-E10
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 160.4017 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38943.534 | 1 | 0 | 38943.534 | 1 | 0 |  | -25.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
38943.5361 | 1 | 0 | 38943.5362 | 1 | 0 |  | 159.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
38943.5383 | 1 | 0 | 38943.5383 | 1 | 0 |  | 344.5 | 530.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
38943.5404 | 5 | 0 | 38943.5404 | 3 | 0 |  | 529 | 715 | 0.30525 | 0 | 0.18315 | 0 | 0.0030525 | 0 | 0.0018315 | 0 | 0.0030525 | 0.0018315 | 52447.6 | 87479.3333 | 52447.5969
38943.5426 | 2 | 0 | 38943.5426 | 2098 | 0 |  | 713.5 | 899.5 | 0.1221 | 0 | 128.083 | 0 | 0.001221 | 0 | 1.2808 | 0 | 0.001221 | 1.2808 | 131269 | 25.2326 | 131268.9988
38943.5447 | 4 | 0 | 38943.5447 | 2016 | 0 |  | 898.5 | 1084.5 | 0.2442 | 0 | 123.0769 | 0 | 0.002442 | 0 | 1.2308 | 0 | 0.002442 | 1.2308 | 65584.5 | 30.3264 | 65584.4976
38943.5468 | 4 | 0 | 38943.5469 | 2611 | 0 |  | 1083.5 | 1269.5 | 0.2442 | 0 | 159.4017 | 0 | 0.002442 | 0 | 1.594 | 0 | 0.002442 | 1.594 | 65584.5 | 0.62735 | 65584.4976
38943.549 | 3 | 0 | 38943.549 | 2381 | 0 |  | 1268 | 1454 | 0.18315 | 0 | 145.3602 | 0 | 0.0018315 | 0 | 1.4536 | 0 | 0.0018315 | 1.4536 | 87479.3333 | 10.3478 | 87479.3315
38943.5511 | 4 | 0 | 38943.5511 | 2416 | 0 |  | 1453 | 1639 | 0.2442 | 0 | 147.4969 | 0 | 0.002442 | 0 | 1.475 | 0 | 0.002442 | 1.475 | 65584.5 | 8.7492 | 65584.4976
38943.5533 | 2148 | 0 | 38943.5533 | 2164 | 0 |  | 1637.5 | 1823.5 | 131.1355 | 0 | 132.1123 | 0 | 1.3114 | 0 | 1.3211 | 0 | 1.3114 | 1.3211 | 22.3175 | 21.4131 | 21.0061
38943.5554 | 1837 | 0 | 38943.5554 | 2025 | 0 |  | 1822.5 | 2008.5 | 112.149 | 0 | 123.6264 | 0 | 1.1215 | 0 | 1.2363 | 0 | 1.1215 | 1.2363 | 43.0256 | 29.7472 | 41.9041
38943.5575 | 2322 | 0 | 38943.5575 | 2416 | 0 |  | 2007 | 2193 | 141.7582 | 0 | 147.4969 | 0 | 1.4176 | 0 | 1.475 | 0 | 1.4176 | 1.475 | 13.1516 | 8.7492 | 11.734
38943.5597 | 1365 | 0 | 38943.5597 | 2247 | 0 |  | 2192 | 2378 | 83.3333 | 0 | 137.1795 | 0 | 0.83333 | 0 | 1.3718 | 0 | 0.83333 | 1.3718 | 92.4821 | 16.9283 | 91.6487
38943.5618 | 1158 | 0 | 38943.5618 | 2420 | 0 |  | 2376.5 | 2562.5 | 70.696 | 0 | 147.7411 | 0 | 0.70696 | 0 | 1.4774 | 0 | 0.70696 | 1.4774 | 126.8895 | 8.5694 | 126.1825
38943.5639 | 572 | 0 | 38943.564 | 2064 | 0 |  | 2561.5 | 2747.5 | 34.9206 | 0 | 126.0073 | 0 | 0.34921 | 0 | 1.2601 | 0 | 0.34921 | 1.2601 | 359.3322 | 27.2955 | 358.983

## D8-E9
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 158.3871 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38943.534 | 1 | 0 | 38943.534 | 1 | 0 |  | -28 | 158 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38943.5361 | 1 | 0 | 38943.5361 | 1 | 0 |  | 156.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38943.5383 | 1 | 0 | 38943.5383 | 1 | 0 |  | 341.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38943.5404 | 2 | 0 | 38943.5404 | 2484 | 0 |  | 526 | 712 | 0.1221 | 0 | 151.6484 | 0 | 0.001221 | 0 | 1.5165 | 0 | 0.001221 | 1.5165 | 129619 | 4.4436 | 129618.9988
38943.5425 | 1 | 0 | 38943.5425 | 2 | 0 |  | 711 | 897 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 259338 | 129619 | 259337.9994
38943.5447 | 2 | 0 | 38943.5447 | 2114 | 0 |  | 895.5 | 1081.5 | 0.1221 | 0 | 129.0598 | 0 | 0.001221 | 0 | 1.2906 | 0 | 0.001221 | 1.2906 | 129619 | 22.7237 | 129618.9988
38943.5468 | 2 | 0 | 38943.5468 | 2204 | 0 |  | 1080.5 | 1266.5 | 0.1221 | 0 | 134.5543 | 0 | 0.001221 | 0 | 1.3455 | 0 | 0.001221 | 1.3455 | 129619 | 17.7123 | 129618.9988
38943.5489 | 2 | 0 | 38943.549 | 2002 | 0 |  | 1265.5 | 1451.5 | 0.1221 | 0 | 122.2222 | 0 | 0.001221 | 0 | 1.2222 | 0 | 0.001221 | 1.2222 | 129619 | 29.5894 | 129618.9988
38943.5511 | 2 | 1 | 38943.5511 | 2213 | 0 |  | 1450 | 1636 | 0.1221 | 0.06105 | 135.1038 | 0 | 0.001221 | 0.0006105 | 1.351 | 0 | 0.0006105 | 1.351 | 53978.5482 | 26.2977 | 53957.7262
38943.5532 | 2141 | 0 | 38943.5532 | 2115 | 0 |  | 1634.5 | 1820.5 | 130.7082 | 0 | 129.1209 | 0 | 1.3071 | 0 | 1.2912 | 0 | 1.3071 | 1.2912 | 21.1761 | 22.6657 | 19.869
38943.5554 | 1910 | 0 | 38943.5554 | 2091 | 0 |  | 1819.5 | 2005.5 | 116.6056 | 0 | 127.6557 | 0 | 1.1661 | 0 | 1.2766 | 0 | 1.1661 | 1.2766 | 35.8314 | 24.0736 | 34.6654
38943.5575 | 2371 | 0 | 38943.5575 | 2176 | 0 |  | 2004.5 | 2190.5 | 144.7497 | 0 | 132.8449 | 0 | 1.4475 | 0 | 1.3284 | 0 | 1.4475 | 1.3284 | 9.4213 | 19.227 | 7.9738
38943.5596 | 1588 | 0 | 38943.5597 | 2570 | 0 |  | 2189 | 2375 | 96.9475 | 0 | 156.8987 | 0 | 0.96947 | 0 | 1.569 | 0 | 0.96947 | 1.569 | 63.3741 | 0.94864 | 62.4046
38943.5618 | 1688 | 0 | 38943.5618 | 2031 | 0 |  | 2374 | 2560 | 103.0525 | 0 | 123.9927 | 0 | 1.0305 | 0 | 1.2399 | 0 | 1.0305 | 1.2399 | 53.6955 | 27.739 | 52.665
38943.5639 | 778 | 0 | 38943.5639 | 2578 | 0 |  | 2558.5 | 2744.5 | 47.4969 | 0 | 157.3871 | 0 | 0.47497 | 0 | 1.5739 | 0 | 0.47497 | 1.5739 | 233.4679 | 0.63538 | 232.9929

## D7-E10
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 160.2186 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38943.5339 | 1 | 0 | 38943.5339 | 1 | 0 |  | -36.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
38943.536 | 1 | 0 | 38943.536 | 1 | 0 |  | 148 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
38943.5381 | 1 | 0 | 38943.5382 | 1 | 0 |  | 333 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
38943.5403 | 4 | 0 | 38943.5403 | 2 | 0 |  | 517.5 | 703.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 65509.5 | 131119 | 65509.4976
38943.5424 | 1 | 0 | 38943.5424 | 2075 | 0 |  | 702.5 | 888.5 | 0.06105 | 0 | 126.6789 | 0 | 0.0006105 | 0 | 1.2668 | 0 | 0.0006105 | 1.2668 | 262338 | 26.4761 | 262337.9994
38943.5446 | 4 | 0 | 38943.5446 | 2603 | 0 |  | 887.5 | 1073.5 | 0.2442 | 0 | 158.9133 | 0 | 0.002442 | 0 | 1.5891 | 0 | 0.002442 | 1.5891 | 65509.5 | 0.82136 | 65509.4976
38943.5467 | 4 | 0 | 38943.5467 | 2207 | 0 |  | 1072 | 1258 | 0.2442 | 0 | 134.7375 | 0 | 0.002442 | 0 | 1.3474 | 0 | 0.002442 | 1.3474 | 65509.5 | 18.9116 | 65509.4976
38943.5488 | 4 | 0 | 38943.5489 | 2379 | 0 |  | 1257 | 1443 | 0.2442 | 0 | 145.2381 | 0 | 0.002442 | 0 | 1.4524 | 0 | 0.002442 | 1.4524 | 65509.5 | 10.3144 | 65509.4976
38943.551 | 4 | 2 | 38943.551 | 2608 | 2 |  | 1441.5 | 1627.5 | 0.2442 | 0.1221 | 159.2186 | 0.1221 | 0.002442 | 0.001221 | 1.5922 | 0.001221 | 0.001221 | 1.591 | 828.651 | 0.63649 | 828.0185
38943.5531 | 1939 | 0 | 38943.5531 | 2582 | 0 |  | 1626.5 | 1812.5 | 118.3761 | 0 | 157.6313 | 0 | 1.1838 | 0 | 1.5763 | 0 | 1.1838 | 1.5763 | 35.3471 | 1.6414 | 34.1633
38943.5553 | 1722 | 0 | 38943.5553 | 2205 | 0 |  | 1811 | 1997 | 105.1282 | 0 | 134.6154 | 0 | 1.0513 | 0 | 1.3462 | 0 | 1.0513 | 1.3462 | 52.403 | 19.0195 | 51.3517
38943.5574 | 2134 | 0 | 38943.5574 | 2426 | 0 |  | 1996 | 2182 | 130.2808 | 0 | 148.1074 | 0 | 1.3028 | 0 | 1.4811 | 0 | 1.3028 | 1.4811 | 22.9794 | 8.1772 | 21.6766
38943.5595 | 1467 | 1 | 38943.5595 | 2318 | 1 |  | 2180.5 | 2366.5 | 89.5604 | 0.06105 | 141.514 | 0.06105 | 0.8956 | 0.0006105 | 1.4151 | 0.0006105 | 0.89499 | 1.4145 | 79.3573 | 13.2303 | 13511.6517
38943.5617 | 1250 | 1 | 38943.5617 | 2384 | 0 |  | 2365.5 | 2551.5 | 76.3126 | 0.06105 | 145.5433 | 0 | 0.76313 | 0.0006105 | 1.4554 | 0 | 0.76252 | 1.4554 | 110.9192 | 10.0831 | 12579.4696
38943.5638 | 1253 | 2 | 38943.5638 | 2332 | 1 |  | 2550.5 | 2736.5 | 76.4957 | 0.1221 | 142.3687 | 0.06105 | 0.76496 | 0.001221 | 1.4237 | 0.0006105 | 0.76374 | 1.4231 | 111.0374 | 12.548 | 7633.6028

## D7-E9
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 158.2039 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38943.5338 | 1 | 0 | 38943.5339 | 1 | 0 |  | -39.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38943.536 | 1 | 0 | 38943.536 | 1 | 0 |  | 145.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38943.5381 | 1 | 0 | 38943.5381 | 1 | 0 |  | 330.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38943.5403 | 2 | 0 | 38943.5403 | 2547 | 0 |  | 515 | 701 | 0.1221 | 0 | 155.4945 | 0 | 0.001221 | 0 | 1.5549 | 0 | 0.001221 | 1.5549 | 129469 | 1.7424 | 129468.9988
38943.5424 | 2 | 0 | 38943.5424 | 2 | 0 |  | 699.5 | 885.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 129469 | 129469 | 129468.9988
38943.5445 | 2 | 0 | 38943.5445 | 2316 | 0 |  | 884.5 | 1070.5 | 0.1221 | 0 | 141.3919 | 0 | 0.001221 | 0 | 1.4139 | 0 | 0.001221 | 1.4139 | 129469 | 11.8903 | 129468.9988
38943.5467 | 2 | 0 | 38943.5467 | 2017 | 0 |  | 1069.5 | 1255.5 | 0.1221 | 0 | 123.138 | 0 | 0.001221 | 0 | 1.2314 | 0 | 0.001221 | 1.2314 | 129469 | 28.4769 | 129468.9988
38943.5488 | 2 | 0 | 38943.5488 | 2556 | 0 |  | 1254 | 1440 | 0.1221 | 0 | 156.044 | 0 | 0.001221 | 0 | 1.5604 | 0 | 0.001221 | 1.5604 | 129469 | 1.3842 | 129468.9988
38943.5509 | 3 | 9 | 38943.551 | 2266 | 4 |  | 1439 | 1625 | 0.18315 | 0.54945 | 138.3394 | 0.2442 | 0.0018315 | 0.0054945 | 1.3834 | 0.002442 | 0.003663 | 1.381 | 4575.5944 | 17.7974 | 4330.0519
38943.5531 | 1665 | 1 | 38943.5531 | 2116 | 0 |  | 1623.5 | 1809.5 | 101.6484 | 0.06105 | 129.1819 | 0 | 1.0165 | 0.0006105 | 1.2918 | 0 | 1.0159 | 1.2918 | 55.8212 | 22.466 | 16975.7868
38943.5552 | 1982 | 2 | 38943.5552 | 2329 | 0 |  | 1808.5 | 1994.5 | 121.0012 | 0.1221 | 142.1856 | 0 | 1.21 | 0.001221 | 1.4219 | 0 | 1.2088 | 1.4219 | 31.0552 | 11.2658 | 3074.8938
38943.5574 | 1987 | 0 | 38943.5574 | 2145 | 0 |  | 1993 | 2179 | 121.3065 | 0 | 130.9524 | 0 | 1.2131 | 0 | 1.3095 | 0 | 1.2131 | 1.3095 | 30.4167 | 20.8103 | 29.2036
38943.5595 | 1693 | 3 | 38943.5595 | 2505 | 1 |  | 2178 | 2364 | 103.3578 | 0.18315 | 152.9304 | 0.06105 | 1.0336 | 0.0018315 | 1.5293 | 0.0006105 | 1.0317 | 1.5287 | 56.0403 | 3.4521 | 995.9445
38943.5616 | 1771 | 4 | 38943.5617 | 2068 | 2 |  | 2362.5 | 2548.5 | 108.1197 | 0.2442 | 126.2515 | 0.1221 | 1.0812 | 0.002442 | 1.2625 | 0.001221 | 1.0788 | 1.2613 | 46.8456 | 25.3855 | 4132.0955
38943.5638 | 858 | 5 | 38943.5638 | 2575 | 3 |  | 2547.5 | 2733.5 | 52.381 | 0.30525 | 157.2039 | 0.18315 | 0.52381 | 0.0030525 | 1.572 | 0.0018315 | 0.52076 | 1.5702 | 2551.636 | 0.63689 | 218.7635

## D7-D8
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 135.4322 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38943.5338 | 1 | 0 | 38943.5338 | 1 | 0 |  | -42 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221738 | 221738 | 221737.9994
38943.5359 | 1 | 0 | 38943.536 | 1 | 0 |  | 142.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221738 | 221738 | 221737.9994
38943.5381 | 1 | 0 | 38943.5381 | 1 | 0 |  | 327.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221738 | 221738 | 221737.9994
38943.5402 | 2 | 0 | 38943.5402 | 1 | 0 |  | 512 | 698 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 110819 | 221738 | 110818.9988
38943.5424 | 1 | 0 | 38943.5424 | 1 | 0 |  | 697 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221738 | 221738 | 221737.9994
38943.5445 | 2 | 0 | 38943.5445 | 2 | 0 |  | 881.5 | 1067.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 110819 | 110819 | 110818.9988
38943.5466 | 2 | 0 | 38943.5467 | 2 | 0 |  | 1066.5 | 1252.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 110819 | 110819 | 110818.9988
38943.5488 | 8 | 4 | 38943.5488 | 6 | 2 |  | 1251.5 | 1437.5 | 0.4884 | 0.2442 | 0.3663 | 0.1221 | 0.004884 | 0.002442 | 0.003663 | 0.001221 | 0.002442 | 0.002442 | 55359.5 | 55359.5 | 55060.0409
38943.5509 | 946 | 1051 | 38943.5509 | 1028 | 1069 |  | 1436 | 1622 | 57.7534 | 64.1636 | 62.7595 | 65.2625 | 0.57753 | 0.64164 | 0.62759 | 0.65263 | 0.064103 | 0.025031 | 477.536 | 650.9878 | 18.2589
38943.5531 | 1738 | 379 | 38943.5531 | 1573 | 312 |  | 1620.5 | 1806.5 | 106.105 | 23.138 | 96.0317 | 19.0476 | 1.0611 | 0.23138 | 0.96032 | 0.19048 | 0.82967 | 0.76984 | 48.0467 | 105.5177 | 13.7338
38943.5552 | 1646 | 312 | 38943.5552 | 1880 | 339 |  | 1805.5 | 1991.5 | 100.4884 | 19.0476 | 114.7741 | 20.696 | 1.0049 | 0.19048 | 1.1477 | 0.20696 | 0.81441 | 0.94078 | 299.0974 | 27.3054 | 17.9001
38943.5573 | 2090 | 52 | 38943.5573 | 2202 | 49 |  | 1990.5 | 2176.5 | 127.5946 | 3.1746 | 134.4322 | 2.9915 | 1.2759 | 0.031746 | 1.3443 | 0.029915 | 1.2442 | 1.3144 | 0.56652 | 0.25214 | 0.36943
38943.5595 | 1782 | 629 | 38943.5595 | 1512 | 454 |  | 2175 | 2361 | 108.7912 | 38.4005 | 92.3077 | 27.7167 | 1.0879 | 0.384 | 0.92308 | 0.27717 | 0.70391 | 0.64591 | 15.2269 | 36.7223 | 8.2251
38943.5616 | 1554 | 564 | 38943.5616 | 1261 | 685 |  | 2360 | 2546 | 94.8718 | 34.4322 | 76.9841 | 41.8193 | 0.94872 | 0.34432 | 0.76984 | 0.41819 | 0.6044 | 0.35165 | 40.0878 | 84.5184 | 8.1523
38943.5638 | 1224 | 882 | 38943.5638 | 1153 | 840 |  | 2544.5 | 2730.5 | 74.7253 | 53.8462 | 70.3907 | 51.2821 | 0.74725 | 0.53846 | 0.70391 | 0.51282 | 0.20879 | 0.19109 | 360.7411 | 1329.2991 | 11.85

## C6-F12
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 148.4969 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38943.5338 | 1 | 0 | 38943.5338 | 1 | 0 |  | -45 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38943.5359 | 1 | 0 | 38943.5359 | 1 | 0 |  | 140 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38943.5381 | 1 | 0 | 38943.5381 | 1 | 0 |  | 324.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38943.5402 | 2 | 0 | 38943.5402 | 2 | 0 |  | 509.5 | 695.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121519 | 121519 | 121518.9988
38943.5423 | 1 | 0 | 38943.5423 | 2 | 0 |  | 694 | 880 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 243138 | 121519 | 243137.9994
38943.5445 | 3 | 0 | 38943.5445 | 2 | 0 |  | 879 | 1065 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 80979.3333 | 121519 | 80979.3315
38943.5466 | 3 | 0 | 38943.5466 | 3 | 0 |  | 1063.5 | 1249.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 80979.3333 | 80979.3333 | 80979.3315
38943.5488 | 2 | 0 | 38943.5488 | 2 | 0 |  | 1248.5 | 1434.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121519 | 121519 | 121518.9988
38943.5509 | 3 | 0 | 38943.5509 | 3 | 0 |  | 1433.5 | 1619.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 80979.3333 | 80979.3333 | 80979.3315
38943.553 | 4 | 0 | 38943.553 | 2325 | 0 |  | 1618 | 1804 | 0.2442 | 0 | 141.9414 | 0 | 0.002442 | 0 | 1.4194 | 0 | 0.002442 | 1.4194 | 60709.5 | 4.6185 | 60709.4976
38943.5552 | 4 | 0 | 38943.5552 | 1956 | 0 |  | 1802.5 | 1988.5 | 0.2442 | 0 | 119.4139 | 0 | 0.002442 | 0 | 1.1941 | 0 | 0.002442 | 1.1941 | 60709.5 | 24.3548 | 60709.4976
38943.5573 | 1008 | 0 | 38943.5573 | 2416 | 0 |  | 1987.5 | 2173.5 | 61.5385 | 0 | 147.4969 | 0 | 0.61538 | 0 | 1.475 | 0 | 0.61538 | 1.475 | 141.3075 | 0.67798 | 140.6922
38943.5594 | 322 | 0 | 38943.5595 | 1975 | 0 |  | 2172.5 | 2358.5 | 19.6581 | 0 | 120.5739 | 0 | 0.19658 | 0 | 1.2057 | 0 | 0.19658 | 1.2057 | 655.3975 | 23.1585 | 655.2009
38943.5616 | 226 | 0 | 38943.5616 | 1247 | 0 |  | 2357 | 2543 | 13.7973 | 0 | 76.1294 | 0 | 0.13797 | 0 | 0.76129 | 0 | 0.13797 | 0.76129 | 976.2743 | 95.0585 | 976.1364
38943.5637 | 26 | 0 | 38943.5637 | 1190 | 0 |  | 2542 | 2728 | 1.5873 | 0 | 72.6496 | 0 | 0.015873 | 0 | 0.7265 | 0 | 0.015873 | 0.7265 | 9255.3077 | 104.4017 | 9255.2918

## C6-F11
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 153.5641 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38943.5338 | 1 | 0 | 38943.5338 | 1 | 0 |  | -47.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38943.5359 | 1 | 0 | 38943.5359 | 1 | 0 |  | 137 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38943.538 | 1 | 0 | 38943.538 | 1 | 0 |  | 321.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38943.5402 | 4 | 0 | 38943.5402 | 2 | 0 |  | 506.5 | 692.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 62784.5 | 125669 | 62784.4976
38943.5423 | 2 | 0 | 38943.5423 | 2 | 0 |  | 691.5 | 877.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125669 | 125669 | 125668.9988
38943.5444 | 4 | 0 | 38943.5445 | 3 | 0 |  | 876 | 1062 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62784.5 | 83746 | 62784.4976
38943.5466 | 4 | 0 | 38943.5466 | 3 | 0 |  | 1061 | 1247 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62784.5 | 83746 | 62784.4976
38943.5487 | 4 | 0 | 38943.5487 | 3 | 0 |  | 1245.5 | 1431.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62784.5 | 83746 | 62784.4976
38943.5509 | 4 | 0 | 38943.5509 | 3 | 0 |  | 1430.5 | 1616.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62784.5 | 83746 | 62784.4976
38943.553 | 4 | 0 | 38943.553 | 2306 | 0 |  | 1615 | 1801 | 0.2442 | 0 | 140.7814 | 0 | 0.002442 | 0 | 1.4078 | 0 | 0.002442 | 1.4078 | 62784.5 | 9.0798 | 62784.4976
38943.5551 | 4 | 0 | 38943.5552 | 2087 | 0 |  | 1800 | 1986 | 0.2442 | 0 | 127.4115 | 0 | 0.002442 | 0 | 1.2741 | 0 | 0.002442 | 1.2741 | 62784.5 | 20.5261 | 62784.4976
38943.5573 | 662 | 0 | 38943.5573 | 2499 | 0 |  | 1984.5 | 2170.5 | 40.4151 | 0 | 152.5641 | 0 | 0.40415 | 0 | 1.5256 | 0 | 0.40415 | 1.5256 | 279.9668 | 0.65546 | 279.5626
38943.5594 | 287 | 0 | 38943.5594 | 2228 | 0 |  | 2169.5 | 2355.5 | 17.5214 | 0 | 136.0195 | 0 | 0.17521 | 0 | 1.3602 | 0 | 0.17521 | 1.3602 | 776.439 | 12.8986 | 776.2638
38943.5616 | 245 | 0 | 38943.5616 | 1137 | 0 |  | 2354.5 | 2540.5 | 14.9573 | 0 | 69.4139 | 0 | 0.14957 | 0 | 0.69414 | 0 | 0.14957 | 0.69414 | 926.6857 | 121.2296 | 926.5361
38943.5637 | 26 | 0 | 38943.5637 | 893 | 0 |  | 2539 | 2725 | 1.5873 | 0 | 54.5177 | 0 | 0.015873 | 0 | 0.54518 | 0 | 0.015873 | 0.54518 | 9574.5385 | 181.6775 | 9574.5226

## C6-E10
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 154.8462 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38943.5337 | 1 | 0 | 38943.5337 | 1 | 0 |  | -50.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38943.5359 | 1 | 0 | 38943.5359 | 1 | 0 |  | 134.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38943.538 | 1 | 0 | 38943.538 | 1 | 0 |  | 319 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
38943.5401 | 4 | 0 | 38943.5401 | 41 | 0 |  | 503.5 | 689.5 | 0.2442 | 0 | 2.5031 | 0 | 0.002442 | 0 | 0.025031 | 0 | 0.002442 | 0.025031 | 63309.5 | 6086.2927 | 63309.4976
38943.5423 | 4 | 0 | 38943.5423 | 2 | 0 |  | 688.5 | 874.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 63309.5 | 126719 | 63309.4976
38943.5444 | 4 | 0 | 38943.5444 | 2507 | 0 |  | 873.5 | 1059.5 | 0.2442 | 0 | 153.0525 | 0 | 0.002442 | 0 | 1.5305 | 0 | 0.002442 | 1.5305 | 63309.5 | 1.1719 | 63309.4976
38943.5465 | 4 | 0 | 38943.5466 | 2093 | 0 |  | 1058 | 1244 | 0.2442 | 0 | 127.7778 | 0 | 0.002442 | 0 | 1.2778 | 0 | 0.002442 | 1.2778 | 63309.5 | 21.1839 | 63309.4976
38943.5487 | 3 | 0 | 38943.5487 | 2348 | 0 |  | 1243 | 1429 | 0.18315 | 0 | 143.3455 | 0 | 0.0018315 | 0 | 1.4335 | 0 | 0.0018315 | 1.4335 | 84446 | 8.023 | 84445.9982
38943.5508 | 3 | 0 | 38943.5508 | 2053 | 0 |  | 1427.5 | 1613.5 | 0.18315 | 0 | 125.3358 | 0 | 0.0018315 | 0 | 1.2534 | 0 | 0.0018315 | 1.2534 | 84446 | 23.5451 | 84445.9982
38943.553 | 4 | 0 | 38943.553 | 2390 | 0 |  | 1612.5 | 1798.5 | 0.2442 | 0 | 145.9096 | 0 | 0.002442 | 0 | 1.4591 | 0 | 0.002442 | 1.4591 | 63309.5 | 6.1247 | 63309.4976
38943.5551 | 4 | 0 | 38943.5551 | 2520 | 0 |  | 1797 | 1983 | 0.2442 | 0 | 153.8462 | 0 | 0.002442 | 0 | 1.5385 | 0 | 0.002442 | 1.5385 | 63309.5 | 0.65 | 63309.4976
38943.5572 | 667 | 0 | 38943.5573 | 2466 | 0 |  | 1982 | 2168 | 40.7204 | 0 | 150.5495 | 0 | 0.4072 | 0 | 1.5055 | 0 | 0.4072 | 1.5055 | 280.2669 | 2.854 | 279.8597
38943.5594 | 232 | 0 | 38943.5594 | 1996 | 0 |  | 2166.5 | 2352.5 | 14.1636 | 0 | 121.8559 | 0 | 0.14164 | 0 | 1.2186 | 0 | 0.14164 | 1.2186 | 993.2672 | 27.0731 | 993.1256
38943.5615 | 231 | 0 | 38943.5615 | 2032 | 0 |  | 2351.5 | 2537.5 | 14.1026 | 0 | 124.0537 | 0 | 0.14103 | 0 | 1.2405 | 0 | 0.14103 | 1.2405 | 998 | 24.8219 | 997.859
38943.5637 | 19 | 0 | 38943.5637 | 2246 | 0 |  | 2536.5 | 2722.5 | 1.16 | 0 | 137.1184 | 0 | 0.0116 | 0 | 1.3712 | 0 | 0.0116 | 1.3712 | 13249.3684 | 12.9288 | 13249.3568

## C6-E9
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 157.105 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38943.5337 | 1 | 0 | 38943.5337 | 1 | 0 |  | -53.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38943.5358 | 1 | 0 | 38943.5358 | 1 | 0 |  | 131.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38943.538 | 1 | 0 | 38943.538 | 1 | 0 |  | 316.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38943.5401 | 2 | 0 | 38943.5401 | 2437 | 0 |  | 501 | 687 | 0.1221 | 0 | 148.779 | 0 | 0.001221 | 0 | 1.4878 | 0 | 0.001221 | 1.4878 | 128569 | 5.5962 | 128568.9988
38943.5422 | 1 | 0 | 38943.5422 | 1943 | 0 |  | 685.5 | 871.5 | 0.06105 | 0 | 118.6203 | 0 | 0.0006105 | 0 | 1.1862 | 0 | 0.0006105 | 1.1862 | 257238 | 32.4436 | 257237.9994
38943.5444 | 2 | 0 | 38943.5444 | 2239 | 0 |  | 870.5 | 1056.5 | 0.1221 | 0 | 136.6911 | 0 | 0.001221 | 0 | 1.3669 | 0 | 0.001221 | 1.3669 | 128569 | 14.9343 | 128568.9988
38943.5465 | 2 | 0 | 38943.5465 | 2022 | 0 |  | 1055.5 | 1241.5 | 0.1221 | 0 | 123.4432 | 0 | 0.001221 | 0 | 1.2344 | 0 | 0.001221 | 1.2344 | 128569 | 27.269 | 128568.9988
38943.5486 | 2 | 0 | 38943.5487 | 2557 | 0 |  | 1240 | 1426 | 0.1221 | 0 | 156.105 | 0 | 0.001221 | 0 | 1.5611 | 0 | 0.001221 | 1.5611 | 128569 | 0.64059 | 128568.9988
38943.5508 | 2 | 0 | 38943.5508 | 2247 | 0 |  | 1425 | 1611 | 0.1221 | 0 | 137.1795 | 0 | 0.001221 | 0 | 1.3718 | 0 | 0.001221 | 1.3718 | 128569 | 14.5251 | 128568.9988
38943.5529 | 4 | 0 | 38943.5529 | 2313 | 0 |  | 1609.5 | 1795.5 | 0.2442 | 0 | 141.2088 | 0 | 0.002442 | 0 | 1.4121 | 0 | 0.002442 | 1.4121 | 64234.5 | 11.2572 | 64234.4976
38943.5551 | 5 | 0 | 38943.5551 | 2178 | 0 |  | 1794.5 | 1980.5 | 0.30525 | 0 | 132.967 | 0 | 0.0030525 | 0 | 1.3297 | 0 | 0.0030525 | 1.3297 | 51367.6 | 18.1534 | 51367.5969
38943.5572 | 283 | 0 | 38943.5572 | 2093 | 0 |  | 1979 | 2165 | 17.2772 | 0 | 127.7778 | 0 | 0.17277 | 0 | 1.2778 | 0 | 0.17277 | 1.2778 | 809.3216 | 22.9517 | 809.1488
38943.5593 | 213 | 0 | 38943.5594 | 2313 | 0 |  | 2164 | 2350 | 13.0037 | 0 | 141.2088 | 0 | 0.13004 | 0 | 1.4121 | 0 | 0.13004 | 1.4121 | 1108.1596 | 11.2572 | 1108.0296
38943.5615 | 179 | 0 | 38943.5615 | 2421 | 0 |  | 2348.5 | 2534.5 | 10.928 | 0 | 147.8022 | 0 | 0.10928 | 0 | 1.478 | 0 | 0.10928 | 1.478 | 1337.6425 | 6.2941 | 1337.5332
38943.5636 | 20 | 0 | 38943.5636 | 2162 | 0 |  | 2533.5 | 2719.5 | 1.221 | 0 | 131.9902 | 0 | 0.01221 | 0 | 1.3199 | 0 | 0.01221 | 1.3199 | 12766.9 | 19.0278 | 12766.8878

## C5-F12
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 141.5372 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38943.5336 | 1 | 0 | 38943.5336 | 1 | 0 |  | -61.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231738 | 231738 | 231737.9994
38943.5357 | 1 | 0 | 38943.5357 | 1 | 0 |  | 123 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231738 | 231738 | 231737.9994
38943.5379 | 1 | 0 | 38943.5379 | 1 | 0 |  | 308 | 494 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231738 | 231738 | 231737.9994
38943.54 | 2 | 0 | 38943.54 | 3 | 0 |  | 492.5 | 678.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 115819 | 77179.3333 | 115818.9988
38943.5421 | 2 | 0 | 38943.5422 | 1 | 0 |  | 677.5 | 863.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115819 | 231738 | 115818.9988
38943.5443 | 3 | 0 | 38943.5443 | 2 | 0 |  | 862 | 1048 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 77179.3333 | 115819 | 77179.3315
38943.5464 | 2 | 0 | 38943.5464 | 2 | 0 |  | 1047 | 1233 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 115819 | 115819 | 115818.9988
38943.5486 | 3 | 0 | 38943.5486 | 3 | 0 |  | 1231.5 | 1417.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 77179.3333 | 77179.3333 | 77179.3315
38943.5507 | 2 | 0 | 38943.5507 | 2 | 0 |  | 1416.5 | 1602.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 115819 | 115819 | 115818.9988
38943.5528 | 4 | 0 | 38943.5528 | 2302 | 0 |  | 1601 | 1787 | 0.2442 | 0 | 140.5372 | 0 | 0.002442 | 0 | 1.4054 | 0 | 0.002442 | 1.4054 | 57859.5 | 0.71156 | 57859.4976
38943.555 | 112 | 0 | 38943.555 | 2100 | 0 |  | 1786 | 1972 | 6.8376 | 0 | 128.2051 | 0 | 0.068376 | 0 | 1.2821 | 0 | 0.068376 | 1.2821 | 1969.9821 | 10.399 | 1969.9138
38943.5571 | 286 | 0 | 38943.5571 | 2001 | 0 |  | 1970.5 | 2156.5 | 17.4603 | 0 | 122.1612 | 0 | 0.1746 | 0 | 1.2216 | 0 | 0.1746 | 1.2216 | 710.6224 | 15.8611 | 710.4478
38943.5592 | 212 | 0 | 38943.5593 | 2138 | 0 |  | 2155.5 | 2341.5 | 12.9426 | 0 | 130.525 | 0 | 0.12943 | 0 | 1.3053 | 0 | 0.12943 | 1.3053 | 993.5755 | 8.4369 | 993.446
38943.5614 | 177 | 0 | 38943.5614 | 1316 | 0 |  | 2340.5 | 2526.5 | 10.8059 | 0 | 80.3419 | 0 | 0.10806 | 0 | 0.80342 | 0 | 0.10806 | 0.80342 | 1209.8192 | 76.1687 | 1209.7112
38943.5635 | 30 | 0 | 38943.5635 | 1696 | 0 |  | 2525 | 2711 | 1.8315 | 0 | 103.5409 | 0 | 0.018315 | 0 | 1.0354 | 0 | 0.018315 | 1.0354 | 7627.9333 | 36.6969 | 7627.915

## C5-F11
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 153.7473 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38943.5336 | 1 | 0 | 38943.5336 | 1 | 0 |  | -64.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38943.5357 | 1 | 0 | 38943.5357 | 1 | 0 |  | 120.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38943.5378 | 1 | 0 | 38943.5378 | 1 | 0 |  | 305 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38943.54 | 4 | 1 | 38943.54 | 3 | 0 |  | 490 | 676 | 0.2442 | 0.06105 | 0.18315 | 0 | 0.002442 | 0.0006105 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 83846 | 83846 | 251038.5956
38943.5421 | 2 | 0 | 38943.5421 | 2 | 0 |  | 674.5 | 860.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125819 | 125819 | 125818.9988
38943.5442 | 3 | 0 | 38943.5443 | 3 | 0 |  | 859.5 | 1045.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 83846 | 83846 | 83845.9982
38943.5464 | 4 | 0 | 38943.5464 | 3 | 0 |  | 1044 | 1230 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62859.5 | 83846 | 62859.4976
38943.5485 | 4 | 0 | 38943.5485 | 3 | 0 |  | 1229 | 1415 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62859.5 | 83846 | 62859.4976
38943.5507 | 4 | 0 | 38943.5507 | 3 | 0 |  | 1413.5 | 1599.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62859.5 | 83846 | 62859.4976
38943.5528 | 4 | 0 | 38943.5528 | 2445 | 0 |  | 1598.5 | 1784.5 | 0.2442 | 0 | 149.2674 | 0 | 0.002442 | 0 | 1.4927 | 0 | 0.002442 | 1.4927 | 62859.5 | 3.0012 | 62859.4976
38943.5549 | 25 | 0 | 38943.555 | 2068 | 0 |  | 1783 | 1969 | 1.5263 | 0 | 126.2515 | 0 | 0.015263 | 0 | 1.2625 | 0 | 0.015263 | 1.2625 | 9973.52 | 21.7785 | 9973.5047
38943.5571 | 207 | 0 | 38943.5571 | 2494 | 0 |  | 1968 | 2154 | 12.6374 | 0 | 152.2589 | 0 | 0.12637 | 0 | 1.5226 | 0 | 0.12637 | 1.5226 | 1116.6087 | 0.97755 | 1116.4823
38943.5592 | 196 | 0 | 38943.5592 | 2502 | 0 |  | 2152.5 | 2338.5 | 11.9658 | 0 | 152.7473 | 0 | 0.11966 | 0 | 1.5275 | 0 | 0.11966 | 1.5275 | 1184.8878 | 0.65468 | 1184.7681
38943.5614 | 156 | 0 | 38943.5614 | 1412 | 0 |  | 2337.5 | 2523.5 | 9.5238 | 0 | 86.2027 | 0 | 0.095238 | 0 | 0.86203 | 0 | 0.095238 | 0.86203 | 1514.3462 | 78.3555 | 1514.2509
38943.5635 | 37 | 0 | 38943.5635 | 895 | 0 |  | 2522.5 | 2708.5 | 2.2589 | 0 | 54.6398 | 0 | 0.022589 | 0 | 0.5464 | 0 | 0.022589 | 0.5464 | 6706.4324 | 181.3832 | 6706.4098

## C5-E10
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 158.6313 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38943.5335 | 1 | 0 | 38943.5335 | 1 | 0 |  | -67.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38943.5357 | 1 | 0 | 38943.5357 | 1 | 0 |  | 117.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38943.5378 | 1 | 0 | 38943.5378 | 1 | 0 |  | 302 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38943.5399 | 3 | 0 | 38943.54 | 1939 | 1 |  | 487 | 673 | 0.18315 | 0 | 118.3761 | 0.06105 | 0.0018315 | 0 | 1.1838 | 0.0006105 | 0.0018315 | 1.1832 | 86512.6667 | 34.0753 | 86512.6648
38943.5421 | 3 | 0 | 38943.5421 | 2 | 0 |  | 671.5 | 857.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 86512.6667 | 129819 | 86512.6648
38943.5442 | 4 | 0 | 38943.5442 | 2568 | 0 |  | 856.5 | 1042.5 | 0.2442 | 0 | 156.7766 | 0 | 0.002442 | 0 | 1.5678 | 0 | 0.002442 | 1.5678 | 64859.5 | 1.183 | 64859.4976
38943.5464 | 4 | 0 | 38943.5464 | 2478 | 0 |  | 1041.5 | 1227.5 | 0.2442 | 0 | 151.2821 | 0 | 0.002442 | 0 | 1.5128 | 0 | 0.002442 | 1.5128 | 64859.5 | 4.8579 | 64859.4976
38943.5485 | 3 | 0 | 38943.5485 | 2174 | 0 |  | 1226 | 1412 | 0.18315 | 0 | 132.7228 | 0 | 0.0018315 | 0 | 1.3272 | 0 | 0.0018315 | 1.3272 | 86512.6667 | 19.5207 | 86512.6648
38943.5506 | 3 | 0 | 38943.5506 | 2064 | 0 |  | 1411 | 1597 | 0.18315 | 0 | 126.0073 | 0 | 0.0018315 | 0 | 1.2601 | 0 | 0.0018315 | 1.2601 | 86512.6667 | 25.8905 | 86512.6648
38943.5528 | 4 | 0 | 38943.5528 | 2245 | 0 |  | 1595.5 | 1781.5 | 0.2442 | 0 | 137.0574 | 0 | 0.002442 | 0 | 1.3706 | 0 | 0.002442 | 1.3706 | 64859.5 | 15.7408 | 64859.4976
38943.5549 | 3 | 0 | 38943.5549 | 2073 | 0 |  | 1780.5 | 1966.5 | 0.18315 | 0 | 126.5568 | 0 | 0.0018315 | 0 | 1.2656 | 0 | 0.0018315 | 1.2656 | 86512.6667 | 25.3439 | 86512.6648
38943.557 | 277 | 0 | 38943.5571 | 2114 | 0 |  | 1965 | 2151 | 16.9109 | 0 | 129.0598 | 0 | 0.16911 | 0 | 1.2906 | 0 | 0.16911 | 1.2906 | 838.0433 | 22.913 | 837.8742
38943.5592 | 197 | 0 | 38943.5592 | 2250 | 0 |  | 2150 | 2336 | 12.0269 | 0 | 137.3626 | 0 | 0.12027 | 0 | 1.3736 | 0 | 0.12027 | 1.3736 | 1218.9746 | 15.4836 | 1218.8544
38943.5613 | 213 | 0 | 38943.5613 | 2071 | 0 |  | 2334.5 | 2520.5 | 13.0037 | 0 | 126.4347 | 0 | 0.13004 | 0 | 1.2643 | 0 | 0.13004 | 1.2643 | 1119.8967 | 25.465 | 1119.7667
38943.5635 | 34 | 0 | 38943.5635 | 2582 | 0 |  | 2519.5 | 2705.5 | 2.0757 | 0 | 157.6313 | 0 | 0.020757 | 0 | 1.5763 | 0 | 0.020757 | 1.5763 | 7542.2941 | 0.63439 | 7542.2734

## C5-E9
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 160.4017 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38943.5335 | 1 | 0 | 38943.5335 | 1 | 0 |  | -70 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
38943.5356 | 1 | 0 | 38943.5356 | 1 | 0 |  | 114.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
38943.5378 | 1 | 0 | 38943.5378 | 1 | 0 |  | 299.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
38943.5399 | 1 | 0 | 38943.5399 | 2381 | 0 |  | 484.5 | 670.5 | 0.06105 | 0 | 145.3602 | 0 | 0.0006105 | 0 | 1.4536 | 0 | 0.0006105 | 1.4536 | 262638 | 10.3478 | 262637.9994
38943.542 | 2 | 0 | 38943.5421 | 1589 | 0 |  | 669 | 855 | 0.1221 | 0 | 97.0085 | 0 | 0.001221 | 0 | 0.97009 | 0 | 0.001221 | 0.97009 | 131269 | 65.348 | 131268.9988
38943.5442 | 2 | 0 | 38943.5442 | 2357 | 0 |  | 853.5 | 1039.5 | 0.1221 | 0 | 143.895 | 0 | 0.001221 | 0 | 1.4389 | 0 | 0.001221 | 1.4389 | 131269 | 11.4714 | 131268.9988
38943.5463 | 2 | 0 | 38943.5463 | 2611 | 0 |  | 1038.5 | 1224.5 | 0.1221 | 0 | 159.4017 | 0 | 0.001221 | 0 | 1.594 | 0 | 0.001221 | 1.594 | 131269 | 0.62735 | 131268.9988
38943.5485 | 2 | 0 | 38943.5485 | 2421 | 0 |  | 1223.5 | 1409.5 | 0.1221 | 0 | 147.8022 | 0 | 0.001221 | 0 | 1.478 | 0 | 0.001221 | 1.478 | 131269 | 8.5246 | 131268.9988
38943.5506 | 2 | 0 | 38943.5506 | 2103 | 0 |  | 1408 | 1594 | 0.1221 | 0 | 128.3883 | 0 | 0.001221 | 0 | 1.2839 | 0 | 0.001221 | 1.2839 | 131269 | 24.9349 | 131268.9988
38943.5527 | 2 | 0 | 38943.5527 | 2065 | 0 |  | 1592.5 | 1778.5 | 0.1221 | 0 | 126.0684 | 0 | 0.001221 | 0 | 1.2607 | 0 | 0.001221 | 1.2607 | 131269 | 27.2339 | 131268.9988
38943.5549 | 3 | 0 | 38943.5549 | 2216 | 0 |  | 1777.5 | 1963.5 | 0.18315 | 0 | 135.2869 | 0 | 0.0018315 | 0 | 1.3529 | 0 | 0.0018315 | 1.3529 | 87479.3333 | 18.5641 | 87479.3315
38943.557 | 305 | 0 | 38943.557 | 2181 | 0 |  | 1962.5 | 2148.5 | 18.6203 | 0 | 133.1502 | 0 | 0.1862 | 0 | 1.3315 | 0 | 0.1862 | 1.3315 | 761.4361 | 20.4668 | 761.2499
38943.5591 | 226 | 1 | 38943.5592 | 2149 | 0 |  | 2147 | 2333 | 13.7973 | 0.06105 | 131.1966 | 0 | 0.13797 | 0.0006105 | 1.312 | 0 | 0.13736 | 1.312 | 1089.0229 | 22.2606 | 43704.8993
38943.5613 | 213 | 0 | 38943.5613 | 2005 | 0 |  | 2332 | 2518 | 13.0037 | 0 | 122.4054 | 0 | 0.13004 | 0 | 1.2241 | 0 | 0.13004 | 1.2241 | 1133.5117 | 31.0414 | 1133.3817
38943.5634 | 34 | 0 | 38943.5634 | 2268 | 0 |  | 2516.5 | 2702.5 | 2.0757 | 0 | 138.4615 | 0 | 0.020757 | 0 | 1.3846 | 0 | 0.020757 | 1.3846 | 7627.5882 | 15.8457 | 7627.5675

## C5-C6
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38943.5334 | 1 | 0 | 38943.5334 | 1 | 0 |  | -78.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5355 | 1 | 0 | 38943.5355 | 1 | 0 |  | 106 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5377 | 1 | 0 | 38943.5377 | 1 | 0 |  | 291 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5398 | 1 | 0 | 38943.5398 | 2 | 0 |  | 475.5 | 661.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38943.5419 | 1 | 0 | 38943.542 | 2 | 0 |  | 660.5 | 846.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38943.5441 | 2 | 0 | 38943.5441 | 2 | 0 |  | 845.5 | 1031.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5462 | 2 | 0 | 38943.5462 | 2 | 0 |  | 1030 | 1216 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5484 | 2 | 0 | 38943.5484 | 2 | 0 |  | 1215 | 1401 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5505 | 2 | 0 | 38943.5505 | 2 | 0 |  | 1399.5 | 1585.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5526 | 4 | 0 | 38943.5527 | 3 | 0 |  | 1584.5 | 1770.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38943.5548 | 649 | 594 | 38943.5548 | 138 | 60 |  | 1769 | 1955 | 39.6215 | 36.2637 | 8.4249 | 3.663 | 0.39621 | 0.36264 | 0.084249 | 0.03663 | 0.033578 | 0.047619 | 4584.429 | 2575.2882 | 140.9932
38943.5569 | 306 | 59 | 38943.5569 | 526 | 313 |  | 1954 | 2140 | 18.6813 | 3.602 | 32.1123 | 19.1087 | 0.18681 | 0.03602 | 0.32112 | 0.19109 | 0.15079 | 0.13004 | 750.9509 | 926.351 | 2674.0779
38943.5591 | 855 | 664 | 38943.5591 | 899 | 715 |  | 2138.5 | 2324.5 | 52.1978 | 40.5372 | 54.884 | 43.6508 | 0.52198 | 0.40537 | 0.54884 | 0.43651 | 0.11661 | 0.11233 | 959.4202 | 1108.9389 | 82.0609
38943.5612 | 982 | 755 | 38943.5612 | 999 | 819 |  | 2323.5 | 2509.5 | 59.9512 | 46.0928 | 60.989 | 50 | 0.59951 | 0.46093 | 0.60989 | 0.5 | 0.13858 | 0.10989 | 548.4869 | 3631.0816 | 48.4691
38943.5633 | 1036 | 909 | 38943.5633 | 1001 | 877 |  | 2508.5 | 2694.5 | 63.2479 | 55.4945 | 61.1111 | 53.5409 | 0.63248 | 0.55495 | 0.61111 | 0.53541 | 0.077534 | 0.075702 | 1404.6552 | 1806.2609 | 17.5144

## B4-E10
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 157.8987 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38943.5333 | 1 | 0 | 38943.5333 | 1 | 0 |  | -87 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38943.5354 | 1 | 0 | 38943.5355 | 1 | 0 |  | 98 | 284 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38943.5376 | 1 | 0 | 38943.5376 | 1 | 0 |  | 282.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38943.5397 | 4 | 0 | 38943.5397 | 1806 | 0 |  | 467.5 | 653.5 | 0.2442 | 0 | 110.2564 | 0 | 0.002442 | 0 | 1.1026 | 0 | 0.002442 | 1.1026 | 64559.5 | 43.2104 | 64559.4976
38943.5418 | 4 | 0 | 38943.5419 | 3 | 0 |  | 652 | 838 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 64559.5 | 86112.6667 | 64559.4976
38943.544 | 4 | 0 | 38943.544 | 2570 | 0 |  | 837 | 1023 | 0.2442 | 0 | 156.8987 | 0 | 0.002442 | 0 | 1.569 | 0 | 0.002442 | 1.569 | 64559.5 | 0.63735 | 64559.4976
38943.5461 | 4 | 0 | 38943.5461 | 2094 | 0 |  | 1021.5 | 1207.5 | 0.2442 | 0 | 127.8388 | 0 | 0.002442 | 0 | 1.2784 | 0 | 0.002442 | 1.2784 | 64559.5 | 23.5138 | 64559.4976
38943.5483 | 4 | 0 | 38943.5483 | 2017 | 0 |  | 1206.5 | 1392.5 | 0.2442 | 0 | 123.138 | 0 | 0.002442 | 0 | 1.2314 | 0 | 0.002442 | 1.2314 | 64559.5 | 28.2291 | 64559.4976
38943.5504 | 4 | 0 | 38943.5504 | 2569 | 0 |  | 1391 | 1577 | 0.2442 | 0 | 156.8376 | 0 | 0.002442 | 0 | 1.5684 | 0 | 0.002442 | 1.5684 | 64559.5 | 0.67653 | 64559.4976
38943.5525 | 4 | 0 | 38943.5526 | 2396 | 0 |  | 1576 | 1762 | 0.2442 | 0 | 146.2759 | 0 | 0.002442 | 0 | 1.4628 | 0 | 0.002442 | 1.4628 | 64559.5 | 7.9457 | 64559.4976
38943.5547 | 184 | 0 | 38943.5547 | 2565 | 0 |  | 1760.5 | 1946.5 | 11.2332 | 0 | 156.5934 | 0 | 0.11233 | 0 | 1.5659 | 0 | 0.11233 | 1.5659 | 1305.6413 | 0.83353 | 1305.529
38943.5568 | 1978 | 0 | 38943.5568 | 1995 | 0 |  | 1945.5 | 2131.5 | 120.757 | 0 | 121.7949 | 0 | 1.2076 | 0 | 1.2179 | 0 | 1.2076 | 1.2179 | 30.7573 | 29.6431 | 29.5498
38943.559 | 2307 | 2 | 38943.559 | 2049 | 0 |  | 2130.5 | 2316.5 | 140.8425 | 0.1221 | 125.0916 | 0 | 1.4084 | 0.001221 | 1.2509 | 0 | 1.4072 | 1.2509 | 12.1608 | 26.2265 | 2881.6041
38943.5611 | 2067 | 0 | 38943.5611 | 1993 | 0 |  | 2315 | 2501 | 126.1905 | 0 | 121.6728 | 0 | 1.2619 | 0 | 1.2167 | 0 | 1.2619 | 1.2167 | 25.1272 | 29.7732 | 23.8653
38943.5632 | 2179 | 0 | 38943.5633 | 2296 | 0 |  | 2500 | 2686 | 133.0281 | 0 | 140.1709 | 0 | 1.3303 | 0 | 1.4017 | 0 | 1.3303 | 1.4017 | 18.6957 | 12.6472 | 17.3655

## B4-E9
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 157.8376 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38943.5333 | 1 | 0 | 38943.5333 | 1 | 0 |  | -89.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38943.5354 | 1 | 0 | 38943.5354 | 1 | 0 |  | 95 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38943.5375 | 1 | 0 | 38943.5376 | 1 | 0 |  | 280 | 466 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38943.5397 | 1 | 0 | 38943.5397 | 2035 | 0 |  | 464.5 | 650.5 | 0.06105 | 0 | 124.2369 | 0 | 0.0006105 | 0 | 1.2424 | 0 | 0.0006105 | 1.2424 | 258438 | 27.0457 | 258437.9994
38943.5418 | 1 | 0 | 38943.5418 | 2384 | 0 |  | 649.5 | 835.5 | 0.06105 | 0 | 145.5433 | 0 | 0.0006105 | 0 | 1.4554 | 0 | 0.0006105 | 1.4554 | 258438 | 8.4471 | 258437.9994
38943.5439 | 1 | 0 | 38943.544 | 2536 | 0 |  | 834 | 1020 | 0.06105 | 0 | 154.823 | 0 | 0.0006105 | 0 | 1.5482 | 0 | 0.0006105 | 1.5482 | 258438 | 1.9472 | 258437.9994
38943.5461 | 1 | 0 | 38943.5461 | 2209 | 0 |  | 1019 | 1205 | 0.06105 | 0 | 134.8596 | 0 | 0.0006105 | 0 | 1.3486 | 0 | 0.0006105 | 1.3486 | 258438 | 17.0385 | 258437.9994
38943.5482 | 2 | 0 | 38943.5482 | 2383 | 0 |  | 1203.5 | 1389.5 | 0.1221 | 0 | 145.4823 | 0 | 0.001221 | 0 | 1.4548 | 0 | 0.001221 | 1.4548 | 129169 | 8.4927 | 129168.9988
38943.5504 | 2 | 0 | 38943.5504 | 2286 | 0 |  | 1388.5 | 1574.5 | 0.1221 | 0 | 139.5604 | 0 | 0.001221 | 0 | 1.3956 | 0 | 0.001221 | 1.3956 | 129169 | 13.0962 | 129168.9988
38943.5525 | 2 | 0 | 38943.5525 | 2013 | 0 |  | 1573.5 | 1759.5 | 0.1221 | 0 | 122.8938 | 0 | 0.001221 | 0 | 1.2289 | 0 | 0.001221 | 1.2289 | 129169 | 28.4342 | 129168.9988
38943.5546 | 34 | 0 | 38943.5547 | 2206 | 0 |  | 1758 | 1944 | 2.0757 | 0 | 134.6764 | 0 | 0.020757 | 0 | 1.3468 | 0 | 0.020757 | 1.3468 | 7504.0588 | 17.1976 | 7504.0381
38943.5568 | 2195 | 0 | 38943.5568 | 2569 | 0 |  | 1942.5 | 2128.5 | 134.0049 | 0 | 156.8376 | 0 | 1.34 | 0 | 1.5684 | 0 | 1.34 | 1.5684 | 17.785 | 0.6376 | 16.4449
38943.5589 | 1640 | 2 | 38943.5589 | 2286 | 0 |  | 2127.5 | 2313.5 | 100.1221 | 0.1221 | 139.5604 | 0 | 1.0012 | 0.001221 | 1.3956 | 0 | 1 | 1.3956 | 58.2587 | 13.0962 | 5462.0424
38943.5611 | 2450 | 0 | 38943.5611 | 2010 | 0 |  | 2312.5 | 2498.5 | 149.5726 | 0 | 122.7106 | 0 | 1.4957 | 0 | 1.2271 | 0 | 1.4957 | 1.2271 | 5.5257 | 28.6259 | 4.03
38943.5632 | 2298 | 0 | 38943.5632 | 2222 | 0 |  | 2497 | 2683 | 140.293 | 0 | 135.6532 | 0 | 1.4029 | 0 | 1.3565 | 0 | 1.4029 | 1.3565 | 12.5057 | 16.3537 | 11.1027

## B4-D8
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 152.6484 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38943.5332 | 1 | 0 | 38943.5332 | 1 | 0 |  | -92.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38943.5354 | 1 | 0 | 38943.5354 | 1 | 0 |  | 92.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38943.5375 | 1 | 0 | 38943.5375 | 1 | 0 |  | 277 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38943.5396 | 1 | 0 | 38943.5397 | 1 | 0 |  | 461.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38943.5418 | 1 | 0 | 38943.5418 | 1 | 0 |  | 646.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38943.5439 | 2 | 0 | 38943.5439 | 1 | 0 |  | 831.5 | 1017.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124919 | 249938 | 124918.9988
38943.5461 | 2 | 0 | 38943.5461 | 2 | 0 |  | 1016 | 1202 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124919 | 124919 | 124918.9988
38943.5482 | 2 | 0 | 38943.5482 | 2 | 0 |  | 1201 | 1387 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124919 | 124919 | 124918.9988
38943.5503 | 2 | 0 | 38943.5503 | 2 | 1 |  | 1385.5 | 1571.5 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 124919 | 249938 | 124918.9988
38943.5525 | 2 | 0 | 38943.5525 | 115 | 0 |  | 1570.5 | 1756.5 | 0.1221 | 0 | 7.0208 | 0 | 0.001221 | 0 | 0.070208 | 0 | 0.001221 | 0.070208 | 124919 | 2074.2435 | 124918.9988
38943.5546 | 1835 | 0 | 38943.5546 | 1925 | 0 |  | 1755.5 | 1941.5 | 112.0269 | 0 | 117.5214 | 0 | 1.1203 | 0 | 1.1752 | 0 | 1.1203 | 1.1752 | 36.2605 | 29.8899 | 35.1402
38943.5567 | 2290 | 0 | 38943.5568 | 2085 | 0 |  | 1940 | 2126 | 139.8046 | 0 | 127.2894 | 0 | 1.398 | 0 | 1.2729 | 0 | 1.398 | 1.2729 | 9.1869 | 19.9223 | 7.7889
38943.5589 | 350 | 0 | 38943.5589 | 1715 | 0 |  | 2124.5 | 2310.5 | 21.3675 | 0 | 104.7009 | 0 | 0.21368 | 0 | 1.047 | 0 | 0.21368 | 1.047 | 614.3943 | 45.7948 | 614.1806
38943.561 | 2484 | 0 | 38943.561 | 1311 | 0 |  | 2309.5 | 2495.5 | 151.6484 | 0 | 80.0366 | 0 | 1.5165 | 0 | 0.80037 | 0 | 1.5165 | 0.80037 | 0.65942 | 90.7231 | 0.85706
38943.5632 | 2176 | 0 | 38943.5632 | 1043 | 0 |  | 2494.5 | 2680.5 | 132.8449 | 0 | 63.6752 | 0 | 1.3284 | 0 | 0.63675 | 0 | 1.3284 | 0.63675 | 14.9072 | 139.7296 | 13.5787

## B4-D7
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 152.0989 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38943.5332 | 1 | 0 | 38943.5332 | 1 | 0 |  | -95.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38943.5353 | 1 | 0 | 38943.5353 | 1 | 0 |  | 89.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38943.5375 | 1 | 0 | 38943.5375 | 1 | 0 |  | 274.5 | 460.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38943.5396 | 2 | 0 | 38943.5396 | 2 | 0 |  | 459 | 645 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124469 | 124469 | 124468.9988
38943.5417 | 2 | 0 | 38943.5418 | 1 | 0 |  | 643.5 | 829.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124469 | 249038 | 124468.9988
38943.5439 | 2 | 0 | 38943.5439 | 1 | 0 |  | 828.5 | 1014.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124469 | 249038 | 124468.9988
38943.546 | 2 | 0 | 38943.546 | 2 | 0 |  | 1013.5 | 1199.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124469 | 124469 | 124468.9988
38943.5482 | 1 | 0 | 38943.5482 | 2 | 0 |  | 1198 | 1384 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249038 | 124469 | 249037.9994
38943.5503 | 2 | 0 | 38943.5503 | 2 | 0 |  | 1383 | 1569 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124469 | 124469 | 124468.9988
38943.5524 | 2 | 0 | 38943.5525 | 76 | 0 |  | 1567.5 | 1753.5 | 0.1221 | 0 | 4.6398 | 0 | 0.001221 | 0 | 0.046398 | 0 | 0.001221 | 0.046398 | 124469 | 3178.1316 | 124468.9988
38943.5546 | 129 | 0 | 38943.5546 | 2132 | 0 |  | 1752.5 | 1938.5 | 7.8755 | 0 | 130.1587 | 0 | 0.078755 | 0 | 1.3016 | 0 | 0.078755 | 1.3016 | 1831.3023 | 16.8565 | 1831.2236
38943.5567 | 2028 | 0 | 38943.5567 | 1922 | 0 |  | 1937.5 | 2123.5 | 123.8095 | 0 | 117.3382 | 0 | 1.2381 | 0 | 1.1734 | 0 | 1.2381 | 1.1734 | 22.8491 | 29.6243 | 21.611
38943.5589 | 1464 | 0 | 38943.5589 | 2239 | 0 |  | 2122 | 2308 | 89.3773 | 0 | 136.6911 | 0 | 0.89377 | 0 | 1.3669 | 0 | 0.89377 | 1.3669 | 70.1762 | 11.272 | 69.2825
38943.561 | 2475 | 0 | 38943.561 | 1414 | 0 |  | 2306.5 | 2492.5 | 151.0989 | 0 | 86.3248 | 0 | 1.511 | 0 | 0.86325 | 0 | 1.511 | 0.86325 | 0.66182 | 76.1938 | 0.84917
38943.5631 | 2318 | 0 | 38943.5631 | 1096 | 0 |  | 2491.5 | 2677.5 | 141.514 | 0 | 66.9109 | 0 | 1.4151 | 0 | 0.66911 | 0 | 1.4151 | 0.66911 | 7.4797 | 127.3157 | 6.0646

## B4-C6
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 147.5812 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38943.5332 | 1 | 0 | 38943.5332 | 1 | 0 |  | -98 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
38943.5353 | 1 | 0 | 38943.5353 | 1 | 0 |  | 86.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
38943.5374 | 1 | 0 | 38943.5375 | 1 | 0 |  | 271.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241638 | 241638 | 241637.9994
38943.5396 | 2 | 0 | 38943.5396 | 2 | 0 |  | 456 | 642 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 120769 | 120769 | 120768.9988
38943.5417 | 2 | 0 | 38943.5417 | 1 | 0 |  | 641 | 827 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 120769 | 241638 | 120768.9988
38943.5439 | 2 | 0 | 38943.5439 | 2 | 0 |  | 825.5 | 1011.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 120769 | 120769 | 120768.9988
38943.546 | 2 | 0 | 38943.546 | 2 | 0 |  | 1010.5 | 1196.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 120769 | 120769 | 120768.9988
38943.5481 | 2 | 0 | 38943.5481 | 2 | 0 |  | 1195.5 | 1381.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 120769 | 120769 | 120768.9988
38943.5503 | 2 | 0 | 38943.5503 | 2 | 0 |  | 1380 | 1566 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 120769 | 120769 | 120768.9988
38943.5524 | 2 | 0 | 38943.5524 | 2 | 0 |  | 1565 | 1751 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 120769 | 120769 | 120768.9988
38943.5545 | 1323 | 0 | 38943.5546 | 391 | 0 |  | 1749.5 | 1935.5 | 80.7692 | 0 | 23.8706 | 0 | 0.80769 | 0 | 0.23871 | 0 | 0.80769 | 0.23871 | 82.7196 | 518.2558 | 81.9119
38943.5567 | 2093 | 0 | 38943.5567 | 342 | 0 |  | 1934.5 | 2120.5 | 127.7778 | 0 | 20.8791 | 0 | 1.2778 | 0 | 0.20879 | 0 | 1.2778 | 0.20879 | 15.4983 | 606.8363 | 14.2205
38943.5588 | 809 | 0 | 38943.5588 | 151 | 0 |  | 2119 | 2305 | 49.3895 | 0 | 9.2186 | 0 | 0.49389 | 0 | 0.092186 | 0 | 0.49389 | 0.092186 | 198.8109 | 1500.9139 | 198.317
38943.561 | 2401 | 0 | 38943.561 | 262 | 0 |  | 2304 | 2490 | 146.5812 | 0 | 15.9951 | 0 | 1.4658 | 0 | 0.15995 | 0 | 1.4658 | 0.15995 | 0.68222 | 822.6641 | 0.7836
38943.5631 | 2235 | 0 | 38943.5631 | 49 | 0 |  | 2488.5 | 2674.5 | 136.4469 | 0 | 2.9915 | 0 | 1.3645 | 0 | 0.029915 | 0 | 1.3645 | 0.029915 | 8.1602 | 4833.4286 | 6.7957

## B4-C5
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 157.044 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38943.5331 | 1 | 0 | 38943.5331 | 1 | 0 |  | -101 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38943.5353 | 1 | 0 | 38943.5353 | 1 | 0 |  | 84 | 270 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38943.5374 | 1 | 0 | 38943.5374 | 1 | 0 |  | 268.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38943.5395 | 2 | 0 | 38943.5396 | 2 | 0 |  | 453.5 | 639.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128519 | 128519 | 128518.9988
38943.5417 | 2 | 0 | 38943.5417 | 1 | 0 |  | 638.5 | 824.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128519 | 257138 | 128518.9988
38943.5438 | 2 | 0 | 38943.5438 | 2 | 0 |  | 823 | 1009 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128519 | 128519 | 128518.9988
38943.546 | 2 | 0 | 38943.546 | 2 | 0 |  | 1007.5 | 1193.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128519 | 128519 | 128518.9988
38943.5481 | 2 | 0 | 38943.5481 | 2 | 0 |  | 1192.5 | 1378.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128519 | 128519 | 128518.9988
38943.5502 | 2 | 0 | 38943.5503 | 2 | 0 |  | 1377.5 | 1563.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128519 | 128519 | 128518.9988
38943.5524 | 4 | 0 | 38943.5524 | 3 | 0 |  | 1562 | 1748 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 64209.5 | 85646 | 64209.4976
38943.5545 | 890 | 0 | 38943.5545 | 337 | 0 |  | 1747 | 1933 | 54.3346 | 0 | 20.5739 | 0 | 0.54335 | 0 | 0.20574 | 0 | 0.54335 | 0.20574 | 189.0315 | 663.3175 | 188.4881
38943.5567 | 2022 | 0 | 38943.5567 | 370 | 0 |  | 1931.5 | 2117.5 | 123.4432 | 0 | 22.5885 | 0 | 1.2344 | 0 | 0.22589 | 0 | 1.2344 | 0.22589 | 27.2196 | 595.2378 | 25.9852
38943.5588 | 2165 | 0 | 38943.5588 | 180 | 0 |  | 2116.5 | 2302.5 | 132.1734 | 0 | 10.989 | 0 | 1.3217 | 0 | 0.10989 | 0 | 1.3217 | 0.10989 | 18.8166 | 1329.1 | 17.4949
38943.5609 | 2556 | 0 | 38943.5609 | 271 | 0 |  | 2301 | 2487 | 156.044 | 0 | 16.5446 | 0 | 1.5604 | 0 | 0.16545 | 0 | 1.5604 | 0.16545 | 0.64085 | 849.2177 | 0.91959
38943.5631 | 2367 | 0 | 38943.5631 | 54 | 0 |  | 2486 | 2672 | 144.5055 | 0 | 3.2967 | 0 | 1.4451 | 0 | 0.032967 | 0 | 1.4451 | 0.032967 | 8.6768 | 4663.6667 | 7.2318

## B3-E10
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 158.326 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38943.533 | 1 | 0 | 38943.533 | 1 | 0 |  | -109.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38943.5352 | 1 | 0 | 38943.5352 | 1 | 0 |  | 75.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38943.5373 | 1 | 0 | 38943.5373 | 1 | 0 |  | 260 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38943.5394 | 4 | 0 | 38943.5395 | 1763 | 0 |  | 445 | 631 | 0.2442 | 0 | 107.6313 | 0 | 0.002442 | 0 | 1.0763 | 0 | 0.002442 | 1.0763 | 64734.5 | 47.1004 | 64734.4976
38943.5416 | 4 | 0 | 38943.5416 | 2 | 0 |  | 629.5 | 815.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 64734.5 | 129569 | 64734.4976
38943.5437 | 4 | 0 | 38943.5437 | 2563 | 0 |  | 814.5 | 1000.5 | 0.2442 | 0 | 156.4713 | 0 | 0.002442 | 0 | 1.5647 | 0 | 0.002442 | 1.5647 | 64734.5 | 1.1853 | 64734.4976
38943.5459 | 4 | 0 | 38943.5459 | 2073 | 0 |  | 999.5 | 1185.5 | 0.2442 | 0 | 126.5568 | 0 | 0.002442 | 0 | 1.2656 | 0 | 0.002442 | 1.2656 | 64734.5 | 25.1027 | 64734.4976
38943.548 | 4 | 0 | 38943.548 | 2577 | 0 |  | 1184 | 1370 | 0.2442 | 0 | 157.326 | 0 | 0.002442 | 0 | 1.5733 | 0 | 0.002442 | 1.5733 | 64734.5 | 0.63562 | 64734.4976
38943.5501 | 4 | 0 | 38943.5502 | 2258 | 0 |  | 1368.5 | 1554.5 | 0.2442 | 0 | 137.851 | 0 | 0.002442 | 0 | 1.3785 | 0 | 0.002442 | 1.3785 | 64734.5 | 14.853 | 64734.4976
38943.5523 | 4 | 0 | 38943.5523 | 2121 | 0 |  | 1553.5 | 1739.5 | 0.2442 | 0 | 129.4872 | 0 | 0.002442 | 0 | 1.2949 | 0 | 0.002442 | 1.2949 | 64734.5 | 22.2716 | 64734.4976
38943.5544 | 2031 | 0 | 38943.5544 | 2234 | 0 |  | 1738.5 | 1924.5 | 123.9927 | 0 | 136.3858 | 0 | 1.2399 | 0 | 1.3639 | 0 | 1.2399 | 1.3639 | 27.6898 | 16.0868 | 26.4499
38943.5566 | 1973 | 0 | 38943.5566 | 2231 | 0 |  | 1923 | 2109 | 120.4518 | 0 | 136.2027 | 0 | 1.2045 | 0 | 1.362 | 0 | 1.2045 | 1.362 | 31.4435 | 16.2429 | 30.239
38943.5587 | 2124 | 0 | 38943.5587 | 2233 | 0 |  | 2108 | 2294 | 129.6703 | 0 | 136.3248 | 0 | 1.2967 | 0 | 1.3632 | 0 | 1.2967 | 1.3632 | 22.0989 | 16.1388 | 20.8022
38943.5608 | 2103 | 0 | 38943.5608 | 2338 | 0 |  | 2292.5 | 2478.5 | 128.3883 | 0 | 142.735 | 0 | 1.2839 | 0 | 1.4274 | 0 | 1.2839 | 1.4274 | 23.3181 | 10.923 | 22.0342
38943.563 | 2197 | 0 | 38943.563 | 2407 | 0 |  | 2477.5 | 2663.5 | 134.127 | 0 | 146.9475 | 0 | 1.3413 | 0 | 1.4695 | 0 | 1.3413 | 1.4695 | 18.0419 | 7.7432 | 16.7006

## B3-E9
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 158.6313 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38943.533 | 1 | 0 | 38943.533 | 1 | 0 |  | -112 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38943.5351 | 1 | 0 | 38943.5352 | 1 | 0 |  | 72.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38943.5373 | 2 | 0 | 38943.5373 | 1 | 0 |  | 257.5 | 443.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129819 | 259738 | 129818.9988
38943.5394 | 1 | 0 | 38943.5394 | 1876 | 0 |  | 442 | 628 | 0.06105 | 0 | 114.5299 | 0 | 0.0006105 | 0 | 1.1453 | 0 | 0.0006105 | 1.1453 | 259738 | 38.5064 | 259737.9994
38943.5416 | 2 | 0 | 38943.5416 | 2198 | 0 |  | 627 | 813 | 0.1221 | 0 | 134.188 | 0 | 0.001221 | 0 | 1.3419 | 0 | 0.001221 | 1.3419 | 129819 | 18.2157 | 129818.9988
38943.5437 | 1 | 0 | 38943.5437 | 2251 | 0 |  | 811.5 | 997.5 | 0.06105 | 0 | 137.4237 | 0 | 0.0006105 | 0 | 1.3742 | 0 | 0.0006105 | 1.3742 | 259738 | 15.4323 | 259737.9994
38943.5458 | 2 | 0 | 38943.5458 | 2353 | 0 |  | 996.5 | 1182.5 | 0.1221 | 0 | 143.6508 | 0 | 0.001221 | 0 | 1.4365 | 0 | 0.001221 | 1.4365 | 129819 | 10.4284 | 129818.9988
38943.548 | 2 | 0 | 38943.548 | 2294 | 0 |  | 1181.5 | 1367.5 | 0.1221 | 0 | 140.0488 | 0 | 0.001221 | 0 | 1.4005 | 0 | 0.001221 | 1.4005 | 129819 | 13.2685 | 129818.9988
38943.5501 | 2 | 0 | 38943.5501 | 2077 | 0 |  | 1366 | 1552 | 0.1221 | 0 | 126.801 | 0 | 0.001221 | 0 | 1.268 | 0 | 0.001221 | 1.268 | 129819 | 25.1026 | 129818.9988
38943.5522 | 2 | 0 | 38943.5523 | 2071 | 0 |  | 1551 | 1737 | 0.1221 | 0 | 126.4347 | 0 | 0.001221 | 0 | 1.2643 | 0 | 0.001221 | 1.2643 | 129819 | 25.465 | 129818.9988
38943.5544 | 2459 | 0 | 38943.5544 | 2462 | 0 |  | 1735.5 | 1921.5 | 150.1221 | 0 | 150.3053 | 0 | 1.5012 | 0 | 1.5031 | 0 | 1.5012 | 1.5031 | 5.6682 | 5.5394 | 4.1669
38943.5565 | 2071 | 0 | 38943.5565 | 2577 | 0 |  | 1920.5 | 2106.5 | 126.4347 | 0 | 157.326 | 0 | 1.2643 | 0 | 1.5733 | 0 | 1.2643 | 1.5733 | 25.465 | 0.82965 | 24.2006
38943.5587 | 2497 | 0 | 38943.5587 | 2564 | 0 |  | 2105 | 2291 | 152.442 | 0 | 156.5324 | 0 | 1.5244 | 0 | 1.5653 | 0 | 1.5244 | 1.5653 | 4.0601 | 1.3409 | 2.5357
38943.5608 | 2516 | 0 | 38943.5608 | 2582 | 0 |  | 2290 | 2476 | 153.602 | 0 | 157.6313 | 0 | 1.536 | 0 | 1.5763 | 0 | 1.536 | 1.5763 | 3.2742 | 0.63439 | 1.7382
38943.5629 | 2298 | 0 | 38943.563 | 2281 | 0 |  | 2474.5 | 2660.5 | 140.293 | 0 | 139.2552 | 0 | 1.4029 | 0 | 1.3926 | 0 | 1.4029 | 1.3926 | 13.0714 | 13.9141 | 11.6684

## B3-D8
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 155.7619 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38943.533 | 1 | 0 | 38943.533 | 1 | 0 |  | -115 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38943.5351 | 1 | 0 | 38943.5351 | 1 | 0 |  | 70 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38943.5372 | 1 | 0 | 38943.5373 | 1 | 0 |  | 254.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38943.5394 | 1 | 0 | 38943.5394 | 1 | 0 |  | 439.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38943.5415 | 1 | 0 | 38943.5415 | 1 | 0 |  | 624 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38943.5437 | 2 | 0 | 38943.5437 | 1 | 0 |  | 809 | 995 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127469 | 255038 | 127468.9988
38943.5458 | 2 | 0 | 38943.5458 | 2 | 0 |  | 993.5 | 1179.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 127469 | 127469 | 127468.9988
38943.5479 | 1 | 0 | 38943.548 | 2 | 0 |  | 1178.5 | 1364.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255038 | 127469 | 255037.9994
38943.5501 | 2 | 0 | 38943.5501 | 2 | 0 |  | 1363.5 | 1549.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 127469 | 127469 | 127468.9988
38943.5522 | 2 | 0 | 38943.5522 | 8 | 0 |  | 1548 | 1734 | 0.1221 | 0 | 0.4884 | 0 | 0.001221 | 0 | 0.004884 | 0 | 0.001221 | 0.004884 | 127469 | 31792.25 | 127468.9988
38943.5544 | 2535 | 0 | 38943.5544 | 1837 | 0 |  | 1733 | 1919 | 154.7619 | 0 | 112.149 | 0 | 1.5476 | 0 | 1.1215 | 0 | 1.5476 | 1.1215 | 0.64615 | 38.8884 | 0.90147
38943.5565 | 2533 | 0 | 38943.5565 | 2272 | 0 |  | 1917.5 | 2103.5 | 154.6398 | 0 | 138.7057 | 0 | 1.5464 | 0 | 1.3871 | 0 | 1.5464 | 1.3871 | 0.72562 | 12.2967 | 0.82078
38943.5586 | 2245 | 0 | 38943.5586 | 1862 | 0 |  | 2102.5 | 2288.5 | 137.0574 | 0 | 113.6752 | 0 | 1.3706 | 0 | 1.1368 | 0 | 1.3706 | 1.1368 | 13.6472 | 37.0236 | 12.2766
38943.5608 | 1999 | 0 | 38943.5608 | 1559 | 0 |  | 2287 | 2473 | 122.0391 | 0 | 95.177 | 0 | 1.2204 | 0 | 0.95177 | 0 | 1.2204 | 0.95177 | 27.6328 | 63.6549 | 26.4124
38943.5629 | 2204 | 0 | 38943.5629 | 1172 | 0 |  | 2472 | 2658 | 134.5543 | 0 | 71.5507 | 0 | 1.3455 | 0 | 0.71551 | 0 | 1.3455 | 0.71551 | 15.7613 | 117.6945 | 14.4158

## B3-D7
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 153.442 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38943.5329 | 1 | 0 | 38943.533 | 1 | 0 |  | -117.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38943.5351 | 1 | 0 | 38943.5351 | 1 | 0 |  | 67 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38943.5372 | 1 | 0 | 38943.5372 | 1 | 0 |  | 251.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38943.5394 | 1 | 0 | 38943.5394 | 1 | 0 |  | 436.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38943.5415 | 1 | 0 | 38943.5415 | 2 | 0 |  | 621.5 | 807.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 251238 | 125569 | 251237.9994
38943.5436 | 2 | 0 | 38943.5436 | 2 | 0 |  | 806 | 992 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125569 | 125569 | 125568.9988
38943.5458 | 2 | 0 | 38943.5458 | 2 | 0 |  | 991 | 1177 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125569 | 125569 | 125568.9988
38943.5479 | 2 | 0 | 38943.5479 | 2 | 0 |  | 1175.5 | 1361.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125569 | 125569 | 125568.9988
38943.55 | 2 | 0 | 38943.5501 | 2 | 0 |  | 1360.5 | 1546.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125569 | 125569 | 125568.9988
38943.5522 | 2 | 0 | 38943.5522 | 33 | 0 |  | 1545 | 1731 | 0.1221 | 0 | 2.0147 | 0 | 0.001221 | 0 | 0.020147 | 0 | 0.001221 | 0.020147 | 125569 | 7516.303 | 125568.9988
38943.5543 | 2497 | 0 | 38943.5543 | 2112 | 0 |  | 1730 | 1916 | 152.442 | 0 | 128.9377 | 0 | 1.5244 | 0 | 1.2894 | 0 | 1.5244 | 1.2894 | 0.65599 | 19.0047 | 0.86843
38943.5565 | 2198 | 0 | 38943.5565 | 2321 | 0 |  | 1914.5 | 2100.5 | 134.188 | 0 | 141.6972 | 0 | 1.3419 | 0 | 1.417 | 0 | 1.3419 | 1.417 | 14.3485 | 8.2887 | 13.0066
38943.5586 | 2185 | 0 | 38943.5586 | 2239 | 0 |  | 2099.5 | 2285.5 | 133.3944 | 0 | 136.6911 | 0 | 1.3339 | 0 | 1.3669 | 0 | 1.3339 | 1.3669 | 15.0288 | 12.2546 | 13.6949
38943.5607 | 2325 | 0 | 38943.5608 | 1878 | 0 |  | 2284.5 | 2470.5 | 141.9414 | 0 | 114.652 | 0 | 1.4194 | 0 | 1.1465 | 0 | 1.4194 | 1.1465 | 8.1024 | 33.8328 | 6.683
38943.5629 | 2190 | 0 | 38943.5629 | 1196 | 0 |  | 2469 | 2655 | 133.6996 | 0 | 73.0159 | 0 | 1.337 | 0 | 0.73016 | 0 | 1.337 | 0.73016 | 14.7662 | 110.1488 | 13.4292

## B3-C6
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 156.4335 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38943.5329 | 1 | 0 | 38943.5329 | 1 | 0 |  | -120.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38943.535 | 1 | 0 | 38943.5351 | 1 | 0 |  | 64.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38943.5372 | 1 | 0 | 38943.5372 | 1 | 0 |  | 249 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38943.5393 | 1 | 0 | 38943.5393 | 1 | 0 |  | 434 | 620 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38943.5415 | 1 | 0 | 38943.5415 | 2 | 0 |  | 618.5 | 804.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 256138 | 128019 | 256137.9994
38943.5436 | 2 | 0 | 38943.5436 | 2 | 0 |  | 803.5 | 989.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128019 | 128019 | 128018.9988
38943.5457 | 2 | 0 | 38943.5458 | 2 | 0 |  | 988 | 1174 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128019 | 128019 | 128018.9988
38943.5479 | 2 | 0 | 38943.5479 | 2 | 0 |  | 1173 | 1359 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128019 | 128019 | 128018.9988
38943.55 | 2 | 0 | 38943.55 | 2 | 0 |  | 1357.5 | 1543.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128019 | 128019 | 128018.9988
38943.5522 | 2 | 0 | 38943.5522 | 2 | 0 |  | 1542.5 | 1728.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128019 | 128019 | 128018.9988
38943.5543 | 2546 | 0 | 38943.5543 | 114 | 0 |  | 1727.5 | 1913.5 | 155.4335 | 0 | 6.9597 | 0 | 1.5543 | 0 | 0.069597 | 0 | 1.5543 | 0.069597 | 0.64336 | 2147.7018 | 0.91097
38943.5564 | 2076 | 0 | 38943.5564 | 373 | 0 |  | 1912 | 2098 | 126.7399 | 0 | 22.7717 | 0 | 1.2674 | 0 | 0.22772 | 0 | 1.2674 | 0.22772 | 23.4287 | 586.9651 | 22.1613
38943.5586 | 2510 | 0 | 38943.5586 | 154 | 0 |  | 2096.5 | 2282.5 | 153.2357 | 0 | 9.4017 | 0 | 1.5324 | 0 | 0.094017 | 0 | 1.5324 | 0.094017 | 2.0869 | 1563.8831 | 0.5545
38943.5607 | 2222 | 0 | 38943.5607 | 262 | 0 |  | 2281.5 | 2467.5 | 135.6532 | 0 | 15.9951 | 0 | 1.3565 | 0 | 0.15995 | 0 | 1.3565 | 0.15995 | 15.3186 | 878.0076 | 13.9621
38943.5628 | 2194 | 0 | 38943.5629 | 49 | 0 |  | 2466.5 | 2652.5 | 133.9438 | 0 | 2.9915 | 0 | 1.3394 | 0 | 0.029915 | 0 | 1.3394 | 0.029915 | 16.7903 | 5129.3469 | 15.4509

## B3-C5
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38943.5329 | 1 | 0 | 38943.5329 | 1 | 0 |  | -123.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.535 | 1 | 0 | 38943.535 | 1 | 0 |  | 61.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5372 | 1 | 0 | 38943.5372 | 1 | 0 |  | 246.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5393 | 1 | 0 | 38943.5393 | 1 | 0 |  | 431 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5414 | 1 | 0 | 38943.5414 | 2 | 0 |  | 615.5 | 801.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38943.5436 | 2 | 0 | 38943.5436 | 1 | 0 |  | 800.5 | 986.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38943.5457 | 2 | 0 | 38943.5457 | 2 | 0 |  | 985.5 | 1171.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5478 | 2 | 0 | 38943.5479 | 2 | 0 |  | 1170 | 1356 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.55 | 2 | 0 | 38943.55 | 1 | 0 |  | 1355 | 1541 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38943.5521 | 2 | 0 | 38943.5521 | 1 | 0 |  | 1539.5 | 1725.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38943.5543 | 1990 | 0 | 38943.5543 | 227 | 0 |  | 1724.5 | 1910.5 | 121.4896 | 0 | 13.8584 | 0 | 1.2149 | 0 | 0.13858 | 0 | 1.2149 | 0.13858 | 6.1819 | 830.8458 | 4.967
38943.5564 | 2092 | 0 | 38943.5564 | 320 | 0 |  | 1909 | 2095 | 127.7167 | 0 | 19.536 | 0 | 1.2772 | 0 | 0.19536 | 0 | 1.2772 | 0.19536 | 1.0048 | 560.3188 | 0.27239
38943.5585 | 2028 | 0 | 38943.5586 | 218 | 0 |  | 2094 | 2280 | 123.8095 | 0 | 13.3089 | 0 | 1.2381 | 0 | 0.13309 | 0 | 1.2381 | 0.13309 | 4.1923 | 869.2752 | 2.9542
38943.5607 | 2047 | 0 | 38943.5607 | 265 | 0 |  | 2278.5 | 2464.5 | 124.9695 | 0 | 16.1783 | 0 | 1.2497 | 0 | 0.16178 | 0 | 1.2497 | 0.16178 | 3.2252 | 697.366 | 1.9755
38943.5628 | 2085 | 0 | 38943.5628 | 80 | 0 |  | 2463.5 | 2649.5 | 127.2894 | 0 | 4.884 | 0 | 1.2729 | 0 | 0.04884 | 0 | 1.2729 | 0.04884 | 1.3439 | 2541.275 | 0.070991

## B3-B4
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 139.4005 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38943.5328 | 1 | 0 | 38943.5329 | 1 | 0 |  | -126 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38943.535 | 1 | 0 | 38943.535 | 1 | 0 |  | 58.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38943.5371 | 1 | 0 | 38943.5371 | 1 | 0 |  | 243.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38943.5393 | 1 | 0 | 38943.5393 | 1 | 0 |  | 428.5 | 614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38943.5414 | 2 | 0 | 38943.5414 | 1 | 0 |  | 613 | 799 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114069 | 228238 | 114068.9988
38943.5435 | 2 | 0 | 38943.5435 | 2 | 0 |  | 797.5 | 983.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114069 | 114069 | 114068.9988
38943.5457 | 3 | 0 | 38943.5457 | 2 | 0 |  | 982.5 | 1168.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76012.6667 | 114069 | 76012.6648
38943.5478 | 2 | 0 | 38943.5478 | 2 | 0 |  | 1167.5 | 1353.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114069 | 114069 | 114068.9988
38943.5499 | 2 | 0 | 38943.55 | 2 | 0 |  | 1352 | 1538 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114069 | 114069 | 114068.9988
38943.5521 | 2 | 0 | 38943.5521 | 2 | 0 |  | 1537 | 1723 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114069 | 114069 | 114068.9988
38943.5542 | 109 | 86 | 38943.5542 | 948 | 102 |  | 1721.5 | 1907.5 | 6.6545 | 5.2503 | 57.8755 | 6.2271 | 0.066545 | 0.052503 | 0.57875 | 0.062271 | 0.014042 | 0.51648 | 6885.5755 | 1002.4748 | 2208.0854
38943.5564 | 2267 | 2 | 38943.5564 | 2069 | 0 |  | 1906.5 | 2092.5 | 138.4005 | 0.1221 | 126.3126 | 0 | 1.384 | 0.001221 | 1.2631 | 0 | 1.3828 | 1.2631 | 0.72939 | 10.3615 | 67.5048
38943.5585 | 2088 | 0 | 38943.5585 | 1946 | 0 |  | 2091 | 2277 | 127.4725 | 0 | 118.8034 | 0 | 1.2747 | 0 | 1.188 | 0 | 1.2747 | 1.188 | 9.3573 | 17.3371 | 8.0826
38943.5606 | 2034 | 0 | 38943.5607 | 2081 | 0 |  | 2276 | 2462 | 124.1758 | 0 | 127.0452 | 0 | 1.2418 | 0 | 1.2705 | 0 | 1.2418 | 1.2705 | 12.2606 | 9.7251 | 11.0188
38943.5628 | 2084 | 0 | 38943.5628 | 2263 | 0 |  | 2460.5 | 2646.5 | 127.2283 | 0 | 138.1563 | 0 | 1.2723 | 0 | 1.3816 | 0 | 1.2723 | 1.3816 | 9.5672 | 0.90057 | 8.2949

## A2-C6
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38943.5326 | 1 | 0 | 38943.5326 | 1 | 0 |  | -145.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5347 | 1 | 0 | 38943.5348 | 1 | 0 |  | 39 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5369 | 1 | 0 | 38943.5369 | 1 | 0 |  | 223.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.539 | 1 | 0 | 38943.539 | 1 | 0 |  | 408.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5412 | 2 | 0 | 38943.5412 | 1 | 0 |  | 593.5 | 779.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38943.5433 | 1 | 0 | 38943.5433 | 1 | 0 |  | 778 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5454 | 2 | 0 | 38943.5455 | 2 | 0 |  | 963 | 1149 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5476 | 2 | 0 | 38943.5476 | 2 | 0 |  | 1147.5 | 1333.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5497 | 2 | 0 | 38943.5497 | 2 | 0 |  | 1332.5 | 1518.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5519 | 2 | 0 | 38943.5519 | 2 | 0 |  | 1517.5 | 1703.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.554 | 151 | 0 | 38943.554 | 3 | 0 |  | 1702 | 1888 | 9.2186 | 0 | 0.18315 | 0 | 0.092186 | 0 | 0.0018315 | 0 | 0.092186 | 0.0018315 | 1299.351 | 70334 | 1299.2588
38943.5561 | 214 | 0 | 38943.5561 | 417 | 0 |  | 1886.5 | 2072.5 | 13.0647 | 0 | 25.4579 | 0 | 0.13065 | 0 | 0.25458 | 0 | 0.13065 | 0.25458 | 887.3925 | 406.7194 | 887.2619
38943.5583 | 302 | 0 | 38943.5583 | 256 | 1 |  | 2071.5 | 2257.5 | 18.4371 | 0 | 15.6288 | 0.06105 | 0.18437 | 0 | 0.15629 | 0.0006105 | 0.18437 | 0.15568 | 599.6755 | 728.6353 | 599.4911
38943.5604 | 187 | 0 | 38943.5604 | 302 | 1 |  | 2256.5 | 2442.5 | 11.4164 | 0 | 18.4371 | 0.06105 | 0.11416 | 0 | 0.18437 | 0.0006105 | 0.11416 | 0.18376 | 1029.9572 | 602 | 1029.8431
38943.5625 | 61 | 0 | 38943.5626 | 93 | 0 |  | 2441 | 2627 | 3.7241 | 0 | 5.6777 | 0 | 0.037241 | 0 | 0.056777 | 0 | 0.037241 | 0.056777 | 3363.9672 | 2172.0645 | 3363.93

## A2-C5
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38943.5326 | 1 | 0 | 38943.5326 | 1 | 0 |  | -148.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5347 | 1 | 0 | 38943.5347 | 1 | 0 |  | 36.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5369 | 1 | 0 | 38943.5369 | 1 | 0 |  | 221 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.539 | 1 | 0 | 38943.539 | 1 | 0 |  | 405.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5411 | 2 | 0 | 38943.5411 | 1 | 0 |  | 590.5 | 776.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38943.5433 | 1 | 0 | 38943.5433 | 1 | 0 |  | 775.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5454 | 2 | 0 | 38943.5454 | 2 | 0 |  | 960 | 1146 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5475 | 2 | 0 | 38943.5476 | 2 | 0 |  | 1145 | 1331 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5497 | 2 | 0 | 38943.5497 | 2 | 0 |  | 1329.5 | 1515.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5518 | 2 | 0 | 38943.5518 | 2 | 0 |  | 1514.5 | 1700.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.554 | 68 | 0 | 38943.554 | 84 | 0 |  | 1699 | 1885 | 4.1514 | 0 | 5.1282 | 0 | 0.041514 | 0 | 0.051282 | 0 | 0.041514 | 0.051282 | 3007.3824 | 2415.5 | 3007.3408
38943.5561 | 261 | 0 | 38943.5561 | 178 | 0 |  | 1884 | 2070 | 15.9341 | 0 | 10.8669 | 0 | 0.15934 | 0 | 0.10867 | 0 | 0.15934 | 0.10867 | 709.5862 | 1087.0899 | 709.4269
38943.5582 | 282 | 0 | 38943.5583 | 220 | 0 |  | 2068.5 | 2254.5 | 17.2161 | 0 | 13.431 | 0 | 0.17216 | 0 | 0.13431 | 0 | 0.17216 | 0.13431 | 649.2979 | 860.4636 | 649.1257
38943.5604 | 193 | 0 | 38943.5604 | 266 | 1 |  | 2253.5 | 2439.5 | 11.7827 | 0 | 16.2393 | 0.06105 | 0.11783 | 0 | 0.16239 | 0.0006105 | 0.11783 | 0.16178 | 994.829 | 697.366 | 994.7112
38943.5625 | 191 | 0 | 38943.5625 | 121 | 0 |  | 2438.5 | 2624.5 | 11.6606 | 0 | 7.3871 | 0 | 0.11661 | 0 | 0.073871 | 0 | 0.11661 | 0.073871 | 1006.2932 | 1646.2975 | 1006.1766

## A2-B4
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38943.5325 | 1 | 0 | 38943.5326 | 1 | 0 |  | -151.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5347 | 1 | 0 | 38943.5347 | 1 | 0 |  | 33.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5368 | 1 | 0 | 38943.5368 | 1 | 0 |  | 218 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.539 | 1 | 0 | 38943.539 | 1 | 0 |  | 403 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5411 | 2 | 0 | 38943.5411 | 1 | 0 |  | 587.5 | 773.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38943.5432 | 1 | 0 | 38943.5433 | 2 | 0 |  | 772.5 | 958.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38943.5454 | 2 | 0 | 38943.5454 | 2 | 0 |  | 957.5 | 1143.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5475 | 2 | 0 | 38943.5475 | 2 | 0 |  | 1142 | 1328 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5497 | 2 | 0 | 38943.5497 | 2 | 0 |  | 1327 | 1513 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5518 | 2 | 0 | 38943.5518 | 2 | 0 |  | 1511.5 | 1697.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5539 | 103 | 14 | 38943.5539 | 149 | 43 |  | 1696.5 | 1882.5 | 6.2882 | 0.8547 | 9.0965 | 2.6252 | 0.062882 | 0.008547 | 0.090965 | 0.026252 | 0.054335 | 0.064713 | 2277.4401 | 1886.4507 | 13539.5591
38943.5561 | 217 | 0 | 38943.5561 | 222 | 0 |  | 1881 | 2067 | 13.2479 | 0 | 13.5531 | 0 | 0.13248 | 0 | 0.13553 | 0 | 0.13248 | 0.13553 | 873.7419 | 851.8108 | 873.6095
38943.5582 | 1205 | 0 | 38943.5582 | 298 | 0 |  | 2066 | 2252 | 73.5653 | 0 | 18.1929 | 0 | 0.73565 | 0 | 0.18193 | 0 | 0.73565 | 0.18193 | 75.3544 | 609.0671 | 74.6187
38943.5603 | 143 | 0 | 38943.5604 | 164 | 0 |  | 2250.5 | 2436.5 | 8.7302 | 0 | 10.0122 | 0 | 0.087302 | 0 | 0.10012 | 0 | 0.087302 | 0.10012 | 1377.6364 | 1188.4268 | 1377.5491
38943.5625 | 128 | 0 | 38943.5625 | 156 | 0 |  | 2435.5 | 2621.5 | 7.8144 | 0 | 9.5238 | 0 | 0.078144 | 0 | 0.095238 | 0 | 0.078144 | 0.095238 | 1550.7969 | 1254.5 | 1550.7187

## A2-B3
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 156.1893 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38943.5325 | 1 | 0 | 38943.5325 | 1 | 0 |  | -154 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38943.5347 | 1 | 0 | 38943.5347 | 1 | 0 |  | 30.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38943.5368 | 1 | 0 | 38943.5368 | 1 | 0 |  | 215.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38943.5389 | 1 | 0 | 38943.5389 | 1 | 0 |  | 400 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38943.5411 | 2 | 0 | 38943.5411 | 2 | 0 |  | 585 | 771 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 127819 | 127819 | 127818.9988
38943.5432 | 2 | 0 | 38943.5432 | 2 | 0 |  | 769.5 | 955.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 127819 | 127819 | 127818.9988
38943.5453 | 2 | 0 | 38943.5454 | 2 | 0 |  | 954.5 | 1140.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 127819 | 127819 | 127818.9988
38943.5475 | 3 | 0 | 38943.5475 | 2 | 0 |  | 1139.5 | 1325.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 85179.3333 | 127819 | 85179.3315
38943.5496 | 2 | 0 | 38943.5496 | 2 | 0 |  | 1324 | 1510 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 127819 | 127819 | 127818.9988
38943.5518 | 3 | 0 | 38943.5518 | 2 | 0 |  | 1509 | 1695 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 85179.3333 | 127819 | 85179.3315
38943.5539 | 84 | 1 | 38943.5539 | 660 | 0 |  | 1693.5 | 1879.5 | 5.1282 | 0.06105 | 40.293 | 0 | 0.051282 | 0.0006105 | 0.40293 | 0 | 0.050672 | 0.40293 | 2993.7206 | 287.6333 | 183530.7939
38943.556 | 187 | 0 | 38943.5561 | 2110 | 0 |  | 1878.5 | 2064.5 | 11.4164 | 0 | 128.8156 | 0 | 0.11416 | 0 | 1.2882 | 0 | 0.11416 | 1.2882 | 1268.1176 | 21.2502 | 1268.0035
38943.5582 | 72 | 0 | 38943.5582 | 2542 | 1 |  | 2063 | 2249 | 4.3956 | 0 | 155.1893 | 0.06105 | 0.043956 | 0 | 1.5519 | 0.0006105 | 0.043956 | 1.5513 | 3453.3056 | 0.68398 | 3453.2616
38943.5603 | 137 | 0 | 38943.5603 | 2250 | 0 |  | 2248 | 2434 | 8.3639 | 0 | 137.3626 | 0 | 0.083639 | 0 | 1.3736 | 0 | 0.083639 | 1.3736 | 1767.4307 | 13.7058 | 1767.347
38943.5625 | 128 | 0 | 38943.5625 | 2338 | 1 |  | 2432.5 | 2618.5 | 7.8144 | 0 | 142.735 | 0.06105 | 0.078144 | 0 | 1.4274 | 0.0006105 | 0.078144 | 1.4267 | 1898.7344 | 9.4728 | 1898.6562

## A1-C6
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38943.5323 | 1 | 0 | 38943.5323 | 1 | 0 |  | -173.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5344 | 1 | 0 | 38943.5344 | 1 | 0 |  | 11 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5366 | 1 | 0 | 38943.5366 | 1 | 0 |  | 196 | 382 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5387 | 1 | 0 | 38943.5387 | 1 | 0 |  | 380.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5408 | 2 | 0 | 38943.5409 | 1 | 0 |  | 565.5 | 751.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38943.543 | 1 | 0 | 38943.543 | 1 | 0 |  | 750 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5451 | 2 | 0 | 38943.5451 | 3 | 0 |  | 935 | 1121 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38943.5473 | 2 | 0 | 38943.5473 | 2 | 0 |  | 1119.5 | 1305.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5494 | 2 | 0 | 38943.5494 | 2 | 0 |  | 1304.5 | 1490.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5515 | 3 | 1 | 38943.5516 | 3 | 1 |  | 1489 | 1675 | 0.18315 | 0.06105 | 0.18315 | 0.06105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.0006105 | 0.001221 | 0.001221 | 105551 | 105551 | 210702.3786
38943.5537 | 41 | 1 | 38943.5537 | 3 | 0 |  | 1674 | 1860 | 2.5031 | 0.06105 | 0.18315 | 0 | 0.025031 | 0.0006105 | 0.0018315 | 0 | 0.02442 | 0.0018315 | 5180.2341 | 70334 | 206807.963
38943.5558 | 93 | 0 | 38943.5558 | 392 | 1 |  | 1858.5 | 2044.5 | 5.6777 | 0 | 23.9316 | 0.06105 | 0.056777 | 0 | 0.23932 | 0.0006105 | 0.056777 | 0.23871 | 2172.0645 | 440.4143 | 2172.0077
38943.558 | 152 | 1 | 38943.558 | 219 | 1 |  | 2043.5 | 2229.5 | 9.2796 | 0.06105 | 13.37 | 0.06105 | 0.092796 | 0.0006105 | 0.1337 | 0.0006105 | 0.092186 | 0.13309 | 1299.6791 | 869.1233 | 175777.3282
38943.5601 | 229 | 0 | 38943.5601 | 266 | 1 |  | 2228.5 | 2414.5 | 13.9805 | 0 | 16.2393 | 0.06105 | 0.1398 | 0 | 0.16239 | 0.0006105 | 0.1398 | 0.16178 | 822.7162 | 697.366 | 822.5764
38943.5622 | 162 | 1 | 38943.5622 | 111 | 1 |  | 2413 | 2599 | 9.8901 | 0.06105 | 6.7766 | 0.06105 | 0.098901 | 0.0006105 | 0.067766 | 0.0006105 | 0.098291 | 0.067155 | 1212.2271 | 1821.3841 | 184852.9621

## A1-C5
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38943.5323 | 1 | 0 | 38943.5323 | 1 | 0 |  | -176.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5344 | 1 | 0 | 38943.5344 | 1 | 0 |  | 8.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5365 | 1 | 0 | 38943.5366 | 1 | 0 |  | 193 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5387 | 1 | 0 | 38943.5387 | 1 | 0 |  | 377.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5408 | 2 | 0 | 38943.5408 | 2 | 0 |  | 562.5 | 748.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.543 | 1 | 0 | 38943.543 | 2 | 0 |  | 747.5 | 933.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38943.5451 | 3 | 0 | 38943.5451 | 2 | 0 |  | 932 | 1118 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38943.5472 | 3 | 0 | 38943.5472 | 2 | 1 |  | 1117 | 1303 | 0.18315 | 0 | 0.1221 | 0.06105 | 0.0018315 | 0 | 0.001221 | 0.0006105 | 0.0018315 | 0.0006105 | 70334 | 211202 | 70333.9982
38943.5494 | 2 | 0 | 38943.5494 | 2 | 0 |  | 1301.5 | 1487.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5515 | 3 | 2 | 38943.5515 | 3 | 1 |  | 1486.5 | 1672.5 | 0.18315 | 0.1221 | 0.18315 | 0.06105 | 0.0018315 | 0.001221 | 0.0018315 | 0.0006105 | 0.0006105 | 0.001221 | 211402.6648 | 105525.9585 | 105301.213
38943.5536 | 46 | 1 | 38943.5537 | 39 | 1 |  | 1671 | 1857 | 2.8083 | 0.06105 | 2.381 | 0.06105 | 0.028083 | 0.0006105 | 0.02381 | 0.0006105 | 0.027473 | 0.023199 | 4595.2477 | 5461.0748 | 202886.8549
38943.5558 | 85 | 1 | 38943.5558 | 68 | 1 |  | 1856 | 2042 | 5.1893 | 0.06105 | 4.1514 | 0.06105 | 0.051893 | 0.0006105 | 0.041514 | 0.0006105 | 0.051282 | 0.040904 | 2415.251 | 3054.156 | 196275.4948
38943.5579 | 139 | 1 | 38943.5579 | 285 | 1 |  | 2040.5 | 2226.5 | 8.486 | 0.06105 | 17.3993 | 0.06105 | 0.08486 | 0.0006105 | 0.17399 | 0.0006105 | 0.084249 | 0.17338 | 1432.0611 | 643.8273 | 170776.7575
38943.5601 | 963 | 1 | 38943.5601 | 245 | 1 |  | 2225.5 | 2411.5 | 58.7912 | 0.06105 | 14.9573 | 0.06105 | 0.58791 | 0.0006105 | 0.14957 | 0.0006105 | 0.5873 | 0.14896 | 119.5609 | 768.2153 | 101667.7249
38943.5622 | 172 | 2 | 38943.5622 | 134 | 2 |  | 2410.5 | 2596.5 | 10.5006 | 0.1221 | 8.1807 | 0.1221 | 0.10501 | 0.001221 | 0.081807 | 0.001221 | 0.10379 | 0.080586 | 1142.6719 | 1501.2482 | 90896.2859

## A1-B4
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 151.1832 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38943.5322 | 1 | 0 | 38943.5322 | 1 | 0 |  | -179.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38943.5344 | 1 | 0 | 38943.5344 | 1 | 0 |  | 5.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38943.5365 | 1 | 0 | 38943.5365 | 1 | 0 |  | 190 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38943.5386 | 1 | 0 | 38943.5387 | 1 | 0 |  | 375 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38943.5408 | 2 | 0 | 38943.5408 | 2 | 0 |  | 559.5 | 745.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 123719 | 123719 | 123718.9988
38943.5429 | 2 | 0 | 38943.5429 | 1 | 0 |  | 744.5 | 930.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123719 | 247538 | 123718.9988
38943.5451 | 3 | 0 | 38943.5451 | 3 | 0 |  | 929.5 | 1115.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 82446 | 82446 | 82445.9982
38943.5472 | 2 | 0 | 38943.5472 | 3 | 0 |  | 1114 | 1300 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 123719 | 82446 | 123718.9988
38943.5493 | 3 | 0 | 38943.5494 | 3 | 0 |  | 1299 | 1485 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 82446 | 82446 | 82445.9982
38943.5515 | 4 | 2 | 38943.5515 | 3 | 2 |  | 1483.5 | 1669.5 | 0.2442 | 0.1221 | 0.18315 | 0.1221 | 0.002442 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 123668.9191 | 247738.6482 | 123469.1615
38943.5536 | 56 | 3 | 38943.5536 | 426 | 2 |  | 1668.5 | 1854.5 | 3.4188 | 0.18315 | 26.0073 | 0.1221 | 0.034188 | 0.0018315 | 0.26007 | 0.001221 | 0.032357 | 0.25885 | 4620.8368 | 483.6296 | 66772.7445
38943.5557 | 54 | 3 | 38943.5558 | 1930 | 1 |  | 1853 | 2039 | 3.2967 | 0.18315 | 117.8266 | 0.06105 | 0.032967 | 0.0018315 | 1.1783 | 0.0006105 | 0.031136 | 1.1777 | 5994.7197 | 28.3248 | 17800.7653
38943.5579 | 122 | 2 | 38943.5579 | 2421 | 1 |  | 2038 | 2224 | 7.4481 | 0.1221 | 147.8022 | 0.06105 | 0.074481 | 0.001221 | 1.478 | 0.0006105 | 0.07326 | 1.4774 | 7221.0658 | 2.2884 | 2631.4249
38943.56 | 302 | 2 | 38943.56 | 2317 | 1 |  | 2222.5 | 2408.5 | 18.4371 | 0.1221 | 141.453 | 0.06105 | 0.18437 | 0.001221 | 1.4145 | 0.0006105 | 0.18315 | 1.4139 | 802.535 | 6.8821 | 6993.903
38943.5622 | 136 | 3 | 38943.5622 | 2460 | 3 |  | 2407.5 | 2593.5 | 8.3028 | 0.18315 | 150.1832 | 0.18315 | 0.083028 | 0.0018315 | 1.5018 | 0.0018315 | 0.081197 | 1.5 | 738.1169 | 1.6298 | 1249.4385

## A1-B3
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 146.9707 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38943.5322 | 1 | 0 | 38943.5322 | 1 | 0 |  | -182 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38943.5343 | 1 | 0 | 38943.5343 | 1 | 0 |  | 2.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38943.5365 | 1 | 0 | 38943.5365 | 1 | 0 |  | 187.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38943.5386 | 1 | 0 | 38943.5386 | 1 | 0 |  | 372 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38943.5407 | 3 | 0 | 38943.5408 | 2 | 0 |  | 557 | 743 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 80146 | 120269 | 80145.9982
38943.5429 | 1 | 0 | 38943.5429 | 1 | 0 |  | 741.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38943.545 | 3 | 0 | 38943.545 | 3 | 0 |  | 926.5 | 1112.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 80146 | 80146 | 80145.9982
38943.5472 | 4 | 0 | 38943.5472 | 3 | 0 |  | 1111.5 | 1297.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 60084.5 | 80146 | 60084.4976
38943.5493 | 3 | 0 | 38943.5493 | 3 | 0 |  | 1296 | 1482 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 80146 | 80146 | 80145.9982
38943.5514 | 4 | 9 | 38943.5514 | 3 | 4 |  | 1480.5 | 1666.5 | 0.2442 | 0.54945 | 0.18315 | 0.2442 | 0.002442 | 0.0054945 | 0.0018315 | 0.002442 | 0.0030525 | 0.0006105 | 48103.3123 | 242454.1116 | 26593.2539
38943.5536 | 37 | 8 | 38943.5536 | 36 | 4 |  | 1665.5 | 1851.5 | 2.2589 | 0.4884 | 2.1978 | 0.2442 | 0.022589 | 0.004884 | 0.021978 | 0.002442 | 0.017705 | 0.019536 | 8204.2182 | 7421.8705 | 29137.1648
38943.5557 | 32 | 8 | 38943.5557 | 2055 | 4 |  | 1850.5 | 2036.5 | 1.9536 | 0.4884 | 125.4579 | 0.2442 | 0.019536 | 0.004884 | 1.2546 | 0.002442 | 0.014652 | 1.2521 | 10527.192 | 557.193 | 25089.4249
38943.5578 | 132 | 6 | 38943.5579 | 2042 | 3 |  | 2035 | 2221 | 8.0586 | 0.3663 | 124.6642 | 0.18315 | 0.080586 | 0.003663 | 1.2466 | 0.0018315 | 0.076923 | 1.2448 | 2459.3637 | 17.9206 | 5748.0385
38943.56 | 296 | 6 | 38943.56 | 2346 | 3 |  | 2220 | 2406 | 18.0708 | 0.3663 | 143.2234 | 0.18315 | 0.18071 | 0.003663 | 1.4322 | 0.0018315 | 0.17705 | 1.4304 | 3462.6291 | 2.6198 | 895.8157
38943.5621 | 123 | 8 | 38943.5621 | 2391 | 5 |  | 2404.5 | 2590.5 | 7.5092 | 0.4884 | 145.9707 | 0.30525 | 0.075092 | 0.004884 | 1.4597 | 0.0030525 | 0.070208 | 1.4567 | 217.2605 | 0.85429 | 241.0277

## A1-A2
Penlight Test 35 |  |  | 2006-08-14 | 12:49 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38943.5322 | 1 | 0 | 38943.5322 | 1 | 0 |  | -185 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5343 | 1 | 0 | 38943.5343 | 1 | 0 |  | 1.0338e-07 | 186 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5364 | 1 | 0 | 38943.5364 | 1 | 0 |  | 184.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5386 | 1 | 0 | 38943.5386 | 1 | 0 |  | 369.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38943.5407 | 2 | 0 | 38943.5407 | 2 | 0 |  | 554 | 740 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.5428 | 2 | 0 | 38943.5429 | 2 | 0 |  | 739 | 925 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38943.545 | 3 | 0 | 38943.545 | 4 | 0 |  | 923.5 | 1109.5 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 70334 | 52725.5 | 70333.9982
38943.5471 | 4 | 0 | 38943.5471 | 3 | 0 |  | 1108.5 | 1294.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38943.5493 | 26 | 22 | 38943.5493 | 36 | 31 |  | 1293 | 1479 | 1.5873 | 1.3431 | 2.1978 | 1.8926 | 0.015873 | 0.013431 | 0.021978 | 0.018926 | 0.002442 | 0.0030525 | 52867.2601 | 42033.3454 | 9364.1766
38943.5514 | 1147 | 1116 | 38943.5514 | 1073 | 1039 |  | 1478 | 1664 | 70.0244 | 68.1319 | 65.5067 | 63.431 | 0.70024 | 0.68132 | 0.65507 | 0.63431 | 0.018926 | 0.020757 | 2714.9494 | 24358.7779 | 13.3841
38943.5535 | 1248 | 1142 | 38943.5536 | 1009 | 906 |  | 1663 | 1849 | 76.1905 | 69.7192 | 61.5995 | 55.3114 | 0.7619 | 0.69719 | 0.616 | 0.55311 | 0.064713 | 0.062882 | 13278.0922 | 1147.9076 | 22.3104
38943.5557 | 1235 | 1158 | 38943.5557 | 1233 | 1117 |  | 1847.5 | 2033.5 | 75.3968 | 70.696 | 75.2747 | 68.1929 | 0.75397 | 0.70696 | 0.75275 | 0.68193 | 0.047009 | 0.070818 | 782.3923 | 3287.6732 | 23.4642
38943.5578 | 1053 | 821 | 38943.5578 | 1344 | 1055 |  | 2032.5 | 2218.5 | 64.2857 | 50.1221 | 82.0513 | 64.4078 | 0.64286 | 0.50122 | 0.82051 | 0.64408 | 0.14164 | 0.17643 | 86.615 | 82.7763 | 13.1849
38943.56 | 1110 | 833 | 38943.56 | 1043 | 827 |  | 2217 | 2403 | 67.7656 | 50.8547 | 63.6752 | 50.4884 | 0.67766 | 0.50855 | 0.63675 | 0.50488 | 0.16911 | 0.13187 | 330.0151 | 3093.0261 | 19.7713
38943.5621 | 1107 | 964 | 38943.5621 | 1296 | 1062 |  | 2402 | 2588 | 67.5824 | 58.8523 | 79.1209 | 64.8352 | 0.67582 | 0.58852 | 0.79121 | 0.64835 | 0.087302 | 0.14286 | 185.6038 | 241.5885 | 3.0828

## AvgC-C
Average Conductor to Conductor Resistances
Penlight Test 35 |  |  | 2006-08-14 | 12:49
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2
Time | C1-C |  | Time | C2-C | Time | C3-C | Time | C4-C | Time | C5-C | Time | C6-C | Time | C7-C | Time | Minimums
-167.6667 | 230169.9994 |  | -131.25 | 225213.9994 | -137.25 | 240531.9994 | -125.25 | 239131.9994 | -116.3333 | 227430.6661 | -111.5833 | 231436.6661 | -74.8333 | 255021.3327 | -167.6667 | 225213.9994
17.1667 | 230169.9994 |  | 53.5833 | 225213.9994 | 47.4167 | 240531.9994 | 59.5833 | 239131.9994 | 68.5 | 227430.6661 | 73.0833 | 231436.6661 | 110 | 255021.3327 | 17.1667 | 225213.9994
201.8333 | 230169.9994 |  | 238.1667 | 225213.9994 | 232.25 | 240531.9994 | 244.3333 | 239131.9994 | 253.25 | 227430.6661 | 257.9167 | 231436.6661 | 294.75 | 255021.3327 | 201.8333 | 225213.9994
386.5833 | 197752.7491 |  | 423 | 204310.8326 | 417 | 240531.9994 | 429.1667 | 176789.1658 | 437.9167 | 205994.166 | 442.5833 | 189846.9992 | 479.5833 | 159494.5821 | 386.5833 | 159494.5821
571.3333 | 97542.0818 |  | 607.75 | 112556.9988 | 601.75 | 173435.3323 | 613.8333 | 119515.9988 | 622.75 | 148882.3323 | 627.4167 | 176074.8324 | 664.1667 | 159044.5821 | 571.3333 | 97542.0818
756.1667 | 159507.7489 |  | 792.5833 | 154930.9155 | 786.4167 | 140277.4989 | 798.5833 | 137124.4989 | 807.5833 | 148882.3323 | 812.1667 | 150885.3323 | 849 | 106203.3317 | 756.1667 | 106203.3317
941 | 78924.2482 |  | 977.3333 | 96235.9151 | 971.3333 | 107186.1097 | 983.5 | 106294.443 | 992.25 | 107795.832 | 997 | 115668.3321 | 1033.9167 | 106203.3317 | 941 | 78924.2482
1125.75 | 79524.7481 |  | 1162.1667 | 86194.5538 | 1156.1667 | 103078.6374 | 1168.25 | 140277.4989 | 1177.1667 | 107795.832 | 1181.75 | 115668.3321 | 1218.5833 | 126964.8318 | 1125.75 | 79524.7481
1310.4167 | 74632.1113 |  | 1346.9167 | 75889.3323 | 1340.8333 | 113528.832 | 1353.0833 | 112637.1653 | 1361.8333 | 113665.3321 | 1366.5 | 115668.3321 | 1403.4167 | 96018.3858 | 1310.4167 | 74632.1113
1495.1667 | 88468.9814 |  | 1531.75 | 66974.4544 | 1525.5833 | 97496.7634 | 1537.75 | 108756.109 | 1546.5833 | 94101.2007 | 1551.3333 | 113666.895 | 1588 | 85046.1677 | 1495.1667 | 66974.4544
1680.0833 | 84275.5812 |  | 1716.5 | 33571.1735 | 1710.4167 | 35813.7984 | 1722.5833 | 14103.6688 | 1731.3333 | 48951.3292 | 1736.0833 | 43283.1058 | 1773 | 23455.5414 | 1680.0833 | 14103.6688
1864.75 | 40231.8993 |  | 1901.1667 | 629.4747 | 1895.1667 | 4410.0623 | 1907.3333 | 3133.9494 | 1916.1667 | 33407.7512 | 1920.75 | 1096.4797 | 1957.6667 | 275.0563 | 1864.75 | 275.0563
2049.5833 | 59161.256 |  | 2086 | 812.899 | 2079.8333 | 1537.7644 | 2092.0833 | 499.8701 | 2100.8333 | 35872.2154 | 2105.5 | 29627.6302 | 2142.5 | 7500.7367 | 2049.5833 | 499.8701
2234.3333 | 18403.6376 |  | 2270.75 | 876.2455 | 2264.75 | 449.467 | 2276.75 | 1397.5039 | 2285.6667 | 17307.8637 | 2290.4167 | 542.1946 | 2327.1667 | 428.1221 | 2234.3333 | 428.1221
2419.1667 | 46209.9163 |  | 2455.5833 | 1315.7127 | 2449.4167 | 362.8217 | 2461.5833 | 471.424 | 2470.5833 | 16592.4745 | 2475.1667 | 33503.9235 | 2512 | 3417.0602 | 2419.1667 | 362.8217
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 35 |  |  | 2006-08-14 | 12:49
XLPE&PE | 7-C | Tray
525 C | 23.0 kW/m2
Time | C1-G |  | Time | C2-G | Time | C3-G | Time | C4-G | Time | C5-G | Time | C6-G | Time | C7-G | Time | C8-G | Time | C9-G | Time | C10-G | Time | C11-G | Time | C12-G | Time | Minimums
-179.3 | 224356.4 |  | -156.9 | 220109.2 | -128.8889 | 246356.2222 | -113.3889 | 244634 | -99.0556 | 234199.7778 | -90.2778 | 237414.8889 | -66.2 | 248678 | -60.6 | 249738 | -48.3333 | 259326.8889 | -45.2778 | 258849.1111 | -27.5 | 214532.3 | -25.3 | 249678 | -86.7519 | 214532.3
5.5 | 224356.4 |  | 27.9 | 220109.2 | 55.8333 | 246356.2222 | 71.4444 | 244634 | 85.7778 | 234199.7778 | 94.4444 | 237414.8889 | 118.5 | 248678 | 124.2 | 249738 | 136.3889 | 259326.8889 | 139.6111 | 258849.1111 | 157.3 | 227194.2 | 159.5 | 249678 | 98.0333 | 220109.2
190.2 | 224356.4 |  | 212.5 | 220109.2 | 240.6111 | 231920.7778 | 256.1667 | 244634 | 270.5 | 234199.7778 | 279.1667 | 237414.8889 | 303.4 | 248678 | 309 | 249738 | 321.3333 | 259326.8889 | 324.2222 | 258849.1111 | 341.9 | 252518 | 344.2 | 249678 | 282.7667 | 220109.2
374.9 | 224356.4 |  | 397.3 | 220109.2 | 425.3889 | 224744.7222 | 440.9444 | 181518.9444 | 455.2222 | 169126.963 | 463.8889 | 142338.2222 | 488 | 136300.9 | 493.6 | 181756.12 | 505.9444 | 15.3894 | 509 | 48857.2976 | 526.7 | 96591.2333 | 529 | 92635.52 | 467.4907 | 15.3894
559.7 | 104103.6 |  | 582.1 | 110004.6 | 610.1111 | 170036.2778 | 625.6667 | 167761.2778 | 640 | 150007.0741 | 648.7222 | 176329.6111 | 672.8 | 197630.4 | 678.4 | 223464.2 | 690.6667 | 32967.8255 | 693.7222 | 76739.1572 | 711.5 | 109246.4667 | 713.7 | 174046.6 | 652.2574 | 32967.8255
744.5 | 178462.4 |  | 766.9 | 173395.2 | 794.8333 | 143734.0556 | 810.4444 | 143203.5 | 824.8333 | 124353.2037 | 833.5 | 123598.3704 | 857.6 | 136080.9 | 863.2 | 162199.7 | 875.3889 | 12.3815 | 878.6667 | 9.5254 | 896.3 | 71444.1 | 898.5 | 83490.92 | 837.0556 | 9.5254
929.3 | 81762.2 |  | 951.7 | 99439.5 | 979.7222 | 107237.6852 | 995.2778 | 124859.9444 | 1009.5556 | 102836.6667 | 1018.2778 | 96207.3704 | 1042.5 | 111167.1 | 1048 | 111682.1 | 1060.3333 | 16.3761 | 1063.2778 | 17.6713 | 1080.8 | 75704.7333 | 1083.3 | 77990.3667 | 1021.837 | 16.3761
1114.1 | 82482.8 |  | 1136.5 | 94433.2667 | 1164.5556 | 125640.5 | 1180.0556 | 124337.7222 | 1194.3889 | 112688.2778 | 1203.0556 | 106973.2778 | 1227.2 | 100075.2 | 1232.9 | 104969.1667 | 1245.1111 | 12.0958 | 1248.1667 | 10.8518 | 1265.9 | 68887.72 | 1268 | 82551 | 1206.6611 | 10.8518
1298.8 | 85312.252 |  | 1321.2 | 97301.0691 | 1349.2222 | 111466.1667 | 1364.8333 | 110496.7222 | 1379.1111 | 116981.5741 | 1387.8333 | 102468.8704 | 1412 | 51183.9563 | 1417.6 | 99524.2072 | 1429.8889 | 17.2309 | 1432.8889 | 10.1792 | 1450.6 | 64294.6336 | 1453 | 66356.5944 | 1391.4148 | 10.1792
1483.5 | 98288.1691 |  | 1506.1 | 85238.2223 | 1534 | 129500.4013 | 1549.6111 | 121717.072 | 1563.8333 | 97499.7732 | 1572.6111 | 86806.8889 | 1596.6 | 2166.7299 | 1602.2 | 6803.101 | 1614.5556 | 21.3369 | 1617.7222 | 13.349 | 1635.4 | 14.4778 | 1637.6 | 10.4248 | 1576.1444 | 10.4248
1668.4 | 7175.7258 |  | 1690.8 | 2145.1603 | 1718.8333 | 1626.285 | 1734.3889 | 1591.2855 | 1748.6111 | 22210.0744 | 1757.3333 | 42675.594 | 1781.5 | 83.6834 | 1787.2 | 34.9881 | 1799.3333 | 17.8138 | 1802.4444 | 15.6224 | 1820.2 | 18.7131 | 1822.4 | 17.2764 | 1760.9537 | 15.6224
1853.1 | 4378.3239 |  | 1875.5 | 1405.3023 | 1903.5556 | 75.0654 | 1919.1111 | 112.6437 | 1933.3889 | 1052.7182 | 1942.0556 | 497.5721 | 1966.3 | 18.3751 | 1971.9 | 11.0088 | 1984.1111 | 10.4582 | 1987.1667 | 16.7636 | 2004.9 | 4.9849 | 2007 | 12.74 | 1945.6741 | 4.9849
2037.9 | 2499.7569 |  | 2060.3 | 972.0819 | 2088.2778 | 9.8973 | 2103.8889 | 177.9234 | 2118.1111 | 1016.5052 | 2126.8333 | 1033.862 | 2151 | 34.8302 | 2156.6 | 55.0794 | 2168.8889 | 8.7527 | 2172 | 17.0704 | 2189.6 | 10.0927 | 2192 | 15.1085 | 2130.45 | 8.7527
2222.7 | 1107.4912 |  | 2245.1 | 1652.5759 | 2273.1111 | 12.1619 | 2288.6111 | 137.5924 | 2302.9444 | 948.6918 | 2311.7222 | 1207.7469 | 2335.8 | 61.5758 | 2341.4 | 83.8963 | 2353.6667 | 17.5682 | 2356.7222 | 18.3635 | 2374.5 | 346.0655 | 2376.7 | 276.3317 | 2315.2481 | 12.1619
2407.5 | 699.176 |  | 2429.9 | 1612.276 | 2457.8333 | 11.0744 | 2473.4444 | 147.4951 | 2487.8333 | 4584.599 | 2496.5 | 6734.2888 | 2520.6 | 652.1758 | 2526.2 | 435.9047 | 2538.3889 | 13.1729 | 2541.6667 | 15.424 | 2559.3 | 370.3972 | 2561.5 | 679.8442 | 2500.0556 | 11.0744

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -186 | 18.7 | 23.2 | 23.5 | 23.6 | 23.3 | 23.4 | 23.8 | 24.6
1 | -185 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
2 | -184 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
3 | -183 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
4 | -182 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.6
5 | -181 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.6
6 | -180 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
7 | -179 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
8 | -178 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
9 | -177 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
10 | -176 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
11 | -175 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
12 | -174 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
13 | -173 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
14 | -172 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
15 | -171 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
16 | -170 | 18.7 | 23.2 | 23.5 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
17 | -169 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
18 | -168 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
19 | -167 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
20 | -166 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
21 | -165 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
22 | -164 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
23 | -163 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
24 | -162 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
25 | -161 | 18.7 | 23.2 | 23.4 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
26 | -160 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
27 | -159 | 18.7 | 23.2 | 23.4 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
28 | -158 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
29 | -157 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
30 | -156 | 18.7 | 23.2 | 23.4 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
31 | -155 | 18.7 | 23.2 | 23.4 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
32 | -154 | 18.7 | 23.2 | 23.5 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
33 | -153 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
34 | -152 | 18.7 | 23.2 | 23.4 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
35 | -151 | 18.7 | 23.2 | 23.4 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
36 | -150 | 18.7 | 23.2 | 23.4 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
37 | -149 | 18.7 | 23.2 | 23.5 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
38 | -148 | 18.7 | 23.2 | 23.5 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
39 | -147 | 18.7 | 23.2 | 23.4 | 23.6 | 23.3 | 23.4 | 23.8 | 24.7
40 | -146 | 18.7 | 23.2 | 23.5 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
41 | -145 | 18.7 | 23.2 | 23.5 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
42 | -144 | 18.7 | 23.2 | 23.5 | 23.7 | 23.3 | 23.4 | 23.8 | 24.7
43 | -143 | 18.7 | 23.2 | 23.5 | 23.7 | 23.4 | 23.4 | 23.8 | 24.7
44 | -142 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
45 | -141 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
46 | -140 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
47 | -139 | 18.5 | 23.3 | 23.2 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
48 | -138 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.1
49 | -137 | 18.5 | 23.3 | 23.2 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
50 | -136 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
51 | -135 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
52 | -134 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
53 | -133 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
54 | -132 | 18.5 | 23.3 | 23.2 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
55 | -131 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
56 | -130 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
57 | -129 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
58 | -128 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
59 | -127 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
60 | -126 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
61 | -125 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
62 | -124 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
63 | -123 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
64 | -122 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
65 | -121 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
66 | -120 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
67 | -119 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
68 | -118 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
69 | -117 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
70 | -116 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
71 | -115 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
72 | -114 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
73 | -113 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
74 | -112 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
75 | -111 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
76 | -110 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
77 | -109 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
78 | -108 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
79 | -107 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
80 | -106 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
81 | -105 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
82 | -104 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
83 | -103 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
84 | -102 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
85 | -101 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
86 | -100 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
87 | -99 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
88 | -98 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
89 | -97 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
90 | -96 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
91 | -95 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
92 | -94 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
93 | -93 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
94 | -92 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
95 | -91 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
96 | -90 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
97 | -89 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
98 | -88 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
99 | -87 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
100 | -86 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
101 | -85 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
102 | -84 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
103 | -83 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
104 | -82 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
105 | -81 | 18.5 | 23.3 | 23.3 | 23.7 | 23.5 | 23.5 | 23.8 | 24.2
106 | -80 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
107 | -79 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
108 | -78 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
109 | -77 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
110 | -76 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
111 | -75 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
112 | -74 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
113 | -73 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
114 | -72 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
115 | -71 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
116 | -70 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
117 | -69 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
118 | -68 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
119 | -67 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
120 | -66 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
121 | -65 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
122 | -64 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
123 | -63 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
124 | -62 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
125 | -61 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
126 | -60 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
127 | -59 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
128 | -58 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
129 | -57 | 18.5 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
130 | -56 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
131 | -55 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
132 | -54 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
133 | -53 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
134 | -52 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
135 | -51 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
136 | -50 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
137 | -49 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
138 | -48 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
139 | -47 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
140 | -46 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
141 | -45 | 18.6 | 23.3 | 23.3 | 23.7 | 23.6 | 23.5 | 23.8 | 24.2
142 | -44 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
143 | -43 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
144 | -42 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
145 | -41 | 18.5 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
146 | -40 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
147 | -39 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
148 | -38 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
149 | -37 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
150 | -36 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
151 | -35 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
152 | -34 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
153 | -33 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
154 | -32 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
155 | -31 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
156 | -30 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
157 | -29 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
158 | -28 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
159 | -27 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
160 | -26 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
161 | -25 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
162 | -24 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
163 | -23 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
164 | -22 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
165 | -21 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
166 | -20 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
167 | -19 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
168 | -18 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
169 | -17 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
170 | -16 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
171 | -15 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
172 | -14 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
173 | -13 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
174 | -12 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
175 | -11 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
176 | -10 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
177 | -9 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
178 | -8 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
179 | -7 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.5 | 23.8 | 24.2
180 | -6 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
181 | -5 | 18.6 | 23.3 | 23.3 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
182 | -4 | 18.6 | 23.3 | 23.2 | 23.8 | 23.6 | 23.6 | 23.8 | 24.2
183 | -3 | 18.5 | 23.4 | 23 | 23.9 | 23.8 | 23.6 | 23.8 | 24
184 | -2 | 18.5 | 23.4 | 23 | 23.9 | 23.8 | 23.6 | 23.8 | 24
185 | -1 | 18.7 | 23.4 | 23.1 | 23.8 | 23.8 | 23.6 | 23.8 | 24
186 | 0 | 19.5 | 23.4 | 23.1 | 23.8 | 23.7 | 23.6 | 23.8 | 24
187 | 1 | 20.9 | 23.4 | 23.1 | 23.8 | 23.7 | 23.6 | 23.8 | 24
188 | 2 | 22.8 | 23.4 | 23.1 | 23.8 | 23.7 | 23.6 | 23.8 | 24
189 | 3 | 25.1 | 23.4 | 23.1 | 23.8 | 23.7 | 23.7 | 23.8 | 24
190 | 4 | 27.7 | 23.4 | 23.1 | 23.8 | 23.7 | 23.7 | 23.9 | 24
191 | 5 | 30.8 | 23.4 | 23.1 | 23.8 | 23.7 | 23.7 | 23.9 | 24.1
192 | 6 | 34.1 | 23.4 | 23.1 | 23.8 | 23.8 | 23.8 | 24 | 24.1
193 | 7 | 37.6 | 23.4 | 23.1 | 23.8 | 23.8 | 23.8 | 24 | 24.1
194 | 8 | 41.4 | 23.4 | 23.1 | 23.8 | 23.8 | 23.9 | 24.1 | 24.2
195 | 9 | 45.4 | 23.4 | 23.1 | 23.8 | 23.8 | 23.9 | 24.2 | 24.2
196 | 10 | 49.5 | 23.4 | 23.1 | 23.9 | 23.8 | 24 | 24.3 | 24.3
197 | 11 | 53.8 | 23.4 | 23.1 | 23.9 | 23.8 | 24.1 | 24.4 | 24.3
198 | 12 | 58.3 | 23.5 | 23.1 | 23.9 | 23.8 | 24.2 | 24.5 | 24.4
199 | 13 | 62.9 | 23.5 | 23.1 | 23.9 | 23.8 | 24.3 | 24.6 | 24.5
200 | 14 | 67.7 | 23.5 | 23.1 | 23.9 | 23.9 | 24.4 | 24.7 | 24.5
201 | 15 | 72.6 | 23.5 | 23.1 | 23.9 | 23.9 | 24.5 | 24.9 | 24.6
202 | 16 | 77.5 | 23.5 | 23.1 | 23.9 | 23.9 | 24.6 | 25 | 24.7
203 | 17 | 82.5 | 23.6 | 23.1 | 24 | 24 | 24.7 | 25.2 | 24.8
204 | 18 | 87.6 | 23.6 | 23.1 | 24 | 24 | 24.9 | 25.4 | 24.9
205 | 19 | 92.9 | 23.6 | 23.2 | 24 | 24.1 | 25 | 25.6 | 25.1
206 | 20 | 98.2 | 23.7 | 23.2 | 24.1 | 24.1 | 25.2 | 25.8 | 25.2
207 | 21 | 103.7 | 23.7 | 23.2 | 24.1 | 24.2 | 25.4 | 26 | 25.4
208 | 22 | 109.1 | 23.8 | 23.2 | 24.2 | 24.2 | 25.6 | 26.2 | 25.5
209 | 23 | 114.7 | 23.8 | 23.2 | 24.2 | 24.3 | 25.8 | 26.5 | 25.7
210 | 24 | 120.2 | 23.9 | 23.3 | 24.3 | 24.4 | 26 | 26.7 | 25.9
211 | 25 | 125.7 | 23.9 | 23.3 | 24.3 | 24.5 | 26.2 | 27 | 26.1
212 | 26 | 131.3 | 24 | 23.3 | 24.4 | 24.6 | 26.5 | 27.3 | 26.3
213 | 27 | 136.9 | 24.1 | 23.4 | 24.5 | 24.7 | 26.7 | 27.6 | 26.5
214 | 28 | 142.6 | 24.2 | 23.4 | 24.5 | 24.8 | 27 | 28 | 26.8
215 | 29 | 148.4 | 24.3 | 23.4 | 24.6 | 24.9 | 27.3 | 28.3 | 27
216 | 30 | 154 | 24.4 | 23.5 | 24.7 | 25 | 27.6 | 28.7 | 27.3
217 | 31 | 159.6 | 24.5 | 23.5 | 24.8 | 25.1 | 27.9 | 29.1 | 27.6
218 | 32 | 165.2 | 24.6 | 23.6 | 24.9 | 25.2 | 28.2 | 29.5 | 27.9
219 | 33 | 170.8 | 24.7 | 23.6 | 25 | 25.4 | 28.6 | 29.9 | 28.2
220 | 34 | 176.5 | 24.8 | 23.7 | 25.1 | 25.5 | 29 | 30.3 | 28.6
221 | 35 | 182.2 | 24.9 | 23.8 | 25.3 | 25.7 | 29.3 | 30.8 | 29
222 | 36 | 187.8 | 25.1 | 23.8 | 25.4 | 25.8 | 29.7 | 31.3 | 29.3
223 | 37 | 193.5 | 25.2 | 23.9 | 25.5 | 26 | 30.2 | 31.8 | 29.7
224 | 38 | 199.2 | 25.3 | 24 | 25.7 | 26.2 | 30.5 | 32.3 | 30.2
225 | 39 | 204.8 | 25.5 | 24.1 | 25.9 | 26.4 | 30.9 | 32.8 | 30.6
226 | 40 | 210.4 | 25.7 | 24.2 | 26 | 26.6 | 31.3 | 33.4 | 31.1
227 | 41 | 216.1 | 25.8 | 24.3 | 26.2 | 26.8 | 31.8 | 34 | 31.6
228 | 42 | 221.7 | 26 | 24.4 | 26.4 | 27 | 32.2 | 34.6 | 32.1
229 | 43 | 227.3 | 26.2 | 24.5 | 26.6 | 27.3 | 32.7 | 35.2 | 32.6
230 | 44 | 232.9 | 26.5 | 24.6 | 26.8 | 27.5 | 33.2 | 35.8 | 33.2
231 | 45 | 238.4 | 26.7 | 24.8 | 27.1 | 27.8 | 33.7 | 36.5 | 33.7
232 | 46 | 243.8 | 26.9 | 24.9 | 27.3 | 28.1 | 34.3 | 37.2 | 34.3
233 | 47 | 249.3 | 27.1 | 25 | 27.6 | 28.4 | 34.8 | 38 | 35
234 | 48 | 254.8 | 27.4 | 25.1 | 27.8 | 28.7 | 35.4 | 38.7 | 35.6
235 | 49 | 260.4 | 27.7 | 25.3 | 28.1 | 29 | 36 | 39.5 | 36.3
236 | 50 | 265.9 | 27.9 | 25.4 | 28.3 | 29.3 | 36.6 | 40.3 | 37
237 | 51 | 271.4 | 28.2 | 25.6 | 28.6 | 29.6 | 37.2 | 41.1 | 37.7
238 | 52 | 276.8 | 28.5 | 25.8 | 28.9 | 29.9 | 37.8 | 41.9 | 38.5
239 | 53 | 282.1 | 28.8 | 25.9 | 29.2 | 30.3 | 38.6 | 42.8 | 39.2
240 | 54 | 287.5 | 29.1 | 26.1 | 29.6 | 30.7 | 39.3 | 43.7 | 40
241 | 55 | 292.8 | 29.5 | 26.3 | 29.9 | 31 | 40 | 44.6 | 40.9
242 | 56 | 298 | 29.8 | 26.5 | 30.2 | 31.4 | 40.7 | 45.5 | 41.7
243 | 57 | 303.4 | 30.2 | 26.7 | 30.6 | 31.8 | 41.5 | 46.5 | 42.6
244 | 58 | 308.8 | 30.5 | 27 | 31 | 32.3 | 42.3 | 47.4 | 43.6
245 | 59 | 314.1 | 30.9 | 27.2 | 31.3 | 32.7 | 43 | 48.4 | 44.6
246 | 60 | 319.4 | 31.3 | 27.4 | 31.8 | 33.1 | 43.9 | 49.4 | 45.6
247 | 61 | 324.7 | 31.7 | 27.7 | 32.2 | 33.6 | 44.8 | 50.3 | 46.6
248 | 62 | 329.8 | 32.1 | 28 | 32.6 | 34.1 | 45.6 | 51.4 | 47.6
249 | 63 | 335 | 32.6 | 28.2 | 33 | 34.6 | 46.5 | 52.5 | 48.7
250 | 64 | 340 | 33 | 28.5 | 33.5 | 35.1 | 47.4 | 53.6 | 49.8
251 | 65 | 344.9 | 33.5 | 28.8 | 33.9 | 35.6 | 48.3 | 54.8 | 51
252 | 66 | 349.9 | 34 | 29.1 | 34.4 | 36.1 | 49.2 | 55.9 | 52.2
253 | 67 | 354.8 | 34.5 | 29.4 | 34.9 | 36.7 | 50 | 57.1 | 53.4
254 | 68 | 359.6 | 35 | 29.7 | 35.4 | 37.2 | 51 | 58.4 | 54.6
255 | 69 | 364.6 | 35.5 | 30.1 | 35.9 | 37.8 | 52.1 | 59.6 | 55.9
256 | 70 | 369.5 | 36.1 | 30.4 | 36.4 | 38.4 | 53.2 | 60.9 | 57.2
257 | 71 | 374.2 | 36.6 | 30.8 | 37 | 39 | 54.2 | 62.2 | 58.6
258 | 72 | 378.9 | 37.2 | 31.1 | 37.5 | 39.6 | 55.3 | 63.5 | 60
259 | 73 | 383.6 | 37.8 | 31.5 | 38.1 | 40.2 | 56.3 | 64.8 | 61.4
260 | 74 | 388.3 | 38.4 | 31.9 | 38.7 | 40.9 | 57.4 | 66 | 62.9
261 | 75 | 393.1 | 39 | 32.3 | 39.3 | 41.6 | 58.5 | 67.4 | 64.4
262 | 76 | 397.7 | 39.6 | 32.7 | 39.9 | 42.2 | 59.7 | 68.9 | 65.9
263 | 77 | 402.5 | 40.3 | 33.2 | 40.5 | 43 | 60.8 | 70.3 | 67.5
264 | 78 | 407.1 | 40.9 | 33.6 | 41.2 | 43.7 | 62 | 71.7 | 69.1
265 | 79 | 411.5 | 41.6 | 34.1 | 41.8 | 44.4 | 63.2 | 73.3 | 70.8
266 | 80 | 415.8 | 42.3 | 34.5 | 42.5 | 45.2 | 64.4 | 74.9 | 72.5
267 | 81 | 420.2 | 43 | 35 | 43.2 | 45.9 | 65.6 | 76.5 | 74.2
268 | 82 | 424.6 | 43.8 | 35.5 | 43.9 | 46.7 | 66.8 | 78.1 | 76
269 | 83 | 429.1 | 44.5 | 36 | 44.7 | 47.5 | 68.1 | 79.7 | 77.8
270 | 84 | 433.3 | 45.3 | 36.5 | 45.4 | 48.4 | 69.5 | 81.2 | 79.7
271 | 85 | 437.7 | 46.1 | 37.1 | 46.2 | 49.2 | 70.9 | 82.7 | 81.6
272 | 86 | 442.1 | 46.9 | 37.6 | 46.9 | 50.1 | 72.1 | 84.2 | 83.5
273 | 87 | 446.5 | 47.7 | 38.2 | 47.7 | 51 | 73.4 | 85.9 | 85.5
274 | 88 | 450.6 | 48.6 | 38.7 | 48.5 | 51.9 | 74.8 | 87.6 | 87.5
275 | 89 | 454.8 | 49.4 | 39.3 | 49.4 | 52.8 | 76.1 | 89.2 | 89.6
276 | 90 | 459.1 | 50.3 | 39.9 | 50.2 | 53.8 | 77.5 | 91 | 91.7
277 | 91 | 463.5 | 51.2 | 40.5 | 51.1 | 54.8 | 78.9 | 92.7 | 93.8
278 | 92 | 467.7 | 52.1 | 41.1 | 52 | 55.8 | 80.4 | 94.4 | 96
279 | 93 | 471.9 | 53.1 | 41.8 | 52.9 | 56.8 | 81.9 | 96.3 | 98.2
280 | 94 | 475.9 | 54 | 42.4 | 53.8 | 57.8 | 83.4 | 98.2 | 100.5
281 | 95 | 479.7 | 55 | 43 | 54.8 | 58.9 | 84.9 | 100 | 102.8
282 | 96 | 483.2 | 56 | 43.7 | 55.7 | 59.9 | 86.5 | 101.8 | 105.1
283 | 97 | 486.4 | 57 | 44.4 | 56.7 | 61 | 88 | 103.6 | 107.5
284 | 98 | 489.4 | 58 | 45.1 | 57.7 | 62 | 89.5 | 105.3 | 109.9
285 | 99 | 492.1 | 59.1 | 45.8 | 58.7 | 63.1 | 91.1 | 107.1 | 112.2
286 | 100 | 495 | 60.1 | 46.6 | 59.7 | 64.2 | 92.6 | 108.8 | 114.6
287 | 101 | 497.5 | 61.2 | 47.3 | 60.7 | 65.3 | 94.2 | 110.5 | 117
288 | 102 | 499.9 | 62.3 | 48 | 61.8 | 66.4 | 95.6 | 112.3 | 119.4
289 | 103 | 502.3 | 63.3 | 48.8 | 62.9 | 67.6 | 97 | 113.9 | 121.9
290 | 104 | 504.4 | 64.4 | 49.6 | 64 | 68.7 | 98.5 | 115.4 | 124.3
291 | 105 | 506.5 | 65.5 | 50.4 | 65.1 | 69.8 | 100 | 117.1 | 126.7
292 | 106 | 508.5 | 66.6 | 51.2 | 66.2 | 71 | 101.5 | 119 | 129.2
293 | 107 | 510.6 | 67.8 | 52 | 67.3 | 72.1 | 103.1 | 120.7 | 131.7
294 | 108 | 512.4 | 68.9 | 52.8 | 68.5 | 73.2 | 104.6 | 122.5 | 134.2
295 | 109 | 513.9 | 70 | 53.6 | 69.6 | 74.4 | 105.8 | 124 | 136.6
296 | 110 | 515.3 | 71.2 | 54.5 | 70.8 | 75.5 | 107.2 | 125.6 | 139.1
297 | 111 | 516.7 | 72.3 | 55.3 | 72 | 76.6 | 108.9 | 126.9 | 141.6
298 | 112 | 517.9 | 73.4 | 56.2 | 73.2 | 77.7 | 110.4 | 128.4 | 144.1
299 | 113 | 518.7 | 74.6 | 57.1 | 74.4 | 78.8 | 111.6 | 129.9 | 146.5
300 | 114 | 519.6 | 75.7 | 57.9 | 75.6 | 80 | 113.1 | 131.5 | 148.9
301 | 115 | 520.1 | 76.9 | 58.8 | 76.9 | 81.1 | 114.6 | 132.6 | 151.3
302 | 116 | 520.4 | 78 | 59.7 | 78.1 | 82.2 | 116.1 | 133.8 | 153.7
303 | 117 | 520.8 | 79.2 | 60.6 | 79.3 | 83.3 | 117.4 | 135.4 | 156.1
304 | 118 | 521.4 | 80.3 | 61.5 | 80.6 | 84.4 | 118.5 | 136.7 | 158.5
305 | 119 | 521.6 | 81.5 | 62.4 | 81.9 | 85.5 | 119.8 | 138.1 | 160.8
306 | 120 | 521.7 | 82.7 | 63.2 | 83.2 | 86.6 | 121.1 | 139.2 | 163.1
307 | 121 | 521.7 | 83.9 | 64.2 | 84.5 | 87.7 | 122.6 | 140.4 | 165.4
308 | 122 | 521.6 | 85 | 65.1 | 85.8 | 88.7 | 123.9 | 142 | 167.7
309 | 123 | 521.6 | 86.2 | 66 | 87.1 | 89.8 | 125.1 | 143.1 | 170
310 | 124 | 521.4 | 87.3 | 66.9 | 88.4 | 90.9 | 126.3 | 144.1 | 172.3
311 | 125 | 521 | 88.5 | 67.8 | 89.7 | 91.9 | 127.4 | 145.5 | 174.6
312 | 126 | 520.5 | 89.6 | 68.8 | 91.1 | 93 | 128.6 | 146.5 | 176.8
313 | 127 | 519.9 | 90.8 | 69.7 | 92.4 | 94 | 129.9 | 147.3 | 179.1
314 | 128 | 519.3 | 91.9 | 70.6 | 93.8 | 95 | 131.2 | 148.3 | 181.3
315 | 129 | 518.8 | 93.1 | 71.6 | 95.2 | 96.1 | 132.4 | 149.2 | 183.5
316 | 130 | 518.6 | 94.2 | 72.5 | 96.6 | 97.1 | 133.5 | 150.2 | 185.7
317 | 131 | 518.6 | 95.3 | 73.5 | 98.1 | 98.1 | 134.6 | 151.1 | 187.8
318 | 132 | 518.5 | 96.4 | 74.5 | 99.6 | 99.1 | 135.7 | 151.9 | 189.9
319 | 133 | 518.4 | 97.5 | 75.4 | 101.1 | 100.1 | 136.7 | 152.9 | 192
320 | 134 | 518.4 | 98.6 | 76.3 | 102.8 | 101.1 | 137.7 | 153.7 | 194.2
321 | 135 | 518.4 | 99.7 | 77.3 | 104.5 | 102.1 | 138.7 | 154.5 | 196.2
322 | 136 | 518.4 | 100.8 | 78.3 | 106.4 | 103 | 139.7 | 155.4 | 198.2
323 | 137 | 518.6 | 101.8 | 79.2 | 108.4 | 104 | 140.8 | 156.4 | 200.3
324 | 138 | 518.7 | 102.9 | 80.1 | 110.6 | 105 | 141.9 | 157.5 | 202.4
325 | 139 | 518.7 | 103.9 | 81.1 | 113.1 | 105.9 | 143.1 | 158.3 | 204.4
326 | 140 | 518.5 | 104.9 | 82 | 115.8 | 106.8 | 144.1 | 159 | 206.5
327 | 141 | 518.3 | 105.9 | 83 | 118.4 | 107.7 | 145 | 159.9 | 208.5
328 | 142 | 518.3 | 106.8 | 83.9 | 120.9 | 108.6 | 146 | 160.9 | 210.5
329 | 143 | 518.5 | 107.7 | 84.9 | 123.3 | 109.5 | 147 | 161.8 | 212.5
330 | 144 | 518.4 | 108.6 | 85.8 | 125.6 | 110.4 | 148.1 | 162.7 | 214.4
331 | 145 | 518.6 | 109.5 | 86.7 | 127.7 | 111.3 | 149.1 | 163.8 | 216.4
332 | 146 | 518.8 | 110.3 | 87.7 | 129.9 | 112.3 | 149.9 | 164.9 | 218.4
333 | 147 | 518.9 | 111.2 | 88.6 | 132 | 113.2 | 150.9 | 165.6 | 220.3
334 | 148 | 519 | 112 | 89.6 | 134.1 | 114.1 | 151.9 | 166.6 | 222.2
335 | 149 | 519.3 | 112.7 | 90.5 | 136.3 | 115.1 | 152.9 | 167.2 | 224.1
336 | 150 | 519.4 | 113.4 | 91.4 | 138.3 | 116 | 153.9 | 167.6 | 226
337 | 151 | 519.4 | 114.2 | 92.3 | 140.3 | 117 | 154.9 | 168.3 | 227.9
338 | 152 | 519.3 | 115 | 93.3 | 142.2 | 117.9 | 155.8 | 169.1 | 229.7
339 | 153 | 519.3 | 115.8 | 94.2 | 144.1 | 118.8 | 156.6 | 170.1 | 231.6
340 | 154 | 519.2 | 116.6 | 95.2 | 145.9 | 119.8 | 157.5 | 170.8 | 233.5
341 | 155 | 519.2 | 117.5 | 96.1 | 147.7 | 120.7 | 158.3 | 171.5 | 235.4
342 | 156 | 519 | 118.3 | 97 | 149.4 | 121.6 | 159.1 | 172.2 | 237.2
343 | 157 | 519 | 119.2 | 97.9 | 151 | 122.6 | 159.8 | 172.6 | 239
344 | 158 | 519.1 | 119.8 | 98.9 | 152.5 | 123.6 | 160.9 | 173.1 | 240.8
345 | 159 | 519.3 | 120.3 | 99.8 | 154 | 124.5 | 161.9 | 173.6 | 242.6
346 | 160 | 519.5 | 120.9 | 100.8 | 155.4 | 125.5 | 162.7 | 174.2 | 244.4
347 | 161 | 519.8 | 121.5 | 101.7 | 156.7 | 126.5 | 163.6 | 175 | 246.1
348 | 162 | 520.1 | 122 | 102.7 | 157.9 | 127.5 | 164.4 | 175.7 | 247.9
349 | 163 | 520.3 | 122.7 | 103.6 | 159.1 | 128.5 | 165.3 | 176.5 | 249.6
350 | 164 | 520.5 | 123.3 | 104.5 | 160.3 | 129.5 | 166.2 | 177.3 | 251.3
351 | 165 | 520.6 | 124 | 105.5 | 161.4 | 130.5 | 166.9 | 178 | 253.1
352 | 166 | 520.7 | 124.7 | 106.5 | 162.5 | 131.5 | 167.8 | 178.9 | 254.8
353 | 167 | 521 | 125.4 | 107.4 | 163.6 | 132.4 | 168.5 | 179.7 | 256.5
354 | 168 | 521.1 | 126.2 | 108.4 | 164.7 | 133.3 | 169.1 | 180.3 | 258.1
355 | 169 | 521.2 | 126.9 | 109.3 | 165.9 | 134.2 | 169.9 | 180.6 | 259.8
356 | 170 | 521.3 | 127.7 | 110.3 | 167 | 135.1 | 170.6 | 181.2 | 261.4
357 | 171 | 521.4 | 128.4 | 111.3 | 168.1 | 136 | 171.4 | 181.7 | 263
358 | 172 | 521.1 | 129.2 | 112.3 | 169.2 | 136.9 | 172.3 | 182.2 | 264.6
359 | 173 | 521 | 129.9 | 113.3 | 170.4 | 137.8 | 173.1 | 183 | 266.1
360 | 174 | 521 | 130.7 | 114.3 | 171.5 | 138.7 | 173.8 | 183.4 | 267.7
361 | 175 | 521 | 131.4 | 115.3 | 172.7 | 139.6 | 174.5 | 183.9 | 269.3
362 | 176 | 521 | 132.1 | 116.4 | 173.8 | 140.5 | 175.1 | 184.4 | 270.8
363 | 177 | 521 | 132.8 | 117.4 | 174.9 | 141.4 | 175.8 | 184.8 | 272.3
364 | 178 | 521.1 | 133.5 | 118.4 | 176 | 142.3 | 176.3 | 185.3 | 273.8
365 | 179 | 521.3 | 134.2 | 119.4 | 177.1 | 143.2 | 177.1 | 185.7 | 275.3
366 | 180 | 521.6 | 134.9 | 120.5 | 178.2 | 144.1 | 177.8 | 186 | 276.8
367 | 181 | 521.8 | 135.6 | 121.6 | 179.4 | 145 | 178.3 | 186.3 | 278.3
368 | 182 | 522 | 136.3 | 122.6 | 180.5 | 146 | 178.8 | 187 | 279.7
369 | 183 | 522 | 136.9 | 123.7 | 181.6 | 146.8 | 179.6 | 187.7 | 281.2
370 | 184 | 522 | 137.5 | 124.8 | 182.7 | 147.7 | 180.3 | 188.2 | 282.6
371 | 185 | 522.2 | 138 | 125.8 | 183.9 | 148.6 | 181 | 188.8 | 284
372 | 186 | 522.6 | 138.4 | 126.9 | 185 | 149.4 | 181.7 | 189.1 | 285.4
373 | 187 | 522.8 | 138.8 | 127.9 | 186.1 | 150.3 | 182.4 | 189.5 | 286.8
374 | 188 | 522.7 | 139.2 | 129 | 187.1 | 151 | 183 | 190.1 | 288.2
375 | 189 | 522.6 | 139.6 | 130.2 | 187.9 | 151.8 | 183.7 | 190.7 | 289.5
376 | 190 | 522.6 | 140 | 131.2 | 188.5 | 152.5 | 184.3 | 191.3 | 290.9
377 | 191 | 522.5 | 140.4 | 132.3 | 189 | 153.3 | 184.8 | 192 | 292.2
378 | 192 | 522.2 | 140.9 | 133.3 | 189.5 | 154.1 | 185.3 | 192.3 | 293.5
379 | 193 | 522.2 | 141.3 | 134.3 | 190 | 154.8 | 185.8 | 193.1 | 294.9
380 | 194 | 522.1 | 141.8 | 135.3 | 190.4 | 155.6 | 186.5 | 193.6 | 296.2
381 | 195 | 522 | 142.3 | 136.3 | 190.9 | 156.4 | 187 | 194.2 | 297.5
382 | 196 | 522 | 142.8 | 137.3 | 191.4 | 157.1 | 187.6 | 194.9 | 298.7
383 | 197 | 521.8 | 143.3 | 138.2 | 192 | 157.9 | 188.2 | 195.2 | 300
384 | 198 | 521.6 | 143.8 | 139.2 | 192.6 | 158.6 | 188.9 | 195.4 | 301.2
385 | 199 | 521.1 | 144.4 | 140.1 | 193.2 | 159.4 | 189.2 | 196 | 302.4
386 | 200 | 520.7 | 145 | 141 | 193.9 | 160.1 | 189.8 | 196.7 | 303.6
387 | 201 | 520.4 | 145.6 | 141.8 | 194.7 | 160.9 | 190.1 | 197.3 | 304.8
388 | 202 | 520 | 146.3 | 142.7 | 195.6 | 161.7 | 190.6 | 198 | 305.9
389 | 203 | 519.9 | 147 | 143.5 | 196.4 | 162.5 | 191 | 198.7 | 307.1
390 | 204 | 519.9 | 147.7 | 144.3 | 197.4 | 163.4 | 191.3 | 199.3 | 308.2
391 | 205 | 519.8 | 148.5 | 145.1 | 198.3 | 164.4 | 191.6 | 200 | 309.4
392 | 206 | 519.6 | 149.3 | 145.9 | 199.3 | 165.3 | 192 | 200.6 | 310.4
393 | 207 | 519.6 | 150.1 | 146.6 | 200.4 | 166.3 | 192.4 | 201.3 | 311.5
394 | 208 | 519.7 | 150.9 | 147.4 | 201.6 | 167.3 | 192.8 | 201.8 | 312.6
395 | 209 | 519.4 | 151.6 | 148.2 | 203 | 168.4 | 193 | 202.2 | 313.6
396 | 210 | 519.1 | 152.3 | 148.9 | 204.4 | 169.5 | 193.3 | 202.5 | 314.7
397 | 211 | 519.2 | 153 | 149.6 | 205.8 | 170.6 | 193.6 | 203 | 315.7
398 | 212 | 519.2 | 153.7 | 150.4 | 207.1 | 171.7 | 194.1 | 203.5 | 316.7
399 | 213 | 519 | 154.4 | 151.2 | 208.4 | 172.9 | 194.5 | 204 | 317.7
400 | 214 | 518.9 | 155.1 | 152 | 209.5 | 174.2 | 194.9 | 204.6 | 318.8
401 | 215 | 518.9 | 155.8 | 152.7 | 210.5 | 175.5 | 195.3 | 205 | 319.8
402 | 216 | 518.8 | 156.5 | 153.4 | 211.4 | 177 | 195.7 | 205.5 | 320.8
403 | 217 | 518.8 | 157.2 | 154.1 | 212.2 | 178.5 | 196.1 | 206.2 | 321.8
404 | 218 | 518.8 | 157.9 | 154.8 | 212.9 | 180.1 | 196.3 | 206.8 | 322.8
405 | 219 | 518.5 | 158.6 | 155.5 | 213.6 | 181.6 | 196.6 | 207.2 | 323.8
406 | 220 | 518.5 | 159.3 | 156.1 | 214.3 | 183.2 | 196.9 | 207.6 | 324.7
407 | 221 | 518.6 | 160 | 156.8 | 215.1 | 184.9 | 197.3 | 208.2 | 325.6
408 | 222 | 518.7 | 160.6 | 157.5 | 216 | 186.7 | 197.5 | 208.5 | 326.5
409 | 223 | 518.8 | 161.3 | 158.2 | 216.7 | 188.8 | 197.9 | 208.7 | 327.4
410 | 224 | 518.8 | 162 | 158.8 | 217.3 | 191.2 | 198.2 | 209.2 | 328.3
411 | 225 | 519 | 162.6 | 159.5 | 217.9 | 193.8 | 198.6 | 209.7 | 329.2
412 | 226 | 519.2 | 163.3 | 160.2 | 218.3 | 196.6 | 198.9 | 210.3 | 330.1
413 | 227 | 519.3 | 163.9 | 161 | 218.9 | 198.9 | 199.3 | 210.7 | 330.9
414 | 228 | 519.6 | 164.6 | 161.7 | 219.6 | 201.1 | 199.7 | 211.4 | 331.7
415 | 229 | 519.7 | 165.2 | 162.4 | 220.3 | 203.2 | 200.1 | 212.2 | 332.6
416 | 230 | 519.8 | 165.9 | 163.1 | 221.2 | 205.2 | 200.4 | 213 | 333.4
417 | 231 | 519.9 | 166.6 | 163.9 | 221.9 | 207.1 | 200.8 | 213.7 | 334.3
418 | 232 | 520.1 | 167.2 | 164.6 | 222.5 | 208.8 | 201.2 | 214.5 | 335.1
419 | 233 | 520.3 | 167.9 | 165.4 | 223.1 | 210.5 | 201.5 | 215.2 | 335.9
420 | 234 | 520.3 | 168.6 | 166.1 | 223.7 | 212.2 | 201.8 | 216 | 336.6
421 | 235 | 520.5 | 169.3 | 166.8 | 224.4 | 213.7 | 202.1 | 216.8 | 337.4
422 | 236 | 520.5 | 170 | 167.5 | 225 | 215.2 | 202.4 | 217.2 | 338.2
423 | 237 | 520.6 | 170.7 | 168.3 | 225.5 | 216.7 | 202.7 | 217.9 | 339
424 | 238 | 520.7 | 171.4 | 169 | 226 | 218 | 202.9 | 218.7 | 339.8
425 | 239 | 520.9 | 172.2 | 169.7 | 226.5 | 219.3 | 203.2 | 219.3 | 340.6
426 | 240 | 521.1 | 172.9 | 170.4 | 227.1 | 220.4 | 203.3 | 220 | 341.3
427 | 241 | 521.2 | 173.6 | 171 | 227.7 | 221.4 | 203.5 | 220.6 | 342
428 | 242 | 521.4 | 174.3 | 171.7 | 228.1 | 222.4 | 203.7 | 221.2 | 342.7
429 | 243 | 521.4 | 175 | 172.3 | 228.5 | 223.3 | 203.8 | 221.7 | 343.5
430 | 244 | 521.4 | 175.6 | 172.9 | 228.9 | 224.1 | 204 | 222.5 | 344.2
431 | 245 | 521.5 | 176.3 | 173.4 | 229.3 | 224.8 | 204.1 | 223.1 | 344.9
432 | 246 | 521.3 | 177 | 173.9 | 229.7 | 225.5 | 204.1 | 224 | 345.6
433 | 247 | 521.1 | 177.7 | 174.3 | 229.9 | 226.1 | 204.2 | 224.8 | 346.3
434 | 248 | 520.9 | 178.4 | 174.4 | 230.2 | 226.6 | 204.3 | 225.6 | 347
435 | 249 | 520.7 | 179 | 174.2 | 230.4 | 227.1 | 204.4 | 226.5 | 347.6
436 | 250 | 520.6 | 179.7 | 174 | 230.4 | 227.6 | 204.5 | 227.2 | 348.3
437 | 251 | 520.5 | 180.4 | 174.1 | 230.8 | 228 | 204.5 | 228.1 | 349
438 | 252 | 520.3 | 181.1 | 174.5 | 231.2 | 228.3 | 204.5 | 228.7 | 349.7
439 | 253 | 520.1 | 181.8 | 174.9 | 231.6 | 228.7 | 204.6 | 229.6 | 350.4
440 | 254 | 520 | 182.5 | 175.4 | 232 | 229 | 204.7 | 230.3 | 351
441 | 255 | 519.9 | 183.2 | 176 | 232.4 | 229.2 | 204.8 | 230.9 | 351.6
442 | 256 | 519.6 | 183.9 | 176.7 | 233.1 | 229.5 | 204.8 | 231.3 | 352.2
443 | 257 | 519.6 | 184.5 | 177.4 | 234 | 229.7 | 204.8 | 232 | 352.8
444 | 258 | 519.6 | 185.2 | 178.2 | 234.6 | 229.9 | 204.9 | 232.9 | 353.3
445 | 259 | 519.5 | 185.9 | 178.9 | 235 | 230.1 | 205 | 233.9 | 353.9
446 | 260 | 519.5 | 186.5 | 179.6 | 235.3 | 230.3 | 205 | 235 | 354.4
447 | 261 | 519.4 | 187.2 | 180.4 | 235.6 | 230.5 | 205.2 | 235.7 | 355
448 | 262 | 519.3 | 187.8 | 181.1 | 235.9 | 230.7 | 205.3 | 236.7 | 355.6
449 | 263 | 519.3 | 188.5 | 181.9 | 236.5 | 230.9 | 205.4 | 237.6 | 356.1
450 | 264 | 519.4 | 189.1 | 182.6 | 237 | 231 | 205.5 | 238.3 | 356.7
451 | 265 | 519.3 | 189.8 | 183.4 | 237.5 | 231.1 | 205.6 | 239 | 357.3
452 | 266 | 519.3 | 190.4 | 184 | 238.1 | 231.2 | 205.7 | 239.5 | 357.8
453 | 267 | 519.3 | 191.1 | 184.7 | 238.5 | 231.4 | 205.8 | 240.6 | 358.3
454 | 268 | 519.1 | 191.7 | 185.4 | 239.1 | 231.5 | 206 | 241.4 | 358.8
455 | 269 | 519 | 192.3 | 186.1 | 240 | 231.6 | 206.1 | 242.1 | 359.3
456 | 270 | 518.8 | 193 | 186.8 | 241.1 | 231.8 | 206.2 | 242.9 | 359.8
457 | 271 | 518.9 | 193.6 | 187.5 | 242.5 | 232.1 | 206.4 | 243.7 | 360.3
458 | 272 | 519 | 194.2 | 188.2 | 243.9 | 232.6 | 206.5 | 243.9 | 360.8
459 | 273 | 519 | 194.8 | 188.9 | 245.4 | 233.1 | 206.6 | 244.5 | 361.2
460 | 274 | 519.1 | 195.4 | 189.6 | 246.8 | 233.6 | 206.8 | 244.8 | 361.7
461 | 275 | 519.2 | 196 | 190.3 | 248 | 234.1 | 206.9 | 245.6 | 362.1
462 | 276 | 519.1 | 196.6 | 191.1 | 249.2 | 234.6 | 207.1 | 245.9 | 362.5
463 | 277 | 519 | 197.2 | 191.8 | 250.2 | 235.1 | 207.3 | 246.4 | 362.9
464 | 278 | 519 | 197.9 | 192.5 | 251.3 | 235.6 | 207.5 | 246.8 | 363.4
465 | 279 | 519 | 198.5 | 193.3 | 252.1 | 236.1 | 207.7 | 247.4 | 363.8
466 | 280 | 518.9 | 199.1 | 194 | 252.9 | 236.7 | 207.9 | 247.7 | 364.2
467 | 281 | 518.9 | 199.7 | 194.7 | 253.7 | 237.3 | 208 | 247.9 | 364.6
468 | 282 | 519 | 200.4 | 195.4 | 254.5 | 237.9 | 208.2 | 248.4 | 365
469 | 283 | 519 | 201 | 196.1 | 255.2 | 238.6 | 208.4 | 249 | 365.4
470 | 284 | 519 | 201.7 | 196.8 | 255.9 | 239.9 | 208.6 | 249.3 | 365.7
471 | 285 | 518.7 | 202.3 | 197.6 | 256.8 | 241.4 | 208.8 | 249.2 | 366.1
472 | 286 | 518.7 | 203 | 198.3 | 257.4 | 242.6 | 209 | 250 | 366.4
473 | 287 | 518.7 | 203.7 | 199 | 257.9 | 243.7 | 209.2 | 250.6 | 366.8
474 | 288 | 518.7 | 204.4 | 199.8 | 258.5 | 244.7 | 209.4 | 251.5 | 367.1
475 | 289 | 518.9 | 205 | 200.5 | 259.1 | 245.8 | 209.7 | 251.8 | 367.5
476 | 290 | 519 | 205.7 | 201.2 | 259.6 | 246.8 | 209.9 | 252.2 | 367.9
477 | 291 | 518.9 | 206.4 | 201.9 | 260.1 | 247.8 | 210.1 | 252.3 | 368.3
478 | 292 | 518.8 | 207 | 202.6 | 260.7 | 248.7 | 210.3 | 252.7 | 368.7
479 | 293 | 518.7 | 207.7 | 203.3 | 261.3 | 249.6 | 210.5 | 253.2 | 369.1
480 | 294 | 518.6 | 208.4 | 204 | 261.7 | 250.4 | 210.7 | 253.6 | 369.5
481 | 295 | 518.6 | 209 | 204.7 | 262.1 | 251.2 | 210.9 | 253.8 | 369.8
482 | 296 | 518.4 | 209.7 | 205.3 | 262.8 | 251.9 | 211.1 | 254.2 | 370.2
483 | 297 | 518.4 | 210.4 | 206 | 263.4 | 252.7 | 211.4 | 254.4 | 370.6
484 | 298 | 518.3 | 211.1 | 206.6 | 263.9 | 253.4 | 211.6 | 254.4 | 370.9
485 | 299 | 518.4 | 211.7 | 207.3 | 264.1 | 254.1 | 211.8 | 254.4 | 371.3
486 | 300 | 518.5 | 212.4 | 208 | 264.3 | 254.7 | 212 | 254.7 | 371.6
487 | 301 | 518.6 | 213.1 | 208.7 | 264.7 | 255.2 | 212.3 | 255.1 | 371.9
488 | 302 | 518.6 | 213.8 | 209.4 | 265.2 | 255.7 | 212.5 | 255.1 | 372.2
489 | 303 | 518.5 | 214.5 | 210 | 265.8 | 256.1 | 212.8 | 255.3 | 372.5
490 | 304 | 518.4 | 215.2 | 210.7 | 266.5 | 256.2 | 213.1 | 255.5 | 372.9
491 | 305 | 518.4 | 215.9 | 211.4 | 267.1 | 256.6 | 213.4 | 255.7 | 373.2
492 | 306 | 518.3 | 216.5 | 212 | 267.6 | 257 | 213.8 | 255.7 | 373.5
493 | 307 | 518.1 | 217.1 | 212.7 | 268.2 | 257.4 | 214.2 | 255.9 | 373.8
494 | 308 | 518.2 | 217.8 | 213.5 | 268.7 | 257.9 | 214.7 | 256 | 374.1
495 | 309 | 518.2 | 218.5 | 214.2 | 269.2 | 258.2 | 215.1 | 255.7 | 374.5
496 | 310 | 518.2 | 219.1 | 214.9 | 269.7 | 258.6 | 215.5 | 256.1 | 374.8
497 | 311 | 518.2 | 219.7 | 215.7 | 270.1 | 259 | 216 | 256.7 | 375.2
498 | 312 | 518.1 | 220.4 | 216.4 | 270.4 | 259.5 | 216.5 | 257 | 375.5
499 | 313 | 517.9 | 221 | 217.2 | 270.8 | 260 | 216.9 | 257.3 | 375.8
500 | 314 | 518 | 221.7 | 217.9 | 271.3 | 260.4 | 217.4 | 258.2 | 376.1
501 | 315 | 518.2 | 222.3 | 218.6 | 271.8 | 260.9 | 217.8 | 258.8 | 376.4
502 | 316 | 518.3 | 223 | 219.3 | 272.4 | 261.2 | 218.2 | 259.5 | 376.7
503 | 317 | 518.3 | 223.6 | 220 | 273.1 | 261.7 | 218.5 | 259.9 | 377.1
504 | 318 | 518.4 | 224.2 | 220.8 | 273.7 | 262.2 | 218.9 | 260.5 | 377.4
505 | 319 | 518.5 | 224.9 | 221.5 | 274.3 | 262.8 | 219.3 | 261 | 377.8
506 | 320 | 518.6 | 225.5 | 222.1 | 274.9 | 263.3 | 219.7 | 261.6 | 378.1
507 | 321 | 518.7 | 226.2 | 222.8 | 275.5 | 263.8 | 220.2 | 261.9 | 378.3
508 | 322 | 518.9 | 226.8 | 223.4 | 275.9 | 264.3 | 220.6 | 262.3 | 378.6
509 | 323 | 518.8 | 227.4 | 224 | 276.4 | 264.8 | 221.1 | 262.3 | 379
510 | 324 | 519 | 228 | 224.7 | 277 | 265.3 | 221.7 | 262.6 | 379.3
511 | 325 | 519 | 228.6 | 225.3 | 277.6 | 265.8 | 222.2 | 263 | 379.6
512 | 326 | 518.8 | 229.2 | 226 | 278.2 | 266.2 | 222.7 | 263 | 379.9
513 | 327 | 518.8 | 229.8 | 226.7 | 278.8 | 266.7 | 223.2 | 263 | 380.2
514 | 328 | 518.8 | 230.3 | 227.3 | 279.4 | 267.2 | 223.6 | 263.4 | 380.5
515 | 329 | 518.8 | 230.9 | 227.9 | 279.9 | 267.6 | 224 | 263.7 | 380.8
516 | 330 | 518.7 | 231.6 | 228.5 | 280.5 | 268 | 224.4 | 263.5 | 381
517 | 331 | 518.5 | 232.2 | 229.2 | 281.3 | 268.4 | 224.7 | 264 | 381.3
518 | 332 | 518.6 | 232.7 | 229.8 | 281.9 | 268.9 | 225.2 | 263.9 | 381.6
519 | 333 | 518.7 | 233.3 | 230.5 | 282.6 | 269.6 | 225.7 | 263.8 | 381.9
520 | 334 | 518.7 | 233.9 | 231.2 | 283.2 | 270.1 | 226.1 | 264 | 382.2
521 | 335 | 518.7 | 234.5 | 231.9 | 283.8 | 270.5 | 226.7 | 264.2 | 382.5
522 | 336 | 518.8 | 235 | 232.5 | 284.5 | 270.9 | 227.2 | 264.8 | 382.8
523 | 337 | 518.9 | 235.5 | 233.2 | 285.2 | 271.5 | 227.6 | 265.4 | 383
524 | 338 | 518.9 | 236 | 233.8 | 285.8 | 272 | 228.1 | 265.6 | 383.2
525 | 339 | 519 | 236.5 | 234.4 | 286.4 | 272.6 | 228.6 | 265.6 | 383.5
526 | 340 | 519 | 236.9 | 235.1 | 287 | 273.1 | 229.1 | 265.8 | 383.8
527 | 341 | 519.1 | 237.3 | 235.9 | 287.5 | 273.8 | 229.6 | 265.8 | 384.1
528 | 342 | 519.1 | 237.7 | 236.6 | 288.1 | 274.5 | 230.2 | 265.6 | 384.3
529 | 343 | 519.2 | 238.2 | 237.2 | 288.7 | 274.9 | 230.8 | 265.7 | 384.6
530 | 344 | 519.3 | 238.6 | 237.8 | 289.3 | 275.4 | 231.3 | 266 | 384.8
531 | 345 | 519.5 | 239 | 238.4 | 289.9 | 275.9 | 231.8 | 266.6 | 385
532 | 346 | 519.7 | 239.4 | 239 | 290.4 | 276.6 | 232.4 | 266.8 | 385.3
533 | 347 | 519.6 | 239.8 | 239.6 | 291 | 277.2 | 232.9 | 266.9 | 385.5
534 | 348 | 519.6 | 240.3 | 240.2 | 291.5 | 277.8 | 233.3 | 267.3 | 385.7
535 | 349 | 519.6 | 240.7 | 240.8 | 292 | 278.4 | 233.8 | 267.9 | 386
536 | 350 | 519.5 | 241.2 | 241.4 | 292.6 | 278.9 | 234.1 | 267.9 | 386.2
537 | 351 | 519.1 | 241.6 | 242.1 | 293.1 | 279.6 | 234.5 | 267.9 | 386.5
538 | 352 | 518.9 | 242.1 | 242.7 | 293.7 | 280.3 | 234.8 | 268.1 | 386.7
539 | 353 | 518.9 | 242.5 | 243.3 | 294.3 | 281 | 235 | 268.6 | 387
540 | 354 | 518.9 | 243 | 244 | 294.8 | 281.6 | 235.2 | 269 | 387.2
541 | 355 | 518.9 | 243.5 | 244.7 | 295.3 | 282.2 | 235.4 | 269.3 | 387.4
542 | 356 | 518.7 | 244 | 245.3 | 295.8 | 282.7 | 235.5 | 269.4 | 387.7
543 | 357 | 518.5 | 244.4 | 246 | 296.2 | 283.3 | 235.7 | 269.6 | 387.9
544 | 358 | 518.4 | 244.9 | 246.6 | 296.6 | 284 | 235.9 | 269.8 | 388.1
545 | 359 | 518.2 | 245.4 | 247.2 | 297.1 | 284.6 | 236.1 | 270.1 | 388.3
546 | 360 | 518.2 | 245.9 | 247.9 | 297.5 | 285.1 | 236.3 | 270.2 | 388.5
547 | 361 | 518.1 | 246.3 | 248.5 | 297.9 | 285.6 | 236.6 | 270.3 | 388.8
548 | 362 | 518 | 246.7 | 249.1 | 298.4 | 286.2 | 236.8 | 270.7 | 389
549 | 363 | 517.7 | 247.1 | 249.6 | 298.9 | 286.9 | 237.2 | 271.4 | 389.2
550 | 364 | 517.4 | 247.5 | 250.2 | 299.4 | 287.5 | 237.5 | 272.4 | 389.4
551 | 365 | 517.4 | 247.9 | 250.8 | 299.9 | 288.2 | 237.8 | 272.9 | 389.6
552 | 366 | 517.6 | 248.4 | 251.4 | 300.4 | 288.8 | 238.1 | 273.6 | 389.8
553 | 367 | 517.7 | 248.9 | 252 | 300.9 | 289.5 | 238.4 | 273.9 | 389.9
554 | 368 | 517.6 | 249.4 | 252.6 | 301.4 | 290.4 | 238.7 | 274 | 390.1
555 | 369 | 517.5 | 249.9 | 253.2 | 302 | 291.1 | 239 | 274.3 | 390.3
556 | 370 | 517.6 | 250.4 | 253.8 | 302.5 | 291.9 | 239.3 | 274.5 | 390.5
557 | 371 | 517.9 | 250.9 | 254.4 | 303 | 292.7 | 239.6 | 274.7 | 390.7
558 | 372 | 518 | 251.4 | 255 | 303.6 | 293.5 | 239.9 | 274.8 | 390.9
559 | 373 | 518 | 252 | 255.7 | 304.1 | 294.2 | 240.2 | 274.7 | 391.1
560 | 374 | 518.2 | 252.6 | 256.3 | 304.6 | 295 | 240.5 | 274.9 | 391.3
561 | 375 | 518.3 | 253.2 | 257 | 305.1 | 295.8 | 240.8 | 275.1 | 391.6
562 | 376 | 518.3 | 253.8 | 257.6 | 305.7 | 296.5 | 241.1 | 275.1 | 391.8
563 | 377 | 518.5 | 254.3 | 258.2 | 306.2 | 297.2 | 241.5 | 275.4 | 392
564 | 378 | 518.5 | 254.9 | 258.9 | 306.7 | 297.9 | 241.7 | 275.9 | 392.3
565 | 379 | 518.4 | 255.5 | 259.5 | 307.2 | 298.6 | 242.1 | 276.5 | 392.5
566 | 380 | 518.4 | 256 | 260.2 | 307.8 | 299.5 | 242.4 | 277.3 | 392.7
567 | 381 | 518.3 | 256.6 | 260.8 | 308.3 | 300.5 | 242.7 | 277.7 | 392.9
568 | 382 | 518.3 | 257.2 | 261.5 | 308.9 | 301.4 | 243.1 | 278.1 | 393.1
569 | 383 | 518.4 | 257.7 | 262.1 | 309.4 | 302.2 | 243.4 | 278.6 | 393.2
570 | 384 | 518.4 | 258.3 | 262.7 | 309.8 | 302.9 | 243.7 | 278.3 | 393.4
571 | 385 | 518.2 | 258.8 | 263.4 | 310.2 | 303.5 | 244 | 278.2 | 393.6
572 | 386 | 518.4 | 259.4 | 264 | 310.6 | 304.1 | 244.3 | 278.8 | 393.7
573 | 387 | 518.4 | 259.9 | 264.6 | 311 | 304.9 | 244.6 | 279 | 393.9
574 | 388 | 518.6 | 260.5 | 265.3 | 311.4 | 305.7 | 244.9 | 279.1 | 394
575 | 389 | 518.6 | 261.1 | 266 | 311.9 | 306.5 | 245.3 | 279.1 | 394.2
576 | 390 | 518.6 | 261.6 | 266.7 | 312.3 | 307.2 | 245.7 | 279 | 394.3
577 | 391 | 518.6 | 262.2 | 267.3 | 312.8 | 307.9 | 246.2 | 279.5 | 394.5
578 | 392 | 518.8 | 262.7 | 267.9 | 313.2 | 308.7 | 246.6 | 279.6 | 394.6
579 | 393 | 518.9 | 263.2 | 268.5 | 313.6 | 309.3 | 247 | 279.9 | 394.8
580 | 394 | 518.7 | 263.8 | 269.1 | 313.9 | 309.8 | 247.4 | 279.7 | 394.9
581 | 395 | 518.6 | 264.3 | 269.7 | 314.4 | 310.5 | 247.8 | 279.9 | 395
582 | 396 | 518.4 | 264.9 | 270.4 | 314.8 | 311.1 | 248.2 | 280.2 | 395.1
583 | 397 | 518.3 | 265.3 | 271 | 315.3 | 311.8 | 248.5 | 280.6 | 395.3
584 | 398 | 518.1 | 265.9 | 271.7 | 315.7 | 312.5 | 248.8 | 280.4 | 395.4
585 | 399 | 518.1 | 266.4 | 272.3 | 316.1 | 313.2 | 249.2 | 280.5 | 395.6
586 | 400 | 518.1 | 266.9 | 272.9 | 316.6 | 313.9 | 249.4 | 280.4 | 395.8
587 | 401 | 518.1 | 267.5 | 273.4 | 317 | 314.4 | 249.7 | 280.5 | 396
588 | 402 | 518.4 | 268 | 274.1 | 317.5 | 314.9 | 249.9 | 280.4 | 396.2
589 | 403 | 518.5 | 268.6 | 274.6 | 318 | 315.5 | 250.2 | 280.3 | 396.3
590 | 404 | 518.5 | 269.1 | 275.2 | 318.4 | 316.2 | 250.4 | 280.5 | 396.5
591 | 405 | 518.7 | 269.7 | 275.8 | 318.9 | 316.8 | 250.7 | 280.4 | 396.7
592 | 406 | 518.7 | 270.3 | 276.5 | 319.5 | 317.4 | 250.9 | 280.3 | 396.8
593 | 407 | 518.5 | 270.8 | 277.1 | 320 | 318 | 251.1 | 280.4 | 397
594 | 408 | 518.2 | 271.4 | 277.8 | 320.5 | 318.5 | 251.3 | 280.7 | 397.2
595 | 409 | 518.2 | 271.9 | 278.5 | 321 | 319.1 | 251.4 | 281.1 | 397.4
596 | 410 | 518.2 | 272.3 | 279.1 | 321.4 | 319.7 | 251.6 | 282 | 397.5
597 | 411 | 518.1 | 272.8 | 279.8 | 321.8 | 320.3 | 251.7 | 282.7 | 397.6
598 | 412 | 518.1 | 273.2 | 280.4 | 322.2 | 320.9 | 251.8 | 283.3 | 397.8
599 | 413 | 518.1 | 273.7 | 281.1 | 322.6 | 321.5 | 252 | 283.1 | 397.9
600 | 414 | 518 | 274.3 | 281.6 | 323.1 | 321.9 | 252.2 | 283 | 398.1
601 | 415 | 518.1 | 274.9 | 282.3 | 323.5 | 322.5 | 252.4 | 282.9 | 398.2
602 | 416 | 518.1 | 275.5 | 283 | 323.9 | 323.2 | 252.7 | 283.3 | 398.3
603 | 417 | 518 | 276 | 283.7 | 324.4 | 323.8 | 253.1 | 283.9 | 398.3
604 | 418 | 518 | 276.6 | 284.3 | 324.8 | 324.4 | 253.4 | 284.4 | 398.4
605 | 419 | 517.9 | 277.2 | 284.9 | 325.3 | 325 | 253.6 | 284.6 | 398.5
606 | 420 | 517.6 | 277.8 | 285.6 | 325.7 | 325.7 | 253.8 | 284.9 | 398.7
607 | 421 | 517.5 | 278.4 | 286.2 | 326.1 | 326.5 | 254 | 285.3 | 398.8
608 | 422 | 517.5 | 279 | 286.9 | 326.4 | 327.3 | 254.1 | 285.4 | 398.9
609 | 423 | 517.3 | 279.6 | 287.5 | 326.8 | 328 | 254.2 | 285.3 | 399
610 | 424 | 517.3 | 280.1 | 288.1 | 327.3 | 328.8 | 254.4 | 285.5 | 399.1
611 | 425 | 517.3 | 280.7 | 288.7 | 327.7 | 329.6 | 254.6 | 286.1 | 399.2
612 | 426 | 517.4 | 281.3 | 289.4 | 328.1 | 330.3 | 254.7 | 286.3 | 399.3
613 | 427 | 517.5 | 281.9 | 290 | 328.5 | 331.1 | 254.8 | 286.3 | 399.5
614 | 428 | 517.5 | 282.5 | 290.6 | 328.8 | 331.9 | 255 | 286.4 | 399.6
615 | 429 | 517.5 | 283.1 | 291.3 | 329.3 | 332.7 | 255.1 | 286.7 | 399.7
616 | 430 | 517.7 | 283.7 | 291.9 | 329.7 | 333.7 | 255.3 | 287.1 | 399.8
617 | 431 | 517.9 | 284.3 | 292.5 | 330.1 | 334.7 | 255.4 | 287.3 | 400
618 | 432 | 517.9 | 284.9 | 293.1 | 330.4 | 335.5 | 255.4 | 287.8 | 400.1
619 | 433 | 518.1 | 285.5 | 293.7 | 330.9 | 336.5 | 255.4 | 288 | 400.2
620 | 434 | 518.4 | 286.1 | 294.3 | 331.3 | 337.3 | 255.4 | 288.5 | 400.3
621 | 435 | 518.5 | 286.7 | 294.9 | 331.8 | 338.2 | 255.5 | 289 | 400.5
622 | 436 | 518.5 | 287.2 | 295.5 | 332.2 | 339 | 255.6 | 289 | 400.6
623 | 437 | 518.4 | 287.8 | 296.1 | 332.6 | 339.7 | 255.8 | 289.2 | 400.7
624 | 438 | 518.4 | 288.4 | 296.7 | 332.9 | 340.4 | 256 | 289.5 | 400.8
625 | 439 | 518.5 | 289 | 297.2 | 333.4 | 341.2 | 256.1 | 289.9 | 400.9
626 | 440 | 518.5 | 289.6 | 297.8 | 333.9 | 342.1 | 256.2 | 290.3 | 401.1
627 | 441 | 518.6 | 290.1 | 298.4 | 334.4 | 342.9 | 256.4 | 290.6 | 401.2
628 | 442 | 518.8 | 290.7 | 299 | 334.9 | 343.8 | 256.5 | 290.6 | 401.3
629 | 443 | 518.9 | 291.2 | 299.7 | 335.4 | 344.5 | 256.5 | 290.7 | 401.5
630 | 444 | 518.9 | 291.8 | 300.4 | 335.8 | 345.3 | 256.6 | 291.3 | 401.6
631 | 445 | 519.1 | 292.4 | 301 | 336.1 | 346 | 256.6 | 291.4 | 401.8
632 | 446 | 519.2 | 292.9 | 301.5 | 336.5 | 346.5 | 256.8 | 291.9 | 401.9
633 | 447 | 519.2 | 293.5 | 302 | 336.8 | 347.1 | 257.1 | 292.1 | 402.1
634 | 448 | 519.3 | 294 | 302.5 | 337.2 | 347.7 | 257.3 | 292.4 | 402.2
635 | 449 | 519.6 | 294.5 | 303.1 | 337.5 | 348.3 | 257.6 | 292.7 | 402.4
636 | 450 | 519.9 | 295.1 | 303.6 | 337.8 | 348.9 | 258 | 293 | 402.4
637 | 451 | 520.2 | 295.6 | 304.2 | 338.2 | 349.7 | 258.2 | 293.1 | 402.5
638 | 452 | 520.4 | 296.2 | 304.7 | 338.6 | 350.5 | 258.5 | 293.2 | 402.6
639 | 453 | 520.5 | 296.7 | 305.3 | 339 | 351.1 | 258.8 | 293.4 | 402.8
640 | 454 | 520.4 | 297.2 | 305.9 | 339.4 | 351.8 | 259.2 | 293.6 | 402.9
641 | 455 | 520.2 | 297.7 | 306.6 | 339.8 | 352.5 | 259.5 | 294.2 | 403
642 | 456 | 520.1 | 298.3 | 307.3 | 340.4 | 353.3 | 259.8 | 294.4 | 403.1
643 | 457 | 519.9 | 298.8 | 307.9 | 340.9 | 354 | 260.2 | 294.6 | 403.2
644 | 458 | 520 | 299.3 | 308.6 | 341.4 | 354.6 | 260.6 | 294.6 | 403.3
645 | 459 | 520 | 299.8 | 309.2 | 341.9 | 355.3 | 261 | 294.7 | 403.4
646 | 460 | 519.9 | 300.4 | 309.8 | 342.3 | 355.9 | 261.3 | 295.3 | 403.5
647 | 461 | 519.8 | 300.9 | 310.5 | 342.8 | 356.5 | 261.6 | 295.8 | 403.6
648 | 462 | 520 | 301.5 | 311.1 | 343.3 | 357.2 | 261.9 | 295.6 | 403.7
649 | 463 | 520.1 | 302 | 311.7 | 343.8 | 357.9 | 262.1 | 295.7 | 403.8
650 | 464 | 520.2 | 302.6 | 312.3 | 344.2 | 358.6 | 262.4 | 296.4 | 404
651 | 465 | 520.3 | 303.1 | 312.9 | 344.7 | 359.3 | 262.8 | 296.5 | 404.1
652 | 466 | 520.3 | 303.7 | 313.4 | 345.2 | 360.1 | 263.1 | 297 | 404.2
653 | 467 | 520.1 | 304.2 | 314 | 345.8 | 360.9 | 263.5 | 297.6 | 404.4
654 | 468 | 519.8 | 304.8 | 314.6 | 346.3 | 361.6 | 263.8 | 297.7 | 404.5
655 | 469 | 519.8 | 305.4 | 315.2 | 346.9 | 362.3 | 264.3 | 297.8 | 404.6
656 | 470 | 519.8 | 306 | 315.8 | 347.4 | 363.1 | 264.7 | 298.1 | 404.6
657 | 471 | 519.8 | 306.5 | 316.4 | 347.9 | 363.8 | 265.1 | 298.5 | 404.8
658 | 472 | 519.6 | 307 | 316.8 | 348.5 | 364.3 | 265.5 | 298.5 | 404.9
659 | 473 | 519.4 | 307.6 | 317.3 | 349 | 365 | 265.8 | 298.4 | 405
660 | 474 | 519.6 | 308.2 | 317.9 | 349.4 | 365.6 | 266.2 | 298.5 | 405.2
661 | 475 | 519.8 | 308.7 | 318.7 | 349.9 | 366.4 | 266.6 | 298.7 | 405.3
662 | 476 | 519.9 | 309.2 | 319.4 | 350.4 | 367 | 267 | 299.1 | 405.5
663 | 477 | 519.6 | 309.7 | 320 | 350.7 | 367.6 | 267.5 | 299.1 | 405.6
664 | 478 | 519.5 | 310.2 | 320.5 | 351.1 | 368.1 | 268.3 | 299.2 | 405.7
665 | 479 | 519.5 | 310.7 | 321.1 | 351.5 | 368.6 | 269 | 299.1 | 405.8
666 | 480 | 519.5 | 311.2 | 321.6 | 351.9 | 369.1 | 269.7 | 299.2 | 405.9
667 | 481 | 519.3 | 311.8 | 322.1 | 352.3 | 369.6 | 270.5 | 299.7 | 406
668 | 482 | 519.1 | 312.3 | 322.7 | 352.7 | 370.2 | 271.1 | 300 | 406
669 | 483 | 519 | 312.9 | 323.3 | 353.2 | 370.8 | 271.6 | 300.2 | 406.1
670 | 484 | 518.9 | 313.4 | 323.9 | 353.6 | 371.5 | 272.1 | 300.8 | 406.2
671 | 485 | 518.9 | 314 | 324.4 | 354 | 372.1 | 272.6 | 301.6 | 406.2
672 | 486 | 519 | 314.5 | 325 | 354.5 | 372.6 | 273.4 | 301.6 | 406.3
673 | 487 | 519 | 315.1 | 325.6 | 354.9 | 373.2 | 273.9 | 301.9 | 406.4
674 | 488 | 518.8 | 315.7 | 326.2 | 355.4 | 373.7 | 274.4 | 302.1 | 406.6
675 | 489 | 518.7 | 316.2 | 326.7 | 356 | 374.3 | 274.9 | 302.5 | 406.7
676 | 490 | 518.6 | 316.8 | 327.2 | 356.6 | 375 | 275.5 | 302.6 | 406.8
677 | 491 | 518.4 | 317.3 | 327.8 | 357.2 | 375.4 | 276.1 | 302.6 | 406.9
678 | 492 | 518.3 | 317.9 | 328.3 | 357.8 | 376.2 | 276.7 | 302.6 | 407
679 | 493 | 518.3 | 318.4 | 328.9 | 358.4 | 376.9 | 277.3 | 302.5 | 407.2
680 | 494 | 518.5 | 318.9 | 329.5 | 359 | 377.5 | 277.8 | 302.9 | 407.4
681 | 495 | 518.6 | 319.5 | 330 | 359.6 | 378.1 | 278.4 | 302.8 | 407.5
682 | 496 | 518.6 | 320 | 330.5 | 360.2 | 378.7 | 278.9 | 303 | 407.6
683 | 497 | 518.5 | 320.5 | 331.1 | 360.8 | 379.3 | 279.4 | 303.3 | 407.7
684 | 498 | 518.4 | 321 | 331.7 | 361.4 | 379.8 | 279.8 | 304.2 | 407.8
685 | 499 | 518.5 | 321.6 | 332.3 | 362 | 380.3 | 280.2 | 304.4 | 407.9
686 | 500 | 518.5 | 322.1 | 332.8 | 362.6 | 380.9 | 280.6 | 304.9 | 408
687 | 501 | 518.5 | 322.6 | 333.3 | 363.2 | 381.5 | 281.1 | 305.2 | 408.1
688 | 502 | 518.5 | 323.2 | 333.9 | 363.8 | 382.1 | 281.5 | 305.2 | 408.2
689 | 503 | 518.6 | 323.7 | 334.6 | 364.4 | 382.7 | 282 | 305 | 408.4
690 | 504 | 518.8 | 324.3 | 335.3 | 365 | 383.4 | 282.4 | 305.7 | 408.5
691 | 505 | 519 | 324.8 | 335.9 | 365.6 | 384 | 282.8 | 305.8 | 408.6
692 | 506 | 519.1 | 325.3 | 336.5 | 366.2 | 384.7 | 283.2 | 305.6 | 408.7
693 | 507 | 519.3 | 325.9 | 337 | 366.8 | 385.2 | 283.7 | 306.4 | 408.8
694 | 508 | 519.2 | 326.5 | 337.6 | 367.4 | 385.7 | 284.1 | 306.8 | 408.8
695 | 509 | 519.2 | 327.1 | 337.7 | 368 | 386.4 | 284.5 | 306.9 | 408.9
696 | 510 | 519.4 | 327.6 | 338.4 | 368.5 | 386.8 | 284.8 | 307.5 | 408.9
697 | 511 | 519.6 | 328.1 | 339.1 | 369.1 | 387.2 | 285.1 | 308.1 | 409
698 | 512 | 519.7 | 328.6 | 339.7 | 369.7 | 387.7 | 285.5 | 307.5 | 409.2
699 | 513 | 519.7 | 329.2 | 340.3 | 370.4 | 388.2 | 285.8 | 307.6 | 409.2
700 | 514 | 519.8 | 329.7 | 340.9 | 371 | 388.7 | 286.3 | 307.9 | 409.4
701 | 515 | 519.8 | 330.3 | 341.4 | 371.6 | 389.2 | 286.7 | 308.2 | 409.5
702 | 516 | 519.6 | 330.8 | 341.9 | 372.2 | 390 | 287.2 | 308.6 | 409.7
703 | 517 | 519.7 | 331.3 | 342.4 | 372.9 | 390.7 | 287.6 | 309 | 409.8
704 | 518 | 519.5 | 331.9 | 343 | 373.5 | 391.4 | 288 | 308.9 | 410
705 | 519 | 519.4 | 332.4 | 343.7 | 374.2 | 392.1 | 288.5 | 308.9 | 410.1
706 | 520 | 519.3 | 332.9 | 344.3 | 374.9 | 392.9 | 289 | 308.6 | 410.2
707 | 521 | 519.3 | 333.5 | 344.8 | 375.5 | 393.5 | 289.4 | 309 | 410.3
708 | 522 | 519.2 | 334 | 345.4 | 376.2 | 394 | 289.8 | 309.5 | 410.4
709 | 523 | 519.2 | 334.6 | 346 | 376.8 | 394.5 | 290.2 | 309.5 | 410.5
710 | 524 | 519.1 | 335.1 | 346.6 | 377.4 | 395 | 290.5 | 310.5 | 410.6
711 | 525 | 519 | 335.7 | 347.3 | 378 | 395.6 | 290.9 | 310.7 | 410.6
712 | 526 | 519 | 336.2 | 348 | 378.6 | 396 | 291.3 | 311 | 410.7
713 | 527 | 519 | 336.7 | 348.6 | 379.2 | 396.5 | 291.7 | 312.1 | 410.8
714 | 528 | 518.8 | 337.2 | 349.2 | 379.7 | 396.9 | 292 | 312.2 | 410.9
715 | 529 | 518.6 | 337.8 | 349.9 | 380.3 | 397.3 | 292.3 | 312.5 | 411
716 | 530 | 518.5 | 338.4 | 350.5 | 380.9 | 397.6 | 292.7 | 312.4 | 411
717 | 531 | 518.5 | 339 | 351.1 | 381.5 | 398 | 293.1 | 312.5 | 411.1
718 | 532 | 518.7 | 339.5 | 351.7 | 382.2 | 398.4 | 293.4 | 312.7 | 411.2
719 | 533 | 519.1 | 340.1 | 352.4 | 382.8 | 398.8 | 293.7 | 312.8 | 411.3
720 | 534 | 519.1 | 340.6 | 353 | 383.4 | 399.1 | 294 | 312.9 | 411.4
721 | 535 | 519.4 | 341.2 | 353.8 | 384 | 399.4 | 294.3 | 313.2 | 411.5
722 | 536 | 519.7 | 341.7 | 354.5 | 384.6 | 399.8 | 294.5 | 313.5 | 411.6
723 | 537 | 520 | 342.3 | 355.3 | 385.3 | 400.3 | 294.7 | 313.7 | 411.7
724 | 538 | 520.1 | 342.8 | 355.9 | 385.9 | 400.8 | 294.8 | 313.8 | 411.8
725 | 539 | 520.1 | 343.4 | 356.6 | 386.5 | 401.2 | 294.9 | 313.9 | 411.9
726 | 540 | 520.1 | 344 | 357.2 | 387.2 | 401.8 | 295.2 | 313.7 | 412
727 | 541 | 520 | 344.6 | 357.7 | 387.9 | 402.3 | 295.5 | 314.2 | 412.1
728 | 542 | 519.8 | 345.2 | 358.1 | 388.6 | 402.8 | 295.8 | 314.8 | 412.2
729 | 543 | 519.9 | 345.8 | 358.6 | 389.4 | 403.3 | 296.2 | 315.2 | 412.3
730 | 544 | 519.7 | 346.4 | 359.1 | 390.2 | 403.9 | 296.6 | 315.6 | 412.4
731 | 545 | 519.7 | 347 | 359.6 | 390.9 | 404.3 | 297 | 316.1 | 412.4
732 | 546 | 519.6 | 347.6 | 360.2 | 391.7 | 404.9 | 297.2 | 316.4 | 412.5
733 | 547 | 519.4 | 348.2 | 360.7 | 392.3 | 405.4 | 297.4 | 316.8 | 412.6
734 | 548 | 519.3 | 348.8 | 361.1 | 392.9 | 405.8 | 297.7 | 316.9 | 412.6
735 | 549 | 519.3 | 349.5 | 361.6 | 393.6 | 406.3 | 298.1 | 316.8 | 412.7
736 | 550 | 519.3 | 350.1 | 362.1 | 394.3 | 406.9 | 298.3 | 316.7 | 412.8
737 | 551 | 519.3 | 350.7 | 362.7 | 395 | 407.4 | 298.6 | 316.8 | 412.9
738 | 552 | 518.9 | 351.3 | 363.2 | 395.7 | 408 | 298.8 | 316.7 | 413
739 | 553 | 518.7 | 352 | 363.7 | 396.3 | 408.6 | 299.1 | 316.8 | 413.1
740 | 554 | 518.6 | 352.7 | 364.3 | 397 | 409 | 299.4 | 317.3 | 413.2
741 | 555 | 518.5 | 353.3 | 364.8 | 397.6 | 409.4 | 299.8 | 317.8 | 413.3
742 | 556 | 518.4 | 353.9 | 365.4 | 398.3 | 409.8 | 300.1 | 317.9 | 413.4
743 | 557 | 518.4 | 354.6 | 365.9 | 398.8 | 410.4 | 300.3 | 318.1 | 413.5
744 | 558 | 518.4 | 355.3 | 366.4 | 399.5 | 410.8 | 300.6 | 318.1 | 413.6
745 | 559 | 518.4 | 355.9 | 367 | 400.1 | 411.4 | 300.9 | 318.4 | 413.7
746 | 560 | 518.4 | 356.6 | 367.6 | 400.7 | 412.1 | 301.2 | 319.2 | 413.7
747 | 561 | 518.5 | 357.3 | 368.2 | 401.4 | 412.8 | 301.6 | 319.4 | 413.8
748 | 562 | 518.7 | 357.9 | 368.8 | 402.1 | 413.3 | 302 | 319.4 | 413.9
749 | 563 | 518.6 | 358.5 | 369.3 | 402.8 | 413.7 | 302.3 | 319.1 | 414
750 | 564 | 518.4 | 359.2 | 369.9 | 403.5 | 413.9 | 302.6 | 319.1 | 414.1
751 | 565 | 518.5 | 359.8 | 370.4 | 404.1 | 414.5 | 302.9 | 319.2 | 414.2
752 | 566 | 518.9 | 360.5 | 371 | 404.6 | 415 | 303.2 | 319.4 | 414.3
753 | 567 | 519.1 | 361.1 | 371.5 | 405.3 | 415.5 | 303.4 | 319.5 | 414.4
754 | 568 | 519.1 | 361.9 | 372.1 | 405.9 | 416 | 303.7 | 320 | 414.4
755 | 569 | 519.1 | 362.6 | 372.7 | 406.4 | 416.4 | 304 | 320.3 | 414.4
756 | 570 | 519.4 | 363.3 | 373.4 | 406.8 | 416.8 | 304.3 | 320.7 | 414.5
757 | 571 | 519.5 | 364 | 374 | 407.4 | 417.2 | 304.6 | 320.3 | 414.5
758 | 572 | 519.4 | 364.7 | 374.6 | 407.9 | 417.6 | 305 | 320.1 | 414.5
759 | 573 | 519.3 | 365.4 | 375.2 | 408.6 | 417.9 | 305.3 | 320.3 | 414.6
760 | 574 | 519.3 | 366.1 | 375.8 | 409.2 | 418.3 | 305.7 | 320.1 | 414.6
761 | 575 | 519.3 | 366.8 | 376.4 | 409.8 | 418.6 | 305.9 | 320.1 | 414.7
762 | 576 | 519.3 | 367.5 | 377 | 410.3 | 419 | 306.2 | 320.2 | 414.8
763 | 577 | 519.1 | 368.2 | 377.5 | 410.9 | 419.3 | 306.7 | 319.6 | 414.9
764 | 578 | 519.1 | 368.9 | 378 | 411.5 | 419.7 | 307.1 | 319.5 | 415
765 | 579 | 519.2 | 369.6 | 378.6 | 412 | 420 | 307.4 | 320 | 415.1
766 | 580 | 519 | 370.3 | 379.1 | 412.3 | 420.4 | 307.6 | 320 | 415.2
767 | 581 | 518.9 | 371 | 379.7 | 412.8 | 420.9 | 307.8 | 320.5 | 415.3
768 | 582 | 518.9 | 371.7 | 380.2 | 413.2 | 421.3 | 308.1 | 320.9 | 415.4
769 | 583 | 519 | 372.4 | 380.8 | 413.6 | 421.7 | 308.4 | 321 | 415.4
770 | 584 | 518.7 | 373 | 381.3 | 414.1 | 422 | 308.8 | 321 | 415.5
771 | 585 | 518.5 | 373.7 | 381.9 | 414.6 | 422.3 | 309.1 | 320.9 | 415.5
772 | 586 | 518.6 | 374.4 | 382.5 | 414.9 | 422.7 | 309.3 | 321.1 | 415.6
773 | 587 | 518.7 | 375.1 | 383 | 415.2 | 423.2 | 309.7 | 321.3 | 415.6
774 | 588 | 518.8 | 375.8 | 383.6 | 415.4 | 423.5 | 310 | 321.4 | 415.7
775 | 589 | 518.9 | 376.5 | 384.1 | 415.6 | 423.8 | 310.3 | 321.7 | 415.8
776 | 590 | 518.9 | 377.2 | 384.6 | 416 | 424.2 | 310.7 | 322.4 | 415.8
777 | 591 | 518.9 | 377.9 | 385.1 | 416.4 | 424.3 | 311 | 322.6 | 415.9
778 | 592 | 519 | 378.5 | 385.7 | 416.7 | 424.5 | 311.4 | 322.3 | 416
779 | 593 | 519.2 | 379.2 | 386.3 | 417.3 | 424.8 | 311.7 | 322.5 | 416.1
780 | 594 | 519.3 | 379.8 | 386.8 | 417.8 | 425.1 | 312.1 | 322.5 | 416.2
781 | 595 | 519.5 | 380.5 | 387.4 | 418.2 | 425.4 | 312.3 | 322.6 | 416.3
782 | 596 | 519.7 | 381.2 | 387.9 | 418.7 | 425.7 | 312.6 | 322.5 | 416.4
783 | 597 | 519.7 | 381.8 | 388.5 | 419.3 | 426.2 | 312.8 | 322.2 | 416.4
784 | 598 | 519.8 | 382.4 | 389 | 419.7 | 426.8 | 313.1 | 322.2 | 416.5
785 | 599 | 519.9 | 383 | 389.6 | 420.2 | 427.1 | 313.4 | 322.1 | 416.7
786 | 600 | 519.9 | 383.6 | 390.2 | 420.6 | 427.6 | 313.6 | 322 | 416.8
787 | 601 | 519.8 | 384.3 | 390.8 | 421.1 | 428.3 | 314 | 322 | 416.9
788 | 602 | 519.8 | 384.8 | 391.3 | 421.4 | 428.5 | 314.3 | 322.2 | 417
789 | 603 | 519.7 | 385.4 | 391.9 | 421.9 | 428.6 | 314.6 | 322.2 | 417.1
790 | 604 | 519.8 | 386 | 392.5 | 422.4 | 429 | 314.9 | 322.8 | 417.2
791 | 605 | 519.8 | 386.6 | 393.1 | 422.8 | 429.2 | 315.1 | 322.9 | 417.3
792 | 606 | 519.8 | 387.2 | 393.6 | 423.3 | 429.3 | 315.4 | 322.7 | 417.4
793 | 607 | 520.1 | 387.8 | 394.2 | 423.6 | 429.7 | 315.6 | 322.8 | 417.5
794 | 608 | 520.2 | 388.3 | 394.7 | 423.9 | 429.9 | 315.8 | 323.2 | 417.5
795 | 609 | 520.3 | 388.9 | 395.2 | 424.3 | 430.3 | 316.1 | 323.6 | 417.6
796 | 610 | 520.4 | 389.4 | 395.8 | 424.4 | 430.8 | 316.3 | 324.3 | 417.7
797 | 611 | 520.4 | 390 | 396.3 | 424.6 | 430.8 | 316.5 | 324.5 | 417.7
798 | 612 | 520.3 | 390.6 | 396.8 | 424.7 | 430.9 | 316.8 | 324.2 | 417.8
799 | 613 | 520.2 | 391.1 | 397.4 | 425 | 430.7 | 317.2 | 323.5 | 417.9
800 | 614 | 520.2 | 391.7 | 397.9 | 425.3 | 431 | 317.5 | 323.2 | 418
801 | 615 | 520.2 | 392.2 | 398.5 | 425.6 | 431.4 | 317.8 | 323.4 | 418.1
802 | 616 | 520.2 | 392.8 | 399 | 425.9 | 431.4 | 318.1 | 323.6 | 418.1
803 | 617 | 520.4 | 393.3 | 399.5 | 426.2 | 431.7 | 318.4 | 323.5 | 418.2
804 | 618 | 520.3 | 393.9 | 399.9 | 426.6 | 432.4 | 318.7 | 323.3 | 418.2
805 | 619 | 520.3 | 394.4 | 400.4 | 427 | 432.7 | 318.9 | 323.7 | 418.3
806 | 620 | 520.4 | 395 | 400.9 | 427.5 | 432.9 | 319.2 | 323.9 | 418.4
807 | 621 | 520.6 | 395.5 | 401.5 | 427.9 | 433.3 | 319.5 | 324.1 | 418.4
808 | 622 | 520.8 | 396.1 | 401.9 | 428.3 | 433.6 | 319.8 | 324.2 | 418.5
809 | 623 | 521 | 396.6 | 402.4 | 428.8 | 433.6 | 320 | 324.2 | 418.6
810 | 624 | 521.3 | 397.1 | 402.7 | 429.4 | 433.7 | 320.3 | 324.7 | 418.6
811 | 625 | 521.4 | 397.6 | 403.2 | 430 | 434 | 320.7 | 324.6 | 418.7
812 | 626 | 521.5 | 398.1 | 403.7 | 430.4 | 433.7 | 321.1 | 324.6 | 418.7
813 | 627 | 521.5 | 398.6 | 404.2 | 430.9 | 433.9 | 321.4 | 324.6 | 418.8
814 | 628 | 521.4 | 399.2 | 404.6 | 431.4 | 434.3 | 321.8 | 324.6 | 418.9
815 | 629 | 521.4 | 399.7 | 405.1 | 431.9 | 434.7 | 322.1 | 324.1 | 419
816 | 630 | 521.1 | 400.2 | 405.6 | 432.2 | 435 | 322.5 | 324.5 | 419
817 | 631 | 520.8 | 400.7 | 406.1 | 432.7 | 435.3 | 322.8 | 325 | 419.1
818 | 632 | 520.6 | 401.1 | 406.6 | 433.1 | 435.2 | 323.2 | 325 | 419.1
819 | 633 | 520.5 | 401.7 | 407 | 433.5 | 435.2 | 323.5 | 325.4 | 419.2
820 | 634 | 520.5 | 402.2 | 407.5 | 433.9 | 435.3 | 323.9 | 325.7 | 419.2
821 | 635 | 520.4 | 402.7 | 408.1 | 434.2 | 435.4 | 324.1 | 325.9 | 419.3
822 | 636 | 520.3 | 403.2 | 408.6 | 434.6 | 435.9 | 324.3 | 325.7 | 419.4
823 | 637 | 519.9 | 403.6 | 409.1 | 434.9 | 436.3 | 324.5 | 325.6 | 419.5
824 | 638 | 519.6 | 404.1 | 409.8 | 435.2 | 436.7 | 324.7 | 325.7 | 419.6
825 | 639 | 519.3 | 404.6 | 410.4 | 435.7 | 437 | 324.9 | 325.5 | 419.7
826 | 640 | 519.2 | 405.1 | 411 | 436.1 | 437 | 325.2 | 325.4 | 419.8
827 | 641 | 519 | 405.6 | 411.5 | 436.3 | 437.3 | 325.5 | 325.2 | 419.8
828 | 642 | 518.9 | 406.1 | 412.1 | 436.6 | 437.8 | 325.7 | 325.4 | 419.9
829 | 643 | 518.5 | 406.5 | 412.6 | 436.9 | 438.4 | 326 | 325.2 | 420
830 | 644 | 518.4 | 407 | 413.1 | 437.2 | 438.9 | 326.2 | 325.4 | 420.1
831 | 645 | 518.2 | 407.5 | 413.5 | 437.4 | 439.1 | 326.4 | 325.8 | 420.3
832 | 646 | 518.2 | 408 | 414 | 437.5 | 439.1 | 326.7 | 326.3 | 420.4
833 | 647 | 518.2 | 408.5 | 414.5 | 437.8 | 439.4 | 326.9 | 326.4 | 420.5
834 | 648 | 518.3 | 408.9 | 414.9 | 438.2 | 439.9 | 327.2 | 326.4 | 420.6
835 | 649 | 518.3 | 409.4 | 415.4 | 438.6 | 440.3 | 327.4 | 326 | 420.7
836 | 650 | 518.2 | 409.9 | 416 | 438.9 | 440.5 | 327.7 | 326.3 | 420.8
837 | 651 | 518.3 | 410.4 | 416.5 | 439.1 | 440.7 | 327.9 | 326.3 | 420.9
838 | 652 | 518.2 | 410.8 | 417.1 | 439.3 | 441 | 328.2 | 326.6 | 421
839 | 653 | 518.2 | 411.3 | 417.6 | 439.8 | 441.6 | 328.5 | 326.8 | 421.1
840 | 654 | 518 | 411.8 | 418.1 | 440.2 | 442.2 | 328.8 | 326.7 | 421.2
841 | 655 | 518 | 412.3 | 418.6 | 440.3 | 442.4 | 329.1 | 326.6 | 421.3
842 | 656 | 517.8 | 412.7 | 419.1 | 440.6 | 442.6 | 329.3 | 326.6 | 421.4
843 | 657 | 517.9 | 413.2 | 419.7 | 440.9 | 442.9 | 329.6 | 327 | 421.5
844 | 658 | 518 | 413.7 | 420.2 | 441.2 | 443.3 | 330 | 327 | 421.6
845 | 659 | 518 | 414.2 | 420.7 | 441.5 | 443.7 | 330.2 | 326.8 | 421.7
846 | 660 | 518 | 414.6 | 421.1 | 441.8 | 443.9 | 330.4 | 327.1 | 421.8
847 | 661 | 518 | 415.1 | 421.5 | 442.1 | 444.1 | 330.7 | 327.4 | 421.9
848 | 662 | 517.9 | 415.5 | 422 | 442.4 | 444.4 | 331.1 | 327.8 | 422
849 | 663 | 517.9 | 416 | 422.5 | 442.5 | 444.6 | 331.4 | 327.8 | 422.2
850 | 664 | 517.9 | 416.5 | 423 | 442.6 | 445 | 331.7 | 328.4 | 422.2
851 | 665 | 518 | 416.9 | 423.4 | 442.8 | 445.4 | 332 | 328.6 | 422.3
852 | 666 | 518 | 417.4 | 423.9 | 443 | 445.4 | 332.3 | 329.6 | 422.5
853 | 667 | 518.1 | 417.9 | 424.5 | 443 | 445.7 | 332.6 | 330.3 | 422.6
854 | 668 | 518.2 | 418.4 | 425 | 443.2 | 446.3 | 332.9 | 330.2 | 422.7
855 | 669 | 518.5 | 418.8 | 425.5 | 443.5 | 446.7 | 333.2 | 329.9 | 422.9
856 | 670 | 518.9 | 419.3 | 426 | 443.7 | 447.1 | 333.5 | 329.8 | 423
857 | 671 | 519.1 | 419.8 | 426.5 | 443.7 | 447.7 | 333.8 | 330 | 423.2
858 | 672 | 519.4 | 420.3 | 427 | 443.8 | 447.8 | 334.1 | 330 | 423.4
859 | 673 | 519.6 | 420.7 | 427.4 | 443.9 | 447.9 | 334.4 | 330.1 | 423.5
860 | 674 | 519.7 | 421.2 | 427.8 | 444.1 | 448.1 | 334.7 | 330.2 | 423.6
861 | 675 | 519.8 | 421.7 | 428.2 | 444.4 | 448.3 | 335 | 330.4 | 423.7
862 | 676 | 520 | 422.2 | 428.7 | 444.5 | 448.5 | 335.3 | 330.6 | 423.9
863 | 677 | 520.1 | 422.6 | 429.2 | 444.8 | 448.6 | 335.5 | 330.6 | 424
864 | 678 | 520.1 | 423.1 | 429.7 | 445.1 | 448.7 | 335.9 | 330.7 | 424.1
865 | 679 | 520 | 423.6 | 430.1 | 445.4 | 449.2 | 336.1 | 330.9 | 424.3
866 | 680 | 520 | 424 | 430.5 | 445.8 | 449.9 | 336.5 | 331 | 424.4
867 | 681 | 520.1 | 424.5 | 430.8 | 446.1 | 449.8 | 336.8 | 331.5 | 424.5
868 | 682 | 520.2 | 424.9 | 431.2 | 446.4 | 450.1 | 337.2 | 331.9 | 424.6
869 | 683 | 520.5 | 425.3 | 431.6 | 446.9 | 450 | 337.5 | 331.8 | 424.7
870 | 684 | 520.6 | 425.8 | 432.1 | 447.1 | 450.2 | 337.8 | 331.9 | 424.8
871 | 685 | 520.7 | 426.2 | 432.6 | 447.4 | 450.3 | 338.2 | 332.1 | 424.9
872 | 686 | 520.9 | 426.6 | 433 | 447.7 | 450.7 | 338.5 | 332 | 425
873 | 687 | 520.9 | 427 | 433.6 | 448.1 | 451.1 | 338.9 | 332.4 | 425.1
874 | 688 | 520.8 | 427.5 | 434 | 448.4 | 451.1 | 339.2 | 332.5 | 425.2
875 | 689 | 520.6 | 427.9 | 434.5 | 448.7 | 451.4 | 339.5 | 333.1 | 425.3
876 | 690 | 520.5 | 428.3 | 434.9 | 448.9 | 452 | 339.9 | 333.3 | 425.4
877 | 691 | 520.4 | 428.8 | 435.2 | 449.2 | 451.9 | 340.3 | 333.5 | 425.4
878 | 692 | 520.4 | 429.2 | 435.4 | 449.4 | 452.1 | 340.7 | 333.6 | 425.5
879 | 693 | 520.5 | 429.6 | 435.8 | 449.7 | 452.5 | 341 | 333.6 | 425.6
880 | 694 | 520.5 | 430 | 436.4 | 449.9 | 452.6 | 341.4 | 333.8 | 425.6
881 | 695 | 520.2 | 430.4 | 436.8 | 450.2 | 452.7 | 341.7 | 333.7 | 425.7
882 | 696 | 520.1 | 430.8 | 437.3 | 450.6 | 453.2 | 342.1 | 334.1 | 425.8
883 | 697 | 520 | 431.3 | 437.9 | 450.8 | 453.3 | 342.4 | 334.2 | 425.8
884 | 698 | 520 | 431.7 | 438.3 | 451.1 | 453.9 | 342.8 | 334.7 | 425.9
885 | 699 | 519.8 | 432.1 | 438.7 | 451.4 | 454.4 | 343.1 | 334.7 | 426.1
886 | 700 | 519.8 | 432.4 | 439.1 | 451.7 | 454.5 | 343.5 | 335 | 426.2
887 | 701 | 519.6 | 432.8 | 439.5 | 451.7 | 454.7 | 343.9 | 335.3 | 426.3
888 | 702 | 519.4 | 433.2 | 439.9 | 451.9 | 454.9 | 344.2 | 335.9 | 426.4
889 | 703 | 519.3 | 433.6 | 440.2 | 452.1 | 455.1 | 344.6 | 336 | 426.5
890 | 704 | 519.1 | 434 | 440.6 | 452.3 | 455.5 | 345 | 336.3 | 426.7
891 | 705 | 519 | 434.5 | 440.9 | 452.5 | 455.8 | 345.3 | 336.6 | 426.8
892 | 706 | 519.1 | 434.9 | 441.2 | 452.7 | 456.1 | 345.6 | 336.7 | 426.9
893 | 707 | 519.1 | 435.2 | 441.6 | 452.8 | 456.2 | 345.9 | 336.8 | 427
894 | 708 | 519.1 | 435.6 | 442 | 452.9 | 456.1 | 346.2 | 337.4 | 427.1
895 | 709 | 519.3 | 436 | 442.4 | 453 | 456.3 | 346.5 | 337.4 | 427.2
896 | 710 | 519.4 | 436.4 | 442.8 | 453.1 | 456.4 | 346.8 | 337.5 | 427.2
897 | 711 | 519.4 | 436.7 | 443.1 | 453.3 | 456.5 | 347.1 | 337.9 | 427.3
898 | 712 | 519.5 | 437.1 | 443.5 | 453.5 | 456.8 | 347.5 | 338.5 | 427.3
899 | 713 | 519.5 | 437.4 | 443.9 | 453.6 | 457.1 | 347.9 | 338.7 | 427.4
900 | 714 | 519.4 | 437.8 | 444.3 | 453.9 | 457 | 348.2 | 339.1 | 427.5
901 | 715 | 519.4 | 438.2 | 444.6 | 454.1 | 457.2 | 348.6 | 339.5 | 427.5
902 | 716 | 519.5 | 438.5 | 445 | 454.4 | 457.5 | 349 | 339.7 | 427.5
903 | 717 | 519.5 | 438.9 | 445.4 | 454.7 | 457.8 | 349.4 | 339.6 | 427.5
904 | 718 | 519.5 | 439.3 | 445.8 | 455 | 458.3 | 349.8 | 339.3 | 427.6
905 | 719 | 519.4 | 439.7 | 446.1 | 455.2 | 458.4 | 350.2 | 339 | 427.6
906 | 720 | 519.4 | 440 | 446.6 | 455.5 | 458.6 | 350.6 | 339 | 427.7
907 | 721 | 519.4 | 440.4 | 447 | 455.7 | 458.9 | 351 | 339.5 | 427.8
908 | 722 | 519.3 | 440.7 | 447.3 | 456 | 459.2 | 351.5 | 339.8 | 427.8
909 | 723 | 519.5 | 441.1 | 447.7 | 456.2 | 459.5 | 351.9 | 339.9 | 427.8
910 | 724 | 519.5 | 441.4 | 448.1 | 456.4 | 460 | 352.3 | 340.3 | 427.9
911 | 725 | 519.3 | 441.8 | 448.5 | 456.6 | 460.5 | 352.6 | 340.8 | 427.9
912 | 726 | 519.2 | 442.1 | 448.8 | 456.9 | 460.7 | 353.1 | 341.8 | 427.9
913 | 727 | 519.2 | 442.5 | 449.2 | 457.2 | 461 | 353.5 | 342.4 | 427.9
914 | 728 | 518.9 | 442.8 | 449.6 | 457.6 | 461.2 | 354 | 342.8 | 428
915 | 729 | 518.6 | 443.1 | 450 | 457.9 | 461.5 | 354.4 | 343.4 | 428
916 | 730 | 518.8 | 443.4 | 450.5 | 458.3 | 461.7 | 354.9 | 343.7 | 428
917 | 731 | 518.7 | 443.7 | 450.9 | 458.6 | 462 | 355.3 | 343.1 | 428
918 | 732 | 518.5 | 444 | 451.2 | 458.9 | 462.2 | 355.7 | 343.3 | 428
919 | 733 | 518.4 | 444.4 | 451.5 | 459.2 | 462.4 | 356.1 | 343.6 | 428.1
920 | 734 | 518.2 | 444.7 | 451.9 | 459.5 | 462.7 | 356.5 | 343.6 | 428
921 | 735 | 518.1 | 445 | 452.3 | 459.9 | 462.9 | 356.9 | 343.7 | 428
922 | 736 | 518.1 | 445.3 | 452.6 | 460.3 | 463.2 | 357.3 | 343.8 | 428
923 | 737 | 518 | 445.6 | 453.2 | 460.6 | 463.5 | 357.6 | 343.9 | 428
924 | 738 | 518 | 445.9 | 453.6 | 460.9 | 463.7 | 358 | 344.4 | 428.1
925 | 739 | 518 | 446.2 | 453.7 | 461.2 | 464 | 358.5 | 344.3 | 428.1
926 | 740 | 518.1 | 446.5 | 454 | 461.5 | 464.1 | 359 | 344.9 | 428.1
927 | 741 | 518.2 | 446.8 | 454.3 | 461.8 | 464.2 | 359.6 | 344.5 | 428.1
928 | 742 | 518.4 | 447.1 | 454.6 | 462.1 | 464.3 | 360.1 | 344.6 | 428.2
929 | 743 | 518.3 | 447.4 | 454.9 | 462.3 | 464.6 | 360.7 | 345 | 428.2
930 | 744 | 518.4 | 447.7 | 455.2 | 462.5 | 464.8 | 361.2 | 345.3 | 428.3
931 | 745 | 518.5 | 448 | 455.6 | 462.7 | 464.9 | 361.6 | 345.3 | 428.3
932 | 746 | 518.3 | 448.3 | 455.9 | 462.9 | 464.9 | 362 | 345.3 | 428.4
933 | 747 | 518.5 | 448.6 | 456.4 | 463.1 | 465 | 362.4 | 345.8 | 428.5
934 | 748 | 518.6 | 448.9 | 456.8 | 463.3 | 465.1 | 362.8 | 346.1 | 428.6
935 | 749 | 518.9 | 449.2 | 457.2 | 463.4 | 465.3 | 363.2 | 346.5 | 428.6
936 | 750 | 519.1 | 449.5 | 457.5 | 463.4 | 465.4 | 363.7 | 346.7 | 428.7
937 | 751 | 519.2 | 449.7 | 457.8 | 463.4 | 465.7 | 364.2 | 346.6 | 428.7
938 | 752 | 519.3 | 450 | 458.1 | 463.4 | 466 | 364.7 | 346.8 | 428.7
939 | 753 | 519.3 | 450.3 | 458.5 | 463.4 | 466.3 | 365.2 | 346.7 | 428.8
940 | 754 | 519.2 | 450.6 | 458.9 | 463.5 | 466.5 | 365.6 | 347.5 | 428.8
941 | 755 | 519.1 | 450.9 | 459.4 | 463.5 | 466.6 | 366 | 347.5 | 428.9
942 | 756 | 519.2 | 451.2 | 459.6 | 463.6 | 466.8 | 366.4 | 347.7 | 428.9
943 | 757 | 519.2 | 451.5 | 459.8 | 463.7 | 467 | 366.9 | 347.9 | 428.9
944 | 758 | 519.3 | 451.8 | 460.1 | 463.8 | 467.1 | 367.4 | 349 | 428.9
945 | 759 | 519.4 | 452.2 | 460.3 | 463.8 | 467.4 | 367.9 | 349 | 428.9
946 | 760 | 519.5 | 452.5 | 460.7 | 463.9 | 467.6 | 368.5 | 348.5 | 428.9
947 | 761 | 519.6 | 452.7 | 461 | 464 | 467.8 | 369 | 348.8 | 428.9
948 | 762 | 519.8 | 453 | 461.4 | 464 | 467.9 | 369.5 | 348.7 | 428.9
949 | 763 | 519.8 | 453.4 | 461.7 | 464.2 | 468.1 | 370.1 | 348.8 | 428.9
950 | 764 | 519.8 | 453.7 | 462 | 464.4 | 468.2 | 370.6 | 349.4 | 428.9
951 | 765 | 520.1 | 454 | 462.6 | 464.5 | 468.4 | 371 | 349.8 | 429
952 | 766 | 520 | 454.3 | 462.9 | 464.6 | 468.5 | 371.4 | 350.1 | 429
953 | 767 | 519.7 | 454.7 | 463.3 | 464.7 | 468.7 | 371.9 | 350.6 | 429
954 | 768 | 519.7 | 455 | 463.7 | 464.8 | 468.8 | 372.3 | 351.2 | 429.1
955 | 769 | 519.4 | 455.3 | 464 | 464.9 | 468.9 | 372.8 | 351.4 | 429.1
956 | 770 | 519.4 | 455.6 | 464.4 | 465.1 | 469.1 | 373.2 | 351.4 | 429.1
957 | 771 | 519.2 | 455.9 | 464.7 | 465.3 | 469.3 | 373.6 | 351.5 | 429.1
958 | 772 | 519.2 | 456.2 | 465 | 465.4 | 469.4 | 374.1 | 351.8 | 429.2
959 | 773 | 519.1 | 456.6 | 465.4 | 465.6 | 469.5 | 374.6 | 352 | 429.2
960 | 774 | 519.1 | 456.9 | 465.7 | 465.9 | 469.7 | 375 | 352.3 | 429.1
961 | 775 | 519.1 | 457.2 | 466.1 | 466.1 | 470 | 375.4 | 352.2 | 429
962 | 776 | 519.2 | 457.5 | 466.6 | 466.3 | 470.1 | 375.8 | 352.9 | 429
963 | 777 | 519.3 | 457.8 | 466.9 | 466.4 | 470 | 376.3 | 353.7 | 429.1
964 | 778 | 519.4 | 458.1 | 467.2 | 466.5 | 469.9 | 376.9 | 353.7 | 429.1
965 | 779 | 519.6 | 458.4 | 467.6 | 466.4 | 470 | 377.3 | 354 | 429.1
966 | 780 | 519.8 | 458.7 | 467.8 | 466.4 | 470 | 377.8 | 354.2 | 429.1
967 | 781 | 520 | 459 | 468.1 | 466.5 | 470.2 | 378.3 | 354.6 | 429.2
968 | 782 | 520.2 | 459.3 | 468.4 | 466.8 | 470.3 | 378.7 | 355 | 429.3
969 | 783 | 520.3 | 459.7 | 468.6 | 467 | 470.5 | 379.1 | 355.3 | 429.4
970 | 784 | 520.2 | 460 | 468.7 | 467.3 | 470.7 | 379.7 | 355.9 | 429.4
971 | 785 | 519.9 | 460.3 | 468.9 | 467.6 | 470.9 | 380.2 | 356.6 | 429.5
972 | 786 | 520 | 460.6 | 469 | 467.8 | 471 | 380.8 | 357.8 | 429.5
973 | 787 | 520.1 | 461 | 469.2 | 468.1 | 471.2 | 381.3 | 358.2 | 429.5
974 | 788 | 520.2 | 461.3 | 469.4 | 468.4 | 471.4 | 381.8 | 358.3 | 429.5
975 | 789 | 520.1 | 461.6 | 469.7 | 468.7 | 471.6 | 382.2 | 358.5 | 429.5
976 | 790 | 520.1 | 461.9 | 470 | 469.1 | 471.8 | 382.6 | 358.7 | 429.6
977 | 791 | 520.1 | 462.2 | 470.2 | 469.5 | 472.1 | 383 | 358.6 | 429.6
978 | 792 | 519.9 | 462.5 | 470.4 | 470 | 472.4 | 383.4 | 358.3 | 429.5
979 | 793 | 520 | 462.8 | 470.7 | 470.4 | 472.6 | 383.7 | 358.1 | 429.6
980 | 794 | 519.8 | 463.1 | 470.9 | 470.8 | 472.8 | 384 | 358.8 | 429.7
981 | 795 | 519.5 | 463.4 | 471.2 | 471.1 | 473 | 384.4 | 359.7 | 429.7
982 | 796 | 519.4 | 463.7 | 471.4 | 471.4 | 473.2 | 384.7 | 359.8 | 429.7
983 | 797 | 519.3 | 464 | 471.6 | 471.7 | 473.5 | 385 | 359.9 | 429.7
984 | 798 | 519.5 | 464.3 | 472 | 471.9 | 473.7 | 385.3 | 360 | 429.7
985 | 799 | 519.5 | 464.5 | 472.3 | 472.1 | 473.9 | 385.7 | 361.2 | 429.7
986 | 800 | 519.7 | 464.8 | 472.6 | 472.4 | 474.1 | 385.9 | 362 | 429.7
987 | 801 | 519.6 | 465.1 | 472.9 | 472.6 | 474.4 | 386.3 | 362.6 | 429.7
988 | 802 | 519.5 | 465.4 | 473.2 | 472.9 | 474.6 | 386.6 | 362.8 | 429.7
989 | 803 | 519.3 | 465.7 | 473.6 | 473.1 | 474.9 | 386.8 | 362.8 | 429.7
990 | 804 | 519.2 | 466 | 474 | 473.3 | 475.1 | 387.1 | 362.7 | 429.7
991 | 805 | 519 | 466.3 | 474.5 | 473.5 | 475.5 | 387.4 | 362.9 | 429.7
992 | 806 | 519.2 | 466.5 | 474.7 | 473.7 | 475.8 | 387.7 | 363.2 | 429.8
993 | 807 | 519.2 | 466.8 | 474.8 | 473.8 | 476 | 388 | 364 | 429.8
994 | 808 | 519.4 | 467.1 | 475 | 473.8 | 476 | 388.3 | 364.6 | 429.8
995 | 809 | 519.4 | 467.4 | 475.3 | 473.8 | 476.3 | 388.6 | 364.7 | 429.9
996 | 810 | 519.4 | 467.6 | 475.6 | 473.9 | 476.5 | 388.8 | 365.3 | 429.9
997 | 811 | 519.6 | 468 | 475.9 | 473.9 | 476.7 | 389.2 | 366.3 | 430
998 | 812 | 519.7 | 468.2 | 476.6 | 474 | 476.9 | 389.4 | 367 | 430
999 | 813 | 519.7 | 468.5 | 477.1 | 474.2 | 477.2 | 389.6 | 367.4 | 430
1000 | 814 | 519.7 | 468.8 | 477.3 | 474.2 | 477.2 | 389.9 | 367.9 | 430
1001 | 815 | 519.6 | 469.1 | 477.5 | 474.3 | 477.2 | 390.2 | 368.9 | 430
1002 | 816 | 519.5 | 469.5 | 477.7 | 474.4 | 477.3 | 390.5 | 369.5 | 430.1
1003 | 817 | 519.7 | 469.8 | 478.1 | 474.6 | 477.5 | 390.8 | 369.7 | 430.1
1004 | 818 | 520 | 470.1 | 478.4 | 474.8 | 477.6 | 391.1 | 370.3 | 430.1
1005 | 819 | 520.3 | 470.5 | 478.4 | 475 | 477.7 | 391.4 | 370.5 | 430.2
1006 | 820 | 520.6 | 470.9 | 478.3 | 475.2 | 477.9 | 391.6 | 370.8 | 430.3
1007 | 821 | 520.9 | 471.2 | 478.6 | 475.5 | 478.1 | 391.8 | 371.1 | 430.4
1008 | 822 | 521 | 471.5 | 479.1 | 475.8 | 478.4 | 392 | 371.5 | 430.5
1009 | 823 | 521.3 | 471.8 | 479.6 | 476 | 478.5 | 392.3 | 371.9 | 430.6
1010 | 824 | 521.4 | 472.2 | 480 | 476.2 | 478.8 | 392.6 | 372.1 | 430.7
1011 | 825 | 521.2 | 472.5 | 480.2 | 476.4 | 479 | 392.9 | 372.8 | 430.7
1012 | 826 | 521.1 | 472.8 | 480.6 | 476.6 | 479.2 | 393.3 | 372.5 | 430.8
1013 | 827 | 521.1 | 473.1 | 481 | 476.8 | 479.3 | 393.6 | 372.7 | 430.9
1014 | 828 | 521.1 | 473.5 | 481.1 | 477.1 | 479.6 | 393.9 | 372.9 | 431
1015 | 829 | 521.2 | 473.8 | 481.5 | 477.4 | 479.8 | 394.1 | 372.7 | 431
1016 | 830 | 521.3 | 474.1 | 481.6 | 477.7 | 480.1 | 394.4 | 373.7 | 431.1
1017 | 831 | 521.3 | 474.4 | 482 | 477.9 | 480.4 | 394.7 | 373.9 | 431.1
1018 | 832 | 521.2 | 474.8 | 482.3 | 478.1 | 480.6 | 395 | 374.4 | 431.2
1019 | 833 | 521.2 | 475.1 | 482.4 | 478.4 | 480.8 | 395.2 | 375.3 | 431.3
1020 | 834 | 521.2 | 475.5 | 482.7 | 478.6 | 481.1 | 395.6 | 376 | 431.3
1021 | 835 | 521 | 475.8 | 483.2 | 478.9 | 481.4 | 395.8 | 375.7 | 431.4
1022 | 836 | 520.9 | 476.1 | 483.4 | 479.2 | 481.7 | 396 | 375.9 | 431.4
1023 | 837 | 520.7 | 476.4 | 483.7 | 479.4 | 481.9 | 396.2 | 376.2 | 431.5
1024 | 838 | 520.6 | 476.8 | 483.9 | 479.6 | 482.1 | 396.3 | 376.3 | 431.5
1025 | 839 | 520.3 | 477.1 | 484.1 | 479.9 | 482.3 | 396.6 | 375.8 | 431.4
1026 | 840 | 520.1 | 477.4 | 484.3 | 480.2 | 482.6 | 396.8 | 375.7 | 431.4
1027 | 841 | 519.9 | 477.7 | 484.6 | 480.6 | 482.9 | 397 | 375.7 | 431.4
1028 | 842 | 519.6 | 478 | 485 | 481 | 483.2 | 397.3 | 375.9 | 431.4
1029 | 843 | 519.4 | 478.3 | 485.3 | 481.4 | 483.5 | 397.4 | 376 | 431.4
1030 | 844 | 519.2 | 478.6 | 485.7 | 481.8 | 483.7 | 397.7 | 376.7 | 431.5
1031 | 845 | 518.9 | 478.9 | 486.1 | 482.2 | 484.1 | 397.9 | 376.6 | 431.5
1032 | 846 | 518.8 | 479.2 | 486.5 | 482.6 | 484.5 | 398.1 | 376.2 | 431.5
1033 | 847 | 518.9 | 479.4 | 486.8 | 482.9 | 484.6 | 398.4 | 376 | 431.4
1034 | 848 | 518.9 | 479.7 | 487.2 | 483.2 | 484.8 | 398.6 | 375.9 | 431.4
1035 | 849 | 518.8 | 480 | 487.5 | 483.5 | 485.1 | 398.8 | 376.3 | 431.4
1036 | 850 | 518.6 | 480.3 | 487.8 | 483.8 | 485.4 | 399 | 376.7 | 431.3
1037 | 851 | 518.3 | 480.5 | 488.1 | 484 | 485.6 | 399.2 | 377.2 | 431.3
1038 | 852 | 518.4 | 480.9 | 488.4 | 484.3 | 485.8 | 399.4 | 377.7 | 431.3
1039 | 853 | 518.5 | 481.2 | 488.6 | 484.6 | 486.2 | 399.6 | 377.9 | 431.3
1040 | 854 | 518.4 | 481.5 | 489 | 484.9 | 486.6 | 399.8 | 378.8 | 431.3
1041 | 855 | 518.3 | 481.8 | 489.3 | 485.2 | 487 | 400.1 | 379.4 | 431.3
1042 | 856 | 518.2 | 482.1 | 489.6 | 485.5 | 487.2 | 400.3 | 379.6 | 431.3
1043 | 857 | 518.3 | 482.4 | 489.9 | 485.7 | 487.5 | 400.6 | 380.6 | 431.4
1044 | 858 | 518.3 | 482.7 | 490 | 485.9 | 487.7 | 400.9 | 381.2 | 431.4
1045 | 859 | 518.6 | 482.9 | 490.4 | 486.2 | 488 | 401.1 | 381.1 | 431.5
1046 | 860 | 518.8 | 483.2 | 490.6 | 486.5 | 488.3 | 401.3 | 380.6 | 431.5
1047 | 861 | 518.9 | 483.4 | 491 | 486.8 | 488.7 | 401.6 | 381.1 | 431.6
1048 | 862 | 519.1 | 483.7 | 491.4 | 487.3 | 489.2 | 401.8 | 381.6 | 431.6
1049 | 863 | 519.1 | 484 | 491.7 | 487.7 | 489.6 | 402.2 | 382.2 | 431.6
1050 | 864 | 519.2 | 484.3 | 492.1 | 488.1 | 490.1 | 402.4 | 382.1 | 431.6
1051 | 865 | 519.4 | 484.6 | 492.5 | 488.4 | 490.3 | 402.6 | 382.1 | 431.7
1052 | 866 | 519.6 | 484.9 | 492.7 | 488.6 | 490.5 | 402.8 | 382.8 | 431.7
1053 | 867 | 519.6 | 485.2 | 492.8 | 488.9 | 490.8 | 403.1 | 382.4 | 431.7
1054 | 868 | 519.8 | 485.5 | 493.1 | 489.4 | 491 | 403.2 | 382.7 | 431.7
1055 | 869 | 519.9 | 485.8 | 493.4 | 489.7 | 491.2 | 403.4 | 383.4 | 431.7
1056 | 870 | 520.1 | 486 | 493.7 | 490.1 | 491.5 | 403.6 | 384 | 431.7
1057 | 871 | 520.3 | 486.3 | 494.3 | 490.5 | 492 | 404 | 383.7 | 431.7
1058 | 872 | 520.5 | 486.5 | 495 | 490.9 | 492.2 | 404.3 | 383.2 | 431.7
1059 | 873 | 520.6 | 486.7 | 495.6 | 491.3 | 492.2 | 404.5 | 383.3 | 431.8
1060 | 874 | 521 | 487 | 495.8 | 491.6 | 492.5 | 404.8 | 383.6 | 431.8
1061 | 875 | 521.3 | 487.2 | 496 | 491.9 | 492.8 | 405 | 384 | 431.9
1062 | 876 | 521.3 | 487.4 | 496.2 | 492.3 | 493.3 | 405.2 | 383.7 | 431.9
1063 | 877 | 521.1 | 487.6 | 496.6 | 492.6 | 493.6 | 405.4 | 383.5 | 432
1064 | 878 | 521 | 487.9 | 497.2 | 492.9 | 493.7 | 405.6 | 384 | 432.1
1065 | 879 | 521.3 | 488.3 | 497.5 | 493.2 | 494 | 405.8 | 384.2 | 432.2
1066 | 880 | 521.5 | 488.7 | 497.5 | 493.4 | 494.3 | 406 | 384.7 | 432.3
1067 | 881 | 521.7 | 489.1 | 497.6 | 493.7 | 494.6 | 406.3 | 384.9 | 432.2
1068 | 882 | 521.8 | 489.5 | 497.8 | 494 | 494.8 | 406.7 | 385 | 432.3
1069 | 883 | 521.8 | 489.8 | 498.1 | 494.3 | 495.1 | 407 | 385.2 | 432.3
1070 | 884 | 521.7 | 490.2 | 498.3 | 494.7 | 495.2 | 407.2 | 385.6 | 432.3
1071 | 885 | 521.7 | 490.4 | 498.8 | 495.2 | 495.5 | 407.5 | 387.6 | 432.3
1072 | 886 | 521.7 | 490.6 | 499.2 | 495.6 | 495.5 | 407.7 | 388.8 | 432.3
1073 | 887 | 521.7 | 490.9 | 499.5 | 496.2 | 495.7 | 407.9 | 389.3 | 432.3
1074 | 888 | 521.7 | 491.2 | 499.8 | 496.9 | 496.3 | 408.2 | 389.7 | 432.3
1075 | 889 | 521.8 | 491.5 | 500.4 | 497.5 | 496.5 | 408.5 | 390.1 | 432.4
1076 | 890 | 521.7 | 491.9 | 500.7 | 498.2 | 496.7 | 408.7 | 389.7 | 432.4
1077 | 891 | 521.6 | 492.3 | 501 | 498.7 | 497.1 | 408.9 | 390.6 | 432.4
1078 | 892 | 521.5 | 492.7 | 501 | 499 | 497.6 | 409.2 | 391.9 | 432.4
1079 | 893 | 521.5 | 493.1 | 501.3 | 499.4 | 498.1 | 409.5 | 393.4 | 432.5
1080 | 894 | 521.5 | 493.6 | 501.6 | 499.8 | 498.7 | 409.7 | 394 | 432.5
1081 | 895 | 521.6 | 493.9 | 502 | 500.1 | 499 | 409.9 | 394.6 | 432.5
1082 | 896 | 521.4 | 494.3 | 502.2 | 500.5 | 499.4 | 410.1 | 393.9 | 432.4
1083 | 897 | 521.2 | 494.5 | 502.5 | 500.9 | 499.9 | 410.2 | 394.1 | 432.4
1084 | 898 | 521.2 | 494.8 | 502.8 | 501.4 | 500.1 | 410.3 | 394.3 | 432.4
1085 | 899 | 521.1 | 495.1 | 503.1 | 501.9 | 500.6 | 410.5 | 394 | 432.5
1086 | 900 | 521 | 495.4 | 503.5 | 502.4 | 501 | 410.8 | 394.2 | 432.5
1087 | 901 | 520.8 | 495.8 | 503.9 | 502.9 | 501.4 | 411 | 394.1 | 432.6
1088 | 902 | 520.7 | 496.1 | 504.1 | 503.3 | 501.9 | 411.2 | 394.7 | 432.6
1089 | 903 | 520.5 | 496.5 | 504.5 | 503.8 | 502.4 | 411.4 | 395 | 432.6
1090 | 904 | 520.3 | 497 | 504.9 | 504.1 | 502.7 | 411.5 | 395 | 432.6
1091 | 905 | 520.3 | 497.4 | 505.2 | 504.7 | 503.2 | 411.7 | 393.9 | 432.6
1092 | 906 | 520.2 | 497.9 | 505.7 | 505.3 | 503.7 | 411.9 | 394.7 | 432.6
1093 | 907 | 520.1 | 498.4 | 506.3 | 505.8 | 504.1 | 412 | 395.8 | 432.6
1094 | 908 | 519.9 | 498.9 | 506.7 | 506.3 | 504.4 | 412.1 | 395 | 432.6
1095 | 909 | 519.8 | 499.4 | 507 | 506.7 | 504.9 | 412.3 | 394.6 | 432.6
1096 | 910 | 519.5 | 499.8 | 507.2 | 507.2 | 505.4 | 412.4 | 394.6 | 432.6
1097 | 911 | 519.5 | 500.2 | 504.5 | 507.8 | 505.9 | 412.6 | 394.5 | 432.7
1098 | 912 | 519.4 | 500.7 | 503.7 | 508.3 | 506.5 | 412.7 | 393.8 | 432.7
1099 | 913 | 519.5 | 501.1 | 504 | 508.9 | 507 | 412.7 | 394.6 | 432.7
1100 | 914 | 519.5 | 501.6 | 504.7 | 509.3 | 507.4 | 412.8 | 394.4 | 432.8
1101 | 915 | 519.4 | 502.1 | 505.2 | 509.7 | 507.9 | 412.9 | 394.6 | 432.8
1102 | 916 | 519.4 | 502.6 | 505.1 | 510.1 | 508.4 | 413 | 394.7 | 432.8
1103 | 917 | 519.5 | 503.1 | 505.6 | 510.5 | 508.8 | 413.1 | 394.7 | 432.8
1104 | 918 | 519.4 | 503.5 | 506.4 | 511.3 | 509.4 | 413.1 | 395.1 | 432.9
1105 | 919 | 519.4 | 503.9 | 506.3 | 511.7 | 509.8 | 413.1 | 395 | 432.9
1106 | 920 | 519.4 | 504.3 | 506.5 | 512 | 510.2 | 413.2 | 394.9 | 432.9
1107 | 921 | 519.5 | 504.7 | 506.3 | 512.3 | 510.4 | 413.3 | 395.2 | 432.9
1108 | 922 | 519.6 | 505 | 506.5 | 512.7 | 510.7 | 413.6 | 395.3 | 433
1109 | 923 | 519.5 | 505.3 | 509.1 | 513.2 | 510.7 | 413.7 | 395.3 | 433
1110 | 924 | 519.1 | 505.6 | 511.3 | 513.6 | 511.1 | 413.8 | 395.8 | 433
1111 | 925 | 519 | 506.1 | 509.8 | 514 | 512 | 414 | 396 | 433.1
1112 | 926 | 519 | 506.5 | 509.2 | 514.4 | 512.8 | 414.1 | 396.1 | 433.1
1113 | 927 | 519 | 507 | 508 | 514.6 | 513.3 | 414.2 | 396.2 | 433.2
1114 | 928 | 519.1 | 507.2 | 509.3 | 514.9 | 513.6 | 414.3 | 396.4 | 433.2
1115 | 929 | 519.1 | 507.5 | 511.6 | 515.1 | 514.1 | 414.3 | 396.5 | 433.2
1116 | 930 | 519.2 | 507.7 | 513.4 | 515.4 | 514.5 | 414.3 | 396.4 | 433.2
1117 | 931 | 519.4 | 508 | 514.7 | 515.8 | 514.7 | 414.3 | 396.8 | 433.2
1118 | 932 | 519.5 | 508.4 | 515.1 | 516.3 | 515 | 414.3 | 397 | 433.2
1119 | 933 | 519.7 | 508.8 | 514.6 | 516.8 | 515.5 | 414.3 | 396.8 | 433.2
1120 | 934 | 519.7 | 509.2 | 513.9 | 517.2 | 516.2 | 414.3 | 397.6 | 433.3
1121 | 935 | 519.6 | 509.6 | 512 | 517.6 | 517 | 414.4 | 398.2 | 433.3
1122 | 936 | 519.5 | 509.9 | 513.9 | 517.8 | 517.5 | 414.5 | 398.5 | 433.3
1123 | 937 | 519.5 | 510.2 | 514.5 | 518 | 518.3 | 414.6 | 398.5 | 433.3
1124 | 938 | 519.4 | 510.5 | 514.7 | 518.3 | 518.9 | 414.7 | 398.5 | 433.3
1125 | 939 | 519.2 | 510.8 | 515.7 | 518.6 | 519.6 | 414.8 | 399.3 | 433.3
1126 | 940 | 519.3 | 511.1 | 515.5 | 519.1 | 520.2 | 414.8 | 399.3 | 433.4
1127 | 941 | 519.5 | 511.6 | 515.2 | 519.6 | 521 | 414.8 | 399.1 | 433.5
1128 | 942 | 519.4 | 511.9 | 517.2 | 520.1 | 521.6 | 414.8 | 399.1 | 433.5
1129 | 943 | 519.3 | 512.5 | 515.5 | 520.6 | 522.4 | 414.8 | 399.2 | 433.6
1130 | 944 | 519.4 | 513 | 516.6 | 521 | 522.9 | 414.8 | 399 | 433.6
1131 | 945 | 519.5 | 513.4 | 517.6 | 521.4 | 523.5 | 414.8 | 399.3 | 433.6
1132 | 946 | 519.5 | 513.8 | 517.1 | 521.8 | 524.2 | 414.9 | 399.7 | 433.6
1133 | 947 | 519.4 | 514.1 | 517.1 | 522 | 524.9 | 414.9 | 399.7 | 433.6
1134 | 948 | 519.4 | 514.4 | 517.9 | 522.4 | 525.7 | 415 | 400.4 | 433.6
1135 | 949 | 519.6 | 514.7 | 518.3 | 522.8 | 526.4 | 415.1 | 400.7 | 433.6
1136 | 950 | 519.7 | 515 | 520.8 | 523.1 | 527 | 415.1 | 401.1 | 433.6
1137 | 951 | 519.7 | 515.3 | 520.3 | 523.5 | 528 | 415.2 | 399.9 | 433.6
1138 | 952 | 520 | 515.8 | 515.8 | 524 | 529.2 | 415.4 | 399.9 | 433.6
1139 | 953 | 520.3 | 516 | 516.5 | 524.3 | 529.9 | 415.5 | 400.1 | 433.6
1140 | 954 | 520.5 | 516.2 | 520.4 | 524.6 | 530.5 | 415.6 | 400.6 | 433.6
1141 | 955 | 520.5 | 516.4 | 523.2 | 524.9 | 531.1 | 415.6 | 400.4 | 433.6
1142 | 956 | 520.6 | 516.6 | 522.8 | 525.3 | 531.7 | 415.6 | 401 | 433.6
1143 | 957 | 520.9 | 516.9 | 522.7 | 525.7 | 532.5 | 415.7 | 401.7 | 433.6
1144 | 958 | 521 | 517.2 | 521.7 | 526.1 | 533.3 | 415.8 | 401.7 | 433.6
1145 | 959 | 521 | 517.5 | 521.3 | 526.5 | 533.9 | 415.8 | 402.4 | 433.6
1146 | 960 | 520.9 | 517.8 | 522 | 526.8 | 534.6 | 415.8 | 401.7 | 433.7
1147 | 961 | 520.8 | 518.2 | 521.3 | 527.2 | 535.4 | 415.8 | 401.5 | 433.7
1148 | 962 | 520.8 | 518.6 | 520.1 | 527.7 | 536.3 | 415.9 | 402.8 | 433.6
1149 | 963 | 520.9 | 518.9 | 520.4 | 528 | 536.9 | 416 | 403 | 433.6
1150 | 964 | 521.2 | 519.3 | 520.8 | 528.4 | 537.4 | 416.1 | 402.9 | 433.6
1151 | 965 | 521.4 | 519.6 | 521 | 528.8 | 538.2 | 416.3 | 403 | 433.6
1152 | 966 | 521.2 | 520 | 521.1 | 529.3 | 538.9 | 416.4 | 403.2 | 433.5
1153 | 967 | 521.3 | 520.4 | 521.8 | 529.7 | 539.2 | 416.5 | 404.2 | 433.5
1154 | 968 | 521.2 | 520.8 | 521.7 | 530.1 | 539.6 | 416.6 | 405.2 | 433.5
1155 | 969 | 521.1 | 521.2 | 521.8 | 530.6 | 540.3 | 416.7 | 405.4 | 433.4
1156 | 970 | 521 | 521.6 | 522.4 | 531.2 | 541 | 416.8 | 405.8 | 433.4
1157 | 971 | 520.8 | 522 | 522.8 | 531.8 | 541.5 | 416.9 | 406 | 433.5
1158 | 972 | 520.9 | 522.4 | 522.8 | 532.5 | 542.1 | 417 | 405.6 | 433.4
1159 | 973 | 520.8 | 522.8 | 523.2 | 533.1 | 542.7 | 417.2 | 406.2 | 433.4
1160 | 974 | 520.8 | 523.2 | 523.9 | 533.7 | 543.2 | 417.4 | 406.6 | 433.5
1161 | 975 | 520.7 | 523.6 | 523.8 | 534.3 | 543.5 | 417.5 | 406.5 | 433.4
1162 | 976 | 520.8 | 523.8 | 524.6 | 534.9 | 544 | 417.6 | 405.9 | 433.5
1163 | 977 | 520.7 | 524.2 | 524.7 | 535.5 | 544.6 | 417.7 | 405.7 | 433.5
1164 | 978 | 520.6 | 524.5 | 525.1 | 536.1 | 545.2 | 417.7 | 406.4 | 433.5
1165 | 979 | 520.6 | 524.9 | 525.2 | 536.7 | 545.6 | 417.8 | 407.7 | 433.5
1166 | 980 | 520.5 | 525.2 | 525.6 | 537.2 | 545.7 | 417.9 | 407.9 | 433.5
1167 | 981 | 520.6 | 525.5 | 526.3 | 537.8 | 545.8 | 418 | 408.6 | 433.5
1168 | 982 | 520.8 | 525.8 | 526.3 | 538.4 | 546.1 | 418.1 | 409.3 | 433.5
1169 | 983 | 520.8 | 526 | 526.6 | 538.9 | 546.4 | 418.1 | 409.7 | 433.5
1170 | 984 | 520.7 | 526.3 | 527.2 | 539.5 | 546.8 | 418.1 | 408.9 | 433.6
1171 | 985 | 520.5 | 526.6 | 527.9 | 540.2 | 547.5 | 418.1 | 408.8 | 433.6
1172 | 986 | 520.5 | 527 | 528.1 | 540.8 | 548.3 | 418.1 | 408 | 433.6
1173 | 987 | 520.3 | 527.3 | 528.6 | 541.3 | 549.1 | 418.1 | 407.9 | 433.6
1174 | 988 | 520.2 | 527.7 | 529.6 | 541.9 | 549.8 | 418.1 | 407.9 | 433.7
1175 | 989 | 520.1 | 528.1 | 529.7 | 542.4 | 550.3 | 418.2 | 408.3 | 433.7
1176 | 990 | 520 | 528.4 | 530 | 542.8 | 550.7 | 418.2 | 408.6 | 433.8
1177 | 991 | 519.9 | 528.8 | 530.8 | 543.2 | 551.2 | 418.3 | 408.4 | 433.8
1178 | 992 | 519.9 | 529.1 | 531.4 | 543.7 | 551.9 | 418.3 | 408.6 | 433.9
1179 | 993 | 519.9 | 529.4 | 531.7 | 544.1 | 552.6 | 418.3 | 409.2 | 433.8
1180 | 994 | 519.8 | 529.7 | 532.4 | 544.6 | 553.2 | 418.3 | 408.6 | 433.9
1181 | 995 | 519.7 | 530 | 533.4 | 545 | 553.8 | 418.3 | 408.8 | 433.9
1182 | 996 | 519.9 | 530.4 | 533.7 | 545.5 | 554.4 | 418.4 | 408.4 | 433.9
1183 | 997 | 519.9 | 530.7 | 534.1 | 545.9 | 555 | 418.4 | 407 | 433.9
1184 | 998 | 520 | 531 | 534.9 | 546.5 | 555.5 | 418.3 | 406.8 | 433.9
1185 | 999 | 519.8 | 531.4 | 535.2 | 547 | 555.6 | 418.3 | 407.5 | 434
1186 | 1000 | 519.8 | 531.8 | 535.3 | 547.5 | 555.9 | 418.4 | 407.3 | 433.9
1187 | 1001 | 519.8 | 532.1 | 535.8 | 548 | 556.3 | 418.4 | 406.8 | 433.9
1188 | 1002 | 519.8 | 532.4 | 536.8 | 548.6 | 556.8 | 418.5 | 407.7 | 434
1189 | 1003 | 519.9 | 532.8 | 536.8 | 549.3 | 557.4 | 418.6 | 407.2 | 433.9
1190 | 1004 | 520 | 533.1 | 536.8 | 549.7 | 558 | 418.6 | 406.7 | 433.9
1191 | 1005 | 520.1 | 533.4 | 537.2 | 550.1 | 558.7 | 418.6 | 407.3 | 433.9
1192 | 1006 | 520 | 533.7 | 538 | 550.6 | 559.1 | 418.7 | 406.6 | 433.9
1193 | 1007 | 520.2 | 533.9 | 538.2 | 551.1 | 559.4 | 418.8 | 407.2 | 433.9
1194 | 1008 | 520.4 | 534.2 | 538.7 | 551.5 | 559.7 | 418.8 | 407.3 | 433.9
1195 | 1009 | 520.5 | 534.5 | 539.6 | 551.9 | 560 | 418.9 | 407.3 | 434
1196 | 1010 | 520.7 | 534.8 | 539.4 | 552.4 | 560.2 | 418.9 | 407 | 434
1197 | 1011 | 520.7 | 535.1 | 539.4 | 552.8 | 560.6 | 419 | 408.2 | 434
1198 | 1012 | 520.6 | 535.3 | 540 | 553.2 | 560.9 | 419.1 | 407.9 | 434
1199 | 1013 | 520.5 | 535.5 | 540.5 | 553.6 | 561.1 | 419.1 | 407.8 | 434.1
1200 | 1014 | 520.5 | 535.8 | 540.4 | 554 | 561.1 | 419.2 | 407.8 | 434.1
1201 | 1015 | 520.6 | 536.1 | 541.1 | 554.5 | 561.3 | 419.3 | 408 | 434.1
1202 | 1016 | 520.7 | 536.4 | 541.6 | 555 | 561.4 | 419.4 | 408.3 | 434.1
1203 | 1017 | 520.7 | 536.7 | 541.8 | 555.5 | 561.5 | 419.4 | 408.1 | 434.1
1204 | 1018 | 520.6 | 537 | 542.1 | 556 | 561.6 | 419.5 | 408.5 | 434.1
1205 | 1019 | 520.6 | 537.4 | 542.5 | 556.6 | 562.2 | 419.7 | 408.5 | 434.1
1206 | 1020 | 520.6 | 537.8 | 542.7 | 557.1 | 563 | 419.9 | 409.3 | 434.1
1207 | 1021 | 520.8 | 538.1 | 543.1 | 557.6 | 563.4 | 420.1 | 408.8 | 434.1
1208 | 1022 | 520.7 | 538.4 | 543.4 | 558.3 | 563.9 | 420.2 | 409.1 | 434.1
1209 | 1023 | 520.6 | 538.8 | 543.9 | 558.9 | 564 | 420.2 | 409.5 | 434.3
1210 | 1024 | 520.7 | 539.1 | 544.3 | 559.6 | 564.2 | 420.4 | 409.7 | 434.4
1211 | 1025 | 520.7 | 539.5 | 544.1 | 560.1 | 564.4 | 420.5 | 409.3 | 434.4
1212 | 1026 | 520.8 | 539.8 | 544.6 | 560.7 | 564.5 | 420.5 | 409.5 | 434.5
1213 | 1027 | 520.9 | 540 | 545.3 | 561.4 | 564.7 | 420.7 | 410.4 | 434.6
1214 | 1028 | 521 | 540.3 | 545.4 | 561.9 | 565.1 | 420.8 | 410.4 | 434.7
1215 | 1029 | 521 | 540.6 | 545.6 | 562.3 | 565.6 | 420.9 | 410 | 434.8
1216 | 1030 | 521.1 | 540.9 | 546.3 | 562.8 | 565.8 | 421 | 410.4 | 434.9
1217 | 1031 | 520.9 | 541.1 | 546.2 | 563.3 | 565.8 | 421.1 | 411.4 | 434.9
1218 | 1032 | 520.8 | 541.4 | 546.4 | 563.8 | 565.9 | 421.2 | 412.9 | 435
1219 | 1033 | 520.5 | 541.6 | 547.1 | 564.3 | 565.8 | 421.4 | 413.2 | 435
1220 | 1034 | 520.6 | 541.8 | 547.5 | 564.9 | 566 | 421.5 | 412.7 | 435
1221 | 1035 | 520.4 | 542.1 | 547.4 | 565.5 | 566.2 | 421.6 | 413.6 | 435
1222 | 1036 | 520.2 | 542.4 | 547.8 | 566 | 566.3 | 421.7 | 413.8 | 435.1
1223 | 1037 | 519.9 | 542.6 | 548.6 | 566.6 | 566.3 | 421.7 | 413.7 | 435.1
1224 | 1038 | 519.8 | 543 | 548.8 | 567.1 | 566.6 | 421.8 | 414.4 | 435.1
1225 | 1039 | 519.5 | 543.3 | 549.2 | 567.6 | 566.8 | 422 | 414.2 | 435.1
1226 | 1040 | 519.3 | 543.6 | 550.4 | 568.1 | 567 | 422.1 | 414.4 | 435.1
1227 | 1041 | 519.1 | 543.9 | 551.2 | 568.6 | 567.3 | 422.1 | 414.1 | 435.2
1228 | 1042 | 518.9 | 544.3 | 551.8 | 569.1 | 567.4 | 422.2 | 413 | 435.2
1229 | 1043 | 518.9 | 544.6 | 552.3 | 569.4 | 567.6 | 422.2 | 412.4 | 435.3
1230 | 1044 | 518.7 | 544.9 | 553 | 570.1 | 568 | 422.2 | 412.4 | 435.3
1231 | 1045 | 518.6 | 545.2 | 553.7 | 570.8 | 568.3 | 422.3 | 412.7 | 435.4
1232 | 1046 | 518.5 | 545.5 | 554.1 | 571.6 | 568.7 | 422.4 | 411.6 | 435.4
1233 | 1047 | 518.3 | 545.7 | 554.7 | 572 | 568.8 | 422.5 | 411.1 | 435.5
1234 | 1048 | 518.2 | 546 | 554.8 | 572.2 | 568.9 | 422.5 | 410.1 | 435.5
1235 | 1049 | 518.2 | 546.4 | 554.8 | 572.4 | 569.3 | 422.5 | 410.2 | 435.5
1236 | 1050 | 518.4 | 546.7 | 554.9 | 572.8 | 569.6 | 422.5 | 410.4 | 435.5
1237 | 1051 | 518.6 | 547 | 555.9 | 573.1 | 570.1 | 422.6 | 409.7 | 435.6
1238 | 1052 | 518.8 | 547.2 | 556.3 | 573.6 | 570.5 | 422.6 | 409.7 | 435.6
1239 | 1053 | 519.1 | 547.5 | 556.7 | 574 | 570.6 | 422.7 | 409.3 | 435.7
1240 | 1054 | 519.3 | 547.8 | 557 | 574.4 | 570.8 | 422.8 | 409.4 | 435.7
1241 | 1055 | 519.5 | 548.1 | 557.6 | 574.8 | 570.9 | 422.8 | 409.2 | 435.7
1242 | 1056 | 519.6 | 548.4 | 557.7 | 575.3 | 570.8 | 422.9 | 409.1 | 435.7
1243 | 1057 | 519.8 | 548.7 | 558.3 | 575.9 | 570.7 | 423.1 | 409.5 | 435.8
1244 | 1058 | 519.8 | 549 | 559 | 576.3 | 570.8 | 423.1 | 409.3 | 435.9
1245 | 1059 | 520.2 | 549.3 | 558.8 | 576.7 | 570.9 | 423.3 | 409.4 | 436
1246 | 1060 | 520.2 | 549.6 | 558.8 | 577 | 570.9 | 423.4 | 409.1 | 436
1247 | 1061 | 519.9 | 549.9 | 559.4 | 577.4 | 570.7 | 423.6 | 408.3 | 436.1
1248 | 1062 | 519.8 | 550.2 | 560.3 | 577.9 | 570.7 | 423.7 | 408.2 | 436.1
1249 | 1063 | 519.8 | 550.5 | 560.4 | 578.5 | 570.8 | 423.9 | 407.8 | 436.1
1250 | 1064 | 519.9 | 550.8 | 561.2 | 579.2 | 570.9 | 423.9 | 407.5 | 436.2
1251 | 1065 | 520 | 551.1 | 561.7 | 579.7 | 570.8 | 424 | 407.3 | 436.2
1252 | 1066 | 520 | 551.4 | 561.7 | 580.2 | 571.1 | 424.1 | 408.4 | 436.3
1253 | 1067 | 520 | 551.6 | 562.2 | 580.9 | 571.1 | 424.1 | 409.7 | 436.3
1254 | 1068 | 519.9 | 551.9 | 562.7 | 581.5 | 571.1 | 424.2 | 409.6 | 436.3
1255 | 1069 | 519.8 | 552.2 | 563.1 | 582 | 571.3 | 424.3 | 409.9 | 436.4
1256 | 1070 | 519.8 | 552.5 | 563.5 | 582.5 | 571.2 | 424.5 | 410.4 | 436.4
1257 | 1071 | 519.9 | 552.8 | 563.7 | 582.9 | 571.2 | 424.6 | 410 | 436.4
1258 | 1072 | 519.7 | 553.1 | 564 | 583.5 | 571.3 | 424.8 | 409.8 | 436.3
1259 | 1073 | 519.5 | 553.4 | 564.8 | 584.3 | 571.3 | 424.9 | 409.8 | 436.3
1260 | 1074 | 519.4 | 553.7 | 565.3 | 584.9 | 571.3 | 425.2 | 409.8 | 436.3
1261 | 1075 | 519.6 | 554.1 | 565.4 | 585.5 | 571.4 | 425.4 | 409.6 | 436.3
1262 | 1076 | 519.6 | 554.4 | 566.1 | 586 | 571.4 | 425.6 | 409.7 | 436.3
1263 | 1077 | 519.5 | 554.7 | 565.5 | 586.6 | 571.6 | 425.8 | 409.8 | 436.3
1264 | 1078 | 519.8 | 554.9 | 566.3 | 587.1 | 571.8 | 425.9 | 409.6 | 436.4
1265 | 1079 | 520 | 555.2 | 567.6 | 587.8 | 572.2 | 426 | 409.1 | 436.5
1266 | 1080 | 520.1 | 555.4 | 567.4 | 588.5 | 572.6 | 426 | 408.6 | 436.6
1267 | 1081 | 520.1 | 555.7 | 567.4 | 589.2 | 572.8 | 426.1 | 408.6 | 436.7
1268 | 1082 | 520.2 | 556 | 567.9 | 589.9 | 573 | 426.2 | 408.5 | 436.8
1269 | 1083 | 520.2 | 556.2 | 568.5 | 590.7 | 573.4 | 426.3 | 408.7 | 436.9
1270 | 1084 | 520.3 | 556.5 | 568.4 | 591.4 | 573.8 | 426.4 | 408.9 | 437
1271 | 1085 | 520.3 | 556.9 | 568.7 | 592 | 574.1 | 426.5 | 409.1 | 437.1
1272 | 1086 | 520.2 | 557.1 | 569.4 | 592.7 | 574.4 | 426.6 | 410 | 437.1
1273 | 1087 | 520 | 557.4 | 569.2 | 593.4 | 574.6 | 426.8 | 409.8 | 437.1
1274 | 1088 | 519.9 | 557.7 | 569.5 | 594.1 | 574.8 | 426.9 | 409 | 437.2
1275 | 1089 | 520.1 | 558 | 570.1 | 594.8 | 575 | 427.1 | 409.2 | 437.2
1276 | 1090 | 520.2 | 558.2 | 570.6 | 595.5 | 575.1 | 427.2 | 408.8 | 437.3
1277 | 1091 | 520 | 558.5 | 570.5 | 596.3 | 575.6 | 427.4 | 408.4 | 437.3
1278 | 1092 | 520 | 558.8 | 571.2 | 597.1 | 576 | 427.6 | 408.1 | 437.4
1279 | 1093 | 519.9 | 559 | 572.2 | 597.9 | 576.3 | 427.7 | 408.3 | 437.5
1280 | 1094 | 519.8 | 559.2 | 572 | 598.6 | 576.4 | 427.7 | 408.7 | 437.6
1281 | 1095 | 519.7 | 559.5 | 572.3 | 599.3 | 576.4 | 427.8 | 409.4 | 437.6
1282 | 1096 | 519.7 | 559.7 | 573.4 | 600 | 576.5 | 427.8 | 409.6 | 437.7
1283 | 1097 | 519.7 | 560 | 574.3 | 600.6 | 576.9 | 427.9 | 409 | 437.8
1284 | 1098 | 519.7 | 560.3 | 574.5 | 601.3 | 577.3 | 427.9 | 409.1 | 437.8
1285 | 1099 | 519.7 | 560.6 | 574.9 | 601.9 | 577.4 | 428 | 408.8 | 437.8
1286 | 1100 | 519.5 | 560.9 | 575.8 | 602.6 | 577.7 | 428.1 | 408.4 | 437.9
1287 | 1101 | 519.4 | 561.2 | 576 | 603.3 | 578.1 | 428.1 | 407.9 | 437.9
1288 | 1102 | 519.4 | 561.5 | 576.2 | 604 | 578.2 | 428.2 | 407.9 | 437.9
1289 | 1103 | 519.5 | 561.8 | 577 | 604.7 | 578.4 | 428.2 | 407.4 | 438
1290 | 1104 | 519.6 | 562 | 577.7 | 605.4 | 578.7 | 428.3 | 407 | 438.1
1291 | 1105 | 519.7 | 562.3 | 578 | 606.1 | 579 | 428.4 | 407.2 | 438.2
1292 | 1106 | 519.6 | 562.6 | 578.5 | 606.8 | 579.3 | 428.4 | 407.2 | 438.2
1293 | 1107 | 519.2 | 562.8 | 579.2 | 607.4 | 579.5 | 428.4 | 407.2 | 438.2
1294 | 1108 | 519 | 563.1 | 578.9 | 607.9 | 579.7 | 428.5 | 407.3 | 438.3
1295 | 1109 | 518.9 | 563.4 | 578.9 | 608.4 | 579.8 | 428.7 | 407.7 | 438.3
1296 | 1110 | 518.8 | 563.6 | 579.4 | 608.8 | 580.2 | 428.9 | 407.4 | 438.4
1297 | 1111 | 518.8 | 563.9 | 579.8 | 609.4 | 580.4 | 429.1 | 407.2 | 438.4
1298 | 1112 | 518.9 | 564.1 | 579.7 | 610.1 | 580.5 | 429.1 | 406.8 | 438.4
1299 | 1113 | 519 | 564.4 | 580 | 610.9 | 580.7 | 429.2 | 406.5 | 438.5
1300 | 1114 | 519.1 | 564.5 | 581.1 | 611.7 | 581 | 429.3 | 406.3 | 438.6
1301 | 1115 | 519.1 | 564.8 | 581.1 | 612.5 | 581.3 | 429.4 | 406.1 | 438.6
1302 | 1116 | 519.3 | 565 | 581.3 | 613.2 | 581.6 | 429.4 | 405.8 | 438.7
1303 | 1117 | 519.6 | 565.2 | 582 | 613.8 | 581.9 | 429.4 | 405.1 | 438.8
1304 | 1118 | 519.6 | 565.5 | 582.5 | 614.4 | 582.2 | 429.4 | 404.9 | 438.8
1305 | 1119 | 519.6 | 565.7 | 583.1 | 615 | 582.4 | 429.6 | 404.8 | 438.9
1306 | 1120 | 519.8 | 565.9 | 583.9 | 615.8 | 582.7 | 429.6 | 404.3 | 439
1307 | 1121 | 520 | 566.2 | 584.3 | 616.4 | 582.9 | 429.7 | 404.3 | 439.1
1308 | 1122 | 520.2 | 566.5 | 584.8 | 616.9 | 583.3 | 429.8 | 404 | 439.1
1309 | 1123 | 520.3 | 566.7 | 585.2 | 617.6 | 583.5 | 430 | 404.6 | 439.2
1310 | 1124 | 520.5 | 567 | 585.5 | 618.3 | 583.6 | 430.2 | 404.4 | 439.3
1311 | 1125 | 520.7 | 567.2 | 586 | 619.1 | 583.9 | 430.4 | 404.7 | 439.3
1312 | 1126 | 520.8 | 567.5 | 586.5 | 619.7 | 584.2 | 430.5 | 404.7 | 439.4
1313 | 1127 | 520.9 | 567.7 | 587 | 620.3 | 584.5 | 430.6 | 404.3 | 439.4
1314 | 1128 | 521.2 | 568 | 587.6 | 620.9 | 584.7 | 430.6 | 404.3 | 439.5
1315 | 1129 | 521.3 | 568.3 | 588.1 | 621.4 | 585.2 | 430.6 | 404 | 439.6
1316 | 1130 | 521.5 | 568.6 | 588.6 | 621.8 | 585.6 | 430.6 | 403.6 | 439.7
1317 | 1131 | 521.5 | 568.8 | 589.1 | 622.4 | 585.8 | 430.8 | 402.9 | 439.7
1318 | 1132 | 521.3 | 569.1 | 589.4 | 622.9 | 586.4 | 430.9 | 403.9 | 439.8
1319 | 1133 | 521 | 569.4 | 590 | 623.7 | 586.7 | 430.9 | 403.9 | 439.9
1320 | 1134 | 521 | 569.7 | 589.7 | 624.3 | 586.9 | 431 | 403.2 | 439.9
1321 | 1135 | 521.1 | 569.9 | 590.7 | 624.9 | 587.1 | 431 | 403 | 440
1322 | 1136 | 520.8 | 570.2 | 591 | 625.5 | 587.4 | 431.1 | 403 | 440.1
1323 | 1137 | 520.6 | 570.5 | 591.3 | 626.1 | 587.5 | 431.1 | 403 | 440.2
1324 | 1138 | 520.3 | 570.8 | 592.3 | 626.7 | 587.7 | 431.1 | 402.9 | 440.2
1325 | 1139 | 520.1 | 571.1 | 593.1 | 627.4 | 587.8 | 431.2 | 402.9 | 440.3
1326 | 1140 | 520.1 | 571.4 | 593 | 628 | 588 | 431.3 | 402.8 | 440.3
1327 | 1141 | 519.9 | 571.8 | 593.5 | 628.5 | 588.2 | 431.4 | 403.1 | 440.4
1328 | 1142 | 519.9 | 572.1 | 594.5 | 629 | 588.4 | 431.7 | 402.9 | 440.5
1329 | 1143 | 520 | 572.4 | 594.6 | 629.7 | 588.6 | 431.8 | 403.1 | 440.5
1330 | 1144 | 520.2 | 572.7 | 594.9 | 630.3 | 588.8 | 431.9 | 402.9 | 440.6
1331 | 1145 | 520.2 | 573 | 596.1 | 630.9 | 588.9 | 431.9 | 402.5 | 440.7
1332 | 1146 | 520.1 | 573.3 | 596.7 | 631.4 | 589.1 | 432.1 | 401.8 | 440.8
1333 | 1147 | 520.2 | 573.6 | 597.1 | 631.9 | 589.3 | 432.2 | 401.8 | 440.9
1334 | 1148 | 520.3 | 573.8 | 597.4 | 632.5 | 589.6 | 432.3 | 402.2 | 440.9
1335 | 1149 | 520.4 | 574.1 | 597.5 | 632.9 | 590 | 432.6 | 402.4 | 441
1336 | 1150 | 520.6 | 574.4 | 597.4 | 633.4 | 590.4 | 432.8 | 403.1 | 441.1
1337 | 1151 | 520.7 | 574.6 | 597.6 | 634 | 590.8 | 432.8 | 403 | 441.1
1338 | 1152 | 520.7 | 574.8 | 598.2 | 634.8 | 591.3 | 432.8 | 403 | 441.2
1339 | 1153 | 520.9 | 575 | 598.7 | 635.3 | 591.9 | 432.9 | 402.2 | 441.3
1340 | 1154 | 520.9 | 575.2 | 598.8 | 635.8 | 592.4 | 433 | 402 | 441.4
1341 | 1155 | 521 | 575.5 | 599.2 | 636.3 | 592.9 | 433.1 | 402.2 | 441.5
1342 | 1156 | 521.1 | 575.6 | 600.1 | 636.7 | 593.3 | 433.2 | 402.3 | 441.6
1343 | 1157 | 521.1 | 575.8 | 600.1 | 637.1 | 593.7 | 433.3 | 402.2 | 441.7
1344 | 1158 | 521.3 | 576 | 601.1 | 637.4 | 594.1 | 433.4 | 401.9 | 441.8
1345 | 1159 | 521.4 | 576.2 | 601.4 | 637.8 | 594.5 | 433.4 | 402.5 | 441.8
1346 | 1160 | 521.6 | 576.4 | 601.7 | 638.2 | 594.9 | 433.4 | 402.1 | 441.9
1347 | 1161 | 521.6 | 576.6 | 602.2 | 638.7 | 595.3 | 433.5 | 402.5 | 442
1348 | 1162 | 521.5 | 576.8 | 601.9 | 639.2 | 595.9 | 433.5 | 403.7 | 442
1349 | 1163 | 521.5 | 577 | 602.6 | 639.5 | 596.3 | 433.6 | 403.1 | 442.1
1350 | 1164 | 521.5 | 577.3 | 602.8 | 640 | 596.9 | 433.6 | 402.8 | 442.1
1351 | 1165 | 521.5 | 577.5 | 603 | 640.2 | 597.4 | 433.5 | 402.5 | 442.2
1352 | 1166 | 521.4 | 577.7 | 603.6 | 640.4 | 597.8 | 433.5 | 403 | 442.3
1353 | 1167 | 521.1 | 577.9 | 604.1 | 640.5 | 598.1 | 433.6 | 403 | 442.3
1354 | 1168 | 520.9 | 578.2 | 604.3 | 640.6 | 598.5 | 433.6 | 403.1 | 442.4
1355 | 1169 | 520.9 | 578.4 | 604.3 | 640.8 | 598.8 | 433.7 | 403.5 | 442.3
1356 | 1170 | 520.8 | 578.7 | 605.1 | 640.8 | 599.2 | 433.7 | 403.7 | 442.4
1357 | 1171 | 520.7 | 578.9 | 605.1 | 640.9 | 599.8 | 433.9 | 402.8 | 442.4
1358 | 1172 | 520.5 | 579.2 | 606.1 | 640.9 | 599.9 | 433.9 | 403.7 | 442.4
1359 | 1173 | 520.3 | 579.5 | 606.6 | 640.9 | 600.3 | 433.9 | 402.5 | 442.5
1360 | 1174 | 520.2 | 579.8 | 607.2 | 641.3 | 600.5 | 433.9 | 402.4 | 442.5
1361 | 1175 | 520.4 | 580.2 | 607.7 | 641.8 | 600.9 | 433.9 | 403 | 442.5
1362 | 1176 | 520.3 | 580.5 | 608 | 641.9 | 601.1 | 434 | 402.5 | 442.6
1363 | 1177 | 520.1 | 580.8 | 608.3 | 642 | 601.6 | 434 | 402.3 | 442.6
1364 | 1178 | 519.9 | 581.2 | 608.9 | 642.2 | 602 | 434.2 | 402.2 | 442.6
1365 | 1179 | 519.8 | 581.5 | 609.8 | 642.5 | 602.4 | 434.3 | 402.3 | 442.7
1366 | 1180 | 520.1 | 581.8 | 610.9 | 643 | 602.8 | 434.4 | 402.4 | 442.7
1367 | 1181 | 520.1 | 582.1 | 611.4 | 643.2 | 603.1 | 434.5 | 402.3 | 442.7
1368 | 1182 | 520.1 | 582.4 | 612 | 643.3 | 603.3 | 434.6 | 402.7 | 442.8
1369 | 1183 | 520.2 | 582.7 | 612.4 | 643.4 | 603.5 | 434.6 | 402.4 | 442.9
1370 | 1184 | 520 | 583 | 612.6 | 643.5 | 603.9 | 434.7 | 402.8 | 442.9
1371 | 1185 | 520 | 583.4 | 613.1 | 643.6 | 604.2 | 434.7 | 403.3 | 442.9
1372 | 1186 | 520.1 | 583.7 | 613.5 | 643.7 | 604.5 | 434.6 | 403.7 | 443
1373 | 1187 | 520.3 | 584 | 613.3 | 643.8 | 604.8 | 434.5 | 403.3 | 443
1374 | 1188 | 520.5 | 584.3 | 613.7 | 643.9 | 605.1 | 434.5 | 402.9 | 443
1375 | 1189 | 520.6 | 584.6 | 613.8 | 644 | 605.4 | 434.5 | 402.4 | 443
1376 | 1190 | 520.8 | 585 | 614 | 643.9 | 605.6 | 434.5 | 401.9 | 443.1
1377 | 1191 | 520.8 | 585.2 | 614.9 | 643.9 | 605.8 | 434.4 | 401.7 | 443.2
1378 | 1192 | 520.8 | 585.5 | 615 | 643.9 | 606 | 434.5 | 401.7 | 443.2
1379 | 1193 | 521.1 | 585.8 | 615.1 | 644 | 606.1 | 434.5 | 402 | 443.3
1380 | 1194 | 521.4 | 586 | 615.6 | 644 | 606.2 | 434.5 | 401.7 | 443.3
1381 | 1195 | 521.5 | 586.3 | 616.1 | 644.1 | 606.3 | 434.6 | 401.9 | 443.4
1382 | 1196 | 521.4 | 586.6 | 615.9 | 644.4 | 606.5 | 434.6 | 402.4 | 443.4
1383 | 1197 | 521.2 | 586.9 | 616.2 | 644.8 | 606.6 | 434.6 | 402.3 | 443.5
1384 | 1198 | 521.1 | 587.1 | 616.6 | 645.2 | 606.9 | 434.6 | 402.6 | 443.6
1385 | 1199 | 521 | 587.4 | 616.4 | 645.6 | 607.3 | 434.7 | 402.8 | 443.6
1386 | 1200 | 520.8 | 587.7 | 616.7 | 645.7 | 607.5 | 434.7 | 402.8 | 443.6
1387 | 1201 | 520.6 | 587.9 | 617.4 | 645.9 | 607.5 | 434.7 | 402.8 | 443.7
1388 | 1202 | 520.4 | 588.2 | 618.2 | 646 | 607.6 | 434.7 | 402.6 | 443.8
1389 | 1203 | 520.5 | 588.6 | 618.7 | 646.2 | 607.6 | 434.7 | 402.2 | 443.9
1390 | 1204 | 520.4 | 588.9 | 619.6 | 646.4 | 607.7 | 434.7 | 402.2 | 444
1391 | 1205 | 520.3 | 589.2 | 620.8 | 646.5 | 607.7 | 434.8 | 401.5 | 444.1
1392 | 1206 | 520.4 | 589.6 | 621.1 | 646.9 | 607.7 | 434.8 | 401.9 | 444.2
1393 | 1207 | 520.4 | 589.9 | 621.5 | 647.1 | 608 | 434.8 | 402.3 | 444.3
1394 | 1208 | 520.2 | 590.2 | 621.7 | 647 | 608.4 | 434.7 | 402.6 | 444.4
1395 | 1209 | 520.2 | 590.5 | 622.4 | 646.9 | 608.7 | 434.7 | 402.6 | 444.5
1396 | 1210 | 520.1 | 590.8 | 622.6 | 646.9 | 609.1 | 434.6 | 402 | 444.5
1397 | 1211 | 520 | 591.1 | 622.9 | 646.9 | 609 | 434.6 | 401.4 | 444.6
1398 | 1212 | 519.9 | 591.3 | 623.8 | 647 | 608.9 | 434.6 | 401.2 | 444.6
1399 | 1213 | 519.8 | 591.6 | 624.3 | 647.4 | 609 | 434.6 | 400.9 | 444.7
1400 | 1214 | 519.6 | 591.9 | 624.3 | 647.6 | 609.1 | 434.6 | 400.4 | 444.7
1401 | 1215 | 519.3 | 592.2 | 624.7 | 647.6 | 609.4 | 434.6 | 400.5 | 444.8
1402 | 1216 | 519 | 592.5 | 624.9 | 647.6 | 609.5 | 434.6 | 400.1 | 444.9
1403 | 1217 | 518.8 | 592.8 | 625.2 | 647.8 | 609.6 | 434.6 | 400.1 | 444.9
1404 | 1218 | 519 | 593.2 | 625.8 | 648.1 | 609.7 | 434.7 | 400.2 | 445
1405 | 1219 | 519.3 | 593.5 | 626.6 | 648.4 | 609.6 | 434.7 | 400.1 | 445.1
1406 | 1220 | 519.6 | 593.8 | 626.6 | 648.5 | 609.9 | 434.7 | 400.1 | 445.2
1407 | 1221 | 519.7 | 594.1 | 626.3 | 648.4 | 610.1 | 434.8 | 399.9 | 445.2
1408 | 1222 | 519.7 | 594.4 | 626.8 | 648.4 | 610 | 434.7 | 399.4 | 445.2
1409 | 1223 | 519.9 | 594.6 | 627.1 | 648.5 | 609.9 | 434.7 | 398.7 | 445.3
1410 | 1224 | 519.8 | 595 | 627.2 | 648.7 | 610.4 | 434.6 | 399.1 | 445.3
1411 | 1225 | 519.9 | 595.3 | 628 | 649 | 610.3 | 434.5 | 399.1 | 445.4
1412 | 1226 | 519.8 | 595.5 | 629.1 | 649.3 | 610.2 | 434.5 | 399.3 | 445.5
1413 | 1227 | 519.4 | 595.8 | 629 | 649.4 | 610.2 | 434.5 | 399.2 | 445.5
1414 | 1228 | 519 | 596.2 | 628.9 | 649.5 | 610.4 | 434.4 | 398.9 | 445.5
1415 | 1229 | 518.7 | 596.6 | 629.1 | 649.4 | 610.6 | 434.4 | 398.7 | 445.6
1416 | 1230 | 518.5 | 596.9 | 629.3 | 649.5 | 610.5 | 434.2 | 398.4 | 445.7
1417 | 1231 | 518.4 | 597.3 | 628.9 | 649.4 | 610.8 | 434.1 | 398.5 | 445.7
1418 | 1232 | 518.4 | 597.7 | 629 | 649.3 | 610.8 | 434 | 398.8 | 445.8
1419 | 1233 | 518.3 | 598 | 629.4 | 649.3 | 610.7 | 434 | 398.4 | 445.9
1420 | 1234 | 518.2 | 598.3 | 629.1 | 649.3 | 611.1 | 434.1 | 398.3 | 446
1421 | 1235 | 518.3 | 598.6 | 629 | 649.3 | 611.2 | 434.1 | 398.4 | 446
1422 | 1236 | 518.5 | 598.8 | 629.3 | 649.4 | 611.1 | 434.1 | 398.3 | 446.1
1423 | 1237 | 518.7 | 599.1 | 629.8 | 649.5 | 611.3 | 434.1 | 398.4 | 446.1
1424 | 1238 | 518.9 | 599.4 | 629.5 | 649.6 | 611.3 | 434 | 398.8 | 446.2
1425 | 1239 | 519 | 599.6 | 629.6 | 649.8 | 611.5 | 434 | 399.2 | 446.2
1426 | 1240 | 519 | 599.8 | 630.4 | 650 | 611.5 | 434 | 399.5 | 446.2
1427 | 1241 | 518.8 | 600.2 | 630.8 | 650.2 | 611.5 | 434 | 398.7 | 446.2
1428 | 1242 | 518.9 | 600.5 | 631.1 | 650.4 | 611.4 | 434 | 398.6 | 446.3
1429 | 1243 | 518.9 | 600.9 | 631.8 | 650.5 | 611.5 | 434.1 | 398.5 | 446.3
1430 | 1244 | 518.9 | 601.3 | 632.4 | 650.6 | 611.7 | 434.3 | 397.7 | 446.4
1431 | 1245 | 518.8 | 601.7 | 632.2 | 650.7 | 611.9 | 434.3 | 397.3 | 446.4
1432 | 1246 | 518.9 | 602 | 632.3 | 650.7 | 612 | 434.4 | 397 | 446.5
1433 | 1247 | 519.1 | 602.2 | 632.8 | 650.7 | 611.9 | 434.4 | 396.8 | 446.5
1434 | 1248 | 519 | 602.6 | 633 | 650.8 | 612.2 | 434.4 | 396.8 | 446.5
1435 | 1249 | 518.8 | 603 | 633.5 | 651.1 | 612.3 | 434.5 | 396.9 | 446.5
1436 | 1250 | 518.8 | 603.3 | 633.7 | 651.1 | 612.4 | 434.5 | 396.7 | 446.6
1437 | 1251 | 519 | 603.6 | 633.6 | 651.1 | 612.4 | 434.4 | 397 | 446.6
1438 | 1252 | 519.3 | 603.9 | 633.1 | 651 | 612.6 | 434.4 | 396.1 | 446.6
1439 | 1253 | 519.5 | 604.2 | 633.5 | 651.1 | 612.8 | 434.5 | 396.2 | 446.6
1440 | 1254 | 519.8 | 604.4 | 634 | 651.1 | 613 | 434.5 | 396.8 | 446.7
1441 | 1255 | 520.1 | 604.7 | 633.5 | 650.9 | 613.2 | 434.5 | 397.1 | 446.7
1442 | 1256 | 520.1 | 604.9 | 633.2 | 650.9 | 613.5 | 434.6 | 397.5 | 446.8
1443 | 1257 | 520.3 | 605.1 | 633.5 | 650.8 | 613.7 | 434.7 | 397.6 | 446.8
1444 | 1258 | 520.4 | 605.3 | 633.7 | 650.9 | 613.9 | 434.9 | 397.8 | 446.9
1445 | 1259 | 520.5 | 605.6 | 633.4 | 650.9 | 614 | 435 | 398.1 | 446.9
1446 | 1260 | 520.6 | 605.9 | 633.5 | 650.8 | 614.1 | 435.1 | 397.9 | 446.9
1447 | 1261 | 520.6 | 606.1 | 633.8 | 650.7 | 614.1 | 435.3 | 398 | 447
1448 | 1262 | 520.5 | 606.5 | 633.6 | 650.7 | 614.5 | 435.5 | 397.7 | 447
1449 | 1263 | 520.7 | 606.8 | 633.4 | 650.6 | 614.6 | 435.6 | 397.7 | 447.1
1450 | 1264 | 520.9 | 607 | 633.7 | 650.4 | 614.5 | 435.6 | 398 | 447.1
1451 | 1265 | 520.9 | 607.3 | 633.9 | 650.3 | 614.6 | 435.6 | 398.2 | 447.2
1452 | 1266 | 520.8 | 607.6 | 633.6 | 650.3 | 615 | 435.6 | 398.3 | 447.2
1453 | 1267 | 520.6 | 607.9 | 633.8 | 650.3 | 614.9 | 435.6 | 398.6 | 447.2
1454 | 1268 | 520.4 | 608.2 | 634.4 | 650.1 | 615.2 | 435.6 | 398.2 | 447.2
1455 | 1269 | 520.4 | 608.5 | 634.1 | 650 | 615.6 | 435.7 | 397.6 | 447.2
1456 | 1270 | 520.4 | 608.8 | 634 | 649.9 | 615.3 | 435.8 | 397.7 | 447.2
1457 | 1271 | 520.3 | 609.1 | 634.5 | 649.7 | 614.6 | 435.8 | 397.4 | 447.3
1458 | 1272 | 520 | 609.3 | 634.9 | 649.5 | 614.6 | 435.8 | 397.7 | 447.3
1459 | 1273 | 519.9 | 609.5 | 634.8 | 649.4 | 614.5 | 435.8 | 398 | 447.3
1460 | 1274 | 519.9 | 609.8 | 635 | 649.3 | 614.6 | 435.8 | 398.8 | 447.4
1461 | 1275 | 519.9 | 610.1 | 635.5 | 649 | 614.8 | 435.8 | 398.4 | 447.4
1462 | 1276 | 519.7 | 610.3 | 635.4 | 648.8 | 614.9 | 435.6 | 398.4 | 447.4
1463 | 1277 | 519.5 | 610.7 | 635.5 | 648.7 | 614.6 | 435.5 | 398.2 | 447.5
1464 | 1278 | 519.5 | 610.9 | 636.3 | 648.5 | 614.4 | 435.5 | 398.5 | 447.6
1465 | 1279 | 519.6 | 611.3 | 636.6 | 648.3 | 614.7 | 435.5 | 398.4 | 447.6
1466 | 1280 | 519.5 | 611.6 | 636.1 | 648 | 615 | 435.5 | 398.2 | 447.6
1467 | 1281 | 519.3 | 611.9 | 636 | 647.7 | 615.2 | 435.5 | 398 | 447.6
1468 | 1282 | 519.2 | 612.1 | 636.5 | 647.5 | 615.1 | 435.6 | 398.6 | 447.7
1469 | 1283 | 519.3 | 612.4 | 636.3 | 647.3 | 615.2 | 435.5 | 398.5 | 447.7
1470 | 1284 | 519.3 | 612.8 | 636.2 | 647.1 | 615.2 | 435.5 | 399.2 | 447.7
1471 | 1285 | 519.3 | 613.1 | 636.5 | 647 | 615.5 | 435.5 | 399.2 | 447.7
1472 | 1286 | 519.3 | 613.4 | 636.9 | 646.7 | 615.7 | 435.5 | 400.1 | 447.7
1473 | 1287 | 519.4 | 613.7 | 636.4 | 646.5 | 615.8 | 435.5 | 400.4 | 447.7
1474 | 1288 | 519.3 | 614 | 636.6 | 646.4 | 616.1 | 435.4 | 401 | 447.7
1475 | 1289 | 519.3 | 614.1 | 637.3 | 646.2 | 616.1 | 435.3 | 401.4 | 447.8
1476 | 1290 | 519.4 | 614.4 | 637.2 | 645.9 | 616.3 | 435.2 | 401.2 | 447.7
1477 | 1291 | 519.4 | 614.6 | 637.3 | 645.6 | 616.3 | 435.2 | 401.8 | 447.7
1478 | 1292 | 519.6 | 614.8 | 637.4 | 645.3 | 616.3 | 435.1 | 401.3 | 447.7
1479 | 1293 | 519.6 | 615 | 637.7 | 644.9 | 616.2 | 435.1 | 400.6 | 447.7
1480 | 1294 | 519.5 | 615.3 | 637.5 | 644.7 | 616.4 | 435.1 | 400.9 | 447.7
1481 | 1295 | 519.5 | 615.5 | 637.6 | 644.4 | 616.2 | 435.1 | 400.3 | 447.7
1482 | 1296 | 519.6 | 615.7 | 638 | 644.1 | 615.8 | 435.1 | 400.5 | 447.8
1483 | 1297 | 519.5 | 615.9 | 637.8 | 643.8 | 615.7 | 435.1 | 400.6 | 447.8
1484 | 1298 | 519.5 | 616.1 | 637.9 | 643.5 | 615.9 | 435.2 | 400.3 | 447.9
1485 | 1299 | 519.5 | 616.2 | 638.3 | 643.2 | 615.9 | 435.2 | 400.8 | 447.9
1486 | 1300 | 519.2 | 616.4 | 639.1 | 642.9 | 616 | 435.2 | 400.2 | 448
1487 | 1301 | 519.1 | 616.7 | 638.9 | 642.6 | 616.2 | 435.3 | 400.2 | 448
1488 | 1302 | 518.9 | 616.9 | 639.3 | 642.2 | 616.2 | 435.4 | 400.2 | 448
1489 | 1303 | 518.9 | 617.1 | 639.9 | 641.8 | 616.2 | 435.4 | 399.9 | 448.1
1490 | 1304 | 519 | 617.4 | 639.6 | 641.4 | 616.6 | 435.4 | 400 | 448.1
1491 | 1305 | 519.1 | 617.7 | 639.3 | 641 | 616.7 | 435.5 | 400 | 448.1
1492 | 1306 | 519.2 | 617.9 | 639.5 | 640.6 | 616.6 | 435.5 | 400.2 | 448
1493 | 1307 | 519.4 | 618.2 | 639.6 | 640.2 | 616.7 | 435.5 | 400.9 | 448.1
1494 | 1308 | 519.3 | 618.5 | 639.2 | 639.8 | 616.9 | 435.6 | 401.2 | 448.1
1495 | 1309 | 519.2 | 618.7 | 639.2 | 639.4 | 617.1 | 435.6 | 401 | 448.1
1496 | 1310 | 519.2 | 618.9 | 639.7 | 638.9 | 617 | 435.6 | 401.2 | 448.2
1497 | 1311 | 519.1 | 619.1 | 640 | 638.5 | 616.7 | 435.5 | 401.2 | 448.2
1498 | 1312 | 519.1 | 619.4 | 640.1 | 638.1 | 616.7 | 435.6 | 401.3 | 448.2
1499 | 1313 | 519.1 | 619.5 | 640.1 | 637.6 | 616.6 | 435.6 | 400.9 | 448.3
1500 | 1314 | 519.1 | 619.7 | 640.1 | 637.1 | 616.4 | 435.6 | 400.6 | 448.4
1501 | 1315 | 518.9 | 620 | 639.5 | 636.6 | 616.4 | 435.7 | 399.7 | 448.4
1502 | 1316 | 518.9 | 620.2 | 639.6 | 636.2 | 616 | 435.8 | 400 | 448.4
1503 | 1317 | 518.9 | 620.4 | 640.4 | 635.7 | 615.6 | 435.8 | 399.3 | 448.5
1504 | 1318 | 518.8 | 620.6 | 640.4 | 635.3 | 615.7 | 435.9 | 399 | 448.5
1505 | 1319 | 518.7 | 620.8 | 640.1 | 634.7 | 615.7 | 435.9 | 398.7 | 448.6
1506 | 1320 | 518.7 | 621 | 640.2 | 634.2 | 615.6 | 435.9 | 398.3 | 448.7
1507 | 1321 | 518.8 | 621.2 | 640.6 | 633.6 | 615.5 | 435.9 | 398.1 | 448.7
1508 | 1322 | 518.9 | 621.4 | 640.5 | 633.1 | 615.7 | 436 | 397.8 | 448.7
1509 | 1323 | 519 | 621.6 | 640.7 | 632.5 | 615.5 | 436 | 397.5 | 448.8
1510 | 1324 | 519.1 | 621.8 | 641.3 | 632 | 615.2 | 435.9 | 397.7 | 448.8
1511 | 1325 | 519.3 | 622 | 641.3 | 631.4 | 615.1 | 435.8 | 397.3 | 448.8
1512 | 1326 | 519.4 | 622.2 | 641.4 | 630.7 | 615.1 | 435.8 | 396.6 | 448.9
1513 | 1327 | 519.5 | 622.3 | 641.7 | 630.1 | 615 | 435.7 | 397.5 | 448.9
1514 | 1328 | 519.6 | 622.5 | 642 | 629.5 | 614.9 | 435.7 | 397.2 | 449
1515 | 1329 | 519.9 | 622.7 | 641.3 | 629 | 615 | 435.7 | 396.9 | 449
1516 | 1330 | 520.1 | 622.8 | 641.3 | 628.5 | 614.8 | 435.7 | 396.8 | 449.1
1517 | 1331 | 520.3 | 622.9 | 641.6 | 627.9 | 614.4 | 435.7 | 396.8 | 449.1
1518 | 1332 | 520.5 | 623.1 | 641.4 | 627.3 | 614.4 | 435.8 | 397.3 | 449.2
1519 | 1333 | 520.6 | 623.3 | 641.3 | 626.6 | 614.4 | 435.9 | 397.4 | 449.3
1520 | 1334 | 520.5 | 623.5 | 641.5 | 626 | 614.3 | 436 | 397.8 | 449.3
1521 | 1335 | 520.4 | 623.7 | 641.8 | 625.3 | 614.1 | 436.1 | 397.2 | 449.3
1522 | 1336 | 520.5 | 623.9 | 641.4 | 624.6 | 614.2 | 436.1 | 397.1 | 449.3
1523 | 1337 | 520.5 | 624 | 641.4 | 623.9 | 614.2 | 436.3 | 397.3 | 449.4
1524 | 1338 | 520.5 | 624.1 | 642 | 623.2 | 614.1 | 436.4 | 396.9 | 449.4
1525 | 1339 | 520.5 | 624.2 | 641.7 | 622.6 | 613.8 | 436.6 | 396.2 | 449.4
1526 | 1340 | 520.6 | 624.4 | 641.4 | 622 | 613.8 | 436.6 | 396.2 | 449.5
1527 | 1341 | 520.6 | 624.6 | 641.8 | 621.5 | 613.8 | 436.7 | 395.8 | 449.6
1528 | 1342 | 520.5 | 624.9 | 642.1 | 621 | 613.8 | 436.7 | 395.7 | 449.6
1529 | 1343 | 520.5 | 625.1 | 641.7 | 620.5 | 614 | 436.9 | 395.3 | 449.6
1530 | 1344 | 520.4 | 625.3 | 641.6 | 619.9 | 614 | 437 | 395.4 | 449.6
1531 | 1345 | 520.4 | 625.6 | 641.7 | 619.5 | 613.6 | 437.1 | 394.8 | 449.7
1532 | 1346 | 520.3 | 625.9 | 641.2 | 619 | 613.5 | 437.2 | 395 | 449.7
1533 | 1347 | 520.2 | 626.1 | 640.7 | 618.6 | 613.8 | 437.2 | 395.2 | 449.8
1534 | 1348 | 520 | 626.2 | 640.6 | 618.1 | 613.9 | 437.3 | 394.6 | 449.8
1535 | 1349 | 519.9 | 626.4 | 640.6 | 617.7 | 613.7 | 437.3 | 394.9 | 449.8
1536 | 1350 | 519.9 | 626.6 | 640 | 617.3 | 613.9 | 437.4 | 395.2 | 449.8
1537 | 1351 | 519.6 | 626.7 | 639.8 | 616.9 | 613.9 | 437.6 | 395.5 | 449.9
1538 | 1352 | 519.5 | 626.7 | 640.2 | 616.5 | 613.6 | 437.6 | 395.7 | 449.9
1539 | 1353 | 519.5 | 626.9 | 639.8 | 616.1 | 613.4 | 437.7 | 395 | 449.9
1540 | 1354 | 519.2 | 627.1 | 639.6 | 615.6 | 613.2 | 437.8 | 394.9 | 450
1541 | 1355 | 518.9 | 627.2 | 639.9 | 615.1 | 612.9 | 437.9 | 394.4 | 450
1542 | 1356 | 518.9 | 627.4 | 640 | 614.7 | 612.6 | 438 | 394.4 | 450.1
1543 | 1357 | 518.8 | 627.6 | 639.4 | 614.3 | 612.9 | 438.1 | 394.4 | 450.1
1544 | 1358 | 518.8 | 627.8 | 639.2 | 613.9 | 613.1 | 438.2 | 394 | 450.1
1545 | 1359 | 519 | 627.9 | 639.4 | 613.5 | 612.9 | 438.2 | 393.9 | 450.1
1546 | 1360 | 519.1 | 628.1 | 638.9 | 613 | 612.9 | 438.2 | 394.5 | 450.2
1547 | 1361 | 519 | 628.2 | 638.6 | 612.5 | 613.1 | 438.3 | 394.4 | 450.2
1548 | 1362 | 518.8 | 628.2 | 638.6 | 611.9 | 612.7 | 438.3 | 394.6 | 450.2
1549 | 1363 | 518.8 | 628.3 | 638.8 | 611.4 | 612.3 | 438.3 | 394 | 450.3
1550 | 1364 | 518.7 | 628.5 | 638.2 | 610.9 | 612.4 | 438.4 | 394.1 | 450.3
1551 | 1365 | 518.5 | 628.6 | 637.9 | 610.5 | 612.3 | 438.5 | 394.2 | 450.3
1552 | 1366 | 518.5 | 628.7 | 638.2 | 609.9 | 611.9 | 438.6 | 394.3 | 450.4
1553 | 1367 | 518.6 | 628.9 | 637.8 | 609.4 | 611.8 | 438.7 | 393.7 | 450.4
1554 | 1368 | 518.5 | 629.1 | 637.5 | 608.9 | 611.7 | 438.7 | 393.5 | 450.4
1555 | 1369 | 518.5 | 629.3 | 637.6 | 608.3 | 611.4 | 438.6 | 393.5 | 450.5
1556 | 1370 | 518.6 | 629.5 | 637.9 | 607.6 | 611.3 | 438.6 | 394.5 | 450.5
1557 | 1371 | 518.7 | 629.7 | 637.5 | 607 | 611.4 | 438.6 | 394.1 | 450.5
1558 | 1372 | 518.8 | 629.8 | 637.3 | 606.5 | 611.3 | 438.6 | 393.5 | 450.5
1559 | 1373 | 519 | 629.9 | 637.4 | 606 | 611.1 | 438.6 | 394.5 | 450.5
1560 | 1374 | 519.1 | 630 | 637 | 605.6 | 611.5 | 438.7 | 394 | 450.5
1561 | 1375 | 519 | 630.2 | 636.6 | 605.2 | 612 | 438.8 | 393.9 | 450.4
1562 | 1376 | 518.8 | 630.3 | 636.5 | 604.8 | 611.8 | 438.9 | 393.7 | 450.4
1563 | 1377 | 518.7 | 630.4 | 636.6 | 604.4 | 611.5 | 438.9 | 393.3 | 450.4
1564 | 1378 | 518.7 | 630.5 | 635.9 | 604 | 611.4 | 439 | 393.3 | 450.4
1565 | 1379 | 518.7 | 630.7 | 635.8 | 603.5 | 611.2 | 439 | 393.2 | 450.4
1566 | 1380 | 518.6 | 630.7 | 636 | 603.1 | 610.8 | 438.9 | 393 | 450.5
1567 | 1381 | 518.4 | 630.8 | 635.5 | 602.6 | 610.6 | 438.9 | 393.2 | 450.4
1568 | 1382 | 518.4 | 630.9 | 635 | 602.2 | 610.4 | 438.9 | 394.2 | 450.4
1569 | 1383 | 518.5 | 631 | 635.1 | 601.9 | 610.4 | 438.9 | 394.1 | 450.4
1570 | 1384 | 518.7 | 631.1 | 635.1 | 601.6 | 610.7 | 439 | 394.2 | 450.4
1571 | 1385 | 518.8 | 631.2 | 634.5 | 601.3 | 611.1 | 439 | 394 | 450.4
1572 | 1386 | 518.9 | 631.3 | 634.3 | 600.9 | 611 | 439.1 | 393.9 | 450.4
1573 | 1387 | 518.9 | 631.4 | 634.4 | 600.5 | 610.7 | 439.1 | 394 | 450.4
1574 | 1388 | 518.7 | 631.3 | 633.8 | 600.1 | 610.8 | 439.2 | 393.6 | 450.3
1575 | 1389 | 518.6 | 631.2 | 633.3 | 599.7 | 610.5 | 439.3 | 393.7 | 450.3
1576 | 1390 | 518.6 | 631 | 633.2 | 599.4 | 610.3 | 439.4 | 393.9 | 450.4
1577 | 1391 | 518.7 | 630.9 | 633.2 | 599 | 609.9 | 439.5 | 394.3 | 450.4
1578 | 1392 | 518.6 | 631 | 632.6 | 598.6 | 610.1 | 439.5 | 393.9 | 450.4
1579 | 1393 | 518.4 | 631.1 | 632.3 | 598.1 | 610.1 | 439.5 | 393.4 | 450.4
1580 | 1394 | 518.4 | 631.2 | 632.5 | 597.6 | 609.6 | 439.5 | 393.8 | 450.4
1581 | 1395 | 518.4 | 631.3 | 632 | 597.1 | 609.6 | 439.5 | 393.5 | 450.4
1582 | 1396 | 518.3 | 631.2 | 631.6 | 596.6 | 609.6 | 439.5 | 394.1 | 450.4
1583 | 1397 | 518.3 | 631.2 | 631.6 | 596.1 | 609.1 | 439.4 | 393.8 | 450.4
1584 | 1398 | 518.4 | 631.2 | 631.6 | 595.6 | 608.6 | 439.4 | 393.4 | 450.4
1585 | 1399 | 518.4 | 631.1 | 631.1 | 595 | 607.8 | 439.4 | 393 | 450.4
1586 | 1400 | 518.3 | 631.1 | 631.1 | 594.3 | 606.8 | 439.4 | 393.1 | 450.4
1587 | 1401 | 518.3 | 631.1 | 631.4 | 593.5 | 606.3 | 439.4 | 393.5 | 450.4
1588 | 1402 | 518.3 | 631 | 631 | 592.7 | 605.7 | 439.5 | 393.4 | 450.4
1589 | 1403 | 518.2 | 630.9 | 630.6 | 592 | 604.9 | 439.4 | 393.3 | 450.4
1590 | 1404 | 518.1 | 630.8 | 630.6 | 591.2 | 604.2 | 439.4 | 393.4 | 450.4
1591 | 1405 | 518.2 | 630.6 | 630.7 | 590.5 | 603.9 | 439.3 | 392.8 | 450.4
1592 | 1406 | 518.2 | 630.6 | 630 | 589.9 | 604 | 439.3 | 392.9 | 450.3
1593 | 1407 | 518.3 | 630.5 | 629.7 | 589.4 | 603.9 | 439.3 | 392.8 | 450.3
1594 | 1408 | 518.4 | 630.6 | 630 | 589 | 603.8 | 439.3 | 392.6 | 450.3
1595 | 1409 | 518.5 | 630.8 | 629.4 | 588.6 | 603.7 | 439.3 | 392.5 | 450.3
1596 | 1410 | 518.6 | 631.1 | 629 | 588.3 | 603.3 | 439.4 | 393.1 | 450.3
1597 | 1411 | 518.9 | 631.3 | 628.9 | 588.1 | 603.2 | 439.4 | 393.8 | 450.3
1598 | 1412 | 519.3 | 631.7 | 628.9 | 587.9 | 603.1 | 439.5 | 393.3 | 450.3
1599 | 1413 | 519.5 | 632 | 628.2 | 587.8 | 602.7 | 439.6 | 393.4 | 450.3
1600 | 1414 | 519.5 | 632.3 | 628 | 587.5 | 602.8 | 439.7 | 393.4 | 450.3
1601 | 1415 | 519.5 | 632.4 | 628.1 | 587.4 | 602.6 | 439.7 | 393.7 | 450.3
1602 | 1416 | 519.6 | 632.5 | 627.5 | 587.2 | 602.5 | 439.8 | 394 | 450.3
1603 | 1417 | 519.8 | 632.6 | 627.1 | 587 | 602.5 | 439.9 | 395.5 | 450.3
1604 | 1418 | 519.9 | 632.6 | 626.9 | 586.7 | 602.2 | 440 | 396.3 | 450.4
1605 | 1419 | 520 | 632.7 | 626.9 | 586.4 | 601.8 | 440.1 | 396.3 | 450.4
1606 | 1420 | 520.2 | 632.8 | 626.2 | 586.1 | 601.5 | 440.2 | 395.7 | 450.3
1607 | 1421 | 520.4 | 632.8 | 626 | 586 | 602.2 | 440.3 | 396.1 | 450.4
1608 | 1422 | 520.6 | 633 | 626.1 | 586.1 | 603.1 | 440.3 | 396.5 | 450.7
1609 | 1423 | 520.8 | 633.3 | 625.8 | 586.3 | 604.1 | 440.5 | 397.5 | 451.2
1610 | 1424 | 521 | 633.8 | 625.5 | 586.3 | 605.1 | 440.5 | 398.2 | 452
1611 | 1425 | 521.2 | 634.2 | 626 | 586.2 | 606.1 | 440.6 | 400 | 453.4
1612 | 1426 | 521.5 | 634.2 | 626.3 | 586.3 | 606.8 | 440.6 | 402.7 | 454.9
1613 | 1427 | 521.9 | 634.1 | 626.5 | 586.5 | 607.5 | 440.6 | 404.3 | 456.6
1614 | 1428 | 522.3 | 633.9 | 626.7 | 586.8 | 608.4 | 440.6 | 405.7 | 458.3
1615 | 1429 | 522.4 | 633.7 | 626.8 | 587.2 | 610.2 | 440.7 | 407.7 | 460
1616 | 1430 | 522.7 | 633.9 | 626.7 | 587.9 | 612.9 | 440.8 | 410.1 | 461.9
1617 | 1431 | 522.9 | 634.2 | 625.9 | 588.9 | 616.1 | 440.8 | 412.7 | 463.8
1618 | 1432 | 523.1 | 634.8 | 626.1 | 589.9 | 618.8 | 440.9 | 415.2 | 465.8
1619 | 1433 | 523.2 | 635.5 | 626.5 | 590.9 | 621.3 | 441 | 418.3 | 468
1620 | 1434 | 522.9 | 636.2 | 626.2 | 591.9 | 623.5 | 441 | 421.2 | 470
1621 | 1435 | 522.8 | 636.7 | 626.4 | 592.8 | 625.6 | 441.1 | 423.7 | 472.1
1622 | 1436 | 523 | 637 | 627 | 593.8 | 627.6 | 441.2 | 425.4 | 474
1623 | 1437 | 523.2 | 637.1 | 626.8 | 594.8 | 629.5 | 441.3 | 428.4 | 475.6
1624 | 1438 | 523.2 | 637.1 | 626.7 | 595.6 | 631.1 | 441.4 | 430.7 | 477
1625 | 1439 | 523.1 | 637 | 627 | 596.5 | 632.6 | 441.5 | 432.2 | 478.5
1626 | 1440 | 523 | 636.9 | 627.3 | 597.3 | 634.1 | 441.6 | 433.8 | 479.9
1627 | 1441 | 522.8 | 636.9 | 627 | 598.1 | 635.3 | 441.8 | 436.3 | 481.2
1628 | 1442 | 522.6 | 637.1 | 627 | 598.9 | 636.6 | 442 | 439.3 | 482.5
1629 | 1443 | 522.3 | 637.3 | 627.5 | 599.7 | 637.6 | 442.1 | 441.3 | 483.9
1630 | 1444 | 522 | 637.7 | 627.5 | 600.5 | 639.1 | 442.3 | 443.5 | 485.3
1631 | 1445 | 521.4 | 638.3 | 627.3 | 601.3 | 640.6 | 442.5 | 446.1 | 486.6
1632 | 1446 | 521.1 | 639.1 | 627.7 | 602.1 | 642 | 442.7 | 448.6 | 488
1633 | 1447 | 520.9 | 640 | 628.1 | 602.9 | 643.1 | 442.9 | 451.5 | 489.5
1634 | 1448 | 520.9 | 640.6 | 628 | 603.6 | 643.8 | 443.3 | 453.8 | 490.8
1635 | 1449 | 520.8 | 641.1 | 628.4 | 604.2 | 644.5 | 444.3 | 456.5 | 492
1636 | 1450 | 520.7 | 641.5 | 629.1 | 604.8 | 645.3 | 446.7 | 459 | 493.5
1637 | 1451 | 520.7 | 641.7 | 629.3 | 605.4 | 646.2 | 449.9 | 461.5 | 495
1638 | 1452 | 520.6 | 641.9 | 629.6 | 606 | 646.8 | 453.9 | 463.2 | 496.4
1639 | 1453 | 520.4 | 642 | 630 | 606.5 | 647.3 | 458.1 | 464.4 | 497.6
1640 | 1454 | 520.2 | 642 | 630.9 | 607.1 | 648 | 462.6 | 465.1 | 498.7
1641 | 1455 | 520.2 | 642.2 | 631.1 | 607.6 | 648.7 | 467 | 466.9 | 499.9
1642 | 1456 | 520 | 642.4 | 631.3 | 608.2 | 649.3 | 471.1 | 468.6 | 500.9
1643 | 1457 | 519.8 | 642.6 | 632.1 | 608.7 | 649.6 | 474.9 | 470.3 | 502.1
1644 | 1458 | 519.7 | 642.9 | 633.2 | 609.2 | 650 | 478.4 | 471 | 503.3
1645 | 1459 | 519.5 | 643.3 | 633.1 | 609.5 | 650 | 481.7 | 472.1 | 504.3
1646 | 1460 | 519.2 | 643.8 | 633.3 | 609.6 | 649.3 | 484.9 | 472.8 | 505.3
1647 | 1461 | 519.2 | 644.4 | 633.6 | 609.6 | 648.7 | 488.1 | 475.1 | 506.3
1648 | 1462 | 519.2 | 645.2 | 633.4 | 609.7 | 648.7 | 491.3 | 477.7 | 507.2
1649 | 1463 | 518.9 | 645.9 | 634.6 | 609.8 | 648.9 | 494.2 | 479.8 | 508.2
1650 | 1464 | 518.7 | 647 | 635.5 | 610 | 649.5 | 497.1 | 483.1 | 509.1
1651 | 1465 | 518.6 | 648 | 635.6 | 610.3 | 649.8 | 500.1 | 483.8 | 510
1652 | 1466 | 518.3 | 649 | 635.5 | 610.5 | 649 | 503.1 | 493.6 | 511
1653 | 1467 | 518.1 | 649.9 | 635.8 | 610.9 | 649 | 506 | 527.2 | 512
1654 | 1468 | 517.9 | 650.6 | 636.4 | 611.4 | 649.8 | 508.8 | 557.7 | 513
1655 | 1469 | 517.7 | 651.4 | 636.4 | 611.9 | 651 | 511.6 | 570.2 | 514
1656 | 1470 | 517.7 | 652.4 | 636.3 | 612.2 | 651.7 | 514.1 | 576.3 | 515.1
1657 | 1471 | 517.6 | 653.2 | 636.5 | 612.2 | 651.6 | 516.7 | 587.1 | 516.3
1658 | 1472 | 517.5 | 653.7 | 637 | 612.2 | 651.8 | 519.5 | 595.5 | 517.4
1659 | 1473 | 517.6 | 654.4 | 636.8 | 612.5 | 652.8 | 522.6 | 602.3 | 518.4
1660 | 1474 | 517.7 | 654.9 | 637.2 | 612.9 | 653 | 525.6 | 610.5 | 519.4
1661 | 1475 | 517.5 | 655.5 | 637.6 | 613.2 | 653.1 | 528.3 | 616.5 | 520.5
1662 | 1476 | 517.5 | 656.3 | 637.6 | 613.6 | 652.8 | 531 | 623.4 | 521.7
1663 | 1477 | 517.6 | 656.9 | 638.8 | 613.7 | 652.7 | 534.4 | 630.7 | 522.9
1664 | 1478 | 517.8 | 657.2 | 639.4 | 613.7 | 652.2 | 538.1 | 636 | 524
1665 | 1479 | 517.7 | 657.8 | 639.3 | 613.7 | 651.6 | 541.3 | 639.5 | 525.3
1666 | 1480 | 517.9 | 658.4 | 639.5 | 613.7 | 651.3 | 544.4 | 643.4 | 526.5
1667 | 1481 | 518.1 | 659.3 | 639.4 | 613.7 | 651.1 | 547 | 648.3 | 527.6
1668 | 1482 | 518.4 | 660.2 | 639.4 | 613.7 | 647.2 | 548.4 | 651.9 | 528.7
1669 | 1483 | 518.7 | 660.8 | 639.1 | 613.6 | 644.7 | 548.7 | 655.1 | 529.7
1670 | 1484 | 518.9 | 661.5 | 639.6 | 613.5 | 642.5 | 549 | 663 | 530.7
1671 | 1485 | 518.9 | 661.8 | 639.8 | 613.6 | 642 | 549.3 | 664.9 | 531.6
1672 | 1486 | 519 | 662.2 | 639.6 | 613.6 | 641.5 | 549.8 | 668.9 | 532.6
1673 | 1487 | 519 | 662.6 | 639.2 | 613.8 | 642 | 550.7 | 671.1 | 533.5
1674 | 1488 | 518.8 | 663.1 | 639.4 | 614 | 641.3 | 551.6 | 672.3 | 534.5
1675 | 1489 | 518.8 | 663.5 | 639.6 | 614.1 | 640.2 | 552.9 | 672.9 | 535.4
1676 | 1490 | 518.8 | 663.8 | 639.3 | 614.2 | 640.2 | 554.3 | 676.4 | 536.3
1677 | 1491 | 518.8 | 664.3 | 639.5 | 614.3 | 639.5 | 555.9 | 674.4 | 537.3
1678 | 1492 | 519 | 664.7 | 639.7 | 614.4 | 639.1 | 557.3 | 675.9 | 538.1
1679 | 1493 | 519.2 | 665.2 | 639.6 | 614.5 | 638.8 | 558.7 | 681.6 | 538.9
1680 | 1494 | 519.5 | 665.6 | 639.5 | 614.6 | 638.9 | 560.2 | 682.9 | 539.5
1681 | 1495 | 519.5 | 665.8 | 639.7 | 614.7 | 639.1 | 561.7 | 686.4 | 540.2
1682 | 1496 | 519.5 | 666.4 | 639.6 | 614.9 | 639.2 | 563.5 | 689.5 | 540.9
1683 | 1497 | 519.5 | 666.8 | 639.1 | 615.2 | 638.9 | 565.3 | 688.8 | 541.6
1684 | 1498 | 519.4 | 667 | 638.8 | 615.4 | 636.7 | 567 | 689.3 | 542.4
1685 | 1499 | 519.3 | 667.3 | 638.9 | 615.4 | 634.5 | 568.6 | 691.3 | 543.1
1686 | 1500 | 519.2 | 667.5 | 639 | 615.4 | 632.1 | 570.1 | 694.5 | 543.8
1687 | 1501 | 519.3 | 667.6 | 639.1 | 615.4 | 631.7 | 571.5 | 695.2 | 544.4
1688 | 1502 | 519.4 | 667.6 | 639.3 | 615.3 | 632.6 | 572.8 | 699.1 | 545
1689 | 1503 | 519.5 | 667.8 | 639.1 | 615.3 | 632.5 | 574.2 | 698.6 | 545.7
1690 | 1504 | 519.6 | 668.2 | 638.6 | 615.2 | 631.8 | 575.9 | 699.4 | 546.4
1691 | 1505 | 519.7 | 668.6 | 638.6 | 615.1 | 631 | 577.3 | 700.6 | 547.2
1692 | 1506 | 519.7 | 668.9 | 639.1 | 614.9 | 629.8 | 578.2 | 700.4 | 547.8
1693 | 1507 | 519.8 | 668.9 | 639 | 614.8 | 629.3 | 579 | 699.5 | 548.4
1694 | 1508 | 520 | 669 | 638.9 | 614.7 | 629.6 | 579.9 | 698.2 | 549.1
1695 | 1509 | 519.8 | 669 | 639.2 | 614.6 | 629.3 | 581.1 | 696.4 | 549.9
1696 | 1510 | 519.6 | 669.1 | 639.2 | 614.6 | 629.6 | 582.6 | 690.9 | 550.7
1697 | 1511 | 519.4 | 669.3 | 639.8 | 614.6 | 630.7 | 584.2 | 690.9 | 551.4
1698 | 1512 | 519.4 | 669.8 | 640.3 | 614.6 | 631.8 | 585.5 | 695.8 | 552.1
1699 | 1513 | 519.2 | 670.2 | 640.9 | 614.5 | 629.3 | 587.2 | 695.8 | 552.6
1700 | 1514 | 519 | 670.5 | 640.8 | 614.5 | 626.7 | 589 | 698.3 | 553.2
1701 | 1515 | 518.7 | 670.8 | 640.6 | 614.4 | 626.5 | 591.3 | 704.1 | 553.7
1702 | 1516 | 518.1 | 670.9 | 640.7 | 614.3 | 626.6 | 593.6 | 712.7 | 554.3
1703 | 1517 | 517.3 | 671.2 | 640.7 | 614.2 | 627.3 | 595.7 | 713.3 | 554.7
1704 | 1518 | 516.5 | 671.6 | 640.6 | 614.1 | 628.8 | 597.2 | 700.2 | 555.1
1705 | 1519 | 515.8 | 672 | 640.9 | 614.2 | 629.2 | 598.6 | 691.5 | 555.5
1706 | 1520 | 515.2 | 672.4 | 640.8 | 614.1 | 629.1 | 600.3 | 683.1 | 555.7
1707 | 1521 | 514.5 | 673 | 640.9 | 614 | 629.4 | 601.9 | 678.1 | 555.8
1708 | 1522 | 513.7 | 673.7 | 640.4 | 614 | 629.8 | 603.4 | 673.7 | 556
1709 | 1523 | 512.8 | 674.3 | 640.5 | 613.9 | 629 | 604.9 | 670 | 556.2
1710 | 1524 | 512 | 674.6 | 640.6 | 613.8 | 628.4 | 606.7 | 667.4 | 556.4
1711 | 1525 | 511.2 | 675.1 | 640.5 | 613.7 | 628.2 | 608.5 | 664.1 | 556.6
1712 | 1526 | 510.3 | 675.7 | 640.1 | 613.5 | 627.7 | 610.3 | 662 | 556.8
1713 | 1527 | 509.3 | 676.4 | 640.2 | 613.3 | 628.6 | 612.5 | 660.6 | 556.9
1714 | 1528 | 508.2 | 677 | 640.3 | 613.2 | 629.6 | 614.2 | 659.4 | 557
1715 | 1529 | 507 | 677.8 | 640.5 | 613.3 | 629.4 | 616.1 | 658.6 | 557
1716 | 1530 | 505.8 | 678.6 | 640.4 | 613.3 | 629.5 | 617.4 | 657.6 | 557.2
1717 | 1531 | 504.7 | 679.2 | 640.4 | 613.3 | 629.8 | 618.8 | 656.3 | 557.4
1718 | 1532 | 503.4 | 679.8 | 640.4 | 613.3 | 629.4 | 620 | 655.7 | 557.5
1719 | 1533 | 502.3 | 680.2 | 640.3 | 613.3 | 628.1 | 621.4 | 654.9 | 557.7
1720 | 1534 | 501.2 | 680.6 | 640.6 | 613.2 | 627.9 | 622.6 | 653.9 | 557.9
1721 | 1535 | 500.3 | 681 | 640.2 | 613.2 | 629.4 | 623.5 | 652.9 | 557.9
1722 | 1536 | 499.6 | 681.4 | 640 | 613.2 | 630.9 | 624.4 | 652.4 | 557.9
1723 | 1537 | 498.8 | 681.8 | 639.8 | 613.2 | 630.4 | 624.9 | 653.2 | 557.9
1724 | 1538 | 497.8 | 682.1 | 639.6 | 613 | 629.7 | 625 | 651.8 | 558
1725 | 1539 | 496.9 | 682.1 | 639.5 | 612.7 | 629.4 | 624.9 | 649.9 | 558
1726 | 1540 | 495.7 | 681.8 | 639.5 | 612.5 | 629 | 625.1 | 648.5 | 558.1
1727 | 1541 | 494.7 | 681.3 | 639.4 | 612.3 | 629.4 | 625.3 | 647.5 | 558.1
1728 | 1542 | 493.6 | 681.2 | 639.2 | 612.3 | 630.1 | 625.2 | 646.6 | 558
1729 | 1543 | 492.5 | 681.3 | 639 | 612.3 | 630 | 625.7 | 646.3 | 557.8
1730 | 1544 | 491.5 | 681.6 | 638.8 | 612.2 | 629.8 | 627 | 644.8 | 557.7
1731 | 1545 | 490.4 | 681.7 | 638.7 | 612.1 | 628.2 | 627.4 | 642.6 | 557.5
1732 | 1546 | 489.5 | 681.7 | 638.2 | 612.1 | 627.1 | 627 | 641.2 | 557.5
1733 | 1547 | 488.6 | 681.5 | 637.9 | 612.1 | 627.7 | 626.6 | 640.8 | 558
1734 | 1548 | 487.5 | 681.3 | 637.7 | 611.9 | 627.9 | 626 | 638.8 | 558.4
1735 | 1549 | 486.4 | 681.3 | 637.3 | 611.6 | 628.5 | 625.3 | 636.9 | 558.5
1736 | 1550 | 485.2 | 681.3 | 637 | 611.3 | 628.8 | 625 | 635.3 | 558.4
1737 | 1551 | 484.1 | 681.3 | 636.7 | 611 | 628.8 | 624.9 | 632.5 | 558.2
1738 | 1552 | 483.2 | 681.2 | 636.2 | 610.5 | 627.9 | 624.7 | 629.9 | 558
1739 | 1553 | 482.3 | 681.3 | 635.4 | 609.9 | 626.2 | 624.3 | 628.3 | 557.7
1740 | 1554 | 481.3 | 681.3 | 635 | 609.1 | 623.8 | 623.9 | 626.7 | 557.5
1741 | 1555 | 480.3 | 681.3 | 634.6 | 608.1 | 621.6 | 623.7 | 625.5 | 557.4
1742 | 1556 | 479.3 | 681.2 | 634.1 | 607 | 619.4 | 623.6 | 623.5 | 557.5
1743 | 1557 | 478.5 | 681.3 | 633.6 | 606 | 618 | 623.5 | 620.5 | 557.4
1744 | 1558 | 477.5 | 681.3 | 632.9 | 605 | 616.8 | 623.6 | 617.6 | 557.4
1745 | 1559 | 476.5 | 681.3 | 632.7 | 604.1 | 615.5 | 623.9 | 615.3 | 557.3
1746 | 1560 | 475.4 | 681.4 | 631.9 | 603.3 | 613 | 623.6 | 612.5 | 557.2
1747 | 1561 | 474.3 | 681.4 | 631.4 | 602.4 | 610 | 623.6 | 609.6 | 557.1
1748 | 1562 | 473.4 | 681.2 | 631.1 | 601.5 | 609.1 | 623.8 | 607.6 | 557.2
1749 | 1563 | 472.6 | 681 | 630.7 | 600.6 | 608 | 623.5 | 605.9 | 557
1750 | 1564 | 471.7 | 680.9 | 630.2 | 599.8 | 607.5 | 622.9 | 603.2 | 556.9
1751 | 1565 | 470.9 | 680.7 | 629.6 | 599 | 606.8 | 622.4 | 600.2 | 556.8
1752 | 1566 | 470.2 | 680.3 | 629.3 | 598.2 | 605.6 | 622 | 598.9 | 556.6
1753 | 1567 | 469.3 | 680 | 628.6 | 597.3 | 604.9 | 622.1 | 597.2 | 556.2
1754 | 1568 | 468.3 | 679.8 | 628 | 596.6 | 604.1 | 622.4 | 595.9 | 556
1755 | 1569 | 467.4 | 679.7 | 627.5 | 595.9 | 603 | 622.4 | 593.5 | 556.1
1756 | 1570 | 466.3 | 679.6 | 627 | 595.2 | 603.5 | 622.4 | 591.7 | 556.1
1757 | 1571 | 465.2 | 679.6 | 626.2 | 594.5 | 602.1 | 622.3 | 589 | 556
1758 | 1572 | 464.2 | 679.5 | 625.7 | 593.9 | 601.9 | 622 | 587.6 | 555.6
1759 | 1573 | 463.4 | 679.1 | 625.3 | 593.3 | 602.1 | 621.4 | 585.7 | 555.2
1760 | 1574 | 462.7 | 678.5 | 624.4 | 592.7 | 602.5 | 621.4 | 584.1 | 554.7
1761 | 1575 | 461.7 | 677.8 | 623.7 | 592 | 602.8 | 621.3 | 582.2 | 554.1
1762 | 1576 | 460.7 | 677 | 623.4 | 591.4 | 602.8 | 621.4 | 580.2 | 553.6
1763 | 1577 | 459.7 | 676.5 | 622.7 | 590.9 | 602.8 | 620.9 | 578.7 | 553
1764 | 1578 | 458.8 | 675.9 | 621.9 | 590.3 | 601.7 | 620.7 | 576.7 | 552.4
1765 | 1579 | 457.9 | 675.7 | 621.1 | 589.6 | 602.1 | 620.3 | 574.6 | 552
1766 | 1580 | 456.8 | 675.4 | 620.4 | 588.8 | 601.6 | 620.1 | 573.1 | 551.6
1767 | 1581 | 455.7 | 675 | 619.5 | 588.1 | 600.6 | 619.8 | 571.3 | 551.4
1768 | 1582 | 454.8 | 674.6 | 619 | 587.4 | 600.7 | 619.4 | 569 | 551.1
1769 | 1583 | 453.9 | 674.3 | 618.4 | 586.6 | 600.3 | 619.1 | 566.9 | 550.5
1770 | 1584 | 453 | 674 | 617.6 | 585.7 | 599.6 | 619 | 565.3 | 549.8
1771 | 1585 | 452 | 673.6 | 616.7 | 584.8 | 599.3 | 619 | 563.3 | 549.2
1772 | 1586 | 451 | 673.2 | 615.9 | 584 | 598.7 | 618.7 | 560.9 | 548.6
1773 | 1587 | 450 | 672.7 | 615.1 | 583.2 | 596.7 | 617.8 | 558.8 | 547.9
1774 | 1588 | 449.2 | 672.5 | 614 | 582.3 | 595.3 | 616.8 | 557 | 547.2
1775 | 1589 | 448.3 | 672.2 | 613.3 | 581.3 | 593.2 | 616 | 554.6 | 546.6
1776 | 1590 | 447.6 | 671.9 | 612.7 | 580.2 | 591.9 | 615.8 | 552.4 | 546.1
1777 | 1591 | 446.7 | 671.4 | 611.8 | 579.1 | 590.4 | 615.7 | 550.2 | 545.8
1778 | 1592 | 446 | 670.7 | 611 | 578 | 588.4 | 615.5 | 548.7 | 545.4
1779 | 1593 | 445.1 | 670.1 | 610.4 | 576.8 | 586.7 | 615.3 | 547.1 | 545
1780 | 1594 | 444.1 | 669.6 | 609.8 | 575.4 | 584.6 | 615.1 | 545 | 544.6
1781 | 1595 | 443.3 | 669.1 | 608.9 | 574.1 | 582.4 | 614.8 | 543.5 | 544.2
1782 | 1596 | 442.6 | 668.7 | 607.8 | 572.9 | 582.1 | 614.5 | 542 | 543.7
1783 | 1597 | 441.6 | 668.3 | 607 | 571.8 | 581.2 | 614.2 | 540.4 | 543.1
1784 | 1598 | 440.6 | 668 | 606.2 | 570.7 | 579.4 | 613.8 | 539 | 542.5
1785 | 1599 | 439.8 | 667.6 | 605.3 | 569.7 | 578.4 | 613.5 | 538.6 | 542
1786 | 1600 | 438.9 | 667 | 604.7 | 568.6 | 578.5 | 613.2 | 537.1 | 541.5
1787 | 1601 | 438.1 | 666.6 | 603.9 | 567.5 | 577.1 | 612.8 | 535.5 | 541
1788 | 1602 | 437.2 | 666.2 | 602.9 | 566.5 | 576.4 | 612.2 | 533.1 | 540.4
1789 | 1603 | 436.3 | 665.7 | 602.2 | 565.4 | 574.7 | 611.8 | 531.8 | 539.9
1790 | 1604 | 435.3 | 665 | 601.5 | 564.3 | 572.6 | 611.4 | 531.5 | 539.3
1791 | 1605 | 434.4 | 664.3 | 600.6 | 563.2 | 570.8 | 611 | 531.6 | 538.6
1792 | 1606 | 433.5 | 663.7 | 599.6 | 561.9 | 569.6 | 610.3 | 529.5 | 537.9
1793 | 1607 | 432.7 | 663 | 599 | 560.7 | 569.8 | 609.9 | 528.5 | 537.2
1794 | 1608 | 432.1 | 662.3 | 598.3 | 559.6 | 569.9 | 609.5 | 527.8 | 536.5
1795 | 1609 | 431.3 | 661.7 | 597.3 | 558.5 | 569.7 | 608.6 | 525.7 | 535.9
1796 | 1610 | 430.5 | 661.2 | 596.4 | 557.5 | 567.9 | 608.1 | 524.2 | 535.3
1797 | 1611 | 429.5 | 660.6 | 595.7 | 556.5 | 565.7 | 607.8 | 523.4 | 534.7
1798 | 1612 | 428.7 | 660 | 594.7 | 555.4 | 565 | 607.4 | 522.7 | 533.9
1799 | 1613 | 428 | 659.3 | 593.8 | 554.3 | 563.9 | 607.1 | 521.5 | 533.2
1800 | 1614 | 427.2 | 658.5 | 593 | 553.3 | 563.8 | 607 | 520.9 | 532.6
1801 | 1615 | 426.5 | 657.7 | 592.2 | 552.4 | 564 | 606.6 | 520.3 | 531.8
1802 | 1616 | 425.6 | 657 | 591.1 | 551.6 | 564.2 | 606.3 | 519.1 | 530.9
1803 | 1617 | 424.7 | 656.2 | 590.2 | 550.8 | 564.2 | 605.5 | 518.5 | 530
1804 | 1618 | 423.7 | 655.6 | 589.4 | 550.1 | 563.9 | 605.1 | 518.1 | 529
1805 | 1619 | 422.8 | 655 | 588.3 | 549.4 | 563.5 | 604.9 | 516.9 | 528.2
1806 | 1620 | 422.1 | 654.5 | 587.4 | 548.5 | 563.1 | 604.4 | 515.5 | 527.3
1807 | 1621 | 421.3 | 653.9 | 586.7 | 547.6 | 562.9 | 603.6 | 514.5 | 526.5
1808 | 1622 | 420.6 | 653.1 | 585.9 | 546.7 | 562.5 | 603.3 | 513.2 | 525.6
1809 | 1623 | 419.9 | 652.3 | 584.9 | 545.9 | 562 | 603.1 | 512.6 | 524.7
1810 | 1624 | 419 | 651.4 | 584 | 545 | 561.1 | 602.7 | 511.8 | 523.8
1811 | 1625 | 418.2 | 650.6 | 583.2 | 544.1 | 558.8 | 602.2 | 510.7 | 522.9
1812 | 1626 | 417.3 | 649.9 | 582.3 | 543.1 | 558.2 | 601.8 | 509.2 | 522
1813 | 1627 | 416.3 | 649.4 | 580.9 | 542 | 556.2 | 601.3 | 507.6 | 521
1814 | 1628 | 415.5 | 648.7 | 580 | 540.8 | 554.6 | 600.7 | 508 | 520.2
1815 | 1629 | 414.8 | 648 | 579.3 | 539.5 | 553.1 | 600.1 | 507.9 | 519.6
1816 | 1630 | 414 | 647 | 578.3 | 538.2 | 551.5 | 599.8 | 506.2 | 518.9
1817 | 1631 | 413.2 | 646.1 | 577.5 | 537 | 550.8 | 599.3 | 504.8 | 518.1
1818 | 1632 | 412.3 | 645.2 | 576.5 | 535.9 | 549.2 | 598.8 | 503.3 | 517.5
1819 | 1633 | 411.3 | 644.4 | 575.6 | 534.8 | 549.5 | 598.1 | 503.1 | 516.8
1820 | 1634 | 410.5 | 643.5 | 574.6 | 533.8 | 549.8 | 597.6 | 501.7 | 515.9
1821 | 1635 | 409.7 | 642.7 | 573.7 | 532.8 | 550.4 | 597.3 | 500.9 | 515
1822 | 1636 | 408.8 | 641.8 | 572.9 | 531.9 | 550.1 | 597.1 | 500.6 | 514.2
1823 | 1637 | 408 | 641.1 | 571.7 | 531 | 549.2 | 596.8 | 500.4 | 513.2
1824 | 1638 | 407.2 | 640.2 | 570.7 | 530.2 | 549.1 | 596.3 | 500 | 512.3
1825 | 1639 | 406.5 | 639.2 | 570 | 529.3 | 548.1 | 595.9 | 499.5 | 511.6
1826 | 1640 | 406 | 638.2 | 569 | 528.5 | 546.5 | 595.1 | 498.9 | 511
1827 | 1641 | 405.3 | 637.1 | 567.9 | 527.7 | 546.5 | 594.9 | 498.8 | 510.7
1828 | 1642 | 404.5 | 635.9 | 567.2 | 526.8 | 546.3 | 594.5 | 498.2 | 510.2
1829 | 1643 | 403.7 | 634.8 | 566.4 | 526 | 546.1 | 594 | 497.5 | 509.6
1830 | 1644 | 402.9 | 633.6 | 565.2 | 525.2 | 546.1 | 593.6 | 497.4 | 508.8
1831 | 1645 | 402 | 632.6 | 564.2 | 524.3 | 546.1 | 593.3 | 496.5 | 507.9
1832 | 1646 | 401.3 | 631.5 | 563.5 | 523.3 | 546 | 592.7 | 496.1 | 507
1833 | 1647 | 400.6 | 630.3 | 562.3 | 522.3 | 545.8 | 591.9 | 495.7 | 506.3
1834 | 1648 | 399.8 | 629.1 | 561.3 | 521.3 | 545.7 | 591.1 | 494.9 | 505.5
1835 | 1649 | 399.3 | 627.9 | 560.2 | 520.2 | 545.1 | 590.1 | 494.8 | 504.7
1836 | 1650 | 398.6 | 626.8 | 559.4 | 519.1 | 544.2 | 589.4 | 493.7 | 503.9
1837 | 1651 | 397.8 | 625.8 | 558.1 | 518.1 | 543.3 | 588.8 | 492.3 | 502.9
1838 | 1652 | 397 | 624.6 | 557.1 | 517.1 | 542.4 | 588.2 | 491.4 | 502
1839 | 1653 | 396.2 | 623.5 | 556.3 | 516.1 | 541.2 | 587.5 | 490.1 | 501.2
1840 | 1654 | 395.4 | 622.3 | 555.1 | 515.1 | 540.4 | 586.7 | 489 | 500.3
1841 | 1655 | 394.7 | 621.1 | 554 | 514.1 | 539.6 | 585.8 | 488.1 | 499.5
1842 | 1656 | 394 | 620 | 552.9 | 513 | 538.7 | 585 | 487.3 | 498.7
1843 | 1657 | 393.3 | 618.8 | 552.2 | 512 | 537.7 | 584.2 | 486.7 | 497.8
1844 | 1658 | 392.5 | 617.6 | 551.1 | 511 | 536.3 | 583.6 | 485.5 | 496.9
1845 | 1659 | 391.7 | 616.3 | 550.1 | 509.9 | 534.5 | 582.8 | 484.5 | 496
1846 | 1660 | 391.1 | 614.9 | 549.4 | 508.8 | 533.8 | 581.8 | 483.9 | 495.2
1847 | 1661 | 390.2 | 613.5 | 548.4 | 507.7 | 532.5 | 580.7 | 483.2 | 494.3
1848 | 1662 | 389.3 | 612.2 | 547.1 | 506.6 | 531.6 | 580.1 | 482.5 | 493.5
1849 | 1663 | 388.5 | 610.7 | 546.3 | 505.5 | 530.8 | 579.5 | 481.7 | 492.8
1850 | 1664 | 387.7 | 609.2 | 545.4 | 504.5 | 530.3 | 578.9 | 481.1 | 492.1
1851 | 1665 | 387 | 607.6 | 544.2 | 503.5 | 529.8 | 578.4 | 480.3 | 491.3
1852 | 1666 | 386.3 | 606.1 | 543.1 | 502.5 | 528.6 | 578.3 | 480.1 | 490.7
1853 | 1667 | 385.7 | 604.6 | 542.3 | 501.5 | 527.7 | 577.6 | 480.2 | 490.2
1854 | 1668 | 384.9 | 603.1 | 541.2 | 500.6 | 527 | 577.1 | 480.5 | 489.6
1855 | 1669 | 384.1 | 601.5 | 540.2 | 499.7 | 525.9 | 576.7 | 480 | 489
1856 | 1670 | 383.4 | 600 | 539.3 | 498.7 | 525.2 | 576.2 | 479.8 | 488.4
1857 | 1671 | 382.9 | 598.4 | 538.4 | 497.7 | 524.4 | 575.4 | 478.6 | 487.6
1858 | 1672 | 382.3 | 596.7 | 537.3 | 496.9 | 523.2 | 574.9 | 477.2 | 486.8
1859 | 1673 | 381.6 | 595.1 | 536.3 | 496.1 | 522.3 | 574.2 | 475.8 | 486
1860 | 1674 | 380.8 | 593.5 | 535.3 | 495.3 | 521.1 | 573.6 | 474.8 | 485.1
1861 | 1675 | 379.9 | 591.9 | 534.2 | 494.5 | 520 | 572.9 | 473.9 | 484.2
1862 | 1676 | 379 | 590.4 | 533.1 | 493.7 | 518.8 | 572.2 | 473.2 | 483.3
1863 | 1677 | 378.5 | 588.9 | 532.1 | 492.7 | 516.8 | 571.5 | 472.8 | 482.4
1864 | 1678 | 377.9 | 587.4 | 531.2 | 491.6 | 515.7 | 570.6 | 471.1 | 481.5
1865 | 1679 | 377.2 | 585.8 | 529.9 | 490.5 | 514.4 | 569.7 | 470.1 | 480.6
1866 | 1680 | 376.6 | 584.3 | 528.8 | 489.4 | 513.9 | 568.8 | 469.4 | 479.7
1867 | 1681 | 375.9 | 582.8 | 527.9 | 488.4 | 512.5 | 567.9 | 468.6 | 478.8
1868 | 1682 | 375.2 | 581.2 | 526.9 | 487.5 | 511.3 | 567 | 468.3 | 478
1869 | 1683 | 374.6 | 579.7 | 525.8 | 486.6 | 510 | 566.1 | 467.2 | 477.2
1870 | 1684 | 374.1 | 578.2 | 524.8 | 485.7 | 508.9 | 565.3 | 465.6 | 476.4
1871 | 1685 | 373.4 | 576.6 | 524.1 | 484.9 | 507.8 | 564.4 | 465.2 | 475.6
1872 | 1686 | 372.7 | 574.9 | 523 | 484 | 506.1 | 563.3 | 464.5 | 474.7
1873 | 1687 | 372.1 | 573.2 | 521.9 | 483 | 502.9 | 562.4 | 463.3 | 473.8
1874 | 1688 | 371.5 | 571.4 | 521 | 481.9 | 501.1 | 561.5 | 462.6 | 472.9
1875 | 1689 | 370.8 | 569.7 | 519.9 | 480.9 | 499 | 560.6 | 461.4 | 472
1876 | 1690 | 370.1 | 567.9 | 518.8 | 479.8 | 497.3 | 559.5 | 460.3 | 471.1
1877 | 1691 | 369.5 | 566.1 | 517.9 | 478.6 | 495.4 | 558.3 | 459.8 | 470.2
1878 | 1692 | 368.9 | 564.3 | 516.9 | 477.5 | 492.6 | 557.3 | 458.8 | 469.4
1879 | 1693 | 368.4 | 562.5 | 515.7 | 476.3 | 491 | 556.2 | 459 | 468.5
1880 | 1694 | 367.7 | 560.8 | 514.5 | 475.3 | 490.4 | 555.2 | 458.1 | 467.6
1881 | 1695 | 367 | 559 | 513.5 | 474.3 | 489.2 | 554.2 | 457.6 | 466.8
1882 | 1696 | 366.4 | 557.1 | 512.3 | 473.4 | 489.3 | 553.4 | 457 | 465.9
1883 | 1697 | 365.8 | 555.1 | 511.1 | 472.4 | 489.1 | 552.5 | 456.5 | 465.1
1884 | 1698 | 365.2 | 553.1 | 510 | 471.5 | 489.3 | 551.5 | 455.9 | 464.3
1885 | 1699 | 364.5 | 550.9 | 509.1 | 470.5 | 489.1 | 550.5 | 455.2 | 463.5
1886 | 1700 | 363.8 | 548.8 | 507.8 | 469.5 | 488.6 | 549.6 | 454.5 | 462.7
1887 | 1701 | 363.1 | 546.8 | 506.7 | 468.6 | 488.5 | 548.7 | 453.4 | 461.9
1888 | 1702 | 362.3 | 544.9 | 505.7 | 467.6 | 487.8 | 547.7 | 452.1 | 461.1
1889 | 1703 | 361.6 | 542.9 | 504.6 | 466.7 | 487.1 | 546.8 | 450.9 | 460.2
1890 | 1704 | 360.8 | 541 | 503.4 | 465.9 | 487.2 | 545.7 | 449.9 | 459.4
1891 | 1705 | 360.2 | 539.1 | 502.3 | 465.1 | 486.9 | 544.6 | 448.8 | 458.5
1892 | 1706 | 359.5 | 537.3 | 501.4 | 464.3 | 486.7 | 543.6 | 447.9 | 457.7
1893 | 1707 | 358.9 | 535.4 | 500.3 | 463.5 | 486.5 | 542.6 | 447.2 | 456.8
1894 | 1708 | 358.1 | 533.3 | 499.2 | 462.7 | 485.9 | 541.3 | 446.1 | 456
1895 | 1709 | 357.5 | 531.1 | 498 | 461.9 | 483.3 | 539.9 | 445.4 | 455.2
1896 | 1710 | 356.9 | 528.8 | 496.8 | 461 | 481.5 | 538.5 | 445.1 | 454.3
1897 | 1711 | 356.4 | 526.4 | 495.8 | 460.1 | 480.8 | 536.8 | 445.3 | 453.5
1898 | 1712 | 355.7 | 523.9 | 494.8 | 459.2 | 480.1 | 535.2 | 444.7 | 452.7
1899 | 1713 | 355 | 521.6 | 493.8 | 458.3 | 479.4 | 533.6 | 443.4 | 451.9
1900 | 1714 | 354.3 | 519.5 | 492.7 | 457.4 | 478.6 | 532.2 | 442.3 | 451.1
1901 | 1715 | 353.7 | 517.5 | 491.6 | 456.6 | 477.4 | 530.8 | 442.6 | 450.3
1902 | 1716 | 353.1 | 515.7 | 490.5 | 455.7 | 476.7 | 529.4 | 442.5 | 449.5
1903 | 1717 | 352.5 | 514 | 489.6 | 454.8 | 475.9 | 528 | 441.9 | 448.7
1904 | 1718 | 351.9 | 512.3 | 488.4 | 453.8 | 475.1 | 526.7 | 442.6 | 447.8
1905 | 1719 | 351.4 | 510.7 | 487.4 | 452.9 | 474.4 | 525.4 | 441.4 | 447
1906 | 1720 | 350.8 | 509.1 | 486.3 | 452 | 474.3 | 524.2 | 440.7 | 446.2
1907 | 1721 | 350.1 | 507.6 | 485.3 | 451.2 | 472.6 | 523 | 440.6 | 445.4
1908 | 1722 | 349.6 | 506.1 | 484.2 | 450.1 | 471.4 | 521.9 | 439.5 | 444.6
1909 | 1723 | 349.1 | 504.6 | 483.2 | 449.1 | 469.9 | 520.8 | 438.3 | 443.8
1910 | 1724 | 348.5 | 503.1 | 482.2 | 448 | 467.8 | 519.6 | 437.3 | 443
1911 | 1725 | 347.9 | 501.7 | 481.2 | 446.9 | 466.7 | 518.5 | 436.2 | 442.2
1912 | 1726 | 347.2 | 500.2 | 480.2 | 445.8 | 465.5 | 517.4 | 434.9 | 441.4
1913 | 1727 | 346.8 | 498.9 | 479.3 | 444.7 | 464.8 | 516.3 | 433.6 | 440.6
1914 | 1728 | 346.2 | 497.4 | 478.4 | 443.7 | 464.5 | 515.3 | 432.6 | 439.8
1915 | 1729 | 345.5 | 496 | 477.5 | 442.8 | 464.2 | 514.3 | 431.5 | 439
1916 | 1730 | 344.9 | 494.6 | 476.6 | 441.9 | 463.7 | 513.3 | 430.8 | 438.2
1917 | 1731 | 344.2 | 493.2 | 475.6 | 441.1 | 462.5 | 512.4 | 430.5 | 437.4
1918 | 1732 | 343.5 | 491.9 | 474.5 | 440.2 | 461.9 | 511.5 | 429.8 | 436.6
1919 | 1733 | 342.9 | 490.5 | 473.7 | 439.3 | 460.8 | 510.5 | 428.8 | 435.8
1920 | 1734 | 342.4 | 489.2 | 472.8 | 438.5 | 459.2 | 509.5 | 427.6 | 435.1
1921 | 1735 | 341.8 | 487.9 | 471.7 | 437.5 | 458.1 | 508.6 | 427.6 | 434.3
1922 | 1736 | 341.2 | 486.6 | 470.7 | 436.6 | 458.1 | 507.7 | 427 | 433.5
1923 | 1737 | 340.6 | 485.3 | 469.7 | 435.7 | 457.1 | 506.8 | 425.9 | 432.8
1924 | 1738 | 339.8 | 484.1 | 468.7 | 434.8 | 455.3 | 506 | 424.5 | 432
1925 | 1739 | 339.1 | 482.8 | 467.8 | 433.8 | 454.4 | 505.2 | 423.2 | 431.2
1926 | 1740 | 338.5 | 481.5 | 466.9 | 432.9 | 453.5 | 504.5 | 422.2 | 430.4
1927 | 1741 | 338 | 480.3 | 466 | 432 | 453 | 503.6 | 421 | 429.6
1928 | 1742 | 337.4 | 479.1 | 465.1 | 431.1 | 452.5 | 502.7 | 419.9 | 428.8
1929 | 1743 | 336.8 | 477.9 | 464.2 | 430.3 | 451.8 | 501.9 | 418.9 | 428
1930 | 1744 | 336.2 | 476.7 | 463.2 | 429.5 | 450.7 | 501.1 | 418.1 | 427.1
1931 | 1745 | 335.8 | 475.5 | 462.3 | 428.7 | 449.6 | 500.2 | 416.9 | 426.3
1932 | 1746 | 335.3 | 474.3 | 461.2 | 427.8 | 447.9 | 499.5 | 415.9 | 425.5
1933 | 1747 | 334.6 | 473.2 | 460.2 | 426.8 | 446 | 498.7 | 415.7 | 424.7
1934 | 1748 | 333.9 | 472 | 459.4 | 425.8 | 444.9 | 497.8 | 414.5 | 424
1935 | 1749 | 333.2 | 470.8 | 458.3 | 424.8 | 444.3 | 497 | 414.3 | 423.2
1936 | 1750 | 332.6 | 469.6 | 457.2 | 423.9 | 443.8 | 496.2 | 413.5 | 422.4
1937 | 1751 | 332.2 | 468.5 | 456.2 | 423 | 442.4 | 495.4 | 412.5 | 421.7
1938 | 1752 | 331.6 | 467.3 | 455.2 | 422 | 440.9 | 494.5 | 412.4 | 420.9
1939 | 1753 | 331.2 | 466.1 | 454.1 | 421 | 439 | 493.6 | 411.1 | 420.1
1940 | 1754 | 330.8 | 465 | 453 | 420 | 437.7 | 492.7 | 409.9 | 419.3
1941 | 1755 | 330.4 | 463.8 | 452 | 419 | 436.9 | 491.8 | 409.1 | 418.6
1942 | 1756 | 329.9 | 462.7 | 451 | 418.1 | 436.4 | 490.9 | 407.9 | 417.8
1943 | 1757 | 329.2 | 461.5 | 450 | 417.2 | 435.1 | 490 | 407.1 | 417
1944 | 1758 | 328.6 | 460.4 | 449.1 | 416.3 | 433.9 | 489 | 405.3 | 416.2
1945 | 1759 | 328 | 459.3 | 448.1 | 415.4 | 432.9 | 488.1 | 404.8 | 415.4
1946 | 1760 | 327.5 | 458.1 | 447.1 | 414.5 | 431.7 | 487.2 | 403.8 | 414.6
1947 | 1761 | 327 | 457 | 446.1 | 413.6 | 430.3 | 486.2 | 403.6 | 413.8
1948 | 1762 | 326.3 | 455.9 | 445 | 412.7 | 428.6 | 485.4 | 403.3 | 413
1949 | 1763 | 325.8 | 454.8 | 444 | 411.8 | 428.1 | 484.6 | 401.9 | 412.1
1950 | 1764 | 325.2 | 453.6 | 443 | 411 | 427.4 | 483.8 | 401.2 | 411.4
1951 | 1765 | 324.6 | 452.5 | 441.5 | 410.2 | 426.7 | 482.9 | 399.7 | 410.6
1952 | 1766 | 324 | 451.4 | 439.6 | 409.4 | 425.6 | 481.9 | 398.1 | 409.8
1953 | 1767 | 323.4 | 450.3 | 438 | 408.6 | 425.2 | 481.1 | 397 | 409
1954 | 1768 | 323 | 449.3 | 436.6 | 407.9 | 425 | 480.1 | 396.5 | 408.2
1955 | 1769 | 322.4 | 448.2 | 435.2 | 407.2 | 424.1 | 479.1 | 395.7 | 407.4
1956 | 1770 | 321.7 | 447.2 | 434 | 406.5 | 423.4 | 478.2 | 394.7 | 406.5
1957 | 1771 | 321.1 | 446.2 | 432.9 | 405.8 | 422.8 | 477.2 | 394.5 | 405.7
1958 | 1772 | 320.7 | 445.1 | 431.8 | 405.1 | 421.7 | 476.3 | 393.6 | 404.9
1959 | 1773 | 320.3 | 444.1 | 430.8 | 404.3 | 420.8 | 475.4 | 393.5 | 404.2
1960 | 1774 | 319.8 | 443.1 | 429.8 | 403.6 | 419.2 | 474.5 | 391.8 | 403.4
1961 | 1775 | 319.3 | 442 | 428.8 | 402.8 | 417.4 | 473.6 | 390.9 | 402.6
1962 | 1776 | 318.8 | 441 | 427.8 | 401.9 | 416.5 | 472.7 | 389.6 | 401.8
1963 | 1777 | 318.3 | 440 | 426.9 | 401.1 | 415.3 | 471.9 | 389.5 | 401
1964 | 1778 | 317.8 | 438.9 | 426 | 400.2 | 414.7 | 471.1 | 388.8 | 400.3
1965 | 1779 | 317.3 | 437.9 | 425 | 399.4 | 414 | 470.3 | 388.3 | 399.6
1966 | 1780 | 316.8 | 436.8 | 424.1 | 398.5 | 413.3 | 469.4 | 387.8 | 398.8
1967 | 1781 | 316.3 | 435.8 | 423.3 | 397.7 | 412.5 | 468.5 | 386.2 | 398
1968 | 1782 | 315.8 | 434.7 | 422.4 | 396.9 | 411.9 | 467.5 | 386.3 | 397.3
1969 | 1783 | 315.3 | 433.7 | 421.5 | 396.2 | 411.4 | 466.6 | 386 | 396.5
1970 | 1784 | 314.8 | 432.7 | 420.7 | 395.5 | 410.7 | 465.8 | 386.1 | 395.7
1971 | 1785 | 314.2 | 431.7 | 419.8 | 394.9 | 409.9 | 464.9 | 386 | 394.9
1972 | 1786 | 313.6 | 430.7 | 418.9 | 394.2 | 408.9 | 464.1 | 386.4 | 394.2
1973 | 1787 | 313.1 | 429.7 | 418.1 | 393.6 | 408 | 463.2 | 385.3 | 393.4
1974 | 1788 | 312.6 | 428.7 | 417.3 | 392.9 | 407 | 462.4 | 384.1 | 392.6
1975 | 1789 | 312 | 427.7 | 416.6 | 392.2 | 407.3 | 461.6 | 383 | 391.9
1976 | 1790 | 311.4 | 426.7 | 415.9 | 391.5 | 407.8 | 460.8 | 382.1 | 391.2
1977 | 1791 | 311 | 425.8 | 415.1 | 390.9 | 407.8 | 460.1 | 381 | 390.5
1978 | 1792 | 310.5 | 424.8 | 414.3 | 390.2 | 407.5 | 459.3 | 379.7 | 389.8
1979 | 1793 | 310 | 423.8 | 413.6 | 389.5 | 406.9 | 458.4 | 378.7 | 389
1980 | 1794 | 309.6 | 422.8 | 412.8 | 388.9 | 406.1 | 457.6 | 378 | 388.2
1981 | 1795 | 309.1 | 421.8 | 412 | 388.2 | 404.6 | 456.6 | 377.7 | 387.4
1982 | 1796 | 308.5 | 420.8 | 411.3 | 387.4 | 403.8 | 455.7 | 378.1 | 386.6
1983 | 1797 | 308 | 419.8 | 410.5 | 386.7 | 402.9 | 454.7 | 377.5 | 385.9
1984 | 1798 | 307.4 | 418.8 | 409.5 | 385.9 | 401.4 | 453.7 | 375.7 | 385.2
1985 | 1799 | 307 | 417.8 | 408.7 | 385.1 | 399.9 | 452.8 | 374.1 | 384.4
1986 | 1800 | 306.5 | 416.8 | 407.9 | 384.2 | 399.2 | 451.9 | 373.2 | 383.7
1987 | 1801 | 305.9 | 415.8 | 407.3 | 383.4 | 398.8 | 451.1 | 372 | 383
1988 | 1802 | 305.5 | 414.7 | 406.6 | 382.5 | 397.9 | 450.1 | 371.1 | 382.2
1989 | 1803 | 304.9 | 413.7 | 405.8 | 381.6 | 397.3 | 449.1 | 369.8 | 381.5
1990 | 1804 | 304.5 | 412.6 | 405 | 380.8 | 396.3 | 448.1 | 368.6 | 380.7
1991 | 1805 | 304.1 | 411.6 | 404.3 | 380 | 395.4 | 447.1 | 367.6 | 379.9
1992 | 1806 | 303.6 | 410.5 | 403.6 | 379.2 | 394.2 | 446.1 | 367.7 | 379.2
1993 | 1807 | 303 | 409.5 | 403 | 378.5 | 392.9 | 445.1 | 367.8 | 378.4
1994 | 1808 | 302.5 | 408.5 | 402.3 | 377.9 | 391.6 | 444.2 | 367.4 | 377.7
1995 | 1809 | 301.9 | 407.4 | 401.6 | 377.2 | 390.7 | 443.3 | 367.8 | 376.9
1996 | 1810 | 301.4 | 406.4 | 400.8 | 376.6 | 390 | 442.4 | 368.3 | 376.2
1997 | 1811 | 301 | 405.4 | 400.1 | 375.9 | 388.7 | 441.6 | 368.3 | 375.4
1998 | 1812 | 300.6 | 404.4 | 399.4 | 375.2 | 387.4 | 440.9 | 367.8 | 374.7
1999 | 1813 | 300 | 403.4 | 398.7 | 374.6 | 386.9 | 440.2 | 367.1 | 374
2000 | 1814 | 299.7 | 402.3 | 398 | 373.9 | 386.8 | 439.5 | 365.8 | 373.3
2001 | 1815 | 299.2 | 401.3 | 397.2 | 373.3 | 386.5 | 438.7 | 366.2 | 372.5
2002 | 1816 | 298.8 | 400.4 | 396.5 | 372.8 | 386.7 | 437.9 | 366.2 | 371.7
2003 | 1817 | 298.3 | 399.4 | 395.8 | 372.2 | 386 | 437.2 | 366.4 | 371
2004 | 1818 | 297.8 | 398.4 | 395 | 371.6 | 386.3 | 436.5 | 366.3 | 370.3
2005 | 1819 | 297.3 | 397.5 | 394.3 | 371 | 386.4 | 435.8 | 365.9 | 369.5
2006 | 1820 | 296.9 | 396.6 | 393.6 | 370.5 | 386.5 | 435 | 365.7 | 368.8
2007 | 1821 | 296.5 | 395.7 | 392.9 | 369.9 | 386.4 | 433.9 | 365.5 | 368.1
2008 | 1822 | 296 | 394.8 | 392.1 | 369.3 | 385.5 | 432.8 | 364.5 | 367.4
2009 | 1823 | 295.4 | 393.9 | 391.4 | 368.7 | 384.1 | 431.7 | 363.2 | 366.7
2010 | 1824 | 294.7 | 393 | 390.6 | 368 | 382.3 | 430.7 | 361.5 | 366
2011 | 1825 | 294.2 | 392.2 | 389.8 | 367.4 | 381.1 | 429.7 | 360.4 | 365.3
2012 | 1826 | 293.7 | 391.3 | 389.1 | 366.8 | 380 | 428.7 | 360.2 | 364.7
2013 | 1827 | 293.2 | 390.5 | 388.3 | 366.2 | 379.3 | 427.7 | 360.2 | 364
2014 | 1828 | 292.7 | 389.7 | 387.6 | 365.7 | 379.5 | 426.7 | 359.6 | 363.4
2015 | 1829 | 292.2 | 388.9 | 386.9 | 365.1 | 379.6 | 425.6 | 359.3 | 362.7
2016 | 1830 | 291.8 | 388.1 | 386.2 | 364.6 | 379.8 | 424.7 | 359.3 | 362
2017 | 1831 | 291.2 | 387.3 | 385.5 | 364.1 | 379.8 | 423.7 | 359.3 | 361.4
2018 | 1832 | 290.7 | 386.5 | 384.9 | 363.6 | 379.6 | 422.8 | 359.1 | 360.7
2019 | 1833 | 290.3 | 385.8 | 384.2 | 363.1 | 379.3 | 421.9 | 358.7 | 360
2020 | 1834 | 289.8 | 385 | 383.5 | 362.6 | 379.1 | 421 | 358.9 | 359.3
2021 | 1835 | 289.4 | 384.2 | 382.9 | 362 | 378.6 | 420 | 358.5 | 358.7
2022 | 1836 | 288.9 | 383.5 | 382.2 | 361.5 | 378.2 | 419 | 357.7 | 358
2023 | 1837 | 288.5 | 382.8 | 381.5 | 360.9 | 377.8 | 418 | 357.2 | 357.3
2024 | 1838 | 288.2 | 382 | 380.8 | 360.3 | 377.5 | 417.1 | 357 | 356.6
2025 | 1839 | 288 | 381.3 | 380.1 | 359.8 | 376.9 | 416.2 | 356 | 355.9
2026 | 1840 | 287.6 | 380.6 | 379.4 | 359.2 | 376.4 | 415.3 | 355.2 | 355.2
2027 | 1841 | 287.1 | 379.8 | 378.7 | 358.7 | 376 | 414.5 | 354.5 | 354.5
2028 | 1842 | 286.6 | 379.1 | 378.1 | 358.1 | 375.5 | 413.6 | 353.5 | 353.8
2029 | 1843 | 286.2 | 378.4 | 377.4 | 357.5 | 375.1 | 412.8 | 352.5 | 353.1
2030 | 1844 | 285.8 | 377.7 | 376.7 | 356.8 | 374.6 | 411.8 | 351.6 | 352.5
2031 | 1845 | 285.4 | 377 | 376 | 356 | 374 | 410.7 | 350.6 | 351.8
2032 | 1846 | 285 | 376.2 | 375.3 | 355.3 | 373.3 | 409.7 | 350.3 | 351.1
2033 | 1847 | 284.6 | 375.5 | 374.6 | 354.6 | 372.9 | 408.5 | 349.4 | 350.3
2034 | 1848 | 284.1 | 374.8 | 374 | 353.9 | 372.2 | 407.3 | 348.9 | 349.6
2035 | 1849 | 283.5 | 374.1 | 373.3 | 353.3 | 371.5 | 406.1 | 347.9 | 348.9
2036 | 1850 | 283 | 373.5 | 372.7 | 352.7 | 370.9 | 405 | 347.7 | 348.1
2037 | 1851 | 282.6 | 372.8 | 372 | 352.2 | 370.4 | 404 | 347 | 347.4
2038 | 1852 | 282.3 | 372.1 | 371.4 | 351.7 | 369.7 | 402.9 | 346.3 | 346.7
2039 | 1853 | 281.9 | 371.4 | 370.8 | 351.2 | 368.9 | 401.9 | 345.7 | 346
2040 | 1854 | 281.4 | 370.7 | 370.1 | 350.8 | 368.5 | 400.9 | 344.9 | 345.3
2041 | 1855 | 281 | 370 | 369.5 | 350.4 | 367.8 | 399.8 | 344.3 | 344.6
2042 | 1856 | 280.5 | 369.4 | 368.9 | 350 | 366.9 | 398.8 | 343.5 | 343.9
2043 | 1857 | 280.1 | 368.7 | 368.3 | 349.6 | 366.4 | 397.7 | 343.7 | 343.2
2044 | 1858 | 279.7 | 368 | 367.6 | 349.3 | 365.4 | 396.6 | 343.7 | 342.5
2045 | 1859 | 279.3 | 367.3 | 367 | 348.8 | 364.5 | 395.4 | 343.6 | 341.8
2046 | 1860 | 279 | 366.6 | 366.3 | 348.3 | 363.7 | 394.3 | 343.4 | 341.1
2047 | 1861 | 278.6 | 365.8 | 365.7 | 347.9 | 362.7 | 393.2 | 343.2 | 340.3
2048 | 1862 | 278.2 | 365.1 | 365 | 347.4 | 361.7 | 392 | 342.5 | 339.6
2049 | 1863 | 277.7 | 364.4 | 364.4 | 346.9 | 361.1 | 390.9 | 341.9 | 338.9
2050 | 1864 | 277.3 | 363.7 | 363.7 | 346.4 | 360.5 | 389.7 | 340.8 | 338.2
2051 | 1865 | 276.8 | 362.9 | 363.1 | 345.8 | 359.5 | 388.7 | 339.8 | 337.5
2052 | 1866 | 276.3 | 362.2 | 362.4 | 345.3 | 357.8 | 387.7 | 338.5 | 336.8
2053 | 1867 | 275.8 | 361.5 | 361.7 | 344.7 | 356.2 | 386.6 | 337.9 | 336.2
2054 | 1868 | 275.2 | 360.7 | 361 | 344 | 355.8 | 385.4 | 336.4 | 335.5
2055 | 1869 | 274.8 | 360 | 360.3 | 343.3 | 355.4 | 384.3 | 336.1 | 334.8
2056 | 1870 | 274.4 | 359.3 | 359.7 | 342.5 | 354.3 | 383.2 | 335.2 | 334.2
2057 | 1871 | 273.9 | 358.5 | 359 | 341.7 | 353.1 | 382 | 333.3 | 333.5
2058 | 1872 | 273.5 | 357.8 | 358.3 | 340.9 | 351.7 | 380.9 | 332 | 332.8
2059 | 1873 | 273 | 357.1 | 357.7 | 340.1 | 351.2 | 379.8 | 330.2 | 332.2
2060 | 1874 | 272.6 | 356.3 | 357 | 339.3 | 350.4 | 378.7 | 329.1 | 331.5
2061 | 1875 | 272.2 | 355.6 | 356.4 | 338.5 | 349.6 | 377.6 | 328.7 | 330.8
2062 | 1876 | 271.6 | 354.9 | 355.7 | 337.8 | 349.1 | 376.6 | 328.1 | 330.1
2063 | 1877 | 271 | 354.1 | 355.1 | 337.1 | 348.3 | 375.6 | 327.3 | 329.5
2064 | 1878 | 270.6 | 353.4 | 354.4 | 336.4 | 347.3 | 374.5 | 325.6 | 328.9
2065 | 1879 | 270.2 | 352.7 | 353.8 | 335.7 | 346.2 | 373.4 | 324.2 | 328.2
2066 | 1880 | 269.8 | 351.9 | 353.1 | 335.1 | 344.8 | 372.3 | 323.7 | 327.5
2067 | 1881 | 269.4 | 351.2 | 352.4 | 334.4 | 343.4 | 371.1 | 323.2 | 326.8
2068 | 1882 | 268.9 | 350.4 | 351.8 | 333.7 | 342.6 | 370 | 322.3 | 326.2
2069 | 1883 | 268.5 | 349.7 | 351.2 | 333 | 341.3 | 368.8 | 320.6 | 325.5
2070 | 1884 | 268.2 | 348.9 | 350.5 | 332.3 | 339.9 | 367.7 | 319.5 | 324.9
2071 | 1885 | 267.8 | 348.1 | 349.9 | 331.5 | 339.2 | 366.6 | 318.4 | 324.3
2072 | 1886 | 267.3 | 347.4 | 349.2 | 330.8 | 338.2 | 365.5 | 317.6 | 323.7
2073 | 1887 | 266.9 | 346.6 | 348.4 | 330.1 | 337.1 | 364.4 | 316.5 | 323.1
2074 | 1888 | 266.5 | 345.9 | 347.8 | 329.4 | 335.9 | 363.4 | 315.5 | 322.5
2075 | 1889 | 266.1 | 345.1 | 347.1 | 328.7 | 335 | 362.3 | 314.2 | 321.9
2076 | 1890 | 265.6 | 344.4 | 346.4 | 327.9 | 333.6 | 361.3 | 312.7 | 321.3
2077 | 1891 | 265.2 | 343.6 | 345.8 | 327 | 332.5 | 360.2 | 313 | 320.7
2078 | 1892 | 264.9 | 342.9 | 345.2 | 326.2 | 331.8 | 359.1 | 312.2 | 320.2
2079 | 1893 | 264.5 | 342.1 | 344.6 | 325.4 | 331.1 | 358.1 | 310.8 | 319.6
2080 | 1894 | 264.1 | 341.4 | 343.8 | 324.6 | 330.3 | 357.1 | 309.4 | 319
2081 | 1895 | 263.6 | 340.6 | 343.2 | 323.9 | 329.8 | 356.2 | 308.1 | 318.5
2082 | 1896 | 263.2 | 339.9 | 342.5 | 323.2 | 328.9 | 355.1 | 306.7 | 317.9
2083 | 1897 | 262.7 | 339.1 | 341.9 | 322.5 | 327.8 | 353.9 | 305.7 | 317.4
2084 | 1898 | 262.3 | 338.4 | 341.2 | 321.9 | 327 | 352.7 | 304.7 | 316.8
2085 | 1899 | 261.9 | 337.6 | 340.5 | 321.2 | 326 | 351.6 | 304.1 | 316.2
2086 | 1900 | 261.5 | 336.9 | 339.8 | 320.5 | 325.9 | 350.6 | 303.5 | 315.7
2087 | 1901 | 261 | 336.2 | 339.3 | 319.9 | 325.9 | 349.6 | 302.4 | 315.1
2088 | 1902 | 260.6 | 335.4 | 338.6 | 319.4 | 325.7 | 348.7 | 301.4 | 314.6
2089 | 1903 | 260.1 | 334.7 | 338 | 318.9 | 325.3 | 347.7 | 301.2 | 314
2090 | 1904 | 259.6 | 333.9 | 337.4 | 318.4 | 325.1 | 346.8 | 301.1 | 313.4
2091 | 1905 | 259.3 | 333.2 | 336.7 | 317.9 | 325.1 | 345.9 | 300.2 | 312.8
2092 | 1906 | 258.8 | 332.5 | 336 | 317.5 | 325 | 344.9 | 299.3 | 312.3
2093 | 1907 | 258.4 | 331.7 | 335.4 | 317 | 324.9 | 343.8 | 298.5 | 311.7
2094 | 1908 | 258 | 331 | 334.7 | 316.5 | 324.6 | 342.5 | 297.6 | 311.1
2095 | 1909 | 257.6 | 330.3 | 334 | 316 | 324.1 | 341.3 | 296.6 | 310.6
2096 | 1910 | 257.2 | 329.5 | 333.4 | 315.5 | 323.7 | 340 | 295.6 | 310
2097 | 1911 | 256.8 | 328.8 | 332.7 | 315 | 323.5 | 338.8 | 294.7 | 309.5
2098 | 1912 | 256.5 | 328.1 | 332 | 314.4 | 322.2 | 337.6 | 293.9 | 309
2099 | 1913 | 256.1 | 327.4 | 331.4 | 313.9 | 321 | 336.2 | 293.1 | 308.5
2100 | 1914 | 255.7 | 326.7 | 330.7 | 313.3 | 320.3 | 334.9 | 292.5 | 307.9
2101 | 1915 | 255.3 | 326 | 330.1 | 312.7 | 319.7 | 333.6 | 291.1 | 307.4
2102 | 1916 | 254.9 | 325.3 | 329.4 | 312.1 | 318.8 | 332.3 | 290 | 306.9
2103 | 1917 | 254.5 | 324.6 | 328.8 | 311.5 | 318 | 331.2 | 288.5 | 306.4
2104 | 1918 | 254.1 | 323.9 | 328.1 | 310.9 | 316.8 | 330.1 | 287.2 | 305.8
2105 | 1919 | 253.8 | 323.3 | 327.5 | 310.2 | 316.2 | 329 | 286.6 | 305.3
2106 | 1920 | 253.5 | 322.6 | 326.9 | 309.6 | 315.1 | 328 | 285.6 | 304.7
2107 | 1921 | 253.1 | 321.9 | 326.3 | 309 | 313.4 | 326.9 | 284.4 | 304.2
2108 | 1922 | 252.7 | 321.2 | 325.5 | 308.3 | 312.3 | 325.8 | 283.9 | 303.7
2109 | 1923 | 252.3 | 320.6 | 324.9 | 307.6 | 311.5 | 324.7 | 283.8 | 303.2
2110 | 1924 | 252 | 319.9 | 324.3 | 306.9 | 310.9 | 323.6 | 283.8 | 302.6
2111 | 1925 | 251.8 | 319.2 | 323.7 | 306.2 | 311.1 | 322.6 | 282.7 | 302.1
2112 | 1926 | 251.5 | 318.6 | 323.1 | 305.6 | 309.7 | 321.5 | 281.2 | 301.6
2113 | 1927 | 251.1 | 317.9 | 322.3 | 304.9 | 308.6 | 320.4 | 280.1 | 301.1
2114 | 1928 | 250.6 | 317.2 | 321.7 | 304.2 | 307.5 | 319.3 | 279.5 | 300.6
2115 | 1929 | 250.2 | 316.5 | 321.2 | 303.5 | 307.1 | 318.3 | 278.4 | 300.1
2116 | 1930 | 249.8 | 315.8 | 320.5 | 302.8 | 306.7 | 317.3 | 277.8 | 299.6
2117 | 1931 | 249.4 | 315.2 | 319.8 | 302 | 305.9 | 316.4 | 276.4 | 299.1
2118 | 1932 | 249.1 | 314.5 | 319.2 | 301.3 | 304.4 | 315.4 | 275.2 | 298.6
2119 | 1933 | 248.7 | 313.8 | 318.6 | 300.6 | 304.4 | 314.4 | 274.8 | 298.1
2120 | 1934 | 248.2 | 313.1 | 318.1 | 299.9 | 304 | 313.4 | 273.7 | 297.6
2121 | 1935 | 247.8 | 312.4 | 317.5 | 299.3 | 304 | 312.4 | 273 | 297.1
2122 | 1936 | 247.3 | 311.7 | 316.9 | 298.7 | 304 | 311.4 | 272.4 | 296.6
2123 | 1937 | 246.9 | 311.1 | 316.1 | 298.2 | 304.1 | 310.4 | 271.5 | 296.1
2124 | 1938 | 246.5 | 310.4 | 315.6 | 297.7 | 304.1 | 309.3 | 270.9 | 295.6
2125 | 1939 | 246.2 | 309.7 | 315 | 297.3 | 304 | 308.2 | 270.2 | 295.1
2126 | 1940 | 245.8 | 309.1 | 314.5 | 296.8 | 303.6 | 307.1 | 269.8 | 294.7
2127 | 1941 | 245.5 | 308.4 | 313.8 | 296.3 | 303.3 | 306.1 | 269.4 | 294.2
2128 | 1942 | 245.1 | 307.8 | 313.2 | 295.8 | 303.3 | 305.1 | 268.4 | 293.7
2129 | 1943 | 244.6 | 307.1 | 312.7 | 295.4 | 302.9 | 304.1 | 268 | 293.2
2130 | 1944 | 244.3 | 306.5 | 312.1 | 295 | 302.4 | 303 | 267.3 | 292.8
2131 | 1945 | 244 | 305.8 | 311.5 | 294.6 | 301.8 | 301.9 | 266.2 | 292.3
2132 | 1946 | 243.6 | 305.2 | 310.9 | 294.1 | 301.1 | 300.9 | 265.2 | 291.8
2133 | 1947 | 243.2 | 304.5 | 310.3 | 293.7 | 300.5 | 299.8 | 264.1 | 291.3
2134 | 1948 | 242.9 | 303.8 | 309.6 | 293.2 | 300.1 | 298.8 | 263.8 | 290.8
2135 | 1949 | 242.6 | 303.2 | 309 | 292.7 | 299.9 | 297.8 | 263.3 | 290.3
2136 | 1950 | 242.2 | 302.5 | 308.5 | 292.2 | 299.3 | 296.8 | 262.2 | 289.8
2137 | 1951 | 241.8 | 301.8 | 307.9 | 291.7 | 298.3 | 295.7 | 261.2 | 289.4
2138 | 1952 | 241.3 | 301.2 | 307.2 | 291.2 | 297.5 | 294.7 | 260.7 | 289
2139 | 1953 | 240.9 | 300.5 | 306.6 | 290.6 | 297 | 293.6 | 260.5 | 288.5
2140 | 1954 | 240.6 | 299.9 | 306 | 290.1 | 296.2 | 292.6 | 259.5 | 288.1
2141 | 1955 | 240.3 | 299.2 | 305.4 | 289.6 | 295.8 | 291.7 | 259.2 | 287.7
2142 | 1956 | 240 | 298.6 | 304.8 | 289.1 | 295.6 | 290.7 | 258.4 | 287.2
2143 | 1957 | 239.7 | 297.9 | 304.2 | 288.7 | 295.3 | 289.7 | 257.7 | 286.8
2144 | 1958 | 239.4 | 297.3 | 303.6 | 288.2 | 294.9 | 288.8 | 257.5 | 286.4
2145 | 1959 | 239.1 | 296.7 | 303.1 | 287.7 | 294.8 | 288 | 257.1 | 286
2146 | 1960 | 238.7 | 296 | 302.5 | 287.3 | 294.5 | 287 | 256.7 | 285.5
2147 | 1961 | 238.3 | 295.4 | 301.9 | 286.9 | 293.6 | 285.9 | 256 | 285.1
2148 | 1962 | 238 | 294.8 | 301.3 | 286.5 | 292.8 | 284.7 | 255.3 | 284.6
2149 | 1963 | 237.7 | 294.2 | 300.7 | 286.1 | 292.2 | 283.6 | 254.9 | 284.2
2150 | 1964 | 237.4 | 293.6 | 300.1 | 285.6 | 292.1 | 282.6 | 254.6 | 283.7
2151 | 1965 | 237.1 | 293 | 299.6 | 285.2 | 292.1 | 281.5 | 254.3 | 283.3
2152 | 1966 | 236.7 | 292.4 | 299 | 284.7 | 291.9 | 280.5 | 254 | 282.8
2153 | 1967 | 236.3 | 291.8 | 298.4 | 284.2 | 291.7 | 279.6 | 253.7 | 282.4
2154 | 1968 | 236 | 291.2 | 297.8 | 283.7 | 291.6 | 278.7 | 253.2 | 282
2155 | 1969 | 235.7 | 290.6 | 297.3 | 283.3 | 291.5 | 277.8 | 253 | 281.5
2156 | 1970 | 235.3 | 290 | 296.7 | 282.8 | 291.3 | 276.9 | 252.6 | 281.1
2157 | 1971 | 235 | 289.4 | 296.2 | 282.4 | 291.1 | 276 | 252.3 | 280.6
2158 | 1972 | 234.6 | 288.8 | 295.6 | 282.1 | 290.6 | 274.9 | 251.9 | 280.2
2159 | 1973 | 234.2 | 288.3 | 295.1 | 281.7 | 290.3 | 273.9 | 251.5 | 279.7
2160 | 1974 | 233.9 | 287.7 | 294.6 | 281.3 | 289.7 | 272.8 | 251 | 279.2
2161 | 1975 | 233.6 | 287.1 | 294 | 281 | 289.3 | 271.8 | 250.5 | 278.8
2162 | 1976 | 233.3 | 286.5 | 293.5 | 280.7 | 288.8 | 270.8 | 250 | 278.3
2163 | 1977 | 232.9 | 286 | 292.9 | 280.4 | 288.5 | 269.7 | 249.5 | 277.9
2164 | 1978 | 232.6 | 285.4 | 292.4 | 280.1 | 288.1 | 268.7 | 248.9 | 277.4
2165 | 1979 | 232.1 | 284.8 | 291.8 | 279.7 | 287.7 | 267.8 | 248.3 | 276.9
2166 | 1980 | 231.7 | 284.3 | 291.3 | 279.3 | 287.3 | 266.9 | 247.8 | 276.4
2167 | 1981 | 231.4 | 283.7 | 290.7 | 279 | 286.8 | 266.1 | 247.2 | 276
2168 | 1982 | 231 | 283.2 | 290.2 | 278.6 | 286.3 | 265.3 | 246.6 | 275.5
2169 | 1983 | 230.6 | 282.6 | 289.6 | 278.3 | 285.7 | 264.4 | 245.9 | 275.1
2170 | 1984 | 230.3 | 282.1 | 289.1 | 277.9 | 285.2 | 263.6 | 245.4 | 274.6
2171 | 1985 | 229.9 | 281.6 | 288.5 | 277.6 | 284.8 | 262.7 | 245.1 | 274.2
2172 | 1986 | 229.7 | 281.1 | 288 | 277.3 | 284.2 | 261.8 | 244.5 | 273.8
2173 | 1987 | 229.4 | 280.5 | 287.4 | 276.9 | 283.5 | 260.9 | 243.6 | 273.3
2174 | 1988 | 229.1 | 280 | 286.9 | 276.5 | 283.1 | 260.1 | 243 | 272.9
2175 | 1989 | 228.7 | 279.5 | 286.3 | 276 | 282.7 | 259.3 | 242.5 | 272.5
2176 | 1990 | 228.4 | 278.9 | 285.8 | 275.5 | 282.2 | 258.4 | 242.1 | 272.1
2177 | 1991 | 228.1 | 278.4 | 285.2 | 275 | 281.7 | 257.5 | 241.5 | 271.7
2178 | 1992 | 227.8 | 277.8 | 284.6 | 274.5 | 281.3 | 256.6 | 241.1 | 271.3
2179 | 1993 | 227.5 | 277.3 | 284 | 274 | 280.6 | 255.7 | 240.4 | 270.9
2180 | 1994 | 227.2 | 276.8 | 283.5 | 273.5 | 279.4 | 254.7 | 239.4 | 270.4
2181 | 1995 | 226.8 | 276.2 | 282.9 | 272.9 | 278.6 | 253.7 | 238.6 | 270
2182 | 1996 | 226.6 | 275.7 | 282.4 | 272.3 | 278.3 | 252.8 | 238.6 | 269.6
2183 | 1997 | 226.3 | 275.1 | 281.8 | 271.8 | 277.7 | 251.9 | 237.7 | 269.2
2184 | 1998 | 225.9 | 274.6 | 281.3 | 271.2 | 277.4 | 251 | 237.7 | 268.8
2185 | 1999 | 225.6 | 274.1 | 280.8 | 270.6 | 276.9 | 250.2 | 237.2 | 268.3
2186 | 2000 | 225.2 | 273.5 | 280.2 | 270 | 276.4 | 249.3 | 236.6 | 267.9
2187 | 2001 | 224.9 | 273 | 279.7 | 269.5 | 275.6 | 248.5 | 235.8 | 267.5
2188 | 2002 | 224.5 | 272.5 | 279.1 | 268.9 | 275.1 | 247.6 | 235.2 | 267.1
2189 | 2003 | 224.1 | 271.9 | 278.6 | 268.4 | 274.8 | 246.9 | 234.5 | 266.7
2190 | 2004 | 223.7 | 271.4 | 278.1 | 267.8 | 274.3 | 246.2 | 234 | 266.3
2191 | 2005 | 223.4 | 270.9 | 277.6 | 267.3 | 273.9 | 245.5 | 233.3 | 265.8
2192 | 2006 | 223.1 | 270.4 | 277.1 | 266.8 | 273.5 | 244.8 | 232.8 | 265.4
2193 | 2007 | 222.8 | 269.9 | 276.6 | 266.3 | 273 | 244 | 232.3 | 265
2194 | 2008 | 222.5 | 269.4 | 276 | 265.8 | 272.8 | 243.3 | 232 | 264.6
2195 | 2009 | 222.4 | 268.8 | 275.5 | 265.3 | 272.4 | 242.6 | 231.6 | 264.2
2196 | 2010 | 222.1 | 268.3 | 274.9 | 264.8 | 271.7 | 241.9 | 231.1 | 263.8
2197 | 2011 | 221.8 | 267.8 | 274.4 | 264.3 | 270.9 | 241.1 | 230.8 | 263.4
2198 | 2012 | 221.4 | 267.3 | 273.8 | 263.7 | 269.3 | 240.3 | 230.6 | 263
2199 | 2013 | 221.2 | 266.8 | 273.3 | 263.1 | 268.1 | 239.4 | 230.1 | 262.6
2200 | 2014 | 220.9 | 266.3 | 272.8 | 262.6 | 267 | 238.6 | 230.2 | 262.2
2201 | 2015 | 220.6 | 265.8 | 272.3 | 262 | 266.3 | 237.8 | 229.9 | 261.8
2202 | 2016 | 220.3 | 265.2 | 271.8 | 261.4 | 265.9 | 237.1 | 229.1 | 261.5
2203 | 2017 | 220.1 | 264.7 | 271.3 | 260.8 | 265.4 | 236.3 | 228.8 | 261.1
2204 | 2018 | 219.8 | 264.2 | 270.8 | 260.3 | 265 | 235.6 | 228.2 | 260.7
2205 | 2019 | 219.5 | 263.7 | 270.3 | 259.7 | 264.5 | 234.9 | 228.2 | 260.3
2206 | 2020 | 219.2 | 263.2 | 269.8 | 259.1 | 263.8 | 234.3 | 227.7 | 260
2207 | 2021 | 218.8 | 262.7 | 269.3 | 258.5 | 263 | 233.6 | 227.8 | 259.6
2208 | 2022 | 218.6 | 262.1 | 268.8 | 258 | 262.1 | 232.9 | 227.5 | 259.2
2209 | 2023 | 218.4 | 261.6 | 268.3 | 257.4 | 261.9 | 232.2 | 226.7 | 258.8
2210 | 2024 | 218 | 261.1 | 267.8 | 256.8 | 261.1 | 231.5 | 226.6 | 258.4
2211 | 2025 | 217.7 | 260.6 | 267.3 | 256.3 | 260.6 | 230.8 | 226.3 | 258.1
2212 | 2026 | 217.4 | 260 | 266.7 | 255.8 | 260.4 | 230.1 | 226.2 | 257.7
2213 | 2027 | 217.1 | 259.5 | 266.2 | 255.3 | 260.3 | 229.4 | 225.7 | 257.3
2214 | 2028 | 216.8 | 259 | 265.7 | 254.7 | 260.1 | 228.8 | 225 | 256.9
2215 | 2029 | 216.5 | 258.4 | 265.1 | 254.2 | 259.8 | 228.2 | 224.5 | 256.5
2216 | 2030 | 216.3 | 257.9 | 264.6 | 253.6 | 258.9 | 227.6 | 223.8 | 256.1
2217 | 2031 | 216 | 257.4 | 264 | 253.1 | 257.5 | 227 | 223.4 | 255.7
2218 | 2032 | 215.7 | 256.8 | 263.5 | 252.5 | 256.8 | 226.4 | 223.1 | 255.3
2219 | 2033 | 215.4 | 256.3 | 263.1 | 252 | 256.4 | 225.8 | 223.1 | 254.9
2220 | 2034 | 215 | 255.7 | 262.6 | 251.5 | 256.1 | 225.2 | 222.7 | 254.5
2221 | 2035 | 214.7 | 255.2 | 262.2 | 251 | 256.1 | 224.5 | 222.7 | 254.1
2222 | 2036 | 214.4 | 254.6 | 261.7 | 250.5 | 255.6 | 224 | 222 | 253.8
2223 | 2037 | 214.1 | 254.1 | 261.2 | 250 | 254.7 | 223.4 | 221.5 | 253.4
2224 | 2038 | 213.9 | 253.5 | 260.7 | 249.5 | 254.4 | 222.8 | 221.4 | 253
2225 | 2039 | 213.7 | 253 | 260.3 | 249.1 | 254.2 | 222.2 | 220.9 | 252.6
2226 | 2040 | 213.4 | 252.5 | 259.7 | 248.6 | 254.3 | 221.6 | 220.4 | 252.3
2227 | 2041 | 213 | 251.9 | 259.3 | 248.2 | 254.1 | 221 | 219.9 | 251.9
2228 | 2042 | 212.6 | 251.4 | 258.8 | 247.8 | 253.7 | 220.3 | 219.3 | 251.6
2229 | 2043 | 212.2 | 250.8 | 258.3 | 247.4 | 253.5 | 219.6 | 218.8 | 251.1
2230 | 2044 | 211.9 | 250.3 | 257.8 | 247 | 253 | 218.9 | 218.3 | 250.7
2231 | 2045 | 211.6 | 249.7 | 257.3 | 246.6 | 252.7 | 218.2 | 217.7 | 250.4
2232 | 2046 | 211.2 | 249.2 | 256.7 | 246.2 | 251.8 | 217.5 | 217.2 | 250
2233 | 2047 | 210.9 | 248.7 | 256.2 | 245.8 | 251 | 216.8 | 216.6 | 249.6
2234 | 2048 | 210.6 | 248.1 | 255.7 | 245.4 | 250.6 | 216.1 | 215.9 | 249.2
2235 | 2049 | 210.4 | 247.6 | 255.2 | 245 | 250.1 | 215.5 | 215.2 | 248.8
2236 | 2050 | 210.1 | 247 | 254.7 | 244.6 | 249.6 | 214.9 | 214.3 | 248.4
2237 | 2051 | 209.8 | 246.5 | 254.2 | 244.2 | 249.3 | 214.2 | 213.4 | 248.1
2238 | 2052 | 209.6 | 246 | 253.7 | 243.8 | 249.1 | 213.6 | 212.6 | 247.7
2239 | 2053 | 209.4 | 245.4 | 253.1 | 243.4 | 248.7 | 213 | 211.8 | 247.3
2240 | 2054 | 209.1 | 244.9 | 252.6 | 243 | 248.3 | 212.5 | 211 | 247
2241 | 2055 | 208.8 | 244.4 | 252.1 | 242.5 | 247.8 | 212 | 210.2 | 246.6
2242 | 2056 | 208.4 | 243.8 | 251.5 | 242 | 247.3 | 211.4 | 209.4 | 246.2
2243 | 2057 | 208.1 | 243.3 | 251 | 241.6 | 246.6 | 210.9 | 209.1 | 245.9
2244 | 2058 | 207.7 | 242.8 | 250.5 | 241.1 | 246.2 | 210.4 | 208.4 | 245.5
2245 | 2059 | 207.5 | 242.3 | 250 | 240.7 | 245.5 | 209.9 | 207.4 | 245.2
2246 | 2060 | 207.2 | 241.7 | 249.5 | 240.2 | 244.5 | 209.4 | 206.7 | 244.8
2247 | 2061 | 206.9 | 241.2 | 249 | 239.8 | 244.2 | 209 | 206.4 | 244.5
2248 | 2062 | 206.6 | 240.7 | 248.6 | 239.4 | 244.1 | 208.5 | 205.9 | 244.1
2249 | 2063 | 206.3 | 240.2 | 248.1 | 239 | 243.5 | 208 | 205.1 | 243.8
2250 | 2064 | 206 | 239.7 | 247.6 | 238.6 | 242.3 | 207.6 | 204 | 243.4
2251 | 2065 | 205.8 | 239.2 | 247.2 | 238.1 | 241.8 | 207.1 | 203.8 | 243.1
2252 | 2066 | 205.6 | 238.7 | 246.7 | 237.7 | 241.3 | 206.7 | 202.9 | 242.7
2253 | 2067 | 205.4 | 238.1 | 246.2 | 237.3 | 240.6 | 206.2 | 202 | 242.4
2254 | 2068 | 205.1 | 237.6 | 245.7 | 236.9 | 240.4 | 205.7 | 201.9 | 242
2255 | 2069 | 204.8 | 237.1 | 245.1 | 236.5 | 240.1 | 205.3 | 201.4 | 241.7
2256 | 2070 | 204.5 | 236.6 | 244.7 | 236.1 | 239.8 | 204.8 | 200.9 | 241.4
2257 | 2071 | 204.2 | 236.2 | 244.2 | 235.7 | 239.4 | 204.4 | 200 | 241
2258 | 2072 | 204 | 235.7 | 243.7 | 235.3 | 239 | 204 | 199.5 | 240.7
2259 | 2073 | 203.7 | 235.2 | 243.3 | 234.9 | 238.3 | 203.6 | 198.7 | 240.4
2260 | 2074 | 203.3 | 234.7 | 242.8 | 234.5 | 237.2 | 203.1 | 198.1 | 240.1
2261 | 2075 | 203.1 | 234.2 | 242.4 | 234.2 | 236.5 | 202.7 | 197.1 | 239.7
2262 | 2076 | 202.9 | 233.7 | 241.9 | 233.8 | 236 | 202.2 | 196.3 | 239.4
2263 | 2077 | 202.6 | 233.2 | 241.4 | 233.4 | 235.8 | 201.8 | 196.1 | 239.1
2264 | 2078 | 202.2 | 232.8 | 241 | 233 | 235.3 | 201.4 | 195.3 | 238.7
2265 | 2079 | 201.9 | 232.3 | 240.5 | 232.6 | 234.8 | 200.9 | 194.6 | 238.4
2266 | 2080 | 201.6 | 231.8 | 240 | 232.2 | 234 | 200.5 | 194 | 238
2267 | 2081 | 201.3 | 231.3 | 239.6 | 231.8 | 233.6 | 200 | 193.2 | 237.7
2268 | 2082 | 201 | 230.9 | 239.1 | 231.4 | 233.4 | 199.5 | 192.6 | 237.3
2269 | 2083 | 200.8 | 230.4 | 238.6 | 231.1 | 233 | 199.1 | 192.1 | 237
2270 | 2084 | 200.5 | 229.9 | 238.1 | 230.7 | 232.6 | 198.6 | 192.2 | 236.7
2271 | 2085 | 200.2 | 229.5 | 237.7 | 230.3 | 231.7 | 198.2 | 192.2 | 236.4
2272 | 2086 | 199.9 | 229 | 237.2 | 229.9 | 231 | 197.8 | 192.2 | 236
2273 | 2087 | 199.7 | 228.5 | 236.7 | 229.5 | 231 | 197.4 | 191.7 | 235.7
2274 | 2088 | 199.4 | 228.1 | 236.3 | 229.1 | 231 | 197 | 191.2 | 235.4
2275 | 2089 | 199.1 | 227.7 | 235.9 | 228.8 | 230.8 | 196.7 | 190.8 | 235
2276 | 2090 | 198.8 | 227.2 | 235.4 | 228.5 | 230.7 | 196.4 | 190.8 | 234.7
2277 | 2091 | 198.5 | 226.8 | 234.9 | 228.2 | 230.5 | 196 | 190.7 | 234.3
2278 | 2092 | 198.2 | 226.4 | 234.5 | 227.9 | 230.4 | 195.6 | 190.5 | 234
2279 | 2093 | 198 | 226 | 234.1 | 227.6 | 230.1 | 195.2 | 190.1 | 233.7
2280 | 2094 | 197.7 | 225.5 | 233.7 | 227.2 | 229.9 | 194.8 | 189.3 | 233.4
2281 | 2095 | 197.5 | 225.1 | 233.2 | 226.9 | 229.7 | 194.3 | 188.8 | 233
2282 | 2096 | 197.3 | 224.7 | 232.8 | 226.6 | 229.2 | 193.9 | 188.3 | 232.7
2283 | 2097 | 197.1 | 224.3 | 232.3 | 226.2 | 228.5 | 193.5 | 188 | 232.3
2284 | 2098 | 196.9 | 223.9 | 231.9 | 225.8 | 227.4 | 193 | 187.9 | 231.9
2285 | 2099 | 196.7 | 223.5 | 231.5 | 225.4 | 226.4 | 192.6 | 187.7 | 231.5
2286 | 2100 | 196.3 | 223.1 | 231 | 225 | 225.7 | 192.1 | 187.2 | 231.2
2287 | 2101 | 196.1 | 222.7 | 230.6 | 224.6 | 225.6 | 191.7 | 187 | 230.8
2288 | 2102 | 195.9 | 222.2 | 230.2 | 224.3 | 225.4 | 191.3 | 186.4 | 230.4
2289 | 2103 | 195.7 | 221.8 | 229.8 | 223.9 | 225.3 | 190.8 | 186.2 | 230.1
2290 | 2104 | 195.5 | 221.4 | 229.4 | 223.6 | 225.4 | 190.4 | 185.9 | 229.8
2291 | 2105 | 195.3 | 221 | 229 | 223.3 | 225.3 | 190 | 185.8 | 229.5
2292 | 2106 | 195 | 220.6 | 228.6 | 223 | 225.3 | 189.7 | 185.6 | 229.1
2293 | 2107 | 194.8 | 220.2 | 228.2 | 222.7 | 225 | 189.3 | 185.6 | 228.8
2294 | 2108 | 194.5 | 219.8 | 227.8 | 222.5 | 224.8 | 188.9 | 185.4 | 228.5
2295 | 2109 | 194.2 | 219.4 | 227.4 | 222.2 | 224.6 | 188.6 | 185 | 228.1
2296 | 2110 | 194 | 219 | 227 | 222 | 224.5 | 188.2 | 184.8 | 227.8
2297 | 2111 | 193.8 | 218.7 | 226.5 | 221.7 | 224.3 | 187.8 | 184.5 | 227.4
2298 | 2112 | 193.6 | 218.3 | 226.2 | 221.4 | 224 | 187.5 | 184.2 | 227.1
2299 | 2113 | 193.4 | 217.9 | 225.8 | 221.2 | 223.7 | 187.1 | 184 | 226.7
2300 | 2114 | 193.2 | 217.6 | 225.4 | 221 | 223.3 | 186.8 | 183.7 | 226.3
2301 | 2115 | 192.9 | 217.2 | 225 | 220.7 | 223 | 186.5 | 183.6 | 226
2302 | 2116 | 192.6 | 216.8 | 224.6 | 220.5 | 222.5 | 186 | 183.2 | 225.6
2303 | 2117 | 192.3 | 216.5 | 224.2 | 220.3 | 221.9 | 185.5 | 183.1 | 225.3
2304 | 2118 | 192.1 | 216.1 | 223.8 | 220 | 221.6 | 185.1 | 182.9 | 224.9
2305 | 2119 | 191.8 | 215.8 | 223.4 | 219.7 | 221.2 | 184.6 | 182.3 | 224.6
2306 | 2120 | 191.6 | 215.4 | 223 | 219.4 | 220.6 | 184.1 | 181.7 | 224.2
2307 | 2121 | 191.4 | 215.1 | 222.5 | 219.1 | 219.9 | 183.7 | 181.8 | 223.9
2308 | 2122 | 191.2 | 214.7 | 222.2 | 218.7 | 219.5 | 183.3 | 182 | 223.5
2309 | 2123 | 191 | 214.4 | 221.7 | 218.5 | 219.3 | 183 | 181.8 | 223.1
2310 | 2124 | 190.7 | 214.1 | 221.2 | 218.2 | 219.3 | 182.7 | 181.8 | 222.7
2311 | 2125 | 190.6 | 213.6 | 221 | 217.8 | 219.1 | 182.3 | 181.9 | 222.4
2312 | 2126 | 190.2 | 213.4 | 220.4 | 217.7 | 219.3 | 182.1 | 181.7 | 222
2313 | 2127 | 190.1 | 212.9 | 220.2 | 217.3 | 218.9 | 181.7 | 181.6 | 221.8
2314 | 2128 | 190 | 212.6 | 219.8 | 217.1 | 218.6 | 181.4 | 181.4 | 221.4
2315 | 2129 | 189.7 | 212.4 | 219.1 | 217.1 | 218.7 | 181.2 | 181.3 | 221
2316 | 2130 | 189.6 | 211.9 | 219.1 | 216.6 | 217.9 | 180.6 | 181.2 | 220.8
2317 | 2131 | 189.4 | 211.5 | 218.8 | 216.4 | 217.4 | 180.3 | 181.1 | 220.4
2318 | 2132 | 188.9 | 211.3 | 218.3 | 216.2 | 217.2 | 180 | 181 | 220
2319 | 2133 | 188.8 | 210.9 | 218.1 | 215.8 | 216.8 | 179.5 | 180.8 | 219.8
2320 | 2134 | 188.3 | 210.7 | 217.4 | 215.7 | 217 | 179.3 | 180.5 | 219.3
2321 | 2135 | 188.2 | 210.3 | 217.2 | 215.4 | 216.7 | 178.9 | 180.2 | 219
2322 | 2136 | 188.1 | 209.9 | 217 | 215 | 216.3 | 178.4 | 180 | 218.8
2323 | 2137 | 187.8 | 209.5 | 216.6 | 214.7 | 216.1 | 178.1 | 179.8 | 218.5
2324 | 2138 | 187.5 | 209.2 | 216.3 | 214.4 | 215.9 | 177.7 | 179.5 | 218.2
2325 | 2139 | 187.2 | 208.9 | 215.9 | 214.1 | 215.6 | 177.3 | 179.2 | 217.8
2326 | 2140 | 186.9 | 208.5 | 215.6 | 213.9 | 215.3 | 176.9 | 178.9 | 217.5
2327 | 2141 | 186.6 | 208.2 | 215.3 | 213.6 | 214.8 | 176.5 | 178.8 | 217.1
2328 | 2142 | 186.4 | 207.9 | 214.9 | 213.3 | 214.3 | 176.1 | 178.8 | 216.8
2329 | 2143 | 186.2 | 207.6 | 214.5 | 213 | 213.7 | 175.7 | 178.7 | 216.5
2330 | 2144 | 186 | 207.2 | 214.2 | 212.7 | 213.3 | 175.2 | 178.6 | 216.2
2331 | 2145 | 185.7 | 206.9 | 213.8 | 212.4 | 213 | 174.7 | 178.5 | 215.8
2332 | 2146 | 185.4 | 206.6 | 213.4 | 212 | 212.5 | 174.3 | 178.1 | 215.5
2333 | 2147 | 185.2 | 206.3 | 213.1 | 211.7 | 211.9 | 174 | 177.7 | 215.3
2334 | 2148 | 184.8 | 205.9 | 212.7 | 211.3 | 211.6 | 173.6 | 177.1 | 214.9
2335 | 2149 | 184.6 | 205.6 | 212.4 | 211 | 211.3 | 173.3 | 176.8 | 214.6
2336 | 2150 | 184.4 | 205.3 | 212 | 210.6 | 210.9 | 172.9 | 176.7 | 214.3
2337 | 2151 | 184.2 | 204.9 | 211.6 | 210.2 | 210.7 | 172.5 | 176.5 | 214
2338 | 2152 | 183.9 | 204.6 | 211.3 | 209.8 | 210.3 | 172.1 | 176.3 | 213.7
2339 | 2153 | 183.6 | 204.3 | 210.9 | 209.5 | 209.9 | 171.6 | 175.9 | 213.4
2340 | 2154 | 183.4 | 203.9 | 210.6 | 209.2 | 209.6 | 171.2 | 175.3 | 213.1
2341 | 2155 | 183.1 | 203.6 | 210.2 | 208.9 | 209.2 | 170.7 | 174.8 | 212.8
2342 | 2156 | 182.9 | 203.2 | 209.8 | 208.5 | 209 | 170.3 | 174.7 | 212.5
2343 | 2157 | 182.7 | 202.9 | 209.4 | 208.1 | 208.6 | 170 | 174.4 | 212.2
2344 | 2158 | 182.4 | 202.5 | 209.1 | 207.7 | 208.1 | 169.6 | 173.7 | 211.9
2345 | 2159 | 182.2 | 202.2 | 208.7 | 207.3 | 207.8 | 169.3 | 173.6 | 211.6
2346 | 2160 | 182 | 201.9 | 208.4 | 206.9 | 207.6 | 168.9 | 173.2 | 211.3
2347 | 2161 | 181.7 | 201.5 | 208.1 | 206.5 | 207.4 | 168.6 | 172.5 | 211
2348 | 2162 | 181.4 | 201.2 | 207.7 | 206.2 | 207.1 | 168.3 | 172.1 | 210.7
2349 | 2163 | 181.2 | 200.9 | 207.4 | 205.8 | 206.8 | 168 | 171.3 | 210.4
2350 | 2164 | 180.9 | 200.5 | 207 | 205.4 | 206.5 | 167.6 | 170.6 | 210.2
2351 | 2165 | 180.6 | 200.2 | 206.7 | 205.1 | 206.2 | 167.3 | 170.5 | 209.9
2352 | 2166 | 180.3 | 199.8 | 206.4 | 204.7 | 205.7 | 167 | 170.4 | 209.6
2353 | 2167 | 180 | 199.5 | 206 | 204.2 | 205.3 | 166.7 | 170.1 | 209.3
2354 | 2168 | 179.7 | 199.2 | 205.7 | 203.8 | 204.8 | 166.3 | 169.8 | 209.1
2355 | 2169 | 179.4 | 198.9 | 205.3 | 203.4 | 204.3 | 166 | 169.3 | 208.8
2356 | 2170 | 179.2 | 198.5 | 205 | 203 | 203.9 | 165.7 | 168.9 | 208.5
2357 | 2171 | 179 | 198.2 | 204.7 | 202.6 | 203.6 | 165.4 | 168.3 | 208.2
2358 | 2172 | 178.9 | 197.9 | 204.3 | 202.2 | 203.1 | 165.1 | 167.8 | 208
2359 | 2173 | 178.6 | 197.5 | 204 | 201.8 | 203 | 164.9 | 167.7 | 207.7
2360 | 2174 | 178.4 | 197.2 | 203.7 | 201.5 | 202.7 | 164.7 | 167.4 | 207.4
2361 | 2175 | 178.2 | 196.9 | 203.4 | 201.1 | 202.3 | 164.4 | 167 | 207.2
2362 | 2176 | 177.9 | 196.6 | 203 | 200.8 | 201.9 | 164.1 | 166.8 | 206.8
2363 | 2177 | 177.7 | 196.2 | 202.7 | 200.5 | 201.7 | 163.8 | 166.5 | 206.5
2364 | 2178 | 177.6 | 195.9 | 202.4 | 200.2 | 201.3 | 163.5 | 166.2 | 206.3
2365 | 2179 | 177.5 | 195.6 | 202 | 199.9 | 200.9 | 163.1 | 165.8 | 206
2366 | 2180 | 177.2 | 195.3 | 201.7 | 199.7 | 200.6 | 162.8 | 165.6 | 205.7
2367 | 2181 | 177 | 195 | 201.4 | 199.4 | 200.4 | 162.4 | 165.6 | 205.4
2368 | 2182 | 176.8 | 194.7 | 201.1 | 199.2 | 200.2 | 162.1 | 165 | 205.1
2369 | 2183 | 176.6 | 194.3 | 200.7 | 199 | 200 | 161.8 | 164.4 | 204.8
2370 | 2184 | 176.4 | 194 | 200.4 | 198.7 | 199.7 | 161.5 | 164 | 204.6
2371 | 2185 | 176.2 | 193.7 | 200.1 | 198.4 | 199.5 | 161.1 | 163.9 | 204.3
2372 | 2186 | 176 | 193.4 | 199.7 | 198.1 | 199.2 | 160.8 | 163.6 | 204
2373 | 2187 | 175.8 | 193.1 | 199.4 | 197.8 | 199 | 160.5 | 162.8 | 203.8
2374 | 2188 | 175.5 | 192.8 | 199 | 197.5 | 198.7 | 160.2 | 162 | 203.5
2375 | 2189 | 175.3 | 192.5 | 198.6 | 197.1 | 198.4 | 159.9 | 161.8 | 203.3
2376 | 2190 | 175 | 192.2 | 198.3 | 196.8 | 198.3 | 159.6 | 161.8 | 203
2377 | 2191 | 174.8 | 191.8 | 198 | 196.5 | 197.8 | 159.3 | 161.4 | 202.7
2378 | 2192 | 174.6 | 191.5 | 197.7 | 196.2 | 197.3 | 159 | 160.8 | 202.5
2379 | 2193 | 174.4 | 191.2 | 197.3 | 195.8 | 196.8 | 158.6 | 160.4 | 202.2
2380 | 2194 | 174.2 | 190.9 | 197 | 195.5 | 196.3 | 158.3 | 160.3 | 201.9
2381 | 2195 | 174 | 190.6 | 196.7 | 195.1 | 196 | 158 | 160.2 | 201.7
2382 | 2196 | 173.8 | 190.3 | 196.3 | 194.7 | 195.9 | 157.7 | 159.7 | 201.4
2383 | 2197 | 173.6 | 190 | 196 | 194.4 | 195.7 | 157.4 | 159.4 | 201.1
2384 | 2198 | 173.4 | 189.6 | 195.7 | 194.1 | 195.3 | 157.1 | 159.2 | 200.8
2385 | 2199 | 173.2 | 189.3 | 195.4 | 193.8 | 195.1 | 156.8 | 158.7 | 200.6
2386 | 2200 | 173 | 189 | 195.1 | 193.5 | 194.8 | 156.5 | 158.2 | 200.4
2387 | 2201 | 172.8 | 188.6 | 194.8 | 193.2 | 194.4 | 156.3 | 157.9 | 200.1
2388 | 2202 | 172.5 | 188.3 | 194.5 | 192.9 | 194 | 156 | 157.4 | 199.9
2389 | 2203 | 172.3 | 188 | 194.1 | 192.5 | 193.2 | 155.7 | 156.8 | 199.6
2390 | 2204 | 172.1 | 187.6 | 193.8 | 192.2 | 192.6 | 155.5 | 156.4 | 199.4
2391 | 2205 | 171.9 | 187.3 | 193.5 | 191.9 | 192.4 | 155.3 | 155.8 | 199.1
2392 | 2206 | 171.6 | 187 | 193.2 | 191.5 | 192.2 | 155.1 | 155.3 | 198.9
2393 | 2207 | 171.4 | 186.6 | 192.8 | 191.1 | 191.7 | 154.9 | 154.8 | 198.6
2394 | 2208 | 171.1 | 186.3 | 192.5 | 190.8 | 191.4 | 154.7 | 154.3 | 198.4
2395 | 2209 | 170.8 | 186 | 192.2 | 190.4 | 190.9 | 154.4 | 153.9 | 198.2
2396 | 2210 | 170.6 | 185.6 | 191.8 | 190 | 190 | 154.2 | 153.3 | 198
2397 | 2211 | 170.4 | 185.3 | 191.5 | 189.6 | 189.3 | 154 | 152.6 | 197.8
2398 | 2212 | 170.2 | 184.9 | 191.2 | 189.2 | 188.9 | 153.7 | 152 | 197.5
2399 | 2213 | 170 | 184.6 | 190.8 | 188.8 | 188.1 | 153.5 | 151.6 | 197.3
2400 | 2214 | 169.8 | 184.3 | 190.5 | 188.4 | 187.5 | 153.2 | 151.1 | 197.1
2401 | 2215 | 169.5 | 183.9 | 190.1 | 188 | 187.1 | 153 | 150.6 | 196.9
2402 | 2216 | 169.3 | 183.6 | 189.8 | 187.6 | 186.8 | 152.7 | 150 | 196.7
2403 | 2217 | 169.1 | 183.2 | 189.5 | 187.2 | 186.5 | 152.5 | 149.6 | 196.5
2404 | 2218 | 168.9 | 182.9 | 189.2 | 186.8 | 186.2 | 152.3 | 149.2 | 196.3
2405 | 2219 | 168.6 | 182.6 | 188.8 | 186.4 | 185.9 | 152.1 | 149.1 | 196
2406 | 2220 | 168.4 | 182.2 | 188.5 | 186 | 185.4 | 151.9 | 148.6 | 195.8
2407 | 2221 | 168.2 | 181.9 | 188.2 | 185.7 | 184.6 | 151.6 | 148.3 | 195.6
2408 | 2222 | 168 | 181.6 | 187.8 | 185.4 | 184 | 151.4 | 147.7 | 195.4
2409 | 2223 | 167.8 | 181.3 | 187.4 | 185 | 183.5 | 151.1 | 147.2 | 195.1
2410 | 2224 | 167.6 | 180.9 | 187 | 184.6 | 182.8 | 150.9 | 146.9 | 195
2411 | 2225 | 167.4 | 180.6 | 186.7 | 184.1 | 182.4 | 150.6 | 146.5 | 194.7
2412 | 2226 | 167.3 | 180.3 | 186.4 | 183.7 | 182 | 150.5 | 145.9 | 194.5
2413 | 2227 | 167.1 | 180 | 186.1 | 183.4 | 181.8 | 150.2 | 145.4 | 194.3
2414 | 2228 | 167 | 179.7 | 185.7 | 183 | 181.2 | 150 | 145 | 194
2415 | 2229 | 166.8 | 179.3 | 185.4 | 182.6 | 180.7 | 149.8 | 144.6 | 193.8
2416 | 2230 | 166.6 | 179 | 185.1 | 182.2 | 180.4 | 149.5 | 144.6 | 193.6
2417 | 2231 | 166.5 | 178.7 | 184.8 | 181.8 | 180 | 149.4 | 144.4 | 193.4
2418 | 2232 | 166.4 | 178.4 | 184.5 | 181.5 | 179.4 | 149.1 | 144.1 | 193.1
2419 | 2233 | 166.2 | 178.1 | 184.2 | 181.2 | 178.8 | 148.9 | 143.9 | 192.9
2420 | 2234 | 166 | 177.8 | 183.9 | 180.9 | 178.6 | 148.6 | 143.7 | 192.7
2421 | 2235 | 165.8 | 177.5 | 183.6 | 180.6 | 177.9 | 148.3 | 143.3 | 192.5
2422 | 2236 | 165.6 | 177.2 | 183.3 | 180.3 | 177.8 | 148.1 | 143.2 | 192.3
2423 | 2237 | 165.3 | 176.9 | 182.9 | 180 | 177.5 | 147.8 | 142.9 | 192
2424 | 2238 | 165.2 | 176.6 | 182.6 | 179.7 | 177.1 | 147.7 | 142.8 | 191.9
2425 | 2239 | 164.9 | 176.3 | 182.3 | 179.3 | 176.9 | 147.6 | 142.7 | 191.6
2426 | 2240 | 164.8 | 176 | 182 | 179 | 176.6 | 147.4 | 142.7 | 191.4
2427 | 2241 | 164.5 | 175.7 | 181.7 | 178.6 | 176.3 | 147.2 | 142.6 | 191.2
2428 | 2242 | 164.3 | 175.4 | 181.4 | 178.3 | 176.1 | 147 | 142.4 | 191
2429 | 2243 | 164.2 | 175.1 | 181.1 | 178 | 175.7 | 146.8 | 142.3 | 190.8
2430 | 2244 | 163.9 | 174.8 | 180.8 | 177.7 | 175.3 | 146.7 | 142.1 | 190.5
2431 | 2245 | 163.7 | 174.4 | 180.6 | 177.4 | 174.7 | 146.5 | 141.8 | 190.3
2432 | 2246 | 163.5 | 174.1 | 180.3 | 177.1 | 174.4 | 146.3 | 141.4 | 190.1
2433 | 2247 | 163.3 | 173.8 | 180 | 176.8 | 174.4 | 146.1 | 141.1 | 189.8
2434 | 2248 | 163.1 | 173.5 | 179.7 | 176.6 | 174.2 | 145.8 | 140.9 | 189.7
2435 | 2249 | 162.9 | 173.3 | 179.4 | 176.4 | 173.9 | 145.6 | 140.8 | 189.4
2436 | 2250 | 162.6 | 172.9 | 179.1 | 176.1 | 173.7 | 145.3 | 140.7 | 189.2
2437 | 2251 | 162.4 | 172.6 | 178.8 | 175.9 | 173.2 | 145.1 | 140.3 | 189
2438 | 2252 | 162.2 | 172.3 | 178.5 | 175.6 | 172.8 | 144.9 | 139.9 | 188.8
2439 | 2253 | 162 | 172 | 178.2 | 175.4 | 172.3 | 144.7 | 139.6 | 188.5
2440 | 2254 | 161.8 | 171.7 | 177.8 | 175.1 | 171.8 | 144.5 | 139.2 | 188.3
2441 | 2255 | 161.6 | 171.4 | 177.5 | 174.8 | 171.7 | 144.2 | 138.8 | 188.1
2442 | 2256 | 161.4 | 171.1 | 177.2 | 174.5 | 171.6 | 144 | 138.4 | 187.8
2443 | 2257 | 161.1 | 170.8 | 176.9 | 174.3 | 171 | 143.9 | 138 | 187.6
2444 | 2258 | 160.9 | 170.6 | 176.6 | 174 | 170.6 | 143.7 | 137.6 | 187.4
2445 | 2259 | 160.8 | 170.3 | 176.3 | 173.7 | 169.7 | 143.6 | 137.3 | 187.2
2446 | 2260 | 160.6 | 170 | 176 | 173.5 | 169.4 | 143.4 | 137 | 186.9
2447 | 2261 | 160.4 | 169.7 | 175.7 | 173.2 | 169.2 | 143.2 | 136.8 | 186.7
2448 | 2262 | 160.2 | 169.4 | 175.4 | 172.9 | 168.7 | 143.1 | 136.6 | 186.5
2449 | 2263 | 160 | 169.2 | 175.1 | 172.6 | 168.4 | 142.9 | 136.2 | 186.2
2450 | 2264 | 159.8 | 168.9 | 174.8 | 172.3 | 168.2 | 142.7 | 136 | 186
2451 | 2265 | 159.6 | 168.6 | 174.5 | 172 | 168 | 142.6 | 135.8 | 185.8
2452 | 2266 | 159.4 | 168.4 | 174.2 | 171.8 | 167.8 | 142.4 | 135.8 | 185.6
2453 | 2267 | 159.2 | 168.1 | 173.9 | 171.5 | 167.8 | 142.2 | 135.9 | 185.3
2454 | 2268 | 159.1 | 167.8 | 173.6 | 171.2 | 167.9 | 142 | 136 | 185.1
2455 | 2269 | 158.9 | 167.6 | 173.3 | 171 | 167.9 | 141.7 | 135.8 | 184.9
2456 | 2270 | 158.7 | 167.3 | 173.1 | 170.8 | 167.8 | 141.5 | 135.4 | 184.7
2457 | 2271 | 158.5 | 167.1 | 172.8 | 170.6 | 167.4 | 141.2 | 135.3 | 184.4
2458 | 2272 | 158.4 | 166.8 | 172.5 | 170.4 | 167.4 | 140.9 | 135.1 | 184.2
2459 | 2273 | 158.2 | 166.5 | 172.2 | 170.2 | 167.4 | 140.6 | 135 | 184
2460 | 2274 | 158 | 166.3 | 171.9 | 170 | 167.3 | 140.4 | 134.8 | 183.8
2461 | 2275 | 157.9 | 166 | 171.7 | 169.8 | 167.1 | 140.2 | 134.5 | 183.5
2462 | 2276 | 157.7 | 165.8 | 171.4 | 169.6 | 166.7 | 140 | 134.2 | 183.3
2463 | 2277 | 157.6 | 165.5 | 171.1 | 169.4 | 166.3 | 139.8 | 134.1 | 183.1
2464 | 2278 | 157.4 | 165.3 | 170.8 | 169.2 | 165.9 | 139.6 | 133.8 | 182.9
2465 | 2279 | 157.3 | 165 | 170.5 | 169 | 165.6 | 139.4 | 133.5 | 182.6
2466 | 2280 | 157.1 | 164.8 | 170.2 | 168.8 | 165.2 | 139.2 | 132.9 | 182.4
2467 | 2281 | 156.9 | 164.5 | 169.9 | 168.5 | 165.1 | 138.9 | 132.6 | 182.2
2468 | 2282 | 156.7 | 164.3 | 169.6 | 168.3 | 164.9 | 138.7 | 132.1 | 182
2469 | 2283 | 156.5 | 164 | 169.3 | 168 | 164.5 | 138.5 | 132.1 | 181.8
2470 | 2284 | 156.3 | 163.8 | 169 | 167.7 | 163.9 | 138.2 | 132.2 | 181.6
2471 | 2285 | 156 | 163.5 | 168.7 | 167.5 | 163.7 | 138 | 132.3 | 181.4
2472 | 2286 | 155.7 | 163.3 | 168.5 | 167.2 | 163.7 | 137.7 | 132.1 | 181.2
2473 | 2287 | 155.5 | 163 | 168.2 | 166.9 | 163.5 | 137.5 | 132 | 181
2474 | 2288 | 155.3 | 162.8 | 167.9 | 166.6 | 163.5 | 137.2 | 131.9 | 180.8
2475 | 2289 | 155.2 | 162.5 | 167.7 | 166.4 | 163.4 | 137 | 131.6 | 180.6
2476 | 2290 | 155 | 162.3 | 167.4 | 166.1 | 163.3 | 136.8 | 131.7 | 180.4
2477 | 2291 | 154.8 | 162 | 167.1 | 165.8 | 163.5 | 136.6 | 131.5 | 180.2
2478 | 2292 | 154.6 | 161.8 | 166.8 | 165.6 | 163.5 | 136.4 | 131.5 | 180
2479 | 2293 | 154.4 | 161.5 | 166.5 | 165.3 | 163.5 | 136.1 | 131.3 | 179.8
2480 | 2294 | 154.2 | 161.3 | 166.3 | 165 | 163.4 | 135.9 | 131.1 | 179.6
2481 | 2295 | 154 | 161 | 166 | 164.8 | 163.5 | 135.6 | 130.9 | 179.4
2482 | 2296 | 153.7 | 160.8 | 165.8 | 164.5 | 163.4 | 135.4 | 130.7 | 179.2
2483 | 2297 | 153.5 | 160.5 | 165.5 | 164.3 | 163.2 | 135.2 | 130.2 | 179
2484 | 2298 | 153.4 | 160.3 | 165.3 | 164 | 162.7 | 135 | 129.8 | 178.8
2485 | 2299 | 153.2 | 160.1 | 165 | 163.8 | 162.6 | 134.9 | 129.5 | 178.5
2486 | 2300 | 153 | 159.8 | 164.8 | 163.6 | 162.4 | 134.8 | 129.3 | 178.3
2487 | 2301 | 152.8 | 159.6 | 164.5 | 163.3 | 162 | 134.7 | 129 | 178.2
2488 | 2302 | 152.6 | 159.3 | 164.3 | 163.1 | 161.6 | 134.5 | 128.7 | 177.9
2489 | 2303 | 152.4 | 159.1 | 164 | 162.8 | 161.1 | 134.4 | 128.7 | 177.7
2490 | 2304 | 152.2 | 158.9 | 163.8 | 162.6 | 161 | 134.2 | 128.4 | 177.6
2491 | 2305 | 152 | 158.6 | 163.6 | 162.3 | 161 | 134.1 | 128.1 | 177.4
2492.1 | 2306.1 | 151.8 | 158.4 | 163.3 | 162.1 | 160.9 | 133.9 | 128.1 | 177.1
2493.1 | 2307.1 | 151.7 | 158.1 | 163.1 | 161.9 | 160.3 | 133.7 | 128.1 | 176.9
2494.1 | 2308.1 | 151.5 | 157.9 | 162.8 | 161.7 | 160.2 | 133.5 | 128.2 | 176.7
2495.1 | 2309.1 | 151.5 | 157.7 | 162.6 | 161.5 | 160 | 133.4 | 127.9 | 176.5
2496.1 | 2310.1 | 151.4 | 157.5 | 162.3 | 161.3 | 159.9 | 133.2 | 127.7 | 176.3
2497.1 | 2311.1 | 151.3 | 157.2 | 162.1 | 161.1 | 160 | 133.1 | 127.8 | 176.1
2498.1 | 2312.1 | 151.2 | 157 | 161.8 | 160.9 | 160.1 | 132.8 | 127.9 | 175.9
2499.1 | 2313.1 | 151.1 | 156.8 | 161.6 | 160.6 | 159.9 | 132.6 | 127.5 | 175.7
2500.1 | 2314.1 | 150.9 | 156.6 | 161.3 | 160.4 | 159.6 | 132.4 | 127.1 | 175.5
2501.1 | 2315.1 | 150.7 | 156.3 | 161.1 | 160.1 | 159.6 | 132.2 | 127.1 | 175.3
2502.1 | 2316.1 | 150.6 | 156.1 | 160.8 | 159.9 | 159.1 | 132 | 126.7 | 175.1
2503.1 | 2317.1 | 150.5 | 155.9 | 160.6 | 159.6 | 158.3 | 131.8 | 126.4 | 174.9
2504.1 | 2318.1 | 150.3 | 155.7 | 160.3 | 159.4 | 157.8 | 131.7 | 126.1 | 174.7
2505.1 | 2319.1 | 150.1 | 155.5 | 160.1 | 159.1 | 157.3 | 131.4 | 125.9 | 174.5
2506.1 | 2320.1 | 150 | 155.3 | 159.9 | 158.8 | 157.2 | 131.2 | 125.8 | 174.3
2507.1 | 2321.1 | 149.8 | 155.1 | 159.6 | 158.6 | 157.1 | 130.9 | 125.5 | 174.1
2508.1 | 2322.1 | 149.6 | 154.8 | 159.3 | 158.3 | 157 | 130.7 | 125.7 | 173.9
2509.1 | 2323.1 | 149.4 | 154.6 | 159.1 | 158.1 | 156.9 | 130.4 | 125.7 | 173.7
2510.1 | 2324.1 | 149.3 | 154.4 | 158.9 | 157.9 | 157 | 130.2 | 125.6 | 173.5
2511.1 | 2325.1 | 149.1 | 154.2 | 158.7 | 157.7 | 157 | 130 | 125.3 | 173.3
2512.1 | 2326.1 | 148.9 | 154 | 158.5 | 157.5 | 156.9 | 129.8 | 125.1 | 173.2
2513.1 | 2327.1 | 148.7 | 153.8 | 158.2 | 157.4 | 156.7 | 129.5 | 125 | 172.9
2514.1 | 2328.1 | 148.6 | 153.5 | 158 | 157.2 | 156.3 | 129.4 | 124.7 | 172.8
2515.1 | 2329.1 | 148.5 | 153.3 | 157.8 | 157 | 155.9 | 129.2 | 124.6 | 172.6
2516.1 | 2330.1 | 148.3 | 153.1 | 157.6 | 156.8 | 155.6 | 129.1 | 124.5 | 172.4
2517.1 | 2331.1 | 148 | 152.9 | 157.3 | 156.6 | 155 | 128.9 | 124.2 | 172.2
2518.1 | 2332.1 | 147.9 | 152.7 | 157.1 | 156.3 | 154.5 | 128.8 | 123.9 | 172
2519.1 | 2333.1 | 147.7 | 152.4 | 156.8 | 156.1 | 154 | 128.5 | 124 | 171.8
2520.1 | 2334.1 | 147.6 | 152.2 | 156.5 | 155.8 | 153.7 | 128.3 | 124 | 171.6
2521.1 | 2335.1 | 147.5 | 152 | 156.3 | 155.6 | 153.5 | 128.1 | 123.7 | 171.5
2522.1 | 2336.1 | 147.3 | 151.8 | 156.1 | 155.3 | 153.4 | 127.9 | 123.4 | 171.3
2523.1 | 2337.1 | 147.1 | 151.6 | 155.9 | 155.1 | 153.2 | 127.7 | 123.4 | 171
2524.1 | 2338.1 | 146.9 | 151.3 | 155.6 | 154.9 | 153.1 | 127.5 | 123.5 | 170.8
2525.1 | 2339.1 | 146.8 | 151.1 | 155.4 | 154.7 | 153.2 | 127.3 | 123.1 | 170.7
2526.1 | 2340.1 | 146.5 | 150.9 | 155.2 | 154.5 | 153.4 | 127 | 122.9 | 170.5
2527.1 | 2341.1 | 146.3 | 150.7 | 155 | 154.3 | 153.5 | 126.8 | 122.8 | 170.3
2528.1 | 2342.1 | 146.1 | 150.5 | 154.8 | 154.1 | 153.5 | 126.6 | 122.6 | 170.1
2529.1 | 2343.1 | 145.9 | 150.3 | 154.6 | 153.9 | 153.2 | 126.4 | 122.6 | 170
2530.1 | 2344.1 | 145.7 | 150.1 | 154.3 | 153.8 | 152.9 | 126.2 | 122.3 | 169.8
2531.1 | 2345.1 | 145.5 | 149.9 | 154.1 | 153.6 | 152.5 | 126 | 122.2 | 169.6
2532.1 | 2346.1 | 145.3 | 149.7 | 153.9 | 153.5 | 152.3 | 125.8 | 121.9 | 169.4
2533.1 | 2347.1 | 145.2 | 149.5 | 153.8 | 153.3 | 152 | 125.6 | 121.7 | 169.2
2534.1 | 2348.1 | 145.1 | 149.3 | 153.5 | 153.1 | 151.8 | 125.4 | 121.3 | 169.1
2535.1 | 2349.1 | 144.9 | 149 | 153.3 | 152.9 | 151.6 | 125.2 | 121.2 | 168.9
2536.1 | 2350.1 | 144.8 | 148.8 | 153.1 | 152.7 | 151.4 | 125 | 121 | 168.7
2537.1 | 2351.1 | 144.7 | 148.6 | 152.9 | 152.5 | 151 | 124.9 | 121 | 168.6
2538.1 | 2352.1 | 144.6 | 148.4 | 152.7 | 152.3 | 150.7 | 124.7 | 120.9 | 168.4
2539.1 | 2353.1 | 144.4 | 148.2 | 152.5 | 152.1 | 150.6 | 124.5 | 120.8 | 168.2
2540.1 | 2354.1 | 144.3 | 148 | 152.2 | 151.9 | 150.4 | 124.3 | 120.6 | 168
2541.1 | 2355.1 | 144.1 | 147.8 | 152 | 151.7 | 150 | 124.2 | 120.5 | 167.8
2542.1 | 2356.1 | 144 | 147.5 | 151.8 | 151.5 | 149.8 | 124.1 | 120.3 | 167.6
2543.1 | 2357.1 | 143.8 | 147.3 | 151.6 | 151.3 | 149.6 | 123.9 | 120.3 | 167.4
2544.1 | 2358.1 | 143.7 | 147.1 | 151.4 | 151.1 | 149.6 | 123.7 | 120.1 | 167.2
2545.1 | 2359.1 | 143.5 | 146.9 | 151.1 | 151 | 149.6 | 123.5 | 120.1 | 167
2546.1 | 2360.1 | 143.3 | 146.7 | 151 | 150.8 | 149.5 | 123.3 | 120.1 | 166.9
2547.1 | 2361.1 | 143.2 | 146.5 | 150.7 | 150.7 | 149.5 | 123.2 | 120.1 | 166.7
2548.1 | 2362.1 | 143.1 | 146.3 | 150.5 | 150.6 | 149.4 | 123 | 120 | 166.5
2549.1 | 2363.1 | 143 | 146.1 | 150.3 | 150.5 | 149.4 | 122.8 | 119.9 | 166.3
2550.1 | 2364.1 | 142.8 | 145.9 | 150.1 | 150.3 | 149.5 | 122.7 | 119.6 | 166.1
2551.1 | 2365.1 | 142.6 | 145.6 | 149.9 | 150.2 | 149.5 | 122.5 | 119.4 | 165.9
2552.1 | 2366.1 | 142.5 | 145.4 | 149.6 | 150.1 | 149.2 | 122.3 | 119.2 | 165.8
2553.1 | 2367.1 | 142.4 | 145.2 | 149.4 | 149.9 | 148.8 | 122.1 | 119.1 | 165.6
2554.1 | 2368.1 | 142.2 | 145 | 149.2 | 149.7 | 148.7 | 121.9 | 118.9 | 165.4
2555.1 | 2369.1 | 142.1 | 144.8 | 149 | 149.5 | 148.4 | 121.7 | 118.8 | 165.2
2556.1 | 2370.1 | 141.9 | 144.6 | 148.8 | 149.3 | 148.1 | 121.5 | 118.6 | 165
2557.1 | 2371.1 | 141.7 | 144.4 | 148.6 | 149.1 | 147.7 | 121.4 | 118.3 | 164.9
2558.1 | 2372.1 | 141.5 | 144.2 | 148.4 | 148.8 | 147.3 | 121.3 | 118.1 | 164.7
2559.1 | 2373.1 | 141.3 | 144 | 148.1 | 148.6 | 146.9 | 121.2 | 117.7 | 164.5
2560.1 | 2374.1 | 141.1 | 143.8 | 147.9 | 148.4 | 146.6 | 121.1 | 117.3 | 164.3
2561.1 | 2375.1 | 140.9 | 143.7 | 147.8 | 148.1 | 146.5 | 121 | 117 | 164.1
2562.1 | 2376.1 | 140.8 | 143.5 | 147.6 | 147.9 | 146.1 | 120.9 | 116.5 | 163.9
2563.1 | 2377.1 | 140.6 | 143.3 | 147.4 | 147.7 | 145.9 | 120.8 | 116.4 | 163.7
2564.1 | 2378.1 | 140.4 | 143.1 | 147.2 | 147.5 | 145.5 | 120.7 | 116.3 | 163.5
2565.1 | 2379.1 | 140.2 | 142.9 | 147 | 147.3 | 145 | 120.6 | 116.1 | 163.3
2566.1 | 2380.1 | 140 | 142.7 | 146.8 | 147.2 | 144.8 | 120.5 | 116.1 | 163.2
2567.1 | 2381.1 | 139.8 | 142.5 | 146.5 | 147 | 144.6 | 120.3 | 116 | 163
2568.1 | 2382.1 | 139.6 | 142.3 | 146.4 | 146.8 | 144.1 | 120.1 | 115.7 | 162.8
2569.1 | 2383.1 | 139.5 | 142.2 | 146.2 | 146.6 | 143.8 | 119.9 | 115.6 | 162.6
2570.1 | 2384.1 | 139.3 | 142 | 146 | 146.4 | 143.8 | 119.7 | 115.3 | 162.4
2571.1 | 2385.1 | 139.2 | 141.8 | 145.8 | 146.3 | 143.8 | 119.5 | 115 | 162.2
2572.1 | 2386.1 | 139 | 141.6 | 145.5 | 146.1 | 143.8 | 119.3 | 114.8 | 162
2573.1 | 2387.1 | 138.8 | 141.4 | 145.3 | 146 | 143.8 | 119.1 | 114.9 | 161.8
2574.1 | 2388.1 | 138.7 | 141.3 | 145.1 | 145.9 | 143.8 | 118.9 | 114.9 | 161.7
2575.1 | 2389.1 | 138.6 | 141.1 | 144.9 | 145.8 | 143.8 | 118.7 | 114.9 | 161.5
2576.1 | 2390.1 | 138.4 | 140.9 | 144.7 | 145.8 | 143.8 | 118.5 | 114.8 | 161.3
2577.1 | 2391.1 | 138.3 | 140.8 | 144.5 | 145.7 | 143.8 | 118.3 | 114.9 | 161.1
2578.1 | 2392.1 | 138.1 | 140.6 | 144.3 | 145.6 | 143.8 | 118.1 | 114.9 | 160.9
2579.1 | 2393.1 | 137.9 | 140.4 | 144.1 | 145.5 | 143.7 | 117.9 | 114.7 | 160.7
2580.1 | 2394.1 | 137.7 | 140.2 | 143.9 | 145.4 | 143.6 | 117.7 | 114.8 | 160.5
2581.1 | 2395.1 | 137.6 | 140.1 | 143.8 | 145.3 | 143.5 | 117.5 | 114.8 | 160.3
2582.1 | 2396.1 | 137.4 | 139.9 | 143.6 | 145.2 | 143.4 | 117.3 | 114.8 | 160.1
2583.1 | 2397.1 | 137.3 | 139.7 | 143.4 | 145.1 | 143.4 | 117.1 | 115 | 159.9
2584.1 | 2398.1 | 137.1 | 139.6 | 143.2 | 145 | 143.4 | 116.9 | 115.1 | 159.7
2585.1 | 2399.1 | 137 | 139.4 | 143.1 | 144.9 | 143.4 | 116.6 | 115.2 | 159.6
2586.1 | 2400.1 | 136.9 | 139.3 | 142.9 | 144.9 | 143.4 | 116.4 | 115.2 | 159.4
2587.1 | 2401.1 | 136.8 | 139.1 | 142.7 | 144.8 | 143.3 | 116.2 | 115.3 | 159.2
2588.1 | 2402.1 | 136.7 | 138.9 | 142.5 | 144.7 | 143.3 | 116 | 115.4 | 159
2589.1 | 2403.1 | 136.6 | 138.8 | 142.4 | 144.6 | 143.2 | 115.8 | 115.4 | 158.8
2590.1 | 2404.1 | 136.5 | 138.6 | 142.2 | 144.5 | 143.2 | 115.6 | 115.4 | 158.6
2591.1 | 2405.1 | 136.4 | 138.5 | 142 | 144.4 | 143.2 | 115.5 | 115.5 | 158.4
2592.1 | 2406.1 | 136.2 | 138.3 | 141.9 | 144.3 | 143.2 | 115.3 | 115.6 | 158.3
2593.1 | 2407.1 | 136 | 138.1 | 141.7 | 144.2 | 143.2 | 115.2 | 115.7 | 158
2594.1 | 2408.1 | 135.9 | 138 | 141.5 | 144.1 | 143.2 | 115 | 115.6 | 157.8
2595.1 | 2409.1 | 135.8 | 137.8 | 141.4 | 144.1 | 143.1 | 114.8 | 115.5 | 157.7
2596.1 | 2410.1 | 135.7 | 137.7 | 141.2 | 144 | 143.1 | 114.7 | 115.4 | 157.5
2597.1 | 2411.1 | 135.6 | 137.5 | 141 | 143.9 | 143 | 114.5 | 115.4 | 157.3
2598.1 | 2412.1 | 135.5 | 137.4 | 140.9 | 143.7 | 142.9 | 114.3 | 115.2 | 157.1
2599.1 | 2413.1 | 135.3 | 137.2 | 140.7 | 143.6 | 142.9 | 114.1 | 115.2 | 156.9
2600.1 | 2414.1 | 135.2 | 137.1 | 140.6 | 143.5 | 142.8 | 113.8 | 115.2 | 156.7
2601.1 | 2415.1 | 135.1 | 136.9 | 140.5 | 143.3 | 142.7 | 113.6 | 115.1 | 156.5
2602.1 | 2416.1 | 134.9 | 136.8 | 140.3 | 143.2 | 142.7 | 113.4 | 114.9 | 156.4
2603.1 | 2417.1 | 134.7 | 136.6 | 140.2 | 143 | 142.6 | 113.2 | 114.8 | 156.2
2604.1 | 2418.1 | 134.5 | 136.5 | 140 | 142.9 | 142.5 | 113 | 114.6 | 156
2605.1 | 2419.1 | 134.4 | 136.3 | 139.9 | 142.7 | 142.4 | 112.9 | 114.4 | 155.8
2606.1 | 2420.1 | 134.3 | 136.2 | 139.7 | 142.5 | 142.3 | 112.7 | 114.2 | 155.6
2607.1 | 2421.1 | 134.1 | 136 | 139.6 | 142.4 | 142.2 | 112.6 | 114.1 | 155.5
2608.1 | 2422.1 | 133.9 | 135.8 | 139.4 | 142.2 | 142.1 | 112.4 | 114 | 155.3
2609.1 | 2423.1 | 133.8 | 135.7 | 139.3 | 142 | 141.9 | 112.2 | 113.9 | 155.1
2610.1 | 2424.1 | 133.7 | 135.5 | 139.1 | 141.8 | 141.5 | 112 | 113.8 | 154.9
2611.1 | 2425.1 | 133.5 | 135.4 | 139 | 141.6 | 141.3 | 111.9 | 113.6 | 154.7
2612.1 | 2426.1 | 133.4 | 135.2 | 138.8 | 141.4 | 141.2 | 111.7 | 113.4 | 154.6
2613.1 | 2427.1 | 133.3 | 135 | 138.7 | 141.2 | 141.1 | 111.6 | 113.3 | 154.4
2614.1 | 2428.1 | 133.1 | 134.9 | 138.5 | 141 | 141 | 111.5 | 113.2 | 154.2
2615.1 | 2429.1 | 133 | 134.7 | 138.4 | 140.8 | 140.9 | 111.3 | 113 | 154.1
2616.1 | 2430.1 | 132.8 | 134.5 | 138.2 | 140.6 | 140.7 | 111.2 | 112.8 | 153.9
2617.1 | 2431.1 | 132.6 | 134.3 | 138 | 140.4 | 140.6 | 111 | 112.6 | 153.8
2618.1 | 2432.1 | 132.4 | 134.1 | 137.9 | 140.3 | 140.5 | 110.9 | 112.5 | 153.6
2619.1 | 2433.1 | 132.2 | 134 | 137.7 | 140.1 | 140.3 | 110.7 | 112.3 | 153.4
2620.1 | 2434.1 | 132.1 | 133.8 | 137.6 | 139.9 | 140.1 | 110.6 | 112 | 153.3
2621.1 | 2435.1 | 131.9 | 133.6 | 137.4 | 139.6 | 140 | 110.5 | 111.9 | 153.1
2622.1 | 2436.1 | 131.8 | 133.4 | 137.2 | 139.4 | 139.8 | 110.4 | 111.8 | 152.9
2623.1 | 2437.1 | 131.6 | 133.3 | 137 | 139.2 | 139.5 | 110.2 | 111.6 | 152.8
2624.1 | 2438.1 | 131.4 | 133.1 | 136.8 | 139 | 139.2 | 110.1 | 111.2 | 152.7
2625.1 | 2439.1 | 131.2 | 132.9 | 136.7 | 138.7 | 138.8 | 110 | 111 | 152.5
2626.1 | 2440.1 | 131 | 132.7 | 136.5 | 138.5 | 138.6 | 109.8 | 110.9 | 152.3
2627.1 | 2441.1 | 130.9 | 132.5 | 136.4 | 138.2 | 138.3 | 109.7 | 110.7 | 152.2
2628.1 | 2442.1 | 130.8 | 132.4 | 136.2 | 138 | 137.8 | 109.6 | 110.5 | 152
2629.1 | 2443.1 | 130.6 | 132.2 | 136 | 137.7 | 137.5 | 109.6 | 110.1 | 151.9
2630.1 | 2444.1 | 130.5 | 132 | 135.9 | 137.5 | 137.4 | 109.4 | 109.8 | 151.7
2631.1 | 2445.1 | 130.3 | 131.9 | 135.7 | 137.2 | 137.2 | 109.3 | 109.8 | 151.6
2632.1 | 2446.1 | 130.2 | 131.7 | 135.5 | 137 | 137.2 | 109.2 | 109.7 | 151.4
2633.1 | 2447.1 | 130 | 131.6 | 135.4 | 136.7 | 137.1 | 109.1 | 109.7 | 151.2
2634.1 | 2448.1 | 129.9 | 131.4 | 135.2 | 136.5 | 137.1 | 109 | 109.4 | 151.1
2635.1 | 2449.1 | 129.7 | 131.2 | 135.1 | 136.4 | 137 | 108.8 | 109.3 | 150.9
2636.1 | 2450.1 | 129.6 | 131.1 | 134.9 | 136.2 | 136.7 | 108.7 | 109.2 | 150.7
2637.1 | 2451.1 | 129.4 | 130.9 | 134.8 | 136.1 | 136.6 | 108.4 | 109.1 | 150.5
2638.1 | 2452.1 | 129.2 | 130.7 | 134.6 | 136 | 136.6 | 108.2 | 109.2 | 150.4
2639.1 | 2453.1 | 129 | 130.6 | 134.4 | 135.8 | 136.5 | 107.9 | 109.2 | 150.2
2640.1 | 2454.1 | 128.9 | 130.4 | 134.3 | 135.7 | 136.5 | 107.8 | 109.2 | 150
2641.1 | 2455.1 | 128.8 | 130.3 | 134.1 | 135.5 | 136.4 | 107.7 | 109.1 | 149.9
2642.1 | 2456.1 | 128.7 | 130.1 | 134 | 135.4 | 136.3 | 107.6 | 109 | 149.7
2643.1 | 2457.1 | 128.6 | 130 | 133.8 | 135.3 | 136.3 | 107.5 | 108.9 | 149.5

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 35 |  |  | 2006-08-14 | 12:49
38943.5322 | 1 | 0 | 1 | XLPE&PE | 7-C | Tray
38943.5343 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38943.5364 | 1 | 0 | 1
38943.5386 | 1 | 0 | 1
38943.5407 | 2 | 0 | 1
38943.5428 | 2 | 0 | 1
38943.545 | 3 | 0 | 1
38943.5471 | 4 | 0 | 1
38943.5493 | 26 | 22 | 1
38943.5514 | 1147 | 1116 | 1
38943.5535 | 1248 | 1142 | 1
38943.5557 | 1235 | 1158 | 1
38943.5578 | 1053 | 821 | 1
38943.56 | 1110 | 833 | 1
38943.5621 | 1107 | 964 | 1
1
38943.5322 | 1 | 0 | 2
38943.5343 | 1 | 0 | 2
38943.5364 | 1 | 0 | 2
38943.5386 | 1 | 0 | 2
38943.5407 | 2 | 0 | 2
38943.5429 | 2 | 0 | 2
38943.545 | 4 | 0 | 2
38943.5471 | 3 | 0 | 2
38943.5493 | 36 | 31 | 2
38943.5514 | 1073 | 1039 | 2
38943.5536 | 1009 | 906 | 2
38943.5557 | 1233 | 1117 | 2
38943.5578 | 1344 | 1055 | 2
38943.56 | 1043 | 827 | 2
38943.5621 | 1296 | 1062 | 2
2
38943.5322 | 1 | 0 | 3
38943.5343 | 1 | 0 | 3
38943.5365 | 1 | 0 | 3
38943.5386 | 1 | 0 | 3
38943.5407 | 3 | 0 | 3
38943.5429 | 1 | 0 | 3
38943.545 | 3 | 0 | 3
38943.5472 | 4 | 0 | 3
38943.5493 | 3 | 0 | 3
38943.5514 | 4 | 9 | 3
38943.5536 | 37 | 8 | 3
38943.5557 | 32 | 8 | 3
38943.5578 | 132 | 6 | 3
38943.56 | 296 | 6 | 3
38943.5621 | 123 | 8 | 3
3
38943.5322 | 1 | 0 | 4
38943.5343 | 1 | 0 | 4
38943.5365 | 1 | 0 | 4
38943.5386 | 1 | 1 | 4
38943.5408 | 2 | 0 | 4
38943.5429 | 1 | 0 | 4
38943.545 | 3 | 0 | 4
38943.5472 | 3 | 0 | 4
38943.5493 | 3 | 0 | 4
38943.5514 | 3 | 4 | 4
38943.5536 | 36 | 4 | 4
38943.5557 | 2055 | 4 | 4
38943.5579 | 2042 | 3 | 4
38943.56 | 2346 | 3 | 4
38943.5621 | 2391 | 5 | 4
4
38943.5322 | 1 | 0 | 5
38943.5344 | 1 | 0 | 5
38943.5365 | 1 | 0 | 5
38943.5386 | 1 | 0 | 5
38943.5408 | 2 | 0 | 5
38943.5429 | 2 | 0 | 5
38943.5451 | 3 | 0 | 5
38943.5472 | 2 | 0 | 5
38943.5493 | 3 | 0 | 5
38943.5515 | 4 | 2 | 5
38943.5536 | 56 | 3 | 5
38943.5557 | 54 | 3 | 5
38943.5579 | 122 | 2 | 5
38943.56 | 302 | 2 | 5
38943.5622 | 136 | 3 | 5
5
38943.5322 | 1 | 0 | 6
38943.5344 | 1 | 0 | 6
38943.5365 | 1 | 0 | 6
38943.5387 | 1 | 0 | 6
38943.5408 | 2 | 0 | 6
38943.5429 | 1 | 0 | 6
38943.5451 | 3 | 0 | 6
38943.5472 | 3 | 0 | 6
38943.5494 | 3 | 0 | 6
38943.5515 | 3 | 2 | 6
38943.5536 | 426 | 2 | 6
38943.5558 | 1930 | 1 | 6
38943.5579 | 2421 | 1 | 6
38943.56 | 2317 | 1 | 6
38943.5622 | 2460 | 3 | 6
6
38943.5323 | 1 | 0 | 7
38943.5344 | 1 | 0 | 7
38943.5365 | 1 | 0 | 7
38943.5387 | 1 | 0 | 7
38943.5408 | 2 | 0 | 7
38943.543 | 1 | 0 | 7
38943.5451 | 3 | 0 | 7
38943.5472 | 3 | 0 | 7
38943.5494 | 2 | 0 | 7
38943.5515 | 3 | 2 | 7
38943.5536 | 46 | 1 | 7
38943.5558 | 85 | 1 | 7
38943.5579 | 139 | 1 | 7
38943.5601 | 963 | 1 | 7
38943.5622 | 172 | 2 | 7
7
38943.5323 | 1 | 0 | 8
38943.5344 | 1 | 0 | 8
38943.5366 | 1 | 0 | 8
38943.5387 | 1 | 0 | 8
38943.5408 | 2 | 0 | 8
38943.543 | 2 | 0 | 8
38943.5451 | 2 | 0 | 8
38943.5472 | 2 | 1 | 8
38943.5494 | 2 | 0 | 8
38943.5515 | 3 | 1 | 8
38943.5537 | 39 | 1 | 8
38943.5558 | 68 | 1 | 8
38943.5579 | 285 | 1 | 8
38943.5601 | 245 | 1 | 8
38943.5622 | 134 | 2 | 8
8
38943.5323 | 1 | 0 | 9
38943.5344 | 1 | 0 | 9
38943.5366 | 1 | 0 | 9
38943.5387 | 1 | 0 | 9
38943.5408 | 2 | 0 | 9
38943.543 | 1 | 0 | 9
38943.5451 | 2 | 0 | 9
38943.5473 | 2 | 0 | 9
38943.5494 | 2 | 0 | 9
38943.5515 | 3 | 1 | 9
38943.5537 | 41 | 1 | 9
38943.5558 | 93 | 0 | 9
38943.558 | 152 | 1 | 9
38943.5601 | 229 | 0 | 9
38943.5622 | 162 | 1 | 9
9
38943.5323 | 1 | 0 | 10
38943.5344 | 1 | 0 | 10
38943.5366 | 1 | 0 | 10
38943.5387 | 1 | 0 | 10
38943.5409 | 1 | 0 | 10
38943.543 | 1 | 0 | 10
38943.5451 | 3 | 0 | 10
38943.5473 | 2 | 0 | 10
38943.5494 | 2 | 0 | 10
38943.5516 | 3 | 1 | 10
38943.5537 | 3 | 0 | 10
38943.5558 | 392 | 1 | 10
38943.558 | 219 | 1 | 10
38943.5601 | 266 | 1 | 10
38943.5622 | 111 | 1 | 10
10
38943.5323 | 1 | 0 | 11
38943.5345 | 1 | 0 | 11
38943.5366 | 1 | 0 | 11
38943.5387 | 1 | 0 | 11
38943.5409 | 1 | 0 | 11
38943.543 | 1 | 0 | 11
38943.5452 | 2 | 0 | 11
38943.5473 | 2 | 0 | 11
38943.5494 | 2 | 0 | 11
38943.5516 | 2 | 1 | 11
38943.5537 | 42 | 0 | 11
38943.5558 | 106 | 0 | 11
38943.558 | 130 | 0 | 11
38943.5601 | 655 | 0 | 11
38943.5623 | 143 | 1 | 11
11
38943.5323 | 1 | 0 | 12
38943.5345 | 1 | 0 | 12
38943.5366 | 1 | 0 | 12
38943.5387 | 1 | 0 | 12
38943.5409 | 2 | 0 | 12
38943.543 | 1 | 0 | 12
38943.5452 | 3 | 0 | 12
38943.5473 | 2 | 0 | 12
38943.5494 | 2 | 0 | 12
38943.5516 | 2 | 0 | 12
38943.5537 | 1811 | 1 | 12
38943.5559 | 2363 | 0 | 12
38943.558 | 2206 | 0 | 12
38943.5601 | 1581 | 1 | 12
38943.5623 | 1967 | 0 | 12
12
38943.5323 | 1 | 0 | 13
38943.5345 | 1 | 0 | 13
38943.5388 | 1 | 0 | 13
38943.5409 | 2 | 0 | 13
38943.543 | 1 | 0 | 13
38943.5452 | 2 | 0 | 13
38943.5473 | 2 | 0 | 13
38943.5495 | 2 | 0 | 13
38943.5516 | 2 | 0 | 13
38943.5537 | 33 | 0 | 13
38943.5559 | 367 | 0 | 13
38943.558 | 153 | 0 | 13
38943.5602 | 1215 | 0 | 13
38943.5623 | 158 | 1 | 13
13
38943.5324 | 1 | 0 | 14
38943.5345 | 1 | 0 | 14
38943.5366 | 1 | 0 | 14
38943.5388 | 1 | 0 | 14
38943.5409 | 1 | 0 | 14
38943.5431 | 1 | 0 | 14
38943.5452 | 2 | 0 | 14
38943.5473 | 2 | 0 | 14
38943.5495 | 2 | 0 | 14
38943.5516 | 2 | 0 | 14
38943.5537 | 2127 | 0 | 14
38943.5559 | 2041 | 0 | 14
38943.558 | 2268 | 0 | 14
38943.5602 | 1385 | 0 | 14
38943.5623 | 1116 | 0 | 14
14
38943.5324 | 1 | 0 | 15
38943.5345 | 1 | 0 | 15
38943.5367 | 1 | 0 | 15
38943.5388 | 1 | 0 | 15
38943.5409 | 2 | 0 | 15
38943.5431 | 1 | 0 | 15
38943.5452 | 2 | 0 | 15
38943.5473 | 2 | 0 | 15
38943.5495 | 2 | 0 | 15
38943.5516 | 2 | 0 | 15
38943.5538 | 41 | 0 | 15
38943.5559 | 126 | 0 | 15
38943.558 | 175 | 0 | 15
38943.5602 | 123 | 0 | 15
38943.5623 | 173 | 0 | 15
15
38943.5324 | 1 | 0 | 16
38943.5345 | 1 | 0 | 16
38943.5367 | 1 | 0 | 16
38943.5388 | 1 | 0 | 16
38943.5409 | 2141 | 0 | 16
38943.5431 | 1929 | 0 | 16
38943.5452 | 2177 | 0 | 16
38943.5474 | 2082 | 0 | 16
38943.5495 | 2139 | 0 | 16
38943.5516 | 2482 | 0 | 16
38943.5538 | 2161 | 0 | 16
38943.5559 | 2355 | 0 | 16
38943.5581 | 2187 | 0 | 16
38943.5602 | 2015 | 0 | 16
38943.5623 | 2411 | 0 | 16
16
38943.5324 | 1 | 0 | 17
38943.5346 | 1 | 0 | 17
38943.5367 | 1 | 0 | 17
38943.5388 | 1 | 0 | 17
38943.541 | 4 | 0 | 17
38943.5431 | 3 | 0 | 17
38943.5452 | 4 | 0 | 17
38943.5474 | 4 | 0 | 17
38943.5495 | 4 | 0 | 17
38943.5517 | 4 | 1 | 17
38943.5538 | 37 | 0 | 17
38943.5559 | 165 | 0 | 17
38943.5581 | 150 | 0 | 17
38943.5602 | 126 | 0 | 17
38943.5624 | 155 | 0 | 17
17
38943.5324 | 1 | 0 | 18
38943.5346 | 1 | 0 | 18
38943.5367 | 1 | 0 | 18
38943.5388 | 1 | 0 | 18
38943.541 | 4 | 0 | 18
38943.5431 | 1790 | 0 | 18
38943.5453 | 2531 | 0 | 18
38943.5474 | 2309 | 0 | 18
38943.5495 | 2003 | 0 | 18
38943.5517 | 2223 | 0 | 18
38943.5538 | 2195 | 0 | 18
38943.556 | 2299 | 0 | 18
38943.5581 | 2460 | 0 | 18
38943.5602 | 2418 | 0 | 18
38943.5624 | 2037 | 0 | 18
18
38943.5325 | 1 | 0 | 19
38943.5346 | 1 | 0 | 19
38943.5367 | 1 | 0 | 19
38943.5389 | 1 | 0 | 19
38943.541 | 2 | 0 | 19
38943.5431 | 4 | 0 | 19
38943.5453 | 4 | 0 | 19
38943.5474 | 4 | 0 | 19
38943.5496 | 3 | 0 | 19
38943.5517 | 4 | 0 | 19
38943.5538 | 38 | 0 | 19
38943.556 | 206 | 0 | 19
38943.5581 | 185 | 0 | 19
38943.5603 | 121 | 0 | 19
38943.5624 | 115 | 0 | 19
19
38943.5325 | 1 | 0 | 20
38943.5346 | 1 | 0 | 20
38943.5367 | 1 | 0 | 20
38943.5389 | 1 | 0 | 20
38943.541 | 2 | 0 | 20
38943.5432 | 2 | 0 | 20
38943.5453 | 3 | 0 | 20
38943.5474 | 3 | 0 | 20
38943.5496 | 3 | 0 | 20
38943.5517 | 3 | 0 | 20
38943.5539 | 1966 | 0 | 20
38943.556 | 2408 | 0 | 20
38943.5581 | 2508 | 0 | 20
38943.5603 | 2218 | 0 | 20
38943.5624 | 1114 | 0 | 20
20
38943.5325 | 1 | 0 | 21
38943.5346 | 1 | 0 | 21
38943.5368 | 1 | 0 | 21
38943.5389 | 1 | 0 | 21
38943.541 | 2 | 0 | 21
38943.5432 | 2 | 0 | 21
38943.5453 | 3 | 0 | 21
38943.5475 | 3 | 0 | 21
38943.5496 | 3 | 0 | 21
38943.5517 | 3 | 0 | 21
38943.5539 | 52 | 0 | 21
38943.556 | 201 | 0 | 21
38943.5581 | 81 | 0 | 21
38943.5603 | 134 | 0 | 21
38943.5624 | 126 | 0 | 21
21
38943.5325 | 1 | 0 | 22
38943.5346 | 1 | 0 | 22
38943.5368 | 1 | 0 | 22
38943.5389 | 1 | 0 | 22
38943.5411 | 2 | 0 | 22
38943.5432 | 2 | 0 | 22
38943.5453 | 2 | 0 | 22
38943.5475 | 2 | 0 | 22
38943.5496 | 3 | 0 | 22
38943.5517 | 2 | 0 | 22
38943.5539 | 2285 | 0 | 22
38943.556 | 1977 | 0 | 22
38943.5582 | 2507 | 0 | 22
38943.5603 | 2241 | 0 | 22
38943.5624 | 1654 | 0 | 22
22
38943.5325 | 1 | 0 | 23
38943.5347 | 1 | 0 | 23
38943.5368 | 1 | 0 | 23
38943.5389 | 1 | 0 | 23
38943.5411 | 2 | 0 | 23
38943.5432 | 2 | 0 | 23
38943.5453 | 2 | 0 | 23
38943.5475 | 3 | 0 | 23
38943.5496 | 2 | 0 | 23
38943.5518 | 3 | 0 | 23
38943.5539 | 84 | 1 | 23
38943.556 | 187 | 0 | 23
38943.5582 | 72 | 0 | 23
38943.5603 | 137 | 0 | 23
38943.5625 | 128 | 0 | 23
23
38943.5325 | 1 | 0 | 24
38943.5347 | 1 | 0 | 24
38943.5368 | 1 | 0 | 24
38943.5389 | 1 | 0 | 24
38943.5411 | 2 | 0 | 24
38943.5432 | 2 | 0 | 24
38943.5454 | 2 | 0 | 24
38943.5475 | 2 | 0 | 24
38943.5496 | 2 | 0 | 24
38943.5518 | 2 | 0 | 24
38943.5539 | 660 | 0 | 24
38943.5561 | 2110 | 0 | 24
38943.5582 | 2542 | 1 | 24
38943.5603 | 2250 | 0 | 24
38943.5625 | 2338 | 1 | 24
24
38943.5325 | 1 | 0 | 25
38943.5347 | 1 | 0 | 25
38943.5368 | 1 | 0 | 25
38943.539 | 1 | 0 | 25
38943.5411 | 2 | 0 | 25
38943.5432 | 1 | 0 | 25
38943.5454 | 2 | 0 | 25
38943.5475 | 2 | 0 | 25
38943.5497 | 2 | 0 | 25
38943.5518 | 2 | 0 | 25
38943.5539 | 103 | 14 | 25
38943.5561 | 217 | 0 | 25
38943.5582 | 1205 | 0 | 25
38943.5603 | 143 | 0 | 25
38943.5625 | 128 | 0 | 25
25
38943.5326 | 1 | 0 | 26
38943.5347 | 1 | 0 | 26
38943.5368 | 1 | 0 | 26
38943.539 | 1 | 0 | 26
38943.5411 | 1 | 0 | 26
38943.5433 | 2 | 0 | 26
38943.5454 | 2 | 0 | 26
38943.5475 | 2 | 0 | 26
38943.5497 | 2 | 0 | 26
38943.5518 | 2 | 0 | 26
38943.5539 | 149 | 43 | 26
38943.5561 | 222 | 0 | 26
38943.5582 | 298 | 0 | 26
38943.5604 | 164 | 0 | 26
38943.5625 | 156 | 0 | 26
26
38943.5326 | 1 | 0 | 27
38943.5347 | 1 | 0 | 27
38943.5369 | 1 | 0 | 27
38943.539 | 1 | 0 | 27
38943.5411 | 2 | 0 | 27
38943.5433 | 1 | 0 | 27
38943.5454 | 2 | 0 | 27
38943.5475 | 2 | 0 | 27
38943.5497 | 2 | 0 | 27
38943.5518 | 2 | 0 | 27
38943.554 | 68 | 0 | 27
38943.5561 | 261 | 0 | 27
38943.5582 | 282 | 0 | 27
38943.5604 | 193 | 0 | 27
38943.5625 | 191 | 0 | 27
27
38943.5326 | 1 | 0 | 28
38943.5347 | 1 | 0 | 28
38943.5369 | 1 | 0 | 28
38943.539 | 1 | 0 | 28
38943.5411 | 1 | 0 | 28
38943.5433 | 1 | 0 | 28
38943.5454 | 2 | 0 | 28
38943.5476 | 2 | 0 | 28
38943.5497 | 2 | 0 | 28
38943.5518 | 2 | 0 | 28
38943.554 | 84 | 0 | 28
38943.5561 | 178 | 0 | 28
38943.5583 | 220 | 0 | 28
38943.5604 | 266 | 1 | 28
38943.5625 | 121 | 0 | 28
28
38943.5326 | 1 | 0 | 29
38943.5347 | 1 | 0 | 29
38943.5369 | 1 | 0 | 29
38943.539 | 1 | 0 | 29
38943.5412 | 2 | 0 | 29
38943.5433 | 1 | 0 | 29
38943.5454 | 2 | 0 | 29
38943.5476 | 2 | 0 | 29
38943.5497 | 2 | 0 | 29
38943.5519 | 2 | 0 | 29
38943.554 | 151 | 0 | 29
38943.5561 | 214 | 0 | 29
38943.5583 | 302 | 0 | 29
38943.5604 | 187 | 0 | 29
38943.5625 | 61 | 0 | 29
29
38943.5326 | 1 | 0 | 30
38943.5348 | 1 | 0 | 30
38943.5369 | 1 | 0 | 30
38943.539 | 1 | 0 | 30
38943.5412 | 1 | 0 | 30
38943.5433 | 1 | 0 | 30
38943.5455 | 2 | 0 | 30
38943.5476 | 2 | 0 | 30
38943.5497 | 2 | 0 | 30
38943.5519 | 2 | 0 | 30
38943.554 | 3 | 0 | 30
38943.5561 | 417 | 0 | 30
38943.5583 | 256 | 1 | 30
38943.5604 | 302 | 1 | 30
38943.5626 | 93 | 0 | 30
30
38943.5326 | 1 | 0 | 31
38943.5348 | 1 | 0 | 31
38943.5369 | 1 | 0 | 31
38943.5391 | 1 | 0 | 31
38943.5412 | 2 | 0 | 31
38943.5433 | 2 | 0 | 31
38943.5455 | 2 | 0 | 31
38943.5476 | 2 | 0 | 31
38943.5498 | 2 | 0 | 31
38943.5519 | 2 | 0 | 31
38943.554 | 107 | 0 | 31
38943.5562 | 216 | 0 | 31
38943.5583 | 281 | 0 | 31
38943.5604 | 190 | 0 | 31
38943.5626 | 45 | 0 | 31
31
38943.5327 | 1 | 0 | 32
38943.5348 | 1 | 0 | 32
38943.5369 | 1 | 1 | 32
38943.5391 | 1 | 0 | 32
38943.5412 | 2 | 0 | 32
38943.5434 | 1 | 0 | 32
38943.5455 | 2 | 0 | 32
38943.5476 | 2 | 0 | 32
38943.5498 | 2 | 0 | 32
38943.5519 | 26 | 0 | 32
38943.5541 | 1750 | 0 | 32
38943.5562 | 2048 | 0 | 32
38943.5583 | 2294 | 0 | 32
38943.5605 | 1440 | 0 | 32
38943.5626 | 1155 | 0 | 32
32
38943.5327 | 1 | 0 | 33
38943.5348 | 1 | 0 | 33
38943.537 | 1 | 0 | 33
38943.5391 | 1 | 0 | 33
38943.5412 | 1 | 0 | 33
38943.5434 | 1 | 0 | 33
38943.5455 | 2 | 0 | 33
38943.5477 | 2 | 0 | 33
38943.5498 | 2 | 0 | 33
38943.5519 | 2 | 0 | 33
38943.5541 | 79 | 0 | 33
38943.5562 | 268 | 0 | 33
38943.5583 | 232 | 0 | 33
38943.5605 | 185 | 0 | 33
38943.5626 | 38 | 0 | 33
33
38943.5327 | 1 | 0 | 34
38943.5348 | 1 | 0 | 34
38943.537 | 1 | 0 | 34
38943.5391 | 2 | 0 | 34
38943.5413 | 1 | 0 | 34
38943.5434 | 1 | 0 | 34
38943.5455 | 2 | 0 | 34
38943.5477 | 2 | 0 | 34
38943.5498 | 2 | 0 | 34
38943.5519 | 2 | 0 | 34
38943.5541 | 2091 | 0 | 34
38943.5562 | 2035 | 0 | 34
38943.5584 | 2311 | 0 | 34
38943.5605 | 1387 | 0 | 34
38943.5626 | 986 | 0 | 34
34
38943.5327 | 1 | 0 | 35
38943.5348 | 1 | 0 | 35
38943.537 | 1 | 0 | 35
38943.5391 | 1 | 0 | 35
38943.5413 | 2 | 0 | 35
38943.5434 | 2 | 0 | 35
38943.5455 | 2 | 0 | 35
38943.5477 | 2 | 0 | 35
38943.5498 | 2 | 0 | 35
38943.552 | 2 | 0 | 35
38943.5541 | 78 | 0 | 35
38943.5562 | 253 | 0 | 35
38943.5584 | 250 | 0 | 35
38943.5605 | 222 | 0 | 35
38943.5627 | 49 | 0 | 35
35
38943.5327 | 1 | 0 | 36
38943.5349 | 1 | 0 | 36
38943.537 | 1 | 0 | 36
38943.5391 | 1 | 0 | 36
38943.5413 | 2374 | 0 | 36
38943.5434 | 1192 | 0 | 36
38943.5456 | 2149 | 0 | 36
38943.5477 | 2544 | 0 | 36
38943.5498 | 2463 | 0 | 36
38943.552 | 2475 | 0 | 36
38943.5541 | 2112 | 0 | 36
38943.5563 | 2512 | 0 | 36
38943.5584 | 2548 | 0 | 36
38943.5605 | 2535 | 0 | 36
38943.5627 | 2301 | 0 | 36
36
38943.5327 | 1 | 0 | 37
38943.5349 | 1 | 0 | 37
38943.537 | 1 | 0 | 37
38943.5392 | 1 | 0 | 37
38943.5413 | 4 | 0 | 37
38943.5434 | 3 | 0 | 37
38943.5456 | 4 | 0 | 37
38943.5477 | 4 | 0 | 37
38943.5498 | 4 | 0 | 37
38943.552 | 4 | 0 | 37
38943.5541 | 100 | 0 | 37
38943.5563 | 248 | 0 | 37
38943.5584 | 247 | 0 | 37
38943.5605 | 197 | 0 | 37
38943.5627 | 50 | 0 | 37
37
38943.5328 | 1 | 0 | 38
38943.5349 | 1 | 0 | 38
38943.537 | 1 | 0 | 38
38943.5392 | 1769 | 0 | 38
38943.5413 | 3 | 0 | 38
38943.5434 | 2017 | 0 | 38
38943.5456 | 2182 | 0 | 38
38943.5477 | 2611 | 0 | 38
38943.5499 | 2138 | 0 | 38
38943.552 | 2136 | 0 | 38
38943.5541 | 2583 | 0 | 38
38943.5563 | 2264 | 0 | 38
38943.5584 | 2270 | 0 | 38
38943.5606 | 2537 | 0 | 38
38943.5627 | 2417 | 0 | 38
38
38943.5328 | 1 | 0 | 39
38943.5349 | 1 | 0 | 39
38943.537 | 1 | 0 | 39
38943.5392 | 4 | 0 | 39
38943.5413 | 2 | 0 | 39
38943.5435 | 4 | 0 | 39
38943.5456 | 4 | 0 | 39
38943.5477 | 4 | 0 | 39
38943.5499 | 4 | 0 | 39
38943.552 | 4 | 0 | 39
38943.5542 | 98 | 0 | 39
38943.5563 | 283 | 0 | 39
38943.5584 | 298 | 0 | 39
38943.5606 | 202 | 0 | 39
38943.5627 | 50 | 0 | 39
39
38943.5328 | 1 | 0 | 40
38943.5349 | 1 | 0 | 40
38943.5371 | 1 | 0 | 40
38943.5392 | 3 | 0 | 40
38943.5413 | 2 | 1 | 40
38943.5435 | 2 | 0 | 40
38943.5456 | 3 | 0 | 40
38943.5478 | 3 | 0 | 40
38943.5499 | 3 | 0 | 40
38943.552 | 3 | 0 | 40
38943.5542 | 2018 | 0 | 40
38943.5563 | 2509 | 0 | 40
38943.5584 | 2341 | 0 | 40
38943.5606 | 2122 | 1 | 40
38943.5627 | 1943 | 0 | 40
40
38943.5328 | 1 | 0 | 41
38943.5349 | 1 | 0 | 41
38943.5371 | 1 | 0 | 41
38943.5392 | 2 | 0 | 41
38943.5414 | 2 | 0 | 41
38943.5435 | 2 | 0 | 41
38943.5456 | 2 | 0 | 41
38943.5478 | 2 | 0 | 41
38943.5499 | 2 | 0 | 41
38943.552 | 2 | 0 | 41
38943.5542 | 87 | 0 | 41
38943.5563 | 280 | 0 | 41
38943.5585 | 300 | 0 | 41
38943.5606 | 210 | 0 | 41
38943.5627 | 53 | 0 | 41
41
38943.5328 | 1 | 0 | 42
38943.535 | 1 | 0 | 42
38943.5371 | 1 | 0 | 42
38943.5392 | 2 | 0 | 42
38943.5414 | 2 | 0 | 42
38943.5435 | 2 | 0 | 42
38943.5456 | 2 | 0 | 42
38943.5478 | 2 | 0 | 42
38943.5499 | 2 | 0 | 42
38943.5521 | 3 | 0 | 42
38943.5542 | 2337 | 0 | 42
38943.5563 | 2479 | 0 | 42
38943.5585 | 1936 | 0 | 42
38943.5606 | 1775 | 0 | 42
38943.5628 | 1091 | 0 | 42
42
38943.5328 | 1 | 0 | 43
38943.535 | 1 | 0 | 43
38943.5371 | 1 | 0 | 43
38943.5393 | 1 | 0 | 43
38943.5414 | 2 | 0 | 43
38943.5435 | 2 | 0 | 43
38943.5457 | 3 | 0 | 43
38943.5478 | 2 | 0 | 43
38943.5499 | 2 | 0 | 43
38943.5521 | 2 | 0 | 43
38943.5542 | 109 | 86 | 43
38943.5564 | 2267 | 2 | 43
38943.5585 | 2088 | 0 | 43
38943.5606 | 2034 | 0 | 43
38943.5628 | 2084 | 0 | 43
43
38943.5329 | 1 | 0 | 44
38943.535 | 1 | 0 | 44
38943.5371 | 1 | 0 | 44
38943.5393 | 1 | 0 | 44
38943.5414 | 1 | 0 | 44
38943.5435 | 2 | 0 | 44
38943.5457 | 2 | 0 | 44
38943.5478 | 2 | 0 | 44
38943.55 | 2 | 0 | 44
38943.5521 | 2 | 0 | 44
38943.5542 | 948 | 102 | 44
38943.5564 | 2069 | 0 | 44
38943.5585 | 1946 | 0 | 44
38943.5607 | 2081 | 0 | 44
38943.5628 | 2263 | 0 | 44
44
38943.5329 | 1 | 0 | 45
38943.535 | 1 | 0 | 45
38943.5372 | 1 | 0 | 45
38943.5393 | 1 | 0 | 45
38943.5414 | 1 | 0 | 45
38943.5436 | 2 | 0 | 45
38943.5457 | 2 | 0 | 45
38943.5478 | 2 | 0 | 45
38943.55 | 2 | 0 | 45
38943.5521 | 2 | 0 | 45
38943.5543 | 1990 | 0 | 45
38943.5564 | 2092 | 0 | 45
38943.5585 | 2028 | 0 | 45
38943.5607 | 2047 | 0 | 45
38943.5628 | 2085 | 0 | 45
45
38943.5329 | 1 | 0 | 46
38943.535 | 1 | 0 | 46
38943.5372 | 1 | 0 | 46
38943.5393 | 1 | 0 | 46
38943.5414 | 2 | 0 | 46
38943.5436 | 1 | 0 | 46
38943.5457 | 2 | 0 | 46
38943.5479 | 2 | 0 | 46
38943.55 | 1 | 0 | 46
38943.5521 | 1 | 0 | 46
38943.5543 | 227 | 0 | 46
38943.5564 | 320 | 0 | 46
38943.5586 | 218 | 0 | 46
38943.5607 | 265 | 0 | 46
38943.5628 | 80 | 0 | 46
46
38943.5329 | 1 | 0 | 47
38943.535 | 1 | 0 | 47
38943.5372 | 1 | 0 | 47
38943.5393 | 1 | 0 | 47
38943.5415 | 1 | 0 | 47
38943.5436 | 2 | 0 | 47
38943.5457 | 2 | 0 | 47
38943.5479 | 2 | 0 | 47
38943.55 | 2 | 0 | 47
38943.5522 | 2 | 0 | 47
38943.5543 | 2546 | 0 | 47
38943.5564 | 2076 | 0 | 47
38943.5586 | 2510 | 0 | 47
38943.5607 | 2222 | 0 | 47
38943.5628 | 2194 | 0 | 47
47
38943.5329 | 1 | 0 | 48
38943.5351 | 1 | 0 | 48
38943.5372 | 1 | 0 | 48
38943.5393 | 1 | 0 | 48
38943.5415 | 2 | 0 | 48
38943.5436 | 2 | 0 | 48
38943.5458 | 2 | 0 | 48
38943.5479 | 2 | 0 | 48
38943.55 | 2 | 0 | 48
38943.5522 | 2 | 0 | 48
38943.5543 | 114 | 0 | 48
38943.5564 | 373 | 0 | 48
38943.5586 | 154 | 0 | 48
38943.5607 | 262 | 0 | 48
38943.5629 | 49 | 0 | 48
48
38943.5329 | 1 | 0 | 49
38943.5351 | 1 | 0 | 49
38943.5372 | 1 | 0 | 49
38943.5394 | 1 | 0 | 49
38943.5415 | 1 | 0 | 49
38943.5436 | 2 | 0 | 49
38943.5458 | 2 | 0 | 49
38943.5479 | 2 | 0 | 49
38943.55 | 2 | 0 | 49
38943.5522 | 2 | 0 | 49
38943.5543 | 2497 | 0 | 49
38943.5565 | 2198 | 0 | 49
38943.5586 | 2185 | 0 | 49
38943.5607 | 2325 | 0 | 49
38943.5629 | 2190 | 0 | 49
49
38943.533 | 1 | 0 | 50
38943.5351 | 1 | 0 | 50
38943.5372 | 1 | 0 | 50
38943.5394 | 1 | 0 | 50
38943.5415 | 2 | 0 | 50
38943.5436 | 2 | 0 | 50
38943.5458 | 2 | 0 | 50
38943.5479 | 2 | 0 | 50
38943.5501 | 2 | 0 | 50
38943.5522 | 33 | 0 | 50
38943.5543 | 2112 | 0 | 50
38943.5565 | 2321 | 0 | 50
38943.5586 | 2239 | 0 | 50
38943.5608 | 1878 | 0 | 50
38943.5629 | 1196 | 0 | 50
50
38943.533 | 1 | 0 | 51
38943.5351 | 1 | 0 | 51
38943.5372 | 1 | 0 | 51
38943.5394 | 1 | 0 | 51
38943.5415 | 1 | 0 | 51
38943.5437 | 2 | 0 | 51
38943.5458 | 2 | 0 | 51
38943.5479 | 1 | 0 | 51
38943.5501 | 2 | 0 | 51
38943.5522 | 2 | 0 | 51
38943.5544 | 2535 | 0 | 51
38943.5565 | 2533 | 0 | 51
38943.5586 | 2245 | 0 | 51
38943.5608 | 1999 | 0 | 51
38943.5629 | 2204 | 0 | 51
51
38943.533 | 1 | 0 | 52
38943.5351 | 1 | 0 | 52
38943.5373 | 1 | 0 | 52
38943.5394 | 1 | 0 | 52
38943.5415 | 1 | 0 | 52
38943.5437 | 1 | 0 | 52
38943.5458 | 2 | 0 | 52
38943.548 | 2 | 0 | 52
38943.5501 | 2 | 0 | 52
38943.5522 | 8 | 0 | 52
38943.5544 | 1837 | 0 | 52
38943.5565 | 2272 | 0 | 52
38943.5586 | 1862 | 0 | 52
38943.5608 | 1559 | 0 | 52
38943.5629 | 1172 | 0 | 52
52
38943.533 | 1 | 0 | 53
38943.5351 | 1 | 0 | 53
38943.5373 | 2 | 0 | 53
38943.5394 | 1 | 0 | 53
38943.5416 | 2 | 0 | 53
38943.5437 | 1 | 0 | 53
38943.5458 | 2 | 0 | 53
38943.548 | 2 | 0 | 53
38943.5501 | 2 | 0 | 53
38943.5522 | 2 | 0 | 53
38943.5544 | 2459 | 0 | 53
38943.5565 | 2071 | 0 | 53
38943.5587 | 2497 | 0 | 53
38943.5608 | 2516 | 0 | 53
38943.5629 | 2298 | 0 | 53
53
38943.533 | 1 | 0 | 54
38943.5352 | 1 | 0 | 54
38943.5373 | 1 | 0 | 54
38943.5394 | 1876 | 0 | 54
38943.5416 | 2198 | 0 | 54
38943.5437 | 2251 | 0 | 54
38943.5458 | 2353 | 0 | 54
38943.548 | 2294 | 0 | 54
38943.5501 | 2077 | 0 | 54
38943.5523 | 2071 | 0 | 54
38943.5544 | 2462 | 0 | 54
38943.5565 | 2577 | 0 | 54
38943.5587 | 2564 | 0 | 54
38943.5608 | 2582 | 0 | 54
38943.563 | 2281 | 0 | 54
54
38943.533 | 1 | 0 | 55
38943.5352 | 1 | 0 | 55
38943.5373 | 1 | 0 | 55
38943.5394 | 4 | 0 | 55
38943.5416 | 4 | 0 | 55
38943.5437 | 4 | 0 | 55
38943.5459 | 4 | 0 | 55
38943.548 | 4 | 0 | 55
38943.5501 | 4 | 0 | 55
38943.5523 | 4 | 0 | 55
38943.5544 | 2031 | 0 | 55
38943.5566 | 1973 | 0 | 55
38943.5587 | 2124 | 0 | 55
38943.5608 | 2103 | 0 | 55
38943.563 | 2197 | 0 | 55
55
38943.533 | 1 | 0 | 56
38943.5352 | 1 | 0 | 56
38943.5373 | 1 | 0 | 56
38943.5395 | 1763 | 0 | 56
38943.5416 | 2 | 0 | 56
38943.5437 | 2563 | 0 | 56
38943.5459 | 2073 | 0 | 56
38943.548 | 2577 | 0 | 56
38943.5502 | 2258 | 0 | 56
38943.5523 | 2121 | 0 | 56
38943.5544 | 2234 | 0 | 56
38943.5566 | 2231 | 0 | 56
38943.5587 | 2233 | 0 | 56
38943.5608 | 2338 | 0 | 56
38943.563 | 2407 | 0 | 56
56
38943.5331 | 1 | 0 | 57
38943.5352 | 1 | 0 | 57
38943.5373 | 1 | 0 | 57
38943.5395 | 4 | 0 | 57
38943.5416 | 2 | 0 | 57
38943.5438 | 4 | 0 | 57
38943.5459 | 4 | 0 | 57
38943.548 | 4 | 0 | 57
38943.5502 | 4 | 0 | 57
38943.5523 | 4 | 0 | 57
38943.5545 | 2323 | 0 | 57
38943.5566 | 2430 | 0 | 57
38943.5587 | 2452 | 0 | 57
38943.5609 | 2470 | 0 | 57
38943.563 | 2535 | 0 | 57
57
38943.5331 | 1 | 0 | 58
38943.5352 | 1 | 0 | 58
38943.5374 | 1 | 0 | 58
38943.5395 | 3 | 0 | 58
38943.5416 | 2 | 0 | 58
38943.5438 | 3 | 0 | 58
38943.5459 | 3 | 0 | 58
38943.5481 | 3 | 0 | 58
38943.5502 | 3 | 0 | 58
38943.5523 | 675 | 0 | 58
38943.5545 | 2326 | 0 | 58
38943.5566 | 2131 | 0 | 58
38943.5587 | 2316 | 0 | 58
38943.5609 | 1615 | 0 | 58
38943.563 | 1269 | 0 | 58
58
38943.5331 | 1 | 0 | 59
38943.5352 | 1 | 0 | 59
38943.5374 | 1 | 0 | 59
38943.5395 | 3 | 0 | 59
38943.5417 | 2 | 0 | 59
38943.5438 | 2 | 0 | 59
38943.5459 | 2 | 0 | 59
38943.5481 | 3 | 0 | 59
38943.5502 | 3 | 0 | 59
38943.5523 | 2 | 0 | 59
38943.5545 | 2035 | 0 | 59
38943.5566 | 2542 | 0 | 59
38943.5588 | 2515 | 0 | 59
38943.5609 | 2153 | 0 | 59
38943.563 | 2277 | 0 | 59
59
38943.5331 | 1 | 0 | 60
38943.5353 | 1 | 0 | 60
38943.5374 | 1 | 0 | 60
38943.5395 | 2 | 0 | 60
38943.5417 | 2 | 0 | 60
38943.5438 | 3 | 0 | 60
38943.5459 | 2 | 0 | 60
38943.5481 | 2 | 0 | 60
38943.5502 | 2 | 0 | 60
38943.5524 | 1928 | 0 | 60
38943.5545 | 2065 | 0 | 60
38943.5566 | 1996 | 0 | 60
38943.5588 | 1970 | 0 | 60
38943.5609 | 1442 | 0 | 60
38943.5631 | 1360 | 0 | 60
60
38943.5331 | 1 | 0 | 61
38943.5353 | 1 | 0 | 61
38943.5374 | 1 | 0 | 61
38943.5395 | 2 | 0 | 61
38943.5417 | 2 | 0 | 61
38943.5438 | 2 | 0 | 61
38943.546 | 2 | 0 | 61
38943.5481 | 2 | 0 | 61
38943.5502 | 2 | 0 | 61
38943.5524 | 4 | 0 | 61
38943.5545 | 890 | 0 | 61
38943.5567 | 2022 | 0 | 61
38943.5588 | 2165 | 0 | 61
38943.5609 | 2556 | 0 | 61
38943.5631 | 2367 | 0 | 61
61
38943.5331 | 1 | 0 | 62
38943.5353 | 1 | 0 | 62
38943.5374 | 1 | 0 | 62
38943.5396 | 2 | 0 | 62
38943.5417 | 1 | 0 | 62
38943.5438 | 2 | 0 | 62
38943.546 | 2 | 0 | 62
38943.5481 | 2 | 0 | 62
38943.5503 | 2 | 0 | 62
38943.5524 | 3 | 0 | 62
38943.5545 | 337 | 0 | 62
38943.5567 | 370 | 0 | 62
38943.5588 | 180 | 0 | 62
38943.5609 | 271 | 0 | 62
38943.5631 | 54 | 0 | 62
62
38943.5332 | 1 | 0 | 63
38943.5353 | 1 | 0 | 63
38943.5374 | 1 | 0 | 63
38943.5396 | 2 | 0 | 63
38943.5417 | 2 | 0 | 63
38943.5439 | 2 | 0 | 63
38943.546 | 2 | 0 | 63
38943.5481 | 2 | 0 | 63
38943.5503 | 2 | 0 | 63
38943.5524 | 2 | 0 | 63
38943.5545 | 1323 | 0 | 63
38943.5567 | 2093 | 0 | 63
38943.5588 | 809 | 0 | 63
38943.561 | 2401 | 0 | 63
38943.5631 | 2235 | 0 | 63
63
38943.5332 | 1 | 0 | 64
38943.5353 | 1 | 0 | 64
38943.5375 | 1 | 0 | 64
38943.5396 | 2 | 0 | 64
38943.5417 | 1 | 0 | 64
38943.5439 | 2 | 0 | 64
38943.546 | 2 | 0 | 64
38943.5481 | 2 | 0 | 64
38943.5503 | 2 | 0 | 64
38943.5524 | 2 | 0 | 64
38943.5546 | 391 | 0 | 64
38943.5567 | 342 | 0 | 64
38943.5588 | 151 | 0 | 64
38943.561 | 262 | 0 | 64
38943.5631 | 49 | 0 | 64
64
38943.5332 | 1 | 0 | 65
38943.5353 | 1 | 0 | 65
38943.5375 | 1 | 0 | 65
38943.5396 | 2 | 0 | 65
38943.5417 | 2 | 0 | 65
38943.5439 | 2 | 0 | 65
38943.546 | 2 | 0 | 65
38943.5482 | 1 | 0 | 65
38943.5503 | 2 | 0 | 65
38943.5524 | 2 | 0 | 65
38943.5546 | 129 | 0 | 65
38943.5567 | 2028 | 0 | 65
38943.5589 | 1464 | 0 | 65
38943.561 | 2475 | 0 | 65
38943.5631 | 2318 | 0 | 65
65
38943.5332 | 1 | 0 | 66
38943.5353 | 1 | 0 | 66
38943.5375 | 1 | 0 | 66
38943.5396 | 2 | 0 | 66
38943.5418 | 1 | 0 | 66
38943.5439 | 1 | 0 | 66
38943.546 | 2 | 0 | 66
38943.5482 | 2 | 0 | 66
38943.5503 | 2 | 0 | 66
38943.5525 | 76 | 0 | 66
38943.5546 | 2132 | 0 | 66
38943.5567 | 1922 | 0 | 66
38943.5589 | 2239 | 0 | 66
38943.561 | 1414 | 0 | 66
38943.5631 | 1096 | 0 | 66
66
38943.5332 | 1 | 0 | 67
38943.5354 | 1 | 0 | 67
38943.5375 | 1 | 0 | 67
38943.5396 | 1 | 0 | 67
38943.5418 | 1 | 0 | 67
38943.5439 | 2 | 0 | 67
38943.5461 | 2 | 0 | 67
38943.5482 | 2 | 0 | 67
38943.5503 | 2 | 0 | 67
38943.5525 | 2 | 0 | 67
38943.5546 | 1835 | 0 | 67
38943.5567 | 2290 | 0 | 67
38943.5589 | 350 | 0 | 67
38943.561 | 2484 | 0 | 67
38943.5632 | 2176 | 0 | 67
67
38943.5332 | 1 | 0 | 68
38943.5354 | 1 | 0 | 68
38943.5375 | 1 | 0 | 68
38943.5397 | 1 | 0 | 68
38943.5418 | 1 | 0 | 68
38943.5439 | 1 | 0 | 68
38943.5461 | 2 | 0 | 68
38943.5482 | 2 | 0 | 68
38943.5503 | 2 | 1 | 68
38943.5525 | 115 | 0 | 68
38943.5546 | 1925 | 0 | 68
38943.5568 | 2085 | 0 | 68
38943.5589 | 1715 | 0 | 68
38943.561 | 1311 | 0 | 68
38943.5632 | 1043 | 0 | 68
68
38943.5333 | 1 | 0 | 69
38943.5354 | 1 | 0 | 69
38943.5375 | 1 | 0 | 69
38943.5397 | 1 | 0 | 69
38943.5418 | 1 | 0 | 69
38943.5439 | 1 | 0 | 69
38943.5461 | 1 | 0 | 69
38943.5482 | 2 | 0 | 69
38943.5504 | 2 | 0 | 69
38943.5525 | 2 | 0 | 69
38943.5546 | 34 | 0 | 69
38943.5568 | 2195 | 0 | 69
38943.5589 | 1640 | 2 | 69
38943.5611 | 2450 | 0 | 69
38943.5632 | 2298 | 0 | 69
69
38943.5333 | 1 | 0 | 70
38943.5354 | 1 | 0 | 70
38943.5376 | 1 | 0 | 70
38943.5397 | 2035 | 0 | 70
38943.5418 | 2384 | 0 | 70
38943.544 | 2536 | 0 | 70
38943.5461 | 2209 | 0 | 70
38943.5482 | 2383 | 0 | 70
38943.5504 | 2286 | 0 | 70
38943.5525 | 2013 | 0 | 70
38943.5547 | 2206 | 0 | 70
38943.5568 | 2569 | 0 | 70
38943.5589 | 2286 | 0 | 70
38943.5611 | 2010 | 0 | 70
38943.5632 | 2222 | 0 | 70
70
38943.5333 | 1 | 0 | 71
38943.5354 | 1 | 0 | 71
38943.5376 | 1 | 0 | 71
38943.5397 | 4 | 0 | 71
38943.5418 | 4 | 0 | 71
38943.544 | 4 | 0 | 71
38943.5461 | 4 | 0 | 71
38943.5483 | 4 | 0 | 71
38943.5504 | 4 | 0 | 71
38943.5525 | 4 | 0 | 71
38943.5547 | 184 | 0 | 71
38943.5568 | 1978 | 0 | 71
38943.559 | 2307 | 2 | 71
38943.5611 | 2067 | 0 | 71
38943.5632 | 2179 | 0 | 71
71
38943.5333 | 1 | 0 | 72
38943.5355 | 1 | 0 | 72
38943.5376 | 1 | 0 | 72
38943.5397 | 1806 | 0 | 72
38943.5419 | 3 | 0 | 72
38943.544 | 2570 | 0 | 72
38943.5461 | 2094 | 0 | 72
38943.5483 | 2017 | 0 | 72
38943.5504 | 2569 | 0 | 72
38943.5526 | 2396 | 0 | 72
38943.5547 | 2565 | 0 | 72
38943.5568 | 1995 | 0 | 72
38943.559 | 2049 | 0 | 72
38943.5611 | 1993 | 0 | 72
38943.5633 | 2296 | 0 | 72
72
38943.5333 | 1 | 0 | 73
38943.5355 | 1 | 0 | 73
38943.5376 | 1 | 0 | 73
38943.5397 | 4 | 0 | 73
38943.5419 | 2 | 0 | 73
38943.544 | 4 | 0 | 73
38943.5462 | 4 | 0 | 73
38943.5483 | 4 | 0 | 73
38943.5504 | 4 | 0 | 73
38943.5526 | 4 | 0 | 73
38943.5547 | 45 | 0 | 73
38943.5569 | 2360 | 0 | 73
38943.559 | 2483 | 0 | 73
38943.5611 | 2420 | 0 | 73
38943.5633 | 2169 | 0 | 73
73
38943.5333 | 1 | 0 | 74
38943.5355 | 1 | 0 | 74
38943.5376 | 1 | 0 | 74
38943.5398 | 3 | 0 | 74
38943.5419 | 2 | 0 | 74
38943.544 | 3 | 0 | 74
38943.5462 | 3 | 0 | 74
38943.5483 | 3 | 0 | 74
38943.5505 | 3 | 0 | 74
38943.5526 | 2449 | 0 | 74
38943.5547 | 2471 | 0 | 74
38943.5569 | 2313 | 0 | 74
38943.559 | 2207 | 0 | 74
38943.5611 | 1948 | 0 | 74
38943.5633 | 898 | 0 | 74
74
38943.5334 | 1 | 0 | 75
38943.5355 | 1 | 0 | 75
38943.5376 | 1 | 0 | 75
38943.5398 | 3 | 0 | 75
38943.5419 | 2 | 0 | 75
38943.5441 | 2 | 0 | 75
38943.5462 | 2 | 0 | 75
38943.5483 | 2 | 0 | 75
38943.5505 | 2 | 0 | 75
38943.5526 | 4 | 0 | 75
38943.5547 | 125 | 0 | 75
38943.5569 | 2274 | 0 | 75
38943.559 | 2094 | 0 | 75
38943.5612 | 2298 | 0 | 75
38943.5633 | 2231 | 0 | 75
75
38943.5334 | 1 | 0 | 76
38943.5355 | 1 | 0 | 76
38943.5377 | 1 | 0 | 76
38943.5398 | 2 | 0 | 76
38943.5419 | 2 | 0 | 76
38943.5441 | 3 | 0 | 76
38943.5462 | 3 | 0 | 76
38943.5483 | 2 | 0 | 76
38943.5505 | 3 | 0 | 76
38943.5526 | 2215 | 0 | 76
38943.5548 | 2418 | 0 | 76
38943.5569 | 2437 | 0 | 76
38943.559 | 2382 | 0 | 76
38943.5612 | 2050 | 0 | 76
38943.5633 | 969 | 0 | 76
76
38943.5334 | 1 | 0 | 77
38943.5355 | 1 | 0 | 77
38943.5377 | 1 | 0 | 77
38943.5398 | 1 | 0 | 77
38943.5419 | 1 | 0 | 77
38943.5441 | 2 | 0 | 77
38943.5462 | 2 | 0 | 77
38943.5484 | 2 | 0 | 77
38943.5505 | 2 | 0 | 77
38943.5526 | 4 | 0 | 77
38943.5548 | 649 | 594 | 77
38943.5569 | 306 | 59 | 77
38943.5591 | 855 | 664 | 77
38943.5612 | 982 | 755 | 77
38943.5633 | 1036 | 909 | 77
77
38943.5334 | 1 | 0 | 78
38943.5355 | 1 | 0 | 78
38943.5377 | 1 | 0 | 78
38943.5398 | 2 | 0 | 78
38943.542 | 2 | 0 | 78
38943.5441 | 2 | 0 | 78
38943.5462 | 2 | 0 | 78
38943.5484 | 2 | 0 | 78
38943.5505 | 2 | 0 | 78
38943.5527 | 3 | 0 | 78
38943.5548 | 138 | 60 | 78
38943.5569 | 526 | 313 | 78
38943.5591 | 899 | 715 | 78
38943.5612 | 999 | 819 | 78
38943.5633 | 1001 | 877 | 78
78
38943.5334 | 1 | 0 | 79
38943.5356 | 1 | 0 | 79
38943.5377 | 1 | 0 | 79
38943.5398 | 2 | 0 | 79
38943.542 | 1 | 0 | 79
38943.5441 | 2 | 0 | 79
38943.5462 | 2 | 0 | 79
38943.5484 | 2 | 0 | 79
38943.5505 | 2 | 0 | 79
38943.5527 | 3 | 0 | 79
38943.5548 | 3 | 2 | 79
38943.5569 | 307 | 0 | 79
38943.5591 | 179 | 4 | 79
38943.5612 | 217 | 4 | 79
38943.5634 | 41 | 3 | 79
79
38943.5334 | 1 | 0 | 80
38943.5356 | 1 | 0 | 80
38943.5377 | 1 | 0 | 80
38943.5398 | 2 | 0 | 80
38943.542 | 1 | 0 | 80
38943.5441 | 2 | 0 | 80
38943.5463 | 2 | 0 | 80
38943.5484 | 2 | 0 | 80
38943.5505 | 2 | 0 | 80
38943.5527 | 538 | 0 | 80
38943.5548 | 1889 | 1 | 80
38943.557 | 2242 | 0 | 80
38943.5591 | 1443 | 2 | 80
38943.5612 | 1094 | 2 | 80
38943.5634 | 945 | 2 | 80
80
38943.5334 | 1 | 0 | 81
38943.5356 | 1 | 0 | 81
38943.5377 | 1 | 0 | 81
38943.5399 | 2 | 0 | 81
38943.542 | 1 | 0 | 81
38943.5441 | 2 | 0 | 81
38943.5463 | 2 | 0 | 81
38943.5484 | 2 | 0 | 81
38943.5506 | 2 | 0 | 81
38943.5527 | 2 | 0 | 81
38943.5548 | 173 | 0 | 81
38943.557 | 294 | 0 | 81
38943.5591 | 192 | 1 | 81
38943.5612 | 231 | 1 | 81
38943.5634 | 36 | 1 | 81
81
38943.5335 | 1 | 0 | 82
38943.5356 | 1 | 0 | 82
38943.5377 | 1 | 0 | 82
38943.5399 | 1 | 0 | 82
38943.542 | 1 | 0 | 82
38943.5442 | 1 | 0 | 82
38943.5463 | 2 | 0 | 82
38943.5484 | 2 | 0 | 82
38943.5506 | 2 | 0 | 82
38943.5527 | 704 | 0 | 82
38943.5548 | 2012 | 0 | 82
38943.557 | 2192 | 0 | 82
38943.5591 | 1525 | 1 | 82
38943.5613 | 1388 | 1 | 82
38943.5634 | 920 | 1 | 82
82
38943.5335 | 1 | 0 | 83
38943.5356 | 1 | 0 | 83
38943.5378 | 1 | 0 | 83
38943.5399 | 1 | 0 | 83
38943.542 | 2 | 0 | 83
38943.5442 | 2 | 0 | 83
38943.5463 | 2 | 0 | 83
38943.5485 | 2 | 0 | 83
38943.5506 | 2 | 0 | 83
38943.5527 | 2 | 0 | 83
38943.5549 | 3 | 0 | 83
38943.557 | 305 | 0 | 83
38943.5591 | 226 | 1 | 83
38943.5613 | 213 | 0 | 83
38943.5634 | 34 | 0 | 83
83
38943.5335 | 1 | 0 | 84
38943.5356 | 1 | 0 | 84
38943.5378 | 1 | 0 | 84
38943.5399 | 2381 | 0 | 84
38943.5421 | 1589 | 0 | 84
38943.5442 | 2357 | 0 | 84
38943.5463 | 2611 | 0 | 84
38943.5485 | 2421 | 0 | 84
38943.5506 | 2103 | 0 | 84
38943.5527 | 2065 | 0 | 84
38943.5549 | 2216 | 0 | 84
38943.557 | 2181 | 0 | 84
38943.5592 | 2149 | 0 | 84
38943.5613 | 2005 | 0 | 84
38943.5634 | 2268 | 0 | 84
84
38943.5335 | 1 | 0 | 85
38943.5357 | 1 | 0 | 85
38943.5378 | 1 | 0 | 85
38943.5399 | 3 | 0 | 85
38943.5421 | 3 | 0 | 85
38943.5442 | 4 | 0 | 85
38943.5464 | 4 | 0 | 85
38943.5485 | 3 | 0 | 85
38943.5506 | 3 | 0 | 85
38943.5528 | 4 | 0 | 85
38943.5549 | 3 | 0 | 85
38943.557 | 277 | 0 | 85
38943.5592 | 197 | 0 | 85
38943.5613 | 213 | 0 | 85
38943.5635 | 34 | 0 | 85
85
38943.5335 | 1 | 0 | 86
38943.5357 | 1 | 0 | 86
38943.5378 | 1 | 0 | 86
38943.54 | 1939 | 1 | 86
38943.5421 | 2 | 0 | 86
38943.5442 | 2568 | 0 | 86
38943.5464 | 2478 | 0 | 86
38943.5485 | 2174 | 0 | 86
38943.5506 | 2064 | 0 | 86
38943.5528 | 2245 | 0 | 86
38943.5549 | 2073 | 0 | 86
38943.5571 | 2114 | 0 | 86
38943.5592 | 2250 | 0 | 86
38943.5613 | 2071 | 0 | 86
38943.5635 | 2582 | 0 | 86
86
38943.5336 | 1 | 0 | 87
38943.5357 | 1 | 0 | 87
38943.5378 | 1 | 0 | 87
38943.54 | 4 | 1 | 87
38943.5421 | 2 | 0 | 87
38943.5442 | 3 | 0 | 87
38943.5464 | 4 | 0 | 87
38943.5485 | 4 | 0 | 87
38943.5507 | 4 | 0 | 87
38943.5528 | 4 | 0 | 87
38943.5549 | 25 | 0 | 87
38943.5571 | 207 | 0 | 87
38943.5592 | 196 | 0 | 87
38943.5614 | 156 | 0 | 87
38943.5635 | 37 | 0 | 87
87
38943.5336 | 1 | 0 | 88
38943.5357 | 1 | 0 | 88
38943.5378 | 1 | 0 | 88
38943.54 | 3 | 0 | 88
38943.5421 | 2 | 0 | 88
38943.5443 | 3 | 0 | 88
38943.5464 | 3 | 0 | 88
38943.5485 | 3 | 0 | 88
38943.5507 | 3 | 0 | 88
38943.5528 | 2445 | 0 | 88
38943.555 | 2068 | 0 | 88
38943.5571 | 2494 | 0 | 88
38943.5592 | 2502 | 0 | 88
38943.5614 | 1412 | 0 | 88
38943.5635 | 895 | 0 | 88
88
38943.5336 | 1 | 0 | 89
38943.5357 | 1 | 0 | 89
38943.5379 | 1 | 0 | 89
38943.54 | 2 | 0 | 89
38943.5421 | 2 | 0 | 89
38943.5443 | 3 | 0 | 89
38943.5464 | 2 | 0 | 89
38943.5486 | 3 | 0 | 89
38943.5507 | 2 | 0 | 89
38943.5528 | 4 | 0 | 89
38943.555 | 112 | 0 | 89
38943.5571 | 286 | 0 | 89
38943.5592 | 212 | 0 | 89
38943.5614 | 177 | 0 | 89
38943.5635 | 30 | 0 | 89
89
38943.5336 | 1 | 0 | 90
38943.5357 | 1 | 0 | 90
38943.5379 | 1 | 0 | 90
38943.54 | 3 | 0 | 90
38943.5422 | 1 | 0 | 90
38943.5443 | 2 | 0 | 90
38943.5464 | 2 | 0 | 90
38943.5486 | 3 | 0 | 90
38943.5507 | 2 | 0 | 90
38943.5528 | 2302 | 0 | 90
38943.555 | 2100 | 0 | 90
38943.5571 | 2001 | 0 | 90
38943.5593 | 2138 | 0 | 90
38943.5614 | 1316 | 0 | 90
38943.5635 | 1696 | 0 | 90
90
38943.5336 | 1 | 0 | 91
38943.5358 | 1 | 0 | 91
38943.5379 | 1 | 0 | 91
38943.54 | 2 | 0 | 91
38943.5422 | 2 | 0 | 91
38943.5443 | 2 | 0 | 91
38943.5464 | 2 | 0 | 91
38943.5486 | 2 | 0 | 91
38943.5507 | 2 | 0 | 91
38943.5529 | 4 | 0 | 91
38943.555 | 7 | 0 | 91
38943.5571 | 193 | 0 | 91
38943.5593 | 235 | 0 | 91
38943.5614 | 236 | 0 | 91
38943.5636 | 23 | 0 | 91
91
38943.5336 | 1 | 0 | 92
38943.5358 | 1 | 0 | 92
38943.5379 | 1 | 0 | 92
38943.54 | 2 | 0 | 92
38943.5443 | 2 | 0 | 92
38943.5465 | 2 | 0 | 92
38943.5486 | 2 | 0 | 92
38943.5507 | 2 | 0 | 92
38943.5529 | 1090 | 0 | 92
38943.555 | 1702 | 0 | 92
38943.5572 | 2310 | 0 | 92
38943.5593 | 1764 | 0 | 92
38943.5614 | 1365 | 0 | 92
38943.5636 | 969 | 0 | 92
92
38943.5336 | 1 | 0 | 93
38943.5358 | 1 | 0 | 93
38943.5379 | 1 | 0 | 93
38943.5401 | 2 | 0 | 93
38943.5422 | 1 | 0 | 93
38943.5443 | 2 | 0 | 93
38943.5465 | 2 | 0 | 93
38943.5486 | 2 | 0 | 93
38943.5508 | 2 | 0 | 93
38943.5529 | 4 | 0 | 93
38943.555 | 5 | 0 | 93
38943.5572 | 384 | 0 | 93
38943.5593 | 226 | 0 | 93
38943.5614 | 204 | 0 | 93
38943.5636 | 24 | 0 | 93
93
38943.5337 | 1 | 0 | 94
38943.5358 | 1 | 0 | 94
38943.5379 | 1 | 0 | 94
38943.5401 | 2 | 0 | 94
38943.5422 | 1 | 0 | 94
38943.5444 | 2 | 0 | 94
38943.5465 | 2 | 0 | 94
38943.5486 | 2 | 0 | 94
38943.5508 | 2 | 0 | 94
38943.5529 | 1459 | 0 | 94
38943.555 | 1846 | 0 | 94
38943.5572 | 1841 | 0 | 94
38943.5593 | 1586 | 0 | 94
38943.5615 | 1337 | 0 | 94
38943.5636 | 719 | 0 | 94
94
38943.5337 | 1 | 0 | 95
38943.5358 | 1 | 0 | 95
38943.538 | 1 | 0 | 95
38943.5401 | 2 | 0 | 95
38943.5422 | 1 | 0 | 95
38943.5444 | 2 | 0 | 95
38943.5465 | 2 | 0 | 95
38943.5486 | 2 | 0 | 95
38943.5508 | 2 | 0 | 95
38943.5529 | 4 | 0 | 95
38943.5551 | 5 | 0 | 95
38943.5572 | 283 | 0 | 95
38943.5593 | 213 | 0 | 95
38943.5615 | 179 | 0 | 95
38943.5636 | 20 | 0 | 95
95
38943.5337 | 1 | 0 | 96
38943.5358 | 1 | 0 | 96
38943.538 | 1 | 0 | 96
38943.5401 | 2437 | 0 | 96
38943.5422 | 1943 | 0 | 96
38943.5444 | 2239 | 0 | 96
38943.5465 | 2022 | 0 | 96
38943.5487 | 2557 | 0 | 96
38943.5508 | 2247 | 0 | 96
38943.5529 | 2313 | 0 | 96
38943.5551 | 2178 | 0 | 96
38943.5572 | 2093 | 0 | 96
38943.5594 | 2313 | 0 | 96
38943.5615 | 2421 | 0 | 96
38943.5636 | 2162 | 0 | 96
96
38943.5337 | 1 | 0 | 97
38943.5359 | 1 | 0 | 97
38943.538 | 1 | 0 | 97
38943.5401 | 4 | 0 | 97
38943.5423 | 4 | 0 | 97
38943.5444 | 4 | 0 | 97
38943.5465 | 4 | 0 | 97
38943.5487 | 3 | 0 | 97
38943.5508 | 3 | 0 | 97
38943.553 | 4 | 0 | 97
38943.5551 | 4 | 0 | 97
38943.5572 | 667 | 0 | 97
38943.5594 | 232 | 0 | 97
38943.5615 | 231 | 0 | 97
38943.5637 | 19 | 0 | 97
97
38943.5337 | 1 | 0 | 98
38943.5359 | 1 | 0 | 98
38943.538 | 1 | 1 | 98
38943.5401 | 41 | 0 | 98
38943.5423 | 2 | 0 | 98
38943.5444 | 2507 | 0 | 98
38943.5466 | 2093 | 0 | 98
38943.5487 | 2348 | 0 | 98
38943.5508 | 2053 | 0 | 98
38943.553 | 2390 | 0 | 98
38943.5551 | 2520 | 0 | 98
38943.5573 | 2466 | 0 | 98
38943.5594 | 1996 | 0 | 98
38943.5615 | 2032 | 0 | 98
38943.5637 | 2246 | 0 | 98
98
38943.5338 | 1 | 0 | 99
38943.5359 | 1 | 0 | 99
38943.538 | 1 | 0 | 99
38943.5402 | 4 | 0 | 99
38943.5423 | 2 | 0 | 99
38943.5444 | 4 | 0 | 99
38943.5466 | 4 | 0 | 99
38943.5487 | 4 | 0 | 99
38943.5509 | 4 | 0 | 99
38943.553 | 4 | 0 | 99
38943.5551 | 4 | 0 | 99
38943.5573 | 662 | 0 | 99
38943.5594 | 287 | 0 | 99
38943.5616 | 245 | 0 | 99
38943.5637 | 26 | 0 | 99
99
38943.5338 | 1 | 0 | 100
38943.5359 | 1 | 0 | 100
38943.538 | 1 | 0 | 100
38943.5402 | 2 | 0 | 100
38943.5423 | 2 | 0 | 100
38943.5445 | 3 | 0 | 100
38943.5466 | 3 | 0 | 100
38943.5487 | 3 | 0 | 100
38943.5509 | 3 | 0 | 100
38943.553 | 2306 | 0 | 100
38943.5552 | 2087 | 0 | 100
38943.5573 | 2499 | 0 | 100
38943.5594 | 2228 | 0 | 100
38943.5616 | 1137 | 0 | 100
38943.5637 | 893 | 0 | 100
100
38943.5338 | 1 | 0 | 101
38943.5359 | 1 | 0 | 101
38943.5381 | 1 | 0 | 101
38943.5402 | 2 | 0 | 101
38943.5423 | 1 | 0 | 101
38943.5445 | 3 | 0 | 101
38943.5466 | 3 | 0 | 101
38943.5488 | 2 | 0 | 101
38943.5509 | 3 | 0 | 101
38943.553 | 4 | 0 | 101
38943.5552 | 4 | 0 | 101
38943.5573 | 1008 | 0 | 101
38943.5594 | 322 | 0 | 101
38943.5616 | 226 | 0 | 101
38943.5637 | 26 | 0 | 101
101
38943.5338 | 1 | 0 | 102
38943.5359 | 1 | 0 | 102
38943.5381 | 1 | 0 | 102
38943.5402 | 2 | 0 | 102
38943.5423 | 2 | 0 | 102
38943.5445 | 2 | 0 | 102
38943.5466 | 3 | 0 | 102
38943.5488 | 2 | 0 | 102
38943.5509 | 3 | 0 | 102
38943.553 | 2325 | 0 | 102
38943.5552 | 1956 | 0 | 102
38943.5573 | 2416 | 0 | 102
38943.5595 | 1975 | 0 | 102
38943.5616 | 1247 | 0 | 102
38943.5637 | 1190 | 0 | 102
102
38943.5338 | 1 | 0 | 103
38943.5359 | 1 | 0 | 103
38943.5381 | 1 | 0 | 103
38943.5402 | 2 | 0 | 103
38943.5424 | 1 | 0 | 103
38943.5445 | 2 | 0 | 103
38943.5466 | 2 | 0 | 103
38943.5488 | 8 | 4 | 103
38943.5509 | 946 | 1051 | 103
38943.5531 | 1738 | 379 | 103
38943.5552 | 1646 | 312 | 103
38943.5573 | 2090 | 52 | 103
38943.5595 | 1782 | 629 | 103
38943.5616 | 1554 | 564 | 103
38943.5638 | 1224 | 882 | 103
103
38943.5338 | 1 | 0 | 104
38943.536 | 1 | 0 | 104
38943.5381 | 1 | 0 | 104
38943.5402 | 1 | 0 | 104
38943.5424 | 1 | 0 | 104
38943.5445 | 2 | 0 | 104
38943.5467 | 2 | 0 | 104
38943.5488 | 6 | 2 | 104
38943.5509 | 1028 | 1069 | 104
38943.5531 | 1573 | 312 | 104
38943.5552 | 1880 | 339 | 104
38943.5573 | 2202 | 49 | 104
38943.5595 | 1512 | 454 | 104
38943.5616 | 1261 | 685 | 104
38943.5638 | 1153 | 840 | 104
104
38943.5338 | 1 | 0 | 105
38943.536 | 1 | 0 | 105
38943.5381 | 1 | 0 | 105
38943.5403 | 2 | 0 | 105
38943.5424 | 2 | 0 | 105
38943.5445 | 2 | 0 | 105
38943.5467 | 2 | 0 | 105
38943.5488 | 2 | 0 | 105
38943.5509 | 3 | 9 | 105
38943.5531 | 1665 | 1 | 105
38943.5552 | 1982 | 2 | 105
38943.5574 | 1987 | 0 | 105
38943.5595 | 1693 | 3 | 105
38943.5616 | 1771 | 4 | 105
38943.5638 | 858 | 5 | 105
105
38943.5339 | 1 | 0 | 106
38943.536 | 1 | 0 | 106
38943.5381 | 1 | 0 | 106
38943.5403 | 2547 | 0 | 106
38943.5424 | 2 | 0 | 106
38943.5445 | 2316 | 0 | 106
38943.5467 | 2017 | 0 | 106
38943.5488 | 2556 | 0 | 106
38943.551 | 2266 | 4 | 106
38943.5531 | 2116 | 0 | 106
38943.5552 | 2329 | 0 | 106
38943.5574 | 2145 | 0 | 106
38943.5595 | 2505 | 1 | 106
38943.5617 | 2068 | 2 | 106
38943.5638 | 2575 | 3 | 106
106
38943.5339 | 1 | 0 | 107
38943.536 | 1 | 0 | 107
38943.5381 | 1 | 0 | 107
38943.5403 | 4 | 0 | 107
38943.5424 | 1 | 0 | 107
38943.5446 | 4 | 0 | 107
38943.5467 | 4 | 0 | 107
38943.5488 | 4 | 0 | 107
38943.551 | 4 | 2 | 107
38943.5531 | 1939 | 0 | 107
38943.5553 | 1722 | 0 | 107
38943.5574 | 2134 | 0 | 107
38943.5595 | 1467 | 1 | 107
38943.5617 | 1250 | 1 | 107
38943.5638 | 1253 | 2 | 107
107
38943.5339 | 1 | 0 | 108
38943.536 | 1 | 0 | 108
38943.5382 | 1 | 0 | 108
38943.5403 | 2 | 0 | 108
38943.5424 | 2075 | 0 | 108
38943.5446 | 2603 | 0 | 108
38943.5467 | 2207 | 0 | 108
38943.5489 | 2379 | 0 | 108
38943.551 | 2608 | 2 | 108
38943.5531 | 2582 | 0 | 108
38943.5553 | 2205 | 0 | 108
38943.5574 | 2426 | 0 | 108
38943.5595 | 2318 | 1 | 108
38943.5617 | 2384 | 0 | 108
38943.5638 | 2332 | 1 | 108
108
38943.5339 | 1 | 0 | 109
38943.536 | 1 | 0 | 109
38943.5382 | 1 | 0 | 109
38943.5403 | 3 | 0 | 109
38943.5425 | 3 | 0 | 109
38943.5446 | 4 | 0 | 109
38943.5467 | 5 | 0 | 109
38943.5489 | 4 | 0 | 109
38943.551 | 4 | 1 | 109
38943.5531 | 1701 | 0 | 109
38943.5553 | 1948 | 0 | 109
38943.5574 | 2149 | 0 | 109
38943.5596 | 1610 | 0 | 109
38943.5617 | 1307 | 0 | 109
38943.5638 | 1123 | 1 | 109
109
38943.5339 | 1 | 0 | 110
38943.5361 | 1 | 0 | 110
38943.5382 | 1 | 0 | 110
38943.5403 | 2 | 0 | 110
38943.5425 | 2 | 0 | 110
38943.5446 | 3 | 0 | 110
38943.5468 | 3 | 0 | 110
38943.5489 | 3 | 0 | 110
38943.551 | 3 | 1 | 110
38943.5532 | 2096 | 0 | 110
38943.5553 | 2010 | 0 | 110
38943.5574 | 1941 | 0 | 110
38943.5596 | 2350 | 0 | 110
38943.5617 | 1457 | 0 | 110
38943.5639 | 1630 | 1 | 110
110
38943.5339 | 1 | 0 | 111
38943.5361 | 1 | 0 | 111
38943.5382 | 1 | 0 | 111
38943.5404 | 2 | 1 | 111
38943.5425 | 2 | 0 | 111
38943.5446 | 2 | 0 | 111
38943.5468 | 3 | 0 | 111
38943.5489 | 3 | 0 | 111
38943.551 | 3 | 1 | 111
38943.5532 | 1704 | 0 | 111
38943.5553 | 1879 | 0 | 111
38943.5575 | 2023 | 0 | 111
38943.5596 | 1807 | 0 | 111
38943.5617 | 1298 | 0 | 111
38943.5639 | 610 | 0 | 111
111
38943.534 | 1 | 0 | 112
38943.5361 | 1 | 0 | 112
38943.5382 | 1 | 0 | 112
38943.5404 | 2 | 0 | 112
38943.5425 | 2 | 0 | 112
38943.5447 | 3 | 0 | 112
38943.5468 | 3 | 0 | 112
38943.5489 | 2 | 0 | 112
38943.5511 | 2 | 0 | 112
38943.5532 | 2059 | 0 | 112
38943.5553 | 2104 | 0 | 112
38943.5575 | 2200 | 0 | 112
38943.5596 | 2500 | 0 | 112
38943.5618 | 1148 | 0 | 112
38943.5639 | 1162 | 0 | 112
112
38943.534 | 1 | 0 | 113
38943.5361 | 1 | 0 | 113
38943.5383 | 1 | 0 | 113
38943.5404 | 2 | 0 | 113
38943.5425 | 1 | 0 | 113
38943.5447 | 2 | 0 | 113
38943.5468 | 2 | 0 | 113
38943.5489 | 2 | 0 | 113
38943.5511 | 2 | 1 | 113
38943.5532 | 2141 | 0 | 113
38943.5554 | 1910 | 0 | 113
38943.5575 | 2371 | 0 | 113
38943.5596 | 1588 | 0 | 113
38943.5618 | 1688 | 0 | 113
38943.5639 | 778 | 0 | 113
113
38943.534 | 1 | 0 | 114
38943.5361 | 1 | 0 | 114
38943.5383 | 1 | 0 | 114
38943.5404 | 2484 | 0 | 114
38943.5425 | 2 | 0 | 114
38943.5447 | 2114 | 0 | 114
38943.5468 | 2204 | 0 | 114
38943.549 | 2002 | 0 | 114
38943.5511 | 2213 | 0 | 114
38943.5532 | 2115 | 0 | 114
38943.5554 | 2091 | 0 | 114
38943.5575 | 2176 | 0 | 114
38943.5597 | 2570 | 0 | 114
38943.5618 | 2031 | 0 | 114
38943.5639 | 2578 | 0 | 114
114
38943.534 | 1 | 0 | 115
38943.5361 | 1 | 0 | 115
38943.5383 | 1 | 0 | 115
38943.5404 | 5 | 0 | 115
38943.5426 | 2 | 0 | 115
38943.5447 | 4 | 0 | 115
38943.5468 | 4 | 0 | 115
38943.549 | 3 | 0 | 115
38943.5511 | 4 | 0 | 115
38943.5533 | 2148 | 0 | 115
38943.5554 | 1837 | 0 | 115
38943.5575 | 2322 | 0 | 115
38943.5597 | 1365 | 0 | 115
38943.5618 | 1158 | 0 | 115
38943.5639 | 572 | 0 | 115
115
38943.534 | 1 | 0 | 116
38943.5362 | 1 | 0 | 116
38943.5383 | 1 | 0 | 116
38943.5404 | 3 | 0 | 116
38943.5426 | 2098 | 0 | 116
38943.5447 | 2016 | 0 | 116
38943.5469 | 2611 | 0 | 116
38943.549 | 2381 | 0 | 116
38943.5511 | 2416 | 0 | 116
38943.5533 | 2164 | 0 | 116
38943.5554 | 2025 | 0 | 116
38943.5575 | 2416 | 0 | 116
38943.5597 | 2247 | 0 | 116
38943.5618 | 2420 | 0 | 116
38943.564 | 2064 | 0 | 116
116
38943.534 | 1 | 0 | 117
38943.5362 | 1 | 0 | 117
38943.5383 | 1 | 0 | 117
38943.5405 | 2 | 0 | 117
38943.5426 | 4 | 0 | 117
38943.5447 | 4 | 0 | 117
38943.5469 | 4 | 0 | 117
38943.549 | 4 | 0 | 117
38943.5511 | 4 | 0 | 117
38943.5533 | 2158 | 0 | 117
38943.5554 | 1686 | 0 | 117
38943.5576 | 2011 | 0 | 117
38943.5597 | 1837 | 0 | 117
38943.5618 | 1313 | 0 | 117
38943.564 | 959 | 0 | 117
117
38943.5341 | 1 | 0 | 118
38943.5362 | 1 | 0 | 118
38943.5383 | 1 | 0 | 118
38943.5405 | 2 | 0 | 118
38943.5426 | 3 | 0 | 118
38943.5447 | 3 | 0 | 118
38943.5469 | 3 | 0 | 118
38943.549 | 3 | 0 | 118
38943.5512 | 3 | 0 | 118
38943.5533 | 1993 | 0 | 118
38943.5554 | 2383 | 0 | 118
38943.5576 | 1964 | 0 | 118
38943.5597 | 2254 | 0 | 118
38943.5619 | 1173 | 0 | 118
38943.564 | 674 | 0 | 118
118
38943.5341 | 1 | 0 | 119
38943.5362 | 1 | 0 | 119
38943.5383 | 1 | 0 | 119
38943.5405 | 2 | 0 | 119
38943.5426 | 2 | 0 | 119
38943.5448 | 3 | 0 | 119
38943.5469 | 3 | 0 | 119
38943.549 | 3 | 0 | 119
38943.5512 | 3 | 0 | 119
38943.5533 | 2044 | 0 | 119
38943.5555 | 1894 | 0 | 119
38943.5576 | 2096 | 0 | 119
38943.5597 | 1805 | 0 | 119
38943.5619 | 1157 | 0 | 119
38943.564 | 589 | 0 | 119
119
38943.5341 | 1 | 0 | 120
38943.5362 | 1 | 0 | 120
38943.5384 | 1 | 0 | 120
38943.5405 | 2 | 0 | 120
38943.5426 | 2 | 0 | 120
38943.5448 | 2 | 0 | 120
38943.5469 | 2 | 0 | 120
38943.5491 | 3 | 0 | 120
38943.5512 | 2 | 0 | 120
38943.5533 | 2507 | 0 | 120
38943.5555 | 2161 | 0 | 120
38943.5576 | 1948 | 0 | 120
38943.5597 | 1952 | 0 | 120
38943.5619 | 1550 | 0 | 120
38943.564 | 579 | 0 | 120
120
38943.5341 | 1 | 0 | 121
38943.5362 | 1 | 0 | 121
38943.5384 | 1 | 0 | 121
38943.5405 | 2240 | 0 | 121
38943.5427 | 1892 | 0 | 121
38943.5448 | 2572 | 0 | 121
38943.5469 | 2399 | 5 | 121
38943.5491 | 2212 | 0 | 121
38943.5512 | 2254 | 0 | 121
38943.5533 | 2055 | 0 | 121
38943.5555 | 2009 | 0 | 121
38943.5576 | 2542 | 0 | 121
38943.5598 | 2467 | 0 | 121
38943.5619 | 2203 | 0 | 121
38943.564 | 2239 | 0 | 121
121
38943.5341 | 1 | 0 | 122
38943.5363 | 1 | 0 | 122
38943.5384 | 1 | 0 | 122
38943.5405 | 4 | 0 | 122
38943.5427 | 3 | 0 | 122
38943.5448 | 2065 | 0 | 122
38943.5469 | 2115 | 0 | 122
38943.5491 | 2527 | 0 | 122
38943.5512 | 2360 | 0 | 122
38943.5534 | 2130 | 0 | 122
38943.5555 | 2246 | 0 | 122
38943.5576 | 2086 | 0 | 122
38943.5598 | 2583 | 0 | 122
38943.5619 | 2551 | 0 | 122
38943.5641 | 2305 | 0 | 122
122
38943.5341 | 1 | 0 | 123
38943.5363 | 1 | 0 | 123
38943.5384 | 1 | 0 | 123
38943.5405 | 2072 | 0 | 123
38943.5427 | 1291 | 0 | 123
38943.5448 | 2252 | 0 | 123
38943.547 | 2170 | 0 | 123
38943.5491 | 2521 | 0 | 123
38943.5512 | 2178 | 0 | 123
38943.5534 | 2063 | 0 | 123
38943.5555 | 2369 | 0 | 123
38943.5577 | 2540 | 0 | 123
38943.5598 | 2189 | 0 | 123
38943.5619 | 2469 | 0 | 123
38943.5641 | 2266 | 0 | 123
123
38943.5342 | 1 | 0 | 124
38943.5363 | 1 | 0 | 124
38943.5384 | 1 | 0 | 124
38943.5406 | 4 | 0 | 124
38943.5427 | 3 | 0 | 124
38943.5448 | 4 | 0 | 124
38943.547 | 4 | 1 | 124
38943.5491 | 5 | 0 | 124
38943.5513 | 4 | 0 | 124
38943.5534 | 1945 | 0 | 124
38943.5555 | 2161 | 0 | 124
38943.5577 | 2434 | 0 | 124
38943.5598 | 2126 | 0 | 124
38943.562 | 1124 | 0 | 124
38943.5641 | 1142 | 0 | 124
124
38943.5342 | 1 | 0 | 125
38943.5363 | 1 | 0 | 125
38943.5384 | 1 | 0 | 125
38943.5406 | 2354 | 0 | 125
38943.5427 | 7 | 0 | 125
38943.5449 | 2214 | 1 | 125
38943.547 | 2193 | 0 | 125
38943.5491 | 2048 | 0 | 125
38943.5513 | 2606 | 0 | 125
38943.5534 | 2519 | 0 | 125
38943.5556 | 2045 | 0 | 125
38943.5577 | 2467 | 0 | 125
38943.5598 | 2515 | 0 | 125
38943.562 | 2244 | 0 | 125
38943.5641 | 2128 | 0 | 125
125
38943.5342 | 1 | 0 | 126
38943.5363 | 1 | 0 | 126
38943.5385 | 1 | 0 | 126
38943.5406 | 5 | 0 | 126
38943.5427 | 2 | 0 | 126
38943.5449 | 4 | 0 | 126
38943.547 | 4 | 0 | 126
38943.5492 | 4 | 0 | 126
38943.5513 | 4 | 0 | 126
38943.5534 | 2284 | 0 | 126
38943.5556 | 2478 | 0 | 126
38943.5577 | 2029 | 0 | 126
38943.5598 | 2181 | 0 | 126
38943.562 | 1401 | 0 | 126
38943.5641 | 1725 | 1 | 126
126
38943.5342 | 1 | 0 | 127
38943.5363 | 1 | 0 | 127
38943.5385 | 1 | 0 | 127
38943.5406 | 4 | 0 | 127
38943.5428 | 152 | 0 | 127
38943.5449 | 2044 | 0 | 127
38943.547 | 2180 | 0 | 127
38943.5492 | 2516 | 0 | 127
38943.5513 | 2478 | 0 | 127
38943.5534 | 2427 | 0 | 127
38943.5556 | 2156 | 0 | 127
38943.5577 | 1999 | 0 | 127
38943.5599 | 2257 | 0 | 127
38943.562 | 2012 | 0 | 127
38943.5641 | 2029 | 0 | 127
127
38943.5342 | 4 | 0 | 128
38943.5364 | 2 | 0 | 128
38943.5385 | 1 | 0 | 128
38943.5406 | 3 | 0 | 128
38943.5428 | 3 | 0 | 128
38943.5449 | 4 | 0 | 128
38943.5492 | 4 | 0 | 128
38943.5513 | 4 | 0 | 128
38943.5535 | 2004 | 0 | 128
38943.5556 | 2435 | 0 | 128
38943.5577 | 2486 | 0 | 128
38943.5599 | 2183 | 0 | 128
38943.562 | 1368 | 0 | 128
38943.5642 | 1652 | 0 | 128
128
38943.5342 | 1 | 0 | 129
38943.5364 | 1 | 0 | 129
38943.5385 | 1 | 0 | 129
38943.5406 | 3 | 0 | 129
38943.5428 | 2 | 0 | 129
38943.5449 | 2591 | 0 | 129
38943.5471 | 2073 | 0 | 129
38943.5492 | 2227 | 0 | 129
38943.5513 | 2485 | 0 | 129
38943.5535 | 2198 | 0 | 129
38943.5556 | 2253 | 0 | 129
38943.5578 | 2349 | 0 | 129
38943.5599 | 2074 | 0 | 129
38943.562 | 2039 | 0 | 129
38943.5642 | 2046 | 0 | 129
129
38943.5342 | 1 | 0 | 130
38943.5364 | 1 | 0 | 130
38943.5385 | 1 | 0 | 130
38943.5407 | 3 | 0 | 130
38943.5428 | 2 | 1 | 130
38943.5449 | 5 | 0 | 130
38943.5471 | 4 | 0 | 130
38943.5492 | 4 | 0 | 130
38943.5514 | 4 | 0 | 130
38943.5535 | 2088 | 0 | 130
38943.5556 | 1984 | 0 | 130
38943.5578 | 2294 | 0 | 130
38943.5599 | 2216 | 0 | 130
38943.562 | 2037 | 0 | 130
38943.5642 | 1570 | 0 | 130
130
38943.5343 | 1 | 0 | 131
38943.5364 | 1 | 0 | 131
38943.5385 | 1 | 0 | 131
38943.5407 | 2 | 0 | 131
38943.5428 | 2 | 0 | 131
38943.545 | 4 | 0 | 131
38943.5471 | 4 | 0 | 131
38943.5492 | 4 | 0 | 131
38943.5514 | 156 | 144 | 131
38943.5535 | 2447 | 0 | 131
38943.5556 | 1945 | 0 | 131
38943.5578 | 2155 | 0 | 131
38943.5599 | 2492 | 1 | 131
38943.5621 | 1034 | 845 | 131
38943.5642 | 972 | 883 | 131
131
38943.5343 | 1 | 0 | 132
38943.5364 | 1 | 0 | 132
38943.5386 | 1 | 0 | 132
38943.5407 | 2 | 0 | 132
38943.5428 | 2 | 0 | 132
38943.545 | 4 | 0 | 132
38943.5471 | 4 | 0 | 132
38943.5492 | 3 | 0 | 132
38943.5514 | 976 | 938 | 132
38943.5535 | 2342 | 0 | 132
38943.5557 | 2193 | 0 | 132
38943.5578 | 2407 | 1 | 132
38943.5599 | 2374 | 1 | 132
38943.5621 | 1106 | 909 | 132
38943.5642 | 1008 | 981 | 132
132

## Test Facts
Last row in IRMS data sheets: | 20
Time when Penlight power was initiated: | 186