## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 42
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, mixture of XLPE (3) & EPR (3) insulated control cables (Items 10 & 2). Cable specimens present: Six lengths of cable were monitored for electrical performance, 3 each of XLPE and EPR, A seventh length of cable (EPR cable Item #2) was monitored for temperature response, No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 108 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
108 | 0 | Initated Penlight Heating
1195-1203 | 1087-1095 | Conductors C5 & C6 both short to ground at less than 1000 ohms (197 & 213) | EPR Cable C shorts to ground prior to any interaction with other cables
1216 | 1108 | Cable C (C5 & C6) shorts internally at less than 100 ohms (9) | EPR Cable C shorts internally
~1247 | ~1139 | Cables ignite and burn
1267 | 1159 | Power to Penlight is shutoff
1294-1353 | 1186-1245 | Cables A (A1 & A2) and B (B3 & B4) short internally (848 & 15) | XLPE Cable A and EPR Cable B short internally
1413-1434 | 1305-1326 | Conductors D7, E9 & E10 all short to ground (184, <1 & <1) | EPR Cable E is shorted to ground
1437 | 1329 | Cable D (D7 & D8) shorts internally at less than 100 ohms (17) | XLPE Cable D shorts internally
1451-1454 | 1343-1346 | Conductors F11 & F12 both short to ground at less than 100 ohms (1 & <1) | XLPE Cable F is shorted to ground
1462-1479 | 1354-1371 | Cables E (E9 & E10) and F (F11 & F12) short internally at less than 100 ohms (2 & 8); the existing internal short in cable A (A1 & A2) decreases to 2 ohms | EPR Cable E and XLPE Cable F short internally
1484-1507 | 1376-1399 | Conductors A1 & A2 both short to ground at less than 1000 ohms (314 & 338) | XLPE Cable A shorts to ground
1515-1518 | 1407-1410 | Conductor A2 shorts to conductors C5 and C6 at less than 1000 ohms (380 & 152) | Interaction between two thermoset cables but all conductors involved are shorted to ground and shorted internally
1535 | 1427 | Conductor B3 shorts to ground at less than 1000 ohms (180)
1546-1549 | 1438-1441 | Conductor B3 shorts to conductors D7 & D8 at less than 1000 ohms (270 & 179) | Interaction between two thermoset cables but all conductors involved are shorted to ground and shorted internally
1550-1565 | 1442-1457 | Conductor B4 shorts to ground at less than 1000 ohms (103); the existing ground fault on conductor C5 decreases to less than 100 ohms (58) | EPR Cable B is shorted to ground
1569-1571 | 1461-1463 | Conductor B4 shorts to conductors D7 & D8 at less than 1000 ohms (151 & 111) | Interaction between two thermoset cables but all conductors involved are shorted to ground and shorted internally
1573-1602 | 1465-1494 | Conductor D8 shorts to ground at less than 1000 ohms (204); the existing ground faults on conductors C6 and D7 decrease to less than 100 ohms (53 & 47) | All conductors have shorted to external ground.
Additional Observations
Observation 1 | The progression of failure modes for the cable bundle demonstrated a mixture of shorting to ground and internal shorting with no particular bias regarding cable location in the bundle.
Observation 2 | It took 1087 s (18.1min.) from the start of heating for the inital short to ground, it took 1108 s (18.5 min.) for the first internal short, and it took ~1139 s (19 min.) from the start of Penlight heating for the cable bundle to ignite.
Observation 3 | No cable to cable interactions took place prior to the individual cables either shorting to ground or shorting internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A, D, F = XLPE Cable Item #10
B, C, E = EPR Cable Item #2
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 42 |  |  | 2006-08-17 | 14:09
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-107.5 | 211201.9994 | -104.5 | 211201.9994 | -102 | 211201.9994 | -99 | 211201.9994 | -96.5 | 211201.9994 | -76.5 | 211201.9994 | -74 | 211201.9994 | -71 | 211201.9994 | -68.5 | 211201.9994 | -48.5 | 211201.9994 | -46 | 211201.9994 | -43 | 211201.9994 | -40.5 | 211201.9994 | -37.5 | 211201.9994 | -34.5 | 248037.9994 | -32 | 255237.9994 | -23.5 | 211201.9994 | -20.5 | 211201.9994 | -18 | 211201.9994 | -15 | 211201.9994 | -12.5 | 244437.9994 | -9.5 | 64234.4976 | -1 | 211201.9994 | 7.5 | 230937.9994 | 10 | 247937.9994 | 13 | 237937.9994 | 15.5 | 249137.9994 | 24 | 211837.9994 | 27 | 261437.9994 | 29.5 | 256937.9994 | 32.5 | 254537.9994 | 35.5 | 211201.9994 | 38 | 243637.9994 | 41 | 260037.9994 | 49.5 | 217337.9994 | 52 | 255837.9994 | 60.5 | 254537.9994 | 63.5 | 254737.9994 | 66 | 256637.9994 | 68.5 | 257837.9994 | 71.5 | 254637.9994 | 74.5 | 258437.9994 | -104.5 | 211201.9994 | -99 | 211201.9994 | -46 | 211201.9994 | -40.5 | 211201.9994 | -34.5 | 64234.4976 | 7.5 | 211837.9994 | 13 | 237937.9994 | 38 | 217337.9994 | 63.5 | 254637.9994
77.5 | 211201.9994 | 80 | 211201.9994 | 83 | 211201.9994 | 85.5 | 211201.9994 | 88.5 | 211201.9994 | 108 | 211201.9994 | 111 | 211201.9994 | 113.5 | 211201.9994 | 116.5 | 211201.9994 | 136 | 211201.9994 | 139 | 211201.9994 | 141.5 | 211201.9994 | 144.5 | 211201.9994 | 147.5 | 211201.9994 | 150 | 248037.9994 | 153 | 255237.9994 | 161.5 | 211201.9994 | 164 | 211201.9994 | 167 | 211201.9994 | 169.5 | 211201.9994 | 172.5 | 244437.9994 | 175.5 | 257237.9994 | 183.5 | 211201.9994 | 192 | 230937.9994 | 194.5 | 247937.9994 | 197.5 | 237937.9994 | 200.5 | 249137.9994 | 209 | 211837.9994 | 211.5 | 261437.9994 | 214.5 | 256937.9994 | 217.5 | 254537.9994 | 220 | 211201.9994 | 223 | 243637.9994 | 225.5 | 260037.9994 | 234 | 217337.9994 | 237 | 255837.9994 | 245.5 | 254537.9994 | 248 | 254737.9994 | 251 | 256637.9994 | 253.5 | 257837.9994 | 256.5 | 254637.9994 | 259 | 258437.9994 | 80 | 211201.9994 | 85.5 | 211201.9994 | 139 | 211201.9994 | 144.5 | 211201.9994 | 150 | 244437.9994 | 192 | 211837.9994 | 197.5 | 237937.9994 | 223 | 217337.9994 | 248 | 254637.9994
262 | 211201.9994 | 265 | 211201.9994 | 267.5 | 211201.9994 | 270.5 | 211201.9994 | 273 | 211201.9994 | 293 | 211201.9994 | 295.5 | 211201.9994 | 298.5 | 211201.9994 | 301.5 | 211201.9994 | 321 | 211201.9994 | 323.5 | 211201.9994 | 326.5 | 211201.9994 | 329.5 | 211201.9994 | 332 | 211201.9994 | 335 | 248037.9994 | 337.5 | 255237.9994 | 346 | 211201.9994 | 349 | 211201.9994 | 351.5 | 211201.9994 | 354.5 | 211201.9994 | 357.5 | 244437.9994 | 360 | 257237.9994 | 368.5 | 211201.9994 | 376.5 | 230937.9994 | 379.5 | 247937.9994 | 382.5 | 237937.9994 | 385 | 249137.9994 | 393.5 | 211837.9994 | 396.5 | 261437.9994 | 399.5 | 256937.9994 | 402 | 254537.9994 | 404.5 | 211201.9994 | 407.5 | 243637.9994 | 410.5 | 260037.9994 | 419 | 217337.9994 | 421.5 | 255837.9994 | 430 | 254537.9994 | 433 | 254737.9994 | 435.5 | 256637.9994 | 438.5 | 257837.9994 | 441.5 | 254637.9994 | 444 | 258437.9994 | 265 | 211201.9994 | 270.5 | 211201.9994 | 323.5 | 211201.9994 | 329.5 | 211201.9994 | 335 | 244437.9994 | 376.5 | 211837.9994 | 382.5 | 237937.9994 | 407.5 | 217337.9994 | 433 | 254637.9994
446.5 | 211201.9994 | 449.5 | 211201.9994 | 452.5 | 211201.9994 | 455.5 | 211201.9994 | 458 | 211201.9994 | 477.5 | 211201.9994 | 480.5 | 211201.9994 | 483 | 211201.9994 | 486 | 211201.9994 | 505.5 | 211201.9994 | 508.5 | 211201.9994 | 511 | 211201.9994 | 514 | 211201.9994 | 516.5 | 211201.9994 | 519.5 | 248037.9994 | 522.5 | 255237.9994 | 531 | 211201.9994 | 533.5 | 211201.9994 | 536.5 | 211201.9994 | 539 | 211201.9994 | 542 | 244437.9994 | 544.5 | 257237.9994 | 553 | 211201.9994 | 561.5 | 230937.9994 | 564.5 | 247937.9994 | 567 | 237937.9994 | 570 | 249137.9994 | 578.5 | 211837.9994 | 581 | 261437.9994 | 584 | 256937.9994 | 586.5 | 254537.9994 | 589.5 | 211201.9994 | 592.5 | 243637.9994 | 595 | 129968.9988 | 603.5 | 217337.9994 | 606.5 | 255837.9994 | 615 | 254537.9994 | 617.5 | 254737.9994 | 620.5 | 256637.9994 | 623 | 257837.9994 | 626 | 254637.9994 | 628.5 | 258437.9994 | 449.5 | 211201.9994 | 455.5 | 211201.9994 | 508.5 | 211201.9994 | 514 | 211201.9994 | 519.5 | 244437.9994 | 561.5 | 211837.9994 | 567 | 237937.9994 | 592.5 | 129968.9988 | 617.5 | 254637.9994
631.5 | 211201.9994 | 634.5 | 211201.9994 | 637 | 211201.9994 | 640 | 211201.9994 | 642.5 | 211201.9994 | 662.5 | 211201.9994 | 665 | 211201.9994 | 668 | 211201.9994 | 670.5 | 211201.9994 | 690.5 | 211201.9994 | 693 | 211201.9994 | 696 | 211201.9994 | 698.5 | 211201.9994 | 701.5 | 211201.9994 | 704.5 | 248037.9994 | 707 | 255237.9994 | 715.5 | 211201.9994 | 718.5 | 211201.9994 | 721 | 211201.9994 | 724 | 211201.9994 | 726.5 | 244437.9994 | 729.5 | 257237.9994 | 738 | 211201.9994 | 746.5 | 230937.9994 | 749.5 | 123918.9988 | 752 | 237937.9994 | 754.5 | 249137.9994 | 763.5 | 211837.9994 | 766 | 261437.9994 | 768.5 | 256937.9994 | 771.5 | 254537.9994 | 774.5 | 211201.9994 | 777 | 243637.9994 | 780 | 260037.9994 | 788.5 | 217337.9994 | 791.5 | 255837.9994 | 799.5 | 254537.9994 | 802.5 | 254737.9994 | 805 | 256637.9994 | 808 | 257837.9994 | 810.5 | 254637.9994 | 813.5 | 258437.9994 | 634.5 | 211201.9994 | 640 | 211201.9994 | 693 | 211201.9994 | 698.5 | 211201.9994 | 704.5 | 244437.9994 | 746.5 | 123918.9988 | 752 | 237937.9994 | 777 | 217337.9994 | 802.5 | 254637.9994
816.5 | 211201.9994 | 819.5 | 211201.9994 | 822 | 211201.9994 | 824.5 | 211201.9994 | 827.5 | 211201.9994 | 847 | 211201.9994 | 850 | 211201.9994 | 852.5 | 211201.9994 | 855.5 | 211201.9994 | 875 | 211201.9994 | 878 | 211201.9994 | 881 | 211201.9994 | 883.5 | 211201.9994 | 886.5 | 211201.9994 | 889 | 248037.9994 | 892 | 255237.9994 | 900.5 | 211201.9994 | 903 | 211201.9994 | 906 | 211201.9994 | 908.5 | 211201.9994 | 911.5 | 244437.9994 | 914.5 | 257237.9994 | 922.5 | 211201.9994 | 931 | 230937.9994 | 934 | 247937.9994 | 936.5 | 237937.9994 | 939.5 | 249137.9994 | 948 | 211837.9994 | 950.5 | 261437.9994 | 953.5 | 256937.9994 | 956.5 | 254537.9994 | 959 | 211201.9994 | 962 | 243637.9994 | 964.5 | 260037.9994 | 973 | 217337.9994 | 976 | 255837.9994 | 984.5 | 254537.9994 | 987 | 254737.9994 | 990 | 256637.9994 | 992.5 | 257837.9994 | 995.5 | 254637.9994 | 998.5 | 258437.9994 | 819.5 | 211201.9994 | 824.5 | 211201.9994 | 878 | 211201.9994 | 883.5 | 211201.9994 | 889 | 244437.9994 | 931 | 211837.9994 | 936.5 | 237937.9994 | 962 | 217337.9994 | 987 | 254637.9994
1001 | 211201.9994 | 1004 | 211201.9994 | 1006.5 | 211201.9994 | 1009.5 | 211201.9994 | 1012.5 | 211201.9994 | 1032 | 211201.9994 | 1034.5 | 211201.9994 | 1037.5 | 211201.9994 | 1040.5 | 211201.9994 | 1060 | 211201.9994 | 1062.5 | 211201.9994 | 1065.5 | 211201.9994 | 1068.5 | 211201.9994 | 1071 | 211201.9994 | 1074 | 248037.9994 | 1076.5 | 255237.9994 | 1085 | 211201.9994 | 1088 | 211201.9994 | 1090.5 | 211201.9994 | 1093.5 | 211201.9994 | 1096.5 | 244437.9994 | 1099 | 257237.9994 | 1107.5 | 8.6093 | 1116 | 230737.9567 | 1118.5 | 247738.0806 | 1121.5 | 237937.9994 | 1124.5 | 249137.9994 | 1132.5 | 211837.9994 | 1135.5 | 261437.9994 | 1138.5 | 256937.9994 | 1141 | 254537.9994 | 1144 | 211201.9994 | 1146.5 | 243637.9994 | 1149.5 | 260037.9994 | 1158 | 217337.9994 | 1160.5 | 255837.9994 | 1169 | 254537.9994 | 1172 | 254737.9994 | 1174.5 | 256637.9994 | 1177.5 | 257837.9994 | 1180.5 | 254637.9994 | 1183 | 258437.9994 | 1004 | 211201.9994 | 1009.5 | 211201.9994 | 1062.5 | 211201.9994 | 1068.5 | 211201.9994 | 1074 | 244437.9994 | 1116 | 211837.9994 | 1121.5 | 237937.9994 | 1146.5 | 217337.9994 | 1172 | 254637.9994
1186 | 848.214 | 1188.5 | 211201.9994 | 1191.5 | 211201.9994 | 1194.5 | 211201.9994 | 1197 | 211201.9994 | 1216.5 | 211201.9994 | 1219.5 | 211201.9994 | 1222.5 | 211201.9994 | 1225 | 211201.9994 | 1244.5 | 15.4663 | 1247.5 | 20970.5629 | 1250.5 | 105401.0946 | 1253 | 211001.9527 | 1256 | 211201.9994 | 1258.5 | 247838.0806 | 1262 | 255237.9994 | 1270 | 105550.9988 | 1272.5 | 211201.9994 | 1275.5 | 211201.9994 | 1278.5 | 211201.9994 | 1281 | 244437.9994 | 1284 | 257237.9994 | 1292.5 | 3.5186 | 1300.5 | 115368.9784 | 1303.5 | 117079.8485 | 1306.5 | 79245.9982 | 1309 | 62209.4976 | 1317.5 | 105868.9988 | 1320.5 | 130668.9988 | 1323 | 64159.4976 | 1326 | 63559.4976 | 1328.5 | 16.883 | 1331.5 | 182.5288 | 1334.5 | 7658.992 | 1342.5 | 1711.596 | 1345.5 | 63884.4976 | 1354 | 1.9669 | 1356.5 | 1.1592 | 1359.5 | 4.8354 | 1362.5 | 17.9296 | 1365 | 0.1661 | 1368 | 7.6409 | 1188.5 | 211201.9994 | 1194.5 | 211201.9994 | 1247.5 | 20970.5629 | 1253 | 211001.9527 | 1258.5 | 244437.9994 | 1300.5 | 105868.9988 | 1306.5 | 62209.4976 | 1331.5 | 182.5288 | 1356.5 | 0.1661
1370.5 | 2.2391 | 1373.5 | 16679.3631 | 1376.5 | 2406.1758 | 1379 | 99161.6715 | 1382 | 29997.9797 | 1401.5 | 7961.0345 | 1404.5 | 3416.0264 | 1407 | 379.5245 | 1410 | 151.6782 | 1429.5 | 234.312 | 1432 | 8329.4447 | 1435 | 18296.0265 | 1438 | 269.7074 | 1440.5 | 179.4093 | 1443.5 | 234.4167 | 1446.5 | 291.2247 | 1454.5 | 55768.8758 | 1457.5 | 22749.8233 | 1460.5 | 151.3376 | 1463 | 111.1162 | 1466 | 102.3696 | 1468.5 | 166.0824 | 1477 | 67.1542 | 1485.5 | 57.5722 | 1488.5 | 83.8696 | 1491 | 61.5889 | 1494 | 57.6902 | 1502.5 | 52.1783 | 1505 | 123.5918 | 1508 | 108.3937 | 1510.5 | 96.76 | 1513.5 | 19.4667 | 1516.5 | 7751.9172 | 1519 | 17662.1849 | 1527.5 | 203.6726 | 1530 | 264.1555 | 1538.5 | 24.8252 | 1541.5 | 23.737 | 1544 | 56.3186 | 1547 | 2.7064 | 1550 | 25.1274 | 1552.5 | 3.0345 | 1373.5 | 2406.1758 | 1379 | 151.6782 | 1432 | 8329.4447 | 1438 | 111.1162 | 1443.5 | 102.3696 | 1485.5 | 52.1783 | 1491 | 57.6902 | 1516.5 | 203.6726 | 1541.5 | 2.7064
1555.5 | 2.8914 | 1558.5 | 1014.4776 | 1561 | 670.4245 | 1563.5 | 196.6217 | 1566.5 | 488.851 | 1586.5 | 550.1173 | 1589 | 251.1236 | 1592 | 138.0684 | 1594.5 | 183.3056 | 1614.5 | 4.9545 | 1617 | 1354.9983 | 1620 | 3958.3971 | 1622.5 | 195.1679 | 1625.5 | 153.2181 | 1628.5 | 36030.771 | 1631 | 85.5417 | 1639.5 | 1611.7173 | 1642.5 | 2082.1276 | 1645 | 124.6525 | 1648 | 195.8047 | 1650.5 | 39063.7244 | 1653.5 | 156.2126 | 1662 | 52.4619 | 1670.5 | 54.4641 | 1673 | 73.9314 | 1676 | 94.0477 | 1678.5 | 115.8377 | 1687 | 86.0366 | 1690 | 91.052 | 1692.5 | 112.9297 | 1695.5 | 100.363 | 1698.5 | 9.9004 | 1701 | 1386.8151 | 1703.5 | 2595.8049 | 1712 | 137.6003 | 1715 | 238.5298 | 1723.5 | 10.2418 | 1726 | 18.8551 | 1729 | 11.1625 | 1732 | 2.4507 | 1734.5 | 2.35 | 1737.5 | 21.183 | 1558.5 | 251.1236 | 1563.5 | 138.0684 | 1617 | 1354.9983 | 1622.5 | 124.6525 | 1628.5 | 85.5417 | 1670.5 | 54.4641 | 1676 | 94.0477 | 1701 | 137.6003 | 1726 | 2.35
1740.5 | 1.7954 | 1743 | 528.6916 | 1746 | 729.2058 | 1748.5 | 314.8835 | 1751.5 | 670.3954 | 1771 | 495.5586 | 1774 | 334.5775 | 1776.5 | 2728.5009 | 1779.5 | 4009.5582 | 1799 | 5.7371 | 1802 | 7973.9198 | 1804.5 | 46703.3327 | 1807.5 | 148.0036 | 1810.5 | 103.6984 | 1813 | 9058.153 | 1815.5 | 31648.6189 | 1824 | 87.3049 | 1827 | 124.696 | 1829.5 | 112.0181 | 1832.5 | 116.4494 | 1835.5 | 464.9513 | 1838 | 21919.3397 | 1846.5 | 60.3547 | 1855 | 107.0891 | 1857.5 | 92.0905 | 1860.5 | 67.3609 | 1863.5 | 35.9847 | 1872 | 92.3515 | 1874.5 | 76.7766 | 1877.5 | 57.5779 | 1880 | 86.9583 | 1883 | 29.9442 | 1886 | 8342.1618 | 1888.5 | 35406.3014 | 1897 | 187.5364 | 1899.5 | 290.3452 | 1908 | 17.7395 | 1911 | 33.7531 | 1913.5 | 43.5575 | 1916.5 | 20.5489 | 1919.5 | 45.8491 | 1922 | 7.9214 | 1743 | 334.5775 | 1748.5 | 314.8835 | 1802 | 87.3049 | 1807.5 | 103.6984 | 1813 | 464.9513 | 1855 | 76.7766 | 1860.5 | 35.9847 | 1886 | 187.5364 | 1911 | 20.5489
1925 | 17.9266 | 1927.5 | 1355.8855 | 1930.5 | 3088.8415 | 1933.5 | 21848.0748 | 1936 | 20046.796 | 1955.5 | 2793.0473 | 1958.5 | 5985.9914 | 1961.5 | 981.931 | 1964.5 | 1803.4109 | 1983.5 | 20.7766 | 1986.5 | 12682.4375 | 1989.5 | 61027.8123 | 1992 | 196.0642 | 1995 | 192.1837 | 1997.5 | 12760.7962 | 2000.5 | 1490.8843 | 2009 | 34865.8719 | 2011.5 | 55178.4858 | 2014.5 | 115.7405 | 2017.5 | 221.2545 | 2020 | 23001.1728 | 2023 | 547.661 | 2031.5 | 39.0664 | 2039.5 | 326.727 | 2042.5 | 327.2976 | 2045.5 | 347.9583 | 2048 | 336.1453 | 2056.5 | 296.5616 | 2059.5 | 388.5295 | 2062 | 308.9128 | 2065 | 339.4358 | 2067.5 | 3.3359 | 2070.5 | 4748.0287 | 2073.5 | 17896.6942 | 2082 | 297.1761 | 2084.5 | 20721.9946 | 2093 | 138.6845 | 2095.5 | 7699.6768 | 2098.5 | 43.4754 | 2101.5 | 53.9012 | 2104 | 50.2415 | 2107 | 2.0571 | 1927.5 | 1355.8855 | 1933.5 | 981.931 | 1986.5 | 12682.4375 | 1992 | 115.7405 | 1997.5 | 547.661 | 2039.5 | 296.5616 | 2045.5 | 308.9128 | 2070.5 | 297.1761 | 2095.5 | 43.4754
2109.5 | 16.6209 | 2112.5 | 1960.614 | 2115.5 | 3200.7278 | 2118 | 24469 | 2121 | 16319.9956 | 2140.5 | 46530.8317 | 2143.5 | 148046.8133 | 2146 | 27625.8631 | 2149 | 11017.2333 | 2168.5 | 25.7556 | 2171.5 | 20218.4995 | 2174.5 | 28902.2545 | 2177 | 442.6975 | 2179.5 | 302.2735 | 2182.5 | 631.7144 | 2185.5 | 81979.9436 | 2193.5 | 116813.396 | 2196.5 | 26752.2011 | 2199.5 | 439.583 | 2202 | 300.1113 | 2205 | 229.3776 | 2207.5 | 47210.1168 | 2216 | 3.0053 | 2224.5 | 40987.0958 | 2227.5 | 120525.8962 | 2230 | 612.4847 | 2233 | 555.6575 | 2241.5 | 560.047 | 2244.5 | 692.3379 | 2247 | 623.834 | 2249.5 | 644.3468 | 2252.5 | 13.91 | 2255.5 | 9212.4191 | 2258 | 18448.0099 | 2266.5 | 681.9814 | 2269.5 | 823.7948 | 2277.5 | 19.567 | 2280.5 | 31.9757 | 2283.5 | 37.6479 | 2286 | 0.92562 | 2289 | 4.3627 | 2291.5 | 27.1409 | 2112.5 | 1960.614 | 2118 | 11017.2333 | 2171.5 | 20218.4995 | 2177 | 300.1113 | 2182.5 | 229.3776 | 2224.5 | 560.047 | 2230 | 555.6575 | 2255.5 | 681.9814 | 2280.5 | 0.92562
2294.5 | 26.6076 | 2297.5 | 12574.0123 | 2300 | 66518.0919 | 2303 | 8241.5554 | 2305.5 | 4018.3811 | 2325 | 100005.8154 | 2328 | 1537.9212 | 2331 | 15570.8297 | 2333.5 | 4253.1559 | 2353.5 | 7.1063 | 2356 | 18013.5425 | 2359 | 77065.5815 | 2361.5 | 1238.433 | 2364.5 | 900.67 | 2367.5 | 521.6562 | 2370 | 845.5315 | 2378.5 | 53768.2874 | 2381.5 | 164693.6499 | 2384 | 831.0778 | 2387 | 2156.869 | 2389.5 | 59376.3376 | 2392.5 | 933.3339 | 2401 | 698.2731 | 2409.5 | 3200.5001 | 2412 | 4176.4818 | 2415 | 3400.5173 | 2417.5 | 3919.9299 | 2426 | 2040.7274 | 2429 | 3169.1762 | 2432 | 3979.9298 | 2434.5 | 4367.2985 | 2437.5 | 18.4166 | 2440 | 37864.8342 | 2443 | 822.8853 | 2451.5 | 200771.1699 | 2454 | 85212.6648 | 2462.5 | 3123.2176 | 2465.5 | 3007.7304 | 2468 | 3620.7985 | 2471 | 26.9715 | 2473.5 | 15.9567 | 2476.5 | 55.2623 | 2297.5 | 1537.9212 | 2303 | 4018.3811 | 2356 | 18013.5425 | 2361.5 | 831.0778 | 2367.5 | 521.6562 | 2409.5 | 2040.7274 | 2415 | 3400.5173 | 2440 | 822.8853 | 2465.5 | 15.9567

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 42 |  |  | 2006-08-17 | 14:09
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-101.9 | 211202 |  | -79.5 | 211202 | -51.4444 | 211202 | -35.9444 | 64234.5 | -21.6111 | 211202 | -12.9444 | 211202 | 11.2 | 211202 | 16.9 | 105551 | 29.1111 | 211838 | 32.1111 | 247938 | 49.8 | 237938 | 52 | 249138 | -101.9 | 64234.5 | -51.4444 | 64234.5 | -21.6111 | 211202 | -14.8222 | 64234.5 | -6.5417 | 64234.5 | 22.3306 | 105551 | 6.6667 | 211202 | 16.8111 | 211202 | 40.7556 | 211838 | -90.7 | 211202 | -43.6944 | 64234.5 | -17.2778 | 211202 | 14.05 | 105551 | 30.6111 | 211838 | 50.9 | 237938
82.9 | 211202 |  | 105.3 | 211202 | 133.2778 | 211202 | 148.8889 | 211202 | 163.0556 | 211202 | 171.8333 | 211202 | 196 | 211202 | 201.6 | 211202 | 213.8889 | 115419 | 216.9444 | 247938 | 234.5 | 237938 | 236.9 | 249138 | 82.9 | 211202 | 133.2778 | 115419 | 163.0556 | 115419 | 169.9417 | 211202 | 178.25 | 115419 | 207.1083 | 115419 | 191.4306 | 115419 | 201.5722 | 211202 | 225.5583 | 115419 | 94.1 | 211202 | 141.0833 | 211202 | 167.4444 | 211202 | 198.8 | 211202 | 215.4167 | 115419 | 235.7 | 237938
267.6 | 211202 |  | 290.1 | 211202 | 318.1111 | 211202 | 333.6111 | 211202 | 347.8333 | 211202 | 356.6667 | 105551 | 380.7 | 211202 | 386.3 | 211202 | 398.6111 | 211838 | 401.7222 | 247938 | 419.5 | 237938 | 421.6 | 249138 | 267.6 | 105551 | 318.1111 | 211202 | 347.8333 | 105551 | 354.6806 | 211202 | 363.0139 | 211202 | 391.8333 | 211202 | 376.2083 | 105551 | 386.4 | 105551 | 410.3583 | 211838 | 278.85 | 211202 | 325.8611 | 211202 | 352.25 | 105551 | 383.5 | 211202 | 400.1667 | 211838 | 420.55 | 237938
452.4 | 211202 |  | 474.7 | 211202 | 502.7222 | 211202 | 518.3333 | 211202 | 532.6667 | 105551 | 541.2778 | 211202 | 565.5 | 129969 | 571 | 211202 | 583.3889 | 121769 | 586.4444 | 247938 | 604 | 237938 | 606.3 | 249138 | 452.4 | 105551 | 502.7222 | 121769 | 532.6667 | 105551 | 539.3889 | 129969 | 547.7222 | 121769 | 576.5833 | 121769 | 560.9444 | 105551 | 571.0611 | 105551 | 595.0333 | 121769 | 463.55 | 211202 | 510.5278 | 211202 | 536.9722 | 105551 | 568.25 | 129969 | 584.9167 | 121769 | 605.15 | 237938
637.1 | 211202 |  | 659.5 | 211202 | 687.5556 | 211202 | 703.0556 | 211202 | 717.4444 | 123919 | 726.1111 | 211202 | 750.2 | 211202 | 756 | 211202 | 768.1667 | 211838 | 771.2778 | 247938 | 788.9 | 237938 | 791 | 249138 | 637.1 | 123919 | 687.5556 | 211202 | 717.4444 | 123919 | 724.2028 | 211202 | 732.5139 | 211202 | 761.4111 | 211202 | 745.75 | 123919 | 755.8639 | 123919 | 779.8361 | 211838 | 648.3 | 211202 | 695.3056 | 211202 | 721.7778 | 123919 | 753.1 | 211202 | 769.7222 | 211838 | 789.95 | 237938
822 | 211202 |  | 844.3 | 211202 | 872.3889 | 211202 | 887.8889 | 211202 | 902.1111 | 211202 | 910.8889 | 211202 | 935 | 211202 | 940.6 | 211202 | 952.8889 | 211838 | 956 | 247938 | 973.6 | 237938 | 976 | 249138 | 822 | 211202 | 872.3889 | 211202 | 902.1111 | 211202 | 908.9694 | 211202 | 917.2917 | 211202 | 946.1222 | 211202 | 930.4722 | 211202 | 940.65 | 211202 | 964.6222 | 211838 | 833.15 | 211202 | 880.1389 | 211202 | 906.5 | 211202 | 937.8 | 211202 | 954.4444 | 211838 | 974.8 | 237938
1006.7 | 211202 |  | 1029.1 | 211202 | 1057.1111 | 211202 | 1072.6111 | 211202 | 1086.9444 | 197.0039 | 1095.7222 | 213.9375 | 1119.8 | 211202 | 1125.4 | 211202 | 1137.6667 | 211838 | 1140.7222 | 247938 | 1158.5 | 237938 | 1160.7 | 249138 | 1006.7 | 197.0039 | 1057.1111 | 211202 | 1086.9444 | 197.0039 | 1093.7306 | 211202 | 1102.0278 | 211202 | 1130.8972 | 211202 | 1115.2639 | 197.0039 | 1125.4667 | 197.0039 | 1149.3972 | 211838 | 1017.9 | 211202 | 1064.8611 | 211202 | 1091.3333 | 197.0039 | 1122.6 | 211202 | 1139.1944 | 211838 | 1159.6 | 237938
1191.5 | 7297.1596 |  | 1213.9 | 157132.1607 | 1241.8889 | 2030.5199 | 1257.4444 | 4836.0298 | 1271.8333 | 2744.5917 | 1280.5 | 11658.9208 | 1304.6 | 183.7598 | 1310.2 | 1685.784 | 1322.3889 | 0.68222 | 1325.7222 | 0.64743 | 1343.3 | 1.2713 | 1345.5 | 0.64718 | 1191.5 | 2030.5199 | 1241.8889 | 0.64743 | 1271.8333 | 0.64718 | 1278.5333 | 183.7598 | 1286.8611 | 0.64743 | 1315.7278 | 0.64743 | 1300.1111 | 0.64743 | 1310.2833 | 0.64718 | 1334.2278 | 0.64718 | 1202.7 | 7297.1596 | 1249.6667 | 2030.5199 | 1276.1667 | 2744.5917 | 1307.4 | 183.7598 | 1324.0556 | 0.64743 | 1344.4 | 0.64718
1376.3 | 313.5604 |  | 1398.7 | 338.8401 | 1426.6667 | 179.8702 | 1442.2778 | 103.1047 | 1456.5 | 58.4623 | 1465.2778 | 53.0238 | 1489.5 | 47.1109 | 1494.9 | 204.1091 | 1507.2778 | 0.6645 | 1510.3333 | 0.64412 | 1528 | 4.5443 | 1530.2 | 0.80649 | 1376.3 | 53.0238 | 1426.6667 | 0.64412 | 1456.5 | 0.64412 | 1463.3361 | 47.1109 | 1471.6389 | 0.64412 | 1500.5028 | 0.64412 | 1484.8472 | 0.64412 | 1494.9944 | 0.80649 | 1518.9528 | 0.64412 | 1387.5 | 313.5604 | 1434.4722 | 103.1047 | 1460.8889 | 53.0238 | 1492.2 | 47.1109 | 1508.8056 | 0.64412 | 1529.1 | 0.80649
1561 | 39.7317 |  | 1583.5 | 46.4834 | 1611.5556 | 36.0442 | 1627.0556 | 47.4547 | 1641.3333 | 49.4507 | 1650.0556 | 56.6102 | 1674.1 | 107.3726 | 1679.8 | 126.5899 | 1692 | 4.0243 | 1695.1111 | 0.64059 | 1712.8 | 1.4757 | 1715 | 0.6421 | 1561 | 36.0442 | 1611.5556 | 0.64059 | 1641.3333 | 0.64059 | 1648.1278 | 36.0442 | 1656.4306 | 0.64059 | 1685.2528 | 0.64059 | 1669.625 | 0.64059 | 1679.7972 | 0.6421 | 1703.7278 | 0.64059 | 1572.25 | 39.7317 | 1619.3056 | 36.0442 | 1645.6944 | 49.4507 | 1676.95 | 107.3726 | 1693.5556 | 0.64059 | 1713.9 | 0.6421
1745.9 | 40.3981 |  | 1768.3 | 53.0293 | 1796.2222 | 37.0429 | 1811.7222 | 84.8954 | 1826 | 36.765 | 1834.7778 | 56.1383 | 1858.9 | 91.1453 | 1864.5 | 187.9974 | 1876.7778 | 0.67478 | 1879.7222 | 0.70564 | 1897.5 | 0.64135 | 1899.7 | 0.66155 | 1745.9 | 36.765 | 1796.2222 | 0.67478 | 1826 | 0.64135 | 1832.8361 | 37.0429 | 1841.1111 | 0.67478 | 1869.975 | 0.67478 | 1854.3194 | 0.67478 | 1864.4944 | 0.64135 | 1888.425 | 0.64135 | 1757.1 | 40.3981 | 1803.9722 | 37.0429 | 1830.3889 | 36.765 | 1861.7 | 91.1453 | 1878.25 | 0.67478 | 1898.6 | 0.64135
1930.5 | 74.2987 |  | 1953 | 78.4902 | 1980.8333 | 51.1601 | 1996.4444 | 58.6685 | 2010.8333 | 94.7735 | 2019.5556 | 186.4147 | 2043.6 | 67.787 | 2049.3 | 87.7693 | 2061.4444 | 14.5736 | 2064.6667 | 38.0382 | 2082.3 | 3.5191 | 2084.5 | 0.6376 | 1930.5 | 51.1601 | 1980.8333 | 14.5736 | 2010.8333 | 0.6376 | 2017.5444 | 51.1601 | 2025.8472 | 14.5736 | 2054.7528 | 14.5736 | 2039.125 | 14.5736 | 2049.2972 | 0.6376 | 2073.2278 | 0.6376 | 1941.75 | 74.2987 | 1988.6389 | 51.1601 | 2015.1944 | 94.7735 | 2046.45 | 67.787 | 2063.0556 | 14.5736 | 2083.4 | 0.6376
2115.3 | 248.6297 |  | 2137.7 | 192.0308 | 2165.7778 | 62.5219 | 2181.2778 | 114.3383 | 2195.5556 | 16.5889 | 2204.3889 | 21.4385 | 2228.5 | 402.2932 | 2234 | 682.1511 | 2246.3333 | 16.2338 | 2249.4444 | 0.63909 | 2267 | 0.69289 | 2269.3 | 0.64743 | 2115.3 | 16.5889 | 2165.7778 | 0.63909 | 2195.5556 | 0.63909 | 2202.3889 | 62.5219 | 2210.7083 | 0.63909 | 2239.5694 | 0.63909 | 2223.9306 | 0.63909 | 2234.0611 | 0.64743 | 2258.0194 | 0.63909 | 2126.5 | 192.0308 | 2173.5278 | 62.5219 | 2199.9722 | 16.5889 | 2231.25 | 402.2932 | 2247.8889 | 0.63909 | 2268.15 | 0.64743
2300.1 | 297.2009 |  | 2322.4 | 1160.8705 | 2350.5 | 102.8907 | 2366.0556 | 210.6142 | 2380.3889 | 696.3451 | 2389.1111 | 644.3642 | 2413.2 | 826.1375 | 2418.9 | 1274.2687 | 2431.1111 | 30.5302 | 2434.1667 | 0.63024 | 2452 | 6.1248 | 2454 | 13.881 | 2300.1 | 102.8907 | 2350.5 | 0.63024 | 2380.3889 | 0.63024 | 2387.1639 | 102.8907 | 2395.4583 | 0.63024 | 2424.3444 | 0.63024 | 2408.6944 | 0.63024 | 2418.875 | 6.1248 | 2442.8194 | 0.63024 | 2311.25 | 297.2009 | 2358.2778 | 102.8907 | 2384.75 | 644.3642 | 2416.05 | 826.1375 | 2432.6389 | 0.63024 | 2453 | 6.1248

## F11-F12
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 157.8376 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38946.591 | 1 | 0 | 38946.591 | 1 | 0 |  | 74.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38946.5931 | 1 | 0 | 38946.5931 | 1 | 0 |  | 259 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38946.5952 | 1 | 0 | 38946.5953 | 1 | 0 |  | 444 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38946.5974 | 1 | 0 | 38946.5974 | 1 | 0 |  | 628.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38946.5995 | 1 | 0 | 38946.5995 | 1 | 0 |  | 813.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38946.6017 | 1 | 0 | 38946.6017 | 1 | 0 |  | 998.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38946.6038 | 1 | 0 | 38946.6038 | 1 | 0 |  | 1183 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38946.6059 | 2370 | 0 | 38946.6059 | 2238 | 0 |  | 1368 | 1476 | 144.6886 | 0 | 136.63 | 0 | 1.4469 | 0 | 1.3663 | 0 | 1.4469 | 1.3663 | 9.0878 | 15.5219 | 7.6409
38946.6081 | 2473 | 0 | 38946.6081 | 2538 | 0 |  | 1552.5 | 1660.5 | 150.9768 | 0 | 154.9451 | 0 | 1.5098 | 0 | 1.5495 | 0 | 1.5098 | 1.5495 | 4.5443 | 1.8668 | 3.0345
38946.6102 | 2111 | 0 | 38946.6102 | 1974 | 0 |  | 1737.5 | 1845.5 | 128.8767 | 0 | 120.5128 | 0 | 1.2888 | 0 | 1.2051 | 0 | 1.2888 | 1.2051 | 22.4718 | 30.9716 | 21.183
38946.6123 | 2364 | 0 | 38946.6124 | 2061 | 0 |  | 1922 | 2030 | 144.3223 | 0 | 125.8242 | 0 | 1.4432 | 0 | 1.2582 | 0 | 1.4432 | 1.2582 | 9.3646 | 25.443 | 7.9214
38946.6145 | 2496 | 0 | 38946.6145 | 2569 | 0 |  | 2107 | 2215 | 152.381 | 0 | 156.8376 | 0 | 1.5238 | 0 | 1.5684 | 0 | 1.5238 | 1.5684 | 3.5809 | 0.6376 | 2.0571
38946.6166 | 2014 | 0 | 38946.6166 | 1958 | 0 |  | 2291.5 | 2399.5 | 122.9548 | 0 | 119.536 | 0 | 1.2295 | 0 | 1.1954 | 0 | 1.2295 | 1.1954 | 28.3704 | 32.0419 | 27.1409
38946.6188 | 1267 | 810 | 38946.6188 | 1485 | 533 |  | 2476.5 | 2584.5 | 77.3504 | 49.4505 | 90.6593 | 32.5397 | 0.7735 | 0.49451 | 0.90659 | 0.3254 | 0.279 | 0.5812 | 379.8706 | 736.7674 | 55.2623

## E10-F12
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 155.5177 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38946.5909 | 1 | 0 | 38946.5909 | 1 | 0 |  | 71.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38946.5931 | 1 | 0 | 38946.5931 | 1 | 0 |  | 256.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38946.5952 | 1 | 0 | 38946.5952 | 1 | 0 |  | 441.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38946.5973 | 1 | 0 | 38946.5974 | 1 | 0 |  | 626 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38946.5995 | 1 | 0 | 38946.5995 | 1 | 0 |  | 810.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38946.6016 | 1 | 0 | 38946.6016 | 1 | 0 |  | 995.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38946.6038 | 1 | 0 | 38946.6038 | 1 | 0 |  | 1180.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38946.6059 | 2513 | 0 | 38946.6059 | 2531 | 0 |  | 1365 | 1473 | 153.4188 | 0 | 154.5177 | 0 | 1.5342 | 0 | 1.5452 | 0 | 1.5342 | 1.5452 | 1.3681 | 0.64718 | 0.1661
38946.608 | 2016 | 0 | 38946.6081 | 2527 | 0 |  | 1550 | 1658 | 123.0769 | 0 | 154.2735 | 0 | 1.2308 | 0 | 1.5427 | 0 | 1.2308 | 1.5427 | 26.3581 | 0.80649 | 25.1274
38946.6102 | 2453 | 0 | 38946.6102 | 2036 | 0 |  | 1734.5 | 1842.5 | 149.7558 | 0 | 124.2979 | 0 | 1.4976 | 0 | 1.243 | 0 | 1.4976 | 1.243 | 3.8475 | 25.1169 | 2.35
38946.6123 | 1734 | 0 | 38946.6123 | 2161 | 0 |  | 1919.5 | 2027.5 | 105.8608 | 0 | 131.9292 | 0 | 1.0586 | 0 | 1.3193 | 0 | 1.0586 | 1.3193 | 46.9077 | 17.8797 | 45.8491
38946.6144 | 1684 | 0 | 38946.6145 | 2482 | 0 |  | 2104 | 2212 | 102.8083 | 0 | 151.5263 | 0 | 1.0281 | 0 | 1.5153 | 0 | 1.0281 | 1.5153 | 51.2696 | 2.6342 | 50.2415
38946.6166 | 2407 | 0 | 38946.6166 | 2250 | 0 |  | 2289 | 2397 | 146.9475 | 0 | 137.3626 | 0 | 1.4695 | 0 | 1.3736 | 0 | 1.4695 | 1.3736 | 5.8322 | 13.2169 | 4.3627
38946.6187 | 2172 | 0 | 38946.6187 | 1890 | 0 |  | 2473.5 | 2581.5 | 132.6007 | 0 | 115.3846 | 0 | 1.326 | 0 | 1.1538 | 0 | 1.326 | 1.1538 | 17.2827 | 34.782 | 15.9567

## E10-F11
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 157.4713 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38946.5909 | 1 | 0 | 38946.5909 | 1 | 0 |  | 68.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38946.593 | 1 | 0 | 38946.593 | 1 | 0 |  | 253.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38946.5952 | 1 | 0 | 38946.5952 | 1 | 0 |  | 438.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38946.5973 | 1 | 0 | 38946.5973 | 1 | 0 |  | 623 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38946.5994 | 1 | 0 | 38946.5995 | 1 | 0 |  | 808 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38946.6016 | 1 | 0 | 38946.6016 | 1 | 0 |  | 992.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38946.6037 | 1 | 0 | 38946.6037 | 1 | 0 |  | 1177.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38946.6059 | 2163 | 0 | 38946.6059 | 2547 | 0 |  | 1362.5 | 1470.5 | 132.0513 | 0 | 155.4945 | 0 | 1.3205 | 0 | 1.5549 | 0 | 1.3205 | 1.5549 | 19.2501 | 1.2713 | 17.9296
38946.608 | 2475 | 0 | 38946.608 | 2449 | 0 |  | 1547 | 1655 | 151.0989 | 0 | 149.5116 | 0 | 1.511 | 0 | 1.4951 | 0 | 1.511 | 1.4951 | 4.2174 | 5.3238 | 2.7064
38946.6101 | 2481 | 0 | 38946.6102 | 1978 | 0 |  | 1732 | 1840 | 151.4652 | 0 | 120.757 | 0 | 1.5147 | 0 | 1.2076 | 0 | 1.5147 | 1.2076 | 3.9653 | 30.4034 | 2.4507
38946.6123 | 2117 | 0 | 38946.6123 | 2533 | 0 |  | 1916.5 | 2024.5 | 129.243 | 0 | 154.6398 | 0 | 1.2924 | 0 | 1.5464 | 0 | 1.2924 | 1.5464 | 21.8413 | 1.831 | 20.5489
38946.6144 | 1665 | 0 | 38946.6144 | 2480 | 0 |  | 2101.5 | 2209.5 | 101.6484 | 0 | 151.4042 | 0 | 1.0165 | 0 | 1.514 | 0 | 1.0165 | 1.514 | 54.9177 | 4.0073 | 53.9012
38946.6166 | 2563 | 0 | 38946.6166 | 2249 | 0 |  | 2286 | 2394 | 156.4713 | 0 | 137.3016 | 0 | 1.5647 | 0 | 1.373 | 0 | 1.5647 | 1.373 | 0.63909 | 14.6901 | 0.92562
38946.6187 | 2012 | 0 | 38946.6187 | 1279 | 0 |  | 2471 | 2579 | 122.8327 | 0 | 78.083 | 0 | 1.2283 | 0 | 0.78083 | 0 | 1.2283 | 0.78083 | 28.1998 | 101.6716 | 26.9715

## E9-F12
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 156.7387 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38946.5909 | 1 | 0 | 38946.5909 | 1 | 0 |  | 66 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
38946.593 | 1 | 0 | 38946.593 | 1 | 0 |  | 251 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
38946.5951 | 1 | 0 | 38946.5952 | 1 | 0 |  | 435.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
38946.5973 | 1 | 0 | 38946.5973 | 1 | 0 |  | 620.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
38946.5994 | 1 | 0 | 38946.5994 | 1 | 0 |  | 805 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
38946.6016 | 1 | 0 | 38946.6016 | 1 | 0 |  | 990 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
38946.6037 | 1 | 0 | 38946.6037 | 1 | 0 |  | 1174.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
38946.6058 | 2415 | 0 | 38946.6058 | 2361 | 0 |  | 1359.5 | 1467.5 | 147.4359 | 0 | 144.1392 | 0 | 1.4744 | 0 | 1.4414 | 0 | 1.4744 | 1.4414 | 6.3097 | 8.7412 | 4.8354
38946.608 | 1632 | 0 | 38946.608 | 2294 | 0 |  | 1544 | 1652 | 99.6337 | 0 | 140.0488 | 0 | 0.99634 | 0 | 1.4005 | 0 | 0.99634 | 1.4005 | 57.315 | 11.9172 | 56.3186
38946.6101 | 2281 | 0 | 38946.6101 | 2551 | 0 |  | 1729 | 1837 | 139.2552 | 0 | 155.7387 | 0 | 1.3926 | 0 | 1.5574 | 0 | 1.3926 | 1.5574 | 12.555 | 0.6421 | 11.1625
38946.6122 | 1775 | 0 | 38946.6123 | 2180 | 0 |  | 1913.5 | 2021.5 | 108.3639 | 0 | 133.0891 | 0 | 1.0836 | 0 | 1.3309 | 0 | 1.0836 | 1.3309 | 44.6411 | 17.7697 | 43.5575
38946.6144 | 1776 | 0 | 38946.6144 | 2400 | 0 |  | 2098.5 | 2206.5 | 108.4249 | 0 | 146.5201 | 0 | 1.0842 | 0 | 1.4652 | 0 | 1.0842 | 1.4652 | 44.5597 | 6.9742 | 43.4754
38946.6165 | 1850 | 0 | 38946.6165 | 2275 | 0 |  | 2283.5 | 2391.5 | 112.9426 | 0 | 138.8889 | 0 | 1.1294 | 0 | 1.3889 | 0 | 1.1294 | 1.3889 | 38.7773 | 12.8519 | 37.6479
38946.6187 | 69 | 0 | 38946.6187 | 1784 | 0 |  | 2468 | 2576 | 4.2125 | 0 | 108.9133 | 0 | 0.042125 | 0 | 1.0891 | 0 | 0.042125 | 1.0891 | 3620.8406 | 43.9114 | 3620.7985

## E9-F11
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 155.5788 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38946.5908 | 1 | 0 | 38946.5908 | 1 | 0 |  | 63.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38946.593 | 1 | 0 | 38946.593 | 1 | 0 |  | 248 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38946.5951 | 1 | 0 | 38946.5951 | 1 | 0 |  | 433 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38946.5972 | 1 | 0 | 38946.5973 | 1 | 0 |  | 617.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38946.5994 | 1 | 0 | 38946.5994 | 1 | 0 |  | 802.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38946.6015 | 1 | 0 | 38946.6015 | 1 | 0 |  | 987 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38946.6037 | 1 | 0 | 38946.6037 | 1 | 0 |  | 1172 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38946.6058 | 2482 | 0 | 38946.6058 | 2287 | 0 |  | 1356.5 | 1464.5 | 151.5263 | 0 | 139.6215 | 0 | 1.5153 | 0 | 1.3962 | 0 | 1.5153 | 1.3962 | 2.6745 | 11.4289 | 1.1592
38946.6079 | 2039 | 0 | 38946.608 | 1999 | 0 |  | 1541.5 | 1649.5 | 124.4811 | 0 | 122.0391 | 0 | 1.2448 | 0 | 1.2204 | 0 | 1.2448 | 1.2204 | 24.9819 | 27.4827 | 23.737
38946.6101 | 2121 | 0 | 38946.6101 | 2227 | 0 |  | 1726 | 1834 | 129.4872 | 0 | 135.9585 | 0 | 1.2949 | 0 | 1.3596 | 0 | 1.2949 | 1.3596 | 20.1499 | 14.4311 | 18.8551
38946.6122 | 1889 | 0 | 38946.6122 | 2532 | 0 |  | 1911 | 2019 | 115.3236 | 0 | 154.5788 | 0 | 1.1532 | 0 | 1.5458 | 0 | 1.1532 | 1.5458 | 34.9063 | 0.64692 | 33.7531
38946.6144 | 1703 | 1 | 38946.6144 | 2316 | 0 |  | 2095.5 | 2203.5 | 103.9683 | 0.06105 | 141.3919 | 0 | 1.0397 | 0.0006105 | 1.4139 | 0 | 1.0391 | 1.4139 | 49.9624 | 10.0337 | 7699.6768
38946.6165 | 1914 | 0 | 38946.6165 | 2211 | 0 |  | 2280.5 | 2388.5 | 116.8498 | 0 | 134.9817 | 0 | 1.1685 | 0 | 1.3498 | 0 | 1.1685 | 1.3498 | 33.1442 | 15.2592 | 31.9757
38946.6186 | 82 | 0 | 38946.6186 | 1630 | 0 |  | 2465.5 | 2573.5 | 5.0061 | 0 | 99.5116 | 0 | 0.050061 | 0 | 0.99512 | 0 | 0.050061 | 0.99512 | 3007.7805 | 56.3423 | 3007.7304

## E9-E10
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 155.4567 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38946.5908 | 1 | 0 | 38946.5908 | 1 | 0 |  | 60.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.5929 | 1 | 0 | 38946.593 | 1 | 0 |  | 245.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.5951 | 1 | 0 | 38946.5951 | 1 | 0 |  | 430 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.5972 | 1 | 0 | 38946.5972 | 1 | 0 |  | 615 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.5994 | 1 | 0 | 38946.5994 | 1 | 0 |  | 799.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.6015 | 1 | 0 | 38946.6015 | 1 | 0 |  | 984.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.6036 | 1 | 0 | 38946.6036 | 1 | 0 |  | 1169 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.6058 | 2461 | 0 | 38946.6058 | 2530 | 0 |  | 1354 | 1462 | 150.2442 | 0 | 154.4567 | 0 | 1.5024 | 0 | 1.5446 | 0 | 1.5024 | 1.5446 | 3.4693 | 0.64743 | 1.9669
38946.6079 | 2020 | 0 | 38946.6079 | 2206 | 0 |  | 1538.5 | 1646.5 | 123.3211 | 0 | 134.6764 | 0 | 1.2332 | 0 | 1.3468 | 0 | 1.2332 | 1.3468 | 26.0584 | 15.4297 | 24.8252
38946.61 | 2281 | 0 | 38946.6101 | 2506 | 0 |  | 1723.5 | 1831.5 | 139.2552 | 0 | 152.9915 | 0 | 1.3926 | 0 | 1.5299 | 0 | 1.3926 | 1.5299 | 11.6344 | 1.6113 | 10.2418
38946.6122 | 2139 | 0 | 38946.6122 | 1957 | 0 |  | 1908 | 2016 | 130.5861 | 0 | 119.475 | 0 | 1.3059 | 0 | 1.1947 | 0 | 1.3059 | 1.1947 | 19.0453 | 30.1165 | 17.7395
38946.6143 | 1625 | 264 | 38946.6143 | 1628 | 399 |  | 2093 | 2201 | 99.2063 | 16.1172 | 99.3895 | 24.359 | 0.99206 | 0.16117 | 0.99389 | 0.24359 | 0.83089 | 0.75031 | 80.0512 | 125.7075 | 138.6845
38946.6165 | 2107 | 0 | 38946.6165 | 2037 | 0 |  | 2277.5 | 2385.5 | 128.6325 | 0 | 124.359 | 0 | 1.2863 | 0 | 1.2436 | 0 | 1.2863 | 1.2436 | 20.8533 | 25.0064 | 19.567
38946.6186 | 79 | 0 | 38946.6186 | 2199 | 0 |  | 2462.5 | 2570.5 | 4.823 | 0 | 134.2491 | 0 | 0.04823 | 0 | 1.3425 | 0 | 0.04823 | 1.3425 | 3123.2658 | 15.7972 | 3123.2176

## D8-E10
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 156.2503 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38946.5907 | 1 | 0 | 38946.5907 | 1 | 0 |  | 52 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38946.5928 | 1 | 0 | 38946.5929 | 1 | 0 |  | 237 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38946.595 | 1 | 0 | 38946.595 | 1 | 0 |  | 421.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38946.5971 | 1 | 0 | 38946.5971 | 1 | 0 |  | 606.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38946.5993 | 1 | 0 | 38946.5993 | 1 | 0 |  | 791.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38946.6014 | 1 | 0 | 38946.6014 | 1 | 0 |  | 976 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38946.6035 | 1 | 0 | 38946.6035 | 1 | 0 |  | 1160.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38946.6057 | 4 | 0 | 38946.6057 | 2422 | 0 |  | 1345.5 | 1453.5 | 0.2442 | 0 | 147.8632 | 0 | 0.002442 | 0 | 1.4786 | 0 | 0.002442 | 1.4786 | 63884.5 | 5.6722 | 63884.4976
38946.6078 | 702 | 0 | 38946.6078 | 2543 | 0 |  | 1530 | 1638 | 42.8571 | 0 | 155.2503 | 0 | 0.42857 | 0 | 1.5525 | 0 | 0.42857 | 1.5525 | 264.584 | 0.64412 | 264.1555
38946.6099 | 755 | 0 | 38946.61 | 2397 | 0 |  | 1715 | 1823 | 46.0928 | 0 | 146.337 | 0 | 0.46093 | 0 | 1.4634 | 0 | 0.46093 | 1.4634 | 238.9907 | 6.7743 | 238.5298
38946.6121 | 655 | 0 | 38946.6121 | 1558 | 0 |  | 1899.5 | 2007.5 | 39.9878 | 0 | 95.116 | 0 | 0.39988 | 0 | 0.95116 | 0 | 0.39988 | 0.95116 | 290.745 | 64.2734 | 290.3452
38946.6142 | 521 | 4 | 38946.6142 | 1538 | 42 |  | 2084.5 | 2192.5 | 31.8071 | 0.2442 | 93.895 | 2.5641 | 0.31807 | 0.002442 | 0.93895 | 0.025641 | 0.31563 | 0.91331 | 398.7578 | 68.7582 | 20721.9946
38946.6164 | 277 | 0 | 38946.6164 | 2045 | 1 |  | 2269.5 | 2377.5 | 16.9109 | 0 | 124.8474 | 0.06105 | 0.16911 | 0 | 1.2485 | 0.0006105 | 0.16911 | 1.2479 | 823.9639 | 25.2143 | 823.7948
38946.6185 | 3 | 0 | 38946.6185 | 2412 | 0 |  | 2454 | 2562 | 0.18315 | 0 | 147.2527 | 0 | 0.0018315 | 0 | 1.4725 | 0 | 0.0018315 | 1.4725 | 85212.6667 | 6.1103 | 85212.6648

## D8-E9
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 132.746 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38946.5907 | 1 | 0 | 38946.5907 | 1 | 0 |  | 49.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217338 | 217338 | 217337.9994
38946.5928 | 1 | 0 | 38946.5928 | 1 | 0 |  | 234 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217338 | 217338 | 217337.9994
38946.5949 | 1 | 0 | 38946.595 | 1 | 0 |  | 419 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217338 | 217338 | 217337.9994
38946.5971 | 1 | 0 | 38946.5971 | 1 | 0 |  | 603.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217338 | 217338 | 217337.9994
38946.5992 | 1 | 0 | 38946.5992 | 1 | 0 |  | 788.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217338 | 217338 | 217337.9994
38946.6014 | 1 | 0 | 38946.6014 | 1 | 0 |  | 973 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217338 | 217338 | 217337.9994
38946.6035 | 1 | 0 | 38946.6035 | 1 | 0 |  | 1158 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 217338 | 217338 | 217337.9994
38946.6056 | 4 | 1 | 38946.6056 | 2158 | 0 |  | 1342.5 | 1450.5 | 0.2442 | 0.06105 | 131.746 | 0 | 0.002442 | 0.0006105 | 1.3175 | 0 | 0.0018315 | 1.3175 | 1685.784 | 0.79525 | 1711.596
38946.6078 | 715 | 0 | 38946.6078 | 1569 | 0 |  | 1527.5 | 1635.5 | 43.6508 | 0 | 95.7875 | 0 | 0.43651 | 0 | 0.95788 | 0 | 0.43651 | 0.95788 | 204.1091 | 38.5838 | 203.6726
38946.6099 | 913 | 0 | 38946.6099 | 1858 | 0 |  | 1712 | 1820 | 55.7387 | 0 | 113.431 | 0 | 0.55739 | 0 | 1.1343 | 0 | 0.55739 | 1.1343 | 138.1577 | 17.028 | 137.6003
38946.612 | 755 | 0 | 38946.6121 | 2103 | 0 |  | 1897 | 2005 | 46.0928 | 0 | 128.3883 | 0 | 0.46093 | 0 | 1.2839 | 0 | 0.46093 | 1.2839 | 187.9974 | 3.3942 | 187.5364
38946.6142 | 547 | 0 | 38946.6142 | 1822 | 2 |  | 2082 | 2190 | 33.3944 | 0 | 111.2332 | 0.1221 | 0.33394 | 0 | 1.1123 | 0.001221 | 0.33394 | 1.1111 | 297.5101 | 19.4714 | 297.1761
38946.6163 | 278 | 0 | 38946.6163 | 1735 | 0 |  | 2266.5 | 2374.5 | 16.9719 | 0 | 105.9219 | 0 | 0.16972 | 0 | 1.0592 | 0 | 0.16972 | 1.0592 | 682.1511 | 25.3245 | 681.9814
38946.6185 | 38 | 1 | 38946.6185 | 130 | 0 |  | 2451.5 | 2559.5 | 2.3199 | 0.06105 | 7.9365 | 0 | 0.023199 | 0.0006105 | 0.079365 | 0 | 0.022589 | 0.079365 | 5783.9404 | 1572.6 | 200771.1699

## D7-E10
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 158.8144 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38946.5906 | 1 | 0 | 38946.5906 | 1 | 0 |  | 41 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
38946.5927 | 1 | 0 | 38946.5927 | 1 | 0 |  | 225.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
38946.5948 | 1 | 0 | 38946.5949 | 1 | 0 |  | 410.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
38946.597 | 2 | 0 | 38946.597 | 1 | 0 |  | 595 | 703 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129969 | 260038 | 129968.9988
38946.5991 | 1 | 0 | 38946.5991 | 1 | 0 |  | 780 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
38946.6013 | 1 | 0 | 38946.6013 | 1 | 0 |  | 964.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
38946.6034 | 1 | 0 | 38946.6034 | 1 | 0 |  | 1149.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
38946.6055 | 4 | 3 | 38946.6056 | 2384 | 2 |  | 1334.5 | 1442.5 | 0.2442 | 0.18315 | 145.5433 | 0.1221 | 0.002442 | 0.0018315 | 1.4554 | 0.001221 | 0.0006105 | 1.4542 | 8148.9888 | 9.717 | 7658.992
38946.6077 | 829 | 1 | 38946.6077 | 2342 | 0 |  | 1519 | 1627 | 50.6105 | 0.06105 | 142.9792 | 0 | 0.50611 | 0.0006105 | 1.4298 | 0 | 0.50549 | 1.4298 | 216.4155 | 11.0751 | 17662.1849
38946.6098 | 899 | 2 | 38946.6098 | 2522 | 1 |  | 1703.5 | 1811.5 | 54.884 | 0.1221 | 153.9683 | 0.06105 | 0.54884 | 0.001221 | 1.5397 | 0.0006105 | 0.54762 | 1.5391 | 204.246 | 3.1494 | 2595.8049
38946.612 | 768 | 1 | 38946.612 | 2099 | 1 |  | 1888.5 | 1996.5 | 46.8864 | 0.06105 | 128.1441 | 0.06105 | 0.46886 | 0.0006105 | 1.2814 | 0.0006105 | 0.46825 | 1.2808 | 240.3409 | 23.9504 | 35406.3014
38946.6141 | 650 | 3 | 38946.6141 | 1886 | 4 |  | 2073.5 | 2181.5 | 39.6825 | 0.18315 | 115.1404 | 0.2442 | 0.39683 | 0.0018315 | 1.1514 | 0.002442 | 0.39499 | 1.149 | 305.3262 | 38.0382 | 17896.6942
38946.6162 | 328 | 2 | 38946.6162 | 2179 | 1 |  | 2258 | 2366 | 20.0244 | 0.1221 | 133.0281 | 0.06105 | 0.20024 | 0.001221 | 1.3303 | 0.0006105 | 0.19902 | 1.3297 | 720.1358 | 19.3943 | 18448.0099
38946.6184 | 3 | 2 | 38946.6184 | 2585 | 1 |  | 2443 | 2551 | 0.18315 | 0.1221 | 157.8144 | 0.06105 | 0.0018315 | 0.001221 | 1.5781 | 0.0006105 | 0.0006105 | 1.5775 | 826.1375 | 0.63791 | 822.8853

## D7-E9
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 148.8022 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38946.5905 | 1 | 0 | 38946.5906 | 1 | 0 |  | 38 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38946.5927 | 1 | 0 | 38946.5927 | 1 | 0 |  | 223 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38946.5948 | 1 | 0 | 38946.5948 | 1 | 0 |  | 407.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38946.597 | 1 | 0 | 38946.597 | 2 | 0 |  | 592.5 | 700.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 243638 | 121769 | 243637.9994
38946.5991 | 1 | 0 | 38946.5991 | 1 | 0 |  | 777 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38946.6012 | 1 | 0 | 38946.6012 | 1 | 0 |  | 962 | 1070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38946.6034 | 1 | 0 | 38946.6034 | 1 | 0 |  | 1146.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38946.6055 | 4 | 9 | 38946.6055 | 2421 | 4 |  | 1331.5 | 1439.5 | 0.2442 | 0.54945 | 147.8022 | 0.2442 | 0.002442 | 0.0054945 | 1.478 | 0.002442 | 0.0030525 | 1.4756 | 183.7598 | 0.68222 | 182.5288
38946.6077 | 1005 | 4 | 38946.6077 | 1909 | 2 |  | 1516.5 | 1624.5 | 61.3553 | 0.2442 | 116.5446 | 0.1221 | 0.61355 | 0.002442 | 1.1654 | 0.001221 | 0.61111 | 1.1642 | 145.1873 | 27.7274 | 7751.9172
38946.6098 | 925 | 6 | 38946.6098 | 2303 | 3 |  | 1701 | 1809 | 56.4713 | 0.3663 | 140.5983 | 0.18315 | 0.56471 | 0.003663 | 1.406 | 0.0018315 | 0.56105 | 1.4042 | 185.2548 | 5.8467 | 1386.8151
38946.6119 | 755 | 5 | 38946.6119 | 1832 | 2 |  | 1886 | 1994 | 46.0928 | 0.30525 | 111.8437 | 0.1221 | 0.46093 | 0.0030525 | 1.1184 | 0.001221 | 0.45788 | 1.1172 | 228.9286 | 33.0967 | 8342.1618
38946.6141 | 566 | 5 | 38946.6141 | 2128 | 4 |  | 2070.5 | 2178.5 | 34.5543 | 0.30525 | 129.9145 | 0.2442 | 0.34554 | 0.0030525 | 1.2991 | 0.002442 | 0.34249 | 1.2967 | 355.3086 | 14.5736 | 4748.0287
38946.6162 | 283 | 5 | 38946.6162 | 1916 | 4 |  | 2255.5 | 2363.5 | 17.2772 | 0.30525 | 116.9719 | 0.2442 | 0.17277 | 0.0030525 | 1.1697 | 0.002442 | 0.16972 | 1.1673 | 829.665 | 27.2757 | 9212.4191
38946.6183 | 5 | 6 | 38946.6184 | 158 | 3 |  | 2440 | 2548 | 0.30525 | 0.3663 | 9.6459 | 0.18315 | 0.0030525 | 0.003663 | 0.096459 | 0.0018315 | 0.0006105 | 0.094628 | 410877.6123 | 1470.5747 | 37864.8342

## D7-D8
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38946.5905 | 1 | 0 | 38946.5905 | 1 | 0 |  | 35.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5926 | 1 | 0 | 38946.5927 | 1 | 0 |  | 220 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5948 | 1 | 0 | 38946.5948 | 1 | 0 |  | 404.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5969 | 1 | 0 | 38946.5969 | 1 | 0 |  | 589.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5991 | 1 | 0 | 38946.5991 | 1 | 0 |  | 774.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6012 | 1 | 0 | 38946.6012 | 1 | 0 |  | 959 | 1067 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6033 | 1 | 0 | 38946.6034 | 1 | 0 |  | 1144 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6055 | 1171 | 1136 | 38946.6055 | 1148 | 1111 |  | 1328.5 | 1436.5 | 71.4896 | 69.3529 | 70.0855 | 67.8266 | 0.7149 | 0.69353 | 0.70085 | 0.67827 | 0.021368 | 0.022589 | 4275.8604 | 8759.4314 | 16.883
38946.6076 | 1624 | 614 | 38946.6076 | 1692 | 548 |  | 1513.5 | 1621.5 | 99.1453 | 37.4847 | 103.2967 | 33.4554 | 0.99145 | 0.37485 | 1.033 | 0.33455 | 0.61661 | 0.69841 | 47.1109 | 2191.4319 | 19.4667
38946.6098 | 1437 | 817 | 38946.6098 | 1401 | 866 |  | 1698.5 | 1806.5 | 87.7289 | 49.8779 | 85.5311 | 52.8694 | 0.87729 | 0.49878 | 0.85531 | 0.52869 | 0.37851 | 0.32662 | 5190.7615 | 134.6016 | 9.9004
38946.6119 | 1572 | 834 | 38946.6119 | 1565 | 701 |  | 1883 | 1991 | 95.9707 | 50.9158 | 95.5433 | 42.7961 | 0.95971 | 0.50916 | 0.95543 | 0.42796 | 0.45055 | 0.52747 | 91.1453 | 577.4813 | 29.9442
38946.614 | 1212 | 841 | 38946.614 | 1450 | 891 |  | 2067.5 | 2175.5 | 73.9927 | 51.3431 | 88.5226 | 54.3956 | 0.73993 | 0.51343 | 0.88523 | 0.54396 | 0.2265 | 0.34127 | 67.787 | 87.7693 | 3.3359
38946.6162 | 1129 | 861 | 38946.6162 | 1049 | 817 |  | 2252.5 | 2360.5 | 68.9255 | 52.5641 | 64.0415 | 49.8779 | 0.68926 | 0.52564 | 0.64042 | 0.49878 | 0.16361 | 0.14164 | 402.2932 | 3679.9101 | 13.91
38946.6183 | 1173 | 1173 | 38946.6183 | 1119 | 1154 |  | 2437.5 | 2545.5 | 71.6117 | 71.6117 | 68.315 | 70.4518 | 0.71612 | 0.71612 | 0.68315 | 0.70452 | 0 | 0.021368 | 1021.1748 | 1274.2687 | 18.4166

## C6-F12
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 155.4567 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38946.5905 | 1 | 0 | 38946.5905 | 1 | 0 |  | 32.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.5926 | 1 | 0 | 38946.5926 | 1 | 0 |  | 217.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.5947 | 1 | 0 | 38946.5948 | 1 | 0 |  | 402 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.5969 | 1 | 0 | 38946.5969 | 1 | 0 |  | 586.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.599 | 1 | 0 | 38946.599 | 1 | 0 |  | 771.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.6012 | 1 | 0 | 38946.6012 | 1 | 0 |  | 956.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.6033 | 1 | 0 | 38946.6033 | 1 | 0 |  | 1141 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38946.6054 | 4 | 0 | 38946.6055 | 2006 | 0 |  | 1326 | 1434 | 0.2442 | 0 | 122.4664 | 0 | 0.002442 | 0 | 1.2247 | 0 | 0.002442 | 1.2247 | 63559.5 | 26.9382 | 63559.4976
38946.6076 | 1289 | 0 | 38946.6076 | 2160 | 0 |  | 1510.5 | 1618.5 | 78.6935 | 0 | 131.8681 | 0 | 0.78694 | 0 | 1.3187 | 0 | 0.78694 | 1.3187 | 97.5469 | 17.888 | 96.76
38946.6097 | 1266 | 0 | 38946.6097 | 2499 | 0 |  | 1695.5 | 1803.5 | 77.2894 | 0 | 152.5641 | 0 | 0.77289 | 0 | 1.5256 | 0 | 0.77289 | 1.5256 | 101.1359 | 1.896 | 100.363
38946.6119 | 1356 | 0 | 38946.6119 | 2388 | 0 |  | 1880 | 1988 | 82.7839 | 0 | 145.7875 | 0 | 0.82784 | 0 | 1.4579 | 0 | 0.82784 | 1.4579 | 87.7861 | 6.6323 | 86.9583
38946.614 | 579 | 0 | 38946.614 | 2517 | 0 |  | 2065 | 2173 | 35.348 | 0 | 153.663 | 0 | 0.35348 | 0 | 1.5366 | 0 | 0.35348 | 1.5366 | 339.7893 | 1.1673 | 339.4358
38946.6161 | 342 | 0 | 38946.6161 | 2530 | 0 |  | 2249.5 | 2357.5 | 20.8791 | 0 | 154.4567 | 0 | 0.20879 | 0 | 1.5446 | 0 | 0.20879 | 1.5446 | 644.5556 | 0.64743 | 644.3468
38946.6183 | 57 | 0 | 38946.6183 | 2236 | 0 |  | 2434.5 | 2542.5 | 3.4799 | 0 | 136.5079 | 0 | 0.034799 | 0 | 1.3651 | 0 | 0.034799 | 1.3651 | 4367.3333 | 13.881 | 4367.2985

## C6-F11
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 156.9219 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38946.5904 | 1 | 0 | 38946.5905 | 1 | 0 |  | 29.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38946.5926 | 1 | 0 | 38946.5926 | 1 | 0 |  | 214.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38946.5947 | 1 | 0 | 38946.5947 | 1 | 0 |  | 399.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38946.5969 | 1 | 0 | 38946.5969 | 1 | 0 |  | 584 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38946.599 | 1 | 0 | 38946.599 | 1 | 0 |  | 768.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38946.6011 | 1 | 0 | 38946.6011 | 1 | 0 |  | 953.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38946.6033 | 1 | 0 | 38946.6033 | 1 | 0 |  | 1138.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38946.6054 | 4 | 0 | 38946.6054 | 2213 | 0 |  | 1323 | 1431 | 0.2442 | 0 | 135.1038 | 0 | 0.002442 | 0 | 1.351 | 0 | 0.002442 | 1.351 | 64159.5 | 16.1491 | 64159.4976
38946.6075 | 1229 | 0 | 38946.6076 | 2163 | 0 |  | 1508 | 1616 | 75.0305 | 0 | 132.0513 | 0 | 0.75031 | 0 | 1.3205 | 0 | 0.75031 | 1.3205 | 109.144 | 18.834 | 108.3937
38946.6097 | 1203 | 0 | 38946.6097 | 2533 | 0 |  | 1692.5 | 1800.5 | 73.4432 | 0 | 154.6398 | 0 | 0.73443 | 0 | 1.5464 | 0 | 0.73443 | 1.5464 | 113.6642 | 1.4757 | 112.9297
38946.6118 | 1621 | 0 | 38946.6118 | 2554 | 0 |  | 1877.5 | 1985.5 | 98.9621 | 0 | 155.9219 | 0 | 0.98962 | 0 | 1.5592 | 0 | 0.98962 | 1.5592 | 58.5676 | 0.64135 | 57.5779
38946.614 | 628 | 0 | 38946.614 | 2483 | 0 |  | 2062 | 2170 | 38.3394 | 0 | 151.5873 | 0 | 0.38339 | 0 | 1.5159 | 0 | 0.38339 | 1.5159 | 309.2962 | 3.5191 | 308.9128
38946.6161 | 355 | 0 | 38946.6161 | 1979 | 0 |  | 2247 | 2355 | 21.6728 | 0 | 120.8181 | 0 | 0.21673 | 0 | 1.2082 | 0 | 0.21673 | 1.2082 | 624.0507 | 29.8828 | 623.834
38946.6182 | 63 | 0 | 38946.6183 | 2176 | 0 |  | 2432 | 2540 | 3.8462 | 0 | 132.8449 | 0 | 0.038462 | 0 | 1.3284 | 0 | 0.038462 | 1.3284 | 3979.9683 | 18.1241 | 3979.9298

## C6-E10
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 159.6691 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38946.5904 | 1 | 0 | 38946.5904 | 1 | 0 |  | 27 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38946.5925 | 1 | 0 | 38946.5926 | 1 | 0 |  | 211.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38946.5947 | 1 | 0 | 38946.5947 | 1 | 0 |  | 396.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38946.5968 | 1 | 0 | 38946.5968 | 1 | 0 |  | 581 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38946.599 | 1 | 0 | 38946.599 | 1 | 0 |  | 766 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38946.6011 | 1 | 0 | 38946.6011 | 1 | 0 |  | 950.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38946.6032 | 1 | 0 | 38946.6033 | 1 | 0 |  | 1135.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38946.6054 | 2 | 0 | 38946.6054 | 2044 | 0 |  | 1320.5 | 1428.5 | 0.1221 | 0 | 124.7863 | 0 | 0.001221 | 0 | 1.2479 | 0 | 0.001221 | 1.2479 | 130669 | 27.954 | 130668.9988
38946.6075 | 1166 | 0 | 38946.6075 | 2024 | 0 |  | 1505 | 1613 | 71.1844 | 0 | 123.5653 | 0 | 0.71184 | 0 | 1.2357 | 0 | 0.71184 | 1.2357 | 124.3036 | 29.2184 | 123.5918
38946.6097 | 1363 | 0 | 38946.6097 | 1993 | 0 |  | 1690 | 1798 | 83.2112 | 0 | 121.6728 | 0 | 0.83211 | 0 | 1.2167 | 0 | 0.83211 | 1.2167 | 91.8841 | 31.2283 | 91.052
38946.6118 | 1472 | 0 | 38946.6118 | 2270 | 0 |  | 1874.5 | 1982.5 | 89.8657 | 0 | 138.5836 | 0 | 0.89866 | 0 | 1.3858 | 0 | 0.89866 | 1.3858 | 77.6753 | 15.215 | 76.7766
38946.6139 | 535 | 0 | 38946.6139 | 1776 | 0 |  | 2059.5 | 2167.5 | 32.6618 | 0 | 108.4249 | 0 | 0.32662 | 0 | 1.0842 | 0 | 0.32662 | 1.0842 | 388.8561 | 47.2624 | 388.5295
38946.6161 | 330 | 0 | 38946.6161 | 2028 | 0 |  | 2244.5 | 2352.5 | 20.1465 | 0 | 123.8095 | 0 | 0.20147 | 0 | 1.2381 | 0 | 0.20147 | 1.2381 | 692.5394 | 28.9635 | 692.3379
38946.6182 | 80 | 0 | 38946.6182 | 2599 | 0 |  | 2429 | 2537 | 4.884 | 0 | 158.6691 | 0 | 0.04884 | 0 | 1.5867 | 0 | 0.04884 | 1.5867 | 3169.225 | 0.63024 | 3169.1762

## C6-E9
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129.3883 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38946.5904 | 1 | 0 | 38946.5904 | 1 | 0 |  | 24 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38946.5925 | 1 | 0 | 38946.5925 | 1 | 0 |  | 209 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38946.5947 | 1 | 0 | 38946.5947 | 1 | 0 |  | 393.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38946.5968 | 1 | 0 | 38946.5968 | 1 | 0 |  | 578.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38946.5989 | 1 | 0 | 38946.5989 | 1 | 0 |  | 763.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38946.6011 | 1 | 0 | 38946.6011 | 1 | 0 |  | 948 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38946.6032 | 1 | 0 | 38946.6032 | 1 | 0 |  | 1132.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38946.6053 | 2 | 0 | 38946.6054 | 2 | 0 |  | 1317.5 | 1425.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105869 | 105869 | 105868.9988
38946.6075 | 1385 | 0 | 38946.6075 | 2089 | 0 |  | 1502.5 | 1610.5 | 84.5543 | 0 | 127.5336 | 0 | 0.84554 | 0 | 1.2753 | 0 | 0.84554 | 1.2753 | 53.0238 | 1.4543 | 52.1783
38946.6096 | 1135 | 0 | 38946.6096 | 2033 | 0 |  | 1687 | 1795 | 69.2918 | 0 | 124.1148 | 0 | 0.69292 | 0 | 1.2411 | 0 | 0.69292 | 1.2411 | 86.7295 | 4.2489 | 86.0366
38946.6118 | 1098 | 0 | 38946.6118 | 2103 | 0 |  | 1872 | 1980 | 67.033 | 0 | 128.3883 | 0 | 0.67033 | 0 | 1.2839 | 0 | 0.67033 | 1.2839 | 93.0219 | 0.77889 | 92.3515
38946.6139 | 534 | 0 | 38946.6139 | 1665 | 0 |  | 2056.5 | 2164.5 | 32.6007 | 0 | 101.6484 | 0 | 0.32601 | 0 | 1.0165 | 0 | 0.32601 | 1.0165 | 296.8876 | 27.2901 | 296.5616
38946.616 | 321 | 0 | 38946.6161 | 1742 | 0 |  | 2241.5 | 2349.5 | 19.5971 | 0 | 106.3492 | 0 | 0.19597 | 0 | 1.0635 | 0 | 0.19597 | 1.0635 | 560.243 | 21.6636 | 560.047
38946.6182 | 99 | 0 | 38946.6182 | 300 | 0 |  | 2426 | 2534 | 6.044 | 0 | 18.315 | 0 | 0.06044 | 0 | 0.18315 | 0 | 0.06044 | 0.18315 | 2040.7879 | 606.46 | 2040.7274

## C5-F12
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 152.16 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38946.5903 | 1 | 0 | 38946.5903 | 1 | 0 |  | 15.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
38946.5924 | 1 | 0 | 38946.5924 | 1 | 0 |  | 200.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
38946.5945 | 1 | 0 | 38946.5946 | 1 | 0 |  | 385 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
38946.5967 | 1 | 0 | 38946.5967 | 1 | 0 |  | 570 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
38946.5988 | 1 | 0 | 38946.5988 | 1 | 0 |  | 754.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
38946.601 | 1 | 0 | 38946.601 | 1 | 0 |  | 939.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
38946.6031 | 1 | 0 | 38946.6031 | 1 | 0 |  | 1124.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
38946.6052 | 4 | 0 | 38946.6053 | 1160 | 0 |  | 1309 | 1417 | 0.2442 | 0 | 70.8181 | 0 | 0.002442 | 0 | 0.70818 | 0 | 0.002442 | 0.70818 | 62209.5 | 114.8603 | 62209.4976
38946.6074 | 1571 | 0 | 38946.6074 | 2270 | 0 |  | 1494 | 1602 | 95.9096 | 0 | 138.5836 | 0 | 0.9591 | 0 | 1.3858 | 0 | 0.9591 | 1.3858 | 58.6493 | 9.7965 | 57.6902
38946.6095 | 1151 | 0 | 38946.6095 | 2378 | 0 |  | 1678.5 | 1786.5 | 70.2686 | 0 | 145.177 | 0 | 0.70269 | 0 | 1.4518 | 0 | 0.70269 | 1.4518 | 116.5404 | 4.8099 | 115.8377
38946.6117 | 1818 | 0 | 38946.6117 | 2476 | 0 |  | 1863.5 | 1971.5 | 110.989 | 0 | 151.16 | 0 | 1.1099 | 0 | 1.5116 | 0 | 1.1099 | 1.5116 | 37.0946 | 0.66155 | 35.9847
38946.6138 | 571 | 0 | 38946.6138 | 2440 | 0 |  | 2048 | 2156 | 34.8596 | 0 | 148.9621 | 0 | 0.3486 | 0 | 1.4896 | 0 | 0.3486 | 1.4896 | 336.4939 | 2.1467 | 336.1453
38946.6159 | 380 | 0 | 38946.616 | 1940 | 0 |  | 2233 | 2341 | 23.199 | 0 | 118.4371 | 0 | 0.23199 | 0 | 1.1844 | 0 | 0.23199 | 1.1844 | 555.8895 | 28.4732 | 555.6575
38946.6181 | 62 | 0 | 38946.6181 | 2046 | 0 |  | 2417.5 | 2525.5 | 3.7851 | 0 | 124.9084 | 0 | 0.037851 | 0 | 1.2491 | 0 | 0.037851 | 1.2491 | 3919.9677 | 21.8172 | 3919.9299

## C5-F11
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 145.3223 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38946.5902 | 1 | 0 | 38946.5903 | 1 | 0 |  | 13 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38946.5924 | 1 | 0 | 38946.5924 | 1 | 0 |  | 197.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38946.5945 | 1 | 0 | 38946.5945 | 1 | 0 |  | 382.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38946.5967 | 1 | 0 | 38946.5967 | 1 | 0 |  | 567 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38946.5988 | 1 | 0 | 38946.5988 | 1 | 0 |  | 752 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38946.6009 | 1 | 0 | 38946.6009 | 1 | 0 |  | 936.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38946.6031 | 1 | 0 | 38946.6031 | 1 | 0 |  | 1121.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38946.6052 | 3 | 0 | 38946.6052 | 2287 | 1 |  | 1306.5 | 1414.5 | 0.18315 | 0 | 139.6215 | 0.06105 | 0.0018315 | 0 | 1.3962 | 0.0006105 | 0.0018315 | 1.3956 | 79246 | 4.1286 | 79245.9982
38946.6073 | 1465 | 0 | 38946.6074 | 1978 | 0 |  | 1491 | 1599 | 89.4383 | 0 | 120.757 | 0 | 0.89438 | 0 | 1.2076 | 0 | 0.89438 | 1.2076 | 62.4833 | 20.3428 | 61.5889
38946.6095 | 1222 | 0 | 38946.6095 | 2111 | 0 |  | 1676 | 1784 | 74.6032 | 0 | 128.8767 | 0 | 0.74603 | 0 | 1.2888 | 0 | 0.74603 | 1.2888 | 94.7938 | 12.7608 | 94.0477
38946.6116 | 1415 | 0 | 38946.6116 | 2099 | 0 |  | 1860.5 | 1968.5 | 86.3858 | 0 | 128.1441 | 0 | 0.86386 | 0 | 1.2814 | 0 | 0.86386 | 1.2814 | 68.2247 | 13.4054 | 67.3609
38946.6138 | 531 | 0 | 38946.6138 | 2104 | 1 |  | 2045.5 | 2153.5 | 32.4176 | 0 | 128.4493 | 0.06105 | 0.32418 | 0 | 1.2845 | 0.0006105 | 0.32418 | 1.2839 | 348.2825 | 13.1897 | 347.9583
38946.6159 | 334 | 0 | 38946.6159 | 2364 | 0 |  | 2230 | 2338 | 20.3907 | 0 | 144.3223 | 0 | 0.20391 | 0 | 1.4432 | 0 | 0.20391 | 1.4432 | 612.6886 | 0.69289 | 612.4847
38946.618 | 68 | 0 | 38946.6181 | 2243 | 0 |  | 2415 | 2523 | 4.1514 | 0 | 136.9353 | 0 | 0.041514 | 0 | 1.3694 | 0 | 0.041514 | 1.3694 | 3400.5588 | 6.1248 | 3400.5173

## C5-E10
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 151.4274 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38946.5902 | 1 | 0 | 38946.5902 | 1 | 0 |  | 10 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247938 | 247938 | 247937.9994
38946.5923 | 1 | 0 | 38946.5924 | 1 | 0 |  | 194.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247938 | 247938 | 247937.9994
38946.5945 | 1 | 0 | 38946.5945 | 1 | 0 |  | 379.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247938 | 247938 | 247937.9994
38946.5966 | 1 | 0 | 38946.5966 | 1 | 0 |  | 564.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247938 | 247938 | 247937.9994
38946.5988 | 2 | 0 | 38946.5988 | 1 | 0 |  | 749.5 | 857.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123919 | 247938 | 123918.9988
38946.6009 | 1 | 0 | 38946.6009 | 1 | 0 |  | 934 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247938 | 247938 | 247937.9994
38946.603 | 1 | 1 | 38946.6031 | 1 | 0 |  | 1118.5 | 1226.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 614732518.44 | 247938 | 247738.0806
38946.6052 | 2 | 1 | 38946.6052 | 1878 | 1 |  | 1303.5 | 1411.5 | 0.1221 | 0.06105 | 114.652 | 0.06105 | 0.001221 | 0.0006105 | 1.1465 | 0.0006105 | 0.0006105 | 1.1459 | 117127.108 | 89.6078 | 117079.8485
38946.6073 | 1343 | 0 | 38946.6073 | 2352 | 0 |  | 1488.5 | 1596.5 | 81.9902 | 0 | 143.5897 | 0 | 0.8199 | 0 | 1.4359 | 0 | 0.8199 | 1.4359 | 84.6895 | 5.4583 | 83.8696
38946.6095 | 1419 | 0 | 38946.6095 | 2134 | 0 |  | 1673 | 1781 | 86.63 | 0 | 130.2808 | 0 | 0.8663 | 0 | 1.3028 | 0 | 0.8663 | 1.3028 | 74.7977 | 16.2315 | 73.9314
38946.6116 | 1286 | 0 | 38946.6116 | 2464 | 1 |  | 1857.5 | 1965.5 | 78.5104 | 0 | 150.4274 | 0.06105 | 0.7851 | 0 | 1.5043 | 0.0006105 | 0.7851 | 1.5037 | 92.8756 | 0.70564 | 92.0905
38946.6137 | 580 | 0 | 38946.6137 | 1725 | 0 |  | 2042.5 | 2150.5 | 35.409 | 0 | 105.3114 | 0 | 0.35409 | 0 | 1.0531 | 0 | 0.35409 | 1.0531 | 327.6517 | 43.7901 | 327.2976
38946.6159 | 401 | 1 | 38946.6159 | 1042 | 0 |  | 2227.5 | 2335.5 | 24.4811 | 0.06105 | 63.6142 | 0 | 0.24481 | 0.0006105 | 0.63614 | 0 | 0.2442 | 0.63614 | 520.7882 | 138.0403 | 120525.8962
38946.618 | 58 | 0 | 38946.618 | 2400 | 0 |  | 2412 | 2520 | 3.5409 | 0 | 146.5201 | 0 | 0.035409 | 0 | 1.4652 | 0 | 0.035409 | 1.4652 | 4176.5172 | 3.3492 | 4176.4818

## C5-E9
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 141.0488 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38946.5902 | 1 | 0 | 38946.5902 | 1 | 0 |  | 7.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38946.5923 | 1 | 0 | 38946.5923 | 2 | 0 |  | 192 | 300 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230938 | 115419 | 230937.9994
38946.5945 | 1 | 0 | 38946.5945 | 1 | 0 |  | 376.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38946.5966 | 1 | 0 | 38946.5966 | 1 | 0 |  | 561.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38946.5987 | 1 | 0 | 38946.5987 | 1 | 0 |  | 746.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38946.6009 | 1 | 0 | 38946.6009 | 1 | 0 |  | 931 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38946.603 | 2 | 1 | 38946.603 | 1 | 1 |  | 1116 | 1224 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 230837.9567 | 533092559.9075 | 230737.9567
38946.6052 | 1 | 2 | 38946.6052 | 1 | 1 |  | 1300.5 | 1408.5 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 230937.9134 | 533323398.5187 | 115368.9784
38946.6073 | 1458 | 0 | 38946.6073 | 2294 | 0 |  | 1485.5 | 1593.5 | 89.011 | 0 | 140.0488 | 0 | 0.89011 | 0 | 1.4005 | 0 | 0.89011 | 1.4005 | 58.4623 | 0.71404 | 57.5722
38946.6094 | 1487 | 0 | 38946.6094 | 2221 | 0 |  | 1670.5 | 1778.5 | 90.7814 | 0 | 135.5922 | 0 | 0.90781 | 0 | 1.3559 | 0 | 0.90781 | 1.3559 | 55.3719 | 4.0243 | 54.4641
38946.6116 | 1112 | 0 | 38946.6116 | 1946 | 0 |  | 1855 | 1963 | 67.8877 | 0 | 118.8034 | 0 | 0.67888 | 0 | 1.188 | 0 | 0.67888 | 1.188 | 107.768 | 18.7246 | 107.0891
38946.6137 | 541 | 0 | 38946.6137 | 1654 | 0 |  | 2039.5 | 2147.5 | 33.0281 | 0 | 100.9768 | 0 | 0.33028 | 0 | 1.0098 | 0 | 0.33028 | 1.0098 | 327.0573 | 39.6844 | 326.727
38946.6158 | 334 | 1 | 38946.6159 | 1831 | 0 |  | 2224.5 | 2332.5 | 20.3907 | 0.06105 | 111.7827 | 0 | 0.20391 | 0.0006105 | 1.1178 | 0 | 0.2033 | 1.1178 | 600.394 | 26.1813 | 40987.0958
38946.618 | 70 | 0 | 38946.618 | 1118 | 0 |  | 2409.5 | 2517.5 | 4.2735 | 0 | 68.254 | 0 | 0.042735 | 0 | 0.68254 | 0 | 0.042735 | 0.68254 | 3200.5429 | 106.653 | 3200.5001

## C5-C6
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38946.5901 | 1 | 0 | 38946.5901 | 1 | 0 |  | -1 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5922 | 1 | 0 | 38946.5922 | 1 | 0 |  | 183.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5944 | 1 | 0 | 38946.5944 | 1 | 0 |  | 368.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5965 | 1 | 0 | 38946.5965 | 1 | 0 |  | 553 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5986 | 1 | 0 | 38946.5987 | 1 | 0 |  | 738 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6008 | 1 | 0 | 38946.6008 | 1 | 0 |  | 922.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6029 | 936 | 1045 | 38946.6029 | 1161 | 1197 |  | 1107.5 | 1215.5 | 57.1429 | 63.7973 | 70.8791 | 73.0769 | 0.57143 | 0.63797 | 0.70879 | 0.73077 | 0.066545 | 0.021978 | 197.0039 | 213.9375 | 8.6093
38946.6051 | 1062 | 1015 | 38946.6051 | 912 | 870 |  | 1292.5 | 1400.5 | 64.8352 | 61.9658 | 55.6777 | 53.1136 | 0.64835 | 0.61966 | 0.55678 | 0.53114 | 0.028694 | 0.025641 | 2744.5917 | 11658.9208 | 3.5186
38946.6072 | 1475 | 285 | 38946.6072 | 1364 | 294 |  | 1477 | 1585 | 90.0488 | 17.3993 | 83.2723 | 17.9487 | 0.90049 | 0.17399 | 0.83272 | 0.17949 | 0.7265 | 0.65324 | 67.2085 | 118.4118 | 67.1542
38946.6093 | 1428 | 393 | 38946.6094 | 1258 | 397 |  | 1662 | 1770 | 87.1795 | 23.9927 | 76.801 | 24.2369 | 0.87179 | 0.23993 | 0.76801 | 0.24237 | 0.63187 | 0.52564 | 78.6144 | 240.1719 | 52.4619
38946.6115 | 1264 | 425 | 38946.6115 | 1285 | 448 |  | 1846.5 | 1954.5 | 77.1673 | 25.9463 | 78.4493 | 27.3504 | 0.77167 | 0.25946 | 0.78449 | 0.2735 | 0.51221 | 0.51099 | 151.2183 | 153.1273 | 60.3547
38946.6136 | 1139 | 665 | 38946.6136 | 995 | 577 |  | 2031.5 | 2139.5 | 69.536 | 40.5983 | 60.7448 | 35.2259 | 0.69536 | 0.40598 | 0.60745 | 0.35226 | 0.28938 | 0.25519 | 279.9003 | 527.7285 | 39.0664
38946.6157 | 1304 | 975 | 38946.6158 | 1119 | 833 |  | 2216 | 2324 | 79.6093 | 59.5238 | 68.315 | 50.8547 | 0.79609 | 0.59524 | 0.68315 | 0.50855 | 0.20085 | 0.1746 | 16.5889 | 21.4385 | 3.0053
38946.6179 | 311 | 211 | 38946.6179 | 661 | 521 |  | 2401 | 2509 | 18.9866 | 12.8816 | 40.3541 | 31.8071 | 0.18987 | 0.12882 | 0.40354 | 0.31807 | 0.06105 | 0.08547 | 2167.2097 | 1252.1746 | 698.2731

## B4-E10
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 157.105 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38946.59 | 4 | 0 | 38946.59 | 1 | 0 |  | -9.5 | 98.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 64234.5 | 257238 | 64234.4976
38946.5921 | 1 | 0 | 38946.5921 | 1 | 0 |  | 175.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38946.5943 | 1 | 0 | 38946.5943 | 1 | 0 |  | 360 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38946.5964 | 1 | 0 | 38946.5964 | 1 | 0 |  | 544.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38946.5985 | 1 | 0 | 38946.5986 | 1 | 0 |  | 729.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38946.6007 | 1 | 0 | 38946.6007 | 1 | 0 |  | 914.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38946.6028 | 1 | 0 | 38946.6028 | 1 | 0 |  | 1099 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38946.605 | 1 | 0 | 38946.605 | 1 | 0 |  | 1284 | 1392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38946.6071 | 965 | 0 | 38946.6071 | 2180 | 0 |  | 1468.5 | 1576.5 | 58.9133 | 0 | 133.0891 | 0 | 0.58913 | 0 | 1.3309 | 0 | 0.58913 | 1.3309 | 166.6715 | 18.045 | 166.0824
38946.6092 | 1002 | 0 | 38946.6092 | 2557 | 0 |  | 1653.5 | 1761.5 | 61.1722 | 0 | 156.105 | 0 | 0.61172 | 0 | 1.5611 | 0 | 0.61172 | 1.5611 | 156.8244 | 0.64059 | 156.2126
38946.6114 | 1037 | 1 | 38946.6114 | 2206 | 0 |  | 1838 | 1946 | 63.3089 | 0.06105 | 134.6764 | 0 | 0.63309 | 0.0006105 | 1.3468 | 0 | 0.63248 | 1.3468 | 149.1638 | 16.6537 | 21919.3397
38946.6135 | 1069 | 119 | 38946.6135 | 1394 | 43 |  | 2023 | 2131 | 65.2625 | 7.265 | 85.1038 | 2.6252 | 0.65263 | 0.07265 | 0.85104 | 0.026252 | 0.57998 | 0.82479 | 184.3519 | 88.8305 | 547.661
38946.6156 | 792 | 1 | 38946.6157 | 1891 | 0 |  | 2207.5 | 2315.5 | 48.3516 | 0.06105 | 115.4457 | 0 | 0.48352 | 0.0006105 | 1.1545 | 0 | 0.48291 | 1.1545 | 225.9978 | 36.0857 | 47210.1168
38946.6178 | 249 | 0 | 38946.6178 | 1895 | 24 |  | 2392.5 | 2500.5 | 15.2015 | 0 | 115.6899 | 1.4652 | 0.15201 | 0 | 1.1569 | 0.014652 | 0.15201 | 1.1422 | 933.4859 | 37.5404 | 933.3339

## B4-E9
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 149.2906 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38946.59 | 1 | 0 | 38946.59 | 1 | 0 |  | -12.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.5921 | 1 | 0 | 38946.5921 | 1 | 0 |  | 172.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.5942 | 1 | 0 | 38946.5942 | 1 | 0 |  | 357.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.5964 | 1 | 0 | 38946.5964 | 1 | 0 |  | 542 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.5985 | 1 | 0 | 38946.5985 | 1 | 0 |  | 726.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.6006 | 1 | 0 | 38946.6007 | 1 | 0 |  | 911.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.6028 | 1 | 0 | 38946.6028 | 1 | 0 |  | 1096.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.6049 | 1 | 0 | 38946.6049 | 1 | 0 |  | 1281 | 1389 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38946.6071 | 1204 | 0 | 38946.6071 | 2403 | 0 |  | 1466 | 1574 | 73.5043 | 0 | 146.7033 | 0 | 0.73504 | 0 | 1.467 | 0 | 0.73504 | 1.467 | 103.1047 | 1.7636 | 102.3696
38946.6092 | 1325 | 1 | 38946.6092 | 1592 | 0 |  | 1650.5 | 1758.5 | 80.8913 | 0.06105 | 97.1917 | 0 | 0.80891 | 0.0006105 | 0.97192 | 0 | 0.8083 | 0.97192 | 84.7402 | 53.6043 | 39063.7244
38946.6113 | 1056 | 2 | 38946.6114 | 2429 | 1 |  | 1835.5 | 1943.5 | 64.4689 | 0.1221 | 148.2906 | 0.06105 | 0.64469 | 0.001221 | 1.4829 | 0.0006105 | 0.64347 | 1.4823 | 183.3905 | 0.67478 | 464.9513
38946.6135 | 1194 | 1 | 38946.6135 | 2002 | 18 |  | 2020 | 2128 | 72.8938 | 0.06105 | 122.2222 | 1.0989 | 0.72894 | 0.0006105 | 1.2222 | 0.010989 | 0.72833 | 1.2112 | 105.285 | 22.542 | 23001.1728
38946.6156 | 825 | 93 | 38946.6156 | 2104 | 1 |  | 2205 | 2313 | 50.3663 | 5.6777 | 128.4493 | 0.06105 | 0.50366 | 0.056777 | 1.2845 | 0.0006105 | 0.44689 | 1.2839 | 1018.3401 | 16.2338 | 229.3776
38946.6178 | 240 | 1 | 38946.6178 | 1787 | 1 |  | 2389.5 | 2497.5 | 14.652 | 0.06105 | 109.0965 | 0.06105 | 0.14652 | 0.0006105 | 1.091 | 0.0006105 | 0.14591 | 1.0904 | 933.3463 | 36.8656 | 59376.3376

## B4-D8
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38946.5899 | 1 | 0 | 38946.5899 | 2 | 0 |  | -15 | 93 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38946.5921 | 1 | 0 | 38946.5921 | 1 | 0 |  | 169.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5942 | 1 | 0 | 38946.5942 | 1 | 0 |  | 354.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5963 | 1 | 0 | 38946.5964 | 1 | 0 |  | 539 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5985 | 1 | 0 | 38946.5985 | 1 | 0 |  | 724 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6006 | 1 | 0 | 38946.6006 | 1 | 0 |  | 908.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6028 | 1 | 0 | 38946.6028 | 1 | 0 |  | 1093.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6049 | 1 | 0 | 38946.6049 | 1 | 0 |  | 1278.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.607 | 998 | 0 | 38946.607 | 561 | 0 |  | 1463 | 1571 | 60.928 | 0 | 34.2491 | 0 | 0.60928 | 0 | 0.34249 | 0 | 0.60928 | 0.34249 | 111.7255 | 276.6524 | 111.1162
38946.6092 | 1158 | 212 | 38946.6092 | 1182 | 246 |  | 1648 | 1756 | 70.696 | 12.9426 | 72.1612 | 15.0183 | 0.70696 | 0.12943 | 0.72161 | 0.15018 | 0.57753 | 0.57143 | 122.6696 | 126.5899 | 195.8047
38946.6113 | 1263 | 346 | 38946.6113 | 1018 | 376 |  | 1832.5 | 1940.5 | 77.1062 | 21.1233 | 62.149 | 22.9548 | 0.77106 | 0.21123 | 0.62149 | 0.22955 | 0.55983 | 0.39194 | 102.3902 | 398.5116 | 116.4494
38946.6134 | 1056 | 278 | 38946.6135 | 834 | 296 |  | 2017.5 | 2125.5 | 64.4689 | 16.9719 | 50.9158 | 18.0708 | 0.64469 | 0.16972 | 0.50916 | 0.18071 | 0.47497 | 0.32845 | 150.1646 | 375.208 | 221.2545
38946.6156 | 920 | 282 | 38946.6156 | 577 | 303 |  | 2202 | 2310 | 56.1661 | 17.2161 | 35.2259 | 18.4982 | 0.56166 | 0.17216 | 0.35226 | 0.18498 | 0.3895 | 0.16728 | 193.5341 | 1307.9367 | 300.1113
38946.6177 | 393 | 74 | 38946.6177 | 226 | 141 |  | 2387 | 2495 | 23.9927 | 4.5177 | 13.7973 | 8.6081 | 0.23993 | 0.045177 | 0.13797 | 0.086081 | 0.19475 | 0.051893 | 543.1332 | 3196.1982 | 2156.869

## B4-D7
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38946.5899 | 1 | 0 | 38946.5899 | 1 | 0 |  | -18 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.592 | 1 | 0 | 38946.592 | 1 | 0 |  | 167 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5942 | 1 | 0 | 38946.5942 | 1 | 0 |  | 351.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5963 | 1 | 0 | 38946.5963 | 1 | 0 |  | 536.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5984 | 1 | 0 | 38946.5985 | 1 | 0 |  | 721 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6006 | 1 | 0 | 38946.6006 | 1 | 0 |  | 906 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6027 | 1 | 0 | 38946.6027 | 1 | 0 |  | 1090.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6049 | 1 | 0 | 38946.6049 | 1 | 0 |  | 1275.5 | 1383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.607 | 839 | 0 | 38946.607 | 311 | 0 |  | 1460.5 | 1568.5 | 51.221 | 0 | 18.9866 | 0 | 0.51221 | 0 | 0.18987 | 0 | 0.51221 | 0.18987 | 151.8498 | 579.4277 | 151.3376
38946.6091 | 1381 | 221 | 38946.6092 | 1295 | 256 |  | 1645 | 1753 | 84.3101 | 13.4921 | 79.0598 | 15.6288 | 0.8431 | 0.13492 | 0.7906 | 0.15629 | 0.70818 | 0.63431 | 75.3848 | 116.9587 | 124.6525
38946.6113 | 1324 | 347 | 38946.6113 | 862 | 317 |  | 1829.5 | 1937.5 | 80.8303 | 21.1844 | 52.6252 | 19.3529 | 0.8083 | 0.21184 | 0.52625 | 0.19353 | 0.59646 | 0.33272 | 84.8954 | 729.0362 | 112.0181
38946.6134 | 1456 | 268 | 38946.6134 | 963 | 248 |  | 2014.5 | 2122.5 | 88.8889 | 16.3614 | 58.7912 | 15.1404 | 0.88889 | 0.16361 | 0.58791 | 0.1514 | 0.72527 | 0.43651 | 58.6685 | 393.4574 | 115.7405
38946.6156 | 769 | 223 | 38946.6156 | 634 | 305 |  | 2199.5 | 2307.5 | 46.9475 | 13.6142 | 38.7057 | 18.6203 | 0.46947 | 0.13614 | 0.38706 | 0.1862 | 0.33333 | 0.20085 | 261.4921 | 696.4627 | 439.583
38946.6177 | 507 | 168 | 38946.6177 | 296 | 200 |  | 2384 | 2492 | 30.9524 | 10.2564 | 18.0708 | 12.21 | 0.30952 | 0.10256 | 0.18071 | 0.1221 | 0.20696 | 0.058608 | 480.8886 | 3339.4766 | 831.0778

## B4-C6
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38946.5899 | 1 | 0 | 38946.5899 | 1 | 0 |  | -20.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.592 | 1 | 0 | 38946.592 | 1 | 0 |  | 164 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5941 | 1 | 0 | 38946.5942 | 1 | 0 |  | 349 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5963 | 1 | 0 | 38946.5963 | 1 | 0 |  | 533.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5984 | 1 | 0 | 38946.5984 | 1 | 0 |  | 718.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6005 | 1 | 0 | 38946.6006 | 1 | 0 |  | 903 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6027 | 1 | 0 | 38946.6027 | 1 | 0 |  | 1088 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6048 | 1 | 0 | 38946.6048 | 1 | 0 |  | 1272.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.607 | 1022 | 2 | 38946.607 | 1231 | 1 |  | 1457.5 | 1565.5 | 62.3932 | 0.1221 | 75.1526 | 0.06105 | 0.62393 | 0.001221 | 0.75153 | 0.0006105 | 0.62271 | 0.75092 | 107.2558 | 71.7633 | 22749.8233
38946.6091 | 1234 | 15 | 38946.6091 | 1362 | 15 |  | 1642.5 | 1750.5 | 75.3358 | 0.91575 | 83.1502 | 0.91575 | 0.75336 | 0.0091575 | 0.8315 | 0.0091575 | 0.7442 | 0.82234 | 73.7122 | 56.6102 | 2082.1276
38946.6112 | 938 | 0 | 38946.6113 | 1288 | 0 |  | 1827 | 1935 | 57.265 | 0 | 78.6325 | 0 | 0.57265 | 0 | 0.78632 | 0 | 0.57265 | 0.78632 | 125.2687 | 64.0543 | 124.696
38946.6134 | 1329 | 1 | 38946.6134 | 624 | 0 |  | 2011.5 | 2119.5 | 81.1355 | 0.06105 | 38.0952 | 0 | 0.81136 | 0.0006105 | 0.38095 | 0 | 0.81074 | 0.38095 | 59.0563 | 238.625 | 55178.4858
38946.6155 | 816 | 4 | 38946.6155 | 367 | 2 |  | 2196.5 | 2304.5 | 49.8168 | 0.2442 | 22.4054 | 0.1221 | 0.49817 | 0.002442 | 0.22405 | 0.001221 | 0.49573 | 0.22283 | 159.8956 | 480.0066 | 26752.2011
38946.6177 | 359 | 1 | 38946.6177 | 129 | 1 |  | 2381.5 | 2489.5 | 21.917 | 0.06105 | 7.8755 | 0.06105 | 0.21917 | 0.0006105 | 0.078755 | 0.0006105 | 0.21856 | 0.078144 | 490.0379 | 1552.4907 | 164693.6499

## B4-C5
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38946.5898 | 1 | 0 | 38946.5898 | 1 | 0 |  | -23.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.592 | 1 | 0 | 38946.592 | 1 | 0 |  | 161.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5941 | 1 | 0 | 38946.5941 | 1 | 0 |  | 346 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5962 | 1 | 0 | 38946.5963 | 2 | 0 |  | 531 | 639 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38946.5984 | 1 | 0 | 38946.5984 | 1 | 0 |  | 715.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6005 | 1 | 0 | 38946.6005 | 1 | 0 |  | 900.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6027 | 1 | 0 | 38946.6027 | 1 | 0 |  | 1085 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6048 | 2 | 0 | 38946.6048 | 2 | 0 |  | 1270 | 1378 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38946.6069 | 757 | 1 | 38946.6069 | 1244 | 1 |  | 1454.5 | 1562.5 | 46.2149 | 0.06105 | 75.9463 | 0.06105 | 0.46215 | 0.0006105 | 0.75946 | 0.0006105 | 0.46154 | 0.75885 | 179.7076 | 69.9444 | 55768.8758
38946.6091 | 1196 | 23 | 38946.6091 | 1262 | 27 |  | 1639.5 | 1747.5 | 73.0159 | 1.4042 | 77.0452 | 1.6484 | 0.73016 | 0.014042 | 0.77045 | 0.016484 | 0.71612 | 0.75397 | 80.403 | 70.8346 | 1611.7173
38946.6112 | 1124 | 0 | 38946.6112 | 1545 | 0 |  | 1824 | 1932 | 68.6203 | 0 | 94.3223 | 0 | 0.6862 | 0 | 0.94322 | 0 | 0.6862 | 0.94322 | 87.9911 | 36.765 | 87.3049
38946.6133 | 1052 | 2 | 38946.6134 | 723 | 1 |  | 2009 | 2117 | 64.2247 | 0.1221 | 44.1392 | 0.06105 | 0.64225 | 0.001221 | 0.44139 | 0.0006105 | 0.64103 | 0.44078 | 101.1495 | 192.7875 | 34865.8719
38946.6155 | 741 | 1 | 38946.6155 | 314 | 1 |  | 2193.5 | 2301.5 | 45.2381 | 0.06105 | 19.1697 | 0.06105 | 0.45238 | 0.0006105 | 0.1917 | 0.0006105 | 0.45177 | 0.19109 | 185.4516 | 575.7587 | 116813.396
38946.6176 | 382 | 3 | 38946.6176 | 144 | 3 |  | 2378.5 | 2486.5 | 23.3211 | 0.18315 | 8.7912 | 0.18315 | 0.23321 | 0.0018315 | 0.087912 | 0.0018315 | 0.23138 | 0.086081 | 456.9913 | 1403.0002 | 53768.2874

## B3-E10
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 155.884 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38946.5897 | 1 | 0 | 38946.5897 | 1 | 0 |  | -32 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38946.5919 | 1 | 0 | 38946.5919 | 1 | 0 |  | 153 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38946.594 | 1 | 0 | 38946.594 | 1 | 0 |  | 337.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38946.5961 | 1 | 0 | 38946.5962 | 1 | 0 |  | 522.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38946.5983 | 1 | 0 | 38946.5983 | 1 | 0 |  | 707 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38946.6004 | 1 | 0 | 38946.6004 | 1 | 0 |  | 892 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38946.6026 | 1 | 0 | 38946.6026 | 1 | 0 |  | 1076.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
| 1 | 0 | 38946.6047 | 1 | 0 |  | 1262 | 1370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38946.6068 | 652 | 0 | 38946.6069 | 2537 | 0 |  | 1446.5 | 1554.5 | 39.8046 | 0 | 154.884 | 0 | 0.39805 | 0 | 1.5488 | 0 | 0.39805 | 1.5488 | 291.6227 | 0.64564 | 291.2247
38946.609 | 1370 | 0 | 38946.609 | 2480 | 0 |  | 1631 | 1739 | 83.6386 | 0 | 151.4042 | 0 | 0.83639 | 0 | 1.514 | 0 | 0.83639 | 1.514 | 86.3781 | 2.9589 | 85.5417
38946.6111 | 1160 | 1 | 38946.6111 | 1973 | 0 |  | 1815.5 | 1923.5 | 70.8181 | 0.06105 | 120.4518 | 0 | 0.70818 | 0.0006105 | 1.2045 | 0 | 0.70757 | 1.2045 | 120.5763 | 29.4161 | 31648.6189
38946.6133 | 1358 | 26 | 38946.6133 | 1766 | 86 |  | 2000.5 | 2108.5 | 82.906 | 1.5873 | 107.8144 | 5.2503 | 0.82906 | 0.015873 | 1.0781 | 0.052503 | 0.81319 | 1.0256 | 93.4208 | 49.5849 | 1490.8843
38946.6154 | 811 | 1 | 38946.6154 | 1352 | 1 |  | 2185.5 | 2293.5 | 49.5116 | 0.06105 | 82.5397 | 0.06105 | 0.49512 | 0.0006105 | 0.8254 | 0.0006105 | 0.49451 | 0.82479 | 215.4076 | 88.9558 | 81979.9436
38946.6175 | 270 | 0 | 38946.6175 | 1983 | 1 |  | 2370 | 2478 | 16.4835 | 0 | 121.0623 | 0.06105 | 0.16484 | 0 | 1.2106 | 0.0006105 | 0.16484 | 1.21 | 845.6963 | 28.8285 | 845.5315

## B3-E9
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 151.4884 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38946.5897 | 1 | 0 | 38946.5897 | 1 | 0 |  | -34.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38946.5918 | 1 | 0 | 38946.5919 | 1 | 0 |  | 150 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38946.594 | 1 | 0 | 38946.594 | 1 | 0 |  | 335 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38946.5961 | 1 | 0 | 38946.5961 | 1 | 0 |  | 519.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38946.5983 | 1 | 0 | 38946.5983 | 1 | 0 |  | 704.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38946.6004 | 1 | 0 | 38946.6004 | 1 | 0 |  | 889 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38946.6025 | 1 | 0 | 38946.6025 | 1 | 0 |  | 1074 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38946.6047 | 1 | 1 | 38946.6047 | 1 | 0 |  | 1258.5 | 1366.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 615228494.44 | 248038 | 247838.0806
38946.6068 | 741 | 0 | 38946.6068 | 2465 | 0 |  | 1443.5 | 1551.5 | 45.2381 | 0 | 150.4884 | 0 | 0.45238 | 0 | 1.5049 | 0 | 0.45238 | 1.5049 | 234.8691 | 0.6645 | 234.4167
38946.6089 | 1174 | 1 | 38946.609 | 1797 | 0 |  | 1628.5 | 1736.5 | 71.6728 | 0.06105 | 109.707 | 0 | 0.71673 | 0.0006105 | 1.0971 | 0 | 0.71612 | 1.0971 | 111.7061 | 38.0846 | 36030.771
38946.6111 | 1140 | 2 | 38946.6111 | 2146 | 1 |  | 1813 | 1921 | 69.5971 | 0.1221 | 131.0134 | 0.06105 | 0.69597 | 0.001221 | 1.3101 | 0.0006105 | 0.69475 | 1.3095 | 119.2111 | 15.6415 | 9058.153
38946.6132 | 1151 | 2 | 38946.6132 | 2005 | 1 |  | 1997.5 | 2105.5 | 70.2686 | 0.1221 | 122.4054 | 0.06105 | 0.70269 | 0.001221 | 1.2241 | 0.0006105 | 0.70147 | 1.2234 | 116.6396 | 23.7816 | 12760.7962
38946.6154 | 1111 | 62 | 38946.6154 | 1751 | 25 |  | 2182.5 | 2290.5 | 67.8266 | 3.7851 | 106.8987 | 1.5263 | 0.67827 | 0.037851 | 1.069 | 0.015263 | 0.64042 | 1.0537 | 151.6101 | 42.7245 | 631.7144
38946.6175 | 399 | 0 | 38946.6175 | 1902 | 1 |  | 2367.5 | 2475.5 | 24.359 | 0 | 116.1172 | 0.06105 | 0.24359 | 0 | 1.1612 | 0.0006105 | 0.24359 | 1.1606 | 521.8997 | 30.5302 | 521.6562

## B3-D8
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38946.5897 | 1 | 0 | 38946.5897 | 1 | 0 |  | -37.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5918 | 1 | 0 | 38946.5918 | 1 | 0 |  | 147.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5939 | 1 | 0 | 38946.594 | 1 | 0 |  | 332 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5961 | 1 | 0 | 38946.5961 | 1 | 0 |  | 516.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5982 | 1 | 0 | 38946.5982 | 1 | 0 |  | 701.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6004 | 1 | 0 | 38946.6004 | 1 | 0 |  | 886.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6025 | 1 | 0 | 38946.6025 | 1 | 0 |  | 1071 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6046 | 1 | 0 | 38946.6047 | 1 | 0 |  | 1256 | 1364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6068 | 755 | 0 | 38946.6068 | 75 | 0 |  | 1440.5 | 1548.5 | 46.0928 | 0 | 4.5788 | 0 | 0.46093 | 0 | 0.045788 | 0 | 0.46093 | 0.045788 | 179.8702 | 2717.36 | 179.4093
38946.6089 | 1348 | 210 | 38946.6089 | 1233 | 260 |  | 1625.5 | 1733.5 | 82.2955 | 12.8205 | 75.2747 | 15.873 | 0.82295 | 0.12821 | 0.75275 | 0.15873 | 0.69475 | 0.59402 | 77.6073 | 137.9385 | 153.2181
38946.6111 | 1359 | 340 | 38946.6111 | 1082 | 397 |  | 1810.5 | 1918.5 | 82.967 | 20.757 | 66.0562 | 24.2369 | 0.82967 | 0.20757 | 0.66056 | 0.24237 | 0.6221 | 0.41819 | 78.5646 | 573.7993 | 103.6984
38946.6132 | 1282 | 240 | 38946.6132 | 954 | 289 |  | 1995 | 2103 | 78.2662 | 14.652 | 58.2418 | 17.6435 | 0.78266 | 0.14652 | 0.58242 | 0.17643 | 0.63614 | 0.40598 | 85.2791 | 355.4049 | 192.1837
38946.6153 | 1199 | 210 | 38946.6153 | 614 | 219 |  | 2179.5 | 2287.5 | 73.199 | 12.8205 | 37.4847 | 13.37 | 0.73199 | 0.12821 | 0.37485 | 0.1337 | 0.60379 | 0.24115 | 94.6101 | 916.6997 | 302.2735
38946.6175 | 530 | 153 | 38946.6175 | 103 | 22 |  | 2364.5 | 2472.5 | 32.3565 | 9.3407 | 6.2882 | 1.3431 | 0.32357 | 0.093407 | 0.062882 | 0.013431 | 0.23016 | 0.049451 | 426.429 | 2650.3122 | 900.67

## B3-D7
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38946.5896 | 1 | 0 | 38946.5896 | 1 | 0 |  | -40.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5918 | 1 | 0 | 38946.5918 | 1 | 0 |  | 144.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5939 | 1 | 0 | 38946.5939 | 1 | 0 |  | 329.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.596 | 1 | 0 | 38946.5961 | 1 | 0 |  | 514 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5982 | 1 | 0 | 38946.5982 | 1 | 0 |  | 698.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6003 | 1 | 0 | 38946.6003 | 1 | 0 |  | 883.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6025 | 1 | 0 | 38946.6025 | 1 | 0 |  | 1068.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6046 | 2 | 1 | 38946.6046 | 1 | 1 |  | 1253 | 1361 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211101.9527 | 445851546.4873 | 211001.9527
38946.6067 | 571 | 0 | 38946.6068 | 38 | 0 |  | 1438 | 1546 | 34.8596 | 0 | 2.3199 | 0 | 0.3486 | 0 | 0.023199 | 0 | 0.3486 | 0.023199 | 270.056 | 5460.5789 | 269.7074
38946.6089 | 1307 | 169 | 38946.6089 | 1268 | 217 |  | 1622.5 | 1730.5 | 79.7924 | 10.3175 | 77.4115 | 13.2479 | 0.79792 | 0.10317 | 0.77411 | 0.13248 | 0.69475 | 0.64164 | 82.1963 | 107.3726 | 195.1679
38946.611 | 1294 | 307 | 38946.611 | 931 | 362 |  | 1807.5 | 1915.5 | 78.9988 | 18.7424 | 56.8376 | 22.1001 | 0.78999 | 0.18742 | 0.56838 | 0.221 | 0.60256 | 0.34737 | 86.3901 | 788.1696 | 148.0036
38946.6131 | 1232 | 252 | 38946.6132 | 963 | 319 |  | 1992 | 2100 | 75.2137 | 15.3846 | 58.7912 | 19.475 | 0.75214 | 0.15385 | 0.58791 | 0.19475 | 0.59829 | 0.39316 | 96.6904 | 366.154 | 196.0642
38946.6153 | 1064 | 177 | 38946.6153 | 536 | 196 |  | 2177 | 2285 | 64.9573 | 10.8059 | 32.7228 | 11.9658 | 0.64957 | 0.10806 | 0.32723 | 0.11966 | 0.54151 | 0.20757 | 120.9913 | 885.9422 | 442.6975
38946.6174 | 621 | 108 | 38946.6174 | 316 | 189 |  | 2361.5 | 2469.5 | 37.9121 | 6.5934 | 19.2918 | 11.5385 | 0.37912 | 0.065934 | 0.19292 | 0.11538 | 0.31319 | 0.077534 | 292.9871 | 2875.5982 | 1238.433

## B3-C6
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38946.5896 | 1 | 0 | 38946.5896 | 1 | 0 |  | -43 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5917 | 1 | 0 | 38946.5917 | 1 | 0 |  | 141.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5939 | 1 | 0 | 38946.5939 | 1 | 0 |  | 326.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.596 | 1 | 0 | 38946.596 | 1 | 0 |  | 511 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5981 | 1 | 0 | 38946.5982 | 1 | 0 |  | 696 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6003 | 1 | 0 | 38946.6003 | 1 | 0 |  | 881 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6024 | 1 | 0 | 38946.6024 | 1 | 0 |  | 1065.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6046 | 2 | 2 | 38946.6046 | 1 | 2 |  | 1250.5 | 1358.5 | 0.1221 | 0.1221 | 0.06105 | 0.1221 | 0.001221 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 222925623.02 | 211201.8105 | 105401.0946
38946.6067 | 585 | 4 | 38946.6067 | 1099 | 1 |  | 1435 | 1543 | 35.7143 | 0.2442 | 67.094 | 0.06105 | 0.35714 | 0.002442 | 0.67094 | 0.0006105 | 0.3547 | 0.67033 | 264.9729 | 92.3833 | 18296.0265
38946.6088 | 1152 | 9 | 38946.6089 | 1328 | 7 |  | 1620 | 1728 | 70.3297 | 0.54945 | 81.0745 | 0.42735 | 0.7033 | 0.0054945 | 0.81074 | 0.0042735 | 0.6978 | 0.80647 | 85.2006 | 59.7981 | 3958.3971
38946.611 | 1083 | 1 | 38946.611 | 1154 | 0 |  | 1804.5 | 1912.5 | 66.1172 | 0.06105 | 70.4518 | 0 | 0.66117 | 0.0006105 | 0.70452 | 0 | 0.66056 | 0.70452 | 95.3019 | 83.104 | 46703.3327
38946.6131 | 1231 | 1 | 38946.6131 | 651 | 1 |  | 1989.5 | 2097.5 | 75.1526 | 0.06105 | 39.7436 | 0.06105 | 0.75153 | 0.0006105 | 0.39744 | 0.0006105 | 0.75092 | 0.39683 | 71.7348 | 225.4096 | 61027.8123
38946.6153 | 1005 | 3 | 38946.6153 | 458 | 2 |  | 2174.5 | 2282.5 | 61.3553 | 0.18315 | 27.9609 | 0.1221 | 0.61355 | 0.0018315 | 0.27961 | 0.001221 | 0.61172 | 0.27839 | 110.6718 | 364.3871 | 28902.2545
38946.6174 | 407 | 2 | 38946.6174 | 204 | 2 |  | 2359 | 2467 | 24.8474 | 0.1221 | 12.4542 | 0.1221 | 0.24847 | 0.001221 | 0.12454 | 0.001221 | 0.24725 | 0.12332 | 421.4592 | 947.2848 | 77065.5815

## B3-C5
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38946.5896 | 1 | 0 | 38946.5896 | 1 | 0 |  | -46 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5917 | 1 | 0 | 38946.5917 | 1 | 0 |  | 139 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5938 | 1 | 0 | 38946.5939 | 1 | 0 |  | 323.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.596 | 1 | 0 | 38946.596 | 1 | 0 |  | 508.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5981 | 1 | 0 | 38946.5981 | 1 | 0 |  | 693 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6003 | 1 | 0 | 38946.6003 | 1 | 0 |  | 878 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6024 | 1 | 0 | 38946.6024 | 1 | 0 |  | 1062.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6045 | 3 | 10 | 38946.6045 | 2 | 5 |  | 1247.5 | 1355.5 | 0.18315 | 0.6105 | 0.1221 | 0.30525 | 0.0018315 | 0.006105 | 0.001221 | 0.0030525 | 0.0042735 | 0.0018315 | 30204.1238 | 70757.7755 | 20970.5629
38946.6067 | 549 | 8 | 38946.6067 | 1211 | 5 |  | 1432 | 1540 | 33.5165 | 0.4884 | 73.9316 | 0.30525 | 0.33516 | 0.004884 | 0.73932 | 0.0030525 | 0.33028 | 0.73626 | 294.9206 | 74.8997 | 8329.4447
38946.6088 | 1274 | 20 | 38946.6088 | 1426 | 15 |  | 1617 | 1725 | 77.7778 | 1.221 | 87.0574 | 0.91575 | 0.77778 | 0.01221 | 0.87057 | 0.0091575 | 0.76557 | 0.86142 | 69.1373 | 49.4507 | 1354.9983
38946.6109 | 1127 | 5 | 38946.611 | 1256 | 2 |  | 1802 | 1910 | 68.8034 | 0.30525 | 76.6789 | 0.1221 | 0.68803 | 0.0030525 | 0.76679 | 0.001221 | 0.68498 | 0.76557 | 88.4563 | 68.4663 | 7973.9198
38946.6131 | 1295 | 4 | 38946.6131 | 801 | 3 |  | 1986.5 | 2094.5 | 79.0598 | 0.2442 | 48.9011 | 0.18315 | 0.7906 | 0.002442 | 0.48901 | 0.0018315 | 0.78816 | 0.48718 | 63.4822 | 165.393 | 12682.4375
38946.6152 | 918 | 5 | 38946.6152 | 321 | 2 |  | 2171.5 | 2279.5 | 56.044 | 0.30525 | 19.5971 | 0.1221 | 0.56044 | 0.0030525 | 0.19597 | 0.001221 | 0.55739 | 0.19475 | 131.0165 | 564.4629 | 20218.4995
38946.6174 | 362 | 9 | 38946.6174 | 151 | 4 |  | 2356 | 2464 | 22.1001 | 0.54945 | 9.2186 | 0.2442 | 0.221 | 0.0054945 | 0.092186 | 0.002442 | 0.21551 | 0.089744 | 496.9838 | 1342.0555 | 18013.5425

## B3-B4
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38946.5895 | 1 | 0 | 38946.5895 | 1 | 0 |  | -48.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5917 | 1 | 0 | 38946.5917 | 1 | 0 |  | 136 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5938 | 1 | 0 | 38946.5938 | 1 | 0 |  | 321 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5959 | 1 | 0 | 38946.596 | 1 | 0 |  | 505.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5981 | 1 | 0 | 38946.5981 | 1 | 0 |  | 690.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6002 | 1 | 0 | 38946.6002 | 1 | 0 |  | 875 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6024 | 1 | 0 | 38946.6024 | 1 | 0 |  | 1060 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6045 | 998 | 963 | 38946.6045 | 1090 | 1059 |  | 1244.5 | 1352.5 | 60.928 | 58.7912 | 66.5446 | 64.652 | 0.60928 | 0.58791 | 0.66545 | 0.64652 | 0.021368 | 0.018926 | 2030.5199 | 4836.0298 | 15.4663
38946.6066 | 728 | 366 | 38946.6067 | 1125 | 775 |  | 1429.5 | 1537.5 | 44.4444 | 22.3443 | 68.6813 | 47.3138 | 0.44444 | 0.22344 | 0.68681 | 0.47314 | 0.221 | 0.21368 | 472.5397 | 531.2146 | 234.312
38946.6088 | 1596 | 565 | 38946.6088 | 1363 | 503 |  | 1614.5 | 1722.5 | 97.4359 | 34.4933 | 83.2112 | 30.7082 | 0.97436 | 0.34493 | 0.83211 | 0.30708 | 0.62943 | 0.52503 | 36.0442 | 140.0571 | 4.9545
38946.6109 | 1542 | 645 | 38946.6109 | 1371 | 571 |  | 1799 | 1907 | 94.1392 | 39.3773 | 83.6996 | 34.8596 | 0.94139 | 0.39377 | 0.837 | 0.3486 | 0.54762 | 0.4884 | 37.0429 | 100.0763 | 5.7371
38946.6131 | 1384 | 509 | 38946.6131 | 1649 | 469 |  | 1983.5 | 2091.5 | 84.4933 | 31.0745 | 100.6716 | 28.6325 | 0.84493 | 0.31074 | 1.0067 | 0.28632 | 0.53419 | 0.72039 | 51.1601 | 92.5493 | 20.7766
38946.6152 | 1294 | 615 | 38946.6152 | 1205 | 585 |  | 2168.5 | 2276.5 | 78.9988 | 37.5458 | 73.5653 | 35.7143 | 0.78999 | 0.37546 | 0.73565 | 0.35714 | 0.41453 | 0.37851 | 163.1961 | 347.1881 | 25.7556
38946.6173 | 1274 | 933 | 38946.6173 | 1135 | 825 |  | 2353.5 | 2461.5 | 77.7778 | 56.9597 | 69.2918 | 50.3663 | 0.77778 | 0.5696 | 0.69292 | 0.50366 | 0.20818 | 0.18926 | 114.8584 | 239.5488 | 7.1063

## A2-C6
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38946.5893 | 1 | 0 | 38946.5893 | 1 | 0 |  | -68.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5914 | 1 | 0 | 38946.5915 | 1 | 0 |  | 116.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5936 | 1 | 0 | 38946.5936 | 2 | 0 |  | 301.5 | 409.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38946.5957 | 1 | 0 | 38946.5957 | 1 | 0 |  | 486 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5979 | 1 | 0 | 38946.5979 | 1 | 0 |  | 670.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6 | 1 | 0 | 38946.6 | 1 | 0 |  | 855.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6021 | 1 | 0 | 38946.6022 | 1 | 0 |  | 1040.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6043 | 1 | 0 | 38946.6043 | 1 | 0 |  | 1225 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6064 | 860 | 394 | 38946.6064 | 868 | 262 |  | 1410 | 1518 | 52.5031 | 24.0537 | 52.9915 | 15.9951 | 0.52503 | 0.24054 | 0.52991 | 0.15995 | 0.28449 | 0.36996 | 426.6964 | 228.6127 | 151.6782
38946.6086 | 1523 | 125 | 38946.6086 | 1179 | 69 |  | 1594.5 | 1702.5 | 92.9792 | 7.6313 | 71.978 | 4.2125 | 0.92979 | 0.076313 | 0.71978 | 0.042125 | 0.85348 | 0.67766 | 46.4834 | 97.1359 | 183.3056
38946.6107 | 1387 | 8 | 38946.6107 | 1200 | 24 |  | 1779.5 | 1887.5 | 84.6764 | 0.4884 | 73.2601 | 1.4652 | 0.84676 | 0.004884 | 0.7326 | 0.014652 | 0.84188 | 0.71795 | 53.0293 | 80.7452 | 4009.5582
38946.6128 | 1033 | 39 | 38946.6128 | 769 | 65 |  | 1964.5 | 2072.5 | 63.0647 | 2.381 | 46.9475 | 3.9683 | 0.63065 | 0.02381 | 0.46947 | 0.039683 | 0.60684 | 0.42979 | 110.7401 | 208.277 | 1803.4109
38946.615 | 344 | 12 | 38946.615 | 532 | 10 |  | 2149 | 2257 | 21.0012 | 0.7326 | 32.4786 | 0.6105 | 0.21001 | 0.007326 | 0.32479 | 0.006105 | 0.20269 | 0.31868 | 539.2498 | 303.9572 | 11017.2333
38946.6171 | 208 | 38 | 38946.6171 | 329 | 48 |  | 2333.5 | 2441.5 | 12.6984 | 2.3199 | 20.0855 | 2.9304 | 0.12698 | 0.023199 | 0.20085 | 0.029304 | 0.10379 | 0.17155 | 1160.8705 | 644.3642 | 4253.1559

## A2-C5
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38946.5893 | 1 | 0 | 38946.5893 | 1 | 0 |  | -71 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5914 | 1 | 0 | 38946.5914 | 1 | 0 |  | 113.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5936 | 1 | 0 | 38946.5936 | 1 | 0 |  | 298.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5957 | 1 | 0 | 38946.5957 | 1 | 0 |  | 483 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5978 | 1 | 0 | 38946.5978 | 1 | 0 |  | 668 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6 | 1 | 0 | 38946.6 | 1 | 0 |  | 852.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6021 | 1 | 0 | 38946.6021 | 1 | 0 |  | 1037.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6042 | 1 | 0 | 38946.6043 | 1 | 0 |  | 1222.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6064 | 683 | 231 | 38946.6064 | 908 | 370 |  | 1407 | 1515 | 41.6972 | 14.1026 | 55.4335 | 22.5885 | 0.41697 | 0.14103 | 0.55433 | 0.22589 | 0.27595 | 0.32845 | 389.5736 | 271.9986 | 379.5245
38946.6085 | 1529 | 145 | 38946.6085 | 1277 | 91 |  | 1592 | 1700 | 93.3455 | 8.8523 | 77.9609 | 5.5556 | 0.93346 | 0.088523 | 0.77961 | 0.055556 | 0.84493 | 0.72405 | 48.2252 | 83.8282 | 138.0684
38946.6107 | 1222 | 13 | 38946.6107 | 1266 | 7 |  | 1776.5 | 1884.5 | 74.6032 | 0.79365 | 77.2894 | 0.42735 | 0.74603 | 0.0079365 | 0.77289 | 0.0042735 | 0.7381 | 0.76862 | 74.8869 | 67.7804 | 2728.5009
38946.6128 | 1199 | 53 | 38946.6128 | 943 | 80 |  | 1961.5 | 2069.5 | 73.199 | 3.2357 | 57.5702 | 4.884 | 0.73199 | 0.032357 | 0.5757 | 0.04884 | 0.69963 | 0.52686 | 82.2468 | 152.7976 | 981.931
38946.6149 | 360 | 5 | 38946.615 | 449 | 6 |  | 2146 | 2254 | 21.978 | 0.30525 | 27.4115 | 0.3663 | 0.21978 | 0.0030525 | 0.27411 | 0.003663 | 0.21673 | 0.27045 | 495.6619 | 376.6545 | 27625.8631
38946.6171 | 166 | 11 | 38946.6171 | 257 | 14 |  | 2331 | 2439 | 10.1343 | 0.67155 | 15.6899 | 0.8547 | 0.10134 | 0.0067155 | 0.1569 | 0.008547 | 0.094628 | 0.14835 | 1267.8688 | 767.2808 | 15570.8297

## A2-B4
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38946.5892 | 1 | 0 | 38946.5893 | 1 | 0 |  | -74 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5914 | 1 | 0 | 38946.5914 | 1 | 0 |  | 111 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5935 | 1 | 0 | 38946.5935 | 1 | 0 |  | 295.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5957 | 1 | 0 | 38946.5957 | 1 | 0 |  | 480.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5978 | 1 | 0 | 38946.5978 | 1 | 0 |  | 665 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5999 | 1 | 0 | 38946.6 | 1 | 0 |  | 850 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6021 | 1 | 0 | 38946.6021 | 1 | 0 |  | 1034.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6042 | 1 | 0 | 38946.6042 | 1 | 0 |  | 1219.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6064 | 497 | 36 | 38946.6064 | 556 | 88 |  | 1404.5 | 1512.5 | 30.3419 | 2.1978 | 33.9438 | 5.3724 | 0.30342 | 0.021978 | 0.33944 | 0.053724 | 0.28144 | 0.28571 | 358.5205 | 351.1114 | 3416.0264
38946.6085 | 1488 | 71 | 38946.6085 | 1509 | 78 |  | 1589 | 1697 | 90.8425 | 4.3346 | 92.1245 | 4.7619 | 0.90842 | 0.043346 | 0.92125 | 0.047619 | 0.86508 | 0.87363 | 49.3158 | 47.4547 | 251.1236
38946.6106 | 1400 | 98 | 38946.6106 | 1112 | 87 |  | 1774 | 1882 | 85.4701 | 5.9829 | 67.8877 | 5.3114 | 0.8547 | 0.059829 | 0.67888 | 0.053114 | 0.79487 | 0.62576 | 58.6278 | 114.1927 | 334.5775
38946.6128 | 1110 | 9 | 38946.6128 | 978 | 9 |  | 1958.5 | 2066.5 | 67.7656 | 0.54945 | 59.707 | 0.54945 | 0.67766 | 0.0054945 | 0.59707 | 0.0054945 | 0.67216 | 0.59158 | 91.7345 | 118.3312 | 5985.9914
38946.6149 | 329 | 1 | 38946.6149 | 390 | 32 |  | 2143.5 | 2251.5 | 20.0855 | 0.06105 | 23.8095 | 1.9536 | 0.20085 | 0.0006105 | 0.2381 | 0.019536 | 0.20024 | 0.21856 | 544.2476 | 489.3271 | 148046.8133
38946.617 | 129 | 0 | 38946.6171 | 125 | 0 |  | 2328 | 2436 | 7.8755 | 0 | 7.6313 | 0 | 0.078755 | 0 | 0.076313 | 0 | 0.078755 | 0.076313 | 1538 | 1590.416 | 1537.9212

## A2-B3
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38946.5892 | 1 | 0 | 38946.5892 | 1 | 0 |  | -76.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5913 | 1 | 0 | 38946.5914 | 1 | 0 |  | 108 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5935 | 1 | 0 | 38946.5935 | 1 | 0 |  | 293 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5956 | 1 | 0 | 38946.5956 | 1 | 0 |  | 477.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5978 | 1 | 0 | 38946.5978 | 1 | 0 |  | 662.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5999 | 1 | 0 | 38946.5999 | 1 | 0 |  | 847 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.602 | 1 | 0 | 38946.6021 | 1 | 0 |  | 1032 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6042 | 1 | 0 | 38946.6042 | 1 | 0 |  | 1216.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6063 | 497 | 18 | 38946.6063 | 303 | 73 |  | 1401.5 | 1509.5 | 30.3419 | 1.0989 | 18.4982 | 4.4567 | 0.30342 | 0.010989 | 0.18498 | 0.044567 | 0.29243 | 0.14042 | 338.8401 | 868.2987 | 7961.0345
38946.6085 | 1323 | 72 | 38946.6085 | 1036 | 64 |  | 1586.5 | 1694.5 | 80.7692 | 4.3956 | 63.2479 | 3.9072 | 0.80769 | 0.043956 | 0.63248 | 0.039072 | 0.76374 | 0.59341 | 66.2502 | 123.0322 | 550.1173
38946.6106 | 1185 | 95 | 38946.6106 | 1029 | 93 |  | 1771 | 1879 | 72.3443 | 5.7998 | 62.8205 | 5.6777 | 0.72344 | 0.057998 | 0.62821 | 0.056777 | 0.66545 | 0.57143 | 91.2595 | 129.964 | 495.5586
38946.6127 | 1198 | 15 | 38946.6127 | 1140 | 10 |  | 1955.5 | 2063.5 | 73.138 | 0.91575 | 69.5971 | 0.6105 | 0.73138 | 0.0091575 | 0.69597 | 0.006105 | 0.72222 | 0.68987 | 78.4902 | 87.0899 | 2793.0473
38946.6149 | 276 | 2 | 38946.6149 | 1042 | 1 |  | 2140.5 | 2248.5 | 16.8498 | 0.1221 | 63.6142 | 0.06105 | 0.1685 | 0.001221 | 0.63614 | 0.0006105 | 0.16728 | 0.63553 | 675.2351 | 102.8984 | 46530.8317
38946.617 | 140 | 1 |  | 1042 | 1 |  | 2325 | 2433 | 8.547 | 0.06105 | 63.6142 | 0.06105 | 0.08547 | 0.0006105 | 0.63614 | 0.0006105 | 0.08486 | 0.63553 | 1429.4336 | 102.8907 | 100005.8154

## A1-C6
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38946.589 | 1 | 0 | 38946.589 | 1 | 0 |  | -96.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5911 | 1 | 0 | 38946.5911 | 1 | 0 |  | 88.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5933 | 1 | 0 | 38946.5933 | 1 | 0 |  | 273 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5954 | 1 | 0 | 38946.5954 | 1 | 0 |  | 458 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5975 | 1 | 0 | 38946.5975 | 1 | 0 |  | 642.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5997 | 1 | 0 | 38946.5997 | 1 | 0 |  | 827.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6018 | 1 | 0 | 38946.6018 | 1 | 0 |  | 1012.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6039 | 1 | 0 | 38946.604 | 1 | 0 |  | 1197 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6061 | 63 | 6 | 38946.6061 | 275 | 25 |  | 1382 | 1490 | 3.8462 | 0.3663 | 16.7888 | 1.5263 | 0.038462 | 0.003663 | 0.16789 | 0.015263 | 0.034799 | 0.15263 | 3648.6222 | 737.2286 | 29997.9797
38946.6082 | 1150 | 81 | 38946.6082 | 1250 | 95 |  | 1566.5 | 1674.5 | 70.2076 | 4.9451 | 76.3126 | 5.7998 | 0.70208 | 0.049451 | 0.76313 | 0.057998 | 0.65263 | 0.70513 | 99.3242 | 81.4667 | 488.851
38946.6104 | 1504 | 31 | 38946.6104 | 1388 | 29 |  | 1751.5 | 1859.5 | 91.8193 | 1.8926 | 84.7375 | 1.7705 | 0.91819 | 0.018926 | 0.84737 | 0.017705 | 0.89927 | 0.82967 | 42.9559 | 56.1383 | 670.3954
38946.6125 | 1186 | 3 | 38946.6125 | 794 | 38 |  | 1936 | 2044 | 72.4054 | 0.18315 | 48.4737 | 2.3199 | 0.72405 | 0.0018315 | 0.48474 | 0.023199 | 0.72222 | 0.46154 | 78.4685 | 186.4147 | 20046.796
38946.6146 | 441 | 8 | 38946.6147 | 465 | 10 |  | 2121 | 2229 | 26.9231 | 0.4884 | 28.3883 | 0.6105 | 0.26923 | 0.004884 | 0.28388 | 0.006105 | 0.26435 | 0.27778 | 388.1164 | 364.2649 | 16319.9956
38946.6168 | 244 | 40 | 38946.6168 | 294 | 39 |  | 2305.5 | 2413.5 | 14.8962 | 2.442 | 17.9487 | 2.381 | 0.14896 | 0.02442 | 0.17949 | 0.02381 | 0.12454 | 0.15568 | 941.6493 | 725.1184 | 4018.3811

## A1-C5
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38946.5889 | 1 | 0 | 38946.589 | 1 | 0 |  | -99 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5911 | 1 | 0 | 38946.5911 | 1 | 0 |  | 85.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5932 | 1 | 0 | 38946.5932 | 1 | 0 |  | 270.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5954 | 1 | 0 | 38946.5954 | 1 | 0 |  | 455.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5975 | 1 | 0 | 38946.5975 | 1 | 0 |  | 640 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5996 | 1 | 0 | 38946.5997 | 1 | 0 |  | 824.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6018 | 1 | 0 | 38946.6018 | 1 | 0 |  | 1009.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6039 | 1 | 0 | 38946.6039 | 1 | 0 |  | 1194.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6061 | 24 | 2 | 38946.6061 | 107 | 2 |  | 1379 | 1487 | 1.4652 | 0.1221 | 6.5324 | 0.1221 | 0.014652 | 0.001221 | 0.065324 | 0.001221 | 0.013431 | 0.064103 | 9540.936 | 1910.8767 | 99161.6715
38946.6082 | 1253 | 157 | 38946.6082 | 1256 | 79 |  | 1563.5 | 1671.5 | 76.4957 | 9.5849 | 76.6789 | 4.823 | 0.76496 | 0.095849 | 0.76679 | 0.04823 | 0.66911 | 0.71856 | 96.0433 | 78.2849 | 196.6217
38946.6103 | 1536 | 74 | 38946.6103 | 1164 | 19 |  | 1748.5 | 1856.5 | 93.7729 | 4.5177 | 71.0623 | 1.16 | 0.93773 | 0.045177 | 0.71062 | 0.0116 | 0.89255 | 0.69902 | 41.9269 | 86.2994 | 314.8835
38946.6125 | 1213 | 2 | 38946.6125 | 1086 | 1 |  | 1933.5 | 2041.5 | 74.0537 | 0.1221 | 66.3004 | 0.06105 | 0.74054 | 0.001221 | 0.663 | 0.0006105 | 0.73932 | 0.66239 | 74.4501 | 94.7735 | 21848.0748
38946.6146 | 482 | 5 | 38946.6146 | 528 | 5 |  | 2118 | 2226 | 29.4261 | 0.30525 | 32.2344 | 0.30525 | 0.29426 | 0.0030525 | 0.32234 | 0.0030525 | 0.29121 | 0.31929 | 343.1164 | 303.9099 | 24469
38946.6167 | 208 | 20 | 38946.6168 | 297 | 33 |  | 2303 | 2411 | 12.6984 | 1.221 | 18.1319 | 2.0147 | 0.12698 | 0.01221 | 0.18132 | 0.020147 | 0.11477 | 0.16117 | 1029.0293 | 696.3451 | 8241.5554

## A1-B4
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38946.5889 | 1 | 0 | 38946.5889 | 1 | 0 |  | -102 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5911 | 1 | 0 | 38946.5911 | 1 | 0 |  | 83 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5932 | 1 | 0 | 38946.5932 | 1 | 0 |  | 267.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5953 | 1 | 0 | 38946.5953 | 1 | 0 |  | 452.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5975 | 1 | 0 | 38946.5975 | 1 | 0 |  | 637 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5996 | 1 | 0 | 38946.5996 | 1 | 0 |  | 822 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6017 | 1 | 0 | 38946.6018 | 1 | 0 |  | 1006.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6039 | 1 | 0 | 38946.6039 | 1 | 0 |  | 1191.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.606 | 137 | 77 | 38946.606 | 173 | 121 |  | 1376.5 | 1484.5 | 8.3639 | 4.7009 | 10.5617 | 7.3871 | 0.083639 | 0.047009 | 0.10562 | 0.073871 | 0.03663 | 0.031746 | 3402.3991 | 4004.6911 | 2406.1758
38946.6082 | 1238 | 68 | 38946.6082 | 1030 | 86 |  | 1561 | 1669 | 75.58 | 4.1514 | 62.8816 | 5.2503 | 0.7558 | 0.041514 | 0.62882 | 0.052503 | 0.71429 | 0.57631 | 78.2928 | 129.8342 | 670.4245
38946.6103 | 1336 | 51 | 38946.6103 | 1101 | 53 |  | 1746 | 1854 | 81.5629 | 3.1136 | 67.2161 | 3.2357 | 0.81563 | 0.031136 | 0.67216 | 0.032357 | 0.78449 | 0.6398 | 62.8435 | 105.018 | 729.2058
38946.6124 | 1041 | 13 | 38946.6125 | 1328 | 22 |  | 1930.5 | 2038.5 | 63.5531 | 0.79365 | 81.0745 | 1.3431 | 0.63553 | 0.0079365 | 0.81074 | 0.013431 | 0.62759 | 0.79731 | 106.487 | 61.0749 | 3088.8415
38946.6146 | 527 | 26 | 38946.6146 | 990 | 6 |  | 2115.5 | 2223.5 | 32.1734 | 1.5873 | 60.4396 | 0.3663 | 0.32173 | 0.015873 | 0.6044 | 0.003663 | 0.30586 | 0.60073 | 331.6226 | 114.3383 | 3200.7278
38946.6167 | 149 | 2 | 38946.6167 | 681 | 1 |  | 2300 | 2408 | 9.0965 | 0.1221 | 41.5751 | 0.06105 | 0.090965 | 0.001221 | 0.41575 | 0.0006105 | 0.089744 | 0.41514 | 1344.755 | 210.6142 | 66518.0919

## A1-B3
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38946.5889 | 1 | 0 | 38946.5889 | 1 | 0 |  | -104.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.591 | 1 | 0 | 38946.591 | 1 | 0 |  | 80 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5932 | 1 | 0 | 38946.5932 | 1 | 0 |  | 265 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5953 | 1 | 0 | 38946.5953 | 1 | 0 |  | 449.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5974 | 1 | 0 | 38946.5975 | 1 | 0 |  | 634.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5996 | 1 | 0 | 38946.5996 | 1 | 0 |  | 819.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6017 | 1 | 0 | 38946.6017 | 1 | 0 |  | 1004 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6039 | 1 | 0 | 38946.6039 | 1 | 0 |  | 1188.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.606 | 63 | 12 | 38946.606 | 63 | 25 |  | 1373.5 | 1481.5 | 3.8462 | 0.7326 | 3.8462 | 1.5263 | 0.038462 | 0.007326 | 0.038462 | 0.015263 | 0.031136 | 0.023199 | 4036.9674 | 5484.1636 | 16679.3631
38946.6081 | 1317 | 46 | 38946.6081 | 929 | 82 |  | 1558.5 | 1666.5 | 80.4029 | 2.8083 | 56.7155 | 5.0061 | 0.80403 | 0.028083 | 0.56716 | 0.050061 | 0.77595 | 0.51709 | 64.0367 | 164.6877 | 1014.4776
38946.6103 | 1523 | 59 | 38946.6103 | 978 | 53 |  | 1743 | 1851 | 92.9792 | 3.602 | 59.707 | 3.2357 | 0.92979 | 0.03602 | 0.59707 | 0.032357 | 0.89377 | 0.56471 | 41.4759 | 142.3731 | 528.6916
38946.6124 | 1097 | 27 | 38946.6124 | 1345 | 19 |  | 1927.5 | 2035.5 | 66.9719 | 1.6484 | 82.1123 | 1.16 | 0.66972 | 0.016484 | 0.82112 | 0.0116 | 0.65324 | 0.80952 | 99.2152 | 58.7688 | 1355.8855
38946.6145 | 658 | 28 | 38946.6146 | 1305 | 9 |  | 2112.5 | 2220.5 | 40.1709 | 1.7094 | 79.6703 | 0.54945 | 0.40171 | 0.017094 | 0.7967 | 0.0054945 | 0.38462 | 0.79121 | 248.6297 | 62.5219 | 1960.614
38946.6167 | 228 | 10 | 38946.6167 | 699 | 4 |  | 2297.5 | 2405.5 | 13.9194 | 0.6105 | 42.674 | 0.2442 | 0.13919 | 0.006105 | 0.42674 | 0.002442 | 0.13309 | 0.4243 | 884.6199 | 203.5886 | 12574.0123

## A1-A2
Penlight Test 42 |  |  | 2006-08-17 | 14:09 |  |  | Vs = |  | 129 |  | R = | 100
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38946.5889 | 1 | 0 | 38946.5889 | 1 | 0 |  | -107.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.591 | 1 | 0 | 38946.591 | 1 | 0 |  | 77.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5931 | 1 | 0 | 38946.5931 | 1 | 0 |  | 262 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5953 | 1 | 0 | 38946.5953 | 1 | 0 |  | 446.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5974 | 1 | 0 | 38946.5974 | 1 | 0 |  | 631.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.5995 | 1 | 0 | 38946.5996 | 1 | 0 |  | 816.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6017 | 1 | 0 | 38946.6017 | 1 | 0 |  | 1001 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38946.6038 | 225 | 199 | 38946.6038 | 199 | 203 |  | 1186 | 1294 | 13.7363 | 12.149 | 12.149 | 12.3932 | 0.13736 | 0.12149 | 0.12149 | 0.12393 | 0.015873 | 0.002442 | 7297.1596 | 157132.1607 | 848.214
38946.606 | 1042 | 1102 | 38946.606 | 1220 | 1098 |  | 1370.5 | 1478.5 | 63.6142 | 67.2772 | 74.4811 | 67.033 | 0.63614 | 0.67277 | 0.74481 | 0.67033 | 0.03663 | 0.074481 | 313.5604 | 391.3806 | 2.2391
38946.6081 | 1612 | 521 | 38946.6081 | 1665 | 515 |  | 1555.5 | 1663.5 | 98.4127 | 31.8071 | 101.6484 | 31.4408 | 0.98413 | 0.31807 | 1.0165 | 0.31441 | 0.66606 | 0.70208 | 39.7317 | 306.4581 | 2.8914
38946.6102 | 1590 | 537 | 38946.6103 | 1380 | 492 |  | 1740.5 | 1848.5 | 97.0696 | 32.7839 | 84.2491 | 30.0366 | 0.9707 | 0.32784 | 0.84249 | 0.30037 | 0.64286 | 0.54212 | 40.3981 | 222.209 | 1.7954
38946.6124 | 1626 | 661 | 38946.6124 | 1730 | 661 |  | 1925 | 2033 | 99.2674 | 40.3541 | 105.6166 | 40.3541 | 0.99267 | 0.40354 | 1.0562 | 0.40354 | 0.58913 | 0.65263 | 74.2987 | 213.563 | 17.9266
38946.6145 | 1442 | 898 | 38946.6145 | 1280 | 795 |  | 2109.5 | 2217.5 | 88.0342 | 54.823 | 78.1441 | 48.5348 | 0.88034 | 0.54823 | 0.78144 | 0.48535 | 0.33211 | 0.29609 | 878.6819 | 192.0308 | 16.6209
38946.6167 | 1339 | 1061 | 38946.6167 | 1133 | 958 |  | 2294.5 | 2402.5 | 81.746 | 64.7741 | 69.1697 | 58.486 | 0.81746 | 0.64774 | 0.6917 | 0.58486 | 0.16972 | 0.10684 | 297.2009 | 6040.969 | 26.6076

## AvgC-C
Average Conductor to Conductor Resistances
Penlight Test 42 |  |  | 2006-08-17 | 14:09
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-C |  | Penlight Time | C2-C | Penlight Time | C3-C | Penlight Time | C4-C | Penlight Time | C5-C | Penlight Time | C6-C | Penlight Time | C7-C | Penlight Time | Minimums
-90.25 | 218541.3327 |  | -53.8333 | 219074.6661 | -59.8333 | 211201.9994 | -47.75 | 211201.9994 | -38.8333 | 214491.3327 | -34.25 | 211307.9994 | 2.5833 | 229809.3327 | -90.25 | 211201.9994
94.5833 | 218541.3327 |  | 130.9167 | 219074.6661 | 124.8333 | 211201.9994 | 137.0833 | 211201.9994 | 145.8333 | 214491.3327 | 150.5 | 211307.9994 | 187.4167 | 229809.3327 | 94.5833 | 211201.9994
279.25 | 218541.3327 |  | 315.75 | 219074.6661 | 309.75 | 211201.9994 | 321.75 | 211201.9994 | 330.5833 | 214491.3327 | 335.3333 | 211307.9994 | 372.0833 | 229809.3327 | 279.25 | 211201.9994
464.0833 | 218541.3327 |  | 500.3333 | 219074.6661 | 494.3333 | 211201.9994 | 506.5833 | 211201.9994 | 515.4167 | 214491.3327 | 520 | 211307.9994 | 556.9167 | 229809.3327 | 464.0833 | 211201.9994
648.75 | 218541.3327 |  | 685.1667 | 219074.6661 | 679.1667 | 211201.9994 | 691.25 | 211201.9994 | 700.1667 | 214491.3327 | 704.8333 | 211307.9994 | 741.6667 | 229809.3327 | 648.75 | 211201.9994
833.6667 | 218541.3327 |  | 870 | 219074.6661 | 864 | 211201.9994 | 876.0833 | 211201.9994 | 884.8333 | 214491.3327 | 889.5833 | 211307.9994 | 926.5 | 229809.3327 | 833.6667 | 211201.9994
1018.3333 | 218541.3327 |  | 1054.75 | 219074.6661 | 1048.75 | 211201.9994 | 1060.75 | 211201.9994 | 1069.6667 | 179259.0939 | 1074.4167 | 176109.101 | 1111.1667 | 229775.9923 | 1018.3333 | 176109.101
1203.25 | 183482.3685 |  | 1239.5833 | 140943.9754 | 1233.4167 | 126632.1792 | 1245.5833 | 158395.7438 | 1254.5833 | 110716.3429 | 1259.1667 | 140813.2684 | 1296.0833 | 149781.2616 | 1203.25 | 110716.3429
1388 | 24756.4423 |  | 1424.3333 | 1985.5895 | 1418.25 | 8628.3147 | 1430.5 | 14121.0918 | 1439.1667 | 27294.0405 | 1444 | 11885.8067 | 1480.9167 | 137.5091 | 1388 | 137.5091
1572.6667 | 409.8013 |  | 1609.1667 | 191.1149 | 1603.1667 | 1179.6855 | 1615.25 | 790.8334 | 1624.0833 | 568.0553 | 1628.75 | 1141.8633 | 1665.5833 | 94.5077 | 1572.6667 | 94.5077
1757.5 | 5648.9318 |  | 1793.9167 | 1262.9853 | 1787.8333 | 9309.2072 | 1799.9167 | 232.2566 | 1808.75 | 1878.6755 | 1813.5 | 8610.1148 | 1850.25 | 5352.6671 | 1757.5 | 232.2566
1942.1667 | 7974.7348 |  | 1978.6667 | 1930.7274 | 1972.4167 | 13012.6706 | 1984.5833 | 16542.6179 | 1993.5833 | 11790.6848 | 1998.25 | 23065.3555 | 2035 | 404.6725 | 1942.1667 | 404.6725
2127 | 21324.4836 |  | 2163.3333 | 38877.4172 | 2157.4167 | 16346.7755 | 2169.5 | 49213.0795 | 2178.25 | 38352.81 | 2183.0833 | 13925.7895 | 2219.9167 | 20739.418 | 2127 | 13925.7895
2311.75 | 15370.6966 |  | 2348.0833 | 20241.5987 | 2342.0833 | 34817.4152 | 2354.25 | 47892.6891 | 2363.1667 | 16582.1647 | 2367.75 | 42128.2948 | 2404.5833 | 1368.5887 | 2311.75 | 1368.5887
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 42 |  |  | 2006-08-17 | 14:09
XLPE&EPR | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | C8-G | Penlight Time | C9-G | Penlight Time | C10-G | Penlight Time | C11-G | Penlight Time | C12-G | Penlight Time | Minimums
-101.9 | 211202 |  | -79.5 | 211202 | -51.4444 | 220187.7778 | -35.9444 | 198565.1667 | -21.6111 | 224662.4444 | -12.9444 | 226751.3333 | 11.2 | 227456.4 | 16.9 | 200226.2 | 29.1111 | 240238 | 32.1111 | 256082.4444 | 49.8 | 253178 | 52 | 254678 | -9.3519 | 198565.1667
82.9 | 211202 |  | 105.3 | 211202 | 133.2778 | 220187.7778 | 148.8889 | 220010 | 163.0556 | 224662.4444 | 171.8333 | 226751.3333 | 196 | 227456.4 | 201.6 | 221356.4 | 213.8889 | 227402.5556 | 216.9444 | 256082.4444 | 234.5 | 253178 | 236.9 | 254678 | 175.4241 | 211202
267.6 | 211202 |  | 290.1 | 211202 | 318.1111 | 220187.7778 | 333.6111 | 220010 | 347.8333 | 224662.4444 | 356.6667 | 215012.3333 | 380.7 | 227456.4 | 386.3 | 221356.4 | 398.6111 | 240238 | 401.7222 | 256082.4444 | 419.5 | 253178 | 421.6 | 254678 | 360.1963 | 211202
452.4 | 211202 |  | 474.7 | 211202 | 502.7222 | 220187.7778 | 518.3333 | 220010 | 532.6667 | 212923.4444 | 541.2778 | 226751.3333 | 565.5 | 201442.6 | 571 | 221356.4 | 583.3889 | 226697 | 586.4444 | 256082.4444 | 604 | 253178 | 606.3 | 254678 | 544.8944 | 201442.6
637.1 | 211202 |  | 659.5 | 211202 | 687.5556 | 220187.7778 | 703.0556 | 220010 | 717.4444 | 210882.5556 | 726.1111 | 226751.3333 | 750.2 | 227456.4 | 756 | 221356.4 | 768.1667 | 240238 | 771.2778 | 256082.4444 | 788.9 | 253178 | 791 | 254678 | 729.6926 | 210882.5556
822 | 211202 |  | 844.3 | 211202 | 872.3889 | 220187.7778 | 887.8889 | 220010 | 902.1111 | 224662.4444 | 910.8889 | 226751.3333 | 935 | 227456.4 | 940.6 | 221356.4 | 952.8889 | 240238 | 956 | 256082.4444 | 973.6 | 253178 | 976 | 254678 | 914.4722 | 211202
1006.7 | 211202 |  | 1029.1 | 211202 | 1057.1111 | 220187.7778 | 1072.6111 | 220010 | 1086.9444 | 68477270.8223 | 1095.7222 | 203308.2153 | 1119.8 | 227456.4 | 1125.4 | 221356.4 | 1137.6667 | 59447084.8786 | 1140.7222 | 256082.4444 | 1158.5 | 253178 | 1160.7 | 254678 | 1099.2481 | 203308.2153
1191.5 | 170421.0319 |  | 1213.9 | 200388.0321 | 1241.8889 | 93254033.1174 | 1257.4444 | 185341.4478 | 1271.8333 | 121219.7654 | 1280.5 | 135635.9702 | 1304.6 | 89215071.4192 | 1310.2 | 99346.7431 | 1322.3889 | 59324639.7166 | 1325.7222 | 56958.913 | 1343.3 | 8.4131 | 1345.5 | 33.3418 | 1284.0648 | 8.4131
1376.3 | 4188.497 |  | 1398.7 | 381.0023 | 1426.6667 | 929.0348 | 1442.2778 | 634.148 | 1456.5 | 295.468 | 1465.2778 | 181.3798 | 1489.5 | 1289.7441 | 1494.9 | 1130.8275 | 1507.2778 | 19.9181 | 1510.3333 | 12.3435 | 1528 | 15.3055 | 1530.2 | 8.455 | 1468.8278 | 8.455
1561 | 75.4857 |  | 1583.5 | 103.3465 | 1611.5556 | 92.8878 | 1627.0556 | 101.2311 | 1641.3333 | 78.0574 | 1650.0556 | 103.1774 | 1674.1 | 1160.9187 | 1679.8 | 155.2557 | 1692 | 18.5751 | 1695.1111 | 7.823 | 1712.8 | 16.3086 | 1715 | 12.6873 | 1653.6093 | 7.823
1745.9 | 45.9201 |  | 1768.3 | 100.0025 | 1796.2222 | 99.7645 | 1811.7222 | 116.9318 | 1826 | 79.6103 | 1834.7778 | 83.8022 | 1858.9 | 415.5241 | 1864.5 | 405.7069 | 1876.7778 | 18.9893 | 1879.7222 | 27.6755 | 1897.5 | 5.1779 | 1899.7 | 13.6773 | 1838.3352 | 5.1779
1930.5 | 86.5839 |  | 1953 | 115.3549 | 1980.8333 | 80.474 | 1996.4444 | 103.4035 | 2010.8333 | 247.2375 | 2019.5556 | 302.3649 | 2043.6 | 297.6066 | 2049.3 | 302.93 | 2061.4444 | 35.7685 | 2064.6667 | 63.1288 | 2082.3 | 6.8661 | 2084.5 | 2.712 | 2023.0815 | 2.712
2115.3 | 438.0334 |  | 2137.7 | 489.285 | 2165.7778 | 128.1026 | 2181.2778 | 332.8405 | 2195.5556 | 458.5706 | 2204.3889 | 450.6048 | 2228.5 | 706.8998 | 2234 | 1482.1323 | 2246.3333 | 28.0198 | 2249.4444 | 40.9035 | 2267 | 17.7791 | 2269.3 | 17.4463 | 2207.8815 | 17.4463
2300.1 | 899.4509 |  | 2322.4 | 2287.4284 | 2350.5 | 380.7548 | 2366.0556 | 653.1625 | 2380.3889 | 2341.4976 | 2389.1111 | 2075.4163 | 2413.2 | 83787.9999 | 2418.9 | 19623.4772 | 2431.1111 | 1508.3967 | 2434.1667 | 15.3751 | 2452 | 112.4267 | 2454 | 170.2318 | 2392.6611 | 15.3751
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -108 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
1 | -107 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
2 | -106 | 18.9 | 27.2 | 20.2 | 26.8 | 30.2 | 23.9 | 23.8 | 28.4
3 | -105 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.4
4 | -104 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
5 | -103 | 19 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
6 | -102 | 18.9 | 27.2 | 20.2 | 26.8 | 30.2 | 23.9 | 23.8 | 28.4
7 | -101 | 18.9 | 27.2 | 20.3 | 26.7 | 30.2 | 23.9 | 23.8 | 28.4
8 | -100 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
9 | -99 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.4
10 | -98 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.4
11 | -97 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
12 | -96 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
13 | -95 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
14 | -94 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
15 | -93 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
16 | -92 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
17 | -91 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
18 | -90 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.2
19 | -89 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
20 | -88 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.2
21 | -87 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
22 | -86 | 18.9 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
23 | -85 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
24 | -84 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
25 | -83 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
26 | -82 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
27 | -81 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
28 | -80 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
29 | -79 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
30 | -78 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
31 | -77 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
32 | -76 | 18.9 | 27.2 | 20.2 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
33 | -75 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
34 | -74 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
35 | -73 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
36 | -72 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
37 | -71 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
38 | -70 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
39 | -69 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
40 | -68 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
41 | -67 | 18.9 | 27.2 | 20.2 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
42 | -66 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
43 | -65 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
44 | -64 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
45 | -63 | 18.9 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
46 | -62 | 19 | 27.1 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
47 | -61 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
48 | -60 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
49 | -59 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
50 | -58 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
51 | -57 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
52 | -56 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
53 | -55 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
54 | -54 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
55 | -53 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
56 | -52 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
57 | -51 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
58 | -50 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
59 | -49 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
60 | -48 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.1
61 | -47 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
62 | -46 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
63 | -45 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
64 | -44 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
65 | -43 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
66 | -42 | 19 | 27.2 | 20.3 | 26.7 | 30.2 | 23.9 | 23.8 | 28.2
67 | -41 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
68 | -40 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
69 | -39 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
70 | -38 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
71 | -37 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
72 | -36 | 19 | 27.2 | 20.3 | 26.7 | 30.2 | 23.9 | 23.8 | 28.2
73 | -35 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
74 | -34 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
75 | -33 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.2
76 | -32 | 19 | 27.1 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
77 | -31 | 19 | 27.2 | 20.2 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
78 | -30 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
79 | -29 | 19 | 27.2 | 20.2 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
80 | -28 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
81 | -27 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
82 | -26 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.5
83 | -25 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.5
84 | -24 | 19 | 27.2 | 20.2 | 26.7 | 30.1 | 23.9 | 23.8 | 28.5
85 | -23 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
86 | -22 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
87 | -21 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
88 | -20 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
89 | -19 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
90 | -18 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
91 | -17 | 19 | 27.1 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
92 | -16 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
93 | -15 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
94 | -14 | 19 | 27.1 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
95 | -13 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
96 | -12 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
97 | -11 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.4
98 | -10 | 19 | 27.1 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
99 | -9 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
100 | -8 | 19 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
101 | -7 | 19 | 27.2 | 20.2 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
102 | -6 | 19 | 27.2 | 20.3 | 26.7 | 30.1 | 23.9 | 23.8 | 28.3
103 | -5 | 19 | 27.2 | 20.3 | 26.7 | 30.2 | 23.9 | 23.8 | 28.3
104 | -4 | 19 | 27.2 | 20.1 | 26.8 | 30.2 | 24 | 23.8 | 28.3
105 | -3 | 18.9 | 28.3 | 17.9 | 27.5 | 31.7 | 24.2 | 23.7 | 28.2
106 | -2 | 18.9 | 28.8 | 16.8 | 27.9 | 32.5 | 24.2 | 23.7 | 28.1
107 | -1 | 19.1 | 28.9 | 16.6 | 28 | 32.6 | 24.3 | 23.7 | 28.1
108 | 0 | 19.8 | 28.9 | 16.7 | 27.9 | 32.6 | 24.3 | 23.7 | 28.1
109 | 1 | 21.1 | 28.9 | 16.7 | 27.9 | 32.6 | 24.3 | 23.7 | 28.1
110 | 2 | 22.9 | 28.9 | 16.7 | 27.9 | 32.6 | 24.3 | 23.7 | 28.1
111 | 3 | 25.2 | 28.9 | 16.7 | 27.9 | 32.6 | 24.3 | 23.8 | 28.1
112 | 4 | 27.8 | 28.9 | 16.7 | 27.9 | 32.5 | 24.3 | 23.8 | 28.1
113 | 5 | 30.8 | 28.9 | 16.7 | 27.9 | 32.6 | 24.3 | 23.8 | 28.2
114 | 6 | 34 | 28.9 | 16.7 | 27.9 | 32.6 | 24.4 | 23.9 | 28.2
115 | 7 | 37.5 | 28.9 | 16.7 | 27.9 | 32.6 | 24.4 | 24 | 28.2
116 | 8 | 41.3 | 28.9 | 16.7 | 27.9 | 32.6 | 24.5 | 24 | 28.3
117 | 9 | 45.3 | 28.9 | 16.7 | 27.9 | 32.6 | 24.6 | 24.1 | 28.3
118 | 10 | 49.4 | 28.9 | 16.7 | 27.9 | 32.7 | 24.6 | 24.2 | 28.4
119 | 11 | 53.6 | 29 | 16.7 | 27.9 | 32.7 | 24.7 | 24.3 | 28.4
120 | 12 | 58.1 | 29 | 16.7 | 27.9 | 32.7 | 24.8 | 24.4 | 28.4
121 | 13 | 62.6 | 29 | 16.7 | 27.9 | 32.8 | 24.9 | 24.5 | 28.5
122 | 14 | 67.3 | 29.1 | 16.7 | 27.9 | 32.8 | 25 | 24.6 | 28.6
123 | 15 | 72.1 | 29.1 | 16.7 | 27.9 | 32.8 | 25.1 | 24.8 | 28.7
124 | 16 | 77.1 | 29.1 | 16.7 | 27.9 | 32.9 | 25.2 | 24.9 | 28.8
125 | 17 | 82.1 | 29.2 | 16.8 | 27.9 | 32.9 | 25.3 | 25 | 29
126 | 18 | 87.2 | 29.2 | 16.8 | 27.9 | 32.9 | 25.4 | 25.2 | 29
127 | 19 | 92.5 | 29.2 | 16.8 | 27.9 | 33 | 25.6 | 25.4 | 29.2
128 | 20 | 97.8 | 29.3 | 16.9 | 27.9 | 33.1 | 25.7 | 25.6 | 29.3
129 | 21 | 103.1 | 29.4 | 16.8 | 28 | 33.2 | 25.9 | 25.8 | 29.5
130 | 22 | 108.5 | 29.5 | 16.8 | 28 | 33.3 | 26.2 | 26 | 29.6
131 | 23 | 113.8 | 29.4 | 17.2 | 27.9 | 33.2 | 26.3 | 26.3 | 29.8
132 | 24 | 119.3 | 29.1 | 18 | 27.6 | 32.8 | 26.4 | 26.5 | 30
133 | 25 | 124.9 | 29 | 18.4 | 27.5 | 32.6 | 26.6 | 26.8 | 30.3
134 | 26 | 130.5 | 29.1 | 18.5 | 27.5 | 32.7 | 26.8 | 27 | 30.5
135 | 27 | 136.1 | 29.2 | 18.5 | 27.5 | 32.8 | 27.1 | 27.3 | 30.7
136 | 28 | 141.8 | 29.3 | 18.6 | 27.5 | 32.9 | 27.3 | 27.6 | 31
137 | 29 | 147.5 | 29.3 | 18.7 | 27.5 | 33 | 27.6 | 28 | 31.2
138 | 30 | 153.2 | 29.4 | 18.7 | 27.6 | 33.2 | 27.9 | 28.3 | 31.4
139 | 31 | 158.8 | 29.6 | 18.7 | 27.6 | 33.4 | 28.2 | 28.7 | 31.6
140 | 32 | 164.4 | 29.7 | 18.9 | 27.6 | 33.5 | 28.5 | 29 | 31.9
141 | 33 | 170.1 | 29.8 | 18.9 | 27.7 | 33.6 | 28.9 | 29.4 | 32.2
142 | 34 | 175.8 | 30 | 19 | 27.7 | 33.8 | 29.2 | 29.8 | 32.5
143 | 35 | 181.3 | 30.1 | 19 | 27.8 | 34 | 29.5 | 30.2 | 32.8
144 | 36 | 187 | 30.3 | 19.1 | 27.8 | 34.2 | 29.8 | 30.6 | 33.1
145 | 37 | 192.7 | 30.5 | 19.2 | 27.9 | 34.4 | 30.1 | 31.1 | 33.5
146 | 38 | 198.3 | 30.7 | 19.2 | 28 | 34.6 | 30.5 | 31.6 | 33.8
147 | 39 | 204 | 30.8 | 19.3 | 28 | 34.9 | 30.9 | 32.1 | 34.2
148 | 40 | 209.6 | 31.1 | 19.4 | 28.1 | 35.1 | 31.3 | 32.6 | 34.6
149 | 41 | 215.2 | 31.3 | 19.5 | 28.2 | 35.4 | 31.7 | 33.1 | 35
150 | 42 | 220.9 | 31.5 | 19.6 | 28.3 | 35.6 | 32.2 | 33.7 | 35.5
151 | 43 | 226.5 | 31.7 | 19.7 | 28.3 | 35.9 | 32.7 | 34.3 | 36
152 | 44 | 232.1 | 31.9 | 19.8 | 28.4 | 36.1 | 33.2 | 34.8 | 36.5
153 | 45 | 237.7 | 32.2 | 19.9 | 28.5 | 36.4 | 33.7 | 35.5 | 37
154 | 46 | 243.1 | 32.4 | 20.1 | 28.6 | 36.7 | 34.3 | 36.1 | 37.5
155 | 47 | 248.6 | 32.7 | 20.2 | 28.7 | 37.1 | 34.7 | 36.7 | 38.1
156 | 48 | 254 | 32.9 | 20.4 | 28.8 | 37.4 | 35.2 | 37.4 | 38.6
157 | 49 | 259.5 | 33.2 | 20.5 | 28.9 | 37.7 | 35.8 | 38.1 | 39.2
158 | 50 | 265 | 33.5 | 20.7 | 29.1 | 38.1 | 36.4 | 38.8 | 39.8
159 | 51 | 270.5 | 33.8 | 20.9 | 29.2 | 38.4 | 36.9 | 39.6 | 40.5
160 | 52 | 275.8 | 34.2 | 21 | 29.3 | 38.8 | 37.6 | 40.3 | 41.2
161 | 53 | 281.2 | 34.5 | 21.2 | 29.5 | 39.2 | 38.2 | 41.1 | 41.9
162 | 54 | 286.4 | 34.9 | 21.4 | 29.6 | 39.6 | 38.9 | 41.9 | 42.6
163 | 55 | 291.7 | 35.2 | 21.6 | 29.8 | 40 | 39.6 | 42.8 | 43.3
164 | 56 | 297 | 35.6 | 21.8 | 29.9 | 40.5 | 40.3 | 43.6 | 44
165 | 57 | 302.3 | 35.9 | 22 | 30.1 | 40.9 | 41 | 44.5 | 44.7
166 | 58 | 307.5 | 36.3 | 22.3 | 30.3 | 41.3 | 41.7 | 45.4 | 45.5
167 | 59 | 312.7 | 36.7 | 22.6 | 30.5 | 41.8 | 42.5 | 46.3 | 46.3
168 | 60 | 317.9 | 37.1 | 22.8 | 30.7 | 42.3 | 43.3 | 47.2 | 47.2
169 | 61 | 323.1 | 37.5 | 23 | 30.9 | 42.8 | 44.1 | 48.2 | 48.1
170 | 62 | 328.2 | 37.9 | 23.3 | 31.1 | 43.3 | 44.8 | 49.1 | 49
171 | 63 | 333.2 | 38.3 | 23.6 | 31.3 | 43.8 | 45.6 | 50.1 | 50
172 | 64 | 338.3 | 38.7 | 23.9 | 31.5 | 44.3 | 46.4 | 51.2 | 51
173 | 65 | 343.1 | 39.2 | 24.1 | 31.8 | 44.9 | 47.2 | 52.2 | 52
174 | 66 | 348 | 39.7 | 24.4 | 32 | 45.5 | 48.1 | 53.3 | 53
175 | 67 | 353.2 | 40.2 | 24.7 | 32.3 | 46.1 | 49.1 | 54.4 | 54
176 | 68 | 358.3 | 40.7 | 25 | 32.6 | 46.7 | 50 | 55.5 | 55.1
177 | 69 | 363.1 | 41.2 | 25.3 | 32.8 | 47.3 | 50.9 | 56.6 | 56.3
178 | 70 | 367.9 | 41.7 | 25.6 | 33.1 | 47.9 | 51.9 | 57.8 | 57.4
179 | 71 | 372.7 | 42.3 | 26.1 | 33.4 | 48.5 | 52.8 | 59 | 58.7
180 | 72 | 377.7 | 42.8 | 26.4 | 33.7 | 49.1 | 53.8 | 60.3 | 59.9
181 | 73 | 382.3 | 43.4 | 26.7 | 34 | 49.8 | 54.9 | 61.5 | 61.2
182 | 74 | 387.1 | 44 | 27.2 | 34.3 | 50.5 | 55.8 | 62.7 | 62.5
183 | 75 | 392 | 44.6 | 27.5 | 34.6 | 51.2 | 56.9 | 64 | 63.8
184 | 76 | 396.7 | 45.2 | 27.9 | 35 | 51.9 | 58 | 65.3 | 65.2
185 | 77 | 401.4 | 45.8 | 28.3 | 35.3 | 52.6 | 59 | 66.6 | 66.6
186 | 78 | 405.8 | 46.5 | 28.6 | 35.7 | 53.4 | 60.1 | 67.9 | 67.9
187 | 79 | 410.1 | 47.2 | 29.1 | 36 | 54.2 | 61.1 | 69.3 | 69.4
188 | 80 | 414.5 | 47.9 | 29.5 | 36.4 | 55 | 62.1 | 70.6 | 70.8
189 | 81 | 418.8 | 48.5 | 29.9 | 36.8 | 55.8 | 63.2 | 72 | 72.3
190 | 82 | 423.2 | 49.3 | 30.3 | 37.2 | 56.7 | 64.3 | 73.4 | 73.9
191 | 83 | 427.5 | 50 | 30.8 | 37.6 | 57.5 | 65.4 | 74.9 | 75.4
192 | 84 | 431.7 | 50.7 | 31.3 | 38 | 58.4 | 66.6 | 76.3 | 77
193 | 85 | 435.8 | 51.5 | 31.9 | 38.4 | 59.2 | 67.8 | 77.8 | 78.7
194 | 86 | 439.6 | 52.3 | 32.4 | 38.8 | 60.2 | 69 | 79.3 | 80.4
195 | 87 | 443.7 | 53.1 | 32.9 | 39.3 | 61.1 | 70.1 | 80.8 | 82.1
196 | 88 | 447.9 | 54 | 33.5 | 39.7 | 62 | 71.4 | 82.3 | 83.9
197 | 89 | 452.2 | 54.9 | 34 | 40.1 | 63 | 72.7 | 83.9 | 85.7
198 | 90 | 456.3 | 55.8 | 34.5 | 40.6 | 64 | 74 | 85.4 | 87.5
199 | 91 | 460.5 | 56.7 | 35.1 | 41.1 | 64.9 | 75.3 | 87 | 89.4
200 | 92 | 464.6 | 57.6 | 35.6 | 41.6 | 65.9 | 76.5 | 88.6 | 91.2
201 | 93 | 468.5 | 58.6 | 36.2 | 42.1 | 67 | 77.8 | 90.1 | 93.1
202 | 94 | 472.4 | 59.6 | 36.8 | 42.6 | 68 | 79.1 | 91.7 | 95.1
203 | 95 | 476.4 | 60.3 | 37.9 | 43 | 68.6 | 80.3 | 93.3 | 97.1
204 | 96 | 480.5 | 61.4 | 38.4 | 43.6 | 69.9 | 81.6 | 95 | 99.1
205 | 97 | 484.2 | 62.5 | 38.9 | 44.1 | 71 | 83 | 96.7 | 101.1
206 | 98 | 487.5 | 63.5 | 39.6 | 44.7 | 72.1 | 84.4 | 98.2 | 103.2
207 | 99 | 490.5 | 64.6 | 40.3 | 45.2 | 73.2 | 85.7 | 99.8 | 105.3
208.1 | 100.1 | 493.3 | 65.7 | 40.9 | 45.8 | 74.3 | 87.1 | 101.4 | 107.3
209.1 | 101.1 | 495.9 | 66.8 | 41.6 | 46.4 | 75.4 | 88.4 | 103 | 109.4
210.1 | 102.1 | 498.5 | 67.8 | 42.3 | 47 | 76.5 | 89.7 | 104.6 | 111.6
211.1 | 103.1 | 500.8 | 69 | 43 | 47.6 | 77.6 | 91.1 | 106.2 | 113.7
212.1 | 104.1 | 503.2 | 70.1 | 43.7 | 48.2 | 78.7 | 92.4 | 107.8 | 115.8
213.1 | 105.1 | 505.4 | 71.2 | 44.3 | 48.8 | 79.9 | 93.5 | 109.3 | 117.9
214.1 | 106.1 | 507.6 | 72.4 | 44.9 | 49.5 | 81.1 | 94.8 | 110.9 | 120.1
215.1 | 107.1 | 509.4 | 73.6 | 45.7 | 50.1 | 82.2 | 96.3 | 112.4 | 122.3
216.1 | 108.1 | 511.2 | 74.6 | 46.5 | 50.7 | 83.2 | 97.7 | 113.9 | 124.5
217.1 | 109.1 | 513 | 75.8 | 47.3 | 51.3 | 84.4 | 99 | 115.5 | 126.7
218.1 | 110.1 | 514.8 | 76.9 | 48.1 | 52 | 85.5 | 100.4 | 117 | 128.9
219.1 | 111.1 | 516.1 | 78.1 | 48.8 | 52.6 | 86.6 | 101.6 | 118.4 | 131.1
220.1 | 112.1 | 517.1 | 79.3 | 49.6 | 53.3 | 87.8 | 102.8 | 119.7 | 133.3
221.1 | 113.1 | 517.8 | 80.5 | 50.4 | 53.9 | 88.9 | 104.1 | 120.9 | 135.5
222.1 | 114.1 | 518.5 | 81.6 | 51.1 | 54.6 | 90.1 | 105.3 | 122.1 | 137.6
223.1 | 115.1 | 519.3 | 82.8 | 51.9 | 55.3 | 91.3 | 106.4 | 123.2 | 139.7
224.1 | 116.1 | 519.7 | 84 | 52.7 | 56 | 92.6 | 107.5 | 124.3 | 141.8
225.1 | 117.1 | 520 | 85.1 | 53.5 | 56.7 | 93.7 | 108.8 | 125.3 | 143.8
226.1 | 118.1 | 520.3 | 86.2 | 54.4 | 57.4 | 94.9 | 110 | 126.4 | 145.8
227.1 | 119.1 | 520.3 | 87.4 | 55.1 | 58.1 | 96.2 | 111 | 127.4 | 147.9
228.1 | 120.1 | 520.2 | 88.5 | 55.9 | 58.8 | 97.4 | 112.1 | 128.2 | 149.9
229.1 | 121.1 | 520 | 89.7 | 56.7 | 59.6 | 98.8 | 113.1 | 129.1 | 151.9
230.1 | 122.1 | 520.1 | 90.9 | 57.4 | 60.3 | 100.1 | 114.2 | 129.9 | 153.9
231.1 | 123.1 | 520.2 | 92 | 58.2 | 61.1 | 101.4 | 115.3 | 130.7 | 155.9
232.1 | 124.1 | 520.2 | 93.1 | 59 | 61.8 | 102.7 | 116.1 | 131.4 | 157.8
233.1 | 125.1 | 519.9 | 94.3 | 59.6 | 62.6 | 104.1 | 117.1 | 132 | 159.7
234.1 | 126.1 | 519.8 | 95.5 | 60.4 | 63.4 | 105.5 | 118.3 | 132.7 | 161.6
235.1 | 127.1 | 520 | 96.6 | 61.3 | 64.1 | 106.8 | 119.2 | 133.3 | 163.5
236.1 | 128.1 | 520 | 97.8 | 62.1 | 64.9 | 108.2 | 119.9 | 133.9 | 165.5
237.1 | 129.1 | 519.7 | 98.9 | 62.8 | 65.7 | 109.6 | 120.8 | 134.5 | 167.4
238.1 | 130.1 | 519.5 | 100.1 | 63.7 | 66.4 | 110.9 | 121.8 | 135.2 | 169.2
239.1 | 131.1 | 519.3 | 101.3 | 64.5 | 67.2 | 112.3 | 122.5 | 135.8 | 171.1
240.1 | 132.1 | 519.3 | 102.4 | 65.3 | 68 | 113.6 | 123.2 | 136.4 | 173.1
241.1 | 133.1 | 519.2 | 103.7 | 66.1 | 68.8 | 115 | 124 | 137 | 175
242.1 | 134.1 | 519.2 | 104.9 | 66.9 | 69.5 | 116.4 | 124.7 | 137.6 | 177
243.1 | 135.1 | 519.2 | 106.1 | 67.8 | 70.3 | 117.7 | 125.5 | 138.2 | 178.8
244.1 | 136.1 | 519 | 107.4 | 68.5 | 71.1 | 119 | 126.5 | 138.8 | 180.7
245.1 | 137.1 | 518.8 | 108.7 | 69.3 | 71.9 | 120.3 | 127.4 | 139.3 | 182.5
246.1 | 138.1 | 518.7 | 109.9 | 70.1 | 72.7 | 121.4 | 128.1 | 139.8 | 184.4
247.1 | 139.1 | 518.7 | 111.2 | 70.9 | 73.5 | 122.6 | 128.8 | 140.3 | 186.3
248.1 | 140.1 | 518.7 | 112.4 | 71.7 | 74.3 | 123.6 | 129.6 | 140.8 | 188.1
249.1 | 141.1 | 518.9 | 113.7 | 72.5 | 75.1 | 124.6 | 130.3 | 141.2 | 190
250.1 | 142.1 | 519.1 | 115 | 73.4 | 75.9 | 125.5 | 131 | 141.7 | 191.8
251.1 | 143.1 | 519.2 | 116.2 | 74.2 | 76.7 | 126.3 | 131.5 | 142.1 | 193.6
252.1 | 144.1 | 519.3 | 117.5 | 75 | 77.5 | 127.1 | 132.2 | 142.5 | 195.4
253.1 | 145.1 | 519.3 | 118.9 | 75.8 | 78.3 | 127.8 | 132.7 | 143 | 197.2
254.1 | 146.1 | 519.5 | 120.3 | 76.7 | 79.1 | 128.4 | 133.3 | 143.5 | 198.9
255.1 | 147.1 | 519.9 | 121.7 | 77.5 | 79.9 | 128.9 | 134.1 | 143.9 | 200.7
256.1 | 148.1 | 520.3 | 123.1 | 78.3 | 80.7 | 129.4 | 134.9 | 144.3 | 202.4
257.1 | 149.1 | 520.6 | 124.5 | 79.1 | 81.5 | 129.8 | 135.7 | 144.7 | 204.2
258.1 | 150.1 | 520.9 | 125.8 | 79.9 | 82.3 | 130.3 | 136.4 | 145.2 | 206
259.1 | 151.1 | 521.4 | 127.2 | 80.7 | 83.1 | 130.8 | 137 | 145.7 | 207.8
260.1 | 152.1 | 521.9 | 128.6 | 81.5 | 83.8 | 131.4 | 137.7 | 146.1 | 209.4
261.1 | 153.1 | 522.1 | 129.9 | 82.3 | 84.6 | 132.1 | 138.4 | 146.6 | 211.2
262.1 | 154.1 | 522.4 | 131.1 | 83.1 | 85.4 | 132.8 | 139.2 | 147 | 212.9
263.1 | 155.1 | 522.6 | 132.3 | 83.9 | 86.2 | 133.6 | 139.9 | 147.6 | 214.6
264.1 | 156.1 | 523 | 133.3 | 84.6 | 87.1 | 134.6 | 140.5 | 148.2 | 216.2
265.1 | 157.1 | 523.2 | 134.3 | 85.5 | 87.9 | 135.4 | 141.3 | 148.9 | 217.9
266.1 | 158.1 | 523.2 | 135.2 | 86.3 | 88.7 | 136.1 | 141.9 | 149.5 | 219.5
267.1 | 159.1 | 523.1 | 136 | 87.1 | 89.5 | 136.6 | 142.6 | 150.1 | 221
268.1 | 160.1 | 523 | 136.6 | 88 | 90.3 | 136.9 | 143.4 | 150.7 | 222.5
269.1 | 161.1 | 523 | 136.9 | 88.9 | 91.2 | 137.3 | 144.1 | 151.4 | 224
270.1 | 162.1 | 523 | 137 | 89.9 | 92 | 137.7 | 144.8 | 152.1 | 225.6
271.1 | 163.1 | 523.3 | 136.8 | 90.8 | 92.9 | 138.6 | 145.5 | 152.8 | 227.1
272.1 | 164.1 | 523.3 | 136.3 | 91.8 | 93.8 | 139.7 | 146.1 | 153.5 | 228.6
273.1 | 165.1 | 523.3 | 136.3 | 92.8 | 94.8 | 141 | 146.7 | 154.3 | 230.2
274.1 | 166.1 | 523.5 | 136.9 | 93.8 | 95.7 | 142.1 | 147.5 | 155 | 231.7
275.1 | 167.1 | 523.3 | 138.7 | 94.9 | 96.7 | 143.4 | 148.3 | 155.8 | 233.3
276.1 | 168.1 | 523.2 | 141 | 96.1 | 97.6 | 145 | 148.8 | 156.4 | 234.8
277.1 | 169.1 | 523 | 143.2 | 97.2 | 98.6 | 147 | 149.5 | 157.1 | 236.3
278.1 | 170.1 | 523.1 | 145.6 | 98.4 | 99.6 | 149.4 | 150.2 | 157.8 | 237.8
279.1 | 171.1 | 523.1 | 148.1 | 99.9 | 100.5 | 151.7 | 150.9 | 158.6 | 239.4
280.1 | 172.1 | 522.9 | 150.9 | 101.2 | 101.5 | 154.3 | 151.6 | 159.4 | 240.9
281.1 | 173.1 | 522.7 | 153.6 | 102.4 | 102.5 | 156.6 | 152.5 | 160.2 | 242.4
282.1 | 174.1 | 522.6 | 156.2 | 103.7 | 103.5 | 158.9 | 153.1 | 160.9 | 243.9
283.1 | 175.1 | 522.6 | 158.5 | 105 | 104.5 | 161 | 154 | 161.8 | 245.3
284.1 | 176.1 | 522.7 | 160.7 | 106.2 | 105.5 | 163.6 | 154.8 | 162.6 | 246.8
285.1 | 177.1 | 522.8 | 162.7 | 107.5 | 106.6 | 166 | 155.6 | 163.4 | 248.3
286.1 | 178.1 | 522.5 | 164.7 | 108.9 | 107.6 | 168.1 | 156.2 | 164.2 | 249.7
287.1 | 179.1 | 522.4 | 166.6 | 110.1 | 108.7 | 170.4 | 156.9 | 164.9 | 251.1
288.1 | 180.1 | 522.5 | 168.5 | 111.4 | 109.8 | 172.6 | 157.6 | 165.7 | 252.6
289.1 | 181.1 | 522.5 | 170.3 | 112.6 | 110.8 | 174.2 | 158.3 | 166.4 | 254
290.1 | 182.1 | 522.3 | 172.1 | 113.9 | 111.9 | 176.1 | 159 | 167.3 | 255.4
291.1 | 183.1 | 522.1 | 173.8 | 115.1 | 113.1 | 178.2 | 159.6 | 168.1 | 256.9
292.1 | 184.1 | 521.9 | 175.5 | 116.3 | 114.2 | 180.3 | 160.2 | 168.9 | 258.2
293.1 | 185.1 | 521.9 | 177.2 | 117.6 | 115.3 | 182.1 | 161 | 169.6 | 259.6
294.1 | 186.1 | 522.1 | 178.7 | 118.9 | 116.5 | 183.5 | 161.7 | 170.4 | 261
295.1 | 187.1 | 522.2 | 180.2 | 120.1 | 117.6 | 185.1 | 162.4 | 171.2 | 262.4
296.1 | 188.1 | 522 | 181.7 | 121.4 | 118.8 | 186.8 | 162.9 | 171.9 | 263.7
297.1 | 189.1 | 522 | 183.1 | 122.7 | 120 | 188.4 | 163.7 | 172.5 | 264.9
298.1 | 190.1 | 522.1 | 184.4 | 123.9 | 121.2 | 190.3 | 164.6 | 173.2 | 266.2
299.1 | 191.1 | 522.2 | 185.8 | 125.2 | 122.4 | 191.8 | 165.4 | 173.8 | 267.5
300.1 | 192.1 | 522.1 | 187.2 | 126.4 | 123.6 | 193.1 | 166.4 | 174.4 | 268.8
301.1 | 193.1 | 521.9 | 188.6 | 127.6 | 124.8 | 194.5 | 167.2 | 174.9 | 270
302.1 | 194.1 | 521.6 | 189.9 | 128.9 | 126 | 195.9 | 168 | 175.4 | 271.2
303.1 | 195.1 | 521.5 | 191.2 | 130.1 | 127.1 | 197 | 168.6 | 175.9 | 272.5
304.1 | 196.1 | 521.4 | 192.6 | 131.3 | 128.3 | 198.7 | 169.3 | 176.4 | 273.8
305.1 | 197.1 | 521.1 | 193.9 | 132.5 | 129.5 | 199.7 | 170.1 | 177 | 275
306.1 | 198.1 | 521.1 | 195.2 | 133.7 | 130.7 | 201.1 | 170.8 | 177.5 | 276.3
307.1 | 199.1 | 521 | 196.4 | 134.9 | 131.9 | 202.3 | 171.5 | 178.1 | 277.5
308.1 | 200.1 | 520.9 | 197.5 | 136.1 | 133.1 | 203.5 | 172.2 | 178.6 | 278.7
309.1 | 201.1 | 520.8 | 198.7 | 137.3 | 134.3 | 204.5 | 172.9 | 179.1 | 279.9
310.1 | 202.1 | 520.4 | 200 | 138.4 | 135.4 | 205.2 | 173.6 | 179.6 | 281.1
311.1 | 203.1 | 520.2 | 201.3 | 139.6 | 136.6 | 206.3 | 174.3 | 180 | 282.3
312.1 | 204.1 | 520.1 | 202.7 | 140.7 | 137.8 | 207.4 | 175 | 180.5 | 283.4
313.1 | 205.1 | 520.2 | 204.1 | 141.8 | 139 | 208.6 | 175.7 | 181 | 284.5
314.1 | 206.1 | 520.2 | 205.4 | 143 | 140.1 | 209.3 | 176.3 | 181.4 | 285.7
315.1 | 207.1 | 520.3 | 206.8 | 144.1 | 141.3 | 210 | 177 | 181.9 | 286.8
316.1 | 208.1 | 520.3 | 208.1 | 145.2 | 142.4 | 211.5 | 177.6 | 182.3 | 287.9
317.1 | 209.1 | 520.4 | 209.3 | 146.3 | 143.6 | 212.8 | 178.2 | 182.8 | 289
318.1 | 210.1 | 520.5 | 210.3 | 147.5 | 144.7 | 212.9 | 178.9 | 183.3 | 290.1
319.1 | 211.1 | 520.8 | 211.3 | 148.6 | 145.8 | 213.9 | 179.6 | 183.7 | 291.2
320.1 | 212.1 | 520.9 | 212.4 | 149.8 | 146.9 | 215 | 180.2 | 184.2 | 292.2
321.1 | 213.1 | 521 | 213.5 | 151 | 148 | 216.2 | 180.9 | 184.6 | 293.2
322.1 | 214.1 | 521 | 214.5 | 152.1 | 149.1 | 216.4 | 181.6 | 185 | 294.3
323.1 | 215.1 | 520.9 | 215.5 | 153.3 | 150.2 | 217 | 182.3 | 185.5 | 295.3
324.1 | 216.1 | 521.1 | 216.5 | 154.4 | 151.3 | 218.4 | 183 | 185.9 | 296.3
325.1 | 217.1 | 521.1 | 217.3 | 155.5 | 152.4 | 219.8 | 183.7 | 186.4 | 297.3
326.1 | 218.1 | 521 | 218.3 | 156.6 | 153.5 | 221.5 | 184.4 | 186.8 | 298.2
327.1 | 219.1 | 520.8 | 219.3 | 157.7 | 154.6 | 223.2 | 185.1 | 187.3 | 299.2
328.1 | 220.1 | 521.1 | 220.3 | 158.8 | 155.7 | 224.4 | 185.9 | 187.7 | 300.3
329.1 | 221.1 | 521.3 | 221.4 | 159.8 | 156.7 | 225.5 | 186.6 | 188.2 | 301.2
330.1 | 222.1 | 521.4 | 222.3 | 160.9 | 157.8 | 226.8 | 187.3 | 188.7 | 302.2
331.1 | 223.1 | 521.3 | 223.2 | 162 | 158.8 | 227.9 | 188 | 189.2 | 303.1
332.1 | 224.1 | 521.2 | 224.1 | 163 | 159.9 | 229.1 | 188.7 | 189.7 | 304.1
333.1 | 225.1 | 521.1 | 225.1 | 164.1 | 161 | 230.2 | 189.4 | 190.2 | 305
334.1 | 226.1 | 521.2 | 226.1 | 165.1 | 162 | 231.6 | 190.1 | 190.7 | 305.9
335.1 | 227.1 | 520.9 | 227.1 | 166.2 | 163 | 233.2 | 190.9 | 191.2 | 306.9
336.1 | 228.1 | 520.8 | 228.2 | 167.2 | 164.1 | 233.9 | 191.6 | 191.7 | 307.8
337.1 | 229.1 | 520.8 | 229.2 | 168.2 | 165.1 | 234.9 | 192.3 | 192.2 | 308.8
338.1 | 230.1 | 520.8 | 230.2 | 169.2 | 166.2 | 235.8 | 193 | 192.8 | 309.7
339.1 | 231.1 | 520.8 | 231 | 170.2 | 167.2 | 236.4 | 193.7 | 193.3 | 310.6
340.1 | 232.1 | 521 | 231.8 | 171.3 | 168.2 | 237.1 | 194.4 | 193.8 | 311.5
341.1 | 233.1 | 521.1 | 232.8 | 172.2 | 169.3 | 238.1 | 195.1 | 194.3 | 312.4
342.1 | 234.1 | 521.2 | 233.8 | 173.3 | 170.3 | 238.5 | 195.8 | 194.8 | 313.3
343.1 | 235.1 | 521.3 | 234.7 | 174.3 | 171.3 | 239.3 | 196.5 | 195.3 | 314.2
344.1 | 236.1 | 521.5 | 235.5 | 175.3 | 172.3 | 240.2 | 197.2 | 195.8 | 315.1
345.1 | 237.1 | 521.4 | 236.2 | 176.3 | 173.3 | 241.3 | 197.8 | 196.3 | 316
346.1 | 238.1 | 521.2 | 237.1 | 177.3 | 174.3 | 241.9 | 198.5 | 196.8 | 316.8
347.1 | 239.1 | 521.3 | 237.9 | 178.3 | 175.3 | 242.6 | 199.1 | 197.3 | 317.6
348.1 | 240.1 | 521.2 | 238.7 | 179.3 | 176.3 | 243.9 | 199.8 | 197.8 | 318.4
349.1 | 241.1 | 521.4 | 239.5 | 180.3 | 177.3 | 244.6 | 200.5 | 198.2 | 319.2
350.1 | 242.1 | 521.3 | 240.5 | 181.3 | 178.3 | 245.3 | 201.1 | 198.7 | 320
351.1 | 243.1 | 521.2 | 241.4 | 182.2 | 179.3 | 245.5 | 201.8 | 199.2 | 320.8
352.1 | 244.1 | 521.1 | 242.2 | 183.1 | 180.3 | 246.6 | 202.4 | 199.7 | 321.6
353.1 | 245.1 | 520.8 | 242.8 | 184.1 | 181.2 | 247.1 | 203.1 | 200.1 | 322.3
354.1 | 246.1 | 520.8 | 243.3 | 185.1 | 182.2 | 247.9 | 203.7 | 200.6 | 323
355.1 | 247.1 | 520.8 | 244.3 | 186 | 183.2 | 249.3 | 204.2 | 201.1 | 323.8
356.1 | 248.1 | 520.9 | 244.9 | 187 | 184.2 | 250.3 | 204.8 | 201.6 | 324.5
357.1 | 249.1 | 520.8 | 245.5 | 187.9 | 185.1 | 251.2 | 205.4 | 202 | 325.2
358.1 | 250.1 | 520.8 | 246.2 | 188.9 | 186.1 | 252 | 206 | 202.5 | 325.9
359.1 | 251.1 | 520.7 | 247 | 189.9 | 187 | 253 | 206.7 | 203 | 326.6
360.1 | 252.1 | 520.8 | 247.7 | 190.8 | 188 | 254.1 | 207.4 | 203.4 | 327.4
361.1 | 253.1 | 520.8 | 248.6 | 191.7 | 188.9 | 255.1 | 208.1 | 203.9 | 328.1
362.1 | 254.1 | 520.6 | 249.4 | 192.6 | 189.9 | 256.2 | 208.8 | 204.4 | 328.8
363.1 | 255.1 | 520.5 | 250.3 | 193.5 | 190.8 | 256.7 | 209.5 | 204.8 | 329.5
364.1 | 256.1 | 520.5 | 251.1 | 194.5 | 191.7 | 257.4 | 210.1 | 205.3 | 330.2
365.1 | 257.1 | 520.5 | 251.8 | 195.3 | 192.7 | 258.3 | 210.7 | 205.8 | 330.8
366.1 | 258.1 | 520.5 | 252.5 | 196.2 | 193.6 | 259.1 | 211.3 | 206.3 | 331.5
367.1 | 259.1 | 520.6 | 253.5 | 197.1 | 194.5 | 259.7 | 211.9 | 206.8 | 332.2
368.1 | 260.1 | 520.6 | 254.7 | 198.1 | 195.4 | 260.2 | 212.5 | 207.2 | 332.8
369.1 | 261.1 | 520.4 | 255.6 | 198.9 | 196.3 | 260.4 | 213.1 | 207.7 | 333.5
370.1 | 262.1 | 520.4 | 256.7 | 199.8 | 197.2 | 261 | 213.7 | 208.1 | 334.2
371.1 | 263.1 | 520.5 | 257.7 | 200.6 | 198.1 | 262.2 | 214.4 | 208.6 | 334.8
372.1 | 264.1 | 520.6 | 258.5 | 201.5 | 199 | 262.8 | 215 | 209 | 335.4
373.1 | 265.1 | 520.6 | 259.5 | 202.3 | 200 | 263.3 | 215.7 | 209.4 | 336
374.1 | 266.1 | 520.6 | 260.5 | 203.2 | 200.9 | 263.2 | 216.3 | 209.9 | 336.6
375.1 | 267.1 | 520.5 | 261.5 | 204.1 | 201.8 | 263.5 | 216.9 | 210.3 | 337.2
376.1 | 268.1 | 520.5 | 262.3 | 204.9 | 202.7 | 264.2 | 217.5 | 210.7 | 337.8
377.1 | 269.1 | 520.5 | 263.2 | 205.7 | 203.6 | 265.7 | 218.2 | 211.1 | 338.4
378.1 | 270.1 | 520.6 | 264.1 | 206.6 | 204.5 | 266.7 | 218.9 | 211.6 | 338.9
379.1 | 271.1 | 520.6 | 265.4 | 207.3 | 205.4 | 268.1 | 219.5 | 212 | 339.5
380.1 | 272.1 | 520.8 | 266.1 | 208.1 | 206.3 | 270.2 | 220.1 | 212.4 | 340.1
381.1 | 273.1 | 521 | 266.8 | 208.9 | 207.1 | 272.4 | 220.7 | 212.8 | 340.7
382.1 | 274.1 | 521 | 267.7 | 209.8 | 208 | 273.6 | 221.4 | 213.2 | 341.3
383.1 | 275.1 | 521.1 | 268.7 | 210.5 | 208.9 | 274.7 | 222 | 213.6 | 341.9
384.1 | 276.1 | 521.2 | 269.8 | 211.3 | 209.7 | 275.7 | 222.7 | 214 | 342.4
385.1 | 277.1 | 521.3 | 271.4 | 212.1 | 210.6 | 276.8 | 223.4 | 214.4 | 343
386.1 | 278.1 | 521.5 | 272.9 | 212.9 | 211.4 | 276.6 | 224 | 214.9 | 343.6
387.1 | 279.1 | 521.5 | 274.2 | 213.8 | 212.3 | 277.1 | 224.6 | 215.3 | 344.1
388.1 | 280.1 | 521.7 | 275.7 | 214.6 | 213.1 | 277.1 | 225.2 | 215.7 | 344.6
389.1 | 281.1 | 521.7 | 276.5 | 215.3 | 214 | 278.6 | 225.8 | 216.2 | 345.2
390.1 | 282.1 | 521.6 | 277.3 | 216.1 | 214.8 | 279.9 | 226.3 | 216.6 | 345.7
391.1 | 283.1 | 521.5 | 278.6 | 216.8 | 215.6 | 280.7 | 226.8 | 217 | 346.3
392.1 | 284.1 | 521.2 | 279.9 | 217.6 | 216.5 | 281 | 227.4 | 217.5 | 346.8
393.1 | 285.1 | 521 | 280.9 | 218.3 | 217.3 | 282.5 | 228 | 217.9 | 347.3
394.1 | 286.1 | 521.1 | 281.2 | 219.1 | 218.1 | 283.1 | 228.5 | 218.4 | 347.8
395.1 | 287.1 | 521.1 | 282.1 | 219.8 | 218.9 | 284.4 | 229.1 | 218.8 | 348.4
396.1 | 288.1 | 521 | 282.2 | 220.6 | 219.7 | 286.5 | 229.6 | 219.2 | 348.9
397.1 | 289.1 | 520.9 | 282.6 | 221.3 | 220.5 | 288.3 | 230.2 | 219.7 | 349.4
398.1 | 290.1 | 520.8 | 283.2 | 222.1 | 221.3 | 289.8 | 230.8 | 220.1 | 350
399.1 | 291.1 | 520.8 | 284.3 | 222.8 | 222.1 | 290.1 | 231.4 | 220.5 | 350.5
400.1 | 292.1 | 520.5 | 285.7 | 223.5 | 222.9 | 290.3 | 231.9 | 220.9 | 350.9
401.1 | 293.1 | 520.3 | 286.5 | 224.3 | 223.7 | 290.4 | 232.5 | 221.4 | 351.4
402.1 | 294.1 | 520.4 | 287 | 225 | 224.5 | 291.4 | 233 | 221.8 | 351.9
403.1 | 295.1 | 520.4 | 287.2 | 225.7 | 225.3 | 292.4 | 233.6 | 222.2 | 352.4
404.1 | 296.1 | 520.3 | 287.3 | 226.5 | 226.1 | 292.9 | 234.1 | 222.7 | 352.8
405.1 | 297.1 | 520.3 | 288.5 | 227.3 | 226.9 | 293.1 | 234.6 | 223.2 | 353.3
406.1 | 298.1 | 520.2 | 289.6 | 228.1 | 227.7 | 293.8 | 235.1 | 223.6 | 353.8
407.1 | 299.1 | 520.2 | 290 | 228.8 | 228.5 | 294.4 | 235.7 | 224.1 | 354.3
408.1 | 300.1 | 520.3 | 290.5 | 229.5 | 229.3 | 295.5 | 236.2 | 224.5 | 354.8
409.1 | 301.1 | 520.4 | 291.2 | 230.2 | 230.1 | 296 | 236.7 | 225 | 355.3
410.1 | 302.1 | 520.2 | 291.9 | 231 | 230.9 | 296.3 | 237.2 | 225.4 | 355.8
411.1 | 303.1 | 520.3 | 292.3 | 231.8 | 231.6 | 297 | 237.8 | 225.8 | 356.3
412.1 | 304.1 | 520.2 | 292.8 | 232.5 | 232.4 | 297 | 238.3 | 226.3 | 356.7
413.1 | 305.1 | 520.2 | 293.5 | 233.3 | 233.2 | 297.5 | 238.8 | 226.7 | 357.2
414.1 | 306.1 | 520.1 | 294.2 | 234 | 234 | 299.5 | 239.3 | 227.1 | 357.7
415.1 | 307.1 | 520.1 | 295.3 | 234.8 | 234.8 | 301.4 | 239.7 | 227.6 | 358.2
416.1 | 308.1 | 520.2 | 296.1 | 235.5 | 235.5 | 303.3 | 240.3 | 228 | 358.7
417.1 | 309.1 | 520.2 | 297.8 | 236.3 | 236.3 | 304.3 | 240.8 | 228.5 | 359.1
418.1 | 310.1 | 520 | 299.6 | 237 | 237.1 | 305.4 | 241.4 | 229 | 359.6
419.1 | 311.1 | 519.7 | 299.9 | 237.7 | 237.9 | 306.4 | 242 | 229.4 | 360.1
420.1 | 312.1 | 519.6 | 300.4 | 238.5 | 238.6 | 307.5 | 242.5 | 229.9 | 360.5
421.1 | 313.1 | 519.5 | 301 | 239.2 | 239.4 | 307.1 | 243 | 230.4 | 360.9
422.1 | 314.1 | 519.4 | 301.4 | 239.9 | 240.2 | 307.4 | 243.5 | 230.9 | 361.3
423.1 | 315.1 | 519.3 | 301 | 240.6 | 241 | 308.1 | 243.9 | 231.3 | 361.7
424.1 | 316.1 | 519.3 | 300.6 | 241.4 | 241.8 | 308.3 | 244.4 | 231.7 | 362.1
425.1 | 317.1 | 519.1 | 300.8 | 242.1 | 242.5 | 308.7 | 244.9 | 232.2 | 362.4
426.1 | 318.1 | 518.9 | 301.1 | 242.9 | 243.3 | 309.7 | 245.4 | 232.6 | 362.8
427.1 | 319.1 | 518.8 | 301 | 243.6 | 244 | 310.8 | 245.8 | 233 | 363.2
428.1 | 320.1 | 518.8 | 301.6 | 244.3 | 244.8 | 311.3 | 246.2 | 233.4 | 363.5
429.1 | 321.1 | 519.1 | 302.2 | 245 | 245.5 | 311.9 | 246.6 | 233.9 | 363.9
430.1 | 322.1 | 519.3 | 303.4 | 245.7 | 246.2 | 312.3 | 247 | 234.3 | 364.3
431.1 | 323.1 | 519.5 | 303.8 | 246.5 | 246.9 | 313.8 | 247.4 | 234.7 | 364.7
432.1 | 324.1 | 519.7 | 303.7 | 247.1 | 247.7 | 315.5 | 247.8 | 235.1 | 365
433.1 | 325.1 | 520 | 302.7 | 247.8 | 248.4 | 316.1 | 248.3 | 235.6 | 365.3
434.1 | 326.1 | 520.1 | 302.6 | 248.5 | 249 | 316.7 | 248.7 | 236 | 365.7
435.1 | 327.1 | 520.3 | 302.3 | 249.2 | 249.7 | 317.1 | 249.2 | 236.4 | 366.1
436.1 | 328.1 | 520.3 | 301.4 | 249.9 | 250.5 | 317.8 | 249.6 | 236.8 | 366.4
437.1 | 329.1 | 520.4 | 301.5 | 250.6 | 251.2 | 318.6 | 250 | 237.3 | 366.8
438.1 | 330.1 | 520.4 | 300.7 | 251.3 | 251.8 | 318.8 | 250.4 | 237.7 | 367.1
439.1 | 331.1 | 520.4 | 300.5 | 252 | 252.5 | 318.7 | 250.8 | 238.1 | 367.5
440.1 | 332.1 | 520.8 | 301.2 | 252.6 | 253.2 | 319.1 | 251.2 | 238.5 | 367.8
441.1 | 333.1 | 520.8 | 301.4 | 253.3 | 253.9 | 320.1 | 251.6 | 238.9 | 368.1
442.1 | 334.1 | 521 | 301.9 | 254 | 254.6 | 320.9 | 252 | 239.3 | 368.5
443.1 | 335.1 | 521 | 302.9 | 254.6 | 255.3 | 321 | 252.4 | 239.7 | 368.8
444.1 | 336.1 | 521 | 304.2 | 255.3 | 255.9 | 321.2 | 252.8 | 240.2 | 369.1
445.1 | 337.1 | 521.1 | 304.1 | 256 | 256.6 | 321.2 | 253.2 | 240.6 | 369.5
446.1 | 338.1 | 521 | 305.1 | 256.7 | 257.2 | 321.8 | 253.5 | 241 | 369.8
447.1 | 339.1 | 520.8 | 305.4 | 257.3 | 257.9 | 322.1 | 253.9 | 241.4 | 370.2
448.1 | 340.1 | 520.7 | 305.1 | 258 | 258.6 | 322.7 | 254.3 | 241.8 | 370.6
449.1 | 341.1 | 520.7 | 305.6 | 258.6 | 259.2 | 324 | 254.6 | 242.2 | 370.9
450.1 | 342.1 | 520.7 | 306.3 | 259.3 | 259.9 | 325 | 254.9 | 242.6 | 371.2
451.1 | 343.1 | 520.8 | 307.3 | 259.9 | 260.5 | 325.6 | 255.2 | 243 | 371.5
452.1 | 344.1 | 520.9 | 309.2 | 260.6 | 261.2 | 325.2 | 255.6 | 243.5 | 371.9
453.1 | 345.1 | 520.8 | 310.5 | 261.2 | 261.9 | 323.9 | 255.9 | 243.9 | 372.2
454.1 | 346.1 | 520.7 | 310.3 | 261.8 | 262.5 | 324 | 256.2 | 244.3 | 372.4
455.1 | 347.1 | 520.4 | 309.7 | 262.4 | 263.2 | 325.2 | 256.5 | 244.7 | 372.7
456.1 | 348.1 | 520.1 | 309.5 | 263 | 263.8 | 326.4 | 256.9 | 245.1 | 373
457.1 | 349.1 | 519.9 | 309.7 | 263.6 | 264.5 | 327.1 | 257.2 | 245.4 | 373.3
458.1 | 350.1 | 519.7 | 309.1 | 264.2 | 265.1 | 328.5 | 257.5 | 245.8 | 373.6
459.1 | 351.1 | 519.6 | 308.5 | 264.8 | 265.7 | 329.8 | 257.8 | 246.2 | 373.8
460.1 | 352.1 | 519.4 | 308.8 | 265.3 | 266.4 | 328.9 | 258.1 | 246.5 | 374.1
461.1 | 353.1 | 519.3 | 309.2 | 266 | 267 | 329.1 | 258.5 | 246.9 | 374.4
462.1 | 354.1 | 519.2 | 309.1 | 266.6 | 267.6 | 329.4 | 258.8 | 247.2 | 374.7
463.1 | 355.1 | 519.4 | 308.3 | 267.2 | 268.2 | 330.1 | 259.1 | 247.5 | 375
464.1 | 356.1 | 519.6 | 307.2 | 267.8 | 268.8 | 331.7 | 259.4 | 247.9 | 375.2
465.1 | 357.1 | 519.7 | 307.9 | 268.4 | 269.4 | 332.6 | 259.7 | 248.2 | 375.5
466.1 | 358.1 | 520 | 308.6 | 269 | 270 | 333.5 | 260 | 248.6 | 375.8
467.1 | 359.1 | 520 | 309.5 | 269.6 | 270.5 | 333.6 | 260.2 | 248.9 | 376
468.1 | 360.1 | 519.9 | 309.9 | 270.2 | 271.2 | 334.3 | 260.5 | 249.2 | 376.3
469.1 | 361.1 | 519.9 | 309.2 | 270.8 | 271.7 | 335.9 | 260.8 | 249.5 | 376.5
470.1 | 362.1 | 519.7 | 309.2 | 271.4 | 272.3 | 336.1 | 261.1 | 249.9 | 376.8
471.1 | 363.1 | 519.5 | 310.6 | 271.9 | 272.9 | 336.4 | 261.3 | 250.2 | 377.1
472.1 | 364.1 | 519.6 | 311.7 | 272.5 | 273.6 | 337.6 | 261.5 | 250.5 | 377.4
473.1 | 365.1 | 519.7 | 312.1 | 273.1 | 274.1 | 338.2 | 261.8 | 250.8 | 377.6
474.1 | 366.1 | 519.7 | 313.9 | 273.7 | 274.7 | 338.1 | 262 | 251.1 | 377.9
475.1 | 367.1 | 519.3 | 315.9 | 274.2 | 275.3 | 338.4 | 262.3 | 251.4 | 378.2
476.1 | 368.1 | 519.3 | 317.5 | 274.8 | 275.9 | 339.3 | 262.6 | 251.7 | 378.5
477.1 | 369.1 | 519.4 | 317.5 | 275.4 | 276.5 | 340.1 | 262.8 | 252 | 378.7
478.1 | 370.1 | 519.5 | 317.2 | 275.9 | 277.1 | 341.4 | 263.1 | 252.3 | 379
479.1 | 371.1 | 519.7 | 318.3 | 276.5 | 277.7 | 342.8 | 263.3 | 252.6 | 379.3
480.1 | 372.1 | 519.8 | 319.5 | 277 | 278.3 | 343 | 263.6 | 252.9 | 379.6
481.1 | 373.1 | 519.9 | 319.1 | 277.6 | 278.9 | 341.7 | 263.8 | 253.1 | 379.8
482.1 | 374.1 | 520 | 318.1 | 278.2 | 279.4 | 342.7 | 264 | 253.4 | 380.1
483.1 | 375.1 | 520 | 318 | 278.7 | 280 | 342.7 | 264.3 | 253.6 | 380.3
484.1 | 376.1 | 519.9 | 318.5 | 279.3 | 280.6 | 342.3 | 264.6 | 253.9 | 380.6
485.1 | 377.1 | 519.9 | 319.8 | 279.8 | 281.2 | 343.6 | 264.9 | 254.2 | 380.8
486.1 | 378.1 | 519.8 | 320.1 | 280.4 | 281.8 | 344.4 | 265.2 | 254.4 | 381
487.1 | 379.1 | 519.8 | 319.7 | 280.9 | 282.4 | 345 | 265.4 | 254.7 | 381.2
488.1 | 380.1 | 519.8 | 319.1 | 281.5 | 283 | 346.2 | 265.7 | 255 | 381.4
489.1 | 381.1 | 519.9 | 318.6 | 282 | 283.6 | 347.1 | 266 | 255.3 | 381.7
490.1 | 382.1 | 519.9 | 319.1 | 282.6 | 284.2 | 347.7 | 266.3 | 255.6 | 381.9
491.1 | 383.1 | 519.8 | 320.4 | 283.2 | 284.8 | 347.9 | 266.5 | 255.9 | 382.2
492.1 | 384.1 | 519.9 | 321.1 | 283.7 | 285.4 | 348.6 | 266.8 | 256.2 | 382.4
493.1 | 385.1 | 520 | 321.2 | 284.2 | 286.1 | 349.3 | 267.1 | 256.5 | 382.7
494.1 | 386.1 | 520.1 | 320.4 | 284.7 | 286.7 | 349.4 | 267.4 | 256.8 | 383
495.1 | 387.1 | 520.4 | 319.8 | 285.1 | 287.3 | 350 | 267.7 | 257.1 | 383.2
496.1 | 388.1 | 520.5 | 320.6 | 285.6 | 287.9 | 350.1 | 268 | 257.4 | 383.4
497.1 | 389.1 | 520.5 | 320.8 | 286.1 | 288.5 | 350.8 | 268.3 | 257.7 | 383.6
498.1 | 390.1 | 520.6 | 320.9 | 286.5 | 289.1 | 350 | 268.5 | 258 | 383.9
499.1 | 391.1 | 520.6 | 321.6 | 287 | 289.7 | 350.7 | 268.8 | 258.3 | 384.1
500.1 | 392.1 | 520.6 | 321.4 | 287.5 | 290.3 | 351.8 | 269.1 | 258.6 | 384.3
501.1 | 393.1 | 520.6 | 321 | 288.1 | 290.8 | 353.1 | 269.4 | 259 | 384.6
502.1 | 394.1 | 520.6 | 321.1 | 288.7 | 291.4 | 353.9 | 269.7 | 259.3 | 384.8
503.1 | 395.1 | 520.7 | 321.7 | 289 | 292 | 354.5 | 270 | 259.6 | 385.1
504.1 | 396.1 | 520.9 | 322.4 | 289.5 | 292.6 | 355.6 | 270.3 | 259.9 | 385.3
505.1 | 397.1 | 520.8 | 322.3 | 289.9 | 293.2 | 355.4 | 270.6 | 260.2 | 385.5
506.1 | 398.1 | 520.8 | 322.4 | 290.3 | 293.8 | 355.2 | 271 | 260.5 | 385.8
507.1 | 399.1 | 520.7 | 322.3 | 290.9 | 294.4 | 355.7 | 271.3 | 260.7 | 386
508.1 | 400.1 | 520.8 | 322.4 | 291.5 | 295 | 355.6 | 271.6 | 261 | 386.3
509.1 | 401.1 | 520.7 | 323.5 | 292 | 295.6 | 355.9 | 271.9 | 261.3 | 386.5
510.1 | 402.1 | 520.7 | 324.1 | 292.4 | 296.2 | 356 | 272.2 | 261.6 | 386.7
511.1 | 403.1 | 520.9 | 324.9 | 293.1 | 296.8 | 357.1 | 272.4 | 261.9 | 387
512.1 | 404.1 | 521 | 326.1 | 293.8 | 297.4 | 356.8 | 272.7 | 262.2 | 387.2
513.1 | 405.1 | 521.1 | 327.1 | 294.2 | 298 | 357.1 | 273 | 262.5 | 387.4
514.1 | 406.1 | 521.1 | 328.1 | 294.6 | 298.6 | 357.3 | 273.3 | 262.7 | 387.7
515.1 | 407.1 | 521.2 | 328.9 | 295.2 | 299.2 | 357.7 | 273.5 | 263 | 387.9
516.1 | 408.1 | 521.4 | 329.2 | 295.8 | 299.7 | 358.8 | 273.8 | 263.3 | 388.1
517.1 | 409.1 | 521.6 | 329.3 | 296.4 | 300.3 | 358.8 | 274.1 | 263.6 | 388.3
518.1 | 410.1 | 521.7 | 329 | 297.1 | 300.9 | 359.2 | 274.4 | 263.8 | 388.5
519.1 | 411.1 | 521.9 | 329.7 | 297.7 | 301.5 | 358.5 | 274.7 | 264.1 | 388.7
520.1 | 412.1 | 521.9 | 330.6 | 298.2 | 302.1 | 357.5 | 275 | 264.3 | 389
521.1 | 413.1 | 521.9 | 330.9 | 298.7 | 302.7 | 357.6 | 275.3 | 264.5 | 389.2
522.1 | 414.1 | 521.9 | 331.1 | 299.3 | 303.2 | 357.3 | 275.6 | 264.7 | 389.5
523.1 | 415.1 | 521.7 | 331.5 | 300 | 303.8 | 357 | 275.9 | 264.9 | 389.7
524.1 | 416.1 | 521.6 | 331 | 300.6 | 304.4 | 359.3 | 276.2 | 265.1 | 390
525.1 | 417.1 | 521.6 | 332.1 | 301.1 | 305 | 360.9 | 276.6 | 265.3 | 390.3
526.1 | 418.1 | 521.1 | 332.1 | 301.8 | 305.5 | 362.2 | 276.9 | 265.4 | 390.5
527.1 | 419.1 | 521 | 333 | 302.3 | 306.1 | 362.3 | 277.2 | 265.6 | 390.7
528.1 | 420.1 | 520.9 | 334 | 302.8 | 306.6 | 362.4 | 277.5 | 265.8 | 390.8
529.1 | 421.1 | 520.5 | 334.6 | 303.3 | 307.2 | 362 | 277.8 | 265.9 | 391
530.1 | 422.1 | 520.3 | 335.5 | 303.9 | 307.8 | 361.9 | 278.1 | 266.1 | 391.1
531.1 | 423.1 | 520.2 | 336.4 | 304.4 | 308.3 | 362.2 | 278.5 | 266.3 | 391.3
532.1 | 424.1 | 520 | 336 | 305 | 308.9 | 362.9 | 278.8 | 266.5 | 391.5
533.1 | 425.1 | 519.9 | 336.3 | 305.4 | 309.4 | 364.1 | 279.1 | 266.6 | 391.6
534.1 | 426.1 | 519.7 | 335.7 | 305.9 | 309.9 | 364.6 | 279.4 | 266.8 | 391.8
535.1 | 427.1 | 519.6 | 336.2 | 306.5 | 310.5 | 364.1 | 279.7 | 267 | 391.9
536.1 | 428.1 | 519.8 | 336.2 | 307.1 | 311 | 364.8 | 280 | 267.2 | 392.1
537.1 | 429.1 | 519.9 | 335.4 | 307.7 | 311.6 | 365.8 | 280.4 | 267.3 | 392.3
538.1 | 430.1 | 520 | 335.4 | 308.3 | 312.1 | 367 | 280.7 | 267.5 | 392.5
539.1 | 431.1 | 519.9 | 335.6 | 308.7 | 312.7 | 368.5 | 281 | 267.7 | 392.7
540.1 | 432.1 | 519.8 | 335.4 | 309.3 | 313.2 | 369 | 281.3 | 267.9 | 392.9
541.1 | 433.1 | 519.7 | 335.4 | 309.8 | 313.7 | 368.6 | 281.6 | 268 | 393.1
542.1 | 434.1 | 519.6 | 336.1 | 310.3 | 314.2 | 368 | 281.9 | 268.2 | 393.3
543.1 | 435.1 | 519.5 | 336.6 | 310.9 | 314.8 | 367.6 | 282.2 | 268.4 | 393.5
544.1 | 436.1 | 519.4 | 337.4 | 311.3 | 315.3 | 368.8 | 282.5 | 268.6 | 393.7
545.1 | 437.1 | 519.3 | 337.6 | 311.8 | 315.8 | 369.7 | 282.8 | 268.8 | 393.8
546.1 | 438.1 | 519.2 | 338.5 | 312.3 | 316.4 | 369.1 | 283.2 | 268.9 | 393.9
547.1 | 439.1 | 519.2 | 339.1 | 312.9 | 316.9 | 369.8 | 283.5 | 269.1 | 394.1
548.1 | 440.1 | 519.1 | 340.1 | 313.4 | 317.5 | 368.9 | 283.8 | 269.3 | 394.2
549.1 | 441.1 | 519.2 | 340.5 | 313.8 | 318 | 368.9 | 284.1 | 269.4 | 394.4
550.1 | 442.1 | 519.1 | 340.5 | 314.4 | 318.5 | 368.6 | 284.4 | 269.6 | 394.6
551.1 | 443.1 | 519.1 | 341.7 | 315 | 319.1 | 368.3 | 284.6 | 269.8 | 394.7
552.1 | 444.1 | 519.1 | 342.5 | 315.5 | 319.6 | 368.8 | 284.9 | 269.9 | 394.9
553.1 | 445.1 | 519.2 | 342.3 | 316 | 320.1 | 369.6 | 285.2 | 270.1 | 395.1
554.1 | 446.1 | 519.4 | 342.7 | 316.5 | 320.7 | 369.9 | 285.5 | 270.3 | 395.2
555.1 | 447.1 | 519.3 | 343.7 | 317 | 321.2 | 370.5 | 285.8 | 270.5 | 395.4
556.1 | 448.1 | 519.2 | 344.4 | 317.5 | 321.7 | 371.2 | 286.1 | 270.6 | 395.5
557.1 | 449.1 | 519.2 | 345.1 | 318 | 322.3 | 372 | 286.4 | 270.8 | 395.7
558.1 | 450.1 | 519.3 | 346 | 318.5 | 322.8 | 372.6 | 286.6 | 271 | 395.9
559.1 | 451.1 | 519.2 | 346.2 | 319 | 323.3 | 373 | 286.9 | 271.2 | 396
560.1 | 452.1 | 519.3 | 345.8 | 319.5 | 323.8 | 373.2 | 287.2 | 271.3 | 396.1
561.1 | 453.1 | 519.2 | 346.2 | 320 | 324.3 | 374 | 287.5 | 271.5 | 396.3
562.1 | 454.1 | 519.2 | 346.3 | 320.5 | 324.8 | 374 | 287.8 | 271.7 | 396.4
563.1 | 455.1 | 519.2 | 346.2 | 321 | 325.4 | 374 | 288.1 | 271.8 | 396.5
564.1 | 456.1 | 519 | 345.9 | 321.4 | 325.9 | 373.4 | 288.5 | 272 | 396.7
565.1 | 457.1 | 518.8 | 346.6 | 321.9 | 326.4 | 374.4 | 288.8 | 272.2 | 396.9
566.1 | 458.1 | 519 | 347.6 | 322.4 | 326.9 | 375.8 | 289.2 | 272.4 | 397.1
567.1 | 459.1 | 519.1 | 347.9 | 323 | 327.4 | 377.1 | 289.5 | 272.6 | 397.2
568.1 | 460.1 | 519.2 | 348.3 | 323.4 | 328 | 377.5 | 289.8 | 272.8 | 397.4
569.1 | 461.1 | 519.4 | 348.8 | 323.9 | 328.5 | 377.4 | 290.2 | 273 | 397.5
570.1 | 462.1 | 519.7 | 349.4 | 324.5 | 329 | 377.7 | 290.5 | 273.2 | 397.7
571.1 | 463.1 | 520 | 350.1 | 324.9 | 329.5 | 377.3 | 290.9 | 273.4 | 397.8
572.1 | 464.1 | 520 | 349.4 | 325.4 | 330 | 377.4 | 291.2 | 273.6 | 398
573.1 | 465.1 | 520.2 | 348.9 | 325.8 | 330.4 | 376.7 | 291.5 | 273.9 | 398.1
574.1 | 466.1 | 520.4 | 348.9 | 326.3 | 331 | 377.6 | 291.8 | 274.1 | 398.3
575.1 | 467.1 | 520.5 | 349.5 | 326.8 | 331.4 | 377.3 | 292.2 | 274.3 | 398.5
576.1 | 468.1 | 520.5 | 348.5 | 327.3 | 331.9 | 377 | 292.5 | 274.5 | 398.6
577.1 | 469.1 | 520.3 | 348.1 | 327.8 | 332.4 | 376.3 | 292.9 | 274.8 | 398.7
578.1 | 470.1 | 520.2 | 347.3 | 328.2 | 332.9 | 377.3 | 293.2 | 275 | 398.9
579.1 | 471.1 | 520.2 | 347.4 | 328.7 | 333.5 | 377.1 | 293.6 | 275.2 | 399
580.1 | 472.1 | 520.1 | 346.6 | 329.1 | 334 | 376.8 | 294 | 275.4 | 399.2
581.1 | 473.1 | 520 | 347.1 | 329.6 | 334.5 | 377 | 294.4 | 275.7 | 399.3
582.1 | 474.1 | 520 | 347.8 | 330.1 | 335 | 376.5 | 294.7 | 275.9 | 399.4
583.1 | 475.1 | 520.1 | 346.9 | 330.6 | 335.5 | 376 | 295.1 | 276.2 | 399.5
584.1 | 476.1 | 520.1 | 346.9 | 331.1 | 336 | 375.6 | 295.5 | 276.4 | 399.7
585.1 | 477.1 | 520.2 | 348.5 | 331.6 | 336.5 | 375.8 | 295.9 | 276.7 | 399.7
586.1 | 478.1 | 520.2 | 348.5 | 332.1 | 337 | 377.5 | 296.2 | 276.9 | 399.8
587.1 | 479.1 | 520.1 | 349 | 332.5 | 337.5 | 379.6 | 296.6 | 277.2 | 400
588.1 | 480.1 | 520 | 349.3 | 333 | 338 | 381.3 | 296.9 | 277.4 | 400.1
589.1 | 481.1 | 519.9 | 348.3 | 333.4 | 338.5 | 382 | 297.3 | 277.7 | 400.1
590.1 | 482.1 | 519.8 | 347.8 | 333.9 | 339 | 383.3 | 297.6 | 277.9 | 400.2
591.1 | 483.1 | 519.7 | 347.8 | 334.3 | 339.5 | 384.2 | 298 | 278.2 | 400.3
592.1 | 484.1 | 519.6 | 348.4 | 334.8 | 340 | 384.7 | 298.3 | 278.4 | 400.4
593.1 | 485.1 | 519.6 | 349.1 | 335.2 | 340.5 | 384.6 | 298.7 | 278.7 | 400.5
594.1 | 486.1 | 519.8 | 349.1 | 335.6 | 341 | 384.9 | 299 | 278.9 | 400.6
595.1 | 487.1 | 519.7 | 350.5 | 336.1 | 341.5 | 384.8 | 299.4 | 279.1 | 400.8
596.1 | 488.1 | 519.8 | 352.4 | 336.6 | 342 | 384.2 | 299.7 | 279.4 | 400.9
597.1 | 489.1 | 519.8 | 353.4 | 337 | 342.5 | 384.4 | 300.1 | 279.6 | 401
598.1 | 490.1 | 519.8 | 353.4 | 337.4 | 342.9 | 385 | 300.4 | 279.8 | 401.2
599.1 | 491.1 | 520.2 | 353.4 | 337.9 | 343.4 | 384.4 | 300.8 | 280.1 | 401.3
600.1 | 492.1 | 520.6 | 353.3 | 338.3 | 343.9 | 384.8 | 301.1 | 280.3 | 401.4
601.1 | 493.1 | 520.8 | 354.3 | 338.7 | 344.3 | 386 | 301.5 | 280.5 | 401.5
602.1 | 494.1 | 520.9 | 355.3 | 339.2 | 344.8 | 387.2 | 301.8 | 280.8 | 401.6
603.1 | 495.1 | 520.9 | 355.4 | 339.7 | 345.3 | 388.2 | 302.2 | 281 | 401.7
604.1 | 496.1 | 520.8 | 354.9 | 340.1 | 345.7 | 389.1 | 302.5 | 281.2 | 401.8
605.1 | 497.1 | 520.8 | 355.6 | 340.5 | 346.2 | 390 | 302.9 | 281.4 | 401.9
606.1 | 498.1 | 520.7 | 355.8 | 340.9 | 346.7 | 389.9 | 303.2 | 281.6 | 402.1
607.1 | 499.1 | 520.5 | 355.2 | 341.4 | 347.1 | 390.1 | 303.6 | 281.9 | 402.2
608.1 | 500.1 | 520.3 | 355 | 341.8 | 347.6 | 390.8 | 303.9 | 282.1 | 402.3
609.1 | 501.1 | 520.1 | 355.3 | 342.2 | 348.1 | 390.5 | 304.3 | 282.3 | 402.4
610.1 | 502.1 | 520.1 | 356.4 | 342.6 | 348.6 | 391.1 | 304.6 | 282.5 | 402.4
611.1 | 503.1 | 520.2 | 356.3 | 343 | 349 | 391.2 | 305 | 282.8 | 402.6
612.1 | 504.1 | 520 | 356.1 | 343.4 | 349.5 | 391.8 | 305.3 | 283 | 402.7
613.1 | 505.1 | 519.9 | 357.9 | 343.9 | 350 | 391.6 | 305.7 | 283.3 | 402.8
614.1 | 506.1 | 519.9 | 359.8 | 344.3 | 350.4 | 392.6 | 306.1 | 283.5 | 402.9
615.1 | 507.1 | 519.8 | 359.3 | 344.6 | 350.9 | 393.6 | 306.4 | 283.7 | 402.9
616.1 | 508.1 | 519.7 | 358.4 | 345 | 351.4 | 394.2 | 306.8 | 284 | 403
617.1 | 509.1 | 519.8 | 358.3 | 345.4 | 351.8 | 394.6 | 307.1 | 284.2 | 403.1
618.1 | 510.1 | 519.8 | 358.6 | 345.8 | 352.2 | 394.8 | 307.4 | 284.5 | 403.2
619.1 | 511.1 | 519.9 | 358.5 | 346.2 | 352.7 | 395 | 307.8 | 284.8 | 403.3
620.1 | 512.1 | 519.7 | 358.2 | 346.6 | 353.1 | 395.6 | 308.1 | 285 | 403.4
621.1 | 513.1 | 519.6 | 357.8 | 347 | 353.5 | 396.4 | 308.4 | 285.3 | 403.5
622.1 | 514.1 | 519.4 | 357.9 | 347.4 | 353.9 | 396.1 | 308.8 | 285.6 | 403.5
623.1 | 515.1 | 519.3 | 357.3 | 347.8 | 354.3 | 396.4 | 309.1 | 285.8 | 403.6
624.1 | 516.1 | 519.3 | 356.7 | 348.1 | 354.8 | 396.8 | 309.4 | 286.1 | 403.8
625.1 | 517.1 | 519.3 | 357.1 | 348.5 | 355.2 | 397 | 309.7 | 286.3 | 403.9
626.1 | 518.1 | 519 | 356.5 | 348.8 | 355.6 | 397.6 | 310.1 | 286.6 | 403.9
627.1 | 519.1 | 518.9 | 356.5 | 349.2 | 356 | 398.4 | 310.4 | 286.8 | 404
628.1 | 520.1 | 519 | 357.6 | 349.6 | 356.4 | 398.3 | 310.7 | 287.1 | 404.1
629.1 | 521.1 | 519 | 358.2 | 350 | 356.8 | 398.7 | 311 | 287.4 | 404.2
630.1 | 522.1 | 519 | 358.2 | 350.4 | 357.2 | 399.4 | 311.4 | 287.6 | 404.3
631.1 | 523.1 | 519 | 358.1 | 350.7 | 357.6 | 400.1 | 311.7 | 287.9 | 404.4
632.1 | 524.1 | 519.1 | 358.8 | 351.1 | 358 | 399.9 | 312 | 288.2 | 404.5
633.1 | 525.1 | 519.2 | 359.1 | 351.4 | 358.4 | 400.1 | 312.3 | 288.5 | 404.6
634.1 | 526.1 | 519.2 | 359 | 351.7 | 358.8 | 400.5 | 312.6 | 288.7 | 404.7
635.1 | 527.1 | 518.9 | 359.4 | 352.1 | 359.2 | 400.6 | 312.9 | 289 | 404.8
636.1 | 528.1 | 518.9 | 359.3 | 352.4 | 359.5 | 401.3 | 313.2 | 289.3 | 404.8
637.1 | 529.1 | 519 | 358.6 | 352.8 | 359.9 | 402.2 | 313.5 | 289.6 | 404.9
638.1 | 530.1 | 519 | 358.5 | 353.2 | 360.3 | 403 | 313.8 | 289.8 | 404.9
639.1 | 531.1 | 519.1 | 358.5 | 353.5 | 360.6 | 403.7 | 314.1 | 290.1 | 405
640.1 | 532.1 | 519.2 | 359.5 | 354 | 360.9 | 404.1 | 314.4 | 290.4 | 405.1
641.1 | 533.1 | 519.1 | 359.9 | 354.3 | 361.3 | 405.1 | 314.7 | 290.6 | 405.2
642.1 | 534.1 | 519.1 | 360.3 | 354.7 | 361.6 | 406.3 | 314.9 | 290.9 | 405.3
643.1 | 535.1 | 519.1 | 360.1 | 355.1 | 362 | 407.3 | 315.2 | 291.1 | 405.4
644.1 | 536.1 | 519.1 | 360.3 | 355.5 | 362.3 | 408.3 | 315.5 | 291.4 | 405.4
645.1 | 537.1 | 519.2 | 360.4 | 355.9 | 362.7 | 409.5 | 315.8 | 291.7 | 405.5
646.1 | 538.1 | 519.2 | 360.7 | 356.3 | 363 | 410.6 | 316 | 291.9 | 405.6
647.1 | 539.1 | 519.4 | 360.6 | 356.7 | 363.4 | 411.2 | 316.3 | 292.2 | 405.6
648.1 | 540.1 | 519.5 | 361.7 | 357.2 | 363.7 | 411.8 | 316.6 | 292.5 | 405.7
649.1 | 541.1 | 519.6 | 362.6 | 357.6 | 364.1 | 412.4 | 316.9 | 292.7 | 405.8
650.1 | 542.1 | 519.8 | 362.3 | 358 | 364.4 | 413 | 317.2 | 293 | 405.9
651.1 | 543.1 | 519.9 | 362.5 | 358.5 | 364.7 | 413.7 | 317.5 | 293.3 | 406
652.1 | 544.1 | 519.9 | 362.6 | 358.9 | 365.1 | 414.4 | 317.8 | 293.5 | 406.1
653.1 | 545.1 | 520 | 363.1 | 359.4 | 365.5 | 415.1 | 318 | 293.8 | 406.2
654.1 | 546.1 | 520 | 363 | 359.8 | 365.8 | 416 | 318.3 | 294.1 | 406.2
655.1 | 547.1 | 520.1 | 363.3 | 360.3 | 366.2 | 416.6 | 318.6 | 294.3 | 406.3
656.1 | 548.1 | 520.3 | 363.2 | 360.7 | 366.6 | 417.3 | 318.9 | 294.6 | 406.3
657.1 | 549.1 | 520.4 | 363 | 361.2 | 366.9 | 417.9 | 319.2 | 294.9 | 406.4
658.1 | 550.1 | 520.3 | 362.9 | 361.7 | 367.3 | 419.1 | 319.4 | 295.2 | 406.5
659.1 | 551.1 | 520.2 | 362.9 | 362.2 | 367.7 | 420.5 | 319.7 | 295.5 | 406.6
660.1 | 552.1 | 520.2 | 362.8 | 362.6 | 368 | 421.6 | 320 | 295.8 | 406.7
661.1 | 553.1 | 520.3 | 362.5 | 363.1 | 368.4 | 422.6 | 320.3 | 296.1 | 406.8
662.1 | 554.1 | 520.5 | 362.6 | 363.7 | 368.7 | 423.2 | 320.6 | 296.3 | 406.9
663.1 | 555.1 | 520.7 | 363.4 | 364.1 | 369.1 | 424.1 | 320.9 | 296.6 | 407
664.1 | 556.1 | 520.8 | 364.5 | 364.7 | 369.5 | 426 | 321.2 | 296.9 | 407
665.1 | 557.1 | 520.7 | 365 | 365.2 | 369.8 | 427.9 | 321.4 | 297.2 | 407.1
666.1 | 558.1 | 520.5 | 365.2 | 365.8 | 370.1 | 429.1 | 321.7 | 297.5 | 407.2
667.1 | 559.1 | 520.5 | 365.2 | 366.3 | 370.5 | 430.2 | 322 | 297.7 | 407.3
668.1 | 560.1 | 520.5 | 365.7 | 366.9 | 370.9 | 431.4 | 322.3 | 298 | 407.4
669.1 | 561.1 | 520.6 | 365.8 | 367.5 | 371.2 | 432.5 | 322.6 | 298.3 | 407.5
670.1 | 562.1 | 520.7 | 367 | 368.1 | 371.6 | 432.9 | 322.8 | 298.5 | 407.6
671.1 | 563.1 | 520.7 | 367.6 | 368.6 | 372 | 433.9 | 323.1 | 298.8 | 407.7
672.1 | 564.1 | 520.7 | 367.7 | 369.1 | 372.3 | 434.6 | 323.4 | 299 | 407.8
673.1 | 565.1 | 520.7 | 367.7 | 369.7 | 372.7 | 435.8 | 323.7 | 299.3 | 407.8
674.1 | 566.1 | 520.6 | 367 | 370.3 | 373.1 | 437.1 | 324 | 299.5 | 407.9
675.1 | 567.1 | 520.6 | 368.3 | 370.8 | 373.4 | 438.7 | 324.3 | 299.7 | 408
676.1 | 568.1 | 520.4 | 368.5 | 371.4 | 373.8 | 440.3 | 324.5 | 300 | 408
677.1 | 569.1 | 520.1 | 368.4 | 372 | 374.2 | 441.4 | 324.8 | 300.2 | 408
678.1 | 570.1 | 519.9 | 368.3 | 372.5 | 374.6 | 442.1 | 325.1 | 300.5 | 408.1
679.1 | 571.1 | 519.9 | 368.6 | 373.2 | 375 | 442.6 | 325.3 | 300.7 | 408.2
680.1 | 572.1 | 520.1 | 369.6 | 373.8 | 375.5 | 443 | 325.6 | 301 | 408.2
681.1 | 573.1 | 520.4 | 370.3 | 374.4 | 375.9 | 443.1 | 325.9 | 301.3 | 408.2
682.1 | 574.1 | 520.5 | 370.8 | 375 | 376.4 | 443.2 | 326.2 | 301.6 | 408.3
683.1 | 575.1 | 520.5 | 371.3 | 375.7 | 376.8 | 443.7 | 326.4 | 301.8 | 408.3
684.1 | 576.1 | 520.6 | 370.8 | 376.3 | 377.2 | 444.8 | 326.7 | 302.1 | 408.3
685.1 | 577.1 | 520.8 | 371.5 | 377 | 377.6 | 445.2 | 326.9 | 302.4 | 408.4
686.1 | 578.1 | 520.8 | 373 | 377.8 | 378 | 445.8 | 327.2 | 302.7 | 408.4
687.1 | 579.1 | 520.7 | 374 | 378.5 | 378.4 | 446 | 327.5 | 302.9 | 408.4
688.1 | 580.1 | 520.7 | 373.4 | 379.2 | 378.9 | 446.5 | 327.8 | 303.2 | 408.4
689.1 | 581.1 | 520.7 | 374.9 | 379.9 | 379.3 | 447.5 | 328 | 303.5 | 408.4
690.1 | 582.1 | 520.6 | 376.3 | 380.6 | 379.7 | 448 | 328.3 | 303.8 | 408.4
691.1 | 583.1 | 520.6 | 377.2 | 381.4 | 380 | 448.5 | 328.5 | 304.1 | 408.5
692.1 | 584.1 | 520.6 | 378.1 | 382.2 | 380.4 | 448.6 | 328.8 | 304.4 | 408.5
693.1 | 585.1 | 520.6 | 378.2 | 383 | 380.8 | 448.6 | 329.1 | 304.7 | 408.5
694.1 | 586.1 | 520.5 | 377.9 | 383.8 | 381.2 | 448.2 | 329.4 | 305 | 408.6
695.1 | 587.1 | 520.3 | 378.2 | 384.5 | 381.7 | 448.1 | 329.6 | 305.3 | 408.6
696.1 | 588.1 | 520.4 | 379.8 | 385.3 | 382.1 | 448.4 | 329.9 | 305.5 | 408.7
697.1 | 589.1 | 520.5 | 381.2 | 386.1 | 382.6 | 448.6 | 330.1 | 305.8 | 408.8
698.1 | 590.1 | 520.4 | 383.2 | 386.9 | 383 | 448.9 | 330.4 | 306.1 | 408.8
699.1 | 591.1 | 520.4 | 385.8 | 387.7 | 383.5 | 449.2 | 330.6 | 306.4 | 408.9
700.1 | 592.1 | 520.5 | 387.6 | 388.5 | 383.9 | 449.7 | 330.8 | 306.6 | 408.9
701.1 | 593.1 | 520.5 | 388.6 | 389.2 | 384.4 | 449.9 | 331.1 | 306.9 | 409
702.1 | 594.1 | 520.3 | 390 | 389.9 | 384.9 | 449.9 | 331.4 | 307.1 | 409
703.1 | 595.1 | 520.4 | 390.4 | 390.6 | 385.3 | 449.6 | 331.6 | 307.4 | 409.1
704.1 | 596.1 | 520.5 | 391.3 | 391.3 | 385.8 | 449.5 | 331.9 | 307.6 | 409.1
705.1 | 597.1 | 520.8 | 392.5 | 391.9 | 386.3 | 450 | 332.1 | 307.9 | 409.2
706.1 | 598.1 | 520.8 | 393.5 | 392.6 | 386.8 | 450.4 | 332.4 | 308.1 | 409.2
707.1 | 599.1 | 520.9 | 393.9 | 393.2 | 387.3 | 450.1 | 332.6 | 308.4 | 409.3
708.1 | 600.1 | 521 | 393 | 393.6 | 387.9 | 450.2 | 332.9 | 308.6 | 409.3
709.1 | 601.1 | 520.9 | 393.3 | 393.9 | 388.4 | 450.9 | 333.2 | 308.9 | 409.4
710.1 | 602.1 | 520.8 | 394 | 394.1 | 389 | 451.5 | 333.4 | 309.1 | 409.4
711.1 | 603.1 | 520.7 | 394.7 | 394.4 | 389.6 | 451.7 | 333.7 | 309.4 | 409.5
712.1 | 604.1 | 520.6 | 395.4 | 394.8 | 390.1 | 451.8 | 334 | 309.6 | 409.5
713.1 | 605.1 | 520.4 | 396.9 | 395.3 | 390.7 | 452.5 | 334.3 | 309.9 | 409.6
714.1 | 606.1 | 520.3 | 396.5 | 395.9 | 391.3 | 453.3 | 334.6 | 310.1 | 409.6
715.1 | 607.1 | 520.2 | 395.2 | 396.5 | 391.9 | 453.9 | 334.9 | 310.4 | 409.7
716.1 | 608.1 | 520.1 | 394.2 | 397 | 392.5 | 454.3 | 335.1 | 310.6 | 409.7
717.1 | 609.1 | 520.1 | 393.7 | 397.4 | 393.2 | 454.9 | 335.4 | 310.8 | 409.8
718.1 | 610.1 | 520.2 | 393.6 | 397.8 | 393.8 | 455.7 | 335.7 | 311.1 | 409.8
719.1 | 611.1 | 520.1 | 394 | 398.4 | 394.4 | 456.9 | 335.9 | 311.3 | 409.9
720.1 | 612.1 | 520.1 | 388.3 | 399 | 395.1 | 457.7 | 336.2 | 311.5 | 409.9
721.1 | 613.1 | 520 | 377.3 | 399.6 | 395.7 | 458.5 | 336.5 | 311.8 | 409.9
722.1 | 614.1 | 520 | 371.1 | 400.3 | 396.4 | 458.6 | 336.7 | 312.1 | 410
723.1 | 615.1 | 520 | 364.6 | 401.1 | 397.1 | 458.9 | 337 | 312.3 | 410
724.1 | 616.1 | 520.1 | 355.1 | 401.8 | 397.8 | 459.7 | 337.3 | 312.5 | 410.1
725.1 | 617.1 | 519.9 | 341.8 | 402.6 | 398.5 | 460.8 | 337.6 | 312.8 | 410.2
726.1 | 618.1 | 519.7 | 332.1 | 403.5 | 399.1 | 461.4 | 337.8 | 313 | 410.2
727.1 | 619.1 | 519.7 | 320.7 | 404.4 | 399.8 | 461.8 | 338.1 | 313.3 | 410.3
728.1 | 620.1 | 519.7 | 310.4 | 405.3 | 400.4 | 462.1 | 338.4 | 313.5 | 410.3
729.1 | 621.1 | 519.7 | 302.7 | 406.3 | 401.1 | 462.3 | 338.6 | 313.7 | 410.4
730.1 | 622.1 | 519.7 | 296.8 | 407.5 | 401.8 | 462.7 | 338.9 | 313.9 | 410.5
731.1 | 623.1 | 519.5 | 290.5 | 408.7 | 402.4 | 463.2 | 339.1 | 314.2 | 410.5
732.1 | 624.1 | 519.5 | 283.6 | 409.9 | 403.1 | 463.1 | 339.3 | 314.4 | 410.5
733.1 | 625.1 | 519.7 | 276.3 | 411.1 | 403.8 | 463.8 | 339.6 | 314.7 | 410.6
734.1 | 626.1 | 519.6 | 269.6 | 412.4 | 404.4 | 464.1 | 339.8 | 314.9 | 410.6
735.1 | 627.1 | 519.4 | 265.3 | 413.6 | 405.1 | 464.5 | 340 | 315.2 | 410.7
736.1 | 628.1 | 519.7 | 262.2 | 414.9 | 405.7 | 464.7 | 340.3 | 315.4 | 410.7
737.1 | 629.1 | 519.9 | 258.2 | 416.1 | 406.4 | 465.5 | 340.5 | 315.6 | 410.8
738.1 | 630.1 | 520.1 | 256.5 | 417.3 | 407.1 | 466.8 | 340.7 | 315.9 | 410.8
739.1 | 631.1 | 520.2 | 254.8 | 418.7 | 407.8 | 467.3 | 341 | 316.1 | 410.9
740.1 | 632.1 | 520.5 | 252.6 | 420 | 408.5 | 468.8 | 341.2 | 316.3 | 410.9
741.1 | 633.1 | 520.8 | 249.1 | 421.5 | 409.1 | 470.1 | 341.5 | 316.5 | 411
742.1 | 634.1 | 520.7 | 246.1 | 423.1 | 409.8 | 470 | 341.7 | 316.7 | 411.1
743.1 | 635.1 | 520.7 | 246 | 424.8 | 410.6 | 470.3 | 341.9 | 317 | 411.1
744.1 | 636.1 | 520.7 | 246.4 | 426.5 | 411.3 | 470.7 | 342.2 | 317.2 | 411.2
745.1 | 637.1 | 520.7 | 248.2 | 428.3 | 412.1 | 471.6 | 342.4 | 317.4 | 411.3
746.1 | 638.1 | 520.6 | 249.4 | 430.1 | 412.8 | 472.7 | 342.6 | 317.6 | 411.3
747.1 | 639.1 | 520.6 | 247.3 | 432.1 | 413.6 | 473.3 | 342.9 | 317.8 | 411.4
748.1 | 640.1 | 520.6 | 245.2 | 434.2 | 414.4 | 472.8 | 343.1 | 318 | 411.5
749.1 | 641.1 | 520.6 | 243.6 | 436.5 | 415.3 | 473.1 | 343.3 | 318.2 | 411.7
750.1 | 642.1 | 520.7 | 242.6 | 439.1 | 416.1 | 473.5 | 343.6 | 318.3 | 411.8
751.1 | 643.1 | 520.8 | 241.4 | 442.2 | 416.9 | 473.9 | 343.8 | 318.5 | 411.9
752.1 | 644.1 | 520.9 | 241.1 | 446.2 | 417.8 | 474.1 | 344.1 | 318.7 | 411.9
753.1 | 645.1 | 521 | 239.8 | 451.4 | 418.7 | 474.6 | 344.3 | 318.9 | 412
754.1 | 646.1 | 521 | 239.5 | 456.9 | 419.7 | 475.1 | 344.5 | 319.1 | 412.1
755.1 | 647.1 | 521 | 239.1 | 461.9 | 420.7 | 475.2 | 344.7 | 319.4 | 412.1
756.1 | 648.1 | 521 | 240.3 | 467.5 | 421.8 | 474.7 | 344.9 | 319.6 | 412.2
757.1 | 649.1 | 521 | 239.8 | 472.1 | 422.9 | 474.8 | 345.1 | 319.8 | 412.2
758.1 | 650.1 | 520.9 | 239.2 | 475.5 | 424.1 | 474.9 | 345.2 | 320.1 | 412.2
759.1 | 651.1 | 520.6 | 238 | 478.2 | 425.3 | 475.4 | 345.4 | 320.3 | 412.2
760.1 | 652.1 | 520.5 | 239.6 | 481.1 | 426.8 | 475.9 | 345.6 | 320.6 | 412.3
761.1 | 653.1 | 520.3 | 240.5 | 483.7 | 430 | 476 | 345.8 | 320.8 | 412.4
762.1 | 654.1 | 520.3 | 241.6 | 485.8 | 433.7 | 477 | 346 | 321.1 | 412.4
763.1 | 655.1 | 520.1 | 242.9 | 487.5 | 436.8 | 478.1 | 346.2 | 321.3 | 412.5
764.1 | 656.1 | 520 | 241.4 | 488.8 | 439 | 479.6 | 346.3 | 321.5 | 412.5
765.1 | 657.1 | 520 | 240.3 | 489.5 | 439.9 | 479.6 | 346.5 | 321.8 | 412.6
766.1 | 658.1 | 520.1 | 239.8 | 490 | 441 | 481.1 | 346.7 | 322 | 412.6
767.1 | 659.1 | 520.3 | 239.9 | 490.7 | 442.4 | 483.5 | 346.9 | 322.2 | 412.6
768.1 | 660.1 | 520.4 | 239.8 | 491.1 | 444.3 | 484.8 | 347.1 | 322.4 | 412.6
769.1 | 661.1 | 520.5 | 241.2 | 492.7 | 445.8 | 486.8 | 347.3 | 322.6 | 412.7
770.1 | 662.1 | 520.5 | 241.8 | 495.7 | 447.5 | 490.4 | 347.5 | 322.9 | 412.7
771.1 | 663.1 | 520.6 | 241.7 | 498.2 | 449.1 | 493.9 | 347.7 | 323.1 | 412.7
772.1 | 664.1 | 520.7 | 240.7 | 501.1 | 452.2 | 497.2 | 347.9 | 323.3 | 412.8
773.1 | 665.1 | 520.8 | 239.6 | 505.2 | 455.5 | 500 | 348.1 | 323.5 | 412.9
774.1 | 666.1 | 520.8 | 238.9 | 509.2 | 458 | 502.4 | 348.3 | 323.7 | 412.9
775.1 | 667.1 | 520.7 | 238.8 | 513.9 | 459.1 | 505.8 | 348.5 | 323.9 | 413
776.1 | 668.1 | 520.7 | 238.2 | 518.1 | 460.1 | 509.3 | 348.7 | 324.1 | 413
777.1 | 669.1 | 520.9 | 237.5 | 525.3 | 462.3 | 512.7 | 348.9 | 324.3 | 413.1
778.1 | 670.1 | 520.9 | 237.8 | 533.2 | 464.1 | 515.2 | 349.1 | 324.5 | 413.1
779.1 | 671.1 | 520.8 | 237.7 | 540.3 | 466.8 | 517.8 | 349.3 | 324.7 | 413.2
780.1 | 672.1 | 520.7 | 236.2 | 549 | 469.3 | 520.9 | 349.5 | 324.9 | 413.3
781.1 | 673.1 | 520.7 | 235.4 | 555.6 | 470.9 | 524.7 | 349.7 | 325.1 | 413.3
782.1 | 674.1 | 520.7 | 234.5 | 563.4 | 472.3 | 528 | 349.9 | 325.3 | 413.4
783.1 | 675.1 | 520.6 | 234.6 | 573.7 | 473.7 | 531.6 | 350.1 | 325.5 | 413.5
784.1 | 676.1 | 520.6 | 233.8 | 583.1 | 474.5 | 535.2 | 350.3 | 325.7 | 413.5
785.1 | 677.1 | 520.6 | 234.5 | 590.2 | 475.1 | 539 | 350.4 | 325.9 | 413.5
786.1 | 678.1 | 520.6 | 239.2 | 597.9 | 475.1 | 542.6 | 350.6 | 326.1 | 413.6
787.1 | 679.1 | 520.6 | 241.5 | 603.6 | 475.2 | 545.1 | 350.8 | 326.3 | 413.7
788.1 | 680.1 | 520.5 | 240.3 | 613.8 | 475.5 | 546.9 | 351 | 326.5 | 413.7
789.1 | 681.1 | 520.5 | 239.7 | 617.9 | 475.6 | 548.8 | 351.1 | 326.6 | 413.8
790.1 | 682.1 | 520.8 | 237.6 | 621.9 | 476.4 | 551.3 | 351.3 | 326.8 | 413.9
791.1 | 683.1 | 520.8 | 236.7 | 622.5 | 476.6 | 553.5 | 351.5 | 327 | 414
792.1 | 684.1 | 520.7 | 237.2 | 630.2 | 476.7 | 556.6 | 351.7 | 327.2 | 414
793.1 | 685.1 | 520.8 | 237.5 | 635.6 | 477.6 | 560.1 | 351.8 | 327.3 | 414.1
794.1 | 686.1 | 520.9 | 236.1 | 637 | 478.5 | 563.2 | 352 | 327.5 | 414.2
795.1 | 687.1 | 521 | 235.7 | 637.1 | 479.6 | 565.7 | 352.2 | 327.7 | 414.3
796.1 | 688.1 | 521 | 235 | 634.7 | 479.8 | 568.1 | 352.3 | 327.9 | 414.4
797.1 | 689.1 | 521.1 | 235 | 635.7 | 480.6 | 571.7 | 352.5 | 328.1 | 414.4
798.1 | 690.1 | 521.1 | 234.9 | 634.6 | 481.2 | 575.3 | 352.6 | 328.3 | 414.4
799.1 | 691.1 | 521 | 234.3 | 634.8 | 481.9 | 579.4 | 352.8 | 328.5 | 414.5
800.1 | 692.1 | 520.8 | 233.3 | 635.2 | 482.5 | 583.5 | 352.9 | 328.7 | 414.6
801.1 | 693.1 | 520.9 | 235.2 | 639.8 | 483 | 587.6 | 353 | 328.9 | 414.7
802.1 | 694.1 | 520.8 | 237.9 | 643 | 483.6 | 591.9 | 353.2 | 329.1 | 414.8
803.1 | 695.1 | 520.8 | 239.8 | 642.9 | 484.4 | 596 | 353.4 | 329.2 | 414.9
804.1 | 696.1 | 520.8 | 238.4 | 640.9 | 484.8 | 599.6 | 353.5 | 329.4 | 415
805.1 | 697.1 | 520.7 | 236.1 | 630.6 | 485 | 603.3 | 353.7 | 329.6 | 415.1
806.1 | 698.1 | 520.8 | 235.3 | 622.2 | 485.2 | 607.8 | 353.8 | 329.8 | 415.3
807.1 | 699.1 | 520.8 | 234.6 | 617.5 | 484.7 | 611.3 | 354 | 329.9 | 415.3
808.1 | 700.1 | 520.7 | 233.6 | 621 | 484.4 | 615.4 | 354.1 | 330.1 | 415.4
809.1 | 701.1 | 520.8 | 232.6 | 622.4 | 484.6 | 619.3 | 354.3 | 330.3 | 415.5
810.1 | 702.1 | 520.7 | 232.6 | 619 | 484.5 | 622.4 | 354.4 | 330.4 | 415.5
811.1 | 703.1 | 520.6 | 234.5 | 618.9 | 484.3 | 623.8 | 354.5 | 330.6 | 415.5
812.1 | 704.1 | 520.4 | 234.9 | 621.8 | 484.3 | 625.2 | 354.6 | 330.8 | 415.6
813.1 | 705.1 | 520 | 234 | 625.5 | 485.1 | 626.5 | 354.7 | 331 | 415.7
814.1 | 706.1 | 519.9 | 233.4 | 631.1 | 485.8 | 629.3 | 354.8 | 331.2 | 415.7
815.1 | 707.1 | 519.8 | 233.1 | 635.1 | 485.8 | 631.6 | 354.9 | 331.4 | 415.7
816.1 | 708.1 | 519.6 | 233 | 636 | 485.9 | 632 | 355 | 331.6 | 415.7
817.1 | 709.1 | 519.5 | 233.3 | 641.1 | 486.5 | 632.6 | 355.1 | 331.8 | 415.8
818.1 | 710.1 | 519.5 | 234.4 | 639.9 | 487.1 | 632.4 | 355.2 | 331.9 | 415.8
819.1 | 711.1 | 519.4 | 233.9 | 637.6 | 487.2 | 631.6 | 355.3 | 332.1 | 415.8
820.1 | 712.1 | 519.4 | 232.9 | 632.8 | 487.8 | 630.3 | 355.4 | 332.3 | 415.9
821.1 | 713.1 | 519.4 | 232 | 626.7 | 488.2 | 629.5 | 355.5 | 332.4 | 415.9
822.1 | 714.1 | 519.1 | 232.8 | 623.8 | 488.6 | 628.6 | 355.5 | 332.5 | 415.9
823.1 | 715.1 | 519 | 233.4 | 615.8 | 488.9 | 627 | 355.6 | 332.7 | 415.9
824.1 | 716.1 | 519.1 | 234 | 609.3 | 489.3 | 624.9 | 355.7 | 332.8 | 415.9
825.1 | 717.1 | 519 | 233.1 | 602.5 | 489.6 | 621.5 | 355.8 | 333 | 416
826.1 | 718.1 | 518.8 | 232.7 | 599.4 | 490.1 | 616.9 | 355.9 | 333.2 | 416
827.1 | 719.1 | 518.9 | 232.5 | 597.5 | 490.1 | 613.1 | 356 | 333.3 | 416
828.1 | 720.1 | 518.8 | 232.9 | 598.8 | 489.9 | 608.2 | 356.1 | 333.4 | 416
829.1 | 721.1 | 518.6 | 232.4 | 597.2 | 490.9 | 604.9 | 356.2 | 333.6 | 416
830.1 | 722.1 | 518.8 | 234 | 598 | 491.8 | 602 | 356.3 | 333.7 | 416.1
831.1 | 723.1 | 519.1 | 235.2 | 599.3 | 492 | 597.9 | 356.3 | 333.9 | 416.1
832.1 | 724.1 | 519.2 | 234.4 | 597.1 | 492.6 | 593.4 | 356.4 | 334 | 416.1
833.1 | 725.1 | 519.4 | 234.2 | 597.2 | 492.9 | 589.9 | 356.5 | 334.1 | 416.2
834.1 | 726.1 | 519.3 | 233.3 | 595.7 | 493 | 585.5 | 356.6 | 334.3 | 416.2
835.1 | 727.1 | 519.3 | 234.3 | 593.2 | 493 | 582.3 | 356.7 | 334.4 | 416.2
836.1 | 728.1 | 519.5 | 234.8 | 588.5 | 493.5 | 579.1 | 356.7 | 334.6 | 416.3
837.1 | 729.1 | 519.5 | 233.9 | 583.7 | 494.7 | 576.2 | 356.8 | 334.7 | 416.3
838.1 | 730.1 | 519.4 | 232.7 | 580.2 | 495.1 | 573.2 | 356.9 | 334.8 | 416.4
839.1 | 731.1 | 519.6 | 231.8 | 578.6 | 495.2 | 569.8 | 357 | 334.9 | 416.5
840.1 | 732.1 | 519.7 | 231.3 | 576.6 | 494.8 | 566.7 | 357.1 | 335 | 416.5
841.1 | 733.1 | 520 | 230.5 | 574.8 | 494.6 | 563.7 | 357.2 | 335.2 | 416.6
842.1 | 734.1 | 520 | 230.9 | 575.3 | 494.5 | 561.5 | 357.3 | 335.3 | 416.6
843.1 | 735.1 | 520.1 | 231 | 575.8 | 494.6 | 559 | 357.4 | 335.5 | 416.6
844.1 | 736.1 | 520.4 | 231.3 | 574.8 | 495.1 | 556.8 | 357.5 | 335.6 | 416.7
845.1 | 737.1 | 520.6 | 231.6 | 572.9 | 495.5 | 554.4 | 357.6 | 335.8 | 416.8
846.1 | 738.1 | 520.7 | 231.5 | 570.4 | 496.5 | 551.9 | 357.7 | 336 | 416.9
847.1 | 739.1 | 520.9 | 232.8 | 568.3 | 496.7 | 549.4 | 357.8 | 336.2 | 416.9
848.1 | 740.1 | 521.1 | 232.4 | 565.8 | 496.8 | 548.1 | 357.9 | 336.4 | 417
849.1 | 741.1 | 521.2 | 233 | 565.2 | 497.6 | 548.1 | 358 | 336.6 | 417.1
850.1 | 742.1 | 521.1 | 232.7 | 567.2 | 497.1 | 546.5 | 358.1 | 336.7 | 417.2
851.1 | 743.1 | 520.9 | 231.9 | 571.2 | 495.9 | 543.4 | 358.2 | 336.8 | 417.2
852.1 | 744.1 | 520.7 | 232.8 | 575.3 | 493.9 | 539 | 358.3 | 337 | 417.4
853.1 | 745.1 | 520.6 | 234.7 | 576.4 | 493 | 536.7 | 358.4 | 337.1 | 417.5
854.1 | 746.1 | 520.4 | 234.9 | 576.1 | 493.8 | 535.5 | 358.5 | 337.3 | 417.6
855.1 | 747.1 | 520.4 | 235.1 | 575.2 | 494.4 | 535.6 | 358.6 | 337.4 | 417.8
856.1 | 748.1 | 520.4 | 233.9 | 575.2 | 495.3 | 536.9 | 358.6 | 337.5 | 417.9
857.1 | 749.1 | 520.3 | 233.2 | 575.6 | 496.9 | 539.1 | 358.7 | 337.6 | 418
858.1 | 750.1 | 520.1 | 232.8 | 574.6 | 497.2 | 539.3 | 358.8 | 337.7 | 418.2
859.1 | 751.1 | 519.8 | 232.6 | 572.7 | 496.8 | 538.1 | 358.9 | 337.9 | 418.3
860.1 | 752.1 | 519.4 | 231.9 | 570.5 | 497.1 | 538.9 | 359.1 | 338 | 418.3
861.1 | 753.1 | 519.4 | 231.2 | 569.1 | 497.7 | 538.6 | 359.1 | 338.1 | 418.4
862.1 | 754.1 | 519.4 | 230.9 | 568.1 | 498.3 | 537.3 | 359.2 | 338.3 | 418.4
863.1 | 755.1 | 519.4 | 231.2 | 566.7 | 497.7 | 537.2 | 359.3 | 338.4 | 418.5
864.1 | 756.1 | 519.4 | 231.9 | 566.3 | 498.1 | 537.5 | 359.4 | 338.5 | 418.6
865.1 | 757.1 | 519.4 | 231.9 | 566.6 | 498.3 | 536.5 | 359.5 | 338.6 | 418.7
866.1 | 758.1 | 519.3 | 232.1 | 566.7 | 498.4 | 535.4 | 359.5 | 338.7 | 418.7
867.1 | 759.1 | 519.2 | 234.1 | 567.9 | 498.9 | 534.5 | 359.6 | 338.9 | 418.8
868.1 | 760.1 | 519.3 | 233.9 | 570 | 499.4 | 535.2 | 359.7 | 339 | 418.9
869.1 | 761.1 | 519.4 | 233.4 | 569.7 | 499.9 | 535.2 | 359.8 | 339.1 | 418.9
870.1 | 762.1 | 519.5 | 233.3 | 570.5 | 500 | 536 | 359.8 | 339.2 | 418.9
871.1 | 763.1 | 519.8 | 232.5 | 571.2 | 500 | 536.5 | 359.9 | 339.4 | 418.9
872.1 | 764.1 | 519.9 | 231.6 | 569.8 | 500.2 | 534.6 | 360 | 339.5 | 419
873.1 | 765.1 | 519.8 | 230.8 | 568.1 | 500.7 | 532.8 | 360 | 339.7 | 419
874.1 | 766.1 | 519.9 | 230.1 | 568.1 | 500.4 | 531.1 | 360.1 | 339.9 | 419.1
875.1 | 767.1 | 520 | 230 | 568.9 | 499.5 | 530.3 | 360.1 | 340 | 419.1
876.1 | 768.1 | 520.1 | 229.5 | 569.6 | 500 | 529.7 | 360.2 | 340.2 | 419.1
877.1 | 769.1 | 520.3 | 228.6 | 569 | 500.8 | 530.8 | 360.3 | 340.3 | 419.1
878.1 | 770.1 | 520.3 | 228.8 | 569.5 | 501.4 | 530 | 360.4 | 340.5 | 419
879.1 | 771.1 | 520.3 | 229.7 | 570.1 | 502.1 | 528.4 | 360.4 | 340.6 | 419
880.1 | 772.1 | 520.3 | 230.2 | 568.9 | 503 | 528.8 | 360.5 | 340.8 | 419
881.1 | 773.1 | 520.2 | 231.1 | 569.5 | 503.6 | 529.4 | 360.6 | 340.9 | 419.1
882.1 | 774.1 | 520.2 | 231.3 | 570.5 | 503.4 | 529.2 | 360.7 | 341.1 | 419.1
883.1 | 775.1 | 520.2 | 232.4 | 571.1 | 503 | 528.9 | 360.8 | 341.2 | 419.1
884.1 | 776.1 | 520.1 | 232.1 | 571.1 | 503.7 | 530.5 | 360.9 | 341.4 | 419.1
885.1 | 777.1 | 520.1 | 231.7 | 571.1 | 504.1 | 530.7 | 361 | 341.5 | 419.2
886.1 | 778.1 | 520 | 231.8 | 570.8 | 504.3 | 531.2 | 361 | 341.6 | 419.2
887.1 | 779.1 | 520 | 231.2 | 570 | 504.5 | 532 | 361.1 | 341.8 | 419.2
888.1 | 780.1 | 519.8 | 232.1 | 570.2 | 504.8 | 530.8 | 361.2 | 342 | 419.3
889.1 | 781.1 | 519.5 | 233.6 | 569.6 | 505.2 | 529.6 | 361.3 | 342.2 | 419.2
890.1 | 782.1 | 519.4 | 235.7 | 569.2 | 505.8 | 528.3 | 361.3 | 342.4 | 419.2
891.1 | 783.1 | 519.3 | 236.9 | 568.5 | 506.3 | 527.9 | 361.4 | 342.6 | 419.2
892.1 | 784.1 | 519.3 | 237 | 567.7 | 506.4 | 528.7 | 361.5 | 342.8 | 419.2
893.1 | 785.1 | 519.5 | 236.2 | 567 | 506.2 | 529.7 | 361.6 | 343 | 419.2
894.1 | 786.1 | 519.3 | 235.7 | 566.8 | 507 | 531.5 | 361.7 | 343.2 | 419.2
895.1 | 787.1 | 519.3 | 236.3 | 566.4 | 507.6 | 532.2 | 361.8 | 343.4 | 419.3
896.1 | 788.1 | 519.4 | 236.4 | 566.9 | 507.8 | 531 | 361.9 | 343.5 | 419.3
897.1 | 789.1 | 519.4 | 235.7 | 567.5 | 508.6 | 532.4 | 362 | 343.7 | 419.4
898.1 | 790.1 | 519.7 | 235.1 | 568 | 508.8 | 534.7 | 362.2 | 343.9 | 419.4
899.1 | 791.1 | 520 | 234.6 | 567.6 | 510.3 | 537.6 | 362.3 | 344.1 | 419.5
900.1 | 792.1 | 520.2 | 234.3 | 567.8 | 510.6 | 539.4 | 362.4 | 344.2 | 419.5
901.1 | 793.1 | 520.3 | 234.2 | 568 | 510.7 | 539.8 | 362.5 | 344.4 | 419.5
902.1 | 794.1 | 520.2 | 234.1 | 568 | 511.6 | 540.7 | 362.6 | 344.6 | 419.6
903.1 | 795.1 | 520.4 | 233.6 | 568.4 | 512.9 | 542.2 | 362.7 | 344.8 | 419.6
904.1 | 796.1 | 520.4 | 233.4 | 569.7 | 514 | 543.8 | 362.8 | 345 | 419.6
905.1 | 797.1 | 520.2 | 232.9 | 570.5 | 514.8 | 543.2 | 362.9 | 345.2 | 419.7
906.1 | 798.1 | 520.1 | 232.6 | 571.3 | 514.9 | 541.7 | 363 | 345.4 | 419.7
907.1 | 799.1 | 520.1 | 232.8 | 572.5 | 515 | 540.8 | 363.1 | 345.6 | 419.7
908.1 | 800.1 | 520 | 233 | 572.6 | 515 | 542.9 | 363.2 | 345.8 | 419.8
909.1 | 801.1 | 520.2 | 232.4 | 573.1 | 516.1 | 544.8 | 363.2 | 346 | 419.9
910.1 | 802.1 | 520.3 | 232.5 | 572.8 | 517.7 | 545.6 | 363.3 | 346.3 | 420
911.1 | 803.1 | 520.4 | 233.1 | 572.1 | 519.2 | 546 | 363.3 | 346.4 | 420.1
912.1 | 804.1 | 520.3 | 233.8 | 572.9 | 520.4 | 545 | 363.4 | 346.6 | 420.2
913.1 | 805.1 | 520.3 | 234.5 | 573.2 | 520.9 | 546.1 | 363.4 | 346.8 | 420.3
914.1 | 806.1 | 520.3 | 234.8 | 572.9 | 521.4 | 547 | 363.5 | 347 | 420.4
915.1 | 807.1 | 520.3 | 235.5 | 573.5 | 521.1 | 546.8 | 363.5 | 347.1 | 420.4
916.1 | 808.1 | 520.3 | 235.1 | 574.1 | 521 | 546.1 | 363.6 | 347.3 | 420.5
917.1 | 809.1 | 520.3 | 235.3 | 574 | 522.1 | 546.1 | 363.7 | 347.4 | 420.6
918.1 | 810.1 | 520.3 | 235.5 | 574.1 | 523.2 | 546.3 | 363.7 | 347.6 | 420.7
919.1 | 811.1 | 520.3 | 236.7 | 573.9 | 525 | 546.4 | 363.8 | 347.7 | 420.7
920.1 | 812.1 | 520.2 | 236 | 574.6 | 527.3 | 548.1 | 363.9 | 347.9 | 420.7
921.1 | 813.1 | 520.1 | 235.2 | 575 | 530.3 | 548.3 | 363.9 | 348 | 420.7
922.1 | 814.1 | 520.2 | 234.8 | 574.9 | 532.4 | 549.5 | 363.9 | 348.2 | 420.8
923.1 | 815.1 | 520.2 | 235.4 | 574.7 | 532.6 | 550.2 | 364 | 348.3 | 420.9
924.1 | 816.1 | 520.2 | 235.3 | 573.8 | 533.5 | 549.2 | 364 | 348.4 | 420.9
925.1 | 817.1 | 520.1 | 236.7 | 574.8 | 534.5 | 549.1 | 364.1 | 348.5 | 421
926.1 | 818.1 | 520 | 236.8 | 575.2 | 535.8 | 549.4 | 364.1 | 348.6 | 421
927.1 | 819.1 | 519.9 | 237.4 | 574.7 | 538 | 549 | 364.2 | 348.8 | 421.1
928.1 | 820.1 | 519.7 | 237.1 | 574.9 | 539.6 | 549.2 | 364.3 | 348.9 | 421.1
929.1 | 821.1 | 519.8 | 238.9 | 575.4 | 540.8 | 549.7 | 364.3 | 349 | 421.2
930.1 | 822.1 | 519.7 | 241.1 | 576 | 542.8 | 549.1 | 364.4 | 349.2 | 421.3
931.1 | 823.1 | 519.7 | 240.5 | 576.8 | 544.1 | 549.1 | 364.4 | 349.3 | 421.4
932.1 | 824.1 | 519.7 | 241 | 577.7 | 545.4 | 549.8 | 364.5 | 349.4 | 421.5
933.1 | 825.1 | 519.9 | 240.1 | 579.9 | 546.4 | 549.2 | 364.5 | 349.6 | 421.6
934.1 | 826.1 | 519.8 | 239.6 | 580.1 | 546.7 | 550.7 | 364.6 | 349.7 | 421.6
935.1 | 827.1 | 519.7 | 238.9 | 579.8 | 547.1 | 551.1 | 364.7 | 349.9 | 421.7
936.1 | 828.1 | 519.7 | 238.2 | 579 | 548 | 551.4 | 364.7 | 350 | 421.7
937.1 | 829.1 | 519.6 | 237.6 | 578.1 | 548.7 | 551.6 | 364.8 | 350.2 | 421.8
938.1 | 830.1 | 519.7 | 237.3 | 578 | 548.8 | 552.3 | 364.8 | 350.3 | 421.9
939.1 | 831.1 | 519.9 | 236.9 | 579.1 | 550.1 | 554.2 | 364.9 | 350.4 | 422.1
940.1 | 832.1 | 520.1 | 235.9 | 579.3 | 552.1 | 553.8 | 364.9 | 350.6 | 422.1
941.1 | 833.1 | 520.3 | 235.5 | 578.7 | 553.2 | 552.8 | 364.9 | 350.7 | 422.2
942.1 | 834.1 | 520.2 | 236 | 577.3 | 553.7 | 552.6 | 364.9 | 350.9 | 422.3
943.1 | 835.1 | 520 | 237.5 | 579.6 | 554.8 | 552.7 | 364.9 | 351 | 422.4
944.1 | 836.1 | 519.9 | 237.1 | 580.1 | 555.1 | 552.5 | 365 | 351.2 | 422.5
945.1 | 837.1 | 520.2 | 236.9 | 580.2 | 555 | 551.8 | 365 | 351.3 | 422.6
946.1 | 838.1 | 520.1 | 236.9 | 580.4 | 555.5 | 549.2 | 365.1 | 351.5 | 422.7
947.1 | 839.1 | 520 | 237.1 | 581.4 | 555.8 | 548.2 | 365.1 | 351.6 | 422.8
948.1 | 840.1 | 519.9 | 237.9 | 581 | 555.9 | 549 | 365.2 | 351.7 | 422.9
949.1 | 841.1 | 520 | 238.4 | 580.3 | 556.7 | 552 | 365.2 | 351.8 | 423
950.1 | 842.1 | 520.1 | 237.8 | 581.3 | 558.3 | 554.4 | 365.2 | 351.9 | 423
951.1 | 843.1 | 520.1 | 238.1 | 581.8 | 559.5 | 555.4 | 365.2 | 352 | 423.1
952.1 | 844.1 | 520.2 | 238.8 | 582.5 | 560.6 | 556.9 | 365.3 | 352.1 | 423.1
953.1 | 845.1 | 520.1 | 237.2 | 583.5 | 561.9 | 555.6 | 365.3 | 352.2 | 423.2
954.1 | 846.1 | 520.2 | 236.5 | 583.4 | 562.5 | 554 | 365.4 | 352.3 | 423.3
955.1 | 847.1 | 520.1 | 235.9 | 582.8 | 562 | 553.4 | 365.4 | 352.4 | 423.3
956.1 | 848.1 | 520 | 235.6 | 583.2 | 561.8 | 554.1 | 365.5 | 352.5 | 423.4
957.1 | 849.1 | 519.9 | 235.1 | 583.1 | 561.5 | 554.4 | 365.5 | 352.7 | 423.4
958.1 | 850.1 | 519.9 | 234.9 | 582.6 | 562 | 553.6 | 365.5 | 352.8 | 423.5
959.1 | 851.1 | 519.9 | 234.9 | 583.2 | 561.8 | 551.8 | 365.6 | 352.9 | 423.6
960.1 | 852.1 | 519.8 | 234.2 | 583.6 | 561.8 | 551.5 | 365.6 | 353 | 423.6
961.1 | 853.1 | 519.7 | 233.6 | 582.8 | 562.4 | 552.1 | 365.6 | 353 | 423.6
962.1 | 854.1 | 519.7 | 233.2 | 582 | 562.3 | 551.9 | 365.6 | 353.1 | 423.7
963.1 | 855.1 | 519.7 | 233.2 | 582.5 | 562.7 | 550.8 | 365.6 | 353.2 | 423.8
964.1 | 856.1 | 519.6 | 233.2 | 582.2 | 563.3 | 550.1 | 365.7 | 353.3 | 423.8
965.1 | 857.1 | 519.5 | 232.5 | 581.6 | 563.3 | 550 | 365.7 | 353.3 | 423.8
966.1 | 858.1 | 519.4 | 232.8 | 580.6 | 563.5 | 549.9 | 365.7 | 353.4 | 423.8
967.1 | 859.1 | 519.2 | 233.5 | 580.5 | 564.4 | 549.4 | 365.8 | 353.5 | 423.9
968.1 | 860.1 | 519.1 | 233.8 | 580.9 | 564.8 | 548.7 | 365.8 | 353.7 | 423.9
969.1 | 861.1 | 519.1 | 234.6 | 580.7 | 565.4 | 548.5 | 365.8 | 353.8 | 423.9
970.1 | 862.1 | 519.2 | 234.5 | 580 | 566.3 | 547.9 | 365.8 | 353.9 | 423.9
971.1 | 863.1 | 519.2 | 234.9 | 580.3 | 567.5 | 548.1 | 365.8 | 354 | 423.9
972.1 | 864.1 | 519.1 | 237.1 | 579.7 | 569.6 | 547.4 | 365.8 | 354.1 | 424
973.1 | 865.1 | 519.1 | 237.2 | 579.9 | 570.6 | 545.1 | 365.8 | 354.2 | 424.1
974.1 | 866.1 | 519.1 | 237.7 | 580.8 | 572 | 545.8 | 365.9 | 354.3 | 424.1
975.1 | 867.1 | 519.3 | 238.9 | 580.7 | 573.4 | 546.4 | 365.9 | 354.4 | 424.2
976.1 | 868.1 | 519.8 | 238.4 | 580.3 | 574.5 | 547 | 365.9 | 354.5 | 424.2
977.1 | 869.1 | 519.9 | 238.2 | 580.5 | 575.6 | 547.9 | 365.9 | 354.6 | 424.3
978.1 | 870.1 | 519.9 | 238.1 | 580.3 | 577 | 549.4 | 365.9 | 354.7 | 424.4
979.1 | 871.1 | 520 | 238.1 | 580.9 | 578.8 | 550.6 | 365.9 | 354.9 | 424.5
980.1 | 872.1 | 520.1 | 237.8 | 581.3 | 580 | 551.4 | 365.9 | 355 | 424.6
981.1 | 873.1 | 520.2 | 237 | 581 | 580.3 | 552.3 | 366 | 355.2 | 424.6
982.1 | 874.1 | 520.2 | 236.5 | 581.1 | 581.1 | 553.1 | 366 | 355.3 | 424.7
983.1 | 875.1 | 520.3 | 236.6 | 580.6 | 581.2 | 553.3 | 366 | 355.4 | 424.8
984.1 | 876.1 | 520.5 | 236.8 | 579.9 | 581.1 | 553.5 | 366.1 | 355.6 | 424.9
985.1 | 877.1 | 520.6 | 236.2 | 579.4 | 580.5 | 552.2 | 366.1 | 355.7 | 425
986.1 | 878.1 | 520.6 | 237 | 579.2 | 580.3 | 552.2 | 366.2 | 355.8 | 425.1
987.1 | 879.1 | 520.5 | 237.1 | 580 | 580.3 | 552.8 | 366.2 | 355.9 | 425.2
988.1 | 880.1 | 520.5 | 237.9 | 580.6 | 580.7 | 553 | 366.3 | 356 | 425.3
989.1 | 881.1 | 520.4 | 237.9 | 581.2 | 580.8 | 551.2 | 366.3 | 356.1 | 425.3
990.1 | 882.1 | 520.3 | 237.6 | 581.3 | 580.9 | 551.1 | 366.3 | 356.2 | 425.4
991.1 | 883.1 | 520.1 | 238.6 | 581.7 | 581 | 551.7 | 366.4 | 356.3 | 425.4
992.1 | 884.1 | 519.9 | 238.7 | 581.9 | 581.9 | 550.8 | 366.4 | 356.4 | 425.5
993.1 | 885.1 | 519.9 | 237.5 | 582.6 | 582.9 | 550.7 | 366.5 | 356.5 | 425.5
994.1 | 886.1 | 519.7 | 235.9 | 583.3 | 583.2 | 550.9 | 366.5 | 356.5 | 425.6
995.1 | 887.1 | 519.5 | 235.3 | 583.5 | 583.7 | 551.1 | 366.6 | 356.6 | 425.6
996.1 | 888.1 | 519.4 | 236 | 583.6 | 584.3 | 551.7 | 366.7 | 356.7 | 425.7
997.1 | 889.1 | 519.2 | 236.1 | 584.3 | 585.1 | 552 | 366.7 | 356.7 | 425.7
998.1 | 890.1 | 519 | 234.9 | 585.5 | 585.8 | 551.8 | 366.8 | 356.8 | 425.7
999.1 | 891.1 | 519 | 233.5 | 585.5 | 585.8 | 551 | 366.8 | 356.9 | 425.8
1000.1 | 892.1 | 519.1 | 233 | 585.2 | 586.3 | 550.9 | 366.8 | 356.9 | 425.9
1001.1 | 893.1 | 519.2 | 232.1 | 585 | 586.7 | 550.9 | 366.9 | 356.9 | 426
1002.1 | 894.1 | 519.2 | 231.7 | 584.9 | 586.8 | 551.5 | 366.9 | 357 | 426.1
1003.1 | 895.1 | 519 | 231.1 | 585.1 | 586.6 | 551.7 | 367 | 357.1 | 426.1
1004.1 | 896.1 | 519.2 | 231.3 | 585.7 | 586.8 | 550.7 | 367 | 357.1 | 426.2
1005.1 | 897.1 | 519.3 | 232.9 | 585.8 | 586.5 | 546.5 | 367.1 | 357.2 | 426.2
1006.1 | 898.1 | 519.3 | 233.4 | 585.5 | 586 | 544.6 | 367.1 | 357.3 | 426.2
1007.1 | 899.1 | 519.2 | 234 | 585.3 | 586.1 | 544.9 | 367.2 | 357.4 | 426.3
1008.1 | 900.1 | 519.3 | 235.2 | 584.6 | 586.2 | 547.6 | 367.2 | 357.4 | 426.3
1009.1 | 901.1 | 519.5 | 235.7 | 584.1 | 586.7 | 549.9 | 367.3 | 357.5 | 426.3
1010.1 | 902.1 | 519.5 | 235 | 584.4 | 587.9 | 551.1 | 367.4 | 357.6 | 426.4
1011.1 | 903.1 | 519.9 | 235.5 | 584.1 | 588.4 | 551.9 | 367.4 | 357.7 | 426.4
1012.1 | 904.1 | 520.1 | 236.3 | 583.8 | 588.7 | 552.6 | 367.5 | 357.8 | 426.5
1013.1 | 905.1 | 520.3 | 240.5 | 584.6 | 589.2 | 555.1 | 367.6 | 357.8 | 426.6
1014.1 | 906.1 | 520.5 | 241.8 | 584.7 | 589.9 | 557.5 | 367.6 | 357.9 | 426.7
1015.1 | 907.1 | 520.9 | 241.7 | 584.2 | 591 | 557.3 | 367.7 | 357.9 | 426.7
1016.1 | 908.1 | 521.2 | 242.3 | 584.5 | 592.3 | 556.7 | 367.7 | 358 | 426.8
1017.1 | 909.1 | 521.4 | 241.6 | 584.6 | 592.8 | 555.8 | 367.8 | 358 | 426.9
1018.1 | 910.1 | 521.5 | 241.1 | 584.8 | 592.4 | 555.2 | 367.8 | 358.1 | 427
1019.1 | 911.1 | 521.5 | 239.8 | 584.7 | 592.7 | 553.7 | 367.9 | 358.1 | 427.1
1020.1 | 912.1 | 521.4 | 238.4 | 584.4 | 593.1 | 551.9 | 367.9 | 358.2 | 427.3
1021.1 | 913.1 | 521.4 | 237.9 | 583.7 | 593.1 | 551.7 | 367.9 | 358.2 | 427.4
1022.1 | 914.1 | 521.3 | 238.6 | 583 | 592.8 | 552.3 | 368 | 358.3 | 427.4
1023.1 | 915.1 | 521.4 | 238.7 | 582.9 | 593 | 552.5 | 368 | 358.4 | 427.5
1024.1 | 916.1 | 521.3 | 238.1 | 583.4 | 593.3 | 552.7 | 368.1 | 358.5 | 427.6
1025.1 | 917.1 | 521.3 | 243.7 | 583 | 593.2 | 553.8 | 368.1 | 358.6 | 427.6
1026.1 | 918.1 | 521.4 | 249.6 | 583.1 | 592.9 | 555.2 | 368.1 | 358.7 | 427.6
1027.1 | 919.1 | 521.4 | 249.1 | 582.9 | 593.9 | 557.2 | 368.2 | 358.8 | 427.6
1028.1 | 920.1 | 521.2 | 247.7 | 583.2 | 595.5 | 557.5 | 368.2 | 358.8 | 427.6
1029.1 | 921.1 | 520.9 | 245.1 | 584 | 595.8 | 556.2 | 368.2 | 358.9 | 427.6
1030.1 | 922.1 | 520.7 | 243.6 | 584.6 | 595.3 | 554.4 | 368.3 | 359 | 427.6
1031.1 | 923.1 | 520.8 | 242.5 | 584.5 | 594.9 | 553.1 | 368.3 | 359 | 427.6
1032.1 | 924.1 | 520.8 | 241.5 | 584.4 | 594.9 | 553.5 | 368.4 | 359.1 | 427.7
1033.1 | 925.1 | 520.7 | 240 | 584 | 594.8 | 552.2 | 368.5 | 359.1 | 427.8
1034.1 | 926.1 | 520.5 | 239 | 583.7 | 594.8 | 549.5 | 368.5 | 359.2 | 427.8
1035.1 | 927.1 | 520.5 | 238.1 | 583.6 | 595.5 | 550.4 | 368.6 | 359.2 | 427.8
1036.1 | 928.1 | 520.4 | 236.9 | 583.3 | 596.6 | 551 | 368.6 | 359.2 | 427.8
1037.1 | 929.1 | 520.2 | 236.1 | 583.4 | 597.7 | 552.1 | 368.7 | 359.3 | 427.8
1038.1 | 930.1 | 520.2 | 236.9 | 583.4 | 598.2 | 552.3 | 368.7 | 359.3 | 427.9
1039.1 | 931.1 | 520.3 | 237.9 | 583 | 599.2 | 554 | 368.8 | 359.4 | 427.9
1040.1 | 932.1 | 520.2 | 237.1 | 582.2 | 600.1 | 555.2 | 368.8 | 359.4 | 427.9
1041.1 | 933.1 | 519.9 | 236.9 | 581.7 | 600.7 | 555.3 | 368.8 | 359.5 | 428
1042.1 | 934.1 | 519.7 | 236.9 | 581.1 | 601.3 | 555.1 | 368.9 | 359.5 | 428.1
1043.1 | 935.1 | 519.7 | 238.1 | 581.1 | 601.2 | 555.6 | 368.9 | 359.5 | 428.2
1044.1 | 936.1 | 519.6 | 236.8 | 581.4 | 601.2 | 554.2 | 368.9 | 359.6 | 428.2
1045.1 | 937.1 | 519.7 | 236.4 | 581.4 | 601.3 | 553.8 | 369 | 359.6 | 428.3
1046.1 | 938.1 | 519.7 | 235.8 | 581.3 | 602.5 | 554.6 | 369 | 359.6 | 428.4
1047.1 | 939.1 | 519.4 | 235.8 | 581.2 | 602.7 | 553.7 | 369 | 359.7 | 428.4
1048.1 | 940.1 | 519.4 | 235.8 | 581 | 603.3 | 555.2 | 369 | 359.7 | 428.5
1049.1 | 941.1 | 519.3 | 234.5 | 580.5 | 604.4 | 556.7 | 369.1 | 359.8 | 428.5
1050.1 | 942.1 | 519.3 | 234.1 | 580.3 | 604.9 | 556.9 | 369.1 | 359.8 | 428.6
1051.1 | 943.1 | 519.3 | 234.4 | 580.5 | 605.7 | 557.1 | 369.1 | 359.9 | 428.7
1052.1 | 944.1 | 519.5 | 234 | 581 | 605 | 557.7 | 369.2 | 359.9 | 428.7
1053.1 | 945.1 | 519.6 | 234.1 | 581.1 | 605.2 | 556.1 | 369.2 | 360 | 428.8
1054.1 | 946.1 | 519.7 | 234.7 | 580.6 | 605.3 | 555.4 | 369.2 | 360.1 | 428.8
1055.1 | 947.1 | 519.7 | 234.7 | 580.2 | 605.5 | 555 | 369.2 | 360.1 | 428.9
1056.1 | 948.1 | 519.4 | 235.2 | 579.7 | 605.8 | 554.7 | 369.3 | 360.2 | 429
1057.1 | 949.1 | 519.1 | 234.5 | 578.5 | 606.6 | 555.5 | 369.3 | 360.3 | 429.1
1058.1 | 950.1 | 519.1 | 234.1 | 577.5 | 607.6 | 555.5 | 369.4 | 360.3 | 429.1
1059.1 | 951.1 | 519.2 | 234.6 | 577 | 608.4 | 555.1 | 369.4 | 360.3 | 429.1
1060.1 | 952.1 | 519.2 | 233.9 | 577.2 | 608.3 | 554 | 369.4 | 360.4 | 429.1
1061.1 | 953.1 | 519 | 233.6 | 577 | 608.3 | 553.3 | 369.5 | 360.4 | 429.1
1062.1 | 954.1 | 518.9 | 234.5 | 576.2 | 608.4 | 552.5 | 369.5 | 360.4 | 429.2
1063.1 | 955.1 | 518.8 | 235.6 | 575.9 | 607 | 551.6 | 369.5 | 360.5 | 429.2
1064.1 | 956.1 | 518.8 | 238.8 | 575.3 | 607.3 | 551.1 | 369.5 | 360.5 | 429.2
1065.1 | 957.1 | 518.8 | 240.2 | 574.3 | 608.1 | 549.9 | 369.6 | 360.6 | 429.2
1066.1 | 958.1 | 518.5 | 243.2 | 573.5 | 608 | 550.2 | 369.6 | 360.6 | 429.2
1067.1 | 959.1 | 518.3 | 243.8 | 572.7 | 608.2 | 552.5 | 369.7 | 360.7 | 429.3
1068.1 | 960.1 | 518.3 | 243.3 | 572.4 | 609 | 555 | 369.7 | 360.7 | 429.3
1069.1 | 961.1 | 518.2 | 241.5 | 573.1 | 610.1 | 556.4 | 369.7 | 360.7 | 429.3
1070.1 | 962.1 | 518.4 | 239.5 | 573.6 | 610.6 | 556.2 | 369.8 | 360.8 | 429.3
1071.1 | 963.1 | 518.6 | 238.2 | 573.8 | 610.6 | 556.3 | 369.8 | 360.8 | 429.4
1072.1 | 964.1 | 518.7 | 237.6 | 573 | 610.8 | 554.6 | 369.8 | 360.9 | 429.5
1073.1 | 965.1 | 518.7 | 236.9 | 573.2 | 610.4 | 552 | 369.8 | 360.9 | 429.5
1074.1 | 966.1 | 518.9 | 236 | 573 | 610.7 | 551.8 | 369.9 | 361 | 429.6
1075.1 | 967.1 | 519 | 235.9 | 572.5 | 610.8 | 551.4 | 369.9 | 361.1 | 429.6
1076.1 | 968.1 | 519 | 235 | 572.3 | 611 | 550.6 | 369.9 | 361.1 | 429.7
1077.1 | 969.1 | 519.1 | 235.1 | 571.8 | 611.3 | 550.2 | 369.9 | 361.2 | 429.7
1078.1 | 970.1 | 519.2 | 235.1 | 569.8 | 611.3 | 549.8 | 369.9 | 361.2 | 429.8
1079.1 | 971.1 | 519.2 | 236.1 | 569.1 | 611.6 | 548.2 | 369.9 | 361.3 | 429.8
1080.1 | 972.1 | 519.2 | 236.2 | 567.9 | 612.2 | 548.7 | 369.9 | 361.3 | 429.8
1081.1 | 973.1 | 519.1 | 235.9 | 567.7 | 612.2 | 548 | 369.9 | 361.3 | 429.9
1082.1 | 974.1 | 519 | 236.1 | 567 | 612.3 | 548 | 369.9 | 361.4 | 429.9
1083.1 | 975.1 | 519 | 235.6 | 567.1 | 613.2 | 548.5 | 369.9 | 361.4 | 429.9
1084.1 | 976.1 | 519.1 | 236.2 | 566.9 | 613.6 | 547.6 | 369.9 | 361.4 | 430
1085.1 | 977.1 | 519.1 | 236.3 | 566.1 | 613.4 | 546.4 | 369.9 | 361.4 | 430
1086.1 | 978.1 | 519.1 | 236 | 565.6 | 613.3 | 543.3 | 370 | 361.5 | 430
1087.1 | 979.1 | 519 | 235.7 | 565.1 | 613.7 | 544.5 | 370 | 361.6 | 430.1
1088.1 | 980.1 | 518.9 | 236 | 564 | 614.3 | 545.9 | 370 | 361.7 | 430.1
1089.1 | 981.1 | 518.8 | 235.7 | 563.1 | 614.9 | 545.5 | 370 | 361.7 | 430.1
1090.1 | 982.1 | 518.8 | 236.5 | 562 | 615.1 | 545.2 | 370 | 361.8 | 430.1
1091.1 | 983.1 | 518.7 | 237.4 | 558.5 | 615.1 | 546.2 | 370 | 361.8 | 430.1
1092.1 | 984.1 | 518.7 | 238.1 | 557.2 | 615.6 | 547.7 | 370 | 361.9 | 430.1
1093.1 | 985.1 | 518.7 | 241.3 | 557 | 615.2 | 549.5 | 370.1 | 362 | 430.1
1094.1 | 986.1 | 519 | 240.7 | 556.9 | 616 | 551.4 | 370.1 | 362.1 | 430.2
1095.1 | 987.1 | 519.1 | 239.5 | 556.5 | 616.1 | 552.2 | 370.1 | 362.1 | 430.2
1096.1 | 988.1 | 519.2 | 239.7 | 556.8 | 617.4 | 552.6 | 370.1 | 362.2 | 430.2
1097.1 | 989.1 | 519.3 | 240.5 | 557.6 | 618 | 551.8 | 370.2 | 362.3 | 430.2
1098.1 | 990.1 | 519.3 | 239.8 | 557.7 | 618.5 | 550.6 | 370.2 | 362.4 | 430.3
1099.1 | 991.1 | 519.4 | 239.8 | 556.6 | 619 | 551.2 | 370.2 | 362.5 | 430.3
1100.1 | 992.1 | 519.5 | 239 | 555.6 | 619.1 | 551.3 | 370.2 | 362.6 | 430.4
1101.1 | 993.1 | 519.8 | 238.2 | 556.2 | 619.5 | 551.8 | 370.3 | 362.7 | 430.4
1102.1 | 994.1 | 520 | 237.7 | 555.8 | 619.8 | 551.1 | 370.3 | 362.8 | 430.5
1103.1 | 995.1 | 520.2 | 237 | 556.3 | 619.9 | 551.1 | 370.3 | 362.9 | 430.6
1104.1 | 996.1 | 520.2 | 236.8 | 555.9 | 619.9 | 550.2 | 370.4 | 363 | 430.6
1105.1 | 997.1 | 520.3 | 236.6 | 555.7 | 619.5 | 548.1 | 370.4 | 363 | 430.7
1106.1 | 998.1 | 520.5 | 236.3 | 555.7 | 619.5 | 549 | 370.4 | 363.1 | 430.8
1107.1 | 999.1 | 520.7 | 236 | 556 | 619.8 | 548.6 | 370.5 | 363.2 | 430.9
1108.1 | 1000.1 | 520.4 | 235.4 | 556.3 | 620 | 548.7 | 370.5 | 363.3 | 431
1109.1 | 1001.1 | 520.4 | 235.2 | 556.3 | 619.7 | 549 | 370.5 | 363.4 | 431
1110.1 | 1002.1 | 520.4 | 235.1 | 556 | 619.2 | 547.1 | 370.6 | 363.5 | 431
1111.1 | 1003.1 | 520.4 | 235.5 | 555.2 | 618.2 | 545.4 | 370.6 | 363.6 | 431
1112.1 | 1004.1 | 520.1 | 236.1 | 554.3 | 618.4 | 544.9 | 370.7 | 363.6 | 431
1113.1 | 1005.1 | 520.1 | 236.5 | 554.6 | 618.6 | 546.5 | 370.7 | 363.7 | 431
1114.1 | 1006.1 | 519.9 | 236 | 554.9 | 619.3 | 548.2 | 370.8 | 363.8 | 431
1115.1 | 1007.1 | 519.8 | 235.8 | 555.2 | 619.5 | 549.1 | 370.8 | 363.9 | 431
1116.1 | 1008.1 | 519.7 | 235.8 | 554.8 | 620.1 | 550.2 | 370.9 | 364 | 431.1
1117.1 | 1009.1 | 519.7 | 237.1 | 554.9 | 620.3 | 549.5 | 370.9 | 364.1 | 431.2
1118.1 | 1010.1 | 519.6 | 236.3 | 555 | 620.5 | 549.1 | 371 | 364.1 | 431.3
1119.1 | 1011.1 | 519.5 | 236.1 | 555.2 | 620.6 | 551.1 | 371 | 364.2 | 431.3
1120.1 | 1012.1 | 519.5 | 235.6 | 555.6 | 621 | 552.7 | 371 | 364.3 | 431.3
1121.1 | 1013.1 | 519.4 | 235.5 | 558.6 | 621.1 | 553.4 | 371.1 | 364.4 | 431.4
1122.1 | 1014.1 | 519.4 | 236.6 | 561.2 | 621.7 | 554.2 | 371.1 | 364.5 | 431.4
1123.1 | 1015.1 | 519.5 | 237.2 | 563.6 | 622.3 | 553.5 | 371.2 | 364.6 | 431.4
1124.1 | 1016.1 | 519.6 | 236.5 | 565.5 | 622.5 | 552.3 | 371.2 | 364.7 | 431.5
1125.1 | 1017.1 | 519.4 | 237 | 567.3 | 622.5 | 553 | 371.2 | 364.7 | 431.5
1126.1 | 1018.1 | 519.5 | 237 | 568.5 | 622.4 | 554.1 | 371.3 | 364.8 | 431.5
1127.1 | 1019.1 | 519.6 | 237.5 | 569.5 | 621.8 | 554.9 | 371.3 | 364.9 | 431.6
1128.1 | 1020.1 | 519.6 | 242 | 569.9 | 621.6 | 554.8 | 371.4 | 365 | 431.6
1129.1 | 1021.1 | 519.5 | 246.1 | 569.9 | 620.9 | 555.9 | 371.4 | 365.1 | 431.7
1130.1 | 1022.1 | 519.6 | 245.8 | 571.2 | 620.3 | 557.2 | 371.5 | 365.1 | 431.8
1131.1 | 1023.1 | 519.8 | 245.3 | 572.6 | 620.3 | 557.6 | 371.6 | 365.1 | 431.9
1132.1 | 1024.1 | 520 | 246 | 573.6 | 620.5 | 555.5 | 371.6 | 365.1 | 432
1133.1 | 1025.1 | 520.1 | 244.2 | 574.7 | 621 | 554.3 | 371.7 | 365.1 | 432
1134.1 | 1026.1 | 520.3 | 245.1 | 576 | 621.2 | 553.7 | 371.8 | 365.1 | 432.1
1135.1 | 1027.1 | 520.2 | 244.9 | 577 | 621.6 | 553.8 | 371.9 | 365.1 | 432.1
1136.1 | 1028.1 | 520.2 | 244.9 | 577.9 | 621.7 | 553.7 | 372 | 365.2 | 432.2
1137.1 | 1029.1 | 520 | 244.6 | 578.1 | 621.7 | 554.2 | 372 | 365.3 | 432.2
1138.1 | 1030.1 | 519.9 | 243.1 | 579 | 621.7 | 552.8 | 372.1 | 365.4 | 432.2
1139.1 | 1031.1 | 520.2 | 242.4 | 579.7 | 622.4 | 552.2 | 372.2 | 365.4 | 432.2
1140.1 | 1032.1 | 520.2 | 242.4 | 580.7 | 622.6 | 553.2 | 372.2 | 365.5 | 432.3
1141.1 | 1033.1 | 520.3 | 242 | 581.2 | 622.5 | 554.2 | 372.3 | 365.6 | 432.4
1142.1 | 1034.1 | 520.4 | 244.4 | 580.9 | 622.2 | 554.7 | 372.4 | 365.7 | 432.4
1143.1 | 1035.1 | 520.5 | 246.4 | 581.3 | 622.5 | 555.6 | 372.4 | 365.7 | 432.5
1144.1 | 1036.1 | 520.5 | 244.9 | 581.9 | 622.8 | 555.6 | 372.5 | 365.8 | 432.6
1145.1 | 1037.1 | 520.3 | 245.9 | 582.8 | 623.2 | 555.3 | 372.6 | 365.9 | 432.7
1146.1 | 1038.1 | 520.3 | 245.1 | 583.7 | 622.6 | 553.4 | 372.6 | 366 | 432.8
1147.1 | 1039.1 | 520.2 | 243.4 | 583.9 | 622.5 | 552.6 | 372.6 | 366 | 432.9
1148.1 | 1040.1 | 520.5 | 241.6 | 584 | 622.4 | 552.3 | 372.7 | 366.1 | 433
1149.1 | 1041.1 | 520.9 | 240.9 | 584.1 | 622.4 | 552.8 | 372.8 | 366.1 | 433.1
1150.1 | 1042.1 | 521 | 239.6 | 583.3 | 622.2 | 552.3 | 372.8 | 366.2 | 433.2
1151.1 | 1043.1 | 521.2 | 239.3 | 582.5 | 621.4 | 552.5 | 372.9 | 366.3 | 433.3
1152.1 | 1044.1 | 521.4 | 238.5 | 582.4 | 621.2 | 552.7 | 372.9 | 366.3 | 433.3
1153.1 | 1045.1 | 521.5 | 237.4 | 582.8 | 621 | 551.8 | 373 | 366.3 | 433.4
1154.1 | 1046.1 | 521.3 | 239 | 582.3 | 620.1 | 550.3 | 373 | 366.4 | 433.5
1155.1 | 1047.1 | 521.3 | 238.7 | 581.9 | 619.7 | 550 | 373.1 | 366.4 | 433.5
1156.1 | 1048.1 | 521.3 | 237.1 | 582.5 | 620.2 | 550.9 | 373.1 | 366.4 | 433.6
1157.1 | 1049.1 | 521.5 | 236.3 | 583.2 | 620.6 | 550.4 | 373.1 | 366.5 | 433.7
1158.1 | 1050.1 | 521.7 | 236.4 | 583.4 | 620.4 | 549.8 | 373.1 | 366.5 | 433.7
1159.1 | 1051.1 | 521.6 | 238 | 582.6 | 619.5 | 549.6 | 373.1 | 366.6 | 433.8
1160.1 | 1052.1 | 521.7 | 240.6 | 582.8 | 618.7 | 549.8 | 373.1 | 366.7 | 433.8
1161.1 | 1053.1 | 521.7 | 240.1 | 583.3 | 618.9 | 550.9 | 373.1 | 366.7 | 433.8
1162.1 | 1054.1 | 521.5 | 238.6 | 583.8 | 619.4 | 551.5 | 373.1 | 366.7 | 433.8
1163.1 | 1055.1 | 521.4 | 239.2 | 583.7 | 619.5 | 552.5 | 373.1 | 366.8 | 433.8
1164.1 | 1056.1 | 521.4 | 240.3 | 583.8 | 620 | 552.5 | 373.2 | 366.8 | 433.9
1165.1 | 1057.1 | 521.3 | 240.8 | 583.8 | 619.9 | 551.7 | 373.1 | 366.9 | 433.9
1166.1 | 1058.1 | 521.4 | 244.6 | 582.6 | 619.5 | 550.2 | 373.2 | 367 | 434
1167.1 | 1059.1 | 521.3 | 244.3 | 581.6 | 619.5 | 550.6 | 373.2 | 367.1 | 434.1
1168.1 | 1060.1 | 521.2 | 242.8 | 582.2 | 619.6 | 549.4 | 373.2 | 367.1 | 434.1
1169.1 | 1061.1 | 521.1 | 242.6 | 583.1 | 619.1 | 549.1 | 373.3 | 367.2 | 434.1
1170.1 | 1062.1 | 520.9 | 243.4 | 583.2 | 619.5 | 550.4 | 373.3 | 367.2 | 434.2
1171.1 | 1063.1 | 520.6 | 244.6 | 583.1 | 620.7 | 550.9 | 373.3 | 367.3 | 434.3
1172.1 | 1064.1 | 520.4 | 243.7 | 583 | 620.9 | 550.5 | 373.3 | 367.3 | 434.3
1173.1 | 1065.1 | 520.3 | 243 | 583.6 | 620.2 | 550.9 | 373.3 | 367.4 | 434.3
1174.1 | 1066.1 | 520.2 | 242.2 | 583.8 | 620.1 | 551.5 | 373.3 | 367.4 | 434.4
1175.1 | 1067.1 | 520.1 | 241.9 | 584.2 | 620.7 | 551.6 | 373.3 | 367.4 | 434.5
1176.1 | 1068.1 | 520 | 241.3 | 584 | 620 | 552.1 | 373.4 | 367.5 | 434.5
1177.1 | 1069.1 | 520 | 241 | 583.7 | 619.3 | 551.2 | 373.4 | 367.5 | 434.5
1178.1 | 1070.1 | 520.1 | 240.1 | 583.2 | 619.3 | 548.4 | 373.3 | 367.6 | 434.5
1179.1 | 1071.1 | 520 | 240.2 | 582.8 | 619.2 | 543 | 373.3 | 367.6 | 434.5
1180.1 | 1072.1 | 520 | 241.3 | 582.7 | 619 | 539.8 | 373.3 | 367.7 | 434.5
1181.1 | 1073.1 | 519.9 | 243.4 | 581.7 | 618.3 | 535.6 | 373.4 | 367.8 | 434.5
1182.1 | 1074.1 | 519.9 | 244.9 | 581.4 | 618 | 530.5 | 373.4 | 367.8 | 434.5
1183.1 | 1075.1 | 519.7 | 248.2 | 580.7 | 617.7 | 527.5 | 373.4 | 367.9 | 434.5
1184.1 | 1076.1 | 519.9 | 249.2 | 580.1 | 617.8 | 526 | 373.4 | 368 | 434.5
1185.1 | 1077.1 | 520.1 | 249.4 | 579 | 618 | 525.5 | 373.4 | 368.1 | 434.5
1186.1 | 1078.1 | 519.9 | 249.4 | 579 | 618.5 | 527 | 373.5 | 368.1 | 434.5
1187.1 | 1079.1 | 519.9 | 249.3 | 580.4 | 618.8 | 527.9 | 373.5 | 368.2 | 434.5
1188.1 | 1080.1 | 519.8 | 248.4 | 581.6 | 619.6 | 529.6 | 373.6 | 368.3 | 434.6
1189.1 | 1081.1 | 519.8 | 247.7 | 582.6 | 620.6 | 532 | 373.6 | 368.4 | 434.6
1190.1 | 1082.1 | 520 | 247.7 | 583.4 | 620.9 | 534.9 | 373.6 | 368.5 | 434.7
1191.1 | 1083.1 | 520.1 | 246.8 | 584.1 | 621.6 | 536.8 | 373.6 | 368.6 | 434.7
1192.1 | 1084.1 | 520.3 | 246.1 | 584 | 622 | 538 | 373.6 | 368.7 | 434.7
1193.1 | 1085.1 | 520.4 | 245.2 | 584.8 | 622.3 | 539.3 | 373.6 | 368.7 | 434.7
1194.1 | 1086.1 | 520.4 | 245 | 585.1 | 622.5 | 541.1 | 373.6 | 368.8 | 434.8
1195.1 | 1087.1 | 520.3 | 244.1 | 585.6 | 622.6 | 540.2 | 373.7 | 368.9 | 434.9
1196.1 | 1088.1 | 520.6 | 243.4 | 586 | 623.1 | 540.5 | 373.7 | 368.9 | 434.9
1197.1 | 1089.1 | 520.7 | 243 | 585.5 | 623.3 | 539 | 373.8 | 369 | 435
1198.1 | 1090.1 | 520.8 | 242.4 | 585.3 | 623.5 | 538.5 | 373.8 | 369 | 435
1199.1 | 1091.1 | 520.8 | 243.2 | 585.4 | 623.9 | 540.2 | 373.8 | 369.1 | 435
1200.1 | 1092.1 | 520.7 | 244 | 585.3 | 624.3 | 541.1 | 373.9 | 369.2 | 435.1
1201.1 | 1093.1 | 520.5 | 243.8 | 585.1 | 624.3 | 541.5 | 373.9 | 369.2 | 435.2
1202.1 | 1094.1 | 520.6 | 243.1 | 585.1 | 625.2 | 542.1 | 374 | 369.3 | 435.2
1203.1 | 1095.1 | 520.6 | 244.7 | 585.5 | 625.8 | 540.9 | 374 | 369.3 | 435.3
1204.1 | 1096.1 | 520.8 | 245.1 | 586.1 | 626.6 | 540.8 | 374 | 369.3 | 435.4
1205.1 | 1097.1 | 520.9 | 243.7 | 587.2 | 627 | 541.2 | 374.1 | 369.3 | 435.4
1206.1 | 1098.1 | 520.8 | 243 | 588.1 | 627.7 | 540.9 | 374.1 | 369.3 | 435.5
1207.1 | 1099.1 | 520.8 | 241.8 | 588.7 | 627.9 | 540.6 | 374.1 | 369.3 | 435.6
1208.1 | 1100.1 | 520.7 | 241 | 589.1 | 628.1 | 540.4 | 374.1 | 369.3 | 435.7
1209.1 | 1101.1 | 520.5 | 239.9 | 589.1 | 628.5 | 540.5 | 374.1 | 369.3 | 435.7
1210.1 | 1102.1 | 520.4 | 239.2 | 588.8 | 629.3 | 541.3 | 374.1 | 369.3 | 435.8
1211.1 | 1103.1 | 520.1 | 239.7 | 588.8 | 630.2 | 540.4 | 374.1 | 369.3 | 435.9
1212.1 | 1104.1 | 519.9 | 239.7 | 589.2 | 630.9 | 540.5 | 374.1 | 369.4 | 435.9
1213.1 | 1105.1 | 520 | 240.1 | 589.5 | 631.6 | 540.4 | 374.1 | 369.4 | 436
1214.1 | 1106.1 | 520.1 | 238.9 | 589.9 | 632.1 | 540.7 | 374.1 | 369.4 | 436
1215.1 | 1107.1 | 520.1 | 237.8 | 590.2 | 633.1 | 540.4 | 374.1 | 369.4 | 436.1
1216.1 | 1108.1 | 519.9 | 237 | 590.5 | 634.1 | 537.4 | 374.1 | 369.4 | 436.1
1217.1 | 1109.1 | 519.6 | 236.9 | 590.3 | 634.3 | 537.6 | 374.2 | 369.4 | 436.1
1218.1 | 1110.1 | 519.6 | 237.1 | 589.5 | 634.8 | 537 | 374.2 | 369.4 | 436.1
1219.1 | 1111.1 | 519.4 | 237 | 589.3 | 635.4 | 536.1 | 374.2 | 369.4 | 436.2
1220.1 | 1112.1 | 519.1 | 236.3 | 589.4 | 635.6 | 537.2 | 374.2 | 369.4 | 436.2
1221.1 | 1113.1 | 519 | 235.9 | 589.7 | 636 | 536.9 | 374.2 | 369.4 | 436.2
1222.1 | 1114.1 | 519.1 | 236.2 | 589.8 | 636.9 | 537.6 | 374.2 | 369.4 | 436.3
1223.1 | 1115.1 | 519.2 | 237.3 | 589.5 | 637.6 | 538 | 374.2 | 369.4 | 436.3
1224.1 | 1116.1 | 519.2 | 237.4 | 589.1 | 638.7 | 539.1 | 374.2 | 369.5 | 436.3
1225.1 | 1117.1 | 519.2 | 236.7 | 589.3 | 639.7 | 539 | 374.2 | 369.5 | 436.4
1226.1 | 1118.1 | 519.4 | 236.4 | 589.7 | 640.2 | 538.4 | 374.2 | 369.5 | 436.5
1227.1 | 1119.1 | 519.4 | 236.3 | 589.2 | 640.5 | 537.5 | 374.2 | 369.5 | 436.6
1228.1 | 1120.1 | 519.6 | 236.3 | 588.4 | 640.3 | 537.6 | 374.2 | 369.5 | 436.6
1229.1 | 1121.1 | 519.7 | 236.5 | 588 | 640.8 | 537.8 | 374.2 | 369.6 | 436.7
1230.1 | 1122.1 | 519.7 | 237.5 | 588.6 | 641.6 | 538.7 | 374.2 | 369.6 | 436.7
1231.1 | 1123.1 | 519.5 | 238 | 588.9 | 642.6 | 538.6 | 374.2 | 369.6 | 436.8
1232.1 | 1124.1 | 519.4 | 237.5 | 591.8 | 644.7 | 539.8 | 374.2 | 369.7 | 436.9
1233.1 | 1125.1 | 519.4 | 237.7 | 596.1 | 646.3 | 541.4 | 374.2 | 369.8 | 437.1
1234.1 | 1126.1 | 519.4 | 237.5 | 599.9 | 647.8 | 541.7 | 374.2 | 369.8 | 437.3
1235.1 | 1127.1 | 519.4 | 238.3 | 603.3 | 649.6 | 541.7 | 374.2 | 369.9 | 437.6
1236.1 | 1128.1 | 519.2 | 238.2 | 606.2 | 651.1 | 541.4 | 374.2 | 370 | 437.9
1237.1 | 1129.1 | 519.4 | 238.5 | 609.2 | 653 | 542.7 | 374.2 | 370 | 438.4
1238.1 | 1130.1 | 519.4 | 239.6 | 612.8 | 655.2 | 544.5 | 374.2 | 370.1 | 439
1239.1 | 1131.1 | 519.4 | 240.8 | 616.5 | 657.8 | 546.6 | 374.2 | 370.2 | 439.6
1240.1 | 1132.1 | 519.5 | 240.5 | 619.9 | 659.6 | 547.1 | 374.2 | 370.2 | 440.3
1241.1 | 1133.1 | 519.8 | 239.5 | 621.5 | 661.7 | 548.7 | 374.2 | 370.3 | 441
1242.1 | 1134.1 | 520 | 239.9 | 625.5 | 664.1 | 550.2 | 374.2 | 370.3 | 441.8
1243.1 | 1135.1 | 520 | 239.5 | 629.4 | 666.1 | 551.6 | 374.3 | 370.4 | 442.6
1244.1 | 1136.1 | 519.9 | 240.4 | 633 | 668.1 | 552.3 | 374.3 | 370.5 | 443.3
1245.1 | 1137.1 | 519.5 | 240.4 | 635.5 | 669.7 | 555.1 | 374.3 | 370.6 | 444.4
1246.1 | 1138.1 | 519.5 | 241.3 | 637.5 | 671.1 | 557.8 | 374.4 | 370.7 | 445.5
1247.1 | 1139.1 | 519.7 | 241.9 | 640.1 | 672.2 | 559.3 | 374.4 | 370.8 | 446.7
1248.1 | 1140.1 | 519.9 | 242.9 | 642.6 | 673.4 | 560.4 | 374.4 | 371 | 448
1249.1 | 1141.1 | 520 | 243.8 | 644.4 | 675.7 | 560.1 | 374.5 | 371.1 | 449.3
1250.1 | 1142.1 | 520.1 | 244.5 | 645.9 | 677.4 | 561.1 | 374.7 | 371.2 | 450.7
1251.1 | 1143.1 | 520.3 | 245.3 | 646.4 | 678.2 | 561.6 | 374.8 | 371.4 | 452.2
1252.1 | 1144.1 | 520.4 | 245.6 | 648.4 | 680 | 563.1 | 375 | 371.5 | 453.7
1253.1 | 1145.1 | 520.3 | 246.3 | 650.7 | 681.5 | 565.3 | 375.2 | 371.7 | 455.1
1254.1 | 1146.1 | 520.3 | 246.9 | 652.8 | 682.5 | 566 | 375.3 | 371.9 | 456.5
1255.1 | 1147.1 | 520.4 | 248.3 | 654.5 | 683.9 | 565.9 | 375.5 | 372.1 | 458
1256.1 | 1148.1 | 520.2 | 249.8 | 655.8 | 684.6 | 565.7 | 375.8 | 372.3 | 459.4
1257.1 | 1149.1 | 520 | 250.9 | 656.1 | 685.7 | 566.7 | 375.9 | 372.5 | 461
1258.1 | 1150.1 | 520 | 251.2 | 657.4 | 685.7 | 567.3 | 376.2 | 372.7 | 462.7
1259.1 | 1151.1 | 519.9 | 254.7 | 658 | 685.6 | 567.9 | 376.6 | 372.9 | 464.3
1260.1 | 1152.1 | 519.9 | 255 | 658.1 | 686 | 567.7 | 376.9 | 373.2 | 466
1261.1 | 1153.1 | 519.8 | 254.9 | 658.8 | 687.7 | 566.7 | 377.4 | 373.5 | 467.4
1262.1 | 1154.1 | 519.7 | 255.7 | 659.9 | 689 | 564.4 | 377.9 | 373.9 | 468.8
1263.1 | 1155.1 | 519.5 | 255.3 | 661.7 | 689.8 | 563 | 378.4 | 374.2 | 470.3
1264.1 | 1156.1 | 519.6 | 254.8 | 663.3 | 690.1 | 562.6 | 378.9 | 374.7 | 471.9
1265.1 | 1157.1 | 519.8 | 255.6 | 663.6 | 689.9 | 565.2 | 379.7 | 375.1 | 473.4
1266.1 | 1158.1 | 519.6 | 256.4 | 664.2 | 689.7 | 568.2 | 380.4 | 375.6 | 474.8
1267.1 | 1159.1 | 519.1 | 255.9 | 664.9 | 690.4 | 571.6 | 381.3 | 376.1 | 476.1
1268.1 | 1160.1 | 518.4 | 255.7 | 666 | 690.6 | 573.9 | 382.1 | 376.6 | 477.3
1269.1 | 1161.1 | 517.8 | 257.5 | 666.7 | 691.6 | 576.1 | 382.8 | 377.1 | 478.7
1270.1 | 1162.1 | 517.1 | 260.2 | 666.7 | 693 | 577.4 | 383.6 | 377.6 | 480
1271.1 | 1163.1 | 516.6 | 261.5 | 666.1 | 695.3 | 577.5 | 384.5 | 378.2 | 481.2
1272.1 | 1164.1 | 515.8 | 263.1 | 665.8 | 697.5 | 577.9 | 385.5 | 378.8 | 482.3
1273.1 | 1165.1 | 514.8 | 265.8 | 665.9 | 699.1 | 576.6 | 386.5 | 379.5 | 483.4
1274.1 | 1166.1 | 513.9 | 267.8 | 666.5 | 700.2 | 574.7 | 387.9 | 380.3 | 484.7
1275.1 | 1167.1 | 513.1 | 268.3 | 667.1 | 699.9 | 573.5 | 389.1 | 381.1 | 485.8
1276.1 | 1168.1 | 512.1 | 270.2 | 667.6 | 700.6 | 572 | 390.4 | 382 | 486.9
1277.1 | 1169.1 | 511.1 | 270.7 | 668.1 | 701.5 | 569.5 | 391.7 | 383 | 488.2
1278.1 | 1170.1 | 510 | 269.9 | 668.5 | 702 | 567 | 393 | 384.1 | 489.3
1279.1 | 1171.1 | 508.9 | 268.1 | 669 | 702.1 | 564.9 | 394.3 | 385.2 | 490.5
1280.1 | 1172.1 | 507.9 | 268.1 | 669.9 | 701.6 | 565.7 | 395.6 | 386.3 | 491.6
1281.1 | 1173.1 | 506.9 | 268.2 | 669.6 | 702 | 565.7 | 397 | 387.6 | 492.7
1282.1 | 1174.1 | 506 | 269.2 | 669.3 | 701.6 | 565.7 | 398.8 | 388.8 | 493.8
1283.1 | 1175.1 | 504.9 | 269.2 | 669.5 | 701 | 566.9 | 400.8 | 390.2 | 495
1284.1 | 1176.1 | 503.8 | 268.2 | 669.2 | 701.9 | 566.6 | 402.8 | 391.6 | 496
1285.1 | 1177.1 | 502.7 | 267.6 | 668.6 | 702.1 | 565.5 | 404.7 | 393 | 496.9
1286.1 | 1178.1 | 501.6 | 264.6 | 668.7 | 700.8 | 566.2 | 406.5 | 394.5 | 497.9
1287.1 | 1179.1 | 500.4 | 262.8 | 668.3 | 699.9 | 566.3 | 408.6 | 396 | 498.9
1288.1 | 1180.1 | 499.3 | 262.7 | 667.2 | 700.2 | 567.5 | 411 | 397.6 | 499.8
1289.1 | 1181.1 | 498.1 | 260.7 | 665.7 | 699.9 | 569 | 413.8 | 399.2 | 500.7
1290.1 | 1182.1 | 496.8 | 260.1 | 665.2 | 698.6 | 570.8 | 417.3 | 400.7 | 501.6
1291.1 | 1183.1 | 495.6 | 258.6 | 664.3 | 698.1 | 572.3 | 421 | 402.3 | 502.4
1292.1 | 1184.1 | 494.5 | 256.8 | 664.2 | 698.4 | 574.6 | 424.6 | 403.9 | 503.2
1293.1 | 1185.1 | 493.4 | 256.2 | 663.7 | 697.4 | 576.5 | 427.8 | 405.5 | 504
1294.1 | 1186.1 | 492.3 | 254 | 663 | 697 | 576.8 | 431.2 | 407 | 504.8
1295.1 | 1187.1 | 491.3 | 253 | 662.3 | 697.5 | 576.4 | 434.4 | 408.5 | 505.6
1296.1 | 1188.1 | 490.2 | 252.7 | 661.1 | 697.7 | 577.6 | 437.1 | 410 | 506.3
1297.1 | 1189.1 | 488.9 | 251.6 | 660.1 | 697.5 | 577.8 | 439.7 | 411.4 | 507
1298.1 | 1190.1 | 488 | 251.2 | 659.5 | 697.6 | 576.1 | 442 | 412.9 | 507.6
1299.1 | 1191.1 | 487 | 253.2 | 658.5 | 697.2 | 577.3 | 444.3 | 414.3 | 508.2
1300.1 | 1192.1 | 485.9 | 253 | 657.5 | 695.8 | 579.1 | 446.3 | 415.7 | 508.8
1301.1 | 1193.1 | 484.6 | 251.8 | 656.6 | 695.1 | 579.2 | 448.1 | 417 | 509.5
1302.1 | 1194.1 | 483.4 | 253 | 655.8 | 695.2 | 578.2 | 449.7 | 418.3 | 510.1
1303.1 | 1195.1 | 482.5 | 252.9 | 655.3 | 696.1 | 578.2 | 451.1 | 419.5 | 510.5
1304.1 | 1196.1 | 481.3 | 252.2 | 654.7 | 696.4 | 578.9 | 452.4 | 420.8 | 510.9
1305.1 | 1197.1 | 480.3 | 251.1 | 654.2 | 695.4 | 578.8 | 453.6 | 422 | 511.5
1306.1 | 1198.1 | 479.3 | 251.4 | 652.6 | 695.2 | 578 | 454.8 | 423.1 | 512
1307.1 | 1199.1 | 478.4 | 250.1 | 651.5 | 695 | 577.8 | 456.3 | 424.2 | 512.6
1308.1 | 1200.1 | 477.4 | 249 | 650.6 | 695.1 | 578.4 | 457.6 | 425.3 | 513.1
1309.1 | 1201.1 | 476.2 | 248.5 | 647.9 | 694.5 | 578.8 | 458.7 | 426.2 | 513.6
1310.1 | 1202.1 | 475.1 | 249 | 646.8 | 694.5 | 579.6 | 459.8 | 427.2 | 514
1311.1 | 1203.1 | 474.1 | 249.4 | 645.6 | 694.2 | 579.9 | 460.9 | 428 | 514.5
1312.1 | 1204.1 | 473.3 | 248.3 | 644.6 | 693.2 | 580.1 | 461.8 | 428.8 | 514.7
1313.1 | 1205.1 | 472.5 | 247.4 | 643.8 | 693.1 | 579.9 | 462.8 | 429.5 | 515
1314.1 | 1206.1 | 471.5 | 248.7 | 642.9 | 693.6 | 578.9 | 463.6 | 430.2 | 515.4
1315.1 | 1207.1 | 470.6 | 248.9 | 641.5 | 692.9 | 579.6 | 464.4 | 430.8 | 515.8
1316.1 | 1208.1 | 469.8 | 248 | 640.5 | 691.5 | 579.8 | 465 | 431.4 | 516.2
1317.1 | 1209.1 | 468.7 | 247.3 | 639.5 | 691.6 | 578.1 | 465.7 | 431.9 | 516.7
1318.1 | 1210.1 | 467.5 | 249.1 | 637.8 | 692.5 | 577.5 | 466.4 | 432.4 | 517
1319.1 | 1211.1 | 466.2 | 248.5 | 636.4 | 693.2 | 575.5 | 466.9 | 432.9 | 517.3
1320.1 | 1212.1 | 465 | 246.9 | 636.2 | 692.9 | 574.9 | 467.5 | 433.4 | 517.5
1321.1 | 1213.1 | 463.9 | 245.3 | 636.1 | 692.2 | 573.9 | 468 | 433.9 | 517.8
1322.1 | 1214.1 | 462.8 | 246.8 | 634.5 | 691.3 | 573.9 | 468.5 | 434.4 | 518.2
1323.1 | 1215.1 | 461.8 | 246 | 633.1 | 690.1 | 573.6 | 468.9 | 434.8 | 518.6
1324.1 | 1216.1 | 460.8 | 245.5 | 632.8 | 689.8 | 573.2 | 469.3 | 435.2 | 519.1
1325.1 | 1217.1 | 459.8 | 246.3 | 632.1 | 689.6 | 573.3 | 469.8 | 435.6 | 519.5
1326.1 | 1218.1 | 458.8 | 246 | 631.4 | 689.9 | 572.7 | 470.1 | 435.9 | 519.8
1327.1 | 1219.1 | 457.8 | 247.7 | 631.2 | 689.1 | 572.4 | 470.4 | 436.3 | 520
1328.1 | 1220.1 | 456.8 | 247.5 | 629.5 | 688.4 | 572.7 | 470.6 | 436.6 | 520.2
1329.1 | 1221.1 | 455.7 | 247 | 627.5 | 688.2 | 571.3 | 470.8 | 436.9 | 520.3
1330.1 | 1222.1 | 454.8 | 245.4 | 625 | 687.6 | 569 | 471 | 437.2 | 520.5
1331.1 | 1223.1 | 453.9 | 244.7 | 624.5 | 686.8 | 566.7 | 471 | 437.5 | 520.6
1332.1 | 1224.1 | 452.8 | 243.9 | 623.4 | 685.4 | 565 | 471.1 | 437.7 | 520.8
1333.1 | 1225.1 | 451.8 | 244.4 | 621.1 | 685.5 | 562.6 | 471.4 | 438 | 520.9
1334.1 | 1226.1 | 450.8 | 244 | 620 | 685.8 | 559.8 | 471.6 | 438.2 | 521
1335.1 | 1227.1 | 449.8 | 243.2 | 619.3 | 684.4 | 558 | 471.7 | 438.4 | 521
1336.1 | 1228.1 | 449 | 241.1 | 618.5 | 683.2 | 558.7 | 471.8 | 438.6 | 521
1337.1 | 1229.1 | 448 | 238.6 | 617.4 | 682.2 | 558.3 | 471.8 | 438.8 | 521
1338.1 | 1230.1 | 447 | 237.6 | 616.5 | 681.7 | 557.5 | 471.9 | 439 | 521
1339.1 | 1231.1 | 446.2 | 236 | 616.1 | 681.6 | 557.2 | 472 | 439.2 | 521.1
1340.1 | 1232.1 | 445.3 | 234.6 | 614.4 | 681 | 556.8 | 472 | 439.4 | 521.1
1341.1 | 1233.1 | 444.5 | 233.5 | 613.4 | 680.9 | 554.8 | 472.1 | 439.5 | 521
1342.1 | 1234.1 | 443.6 | 232.8 | 613.1 | 680.3 | 553.3 | 472 | 439.7 | 521.1
1343.1 | 1235.1 | 442.6 | 234.7 | 612.9 | 679.5 | 553.3 | 472 | 439.9 | 521.1
1344.1 | 1236.1 | 441.6 | 236.9 | 612.4 | 678.3 | 553.5 | 471.9 | 440.1 | 521.1
1345.1 | 1237.1 | 440.6 | 237.4 | 611.8 | 678.1 | 553.4 | 471.9 | 440.4 | 521.2
1346.1 | 1238.1 | 439.6 | 237.7 | 610.9 | 678 | 552.3 | 472 | 440.7 | 521.2
1347.1 | 1239.1 | 438.6 | 237.2 | 609.1 | 677.6 | 550.6 | 471.9 | 441 | 521.1
1348.1 | 1240.1 | 437.7 | 237.8 | 607.8 | 677.6 | 547.5 | 472 | 441.5 | 521.1
1349.1 | 1241.1 | 436.8 | 237.7 | 605.7 | 676.9 | 544.6 | 472 | 442 | 521.2
1350.1 | 1242.1 | 435.9 | 236.2 | 602.8 | 675.1 | 545.7 | 472.1 | 442.5 | 521.1
1351.1 | 1243.1 | 434.9 | 234.3 | 601.2 | 673.5 | 546.9 | 472.2 | 443.2 | 520.9
1352.1 | 1244.1 | 434.1 | 232.1 | 600.9 | 672.4 | 548 | 472.5 | 443.9 | 520.9
1353.1 | 1245.1 | 433.4 | 231 | 600.9 | 671.5 | 549.4 | 472.8 | 444.7 | 520.7
1354.1 | 1246.1 | 432.6 | 230.1 | 600.6 | 671 | 549.2 | 473.2 | 445.6 | 520.5
1355.1 | 1247.1 | 431.6 | 229.8 | 600 | 669.9 | 549.2 | 473.5 | 446.5 | 520.4
1356.1 | 1248.1 | 430.7 | 229.3 | 599.3 | 669.6 | 549 | 474 | 447.4 | 520.3
1357.1 | 1249.1 | 429.8 | 229.4 | 598.6 | 669.3 | 547.6 | 474.4 | 448.5 | 520.3
1358.1 | 1250.1 | 429.1 | 229.3 | 597.4 | 669.3 | 546.6 | 474.8 | 449.7 | 520.1
1359.1 | 1251.1 | 428.2 | 228.7 | 596.5 | 669.5 | 546.4 | 475.2 | 450.9 | 519.9
1360.1 | 1252.1 | 427.4 | 228.7 | 595.7 | 668.8 | 547.7 | 475.6 | 452.3 | 519.8
1361.1 | 1253.1 | 426.6 | 227.3 | 595 | 668.6 | 547.8 | 476 | 453.7 | 519.8
1362.1 | 1254.1 | 425.8 | 226.2 | 593.4 | 668.4 | 546.2 | 476.4 | 455.2 | 519.7
1363.1 | 1255.1 | 425 | 224.4 | 592.5 | 667.5 | 545.9 | 476.7 | 456.8 | 519.7
1364.1 | 1256.1 | 424.1 | 224.1 | 591.5 | 667.1 | 544.9 | 477 | 458.5 | 519.6
1365.1 | 1257.1 | 423.2 | 224.8 | 590.6 | 666.6 | 544.7 | 477.2 | 460.1 | 519.4
1366.1 | 1258.1 | 422.2 | 227.5 | 589.6 | 666 | 544.1 | 477.5 | 461.9 | 519.4
1367.1 | 1259.1 | 421.4 | 227.2 | 588 | 665.6 | 542.6 | 477.9 | 463.5 | 519.3
1368.1 | 1260.1 | 420.4 | 226.5 | 587.1 | 666 | 542.6 | 478.2 | 465.1 | 519.2
1369.1 | 1261.1 | 419.5 | 225.8 | 585.5 | 666.2 | 538 | 478.4 | 466.5 | 519.1
1370.1 | 1262.1 | 418.7 | 224.9 | 585.4 | 665.8 | 531.2 | 478.7 | 468 | 518.9
1371.1 | 1263.1 | 417.9 | 224.9 | 584.8 | 665.1 | 526.2 | 479 | 469.2 | 518.8
1372.1 | 1264.1 | 417.1 | 224.9 | 584 | 664.3 | 521.8 | 479.3 | 470.3 | 518.5
1373.1 | 1265.1 | 416.4 | 226.1 | 584 | 663.6 | 516.3 | 479.7 | 471.3 | 518.4
1374.1 | 1266.1 | 415.6 | 225.5 | 583.4 | 663.1 | 513.1 | 480.1 | 472.1 | 518.4
1375.1 | 1267.1 | 414.8 | 227.1 | 582.6 | 662 | 512.7 | 480.4 | 472.8 | 518.5
1376.1 | 1268.1 | 414.1 | 226.9 | 581.5 | 661.2 | 510.5 | 480.8 | 473.2 | 518.5
1377.1 | 1269.1 | 413.2 | 229.6 | 580.1 | 660.3 | 509.2 | 481.2 | 473.3 | 518.3
1378.1 | 1270.1 | 412.4 | 230.2 | 579 | 660.1 | 510.6 | 481.6 | 473.1 | 518.1
1379.1 | 1271.1 | 411.7 | 228.7 | 578.7 | 660.7 | 510.3 | 482 | 472.8 | 517.9
1380.1 | 1272.1 | 411 | 226.9 | 577.8 | 660.4 | 511.3 | 482.5 | 472.3 | 517.7
1381.1 | 1273.1 | 410.3 | 227.3 | 577.5 | 659.9 | 513.2 | 482.7 | 471.9 | 517.7
1382.1 | 1274.1 | 409.5 | 226.8 | 575.8 | 659.3 | 513.6 | 483.1 | 471.5 | 517.7
1383.1 | 1275.1 | 408.7 | 227.7 | 575.2 | 658.8 | 513.1 | 483.6 | 471 | 517.7
1384.1 | 1276.1 | 408 | 228.4 | 574.5 | 657.9 | 512.4 | 484.1 | 470.6 | 517.6
1385.1 | 1277.1 | 407.1 | 228.2 | 574 | 658.1 | 511.1 | 484.7 | 470.2 | 517.6
1386.1 | 1278.1 | 406.3 | 226.7 | 573.5 | 656.8 | 507.7 | 485.3 | 469.9 | 517.6
1387.1 | 1279.1 | 405.5 | 224.9 | 571.1 | 654.3 | 504.1 | 486 | 469.4 | 517.6
1388.1 | 1280.1 | 404.7 | 223.8 | 570.4 | 652.2 | 501.9 | 486.6 | 468.9 | 517.6
1389.1 | 1281.1 | 404 | 223.8 | 569.9 | 651.1 | 502.1 | 487.2 | 468.3 | 517.6
1390.1 | 1282.1 | 403.3 | 221.8 | 569.9 | 650.2 | 498.9 | 487.8 | 467.8 | 517.4
1391.1 | 1283.1 | 402.7 | 219.3 | 569.7 | 648.8 | 494.8 | 488.3 | 467.3 | 517.2
1392.1 | 1284.1 | 401.8 | 218.2 | 569.7 | 648 | 489 | 488.9 | 466.7 | 517
1393.1 | 1285.1 | 400.9 | 217.8 | 569.4 | 647.9 | 490.7 | 489.4 | 466.2 | 516.9
1394.1 | 1286.1 | 400.2 | 216.8 | 568.9 | 647.8 | 491.5 | 490 | 465.7 | 516.6
1395.1 | 1287.1 | 399.6 | 216.5 | 568.6 | 647.6 | 491.2 | 490.7 | 465.1 | 516.3
1396.1 | 1288.1 | 398.8 | 219.2 | 568 | 647.5 | 488.9 | 491.3 | 464.5 | 516.1
1397.1 | 1289.1 | 398.1 | 220.2 | 567.9 | 647.5 | 487 | 491.8 | 464 | 515.9
1398.1 | 1290.1 | 397.3 | 219.4 | 567.2 | 646.4 | 482.8 | 492.4 | 463.4 | 515.7
1399.1 | 1291.1 | 396.6 | 219.7 | 566.7 | 645.8 | 479.5 | 492.8 | 462.8 | 515.4
1400.1 | 1292.1 | 395.9 | 219.7 | 566.1 | 645.1 | 475.5 | 493.1 | 462.3 | 515.3
1401.1 | 1293.1 | 394.9 | 218.7 | 565.3 | 644 | 474 | 493.4 | 461.7 | 515.1
1402.1 | 1294.1 | 394 | 218.1 | 564.3 | 643.4 | 475.4 | 493.5 | 461.1 | 514.8
1403.1 | 1295.1 | 392.9 | 216.8 | 563.3 | 642.7 | 474.2 | 493.8 | 460.4 | 514.4
1404.1 | 1296.1 | 392 | 217.9 | 562.6 | 641.9 | 474.3 | 494 | 459.8 | 514.1
1405.1 | 1297.1 | 391.1 | 219.4 | 562.1 | 641.6 | 471.6 | 494.3 | 459.1 | 514
1406.1 | 1298.1 | 390.4 | 218.7 | 561 | 639.9 | 471.6 | 494.8 | 458.4 | 513.9
1407.1 | 1299.1 | 389.8 | 217.3 | 560.1 | 620.3 | 473.8 | 495.1 | 457.6 | 513.7
1408.1 | 1300.1 | 389.1 | 215.8 | 559.4 | 595.4 | 476.5 | 495.3 | 456.9 | 513.5
1409.1 | 1301.1 | 388.4 | 214.8 | 558.3 | 576.4 | 478.1 | 495.5 | 456.2 | 513.3
1410.1 | 1302.1 | 387.9 | 215.7 | 557.8 | 558.5 | 478.2 | 495.5 | 455.5 | 513
1411.1 | 1303.1 | 387.3 | 215.3 | 557.2 | 544.3 | 478.2 | 495.6 | 454.7 | 512.8
1412.1 | 1304.1 | 386.6 | 216.6 | 556.2 | 535.1 | 478.7 | 495.8 | 454 | 512.6
1413.1 | 1305.1 | 386.1 | 216.8 | 555.6 | 527.9 | 479.2 | 496 | 453.2 | 512.3
1414.1 | 1306.1 | 385.4 | 217.1 | 555.2 | 522.1 | 479.3 | 496.2 | 452.5 | 512
1415.1 | 1307.1 | 384.8 | 215.9 | 554.4 | 519.1 | 480.7 | 496.4 | 451.7 | 511.8
1416.1 | 1308.1 | 384 | 217.1 | 553.6 | 516 | 481.4 | 496.6 | 450.9 | 511.5
1417.1 | 1309.1 | 383.3 | 217.6 | 552.8 | 510.6 | 480.5 | 496.8 | 450.1 | 511.2
1418.1 | 1310.1 | 382.7 | 218.7 | 552.2 | 507 | 478.5 | 497.1 | 449.4 | 511
1419.1 | 1311.1 | 382 | 221 | 551.4 | 505.5 | 476.9 | 497.4 | 448.6 | 510.7
1420.1 | 1312.1 | 381.3 | 221.5 | 550.9 | 500.1 | 474.8 | 497.7 | 447.8 | 510.6
1421.1 | 1313.1 | 380.9 | 222.4 | 550.4 | 496.1 | 472.6 | 497.9 | 447 | 510.5
1422.1 | 1314.1 | 380.2 | 222 | 550 | 491.8 | 470.3 | 498.2 | 446.2 | 510.5
1423.1 | 1315.1 | 379.5 | 221.2 | 549.1 | 487.8 | 469.5 | 498.4 | 445.4 | 510.4
1424.1 | 1316.1 | 378.8 | 218.4 | 548.5 | 481.9 | 465.7 | 498.6 | 444.7 | 510.3
1425.1 | 1317.1 | 378 | 216.9 | 548.3 | 477.7 | 463.2 | 498.8 | 444 | 510.2
1426.1 | 1318.1 | 377.4 | 216.8 | 548 | 475.7 | 462.2 | 498.9 | 443.3 | 510.1
1427.1 | 1319.1 | 376.8 | 216.7 | 547.6 | 474.6 | 460.2 | 499.1 | 442.5 | 510.1
1428.1 | 1320.1 | 376.1 | 214.3 | 546.5 | 471.9 | 458.7 | 499.3 | 441.8 | 510
1429.1 | 1321.1 | 375.5 | 212.5 | 545.5 | 468.8 | 458 | 499.5 | 441.1 | 509.8
1430.1 | 1322.1 | 374.9 | 211.9 | 544.7 | 466.9 | 459.2 | 499.8 | 440.5 | 509.7
1431.1 | 1323.1 | 374.2 | 214.6 | 544.2 | 465.9 | 459.1 | 500 | 439.8 | 509.5
1432.1 | 1324.1 | 373.5 | 218 | 543.7 | 465.3 | 457.8 | 500.3 | 439.1 | 509.3
1433.1 | 1325.1 | 372.8 | 219.3 | 542.9 | 463.4 | 457.1 | 500.7 | 438.4 | 509.1
1434.1 | 1326.1 | 372.2 | 217.7 | 542.2 | 461.5 | 457.4 | 500.9 | 437.7 | 509
1435.1 | 1327.1 | 371.6 | 218.7 | 542 | 458.9 | 456.5 | 501.2 | 437.1 | 508.9
1436.1 | 1328.1 | 371 | 217.7 | 541.7 | 456.9 | 455.7 | 501.4 | 436.4 | 508.7
1437.1 | 1329.1 | 370.4 | 216.8 | 540.9 | 453.7 | 455.2 | 501.7 | 435.8 | 508.5
1438.1 | 1330.1 | 369.8 | 215.2 | 540.4 | 451.4 | 454.6 | 502 | 435.1 | 508.3
1439.1 | 1331.1 | 369.1 | 214.4 | 540.2 | 446.7 | 454.6 | 502.3 | 434.5 | 508.1
1440.1 | 1332.1 | 368.4 | 216.4 | 539.3 | 443.9 | 455.6 | 502.7 | 433.9 | 507.9
1441.1 | 1333.1 | 367.7 | 216.9 | 538.2 | 443 | 454.5 | 503.1 | 433.2 | 507.7
1442.1 | 1334.1 | 367.2 | 215.9 | 537.9 | 440.4 | 452.9 | 503.5 | 432.6 | 507.5
1443.1 | 1335.1 | 366.6 | 214.4 | 537.8 | 442 | 451.4 | 504 | 432 | 507.3
1444.1 | 1336.1 | 366 | 214.5 | 537 | 438.7 | 450.2 | 504.5 | 431.4 | 507.3
1445.1 | 1337.1 | 365.5 | 216 | 536.6 | 436.2 | 448.5 | 505 | 430.8 | 507.2
1446.1 | 1338.1 | 364.9 | 220.5 | 536.2 | 431.9 | 447.9 | 505.4 | 430.1 | 507.2
1447.1 | 1339.1 | 364.3 | 223 | 535.1 | 428.8 | 448.3 | 506.1 | 429.5 | 507.1
1448.1 | 1340.1 | 363.8 | 222.4 | 535.1 | 426.7 | 445.7 | 506.4 | 428.9 | 507
1449.1 | 1341.1 | 363.2 | 221.3 | 534.8 | 423.9 | 441.7 | 506.8 | 428.3 | 506.9
1450.1 | 1342.1 | 362.6 | 221.4 | 534.6 | 422.4 | 439.7 | 507.3 | 427.7 | 506.8
1451.1 | 1343.1 | 362.1 | 221.8 | 533.9 | 419.5 | 437.8 | 508 | 427.1 | 506.6
1452.1 | 1344.1 | 361.6 | 224 | 533.4 | 417.9 | 436 | 508.4 | 426.6 | 506.4
1453.1 | 1345.1 | 361.1 | 226.4 | 532.8 | 415.3 | 435.2 | 508.7 | 426 | 506.2
1454.1 | 1346.1 | 360.6 | 223.5 | 531.9 | 411.9 | 434.4 | 509.2 | 425.4 | 505.9
1455.1 | 1347.1 | 360 | 224.4 | 531.3 | 409.8 | 435.3 | 509.7 | 424.8 | 505.7
1456.1 | 1348.1 | 359.4 | 225.9 | 531.2 | 408.3 | 437 | 510.2 | 424.1 | 505.6
1457.1 | 1349.1 | 358.7 | 224.3 | 530.7 | 407.3 | 437.4 | 510.7 | 423.5 | 505.5
1458.1 | 1350.1 | 358 | 222.5 | 529.8 | 407.5 | 437.3 | 511.3 | 422.9 | 505.3
1459.1 | 1351.1 | 357.6 | 222.5 | 529.7 | 405.2 | 437.4 | 511.7 | 422.3 | 505.2
1460.1 | 1352.1 | 356.9 | 223.2 | 529.6 | 403.1 | 436.5 | 512.1 | 421.7 | 505.1
1461.1 | 1353.1 | 356.5 | 220.4 | 529.3 | 402.1 | 436.8 | 512.7 | 421.1 | 505
1462.1 | 1354.1 | 355.9 | 219.9 | 528.8 | 400.8 | 434.3 | 513.4 | 420.5 | 504.9
1463.1 | 1355.1 | 355.3 | 216.7 | 528.8 | 397.8 | 431.8 | 513.9 | 419.9 | 504.8
1464.1 | 1356.1 | 354.7 | 216 | 528.7 | 397.8 | 430.2 | 514.5 | 419.3 | 504.8
1465.1 | 1357.1 | 354.2 | 215 | 528.7 | 393.5 | 428.5 | 515.2 | 418.8 | 504.7
1466.1 | 1358.1 | 353.8 | 216.1 | 528.9 | 388.6 | 426.9 | 515.8 | 418.2 | 504.6
1467.1 | 1359.1 | 353.2 | 215 | 529.1 | 386.5 | 425.6 | 516.4 | 417.6 | 504.6
1468.1 | 1360.1 | 352.6 | 214.6 | 529.4 | 382 | 424.1 | 517.1 | 417.1 | 504.5
1469.1 | 1361.1 | 351.9 | 214.2 | 530 | 379.9 | 422.9 | 517.8 | 416.5 | 504.5
1470.1 | 1362.1 | 351.3 | 214.3 | 530.4 | 377.5 | 422 | 518.4 | 415.9 | 504.4
1471.1 | 1363.1 | 350.8 | 214.4 | 530.2 | 373.2 | 422.2 | 519 | 415.4 | 504.4
1472.1 | 1364.1 | 350.4 | 212.7 | 529.4 | 369.1 | 420.2 | 519.6 | 414.8 | 504.3
1473.1 | 1365.1 | 349.9 | 210.1 | 528.7 | 366.7 | 419.5 | 520.1 | 414.3 | 504.3
1474.1 | 1366.1 | 349.3 | 209.8 | 528.7 | 368.5 | 421.3 | 520.5 | 413.7 | 504.4
1475.1 | 1367.1 | 348.9 | 209.7 | 528.2 | 367.9 | 424.7 | 520.8 | 413.1 | 504.2
1476.1 | 1368.1 | 348.4 | 210.5 | 527.8 | 370.9 | 429.7 | 521.1 | 412.6 | 504.1
1477.1 | 1369.1 | 347.8 | 209.3 | 528 | 371.8 | 431 | 521.3 | 412 | 504
1478.1 | 1370.1 | 347.2 | 209.1 | 528.5 | 371.1 | 429.3 | 521.6 | 411.5 | 503.9
1479.1 | 1371.1 | 346.7 | 212.3 | 528.8 | 371.1 | 428.8 | 521.8 | 410.9 | 503.9
1480.1 | 1372.1 | 346.2 | 212.6 | 529 | 370.6 | 428.8 | 521.9 | 410.4 | 503.9
1481.1 | 1373.1 | 345.7 | 212.3 | 529.2 | 368.9 | 428.6 | 521.9 | 409.9 | 503.9
1482.1 | 1374.1 | 345.2 | 214.9 | 529 | 366.6 | 427.4 | 521.9 | 409.4 | 503.8
1483.1 | 1375.1 | 345 | 212.8 | 528.9 | 366.5 | 425.3 | 522.1 | 408.9 | 503.8
1484.1 | 1376.1 | 344.7 | 211.2 | 529.2 | 363.8 | 426.3 | 522.2 | 408.3 | 503.7
1485.1 | 1377.1 | 344.1 | 213.8 | 529.6 | 360.6 | 424.2 | 522.1 | 407.9 | 503.8
1486.1 | 1378.1 | 343.6 | 211.1 | 529.4 | 358.9 | 423.2 | 522.2 | 407.4 | 503.7
1487.1 | 1379.1 | 343.3 | 209.3 | 529.1 | 358.1 | 422.9 | 522.1 | 406.9 | 503.8
1488.1 | 1380.1 | 342.9 | 210.5 | 529 | 356.2 | 423.1 | 522 | 406.4 | 503.8
1489.1 | 1381.1 | 342.3 | 212.6 | 530.2 | 355.7 | 425 | 521.9 | 405.9 | 503.8
1490.1 | 1382.1 | 341.9 | 213.7 | 531 | 355 | 424.6 | 521.8 | 405.5 | 503.7
1491.1 | 1383.1 | 341.4 | 211.7 | 531.1 | 354.6 | 424.1 | 521.6 | 405 | 503.5
1492.1 | 1384.1 | 340.8 | 209.6 | 530.8 | 353.6 | 425.2 | 521.5 | 404.6 | 503.3
1493.1 | 1385.1 | 340.4 | 207.3 | 530.5 | 353.3 | 429 | 521.4 | 404.1 | 503.1
1494.1 | 1386.1 | 339.9 | 207.2 | 530.7 | 352.5 | 428.2 | 521.3 | 403.7 | 502.9
1495.1 | 1387.1 | 339.4 | 207.9 | 530.7 | 351.5 | 425.5 | 521.1 | 403.2 | 502.7
1496.1 | 1388.1 | 339 | 209 | 530.4 | 349.4 | 423.4 | 520.9 | 402.8 | 502.6
1497.1 | 1389.1 | 338.5 | 208.4 | 529.5 | 347.4 | 420.6 | 520.7 | 402.3 | 502.3
1498.1 | 1390.1 | 338 | 205.2 | 529.1 | 347.4 | 418.1 | 520.4 | 401.9 | 502.2
1499.1 | 1391.1 | 337.6 | 202.6 | 529.3 | 346.5 | 417.6 | 520.2 | 401.4 | 502.1
1500.1 | 1392.1 | 337.2 | 199.3 | 529.3 | 346 | 417.5 | 520 | 401 | 502.1
1501.1 | 1393.1 | 336.7 | 197.1 | 529.6 | 348.3 | 415.7 | 519.8 | 400.5 | 501.9
1502.1 | 1394.1 | 336.3 | 195.7 | 530.8 | 351 | 412.9 | 519.5 | 400.1 | 501.9
1503.1 | 1395.1 | 335.9 | 198.1 | 530.8 | 351.3 | 411.3 | 519.3 | 399.6 | 501.8
1504.1 | 1396.1 | 335.5 | 196.8 | 529.8 | 348.4 | 409.2 | 519.1 | 399.2 | 501.7
1505.1 | 1397.1 | 335 | 195.3 | 529.5 | 346 | 407.2 | 518.8 | 398.8 | 501.5
1506.1 | 1398.1 | 334.6 | 193.8 | 529.4 | 343.1 | 404.5 | 518.5 | 398.4 | 501.3
1507.1 | 1399.1 | 334.1 | 194 | 529.1 | 341.1 | 403.4 | 518.3 | 398 | 501.3
1508.1 | 1400.1 | 333.7 | 194.9 | 528.1 | 340.4 | 402 | 518 | 397.6 | 501.3
1509.1 | 1401.1 | 333.2 | 196.9 | 527.2 | 339.5 | 401.2 | 517.7 | 397.2 | 501.3
1510.1 | 1402.1 | 332.7 | 194.4 | 526.6 | 337.5 | 399.9 | 517.4 | 396.7 | 501.2
1511.1 | 1403.1 | 332.2 | 199.1 | 526.6 | 335.9 | 400.2 | 517.2 | 396.3 | 501.1
1512.1 | 1404.1 | 331.6 | 200.1 | 525.6 | 334.9 | 400.2 | 516.9 | 395.9 | 500.9
1513.1 | 1405.1 | 331.1 | 197.3 | 525.3 | 335.1 | 398.8 | 516.6 | 395.5 | 500.7
1514.1 | 1406.1 | 330.7 | 198.7 | 525.2 | 335.7 | 397.6 | 516.4 | 395.1 | 500.6
1515.1 | 1407.1 | 330.3 | 196.8 | 524.1 | 334.1 | 396.8 | 516.1 | 394.7 | 500.6
1516.1 | 1408.1 | 329.8 | 198.5 | 523.6 | 334.5 | 397.2 | 515.8 | 394.3 | 500.5
1517.1 | 1409.1 | 329.5 | 198.5 | 523.3 | 335.5 | 399.1 | 515.5 | 393.9 | 500.2
1518.1 | 1410.1 | 329.2 | 197.6 | 522.5 | 335.4 | 401.4 | 515 | 393.5 | 500.2
1519.1 | 1411.1 | 328.8 | 198.3 | 521.4 | 335.9 | 404.6 | 514.6 | 393.1 | 500.3
1520.1 | 1412.1 | 328.3 | 199.2 | 520.7 | 338.6 | 406.7 | 514.2 | 392.8 | 500.2
1521.1 | 1413.1 | 327.9 | 198.9 | 520 | 342.2 | 407.1 | 513.7 | 392.4 | 500.2
1522.1 | 1414.1 | 327.4 | 199.3 | 519.5 | 346.2 | 408.9 | 513.2 | 392 | 500.1
1523.1 | 1415.1 | 327.1 | 201.2 | 518.8 | 349.9 | 411.2 | 512.7 | 391.6 | 500.1
1524.1 | 1416.1 | 326.7 | 204.1 | 518 | 350.3 | 414.5 | 512.3 | 391.2 | 500
1525.1 | 1417.1 | 326.3 | 205.6 | 517.4 | 349.1 | 417.4 | 511.7 | 390.7 | 500.1
1526.1 | 1418.1 | 325.8 | 206.4 | 516.5 | 351 | 418.6 | 511.1 | 390.3 | 500
1527.1 | 1419.1 | 325.4 | 206.1 | 516.2 | 352 | 418.1 | 510.6 | 389.8 | 499.9
1528.1 | 1420.1 | 324.8 | 204.9 | 516.1 | 350.7 | 417.9 | 510.3 | 389.4 | 499.9
1529.1 | 1421.1 | 324.3 | 205.7 | 515.5 | 349.8 | 416.4 | 510.2 | 388.9 | 499.8
1530.1 | 1422.1 | 323.9 | 204.3 | 514.4 | 346.9 | 413.8 | 510.2 | 388.5 | 499.8
1531.1 | 1423.1 | 323.5 | 201.2 | 513.5 | 344.2 | 411.7 | 510.3 | 388.2 | 499.8
1532.1 | 1424.1 | 322.9 | 198.6 | 513.2 | 343 | 410 | 510.3 | 387.8 | 499.8
1533.1 | 1425.1 | 322.3 | 197.5 | 512.9 | 341.6 | 407.3 | 510.2 | 387.4 | 499.7
1534.1 | 1426.1 | 321.9 | 197.1 | 513.2 | 338.7 | 406 | 510 | 387.1 | 499.5
1535.1 | 1427.1 | 321.5 | 193.9 | 513.3 | 336.5 | 404.4 | 509.9 | 386.7 | 499.2
1536.1 | 1428.1 | 321 | 190.8 | 513.6 | 334.6 | 401 | 509.8 | 386.3 | 499
1537.1 | 1429.1 | 320.5 | 188.4 | 513.7 | 332.6 | 398.4 | 509.5 | 385.9 | 498.8
1538.1 | 1430.1 | 319.8 | 188.3 | 513.1 | 330.4 | 397.8 | 509.3 | 385.5 | 498.6
1539.1 | 1431.1 | 319.3 | 189.3 | 512.3 | 331.6 | 398.6 | 509.1 | 385.2 | 498.4
1540.1 | 1432.1 | 318.9 | 188.7 | 512.1 | 332.4 | 399 | 508.9 | 384.8 | 498.1
1541.1 | 1433.1 | 318.5 | 186.5 | 512 | 329.6 | 400.3 | 508.6 | 384.4 | 497.8
1542.1 | 1434.1 | 318.1 | 184.5 | 511.3 | 328.3 | 399.9 | 508.3 | 384.1 | 497.5
1543.1 | 1435.1 | 317.6 | 184.7 | 509.8 | 327.7 | 399.5 | 508 | 383.7 | 497.3
1544.1 | 1436.1 | 317.2 | 185.4 | 508.4 | 327.6 | 398.5 | 507.6 | 383.4 | 497
1545.1 | 1437.1 | 316.8 | 185.4 | 508 | 326.9 | 397.5 | 507.2 | 383 | 496.7
1546.1 | 1438.1 | 316.3 | 184.6 | 507.2 | 325.6 | 398.1 | 506.9 | 382.7 | 496.5
1547.1 | 1439.1 | 316 | 184.2 | 507.1 | 324.1 | 398.6 | 506.6 | 382.3 | 496.4
1548.1 | 1440.1 | 315.5 | 183.1 | 506.7 | 323.1 | 398.1 | 506.2 | 382 | 496.1
1549.1 | 1441.1 | 315 | 183.5 | 506.1 | 323.2 | 397.3 | 505.9 | 381.6 | 495.9
1550.1 | 1442.1 | 314.6 | 182.1 | 505.1 | 321.5 | 396.2 | 505.4 | 381.3 | 495.7
1551.1 | 1443.1 | 314.1 | 180.4 | 503.6 | 319.5 | 395 | 504.9 | 380.9 | 495.5
1552.1 | 1444.1 | 313.6 | 179.7 | 502.8 | 317.6 | 394.2 | 504.5 | 380.6 | 495.2
1553.1 | 1445.1 | 313.1 | 178.5 | 502.4 | 315.5 | 392.6 | 504.2 | 380.2 | 495
1554.1 | 1446.1 | 312.6 | 177.1 | 501.9 | 313.6 | 391.4 | 503.8 | 379.9 | 494.8
1555.1 | 1447.1 | 312.3 | 176.4 | 501.5 | 311.9 | 390.1 | 503.3 | 379.5 | 494.5
1556.1 | 1448.1 | 311.8 | 177.7 | 501.3 | 311.7 | 388.1 | 502.9 | 379.1 | 494.2
1557.1 | 1449.1 | 311.4 | 178 | 500.7 | 311.4 | 386.1 | 502.5 | 378.8 | 493.9
1558.1 | 1450.1 | 310.9 | 178.7 | 500.3 | 309.8 | 382.7 | 501.9 | 378.4 | 493.6
1559.1 | 1451.1 | 310.3 | 178.6 | 500 | 309.7 | 380.7 | 501.4 | 378.1 | 493.3
1560.1 | 1452.1 | 309.9 | 177.2 | 498.7 | 309.3 | 380.1 | 500.9 | 377.7 | 492.9
1561.1 | 1453.1 | 309.5 | 175.9 | 497.5 | 309.7 | 380.4 | 500.2 | 377.4 | 492.4
1562.1 | 1454.1 | 309.1 | 175 | 496.9 | 311.7 | 381.1 | 499.8 | 377.1 | 492
1563.1 | 1455.1 | 308.7 | 174.6 | 495.9 | 312.2 | 381.5 | 499.1 | 376.7 | 491.7
1564.1 | 1456.1 | 308.4 | 173.2 | 494.9 | 312.1 | 381.1 | 498.5 | 376.3 | 491.5
1565.1 | 1457.1 | 308 | 173.2 | 493.6 | 311.5 | 381.6 | 497.9 | 376 | 491.2
1566.1 | 1458.1 | 307.5 | 173 | 492.5 | 311 | 382.3 | 497.4 | 375.7 | 490.9
1567.1 | 1459.1 | 307.1 | 170.7 | 491.4 | 310.5 | 383.9 | 496.9 | 375.3 | 490.6
1568.1 | 1460.1 | 306.6 | 170.4 | 490.6 | 309.6 | 384 | 496.3 | 375 | 490.4
1569.1 | 1461.1 | 306.3 | 169.4 | 490.1 | 307.5 | 382.9 | 495.7 | 374.7 | 490.1
1570.1 | 1462.1 | 305.9 | 168.6 | 489.6 | 305.6 | 381.9 | 495.1 | 374.4 | 489.9
1571.1 | 1463.1 | 305.4 | 168.2 | 488.7 | 304.2 | 379.8 | 494.6 | 374.1 | 489.6
1572.1 | 1464.1 | 305 | 166.9 | 485.3 | 302.5 | 377.5 | 494.1 | 373.8 | 489.4
1573.1 | 1465.1 | 304.6 | 170.2 | 478.8 | 299.7 | 375.1 | 493.6 | 373.5 | 489.2
1574.1 | 1466.1 | 304.2 | 171.5 | 473.1 | 297.3 | 374.1 | 492.9 | 373.2 | 488.9
1575.1 | 1467.1 | 303.9 | 175.8 | 467 | 296.5 | 373.2 | 492.2 | 372.9 | 488.7
1576.1 | 1468.1 | 303.5 | 180.3 | 461.4 | 295 | 371.3 | 491.6 | 372.6 | 488.5
1577.1 | 1469.1 | 303.1 | 183.7 | 455.8 | 296 | 369.4 | 491 | 372.3 | 488.1
1578.1 | 1470.1 | 302.7 | 187.4 | 450.6 | 295.1 | 367.7 | 490.4 | 372.1 | 487.6
1579.1 | 1471.1 | 302.3 | 190.1 | 445.8 | 294.3 | 365.8 | 489.8 | 371.8 | 487.2
1580.1 | 1472.1 | 301.9 | 192 | 441.6 | 293 | 364.1 | 489.1 | 371.5 | 486.8
1581.1 | 1473.1 | 301.5 | 188.6 | 438.2 | 290.4 | 362.5 | 488.3 | 371.3 | 486.3
1582.1 | 1474.1 | 301 | 184.9 | 434.4 | 287.7 | 360.2 | 487.5 | 371 | 485.7
1583.1 | 1475.1 | 300.7 | 185.7 | 431.7 | 286.5 | 358.5 | 486.6 | 370.7 | 485.3
1584.1 | 1476.1 | 300.1 | 186.6 | 429 | 285.9 | 357.4 | 485.8 | 370.5 | 485
1585.1 | 1477.1 | 299.5 | 191.2 | 426.6 | 285.6 | 355.6 | 485 | 370.2 | 484.6
1586.1 | 1478.1 | 299.1 | 193.7 | 424.3 | 284.6 | 353.7 | 484.1 | 369.9 | 484.2
1587.1 | 1479.1 | 298.7 | 190.6 | 421.3 | 283.8 | 352.9 | 483.2 | 369.7 | 483.9
1588.1 | 1480.1 | 298.2 | 187.3 | 419.4 | 282.8 | 353.5 | 482.1 | 369.4 | 483.6
1589.1 | 1481.1 | 297.8 | 185.2 | 418 | 281.2 | 352.9 | 481.1 | 369.2 | 483.2
1590.1 | 1482.1 | 297.3 | 182.2 | 416.9 | 280.1 | 351.9 | 480 | 368.9 | 482.9
1591.1 | 1483.1 | 296.8 | 178.8 | 413.7 | 279.1 | 352.3 | 479 | 368.6 | 482.6
1592.1 | 1484.1 | 296.4 | 176.6 | 410.3 | 278.7 | 352.8 | 477.9 | 368.3 | 482.3
1593.1 | 1485.1 | 295.9 | 175.6 | 406.2 | 279 | 353.8 | 476.7 | 368.1 | 482
1594.1 | 1486.1 | 295.5 | 174.9 | 403.3 | 279.1 | 354.2 | 475.4 | 367.8 | 481.8
1595.1 | 1487.1 | 295.1 | 174.6 | 401.6 | 280 | 354.9 | 474.3 | 367.5 | 481.4
1596.1 | 1488.1 | 294.7 | 173 | 399.9 | 281.2 | 356.8 | 472.9 | 367.2 | 481.1
1597.1 | 1489.1 | 294.2 | 171.1 | 398.7 | 281.6 | 358.3 | 471.3 | 367 | 480.9
1598.1 | 1490.1 | 293.8 | 168.9 | 397.4 | 282.9 | 359.1 | 469.9 | 366.7 | 480.7
1599.1 | 1491.1 | 293.4 | 168.1 | 395.5 | 285.9 | 359.7 | 468.6 | 366.4 | 480.5
1600.1 | 1492.1 | 292.9 | 167.8 | 394.8 | 287.1 | 360.2 | 467.3 | 366.1 | 480.3
1601.1 | 1493.1 | 292.5 | 166.4 | 393.2 | 287.3 | 360.1 | 466.2 | 365.7 | 480.1
1602.1 | 1494.1 | 292.1 | 166.5 | 391.9 | 287 | 360 | 465.1 | 365.4 | 479.9
1603.1 | 1495.1 | 291.8 | 166.1 | 390.7 | 286.3 | 360.1 | 464.1 | 365.1 | 479.7
1604.1 | 1496.1 | 291.4 | 164.4 | 389.7 | 285 | 359.8 | 463.1 | 364.8 | 479.4
1605.1 | 1497.1 | 291 | 163.3 | 388.7 | 282.4 | 360.1 | 462.1 | 364.5 | 479.1
1606.1 | 1498.1 | 290.6 | 162.2 | 387.6 | 281.6 | 360 | 461 | 364.2 | 479
1607.1 | 1499.1 | 290.3 | 162.5 | 386.9 | 280.3 | 359 | 459.8 | 363.9 | 478.8
1608.1 | 1500.1 | 289.9 | 161.1 | 386.8 | 278 | 358.3 | 458.6 | 363.6 | 478.6
1609.1 | 1501.1 | 289.5 | 159.3 | 386.4 | 276.6 | 357.6 | 457.3 | 363.3 | 478.3
1610.1 | 1502.1 | 289 | 158.4 | 385.7 | 274.6 | 355.5 | 456 | 363 | 478
1611.1 | 1503.1 | 288.5 | 158.1 | 385 | 272.9 | 353.5 | 454.8 | 362.7 | 477.8
1612.1 | 1504.1 | 288 | 156.8 | 383.3 | 271.8 | 353.5 | 453.5 | 362.4 | 477.5
1613.1 | 1505.1 | 287.6 | 155.9 | 382.2 | 271.2 | 353.8 | 452.1 | 362.1 | 477.3
1614.1 | 1506.1 | 287.3 | 155.6 | 381.3 | 270.6 | 353.9 | 450.7 | 361.9 | 477.1
1615.1 | 1507.1 | 287 | 154.9 | 380.1 | 270.8 | 354.2 | 449.4 | 361.6 | 476.7
1616.1 | 1508.1 | 286.7 | 154.8 | 378.6 | 271 | 355 | 448.1 | 361.3 | 476.5
1617.1 | 1509.1 | 286.3 | 156.1 | 378.1 | 272.4 | 355.4 | 446.7 | 361 | 476.3
1618.1 | 1510.1 | 285.9 | 157.6 | 377.5 | 273.4 | 356 | 445.4 | 360.7 | 476.1
1619.1 | 1511.1 | 285.5 | 158.9 | 377.2 | 273.7 | 357 | 444.1 | 360.4 | 475.9
1620.1 | 1512.1 | 285 | 160.5 | 376.9 | 273.6 | 357.6 | 442.7 | 360.1 | 475.7
1621.1 | 1513.1 | 284.6 | 161.5 | 376.2 | 273.6 | 357.8 | 441.3 | 359.7 | 475.5
1622.1 | 1514.1 | 284.3 | 161.8 | 375.5 | 272.7 | 357.7 | 440 | 359.4 | 475.4
1623.1 | 1515.1 | 283.8 | 163 | 375 | 271.6 | 359.2 | 438.7 | 359.1 | 475.3
1624.1 | 1516.1 | 283.3 | 165.7 | 375 | 271.2 | 360.5 | 437.3 | 358.8 | 475.3
1625.1 | 1517.1 | 282.8 | 167.6 | 375.5 | 271.2 | 361.8 | 435.9 | 358.4 | 475.3
1626.1 | 1518.1 | 282.4 | 169.7 | 375.7 | 272.8 | 362.7 | 434.6 | 358.1 | 475.1
1627.1 | 1519.1 | 282 | 170.9 | 375.8 | 274.4 | 363.5 | 433.2 | 357.8 | 474.8
1628.1 | 1520.1 | 281.7 | 171 | 375.4 | 276.9 | 364.3 | 431.9 | 357.4 | 474.7
1629.1 | 1521.1 | 281.5 | 173.5 | 374.7 | 277.2 | 364.9 | 430.6 | 357.1 | 474.5
1630.1 | 1522.1 | 281.1 | 174.9 | 374.2 | 276.5 | 365.7 | 429.4 | 356.8 | 474.4
1631.1 | 1523.1 | 280.8 | 176.1 | 374.2 | 277 | 366.2 | 428.2 | 356.4 | 474.4
1632.1 | 1524.1 | 280.5 | 178.3 | 374.3 | 279.3 | 366.5 | 427.1 | 356.1 | 474.1
1633.1 | 1525.1 | 280.2 | 180.6 | 373.4 | 281.6 | 367.1 | 425.9 | 355.7 | 473.7
1634.1 | 1526.1 | 279.9 | 181.6 | 373 | 281.1 | 367 | 424.8 | 355.4 | 473.5
1635.1 | 1527.1 | 279.5 | 181.6 | 373 | 281.8 | 367 | 423.6 | 355 | 473.2
1636.1 | 1528.1 | 279.2 | 182.1 | 373 | 282.1 | 367.1 | 422.5 | 354.7 | 472.8
1637.1 | 1529.1 | 278.9 | 182.4 | 372.8 | 281 | 366.7 | 421.4 | 354.4 | 472.5
1638.1 | 1530.1 | 278.5 | 184.9 | 372.9 | 280.4 | 366.4 | 420.3 | 354.1 | 472.1
1639.1 | 1531.1 | 278 | 186.4 | 372.3 | 280.3 | 365 | 419.3 | 353.8 | 471.8
1640.1 | 1532.1 | 277.6 | 186.8 | 370.7 | 280.2 | 363 | 418.2 | 353.5 | 471.4
1641.1 | 1533.1 | 277.3 | 184.9 | 368.8 | 279.8 | 361.3 | 417.1 | 353.1 | 471.2
1642.1 | 1534.1 | 277 | 185.2 | 367 | 280.3 | 360.1 | 416 | 352.8 | 471
1643.1 | 1535.1 | 276.6 | 185.8 | 365.2 | 281.3 | 359.5 | 415 | 352.5 | 470.7
1644.1 | 1536.1 | 276.2 | 187.6 | 363.3 | 282.1 | 358.7 | 414 | 352.2 | 470.5
1645.1 | 1537.1 | 275.8 | 189.8 | 361.8 | 283.6 | 358 | 413 | 351.9 | 470.1
1646.1 | 1538.1 | 275.4 | 187 | 359.9 | 283.2 | 357.7 | 412.1 | 351.5 | 469.9
1647.1 | 1539.1 | 275 | 182.2 | 357.7 | 280.9 | 356.6 | 411.2 | 351.2 | 469.6
1648.1 | 1540.1 | 274.6 | 179.5 | 356.2 | 278.9 | 355.5 | 410.3 | 350.9 | 469.2
1649.1 | 1541.1 | 274.2 | 177.5 | 355.1 | 277.4 | 354.8 | 409.4 | 350.6 | 468.7
1650.1 | 1542.1 | 273.7 | 175.9 | 353.6 | 276.3 | 354.5 | 408.5 | 350.3 | 468.2
1651.1 | 1543.1 | 273.3 | 173.8 | 351.8 | 275 | 353.2 | 407.5 | 350 | 467.8
1652.1 | 1544.1 | 273 | 171.6 | 350.2 | 272.9 | 353.4 | 406.6 | 349.7 | 467.3
1653.1 | 1545.1 | 272.5 | 169.2 | 348.8 | 271.4 | 353.3 | 405.7 | 349.4 | 466.9
1654.1 | 1546.1 | 272.1 | 167.2 | 348.1 | 270.6 | 352.5 | 404.8 | 349.2 | 466.4
1655.1 | 1547.1 | 271.7 | 166 | 347.7 | 269.6 | 351.4 | 403.8 | 348.9 | 465.8
1656.1 | 1548.1 | 271.3 | 164.9 | 346.8 | 268.5 | 350.2 | 402.8 | 348.6 | 465.2
1657.1 | 1549.1 | 270.9 | 163.6 | 346.1 | 267.5 | 349 | 401.9 | 348.3 | 464.7
1658.1 | 1550.1 | 270.4 | 162.9 | 345.5 | 266.5 | 348 | 401 | 348 | 464.3
1659.1 | 1551.1 | 269.9 | 160.8 | 344.6 | 265.2 | 346.8 | 400 | 347.7 | 464
1660.1 | 1552.1 | 269.5 | 157.1 | 343.4 | 263.9 | 345.5 | 399 | 347.4 | 463.7
1661.1 | 1553.1 | 269 | 153.2 | 341.8 | 263 | 344.7 | 398.1 | 347.1 | 463.2
1662.1 | 1554.1 | 268.5 | 150.9 | 341 | 262.5 | 344 | 397.2 | 346.8 | 462.7
1663.1 | 1555.1 | 268.1 | 150.2 | 340.2 | 262.5 | 343.3 | 396.2 | 346.5 | 462.3
1664.1 | 1556.1 | 267.7 | 150.6 | 339.3 | 261.9 | 343.2 | 395.3 | 346.2 | 461.9
1665.1 | 1557.1 | 267.3 | 148.9 | 338.7 | 260.7 | 342.5 | 394.4 | 345.9 | 461.3
1666.1 | 1558.1 | 267 | 146.8 | 338 | 259.7 | 341.4 | 393.5 | 345.7 | 460.9
1667.1 | 1559.1 | 266.7 | 144.9 | 336.8 | 258.3 | 339.9 | 392.6 | 345.3 | 460.6
1668.1 | 1560.1 | 266.5 | 143.4 | 335.9 | 257.7 | 338.8 | 391.8 | 345.1 | 460.3
1669.1 | 1561.1 | 266.2 | 141.9 | 334.8 | 257.6 | 338.1 | 390.9 | 344.8 | 459.9
1670.1 | 1562.1 | 265.8 | 140.5 | 333.8 | 257.9 | 337.1 | 390 | 344.5 | 459.6
1671.1 | 1563.1 | 265.5 | 139.7 | 333 | 256.5 | 336 | 389.1 | 344.2 | 459.2
1672.1 | 1564.1 | 265.2 | 138.2 | 332.1 | 255.7 | 335.6 | 388.2 | 343.9 | 458.6
1673.1 | 1565.1 | 264.9 | 136.4 | 330.8 | 255.9 | 334.9 | 387.4 | 343.6 | 457.9
1674.1 | 1566.1 | 264.6 | 135.7 | 330 | 257 | 334.9 | 386.5 | 343.3 | 457.2
1675.1 | 1567.1 | 264.3 | 135.6 | 328.9 | 256 | 334.5 | 385.7 | 343 | 456.5
1676.1 | 1568.1 | 263.9 | 134.5 | 327.9 | 254.9 | 333 | 384.9 | 342.7 | 455.9
1677.1 | 1569.1 | 263.6 | 134 | 327.2 | 253 | 331.1 | 384 | 342.4 | 455.2
1678.1 | 1570.1 | 263.3 | 133.3 | 326 | 252.5 | 330.1 | 383.2 | 342.1 | 454.5
1679.1 | 1571.1 | 263.1 | 132.8 | 325.4 | 250.6 | 328.8 | 382.4 | 341.8 | 453.8
1680.1 | 1572.1 | 262.8 | 132.1 | 324.3 | 250.2 | 328.9 | 381.5 | 341.5 | 453.1
1681.1 | 1573.1 | 262.4 | 132.6 | 323.8 | 250 | 328.7 | 380.7 | 341.2 | 452.4
1682.1 | 1574.1 | 262.1 | 132.2 | 322.6 | 249.9 | 328.4 | 380 | 340.8 | 451.7
1683.1 | 1575.1 | 261.8 | 132.1 | 321.9 | 249.4 | 328.2 | 379.2 | 340.6 | 450.9
1684.1 | 1576.1 | 261.4 | 131.8 | 321.4 | 249.4 | 327.7 | 378.4 | 340.3 | 450.2
1685.1 | 1577.1 | 261 | 132.3 | 320.9 | 249.4 | 327.4 | 377.6 | 340 | 449.5
1686.1 | 1578.1 | 260.6 | 131.6 | 319.9 | 248 | 326.9 | 376.9 | 339.7 | 448.8
1687.1 | 1579.1 | 260.2 | 130.7 | 319.4 | 247.2 | 326.7 | 376.1 | 339.4 | 448.1
1688.1 | 1580.1 | 260 | 129.6 | 319 | 245.7 | 325.8 | 375.3 | 339.1 | 447.4
1689.1 | 1581.1 | 259.6 | 129.3 | 318.3 | 243.6 | 324.8 | 374.5 | 338.8 | 446.6
1690.1 | 1582.1 | 259.2 | 129.4 | 317.9 | 242 | 323.5 | 373.7 | 338.5 | 445.7
1691.1 | 1583.1 | 258.8 | 130.3 | 317.5 | 240.1 | 322 | 372.9 | 338.2 | 444.8
1692.1 | 1584.1 | 258.5 | 132.2 | 317.8 | 239.4 | 320.9 | 372.1 | 337.9 | 443.8
1693.1 | 1585.1 | 258.1 | 133 | 318.2 | 238.3 | 320.4 | 371.4 | 337.6 | 442.8
1694.1 | 1586.1 | 257.8 | 132.4 | 317.6 | 237.5 | 320 | 370.6 | 337.4 | 441.8
1695.1 | 1587.1 | 257.4 | 131.2 | 317.4 | 237.9 | 320.1 | 369.8 | 337.1 | 440.8
1696.1 | 1588.1 | 257.1 | 130.2 | 316.7 | 237.6 | 320.2 | 369.1 | 336.8 | 439.8
1697.1 | 1589.1 | 256.7 | 131.4 | 316.4 | 236.7 | 319.6 | 368.3 | 336.6 | 438.8
1698.1 | 1590.1 | 256.4 | 132.9 | 316.4 | 235.5 | 318.6 | 367.6 | 336.3 | 437.9
1699.1 | 1591.1 | 256.1 | 131.8 | 316.3 | 235.1 | 318.3 | 366.8 | 336 | 437
1700.1 | 1592.1 | 255.8 | 130.3 | 315.8 | 234.5 | 318.4 | 366 | 335.8 | 436
1701.1 | 1593.1 | 255.4 | 128.9 | 314.8 | 234.6 | 317.3 | 365.3 | 335.5 | 434.9
1702.1 | 1594.1 | 255 | 127.7 | 313.7 | 235.4 | 316.7 | 364.5 | 335.2 | 433.8
1703.1 | 1595.1 | 254.6 | 127 | 313.5 | 236.4 | 316.6 | 363.7 | 334.9 | 432.6
1704.1 | 1596.1 | 254.2 | 126.3 | 313 | 235.3 | 315.9 | 362.9 | 334.7 | 431.5
1705.1 | 1597.1 | 253.8 | 125.2 | 312.1 | 234.5 | 314.9 | 362.1 | 334.4 | 430.4
1706.1 | 1598.1 | 253.4 | 125.1 | 311.2 | 232.3 | 314.3 | 361.2 | 334.1 | 429.3
1707.1 | 1599.1 | 253.1 | 123.8 | 310.4 | 231.9 | 314.4 | 360.5 | 333.8 | 428.2
1708.1 | 1600.1 | 252.7 | 123.8 | 309.9 | 231 | 314.9 | 359.7 | 333.5 | 427.2
1709.1 | 1601.1 | 252.4 | 123.6 | 309 | 229.6 | 314.6 | 358.9 | 333.2 | 426.2
1710.1 | 1602.1 | 252.1 | 123.2 | 308.3 | 229.9 | 314.2 | 358.2 | 332.8 | 425.1
1711.1 | 1603.1 | 251.8 | 123.6 | 307.9 | 229.6 | 312.8 | 357.4 | 332.5 | 424.2
1712.1 | 1604.1 | 251.4 | 122.6 | 307 | 229.3 | 311.4 | 356.6 | 332.2 | 423.2
1713.1 | 1605.1 | 251.1 | 122.5 | 306.1 | 229.9 | 310.2 | 355.9 | 331.9 | 422.3
1714.1 | 1606.1 | 250.8 | 122.5 | 305.3 | 230.8 | 310.5 | 355.1 | 331.6 | 421.4
1715.1 | 1607.1 | 250.5 | 122.5 | 304.1 | 231.1 | 310 | 354.3 | 331.3 | 420.5
1716.1 | 1608.1 | 250.3 | 122.8 | 303.4 | 231.6 | 309.4 | 353.5 | 331 | 419.7
1717.1 | 1609.1 | 249.9 | 122.6 | 301.8 | 231.2 | 309.4 | 352.7 | 330.6 | 418.7
1718.1 | 1610.1 | 249.6 | 121.2 | 300.8 | 230.9 | 308.9 | 351.8 | 330.3 | 417.9
1719.1 | 1611.1 | 249.3 | 120.3 | 300.2 | 230.9 | 308 | 351 | 330 | 417
1720.1 | 1612.1 | 249 | 120.5 | 300.2 | 230.6 | 307.5 | 350.1 | 329.7 | 416
1721.1 | 1613.1 | 248.6 | 119.8 | 299.8 | 230.4 | 307.5 | 349.3 | 329.4 | 415.1
1722.1 | 1614.1 | 248.3 | 119.8 | 299.9 | 229 | 307.5 | 348.5 | 329.1 | 414.3
1723.1 | 1615.1 | 248 | 118.9 | 300 | 229.5 | 307.6 | 347.6 | 328.8 | 413.5
1724.1 | 1616.1 | 247.8 | 118.9 | 299.2 | 230.3 | 307.2 | 346.8 | 328.5 | 412.7
1725.1 | 1617.1 | 247.5 | 118.5 | 298.4 | 230.3 | 306.6 | 346 | 328.1 | 411.9
1726.1 | 1618.1 | 247.2 | 118.2 | 298.3 | 230.1 | 306.5 | 345.1 | 327.8 | 411.2
1727.1 | 1619.1 | 246.9 | 117.9 | 297.9 | 230.3 | 306.6 | 344.3 | 327.5 | 410.4
1728.1 | 1620.1 | 246.5 | 117.2 | 297.8 | 230 | 306.9 | 343.4 | 327.2 | 409.6
1729.1 | 1621.1 | 246.2 | 116.6 | 298.3 | 229.3 | 307 | 342.5 | 326.9 | 408.9
1730.1 | 1622.1 | 245.8 | 116.3 | 297.9 | 229 | 306.7 | 341.6 | 326.5 | 408.2
1731.1 | 1623.1 | 245.3 | 115.6 | 297.2 | 229.3 | 306.3 | 340.8 | 326.2 | 407.5
1732.1 | 1624.1 | 244.9 | 115 | 296.8 | 229.4 | 305.6 | 339.9 | 325.9 | 406.8
1733.1 | 1625.1 | 244.5 | 114.8 | 296.4 | 229.6 | 305.4 | 339 | 325.6 | 406.1
1734.1 | 1626.1 | 244.1 | 115.7 | 296.4 | 229.1 | 305.1 | 338.1 | 325.2 | 405.4
1735.1 | 1627.1 | 243.8 | 116.3 | 296 | 228.4 | 304.9 | 337.2 | 324.9 | 404.6
1736.1 | 1628.1 | 243.5 | 116.3 | 295.1 | 228.3 | 304.5 | 336.3 | 324.6 | 403.9
1737.1 | 1629.1 | 243.2 | 115.9 | 294.7 | 227.8 | 304.1 | 335.5 | 324.2 | 403.2
1738.1 | 1630.1 | 242.9 | 115.4 | 294.2 | 227.6 | 304.1 | 334.6 | 323.9 | 402.4
1739.1 | 1631.1 | 242.6 | 115 | 293.5 | 227.2 | 303.7 | 333.8 | 323.5 | 401.7
1740.1 | 1632.1 | 242.3 | 114.6 | 293 | 227.1 | 303 | 332.9 | 323.2 | 400.9
1741.1 | 1633.1 | 242.1 | 114.2 | 292.3 | 227 | 302.8 | 332.1 | 322.8 | 400.2
1742.1 | 1634.1 | 241.8 | 113.3 | 291.7 | 226.7 | 302.4 | 331.3 | 322.5 | 399.4
1743.1 | 1635.1 | 241.5 | 113.1 | 291.3 | 227.2 | 301.8 | 330.5 | 322.1 | 398.7
1744.1 | 1636.1 | 241.1 | 113.3 | 291.1 | 226.6 | 301.1 | 329.7 | 321.7 | 398.1
1745.1 | 1637.1 | 240.8 | 112.8 | 290.6 | 225.9 | 300.8 | 328.9 | 321.4 | 397.4
1746.1 | 1638.1 | 240.5 | 112.4 | 290.2 | 225.8 | 300.7 | 328.1 | 321 | 396.7
1747.1 | 1639.1 | 240.3 | 112 | 289.9 | 225.6 | 300.5 | 327.3 | 320.7 | 396
1748.1 | 1640.1 | 240 | 111.3 | 290.4 | 224.9 | 300.3 | 326.6 | 320.3 | 395.3
1749.1 | 1641.1 | 239.8 | 110.7 | 290.2 | 225.1 | 300.5 | 325.8 | 320 | 394.7
1750.1 | 1642.1 | 239.5 | 110.1 | 289.3 | 225.3 | 299.7 | 325.1 | 319.6 | 394
1751.1 | 1643.1 | 239.3 | 109.7 | 288.2 | 224.8 | 298.7 | 324.3 | 319.3 | 393.4
1752.1 | 1644.1 | 239 | 110.3 | 287.6 | 224.9 | 298.1 | 323.6 | 318.9 | 392.8
1753.1 | 1645.1 | 238.6 | 111.2 | 287.2 | 224.8 | 298.2 | 322.8 | 318.6 | 392.2
1754.1 | 1646.1 | 238.2 | 112.9 | 287.5 | 224.4 | 298.5 | 322.1 | 318.2 | 391.7
1755.1 | 1647.1 | 237.9 | 112.4 | 287.6 | 223.4 | 297.8 | 321.4 | 317.9 | 391.2
1756.1 | 1648.1 | 237.6 | 112.3 | 287.4 | 222.9 | 297.2 | 320.6 | 317.5 | 390.6
1757.1 | 1649.1 | 237.2 | 112.1 | 287.3 | 222.4 | 296.5 | 319.9 | 317.2 | 390
1758.1 | 1650.1 | 236.8 | 111.9 | 287 | 222 | 295.9 | 319.2 | 316.9 | 389.4
1759.1 | 1651.1 | 236.4 | 111.4 | 286 | 221.7 | 295.5 | 318.5 | 316.5 | 388.8
1760.1 | 1652.1 | 236.1 | 111 | 285.4 | 221.9 | 295.5 | 317.8 | 316.2 | 388.1
1761.1 | 1653.1 | 235.8 | 110.6 | 284.8 | 222 | 295.4 | 317 | 315.9 | 387.5
1762.1 | 1654.1 | 235.4 | 110.6 | 284.6 | 221.9 | 295.5 | 316.3 | 315.6 | 386.9
1763.1 | 1655.1 | 235.1 | 112.4 | 284.1 | 221.6 | 295.4 | 315.6 | 315.3 | 386.3
1764.1 | 1656.1 | 234.8 | 112.5 | 283.2 | 221.6 | 294.9 | 314.9 | 314.9 | 385.7
1765.1 | 1657.1 | 234.5 | 111.6 | 282.1 | 220.9 | 293.9 | 314.2 | 314.6 | 385.1
1766.1 | 1658.1 | 234.2 | 112 | 281.9 | 221 | 293.3 | 313.5 | 314.3 | 384.4
1767.1 | 1659.1 | 233.9 | 111.5 | 281.6 | 220.8 | 292.6 | 312.9 | 313.9 | 383.8
1768.1 | 1660.1 | 233.6 | 112 | 281.3 | 220.5 | 293 | 312.2 | 313.6 | 383.3
1769.1 | 1661.1 | 233.2 | 112.7 | 280.7 | 220.3 | 292.8 | 311.6 | 313.2 | 382.7
1770.1 | 1662.1 | 232.9 | 112.5 | 280.2 | 219.8 | 292.8 | 311 | 312.9 | 382.1
1771.1 | 1663.1 | 232.5 | 113.2 | 279.7 | 219.4 | 292.3 | 310.4 | 312.5 | 381.6
1772.1 | 1664.1 | 232.2 | 113.2 | 279.4 | 218.6 | 292 | 309.8 | 312.2 | 381
1773.1 | 1665.1 | 231.8 | 113.1 | 279.1 | 218.3 | 292.7 | 309.2 | 311.9 | 380.4
1774.1 | 1666.1 | 231.4 | 112.7 | 279.1 | 218.1 | 292.4 | 308.5 | 311.5 | 379.8
1775.1 | 1667.1 | 231.1 | 111.5 | 279.2 | 218.3 | 292.4 | 307.9 | 311.2 | 379.3
1776.1 | 1668.1 | 230.7 | 111.2 | 279.4 | 218.4 | 292.5 | 307.2 | 310.9 | 378.8
1777.1 | 1669.1 | 230.5 | 111.3 | 279.8 | 218.4 | 292.6 | 306.6 | 310.6 | 378.3
1778.1 | 1670.1 | 230.2 | 112.1 | 279.8 | 217.5 | 292.8 | 306 | 310.3 | 377.8
1779.1 | 1671.1 | 229.9 | 111.9 | 279.8 | 216.9 | 292.7 | 305.4 | 309.9 | 377.4
1780.1 | 1672.1 | 229.5 | 111.3 | 279.5 | 216.5 | 292.7 | 304.9 | 309.6 | 376.9
1781.1 | 1673.1 | 229.3 | 111.7 | 279.2 | 216.6 | 292.2 | 304.3 | 309.2 | 376.5
1782.1 | 1674.1 | 228.9 | 112.7 | 279.7 | 216.5 | 291.3 | 303.7 | 308.9 | 376
1783.1 | 1675.1 | 228.6 | 113 | 279.7 | 216.2 | 290.7 | 303.1 | 308.6 | 375.5
1784.1 | 1676.1 | 228.3 | 112.4 | 279 | 215.8 | 290.1 | 302.6 | 308.2 | 375.1
1785.1 | 1677.1 | 227.9 | 112 | 278.5 | 215.7 | 289.2 | 302 | 307.9 | 374.6
1786.1 | 1678.1 | 227.6 | 110.9 | 277.9 | 215.9 | 288.7 | 301.4 | 307.5 | 374.1
1787.1 | 1679.1 | 227.2 | 110.4 | 277.2 | 215.5 | 288.7 | 300.9 | 307.2 | 373.6
1788.1 | 1680.1 | 226.9 | 111.1 | 277 | 215.1 | 288.8 | 300.3 | 306.8 | 373.1
1789.1 | 1681.1 | 226.6 | 110.8 | 276.6 | 214.8 | 288.5 | 299.8 | 306.5 | 372.5
1790.1 | 1682.1 | 226.3 | 110.6 | 275.9 | 214.9 | 288.4 | 299.2 | 306.2 | 372
1791.1 | 1683.1 | 226 | 109.9 | 275 | 214.2 | 288.4 | 298.6 | 305.8 | 371.5
1792.1 | 1684.1 | 225.7 | 108.6 | 274.3 | 213.3 | 288.3 | 298 | 305.5 | 371.1
1793.1 | 1685.1 | 225.3 | 107.8 | 274.1 | 213.1 | 288.3 | 297.5 | 305.2 | 370.6
1794.1 | 1686.1 | 225.1 | 107.7 | 273.4 | 212.9 | 288.5 | 296.9 | 304.8 | 370.1
1795.1 | 1687.1 | 224.8 | 109.1 | 272.6 | 212.6 | 288.3 | 296.3 | 304.5 | 369.6
1796.1 | 1688.1 | 224.5 | 109.1 | 272 | 211.6 | 287.6 | 295.7 | 304.2 | 369.2
1797.1 | 1689.1 | 224.2 | 108.6 | 271.3 | 210.8 | 287.1 | 295.1 | 303.9 | 368.8
1798.1 | 1690.1 | 223.9 | 107.9 | 270.9 | 210.5 | 287.1 | 294.5 | 303.5 | 368.3
1799.1 | 1691.1 | 223.6 | 107.3 | 270.6 | 210.2 | 287 | 294 | 303.2 | 367.9
1800.1 | 1692.1 | 223.4 | 106.6 | 270.4 | 209.3 | 286.6 | 293.4 | 302.9 | 367.4
1801.1 | 1693.1 | 223.1 | 106.4 | 269.9 | 208.8 | 286.5 | 292.8 | 302.5 | 367
1802.1 | 1694.1 | 222.8 | 106 | 269.3 | 208.7 | 286.8 | 292.3 | 302.2 | 366.5
1803.1 | 1695.1 | 222.4 | 106.7 | 269.1 | 208.7 | 287.2 | 291.7 | 301.9 | 366
1804.1 | 1696.1 | 222.1 | 106.9 | 269.3 | 208.5 | 287.4 | 291.1 | 301.6 | 365.5
1805.1 | 1697.1 | 221.8 | 106.3 | 269.5 | 208.1 | 287.8 | 290.6 | 301.3 | 365
1806.1 | 1698.1 | 221.5 | 106 | 269.8 | 207.9 | 287.9 | 290 | 301 | 364.5
1807.1 | 1699.1 | 221.2 | 106.8 | 269.8 | 207.9 | 287.9 | 289.4 | 300.7 | 364.1
1808.1 | 1700.1 | 221 | 106.7 | 269.1 | 208 | 287.7 | 288.9 | 300.4 | 363.5
1809.1 | 1701.1 | 220.7 | 105.6 | 268.8 | 207.8 | 287.2 | 288.3 | 300 | 363
1810.1 | 1702.1 | 220.4 | 105.4 | 268.5 | 207.4 | 286.7 | 287.7 | 299.7 | 362.6
1811.1 | 1703.1 | 220.1 | 105.1 | 267.9 | 207.2 | 286.3 | 287.2 | 299.4 | 362.2
1812.1 | 1704.1 | 219.8 | 104.5 | 267.5 | 206.9 | 285.5 | 286.6 | 299.1 | 361.7
1813.1 | 1705.1 | 219.6 | 104.2 | 266.6 | 206.8 | 284.9 | 286.1 | 298.7 | 361.3
1814.1 | 1706.1 | 219.3 | 103.4 | 265.8 | 207 | 283.7 | 285.5 | 298.4 | 360.9
1815.1 | 1707.1 | 219.1 | 102.6 | 264.7 | 206.2 | 282.3 | 284.9 | 298 | 360.5
1816.1 | 1708.1 | 218.8 | 101.5 | 263.7 | 206.1 | 281.1 | 284.3 | 297.6 | 360.1
1817.1 | 1709.1 | 218.6 | 100.8 | 263 | 206.3 | 280 | 283.7 | 297.3 | 359.7
1818.1 | 1710.1 | 218.4 | 100.3 | 262.6 | 206.6 | 279.3 | 283.1 | 296.9 | 359.2
1819.1 | 1711.1 | 218.2 | 100.3 | 262.4 | 206.5 | 278.6 | 282.5 | 296.6 | 358.7
1820.1 | 1712.1 | 217.9 | 100.3 | 262.5 | 206.3 | 278.4 | 281.8 | 296.3 | 358.2
1821.1 | 1713.1 | 217.5 | 99.7 | 262.5 | 205.7 | 278.4 | 281.2 | 296 | 357.8
1822.1 | 1714.1 | 217.2 | 99.1 | 262.4 | 205.7 | 278.1 | 280.6 | 295.6 | 357.3
1823.1 | 1715.1 | 216.9 | 98.6 | 262.1 | 205.6 | 277.2 | 280 | 295.3 | 356.7
1824.1 | 1716.1 | 216.6 | 98.2 | 261.3 | 205.3 | 276 | 279.4 | 294.9 | 356.3
1825.1 | 1717.1 | 216.1 | 97.7 | 260.7 | 204.8 | 276.2 | 278.8 | 294.6 | 355.8
1826.1 | 1718.1 | 215.8 | 97.3 | 260.2 | 204.6 | 276 | 278.3 | 294.3 | 355.4
1827.1 | 1719.1 | 215.5 | 97.3 | 259.9 | 204.4 | 275.6 | 277.7 | 293.9 | 355
1828.1 | 1720.1 | 215.1 | 99.3 | 260 | 203.8 | 274.8 | 277.1 | 293.6 | 354.6
1829.1 | 1721.1 | 214.9 | 100.5 | 259.6 | 203.3 | 274.6 | 276.5 | 293.2 | 354.2
1830.1 | 1722.1 | 214.6 | 100.1 | 259.3 | 203.1 | 274.6 | 276 | 292.9 | 353.6
1831.1 | 1723.1 | 214.4 | 99.9 | 259.2 | 202.4 | 274.8 | 275.4 | 292.6 | 353.2
1832.1 | 1724.1 | 214.1 | 100 | 258.7 | 202.6 | 274.6 | 274.8 | 292.2 | 352.7
1833.1 | 1725.1 | 213.8 | 99.8 | 258.7 | 202.8 | 274.5 | 274.3 | 291.9 | 352.2
1834.1 | 1726.1 | 213.5 | 99.5 | 258.5 | 202.2 | 274.7 | 273.7 | 291.6 | 351.8
1835.1 | 1727.1 | 213.3 | 100.4 | 258.1 | 202.2 | 274.9 | 273.1 | 291.3 | 351.3
1836.1 | 1728.1 | 213 | 102.8 | 258.4 | 202.4 | 274.8 | 272.6 | 291 | 350.8
1837.1 | 1729.1 | 212.7 | 102.8 | 258.6 | 201.8 | 275.2 | 272 | 290.7 | 350.4
1838.1 | 1730.1 | 212.4 | 101.9 | 258.2 | 200.4 | 274.5 | 271.5 | 290.4 | 350
1839.1 | 1731.1 | 212.1 | 100.9 | 257.4 | 200.7 | 274.4 | 270.9 | 290.1 | 349.6
1840.1 | 1732.1 | 211.9 | 100.2 | 256.7 | 201.8 | 274.2 | 270.3 | 289.7 | 349.3
1841.1 | 1733.1 | 211.7 | 100.5 | 256.6 | 201.4 | 274.2 | 269.7 | 289.4 | 348.8
1842.1 | 1734.1 | 211.4 | 100.7 | 256.3 | 200.6 | 273.5 | 269.1 | 289.1 | 348.4
1843.1 | 1735.1 | 211.1 | 99.8 | 256 | 199.6 | 273.2 | 268.6 | 288.8 | 348
1844.1 | 1736.1 | 210.8 | 98.9 | 256 | 199.3 | 273.4 | 268 | 288.5 | 347.6
1845.1 | 1737.1 | 210.5 | 98.6 | 255.8 | 199.2 | 273 | 267.4 | 288.1 | 347.2
1846.1 | 1738.1 | 210.2 | 98.7 | 255.5 | 199.2 | 272.3 | 266.8 | 287.8 | 346.9
1847.1 | 1739.1 | 210 | 99.3 | 254.9 | 198.8 | 272.1 | 266.2 | 287.5 | 346.6
1848.1 | 1740.1 | 209.7 | 99.1 | 254.5 | 198.4 | 271.4 | 265.6 | 287.1 | 346.2
1849.1 | 1741.1 | 209.4 | 100 | 253.9 | 197.9 | 270.3 | 265 | 286.8 | 345.8
1850.1 | 1742.1 | 209.1 | 98.9 | 253.1 | 197.5 | 269.7 | 264.4 | 286.4 | 345.5
1851.1 | 1743.1 | 208.9 | 98.2 | 252.7 | 197.1 | 269.1 | 263.8 | 286.1 | 345.2
1852.1 | 1744.1 | 208.6 | 98.4 | 252.5 | 197 | 268.5 | 263.2 | 285.7 | 344.8
1853.1 | 1745.1 | 208.4 | 98.7 | 252.3 | 196.7 | 267.9 | 262.6 | 285.4 | 344.5
1854.1 | 1746.1 | 208.2 | 98.6 | 252 | 196.4 | 267.5 | 262 | 285 | 344.2
1855.1 | 1747.1 | 207.9 | 98.1 | 251.8 | 196.1 | 267.2 | 261.5 | 284.7 | 343.8
1856.1 | 1748.1 | 207.6 | 97.6 | 252.2 | 195.8 | 267.4 | 260.9 | 284.3 | 343.5
1857.1 | 1749.1 | 207.3 | 97.4 | 252 | 195.4 | 267.3 | 260.4 | 284 | 343.1
1858.1 | 1750.1 | 207.1 | 96.8 | 251.2 | 195 | 266.8 | 259.8 | 283.6 | 342.7
1859.1 | 1751.1 | 206.9 | 96.6 | 250.2 | 194.5 | 266.1 | 259.3 | 283.3 | 342.3
1860.1 | 1752.1 | 206.5 | 96.7 | 249.6 | 194.1 | 265.7 | 258.7 | 282.9 | 341.9
1861.1 | 1753.1 | 206.1 | 96.9 | 249.3 | 193.8 | 265.8 | 258.1 | 282.5 | 341.5
1862.1 | 1754.1 | 205.9 | 98.2 | 248.9 | 192.9 | 266.7 | 257.6 | 282.2 | 341.2
1863.1 | 1755.1 | 205.6 | 99.3 | 248.1 | 192.9 | 267.6 | 257 | 281.8 | 340.7
1864.1 | 1756.1 | 205.4 | 101.1 | 247.1 | 193.5 | 268.3 | 256.5 | 281.4 | 340.2
1865.1 | 1757.1 | 205.1 | 102.7 | 246.8 | 193 | 268 | 256 | 281 | 339.7
1866.1 | 1758.1 | 204.8 | 103.8 | 246.7 | 193.2 | 268.9 | 255.5 | 280.6 | 339.2
1867.1 | 1759.1 | 204.5 | 103 | 246.6 | 193.3 | 269.6 | 255.1 | 280.2 | 338.8
1868.1 | 1760.1 | 204.3 | 103.3 | 246.4 | 193.7 | 269.1 | 254.6 | 279.8 | 338.4
1869.1 | 1761.1 | 204.1 | 105.2 | 245.9 | 194.1 | 268.1 | 254.2 | 279.4 | 337.9
1870.1 | 1762.1 | 203.9 | 105.4 | 245.5 | 195.2 | 268.1 | 253.7 | 279 | 337.5
1871.1 | 1763.1 | 203.6 | 105.3 | 245 | 196.1 | 267.4 | 253.2 | 278.6 | 337.2
1872.1 | 1764.1 | 203.3 | 105.2 | 245.2 | 195.2 | 266.6 | 252.6 | 278.2 | 336.8
1873.1 | 1765.1 | 203.1 | 103.7 | 245 | 194.5 | 265.8 | 252.1 | 277.8 | 336.4
1874.1 | 1766.1 | 202.7 | 102.2 | 244 | 194 | 265.5 | 251.5 | 277.4 | 336
1875.1 | 1767.1 | 202.4 | 101.3 | 243 | 193.2 | 265.1 | 251 | 277 | 335.6
1876.1 | 1768.1 | 202.2 | 100.2 | 242.1 | 192.8 | 264.7 | 250.4 | 276.6 | 335.2
1877.1 | 1769.1 | 201.8 | 100.5 | 241.9 | 192.1 | 264 | 249.8 | 276.3 | 334.7
1878.1 | 1770.1 | 201.6 | 100.6 | 241.5 | 191.6 | 263.4 | 249.3 | 275.9 | 334.3
1879.1 | 1771.1 | 201.3 | 99.2 | 241.3 | 191.2 | 262.8 | 248.8 | 275.5 | 333.9
1880.1 | 1772.1 | 201 | 98.1 | 240.6 | 190.8 | 262.4 | 248.2 | 275.1 | 333.5
1881.1 | 1773.1 | 200.8 | 97.1 | 239.6 | 190.3 | 262.2 | 247.6 | 274.7 | 333.2
1882.1 | 1774.1 | 200.6 | 96.2 | 239.2 | 189.9 | 261.9 | 247.1 | 274.3 | 332.8
1883.1 | 1775.1 | 200.3 | 95.2 | 239 | 189.6 | 261.8 | 246.6 | 273.9 | 332.4
1884.1 | 1776.1 | 200.1 | 96.4 | 239.3 | 188.9 | 261.2 | 246 | 273.5 | 332
1885.1 | 1777.1 | 199.8 | 96.2 | 238.9 | 188.6 | 260.8 | 245.5 | 273.2 | 331.6
1886.1 | 1778.1 | 199.6 | 95.5 | 238.4 | 188.5 | 260.9 | 245 | 272.8 | 331.3
1887.1 | 1779.1 | 199.4 | 94.4 | 238.3 | 188.1 | 260.7 | 244.5 | 272.4 | 331
1888.1 | 1780.1 | 199.1 | 93.9 | 238 | 187.9 | 259.9 | 244 | 272 | 330.7
1889.1 | 1781.1 | 198.9 | 94 | 237 | 187.9 | 258.6 | 243.5 | 271.6 | 330.4
1890.1 | 1782.1 | 198.7 | 95.3 | 236.2 | 187.8 | 258.4 | 243 | 271.2 | 330
1891.1 | 1783.1 | 198.4 | 94.9 | 235.7 | 187.6 | 258.3 | 242.5 | 270.8 | 329.6
1892.1 | 1784.1 | 198.2 | 94.1 | 236 | 186.8 | 258.8 | 242 | 270.4 | 329.2
1893.1 | 1785.1 | 198 | 93.6 | 236.1 | 186.7 | 259 | 241.5 | 270 | 328.8
1894.1 | 1786.1 | 197.7 | 93 | 236.2 | 186.5 | 258.8 | 241 | 269.6 | 328.5
1895.1 | 1787.1 | 197.4 | 92.8 | 235.9 | 186.1 | 258.4 | 240.5 | 269.3 | 328.2
1896.1 | 1788.1 | 197.2 | 92.2 | 235.5 | 185.5 | 258.3 | 240.1 | 268.9 | 327.9
1897.1 | 1789.1 | 196.9 | 91.7 | 235.7 | 185 | 258.3 | 239.6 | 268.5 | 327.6
1898.1 | 1790.1 | 196.6 | 91.6 | 235.6 | 185 | 257.9 | 239.1 | 268.1 | 327.2
1899.1 | 1791.1 | 196.3 | 90.9 | 235.8 | 184.5 | 257.4 | 238.7 | 267.7 | 326.8
1900.1 | 1792.1 | 196.1 | 90.5 | 235.3 | 184.1 | 256.9 | 238.2 | 267.4 | 326.4
1901.1 | 1793.1 | 195.9 | 90.1 | 234.7 | 183.8 | 256.1 | 237.7 | 267 | 326
1902.1 | 1794.1 | 195.6 | 89.8 | 234.2 | 183.5 | 255.7 | 237.2 | 266.6 | 325.6
1903.1 | 1795.1 | 195.4 | 90 | 233.8 | 183.5 | 255.7 | 236.7 | 266.2 | 325.2
1904.1 | 1796.1 | 195.1 | 89.9 | 233.5 | 184.3 | 255.6 | 236.1 | 265.9 | 324.8
1905.1 | 1797.1 | 194.8 | 90.3 | 233.4 | 184.3 | 255.2 | 235.6 | 265.5 | 324.4
1906.1 | 1798.1 | 194.6 | 91.2 | 233.1 | 184 | 254.5 | 235 | 265.1 | 324
1907.1 | 1799.1 | 194.4 | 91.2 | 232.9 | 183.8 | 254.4 | 234.5 | 264.7 | 323.6
1908.1 | 1800.1 | 194.2 | 90.7 | 232.4 | 183.3 | 254.4 | 234 | 264.4 | 323.2
1909.1 | 1801.1 | 194 | 90.6 | 232 | 182.6 | 254.1 | 233.5 | 264 | 322.8
1910.1 | 1802.1 | 193.7 | 91.5 | 232.1 | 182.9 | 253.6 | 233 | 263.6 | 322.5
1911.1 | 1803.1 | 193.5 | 90.9 | 232.1 | 182.6 | 253.1 | 232.4 | 263.2 | 322.1
1912.1 | 1804.1 | 193.3 | 90 | 232 | 181.9 | 252.3 | 231.9 | 262.8 | 321.8
1913.1 | 1805.1 | 193 | 89.7 | 231.4 | 181.6 | 251.4 | 231.4 | 262.4 | 321.5
1914.1 | 1806.1 | 192.9 | 89.8 | 231.3 | 181.3 | 250.2 | 230.9 | 262 | 321.2
1915.1 | 1807.1 | 192.7 | 88.9 | 231.2 | 181.2 | 249.4 | 230.4 | 261.6 | 321
1916.1 | 1808.1 | 192.5 | 88.4 | 231.1 | 180.6 | 248.7 | 229.9 | 261.3 | 320.7
1917.1 | 1809.1 | 192.4 | 87.6 | 230.8 | 180.3 | 248.2 | 229.4 | 260.9 | 320.4
1918.1 | 1810.1 | 192.2 | 87.9 | 230.7 | 179.9 | 248 | 228.9 | 260.5 | 320
1919.1 | 1811.1 | 191.9 | 88.4 | 230.8 | 180.2 | 247.5 | 228.4 | 260.1 | 319.7
1920.1 | 1812.1 | 191.7 | 89.1 | 230.1 | 180.7 | 246.7 | 227.9 | 259.7 | 319.3
1921.1 | 1813.1 | 191.4 | 89 | 230.2 | 180.6 | 246.2 | 227.5 | 259.3 | 319
1922.1 | 1814.1 | 191.2 | 89.1 | 230 | 179.8 | 245.8 | 227 | 258.9 | 318.7
1923.1 | 1815.1 | 190.9 | 89.7 | 229.6 | 178.7 | 245 | 226.6 | 258.5 | 318.4
1924.1 | 1816.1 | 190.7 | 90.2 | 229.1 | 177.6 | 244.6 | 226.1 | 258.1 | 318
1925.1 | 1817.1 | 190.4 | 91.2 | 228.6 | 176.8 | 244.2 | 225.6 | 257.7 | 317.6
1926.1 | 1818.1 | 190.2 | 91.1 | 228.5 | 176.5 | 244 | 225.2 | 257.3 | 317.3
1927.1 | 1819.1 | 189.9 | 90.9 | 228 | 176.4 | 243.9 | 224.7 | 256.9 | 316.9
1928.1 | 1820.1 | 189.6 | 90.1 | 227.6 | 176.1 | 243.5 | 224.3 | 256.5 | 316.5
1929.1 | 1821.1 | 189.3 | 88.8 | 227.4 | 175.7 | 242.9 | 223.8 | 256.1 | 316.2
1930.1 | 1822.1 | 189 | 88 | 227.4 | 175 | 242.1 | 223.4 | 255.7 | 315.8
1931.1 | 1823.1 | 188.8 | 88.1 | 227.6 | 174.7 | 242.2 | 222.9 | 255.3 | 315.4
1932.1 | 1824.1 | 188.6 | 88.3 | 228.2 | 175 | 242.2 | 222.5 | 254.9 | 315
1933.1 | 1825.1 | 188.4 | 88.5 | 228.3 | 175.3 | 241.9 | 222 | 254.5 | 314.7
1934.1 | 1826.1 | 188.1 | 89.3 | 227.4 | 175.5 | 241.5 | 221.6 | 254 | 314.3
1935.1 | 1827.1 | 187.9 | 88.2 | 226.3 | 175.3 | 241.6 | 221.2 | 253.6 | 313.9
1936.1 | 1828.1 | 187.7 | 87.5 | 225.5 | 174.9 | 241.5 | 220.7 | 253.2 | 313.6
1937.1 | 1829.1 | 187.5 | 87 | 225.4 | 174.6 | 241 | 220.3 | 252.8 | 313.3
1938.1 | 1830.1 | 187.3 | 87.9 | 225.7 | 175.1 | 240.8 | 219.8 | 252.3 | 312.9
1939.1 | 1831.1 | 187.2 | 88 | 225.1 | 175.6 | 240.5 | 219.4 | 251.9 | 312.6
1940.1 | 1832.1 | 187 | 87.9 | 224.8 | 174.8 | 240.2 | 218.9 | 251.5 | 312.3
1941.1 | 1833.1 | 186.9 | 87.7 | 225 | 174.5 | 239.7 | 218.5 | 251 | 312.1
1942.1 | 1834.1 | 186.7 | 86.9 | 225.3 | 175 | 239.3 | 218.1 | 250.6 | 311.8
1943.1 | 1835.1 | 186.5 | 86.3 | 225.5 | 175.1 | 239.2 | 217.6 | 250.2 | 311.5
1944.1 | 1836.1 | 186.2 | 87.4 | 224.7 | 175.2 | 239.2 | 217.2 | 249.7 | 311.2
1945.1 | 1837.1 | 186 | 88 | 224.2 | 175.8 | 239.3 | 216.8 | 249.3 | 310.9
1946.1 | 1838.1 | 185.8 | 89.3 | 224.1 | 176.1 | 238.6 | 216.3 | 248.9 | 310.6
1947.1 | 1839.1 | 185.5 | 88.8 | 223.7 | 175.5 | 238.4 | 215.9 | 248.4 | 310.2
1948.1 | 1840.1 | 185.3 | 88.6 | 223.3 | 175.3 | 238.4 | 215.4 | 248 | 309.9
1949.1 | 1841.1 | 184.9 | 88.3 | 223 | 174.9 | 237.8 | 215 | 247.6 | 309.6
1950.1 | 1842.1 | 184.7 | 87.8 | 222.7 | 174.6 | 237.2 | 214.6 | 247.2 | 309.2
1951.1 | 1843.1 | 184.5 | 86.6 | 222 | 174.1 | 236.9 | 214.1 | 246.7 | 308.9
1952.1 | 1844.1 | 184.2 | 86 | 221.6 | 173.3 | 237 | 213.7 | 246.3 | 308.6
1953.1 | 1845.1 | 183.9 | 85.6 | 221.8 | 172.9 | 236.9 | 213.2 | 245.9 | 308.3
1954.1 | 1846.1 | 183.7 | 85.8 | 220.9 | 172.9 | 236.5 | 212.8 | 245.4 | 308
1955.1 | 1847.1 | 183.4 | 86.1 | 219.1 | 173.1 | 237.2 | 212.5 | 245 | 307.6
1956.1 | 1848.1 | 183.1 | 85.7 | 218.5 | 173.2 | 237 | 212.1 | 244.5 | 307.2
1957.1 | 1849.1 | 182.8 | 85.5 | 217.9 | 173.2 | 237.8 | 211.6 | 244.1 | 306.8
1958.1 | 1850.1 | 182.5 | 86.2 | 217.1 | 173 | 237.7 | 211.2 | 243.7 | 306.4
1959.1 | 1851.1 | 182.3 | 87 | 216.1 | 173 | 237.8 | 210.9 | 243.2 | 306.1
1960.1 | 1852.1 | 182.1 | 88 | 216.4 | 172.9 | 238.3 | 210.5 | 242.8 | 305.8
1961.1 | 1853.1 | 181.9 | 88.3 | 216.9 | 173 | 238.4 | 210.1 | 242.4 | 305.5
1962.1 | 1854.1 | 181.7 | 88.5 | 216.4 | 172.9 | 237.9 | 209.8 | 241.9 | 305.3
1963.1 | 1855.1 | 181.5 | 89.4 | 216.1 | 172.6 | 237.6 | 209.4 | 241.4 | 304.9
1964.1 | 1856.1 | 181.3 | 91 | 217.6 | 172.4 | 237.2 | 209 | 241 | 304.6
1965.1 | 1857.1 | 181.1 | 92.7 | 219.3 | 171.5 | 237.5 | 208.6 | 240.5 | 304.3
1966.1 | 1858.1 | 180.9 | 92.3 | 220.4 | 171.7 | 238.4 | 208.2 | 240.1 | 304
1967.1 | 1859.1 | 180.7 | 92.6 | 221.2 | 171.5 | 238.7 | 207.8 | 239.6 | 303.7
1968.1 | 1860.1 | 180.4 | 92.7 | 221.9 | 171.2 | 238.2 | 207.4 | 239.1 | 303.5
1969.1 | 1861.1 | 180.1 | 93.8 | 222.4 | 171.2 | 238.1 | 207 | 238.7 | 303.1
1970.1 | 1862.1 | 179.9 | 94.9 | 223.1 | 172.1 | 237.9 | 206.6 | 238.2 | 302.7
1971.1 | 1863.1 | 179.7 | 94.6 | 223.9 | 172.8 | 237.3 | 206.2 | 237.7 | 302.5
1972.1 | 1864.1 | 179.5 | 94.7 | 224.2 | 172.3 | 236.9 | 205.9 | 237.3 | 302.2
1973.1 | 1865.1 | 179.3 | 94.2 | 224 | 171.6 | 236.9 | 205.5 | 236.9 | 301.9
1974.1 | 1866.1 | 179.1 | 94.4 | 223.7 | 171.3 | 236.6 | 205.1 | 236.4 | 301.6
1975.1 | 1867.1 | 178.9 | 93.8 | 223.9 | 170.4 | 236 | 204.8 | 236 | 301.2
1976.1 | 1868.1 | 178.7 | 95.4 | 223.8 | 169.7 | 235.9 | 204.4 | 235.5 | 300.9
1977.1 | 1869.1 | 178.5 | 95.7 | 223.7 | 169.2 | 236.6 | 204.1 | 235.1 | 300.5
1978.1 | 1870.1 | 178.2 | 95 | 223.6 | 168.7 | 236.4 | 203.8 | 234.6 | 300.2
1979.1 | 1871.1 | 177.9 | 94.5 | 224 | 168.6 | 236.9 | 203.4 | 234.2 | 299.8
1980.1 | 1872.1 | 177.7 | 95.7 | 224.2 | 169.5 | 237.3 | 203.1 | 233.7 | 299.5
1981.1 | 1873.1 | 177.5 | 97.2 | 224.2 | 170.1 | 237.7 | 202.8 | 233.3 | 299.2
1982.1 | 1874.1 | 177.3 | 98 | 224.2 | 169.9 | 237.2 | 202.5 | 232.8 | 299
1983.1 | 1875.1 | 177.1 | 99.2 | 223.7 | 169.7 | 237.6 | 202.2 | 232.4 | 298.7
1984.1 | 1876.1 | 176.9 | 100.3 | 223.7 | 170.3 | 238.5 | 201.9 | 231.9 | 298.4
1985.1 | 1877.1 | 176.7 | 101.3 | 223.6 | 170.3 | 239.1 | 201.6 | 231.4 | 298.2
1986.1 | 1878.1 | 176.4 | 102.4 | 223.8 | 170.1 | 239.1 | 201.3 | 231 | 297.9
1987.1 | 1879.1 | 176.3 | 103.1 | 224 | 169.9 | 239.2 | 201 | 230.5 | 297.6
1988.1 | 1880.1 | 176.1 | 102.5 | 224.2 | 169.7 | 239.7 | 200.6 | 230.1 | 297.3
1989.1 | 1881.1 | 176 | 100.8 | 224.4 | 169.4 | 240 | 200.3 | 229.6 | 297
1990.1 | 1882.1 | 175.8 | 100.5 | 224.2 | 170.4 | 240.5 | 200 | 229.2 | 296.7
1991.1 | 1883.1 | 175.5 | 101 | 224 | 170.7 | 240.3 | 199.6 | 228.7 | 296.2
1992.1 | 1884.1 | 175.3 | 101.3 | 223.6 | 172 | 240.6 | 199.3 | 228.3 | 295.9
1993.1 | 1885.1 | 175.1 | 103.4 | 223.6 | 172.4 | 240.4 | 198.9 | 227.9 | 295.5
1994.1 | 1886.1 | 174.9 | 103.1 | 223.2 | 173 | 240.6 | 198.6 | 227.4 | 295.2
1995.1 | 1887.1 | 174.6 | 102.2 | 223.2 | 173.4 | 240.7 | 198.2 | 227 | 294.8
1996.1 | 1888.1 | 174.5 | 101.3 | 223.2 | 172.4 | 240.4 | 197.8 | 226.6 | 294.5
1997.1 | 1889.1 | 174.3 | 101.2 | 222.6 | 171.2 | 240 | 197.4 | 226.2 | 294.3
1998.1 | 1890.1 | 174.2 | 101.3 | 222 | 171.8 | 239.9 | 197.1 | 225.8 | 294
1999.1 | 1891.1 | 174 | 99.9 | 221.4 | 172.4 | 239.9 | 196.7 | 225.4 | 293.6
2000.1 | 1892.1 | 173.8 | 98.1 | 220.4 | 172 | 240.1 | 196.3 | 224.9 | 293.2
2001.1 | 1893.1 | 173.7 | 97.4 | 220.2 | 172.8 | 240.1 | 195.9 | 224.5 | 292.8
2002.1 | 1894.1 | 173.5 | 97.2 | 220.3 | 172 | 240 | 195.6 | 224 | 292.5
2003.1 | 1895.1 | 173.3 | 95.7 | 219.9 | 172.2 | 239.4 | 195.2 | 223.6 | 292.2
2004.1 | 1896.1 | 173.1 | 94.7 | 218.9 | 171.5 | 239.4 | 194.8 | 223.2 | 291.8
2005.1 | 1897.1 | 173 | 94.6 | 218.6 | 170.8 | 239.5 | 194.4 | 222.7 | 291.5
2006.1 | 1898.1 | 172.7 | 94.8 | 218.3 | 170.4 | 239.1 | 194 | 222.3 | 291.1
2007.1 | 1899.1 | 172.5 | 95 | 218.3 | 169.7 | 238.2 | 193.6 | 221.9 | 290.8
2008.1 | 1900.1 | 172.3 | 95.8 | 217.9 | 169.1 | 237 | 193.2 | 221.4 | 290.6
2009.1 | 1901.1 | 172.1 | 95.5 | 217.6 | 168.8 | 236.1 | 192.8 | 221 | 290.3
2010.1 | 1902.1 | 172 | 95.2 | 217.8 | 168.2 | 235.2 | 192.3 | 220.6 | 290
2011.1 | 1903.1 | 171.8 | 95.1 | 217.6 | 168 | 234.5 | 191.9 | 220.2 | 289.7
2012.1 | 1904.1 | 171.5 | 95 | 217.4 | 166.6 | 234.4 | 191.5 | 219.7 | 289.4
2013.1 | 1905.1 | 171.2 | 95.1 | 217.1 | 166 | 234.4 | 191 | 219.3 | 289.1
2014.1 | 1906.1 | 171 | 95 | 216.7 | 165.7 | 234 | 190.6 | 218.9 | 288.9
2015.1 | 1907.1 | 170.9 | 94.1 | 216.8 | 165.8 | 233.6 | 190.2 | 218.4 | 288.6
2016.1 | 1908.1 | 170.7 | 93.5 | 217.1 | 165.5 | 233.2 | 189.8 | 218 | 288.2
2017.1 | 1909.1 | 170.5 | 93.4 | 217.3 | 164.4 | 233 | 189.4 | 217.6 | 287.8
2018.1 | 1910.1 | 170.3 | 94.3 | 217 | 163.3 | 233.1 | 189 | 217.2 | 287.4
2019.1 | 1911.1 | 170.1 | 93.4 | 216.8 | 162.2 | 233 | 188.6 | 216.7 | 287
2020.1 | 1912.1 | 169.8 | 91.8 | 216.8 | 161 | 231.9 | 188.2 | 216.3 | 286.7
2021.1 | 1913.1 | 169.6 | 90.5 | 216.6 | 160.2 | 231 | 187.8 | 215.9 | 286.4
2022.1 | 1914.1 | 169.4 | 89.6 | 216.3 | 159.4 | 230.6 | 187.4 | 215.5 | 286.1
2023.1 | 1915.1 | 169.2 | 89.1 | 215.9 | 158.6 | 230.3 | 187 | 215 | 285.9
2024.1 | 1916.1 | 169.1 | 89.3 | 216.1 | 157.7 | 229.4 | 186.6 | 214.6 | 285.7
2025.1 | 1917.1 | 168.9 | 89.2 | 216.1 | 156.8 | 228.8 | 186.2 | 214.2 | 285.4
2026.1 | 1918.1 | 168.7 | 88.8 | 215.9 | 155.8 | 228.3 | 185.8 | 213.7 | 285.1
2027.1 | 1919.1 | 168.4 | 88.6 | 215.7 | 155.4 | 228 | 185.4 | 213.3 | 284.7
2028.1 | 1920.1 | 168.2 | 88.5 | 215.3 | 155.7 | 227.8 | 185.1 | 212.8 | 284.4
2029.1 | 1921.1 | 168 | 88.7 | 214.7 | 155.3 | 227.4 | 184.7 | 212.4 | 284
2030.1 | 1922.1 | 167.8 | 89.6 | 214.3 | 154.4 | 226.5 | 184.3 | 211.9 | 283.6
2031.1 | 1923.1 | 167.6 | 88.4 | 214.1 | 153.7 | 225.7 | 183.9 | 211.5 | 283.4
2032.1 | 1924.1 | 167.4 | 87.6 | 213.5 | 152.9 | 225.1 | 183.5 | 211.1 | 283.2
2033.1 | 1925.1 | 167.1 | 86.6 | 212.6 | 152.1 | 224.3 | 183.1 | 210.6 | 283
2034.1 | 1926.1 | 166.9 | 85.5 | 212.7 | 151.6 | 224.1 | 182.7 | 210.2 | 282.8
2035.1 | 1927.1 | 166.7 | 84.9 | 212.3 | 151 | 223.4 | 182.3 | 209.7 | 282.6
2036.1 | 1928.1 | 166.5 | 85.1 | 211.5 | 150.7 | 222.7 | 181.8 | 209.3 | 282.3
2037.1 | 1929.1 | 166.3 | 86 | 210.9 | 150.2 | 221.9 | 181.4 | 208.8 | 282
2038.1 | 1930.1 | 166.2 | 86.6 | 210.7 | 149.8 | 221 | 180.9 | 208.4 | 281.8
2039.1 | 1931.1 | 166 | 86.7 | 210 | 149.9 | 220.8 | 180.5 | 208 | 281.6
2040.1 | 1932.1 | 165.7 | 86 | 209 | 150 | 220.8 | 180.1 | 207.5 | 281.4
2041.1 | 1933.1 | 165.6 | 86.7 | 208 | 149.7 | 220.4 | 179.6 | 207.1 | 281.2
2042.1 | 1934.1 | 165.4 | 87.1 | 207.1 | 149.5 | 220.3 | 179.2 | 206.6 | 281
2043.1 | 1935.1 | 165.3 | 86.5 | 206 | 149.7 | 220.7 | 178.8 | 206.2 | 280.8
2044.1 | 1936.1 | 165.1 | 85.4 | 205.4 | 149.8 | 220.7 | 178.4 | 205.7 | 280.5
2045.1 | 1937.1 | 165 | 84.8 | 204.7 | 149.5 | 220.6 | 178 | 205.3 | 280.3
2046.1 | 1938.1 | 164.8 | 84.5 | 203.7 | 149.1 | 220.3 | 177.7 | 204.8 | 280
2047.1 | 1939.1 | 164.5 | 84.8 | 202.9 | 149.2 | 219.6 | 177.3 | 204.4 | 279.7
2048.1 | 1940.1 | 164.3 | 84.7 | 202.1 | 149.5 | 219.6 | 176.9 | 204 | 279.4
2049.1 | 1941.1 | 164.1 | 85.7 | 201 | 149.7 | 219.7 | 176.5 | 203.5 | 279
2050.1 | 1942.1 | 163.9 | 85.9 | 200.1 | 149.8 | 219.3 | 176.1 | 203.1 | 278.6
2051.1 | 1943.1 | 163.6 | 86.1 | 199.7 | 149.4 | 219.1 | 175.7 | 202.6 | 278.3
2052.1 | 1944.1 | 163.4 | 86.9 | 199.1 | 149 | 219 | 175.3 | 202.2 | 278
2053.1 | 1945.1 | 163.3 | 86.9 | 198.2 | 148.9 | 218.4 | 174.9 | 201.8 | 277.7
2054.1 | 1946.1 | 163.1 | 85.7 | 197.7 | 149 | 218.1 | 174.5 | 201.3 | 277.4
2055.1 | 1947.1 | 162.9 | 84.4 | 197.3 | 148.1 | 217.4 | 174.1 | 200.9 | 277.1
2056.1 | 1948.1 | 162.7 | 84.9 | 196.9 | 147.5 | 216.5 | 173.7 | 200.4 | 276.8
2057.1 | 1949.1 | 162.5 | 84.5 | 196.3 | 147.2 | 215.9 | 173.3 | 200 | 276.5
2058.1 | 1950.1 | 162.3 | 84.9 | 195.9 | 146.9 | 215.1 | 173 | 199.5 | 276.2
2059.1 | 1951.1 | 162.2 | 84.2 | 195.8 | 146.3 | 214.6 | 172.6 | 199.1 | 275.8
2060.1 | 1952.1 | 162 | 84.7 | 195.6 | 146.1 | 214.8 | 172.3 | 198.7 | 275.5
2061.1 | 1953.1 | 161.8 | 84.9 | 195.7 | 146.1 | 214.7 | 171.9 | 198.3 | 275.1
2062.1 | 1954.1 | 161.6 | 84.7 | 196 | 145.7 | 214.1 | 171.6 | 197.9 | 274.8
2063.1 | 1955.1 | 161.5 | 83.6 | 196.1 | 145 | 213.2 | 171.2 | 197.5 | 274.5
2064.1 | 1956.1 | 161.4 | 82.7 | 196 | 144.6 | 212.5 | 170.9 | 197 | 274.1
2065.1 | 1957.1 | 161.3 | 82.1 | 195.8 | 144.5 | 211.9 | 170.5 | 196.6 | 273.8
2066.1 | 1958.1 | 161.1 | 81.3 | 196 | 144.2 | 211.2 | 170.2 | 196.2 | 273.5
2067.1 | 1959.1 | 160.9 | 80.5 | 195.4 | 144.1 | 210.5 | 169.9 | 195.8 | 273.2
2068.1 | 1960.1 | 160.7 | 80.3 | 195.2 | 143.5 | 209.9 | 169.5 | 195.4 | 272.9
2069.1 | 1961.1 | 160.6 | 80.1 | 195.3 | 142.9 | 209.6 | 169.2 | 195 | 272.7
2070.1 | 1962.1 | 160.4 | 79.3 | 194.9 | 142.8 | 208.9 | 168.8 | 194.6 | 272.5
2071.1 | 1963.1 | 160.3 | 78.7 | 194.4 | 142.7 | 208.3 | 168.5 | 194.2 | 272.3
2072.1 | 1964.1 | 160.1 | 77.8 | 194.3 | 142.4 | 207.7 | 168.1 | 193.8 | 272.1
2073.1 | 1965.1 | 159.9 | 77.3 | 194.2 | 142 | 206.9 | 167.8 | 193.4 | 272
2074.1 | 1966.1 | 159.8 | 76.8 | 193.4 | 141.5 | 206 | 167.5 | 192.9 | 271.7
2075.1 | 1967.1 | 159.5 | 76.7 | 192.7 | 141.2 | 204.7 | 167.2 | 192.5 | 271.5
2076.1 | 1968.1 | 159.3 | 77 | 192.1 | 141.1 | 203.7 | 166.9 | 192.1 | 271.2
2077.1 | 1969.1 | 159 | 76.6 | 191.2 | 140.9 | 203.7 | 166.5 | 191.7 | 270.9
2078.1 | 1970.1 | 158.8 | 76.6 | 190.3 | 140.9 | 203.8 | 166.2 | 191.3 | 270.5
2079.1 | 1971.1 | 158.5 | 78.6 | 189.8 | 140.7 | 202.9 | 165.9 | 190.9 | 270.1
2080.1 | 1972.1 | 158.3 | 78.6 | 189.2 | 140.7 | 201.9 | 165.6 | 190.5 | 269.8
2081.1 | 1973.1 | 158.2 | 78.9 | 188.3 | 140.6 | 202.1 | 165.3 | 190 | 269.5
2082.1 | 1974.1 | 158 | 78.4 | 187.9 | 140.3 | 201.9 | 165 | 189.6 | 269.1
2083.1 | 1975.1 | 157.9 | 77.5 | 187.4 | 139.9 | 201.8 | 164.7 | 189.2 | 268.8
2084.1 | 1976.1 | 157.7 | 77.4 | 187 | 139.6 | 201.9 | 164.3 | 188.8 | 268.4
2085.1 | 1977.1 | 157.5 | 78 | 186.4 | 139.2 | 201.2 | 164 | 188.4 | 268.1
2086.1 | 1978.1 | 157.4 | 78.5 | 185.8 | 139.2 | 200.6 | 163.6 | 188 | 267.7
2087.1 | 1979.1 | 157.2 | 79.7 | 185.5 | 139.4 | 201 | 163.2 | 187.6 | 267.5
2088.1 | 1980.1 | 157.1 | 81.3 | 185.2 | 141 | 201.5 | 162.9 | 187.2 | 267.1
2089.1 | 1981.1 | 156.9 | 81.4 | 185.4 | 141.1 | 201.5 | 162.6 | 186.8 | 266.7
2090.1 | 1982.1 | 156.7 | 82.2 | 185.4 | 141.5 | 201.7 | 162.2 | 186.4 | 266.4
2091.1 | 1983.1 | 156.6 | 83.4 | 185.3 | 141.8 | 202 | 161.9 | 186.1 | 266
2092.1 | 1984.1 | 156.4 | 84.1 | 185.4 | 142.1 | 202.6 | 161.6 | 185.7 | 265.7
2093.1 | 1985.1 | 156.2 | 84.8 | 185.6 | 142.3 | 202.9 | 161.3 | 185.3 | 265.4
2094.1 | 1986.1 | 156 | 84.6 | 186 | 143.1 | 203.2 | 161.1 | 184.9 | 265.1
2095.1 | 1987.1 | 155.8 | 83.7 | 186.1 | 143.4 | 204.1 | 160.8 | 184.5 | 264.8
2096.1 | 1988.1 | 155.7 | 83.2 | 186 | 143.6 | 204.4 | 160.5 | 184.1 | 264.7
2097.1 | 1989.1 | 155.5 | 83 | 186.3 | 143.4 | 204.6 | 160.2 | 183.7 | 264.5
2098.1 | 1990.1 | 155.4 | 83 | 186.4 | 143.8 | 204.7 | 159.9 | 183.3 | 264.3
2099.1 | 1991.1 | 155.2 | 83.1 | 186.3 | 144 | 204.9 | 159.6 | 182.9 | 264.1
2100.1 | 1992.1 | 155.1 | 83.7 | 186.1 | 143.7 | 205.1 | 159.3 | 182.5 | 263.9
2101.1 | 1993.1 | 154.9 | 84.1 | 186.3 | 144.5 | 204.9 | 159 | 182.2 | 263.7
2102.1 | 1994.1 | 154.8 | 84.9 | 186.2 | 145.5 | 205.4 | 158.6 | 181.8 | 263.4
2103.1 | 1995.1 | 154.6 | 85.9 | 185.9 | 146.1 | 205.5 | 158.3 | 181.4 | 263.1
2104.1 | 1996.1 | 154.4 | 87.6 | 186 | 144.8 | 205.3 | 158 | 181 | 262.9
2105.1 | 1997.1 | 154.3 | 87.8 | 186 | 144.9 | 205.5 | 157.6 | 180.7 | 262.6
2106.1 | 1998.1 | 154.2 | 87.8 | 185.7 | 145.4 | 205.9 | 157.3 | 180.3 | 262.3
2107.1 | 1999.1 | 154.1 | 88.1 | 186 | 145.7 | 205.5 | 157 | 180 | 261.9
2108.1 | 2000.1 | 153.9 | 87.7 | 186.2 | 146.6 | 205.2 | 156.6 | 179.6 | 261.6
2109.1 | 2001.1 | 153.8 | 87.3 | 186.2 | 146.8 | 205.3 | 156.3 | 179.3 | 261.3
2110.1 | 2002.1 | 153.5 | 86.7 | 186.2 | 147.2 | 205.7 | 156 | 179 | 261.1
2111.1 | 2003.1 | 153.3 | 86.9 | 186.2 | 146.8 | 205.7 | 155.6 | 178.6 | 260.8
2112.1 | 2004.1 | 153.1 | 85.5 | 186.3 | 145.8 | 205.8 | 155.3 | 178.3 | 260.5
2113.1 | 2005.1 | 153 | 84.7 | 186.4 | 144.4 | 205.8 | 155 | 178 | 260.2
2114.1 | 2006.1 | 152.8 | 84.6 | 186.3 | 143.3 | 205.4 | 154.6 | 177.6 | 259.8
2115.1 | 2007.1 | 152.5 | 84.6 | 186.3 | 142.8 | 205.2 | 154.3 | 177.3 | 259.5
2116.1 | 2008.1 | 152.3 | 83.7 | 185.9 | 142.8 | 205.1 | 154 | 177 | 259.1
2117.1 | 2009.1 | 152.1 | 82.9 | 185.8 | 141.8 | 204.6 | 153.6 | 176.6 | 258.8
2118.1 | 2010.1 | 152 | 82.3 | 185.7 | 141.2 | 203.9 | 153.3 | 176.3 | 258.5
2119.1 | 2011.1 | 151.7 | 81.8 | 185.3 | 140.3 | 203.6 | 152.9 | 175.9 | 258.2
2120.1 | 2012.1 | 151.5 | 80.3 | 184.8 | 139.6 | 203.2 | 152.6 | 175.6 | 258
2121.1 | 2013.1 | 151.4 | 78.9 | 184.5 | 139.3 | 202.3 | 152.3 | 175.3 | 257.8
2122.1 | 2014.1 | 151.2 | 78.2 | 184.3 | 138.4 | 201.2 | 151.9 | 174.9 | 257.5
2123.1 | 2015.1 | 151.1 | 78.3 | 183.6 | 137.7 | 200.6 | 151.6 | 174.6 | 257.3
2124.1 | 2016.1 | 150.9 | 78.2 | 183 | 137.1 | 200 | 151.2 | 174.2 | 257.1
2125.1 | 2017.1 | 150.7 | 77.7 | 182.5 | 136.7 | 199.6 | 150.9 | 173.9 | 256.8
2126.1 | 2018.1 | 150.6 | 78 | 181.7 | 136.8 | 199.2 | 150.5 | 173.5 | 256.5
2127.1 | 2019.1 | 150.4 | 78.8 | 180.7 | 136.8 | 198.8 | 150.2 | 173.2 | 256.3
2128.1 | 2020.1 | 150.2 | 78.5 | 180 | 136.3 | 198 | 149.9 | 172.8 | 256
2129.1 | 2021.1 | 150 | 77.2 | 179.7 | 135.9 | 196.9 | 149.5 | 172.5 | 255.8
2130.1 | 2022.1 | 149.9 | 76.3 | 179.2 | 135.6 | 196.2 | 149.2 | 172.1 | 255.5
2131.1 | 2023.1 | 149.7 | 75.7 | 179 | 134.9 | 195.6 | 148.9 | 171.8 | 255.3
2132.1 | 2024.1 | 149.6 | 74.4 | 178.5 | 134.5 | 194.8 | 148.6 | 171.4 | 255
2133.1 | 2025.1 | 149.4 | 74 | 177.8 | 133.8 | 193.8 | 148.2 | 171.1 | 254.7
2134.1 | 2026.1 | 149.2 | 73.2 | 177.1 | 133.5 | 193.1 | 148 | 170.7 | 254.5
2135.1 | 2027.1 | 149 | 72.5 | 177 | 133.1 | 192.5 | 147.6 | 170.4 | 254.3
2136.1 | 2028.1 | 148.9 | 71.8 | 176.8 | 132.5 | 191.9 | 147.3 | 170.1 | 254
2137.1 | 2029.1 | 148.7 | 71.6 | 176.2 | 132.1 | 191.5 | 147 | 169.7 | 253.8
2138.1 | 2030.1 | 148.6 | 71.4 | 175.6 | 131.8 | 191.1 | 146.7 | 169.4 | 253.6
2139.1 | 2031.1 | 148.4 | 71.6 | 175 | 131.8 | 190.9 | 146.4 | 169.1 | 253.2
2140.1 | 2032.1 | 148.2 | 72 | 174.4 | 131.8 | 190.2 | 146.1 | 168.7 | 253
2141.1 | 2033.1 | 148 | 72.8 | 173.6 | 131.8 | 190 | 145.8 | 168.4 | 252.7
2142.1 | 2034.1 | 147.8 | 73.3 | 173 | 132 | 190.3 | 145.6 | 168.1 | 252.3
2143.1 | 2035.1 | 147.6 | 72.9 | 172.8 | 131.8 | 190 | 145.2 | 167.7 | 252.1
2144.1 | 2036.1 | 147.4 | 73.7 | 171.9 | 132 | 190.3 | 144.9 | 167.4 | 251.9
2145.1 | 2037.1 | 147.3 | 74.5 | 171.2 | 132.1 | 190 | 144.7 | 167.1 | 251.6
2146.1 | 2038.1 | 147.1 | 75.8 | 170.7 | 132.1 | 190.2 | 144.4 | 166.7 | 251.4
2147.1 | 2039.1 | 146.9 | 76.5 | 170 | 131.6 | 190.1 | 144.1 | 166.4 | 251.2
2148.1 | 2040.1 | 146.8 | 75.6 | 169.1 | 131.8 | 190.5 | 143.8 | 166.1 | 250.9
2149.1 | 2041.1 | 146.6 | 74.6 | 168.6 | 132.1 | 190.6 | 143.6 | 165.7 | 250.6
2150.1 | 2042.1 | 146.4 | 74.4 | 168.3 | 131.8 | 190.4 | 143.3 | 165.4 | 250.4
2151.1 | 2043.1 | 146.2 | 75.3 | 167.7 | 131.5 | 190.4 | 143 | 165.1 | 250.1
2152.1 | 2044.1 | 146 | 76.5 | 167.1 | 130.8 | 190.2 | 142.8 | 164.8 | 249.8
2153.1 | 2045.1 | 145.9 | 76.3 | 166.6 | 130.8 | 190.1 | 142.6 | 164.5 | 249.5
2154.1 | 2046.1 | 145.9 | 75.5 | 166.7 | 130.8 | 190 | 142.3 | 164.1 | 249.2
2155.1 | 2047.1 | 145.8 | 74.6 | 166.4 | 131.6 | 189.8 | 142.1 | 163.9 | 248.8
2156.1 | 2048.1 | 145.7 | 75.5 | 166.3 | 131.6 | 189.7 | 141.8 | 163.6 | 248.5
2157.1 | 2049.1 | 145.5 | 76.4 | 166.4 | 131.3 | 189.7 | 141.6 | 163.3 | 248.2
2158.1 | 2050.1 | 145.4 | 75.5 | 166.2 | 131.5 | 189.7 | 141.3 | 163 | 248
2159.1 | 2051.1 | 145.3 | 74.7 | 166.3 | 132.1 | 189.8 | 141.1 | 162.7 | 247.8
2160.1 | 2052.1 | 145.1 | 74 | 166.3 | 132.4 | 189.6 | 140.8 | 162.4 | 247.6
2161.1 | 2053.1 | 144.9 | 73.4 | 166.4 | 132.1 | 189.4 | 140.6 | 162.1 | 247.3
2162.1 | 2054.1 | 144.7 | 72.8 | 166.3 | 131.6 | 189.1 | 140.4 | 161.8 | 247.1
2163.1 | 2055.1 | 144.5 | 73 | 166.1 | 131 | 188.9 | 140.1 | 161.5 | 246.9
2164.1 | 2056.1 | 144.3 | 73.1 | 166.1 | 130.5 | 188.6 | 139.9 | 161.2 | 246.6
2165.1 | 2057.1 | 144.1 | 72.6 | 165.9 | 129.9 | 188.4 | 139.6 | 160.9 | 246.4
2166.1 | 2058.1 | 144 | 73.2 | 165.6 | 129.6 | 187.8 | 139.4 | 160.6 | 246.3
2167.1 | 2059.1 | 143.8 | 74.6 | 165.5 | 129.8 | 187.1 | 139.1 | 160.3 | 246
2168.1 | 2060.1 | 143.6 | 76 | 165.2 | 130.1 | 187 | 138.8 | 160 | 245.6
2169.1 | 2061.1 | 143.5 | 77.3 | 164.9 | 130.8 | 186.8 | 138.6 | 159.8 | 245.3
2170.1 | 2062.1 | 143.4 | 76.5 | 164.9 | 130.9 | 186.6 | 138.3 | 159.5 | 245.1
2171.1 | 2063.1 | 143.2 | 76.2 | 164.8 | 131 | 186.1 | 138 | 159.2 | 244.8
2172.1 | 2064.1 | 143.1 | 76.1 | 164.4 | 131.3 | 185.7 | 137.8 | 159 | 244.6
2173.1 | 2065.1 | 143 | 76.1 | 163.8 | 130.6 | 185.7 | 137.6 | 158.7 | 244.3
2174.1 | 2066.1 | 142.7 | 76 | 163.3 | 130.8 | 185.6 | 137.3 | 158.4 | 243.9
2175.1 | 2067.1 | 142.5 | 76 | 163 | 130.3 | 185.1 | 137.1 | 158.2 | 243.5
2176.1 | 2068.1 | 142.4 | 76.1 | 162.7 | 129.7 | 184.5 | 136.9 | 157.9 | 243.2
2177.1 | 2069.1 | 142.3 | 76.2 | 162.3 | 129.1 | 184 | 136.6 | 157.6 | 243
2178.1 | 2070.1 | 142.2 | 76.2 | 162.1 | 129 | 183.9 | 136.3 | 157.3 | 242.7
2179.1 | 2071.1 | 142 | 76.2 | 161.6 | 128.7 | 183.9 | 136.1 | 157 | 242.6
2180.1 | 2072.1 | 141.9 | 76.3 | 161.2 | 128.1 | 183.4 | 135.8 | 156.7 | 242.3
2181.1 | 2073.1 | 141.8 | 76.4 | 161.1 | 127.6 | 182.7 | 135.6 | 156.4 | 242.1
2182.1 | 2074.1 | 141.6 | 76 | 160.8 | 127.4 | 182.1 | 135.3 | 156.2 | 241.9
2183.1 | 2075.1 | 141.4 | 75.8 | 160.7 | 127 | 181.8 | 135.1 | 155.9 | 241.8
2184.1 | 2076.1 | 141.3 | 74.9 | 160.7 | 126.4 | 180.7 | 134.9 | 155.6 | 241.6
2185.1 | 2077.1 | 141.1 | 74.2 | 160.6 | 126.5 | 179.9 | 134.6 | 155.3 | 241.4
2186.1 | 2078.1 | 140.9 | 74.9 | 160 | 127.2 | 179.6 | 134.4 | 155 | 241.3
2187.1 | 2079.1 | 140.8 | 74.9 | 159.4 | 127.1 | 179.2 | 134.1 | 154.7 | 241.1
2188.1 | 2080.1 | 140.7 | 74.8 | 159.2 | 126.9 | 178.7 | 133.9 | 154.5 | 240.8
2189.1 | 2081.1 | 140.6 | 74 | 158.9 | 126.9 | 178.3 | 133.6 | 154.2 | 240.6
2190.1 | 2082.1 | 140.4 | 73.3 | 158.3 | 126.8 | 178.5 | 133.4 | 153.9 | 240.4
2191.1 | 2083.1 | 140.3 | 72.8 | 158 | 126.6 | 178.5 | 133.1 | 153.6 | 240.2
2192.1 | 2084.1 | 140.2 | 72.3 | 157.5 | 126.2 | 178.3 | 132.8 | 153.3 | 239.9
2193.1 | 2085.1 | 140.1 | 71.4 | 157 | 125.8 | 178.3 | 132.6 | 153.1 | 239.6
2194.1 | 2086.1 | 139.9 | 71.5 | 156.9 | 125.2 | 177.8 | 132.3 | 152.8 | 239.3
2195.1 | 2087.1 | 139.8 | 71.6 | 156.7 | 124.6 | 177.2 | 132.1 | 152.5 | 239.1
2196.1 | 2088.1 | 139.7 | 71.4 | 156.5 | 124 | 176.4 | 131.9 | 152.3 | 239
2197.1 | 2089.1 | 139.5 | 71.9 | 156.1 | 124.4 | 176.7 | 131.7 | 152 | 238.8
2198.1 | 2090.1 | 139.3 | 71.3 | 156.1 | 125 | 176.5 | 131.5 | 151.8 | 238.6
2199.1 | 2091.1 | 139.2 | 70.7 | 155.9 | 125.4 | 176.4 | 131.2 | 151.5 | 238.4
2200.1 | 2092.1 | 139 | 71.2 | 155.4 | 126 | 176.2 | 131 | 151.3 | 238.1
2201.1 | 2093.1 | 138.8 | 70.9 | 155.4 | 125.7 | 175.9 | 130.8 | 151 | 237.9
2202.1 | 2094.1 | 138.6 | 70.6 | 155.6 | 124.9 | 175.6 | 130.6 | 150.8 | 237.8
2203.1 | 2095.1 | 138.4 | 71.3 | 155.5 | 125.2 | 175.6 | 130.4 | 150.5 | 237.5
2204.1 | 2096.1 | 138.3 | 71.8 | 155.3 | 125.4 | 175.8 | 130.2 | 150.3 | 237.2
2205.1 | 2097.1 | 138.2 | 72 | 155.3 | 126 | 175.6 | 130 | 150 | 236.9
2206.1 | 2098.1 | 138 | 71.8 | 155.8 | 125.8 | 175.5 | 129.8 | 149.8 | 236.6
2207.1 | 2099.1 | 137.9 | 72.6 | 156.1 | 125.6 | 175.8 | 129.5 | 149.5 | 236.4
2208.1 | 2100.1 | 137.7 | 72.5 | 156.2 | 125.6 | 175.7 | 129.3 | 149.3 | 236.1
2209.1 | 2101.1 | 137.6 | 73 | 156.3 | 126.9 | 175.6 | 129.1 | 149.1 | 235.9
2210.1 | 2102.1 | 137.5 | 73.2 | 156.5 | 127.1 | 175.8 | 128.8 | 148.8 | 235.8
2211.1 | 2103.1 | 137.4 | 73.1 | 156.5 | 126.5 | 176 | 128.6 | 148.6 | 235.6
2212.1 | 2104.1 | 137.2 | 72.8 | 156.6 | 126.5 | 176.1 | 128.4 | 148.4 | 235.4
2213.1 | 2105.1 | 137 | 72.8 | 156.7 | 126.3 | 176.3 | 128.1 | 148.1 | 235.2
2214.1 | 2106.1 | 136.9 | 72.3 | 156.5 | 126.4 | 176.6 | 127.9 | 147.9 | 235
2215.1 | 2107.1 | 136.8 | 72 | 156.1 | 126.5 | 176.9 | 127.7 | 147.7 | 234.8
2216.1 | 2108.1 | 136.6 | 71.8 | 156 | 126.8 | 176.9 | 127.4 | 147.5 | 234.7
2217.1 | 2109.1 | 136.5 | 70.9 | 155.6 | 127.5 | 177 | 127.2 | 147.2 | 234.5
2218.1 | 2110.1 | 136.3 | 71 | 155 | 127.7 | 177 | 127 | 147 | 234.3
2219.1 | 2111.1 | 136.2 | 70.8 | 154.7 | 127.6 | 176.8 | 126.8 | 146.8 | 234.1
2220.1 | 2112.1 | 136.1 | 72.4 | 154.8 | 127.4 | 176.6 | 126.6 | 146.6 | 234
2221.1 | 2113.1 | 136 | 73.6 | 154.7 | 127.4 | 176.6 | 126.4 | 146.4 | 233.9
2222.1 | 2114.1 | 135.8 | 75.1 | 154.9 | 127 | 176.5 | 126.2 | 146.2 | 233.7
2223.1 | 2115.1 | 135.7 | 75 | 155.1 | 126.7 | 176.4 | 126 | 146 | 233.7
2224.1 | 2116.1 | 135.5 | 73.6 | 155 | 126.4 | 176.5 | 125.9 | 145.8 | 233.6
2225.1 | 2117.1 | 135.4 | 72.8 | 154.4 | 126.2 | 176.6 | 125.7 | 145.6 | 233.5
2226.1 | 2118.1 | 135.2 | 72.2 | 153.9 | 126.1 | 176.6 | 125.5 | 145.4 | 233.3
2227.1 | 2119.1 | 135.1 | 72.9 | 153.8 | 126.1 | 176.3 | 125.3 | 145.2 | 233.2
2228.1 | 2120.1 | 134.9 | 74 | 153.8 | 125.8 | 175.9 | 125.1 | 145 | 232.9
2229.1 | 2121.1 | 134.8 | 73.5 | 153.7 | 125.2 | 175.4 | 124.9 | 144.7 | 232.7
2230.1 | 2122.1 | 134.7 | 74 | 153.6 | 125.8 | 175.1 | 124.7 | 144.5 | 232.6
2231.1 | 2123.1 | 134.5 | 74.5 | 153.4 | 126 | 175 | 124.5 | 144.3 | 232.3
2232.1 | 2124.1 | 134.4 | 74.7 | 153.1 | 125.2 | 174.8 | 124.3 | 144.1 | 232.2
2233.1 | 2125.1 | 134.2 | 74.8 | 153 | 124.3 | 174.4 | 124.1 | 143.9 | 231.9
2234.1 | 2126.1 | 134 | 75.1 | 152.5 | 123.9 | 174.1 | 123.9 | 143.6 | 231.7
2235.1 | 2127.1 | 133.9 | 74.7 | 151.9 | 123.5 | 173.8 | 123.8 | 143.4 | 231.5
2236.1 | 2128.1 | 133.8 | 74.6 | 151.9 | 123.2 | 173.4 | 123.6 | 143.2 | 231.3
2237.1 | 2129.1 | 133.7 | 74.6 | 152.1 | 123.6 | 173 | 123.4 | 143 | 231.1
2238.1 | 2130.1 | 133.5 | 75 | 152 | 123.4 | 172.8 | 123.2 | 142.8 | 230.8
2239.1 | 2131.1 | 133.4 | 75.1 | 151.5 | 123 | 173 | 123 | 142.6 | 230.6
2240.1 | 2132.1 | 133.3 | 74.5 | 151.2 | 122.7 | 172.9 | 122.9 | 142.4 | 230.4
2241.1 | 2133.1 | 133.1 | 73.4 | 151.1 | 122.8 | 172.5 | 122.7 | 142.2 | 230.2
2242.1 | 2134.1 | 132.9 | 73.9 | 150.8 | 122.9 | 172.7 | 122.5 | 141.9 | 230
2243.1 | 2135.1 | 132.8 | 74.7 | 150.6 | 122.9 | 172.5 | 122.3 | 141.7 | 229.7
2244.1 | 2136.1 | 132.6 | 75.5 | 150.5 | 122.8 | 172.3 | 122.1 | 141.5 | 229.4
2245.1 | 2137.1 | 132.5 | 77 | 150.6 | 122.4 | 172.2 | 121.9 | 141.3 | 229.1
2246.1 | 2138.1 | 132.4 | 77.2 | 150.4 | 123.1 | 172.6 | 121.7 | 141.1 | 228.8
2247.1 | 2139.1 | 132.2 | 77.3 | 150.3 | 122.9 | 172.5 | 121.4 | 140.9 | 228.6
2248.1 | 2140.1 | 132.1 | 77.1 | 150.5 | 122.2 | 172.2 | 121.2 | 140.7 | 228.3
2249.1 | 2141.1 | 131.9 | 77 | 150.6 | 121.9 | 172.1 | 121 | 140.5 | 228
2250.1 | 2142.1 | 131.7 | 75.2 | 150.3 | 122.8 | 172.3 | 120.7 | 140.3 | 227.7
2251.1 | 2143.1 | 131.5 | 74.1 | 150.3 | 123.6 | 172.3 | 120.5 | 140.1 | 227.5
2252.1 | 2144.1 | 131.4 | 74.1 | 150.1 | 123.7 | 172.1 | 120.3 | 139.8 | 227.2
2253.1 | 2145.1 | 131.3 | 73.5 | 149.8 | 123.5 | 171.9 | 120.1 | 139.6 | 227.1
2254.1 | 2146.1 | 131.2 | 73.4 | 149.6 | 122.5 | 171.8 | 119.9 | 139.4 | 226.8
2255.1 | 2147.1 | 131.1 | 73.2 | 149.7 | 122 | 171.9 | 119.7 | 139.2 | 226.7
2256.1 | 2148.1 | 130.9 | 72.8 | 149.3 | 121.9 | 171.7 | 119.5 | 139 | 226.6
2257.1 | 2149.1 | 130.7 | 72.8 | 149 | 121.3 | 171.3 | 119.4 | 138.8 | 226.4
2258.1 | 2150.1 | 130.6 | 72.9 | 148.9 | 120.8 | 170.8 | 119.2 | 138.6 | 226.3
2259.1 | 2151.1 | 130.4 | 72.4 | 148.5 | 119.9 | 170.6 | 119 | 138.4 | 226.2
2260.1 | 2152.1 | 130.3 | 72 | 148.3 | 119.3 | 170.6 | 118.9 | 138.2 | 226
2261.1 | 2153.1 | 130.2 | 71.4 | 148.2 | 119.2 | 170.5 | 118.7 | 138 | 225.8
2262.1 | 2154.1 | 130.1 | 70 | 147.8 | 119.5 | 170.2 | 118.5 | 137.8 | 225.6
2263.1 | 2155.1 | 129.9 | 69.6 | 147.1 | 119.4 | 169.9 | 118.3 | 137.6 | 225.3
2264.1 | 2156.1 | 129.8 | 69.7 | 146.7 | 119 | 169.6 | 118.1 | 137.4 | 225
2265.1 | 2157.1 | 129.7 | 69.7 | 146.3 | 118.7 | 169.2 | 118 | 137.2 | 224.8
2266.1 | 2158.1 | 129.6 | 69.7 | 145.9 | 119.2 | 168.9 | 117.8 | 137 | 224.4
2267.1 | 2159.1 | 129.5 | 70.1 | 145.4 | 119.6 | 168.7 | 117.7 | 136.8 | 224.1
2268.1 | 2160.1 | 129.3 | 69.7 | 145.6 | 119.6 | 168.3 | 117.5 | 136.7 | 223.9
2269.1 | 2161.1 | 129.2 | 70.3 | 145.7 | 119.2 | 167.6 | 117.3 | 136.5 | 223.6
2270.1 | 2162.1 | 129.1 | 70.8 | 145.3 | 119.5 | 167.8 | 117.2 | 136.3 | 223.3
2271.1 | 2163.1 | 129 | 71 | 145.1 | 120.5 | 167.8 | 117 | 136.1 | 223
2272.1 | 2164.1 | 128.9 | 72 | 145 | 120.4 | 167.6 | 116.8 | 135.9 | 222.8
2273.1 | 2165.1 | 128.8 | 73.9 | 144.8 | 120.4 | 167.3 | 116.7 | 135.7 | 222.6
2274.1 | 2166.1 | 128.7 | 75.8 | 144.8 | 120 | 167.3 | 116.5 | 135.5 | 222.4
2275.1 | 2167.1 | 128.6 | 75.8 | 144.8 | 120.6 | 167.4 | 116.4 | 135.3 | 222.1
2276.1 | 2168.1 | 128.4 | 76.4 | 145 | 120.7 | 167.3 | 116.2 | 135.2 | 221.9
2277.1 | 2169.1 | 128.3 | 76.4 | 144.9 | 120.3 | 167.1 | 116.1 | 135 | 221.7
2278.1 | 2170.1 | 128.2 | 76.8 | 144.9 | 120.3 | 167 | 115.9 | 134.8 | 221.4
2279.1 | 2171.1 | 128.1 | 76.9 | 145 | 120.2 | 166.8 | 115.8 | 134.6 | 221.1
2280.1 | 2172.1 | 128 | 75.9 | 145.1 | 120.7 | 166.9 | 115.6 | 134.5 | 221
2281.1 | 2173.1 | 127.8 | 75.7 | 145.2 | 120.5 | 166.7 | 115.4 | 134.3 | 220.9
2282.1 | 2174.1 | 127.6 | 74.6 | 145.4 | 120.6 | 166.5 | 115.2 | 134.1 | 220.6
2283.1 | 2175.1 | 127.5 | 73.5 | 145.6 | 120.5 | 166.3 | 115.1 | 134 | 220.4
2284.1 | 2176.1 | 127.3 | 72.4 | 145.7 | 120.5 | 166.4 | 114.9 | 133.8 | 220.2
2285.1 | 2177.1 | 127.1 | 71.4 | 145.8 | 120.6 | 166.6 | 114.7 | 133.6 | 220
2286.1 | 2178.1 | 127 | 70.7 | 145.8 | 120.8 | 166.6 | 114.5 | 133.5 | 219.9
2287.1 | 2179.1 | 126.9 | 69.8 | 145.5 | 121 | 166.4 | 114.4 | 133.3 | 219.9
2288.1 | 2180.1 | 126.8 | 68.9 | 145.3 | 120.6 | 166.5 | 114.2 | 133.1 | 219.8
2289.1 | 2181.1 | 126.6 | 67.9 | 145.3 | 121.1 | 166.5 | 114 | 133 | 219.5
2290.1 | 2182.1 | 126.5 | 67.4 | 145.3 | 120.9 | 166.1 | 113.8 | 132.8 | 219.3
2291.1 | 2183.1 | 126.3 | 68.1 | 145 | 120.3 | 165.7 | 113.7 | 132.7 | 219
2292.1 | 2184.1 | 126.2 | 68.5 | 144.7 | 119.3 | 165.5 | 113.5 | 132.5 | 218.7
2293.1 | 2185.1 | 126.1 | 69.3 | 144.5 | 119.3 | 165.3 | 113.4 | 132.3 | 218.6
2294.1 | 2186.1 | 126 | 69.7 | 144.2 | 118.7 | 165.1 | 113.2 | 132.2 | 218.4
2295.1 | 2187.1 | 125.8 | 70.2 | 143.8 | 117.9 | 164.8 | 113 | 132 | 218.1
2296.1 | 2188.1 | 125.7 | 71.1 | 143.4 | 118.1 | 164.6 | 112.9 | 131.8 | 217.9
2297.1 | 2189.1 | 125.5 | 72.3 | 143.6 | 117.7 | 164.1 | 112.7 | 131.7 | 217.7
2298.1 | 2190.1 | 125.4 | 72.1 | 143.3 | 117.6 | 163.8 | 112.5 | 131.5 | 217.5
2299.1 | 2191.1 | 125.3 | 70.8 | 143.2 | 117.8 | 163.9 | 112.4 | 131.3 | 217.3
2300.1 | 2192.1 | 125.2 | 70.1 | 143.1 | 117.9 | 163.9 | 112.2 | 131.2 | 217.1
2301.1 | 2193.1 | 125 | 70.1 | 143 | 117.9 | 164 | 112 | 131 | 216.9
2302.1 | 2194.1 | 124.8 | 69.5 | 142.7 | 117.3 | 164 | 111.9 | 130.8 | 216.6
2303.1 | 2195.1 | 124.7 | 69 | 142.8 | 117.1 | 163.8 | 111.7 | 130.6 | 216.5
2304.1 | 2196.1 | 124.5 | 69.2 | 143 | 117 | 163.5 | 111.6 | 130.5 | 216.4
2305.1 | 2197.1 | 124.4 | 69 | 142.5 | 116.7 | 163.1 | 111.4 | 130.3 | 216.2
2306.1 | 2198.1 | 124.3 | 69.2 | 142.2 | 117.1 | 163 | 111.3 | 130.1 | 216.1
2307.1 | 2199.1 | 124.3 | 70.2 | 142.5 | 117.6 | 162.5 | 111.1 | 129.9 | 216
2308.1 | 2200.1 | 124.2 | 71.3 | 142.6 | 117.6 | 162.1 | 111 | 129.8 | 215.8
2309.1 | 2201.1 | 124.1 | 72 | 142.1 | 117.2 | 162 | 110.8 | 129.6 | 215.7
2310.1 | 2202.1 | 123.9 | 71.7 | 142 | 116.9 | 161.9 | 110.7 | 129.4 | 215.6
2311.1 | 2203.1 | 123.8 | 70.8 | 141.9 | 116.3 | 161.7 | 110.5 | 129.2 | 215.5
2312.1 | 2204.1 | 123.7 | 70.2 | 141.6 | 116.6 | 161.7 | 110.3 | 129.1 | 215.4
2313.1 | 2205.1 | 123.6 | 70 | 141.5 | 116.7 | 161.7 | 110.2 | 128.9 | 215.2
2314.1 | 2206.1 | 123.4 | 70.2 | 141.5 | 117.2 | 161.9 | 110 | 128.7 | 215.1
2315.1 | 2207.1 | 123.3 | 71.1 | 141.5 | 117 | 161.9 | 109.8 | 128.5 | 215
2316.1 | 2208.1 | 123.1 | 70.8 | 141.4 | 117.6 | 162 | 109.7 | 128.4 | 214.8
2317.1 | 2209.1 | 123 | 70.5 | 141.4 | 116.9 | 161.9 | 109.5 | 128.2 | 214.6
2318.1 | 2210.1 | 122.9 | 69.7 | 141.5 | 117.1 | 161.8 | 109.3 | 128 | 214.3
2319.1 | 2211.1 | 122.7 | 69 | 141.4 | 117.4 | 161.9 | 109.2 | 127.9 | 214.1
2320.1 | 2212.1 | 122.6 | 68.8 | 141.1 | 117.5 | 161.9 | 109 | 127.7 | 213.9
2321.1 | 2213.1 | 122.6 | 70.1 | 140.8 | 116.8 | 161.8 | 108.8 | 127.5 | 213.7
2322.1 | 2214.1 | 122.5 | 70.2 | 140.6 | 116.5 | 161.6 | 108.6 | 127.4 | 213.6
2323.1 | 2215.1 | 122.3 | 70 | 140.2 | 116.1 | 161.6 | 108.4 | 127.2 | 213.4
2324.1 | 2216.1 | 122.1 | 69.4 | 139.8 | 116.1 | 161.7 | 108.3 | 127 | 213.2
2325.1 | 2217.1 | 122 | 68.7 | 140.2 | 115.9 | 161.4 | 108 | 126.9 | 213
2326.1 | 2218.1 | 121.8 | 68.5 | 140.1 | 115.7 | 161.4 | 107.8 | 126.7 | 212.8
2327.1 | 2219.1 | 121.7 | 68.9 | 140.1 | 115.5 | 161.3 | 107.6 | 126.6 | 212.6
2328.1 | 2220.1 | 121.5 | 68.9 | 140.3 | 115.9 | 161.3 | 107.4 | 126.4 | 212.4
2329.1 | 2221.1 | 121.3 | 68.9 | 140.6 | 115.9 | 161.2 | 107.2 | 126.3 | 212.4
2330.1 | 2222.1 | 121.2 | 68 | 140.4 | 115.7 | 161.2 | 107 | 126.1 | 212.3
2331.1 | 2223.1 | 121 | 67.4 | 140.3 | 115.7 | 161.1 | 106.9 | 126 | 212.2
2332.1 | 2224.1 | 121 | 67.1 | 140.4 | 115.5 | 160.9 | 106.7 | 125.8 | 212.1
2333.1 | 2225.1 | 120.8 | 66.5 | 140 | 115.1 | 161 | 106.5 | 125.7 | 212
2334.1 | 2226.1 | 120.7 | 66.3 | 139.7 | 114.8 | 160.9 | 106.3 | 125.5 | 211.8
2335.1 | 2227.1 | 120.5 | 65.9 | 139.6 | 114.2 | 160.7 | 106.1 | 125.4 | 211.8
2336.1 | 2228.1 | 120.4 | 65.6 | 139.4 | 114 | 160.5 | 106 | 125.2 | 211.7
2337.1 | 2229.1 | 120.2 | 66.1 | 139 | 113.2 | 160.1 | 105.8 | 125 | 211.5
2338.1 | 2230.1 | 120.1 | 65.8 | 138.8 | 112.3 | 160 | 105.6 | 124.9 | 211.2
2339.1 | 2231.1 | 120 | 65 | 138.6 | 111.5 | 159.7 | 105.5 | 124.7 | 211
2340.1 | 2232.1 | 119.9 | 64.7 | 138.1 | 111.1 | 159.4 | 105.3 | 124.6 | 210.8
2341.1 | 2233.1 | 119.8 | 64.3 | 137.7 | 110.6 | 159 | 105.2 | 124.4 | 210.6
2342.1 | 2234.1 | 119.7 | 63.7 | 137.4 | 109.6 | 158.3 | 105 | 124.3 | 210.3
2343.1 | 2235.1 | 119.6 | 63.7 | 136.7 | 109.4 | 158.1 | 104.9 | 124.1 | 210
2344.1 | 2236.1 | 119.5 | 63.6 | 136.1 | 109.4 | 157.7 | 104.7 | 124 | 209.8
2345.1 | 2237.1 | 119.4 | 63.5 | 135.3 | 109.1 | 157.3 | 104.6 | 123.8 | 209.6
2346.1 | 2238.1 | 119.3 | 62.6 | 134.9 | 108.6 | 156.7 | 104.4 | 123.6 | 209.5
2347.1 | 2239.1 | 119.2 | 62.4 | 134.3 | 108.2 | 156.1 | 104.3 | 123.5 | 209.3
2348.1 | 2240.1 | 119.1 | 62 | 133.7 | 107.7 | 155.9 | 104.1 | 123.3 | 209.2
2349.1 | 2241.1 | 119 | 61.4 | 133.4 | 107.2 | 155.4 | 104 | 123.2 | 209.1
2350.1 | 2242.1 | 118.9 | 61.3 | 133.2 | 106.8 | 154.9 | 103.8 | 123 | 208.9
2351.1 | 2243.1 | 118.8 | 61 | 132.7 | 106.9 | 154.4 | 103.7 | 122.9 | 208.8
2352.1 | 2244.1 | 118.6 | 60.7 | 132.3 | 106.7 | 154 | 103.5 | 122.7 | 208.8
2353.1 | 2245.1 | 118.5 | 60.8 | 132 | 106.8 | 153.6 | 103.3 | 122.6 | 208.8
2354.1 | 2246.1 | 118.5 | 60.9 | 131.2 | 107.4 | 153.5 | 103.2 | 122.4 | 208.7
2355.1 | 2247.1 | 118.3 | 61.6 | 130.8 | 107 | 153.1 | 103 | 122.2 | 208.5
2356.1 | 2248.1 | 118.1 | 61.9 | 130.4 | 106.5 | 152.8 | 102.9 | 122.1 | 208.3
2357.1 | 2249.1 | 118 | 61.4 | 130.1 | 106.4 | 152.4 | 102.8 | 121.9 | 208.1
2358.1 | 2250.1 | 117.9 | 61.6 | 129.7 | 106.3 | 151.8 | 102.6 | 121.8 | 207.9
2359.1 | 2251.1 | 117.7 | 62.2 | 129.4 | 105.8 | 151.6 | 102.5 | 121.7 | 207.6
2360.1 | 2252.1 | 117.6 | 62 | 129.1 | 105.9 | 151.3 | 102.4 | 121.5 | 207.4
2361.1 | 2253.1 | 117.5 | 61.9 | 129 | 105.9 | 151.1 | 102.2 | 121.4 | 207.1
2362.1 | 2254.1 | 117.4 | 62 | 128.7 | 105.8 | 150.8 | 102.1 | 121.2 | 206.9
2363.1 | 2255.1 | 117.3 | 62.2 | 128.4 | 106.4 | 150.5 | 101.9 | 121.1 | 206.6
2364.1 | 2256.1 | 117.2 | 64.4 | 128.5 | 106.7 | 150.4 | 101.8 | 121 | 206.4
2365.1 | 2257.1 | 117.1 | 64.9 | 128.4 | 106.7 | 150.4 | 101.7 | 120.9 | 206.3
2366.1 | 2258.1 | 117 | 65 | 128.3 | 106.3 | 150.3 | 101.5 | 120.7 | 206.2
2367.1 | 2259.1 | 116.9 | 64.6 | 128.4 | 105.9 | 149.9 | 101.4 | 120.6 | 206.2
2368.1 | 2260.1 | 116.8 | 64.5 | 128.3 | 106.6 | 149.9 | 101.3 | 120.5 | 206.1
2369.1 | 2261.1 | 116.7 | 64.4 | 128.2 | 107 | 150 | 101.1 | 120.4 | 206
2370.1 | 2262.1 | 116.5 | 64 | 128.3 | 107.1 | 150.1 | 101 | 120.3 | 205.9
2371.1 | 2263.1 | 116.4 | 64 | 128.5 | 107.5 | 149.8 | 100.9 | 120.1 | 205.8
2372.1 | 2264.1 | 116.3 | 64.1 | 128.6 | 108.2 | 149.6 | 100.8 | 120 | 205.6
2373.1 | 2265.1 | 116.1 | 64.1 | 128.8 | 108.4 | 149.6 | 100.7 | 119.9 | 205.4
2374.1 | 2266.1 | 116 | 64.3 | 129 | 108.9 | 149.1 | 100.5 | 119.8 | 205
2375.1 | 2267.1 | 115.9 | 64.3 | 129 | 108.7 | 149 | 100.4 | 119.7 | 204.7
2376.1 | 2268.1 | 115.8 | 64.3 | 128.9 | 108.7 | 149.3 | 100.3 | 119.6 | 204.5
2377.1 | 2269.1 | 115.7 | 64.4 | 129 | 107.9 | 149.2 | 100.2 | 119.4 | 204.4
2378.1 | 2270.1 | 115.7 | 64.8 | 129.1 | 107.5 | 149 | 100 | 119.4 | 204.2
2379.1 | 2271.1 | 115.5 | 64.8 | 129.1 | 107.5 | 148.9 | 99.9 | 119.3 | 204
2380.1 | 2272.1 | 115.4 | 63.9 | 129.4 | 107.3 | 148.9 | 99.8 | 119.2 | 203.9
2381.1 | 2273.1 | 115.3 | 63 | 129.9 | 107.2 | 148.9 | 99.6 | 119 | 203.8
2382.1 | 2274.1 | 115.2 | 62.5 | 129.8 | 107.4 | 149.2 | 99.5 | 118.9 | 203.7
2383.1 | 2275.1 | 115.1 | 62.1 | 129.8 | 107.5 | 149.1 | 99.3 | 118.8 | 203.6
2384.1 | 2276.1 | 115.1 | 62.4 | 130 | 107.7 | 149.1 | 99.2 | 118.7 | 203.4
2385.1 | 2277.1 | 114.9 | 62.5 | 130.2 | 107.7 | 149.2 | 99.1 | 118.6 | 203.2
2386.1 | 2278.1 | 114.8 | 62.8 | 130.2 | 108.1 | 149.6 | 98.9 | 118.5 | 203
2387.1 | 2279.1 | 114.7 | 62.7 | 130.2 | 108.4 | 149.7 | 98.8 | 118.4 | 202.8
2388.1 | 2280.1 | 114.6 | 61.8 | 130.5 | 108.7 | 149.7 | 98.7 | 118.3 | 202.5
2389.1 | 2281.1 | 114.5 | 61.3 | 130.6 | 108.7 | 149.9 | 98.5 | 118.2 | 202.2
2390.1 | 2282.1 | 114.4 | 61 | 130.6 | 108.9 | 149.8 | 98.4 | 118.1 | 202.1
2391.1 | 2283.1 | 114.3 | 61.3 | 130.7 | 109 | 149.5 | 98.3 | 118 | 202
2392.1 | 2284.1 | 114.2 | 62 | 130.6 | 108.7 | 149.5 | 98.1 | 117.9 | 201.9
2393.1 | 2285.1 | 114 | 62.4 | 130.4 | 108.7 | 149.7 | 98 | 117.8 | 201.8
2394.1 | 2286.1 | 113.9 | 62 | 130.3 | 109 | 149.9 | 97.9 | 117.7 | 201.8
2395.1 | 2287.1 | 113.8 | 61.1 | 130.4 | 109.2 | 149.8 | 97.8 | 117.6 | 201.7
2396.1 | 2288.1 | 113.7 | 60.3 | 130.1 | 109.4 | 149.7 | 97.7 | 117.5 | 201.5
2397.1 | 2289.1 | 113.6 | 59.8 | 130.1 | 109.3 | 149.9 | 97.6 | 117.4 | 201.4
2398.1 | 2290.1 | 113.4 | 59.9 | 130.1 | 108.7 | 150 | 97.4 | 117.3 | 201.2
2399.1 | 2291.1 | 113.3 | 60.1 | 130 | 108.3 | 149.7 | 97.3 | 117.2 | 201.1
2400.1 | 2292.1 | 113.2 | 59.6 | 129.9 | 108.3 | 149.6 | 97.2 | 117.1 | 200.9
2401.1 | 2293.1 | 113.1 | 59.2 | 129.7 | 107.6 | 149.4 | 97.1 | 117 | 200.8
2402.1 | 2294.1 | 113 | 58.7 | 129.7 | 107 | 149.1 | 96.9 | 116.9 | 200.8
2403.1 | 2295.1 | 112.9 | 59.5 | 129.5 | 106.9 | 149.2 | 96.8 | 116.8 | 200.7
2404.1 | 2296.1 | 112.7 | 60.5 | 129.4 | 106.5 | 149.2 | 96.7 | 116.7 | 200.6
2405.1 | 2297.1 | 112.6 | 61.2 | 129.1 | 106.1 | 149.1 | 96.5 | 116.6 | 200.5
2406.1 | 2298.1 | 112.5 | 61.3 | 128.8 | 105.4 | 148.8 | 96.4 | 116.5 | 200.4
2407.1 | 2299.1 | 112.4 | 61.9 | 128.4 | 105.1 | 148.5 | 96.2 | 116.4 | 200.3
2408.1 | 2300.1 | 112.3 | 61.8 | 128.2 | 105.4 | 148.1 | 96.1 | 116.3 | 200.2
2409.1 | 2301.1 | 112.2 | 62.4 | 128.4 | 104.9 | 148 | 95.9 | 116.2 | 200.3
2410.1 | 2302.1 | 112.1 | 62.8 | 128 | 105.2 | 148 | 95.8 | 116.1 | 200.3
2411.1 | 2303.1 | 112 | 63 | 127.6 | 105.4 | 147.6 | 95.7 | 116 | 200.3
2412.1 | 2304.1 | 111.9 | 62.6 | 127.7 | 104.6 | 147.3 | 95.6 | 115.9 | 200.1
2413.1 | 2305.1 | 111.8 | 61.8 | 127.6 | 104.3 | 147.2 | 95.4 | 115.8 | 200
2414.1 | 2306.1 | 111.7 | 61.3 | 127.1 | 105.4 | 147.4 | 95.3 | 115.7 | 199.8
2415.1 | 2307.1 | 111.6 | 61.9 | 127.1 | 105.7 | 147.3 | 95.2 | 115.6 | 199.6
2416.1 | 2308.1 | 111.5 | 63.3 | 127.4 | 105.2 | 147 | 95.1 | 115.5 | 199.3
2417.1 | 2309.1 | 111.4 | 64.2 | 127.2 | 104.5 | 146.9 | 95 | 115.4 | 199
2418.1 | 2310.1 | 111.3 | 64.3 | 126.9 | 104.2 | 146.8 | 94.9 | 115.3 | 198.7
2419.1 | 2311.1 | 111.2 | 63.6 | 126.9 | 103.9 | 146.6 | 94.8 | 115.2 | 198.4
2420.1 | 2312.1 | 111.1 | 62.9 | 126.8 | 104.1 | 146.4 | 94.7 | 115.1 | 198.1
2421.1 | 2313.1 | 111 | 62.5 | 126.4 | 103.9 | 146.4 | 94.6 | 115 | 197.9
2422.1 | 2314.1 | 110.9 | 62.4 | 126 | 103.5 | 146.2 | 94.6 | 114.9 | 197.6
2423.1 | 2315.1 | 110.8 | 61.8 | 126 | 103.9 | 145.9 | 94.5 | 114.8 | 197.4
2424.1 | 2316.1 | 110.7 | 61.7 | 125.9 | 103.9 | 145.6 | 94.4 | 114.7 | 197.2
2425.1 | 2317.1 | 110.6 | 61.7 | 125.7 | 104 | 145.4 | 94.3 | 114.6 | 196.9
2426.1 | 2318.1 | 110.6 | 61.7 | 125.8 | 103.6 | 145.2 | 94.2 | 114.5 | 196.7
2427.1 | 2319.1 | 110.5 | 61.5 | 125.7 | 103.3 | 145.1 | 94.1 | 114.4 | 196.6
2428.1 | 2320.1 | 110.4 | 61.6 | 125.5 | 102.9 | 145.1 | 94 | 114.3 | 196.4
2429.1 | 2321.1 | 110.3 | 61 | 125.1 | 102.6 | 144.9 | 94 | 114.2 | 196.2
2430.1 | 2322.1 | 110.1 | 60.7 | 125 | 102.2 | 144.6 | 93.9 | 114.1 | 196
2431.1 | 2323.1 | 110 | 61.2 | 124.9 | 102 | 144.7 | 93.8 | 114 | 195.8
2432.1 | 2324.1 | 109.9 | 62.3 | 124.9 | 102.3 | 144.7 | 93.7 | 113.9 | 195.6
2433.1 | 2325.1 | 109.7 | 63.3 | 124.9 | 102.3 | 144.6 | 93.6 | 113.8 | 195.4
2434.1 | 2326.1 | 109.6 | 63.6 | 124.8 | 102.2 | 144.5 | 93.5 | 113.8 | 195.1
2435.1 | 2327.1 | 109.6 | 63.7 | 124.4 | 102.2 | 144.4 | 93.5 | 113.6 | 194.9
2436.1 | 2328.1 | 109.5 | 63.6 | 124.4 | 102.2 | 144.5 | 93.4 | 113.6 | 194.6
2437.1 | 2329.1 | 109.4 | 63.1 | 124.6 | 102.3 | 144.4 | 93.3 | 113.5 | 194.5
2438.1 | 2330.1 | 109.3 | 62.7 | 124.5 | 102.5 | 144.4 | 93.2 | 113.4 | 194.3
2439.1 | 2331.1 | 109.2 | 62.7 | 124.5 | 101.9 | 144 | 93.1 | 113.3 | 194.1
2440.1 | 2332.1 | 109.1 | 62.8 | 124.7 | 101.3 | 143.4 | 93 | 113.2 | 194
2441.1 | 2333.1 | 109 | 63.4 | 124.8 | 100.5 | 143 | 92.9 | 113.1 | 194
2442.1 | 2334.1 | 108.9 | 63.6 | 124.5 | 100.4 | 143.1 | 92.8 | 113 | 193.8
2443.1 | 2335.1 | 108.8 | 63.2 | 124.3 | 100.3 | 142.9 | 92.7 | 112.9 | 193.7
2444.1 | 2336.1 | 108.8 | 63.6 | 124.4 | 100.6 | 142.6 | 92.6 | 112.8 | 193.6
2445.1 | 2337.1 | 108.7 | 65 | 124.4 | 101.4 | 142.8 | 92.5 | 112.7 | 193.5
2446.1 | 2338.1 | 108.6 | 64.8 | 124 | 101.5 | 142.9 | 92.4 | 112.6 | 193.3
2447.1 | 2339.1 | 108.5 | 65 | 123.9 | 101.8 | 142.6 | 92.3 | 112.6 | 193.1
2448.1 | 2340.1 | 108.3 | 64.9 | 123.9 | 101.9 | 142.5 | 92.2 | 112.5 | 192.9
2449.1 | 2341.1 | 108.2 | 64.9 | 123.3 | 101.5 | 142.6 | 92.1 | 112.4 | 192.6
2450.1 | 2342.1 | 108.1 | 64.7 | 123.1 | 101.7 | 142.5 | 92 | 112.3 | 192.4
2451.1 | 2343.1 | 108 | 64.8 | 123.3 | 101.7 | 142.4 | 91.8 | 112.2 | 192
2452.1 | 2344.1 | 107.9 | 65.3 | 123.1 | 101.5 | 142.7 | 91.7 | 112.1 | 191.7
2453.1 | 2345.1 | 107.7 | 64.6 | 122.8 | 101.5 | 142.7 | 91.7 | 112 | 191.4
2454.1 | 2346.1 | 107.6 | 63.8 | 122.8 | 101.5 | 142.5 | 91.6 | 112 | 191.2
2455.1 | 2347.1 | 107.5 | 63.5 | 122.9 | 101.1 | 142.5 | 91.5 | 111.9 | 190.9
2456.1 | 2348.1 | 107.4 | 63.5 | 122.6 | 101.1 | 142.6 | 91.4 | 111.8 | 190.6
2457.1 | 2349.1 | 107.3 | 62.8 | 122.6 | 100.8 | 142.7 | 91.3 | 111.7 | 190.3
2458.1 | 2350.1 | 107.2 | 62 | 122.4 | 101.5 | 142.6 | 91.2 | 111.6 | 190.2
2459.1 | 2351.1 | 107.1 | 62.5 | 122.1 | 101.9 | 142.3 | 91.1 | 111.5 | 190
2460.1 | 2352.1 | 107 | 63.4 | 122.2 | 102.2 | 142.2 | 91 | 111.4 | 189.7
2461.1 | 2353.1 | 106.9 | 64.3 | 122.3 | 101.9 | 142.1 | 90.9 | 111.4 | 189.4
2462.1 | 2354.1 | 106.8 | 64.8 | 122 | 101.2 | 142 | 90.8 | 111.3 | 189.3
2463.1 | 2355.1 | 106.6 | 65.2 | 121.7 | 100.8 | 142.1 | 90.7 | 111.2 | 189.1
2464.1 | 2356.1 | 106.5 | 64.8 | 121.5 | 100.1 | 141.9 | 90.6 | 111.1 | 188.8
2465.1 | 2357.1 | 106.5 | 63.6 | 121.5 | 100 | 141.6 | 90.5 | 111.1 | 188.7
2466.1 | 2358.1 | 106.3 | 62.8 | 121.5 | 100 | 141.5 | 90.4 | 111 | 188.6
2467.1 | 2359.1 | 106.2 | 62.2 | 121 | 100.7 | 141.6 | 90.3 | 110.9 | 188.6
2468.1 | 2360.1 | 106.1 | 62.9 | 120.8 | 100.3 | 141.3 | 90.2 | 110.8 | 188.7
2469.1 | 2361.1 | 106 | 63.1 | 120.7 | 100.3 | 141.3 | 90.1 | 110.7 | 188.7
2470.1 | 2362.1 | 105.9 | 63.1 | 120.4 | 100.5 | 141.6 | 90 | 110.6 | 188.7
2471.1 | 2363.1 | 105.8 | 62.5 | 120.1 | 100.3 | 141.6 | 89.9 | 110.5 | 188.7
2472.1 | 2364.1 | 105.7 | 61.7 | 120 | 100.1 | 141.3 | 89.8 | 110.4 | 188.6
2473.1 | 2365.1 | 105.7 | 62.2 | 119.7 | 99.8 | 141.2 | 89.8 | 110.3 | 188.6
2474.1 | 2366.1 | 105.6 | 63.2 | 119.5 | 99.4 | 141.1 | 89.7 | 110.2 | 188.4
2475.1 | 2367.1 | 105.5 | 63.5 | 119.3 | 99.1 | 141 | 89.6 | 110.1 | 188.3
2476.1 | 2368.1 | 105.4 | 63.3 | 119.3 | 98.9 | 140.7 | 89.5 | 110 | 188.2
2477.1 | 2369.1 | 105.4 | 62.5 | 119 | 99.2 | 140.8 | 89.4 | 109.9 | 188.1
2478.1 | 2370.1 | 105.3 | 62.3 | 119.1 | 99.7 | 140.8 | 89.4 | 109.8 | 187.9
2479.1 | 2371.1 | 105.2 | 62.5 | 119.4 | 100 | 140.5 | 89.3 | 109.7 | 187.6
2480.1 | 2372.1 | 105.1 | 62.8 | 119.3 | 100 | 140.4 | 89.2 | 109.6 | 187.3
2481.1 | 2373.1 | 105 | 62.1 | 119.2 | 100.3 | 140.2 | 89.1 | 109.5 | 187.1
2482.1 | 2374.1 | 104.9 | 61.9 | 119.4 | 99.8 | 139.8 | 89 | 109.4 | 186.9
2483.1 | 2375.1 | 104.8 | 61.1 | 119.3 | 99 | 139.7 | 88.9 | 109.4 | 186.6
2484.1 | 2376.1 | 104.7 | 60.6 | 119 | 98.3 | 139.6 | 88.9 | 109.3 | 186.4
2485.1 | 2377.1 | 104.6 | 60.2 | 118.9 | 97.8 | 139.2 | 88.8 | 109.2 | 186.3
2486.1 | 2378.1 | 104.5 | 59.6 | 118.8 | 97 | 138.9 | 88.7 | 109.1 | 186.1
2487.1 | 2379.1 | 104.4 | 59.3 | 118.5 | 96.7 | 138.7 | 88.6 | 109 | 185.9
2488.1 | 2380.1 | 104.3 | 59.3 | 118.2 | 96.7 | 138.4 | 88.5 | 108.9 | 185.5
2489.1 | 2381.1 | 104.2 | 60 | 117.9 | 96.4 | 138.1 | 88.4 | 108.8 | 185.3
2490.1 | 2382.1 | 104.1 | 60.1 | 117.5 | 96.2 | 137.9 | 88.4 | 108.7 | 185.3
2491.1 | 2383.1 | 104 | 60.3 | 117.1 | 95.8 | 137.7 | 88.3 | 108.6 | 185.2
2492.1 | 2384.1 | 103.9 | 59.6 | 117.1 | 95.9 | 137.5 | 88.2 | 108.4 | 185.1
2493.1 | 2385.1 | 103.7 | 59.2 | 117.3 | 96.1 | 137.2 | 88.1 | 108.3 | 185.1
2494.1 | 2386.1 | 103.6 | 58.7 | 117.2 | 96.6 | 136.9 | 88 | 108.2 | 185
2495.1 | 2387.1 | 103.5 | 58.7 | 117 | 96.7 | 136.7 | 88 | 108.1 | 185.1
2496.1 | 2388.1 | 103.4 | 58.7 | 116.9 | 96.5 | 136.4 | 87.9 | 107.9 | 185.1
2497.1 | 2389.1 | 103.3 | 58.9 | 116.9 | 96.2 | 136.3 | 87.8 | 107.8 | 185.1
2498.1 | 2390.1 | 103.2 | 59.3 | 116.6 | 96.3 | 136.4 | 87.7 | 107.6 | 184.8
2499.1 | 2391.1 | 103.1 | 59.6 | 116.5 | 96.4 | 136.3 | 87.6 | 107.5 | 184.6
2500.1 | 2392.1 | 103 | 59.2 | 116.5 | 96.3 | 136.1 | 87.5 | 107.3 | 184.4
2501.1 | 2393.1 | 102.9 | 59.3 | 116.3 | 96.3 | 136 | 87.4 | 107.2 | 184.2
2502.1 | 2394.1 | 102.8 | 59.5 | 116.2 | 96.4 | 136 | 87.4 | 107.1 | 184
2503.1 | 2395.1 | 102.8 | 60.3 | 116.1 | 96.1 | 135.8 | 87.3 | 106.9 | 183.9
2504.1 | 2396.1 | 102.7 | 61.1 | 116 | 95.6 | 135.4 | 87.2 | 106.8 | 183.7
2505.1 | 2397.1 | 102.6 | 62 | 115.8 | 95.4 | 135.4 | 87.1 | 106.7 | 183.5
2506.1 | 2398.1 | 102.5 | 61.9 | 115.8 | 95.1 | 135.3 | 87 | 106.6 | 183.1
2507.1 | 2399.1 | 102.4 | 61.1 | 115.7 | 94.8 | 135 | 86.9 | 106.5 | 182.9
2508.1 | 2400.1 | 102.4 | 60.5 | 115.2 | 95.3 | 135 | 86.9 | 106.4 | 182.7
2509.1 | 2401.1 | 102.3 | 59.7 | 114.8 | 95 | 134.8 | 86.8 | 106.2 | 182.6
2510.1 | 2402.1 | 102.2 | 58.7 | 114.6 | 94.4 | 134.1 | 86.7 | 106.1 | 182.5
2511.1 | 2403.1 | 102.1 | 58.4 | 114.4 | 93.8 | 133.6 | 86.6 | 106 | 182.3

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 42 |  |  | 2006-08-17 | 14:09
38946.5889 | 1 | 0 | 1 | XLPE&EPR | 7-C | Tray
38946.591 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38946.5931 | 1 | 0 | 1
38946.5953 | 1 | 0 | 1
38946.5974 | 1 | 0 | 1
38946.5995 | 1 | 0 | 1
38946.6017 | 1 | 0 | 1
38946.6038 | 225 | 199 | 1
38946.606 | 1042 | 1102 | 1
38946.6081 | 1612 | 521 | 1
38946.6102 | 1590 | 537 | 1
38946.6124 | 1626 | 661 | 1
38946.6145 | 1442 | 898 | 1
38946.6167 | 1339 | 1061 | 1
1
38946.5889 | 1 | 0 | 2
38946.591 | 1 | 0 | 2
38946.5931 | 1 | 0 | 2
38946.5953 | 1 | 0 | 2
38946.5974 | 1 | 0 | 2
38946.5996 | 1 | 0 | 2
38946.6017 | 1 | 0 | 2
38946.6038 | 199 | 203 | 2
38946.606 | 1220 | 1098 | 2
38946.6081 | 1665 | 515 | 2
38946.6103 | 1380 | 492 | 2
38946.6124 | 1730 | 661 | 2
38946.6145 | 1280 | 795 | 2
38946.6167 | 1133 | 958 | 2
2
38946.5889 | 1 | 0 | 3
38946.591 | 1 | 0 | 3
38946.5932 | 1 | 0 | 3
38946.5953 | 1 | 0 | 3
38946.5974 | 1 | 0 | 3
38946.5996 | 1 | 0 | 3
38946.6017 | 1 | 0 | 3
38946.6039 | 1 | 0 | 3
38946.606 | 63 | 12 | 3
38946.6081 | 1317 | 46 | 3
38946.6103 | 1523 | 59 | 3
38946.6124 | 1097 | 27 | 3
38946.6145 | 658 | 28 | 3
38946.6167 | 228 | 10 | 3
3
38946.5889 | 1 | 0 | 4
38946.591 | 1 | 0 | 4
38946.5932 | 1 | 0 | 4
38946.5953 | 1 | 0 | 4
38946.5975 | 1 | 0 | 4
38946.5996 | 1 | 0 | 4
38946.6017 | 1 | 0 | 4
38946.6039 | 1 | 0 | 4
38946.606 | 63 | 25 | 4
38946.6081 | 929 | 82 | 4
38946.6103 | 978 | 53 | 4
38946.6124 | 1345 | 19 | 4
38946.6146 | 1305 | 9 | 4
38946.6167 | 699 | 4 | 4
4
38946.5889 | 1 | 0 | 5
38946.5911 | 1 | 0 | 5
38946.5932 | 1 | 0 | 5
38946.5953 | 1 | 0 | 5
38946.5975 | 1 | 0 | 5
38946.5996 | 1 | 0 | 5
38946.6017 | 1 | 0 | 5
38946.6039 | 1 | 0 | 5
38946.606 | 137 | 77 | 5
38946.6082 | 1238 | 68 | 5
38946.6103 | 1336 | 51 | 5
38946.6124 | 1041 | 13 | 5
38946.6146 | 527 | 26 | 5
38946.6167 | 149 | 2 | 5
5
38946.5889 | 1 | 0 | 6
38946.5911 | 1 | 0 | 6
38946.5932 | 1 | 0 | 6
38946.5953 | 1 | 0 | 6
38946.5975 | 1 | 0 | 6
38946.5996 | 1 | 0 | 6
38946.6018 | 1 | 0 | 6
38946.6039 | 1 | 0 | 6
38946.606 | 173 | 121 | 6
38946.6082 | 1030 | 86 | 6
38946.6103 | 1101 | 53 | 6
38946.6125 | 1328 | 22 | 6
38946.6146 | 990 | 6 | 6
38946.6167 | 681 | 1 | 6
6
38946.5889 | 1 | 0 | 7
38946.5911 | 1 | 0 | 7
38946.5932 | 1 | 0 | 7
38946.5954 | 1 | 0 | 7
38946.5975 | 1 | 0 | 7
38946.5996 | 1 | 0 | 7
38946.6018 | 1 | 0 | 7
38946.6039 | 1 | 0 | 7
38946.6061 | 24 | 2 | 7
38946.6082 | 1253 | 157 | 7
38946.6103 | 1536 | 74 | 7
38946.6125 | 1213 | 2 | 7
38946.6146 | 482 | 5 | 7
38946.6167 | 208 | 20 | 7
7
38946.589 | 1 | 0 | 8
38946.5911 | 1 | 0 | 8
38946.5932 | 1 | 0 | 8
38946.5954 | 1 | 0 | 8
38946.5975 | 1 | 0 | 8
38946.5997 | 1 | 0 | 8
38946.6018 | 1 | 0 | 8
38946.6039 | 1 | 0 | 8
38946.6061 | 107 | 2 | 8
38946.6082 | 1256 | 79 | 8
38946.6103 | 1164 | 19 | 8
38946.6125 | 1086 | 1 | 8
38946.6146 | 528 | 5 | 8
38946.6168 | 297 | 33 | 8
8
38946.589 | 1 | 0 | 9
38946.5911 | 1 | 0 | 9
38946.5933 | 1 | 0 | 9
38946.5954 | 1 | 0 | 9
38946.5975 | 1 | 0 | 9
38946.5997 | 1 | 0 | 9
38946.6018 | 1 | 0 | 9
38946.6039 | 1 | 0 | 9
38946.6061 | 63 | 6 | 9
38946.6082 | 1150 | 81 | 9
38946.6104 | 1504 | 31 | 9
38946.6125 | 1186 | 3 | 9
38946.6146 | 441 | 8 | 9
38946.6168 | 244 | 40 | 9
9
38946.589 | 1 | 0 | 10
38946.5911 | 1 | 0 | 10
38946.5933 | 1 | 0 | 10
38946.5954 | 1 | 0 | 10
38946.5975 | 1 | 0 | 10
38946.5997 | 1 | 0 | 10
38946.6018 | 1 | 0 | 10
38946.604 | 1 | 0 | 10
38946.6061 | 275 | 25 | 10
38946.6082 | 1250 | 95 | 10
38946.6104 | 1388 | 29 | 10
38946.6125 | 794 | 38 | 10
38946.6147 | 465 | 10 | 10
38946.6168 | 294 | 39 | 10
10
38946.589 | 1 | 0 | 11
38946.5912 | 1 | 0 | 11
38946.5933 | 1 | 0 | 11
38946.5954 | 1 | 0 | 11
38946.5976 | 1 | 0 | 11
38946.5997 | 1 | 0 | 11
38946.6018 | 1 | 0 | 11
38946.604 | 1 | 0 | 11
38946.6061 | 73 | 1 | 11
38946.6083 | 1363 | 74 | 11
38946.6104 | 1240 | 45 | 11
38946.6125 | 1060 | 3 | 11
38946.6147 | 301 | 1 | 11
38946.6168 | 137 | 0 | 11
11
38946.589 | 1 | 0 | 12
38946.5912 | 1 | 0 | 12
38946.5933 | 1 | 0 | 12
38946.5955 | 1 | 0 | 12
38946.5976 | 1 | 0 | 12
38946.5997 | 1 | 0 | 12
38946.6019 | 1 | 0 | 12
38946.604 | 1 | 0 | 12
38946.6061 | 3 | 0 | 12
38946.6083 | 1092 | 70 | 12
38946.6104 | 1051 | 83 | 12
38946.6126 | 710 | 2 | 12
38946.6147 | 454 | 0 | 12
38946.6168 | 279 | 0 | 12
12
38946.5891 | 1 | 0 | 13
38946.5912 | 1 | 0 | 13
38946.5933 | 1 | 0 | 13
38946.5955 | 1 | 0 | 13
38946.5976 | 1 | 0 | 13
38946.5997 | 1 | 0 | 13
38946.6019 | 1 | 0 | 13
38946.604 | 1 | 0 | 13
38946.6062 | 96 | 0 | 13
38946.6083 | 1253 | 54 | 13
38946.6104 | 1331 | 68 | 13
38946.6126 | 958 | 1 | 13
38946.6147 | 293 | 0 | 13
38946.6169 | 149 | 0 | 13
13
38946.5891 | 1 | 0 | 14
38946.5912 | 1 | 0 | 14
38946.5933 | 1 | 0 | 14
38946.5955 | 1 | 0 | 14
38946.5976 | 1 | 0 | 14
38946.5998 | 1 | 0 | 14
38946.6019 | 1 | 0 | 14
38946.604 | 1 | 0 | 14
38946.6062 | 4 | 0 | 14
38946.6083 | 838 | 67 | 14
38946.6105 | 821 | 55 | 14
38946.6126 | 811 | 1 | 14
38946.6147 | 463 | 0 | 14
38946.6169 | 277 | 0 | 14
14
38946.5891 | 1 | 0 | 15
38946.5912 | 1 | 0 | 15
38946.5934 | 1 | 0 | 15
38946.5955 | 1 | 0 | 15
38946.5976 | 1 | 0 | 15
38946.5998 | 1 | 0 | 15
38946.6019 | 1 | 0 | 15
38946.6041 | 1 | 0 | 15
38946.6062 | 119 | 0 | 15
38946.6083 | 1395 | 0 | 15
38946.6105 | 1559 | 0 | 15
38946.6126 | 958 | 0 | 15
38946.6147 | 263 | 0 | 15
38946.6169 | 152 | 0 | 15
15
38946.5891 | 1 | 0 | 16
38946.5912 | 1 | 0 | 16
38946.5934 | 1 | 0 | 16
38946.5955 | 1 | 0 | 16
38946.5977 | 1 | 0 | 16
38946.5998 | 1 | 0 | 16
38946.6019 | 1 | 0 | 16
38946.6041 | 1 | 0 | 16
38946.6062 | 2095 | 0 | 16
38946.6083 | 2094 | 0 | 16
38946.6105 | 2316 | 0 | 16
38946.6126 | 2074 | 0 | 16
38946.6148 | 1778 | 0 | 16
38946.6169 | 1899 | 0 | 16
16
38946.5891 | 1 | 0 | 17
38946.5912 | 1 | 0 | 17
38946.5934 | 1 | 0 | 17
38946.5955 | 1 | 0 | 17
38946.5977 | 1 | 0 | 17
38946.5998 | 1 | 0 | 17
38946.6019 | 1 | 0 | 17
38946.6041 | 1 | 0 | 17
38946.6062 | 203 | 0 | 17
38946.6084 | 1389 | 0 | 17
38946.6105 | 1372 | 0 | 17
38946.6126 | 1059 | 0 | 17
38946.6148 | 270 | 0 | 17
38946.6169 | 151 | 0 | 17
17
38946.5891 | 1 | 0 | 18
38946.5913 | 1 | 0 | 18
38946.5934 | 1 | 0 | 18
38946.5955 | 1 | 0 | 18
38946.5977 | 1 | 0 | 18
38946.5998 | 1 | 0 | 18
38946.602 | 1 | 0 | 18
38946.6041 | 1 | 0 | 18
38946.6062 | 2188 | 0 | 18
38946.6084 | 2363 | 0 | 18
38946.6105 | 2075 | 0 | 18
38946.6127 | 1635 | 0 | 18
38946.6148 | 1800 | 0 | 18
38946.6169 | 2100 | 0 | 18
18
38946.5891 | 1 | 0 | 19
38946.5913 | 1 | 0 | 19
38946.5934 | 1 | 0 | 19
38946.5956 | 1 | 0 | 19
38946.5977 | 1 | 0 | 19
38946.602 | 1 | 0 | 19
38946.6041 | 1 | 0 | 19
38946.6062 | 224 | 0 | 19
38946.6084 | 1434 | 0 | 19
38946.6105 | 1113 | 0 | 19
38946.6127 | 1101 | 0 | 19
38946.6148 | 317 | 0 | 19
38946.6169 | 123 | 0 | 19
19
38946.5892 | 1 | 0 | 20
38946.5913 | 1 | 0 | 20
38946.5934 | 1 | 0 | 20
38946.5956 | 1 | 0 | 20
38946.5977 | 1 | 0 | 20
38946.5998 | 1 | 0 | 20
38946.602 | 1 | 0 | 20
38946.6041 | 1 | 0 | 20
38946.6063 | 2220 | 0 | 20
38946.6084 | 2424 | 0 | 20
38946.6105 | 1964 | 0 | 20
38946.6127 | 2137 | 0 | 20
38946.6148 | 2561 | 0 | 20
38946.617 | 1947 | 0 | 20
20
38946.5892 | 1 | 0 | 21
38946.5913 | 1 | 0 | 21
38946.5934 | 1 | 0 | 21
38946.5956 | 1 | 0 | 21
38946.5977 | 1 | 0 | 21
38946.5999 | 1 | 0 | 21
38946.602 | 1 | 0 | 21
38946.6041 | 1 | 0 | 21
38946.6063 | 334 | 0 | 21
38946.6084 | 1350 | 0 | 21
38946.6106 | 1099 | 0 | 21
38946.6127 | 1015 | 0 | 21
38946.6148 | 259 | 0 | 21
38946.617 | 118 | 0 | 21
21
38946.5892 | 1 | 0 | 22
38946.5913 | 1 | 0 | 22
38946.5935 | 1 | 0 | 22
38946.5956 | 1 | 0 | 22
38946.5977 | 1 | 0 | 22
38946.5999 | 1 | 0 | 22
38946.602 | 1 | 0 | 22
38946.6042 | 1 | 0 | 22
38946.6063 | 2351 | 0 | 22
38946.6084 | 2286 | 0 | 22
38946.6106 | 2220 | 0 | 22
38946.6127 | 2424 | 0 | 22
38946.6148 | 2072 | 0 | 22
38946.617 | 2357 | 0 | 22
22
38946.5892 | 1 | 0 | 23
38946.5913 | 1 | 0 | 23
38946.5935 | 1 | 0 | 23
38946.5956 | 1 | 0 | 23
38946.5978 | 1 | 0 | 23
38946.5999 | 1 | 0 | 23
38946.602 | 1 | 0 | 23
38946.6042 | 1 | 0 | 23
38946.6063 | 497 | 18 | 23
38946.6085 | 1323 | 72 | 23
38946.6106 | 1185 | 95 | 23
38946.6127 | 1198 | 15 | 23
38946.6149 | 276 | 2 | 23
38946.617 | 140 | 1 | 23
23
38946.5892 | 1 | 0 | 24
38946.5914 | 1 | 0 | 24
38946.5935 | 1 | 0 | 24
38946.5956 | 1 | 0 | 24
38946.5978 | 1 | 0 | 24
38946.5999 | 1 | 0 | 24
38946.6021 | 1 | 0 | 24
38946.6042 | 1 | 0 | 24
38946.6063 | 303 | 73 | 24
38946.6085 | 1036 | 64 | 24
38946.6106 | 1029 | 93 | 24
38946.6127 | 1140 | 10 | 24
38946.6149 | 1042 | 1 | 24
24
38946.5892 | 1 | 0 | 25
38946.5914 | 1 | 0 | 25
38946.5935 | 1 | 0 | 25
38946.5957 | 1 | 0 | 25
38946.5978 | 1 | 0 | 25
38946.5999 | 1 | 0 | 25
38946.6021 | 1 | 0 | 25
38946.6042 | 1 | 0 | 25
38946.6064 | 497 | 36 | 25
38946.6085 | 1488 | 71 | 25
38946.6106 | 1400 | 98 | 25
38946.6128 | 1110 | 9 | 25
38946.6149 | 329 | 1 | 25
38946.617 | 129 | 0 | 25
25
38946.5893 | 1 | 0 | 26
38946.5914 | 1 | 0 | 26
38946.5935 | 1 | 0 | 26
38946.5957 | 1 | 0 | 26
38946.5978 | 1 | 0 | 26
38946.6 | 1 | 0 | 26
38946.6021 | 1 | 0 | 26
38946.6042 | 1 | 0 | 26
38946.6064 | 556 | 88 | 26
38946.6085 | 1509 | 78 | 26
38946.6106 | 1112 | 87 | 26
38946.6128 | 978 | 9 | 26
38946.6149 | 390 | 32 | 26
38946.6171 | 125 | 0 | 26
26
38946.5893 | 1 | 0 | 27
38946.5914 | 1 | 0 | 27
38946.5936 | 1 | 0 | 27
38946.5957 | 1 | 0 | 27
38946.5978 | 1 | 0 | 27
38946.6 | 1 | 0 | 27
38946.6021 | 1 | 0 | 27
38946.6042 | 1 | 0 | 27
38946.6064 | 683 | 231 | 27
38946.6085 | 1529 | 145 | 27
38946.6107 | 1222 | 13 | 27
38946.6128 | 1199 | 53 | 27
38946.6149 | 360 | 5 | 27
38946.6171 | 166 | 11 | 27
27
38946.5893 | 1 | 0 | 28
38946.5914 | 1 | 0 | 28
38946.5936 | 1 | 0 | 28
38946.5957 | 1 | 0 | 28
38946.5978 | 1 | 0 | 28
38946.6 | 1 | 0 | 28
38946.6021 | 1 | 0 | 28
38946.6043 | 1 | 0 | 28
38946.6064 | 908 | 370 | 28
38946.6085 | 1277 | 91 | 28
38946.6107 | 1266 | 7 | 28
38946.6128 | 943 | 80 | 28
38946.615 | 449 | 6 | 28
38946.6171 | 257 | 14 | 28
28
38946.5893 | 1 | 0 | 29
38946.5914 | 1 | 0 | 29
38946.5936 | 1 | 0 | 29
38946.5957 | 1 | 0 | 29
38946.5979 | 1 | 0 | 29
38946.6 | 1 | 0 | 29
38946.6021 | 1 | 0 | 29
38946.6043 | 1 | 0 | 29
38946.6064 | 860 | 394 | 29
38946.6086 | 1523 | 125 | 29
38946.6107 | 1387 | 8 | 29
38946.6128 | 1033 | 39 | 29
38946.615 | 344 | 12 | 29
38946.6171 | 208 | 38 | 29
29
38946.5893 | 1 | 0 | 30
38946.5915 | 1 | 0 | 30
38946.5936 | 2 | 0 | 30
38946.5957 | 1 | 0 | 30
38946.5979 | 1 | 0 | 30
38946.6 | 1 | 0 | 30
38946.6022 | 1 | 0 | 30
38946.6043 | 1 | 0 | 30
38946.6064 | 868 | 262 | 30
38946.6086 | 1179 | 69 | 30
38946.6107 | 1200 | 24 | 30
38946.6128 | 769 | 65 | 30
38946.615 | 532 | 10 | 30
38946.6171 | 329 | 48 | 30
30
38946.5893 | 1 | 0 | 31
38946.5915 | 1 | 0 | 31
38946.5936 | 1 | 0 | 31
38946.5958 | 1 | 0 | 31
38946.5979 | 1 | 0 | 31
38946.6 | 1 | 0 | 31
38946.6022 | 1 | 0 | 31
38946.6043 | 1 | 0 | 31
38946.6064 | 643 | 2 | 31
38946.6086 | 1277 | 50 | 31
38946.6107 | 1307 | 92 | 31
38946.6129 | 1236 | 1 | 31
38946.615 | 331 | 0 | 31
38946.6171 | 126 | 0 | 31
31
38946.5894 | 1 | 0 | 32
38946.5915 | 1 | 0 | 32
38946.5936 | 1 | 0 | 32
38946.5958 | 1 | 0 | 32
38946.5979 | 1 | 0 | 32
38946.6 | 1 | 0 | 32
38946.6022 | 1 | 0 | 32
38946.6043 | 1 | 0 | 32
38946.6065 | 5 | 1 | 32
38946.6086 | 1133 | 49 | 32
38946.6107 | 1049 | 91 | 32
38946.6129 | 789 | 0 | 32
38946.615 | 575 | 0 | 32
38946.6172 | 172 | 0 | 32
32
38946.5894 | 1 | 0 | 33
38946.5915 | 1 | 0 | 33
38946.5936 | 1 | 0 | 33
38946.5958 | 1 | 0 | 33
38946.5979 | 1 | 0 | 33
38946.6001 | 1 | 0 | 33
38946.6022 | 1 | 0 | 33
38946.6043 | 1 | 0 | 33
38946.6065 | 717 | 1 | 33
38946.6086 | 1321 | 34 | 33
38946.6108 | 1125 | 21 | 33
38946.6129 | 1179 | 1 | 33
38946.615 | 349 | 0 | 33
38946.6172 | 140 | 0 | 33
33
38946.5894 | 1 | 0 | 34
38946.5915 | 1 | 0 | 34
38946.5937 | 1 | 0 | 34
38946.5958 | 1 | 0 | 34
38946.5979 | 1 | 0 | 34
38946.6001 | 1 | 0 | 34
38946.6022 | 1 | 0 | 34
38946.6044 | 1 | 0 | 34
38946.6065 | 5 | 0 | 34
38946.6086 | 1012 | 15 | 34
38946.6108 | 1059 | 86 | 34
38946.6129 | 742 | 0 | 34
38946.615 | 453 | 0 | 34
38946.6172 | 188 | 0 | 34
34
38946.5894 | 1 | 0 | 35
38946.5915 | 1 | 0 | 35
38946.5937 | 1 | 0 | 35
38946.5958 | 1 | 0 | 35
38946.598 | 1 | 0 | 35
38946.6001 | 1 | 0 | 35
38946.6022 | 1 | 0 | 35
38946.6044 | 1 | 0 | 35
38946.6065 | 785 | 0 | 35
38946.6086 | 1484 | 0 | 35
38946.6108 | 1151 | 0 | 35
38946.6129 | 977 | 0 | 35
38946.6151 | 274 | 0 | 35
38946.6172 | 103 | 0 | 35
35
38946.5916 | 1 | 0 | 36
38946.5937 | 1 | 0 | 36
38946.5958 | 1 | 0 | 36
38946.598 | 1 | 0 | 36
38946.6001 | 1 | 0 | 36
38946.6022 | 1 | 0 | 36
38946.6044 | 1 | 0 | 36
38946.6065 | 2004 | 0 | 36
38946.6087 | 1876 | 0 | 36
38946.6108 | 2445 | 0 | 36
38946.6129 | 1894 | 0 | 36
38946.6151 | 2016 | 0 | 36
38946.6172 | 1716 | 0 | 36
36
38946.5894 | 1 | 0 | 37
38946.5916 | 1 | 0 | 37
38946.5937 | 1 | 0 | 37
38946.5958 | 1 | 0 | 37
38946.598 | 1 | 0 | 37
38946.6001 | 1 | 0 | 37
38946.6023 | 1 | 0 | 37
38946.6044 | 1 | 0 | 37
38946.6065 | 909 | 0 | 37
38946.6087 | 1361 | 0 | 37
38946.6108 | 1398 | 0 | 37
38946.613 | 1156 | 0 | 37
38946.6151 | 301 | 0 | 37
38946.6172 | 105 | 0 | 37
37
38946.5895 | 1 | 0 | 38
38946.5916 | 1 | 0 | 38
38946.5937 | 1 | 0 | 38
38946.5959 | 1 | 0 | 38
38946.598 | 1 | 0 | 38
38946.6001 | 1 | 0 | 38
38946.6023 | 1 | 0 | 38
38946.6044 | 1 | 0 | 38
38946.6066 | 2134 | 0 | 38
38946.6087 | 1988 | 0 | 38
38946.6108 | 2105 | 0 | 38
38946.613 | 1942 | 1 | 38
38946.6173 | 2589 | 0 | 38
38
38946.5895 | 1 | 0 | 39
38946.5916 | 1 | 0 | 39
38946.5938 | 1 | 0 | 39
38946.5959 | 1 | 0 | 39
38946.598 | 1 | 0 | 39
38946.6002 | 1 | 0 | 39
38946.6023 | 1 | 0 | 39
38946.6044 | 1 | 0 | 39
38946.6066 | 799 | 0 | 39
38946.6087 | 1387 | 0 | 39
38946.6109 | 1436 | 0 | 39
38946.613 | 1141 | 0 | 39
38946.6151 | 299 | 0 | 39
38946.6173 | 112 | 0 | 39
39
38946.5895 | 1 | 0 | 40
38946.5916 | 1 | 0 | 40
38946.5938 | 1 | 0 | 40
38946.5959 | 1 | 0 | 40
38946.598 | 1 | 0 | 40
38946.6002 | 1 | 0 | 40
38946.6023 | 1 | 0 | 40
38946.6045 | 1 | 0 | 40
38946.6066 | 2116 | 0 | 40
38946.6087 | 2411 | 0 | 40
38946.6109 | 2029 | 0 | 40
38946.613 | 2077 | 0 | 40
38946.6152 | 2374 | 0 | 40
38946.6173 | 2212 | 0 | 40
40
38946.5895 | 1 | 0 | 41
38946.5916 | 1 | 0 | 41
38946.5938 | 1 | 0 | 41
38946.5959 | 1 | 0 | 41
38946.5981 | 1 | 0 | 41
38946.6002 | 1 | 0 | 41
38946.6023 | 1 | 0 | 41
38946.6045 | 1 | 0 | 41
38946.6066 | 1038 | 0 | 41
38946.6087 | 1629 | 0 | 41
38946.6109 | 1342 | 0 | 41
38946.613 | 958 | 0 | 41
38946.6152 | 293 | 0 | 41
38946.6173 | 106 | 0 | 41
41
38946.5895 | 1 | 0 | 42
38946.5917 | 1 | 0 | 42
38946.5938 | 1 | 0 | 42
38946.5959 | 1 | 0 | 42
38946.5981 | 1 | 0 | 42
38946.6002 | 1 | 0 | 42
38946.6023 | 1 | 0 | 42
38946.6045 | 1 | 0 | 42
38946.6066 | 2492 | 0 | 42
38946.6088 | 2181 | 0 | 42
38946.6109 | 2536 | 0 | 42
38946.613 | 2532 | 0 | 42
38946.6152 | 2042 | 0 | 42
38946.6173 | 2083 | 0 | 42
42
38946.5895 | 1 | 0 | 43
38946.5917 | 1 | 0 | 43
38946.5938 | 1 | 0 | 43
38946.5959 | 1 | 0 | 43
38946.5981 | 1 | 0 | 43
38946.6002 | 1 | 0 | 43
38946.6024 | 1 | 0 | 43
38946.6045 | 998 | 963 | 43
38946.6066 | 728 | 366 | 43
38946.6088 | 1596 | 565 | 43
38946.6109 | 1542 | 645 | 43
38946.6131 | 1384 | 509 | 43
38946.6152 | 1294 | 615 | 43
38946.6173 | 1274 | 933 | 43
43
38946.5895 | 1 | 0 | 44
38946.5917 | 1 | 0 | 44
38946.5938 | 1 | 0 | 44
38946.596 | 1 | 0 | 44
38946.5981 | 1 | 0 | 44
38946.6002 | 1 | 0 | 44
38946.6024 | 1 | 0 | 44
38946.6045 | 1090 | 1059 | 44
38946.6067 | 1125 | 775 | 44
38946.6088 | 1363 | 503 | 44
38946.6109 | 1371 | 571 | 44
38946.6131 | 1649 | 469 | 44
38946.6152 | 1205 | 585 | 44
38946.6173 | 1135 | 825 | 44
44
38946.5896 | 1 | 0 | 45
38946.5917 | 1 | 0 | 45
38946.5938 | 1 | 0 | 45
38946.596 | 1 | 0 | 45
38946.5981 | 1 | 0 | 45
38946.6003 | 1 | 0 | 45
38946.6024 | 1 | 0 | 45
38946.6045 | 3 | 10 | 45
38946.6067 | 549 | 8 | 45
38946.6088 | 1274 | 20 | 45
38946.6109 | 1127 | 5 | 45
38946.6131 | 1295 | 4 | 45
38946.6152 | 918 | 5 | 45
38946.6174 | 362 | 9 | 45
45
38946.5896 | 1 | 0 | 46
38946.5917 | 1 | 0 | 46
38946.5939 | 1 | 0 | 46
38946.596 | 1 | 0 | 46
38946.5981 | 1 | 0 | 46
38946.6003 | 1 | 0 | 46
38946.6024 | 1 | 0 | 46
38946.6045 | 2 | 5 | 46
38946.6067 | 1211 | 5 | 46
38946.6088 | 1426 | 15 | 46
38946.611 | 1256 | 2 | 46
38946.6131 | 801 | 3 | 46
38946.6152 | 321 | 2 | 46
38946.6174 | 151 | 4 | 46
46
38946.5896 | 1 | 0 | 47
38946.5917 | 1 | 0 | 47
38946.5939 | 1 | 0 | 47
38946.596 | 1 | 0 | 47
38946.5981 | 1 | 0 | 47
38946.6003 | 1 | 0 | 47
38946.6024 | 1 | 0 | 47
38946.6046 | 2 | 2 | 47
38946.6067 | 585 | 4 | 47
38946.6088 | 1152 | 9 | 47
38946.611 | 1083 | 1 | 47
38946.6131 | 1231 | 1 | 47
38946.6153 | 1005 | 3 | 47
38946.6174 | 407 | 2 | 47
47
38946.5896 | 1 | 0 | 48
38946.5917 | 1 | 0 | 48
38946.5939 | 1 | 0 | 48
38946.596 | 1 | 0 | 48
38946.5982 | 1 | 0 | 48
38946.6003 | 1 | 0 | 48
38946.6024 | 1 | 0 | 48
38946.6046 | 1 | 2 | 48
38946.6067 | 1099 | 1 | 48
38946.6089 | 1328 | 7 | 48
38946.611 | 1154 | 0 | 48
38946.6131 | 651 | 1 | 48
38946.6153 | 458 | 2 | 48
38946.6174 | 204 | 2 | 48
48
38946.5896 | 1 | 0 | 49
38946.5918 | 1 | 0 | 49
38946.5939 | 1 | 0 | 49
38946.596 | 1 | 0 | 49
38946.5982 | 1 | 0 | 49
38946.6003 | 1 | 0 | 49
38946.6025 | 1 | 0 | 49
38946.6046 | 2 | 1 | 49
38946.6067 | 571 | 0 | 49
38946.6089 | 1307 | 169 | 49
38946.611 | 1294 | 307 | 49
38946.6131 | 1232 | 252 | 49
38946.6153 | 1064 | 177 | 49
38946.6174 | 621 | 108 | 49
49
38946.5896 | 1 | 0 | 50
38946.5918 | 1 | 0 | 50
38946.5939 | 1 | 0 | 50
38946.5961 | 1 | 0 | 50
38946.5982 | 1 | 0 | 50
38946.6003 | 1 | 0 | 50
38946.6025 | 1 | 0 | 50
38946.6046 | 1 | 1 | 50
38946.6068 | 38 | 0 | 50
38946.6089 | 1268 | 217 | 50
38946.611 | 931 | 362 | 50
38946.6132 | 963 | 319 | 50
38946.6153 | 536 | 196 | 50
38946.6174 | 316 | 189 | 50
50
38946.5897 | 1 | 0 | 51
38946.5918 | 1 | 0 | 51
38946.5939 | 1 | 0 | 51
38946.5961 | 1 | 0 | 51
38946.5982 | 1 | 0 | 51
38946.6004 | 1 | 0 | 51
38946.6025 | 1 | 0 | 51
38946.6046 | 1 | 0 | 51
38946.6068 | 755 | 0 | 51
38946.6089 | 1348 | 210 | 51
38946.6111 | 1359 | 340 | 51
38946.6132 | 1282 | 240 | 51
38946.6153 | 1199 | 210 | 51
38946.6175 | 530 | 153 | 51
51
38946.5897 | 1 | 0 | 52
38946.5918 | 1 | 0 | 52
38946.594 | 1 | 0 | 52
38946.5961 | 1 | 0 | 52
38946.5982 | 1 | 0 | 52
38946.6004 | 1 | 0 | 52
38946.6025 | 1 | 0 | 52
38946.6047 | 1 | 1 | 52
38946.6068 | 75 | 0 | 52
38946.6089 | 1233 | 260 | 52
38946.6111 | 1082 | 397 | 52
38946.6132 | 954 | 289 | 52
38946.6153 | 614 | 219 | 52
38946.6175 | 103 | 22 | 52
52
38946.5897 | 1 | 0 | 53
38946.5918 | 1 | 0 | 53
38946.594 | 1 | 0 | 53
38946.5961 | 1 | 0 | 53
38946.5983 | 1 | 0 | 53
38946.6004 | 1 | 0 | 53
38946.6025 | 1 | 0 | 53
38946.6047 | 1 | 1 | 53
38946.6068 | 741 | 0 | 53
38946.6089 | 1174 | 1 | 53
38946.6111 | 1140 | 2 | 53
38946.6132 | 1151 | 2 | 53
38946.6154 | 1111 | 62 | 53
38946.6175 | 399 | 0 | 53
53
38946.5897 | 1 | 0 | 54
38946.5919 | 1 | 0 | 54
38946.594 | 1 | 0 | 54
38946.5961 | 1 | 0 | 54
38946.5983 | 1 | 0 | 54
38946.6004 | 1 | 0 | 54
38946.6025 | 1 | 0 | 54
38946.6047 | 1 | 0 | 54
38946.6068 | 2465 | 0 | 54
38946.609 | 1797 | 0 | 54
38946.6111 | 2146 | 1 | 54
38946.6132 | 2005 | 1 | 54
38946.6154 | 1751 | 25 | 54
38946.6175 | 1902 | 1 | 54
54
38946.5897 | 1 | 0 | 55
38946.5919 | 1 | 0 | 55
38946.594 | 1 | 0 | 55
38946.5961 | 1 | 0 | 55
38946.5983 | 1 | 0 | 55
38946.6004 | 1 | 0 | 55
38946.6026 | 1 | 0 | 55
38946.6068 | 652 | 0 | 55
38946.609 | 1370 | 0 | 55
38946.6111 | 1160 | 1 | 55
38946.6133 | 1358 | 26 | 55
38946.6154 | 811 | 1 | 55
38946.6175 | 270 | 0 | 55
55
38946.5897 | 1 | 0 | 56
38946.5919 | 1 | 0 | 56
38946.594 | 1 | 0 | 56
38946.5962 | 1 | 0 | 56
38946.5983 | 1 | 0 | 56
38946.6004 | 1 | 0 | 56
38946.6026 | 1 | 0 | 56
38946.6047 | 1 | 0 | 56
38946.6069 | 2537 | 0 | 56
38946.609 | 2480 | 0 | 56
38946.6111 | 1973 | 0 | 56
38946.6133 | 1766 | 86 | 56
38946.6154 | 1352 | 1 | 56
38946.6175 | 1983 | 1 | 56
56
38946.5898 | 1 | 0 | 57
38946.5919 | 1 | 0 | 57
38946.594 | 1 | 0 | 57
38946.5962 | 1 | 0 | 57
38946.5983 | 1 | 0 | 57
38946.6005 | 1 | 0 | 57
38946.6026 | 1 | 0 | 57
38946.6047 | 1 | 0 | 57
38946.6069 | 786 | 0 | 57
38946.609 | 1344 | 0 | 57
38946.6111 | 980 | 0 | 57
38946.6133 | 1019 | 0 | 57
38946.6154 | 814 | 0 | 57
38946.6176 | 249 | 1 | 57
57
38946.5898 | 1 | 0 | 58
38946.5919 | 1 | 0 | 58
38946.5941 | 1 | 0 | 58
38946.5962 | 1 | 0 | 58
38946.5983 | 1 | 0 | 58
38946.6005 | 1 | 0 | 58
38946.6026 | 1 | 0 | 58
38946.6047 | 1780 | 0 | 58
38946.6069 | 2524 | 0 | 58
38946.609 | 2312 | 0 | 58
38946.6112 | 2277 | 0 | 58
38946.6133 | 2094 | 0 | 58
38946.6154 | 2393 | 0 | 58
38946.6176 | 2321 | 0 | 58
58
38946.5898 | 1 | 0 | 59
38946.5919 | 1 | 0 | 59
38946.5941 | 1 | 0 | 59
38946.5962 | 1 | 0 | 59
38946.5983 | 1 | 0 | 59
38946.6005 | 1 | 0 | 59
38946.6026 | 1 | 0 | 59
38946.6048 | 3 | 0 | 59
38946.6069 | 825 | 0 | 59
38946.609 | 1444 | 0 | 59
38946.6112 | 1085 | 0 | 59
38946.6133 | 1206 | 0 | 59
38946.6155 | 894 | 0 | 59
38946.6176 | 357 | 0 | 59
59
38946.5898 | 1 | 0 | 60
38946.5919 | 1 | 0 | 60
38946.5941 | 1 | 0 | 60
38946.5962 | 1 | 0 | 60
38946.5984 | 1 | 0 | 60
38946.6005 | 1 | 0 | 60
38946.6026 | 1 | 0 | 60
38946.6048 | 162 | 0 | 60
38946.6069 | 2280 | 0 | 60
38946.6091 | 2488 | 0 | 60
38946.6112 | 2550 | 0 | 60
38946.6133 | 2563 | 0 | 60
38946.6155 | 2229 | 0 | 60
38946.6176 | 2011 | 0 | 60
60
38946.5898 | 1 | 0 | 61
38946.592 | 1 | 0 | 61
38946.5941 | 1 | 0 | 61
38946.5962 | 1 | 0 | 61
38946.5984 | 1 | 0 | 61
38946.6005 | 1 | 0 | 61
38946.6027 | 1 | 0 | 61
38946.6048 | 2 | 0 | 61
38946.6069 | 757 | 1 | 61
38946.6091 | 1196 | 23 | 61
38946.6112 | 1124 | 0 | 61
38946.6133 | 1052 | 2 | 61
38946.6155 | 741 | 1 | 61
38946.6176 | 382 | 3 | 61
61
38946.5898 | 1 | 0 | 62
38946.592 | 1 | 0 | 62
38946.5941 | 1 | 0 | 62
38946.5963 | 2 | 0 | 62
38946.5984 | 1 | 0 | 62
38946.6005 | 1 | 0 | 62
38946.6027 | 1 | 0 | 62
38946.6048 | 2 | 0 | 62
38946.6069 | 1244 | 1 | 62
38946.6091 | 1262 | 27 | 62
38946.6112 | 1545 | 0 | 62
38946.6134 | 723 | 1 | 62
38946.6155 | 314 | 1 | 62
38946.6176 | 144 | 3 | 62
62
38946.5899 | 1 | 0 | 63
38946.592 | 1 | 0 | 63
38946.5941 | 1 | 0 | 63
38946.5963 | 1 | 0 | 63
38946.5984 | 1 | 0 | 63
38946.6005 | 1 | 0 | 63
38946.6027 | 1 | 0 | 63
38946.6048 | 1 | 0 | 63
38946.607 | 1022 | 2 | 63
38946.6091 | 1234 | 15 | 63
38946.6112 | 938 | 0 | 63
38946.6134 | 1329 | 1 | 63
38946.6155 | 816 | 4 | 63
38946.6177 | 359 | 1 | 63
63
38946.5899 | 1 | 0 | 64
38946.592 | 1 | 0 | 64
38946.5942 | 1 | 0 | 64
38946.5963 | 1 | 0 | 64
38946.5984 | 1 | 0 | 64
38946.6006 | 1 | 0 | 64
38946.6027 | 1 | 0 | 64
38946.6048 | 1 | 0 | 64
38946.607 | 1231 | 1 | 64
38946.6091 | 1362 | 15 | 64
38946.6113 | 1288 | 0 | 64
38946.6134 | 624 | 0 | 64
38946.6155 | 367 | 2 | 64
38946.6177 | 129 | 1 | 64
64
38946.5899 | 1 | 0 | 65
38946.592 | 1 | 0 | 65
38946.5942 | 1 | 0 | 65
38946.5963 | 1 | 0 | 65
38946.5984 | 1 | 0 | 65
38946.6006 | 1 | 0 | 65
38946.6027 | 1 | 0 | 65
38946.6049 | 1 | 0 | 65
38946.607 | 839 | 0 | 65
38946.6091 | 1381 | 221 | 65
38946.6113 | 1324 | 347 | 65
38946.6134 | 1456 | 268 | 65
38946.6156 | 769 | 223 | 65
38946.6177 | 507 | 168 | 65
65
38946.5899 | 1 | 0 | 66
38946.592 | 1 | 0 | 66
38946.5942 | 1 | 0 | 66
38946.5963 | 1 | 0 | 66
38946.5985 | 1 | 0 | 66
38946.6006 | 1 | 0 | 66
38946.6027 | 1 | 0 | 66
38946.6049 | 1 | 0 | 66
38946.607 | 311 | 0 | 66
38946.6092 | 1295 | 256 | 66
38946.6113 | 862 | 317 | 66
38946.6134 | 963 | 248 | 66
38946.6156 | 634 | 305 | 66
38946.6177 | 296 | 200 | 66
66
38946.5899 | 1 | 0 | 67
38946.5921 | 1 | 0 | 67
38946.5942 | 1 | 0 | 67
38946.5963 | 1 | 0 | 67
38946.5985 | 1 | 0 | 67
38946.6006 | 1 | 0 | 67
38946.6028 | 1 | 0 | 67
38946.6049 | 1 | 0 | 67
38946.607 | 998 | 0 | 67
38946.6092 | 1158 | 212 | 67
38946.6113 | 1263 | 346 | 67
38946.6134 | 1056 | 278 | 67
38946.6156 | 920 | 282 | 67
38946.6177 | 393 | 74 | 67
67
38946.5899 | 2 | 0 | 68
38946.5921 | 1 | 0 | 68
38946.5942 | 1 | 0 | 68
38946.5964 | 1 | 0 | 68
38946.5985 | 1 | 0 | 68
38946.6006 | 1 | 0 | 68
38946.6028 | 1 | 0 | 68
38946.6049 | 1 | 0 | 68
38946.607 | 561 | 0 | 68
38946.6092 | 1182 | 246 | 68
38946.6113 | 1018 | 376 | 68
38946.6135 | 834 | 296 | 68
38946.6156 | 577 | 303 | 68
38946.6177 | 226 | 141 | 68
68
38946.59 | 1 | 0 | 69
38946.5921 | 1 | 0 | 69
38946.5942 | 1 | 0 | 69
38946.5964 | 1 | 0 | 69
38946.5985 | 1 | 0 | 69
38946.6006 | 1 | 0 | 69
38946.6028 | 1 | 0 | 69
38946.6049 | 1 | 0 | 69
38946.6071 | 1204 | 0 | 69
38946.6092 | 1325 | 1 | 69
38946.6113 | 1056 | 2 | 69
38946.6135 | 1194 | 1 | 69
38946.6156 | 825 | 93 | 69
38946.6178 | 240 | 1 | 69
69
38946.59 | 1 | 0 | 70
38946.5921 | 1 | 0 | 70
38946.5942 | 1 | 0 | 70
38946.5964 | 1 | 0 | 70
38946.5985 | 1 | 0 | 70
38946.6007 | 1 | 0 | 70
38946.6028 | 1 | 0 | 70
38946.6049 | 1 | 0 | 70
38946.6071 | 2403 | 0 | 70
38946.6092 | 1592 | 0 | 70
38946.6114 | 2429 | 1 | 70
38946.6135 | 2002 | 18 | 70
38946.6156 | 2104 | 1 | 70
38946.6178 | 1787 | 1 | 70
70
38946.59 | 4 | 0 | 71
38946.5921 | 1 | 0 | 71
38946.5943 | 1 | 0 | 71
38946.5964 | 1 | 0 | 71
38946.5985 | 1 | 0 | 71
38946.6007 | 1 | 0 | 71
38946.6028 | 1 | 0 | 71
38946.605 | 1 | 0 | 71
38946.6071 | 965 | 0 | 71
38946.6092 | 1002 | 0 | 71
38946.6114 | 1037 | 1 | 71
38946.6135 | 1069 | 119 | 71
38946.6156 | 792 | 1 | 71
38946.6178 | 249 | 0 | 71
71
38946.59 | 1 | 0 | 72
38946.5921 | 1 | 0 | 72
38946.5943 | 1 | 0 | 72
38946.5964 | 1 | 0 | 72
38946.5986 | 1 | 0 | 72
38946.6007 | 1 | 0 | 72
38946.6028 | 1 | 0 | 72
38946.605 | 1 | 0 | 72
38946.6071 | 2180 | 0 | 72
38946.6092 | 2557 | 0 | 72
38946.6114 | 2206 | 0 | 72
38946.6135 | 1394 | 43 | 72
38946.6157 | 1891 | 0 | 72
38946.6178 | 1895 | 24 | 72
72
38946.59 | 1 | 0 | 73
38946.5922 | 1 | 0 | 73
38946.5943 | 1 | 0 | 73
38946.5964 | 1 | 0 | 73
38946.5986 | 1 | 0 | 73
38946.6007 | 1 | 0 | 73
38946.6028 | 1 | 0 | 73
38946.605 | 1 | 0 | 73
38946.6071 | 1231 | 0 | 73
38946.6093 | 1174 | 0 | 73
38946.6114 | 1093 | 0 | 73
38946.6135 | 1174 | 0 | 73
38946.6157 | 754 | 0 | 73
38946.6178 | 205 | 0 | 73
73
38946.59 | 1 | 0 | 74
38946.5922 | 1 | 0 | 74
38946.5943 | 1 | 0 | 74
38946.5964 | 1 | 0 | 74
38946.5986 | 1 | 1 | 74
38946.6007 | 1 | 0 | 74
38946.6029 | 2 | 0 | 74
38946.605 | 2480 | 0 | 74
38946.6071 | 2243 | 0 | 74
38946.6093 | 2479 | 0 | 74
38946.6114 | 2525 | 0 | 74
38946.6136 | 2347 | 0 | 74
38946.6157 | 2495 | 0 | 74
38946.6178 | 2199 | 0 | 74
74
38946.59 | 1 | 0 | 75
38946.5922 | 1 | 0 | 75
38946.5943 | 1 | 0 | 75
38946.5965 | 1 | 0 | 75
38946.5986 | 1 | 0 | 75
38946.6007 | 1 | 0 | 75
38946.6029 | 1 | 0 | 75
38946.605 | 3 | 0 | 75
38946.6072 | 1399 | 0 | 75
38946.6093 | 997 | 0 | 75
38946.6114 | 1112 | 0 | 75
38946.6136 | 1213 | 0 | 75
38946.6157 | 844 | 0 | 75
38946.6178 | 218 | 0 | 75
75
38946.5901 | 1 | 0 | 76
38946.5922 | 1 | 0 | 76
38946.5943 | 1 | 0 | 76
38946.5965 | 1 | 0 | 76
38946.5986 | 1 | 0 | 76
38946.6008 | 1 | 0 | 76
38946.6029 | 1 | 0 | 76
38946.605 | 285 | 0 | 76
38946.6072 | 2563 | 0 | 76
38946.6093 | 1972 | 0 | 76
38946.6115 | 1993 | 0 | 76
38946.6136 | 2178 | 0 | 76
38946.6157 | 1998 | 0 | 76
38946.6179 | 2021 | 0 | 76
76
38946.5901 | 1 | 0 | 77
38946.5922 | 1 | 0 | 77
38946.5944 | 1 | 0 | 77
38946.5965 | 1 | 0 | 77
38946.5986 | 1 | 0 | 77
38946.6008 | 1 | 0 | 77
38946.6029 | 936 | 1045 | 77
38946.6051 | 1062 | 1015 | 77
38946.6072 | 1475 | 285 | 77
38946.6093 | 1428 | 393 | 77
38946.6115 | 1264 | 425 | 77
38946.6136 | 1139 | 665 | 77
38946.6157 | 1304 | 975 | 77
38946.6179 | 311 | 211 | 77
77
38946.5901 | 1 | 0 | 78
38946.5922 | 1 | 0 | 78
38946.5944 | 1 | 0 | 78
38946.5965 | 1 | 0 | 78
38946.5987 | 1 | 0 | 78
38946.6008 | 1 | 0 | 78
38946.6029 | 1161 | 1197 | 78
38946.6051 | 912 | 870 | 78
38946.6072 | 1364 | 294 | 78
38946.6094 | 1258 | 397 | 78
38946.6115 | 1285 | 448 | 78
38946.6136 | 995 | 577 | 78
38946.6158 | 1119 | 833 | 78
38946.6179 | 661 | 521 | 78
78
38946.5901 | 1 | 0 | 79
38946.5923 | 1 | 0 | 79
38946.5944 | 1 | 0 | 79
38946.5965 | 1 | 0 | 79
38946.5987 | 1 | 0 | 79
38946.6008 | 1 | 0 | 79
38946.603 | 3 | 9 | 79
38946.6051 | 3 | 8 | 79
38946.6072 | 1320 | 1 | 79
38946.6094 | 1252 | 3 | 79
38946.6115 | 1159 | 3 | 79
38946.6136 | 538 | 4 | 79
38946.6158 | 368 | 6 | 79
38946.6179 | 103 | 2 | 79
79
38946.5901 | 1 | 0 | 80
38946.5923 | 1 | 0 | 80
38946.5944 | 1 | 0 | 80
38946.5966 | 1 | 0 | 80
38946.5987 | 1 | 0 | 80
38946.6008 | 1 | 0 | 80
38946.603 | 2 | 3 | 80
38946.6051 | 2 | 4 | 80
38946.6072 | 991 | 0 | 80
38946.6094 | 774 | 3 | 80
38946.6115 | 889 | 1 | 80
38946.6137 | 834 | 2 | 80
38946.6158 | 369 | 4 | 80
38946.6179 | 45 | 0 | 80
80
38946.5902 | 1 | 0 | 81
38946.5923 | 1 | 0 | 81
38946.5944 | 1 | 0 | 81
38946.5966 | 1 | 0 | 81
38946.5987 | 1 | 0 | 81
38946.6008 | 1 | 0 | 81
38946.603 | 2 | 2 | 81
38946.6051 | 2 | 2 | 81
38946.6073 | 1388 | 0 | 81
38946.6094 | 1215 | 1 | 81
38946.6115 | 1248 | 1 | 81
38946.6137 | 558 | 1 | 81
38946.6158 | 385 | 2 | 81
38946.618 | 66 | 0 | 81
81
38946.5902 | 1 | 0 | 82
38946.5923 | 1 | 0 | 82
38946.5944 | 1 | 0 | 82
38946.5966 | 1 | 0 | 82
38946.5987 | 1 | 0 | 82
38946.6009 | 1 | 0 | 82
38946.603 | 1 | 2 | 82
38946.6051 | 2 | 2 | 82
38946.6073 | 1271 | 0 | 82
38946.6094 | 768 | 1 | 82
38946.6116 | 862 | 0 | 82
38946.6137 | 820 | 1 | 82
38946.6158 | 347 | 1 | 82
38946.618 | 47 | 0 | 82
82
38946.5902 | 1 | 0 | 83
38946.5923 | 1 | 0 | 83
38946.5945 | 1 | 0 | 83
38946.5966 | 1 | 0 | 83
38946.5987 | 1 | 0 | 83
38946.6009 | 1 | 0 | 83
38946.603 | 2 | 1 | 83
38946.6052 | 1 | 2 | 83
38946.6073 | 1458 | 0 | 83
38946.6094 | 1487 | 0 | 83
38946.6116 | 1112 | 0 | 83
38946.6137 | 541 | 0 | 83
38946.6158 | 334 | 1 | 83
38946.618 | 70 | 0 | 83
83
38946.5902 | 1 | 0 | 84
38946.5923 | 2 | 0 | 84
38946.5945 | 1 | 0 | 84
38946.5966 | 1 | 0 | 84
38946.5987 | 1 | 0 | 84
38946.6009 | 1 | 0 | 84
38946.603 | 1 | 1 | 84
38946.6052 | 1 | 1 | 84
38946.6073 | 2294 | 0 | 84
38946.6094 | 2221 | 0 | 84
38946.6116 | 1946 | 0 | 84
38946.6137 | 1654 | 0 | 84
38946.6159 | 1831 | 0 | 84
38946.618 | 1118 | 0 | 84
84
38946.5902 | 1 | 0 | 85
38946.5923 | 1 | 0 | 85
38946.5945 | 1 | 0 | 85
38946.5966 | 1 | 0 | 85
38946.5988 | 2 | 0 | 85
38946.6009 | 1 | 0 | 85
38946.603 | 1 | 1 | 85
38946.6052 | 2 | 1 | 85
38946.6073 | 1343 | 0 | 85
38946.6095 | 1419 | 0 | 85
38946.6116 | 1286 | 0 | 85
38946.6137 | 580 | 0 | 85
38946.6159 | 401 | 1 | 85
38946.618 | 58 | 0 | 85
85
38946.5902 | 1 | 0 | 86
38946.5924 | 1 | 0 | 86
38946.5945 | 1 | 0 | 86
38946.5966 | 1 | 0 | 86
38946.5988 | 1 | 0 | 86
38946.6009 | 1 | 0 | 86
38946.6031 | 1 | 1 | 86
38946.6052 | 1878 | 1 | 86
38946.6073 | 2352 | 0 | 86
38946.6095 | 2134 | 0 | 86
38946.6116 | 2464 | 1 | 86
38946.6137 | 1725 | 0 | 86
38946.6159 | 1042 | 0 | 86
38946.618 | 2400 | 0 | 86
86
38946.5902 | 1 | 0 | 87
38946.5924 | 1 | 0 | 87
38946.5945 | 1 | 0 | 87
38946.5967 | 1 | 0 | 87
38946.5988 | 1 | 0 | 87
38946.6009 | 1 | 0 | 87
38946.6031 | 1 | 0 | 87
38946.6052 | 3 | 0 | 87
38946.6073 | 1465 | 0 | 87
38946.6095 | 1222 | 0 | 87
38946.6116 | 1415 | 0 | 87
38946.6138 | 531 | 0 | 87
38946.6159 | 334 | 0 | 87
38946.618 | 68 | 0 | 87
87
38946.5903 | 1 | 0 | 88
38946.5924 | 1 | 0 | 88
38946.5945 | 1 | 0 | 88
38946.5967 | 1 | 0 | 88
38946.5988 | 1 | 0 | 88
38946.6009 | 1 | 0 | 88
38946.6031 | 1 | 0 | 88
38946.6052 | 2287 | 1 | 88
38946.6074 | 1978 | 0 | 88
38946.6095 | 2111 | 0 | 88
38946.6116 | 2099 | 0 | 88
38946.6138 | 2104 | 1 | 88
38946.6159 | 2364 | 0 | 88
38946.6181 | 2243 | 0 | 88
88
38946.5903 | 1 | 0 | 89
38946.5924 | 1 | 0 | 89
38946.5945 | 1 | 0 | 89
38946.5967 | 1 | 0 | 89
38946.5988 | 1 | 0 | 89
38946.601 | 1 | 0 | 89
38946.6031 | 1 | 0 | 89
38946.6052 | 4 | 0 | 89
38946.6074 | 1571 | 0 | 89
38946.6095 | 1151 | 0 | 89
38946.6117 | 1818 | 0 | 89
38946.6138 | 571 | 0 | 89
38946.6159 | 380 | 0 | 89
38946.6181 | 62 | 0 | 89
89
38946.5903 | 1 | 0 | 90
38946.5924 | 1 | 0 | 90
38946.5946 | 1 | 0 | 90
38946.5967 | 1 | 0 | 90
38946.5988 | 1 | 0 | 90
38946.601 | 1 | 0 | 90
38946.6031 | 1 | 0 | 90
38946.6053 | 1160 | 0 | 90
38946.6074 | 2270 | 0 | 90
38946.6095 | 2378 | 0 | 90
38946.6117 | 2476 | 0 | 90
38946.6138 | 2440 | 0 | 90
38946.616 | 1940 | 0 | 90
38946.6181 | 2046 | 0 | 90
90
38946.5903 | 1 | 0 | 91
38946.5925 | 1 | 0 | 91
38946.5946 | 1 | 0 | 91
38946.5967 | 1 | 0 | 91
38946.5989 | 1 | 0 | 91
38946.601 | 1 | 0 | 91
38946.6031 | 1 | 0 | 91
38946.6053 | 4 | 0 | 91
38946.6074 | 1395 | 0 | 91
38946.6096 | 1382 | 1 | 91
38946.6117 | 1496 | 0 | 91
38946.6138 | 621 | 0 | 91
38946.616 | 374 | 0 | 91
38946.6181 | 82 | 0 | 91
91
38946.5903 | 1 | 0 | 92
38946.5925 | 1 | 0 | 92
38946.5946 | 1 | 0 | 92
38946.5967 | 1 | 0 | 92
38946.5989 | 1 | 0 | 92
38946.601 | 1 | 0 | 92
38946.6032 | 1 | 0 | 92
38946.6053 | 2 | 0 | 92
38946.6074 | 449 | 0 | 92
38946.6096 | 846 | 0 | 92
38946.6117 | 809 | 0 | 92
38946.6139 | 701 | 0 | 92
38946.616 | 301 | 0 | 92
38946.6181 | 6 | 0 | 92
92
38946.5903 | 1 | 0 | 93
38946.5925 | 1 | 0 | 93
38946.5946 | 1 | 0 | 93
38946.5968 | 1 | 0 | 93
38946.5989 | 1 | 0 | 93
38946.601 | 1 | 0 | 93
38946.6032 | 1 | 1 | 93
38946.6053 | 2 | 0 | 93
38946.6075 | 1772 | 0 | 93
38946.6096 | 1326 | 0 | 93
38946.6117 | 1465 | 0 | 93
38946.6139 | 506 | 0 | 93
38946.616 | 418 | 0 | 93
38946.6181 | 85 | 0 | 93
93
38946.5904 | 1 | 0 | 94
38946.5925 | 1 | 0 | 94
38946.5946 | 1 | 0 | 94
38946.5968 | 1 | 0 | 94
38946.5989 | 1 | 0 | 94
38946.6011 | 1 | 0 | 94
38946.6032 | 1 | 0 | 94
38946.6053 | 2 | 0 | 94
38946.6075 | 736 | 0 | 94
38946.6096 | 1000 | 0 | 94
38946.6117 | 931 | 0 | 94
38946.6139 | 704 | 0 | 94
38946.616 | 328 | 0 | 94
38946.6182 | 5 | 0 | 94
94
38946.5904 | 1 | 0 | 95
38946.5925 | 1 | 0 | 95
38946.5947 | 1 | 0 | 95
38946.5968 | 1 | 0 | 95
38946.5989 | 1 | 0 | 95
38946.6011 | 1 | 0 | 95
38946.6032 | 1 | 0 | 95
38946.6053 | 2 | 0 | 95
38946.6075 | 1385 | 0 | 95
38946.6096 | 1135 | 0 | 95
38946.6118 | 1098 | 0 | 95
38946.6139 | 534 | 0 | 95
38946.616 | 321 | 0 | 95
38946.6182 | 99 | 0 | 95
95
38946.5904 | 1 | 0 | 96
38946.5925 | 1 | 0 | 96
38946.5947 | 1 | 0 | 96
38946.5968 | 1 | 0 | 96
38946.5989 | 1 | 0 | 96
38946.6011 | 1 | 0 | 96
38946.6032 | 1 | 0 | 96
38946.6054 | 2 | 0 | 96
38946.6075 | 2089 | 0 | 96
38946.6096 | 2033 | 0 | 96
38946.6118 | 2103 | 0 | 96
38946.6139 | 1665 | 0 | 96
38946.6161 | 1742 | 0 | 96
38946.6182 | 300 | 0 | 96
96
38946.5904 | 1 | 0 | 97
38946.5925 | 1 | 0 | 97
38946.5947 | 1 | 0 | 97
38946.5968 | 1 | 0 | 97
38946.599 | 1 | 0 | 97
38946.6011 | 1 | 0 | 97
38946.6032 | 1 | 0 | 97
38946.6054 | 2 | 0 | 97
38946.6075 | 1166 | 0 | 97
38946.6097 | 1363 | 0 | 97
38946.6118 | 1472 | 0 | 97
38946.6139 | 535 | 0 | 97
38946.6161 | 330 | 0 | 97
38946.6182 | 80 | 0 | 97
97
38946.5904 | 1 | 0 | 98
38946.5926 | 1 | 0 | 98
38946.5947 | 1 | 0 | 98
38946.5968 | 1 | 0 | 98
38946.599 | 1 | 0 | 98
38946.6011 | 1 | 0 | 98
38946.6033 | 1 | 0 | 98
38946.6054 | 2044 | 0 | 98
38946.6075 | 2024 | 0 | 98
38946.6097 | 1993 | 0 | 98
38946.6118 | 2270 | 0 | 98
38946.6139 | 1776 | 0 | 98
38946.6161 | 2028 | 0 | 98
38946.6182 | 2599 | 0 | 98
98
38946.5904 | 1 | 0 | 99
38946.5926 | 1 | 0 | 99
38946.5947 | 1 | 0 | 99
38946.5969 | 1 | 0 | 99
38946.599 | 1 | 0 | 99
38946.6011 | 1 | 0 | 99
38946.6033 | 1 | 0 | 99
38946.6054 | 4 | 0 | 99
38946.6075 | 1229 | 0 | 99
38946.6097 | 1203 | 0 | 99
38946.6118 | 1621 | 0 | 99
38946.614 | 628 | 0 | 99
38946.6161 | 355 | 0 | 99
38946.6182 | 63 | 0 | 99
99
38946.5905 | 1 | 0 | 100
38946.5926 | 1 | 0 | 100
38946.5947 | 1 | 0 | 100
38946.5969 | 1 | 0 | 100
38946.599 | 1 | 0 | 100
38946.6011 | 1 | 0 | 100
38946.6033 | 1 | 0 | 100
38946.6054 | 2213 | 0 | 100
38946.6076 | 2163 | 0 | 100
38946.6097 | 2533 | 0 | 100
38946.6118 | 2554 | 0 | 100
38946.614 | 2483 | 0 | 100
38946.6161 | 1979 | 0 | 100
38946.6183 | 2176 | 0 | 100
100
38946.5905 | 1 | 0 | 101
38946.5926 | 1 | 0 | 101
38946.5947 | 1 | 0 | 101
38946.5969 | 1 | 0 | 101
38946.599 | 1 | 0 | 101
38946.6012 | 1 | 0 | 101
38946.6033 | 1 | 0 | 101
38946.6054 | 4 | 0 | 101
38946.6076 | 1289 | 0 | 101
38946.6097 | 1266 | 0 | 101
38946.6119 | 1356 | 0 | 101
38946.614 | 579 | 0 | 101
38946.6161 | 342 | 0 | 101
38946.6183 | 57 | 0 | 101
101
38946.5905 | 1 | 0 | 102
38946.5926 | 1 | 0 | 102
38946.5948 | 1 | 0 | 102
38946.5969 | 1 | 0 | 102
38946.599 | 1 | 0 | 102
38946.6012 | 1 | 0 | 102
38946.6033 | 1 | 0 | 102
38946.6055 | 2006 | 0 | 102
38946.6076 | 2160 | 0 | 102
38946.6097 | 2499 | 0 | 102
38946.6119 | 2388 | 0 | 102
38946.614 | 2517 | 0 | 102
38946.6161 | 2530 | 0 | 102
38946.6183 | 2236 | 0 | 102
102
38946.5905 | 1 | 0 | 103
38946.5926 | 1 | 0 | 103
38946.5948 | 1 | 0 | 103
38946.5969 | 1 | 0 | 103
38946.5991 | 1 | 0 | 103
38946.6012 | 1 | 0 | 103
38946.6033 | 1 | 0 | 103
38946.6055 | 1171 | 1136 | 103
38946.6076 | 1624 | 614 | 103
38946.6098 | 1437 | 817 | 103
38946.6119 | 1572 | 834 | 103
38946.614 | 1212 | 841 | 103
38946.6162 | 1129 | 861 | 103
38946.6183 | 1173 | 1173 | 103
103
38946.5905 | 1 | 0 | 104
38946.5927 | 1 | 0 | 104
38946.5948 | 1 | 0 | 104
38946.5969 | 1 | 0 | 104
38946.5991 | 1 | 0 | 104
38946.6012 | 1 | 0 | 104
38946.6034 | 1 | 0 | 104
38946.6055 | 1148 | 1111 | 104
38946.6076 | 1692 | 548 | 104
38946.6098 | 1401 | 866 | 104
38946.6119 | 1565 | 701 | 104
38946.614 | 1450 | 891 | 104
38946.6162 | 1049 | 817 | 104
38946.6183 | 1119 | 1154 | 104
104
38946.5905 | 1 | 0 | 105
38946.5927 | 1 | 0 | 105
38946.5948 | 1 | 0 | 105
38946.597 | 1 | 0 | 105
38946.5991 | 1 | 0 | 105
38946.6012 | 1 | 0 | 105
38946.6034 | 1 | 0 | 105
38946.6055 | 4 | 9 | 105
38946.6077 | 1005 | 4 | 105
38946.6098 | 925 | 6 | 105
38946.6119 | 755 | 5 | 105
38946.6141 | 566 | 5 | 105
38946.6162 | 283 | 5 | 105
38946.6183 | 5 | 6 | 105
105
38946.5906 | 1 | 0 | 106
38946.5927 | 1 | 0 | 106
38946.5948 | 1 | 0 | 106
38946.597 | 2 | 0 | 106
38946.5991 | 1 | 0 | 106
38946.6012 | 1 | 0 | 106
38946.6034 | 1 | 0 | 106
38946.6055 | 2421 | 4 | 106
38946.6077 | 1909 | 2 | 106
38946.6098 | 2303 | 3 | 106
38946.6119 | 1832 | 2 | 106
38946.6141 | 2128 | 4 | 106
38946.6162 | 1916 | 4 | 106
38946.6184 | 158 | 3 | 106
106
38946.5906 | 1 | 0 | 107
38946.5927 | 1 | 0 | 107
38946.5948 | 1 | 0 | 107
38946.597 | 2 | 0 | 107
38946.5991 | 1 | 0 | 107
38946.6013 | 1 | 0 | 107
38946.6034 | 1 | 0 | 107
38946.6055 | 4 | 3 | 107
38946.6077 | 829 | 1 | 107
38946.6098 | 899 | 2 | 107
38946.612 | 768 | 1 | 107
38946.6141 | 650 | 3 | 107
38946.6162 | 328 | 2 | 107
38946.6184 | 3 | 2 | 107
107
38946.5906 | 1 | 0 | 108
38946.5927 | 1 | 0 | 108
38946.5949 | 1 | 0 | 108
38946.597 | 1 | 0 | 108
38946.5991 | 1 | 0 | 108
38946.6013 | 1 | 0 | 108
38946.6034 | 1 | 0 | 108
38946.6056 | 2384 | 2 | 108
38946.6077 | 2342 | 0 | 108
38946.6098 | 2522 | 1 | 108
38946.612 | 2099 | 1 | 108
38946.6141 | 1886 | 4 | 108
38946.6162 | 2179 | 1 | 108
38946.6184 | 2585 | 1 | 108
108
38946.5906 | 1 | 0 | 109
38946.5927 | 1 | 0 | 109
38946.5949 | 1 | 0 | 109
38946.597 | 1 | 0 | 109
38946.5992 | 1 | 0 | 109
38946.6013 | 1 | 0 | 109
38946.6034 | 1 | 0 | 109
38946.6056 | 4 | 1 | 109
38946.6077 | 768 | 0 | 109
38946.6098 | 773 | 1 | 109
38946.612 | 803 | 1 | 109
38946.6141 | 564 | 1 | 109
38946.6163 | 254 | 1 | 109
38946.6184 | 4 | 1 | 109
109
38946.5906 | 1 | 0 | 110
38946.5928 | 1 | 0 | 110
38946.5949 | 1 | 0 | 110
38946.597 | 1 | 0 | 110
38946.5992 | 1 | 0 | 110
38946.6013 | 1 | 0 | 110
38946.6034 | 1 | 0 | 110
38946.6056 | 2379 | 1 | 110
38946.6077 | 2557 | 0 | 110
38946.6099 | 2164 | 0 | 110
38946.612 | 2506 | 1 | 110
38946.6141 | 2230 | 0 | 110
38946.6163 | 2320 | 0 | 110
38946.6184 | 2233 | 1 | 110
110
38946.5906 | 1 | 0 | 111
38946.5928 | 1 | 0 | 111
38946.5949 | 1 | 0 | 111
38946.597 | 1 | 0 | 111
38946.5992 | 1 | 0 | 111
38946.6013 | 1 | 0 | 111
38946.6035 | 1 | 0 | 111
38946.6056 | 4 | 1 | 111
38946.6077 | 689 | 0 | 111
38946.6099 | 974 | 0 | 111
38946.612 | 805 | 0 | 111
38946.6142 | 640 | 0 | 111
38946.6163 | 243 | 1 | 111
38946.6184 | 4 | 1 | 111
111
38946.5906 | 1 | 0 | 112
38946.5928 | 1 | 0 | 112
38946.5949 | 1 | 0 | 112
38946.5971 | 1 | 0 | 112
38946.5992 | 1 | 0 | 112
38946.6013 | 1 | 0 | 112
38946.6035 | 1 | 0 | 112
38946.6056 | 2381 | 1 | 112
38946.6078 | 2252 | 0 | 112
38946.6099 | 2008 | 0 | 112
38946.612 | 2005 | 0 | 112
38946.6142 | 2547 | 0 | 112
38946.6163 | 2459 | 0 | 112
38946.6184 | 2182 | 0 | 112
112
38946.5907 | 1 | 0 | 113
38946.5928 | 1 | 0 | 113
38946.5949 | 1 | 0 | 113
38946.5971 | 1 | 0 | 113
38946.5992 | 1 | 0 | 113
38946.6014 | 1 | 0 | 113
38946.6035 | 1 | 0 | 113
38946.6056 | 4 | 1 | 113
38946.6078 | 715 | 0 | 113
38946.6099 | 913 | 0 | 113
38946.612 | 755 | 0 | 113
38946.6142 | 547 | 0 | 113
38946.6163 | 278 | 0 | 113
38946.6185 | 38 | 1 | 113
113
38946.5907 | 1 | 0 | 114
38946.5928 | 1 | 0 | 114
38946.595 | 1 | 0 | 114
38946.5971 | 1 | 0 | 114
38946.5992 | 1 | 0 | 114
38946.6014 | 1 | 0 | 114
38946.6035 | 1 | 0 | 114
38946.6056 | 2158 | 0 | 114
38946.6078 | 1569 | 0 | 114
38946.6099 | 1858 | 0 | 114
38946.6121 | 2103 | 0 | 114
38946.6142 | 1822 | 2 | 114
38946.6163 | 1735 | 0 | 114
38946.6185 | 130 | 0 | 114
114
38946.5907 | 1 | 0 | 115
38946.5928 | 1 | 0 | 115
38946.595 | 1 | 0 | 115
38946.5971 | 1 | 0 | 115
38946.5993 | 1 | 0 | 115
38946.6014 | 1 | 0 | 115
38946.6035 | 1 | 0 | 115
38946.6057 | 4 | 0 | 115
38946.6078 | 702 | 0 | 115
38946.6099 | 755 | 0 | 115
38946.6121 | 655 | 0 | 115
38946.6142 | 521 | 4 | 115
38946.6164 | 277 | 0 | 115
38946.6185 | 3 | 0 | 115
115
38946.5907 | 1 | 0 | 116
38946.5929 | 1 | 0 | 116
38946.595 | 1 | 0 | 116
38946.5971 | 1 | 0 | 116
38946.5993 | 1 | 0 | 116
38946.6014 | 1 | 0 | 116
38946.6035 | 1 | 0 | 116
38946.6057 | 2422 | 0 | 116
38946.6078 | 2543 | 0 | 116
38946.61 | 2397 | 0 | 116
38946.6121 | 1558 | 0 | 116
38946.6142 | 1538 | 42 | 116
38946.6164 | 2045 | 1 | 116
38946.6185 | 2412 | 0 | 116
116
38946.5907 | 1 | 0 | 117
38946.5929 | 1 | 0 | 117
38946.595 | 1 | 0 | 117
38946.5972 | 1 | 0 | 117
38946.5993 | 1 | 0 | 117
38946.6014 | 1 | 0 | 117
38946.6036 | 1 | 0 | 117
38946.6057 | 4 | 0 | 117
38946.6078 | 830 | 0 | 117
38946.61 | 892 | 0 | 117
38946.6121 | 813 | 0 | 117
38946.6143 | 571 | 0 | 117
38946.6164 | 288 | 0 | 117
38946.6185 | 4 | 0 | 117
117
38946.5908 | 1 | 0 | 118
38946.5929 | 1 | 0 | 118
38946.595 | 1 | 0 | 118
38946.5972 | 1 | 0 | 118
38946.5993 | 1 | 0 | 118
38946.6014 | 1 | 0 | 118
38946.6036 | 1 | 0 | 118
38946.6057 | 2336 | 0 | 118
38946.6079 | 2520 | 0 | 118
38946.61 | 2098 | 0 | 118
38946.6121 | 2015 | 0 | 118
38946.6143 | 2444 | 0 | 118
38946.6164 | 2260 | 0 | 118
38946.6186 | 1703 | 0 | 118
118
38946.5908 | 1 | 0 | 119
38946.5929 | 1 | 0 | 119
38946.595 | 1 | 0 | 119
38946.5972 | 1 | 0 | 119
38946.5993 | 1 | 0 | 119
38946.6015 | 1 | 0 | 119
38946.6036 | 1 | 0 | 119
38946.6057 | 4 | 0 | 119
38946.6079 | 688 | 0 | 119
38946.61 | 783 | 0 | 119
38946.6122 | 755 | 0 | 119
38946.6143 | 607 | 0 | 119
38946.6164 | 302 | 0 | 119
38946.6186 | 3 | 1 | 119
119
38946.5908 | 1 | 0 | 120
38946.5929 | 1 | 0 | 120
38946.5951 | 1 | 0 | 120
38946.5972 | 1 | 0 | 120
38946.5993 | 1 | 0 | 120
38946.6015 | 1 | 0 | 120
38946.6036 | 1 | 0 | 120
38946.6058 | 1992 | 0 | 120
38946.6079 | 2472 | 0 | 120
38946.61 | 2540 | 0 | 120
38946.6122 | 2363 | 0 | 120
38946.6143 | 1980 | 0 | 120
38946.6164 | 2219 | 0 | 120
38946.6186 | 1683 | 0 | 120
120
38946.5908 | 1 | 0 | 121
38946.5929 | 1 | 0 | 121
38946.5951 | 1 | 0 | 121
38946.5972 | 1 | 0 | 121
38946.5994 | 1 | 0 | 121
38946.6015 | 1 | 0 | 121
38946.6036 | 1 | 0 | 121
38946.6058 | 2461 | 0 | 121
38946.6079 | 2020 | 0 | 121
38946.61 | 2281 | 0 | 121
38946.6122 | 2139 | 0 | 121
38946.6143 | 1625 | 264 | 121
38946.6165 | 2107 | 0 | 121
38946.6186 | 79 | 0 | 121
121
38946.5908 | 1 | 0 | 122
38946.593 | 1 | 0 | 122
38946.5951 | 1 | 0 | 122
38946.5972 | 1 | 0 | 122
38946.5994 | 1 | 0 | 122
38946.6015 | 1 | 0 | 122
38946.6036 | 1 | 0 | 122
38946.6058 | 2530 | 0 | 122
38946.6079 | 2206 | 0 | 122
38946.6101 | 2506 | 0 | 122
38946.6122 | 1957 | 0 | 122
38946.6143 | 1628 | 399 | 122
38946.6165 | 2037 | 0 | 122
38946.6186 | 2199 | 0 | 122
122
38946.5908 | 1 | 0 | 123
38946.593 | 1 | 0 | 123
38946.5951 | 1 | 0 | 123
38946.5972 | 1 | 0 | 123
38946.5994 | 1 | 0 | 123
38946.6015 | 1 | 0 | 123
38946.6037 | 1 | 0 | 123
38946.6058 | 2482 | 0 | 123
38946.6079 | 2039 | 0 | 123
38946.6101 | 2121 | 0 | 123
38946.6122 | 1889 | 0 | 123
38946.6144 | 1703 | 1 | 123
38946.6165 | 1914 | 0 | 123
38946.6186 | 82 | 0 | 123
123
38946.5908 | 1 | 0 | 124
38946.593 | 1 | 0 | 124
38946.5951 | 1 | 0 | 124
38946.5973 | 1 | 0 | 124
38946.5994 | 1 | 0 | 124
38946.6015 | 1 | 0 | 124
38946.6037 | 1 | 0 | 124
38946.6058 | 2287 | 0 | 124
38946.608 | 1999 | 0 | 124
38946.6101 | 2227 | 0 | 124
38946.6122 | 2532 | 0 | 124
38946.6144 | 2316 | 0 | 124
38946.6165 | 2211 | 0 | 124
38946.6186 | 1630 | 0 | 124
124
38946.5909 | 1 | 0 | 125
38946.593 | 1 | 0 | 125
38946.5951 | 1 | 0 | 125
38946.5973 | 1 | 0 | 125
38946.5994 | 1 | 0 | 125
38946.6016 | 1 | 0 | 125
38946.6037 | 1 | 0 | 125
38946.6058 | 2415 | 0 | 125
38946.608 | 1632 | 0 | 125
38946.6101 | 2281 | 0 | 125
38946.6122 | 1775 | 0 | 125
38946.6144 | 1776 | 0 | 125
38946.6165 | 1850 | 0 | 125
38946.6187 | 69 | 0 | 125
125
38946.5909 | 1 | 0 | 126
38946.593 | 1 | 0 | 126
38946.5952 | 1 | 0 | 126
38946.5973 | 1 | 0 | 126
38946.5994 | 1 | 0 | 126
38946.6016 | 1 | 0 | 126
38946.6037 | 1 | 0 | 126
38946.6058 | 2361 | 0 | 126
38946.608 | 2294 | 0 | 126
38946.6101 | 2551 | 0 | 126
38946.6123 | 2180 | 0 | 126
38946.6144 | 2400 | 0 | 126
38946.6165 | 2275 | 0 | 126
38946.6187 | 1784 | 0 | 126
126
38946.5909 | 1 | 0 | 127
38946.593 | 1 | 0 | 127
38946.5952 | 1 | 0 | 127
38946.5973 | 1 | 0 | 127
38946.5994 | 1 | 0 | 127
38946.6016 | 1 | 0 | 127
38946.6037 | 1 | 0 | 127
38946.6059 | 2163 | 0 | 127
38946.608 | 2475 | 0 | 127
38946.6101 | 2481 | 0 | 127
38946.6123 | 2117 | 0 | 127
38946.6144 | 1665 | 0 | 127
38946.6166 | 2563 | 0 | 127
38946.6187 | 2012 | 0 | 127
127
38946.5909 | 1 | 0 | 128
38946.593 | 1 | 0 | 128
38946.5952 | 1 | 0 | 128
38946.5973 | 1 | 0 | 128
38946.5995 | 1 | 0 | 128
38946.6016 | 1 | 0 | 128
38946.6037 | 1 | 0 | 128
38946.6059 | 2547 | 0 | 128
38946.608 | 2449 | 0 | 128
38946.6102 | 1978 | 0 | 128
38946.6123 | 2533 | 0 | 128
38946.6144 | 2480 | 0 | 128
38946.6166 | 2249 | 0 | 128
38946.6187 | 1279 | 0 | 128
128
38946.5909 | 1 | 0 | 129
38946.5931 | 1 | 0 | 129
38946.5952 | 1 | 0 | 129
38946.5973 | 1 | 0 | 129
38946.5995 | 1 | 0 | 129
38946.6016 | 1 | 0 | 129
38946.6038 | 1 | 0 | 129
38946.6059 | 2513 | 0 | 129
38946.608 | 2016 | 0 | 129
38946.6102 | 2453 | 0 | 129
38946.6123 | 1734 | 0 | 129
38946.6144 | 1684 | 0 | 129
38946.6166 | 2407 | 0 | 129
38946.6187 | 2172 | 0 | 129
129
38946.5909 | 1 | 0 | 130
38946.5931 | 1 | 0 | 130
38946.5952 | 1 | 0 | 130
38946.5974 | 1 | 0 | 130
38946.5995 | 1 | 0 | 130
38946.6016 | 1 | 0 | 130
38946.6038 | 1 | 0 | 130
38946.6059 | 2531 | 0 | 130
38946.6081 | 2527 | 0 | 130
38946.6102 | 2036 | 0 | 130
38946.6123 | 2161 | 0 | 130
38946.6145 | 2482 | 0 | 130
38946.6166 | 2250 | 0 | 130
38946.6187 | 1890 | 0 | 130
130
38946.591 | 1 | 0 | 131
38946.5931 | 1 | 0 | 131
38946.5952 | 1 | 0 | 131
38946.5974 | 1 | 0 | 131
38946.5995 | 1 | 0 | 131
38946.6017 | 1 | 0 | 131
38946.6038 | 1 | 0 | 131
38946.6059 | 2370 | 0 | 131
38946.6081 | 2473 | 0 | 131
38946.6102 | 2111 | 0 | 131
38946.6123 | 2364 | 0 | 131
38946.6145 | 2496 | 0 | 131
38946.6166 | 2014 | 0 | 131
38946.6188 | 1267 | 810 | 131
131
38946.591 | 1 | 0 | 132
38946.5931 | 1 | 0 | 132
38946.5953 | 1 | 0 | 132
38946.5974 | 1 | 0 | 132
38946.5995 | 1 | 0 | 132
38946.6017 | 1 | 0 | 132
38946.6038 | 1 | 0 | 132
38946.6059 | 2238 | 0 | 132
38946.6081 | 2538 | 0 | 132
38946.6102 | 1974 | 0 | 132
38946.6124 | 2061 | 0 | 132
38946.6145 | 2569 | 0 | 132
38946.6166 | 1958 | 0 | 132
38946.6188 | 1485 | 533 | 132
132

## Test Facts
Last row in IRMS data sheets: | 19
Time when Penlight power was initiated: | 108