## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 43
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, mixture of EPR (3) & PE (3) insulated control cables (Items 2 & 15). Cable specimens present: Six lengths of cable were monitored for electrical performance, 3 each of EPR and PE, A seventh length of cable (EPR cable Item #2) was monitored for temperature response, No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 119 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
119 | 0 | Initated Penlight Heating
895 | 776 | Cables ignite and burn
917 | 798 | Power to Penlight is shutoff
1043-1064 | 924-945 | Conductors D7, E9 & E10 all short to ground (657, <1 & 24) | PE Cable E is shorted to ground; EPR Cable D partially shorts to ground
1068 | 949 | Conductors D7 & D8 short together at less than 100 ohms (24) | EPR Cable D shorts internally
1082-1084 | 963-965 | Conductors F11 & F12 both short to ground at much less than 100 ohms (<1 & <1) | EPR Cable F is shorted to ground
1093-1109 | 894-990 | Conductors E9 & E10 short together (3), conductors F11 & F12 short together (2), and conductors A1 & A2 short together (29) | EPR Cables A and F are shorted internally; PE Cable E shorts internally
1228-1573 | 1109-1454 | The existing ground fault on conductor D7 decreases to less than 100 ohms (2); conductors A1, A2, C5, C6 & D8 all short to ground (683, 166, 748, 595 & 6) | EPR Cables A and D are shorted to ground; PE Cable C shorts to ground
1585 | 1466 | Conductors C5 & C6 short together at less than 100 ohms (5) | PE Cable C is shorted internally
1691-1904 | 1572-1785 | The existing ground fault on conductor A2 decreases to less than 100 ohms (99); conductors B4 & B3 both short to ground at less than 100 ohms (54 & 71) | PE Cable B is shorted to ground; all conductors are shorted to ground
1907 | 1788 | Conductors B3 & B4 short together at less than 100 ohms (5) | PE Cable B is shorts internally
1934-1942 | 1815-1823 | The existing ground faults on conductors C5 & C6 decrease to less than 100 ohms (10 & 13)
Additional Observations
Observation 1 | The progression of failure modes for the cable bundle demonstrated a tendancy that the cables on the cable tray rungs short to ground prior to the cables higher in the bundle.
Observation 2 | It took 776 s (12.9min.) from the start of Penlight heating for the cable bundle to ignite, 924 s (15.4 min.) for the first short to ground, and 949 s (15.8 min.) for the initial internal short.
Observation 3 | No cable to cable interactions took place prior to the individual cables either shorting to ground or shorting internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A, D, F = EPR Cable Item #2
B, C, E = PE Cable Item #15
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 43 |  |  | 2006-08-18 | 15:20
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-118.5 | 211201.9994 | -115.5 | 211201.9994 | -113 | 211201.9994 | -110 | 211201.9994 | -107 | 211201.9994 | -87.5 | 211201.9994 | -85 | 211201.9994 | -82 | 211201.9994 | -79.5 | 211201.9994 | -59.5 | 211201.9994 | -57 | 211201.9994 | -54 | 211201.9994 | -51 | 230937.9994 | -48.5 | 212837.9994 | -45.5 | 237537.9994 | -43 | 251937.9994 | -34.5 | 211201.9994 | -31.5 | 211201.9994 | -29 | 218737.9994 | -26 | 211201.9994 | -23.5 | 252237.9994 | -20.5 | 259537.9994 | -12 | 211201.9994 | -3.5 | 248437.9994 | -1 | 259337.9994 | 2 | 212237.9994 | 5 | 235637.9994 | 13 | 244237.9994 | 16 | 218037.9994 | 19 | 247337.9994 | 21.5 | 229537.9994 | 24.5 | 230137.9994 | 27 | 251237.9994 | 30 | 249737.9994 | 38.5 | 256437.9994 | 41 | 255137.9994 | 49.5 | 259737.9994 | 52.5 | 249838.08 | 55.5 | 259337.9994 | 58 | 254437.9994 | 61 | 258337.9994 | 63.5 | 251337.9994 | -100.25 | 211201.9994 | -94.625 | 211201.9994 | -44.25 | 211201.9994 | -38.625 | 211201.9994 | -33.125 | 237537.9994 | 6.125 | 218037.9994 | 11.875 | 212237.9994 | 34.125 | 249737.9994 | 56.75 | 249838.08
66.5 | 211201.9994 | 69 | 211201.9994 | 72 | 211201.9994 | 74.5 | 211201.9994 | 77.5 | 211201.9994 | 97 | 211201.9994 | 100 | 211201.9994 | 102.5 | 211201.9994 | 105.5 | 211201.9994 | 124 | 211201.9994 | 128 | 211201.9994 | 131 | 211201.9994 | 133.5 | 230937.9994 | 136.5 | 212837.9994 | 139 | 237338.0842 | 142 | 251937.9994 | 150.5 | 211201.9994 | 153 | 211201.9994 | 156 | 218737.9994 | 158.5 | 211201.9994 | 161.5 | 252237.9994 | 164.5 | 259537.9994 | 172.5 | 211201.9994 | 181 | 248437.9994 | 184 | 259138.0771 | 186.5 | 212237.9994 | 189.5 | 235637.9994 | 198 | 244237.9994 | 200.5 | 218037.9994 | 203.5 | 247337.9994 | 206.5 | 229338.0871 | 209 | 230137.9994 | 212 | 251237.9994 | 214.5 | 249737.9994 | 223.5 | 256238.078 | 226 | 255137.9994 | 234.5 | 259737.9994 | 237 | 250037.9994 | 240 | 259337.9994 | 242.5 | 254437.9994 | 245.5 | 258337.9994 | 248.5 | 251337.9994 | 84.5 | 211201.9994 | 90 | 211201.9994 | 140.625 | 211201.9994 | 146.125 | 211201.9994 | 151.75 | 237338.0842 | 190.875 | 218037.9994 | 196.5 | 212237.9994 | 219 | 249737.9994 | 241.25 | 250037.9994
251 | 211002.0947 | 254 | 211201.9994 | 256.5 | 211201.9994 | 259.5 | 211201.9994 | 262.5 | 211201.9994 | 282 | 211201.9994 | 284.5 | 211201.9994 | 287.5 | 211002.0947 | 290.5 | 211201.9994 | 310 | 211201.9994 | 312.5 | 211201.9994 | 315.5 | 211201.9994 | 318.5 | 230937.9994 | 321 | 212837.9994 | 324 | 237537.9994 | 326.5 | 251937.9994 | 335 | 211201.9994 | 338 | 211201.9994 | 340.5 | 218737.9994 | 343.5 | 211201.9994 | 346.5 | 252237.9994 | 349 | 259537.9994 | 357.5 | 211201.9994 | 366 | 248437.9994 | 368.5 | 259337.9994 | 371.5 | 212237.9994 | 374.5 | 235637.9994 | 382.5 | 244237.9994 | 385.5 | 218037.9994 | 388.5 | 247337.9994 | 391 | 229537.9994 | 394 | 230137.9994 | 396.5 | 251237.9994 | 399.5 | 249737.9994 | 408 | 256437.9994 | 410.5 | 255137.9994 | 419 | 259737.9994 | 422 | 250037.9994 | 424.5 | 259337.9994 | 427.5 | 254437.9994 | 430.5 | 258337.9994 | 433 | 251337.9994 | 269.25 | 211201.9994 | 275 | 211002.0947 | 325.25 | 211201.9994 | 330.875 | 211201.9994 | 336.5 | 237537.9994 | 375.625 | 218037.9994 | 381.375 | 212237.9994 | 403.625 | 249737.9994 | 426.125 | 250037.9994
436 | 211201.9994 | 438.5 | 211201.9994 | 441.5 | 211201.9994 | 444.5 | 105550.9988 | 447 | 211201.9994 | 466.5 | 211201.9994 | 469.5 | 211201.9994 | 472.5 | 211201.9994 | 475 | 211201.9994 | 494.5 | 211201.9994 | 497.5 | 211201.9994 | 500.5 | 211201.9994 | 503 | 115418.9988 | 506 | 212837.9994 | 508.5 | 237537.9994 | 511.5 | 251937.9994 | 520 | 211201.9994 | 522.5 | 211201.9994 | 525.5 | 218737.9994 | 528.5 | 211201.9994 | 531 | 252237.9994 | 534 | 259537.9994 | 542.5 | 211201.9994 | 550.5 | 248437.9994 | 553.5 | 259337.9994 | 556.5 | 212237.9994 | 559 | 235637.9994 | 567.5 | 244237.9994 | 570.5 | 218037.9994 | 573 | 247337.9994 | 576 | 229537.9994 | 578.5 | 230137.9994 | 581.5 | 251237.9994 | 584.5 | 249737.9994 | 592.5 | 256437.9994 | 595.5 | 255137.9994 | 604 | 259737.9994 | 607 | 250037.9994 | 609.5 | 259337.9994 | 612.5 | 254437.9994 | 615 | 258337.9994 | 618 | 251138.0795 | 454 | 211201.9994 | 459.75 | 105550.9988 | 510.125 | 211201.9994 | 515.75 | 115418.9988 | 521.25 | 237537.9994 | 560.5 | 218037.9994 | 566.125 | 212237.9994 | 588.5 | 249737.9994 | 611 | 250037.9994
620.5 | 211201.9994 | 623.5 | 211201.9994 | 626.5 | 211201.9994 | 629 | 211201.9994 | 632 | 211201.9994 | 651.5 | 211201.9994 | 654.5 | 211201.9994 | 657 | 211201.9994 | 660 | 211201.9994 | 679.5 | 211201.9994 | 682.5 | 211201.9994 | 685 | 211201.9994 | 688 | 230937.9994 | 690.5 | 212837.9994 | 693.5 | 237537.9994 | 696.5 | 251937.9994 | 704.5 | 211201.9994 | 707.5 | 211201.9994 | 710.5 | 218737.9994 | 713 | 211201.9994 | 716 | 252237.9994 | 718.5 | 259537.9994 | 727 | 211201.9994 | 735.5 | 248437.9994 | 738.5 | 259337.9994 | 741 | 212237.9994 | 744 | 235637.9994 | 752.5 | 244237.9994 | 755 | 218037.9994 | 758 | 247337.9994 | 760.5 | 229537.9994 | 763.5 | 230137.9994 | 766.5 | 125568.9988 | 769 | 249737.9994 | 777.5 | 256437.9994 | 780.5 | 255137.9994 | 788.5 | 259737.9994 | 791.5 | 250037.9994 | 794.5 | 259337.9994 | 797 | 254437.9994 | 800 | 258337.9994 | 802.5 | 251337.9994 | 639 | 211201.9994 | 644.5 | 211201.9994 | 694.875 | 211201.9994 | 700.5 | 211201.9994 | 706.125 | 237537.9994 | 745.375 | 218037.9994 | 750.875 | 212237.9994 | 773.375 | 125568.9988 | 795.75 | 250037.9994
805.5 | 211002.0473 | 808.5 | 211201.9994 | 811 | 211201.9994 | 814 | 211201.9994 | 816.5 | 211201.9994 | 836.5 | 211201.9994 | 839 | 211201.9994 | 842 | 211201.9994 | 844.5 | 211201.9994 | 864.5 | 211201.9994 | 867 | 105550.9988 | 869.5 | 211201.9994 | 872.5 | 230937.9994 | 875.5 | 212837.9994 | 878.5 | 237537.9994 | 881 | 251937.9994 | 889.5 | 105550.9988 | 892.5 | 105550.9988 | 895 | 218737.9994 | 898 | 105550.9988 | 900.5 | 252237.9994 | 903.5 | 259537.9994 | 912 | 70333.9982 | 920.5 | 124168.9988 | 923 | 129618.9988 | 926 | 106068.9988 | 928.5 | 58834.4976 | 937 | 122068.9988 | 939.5 | 108968.9988 | 942.5 | 82379.3315 | 945.5 | 57309.4976 | 948.5 | 24.4359 | 951 | 25238.2354 | 954 | 47600.2169 | 962 | 18224.1343 | 965 | 42439.663 | 973.5 | 3.3881 | 976.5 | 0.85794 | 979 | 21.7272 | 982 | 2607.7937 | 984.5 | 3051.6329 | 987.5 | 1.6445 | 823.75 | 211201.9994 | 829.25 | 211201.9994 | 879.625 | 105550.9988 | 885.25 | 105550.9988 | 890.875 | 237537.9994 | 930 | 108968.9988 | 935.625 | 57309.4976 | 958 | 18224.1343 | 980.5 | 0.85794
990 | 28.6794 | 993 | 20920.2235 | 996 | 105301.213 | 998.5 | 210602.5679 | 1001.5 | 70333.9982 | 1021 | 3025.2232 | 1023.5 | 70333.9982 | 1026.5 | 70333.9982 | 1029.5 | 105550.9988 | 1049 | 52725.4976 | 1052 | 70333.9982 | 1054.5 | 70333.9982 | 1057.5 | 76912.6648 | 1060.5 | 106368.9988 | 1063 | 79112.6648 | 1066 | 83912.6648 | 1074.5 | 70333.9982 | 1077 | 70333.9982 | 1080 | 109318.9988 | 1082.5 | 70333.9982 | 1085.5 | 84012.6648 | 1088 | 86445.9982 | 1096.5 | 52725.4976 | 1105 | 62034.4976 | 1107.5 | 64759.4976 | 1110.5 | 70679.3315 | 1113.5 | 26093.1056 | 1121.5 | 81345.9982 | 1124.5 | 72612.6648 | 1127.5 | 82379.3315 | 1130 | 57309.4976 | 1133 | 1.9245 | 1136 | 35.924 | 1138.5 | 31.1062 | 1147 | 37.9946 | 1149.5 | 17.1799 | 1158 | 14.8941 | 1161 | 5.5143 | 1163.5 | 28.0413 | 1166.5 | 18.201 | 1169.5 | 2.8229 | 1172.5 | 0.86931 | 1008.375 | 3025.2232 | 1014 | 70333.9982 | 1064.5 | 70333.9982 | 1070.125 | 70333.9982 | 1075.625 | 79112.6648 | 1114.625 | 62034.4976 | 1120.375 | 26093.1056 | 1142.75 | 17.1799 | 1165.125 | 2.8229
1175 | 15.642 | 1178 | 35033.643 | 1180.5 | 105101.4969 | 1183.5 | 42160.3969 | 1186.5 | 42160.3969 | 1206 | 16153.9921 | 1208.5 | 16153.9921 | 1211.5 | 2172.0077 | 1214 | 2680.2431 | 1234 | 70333.9982 | 1236.5 | 70333.9982 | 1239.5 | 70333.9982 | 1242.5 | 76912.6648 | 1245 | 70879.3315 | 1248 | 79112.6648 | 1250.5 | 83912.6648 | 1259 | 105550.9988 | 1262 | 70333.9982 | 1264.5 | 72845.9982 | 1267.5 | 70333.9982 | 1270 | 84012.6648 | 1273 | 86445.9982 | 1281.5 | 70333.9982 | 1290 | 82745.9982 | 1292.5 | 64759.4976 | 1295.5 | 42367.5969 | 1298.5 | 23473.7939 | 1306.5 | 2879.6816 | 1309.5 | 72612.6648 | 1312.5 | 82379.3315 | 1315 | 7818.534 | 1318 | 68.9389 | 1320.5 | 10.3322 | 1323.5 | 17.9754 | 1331.5 | 57.6634 | 1334.5 | 20.143 | 1343 | 26.6961 | 1346 | 22.1041 | 1348.5 | 4.8816 | 1351.5 | 19.6936 | 1354 | 24.4442 | 1357 | 1.9026 | 1193.25 | 16153.9921 | 1198.875 | 2172.0077 | 1249.25 | 70333.9982 | 1254.875 | 70333.9982 | 1260.375 | 79112.6648 | 1299.625 | 2879.6816 | 1305.375 | 7818.534 | 1327.5 | 10.3322 | 1350 | 4.8816
1359.5 | 17.7047 | 1362.5 | 29585.2439 | 1365.5 | 104801.9227 | 1368 | 184891.2552 | 1371 | 187717.6629 | 1390.5 | 65762.1858 | 1393.5 | 6716.1746 | 1396.5 | 8352.0647 | 1399 | 6943.3817 | 1418.5 | 52725.4976 | 1421.5 | 42160.3969 | 1424 | 70333.9982 | 1427 | 115418.9988 | 1430 | 70879.3315 | 1432.5 | 47427.5969 | 1435.5 | 83912.6648 | 1443.5 | 70333.9982 | 1447 | 70333.9982 | 1449.5 | 72845.9982 | 1452 | 70333.9982 | 1455 | 84012.6648 | 1457.5 | 86445.9982 | 1466 | 4.8647 | 1474.5 | 82745.9982 | 1477.5 | 86379.3315 | 1480 | 52984.4976 | 1483 | 78479.3315 | 1491.5 | 81345.9982 | 1494 | 72612.6648 | 1497 | 82379.3315 | 1499.5 | 76445.9982 | 1502.5 | 45.7618 | 1505.5 | 9.0402 | 1508.5 | 13.0614 | 1516.5 | 41.9025 | 1519.5 | 36.0892 | 1527.5 | 0.94192 | 1530.5 | 14.7032 | 1533.5 | 0.93849 | 1536 | 9.5577 | 1539 | 15.2708 | 1541.5 | 62.7573 | 1378 | 6716.1746 | 1383.625 | 6943.3817 | 1434 | 42160.3969 | 1439.625 | 70333.9982 | 1445.125 | 47427.5969 | 1484.375 | 72612.6648 | 1489.875 | 52984.4976 | 1512.5 | 9.0402 | 1534.75 | 0.93849
1544.5 | 9.4041 | 1547.5 | 33164.3778 | 1550 | 97070.8746 | 1553 | 204155.2887 | 1555.5 | 202973.367 | 1575.5 | 1931.6865 | 1578 | 3053.7203 | 1581 | 2717.3142 | 1583.5 | 2056.083 | 1603.5 | 70333.9982 | 1606 | 70333.9982 | 1609 | 70333.9982 | 1611.5 | 10401.7138 | 1614.5 | 42487.5969 | 1617.5 | 79112.6648 | 1620 | 25103.7939 | 1628.5 | 53.2855 | 1631.5 | 140.4019 | 1634 | 226.1289 | 1637 | 488.3658 | 1639.5 | 249.0578 | 1642.5 | 280.2845 | 1651 | 9.5372 | 1659.5 | 1702.0076 | 1662 | 64759.4976 | 1665 | 42367.5969 | 1667.5 | 11686.8878 | 1676 | 12116.8878 | 1679 | 5353.4256 | 1681.5 | 4240.9827 | 1684.5 | 2292.0039 | 1687.5 | 28.4072 | 1690 | 24.766 | 1693 | 25.6837 | 1701.5 | 85412.6648 | 1704 | 3396.3664 | 1712.5 | 15.9025 | 1715.5 | 13.6247 | 1718 | 0.59027 | 1721 | 4.3242 | 1723.5 | 27.4783 | 1726.5 | 11657.262 | 1562.75 | 1931.6865 | 1568.25 | 2056.083 | 1618.75 | 53.2855 | 1624.25 | 226.1289 | 1629.875 | 249.0578 | 1669.125 | 1702.0076 | 1674.625 | 2292.0039 | 1697.125 | 24.766 | 1719.5 | 0.59027
1729.5 | 9.1222 | 1732 | 28150.3405 | 1735 | 103553.698 | 1737.5 | 196322.8706 | 1740.5 | 105550.9988 | 1760 | 70333.9982 | 1763 | 70333.9982 | 1765.5 | 70333.9982 | 1768.5 | 70333.9982 | 1788 | 5.4053 | 1791 | 31135.9373 | 1793.5 | 90348.3283 | 1796.5 | 123502.7909 | 1799.5 | 26517.2451 | 1802 | 4945.366 | 1805 | 83912.6648 | 1813.5 | 52725.4976 | 1816 | 52725.4976 | 1819 | 4190.91 | 1821.5 | 52725.4976 | 1824.5 | 84012.6648 | 1827.5 | 64809.4976 | 1835.5 | 16.6781 | 1844 | 39.0173 | 1847 | 47.524 | 1849.5 | 9.1882 | 1852.5 | 24.7177 | 1861 | 48.1685 | 1863.5 | 39.5142 | 1866.5 | 34.244 | 1869.5 | 12.1086 | 1872 | 0.67907 | 1875 | 19.919 | 1877.5 | 11.6479 | 1886.5 | 85412.6648 | 1889 | 84979.3315 | 1897.5 | 11.7183 | 1900 | 0.44513 | 1903 | 0.018537 | 1905.5 | 0.89627 | 1908.5 | 0.92992 | 1911.5 | 20.7997 | 1747.5 | 28150.3405 | 1753 | 70333.9982 | 1803.5 | 31135.9373 | 1809.125 | 4190.91 | 1814.75 | 4945.366 | 1853.875 | 39.0173 | 1859.5 | 9.1882 | 1882 | 11.6479 | 1904.25 | 0.018537
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 43 |  |  | 2006-08-18 | 15:20
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-112.8 | 211202 |  | -90.5 | 211202 | -62.3889 | 211202 | -46.9444 | 211202 | -32.5556 | 211202 | -23.8333 | 211202 | 0.3 | 218738 | 5.9 | 211202 | 18.1667 | 237538 | 21.2222 | 218038 | 39 | 212238 | 41.3 | 229538 | -112.8 | 211202 | -62.3889 | 211202 | -32.5556 | 211202 | -25.7833 | 211202 | -17.4861 | 211202 | 11.3972 | 211202 | -4.25 | 211202 | 5.9778 | 211202 | 29.9222 | 212238 | -101.65 | 211202 | -54.6667 | 211202 | -28.1944 | 211202 | 3.1 | 211202 | 19.6944 | 218038 | 40.15 | 212238
71.9 | 211202 |  | 94.3 | 211202 | 122.2222 | 211202 | 137.7778 | 211202 | 152.1111 | 211202 | 160.8889 | 211202 | 185 | 218738 | 190.7 | 211202 | 202.9444 | 237538 | 206 | 218038 | 223.6 | 212238 | 226 | 229538 | 71.9 | 211202 | 122.2222 | 211202 | 152.1111 | 211202 | 158.925 | 211202 | 167.2361 | 211202 | 196.1611 | 211202 | 180.4861 | 211202 | 190.65 | 211202 | 214.6361 | 212238 | 83.1 | 211202 | 130 | 211202 | 156.5 | 211202 | 187.85 | 211202 | 204.4722 | 218038 | 224.8 | 212238
256.7 | 211202 |  | 279.1 | 211202 | 307.1111 | 211202 | 322.6111 | 211202 | 336.9444 | 211202 | 345.7222 | 211202 | 369.8 | 218738 | 375.4 | 211202 | 387.6667 | 237538 | 390.7222 | 218038 | 408.5 | 212238 | 410.7 | 229538 | 256.7 | 211202 | 307.1111 | 211202 | 336.9444 | 211202 | 343.7306 | 211202 | 352.0278 | 211202 | 380.8972 | 211202 | 365.2639 | 211202 | 375.4667 | 211202 | 399.3972 | 212238 | 267.9 | 211202 | 314.8611 | 211202 | 341.3333 | 211202 | 372.6 | 211202 | 389.1944 | 218038 | 409.6 | 212238
441.5 | 105551 |  | 463.9 | 211202 | 491.8333 | 115419 | 507.4444 | 211202 | 521.8333 | 105551 | 530.5 | 211202 | 554.6 | 218738 | 560.2 | 211202 | 572.4444 | 237538 | 575.6667 | 218038 | 593.4 | 212238 | 595.5 | 229538 | 441.5 | 105551 | 491.8333 | 115419 | 521.8333 | 105551 | 528.5194 | 115419 | 536.8472 | 115419 | 565.7278 | 211202 | 550.1111 | 105551 | 560.3083 | 105551 | 584.2528 | 212238 | 452.7 | 105551 | 499.6389 | 115419 | 526.1667 | 105551 | 557.4 | 211202 | 574.0556 | 218038 | 594.45 | 212238
626.3 | 211202 |  | 648.7 | 211202 | 676.7222 | 211202 | 692.2778 | 211202 | 706.5556 | 211202 | 715.2778 | 211202 | 739.5 | 125569 | 745 | 211202 | 757.3333 | 237538 | 760.3889 | 218038 | 778 | 212238 | 780.3 | 229538 | 626.3 | 211202 | 676.7222 | 125569 | 706.5556 | 211202 | 713.375 | 125569 | 721.6806 | 211202 | 750.5556 | 125569 | 734.8889 | 211202 | 745.0333 | 211202 | 769.0056 | 212238 | 637.5 | 211202 | 684.5 | 211202 | 710.9167 | 211202 | 742.25 | 125569 | 758.8611 | 218038 | 779.15 | 212238
811.1 | 211202 |  | 833.5 | 211101.9527 | 861.5 | 105551 | 877.0556 | 105551 | 891.3889 | 58834.5 | 899.9444 | 57309.5 | 924.2 | 656.9533 | 929.8 | 2369.4911 | 942.0556 | 0.65915 | 945.1111 | 24.366 | 962.9 | 0.6664 | 965 | 0.6997 | 811.1 | 57309.5 | 861.5 | 0.65915 | 891.3889 | 0.65915 | 898.1389 | 656.9533 | 906.4306 | 0.65915 | 935.2917 | 0.65915 | 919.625 | 0.65915 | 929.8083 | 0.6664 | 953.7667 | 0.65915 | 822.3 | 211101.9527 | 869.2778 | 105551 | 895.6667 | 57309.5 | 927 | 656.9533 | 943.5833 | 0.65915 | 963.95 | 0.6664
995.8 | 5742.9563 |  | 1018.1 | 7210.9024 | 1046.2778 | 52725.5 | 1061.7778 | 16154 | 1076.0556 | 26093.1111 | 1084.7222 | 57309.5 | 1109 | 2.0142 | 1114.5 | 6.3039 | 1126.7222 | 0.65337 | 1129.7778 | 0.63488 | 1147.6 | 0.65572 | 1149.8 | 13.4136 | 995.8 | 5742.9563 | 1046.2778 | 0.63488 | 1076.0556 | 0.63488 | 1082.8889 | 2.0142 | 1091.1389 | 0.63488 | 1120 | 0.63488 | 1104.3194 | 0.63488 | 1114.5444 | 0.65572 | 1138.475 | 0.63488 | 1006.95 | 5742.9563 | 1054.0278 | 16154 | 1080.3889 | 26093.1111 | 1111.75 | 2.0142 | 1128.25 | 0.63488 | 1148.7 | 0.65572
1180.7 | 682.9256 |  | 1203 | 1406.5884 | 1231.1111 | 70334 | 1246.5556 | 2876.0845 | 1260.9444 | 23473.8 | 1269.6667 | 2879.7317 | 1293.8 | 0.75414 | 1299.3 | 0.7752 | 1311.5556 | 0.65599 | 1314.6667 | 0.63538 | 1332.5 | 3.3873 | 1334.6 | 4.1151 | 1180.7 | 682.9256 | 1231.1111 | 0.63538 | 1260.9444 | 0.63538 | 1267.6917 | 0.75414 | 1275.9722 | 0.63538 | 1304.8306 | 0.63538 | 1289.2083 | 0.63538 | 1299.4278 | 3.3873 | 1323.3306 | 0.63538 | 1191.85 | 682.9256 | 1238.8333 | 2876.0845 | 1265.3056 | 2879.7317 | 1296.55 | 0.75414 | 1313.1111 | 0.63538 | 1333.55 | 3.3873
1365.3 | 205.0054 |  | 1387.8 | 165.7459 | 1415.7778 | 32056.0467 | 1431.3333 | 1308.68 | 1445.6111 | 748.2221 | 1454.3333 | 594.706 | 1478.6 | 0.71404 | 1484.1 | 6.9503 | 1496.3333 | 0.63439 | 1499.4444 | 0.6459 | 1517 | 11.9123 | 1519.3 | 0.71842 | 1365.3 | 165.7459 | 1415.7778 | 0.63439 | 1445.6111 | 0.63439 | 1452.4528 | 0.71404 | 1460.7222 | 0.63439 | 1489.6194 | 0.63439 | 1473.9306 | 0.63439 | 1484.0611 | 0.71842 | 1508.0194 | 0.63439 | 1376.55 | 165.7459 | 1423.5556 | 1308.68 | 1449.9722 | 594.706 | 1481.35 | 0.71404 | 1497.8889 | 0.63439 | 1518.15 | 0.71842
1550.1 | 106.2707 |  | 1572.5 | 98.8752 | 1600.5556 | 10401.7273 | 1616.0556 | 54.1225 | 1630.3889 | 1679.6428 | 1639.0556 | 2292.0625 | 1663.2 | 6.4691 | 1668.9 | 127.7412 | 1681.1111 | 0.6426 | 1684.1667 | 2.8699 | 1701.9 | 23.349 | 1704 | 14.342 | 1550.1 | 54.1225 | 1600.5556 | 0.6426 | 1630.3889 | 0.6426 | 1637.1778 | 6.4691 | 1645.4722 | 0.6426 | 1674.3444 | 0.6426 | 1658.6806 | 0.6426 | 1668.8361 | 14.342 | 1692.7944 | 0.6426 | 1561.3 | 98.8752 | 1608.3056 | 54.1225 | 1634.7222 | 1679.6428 | 1666.05 | 6.4691 | 1682.6389 | 0.6426 | 1702.95 | 14.342
1734.9 | 22893.5735 |  | 1757.3 | 1210.4948 | 1785.2778 | 70.9451 | 1800.8889 | 66.1135 | 1815.1111 | 10.3628 | 1823.8333 | 13.3455 | 1848 | 0.71654 | 1853.7 | 70334 | 1865.9444 | 1.0659 | 1869 | 0.63785 | 1886.6 | 22.0573 | 1889 | 26.5415 | 1734.9 | 10.3628 | 1785.2778 | 0.63785 | 1815.1111 | 0.63785 | 1821.9667 | 0.71654 | 1830.2778 | 0.63785 | 1859.1611 | 0.63785 | 1843.4722 | 0.63785 | 1853.6361 | 10.3628 | 1877.6361 | 0.63785 | 1746.1 | 1210.4948 | 1793.0833 | 66.1135 | 1819.4722 | 10.3628 | 1850.85 | 0.71654 | 1867.4722 | 0.63785 | 1887.8 | 22.0573
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0

## F11-F12
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 153.5031 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38947.6399 | 1 | 0 | 38947.6399 | 1 | 0 |  | 63.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38947.642 | 1 | 0 | 38947.642 | 1 | 0 |  | 248.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38947.6441 | 1 | 0 | 38947.6442 | 1 | 0 |  | 433 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38947.6463 | 1 | 1 | 38947.6463 | 1 | 0 |  | 618 | 737 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 631707902.44 | 251338 | 251138.0795
38947.6484 | 1 | 0 | 38947.6484 | 1 | 0 |  | 802.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38947.6506 | 2438 | 0 | 38947.6506 | 2291 | 0 |  | 987.5 | 1106.5 | 148.84 | 0 | 139.8657 | 0 | 1.4884 | 0 | 1.3987 | 0 | 1.4884 | 1.3987 | 3.1329 | 9.7503 | 1.6445
38947.6527 | 2498 | 0 | 38947.6527 | 2217 | 0 |  | 1172.5 | 1291.5 | 152.5031 | 0 | 135.348 | 0 | 1.525 | 0 | 1.3535 | 0 | 1.525 | 1.3535 | 0.65572 | 13.4136 | 0.86931
38947.6548 | 2432 | 0 | 38947.6548 | 2415 | 0 |  | 1357 | 1476 | 148.4737 | 0 | 147.4359 | 0 | 1.4847 | 0 | 1.4744 | 0 | 1.4847 | 1.4744 | 3.3873 | 4.1151 | 1.9026
38947.657 | 1663 | 356 | 38947.657 | 1533 | 167 |  | 1541.5 | 1660.5 | 101.5263 | 21.7338 | 93.5897 | 10.1954 | 1.0153 | 0.21734 | 0.9359 | 0.10195 | 0.79792 | 0.83394 | 97.4519 | 82.1491 | 62.7573
38947.6591 | 1584 | 1 | 38947.6591 | 2199 | 0 |  | 1726.5 | 1845.5 | 96.7033 | 0.06105 | 134.2491 | 0 | 0.96703 | 0.0006105 | 1.3425 | 0 | 0.96642 | 1.3425 | 59.0332 | 14.342 | 11657.262
38947.6612 | 2060 | 0 | 38947.6613 | 1987 | 0 |  | 1911.5 | 2030.5 | 125.7631 | 0 | 121.3065 | 0 | 1.2576 | 0 | 1.2131 | 0 | 1.2576 | 1.2131 | 22.0573 | 26.5415 | 20.7997

## E10-F12
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 157.7766 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38947.6398 | 1 | 0 | 38947.6398 | 1 | 0 |  | 61 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38947.642 | 1 | 0 | 38947.642 | 1 | 0 |  | 245.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38947.6441 | 1 | 0 | 38947.6441 | 1 | 0 |  | 430.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38947.6462 | 1 | 0 | 38947.6463 | 1 | 0 |  | 615 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38947.6484 | 1 | 0 | 38947.6484 | 1 | 0 |  | 800 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38947.6505 | 82 | 0 | 38947.6505 | 1944 | 0 |  | 984.5 | 1103.5 | 5.0061 | 0 | 118.6813 | 0 | 0.050061 | 0 | 1.1868 | 0 | 0.050061 | 1.1868 | 3051.6829 | 32.9414 | 3051.6329
38947.6527 | 2477 | 0 | 38947.6527 | 2010 | 0 |  | 1169.5 | 1288.5 | 151.221 | 0 | 122.7106 | 0 | 1.5122 | 0 | 1.2271 | 0 | 1.5122 | 1.2271 | 4.3351 | 28.5761 | 2.8229
38947.6548 | 2056 | 0 | 38947.6548 | 2055 | 0 |  | 1354 | 1473 | 125.5189 | 0 | 125.4579 | 0 | 1.2552 | 0 | 1.2546 | 0 | 1.2552 | 1.2546 | 25.6994 | 25.7606 | 24.4442
38947.6569 | 2216 | 0 | 38947.657 | 1606 | 0 |  | 1539 | 1658 | 135.2869 | 0 | 98.0464 | 0 | 1.3529 | 0 | 0.98046 | 0 | 1.3529 | 0.98046 | 16.6236 | 60.9203 | 15.2708
38947.6591 | 2008 | 0 | 38947.6591 | 1991 | 0 |  | 1723.5 | 1842.5 | 122.5885 | 0 | 121.5507 | 0 | 1.2259 | 0 | 1.2155 | 0 | 1.2259 | 1.2155 | 28.7042 | 29.8031 | 27.4783
38947.6612 | 2568 | 0 | 38947.6612 | 1558 | 0 |  | 1908.5 | 2027.5 | 156.7766 | 0 | 95.116 | 0 | 1.5678 | 0 | 0.95116 | 0 | 1.5678 | 0.95116 | 0.63785 | 65.878 | 0.92992

## E10-F11
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 155.3956 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38947.6398 | 1 | 0 | 38947.6398 | 1 | 0 |  | 58 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38947.6419 | 1 | 0 | 38947.6419 | 1 | 0 |  | 242.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38947.6441 | 1 | 0 | 38947.6441 | 1 | 0 |  | 427.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38947.6462 | 1 | 0 | 38947.6462 | 1 | 0 |  | 612.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38947.6483 | 1 | 0 | 38947.6484 | 1 | 0 |  | 797 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38947.6505 | 94 | 0 | 38947.6505 | 1928 | 0 |  | 982 | 1101 | 5.7387 | 0 | 117.7045 | 0 | 0.057387 | 0 | 1.177 | 0 | 0.057387 | 1.177 | 2607.8511 | 32.0218 | 2607.7937
38947.6526 | 2130 | 0 | 38947.6526 | 1959 | 0 |  | 1166.5 | 1285.5 | 130.0366 | 0 | 119.5971 | 0 | 1.3004 | 0 | 1.196 | 0 | 1.3004 | 1.196 | 19.5014 | 29.9326 | 18.201
38947.6548 | 2104 | 0 | 38947.6548 | 2020 | 0 |  | 1351.5 | 1470.5 | 128.4493 | 0 | 123.3211 | 0 | 1.2845 | 0 | 1.2332 | 0 | 1.2845 | 1.2332 | 20.9781 | 26.0089 | 19.6936
38947.6569 | 2294 | 0 | 38947.6569 | 2033 | 0 |  | 1536 | 1655 | 140.0488 | 0 | 124.1148 | 0 | 1.4005 | 0 | 1.2411 | 0 | 1.4005 | 1.2411 | 10.9582 | 25.2031 | 9.5577
38947.659 | 2406 | 0 | 38947.6591 | 1524 | 0 |  | 1721 | 1840 | 146.8864 | 0 | 93.0403 | 0 | 1.4689 | 0 | 0.9304 | 0 | 1.4689 | 0.9304 | 5.793 | 67.0197 | 4.3242
38947.6612 | 2529 | 0 | 38947.6612 | 1997 | 0 |  | 1905.5 | 2024.5 | 154.3956 | 0 | 121.917 | 0 | 1.544 | 0 | 1.2192 | 0 | 1.544 | 1.2192 | 0.64769 | 27.4602 | 0.89627

## E9-F12
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 158.3871 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38947.6398 | 1 | 0 | 38947.6398 | 1 | 0 |  | 55.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6419 | 1 | 0 | 38947.6419 | 1 | 0 |  | 240 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.644 | 1 | 0 | 38947.6441 | 1 | 0 |  | 424.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6462 | 1 | 0 | 38947.6462 | 1 | 0 |  | 609.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6483 | 1 | 0 | 38947.6483 | 1 | 0 |  | 794.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6505 | 2109 | 0 | 38947.6505 | 1976 | 0 |  | 979 | 1098 | 128.7546 | 0 | 120.6349 | 0 | 1.2875 | 0 | 1.2063 | 0 | 1.2875 | 1.2063 | 23.0147 | 31.2945 | 21.7272
38947.6526 | 2007 | 0 | 38947.6526 | 2238 | 0 |  | 1163.5 | 1282.5 | 122.5275 | 0 | 136.63 | 0 | 1.2253 | 0 | 1.3663 | 0 | 1.2253 | 1.3663 | 29.2666 | 15.924 | 28.0413
38947.6547 | 2439 | 0 | 38947.6547 | 2105 | 0 |  | 1348.5 | 1467.5 | 148.9011 | 0 | 128.5104 | 0 | 1.489 | 0 | 1.2851 | 0 | 1.489 | 1.2851 | 6.3706 | 23.2485 | 4.8816
38947.6569 | 2578 | 0 | 38947.6569 | 1923 | 0 |  | 1533.5 | 1652.5 | 157.3871 | 0 | 117.3993 | 0 | 1.5739 | 0 | 1.174 | 0 | 1.5739 | 1.174 | 0.63538 | 34.9132 | 0.93849
38947.659 | 2540 | 0 | 38947.659 | 1912 | 0 |  | 1718 | 1837 | 155.0672 | 0 | 116.7277 | 0 | 1.5507 | 0 | 1.1673 | 0 | 1.5507 | 1.1673 | 2.1409 | 35.6893 | 0.59027
38947.6611 | 2555 | 0 | 38947.6612 | 1190 | 0 |  | 1903 | 2022 | 155.9829 | 0 | 72.6496 | 0 | 1.5598 | 0 | 0.7265 | 0 | 1.5598 | 0.7265 | 1.5413 | 118.0151 | 0.018537

## E9-F11
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 152.7094 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38947.6397 | 1 | 1 | 38947.6397 | 1 | 0 |  | 52.5 | 171.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 625190014.44 | 250038 | 249838.08
38947.6419 | 1 | 0 | 38947.6419 | 1 | 0 |  | 237 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38947.644 | 1 | 0 | 38947.644 | 1 | 0 |  | 422 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
| 1 | 0 | 38947.6462 | 1 | 0 |  | 607 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38947.6483 | 1 | 0 | 38947.6483 | 1 | 0 |  | 791.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38947.6504 | 2485 | 0 | 38947.6504 | 1840 | 0 |  | 976.5 | 1095.5 | 151.7094 | 0 | 112.3321 | 0 | 1.5171 | 0 | 1.1233 | 0 | 1.5171 | 1.1233 | 0.65915 | 35.9446 | 0.85794
38947.6526 | 2339 | 0 | 38947.6526 | 2101 | 0 |  | 1161 | 1280 | 142.7961 | 0 | 128.2662 | 0 | 1.428 | 0 | 1.2827 | 0 | 1.428 | 1.2827 | 6.9423 | 19.0566 | 5.5143
38947.6547 | 2028 | 0 | 38947.6547 | 1920 | 0 |  | 1346 | 1465 | 123.8095 | 0 | 117.2161 | 0 | 1.2381 | 0 | 1.1722 | 0 | 1.2381 | 1.1722 | 23.3422 | 30.2802 | 22.1041
38947.6568 | 2156 | 0 | 38947.6569 | 1689 | 0 |  | 1530.5 | 1649.5 | 131.6239 | 0 | 103.1136 | 0 | 1.3162 | 0 | 1.0311 | 0 | 1.3162 | 1.0311 | 16.0195 | 48.0983 | 14.7032
38947.659 | 2176 | 0 | 38947.659 | 1362 | 0 |  | 1715.5 | 1834.5 | 132.8449 | 0 | 83.1502 | 0 | 1.3284 | 0 | 0.8315 | 0 | 1.3284 | 0.8315 | 14.9531 | 83.6549 | 13.6247
38947.6611 | 2475 | 0 | 38947.6611 | 1817 | 0 |  | 1900 | 2019 | 151.0989 | 0 | 110.928 | 0 | 1.511 | 0 | 1.1093 | 0 | 1.511 | 1.1093 | 1.0659 | 37.6654 | 0.44513

## E9-E10
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 158.6313 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38947.6397 | 1 | 0 | 38947.6397 | 1 | 0 |  | 49.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38947.6418 | 1 | 0 | 38947.6419 | 1 | 0 |  | 234.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38947.644 | 1 | 0 | 38947.644 | 1 | 0 |  | 419 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38947.6461 | 1 | 0 | 38947.6461 | 1 | 0 |  | 604 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38947.6483 | 1 | 0 | 38947.6483 | 1 | 0 |  | 788.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
38947.6504 | 2477 | 0 | 38947.6504 | 1164 | 2 |  | 973.5 | 1092.5 | 151.221 | 0 | 71.0623 | 0.1221 | 1.5122 | 0 | 0.71062 | 0.001221 | 1.5122 | 0.7094 | 4.9003 | 123.6127 | 3.3881
38947.6525 | 2235 | 0 | 38947.6525 | 2205 | 0 |  | 1158 | 1277 | 136.4469 | 0 | 134.6154 | 0 | 1.3645 | 0 | 1.3462 | 0 | 1.3645 | 1.3462 | 16.2586 | 17.8404 | 14.8941
38947.6547 | 2031 | 0 | 38947.6547 | 2102 | 0 |  | 1343 | 1462 | 123.9927 | 0 | 128.3272 | 0 | 1.2399 | 0 | 1.2833 | 0 | 1.2399 | 1.2833 | 27.936 | 23.6147 | 26.6961
38947.6568 | 2582 | 0 | 38947.6568 | 2559 | 0 |  | 1527.5 | 1646.5 | 157.6313 | 0 | 156.2271 | 0 | 1.5763 | 0 | 1.5623 | 0 | 1.5763 | 1.5623 | 0.63439 | 1.5389 | 0.94192
38947.6589 | 2216 | 0 | 38947.659 | 2286 | 0 |  | 1712.5 | 1831.5 | 135.2869 | 0 | 139.5604 | 0 | 1.3529 | 0 | 1.3956 | 0 | 1.3529 | 1.3956 | 17.2554 | 13.6649 | 15.9025
38947.6611 | 2297 | 0 | 38947.6611 | 2366 | 0 |  | 1897.5 | 2016.5 | 140.232 | 0 | 144.4444 | 0 | 1.4023 | 0 | 1.4444 | 0 | 1.4023 | 1.4444 | 13.1206 | 9.8216 | 11.7183

## D8-E10
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 155.823 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38947.6396 | 1 | 0 | 38947.6396 | 1 | 0 |  | 41 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38947.6417 | 1 | 0 | 38947.6418 | 1 | 0 |  | 226 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38947.6439 | 1 | 0 | 38947.6439 | 1 | 0 |  | 410.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38947.646 | 1 | 0 | 38947.646 | 1 | 0 |  | 595.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38947.6482 | 1 | 0 | 38947.6482 | 1 | 0 |  | 780.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38947.6503 | 6 | 0 | 38947.6503 | 34 | 0 |  | 965 | 1084 | 0.3663 | 0 | 2.0757 | 0 | 0.003663 | 0 | 0.020757 | 0 | 0.003663 | 0.020757 | 42439.6667 | 7407 | 42439.663
38947.6524 | 2154 | 0 | 38947.6524 | 2433 | 0 |  | 1149.5 | 1268.5 | 131.5018 | 0 | 148.5348 | 0 | 1.315 | 0 | 1.4853 | 0 | 1.315 | 1.4853 | 18.4949 | 4.9067 | 17.1799
38947.6546 | 2102 | 0 | 38947.6546 | 2135 | 0 |  | 1334.5 | 1453.5 | 128.3272 | 0 | 130.3419 | 0 | 1.2833 | 0 | 1.3034 | 0 | 1.2833 | 1.3034 | 21.4263 | 19.5494 | 20.143
38947.6567 | 1860 | 0 | 38947.6567 | 2536 | 0 |  | 1519.5 | 1638.5 | 113.5531 | 0 | 154.823 | 0 | 1.1355 | 0 | 1.5482 | 0 | 1.1355 | 1.5482 | 37.2247 | 0.6459 | 36.0892
38947.6588 | 73 | 0 | 38947.6589 | 2303 | 0 |  | 1704 | 1823 | 4.4567 | 0 | 140.5983 | 0 | 0.044567 | 0 | 1.406 | 0 | 0.044567 | 1.406 | 3396.411 | 10.8285 | 3396.3664
38947.661 | 3 | 0 | 38947.661 | 2235 | 0 |  | 1889 | 2008 | 0.18315 | 0 | 136.4469 | 0 | 0.0018315 | 0 | 1.3645 | 0 | 0.0018315 | 1.3645 | 84979.3333 | 14.2004 | 84979.3315

## D8-E9
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 156.6166 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38947.6396 | 1 | 0 | 38947.6396 | 1 | 0 |  | 38.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38947.6417 | 1 | 1 | 38947.6417 | 1 | 0 |  | 223.5 | 342.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 657604478.44 | 256438 | 256238.078
38947.6438 | 1 | 0 | 38947.6439 | 1 | 0 |  | 408 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38947.646 | 1 | 0 | 38947.646 | 1 | 0 |  | 592.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38947.6481 | 1 | 0 | 38947.6481 | 1 | 0 |  | 777.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38947.6503 | 14 | 0 | 38947.6503 | 2179 | 0 |  | 962 | 1081 | 0.8547 | 0 | 133.0281 | 0 | 0.008547 | 0 | 1.3303 | 0 | 0.008547 | 1.3303 | 18224.1429 | 17.732 | 18224.1343
38947.6524 | 1844 | 0 | 38947.6524 | 2449 | 0 |  | 1147 | 1266 | 112.5763 | 0 | 149.5116 | 0 | 1.1258 | 0 | 1.4951 | 0 | 1.1258 | 1.4951 | 39.1204 | 4.7521 | 37.9946
38947.6545 | 1617 | 0 | 38947.6545 | 2167 | 0 |  | 1331.5 | 1450.5 | 98.7179 | 0 | 132.2955 | 0 | 0.98718 | 0 | 1.323 | 0 | 0.98718 | 1.323 | 58.6506 | 18.3839 | 57.6634
38947.6567 | 1794 | 0 | 38947.6567 | 2184 | 0 |  | 1516.5 | 1635.5 | 109.5238 | 0 | 133.3333 | 0 | 1.0952 | 0 | 1.3333 | 0 | 1.0952 | 1.3333 | 42.9978 | 17.4625 | 41.9025
38947.6588 | 3 | 0 | 38947.6588 | 2549 | 0 |  | 1701.5 | 1820.5 | 0.18315 | 0 | 155.6166 | 0 | 0.0018315 | 0 | 1.5562 | 0 | 0.0018315 | 1.5562 | 85412.6667 | 0.6426 | 85412.6648
38947.661 | 3 | 0 | 38947.661 | 2374 | 0 |  | 1886.5 | 2005.5 | 0.18315 | 0 | 144.9328 | 0 | 0.0018315 | 0 | 1.4493 | 0 | 0.0018315 | 1.4493 | 85412.6667 | 8.0615 | 85412.6648

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 43 |  |  | 2006-08-18 | 15:20
38947.6378 | 1 | 0 | 1 | EPR&PE | 7-C | Tray
38947.6399 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38947.642 | 1 | 1 | 1
38947.6442 | 1 | 0 | 1
38947.6463 | 1 | 0 | 1
38947.6484 | 1 | 1 | 1
38947.6506 | 941 | 908 | 1
38947.6527 | 1179 | 1122 | 1
38947.6549 | 937 | 916 | 1
38947.657 | 1019 | 920 | 1
38947.6591 | 1155 | 1063 | 1
1
38947.6378 | 1 | 0 | 2
38947.6399 | 1 | 0 | 2
38947.642 | 1 | 0 | 2
38947.6442 | 1 | 0 | 2
38947.6463 | 1 | 0 | 2
38947.6485 | 2 | 1 | 2
38947.6506 | 918 | 886 | 2
38947.6527 | 1086 | 1102 | 2
38947.6549 | 1179 | 1118 | 2
38947.657 | 1194 | 1131 | 2
38947.6592 | 1113 | 1027 | 2
2
38947.6378 | 1 | 0 | 3
38947.6399 | 1 | 0 | 3
38947.6421 | 1 | 0 | 3
38947.6442 | 1 | 0 | 3
38947.6463 | 1 | 0 | 3
38947.6485 | 1 | 0 | 3
38947.6506 | 10 | 10 | 3
38947.6528 | 5 | 6 | 3
38947.6549 | 35 | 7 | 3
38947.657 | 117 | 6 | 3
38947.6592 | 4 | 7 | 3
3
38947.6378 | 1 | 0 | 4
38947.6399 | 1 | 0 | 4
38947.6421 | 1 | 0 | 4
38947.6442 | 1 | 0 | 4
38947.6464 | 1 | 0 | 4
38947.6485 | 1 | 0 | 4
38947.6506 | 16 | 15 | 4
38947.6528 | 3 | 3 | 4
38947.6549 | 4 | 4 | 4
38947.657 | 3 | 3 | 4
38947.6592 | 135 | 3 | 4
4
38947.6378 | 1 | 0 | 5
38947.64 | 1 | 0 | 5
38947.6421 | 1 | 0 | 5
38947.6442 | 1 | 0 | 5
38947.6464 | 1 | 0 | 5
38947.6485 | 1 | 0 | 5
38947.6506 | 3 | 2 | 5
38947.6528 | 7 | 2 | 5
38947.6549 | 13 | 2 | 5
38947.6571 | 136 | 2 | 5
38947.6592 | 2 | 2 | 5
5
38947.6378 | 1 | 0 | 6
38947.64 | 1 | 0 | 6
38947.6421 | 1 | 0 | 6
38947.6442 | 1 | 0 | 6
38947.6464 | 1 | 0 | 6
38947.6485 | 1 | 0 | 6
38947.6507 | 3 | 1 | 6
38947.6528 | 3 | 1 | 6
38947.6549 | 3 | 1 | 6
38947.6571 | 37 | 1 | 6
38947.6592 | 39 | 1 | 6
6
38947.6378 | 1 | 0 | 7
38947.64 | 1 | 0 | 7
38947.6421 | 1 | 0 | 7
38947.6443 | 2 | 0 | 7
38947.6464 | 1 | 0 | 7
38947.6485 | 1 | 0 | 7
38947.6507 | 3 | 1 | 7
38947.6528 | 5 | 0 | 7
38947.655 | 16 | 1 | 7
38947.6571 | 49 | 1 | 7
38947.6592 | 2 | 1 | 7
7
38947.6379 | 1 | 0 | 8
38947.64 | 1 | 0 | 8
38947.6421 | 1 | 0 | 8
38947.6443 | 1 | 0 | 8
38947.6464 | 1 | 0 | 8
38947.6486 | 1 | 0 | 8
38947.6507 | 3 | 0 | 8
38947.6528 | 3 | 1 | 8
38947.655 | 250 | 1 | 8
38947.6571 | 23 | 1 | 8
38947.6592 | 147 | 0 | 8
8
38947.6379 | 1 | 0 | 9
38947.64 | 1 | 0 | 9
38947.6422 | 1 | 0 | 9
38947.6443 | 1 | 0 | 9
38947.6464 | 1 | 0 | 9
38947.6486 | 1 | 0 | 9
38947.6507 | 3 | 0 | 9
38947.6529 | 5 | 0 | 9
38947.655 | 20 | 1 | 9
38947.6571 | 57 | 1 | 9
38947.6593 | 2 | 0 | 9
9
38947.6379 | 1 | 0 | 10
38947.64 | 1 | 0 | 10
38947.6422 | 1 | 0 | 10
38947.6443 | 1 | 0 | 10
38947.6465 | 1 | 0 | 10
38947.6486 | 1 | 0 | 10
38947.6507 | 3 | 0 | 10
38947.6529 | 3 | 0 | 10
38947.655 | 217 | 0 | 10
38947.6571 | 26 | 0 | 10
38947.6593 | 153 | 0 | 10
10
38947.6379 | 1 | 0 | 11
38947.6401 | 1 | 0 | 11
38947.6422 | 1 | 0 | 11
38947.6443 | 1 | 0 | 11
38947.6465 | 1 | 0 | 11
38947.6486 | 1 | 0 | 11
38947.6508 | 3 | 0 | 11
38947.6529 | 15 | 0 | 11
38947.655 | 8 | 0 | 11
38947.6572 | 49 | 0 | 11
38947.6593 | 2 | 0 | 11
11
38947.6379 | 1 | 0 | 12
38947.6401 | 1 | 0 | 12
38947.6422 | 1 | 0 | 12
38947.6444 | 1 | 0 | 12
38947.6465 | 1 | 0 | 12
38947.6486 | 1 | 0 | 12
38947.6508 | 274 | 0 | 12
38947.6529 | 2238 | 0 | 12
38947.655 | 1905 | 0 | 12
38947.6572 | 1938 | 0 | 12
38947.6593 | 2060 | 0 | 12
12
38947.638 | 1 | 0 | 13
38947.6401 | 1 | 0 | 13
38947.6422 | 1 | 0 | 13
38947.6444 | 1 | 0 | 13
38947.6465 | 1 | 0 | 13
38947.6486 | 1 | 0 | 13
38947.6508 | 3 | 0 | 13
38947.6529 | 34 | 0 | 13
38947.6551 | 9 | 0 | 13
38947.6572 | 50 | 0 | 13
38947.6593 | 3 | 0 | 13
13
38947.638 | 1 | 0 | 14
38947.6401 | 1 | 0 | 14
38947.6422 | 1 | 0 | 14
38947.6444 | 1 | 0 | 14
38947.6465 | 1 | 0 | 14
38947.6487 | 1 | 0 | 14
38947.6508 | 214 | 0 | 14
38947.6529 | 1819 | 0 | 14
38947.6551 | 1867 | 0 | 14
38947.6572 | 2174 | 0 | 14
38947.6594 | 2 | 0 | 14
14
38947.638 | 1 | 0 | 15
38947.6401 | 1 | 0 | 15
38947.6423 | 1 | 0 | 15
38947.6444 | 1 | 0 | 15
38947.6465 | 1 | 0 | 15
38947.6487 | 1 | 0 | 15
38947.6508 | 3 | 0 | 15
38947.653 | 7 | 0 | 15
38947.6551 | 18 | 0 | 15
38947.6572 | 40 | 0 | 15
38947.6594 | 2 | 0 | 15
15
38947.638 | 1 | 0 | 16
38947.6401 | 1 | 0 | 16
38947.6423 | 1 | 0 | 16
38947.6444 | 1 | 0 | 16
38947.6466 | 1 | 0 | 16
38947.6487 | 1 | 0 | 16
38947.6508 | 2121 | 0 | 16
38947.653 | 2547 | 0 | 16
38947.6551 | 2027 | 0 | 16
38947.6572 | 2402 | 0 | 16
38947.6594 | 2204 | 0 | 16
16
38947.638 | 1 | 0 | 17
38947.6402 | 1 | 0 | 17
38947.6423 | 1 | 0 | 17
38947.6444 | 1 | 0 | 17
38947.6466 | 1 | 0 | 17
38947.6487 | 1 | 0 | 17
38947.6508 | 4 | 0 | 17
38947.653 | 6 | 0 | 17
38947.6551 | 20 | 0 | 17
38947.6573 | 51 | 0 | 17
38947.6594 | 3 | 0 | 17
17
38947.638 | 1 | 0 | 18
38947.6402 | 1 | 0 | 18
38947.6423 | 1 | 0 | 18
38947.6444 | 1 | 0 | 18
38947.6466 | 1 | 0 | 18
38947.6487 | 1 | 0 | 18
38947.6509 | 89 | 0 | 18
38947.653 | 1997 | 0 | 18
38947.6551 | 1996 | 0 | 18
38947.6573 | 2343 | 0 | 18
38947.6594 | 2266 | 0 | 18
18
38947.638 | 1 | 0 | 19
38947.6402 | 2 | 0 | 19
38947.6423 | 1 | 0 | 19
38947.6445 | 1 | 0 | 19
38947.6466 | 1 | 0 | 19
38947.6487 | 1 | 0 | 19
38947.6509 | 3 | 0 | 19
38947.653 | 8 | 0 | 19
38947.6552 | 19 | 0 | 19
38947.6573 | 57 | 0 | 19
38947.6594 | 3 | 0 | 19
19
38947.6381 | 1 | 0 | 20
38947.6402 | 1 | 0 | 20
38947.6423 | 1 | 0 | 20
38947.6445 | 1 | 0 | 20
38947.6466 | 1 | 0 | 20
38947.6488 | 1120 | 0 | 20
38947.6509 | 2347 | 0 | 20
38947.653 | 1918 | 0 | 20
38947.6552 | 2183 | 0 | 20
38947.6573 | 1837 | 0 | 20
38947.6594 | 1378 | 0 | 20
20
38947.6381 | 1 | 0 | 21
38947.6402 | 1 | 0 | 21
38947.6423 | 1 | 0 | 21
38947.6445 | 1 | 0 | 21
38947.6466 | 1 | 0 | 21
38947.6488 | 2 | 0 | 21
38947.6509 | 4 | 0 | 21
38947.653 | 8 | 0 | 21
38947.6552 | 21 | 0 | 21
38947.6573 | 57 | 0 | 21
38947.6595 | 2 | 0 | 21
21
38947.6381 | 1 | 0 | 22
38947.6402 | 1 | 0 | 22
38947.6424 | 1 | 0 | 22
38947.6445 | 1 | 0 | 22
38947.6466 | 1 | 0 | 22
38947.6488 | 2 | 0 | 22
38947.6509 | 2165 | 0 | 22
38947.6531 | 2306 | 0 | 22
38947.6552 | 1920 | 0 | 22
38947.6573 | 1907 | 0 | 22
38947.6595 | 1481 | 0 | 22
22
38947.6381 | 1 | 0 | 23
38947.6402 | 1 | 0 | 23
38947.6424 | 1 | 0 | 23
38947.6445 | 1 | 0 | 23
38947.6467 | 1 | 0 | 23
38947.6488 | 1 | 0 | 23
38947.6509 | 78 | 65 | 23
38947.6531 | 13 | 0 | 23
38947.6552 | 131 | 3 | 23
38947.6574 | 104 | 0 | 23
38947.6595 | 3 | 0 | 23
23
38947.6381 | 1 | 0 | 24
38947.6403 | 1 | 0 | 24
38947.6424 | 1 | 0 | 24
38947.6445 | 1 | 0 | 24
38947.6467 | 1 | 0 | 24
38947.6488 | 1 | 0 | 24
38947.651 | 29 | 25 | 24
38947.6531 | 3 | 0 | 24
38947.6552 | 14 | 7 | 24
38947.6574 | 6 | 3 | 24
38947.6595 | 40 | 0 | 24
24
38947.6381 | 1 | 0 | 25
38947.6403 | 1 | 0 | 25
38947.6424 | 1 | 0 | 25
38947.6446 | 1 | 0 | 25
38947.6467 | 1 | 0 | 25
38947.6488 | 1 | 0 | 25
38947.651 | 3 | 0 | 25
38947.6531 | 13 | 0 | 25
38947.6553 | 31 | 0 | 25
38947.6574 | 67 | 0 | 25
38947.6595 | 3 | 0 | 25
25
38947.6382 | 1 | 0 | 26
38947.6403 | 1 | 0 | 26
38947.6424 | 1 | 0 | 26
38947.6446 | 1 | 0 | 26
38947.6467 | 1 | 0 | 26
38947.6489 | 1 | 0 | 26
38947.651 | 39 | 26 | 26
38947.6531 | 71 | 0 | 26
38947.6553 | 174 | 24 | 26
38947.6574 | 125 | 1 | 26
38947.6595 | 2 | 0 | 26
26
38947.6382 | 1 | 0 | 27
38947.6403 | 1 | 0 | 27
38947.6425 | 1 | 1 | 27
38947.6446 | 1 | 0 | 27
38947.6467 | 1 | 0 | 27
38947.6489 | 1 | 0 | 27
38947.651 | 3 | 0 | 27
38947.6531 | 93 | 0 | 27
38947.6553 | 25 | 0 | 27
38947.6574 | 75 | 0 | 27
38947.6596 | 3 | 0 | 27
27
38947.6382 | 1 | 0 | 28
38947.6403 | 1 | 0 | 28
38947.6425 | 1 | 0 | 28
38947.6446 | 1 | 0 | 28
38947.6467 | 1 | 0 | 28
38947.6489 | 1 | 0 | 28
38947.651 | 3 | 0 | 28
38947.6532 | 3 | 0 | 28
38947.6553 | 3 | 0 | 28
38947.6574 | 14 | 0 | 28
38947.6596 | 211 | 0 | 28
28
38947.6382 | 1 | 0 | 29
38947.6403 | 1 | 0 | 29
38947.6425 | 1 | 0 | 29
38947.6446 | 1 | 0 | 29
38947.6468 | 1 | 0 | 29
38947.6489 | 1 | 0 | 29
38947.651 | 2 | 0 | 29
38947.6532 | 76 | 0 | 29
38947.6553 | 30 | 0 | 29
38947.6575 | 98 | 0 | 29
38947.6596 | 3 | 0 | 29
29
38947.6382 | 1 | 0 | 30
38947.6404 | 1 | 0 | 30
38947.6425 | 1 | 0 | 30
38947.6446 | 1 | 0 | 30
38947.6468 | 1 | 0 | 30
38947.6489 | 1 | 0 | 30
38947.6511 | 2 | 0 | 30
38947.6532 | 3 | 0 | 30
38947.6553 | 4 | 0 | 30
38947.6575 | 20 | 0 | 30
38947.6596 | 217 | 0 | 30
30
38947.6382 | 1 | 0 | 31
38947.6404 | 1 | 0 | 31
38947.6425 | 1 | 0 | 31
38947.6447 | 1 | 0 | 31
38947.6468 | 1 | 0 | 31
38947.6489 | 1 | 0 | 31
38947.6511 | 2 | 0 | 31
38947.6532 | 41 | 0 | 31
38947.6553 | 12 | 0 | 31
38947.6575 | 77 | 0 | 31
38947.6596 | 2 | 0 | 31
31
38947.6383 | 1 | 0 | 32
38947.6404 | 1 | 0 | 32
38947.6425 | 1 | 0 | 32
38947.6447 | 1 | 0 | 32
38947.6468 | 1 | 0 | 32
38947.6489 | 2 | 0 | 32
38947.6511 | 683 | 0 | 32
38947.6532 | 1694 | 0 | 32
38947.6554 | 1676 | 0 | 32
38947.6575 | 2202 | 0 | 32
38947.6596 | 1891 | 0 | 32
32
38947.6383 | 1 | 0 | 33
38947.6404 | 1 | 0 | 33
38947.6425 | 1 | 0 | 33
38947.6447 | 1 | 0 | 33
38947.6468 | 1 | 0 | 33
38947.649 | 1 | 0 | 33
38947.6511 | 3 | 0 | 33
38947.6532 | 7 | 0 | 33
38947.6554 | 13 | 0 | 33
38947.6575 | 71 | 0 | 33
38947.6597 | 2 | 0 | 33
33
38947.6383 | 1 | 0 | 34
38947.6404 | 1 | 0 | 34
38947.6426 | 2 | 0 | 34
38947.6447 | 1 | 0 | 34
38947.6468 | 1 | 0 | 34
38947.649 | 1 | 0 | 34
38947.6511 | 1029 | 0 | 34
38947.6533 | 2141 | 0 | 34
38947.6554 | 1649 | 0 | 34
38947.6575 | 1461 | 0 | 34
38947.6597 | 2 | 0 | 34
34
38947.6383 | 1 | 0 | 35
38947.6404 | 1 | 0 | 35
38947.6426 | 1 | 0 | 35
38947.6447 | 1 | 0 | 35
38947.6469 | 1 | 0 | 35
38947.649 | 1 | 0 | 35
38947.6511 | 3 | 0 | 35
38947.6533 | 7 | 0 | 35
38947.6554 | 16 | 0 | 35
38947.6575 | 83 | 0 | 35
38947.6597 | 2 | 0 | 35
35
38947.6383 | 1 | 0 | 36
38947.6405 | 1 | 0 | 36
38947.6426 | 1 | 0 | 36
38947.6447 | 1 | 0 | 36
38947.6469 | 1 | 0 | 36
38947.649 | 1 | 0 | 36
38947.6512 | 2153 | 0 | 36
38947.6533 | 2562 | 0 | 36
38947.6554 | 2516 | 0 | 36
38947.6576 | 1991 | 0 | 36
38947.6597 | 2291 | 0 | 36
36
38947.6383 | 1 | 0 | 37
38947.6405 | 1 | 0 | 37
38947.6426 | 1 | 0 | 37
38947.6448 | 1 | 0 | 37
38947.6469 | 1 | 0 | 37
38947.649 | 1 | 0 | 37
38947.6512 | 3 | 0 | 37
38947.6533 | 7 | 0 | 37
38947.6554 | 18 | 0 | 37
38947.6576 | 72 | 0 | 37
38947.6597 | 3 | 0 | 37
37
38947.6384 | 1 | 0 | 38
38947.6405 | 1 | 0 | 38
38947.6426 | 1 | 0 | 38
38947.6448 | 1 | 0 | 38
38947.6469 | 2 | 0 | 38
38947.6491 | 1 | 0 | 38
38947.6512 | 1609 | 0 | 38
38947.6533 | 2081 | 0 | 38
38947.6555 | 2097 | 0 | 38
38947.6576 | 2207 | 0 | 38
38947.6597 | 2321 | 0 | 38
38
38947.6384 | 1 | 0 | 39
38947.6405 | 1 | 0 | 39
38947.6427 | 1 | 0 | 39
38947.6448 | 1 | 0 | 39
38947.6469 | 1 | 0 | 39
38947.6491 | 1 | 0 | 39
38947.6512 | 3 | 0 | 39
38947.6533 | 7 | 0 | 39
38947.6555 | 15 | 0 | 39
38947.6576 | 90 | 0 | 39
38947.6598 | 3 | 0 | 39
39
38947.6384 | 1 | 0 | 40
38947.6405 | 1 | 0 | 40
38947.6427 | 1 | 0 | 40
38947.6448 | 1 | 1 | 40
38947.6469 | 1 | 0 | 40
38947.6491 | 1 | 0 | 40
38947.6512 | 1945 | 0 | 40
38947.6534 | 2152 | 0 | 40
38947.6555 | 1995 | 0 | 40
38947.6576 | 1559 | 0 | 40
38947.6598 | 1281 | 0 | 40
40
38947.6384 | 1 | 0 | 41
38947.6405 | 1 | 0 | 41
38947.6427 | 1 | 0 | 41
38947.6448 | 1 | 0 | 41
38947.647 | 1 | 0 | 41
38947.6491 | 1 | 0 | 41
38947.6512 | 4 | 0 | 41
38947.6534 | 19 | 0 | 41
38947.6555 | 15 | 0 | 41
38947.6577 | 82 | 0 | 41
38947.6598 | 2 | 0 | 41
41
38947.6384 | 1 | 0 | 42
38947.6406 | 1 | 0 | 42
38947.6427 | 1 | 0 | 42
38947.6448 | 1 | 0 | 42
38947.647 | 1 | 0 | 42
38947.6491 | 5 | 0 | 42
38947.6513 | 2003 | 0 | 42
38947.6534 | 2074 | 0 | 42
38947.6555 | 2089 | 0 | 42
38947.6577 | 1985 | 0 | 42
38947.6598 | 1404 | 0 | 42
42
38947.6384 | 1 | 0 | 43
38947.6406 | 1 | 0 | 43
38947.6427 | 1 | 0 | 43
38947.6448 | 1 | 0 | 43
38947.647 | 1 | 0 | 43
38947.6491 | 1 | 0 | 43
38947.6513 | 4 | 0 | 43
38947.6534 | 3 | 0 | 43
38947.6555 | 4 | 0 | 43
38947.6577 | 3 | 0 | 43
38947.6598 | 1034 | 950 | 43
43
38947.6384 | 1 | 0 | 44
38947.6427 | 1 | 0 | 44
38947.6449 | 1 | 0 | 44
38947.647 | 1 | 0 | 44
38947.6491 | 1 | 0 | 44
38947.6513 | 3 | 0 | 44
38947.6534 | 3 | 0 | 44
38947.6556 | 3 | 0 | 44
38947.6577 | 973 | 0 | 44
38947.6598 | 1102 | 1092 | 44
44
38947.6385 | 1 | 0 | 45
38947.6406 | 1 | 0 | 45
38947.6427 | 1 | 0 | 45
38947.6449 | 1 | 0 | 45
38947.647 | 1 | 0 | 45
38947.6492 | 2 | 0 | 45
38947.6513 | 3 | 0 | 45
38947.6534 | 3 | 0 | 45
38947.6556 | 5 | 0 | 45
38947.6577 | 3 | 0 | 45
38947.6598 | 17 | 6 | 45
45
38947.6385 | 1 | 0 | 46
38947.6406 | 1 | 0 | 46
38947.6428 | 1 | 0 | 46
38947.6449 | 2 | 0 | 46
38947.647 | 1 | 0 | 46
38947.6492 | 1 | 0 | 46
38947.6513 | 2 | 0 | 46
38947.6534 | 3 | 0 | 46
38947.6556 | 4 | 0 | 46
38947.6577 | 6 | 0 | 46
38947.6599 | 227 | 3 | 46
46
38947.6385 | 1 | 0 | 47
38947.6406 | 1 | 0 | 47
38947.6428 | 1 | 0 | 47
38947.6449 | 1 | 0 | 47
38947.647 | 1 | 0 | 47
38947.6492 | 1 | 0 | 47
38947.6513 | 3 | 0 | 47
38947.6535 | 3 | 0 | 47
38947.6556 | 3 | 0 | 47
38947.6577 | 3 | 0 | 47
38947.6599 | 13 | 2 | 47
47
38947.6385 | 1 | 0 | 48
38947.6407 | 1 | 0 | 48
38947.6428 | 1 | 0 | 48
38947.6449 | 1 | 0 | 48
38947.6471 | 1 | 0 | 48
38947.6492 | 1 | 0 | 48
38947.6513 | 3 | 0 | 48
38947.6535 | 3 | 0 | 48
38947.6556 | 2 | 0 | 48
38947.6578 | 5 | 0 | 48
38947.6599 | 294 | 1 | 48
48
38947.6385 | 1 | 0 | 49
38947.6407 | 1 | 0 | 49
38947.6428 | 1 | 0 | 49
38947.6449 | 2 | 0 | 49
38947.6471 | 1 | 0 | 49
38947.6492 | 1 | 0 | 49
38947.6514 | 3 | 0 | 49
38947.6535 | 3 | 0 | 49
38947.6556 | 2 | 0 | 49
38947.6578 | 22 | 0 | 49
38947.6599 | 14 | 1 | 49
49
38947.6386 | 1 | 0 | 50
38947.6407 | 1 | 0 | 50
38947.6428 | 1 | 0 | 50
38947.645 | 1 | 0 | 50
38947.6471 | 1 | 0 | 50
38947.6492 | 1 | 0 | 50
38947.6514 | 1312 | 0 | 50
38947.6535 | 1689 | 0 | 50
38947.6557 | 2294 | 0 | 50
38947.6578 | 2170 | 0 | 50
38947.6599 | 2222 | 0 | 50
50
38947.6386 | 1 | 0 | 51
38947.6407 | 1 | 0 | 51
38947.6428 | 1 | 0 | 51
38947.645 | 1 | 0 | 51
38947.6471 | 1 | 0 | 51
38947.6493 | 1 | 0 | 51
38947.6514 | 2 | 0 | 51
38947.6535 | 3 | 0 | 51
38947.6557 | 3 | 0 | 51
38947.6578 | 5 | 0 | 51
38947.66 | 8 | 0 | 51
51
38947.6386 | 1 | 0 | 52
38947.6407 | 1 | 0 | 52
38947.6429 | 1 | 0 | 52
38947.645 | 1 | 0 | 52
38947.6471 | 1 | 0 | 52
38947.6493 | 1 | 0 | 52
38947.6514 | 1393 | 0 | 52
38947.6536 | 2113 | 0 | 52
38947.6557 | 1991 | 0 | 52
38947.6578 | 935 | 0 | 52
38947.66 | 2 | 0 | 52
52
38947.6386 | 1 | 0 | 53
38947.6407 | 1 | 1 | 53
38947.6429 | 1 | 0 | 53
38947.645 | 1 | 0 | 53
38947.6472 | 1 | 0 | 53
38947.6493 | 1 | 0 | 53
38947.6514 | 3 | 0 | 53
38947.6536 | 3 | 0 | 53
38947.6557 | 5 | 0 | 53
38947.6578 | 3 | 0 | 53
38947.66 | 15 | 1 | 53
53
38947.6386 | 1 | 0 | 54
38947.6408 | 1 | 0 | 54
38947.6429 | 1 | 1 | 54
38947.645 | 1 | 0 | 54
38947.6472 | 1 | 0 | 54
38947.6493 | 1 | 0 | 54
38947.6514 | 2156 | 0 | 54
38947.6536 | 2360 | 0 | 54
38947.6557 | 2093 | 0 | 54
38947.6579 | 2312 | 0 | 54
38947.66 | 2345 | 0 | 54
54
38947.6386 | 1 | 0 | 55
38947.6408 | 1 | 0 | 55
38947.6429 | 1 | 0 | 55
38947.645 | 1 | 0 | 55
38947.6472 | 1 | 0 | 55
38947.6493 | 1 | 0 | 55
38947.6515 | 3 | 0 | 55
38947.6536 | 3 | 0 | 55
38947.6557 | 3 | 0 | 55
38947.6579 | 10 | 0 | 55
38947.66 | 3 | 0 | 55
55
38947.6386 | 1 | 0 | 56
38947.6408 | 1 | 0 | 56
38947.6429 | 1 | 0 | 56
38947.6451 | 1 | 0 | 56
38947.6472 | 1 | 0 | 56
38947.6493 | 1 | 0 | 56
38947.6515 | 1444 | 1 | 56
38947.6536 | 2504 | 0 | 56
38947.6558 | 2319 | 0 | 56
38947.6579 | 2112 | 0 | 56
38947.66 | 2000 | 0 | 56
56
38947.6387 | 1 | 0 | 57
38947.6408 | 1 | 0 | 57
38947.6429 | 1 | 0 | 57
38947.6451 | 1 | 0 | 57
38947.6472 | 1 | 0 | 57
38947.6494 | 1 | 0 | 57
38947.6515 | 3 | 0 | 57
38947.6536 | 4 | 0 | 57
38947.6558 | 7 | 0 | 57
38947.6579 | 3 | 0 | 57
38947.66 | 5 | 0 | 57
57
38947.6387 | 1 | 0 | 58
38947.6408 | 1 | 0 | 58
38947.643 | 1 | 0 | 58
38947.6451 | 1 | 0 | 58
38947.6472 | 1 | 0 | 58
38947.6494 | 2221 | 0 | 58
38947.6515 | 1980 | 1 | 58
38947.6536 | 1792 | 0 | 58
38947.6558 | 1958 | 0 | 58
38947.6579 | 1958 | 0 | 58
38947.6601 | 1230 | 0 | 58
58
38947.6387 | 1 | 0 | 59
38947.6408 | 1 | 0 | 59
38947.643 | 1 | 0 | 59
38947.6451 | 1 | 0 | 59
38947.6472 | 1 | 0 | 59
38947.6494 | 2 | 0 | 59
38947.6515 | 3 | 0 | 59
38947.6537 | 4 | 0 | 59
38947.6558 | 8 | 0 | 59
38947.6579 | 12 | 0 | 59
38947.6601 | 4 | 0 | 59
59
38947.6387 | 1 | 0 | 60
38947.6408 | 1 | 0 | 60
38947.643 | 1 | 0 | 60
38947.6451 | 1 | 1 | 60
38947.6473 | 1 | 0 | 60
38947.6494 | 1932 | 0 | 60
38947.6515 | 2024 | 0 | 60
38947.6537 | 1947 | 0 | 60
38947.6558 | 1935 | 0 | 60
38947.658 | 2028 | 0 | 60
38947.6601 | 1540 | 0 | 60
60
38947.6387 | 1 | 0 | 61
38947.6409 | 1 | 0 | 61
38947.643 | 1 | 0 | 61
38947.6451 | 1 | 0 | 61
38947.6473 | 1 | 0 | 61
38947.6494 | 2 | 0 | 61
38947.6516 | 3 | 0 | 61
38947.6537 | 2 | 0 | 61
38947.6558 | 3 | 0 | 61
38947.658 | 1371 | 0 | 61
38947.6601 | 4 | 0 | 61
61
38947.6387 | 1 | 0 | 62
38947.6409 | 1 | 0 | 62
38947.643 | 1 | 1 | 62
38947.6452 | 1 | 0 | 62
38947.6473 | 1 | 0 | 62
38947.6494 | 2 | 0 | 62
38947.6516 | 3 | 0 | 62
38947.6537 | 3 | 0 | 62
38947.6558 | 142 | 0 | 62
38947.658 | 5 | 0 | 62
38947.6601 | 336 | 0 | 62
62
38947.6388 | 1 | 0 | 63
38947.6409 | 1 | 0 | 63
38947.643 | 1 | 0 | 63
38947.6452 | 1 | 0 | 63
38947.6473 | 1 | 0 | 63
38947.6495 | 2 | 0 | 63
38947.6516 | 3 | 0 | 63
38947.6537 | 3 | 0 | 63
38947.658 | 877 | 0 | 63
38947.6601 | 4 | 0 | 63
63
38947.6388 | 1 | 0 | 64
38947.6409 | 1 | 0 | 64
38947.6431 | 1 | 0 | 64
38947.6452 | 1 | 0 | 64
38947.6473 | 1 | 0 | 64
38947.6495 | 2 | 0 | 64
38947.6516 | 2 | 0 | 64
38947.6537 | 3 | 0 | 64
38947.6559 | 3 | 0 | 64
38947.658 | 5 | 0 | 64
38947.6602 | 357 | 0 | 64
64
38947.6388 | 1 | 0 | 65
38947.6409 | 1 | 0 | 65
38947.6431 | 1 | 0 | 65
38947.6452 | 1 | 0 | 65
38947.6473 | 1 | 0 | 65
38947.6495 | 1 | 0 | 65
38947.6516 | 2 | 0 | 65
38947.6538 | 3 | 0 | 65
38947.6559 | 3 | 0 | 65
38947.658 | 1165 | 95 | 65
38947.6602 | 51 | 0 | 65
65
38947.6388 | 1 | 0 | 66
38947.6409 | 1 | 0 | 66
38947.6431 | 1 | 0 | 66
38947.6452 | 1 | 0 | 66
38947.6474 | 1 | 0 | 66
38947.6495 | 1 | 0 | 66
38947.6516 | 1879 | 0 | 66
38947.6538 | 2172 | 0 | 66
38947.6559 | 1862 | 0 | 66
38947.6581 | 1682 | 0 | 66
38947.6602 | 2077 | 0 | 66
66
38947.6388 | 1 | 0 | 67
38947.641 | 1 | 0 | 67
38947.6431 | 1 | 0 | 67
38947.6452 | 1 | 0 | 67
38947.6474 | 1 | 0 | 67
38947.6495 | 2 | 0 | 67
38947.6517 | 3 | 0 | 67
38947.6538 | 3 | 0 | 67
38947.6559 | 3 | 0 | 67
38947.6581 | 359 | 0 | 67
38947.6602 | 4 | 0 | 67
67
38947.6388 | 1 | 0 | 68
38947.641 | 1 | 0 | 68
38947.6431 | 1 | 0 | 68
38947.6453 | 1 | 0 | 68
38947.6474 | 1 | 0 | 68
38947.6495 | 2 | 0 | 68
38947.6517 | 1832 | 0 | 68
38947.6538 | 1684 | 0 | 68
38947.6559 | 1804 | 0 | 68
38947.6581 | 380 | 0 | 68
38947.6602 | 3 | 0 | 68
68
38947.6389 | 1 | 0 | 69
38947.641 | 1 | 0 | 69
38947.6431 | 1 | 0 | 69
38947.6453 | 1 | 0 | 69
38947.6474 | 1 | 0 | 69
38947.6495 | 1 | 0 | 69
38947.6517 | 3 | 0 | 69
38947.6538 | 3 | 0 | 69
38947.656 | 3 | 0 | 69
38947.6581 | 722 | 0 | 69
38947.6602 | 3 | 0 | 69
69
38947.6389 | 1 | 0 | 70
38947.641 | 1 | 0 | 70
38947.6431 | 1 | 0 | 70
38947.6453 | 1 | 0 | 70
38947.6474 | 1 | 0 | 70
38947.6496 | 1 | 0 | 70
38947.6517 | 2507 | 0 | 70
38947.6538 | 2250 | 0 | 70
38947.656 | 2500 | 0 | 70
38947.6581 | 2469 | 0 | 70
38947.6603 | 2068 | 0 | 70
70
38947.6389 | 0 | 0 | 71
38947.641 | 1 | 0 | 71
38947.6432 | 1 | 0 | 71
38947.6453 | 1 | 0 | 71
38947.6474 | 1 | 0 | 71
38947.6496 | 1 | 0 | 71
38947.6517 | 3 | 0 | 71
38947.6539 | 3 | 0 | 71
38947.656 | 3 | 0 | 71
38947.6581 | 682 | 0 | 71
38947.6603 | 4 | 0 | 71
71
38947.6389 | 1 | 0 | 72
38947.641 | 1 | 0 | 72
38947.6432 | 1 | 0 | 72
38947.6453 | 1 | 0 | 72
38947.6475 | 1 | 0 | 72
38947.6496 | 2036 | 0 | 72
38947.6517 | 2580 | 0 | 72
38947.6539 | 2269 | 0 | 72
38947.656 | 2185 | 0 | 72
38947.6581 | 2431 | 0 | 72
38947.6603 | 2029 | 0 | 72
72
38947.6389 | 1 | 0 | 73
38947.6411 | 1 | 0 | 73
38947.6432 | 1 | 0 | 73
38947.6453 | 1 | 0 | 73
38947.6475 | 1 | 0 | 73
38947.6496 | 2 | 0 | 73
38947.6517 | 3 | 0 | 73
38947.6539 | 3 | 0 | 73
38947.656 | 3 | 0 | 73
38947.6582 | 489 | 0 | 73
38947.6603 | 4 | 0 | 73
73
38947.6389 | 1 | 0 | 74
38947.6411 | 1 | 0 | 74
38947.6432 | 1 | 0 | 74
38947.6453 | 1 | 0 | 74
38947.6475 | 1 | 0 | 74
38947.6496 | 2075 | 0 | 74
38947.6518 | 2105 | 0 | 74
38947.6539 | 1787 | 0 | 74
38947.656 | 1819 | 0 | 74
38947.6582 | 1267 | 0 | 74
38947.6603 | 1471 | 0 | 74
74
38947.6389 | 1 | 0 | 75
38947.6411 | 2 | 0 | 75
38947.6432 | 1 | 0 | 75
38947.6454 | 1 | 0 | 75
38947.6475 | 1 | 0 | 75
38947.6496 | 3 | 0 | 75
38947.6518 | 4 | 0 | 75
38947.6539 | 3 | 0 | 75
38947.6561 | 3 | 0 | 75
38947.6582 | 606 | 0 | 75
38947.6603 | 4 | 0 | 75
75
38947.639 | 1 | 0 | 76
38947.6411 | 1 | 1 | 76
38947.6432 | 1 | 0 | 76
38947.6454 | 1 | 0 | 76
38947.6475 | 1 | 0 | 76
38947.6497 | 2356 | 0 | 76
38947.6518 | 2170 | 0 | 76
38947.6539 | 1639 | 0 | 76
38947.6561 | 1771 | 0 | 76
38947.6582 | 1644 | 0 | 76
38947.6604 | 1600 | 0 | 76
76
38947.639 | 1 | 0 | 77
38947.6411 | 1 | 0 | 77
38947.6433 | 1 | 0 | 77
38947.6454 | 1 | 0 | 77
38947.6475 | 1 | 0 | 77
38947.6497 | 3 | 0 | 77
38947.6518 | 4 | 0 | 77
38947.654 | 3 | 0 | 77
38947.6561 | 1127 | 933 | 77
38947.6582 | 1048 | 971 | 77
38947.6604 | 1075 | 857 | 77
77
38947.639 | 1 | 0 | 78
38947.6411 | 1 | 0 | 78
38947.6433 | 1 | 1 | 78
38947.6454 | 1 | 0 | 78
38947.6476 | 1 | 0 | 78
38947.6497 | 3 | 0 | 78
38947.6518 | 3 | 0 | 78
38947.654 | 936 | 892 | 78
38947.6561 | 1207 | 1021 | 78
38947.6583 | 872 | 806 | 78
38947.6604 | 1204 | 876 | 78
78
38947.639 | 1 | 0 | 79
38947.6412 | 1 | 0 | 79
38947.6433 | 1 | 0 | 79
38947.6454 | 1 | 0 | 79
38947.6476 | 1 | 0 | 79
38947.6497 | 2 | 0 | 79
38947.6519 | 8 | 0 | 79
38947.654 | 3 | 2 | 79
38947.6561 | 117 | 4 | 79
38947.6583 | 4 | 5 | 79
38947.6604 | 1162 | 4 | 79
79
38947.639 | 1 | 0 | 80
38947.6412 | 1 | 0 | 80
38947.6433 | 1 | 0 | 80
38947.6455 | 1 | 0 | 80
38947.6476 | 1 | 0 | 80
38947.6497 | 2 | 0 | 80
38947.6519 | 1669 | 0 | 80
38947.654 | 1719 | 0 | 80
38947.6561 | 2115 | 2 | 80
38947.6583 | 2062 | 3 | 80
38947.6604 | 1367 | 2 | 80
80
38947.6391 | 1 | 0 | 81
38947.6412 | 1 | 0 | 81
38947.6433 | 1 | 0 | 81
38947.6455 | 1 | 0 | 81
38947.6476 | 1 | 0 | 81
38947.6497 | 2 | 0 | 81
38947.6519 | 4 | 0 | 81
38947.654 | 3 | 0 | 81
38947.6562 | 4 | 2 | 81
38947.6583 | 3 | 2 | 81
38947.6604 | 1466 | 1 | 81
81
38947.6391 | 1 | 0 | 82
38947.6412 | 1 | 0 | 82
38947.6433 | 1 | 0 | 82
38947.6455 | 1 | 0 | 82
38947.6476 | 1 | 0 | 82
38947.6498 | 1 | 0 | 82
38947.6519 | 1900 | 0 | 82
38947.654 | 1894 | 0 | 82
38947.6562 | 1947 | 1 | 82
38947.6583 | 334 | 1 | 82
38947.6605 | 3 | 1 | 82
82
38947.6391 | 1 | 0 | 83
38947.6412 | 1 | 0 | 83
38947.6434 | 1 | 0 | 83
38947.6455 | 1 | 0 | 83
38947.6476 | 1 | 0 | 83
38947.6498 | 2 | 0 | 83
38947.6519 | 4 | 0 | 83
38947.6541 | 3 | 0 | 83
38947.6562 | 3 | 0 | 83
38947.6583 | 4 | 1 | 83
38947.6605 | 1774 | 0 | 83
83
38947.6391 | 1 | 0 | 84
38947.6412 | 1 | 0 | 84
38947.6434 | 1 | 0 | 84
38947.6455 | 1 | 0 | 84
38947.6477 | 1 | 0 | 84
38947.6498 | 2 | 0 | 84
38947.6519 | 2449 | 0 | 84
38947.6541 | 2197 | 0 | 84
38947.6562 | 2002 | 0 | 84
38947.6583 | 2469 | 0 | 84
38947.6605 | 2241 | 1 | 84
84
38947.6391 | 1 | 0 | 85
38947.6413 | 1 | 1 | 85
38947.6434 | 1 | 0 | 85
38947.6455 | 1 | 0 | 85
38947.6477 | 1 | 0 | 85
38947.6498 | 2 | 0 | 85
38947.6519 | 4 | 0 | 85
38947.6541 | 4 | 0 | 85
38947.6562 | 3 | 0 | 85
38947.6584 | 4 | 0 | 85
38947.6605 | 1746 | 0 | 85
85
38947.6391 | 1 | 0 | 86
38947.6413 | 1 | 0 | 86
38947.6434 | 1 | 0 | 86
38947.6455 | 1 | 0 | 86
38947.6477 | 1 | 0 | 86
38947.6498 | 1797 | 0 | 86
38947.652 | 2042 | 0 | 86
38947.6541 | 2578 | 0 | 86
38947.6562 | 2410 | 0 | 86
38947.6584 | 2522 | 0 | 86
38947.6605 | 2337 | 0 | 86
86
38947.6391 | 1 | 0 | 87
38947.6413 | 1 | 0 | 87
38947.6434 | 1 | 0 | 87
38947.6456 | 1 | 0 | 87
38947.6477 | 1 | 0 | 87
38947.6498 | 2 | 0 | 87
38947.652 | 3 | 0 | 87
38947.6541 | 5 | 0 | 87
38947.6562 | 4 | 0 | 87
38947.6584 | 5 | 0 | 87
38947.6605 | 1924 | 0 | 87
87
38947.6392 | 1 | 0 | 88
38947.6413 | 1 | 0 | 88
38947.6434 | 1 | 0 | 88
38947.6456 | 1 | 0 | 88
38947.6477 | 1 | 0 | 88
38947.6499 | 1946 | 0 | 88
38947.652 | 2107 | 0 | 88
38947.6541 | 1797 | 0 | 88
38947.6563 | 1715 | 0 | 88
38947.6584 | 1335 | 0 | 88
38947.6605 | 1613 | 0 | 88
88
38947.6392 | 1 | 0 | 89
38947.6413 | 1 | 0 | 89
38947.6435 | 1 | 0 | 89
38947.6456 | 1 | 0 | 89
38947.6477 | 1 | 0 | 89
38947.6499 | 4 | 0 | 89
38947.652 | 9 | 0 | 89
38947.6542 | 10 | 0 | 89
38947.6563 | 3 | 0 | 89
38947.6584 | 20 | 0 | 89
38947.6606 | 1873 | 0 | 89
89
38947.6392 | 1 | 0 | 90
38947.6413 | 1 | 0 | 90
38947.6435 | 1 | 0 | 90
38947.6456 | 1 | 0 | 90
38947.6478 | 1 | 0 | 90
38947.6499 | 2341 | 0 | 90
38947.652 | 2070 | 0 | 90
38947.6542 | 1985 | 0 | 90
38947.6563 | 2106 | 0 | 90
38947.6584 | 1805 | 0 | 90
38947.6606 | 1821 | 0 | 90
90
38947.6392 | 1 | 0 | 91
38947.6414 | 1 | 0 | 91
38947.6435 | 1 | 0 | 91
38947.6456 | 1 | 0 | 91
38947.6478 | 1 | 0 | 91
38947.6499 | 3 | 0 | 91
38947.652 | 4 | 0 | 91
38947.6542 | 107 | 0 | 91
38947.6563 | 10 | 0 | 91
38947.6585 | 12 | 0 | 91
38947.6606 | 1730 | 0 | 91
91
38947.6392 | 1 | 0 | 92
38947.6414 | 1 | 0 | 92
38947.6435 | 1 | 0 | 92
38947.6456 | 1 | 0 | 92
38947.6478 | 1 | 0 | 92
38947.6499 | 3 | 0 | 92
38947.6521 | 2076 | 0 | 92
38947.6542 | 1724 | 0 | 92
38947.6563 | 2313 | 0 | 92
38947.6585 | 1749 | 0 | 92
38947.6606 | 1485 | 0 | 92
92
38947.6392 | 1 | 0 | 93
38947.6414 | 1 | 0 | 93
38947.6435 | 1 | 0 | 93
38947.6457 | 1 | 0 | 93
38947.6478 | 1 | 0 | 93
38947.6499 | 3 | 0 | 93
38947.6521 | 3 | 0 | 93
38947.6542 | 505 | 0 | 93
38947.6564 | 4 | 0 | 93
38947.6585 | 18 | 0 | 93
38947.6606 | 1766 | 0 | 93
93
38947.6393 | 1 | 0 | 94
38947.6414 | 1 | 0 | 94
38947.6435 | 1 | 1 | 94
38947.6457 | 1 | 0 | 94
38947.6478 | 1 | 0 | 94
38947.65 | 2 | 0 | 94
38947.6521 | 2077 | 0 | 94
38947.6542 | 1620 | 0 | 94
38947.6564 | 1948 | 0 | 94
38947.6585 | 333 | 0 | 94
38947.6606 | 3 | 0 | 94
94
38947.6393 | 1 | 0 | 95
38947.6414 | 1 | 0 | 95
38947.6436 | 1 | 0 | 95
38947.6457 | 1 | 0 | 95
38947.6478 | 1 | 0 | 95
38947.65 | 2 | 0 | 95
38947.6521 | 3 | 0 | 95
38947.6542 | 82 | 0 | 95
38947.6564 | 3 | 0 | 95
38947.6585 | 20 | 0 | 95
38947.6607 | 1638 | 0 | 95
95
38947.6393 | 1 | 0 | 96
38947.6414 | 1 | 0 | 96
38947.6436 | 1 | 0 | 96
38947.6457 | 1 | 0 | 96
38947.6478 | 1 | 0 | 96
38947.65 | 770 | 3 | 96
38947.6521 | 2238 | 0 | 96
38947.6543 | 2427 | 0 | 96
38947.6564 | 2040 | 0 | 96
38947.6585 | 2387 | 0 | 96
38947.6607 | 2012 | 0 | 96
96
38947.6393 | 1 | 0 | 97
38947.6414 | 1 | 0 | 97
38947.6436 | 1 | 0 | 97
38947.6457 | 1 | 0 | 97
38947.6479 | 1 | 0 | 97
38947.65 | 2 | 0 | 97
38947.6521 | 3 | 0 | 97
38947.6543 | 3 | 0 | 97
38947.6564 | 3 | 0 | 97
38947.6586 | 40 | 0 | 97
38947.6607 | 1553 | 0 | 97
97
38947.6393 | 1 | 0 | 98
38947.6415 | 1 | 0 | 98
38947.6436 | 1 | 0 | 98
38947.6457 | 1 | 0 | 98
38947.6479 | 1 | 0 | 98
38947.65 | 1757 | 3 | 98
38947.6522 | 2073 | 0 | 98
38947.6543 | 1995 | 0 | 98
38947.6564 | 2165 | 0 | 98
38947.6586 | 2078 | 0 | 98
38947.6607 | 2138 | 0 | 98
98
38947.6393 | 1 | 0 | 99
38947.6415 | 1 | 0 | 99
38947.6436 | 1 | 0 | 99
38947.6458 | 1 | 0 | 99
38947.6479 | 1 | 0 | 99
38947.65 | 3 | 0 | 99
38947.6522 | 3 | 0 | 99
38947.6543 | 3 | 0 | 99
38947.6564 | 3 | 0 | 99
38947.6586 | 57 | 0 | 99
38947.6607 | 1828 | 0 | 99
99
38947.6394 | 1 | 0 | 100
38947.6415 | 1 | 0 | 100
38947.6436 | 1 | 0 | 100
38947.6458 | 1 | 0 | 100
38947.6479 | 1 | 0 | 100
38947.65 | 2458 | 0 | 100
38947.6522 | 2307 | 0 | 100
38947.6543 | 1752 | 0 | 100
38947.6565 | 2211 | 0 | 100
38947.6586 | 2006 | 0 | 100
38947.6607 | 1414 | 0 | 100
100
38947.6394 | 1 | 0 | 101
38947.6415 | 1 | 1 | 101
38947.6436 | 1 | 0 | 101
38947.6458 | 1 | 0 | 101
38947.6479 | 1 | 0 | 101
38947.6501 | 4 | 0 | 101
38947.6522 | 4 | 0 | 101
38947.6543 | 29 | 0 | 101
38947.6565 | 3 | 0 | 101
38947.6586 | 96 | 0 | 101
38947.6608 | 2026 | 0 | 101
101
38947.6394 | 1 | 0 | 102
38947.6415 | 1 | 0 | 102
38947.6437 | 1 | 0 | 102
38947.6458 | 1 | 0 | 102
38947.6479 | 1 | 0 | 102
38947.6501 | 2279 | 0 | 102
38947.6522 | 2004 | 0 | 102
38947.6544 | 1917 | 0 | 102
38947.6565 | 2280 | 0 | 102
38947.6586 | 1698 | 0 | 102
38947.6608 | 1546 | 0 | 102
102
38947.6394 | 1 | 0 | 103
38947.6415 | 1 | 0 | 103
38947.6437 | 1 | 0 | 103
38947.6458 | 1 | 0 | 103
38947.648 | 1 | 0 | 103
38947.6501 | 1059 | 991 | 103
38947.6522 | 2222 | 119 | 103
38947.6544 | 1845 | 155 | 103
38947.6565 | 2067 | 91 | 103
38947.6587 | 1778 | 0 | 103
38947.6608 | 2286 | 0 | 103
103
38947.6394 | 1 | 0 | 104
38947.6416 | 1 | 0 | 104
38947.6437 | 1 | 0 | 104
38947.6458 | 1 | 0 | 104
38947.648 | 1 | 0 | 104
38947.6501 | 1070 | 997 | 104
38947.6523 | 2062 | 116 | 104
38947.6544 | 1663 | 121 | 104
38947.6565 | 1743 | 43 | 104
38947.6587 | 3 | 0 | 104
38947.6608 | 3 | 0 | 104
104
38947.6394 | 1 | 0 | 105
38947.6416 | 1 | 0 | 105
38947.6437 | 1 | 0 | 105
38947.6459 | 1 | 0 | 105
38947.648 | 2 | 0 | 105
38947.6501 | 101 | 6 | 105
38947.6523 | 1834 | 0 | 105
38947.6544 | 2250 | 0 | 105
38947.6566 | 2276 | 0 | 105
38947.6587 | 1995 | 0 | 105
38947.6608 | 2074 | 0 | 105
105
38947.6395 | 1 | 0 | 106
38947.6416 | 1 | 0 | 106
38947.6437 | 1 | 0 | 106
38947.6459 | 1 | 0 | 106
38947.648 | 1 | 0 | 106
38947.6502 | 952 | 31 | 106
38947.6523 | 2458 | 0 | 106
38947.6544 | 2497 | 0 | 106
38947.6566 | 2410 | 0 | 106
38947.6587 | 1996 | 0 | 106
38947.6608 | 2479 | 0 | 106
106
38947.6395 | 1 | 0 | 107
38947.6416 | 1 | 0 | 107
38947.6438 | 1 | 0 | 107
38947.6459 | 1 | 0 | 107
38947.648 | 1 | 0 | 107
38947.6502 | 334 | 2 | 107
38947.6523 | 1889 | 0 | 107
38947.6544 | 2095 | 0 | 107
38947.6566 | 2184 | 0 | 107
38947.6587 | 1969 | 0 | 107
38947.6609 | 2211 | 0 | 107
107
38947.6395 | 1 | 0 | 108
38947.6416 | 1 | 0 | 108
38947.6438 | 1 | 0 | 108
38947.6459 | 1 | 0 | 108
38947.648 | 1 | 0 | 108
38947.6502 | 1402 | 7 | 108
38947.6523 | 2110 | 0 | 108
38947.6545 | 2201 | 0 | 108
38947.6566 | 2464 | 0 | 108
38947.6587 | 2222 | 0 | 108
38947.6609 | 2482 | 0 | 108
108
38947.6395 | 1 | 0 | 109
38947.6416 | 1 | 0 | 109
38947.6438 | 1 | 1 | 109
38947.6459 | 1 | 0 | 109
38947.6481 | 1 | 0 | 109
38947.6502 | 35 | 1 | 109
38947.6523 | 1976 | 0 | 109
38947.6545 | 1843 | 0 | 109
38947.6566 | 2003 | 0 | 109
38947.6588 | 2122 | 0 | 109
38947.6609 | 2314 | 0 | 109
109
38947.6395 | 1 | 0 | 110
38947.6417 | 1 | 0 | 110
38947.6438 | 1 | 0 | 110
38947.6459 | 1 | 0 | 110
38947.6481 | 1 | 0 | 110
38947.6502 | 2487 | 0 | 110
38947.6523 | 2010 | 0 | 110
38947.6545 | 2374 | 0 | 110
38947.6566 | 1652 | 0 | 110
38947.6588 | 1650 | 0 | 110
38947.6609 | 1501 | 0 | 110
110
38947.6395 | 1 | 0 | 111
38947.6417 | 1 | 0 | 111
38947.6438 | 1 | 0 | 111
38947.6459 | 1 | 0 | 111
38947.6481 | 1 | 0 | 111
38947.6502 | 4 | 0 | 111
38947.6524 | 1786 | 0 | 111
38947.6545 | 2031 | 0 | 111
38947.6566 | 1935 | 0 | 111
38947.6588 | 1907 | 0 | 111
38947.6609 | 2335 | 0 | 111
111
38947.6395 | 1 | 0 | 112
38947.6417 | 1 | 0 | 112
38947.6438 | 1 | 0 | 112
38947.646 | 1 | 0 | 112
38947.6481 | 1 | 0 | 112
38947.6502 | 2245 | 0 | 112
38947.6524 | 2315 | 0 | 112
38947.6545 | 2188 | 0 | 112
38947.6567 | 1715 | 0 | 112
38947.6588 | 2178 | 0 | 112
38947.6609 | 1749 | 0 | 112
112
38947.6396 | 1 | 0 | 113
38947.6417 | 1 | 1 | 113
38947.6438 | 1 | 0 | 113
38947.646 | 1 | 0 | 113
38947.6481 | 1 | 0 | 113
38947.6503 | 14 | 0 | 113
38947.6524 | 1844 | 0 | 113
38947.6545 | 1617 | 0 | 113
38947.6567 | 1794 | 0 | 113
38947.6588 | 3 | 0 | 113
38947.661 | 3 | 0 | 113
113
38947.6396 | 1 | 0 | 114
38947.6417 | 1 | 0 | 114
38947.6439 | 1 | 0 | 114
38947.646 | 1 | 0 | 114
38947.6481 | 1 | 0 | 114
38947.6503 | 2179 | 0 | 114
38947.6524 | 2449 | 0 | 114
38947.6545 | 2167 | 0 | 114
38947.6567 | 2184 | 0 | 114
38947.6588 | 2549 | 0 | 114
38947.661 | 2374 | 0 | 114
114
38947.6396 | 1 | 0 | 115
38947.6417 | 1 | 0 | 115
38947.6439 | 1 | 0 | 115
38947.646 | 1 | 0 | 115
38947.6482 | 1 | 0 | 115
38947.6503 | 6 | 0 | 115
38947.6524 | 2154 | 0 | 115
38947.6546 | 2102 | 0 | 115
38947.6567 | 1860 | 0 | 115
38947.6588 | 73 | 0 | 115
38947.661 | 3 | 0 | 115
115
38947.6396 | 1 | 0 | 116
38947.6418 | 1 | 0 | 116
38947.6439 | 1 | 0 | 116
38947.646 | 1 | 0 | 116
38947.6482 | 1 | 0 | 116
38947.6503 | 34 | 0 | 116
38947.6524 | 2433 | 0 | 116
38947.6546 | 2135 | 0 | 116
38947.6567 | 2536 | 0 | 116
38947.6589 | 2303 | 0 | 116
38947.661 | 2235 | 0 | 116
116
38947.6396 | 1 | 0 | 117
38947.6418 | 1 | 0 | 117
38947.6439 | 1 | 0 | 117
38947.6461 | 1 | 0 | 117
38947.6482 | 1 | 0 | 117
38947.6503 | 93 | 0 | 117
38947.6525 | 2153 | 0 | 117
38947.6546 | 1883 | 0 | 117
38947.6567 | 1602 | 0 | 117
38947.6589 | 3 | 0 | 117
38947.661 | 3 | 0 | 117
117
38947.6397 | 1 | 0 | 118
38947.6418 | 1 | 1 | 118
38947.6439 | 1 | 1 | 118
38947.6461 | 1 | 0 | 118
38947.6482 | 1 | 0 | 118
38947.6503 | 2219 | 0 | 118
38947.6525 | 2331 | 0 | 118
38947.6546 | 2464 | 0 | 118
38947.6568 | 1682 | 0 | 118
38947.6589 | 1366 | 0 | 118
38947.661 | 1213 | 0 | 118
118
38947.6397 | 1 | 0 | 119
38947.6418 | 1 | 0 | 119
38947.6439 | 1 | 0 | 119
38947.6461 | 1 | 0 | 119
38947.6482 | 1 | 0 | 119
38947.6504 | 311 | 0 | 119
38947.6525 | 1852 | 0 | 119
38947.6546 | 1943 | 0 | 119
38947.6568 | 1572 | 0 | 119
38947.6589 | 3 | 0 | 119
38947.6611 | 3 | 0 | 119
119
38947.6397 | 1 | 0 | 120
38947.6418 | 1 | 0 | 120
38947.644 | 2 | 1 | 120
38947.6461 | 1 | 1 | 120
38947.6482 | 1 | 0 | 120
38947.6504 | 2155 | 0 | 120
38947.6525 | 2305 | 0 | 120
38947.6547 | 2369 | 0 | 120
38947.6568 | 1513 | 0 | 120
38947.6589 | 1838 | 0 | 120
38947.6611 | 1405 | 0 | 120
120
38947.6397 | 1 | 0 | 121
38947.6418 | 1 | 0 | 121
38947.644 | 1 | 0 | 121
38947.6461 | 1 | 0 | 121
38947.6483 | 1 | 0 | 121
38947.6504 | 2477 | 0 | 121
38947.6525 | 2235 | 0 | 121
38947.6547 | 2031 | 0 | 121
38947.6568 | 2582 | 0 | 121
38947.6589 | 2216 | 0 | 121
38947.6611 | 2297 | 0 | 121
121
38947.6397 | 1 | 0 | 122
38947.6419 | 1 | 0 | 122
38947.644 | 1 | 0 | 122
38947.6461 | 1 | 0 | 122
38947.6483 | 1 | 0 | 122
38947.6504 | 1164 | 2 | 122
38947.6525 | 2205 | 0 | 122
38947.6547 | 2102 | 0 | 122
38947.6568 | 2559 | 0 | 122
38947.659 | 2286 | 0 | 122
38947.6611 | 2366 | 0 | 122
122
38947.6397 | 1 | 1 | 123
38947.6419 | 1 | 0 | 123
38947.644 | 1 | 0 | 123
38947.6483 | 1 | 0 | 123
38947.6504 | 2485 | 0 | 123
38947.6526 | 2339 | 0 | 123
38947.6547 | 2028 | 0 | 123
38947.6568 | 2156 | 0 | 123
38947.659 | 2176 | 0 | 123
38947.6611 | 2475 | 0 | 123
123
38947.6397 | 1 | 0 | 124
38947.6419 | 1 | 0 | 124
38947.644 | 1 | 0 | 124
38947.6462 | 1 | 0 | 124
38947.6483 | 1 | 0 | 124
38947.6504 | 1840 | 0 | 124
38947.6526 | 2101 | 0 | 124
38947.6547 | 1920 | 0 | 124
38947.6569 | 1689 | 0 | 124
38947.659 | 1362 | 0 | 124
38947.6611 | 1817 | 0 | 124
124
38947.6398 | 1 | 0 | 125
38947.6419 | 1 | 0 | 125
38947.644 | 1 | 0 | 125
38947.6462 | 1 | 0 | 125
38947.6483 | 1 | 0 | 125
38947.6505 | 2109 | 0 | 125
38947.6526 | 2007 | 0 | 125
38947.6547 | 2439 | 0 | 125
38947.6569 | 2578 | 0 | 125
38947.659 | 2540 | 0 | 125
38947.6611 | 2555 | 0 | 125
125
38947.6398 | 1 | 0 | 126
38947.6419 | 1 | 0 | 126
38947.6441 | 1 | 0 | 126
38947.6462 | 1 | 0 | 126
38947.6483 | 1 | 0 | 126
38947.6505 | 1976 | 0 | 126
38947.6526 | 2238 | 0 | 126
38947.6547 | 2105 | 0 | 126
38947.6569 | 1923 | 0 | 126
38947.659 | 1912 | 0 | 126
38947.6612 | 1190 | 0 | 126
126
38947.6398 | 1 | 0 | 127
38947.6419 | 1 | 0 | 127
38947.6441 | 1 | 0 | 127
38947.6462 | 1 | 0 | 127
38947.6483 | 1 | 0 | 127
38947.6505 | 94 | 0 | 127
38947.6526 | 2130 | 0 | 127
38947.6548 | 2104 | 0 | 127
38947.6569 | 2294 | 0 | 127
38947.659 | 2406 | 0 | 127
38947.6612 | 2529 | 0 | 127
127
38947.6398 | 1 | 0 | 128
38947.6419 | 1 | 0 | 128
38947.6441 | 1 | 0 | 128
38947.6462 | 1 | 0 | 128
38947.6484 | 1 | 0 | 128
38947.6505 | 1928 | 0 | 128
38947.6526 | 1959 | 0 | 128
38947.6548 | 2020 | 0 | 128
38947.6569 | 2033 | 0 | 128
38947.6591 | 1524 | 0 | 128
38947.6612 | 1997 | 0 | 128
128
38947.6398 | 1 | 0 | 129
38947.642 | 1 | 0 | 129
38947.6441 | 1 | 0 | 129
38947.6462 | 1 | 0 | 129
38947.6484 | 1 | 0 | 129
38947.6505 | 82 | 0 | 129
38947.6527 | 2477 | 0 | 129
38947.6548 | 2056 | 0 | 129
38947.6569 | 2216 | 0 | 129
38947.6591 | 2008 | 0 | 129
38947.6612 | 2568 | 0 | 129
129
38947.6398 | 1 | 0 | 130
38947.642 | 1 | 0 | 130
38947.6441 | 1 | 0 | 130
38947.6463 | 1 | 0 | 130
38947.6484 | 1 | 0 | 130
38947.6505 | 1944 | 0 | 130
38947.6527 | 2010 | 0 | 130
38947.6548 | 2055 | 0 | 130
38947.657 | 1606 | 0 | 130
38947.6591 | 1991 | 0 | 130
38947.6612 | 1558 | 0 | 130
130
38947.6399 | 1 | 0 | 131
38947.642 | 1 | 0 | 131
38947.6441 | 1 | 0 | 131
38947.6463 | 1 | 1 | 131
38947.6484 | 1 | 0 | 131
38947.6506 | 2438 | 0 | 131
38947.6527 | 2498 | 0 | 131
38947.6548 | 2432 | 0 | 131
38947.657 | 1663 | 356 | 131
38947.6591 | 1584 | 1 | 131
38947.6612 | 2060 | 0 | 131
131
38947.6399 | 1 | 0 | 132
38947.642 | 1 | 0 | 132
38947.6442 | 1 | 0 | 132
38947.6463 | 1 | 0 | 132
38947.6484 | 1 | 0 | 132
38947.6506 | 2291 | 0 | 132
38947.6527 | 2217 | 0 | 132
38947.6548 | 2415 | 0 | 132
38947.657 | 1533 | 167 | 132
38947.6591 | 2199 | 0 | 132
38947.6613 | 1987 | 0 | 132
132

## D7-E10
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 152.5263 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38947.6395 | 1 | 0 | 38947.6395 | 1 | 0 |  | 30 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38947.6416 | 1 | 0 | 38947.6416 | 1 | 0 |  | 214.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38947.6438 | 1 | 0 | 38947.6438 | 1 | 0 |  | 399.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38947.6459 | 1 | 0 | 38947.6459 | 1 | 0 |  | 584.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38947.648 | 1 | 0 | 38947.648 | 1 | 0 |  | 769 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38947.6502 | 334 | 2 | 38947.6502 | 1402 | 7 |  | 954 | 1073 | 20.3907 | 0.1221 | 85.5922 | 0.42735 | 0.20391 | 0.001221 | 0.85592 | 0.0042735 | 0.20269 | 0.85165 | 656.9533 | 78.6536 | 47600.2169
38947.6523 | 1889 | 0 | 38947.6523 | 2110 | 0 |  | 1138.5 | 1257.5 | 115.3236 | 0 | 128.8156 | 0 | 1.1532 | 0 | 1.2882 | 0 | 1.1532 | 1.2882 | 32.2594 | 18.4066 | 31.1062
38947.6544 | 2095 | 0 | 38947.6545 | 2201 | 0 |  | 1323.5 | 1442.5 | 127.8999 | 0 | 134.3712 | 0 | 1.279 | 0 | 1.3437 | 0 | 1.279 | 1.3437 | 19.2544 | 13.5111 | 17.9754
38947.6566 | 2184 | 0 | 38947.6566 | 2464 | 0 |  | 1508.5 | 1627.5 | 133.3333 | 0 | 150.4274 | 0 | 1.3333 | 0 | 1.5043 | 0 | 1.3333 | 1.5043 | 14.3947 | 1.3953 | 13.0614
38947.6587 | 1969 | 0 | 38947.6587 | 2222 | 0 |  | 1693 | 1812 | 120.2076 | 0 | 135.6532 | 0 | 1.2021 | 0 | 1.3565 | 0 | 1.2021 | 1.3565 | 26.8857 | 12.4383 | 25.6837
38947.6609 | 2211 | 0 | 38947.6609 | 2482 | 0 |  | 1877.5 | 1996.5 | 134.9817 | 0 | 151.5263 | 0 | 1.3498 | 0 | 1.5153 | 0 | 1.3498 | 1.5153 | 12.9977 | 0.65995 | 11.6479

## D7-E9
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 153.442 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38947.6394 | 1 | 0 | 38947.6395 | 1 | 0 |  | 27 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38947.6416 | 1 | 0 | 38947.6416 | 1 | 0 |  | 212 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38947.6437 | 1 | 0 | 38947.6437 | 1 | 0 |  | 396.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38947.6459 | 1 | 0 | 38947.6459 | 1 | 0 |  | 581.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
38947.648 | 2 | 0 | 38947.648 | 1 | 0 |  | 766.5 | 885.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125569 | 251238 | 125568.9988
38947.6501 | 101 | 6 | 38947.6502 | 952 | 31 |  | 951 | 1070 | 6.1661 | 0.3663 | 58.1197 | 1.8926 | 0.061661 | 0.003663 | 0.5812 | 0.018926 | 0.057998 | 0.56227 | 2637.48 | 169.7476 | 25238.2354
38947.6523 | 1834 | 0 | 38947.6523 | 2458 | 0 |  | 1136 | 1255 | 111.9658 | 0 | 150.0611 | 0 | 1.1197 | 0 | 1.5006 | 0 | 1.1197 | 1.5006 | 37.0436 | 2.2531 | 35.924
38947.6544 | 2250 | 0 | 38947.6544 | 2497 | 0 |  | 1320.5 | 1439.5 | 137.3626 | 0 | 152.442 | 0 | 1.3736 | 0 | 1.5244 | 0 | 1.3736 | 1.5244 | 11.7058 | 0.65599 | 10.3322
38947.6566 | 2276 | 0 | 38947.6566 | 2410 | 0 |  | 1505.5 | 1624.5 | 138.9499 | 0 | 147.1306 | 0 | 1.3895 | 0 | 1.4713 | 0 | 1.3895 | 1.4713 | 10.4297 | 4.2896 | 9.0402
38947.6587 | 1995 | 0 | 38947.6587 | 1996 | 0 |  | 1690 | 1809 | 121.7949 | 0 | 121.8559 | 0 | 1.2179 | 0 | 1.2186 | 0 | 1.2179 | 1.2186 | 25.984 | 25.9208 | 24.766
38947.6608 | 2074 | 0 | 38947.6608 | 2479 | 0 |  | 1875 | 1994 | 126.6178 | 0 | 151.3431 | 0 | 1.2662 | 0 | 1.5134 | 0 | 1.2662 | 1.5134 | 21.1851 | 1.3868 | 19.919

## D7-D8
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 140.5604 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38947.6394 | 1 | 0 | 38947.6394 | 1 | 0 |  | 24.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230138 | 230138 | 230137.9994
38947.6415 | 1 | 0 | 38947.6416 | 1 | 0 |  | 209 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230138 | 230138 | 230137.9994
38947.6437 | 1 | 0 | 38947.6437 | 1 | 0 |  | 394 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230138 | 230138 | 230137.9994
38947.6458 | 1 | 0 | 38947.6458 | 1 | 0 |  | 578.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230138 | 230138 | 230137.9994
38947.648 | 1 | 0 | 38947.648 | 1 | 0 |  | 763.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230138 | 230138 | 230137.9994
38947.6501 | 1059 | 991 | 38947.6501 | 1070 | 997 |  | 948.5 | 1067.5 | 64.652 | 60.5006 | 65.3236 | 60.8669 | 0.64652 | 0.60501 | 0.65324 | 0.60867 | 0.041514 | 0.044567 | 4749.9541 | 2369.4911 | 24.4359
38947.6522 | 2222 | 119 | 38947.6523 | 2062 | 116 |  | 1133 | 1252 | 135.6532 | 7.265 | 125.8852 | 7.0818 | 1.3565 | 0.07265 | 1.2589 | 0.070818 | 1.2839 | 1.188 | 2.0142 | 6.3039 | 1.9245
38947.6544 | 1845 | 155 | 38947.6544 | 1663 | 121 |  | 1318 | 1437 | 112.6374 | 9.4628 | 101.5263 | 7.3871 | 1.1264 | 0.094628 | 1.0153 | 0.073871 | 1.0317 | 0.94139 | 32.5218 | 54.6506 | 68.9389
38947.6565 | 2067 | 91 | 38947.6565 | 1743 | 43 |  | 1502.5 | 1621.5 | 126.1905 | 5.5556 | 106.4103 | 2.6252 | 1.2619 | 0.055556 | 1.0641 | 0.026252 | 1.2063 | 1.0379 | 13.4388 | 40.5339 | 45.7618
38947.6587 | 1778 | 0 | 38947.6587 | 3 | 0 |  | 1687.5 | 1806.5 | 108.547 | 0 | 0.18315 | 0 | 1.0855 | 0 | 0.0018315 | 0 | 1.0855 | 0.0018315 | 29.4927 | 76646 | 28.4072
38947.6608 | 2286 | 0 | 38947.6608 | 3 | 0 |  | 1872 | 1991 | 139.5604 | 0 | 0.18315 | 0 | 1.3956 | 0 | 0.0018315 | 0 | 1.3956 | 0.0018315 | 0.71654 | 76646 | 0.67907

## C6-F12
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 140.1941 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38947.6394 | 1 | 0 | 38947.6394 | 1 | 0 |  | 21.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229538 | 229538 | 229537.9994
38947.6415 | 1 | 1 | 38947.6415 | 1 | 0 |  | 206.5 | 325.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 526876934.44 | 229538 | 229338.0871
38947.6436 | 1 | 0 | 38947.6437 | 1 | 0 |  | 391 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229538 | 229538 | 229537.9994
38947.6458 | 1 | 0 | 38947.6458 | 1 | 0 |  | 576 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229538 | 229538 | 229537.9994
38947.6479 | 1 | 0 | 38947.6479 | 1 | 0 |  | 760.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229538 | 229538 | 229537.9994
38947.6501 | 4 | 0 | 38947.6501 | 2279 | 0 |  | 945.5 | 1064.5 | 0.2442 | 0 | 139.1331 | 0 | 0.002442 | 0 | 1.3913 | 0 | 0.002442 | 1.3913 | 57309.5 | 0.76262 | 57309.4976
38947.6522 | 4 | 0 | 38947.6522 | 2004 | 0 |  | 1130 | 1249 | 0.2442 | 0 | 122.3443 | 0 | 0.002442 | 0 | 1.2234 | 0 | 0.002442 | 1.2234 | 57309.5 | 14.5898 | 57309.4976
38947.6543 | 29 | 0 | 38947.6544 | 1917 | 0 |  | 1315 | 1434 | 1.7705 | 0 | 117.033 | 0 | 0.017705 | 0 | 1.1703 | 0 | 0.017705 | 1.1703 | 7818.5517 | 19.7903 | 7818.534
38947.6565 | 3 | 0 | 38947.6565 | 2280 | 0 |  | 1499.5 | 1618.5 | 0.18315 | 0 | 139.1941 | 0 | 0.0018315 | 0 | 1.3919 | 0 | 0.0018315 | 1.3919 | 76446 | 0.71842 | 76445.9982
38947.6586 | 96 | 0 | 38947.6586 | 1698 | 0 |  | 1684.5 | 1803.5 | 5.8608 | 0 | 103.663 | 0 | 0.058608 | 0 | 1.0366 | 0 | 0.058608 | 1.0366 | 2292.0625 | 35.2403 | 2292.0039
38947.6608 | 2026 | 0 | 38947.6608 | 1546 | 0 |  | 1869.5 | 1988.5 | 123.6874 | 0 | 94.3834 | 0 | 1.2369 | 0 | 0.94383 | 0 | 1.2369 | 0.94383 | 13.3455 | 48.5369 | 12.1086

## C6-F11
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 151.0611 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38947.6393 | 1 | 0 | 38947.6394 | 1 | 0 |  | 19 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38947.6415 | 1 | 0 | 38947.6415 | 1 | 0 |  | 203.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38947.6436 | 1 | 0 | 38947.6436 | 1 | 0 |  | 388.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38947.6458 | 1 | 0 | 38947.6458 | 1 | 0 |  | 573 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38947.6479 | 1 | 0 | 38947.6479 | 1 | 0 |  | 758 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38947.65 | 3 | 0 | 38947.65 | 2458 | 0 |  | 942.5 | 1061.5 | 0.18315 | 0 | 150.0611 | 0 | 0.0018315 | 0 | 1.5006 | 0 | 0.0018315 | 1.5006 | 82379.3333 | 0.6664 | 82379.3315
38947.6522 | 3 | 0 | 38947.6522 | 2307 | 0 |  | 1127.5 | 1246.5 | 0.18315 | 0 | 140.8425 | 0 | 0.0018315 | 0 | 1.4084 | 0 | 0.0018315 | 1.4084 | 82379.3333 | 7.2553 | 82379.3315
38947.6543 | 3 | 0 | 38947.6543 | 1752 | 0 |  | 1312.5 | 1431.5 | 0.18315 | 0 | 106.9597 | 0 | 0.0018315 | 0 | 1.0696 | 0 | 0.0018315 | 1.0696 | 82379.3333 | 41.2317 | 82379.3315
38947.6564 | 3 | 0 | 38947.6565 | 2211 | 0 |  | 1497 | 1616 | 0.18315 | 0 | 134.9817 | 0 | 0.0018315 | 0 | 1.3498 | 0 | 0.0018315 | 1.3498 | 82379.3333 | 11.9123 | 82379.3315
38947.6586 | 57 | 0 | 38947.6586 | 2006 | 0 |  | 1681.5 | 1800.5 | 3.4799 | 0 | 122.4664 | 0 | 0.034799 | 0 | 1.2247 | 0 | 0.034799 | 1.2247 | 4241.0175 | 23.349 | 4240.9827
38947.6607 | 1828 | 0 | 38947.6607 | 1414 | 0 |  | 1866.5 | 1985.5 | 111.5995 | 0 | 86.3248 | 0 | 1.116 | 0 | 0.86325 | 0 | 1.116 | 0.86325 | 35.36 | 74.9915 | 34.244

## C6-E10
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 133.1734 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38947.6393 | 1 | 0 | 38947.6393 | 1 | 0 |  | 16 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218038 | 218038 | 218037.9994
38947.6414 | 1 | 0 | 38947.6415 | 1 | 0 |  | 200.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218038 | 218038 | 218037.9994
38947.6436 | 1 | 0 | 38947.6436 | 1 | 0 |  | 385.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218038 | 218038 | 218037.9994
38947.6457 | 1 | 0 | 38947.6457 | 1 | 0 |  | 570.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218038 | 218038 | 218037.9994
38947.6479 | 1 | 0 | 38947.6479 | 1 | 0 |  | 755 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218038 | 218038 | 218037.9994
38947.65 | 2 | 0 | 38947.65 | 1757 | 3 |  | 939.5 | 1058.5 | 0.1221 | 0 | 107.265 | 0.18315 | 0.001221 | 0 | 1.0726 | 0.0018315 | 0.001221 | 1.0708 | 108969 | 24.366 | 108968.9988
38947.6521 | 3 | 0 | 38947.6522 | 2073 | 0 |  | 1124.5 | 1243.5 | 0.18315 | 0 | 126.5568 | 0 | 0.0018315 | 0 | 1.2656 | 0 | 0.0018315 | 1.2656 | 72612.6667 | 5.2282 | 72612.6648
38947.6543 | 3 | 0 | 38947.6543 | 1995 | 0 |  | 1309.5 | 1428.5 | 0.18315 | 0 | 121.7949 | 0 | 0.0018315 | 0 | 1.2179 | 0 | 0.0018315 | 1.2179 | 72612.6667 | 9.3424 | 72612.6648
38947.6564 | 3 | 0 | 38947.6564 | 2165 | 0 |  | 1494 | 1613 | 0.18315 | 0 | 132.1734 | 0 | 0.0018315 | 0 | 1.3217 | 0 | 0.0018315 | 1.3217 | 72612.6667 | 0.75658 | 72612.6648
38947.6586 | 40 | 0 | 38947.6586 | 2078 | 0 |  | 1679 | 1798 | 2.442 | 0 | 126.862 | 0 | 0.02442 | 0 | 1.2686 | 0 | 0.02442 | 1.2686 | 5353.45 | 4.975 | 5353.4256
38947.6607 | 1553 | 0 | 38947.6607 | 2138 | 0 |  | 1863.5 | 1982.5 | 94.8107 | 0 | 130.525 | 0 | 0.94811 | 0 | 1.3053 | 0 | 0.94811 | 1.3053 | 40.4623 | 2.029 | 39.5142

## C6-E9
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 149.1685 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38947.6393 | 1 | 0 | 38947.6393 | 1 | 0 |  | 13 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38947.6414 | 1 | 0 | 38947.6414 | 1 | 0 |  | 198 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38947.6436 | 1 | 0 | 38947.6436 | 1 | 0 |  | 382.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38947.6457 | 1 | 0 | 38947.6457 | 1 | 0 |  | 567.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38947.6478 | 1 | 0 | 38947.6478 | 1 | 0 |  | 752.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38947.65 | 2 | 0 | 38947.65 | 770 | 3 |  | 937 | 1056 | 0.1221 | 0 | 47.0085 | 0.18315 | 0.001221 | 0 | 0.47009 | 0.0018315 | 0.001221 | 0.46825 | 122069 | 218.5632 | 122068.9988
38947.6521 | 3 | 0 | 38947.6521 | 2238 | 0 |  | 1121.5 | 1240.5 | 0.18315 | 0 | 136.63 | 0 | 0.0018315 | 0 | 1.3663 | 0 | 0.0018315 | 1.3663 | 81346 | 9.1769 | 81345.9982
38947.6542 | 82 | 0 | 38947.6543 | 2427 | 0 |  | 1306.5 | 1425.5 | 5.0061 | 0 | 148.1685 | 0 | 0.050061 | 0 | 1.4817 | 0 | 0.050061 | 1.4817 | 2879.7317 | 0.67491 | 2879.6816
38947.6564 | 3 | 0 | 38947.6564 | 2040 | 0 |  | 1491.5 | 1610.5 | 0.18315 | 0 | 124.5421 | 0 | 0.0018315 | 0 | 1.2454 | 0 | 0.0018315 | 1.2454 | 81346 | 19.7735 | 81345.9982
38947.6585 | 20 | 0 | 38947.6585 | 2387 | 0 |  | 1676 | 1795 | 1.221 | 0 | 145.7265 | 0 | 0.01221 | 0 | 1.4573 | 0 | 0.01221 | 1.4573 | 12116.9 | 2.362 | 12116.8878
38947.6607 | 1638 | 0 | 38947.6607 | 2012 | 0 |  | 1861 | 1980 | 100 | 0 | 122.8327 | 0 | 1 | 0 | 1.2283 | 0 | 1 | 1.2283 | 49.1685 | 21.4404 | 48.1685

## C5-F12
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 143.9182 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38947.6392 | 1 | 0 | 38947.6392 | 1 | 0 |  | 5 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235638 | 235638 | 235637.9994
38947.6413 | 1 | 0 | 38947.6413 | 1 | 0 |  | 189.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235638 | 235638 | 235637.9994
38947.6435 | 1 | 0 | 38947.6435 | 1 | 0 |  | 374.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235638 | 235638 | 235637.9994
38947.6456 | 1 | 0 | 38947.6456 | 1 | 0 |  | 559 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235638 | 235638 | 235637.9994
38947.6477 | 1 | 0 | 38947.6478 | 1 | 0 |  | 744 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235638 | 235638 | 235637.9994
38947.6499 | 4 | 0 | 38947.6499 | 2341 | 0 |  | 928.5 | 1047.5 | 0.2442 | 0 | 142.9182 | 0 | 0.002442 | 0 | 1.4292 | 0 | 0.002442 | 1.4292 | 58834.5 | 0.6997 | 58834.4976
38947.652 | 9 | 0 | 38947.652 | 2070 | 0 |  | 1113.5 | 1232.5 | 0.54945 | 0 | 126.3736 | 0 | 0.0054945 | 0 | 1.2637 | 0 | 0.0054945 | 1.2637 | 26093.1111 | 13.8831 | 26093.1056
38947.6542 | 10 | 0 | 38947.6542 | 1985 | 0 |  | 1298.5 | 1417.5 | 0.6105 | 0 | 121.1844 | 0 | 0.006105 | 0 | 1.2118 | 0 | 0.006105 | 1.2118 | 23473.8 | 18.7597 | 23473.7939
38947.6563 | 3 | 0 | 38947.6563 | 2106 | 0 |  | 1483 | 1602 | 0.18315 | 0 | 128.5714 | 0 | 0.0018315 | 0 | 1.2857 | 0 | 0.0018315 | 1.2857 | 78479.3333 | 11.9364 | 78479.3315
38947.6584 | 20 | 0 | 38947.6584 | 1805 | 0 |  | 1667.5 | 1786.5 | 1.221 | 0 | 110.1954 | 0 | 0.01221 | 0 | 1.102 | 0 | 0.01221 | 1.102 | 11686.9 | 30.6028 | 11686.8878
38947.6606 | 1873 | 0 | 38947.6606 | 1821 | 0 |  | 1852.5 | 1971.5 | 114.3468 | 0 | 111.1722 | 0 | 1.1435 | 0 | 1.1117 | 0 | 1.1435 | 1.1117 | 25.8612 | 29.4552 | 24.7177

## C5-F11
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129.6325 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38947.6391 | 1 | 0 | 38947.6392 | 1 | 0 |  | 2 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212238 | 212238 | 212237.9994
38947.6413 | 1 | 0 | 38947.6413 | 1 | 0 |  | 186.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212238 | 212238 | 212237.9994
38947.6434 | 1 | 0 | 38947.6434 | 1 | 0 |  | 371.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212238 | 212238 | 212237.9994
38947.6456 | 1 | 0 | 38947.6456 | 1 | 0 |  | 556.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212238 | 212238 | 212237.9994
38947.6477 | 1 | 0 | 38947.6477 | 1 | 0 |  | 741 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212238 | 212238 | 212237.9994
38947.6498 | 2 | 0 | 38947.6499 | 1946 | 0 |  | 926 | 1045 | 0.1221 | 0 | 118.8034 | 0 | 0.001221 | 0 | 1.188 | 0 | 0.001221 | 1.188 | 106069 | 9.1151 | 106068.9988
38947.652 | 3 | 0 | 38947.652 | 2107 | 0 |  | 1110.5 | 1229.5 | 0.18315 | 0 | 128.6325 | 0 | 0.0018315 | 0 | 1.2863 | 0 | 0.0018315 | 1.2863 | 70679.3333 | 0.77741 | 70679.3315
38947.6541 | 5 | 0 | 38947.6541 | 1797 | 0 |  | 1295.5 | 1414.5 | 0.30525 | 0 | 109.707 | 0 | 0.0030525 | 0 | 1.0971 | 0 | 0.0030525 | 1.0971 | 42367.6 | 18.1625 | 42367.5969
38947.6562 | 4 | 0 | 38947.6563 | 1715 | 0 |  | 1480 | 1599 | 0.2442 | 0 | 104.7009 | 0 | 0.002442 | 0 | 1.047 | 0 | 0.002442 | 1.047 | 52984.5 | 23.8122 | 52984.4976
38947.6584 | 5 | 0 | 38947.6584 | 1335 | 0 |  | 1665 | 1784 | 0.30525 | 0 | 81.5018 | 0 | 0.0030525 | 0 | 0.81502 | 0 | 0.0030525 | 0.81502 | 42367.6 | 59.0547 | 42367.5969
38947.6605 | 1924 | 0 | 38947.6605 | 1613 | 0 |  | 1849.5 | 1968.5 | 117.4603 | 0 | 98.4737 | 0 | 1.1746 | 0 | 0.98474 | 0 | 1.1746 | 0.98474 | 10.3628 | 31.6417 | 9.1882

## C5-E10
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 158.3871 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38947.6391 | 1 | 0 | 38947.6391 | 1 | 0 |  | -1 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6413 | 1 | 1 | 38947.6413 | 1 | 0 |  | 184 | 303 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 672561982.44 | 259338 | 259138.0771
38947.6434 | 1 | 0 | 38947.6434 | 1 | 0 |  | 368.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6455 | 1 | 0 | 38947.6455 | 1 | 0 |  | 553.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6477 | 1 | 0 | 38947.6477 | 1 | 0 |  | 738.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259338 | 259338 | 259337.9994
38947.6498 | 2 | 0 | 38947.6498 | 1797 | 0 |  | 923 | 1042 | 0.1221 | 0 | 109.707 | 0 | 0.001221 | 0 | 1.0971 | 0 | 0.001221 | 1.0971 | 129619 | 44.3728 | 129618.9988
38947.6519 | 4 | 0 | 38947.652 | 2042 | 0 |  | 1107.5 | 1226.5 | 0.2442 | 0 | 124.6642 | 0 | 0.002442 | 0 | 1.2466 | 0 | 0.002442 | 1.2466 | 64759.5 | 27.0509 | 64759.4976
38947.6541 | 4 | 0 | 38947.6541 | 2578 | 0 |  | 1292.5 | 1411.5 | 0.2442 | 0 | 157.3871 | 0 | 0.002442 | 0 | 1.5739 | 0 | 0.002442 | 1.5739 | 64759.5 | 0.63538 | 64759.4976
38947.6562 | 3 | 0 | 38947.6562 | 2410 | 0 |  | 1477.5 | 1596.5 | 0.18315 | 0 | 147.1306 | 0 | 0.0018315 | 0 | 1.4713 | 0 | 0.0018315 | 1.4713 | 86379.3333 | 7.6506 | 86379.3315
38947.6584 | 4 | 0 | 38947.6584 | 2522 | 0 |  | 1662 | 1781 | 0.2442 | 0 | 153.9683 | 0 | 0.002442 | 0 | 1.5397 | 0 | 0.002442 | 1.5397 | 64759.5 | 2.8699 | 64759.4976
38947.6605 | 1746 | 0 | 38947.6605 | 2337 | 0 |  | 1847 | 1966 | 106.5934 | 0 | 142.674 | 0 | 1.0659 | 0 | 1.4267 | 0 | 1.0659 | 1.4267 | 48.5899 | 11.0133 | 47.524

## C5-E9
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 151.7326 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38947.6391 | 1 | 0 | 38947.6391 | 1 | 0 |  | -3.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38947.6412 | 1 | 0 | 38947.6412 | 1 | 0 |  | 181 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38947.6434 | 1 | 0 | 38947.6434 | 1 | 0 |  | 366 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38947.6455 | 1 | 0 | 38947.6455 | 1 | 0 |  | 550.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38947.6476 | 1 | 0 | 38947.6477 | 1 | 0 |  | 735.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38947.6498 | 2 | 0 | 38947.6498 | 2 | 0 |  | 920.5 | 1039.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124169 | 124169 | 124168.9988
38947.6519 | 4 | 0 | 38947.6519 | 2449 | 0 |  | 1105 | 1224 | 0.2442 | 0 | 149.5116 | 0 | 0.002442 | 0 | 1.4951 | 0 | 0.002442 | 1.4951 | 62034.5 | 1.4855 | 62034.4976
38947.6541 | 3 | 0 | 38947.6541 | 2197 | 0 |  | 1290 | 1409 | 0.18315 | 0 | 134.127 | 0 | 0.0018315 | 0 | 1.3413 | 0 | 0.0018315 | 1.3413 | 82746 | 13.1261 | 82745.9982
38947.6562 | 3 | 0 | 38947.6562 | 2002 | 0 |  | 1474.5 | 1593.5 | 0.18315 | 0 | 122.2222 | 0 | 0.0018315 | 0 | 1.2222 | 0 | 0.0018315 | 1.2222 | 82746 | 24.1449 | 82745.9982
38947.6583 | 4 | 1 | 38947.6583 | 2469 | 0 |  | 1659.5 | 1778.5 | 0.2442 | 0.06105 | 150.7326 | 0 | 0.002442 | 0.0006105 | 1.5073 | 0 | 0.0018315 | 1.5073 | 1679.6428 | 0.69093 | 1702.0076
38947.6605 | 1774 | 0 | 38947.6605 | 2241 | 1 |  | 1844 | 1963 | 108.3028 | 0 | 136.8132 | 0.06105 | 1.083 | 0 | 1.3681 | 0.0006105 | 1.083 | 1.3675 | 40.1003 | 10.9545 | 39.0173

## C5-C6
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38947.639 | 1 | 0 | 38947.639 | 1 | 0 |  | -12 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6411 | 1 | 0 | 38947.6411 | 1 | 0 |  | 172.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6433 | 1 | 0 | 38947.6433 | 1 | 0 |  | 357.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6454 | 1 | 0 | 38947.6454 | 1 | 0 |  | 542.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6475 | 1 | 0 | 38947.6476 | 1 | 0 |  | 727 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6497 | 3 | 0 | 38947.6497 | 3 | 0 |  | 912 | 1031 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6518 | 4 | 0 | 38947.6518 | 3 | 0 |  | 1096.5 | 1215.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38947.654 | 3 | 0 | 38947.654 | 936 | 892 |  | 1281.5 | 1400.5 | 0.18315 | 0 | 57.1429 | 54.4567 | 0.0018315 | 0 | 0.57143 | 0.54457 | 0.0018315 | 0.026862 | 70334 | 4702.3182 | 70333.9982
38947.6561 | 1127 | 933 | 38947.6561 | 1207 | 1021 |  | 1466 | 1585 | 68.8034 | 56.9597 | 73.6874 | 62.3321 | 0.68803 | 0.5696 | 0.73687 | 0.62332 | 0.11844 | 0.11355 | 2656.6075 | 594.706 | 4.8647
38947.6582 | 1048 | 971 | 38947.6583 | 872 | 806 |  | 1651 | 1770 | 63.9805 | 59.2796 | 53.2357 | 49.2063 | 0.6398 | 0.5928 | 0.53236 | 0.49206 | 0.047009 | 0.040293 | 1712.8745 | 6550.7857 | 9.5372
38947.6604 | 1075 | 857 | 38947.6604 | 1204 | 876 |  | 1835.5 | 1954.5 | 65.6288 | 52.3199 | 73.5043 | 53.4799 | 0.65629 | 0.5232 | 0.73504 | 0.5348 | 0.13309 | 0.20024 | 232.5453 | 375.2627 | 16.6781

## B4-E10
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 158.5092 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38947.6389 | 1 | 0 | 38947.6389 | 1 | 0 |  | -20.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
38947.641 | 1 | 0 | 38947.641 | 1 | 0 |  | 164.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
38947.6432 | 1 | 0 | 38947.6432 | 1 | 0 |  | 349 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
38947.6453 | 1 | 0 | 38947.6453 | 1 | 0 |  | 534 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
38947.6474 | 1 | 0 | 38947.6475 | 1 | 0 |  | 718.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
38947.6496 | 1 | 0 | 38947.6496 | 2036 | 0 |  | 903.5 | 1022.5 | 0.06105 | 0 | 124.2979 | 0 | 0.0006105 | 0 | 1.243 | 0 | 0.0006105 | 1.243 | 259538 | 27.5236 | 259537.9994
38947.6517 | 3 | 0 | 38947.6517 | 2580 | 0 |  | 1088 | 1207 | 0.18315 | 0 | 157.5092 | 0 | 0.0018315 | 0 | 1.5751 | 0 | 0.0018315 | 1.5751 | 86446 | 0.63488 | 86445.9982
38947.6539 | 3 | 0 | 38947.6539 | 2269 | 0 |  | 1273 | 1392 | 0.18315 | 0 | 138.5226 | 0 | 0.0018315 | 0 | 1.3852 | 0 | 0.0018315 | 1.3852 | 86446 | 14.4284 | 86445.9982
38947.656 | 3 | 0 | 38947.656 | 2185 | 0 |  | 1457.5 | 1576.5 | 0.18315 | 0 | 133.3944 | 0 | 0.0018315 | 0 | 1.3339 | 0 | 0.0018315 | 1.3339 | 86446 | 18.8275 | 86445.9982
38947.6581 | 682 | 0 | 38947.6581 | 2431 | 0 |  | 1642.5 | 1761.5 | 41.6361 | 0 | 148.4127 | 0 | 0.41636 | 0 | 1.4841 | 0 | 0.41636 | 1.4841 | 280.7009 | 6.803 | 280.2845
38947.6603 | 4 | 0 | 38947.6603 | 2029 | 0 |  | 1827.5 | 1946.5 | 0.2442 | 0 | 123.8706 | 0 | 0.002442 | 0 | 1.2387 | 0 | 0.002442 | 1.2387 | 64809.5 | 27.9635 | 64809.4976

## B4-E9
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 154.0525 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38947.6389 | 1 | 0 | 38947.6389 | 1 | 0 |  | -23.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38947.641 | 1 | 0 | 38947.641 | 1 | 0 |  | 161.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38947.6431 | 1 | 0 | 38947.6431 | 1 | 0 |  | 346.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38947.6453 | 1 | 0 | 38947.6453 | 1 | 0 |  | 531 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38947.6474 | 1 | 0 | 38947.6474 | 1 | 0 |  | 716 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38947.6495 | 1 | 0 | 38947.6496 | 1 | 0 |  | 900.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38947.6517 | 3 | 0 | 38947.6517 | 2507 | 0 |  | 1085.5 | 1204.5 | 0.18315 | 0 | 153.0525 | 0 | 0.0018315 | 0 | 1.5305 | 0 | 0.0018315 | 1.5305 | 84012.6667 | 0.65337 | 84012.6648
38947.6538 | 3 | 0 | 38947.6538 | 2250 | 0 |  | 1270 | 1389 | 0.18315 | 0 | 137.3626 | 0 | 0.0018315 | 0 | 1.3736 | 0 | 0.0018315 | 1.3736 | 84012.6667 | 12.1502 | 84012.6648
38947.656 | 3 | 0 | 38947.656 | 2500 | 0 |  | 1455 | 1574 | 0.18315 | 0 | 152.6252 | 0 | 0.0018315 | 0 | 1.5263 | 0 | 0.0018315 | 1.5263 | 84012.6667 | 0.9352 | 84012.6648
38947.6581 | 722 | 0 | 38947.6581 | 2469 | 0 |  | 1639.5 | 1758.5 | 44.0781 | 0 | 150.7326 | 0 | 0.44078 | 0 | 1.5073 | 0 | 0.44078 | 1.5073 | 249.4986 | 2.2025 | 249.0578
38947.6602 | 3 | 0 | 38947.6603 | 2068 | 0 |  | 1824.5 | 1943.5 | 0.18315 | 0 | 126.2515 | 0 | 0.0018315 | 0 | 1.2625 | 0 | 0.0018315 | 1.2625 | 84012.6667 | 22.0203 | 84012.6648

## B4-D8
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38947.6388 | 1 | 0 | 38947.6388 | 1 | 0 |  | -26 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.641 | 1 | 0 | 38947.641 | 1 | 0 |  | 158.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6431 | 1 | 0 | 38947.6431 | 1 | 0 |  | 343.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6452 | 1 | 0 | 38947.6453 | 1 | 0 |  | 528.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6474 | 1 | 0 | 38947.6474 | 1 | 0 |  | 713 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6495 | 2 | 0 | 38947.6495 | 2 | 0 |  | 898 | 1017 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38947.6517 | 3 | 0 | 38947.6517 | 1832 | 0 |  | 1082.5 | 1201.5 | 0.18315 | 0 | 111.8437 | 0 | 0.0018315 | 0 | 1.1184 | 0 | 0.0018315 | 1.1184 | 70334 | 15.3395 | 70333.9982
38947.6538 | 3 | 0 | 38947.6538 | 1684 | 0 |  | 1267.5 | 1386.5 | 0.18315 | 0 | 102.8083 | 0 | 0.0018315 | 0 | 1.0281 | 0 | 0.0018315 | 1.0281 | 70334 | 25.4762 | 70333.9982
38947.6559 | 3 | 0 | 38947.6559 | 1804 | 0 |  | 1452 | 1571 | 0.18315 | 0 | 110.1343 | 0 | 0.0018315 | 0 | 1.1013 | 0 | 0.0018315 | 1.1013 | 70334 | 17.1297 | 70333.9982
38947.6581 | 359 | 0 | 38947.6581 | 380 | 0 |  | 1637 | 1756 | 21.917 | 0 | 23.199 | 0 | 0.21917 | 0 | 0.23199 | 0 | 0.21917 | 0.23199 | 488.585 | 456.0579 | 488.3658
38947.6602 | 4 | 0 | 38947.6602 | 3 | 0 |  | 1821.5 | 1940.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976

## B4-D7
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 133.6007 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38947.6388 | 1 | 0 | 38947.6388 | 1 | 0 |  | -29 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218738 | 218738 | 218737.9994
38947.6409 | 1 | 0 | 38947.6409 | 1 | 0 |  | 156 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218738 | 218738 | 218737.9994
38947.6431 | 1 | 0 | 38947.6431 | 1 | 0 |  | 340.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218738 | 218738 | 218737.9994
38947.6452 | 1 | 0 | 38947.6452 | 1 | 0 |  | 525.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218738 | 218738 | 218737.9994
38947.6473 | 1 | 0 | 38947.6474 | 1 | 0 |  | 710.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218738 | 218738 | 218737.9994
38947.6495 | 1 | 0 | 38947.6495 | 1 | 0 |  | 895 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218738 | 218738 | 218737.9994
38947.6516 | 2 | 0 | 38947.6516 | 1879 | 0 |  | 1080 | 1199 | 0.1221 | 0 | 114.7131 | 0 | 0.001221 | 0 | 1.1471 | 0 | 0.001221 | 1.1471 | 109319 | 16.4651 | 109318.9988
38947.6538 | 3 | 0 | 38947.6538 | 2172 | 0 |  | 1264.5 | 1383.5 | 0.18315 | 0 | 132.6007 | 0 | 0.0018315 | 0 | 1.326 | 0 | 0.0018315 | 1.326 | 72846 | 0.75414 | 72845.9982
38947.6559 | 3 | 0 | 38947.6559 | 1862 | 0 |  | 1449.5 | 1568.5 | 0.18315 | 0 | 113.6752 | 0 | 0.0018315 | 0 | 1.1368 | 0 | 0.0018315 | 1.1368 | 72846 | 17.5285 | 72845.9982
38947.658 | 1165 | 95 | 38947.6581 | 1682 | 0 |  | 1634 | 1753 | 71.1233 | 5.7998 | 102.6862 | 0 | 0.71123 | 0.057998 | 1.0269 | 0 | 0.65324 | 1.0269 | 135.6465 | 30.1058 | 226.1289
38947.6602 | 51 | 0 | 38947.6602 | 2077 | 0 |  | 1819 | 1938 | 3.1136 | 0 | 126.801 | 0 | 0.031136 | 0 | 1.268 | 0 | 0.031136 | 1.268 | 4190.9412 | 5.3625 | 4190.91

## B4-C6
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38947.6388 | 1 | 0 | 38947.6388 | 1 | 0 |  | -31.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6409 | 1 | 0 | 38947.6409 | 1 | 0 |  | 153 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.643 | 1 | 0 | 38947.6431 | 1 | 0 |  | 338 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6452 | 1 | 0 | 38947.6452 | 1 | 0 |  | 522.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6473 | 1 | 0 | 38947.6473 | 1 | 0 |  | 707.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6495 | 2 | 0 | 38947.6495 | 2 | 0 |  | 892.5 | 1011.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38947.6516 | 3 | 0 | 38947.6516 | 2 | 0 |  | 1077 | 1196 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38947.6537 | 3 | 0 | 38947.6537 | 3 | 0 |  | 1262 | 1381 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
| 3 | 0 | 38947.6559 | 3 | 0 |  | 1447 | 1566 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.658 | 877 | 0 | 38947.658 | 5 | 0 |  | 1631.5 | 1750.5 | 53.5409 | 0 | 0.30525 | 0 | 0.53541 | 0 | 0.0030525 | 0 | 0.53541 | 0.0030525 | 140.9373 | 42160.4 | 140.4019
38947.6601 | 4 | 0 | 38947.6602 | 357 | 0 |  | 1816 | 1935 | 0.2442 | 0 | 21.7949 | 0 | 0.002442 | 0 | 0.21795 | 0 | 0.002442 | 0.21795 | 52725.5 | 491.8824 | 52725.4976

## B4-C5
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38947.6387 | 1 | 0 | 38947.6387 | 1 | 0 |  | -34.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6409 | 1 | 0 | 38947.6409 | 1 | 0 |  | 150.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.643 | 1 | 0 | 38947.643 | 1 | 0 |  | 335 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6451 | 1 | 0 | 38947.6452 | 1 | 0 |  | 520 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6473 | 1 | 0 | 38947.6473 | 1 | 0 |  | 704.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6494 | 2 | 0 | 38947.6494 | 2 | 0 |  | 889.5 | 1008.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38947.6516 | 3 | 0 | 38947.6516 | 3 | 0 |  | 1074.5 | 1193.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6537 | 2 | 0 | 38947.6537 | 3 | 0 |  | 1259 | 1378 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38947.6558 | 3 | 0 | 38947.6558 | 142 | 0 |  | 1443.5 | 1562.5 | 0.18315 | 0 | 8.6691 | 0 | 0.0018315 | 0 | 0.086691 | 0 | 0.0018315 | 0.086691 | 70334 | 1388.0423 | 70333.9982
38947.658 | 1371 | 0 | 38947.658 | 5 | 0 |  | 1628.5 | 1747.5 | 83.6996 | 0 | 0.30525 | 0 | 0.837 | 0 | 0.0030525 | 0 | 0.837 | 0.0030525 | 54.1225 | 42160.4 | 53.2855
38947.6601 | 4 | 0 | 38947.6601 | 336 | 0 |  | 1813.5 | 1932.5 | 0.2442 | 0 | 20.5128 | 0 | 0.002442 | 0 | 0.20513 | 0 | 0.002442 | 0.20513 | 52725.5 | 528.875 | 52725.4976

## B3-E10
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 153.8694 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38947.6386 | 1 | 0 | 38947.6386 | 1 | 0 |  | -43 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38947.6408 | 1 | 0 | 38947.6408 | 1 | 0 |  | 142 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38947.6429 | 1 | 0 | 38947.6429 | 1 | 0 |  | 326.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38947.645 | 1 | 0 | 38947.6451 | 1 | 0 |  | 511.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38947.6472 | 1 | 0 | 38947.6472 | 1 | 0 |  | 696.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38947.6493 | 1 | 0 | 38947.6493 | 1 | 0 |  | 881 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38947.6515 | 3 | 0 | 38947.6515 | 1444 | 1 |  | 1066 | 1185 | 0.18315 | 0 | 88.1563 | 0.06105 | 0.0018315 | 0 | 0.88156 | 0.0006105 | 0.0018315 | 0.88095 | 83912.6667 | 74.6625 | 83912.6648
38947.6536 | 3 | 0 | 38947.6536 | 2504 | 0 |  | 1250.5 | 1369.5 | 0.18315 | 0 | 152.8694 | 0 | 0.0018315 | 0 | 1.5287 | 0 | 0.0018315 | 1.5287 | 83912.6667 | 0.65415 | 83912.6648
38947.6557 | 3 | 0 | 38947.6558 | 2319 | 0 |  | 1435.5 | 1554.5 | 0.18315 | 0 | 141.5751 | 0 | 0.0018315 | 0 | 1.4158 | 0 | 0.0018315 | 1.4158 | 83912.6667 | 8.6839 | 83912.6648
38947.6579 | 10 | 0 | 38947.6579 | 2112 | 0 |  | 1620 | 1739 | 0.6105 | 0 | 128.9377 | 0 | 0.006105 | 0 | 1.2894 | 0 | 0.006105 | 1.2894 | 25103.8 | 19.3362 | 25103.7939
38947.66 | 3 | 0 | 38947.66 | 2000 | 0 |  | 1805 | 1924 | 0.18315 | 0 | 122.1001 | 0 | 0.0018315 | 0 | 1.221 | 0 | 0.0018315 | 1.221 | 83912.6667 | 26.019 | 83912.6648

## B3-E9
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 145.0781 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38947.6386 | 1 | 0 | 38947.6386 | 1 | 0 |  | -45.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237538 | 237538 | 237537.9994
38947.6407 | 1 | 1 | 38947.6408 | 1 | 0 |  | 139 | 258 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 564243014.44 | 237538 | 237338.0842
38947.6429 | 1 | 0 | 38947.6429 | 1 | 0 |  | 324 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237538 | 237538 | 237537.9994
38947.645 | 1 | 0 | 38947.645 | 1 | 0 |  | 508.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237538 | 237538 | 237537.9994
38947.6472 | 1 | 0 | 38947.6472 | 1 | 0 |  | 693.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237538 | 237538 | 237537.9994
38947.6493 | 1 | 0 | 38947.6493 | 1 | 0 |  | 878.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237538 | 237538 | 237537.9994
38947.6514 | 3 | 0 | 38947.6514 | 2156 | 0 |  | 1063 | 1182 | 0.18315 | 0 | 131.6239 | 0 | 0.0018315 | 0 | 1.3162 | 0 | 0.0018315 | 1.3162 | 79112.6667 | 10.2217 | 79112.6648
38947.6536 | 3 | 0 | 38947.6536 | 2360 | 0 |  | 1248 | 1367 | 0.18315 | 0 | 144.0781 | 0 | 0.0018315 | 0 | 1.4408 | 0 | 0.0018315 | 1.4408 | 79112.6667 | 0.69407 | 79112.6648
38947.6557 | 5 | 0 | 38947.6557 | 2093 | 0 |  | 1432.5 | 1551.5 | 0.30525 | 0 | 127.7778 | 0 | 0.0030525 | 0 | 1.2778 | 0 | 0.0030525 | 1.2778 | 47427.6 | 13.5394 | 47427.5969
38947.6578 | 3 | 0 | 38947.6579 | 2312 | 0 |  | 1617.5 | 1736.5 | 0.18315 | 0 | 141.1477 | 0 | 0.0018315 | 0 | 1.4115 | 0 | 0.0018315 | 1.4115 | 79112.6667 | 2.7846 | 79112.6648
38947.66 | 15 | 1 | 38947.66 | 2345 | 0 |  | 1802 | 1921 | 0.91575 | 0.06105 | 143.1624 | 0 | 0.0091575 | 0.0006105 | 1.4316 | 0 | 0.008547 | 1.4316 | 3888.3813 | 2.14 | 4945.366

## B3-D8
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129.9988 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38947.6386 | 1 | 0 | 38947.6386 | 1 | 0 |  | -48.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212838 | 212838 | 212837.9994
38947.6407 | 1 | 0 | 38947.6407 | 1 | 0 |  | 136.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212838 | 212838 | 212837.9994
38947.6428 | 1 | 0 | 38947.6429 | 1 | 0 |  | 321 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212838 | 212838 | 212837.9994
38947.645 | 1 | 0 | 38947.645 | 1 | 0 |  | 506 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212838 | 212838 | 212837.9994
38947.6471 | 1 | 0 | 38947.6471 | 1 | 0 |  | 690.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212838 | 212838 | 212837.9994
38947.6493 | 1 | 0 | 38947.6493 | 1 | 0 |  | 875.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212838 | 212838 | 212837.9994
38947.6514 | 2 | 0 | 38947.6514 | 1393 | 0 |  | 1060.5 | 1179.5 | 0.1221 | 0 | 85.0427 | 0 | 0.001221 | 0 | 0.85043 | 0 | 0.001221 | 0.85043 | 106369 | 52.8629 | 106368.9988
38947.6535 | 3 | 0 | 38947.6536 | 2113 | 0 |  | 1245 | 1364 | 0.18315 | 0 | 128.9988 | 0 | 0.0018315 | 0 | 1.29 | 0 | 0.0018315 | 1.29 | 70879.3333 | 0.7752 | 70879.3315
38947.6557 | 3 | 0 | 38947.6557 | 1991 | 0 |  | 1430 | 1549 | 0.18315 | 0 | 121.5507 | 0 | 0.0018315 | 0 | 1.2155 | 0 | 0.0018315 | 1.2155 | 70879.3333 | 6.9503 | 70879.3315
38947.6578 | 5 | 0 | 38947.6578 | 935 | 0 |  | 1614.5 | 1733.5 | 0.30525 | 0 | 57.0818 | 0 | 0.0030525 | 0 | 0.57082 | 0 | 0.0030525 | 0.57082 | 42487.6 | 127.7412 | 42487.5969
38947.66 | 8 | 0 | 38947.66 | 2 | 0 |  | 1799.5 | 1918.5 | 0.4884 | 0 | 0.1221 | 0 | 0.004884 | 0 | 0.001221 | 0 | 0.004884 | 0.001221 | 26517.25 | 106369 | 26517.2451

## B3-D7
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 141.0488 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38947.6385 | 1 | 0 | 38947.6386 | 1 | 0 |  | -51 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38947.6407 | 1 | 0 | 38947.6407 | 1 | 0 |  | 133.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38947.6428 | 1 | 0 | 38947.6428 | 1 | 0 |  | 318.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38947.6449 | 2 | 0 | 38947.645 | 1 | 0 |  | 503 | 622 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38947.6471 | 1 | 0 | 38947.6471 | 1 | 0 |  | 688 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38947.6492 | 1 | 0 | 38947.6492 | 1 | 0 |  | 872.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38947.6514 | 3 | 0 | 38947.6514 | 1312 | 0 |  | 1057.5 | 1176.5 | 0.18315 | 0 | 80.0977 | 0 | 0.0018315 | 0 | 0.80098 | 0 | 0.0018315 | 0.80098 | 76912.6667 | 76.096 | 76912.6648
38947.6535 | 3 | 0 | 38947.6535 | 1689 | 0 |  | 1242.5 | 1361.5 | 0.18315 | 0 | 103.1136 | 0 | 0.0018315 | 0 | 1.0311 | 0 | 0.0018315 | 1.0311 | 76912.6667 | 36.7898 | 76912.6648
38947.6556 | 2 | 0 | 38947.6557 | 2294 | 0 |  | 1427 | 1546 | 0.1221 | 0 | 140.0488 | 0 | 0.001221 | 0 | 1.4005 | 0 | 0.001221 | 1.4005 | 115419 | 0.71404 | 115418.9988
38947.6578 | 22 | 0 | 38947.6578 | 2170 | 0 |  | 1611.5 | 1730.5 | 1.3431 | 0 | 132.4786 | 0 | 0.013431 | 0 | 1.3248 | 0 | 0.013431 | 1.3248 | 10401.7273 | 6.4691 | 10401.7138
38947.6599 | 14 | 1 | 38947.6599 | 2222 | 0 |  | 1796.5 | 1915.5 | 0.8547 | 0.06105 | 135.6532 | 0 | 0.008547 | 0.0006105 | 1.3565 | 0 | 0.0079365 | 1.3565 | 18913.5803 | 116.4734 | 123502.7909

## B3-C6
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38947.6385 | 1 | 0 | 38947.6385 | 1 | 0 |  | -54 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6406 | 1 | 0 | 38947.6407 | 1 | 0 |  | 131 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6428 | 1 | 0 | 38947.6428 | 1 | 0 |  | 315.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6449 | 1 | 0 | 38947.6449 | 1 | 0 |  | 500.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.647 | 1 | 0 | 38947.6471 | 1 | 0 |  | 685 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6492 | 1 | 0 | 38947.6492 | 1 | 0 |  | 869.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6513 | 3 | 0 | 38947.6513 | 3 | 0 |  | 1054.5 | 1173.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6535 | 3 | 0 | 38947.6535 | 3 | 0 |  | 1239.5 | 1358.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6556 | 3 | 0 | 38947.6556 | 2 | 0 |  | 1424 | 1543 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38947.6577 | 3 | 0 | 38947.6578 | 5 | 0 |  | 1609 | 1728 | 0.18315 | 0 | 0.30525 | 0 | 0.0018315 | 0 | 0.0030525 | 0 | 0.0018315 | 0.0030525 | 70334 | 42160.4 | 70333.9982
38947.6599 | 13 | 2 | 38947.6599 | 294 | 1 |  | 1793.5 | 1912.5 | 0.79365 | 0.1221 | 17.9487 | 0.06105 | 0.0079365 | 0.001221 | 0.17949 | 0.0006105 | 0.0067155 | 0.17888 | 19667.0603 | 620.8367 | 90348.3283

## B3-C5
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38947.6385 | 1 | 0 | 38947.6385 | 1 | 0 |  | -57 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6406 | 1 | 0 | 38947.6406 | 1 | 0 |  | 128 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6427 | 1 | 0 | 38947.6428 | 1 | 0 |  | 312.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6449 | 1 | 0 | 38947.6449 | 2 | 0 |  | 497.5 | 616.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38947.647 | 1 | 0 | 38947.647 | 1 | 0 |  | 682.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6492 | 2 | 0 | 38947.6492 | 1 | 0 |  | 867 | 986 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38947.6513 | 3 | 0 | 38947.6513 | 2 | 0 |  | 1052 | 1171 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38947.6534 | 3 | 0 | 38947.6534 | 3 | 0 |  | 1236.5 | 1355.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6556 | 5 | 0 | 38947.6556 | 4 | 0 |  | 1421.5 | 1540.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38947.6577 | 3 | 0 | 38947.6577 | 6 | 0 |  | 1606 | 1725 | 0.18315 | 0 | 0.3663 | 0 | 0.0018315 | 0 | 0.003663 | 0 | 0.0018315 | 0.003663 | 70334 | 35117 | 70333.9982
38947.6598 | 17 | 6 | 38947.6599 | 227 | 3 |  | 1791 | 1910 | 1.0379 | 0.3663 | 13.8584 | 0.18315 | 0.010379 | 0.003663 | 0.13858 | 0.0018315 | 0.0067155 | 0.13675 | 20374.5635 | 842.0286 | 31135.9373

## B3-B4
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38947.6384 | 1 | 0 | 38947.6384 | 1 | 0 |  | -59.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6406 | 1 | 0 |  | 1 | 0 |  | 124 | 243 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6427 | 1 | 0 | 38947.6427 | 1 | 0 |  | 310 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6448 | 1 | 0 | 38947.6449 | 1 | 0 |  | 494.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.647 | 1 | 0 | 38947.647 | 1 | 0 |  | 679.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6491 | 1 | 0 | 38947.6491 | 1 | 0 |  | 864.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6513 | 4 | 0 | 38947.6513 | 3 | 0 |  | 1049 | 1168 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38947.6534 | 3 | 0 | 38947.6534 | 3 | 0 |  | 1234 | 1353 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6555 | 4 | 0 | 38947.6556 | 3 | 0 |  | 1418.5 | 1537.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38947.6577 | 3 | 0 | 38947.6577 | 973 | 0 |  | 1603.5 | 1722.5 | 0.18315 | 0 | 59.4017 | 0 | 0.0018315 | 0 | 0.59402 | 0 | 0.0018315 | 0.59402 | 70334 | 117.1655 | 70333.9982
38947.6598 | 1034 | 950 | 38947.6598 | 1102 | 1092 |  | 1788 | 1907 | 63.1258 | 57.9976 | 67.2772 | 66.6667 | 0.63126 | 0.57998 | 0.67277 | 0.66667 | 0.051282 | 0.006105 | 70.9451 | 66.1135 | 5.4053

## A2-C6
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38947.6382 | 1 | 0 | 38947.6382 | 1 | 0 |  | -79.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6403 | 1 | 0 | 38947.6404 | 1 | 0 |  | 105.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6425 | 1 | 0 | 38947.6425 | 1 | 0 |  | 290.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6446 | 1 | 0 | 38947.6446 | 1 | 0 |  | 475 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6468 | 1 | 0 | 38947.6468 | 1 | 0 |  | 660 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6489 | 1 | 0 | 38947.6489 | 1 | 0 |  | 844.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.651 | 2 | 0 | 38947.6511 | 2 | 0 |  | 1029.5 | 1148.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38947.6532 | 76 | 0 | 38947.6532 | 3 | 0 |  | 1214 | 1333 | 4.6398 | 0 | 0.18315 | 0 | 0.046398 | 0 | 0.0018315 | 0 | 0.046398 | 0.0018315 | 2680.2895 | 70334 | 2680.2431
38947.6553 | 30 | 0 | 38947.6553 | 4 | 0 |  | 1399 | 1518 | 1.8315 | 0 | 0.2442 | 0 | 0.018315 | 0 | 0.002442 | 0 | 0.018315 | 0.002442 | 6943.4 | 52725.5 | 6943.3817
38947.6575 | 98 | 0 | 38947.6575 | 20 | 0 |  | 1583.5 | 1702.5 | 5.9829 | 0 | 1.221 | 0 | 0.059829 | 0 | 0.01221 | 0 | 0.059829 | 0.01221 | 2056.1429 | 10465.1 | 2056.083
38947.6596 | 3 | 0 | 38947.6596 | 217 | 0 |  | 1768.5 | 1887.5 | 0.18315 | 0 | 13.2479 | 0 | 0.0018315 | 0 | 0.13248 | 0 | 0.0018315 | 0.13248 | 70334 | 873.7419 | 70333.9982

## A2-C5
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38947.6382 | 1 | 0 | 38947.6382 | 1 | 0 |  | -82 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6403 | 1 | 0 | 38947.6403 | 1 | 0 |  | 102.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6425 | 1 | 1 | 38947.6425 | 1 | 0 |  | 287.5 | 406.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38947.6446 | 1 | 0 | 38947.6446 | 1 | 0 |  | 472.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6467 | 1 | 0 | 38947.6467 | 1 | 0 |  | 657 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6489 | 1 | 0 | 38947.6489 | 1 | 0 |  | 842 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.651 | 3 | 0 | 38947.651 | 3 | 0 |  | 1026.5 | 1145.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6531 | 93 | 0 | 38947.6532 | 3 | 0 |  | 1211.5 | 1330.5 | 5.6777 | 0 | 0.18315 | 0 | 0.056777 | 0 | 0.0018315 | 0 | 0.056777 | 0.0018315 | 2172.0645 | 70334 | 2172.0077
38947.6553 | 25 | 0 | 38947.6553 | 3 | 0 |  | 1396.5 | 1515.5 | 1.5263 | 0 | 0.18315 | 0 | 0.015263 | 0 | 0.0018315 | 0 | 0.015263 | 0.0018315 | 8352.08 | 70334 | 8352.0647
38947.6574 | 75 | 0 | 38947.6574 | 14 | 0 |  | 1581 | 1700 | 4.5788 | 0 | 0.8547 | 0 | 0.045788 | 0 | 0.008547 | 0 | 0.045788 | 0.008547 | 2717.36 | 14993 | 2717.3142
38947.6596 | 3 | 0 | 38947.6596 | 211 | 0 |  | 1765.5 | 1884.5 | 0.18315 | 0 | 12.8816 | 0 | 0.0018315 | 0 | 0.12882 | 0 | 0.0018315 | 0.12882 | 70334 | 901.4313 | 70333.9982

## A2-B4
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38947.6381 | 1 | 0 | 38947.6382 | 1 | 0 |  | -85 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6403 | 1 | 0 | 38947.6403 | 1 | 0 |  | 100 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6424 | 1 | 0 | 38947.6424 | 1 | 0 |  | 284.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6446 | 1 | 0 | 38947.6446 | 1 | 0 |  | 469.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6467 | 1 | 0 | 38947.6467 | 1 | 0 |  | 654.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6488 | 1 | 0 | 38947.6489 | 1 | 0 |  | 839 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.651 | 3 | 0 | 38947.651 | 39 | 26 |  | 1023.5 | 1142.5 | 0.18315 | 0 | 2.381 | 1.5873 | 0.0018315 | 0 | 0.02381 | 0.015873 | 0.0018315 | 0.0079365 | 70334 | 16154 | 70333.9982
38947.6531 | 13 | 0 | 38947.6531 | 71 | 0 |  | 1208.5 | 1327.5 | 0.79365 | 0 | 4.3346 | 0 | 0.0079365 | 0 | 0.043346 | 0 | 0.0079365 | 0.043346 | 16154 | 2876.0845 | 16153.9921
38947.6553 | 31 | 0 | 38947.6553 | 174 | 24 |  | 1393.5 | 1512.5 | 1.8926 | 0 | 10.6227 | 1.4652 | 0.018926 | 0 | 0.10623 | 0.014652 | 0.018926 | 0.091575 | 6716.1935 | 1308.68 | 6716.1746
38947.6574 | 67 | 0 | 38947.6574 | 125 | 1 |  | 1578 | 1697 | 4.0904 | 0 | 7.6313 | 0.06105 | 0.040904 | 0 | 0.076313 | 0.0006105 | 0.040904 | 0.075702 | 3053.7612 | 1604.0484 | 3053.7203
38947.6595 | 3 | 0 | 38947.6595 | 2 | 0 |  | 1763 | 1882 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982

## A2-B3
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38947.6381 | 1 | 0 | 38947.6381 | 1 | 0 |  | -87.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6402 | 1 | 0 | 38947.6403 | 1 | 0 |  | 97 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6424 | 1 | 0 | 38947.6424 | 1 | 0 |  | 282 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6445 | 1 | 0 | 38947.6445 | 1 | 0 |  | 466.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6467 | 1 | 0 | 38947.6467 | 1 | 0 |  | 651.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6488 | 1 | 0 | 38947.6488 | 1 | 0 |  | 836.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6509 | 78 | 65 | 38947.651 | 29 | 25 |  | 1021 | 1140 | 4.7619 | 3.9683 | 1.7705 | 1.5263 | 0.047619 | 0.039683 | 0.017705 | 0.015263 | 0.0079365 | 0.002442 | 15799.6284 | 54246.3721 | 3025.2232
38947.6531 | 13 | 0 | 38947.6531 | 3 | 0 |  | 1206 | 1325 | 0.79365 | 0 | 0.18315 | 0 | 0.0079365 | 0 | 0.0018315 | 0 | 0.0079365 | 0.0018315 | 16154 | 70334 | 16153.9921
38947.6552 | 131 | 3 | 38947.6552 | 14 | 7 |  | 1390.5 | 1509.5 | 7.9976 | 0.18315 | 0.8547 | 0.42735 | 0.079976 | 0.0018315 | 0.008547 | 0.0042735 | 0.078144 | 0.0042735 | 1548.5663 | 32056.0467 | 65762.1858
38947.6574 | 104 | 0 | 38947.6574 | 6 | 3 |  | 1575.5 | 1694.5 | 6.3492 | 0 | 0.3663 | 0.18315 | 0.063492 | 0 | 0.003663 | 0.0018315 | 0.063492 | 0.0018315 | 1931.75 | 70334 | 1931.6865
38947.6595 | 3 | 0 | 38947.6595 | 40 | 0 |  | 1760 | 1879 | 0.18315 | 0 | 2.442 | 0 | 0.0018315 | 0 | 0.02442 | 0 | 0.0018315 | 0.02442 | 70334 | 5182.55 | 70333.9982

## A1-C6
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38947.6379 | 1 | 0 | 38947.6379 | 1 | 0 |  | -107 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.64 | 1 | 0 | 38947.64 | 1 | 0 |  | 77.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6422 | 1 | 0 | 38947.6422 | 1 | 0 |  | 262.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6443 | 1 | 0 | 38947.6443 | 1 | 0 |  | 447 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6464 | 1 | 0 | 38947.6465 | 1 | 0 |  | 632 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6486 | 1 | 0 | 38947.6486 | 1 | 0 |  | 816.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6507 | 3 | 0 | 38947.6507 | 3 | 0 |  | 1001.5 | 1120.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38947.6529 | 5 | 0 | 38947.6529 | 3 | 0 |  | 1186.5 | 1305.5 | 0.30525 | 0 | 0.18315 | 0 | 0.0030525 | 0 | 0.0018315 | 0 | 0.0030525 | 0.0018315 | 42160.4 | 70334 | 42160.3969
38947.655 | 20 | 1 | 38947.655 | 217 | 0 |  | 1371 | 1490 | 1.221 | 0.06105 | 13.2479 | 0 | 0.01221 | 0.0006105 | 0.13248 | 0 | 0.0116 | 0.13248 | 11082.6533 | 873.7419 | 187717.6629
38947.6571 | 57 | 1 | 38947.6571 | 26 | 0 |  | 1555.5 | 1674.5 | 3.4799 | 0.06105 | 1.5873 | 0 | 0.034799 | 0.0006105 | 0.015873 | 0 | 0.034188 | 0.015873 | 3672.2812 | 8027 | 202973.367
38947.6593 | 2 | 0 | 38947.6593 | 153 | 0 |  | 1740.5 | 1859.5 | 0.1221 | 0 | 9.3407 | 0 | 0.001221 | 0 | 0.093407 | 0 | 0.001221 | 0.093407 | 105551 | 1281.0588 | 105550.9988

## A1-C5
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38947.6378 | 1 | 0 | 38947.6379 | 1 | 0 |  | -110 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.64 | 1 | 0 | 38947.64 | 1 | 0 |  | 74.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6421 | 1 | 0 | 38947.6421 | 1 | 0 |  | 259.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6443 | 2 | 0 | 38947.6443 | 1 | 0 |  | 444.5 | 563.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38947.6464 | 1 | 0 | 38947.6464 | 1 | 0 |  | 629 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6485 | 1 | 0 | 38947.6486 | 1 | 0 |  | 814 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6507 | 3 | 1 | 38947.6507 | 3 | 0 |  | 998.5 | 1117.5 | 0.18315 | 0.06105 | 0.18315 | 0 | 0.0018315 | 0.0006105 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105576.0534 | 70334 | 210602.5679
38947.6528 | 5 | 0 | 38947.6528 | 3 | 1 |  | 1183.5 | 1302.5 | 0.30525 | 0 | 0.18315 | 0.06105 | 0.0030525 | 0 | 0.0018315 | 0.0006105 | 0.0030525 | 0.001221 | 42160.4 | 105551 | 42160.3969
38947.655 | 16 | 1 | 38947.655 | 250 | 1 |  | 1368 | 1487 | 0.9768 | 0.06105 | 15.2625 | 0.06105 | 0.009768 | 0.0006105 | 0.15263 | 0.0006105 | 0.0091575 | 0.15201 | 14105.8163 | 748.2221 | 184891.2552
38947.6571 | 49 | 1 | 38947.6571 | 23 | 1 |  | 1553 | 1672 | 2.9915 | 0.06105 | 1.4042 | 0.06105 | 0.029915 | 0.0006105 | 0.014042 | 0.0006105 | 0.029304 | 0.013431 | 4300.9839 | 9510.1416 | 204155.2887
38947.6592 | 2 | 1 | 38947.6592 | 147 | 0 |  | 1737.5 | 1856.5 | 0.1221 | 0.06105 | 8.9744 | 0 | 0.001221 | 0.0006105 | 0.089744 | 0 | 0.0006105 | 0.089744 | 228161.7322 | 1337.4286 | 196322.8706

## A1-B4
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38947.6378 | 1 | 0 | 38947.6378 | 1 | 0 |  | -113 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.64 | 1 | 0 | 38947.64 | 1 | 0 |  | 72 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6421 | 1 | 0 | 38947.6421 | 1 | 0 |  | 256.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6442 | 1 | 0 | 38947.6442 | 1 | 0 |  | 441.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6464 | 1 | 0 | 38947.6464 | 1 | 0 |  | 626.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6485 | 1 | 0 | 38947.6485 | 1 | 0 |  | 811 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6506 | 3 | 2 | 38947.6507 | 3 | 1 |  | 996 | 1115 | 0.18315 | 0.1221 | 0.18315 | 0.06105 | 0.0018315 | 0.001221 | 0.0018315 | 0.0006105 | 0.0006105 | 0.001221 | 211402.6648 | 105525.9585 | 105301.213
38947.6528 | 7 | 2 | 38947.6528 | 3 | 1 |  | 1180.5 | 1299.5 | 0.42735 | 0.1221 | 0.18315 | 0.06105 | 0.0042735 | 0.001221 | 0.0018315 | 0.0006105 | 0.0030525 | 0.001221 | 42136.3568 | 105626.3387 | 105101.4969
38947.6549 | 13 | 2 | 38947.6549 | 3 | 1 |  | 1365.5 | 1484.5 | 0.79365 | 0.1221 | 0.18315 | 0.06105 | 0.0079365 | 0.001221 | 0.0018315 | 0.0006105 | 0.0067155 | 0.001221 | 19094.373 | 105777.9873 | 104801.9227
38947.6571 | 136 | 2 | 38947.6571 | 37 | 1 |  | 1550 | 1669 | 8.3028 | 0.1221 | 2.2589 | 0.06105 | 0.083028 | 0.001221 | 0.022589 | 0.0006105 | 0.081807 | 0.021978 | 1475.7693 | 5777.5971 | 97070.8746
38947.6592 | 2 | 2 | 38947.6592 | 39 | 1 |  | 1735 | 1854 | 0.1221 | 0.1221 | 2.381 | 0.06105 | 0.001221 | 0.001221 | 0.02381 | 0.0006105 | 0 | 0.023199 | 5760915.3953 | 5457.9449 | 103553.698

## A1-B3
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38947.6378 | 1 | 0 | 38947.6378 | 1 | 0 |  | -115.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6399 | 1 | 0 | 38947.6399 | 1 | 0 |  | 69 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6421 | 1 | 0 | 38947.6421 | 1 | 0 |  | 254 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6442 | 1 | 0 | 38947.6442 | 1 | 0 |  | 438.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6463 | 1 | 0 | 38947.6464 | 1 | 0 |  | 623.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6485 | 1 | 0 | 38947.6485 | 1 | 0 |  | 808.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6506 | 10 | 10 | 38947.6506 | 16 | 15 |  | 993 | 1112 | 0.6105 | 0.6105 | 0.9768 | 0.91575 | 0.006105 | 0.006105 | 0.009768 | 0.0091575 | 0 | 0.0006105 | 44099250.004 | 209694.8674 | 20920.2235
38947.6528 | 5 | 6 | 38947.6528 | 3 | 3 |  | 1178 | 1297 | 0.30525 | 0.3663 | 0.18315 | 0.18315 | 0.0030525 | 0.003663 | 0.0018315 | 0.0018315 | 0.0006105 | 0 | 210801.1469 | 148264878.6857 | 35033.643
38947.6549 | 35 | 7 | 38947.6549 | 4 | 4 |  | 1362.5 | 1481.5 | 2.1368 | 0.42735 | 0.2442 | 0.2442 | 0.021368 | 0.0042735 | 0.002442 | 0.002442 | 0.017094 | 0 | 7421.4526 | 3912997.9825 | 29585.2439
38947.657 | 117 | 6 | 38947.657 | 3 | 3 |  | 1547.5 | 1666.5 | 7.1429 | 0.3663 | 0.18315 | 0.18315 | 0.071429 | 0.003663 | 0.0018315 | 0.0018315 | 0.067766 | 0 | 1798.2085 | 1264751.9881 | 33164.3778
38947.6592 | 4 | 7 | 38947.6592 | 135 | 3 |  | 1732 | 1851 | 0.2442 | 0.42735 | 8.2418 | 0.18315 | 0.002442 | 0.0042735 | 0.082418 | 0.0018315 | 0.0018315 | 0.080586 | 83265.7242 | 1498.5409 | 28150.3405

## A1-A2
Penlight Test 43 |  |  | 2006-08-18 | 15:20 |  |  | Vs = |  | 129 |  | R = | 100
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38947.6378 | 1 | 0 | 38947.6378 | 1 | 0 |  | -118.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6399 | 1 | 0 | 38947.6399 | 1 | 0 |  | 66.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.642 | 1 | 1 | 38947.642 | 1 | 0 |  | 251 | 370 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38947.6442 | 1 | 0 | 38947.6442 | 1 | 0 |  | 436 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6463 | 1 | 0 | 38947.6463 | 1 | 0 |  | 620.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38947.6484 | 1 | 1 | 38947.6485 | 2 | 1 |  | 805.5 | 924.5 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 445851546.04 | 211101.9527 | 211002.0473
38947.6506 | 941 | 908 | 38947.6506 | 918 | 886 |  | 990 | 1109 | 57.4481 | 55.4335 | 56.044 | 54.0904 | 0.57448 | 0.55433 | 0.56044 | 0.5409 | 0.020147 | 0.019536 | 5742.9563 | 7210.9024 | 28.6794
38947.6527 | 1179 | 1122 | 38947.6527 | 1086 | 1102 |  | 1175 | 1294 | 71.978 | 68.4982 | 66.3004 | 67.2772 | 0.71978 | 0.68498 | 0.663 | 0.67277 | 0.034799 | 0.009768 | 682.9256 | 1406.5884 | 15.642
38947.6549 | 937 | 916 | 38947.6549 | 1179 | 1118 |  | 1359.5 | 1478.5 | 57.2039 | 55.9219 | 71.978 | 68.254 | 0.57204 | 0.55922 | 0.71978 | 0.68254 | 0.012821 | 0.037241 | 205.0054 | 165.7459 | 17.7047
38947.657 | 1019 | 920 | 38947.657 | 1194 | 1131 |  | 1544.5 | 1663.5 | 62.21 | 56.1661 | 72.8938 | 69.0476 | 0.6221 | 0.56166 | 0.72894 | 0.69048 | 0.06044 | 0.038462 | 106.2707 | 98.8752 | 9.4041
38947.6591 | 1155 | 1063 | 38947.6592 | 1113 | 1027 |  | 1729.5 | 1848.5 | 70.5128 | 64.8962 | 67.9487 | 62.6984 | 0.70513 | 0.64896 | 0.67949 | 0.62698 | 0.056166 | 0.052503 | 22893.5735 | 1210.4948 | 9.1222

## AvgC-C
Average Conductor to Conductor Resistances
Penlight Test 43 |  |  | 2006-08-18 | 15:20
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-C |  | Penlight Time | C2-C | Penlight Time | C3-C | Penlight Time | C4-C | Penlight Time | C5-C | Penlight Time | C6-C | Penlight Time | C7-C | Penlight Time | Minimums
-101.1667 | 217991.3327 |  | -64.8333 | 217891.3327 | -70.75 | 214491.3327 | -58.75 | 212457.9994 | -49.8333 | 217407.9994 | -45.1667 | 216707.9994 | -8.3333 | 240937.9994 | -101.1667 | 212457.9994
83.5833 | 217991.3327 |  | 120 | 217891.3327 | 113.75 | 214491.3327 | 125.9167 | 212457.9994 | 134.8333 | 217407.9994 | 139.5833 | 216707.9994 | 176.5 | 240937.9994 | 83.5833 | 212457.9994
268.3333 | 217958.0153 |  | 304.75 | 217824.6978 | 298.75 | 214491.3327 | 310.75 | 212457.9994 | 319.6667 | 217374.6819 | 324.4167 | 216707.9994 | 361.1667 | 240937.9994 | 268.3333 | 212457.9994
453.1667 | 200382.8326 |  | 489.5833 | 217858.0127 | 483.4167 | 195238.166 | 495.5833 | 212457.9994 | 504.5833 | 199799.4993 | 509.1667 | 216707.9994 | 546 | 221651.5126 | 453.1667 | 195238.166
638 | 217991.3327 |  | 674.3333 | 217891.3327 | 668.3333 | 214491.3327 | 680.5 | 212457.9994 | 689.25 | 217407.9994 | 694 | 216707.9994 | 730.9167 | 240937.9994 | 638 | 212457.9994
822.75 | 217958.0074 |  | 859.1667 | 175968.6149 | 853.0833 | 196882.8326 | 865.25 | 177240.9992 | 874.1667 | 138001.4989 | 878.6667 | 155259.999 | 915.5833 | 157975.6067 | 822.75 | 138001.4989
1007.5 | 81849.8911 |  | 1043.8333 | 41545.6278 | 1037.8333 | 49041.9342 | 1050 | 79724.6173 | 1058.8333 | 89394.0929 | 1063.4167 | 75104.0815 | 1100.4167 | 68920.9489 | 1007.5 | 41545.6278
1192.3333 | 51397.3734 |  | 1228.6667 | 6196.2966 | 1222.75 | 56517.0491 | 1234.75 | 73386.747 | 1243.6667 | 62216.233 | 1248.3333 | 43120.386 | 1285.1667 | 53216.485 | 1192.3333 | 6196.2966
1377 | 98487.7424 |  | 1413.4167 | 14642.3781 | 1407.3333 | 62664.3869 | 1419.5833 | 62959.5982 | 1428.3333 | 64748.0963 | 1433.0833 | 69446.6506 | 1469.9167 | 72722.0692 | 1377 | 14642.3781
1561.75 | 93746.1844 |  | 1598.1667 | 3570.9117 | 1592.1667 | 42749.9621 | 1604.25 | 28479.7349 | 1613.1667 | 46495.2386 | 1617.75 | 47938.3792 | 1654.5833 | 10201.299 | 1561.75 | 3570.9117
1746.5833 | 86249.9492 |  | 1783 | 46894.3191 | 1776.8333 | 57246.1334 | 1789.0833 | 47255.8344 | 1797.8333 | 58428.9998 | 1802.5 | 53170.6116 | 1839.5 | 35285.7252 | 1746.5833 | 35285.7252
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 43 |  |  | 2006-08-18 | 15:20
EPR&PE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | C8-G | Penlight Time | C9-G | Penlight Time | C10-G | Penlight Time | C11-G | Penlight Time | C12-G | Penlight Time | Minimums
-112.8 | 211202 |  | -90.5 | 211202 | -62.3889 | 221029.1111 | -46.9444 | 221969.5556 | -32.5556 | 223518 | -23.8333 | 221684.6667 | 0.3 | 236158 | 5.9 | 233150.8 | 18.1667 | 69688802.0489 | 21.2222 | 251804.6667 | 39 | 243078 | 41.3 | 246838 | -20.2611 | 211202
71.9 | 211202 |  | 94.3 | 211202 | 122.2222 | 62888304.2711 | 137.7778 | 221969.5556 | 152.1111 | 74923811.8267 | 160.8889 | 58738062.0489 | 185 | 236158 | 190.7 | 131702758.888 | 202.9444 | 251026.8889 | 206 | 251804.6667 | 223.6 | 243078 | 226 | 246838 | 164.4537 | 211202
256.7 | 89381531.208 |  | 279.1 | 89381531.208 | 307.1111 | 221029.1111 | 322.6111 | 221969.5556 | 336.9444 | 223518 | 345.7222 | 221684.6667 | 369.8 | 236158 | 375.4 | 233150.8 | 387.6667 | 251026.8889 | 390.7222 | 251804.6667 | 408.5 | 243078 | 410.7 | 246838 | 349.2481 | 221029.1111
441.5 | 190071.8 |  | 463.9 | 211202 | 491.8333 | 208193.6667 | 507.4444 | 221969.5556 | 521.8333 | 211779 | 530.5 | 221684.6667 | 554.6 | 236158 | 560.2 | 233150.8 | 572.4444 | 251026.8889 | 575.6667 | 251804.6667 | 593.4 | 126534390.888 | 595.5 | 246838 | 534.0685 | 190071.8
626.3 | 211202 |  | 648.7 | 211202 | 676.7222 | 221029.1111 | 692.2778 | 221969.5556 | 706.5556 | 223518 | 715.2778 | 221684.6667 | 739.5 | 211024.2 | 745 | 233150.8 | 757.3333 | 251026.8889 | 760.3889 | 251804.6667 | 778 | 243078 | 780.3 | 246838 | 718.863 | 211024.2
811.1 | 89339270.808 |  | 833.5 | 211181.9905 | 861.5 | 209290.1111 | 877.0556 | 186752.5556 | 891.3889 | 136464.7222 | 899.9444 | 131135.3148 | 924.2 | 91544.0775 | 929.8 | 76284.4601 | 942.0556 | 68264.4019 | 945.1111 | 29478.1181 | 962.9 | 16.1761 | 965 | 15.0897 | 903.6296 | 15.0897
995.8 | 8898461.1357 |  | 1018.1 | 53845.9062 | 1046.2778 | 89293.5266 | 1061.7778 | 75865.9584 | 1076.0556 | 65871.6605 | 1084.7222 | 79527.9444 | 1109 | 32.7757 | 1114.5 | 26.4243 | 1126.7222 | 9.0011 | 1129.7778 | 19.1741 | 1147.6 | 11.5355 | 1149.8 | 17.2773 | 1088.3444 | 9.0011
1180.7 | 67588.2458 |  | 1203 | 7713.3885 | 1231.1111 | 16539670.2243 | 1246.5556 | 74262.2322 | 1260.9444 | 66692.6556 | 1269.6667 | 50192.0668 | 1293.8 | 20.2052 | 1299.3 | 32.1958 | 1311.5556 | 11.4816 | 1314.6667 | 14.2681 | 1332.5 | 23.8141 | 1334.6 | 18.3348 | 1273.2 | 11.4816
1365.3 | 10381.8601 |  | 1387.8 | 4745.1972 | 1415.7778 | 491990.281 | 1431.3333 | 70191.926 | 1445.6111 | 47604.6154 | 1454.3333 | 60318.1053 | 1478.6 | 11.3011 | 1484.1 | 28.9673 | 1496.3333 | 10.826 | 1499.4444 | 7.4534 | 1517 | 41.2956 | 1519.3 | 38.1275 | 1457.9111 | 7.4534
1550.1 | 2270.7027 |  | 1572.5 | 1971.5779 | 1600.5556 | 189243.7536 | 1616.0556 | 983.1446 | 1630.3889 | 24887.451 | 1639.0556 | 14818.5684 | 1663.2 | 23.7875 | 1668.9 | 33207.7753 | 1681.1111 | 7.6614 | 1684.1667 | 11.7126 | 1701.9 | 58.4223 | 1704 | 29.1355 | 1642.6611 | 7.6614
1734.9 | 1240157.485 |  | 1757.3 | 56509.299 | 1785.2778 | 20002.8376 | 1800.8889 | 46918.2962 | 1815.1111 | 440.8025 | 1823.8333 | 420.1243 | 1848 | 31.3471 | 1853.7 | 84748.2 | 1865.9444 | 9.0812 | 1869 | 10.3325 | 1886.6 | 38.7632 | 1889 | 57.6854 | 1827.463 | 9.0812
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -119 | 19 | 26.8 | 21.8 | 26.6 | 29.1 | 24.2 | 24 | 27.9
1 | -118 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 27.9
2 | -117 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 27.9
3 | -116 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
4 | -115 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
5 | -114 | 19 | 26.8 | 21.8 | 26.6 | 29.1 | 24.2 | 24 | 28
6 | -113 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 27.9
7 | -112 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 27.9
8 | -111 | 19 | 26.9 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 27.8
9 | -110 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 27.8
10 | -109 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 27.9
11 | -108 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 27.9
12 | -107 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
13 | -106 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
14 | -105 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
15 | -104 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
16 | -103 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
17 | -102 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
18 | -101 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
19 | -100 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
20 | -99 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
21 | -98 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
22 | -97 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
23 | -96 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
24 | -95 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
25 | -94 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
26 | -93 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
27 | -92 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
28 | -91 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
29 | -90 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
30 | -89 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
31 | -88 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
32 | -87 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
33 | -86 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
34 | -85 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
35 | -84 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
36 | -83 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
37 | -82 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
38 | -81 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
39 | -80 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
40 | -79 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
41 | -78 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
42 | -77 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
43 | -76 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
44 | -75 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
45 | -74 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
46 | -73 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
47 | -72 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28
48 | -71 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
49 | -70 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
50 | -69 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
51 | -68 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
52 | -67 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
53 | -66 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
54 | -65 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
55 | -64 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.2
56 | -63 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
57 | -62 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
58 | -61 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
59 | -60 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
60 | -59 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
61 | -58 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
62 | -57 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
63 | -56 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28
64 | -55 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
65 | -54 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28
66 | -53 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
67 | -52 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
68 | -51 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
69 | -50 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
70 | -49 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
71 | -48 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
72 | -47 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
73 | -46 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.2
74 | -45 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.2
75 | -44 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.2
76 | -43 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
77 | -42 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
78 | -41 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
79 | -40 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
80 | -39 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.2
81 | -38 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.1
82 | -37 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
83 | -36 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.2
84 | -35 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
85 | -34 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
86 | -33 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
87 | -32 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
88 | -31 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
89 | -30 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.2
90 | -29 | 19 | 26.8 | 21.7 | 26.6 | 29.2 | 24.2 | 24 | 28.2
91 | -28 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
92 | -27 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
93 | -26 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
94 | -25 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
95 | -24 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
96 | -23 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.2
97 | -22 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.2
98 | -21 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.2
99 | -20 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.2
100 | -19 | 19 | 26.8 | 21.6 | 26.6 | 29.1 | 24.2 | 24 | 28.1
101 | -18 | 19 | 26.8 | 21.6 | 26.6 | 29.2 | 24.2 | 24 | 28.1
102 | -17 | 19 | 26.8 | 21.6 | 26.6 | 29.1 | 24.2 | 24 | 28.1
103 | -16 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
104 | -15 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
105 | -14 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
106 | -13 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
107 | -12 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
108 | -11 | 19 | 26.8 | 21.7 | 26.6 | 29.1 | 24.2 | 24 | 28.1
109 | -10 | 19 | 26.8 | 21.7 | 26.5 | 29.1 | 24.2 | 24 | 28.2
110 | -9 | 19 | 26.8 | 21.7 | 26.5 | 29.1 | 24.2 | 24 | 28.2
111 | -8 | 19 | 26.8 | 21.7 | 26.5 | 29.1 | 24.2 | 24 | 28.2
112 | -7 | 19 | 26.8 | 21.7 | 26.5 | 29.1 | 24.2 | 24 | 28.2
113 | -6 | 19 | 26.8 | 21.7 | 26.5 | 29.1 | 24.2 | 24 | 28.2
114 | -5 | 19 | 26.8 | 21.7 | 26.5 | 29.1 | 24.2 | 24 | 28.2
115 | -4 | 19 | 26.9 | 21.5 | 26.6 | 29.2 | 24.2 | 24 | 28.1
116 | -3 | 19 | 27.7 | 20 | 27.1 | 30.6 | 24.3 | 23.9 | 28
117 | -2 | 19 | 28 | 19.5 | 27.3 | 31.1 | 24.4 | 23.9 | 27.9
118 | -1 | 19.2 | 28 | 19.4 | 27.3 | 31.2 | 24.4 | 23.9 | 27.9
119 | 0 | 20 | 28 | 19.4 | 27.3 | 31.2 | 24.4 | 23.9 | 27.9
120 | 1 | 21.4 | 28 | 19.5 | 27.3 | 31.1 | 24.4 | 23.9 | 27.9
121 | 2 | 23.2 | 27.9 | 19.5 | 27.3 | 31.1 | 24.4 | 24 | 28
122 | 3 | 25.5 | 28 | 19.4 | 27.3 | 31.2 | 24.4 | 24 | 28
123 | 4 | 28.2 | 28 | 19.4 | 27.3 | 31.2 | 24.5 | 24 | 28
124 | 5 | 31.2 | 28 | 19.4 | 27.3 | 31.2 | 24.5 | 24.1 | 28
125 | 6 | 34.5 | 28 | 19.4 | 27.3 | 31.2 | 24.6 | 24.1 | 28.1
126 | 7 | 38 | 28 | 19.4 | 27.3 | 31.2 | 24.6 | 24.2 | 28.2
127 | 8 | 41.8 | 28 | 19.5 | 27.3 | 31.2 | 24.7 | 24.3 | 28.2
128 | 9 | 45.8 | 28 | 19.5 | 27.3 | 31.2 | 24.8 | 24.4 | 28.3
129 | 10 | 49.9 | 28.1 | 19.4 | 27.3 | 31.3 | 24.9 | 24.5 | 28.3
130 | 11 | 54.3 | 28.1 | 19.4 | 27.3 | 31.3 | 24.9 | 24.6 | 28.3
131 | 12 | 58.7 | 28.2 | 19.4 | 27.3 | 31.3 | 25 | 24.7 | 28.3
132 | 13 | 63.4 | 28.2 | 19.4 | 27.3 | 31.4 | 25.1 | 24.8 | 28.3
133 | 14 | 68.1 | 28.2 | 19.4 | 27.3 | 31.4 | 25.3 | 24.9 | 28.4
134 | 15 | 73 | 28.3 | 19.5 | 27.3 | 31.4 | 25.4 | 25.1 | 28.5
135 | 16 | 77.9 | 28.3 | 19.5 | 27.3 | 31.4 | 25.6 | 25.3 | 28.6
136 | 17 | 82.9 | 28.4 | 19.6 | 27.3 | 31.5 | 25.7 | 25.4 | 28.7
137 | 18 | 88.1 | 28.4 | 19.6 | 27.3 | 31.6 | 25.9 | 25.6 | 28.8
138 | 19 | 93.3 | 28.5 | 19.5 | 27.3 | 31.7 | 26.1 | 25.8 | 28.9
139 | 20 | 98.6 | 28.6 | 19.5 | 27.3 | 31.8 | 26.3 | 26 | 29
140 | 21 | 103.9 | 28.7 | 19.5 | 27.4 | 31.9 | 26.5 | 26.2 | 29.1
141 | 22 | 109.4 | 28.8 | 19.5 | 27.4 | 32 | 26.8 | 26.5 | 29.2
142 | 23 | 114.8 | 28.9 | 19.6 | 27.4 | 32 | 27 | 26.7 | 29.5
143 | 24 | 120.3 | 29 | 19.6 | 27.4 | 32.1 | 27.3 | 27 | 29.6
144 | 25 | 125.7 | 29.1 | 19.6 | 27.4 | 32.3 | 27.5 | 27.3 | 29.7
145 | 26 | 131.2 | 29.2 | 19.7 | 27.5 | 32.3 | 27.8 | 27.5 | 29.8
146 | 27 | 136.8 | 29.4 | 19.7 | 27.5 | 32.5 | 28.1 | 27.9 | 30.1
147 | 28 | 142.4 | 29.5 | 19.8 | 27.5 | 32.6 | 28.4 | 28.2 | 30.3
148 | 29 | 148 | 29.7 | 19.8 | 27.5 | 32.7 | 28.8 | 28.5 | 30.5
149 | 30 | 153.6 | 29.8 | 19.8 | 27.6 | 32.9 | 29.1 | 28.9 | 30.7
150 | 31 | 159.2 | 30 | 19.9 | 27.6 | 33 | 29.5 | 29.2 | 31
151 | 32 | 164.8 | 30.2 | 19.9 | 27.7 | 33.2 | 29.8 | 29.6 | 31.2
152 | 33 | 170.5 | 30.4 | 19.9 | 27.7 | 33.4 | 30.2 | 30 | 31.5
153 | 34 | 176.2 | 30.6 | 20 | 27.8 | 33.6 | 30.7 | 30.4 | 31.8
154 | 35 | 181.8 | 30.8 | 20.1 | 27.8 | 33.8 | 31.1 | 30.8 | 32.1
155 | 36 | 187.4 | 31 | 20.1 | 27.9 | 34 | 31.6 | 31.3 | 32.5
156 | 37 | 192.9 | 31.3 | 20.2 | 28 | 34.2 | 32.1 | 31.8 | 32.8
157 | 38 | 198.5 | 31.5 | 20.3 | 28.1 | 34.4 | 32.6 | 32.3 | 33.2
158 | 39 | 204.1 | 31.8 | 20.4 | 28.1 | 34.7 | 33.1 | 32.8 | 33.5
159 | 40 | 209.8 | 32 | 20.5 | 28.2 | 34.9 | 33.6 | 33.3 | 33.9
160 | 41 | 215.4 | 32.3 | 20.5 | 28.3 | 35.2 | 34.1 | 33.9 | 34.3
161 | 42 | 221 | 32.6 | 20.7 | 28.4 | 35.4 | 34.7 | 34.4 | 34.7
162 | 43 | 226.6 | 32.9 | 20.7 | 28.5 | 35.7 | 35.2 | 35 | 35.2
163 | 44 | 232.2 | 33.2 | 20.8 | 28.6 | 36 | 35.8 | 35.6 | 35.6
164 | 45 | 237.7 | 33.5 | 21 | 28.7 | 36.3 | 36.4 | 36.2 | 36.1
165 | 46 | 243.2 | 33.9 | 21.1 | 28.8 | 36.6 | 37.1 | 36.9 | 36.6
166 | 47 | 248.6 | 34.3 | 21.3 | 28.9 | 37 | 37.7 | 37.6 | 37.2
167 | 48 | 254.2 | 34.6 | 21.4 | 29.1 | 37.3 | 38.4 | 38.2 | 37.7
168 | 49 | 259.7 | 35 | 21.5 | 29.2 | 37.7 | 39.1 | 38.9 | 38.3
169 | 50 | 265.2 | 35.5 | 21.7 | 29.4 | 38 | 39.8 | 39.6 | 38.9
170 | 51 | 270.9 | 35.9 | 21.8 | 29.5 | 38.4 | 40.5 | 40.4 | 39.5
171 | 52 | 276.3 | 36.3 | 22 | 29.6 | 38.8 | 41.2 | 41.2 | 40.2
172 | 53 | 281.7 | 36.7 | 22.2 | 29.8 | 39.2 | 42 | 42.1 | 40.9
173 | 54 | 287 | 37.2 | 22.4 | 30 | 39.6 | 42.8 | 42.9 | 41.6
174 | 55 | 292.2 | 37.7 | 22.6 | 30.2 | 40 | 43.6 | 43.8 | 42.3
175 | 56 | 297.5 | 38.1 | 22.8 | 30.3 | 40.5 | 44.4 | 44.7 | 43
176 | 57 | 302.7 | 38.6 | 23.1 | 30.5 | 40.9 | 45.3 | 45.6 | 43.8
177 | 58 | 307.9 | 39.1 | 23.3 | 30.7 | 41.3 | 46.2 | 46.4 | 44.6
178 | 59 | 313 | 39.7 | 23.5 | 30.9 | 41.8 | 47.2 | 47.3 | 45.5
179 | 60 | 318.1 | 40.2 | 23.8 | 31.2 | 42.3 | 48.1 | 48.2 | 46.3
180 | 61 | 323.2 | 40.8 | 24 | 31.4 | 42.9 | 49 | 49.2 | 47.2
181 | 62 | 328.4 | 41.4 | 24.2 | 31.6 | 43.4 | 49.9 | 50.1 | 48.1
182 | 63 | 333.5 | 42 | 24.4 | 31.9 | 43.9 | 50.9 | 51.1 | 49.1
183 | 64 | 338.4 | 42.6 | 24.7 | 32.2 | 44.5 | 52 | 52.1 | 50
184 | 65 | 343.5 | 43.2 | 24.9 | 32.5 | 45 | 52.9 | 53.2 | 51
185 | 66 | 348.6 | 43.8 | 25.3 | 32.7 | 45.5 | 53.9 | 54.3 | 52
186 | 67 | 353.7 | 44.5 | 25.5 | 33 | 46.1 | 54.9 | 55.4 | 53.1
187 | 68 | 358.7 | 45.2 | 25.8 | 33.3 | 46.7 | 56 | 56.6 | 54.2
188 | 69 | 363.6 | 45.9 | 26.1 | 33.7 | 47.3 | 57 | 57.7 | 55.3
189 | 70 | 368.5 | 46.6 | 26.4 | 34 | 47.9 | 58.2 | 58.9 | 56.4
190 | 71 | 373.3 | 47.3 | 26.7 | 34.3 | 48.6 | 59.3 | 60.2 | 57.6
191 | 72 | 377.9 | 48.1 | 27.1 | 34.7 | 49.2 | 60.6 | 61.4 | 58.8
192 | 73 | 382.4 | 48.8 | 27.5 | 35 | 49.8 | 61.8 | 62.7 | 60.1
193 | 74 | 386.9 | 49.6 | 27.8 | 35.4 | 50.5 | 63.1 | 63.9 | 61.4
194 | 75 | 391.6 | 50.4 | 28.2 | 35.7 | 51.2 | 64.5 | 65.2 | 62.7
195 | 76 | 396.4 | 51.3 | 28.5 | 36.1 | 52 | 65.8 | 66.3 | 64.1
196 | 77 | 401 | 52.2 | 28.9 | 36.5 | 52.7 | 67 | 67.6 | 65.4
197 | 78 | 405.4 | 53.1 | 29.3 | 36.9 | 53.5 | 68.2 | 68.8 | 66.9
198 | 79 | 410 | 54.1 | 29.7 | 37.4 | 54.2 | 69.6 | 70.1 | 68.3
199 | 80 | 414.8 | 55 | 30.1 | 37.8 | 55 | 71 | 71.6 | 69.8
200 | 81 | 419.4 | 56 | 30.5 | 38.2 | 55.9 | 72.3 | 73.1 | 71.3
201 | 82 | 423.7 | 57 | 31 | 38.7 | 56.7 | 73.5 | 74.4 | 72.9
202 | 83 | 427.9 | 58.1 | 31.4 | 39.1 | 57.5 | 74.9 | 75.8 | 74.4
203 | 84 | 432.3 | 59.2 | 31.8 | 39.6 | 58.4 | 76.5 | 77.2 | 76
204 | 85 | 436.7 | 60.2 | 32.4 | 40 | 59.2 | 77.9 | 78.6 | 77.7
205 | 86 | 441 | 61.3 | 32.9 | 40.5 | 60.1 | 79.6 | 80.1 | 79.4
206 | 87 | 444.9 | 62.5 | 33.3 | 41 | 61 | 81.1 | 81.5 | 81.1
207 | 88 | 448.9 | 63.6 | 33.8 | 41.5 | 61.9 | 82.6 | 82.8 | 82.9
208 | 89 | 453.1 | 64.8 | 34.3 | 42 | 62.8 | 84.2 | 84.3 | 84.7
209 | 90 | 457.2 | 66 | 34.8 | 42.5 | 63.7 | 85.6 | 85.7 | 86.5
210 | 91 | 461.2 | 67.1 | 35.5 | 43 | 64.7 | 87.1 | 87.1 | 88.3
211 | 92 | 465.2 | 68.4 | 36 | 43.6 | 65.6 | 88.6 | 88.7 | 90.2
212 | 93 | 469.1 | 69.7 | 36.5 | 44.2 | 66.6 | 90.3 | 90.2 | 92.1
213 | 94 | 472.9 | 71 | 37.1 | 44.8 | 67.6 | 91.9 | 91.6 | 94.1
214 | 95 | 476.8 | 72 | 38.1 | 45.2 | 68.1 | 93.6 | 92.9 | 96.1
215 | 96 | 480.8 | 73.4 | 38.6 | 45.8 | 69.2 | 95.1 | 94.4 | 98.1
216 | 97 | 484.4 | 74.8 | 39.2 | 46.4 | 70.3 | 96.9 | 95.7 | 100.2
217 | 98 | 487.8 | 76.2 | 39.8 | 47 | 71.3 | 98.5 | 97.2 | 102.2
218 | 99 | 490.7 | 77.6 | 40.4 | 47.6 | 72.2 | 100.2 | 98.9 | 104.3
219 | 100 | 493.5 | 79.1 | 41 | 48.2 | 73.3 | 101.9 | 100.3 | 106.4
220 | 101 | 496.1 | 80.6 | 41.7 | 48.8 | 74.3 | 103.4 | 102 | 108.5
221 | 102 | 498.5 | 82.1 | 42.4 | 49.4 | 75.2 | 105 | 103.6 | 110.6
222 | 103 | 500.6 | 83.6 | 43.1 | 50 | 76.2 | 106.6 | 105.3 | 112.8
223 | 104 | 502.8 | 85.2 | 43.8 | 50.6 | 77.2 | 108.2 | 106.8 | 114.9
224 | 105 | 504.8 | 86.8 | 44.4 | 51.3 | 78.3 | 109.8 | 108.4 | 117.1
225 | 106 | 506.8 | 88.4 | 44.9 | 52.1 | 79.5 | 111.3 | 110 | 119.3
226 | 107 | 508.9 | 90.1 | 45.5 | 52.8 | 80.6 | 112.8 | 111.4 | 121.5
227 | 108 | 510.9 | 91.7 | 46.2 | 53.5 | 81.7 | 114.3 | 113 | 123.7
228 | 109 | 512.7 | 93.4 | 46.9 | 54.2 | 82.7 | 115.9 | 114.7 | 125.9
229 | 110 | 514.4 | 95 | 47.5 | 54.8 | 83.8 | 117.6 | 116.4 | 128.2
230 | 111 | 515.9 | 96.7 | 48.3 | 55.5 | 84.7 | 119.1 | 117.7 | 130.5
231 | 112 | 517.3 | 98.3 | 49.1 | 56.2 | 85.8 | 120.4 | 118.8 | 132.7
232 | 113 | 518.3 | 100 | 49.8 | 56.8 | 86.8 | 121.9 | 120.1 | 135
233 | 114 | 519.5 | 101.7 | 50.7 | 57.4 | 87.7 | 123.3 | 121.3 | 137.2
234 | 115 | 520.4 | 103.4 | 51.5 | 58.1 | 88.6 | 124.4 | 122.9 | 139.4
235 | 116 | 521.1 | 105.1 | 52.3 | 58.7 | 89.6 | 125.8 | 124.2 | 141.6
236 | 117 | 521.5 | 106.9 | 53.1 | 59.4 | 90.5 | 127 | 125.2 | 143.7
237 | 118 | 521.7 | 108.7 | 53.9 | 60.1 | 91.6 | 128.3 | 126.6 | 145.9
238 | 119 | 521.6 | 110.6 | 54.5 | 60.8 | 92.8 | 129.7 | 127.7 | 148.1
239 | 120 | 521.3 | 112.4 | 55.1 | 61.6 | 94 | 131 | 128.7 | 150.3
240 | 121 | 521.2 | 114.1 | 55.8 | 62.3 | 95.1 | 132 | 130.1 | 152.5
241 | 122 | 521.1 | 115.8 | 56.5 | 63.1 | 96.2 | 133.1 | 131.2 | 154.6
242 | 123 | 520.8 | 117.4 | 57.2 | 63.8 | 97.4 | 134.1 | 132.1 | 156.7
243 | 124 | 520.3 | 118.9 | 57.9 | 64.6 | 98.4 | 135.1 | 132.7 | 158.8
244 | 125 | 519.9 | 120.2 | 58.7 | 65.4 | 99.5 | 136.2 | 133.4 | 160.9
245 | 126 | 519.5 | 121.4 | 59.4 | 66.2 | 100.5 | 137.5 | 134 | 163
246 | 127 | 519 | 122.6 | 60.1 | 66.9 | 101.5 | 138.5 | 134.8 | 165.1
247 | 128 | 518.7 | 123.6 | 61 | 67.7 | 102.5 | 139.4 | 135.9 | 167.2
248 | 129 | 518.3 | 124.6 | 61.7 | 68.6 | 103.5 | 140.5 | 137.1 | 169.3
249 | 130 | 518 | 125.6 | 62.4 | 69.4 | 104.5 | 141.5 | 138.1 | 171.4
250 | 131 | 517.9 | 126.5 | 63.2 | 70.2 | 105.5 | 142.8 | 139.2 | 173.4
251 | 132 | 517.8 | 127.3 | 64 | 71 | 106.5 | 143.4 | 140 | 175.4
252 | 133 | 517.9 | 128 | 64.8 | 71.8 | 107.4 | 144.1 | 140.8 | 177.5
253 | 134 | 518.2 | 128.7 | 65.6 | 72.7 | 108.4 | 144.9 | 141.9 | 179.5
254 | 135 | 518.3 | 129.3 | 66.4 | 73.5 | 109.3 | 145.8 | 142.8 | 181.5
255 | 136 | 518.4 | 129.9 | 67.1 | 74.3 | 110.3 | 146.7 | 143.5 | 183.6
256 | 137 | 518.7 | 130.5 | 68 | 75.1 | 111.1 | 147.5 | 144.4 | 185.6
257 | 138 | 519 | 131.1 | 68.8 | 76 | 112 | 148 | 145.3 | 187.6
258 | 139 | 519.1 | 131.7 | 69.7 | 76.8 | 112.8 | 148.5 | 146.3 | 189.6
259 | 140 | 519.3 | 132.2 | 70.5 | 77.5 | 113.5 | 149.1 | 147.1 | 191.5
260 | 141 | 519.5 | 132.8 | 71.3 | 78.3 | 114.1 | 150.1 | 147.9 | 193.4
261 | 142 | 519.7 | 133.3 | 72.1 | 79.2 | 114.7 | 150.8 | 148.6 | 195.3
262 | 143 | 519.9 | 133.8 | 72.9 | 80 | 115.2 | 151.4 | 149.2 | 197.2
263 | 144 | 519.9 | 134.2 | 73.7 | 80.7 | 115.3 | 152.3 | 150 | 199
264 | 145 | 519.9 | 134.4 | 74.5 | 81.5 | 115.5 | 153.2 | 150.7 | 201
265 | 146 | 520.2 | 134.4 | 75.3 | 82.3 | 115.7 | 154.2 | 151.6 | 202.8
266 | 147 | 520.4 | 134.6 | 76.1 | 83.1 | 116 | 154.8 | 152.4 | 204.6
267 | 148 | 520.5 | 134.8 | 76.9 | 83.9 | 116.2 | 155.4 | 153.2 | 206.4
268 | 149 | 520.5 | 134.9 | 77.7 | 84.7 | 116.5 | 156.2 | 153.7 | 208.2
269 | 150 | 520.5 | 135.1 | 78.5 | 85.5 | 116.8 | 157.1 | 154.4 | 210
270 | 151 | 520.7 | 135.2 | 79.4 | 86.3 | 117 | 157.7 | 155.2 | 211.9
271 | 152 | 520.9 | 135.3 | 80.2 | 87.1 | 117.3 | 158.6 | 156.3 | 213.7
272 | 153 | 521.1 | 135.4 | 81 | 87.9 | 117.6 | 159.6 | 157.2 | 215.6
273 | 154 | 521.3 | 135.5 | 81.9 | 88.6 | 117.9 | 160.2 | 158.3 | 217.5
274 | 155 | 521.7 | 135.6 | 82.6 | 89.4 | 118.3 | 161.2 | 159.2 | 219.2
275 | 156 | 522 | 135.5 | 83.5 | 90.2 | 118.8 | 162.2 | 160.1 | 221
276 | 157 | 522 | 134.9 | 84.3 | 91 | 119.2 | 163.2 | 161.2 | 222.8
277 | 158 | 522.2 | 133.9 | 85.1 | 91.8 | 119.6 | 164.1 | 162.6 | 224.5
278 | 159 | 522.2 | 133.1 | 85.9 | 92.6 | 120 | 165.2 | 163.4 | 226.2
279 | 160 | 522.1 | 132.5 | 86.8 | 93.5 | 120.3 | 166 | 164.2 | 227.9
280 | 161 | 522.1 | 132.2 | 87.7 | 94.3 | 120.6 | 167.1 | 164.9 | 229.6
281 | 162 | 522.2 | 132.2 | 88.6 | 95.1 | 120.8 | 167.5 | 165.2 | 231.4
282 | 163 | 522.2 | 132.6 | 89.4 | 96 | 121 | 168.1 | 165.8 | 233.1
283 | 164 | 522.1 | 133.3 | 90.4 | 96.9 | 121.3 | 168.8 | 166.6 | 234.7
284 | 165 | 522.3 | 134.4 | 91.3 | 97.8 | 121.7 | 169.5 | 167.5 | 236.4
285 | 166 | 522.5 | 135.7 | 92.2 | 98.7 | 122.4 | 170.3 | 168.2 | 238.1
286 | 167 | 522.6 | 137.3 | 93.1 | 99.7 | 123.1 | 171.1 | 168.5 | 239.7
287 | 168 | 522.6 | 139.1 | 94.1 | 100.6 | 124.1 | 172.2 | 168.9 | 241.3
288 | 169 | 522.6 | 141.1 | 95.1 | 101.6 | 125.5 | 173 | 169.7 | 242.9
289 | 170 | 522.5 | 143.2 | 96.1 | 102.6 | 127.2 | 173.9 | 170.6 | 244.4
290 | 171 | 522.4 | 145.6 | 97 | 103.6 | 129.2 | 174.6 | 171.4 | 246
291 | 172 | 522.4 | 148.2 | 98 | 104.6 | 131.2 | 175.4 | 171.7 | 247.6
292 | 173 | 522.3 | 151.1 | 99 | 105.6 | 133.3 | 176.3 | 171.7 | 249.1
293 | 174 | 522.3 | 154.2 | 100 | 106.6 | 135.1 | 176.7 | 172.2 | 250.6
294 | 175 | 522.6 | 158.1 | 101 | 107.7 | 136.9 | 177.6 | 172.7 | 252
295 | 176 | 522.7 | 162.5 | 102 | 108.7 | 138.7 | 178.4 | 173.3 | 253.5
296 | 177 | 522.7 | 166.7 | 103.1 | 109.8 | 140.7 | 179.2 | 173.9 | 254.9
297 | 178 | 522.7 | 170.6 | 104.1 | 110.8 | 142.7 | 180 | 174.4 | 256.3
298 | 179 | 522.5 | 174 | 105 | 111.9 | 144.7 | 181.1 | 175.3 | 257.8
299 | 180 | 522.5 | 177.4 | 106.1 | 112.9 | 146.7 | 181.9 | 176 | 259.2
300 | 181 | 522.6 | 181.2 | 107.1 | 114 | 148.5 | 183 | 176.6 | 260.7
301 | 182 | 522.6 | 184.9 | 108.1 | 115 | 150.4 | 183.7 | 176.8 | 262.2
302 | 183 | 522.7 | 188.2 | 109.2 | 116.1 | 152.3 | 184.5 | 177.4 | 263.6
303 | 184 | 523 | 191.5 | 110.2 | 117.1 | 154.3 | 185.4 | 178.2 | 265
304 | 185 | 523.3 | 194.5 | 111.3 | 118.1 | 156.3 | 186 | 178.7 | 266.3
305 | 186 | 523.5 | 197.4 | 112.4 | 119.2 | 158.3 | 186.5 | 179.3 | 267.7
306 | 187 | 523.7 | 199.9 | 113.5 | 120.2 | 160.2 | 187.1 | 180.3 | 269
307 | 188 | 523.8 | 202.5 | 114.6 | 121.2 | 162.1 | 187.9 | 180.9 | 270.4
308 | 189 | 523.6 | 205 | 115.7 | 122.3 | 164 | 188.5 | 181.9 | 271.7
309 | 190 | 523.5 | 207.1 | 116.8 | 123.3 | 165.9 | 189.1 | 182.7 | 273
310 | 191 | 523.4 | 209.3 | 117.9 | 124.4 | 167.6 | 189.9 | 183 | 274.2
311 | 192 | 523.2 | 211.2 | 119.1 | 125.5 | 169.5 | 190.8 | 183.4 | 275.5
312 | 193 | 523 | 213 | 120.2 | 126.5 | 171 | 191.4 | 183.9 | 276.8
313 | 194 | 522.8 | 214.8 | 121.3 | 127.6 | 172.7 | 192.1 | 184.6 | 278.2
314 | 195 | 522.7 | 216.8 | 122.4 | 128.7 | 174.1 | 192.7 | 185.4 | 279.4
315 | 196 | 522.6 | 218.6 | 123.5 | 129.8 | 175.3 | 193.5 | 186 | 280.6
316 | 197 | 522.3 | 220.1 | 124.6 | 130.9 | 176.2 | 194.6 | 186.3 | 281.8
317 | 198 | 522 | 221.4 | 125.7 | 131.9 | 177.4 | 195.5 | 187.1 | 283
318 | 199 | 522 | 222.6 | 126.9 | 133 | 178.8 | 196.2 | 187.5 | 284.2
319 | 200 | 522 | 223.8 | 128 | 134.1 | 179.8 | 196.9 | 188 | 285.4
320 | 201 | 521.7 | 225.1 | 129.1 | 135.2 | 180.6 | 197.5 | 188.5 | 286.5
321 | 202 | 521.7 | 226.4 | 130.2 | 136.3 | 182 | 198.2 | 189.3 | 287.6
322 | 203 | 521.7 | 227 | 131.3 | 137.4 | 183.9 | 199.2 | 189.9 | 288.8
323 | 204 | 521.5 | 228 | 132.4 | 138.4 | 185.8 | 200.3 | 190.4 | 289.9
324 | 205 | 521.2 | 229.6 | 133.4 | 139.5 | 187.4 | 201.1 | 190.6 | 291
325 | 206 | 521.1 | 231.1 | 134.6 | 140.5 | 188.6 | 201.7 | 191.2 | 292.2
326 | 207 | 521.3 | 232.5 | 135.6 | 141.6 | 190.2 | 202.5 | 191.7 | 293.3
327 | 208 | 521.5 | 233.7 | 136.7 | 142.6 | 191.4 | 202.9 | 192.4 | 294.4
328 | 209 | 521.6 | 235 | 137.7 | 143.7 | 192.1 | 203.3 | 192.8 | 295.5
329 | 210 | 521.5 | 236.2 | 138.8 | 144.7 | 192.8 | 203.9 | 193.3 | 296.5
330 | 211 | 521.6 | 237.2 | 139.9 | 145.8 | 194 | 204.6 | 193.8 | 297.6
331 | 212 | 521.6 | 238.2 | 140.9 | 146.8 | 195.3 | 205.3 | 194.4 | 298.7
332 | 213 | 521.5 | 239.2 | 142 | 147.8 | 196.4 | 206 | 195.3 | 299.7
333 | 214 | 521.7 | 240.1 | 143.1 | 148.9 | 197.5 | 206.7 | 196.1 | 300.8
334 | 215 | 521.9 | 240.9 | 144.1 | 149.9 | 197.8 | 207.4 | 196.5 | 301.8
335 | 216 | 522 | 241.7 | 145.2 | 150.9 | 198.1 | 208.2 | 197 | 302.8
336 | 217 | 522.1 | 242.7 | 146.3 | 151.9 | 199.4 | 208.7 | 197.4 | 303.8
337 | 218 | 522.2 | 243.6 | 147.3 | 152.9 | 200.3 | 209.6 | 197.9 | 304.8
338 | 219 | 522.3 | 244.3 | 148.3 | 153.9 | 201.2 | 210.4 | 198.5 | 305.8
339 | 220 | 522.2 | 245.2 | 149.4 | 155 | 202.7 | 211 | 198.9 | 306.8
340 | 221 | 522.1 | 245.8 | 150.4 | 156 | 203.2 | 211.8 | 199.3 | 307.8
341 | 222 | 522 | 246.5 | 151.4 | 157 | 203.6 | 212.7 | 199.7 | 308.8
342 | 223 | 521.9 | 247.6 | 152.4 | 158 | 205.1 | 213.3 | 200.1 | 309.7
343 | 224 | 521.9 | 248.6 | 153.4 | 159.1 | 206.8 | 213.7 | 200.6 | 310.7
344 | 225 | 521.8 | 249.6 | 154.4 | 160.3 | 208.3 | 214.2 | 201.1 | 311.7
345 | 226 | 521.8 | 250.1 | 155.4 | 161.4 | 210 | 214.9 | 201.4 | 312.6
346 | 227 | 521.6 | 251.1 | 156.4 | 162.5 | 211.4 | 215.4 | 201.7 | 313.6
347 | 228 | 521.7 | 252.4 | 157.4 | 163.6 | 212.9 | 216.3 | 202.2 | 314.5
348 | 229 | 521.8 | 253.3 | 158.4 | 164.6 | 214.1 | 217.4 | 202.6 | 315.4
349 | 230 | 521.7 | 254.4 | 159.4 | 165.6 | 215.3 | 217.8 | 203 | 316.3
350 | 231 | 521.8 | 255 | 160.3 | 166.6 | 216.2 | 218.2 | 203.3 | 317.1
351 | 232 | 521.9 | 255.8 | 161.3 | 167.7 | 217.2 | 219 | 203.8 | 318
352 | 233 | 522.2 | 256.5 | 162.3 | 168.7 | 218.5 | 219.5 | 204.4 | 318.9
353 | 234 | 522.4 | 257.2 | 163.3 | 169.7 | 219.9 | 220 | 204.9 | 319.8
354 | 235 | 522.4 | 258.2 | 164.3 | 170.7 | 221.1 | 220.6 | 205 | 320.6
355 | 236 | 522.2 | 259.3 | 165.2 | 171.7 | 221.6 | 220.9 | 205.5 | 321.4
356 | 237 | 522.2 | 260 | 166.2 | 172.6 | 222.4 | 221.7 | 205.8 | 322.3
357 | 238 | 522.4 | 260.9 | 167.2 | 173.6 | 223.3 | 222.7 | 206.1 | 323.2
358 | 239 | 522.4 | 262 | 168.1 | 174.5 | 224.4 | 223.5 | 206.6 | 324
359 | 240 | 522.4 | 262.9 | 169 | 175.5 | 225.5 | 224.4 | 206.9 | 324.8
360 | 241 | 522.6 | 263.7 | 170 | 176.4 | 226.8 | 225.2 | 207.3 | 325.6
361 | 242 | 522.7 | 264 | 170.9 | 177.3 | 227.8 | 225.8 | 207.5 | 326.4
362 | 243 | 522.9 | 264.5 | 171.9 | 178.3 | 228.8 | 226.5 | 208 | 327.2
363 | 244 | 523 | 265.4 | 172.9 | 179.1 | 229 | 227.5 | 208.6 | 328
364 | 245 | 523.2 | 266.3 | 173.8 | 180.1 | 230.5 | 228.4 | 208.7 | 328.8
365 | 246 | 523.3 | 267.3 | 174.8 | 181 | 231.9 | 229 | 209 | 329.6
366 | 247 | 523.2 | 268.4 | 175.6 | 181.9 | 233.3 | 229.9 | 209.4 | 330.4
367 | 248 | 523.2 | 269.4 | 176.6 | 182.8 | 234.1 | 230.4 | 209.7 | 331.2
368 | 249 | 523.2 | 270.2 | 177.5 | 183.7 | 234.5 | 230.9 | 210 | 331.9
369 | 250 | 522.8 | 270.8 | 178.3 | 184.6 | 235.6 | 231.3 | 210.2 | 332.7
370 | 251 | 522.5 | 271.4 | 179.2 | 185.5 | 236.8 | 231.9 | 210.5 | 333.4
371 | 252 | 522.4 | 272.4 | 180.1 | 186.4 | 238 | 232.4 | 210.7 | 334.2
372 | 253 | 522.3 | 272.8 | 181 | 187.3 | 239 | 233.1 | 211 | 334.9
373 | 254 | 522.1 | 273.2 | 181.8 | 188.3 | 239.4 | 233.7 | 211.4 | 335.6
374 | 255 | 521.8 | 274 | 182.7 | 189.2 | 240.1 | 234.3 | 211.9 | 336.3
375 | 256 | 521.7 | 274.7 | 183.5 | 190.1 | 240.6 | 234.9 | 212.4 | 337.1
376 | 257 | 521.8 | 275.6 | 184.4 | 191 | 241.5 | 235.5 | 212.7 | 337.7
377 | 258 | 521.7 | 276.4 | 185.2 | 191.9 | 242.5 | 235.9 | 212.9 | 338.4
378 | 259 | 521.8 | 277.3 | 186.1 | 192.8 | 243.4 | 236.4 | 213.2 | 339
379 | 260 | 521.6 | 277.9 | 187 | 193.7 | 243.7 | 236.9 | 213.6 | 339.7
380 | 261 | 521.4 | 278.7 | 187.9 | 194.5 | 244.9 | 237.5 | 213.9 | 340.3
381 | 262 | 521.6 | 279.7 | 188.7 | 195.4 | 246 | 238.3 | 214.1 | 341
382 | 263 | 521.7 | 280.3 | 189.6 | 196.3 | 246.4 | 238.9 | 214.5 | 341.7
383 | 264 | 521.6 | 281 | 190.4 | 197.2 | 247.5 | 239.8 | 214.9 | 342.4
384 | 265 | 521.5 | 281.7 | 191.3 | 198 | 248.9 | 240.3 | 215.5 | 343
385 | 266 | 521.4 | 282.3 | 192.1 | 198.9 | 250 | 240.8 | 215.8 | 343.7
386 | 267 | 521.3 | 282.8 | 193 | 199.8 | 251.1 | 241.5 | 216.2 | 344.3
387 | 268 | 521.4 | 283.4 | 193.9 | 200.6 | 251.9 | 242.1 | 216.5 | 345
388 | 269 | 521.3 | 284 | 194.8 | 201.4 | 252.5 | 242.8 | 216.9 | 345.6
389 | 270 | 521.2 | 284.9 | 195.7 | 202.2 | 253.4 | 243.6 | 217.2 | 346.2
390 | 271 | 520.9 | 285.5 | 196.7 | 203 | 254.1 | 244.5 | 217.7 | 346.9
391 | 272 | 520.6 | 286.4 | 197.4 | 203.9 | 254.9 | 245.4 | 218.3 | 347.5
392 | 273 | 520.6 | 287.1 | 198.2 | 204.7 | 255.4 | 246.2 | 218.7 | 348.1
393 | 274 | 520.4 | 287.6 | 198.9 | 205.6 | 256.6 | 246.9 | 219.1 | 348.7
394 | 275 | 520.3 | 288.2 | 199.7 | 206.5 | 257.4 | 247.4 | 219.4 | 349.2
395 | 276 | 520 | 288.4 | 200.5 | 207.3 | 258.2 | 247.9 | 219.9 | 349.7
396 | 277 | 519.6 | 288.5 | 201.3 | 208.1 | 258.7 | 248.6 | 220.3 | 350.3
397 | 278 | 519.3 | 289.3 | 202.1 | 209 | 259.3 | 249.1 | 220.7 | 350.8
398 | 279 | 519.1 | 290 | 202.8 | 209.8 | 260.6 | 250 | 221.1 | 351.4
399 | 280 | 518.9 | 290.5 | 203.6 | 210.6 | 261.4 | 250.6 | 221.5 | 351.9
400 | 281 | 518.9 | 290.4 | 204.5 | 211.4 | 262.4 | 251.2 | 221.9 | 352.4
401 | 282 | 518.8 | 290.1 | 205.3 | 212.3 | 263.4 | 251.6 | 222.3 | 352.9
402 | 283 | 518.8 | 289.7 | 206.1 | 213.1 | 264.1 | 252.3 | 222.8 | 353.5
403 | 284 | 518.7 | 290 | 206.9 | 213.9 | 264.5 | 252.7 | 223.2 | 353.9
404 | 285 | 518.8 | 290.2 | 207.7 | 214.7 | 265.3 | 253.1 | 223.8 | 354.4
405 | 286 | 519 | 290.4 | 208.5 | 215.5 | 265.7 | 253.7 | 224.2 | 354.9
406 | 287 | 519.2 | 290.9 | 209.3 | 216.3 | 266.2 | 254 | 224.5 | 355.5
407 | 288 | 519.1 | 291 | 210.1 | 217.1 | 267 | 254.5 | 224.8 | 355.9
408 | 289 | 518.8 | 291.1 | 210.8 | 217.9 | 268 | 255.1 | 225.1 | 356.5
409 | 290 | 518.8 | 291 | 211.6 | 218.6 | 268.6 | 255.5 | 225.5 | 357
410 | 291 | 518.8 | 291.1 | 212.4 | 219.4 | 269.1 | 256.1 | 226 | 357.4
411 | 292 | 518.9 | 291.4 | 213.2 | 220.2 | 270.1 | 256.6 | 226.3 | 357.9
412 | 293 | 519.1 | 291.1 | 213.9 | 221 | 271 | 257.3 | 226.6 | 358.4
413 | 294 | 519.1 | 291.4 | 214.7 | 221.8 | 271.8 | 257.9 | 226.9 | 358.9
414 | 295 | 519.1 | 292.2 | 215.4 | 222.5 | 272.7 | 258.4 | 227.3 | 359.3
415 | 296 | 519.2 | 292.9 | 216.2 | 223.3 | 273.1 | 258.9 | 227.9 | 359.8
416 | 297 | 519.2 | 293.3 | 216.9 | 224.1 | 273.4 | 259.2 | 228.2 | 360.2
417 | 298 | 519.3 | 293.5 | 217.6 | 224.8 | 274.1 | 259.6 | 228.7 | 360.7
418 | 299 | 519.4 | 294 | 218.4 | 225.6 | 275.3 | 260.1 | 229.1 | 361.1
419 | 300 | 519.4 | 294.6 | 219.1 | 226.4 | 275.8 | 260.6 | 229.4 | 361.6
420 | 301 | 519.4 | 295.3 | 219.9 | 227.1 | 276.5 | 261 | 229.7 | 362.1
421 | 302 | 519.4 | 296.1 | 220.7 | 227.9 | 277.2 | 261.2 | 229.9 | 362.5
422 | 303 | 519.5 | 296.8 | 221.4 | 228.6 | 277.9 | 261.5 | 230.2 | 362.9
423 | 304 | 519.7 | 297.3 | 222.2 | 229.4 | 278.6 | 261.8 | 230.6 | 363.4
424 | 305 | 519.7 | 297.9 | 223 | 230.1 | 279.4 | 262.4 | 231 | 363.8
425 | 306 | 519.7 | 298.3 | 223.7 | 230.9 | 280.1 | 262.8 | 231.4 | 364.2
426 | 307 | 519.6 | 298.8 | 224.4 | 231.6 | 280.8 | 263.2 | 231.8 | 364.6
427 | 308 | 519.4 | 299.3 | 225.2 | 232.2 | 281.5 | 263.6 | 232.1 | 365
428 | 309 | 519.2 | 299.6 | 225.9 | 233 | 282.1 | 264.2 | 232.5 | 365.4
429 | 310 | 519.3 | 300 | 226.7 | 233.7 | 283 | 264.8 | 232.8 | 365.8
430 | 311 | 519.3 | 300.4 | 227.4 | 234.4 | 283.5 | 265 | 233.2 | 366.2
431 | 312 | 519.4 | 300.8 | 228.1 | 235.1 | 284.1 | 265.3 | 233.6 | 366.6
432 | 313 | 519.4 | 301.5 | 228.9 | 235.8 | 285.1 | 265.9 | 233.9 | 367
433 | 314 | 519.6 | 302.1 | 229.6 | 236.5 | 286.1 | 266.5 | 234.2 | 367.4
434 | 315 | 519.8 | 302.5 | 230.3 | 237.2 | 286.6 | 266.6 | 234.7 | 367.8
435 | 316 | 519.8 | 303.1 | 231 | 237.9 | 287.3 | 267.1 | 235.1 | 368.2
436 | 317 | 519.7 | 303.7 | 231.7 | 238.6 | 287.9 | 267.6 | 235.4 | 368.5
437 | 318 | 519.4 | 304.1 | 232.4 | 239.3 | 288.3 | 267.9 | 235.7 | 368.9
438 | 319 | 519.3 | 304.2 | 233.1 | 240 | 288.8 | 268.4 | 236 | 369.3
439 | 320 | 519 | 304.8 | 233.9 | 240.7 | 289.6 | 268.8 | 236.5 | 369.6
440 | 321 | 518.8 | 305.3 | 234.6 | 241.4 | 290.2 | 269.3 | 236.8 | 370
441 | 322 | 518.8 | 305.6 | 235.3 | 242.1 | 290.6 | 269.8 | 237.2 | 370.3
442 | 323 | 518.8 | 306.1 | 236 | 242.8 | 291.2 | 270.2 | 237.5 | 370.7
443 | 324 | 518.8 | 306.6 | 236.6 | 243.5 | 291.9 | 270.7 | 237.9 | 371
444 | 325 | 518.7 | 306.7 | 237.3 | 244.2 | 292.5 | 271.3 | 238.3 | 371.3
445 | 326 | 518.8 | 306.9 | 238 | 244.9 | 293.1 | 271.8 | 238.8 | 371.6
446 | 327 | 518.8 | 307.1 | 238.6 | 245.6 | 293.8 | 272.2 | 239.3 | 372
447 | 328 | 518.7 | 307 | 239.4 | 246.3 | 294.5 | 272.6 | 239.6 | 372.3
448 | 329 | 518.8 | 306.7 | 240 | 246.9 | 295.1 | 273 | 240 | 372.6
449 | 330 | 518.8 | 306.5 | 240.8 | 247.6 | 295.4 | 273.5 | 240.4 | 373
450 | 331 | 518.8 | 306.6 | 241.4 | 248.2 | 296.2 | 274 | 240.8 | 373.3
451 | 332 | 519 | 307.5 | 242.1 | 248.9 | 296.6 | 274.5 | 241.3 | 373.6
452 | 333 | 519 | 308 | 242.8 | 249.5 | 297.1 | 275 | 241.8 | 373.9
453 | 334 | 519.2 | 308.5 | 243.6 | 250.1 | 297.3 | 275.4 | 241.9 | 374.2
454 | 335 | 519.4 | 309.2 | 244.2 | 250.8 | 297.9 | 275.9 | 242.1 | 374.6
455 | 336 | 519.6 | 309.7 | 244.9 | 251.4 | 298.9 | 276.4 | 242.4 | 374.9
456 | 337 | 519.7 | 310.6 | 245.6 | 252.1 | 299.8 | 276.8 | 242.7 | 375.2
457 | 338 | 519.8 | 311.1 | 246.3 | 252.8 | 300.7 | 277.2 | 243 | 375.5
458 | 339 | 519.9 | 311.9 | 247 | 253.5 | 301.3 | 277.6 | 243.3 | 375.8
459 | 340 | 520 | 312.8 | 247.7 | 254.1 | 301.7 | 277.7 | 243.6 | 376.1
460 | 341 | 520.1 | 313.9 | 248.5 | 254.8 | 301.8 | 278 | 244 | 376.4
461 | 342 | 520.2 | 314.8 | 249.2 | 255.4 | 301.5 | 278.1 | 244.2 | 376.6
462 | 343 | 520.4 | 315.6 | 249.9 | 256 | 301.2 | 278.3 | 244.5 | 376.9
463 | 344 | 520.5 | 316.2 | 250.6 | 256.7 | 301.8 | 278.3 | 244.8 | 377.2
464 | 345 | 520.7 | 316.5 | 251.3 | 257.3 | 302.6 | 278.4 | 245.1 | 377.5
465 | 346 | 520.8 | 317.2 | 252 | 257.9 | 302.3 | 278.6 | 245.2 | 377.8
466 | 347 | 520.8 | 318.1 | 252.7 | 258.6 | 302 | 278.8 | 245.2 | 378.1
467 | 348 | 520.8 | 318.9 | 253.5 | 259.2 | 302.5 | 279 | 245.6 | 378.4
468 | 349 | 520.8 | 319.8 | 254.2 | 259.8 | 303.2 | 279.2 | 246 | 378.7
469 | 350 | 520.9 | 321.7 | 252.8 | 261.2 | 305.9 | 279.6 | 246.4 | 378.8
470 | 351 | 520.8 | 323 | 252.1 | 262.3 | 307.4 | 279.9 | 246.7 | 379.1
471 | 352 | 520.8 | 323.5 | 252.8 | 262.9 | 308.3 | 280 | 247.1 | 379.4
472 | 353 | 520.7 | 324 | 253.5 | 263.6 | 308.9 | 280.1 | 247.6 | 379.7
473 | 354 | 520.6 | 324.9 | 254.1 | 264.2 | 309.5 | 280.3 | 248.2 | 380
474 | 355 | 520.3 | 325.8 | 254.8 | 264.8 | 309.1 | 280.5 | 248.6 | 380.2
475 | 356 | 520.2 | 326.7 | 255.4 | 265.5 | 310 | 280.7 | 249 | 380.5
476 | 357 | 519.9 | 327.3 | 256 | 266.1 | 310.8 | 280.9 | 249.3 | 380.8
477 | 358 | 519.6 | 328 | 256.6 | 266.8 | 311.8 | 281.2 | 249.6 | 381
478 | 359 | 519.3 | 328.6 | 257.3 | 267.4 | 311.8 | 281.4 | 249.8 | 381.3
479 | 360 | 519.4 | 329.3 | 257.9 | 268 | 312 | 281.6 | 250.1 | 381.5
480 | 361 | 519.3 | 329.8 | 258.4 | 268.6 | 313.1 | 281.9 | 250.3 | 381.8
481 | 362 | 519.3 | 330 | 259.1 | 269.2 | 314.2 | 282 | 250.5 | 382.1
482 | 363 | 519.1 | 330.6 | 259.7 | 269.9 | 315.2 | 282.1 | 250.6 | 382.3
483 | 364 | 519 | 331.4 | 260.4 | 270.5 | 315.7 | 282.3 | 250.7 | 382.6
484 | 365 | 519.1 | 332.2 | 261 | 271.1 | 315.5 | 282.5 | 250.9 | 382.9
485 | 366 | 519.1 | 333.1 | 261.7 | 271.7 | 316.5 | 282.7 | 251.1 | 383.1
486 | 367 | 519.1 | 333.8 | 262.3 | 272.3 | 317 | 282.9 | 251.5 | 383.4
487 | 368 | 519.1 | 334.5 | 263.1 | 272.9 | 317.2 | 283.1 | 251.7 | 383.6
488 | 369 | 519.3 | 334.7 | 263.7 | 273.5 | 317.4 | 283.5 | 252.1 | 383.9
489 | 370 | 519.3 | 335.4 | 264.3 | 274.1 | 318.2 | 283.8 | 252.3 | 384.1
490 | 371 | 519.2 | 336 | 265 | 274.7 | 318.7 | 284.2 | 252.5 | 384.3
491 | 372 | 519.3 | 336.6 | 265.6 | 275.3 | 319.6 | 284.5 | 252.7 | 384.6
492 | 373 | 519.5 | 337.2 | 266.3 | 275.8 | 320 | 284.7 | 252.8 | 384.9
493 | 374 | 519.6 | 337.8 | 267 | 276.4 | 320.9 | 285 | 253.2 | 385.1
494 | 375 | 519.8 | 338.1 | 267.6 | 277 | 321.9 | 285.4 | 253.7 | 385.4
495 | 376 | 520 | 338.5 | 268.3 | 277.6 | 322.9 | 285.9 | 254 | 385.7
496 | 377 | 519.9 | 338.8 | 268.9 | 278.1 | 323 | 286.3 | 254.3 | 385.9
497 | 378 | 519.9 | 339.3 | 269.5 | 278.7 | 323.5 | 286.4 | 254.6 | 386.2
498 | 379 | 519.9 | 340 | 270.1 | 279.3 | 324.6 | 286.7 | 254.8 | 386.5
499 | 380 | 520 | 340.6 | 270.7 | 279.9 | 325.4 | 287.1 | 254.9 | 386.7
500 | 381 | 520 | 340.8 | 271.3 | 280.4 | 326.3 | 287.6 | 255.1 | 387
501 | 382 | 520 | 341.4 | 271.9 | 281 | 327.4 | 288 | 255.3 | 387.3
502 | 383 | 520.1 | 341.8 | 272.5 | 281.6 | 328.1 | 288.4 | 255.5 | 387.6
503 | 384 | 520.3 | 342.6 | 273.2 | 282.1 | 328.7 | 288.9 | 255.8 | 387.9
504 | 385 | 520.5 | 343.3 | 273.8 | 282.7 | 328.7 | 289.1 | 256.2 | 388.1
505 | 386 | 520.5 | 343.8 | 274.4 | 283.3 | 329.3 | 289.4 | 256.5 | 388.4
506 | 387 | 520.5 | 344.3 | 274.9 | 283.9 | 330.1 | 289.8 | 256.7 | 388.6
507 | 388 | 520.5 | 344.7 | 275.4 | 284.5 | 331.3 | 290.2 | 257.1 | 388.8
508 | 389 | 520.5 | 344.9 | 276 | 285.1 | 332 | 290.6 | 257.4 | 389.1
509 | 390 | 520.5 | 345.3 | 276.5 | 285.7 | 332.7 | 291 | 257.8 | 389.3
510 | 391 | 520.5 | 345.6 | 277 | 286.3 | 333.2 | 291.4 | 258.2 | 389.5
511 | 392 | 520.5 | 346.1 | 277.5 | 286.9 | 333.3 | 291.9 | 258.6 | 389.7
512 | 393 | 520.5 | 346.1 | 278.2 | 287.5 | 333.7 | 292.2 | 258.9 | 389.9
513 | 394 | 520.6 | 345.8 | 278.8 | 288.1 | 334.6 | 292.5 | 259.2 | 390.1
514 | 395 | 520.5 | 345.9 | 279.3 | 288.6 | 335.4 | 292.9 | 259.6 | 390.3
515 | 396 | 520.5 | 346.3 | 279.9 | 289.2 | 336.7 | 293.2 | 259.9 | 390.5
516 | 397 | 520.4 | 346.8 | 280.5 | 289.8 | 337.5 | 293.6 | 260.3 | 390.7
517 | 398 | 520.5 | 347 | 281.1 | 290.4 | 338 | 293.9 | 260.7 | 390.9
518 | 399 | 520.5 | 347.9 | 281.7 | 291 | 338.3 | 294.3 | 261 | 391
519 | 400 | 520.7 | 348.7 | 282.3 | 291.5 | 338.8 | 294.8 | 261.3 | 391.3
520 | 401 | 521 | 349.2 | 283 | 292.1 | 338.8 | 295.3 | 261.6 | 391.4
521 | 402 | 521.2 | 349.6 | 283.5 | 292.6 | 339.1 | 295.7 | 261.8 | 391.6
522 | 403 | 521.1 | 349.6 | 284.1 | 293 | 339.6 | 296.1 | 262 | 391.8
523 | 404 | 521.1 | 350.3 | 284.7 | 293.6 | 340.2 | 296.4 | 262.2 | 392
524 | 405 | 521 | 350.9 | 285.3 | 294.1 | 340.8 | 296.7 | 262.4 | 392.2
525 | 406 | 520.7 | 351.1 | 285.8 | 294.7 | 340.7 | 296.9 | 262.9 | 392.5
526 | 407 | 520.5 | 351.8 | 286.3 | 295.3 | 341.4 | 297.2 | 263.3 | 392.7
527 | 408 | 520.5 | 352.4 | 286.7 | 295.9 | 341.9 | 297.5 | 263.7 | 392.9
528 | 409 | 520.4 | 352.9 | 287.2 | 296.5 | 341.9 | 297.7 | 264.1 | 393.1
529 | 410 | 520.2 | 353.4 | 287.7 | 297 | 342.8 | 297.8 | 264.5 | 393.3
530 | 411 | 520 | 353.8 | 288.3 | 297.6 | 343.6 | 298 | 264.8 | 393.4
531 | 412 | 519.8 | 354.4 | 288.8 | 298.1 | 344.2 | 298.2 | 265.1 | 393.7
532 | 413 | 519.6 | 355.2 | 289.3 | 298.8 | 344.7 | 298.5 | 265.3 | 393.9
533 | 414 | 519.3 | 355.8 | 289.8 | 299.3 | 345.5 | 298.7 | 265.5 | 394.1
534 | 415 | 519.3 | 356.4 | 290.3 | 299.9 | 346.2 | 298.9 | 265.6 | 394.2
535 | 416 | 519.3 | 356.8 | 290.9 | 300.5 | 346.6 | 299.3 | 265.7 | 394.4
536 | 417 | 519.3 | 357 | 291.4 | 301.1 | 346.8 | 299.6 | 265.9 | 394.6
537 | 418 | 519.3 | 357.2 | 292 | 301.7 | 347.2 | 299.9 | 266.1 | 394.8
538 | 419 | 519.2 | 357.7 | 292.6 | 302.3 | 347.9 | 300.3 | 266.1 | 394.9
539 | 420 | 519 | 358.3 | 293.1 | 302.8 | 348.4 | 300.7 | 266.1 | 395.1
540 | 421 | 519 | 358.6 | 293.8 | 303.4 | 348.7 | 301 | 266.1 | 395.3
541 | 422 | 518.8 | 358.9 | 294.4 | 303.9 | 348.9 | 301.4 | 266.4 | 395.5
542 | 423 | 518.7 | 359.2 | 295.1 | 304.4 | 349.7 | 301.7 | 266.6 | 395.7
543 | 424 | 518.7 | 359.8 | 295.6 | 305 | 349.7 | 302 | 266.9 | 395.8
544 | 425 | 518.8 | 360.4 | 296.2 | 305.6 | 349.8 | 302.3 | 267.1 | 396
545 | 426 | 518.9 | 361 | 296.8 | 306.2 | 350.3 | 302.6 | 267.5 | 396.1
546 | 427 | 518.9 | 361.4 | 297.4 | 306.7 | 351 | 302.9 | 267.7 | 396.3
547 | 428 | 518.7 | 361.6 | 297.9 | 307.4 | 351.6 | 303.2 | 267.9 | 396.5
548 | 429 | 518.7 | 362.3 | 298.5 | 308 | 352.3 | 303.6 | 268.1 | 396.7
549 | 430 | 518.6 | 362.8 | 299.1 | 308.5 | 352.7 | 303.9 | 268.2 | 396.9
550 | 431 | 518.4 | 363.5 | 299.6 | 309.1 | 352.9 | 304.1 | 268.3 | 397.1
551 | 432 | 518.5 | 363.9 | 300.2 | 309.6 | 353 | 304.4 | 268.5 | 397.2
552 | 433 | 518.4 | 364.2 | 300.8 | 310.2 | 353.4 | 304.7 | 268.6 | 397.3
553 | 434 | 518.3 | 364.7 | 301.3 | 310.7 | 353.9 | 305 | 268.7 | 397.5
554 | 435 | 518.3 | 365 | 301.8 | 311.3 | 354.2 | 305.3 | 268.9 | 397.7
555 | 436 | 518.4 | 365.5 | 302.3 | 311.8 | 354.6 | 305.6 | 269.1 | 397.8
556 | 437 | 518.5 | 366 | 302.9 | 312.4 | 355 | 305.9 | 269.2 | 398
557 | 438 | 518.5 | 366.3 | 303.5 | 312.9 | 354.9 | 306.2 | 269.4 | 398.1
558 | 439 | 518.5 | 366.7 | 304.1 | 313.5 | 355.1 | 306.5 | 269.6 | 398.3
559 | 440 | 518.5 | 367 | 304.6 | 314 | 355.7 | 306.8 | 269.8 | 398.5
560 | 441 | 518.5 | 367.4 | 305.2 | 314.5 | 356.4 | 307.1 | 270 | 398.7
561 | 442 | 518.3 | 368.1 | 305.6 | 315.1 | 357 | 307.5 | 270.1 | 398.9
562 | 443 | 518.3 | 368.5 | 306.1 | 315.7 | 357.8 | 307.9 | 270.2 | 399
563 | 444 | 518.4 | 369 | 306.6 | 316.2 | 358.4 | 308.3 | 270.3 | 399.2
564 | 445 | 518.5 | 369.6 | 307.1 | 316.8 | 358.9 | 308.6 | 270.5 | 399.3
565 | 446 | 518.6 | 370 | 307.7 | 317.2 | 359.3 | 308.8 | 270.5 | 399.5
566 | 447 | 518.5 | 370.5 | 308.2 | 317.8 | 359.7 | 309.2 | 270.6 | 399.7
567 | 448 | 518.4 | 371 | 308.8 | 318.3 | 360.2 | 309.5 | 270.7 | 399.8
568 | 449 | 518.5 | 371.6 | 309.3 | 318.8 | 361 | 309.8 | 270.9 | 400
569 | 450 | 518.6 | 371.8 | 309.8 | 319.3 | 361.5 | 310.2 | 271 | 400.2
570 | 451 | 518.5 | 372.1 | 310.4 | 319.8 | 362 | 310.7 | 271.2 | 400.3
571 | 452 | 518.3 | 371.9 | 310.9 | 320.4 | 362.5 | 311 | 271.4 | 400.5
572 | 453 | 518.3 | 372.4 | 311.5 | 320.9 | 363 | 311.4 | 271.5 | 400.6
573 | 454 | 518.5 | 372.9 | 312 | 321.4 | 363.7 | 311.7 | 271.8 | 400.8
574 | 455 | 518.4 | 373.5 | 312.5 | 321.9 | 364.1 | 312 | 272 | 401
575 | 456 | 518.4 | 373.9 | 312.9 | 322.5 | 364.5 | 312.4 | 272.2 | 401.1
576 | 457 | 518.4 | 374.2 | 313.4 | 323 | 364.8 | 312.7 | 272.4 | 401.3
577 | 458 | 518.4 | 374.8 | 313.9 | 323.5 | 364.8 | 313 | 272.5 | 401.5
578 | 459 | 518.4 | 375.3 | 314.4 | 324 | 364.1 | 313.3 | 272.6 | 401.6
579 | 460 | 518.2 | 375.8 | 314.8 | 324.5 | 364.1 | 313.6 | 272.8 | 401.8
580 | 461 | 518.2 | 376.3 | 315.4 | 324.9 | 364.5 | 314 | 273 | 401.9
581 | 462 | 518.2 | 376.6 | 315.9 | 325.4 | 364.8 | 314.2 | 273.2 | 402
582 | 463 | 518.2 | 376.8 | 316.4 | 325.9 | 365 | 314.6 | 273.5 | 402.2
583 | 464 | 518.3 | 377 | 316.8 | 326.4 | 365.3 | 314.9 | 273.6 | 402.3
584 | 465 | 518.5 | 377.5 | 317.3 | 326.9 | 366 | 315.2 | 273.8 | 402.5
585 | 466 | 518.5 | 378 | 317.8 | 327.4 | 366.1 | 315.6 | 273.9 | 402.6
586 | 467 | 518.7 | 378.5 | 318.3 | 327.9 | 366.2 | 316.1 | 274 | 402.8
587 | 468 | 519.2 | 378.8 | 318.8 | 328.4 | 366.9 | 316.5 | 274.2 | 402.9
588 | 469 | 519.5 | 379.3 | 319.3 | 328.8 | 367.3 | 316.8 | 274.3 | 403.1
589 | 470 | 519.7 | 379.9 | 319.7 | 329.3 | 367.9 | 317.1 | 274.3 | 403.3
590 | 471 | 519.8 | 380.2 | 320.2 | 329.8 | 368.6 | 317.4 | 274.5 | 403.5
591 | 472 | 519.9 | 380.4 | 320.7 | 330.3 | 368.9 | 317.7 | 274.7 | 403.7
592 | 473 | 519.9 | 380.8 | 321.1 | 330.8 | 369.2 | 318 | 275 | 403.9
593 | 474 | 520.1 | 381.3 | 321.6 | 331.2 | 369.2 | 318.4 | 275.1 | 404.1
594 | 475 | 520.2 | 381.9 | 322.1 | 331.7 | 368.9 | 318.7 | 275.2 | 404
595 | 476 | 520.2 | 382.1 | 322.6 | 332.1 | 368.7 | 319 | 275.3 | 404.2
596 | 477 | 520.3 | 382.4 | 323.1 | 332.6 | 369.3 | 319.3 | 275.5 | 404.5
597 | 478 | 520.4 | 382.7 | 323.5 | 333.1 | 369.2 | 319.7 | 275.6 | 404.6
598 | 479 | 520.5 | 383 | 324 | 333.5 | 369.4 | 320.1 | 275.7 | 404.8
599 | 480 | 520.7 | 383.2 | 324.6 | 334 | 368.9 | 320.6 | 275.7 | 405
600 | 481 | 520.9 | 383.4 | 325.1 | 334.4 | 368.7 | 321 | 275.8 | 405.1
601 | 482 | 520.8 | 383.7 | 325.5 | 334.9 | 369.2 | 321.5 | 275.9 | 405.3
602 | 483 | 520.4 | 383.9 | 326 | 335.3 | 369.8 | 321.9 | 276 | 405.5
603 | 484 | 520.2 | 384.1 | 326.5 | 335.8 | 370.5 | 322.3 | 276.1 | 405.6
604 | 485 | 520 | 384.4 | 327 | 336.3 | 371 | 322.6 | 276.2 | 405.8
605 | 486 | 519.8 | 384.4 | 327.4 | 336.8 | 371.9 | 322.8 | 276.3 | 406
606 | 487 | 520 | 384.4 | 327.7 | 337.3 | 372.3 | 323.1 | 276.4 | 406.1
607 | 488 | 519.8 | 384.6 | 328 | 337.8 | 372.8 | 323.5 | 276.5 | 406.3
608 | 489 | 519.6 | 384.8 | 328.4 | 338.3 | 373.5 | 323.9 | 276.6 | 406.4
609 | 490 | 519.5 | 385 | 328.8 | 338.8 | 373.7 | 324.2 | 276.6 | 406.6
610 | 491 | 519.5 | 385.2 | 329.2 | 339.2 | 374.5 | 324.6 | 276.8 | 406.7
611 | 492 | 519.5 | 385.3 | 329.7 | 339.7 | 374.7 | 324.9 | 277.1 | 406.9
612 | 493 | 519.3 | 385.6 | 330 | 340.2 | 375.3 | 325.3 | 277.4 | 407.1
613 | 494 | 519.2 | 385.8 | 330.5 | 340.6 | 376 | 325.6 | 277.7 | 407.2
614 | 495 | 519.3 | 386 | 330.9 | 341.1 | 376.6 | 325.8 | 277.8 | 407.4
615 | 496 | 519.2 | 386.3 | 331.3 | 341.5 | 377 | 326.2 | 277.9 | 407.5
616 | 497 | 519.2 | 386.7 | 331.7 | 342 | 377.9 | 326.6 | 278 | 407.7
617 | 498 | 519.2 | 386.9 | 332.1 | 342.4 | 378.2 | 326.9 | 278 | 407.8
618 | 499 | 519.3 | 387.3 | 332.6 | 342.9 | 379.1 | 327.1 | 278.1 | 408
619 | 500 | 519.5 | 387.8 | 333 | 343.3 | 379.6 | 327.5 | 278.3 | 408.2
620 | 501 | 519.4 | 388.3 | 333.4 | 343.7 | 380.2 | 327.8 | 278.5 | 408.3
621 | 502 | 519.4 | 388.9 | 333.8 | 344.2 | 380.1 | 328.2 | 278.6 | 408.4
622 | 503 | 519.3 | 389.3 | 334.3 | 344.6 | 380.2 | 328.4 | 278.6 | 408.5
623 | 504 | 519.5 | 389.9 | 334.7 | 345 | 380.2 | 328.6 | 278.8 | 408.7
624 | 505 | 519.6 | 390.5 | 335.1 | 345.4 | 380.6 | 328.8 | 278.8 | 408.8
625 | 506 | 519.7 | 391.1 | 335.5 | 345.9 | 380.1 | 329 | 279.3 | 408.9
626 | 507 | 519.8 | 391.8 | 335.9 | 346.3 | 380.3 | 329.2 | 279.6 | 409.1
627 | 508 | 520 | 392.5 | 336.4 | 346.6 | 380.7 | 329.4 | 279.8 | 409.2
628 | 509 | 520.1 | 393.4 | 336.8 | 347.1 | 380.8 | 329.7 | 280 | 409.3
629 | 510 | 520.1 | 394.4 | 337.2 | 347.5 | 381.4 | 329.9 | 280.1 | 409.4
630 | 511 | 519.9 | 395.3 | 337.6 | 347.9 | 382 | 330.1 | 280.4 | 409.5
631 | 512 | 519.7 | 396.3 | 338 | 348.3 | 382.3 | 330.4 | 280.5 | 409.6
632 | 513 | 519.8 | 397.2 | 338.3 | 348.7 | 383.1 | 330.7 | 280.7 | 409.8
633 | 514 | 519.6 | 398.2 | 338.7 | 349.2 | 383.7 | 330.9 | 280.9 | 409.9
634 | 515 | 519.4 | 399.1 | 339.1 | 349.5 | 384.1 | 331.1 | 281.1 | 410.1
635 | 516 | 519.5 | 400.1 | 339.4 | 349.9 | 384.9 | 331.4 | 281.2 | 410.2
636 | 517 | 519.6 | 401 | 339.8 | 350.4 | 385.7 | 331.7 | 281.4 | 410.3
637 | 518 | 519.3 | 402 | 340.1 | 350.8 | 386.1 | 332 | 281.5 | 410.4
638 | 519 | 519 | 402.9 | 340.5 | 351.2 | 386.5 | 332.3 | 281.6 | 410.5
639 | 520 | 518.9 | 403.9 | 340.9 | 351.5 | 387.3 | 332.6 | 281.6 | 410.6
640 | 521 | 518.9 | 405 | 341.3 | 351.9 | 388 | 332.8 | 281.6 | 410.8
641 | 522 | 518.9 | 406.1 | 341.7 | 352.3 | 388.3 | 333 | 281.6 | 410.9
642 | 523 | 518.8 | 407.4 | 342 | 352.6 | 388 | 333.2 | 281.6 | 410.9
643 | 524 | 518.7 | 408.6 | 342.3 | 353 | 387.9 | 333.4 | 281.8 | 411
644 | 525 | 518.6 | 409.9 | 342.7 | 353.3 | 388 | 333.5 | 282.1 | 411.2
645 | 526 | 518.5 | 411.1 | 343.1 | 353.7 | 388 | 333.7 | 282.3 | 411.3
646 | 527 | 518.4 | 412.4 | 343.5 | 354 | 388 | 333.9 | 282.5 | 411.4
647 | 528 | 518.6 | 413.6 | 343.8 | 354.4 | 388.6 | 334.1 | 282.6 | 411.5
648 | 529 | 518.7 | 414.8 | 344.1 | 354.7 | 388.8 | 334.3 | 282.7 | 411.6
649 | 530 | 518.7 | 415.9 | 344.5 | 355.1 | 388.5 | 334.7 | 283 | 411.7
650 | 531 | 518.8 | 417 | 344.9 | 355.5 | 388.1 | 334.9 | 283.2 | 411.8
651 | 532 | 518.7 | 418 | 345.2 | 355.8 | 388 | 335.1 | 283.5 | 411.8
652 | 533 | 518.8 | 419 | 345.6 | 356.1 | 388.4 | 335.4 | 283.8 | 411.9
653 | 534 | 519 | 420.1 | 345.9 | 356.5 | 388.7 | 335.6 | 283.9 | 412
654 | 535 | 519.1 | 421.2 | 346.2 | 356.8 | 389.2 | 335.7 | 284.1 | 412.1
655 | 536 | 519.2 | 422.4 | 346.6 | 357.2 | 389.8 | 335.8 | 284.2 | 412.1
656 | 537 | 519.2 | 423.6 | 347 | 357.5 | 390.2 | 336 | 284.3 | 412.2
657 | 538 | 519.3 | 424.7 | 347.3 | 357.9 | 390.7 | 336.2 | 284.4 | 412.3
658 | 539 | 519.5 | 426 | 347.6 | 358.2 | 391.4 | 336.4 | 284.7 | 412.4
659 | 540 | 519.7 | 427.2 | 347.9 | 358.5 | 392.2 | 336.6 | 284.9 | 412.5
660 | 541 | 519.9 | 428.4 | 348.2 | 358.8 | 392.8 | 336.8 | 285.1 | 412.6
661 | 542 | 519.9 | 429.5 | 348.6 | 359.1 | 393.7 | 337.2 | 285.3 | 412.7
662 | 543 | 520 | 430.5 | 348.9 | 359.5 | 394.5 | 337.6 | 285.6 | 412.8
663 | 544 | 520 | 431.5 | 349.3 | 359.9 | 395.3 | 338 | 285.7 | 412.9
664 | 545 | 520.2 | 432.4 | 349.7 | 360.1 | 396 | 338.3 | 285.9 | 413
665 | 546 | 520.4 | 433.5 | 350 | 360.5 | 396.8 | 338.6 | 286.1 | 413.1
666 | 547 | 520.6 | 434.5 | 350.4 | 360.8 | 397.5 | 338.9 | 286.2 | 413.3
667 | 548 | 520.7 | 435.5 | 350.8 | 361.1 | 398.2 | 339.3 | 286.4 | 413.4
668 | 549 | 520.6 | 436.6 | 351.1 | 361.4 | 398.8 | 339.5 | 286.6 | 413.5
669 | 550 | 520.6 | 437.7 | 351.4 | 361.7 | 399.4 | 339.8 | 286.8 | 413.6
670 | 551 | 520.5 | 438.7 | 351.8 | 362 | 400.1 | 340.1 | 287 | 413.8
671 | 552 | 520.6 | 439.7 | 352.1 | 362.4 | 400.8 | 340.4 | 287.2 | 413.8
672 | 553 | 520.6 | 440.1 | 352.4 | 362.7 | 401.6 | 340.8 | 287.4 | 413.9
673 | 554 | 520.6 | 440.6 | 352.7 | 363 | 402.2 | 341.1 | 287.6 | 414.1
674 | 555 | 520.6 | 440.6 | 353.1 | 363.3 | 402.9 | 341.5 | 287.8 | 414.2
675 | 556 | 520.3 | 440.8 | 353.5 | 363.7 | 403.6 | 341.9 | 287.9 | 414.3
676 | 557 | 520 | 441.2 | 353.9 | 364 | 404.4 | 342.3 | 288.1 | 414.3
677 | 558 | 519.9 | 441.8 | 354.3 | 364.3 | 405.3 | 342.8 | 288.3 | 414.4
678 | 559 | 519.8 | 442.6 | 354.7 | 364.7 | 406.1 | 343.3 | 288.6 | 414.5
679 | 560 | 519.8 | 443 | 355.2 | 365 | 406.9 | 343.6 | 288.7 | 414.6
680 | 561 | 519.8 | 443.1 | 355.7 | 365.3 | 407.7 | 344.1 | 288.7 | 414.7
681 | 562 | 519.7 | 443.1 | 356.1 | 365.6 | 408.6 | 344.3 | 288.8 | 414.8
682 | 563 | 519.5 | 443.2 | 356.6 | 365.9 | 409.5 | 344.6 | 288.9 | 414.9
683 | 564 | 519.4 | 443.2 | 356.9 | 366.2 | 410.5 | 344.7 | 289.1 | 414.9
684 | 565 | 519.2 | 443.4 | 357.3 | 366.5 | 411.5 | 344.7 | 289.3 | 415
685 | 566 | 519.2 | 443.9 | 357.7 | 366.8 | 412.5 | 344.8 | 289.3 | 415
686 | 567 | 519 | 444.6 | 358.1 | 367.2 | 413.5 | 344.9 | 289.4 | 415.1
687 | 568 | 518.9 | 445.3 | 358.5 | 367.6 | 414.6 | 345.1 | 289.6 | 415.1
688 | 569 | 518.8 | 446.1 | 358.8 | 368 | 415.7 | 345.2 | 289.9 | 415.2
689 | 570 | 518.8 | 446.8 | 359.2 | 368.4 | 416.8 | 345.2 | 290.1 | 415.3
690 | 571 | 518.8 | 447.4 | 359.7 | 368.7 | 417.8 | 345.4 | 290.4 | 415.4
691 | 572 | 518.7 | 448.2 | 360.1 | 369.1 | 418.9 | 345.4 | 290.5 | 415.5
692 | 573 | 518.5 | 448.8 | 360.5 | 369.5 | 419.8 | 345.5 | 290.7 | 415.5
693 | 574 | 518.5 | 449.6 | 360.9 | 369.8 | 420.7 | 345.6 | 290.8 | 415.6
694 | 575 | 518.5 | 450.3 | 361.3 | 370.2 | 421.6 | 345.8 | 290.9 | 415.7
695 | 576 | 518.6 | 451.1 | 361.8 | 370.5 | 422.5 | 346 | 291.1 | 415.8
696 | 577 | 518.5 | 452.1 | 362.2 | 370.9 | 423.6 | 346.1 | 291.4 | 415.8
697 | 578 | 518.3 | 452.9 | 362.7 | 371.2 | 424.7 | 346.2 | 291.6 | 415.9
698 | 579 | 518.5 | 453.6 | 363.1 | 371.6 | 425.9 | 346.4 | 291.8 | 416
699 | 580 | 518.7 | 454.2 | 363.6 | 371.9 | 427 | 346.5 | 292 | 416
700 | 581 | 518.9 | 454.8 | 364.1 | 372.3 | 428.1 | 346.6 | 292.1 | 416.1
701 | 582 | 519 | 455.4 | 364.5 | 372.6 | 429.1 | 346.7 | 292.2 | 416.1
702 | 583 | 519 | 455.9 | 365 | 372.9 | 430.1 | 346.7 | 292.5 | 416.2
703 | 584 | 519.1 | 456.4 | 365.5 | 373.3 | 431.1 | 346.9 | 292.7 | 416.2
704 | 585 | 519.2 | 456.8 | 366.1 | 373.6 | 432 | 347 | 292.9 | 416.3
705 | 586 | 519.3 | 457 | 366.6 | 373.9 | 433 | 347.1 | 293.2 | 416.4
706 | 587 | 519.3 | 457 | 367.1 | 374.2 | 433.9 | 347.1 | 293.4 | 416.4
707 | 588 | 519.4 | 457 | 367.5 | 374.6 | 434.9 | 347.2 | 293.7 | 416.5
708 | 589 | 519.4 | 457 | 368 | 375 | 435.9 | 347.3 | 293.9 | 416.6
709 | 590 | 519.5 | 456.9 | 368.5 | 375.3 | 436.6 | 347.3 | 294.1 | 416.7
710 | 591 | 519.4 | 456.8 | 369 | 375.6 | 437 | 347.3 | 294.2 | 416.7
711 | 592 | 519.3 | 456.8 | 369.4 | 376 | 437.6 | 347.3 | 294.5 | 416.8
712 | 593 | 519.3 | 456.8 | 369.9 | 376.4 | 438.1 | 347.3 | 294.7 | 416.8
713 | 594 | 519.1 | 456.8 | 370.3 | 376.7 | 438.6 | 347.4 | 295 | 416.8
714 | 595 | 518.9 | 456.9 | 370.9 | 377.1 | 439.2 | 347.5 | 295.2 | 416.9
715 | 596 | 518.8 | 457 | 371.5 | 377.4 | 439.7 | 347.6 | 295.4 | 416.9
716 | 597 | 518.7 | 457.1 | 372.1 | 377.7 | 440.2 | 347.8 | 295.6 | 417
717 | 598 | 518.8 | 457.4 | 372.6 | 378.1 | 440.7 | 348 | 295.9 | 417
718 | 599 | 518.6 | 457.8 | 373.2 | 378.4 | 441.1 | 348 | 296 | 417.1
719 | 600 | 518.6 | 458.1 | 373.7 | 378.8 | 441.4 | 348 | 296.3 | 417.1
720 | 601 | 518.6 | 458.6 | 374.1 | 379.1 | 441.7 | 348.1 | 296.6 | 417.1
721 | 602 | 518.6 | 459.1 | 374.7 | 379.4 | 441.7 | 348.1 | 296.8 | 417.1
722 | 603 | 518.6 | 458.8 | 375.2 | 379.7 | 441.9 | 348.2 | 296.9 | 417.2
723 | 604 | 518.7 | 459.2 | 375.9 | 380.1 | 441.9 | 348.1 | 297 | 417.3
724 | 605 | 518.6 | 459.8 | 376.4 | 380.4 | 441.8 | 348.2 | 297.1 | 417.3
725 | 606 | 518.7 | 460.7 | 377 | 380.8 | 441.8 | 348.2 | 297.3 | 417.4
726 | 607 | 518.8 | 461.9 | 377.7 | 381.2 | 441.8 | 348.3 | 297.5 | 417.4
727 | 608 | 518.8 | 463.4 | 378.1 | 381.6 | 441.7 | 348.3 | 297.7 | 417.5
728 | 609 | 518.8 | 465.3 | 378.6 | 381.9 | 441.7 | 348.4 | 297.9 | 417.5
729 | 610 | 518.9 | 467.6 | 379.3 | 382.3 | 441.7 | 348.5 | 298 | 417.5
730 | 611 | 519.1 | 469.8 | 379.9 | 382.7 | 441.8 | 348.6 | 298.2 | 417.6
731 | 612 | 519.2 | 472.2 | 380.5 | 383 | 441.7 | 348.7 | 298.5 | 417.6
732 | 613 | 519.4 | 474.2 | 381 | 383.5 | 441.8 | 348.8 | 298.7 | 417.7
733 | 614 | 519.6 | 476.7 | 381.3 | 383.9 | 441.9 | 348.8 | 299 | 417.7
734 | 615 | 519.5 | 478.7 | 381.5 | 384.4 | 442.1 | 348.9 | 299.2 | 417.8
735 | 616 | 519.4 | 480.7 | 381.7 | 385 | 442.4 | 348.9 | 299.4 | 417.8
736 | 617 | 519.3 | 483.1 | 381.9 | 385.5 | 442.7 | 348.9 | 299.6 | 417.9
737 | 618 | 519.5 | 485.1 | 382.2 | 386 | 443 | 348.9 | 299.9 | 417.8
738 | 619 | 519.6 | 487.2 | 382.4 | 386.5 | 443.2 | 348.9 | 300.1 | 417.9
739 | 620 | 519.8 | 489.3 | 382.6 | 387.1 | 443.5 | 348.9 | 300.2 | 417.9
740 | 621 | 519.7 | 490.7 | 382.9 | 387.6 | 443.7 | 348.9 | 300.4 | 417.9
741 | 622 | 519.7 | 492.6 | 383.3 | 388.1 | 444 | 348.9 | 300.5 | 417.9
742 | 623 | 519.6 | 494.9 | 383.7 | 388.6 | 444.3 | 348.9 | 300.6 | 417.9
743 | 624 | 519.7 | 497.3 | 384 | 389.1 | 444.7 | 349 | 300.8 | 418
744 | 625 | 519.7 | 499.7 | 384.3 | 389.6 | 445.1 | 349 | 301 | 418
745 | 626 | 519.7 | 502 | 384.7 | 390.2 | 445.5 | 349.1 | 301.3 | 418.1
746 | 627 | 520 | 505.1 | 385 | 390.7 | 445.9 | 349.1 | 301.5 | 418.2
747 | 628 | 520.1 | 507.7 | 385.4 | 391.3 | 446.4 | 349.3 | 301.7 | 418.2
748 | 629 | 520.1 | 510.8 | 385.8 | 391.9 | 446.9 | 349.4 | 301.8 | 418.3
749 | 630 | 520.1 | 513.3 | 386.3 | 392.4 | 447.5 | 349.5 | 302 | 418.4
750 | 631 | 520.2 | 516.3 | 386.7 | 393 | 448.1 | 349.7 | 302.2 | 418.4
751 | 632 | 520.3 | 519.9 | 387.2 | 393.6 | 448.8 | 349.9 | 302.3 | 418.5
752 | 633 | 520.3 | 522.7 | 387.7 | 394.2 | 449.4 | 350.1 | 302.5 | 418.5
753 | 634 | 520.4 | 525.6 | 388.3 | 394.8 | 450.1 | 350.3 | 302.7 | 418.6
754 | 635 | 520.4 | 527.4 | 388.8 | 395.4 | 450.9 | 350.4 | 302.9 | 418.6
755 | 636 | 520.3 | 529.1 | 389.3 | 396 | 451.6 | 350.7 | 303.1 | 418.7
756 | 637 | 520.4 | 530.7 | 389.9 | 396.6 | 452.3 | 350.8 | 303.3 | 418.7
757 | 638 | 520.3 | 531.6 | 390.4 | 397.3 | 453 | 350.9 | 303.5 | 418.7
758 | 639 | 520.3 | 533.2 | 390.9 | 397.9 | 453.8 | 350.9 | 303.6 | 418.8
759 | 640 | 520.4 | 534.9 | 391.5 | 398.6 | 454.7 | 351 | 303.7 | 418.9
760 | 641 | 520.5 | 534.9 | 392 | 399.2 | 455.5 | 351.2 | 303.8 | 418.9
761 | 642 | 520.6 | 535.6 | 392.6 | 399.9 | 456.3 | 351.4 | 303.9 | 419
762 | 643 | 520.5 | 535.8 | 393.3 | 400.5 | 457 | 351.6 | 303.9 | 419.1
763 | 644 | 520.5 | 537.3 | 393.9 | 401.1 | 457.7 | 351.6 | 303.9 | 419.1
764 | 645 | 520.4 | 540.2 | 394.5 | 401.8 | 458.3 | 351.7 | 304 | 419.2
765 | 646 | 520.4 | 542.4 | 395.1 | 402.4 | 458.9 | 351.6 | 304.2 | 419.2
766 | 647 | 520.3 | 543.7 | 395.7 | 403 | 459.4 | 351.7 | 304.5 | 419.3
767 | 648 | 520.2 | 545.6 | 396.2 | 403.7 | 459.9 | 351.8 | 304.7 | 419.3
768 | 649 | 520.1 | 547.3 | 396.9 | 404.3 | 460.3 | 351.8 | 304.9 | 419.4
769 | 650 | 520.3 | 548.2 | 397.4 | 405 | 460.7 | 351.8 | 305 | 419.4
770 | 651 | 520.1 | 549.2 | 397.9 | 405.6 | 461.1 | 351.9 | 305.1 | 419.5
771 | 652 | 519.9 | 550.5 | 398.5 | 406.2 | 461.5 | 352.1 | 305.3 | 419.5
772 | 653 | 519.9 | 552.1 | 399.1 | 406.9 | 461.9 | 352.1 | 305.4 | 419.6
773 | 654 | 519.9 | 554.1 | 399.6 | 407.5 | 462.2 | 352.2 | 305.6 | 419.6
774 | 655 | 520.1 | 556.4 | 400.2 | 408.1 | 462.5 | 352.2 | 305.8 | 419.7
775 | 656 | 520.2 | 558.5 | 400.8 | 408.7 | 462.9 | 352.4 | 305.9 | 419.7
776 | 657 | 520.4 | 560.5 | 401.4 | 409.3 | 463.3 | 352.4 | 306.2 | 419.8
777 | 658 | 520.4 | 562.2 | 402 | 410 | 463.7 | 352.5 | 306.4 | 419.8
778 | 659 | 520.6 | 563.7 | 402.5 | 410.6 | 464 | 352.7 | 306.6 | 419.9
779 | 660 | 520.9 | 565.1 | 403.1 | 411.2 | 464.3 | 352.7 | 306.8 | 419.9
780 | 661 | 521 | 566.3 | 403.8 | 411.8 | 464.5 | 352.9 | 307 | 420
781 | 662 | 521.2 | 567.5 | 404.3 | 412.3 | 464.8 | 353 | 307.1 | 420
782 | 663 | 521.3 | 568.6 | 404.9 | 413 | 465.1 | 353.2 | 307.2 | 420.1
783 | 664 | 521.5 | 568.6 | 405.4 | 413.5 | 465.4 | 353.4 | 307.5 | 420.1
784 | 665 | 521.4 | 568.6 | 406 | 414.2 | 465.8 | 353.4 | 307.8 | 420.1
785 | 666 | 521.3 | 569.5 | 406.6 | 414.7 | 466.2 | 353.5 | 308.1 | 420.2
786 | 667 | 521.2 | 569.2 | 407.2 | 415.3 | 466.7 | 353.6 | 308.3 | 420.2
787 | 668 | 521.2 | 569.9 | 407.7 | 415.9 | 467.1 | 353.7 | 308.5 | 420.2
788 | 669 | 521.4 | 569.4 | 408.2 | 416.5 | 467.6 | 353.8 | 308.7 | 420.2
789 | 670 | 521.5 | 569.9 | 408.8 | 417.1 | 467.9 | 353.8 | 308.8 | 420.3
790 | 671 | 521.4 | 570.4 | 409.4 | 417.7 | 468.3 | 353.9 | 309 | 420.3
791 | 672 | 521.4 | 572 | 410 | 418.2 | 468.6 | 353.9 | 309 | 420.4
792 | 673 | 521.5 | 574.1 | 410.6 | 418.8 | 468.8 | 354 | 309.2 | 420.4
793 | 674 | 521.2 | 575.3 | 411.1 | 419.4 | 469.1 | 354.1 | 309.4 | 420.5
794 | 675 | 521 | 575.7 | 411.7 | 420 | 469.3 | 354.2 | 309.6 | 420.6
795 | 676 | 521 | 576.8 | 412.2 | 420.5 | 469.6 | 354.2 | 309.8 | 420.6
796 | 677 | 521 | 577.1 | 412.7 | 421.1 | 470 | 354.2 | 310 | 420.7
797 | 678 | 520.9 | 576.9 | 413.2 | 421.7 | 470.3 | 354.3 | 310.1 | 420.7
798 | 679 | 520.9 | 577.7 | 413.6 | 422.2 | 470.7 | 354.4 | 310.4 | 420.8
799 | 680 | 520.8 | 577.5 | 414.2 | 422.8 | 470.9 | 354.4 | 310.5 | 420.9
800 | 681 | 520.8 | 576.5 | 414.8 | 423.3 | 471.2 | 354.5 | 310.7 | 420.9
801 | 682 | 520.8 | 575 | 415.4 | 423.8 | 471.5 | 354.6 | 310.8 | 421
802 | 683 | 520.7 | 574.3 | 416 | 424.2 | 471.8 | 354.7 | 310.9 | 421
803 | 684 | 520.5 | 574.3 | 416.7 | 424.6 | 472.1 | 354.9 | 311.1 | 421.1
804 | 685 | 520.5 | 574.8 | 417.3 | 425.1 | 472.3 | 355 | 311.1 | 421.2
805 | 686 | 520.5 | 574 | 417.9 | 425.5 | 472.6 | 355.2 | 311.2 | 421.2
806 | 687 | 520.5 | 573.6 | 418.5 | 425.9 | 472.8 | 355.4 | 311.3 | 421.2
807 | 688 | 520.3 | 573.1 | 419 | 426.3 | 473.2 | 355.6 | 311.6 | 421.3
808 | 689 | 520.2 | 572.9 | 419.5 | 426.8 | 473.6 | 355.7 | 311.7 | 421.4
809 | 690 | 520 | 572.2 | 420.1 | 427.2 | 473.8 | 356.1 | 311.8 | 421.4
810 | 691 | 520 | 569.3 | 420.7 | 427.6 | 474 | 356.3 | 311.9 | 421.4
811 | 692 | 519.9 | 568.6 | 421.3 | 428 | 474.2 | 356.4 | 312.1 | 421.5
812 | 693 | 520 | 568.6 | 421.8 | 428.4 | 474.5 | 356.5 | 312.2 | 421.6
813 | 694 | 519.9 | 567 | 422.4 | 428.7 | 474.7 | 356.6 | 312.2 | 421.6
814 | 695 | 519.8 | 565.1 | 422.9 | 429.1 | 475 | 356.7 | 312.3 | 421.7
815 | 696 | 519.5 | 564.6 | 423.4 | 429.5 | 475.5 | 356.9 | 312.4 | 421.8
816 | 697 | 519.3 | 562.9 | 423.9 | 429.9 | 475.9 | 356.9 | 312.5 | 421.9
817 | 698 | 519.5 | 560.5 | 424.4 | 430.3 | 476.3 | 357 | 312.5 | 421.9
818 | 699 | 519.6 | 558.3 | 424.8 | 430.7 | 476.8 | 357.2 | 312.7 | 422
819 | 700 | 519.4 | 556.8 | 425.3 | 431.1 | 477.4 | 357.4 | 312.9 | 422
820 | 701 | 519.2 | 556.9 | 425.7 | 431.5 | 477.9 | 357.5 | 313 | 422.1
821 | 702 | 519.2 | 555.4 | 426.2 | 432 | 478.2 | 357.5 | 313.1 | 422.2
822 | 703 | 519.2 | 554.1 | 426.7 | 432.4 | 478.5 | 357.5 | 313.3 | 422.2
823 | 704 | 519.1 | 554 | 427.3 | 433 | 478.9 | 357.7 | 313.4 | 422.3
824 | 705 | 519.1 | 552.5 | 427.7 | 433.6 | 479.5 | 357.8 | 313.6 | 422.4
825 | 706 | 519.2 | 550.5 | 428.2 | 434.2 | 480.2 | 357.8 | 313.7 | 422.4
826 | 707 | 519 | 549 | 428.6 | 434.9 | 480.7 | 357.9 | 313.8 | 422.5
827 | 708 | 519.1 | 547.4 | 429 | 435.5 | 481.1 | 358 | 313.9 | 422.5
828 | 709 | 519.2 | 546.4 | 429.4 | 436.3 | 481.7 | 358.1 | 314.1 | 422.6
829 | 710 | 519.3 | 546.2 | 429.9 | 437 | 482.2 | 358.2 | 314.2 | 422.7
830 | 711 | 519.5 | 545.9 | 430.4 | 437.7 | 482.5 | 358.4 | 314.3 | 422.7
831 | 712 | 520 | 544 | 430.9 | 438.5 | 482.9 | 358.5 | 314.5 | 422.8
832 | 713 | 520.1 | 543 | 431.4 | 439.4 | 483.3 | 358.6 | 314.7 | 422.9
833 | 714 | 520.2 | 543.2 | 432.2 | 440.2 | 483.7 | 358.7 | 314.9 | 422.9
834 | 715 | 520.2 | 542.9 | 432.9 | 441.1 | 483.8 | 358.8 | 315.1 | 423
835 | 716 | 520.3 | 542.4 | 433.7 | 441.9 | 484 | 359 | 315.4 | 423
836 | 717 | 520.2 | 541.9 | 434.4 | 442.8 | 484.3 | 359.2 | 315.6 | 423.1
837 | 718 | 520.2 | 540.9 | 435.1 | 443.6 | 484.6 | 359.3 | 315.8 | 423.1
838 | 719 | 520.2 | 540.8 | 435.7 | 444.5 | 484.9 | 359.4 | 316.1 | 423.2
839 | 720 | 520.5 | 541.6 | 436.3 | 445.4 | 485 | 359.5 | 316.4 | 423.3
840 | 721 | 520.8 | 542.2 | 436.9 | 446.2 | 485.4 | 359.5 | 316.7 | 423.4
841 | 722 | 520.9 | 542.9 | 437.4 | 447.1 | 486 | 359.6 | 316.9 | 423.4
842 | 723 | 520.8 | 544.6 | 438 | 448 | 486.3 | 359.8 | 317.1 | 423.4
843 | 724 | 520.6 | 544.5 | 438.5 | 448.9 | 486.5 | 360 | 317.2 | 423.5
844 | 725 | 520.5 | 543.1 | 439.1 | 449.8 | 486.6 | 360.2 | 317.3 | 423.5
845 | 726 | 520.4 | 541.3 | 439.6 | 450.8 | 486.6 | 360.5 | 317.4 | 423.5
846 | 727 | 520.3 | 540.8 | 440.2 | 451.9 | 486.7 | 360.7 | 317.5 | 423.6
847 | 728 | 520.2 | 540.1 | 440.7 | 452.9 | 486.7 | 360.7 | 317.6 | 423.6
848 | 729 | 520.1 | 538.9 | 441.2 | 453.8 | 486.6 | 360.8 | 317.8 | 423.7
849 | 730 | 519.9 | 538.8 | 441.7 | 454.9 | 486.8 | 360.9 | 317.9 | 423.8
850 | 731 | 519.8 | 539.3 | 442.2 | 455.8 | 487 | 361 | 318 | 423.8
851 | 732 | 519.8 | 539.2 | 442.7 | 456.8 | 487.2 | 361 | 318.2 | 423.8
852 | 733 | 519.6 | 539.3 | 443.2 | 457.7 | 487.7 | 361.1 | 318.4 | 423.9
853 | 734 | 519.4 | 538.4 | 443.7 | 458.7 | 488.9 | 361.2 | 318.7 | 424
854 | 735 | 519.4 | 539.5 | 444.1 | 459.7 | 489.9 | 361.1 | 318.9 | 424
855 | 736 | 519.5 | 539.3 | 444.5 | 460.6 | 490.9 | 361.1 | 319.1 | 424.1
856 | 737 | 519.6 | 539.7 | 444.9 | 461.5 | 492.2 | 361.1 | 319.3 | 424.1
857 | 738 | 519.6 | 539.7 | 445.3 | 462.3 | 493.3 | 361.2 | 319.5 | 424.1
858 | 739 | 519.5 | 541.8 | 445.7 | 463 | 493.8 | 361.2 | 319.7 | 424.1
859 | 740 | 519.5 | 542.9 | 446.2 | 463.7 | 494.8 | 361.4 | 319.9 | 424.1
860 | 741 | 519.4 | 541.8 | 446.7 | 464.3 | 496 | 361.4 | 320.1 | 424
861 | 742 | 519.4 | 540.9 | 447.3 | 464.8 | 496.4 | 361.5 | 320.2 | 424.1
862 | 743 | 519.6 | 541.3 | 447.8 | 465.3 | 497.1 | 361.6 | 320.4 | 424.1
863 | 744 | 519.9 | 540.3 | 448.4 | 465.7 | 497.5 | 361.8 | 320.5 | 424.1
864 | 745 | 519.9 | 538.9 | 449.1 | 466.1 | 498.1 | 361.9 | 320.6 | 424.1
865 | 746 | 520 | 537.7 | 449.7 | 466.4 | 498.4 | 362.2 | 320.7 | 424.1
866 | 747 | 520 | 535.7 | 450.3 | 466.8 | 499 | 362.3 | 320.9 | 424.1
867 | 748 | 520.1 | 535.3 | 450.9 | 467.1 | 499.2 | 362.3 | 320.9 | 424.2
868 | 749 | 520.2 | 535.2 | 451.5 | 467.4 | 499.3 | 362.3 | 320.9 | 424.1
869 | 750 | 520.1 | 535.2 | 452.2 | 467.6 | 499.2 | 362.4 | 321.1 | 424.2
870 | 751 | 520.2 | 535.1 | 452.9 | 467.9 | 499.2 | 362.5 | 321.3 | 424.2
871 | 752 | 520.1 | 536.6 | 453.7 | 468.3 | 499.1 | 362.6 | 321.5 | 424.2
872 | 753 | 520.1 | 537 | 454.6 | 468.6 | 498.9 | 362.7 | 321.6 | 424.3
873 | 754 | 520.1 | 535.5 | 455.3 | 468.8 | 498.9 | 362.7 | 321.7 | 424.3
874 | 755 | 520.1 | 533.6 | 455.9 | 469 | 499.3 | 362.8 | 321.8 | 424.4
875 | 756 | 520.1 | 532.8 | 456.6 | 469.1 | 499.6 | 362.9 | 321.9 | 424.4
876 | 757 | 520.1 | 531.9 | 457.2 | 469.3 | 500.1 | 363.1 | 322 | 424.5
877 | 758 | 520 | 531.3 | 457.8 | 469.4 | 500 | 363.3 | 322 | 424.5
878 | 759 | 519.9 | 530.3 | 458.4 | 469.6 | 499.9 | 363.6 | 322.1 | 424.6
879 | 760 | 519.6 | 528.6 | 458.9 | 469.8 | 500.4 | 363.7 | 322.2 | 424.6
880 | 761 | 519.4 | 528.1 | 459.5 | 470 | 500.8 | 363.8 | 322.4 | 424.7
881 | 762 | 519.3 | 529.2 | 460.1 | 470.2 | 500.7 | 363.8 | 322.5 | 424.7
882 | 763 | 519.3 | 528.2 | 461.2 | 470.5 | 501 | 364 | 322.7 | 424.7
883 | 764 | 519.3 | 528.9 | 462 | 470.7 | 501 | 364.1 | 322.9 | 424.8
884 | 765 | 519.3 | 532.3 | 462.8 | 471.2 | 501.2 | 364.2 | 323.2 | 424.8
885 | 766 | 519.2 | 545.3 | 463.7 | 472.5 | 502.4 | 364.4 | 323.4 | 424.9
886 | 767 | 519.2 | 555.9 | 464.7 | 474.1 | 504.9 | 364.4 | 323.5 | 425
887 | 768 | 519.3 | 566.4 | 465.4 | 476.3 | 508.5 | 364.3 | 323.7 | 425.1
888 | 769 | 519.3 | 577.6 | 466.3 | 479.3 | 511.7 | 364.3 | 323.9 | 425.2
889 | 770 | 519.5 | 587.4 | 467.1 | 482.4 | 515 | 364.3 | 324.1 | 425.4
890 | 771 | 519.8 | 594.2 | 468 | 485.3 | 518.7 | 364.6 | 324.2 | 425.7
891 | 772 | 520.2 | 595 | 469.3 | 488.3 | 522.5 | 365.5 | 324.3 | 426
892 | 773 | 520.5 | 592.4 | 470.5 | 490.8 | 525.4 | 366.4 | 324.4 | 426.5
893 | 774 | 520.7 | 589.6 | 471.6 | 492.8 | 527.4 | 368.1 | 324.5 | 427
894 | 775 | 521.1 | 587.8 | 472.9 | 494.4 | 529.1 | 370.9 | 324.6 | 427.6
895 | 776 | 521.5 | 586.6 | 474.3 | 495.9 | 531.8 | 374.6 | 324.7 | 428.3
896 | 777 | 521.8 | 586.4 | 475.7 | 497.5 | 534.5 | 380.2 | 324.9 | 429.1
897 | 778 | 522 | 586.8 | 477.2 | 499.3 | 536.6 | 386.6 | 325 | 430
898 | 779 | 522.4 | 587.2 | 478.7 | 500.5 | 538.2 | 394 | 325.1 | 431.1
899 | 780 | 522.4 | 588.1 | 480.3 | 502.4 | 539.8 | 402.2 | 325.4 | 432.4
900 | 781 | 522.5 | 589.8 | 481.8 | 504.7 | 541.4 | 411.7 | 325.4 | 433.7
901 | 782 | 522.4 | 590.1 | 483.3 | 506.8 | 543 | 418.9 | 325.5 | 435.1
902 | 783 | 522.3 | 589.7 | 484.8 | 508.9 | 544.5 | 426.1 | 325.5 | 436.6
903 | 784 | 522.4 | 589.4 | 486.3 | 511.1 | 545.5 | 433.2 | 325.7 | 438.1
904 | 785 | 522.2 | 589.2 | 488.1 | 512.8 | 546.7 | 441.3 | 325.9 | 439.7
905 | 786 | 521.9 | 589.2 | 489.9 | 514.4 | 548.2 | 451.2 | 326.1 | 441.2
906 | 787 | 521.6 | 588.3 | 491.5 | 515.9 | 549.4 | 456.3 | 326.2 | 442.7
907 | 788 | 521.4 | 586.2 | 492.6 | 516.9 | 550.3 | 459 | 326.4 | 444.2
908 | 789 | 520.8 | 584.5 | 493.8 | 517.6 | 551.1 | 462.1 | 326.6 | 445.7
909 | 790 | 520.4 | 583.2 | 495.3 | 518.4 | 552 | 466.8 | 326.9 | 447.2
910 | 791 | 520.2 | 581.7 | 496.7 | 519.3 | 553.3 | 472.1 | 327.1 | 448.7
911 | 792 | 519.9 | 580.7 | 497.8 | 520.1 | 555 | 477.1 | 327.3 | 450.2
912 | 793 | 519.7 | 580.3 | 498.9 | 521 | 556.6 | 481.6 | 327.4 | 451.6
913 | 794 | 519.5 | 580.3 | 500.1 | 521.7 | 558.5 | 484.2 | 327.6 | 453.1
914 | 795 | 519.4 | 579.6 | 501.7 | 522.3 | 560.5 | 483.7 | 327.8 | 454.6
915 | 796 | 519.3 | 579 | 503.1 | 522.7 | 563.1 | 484.6 | 328 | 456
916 | 797 | 519.3 | 578.2 | 505.9 | 523 | 565.5 | 486.4 | 328.2 | 457.5
917 | 798 | 519 | 578 | 507.2 | 523.7 | 569.4 | 488.1 | 328.4 | 458.9
918 | 799 | 518.7 | 576.9 | 508.5 | 524.4 | 573.4 | 488.4 | 328.6 | 460.3
919 | 800 | 518.2 | 576 | 509.8 | 524.9 | 576.9 | 490.5 | 328.8 | 461.6
920 | 801 | 517.7 | 575.6 | 510.9 | 525.4 | 580.2 | 492.2 | 328.9 | 462.9
921 | 802 | 517 | 574.6 | 512.2 | 526.1 | 582.9 | 492.2 | 329.1 | 464.2
922 | 803 | 516.1 | 574.5 | 513.6 | 526.8 | 585.1 | 492.5 | 329.3 | 465.5
923 | 804 | 515.3 | 573.7 | 515.1 | 527.8 | 586.8 | 492.7 | 329.4 | 466.8
924 | 805 | 514.5 | 572.7 | 516.5 | 528.7 | 588.7 | 490.3 | 329.5 | 468.1
925 | 806 | 513.5 | 571.5 | 518 | 529.6 | 590 | 486.3 | 329.7 | 469.3
926 | 807 | 512.5 | 570.7 | 519.6 | 530.5 | 592.2 | 485 | 329.7 | 470.6
927 | 808 | 511.4 | 570.9 | 521.2 | 531.5 | 594.9 | 487.7 | 329.7 | 471.8
928 | 809 | 510.4 | 570.9 | 522.9 | 532.4 | 596.3 | 490.1 | 329.8 | 473.1
929 | 810 | 509.4 | 570.7 | 524.6 | 533.4 | 597.7 | 489.8 | 329.9 | 474.2
930 | 811 | 508.4 | 571.2 | 526.2 | 534.5 | 599.7 | 491.6 | 330 | 475.4
931 | 812 | 507.4 | 571.1 | 527.9 | 535.5 | 600.8 | 492 | 330.1 | 476.6
932 | 813 | 506.2 | 572.2 | 529.5 | 536.5 | 601.5 | 492.3 | 330.2 | 477.8
933 | 814 | 505.1 | 572.6 | 531.2 | 537.6 | 602.2 | 489.9 | 330.2 | 478.9
934 | 815 | 504.1 | 573.6 | 532.7 | 538.6 | 602.9 | 491.2 | 330.4 | 479.9
935 | 816 | 503.3 | 574.1 | 534.2 | 539.9 | 603.8 | 488.7 | 330.5 | 481
936 | 817 | 502.4 | 574.9 | 535.5 | 541.1 | 605.3 | 484.8 | 330.6 | 482.1
937 | 818 | 501.4 | 576.1 | 537 | 542.3 | 606.9 | 483.8 | 330.8 | 483.1
938 | 819 | 500.5 | 576.1 | 538.5 | 543.4 | 607.5 | 482.3 | 330.8 | 484.1
939 | 820 | 499.7 | 577 | 539.8 | 544.6 | 609 | 481 | 330.8 | 485.1
940 | 821 | 498.7 | 577.7 | 541.1 | 546.1 | 610.9 | 481.1 | 330.9 | 486
941 | 822 | 497.3 | 579.7 | 542.5 | 547.7 | 612.8 | 482.8 | 331 | 486.9
942 | 823 | 496.2 | 581.3 | 543.9 | 549.3 | 614.1 | 481.3 | 331.1 | 487.7
943 | 824 | 495.2 | 583 | 545.1 | 550.6 | 614.3 | 480 | 331.2 | 488.6
944 | 825 | 494.3 | 584.1 | 546.6 | 551.8 | 615.7 | 479.6 | 331.4 | 489.4
945 | 826 | 493.3 | 585.8 | 548 | 553 | 617.1 | 479.1 | 331.5 | 490.1
946 | 827 | 492.2 | 588.3 | 549.7 | 554.3 | 618.6 | 479.8 | 331.7 | 490.9
947 | 828 | 491 | 590.7 | 551.4 | 555.6 | 619.9 | 481 | 331.8 | 491.7
948 | 829 | 489.9 | 593.1 | 552.8 | 557 | 620 | 480 | 331.9 | 492.4
949 | 830 | 488.8 | 595.9 | 554.4 | 558.2 | 620.3 | 479.6 | 331.9 | 493.2
950 | 831 | 487.8 | 599.5 | 555.9 | 559.4 | 621.4 | 479.7 | 332 | 493.9
951 | 832 | 486.7 | 602.4 | 557.4 | 560.5 | 622.5 | 480.1 | 332.1 | 494.6
952 | 833 | 485.6 | 605.3 | 558.9 | 561.6 | 623.4 | 479.3 | 332.2 | 495.3
953 | 834 | 484.5 | 609.2 | 560.6 | 562.5 | 624.5 | 479.7 | 332.3 | 495.8
954 | 835 | 483.4 | 612.7 | 562.2 | 563.5 | 624.8 | 479.9 | 332.5 | 496.4
955 | 836 | 482.4 | 616.4 | 563.8 | 564.8 | 624.9 | 480.1 | 332.6 | 497
956 | 837 | 481.5 | 620 | 565.6 | 566.2 | 625 | 480.7 | 332.8 | 497.6
957 | 838 | 480.5 | 622.5 | 567.2 | 567.6 | 625.1 | 480.6 | 332.9 | 498.2
958 | 839 | 479.4 | 626 | 568.9 | 569.1 | 626.1 | 480.3 | 333.1 | 498.8
959 | 840 | 478.4 | 628.1 | 570.6 | 570.8 | 627.1 | 480.5 | 333.4 | 499.3
960 | 841 | 477.5 | 628.7 | 572.3 | 572.2 | 627.8 | 480.4 | 333.6 | 499.9
961 | 842 | 476.4 | 630.3 | 574.2 | 573.3 | 628.2 | 481 | 333.7 | 500.3
962 | 843 | 475.2 | 632 | 576 | 574.4 | 627.8 | 481.1 | 333.9 | 500.9
963 | 844 | 474.2 | 632.6 | 577.8 | 575.7 | 626.9 | 482 | 334.1 | 501.3
964 | 845 | 473.1 | 631.4 | 579.8 | 577.9 | 627.3 | 485.5 | 334.3 | 501.7
965 | 846 | 472.1 | 631.6 | 581.4 | 580.9 | 628.9 | 491.4 | 334.4 | 502.1
966 | 847 | 471.1 | 632.2 | 582.7 | 583.7 | 630.5 | 496 | 334.5 | 502.4
967 | 848 | 470.1 | 633.5 | 583.9 | 586.3 | 631.8 | 499.2 | 334.6 | 502.7
968 | 849 | 469.2 | 634.9 | 585.2 | 588.1 | 632.4 | 501.6 | 334.7 | 503
969 | 850 | 468.4 | 637.3 | 586.5 | 589.5 | 633.2 | 505.7 | 334.9 | 503.2
970 | 851 | 467.6 | 638.3 | 587.8 | 591.5 | 634.8 | 509.5 | 335.1 | 503.4
971 | 852 | 466.8 | 639 | 589 | 593.3 | 636.9 | 512.6 | 335.3 | 503.5
972 | 853 | 466 | 640.4 | 590.3 | 594.4 | 638.3 | 514.6 | 335.4 | 503.6
973 | 854 | 465.2 | 643.4 | 591.6 | 595.5 | 639.7 | 516.5 | 335.5 | 503.7
974 | 855 | 464.3 | 644.6 | 592.8 | 596.9 | 642.4 | 518.8 | 335.6 | 503.7
975 | 856 | 463.2 | 643.9 | 594 | 599.4 | 645.6 | 520.4 | 335.7 | 503.6
976 | 857 | 462.1 | 641.9 | 595.3 | 602 | 649.2 | 520.9 | 336 | 503.4
977 | 858 | 461.1 | 638.9 | 596.6 | 604.3 | 653.3 | 522.3 | 336.3 | 503.2
978 | 859 | 460 | 635.8 | 597.9 | 606.4 | 657.4 | 523.5 | 336.6 | 502.9
979 | 860 | 458.9 | 635.3 | 599 | 607.6 | 661.1 | 525.7 | 336.8 | 502.7
980 | 861 | 457.9 | 638.1 | 600.1 | 607.9 | 663.7 | 525.5 | 337.1 | 502.4
981 | 862 | 456.9 | 640.2 | 601.3 | 608 | 664.9 | 524.8 | 337.3 | 502.1
982 | 863 | 455.9 | 640.1 | 602.4 | 608.2 | 666.6 | 524.1 | 337.4 | 501.8
983 | 864 | 454.9 | 642.2 | 603.3 | 608.3 | 668.3 | 524.5 | 337.6 | 501.5
984 | 865 | 453.7 | 645.2 | 604.3 | 608.3 | 668.8 | 523.7 | 337.7 | 501.2
985 | 866 | 452.6 | 648.1 | 605.2 | 608.3 | 668.7 | 524.3 | 337.9 | 500.8
986 | 867 | 451.7 | 650.7 | 605.9 | 608.7 | 669.2 | 522.8 | 338.1 | 500.5
987 | 868 | 450.9 | 651.5 | 607.2 | 609.2 | 669.2 | 522 | 338.2 | 500.2
988 | 869 | 450 | 650.6 | 608.2 | 610.2 | 671.4 | 522.4 | 338.4 | 500
989 | 870 | 449.2 | 647.8 | 609.1 | 612.1 | 675.6 | 522.5 | 338.6 | 499.7
990 | 871 | 448.3 | 650.5 | 610 | 612.8 | 674.9 | 522.9 | 338.7 | 499.4
991 | 872 | 447.4 | 652.2 | 610.9 | 613 | 672.7 | 521.8 | 338.9 | 499
992 | 873 | 446.5 | 653 | 612 | 613.5 | 671.7 | 520.9 | 339.1 | 498.7
993 | 874 | 445.5 | 655.7 | 612.9 | 614.1 | 669.9 | 520.7 | 339.3 | 498.3
994 | 875 | 444.5 | 658.1 | 614 | 614.7 | 667.6 | 519.1 | 339.6 | 498
995 | 876 | 443.6 | 661.7 | 615.1 | 615.2 | 668.4 | 518 | 339.7 | 497.6
996 | 877 | 442.7 | 660 | 615.9 | 616.1 | 672.1 | 516.8 | 340 | 497.3
997 | 878 | 441.9 | 658 | 616.8 | 617.1 | 675.2 | 516 | 340.5 | 496.9
998 | 879 | 441.1 | 653.7 | 617.6 | 619 | 679.9 | 514.2 | 341 | 496.5
999 | 880 | 440.4 | 649 | 618.5 | 621.1 | 684.6 | 513.4 | 341.5 | 496.2
1000 | 881 | 439.7 | 646.2 | 619.1 | 623.1 | 687.8 | 513.2 | 341.7 | 495.8
1001 | 882 | 438.7 | 646.6 | 619.8 | 625.4 | 693.9 | 513.1 | 342 | 495.4
1002 | 883 | 437.9 | 652.9 | 620.4 | 627.3 | 698 | 512.2 | 342.3 | 495.1
1003 | 884 | 437 | 653.3 | 620.9 | 628.7 | 700.2 | 511 | 342.6 | 494.7
1004 | 885 | 436.1 | 655 | 621.6 | 629.9 | 702.2 | 508.3 | 342.9 | 494.2
1005 | 886 | 435.1 | 655.3 | 622.2 | 631.2 | 704 | 507.2 | 343.1 | 493.9
1006 | 887 | 434.2 | 659 | 622.6 | 632.2 | 704.6 | 507.2 | 343.5 | 493.6
1007 | 888 | 433.3 | 665.4 | 623.1 | 633.3 | 705.6 | 506.9 | 343.7 | 493.4
1008 | 889 | 432.5 | 667.8 | 623.2 | 634.4 | 705 | 507.6 | 344 | 493.2
1009 | 890 | 431.7 | 672.1 | 623.7 | 635.7 | 704.3 | 507.9 | 344.3 | 492.9
1010 | 891 | 430.8 | 675.3 | 624.3 | 636.5 | 705 | 510.1 | 344.5 | 492.6
1011 | 892 | 429.9 | 679.3 | 625.1 | 637.1 | 703.6 | 511.3 | 344.7 | 492.5
1012 | 893 | 429.3 | 680 | 625.8 | 637.4 | 700 | 512.8 | 344.8 | 492.3
1013 | 894 | 428.6 | 680.5 | 626.4 | 637.5 | 697.1 | 513.4 | 345 | 492
1014 | 895 | 427.9 | 683.1 | 627.1 | 637.4 | 693.5 | 514.1 | 345.2 | 491.8
1015 | 896 | 427.4 | 686.3 | 627.8 | 637.4 | 693.4 | 513.7 | 345.5 | 491.6
1016 | 897 | 426.7 | 687.1 | 628.3 | 637.6 | 695 | 512.4 | 345.7 | 491.3
1017 | 898 | 425.7 | 688.7 | 629 | 637.8 | 695.5 | 512.7 | 345.9 | 491
1018 | 899 | 424.7 | 690.1 | 629.9 | 637.8 | 694.3 | 514.5 | 346.1 | 490.9
1019 | 900 | 423.7 | 691.2 | 630.5 | 637.8 | 692.9 | 515.9 | 346.3 | 490.6
1020 | 901 | 422.7 | 698.8 | 631 | 637.9 | 692.2 | 515.8 | 346.6 | 490.4
1021 | 902 | 421.9 | 710 | 631.6 | 637.2 | 692.8 | 516 | 346.8 | 490.2
1022 | 903 | 421.1 | 720.2 | 632.3 | 637.7 | 696.9 | 516.7 | 347.1 | 490
1023 | 904 | 420.4 | 730.3 | 632.8 | 639.2 | 702.2 | 517.7 | 347.4 | 489.8
1024 | 905 | 419.7 | 738.8 | 633.4 | 641.1 | 705.5 | 519 | 347.7 | 489.6
1025 | 906 | 419.1 | 746.8 | 634.3 | 642.2 | 707 | 520.6 | 348 | 489.5
1026 | 907 | 418.3 | 751 | 635 | 644.1 | 713.5 | 521.4 | 348.2 | 489.3
1027 | 908 | 417.5 | 754.6 | 635.8 | 646.4 | 720.5 | 521.5 | 348.5 | 489.2
1028 | 909 | 416.7 | 761.1 | 636.5 | 648.4 | 725.6 | 522.3 | 348.8 | 489.1
1029 | 910 | 415.9 | 765 | 637.4 | 649.9 | 729.2 | 523.1 | 349.2 | 489
1030 | 911 | 415.1 | 765.9 | 637.9 | 650.7 | 729.3 | 523.4 | 349.6 | 488.9
1031 | 912 | 414.3 | 765.4 | 639 | 650.7 | 728.1 | 523.7 | 350 | 488.9
1032 | 913 | 413.5 | 762.3 | 640 | 651 | 728.4 | 523.5 | 350.3 | 488.8
1033 | 914 | 412.9 | 758.9 | 640.6 | 651.5 | 728.8 | 523.1 | 350.7 | 488.8
1034 | 915 | 412.2 | 755 | 641.2 | 652.3 | 727.9 | 523.7 | 350.9 | 488.8
1035 | 916 | 411.5 | 749.8 | 641.9 | 652.3 | 724.7 | 524 | 351.2 | 488.9
1036 | 917 | 410.7 | 743.3 | 642.6 | 652.5 | 721.9 | 524.2 | 351.5 | 489
1037 | 918 | 409.9 | 735.9 | 643.2 | 652.7 | 719.8 | 524.4 | 351.8 | 489
1038 | 919 | 409.2 | 728 | 643.8 | 653 | 715.8 | 524.2 | 352.1 | 489.1
1039 | 920 | 408.4 | 719.9 | 644.8 | 653.6 | 710.5 | 523.8 | 352.5 | 489.1
1040 | 921 | 407.5 | 714 | 645.4 | 654.4 | 706.4 | 523.2 | 352.7 | 489.1
1041 | 922 | 406.9 | 709.4 | 646.1 | 654.5 | 704 | 522.5 | 352.9 | 489.2
1042 | 923 | 406.3 | 704.2 | 646.7 | 654.6 | 702.2 | 522.4 | 353.1 | 489.2
1043 | 924 | 405.6 | 698.6 | 647.5 | 655.2 | 698.6 | 523 | 353.3 | 489.3
1044 | 925 | 404.8 | 693.6 | 648.1 | 656.4 | 696.1 | 522.9 | 353.5 | 489.3
1045 | 926 | 404 | 689 | 648.8 | 656.8 | 693.2 | 523.8 | 353.6 | 489.2
1046 | 927 | 403.2 | 685.5 | 649.6 | 656.8 | 691.4 | 527.3 | 353.8 | 489.3
1047 | 928 | 402.4 | 683 | 649.7 | 657 | 692.5 | 529.9 | 353.9 | 489.3
1048 | 929 | 401.8 | 681.1 | 650.2 | 656.8 | 694.8 | 531.9 | 354.1 | 489.3
1049 | 930 | 401.3 | 679 | 650.8 | 657.4 | 695.7 | 533.9 | 354.2 | 489.3
1050 | 931 | 400.6 | 676.7 | 651 | 657.6 | 695.4 | 534.4 | 354.3 | 489.3
1051 | 932 | 399.8 | 673.9 | 651.3 | 657.8 | 693.9 | 534.7 | 354.4 | 489.4
1052 | 933 | 398.9 | 671.9 | 652 | 658.6 | 694.6 | 533.6 | 354.6 | 489.5
1053 | 934 | 398.1 | 669 | 652.9 | 659.3 | 693.5 | 533.4 | 354.8 | 489.5
1054 | 935 | 397.4 | 666.4 | 653.4 | 659.9 | 691 | 534.1 | 355 | 489.6
1055 | 936 | 396.8 | 664.4 | 653.9 | 660.4 | 687.9 | 534.5 | 355.2 | 489.7
1056 | 937 | 396 | 662.6 | 654.3 | 661.1 | 687.1 | 534.3 | 355.5 | 489.8
1057 | 938 | 395.1 | 661.3 | 654.6 | 661.7 | 687.5 | 535.4 | 355.7 | 489.8
1058 | 939 | 394.3 | 659.1 | 655 | 662.4 | 688.1 | 536.7 | 355.9 | 489.8
1059 | 940 | 393.7 | 656.6 | 655.6 | 662.7 | 688.2 | 538.3 | 356 | 489.9
1060 | 941 | 393.1 | 654.7 | 656.3 | 662.9 | 686.5 | 539.8 | 356.3 | 489.9
1061 | 942 | 392.4 | 652.8 | 656 | 664.4 | 685.5 | 542.1 | 356.6 | 489.9
1062 | 943 | 391.8 | 650.5 | 656.8 | 664.6 | 683.8 | 545.2 | 356.9 | 490
1063 | 944 | 391 | 648.5 | 657.2 | 664.7 | 683.1 | 548.7 | 357.3 | 490
1064 | 945 | 390.3 | 646.9 | 657 | 667.1 | 683.3 | 552.7 | 357.7 | 490
1065 | 946 | 389.7 | 644.8 | 657.5 | 669.3 | 680 | 556.8 | 358 | 490.1
1066 | 947 | 388.9 | 643.4 | 657.6 | 668.9 | 680 | 561 | 358.3 | 490.1
1067 | 948 | 388.2 | 642.6 | 657.8 | 668.1 | 678.5 | 564.9 | 358.6 | 490.2
1068 | 949 | 387.4 | 640.8 | 657.7 | 668.2 | 676.7 | 569.1 | 358.9 | 490.2
1069 | 950 | 386.7 | 639 | 657.8 | 670.4 | 673.9 | 572.6 | 359.2 | 490.2
1070 | 951 | 386.2 | 637.2 | 658.2 | 671.3 | 672.9 | 575.6 | 359.5 | 490.2
1071 | 952 | 385.3 | 635.4 | 658.6 | 671.5 | 671.5 | 578.4 | 359.7 | 490.2
1072 | 953 | 384.4 | 633.5 | 658.8 | 672.4 | 669.7 | 580.9 | 360 | 490.1
1073 | 954 | 383.5 | 631.5 | 659 | 673.1 | 668.7 | 584.2 | 360.3 | 490.1
1074 | 955 | 382.7 | 630.1 | 659.2 | 674 | 667.4 | 587.7 | 360.6 | 490
1075 | 956 | 381.4 | 631 | 653.8 | 678.6 | 669.3 | 593.5 | 360.6 | 489.5
1076 | 957 | 380.9 | 627.8 | 658.2 | 677.6 | 664.5 | 597.1 | 360.9 | 489.7
1077 | 958 | 380.3 | 625.8 | 660 | 677 | 661.2 | 604.5 | 361.1 | 489.7
1078 | 959 | 379.4 | 624.9 | 659.5 | 678.9 | 659.3 | 610.4 | 361.2 | 489.4
1079 | 960 | 378.7 | 623.4 | 660 | 682.7 | 657.1 | 615.2 | 361.3 | 489.3
1080 | 961 | 378.1 | 622.2 | 660.2 | 683.7 | 655.4 | 620.2 | 361.3 | 489.2
1081 | 962 | 377.4 | 620.7 | 660.4 | 684.2 | 653.7 | 626.4 | 361.4 | 489
1082 | 963 | 376.7 | 619.5 | 660.6 | 685.1 | 652.2 | 627.2 | 361.4 | 488.8
1083 | 964 | 376.1 | 618.4 | 660.6 | 688.4 | 650.7 | 627.2 | 361.4 | 488.6
1084 | 965 | 375.5 | 617.1 | 660.8 | 691.2 | 649.1 | 629 | 361.4 | 488.4
1085 | 966 | 374.7 | 615.8 | 661.1 | 692.8 | 647.6 | 632.2 | 361.4 | 488.2
1086 | 967 | 374 | 614.9 | 661 | 694.1 | 646.2 | 635.3 | 361.3 | 488
1087 | 968 | 373.4 | 614 | 660.6 | 697.5 | 644.9 | 638.1 | 361.3 | 487.7
1088 | 969 | 372.7 | 612.9 | 660.5 | 700.2 | 643.7 | 639.3 | 361.3 | 487.4
1089 | 970 | 372 | 611.7 | 660.1 | 702.5 | 642.6 | 639.5 | 361.4 | 487.2
1090 | 971 | 371.3 | 610.6 | 660 | 701.2 | 641.5 | 639.6 | 361.4 | 486.9
1091 | 972 | 370.7 | 609.2 | 659.8 | 698.3 | 640.6 | 639.5 | 361.5 | 486.6
1092 | 973 | 370 | 608.5 | 659.3 | 696.1 | 640.7 | 639 | 361.6 | 486.3
1093 | 974 | 369.3 | 607.4 | 658.6 | 695.4 | 641.5 | 638.8 | 361.7 | 486
1094 | 975 | 368.6 | 606.4 | 658.3 | 694.3 | 642.3 | 638.5 | 361.7 | 485.7
1095 | 976 | 368.1 | 605.5 | 658 | 693.5 | 642.5 | 637.9 | 361.8 | 485.4
1096 | 977 | 367.4 | 604.9 | 657.7 | 692.3 | 642.7 | 638.4 | 361.9 | 485.1
1097 | 978 | 366.6 | 603.7 | 657.9 | 694.8 | 642.1 | 638.9 | 361.9 | 484.8
1098 | 979 | 365.8 | 603.2 | 657.8 | 697.1 | 641.4 | 639.6 | 361.9 | 484.5
1099 | 980 | 365.1 | 603.3 | 657.8 | 701.1 | 641.2 | 639.5 | 361.9 | 484.2
1100 | 981 | 364.4 | 603.7 | 657.6 | 699.1 | 641.4 | 639.4 | 361.9 | 483.9
1101 | 982 | 363.8 | 603.2 | 657.4 | 697.8 | 641.2 | 639.3 | 361.9 | 483.6
1102 | 983 | 363.1 | 602 | 657.6 | 701.5 | 640.6 | 639.4 | 361.9 | 483.2
1103 | 984 | 362.5 | 600.8 | 657.8 | 701.3 | 640.5 | 640.3 | 361.8 | 482.9
1104 | 985 | 361.8 | 599.8 | 658.4 | 702.4 | 639.9 | 639.8 | 361.8 | 482.5
1105 | 986 | 361.2 | 598.5 | 659 | 702.5 | 639.1 | 638.9 | 361.8 | 482.2
1106 | 987 | 360.5 | 596.7 | 659.8 | 702.4 | 638.2 | 637.8 | 361.8 | 481.9
1107 | 988 | 359.8 | 595.2 | 660 | 702.6 | 637.4 | 636.6 | 361.9 | 481.5
1108 | 989 | 359 | 593.7 | 660.2 | 704 | 636.5 | 635.5 | 362 | 481.2
1109 | 990 | 358.3 | 592 | 660.7 | 709 | 635.3 | 634.8 | 362 | 480.8
1110 | 991 | 357.6 | 590.9 | 660.6 | 711.7 | 634.5 | 633.3 | 362.1 | 480.4
1111 | 992 | 356.9 | 590 | 661.1 | 711.3 | 633.5 | 632.2 | 362.1 | 480.1
1112 | 993 | 356.2 | 589.1 | 661.6 | 711.6 | 632.6 | 631.2 | 362.2 | 479.7
1113 | 994 | 355.5 | 587.8 | 661.8 | 714.7 | 631.7 | 629.7 | 362.2 | 479.4
1114 | 995 | 354.9 | 587.4 | 661.5 | 717.7 | 630.8 | 627.5 | 362.2 | 479
1115 | 996 | 354.2 | 586.8 | 661.4 | 715.1 | 629.8 | 624.7 | 362.2 | 478.6
1116 | 997 | 353.6 | 585.6 | 661.7 | 713.2 | 628.5 | 621.6 | 362.2 | 478.3
1117 | 998 | 353.1 | 584.1 | 662.2 | 712.8 | 627.8 | 618.2 | 362.3 | 477.9
1118 | 999 | 352.7 | 582.5 | 662.8 | 714.2 | 627.1 | 614.4 | 362.3 | 477.5
1119 | 1000 | 352.1 | 580.7 | 663.3 | 714.8 | 626.5 | 610.8 | 362.4 | 477.2
1120 | 1001 | 351.4 | 579 | 663.8 | 713.3 | 625.9 | 607.5 | 362.4 | 476.9
1121 | 1002 | 350.8 | 577.5 | 664.1 | 714.7 | 625.9 | 604 | 362.4 | 476.5
1122 | 1003 | 350.2 | 576 | 664.2 | 714.5 | 625.8 | 600.2 | 362.4 | 476.1
1123 | 1004 | 349.5 | 574.5 | 664 | 711.6 | 625.1 | 595.8 | 362.4 | 475.7
1124 | 1005 | 349.1 | 573.3 | 663.4 | 709 | 624.9 | 591.8 | 362.4 | 475.3
1125 | 1006 | 348.5 | 572.1 | 663 | 713.3 | 624.6 | 587.3 | 362.4 | 475
1126 | 1007 | 347.9 | 571.1 | 662.9 | 715.2 | 624.1 | 582.2 | 362.5 | 474.6
1127 | 1008 | 347.3 | 570.1 | 662.6 | 713 | 623.5 | 577.4 | 362.4 | 474.3
1128 | 1009 | 346.7 | 569 | 662.6 | 713.3 | 622.9 | 572.9 | 362.3 | 473.9
1129 | 1010 | 346 | 567.5 | 662.8 | 715 | 622.6 | 566.9 | 362.3 | 473.5
1130 | 1011 | 345.3 | 566.1 | 662.8 | 718.3 | 622.3 | 558.7 | 362.3 | 473.1
1131 | 1012 | 344.6 | 565.2 | 662.6 | 721.1 | 622.1 | 551.4 | 362.3 | 472.7
1132 | 1013 | 343.9 | 564.3 | 663.4 | 724.1 | 621.8 | 544.5 | 362.3 | 472.3
1133 | 1014 | 343.2 | 563 | 664.3 | 724.1 | 622 | 540.1 | 362.3 | 471.9
1134 | 1015 | 342.7 | 561.7 | 664.3 | 724.4 | 622 | 535.9 | 362.2 | 471.5
1135 | 1016 | 342 | 561 | 664.1 | 725.5 | 621.8 | 531.3 | 362.1 | 471.1
1136 | 1017 | 341.4 | 560.2 | 663.7 | 722.9 | 621 | 527 | 362.1 | 470.7
1137 | 1018 | 340.7 | 559.4 | 663.5 | 724.7 | 620.1 | 523.5 | 362.1 | 470.4
1138 | 1019 | 340.2 | 558.6 | 664.1 | 726.5 | 619.9 | 519.2 | 362.1 | 470
1139 | 1020 | 339.6 | 558 | 663.9 | 729.1 | 619.6 | 516.7 | 362.1 | 469.6
1140 | 1021 | 339.1 | 557 | 663.7 | 729.5 | 618.7 | 513 | 362.2 | 469.2
1141 | 1022 | 338.6 | 556.2 | 664.2 | 730.1 | 617.9 | 510.1 | 362.2 | 468.9
1142 | 1023 | 337.9 | 555.9 | 664.2 | 729.4 | 617.4 | 508 | 362.2 | 468.5
1143 | 1024 | 337.4 | 555 | 663.7 | 726.8 | 617.3 | 505.2 | 362.2 | 468.1
1144 | 1025 | 336.9 | 553.8 | 663.1 | 728.3 | 617.4 | 502.4 | 362.2 | 467.7
1145 | 1026 | 336.3 | 552.8 | 661.8 | 727 | 619.3 | 499.8 | 362.3 | 467.3
1146 | 1027 | 335.8 | 552.1 | 660.7 | 722.8 | 620.7 | 497 | 362.3 | 467
1147 | 1028 | 335.2 | 551.1 | 661.1 | 724.8 | 621.2 | 494 | 362.2 | 466.6
1148 | 1029 | 334.6 | 550.2 | 662.4 | 727.5 | 621.1 | 492.1 | 362.2 | 466.2
1149 | 1030 | 333.9 | 549.5 | 662.7 | 729.6 | 621.2 | 488.3 | 362.2 | 465.9
1150 | 1031 | 333.4 | 548.6 | 662.9 | 728.9 | 621.1 | 485.6 | 362.2 | 465.4
1151 | 1032 | 332.8 | 547.7 | 663.9 | 728.6 | 620.2 | 483.9 | 362.1 | 465
1152 | 1033 | 332.3 | 547.3 | 663.6 | 725.4 | 619.4 | 482.2 | 362.1 | 464.6
1153 | 1034 | 331.7 | 546.8 | 662.8 | 725 | 619 | 480.3 | 362 | 464.2
1154 | 1035 | 331.1 | 545.7 | 662.8 | 724.1 | 618.9 | 478.5 | 362 | 463.8
1155 | 1036 | 330.4 | 544.7 | 663 | 725 | 619 | 476.8 | 361.9 | 463.4
1156 | 1037 | 329.7 | 543.9 | 662.8 | 725.7 | 619.1 | 475.2 | 361.8 | 463
1157 | 1038 | 329.2 | 543.2 | 662.5 | 728 | 619.3 | 473.5 | 361.9 | 462.5
1158 | 1039 | 328.7 | 542.4 | 662.8 | 729.3 | 620.3 | 471.8 | 361.9 | 462.1
1159 | 1040 | 328.1 | 541.8 | 663.6 | 730.8 | 620.3 | 470 | 361.9 | 461.7
1160 | 1041 | 327.6 | 541.4 | 663.5 | 732.7 | 620.4 | 467.9 | 361.9 | 461.2
1161 | 1042 | 327 | 541.1 | 662.5 | 735 | 620.3 | 466 | 361.9 | 460.8
1162 | 1043 | 326.4 | 541.2 | 662.6 | 736.7 | 619.6 | 464.7 | 361.9 | 460.3
1163 | 1044 | 325.8 | 541.4 | 662.4 | 735.8 | 618.7 | 463 | 361.8 | 459.9
1164 | 1045 | 325.2 | 541 | 662.2 | 734.4 | 617.7 | 462 | 361.7 | 459.5
1165 | 1046 | 324.5 | 540.3 | 660.8 | 731 | 617.2 | 460.8 | 361.6 | 459
1166 | 1047 | 323.9 | 539.7 | 660 | 727.7 | 617.1 | 458.7 | 361.6 | 458.6
1167 | 1048 | 323.4 | 539 | 660 | 726.9 | 617.5 | 457.6 | 361.5 | 458.1
1168 | 1049 | 322.8 | 538.1 | 659.8 | 727.2 | 617.8 | 456 | 361.5 | 457.7
1169 | 1050 | 322.2 | 537.4 | 659.2 | 726.2 | 617.7 | 455.2 | 361.4 | 457.2
1170 | 1051 | 321.7 | 536.9 | 658.4 | 724.2 | 617.4 | 453.6 | 361.3 | 456.8
1171 | 1052 | 321.2 | 535.9 | 657.9 | 723.2 | 616.7 | 452.1 | 361.2 | 456.3
1172 | 1053 | 320.7 | 534.9 | 658 | 721.6 | 615.9 | 450.9 | 361.1 | 456
1173 | 1054 | 320.1 | 534 | 657.7 | 720.8 | 615.7 | 450.1 | 361.1 | 455.5
1174 | 1055 | 319.5 | 533.3 | 657.6 | 719.6 | 615.2 | 448.8 | 361 | 455.1
1175 | 1056 | 319 | 532.6 | 656.6 | 716.3 | 614.4 | 448.2 | 361 | 454.6
1176 | 1057 | 318.3 | 532 | 656.3 | 714.2 | 613.7 | 446.9 | 360.9 | 454.2
1177 | 1058 | 317.8 | 531.4 | 655.3 | 712.8 | 613.3 | 446 | 360.9 | 453.8
1178 | 1059 | 317.2 | 530.4 | 656.9 | 713.9 | 613.1 | 445.1 | 360.8 | 453.4
1179 | 1060 | 316.7 | 529.2 | 659.7 | 716.2 | 612.6 | 444 | 360.6 | 452.9
1180 | 1061 | 316.2 | 528.2 | 661.2 | 717.6 | 611.5 | 443.1 | 360.5 | 452.5
1181 | 1062 | 315.7 | 527.3 | 661.9 | 718.3 | 610.3 | 442.4 | 360.4 | 452
1182 | 1063 | 315.2 | 526.2 | 661.1 | 716.5 | 609.3 | 442.1 | 360.3 | 451.6
1183 | 1064 | 314.6 | 525.4 | 661.5 | 715 | 609.1 | 441 | 360.2 | 451.1
1184 | 1065 | 314.2 | 524.7 | 661.1 | 714 | 608.8 | 440.1 | 360.1 | 450.7
1185 | 1066 | 313.7 | 524.2 | 659.9 | 712.2 | 607.9 | 439.6 | 359.9 | 450.3
1186 | 1067 | 313.3 | 523.4 | 660.4 | 712.8 | 607.1 | 438.1 | 359.7 | 449.8
1187 | 1068 | 312.9 | 522.7 | 661 | 713.5 | 606.3 | 437.6 | 359.5 | 449.4
1188 | 1069 | 312.4 | 522.1 | 660.8 | 712.2 | 605.5 | 436.9 | 359.4 | 449
1189 | 1070 | 311.8 | 521.6 | 660.6 | 711.3 | 604.6 | 436 | 359.3 | 448.5
1190 | 1071 | 311.1 | 521.3 | 658.9 | 710.2 | 604.6 | 435.2 | 359.2 | 448.1
1191 | 1072 | 310.5 | 520.3 | 659.2 | 708.7 | 603.4 | 434.4 | 359.1 | 447.6
1192 | 1073 | 310 | 519.5 | 659.2 | 708.4 | 603.6 | 433 | 358.9 | 447.2
1193 | 1074 | 309.5 | 518.5 | 659.9 | 708.5 | 603.2 | 432 | 358.7 | 446.8
1194 | 1075 | 308.9 | 517.6 | 660.5 | 708.4 | 602.6 | 431.3 | 358.6 | 446.3
1195 | 1076 | 308.3 | 516.9 | 659.1 | 707.2 | 601.9 | 430.6 | 358.4 | 445.9
1196 | 1077 | 307.8 | 516.1 | 657.7 | 705.2 | 601.9 | 429.4 | 358.2 | 445.4
1197 | 1078 | 307.3 | 515.3 | 658.4 | 704.4 | 601.5 | 428.7 | 358 | 445
1198 | 1079 | 306.7 | 514.6 | 657.8 | 703.5 | 601.4 | 428.3 | 357.8 | 444.6
1199 | 1080 | 306.1 | 513.8 | 656.2 | 703 | 600.3 | 427.9 | 357.6 | 444.2
1200 | 1081 | 305.7 | 513 | 655.1 | 701.9 | 599.4 | 427.6 | 357.4 | 443.8
1201 | 1082 | 305.2 | 512.2 | 655.3 | 701.4 | 598.7 | 426.8 | 357.2 | 443.4
1202 | 1083 | 304.7 | 511.3 | 655.7 | 700.9 | 597.8 | 425.8 | 357 | 443
1203 | 1084 | 304.4 | 510 | 656.5 | 700.5 | 596.4 | 424.9 | 356.8 | 442.6
1204 | 1085 | 303.9 | 508.9 | 656.9 | 699.9 | 594.9 | 424 | 356.6 | 442.1
1205 | 1086 | 303.6 | 508.3 | 655.9 | 699.6 | 593.8 | 422.9 | 356.4 | 441.7
1206 | 1087 | 303.1 | 507.5 | 654.9 | 698.5 | 592.7 | 422.3 | 356.2 | 441.2
1207 | 1088 | 302.6 | 506.3 | 654.8 | 697 | 591.5 | 422 | 355.9 | 440.7
1208 | 1089 | 302.1 | 505.6 | 654.2 | 695.9 | 590.7 | 420.8 | 355.6 | 440.2
1209 | 1090 | 301.7 | 504.9 | 652.8 | 694.9 | 590 | 419.6 | 355.4 | 439.8
1210 | 1091 | 301.2 | 504.2 | 651.7 | 693.7 | 588.9 | 418.3 | 355.2 | 439.4
1211 | 1092 | 300.8 | 503.6 | 650.5 | 692.5 | 588 | 417.8 | 354.9 | 438.9
1212 | 1093 | 300.3 | 503.2 | 648.8 | 691.4 | 587.9 | 416.9 | 354.6 | 438.5
1213 | 1094 | 299.8 | 502.6 | 648.6 | 690.3 | 587.4 | 415.7 | 354.3 | 438
1214 | 1095 | 299.3 | 501.8 | 648.4 | 689.4 | 586.9 | 415.5 | 354.1 | 437.5
1215 | 1096 | 298.7 | 501.1 | 647 | 688.5 | 586.4 | 414.9 | 353.7 | 437.1
1216 | 1097 | 298.1 | 500.1 | 646.6 | 687.7 | 585.7 | 414.1 | 353.4 | 436.7
1217 | 1098 | 297.6 | 499.3 | 646.2 | 686.9 | 584.7 | 412.6 | 353 | 436.2
1218 | 1099 | 297.2 | 498.5 | 645.1 | 686.2 | 583.7 | 411.6 | 352.7 | 435.8
1219 | 1100 | 296.7 | 497.6 | 643.2 | 685.5 | 582.6 | 410.3 | 352.4 | 435.4
1220 | 1101 | 296.2 | 496.6 | 641.3 | 684.6 | 581.4 | 408.8 | 352.1 | 434.9
1221 | 1102 | 295.7 | 495.8 | 639.4 | 683.7 | 579.9 | 407.5 | 351.9 | 434.5
1222 | 1103 | 295.4 | 495.1 | 637.3 | 682.6 | 579.2 | 406.2 | 351.6 | 434.1
1223 | 1104 | 295 | 494.7 | 635.7 | 681.4 | 579.2 | 405.2 | 351.4 | 433.7
1224 | 1105 | 294.6 | 494.3 | 633.1 | 680.4 | 578.4 | 404 | 351.1 | 433.4
1225 | 1106 | 294.2 | 493.7 | 630.8 | 679.4 | 577.4 | 402.6 | 350.8 | 433
1226 | 1107 | 293.8 | 493 | 628.2 | 678.3 | 576.9 | 400.8 | 350.5 | 432.5
1227 | 1108 | 293.3 | 492.4 | 625.5 | 677.1 | 576.3 | 398.9 | 350.2 | 432
1228 | 1109 | 292.9 | 491.4 | 623.4 | 676 | 575.6 | 399.1 | 349.9 | 431.6
1229 | 1110 | 292.4 | 490.1 | 621.8 | 674.7 | 575.7 | 398.7 | 349.5 | 431.1
1230 | 1111 | 291.9 | 488.3 | 620.3 | 673.6 | 575.8 | 398.9 | 349.3 | 430.7
1231 | 1112 | 291.5 | 486.9 | 618.8 | 672.5 | 575.3 | 398.8 | 349.1 | 430.3
1232 | 1113 | 291 | 486.1 | 616.4 | 671.6 | 574.3 | 397.7 | 348.7 | 429.9
1233 | 1114 | 290.6 | 485.7 | 613.8 | 671 | 573.4 | 396.4 | 348.4 | 429.5
1234 | 1115 | 290.2 | 485.4 | 611.2 | 670.2 | 572.5 | 394.5 | 348 | 429
1235 | 1116 | 289.6 | 485 | 609.3 | 669.1 | 571.9 | 392.6 | 347.6 | 428.6
1236 | 1117 | 289.1 | 484.6 | 606.9 | 668.2 | 572.1 | 391 | 347.2 | 428.2
1237 | 1118 | 288.7 | 483.9 | 604.6 | 667.3 | 572.3 | 389.3 | 346.8 | 427.8
1238 | 1119 | 288.3 | 483.1 | 602.4 | 666.8 | 571.9 | 388.3 | 346.3 | 427.4
1239 | 1120 | 287.8 | 482.2 | 600.3 | 666 | 570.7 | 387.4 | 345.9 | 427.1
1240 | 1121 | 287.3 | 481.6 | 597.9 | 665.1 | 570 | 386.1 | 345.5 | 426.7
1241 | 1122 | 286.9 | 481 | 595.8 | 663.8 | 570.2 | 383.3 | 345.1 | 426.3
1242 | 1123 | 286.4 | 480.4 | 594 | 662.4 | 569.4 | 381.1 | 344.7 | 425.9
1243 | 1124 | 285.9 | 480.1 | 592 | 661.4 | 568.5 | 379.1 | 344.3 | 425.6
1244 | 1125 | 285.5 | 479.8 | 590 | 660.8 | 567.3 | 379.4 | 344.1 | 425.2
1245 | 1126 | 285 | 479.3 | 588.2 | 659.8 | 566.8 | 378.1 | 343.7 | 424.9
1246 | 1127 | 284.5 | 478.8 | 586.7 | 658.7 | 566.7 | 376.7 | 343.2 | 424.4
1247 | 1128 | 284 | 478.5 | 585 | 657.7 | 566.4 | 374.8 | 342.7 | 424
1248 | 1129 | 283.6 | 478.2 | 583.5 | 656.7 | 565.8 | 373.3 | 342.3 | 423.6
1249 | 1130 | 283.2 | 477.7 | 582.4 | 655.5 | 564.8 | 371.8 | 341.9 | 423.2
1250 | 1131 | 282.8 | 477.5 | 580.7 | 654.4 | 563.9 | 370.4 | 341.4 | 422.8
1251 | 1132 | 282.4 | 477.3 | 579.2 | 653.4 | 563.1 | 367.9 | 340.9 | 422.4
1252 | 1133 | 281.9 | 476.9 | 577.9 | 652.3 | 562.3 | 365.1 | 340.4 | 421.9
1253 | 1134 | 281.5 | 476.5 | 576.6 | 651.1 | 561.2 | 365.2 | 340 | 421.5
1254 | 1135 | 281 | 476.2 | 575.2 | 650.2 | 560.2 | 365.4 | 339.6 | 421
1255 | 1136 | 280.6 | 475.6 | 573.9 | 649.1 | 559.4 | 364.3 | 339.2 | 420.6
1256 | 1137 | 280 | 474.5 | 573 | 647.8 | 558.6 | 363.2 | 338.8 | 420.2
1257 | 1138 | 279.6 | 473.7 | 571.6 | 646.8 | 557.9 | 362 | 338.4 | 419.9
1258 | 1139 | 279.1 | 473 | 570.4 | 645.9 | 557 | 360 | 337.9 | 419.4
1259 | 1140 | 278.6 | 472.2 | 570 | 644.5 | 556.1 | 356.4 | 337.5 | 419
1260 | 1141 | 278 | 471.2 | 569.7 | 643.1 | 555.5 | 352.5 | 337.2 | 418.6
1261 | 1142 | 277.5 | 470.2 | 568.7 | 642 | 555.1 | 351.5 | 336.8 | 418.2
1262 | 1143 | 277 | 469.2 | 567.9 | 640.8 | 554.6 | 351.3 | 336.5 | 417.8
1263 | 1144 | 276.5 | 468.3 | 567.1 | 639.6 | 553.6 | 350.4 | 336.2 | 417.3
1264 | 1145 | 276 | 467.4 | 566 | 638.7 | 552.8 | 349.7 | 335.8 | 416.9
1265 | 1146 | 275.6 | 466.7 | 564.8 | 638 | 551.3 | 348.7 | 335.5 | 416.5
1266 | 1147 | 275.2 | 465.6 | 564 | 636.9 | 550.1 | 347.5 | 335.1 | 416
1267 | 1148 | 274.8 | 464.7 | 563 | 635.4 | 549.5 | 346.6 | 334.7 | 415.5
1268 | 1149 | 274.4 | 463.9 | 561.7 | 634.2 | 549.3 | 345.5 | 334.3 | 415
1269 | 1150 | 274 | 463 | 560.6 | 632.5 | 549.5 | 344.7 | 334 | 414.5
1270 | 1151 | 273.7 | 461.9 | 559.5 | 631 | 549.1 | 343.9 | 333.6 | 414.1
1271 | 1152 | 273.3 | 461 | 558.2 | 629.5 | 548.6 | 342.7 | 333.3 | 413.7
1272 | 1153 | 272.8 | 460.1 | 556.8 | 628 | 548.5 | 342.2 | 332.9 | 413.2
1273 | 1154 | 272.2 | 459 | 555.7 | 626.4 | 548.7 | 341.4 | 332.4 | 412.8
1274 | 1155 | 271.8 | 458.1 | 554.6 | 625.1 | 548.8 | 340.6 | 332 | 412.3
1275 | 1156 | 271.4 | 457.4 | 553.1 | 623.8 | 548.7 | 339.5 | 331.6 | 411.8
1276 | 1157 | 271.1 | 456.6 | 550.5 | 622.6 | 548.1 | 338.4 | 331.1 | 411.3
1277 | 1158 | 270.6 | 455.8 | 548.8 | 621.6 | 547.2 | 337.6 | 330.7 | 410.9
1278 | 1159 | 270.1 | 454.9 | 547.2 | 620.9 | 546.4 | 336.6 | 330.3 | 410.4
1279 | 1160 | 269.6 | 454 | 545.5 | 620.1 | 545.4 | 335.8 | 329.9 | 409.9
1280 | 1161 | 269.2 | 452.8 | 543.6 | 619.1 | 544.3 | 334.3 | 329.5 | 409.4
1281 | 1162 | 268.8 | 451.7 | 542.2 | 618.1 | 543.7 | 332.9 | 329.1 | 409
1282 | 1163 | 268.4 | 450.7 | 540.6 | 617.2 | 542.8 | 332.1 | 328.6 | 408.6
1283 | 1164 | 267.9 | 449.6 | 539.4 | 616 | 542.2 | 330.6 | 328.2 | 408.2
1284 | 1165 | 267.3 | 448.4 | 537.9 | 614.6 | 541.4 | 329.4 | 327.7 | 407.8
1285 | 1166 | 266.9 | 447.4 | 536.2 | 613.4 | 540.8 | 328.7 | 327.1 | 407.3
1286 | 1167 | 266.5 | 446.4 | 534.5 | 612.1 | 540.7 | 327.9 | 326.5 | 406.8
1287 | 1168 | 266.1 | 445.2 | 533 | 610.6 | 540.5 | 327 | 326 | 406.4
1288 | 1169 | 265.7 | 444.2 | 531.2 | 608.9 | 540 | 325.2 | 325.5 | 405.9
1289 | 1170 | 265.3 | 443.6 | 529.1 | 607.5 | 539.3 | 323.5 | 325.1 | 405.5
1290 | 1171 | 265 | 443 | 527 | 606.2 | 538.3 | 322.6 | 324.6 | 405
1291 | 1172 | 264.6 | 442.1 | 525.5 | 604.9 | 536.8 | 320.8 | 324.2 | 404.6
1292 | 1173 | 264.2 | 441.4 | 523.5 | 603.6 | 536.3 | 319 | 323.8 | 404.1
1293 | 1174 | 263.7 | 440.5 | 521.3 | 602.3 | 536 | 317.5 | 323.4 | 403.6
1294 | 1175 | 263.4 | 439.4 | 519.4 | 600.9 | 535.2 | 316.2 | 322.9 | 403.2
1295 | 1176 | 262.9 | 438.5 | 517.3 | 599.7 | 534.6 | 315.3 | 322.4 | 402.8
1296 | 1177 | 262.4 | 437.7 | 515.2 | 598.3 | 534 | 313.7 | 321.9 | 402.4
1297 | 1178 | 261.9 | 436.9 | 513.5 | 596.9 | 533.1 | 312.5 | 321.4 | 401.9
1298 | 1179 | 261.6 | 436 | 511.9 | 595.6 | 532 | 312 | 320.9 | 401.5
1299 | 1180 | 261.2 | 435.3 | 509.8 | 594.4 | 531.5 | 311.2 | 320.4 | 401.1
1300 | 1181 | 260.7 | 434.5 | 507.9 | 592.8 | 531.3 | 310 | 319.9 | 400.7
1301 | 1182 | 260.3 | 433.7 | 506.3 | 591 | 530.8 | 308.9 | 319.4 | 400.2
1302 | 1183 | 260 | 432.8 | 504 | 589.2 | 530.5 | 307.7 | 318.9 | 399.8
1303 | 1184 | 259.5 | 432.1 | 501.4 | 587.4 | 530.3 | 305.9 | 318.4 | 399.3
1304 | 1185 | 259.1 | 431.4 | 499.4 | 585.8 | 529.9 | 304.8 | 317.9 | 398.9
1305 | 1186 | 258.7 | 430.6 | 497.7 | 584.2 | 529.2 | 302.9 | 317.4 | 398.5
1306 | 1187 | 258.4 | 429.9 | 495.6 | 582.7 | 528.4 | 301.5 | 316.8 | 398.1
1307 | 1188 | 258 | 429 | 493.3 | 581.1 | 527.4 | 300.9 | 316.3 | 397.7
1308 | 1189 | 257.6 | 428.2 | 491.7 | 579.6 | 526.3 | 300 | 315.8 | 397.3
1309 | 1190 | 257.3 | 427.5 | 490.4 | 578.1 | 525.3 | 298.2 | 315.3 | 396.9
1310 | 1191 | 257 | 426.9 | 489.5 | 576.9 | 524.7 | 296.5 | 314.9 | 396.5
1311 | 1192 | 256.6 | 426 | 488.4 | 575.5 | 524.3 | 295.1 | 314.4 | 396
1312 | 1193 | 256.3 | 424.9 | 487.2 | 574 | 523.7 | 294.6 | 313.9 | 395.6
1313 | 1194 | 256 | 423.8 | 485.5 | 572.8 | 523.5 | 294 | 313.5 | 395.2
1314 | 1195 | 255.6 | 422.9 | 483.7 | 571.5 | 523.2 | 293.1 | 313 | 394.7
1315 | 1196 | 255.2 | 422.1 | 482.2 | 570.1 | 522.3 | 292.1 | 312.4 | 394.3
1316 | 1197 | 255 | 421.2 | 481 | 568.6 | 521.3 | 291.4 | 311.9 | 393.9
1317 | 1198 | 254.7 | 420.4 | 479.5 | 567.3 | 520.6 | 290.7 | 311.4 | 393.4
1318 | 1199 | 254.3 | 419.6 | 477.9 | 565.9 | 520.2 | 290 | 310.9 | 393
1319 | 1200 | 254.1 | 418.6 | 477.2 | 564.5 | 519.1 | 289.5 | 310.3 | 392.7
1320 | 1201 | 253.8 | 417.7 | 476 | 563.1 | 517.9 | 288.6 | 309.9 | 392.3
1321 | 1202 | 253.5 | 416.8 | 474.6 | 561.7 | 517 | 287.3 | 309.4 | 391.8
1322 | 1203 | 253.1 | 416 | 473.6 | 560.3 | 516.3 | 287 | 308.9 | 391.4
1323 | 1204 | 252.8 | 415.2 | 473.1 | 558.9 | 515.4 | 286.3 | 308.4 | 391.1
1324 | 1205 | 252.4 | 414.5 | 472 | 557.3 | 514.7 | 285.2 | 307.9 | 390.7
1325 | 1206 | 252 | 413.7 | 470.7 | 555.6 | 514.1 | 284.1 | 307.4 | 390.3
1326 | 1207 | 251.7 | 412.7 | 469.7 | 553.9 | 513.1 | 283.9 | 307 | 389.9
1327 | 1208 | 251.3 | 411.9 | 468.4 | 552.4 | 512.5 | 283.2 | 306.5 | 389.5
1328 | 1209 | 251 | 411.1 | 467.1 | 550.8 | 511.8 | 282.4 | 306 | 389.1
1329 | 1210 | 250.7 | 410 | 465.3 | 549.2 | 511.1 | 281.7 | 305.5 | 388.6
1330 | 1211 | 250.4 | 408.8 | 463.7 | 547.8 | 510.7 | 280.9 | 304.9 | 388.2
1331 | 1212 | 250 | 407.8 | 462.4 | 546.6 | 510.6 | 280.1 | 304.4 | 387.8
1332 | 1213 | 249.6 | 406.7 | 460.9 | 545.2 | 510.6 | 279 | 303.9 | 387.4
1333 | 1214 | 249.3 | 405.6 | 459.6 | 543.9 | 510 | 278.1 | 303.4 | 387
1334 | 1215 | 248.8 | 404.7 | 458.2 | 542.6 | 509.3 | 277.4 | 302.8 | 386.6
1335 | 1216 | 248.4 | 403.7 | 456.8 | 541.3 | 508.5 | 277 | 302.3 | 386.2
1336 | 1217 | 248 | 402.8 | 455 | 539.8 | 507.7 | 276.6 | 301.8 | 385.7
1337 | 1218 | 247.5 | 402.1 | 453.6 | 538.5 | 506.9 | 275.9 | 301.3 | 385.4
1338 | 1219 | 247.2 | 401.7 | 452.8 | 537.1 | 506.2 | 275.7 | 300.8 | 385
1339 | 1220 | 246.8 | 401 | 451.8 | 535.3 | 505.5 | 275.3 | 300.3 | 384.6
1340 | 1221 | 246.5 | 400 | 450.9 | 533.6 | 504.5 | 274.8 | 299.8 | 384.1
1341 | 1222 | 246.1 | 399.1 | 449.7 | 531.9 | 503.9 | 273.8 | 299.3 | 383.7
1342 | 1223 | 245.7 | 398.3 | 448.3 | 530.1 | 503.9 | 272.6 | 298.8 | 383.3
1343 | 1224 | 245.3 | 397.5 | 446.8 | 528.4 | 503.8 | 272.4 | 298.3 | 382.9
1344 | 1225 | 244.9 | 396.8 | 445.7 | 526.6 | 503.5 | 271.9 | 297.7 | 382.4
1345 | 1226 | 244.4 | 396 | 443.8 | 524.8 | 503.4 | 271.5 | 297.2 | 382
1346 | 1227 | 244 | 395.2 | 442.1 | 522.9 | 503.2 | 270.6 | 296.7 | 381.7
1347 | 1228 | 243.7 | 394.4 | 440.7 | 520.9 | 502.7 | 270.3 | 296.1 | 381.2
1348 | 1229 | 243.4 | 393.8 | 439.1 | 519 | 502.6 | 269.6 | 295.5 | 380.8
1349 | 1230 | 243 | 393.3 | 438 | 517.3 | 502.5 | 267.4 | 295 | 380.3
1350 | 1231 | 242.6 | 392.8 | 437.3 | 515.6 | 502.3 | 266.9 | 294.4 | 379.9
1351 | 1232 | 242.1 | 392.1 | 436.2 | 513.8 | 501.6 | 266.9 | 293.9 | 379.5
1352 | 1233 | 241.8 | 391.5 | 434.6 | 512 | 501 | 266.2 | 293.4 | 379
1353 | 1234 | 241.3 | 390.7 | 432.8 | 510.2 | 500.2 | 265.3 | 292.9 | 378.6
1354 | 1235 | 240.9 | 389.8 | 431.5 | 508.3 | 499.3 | 265.2 | 292.3 | 378.3
1355 | 1236 | 240.6 | 389.1 | 429.9 | 506.6 | 498.5 | 264.4 | 291.7 | 377.8
1356 | 1237 | 240.2 | 388.5 | 428.7 | 504.8 | 497.4 | 263.7 | 291.2 | 377.4
1357 | 1238 | 239.9 | 387.6 | 427.6 | 502.9 | 496.3 | 262.4 | 290.6 | 377
1358 | 1239 | 239.6 | 386.7 | 425.9 | 501.3 | 495.2 | 261.6 | 290 | 376.6
1359 | 1240 | 239.2 | 386 | 424.3 | 499.9 | 494.6 | 261.1 | 289.5 | 376.2
1360 | 1241 | 238.8 | 385.1 | 422.5 | 498.3 | 494.1 | 260.9 | 288.8 | 375.8
1361 | 1242 | 238.5 | 384.1 | 421.5 | 496.7 | 493.3 | 260.6 | 288.3 | 375.5
1362 | 1243 | 238.2 | 383.3 | 419.9 | 495 | 492.8 | 260.1 | 287.7 | 375.1
1363 | 1244 | 237.9 | 382.4 | 417.9 | 493.5 | 492.5 | 259.5 | 287.1 | 374.7
1364 | 1245 | 237.6 | 381.5 | 416.2 | 492 | 491.7 | 258.3 | 286.6 | 374.3
1365 | 1246 | 237.3 | 380.7 | 414.6 | 490.6 | 491.3 | 257.1 | 286.1 | 373.9
1366 | 1247 | 237.1 | 380.1 | 413.5 | 489.2 | 491.2 | 257.6 | 285.6 | 373.5
1367 | 1248 | 236.8 | 379.4 | 412.7 | 487.5 | 490.9 | 257.7 | 285 | 373.1
1368 | 1249 | 236.5 | 378.7 | 411.5 | 485.6 | 490.6 | 257 | 284.5 | 372.7
1369 | 1250 | 236.1 | 378.1 | 410.4 | 483.9 | 490.6 | 256.6 | 283.9 | 372.4
1370 | 1251 | 235.7 | 377.5 | 407.9 | 482 | 490.5 | 256.6 | 283.3 | 372
1371 | 1252 | 235.3 | 376.8 | 406 | 480.3 | 490.2 | 256.1 | 282.7 | 371.5
1372 | 1253 | 235 | 376.2 | 405.2 | 478.7 | 489.6 | 255.9 | 282.2 | 371.1
1373 | 1254 | 234.8 | 375.5 | 404.2 | 477.1 | 488.9 | 255.3 | 281.7 | 370.6
1374 | 1255 | 234.6 | 374.9 | 402.8 | 475.5 | 488.1 | 254.9 | 281.1 | 370.2
1375 | 1256 | 234.2 | 374.1 | 401.9 | 473.9 | 487 | 254 | 280.5 | 369.8
1376 | 1257 | 233.8 | 373.5 | 400.3 | 472.5 | 486.2 | 253 | 279.9 | 369.4
1377 | 1258 | 233.4 | 372.8 | 399.1 | 471 | 485.5 | 252.7 | 279.3 | 369.1
1378 | 1259 | 233 | 372 | 398.5 | 469.6 | 484.2 | 252.2 | 278.6 | 368.7
1379 | 1260 | 232.7 | 371.2 | 397 | 468.2 | 483.4 | 251.4 | 278 | 368.4
1380 | 1261 | 232.4 | 370.4 | 395.3 | 466.8 | 483.2 | 250.1 | 277.4 | 368
1381 | 1262 | 232.1 | 369.5 | 393.8 | 465.5 | 482.8 | 248.7 | 276.8 | 367.6
1382 | 1263 | 231.7 | 368.7 | 392.6 | 464 | 482.4 | 248.2 | 276.2 | 367.2
1383 | 1264 | 231.3 | 368.2 | 391.1 | 462.6 | 482.2 | 247.7 | 275.7 | 366.8
1384 | 1265 | 231 | 367.8 | 390 | 461.2 | 481.7 | 246.6 | 275.1 | 366.4
1385 | 1266 | 230.7 | 367.4 | 389.2 | 459.8 | 481 | 244.9 | 274.5 | 366
1386 | 1267 | 230.5 | 367.1 | 388.1 | 458.5 | 480.2 | 244.4 | 273.9 | 365.6
1387 | 1268 | 230.2 | 366.9 | 386.5 | 457.3 | 479.4 | 243.5 | 273.3 | 365.3
1388 | 1269 | 229.9 | 366.6 | 385 | 456.1 | 478.2 | 243.4 | 272.7 | 365
1389 | 1270 | 229.6 | 366.1 | 383.8 | 454.7 | 476.9 | 242.5 | 272.1 | 364.7
1390 | 1271 | 229.3 | 365.8 | 382.6 | 453.6 | 475.9 | 241.9 | 271.5 | 364.3
1391 | 1272 | 229.1 | 365.3 | 381.4 | 452.2 | 474.8 | 241 | 271 | 363.9
1392 | 1273 | 228.7 | 364.7 | 380.1 | 450.8 | 474.2 | 240.7 | 270.4 | 363.6
1393 | 1274 | 228.3 | 364.1 | 379 | 449.6 | 473.9 | 240 | 269.7 | 363.3
1394 | 1275 | 228 | 363.7 | 377.7 | 448.6 | 473.5 | 239.4 | 269 | 362.9
1395 | 1276 | 227.7 | 363.1 | 376.1 | 447.3 | 473 | 239.3 | 268.4 | 362.5
1396 | 1277 | 227.3 | 362.6 | 375 | 446 | 472.3 | 238.5 | 267.7 | 362.1
1397 | 1278 | 226.9 | 362.1 | 373.6 | 444.7 | 471.5 | 237.7 | 267.1 | 361.7
1398 | 1279 | 226.6 | 361.5 | 372.4 | 443.3 | 470.6 | 236.2 | 266.6 | 361.3
1399 | 1280 | 226.3 | 360.7 | 371.3 | 441.7 | 469.8 | 235.9 | 266 | 360.9
1400 | 1281 | 225.8 | 359.9 | 370.1 | 439.9 | 469 | 234.6 | 265.3 | 360.4
1401 | 1282 | 225.4 | 359.3 | 368.6 | 438.1 | 468.2 | 234.4 | 264.7 | 360.1
1402 | 1283 | 225.2 | 358.5 | 367.6 | 436.3 | 467.3 | 234.6 | 264.1 | 359.8
1403 | 1284 | 224.7 | 357.6 | 366.9 | 434.6 | 466.2 | 233.1 | 263.5 | 359.4
1404 | 1285 | 224.4 | 356.9 | 365.8 | 433 | 465.5 | 233 | 262.9 | 359.1
1405 | 1286 | 224.2 | 356.2 | 364.8 | 431.3 | 464.8 | 232.5 | 262.4 | 358.8
1406 | 1287 | 223.8 | 355.4 | 364 | 429.5 | 464.3 | 232.1 | 261.8 | 358.4
1407 | 1288 | 223.5 | 354.3 | 363.3 | 427.7 | 463.5 | 231.8 | 261.4 | 358
1408 | 1289 | 223.2 | 353.4 | 362.2 | 426.2 | 463.2 | 230.8 | 260.8 | 357.6
1409 | 1290 | 223 | 352.5 | 361.1 | 424.7 | 462.7 | 229.5 | 260.2 | 357.3
1410 | 1291 | 222.7 | 351.4 | 359.4 | 423.3 | 462.1 | 229.2 | 259.5 | 357
1411 | 1292 | 222.5 | 350.5 | 357.9 | 421.9 | 461.6 | 229.2 | 258.9 | 356.7
1412 | 1293 | 222.1 | 349.8 | 356.8 | 420.2 | 460.9 | 229 | 258.2 | 356.4
1413 | 1294 | 221.8 | 348.9 | 355.7 | 418.6 | 460.3 | 228.6 | 257.6 | 356.1
1414 | 1295 | 221.5 | 348 | 354.2 | 417.2 | 459.9 | 227.9 | 257 | 355.7
1415 | 1296 | 221.3 | 347.2 | 352.4 | 415.8 | 459.9 | 227.6 | 256.4 | 355.3
1416 | 1297 | 221 | 346.5 | 351 | 414.3 | 459.7 | 227.7 | 255.7 | 354.9
1417 | 1298 | 220.8 | 345.6 | 349.9 | 412.7 | 459 | 227.1 | 255 | 354.6
1418 | 1299 | 220.4 | 344.8 | 348.4 | 411.2 | 458.2 | 226.6 | 254.4 | 354.2
1419 | 1300 | 220 | 344.1 | 347 | 409.9 | 457.3 | 226 | 253.8 | 353.9
1420 | 1301 | 219.7 | 343.2 | 346.1 | 408.4 | 456.3 | 225.5 | 253.2 | 353.7
1421 | 1302 | 219.3 | 342.4 | 345.3 | 407 | 455.4 | 224.6 | 252.5 | 353.3
1422 | 1303 | 218.9 | 341.5 | 344.1 | 405.6 | 454.7 | 223.9 | 251.9 | 352.9
1423 | 1304 | 218.5 | 340.5 | 342.8 | 404.4 | 454.4 | 223.5 | 251.3 | 352.6
1424 | 1305 | 218.1 | 339.4 | 341.8 | 403.2 | 453.8 | 223.5 | 250.7 | 352.2
1425 | 1306 | 217.9 | 338.4 | 340.7 | 402.1 | 453.3 | 223.3 | 250.1 | 351.9
1426 | 1307 | 217.6 | 337.5 | 339.7 | 401.1 | 452.7 | 223.1 | 249.5 | 351.5
1427 | 1308 | 217.3 | 336.5 | 338.7 | 400.1 | 452.1 | 222.7 | 248.9 | 351.2
1428 | 1309 | 217.1 | 335.5 | 337.4 | 399.2 | 451.4 | 222.5 | 248.3 | 350.8
1429 | 1310 | 216.9 | 334.9 | 336.3 | 398.1 | 450.8 | 221.9 | 247.7 | 350.4
1430 | 1311 | 216.6 | 334.1 | 335.3 | 396.5 | 450.1 | 221.3 | 247.1 | 350.1
1431 | 1312 | 216.3 | 333.1 | 334.2 | 395.1 | 449.4 | 220.9 | 246.5 | 349.7
1432 | 1313 | 215.9 | 332.3 | 332.6 | 393.9 | 448.8 | 219.8 | 245.9 | 349.3
1433 | 1314 | 215.6 | 331.6 | 331.5 | 392.5 | 448 | 219 | 245.2 | 348.9
1434 | 1315 | 215.3 | 330.6 | 330.9 | 391.2 | 447.2 | 219.1 | 244.7 | 348.5
1435 | 1316 | 215 | 329.7 | 329.6 | 390.1 | 446.6 | 218.8 | 244.1 | 348.1
1436 | 1317 | 214.7 | 328.9 | 327.9 | 388.9 | 446.1 | 218.9 | 243.5 | 347.8
1437 | 1318 | 214.4 | 327.9 | 326.6 | 387.6 | 445.2 | 218.8 | 242.8 | 347.4
1438 | 1319 | 214 | 326.9 | 325.3 | 386.3 | 444.4 | 218.7 | 242.2 | 347.1
1439 | 1320 | 213.6 | 326.1 | 324.8 | 384.8 | 443.8 | 218.5 | 241.6 | 346.7
1440 | 1321 | 213.3 | 325.2 | 324.3 | 382.7 | 443.1 | 218.1 | 241 | 346.3
1441 | 1322 | 213 | 324.2 | 322.4 | 380.9 | 442.3 | 217.8 | 240.4 | 345.9
1442 | 1323 | 212.7 | 323.4 | 320.5 | 378.7 | 441.5 | 217.4 | 239.9 | 345.6
1443 | 1324 | 212.5 | 322.6 | 319.1 | 376.5 | 440.3 | 217 | 239.3 | 345.2
1444 | 1325 | 212.3 | 321.7 | 317.6 | 374.9 | 439.3 | 216.7 | 238.7 | 344.8
1445 | 1326 | 212.1 | 320.9 | 315.1 | 373.2 | 438.2 | 216.4 | 238.2 | 344.5
1446 | 1327 | 211.8 | 320 | 312.4 | 371.8 | 437.3 | 216.2 | 237.6 | 344.1
1447 | 1328 | 211.5 | 319.2 | 311.6 | 370.3 | 436.6 | 216.1 | 237 | 343.7
1448 | 1329 | 211.2 | 318.5 | 311.6 | 368.6 | 435.6 | 215.7 | 236.4 | 343.4
1449 | 1330 | 210.9 | 317.7 | 310.6 | 367.2 | 434.8 | 215.5 | 235.9 | 343
1450 | 1331 | 210.6 | 317.1 | 309.3 | 365.7 | 434.2 | 215.6 | 235.3 | 342.6
1451 | 1332 | 210.4 | 316.3 | 308.3 | 364.5 | 433.5 | 215.5 | 234.7 | 342.2
1452 | 1333 | 210.1 | 315.4 | 307.7 | 363.5 | 432.8 | 215.4 | 234.2 | 341.9
1453 | 1334 | 209.9 | 314.7 | 306.5 | 362.6 | 432.3 | 215.2 | 233.6 | 341.5
1454 | 1335 | 209.6 | 314 | 306.2 | 361.9 | 431.9 | 215.3 | 233 | 341.1
1455 | 1336 | 209.3 | 313.2 | 305.8 | 361.3 | 431.2 | 214.9 | 232.4 | 340.8
1456 | 1337 | 208.9 | 312.4 | 305.4 | 360.6 | 430.5 | 214.8 | 231.9 | 340.4
1457 | 1338 | 208.6 | 311.9 | 304.8 | 359.5 | 429.8 | 214.5 | 231.3 | 340
1458 | 1339 | 208.3 | 311.4 | 304 | 358.8 | 429.3 | 214.3 | 230.8 | 339.6
1459 | 1340 | 208 | 310.9 | 303.1 | 358 | 428.6 | 213.7 | 230.2 | 339.2
1460 | 1341 | 207.7 | 310.5 | 302.4 | 357.2 | 427.9 | 213.3 | 229.6 | 338.8
1461 | 1342 | 207.4 | 310 | 302.1 | 355.8 | 427 | 213.3 | 229 | 338.5
1462 | 1343 | 207.1 | 309.5 | 301.5 | 354 | 425.9 | 213.2 | 228.5 | 338.1
1463 | 1344 | 207 | 308.7 | 300.9 | 352.1 | 424.6 | 212.7 | 227.9 | 337.7
1464 | 1345 | 206.7 | 308.2 | 300 | 350.8 | 424 | 212.5 | 227.3 | 337.4
1465 | 1346 | 206.5 | 307.7 | 299.2 | 349.5 | 423.3 | 212.5 | 226.7 | 337
1466 | 1347 | 206.3 | 306.9 | 298.5 | 348.2 | 422.3 | 212.2 | 226.1 | 336.7
1467 | 1348 | 206 | 306.2 | 297.4 | 347.1 | 421.5 | 211.6 | 225.6 | 336.2
1468 | 1349 | 205.7 | 305.5 | 296.7 | 346.3 | 420.9 | 211.3 | 225 | 335.9
1469 | 1350 | 205.4 | 304.9 | 296.1 | 345.3 | 420.3 | 209.8 | 224.5 | 335.6
1470 | 1351 | 205.1 | 304.1 | 295.3 | 344.5 | 419.6 | 208.9 | 224 | 335.2
1471 | 1352 | 204.9 | 303.6 | 294.4 | 343.9 | 419.2 | 208.7 | 223.4 | 334.9
1472 | 1353 | 204.6 | 303 | 293.4 | 343.4 | 418.8 | 208.6 | 222.8 | 334.5
1473 | 1354 | 204.4 | 302.2 | 292.5 | 342.8 | 418.2 | 208.1 | 222.3 | 334.1
1474 | 1355 | 204.1 | 301.7 | 291 | 342.3 | 417.7 | 207 | 221.7 | 333.7
1475 | 1356 | 203.8 | 301.3 | 290.1 | 341.8 | 417.2 | 206.6 | 221.1 | 333.4
1476 | 1357 | 203.4 | 300.8 | 289.7 | 341.1 | 416.4 | 206.3 | 220.6 | 333.1
1477 | 1358 | 203.1 | 300.2 | 289.5 | 340.4 | 415.6 | 206.1 | 220.1 | 332.7
1478 | 1359 | 202.7 | 299.8 | 289 | 339.6 | 414.9 | 205.9 | 219.5 | 332.3
1479 | 1360 | 202.4 | 299.3 | 287.8 | 338.9 | 414 | 205.6 | 219 | 331.9
1480 | 1361 | 202.2 | 298.5 | 287 | 338 | 412.9 | 205.2 | 218.5 | 331.6
1481 | 1362 | 202 | 297.8 | 285.9 | 337.4 | 411.9 | 205 | 218 | 331.3
1482 | 1363 | 201.8 | 297.1 | 284.6 | 336.7 | 410.9 | 204.6 | 217.5 | 331
1483 | 1364 | 201.5 | 296.2 | 284.4 | 335.7 | 409.6 | 203.7 | 216.9 | 330.7
1484 | 1365 | 201.2 | 295.3 | 283.8 | 334.5 | 408.5 | 202.9 | 216.4 | 330.3
1485 | 1366 | 201 | 294.7 | 283.1 | 333.1 | 407.4 | 202.3 | 215.9 | 330
1486 | 1367 | 200.8 | 294 | 282.2 | 331.8 | 406.3 | 202.1 | 215.4 | 329.7
1487 | 1368 | 200.6 | 293 | 280.6 | 330.7 | 405.2 | 201.6 | 214.8 | 329.4
1488 | 1369 | 200.3 | 292.5 | 279.7 | 329.7 | 404.5 | 201.2 | 214.3 | 329.1
1489 | 1370 | 200.1 | 291.8 | 279.1 | 328.7 | 403.7 | 201 | 213.8 | 328.7
1490 | 1371 | 199.9 | 291.1 | 278.7 | 327.9 | 402.8 | 200.6 | 213.3 | 328.4
1491 | 1372 | 199.6 | 290.4 | 278.5 | 327 | 402 | 200 | 212.7 | 328.1
1492 | 1373 | 199.4 | 289.8 | 277.6 | 326.3 | 401.4 | 199.4 | 212.2 | 327.7
1493 | 1374 | 199.1 | 289 | 276.7 | 325.7 | 400.7 | 199.1 | 211.7 | 327.4
1494 | 1375 | 198.9 | 288.3 | 275.7 | 325.1 | 399.9 | 198.8 | 211.2 | 327
1495 | 1376 | 198.6 | 287.2 | 274.6 | 324.6 | 399.3 | 198.5 | 210.6 | 326.6
1496 | 1377 | 198.3 | 285.1 | 273.9 | 324.1 | 398.6 | 198.1 | 210.2 | 326.3
1497 | 1378 | 197.9 | 282.8 | 273.2 | 323.5 | 397.8 | 197.9 | 209.7 | 325.9
1498 | 1379 | 197.6 | 280.8 | 272.5 | 323 | 396.9 | 196.8 | 209.2 | 325.5
1499 | 1380 | 197.3 | 279.3 | 271.6 | 322.6 | 396.4 | 195.4 | 208.8 | 325.2
1500 | 1381 | 197.1 | 277.7 | 271 | 322.2 | 395.8 | 195.4 | 208.2 | 324.8
1501 | 1382 | 196.9 | 275.9 | 270.6 | 321.7 | 395 | 194.6 | 207.7 | 324.4
1502 | 1383 | 196.6 | 274.2 | 269.8 | 321.2 | 394.2 | 194.2 | 207.2 | 324
1503 | 1384 | 196.4 | 272.4 | 269.5 | 320.3 | 392.9 | 194.2 | 206.8 | 323.6
1504 | 1385 | 196.2 | 270.4 | 268.5 | 319.2 | 391.6 | 193.5 | 206.3 | 323.2
1505 | 1386 | 195.9 | 268.7 | 267.5 | 318 | 390.5 | 193.1 | 205.7 | 322.8
1506 | 1387 | 195.7 | 267.1 | 266.6 | 316.9 | 389.4 | 191.9 | 205.2 | 322.4
1507 | 1388 | 195.5 | 265.3 | 266 | 315.8 | 388.2 | 191.3 | 204.8 | 321.9
1508 | 1389 | 195.3 | 263.8 | 265.4 | 314.8 | 387.1 | 191 | 204.3 | 321.5
1509 | 1390 | 195.1 | 262.9 | 264.8 | 313.9 | 386.2 | 190.5 | 203.8 | 321.1
1510 | 1391 | 194.9 | 261.7 | 264.3 | 313 | 385.1 | 190.6 | 203.3 | 320.7
1511 | 1392 | 194.6 | 260.1 | 263.7 | 312.1 | 384 | 190.2 | 202.9 | 320.3
1512 | 1393 | 194.4 | 258.5 | 263.2 | 310.9 | 383 | 189.4 | 202.4 | 319.9
1513 | 1394 | 194.2 | 257.3 | 262.3 | 309.8 | 382 | 189 | 202 | 319.6
1514 | 1395 | 193.9 | 256.2 | 261.4 | 308.5 | 380.5 | 188.3 | 201.5 | 319.2
1515 | 1396 | 193.8 | 254.7 | 260.6 | 307.2 | 378.9 | 188.1 | 201.1 | 318.9
1516 | 1397 | 193.6 | 253.5 | 259.7 | 306.1 | 377.8 | 187.2 | 200.6 | 318.6
1517 | 1398 | 193.3 | 252.7 | 259 | 305.3 | 377.3 | 186.9 | 200.1 | 318.2
1518 | 1399 | 193 | 251.6 | 258.6 | 304.4 | 376.9 | 186.6 | 199.7 | 317.9
1519 | 1400 | 192.7 | 250.4 | 257.8 | 303.6 | 376.4 | 186.1 | 199.2 | 317.4
1520 | 1401 | 192.3 | 249.5 | 256.7 | 302.9 | 375.8 | 185.7 | 198.7 | 317
1521 | 1402 | 192 | 248.7 | 255.9 | 302.2 | 374.9 | 185.4 | 198.3 | 316.7
1522 | 1403 | 191.7 | 247.5 | 255.5 | 301.2 | 373.7 | 185 | 197.8 | 316.3
1523 | 1404 | 191.5 | 246.3 | 254.5 | 300.3 | 373.1 | 184.5 | 197.4 | 315.9
1524 | 1405 | 191.3 | 245.1 | 253.5 | 299.3 | 372.4 | 184.5 | 196.9 | 315.5
1525 | 1406 | 191.1 | 243.9 | 252.8 | 298.1 | 371.6 | 184 | 196.5 | 315.2
1526 | 1407 | 190.9 | 242.9 | 252.3 | 297.1 | 370.7 | 183.5 | 196.1 | 314.8
1527 | 1408 | 190.7 | 242.1 | 251.5 | 296.1 | 370.1 | 183.2 | 195.7 | 314.3
1528 | 1409 | 190.5 | 241.1 | 250.9 | 295 | 369.1 | 182.8 | 195.3 | 313.9
1529 | 1410 | 190.3 | 240.1 | 250.9 | 293.9 | 367.8 | 182.3 | 194.9 | 313.5
1530 | 1411 | 190.1 | 239.4 | 250.4 | 292.8 | 367 | 181.4 | 194.4 | 313.1
1531 | 1412 | 189.8 | 238.5 | 250 | 291.4 | 365.8 | 180.7 | 194 | 312.7
1532 | 1413 | 189.6 | 237.3 | 249.4 | 289.8 | 364.7 | 180.7 | 193.5 | 312.2
1533 | 1414 | 189.4 | 236.3 | 248.6 | 288.2 | 363.5 | 180.3 | 193.1 | 311.8
1534 | 1415 | 189.2 | 235.6 | 247.5 | 286.6 | 362.1 | 179.9 | 192.7 | 311.4
1535 | 1416 | 189 | 234.7 | 246.7 | 284.9 | 360.8 | 179.5 | 192.2 | 311.1
1536 | 1417 | 188.8 | 233.6 | 246.3 | 283.5 | 359.9 | 179 | 191.9 | 310.7
1537 | 1418 | 188.6 | 232.7 | 245.5 | 282.5 | 359.2 | 178.7 | 191.4 | 310.2
1538 | 1419 | 188.5 | 231.8 | 244.9 | 281.5 | 358.2 | 178.6 | 191 | 309.9
1539 | 1420 | 188.3 | 231 | 244.5 | 280.4 | 356.8 | 178.9 | 190.7 | 309.6
1540 | 1421 | 188 | 230.1 | 244.2 | 279.3 | 355.6 | 178.6 | 190.3 | 309.3
1541 | 1422 | 187.7 | 229.3 | 243.5 | 278.1 | 354.5 | 178.3 | 189.9 | 308.9
1542 | 1423 | 187.4 | 228.3 | 242.8 | 276.6 | 353.4 | 177.6 | 189.4 | 308.5
1543 | 1424 | 187.2 | 227.5 | 241.5 | 275.4 | 352.2 | 177.2 | 189.1 | 308.1
1544 | 1425 | 187 | 226.9 | 240.3 | 274.5 | 351.6 | 176.7 | 188.7 | 307.7
1545 | 1426 | 186.8 | 226.4 | 239.9 | 273.7 | 350.9 | 175.3 | 188.3 | 307.3
1546 | 1427 | 186.6 | 225.9 | 239.5 | 272.9 | 349.9 | 174.6 | 187.9 | 307
1547 | 1428 | 186.3 | 225.6 | 238.6 | 272.1 | 348.8 | 174.2 | 187.5 | 306.6
1548 | 1429 | 186.1 | 225.3 | 236.9 | 271.5 | 348.3 | 173.8 | 187.1 | 306.1
1549 | 1430 | 185.9 | 224.9 | 236.6 | 270.8 | 347.7 | 173.5 | 186.7 | 305.8
1550 | 1431 | 185.7 | 224.6 | 237.3 | 270.2 | 347.1 | 173.1 | 186.3 | 305.4
1551 | 1432 | 185.4 | 224.5 | 237.2 | 269.8 | 346.6 | 172.3 | 185.9 | 304.9
1552 | 1433 | 185.2 | 224.7 | 237.1 | 269.6 | 346.3 | 171.8 | 185.5 | 304.5
1553 | 1434 | 184.9 | 224.7 | 237.3 | 269.2 | 346 | 171.1 | 185.1 | 304.1
1554 | 1435 | 184.7 | 224.7 | 237.2 | 268.9 | 345.2 | 169.7 | 184.7 | 303.7
1555 | 1436 | 184.4 | 224.6 | 236.6 | 268.7 | 344.5 | 168.5 | 184.3 | 303.3
1556 | 1437 | 184.2 | 224.4 | 236.1 | 268.3 | 343.8 | 168.3 | 183.9 | 302.9
1557 | 1438 | 184 | 223.9 | 235.7 | 267.5 | 342.9 | 167.8 | 183.5 | 302.5
1558 | 1439 | 183.9 | 223.4 | 234.4 | 266.8 | 342.5 | 167.1 | 183.1 | 302
1559 | 1440 | 183.6 | 223 | 233.7 | 266.2 | 342.5 | 166.8 | 182.7 | 301.6
1560 | 1441 | 183.2 | 222.6 | 233.3 | 265.6 | 341.7 | 165.8 | 182.3 | 301.3
1561 | 1442 | 183 | 222.2 | 232.7 | 264.9 | 340.7 | 165.6 | 181.9 | 300.8
1562 | 1443 | 182.8 | 222.1 | 232.6 | 264.3 | 339.8 | 165.2 | 181.5 | 300.5
1563 | 1444 | 182.6 | 221.7 | 232.4 | 263.6 | 338.8 | 165.3 | 181.1 | 300.1
1564 | 1445 | 182.3 | 221.3 | 232.1 | 262.8 | 337.9 | 165 | 180.7 | 299.6
1565 | 1446 | 182.1 | 221 | 231.9 | 262.1 | 337.3 | 164.7 | 180.4 | 299.1
1566 | 1447 | 181.9 | 220.9 | 231.2 | 261.5 | 337.2 | 164.4 | 180 | 298.7
1567 | 1448 | 181.6 | 220.2 | 230.5 | 260.7 | 336.8 | 164.1 | 179.6 | 298.2
1568 | 1449 | 181.4 | 219.4 | 230.5 | 259.5 | 335.7 | 163.7 | 179.2 | 297.9
1569 | 1450 | 181.1 | 218.8 | 229.8 | 258.3 | 334.7 | 163.5 | 178.9 | 297.5
1570 | 1451 | 181 | 218.1 | 229 | 256.7 | 333.5 | 162.9 | 178.5 | 297.1
1571 | 1452 | 180.8 | 217.2 | 229.1 | 255.2 | 332.3 | 162.5 | 178.1 | 296.8
1572 | 1453 | 180.6 | 216.6 | 228.3 | 253.8 | 331.7 | 162.5 | 177.7 | 296.4
1573 | 1454 | 180.4 | 216 | 227.6 | 252.5 | 331.1 | 162.3 | 177.4 | 296
1574 | 1455 | 180.2 | 215.3 | 227.4 | 251.2 | 330.4 | 162 | 177 | 295.7
1575 | 1456 | 180.1 | 214.4 | 226.7 | 249 | 329.2 | 161.6 | 176.6 | 295.3
1576 | 1457 | 179.9 | 213.9 | 225.5 | 247.6 | 328.5 | 161.1 | 176.3 | 294.9
1577 | 1458 | 179.7 | 213.2 | 225.4 | 246.6 | 327.7 | 160.9 | 176 | 294.4
1578 | 1459 | 179.6 | 212.4 | 225.4 | 245.5 | 327 | 160.6 | 175.6 | 294
1579 | 1460 | 179.3 | 211.7 | 224.6 | 244.3 | 326.4 | 160.4 | 175.3 | 293.5
1580 | 1461 | 179.1 | 211 | 223.8 | 243.2 | 325.9 | 160.2 | 175 | 293.1
1581 | 1462 | 178.8 | 210.2 | 223.4 | 242.3 | 325.4 | 159.9 | 174.7 | 292.8
1582 | 1463 | 178.7 | 209.4 | 222.7 | 241.5 | 324.6 | 159.5 | 174.3 | 292.4
1583 | 1464 | 178.4 | 208.9 | 221.7 | 241 | 324.1 | 159.5 | 174 | 292
1584 | 1465 | 178.2 | 208.5 | 221.3 | 240.2 | 323.1 | 159 | 173.7 | 291.5
1585 | 1466 | 178 | 208.1 | 221.7 | 238.8 | 322.3 | 158.2 | 173.4 | 291.1
1586 | 1467 | 177.8 | 207.8 | 221.6 | 238.2 | 322.4 | 158.2 | 173 | 290.6
1587 | 1468 | 177.6 | 207.5 | 221.7 | 237.6 | 322.6 | 157.7 | 172.7 | 290.2
1588 | 1469 | 177.4 | 207.3 | 221.9 | 237.2 | 322.8 | 157.5 | 172.3 | 289.7
1589 | 1470 | 177.2 | 207.2 | 222.4 | 237 | 322.8 | 156.9 | 172 | 289.4
1590 | 1471 | 176.9 | 207.4 | 222.3 | 236.9 | 322.9 | 156 | 171.7 | 288.9
1591 | 1472 | 176.7 | 207.6 | 222.1 | 237 | 322.9 | 155.6 | 171.4 | 288.5
1592 | 1473 | 176.5 | 207.9 | 222.5 | 237 | 322.8 | 155 | 171.2 | 288.1
1593 | 1474 | 176.3 | 208.3 | 222.4 | 237.1 | 322.6 | 155.1 | 170.8 | 287.6
1594 | 1475 | 176.1 | 208.8 | 222 | 237.2 | 322.4 | 154.6 | 170.5 | 287.2
1595 | 1476 | 175.9 | 209.2 | 221.9 | 237.3 | 322.3 | 153.8 | 170.2 | 286.8
1596 | 1477 | 175.7 | 209.5 | 222.1 | 237.4 | 321.9 | 153.2 | 169.9 | 286.4
1597 | 1478 | 175.5 | 209.9 | 221.9 | 237.6 | 321.5 | 153 | 169.5 | 286
1598 | 1479 | 175.2 | 210.1 | 221.6 | 237.7 | 321 | 153 | 169.2 | 285.6
1599 | 1480 | 175.1 | 210 | 221.6 | 237.8 | 320.3 | 153.1 | 169 | 285.2
1600 | 1481 | 174.9 | 209.9 | 221 | 237.7 | 319.7 | 152.3 | 168.8 | 284.8
1601 | 1482 | 174.7 | 209.7 | 220.8 | 237.3 | 319.1 | 151.8 | 168.5 | 284.3
1602 | 1483 | 174.4 | 209.5 | 220.5 | 236.9 | 318.4 | 152 | 168.2 | 283.9
1603 | 1484 | 174.2 | 209.2 | 220.4 | 236.4 | 317.7 | 151.5 | 167.9 | 283.5
1604 | 1485 | 174.1 | 209.3 | 220.1 | 236.1 | 317.4 | 150.9 | 167.6 | 283
1605 | 1486 | 173.9 | 209.1 | 219.9 | 235.8 | 316.7 | 150.5 | 167.3 | 282.6
1606 | 1487 | 173.7 | 209.1 | 219.7 | 235.4 | 315.6 | 149.9 | 167.1 | 282.2
1607 | 1488 | 173.4 | 209.1 | 219.2 | 235.1 | 315 | 149.6 | 166.7 | 281.7
1608 | 1489 | 173.2 | 209 | 218.8 | 234.8 | 314.6 | 148.9 | 166.4 | 281.3
1609 | 1490 | 172.9 | 208.7 | 218.5 | 234.5 | 314 | 148.3 | 166.1 | 280.8
1610 | 1491 | 172.7 | 208.4 | 218.3 | 234.2 | 313.4 | 148.4 | 165.8 | 280.3
1611 | 1492 | 172.4 | 208.2 | 217.8 | 234 | 313.1 | 148.5 | 165.6 | 279.9
1612 | 1493 | 172.2 | 207.9 | 217.5 | 233.7 | 312.7 | 147.9 | 165.4 | 279.5
1613 | 1494 | 172 | 207.4 | 217.5 | 233.2 | 311.9 | 147.2 | 165.1 | 279.1
1614 | 1495 | 171.8 | 207.2 | 216.9 | 232.9 | 311.5 | 146.5 | 164.8 | 278.6
1615 | 1496 | 171.6 | 206.9 | 216.5 | 232.5 | 311 | 146.3 | 164.4 | 278.2
1616 | 1497 | 171.4 | 206.5 | 216.3 | 231.9 | 309.9 | 145.8 | 164.1 | 277.9
1617 | 1498 | 171.2 | 206 | 216 | 231.2 | 308.8 | 145.1 | 163.8 | 277.5
1618 | 1499 | 171 | 205.7 | 215.5 | 230.5 | 308 | 144 | 163.5 | 277.1
1619 | 1500 | 170.9 | 205.3 | 215.4 | 229.9 | 306.9 | 143.1 | 163.2 | 276.8
1620 | 1501 | 170.7 | 204.9 | 215.1 | 229.3 | 305.8 | 142.4 | 163 | 276.4
1621 | 1502 | 170.5 | 204.6 | 214.4 | 228.9 | 305.1 | 141.6 | 162.7 | 275.9
1622 | 1503 | 170.4 | 204.2 | 213.7 | 228.4 | 304.7 | 141.3 | 162.3 | 275.4
1623 | 1504 | 170.2 | 203.8 | 213.2 | 227.9 | 303.8 | 141.3 | 162.1 | 275.1
1624 | 1505 | 170 | 203.4 | 213.2 | 227.2 | 302.5 | 141.1 | 161.8 | 274.8
1625 | 1506 | 169.9 | 203.1 | 212.5 | 226.5 | 301.7 | 140.8 | 161.5 | 274.3
1626 | 1507 | 169.7 | 202.6 | 212.3 | 225.9 | 301 | 140.8 | 161.2 | 273.8
1627 | 1508 | 169.4 | 201.8 | 212.4 | 225.1 | 300 | 140.5 | 161 | 273.4
1628 | 1509 | 169.1 | 201.3 | 212 | 224.5 | 298.9 | 139.9 | 160.7 | 273.1
1629 | 1510 | 168.9 | 201 | 211.8 | 223.7 | 297.6 | 139.2 | 160.4 | 272.7
1630 | 1511 | 168.7 | 200.7 | 211.6 | 223 | 296.2 | 138.3 | 160.1 | 272.3
1631 | 1512 | 168.5 | 200.4 | 211.4 | 222.3 | 294.8 | 137.9 | 159.8 | 271.9
1632 | 1513 | 168.3 | 200.1 | 210.9 | 221.8 | 293.7 | 137.9 | 159.5 | 271.5
1633 | 1514 | 168.1 | 199.8 | 210.3 | 221.3 | 292.2 | 137.9 | 159.2 | 271.2
1634 | 1515 | 167.9 | 199.4 | 209.9 | 220.7 | 290.4 | 137.8 | 158.9 | 270.8
1635 | 1516 | 167.6 | 199.1 | 209.2 | 220.1 | 289.1 | 137.3 | 158.7 | 270.3
1636 | 1517 | 167.4 | 198.8 | 208.3 | 219.4 | 287.7 | 136.8 | 158.5 | 269.9
1637 | 1518 | 167.1 | 198.4 | 207.7 | 218.6 | 286.2 | 136.5 | 158.3 | 269.4
1638 | 1519 | 166.9 | 197.7 | 207.3 | 217.8 | 284.8 | 136 | 158 | 269.1
1639 | 1520 | 166.6 | 197.1 | 206.6 | 217.1 | 283.5 | 135.5 | 157.8 | 268.7
1640 | 1521 | 166.4 | 196.3 | 206.4 | 216.4 | 282.1 | 135.2 | 157.5 | 268.3
1641 | 1522 | 166.3 | 195.6 | 205.8 | 215.5 | 280.9 | 135.2 | 157.3 | 267.9
1642 | 1523 | 166.1 | 195 | 205 | 214.7 | 279.9 | 134.6 | 157 | 267.6
1643 | 1524 | 165.9 | 194.5 | 204.1 | 214.1 | 279 | 134 | 156.8 | 267.2
1644 | 1525 | 165.7 | 194.1 | 203.7 | 213.5 | 277.8 | 133.7 | 156.5 | 266.9
1645 | 1526 | 165.5 | 193.2 | 203.3 | 213 | 276.5 | 133.5 | 156.2 | 266.5
1646 | 1527 | 165.3 | 192.5 | 202.6 | 212.5 | 275.4 | 133.1 | 155.9 | 266.2
1647 | 1528 | 165.1 | 191.9 | 201.7 | 211.7 | 274.2 | 132.8 | 155.7 | 265.9
1648 | 1529 | 164.9 | 191.3 | 201.3 | 211 | 273.1 | 132.7 | 155.4 | 265.5
1649 | 1530 | 164.7 | 190.6 | 200.5 | 210.4 | 272.2 | 132.1 | 155.1 | 265.1
1650 | 1531 | 164.6 | 189.9 | 199.9 | 209.5 | 271 | 131.7 | 154.9 | 264.8
1651 | 1532 | 164.4 | 189 | 198.9 | 208.4 | 269.4 | 131.6 | 154.6 | 264.5
1652 | 1533 | 164.3 | 188.3 | 198.6 | 206.8 | 267.3 | 131.3 | 154.3 | 264.2
1653 | 1534 | 164.2 | 187.7 | 198 | 205.6 | 265.9 | 131.2 | 154.1 | 263.8
1654 | 1535 | 164.1 | 187.1 | 197.7 | 204.7 | 264.8 | 131.1 | 153.8 | 263.5
1655 | 1536 | 163.9 | 186.5 | 197.9 | 204.1 | 263.6 | 131 | 153.5 | 263.2
1656 | 1537 | 163.7 | 186.2 | 197.5 | 203.6 | 262.5 | 130.7 | 153.3 | 262.8
1657 | 1538 | 163.5 | 186 | 197.1 | 203 | 261.5 | 130.9 | 153.1 | 262.6
1658 | 1539 | 163.4 | 185.6 | 197 | 202.3 | 260.5 | 130.5 | 152.8 | 262.2
1659 | 1540 | 163.2 | 185.3 | 197.1 | 201.7 | 259.8 | 129.9 | 152.7 | 262
1660 | 1541 | 163 | 185.3 | 196.8 | 201 | 259.5 | 129.8 | 152.4 | 261.7
1661 | 1542 | 162.9 | 185.1 | 196.7 | 200.3 | 259.2 | 129.7 | 152.2 | 261.4
1662 | 1543 | 162.7 | 184.6 | 196.8 | 199.6 | 258.6 | 129.5 | 151.9 | 261.1
1663 | 1544 | 162.5 | 184.3 | 196.3 | 199 | 258.2 | 129 | 151.7 | 260.8
1664 | 1545 | 162.3 | 184.1 | 196.1 | 198.8 | 257.8 | 128.7 | 151.4 | 260.4
1665 | 1546 | 162.1 | 183.9 | 195.9 | 198.4 | 257.3 | 128.4 | 151.1 | 260.1
1666 | 1547 | 161.9 | 183.6 | 195.5 | 197.7 | 256.7 | 128.4 | 150.9 | 259.8
1667 | 1548 | 161.7 | 183.2 | 194.9 | 196.9 | 256.4 | 128.1 | 150.7 | 259.5
1668 | 1549 | 161.5 | 182.8 | 194.8 | 195.8 | 255.8 | 127.6 | 150.4 | 259.3
1669 | 1550 | 161.4 | 182.5 | 194.4 | 194.5 | 255.3 | 127.3 | 150.2 | 259.1
1670 | 1551 | 161.2 | 182.2 | 194.1 | 194 | 255.1 | 127.4 | 150 | 258.8
1671 | 1552 | 161.1 | 182 | 193.9 | 193.7 | 254.9 | 126.3 | 149.8 | 258.5
1672 | 1553 | 161 | 181.9 | 193.7 | 193.4 | 254.4 | 126 | 149.5 | 258.2
1673 | 1554 | 160.8 | 181.7 | 193.4 | 193 | 253.9 | 125.8 | 149.2 | 257.9
1674 | 1555 | 160.7 | 181.5 | 193.1 | 192.6 | 253.6 | 125.5 | 149 | 257.5
1675 | 1556 | 160.4 | 181.2 | 192.7 | 192 | 253.3 | 124.8 | 148.7 | 257.2
1676 | 1557 | 160.2 | 180.8 | 192.4 | 191.3 | 252.9 | 124.6 | 148.4 | 256.9
1677 | 1558 | 160.1 | 180.6 | 191.9 | 190.8 | 252.5 | 124.6 | 148.2 | 256.6
1678 | 1559 | 159.9 | 180.4 | 191.5 | 190.7 | 252.1 | 124.3 | 147.9 | 256.2
1679 | 1560 | 159.8 | 180.1 | 191.3 | 190.5 | 251.6 | 123.9 | 147.7 | 255.8
1680 | 1561 | 159.6 | 179.8 | 191 | 190.2 | 250.9 | 123.5 | 147.4 | 255.4
1681 | 1562 | 159.4 | 179.6 | 190.4 | 189.1 | 249.6 | 122.6 | 147.1 | 255
1682 | 1563 | 159.2 | 179.3 | 190.2 | 187.5 | 247.7 | 122.2 | 146.9 | 254.6
1683 | 1564 | 159.1 | 179 | 190.1 | 186 | 245 | 122.1 | 146.6 | 254.2
1684 | 1565 | 158.9 | 178.6 | 189.5 | 184.6 | 242.5 | 122.1 | 146.4 | 253.7
1685 | 1566 | 158.7 | 178.3 | 188.9 | 183.2 | 240.5 | 121.7 | 146.2 | 253.3
1686 | 1567 | 158.5 | 177.8 | 188.6 | 181.9 | 238.8 | 121.4 | 146 | 252.9
1687 | 1568 | 158.3 | 177.3 | 188.3 | 180.9 | 236.7 | 120.9 | 145.8 | 252.5
1688 | 1569 | 158.1 | 177.1 | 187.7 | 180.5 | 234.6 | 120.2 | 145.6 | 252.1
1689 | 1570 | 157.8 | 177 | 187.3 | 180.2 | 232.6 | 119.7 | 145.4 | 251.6
1690 | 1571 | 157.6 | 176.8 | 187 | 179.7 | 230.9 | 119.2 | 145.1 | 251.1
1691 | 1572 | 157.4 | 176.5 | 186.5 | 179.3 | 229.7 | 118.8 | 144.9 | 250.6
1692 | 1573 | 157.3 | 176.2 | 186 | 178.8 | 228.3 | 118.5 | 144.7 | 250.1
1693 | 1574 | 157 | 176 | 185.5 | 178.3 | 227 | 118.4 | 144.5 | 249.6
1694 | 1575 | 156.9 | 175.7 | 185.1 | 177.6 | 225.1 | 118.3 | 144.3 | 249.2
1695 | 1576 | 156.7 | 175.5 | 184.6 | 177 | 223.5 | 118 | 144.1 | 248.8
1696 | 1577 | 156.5 | 175.3 | 184.2 | 176.3 | 221.7 | 117.4 | 143.9 | 248.4
1697 | 1578 | 156.3 | 175 | 183.9 | 175.5 | 220.1 | 117.2 | 143.6 | 248
1698 | 1579 | 156.2 | 174.8 | 183.3 | 175 | 218.2 | 117.1 | 143.4 | 247.7
1699 | 1580 | 156.1 | 174.5 | 182.9 | 174.5 | 216.7 | 116.7 | 143.2 | 247.2
1700 | 1581 | 155.9 | 174.2 | 182.6 | 174.3 | 215.8 | 116.8 | 143 | 246.9
1701 | 1582 | 155.7 | 173.8 | 182.3 | 174 | 215 | 116.8 | 142.8 | 246.6
1702 | 1583 | 155.5 | 173.4 | 182 | 173.5 | 213.6 | 116.7 | 142.6 | 246.2
1703 | 1584 | 155.4 | 173 | 181.5 | 173.1 | 212.4 | 116.7 | 142.4 | 245.8
1704 | 1585 | 155.2 | 172.5 | 181.4 | 172.3 | 211.3 | 116 | 142.2 | 245.4
1705 | 1586 | 154.9 | 172.3 | 180.7 | 171.8 | 210.7 | 115.8 | 141.9 | 245.1
1706 | 1587 | 154.7 | 172 | 180.2 | 170.9 | 210.1 | 115.6 | 141.6 | 244.7
1707 | 1588 | 154.6 | 171.5 | 179.7 | 169.9 | 209 | 115.5 | 141.4 | 244.3
1708 | 1589 | 154.5 | 171 | 179.2 | 169.1 | 207.6 | 115.6 | 141.2 | 243.9
1709 | 1590 | 154.3 | 170.6 | 178.8 | 168.5 | 205.9 | 115.6 | 141 | 243.4
1710 | 1591 | 154.1 | 170.2 | 178.3 | 167.8 | 203.6 | 115.4 | 140.8 | 242.9
1711 | 1592 | 153.9 | 169.5 | 177.9 | 166.8 | 201.8 | 115.3 | 140.6 | 242.5
1712 | 1593 | 153.7 | 168.8 | 176.8 | 165.5 | 200.3 | 115.1 | 140.5 | 242
1713 | 1594 | 153.5 | 168.2 | 176 | 164.4 | 199.1 | 114.9 | 140.4 | 241.6
1714 | 1595 | 153.3 | 167.6 | 175.7 | 163.7 | 197 | 114.7 | 140.2 | 241.2
1715 | 1596 | 153.2 | 167.2 | 175.3 | 163.1 | 195 | 114.5 | 140 | 240.7
1716 | 1597 | 153 | 166.8 | 174.7 | 162.6 | 193.9 | 114.3 | 139.8 | 240.4
1717 | 1598 | 152.9 | 166.5 | 174.3 | 162.3 | 192.9 | 113.9 | 139.6 | 240
1718 | 1599 | 152.7 | 166.2 | 174.2 | 161.8 | 192.2 | 113.2 | 139.4 | 239.5
1719 | 1600 | 152.5 | 166 | 174.1 | 161.5 | 192.3 | 113.1 | 139.1 | 239.1
1720 | 1601 | 152.3 | 165.9 | 173.9 | 161.4 | 192 | 113.2 | 138.9 | 238.6
1721 | 1602 | 152.1 | 165.6 | 173.6 | 161.3 | 191.4 | 113.1 | 138.7 | 238.2
1722 | 1603 | 151.9 | 165.2 | 173.3 | 160.8 | 190.7 | 113.1 | 138.5 | 237.7
1723 | 1604 | 151.7 | 165.1 | 172.9 | 160.4 | 190.1 | 112.7 | 138.3 | 237.4
1724 | 1605 | 151.5 | 164.9 | 172.6 | 159.9 | 190.2 | 112.3 | 138.1 | 237
1725 | 1606 | 151.3 | 164.6 | 172.5 | 159.3 | 190.4 | 112.7 | 137.9 | 236.7
1726 | 1607 | 151.2 | 164.4 | 172 | 158.8 | 190.4 | 112.7 | 137.6 | 236.4
1727 | 1608 | 151 | 164.2 | 171.4 | 158.4 | 190.1 | 112.4 | 137.4 | 236.1
1728 | 1609 | 150.8 | 163.9 | 171.1 | 157.7 | 189.6 | 112 | 137.2 | 235.8
1729 | 1610 | 150.6 | 163.6 | 170.9 | 157.3 | 189.1 | 111.6 | 137 | 235.5
1730 | 1611 | 150.5 | 163.6 | 170.3 | 157.1 | 189.2 | 111.5 | 136.8 | 235.1
1731 | 1612 | 150.3 | 163.5 | 170 | 156.7 | 189.2 | 111.3 | 136.6 | 234.8
1732 | 1613 | 150.1 | 163.2 | 170 | 156.1 | 188.9 | 111.2 | 136.4 | 234.5
1733 | 1614 | 149.9 | 163.1 | 169.6 | 155.6 | 188.1 | 110.9 | 136.1 | 234.1
1734 | 1615 | 149.8 | 163 | 169.1 | 155.3 | 187.5 | 110.4 | 135.9 | 233.7
1735 | 1616 | 149.7 | 162.8 | 168.9 | 154.8 | 187.1 | 110.1 | 135.7 | 233.4
1736 | 1617 | 149.6 | 162.5 | 168.6 | 154.2 | 186.7 | 109.9 | 135.5 | 233
1737 | 1618 | 149.5 | 162.4 | 167.9 | 153.9 | 186.5 | 109.6 | 135.3 | 232.6
1738 | 1619 | 149.3 | 162 | 167.7 | 153.4 | 186.3 | 109.4 | 135.1 | 232.2
1739 | 1620 | 149.1 | 161.6 | 167.6 | 152.7 | 185.6 | 109.3 | 134.9 | 231.8
1740 | 1621 | 149 | 161.3 | 167.1 | 151.9 | 184.5 | 109.2 | 134.7 | 231.5
1741 | 1622 | 148.8 | 161 | 166.6 | 151.4 | 183.6 | 109.3 | 134.5 | 231.2
1742 | 1623 | 148.7 | 160.7 | 166.2 | 150.6 | 183.1 | 109.1 | 134.4 | 230.8
1743 | 1624 | 148.5 | 160.3 | 165.8 | 149.8 | 182.5 | 109 | 134.3 | 230.5
1744 | 1625 | 148.3 | 160.1 | 165.1 | 149.2 | 182 | 108.5 | 134.1 | 230.1
1745 | 1626 | 148.2 | 159.7 | 164.6 | 148.7 | 181.6 | 108 | 133.9 | 229.7
1746 | 1627 | 148.1 | 159.3 | 164.2 | 148.3 | 180.7 | 107.7 | 133.8 | 229.3
1747 | 1628 | 147.9 | 159 | 163.5 | 147.7 | 179.5 | 107.3 | 133.6 | 228.9
1748 | 1629 | 147.7 | 158.7 | 163 | 147.2 | 178.4 | 107 | 133.4 | 228.6
1749 | 1630 | 147.6 | 158.5 | 162.8 | 146.8 | 177.9 | 106.6 | 133.2 | 228.3
1750 | 1631 | 147.4 | 158.2 | 162.6 | 146.5 | 177.6 | 106.4 | 133.1 | 228
1751 | 1632 | 147.2 | 158 | 161.9 | 146.3 | 177.4 | 106.2 | 132.9 | 227.6
1752 | 1633 | 147.1 | 157.5 | 161.2 | 145.7 | 176.6 | 106.3 | 132.7 | 227.3
1753 | 1634 | 146.9 | 156.8 | 160.6 | 144.8 | 176 | 106.5 | 132.5 | 227
1754 | 1635 | 146.8 | 156.4 | 160.1 | 144.7 | 175.9 | 106.4 | 132.3 | 226.7
1755 | 1636 | 146.6 | 156.1 | 159.7 | 144.5 | 175.2 | 106.3 | 132.2 | 226.4
1756 | 1637 | 146.5 | 155.6 | 159.4 | 143.9 | 174.1 | 106.6 | 132 | 226.2
1757 | 1638 | 146.3 | 155.2 | 159.4 | 143 | 173.4 | 106.2 | 131.8 | 226
1758 | 1639 | 146.1 | 154.8 | 159.1 | 142 | 173 | 105.6 | 131.6 | 225.7
1759 | 1640 | 145.9 | 154.5 | 158.8 | 140.9 | 172.5 | 105.1 | 131.5 | 225.2
1760 | 1641 | 145.8 | 154.2 | 159 | 140.3 | 172 | 104.7 | 131.3 | 224.8
1761 | 1642 | 145.6 | 154.2 | 158.7 | 139.8 | 171.9 | 104.4 | 131.1 | 224.4
1762 | 1643 | 145.4 | 154 | 158.4 | 139.3 | 171.7 | 104.1 | 130.9 | 224
1763 | 1644 | 145.3 | 153.8 | 158.2 | 139.1 | 171.3 | 103.8 | 130.7 | 223.6
1764 | 1645 | 145.2 | 153.6 | 157.9 | 138.9 | 170.5 | 103.6 | 130.5 | 223.3
1765 | 1646 | 145.1 | 153.6 | 157.5 | 138.8 | 170.2 | 103.7 | 130.3 | 222.9
1766 | 1647 | 144.9 | 153.5 | 157.3 | 138.5 | 169.9 | 103.9 | 130.1 | 222.5
1767 | 1648 | 144.7 | 153.2 | 157.2 | 138.1 | 169.2 | 104 | 130 | 222.1
1768 | 1649 | 144.6 | 153 | 156.8 | 138.1 | 168.8 | 103.9 | 129.8 | 221.7
1769 | 1650 | 144.4 | 152.8 | 156.5 | 138 | 168.9 | 103.7 | 129.7 | 221.3
1770 | 1651 | 144.2 | 152.5 | 156.3 | 137.8 | 168.8 | 103 | 129.5 | 220.9
1771 | 1652 | 144.1 | 152.2 | 156.2 | 137.6 | 168.3 | 102.7 | 129.3 | 220.5
1772 | 1653 | 143.9 | 152.1 | 155.7 | 137.6 | 168 | 102.6 | 129.1 | 220.1
1773 | 1654 | 143.8 | 152 | 155.6 | 137.2 | 167.8 | 102.6 | 129 | 219.8
1774 | 1655 | 143.6 | 151.8 | 155.4 | 136.9 | 167.6 | 102.7 | 128.8 | 219.5
1775 | 1656 | 143.5 | 151.6 | 155.1 | 136.3 | 167.2 | 102.5 | 128.6 | 219.2
1776 | 1657 | 143.3 | 151.4 | 154.8 | 135.7 | 166.9 | 102.1 | 128.4 | 218.9
1777 | 1658 | 143.2 | 151 | 154.5 | 135.4 | 166.7 | 102 | 128.2 | 218.6
1778 | 1659 | 143.1 | 150.6 | 154.1 | 135 | 166.3 | 102 | 128.1 | 218.4
1779 | 1660 | 143 | 150.4 | 153.4 | 134.4 | 166.1 | 102.2 | 127.9 | 218
1780 | 1661 | 142.9 | 149.9 | 152.8 | 133.9 | 165.6 | 102.2 | 127.8 | 217.6
1781 | 1662 | 142.8 | 149.4 | 152.3 | 133.3 | 165.1 | 101.8 | 127.6 | 217.2
1782 | 1663 | 142.6 | 148.9 | 151.6 | 132.5 | 164.6 | 101.6 | 127.5 | 216.8
1783 | 1664 | 142.4 | 148.6 | 151.2 | 131.9 | 164 | 101.6 | 127.3 | 216.5
1784 | 1665 | 142.2 | 148.2 | 151 | 131.5 | 163.2 | 101.6 | 127.2 | 216.1
1785 | 1666 | 142 | 147.6 | 150.5 | 131 | 162.2 | 101.2 | 127 | 215.7
1786 | 1667 | 141.8 | 147.1 | 149.9 | 130.4 | 161.5 | 101.3 | 126.8 | 215.4
1787 | 1668 | 141.6 | 146.6 | 149.7 | 129.7 | 161.1 | 101.2 | 126.7 | 215
1788 | 1669 | 141.4 | 146.3 | 149.7 | 129.5 | 161.1 | 101.2 | 126.5 | 214.6
1789 | 1670 | 141.3 | 146.2 | 149.4 | 129.7 | 161 | 100.9 | 126.3 | 214.3
1790 | 1671 | 141.1 | 146.1 | 149.2 | 130 | 161 | 100.4 | 126.2 | 213.9
1791 | 1672 | 141.1 | 145.9 | 149.2 | 130.1 | 161.1 | 100.4 | 126.1 | 213.5
1792 | 1673 | 141 | 145.7 | 149 | 130.1 | 160.8 | 100 | 125.9 | 213.2
1793 | 1674 | 140.8 | 145.7 | 148.6 | 129.9 | 160.8 | 100 | 125.8 | 212.9
1794 | 1675 | 140.6 | 145.5 | 148.3 | 129.6 | 160.4 | 100 | 125.7 | 212.7
1795 | 1676 | 140.5 | 145.2 | 148.3 | 129.2 | 159.8 | 99.8 | 125.5 | 212.4
1796 | 1677 | 140.4 | 145 | 147.9 | 128.9 | 159.8 | 99.4 | 125.3 | 212.1
1797 | 1678 | 140.2 | 144.7 | 147.6 | 129 | 159.8 | 98.9 | 125.1 | 211.8
1798 | 1679 | 140.1 | 144.5 | 147.5 | 129.1 | 159.2 | 98.9 | 125 | 211.4
1799 | 1680 | 139.9 | 144.2 | 147.4 | 129 | 159.1 | 99.2 | 124.9 | 211
1800 | 1681 | 139.7 | 144.1 | 146.9 | 129 | 159.5 | 98.8 | 124.7 | 210.7
1801 | 1682 | 139.5 | 144 | 146.8 | 129 | 159.2 | 98.7 | 124.6 | 210.4
1802 | 1683 | 139.3 | 143.8 | 146.5 | 128.8 | 158.7 | 98.8 | 124.5 | 210
1803 | 1684 | 139.2 | 143.7 | 146 | 128.6 | 158.7 | 98.7 | 124.3 | 209.7
1804 | 1685 | 139.1 | 143.4 | 145.2 | 128.4 | 158.1 | 98.7 | 124.2 | 209.4
1805 | 1686 | 138.9 | 143 | 144.7 | 127.7 | 157 | 98.5 | 124.1 | 209.2
1806 | 1687 | 138.9 | 142.7 | 144.4 | 126.9 | 156.1 | 98.4 | 123.9 | 208.8
1807 | 1688 | 138.8 | 142.5 | 144 | 126.5 | 155.7 | 98.4 | 123.8 | 208.5
1808 | 1689 | 138.7 | 142.3 | 143.7 | 126.3 | 154.8 | 98.3 | 123.6 | 208
1809 | 1690 | 138.5 | 142 | 143.6 | 126.1 | 154 | 98.5 | 123.5 | 207.7
1810 | 1691 | 138.4 | 141.7 | 143.3 | 125.7 | 153.9 | 98.2 | 123.3 | 207.5
1811 | 1692 | 138.2 | 141.4 | 142.7 | 125.2 | 153.7 | 97.9 | 123.2 | 207.2
1812 | 1693 | 138.1 | 141.1 | 142.4 | 124.8 | 153.4 | 97.9 | 123 | 207
1813 | 1694 | 138 | 140.7 | 142.2 | 124.2 | 152.8 | 97.8 | 122.9 | 206.8
1814 | 1695 | 137.8 | 140.3 | 141.2 | 123.7 | 152.6 | 97.7 | 122.8 | 206.6
1815 | 1696 | 137.7 | 139.9 | 140.8 | 123.6 | 152.7 | 97.4 | 122.6 | 206.3
1816 | 1697 | 137.5 | 139.5 | 140.8 | 123.8 | 152.4 | 97.1 | 122.5 | 206.1
1817 | 1698 | 137.4 | 139.2 | 140.5 | 123.7 | 152 | 96.5 | 122.4 | 205.8
1818 | 1699 | 137.2 | 139 | 140.2 | 123.7 | 151.9 | 96.2 | 122.2 | 205.5
1819 | 1700 | 137 | 138.8 | 140.2 | 123.9 | 151.8 | 96.2 | 122.1 | 205.2
1820 | 1701 | 136.9 | 138.6 | 140.4 | 124 | 151.4 | 96.2 | 121.9 | 204.9
1821 | 1702 | 136.7 | 138.5 | 140.1 | 124.2 | 151.4 | 96 | 121.8 | 204.6
1822 | 1703 | 136.5 | 138.3 | 140 | 124.4 | 151.5 | 95.7 | 121.6 | 204.4
1823 | 1704 | 136.4 | 138.1 | 140 | 124.4 | 151.5 | 95.4 | 121.4 | 204.1
1824 | 1705 | 136.2 | 137.8 | 139.5 | 124.4 | 151.5 | 95.3 | 121.3 | 203.9
1825 | 1706 | 136.1 | 137.5 | 139.2 | 124.3 | 151.3 | 95.2 | 121.1 | 203.6
1826 | 1707 | 135.9 | 137.3 | 138.9 | 124.1 | 150.8 | 95.1 | 121 | 203.4
1827 | 1708 | 135.8 | 137 | 138.9 | 124 | 150.1 | 94.8 | 120.9 | 203.2
1828 | 1709 | 135.7 | 136.9 | 138.5 | 123.9 | 149.8 | 94.6 | 120.8 | 203
1829 | 1710 | 135.5 | 136.6 | 138 | 123.7 | 148.9 | 94.7 | 120.6 | 202.7
1830 | 1711 | 135.4 | 136.2 | 137.7 | 123.3 | 147.7 | 94.6 | 120.5 | 202.5
1831 | 1712 | 135.3 | 135.8 | 137.2 | 123 | 147.5 | 94.6 | 120.4 | 202.1
1832 | 1713 | 135.1 | 135.4 | 136.8 | 122.7 | 146.7 | 94.7 | 120.2 | 201.8
1833 | 1714 | 134.9 | 135 | 136.5 | 122.4 | 145.6 | 94.7 | 120.1 | 201.7
1834 | 1715 | 134.7 | 134.6 | 136.3 | 122.1 | 144.7 | 94.5 | 120 | 201.4
1835 | 1716 | 134.6 | 134.4 | 135.7 | 122 | 144.6 | 94.5 | 119.8 | 201.2
1836 | 1717 | 134.5 | 134 | 135.1 | 121.8 | 143.7 | 94.6 | 119.7 | 200.9
1837 | 1718 | 134.3 | 133.3 | 134.9 | 121.2 | 142.2 | 94.4 | 119.6 | 200.7
1838 | 1719 | 134.2 | 133 | 134.2 | 120.8 | 141.4 | 94.3 | 119.4 | 200.5
1839 | 1720 | 134 | 132.7 | 133.8 | 120.3 | 141.1 | 94.1 | 119.3 | 200.3
1840 | 1721 | 133.9 | 132.3 | 133.6 | 120 | 141 | 94.3 | 119.2 | 200.1
1841 | 1722 | 133.7 | 132.1 | 133.6 | 119.6 | 141 | 94.1 | 119.1 | 199.8
1842 | 1723 | 133.5 | 131.9 | 133.2 | 119.6 | 141.5 | 93.7 | 118.9 | 199.6
1843 | 1724 | 133.4 | 131.6 | 133.2 | 119.3 | 141.3 | 93.2 | 118.8 | 199.4
1844 | 1725 | 133.2 | 131.3 | 133.3 | 118.9 | 140.9 | 93.3 | 118.7 | 199.2
1845 | 1726 | 133 | 131.2 | 133.2 | 118.9 | 141 | 93.5 | 118.5 | 199
1846 | 1727 | 132.9 | 131.1 | 133 | 119 | 141 | 93.4 | 118.4 | 198.9
1847 | 1728 | 132.7 | 131 | 132.7 | 118.9 | 141 | 93.1 | 118.3 | 198.7
1848 | 1729 | 132.6 | 130.8 | 132.7 | 118.5 | 141.2 | 93.2 | 118.2 | 198.4
1849 | 1730 | 132.4 | 130.8 | 132.4 | 118.4 | 141.5 | 93 | 118.1 | 198.2
1850 | 1731 | 132.2 | 130.7 | 132.2 | 118.4 | 141.4 | 92.7 | 117.9 | 198.1
1851 | 1732 | 132.1 | 130.3 | 132.4 | 118 | 141 | 92.5 | 117.8 | 197.9
1852 | 1733 | 132.1 | 130.1 | 132.1 | 118.1 | 141.1 | 92.3 | 117.7 | 197.7
1853 | 1734 | 132 | 129.9 | 131.8 | 118.2 | 141.6 | 92 | 117.5 | 197.5
1854 | 1735 | 131.9 | 129.8 | 131.7 | 118.1 | 141.5 | 91.9 | 117.4 | 197.4
1855 | 1736 | 131.7 | 129.7 | 131.5 | 118 | 141.2 | 91.9 | 117.2 | 197.2
1856 | 1737 | 131.6 | 129.7 | 131.1 | 117.8 | 141.4 | 91.9 | 117.1 | 197
1857 | 1738 | 131.6 | 129.6 | 130.8 | 117.6 | 141.9 | 91.5 | 116.9 | 196.8
1858 | 1739 | 131.4 | 129.4 | 130.8 | 117.4 | 141.8 | 91.5 | 116.8 | 196.6
1859 | 1740 | 131.3 | 129.4 | 130.4 | 117.5 | 141.5 | 91 | 116.6 | 196.3
1860 | 1741 | 131.1 | 129.4 | 130 | 117.5 | 141.2 | 90.5 | 116.5 | 196
1861 | 1742 | 130.9 | 129.3 | 129.9 | 117.4 | 140.6 | 90.5 | 116.4 | 195.7
1862 | 1743 | 130.8 | 129 | 129.8 | 117.4 | 140.4 | 90.5 | 116.3 | 195.5
1863 | 1744 | 130.6 | 129 | 129.5 | 117.2 | 140.5 | 90.2 | 116.2 | 195.2
1864 | 1745 | 130.5 | 128.9 | 129.4 | 117.1 | 140.2 | 89.9 | 116.2 | 194.9
1865 | 1746 | 130.4 | 128.8 | 129.3 | 117 | 140.1 | 89.9 | 116.2 | 194.7
1866 | 1747 | 130.3 | 128.7 | 129.2 | 117.1 | 140.1 | 89.9 | 116.1 | 194.3
1867 | 1748 | 130.2 | 128.8 | 128.8 | 117.3 | 139.6 | 89.6 | 116.1 | 194
1868 | 1749 | 129.9 | 128.5 | 128.8 | 117.3 | 139.5 | 89.5 | 116 | 193.6
1869 | 1750 | 129.7 | 128.3 | 128.8 | 117.2 | 139.1 | 89.5 | 115.9 | 193.3
1870 | 1751 | 129.6 | 128.3 | 128.4 | 117.3 | 138.6 | 89.6 | 115.7 | 192.9
1871 | 1752 | 129.5 | 128.2 | 128.1 | 117.1 | 138.4 | 89.5 | 115.6 | 192.6
1872 | 1753 | 129.4 | 128.1 | 128.1 | 116.8 | 138.1 | 88.9 | 115.4 | 192.4
1873 | 1754 | 129.3 | 128 | 127.8 | 116.7 | 137.9 | 88.7 | 115.3 | 192.1
1874 | 1755 | 129.2 | 128.1 | 127.6 | 116.8 | 137.4 | 88.8 | 115.2 | 191.8
1875 | 1756 | 129.1 | 128 | 127.6 | 116.9 | 137.1 | 88.9 | 115.2 | 191.5
1876 | 1757 | 129 | 127.9 | 127.5 | 116.8 | 136.9 | 88.6 | 115.1 | 191.1
1877 | 1758 | 128.9 | 128 | 127.1 | 117 | 137.2 | 88.5 | 115 | 190.6
1878 | 1759 | 128.7 | 128.1 | 127 | 117.2 | 137.2 | 88.6 | 114.9 | 190.3
1879 | 1760 | 128.5 | 128 | 127 | 117.3 | 136.7 | 88.6 | 114.8 | 190
1880 | 1761 | 128.4 | 127.9 | 126.7 | 117.4 | 136.4 | 88.1 | 114.7 | 189.6
1881 | 1762 | 128.3 | 127.8 | 126.3 | 117.3 | 136.1 | 88.2 | 114.6 | 189.2
1882 | 1763 | 128.1 | 127.7 | 126.3 | 117.4 | 136.2 | 88.2 | 114.4 | 188.9
1883 | 1764 | 128 | 127.5 | 126.2 | 117.5 | 136.5 | 88.1 | 114.3 | 188.5
1884 | 1765 | 127.9 | 127.5 | 125.8 | 117.7 | 136.9 | 88.3 | 114.1 | 188.2
1885 | 1766 | 127.8 | 127.4 | 125.7 | 117.7 | 136.9 | 88.2 | 114 | 188
1886 | 1767 | 127.7 | 127.3 | 125.5 | 117.4 | 137 | 88 | 113.8 | 187.7
1887 | 1768 | 127.6 | 127.2 | 125.2 | 117.3 | 137.3 | 87.9 | 113.7 | 187.4
1888 | 1769 | 127.5 | 127.1 | 125.2 | 117.3 | 137.4 | 87.9 | 113.6 | 187.1
1889 | 1770 | 127.4 | 127 | 125 | 117.3 | 137 | 87.9 | 113.5 | 186.8
1890 | 1771 | 127.3 | 126.9 | 125 | 117.3 | 136.5 | 87.8 | 113.3 | 186.6
1891 | 1772 | 127.2 | 126.8 | 124.7 | 117.3 | 136.7 | 87.6 | 113.2 | 186.3
1892 | 1773 | 127 | 126.7 | 124.6 | 117.4 | 137.4 | 87.4 | 113 | 186
1893 | 1774 | 126.9 | 126.4 | 124.8 | 117.3 | 137.4 | 87.3 | 112.9 | 185.8
1894 | 1775 | 126.7 | 126.2 | 124.5 | 117.3 | 137.5 | 87.1 | 112.8 | 185.5
1895 | 1776 | 126.6 | 126 | 124.2 | 117.4 | 137.5 | 86.9 | 112.7 | 185.2
1896 | 1777 | 126.5 | 125.7 | 124 | 117.5 | 137.1 | 86.7 | 112.6 | 184.9
1897 | 1778 | 126.4 | 125.5 | 124.1 | 117.6 | 136.9 | 86.7 | 112.5 | 184.6
1898 | 1779 | 126.3 | 125.4 | 123.6 | 117.7 | 136.9 | 86.5 | 112.4 | 184.3
1899 | 1780 | 126.2 | 125 | 123.3 | 117.5 | 136.4 | 86.7 | 112.2 | 184
1900 | 1781 | 126.1 | 124.5 | 123.1 | 117.1 | 135.9 | 86.8 | 112.1 | 183.8
1901 | 1782 | 126 | 124.2 | 122.7 | 116.6 | 135.6 | 87 | 111.9 | 183.6
1902 | 1783 | 125.8 | 124 | 122.4 | 116.1 | 135.4 | 86.9 | 111.8 | 183.3
1903 | 1784 | 125.7 | 123.7 | 122.4 | 115.6 | 134.7 | 86.5 | 111.7 | 183.1
1904 | 1785 | 125.5 | 123.4 | 122.4 | 115 | 134.2 | 86.6 | 111.5 | 182.9
1905 | 1786 | 125.3 | 123.3 | 121.8 | 114.5 | 134.2 | 86.7 | 111.4 | 182.6
1906 | 1787 | 125.2 | 123.1 | 121.4 | 114.1 | 133.9 | 86.4 | 111.3 | 182.3
1907 | 1788 | 125 | 123 | 121.4 | 113.9 | 133.7 | 86.1 | 111.1 | 182
1908 | 1789 | 124.9 | 122.9 | 121.3 | 114 | 133.5 | 86.2 | 111 | 181.8
1909 | 1790 | 124.8 | 122.8 | 121.2 | 113.9 | 133.6 | 86.1 | 110.9 | 181.5
1910 | 1791 | 124.8 | 122.5 | 121.1 | 113.9 | 133.5 | 85.9 | 110.8 | 181.3
1911 | 1792 | 124.7 | 122.2 | 121 | 113.8 | 133.3 | 85.6 | 110.6 | 181
1912 | 1793 | 124.5 | 122.2 | 120.7 | 113.9 | 133.6 | 85.7 | 110.5 | 180.8
1913 | 1794 | 124.4 | 122.1 | 120.4 | 114 | 133.7 | 85.7 | 110.3 | 180.6
1914 | 1795 | 124.3 | 121.7 | 120.4 | 114 | 133.7 | 85.7 | 110.2 | 180.3
1915 | 1796 | 124.2 | 121.6 | 120.1 | 114 | 134 | 85.6 | 110 | 180.1
1916 | 1797 | 124.1 | 121.5 | 120 | 113.8 | 134.2 | 85.6 | 109.9 | 179.9
1917 | 1798 | 124 | 121.3 | 120.2 | 113.6 | 133.8 | 85.6 | 109.7 | 179.7
1918 | 1799 | 123.9 | 121.2 | 120.2 | 113.7 | 133.4 | 85.5 | 109.6 | 179.4
1919 | 1800 | 123.8 | 121.2 | 119.8 | 113.7 | 133.2 | 85.6 | 109.4 | 179.2
1920 | 1801 | 123.6 | 121.1 | 119.7 | 113.7 | 133 | 85.5 | 109.2 | 179
1921 | 1802 | 123.5 | 121 | 119.7 | 113.7 | 133 | 85.4 | 109.1 | 178.7
1922 | 1803 | 123.3 | 120.8 | 119.5 | 113.7 | 133.2 | 85.4 | 108.9 | 178.4
1923 | 1804 | 123.1 | 120.7 | 119.5 | 113.6 | 133.3 | 85.2 | 108.8 | 178.1
1924 | 1805 | 123 | 120.4 | 119.3 | 113.6 | 133 | 85.3 | 108.7 | 177.9
1925 | 1806 | 122.8 | 120.1 | 119.1 | 113.5 | 132.9 | 85.2 | 108.5 | 177.7
1926 | 1807 | 122.7 | 119.9 | 118.6 | 113.3 | 132.9 | 85.1 | 108.4 | 177.4
1927 | 1808 | 122.5 | 119.5 | 118.4 | 112.9 | 132.9 | 85.1 | 108.3 | 177.2
1928 | 1809 | 122.4 | 119.2 | 118.3 | 112.4 | 132.8 | 85.1 | 108.1 | 177.1
1929 | 1810 | 122.2 | 118.9 | 118 | 111.9 | 132.6 | 85.2 | 108 | 176.9
1930 | 1811 | 122.1 | 118.7 | 117.6 | 111.5 | 131.9 | 84.9 | 107.8 | 176.6
1931 | 1812 | 122 | 118.6 | 117.4 | 111.1 | 131 | 84.5 | 107.7 | 176.3
1932 | 1813 | 121.9 | 118.3 | 117.1 | 110.6 | 130.3 | 84.5 | 107.6 | 176.1
1933 | 1814 | 121.7 | 118.2 | 116.5 | 110.3 | 129.8 | 84.5 | 107.5 | 175.9
1934 | 1815 | 121.6 | 117.9 | 116.3 | 110.2 | 129.4 | 84.4 | 107.4 | 175.6
1935 | 1816 | 121.5 | 117.5 | 116.3 | 109.9 | 128.8 | 84.4 | 107.3 | 175.3
1936 | 1817 | 121.4 | 117.3 | 116.2 | 109.8 | 128.1 | 84.2 | 107.1 | 175.1
1937 | 1818 | 121.2 | 117.1 | 116 | 109.7 | 127.7 | 84 | 107 | 174.9
1938 | 1819 | 121 | 116.9 | 116 | 109.7 | 127.6 | 84.1 | 106.9 | 174.6
1939 | 1820 | 120.9 | 116.7 | 116.1 | 109.6 | 127.3 | 83.8 | 106.7 | 174.4

## Test Facts
Last row in IRMS data sheets: | 16
Time when Penlight power was initiated: | 119