## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 1
Test conditions: Cable: 3-conductor plus drain wires, 8AWG, XLPE insulated, Hypalon jacketed, CAROLFIRE Cable Item #14. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 475C, nominal 17.7 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), cable tray was grounded. Thermal response monitoring: Shroud temperature and five cable temperatures (see maps). Shroud power: Initiated after 184 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
184 |  | Shroud power initiated
955 |  | Conductor 1 shorts to Drain wire at less than 1000 ohms (405) | First short circuit inditations are between conductor one and the un-insulated drain wire
966 (next cycle) |  | C1-Drain short drops below 100 ohms. This short persists through test although resistance level varies between about 5 and 1000 ohms | All conductors initially show interactions with un-insulated drain wire. The faults quickly progress to low IR values (less than 100 ohms), and all conductors and the drain ultimatly form a common intra-cable shorting group.
1012, 1014 |  | Both Conductors 2 and 3 short to the drain wire at less than 1000 ohms
1021-1028 |  | All conductors and drain form a mutual intra-cable shorting group with all resistances below 1000 ohms, some less than 100 ohms.
1033, 1040 |  | Drain wire and Conductor 1 show shorts to external ground at less than 1000 ohms | First indications of significant interactions with external ground are approximately 78 seconds after first indications of C1-Drain wire faulting.
1054, 1063 |  | Conductors 2 and 3 also show shorts to external ground at less than 1000 ohms
1128-1136 |  | All concuctors and drain wire show shorts to external ground at less than 100 ohms. Shorts persist for duration of test, although resistance values vary. | All conductors have shorted to external ground.
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).
Observation 2 | This test followed an expected behavior that has been observed in previous testing (NUREG/CR-5546). The drain wire is within the cable jacket, but is not insulated. This makes it more likely that intra-cable shorting will occur between a conductor and t

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, center position
| TC3 | = | Cable 3 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC4 | = | Cable 4 | On outer cable surface, outboard from cable center
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 1 |  |  | 2006-06-29 | 13:39
XLPE | 3-C | Tray
475 C | 17.7 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | IR C1-C4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums
-183.5 | 244337.9994 | -181.5 | 244937.9994 | -179.5 | 244437.9994 | -177.5 | 243637.9994 | -176 | 245037.9994 | -174.5 | 245537.9994 | -183.5 | 243637.9994
-172.5 | 244337.9994 | -170.5 | 244937.9994 | -168.5 | 244437.9994 | -167 | 243637.9994 | -165.5 | 245037.9994 | -163.5 | 245537.9994 | -172.5 | 243637.9994
-161.5 | 244337.9994 | -159.5 | 244937.9994 | -158.5 | 244437.9994 | -156.5 | 243637.9994 | -154.5 | 245037.9994 | -152.5 | 245537.9994 | -161.5 | 243637.9994
-150.5 | 244337.9994 | -149.5 | 244937.9994 | -147.5 | 244437.9994 | -145.5 | 243637.9994 | -143.5 | 245037.9994 | -141.5 | 245537.9994 | -150.5 | 243637.9994
-140.5 | 244337.9994 | -138.5 | 244937.9994 | -136.5 | 244437.9994 | -134.5 | 243637.9994 | -132.5 | 122468.9988 | -131.5 | 245537.9994 | -140.5 | 122468.9988
-129.5 | 244337.9994 | -127.5 | 244937.9994 | -125.5 | 244437.9994 | -123.5 | 243637.9994 | -122.5 | 245037.9994 | -120.5 | 245537.9994 | -129.5 | 243637.9994
-118.5 | 244337.9994 | -116.5 | 122418.9988 | -114.5 | 244437.9994 | -113.5 | 243637.9994 | -111.5 | 245037.9994 | -109.5 | 245537.9994 | -118.5 | 122418.9988
-107.5 | 244337.9994 | -105.5 | 244937.9994 | -104.5 | 244437.9994 | -102.5 | 243637.9994 | -100.5 | 245037.9994 | -98.5 | 245537.9994 | -107.5 | 243637.9994
-96.5 | 244337.9994 | -95.5 | 244937.9994 | -93.5 | 244437.9994 | -91.5 | 243637.9994 | -89.5 | 245037.9994 | -87.5 | 245537.9994 | -96.5 | 243637.9994
-86.5 | 244337.9994 | -84.5 | 244937.9994 | -82.5 | 244437.9994 | -80.5 | 243637.9994 | -78.5 | 245037.9994 | -77.5 | 245537.9994 | -86.5 | 243637.9994
-75.5 | 244337.9994 | -73.5 | 244937.9994 | -71.5 | 244437.9994 | -69.5 | 243637.9994 | -68.5 | 245037.9994 | -66.5 | 245537.9994 | -75.5 | 243637.9994
-64.5 | 244337.9994 | -62.5 | 244937.9994 | -60.5 | 244437.9994 | -59 | 243637.9994 | -57.5 | 245037.9994 | -55.5 | 245537.9994 | -64.5 | 243637.9994
-53.5 | 244337.9994 | -51.5 | 244937.9994 | -50.5 | 244437.9994 | -48.5 | 243637.9994 | -46.5 | 245037.9994 | -44.5 | 122718.9988 | -53.5 | 122718.9988
-42.5 | 122118.9988 | -41 | 122418.9988 | -39.5 | 122168.9988 | -37.5 | 243637.9994 | -35.5 | 245037.9994 | -33.5 | 245537.9994 | -42.5 | 122118.9988
-32 | 122118.9988 | -30.5 | 244937.9994 | -28.5 | 244437.9994 | -26.5 | 243637.9994 | -24.5 | 245037.9994 | -23 | 245537.9994 | -32 | 122118.9988
-21.5 | 244337.9994 | -19.5 | 244937.9994 | -17.5 | 244437.9994 | -15.5 | 243637.9994 | -14.5 | 245037.9994 | -12.5 | 245537.9994 | -21.5 | 243637.9994
-10.5 | 244337.9994 | -8.5 | 244937.9994 | -6 | 244437.9994 | -5.5 | 121768.9988 | -3.5 | 245037.9994 | -1.5 | 122718.9988 | -10.5 | 121768.9988
0.5 | 244138.0818 | 2.5 | 244937.9994 | 4 | 244437.9994 | 5.5 | 243637.9994 | 7.5 | 244838.0816 | 9.5 | 245537.9994 | 0.5 | 243637.9994
11.5 | 244337.9994 | 13 | 244937.9994 | 14.5 | 122168.9988 | 16.5 | 121768.9988 | 18.5 | 122468.9988 | 20.5 | 245537.9994 | 11.5 | 121768.9988
22 | 244337.9994 | 23.5 | 244937.9994 | 25.5 | 244437.9994 | 27.5 | 243637.9994 | 29.5 | 245037.9994 | 31 | 245537.9994 | 22 | 243637.9994
32.5 | 244337.9994 | 34.5 | 244937.9994 | 36.5 | 244437.9994 | 38.5 | 243637.9994 | 39.5 | 245037.9994 | 41.5 | 245537.9994 | 32.5 | 243637.9994
43.5 | 244337.9994 | 45.5 | 122418.9988 | 47.5 | 122168.9988 | 49 | 243637.9994 | 50.5 | 245037.9994 | 52.5 | 245537.9994 | 43.5 | 122168.9988
54.5 | 244337.9994 | 56.5 | 244937.9994 | 57.5 | 244437.9994 | 59.5 | 243637.9994 | 61.5 | 245037.9994 | 63.5 | 245537.9994 | 54.5 | 243637.9994
65.5 | 244337.9994 | 66.5 | 244937.9994 | 68.5 | 244437.9994 | 70.5 | 243637.9994 | 72.5 | 245037.9994 | 74.5 | 245537.9994 | 65.5 | 243637.9994
75.5 | 244337.9994 | 77.5 | 244937.9994 | 79.5 | 244437.9994 | 81.5 | 243637.9994 | 83.5 | 245037.9994 | 85 | 245537.9994 | 75.5 | 243637.9994
86.5 | 244337.9994 | 88.5 | 244937.9994 | 90.5 | 244437.9994 | 92.5 | 243637.9994 | 94 | 245037.9994 | 95.5 | 245537.9994 | 86.5 | 243637.9994
97.5 | 244337.9994 | 99.5 | 244937.9994 | 101.5 | 244437.9994 | 103 | 243637.9994 | 104.5 | 245037.9994 | 106.5 | 245537.9994 | 97.5 | 243637.9994
108.5 | 244337.9994 | 110.5 | 244937.9994 | 112 | 244437.9994 | 113.5 | 243637.9994 | 115.5 | 245037.9994 | 117.5 | 245537.9994 | 108.5 | 243637.9994
119.5 | 244337.9994 | 120.5 | 122418.9988 | 122.5 | 244437.9994 | 124.5 | 243637.9994 | 126.5 | 245037.9994 | 128.5 | 245338.0814 | 119.5 | 122418.9988
129.5 | 244337.9994 | 131.5 | 244937.9994 | 133.5 | 244437.9994 | 135.5 | 243637.9994 | 137.5 | 244838.0816 | 138.5 | 245537.9994 | 129.5 | 243637.9994
140.5 | 244138.0818 | 142.5 | 244937.9994 | 144.5 | 244437.9994 | 146.5 | 243637.9994 | 147.5 | 245037.9994 | 149.5 | 245537.9994 | 140.5 | 243637.9994
151.5 | 244138.0818 | 153.5 | 244937.9994 | 155.5 | 122168.9988 | 156.5 | 243637.9994 | 158.5 | 245037.9994 | 160.5 | 245537.9994 | 151.5 | 122168.9988
162.5 | 244337.9994 | 164.5 | 244937.9994 | 165.5 | 244437.9994 | 167.5 | 121768.9988 | 169.5 | 122468.9988 | 171.5 | 245537.9994 | 162.5 | 121768.9988
174 | 244337.9994 | 174.5 | 244937.9994 | 176.5 | 244437.9994 | 178.5 | 243637.9994 | 180.5 | 245037.9994 | 182.5 | 245537.9994 | 174 | 243637.9994
183.5 | 244038.1636 | 185.5 | 244937.9994 | 187.5 | 244238.0818 | 189.5 | 243438.0821 | 191.5 | 245037.9994 | 192.5 | 245338.0814 | 183.5 | 243438.0821
194.5 | 244337.9994 | 196.5 | 244937.9994 | 198.5 | 244437.9994 | 200.5 | 243637.9994 | 201.5 | 245037.9994 | 203.5 | 245537.9994 | 194.5 | 243637.9994
205.5 | 244337.9994 | 207.5 | 244937.9994 | 209.5 | 244437.9994 | 211 | 243637.9994 | 212.5 | 122468.9988 | 214.5 | 245537.9994 | 205.5 | 122468.9988
216.5 | 244337.9994 | 218.5 | 244937.9994 | 220 | 244437.9994 | 221.5 | 243637.9994 | 223.5 | 244838.0816 | 225.5 | 245338.0814 | 216.5 | 243637.9994
227.5 | 244337.9994 | 228.5 | 244937.9994 | 230.5 | 244238.0818 | 232.5 | 243637.9994 | 234.5 | 245037.9994 | 236.5 | 245537.9994 | 227.5 | 243637.9994
237.5 | 244337.9994 | 239.5 | 244937.9994 | 241.5 | 244238.0818 | 243.5 | 121768.9988 | 245.5 | 245037.9994 | 246.5 | 245537.9994 | 237.5 | 121768.9988
248.5 | 244337.9994 | 250.5 | 244937.9994 | 252.5 | 244437.9994 | 254.5 | 243637.9994 | 255.5 | 245037.9994 | 257.5 | 245537.9994 | 248.5 | 243637.9994
259.5 | 244337.9994 | 261.5 | 244937.9994 | 263.5 | 244437.9994 | 264.5 | 121768.9988 | 266.5 | 245037.9994 | 268.5 | 245537.9994 | 259.5 | 121768.9988
270.5 | 122118.9988 | 272.5 | 244937.9994 | 274 | 244437.9994 | 275.5 | 243637.9994 | 277.5 | 245037.9994 | 279.5 | 245537.9994 | 270.5 | 122118.9988
281.5 | 244337.9994 | 282.5 | 122418.9988 | 284.5 | 244437.9994 | 286.5 | 243637.9994 | 288.5 | 245037.9994 | 290 | 245537.9994 | 281.5 | 122418.9988
291.5 | 244337.9994 | 293.5 | 244937.9994 | 295.5 | 244437.9994 | 297.5 | 243637.9994 | 299.5 | 245037.9994 | 300.5 | 245537.9994 | 291.5 | 243637.9994
302.5 | 244337.9994 | 304.5 | 244937.9994 | 306.5 | 244437.9994 | 308.5 | 243637.9994 | 309.5 | 245037.9994 | 311.5 | 245537.9994 | 302.5 | 243637.9994
313.5 | 244337.9994 | 315.5 | 244937.9994 | 317.5 | 244437.9994 | 319 | 243637.9994 | 320.5 | 245037.9994 | 322.5 | 122718.9988 | 313.5 | 122718.9988
324.5 | 122118.9988 | 326.5 | 244937.9994 | 327.5 | 244437.9994 | 329.5 | 243637.9994 | 331.5 | 245037.9994 | 333.5 | 245537.9994 | 324.5 | 122118.9988
335.5 | 244337.9994 | 336.5 | 122418.9988 | 338.5 | 244238.0818 | 340.5 | 243637.9994 | 342.5 | 245037.9994 | 344.5 | 245537.9994 | 335.5 | 122418.9988
345.5 | 244337.9994 | 347.5 | 244937.9994 | 349.5 | 244437.9994 | 351.5 | 243637.9994 | 354 | 245037.9994 | 354.5 | 245537.9994 | 345.5 | 243637.9994
356.5 | 244337.9994 | 358.5 | 244937.9994 | 360.5 | 244437.9994 | 362.5 | 121768.9988 | 363.5 | 245037.9994 | 365.5 | 245338.0814 | 356.5 | 121768.9988
367.5 | 244337.9994 | 369.5 | 244937.9994 | 371.5 | 244437.9994 | 372.5 | 243637.9994 | 374.5 | 245037.9994 | 376.5 | 122718.9988 | 367.5 | 122718.9988
378.5 | 244337.9994 | 380.5 | 244738.0816 | 381.5 | 244437.9994 | 383.5 | 243637.9994 | 385.5 | 245037.9994 | 387.5 | 122718.9988 | 378.5 | 122718.9988
389.5 | 244337.9994 | 390.5 | 244937.9994 | 392.5 | 244437.9994 | 394.5 | 243637.9994 | 396.5 | 245037.9994 | 398.5 | 245537.9994 | 389.5 | 243637.9994
399.5 | 244337.9994 | 401.5 | 244937.9994 | 403.5 | 244437.9994 | 405.5 | 243637.9994 | 407.5 | 245037.9994 | 408.5 | 245537.9994 | 399.5 | 243637.9994
410.5 | 244337.9994 | 412.5 | 244937.9994 | 414.5 | 244437.9994 | 416.5 | 243637.9994 | 417.5 | 245037.9994 | 419.5 | 245537.9994 | 410.5 | 243637.9994
421.5 | 244337.9994 | 423.5 | 244937.9994 | 425.5 | 244437.9994 | 426.5 | 243637.9994 | 428.5 | 245037.9994 | 430.5 | 245537.9994 | 421.5 | 243637.9994
432.5 | 244337.9994 | 434.5 | 244937.9994 | 435.5 | 244437.9994 | 437.5 | 243637.9994 | 439.5 | 244838.0816 | 441.5 | 245537.9994 | 432.5 | 243637.9994
443.5 | 244337.9994 | 444.5 | 244937.9994 | 446.5 | 244437.9994 | 448.5 | 243637.9994 | 450.5 | 245037.9994 | 452.5 | 245537.9994 | 443.5 | 243637.9994
453.5 | 244337.9994 | 455.5 | 244937.9994 | 457.5 | 244437.9994 | 459.5 | 243637.9994 | 461.5 | 245037.9994 | 462.5 | 245537.9994 | 453.5 | 243637.9994
464.5 | 244337.9994 | 466.5 | 244937.9994 | 468.5 | 244437.9994 | 470.5 | 243637.9994 | 471.5 | 245037.9994 | 473.5 | 245537.9994 | 464.5 | 243637.9994
475.5 | 244337.9994 | 477.5 | 244937.9994 | 479 | 244437.9994 | 480.5 | 243637.9994 | 482.5 | 245037.9994 | 484.5 | 245537.9994 | 475.5 | 243637.9994
486.5 | 244337.9994 | 488 | 122418.9988 | 489.5 | 244437.9994 | 491.5 | 243637.9994 | 493.5 | 245037.9994 | 495.5 | 245537.9994 | 486.5 | 122418.9988
497.5 | 244337.9994 | 498.5 | 244937.9994 | 500.5 | 244437.9994 | 502.5 | 243637.9994 | 504.5 | 245037.9994 | 506 | 245537.9994 | 497.5 | 243637.9994
507.5 | 244337.9994 | 509.5 | 244937.9994 | 511.5 | 244437.9994 | 513.5 | 243637.9994 | 515 | 245037.9994 | 516.5 | 245537.9994 | 507.5 | 243637.9994
518.5 | 244337.9994 | 520.5 | 244937.9994 | 522.5 | 244437.9994 | 524 | 243637.9994 | 525.5 | 245037.9994 | 527.5 | 245537.9994 | 518.5 | 243637.9994
529.5 | 244337.9994 | 531.5 | 244937.9994 | 533 | 244437.9994 | 534.5 | 243637.9994 | 536.5 | 245037.9994 | 538.5 | 245537.9994 | 529.5 | 243637.9994
540.5 | 244337.9994 | 542.5 | 244937.9994 | 543.5 | 244437.9994 | 545.5 | 243637.9994 | 547.5 | 245037.9994 | 549.5 | 245537.9994 | 540.5 | 243637.9994
551.5 | 244337.9994 | 552.5 | 244937.9994 | 554.5 | 244437.9994 | 556.5 | 243637.9994 | 558.5 | 245037.9994 | 560.5 | 245537.9994 | 551.5 | 243637.9994
561.5 | 244337.9994 | 563.5 | 244937.9994 | 565.5 | 244437.9994 | 567.5 | 243637.9994 | 569.5 | 245037.9994 | 570.5 | 245537.9994 | 561.5 | 243637.9994
572.5 | 244337.9994 | 574.5 | 244937.9994 | 576.5 | 244437.9994 | 578 | 243637.9994 | 579.5 | 245037.9994 | 581.5 | 245537.9994 | 572.5 | 243637.9994
583.5 | 244337.9994 | 585.5 | 244937.9994 | 587.5 | 244437.9994 | 588.5 | 243637.9994 | 590.5 | 245037.9994 | 592.5 | 245537.9994 | 583.5 | 243637.9994
594.5 | 244337.9994 | 596.5 | 244937.9994 | 597.5 | 244437.9994 | 599.5 | 243637.9994 | 601.5 | 245037.9994 | 603.5 | 245338.0814 | 594.5 | 243637.9994
605.5 | 244337.9994 | 606.5 | 244937.9994 | 608.5 | 244437.9994 | 610.5 | 243637.9994 | 612.5 | 245037.9994 | 614 | 245537.9994 | 605.5 | 243637.9994
615.5 | 244337.9994 | 617.5 | 244937.9994 | 619.5 | 244437.9994 | 621.5 | 243637.9994 | 623.5 | 245037.9994 | 624.5 | 245537.9994 | 615.5 | 243637.9994
626.5 | 244337.9994 | 628.5 | 244937.9994 | 630.5 | 244437.9994 | 632.5 | 243637.9994 | 633.5 | 245037.9994 | 635.5 | 245537.9994 | 626.5 | 243637.9994
637.5 | 244337.9994 | 639.5 | 244937.9994 | 641.5 | 244437.9994 | 642.5 | 243637.9994 | 644.5 | 245037.9994 | 646.5 | 245537.9994 | 637.5 | 243637.9994
648.5 | 244337.9994 | 650.5 | 244937.9994 | 651.5 | 244437.9994 | 653.5 | 243637.9994 | 655.5 | 245037.9994 | 657.5 | 245537.9994 | 648.5 | 243637.9994
659 | 244337.9994 | 660.5 | 244937.9994 | 662.5 | 244437.9994 | 664.5 | 243637.9994 | 666.5 | 245037.9994 | 668 | 245537.9994 | 659 | 243637.9994
669.5 | 244337.9994 | 671.5 | 244937.9994 | 673.5 | 244437.9994 | 675.5 | 243637.9994 | 677 | 245037.9994 | 678.5 | 245537.9994 | 669.5 | 243637.9994
680.5 | 244337.9994 | 682.5 | 244937.9994 | 684.5 | 244437.9994 | 686 | 243637.9994 | 687.5 | 245037.9994 | 689.5 | 245537.9994 | 680.5 | 243637.9994
691.5 | 244337.9994 | 693.5 | 122418.9988 | 695 | 244437.9994 | 696.5 | 243637.9994 | 698.5 | 245037.9994 | 700.5 | 245537.9994 | 691.5 | 122418.9988
702.5 | 244337.9994 | 704 | 244937.9994 | 705.5 | 244437.9994 | 707.5 | 243637.9994 | 709.5 | 245037.9994 | 711.5 | 245537.9994 | 702.5 | 243637.9994
713 | 244337.9994 | 714.5 | 244937.9994 | 716.5 | 244437.9994 | 718.5 | 243637.9994 | 720.5 | 245037.9994 | 722 | 245537.9994 | 713 | 243637.9994
723.5 | 244337.9994 | 725.5 | 244937.9994 | 727.5 | 244437.9994 | 729.5 | 243637.9994 | 731 | 245037.9994 | 732.5 | 245537.9994 | 723.5 | 243637.9994
734.5 | 244337.9994 | 736.5 | 244937.9994 | 738.5 | 244437.9994 | 740 | 243637.9994 | 741.5 | 245037.9994 | 743.5 | 245537.9994 | 734.5 | 243637.9994
745.5 | 244337.9994 | 747.5 | 244937.9994 | 749 | 244437.9994 | 750.5 | 243637.9994 | 752.5 | 245037.9994 | 754.5 | 245537.9994 | 745.5 | 243637.9994
756.5 | 244337.9994 | 758 | 244937.9994 | 759.5 | 40120.3856 | 761.5 | 243637.9994 | 763.5 | 245037.9994 | 765.5 | 245537.9994 | 756.5 | 40120.3856
767 | 244337.9994 | 768.5 | 244937.9994 | 770.5 | 404.5763 | 772.5 | 243438.0821 | 774.5 | 245037.9994 | 776 | 245537.9994 | 767 | 404.5763
777.5 | 244337.9994 | 779.5 | 244937.9994 | 781.5 | 98.1996 | 783.5 | 10916.6168 | 785 | 48887.7385 | 786.5 | 122619.061 | 777.5 | 98.1996
788.5 | 244137.9591 | 790.5 | 244337.796 | 792.5 | 78.0173 | 794.5 | 10425.0222 | 795.5 | 22085.7054 | 797.5 | 7925.5108 | 788.5 | 78.0173
799.5 | 242040.6577 | 801.5 | 17933.7691 | 803 | 91.6128 | 804.5 | 9225.6675 | 806.5 | 4209.5021 | 808.5 | 3934.4368 | 799.5 | 91.6128
810.5 | 4934.0616 | 812 | 5705.0921 | 813.5 | 102.2204 | 815.5 | 14485.9699 | 817.5 | 1828.8242 | 819.5 | 1692.5523 | 810.5 | 102.2204
821 | 1944.0436 | 822.5 | 3120.8631 | 824.5 | 314.7105 | 826.5 | 1476.2514 | 828.5 | 835.5124 | 830 | 221.7198 | 821 | 221.7198
831.5 | 1426.5296 | 833.5 | 1211.0533 | 835.5 | 41.9592 | 837.5 | 453.8897 | 839 | 423.6623 | 840.5 | 22.6545 | 831.5 | 22.6545
842.5 | 543.7653 | 844.5 | 99.191 | 846.5 | 73.822 | 848 | 350.5676 | 849.5 | 282.7088 | 851.5 | 51.5205 | 842.5 | 51.5205
853.5 | 402.9124 | 855.5 | 64.1005 | 857.5 | 71.6668 | 858.5 | 383.2067 | 860.5 | 356.8656 | 862.5 | 38.3145 | 853.5 | 38.3145
864.5 | 318.5371 | 866 | 59.7071 | 867.5 | 82.0961 | 869.5 | 205.9383 | 871.5 | 313.9486 | 873.5 | 26.0379 | 864.5 | 26.0379
875 | 353.8317 | 876.5 | 31.7837 | 878.5 | 58.5077 | 880.5 | 231.4506 | 882.5 | 32.4365 | 884 | 69.846 | 875 | 31.7837
885.5 | 25.3159 | 887.5 | 45.4774 | 889.5 | 32.1006 | 891.5 | 4.0055 | 893 | 33.9684 | 894.5 | 24.5424 | 885.5 | 4.0055
896.5 | 12.7461 | 898.5 | 40.2252 | 900.5 | 4.8115 | 902 | 20.3541 | 903.5 | 65.5751 | 905.5 | 22.2391 | 896.5 | 4.8115
907.5 | 13.3456 | 909.5 | 11.3665 | 910.5 | 25.7935 | 912.5 | 61.8575 | 914.5 | 42.9152 | 916.5 | 40.3307 | 907.5 | 11.3665
918.5 | 48.7069 | 920 | 19.3429 | 921.5 | 45.7924 | 923.5 | 109.1269 | 925.5 | 49.3122 | 927.5 | 89.7694 | 918.5 | 19.3429
929 | 28.975 | 930.5 | 32.4957 | 932.5 | 56.0599 | 934.5 | 16.5854 | 936.5 | 48.8799 | 938 | 42.1719 | 929 | 16.5854
939.5 | 50.153 | 941.5 | 15.0817 | 943.5 | 11.8225 | 945.5 | 30.7882 | 947 | 37.5668 | 948.5 | 93.3933 | 939.5 | 11.8225
950.5 | 106.2829 | 952.5 | 1.9226 | 954.5 | 85.3298 | 956 | 5.1898 | 957.5 | 55.3046 | 959.5 | 2.1862 | 950.5 | 1.9226
961.5 | 71.8857 | 963.5 | 15.3015 | 964.5 | 37.7469 | 966.5 | 14.0704 | 968.5 | 50.8611 | 970.5 | 45.4769 | 961.5 | 14.0704
972.5 | 44.9224 | 974.5 | 12.4983 | 975.5 | 50.9751 | 977.5 | 17.4809 | 979.5 | 23.3999 | 981.5 | 54.0767 | 972.5 | 12.4983
983.5 | 23.5442 | 984.5 | 15.2328 | 986.5 | 32.6963 | 988.5 | 20.3047 | 990.5 | 73.4364 | 992 | 49.446 | 983.5 | 15.2328
993.5 | 37.1659 | 995.5 | 21.0469 | 997.5 | 61.7309 | 999.5 | 32.5932 | 1001.5 | 61.7753 | 1002.5 | 56.1016 | 993.5 | 21.0469
1004.5 | 26.049 | 1006.5 | 6.3895 | 1008.5 | 54.7174 | 1010.5 | 27.5741 | 1011.5 | 40.3553 | 1013.5 | 81.8463 | 1004.5 | 6.3895
1015.5 | 22.6936 | 1017.5 | 2.4435 | 1019 | 506.88 | 1020.5 | 497.4809 | 1022.5 | 139.2357 | 1024.5 | 44.938 | 1015.5 | 2.4435
1026.5 | 288.1193 | 1028 | 226.3187 | 1029.5 | 129.1144 | 1031.5 | 1.3448 | 1033.5 | 158.9522 | 1035.5 | 496.8675 | 1026.5 | 1.3448
1037 | 15.3772 | 1038.5 | 149.9424 | 1040.5 | 928.1803 | 1042.5 | 38.9394 | 1044.5 | 455.0611 | 1046 | 101.4139 | 1037 | 15.3772
1047.5 | 423.3916 | 1049.5 | 670.2063 | 1051.5 | 507.0052 | 1053.5 | 199.0032 | 1055 | 28.5226 | 1056.5 | 72.714 | 1047.5 | 28.5226
1058.5 | 267.8314 | 1060.5 | 261.4042 | 1062.5 | 59.5416 | 1064.5 | 639.4361 | 1065.5 | 227.159 | 1067.5 | 33.3955 | 1058.5 | 33.3955
1069.5 | 17.8131 | 1071.5 | 149.1627 | 1073 | 1201.7697 | 1074.5 | 9.1148 | 1076.5 | 183.4337 | 1078.5 | 682.9916 | 1069.5 | 9.1148
1080.5 | 727.0403 | 1082 | 46.433 | 1083.5 | 130.0444 | 1085.5 | 281.3726 | 1087.5 | 286.7889 | 1089.5 | 145.1907 | 1080.5 | 46.433
1091 | 554.7837 | 1092.5 | 1477.4029 | 1094.5 | 2575.6958 | 1096.5 | 15.7113 | 1098.5 | 78.664 | 1100 | 113.462 | 1091 | 15.7113
1101.5 | 520.383 | 1103.5 | 195.8226 | 1105.5 | 110.8377 | 1107.5 | 81.0632 | 1109 | 1158.65 | 1110.5 | 331.12 | 1101.5 | 81.0632
1112.5 | 435.4989 | 1114.5 | 45.7643 | 1116.5 | 973.6227 | 1118 | 2584.5768 | 1119.5 | 460.8326 | 1121.5 | 41.5168 | 1112.5 | 41.5168
1123.5 | 127.9637 | 1125.5 | 2432.2591 | 1127 | 431.4146 | 1128.5 | 90.8445 | 1130.5 | 57.729 | 1132.5 | 311.8597 | 1123.5 | 57.729
1134.5 | 1799.1643 | 1136 | 101.4419 | 1137.5 | 1905.4837 | 1139.5 | 1026.6081 | 1141.5 | 39.7128 | 1143.5 | 175.7461 | 1134.5 | 39.7128
1145 | 357.7917 | 1146.5 | 1524.4378 | 1148.5 | 988.582 | 1150.5 | 994.7943 | 1152.5 | 97.2696 | 1154 | 956.7824 | 1145 | 97.2696
1155.5 | 928.3067 | 1157.5 | 545.226 | 1159.5 | 821.8452 | 1161.5 | 777.9942 | 1163 | 790.4639 | 1164.5 | 82.4206 | 1155.5 | 82.4206
1166.5 | 987.5296 | 1168.5 | 945.8089 | 1170.5 | 127.1901 | 1172 | 385.617 | 1173.5 | 2157.3778 | 1175.5 | 887.3202 | 1166.5 | 127.1901
1177.5 | 273.7172 | 1179.5 | 138.3621 | 1181 | 17.8356 | 1182.5 | 1008.9258 | 1184.5 | 1082.9363 | 1186.5 | 295.6202 | 1177.5 | 17.8356
1188.5 | 1356.3949 | 1189.5 | 521.7746 | 1191.5 | 227.8662 | 1193.5 | 1241.5511 | 1195.5 | 710.5518 | 1197.5 | 110.1194 | 1188.5 | 110.1194
1199 | 36.9844 | 1200.5 | 1916.2106 | 1202.5 | 521.9335 | 1204.5 | 1043.3532 | 1206.5 | 871.2395 | 1208 | 352.5846 | 1199 | 36.9844
1209.5 | 125.0953 | 1211.5 | 621.6499 | 1213.5 | 395.8939 | 1215.5 | 72.8629 | 1217 | 377.1988 | 1218.5 | 529.3831 | 1209.5 | 72.8629
1220.5 | 261.8071 | 1222.5 | 1859.969 | 1224.5 | 39.8837 | 1226 | 52.0156 | 1227.5 | 592.2801 | 1229.5 | 106.3863 | 1220.5 | 39.8837
1231.5 | 235.2429 | 1233.5 | 266.8531 | 1235 | 310.0989 | 1236.5 | 608.573 | 1238.5 | 1190.4903 | 1240.5 | 31.411 | 1231.5 | 31.411
1242.5 | 108.7042 | 1244 | 99.0376 | 1245.5 | 659.0024 | 1247.5 | 65.7815 | 1249.5 | 40.6441 | 1251.5 | 151.238 | 1242.5 | 40.6441
1253 | 126.5816 | 1254.5 | 538.9043 | 1256.5 | 647.5456 | 1258.5 | 277.2986 | 1260.5 | 533.2363 | 1262 | 29.5832 | 1253 | 29.5832
1263.5 | 740.5919 | 1265.5 | 1302.4911 | 1267.5 | 194.1562 | 1269.5 | 68.893 | 1271 | 541.9143 | 1272.5 | 168.5114 | 1263.5 | 68.893
1274.5 | 819.9214 | 1276.5 | 300.3371 | 1278.5 | 230.5066 | 1280 | 867.8372 | 1281.5 | 76.0231 | 1283.5 | 440.0411 | 1274.5 | 76.0231
1285.5 | 85.4709 | 1287.5 | 934.982 | 1289 | 113.1062 | 1290.5 | 186.6222 | 1292.5 | 55.2753 | 1294.5 | 25.5886 | 1285.5 | 25.5886
1296.5 | 69.0272 | 1298 | 756.4794 | 1299.5 | 79.8142 | 1301.5 | 125.3634 | 1303.5 | 242.2871 | 1305.5 | 724.5544 | 1296.5 | 69.0272
1307 | 368.2049 | 1308.5 | 185.4709 | 1310.5 | 451.3619 | 1312.5 | 56.7008 | 1314.5 | 290.4862 | 1316 | 225.8046 | 1307 | 56.7008
1317.5 | 18.5267 | 1319.5 | 302.5632 | 1321.5 | 127.1299 | 1323.5 | 701.4452 | 1325 | 429.4852 | 1326.5 | 1020.9128 | 1317.5 | 18.5267
1328.5 | 157.6847 | 1330.5 | 717.7052 | 1332.5 | 423.7548 | 1333.5 | 537.5108 | 1335.5 | 379.2769 | 1337.5 | 65.4546 | 1328.5 | 65.4546
1339.5 | 39.8627 | 1341.5 | 112.4779 | 1342.5 | 95.3334 | 1344.5 | 477.3567 | 1346.5 | 131.549 | 1348.5 | 289.9765 | 1339.5 | 39.8627
1350.5 | 19.9792 | 1351.5 | 964.3073 | 1353.5 | 172.4714 | 1355.5 | 139.4994 | 1357.5 | 33.5613 | 1359.5 | 36.2042 | 1350.5 | 19.9792
1360.5 | 236.3492 | 1362.5 | 452.7963 | 1364.5 | 51.0634 | 1366.5 | 388.8227 | 1368.5 | 18.6105 | 1369.5 | 263.9325 | 1360.5 | 18.6105
1371.5 | 82.2791 | 1373.5 | 515.9141 | 1375.5 | 98.0918 | 1377.5 | 550.7163 | 1379 | 151.1271 | 1380.5 | 333.4916 | 1371.5 | 82.2791
1382.5 | 401.597 | 1384.5 | 61.8622 | 1386.5 | 256.5112 | 1388 | 81.6161 | 1389.5 | 62.679 | 1391.5 | 454.0078 | 1382.5 | 61.8622
1393.5 | 476.0806 | 1395.5 | 240.6811 | 1396.5 | 76.1802 | 1398.5 | 296.2557 | 1400.5 | 91.1829 | 1402.5 | 94.3558 | 1393.5 | 76.1802
1404.5 | 114.9203 | 1405.5 | 126.6327 | 1407.5 | 130.8516 | 1409.5 | 81.8323 | 1411.5 | 102.1347 | 1413.5 | 221.0675 | 1404.5 | 81.8323
1414.5 | 3.1692 | 1416.5 | 43.144 | 1418.5 | 27.9463 | 1420.5 | 2.2429 | 1422.5 | 21.0774 | 1423.5 | 29.0067 | 1414.5 | 2.2429
1425.5 | 66.0627 | 1427.5 | 68.0088 | 1429.5 | 104.3294 | 1431.5 | 55.1085 | 1432.5 | 16.9844 | 1434.5 | 49.7612 | 1425.5 | 16.9844
1436.5 | 15.8732 | 1438.5 | 213.6199 | 1440.5 | 163.704 | 1441.5 | 16.3197 | 1443.5 | 40.2956 | 1445.5 | 52.3606 | 1436.5 | 15.8732
1447.5 | 116.6676 | 1449.5 | 152.3073 | 1450.5 | 78.2021 | 1452.5 | 47.4137 | 1454.5 | 179.9542 | 1456.5 | 37.1789 | 1447.5 | 37.1789
1458.5 | 59.8428 | 1459.5 | 188.1862 | 1461.5 | 100.6896 | 1463.5 | 79.4279 | 1465.5 | 17.2465 | 1467.5 | 68.7802 | 1458.5 | 17.2465
1468.5 | 152.4256 | 1470.5 | 150.8778 | 1472.5 | 28.726 | 1474.5 | 158.4132 | 1476.5 | 24.9926 | 1477.5 | 19.6272 | 1468.5 | 19.6272

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 1 |  |  | 2006-06-29 | 13:39
XLPE | 3-C | Tray
475 C | 17.7 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums Overall
-181.5 | 244338 |  | -179 | 243638 | -177.8333 | 243638 | -176.6667 | 244438 | -181.5 | 243638
-170.5 | 244338 |  | -168.3333 | 243638 | -167 | 243638 | -165.8333 | 244438 | -170.5 | 243638
-159.8333 | 244338 |  | -157.5 | 243638 | -156.1667 | 243638 | -155.1667 | 244438 | -159.8333 | 243638
-149.1667 | 244338 |  | -146.5 | 243638 | -145.5 | 243638 | -144.1667 | 244438 | -149.1667 | 243638
-138.5 | 244338 |  | -135.8333 | 122469 | -134.8333 | 243638 | -133.5 | 244438 | -138.5 | 122469
-127.5 | 244338 |  | -125.1667 | 122119 | -123.8333 | 243638 | -122.8333 | 244438 | -127.5 | 122119
-116.5 | 122419 |  | -114.5 | 243638 | -113.1667 | 243638 | -111.8333 | 244438 | -116.5 | 122419
-105.8333 | 244338 |  | -103.5 | 243638 | -102.1667 | 243638 | -101.1667 | 244438 | -105.8333 | 243638
-95.1667 | 244338 |  | -92.5 | 243638 | -91.5 | 243638 | -90.1667 | 122469 | -95.1667 | 122469
-84.5 | 244338 |  | -81.8333 | 243638 | -80.8333 | 243638 | -79.5 | 122169 | -84.5 | 122169
-73.5 | 244338 |  | -71.1667 | 243638 | -69.8333 | 243638 | -68.8333 | 244438 | -73.5 | 243638
-62.5 | 244338 |  | -60.3333 | 243638 | -59 | 243638 | -57.8333 | 244438 | -62.5 | 243638
-51.8333 | 244338 |  | -49.5 | 243638 | -48.1667 | 122719 | -47.1667 | 122469 | -51.8333 | 122469
-41 | 122119 |  | -38.5 | 122119 | -37.3333 | 122419 | -36.1667 | 122169 | -41 | 122119
-30.3333 | 122119 |  | -27.6667 | 122119 | -26.6667 | 243638 | -25.3333 | 244438 | -30.3333 | 122119
-19.5 | 244338 |  | -17.1667 | 243638 | -15.8333 | 243638 | -14.8333 | 244438 | -19.5 | 243638
-8.3333 | 244338 |  | -6.5 | 121769 | -5.1667 | 122719 | -3.6667 | 244438 | -8.3333 | 121769
2.3333 | 244438 |  | 4.5 | 243638 | 5.8333 | 243638 | 7 | 244438 | 2.3333 | 243638
13 | 122169 |  | 15.5 | 121769 | 16.6667 | 243638 | 17.8333 | 244438 | 13 | 121769
23.6667 | 244338 |  | 26.3333 | 243638 | 27.3333 | 243638 | 28.6667 | 122469 | 23.6667 | 122469
34.5 | 244338 |  | 36.8333 | 243638 | 38.1667 | 243638 | 39.1667 | 122469 | 34.5 | 122469
45.5 | 122169 |  | 47.6667 | 243638 | 49 | 243638 | 50.1667 | 122469 | 45.5 | 122169
56.1667 | 244338 |  | 58.5 | 243638 | 59.8333 | 243638 | 60.8333 | 244438 | 56.1667 | 243638
66.8333 | 244338 |  | 69.5 | 243638 | 70.5 | 243638 | 71.8333 | 122169 | 66.8333 | 122169
77.5 | 244338 |  | 80.1667 | 243638 | 81.3333 | 243638 | 82.6667 | 244438 | 77.5 | 243638
88.5 | 244338 |  | 91 | 243638 | 92.1667 | 243638 | 93.3333 | 122169 | 88.5 | 122169
99.5 | 244338 |  | 101.6667 | 243638 | 103 | 243638 | 104.1667 | 244438 | 99.5 | 243638
110.3333 | 244338 |  | 112.5 | 243638 | 113.8333 | 243638 | 115 | 122169 | 110.3333 | 122169
120.8333 | 122419 |  | 123.5 | 243638 | 124.5 | 243638 | 125.8333 | 244438 | 120.8333 | 122419
131.5 | 244338 |  | 134.1667 | 243638 | 135.1667 | 243638 | 136.5 | 244438 | 131.5 | 243638
142.5 | 244438 |  | 144.8333 | 243638 | 146.1667 | 122419 | 147.1667 | 244438 | 142.5 | 122419
153.5 | 122169 |  | 155.5 | 243638 | 156.8333 | 243638 | 158.1667 | 244438 | 153.5 | 122169
164.1667 | 244338 |  | 166.5 | 121769 | 167.8333 | 121769 | 168.8333 | 122469 | 164.1667 | 121769
175 | 244338 |  | 177.6667 | 122119 | 178.5 | 243638 | 179.8333 | 244438 | 175 | 122119
185.5 | 244938 |  | 188.1667 | 122119 | 189.1667 | 243638 | 190.5 | 244438 | 185.5 | 122119
196.5 | 244338 |  | 198.8333 | 122119 | 200.1667 | 243638 | 201.1667 | 122719 | 196.5 | 122119
207.5 | 244338 |  | 209.6667 | 122469 | 211 | 243638 | 212.1667 | 122169 | 207.5 | 122169
218.3333 | 244338 |  | 220.5 | 243638 | 221.8333 | 243638 | 223 | 244438 | 218.3333 | 243638
228.8333 | 244338 |  | 231.5 | 243638 | 232.5 | 243638 | 233.8333 | 244438 | 228.8333 | 243638
239.5 | 244338 |  | 242.1667 | 121769 | 243.1667 | 121769 | 244.5 | 122469 | 239.5 | 121769
250.5 | 244338 |  | 252.8333 | 122119 | 254.1667 | 243638 | 255.1667 | 244438 | 250.5 | 122119
261.5 | 244338 |  | 263.5 | 121769 | 264.8333 | 243638 | 266.1667 | 244438 | 261.5 | 121769
272.3333 | 122119 |  | 274.5 | 243638 | 275.8333 | 243638 | 277 | 244438 | 272.3333 | 122119
282.8333 | 122419 |  | 285.5 | 243638 | 286.3333 | 243638 | 287.6667 | 244438 | 282.8333 | 122419
293.5 | 244338 |  | 296.1667 | 243638 | 297.1667 | 243638 | 298.5 | 244438 | 293.5 | 243638
304.5 | 244338 |  | 306.8333 | 243638 | 308.1667 | 243638 | 309.1667 | 122469 | 304.5 | 122469
315.5 | 244338 |  | 317.6667 | 243638 | 319 | 122719 | 320.1667 | 244438 | 315.5 | 122719
326.1667 | 122119 |  | 328.5 | 243638 | 329.8333 | 122419 | 330.8333 | 244438 | 326.1667 | 122119
336.8333 | 122419 |  | 339.5 | 243638 | 340.5 | 243638 | 341.8333 | 244438 | 336.8333 | 122419
347.5 | 244338 |  | 350.3333 | 243638 | 351.1667 | 243638 | 352.6667 | 244438 | 347.5 | 243638
358.5 | 244338 |  | 360.8333 | 121769 | 362.1667 | 243638 | 363.1667 | 122169 | 358.5 | 121769
369.5 | 244338 |  | 371.5 | 243638 | 372.8333 | 122719 | 374.1667 | 244438 | 369.5 | 122719
380.1667 | 244338 |  | 382.5 | 243638 | 383.8333 | 122719 | 384.8333 | 244438 | 380.1667 | 122719
390.8333 | 244338 |  | 393.5 | 243638 | 394.5 | 122419 | 395.8333 | 244438 | 390.8333 | 122419
401.5 | 244338 |  | 404.1667 | 243638 | 405.1667 | 243638 | 406.5 | 244438 | 401.5 | 243638
412.5 | 244338 |  | 414.8333 | 243638 | 416.1667 | 243638 | 417.1667 | 244438 | 412.5 | 243638
423.5 | 244338 |  | 425.5 | 243638 | 426.8333 | 243638 | 428.1667 | 244438 | 423.5 | 243638
434.1667 | 244338 |  | 436.5 | 243638 | 437.8333 | 243638 | 438.8333 | 244438 | 434.1667 | 243638
444.8333 | 244338 |  | 447.5 | 243638 | 448.5 | 243638 | 449.8333 | 244438 | 444.8333 | 243638
455.5 | 244338 |  | 458.1667 | 243638 | 459.1667 | 243638 | 460.5 | 244438 | 455.5 | 243638
466.5 | 244338 |  | 468.8333 | 243638 | 470.1667 | 243638 | 471.1667 | 244438 | 466.5 | 243638
477.3333 | 244338 |  | 479.5 | 243638 | 480.8333 | 243638 | 482 | 122469 | 477.3333 | 122469
488 | 122419 |  | 490.5 | 243638 | 491.6667 | 243638 | 492.8333 | 122469 | 488 | 122419
498.8333 | 244338 |  | 501.5 | 243638 | 502.3333 | 243638 | 503.6667 | 244438 | 498.8333 | 243638
509.5 | 244338 |  | 512 | 243638 | 513.1667 | 121769 | 514.3333 | 244438 | 509.5 | 121769
520.5 | 244338 |  | 522.6667 | 243638 | 524 | 122419 | 525.1667 | 244438 | 520.5 | 122419
531.3333 | 244338 |  | 533.5 | 243638 | 534.8333 | 243638 | 536 | 122719 | 531.3333 | 122719
542.1667 | 244338 |  | 544.5 | 243638 | 545.8333 | 243638 | 546.8333 | 244438 | 542.1667 | 243638
552.8333 | 244338 |  | 555.5 | 122119 | 556.5 | 243638 | 557.8333 | 244438 | 552.8333 | 122119
563.5 | 244338 |  | 566.1667 | 243638 | 567.1667 | 243638 | 568.5 | 244438 | 563.5 | 243638
574.5 | 244338 |  | 576.6667 | 243638 | 578 | 243638 | 579.1667 | 244438 | 574.5 | 243638
585.5 | 244338 |  | 587.5 | 243638 | 588.8333 | 243638 | 590.1667 | 122719 | 585.5 | 122719
596.1667 | 244338 |  | 598.5 | 243638 | 599.8333 | 243638 | 600.8333 | 244438 | 596.1667 | 243638
606.8333 | 244338 |  | 609.5 | 243638 | 610.3333 | 243638 | 611.6667 | 244438 | 606.8333 | 243638
617.5 | 244338 |  | 620.1667 | 243638 | 621.1667 | 243638 | 622.5 | 244438 | 617.5 | 243638
628.5 | 244338 |  | 630.8333 | 243638 | 632.1667 | 243638 | 633.1667 | 122719 | 628.5 | 122719
639.5 | 244338 |  | 641.5 | 122119 | 642.8333 | 243638 | 644.1667 | 244438 | 639.5 | 122119
650.1667 | 244338 |  | 652.5 | 243638 | 653.8333 | 243638 | 654.8333 | 244438 | 650.1667 | 243638
660.6667 | 244338 |  | 663.3333 | 243638 | 664.3333 | 243638 | 665.6667 | 244438 | 660.6667 | 243638
671.5 | 244338 |  | 674 | 243638 | 675.1667 | 243638 | 676.3333 | 244438 | 671.5 | 243638
682.5 | 244338 |  | 684.6667 | 243638 | 686 | 243638 | 687.1667 | 244438 | 682.5 | 243638
693.3333 | 122419 |  | 695.5 | 243638 | 696.8333 | 243638 | 698 | 244438 | 693.3333 | 122419
704 | 244338 |  | 706.5 | 243638 | 707.6667 | 243638 | 708.8333 | 244438 | 704 | 243638
714.6667 | 244338 |  | 717.3333 | 243638 | 718.3333 | 243638 | 719.6667 | 244438 | 714.6667 | 243638
725.5 | 244338 |  | 728 | 243638 | 729.1667 | 243638 | 730.3333 | 244438 | 725.5 | 243638
736.5 | 244338 |  | 738.6667 | 243638 | 740 | 243638 | 741.1667 | 244438 | 736.5 | 243638
747.3333 | 244338 |  | 749.5 | 243638 | 750.8333 | 243638 | 752 | 244438 | 747.3333 | 243638
758 | 82805.8074 |  | 760.5 | 243638 | 761.6667 | 243638 | 762.8333 | 10395.2907 | 758 | 10395.2907
768.6667 | 6011.4458 |  | 771.3333 | 244338 | 772.3333 | 243638 | 773.6667 | 11236.6154 | 768.6667 | 6011.4458
779.5 | 10161.8434 |  | 782 | 12242.6422 | 783.1667 | 20484.4304 | 784.3333 | 3606.4952 | 779.5 | 3606.4952
790.5 | 629.3871 |  | 792.8333 | 11675.0405 | 794.1667 | 16395.0183 | 795.1667 | 2642.3874 | 790.5 | 629.3871
801.3333 | 2108.8358 |  | 803.5 | 10632.9001 | 804.8333 | 12535.6026 | 806 | 1850.0171 | 801.3333 | 1850.0171
812 | 1883.4125 |  | 814.5 | 6161.6997 | 815.6667 | 4766.6091 | 816.8333 | 1483.2218 | 812 | 1483.2218
822.6667 | 1773.346 |  | 825.3333 | 3747.2216 | 826.3333 | 1605.6233 | 827.6667 | 1239.6176 | 822.6667 | 1239.6176
833.5 | 1054.2132 |  | 836 | 4226.5129 | 837.1667 | 1734.9255 | 838.3333 | 1259.4046 | 833.5 | 1054.2132
844.5 | 1151.0818 |  | 846.6667 | 3504.1236 | 848 | 1247.6875 | 849.1667 | 963.6595 | 844.5 | 963.6595
855.5 | 660.7563 |  | 857.5 | 2683.9998 | 858.8333 | 1049.027 | 860.1667 | 769.7115 | 855.5 | 660.7563
866 | 919.179 |  | 868.5 | 2931.1943 | 869.6667 | 920.987 | 870.8333 | 900.7977 | 866 | 900.7977
876.6667 | 705.7653 |  | 879.3333 | 159.2204 | 880.3333 | 865.9731 | 881.6667 | 255.3969 | 876.6667 | 159.2204
887.5 | 1215.5403 |  | 890 | 1008.9305 | 891.1667 | 441.3066 | 892.3333 | 753.4387 | 887.5 | 441.3066
898.5 | 828.5235 |  | 900.6667 | 669.9232 | 902 | 442.4988 | 903.1667 | 1234.9555 | 898.5 | 442.4988
909.1667 | 416.5031 |  | 911.5 | 564.0274 | 912.8333 | 653.8298 | 913.8333 | 700.4287 | 909.1667 | 416.5031
920 | 391.262 |  | 922.5 | 365.9003 | 923.6667 | 1680.6713 | 924.8333 | 528.2116 | 920 | 365.9003
930.6667 | 126.1274 |  | 933.3333 | 338.5712 | 934.3333 | 316.0518 | 935.6667 | 223.2255 | 930.6667 | 126.1274
941.5 | 341.2098 |  | 944 | 64.8692 | 945.1667 | 69.554 | 946.3333 | 29.1879 | 941.5 | 29.1879
952.5 | 13.4735 |  | 954.6667 | 35.2374 | 956 | 24.7226 | 957.1667 | 73.5929 | 952.5 | 13.4735
963.1667 | 36.8529 |  | 965.5 | 102.0659 | 966.8333 | 82.4491 | 967.8333 | 58.9726 | 963.1667 | 36.8529
974.1667 | 36.7622 |  | 976.5 | 66.1731 | 977.8333 | 176.0495 | 978.8333 | 77.5911 | 974.1667 | 36.7622
984.8333 | 58.5331 |  | 987.5 | 77.7731 | 988.3333 | 138.8461 | 989.6667 | 171.9232 | 984.8333 | 58.5331
995.5 | 119.2057 |  | 998.1667 | 108.5435 | 999.1667 | 187.6643 | 1000.5 | 135.7216 | 995.5 | 108.5435
1006.5 | 305.5209 |  | 1008.8333 | 29.7141 | 1010.1667 | 6.7601 | 1011.1667 | 12.992 | 1006.5 | 6.7601
1017.3333 | 0.96027 |  | 1019.5 | 2.2712 | 1020.8333 | 3.2897 | 1022 | 19.7998 | 1017.3333 | 0.96027
1028 | 19.7372 |  | 1030.5 | 0.67763 | 1031.6667 | 9.3409 | 1032.8333 | 6.85 | 1028 | 0.67763
1038.6667 | 19.5284 |  | 1041.3333 | 0.75115 | 1042.3333 | 6.4119 | 1043.6667 | 7.3785 | 1038.6667 | 0.75115
1049.5 | 10.9677 |  | 1052 | 0.84859 | 1053.1667 | 15.3525 | 1054.3333 | 3.3221 | 1049.5 | 0.84859
1060.5 | 5.5233 |  | 1062.8333 | 4.9 | 1064.1667 | 3.1834 | 1065.1667 | 0.68146 | 1060.5 | 0.68146
1071.3333 | 8.8227 |  | 1073.5 | 0.95819 | 1074.8333 | 0.78702 | 1076 | 11.3078 | 1071.3333 | 0.78702
1082 | 2.2213 |  | 1084.5 | 4.0367 | 1085.6667 | 3.0752 | 1086.8333 | 1.9547 | 1082 | 1.9547
1092.6667 | 27.1239 |  | 1095.3333 | 4.0057 | 1096.3333 | 0.82624 | 1097.6667 | 1.0958 | 1092.6667 | 0.82624
1103.5 | 2.9897 |  | 1106 | 1.981 | 1107.1667 | 13.6946 | 1108.3333 | 7.0825 | 1103.5 | 1.981
1114.5 | 0.6793 |  | 1116.6667 | 12.2532 | 1118 | 3.865 | 1119.1667 | 3.2824 | 1114.5 | 0.6793
1125.3333 | 1.8296 |  | 1127.5 | 11.4376 | 1128.8333 | 2.5479 | 1130 | 0.68158 | 1125.3333 | 0.68158
1136 | 9.3935 |  | 1138.5 | 0.93531 | 1139.6667 | 2.752 | 1140.8333 | 17.8433 | 1136 | 0.93531
1146.6667 | 4.4229 |  | 1149.3333 | 1.1825 | 1150.3333 | 11.9449 | 1151.6667 | 11.1756 | 1146.6667 | 1.1825
1157.5 | 8.5222 |  | 1160 | 23.7314 | 1161.1667 | 7.4543 | 1162.3333 | 0.84471 | 1157.5 | 0.84471
1168.5 | 13.1848 |  | 1170.6667 | 8.371 | 1172 | 6.1977 | 1173.1667 | 2.5436 | 1168.5 | 2.5436
1179.3333 | 6.4669 |  | 1181.5 | 13.3567 | 1182.8333 | 4.6358 | 1184 | 0.68928 | 1179.3333 | 0.68928
1189.8333 | 9.7003 |  | 1192.5 | 9.4481 | 1193.5 | 4.8972 | 1194.8333 | 7.245 | 1189.8333 | 4.8972
1200.6667 | 7.2991 |  | 1203.3333 | 1.6665 | 1204.3333 | 16.5271 | 1205.6667 | 9.0068 | 1200.6667 | 1.6665
1211.5 | 1.6991 |  | 1214 | 18.4136 | 1215.1667 | 1.6873 | 1216.3333 | 7.9297 | 1211.5 | 1.6873
1222.5 | 11.591 |  | 1224.6667 | 4.6658 | 1226 | 2.2165 | 1227.1667 | 1.8814 | 1222.5 | 1.8814
1233.3333 | 4.7725 |  | 1235.5 | 20.7401 | 1236.8333 | 2.1107 | 1238 | 11.5586 | 1233.3333 | 2.1107
1244 | 1.8724 |  | 1246.5 | 1.6813 | 1247.6667 | 3.3147 | 1248.8333 | 14.6177 | 1244 | 1.6813
1254.6667 | 3.7608 |  | 1257.3333 | 15.4381 | 1258.3333 | 2.2717 | 1259.6667 | 6.7036 | 1254.6667 | 2.2717
1265.5 | 13.7777 |  | 1268 | 11.3279 | 1269.1667 | 3.4362 | 1270.3333 | 4.6239 | 1265.5 | 3.4362
1276.5 | 7.2558 |  | 1278.6667 | 6.0778 | 1280 | 19.6109 | 1281.1667 | 6.5011 | 1276.5 | 6.0778
1287.3333 | 2.1892 |  | 1289.5 | 4.8062 | 1290.8333 | 14.4516 | 1292 | 1.5256 | 1287.3333 | 1.5256
1298 | 2.4188 |  | 1300.5 | 1.2386 | 1301.6667 | 17.0098 | 1302.8333 | 20.7857 | 1298 | 1.2386
1308.6667 | 4.3136 |  | 1311.3333 | 1.5847 | 1312.3333 | 9.6894 | 1313.6667 | 6.7637 | 1308.6667 | 1.5847
1319.5 | 20.5795 |  | 1322 | 1.1581 | 1323.1667 | 6.9016 | 1324.3333 | 2.7188 | 1319.5 | 1.1581
1330.5 | 12.4581 |  | 1332.5 | 6.2561 | 1333.8333 | 3.0054 | 1335.1667 | 9.0869 | 1330.5 | 3.0054
1341.1667 | 4.7458 |  | 1343.5 | 5.1525 | 1344.8333 | 15.5197 | 1345.8333 | 6.5568 | 1341.1667 | 4.7458
1351.8333 | 5.4449 |  | 1354.5 | 3.5099 | 1355.5 | 4.4476 | 1356.8333 | 2.6573 | 1351.8333 | 2.6573
1362.5 | 10.6253 |  | 1365.1667 | 8.2672 | 1366.1667 | 16.5196 | 1367.5 | 2.3061 | 1362.5 | 2.3061
1373.5 | 3.3234 |  | 1376 | 21.2411 | 1377.1667 | 20.1907 | 1378.3333 | 4.9354 | 1373.5 | 3.3234
1384.5 | 3.4291 |  | 1386.6667 | 19.6114 | 1388 | 3.8877 | 1389.1667 | 2.5182 | 1384.5 | 2.5182
1395.1667 | 14.0421 |  | 1397.5 | 17.0295 | 1398.8333 | 15.8423 | 1399.8333 | 6.6169 | 1395.1667 | 6.6169
1405.8333 | 10.7654 |  | 1408.5 | 8.1466 | 1409.5 | 16.9828 | 1410.8333 | 19.0351 | 1405.8333 | 8.1466
1416.5 | 40.7998 |  | 1419.1667 | 70.9374 | 1420.1667 | 38.1225 | 1421.5 | 39.4972 | 1416.5 | 38.1225
1427.5 | 86.9252 |  | 1429.8333 | 8.226 | 1431.1667 | 31.8148 | 1432.1667 | 12.3975 | 1427.5 | 8.226
1438.5 | 12.0244 |  | 1440.5 | 11.6722 | 1441.8333 | 5.6011 | 1443.1667 | 7.2108 | 1438.5 | 5.6011
1449.1667 | 13.3812 |  | 1451.5 | 10.283 | 1452.8333 | 27.1286 | 1453.8333 | 10.829 | 1449.1667 | 10.283
1459.8333 | 20.7901 |  | 1462.5 | 17.3758 | 1463.5 | 27.4281 | 1464.8333 | 8.2383 | 1459.8333 | 8.2383
1470.5 | 6.6751 |  | 1473.1667 | 6.4653 | 1474.1667 | 18.2485 | 1475.5 | 6.485 | 1470.5 | 6.4653

## C3-4
Penlight Test 1 |  |  | 2006-06-29 | 13:39 |  | Vs = |  | 149.9621 |  | R = | 100
XLPE | 3-C | Tray
475 C | 17.7 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38897.5681 | 1 | 0 | 38897.5681 | 1 | 0 | -174.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5683 | 1 | 0 | 38897.5683 | 1 | 0 | -163.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5684 | 1 | 0 | 38897.5684 | 1 | 0 | -152.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5685 | 1 | 0 | 38897.5685 | 1 | 0 | -141.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5686 | 1 | 0 | 38897.5686 | 1 | 0 | -131.5 | 52.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5687 | 1 | 0 | 38897.5688 | 1 | 0 | -120.5 | 63.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5689 | 1 | 0 | 38897.5689 | 1 | 0 | -109.5 | 74.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.569 | 1 | 0 | 38897.569 | 1 | 0 | -98.5 | 85.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5691 | 1 | 0 | 38897.5691 | 1 | 0 | -87.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5692 | 1 | 0 | 38897.5693 | 1 | 0 | -77.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5694 | 1 | 0 | 38897.5694 | 1 | 0 | -66.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5695 | 1 | 0 | 38897.5695 | 1 | 0 | -55.5 | 128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5696 | 2 | 0 | 38897.5696 | 2 | 0 | -44.5 | 139.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122719 | 122719 | 122718.9988
38897.5698 | 1 | 0 | 38897.5698 | 1 | 0 | -33.5 | 150.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5699 | 1 | 0 | 38897.5699 | 1 | 0 | -23 | 161 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.57 | 1 | 0 | 38897.57 | 1 | 0 | -12.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5701 | 2 | 0 | 38897.5701 | 1 | 0 | -1.5 | 182.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122719 | 245538 | 122718.9988
38897.5703 | 1 | 0 | 38897.5703 | 1 | 0 | 9.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5704 | 1 | 0 | 38897.5704 | 1 | 0 | 20.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5705 | 1 | 0 | 38897.5705 | 1 | 0 | 31 | 215 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5706 | 1 | 0 | 38897.5706 | 1 | 0 | 41.5 | 225.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5708 | 1 | 0 | 38897.5708 | 1 | 0 | 52.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5709 | 1 | 0 | 38897.5709 | 1 | 0 | 63.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.571 | 1 | 0 | 38897.571 | 1 | 0 | 74.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5711 | 1 | 0 | 38897.5711 | 1 | 0 | 85 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5713 | 1 | 0 | 38897.5713 | 1 | 0 | 95.5 | 279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5714 | 1 | 0 | 38897.5714 | 1 | 0 | 106.5 | 290.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5715 | 1 | 0 | 38897.5715 | 1 | 0 | 117.5 | 301.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5716 | 1 | 1 | 38897.5716 | 1 | 0 | 128.5 | 312.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 602889094.44 | 245538 | 245338.0814
38897.5717 | 1 | 0 | 38897.5718 | 1 | 0 | 138.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5719 | 1 | 0 | 38897.5719 | 1 | 0 | 149.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.572 | 1 | 0 | 38897.572 | 1 | 0 | 160.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5721 | 1 | 0 | 38897.5721 | 1 | 0 | 171.5 | 355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5723 | 1 | 0 | 38897.5723 | 1 | 0 | 182.5 | 366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5724 | 1 | 1 | 38897.5724 | 1 | 0 | 192.5 | 376.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 602889094.44 | 245538 | 245338.0814
38897.5725 | 1 | 0 | 38897.5725 | 2 | 0 | 203.5 | 387.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38897.5726 | 1 | 0 | 38897.5726 | 1 | 0 | 214.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5728 | 1 | 1 | 38897.5728 | 1 | 0 | 225.5 | 409.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 602889094.44 | 245538 | 245338.0814
38897.5729 | 1 | 0 | 38897.5729 | 1 | 0 | 236.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.573 | 1 | 0 | 38897.573 | 1 | 0 | 246.5 | 430.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5731 | 1 | 0 | 38897.5731 | 1 | 0 | 257.5 | 441.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5733 | 1 | 0 | 38897.5733 | 1 | 0 | 268.5 | 452.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5734 | 1 | 0 | 38897.5734 | 1 | 0 | 279.5 | 463.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5735 | 1 | 0 | 38897.5735 | 1 | 0 | 290 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5736 | 1 | 0 | 38897.5736 | 1 | 0 | 300.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5738 | 1 | 0 | 38897.5738 | 1 | 0 | 311.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5739 | 2 | 0 | 38897.5739 | 1 | 0 | 322.5 | 506.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122719 | 245538 | 122718.9988
38897.574 | 1 | 0 | 38897.574 | 1 | 0 | 333.5 | 517.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5741 | 1 | 0 | 38897.5741 | 1 | 0 | 344.5 | 528.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5742 | 1 | 0 | 38897.5743 | 1 | 0 | 354.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5744 | 1 | 1 | 38897.5744 | 1 | 0 | 365.5 | 549.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 602889094.44 | 245538 | 245338.0814
38897.5745 | 2 | 0 | 38897.5745 | 1 | 0 | 376.5 | 560.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122719 | 245538 | 122718.9988
38897.5746 | 2 | 0 | 38897.5746 | 1 | 0 | 387.5 | 571.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122719 | 245538 | 122718.9988
38897.5748 | 1 | 0 | 38897.5748 | 1 | 0 | 398.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5749 | 1 | 0 | 38897.5749 | 1 | 0 | 408.5 | 592.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.575 | 1 | 0 | 38897.575 | 1 | 0 | 419.5 | 603.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5751 | 1 | 0 | 38897.5751 | 1 | 0 | 430.5 | 614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5753 | 1 | 0 | 38897.5753 | 1 | 0 | 441.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5754 | 1 | 0 | 38897.5754 | 1 | 0 | 452.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5755 | 1 | 0 | 38897.5755 | 1 | 0 | 462.5 | 646.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5756 | 1 | 0 | 38897.5756 | 1 | 0 | 473.5 | 657.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5758 | 1 | 0 | 38897.5758 | 1 | 0 | 484.5 | 668.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5759 | 1 | 0 | 38897.5759 | 1 | 0 | 495.5 | 679.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.576 | 1 | 0 | 38897.576 | 1 | 0 | 506 | 690 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5761 | 1 | 0 | 38897.5761 | 1 | 0 | 516.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5762 | 1 | 0 | 38897.5763 | 1 | 0 | 527.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5764 | 1 | 0 | 38897.5764 | 2 | 0 | 538.5 | 722.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38897.5765 | 1 | 0 | 38897.5765 | 1 | 0 | 549.5 | 733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5766 | 1 | 0 | 38897.5766 | 1 | 0 | 560.5 | 744.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5767 | 1 | 0 | 38897.5768 | 1 | 0 | 570.5 | 754.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5769 | 1 | 0 | 38897.5769 | 1 | 0 | 581.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.577 | 1 | 0 | 38897.577 | 2 | 0 | 592.5 | 776.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38897.5771 | 1 | 1 | 38897.5771 | 1 | 0 | 603.5 | 787.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 602889094.44 | 245538 | 245338.0814
38897.5773 | 1 | 0 | 38897.5773 | 1 | 0 | 614 | 798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5774 | 1 | 0 | 38897.5774 | 1 | 0 | 624.5 | 808.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5775 | 1 | 0 | 38897.5775 | 2 | 0 | 635.5 | 819.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38897.5776 | 1 | 0 | 38897.5776 | 1 | 0 | 646.5 | 830.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5778 | 1 | 0 | 38897.5778 | 1 | 0 | 657.5 | 841.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5779 | 1 | 0 | 38897.5779 | 1 | 0 | 668 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.578 | 1 | 0 | 38897.578 | 1 | 0 | 678.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5781 | 1 | 0 | 38897.5781 | 1 | 0 | 689.5 | 873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5783 | 1 | 0 | 38897.5783 | 1 | 0 | 700.5 | 884.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5784 | 1 | 0 | 38897.5784 | 1 | 0 | 711.5 | 895.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5785 | 1 | 0 | 38897.5785 | 1 | 0 | 722 | 906 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5786 | 1 | 0 | 38897.5786 | 1 | 0 | 732.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5788 | 1 | 0 | 38897.5788 | 1 | 0 | 743.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5789 | 1 | 0 | 38897.5789 | 1 | 0 | 754.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.579 | 1 | 0 | 38897.579 | 1 | 0 | 765.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5791 | 1 | 0 | 38897.5791 | 1 | 0 | 776 | 960 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38897.5792 | 1 | 2 | 38897.5793 | 2 | 1 | 786.5 | 970.5 | 0.06105 | 0.1221 | 0.1221 | 0.06105 | 0.0006105 | 0.001221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 245738.1631 | 245537.9185 | 122619.061
38897.5794 | 42 | 29 | 38897.5794 | 107 | 18 | 797.5 | 981.5 | 2.5641 | 1.7705 | 6.5324 | 1.0989 | 0.025641 | 0.017705 | 0.065324 | 0.010989 | 0.0079365 | 0.054335 | 20284.6331 | 2642.3874 | 7925.5108
38897.5795 | 78 | 56 | 38897.5795 | 169 | 45 | 808.5 | 992.5 | 4.7619 | 3.4188 | 10.3175 | 2.7473 | 0.047619 | 0.034188 | 0.10317 | 0.027473 | 0.013431 | 0.075702 | 12535.6026 | 1850.0171 | 3934.4368
38897.5796 | 174 | 120 | 38897.5796 | 291 | 148 | 819.5 | 1003.5 | 10.6227 | 7.326 | 17.7656 | 9.0354 | 0.10623 | 0.07326 | 0.17766 | 0.090354 | 0.032967 | 0.087302 | 4935.7866 | 1546.6835 | 1692.5523
38897.5798 | 653 | 543 | 38897.5798 | 316 | 206 | 830 | 1014 | 39.8657 | 33.1502 | 19.2918 | 12.5763 | 0.39866 | 0.3315 | 0.19292 | 0.12576 | 0.067155 | 0.067155 | 2133.0727 | 2133.0727 | 221.7198
38897.5799 | 1177 | 1028 | 38897.5799 | 956 | 795 | 840.5 | 1024.5 | 71.8559 | 62.7595 | 58.3639 | 48.5348 | 0.71856 | 0.62759 | 0.58364 | 0.48535 | 0.090965 | 0.098291 | 1898.9188 | 1259.4046 | 22.6545
38897.58 | 1061 | 899 | 38897.58 | 964 | 801 | 851.5 | 1035.5 | 64.7741 | 54.884 | 58.8523 | 48.9011 | 0.64774 | 0.54884 | 0.58852 | 0.48901 | 0.098901 | 0.099512 | 1430.5983 | 1394.6246 | 51.5205
38897.5801 | 1108 | 941 | 38897.5801 | 1227 | 1033 | 862.5 | 1046.5 | 67.6435 | 57.4481 | 74.9084 | 63.0647 | 0.67643 | 0.57448 | 0.74908 | 0.63065 | 0.10195 | 0.11844 | 3013.3814 | 769.7115 | 38.3145
38897.5803 | 1176 | 998 | 38897.5803 | 1106 | 923 | 873.5 | 1057.5 | 71.7949 | 60.928 | 67.5214 | 56.3492 | 0.71795 | 0.60928 | 0.67521 | 0.56349 | 0.10867 | 0.11172 | 1399.2631 | 1153.8089 | 26.0379
38897.5804 | 1005 | 823 | 38897.5804 | 1060 | 867 | 884 | 1068 | 61.3553 | 50.2442 | 64.7131 | 52.9304 | 0.61355 | 0.50244 | 0.64713 | 0.5293 | 0.11111 | 0.11783 | 1377.867 | 1073.5055 | 69.846
38897.5805 | 1203 | 992 | 38897.5805 | 1256 | 1096 | 894.5 | 1078.5 | 73.4432 | 60.5617 | 76.6789 | 66.9109 | 0.73443 | 0.60562 | 0.76679 | 0.66911 | 0.12882 | 0.09768 | 441.3066 | 1358.6116 | 24.5424
38897.5806 | 1231 | 995 | 38897.5806 | 1007 | 870 | 905.5 | 1089.5 | 75.1526 | 60.7448 | 61.4774 | 53.1136 | 0.75153 | 0.60745 | 0.61477 | 0.53114 | 0.14408 | 0.083639 | 442.4988 | 2431.4097 | 22.2391
38897.5808 | 1174 | 888 | 38897.5808 | 1301 | 1027 | 916.5 | 1100.5 | 71.6728 | 54.2125 | 79.4261 | 62.6984 | 0.71673 | 0.54212 | 0.79426 | 0.62698 | 0.1746 | 0.16728 | 653.8298 | 988.1336 | 40.3307
38897.5809 | 947 | 730 | 38897.5809 | 982 | 668 | 927.5 | 1111.5 | 57.8144 | 44.5665 | 59.9512 | 40.7814 | 0.57814 | 0.44567 | 0.59951 | 0.40781 | 0.13248 | 0.1917 | 1915.5102 | 528.2116 | 89.7694
38897.581 | 1299 | 764 | 38897.581 | 1389 | 876 | 938 | 1122 | 79.304 | 46.6422 | 84.7985 | 53.4799 | 0.79304 | 0.46642 | 0.84799 | 0.5348 | 0.32662 | 0.31319 | 316.0518 | 452.6052 | 42.1719
38897.5811 | 1712 | 145 | 38897.5811 | 1973 | 130 | 948.5 | 1132.5 | 104.5177 | 8.8523 | 120.4518 | 7.9365 | 1.0452 | 0.088523 | 1.2045 | 0.079365 | 0.95665 | 1.1252 | 69.554 | 29.1879 | 93.3933
38897.5813 | 1930 | 555 | 38897.5813 | 1847 | 657 | 959.5 | 1143.5 | 117.8266 | 33.8828 | 112.7595 | 40.1099 | 1.1783 | 0.33883 | 1.1276 | 0.4011 | 0.83944 | 0.7265 | 24.7226 | 73.5929 | 2.1862
38897.5814 | 1359 | 493 | 38897.5814 | 1738 | 506 | 970.5 | 1154.5 | 82.967 | 30.0977 | 106.105 | 30.8913 | 0.82967 | 0.30098 | 1.0611 | 0.30891 | 0.52869 | 0.75214 | 3655.6198 | 58.9726 | 45.4769
38897.5815 | 1342 | 498 | 38897.5815 | 1697 | 608 | 981.5 | 1165.5 | 81.9292 | 30.4029 | 103.602 | 37.1184 | 0.81929 | 0.30403 | 1.036 | 0.37118 | 0.51526 | 0.66484 | 551.1998 | 77.5911 | 54.0767
38897.5816 | 1421 | 581 | 38897.5816 | 1461 | 594 | 992 | 1176 | 86.7521 | 35.4701 | 89.1941 | 36.2637 | 0.86752 | 0.3547 | 0.89194 | 0.36264 | 0.51282 | 0.5293 | 206.227 | 171.9232 | 49.446
38897.5817 | 1246 | 658 | 38897.5818 | 1278 | 570 | 1002.5 | 1186.5 | 76.0684 | 40.1709 | 78.022 | 34.7985 | 0.76068 | 0.40171 | 0.78022 | 0.34799 | 0.35897 | 0.43223 | 463.048 | 201.466 | 56.1016
38897.5819 | 2310 | 28 | 38897.5819 | 2042 | 20 | 1013.5 | 1197.5 | 141.0256 | 1.7094 | 124.6642 | 1.221 | 1.4103 | 0.017094 | 1.2466 | 0.01221 | 1.3932 | 1.2344 | 6.7601 | 24.0061 | 81.8463
38897.582 | 2382 | 20 | 38897.582 | 2149 | 19 | 1024.5 | 1208.5 | 145.4212 | 1.221 | 131.1966 | 1.16 | 1.4542 | 0.01221 | 1.312 | 0.0116 | 1.442 | 1.3004 | 3.2897 | 19.7998 | 44.938
38897.5821 | 2055 | 16 | 38897.5821 | 1968 | 15 | 1035.5 | 1219.5 | 125.4579 | 0.9768 | 120.1465 | 0.91575 | 1.2546 | 0.009768 | 1.2015 | 0.0091575 | 1.2448 | 1.1923 | 20.298 | 25.9901 | 496.8675
38897.5823 | 2220 | 15 | 38897.5823 | 2298 | 16 | 1046 | 1230 | 135.5311 | 0.91575 | 140.293 | 0.9768 | 1.3553 | 0.0091575 | 1.4029 | 0.009768 | 1.3462 | 1.3932 | 11.8089 | 7.3785 | 101.4139
38897.5824 | 2173 | 12 | 38897.5824 | 2380 | 11 | 1056.5 | 1240.5 | 132.6618 | 0.7326 | 145.2991 | 0.67155 | 1.3266 | 0.007326 | 1.453 | 0.0067155 | 1.3193 | 1.4463 | 15.7452 | 3.3221 | 72.714
38897.5825 | 2104 | 7 | 38897.5825 | 2440 | 9 | 1067.5 | 1251.5 | 128.4493 | 0.42735 | 148.9621 | 0.54945 | 1.2845 | 0.0042735 | 1.4896 | 0.0054945 | 1.2802 | 1.4841 | 32.9392 | 0.68146 | 33.3955
38897.5826 | 2047 | 6 | 38897.5826 | 2211 | 7 | 1078.5 | 1262.5 | 124.9695 | 0.3663 | 134.9817 | 0.42735 | 1.2497 | 0.003663 | 1.3498 | 0.0042735 | 1.246 | 1.3455 | 20.5932 | 11.3078 | 682.9916
38897.5828 | 1996 | 6 | 38897.5828 | 2410 | 8 | 1089.5 | 1273.5 | 121.8559 | 0.3663 | 147.1306 | 0.4884 | 1.2186 | 0.003663 | 1.4713 | 0.004884 | 1.2149 | 1.4664 | 27.354 | 1.9547 | 145.1907
38897.5829 | 1928 | 5 | 38897.5829 | 2430 | 6 | 1100 | 1284 | 117.7045 | 0.30525 | 148.3516 | 0.3663 | 1.177 | 0.0030525 | 1.4835 | 0.003663 | 1.174 | 1.4799 | 36.0247 | 1.0958 | 113.462
38897.583 | 2150 | 6 | 38897.583 | 2298 | 8 | 1110.5 | 1294.5 | 131.2576 | 0.3663 | 140.293 | 0.4884 | 1.3126 | 0.003663 | 1.4029 | 0.004884 | 1.3089 | 1.398 | 14.878 | 7.0825 | 331.12
38897.5831 | 2372 | 6 | 38897.5831 | 2386 | 9 | 1121.5 | 1305.5 | 144.8107 | 0.3663 | 145.6654 | 0.54945 | 1.4481 | 0.003663 | 1.4567 | 0.0054945 | 1.4444 | 1.4512 | 3.865 | 3.2824 | 41.5168
38897.5833 | 2371 | 5 | 38897.5833 | 2013 | 6 | 1132.5 | 1316.5 | 144.7497 | 0.30525 | 122.8938 | 0.3663 | 1.4475 | 0.0030525 | 1.2289 | 0.003663 | 1.4444 | 1.2253 | 3.6406 | 24.0681 | 311.8597
38897.5834 | 2391 | 8 | 38897.5834 | 1909 | 6 | 1143.5 | 1327.5 | 145.9707 | 0.4884 | 116.5446 | 0.3663 | 1.4597 | 0.004884 | 1.1654 | 0.003663 | 1.4548 | 1.1618 | 2.7723 | 32.4552 | 175.7461
38897.5835 | 2117 | 6 | 38897.5835 | 2042 | 7 | 1154 | 1338 | 129.243 | 0.3663 | 124.6642 | 0.42735 | 1.2924 | 0.003663 | 1.2466 | 0.0042735 | 1.2888 | 1.2424 | 16.2995 | 20.8016 | 956.7824
38897.5836 | 1860 | 6 | 38897.5836 | 2436 | 8 | 1164.5 | 1348.5 | 113.5531 | 0.3663 | 148.7179 | 0.4884 | 1.1355 | 0.003663 | 1.4872 | 0.004884 | 1.1319 | 1.4823 | 52.1449 | 0.84471 | 82.4206
38897.5837 | 2135 | 7 | 38897.5838 | 1980 | 6 | 1175.5 | 1359.5 | 130.3419 | 0.42735 | 120.8791 | 0.3663 | 1.3034 | 0.0042735 | 1.2088 | 0.003663 | 1.2991 | 1.2051 | 15.3069 | 24.6216 | 887.3202
38897.5839 | 1980 | 7 | 38897.5839 | 2350 | 9 | 1186.5 | 1370.5 | 120.8791 | 0.42735 | 143.4676 | 0.54945 | 1.2088 | 0.0042735 | 1.4347 | 0.0054945 | 1.2045 | 1.4292 | 26.1572 | 4.612 | 295.6202
38897.584 | 2346 | 9 | 38897.584 | 2233 | 8 | 1197.5 | 1381.5 | 143.2234 | 0.54945 | 136.3248 | 0.4884 | 1.4322 | 0.0054945 | 1.3632 | 0.004884 | 1.4267 | 1.3584 | 4.8972 | 10.8351 | 110.1194
38897.5841 | 2107 | 8 | 38897.5841 | 2259 | 10 | 1208 | 1392 | 128.6325 | 0.4884 | 137.9121 | 0.6105 | 1.2863 | 0.004884 | 1.3791 | 0.006105 | 1.2814 | 1.373 | 17.3806 | 9.0068 | 352.5846
38897.5842 | 2147 | 10 | 38897.5843 | 2033 | 8 | 1218.5 | 1402.5 | 131.0745 | 0.6105 | 124.1148 | 0.4884 | 1.3107 | 0.006105 | 1.2411 | 0.004884 | 1.3046 | 1.2363 | 14.7997 | 21.4811 | 529.3831
38897.5844 | 2404 | 9 | 38897.5844 | 2016 | 10 | 1229.5 | 1413.5 | 146.7643 | 0.54945 | 123.0769 | 0.6105 | 1.4676 | 0.0054945 | 1.2308 | 0.006105 | 1.4621 | 1.2247 | 2.2165 | 28.3233 | 106.3863
38897.5845 | 2408 | 12 | 38897.5845 | 2252 | 10 | 1240.5 | 1424.5 | 147.0085 | 0.7326 | 137.4847 | 0.6105 | 1.4701 | 0.007326 | 1.3748 | 0.006105 | 1.4628 | 1.3687 | 2.1107 | 11.5586 | 31.411
38897.5846 | 2379 | 10 | 38897.5846 | 1961 | 8 | 1251.5 | 1435.5 | 145.2381 | 0.6105 | 119.7192 | 0.4884 | 1.4524 | 0.006105 | 1.1972 | 0.004884 | 1.4463 | 1.1923 | 3.3147 | 28.9416 | 151.238
38897.5848 | 2405 | 9 | 38897.5848 | 2336 | 12 | 1262 | 1446 | 146.8254 | 0.54945 | 142.6129 | 0.7326 | 1.4683 | 0.0054945 | 1.4261 | 0.007326 | 1.4628 | 1.4188 | 2.2717 | 6.7036 | 29.5832
38897.5849 | 2370 | 11 | 38897.5849 | 1921 | 10 | 1272.5 | 1456.5 | 144.6886 | 0.67155 | 117.2772 | 0.6105 | 1.4469 | 0.0067155 | 1.1728 | 0.006105 | 1.4402 | 1.1667 | 3.7148 | 32.6091 | 168.5114
38897.585 | 1844 | 12 | 38897.585 | 2245 | 14 | 1283.5 | 1467.5 | 112.5763 | 0.7326 | 137.0574 | 0.8547 | 1.1258 | 0.007326 | 1.3706 | 0.008547 | 1.1184 | 1.362 | 35.8628 | 9.6434 | 440.0411
38897.5851 | 2222 | 13 | 38897.5851 | 2421 | 15 | 1294.5 | 1478.5 | 135.6532 | 0.79365 | 147.8022 | 0.91575 | 1.3565 | 0.0079365 | 1.478 | 0.0091575 | 1.3486 | 1.4689 | 17.2739 | 1.5256 | 25.5886
38897.5853 | 2075 | 12 | 38897.5853 | 1896 | 12 | 1305.5 | 1489.5 | 126.6789 | 0.7326 | 115.7509 | 0.7326 | 1.2668 | 0.007326 | 1.1575 | 0.007326 | 1.2595 | 1.1502 | 18.8427 | 30.7848 | 724.5544
38897.5854 | 2247 | 15 | 38897.5854 | 2054 | 13 | 1316 | 1500 | 137.1795 | 0.91575 | 125.3968 | 0.79365 | 1.3718 | 0.0091575 | 1.254 | 0.0079365 | 1.3626 | 1.246 | 9.6894 | 21.102 | 225.8046
38897.5855 | 1855 | 13 | 38897.5855 | 1914 | 13 | 1326.5 | 1510.5 | 113.2479 | 0.79365 | 116.8498 | 0.79365 | 1.1325 | 0.0079365 | 1.1685 | 0.0079365 | 1.1245 | 1.1606 | 33.4589 | 29.1266 | 1020.9128
38897.5856 | 2387 | 18 | 38897.5856 | 2011 | 15 | 1337.5 | 1521.5 | 145.7265 | 1.0989 | 122.7717 | 0.91575 | 1.4573 | 0.010989 | 1.2277 | 0.0091575 | 1.4463 | 1.2186 | 3.0054 | 29.7535 | 65.4546
38897.5858 | 1975 | 16 | 38897.5858 | 2221 | 20 | 1348.5 | 1532.5 | 120.5739 | 0.9768 | 135.5922 | 1.221 | 1.2057 | 0.009768 | 1.3559 | 0.01221 | 1.196 | 1.3437 | 26.5295 | 11.0735 | 289.9765
38897.5859 | 2361 | 17 | 38897.5859 | 2293 | 16 | 1359.5 | 1543.5 | 144.1392 | 1.0379 | 139.9878 | 0.9768 | 1.4414 | 0.010379 | 1.3999 | 0.009768 | 1.431 | 1.3901 | 4.4476 | 8.5215 | 36.2042
38897.586 | 1923 | 19 | 38897.586 | 2226 | 22 | 1369.5 | 1553.5 | 117.3993 | 1.16 | 135.8974 | 1.3431 | 1.174 | 0.0116 | 1.359 | 0.013431 | 1.1624 | 1.3455 | 30.8649 | 10.8022 | 263.9325
38897.5861 | 1857 | 20 | 38897.5861 | 2185 | 26 | 1380.5 | 1564.5 | 113.37 | 1.221 | 133.3944 | 1.5873 | 1.1337 | 0.01221 | 1.3339 | 0.015873 | 1.1215 | 1.3181 | 35.6081 | 13.0097 | 333.4916
38897.5863 | 1838 | 24 | 38897.5863 | 2024 | 26 | 1391.5 | 1575.5 | 112.21 | 1.4652 | 123.5653 | 1.5873 | 1.1221 | 0.014652 | 1.2357 | 0.015873 | 1.1074 | 1.2198 | 36.2244 | 22.447 | 454.0078
38897.5864 | 2050 | 31 | 38897.5864 | 2278 | 33 | 1402.5 | 1586.5 | 125.1526 | 1.8926 | 139.072 | 2.0147 | 1.2515 | 0.018926 | 1.3907 | 0.020147 | 1.2326 | 1.3706 | 24.5968 | 8.4507 | 94.3558
38897.5865 | 1982 | 32 | 38897.5865 | 2094 | 40 | 1413.5 | 1597.5 | 121.0012 | 1.9536 | 127.8388 | 2.442 | 1.21 | 0.019536 | 1.2784 | 0.02442 | 1.1905 | 1.254 | 26.6223 | 19.0351 | 221.0675
38897.5866 | 1821 | 461 | 38897.5866 | 1643 | 478 | 1423.5 | 1607.5 | 111.1722 | 28.1441 | 100.3053 | 29.1819 | 1.1117 | 0.28144 | 1.0031 | 0.29182 | 0.83028 | 0.71123 | 52.0877 | 328.8828 | 29.0067
38897.5867 | 2032 | 77 | 38897.5868 | 2222 | 80 | 1434.5 | 1618.5 | 124.0537 | 4.7009 | 135.6532 | 4.884 | 1.2405 | 0.047009 | 1.3565 | 0.04884 | 1.1935 | 1.3077 | 31.8148 | 12.3975 | 49.7612
38897.5869 | 1859 | 68 | 38897.5869 | 2305 | 85 | 1445.5 | 1629.5 | 113.4921 | 4.1514 | 140.7204 | 5.1893 | 1.1349 | 0.041514 | 1.4072 | 0.051893 | 1.0934 | 1.3553 | 70.448 | 7.2108 | 52.3606
38897.587 | 2096 | 75 | 38897.587 | 2253 | 80 | 1456.5 | 1640.5 | 127.9609 | 4.5788 | 137.5458 | 4.884 | 1.2796 | 0.045788 | 1.3755 | 0.04884 | 1.2338 | 1.3266 | 27.1286 | 10.829 | 37.1789
38897.5871 | 1804 | 65 | 38897.5871 | 2284 | 78 | 1467.5 | 1651.5 | 110.1343 | 3.9683 | 139.4383 | 4.7619 | 1.1013 | 0.039683 | 1.3944 | 0.047619 | 1.0617 | 1.3468 | 68.6712 | 8.2383 | 68.7802
38897.5872 | 2127 | 78 | 38897.5873 | 2322 | 70 | 1477.5 | 1661.5 | 129.8535 | 4.7619 | 141.7582 | 4.2735 | 1.2985 | 0.047619 | 1.4176 | 0.042735 | 1.2509 | 1.3748 | 38.9233 | 6.485 | 19.6272

## C2-4
Penlight Test 1 |  |  | 2006-06-29 | 13:39 |  | Vs = |  | 149.6569 |  | R = | 100
XLPE | 3-C | Tray
475 C | 17.7 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38897.5681 | 1 | 0 | 38897.5681 | 1 | 0 | -176 | 8 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5682 | 1 | 0 | 38897.5682 | 1 | 0 | -165.5 | 18.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5684 | 1 | 0 | 38897.5684 | 1 | 0 | -154.5 | 29.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5685 | 1 | 0 | 38897.5685 | 1 | 0 | -143.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5686 | 2 | 0 | 38897.5686 | 1 | 0 | -132.5 | 51.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122469 | 245038 | 122468.9988
38897.5687 | 1 | 0 | 38897.5687 | 1 | 0 | -122.5 | 61.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5689 | 1 | 0 | 38897.5689 | 1 | 0 | -111.5 | 72.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.569 | 1 | 0 | 38897.569 | 1 | 0 | -100.5 | 83.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5691 | 1 | 0 | 38897.5691 | 2 | 0 | -89.5 | 94.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5692 | 1 | 0 | 38897.5692 | 1 | 0 | -78.5 | 105.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5694 | 1 | 0 | 38897.5694 | 1 | 0 | -68.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5695 | 1 | 0 | 38897.5695 | 1 | 0 | -57.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5696 | 1 | 0 | 38897.5696 | 2 | 0 | -46.5 | 137.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5697 | 1 | 0 | 38897.5697 | 1 | 0 | -35.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5699 | 1 | 0 | 38897.5699 | 1 | 0 | -24.5 | 159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.57 | 1 | 0 | 38897.57 | 1 | 0 | -14.5 | 169.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5701 | 1 | 0 | 38897.5701 | 1 | 0 | -3.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5702 | 1 | 1 | 38897.5702 | 1 | 0 | 7.5 | 191.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600436214.44 | 245038 | 244838.0816
38897.5704 | 2 | 0 | 38897.5704 | 1 | 0 | 18.5 | 202.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122469 | 245038 | 122468.9988
38897.5705 | 1 | 0 | 38897.5705 | 2 | 0 | 29.5 | 213.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5706 | 1 | 0 | 38897.5706 | 2 | 0 | 39.5 | 223.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5707 | 1 | 0 | 38897.5707 | 2 | 0 | 50.5 | 234.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5709 | 1 | 0 | 38897.5709 | 1 | 0 | 61.5 | 245.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.571 | 1 | 0 | 38897.571 | 1 | 0 | 72.5 | 256.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5711 | 1 | 0 | 38897.5711 | 1 | 0 | 83.5 | 267.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5712 | 1 | 0 | 38897.5712 | 1 | 0 | 94 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5714 | 1 | 0 | 38897.5714 | 1 | 0 | 104.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5715 | 1 | 0 | 38897.5715 | 1 | 0 | 115.5 | 299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5716 | 1 | 0 | 38897.5716 | 1 | 0 | 126.5 | 310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5717 | 1 | 1 | 38897.5717 | 1 | 0 | 137.5 | 321.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600436214.44 | 245038 | 244838.0816
38897.5719 | 1 | 0 | 38897.5719 | 1 | 0 | 147.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.572 | 1 | 0 | 38897.572 | 1 | 0 | 158.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5721 | 2 | 0 | 38897.5721 | 2 | 0 | 169.5 | 353.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122469 | 122469 | 122468.9988
38897.5722 | 1 | 0 | 38897.5722 | 1 | 0 | 180.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5724 | 1 | 0 | 38897.5724 | 1 | 0 | 191.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5725 | 1 | 0 | 38897.5725 | 1 | 0 | 201.5 | 385.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5726 | 2 | 0 | 38897.5726 | 1 | 0 | 212.5 | 396.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122469 | 245038 | 122468.9988
38897.5727 | 1 | 1 | 38897.5727 | 1 | 0 | 223.5 | 407.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600436214.44 | 245038 | 244838.0816
38897.5729 | 1 | 0 | 38897.5729 | 1 | 0 | 234.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.573 | 1 | 0 | 38897.573 | 2 | 0 | 245.5 | 429.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5731 | 1 | 0 | 38897.5731 | 1 | 0 | 255.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5732 | 1 | 0 | 38897.5732 | 1 | 0 | 266.5 | 450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5734 | 1 | 0 | 38897.5734 | 1 | 0 | 277.5 | 461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5735 | 1 | 0 | 38897.5735 | 1 | 0 | 288.5 | 472.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5736 | 1 | 0 | 38897.5736 | 1 | 0 | 299.5 | 483.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5737 | 1 | 0 | 38897.5737 | 2 | 0 | 309.5 | 493.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5739 | 1 | 0 | 38897.5739 | 1 | 0 | 320.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.574 | 1 | 0 | 38897.574 | 1 | 0 | 331.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5741 | 1 | 0 | 38897.5741 | 1 | 0 | 342.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
| 1 | 0 | 38897.5742 | 1 | 0 | 354 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5744 | 1 | 0 | 38897.5744 | 1 | 0 | 363.5 | 547.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5745 | 1 | 0 | 38897.5745 | 1 | 0 | 374.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5746 | 1 | 0 | 38897.5746 | 1 | 0 | 385.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5747 | 1 | 0 | 38897.5747 | 1 | 0 | 396.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5749 | 1 | 0 | 38897.5749 | 2 | 1 | 407.5 | 591.5 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.575 | 1 | 0 | 38897.575 | 1 | 0 | 417.5 | 601.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5751 | 1 | 0 | 38897.5751 | 1 | 0 | 428.5 | 612.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5752 | 1 | 1 | 38897.5752 | 1 | 0 | 439.5 | 623.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600436214.44 | 245038 | 244838.0816
38897.5754 | 1 | 0 | 38897.5754 | 1 | 0 | 450.5 | 634.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5755 | 1 | 0 | 38897.5755 | 1 | 0 | 461.5 | 645.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5756 | 1 | 0 | 38897.5756 | 1 | 0 | 471.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5757 | 1 | 0 | 38897.5757 | 2 | 0 | 482.5 | 666.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.5759 | 1 | 0 | 38897.5759 | 2 | 0 | 493.5 | 677.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38897.576 | 1 | 0 | 38897.576 | 1 | 0 | 504.5 | 688.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5761 | 1 | 0 | 38897.5761 | 1 | 0 | 515 | 699 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5762 | 1 | 0 | 38897.5762 | 1 | 0 | 525.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5764 | 1 | 0 | 38897.5764 | 1 | 0 | 536.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5765 | 1 | 0 | 38897.5765 | 1 | 0 | 547.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5766 | 1 | 0 | 38897.5766 | 1 | 0 | 558.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5767 | 1 | 0 | 38897.5767 | 1 | 0 | 569.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5769 | 1 | 0 | 38897.5769 | 1 | 0 | 579.5 | 763.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.577 | 1 | 0 | 38897.577 | 1 | 0 | 590.5 | 774.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5771 | 1 | 0 | 38897.5771 | 1 | 0 | 601.5 | 785.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5772 | 1 | 0 | 38897.5772 | 1 | 0 | 612.5 | 796.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5774 | 1 | 0 | 38897.5774 | 1 | 0 | 623.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5775 | 1 | 0 | 38897.5775 | 1 | 0 | 633.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5776 | 1 | 0 | 38897.5776 | 1 | 0 | 644.5 | 828.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5777 | 1 | 0 | 38897.5777 | 1 | 0 | 655.5 | 839.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5779 | 1 | 0 | 38897.5779 | 1 | 0 | 666.5 | 850.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.578 | 1 | 0 | 38897.578 | 1 | 0 | 677 | 861 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5781 | 1 | 0 | 38897.5781 | 1 | 0 | 687.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5782 | 1 | 0 | 38897.5782 | 1 | 0 | 698.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5784 | 1 | 0 | 38897.5784 | 1 | 0 | 709.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5785 | 1 | 0 | 38897.5785 | 1 | 0 | 720.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5786 | 1 | 0 | 38897.5786 | 1 | 0 | 731 | 915 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5787 | 1 | 0 | 38897.5787 | 1 | 0 | 741.5 | 925.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5789 | 1 | 0 | 38897.5789 | 1 | 0 | 752.5 | 936.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.579 | 1 | 0 | 38897.579 | 1 | 0 | 763.5 | 947.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5791 | 1 | 0 | 38897.5791 | 1 | 0 | 774.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38897.5792 | 1 | 5 | 38897.5792 | 2 | 3 | 785 | 969 | 0.06105 | 0.30525 | 0.1221 | 0.18315 | 0.0006105 | 0.0030525 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 61290.6255 | 246142.7983 | 48887.7385
38897.5794 | 2 | 11 | 38897.5794 | 14 | 5 | 795.5 | 979.5 | 0.1221 | 0.67155 | 0.8547 | 0.30525 | 0.001221 | 0.0067155 | 0.008547 | 0.0030525 | 0.0054945 | 0.0054945 | 27338.4623 | 27137.1465 | 22085.7054
38897.5795 | 68 | 53 | 38897.5795 | 143 | 40 | 806.5 | 990.5 | 4.1514 | 3.2357 | 8.7302 | 2.442 | 0.041514 | 0.032357 | 0.087302 | 0.02442 | 0.0091575 | 0.062882 | 18855.8415 | 2245.771 | 4209.5021
38897.5796 | 153 | 112 | 38897.5796 | 286 | 138 | 817.5 | 1001.5 | 9.3407 | 6.8376 | 17.4603 | 8.4249 | 0.093407 | 0.068376 | 0.1746 | 0.084249 | 0.025031 | 0.090354 | 6871.3232 | 1483.2218 | 1828.8242
38897.5797 | 255 | 219 | 38897.5797 | 392 | 224 | 828.5 | 1012.5 | 15.5678 | 13.37 | 23.9316 | 13.6752 | 0.15568 | 0.1337 | 0.23932 | 0.13675 | 0.021978 | 0.10256 | 11980.3015 | 1239.6176 | 835.5124
38897.5799 | 404 | 373 | 38897.5799 | 443 | 322 | 839 | 1023 | 24.6642 | 22.7717 | 27.0452 | 19.6581 | 0.24664 | 0.22772 | 0.27045 | 0.19658 | 0.018926 | 0.073871 | 23307.4229 | 1678.9883 | 423.6623
38897.58 | 532 | 471 | 38897.58 | 507 | 333 | 849.5 | 1033.5 | 32.4786 | 28.7546 | 30.9524 | 20.3297 | 0.32479 | 0.28755 | 0.30952 | 0.2033 | 0.037241 | 0.10623 | 9754.027 | 1139.8237 | 282.7088
38897.5801 | 505 | 403 | 38897.5801 | 517 | 362 | 860.5 | 1044.5 | 30.8303 | 24.6032 | 31.5629 | 22.1001 | 0.3083 | 0.24603 | 0.31563 | 0.221 | 0.062271 | 0.094628 | 2683.9998 | 1366.9306 | 356.8656
38897.5802 | 535 | 427 | 38897.5802 | 673 | 461 | 871.5 | 1055.5 | 32.6618 | 26.0684 | 41.0867 | 28.1441 | 0.32662 | 0.26068 | 0.41087 | 0.28144 | 0.065934 | 0.12943 | 3162.4699 | 900.7977 | 313.9486
38897.5804 | 1254 | 825 | 38897.5804 | 1125 | 1010 | 882.5 | 1066.5 | 76.5568 | 50.3663 | 68.6813 | 61.6606 | 0.76557 | 0.50366 | 0.68681 | 0.61661 | 0.2619 | 0.070208 | 159.2204 | 255.3969 | 32.4365
38897.5805 | 1104 | 973 | 38897.5805 | 1015 | 820 | 893 | 1077 | 67.3993 | 59.4017 | 61.9658 | 50.0611 | 0.67399 | 0.59402 | 0.61966 | 0.50061 | 0.079976 | 0.11905 | 72487.5852 | 753.4387 | 33.9684
38897.5806 | 1054 | 843 | 38897.5806 | 1106 | 959 | 903.5 | 1087.5 | 64.3468 | 51.4652 | 67.5214 | 58.547 | 0.64347 | 0.51465 | 0.67521 | 0.58547 | 0.12882 | 0.089744 | 669.9232 | 34951.6972 | 65.5751
38897.5807 | 1110 | 900 | 38897.5807 | 1228 | 993 | 914.5 | 1098.5 | 67.7656 | 54.9451 | 74.9695 | 60.6227 | 0.67766 | 0.54945 | 0.74969 | 0.60623 | 0.12821 | 0.14347 | 1645.7185 | 700.4287 | 42.9152
38897.5809 | 1118 | 847 | 38897.5809 | 1220 | 926 | 925.5 | 1109.5 | 68.254 | 51.7094 | 74.4811 | 56.5324 | 0.68254 | 0.51709 | 0.74481 | 0.56532 | 0.16545 | 0.17949 | 1012.6534 | 607.9176 | 49.3122
38897.581 | 1203 | 731 | 38897.581 | 1361 | 782 | 936.5 | 1120.5 | 73.4432 | 44.6276 | 83.0891 | 47.7411 | 0.73443 | 0.44628 | 0.83089 | 0.47741 | 0.28816 | 0.35348 | 863.7605 | 223.2255 | 48.8799
| 1399 | 553 | 38897.5811 | 1957 | 461 | 947 | 1131 | 85.409 | 33.7607 | 119.475 | 28.1441 | 0.85409 | 0.33761 | 1.1947 | 0.28144 | 0.51648 | 0.91331 | 64.8692 | 71.2344 | 37.5668
38897.5812 | 1594 | 375 | 38897.5812 | 1772 | 473 | 957.5 | 1141.5 | 97.3138 | 22.8938 | 108.1807 | 28.8767 | 0.97314 | 0.22894 | 1.0818 | 0.28877 | 0.7442 | 0.79304 | 118.7875 | 75.4188 | 55.3046
38897.5814 | 1491 | 499 | 38897.5814 | 1692 | 666 | 968.5 | 1152.5 | 91.0256 | 30.464 | 103.2967 | 40.6593 | 0.91026 | 0.30464 | 1.033 | 0.40659 | 0.60562 | 0.62637 | 164.4875 | 122.2625 | 50.8611
38897.5815 | 1626 | 545 | 38897.5815 | 1768 | 625 | 979.5 | 1163.5 | 99.2674 | 33.2723 | 107.9365 | 38.1563 | 0.99267 | 0.33272 | 1.0794 | 0.38156 | 0.65995 | 0.6978 | 192.9409 | 83.434 | 23.3999
38897.5816 | 1479 | 488 | 38897.5816 | 1378 | 543 | 990.5 | 1174.5 | 90.293 | 29.7924 | 84.127 | 33.1502 | 0.90293 | 0.29792 | 0.84127 | 0.3315 | 0.60501 | 0.50977 | 118.6684 | 284.3974 | 73.4364
38897.5817 | 1319 | 565 | 38897.5817 | 1498 | 666 | 1001.5 | 1185.5 | 80.525 | 34.4933 | 91.453 | 40.6593 | 0.80525 | 0.34493 | 0.91453 | 0.40659 | 0.46032 | 0.50794 | 282.712 | 159.8492 | 61.7753
38897.5819 | 1811 | 142 | 38897.5819 | 2180 | 48 | 1011.5 | 1195.5 | 110.5617 | 8.6691 | 133.0891 | 2.9304 | 1.1056 | 0.086691 | 1.3309 | 0.029304 | 1.0189 | 1.3016 | 111.1733 | 12.992 | 40.3553
38897.582 | 2275 | 20 | 38897.582 | 2055 | 17 | 1022.5 | 1206.5 | 138.8889 | 1.221 | 125.4579 | 1.0379 | 1.3889 | 0.01221 | 1.2546 | 0.010379 | 1.3767 | 1.2442 | 8.1556 | 21.6654 | 139.2357
38897.5821 | 2289 | 20 | 38897.5821 | 1956 | 16 | 1033.5 | 1217.5 | 139.7436 | 1.221 | 119.4139 | 0.9768 | 1.3974 | 0.01221 | 1.1941 | 0.009768 | 1.3852 | 1.1844 | 7.3828 | 28.7463 | 158.9522
38897.5822 | 2087 | 15 | 38897.5822 | 1989 | 13 | 1044.5 | 1228.5 | 127.4115 | 0.91575 | 121.4286 | 0.79365 | 1.2741 | 0.0091575 | 1.2143 | 0.0079365 | 1.265 | 1.2063 | 18.1263 | 24.2811 | 455.0611
38897.5824 | 2431 | 12 | 38897.5824 | 1887 | 9 | 1055 | 1239 | 148.4127 | 0.7326 | 115.2015 | 0.54945 | 1.4841 | 0.007326 | 1.152 | 0.0054945 | 1.4768 | 1.1465 | 0.84859 | 69.0439 | 28.5226
38897.5825 | 2339 | 9 | 38897.5825 | 1992 | 6 | 1065.5 | 1249.5 | 142.7961 | 0.54945 | 121.6117 | 0.3663 | 1.428 | 0.0054945 | 1.2161 | 0.003663 | 1.4225 | 1.2125 | 4.9 | 24.6508 | 227.159
38897.5826 | 2385 | 8 | 38897.5826 | 1881 | 5 | 1076.5 | 1260.5 | 145.6044 | 0.4884 | 114.8352 | 0.30525 | 1.456 | 0.004884 | 1.1484 | 0.0030525 | 1.4512 | 1.1453 | 2.8209 | 33.5765 | 183.4337
38897.5827 | 2022 | 5 | 38897.5827 | 2370 | 8 | 1087.5 | 1271.5 | 123.4432 | 0.30525 | 144.6886 | 0.4884 | 1.2344 | 0.0030525 | 1.4469 | 0.004884 | 1.2314 | 1.442 | 22.9122 | 3.4971 | 286.7889
38897.5829 | 2361 | 8 | 38897.5829 | 2278 | 7 | 1098.5 | 1282.5 | 144.1392 | 0.4884 | 139.072 | 0.42735 | 1.4414 | 0.004884 | 1.3907 | 0.0042735 | 1.4365 | 1.3864 | 4.0057 | 8.271 | 78.664
38897.583 | 2119 | 6 | 38897.583 | 1937 | 5 | 1109 | 1293 | 129.3651 | 0.3663 | 118.254 | 0.30525 | 1.2937 | 0.003663 | 1.1825 | 0.0030525 | 1.29 | 1.1795 | 15.897 | 27.0648 | 1158.65
38897.5831 | 2084 | 7 | 38897.5831 | 2236 | 7 | 1119.5 | 1303.5 | 127.2283 | 0.42735 | 136.5079 | 0.42735 | 1.2723 | 0.0042735 | 1.3651 | 0.0042735 | 1.268 | 1.3608 | 18.3159 | 9.8312 | 460.8326
38897.5832 | 2020 | 5 | 38897.5832 | 2435 | 8 | 1130.5 | 1314.5 | 123.3211 | 0.30525 | 148.6569 | 0.4884 | 1.2332 | 0.0030525 | 1.4866 | 0.004884 | 1.2302 | 1.4817 | 33.6644 | 0.68158 | 57.729
38897.5834 | 2429 | 8 | 38897.5834 | 2029 | 5 | 1141.5 | 1325.5 | 148.2906 | 0.4884 | 123.8706 | 0.30525 | 1.4829 | 0.004884 | 1.2387 | 0.0030525 | 1.478 | 1.2357 | 0.93531 | 28.3587 | 39.7128
38897.5835 | 2423 | 6 | 38897.5835 | 1946 | 6 | 1152.5 | 1336.5 | 147.9243 | 0.3663 | 118.8034 | 0.3663 | 1.4792 | 0.003663 | 1.188 | 0.003663 | 1.4756 | 1.1844 | 1.1825 | 35.2771 | 97.2696
38897.5836 | 1907 | 5 | 38897.5836 | 2274 | 7 | 1163 | 1347 | 116.4225 | 0.30525 | 138.8278 | 0.42735 | 1.1642 | 0.0030525 | 1.3883 | 0.0042735 | 1.1612 | 1.384 | 29.6058 | 7.9069 | 790.4639
38897.5837 | 1880 | 6 | 38897.5837 | 1895 | 5 | 1173.5 | 1357.5 | 114.7741 | 0.3663 | 115.6899 | 0.30525 | 1.1477 | 0.003663 | 1.1569 | 0.0030525 | 1.1441 | 1.1538 | 30.8222 | 29.693 | 2157.3778
38897.5839 | 1874 | 7 | 38897.5839 | 2130 | 8 | 1184.5 | 1368.5 | 114.4078 | 0.42735 | 130.0366 | 0.4884 | 1.1441 | 0.0042735 | 1.3004 | 0.004884 | 1.1398 | 1.2955 | 31.701 | 15.3274 | 1082.9363
38897.584 | 1867 | 7 | 38897.584 | 2243 | 8 | 1195.5 | 1379.5 | 113.9805 | 0.42735 | 136.9353 | 0.4884 | 1.1398 | 0.0042735 | 1.3694 | 0.004884 | 1.1355 | 1.3645 | 32.7248 | 9.4266 | 710.5518
38897.5841 | 2190 | 7 | 38897.5841 | 1877 | 6 | 1206.5 | 1390.5 | 133.6996 | 0.42735 | 114.591 | 0.3663 | 1.337 | 0.0042735 | 1.1459 | 0.003663 | 1.3327 | 1.1422 | 12.0964 | 31.5351 | 871.2395
38897.5842 | 2085 | 7 | 38897.5842 | 2276 | 10 | 1217 | 1401 | 127.2894 | 0.42735 | 138.9499 | 0.6105 | 1.2729 | 0.0042735 | 1.3895 | 0.006105 | 1.2686 | 1.3834 | 18.4136 | 7.9297 | 377.1988
38897.5844 | 2011 | 7 | 38897.5844 | 2221 | 8 | 1227.5 | 1411.5 | 122.7717 | 0.42735 | 135.5922 | 0.4884 | 1.2277 | 0.0042735 | 1.3559 | 0.004884 | 1.2234 | 1.351 | 22.7254 | 10.5786 | 592.2801
38897.5845 | 1872 | 8 | 38897.5845 | 2049 | 9 | 1238.5 | 1422.5 | 114.2857 | 0.4884 | 125.0916 | 0.54945 | 1.1429 | 0.004884 | 1.2509 | 0.0054945 | 1.138 | 1.2454 | 31.7642 | 20.0023 | 1190.4903
38897.5846 | 2412 | 11 | 38897.5846 | 2170 | 11 | 1249.5 | 1433.5 | 147.2527 | 0.67155 | 132.4786 | 0.67155 | 1.4725 | 0.0067155 | 1.3248 | 0.0067155 | 1.4658 | 1.3181 | 1.6813 | 18.6993 | 40.6441
38897.5847 | 2024 | 10 | 38897.5847 | 2146 | 11 | 1260.5 | 1444.5 | 123.5653 | 0.6105 | 131.0134 | 0.67155 | 1.2357 | 0.006105 | 1.3101 | 0.0067155 | 1.2295 | 1.3034 | 21.9651 | 14.6471 | 533.2363
38897.5849 | 1907 | 9 | 38897.5849 | 2232 | 10 | 1271 | 1455 | 116.4225 | 0.54945 | 136.2637 | 0.6105 | 1.1642 | 0.0054945 | 1.3626 | 0.006105 | 1.1587 | 1.3565 | 30.1061 | 10.0229 | 541.9143
38897.585 | 2320 | 11 | 38897.585 | 2292 | 9 | 1281.5 | 1465.5 | 141.6361 | 0.67155 | 139.9267 | 0.54945 | 1.4164 | 0.0067155 | 1.3993 | 0.0054945 | 1.4096 | 1.3938 | 6.0778 | 7.4654 | 76.0231
38897.5851 | 2168 | 12 | 38897.5851 | 2394 | 15 | 1292.5 | 1476.5 | 132.3565 | 0.7326 | 146.1538 | 0.91575 | 1.3236 | 0.007326 | 1.4615 | 0.0091575 | 1.3162 | 1.4524 | 16.8976 | 2.5054 | 55.2753
38897.5852 | 2282 | 14 | 38897.5852 | 1947 | 10 | 1303.5 | 1487.5 | 139.3162 | 0.8547 | 118.8645 | 0.6105 | 1.3932 | 0.008547 | 1.1886 | 0.006105 | 1.3846 | 1.1825 | 7.6371 | 27.9271 | 242.2871
38897.5854 | 1936 | 11 | 38897.5854 | 2300 | 14 | 1314.5 | 1498.5 | 118.1929 | 0.67155 | 140.4151 | 0.8547 | 1.1819 | 0.0067155 | 1.4042 | 0.008547 | 1.1752 | 1.3956 | 29.2436 | 6.7637 | 290.4862
38897.5855 | 1977 | 11 | 38897.5855 | 2208 | 13 | 1325 | 1509 | 120.696 | 0.67155 | 134.7985 | 0.79365 | 1.207 | 0.0067155 | 1.348 | 0.0079365 | 1.2002 | 1.34 | 25.38 | 11.3529 | 429.4852
38897.5856 | 1893 | 12 | 38897.5856 | 2252 | 14 | 1335.5 | 1519.5 | 115.5678 | 0.7326 | 137.4847 | 0.8547 | 1.1557 | 0.007326 | 1.3748 | 0.008547 | 1.1484 | 1.3663 | 31.9267 | 9.0869 | 379.2769
38897.5857 | 2335 | 16 | 38897.5857 | 1993 | 13 | 1346.5 | 1530.5 | 142.5519 | 0.9768 | 121.6728 | 0.79365 | 1.4255 | 0.009768 | 1.2167 | 0.0079365 | 1.4158 | 1.2088 | 5.1525 | 26.5313 | 131.549
38897.5859 | 2200 | 18 | 38897.5859 | 2391 | 17 | 1357.5 | 1541.5 | 134.3101 | 1.0989 | 145.9707 | 1.0379 | 1.3431 | 0.010989 | 1.4597 | 0.010379 | 1.3321 | 1.4493 | 16.7073 | 2.6573 | 33.5613
38897.586 | 2257 | 21 | 38897.586 | 2400 | 22 | 1368.5 | 1552.5 | 137.79 | 1.2821 | 146.5201 | 1.3431 | 1.3779 | 0.012821 | 1.4652 | 0.013431 | 1.3651 | 1.4518 | 14.666 | 2.3061 | 18.6105
38897.5861 | 1855 | 18 | 38897.5861 | 2340 | 24 | 1379 | 1563 | 113.2479 | 1.0989 | 142.8571 | 1.4652 | 1.1325 | 0.010989 | 1.4286 | 0.014652 | 1.1215 | 1.4139 | 40.507 | 4.9354 | 151.1271
38897.5862 | 1868 | 22 | 38897.5862 | 2393 | 28 | 1389.5 | 1573.5 | 114.0415 | 1.3431 | 146.0928 | 1.7094 | 1.1404 | 0.013431 | 1.4609 | 0.017094 | 1.127 | 1.4438 | 59.9965 | 2.5182 | 62.679
38897.5864 | 2012 | 28 | 38897.5864 | 2308 | 31 | 1400.5 | 1584.5 | 122.8327 | 1.7094 | 140.9035 | 1.8926 | 1.2283 | 0.017094 | 1.409 | 0.018926 | 1.2112 | 1.3901 | 28.1502 | 6.6169 | 91.1829
38897.5865 | 2277 | 35 | 38897.5865 | 1918 | 28 | 1411.5 | 1595.5 | 139.011 | 2.1368 | 117.094 | 1.7094 | 1.3901 | 0.021368 | 1.1709 | 0.017094 | 1.3687 | 1.1538 | 8.1466 | 34.494 | 102.1347
38897.5866 | 1867 | 335 | 38897.5866 | 2008 | 408 | 1422.5 | 1606.5 | 113.9805 | 20.4518 | 122.5885 | 24.9084 | 1.1398 | 0.20452 | 1.2259 | 0.24908 | 0.93529 | 0.9768 | 85.4558 | 39.4972 | 21.0774
38897.5867 | 2277 | 100 | 38897.5867 | 2150 | 98 | 1432.5 | 1616.5 | 139.011 | 6.105 | 131.2576 | 5.9829 | 1.3901 | 0.06105 | 1.3126 | 0.059829 | 1.3291 | 1.2527 | 9.482 | 29.5917 | 16.9844
38897.5869 | 2129 | 75 | 38897.5869 | 2209 | 82 | 1443.5 | 1627.5 | 129.9756 | 4.5788 | 134.8596 | 5.0061 | 1.2998 | 0.045788 | 1.3486 | 0.050061 | 1.254 | 1.2985 | 21.278 | 13.9169 | 40.2956
38897.587 | 1963 | 69 | 38897.587 | 1813 | 65 | 1454.5 | 1638.5 | 119.8413 | 4.2125 | 110.6838 | 3.9683 | 1.1984 | 0.042125 | 1.1068 | 0.039683 | 1.1563 | 1.0672 | 28.2308 | 42.0608 | 179.9542
38897.5871 | 2221 | 76 | 38897.5871 | 2292 | 85 | 1465.5 | 1649.5 | 135.5922 | 4.6398 | 139.9267 | 5.1893 | 1.3559 | 0.046398 | 1.3993 | 0.051893 | 1.3095 | 1.3474 | 17.3758 | 9.2781 | 17.2465
38897.5872 | 2315 | 85 | 38897.5872 | 1894 | 67 | 1476.5 | 1660.5 | 141.3309 | 5.1893 | 115.6288 | 4.0904 | 1.4133 | 0.051893 | 1.1563 | 0.040904 | 1.3614 | 1.1154 | 6.4653 | 70.4923 | 24.9926

## C2-3
Penlight Test 1 |  |  | 2006-06-29 | 13:39 |  | Vs = |  | 148.8022 |  | R = | 100
XLPE | 3-C | Tray
475 C | 17.7 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38897.5681 | 1 | 0 | 38897.5681 | 1 | 0 | -177.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5682 | 1 | 0 | 38897.5682 | 1 | 0 | -167 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5683 | 1 | 0 | 38897.5683 | 1 | 0 | -156.5 | 27.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5685 | 1 | 0 | 38897.5685 | 1 | 0 | -145.5 | 38.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5686 | 1 | 0 | 38897.5686 | 1 | 0 | -134.5 | 49.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5687 | 1 | 0 | 38897.5687 | 1 | 0 | -123.5 | 60.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5688 | 1 | 0 | 38897.5688 | 1 | 0 | -113.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.569 | 1 | 0 | 38897.569 | 1 | 0 | -102.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5691 | 1 | 0 | 38897.5691 | 1 | 0 | -91.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5692 | 1 | 0 | 38897.5692 | 1 | 0 | -80.5 | 103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5693 | 1 | 0 | 38897.5694 | 1 | 0 | -69.5 | 114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5695 | 1 | 0 | 38897.5695 | 1 | 0 | -59 | 125 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5696 | 1 | 0 | 38897.5696 | 1 | 0 | -48.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5697 | 1 | 0 | 38897.5697 | 1 | 0 | -37.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5698 | 1 | 0 | 38897.5698 | 1 | 0 | -26.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.57 | 1 | 0 | 38897.57 | 1 | 0 | -15.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5701 | 2 | 0 | 38897.5701 | 1 | 0 | -5.5 | 178.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121769 | 243638 | 121768.9988
38897.5702 | 1 | 0 | 38897.5702 | 1 | 0 | 5.5 | 189.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5703 | 2 | 0 | 38897.5703 | 1 | 0 | 16.5 | 200.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121769 | 243638 | 121768.9988
38897.5705 | 1 | 0 | 38897.5705 | 1 | 0 | 27.5 | 211.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5706 | 1 | 0 | 38897.5706 | 1 | 0 | 38.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5707 | 1 | 0 | 38897.5707 | 1 | 0 | 49 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5708 | 1 | 0 | 38897.5708 | 1 | 0 | 59.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.571 | 1 | 0 | 38897.571 | 1 | 0 | 70.5 | 254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5711 | 1 | 0 | 38897.5711 | 1 | 0 | 81.5 | 265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5712 | 1 | 0 | 38897.5712 | 1 | 0 | 92.5 | 276.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5713 | 1 | 0 | 38897.5713 | 1 | 0 | 103 | 287 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5715 | 1 | 0 | 38897.5715 | 1 | 0 | 113.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5716 | 1 | 0 | 38897.5716 | 1 | 0 | 124.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5717 | 1 | 0 | 38897.5717 | 1 | 0 | 135.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5718 | 1 | 0 | 38897.5719 | 1 | 0 | 146.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.572 | 1 | 0 | 38897.572 | 1 | 0 | 156.5 | 340.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5721 | 2 | 0 | 38897.5721 | 2 | 0 | 167.5 | 351.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121769 | 121769 | 121768.9988
38897.5722 | 1 | 0 | 38897.5722 | 1 | 0 | 178.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5723 | 1 | 1 | 38897.5723 | 1 | 0 | 189.5 | 373.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 593594750.44 | 243638 | 243438.0821
38897.5725 | 1 | 0 | 38897.5725 | 1 | 0 | 200.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5726 | 1 | 0 | 38897.5726 | 1 | 0 | 211 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5727 | 1 | 0 | 38897.5727 | 1 | 0 | 221.5 | 405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5728 | 1 | 0 | 38897.5728 | 1 | 0 | 232.5 | 416.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.573 | 2 | 0 | 38897.573 | 2 | 0 | 243.5 | 427.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121769 | 121769 | 121768.9988
38897.5731 | 1 | 0 | 38897.5731 | 1 | 0 | 254.5 | 438.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5732 | 2 | 0 | 38897.5732 | 1 | 0 | 264.5 | 448.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121769 | 243638 | 121768.9988
38897.5733 | 1 | 0 | 38897.5733 | 1 | 0 | 275.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5735 | 1 | 0 | 38897.5735 | 1 | 0 | 286.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5736 | 1 | 0 | 38897.5736 | 1 | 0 | 297.5 | 481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5737 | 1 | 0 | 38897.5737 | 1 | 0 | 308.5 | 492.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5738 | 1 | 0 | 38897.5738 | 1 | 0 | 319 | 503 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.574 | 1 | 0 | 38897.574 | 1 | 0 | 329.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5741 | 1 | 0 | 38897.5741 | 1 | 0 | 340.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5742 | 1 | 0 | 38897.5742 | 1 | 0 | 351.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5743 | 2 | 0 | 38897.5744 | 1 | 0 | 362.5 | 546.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121769 | 243638 | 121768.9988
38897.5745 | 1 | 0 | 38897.5745 | 1 | 0 | 372.5 | 556.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5746 | 1 | 0 | 38897.5746 | 1 | 0 | 383.5 | 567.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5747 | 1 | 0 | 38897.5747 | 1 | 0 | 394.5 | 578.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5748 | 1 | 0 | 38897.5748 | 1 | 0 | 405.5 | 589.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.575 | 1 | 0 | 38897.575 | 1 | 0 | 416.5 | 600.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5751 | 1 | 0 | 38897.5751 | 1 | 0 | 426.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5752 | 1 | 0 | 38897.5752 | 1 | 0 | 437.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5753 | 1 | 0 | 38897.5753 | 1 | 0 | 448.5 | 632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5755 | 1 | 0 | 38897.5755 | 1 | 0 | 459.5 | 643.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5756 | 1 | 0 | 38897.5756 | 1 | 0 | 470.5 | 654.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5757 | 1 | 0 | 38897.5757 | 1 | 0 | 480.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5758 | 1 | 0 | 38897.5758 | 1 | 0 | 491.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.576 | 1 | 0 | 38897.576 | 1 | 0 | 502.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5761 | 1 | 0 | 38897.5761 | 2 | 0 | 513.5 | 697.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 243638 | 121769 | 243637.9994
38897.5762 | 1 | 0 | 38897.5762 | 1 | 0 | 524 | 708 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5763 | 1 | 0 | 38897.5763 | 1 | 0 | 534.5 | 718.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5765 | 1 | 0 | 38897.5765 | 1 | 0 | 545.5 | 729.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5766 | 1 | 0 | 38897.5766 | 1 | 0 | 556.5 | 740.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5767 | 1 | 0 | 38897.5767 | 1 | 0 | 567.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5768 | 1 | 0 | 38897.5768 | 1 | 0 | 578 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.577 | 1 | 0 | 38897.577 | 1 | 0 | 588.5 | 772.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5771 | 1 | 0 | 38897.5771 | 1 | 0 | 599.5 | 783.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5772 | 1 | 0 | 38897.5772 | 1 | 0 | 610.5 | 794.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5773 | 1 | 0 | 38897.5773 | 1 | 0 | 621.5 | 805.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5775 | 1 | 0 | 38897.5775 | 1 | 0 | 632.5 | 816.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5776 | 1 | 0 | 38897.5776 | 1 | 0 | 642.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5777 | 1 | 0 | 38897.5777 | 1 | 0 | 653.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5778 | 1 | 0 | 38897.5778 | 1 | 0 | 664.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.578 | 1 | 0 | 38897.578 | 1 | 0 | 675.5 | 859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5781 | 1 | 0 | 38897.5781 | 1 | 0 | 686 | 870 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5782 | 1 | 0 | 38897.5782 | 1 | 0 | 696.5 | 880.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5783 | 1 | 0 | 38897.5783 | 1 | 0 | 707.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5785 | 1 | 0 | 38897.5785 | 1 | 0 | 718.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5786 | 1 | 0 | 38897.5786 | 1 | 0 | 729.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5787 | 1 | 0 | 38897.5787 | 1 | 0 | 740 | 924 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5788 | 1 | 0 | 38897.5788 | 1 | 0 | 750.5 | 934.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.579 | 1 | 0 | 38897.579 | 1 | 0 | 761.5 | 945.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243638 | 243638 | 243637.9994
38897.5791 | 1 | 1 | 38897.5791 | 1 | 0 | 772.5 | 956.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 593594750.44 | 243638 | 243438.0821
38897.5792 | 2 | 22 | 38897.5792 | 1 | 13 | 783.5 | 967.5 | 0.1221 | 1.3431 | 0.06105 | 0.79365 | 0.001221 | 0.013431 | 0.0006105 | 0.0079365 | 0.01221 | 0.007326 | 12242.6422 | 20484.4304 | 10916.6168
38897.5793 | 2 | 23 | 38897.5794 | 2 | 17 | 794.5 | 978.5 | 0.1221 | 1.4042 | 0.1221 | 1.0379 | 0.001221 | 0.014042 | 0.001221 | 0.010379 | 0.012821 | 0.0091575 | 11675.0405 | 16395.0183 | 10425.0222
38897.5795 | 3 | 26 | 38897.5795 | 8 | 18 | 804.5 | 988.5 | 0.18315 | 1.5873 | 0.4884 | 1.0989 | 0.0018315 | 0.015873 | 0.004884 | 0.010989 | 0.014042 | 0.006105 | 10632.9001 | 24712.1417 | 9225.6675
38897.5796 | 55 | 16 | 38897.5796 | 68 | 18 | 815.5 | 999.5 | 3.3578 | 0.9768 | 4.1514 | 1.0989 | 0.033578 | 0.009768 | 0.041514 | 0.010989 | 0.02381 | 0.030525 | 6161.6997 | 4766.6091 | 14485.9699
38897.5797 | 202 | 134 | 38897.5797 | 342 | 206 | 826.5 | 1010.5 | 12.3321 | 8.1807 | 20.8791 | 12.5763 | 0.12332 | 0.081807 | 0.20879 | 0.12576 | 0.041514 | 0.083028 | 3747.2216 | 1605.6233 | 1476.2514
38897.5798 | 413 | 349 | 38897.5798 | 469 | 348 | 837.5 | 1021.5 | 25.2137 | 21.3065 | 28.6325 | 21.2454 | 0.25214 | 0.21306 | 0.28632 | 0.21245 | 0.039072 | 0.073871 | 4613.0397 | 1734.9255 | 453.8897
38897.58 | 494 | 406 | 38897.58 | 457 | 290 | 848 | 1032 | 30.1587 | 24.7863 | 27.8999 | 17.7045 | 0.30159 | 0.24786 | 0.279 | 0.17705 | 0.053724 | 0.10195 | 3504.1236 | 1247.6875 | 350.5676
38897.5801 | 426 | 387 | 38897.5801 | 532 | 350 | 858.5 | 1042.5 | 26.0073 | 23.6264 | 32.4786 | 21.3675 | 0.26007 | 0.23626 | 0.32479 | 0.21368 | 0.02381 | 0.11111 | 95386.0918 | 1049.027 | 383.2067
38897.5802 | 658 | 542 | 38897.5802 | 748 | 547 | 869.5 | 1053.5 | 40.1709 | 33.0891 | 45.6654 | 33.3944 | 0.40171 | 0.33089 | 0.45665 | 0.33394 | 0.070818 | 0.12271 | 3113.5207 | 920.987 | 205.9383
38897.5803 | 625 | 506 | 38897.5803 | 1075 | 888 | 880.5 | 1064.5 | 38.1563 | 30.8913 | 65.6288 | 54.2125 | 0.38156 | 0.30891 | 0.65629 | 0.54212 | 0.07265 | 0.11416 | 2992.2752 | 865.9731 | 231.4506
38897.5805 | 1296 | 1094 | 38897.5805 | 1036 | 839 | 891.5 | 1075.5 | 79.1209 | 66.7888 | 63.2479 | 51.221 | 0.79121 | 0.66789 | 0.63248 | 0.51221 | 0.12332 | 0.12027 | 1008.9305 | 1230.9799 | 4.0055
38897.5806 | 1180 | 1038 | 38897.5806 | 1242 | 1016 | 902 | 1086 | 72.0391 | 63.37 | 75.8242 | 62.0269 | 0.72039 | 0.6337 | 0.75824 | 0.62027 | 0.086691 | 0.13797 | 691.5653 | 2606.9584 | 20.3541
38897.5807 | 1083 | 833 | 38897.5807 | 1213 | 1018 | 912.5 | 1096.5 | 66.1172 | 50.8547 | 74.0537 | 62.149 | 0.66117 | 0.50855 | 0.74054 | 0.62149 | 0.15263 | 0.11905 | 564.0274 | 8436.832 | 61.8575
38897.5808 | 1034 | 664 | 38897.5808 | 1006 | 813 | 923.5 | 1107.5 | 63.1258 | 40.5372 | 61.4164 | 49.6337 | 0.63126 | 0.40537 | 0.61416 | 0.49634 | 0.22589 | 0.11783 | 365.9003 | 4903.3805 | 109.1269
38897.581 | 1309 | 936 | 38897.581 | 1121 | 712 | 934.5 | 1118.5 | 79.9145 | 57.1429 | 68.4371 | 43.4676 | 0.79915 | 0.57143 | 0.68437 | 0.43468 | 0.22772 | 0.24969 | 756.9804 | 417.9753 | 16.5854
38897.5811 | 1303 | 783 | 38897.5811 | 1415 | 829 | 945.5 | 1129.5 | 79.5482 | 47.8022 | 86.3858 | 50.6105 | 0.79548 | 0.47802 | 0.86386 | 0.50611 | 0.31746 | 0.35775 | 701.4605 | 218.5423 | 30.7882
38897.5812 | 1866 | 480 | 38897.5812 | 1914 | 437 | 956 | 1140 | 113.9194 | 29.304 | 116.8498 | 26.6789 | 1.1392 | 0.29304 | 1.1685 | 0.26679 | 0.84615 | 0.90171 | 542.965 | 37.4776 | 5.1898
38897.5813 | 1703 | 596 | 38897.5813 | 1475 | 429 | 966.5 | 1150.5 | 103.9683 | 36.3858 | 90.0488 | 26.1905 | 1.0397 | 0.36386 | 0.90049 | 0.2619 | 0.67582 | 0.63858 | 102.0659 | 153.8126 | 14.0704
38897.5815 | 1741 | 576 | 38897.5815 | 1472 | 511 | 977.5 | 1161.5 | 106.2882 | 35.1648 | 89.8657 | 31.1966 | 1.0629 | 0.35165 | 0.89866 | 0.31197 | 0.71123 | 0.58669 | 66.1731 | 511.3717 | 17.4809
38897.5816 | 1644 | 588 | 38897.5816 | 1546 | 503 | 988.5 | 1172.5 | 100.3663 | 35.8974 | 94.3834 | 30.7082 | 1.0037 | 0.35897 | 0.94383 | 0.30708 | 0.64469 | 0.63675 | 125.4337 | 138.8461 | 20.3047
38897.5817 | 1567 | 621 | 38897.5817 | 1585 | 722 | 999.5 | 1183.5 | 95.6654 | 37.9121 | 96.7643 | 44.0781 | 0.95665 | 0.37912 | 0.96764 | 0.44078 | 0.57753 | 0.52686 | 108.5435 | 430.8675 | 32.5932
38897.5818 | 1994 | 305 | 38897.5819 | 1683 | 274 | 1010.5 | 1194.5 | 121.7338 | 18.6203 | 102.7473 | 16.7277 | 1.2173 | 0.1862 | 1.0275 | 0.16728 | 1.0311 | 0.8602 | 29.7141 | 154.9417 | 27.5741
38897.582 | 1929 | 16 | 38897.582 | 2056 | 17 | 1020.5 | 1204.5 | 117.7656 | 0.9768 | 125.5189 | 1.0379 | 1.1777 | 0.009768 | 1.2552 | 0.010379 | 1.1679 | 1.2448 | 27.7799 | 19.283 | 497.4809
38897.5821 | 2421 | 16 | 38897.5821 | 2180 | 16 | 1031.5 | 1215.5 | 147.8022 | 0.9768 | 133.0891 | 0.9768 | 1.478 | 0.009768 | 1.3309 | 0.009768 | 1.4683 | 1.3211 | 0.67763 | 130.5307 | 1.3448
38897.5822 | 2398 | 16 | 38897.5822 | 1997 | 13 | 1042.5 | 1226.5 | 146.398 | 0.9768 | 121.917 | 0.79365 | 1.464 | 0.009768 | 1.2192 | 0.0079365 | 1.4542 | 1.2112 | 1.6844 | 36.329 | 38.9394
38897.5823 | 2230 | 13 | 38897.5823 | 2128 | 10 | 1053.5 | 1237.5 | 136.1416 | 0.79365 | 129.9145 | 0.6105 | 1.3614 | 0.0079365 | 1.2991 | 0.006105 | 1.3535 | 1.293 | 9.7255 | 15.3525 | 199.0032
38897.5825 | 2247 | 6 | 38897.5825 | 1946 | 6 | 1064.5 | 1248.5 | 137.1795 | 0.3663 | 118.8034 | 0.3663 | 1.3718 | 0.003663 | 1.188 | 0.003663 | 1.3681 | 1.1844 | 8.5828 | 26.2757 | 639.4361
38897.5826 | 2336 | 8 | 38897.5826 | 2419 | 6 | 1074.5 | 1258.5 | 142.6129 | 0.4884 | 147.6801 | 0.3663 | 1.4261 | 0.004884 | 1.4768 | 0.003663 | 1.4212 | 1.4731 | 7.73 | 0.78702 | 9.1148
38897.5827 | 2344 | 7 | 38897.5827 | 1911 | 5 | 1085.5 | 1269.5 | 143.1013 | 0.42735 | 116.6667 | 0.30525 | 1.431 | 0.0042735 | 1.1667 | 0.0030525 | 1.4267 | 1.1636 | 4.0367 | 29.5365 | 281.3726
38897.5828 | 2276 | 8 | 38897.5828 | 2418 | 8 | 1096.5 | 1280.5 | 138.9499 | 0.4884 | 147.619 | 0.4884 | 1.3895 | 0.004884 | 1.4762 | 0.004884 | 1.3846 | 1.4713 | 12.4162 | 0.82624 | 15.7113
38897.583 | 2391 | 6 | 38897.583 | 2181 | 6 | 1107.5 | 1291.5 | 145.9707 | 0.3663 | 133.1502 | 0.3663 | 1.4597 | 0.003663 | 1.3315 | 0.003663 | 1.456 | 1.3278 | 1.981 | 13.6946 | 81.0632
38897.5831 | 1889 | 5 | 38897.5831 | 1864 | 6 | 1118 | 1302 | 115.3236 | 0.30525 | 113.7973 | 0.3663 | 1.1532 | 0.0030525 | 1.138 | 0.003663 | 1.1502 | 1.1343 | 29.3569 | 31.2033 | 2584.5768
38897.5832 | 2212 | 6 | 38897.5832 | 2379 | 9 | 1128.5 | 1312.5 | 135.0427 | 0.3663 | 145.2381 | 0.54945 | 1.3504 | 0.003663 | 1.4524 | 0.0054945 | 1.3468 | 1.4469 | 11.4376 | 2.5479 | 90.8445
38897.5833 | 1927 | 4 | 38897.5833 | 2242 | 6 | 1139.5 | 1323.5 | 117.6435 | 0.2442 | 136.8742 | 0.3663 | 1.1764 | 0.002442 | 1.3687 | 0.003663 | 1.174 | 1.3651 | 27.1815 | 8.825 | 1026.6081
38897.5835 | 1872 | 6 | 38897.5835 | 2180 | 6 | 1150.5 | 1334.5 | 114.2857 | 0.3663 | 133.0891 | 0.3663 | 1.1429 | 0.003663 | 1.3309 | 0.003663 | 1.1392 | 1.3272 | 31.1372 | 11.9449 | 994.7943
38897.5836 | 1981 | 6 | 38897.5836 | 2188 | 6 | 1161.5 | 1345.5 | 120.9402 | 0.3663 | 133.5775 | 0.3663 | 1.2094 | 0.003663 | 1.3358 | 0.003663 | 1.2057 | 1.3321 | 23.7314 | 11.5629 | 777.9942
38897.5837 | 2102 | 5 | 38897.5837 | 2298 | 7 | 1172 | 1356 | 128.3272 | 0.30525 | 140.293 | 0.42735 | 1.2833 | 0.0030525 | 1.4029 | 0.0042735 | 1.2802 | 1.3987 | 16.6332 | 6.1977 | 385.617
38897.5838 | 1912 | 6 | 38897.5838 | 2157 | 7 | 1182.5 | 1366.5 | 116.7277 | 0.3663 | 131.685 | 0.42735 | 1.1673 | 0.003663 | 1.3168 | 0.0042735 | 1.1636 | 1.3126 | 28.2383 | 13.193 | 1008.9258
38897.584 | 1997 | 6 | 38897.584 | 2025 | 6 | 1193.5 | 1377.5 | 121.917 | 0.3663 | 123.6264 | 0.3663 | 1.2192 | 0.003663 | 1.2363 | 0.003663 | 1.2155 | 1.2326 | 22.4453 | 20.699 | 1241.5511
38897.5841 | 1990 | 6 | 38897.5841 | 2097 | 7 | 1204.5 | 1388.5 | 121.4896 | 0.3663 | 128.022 | 0.42735 | 1.2149 | 0.003663 | 1.2802 | 0.0042735 | 1.2112 | 1.2759 | 22.9697 | 16.5271 | 1043.3532
38897.5842 | 2123 | 7 | 38897.5842 | 2398 | 10 | 1215.5 | 1399.5 | 129.6093 | 0.42735 | 146.398 | 0.6105 | 1.2961 | 0.0042735 | 1.464 | 0.006105 | 1.2918 | 1.4579 | 18.4806 | 1.6873 | 72.8629
38897.5843 | 2238 | 9 | 38897.5843 | 2380 | 10 | 1226 | 1410 | 136.63 | 0.54945 | 145.2991 | 0.6105 | 1.3663 | 0.0054945 | 1.453 | 0.006105 | 1.3608 | 1.4469 | 10.6507 | 2.521 | 52.0156
38897.5845 | 2030 | 7 | 38897.5845 | 2183 | 8 | 1236.5 | 1420.5 | 123.9316 | 0.42735 | 133.2723 | 0.4884 | 1.2393 | 0.0042735 | 1.3327 | 0.004884 | 1.235 | 1.3278 | 20.7401 | 11.9068 | 608.573
38897.5846 | 2349 | 11 | 38897.5846 | 2234 | 10 | 1247.5 | 1431.5 | 143.4066 | 0.67155 | 136.3858 | 0.6105 | 1.4341 | 0.0067155 | 1.3639 | 0.006105 | 1.4274 | 1.3578 | 3.9608 | 10.3159 | 65.7815
38897.5847 | 2126 | 9 | 38897.5847 | 2243 | 11 | 1258.5 | 1442.5 | 129.7924 | 0.54945 | 136.9353 | 0.67155 | 1.2979 | 0.0054945 | 1.3694 | 0.0067155 | 1.2924 | 1.3626 | 15.4381 | 8.996 | 277.2986
38897.5848 | 2220 | 10 | 38897.5848 | 2360 | 11 | 1269.5 | 1453.5 | 135.5311 | 0.6105 | 144.0781 | 0.67155 | 1.3553 | 0.006105 | 1.4408 | 0.0067155 | 1.3492 | 1.4341 | 11.3279 | 3.4362 | 68.893
38897.585 | 1952 | 9 | 38897.585 | 2045 | 9 | 1280 | 1464 | 119.1697 | 0.54945 | 124.8474 | 0.54945 | 1.1917 | 0.0054945 | 1.2485 | 0.0054945 | 1.1862 | 1.243 | 25.5853 | 19.6109 | 867.8372
38897.5851 | 2328 | 12 | 38897.5851 | 1927 | 10 | 1290.5 | 1474.5 | 142.1245 | 0.7326 | 117.6435 | 0.6105 | 1.4212 | 0.007326 | 1.1764 | 0.006105 | 1.4139 | 1.1703 | 4.8062 | 29.8654 | 186.6222
38897.5852 | 2316 | 14 | 38897.5852 | 2077 | 12 | 1301.5 | 1485.5 | 141.3919 | 0.8547 | 126.801 | 0.7326 | 1.4139 | 0.008547 | 1.268 | 0.007326 | 1.4054 | 1.2607 | 5.4422 | 19.5381 | 125.3634
38897.5853 | 2400 | 14 | 38897.5853 | 1871 | 12 | 1312.5 | 1496.5 | 146.5201 | 0.8547 | 114.2247 | 0.7326 | 1.4652 | 0.008547 | 1.1422 | 0.007326 | 1.4567 | 1.1349 | 1.5847 | 51.4063 | 56.7008
38897.5855 | 1965 | 11 | 38897.5855 | 2039 | 11 | 1323.5 | 1507.5 | 119.9634 | 0.67155 | 124.4811 | 0.67155 | 1.1996 | 0.0067155 | 1.2448 | 0.0067155 | 1.1929 | 1.2381 | 24.8723 | 20.0819 | 701.4452
38897.5856 | 1902 | 12 | 38897.5856 | 2144 | 13 | 1333.5 | 1517.5 | 116.1172 | 0.7326 | 130.8913 | 0.79365 | 1.1612 | 0.007326 | 1.3089 | 0.0079365 | 1.1538 | 1.301 | 29.667 | 14.0563 | 537.5108
38897.5857 | 1999 | 12 | 38897.5857 | 2120 | 14 | 1344.5 | 1528.5 | 122.0391 | 0.7326 | 129.4261 | 0.8547 | 1.2204 | 0.007326 | 1.2943 | 0.008547 | 1.2131 | 1.2857 | 22.9557 | 15.5197 | 477.3567
38897.5858 | 2330 | 17 | 38897.5858 | 1879 | 14 | 1355.5 | 1539.5 | 142.2466 | 1.0379 | 114.7131 | 0.8547 | 1.4225 | 0.010379 | 1.1471 | 0.008547 | 1.4121 | 1.1386 | 4.7404 | 35.5732 | 139.4994
38897.586 | 2011 | 15 | 38897.586 | 2105 | 17 | 1366.5 | 1550.5 | 122.7717 | 0.91575 | 128.5104 | 1.0379 | 1.2277 | 0.0091575 | 1.2851 | 0.010379 | 1.2186 | 1.2747 | 22.3798 | 16.5196 | 388.8227
38897.5861 | 2023 | 17 | 38897.5861 | 1886 | 17 | 1377.5 | 1561.5 | 123.5043 | 1.0379 | 115.1404 | 1.0379 | 1.235 | 0.010379 | 1.1514 | 0.010379 | 1.2247 | 1.141 | 21.2411 | 30.8211 | 550.7163
38897.5862 | 2004 | 19 | 38897.5862 | 2350 | 23 | 1388 | 1572 | 122.3443 | 1.16 | 143.4676 | 1.4042 | 1.2234 | 0.0116 | 1.4347 | 0.014042 | 1.2118 | 1.4206 | 28.9638 | 3.8877 | 81.6161
38897.5863 | 2098 | 28 | 38897.5863 | 1832 | 24 | 1398.5 | 1582.5 | 128.083 | 1.7094 | 111.8437 | 1.4652 | 1.2808 | 0.017094 | 1.1184 | 0.014652 | 1.2637 | 1.1038 | 17.0295 | 36.3141 | 296.2557
38897.5865 | 2225 | 32 | 38897.5865 | 2129 | 30 | 1409.5 | 1593.5 | 135.8364 | 1.9536 | 129.9756 | 1.8315 | 1.3584 | 0.019536 | 1.2998 | 0.018315 | 1.3388 | 1.2814 | 10.5948 | 16.9828 | 81.8323
38897.5866 | 1851 | 553 | 38897.5866 | 1738 | 343 | 1420.5 | 1604.5 | 113.0037 | 33.7607 | 106.105 | 20.9402 | 1.13 | 0.33761 | 1.0611 | 0.2094 | 0.79243 | 0.85165 | 161.6479 | 59.1287 | 2.2429
38897.5867 | 2265 | 79 | 38897.5867 | 1804 | 82 | 1431.5 | 1615.5 | 138.2784 | 4.823 | 110.1343 | 5.0061 | 1.3828 | 0.04823 | 1.1013 | 0.050061 | 1.3346 | 1.0513 | 8.226 | 87.3435 | 55.1085
38897.5868 | 2099 | 83 | 38897.5868 | 2320 | 87 | 1441.5 | 1625.5 | 128.1441 | 5.0672 | 141.6361 | 5.3114 | 1.2814 | 0.050672 | 1.4164 | 0.053114 | 1.2308 | 1.3632 | 63.3502 | 5.6011 | 16.3197
38897.587 | 2233 | 88 | 38897.587 | 1825 | 68 | 1452.5 | 1636.5 | 136.3248 | 5.3724 | 111.4164 | 4.1514 | 1.3632 | 0.053724 | 1.1142 | 0.041514 | 1.3095 | 1.0726 | 10.283 | 55.8885 | 47.4137
38897.5871 | 2095 | 73 | 38897.5871 | 2013 | 76 | 1463.5 | 1647.5 | 127.8999 | 4.4567 | 122.8938 | 4.6398 | 1.279 | 0.044567 | 1.2289 | 0.046398 | 1.2344 | 1.1825 | 19.4994 | 27.4281 | 79.4279
38897.5872 | 1794 | 64 | 38897.5872 | 2052 | 73 | 1474.5 | 1658.5 | 109.5238 | 3.9072 | 125.2747 | 4.4567 | 1.0952 | 0.039072 | 1.2527 | 0.044567 | 1.0562 | 1.2082 | 45.0464 | 21.2103 | 158.4132

## C1-4
Penlight Test 1 |  |  | 2006-06-29 | 13:39 |  | Vs = |  | 149.2906 |  | R = | 100
XLPE | 3-C | Tray
475 C | 17.7 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38897.5681 | 1 | 0 | 38897.5681 | 1 | 0 | -179.5 | 4.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5682 | 1 | 0 | 38897.5682 | 1 | 0 | -168.5 | 15.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5683 | 1 | 0 | 38897.5683 | 1 | 0 | -158.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5684 | 1 | 0 | 38897.5684 | 1 | 0 | -147.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5686 | 1 | 0 | 38897.5686 | 1 | 0 | -136.5 | 47.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5687 | 1 | 0 | 38897.5687 | 1 | 0 | -125.5 | 58.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5688 | 1 | 0 | 38897.5688 | 1 | 0 | -114.5 | 69.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5689 | 1 | 0 | 38897.5689 | 1 | 0 | -104.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5691 | 1 | 0 | 38897.5691 | 1 | 0 | -93.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5692 | 1 | 0 | 38897.5692 | 2 | 0 | -82.5 | 101.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244438 | 122169 | 244437.9994
38897.5693 | 1 | 0 | 38897.5693 | 1 | 0 | -71.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5694 | 1 | 0 | 38897.5695 | 1 | 0 | -60.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5696 | 1 | 0 | 38897.5696 | 1 | 0 | -50.5 | 133.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5697 | 2 | 0 | 38897.5697 | 2 | 0 | -39.5 | 144.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122169 | 122169 | 122168.9988
38897.5698 | 1 | 0 | 38897.5698 | 1 | 0 | -28.5 | 155.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5699 | 1 | 0 | 38897.57 | 1 | 0 | -17.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
| 1 | 0 | 38897.5701 | 1 | 0 | -6 | 178 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5702 | 1 | 0 | 38897.5702 | 1 | 0 | 4 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5703 | 2 | 0 | 38897.5703 | 1 | 0 | 14.5 | 198.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122169 | 244438 | 122168.9988
38897.5704 | 1 | 0 | 38897.5705 | 1 | 0 | 25.5 | 209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5706 | 1 | 0 | 38897.5706 | 1 | 0 | 36.5 | 220.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5707 | 2 | 0 | 38897.5707 | 1 | 0 | 47.5 | 231.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122169 | 244438 | 122168.9988
38897.5708 | 1 | 0 | 38897.5708 | 1 | 0 | 57.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5709 | 1 | 0 | 38897.5709 | 2 | 0 | 68.5 | 252.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244438 | 122169 | 244437.9994
38897.5711 | 1 | 0 | 38897.5711 | 1 | 0 | 79.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5712 | 1 | 0 | 38897.5712 | 2 | 0 | 90.5 | 274.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244438 | 122169 | 244437.9994
38897.5713 | 1 | 0 | 38897.5713 | 1 | 0 | 101.5 | 285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5714 | 1 | 0 | 38897.5714 | 2 | 0 | 112 | 296 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244438 | 122169 | 244437.9994
38897.5716 | 1 | 0 | 38897.5716 | 1 | 0 | 122.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5717 | 1 | 0 | 38897.5717 | 1 | 0 | 133.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5718 | 1 | 0 | 38897.5718 | 1 | 0 | 144.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5719 | 2 | 0 | 38897.572 | 1 | 0 | 155.5 | 339.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122169 | 244438 | 122168.9988
38897.5721 | 1 | 0 | 38897.5721 | 1 | 0 | 165.5 | 349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5722 | 1 | 0 | 38897.5722 | 1 | 0 | 176.5 | 360.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5723 | 1 | 1 | 38897.5723 | 1 | 0 | 187.5 | 371.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 597499358.44 | 244438 | 244238.0818
38897.5724 | 1 | 0 | 38897.5725 | 1 | 0 | 198.5 | 382.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5726 | 1 | 0 | 38897.5726 | 2 | 0 | 209.5 | 393.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244438 | 122169 | 244437.9994
38897.5727 | 1 | 0 | 38897.5727 | 1 | 0 | 220 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5728 | 1 | 1 | 38897.5728 | 1 | 0 | 230.5 | 414.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 597499358.44 | 244438 | 244238.0818
38897.5729 | 1 | 1 | 38897.573 | 1 | 0 | 241.5 | 425.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 597499358.44 | 244438 | 244238.0818
38897.5731 | 1 | 0 | 38897.5731 | 1 | 0 | 252.5 | 436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5732 | 1 | 0 | 38897.5732 | 1 | 0 | 263.5 | 447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5733 | 1 | 0 | 38897.5733 | 1 | 0 | 274 | 458 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5734 | 1 | 0 | 38897.5734 | 1 | 0 | 284.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5736 | 1 | 0 | 38897.5736 | 1 | 0 | 295.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5737 | 1 | 0 | 38897.5737 | 1 | 0 | 306.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5738 | 1 | 0 | 38897.5738 | 1 | 0 | 317.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5739 | 1 | 0 | 38897.5739 | 1 | 0 | 327.5 | 511.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5741 | 1 | 1 | 38897.5741 | 1 | 0 | 338.5 | 522.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 597499358.44 | 244438 | 244238.0818
38897.5742 | 1 | 0 | 38897.5742 | 1 | 0 | 349.5 | 533.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5743 | 1 | 0 | 38897.5743 | 2 | 0 | 360.5 | 544.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244438 | 122169 | 244437.9994
38897.5744 | 1 | 0 | 38897.5745 | 1 | 0 | 371.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5746 | 1 | 0 | 38897.5746 | 1 | 0 | 381.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5747 | 1 | 0 | 38897.5747 | 1 | 0 | 392.5 | 576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5748 | 1 | 0 | 38897.5748 | 1 | 0 | 403.5 | 587.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5749 | 1 | 0 | 38897.575 | 1 | 0 | 414.5 | 598.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5751 | 1 | 0 | 38897.5751 | 1 | 0 | 425.5 | 609.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5752 | 1 | 0 | 38897.5752 | 1 | 0 | 435.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5753 | 1 | 0 | 38897.5753 | 1 | 0 | 446.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5754 | 1 | 0 | 38897.5755 | 1 | 0 | 457.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5756 | 1 | 0 | 38897.5756 | 1 | 0 | 468.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5757 | 1 | 0 | 38897.5757 | 1 | 0 | 479 | 663 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5758 | 1 | 0 | 38897.5758 | 1 | 0 | 489.5 | 673.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5759 | 1 | 0 | 38897.5759 | 1 | 0 | 500.5 | 684.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5761 | 1 | 0 | 38897.5761 | 1 | 0 | 511.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5762 | 1 | 0 | 38897.5762 | 1 | 0 | 522.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5763 | 1 | 0 | 38897.5763 | 1 | 0 | 533 | 717 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5764 | 1 | 0 | 38897.5764 | 1 | 0 | 543.5 | 727.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5766 | 1 | 0 | 38897.5766 | 1 | 0 | 554.5 | 738.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5767 | 1 | 0 | 38897.5767 | 1 | 0 | 565.5 | 749.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5768 | 1 | 0 | 38897.5768 | 1 | 0 | 576.5 | 760.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5769 | 1 | 0 | 38897.577 | 1 | 0 | 587.5 | 771.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5771 | 1 | 0 | 38897.5771 | 1 | 0 | 597.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5772 | 1 | 0 | 38897.5772 | 1 | 0 | 608.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5773 | 1 | 0 | 38897.5773 | 1 | 0 | 619.5 | 803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5774 | 1 | 0 | 38897.5775 | 1 | 0 | 630.5 | 814.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5776 | 1 | 0 | 38897.5776 | 1 | 0 | 641.5 | 825.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5777 | 1 | 0 | 38897.5777 | 1 | 0 | 651.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5778 | 1 | 0 | 38897.5778 | 1 | 0 | 662.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5779 | 1 | 0 | 38897.578 | 1 | 0 | 673.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5781 | 1 | 0 | 38897.5781 | 1 | 0 | 684.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5782 | 1 | 0 | 38897.5782 | 1 | 0 | 695 | 879 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5783 | 1 | 0 | 38897.5783 | 1 | 0 | 705.5 | 889.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5784 | 1 | 0 | 38897.5784 | 1 | 0 | 716.5 | 900.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5786 | 1 | 0 | 38897.5786 | 1 | 0 | 727.5 | 911.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5787 | 1 | 0 | 38897.5787 | 1 | 0 | 738.5 | 922.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5788 | 1 | 0 | 38897.5788 | 1 | 0 | 749 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38897.5789 | 9 | 6 | 38897.5789 | 178 | 156 | 759.5 | 943.5 | 0.54945 | 0.3663 | 10.8669 | 9.5238 | 0.0054945 | 0.003663 | 0.10867 | 0.095238 | 0.0018315 | 0.013431 | 82805.8074 | 10395.2907 | 40120.3856
38897.5791 | 433 | 396 | 38897.5791 | 78 | 56 | 770.5 | 954.5 | 26.4347 | 24.1758 | 4.7619 | 3.4188 | 0.26435 | 0.24176 | 0.047619 | 0.034188 | 0.022589 | 0.013431 | 6011.4458 | 11236.6154 | 404.5763
38897.5792 | 838 | 800 | 38897.5792 | 952 | 860 | 781.5 | 965.5 | 51.16 | 48.84 | 58.1197 | 52.5031 | 0.5116 | 0.4884 | 0.5812 | 0.52503 | 0.023199 | 0.056166 | 10161.8434 | 3606.4952 | 98.1996
38897.5793 | 1007 | 799 | 38897.5793 | 1006 | 900 | 792.5 | 976.5 | 61.4774 | 48.779 | 61.4164 | 54.9451 | 0.61477 | 0.48779 | 0.61416 | 0.54945 | 0.12698 | 0.064713 | 629.3871 | 3890.6089 | 78.0173
38897.5794 | 900 | 788 | 38897.5794 | 1047 | 934 | 803 | 987 | 54.9451 | 48.1074 | 63.9194 | 57.0208 | 0.54945 | 0.48107 | 0.63919 | 0.57021 | 0.068376 | 0.068987 | 2108.8358 | 2035.1867 | 91.6128
38897.5796 | 781 | 813 | 38897.5796 | 301 | 186 | 813.5 | 997.5 | 47.6801 | 49.6337 | 18.3761 | 11.3553 | 0.4768 | 0.49634 | 0.18376 | 0.11355 | 0.019536 | 0.070208 | 13740.1695 | 4088.1475 | 102.2204
38897.5797 | 533 | 437 | 38897.5797 | 506 | 353 | 824.5 | 1008.5 | 32.5397 | 26.6789 | 30.8913 | 21.5507 | 0.3254 | 0.26679 | 0.30891 | 0.21551 | 0.058608 | 0.093407 | 2979.0362 | 1373.98 | 314.7105
38897.5798 | 1041 | 979 | 38897.5798 | 925 | 802 | 835.5 | 1019.5 | 63.5531 | 59.768 | 56.4713 | 48.9621 | 0.63553 | 0.59768 | 0.56471 | 0.48962 | 0.037851 | 0.075092 | 5161.9721 | 2813.7253 | 41.9592
38897.5799 | 930 | 835 | 38897.58 | 1095 | 933 | 846.5 | 1030.5 | 56.7766 | 50.9768 | 66.8498 | 56.9597 | 0.56777 | 0.50977 | 0.6685 | 0.5696 | 0.057998 | 0.098901 | 18145.7902 | 963.6595 | 73.822
38897.5801 | 1043 | 807 | 38897.5801 | 1015 | 845 | 857.5 | 1041.5 | 63.6752 | 49.2674 | 61.9658 | 51.5873 | 0.63675 | 0.49267 | 0.61966 | 0.51587 | 0.14408 | 0.10379 | 660.7563 | 3396.2675 | 71.6668
38897.5802 | 972 | 807 | 38897.5802 | 1003 | 897 | 867.5 | 1051.5 | 59.3407 | 49.2674 | 61.2332 | 54.7619 | 0.59341 | 0.49267 | 0.61233 | 0.54762 | 0.10073 | 0.064713 | 919.179 | 17144.8286 | 82.0961
38897.5803 | 1055 | 872 | 38897.5803 | 1074 | 960 | 878.5 | 1062.5 | 64.4078 | 53.2357 | 65.5678 | 58.6081 | 0.64408 | 0.53236 | 0.65568 | 0.58608 | 0.11172 | 0.069597 | 705.7653 | 6227.1599 | 58.5077
38897.5804 | 1157 | 951 | 38897.5805 | 1258 | 1047 | 889.5 | 1073.5 | 70.6349 | 58.0586 | 76.801 | 63.9194 | 0.70635 | 0.58059 | 0.76801 | 0.63919 | 0.12576 | 0.12882 | 1215.5403 | 950.9275 | 32.1006
38897.5806 | 1305 | 1084 | 38897.5806 | 1081 | 869 | 900.5 | 1084.5 | 79.6703 | 66.1783 | 65.9951 | 53.0525 | 0.7967 | 0.66178 | 0.65995 | 0.53053 | 0.13492 | 0.12943 | 855.9897 | 1234.9555 | 4.8115
38897.5807 | 1222 | 965 | 38897.5807 | 1277 | 803 | 910.5 | 1094.5 | 74.6032 | 58.9133 | 77.9609 | 49.0232 | 0.74603 | 0.58913 | 0.77961 | 0.49023 | 0.1569 | 0.28938 | 416.5031 | 2627.5301 | 25.7935
38897.5808 | 1181 | 865 | 38897.5808 | 1095 | 881 | 921.5 | 1105.5 | 72.1001 | 52.8083 | 66.8498 | 53.7851 | 0.721 | 0.52808 | 0.6685 | 0.53785 | 0.19292 | 0.13065 | 391.262 | 12090.6402 | 45.7924
38897.5809 | 1114 | 747 | 38897.5809 | 1353 | 874 | 932.5 | 1116.5 | 68.0098 | 45.6044 | 82.6007 | 53.3578 | 0.6801 | 0.45604 | 0.82601 | 0.53358 | 0.22405 | 0.29243 | 1860.0286 | 252.859 | 56.0599
38897.5811 | 1408 | 904 | 38897.5811 | 1191 | 693 | 943.5 | 1127.5 | 85.9585 | 55.1893 | 72.7106 | 42.3077 | 0.85958 | 0.55189 | 0.72711 | 0.42308 | 0.30769 | 0.30403 | 370.7358 | 403.2411 | 11.8225
38897.5812 | 1581 | 314 | 38897.5812 | 1696 | 435 | 954.5 | 1138.5 | 96.5201 | 19.1697 | 103.5409 | 26.5568 | 0.9652 | 0.1917 | 1.0354 | 0.26557 | 0.7735 | 0.76984 | 92.3486 | 94.8632 | 85.3298
38897.5813 | 1462 | 548 | 38897.5813 | 1620 | 539 | 964.5 | 1148.5 | 89.2552 | 33.4554 | 98.9011 | 32.906 | 0.89255 | 0.33455 | 0.98901 | 0.32906 | 0.558 | 0.65995 | 318.6793 | 90.5156 | 37.7469
38897.5814 | 1303 | 593 | 38897.5814 | 1559 | 697 | 975.5 | 1159.5 | 79.5482 | 36.2027 | 95.177 | 42.5519 | 0.79548 | 0.36203 | 0.95177 | 0.42552 | 0.43346 | 0.52625 | 507.145 | 122.3329 | 50.9751
38897.5816 | 1622 | 545 | 38897.5816 | 1517 | 514 | 986.5 | 1170.5 | 99.0232 | 33.2723 | 92.6129 | 31.3797 | 0.99023 | 0.33272 | 0.92613 | 0.3138 | 0.65751 | 0.61233 | 106.8507 | 177.866 | 32.6963
38897.5817 | 1343 | 532 | 38897.5817 | 1422 | 484 | 997.5 | 1181.5 | 81.9902 | 32.4786 | 86.8132 | 29.5482 | 0.8199 | 0.32479 | 0.86813 | 0.29548 | 0.49512 | 0.57265 | 263.0846 | 135.7216 | 61.7309
38897.5818 | 1352 | 495 | 38897.5818 | 1606 | 478 | 1008.5 | 1192.5 | 82.5397 | 30.2198 | 98.0464 | 29.1819 | 0.8254 | 0.3022 | 0.98046 | 0.29182 | 0.5232 | 0.68864 | 423.1051 | 82.6954 | 54.7174
38897.5819 | 1980 | 17 | 38897.5819 | 1991 | 16 | 1019 | 1203 | 120.8791 | 1.0379 | 121.5507 | 0.9768 | 1.2088 | 0.010379 | 1.2155 | 0.009768 | 1.1984 | 1.2057 | 24.6032 | 23.7899 | 506.88
38897.5821 | 2086 | 17 | 38897.5821 | 2296 | 19 | 1029.5 | 1213.5 | 127.3504 | 1.0379 | 140.1709 | 1.16 | 1.2735 | 0.010379 | 1.4017 | 0.0116 | 1.2631 | 1.3901 | 19.7372 | 6.85 | 129.1144
38897.5822 | 1883 | 14 | 38897.5822 | 1881 | 15 | 1040.5 | 1224.5 | 114.9573 | 0.8547 | 114.8352 | 0.91575 | 1.1496 | 0.008547 | 1.1484 | 0.0091575 | 1.141 | 1.1392 | 30.8336 | 31.0551 | 928.1803
38897.5823 | 1932 | 11 | 38897.5823 | 2180 | 12 | 1051.5 | 1235.5 | 117.9487 | 0.67155 | 133.0891 | 0.7326 | 1.1795 | 0.0067155 | 1.3309 | 0.007326 | 1.1728 | 1.3236 | 28.009 | 12.4876 | 507.0052
38897.5824 | 2327 | 9 | 38897.5825 | 2334 | 9 | 1062.5 | 1246.5 | 142.0635 | 0.54945 | 142.4908 | 0.54945 | 1.4206 | 0.0054945 | 1.4249 | 0.0054945 | 1.4151 | 1.4194 | 5.5233 | 5.1516 | 59.5416
38897.5826 | 2034 | 5 | 38897.5826 | 2089 | 6 | 1073 | 1257 | 124.1758 | 0.30525 | 127.5336 | 0.3663 | 1.2418 | 0.0030525 | 1.2753 | 0.003663 | 1.2387 | 1.2717 | 20.5671 | 17.352 | 1201.7697
38897.5827 | 2393 | 7 | 38897.5827 | 2001 | 5 | 1083.5 | 1267.5 | 146.0928 | 0.42735 | 122.1612 | 0.30525 | 1.4609 | 0.0042735 | 1.2216 | 0.0030525 | 1.4567 | 1.2186 | 2.2213 | 25.0934 | 130.0444
38897.5828 | 1870 | 4 | 38897.5828 | 2009 | 6 | 1094.5 | 1278.5 | 114.1636 | 0.2442 | 122.6496 | 0.3663 | 1.1416 | 0.002442 | 1.2265 | 0.003663 | 1.1392 | 1.2228 | 31.1384 | 21.9979 | 2575.6958
38897.5829 | 2376 | 8 | 38897.583 | 2117 | 5 | 1105.5 | 1289.5 | 145.0549 | 0.4884 | 129.243 | 0.30525 | 1.4505 | 0.004884 | 1.2924 | 0.0030525 | 1.4457 | 1.2894 | 2.9897 | 16.8854 | 110.8377
38897.5831 | 1926 | 5 | 38897.5831 | 2217 | 7 | 1116.5 | 1300.5 | 117.5824 | 0.30525 | 135.348 | 0.42735 | 1.1758 | 0.0030525 | 1.3535 | 0.0042735 | 1.1728 | 1.3492 | 27.7274 | 10.4533 | 973.6227
38897.5832 | 2294 | 6 | 38897.5832 | 2027 | 6 | 1127 | 1311 | 140.0488 | 0.3663 | 123.7485 | 0.3663 | 1.4005 | 0.003663 | 1.2375 | 0.003663 | 1.3968 | 1.2338 | 6.6973 | 21.6619 | 431.4146
38897.5833 | 1938 | 4 | 38897.5833 | 2078 | 4 | 1137.5 | 1321.5 | 118.315 | 0.2442 | 126.862 | 0.2442 | 1.1832 | 0.002442 | 1.2686 | 0.002442 | 1.1807 | 1.2662 | 26.5424 | 17.8433 | 1905.4837
38897.5834 | 2048 | 4 | 38897.5834 | 2202 | 4 | 1148.5 | 1332.5 | 125.0305 | 0.2442 | 134.4322 | 0.2442 | 1.2503 | 0.002442 | 1.3443 | 0.002442 | 1.2479 | 1.3419 | 19.7878 | 11.1756 | 988.582
38897.5836 | 1849 | 4 | 38897.5836 | 2311 | 6 | 1159.5 | 1343.5 | 112.8816 | 0.2442 | 141.0867 | 0.3663 | 1.1288 | 0.002442 | 1.4109 | 0.003663 | 1.1264 | 1.4072 | 33.5626 | 5.8755 | 821.8452
38897.5837 | 2184 | 5 | 38897.5837 | 2386 | 6 | 1170.5 | 1354.5 | 133.3333 | 0.30525 | 145.6654 | 0.3663 | 1.3333 | 0.0030525 | 1.4567 | 0.003663 | 1.3303 | 1.453 | 13.1848 | 2.5436 | 127.1901
38897.5838 | 2256 | 7 | 38897.5838 | 2429 | 7 | 1181 | 1365 | 137.7289 | 0.42735 | 148.2906 | 0.42735 | 1.3773 | 0.0042735 | 1.4829 | 0.0042735 | 1.373 | 1.4786 | 15.3538 | 0.68928 | 17.8356
38897.5839 | 2237 | 6 | 38897.5839 | 2284 | 5 | 1191.5 | 1375.5 | 136.569 | 0.3663 | 139.4383 | 0.30525 | 1.3657 | 0.003663 | 1.3944 | 0.0030525 | 1.362 | 1.3913 | 9.7003 | 7.245 | 227.8662
38897.5841 | 2276 | 7 | 38897.5841 | 1908 | 4 | 1202.5 | 1386.5 | 138.9499 | 0.42735 | 116.4835 | 0.2442 | 1.3895 | 0.0042735 | 1.1648 | 0.002442 | 1.3852 | 1.1624 | 7.5451 | 29.0321 | 521.9335
38897.5842 | 2307 | 8 | 38897.5842 | 1881 | 7 | 1213.5 | 1397.5 | 140.8425 | 0.4884 | 114.8352 | 0.42735 | 1.4084 | 0.004884 | 1.1484 | 0.0042735 | 1.4035 | 1.1441 | 6.0851 | 32.0859 | 395.8939
38897.5843 | 2242 | 9 | 38897.5843 | 2402 | 10 | 1224.5 | 1408.5 | 136.8742 | 0.54945 | 146.6422 | 0.6105 | 1.3687 | 0.0054945 | 1.4664 | 0.006105 | 1.3632 | 1.4603 | 11.591 | 1.8814 | 39.8837
38897.5844 | 2312 | 9 | 38897.5844 | 1925 | 7 | 1235 | 1419 | 141.1477 | 0.54945 | 117.5214 | 0.42735 | 1.4115 | 0.0054945 | 1.1752 | 0.0042735 | 1.406 | 1.1709 | 5.8709 | 28.9298 | 310.0989
38897.5846 | 2024 | 8 | 38897.5846 | 2140 | 9 | 1245.5 | 1429.5 | 123.5653 | 0.4884 | 130.6471 | 0.54945 | 1.2357 | 0.004884 | 1.3065 | 0.0054945 | 1.2308 | 1.301 | 21.485 | 14.6177 | 659.0024
38897.5847 | 2154 | 9 | 38897.5847 | 1956 | 9 | 1256.5 | 1440.5 | 131.5018 | 0.54945 | 119.4139 | 0.54945 | 1.315 | 0.0054945 | 1.1941 | 0.0054945 | 1.3095 | 1.1886 | 13.8069 | 26.0057 | 647.5456
38897.5848 | 2041 | 9 | 38897.5848 | 2340 | 11 | 1267.5 | 1451.5 | 124.6032 | 0.54945 | 142.8571 | 0.67155 | 1.246 | 0.0054945 | 1.4286 | 0.0067155 | 1.2405 | 1.4219 | 22.0088 | 4.6239 | 194.1562
38897.5849 | 2019 | 11 | 38897.585 | 2300 | 12 | 1278.5 | 1462.5 | 123.2601 | 0.67155 | 140.4151 | 0.7326 | 1.2326 | 0.0067155 | 1.4042 | 0.007326 | 1.2259 | 1.3968 | 23.188 | 6.5011 | 230.5066
38897.5851 | 2363 | 12 | 38897.5851 | 2024 | 9 | 1289 | 1473 | 144.2613 | 0.7326 | 123.5653 | 0.54945 | 1.4426 | 0.007326 | 1.2357 | 0.0054945 | 1.4353 | 1.2302 | 3.5805 | 23.8926 | 113.1062
38897.5852 | 2389 | 10 | 38897.5852 | 2112 | 12 | 1299.5 | 1483.5 | 145.8486 | 0.6105 | 128.9377 | 0.7326 | 1.4585 | 0.006105 | 1.2894 | 0.007326 | 1.4524 | 1.2821 | 2.4188 | 20.7857 | 79.8142
38897.5853 | 2147 | 13 | 38897.5853 | 1959 | 10 | 1310.5 | 1494.5 | 131.0745 | 0.79365 | 119.5971 | 0.6105 | 1.3107 | 0.0079365 | 1.196 | 0.006105 | 1.3028 | 1.1899 | 14.3192 | 25.8828 | 451.3619
38897.5854 | 1857 | 12 | 38897.5855 | 2382 | 15 | 1321.5 | 1505.5 | 113.37 | 0.7326 | 145.4212 | 0.91575 | 1.1337 | 0.007326 | 1.4542 | 0.0091575 | 1.1264 | 1.4451 | 41.9187 | 2.7188 | 127.1299
38897.5856 | 2181 | 15 | 38897.5856 | 1852 | 13 | 1332.5 | 1516.5 | 133.1502 | 0.91575 | 113.0647 | 0.79365 | 1.3315 | 0.0091575 | 1.1306 | 0.0079365 | 1.3223 | 1.1227 | 12.4581 | 34.2075 | 423.7548
38897.5857 | 2165 | 17 | 38897.5857 | 2303 | 17 | 1342.5 | 1526.5 | 132.1734 | 1.0379 | 140.5983 | 1.0379 | 1.3217 | 0.010379 | 1.406 | 0.010379 | 1.3114 | 1.3956 | 14.8449 | 6.5568 | 95.3334
38897.5858 | 2277 | 17 | 38897.5858 | 2007 | 13 | 1353.5 | 1537.5 | 139.011 | 1.0379 | 122.5275 | 0.79365 | 1.3901 | 0.010379 | 1.2253 | 0.0079365 | 1.3797 | 1.2173 | 7.6913 | 24.0211 | 172.4714
38897.5859 | 2245 | 17 | 38897.5859 | 2338 | 17 | 1364.5 | 1548.5 | 137.0574 | 1.0379 | 142.735 | 1.0379 | 1.3706 | 0.010379 | 1.4274 | 0.010379 | 1.3602 | 1.417 | 10.6253 | 4.969 | 51.0634
38897.5861 | 2340 | 23 | 38897.5861 | 1880 | 17 | 1375.5 | 1559.5 | 142.8571 | 1.4042 | 114.7741 | 1.0379 | 1.4286 | 0.014042 | 1.1477 | 0.010379 | 1.4145 | 1.1374 | 4.6711 | 37.7157 | 98.0918
38897.5862 | 2156 | 22 | 38897.5862 | 1960 | 18 | 1386.5 | 1570.5 | 131.6239 | 1.3431 | 119.6581 | 1.0989 | 1.3162 | 0.013431 | 1.1966 | 0.010989 | 1.3028 | 1.1856 | 14.104 | 26.7519 | 256.5112
38897.5863 | 2182 | 30 | 38897.5863 | 2225 | 24 | 1396.5 | 1580.5 | 133.2112 | 1.8315 | 135.8364 | 1.4652 | 1.3321 | 0.018315 | 1.3584 | 0.014652 | 1.3138 | 1.3437 | 14.0421 | 10.8557 | 76.1802
38897.5864 | 2222 | 31 | 38897.5864 | 1984 | 25 | 1407.5 | 1591.5 | 135.6532 | 1.8926 | 121.1233 | 1.5263 | 1.3565 | 0.018926 | 1.2112 | 0.015263 | 1.3376 | 1.196 | 10.7654 | 26.7192 | 130.8516
38897.5866 | 1901 | 386 | 38897.5866 | 1626 | 360 | 1418.5 | 1602.5 | 116.0562 | 23.5653 | 99.2674 | 21.978 | 1.1606 | 0.23565 | 0.99267 | 0.21978 | 0.92491 | 0.77289 | 40.7998 | 213.5785 | 27.9463
38897.5867 | 1435 | 399 | 38897.5867 | 2020 | 65 | 1429.5 | 1613.5 | 87.6068 | 24.359 | 123.3211 | 3.9683 | 0.87607 | 0.24359 | 1.2332 | 0.039683 | 0.63248 | 1.1935 | 119.0095 | 213.3584 | 104.3294
38897.5868 | 1805 | 59 | 38897.5868 | 2076 | 68 | 1440.5 | 1624.5 | 110.1954 | 3.602 | 126.7399 | 4.1514 | 1.102 | 0.03602 | 1.2674 | 0.041514 | 1.0659 | 1.2259 | 44.1684 | 19.9229 | 163.704
38897.5869 | 2184 | 81 | 38897.5869 | 1786 | 67 | 1450.5 | 1634.5 | 133.3333 | 4.9451 | 109.0354 | 4.0904 | 1.3333 | 0.049451 | 1.0904 | 0.040904 | 1.2839 | 1.0495 | 13.3812 | 54.1231 | 78.2021
38897.5871 | 2075 | 71 | 38897.5871 | 1957 | 69 | 1461.5 | 1645.5 | 126.6789 | 4.3346 | 119.475 | 4.2125 | 1.2668 | 0.043346 | 1.1947 | 0.042125 | 1.2234 | 1.1526 | 20.8351 | 31.3702 | 100.6896
38897.5872 | 2309 | 60 | 38897.5872 | 2146 | 70 | 1472.5 | 1656.5 | 140.9646 | 3.663 | 131.0134 | 4.2735 | 1.4096 | 0.03663 | 1.3101 | 0.042735 | 1.373 | 1.2674 | 6.6751 | 29.1416 | 28.726

## C1-3
Penlight Test 1 |  |  | 2006-06-29 | 13:39 |  | Vs = |  | 149.5958 |  | R = | 100
XLPE | 3-C | Tray
475 C | 17.7 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38897.568 | 1 | 0 | 38897.5681 | 1 | 0 | -181.5 | 2.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5682 | 1 | 0 | 38897.5682 | 1 | 0 | -170.5 | 13.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5683 | 1 | 0 | 38897.5683 | 1 | 0 | -159.5 | 24.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5684 | 1 | 0 | 38897.5684 | 1 | 0 | -149.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5685 | 1 | 0 | 38897.5686 | 1 | 0 | -138.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5687 | 1 | 0 | 38897.5687 | 1 | 0 | -127.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5688 | 2 | 0 | 38897.5688 | 1 | 0 | -116.5 | 67.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122419 | 244938 | 122418.9988
38897.5689 | 1 | 0 | 38897.5689 | 1 | 0 | -105.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.569 | 1 | 0 | 38897.5691 | 1 | 0 | -95.5 | 88.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5692 | 1 | 0 | 38897.5692 | 1 | 0 | -84.5 | 99.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5693 | 1 | 0 | 38897.5693 | 1 | 0 | -73.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5694 | 1 | 0 | 38897.5694 | 1 | 0 | -62.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5695 | 1 | 0 | 38897.5696 | 1 | 0 | -51.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5697 | 2 | 0 | 38897.5697 | 2 | 0 | -41 | 143 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122419 | 122419 | 122418.9988
38897.5698 | 1 | 0 | 38897.5698 | 1 | 0 | -30.5 | 153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5699 | 1 | 0 | 38897.5699 | 1 | 0 | -19.5 | 164.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.57 | 1 | 0 | 38897.5701 | 1 | 0 | -8.5 | 175.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5702 | 1 | 0 | 38897.5702 | 1 | 0 | 2.5 | 186.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5703 | 1 | 0 | 38897.5703 | 1 | 0 | 13 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5704 | 1 | 0 | 38897.5704 | 1 | 0 | 23.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5705 | 1 | 0 | 38897.5706 | 1 | 0 | 34.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5707 | 2 | 0 | 38897.5707 | 1 | 0 | 45.5 | 229.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122419 | 244938 | 122418.9988
38897.5708 | 1 | 0 | 38897.5708 | 1 | 0 | 56.5 | 240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5709 | 1 | 0 | 38897.5709 | 1 | 0 | 66.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.571 | 1 | 0 | 38897.5711 | 1 | 0 | 77.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5712 | 1 | 0 | 38897.5712 | 1 | 0 | 88.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5713 | 1 | 0 | 38897.5713 | 1 | 0 | 99.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5714 | 1 | 0 | 38897.5714 | 1 | 0 | 110.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5715 | 2 | 0 | 38897.5716 | 1 | 0 | 120.5 | 304.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122419 | 244938 | 122418.9988
38897.5717 | 1 | 0 | 38897.5717 | 1 | 0 | 131.5 | 315.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5718 | 1 | 0 | 38897.5718 | 2 | 0 | 142.5 | 326.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244938 | 122419 | 244937.9994
38897.5719 | 1 | 0 | 38897.5719 | 1 | 0 | 153.5 | 337.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.572 | 1 | 0 | 38897.5721 | 1 | 0 | 164.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5722 | 1 | 0 | 38897.5722 | 1 | 0 | 174.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5723 | 1 | 0 | 38897.5723 | 1 | 0 | 185.5 | 369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5724 | 1 | 0 | 38897.5724 | 1 | 0 | 196.5 | 380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5725 | 1 | 0 | 38897.5726 | 1 | 0 | 207.5 | 391.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5727 | 1 | 0 | 38897.5727 | 1 | 0 | 218.5 | 402.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5728 | 1 | 0 | 38897.5728 | 1 | 0 | 228.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5729 | 1 | 0 | 38897.5729 | 1 | 0 | 239.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.573 | 1 | 0 | 38897.5731 | 1 | 0 | 250.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5732 | 1 | 0 | 38897.5732 | 1 | 0 | 261.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5733 | 1 | 0 | 38897.5733 | 1 | 0 | 272.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5734 | 2 | 0 | 38897.5734 | 1 | 0 | 282.5 | 466.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122419 | 244938 | 122418.9988
38897.5735 | 1 | 0 | 38897.5736 | 1 | 0 | 293.5 | 477.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5737 | 1 | 0 | 38897.5737 | 1 | 0 | 304.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5738 | 1 | 0 | 38897.5738 | 1 | 0 | 315.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5739 | 1 | 0 | 38897.5739 | 2 | 0 | 326.5 | 510.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244938 | 122419 | 244937.9994
38897.574 | 2 | 0 | 38897.5741 | 1 | 0 | 336.5 | 520.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122419 | 244938 | 122418.9988
38897.5742 | 1 | 0 | 38897.5742 | 1 | 0 | 347.5 | 531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5743 | 1 | 0 | 38897.5743 | 1 | 0 | 358.5 | 542.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5744 | 1 | 0 | 38897.5744 | 1 | 0 | 369.5 | 553.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5745 | 1 | 1 | 38897.5746 | 1 | 0 | 380.5 | 564.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 599946238.44 | 244938 | 244738.0816
38897.5747 | 1 | 0 | 38897.5747 | 2 | 0 | 390.5 | 574.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244938 | 122419 | 244937.9994
38897.5748 | 1 | 0 | 38897.5748 | 1 | 0 | 401.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5749 | 1 | 0 | 38897.5749 | 1 | 0 | 412.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.575 | 1 | 0 | 38897.5751 | 1 | 0 | 423.5 | 607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5752 | 1 | 0 | 38897.5752 | 1 | 0 | 434.5 | 618.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5753 | 1 | 0 | 38897.5753 | 1 | 0 | 444.5 | 628.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5754 | 1 | 0 | 38897.5754 | 1 | 0 | 455.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5755 | 1 | 0 | 38897.5756 | 1 | 0 | 466.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5757 | 1 | 0 | 38897.5757 | 1 | 0 | 477.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5758 | 2 | 0 | 38897.5758 | 1 | 0 | 488 | 672 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122419 | 244938 | 122418.9988
38897.5759 | 1 | 0 | 38897.5759 | 1 | 0 | 498.5 | 682.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.576 | 1 | 0 | 38897.5761 | 1 | 0 | 509.5 | 693.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5762 | 1 | 0 | 38897.5762 | 2 | 0 | 520.5 | 704.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244938 | 122419 | 244937.9994
38897.5763 | 1 | 0 | 38897.5763 | 1 | 0 | 531.5 | 715.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5764 | 1 | 0 | 38897.5764 | 1 | 0 | 542.5 | 726.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5765 | 1 | 0 | 38897.5766 | 1 | 0 | 552.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5767 | 1 | 0 | 38897.5767 | 1 | 0 | 563.5 | 747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5768 | 1 | 0 | 38897.5768 | 1 | 0 | 574.5 | 758.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5769 | 1 | 0 | 38897.5769 | 1 | 0 | 585.5 | 769.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.577 | 1 | 0 | 38897.5771 | 1 | 0 | 596.5 | 780.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5772 | 1 | 0 | 38897.5772 | 1 | 0 | 606.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5773 | 1 | 0 | 38897.5773 | 1 | 0 | 617.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5774 | 1 | 0 | 38897.5774 | 1 | 0 | 628.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5775 | 1 | 0 | 38897.5776 | 1 | 0 | 639.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5777 | 1 | 0 | 38897.5777 | 1 | 0 | 650.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5778 | 1 | 0 | 38897.5778 | 1 | 0 | 660.5 | 844.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5779 | 1 | 0 | 38897.5779 | 1 | 0 | 671.5 | 855.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.578 | 1 | 0 | 38897.5781 | 1 | 0 | 682.5 | 866.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5782 | 2 | 0 | 38897.5782 | 1 | 0 | 693.5 | 877.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122419 | 244938 | 122418.9988
38897.5783 | 1 | 0 | 38897.5783 | 1 | 0 | 704 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5784 | 1 | 0 | 38897.5784 | 1 | 0 | 714.5 | 898.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5785 | 1 | 0 | 38897.5786 | 1 | 0 | 725.5 | 909.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5787 | 1 | 0 | 38897.5787 | 1 | 0 | 736.5 | 920.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5788 | 1 | 0 | 38897.5788 | 1 | 0 | 747.5 | 931.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5789 | 1 | 0 | 38897.5789 | 1 | 0 | 758 | 942 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.579 | 1 | 0 | 38897.5791 | 1 | 0 | 768.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5792 | 1 | 0 | 38897.5792 | 1 | 0 | 779.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
38897.5793 | 6 | 1 | 38897.5793 | 1 | 1 | 790.5 | 974.5 | 0.3663 | 0.06105 | 0.06105 | 0.06105 | 0.003663 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0030525 | 0 | 48887.5918 | 119744289.6963 | 244337.796
38897.5794 | 93 | 13 | 38897.5794 | 29 | 15 | 801.5 | 985.5 | 5.6777 | 0.79365 | 1.7705 | 0.91575 | 0.056777 | 0.0079365 | 0.017705 | 0.0091575 | 0.04884 | 0.008547 | 2949.3954 | 17947.5532 | 17933.7691
38897.5795 | 161 | 39 | 38897.5795 | 87 | 57 | 812 | 996 | 9.8291 | 2.381 | 5.3114 | 3.4799 | 0.098291 | 0.02381 | 0.053114 | 0.034799 | 0.074481 | 0.018315 | 1883.4125 | 8761.8333 | 5705.0921
38897.5797 | 172 | 69 | 38897.5797 | 227 | 162 | 822.5 | 1006.5 | 10.5006 | 4.2125 | 13.8584 | 9.8901 | 0.10501 | 0.042125 | 0.13858 | 0.098901 | 0.062882 | 0.039683 | 2251.2274 | 3846.417 | 3120.8631
38897.5798 | 321 | 159 | 38897.5798 | 293 | 226 | 833.5 | 1017.5 | 19.5971 | 9.707 | 17.8877 | 13.7973 | 0.19597 | 0.09707 | 0.17888 | 0.13797 | 0.098901 | 0.040904 | 1345.1521 | 4297.6617 | 1211.0533
38897.5799 | 906 | 749 | 38897.5799 | 1025 | 866 | 844.5 | 1028.5 | 55.3114 | 45.7265 | 62.5763 | 52.8694 | 0.55311 | 0.45726 | 0.62576 | 0.52869 | 0.095849 | 0.09707 | 1483.0835 | 1416.7641 | 99.191
38897.58 | 1011 | 851 | 38897.5801 | 1141 | 975 | 855.5 | 1039.5 | 61.7216 | 51.9536 | 69.6581 | 59.5238 | 0.61722 | 0.51954 | 0.69658 | 0.59524 | 0.09768 | 0.10134 | 1546.0885 | 1272.0129 | 64.1005
38897.5802 | 1029 | 863 | 38897.5802 | 1165 | 992 | 866 | 1050 | 62.8205 | 52.6862 | 71.1233 | 60.5617 | 0.62821 | 0.52686 | 0.71123 | 0.60562 | 0.10134 | 0.10562 | 1515.3045 | 1195.3175 | 59.7071
38897.5803 | 1162 | 976 | 38897.5803 | 931 | 808 | 876.5 | 1060.5 | 70.9402 | 59.5849 | 56.8376 | 49.3284 | 0.7094 | 0.59585 | 0.56838 | 0.49328 | 0.11355 | 0.075092 | 719.0912 | 14285.3226 | 31.7837
38897.5804 | 1097 | 898 | 38897.5804 | 1287 | 1077 | 887.5 | 1071.5 | 66.9719 | 54.823 | 78.5714 | 65.7509 | 0.66972 | 0.54823 | 0.78571 | 0.65751 | 0.12149 | 0.12821 | 1414.6568 | 869.0471 | 45.4774
38897.5805 | 1096 | 957 | 38897.5806 | 1262 | 1038 | 898.5 | 1082.5 | 66.9109 | 58.4249 | 77.0452 | 63.37 | 0.66911 | 0.58425 | 0.77045 | 0.6337 | 0.08486 | 0.13675 | 1252.77 | 3098.1732 | 40.2252
38897.5807 | 1257 | 1071 | 38897.5807 | 1252 | 992 | 909.5 | 1093.5 | 76.7399 | 65.3846 | 76.4347 | 60.5617 | 0.7674 | 0.65385 | 0.76435 | 0.60562 | 0.11355 | 0.15873 | 661.7746 | 18889.7925 | 11.3665
38897.5808 | 1284 | 968 | 38897.5808 | 1113 | 846 | 920 | 1104 | 78.3883 | 59.0965 | 67.9487 | 51.6484 | 0.78388 | 0.59096 | 0.67949 | 0.51648 | 0.19292 | 0.163 | 451.3785 | 1680.6713 | 19.3429
38897.5809 | 1297 | 867 | 38897.5809 | 1073 | 791 | 930.5 | 1114.5 | 79.1819 | 52.9304 | 65.5067 | 48.2906 | 0.79182 | 0.5293 | 0.65507 | 0.48291 | 0.26252 | 0.17216 | 259.6029 | 6068.7992 | 32.4957
38897.581 | 1380 | 903 | 38897.5811 | 1226 | 755 | 941.5 | 1125.5 | 84.2491 | 55.1282 | 74.8474 | 46.0928 | 0.84249 | 0.55128 | 0.74847 | 0.46093 | 0.29121 | 0.28755 | 396.1704 | 436.6152 | 15.0817
38897.5812 | 2063 | 358 | 38897.5812 | 1949 | 426 | 952.5 | 1136.5 | 125.9463 | 21.8559 | 118.9866 | 26.0073 | 1.2595 | 0.21856 | 1.1899 | 0.26007 | 1.0409 | 0.92979 | 13.4735 | 30.5952 | 1.9226
38897.5813 | 1761 | 515 | 38897.5813 | 1628 | 707 | 963.5 | 1147.5 | 107.5092 | 31.4408 | 99.3895 | 43.1624 | 1.0751 | 0.31441 | 0.99389 | 0.43162 | 0.76068 | 0.56227 | 36.8529 | 82.4491 | 15.3015
38897.5814 | 1850 | 502 | 38897.5814 | 1437 | 541 | 974.5 | 1158.5 | 112.9426 | 30.6471 | 87.7289 | 33.0281 | 1.1294 | 0.30647 | 0.87729 | 0.33028 | 0.82295 | 0.54701 | 36.7622 | 176.0495 | 12.4983
38897.5815 | 1751 | 601 | 38897.5816 | 1459 | 566 | 984.5 | 1168.5 | 106.8987 | 36.6911 | 89.072 | 34.5543 | 1.069 | 0.36691 | 0.89072 | 0.34554 | 0.70208 | 0.54518 | 58.5331 | 1340.1757 | 15.2328
38897.5817 | 1633 | 618 | 38897.5817 | 1580 | 607 | 995.5 | 1179.5 | 99.6947 | 37.7289 | 96.4591 | 37.0574 | 0.99695 | 0.37729 | 0.96459 | 0.37057 | 0.61966 | 0.59402 | 119.2057 | 187.6643 | 21.0469
38897.5818 | 1611 | 754 | 38897.5818 | 1586 | 692 | 1006.5 | 1190.5 | 98.3516 | 46.0317 | 96.8254 | 42.2466 | 0.98352 | 0.46032 | 0.96825 | 0.42247 | 0.5232 | 0.54579 | 305.5209 | 129.4948 | 6.3895
38897.5819 | 2428 | 20 | 38897.5819 | 2379 | 20 | 1017.5 | 1201.5 | 148.2295 | 1.221 | 145.2381 | 1.221 | 1.4823 | 0.01221 | 1.4524 | 0.01221 | 1.4701 | 1.4402 | 0.96027 | 25.8389 | 2.4435
38897.582 | 2038 | 15 | 38897.582 | 2250 | 19 | 1028 | 1212 | 124.42 | 0.91575 | 137.3626 | 1.16 | 1.2442 | 0.0091575 | 1.3736 | 0.0116 | 1.235 | 1.362 | 22.1422 | 9.3409 | 226.3187
38897.5822 | 2088 | 14 | 38897.5822 | 2309 | 17 | 1038.5 | 1222.5 | 127.4725 | 0.8547 | 140.9646 | 1.0379 | 1.2747 | 0.008547 | 1.4096 | 0.010379 | 1.2662 | 1.3993 | 19.5284 | 6.4119 | 149.9424
38897.5823 | 1930 | 11 | 38897.5823 | 2103 | 11 | 1049.5 | 1233.5 | 117.8266 | 0.67155 | 128.3883 | 0.67155 | 1.1783 | 0.0067155 | 1.2839 | 0.0067155 | 1.1716 | 1.2772 | 28.068 | 16.9222 | 670.2063
38897.5824 | 1936 | 6 | 38897.5824 | 2376 | 9 | 1060.5 | 1244.5 | 118.1929 | 0.3663 | 145.0549 | 0.54945 | 1.1819 | 0.003663 | 1.4505 | 0.0054945 | 1.1783 | 1.4451 | 29.5363 | 3.1834 | 261.4042
38897.5825 | 1934 | 5 | 38897.5826 | 2415 | 6 | 1071.5 | 1255.5 | 118.0708 | 0.30525 | 147.4359 | 0.3663 | 1.1807 | 0.0030525 | 1.4744 | 0.003663 | 1.1777 | 1.4707 | 32.4529 | 1.48 | 149.1627
38897.5827 | 2351 | 6 | 38897.5827 | 2382 | 7 | 1082 | 1266 | 143.5287 | 0.3663 | 145.4212 | 0.42735 | 1.4353 | 0.003663 | 1.4542 | 0.0042735 | 1.4316 | 1.4499 | 4.6226 | 3.0752 | 46.433
38897.5828 | 1894 | 5 | 38897.5828 | 2125 | 5 | 1092.5 | 1276.5 | 115.6288 | 0.30525 | 129.7314 | 0.30525 | 1.1563 | 0.0030525 | 1.2973 | 0.0030525 | 1.1532 | 1.2943 | 29.9664 | 15.4699 | 1477.4029
38897.5829 | 2347 | 7 | 38897.5829 | 2125 | 7 | 1103.5 | 1287.5 | 143.2845 | 0.42735 | 129.7314 | 0.42735 | 1.4328 | 0.0042735 | 1.2973 | 0.0042735 | 1.4286 | 1.293 | 4.4991 | 16.5806 | 195.8226
38897.583 | 2434 | 6 | 38897.5831 | 1959 | 4 | 1114.5 | 1298.5 | 148.5958 | 0.3663 | 119.5971 | 0.2442 | 1.486 | 0.003663 | 1.196 | 0.002442 | 1.4823 | 1.1935 | 0.6793 | 35.9681 | 45.7643
38897.5832 | 1870 | 5 | 38897.5832 | 1936 | 4 | 1125.5 | 1309.5 | 114.1636 | 0.30525 | 118.1929 | 0.2442 | 1.1416 | 0.0030525 | 1.1819 | 0.002442 | 1.1386 | 1.1795 | 31.434 | 26.8007 | 2432.2591
38897.5833 | 2256 | 5 | 38897.5833 | 2386 | 4 | 1136 | 1320 | 137.7289 | 0.30525 | 145.6654 | 0.2442 | 1.3773 | 0.0030525 | 1.4567 | 0.002442 | 1.3742 | 1.4542 | 9.3935 | 2.752 | 101.4419
38897.5834 | 2186 | 4 | 38897.5834 | 1883 | 3 | 1146.5 | 1330.5 | 133.4554 | 0.2442 | 114.9573 | 0.18315 | 1.3346 | 0.002442 | 1.1496 | 0.0018315 | 1.3321 | 1.1477 | 12.1895 | 30.5801 | 1524.4378
38897.5835 | 2132 | 4 | 38897.5836 | 2283 | 5 | 1157.5 | 1341.5 | 130.1587 | 0.2442 | 139.3773 | 0.30525 | 1.3016 | 0.002442 | 1.3938 | 0.0030525 | 1.2991 | 1.3907 | 15.3485 | 7.4543 | 545.226
38897.5837 | 2103 | 4 | 38897.5837 | 2185 | 6 | 1168.5 | 1352.5 | 128.3883 | 0.2442 | 133.3944 | 0.3663 | 1.2839 | 0.002442 | 1.3339 | 0.003663 | 1.2814 | 1.3303 | 16.8085 | 12.3818 | 945.8089
38897.5838 | 2257 | 6 | 38897.5838 | 2345 | 6 | 1179.5 | 1363.5 | 137.79 | 0.3663 | 143.1624 | 0.3663 | 1.3779 | 0.003663 | 1.4316 | 0.003663 | 1.3742 | 1.428 | 9.1149 | 4.6358 | 138.3621
38897.5839 | 2175 | 8 | 38897.5839 | 2076 | 6 | 1189.5 | 1373.5 | 132.7839 | 0.4884 | 126.7399 | 0.3663 | 1.3278 | 0.004884 | 1.2674 | 0.003663 | 1.323 | 1.2637 | 12.9667 | 18.4995 | 521.7746
38897.584 | 1861 | 5 | 38897.5841 | 2052 | 5 | 1200.5 | 1384.5 | 113.6142 | 0.30525 | 125.2747 | 0.30525 | 1.1361 | 0.0030525 | 1.2527 | 0.0030525 | 1.1331 | 1.2497 | 32.1977 | 19.6104 | 1916.2106
38897.5842 | 2260 | 7 | 38897.5842 | 1884 | 5 | 1211.5 | 1395.5 | 137.9731 | 0.42735 | 115.0183 | 0.30525 | 1.3797 | 0.0042735 | 1.1502 | 0.0030525 | 1.3755 | 1.1471 | 8.5353 | 31.1126 | 621.6499
38897.5843 | 1883 | 7 | 38897.5843 | 1888 | 7 | 1222.5 | 1406.5 | 114.9573 | 0.42735 | 115.2625 | 0.42735 | 1.1496 | 0.0042735 | 1.1526 | 0.0042735 | 1.1453 | 1.1484 | 30.6217 | 30.2657 | 1859.969
38897.5844 | 2250 | 8 | 38897.5844 | 2189 | 8 | 1233.5 | 1417.5 | 137.3626 | 0.4884 | 133.6386 | 0.4884 | 1.3736 | 0.004884 | 1.3364 | 0.004884 | 1.3687 | 1.3315 | 9.2006 | 12.482 | 266.8531
38897.5845 | 2406 | 9 | 38897.5845 | 1929 | 7 | 1244 | 1428 | 146.8864 | 0.54945 | 117.7656 | 0.42735 | 1.4689 | 0.0054945 | 1.1777 | 0.0042735 | 1.4634 | 1.1734 | 1.8724 | 33.6778 | 99.0376
38897.5847 | 2265 | 8 | 38897.5847 | 1877 | 7 | 1254.5 | 1438.5 | 138.2784 | 0.4884 | 114.591 | 0.42735 | 1.3828 | 0.004884 | 1.1459 | 0.0042735 | 1.3779 | 1.1416 | 8.3052 | 32.1093 | 538.9043
38897.5848 | 1993 | 8 | 38897.5848 | 1892 | 8 | 1265.5 | 1449.5 | 121.6728 | 0.4884 | 115.5067 | 0.4884 | 1.2167 | 0.004884 | 1.1551 | 0.004884 | 1.2118 | 1.1502 | 23.3536 | 30.1869 | 1302.4911
38897.5849 | 2288 | 12 | 38897.5849 | 1895 | 9 | 1276.5 | 1460.5 | 139.6825 | 0.7326 | 115.6899 | 0.54945 | 1.3968 | 0.007326 | 1.1569 | 0.0054945 | 1.3895 | 1.1514 | 7.2558 | 31.5206 | 300.3371
38897.585 | 1850 | 8 | 38897.5851 | 2147 | 12 | 1287.5 | 1471.5 | 112.9426 | 0.4884 | 131.0745 | 0.7326 | 1.1294 | 0.004884 | 1.3107 | 0.007326 | 1.1245 | 1.3034 | 33.6038 | 14.4516 | 934.982
38897.5852 | 1920 | 10 | 38897.5852 | 2102 | 12 | 1298 | 1482 | 117.2161 | 0.6105 | 128.3272 | 0.7326 | 1.1722 | 0.006105 | 1.2833 | 0.007326 | 1.1661 | 1.2759 | 28.6504 | 17.0098 | 756.4794
38897.5853 | 2351 | 12 | 38897.5853 | 1894 | 11 | 1308.5 | 1492.5 | 143.5287 | 0.7326 | 115.6288 | 0.67155 | 1.4353 | 0.007326 | 1.1563 | 0.0067155 | 1.428 | 1.1496 | 4.3136 | 34.1759 | 185.4709
38897.5854 | 1876 | 12 | 38897.5854 | 2296 | 15 | 1319.5 | 1503.5 | 114.5299 | 0.7326 | 140.1709 | 0.91575 | 1.1453 | 0.007326 | 1.4017 | 0.0091575 | 1.138 | 1.3926 | 33.9844 | 6.9016 | 302.5632
38897.5855 | 2018 | 13 | 38897.5856 | 1920 | 12 | 1330.5 | 1514.5 | 123.199 | 0.79365 | 117.2161 | 0.7326 | 1.232 | 0.0079365 | 1.1722 | 0.007326 | 1.2241 | 1.1648 | 22.0651 | 28.6133 | 717.7052
38897.5857 | 2343 | 17 | 38897.5857 | 1988 | 12 | 1341.5 | 1525.5 | 143.0403 | 1.0379 | 121.3675 | 0.7326 | 1.4304 | 0.010379 | 1.2137 | 0.007326 | 1.42 | 1.2063 | 4.7458 | 26.8335 | 112.4779
38897.5858 | 1848 | 13 | 38897.5858 | 1941 | 14 | 1351.5 | 1535.5 | 112.8205 | 0.79365 | 118.4982 | 0.8547 | 1.1282 | 0.0079365 | 1.185 | 0.008547 | 1.1203 | 1.1764 | 33.7113 | 27.0161 | 964.3073
38897.5859 | 2068 | 16 | 38897.5859 | 1983 | 14 | 1362.5 | 1546.5 | 126.2515 | 0.9768 | 121.0623 | 0.8547 | 1.2625 | 0.009768 | 1.2106 | 0.008547 | 1.2527 | 1.2021 | 19.2433 | 24.6476 | 452.7963
38897.586 | 1943 | 16 | 38897.5861 | 2052 | 17 | 1373.5 | 1557.5 | 118.6203 | 0.9768 | 125.2747 | 1.0379 | 1.1862 | 0.009768 | 1.2527 | 0.010379 | 1.1764 | 1.2424 | 27.4593 | 20.1907 | 515.9141
38897.5862 | 2372 | 25 | 38897.5862 | 1889 | 17 | 1384.5 | 1568.5 | 144.8107 | 1.5263 | 115.3236 | 1.0379 | 1.4481 | 0.015263 | 1.1532 | 0.010379 | 1.4328 | 1.1429 | 3.4291 | 40.7906 | 61.8622
38897.5863 | 2004 | 24 | 38897.5863 | 2132 | 24 | 1395.5 | 1579.5 | 122.3443 | 1.4652 | 130.1587 | 1.4652 | 1.2234 | 0.014652 | 1.3016 | 0.014652 | 1.2088 | 1.2869 | 24.4123 | 15.8423 | 240.6811
38897.5864 | 2226 | 31 | 38897.5864 | 2007 | 26 | 1405.5 | 1589.5 | 135.8974 | 1.8926 | 122.5275 | 1.5873 | 1.359 | 0.018926 | 1.2253 | 0.015873 | 1.34 | 1.2094 | 10.8224 | 25.4705 | 126.6327
38897.5865 | 1461 | 386 | 38897.5866 | 1902 | 436 | 1416.5 | 1600.5 | 89.1941 | 23.5653 | 116.1172 | 26.6178 | 0.89194 | 0.23565 | 1.1612 | 0.26618 | 0.65629 | 0.89499 | 1583.6674 | 38.1225 | 43.144
38897.5867 | 1625 | 366 | 38897.5867 | 1640 | 444 | 1427.5 | 1611.5 | 99.2063 | 22.3443 | 100.1221 | 27.1062 | 0.99206 | 0.22344 | 1.0012 | 0.27106 | 0.76862 | 0.73016 | 86.9252 | 118.2664 | 68.0088
38897.5868 | 1834 | 60 | 38897.5868 | 1935 | 60 | 1438.5 | 1622.5 | 111.9658 | 3.663 | 118.1319 | 3.663 | 1.1197 | 0.03663 | 1.1813 | 0.03663 | 1.083 | 1.1447 | 39.1714 | 29.9322 | 213.6199
38897.5869 | 1961 | 64 | 38897.5869 | 1958 | 68 | 1449.5 | 1633.5 | 119.7192 | 3.9072 | 119.536 | 4.1514 | 1.1972 | 0.039072 | 1.1954 | 0.041514 | 1.1581 | 1.1538 | 29.1002 | 29.7273 | 152.3073
38897.587 | 1910 | 67 | 38897.587 | 1866 | 63 | 1459.5 | 1643.5 | 116.6056 | 4.0904 | 113.9194 | 3.8462 | 1.1661 | 0.040904 | 1.1392 | 0.038462 | 1.1252 | 1.1007 | 32.5834 | 36.3048 | 188.1862
38897.5872 | 1793 | 61 | 38897.5872 | 2106 | 70 | 1470.5 | 1654.5 | 109.4628 | 3.7241 | 128.5714 | 4.2735 | 1.0946 | 0.037241 | 1.2857 | 0.042735 | 1.0574 | 1.243 | 47.0321 | 18.2485 | 150.8778

## C1-2
Penlight Test 1 |  |  | 2006-06-29 | 13:39 |  | Vs = |  | 149.2295 |  | R = | 100
XLPE | 3-C | Tray
475 C | 17.7 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38897.568 | 1 | 0 | 38897.568 | 1 | 0 | -183.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5681 | 1 | 0 | 38897.5682 | 1 | 0 | -172.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5683 | 1 | 0 | 38897.5683 | 1 | 0 | -161.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5684 | 1 | 0 | 38897.5684 | 1 | 0 | -150.5 | 33.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5685 | 1 | 0 | 38897.5685 | 1 | 0 | -140.5 | 43.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5686 | 1 | 0 | 38897.5687 | 2 | 0 | -129.5 | 54.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244338 | 122119 | 244337.9994
38897.5688 | 1 | 0 | 38897.5688 | 1 | 0 | -118.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5689 | 1 | 0 | 38897.5689 | 1 | 0 | -107.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.569 | 1 | 0 | 38897.569 | 1 | 0 | -96.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5691 | 1 | 0 | 38897.5692 | 1 | 0 | -86.5 | 97.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5693 | 1 | 0 | 38897.5693 | 1 | 0 | -75.5 | 108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5694 | 1 | 0 | 38897.5694 | 1 | 0 | -64.5 | 119.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5695 | 1 | 0 | 38897.5695 | 1 | 0 | -53.5 | 130.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5697 | 2 | 0 | 38897.5697 | 2 | 0 | -42.5 | 141.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122119 | 122119 | 122118.9988
38897.5698 | 2 | 0 | 38897.5698 | 2 | 0 | -32 | 152 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122119 | 122119 | 122118.9988
38897.5699 | 1 | 0 | 38897.5699 | 1 | 0 | -21.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.57 | 1 | 0 | 38897.57 | 2 | 0 | -10.5 | 173.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244338 | 122119 | 244337.9994
38897.5702 | 1 | 1 | 38897.5702 | 1 | 0 | 0.5 | 184.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 597010582.44 | 244338 | 244138.0818
38897.5703 | 1 | 0 | 38897.5703 | 1 | 0 | 11.5 | 195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5704 | 1 | 0 | 38897.5704 | 1 | 0 | 22 | 206 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5705 | 1 | 0 | 38897.5705 | 1 | 0 | 32.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5706 | 1 | 0 | 38897.5707 | 1 | 0 | 43.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5708 | 1 | 0 | 38897.5708 | 1 | 0 | 54.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5709 | 1 | 0 | 38897.5709 | 1 | 0 | 65.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.571 | 1 | 0 | 38897.571 | 1 | 0 | 75.5 | 259.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5711 | 1 | 0 | 38897.5712 | 1 | 0 | 86.5 | 270.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5713 | 1 | 0 | 38897.5713 | 1 | 0 | 97.5 | 281.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5714 | 1 | 0 | 38897.5714 | 1 | 0 | 108.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5715 | 1 | 0 | 38897.5715 | 1 | 0 | 119.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5716 | 1 | 0 | 38897.5717 | 1 | 0 | 129.5 | 313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5718 | 1 | 1 | 38897.5718 | 1 | 0 | 140.5 | 324.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 597010582.44 | 244338 | 244138.0818
38897.5719 | 1 | 1 | 38897.5719 | 1 | 0 | 151.5 | 335.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 597010582.44 | 244338 | 244138.0818
38897.572 | 1 | 0 | 38897.572 | 1 | 0 | 162.5 | 346.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
| 1 | 0 | 38897.5722 | 2 | 0 | 174 | 358 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244338 | 122119 | 244337.9994
38897.5723 | 1 | 1 | 38897.5723 | 2 | 0 | 183.5 | 367.5 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 298383122.22 | 122119 | 244038.1636
38897.5724 | 1 | 0 | 38897.5724 | 2 | 0 | 194.5 | 378.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244338 | 122119 | 244337.9994
38897.5725 | 1 | 0 | 38897.5725 | 1 | 0 | 205.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5727 | 1 | 0 | 38897.5727 | 1 | 0 | 216.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5728 | 1 | 0 | 38897.5728 | 1 | 0 | 227.5 | 411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5729 | 1 | 0 | 38897.5729 | 1 | 0 | 237.5 | 421.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.573 | 1 | 0 | 38897.573 | 2 | 0 | 248.5 | 432.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244338 | 122119 | 244337.9994
38897.5731 | 1 | 0 | 38897.5732 | 1 | 0 | 259.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5733 | 2 | 0 | 38897.5733 | 1 | 0 | 270.5 | 454.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122119 | 244338 | 122118.9988
38897.5734 | 1 | 0 | 38897.5734 | 1 | 0 | 281.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5735 | 1 | 0 | 38897.5735 | 1 | 0 | 291.5 | 475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5736 | 1 | 0 | 38897.5737 | 1 | 0 | 302.5 | 486.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5738 | 1 | 0 | 38897.5738 | 1 | 0 | 313.5 | 497.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5739 | 2 | 0 | 38897.5739 | 1 | 0 | 324.5 | 508.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122119 | 244338 | 122118.9988
38897.574 | 1 | 0 | 38897.574 | 1 | 0 | 335.5 | 519.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5741 | 1 | 0 | 38897.5742 | 1 | 0 | 345.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5743 | 1 | 0 | 38897.5743 | 1 | 0 | 356.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5744 | 1 | 0 | 38897.5744 | 1 | 0 | 367.5 | 551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5745 | 1 | 0 | 38897.5745 | 1 | 0 | 378.5 | 562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5747 | 1 | 0 | 38897.5747 | 1 | 0 | 389.5 | 573.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5748 | 1 | 0 | 38897.5748 | 1 | 0 | 399.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5749 | 1 | 0 | 38897.5749 | 1 | 0 | 410.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.575 | 1 | 0 | 38897.575 | 1 | 0 | 421.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5752 | 1 | 0 | 38897.5752 | 1 | 0 | 432.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5753 | 1 | 0 | 38897.5753 | 1 | 0 | 443.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5754 | 1 | 0 | 38897.5754 | 1 | 0 | 453.5 | 637.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5755 | 1 | 0 | 38897.5755 | 1 | 0 | 464.5 | 648.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5756 | 1 | 0 | 38897.5757 | 1 | 0 | 475.5 | 659.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5758 | 1 | 0 | 38897.5758 | 1 | 0 | 486.5 | 670.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5759 | 1 | 0 | 38897.5759 | 1 | 0 | 497.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.576 | 1 | 0 | 38897.576 | 1 | 0 | 507.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5761 | 1 | 0 | 38897.5762 | 1 | 0 | 518.5 | 702.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5763 | 1 | 0 | 38897.5763 | 1 | 0 | 529.5 | 713.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5764 | 1 | 0 | 38897.5764 | 1 | 0 | 540.5 | 724.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5765 | 1 | 0 | 38897.5765 | 2 | 0 | 551.5 | 735.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244338 | 122119 | 244337.9994
38897.5766 | 1 | 0 | 38897.5767 | 1 | 0 | 561.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5768 | 1 | 0 | 38897.5768 | 1 | 0 | 572.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5769 | 1 | 0 | 38897.5769 | 1 | 0 | 583.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.577 | 1 | 0 | 38897.577 | 1 | 0 | 594.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5772 | 1 | 0 | 38897.5772 | 1 | 0 | 605.5 | 789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5773 | 1 | 0 | 38897.5773 | 1 | 0 | 615.5 | 799.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5774 | 1 | 0 | 38897.5774 | 1 | 0 | 626.5 | 810.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5775 | 1 | 0 | 38897.5775 | 2 | 0 | 637.5 | 821.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244338 | 122119 | 244337.9994
38897.5777 | 1 | 0 | 38897.5777 | 1 | 0 | 648.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5778 | 1 | 0 | 38897.5778 | 1 | 0 | 659 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5779 | 1 | 0 | 38897.5779 | 1 | 0 | 669.5 | 853.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.578 | 1 | 0 | 38897.578 | 1 | 0 | 680.5 | 864.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5781 | 1 | 0 | 38897.5782 | 1 | 0 | 691.5 | 875.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5783 | 1 | 0 | 38897.5783 | 1 | 0 | 702.5 | 886.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5784 | 1 | 0 | 38897.5784 | 1 | 0 | 713 | 897 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5785 | 1 | 0 | 38897.5785 | 1 | 0 | 723.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5786 | 1 | 0 | 38897.5787 | 1 | 0 | 734.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5788 | 1 | 0 | 38897.5788 | 1 | 0 | 745.5 | 929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5789 | 1 | 0 | 38897.5789 | 1 | 0 | 756.5 | 940.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.579 | 1 | 0 | 38897.579 | 1 | 0 | 767 | 951 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5791 | 1 | 0 | 38897.5792 | 1 | 0 | 777.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244338 | 244338 | 244337.9994
38897.5793 | 2 | 1 | 38897.5793 | 1 | 1 | 788.5 | 972.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 244237.9591 | 596766144.0822 | 244137.9591
38897.5794 | 22 | 1 | 38897.5794 | 1 | 2 | 799.5 | 983.5 | 1.3431 | 0.06105 | 0.06105 | 0.1221 | 0.013431 | 0.0006105 | 0.0006105 | 0.001221 | 0.012821 | 0.0006105 | 11535.3638 | 248649.0747 | 242040.6577
38897.5795 | 157 | 45 | 38897.5795 | 77 | 51 | 810.5 | 994.5 | 9.5849 | 2.7473 | 4.7009 | 3.1136 | 0.095849 | 0.027473 | 0.047009 | 0.031136 | 0.068376 | 0.015873 | 2050.4861 | 10068.4798 | 4934.0616
38897.5797 | 233 | 106 | 38897.5797 | 177 | 121 | 821 | 1005 | 14.2247 | 6.4713 | 10.8059 | 7.3871 | 0.14225 | 0.064713 | 0.10806 | 0.073871 | 0.077534 | 0.034188 | 1773.346 | 4610.6756 | 1944.0436
38897.5798 | 338 | 135 | 38897.5798 | 218 | 151 | 831.5 | 1015.5 | 20.6349 | 8.2418 | 13.3089 | 9.2186 | 0.20635 | 0.082418 | 0.13309 | 0.092186 | 0.12393 | 0.040904 | 1054.2132 | 4226.5129 | 1426.5296
38897.5799 | 477 | 303 | 38897.5799 | 455 | 400 | 842.5 | 1026.5 | 29.1209 | 18.4982 | 27.7778 | 24.42 | 0.29121 | 0.18498 | 0.27778 | 0.2442 | 0.10623 | 0.033578 | 1151.0818 | 9824.0591 | 543.7653
38897.58 | 544 | 374 | 38897.58 | 513 | 449 | 853.5 | 1037.5 | 33.2112 | 22.8327 | 31.3187 | 27.4115 | 0.33211 | 0.22833 | 0.31319 | 0.27411 | 0.10379 | 0.039072 | 1150.6064 | 7732.6029 | 402.9124
38897.5802 | 628 | 423 | 38897.5802 | 492 | 385 | 864.5 | 1048.5 | 38.3394 | 25.8242 | 30.0366 | 23.5043 | 0.38339 | 0.25824 | 0.30037 | 0.23504 | 0.12515 | 0.065324 | 953.135 | 2931.1943 | 318.5371
38897.5803 | 594 | 396 | 38897.5803 | 605 | 487 | 875 | 1059 | 36.2637 | 24.1758 | 36.9353 | 29.7314 | 0.36264 | 0.24176 | 0.36935 | 0.29731 | 0.12088 | 0.072039 | 1011.3421 | 2633.4732 | 353.8317
38897.5804 | 1145 | 1020 | 38897.5804 | 1067 | 870 | 885.5 | 1069.5 | 69.9023 | 62.2711 | 65.1404 | 53.1136 | 0.69902 | 0.62271 | 0.6514 | 0.53114 | 0.076313 | 0.12027 | 3136.6647 | 1220.4684 | 25.3159
38897.5805 | 1260 | 1042 | 38897.5805 | 1057 | 854 | 896.5 | 1080.5 | 76.9231 | 63.6142 | 64.5299 | 52.1368 | 0.76923 | 0.63614 | 0.6453 | 0.52137 | 0.13309 | 0.12393 | 828.5235 | 1388.4203 | 12.7461
38897.5806 | 1272 | 1025 | 38897.5807 | 1071 | 844 | 907.5 | 1091.5 | 77.6557 | 62.5763 | 65.3846 | 51.5263 | 0.77656 | 0.62576 | 0.65385 | 0.51526 | 0.15079 | 0.13858 | 699.225 | 1292.0466 | 13.3456
38897.5808 | 1040 | 939 | 38897.5808 | 1094 | 851 | 918.5 | 1102.5 | 63.4921 | 57.326 | 66.7888 | 51.9536 | 0.63492 | 0.57326 | 0.66789 | 0.51954 | 0.061661 | 0.14835 | 1195.5269 | 5701.4336 | 48.7069
38897.5809 | 1384 | 771 | 38897.5809 | 1161 | 859 | 929 | 1113 | 84.4933 | 47.0696 | 70.8791 | 52.442 | 0.84493 | 0.4707 | 0.70879 | 0.52442 | 0.37424 | 0.18437 | 126.1274 | 338.5712 | 28.975
38897.581 | 1267 | 715 | 38897.581 | 1375 | 824 | 939.5 | 1123.5 | 77.3504 | 43.6508 | 83.9438 | 50.3053 | 0.7735 | 0.43651 | 0.83944 | 0.50305 | 0.337 | 0.33639 | 341.2098 | 345.5115 | 50.153
38897.5811 | 1713 | 144 | 38897.5812 | 1918 | 164 | 950.5 | 1134.5 | 104.5788 | 8.7912 | 117.094 | 10.0122 | 1.0458 | 0.087912 | 1.1709 | 0.10012 | 0.95788 | 1.0708 | 63.0314 | 35.2374 | 106.2829
38897.5813 | 1467 | 417 | 38897.5813 | 1576 | 482 | 961.5 | 1145.5 | 89.5604 | 25.4579 | 96.2149 | 29.4261 | 0.8956 | 0.25458 | 0.96215 | 0.29426 | 0.64103 | 0.66789 | 142.1734 | 115.0207 | 71.8857
38897.5814 | 1594 | 517 | 38897.5814 | 1634 | 640 | 972.5 | 1156.5 | 97.3138 | 31.5629 | 99.7558 | 39.072 | 0.97314 | 0.31563 | 0.99756 | 0.39072 | 0.65751 | 0.60684 | 99.8244 | 229.6514 | 44.9224
38897.5815 | 1603 | 547 | 38897.5815 | 1750 | 604 | 983.5 | 1167.5 | 97.8632 | 33.3944 | 106.8376 | 36.8742 | 0.97863 | 0.33394 | 1.0684 | 0.36874 | 0.64469 | 0.69963 | 238.573 | 77.7731 | 23.5442
38897.5816 | 1369 | 648 | 38897.5817 | 1459 | 578 | 993.5 | 1177.5 | 83.5775 | 39.5604 | 89.072 | 35.2869 | 0.83578 | 0.3956 | 0.89072 | 0.35287 | 0.44017 | 0.53785 | 490.8713 | 129.1031 | 37.1659
38897.5818 | 1425 | 687 | 38897.5818 | 1514 | 625 | 1004.5 | 1188.5 | 86.9963 | 41.9414 | 92.4298 | 38.1563 | 0.86996 | 0.41941 | 0.9243 | 0.38156 | 0.45055 | 0.54274 | 684.0449 | 116.6428 | 26.049
38897.5819 | 2220 | 20 | 38897.5819 | 2393 | 19 | 1015.5 | 1199.5 | 135.5311 | 1.221 | 146.0928 | 1.16 | 1.3553 | 0.01221 | 1.4609 | 0.0116 | 1.3431 | 1.4493 | 17.0063 | 2.2712 | 22.6936
38897.582 | 1942 | 16 | 38897.582 | 2220 | 17 | 1026.5 | 1210.5 | 118.5592 | 0.9768 | 135.5311 | 1.0379 | 1.1856 | 0.009768 | 1.3553 | 0.010379 | 1.1758 | 1.3449 | 28.332 | 10.4704 | 288.1193
38897.5822 | 2120 | 15 | 38897.5822 | 2428 | 17 | 1037 | 1221 | 129.4261 | 0.91575 | 148.2295 | 1.0379 | 1.2943 | 0.0091575 | 1.4823 | 0.010379 | 1.2851 | 1.4719 | 300.1807 | 0.75115 | 15.3772
38897.5823 | 2208 | 13 | 38897.5823 | 1872 | 12 | 1047.5 | 1231.5 | 134.7985 | 0.79365 | 114.2857 | 0.7326 | 1.348 | 0.0079365 | 1.1429 | 0.007326 | 1.34 | 1.1355 | 10.9677 | 32.6964 | 423.3916
38897.5824 | 2058 | 8 | 38897.5824 | 2309 | 9 | 1058.5 | 1242.5 | 125.641 | 0.4884 | 140.9646 | 0.54945 | 1.2564 | 0.004884 | 1.4096 | 0.0054945 | 1.2515 | 1.4042 | 20.1583 | 6.0026 | 267.8314
38897.5825 | 2306 | 7 | 38897.5825 | 2422 | 7 | 1069.5 | 1253.5 | 140.7814 | 0.42735 | 147.8632 | 0.42735 | 1.4078 | 0.0042735 | 1.4786 | 0.0042735 | 1.4035 | 1.4744 | 8.8227 | 0.95819 | 17.8131
38897.5827 | 1969 | 6 | 38897.5827 | 2220 | 6 | 1080.5 | 1264.5 | 120.2076 | 0.3663 | 135.5311 | 0.3663 | 1.2021 | 0.003663 | 1.3553 | 0.003663 | 1.1984 | 1.3516 | 24.9617 | 10.2458 | 727.0403
38897.5828 | 1942 | 4 | 38897.5828 | 2337 | 7 | 1091 | 1275 | 118.5592 | 0.2442 | 142.674 | 0.42735 | 1.1856 | 0.002442 | 1.4267 | 0.0042735 | 1.1832 | 1.4225 | 27.1239 | 4.6602 | 554.7837
38897.5829 | 2020 | 4 | 38897.5829 | 2325 | 6 | 1101.5 | 1285.5 | 123.3211 | 0.2442 | 141.9414 | 0.3663 | 1.2332 | 0.002442 | 1.4194 | 0.003663 | 1.2308 | 1.4158 | 21.8841 | 5.2095 | 520.383
38897.583 | 2199 | 6 | 38897.583 | 2185 | 7 | 1112.5 | 1296.5 | 134.2491 | 0.3663 | 133.3944 | 0.42735 | 1.3425 | 0.003663 | 1.3339 | 0.0042735 | 1.3388 | 1.3297 | 11.4448 | 12.2532 | 435.4989
38897.5831 | 2401 | 5 | 38897.5832 | 2074 | 4 | 1123.5 | 1307.5 | 146.5812 | 0.30525 | 126.6178 | 0.2442 | 1.4658 | 0.0030525 | 1.2662 | 0.002442 | 1.4628 | 1.2637 | 1.8296 | 20.0057 | 127.9637
38897.5833 | 1906 | 4 | 38897.5833 | 2117 | 3 | 1134.5 | 1318.5 | 116.3614 | 0.2442 | 129.243 | 0.18315 | 1.1636 | 0.002442 | 1.2924 | 0.0018315 | 1.1612 | 1.2906 | 28.6937 | 15.5633 | 1799.1643
38897.5834 | 2342 | 5 | 38897.5834 | 2004 | 2 | 1145 | 1329 | 142.9792 | 0.30525 | 122.3443 | 0.1221 | 1.4298 | 0.0030525 | 1.2234 | 0.001221 | 1.4267 | 1.2222 | 4.4229 | 22.5053 | 357.7917
38897.5835 | 2254 | 4 | 38897.5835 | 1965 | 3 | 1155.5 | 1339.5 | 137.6068 | 0.2442 | 119.9634 | 0.18315 | 1.3761 | 0.002442 | 1.1996 | 0.0018315 | 1.3736 | 1.1978 | 8.5222 | 24.8796 | 928.3067
38897.5836 | 1929 | 4 | 38897.5837 | 2257 | 4 | 1166.5 | 1350.5 | 117.7656 | 0.2442 | 137.79 | 0.2442 | 1.1777 | 0.002442 | 1.3779 | 0.002442 | 1.1752 | 1.3755 | 27.4545 | 8.371 | 987.5296
38897.5838 | 2299 | 6 | 38897.5838 | 2168 | 6 | 1177.5 | 1361.5 | 140.3541 | 0.3663 | 132.3565 | 0.3663 | 1.4035 | 0.003663 | 1.3236 | 0.003663 | 1.3999 | 1.3199 | 6.4669 | 13.3567 | 273.7172
38897.5839 | 1970 | 3 | 38897.5839 | 2236 | 6 | 1188.5 | 1372.5 | 120.2686 | 0.18315 | 136.5079 | 0.3663 | 1.2027 | 0.0018315 | 1.3651 | 0.003663 | 1.2009 | 1.3614 | 24.5126 | 9.4481 | 1356.3949
38897.584 | 2303 | 6 | 38897.584 | 2406 | 7 | 1199 | 1383 | 140.5983 | 0.3663 | 146.8864 | 0.42735 | 1.406 | 0.003663 | 1.4689 | 0.0042735 | 1.4023 | 1.4646 | 7.2991 | 1.6665 | 36.9844
38897.5841 | 2404 | 6 | 38897.5842 | 1963 | 4 | 1209.5 | 1393.5 | 146.7643 | 0.3663 | 119.8413 | 0.2442 | 1.4676 | 0.003663 | 1.1984 | 0.002442 | 1.464 | 1.196 | 1.6991 | 27.929 | 125.0953
38897.5843 | 2086 | 6 | 38897.5843 | 2338 | 9 | 1220.5 | 1404.5 | 127.3504 | 0.3663 | 142.735 | 0.54945 | 1.2735 | 0.003663 | 1.4274 | 0.0054945 | 1.2698 | 1.4219 | 18.3652 | 4.6658 | 261.8071
38897.5844 | 2335 | 8 | 38897.5844 | 2011 | 5 | 1231.5 | 1415.5 | 142.5519 | 0.4884 | 122.7717 | 0.30525 | 1.4255 | 0.004884 | 1.2277 | 0.0030525 | 1.4206 | 1.2247 | 4.7725 | 22.7947 | 235.2429
38897.5845 | 2400 | 8 | 38897.5845 | 1925 | 5 | 1242.5 | 1426.5 | 146.5201 | 0.4884 | 117.5214 | 0.30525 | 1.4652 | 0.004884 | 1.1752 | 0.0030525 | 1.4603 | 1.1722 | 1.8753 | 31.4133 | 108.7042
38897.5847 | 2358 | 9 | 38897.5847 | 2117 | 8 | 1253 | 1437 | 143.956 | 0.54945 | 129.243 | 0.4884 | 1.4396 | 0.0054945 | 1.2924 | 0.004884 | 1.4341 | 1.2875 | 3.7608 | 17.2643 | 126.5816
38897.5848 | 2153 | 9 | 38897.5848 | 1883 | 8 | 1263.5 | 1447.5 | 131.4408 | 0.54945 | 114.9573 | 0.4884 | 1.3144 | 0.0054945 | 1.1496 | 0.004884 | 1.3089 | 1.1447 | 13.7777 | 30.8971 | 740.5919
38897.5849 | 1845 | 7 | 38897.5849 | 2211 | 9 | 1274.5 | 1458.5 | 112.6374 | 0.42735 | 134.9817 | 0.54945 | 1.1264 | 0.0042735 | 1.3498 | 0.0054945 | 1.1221 | 1.3443 | 33.8107 | 10.7282 | 819.9214
38897.585 | 2393 | 12 | 38897.585 | 1905 | 8 | 1285.5 | 1469.5 | 146.0928 | 0.7326 | 116.3004 | 0.4884 | 1.4609 | 0.007326 | 1.163 | 0.004884 | 1.4536 | 1.1581 | 2.1892 | 35.2173 | 85.4709
38897.5852 | 1985 | 8 | 38897.5852 | 2415 | 11 | 1296.5 | 1480.5 | 121.1844 | 0.4884 | 147.4359 | 0.67155 | 1.2118 | 0.004884 | 1.4744 | 0.0067155 | 1.207 | 1.4676 | 34.5117 | 1.2386 | 69.0272
38897.5853 | 2051 | 8 | 38897.5853 | 2263 | 12 | 1307 | 1491 | 125.2137 | 0.4884 | 138.1563 | 0.7326 | 1.2521 | 0.004884 | 1.3816 | 0.007326 | 1.2473 | 1.3742 | 20.2113 | 8.276 | 368.2049
38897.5854 | 2221 | 13 | 38897.5854 | 2417 | 9 | 1317.5 | 1501.5 | 135.5922 | 0.79365 | 147.558 | 0.54945 | 1.3559 | 0.0079365 | 1.4756 | 0.0054945 | 1.348 | 1.4701 | 20.5795 | 1.1581 | 18.5267
38897.5855 | 2111 | 12 | 38897.5855 | 2306 | 14 | 1328.5 | 1512.5 | 128.8767 | 0.7326 | 140.7814 | 0.8547 | 1.2888 | 0.007326 | 1.4078 | 0.008547 | 1.2814 | 1.3993 | 17.4802 | 6.2561 | 157.6847
38897.5856 | 2339 | 16 | 38897.5857 | 2291 | 14 | 1339.5 | 1523.5 | 142.7961 | 0.9768 | 139.8657 | 0.8547 | 1.428 | 0.009768 | 1.3987 | 0.008547 | 1.4182 | 1.3901 | 4.983 | 7.6842 | 39.8627
38897.5858 | 2341 | 15 | 38897.5858 | 2372 | 16 | 1350.5 | 1534.5 | 142.9182 | 0.91575 | 144.8107 | 0.9768 | 1.4292 | 0.0091575 | 1.4481 | 0.009768 | 1.42 | 1.4383 | 5.4449 | 3.5099 | 19.9792
38897.5859 | 2029 | 13 | 38897.5859 | 2264 | 15 | 1360.5 | 1544.5 | 123.8706 | 0.79365 | 138.2173 | 0.91575 | 1.2387 | 0.0079365 | 1.3822 | 0.0091575 | 1.2308 | 1.373 | 22.3473 | 8.2672 | 236.3492
38897.586 | 2368 | 19 | 38897.586 | 1897 | 14 | 1371.5 | 1555.5 | 144.5665 | 1.16 | 115.812 | 0.8547 | 1.4457 | 0.0116 | 1.1581 | 0.008547 | 1.4341 | 1.1496 | 3.3234 | 37.4471 | 82.2791
38897.5861 | 1960 | 19 | 38897.5862 | 2057 | 17 | 1382.5 | 1566.5 | 119.6581 | 1.16 | 125.58 | 1.0379 | 1.1966 | 0.0116 | 1.2558 | 0.010379 | 1.185 | 1.2454 | 26.2662 | 19.6114 | 401.597
38897.5863 | 1955 | 20 | 38897.5863 | 1967 | 19 | 1393.5 | 1577.5 | 119.3529 | 1.221 | 120.0855 | 1.16 | 1.1935 | 0.01221 | 1.2009 | 0.0116 | 1.1813 | 1.1893 | 26.3617 | 25.4477 | 476.0806
38897.5864 | 2214 | 27 | 38897.5864 | 2115 | 29 | 1404.5 | 1588.5 | 135.1648 | 1.6484 | 129.1209 | 1.7705 | 1.3516 | 0.016484 | 1.2912 | 0.017705 | 1.3352 | 1.2735 | 11.3096 | 18.003 | 114.9203
38897.5865 | 1988 | 424 | 38897.5865 | 1875 | 344 | 1414.5 | 1598.5 | 121.3675 | 25.8852 | 114.4689 | 21.0012 | 1.2137 | 0.25885 | 1.1447 | 0.21001 | 0.95482 | 0.93468 | 47.2301 | 70.9374 | 3.1692
38897.5866 | 1497 | 378 | 38897.5867 | 1702 | 450 | 1425.5 | 1609.5 | 91.3919 | 23.0769 | 103.9072 | 27.4725 | 0.91392 | 0.23077 | 1.0391 | 0.27473 | 0.68315 | 0.76435 | 149.165 | 78.1189 | 66.0627
38897.5868 | 2258 | 74 | 38897.5868 | 2259 | 72 | 1436.5 | 1620.5 | 137.851 | 4.5177 | 137.9121 | 4.3956 | 1.3785 | 0.045177 | 1.3791 | 0.043956 | 1.3333 | 1.3352 | 12.0244 | 11.6722 | 15.8732
38897.5869 | 1914 | 63 | 38897.5869 | 2103 | 71 | 1447.5 | 1631.5 | 116.8498 | 3.8462 | 128.3883 | 4.3346 | 1.1685 | 0.038462 | 1.2839 | 0.043346 | 1.13 | 1.2405 | 35.0458 | 18.6607 | 116.6676
38897.587 | 2102 | 70 | 38897.587 | 2131 | 70 | 1458.5 | 1642.5 | 128.3272 | 4.2735 | 130.0977 | 4.2735 | 1.2833 | 0.042735 | 1.301 | 0.042735 | 1.2405 | 1.2582 | 20.7901 | 18.1743 | 59.8428
38897.5871 | 1813 | 61 | 38897.5872 | 2086 | 75 | 1468.5 | 1652.5 | 110.6838 | 3.7241 | 127.3504 | 4.5788 | 1.1068 | 0.037241 | 1.2735 | 0.045788 | 1.0696 | 1.2277 | 43.8825 | 19.4762 | 152.4256

## AvgC-C
Average Conductor to Conductor Resistances
Penlight Test 1 |  |  | 2006-06-29 | 13:39
XLPE | 3-C | Tray
475 C | 17.7 kW/m2
Penlight Time | C1-C |  | Penlight Time | C2-C | Penlight Time | C3-C | Penlight Time | C4-C | Penlight Time | Minimums
-181.5 | 244571.3327 |  | -179 | 244337.9994 | -177.8333 | 244704.6661 | -176.6667 | 245004.6661 | -181.5 | 244337.9994
-170.5 | 244571.3327 |  | -168.3333 | 244337.9994 | -167 | 244704.6661 | -165.8333 | 245004.6661 | -170.5 | 244337.9994
-159.8333 | 244571.3327 |  | -157.5 | 244337.9994 | -156.1667 | 244704.6661 | -155.1667 | 245004.6661 | -159.8333 | 244337.9994
-149.1667 | 244571.3327 |  | -146.5 | 244337.9994 | -145.5 | 244704.6661 | -144.1667 | 245004.6661 | -149.1667 | 244337.9994
-138.5 | 244571.3327 |  | -135.8333 | 203481.6659 | -134.8333 | 244704.6661 | -133.5 | 204148.3325 | -138.5 | 203481.6659
-127.5 | 244571.3327 |  | -125.1667 | 244337.9994 | -123.8333 | 244704.6661 | -122.8333 | 245004.6661 | -127.5 | 244337.9994
-116.5 | 203731.6659 |  | -114.5 | 244337.9994 | -113.1667 | 203864.9992 | -111.8333 | 245004.6661 | -116.5 | 203731.6659
-105.8333 | 244571.3327 |  | -103.5 | 244337.9994 | -102.1667 | 244704.6661 | -101.1667 | 245004.6661 | -105.8333 | 244337.9994
-95.1667 | 244571.3327 |  | -92.5 | 244337.9994 | -91.5 | 244704.6661 | -90.1667 | 245004.6661 | -95.1667 | 244337.9994
-84.5 | 244571.3327 |  | -81.8333 | 244337.9994 | -80.8333 | 244704.6661 | -79.5 | 245004.6661 | -84.5 | 244337.9994
-73.5 | 244571.3327 |  | -71.1667 | 244337.9994 | -69.8333 | 244704.6661 | -68.8333 | 245004.6661 | -73.5 | 244337.9994
-62.5 | 244571.3327 |  | -60.3333 | 244337.9994 | -59 | 244704.6661 | -57.8333 | 245004.6661 | -62.5 | 244337.9994
-51.8333 | 244571.3327 |  | -49.5 | 244337.9994 | -48.1667 | 203764.9992 | -47.1667 | 204064.9992 | -51.8333 | 203764.9992
-41 | 122235.6654 |  | -38.5 | 203598.3325 | -37.3333 | 203864.9992 | -36.1667 | 204248.3325 | -41 | 122235.6654
-30.3333 | 203831.6659 |  | -27.6667 | 203598.3325 | -26.6667 | 244704.6661 | -25.3333 | 245004.6661 | -30.3333 | 203598.3325
-19.5 | 244571.3327 |  | -17.1667 | 244337.9994 | -15.8333 | 244704.6661 | -14.8333 | 245004.6661 | -19.5 | 244337.9994
-8.3333 | 244571.3327 |  | -6.5 | 203714.9992 | -5.1667 | 163141.999 | -3.6667 | 204064.9992 | -8.3333 | 163141.999
2.3333 | 244504.6935 |  | 4.5 | 244204.7209 | 5.8333 | 244704.6661 | 7 | 244938.0268 | 2.3333 | 244204.7209
13 | 203814.9992 |  | 15.5 | 162858.6656 | 16.6667 | 204081.6659 | 17.8333 | 163391.999 | 13 | 162858.6656
23.6667 | 244571.3327 |  | 26.3333 | 244337.9994 | 27.3333 | 244704.6661 | 28.6667 | 245004.6661 | 23.6667 | 244337.9994
34.5 | 244571.3327 |  | 36.8333 | 244337.9994 | 38.1667 | 244704.6661 | 39.1667 | 245004.6661 | 34.5 | 244337.9994
45.5 | 162975.3323 |  | 47.6667 | 244337.9994 | 49 | 203864.9992 | 50.1667 | 204248.3325 | 45.5 | 162975.3323
56.1667 | 244571.3327 |  | 58.5 | 244337.9994 | 59.8333 | 244704.6661 | 60.8333 | 245004.6661 | 56.1667 | 244337.9994
66.8333 | 244571.3327 |  | 69.5 | 244337.9994 | 70.5 | 244704.6661 | 71.8333 | 245004.6661 | 66.8333 | 244337.9994
77.5 | 244571.3327 |  | 80.1667 | 244337.9994 | 81.3333 | 244704.6661 | 82.6667 | 245004.6661 | 77.5 | 244337.9994
88.5 | 244571.3327 |  | 91 | 244337.9994 | 92.1667 | 244704.6661 | 93.3333 | 245004.6661 | 88.5 | 244337.9994
99.5 | 244571.3327 |  | 101.6667 | 244337.9994 | 103 | 244704.6661 | 104.1667 | 245004.6661 | 99.5 | 244337.9994
110.3333 | 244571.3327 |  | 112.5 | 244337.9994 | 113.8333 | 244704.6661 | 115 | 245004.6661 | 110.3333 | 244337.9994
120.8333 | 203731.6659 |  | 123.5 | 244337.9994 | 124.5 | 203798.3599 | 125.8333 | 244938.0267 | 120.8333 | 203731.6659
131.5 | 244571.3327 |  | 134.1667 | 244271.3601 | 135.1667 | 244704.6661 | 136.5 | 244938.0268 | 131.5 | 244271.3601
142.5 | 244504.6935 |  | 144.8333 | 244271.3602 | 146.1667 | 244704.6661 | 147.1667 | 245004.6661 | 142.5 | 244271.3602
153.5 | 203748.36 |  | 155.5 | 244271.3602 | 156.8333 | 244704.6661 | 158.1667 | 204248.3325 | 153.5 | 203748.36
164.1667 | 244571.3327 |  | 166.5 | 162858.6656 | 167.8333 | 204081.6659 | 168.8333 | 204148.3325 | 164.1667 | 162858.6656
175 | 244571.3327 |  | 177.6667 | 244337.9994 | 178.5 | 244704.6661 | 179.8333 | 245004.6661 | 175 | 244337.9994
185.5 | 244404.7483 |  | 188.1667 | 244171.415 | 189.1667 | 244571.3876 | 190.5 | 244871.3875 | 185.5 | 244171.415
196.5 | 244571.3327 |  | 198.8333 | 244337.9994 | 200.1667 | 244704.6661 | 201.1667 | 245004.6661 | 196.5 | 244337.9994
207.5 | 244571.3327 |  | 209.6667 | 203481.6659 | 211 | 244704.6661 | 212.1667 | 204148.3325 | 207.5 | 203481.6659
218.3333 | 244571.3327 |  | 220.5 | 244271.3601 | 221.8333 | 244638.0267 | 223 | 244871.3875 | 218.3333 | 244271.3601
228.8333 | 244504.6935 |  | 231.5 | 244337.9994 | 232.5 | 244704.6661 | 233.8333 | 244938.0269 | 228.8333 | 244337.9994
239.5 | 244504.6935 |  | 242.1667 | 203714.9992 | 243.1667 | 204081.6659 | 244.5 | 244938.0269 | 239.5 | 203714.9992
250.5 | 244571.3327 |  | 252.8333 | 244337.9994 | 254.1667 | 244704.6661 | 255.1667 | 245004.6661 | 250.5 | 244337.9994
261.5 | 244571.3327 |  | 263.5 | 203714.9992 | 264.8333 | 204081.6659 | 266.1667 | 245004.6661 | 261.5 | 203714.9992
272.3333 | 203831.6659 |  | 274.5 | 203598.3325 | 275.8333 | 244704.6661 | 277 | 245004.6661 | 272.3333 | 203598.3325
282.8333 | 203731.6659 |  | 285.5 | 244337.9994 | 286.3333 | 203864.9992 | 287.6667 | 245004.6661 | 282.8333 | 203731.6659
293.5 | 244571.3327 |  | 296.1667 | 244337.9994 | 297.1667 | 244704.6661 | 298.5 | 245004.6661 | 293.5 | 244337.9994
304.5 | 244571.3327 |  | 306.8333 | 244337.9994 | 308.1667 | 244704.6661 | 309.1667 | 245004.6661 | 304.5 | 244337.9994
315.5 | 244571.3327 |  | 317.6667 | 244337.9994 | 319 | 203764.9992 | 320.1667 | 204064.9992 | 315.5 | 203764.9992
326.1667 | 203831.6659 |  | 328.5 | 203598.3325 | 329.8333 | 244704.6661 | 330.8333 | 245004.6661 | 326.1667 | 203598.3325
336.8333 | 203665.0267 |  | 339.5 | 244337.9994 | 340.5 | 203864.9992 | 341.8333 | 244938.0269 | 336.8333 | 203665.0267
347.5 | 244571.3327 |  | 350.3333 | 244337.9994 | 351.1667 | 244704.6661 | 352.6667 | 245004.6661 | 347.5 | 244337.9994
358.5 | 244571.3327 |  | 360.8333 | 203714.9992 | 362.1667 | 204015.0265 | 363.1667 | 244938.0267 | 358.5 | 203714.9992
369.5 | 244571.3327 |  | 371.5 | 244337.9994 | 372.8333 | 203764.9992 | 374.1667 | 204064.9992 | 369.5 | 203764.9992
380.1667 | 244504.6935 |  | 382.5 | 244337.9994 | 383.8333 | 203698.3599 | 384.8333 | 204064.9992 | 380.1667 | 203698.3599
390.8333 | 244571.3327 |  | 393.5 | 244337.9994 | 394.5 | 244704.6661 | 395.8333 | 245004.6661 | 390.8333 | 244337.9994
401.5 | 244571.3327 |  | 404.1667 | 244337.9994 | 405.1667 | 244704.6661 | 406.5 | 245004.6661 | 401.5 | 244337.9994
412.5 | 244571.3327 |  | 414.8333 | 244337.9994 | 416.1667 | 244704.6661 | 417.1667 | 245004.6661 | 412.5 | 244337.9994
423.5 | 244571.3327 |  | 425.5 | 244337.9994 | 426.8333 | 244704.6661 | 428.1667 | 245004.6661 | 423.5 | 244337.9994
434.1667 | 244571.3327 |  | 436.5 | 244271.3601 | 437.8333 | 244704.6661 | 438.8333 | 244938.0268 | 434.1667 | 244271.3601
444.8333 | 244571.3327 |  | 447.5 | 244337.9994 | 448.5 | 244704.6661 | 449.8333 | 245004.6661 | 444.8333 | 244337.9994
455.5 | 244571.3327 |  | 458.1667 | 244337.9994 | 459.1667 | 244704.6661 | 460.5 | 245004.6661 | 455.5 | 244337.9994
466.5 | 244571.3327 |  | 468.8333 | 244337.9994 | 470.1667 | 244704.6661 | 471.1667 | 245004.6661 | 466.5 | 244337.9994
477.3333 | 244571.3327 |  | 479.5 | 244337.9994 | 480.8333 | 244704.6661 | 482 | 245004.6661 | 477.3333 | 244337.9994
488 | 203731.6659 |  | 490.5 | 244337.9994 | 491.6667 | 203864.9992 | 492.8333 | 245004.6661 | 488 | 203731.6659
498.8333 | 244571.3327 |  | 501.5 | 244337.9994 | 502.3333 | 244704.6661 | 503.6667 | 245004.6661 | 498.8333 | 244337.9994
509.5 | 244571.3327 |  | 512 | 244337.9994 | 513.1667 | 244704.6661 | 514.3333 | 245004.6661 | 509.5 | 244337.9994
520.5 | 244571.3327 |  | 522.6667 | 244337.9994 | 524 | 244704.6661 | 525.1667 | 245004.6661 | 520.5 | 244337.9994
531.3333 | 244571.3327 |  | 533.5 | 244337.9994 | 534.8333 | 244704.6661 | 536 | 245004.6661 | 531.3333 | 244337.9994
542.1667 | 244571.3327 |  | 544.5 | 244337.9994 | 545.8333 | 244704.6661 | 546.8333 | 245004.6661 | 542.1667 | 244337.9994
552.8333 | 244571.3327 |  | 555.5 | 244337.9994 | 556.5 | 244704.6661 | 557.8333 | 245004.6661 | 552.8333 | 244337.9994
563.5 | 244571.3327 |  | 566.1667 | 244337.9994 | 567.1667 | 244704.6661 | 568.5 | 245004.6661 | 563.5 | 244337.9994
574.5 | 244571.3327 |  | 576.6667 | 244337.9994 | 578 | 244704.6661 | 579.1667 | 245004.6661 | 574.5 | 244337.9994
585.5 | 244571.3327 |  | 587.5 | 244337.9994 | 588.8333 | 244704.6661 | 590.1667 | 245004.6661 | 585.5 | 244337.9994
596.1667 | 244571.3327 |  | 598.5 | 244337.9994 | 599.8333 | 244638.0267 | 600.8333 | 244938.0267 | 596.1667 | 244337.9994
606.8333 | 244571.3327 |  | 609.5 | 244337.9994 | 610.3333 | 244704.6661 | 611.6667 | 245004.6661 | 606.8333 | 244337.9994
617.5 | 244571.3327 |  | 620.1667 | 244337.9994 | 621.1667 | 244704.6661 | 622.5 | 245004.6661 | 617.5 | 244337.9994
628.5 | 244571.3327 |  | 630.8333 | 244337.9994 | 632.1667 | 244704.6661 | 633.1667 | 245004.6661 | 628.5 | 244337.9994
639.5 | 244571.3327 |  | 641.5 | 244337.9994 | 642.8333 | 244704.6661 | 644.1667 | 245004.6661 | 639.5 | 244337.9994
650.1667 | 244571.3327 |  | 652.5 | 244337.9994 | 653.8333 | 244704.6661 | 654.8333 | 245004.6661 | 650.1667 | 244337.9994
660.6667 | 244571.3327 |  | 663.3333 | 244337.9994 | 664.3333 | 244704.6661 | 665.6667 | 245004.6661 | 660.6667 | 244337.9994
671.5 | 244571.3327 |  | 674 | 244337.9994 | 675.1667 | 244704.6661 | 676.3333 | 245004.6661 | 671.5 | 244337.9994
682.5 | 244571.3327 |  | 684.6667 | 244337.9994 | 686 | 244704.6661 | 687.1667 | 245004.6661 | 682.5 | 244337.9994
693.3333 | 203731.6659 |  | 695.5 | 244337.9994 | 696.8333 | 203864.9992 | 698 | 245004.6661 | 693.3333 | 203731.6659
704 | 244571.3327 |  | 706.5 | 244337.9994 | 707.6667 | 244704.6661 | 708.8333 | 245004.6661 | 704 | 244337.9994
714.6667 | 244571.3327 |  | 717.3333 | 244337.9994 | 718.3333 | 244704.6661 | 719.6667 | 245004.6661 | 714.6667 | 244337.9994
725.5 | 244571.3327 |  | 728 | 244337.9994 | 729.1667 | 244704.6661 | 730.3333 | 245004.6661 | 725.5 | 244337.9994
736.5 | 244571.3327 |  | 738.6667 | 244337.9994 | 740 | 244704.6661 | 741.1667 | 245004.6661 | 736.5 | 244337.9994
747.3333 | 244571.3327 |  | 749.5 | 244337.9994 | 750.8333 | 244704.6661 | 752 | 245004.6661 | 747.3333 | 244337.9994
758 | 176465.4615 |  | 760.5 | 244337.9994 | 761.6667 | 244704.6661 | 762.8333 | 176898.7948 | 758 | 176465.4615
768.6667 | 163226.8583 |  | 771.3333 | 244271.3603 | 772.3333 | 244638.0269 | 773.6667 | 163660.1917 | 768.6667 | 163226.8583
779.5 | 163124.7328 |  | 782 | 101380.7849 | 783.1667 | 126157.8924 | 784.3333 | 57201.6664 | 779.5 | 57201.6664
790.5 | 162851.2574 |  | 792.8333 | 92216.2289 | 794.1667 | 87562.7763 | 795.1667 | 10029.7445 | 790.5 | 10029.7445
801.3333 | 86688.6799 |  | 803.5 | 85158.6091 | 804.8333 | 10364.6245 | 806 | 2745.1839 | 801.3333 | 2745.1839
812 | 3580.458 |  | 814.5 | 7082.9519 | 815.6667 | 7294.5381 | 816.8333 | 1207.8656 | 812 | 1207.8656
822.6667 | 1793.2057 |  | 825.3333 | 1418.6025 | 826.3333 | 1606.2781 | 827.6667 | 457.3142 | 822.6667 | 457.3142
833.5 | 893.1807 |  | 836 | 768.0272 | 837.1667 | 562.5325 | 838.3333 | 162.7587 | 833.5 | 162.7587
844.5 | 238.9261 |  | 846.6667 | 392.3473 | 848 | 167.093 | 849.1667 | 136.0171 | 844.5 | 136.0171
855.5 | 179.5599 |  | 857.5 | 380.9949 | 858.8333 | 161.8739 | 860.1667 | 155.6156 | 855.5 | 155.6156
866 | 153.4468 |  | 868.5 | 279.4747 | 869.6667 | 97.2278 | 870.8333 | 140.6942 | 866 | 97.2278
876.6667 | 148.041 |  | 879.3333 | 205.9063 | 880.3333 | 111.0268 | 881.6667 | 53.5967 | 876.6667 | 53.5967
887.5 | 34.298 |  | 890 | 21.0966 | 891.1667 | 24.6751 | 892.3333 | 30.2038 | 887.5 | 21.0966
898.5 | 19.2609 |  | 900.6667 | 32.8918 | 902 | 27.6061 | 903.1667 | 30.8752 | 898.5 | 19.2609
909.1667 | 16.8352 |  | 911.5 | 39.3728 | 912.8333 | 37.8515 | 913.8333 | 36.3465 | 909.1667 | 16.8352
920 | 37.9474 |  | 922.5 | 69.0487 | 923.6667 | 72.7464 | 924.8333 | 61.6247 | 920 | 37.9474
930.6667 | 39.1769 |  | 933.3333 | 31.4801 | 934.3333 | 30.4177 | 935.6667 | 49.0372 | 930.6667 | 30.4177
941.5 | 25.6858 |  | 944 | 39.5027 | 945.1667 | 46.4211 | 946.3333 | 47.5942 | 941.5 | 25.6858
952.5 | 64.5118 |  | 954.6667 | 55.5924 | 956 | 3.0995 | 957.1667 | 47.6069 | 952.5 | 3.0995
963.1667 | 41.6447 |  | 965.5 | 45.6057 | 966.8333 | 24.9496 | 967.8333 | 44.695 | 963.1667 | 24.9496
974.1667 | 36.1319 |  | 976.5 | 28.6011 | 977.8333 | 28.0186 | 978.8333 | 42.8172 | 974.1667 | 28.0186
984.8333 | 23.8244 |  | 987.5 | 39.0951 | 988.3333 | 28.3278 | 989.6667 | 51.8596 | 984.8333 | 23.8244
995.5 | 39.9812 |  | 998.1667 | 43.8448 | 999.1667 | 36.5806 | 1000.5 | 59.8693 | 995.5 | 36.5806
1006.5 | 29.052 |  | 1008.8333 | 31.3261 | 1010.1667 | 38.6033 | 1011.1667 | 58.973 | 1006.5 | 29.052
1017.3333 | 177.339 |  | 1019.5 | 219.8034 | 1020.8333 | 181.6208 | 1022 | 230.3512 | 1017.3333 | 177.339
1028 | 214.5175 |  | 1030.5 | 149.4721 | 1031.6667 | 241.5103 | 1032.8333 | 261.6447 | 1028 | 149.4721
1038.6667 | 364.5 |  | 1041.3333 | 169.7926 | 1042.3333 | 96.7652 | 1043.6667 | 494.8851 | 1038.6667 | 96.7652
1049.5 | 533.5344 |  | 1052 | 216.9725 | 1053.1667 | 313.9745 | 1054.3333 | 202.7473 | 1049.5 | 202.7473
1060.5 | 196.2591 |  | 1062.8333 | 378.1422 | 1064.1667 | 311.4119 | 1065.1667 | 106.6987 | 1060.5 | 106.6987
1071.3333 | 456.2485 |  | 1073.5 | 70.1205 | 1074.8333 | 280.423 | 1076 | 689.3983 | 1071.3333 | 70.1205
1082 | 301.1726 |  | 1084.5 | 431.7339 | 1085.6667 | 157.6654 | 1086.8333 | 187.3413 | 1082 | 157.6654
1092.6667 | 1535.9608 |  | 1095.3333 | 216.3863 | 1096.3333 | 535.5254 | 1097.6667 | 922.6072 | 1092.6667 | 216.3863
1103.5 | 275.6811 |  | 1106 | 586.6987 | 1107.1667 | 202.6686 | 1108.3333 | 533.5359 | 1103.5 | 202.6686
1114.5 | 484.9619 |  | 1116.6667 | 1160.3028 | 1118 | 890.6193 | 1119.1667 | 491.9907 | 1114.5 | 484.9619
1125.3333 | 997.2125 |  | 1127.5 | 92.1791 | 1128.8333 | 944.9878 | 1130 | 267.0011 | 1125.3333 | 92.1791
1136 | 1268.6966 |  | 1138.5 | 955.1617 | 1139.6667 | 434.5987 | 1140.8333 | 706.9809 | 1136 | 434.5987
1146.6667 | 956.9372 |  | 1149.3333 | 483.2852 | 1150.3333 | 1158.6715 | 1151.6667 | 680.878 | 1146.6667 | 483.2852
1157.5 | 765.126 |  | 1160 | 832.2549 | 1161.1667 | 468.5469 | 1162.3333 | 564.9099 | 1157.5 | 468.5469
1168.5 | 686.8429 |  | 1170.6667 | 1176.8415 | 1172 | 739.582 | 1173.1667 | 1057.296 | 1168.5 | 686.8429
1179.3333 | 143.305 |  | 1181.5 | 788.5264 | 1182.8333 | 480.9694 | 1184 | 465.464 | 1179.3333 | 143.305
1189.8333 | 702.0119 |  | 1192.5 | 1102.8326 | 1193.5 | 624.4817 | 1194.8333 | 349.5125 | 1189.8333 | 349.5125
1200.6667 | 825.0428 |  | 1203.3333 | 650.5257 | 1204.3333 | 1104.0495 | 1205.6667 | 581.9192 | 1200.6667 | 581.9192
1211.5 | 380.8797 |  | 1214 | 191.719 | 1215.1667 | 407.9653 | 1216.3333 | 434.1586 | 1211.5 | 191.719
1222.5 | 720.5533 |  | 1224.6667 | 302.0343 | 1226 | 672.7903 | 1227.1667 | 246.1834 | 1222.5 | 246.1834
1233.3333 | 270.7316 |  | 1235.5 | 678.1021 | 1236.8333 | 302.2791 | 1238 | 510.6668 | 1233.3333 | 270.7316
1244 | 288.9147 |  | 1246.5 | 71.7099 | 1247.6667 | 105.3524 | 1248.8333 | 283.6282 | 1244 | 71.7099
1254.6667 | 437.6771 |  | 1257.3333 | 312.3722 | 1258.3333 | 281.9287 | 1259.6667 | 403.455 | 1254.6667 | 281.9287
1265.5 | 745.7464 |  | 1268 | 450.4664 | 1269.1667 | 513.2985 | 1270.3333 | 301.5273 | 1265.5 | 301.5273
1276.5 | 450.2551 |  | 1278.6667 | 587.9272 | 1280 | 536.0718 | 1281.1667 | 248.8569 | 1276.5 | 248.8569
1287.3333 | 377.853 |  | 1289.5 | 109.1228 | 1290.8333 | 382.3976 | 1292 | 64.6567 | 1287.3333 | 64.6567
1298 | 301.7736 |  | 1300.5 | 145.5593 | 1301.6667 | 535.4658 | 1302.8333 | 348.8853 | 1298 | 145.5593
1308.6667 | 335.0126 |  | 1311.3333 | 238.4639 | 1312.3333 | 155.9921 | 1313.6667 | 322.5509 | 1308.6667 | 155.9921
1319.5 | 149.4066 |  | 1322 | 383.1524 | 1323.1667 | 674.9738 | 1324.3333 | 525.8426 | 1319.5 | 149.4066
1330.5 | 433.0482 |  | 1332.5 | 358.1575 | 1333.8333 | 440.2235 | 1335.1667 | 289.4954 | 1330.5 | 289.4954
1341.1667 | 82.558 |  | 1343.5 | 216.2561 | 1344.8333 | 293.2703 | 1345.8333 | 172.2863 | 1341.1667 | 82.558
1351.8333 | 385.586 |  | 1354.5 | 64.3466 | 1355.5 | 380.0036 | 1356.8333 | 80.7456 | 1351.8333 | 64.3466
1362.5 | 246.7363 |  | 1365.1667 | 214.5941 | 1366.1667 | 368.5172 | 1367.5 | 111.2021 | 1362.5 | 111.2021
1373.5 | 232.095 |  | 1376 | 261.3742 | 1377.1667 | 466.7073 | 1378.3333 | 194.2368 | 1373.5 | 194.2368
1384.5 | 239.9901 |  | 1386.6667 | 181.964 | 1388 | 199.162 | 1389.1667 | 257.7327 | 1384.5 | 181.964
1395.1667 | 264.314 |  | 1397.5 | 287.8398 | 1398.8333 | 210.4309 | 1399.8333 | 87.2397 | 1395.1667 | 87.2397
1405.8333 | 124.1349 |  | 1408.5 | 99.6291 | 1409.5 | 143.1775 | 1410.8333 | 151.3513 | 1405.8333 | 99.6291
1416.5 | 24.7532 |  | 1419.1667 | 8.8298 | 1420.1667 | 24.7979 | 1421.5 | 26.0101 | 1416.5 | 8.8298
1427.5 | 79.467 |  | 1429.8333 | 46.0519 | 1431.1667 | 57.6262 | 1432.1667 | 57.025 | 1427.5 | 46.0519
1438.5 | 131.0657 |  | 1440.5 | 24.1628 | 1441.8333 | 94.1001 | 1443.1667 | 85.4534 | 1438.5 | 24.1628
1449.1667 | 115.7257 |  | 1451.5 | 114.6785 | 1452.8333 | 78.9667 | 1453.8333 | 98.445 | 1449.1667 | 78.9667
1459.8333 | 116.2396 |  | 1462.5 | 52.1724 | 1463.5 | 112.1315 | 1464.8333 | 62.2388 | 1459.8333 | 52.1724
1470.5 | 110.6765 |  | 1473.1667 | 111.9438 | 1474.1667 | 109.6394 | 1475.5 | 24.4486 | 1470.5 | 24.4486

## C-G AVG
Average Conductor to Ground Resistances
Penlight Test 1 |  |  | 2006-06-29 | 13:39
XLPE | 3-C | Tray
475 C | 17.7 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-181.5 | 244571.3333 |  | -179 | 244338 | -177.8333 | 244704.6667 | -176.6667 | 245004.6667 | -181.5 | 244338
-170.5 | 244571.3333 |  | -168.3333 | 244338 | -167 | 244704.6667 | -165.8333 | 245004.6667 | -170.5 | 244338
-159.8333 | 244571.3333 |  | -157.5 | 244338 | -156.1667 | 244704.6667 | -155.1667 | 245004.6667 | -159.8333 | 244338
-149.1667 | 244571.3333 |  | -146.5 | 244338 | -145.5 | 244704.6667 | -144.1667 | 245004.6667 | -149.1667 | 244338
-138.5 | 244571.3333 |  | -135.8333 | 203481.6667 | -134.8333 | 244704.6667 | -133.5 | 245004.6667 | -138.5 | 203481.6667
-127.5 | 244571.3333 |  | -125.1667 | 203598.3333 | -123.8333 | 244704.6667 | -122.8333 | 245004.6667 | -127.5 | 203598.3333
-116.5 | 203731.6667 |  | -114.5 | 244338 | -113.1667 | 244704.6667 | -111.8333 | 245004.6667 | -116.5 | 203731.6667
-105.8333 | 244571.3333 |  | -103.5 | 244338 | -102.1667 | 244704.6667 | -101.1667 | 245004.6667 | -105.8333 | 244338
-95.1667 | 244571.3333 |  | -92.5 | 244338 | -91.5 | 244704.6667 | -90.1667 | 204148.3333 | -95.1667 | 204148.3333
-84.5 | 244571.3333 |  | -81.8333 | 244338 | -80.8333 | 244704.6667 | -79.5 | 204248.3333 | -84.5 | 204248.3333
-73.5 | 244571.3333 |  | -71.1667 | 244338 | -69.8333 | 244704.6667 | -68.8333 | 245004.6667 | -73.5 | 244338
-62.5 | 244571.3333 |  | -60.3333 | 244338 | -59 | 244704.6667 | -57.8333 | 245004.6667 | -62.5 | 244338
-51.8333 | 244571.3333 |  | -49.5 | 244338 | -48.1667 | 203765 | -47.1667 | 163208.6667 | -51.8333 | 163208.6667
-41 | 122235.6667 |  | -38.5 | 203598.3333 | -37.3333 | 203865 | -36.1667 | 204248.3333 | -41 | 122235.6667
-30.3333 | 203831.6667 |  | -27.6667 | 203598.3333 | -26.6667 | 244704.6667 | -25.3333 | 245004.6667 | -30.3333 | 203598.3333
-19.5 | 244571.3333 |  | -17.1667 | 244338 | -15.8333 | 244704.6667 | -14.8333 | 245004.6667 | -19.5 | 244338
-8.3333 | 244571.3333 |  | -6.5 | 162975.3333 | -5.1667 | 203765 | -3.6667 | 245004.6667 | -8.3333 | 162975.3333
2.3333 | 199166652.8133 |  | 4.5 | 200308063.48 | 5.8333 | 244704.6667 | 7 | 245004.6667 | 2.3333 | 244704.6667
13 | 203815 |  | 15.5 | 162858.6667 | 16.6667 | 244704.6667 | 17.8333 | 245004.6667 | 13 | 162858.6667
23.6667 | 244571.3333 |  | 26.3333 | 244338 | 27.3333 | 244704.6667 | 28.6667 | 204148.3333 | 23.6667 | 204148.3333
34.5 | 244571.3333 |  | 36.8333 | 244338 | 38.1667 | 244704.6667 | 39.1667 | 204148.3333 | 34.5 | 204148.3333
45.5 | 162975.3333 |  | 47.6667 | 244338 | 49 | 244704.6667 | 50.1667 | 204148.3333 | 45.5 | 162975.3333
56.1667 | 244571.3333 |  | 58.5 | 244338 | 59.8333 | 244704.6667 | 60.8333 | 245004.6667 | 56.1667 | 244338
66.8333 | 244571.3333 |  | 69.5 | 244338 | 70.5 | 244704.6667 | 71.8333 | 204248.3333 | 66.8333 | 204248.3333
77.5 | 244571.3333 |  | 80.1667 | 244338 | 81.3333 | 244704.6667 | 82.6667 | 245004.6667 | 77.5 | 244338
88.5 | 244571.3333 |  | 91 | 244338 | 92.1667 | 244704.6667 | 93.3333 | 204248.3333 | 88.5 | 204248.3333
99.5 | 244571.3333 |  | 101.6667 | 244338 | 103 | 244704.6667 | 104.1667 | 245004.6667 | 99.5 | 244338
110.3333 | 244571.3333 |  | 112.5 | 244338 | 113.8333 | 244704.6667 | 115 | 204248.3333 | 110.3333 | 204248.3333
120.8333 | 203731.6667 |  | 123.5 | 244338 | 124.5 | 201125890.1467 | 125.8333 | 245004.6667 | 120.8333 | 203731.6667
131.5 | 244571.3333 |  | 134.1667 | 200308063.48 | 135.1667 | 244704.6667 | 136.5 | 245004.6667 | 131.5 | 244571.3333
142.5 | 199166652.8133 |  | 144.8333 | 244338 | 146.1667 | 203865 | 147.1667 | 245004.6667 | 142.5 | 203865
153.5 | 199125896.48 |  | 155.5 | 244338 | 156.8333 | 244704.6667 | 158.1667 | 245004.6667 | 153.5 | 244338
164.1667 | 244571.3333 |  | 166.5 | 162858.6667 | 167.8333 | 204081.6667 | 168.8333 | 204148.3333 | 164.1667 | 162858.6667
175 | 244571.3333 |  | 177.6667 | 203598.3333 | 178.5 | 244704.6667 | 179.8333 | 245004.6667 | 175 | 203598.3333
185.5 | 298709139.5533 |  | 188.1667 | 197987302.48 | 189.1667 | 201125890.1467 | 190.5 | 245004.6667 | 185.5 | 245004.6667
196.5 | 244571.3333 |  | 198.8333 | 203598.3333 | 200.1667 | 244704.6667 | 201.1667 | 204065 | 196.5 | 203598.3333
207.5 | 244571.3333 |  | 209.6667 | 203481.6667 | 211 | 244704.6667 | 212.1667 | 204248.3333 | 207.5 | 203481.6667
218.3333 | 244571.3333 |  | 220.5 | 200308063.48 | 221.8333 | 201125890.1467 | 223 | 245004.6667 | 218.3333 | 244571.3333
228.8333 | 199329544.8133 |  | 231.5 | 244338 | 232.5 | 244704.6667 | 233.8333 | 245004.6667 | 228.8333 | 244338
239.5 | 199329544.8133 |  | 242.1667 | 203715 | 243.1667 | 204081.6667 | 244.5 | 204148.3333 | 239.5 | 203715
250.5 | 244571.3333 |  | 252.8333 | 203598.3333 | 254.1667 | 244704.6667 | 255.1667 | 245004.6667 | 250.5 | 203598.3333
261.5 | 244571.3333 |  | 263.5 | 203715 | 264.8333 | 244704.6667 | 266.1667 | 245004.6667 | 261.5 | 203715
272.3333 | 203831.6667 |  | 274.5 | 244338 | 275.8333 | 244704.6667 | 277 | 245004.6667 | 272.3333 | 203831.6667
282.8333 | 203731.6667 |  | 285.5 | 244338 | 286.3333 | 244704.6667 | 287.6667 | 245004.6667 | 282.8333 | 203731.6667
293.5 | 244571.3333 |  | 296.1667 | 244338 | 297.1667 | 244704.6667 | 298.5 | 245004.6667 | 293.5 | 244338
304.5 | 244571.3333 |  | 306.8333 | 244338 | 308.1667 | 244704.6667 | 309.1667 | 204148.3333 | 304.5 | 204148.3333
315.5 | 244571.3333 |  | 317.6667 | 244338 | 319 | 203765 | 320.1667 | 245004.6667 | 315.5 | 203765
326.1667 | 203831.6667 |  | 328.5 | 244338 | 329.8333 | 203865 | 330.8333 | 245004.6667 | 326.1667 | 203831.6667
336.8333 | 199288705.1467 |  | 339.5 | 244338 | 340.5 | 244704.6667 | 341.8333 | 245004.6667 | 336.8333 | 244338
347.5 | 244571.3333 |  | 350.3333 | 244338 | 351.1667 | 244704.6667 | 352.6667 | 245004.6667 | 347.5 | 244338
358.5 | 244571.3333 |  | 360.8333 | 203715 | 362.1667 | 201125890.1467 | 363.1667 | 204248.3333 | 358.5 | 203715
369.5 | 244571.3333 |  | 371.5 | 244338 | 372.8333 | 203765 | 374.1667 | 245004.6667 | 369.5 | 203765
380.1667 | 200145004.8133 |  | 382.5 | 244338 | 383.8333 | 203765 | 384.8333 | 245004.6667 | 380.1667 | 203765
390.8333 | 244571.3333 |  | 393.5 | 244338 | 394.5 | 203865 | 395.8333 | 245004.6667 | 390.8333 | 203865
401.5 | 244571.3333 |  | 404.1667 | 244338 | 405.1667 | 244704.6667 | 406.5 | 245004.6667 | 401.5 | 244338
412.5 | 244571.3333 |  | 414.8333 | 244338 | 416.1667 | 244704.6667 | 417.1667 | 245004.6667 | 412.5 | 244338
423.5 | 244571.3333 |  | 425.5 | 244338 | 426.8333 | 244704.6667 | 428.1667 | 245004.6667 | 423.5 | 244338
434.1667 | 244571.3333 |  | 436.5 | 200308063.48 | 437.8333 | 244704.6667 | 438.8333 | 245004.6667 | 434.1667 | 244571.3333
444.8333 | 244571.3333 |  | 447.5 | 244338 | 448.5 | 244704.6667 | 449.8333 | 245004.6667 | 444.8333 | 244338
455.5 | 244571.3333 |  | 458.1667 | 244338 | 459.1667 | 244704.6667 | 460.5 | 245004.6667 | 455.5 | 244338
466.5 | 244571.3333 |  | 468.8333 | 244338 | 470.1667 | 244704.6667 | 471.1667 | 245004.6667 | 466.5 | 244338
477.3333 | 244571.3333 |  | 479.5 | 244338 | 480.8333 | 244704.6667 | 482 | 204148.3333 | 477.3333 | 204148.3333
488 | 203731.6667 |  | 490.5 | 244338 | 491.6667 | 244704.6667 | 492.8333 | 204148.3333 | 488 | 203731.6667
498.8333 | 244571.3333 |  | 501.5 | 244338 | 502.3333 | 244704.6667 | 503.6667 | 245004.6667 | 498.8333 | 244338
509.5 | 244571.3333 |  | 512 | 244338 | 513.1667 | 204081.6667 | 514.3333 | 245004.6667 | 509.5 | 204081.6667
520.5 | 244571.3333 |  | 522.6667 | 244338 | 524 | 203865 | 525.1667 | 245004.6667 | 520.5 | 203865
531.3333 | 244571.3333 |  | 533.5 | 244338 | 534.8333 | 244704.6667 | 536 | 204065 | 531.3333 | 204065
542.1667 | 244571.3333 |  | 544.5 | 244338 | 545.8333 | 244704.6667 | 546.8333 | 245004.6667 | 542.1667 | 244338
552.8333 | 244571.3333 |  | 555.5 | 203598.3333 | 556.5 | 244704.6667 | 557.8333 | 245004.6667 | 552.8333 | 203598.3333
563.5 | 244571.3333 |  | 566.1667 | 244338 | 567.1667 | 244704.6667 | 568.5 | 245004.6667 | 563.5 | 244338
574.5 | 244571.3333 |  | 576.6667 | 244338 | 578 | 244704.6667 | 579.1667 | 245004.6667 | 574.5 | 244338
585.5 | 244571.3333 |  | 587.5 | 244338 | 588.8333 | 244704.6667 | 590.1667 | 204065 | 585.5 | 204065
596.1667 | 244571.3333 |  | 598.5 | 244338 | 599.8333 | 201125890.1467 | 600.8333 | 245004.6667 | 596.1667 | 244338
606.8333 | 244571.3333 |  | 609.5 | 244338 | 610.3333 | 244704.6667 | 611.6667 | 245004.6667 | 606.8333 | 244338
617.5 | 244571.3333 |  | 620.1667 | 244338 | 621.1667 | 244704.6667 | 622.5 | 245004.6667 | 617.5 | 244338
628.5 | 244571.3333 |  | 630.8333 | 244338 | 632.1667 | 244704.6667 | 633.1667 | 204065 | 628.5 | 204065
639.5 | 244571.3333 |  | 641.5 | 203598.3333 | 642.8333 | 244704.6667 | 644.1667 | 245004.6667 | 639.5 | 203598.3333
650.1667 | 244571.3333 |  | 652.5 | 244338 | 653.8333 | 244704.6667 | 654.8333 | 245004.6667 | 650.1667 | 244338
660.6667 | 244571.3333 |  | 663.3333 | 244338 | 664.3333 | 244704.6667 | 665.6667 | 245004.6667 | 660.6667 | 244338
671.5 | 244571.3333 |  | 674 | 244338 | 675.1667 | 244704.6667 | 676.3333 | 245004.6667 | 671.5 | 244338
682.5 | 244571.3333 |  | 684.6667 | 244338 | 686 | 244704.6667 | 687.1667 | 245004.6667 | 682.5 | 244338
693.3333 | 203731.6667 |  | 695.5 | 244338 | 696.8333 | 244704.6667 | 698 | 245004.6667 | 693.3333 | 203731.6667
704 | 244571.3333 |  | 706.5 | 244338 | 707.6667 | 244704.6667 | 708.8333 | 245004.6667 | 704 | 244338
714.6667 | 244571.3333 |  | 717.3333 | 244338 | 718.3333 | 244704.6667 | 719.6667 | 245004.6667 | 714.6667 | 244338
725.5 | 244571.3333 |  | 728 | 244338 | 729.1667 | 244704.6667 | 730.3333 | 245004.6667 | 725.5 | 244338
736.5 | 244571.3333 |  | 738.6667 | 244338 | 740 | 244704.6667 | 741.1667 | 245004.6667 | 736.5 | 244338
747.3333 | 244571.3333 |  | 749.5 | 244338 | 750.8333 | 244704.6667 | 752 | 245004.6667 | 747.3333 | 244338
758 | 190693.9358 |  | 760.5 | 244338 | 761.6667 | 244704.6667 | 762.8333 | 166990.4302 | 758 | 166990.4302
768.6667 | 165095.8153 |  | 771.3333 | 198028042.1467 | 772.3333 | 244704.6667 | 773.6667 | 167270.8718 | 768.6667 | 165095.8153
779.5 | 166479.2811 |  | 782 | 105957.0892 | 783.1667 | 170386.8645 | 784.3333 | 165095.7373 | 779.5 | 105957.0892
790.5 | 97918.3127 |  | 792.8333 | 198935052.5283 | 794.1667 | 39926989.7826 | 795.1667 | 11223.3809 | 790.5 | 11223.3809
801.3333 | 5531.1983 |  | 803.5 | 92712.6054 | 804.8333 | 18398.4325 | 806 | 2043.6582 | 801.3333 | 2043.6582
812 | 5891.3561 |  | 814.5 | 7700.5009 | 815.6667 | 6154.743 | 816.8333 | 2372.6843 | 812 | 2372.6843
822.6667 | 2334.5366 |  | 825.3333 | 6779.3996 | 826.3333 | 2528.371 | 827.6667 | 1582.2234 | 822.6667 | 1582.2234
833.5 | 2520.4458 |  | 836 | 10715.6585 | 837.1667 | 2643.8353 | 838.3333 | 1917.3727 | 833.5 | 1917.3727
844.5 | 6926.6519 |  | 846.6667 | 7694.0699 | 848 | 1365.0166 | 849.1667 | 1166.0359 | 844.5 | 1166.0359
855.5 | 1119.1504 |  | 857.5 | 35267.5649 | 858.8333 | 1778.1405 | 860.1667 | 1844.3032 | 855.5 | 1119.1504
866 | 1129.2062 |  | 868.5 | 3069.0616 | 869.6667 | 1171.8559 | 870.8333 | 6399.8117 | 866 | 1129.2062
876.6667 | 812.0662 |  | 879.3333 | 1928.3229 | 880.3333 | 5509.7209 | 881.6667 | 2518.6874 | 876.6667 | 812.0662
887.5 | 1922.2873 |  | 890 | 24905.6614 | 891.1667 | 847.1112 | 892.3333 | 1020.9926 | 887.5 | 847.1112
898.5 | 979.0944 |  | 900.6667 | 916.6363 | 902 | 2049.2102 | 903.1667 | 12872.6875 | 898.5 | 916.6363
909.1667 | 592.5009 |  | 911.5 | 1167.2641 | 912.8333 | 9326.8181 | 913.8333 | 1438.6974 | 909.1667 | 592.5009
920 | 679.3892 |  | 922.5 | 2359.9958 | 923.6667 | 2833.1873 | 924.8333 | 4408.9231 | 920 | 679.3892
930.6667 | 748.5863 |  | 933.3333 | 653.104 | 934.3333 | 2267.6087 | 935.6667 | 309.5633 | 930.6667 | 309.5633
941.5 | 369.372 |  | 944 | 370.6137 | 945.1667 | 241.5705 | 946.3333 | 167.8878 | 941.5 | 167.8878
952.5 | 56.2845 |  | 954.6667 | 232.33 | 956 | 30.9318 | 957.1667 | 81.2916 | 952.5 | 30.9318
963.1667 | 165.9018 |  | 965.5 | 127.1914 | 966.8333 | 1297.2939 | 967.8333 | 90.5836 | 963.1667 | 90.5836
974.1667 | 214.5772 |  | 976.5 | 162.9218 | 977.8333 | 412.8737 | 978.8333 | 94.4527 | 974.1667 | 94.4527
984.8333 | 134.6522 |  | 987.5 | 107.2917 | 988.3333 | 561.7496 | 989.6667 | 211.3955 | 984.8333 | 107.2917
995.5 | 291.0539 |  | 998.1667 | 173.4529 | 999.1667 | 360.5266 | 1000.5 | 165.679 | 995.5 | 165.679
1006.5 | 470.8903 |  | 1008.8333 | 85.8434 | 1010.1667 | 97.0655 | 1011.1667 | 39.8978 | 1006.5 | 39.8978
1017.3333 | 14.1899 |  | 1019.5 | 12.7356 | 1020.8333 | 16.1372 | 1022 | 21.7517 | 1017.3333 | 12.7356
1028 | 23.4038 |  | 1030.5 | 6.1769 | 1031.6667 | 53.3899 | 1032.8333 | 20.5288 | 1028 | 6.1769
1038.6667 | 116.8476 |  | 1041.3333 | 6.854 | 1042.3333 | 18.1833 | 1043.6667 | 20.9049 | 1038.6667 | 6.854
1049.5 | 22.3482 |  | 1052 | 14.4235 | 1053.1667 | 16.0066 | 1054.3333 | 28.2845 | 1049.5 | 14.4235
1060.5 | 18.406 |  | 1062.8333 | 6.4951 | 1064.1667 | 20.7994 | 1065.1667 | 10.1613 | 1060.5 | 6.4951
1071.3333 | 20.6142 |  | 1073.5 | 3.8364 | 1074.8333 | 7.6201 | 1076 | 20.7454 | 1071.3333 | 3.8364
1082 | 10.6018 |  | 1084.5 | 12.3982 | 1085.6667 | 19.9886 | 1086.8333 | 10.1817 | 1082 | 10.1817
1092.6667 | 29.4096 |  | 1095.3333 | 7.0274 | 1096.3333 | 17.4403 | 1097.6667 | 10.4549 | 1092.6667 | 7.0274
1103.5 | 9.791 |  | 1106 | 7.6959 | 1107.1667 | 15.0511 | 1108.3333 | 17.0109 | 1103.5 | 7.6959
1114.5 | 13.2838 |  | 1116.6667 | 19.9753 | 1118 | 23.6788 | 1119.1667 | 7.8557 | 1114.5 | 7.8557
1125.3333 | 13.3203 |  | 1127.5 | 21.7026 | 1128.8333 | 10.9964 | 1130 | 15.4705 | 1125.3333 | 10.9964
1136 | 21.5432 |  | 1138.5 | 14.56 | 1139.6667 | 4.7831 | 1140.8333 | 26.2191 | 1136 | 4.7831
1146.6667 | 12.1334 |  | 1149.3333 | 18.275 | 1150.3333 | 19.6081 | 1151.6667 | 22.4181 | 1146.6667 | 12.1334
1157.5 | 19.1444 |  | 1160 | 26.0722 | 1161.1667 | 23.7207 | 1162.3333 | 4.8757 | 1157.5 | 4.8757
1168.5 | 19.1493 |  | 1170.6667 | 18.6088 | 1172 | 11.2955 | 1173.1667 | 18.9527 | 1168.5 | 11.2955
1179.3333 | 10.3119 |  | 1181.5 | 24.432 | 1182.8333 | 14.662 | 1184 | 6.8762 | 1179.3333 | 6.8762
1189.8333 | 15.7265 |  | 1192.5 | 21.5394 | 1193.5 | 14.6986 | 1194.8333 | 9.1689 | 1189.8333 | 9.1689
1200.6667 | 15.6806 |  | 1203.3333 | 12.2442 | 1204.3333 | 17.8394 | 1205.6667 | 23.1913 | 1200.6667 | 12.2442
1211.5 | 5.4399 |  | 1214 | 21.6077 | 1215.1667 | 15.8665 | 1216.3333 | 20.4989 | 1211.5 | 5.4399
1222.5 | 20.1926 |  | 1224.6667 | 12.6806 | 1226 | 11.6677 | 1227.1667 | 13.5944 | 1222.5 | 11.6677
1233.3333 | 6.6146 |  | 1235.5 | 25.0997 | 1236.8333 | 8.8332 | 1238 | 20.1636 | 1233.3333 | 6.6146
1244 | 8.4109 |  | 1246.5 | 12.3518 | 1247.6667 | 15.7695 | 1248.8333 | 20.7529 | 1244 | 8.4109
1254.6667 | 8.6243 |  | 1257.3333 | 18.2225 | 1258.3333 | 14.459 | 1259.6667 | 15.7855 | 1254.6667 | 8.6243
1265.5 | 19.7133 |  | 1268 | 24.1104 | 1269.1667 | 12.446 | 1270.3333 | 15.752 | 1265.5 | 12.446
1276.5 | 21.4182 |  | 1278.6667 | 14.1304 | 1280 | 28.9981 | 1281.1667 | 7.87 | 1276.5 | 7.87
1287.3333 | 13.1245 |  | 1289.5 | 18.9737 | 1290.8333 | 20.5303 | 1292 | 9.3079 | 1287.3333 | 9.3079
1298 | 21.8603 |  | 1300.5 | 4.7726 | 1301.6667 | 18.4635 | 1302.8333 | 26.4992 | 1298 | 4.7726
1308.6667 | 12.948 |  | 1311.3333 | 13.0348 | 1312.3333 | 31.7572 | 1313.6667 | 17.9162 | 1308.6667 | 12.948
1319.5 | 32.1609 |  | 1322 | 17.1368 | 1323.1667 | 20.1475 | 1324.3333 | 14.3994 | 1319.5 | 14.3994
1330.5 | 17.3345 |  | 1332.5 | 22.6166 | 1333.8333 | 15.225 | 1335.1667 | 24.3493 | 1330.5 | 15.225
1341.1667 | 8.1912 |  | 1343.5 | 11.9308 | 1344.8333 | 22.9609 | 1345.8333 | 14.7205 | 1341.1667 | 8.1912
1351.8333 | 15.6158 |  | 1354.5 | 8.3192 | 1355.5 | 22.3456 | 1356.8333 | 11.7333 | 1351.8333 | 8.3192
1362.5 | 17.4053 |  | 1365.1667 | 15.1043 | 1366.1667 | 24.0107 | 1367.5 | 6.0258 | 1362.5 | 6.0258
1373.5 | 11.8179 |  | 1376 | 33.0651 | 1377.1667 | 28.8733 | 1378.3333 | 18.5536 | 1373.5 | 11.8179
1384.5 | 14.5998 |  | 1386.6667 | 36.1906 | 1388 | 26.9676 | 1389.1667 | 17.239 | 1384.5 | 14.5998
1395.1667 | 21.6053 |  | 1397.5 | 23.5425 | 1398.8333 | 25.5844 | 1399.8333 | 8.6411 | 1395.1667 | 8.6411
1405.8333 | 10.9658 |  | 1408.5 | 12.2481 | 1409.5 | 23.0252 | 1410.8333 | 26.7494 | 1405.8333 | 10.9658
1416.5 | 557.2325 |  | 1419.1667 | 106.0137 | 1420.1667 | 49.7796 | 1421.5 | 193.9862 | 1416.5 | 49.7796
1427.5 | 118.3666 |  | 1429.8333 | 31.9423 | 1431.1667 | 79.1416 | 1432.1667 | 85.1159 | 1427.5 | 31.9423
1438.5 | 31.7881 |  | 1440.5 | 32.1001 | 1441.8333 | 35.3271 | 1443.1667 | 13.6835 | 1438.5 | 13.6835
1449.1667 | 25.8424 |  | 1451.5 | 19.0582 | 1452.8333 | 37.5815 | 1453.8333 | 35.671 | 1449.1667 | 19.0582
1459.8333 | 24.7362 |  | 1462.5 | 18.3499 | 1463.5 | 44.1347 | 1464.8333 | 16.2955 | 1459.8333 | 16.2955
1470.5 | 32.5299 |  | 1473.1667 | 23.6626 | 1474.1667 | 26.1274 | 1475.5 | 35.373 | 1470.5 | 23.6626
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5
0 | -184 | 24.238 | 24.77 | 24.7718 | 24.6463 | 23.5045 | 23.5542
0.6309 | -183.3691 | 24.2414 | 24.7638 | 24.7788 | 24.6437 | 23.4964 | 23.5541
1.5122 | -182.4878 | 24.2358 | 24.7634 | 24.7775 | 24.6447 | 23.4946 | 23.5516
2.4736 | -181.5264 | 24.237 | 24.7627 | 24.7714 | 24.6384 | 23.4982 | 23.5526
3.475 | -180.525 | 24.2388 | 24.759 | 24.7592 | 24.6354 | 23.4905 | 23.5555
4.4764 | -179.5236 | 24.2392 | 24.7538 | 24.7593 | 24.6367 | 23.4994 | 23.547
5.4779 | -178.5221 | 24.2465 | 24.7576 | 24.7585 | 24.6354 | 23.486 | 23.5485
6.4793 | -177.5207 | 24.2466 | 24.7537 | 24.7614 | 24.6322 | 23.5057 | 23.5453
7.4808 | -176.5192 | 24.2363 | 24.7539 | 24.7602 | 24.6364 | 23.4898 | 23.5473
8.4922 | -175.5078 | 24.2469 | 24.7578 | 24.7648 | 24.6365 | 23.4975 | 23.5529
9.4736 | -174.5264 | 24.238 | 24.7542 | 24.7693 | 24.6273 | 23.4925 | 23.5479
10.4751 | -173.5249 | 24.2329 | 24.7547 | 24.775 | 24.6332 | 23.4911 | 23.5493
11.4765 | -172.5235 | 24.2344 | 24.7532 | 24.7654 | 24.6345 | 23.4896 | 23.5502
12.4779 | -171.5221 | 24.239 | 24.7479 | 24.7417 | 24.6384 | 23.4907 | 23.5494
13.4794 | -170.5206 | 24.2363 | 24.7474 | 24.7579 | 24.6308 | 23.4828 | 23.5436
14.4708 | -169.5292 | 24.2339 | 24.745 | 24.7567 | 24.6319 | 23.4875 | 23.5443
15.4722 | -168.5278 | 24.2347 | 24.7448 | 24.7589 | 24.6349 | 23.4904 | 23.542
16.4737 | -167.5263 | 24.2328 | 24.7531 | 24.7629 | 24.6275 | 23.4899 | 23.5425
17.4952 | -166.5048 | 24.2315 | 24.747 | 24.7595 | 24.6312 | 23.4898 | 23.5395
18.4766 | -165.5234 | 24.2287 | 24.746 | 24.7608 | 24.6325 | 23.4703 | 23.5399
19.478 | -164.522 | 24.2293 | 24.7455 | 24.7511 | 24.6242 | 23.4869 | 23.5373
20.4794 | -163.5206 | 24.2265 | 24.7468 | 24.7531 | 24.6279 | 23.4877 | 23.5414
21.4809 | -162.5191 | 24.2245 | 24.7468 | 24.76 | 24.6298 | 23.4697 | 23.5365
22.4723 | -161.5277 | 24.223 | 24.7437 | 24.7582 | 24.6278 | 23.4869 | 23.5357
23.4738 | -160.5262 | 24.2278 | 24.7488 | 24.758 | 24.625 | 23.4881 | 23.533
24.4752 | -159.5248 | 24.229 | 24.7467 | 24.7487 | 24.6263 | 23.4871 | 23.5323
25.4766 | -158.5234 | 24.2235 | 24.7474 | 24.752 | 24.6308 | 23.493 | 23.5353
26.4781 | -157.5219 | 24.2251 | 24.7428 | 24.7628 | 24.6276 | 23.4872 | 23.5343
27.4795 | -156.5205 | 24.2215 | 24.7397 | 24.7509 | 24.6212 | 23.4803 | 23.5303
28.481 | -155.519 | 24.2244 | 24.7429 | 24.7544 | 24.628 | 23.4823 | 23.5391
29.4724 | -154.5276 | 24.2241 | 24.7404 | 24.7481 | 24.6302 | 23.4824 | 23.5381
30.4738 | -153.5262 | 24.2325 | 24.7414 | 24.7522 | 24.6251 | 23.4804 | 23.5398
31.4753 | -152.5247 | 24.2231 | 24.7449 | 24.7514 | 24.6333 | 23.4706 | 23.5379
32.4767 | -151.5233 | 24.2279 | 24.7415 | 24.7405 | 24.6285 | 23.4763 | 23.5364
33.4781 | -150.5219 | 24.2206 | 24.7397 | 24.7524 | 24.6206 | 23.474 | 23.5381
34.4796 | -149.5204 | 24.2276 | 24.7425 | 24.744 | 24.6202 | 23.4791 | 23.5352
35.471 | -148.529 | 24.2215 | 24.74 | 24.742 | 24.6216 | 23.4802 | 23.5356
36.4724 | -147.5276 | 24.2281 | 24.7415 | 24.743 | 24.6259 | 23.4906 | 23.5366
37.4739 | -146.5261 | 24.2208 | 24.7352 | 24.7526 | 24.6262 | 23.4848 | 23.5376
38.4753 | -145.5247 | 24.2249 | 24.7335 | 24.7443 | 24.6252 | 23.4628 | 23.5316
39.4768 | -144.5232 | 24.2155 | 24.7456 | 24.7443 | 24.6222 | 23.4761 | 23.5428
40.4782 | -143.5218 | 24.2247 | 24.7398 | 24.7416 | 24.6261 | 23.4776 | 23.5339
41.4796 | -142.5204 | 24.22 | 24.7379 | 24.7416 | 24.6268 | 23.4807 | 23.5377
42.4811 | -141.5189 | 24.2277 | 24.7329 | 24.7533 | 24.6262 | 23.4688 | 23.5315
43.4725 | -140.5275 | 24.2308 | 24.7371 | 24.7453 | 24.6207 | 23.4699 | 23.5317
44.474 | -139.526 | 24.2288 | 24.7313 | 24.7528 | 24.6204 | 23.4713 | 23.5368
45.4754 | -138.5246 | 24.2292 | 24.7353 | 24.7425 | 24.6251 | 23.4728 | 23.533
46.4768 | -137.5232 | 24.2286 | 24.7343 | 24.7372 | 24.6262 | 23.4884 | 23.5331
47.4883 | -136.5117 | 24.2293 | 24.7315 | 24.7512 | 24.6234 | 23.4763 | 23.5277
48.4797 | -135.5203 | 24.2382 | 24.7347 | 24.7521 | 24.6222 | 23.4777 | 23.5282
49.4812 | -134.5188 | 24.2383 | 24.7348 | 24.7451 | 24.6251 | 23.483 | 23.5329
50.4826 | -133.5174 | 24.235 | 24.7279 | 24.7335 | 24.6213 | 23.4787 | 23.5223
51.474 | -132.526 | 24.2362 | 24.7306 | 24.7404 | 24.619 | 23.4688 | 23.5282
52.4755 | -131.5245 | 24.2342 | 24.7265 | 24.742 | 24.6239 | 23.4766 | 23.5346
53.4869 | -130.5131 | 24.2327 | 24.7279 | 24.7392 | 24.6178 | 23.4709 | 23.5263
54.4783 | -129.5217 | 24.2351 | 24.7288 | 24.736 | 24.6231 | 23.4661 | 23.529
55.4798 | -128.5202 | 24.2418 | 24.7225 | 24.7402 | 24.6192 | 23.4799 | 23.5301
56.4712 | -127.5288 | 24.2422 | 24.7282 | 24.7352 | 24.6258 | 23.4762 | 23.5285
57.4726 | -126.5274 | 24.2363 | 24.7277 | 24.7354 | 24.6142 | 23.4676 | 23.5251
58.5242 | -125.4758 | 24.2323 | 24.7274 | 24.7429 | 24.6154 | 23.4683 | 23.532
59.4755 | -124.5245 | 24.2332 | 24.7332 | 24.734 | 24.6176 | 23.4814 | 23.5332
60.477 | -123.523 | 24.2308 | 24.7256 | 24.7366 | 24.6178 | 23.4629 | 23.5337
61.4784 | -122.5216 | 24.235 | 24.7246 | 24.7415 | 24.6201 | 23.4707 | 23.5272
62.4798 | -121.5202 | 24.2356 | 24.7208 | 24.7325 | 24.6147 | 23.4648 | 23.5286
63.4713 | -120.5287 | 24.238 | 24.7198 | 24.7232 | 24.6091 | 23.4812 | 23.53
64.4727 | -119.5273 | 24.2359 | 24.7239 | 24.735 | 24.6078 | 23.4655 | 23.5249
65.4741 | -118.5259 | 24.2292 | 24.7186 | 24.7336 | 24.611 | 23.4744 | 23.53
66.5156 | -117.4844 | 24.2297 | 24.7189 | 24.7389 | 24.6118 | 23.4754 | 23.5265
67.477 | -116.523 | 24.2307 | 24.7236 | 24.7318 | 24.6134 | 23.4671 | 23.5291
68.4785 | -115.5215 | 24.2368 | 24.7196 | 24.7334 | 24.6115 | 23.4652 | 23.5269
69.4799 | -114.5201 | 24.2292 | 24.7185 | 24.7303 | 24.6159 | 23.4655 | 23.5283
70.4713 | -113.5287 | 24.2343 | 24.7212 | 24.7355 | 24.6145 | 23.4646 | 23.5209
71.4728 | -112.5272 | 24.2306 | 24.7241 | 24.7349 | 24.6146 | 23.4567 | 23.5303
72.4742 | -111.5258 | 24.2309 | 24.7177 | 24.7341 | 24.6115 | 23.4647 | 23.5212
73.4757 | -110.5243 | 24.2285 | 24.7251 | 24.7255 | 24.6081 | 23.4709 | 23.5237
74.4771 | -109.5229 | 24.2288 | 24.7204 | 24.7359 | 24.6178 | 23.4672 | 23.5226
75.4785 | -108.5215 | 24.2292 | 24.7173 | 24.7262 | 24.6106 | 23.461 | 23.5171
76.48 | -107.52 | 24.2224 | 24.7202 | 24.731 | 24.6093 | 23.467 | 23.524
77.4714 | -106.5286 | 24.2238 | 24.7172 | 24.7294 | 24.6115 | 23.471 | 23.5229
78.4728 | -105.5272 | 24.2256 | 24.7198 | 24.7251 | 24.6105 | 23.4689 | 23.5269
79.4743 | -104.5257 | 24.2339 | 24.7209 | 24.7222 | 24.6103 | 23.4712 | 23.5269
80.4757 | -103.5243 | 24.2329 | 24.7167 | 24.7248 | 24.6107 | 23.4783 | 23.5287
81.4772 | -102.5228 | 24.2315 | 24.7199 | 24.7309 | 24.613 | 23.4582 | 23.5261
82.4786 | -101.5214 | 24.2283 | 24.7167 | 24.7317 | 24.6096 | 23.4693 | 23.5264
83.48 | -100.52 | 24.2276 | 24.7126 | 24.7241 | 24.6095 | 23.4653 | 23.5261
84.4815 | -99.5185 | 24.2328 | 24.7125 | 24.7349 | 24.6123 | 23.4657 | 23.5244
85.4729 | -98.5271 | 24.2348 | 24.7134 | 24.7334 | 24.6098 | 23.459 | 23.5231
86.4743 | -97.5257 | 24.2294 | 24.7106 | 24.7197 | 24.6093 | 23.4637 | 23.5181
87.4758 | -96.5242 | 24.2261 | 24.7167 | 24.7318 | 24.6084 | 23.4661 | 23.5201
88.4772 | -95.5228 | 24.2261 | 24.7149 | 24.7308 | 24.6061 | 23.4739 | 23.5217
89.4787 | -94.5213 | 24.2298 | 24.7127 | 24.7237 | 24.606 | 23.4722 | 23.5144
90.4801 | -93.5199 | 24.2238 | 24.7106 | 24.7138 | 24.6009 | 23.4633 | 23.5137
91.4715 | -92.5285 | 24.2289 | 24.7184 | 24.7254 | 24.6094 | 23.4623 | 23.5208
92.473 | -91.527 | 24.2285 | 24.7108 | 24.727 | 24.6089 | 23.4699 | 23.5186
93.4744 | -90.5256 | 24.228 | 24.7123 | 24.7183 | 24.6023 | 23.4683 | 23.5222
94.4758 | -89.5242 | 24.2249 | 24.7087 | 24.7324 | 24.6049 | 23.4689 | 23.5212
95.4773 | -88.5227 | 24.2299 | 24.7072 | 24.7231 | 24.6048 | 23.4612 | 23.5145
96.4787 | -87.5213 | 24.2301 | 24.7107 | 24.7109 | 24.6062 | 23.4643 | 23.5147
97.4802 | -86.5198 | 24.2328 | 24.7037 | 24.7182 | 24.6048 | 23.48 | 23.5181
98.4716 | -85.5284 | 24.2298 | 24.7109 | 24.7217 | 24.6061 | 23.4477 | 23.5192
99.473 | -84.527 | 24.2251 | 24.7129 | 24.7102 | 24.6044 | 23.4644 | 23.5212
100.4745 | -83.5255 | 24.2335 | 24.7136 | 24.722 | 24.5989 | 23.4553 | 23.5202
101.4759 | -82.5241 | 24.2279 | 24.7103 | 24.7083 | 24.5984 | 23.4679 | 23.5164
102.4774 | -81.5226 | 24.2288 | 24.7045 | 24.706 | 24.6 | 23.4635 | 23.5163
103.4788 | -80.5212 | 24.2234 | 24.707 | 24.714 | 24.6006 | 23.4568 | 23.5195
104.4802 | -79.5198 | 24.221 | 24.7011 | 24.7154 | 24.5956 | 23.4616 | 23.5144
105.4717 | -78.5283 | 24.229 | 24.6989 | 24.7173 | 24.6024 | 23.4596 | 23.5174
106.4731 | -77.5269 | 24.2265 | 24.7015 | 24.7113 | 24.595 | 23.4688 | 23.5178
107.4745 | -76.5255 | 24.2273 | 24.7007 | 24.7165 | 24.5998 | 23.4577 | 23.5114
108.486 | -75.514 | 24.2271 | 24.7072 | 24.719 | 24.6001 | 23.4651 | 23.5134
109.4774 | -74.5226 | 24.2246 | 24.6979 | 24.7193 | 24.6014 | 23.4693 | 23.509
110.4789 | -73.5211 | 24.23 | 24.7048 | 24.7135 | 24.5942 | 23.453 | 23.5107
111.4803 | -72.5197 | 24.2297 | 24.7071 | 24.7212 | 24.5927 | 23.4619 | 23.5074
112.4717 | -71.5283 | 24.232 | 24.7057 | 24.7134 | 24.5915 | 23.4638 | 23.5087
113.4732 | -70.5268 | 24.229 | 24.7067 | 24.7087 | 24.5979 | 23.4491 | 23.5088
114.4746 | -69.5254 | 24.2332 | 24.7007 | 24.7157 | 24.5983 | 23.4666 | 23.5059
115.476 | -68.524 | 24.2273 | 24.704 | 24.7081 | 24.5874 | 23.4633 | 23.508
116.4775 | -67.5225 | 24.2231 | 24.7048 | 24.7175 | 24.5951 | 23.4596 | 23.5017
117.4789 | -66.5211 | 24.2236 | 24.6956 | 24.713 | 24.5937 | 23.454 | 23.5138
118.5204 | -65.4796 | 24.2222 | 24.7013 | 24.7119 | 24.5921 | 23.4519 | 23.5134
119.4818 | -64.5182 | 24.2316 | 24.6993 | 24.7143 | 24.5967 | 23.4515 | 23.5078
120.4732 | -63.5268 | 24.2279 | 24.6958 | 24.7243 | 24.5927 | 23.447 | 23.5064
121.4747 | -62.5253 | 24.2253 | 24.7024 | 24.7011 | 24.594 | 23.4427 | 23.5087
122.4761 | -61.5239 | 24.2233 | 24.6991 | 24.7049 | 24.587 | 23.4617 | 23.5045
123.4776 | -60.5224 | 24.2259 | 24.7053 | 24.6953 | 24.588 | 23.4632 | 23.5093
124.519 | -59.481 | 24.2254 | 24.7004 | 24.7078 | 24.5866 | 23.4488 | 23.5082
125.4804 | -58.5196 | 24.2245 | 24.6966 | 24.709 | 24.5852 | 23.4509 | 23.5084
126.4719 | -57.5281 | 24.2202 | 24.7005 | 24.7044 | 24.5905 | 23.4612 | 23.5005
127.4733 | -56.5267 | 24.2264 | 24.6979 | 24.7023 | 24.5934 | 23.4501 | 23.5012
128.4747 | -55.5253 | 24.2276 | 24.6901 | 24.7072 | 24.5865 | 23.4437 | 23.5019
129.4762 | -54.5238 | 24.2276 | 24.6964 | 24.7038 | 24.5897 | 23.463 | 23.5023
130.4776 | -53.5224 | 24.2239 | 24.6927 | 24.7125 | 24.5863 | 23.4503 | 23.5083
131.4791 | -52.5209 | 24.2298 | 24.6996 | 24.7122 | 24.5818 | 23.4402 | 23.5019
132.4805 | -51.5195 | 24.2257 | 24.7 | 24.7063 | 24.5886 | 23.4581 | 23.5009
133.4719 | -50.5281 | 24.222 | 24.6944 | 24.7047 | 24.5828 | 23.4463 | 23.4991
134.4734 | -49.5266 | 24.2277 | 24.6955 | 24.7015 | 24.5893 | 23.4458 | 23.5035
135.4748 | -48.5252 | 24.2279 | 24.6898 | 24.7088 | 24.5822 | 23.4505 | 23.5
136.4762 | -47.5238 | 24.2245 | 24.6905 | 24.6901 | 24.58 | 23.4424 | 23.498
137.4777 | -46.5223 | 24.2235 | 24.6918 | 24.6997 | 24.5802 | 23.4454 | 23.4951
138.4791 | -45.5209 | 24.2291 | 24.6909 | 24.7071 | 24.5809 | 23.4572 | 23.5031
139.4806 | -44.5194 | 24.2276 | 24.7004 | 24.6889 | 24.5774 | 23.4594 | 23.4959
140.482 | -43.518 | 24.2246 | 24.6868 | 24.7049 | 24.5813 | 23.4603 | 23.4993
141.4734 | -42.5266 | 24.2226 | 24.6929 | 24.7025 | 24.582 | 23.4527 | 23.4981
142.4749 | -41.5251 | 24.2185 | 24.6873 | 24.6961 | 24.573 | 23.4454 | 23.5014
143.4763 | -40.5237 | 24.2225 | 24.6845 | 24.6884 | 24.5778 | 23.4598 | 23.5024
144.4777 | -39.5223 | 24.2269 | 24.69 | 24.7034 | 24.5791 | 23.4467 | 23.5009
145.4792 | -38.5208 | 24.2269 | 24.6863 | 24.7029 | 24.577 | 23.4602 | 23.5026
146.4806 | -37.5194 | 24.2285 | 24.6851 | 24.7017 | 24.5737 | 23.4394 | 23.4981
147.4721 | -36.5279 | 24.2331 | 24.6823 | 24.698 | 24.5746 | 23.4425 | 23.4978
148.4735 | -35.5265 | 24.2341 | 24.6878 | 24.6898 | 24.5773 | 23.4454 | 23.4984
149.4749 | -34.5251 | 24.2317 | 24.6862 | 24.6927 | 24.5757 | 23.4639 | 23.4949
150.4764 | -33.5236 | 24.2367 | 24.6705 | 24.6915 | 24.5686 | 23.4544 | 23.501
151.4778 | -32.5222 | 24.233 | 24.6832 | 24.6963 | 24.5737 | 23.4642 | 23.4995
152.4793 | -31.5207 | 24.24 | 24.6799 | 24.6968 | 24.5675 | 23.4512 | 23.5007
153.4807 | -30.5193 | 24.2406 | 24.6699 | 24.6986 | 24.5762 | 23.4565 | 23.4913
154.4821 | -29.5179 | 24.2365 | 24.6755 | 24.698 | 24.5719 | 23.4595 | 23.4972
155.4736 | -28.5264 | 24.2323 | 24.6764 | 24.6911 | 24.5695 | 23.4657 | 23.4998
156.475 | -27.525 | 24.238 | 24.6772 | 24.6922 | 24.5691 | 23.4596 | 23.5003
157.4764 | -26.5236 | 24.2341 | 24.671 | 24.6874 | 24.5662 | 23.4522 | 23.4851
158.4779 | -25.5221 | 24.2309 | 24.6707 | 24.6791 | 24.5695 | 23.4564 | 23.4922
159.4793 | -24.5207 | 24.2324 | 24.6722 | 24.6965 | 24.5717 | 23.4483 | 23.493
160.4808 | -23.5192 | 24.2299 | 24.6797 | 24.6952 | 24.5669 | 23.4574 | 23.4924
161.4722 | -22.5278 | 24.2294 | 24.6734 | 24.6979 | 24.5682 | 23.4454 | 23.5008
162.4736 | -21.5264 | 24.2271 | 24.6767 | 24.6955 | 24.5686 | 23.4592 | 23.4942
163.4751 | -20.5249 | 24.2292 | 24.6757 | 24.6931 | 24.573 | 23.4397 | 23.4927
164.4765 | -19.5235 | 24.2293 | 24.6756 | 24.6882 | 24.5647 | 23.4472 | 23.4954
165.4779 | -18.5221 | 24.2256 | 24.6789 | 24.6972 | 24.5639 | 23.4528 | 23.4911
166.4794 | -17.5206 | 24.2283 | 24.6664 | 24.6963 | 24.5635 | 23.4481 | 23.4895
167.4708 | -16.5292 | 24.2277 | 24.6751 | 24.699 | 24.5655 | 23.4511 | 23.4883
168.4723 | -15.5277 | 24.2287 | 24.6671 | 24.6939 | 24.5602 | 23.4531 | 23.4874
169.4737 | -14.5263 | 24.2302 | 24.6772 | 24.6806 | 24.561 | 23.4558 | 23.493
170.4751 | -13.5249 | 24.2272 | 24.6699 | 24.696 | 24.5604 | 23.449 | 23.4947
171.4766 | -12.5234 | 24.2283 | 24.67 | 24.6874 | 24.5636 | 23.4451 | 23.4932
172.478 | -11.522 | 24.2232 | 24.6674 | 24.6899 | 24.5643 | 23.4477 | 23.4915
173.4795 | -10.5205 | 24.2211 | 24.6677 | 24.6919 | 24.5633 | 23.4435 | 23.4913
174.4809 | -9.5191 | 24.2194 | 24.6676 | 24.6741 | 24.5606 | 23.4445 | 23.4881
175.4723 | -8.5277 | 24.2302 | 24.6714 | 24.6911 | 24.5583 | 23.4479 | 23.486
176.4738 | -7.5262 | 24.2187 | 24.667 | 24.6976 | 24.5676 | 23.452 | 23.4859
177.4752 | -6.5248 | 24.2236 | 24.6627 | 24.6831 | 24.5633 | 23.4382 | 23.4863
178.4766 | -5.5234 | 24.2214 | 24.6669 | 24.6867 | 24.5631 | 23.4333 | 23.4809
179.4781 | -4.5219 | 24.2241 | 24.6681 | 24.6751 | 24.5643 | 23.4475 | 23.4858
180.4795 | -3.5205 | 24.2273 | 24.6666 | 24.6852 | 24.5642 | 23.4424 | 23.485
181.481 | -2.519 | 24.2241 | 24.6677 | 24.6867 | 24.5641 | 23.4345 | 23.4889
182.4824 | -1.5176 | 24.2297 | 24.6715 | 24.6928 | 24.5586 | 23.4473 | 23.4844
183.4738 | -0.5262 | 24.2325 | 24.477 | 24.6647 | 24.4669 | 23.4913 | 23.5235
184.4753 | 0.4753 | 24.2331 | 24.5641 | 24.6871 | 24.5155 | 23.4661 | 23.4943
185.4767 | 1.4767 | 24.3087 | 24.6031 | 24.68 | 24.539 | 23.4439 | 23.4901
186.4781 | 2.4781 | 24.7755 | 24.6237 | 24.6836 | 24.5404 | 23.4479 | 23.4948
187.4796 | 3.4796 | 25.8023 | 24.6383 | 24.6836 | 24.5496 | 23.4524 | 23.4993
188.471 | 4.471 | 27.4089 | 24.6342 | 24.686 | 24.5452 | 23.4601 | 23.5178
189.4724 | 5.4724 | 29.5315 | 24.6478 | 24.6847 | 24.5598 | 23.477 | 23.5343
190.4739 | 6.4739 | 32.0945 | 24.6484 | 24.6823 | 24.5729 | 23.5001 | 23.5647
191.4753 | 7.4753 | 35.0243 | 24.6564 | 24.6787 | 24.5818 | 23.5237 | 23.5956
192.4768 | 8.4768 | 38.2616 | 24.6583 | 24.6841 | 24.601 | 23.5575 | 23.6342
193.4782 | 9.4782 | 41.7826 | 24.6632 | 24.6874 | 24.6212 | 23.5915 | 23.6874
194.4796 | 10.4796 | 45.5536 | 24.6785 | 24.668 | 24.6553 | 23.641 | 23.7384
195.4711 | 11.4711 | 49.5544 | 24.6917 | 24.6897 | 24.6895 | 23.7133 | 23.7978
196.4725 | 12.4725 | 53.7341 | 24.7186 | 24.6833 | 24.7384 | 23.7733 | 23.8815
197.474 | 13.474 | 58.0597 | 24.7335 | 24.688 | 24.7866 | 23.8686 | 23.9727
198.4754 | 14.4754 | 62.5259 | 24.7707 | 24.6841 | 24.8473 | 23.982 | 24.0651
199.4768 | 15.4768 | 67.1007 | 24.8052 | 24.6959 | 24.9209 | 24.1052 | 24.2071
200.4783 | 16.4783 | 71.8344 | 24.8524 | 24.6947 | 25.002 | 24.2503 | 24.3451
201.4797 | 17.4797 | 76.7366 | 24.8927 | 24.6894 | 25.0874 | 24.3906 | 24.4689
202.4812 | 18.4812 | 81.7441 | 24.9432 | 24.6837 | 25.1937 | 24.5385 | 24.6376
203.4726 | 19.4726 | 86.8428 | 25.0115 | 24.6814 | 25.3074 | 24.7066 | 24.8307
204.474 | 20.474 | 91.9866 | 25.0772 | 24.688 | 25.4399 | 24.8835 | 25.0351
205.4755 | 21.4755 | 97.2277 | 25.1721 | 24.6877 | 25.5775 | 25.0751 | 25.2571
206.4769 | 22.4769 | 102.579 | 25.251 | 24.7014 | 25.7296 | 25.3113 | 25.4677
207.4783 | 23.4783 | 108.0504 | 25.3524 | 24.689 | 25.8976 | 25.5711 | 25.6919
208.4798 | 24.4798 | 113.5769 | 25.4606 | 24.672 | 26.0832 | 25.8082 | 25.97
209.4712 | 25.4712 | 119.1989 | 25.5859 | 24.7015 | 26.2774 | 26.093 | 26.2923
210.4726 | 26.4726 | 124.8862 | 25.7218 | 24.7061 | 26.4857 | 26.3489 | 26.5879
211.4741 | 27.4741 | 130.5167 | 25.8584 | 24.7127 | 26.7168 | 26.6366 | 26.9366
212.4755 | 28.4755 | 136.122 | 26.0255 | 24.7196 | 26.9664 | 26.9529 | 27.2611
213.477 | 29.477 | 141.7799 | 26.2006 | 24.7302 | 27.2209 | 27.2827 | 27.6038
214.4784 | 30.4784 | 147.3984 | 26.3892 | 24.7409 | 27.5067 | 27.6092 | 27.9712
215.4798 | 31.4798 | 153.0176 | 26.584 | 24.7446 | 27.7985 | 27.9699 | 28.3275
216.4813 | 32.4813 | 158.6726 | 26.801 | 24.7631 | 28.1084 | 28.3795 | 28.7241
217.4727 | 33.4727 | 164.3888 | 27.0252 | 24.773 | 28.4339 | 28.7891 | 29.1884
218.4742 | 34.4742 | 170.1232 | 27.2729 | 24.788 | 28.7781 | 29.1757 | 29.62
219.4756 | 35.4756 | 175.7632 | 27.5266 | 24.8046 | 29.1459 | 29.6219 | 30.0663
220.477 | 36.477 | 181.322 | 27.7928 | 24.823 | 29.5257 | 30.0905 | 30.55
221.4785 | 37.4785 | 186.7981 | 28.0886 | 24.8267 | 29.9208 | 30.5624 | 31.0128
222.4799 | 38.4799 | 192.2315 | 28.3895 | 24.8598 | 30.3333 | 31.0487 | 31.5658
223.4814 | 39.4814 | 197.6926 | 28.7203 | 24.8744 | 30.7721 | 31.5068 | 32.0662
224.4728 | 40.4728 | 203.1038 | 29.0581 | 24.9057 | 31.2226 | 32.0146 | 32.5773
225.4742 | 41.4742 | 208.6162 | 29.4289 | 24.9395 | 31.7034 | 32.6342 | 33.1912
226.4757 | 42.4757 | 214.0848 | 29.8016 | 24.9735 | 32.2071 | 33.2308 | 33.815
227.4771 | 43.4771 | 219.5455 | 30.1993 | 25.0022 | 32.7279 | 33.776 | 34.4459
228.4785 | 44.4785 | 225.0693 | 30.6113 | 25.0319 | 33.2726 | 34.4046 | 35.0879
229.48 | 45.48 | 230.5833 | 31.0417 | 25.0856 | 33.8479 | 35.0346 | 35.743
230.4714 | 46.4714 | 236.0182 | 31.4912 | 25.1243 | 34.4438 | 35.7558 | 36.4472
231.4728 | 47.4728 | 241.4016 | 31.959 | 25.1676 | 35.0563 | 36.4695 | 37.2259
232.4743 | 48.4743 | 246.815 | 32.4516 | 25.2116 | 35.6926 | 37.1718 | 37.8982
233.4757 | 49.4757 | 252.2924 | 32.9578 | 25.2706 | 36.3465 | 37.8781 | 38.646
234.4772 | 50.4772 | 257.6449 | 33.5005 | 25.3309 | 37.0222 | 38.6539 | 39.4458
235.4786 | 51.4786 | 263.0401 | 34.0493 | 25.3832 | 37.7238 | 39.4109 | 40.2582
236.48 | 52.48 | 268.3288 | 34.6269 | 25.4481 | 38.4487 | 40.2081 | 41.1347
237.4715 | 53.4715 | 273.615 | 35.2147 | 25.5236 | 39.2093 | 41.0439 | 41.8501
238.4829 | 54.4829 | 278.9068 | 35.838 | 25.5902 | 39.9865 | 41.896 | 42.7281
239.4743 | 55.4743 | 284.0633 | 36.4839 | 25.6741 | 40.7783 | 42.7237 | 43.5862
240.4758 | 56.4758 | 289.2579 | 37.1482 | 25.7462 | 41.5843 | 43.5911 | 44.4183
241.4772 | 57.4772 | 294.4474 | 37.8351 | 25.8346 | 42.4242 | 44.4943 | 45.2808
242.4787 | 58.4787 | 299.7124 | 38.534 | 25.9349 | 43.2822 | 45.4826 | 46.2633
243.4801 | 59.4801 | 305.0309 | 39.2851 | 26.0028 | 44.1678 | 46.4417 | 47.2029
244.4715 | 60.4715 | 310.3803 | 40.0384 | 26.1273 | 45.0827 | 47.4419 | 48.0991
245.473 | 61.473 | 315.7681 | 40.817 | 26.2467 | 46.027 | 48.4473 | 49.1296
246.4744 | 62.4744 | 321.0796 | 41.616 | 26.3455 | 47.0053 | 49.4785 | 50.1357
247.4759 | 63.4759 | 326.2091 | 42.4406 | 26.4709 | 48.012 | 50.5444 | 51.2385
248.4773 | 64.4773 | 331.3505 | 43.2791 | 26.6043 | 49.0609 | 51.669 | 52.2334
249.4787 | 65.4787 | 336.5193 | 44.1458 | 26.7249 | 50.121 | 52.8297 | 53.3937
250.4802 | 66.4802 | 341.7152 | 45.0391 | 26.8614 | 51.2082 | 54.0501 | 54.5834
251.4716 | 67.4716 | 346.8004 | 45.9517 | 27.0124 | 52.3224 | 55.3908 | 55.7715
252.473 | 68.473 | 351.8028 | 46.9018 | 27.1495 | 53.4571 | 56.5677 | 56.9672
253.4745 | 69.4745 | 356.9432 | 47.8763 | 27.3087 | 54.6096 | 57.8512 | 58.1449
254.4759 | 70.4759 | 362.0207 | 48.8866 | 27.485 | 55.7781 | 59.1904 | 59.3403
255.4774 | 71.4774 | 367.0064 | 49.9076 | 27.6551 | 56.9837 | 60.4726 | 60.5478
256.4788 | 72.4788 | 372.0617 | 50.9719 | 27.8392 | 58.2388 | 61.9139 | 61.8417
257.4802 | 73.4802 | 377.0902 | 52.0609 | 28.02 | 59.5085 | 63.268 | 63.2035
258.4717 | 74.4717 | 382.1264 | 53.1758 | 28.1942 | 60.8042 | 64.6833 | 64.5247
259.4731 | 75.4731 | 386.9566 | 54.3395 | 28.408 | 62.1331 | 66.1251 | 65.8919
260.4745 | 76.4745 | 391.6561 | 55.5261 | 28.6147 | 63.4871 | 67.623 | 67.3615
261.476 | 77.476 | 396.4254 | 56.7563 | 28.8423 | 64.8729 | 69.1593 | 68.8409
262.4874 | 78.4874 | 401.3787 | 58.0243 | 29.0707 | 66.3 | 70.7018 | 70.3662
263.4789 | 79.4789 | 406.2161 | 59.2965 | 29.2997 | 67.7261 | 72.3303 | 71.7986
264.4803 | 80.4803 | 411.0424 | 60.603 | 29.5201 | 69.2011 | 73.8625 | 73.3598
265.4817 | 81.4817 | 415.7733 | 61.9519 | 29.7973 | 70.7067 | 75.4998 | 74.8941
266.4732 | 82.4732 | 420.3977 | 63.3245 | 30.0322 | 72.2471 | 77.1873 | 76.5143
267.4746 | 83.4746 | 425.0847 | 64.7162 | 30.3262 | 73.8064 | 79.0086 | 78.1578
268.476 | 84.476 | 429.8261 | 66.1462 | 30.5913 | 75.4012 | 80.7138 | 79.7755
269.4775 | 85.4775 | 434.6924 | 67.6128 | 30.8792 | 77.0255 | 82.5329 | 81.4009
270.5691 | 86.5691 | 439.7901 | 69.157 | 31.1756 | 78.7814 | 84.4815 | 83.2717
271.4804 | 87.4804 | 443.7849 | 70.4232 | 31.4729 | 80.2683 | 86.0987 | 84.8661
272.4718 | 88.4718 | 447.9474 | 72.0411 | 31.7798 | 81.9971 | 87.9257 | 86.6194
273.4732 | 89.4732 | 451.9086 | 73.5972 | 32.106 | 83.7224 | 89.7451 | 88.2674
274.4747 | 90.4747 | 455.7478 | 75.2035 | 32.4241 | 85.4726 | 91.7276 | 89.9736
275.4761 | 91.4761 | 459.15 | 76.8207 | 32.7532 | 87.2407 | 93.6643 | 91.698
276.4776 | 92.4776 | 462.1512 | 78.4391 | 33.1228 | 88.9996 | 95.5594 | 93.3382
277.479 | 93.479 | 464.7705 | 80.0934 | 33.4609 | 90.7838 | 97.4312 | 95.0144
278.4804 | 94.4804 | 467.3061 | 81.7487 | 33.8331 | 92.5533 | 99.3011 | 96.7097
279.4719 | 95.4719 | 469.7434 | 83.4017 | 34.2278 | 94.3163 | 101.1728 | 98.396
280.4733 | 96.4733 | 472.0013 | 85.029 | 34.6135 | 96.0605 | 103.0083 | 100.1217
281.4747 | 97.4747 | 474.0748 | 86.7802 | 34.9993 | 97.8528 | 104.8691 | 101.8142
282.4762 | 98.4762 | 476.1391 | 88.5414 | 35.396 | 99.6581 | 106.6878 | 103.4483
283.4776 | 99.4776 | 477.7963 | 90.2837 | 35.8136 | 101.4519 | 108.5916 | 105.1175
284.4791 | 100.4791 | 479.4939 | 92.0066 | 36.2486 | 103.2047 | 110.3827 | 106.7375
285.4805 | 101.4805 | 481.1235 | 93.7595 | 36.6896 | 104.9776 | 112.331 | 108.3312
286.4719 | 102.4719 | 482.7629 | 95.5226 | 37.1362 | 106.7256 | 114.1075 | 110.0162
287.4734 | 103.4734 | 483.831 | 97.2715 | 37.5858 | 108.4606 | 115.8725 | 111.579
288.4748 | 104.4748 | 484.7696 | 99.043 | 38.0511 | 110.1987 | 117.6173 | 113.1713
289.4762 | 105.4762 | 485.4041 | 100.7954 | 38.5256 | 111.9101 | 119.3351 | 114.713
290.4777 | 106.4777 | 485.9978 | 102.5916 | 39.0101 | 113.6077 | 121.0635 | 116.2407
291.4791 | 107.4791 | 486.4401 | 104.3222 | 39.498 | 115.2853 | 122.8675 | 117.7258
292.4806 | 108.4806 | 486.6746 | 106.0937 | 39.9929 | 116.9366 | 124.4696 | 119.1914
293.472 | 109.472 | 486.7223 | 107.8372 | 40.5079 | 118.5565 | 126.1795 | 120.6304
294.4734 | 110.4734 | 486.8815 | 109.5765 | 41.0072 | 120.1624 | 127.7974 | 122.0525
295.4749 | 111.4749 | 486.8892 | 111.3086 | 41.5279 | 121.7293 | 129.4112 | 123.4276
296.4763 | 112.4763 | 486.7958 | 113.0104 | 42.0594 | 123.2966 | 130.9943 | 124.7942
297.4778 | 113.4778 | 486.8504 | 114.7416 | 42.5833 | 124.8484 | 132.4299 | 126.1539
298.4792 | 114.4792 | 486.769 | 116.4222 | 43.1354 | 126.3666 | 133.9659 | 127.4405
299.5207 | 115.5207 | 486.722 | 118.1748 | 43.6894 | 127.9103 | 135.4723 | 128.7798
300.4821 | 116.4821 | 486.4841 | 119.7451 | 44.2199 | 129.3038 | 136.9246 | 129.9846
301.4735 | 117.4735 | 486.2245 | 121.3823 | 44.7857 | 130.7351 | 138.3524 | 131.2748
302.4749 | 118.4749 | 485.7736 | 122.9905 | 45.3424 | 132.1365 | 139.7415 | 132.502
303.4764 | 119.4764 | 485.4389 | 124.5939 | 45.89 | 133.5107 | 141.1585 | 133.6945
304.4778 | 120.4778 | 485.1348 | 126.1468 | 46.464 | 134.854 | 142.541 | 134.9396
305.4793 | 121.4793 | 484.8379 | 127.6796 | 47.0194 | 136.1795 | 143.9053 | 136.0985
306.4807 | 122.4807 | 484.1099 | 129.2072 | 47.5826 | 137.4933 | 145.3592 | 137.2562
307.4821 | 123.4821 | 483.7218 | 130.7158 | 48.1634 | 138.7708 | 146.6505 | 138.4075
308.4736 | 124.4736 | 483.4435 | 132.215 | 48.7474 | 140.0298 | 147.9415 | 139.5209
309.475 | 125.475 | 483.1915 | 133.6964 | 49.3311 | 141.2373 | 149.2279 | 140.6177
310.4764 | 126.4764 | 482.9136 | 135.1648 | 49.9006 | 142.4306 | 150.4602 | 141.7157
311.4779 | 127.4779 | 482.6189 | 136.6207 | 50.4919 | 143.6061 | 151.6923 | 142.8219
312.4793 | 128.4793 | 482.3928 | 138.0808 | 51.0832 | 144.7613 | 152.9336 | 143.9006
313.4808 | 129.4808 | 481.8822 | 139.5416 | 51.6826 | 145.9119 | 154.1142 | 144.9684
314.4722 | 130.4722 | 481.6921 | 140.9831 | 52.2617 | 147.0556 | 155.3157 | 145.9508
315.4736 | 131.4736 | 481.4065 | 142.4176 | 52.8912 | 148.1933 | 156.5748 | 147.0025
316.4751 | 132.4751 | 481.1339 | 143.8736 | 53.5017 | 149.3092 | 157.7655 | 148.0324
317.4765 | 133.4765 | 480.7416 | 145.4037 | 54.1019 | 150.4112 | 158.9508 | 149.0221
318.4779 | 134.4779 | 480.461 | 146.9324 | 54.7401 | 151.4795 | 160.1399 | 150.0184
319.4794 | 135.4794 | 480.4185 | 148.4894 | 55.3613 | 152.5482 | 161.3275 | 151.0573
320.4808 | 136.4808 | 480.3453 | 150.0753 | 55.9777 | 153.6243 | 162.5383 | 152.0785
321.4723 | 137.4723 | 480.3035 | 151.6607 | 56.6094 | 154.6687 | 163.6992 | 153.1105
322.4737 | 138.4737 | 480.5679 | 153.2896 | 57.2331 | 155.6981 | 164.8597 | 154.102
323.4751 | 139.4751 | 480.5251 | 154.9125 | 57.864 | 156.7119 | 166.0222 | 155.1053
324.4766 | 140.4766 | 480.593 | 156.5282 | 58.5235 | 157.696 | 167.1405 | 156.1076
325.478 | 141.478 | 480.6254 | 158.1508 | 59.1587 | 158.6885 | 168.2957 | 157.0892
326.4795 | 142.4795 | 480.7452 | 159.7415 | 59.7903 | 159.6795 | 169.4731 | 158.0053
327.4809 | 143.4809 | 480.7991 | 161.2949 | 60.4271 | 160.6708 | 170.6159 | 159.0049
328.4723 | 144.4723 | 480.8567 | 162.8181 | 61.0754 | 161.6631 | 171.7483 | 159.9782
329.4738 | 145.4738 | 480.9742 | 164.2522 | 61.7171 | 162.6478 | 172.8675 | 160.9163
330.4752 | 146.4752 | 480.9883 | 165.6236 | 62.3503 | 163.6234 | 174.0426 | 161.9001
331.4766 | 147.4766 | 481.2336 | 166.8608 | 62.992 | 164.599 | 175.1933 | 162.8597
332.4781 | 148.4781 | 481.3147 | 167.9702 | 63.6375 | 165.5632 | 176.3282 | 163.8111
333.4795 | 149.4795 | 481.4102 | 168.9919 | 64.2695 | 166.512 | 177.5168 | 164.7284
334.481 | 150.481 | 481.7271 | 170.0068 | 64.918 | 167.4456 | 178.6695 | 165.6357
335.4724 | 151.4724 | 481.8409 | 171.016 | 65.5616 | 168.3771 | 179.7321 | 166.5669
336.4738 | 152.4738 | 481.8925 | 171.9743 | 66.1966 | 169.2997 | 180.7894 | 167.4996
337.4753 | 153.4753 | 481.9934 | 172.9041 | 66.8432 | 170.2092 | 181.9019 | 168.3926
338.4767 | 154.4767 | 482.1076 | 173.7804 | 67.4925 | 171.1018 | 182.9169 | 169.2704
339.4781 | 155.4781 | 482.5847 | 174.64 | 68.1302 | 171.9811 | 183.9327 | 170.1874
340.4796 | 156.4796 | 483.0102 | 175.4523 | 68.7644 | 172.8554 | 185.0125 | 171.1008
341.471 | 157.471 | 483.1596 | 176.244 | 69.3969 | 173.6945 | 186.0648 | 172.0157
342.4725 | 158.4725 | 483.0384 | 176.9853 | 70.0325 | 174.5177 | 187.1145 | 172.886
343.4739 | 159.4739 | 483.0273 | 177.6985 | 70.6592 | 175.3084 | 188.1893 | 173.7863
344.4753 | 160.4753 | 483.1478 | 178.4008 | 71.297 | 176.079 | 189.212 | 174.6644
345.4768 | 161.4768 | 483.3272 | 179.086 | 71.9268 | 176.8076 | 190.2245 | 175.5413
346.4882 | 162.4882 | 483.3861 | 179.7635 | 72.5597 | 177.5043 | 191.2365 | 176.4029
347.4897 | 163.4897 | 483.4849 | 180.4283 | 73.1896 | 178.1721 | 192.3154 | 177.2549
348.4811 | 164.4811 | 483.5961 | 181.0591 | 73.7964 | 178.8113 | 193.2345 | 178.1256
349.4825 | 165.4825 | 483.8654 | 181.6686 | 74.4325 | 179.4395 | 194.2166 | 178.9526
350.474 | 166.474 | 484.2207 | 182.2435 | 75.0404 | 180.0293 | 195.1533 | 179.79
351.4754 | 167.4754 | 484.3661 | 182.7934 | 75.6529 | 180.6087 | 196.1196 | 180.6442
352.4768 | 168.4768 | 484.398 | 183.3106 | 76.2686 | 181.1759 | 197.0677 | 181.5139
353.4783 | 169.4783 | 484.4506 | 183.8124 | 76.8693 | 181.742 | 198.0059 | 182.3565
354.4897 | 170.4897 | 484.5682 | 184.3089 | 77.4759 | 182.3193 | 198.9207 | 183.1772
355.4912 | 171.4912 | 484.5114 | 184.7898 | 78.0652 | 182.8961 | 199.8273 | 183.9768
356.4826 | 172.4826 | 484.5708 | 185.2459 | 78.6383 | 183.4449 | 200.6889 | 184.811
357.474 | 173.474 | 484.5772 | 185.6801 | 79.1866 | 183.9884 | 201.612 | 185.5842
358.4855 | 174.4855 | 484.6006 | 186.1022 | 79.7264 | 184.5402 | 202.5748 | 186.4183
359.4769 | 175.4769 | 484.6501 | 186.4981 | 80.2477 | 185.0602 | 203.4351 | 187.2301
360.4783 | 176.4783 | 484.7567 | 186.8735 | 80.7455 | 185.5888 | 204.3259 | 188.0304
361.4798 | 177.4798 | 484.7711 | 187.2338 | 81.2288 | 186.0931 | 205.2154 | 188.822
362.4712 | 178.4712 | 484.9192 | 187.5901 | 81.6935 | 186.5925 | 205.948 | 189.6509
363.4726 | 179.4726 | 485.1099 | 187.9131 | 82.1255 | 187.0873 | 206.7763 | 190.4668
364.4741 | 180.4741 | 485.2692 | 188.2102 | 82.5535 | 187.5841 | 207.6895 | 191.258
365.4755 | 181.4755 | 485.4664 | 188.5036 | 82.9966 | 188.0881 | 208.5442 | 192.0417
366.477 | 182.477 | 485.6278 | 188.8066 | 83.4593 | 188.5868 | 209.3686 | 192.8115
367.4784 | 183.4784 | 485.6415 | 189.0829 | 83.9781 | 189.0786 | 210.1224 | 193.5834
368.4798 | 184.4798 | 485.8502 | 189.3348 | 84.5349 | 189.5755 | 210.9386 | 194.3786
369.4713 | 185.4713 | 485.9074 | 189.5805 | 85.1187 | 190.0695 | 211.6935 | 195.1527
370.4727 | 186.4727 | 485.9912 | 189.7999 | 85.7382 | 190.5499 | 212.442 | 195.9155
371.4742 | 187.4742 | 485.9657 | 190.0113 | 86.3483 | 191.0101 | 213.2231 | 196.6471
372.4756 | 188.4756 | 486.0104 | 190.2295 | 86.9724 | 191.4781 | 213.8846 | 197.3683
373.477 | 189.477 | 485.9999 | 190.4421 | 87.5861 | 191.9359 | 214.5993 | 198.0776
374.4785 | 190.4785 | 485.9658 | 190.6236 | 88.2134 | 192.3848 | 215.3188 | 198.7782
375.4799 | 191.4799 | 485.9837 | 190.8115 | 88.8257 | 192.8512 | 216.0216 | 199.4908
376.4713 | 192.4713 | 485.8876 | 190.9501 | 89.4322 | 193.298 | 216.6329 | 200.2071
377.4728 | 193.4728 | 485.8535 | 191.1398 | 90.0294 | 193.7672 | 217.3186 | 200.9221
378.4742 | 194.4742 | 485.7143 | 191.2688 | 90.627 | 194.2236 | 218.1174 | 201.613
379.4757 | 195.4757 | 485.5867 | 191.4165 | 91.2187 | 194.6954 | 218.7943 | 202.3155
380.4771 | 196.4771 | 485.7072 | 191.5218 | 91.8264 | 195.1692 | 219.555 | 202.9815
381.4785 | 197.4785 | 485.6119 | 191.6189 | 92.4119 | 195.6343 | 220.2992 | 203.6881
382.48 | 198.48 | 485.5353 | 191.7254 | 92.9961 | 196.1037 | 220.9962 | 204.3421
383.4714 | 199.4714 | 485.617 | 191.7694 | 93.5836 | 196.5651 | 221.7573 | 205.0258
384.4728 | 200.4728 | 485.7307 | 191.9447 | 94.1618 | 197.0317 | 222.4382 | 205.6692
385.4743 | 201.4743 | 485.8744 | 192.2133 | 94.7493 | 197.4983 | 223.1328 | 206.3491
386.4757 | 202.4757 | 485.7488 | 192.5823 | 95.319 | 197.9821 | 223.8531 | 206.9729
387.4772 | 203.4772 | 485.6711 | 193.0157 | 95.9212 | 198.4572 | 224.5198 | 207.6005
388.4786 | 204.4786 | 485.554 | 193.5283 | 96.4895 | 198.9346 | 225.2057 | 208.269
389.48 | 205.48 | 485.4488 | 194.0511 | 97.0471 | 199.4188 | 225.8739 | 208.8771
390.4715 | 206.4715 | 485.2858 | 194.5761 | 97.6812 | 199.8948 | 226.547 | 209.5287
391.4829 | 207.4829 | 485.1806 | 195.12 | 98.2827 | 200.3955 | 227.2341 | 210.1283
392.4744 | 208.4744 | 485.0443 | 195.595 | 98.9267 | 200.892 | 227.8711 | 210.747
393.4758 | 209.4758 | 484.8907 | 196.0695 | 99.5668 | 201.4233 | 228.501 | 211.3587
394.4772 | 210.4772 | 484.7518 | 196.4221 | 100.2578 | 201.936 | 229.149 | 211.9864
395.4787 | 211.4787 | 484.7122 | 196.737 | 100.977 | 202.4599 | 229.7328 | 212.5357
396.4801 | 212.4801 | 484.5799 | 196.9669 | 101.7222 | 202.9833 | 230.3968 | 213.1323
397.4816 | 213.4816 | 484.5571 | 197.0416 | 102.4918 | 203.5256 | 230.9923 | 213.6601
398.473 | 214.473 | 484.4204 | 196.8666 | 103.2622 | 204.0782 | 231.6074 | 214.247
399.4744 | 215.4744 | 484.5651 | 196.4082 | 104.0424 | 204.6281 | 232.2639 | 214.8089
400.4759 | 216.4759 | 484.7934 | 196.0067 | 104.7991 | 205.1698 | 232.7478 | 215.4063
401.4773 | 217.4773 | 484.8502 | 195.6386 | 105.5636 | 205.7021 | 233.2892 | 215.9505
402.4787 | 218.4787 | 484.8413 | 195.3328 | 106.2835 | 206.2422 | 233.8475 | 216.5007
403.4802 | 219.4802 | 485.0197 | 195.1125 | 106.9843 | 206.7709 | 234.4359 | 217.0747
404.4716 | 220.4716 | 485.0821 | 194.949 | 107.6633 | 207.3301 | 235.037 | 217.6078
405.473 | 221.473 | 485.0767 | 194.778 | 108.2979 | 207.8996 | 235.6157 | 218.1538
406.4745 | 222.4745 | 484.982 | 194.6611 | 108.8833 | 208.4685 | 236.202 | 218.7058
407.4759 | 223.4759 | 484.9327 | 194.6078 | 109.4273 | 209.0301 | 236.7296 | 219.2299
408.4774 | 224.4774 | 484.8403 | 194.6181 | 109.9295 | 209.6019 | 237.3045 | 219.7131
409.4788 | 225.4788 | 484.6286 | 194.5873 | 110.3762 | 210.1898 | 237.9026 | 220.201
410.4802 | 226.4802 | 484.6243 | 194.4958 | 110.7698 | 210.7597 | 238.4615 | 220.712
411.4717 | 227.4717 | 484.4801 | 194.446 | 111.1493 | 211.3566 | 239.0052 | 221.2209
412.4731 | 228.4731 | 484.386 | 194.3961 | 111.5403 | 211.9347 | 239.4966 | 221.7285
413.4745 | 229.4745 | 484.3394 | 194.2944 | 111.9416 | 212.5006 | 240.0941 | 222.2403
414.476 | 230.476 | 484.3427 | 194.1747 | 112.437 | 213.0577 | 240.6099 | 222.717
415.4774 | 231.4774 | 484.2951 | 194.1371 | 112.9423 | 213.6252 | 241.1431 | 223.2076
416.4789 | 232.4789 | 484.3215 | 194.1425 | 113.4648 | 214.1887 | 241.7203 | 223.6961
417.4803 | 233.4803 | 484.4136 | 194.2249 | 113.9987 | 214.7501 | 242.3317 | 224.1747
418.4717 | 234.4717 | 484.3537 | 194.3324 | 114.5101 | 215.3084 | 242.8895 | 224.6134
419.4732 | 235.4732 | 484.2875 | 194.4404 | 115.0611 | 215.8837 | 243.4292 | 225.0741
420.4746 | 236.4746 | 484.3381 | 194.592 | 115.563 | 216.4525 | 244.0293 | 225.5459
421.4761 | 237.4761 | 484.21 | 194.729 | 116.0573 | 217.0218 | 244.5565 | 226.0017
422.4775 | 238.4775 | 484.1635 | 194.901 | 116.5421 | 217.5843 | 245.1415 | 226.493
423.4789 | 239.4789 | 484.2729 | 195.0403 | 117.0173 | 218.1251 | 245.7396 | 226.9194
424.4804 | 240.4804 | 484.2842 | 195.1982 | 117.4916 | 218.6915 | 246.3262 | 227.3388
425.4718 | 241.4718 | 484.4041 | 195.3662 | 117.9709 | 219.2619 | 246.8884 | 227.7697
426.4732 | 242.4732 | 484.4746 | 195.5476 | 118.4892 | 219.8343 | 247.4649 | 228.1927
427.4747 | 243.4747 | 484.5128 | 195.7447 | 119.085 | 220.3997 | 247.9967 | 228.6319
428.4761 | 244.4761 | 484.5816 | 195.943 | 119.8591 | 220.9809 | 248.55 | 229.0931
429.4776 | 245.4776 | 484.6849 | 196.1626 | 120.8769 | 221.5768 | 249.0986 | 229.5876
430.479 | 246.479 | 484.77 | 196.3801 | 122.1424 | 222.1712 | 249.5917 | 230.0024
431.4804 | 247.4804 | 485.0437 | 196.6066 | 123.5426 | 222.7894 | 250.227 | 230.4866
432.4819 | 248.4819 | 485.208 | 196.8197 | 124.9876 | 223.4153 | 250.7713 | 230.9701
433.4733 | 249.4733 | 485.3191 | 197.0599 | 126.4189 | 224.0624 | 251.3072 | 231.3916
434.4747 | 250.4747 | 485.3007 | 197.3023 | 127.8256 | 224.7236 | 251.839 | 231.7987
435.4762 | 251.4762 | 485.1967 | 197.5717 | 129.2123 | 225.4126 | 252.3375 | 232.2504
436.4776 | 252.4776 | 485.1266 | 197.8463 | 130.5399 | 226.12 | 252.8495 | 232.7076
437.4791 | 253.4791 | 485.065 | 198.1586 | 131.8359 | 226.8202 | 253.3864 | 233.1437
438.4805 | 254.4805 | 484.8363 | 198.4983 | 133.0761 | 227.5324 | 254.0664 | 233.4888
439.4819 | 255.4819 | 484.5821 | 198.8377 | 134.292 | 228.2473 | 254.6112 | 233.8857
440.4734 | 256.4734 | 484.6219 | 199.1866 | 135.4498 | 228.9745 | 255.1231 | 234.3344
441.4748 | 257.4748 | 484.4641 | 199.5278 | 136.5948 | 229.6943 | 255.7023 | 234.7395
442.4762 | 258.4762 | 484.0789 | 199.8843 | 137.723 | 230.4181 | 256.2167 | 235.1604
443.4777 | 259.4777 | 483.8595 | 200.2148 | 138.8106 | 231.155 | 256.7723 | 235.5404
444.4791 | 260.4791 | 483.5531 | 200.5344 | 139.8878 | 231.8872 | 257.23 | 235.9346
445.4806 | 261.4806 | 483.4328 | 200.8334 | 140.9181 | 232.6287 | 257.7475 | 236.3499
446.472 | 262.472 | 483.4088 | 201.1313 | 141.9346 | 233.366 | 258.2658 | 236.7187
447.4734 | 263.4734 | 483.3642 | 201.3863 | 142.953 | 234.1103 | 258.7681 | 237.1285
448.4749 | 264.4749 | 483.4065 | 201.665 | 143.9412 | 234.8717 | 259.2694 | 237.4545
449.4763 | 265.4763 | 483.3814 | 201.9535 | 144.9019 | 235.6331 | 259.7187 | 237.816
450.4778 | 266.4778 | 483.2612 | 202.4433 | 145.8824 | 236.4071 | 260.1038 | 238.2597
451.4792 | 267.4792 | 483.2758 | 203.0197 | 146.8222 | 237.1773 | 260.5422 | 238.6257
452.4806 | 268.4806 | 483.3158 | 203.583 | 147.749 | 237.728 | 261.0297 | 239.0188
453.4721 | 269.4721 | 483.4363 | 204.1204 | 148.6671 | 238.4055 | 261.48 | 239.3919
454.4735 | 270.4735 | 483.5213 | 204.6471 | 149.5623 | 239.1567 | 261.882 | 239.7845
455.4749 | 271.4749 | 483.5178 | 205.2026 | 150.468 | 239.9338 | 262.3354 | 240.1845
456.4764 | 272.4764 | 483.6098 | 205.7259 | 151.3558 | 240.7634 | 262.8512 | 240.6085
457.4778 | 273.4778 | 483.8847 | 206.2714 | 152.2182 | 241.4842 | 263.2972 | 241.0128
458.4793 | 274.4793 | 484.0176 | 206.8362 | 153.0856 | 242.2279 | 263.7129 | 241.397
459.4807 | 275.4807 | 484.197 | 207.4209 | 153.9288 | 242.9155 | 264.253 | 241.7439
460.4721 | 276.4721 | 484.3066 | 207.9152 | 154.7801 | 243.5325 | 264.7854 | 242.1429
461.4736 | 277.4736 | 484.3425 | 208.5394 | 155.6137 | 244.0797 | 265.3114 | 242.5157
462.475 | 278.475 | 484.3948 | 209.3029 | 156.4494 | 244.4581 | 265.8256 | 242.8865
463.4764 | 279.4764 | 484.4137 | 210.1768 | 157.2515 | 244.6569 | 266.3428 | 243.2682
464.4779 | 280.4779 | 484.3582 | 211.4322 | 158.072 | 244.4245 | 266.8932 | 243.6531
465.4793 | 281.4793 | 484.1821 | 213.0472 | 158.8707 | 244.0028 | 267.2993 | 244.0457
466.4808 | 282.4808 | 484.3625 | 214.7647 | 159.6747 | 243.4928 | 267.7714 | 244.4308
467.4722 | 283.4722 | 484.5859 | 216.1989 | 160.4698 | 242.9844 | 268.1981 | 244.8106
468.4736 | 284.4736 | 484.6612 | 217.4127 | 161.2439 | 242.4879 | 268.6796 | 245.1846
469.4751 | 285.4751 | 484.8125 | 218.4835 | 162.0071 | 242.0475 | 269.1159 | 245.5896
470.4765 | 286.4765 | 485.0887 | 219.381 | 162.7837 | 241.7952 | 269.6742 | 245.948
471.478 | 287.478 | 485.2183 | 220.0822 | 163.5391 | 241.6567 | 270.1564 | 246.239
472.4794 | 288.4794 | 485.3659 | 220.8788 | 164.294 | 241.6244 | 270.6691 | 246.6111
473.4708 | 289.4708 | 485.3383 | 221.7474 | 165.0516 | 241.6277 | 271.1201 | 246.951
474.4723 | 290.4723 | 485.2876 | 222.1651 | 165.7603 | 241.5883 | 271.578 | 247.3111
475.4737 | 291.4737 | 485.1359 | 222.6423 | 166.5289 | 241.536 | 271.9442 | 247.676
476.4751 | 292.4751 | 485.0721 | 223.1456 | 167.2622 | 241.4644 | 272.3771 | 248.0086
477.4766 | 293.4766 | 484.928 | 223.5481 | 167.978 | 241.4294 | 272.6529 | 248.3504
478.478 | 294.478 | 484.7366 | 223.7513 | 168.7157 | 241.3962 | 272.7779 | 248.6789
479.4795 | 295.4795 | 484.6175 | 224.2432 | 169.4231 | 241.322 | 273.108 | 248.9999
480.4809 | 296.4809 | 484.4932 | 224.7673 | 170.1223 | 241.2858 | 273.477 | 249.3646
481.4823 | 297.4823 | 484.4326 | 225.0788 | 170.8132 | 241.2309 | 273.9381 | 249.7345
482.4738 | 298.4738 | 484.4288 | 225.4805 | 171.5161 | 241.1421 | 274.4286 | 250.0765
483.4752 | 299.4752 | 484.4102 | 226.557 | 172.2199 | 241.0331 | 274.9189 | 250.4166
484.4766 | 300.4766 | 484.3816 | 227.3507 | 172.9105 | 240.924 | 275.2348 | 250.7509
485.4781 | 301.4781 | 484.2883 | 228.0567 | 173.5887 | 240.856 | 275.6844 | 251.1092
486.4795 | 302.4795 | 484.2693 | 228.5728 | 174.2745 | 240.9377 | 276.14 | 251.5007
487.481 | 303.481 | 484.1979 | 229.0386 | 174.9306 | 241.08 | 276.5367 | 251.8978
488.4724 | 304.4724 | 484.2182 | 229.5013 | 175.6042 | 241.3134 | 276.7898 | 252.2799
489.4738 | 305.4738 | 484.4754 | 230.1063 | 176.264 | 241.5953 | 277.213 | 252.5958
490.4753 | 306.4753 | 484.6355 | 230.4389 | 176.9253 | 241.9777 | 277.5756 | 252.9812
491.4767 | 307.4767 | 484.7508 | 230.6849 | 177.5778 | 242.4751 | 277.7988 | 253.3689
492.4781 | 308.4781 | 484.7355 | 230.9905 | 178.2195 | 243.0524 | 278.2069 | 253.7415
493.4796 | 309.4796 | 484.5918 | 231.2734 | 178.8511 | 243.6403 | 278.6313 | 254.0885
494.471 | 310.471 | 484.6202 | 231.5858 | 179.5021 | 244.2523 | 279.0745 | 254.4003
495.4725 | 311.4725 | 484.6099 | 231.8262 | 180.119 | 244.9108 | 279.6097 | 254.774
496.4739 | 312.4739 | 484.6782 | 232.0803 | 180.7584 | 247.5207 | 280.1481 | 255.1484
497.4753 | 313.4753 | 484.6939 | 232.8308 | 181.3813 | 248.2969 | 280.7043 | 255.5302
498.4768 | 314.4768 | 484.6007 | 233.3382 | 182.0081 | 249.189 | 281.2001 | 255.9311
499.4782 | 315.4782 | 484.6417 | 233.8088 | 182.6209 | 250.1475 | 281.7749 | 256.304
500.4797 | 316.4797 | 484.6888 | 233.9941 | 183.2419 | 249.9988 | 282.226 | 256.6855
501.4711 | 317.4711 | 484.8761 | 234.2894 | 183.8405 | 249.9482 | 282.6787 | 257.082
502.4725 | 318.4725 | 484.9036 | 234.1927 | 184.4492 | 249.9836 | 282.9709 | 257.418
503.474 | 319.474 | 485.0847 | 233.7194 | 185.0507 | 249.7528 | 283.3672 | 257.8237
504.4754 | 320.4754 | 485.0381 | 233.892 | 185.6377 | 249.9407 | 283.7983 | 258.1777
505.4768 | 321.4768 | 485.0293 | 234.0834 | 186.2247 | 250.217 | 284.268 | 258.6184
506.4783 | 322.4783 | 485.0495 | 234.3991 | 186.8262 | 250.5051 | 284.6225 | 259.0831
507.4797 | 323.4797 | 485.1412 | 234.7776 | 187.4034 | 250.8561 | 285.0714 | 259.4562
508.4812 | 324.4812 | 485.2464 | 235.1781 | 187.9804 | 251.1318 | 285.4299 | 259.9344
509.4726 | 325.4726 | 485.2078 | 235.5512 | 188.5652 | 251.498 | 285.8481 | 260.3065
510.474 | 326.474 | 485.189 | 235.9041 | 189.1236 | 251.9091 | 286.3012 | 260.7015
511.4755 | 327.4755 | 485.2069 | 236.4818 | 189.691 | 252.2675 | 286.7732 | 261.0911
512.4769 | 328.4769 | 485.0315 | 236.8612 | 190.2459 | 252.6152 | 287.1661 | 261.4944
513.4783 | 329.4783 | 484.8506 | 237.0817 | 190.8091 | 252.894 | 287.6352 | 261.9077
514.4798 | 330.4798 | 484.5127 | 238.2344 | 191.3687 | 252.2984 | 288.1312 | 262.3164
515.4812 | 331.4812 | 484.4571 | 240.6241 | 191.9127 | 251.594 | 288.4708 | 262.7349
516.4727 | 332.4727 | 484.534 | 243.7708 | 192.468 | 251.2876 | 288.8195 | 263.1137
517.4741 | 333.4741 | 484.5307 | 247.7824 | 193.0116 | 251.0732 | 289.1017 | 263.5327
518.4755 | 334.4755 | 484.5083 | 251.3549 | 193.5511 | 250.7022 | 289.4538 | 264.0082
519.477 | 335.477 | 484.443 | 254.4604 | 194.0792 | 250.2698 | 289.8343 | 264.4688
520.4784 | 336.4784 | 484.4024 | 257.1713 | 194.6272 | 250.2113 | 290.1812 | 264.9572
521.4799 | 337.4799 | 484.2533 | 259.5412 | 195.1437 | 250.3601 | 290.6389 | 265.3725
522.4713 | 338.4713 | 484.1313 | 261.9065 | 195.6741 | 250.6729 | 291.0391 | 265.8661
523.4827 | 339.4827 | 484.1903 | 264.0677 | 196.2009 | 251.0904 | 291.4403 | 266.2439
524.4742 | 340.4742 | 484.3255 | 266.0712 | 196.7215 | 251.5188 | 291.6386 | 266.6719
525.4756 | 341.4756 | 484.497 | 267.9656 | 197.2366 | 251.9823 | 292.0305 | 267.1125
526.477 | 342.477 | 484.6029 | 269.8277 | 197.7592 | 252.458 | 292.3903 | 267.5329
527.4785 | 343.4785 | 484.5861 | 271.5604 | 198.2795 | 252.9691 | 292.6882 | 267.9789
528.4799 | 344.4799 | 484.5983 | 273.1828 | 198.7799 | 253.4382 | 292.903 | 268.4114
529.4814 | 345.4814 | 484.5909 | 274.7144 | 199.2829 | 253.9201 | 293.0478 | 268.8229
530.4728 | 346.4728 | 484.6925 | 276.1616 | 199.7946 | 254.4579 | 293.3565 | 269.3418
531.4742 | 347.4742 | 484.5753 | 277.5011 | 200.2938 | 254.9156 | 293.5827 | 269.826
532.4757 | 348.4757 | 484.3657 | 278.8158 | 200.7851 | 255.4529 | 293.9425 | 270.3063
533.4771 | 349.4771 | 484.1549 | 280.0953 | 201.294 | 256.1145 | 294.3709 | 270.8151
534.4785 | 350.4785 | 484.1476 | 281.3223 | 201.7728 | 256.8181 | 294.8201 | 271.2445
535.48 | 351.48 | 484.1023 | 282.4635 | 202.2735 | 257.6289 | 295.2831 | 271.7383
536.4814 | 352.4814 | 484.1201 | 283.6219 | 202.7382 | 258.4645 | 295.7966 | 272.229
537.4728 | 353.4728 | 484.0347 | 284.7662 | 203.2207 | 259.2709 | 296.2008 | 272.6698
538.4743 | 354.4743 | 483.9933 | 285.9663 | 203.6983 | 260.065 | 296.6664 | 273.155
539.4757 | 355.4757 | 483.9804 | 287.0708 | 204.166 | 260.8638 | 297.1155 | 273.6037
540.4772 | 356.4772 | 484.0795 | 288.0862 | 204.6571 | 261.6846 | 297.518 | 274.1021
541.4786 | 357.4786 | 484.2163 | 289.2986 | 205.1067 | 262.4632 | 297.8641 | 274.5439
542.48 | 358.48 | 484.3898 | 290.4055 | 205.5697 | 263.2693 | 298.3227 | 275.0232
543.4715 | 359.4715 | 484.4023 | 291.4773 | 206.0469 | 264.0987 | 298.7709 | 275.5247
544.4729 | 360.4729 | 484.3454 | 292.5137 | 206.5053 | 264.9583 | 299.1706 | 275.9751
545.4744 | 361.4744 | 484.2392 | 293.5216 | 206.9557 | 265.7506 | 299.5597 | 276.4783
546.4758 | 362.4758 | 484.1721 | 294.5208 | 207.4257 | 266.9413 | 299.9322 | 276.9058
547.4772 | 363.4772 | 484.0405 | 295.5163 | 207.8801 | 268.5515 | 300.2643 | 277.3763
548.4787 | 364.4787 | 484.1022 | 296.517 | 208.3295 | 270.1117 | 300.662 | 277.8866
549.4801 | 365.4801 | 484.2353 | 297.5051 | 208.7802 | 271.3351 | 301.0527 | 278.363
550.4816 | 366.4816 | 484.2949 | 298.4604 | 209.2442 | 272.4933 | 301.3709 | 278.7977
551.473 | 367.473 | 484.2216 | 299.3983 | 209.6927 | 273.6774 | 301.7201 | 279.2144
552.4744 | 368.4744 | 484.2816 | 300.2736 | 210.1316 | 274.7494 | 302.1868 | 279.6919
553.4759 | 369.4759 | 484.3455 | 301.1666 | 210.5734 | 275.6853 | 302.4367 | 280.1133
554.4773 | 370.4773 | 484.2176 | 302.007 | 211.0367 | 276.676 | 302.8674 | 280.5883
555.4787 | 371.4787 | 484.2111 | 302.8529 | 211.4865 | 277.9902 | 303.1789 | 281.009
556.4802 | 372.4802 | 484.2706 | 303.7176 | 211.9423 | 279.0208 | 303.4985 | 281.477
557.4716 | 373.4716 | 484.221 | 304.5529 | 212.3681 | 279.9903 | 303.782 | 281.8632
558.473 | 374.473 | 484.1972 | 305.3857 | 212.8222 | 280.8893 | 304.1353 | 282.2979
559.4745 | 375.4745 | 484.1526 | 306.1888 | 213.2414 | 281.6788 | 304.4483 | 282.7134
560.4759 | 376.4759 | 484.1493 | 306.9903 | 213.6999 | 282.4484 | 304.7224 | 283.1628
561.4774 | 377.4774 | 484.2429 | 307.8615 | 214.1586 | 283.2584 | 304.9491 | 283.6351
562.4788 | 378.4788 | 484.3185 | 308.7042 | 214.5916 | 284.1205 | 305.3031 | 284.1373
563.4802 | 379.4802 | 484.3542 | 309.5626 | 215.0327 | 284.932 | 305.6158 | 284.545
564.4717 | 380.4717 | 484.6919 | 310.3954 | 215.4712 | 285.7193 | 305.9593 | 284.9831
565.4831 | 381.4831 | 484.8408 | 311.2281 | 215.9288 | 286.4077 | 306.2831 | 285.4212
566.4746 | 382.4746 | 484.8633 | 312.0349 | 216.3525 | 287.0052 | 306.6606 | 285.8565
567.476 | 383.476 | 485.012 | 312.7827 | 216.789 | 287.6207 | 307.016 | 286.2903
568.4774 | 384.4774 | 485.1859 | 313.4493 | 217.2233 | 288.1347 | 307.3508 | 286.7124
569.4789 | 385.4789 | 485.1712 | 314.099 | 217.6626 | 288.5701 | 307.7048 | 287.1933
570.5704 | 386.5704 | 485.1815 | 314.8159 | 218.1411 | 289.1504 | 308.0805 | 287.6984
571.4818 | 387.4818 | 485.1822 | 315.461 | 218.5456 | 289.6416 | 308.3855 | 288.0618
572.4732 | 388.4732 | 485.1014 | 316.1967 | 218.9773 | 290.195 | 308.7087 | 288.478
573.4746 | 389.4746 | 485.1152 | 316.9625 | 219.4126 | 290.7565 | 309.0341 | 288.9402
574.4761 | 390.4761 | 484.947 | 317.7202 | 219.862 | 291.4138 | 309.4028 | 289.3962
575.4775 | 391.4775 | 484.9258 | 318.4913 | 220.2905 | 292.008 | 309.7005 | 289.7142
576.4789 | 392.4789 | 484.97 | 319.3084 | 220.7199 | 292.2242 | 309.9356 | 290.1618
577.4804 | 393.4804 | 484.7759 | 320.112 | 221.1519 | 292.2045 | 310.1986 | 290.5537
578.4718 | 394.4718 | 484.5878 | 320.9161 | 221.5751 | 292.5003 | 310.5295 | 290.9173
579.4732 | 395.4732 | 484.6982 | 321.6612 | 222.0178 | 292.8795 | 308.2836 | 291.3176
580.4747 | 396.4747 | 484.7163 | 322.439 | 222.4531 | 293.3099 | 306.6121 | 291.6547
581.4761 | 397.4761 | 484.6829 | 323.1885 | 222.8818 | 293.7603 | 305.9514 | 292.0414
582.4776 | 398.4776 | 484.8081 | 323.9331 | 223.3052 | 294.2549 | 305.6586 | 292.3762
583.479 | 399.479 | 484.5707 | 324.6669 | 223.7338 | 294.7403 | 305.4176 | 292.7197
584.4804 | 400.4804 | 484.267 | 325.3809 | 224.1675 | 295.3138 | 305.5149 | 293.0108
585.4719 | 401.4719 | 484.148 | 326.1042 | 224.5915 | 295.8397 | 305.8841 | 293.2537
586.4733 | 402.4733 | 483.9875 | 326.7893 | 225.0193 | 296.4146 | 305.6534 | 293.6388
587.4747 | 403.4747 | 483.736 | 327.4728 | 225.4378 | 296.9881 | 305.828 | 294
588.4762 | 404.4762 | 483.7591 | 328.133 | 225.865 | 297.534 | 305.9454 | 294.3239
589.4776 | 405.4776 | 483.8276 | 328.8412 | 226.3021 | 298.1046 | 305.6651 | 294.5896
590.4791 | 406.4791 | 483.8072 | 329.5225 | 226.7291 | 298.7606 | 305.9275 | 294.8293
591.4805 | 407.4805 | 483.7552 | 330.1829 | 227.1617 | 299.4582 | 306.1222 | 295.1555
592.4819 | 408.4819 | 483.8472 | 330.8437 | 227.596 | 300.1274 | 306.0015 | 295.4622
593.4834 | 409.4834 | 483.9151 | 331.4734 | 228.027 | 300.7369 | 305.7454 | 295.8311
594.4748 | 410.4748 | 484.0516 | 332.1262 | 228.4468 | 301.3538 | 306.0764 | 296.1429
595.4763 | 411.4763 | 484.0358 | 332.8138 | 228.8855 | 302.0107 | 306.2252 | 296.4602
596.4777 | 412.4777 | 483.9902 | 333.4314 | 229.3116 | 302.64 | 305.9753 | 296.7526
597.4791 | 413.4791 | 483.9471 | 333.9894 | 229.7503 | 303.2787 | 306.4438 | 297.0101
598.4806 | 414.4806 | 483.9097 | 334.6075 | 230.1786 | 303.8896 | 306.7142 | 297.3485
599.472 | 415.472 | 483.9155 | 335.2055 | 230.6169 | 304.5059 | 306.7158 | 297.6276
600.4734 | 416.4734 | 483.8563 | 335.7995 | 231.0471 | 305.0959 | 306.9802 | 297.9035
601.4749 | 417.4749 | 483.7798 | 336.3589 | 231.4848 | 305.6555 | 307.8935 | 298.1176
602.4763 | 418.4763 | 483.6932 | 336.9169 | 231.9301 | 306.1479 | 308.3467 | 298.3907
603.4778 | 419.4778 | 483.6535 | 337.4783 | 232.3599 | 306.7401 | 308.5949 | 298.6537
604.4792 | 420.4792 | 483.6145 | 338.0229 | 232.7973 | 307.3467 | 308.2094 | 298.9273
605.4806 | 421.4806 | 483.5614 | 338.5124 | 233.1981 | 307.893 | 309.1824 | 299.1856
606.4721 | 422.4721 | 483.5436 | 339.0255 | 233.644 | 308.2565 | 309.1793 | 299.4634
607.4735 | 423.4735 | 483.6157 | 339.5363 | 234.0689 | 308.5965 | 309.0663 | 299.702
608.4749 | 424.4749 | 483.7622 | 340.0307 | 234.4944 | 309.0114 | 309.3442 | 299.7395
609.4764 | 425.4764 | 483.8931 | 340.5188 | 234.9152 | 309.4728 | 308.7747 | 300.0053
610.4778 | 426.4778 | 483.8785 | 340.9595 | 235.3353 | 309.9159 | 308.0019 | 300.3145
611.4793 | 427.4793 | 483.9483 | 341.3965 | 235.7657 | 310.3843 | 307.8838 | 300.6373
612.4807 | 428.4807 | 483.9199 | 341.8456 | 236.1991 | 310.9082 | 307.4997 | 300.8785
613.4821 | 429.4821 | 483.6962 | 342.2911 | 236.6261 | 311.4203 | 307.8334 | 301.0937
614.4736 | 430.4736 | 483.5305 | 342.6825 | 237.0584 | 311.8839 | 307.9556 | 301.2862
615.475 | 431.475 | 483.5144 | 343.0863 | 237.4917 | 312.3107 | 307.971 | 301.464
616.4764 | 432.4764 | 483.4559 | 343.4932 | 237.922 | 312.7566 | 307.2858 | 301.6612
617.4779 | 433.4779 | 483.3978 | 343.8866 | 238.3398 | 313.1612 | 307.6773 | 301.8886
618.4793 | 434.4793 | 483.5759 | 344.2666 | 238.7859 | 313.5466 | 307.2344 | 302.1059
619.4808 | 435.4808 | 483.5902 | 344.6512 | 239.2175 | 313.9609 | 307.3867 | 302.317
620.4722 | 436.4722 | 483.5734 | 345.0232 | 239.6457 | 314.3434 | 307.3286 | 302.522
621.4736 | 437.4736 | 483.5681 | 345.392 | 240.0691 | 314.786 | 307.9196 | 302.7409
622.4751 | 438.4751 | 483.5598 | 345.7267 | 240.5132 | 315.2343 | 307.6452 | 302.8901
623.4765 | 439.4765 | 483.573 | 346.0634 | 240.9364 | 315.6764 | 307.3066 | 303.1114
624.478 | 440.478 | 483.6708 | 346.3912 | 241.379 | 316.1047 | 307.3599 | 303.3201
625.4794 | 441.4794 | 483.8481 | 346.7236 | 241.797 | 316.5279 | 307.4978 | 303.499
626.4808 | 442.4808 | 483.9211 | 347.0164 | 242.2414 | 316.8574 | 307.3634 | 303.7136
627.4723 | 443.4723 | 483.9697 | 347.3383 | 242.6797 | 317.262 | 307.5138 | 303.9322
628.4737 | 444.4737 | 484.0916 | 347.6136 | 243.1123 | 317.6567 | 307.3167 | 304.1385
629.4751 | 445.4751 | 484.1519 | 347.94 | 243.5542 | 318.0284 | 307.3033 | 304.4139
630.4766 | 446.4766 | 484.2714 | 348.2714 | 243.987 | 318.4153 | 307.9091 | 304.6587
631.478 | 447.478 | 484.3254 | 348.5862 | 244.4316 | 318.8246 | 308.4956 | 304.8509
632.4795 | 448.4795 | 484.2393 | 348.9247 | 244.8688 | 319.1712 | 308.2195 | 305.0797
633.4809 | 449.4809 | 484.2702 | 349.1854 | 245.3073 | 319.5087 | 308.0348 | 305.2696
634.4723 | 450.4723 | 484.269 | 349.4379 | 245.7516 | 319.9238 | 307.8933 | 305.5766
635.4738 | 451.4738 | 484.4222 | 349.6884 | 246.19 | 320.2535 | 307.7823 | 305.8444
636.4752 | 452.4752 | 484.4524 | 349.9499 | 246.5899 | 320.5665 | 307.4993 | 306.1484
637.4766 | 453.4766 | 484.4745 | 350.2044 | 247.0603 | 320.9025 | 307.1587 | 306.4431
638.4781 | 454.4781 | 484.5003 | 350.4369 | 247.4832 | 321.2484 | 306.5644 | 306.7441
639.4795 | 455.4795 | 484.4207 | 350.6491 | 247.9186 | 321.5839 | 306.5354 | 307.0101
640.481 | 456.481 | 484.4282 | 350.8775 | 248.3417 | 321.9044 | 305.4565 | 307.285
641.4724 | 457.4724 | 484.3275 | 351.0973 | 248.7867 | 322.301 | 304.8329 | 307.5248
642.4738 | 458.4738 | 484.2879 | 351.3132 | 249.227 | 322.7867 | 304.7231 | 307.8682
643.4753 | 459.4753 | 484.2017 | 351.535 | 249.6924 | 323.1557 | 304.3692 | 308.2086
644.4767 | 460.4767 | 484.1913 | 351.7686 | 250.1325 | 323.5653 | 304.0789 | 308.4612
645.4782 | 461.4782 | 484.2219 | 351.9347 | 250.5535 | 323.8699 | 303.5318 | 308.7374
646.4796 | 462.4796 | 484.1739 | 352.1148 | 250.9901 | 324.2354 | 302.4093 | 308.9835
647.481 | 463.481 | 484.2193 | 352.2933 | 251.4075 | 324.4802 | 302.3337 | 309.2743
648.4725 | 464.4725 | 484.136 | 352.4511 | 251.8097 | 324.9118 | 302.2525 | 309.5476
649.4739 | 465.4739 | 484.0595 | 352.6515 | 252.2206 | 325.2817 | 301.8474 | 309.8076
650.4753 | 466.4753 | 484.0696 | 352.8364 | 252.6317 | 325.6036 | 301.5754 | 310.1071
651.4768 | 467.4768 | 483.9491 | 352.9834 | 253.0701 | 325.9538 | 301.3712 | 310.4569
652.4782 | 468.4782 | 483.9705 | 353.136 | 253.4697 | 326.3835 | 301.3323 | 310.8096
653.4797 | 469.4797 | 484.0677 | 353.2266 | 253.8998 | 326.8288 | 301.1313 | 311.0676
654.4811 | 470.4811 | 484.0311 | 353.3865 | 254.3028 | 327.1969 | 300.6652 | 311.2338
655.4725 | 471.4725 | 484.2113 | 353.4691 | 254.7191 | 327.5393 | 301.6033 | 311.3769
656.474 | 472.474 | 484.3967 | 353.303 | 255.1164 | 327.8931 | 301.1007 | 311.6876
657.4754 | 473.4754 | 484.5941 | 353.2342 | 255.5596 | 328.2117 | 300.1862 | 311.9745
658.4768 | 474.4768 | 484.6613 | 353.4258 | 255.98 | 328.5585 | 299.8234 | 312.2504
659.4783 | 475.4783 | 484.8441 | 353.4052 | 256.3844 | 328.9208 | 299.4362 | 312.5313
660.5899 | 476.5899 | 484.9688 | 352.9 | 256.8489 | 329.3621 | 299.2544 | 312.8173
661.4812 | 477.4812 | 485.0471 | 352.4409 | 257.2276 | 329.7398 | 298.3692 | 313.0321
662.4726 | 478.4726 | 485.0176 | 352.2951 | 257.6335 | 330.0485 | 298.4117 | 313.3235
663.474 | 479.474 | 484.9663 | 352.3406 | 258.0545 | 330.3571 | 298.4579 | 313.6381
664.4755 | 480.4755 | 484.896 | 352.3643 | 258.463 | 330.5554 | 298.9186 | 313.9441
665.4769 | 481.4769 | 484.7178 | 352.41 | 258.8888 | 330.82 | 299.5864 | 314.3453
666.4783 | 482.4783 | 484.6883 | 352.3814 | 259.3804 | 331.0401 | 300.4903 | 314.7764
667.4798 | 483.4798 | 484.8049 | 352.2818 | 259.7568 | 331.2427 | 301.0533 | 315.1661
668.4812 | 484.4812 | 484.8923 | 352.0351 | 260.167 | 331.393 | 301.0951 | 315.4999
669.4727 | 485.4727 | 485.032 | 351.6522 | 260.5737 | 331.5782 | 301.1343 | 315.8415
670.4741 | 486.4741 | 484.94 | 351.2778 | 260.979 | 331.7768 | 301.4607 | 316.1976
671.4755 | 487.4755 | 484.6912 | 350.3027 | 261.3885 | 331.9485 | 301.196 | 316.5418
672.477 | 488.477 | 484.4366 | 349.5324 | 261.7862 | 332.6343 | 300.5138 | 316.8905
673.4784 | 489.4784 | 484.3378 | 349.4583 | 262.1901 | 332.7658 | 300.7698 | 317.1842
674.4799 | 490.4799 | 484.2415 | 349.5807 | 262.5963 | 332.7104 | 300.7803 | 317.4058
675.4813 | 491.4813 | 483.9347 | 349.6445 | 263.0028 | 332.7801 | 300.9666 | 317.6398
676.4727 | 492.4727 | 483.7647 | 349.9173 | 263.3988 | 332.8774 | 300.9379 | 317.835
677.4742 | 493.4742 | 483.604 | 350.1878 | 263.8092 | 333.0451 | 300.7596 | 318.0434
678.4756 | 494.4756 | 483.6117 | 350.406 | 264.2084 | 333.2455 | 300.8826 | 318.2748
679.477 | 495.477 | 483.601 | 350.3962 | 264.6166 | 333.5829 | 301.5493 | 318.4641
680.4785 | 496.4785 | 483.6353 | 350.3433 | 265.0322 | 333.6774 | 302.0008 | 318.8571
681.4799 | 497.4799 | 483.6537 | 350.0598 | 265.4058 | 333.8655 | 301.7287 | 319.1806
682.4814 | 498.4814 | 483.6415 | 349.7952 | 265.8278 | 334.2222 | 301.9164 | 319.5565
683.4728 | 499.4728 | 483.6905 | 349.3912 | 266.2412 | 334.4014 | 301.8307 | 319.8278
684.4742 | 500.4742 | 483.7424 | 349.2305 | 266.6449 | 334.7038 | 301.9677 | 320.1305
685.4757 | 501.4757 | 483.9269 | 349.1347 | 267.0453 | 335.0047 | 301.6643 | 320.42
686.4771 | 502.4771 | 483.9334 | 348.9583 | 267.4629 | 335.2423 | 302.0613 | 320.6506
687.4785 | 503.4785 | 483.8939 | 349.1628 | 267.8731 | 335.5681 | 302.0877 | 321.0009
688.48 | 504.48 | 483.9454 | 349.5734 | 268.2641 | 335.8409 | 302.3977 | 321.271
689.4714 | 505.4714 | 483.9223 | 350.0117 | 268.6778 | 335.959 | 302.4888 | 321.5936
690.4729 | 506.4729 | 483.7809 | 350.2129 | 269.0853 | 336.0803 | 302.7887 | 321.81
691.4743 | 507.4743 | 483.6805 | 349.804 | 269.4856 | 336.2466 | 303.0416 | 322.1066
692.4757 | 508.4757 | 483.5703 | 349.7929 | 269.9129 | 336.3521 | 303.4149 | 322.4095
693.4772 | 509.4772 | 483.4787 | 349.685 | 270.3201 | 336.5795 | 303.3705 | 322.6707
694.4786 | 510.4786 | 483.5003 | 349.7158 | 270.7291 | 336.8277 | 303.7146 | 322.9526
695.4801 | 511.4801 | 483.5831 | 349.8033 | 271.1488 | 337.1357 | 303.8387 | 323.2254
696.4815 | 512.4815 | 483.4669 | 350.0768 | 271.5765 | 337.4226 | 304.195 | 323.5366
697.4829 | 513.4829 | 483.4101 | 350.1874 | 271.9886 | 337.6819 | 304.3914 | 323.7624
698.4744 | 514.4744 | 483.4583 | 350.2741 | 272.4269 | 337.8601 | 304.7883 | 324.1527
699.4758 | 515.4758 | 483.5528 | 350.6405 | 272.9243 | 338.0934 | 304.6829 | 324.4492
700.4772 | 516.4772 | 483.4589 | 350.8615 | 273.432 | 338.2915 | 304.9634 | 324.7229
701.4787 | 517.4787 | 483.3712 | 351.0026 | 273.8498 | 338.1979 | 305.2132 | 325.0088
702.4801 | 518.4801 | 483.4294 | 351.24 | 274.2627 | 338.1473 | 304.5618 | 325.3074
703.4816 | 519.4816 | 483.5314 | 351.4771 | 274.6702 | 338.2996 | 304.5338 | 325.6393
704.473 | 520.473 | 483.5964 | 351.636 | 275.1118 | 338.5106 | 305.1914 | 325.8919
705.4744 | 521.4744 | 483.6826 | 351.9655 | 275.5138 | 338.7168 | 305.727 | 326.2258
706.4759 | 522.4759 | 483.8027 | 352.2495 | 275.9413 | 338.9748 | 305.7105 | 326.6013
707.4773 | 523.4773 | 483.8381 | 352.5949 | 276.3722 | 339.1766 | 305.9789 | 326.87
708.4787 | 524.4787 | 483.8927 | 352.7936 | 276.807 | 339.3815 | 305.7084 | 327.1911
709.4802 | 525.4802 | 483.8665 | 352.8179 | 277.2301 | 339.5886 | 305.4136 | 327.4628
710.4716 | 526.4716 | 483.7726 | 352.798 | 277.7503 | 339.808 | 305.4894 | 327.8047
711.473 | 527.473 | 483.7334 | 353.1516 | 278.1866 | 339.9646 | 305.6703 | 328.0609
712.4745 | 528.4745 | 483.7339 | 353.4528 | 278.6035 | 340.2427 | 305.1787 | 328.3569
713.4759 | 529.4759 | 483.7032 | 353.91 | 279.0803 | 340.4839 | 304.431 | 328.626
714.4774 | 530.4774 | 483.6223 | 354.0801 | 279.5134 | 340.7322 | 304.4806 | 328.7758
715.4788 | 531.4788 | 483.7179 | 354.1246 | 279.9231 | 340.9372 | 304.4019 | 329.0013
716.4802 | 532.4802 | 483.7725 | 354.0849 | 280.3505 | 341.2246 | 304.416 | 329.2641
717.4717 | 533.4717 | 483.6443 | 353.6726 | 280.7578 | 341.1208 | 304.7447 | 329.5265
718.4731 | 534.4731 | 483.6876 | 353.6835 | 281.1958 | 341.0412 | 305.0474 | 329.7428
719.4746 | 535.4746 | 483.6653 | 353.7975 | 281.6103 | 341.1402 | 305.8044 | 329.9723
720.476 | 536.476 | 483.8275 | 354.2334 | 282.0217 | 341.3809 | 306.7584 | 330.2306
721.4774 | 537.4774 | 483.9408 | 354.0994 | 282.4396 | 341.7647 | 307.0504 | 330.5045
722.4789 | 538.4789 | 483.933 | 354.0616 | 282.8529 | 341.8588 | 306.9971 | 330.8013
723.4803 | 539.4803 | 483.9266 | 353.7172 | 283.2604 | 341.9714 | 306.8383 | 331.018
724.4818 | 540.4818 | 483.8624 | 353.3954 | 283.6845 | 342.2565 | 306.6504 | 331.1597
725.4732 | 541.4732 | 483.8008 | 353.4762 | 284.1413 | 342.7424 | 306.896 | 331.3243
726.4746 | 542.4746 | 483.785 | 353.8759 | 284.5448 | 342.9128 | 306.6061 | 331.5649
727.4761 | 543.4761 | 483.7857 | 354.4311 | 284.9568 | 343.0211 | 307.22 | 331.7847
728.4775 | 544.4775 | 483.7618 | 354.992 | 285.3695 | 343.2787 | 307.0917 | 331.931
729.4789 | 545.4789 | 483.7533 | 355.3111 | 285.7787 | 343.5975 | 307.3382 | 332.133
730.4804 | 546.4804 | 483.8298 | 355.3919 | 286.1919 | 343.7555 | 307.5423 | 332.3007
731.4718 | 547.4718 | 483.7512 | 355.5496 | 286.5878 | 343.9773 | 308.0074 | 332.481
732.4732 | 548.4732 | 483.6966 | 355.5053 | 286.9804 | 344.1387 | 307.1392 | 332.6451
733.4747 | 549.4747 | 483.6493 | 355.3162 | 287.3802 | 344.3699 | 307.2961 | 332.8043
734.4761 | 550.4761 | 483.577 | 355.1602 | 287.7751 | 344.6646 | 306.4883 | 333.0101
735.4776 | 551.4776 | 483.557 | 355.2191 | 288.1597 | 344.8026 | 305.5854 | 333.2886
736.479 | 552.479 | 483.5755 | 355.4051 | 288.5668 | 344.8981 | 305.6288 | 333.578
737.4804 | 553.4804 | 483.6187 | 355.5638 | 288.9858 | 345.0742 | 305.3784 | 333.7953
738.4819 | 554.4819 | 483.7614 | 355.8953 | 289.3862 | 345.396 | 305.1966 | 333.9975
739.4733 | 555.4733 | 483.8724 | 356.0354 | 289.7868 | 345.638 | 305.3308 | 334.1413
740.4748 | 556.4748 | 483.7953 | 356.1238 | 290.1865 | 345.9145 | 305.6545 | 334.4057
741.4762 | 557.4762 | 483.6024 | 355.8629 | 290.5911 | 346.1421 | 305.7077 | 334.6487
742.4776 | 558.4776 | 483.5327 | 356.0366 | 290.9822 | 346.3358 | 305.9795 | 334.8001
743.4791 | 559.4791 | 483.4238 | 355.9437 | 291.3748 | 346.6094 | 306.755 | 335.0873
744.4805 | 560.4805 | 483.3432 | 356.0864 | 291.7918 | 346.8682 | 307.7339 | 335.2789
745.482 | 561.482 | 483.5103 | 356.1672 | 292.1967 | 347.048 | 308.2641 | 335.4635
746.4734 | 562.4734 | 483.673 | 356.4407 | 292.6054 | 347.2612 | 308.3497 | 335.6501
747.4748 | 563.4748 | 483.7873 | 356.5547 | 293.0134 | 347.1934 | 307.8508 | 335.7772
748.4763 | 564.4763 | 483.8498 | 356.5016 | 293.4099 | 347.324 | 307.8124 | 336.0684
749.4777 | 565.4777 | 483.9888 | 356.3363 | 293.8064 | 347.5557 | 308.2321 | 336.2215
750.5192 | 566.5192 | 484.1721 | 356.101 | 294.2086 | 347.7999 | 308.0626 | 336.5317
751.4806 | 567.4806 | 484.2764 | 356.1279 | 294.5797 | 347.9371 | 307.882 | 336.6704
752.472 | 568.472 | 484.3826 | 356.4174 | 294.9699 | 348.2245 | 307.0961 | 336.9393
753.4734 | 569.4734 | 484.3925 | 356.664 | 295.359 | 348.5537 | 307.5629 | 337.0888
754.4749 | 570.4749 | 484.4433 | 356.8583 | 295.7479 | 348.6988 | 307.7456 | 337.3345
755.4763 | 571.4763 | 484.4991 | 357.2025 | 296.1407 | 349.0183 | 308.0619 | 337.5722
756.4778 | 572.4778 | 484.5205 | 357.0626 | 296.5847 | 349.3696 | 308.1536 | 337.8489
757.4792 | 573.4792 | 484.4575 | 357.2963 | 296.9539 | 349.613 | 308.129 | 338.1247
758.4806 | 574.4806 | 484.4486 | 357.448 | 297.3213 | 349.864 | 308.4912 | 338.3959
759.4721 | 575.4721 | 484.4027 | 357.5273 | 297.6968 | 350.1481 | 308.8796 | 338.5548
760.4735 | 576.4735 | 484.3355 | 357.6625 | 298.0722 | 350.3754 | 309.0158 | 338.7736
761.4749 | 577.4749 | 484.3588 | 358.0309 | 298.4627 | 350.521 | 308.9874 | 338.975
762.4764 | 578.4764 | 484.3597 | 358.2368 | 298.8364 | 350.715 | 309.174 | 339.1892
763.4778 | 579.4778 | 484.3899 | 358.5034 | 299.238 | 350.921 | 309.032 | 339.4199
764.4793 | 580.4793 | 484.335 | 358.6624 | 299.6357 | 351.0748 | 309.1864 | 339.9393
765.4807 | 581.4807 | 484.1386 | 358.9893 | 299.9882 | 350.9123 | 308.8559 | 340.0406
766.4821 | 582.4821 | 484.0375 | 359.4511 | 300.3558 | 351.1619 | 309.3765 | 340.2037
767.4736 | 583.4736 | 483.8351 | 359.7636 | 300.7268 | 351.3983 | 309.4235 | 340.632
768.475 | 584.475 | 483.8697 | 359.9631 | 301.0889 | 351.5293 | 309.7482 | 341.0171
769.4765 | 585.4765 | 483.8478 | 360.2635 | 301.4588 | 351.6673 | 310.3666 | 341.2052
770.4779 | 586.4779 | 483.8204 | 360.4946 | 301.8303 | 351.9941 | 310.3635 | 341.3622
771.4793 | 587.4793 | 483.8695 | 360.6757 | 302.2014 | 352.3612 | 310.4699 | 341.5199
772.4808 | 588.4808 | 483.8825 | 360.9635 | 302.5861 | 352.6473 | 310.3947 | 341.8415
773.4722 | 589.4722 | 483.9471 | 361.1791 | 302.9673 | 352.9322 | 309.4813 | 342.027
774.4736 | 590.4736 | 484.0257 | 361.628 | 303.3303 | 353.2427 | 309.7307 | 342.3058
775.4751 | 591.4751 | 484.031 | 361.8479 | 303.7003 | 353.495 | 310.3245 | 342.4677
776.4765 | 592.4765 | 483.8834 | 362.061 | 304.0677 | 353.812 | 310.1907 | 342.7161
777.478 | 593.478 | 483.8366 | 362.2847 | 304.4458 | 353.9209 | 310.1936 | 342.8807
778.4794 | 594.4794 | 483.7569 | 362.4952 | 304.8103 | 354.2457 | 309.3954 | 343.2062
779.4708 | 595.4708 | 483.6221 | 362.614 | 305.182 | 354.4864 | 309.4001 | 343.3602
780.4823 | 596.4823 | 483.3737 | 362.8856 | 305.5536 | 354.7231 | 309.7166 | 343.5706
781.4737 | 597.4737 | 483.1271 | 363.0156 | 305.9264 | 355.0017 | 309.5377 | 343.9487
782.4751 | 598.4751 | 482.9971 | 363.3068 | 306.2957 | 355.3047 | 309.1169 | 344.4394
783.4766 | 599.4766 | 483.1865 | 363.4509 | 306.6682 | 355.6043 | 308.3217 | 344.5227
784.478 | 600.478 | 483.3177 | 363.6068 | 307.0554 | 355.873 | 308.6319 | 344.7738
785.4795 | 601.4795 | 483.1812 | 363.759 | 307.4406 | 356.1112 | 308.5908 | 344.9053
786.4809 | 602.4809 | 482.9873 | 363.8253 | 307.8284 | 356.2131 | 309.1511 | 345.105
787.4823 | 603.4823 | 482.7905 | 364.1377 | 308.1893 | 356.2252 | 308.967 | 345.178
788.4738 | 604.4738 | 482.7481 | 364.491 | 308.5814 | 356.5249 | 309.48 | 345.4113
789.4752 | 605.4752 | 482.6886 | 364.618 | 308.9822 | 356.837 | 310.1556 | 345.8416
790.4766 | 606.4766 | 482.6344 | 364.5904 | 309.3582 | 357.0798 | 310.6591 | 346.0983
791.4781 | 607.4781 | 482.479 | 364.7829 | 309.7422 | 357.3869 | 310.4706 | 346.3702
792.4795 | 608.4795 | 482.2772 | 364.9362 | 310.1205 | 357.7971 | 310.22 | 346.8012
793.481 | 609.481 | 482.267 | 365.1399 | 310.5006 | 358.1136 | 309.8981 | 346.9913
794.4724 | 610.4724 | 482.3438 | 365.3981 | 310.8476 | 358.4005 | 310.2974 | 346.9905
795.4738 | 611.4738 | 482.4108 | 365.3372 | 311.2332 | 358.7512 | 310.1279 | 347.359
796.4753 | 612.4753 | 482.3169 | 365.6076 | 311.6122 | 358.998 | 310.2557 | 347.8164
797.4767 | 613.4767 | 482.2967 | 365.7954 | 311.9798 | 359.2368 | 310.0256 | 348.4794
798.4782 | 614.4782 | 482.2726 | 366.0461 | 312.3393 | 359.4312 | 309.4875 | 348.5245
799.4796 | 615.4796 | 482.3411 | 366.3406 | 312.711 | 359.6306 | 309.4634 | 348.4047
800.471 | 616.471 | 482.5056 | 366.2081 | 313.0779 | 359.8908 | 308.7089 | 348.6539
801.4725 | 617.4725 | 482.709 | 366.6163 | 313.4338 | 359.96 | 308.4841 | 349.0581
802.4739 | 618.4739 | 482.7774 | 366.9647 | 313.8025 | 360.2329 | 308.2526 | 349.5164
803.4753 | 619.4753 | 482.878 | 366.7939 | 314.1747 | 360.4225 | 308.3956 | 349.9353
804.4768 | 620.4768 | 482.9776 | 367.0876 | 314.5314 | 360.7829 | 308.7683 | 350.1282
805.4782 | 621.4782 | 482.9889 | 367.5026 | 314.8918 | 361.0755 | 308.4587 | 350.3672
806.4797 | 622.4797 | 483.094 | 367.7571 | 315.2756 | 361.2941 | 308.8414 | 350.3552
807.4811 | 623.4811 | 483.1485 | 368.0622 | 315.6391 | 361.59 | 308.6091 | 350.5471
808.4825 | 624.4825 | 483.2858 | 368.2764 | 315.996 | 361.7065 | 308.2845 | 350.704
809.474 | 625.474 | 483.3248 | 368.3896 | 316.3464 | 361.8717 | 308.413 | 350.9744
810.4754 | 626.4754 | 483.3197 | 368.7322 | 316.6969 | 362.1572 | 308.2811 | 351.0593
811.4768 | 627.4768 | 483.4392 | 368.9448 | 317.0685 | 362.4007 | 308.1122 | 351.1105
812.4783 | 628.4783 | 483.4045 | 369.084 | 317.4561 | 362.6499 | 308.4951 | 351.5133
813.4797 | 629.4797 | 483.4635 | 369.3144 | 317.7988 | 362.8926 | 308.61 | 351.5712
814.4812 | 630.4812 | 483.595 | 369.5228 | 318.1552 | 363.1183 | 308.736 | 351.9975
815.4726 | 631.4726 | 483.6613 | 369.8501 | 318.5021 | 363.3776 | 308.9585 | 352.395
816.474 | 632.474 | 483.7335 | 369.9519 | 318.847 | 363.6779 | 308.9607 | 352.2288
817.4755 | 633.4755 | 483.854 | 370.2638 | 319.2136 | 363.9211 | 309.4522 | 352.2198
818.4769 | 634.4769 | 483.9793 | 370.5196 | 319.5679 | 364.0393 | 310.1415 | 352.276
819.4784 | 635.4784 | 484.0581 | 370.642 | 319.9097 | 364.3045 | 310.6117 | 352.9393
820.4798 | 636.4798 | 484.0511 | 370.9276 | 320.2527 | 364.4837 | 311.192 | 352.7501
821.4712 | 637.4712 | 484.0985 | 370.9761 | 320.5957 | 364.6899 | 311.126 | 352.9687
822.4727 | 638.4727 | 484.1844 | 371.1874 | 320.9523 | 364.9524 | 311.4547 | 353.379
823.4741 | 639.4741 | 484.2477 | 371.4494 | 321.289 | 365.247 | 312.0764 | 353.6478
824.4755 | 640.4755 | 484.2295 | 371.5511 | 321.6339 | 365.5048 | 312.6635 | 353.4497
825.477 | 641.477 | 484.2602 | 371.7094 | 322.0035 | 365.8025 | 312.7371 | 353.6782
826.4784 | 642.4784 | 484.3304 | 371.926 | 322.3439 | 366.0772 | 313.0972 | 353.9357
827.4799 | 643.4799 | 484.3515 | 372.1363 | 322.6894 | 366.3592 | 313.1452 | 353.919
828.4813 | 644.4813 | 484.2403 | 372.3706 | 323.0448 | 366.6565 | 313.6138 | 353.9983
829.4827 | 645.4827 | 484.2009 | 372.6355 | 323.3743 | 366.6916 | 314.0211 | 354.0051
830.4742 | 646.4742 | 484.0824 | 372.8664 | 323.7294 | 366.9832 | 314.276 | 354.2133
831.4756 | 647.4756 | 484.067 | 373.1032 | 324.0631 | 367.2573 | 314.496 | 354.4467
832.477 | 648.477 | 484.1165 | 373.3044 | 324.3952 | 367.4991 | 314.6574 | 354.8438
833.4785 | 649.4785 | 484.0078 | 373.5412 | 324.7375 | 367.748 | 314.8942 | 355.1729
834.4799 | 650.4799 | 483.8984 | 373.7975 | 325.0701 | 368.0125 | 314.2701 | 354.9001
835.4814 | 651.4814 | 483.8162 | 373.9585 | 325.4077 | 368.3499 | 313.481 | 355.2235
836.4728 | 652.4728 | 483.7474 | 374.2397 | 325.7588 | 368.6373 | 313.1596 | 355.387
837.4742 | 653.4742 | 483.6371 | 374.4056 | 326.0909 | 368.9912 | 312.9885 | 355.9029
838.4757 | 654.4757 | 483.5415 | 374.6767 | 326.4281 | 369.2627 | 312.301 | 356.198
839.4771 | 655.4771 | 483.3537 | 374.8541 | 326.7765 | 369.4945 | 312.3956 | 356.3381
840.4785 | 656.4785 | 483.1809 | 375.1061 | 327.1058 | 369.6914 | 311.5989 | 356.4395
841.48 | 657.48 | 483.0975 | 375.3319 | 327.4405 | 369.8448 | 312.2566 | 356.7294
842.4814 | 658.4814 | 483.0432 | 375.6313 | 327.776 | 369.9849 | 312.3123 | 356.5381
843.4729 | 659.4729 | 482.9656 | 375.7442 | 328.0988 | 370.2041 | 312.9896 | 356.718
844.4743 | 660.4743 | 482.9066 | 375.9691 | 328.428 | 370.4336 | 312.761 | 357.1036
845.4757 | 661.4757 | 483.0258 | 376.1522 | 328.746 | 370.4633 | 312.9179 | 357.2009
846.4772 | 662.4772 | 483.0297 | 376.3236 | 329.0623 | 370.6643 | 312.7257 | 357.1471
847.4786 | 663.4786 | 482.9976 | 376.5821 | 329.3792 | 370.9068 | 312.7411 | 357.3542
848.4801 | 664.4801 | 483.1026 | 376.7798 | 329.7196 | 371.132 | 313.3356 | 357.3138
849.4815 | 665.4815 | 483.1362 | 376.944 | 330.0634 | 371.3502 | 313.2653 | 357.3193
850.4829 | 666.4829 | 483.2385 | 377.1725 | 330.4139 | 371.575 | 314.0565 | 357.4238
851.4744 | 667.4744 | 483.3479 | 377.3796 | 330.7694 | 371.722 | 313.934 | 357.3495
852.4758 | 668.4758 | 483.2951 | 377.6336 | 331.0894 | 371.9283 | 314.5013 | 357.5066
853.4772 | 669.4772 | 483.1678 | 378.0405 | 331.4098 | 372.1056 | 314.6078 | 357.5128
854.4787 | 670.4787 | 483.1808 | 378.3961 | 331.744 | 372.3454 | 314.7188 | 357.6973
855.4801 | 671.4801 | 483.0461 | 378.5653 | 332.0583 | 372.5979 | 315.3993 | 357.9807
856.4816 | 672.4816 | 482.9759 | 378.9347 | 332.3776 | 372.8297 | 315.2502 | 357.8568
857.473 | 673.473 | 482.9083 | 379.1025 | 332.6954 | 373.036 | 315.212 | 357.8653
858.4744 | 674.4744 | 482.7644 | 379.3884 | 333.0095 | 373.2594 | 315.3246 | 358.2096
859.4759 | 675.4759 | 482.7631 | 379.7353 | 333.3371 | 373.4476 | 315.8465 | 358.3009
860.4773 | 676.4773 | 482.7457 | 380.1071 | 333.6589 | 373.659 | 315.317 | 358.2653
861.4787 | 677.4787 | 482.6861 | 380.339 | 333.9748 | 373.8099 | 315.0673 | 358.5504
862.4802 | 678.4802 | 482.7476 | 380.547 | 334.2939 | 374.0075 | 314.8375 | 358.6922
863.4816 | 679.4816 | 482.8763 | 380.7753 | 334.6085 | 374.2271 | 314.8788 | 358.9936
864.4731 | 680.4731 | 482.8415 | 381.1266 | 334.9224 | 374.4547 | 314.1019 | 359.0496
865.4745 | 681.4745 | 482.7972 | 381.361 | 335.2645 | 374.6538 | 313.792 | 359.2099
866.4759 | 682.4759 | 482.7998 | 381.6034 | 335.5872 | 374.9156 | 314.1127 | 359.1151
867.4774 | 683.4774 | 482.777 | 381.7916 | 335.9181 | 375.0067 | 314.3697 | 359.3371
868.4788 | 684.4788 | 482.8927 | 382.0367 | 336.2332 | 375.2813 | 314.2541 | 359.354
869.4803 | 685.4803 | 482.9956 | 382.0596 | 336.5534 | 375.6507 | 313.8167 | 359.5005
870.5418 | 686.5418 | 482.855 | 382.439 | 336.8793 | 376.0369 | 314.0219 | 359.8111
871.4831 | 687.4831 | 482.8203 | 382.5743 | 337.1748 | 376.3369 | 314.4106 | 359.7452
872.4746 | 688.4746 | 482.7685 | 382.748 | 337.4937 | 376.5667 | 314.7139 | 360.3305
873.476 | 689.476 | 482.7021 | 383.0475 | 337.828 | 376.7918 | 314.6082 | 360.3327
874.4774 | 690.4774 | 482.7256 | 383.2375 | 338.1494 | 377.0322 | 314.2979 | 360.3545
875.4789 | 691.4789 | 482.7855 | 383.4256 | 338.4558 | 377.2555 | 313.936 | 360.4708
876.4803 | 692.4803 | 482.7062 | 383.6151 | 338.782 | 377.5001 | 313.285 | 360.602
877.4818 | 693.4818 | 482.8211 | 383.7762 | 339.1194 | 377.7154 | 312.5791 | 360.6382
878.4732 | 694.4732 | 482.8827 | 383.9549 | 339.4425 | 377.8909 | 312.7329 | 360.717
879.4746 | 695.4746 | 482.8168 | 384.1639 | 339.7456 | 378.1469 | 313.1633 | 361.102
880.4761 | 696.4761 | 482.9084 | 384.3294 | 340.0575 | 378.3452 | 313.3433 | 361.4492
881.4775 | 697.4775 | 482.9598 | 384.4963 | 340.365 | 378.6354 | 313.3137 | 361.5553
882.4789 | 698.4789 | 483.0312 | 384.7049 | 340.6867 | 378.952 | 313.0185 | 361.7596
883.4804 | 699.4804 | 483.0611 | 384.9261 | 340.9864 | 379.1966 | 312.6721 | 362.0663
884.4718 | 700.4718 | 483.2674 | 385.037 | 341.3211 | 379.5276 | 313.0905 | 361.971
885.4732 | 701.4732 | 483.3708 | 385.13 | 341.6239 | 379.7664 | 313.1601 | 362.12
886.4747 | 702.4747 | 483.1386 | 385.3918 | 341.9174 | 379.9746 | 313.0742 | 362.2073
887.4761 | 703.4761 | 483.0436 | 385.5768 | 342.252 | 380.2723 | 312.9752 | 362.1777
888.4776 | 704.4776 | 482.9187 | 385.702 | 342.5709 | 380.4686 | 312.45 | 362.2297
889.479 | 705.479 | 482.7506 | 385.8161 | 342.8751 | 380.7165 | 312.9393 | 362.3694
890.4804 | 706.4804 | 482.6421 | 386.0745 | 343.1842 | 380.9922 | 313.1396 | 362.4458
891.4819 | 707.4819 | 482.6057 | 386.0872 | 343.4661 | 381.2343 | 312.8678 | 362.6703
892.4733 | 708.4733 | 482.3979 | 386.2894 | 343.7783 | 381.5306 | 313.79 | 362.8746
893.4748 | 709.4748 | 482.3022 | 386.4322 | 344.0851 | 381.7105 | 313.5508 | 362.9857
894.4862 | 710.4862 | 482.2603 | 386.6531 | 344.3851 | 381.9051 | 313.7039 | 362.9467
895.4776 | 711.4776 | 482.2744 | 386.8213 | 344.6876 | 382.1199 | 313.1983 | 363.2233
896.4791 | 712.4791 | 482.0699 | 386.9401 | 344.997 | 382.2885 | 313.8051 | 363.6175
897.4805 | 713.4805 | 482.1523 | 387.1886 | 345.3155 | 382.5225 | 313.1666 | 363.8687
898.482 | 714.482 | 482.4982 | 387.2464 | 345.6183 | 382.7218 | 312.2729 | 363.8529
899.4734 | 715.4734 | 482.6274 | 387.482 | 345.9158 | 382.9606 | 311.6733 | 363.8348
900.4748 | 716.4748 | 482.6115 | 387.5591 | 346.2364 | 383.2091 | 311.1126 | 364.0699
901.4763 | 717.4763 | 482.5333 | 387.8532 | 346.5541 | 383.4416 | 310.5685 | 364.5166
902.4777 | 718.4777 | 482.7225 | 388.0033 | 346.8563 | 383.6516 | 310.0432 | 364.5983
903.4791 | 719.4791 | 482.8872 | 388.0761 | 347.1533 | 383.9143 | 309.7711 | 364.7112
904.4806 | 720.4806 | 482.9817 | 388.321 | 347.4705 | 384.1485 | 309.2606 | 364.7781
905.472 | 721.472 | 482.8896 | 388.5156 | 347.7777 | 384.3725 | 309.2614 | 364.6583
906.4734 | 722.4734 | 482.8113 | 388.6994 | 348.0635 | 384.616 | 309.7879 | 364.6497
907.4749 | 723.4749 | 482.8425 | 388.8321 | 348.3697 | 384.8522 | 309.2647 | 364.9671
908.4763 | 724.4763 | 482.971 | 388.9506 | 348.6559 | 385.0268 | 308.7285 | 365.169
909.4778 | 725.4778 | 483.0658 | 389.1745 | 348.9519 | 385.2304 | 308.2172 | 365.2794
910.4792 | 726.4792 | 483.0302 | 389.4183 | 349.2489 | 385.4443 | 307.1082 | 365.3196
911.4806 | 727.4806 | 482.8901 | 389.4563 | 349.5458 | 385.4568 | 306.4213 | 365.3618
912.4821 | 728.4821 | 482.7535 | 389.5468 | 349.8327 | 385.7154 | 305.6376 | 365.3052
913.4735 | 729.4735 | 482.6221 | 389.7121 | 350.1301 | 385.8759 | 305.1549 | 365.6383
914.475 | 730.475 | 482.4966 | 389.8217 | 350.4285 | 386.0912 | 305.3792 | 365.7055
915.4764 | 731.4764 | 482.331 | 390.0067 | 350.7212 | 386.309 | 305.4041 | 365.7062
916.4778 | 732.4778 | 482.2053 | 390.1704 | 351.0115 | 386.5215 | 305.3153 | 365.8201
917.4793 | 733.4793 | 482.1696 | 390.3288 | 351.3032 | 386.7397 | 305.7202 | 365.9607
918.4807 | 734.4807 | 482.1149 | 390.3917 | 351.5918 | 386.9466 | 305.607 | 366.0315
919.4822 | 735.4822 | 481.942 | 390.443 | 351.8917 | 387.1551 | 305.5699 | 366.3499
920.4736 | 736.4736 | 481.7688 | 390.5985 | 352.1699 | 387.3787 | 306.5757 | 366.7894
921.475 | 737.475 | 481.7711 | 390.6797 | 352.4808 | 387.5626 | 307.3938 | 366.7533
922.4765 | 738.4765 | 481.7953 | 390.8474 | 352.7715 | 387.7601 | 308.1202 | 366.7092
923.4779 | 739.4779 | 481.8194 | 390.9995 | 353.0648 | 387.9338 | 309.0245 | 367.0019
924.4793 | 740.4793 | 481.9885 | 391.1098 | 353.3408 | 388.1549 | 309.4252 | 366.8375
925.4708 | 741.4708 | 482.3145 | 391.2986 | 353.6315 | 388.3627 | 309.6714 | 366.7753
926.4722 | 742.4722 | 482.6773 | 391.4544 | 353.9307 | 388.5829 | 310.2647 | 366.8892
927.4736 | 743.4736 | 482.9433 | 391.613 | 354.2097 | 388.7453 | 311.1048 | 366.621
928.4751 | 744.4751 | 483.0799 | 391.7776 | 354.4992 | 388.9464 | 311.8923 | 366.5031
929.4765 | 745.4765 | 483.0163 | 391.8972 | 354.7972 | 389.1184 | 312.7672 | 366.2629
930.478 | 746.478 | 482.8218 | 391.9562 | 355.0904 | 389.2782 | 312.8865 | 366.1724
931.4794 | 747.4794 | 482.6539 | 392.1371 | 355.3702 | 389.4262 | 312.8156 | 365.8855
932.4708 | 748.4708 | 482.6801 | 392.2618 | 355.6428 | 389.5679 | 312.6286 | 365.9528
933.4823 | 749.4823 | 482.7052 | 392.4446 | 355.9106 | 389.7022 | 312.6261 | 365.8871
934.4737 | 750.4737 | 482.6961 | 392.5414 | 356.2197 | 389.8575 | 311.879 | 365.9166
935.4751 | 751.4751 | 482.6972 | 392.7502 | 356.5175 | 390.0259 | 311.7297 | 365.7703
936.4766 | 752.4766 | 482.727 | 392.8559 | 356.8021 | 390.22 | 311.2121 | 365.8245
937.478 | 753.478 | 482.7899 | 393.0378 | 357.1009 | 390.4012 | 310.8994 | 365.6108
938.4795 | 754.4795 | 482.7924 | 393.1489 | 357.3884 | 390.597 | 310.4784 | 365.6081
939.4809 | 755.4809 | 482.8356 | 393.3103 | 357.6935 | 390.7963 | 310.3817 | 365.3634
940.4823 | 756.4823 | 482.9004 | 393.5046 | 357.994 | 390.9794 | 310.3179 | 365.454
941.4738 | 757.4738 | 482.8637 | 393.5945 | 358.2933 | 391.1771 | 309.9214 | 365.1742
942.4752 | 758.4752 | 482.8095 | 393.7355 | 358.5761 | 391.3952 | 309.391 | 364.7886
943.4767 | 759.4767 | 482.8417 | 393.9245 | 358.88 | 391.5521 | 309.7292 | 364.4966
944.4781 | 760.4781 | 483.0398 | 393.9455 | 359.1752 | 391.6827 | 310.0593 | 364.5075
945.4795 | 761.4795 | 483.1147 | 394.0823 | 359.4701 | 391.8352 | 309.5353 | 364.4389
946.481 | 762.481 | 483.1411 | 394.3142 | 359.7753 | 391.9853 | 309.4904 | 364.1942
947.4724 | 763.4724 | 483.0433 | 394.5027 | 360.0702 | 392.1475 | 309.3321 | 364.072
948.4738 | 764.4738 | 483.1133 | 394.7104 | 360.3588 | 392.2981 | 308.2894 | 363.8587
949.4753 | 765.4753 | 483.082 | 394.8459 | 360.6653 | 392.4597 | 308.132 | 364.0635
950.4767 | 766.4767 | 483.1648 | 395.0579 | 360.9671 | 392.6141 | 308.5587 | 364.1424
951.4782 | 767.4782 | 483.1338 | 395.1796 | 361.2456 | 392.7921 | 308.9061 | 364.2608
952.4796 | 768.4796 | 483.0888 | 395.3355 | 361.5448 | 392.9709 | 308.3327 | 364.008
953.481 | 769.481 | 483.137 | 395.4271 | 361.8433 | 393.125 | 308.4493 | 363.9999
954.4825 | 770.4825 | 483.0736 | 395.612 | 362.1263 | 393.3193 | 308.5831 | 363.981
955.4739 | 771.4739 | 483.045 | 395.7912 | 362.4296 | 393.4747 | 308.5832 | 364.104
956.4753 | 772.4753 | 483.0437 | 395.9849 | 362.7086 | 393.6635 | 308.682 | 364.2382
957.4768 | 773.4768 | 483.0736 | 396.1293 | 363.0043 | 393.851 | 307.7393 | 364.2917
958.4782 | 774.4782 | 483.1026 | 396.1586 | 363.2992 | 394.0557 | 307.237 | 363.8096
959.4797 | 775.4797 | 483.2927 | 396.24 | 363.5973 | 394.2608 | 306.5921 | 363.0563
960.4811 | 776.4811 | 483.438 | 396.3441 | 363.9143 | 394.475 | 306.2252 | 362.6684
961.4825 | 777.4825 | 483.4918 | 396.4378 | 364.2159 | 394.6601 | 306.5141 | 362.5528
962.474 | 778.474 | 483.5237 | 396.5569 | 364.5135 | 394.8406 | 306.1967 | 362.7061
963.4754 | 779.4754 | 483.5354 | 396.664 | 364.8131 | 394.9963 | 306.4214 | 362.7404
964.4768 | 780.4768 | 483.5365 | 396.7582 | 365.1246 | 395.1646 | 306.4964 | 362.9473
965.4783 | 781.4783 | 483.5734 | 396.7775 | 365.4337 | 395.3472 | 306.5335 | 363.1321
966.4797 | 782.4797 | 483.4841 | 396.8949 | 365.7441 | 395.5407 | 306.9484 | 363.1656
967.4812 | 783.4812 | 483.3825 | 396.9667 | 366.0452 | 395.7161 | 306.9892 | 363.3112
968.4726 | 784.4726 | 483.3473 | 397.0798 | 366.3482 | 395.8892 | 306.7572 | 363.322
969.474 | 785.474 | 483.4363 | 397.1759 | 366.6585 | 396.06 | 306.4709 | 363.5363
970.4755 | 786.4755 | 483.4153 | 397.2547 | 366.9683 | 396.2372 | 306.5381 | 363.5764
971.4769 | 787.4769 | 483.3756 | 397.364 | 367.2698 | 396.3924 | 307.1064 | 363.6235
972.4784 | 788.4784 | 483.4672 | 397.4492 | 367.5775 | 396.5555 | 307.8576 | 363.6392
973.4798 | 789.4798 | 483.6282 | 397.6155 | 367.8861 | 396.7219 | 308.3966 | 363.7327
974.4712 | 790.4712 | 483.6263 | 397.7188 | 368.182 | 396.8815 | 308.1295 | 363.7613
975.4727 | 791.4727 | 483.6939 | 397.7812 | 368.463 | 397.0202 | 307.8544 | 363.7407
976.4741 | 792.4741 | 483.728 | 397.8562 | 368.7237 | 397.1755 | 307.9902 | 363.8281
977.4755 | 793.4755 | 483.6348 | 397.9225 | 368.9876 | 397.3139 | 308.3762 | 363.8005
978.477 | 794.477 | 483.7161 | 398.086 | 369.2555 | 397.4479 | 308.9438 | 363.7372
979.4784 | 795.4784 | 483.7781 | 398.242 | 369.5382 | 397.5874 | 309.5151 | 363.7724
980.4799 | 796.4799 | 483.7803 | 398.3976 | 369.8024 | 397.727 | 309.762 | 363.7303
981.4813 | 797.4813 | 483.8389 | 398.5076 | 370.0702 | 397.8664 | 310.1713 | 363.7429
982.4827 | 798.4827 | 483.8791 | 398.6232 | 370.3476 | 397.995 | 310.1518 | 363.9716
983.4742 | 799.4742 | 483.7391 | 398.7591 | 370.5949 | 398.1346 | 310.6084 | 363.9292
984.4756 | 800.4756 | 483.6071 | 398.8817 | 370.8509 | 398.2819 | 310.2447 | 363.9648
985.477 | 801.477 | 483.4165 | 399.0161 | 371.1568 | 398.4061 | 310.5067 | 363.9829
986.4785 | 802.4785 | 483.1874 | 399.1576 | 371.4109 | 398.5464 | 310.3435 | 363.94
987.4799 | 803.4799 | 483.0211 | 399.299 | 371.6714 | 398.686 | 310.2493 | 363.8801
988.4814 | 804.4814 | 482.9581 | 399.4156 | 371.9326 | 398.8465 | 310.3321 | 363.8753
989.4728 | 805.4728 | 482.8886 | 399.5165 | 372.1775 | 399.0189 | 310.1251 | 363.9793
990.4742 | 806.4742 | 482.7675 | 399.6114 | 372.407 | 399.1796 | 309.3847 | 364.1245
991.4757 | 807.4757 | 482.9439 | 399.7071 | 372.6427 | 399.3578 | 309.1797 | 364.1819
992.4771 | 808.4771 | 483.0837 | 399.8273 | 372.8561 | 399.5832 | 309.4385 | 364.3707
993.4786 | 809.4786 | 483.2173 | 400.0333 | 373.0645 | 400.056 | 308.5863 | 364.7232
994.48 | 810.48 | 483.4327 | 400.0983 | 373.2903 | 400.8187 | 309.2422 | 365.1577
995.4814 | 811.4814 | 483.4143 | 400.2801 | 373.4552 | 401.8454 | 309.0884 | 365.6755
996.4829 | 812.4829 | 483.4904 | 400.5716 | 373.6114 | 403.1461 | 309.561 | 366.2486
997.4743 | 813.4743 | 483.6155 | 400.8682 | 373.7656 | 404.6928 | 309.4795 | 367.6876
998.4757 | 814.4757 | 483.6274 | 401.1841 | 373.8603 | 406.4436 | 310.1724 | 368.5687
999.4772 | 815.4772 | 483.7679 | 401.848 | 373.9496 | 408.36 | 310.8288 | 369.817
1000.4786 | 816.4786 | 483.9922 | 403.1255 | 373.9881 | 410.3642 | 312.3269 | 373.3506
1001.4801 | 817.4801 | 484.3037 | 404.6299 | 374.0411 | 412.4586 | 312.771 | 377.7352
1002.4815 | 818.4815 | 484.5055 | 406.4446 | 374.1237 | 414.7483 | 313.266 | 381.6466
1003.4829 | 819.4829 | 484.6347 | 408.3908 | 374.2017 | 417.0946 | 313.8873 | 386.3088
1004.4744 | 820.4744 | 484.655 | 410.3925 | 374.333 | 419.5007 | 314.5116 | 390.9791
1005.4758 | 821.4758 | 484.8368 | 412.3215 | 374.564 | 421.9259 | 315.8345 | 395.4485
1006.4772 | 822.4772 | 484.8238 | 414.2115 | 374.7384 | 424.5173 | 315.8892 | 399.908
1007.4787 | 823.4787 | 484.7639 | 416.053 | 374.8054 | 427.2014 | 316.7794 | 405.0424
1008.4801 | 824.4801 | 484.7675 | 417.8324 | 374.863 | 430.008 | 317.6558 | 409.4147
1009.4715 | 825.4715 | 484.8308 | 419.5823 | 374.9591 | 432.7628 | 318.7802 | 413.3532
1010.473 | 826.473 | 484.8525 | 421.1501 | 375.0704 | 435.4759 | 319.9459 | 416.7356
1011.4744 | 827.4744 | 484.8621 | 422.654 | 375.0382 | 438.1063 | 320.5202 | 422.1308
1012.4759 | 828.4759 | 484.7307 | 424.1043 | 375.1551 | 440.7821 | 320.9922 | 426.0329
1013.4773 | 829.4773 | 484.699 | 425.4594 | 375.3805 | 444.5128 | 321.8497 | 430.7598
1014.4787 | 830.4787 | 484.6925 | 426.8651 | 375.4453 | 448.6243 | 322.8864 | 435.1064
1015.4802 | 831.4802 | 484.5632 | 428.3126 | 375.4604 | 452.6899 | 323.8693 | 440.291
1016.4716 | 832.4716 | 484.4614 | 429.7246 | 375.474 | 456.6681 | 325.3056 | 444.2457
1017.4731 | 833.4731 | 484.2895 | 431.1287 | 375.4474 | 460.6016 | 326.9912 | 445.0021
1018.4745 | 834.4745 | 484.2016 | 432.6285 | 375.2018 | 464.6384 | 328.072 | 449.2229
1019.4759 | 835.4759 | 484.1462 | 434.1547 | 374.9445 | 468.4587 | 328.818 | 453.1928
1020.4774 | 836.4774 | 484.014 | 435.6254 | 374.6633 | 471.9131 | 329.9857 | 455.0594
1021.5089 | 837.5089 | 483.8779 | 437.1432 | 374.4309 | 475.5938 | 331.5129 | 458.206
1022.4803 | 838.4803 | 483.8302 | 438.5701 | 374.2034 | 478.9928 | 332.6754 | 461.5232
1023.4817 | 839.4817 | 483.7499 | 440.0334 | 374.0412 | 482.2247 | 334.5064 | 464.7407
1024.4831 | 840.4831 | 483.6776 | 441.4561 | 373.8519 | 485.2936 | 335.9978 | 467.1267
1025.4746 | 841.4746 | 483.6391 | 442.8706 | 373.7373 | 488.2146 | 337.3479 | 468.5763
1026.476 | 842.476 | 483.4395 | 444.251 | 373.5215 | 490.7884 | 338.277 | 470.1142
1027.4774 | 843.4774 | 483.3487 | 445.619 | 373.4016 | 493.2419 | 339.4528 | 469.4992
1028.4789 | 844.4789 | 483.2321 | 446.9227 | 373.4441 | 495.5987 | 341.2031 | 468.7611
1029.4803 | 845.4803 | 483.2012 | 448.2001 | 373.4717 | 497.905 | 342.5504 | 467.1174
1030.4818 | 846.4818 | 483.1734 | 449.5263 | 373.5146 | 499.9728 | 344.8056 | 467.0972
1031.4732 | 847.4732 | 483.0091 | 450.8345 | 373.548 | 501.7993 | 346.6508 | 467.4145
1032.4746 | 848.4746 | 482.748 | 452.0978 | 373.5724 | 503.5346 | 348.4079 | 470.3296
1033.4761 | 849.4761 | 482.5165 | 453.3441 | 373.5628 | 505.016 | 349.4643 | 472.7521
1034.4775 | 850.4775 | 482.3418 | 454.5539 | 373.5662 | 506.6398 | 351.0658 | 474.4383
1035.4789 | 851.4789 | 482.0119 | 455.7408 | 373.5359 | 508.1336 | 352.6325 | 475.3824
1036.4804 | 852.4804 | 481.7008 | 456.8973 | 373.5546 | 509.6744 | 353.527 | 475.77
1037.4718 | 853.4718 | 481.52 | 458.018 | 373.5998 | 510.9789 | 354.2548 | 475.7803
1038.4733 | 854.4733 | 481.1897 | 459.1213 | 373.6785 | 512.1879 | 355.1469 | 475.8036
1039.4747 | 855.4747 | 480.8333 | 460.1755 | 373.7336 | 513.2407 | 355.3521 | 475.2013
1040.4761 | 856.4761 | 480.5016 | 461.1679 | 373.7858 | 514.1727 | 355.7589 | 473.4235
1041.4776 | 857.4776 | 480.1751 | 462.1214 | 373.8353 | 514.4106 | 355.8757 | 472.8854
1042.479 | 858.479 | 480.0397 | 463.0767 | 373.8279 | 515.2656 | 356.0711 | 472.8002
1043.4805 | 859.4805 | 479.8821 | 464.0742 | 373.8558 | 515.9156 | 356.4491 | 472.7456
1044.4819 | 860.4819 | 479.5546 | 464.9263 | 373.9133 | 516.4932 | 357.2588 | 472.7608
1045.4733 | 861.4733 | 479.3235 | 465.6765 | 374.013 | 517.0962 | 358.1399 | 471.9043
1046.4748 | 862.4748 | 478.986 | 466.3989 | 374.0965 | 518.2511 | 359.182 | 470.7607
1047.4762 | 863.4762 | 478.5425 | 467.0907 | 374.2258 | 519.0673 | 359.5875 | 470.6783
1048.4776 | 864.4776 | 477.9945 | 467.7387 | 374.3287 | 520.3479 | 360.6571 | 470.2022
1049.4791 | 865.4791 | 477.5714 | 468.3677 | 374.4569 | 521.0078 | 361.1048 | 470.1225
1050.5206 | 866.5206 | 477.0899 | 469.1003 | 374.6027 | 521.5264 | 361.449 | 470.5084
1051.482 | 867.482 | 476.5362 | 469.8065 | 374.7291 | 521.8875 | 361.7538 | 471.1426
1052.4734 | 868.4734 | 476.033 | 470.4498 | 374.8826 | 522.8806 | 362.6964 | 472.1507
1053.4748 | 869.4748 | 475.4234 | 471.1111 | 375.087 | 523.4322 | 362.8035 | 472.4096
1054.4763 | 870.4763 | 474.8152 | 471.7649 | 375.2478 | 524.1174 | 363.0022 | 472.077
1055.4777 | 871.4777 | 474.3284 | 472.4413 | 375.4145 | 525.051 | 363.7233 | 472.2781
1056.4791 | 872.4791 | 473.8046 | 473.1667 | 375.6141 | 525.7545 | 363.4277 | 472.5676
1057.4706 | 873.4706 | 473.1533 | 473.9152 | 375.7952 | 526.909 | 363.3228 | 473.1795
1058.472 | 874.472 | 472.6747 | 474.7203 | 376.0236 | 527.5743 | 363.2173 | 474.7049
1059.4734 | 875.4734 | 472.1492 | 475.5099 | 376.2276 | 528.7951 | 362.4437 | 476.3013
1060.4749 | 876.4749 | 471.5067 | 476.2794 | 376.4261 | 530.1111 | 362.857 | 479.1315
1061.4763 | 877.4763 | 470.9106 | 477.0992 | 376.6696 | 531.4607 | 363.175 | 481.19
1062.4778 | 878.4778 | 470.4183 | 477.8892 | 376.846 | 532.9931 | 363.4396 | 482.6236
1063.4792 | 879.4792 | 469.9024 | 478.7403 | 377.0494 | 534.6766 | 363.425 | 484.1416
1064.4806 | 880.4806 | 469.319 | 479.556 | 377.1336 | 536.2841 | 363.9242 | 485.9479
1065.4821 | 881.4821 | 468.7047 | 480.3662 | 377.3981 | 538.3208 | 363.6902 | 487.6131
1066.4735 | 882.4735 | 468.084 | 481.2199 | 377.6182 | 540.1348 | 363.8811 | 489.4185
1067.475 | 883.475 | 467.3988 | 482.0463 | 377.8936 | 541.8515 | 364.6634 | 491.042
1068.4764 | 884.4764 | 466.8269 | 482.7485 | 378.149 | 543.3016 | 365.0959 | 492.7451
1069.4778 | 885.4778 | 466.3897 | 483.5021 | 378.3889 | 544.6919 | 365.0327 | 494.4916
1070.4793 | 886.4793 | 465.793 | 484.1393 | 378.6417 | 546.2337 | 364.3507 | 495.8516
1071.4807 | 887.4807 | 465.1824 | 484.7909 | 378.9013 | 547.6373 | 364.4352 | 498.1319
1072.4822 | 888.4822 | 464.5622 | 485.4791 | 379.1539 | 548.9373 | 364.2875 | 499.255
1073.4736 | 889.4736 | 463.9055 | 486.0834 | 379.4189 | 550.1328 | 363.615 | 500.5422
1074.475 | 890.475 | 463.3338 | 486.6731 | 379.6808 | 551.4058 | 363.091 | 502.0102
1075.4765 | 891.4765 | 462.743 | 487.2544 | 379.9554 | 552.7468 | 363.244 | 503.7522
1076.4779 | 892.4779 | 462.0832 | 487.7722 | 380.2696 | 553.9683 | 363.2453 | 505.2303
1077.4793 | 893.4793 | 461.5569 | 488.2149 | 380.5565 | 555.0477 | 362.3711 | 505.8427
1078.4808 | 894.4808 | 461.094 | 488.8643 | 380.8492 | 556.1182 | 361.968 | 506.337
1079.4722 | 895.4722 | 460.5288 | 489.6056 | 381.1175 | 557.133 | 361.7586 | 507.9938
1080.4736 | 896.4736 | 459.9191 | 490.227 | 381.3871 | 558.0183 | 361.1988 | 509.2161
1081.4751 | 897.4751 | 459.3673 | 490.7949 | 381.6983 | 558.8672 | 360.8117 | 510.3033
1082.4765 | 898.4765 | 458.7898 | 491.2957 | 381.9975 | 559.8687 | 359.5651 | 511.4309
1083.478 | 899.478 | 458.2241 | 491.8156 | 382.3093 | 560.6511 | 358.5226 | 512.1127
1084.4794 | 900.4794 | 457.6106 | 492.1642 | 382.6495 | 561.3438 | 357.9503 | 513.0669
1085.4808 | 901.4808 | 457.0642 | 492.7103 | 383.0219 | 562.142 | 357.7841 | 513.9611
1086.4823 | 902.4823 | 456.5417 | 493.1814 | 383.3757 | 563.2281 | 357.0648 | 514.023
1087.4737 | 903.4737 | 456.0806 | 493.5672 | 383.728 | 564.1513 | 355.8557 | 514.5471
1088.4752 | 904.4752 | 455.5658 | 493.8903 | 384.0561 | 565.1146 | 355.664 | 515.2819
1089.4766 | 905.4766 | 455.027 | 494.3411 | 384.3956 | 565.9977 | 354.6634 | 515.7415
1090.478 | 906.478 | 454.4819 | 494.7125 | 384.7464 | 566.8683 | 354.0026 | 515.5046
1091.4795 | 907.4795 | 454.1253 | 495.0406 | 385.1369 | 567.6506 | 353.6097 | 515.7327
1092.4809 | 908.4809 | 453.7161 | 495.3733 | 385.5382 | 568.2957 | 353.2217 | 516.4937
1093.4824 | 909.4824 | 453.2253 | 495.6106 | 385.9479 | 568.9978 | 352.8373 | 517.094
1094.4738 | 910.4738 | 452.6264 | 495.9226 | 386.3013 | 569.7855 | 352.6419 | 517.8326
1095.4752 | 911.4752 | 451.9157 | 496.3019 | 386.7089 | 570.5223 | 352.5198 | 518.2206
1096.4767 | 912.4767 | 451.364 | 496.8556 | 387.1121 | 570.9697 | 351.3775 | 518.4514
1097.4781 | 913.4781 | 450.8147 | 497.1519 | 387.5407 | 571.5047 | 350.8853 | 519.0274
1098.4795 | 914.4795 | 450.2582 | 497.4179 | 387.9674 | 572.0358 | 350.5031 | 519.6904
1099.471 | 915.471 | 449.5924 | 497.6744 | 388.4016 | 572.515 | 350.0686 | 519.9432
1100.4724 | 916.4724 | 448.9756 | 497.682 | 388.8037 | 573.2908 | 349.214 | 520.4285
1101.4738 | 917.4738 | 448.3851 | 497.812 | 389.2421 | 574.191 | 349.1381 | 520.5974
1102.4753 | 918.4753 | 447.8309 | 498.0518 | 389.6437 | 574.7416 | 348.5727 | 520.4556
1103.4767 | 919.4767 | 447.3042 | 498.4745 | 390.0689 | 575.5088 | 347.6169 | 520.8418
1104.4782 | 920.4782 | 446.7856 | 498.8447 | 390.5043 | 576.3811 | 346.8699 | 521.262
1105.4796 | 921.4796 | 446.208 | 499.1568 | 390.9233 | 577.1163 | 346.5303 | 521.2738
1106.481 | 922.481 | 445.6397 | 499.545 | 391.3981 | 577.6656 | 345.2482 | 521.5768
1107.4825 | 923.4825 | 445.0989 | 499.6558 | 391.8555 | 578.1977 | 344.8844 | 521.778
1108.4739 | 924.4739 | 444.4977 | 500.053 | 392.3378 | 578.8114 | 345.0214 | 521.8011
1109.4753 | 925.4753 | 443.864 | 500.2561 | 392.7471 | 579.4201 | 344.4144 | 522.301
1110.4768 | 926.4768 | 443.3182 | 500.4532 | 393.179 | 580.077 | 344.0171 | 523.2514
1111.4782 | 927.4782 | 442.7758 | 500.6218 | 393.6512 | 580.475 | 343.2593 | 523.5981
1112.4797 | 928.4797 | 442.3141 | 500.6492 | 394.1027 | 581.0016 | 342.4027 | 523.9504
1113.4811 | 929.4811 | 441.7278 | 500.5094 | 394.6586 | 581.2996 | 341.869 | 524.3804
1114.4725 | 930.4725 | 441.1316 | 501.0699 | 395.1307 | 581.3475 | 341.7569 | 524.7798
1115.474 | 931.474 | 440.6317 | 501.562 | 395.6254 | 581.6454 | 342.0101 | 525.3157
1116.4754 | 932.4754 | 440.178 | 501.9841 | 396.1466 | 581.99 | 341.3281 | 525.8015
1117.4769 | 933.4769 | 439.8357 | 502.2006 | 396.68 | 581.9633 | 340.971 | 526.3928
1118.4783 | 934.4783 | 439.3436 | 502.7867 | 397.2379 | 581.9111 | 341.3351 | 526.8602
1119.4797 | 935.4797 | 438.8317 | 503.4741 | 397.8484 | 581.8923 | 341.4488 | 527.5891
1120.4812 | 936.4812 | 438.2362 | 504.0442 | 398.4974 | 582.1774 | 341.2578 | 527.9218
1121.4726 | 937.4726 | 437.5475 | 503.4647 | 399.1938 | 582.426 | 340.7298 | 528.5755
1122.474 | 938.474 | 436.7818 | 502.7974 | 399.9102 | 582.6633 | 340.3729 | 529.38
1123.4755 | 939.4755 | 436.1469 | 503.1197 | 400.6689 | 583.1006 | 339.6559 | 529.976
1124.4769 | 940.4769 | 435.5586 | 503.6135 | 401.5158 | 583.5269 | 338.8681 | 530.3093
1125.4784 | 941.4784 | 434.9885 | 504.1769 | 402.4204 | 583.378 | 337.4184 | 530.9794
1126.4798 | 942.4798 | 434.4911 | 504.7713 | 403.4501 | 583.1186 | 336.5804 | 532.292
1127.4812 | 943.4812 | 434.0167 | 505.5861 | 404.4777 | 582.8463 | 336.1239 | 532.8941
1128.4827 | 944.4827 | 433.6085 | 506.2258 | 405.4959 | 582.3784 | 335.6748 | 533.4381
1129.4741 | 945.4741 | 433.0745 | 506.7497 | 406.6758 | 582.0793 | 335.2125 | 534.4959
1130.4755 | 946.4755 | 432.5971 | 507.2204 | 407.8394 | 581.8928 | 335.1177 | 535.5401
1131.477 | 947.477 | 432.2529 | 507.7319 | 409.11 | 581.9384 | 334.8141 | 536.4881
1132.4784 | 948.4784 | 431.9028 | 508.1959 | 410.2928 | 582.2554 | 333.7273 | 537.1871
1133.4799 | 949.4799 | 431.3088 | 508.6393 | 411.5274 | 582.589 | 333.2648 | 538.0472
1134.4813 | 950.4813 | 430.7183 | 509.0553 | 412.7316 | 583.0678 | 332.7581 | 539.0776
1135.4727 | 951.4727 | 430.1699 | 509.4823 | 414.0647 | 583.7533 | 332.4311 | 539.5758
1136.4742 | 952.4742 | 429.6593 | 509.8635 | 415.3747 | 584.1877 | 331.9112 | 539.9278
1137.4756 | 953.4756 | 429.1997 | 510.2744 | 416.592 | 584.5031 | 330.9146 | 540.7575
1138.477 | 954.477 | 428.7276 | 510.686 | 417.8379 | 585.0279 | 330.1242 | 541.3625
1139.4785 | 955.4785 | 428.299 | 510.9798 | 419.1006 | 585.5057 | 329.3458 | 541.7994
1140.4799 | 956.4799 | 427.7517 | 511.1331 | 420.1402 | 585.9148 | 329.2482 | 542.4745
1141.4714 | 957.4714 | 427.1358 | 511.4031 | 421.1846 | 586.5505 | 328.5854 | 543.1478
1142.4728 | 958.4728 | 426.5356 | 511.8213 | 422.3093 | 587.0608 | 328.7807 | 543.8523
1143.4742 | 959.4742 | 425.982 | 512.2828 | 423.3563 | 587.53 | 328.6247 | 544.3786
1144.4757 | 960.4757 | 425.4259 | 512.6289 | 424.517 | 587.9728 | 328.5495 | 545.3287
1145.4771 | 961.4771 | 424.9886 | 513.1278 | 425.6351 | 588.0255 | 328.6976 | 546.128
1146.4786 | 962.4786 | 424.4217 | 513.6344 | 426.7605 | 587.9393 | 328.1159 | 546.9434
1147.48 | 963.48 | 423.9828 | 513.9781 | 427.8479 | 588.2202 | 328.4385 | 547.4944
1148.4814 | 964.4814 | 423.5831 | 514.4689 | 428.8428 | 588.2829 | 328.0339 | 548.1788
1149.4829 | 965.4829 | 423.1849 | 513.1314 | 429.8856 | 587.8875 | 327.859 | 548.7795
1150.4743 | 966.4743 | 422.7558 | 512.4578 | 430.8571 | 588.164 | 328.1999 | 549.5398
1151.4757 | 967.4757 | 422.2307 | 511.2833 | 431.9023 | 588.353 | 328.4592 | 550.2049
1152.4772 | 968.4772 | 421.7174 | 510.0507 | 432.9128 | 588.6716 | 328.1396 | 550.6905
1153.4786 | 969.4786 | 421.1856 | 509.2729 | 433.8897 | 588.9308 | 328.5187 | 551.2988
1154.4801 | 970.4801 | 420.6216 | 509.031 | 434.8086 | 589.1493 | 328.2619 | 551.9716
1155.4815 | 971.4815 | 420.1495 | 508.7252 | 435.8193 | 589.2927 | 328.3126 | 552.7193
1156.4729 | 972.4729 | 419.6411 | 508.178 | 436.7296 | 589.3671 | 328.7767 | 553.5841
1157.4744 | 973.4744 | 419.0803 | 507.897 | 437.5865 | 589.5806 | 328.701 | 553.9534
1158.4758 | 974.4758 | 418.5902 | 507.566 | 438.4252 | 589.9896 | 329.2142 | 554.1426
1159.4772 | 975.4772 | 418.2715 | 507.2433 | 439.2952 | 590.1625 | 329.0802 | 554.7524
1160.4787 | 976.4787 | 417.9123 | 507.34 | 440.1735 | 590.5715 | 329.0638 | 555.0178
1161.4801 | 977.4801 | 417.5016 | 507.6132 | 441.0494 | 590.9152 | 329.215 | 555.6676
1162.4816 | 978.4816 | 417.1771 | 507.285 | 441.8876 | 590.9086 | 329.4621 | 556.1578
1163.473 | 979.473 | 416.7621 | 507.1452 | 442.7714 | 591.3264 | 329.322 | 556.7323
1164.4744 | 980.4744 | 416.276 | 507.6934 | 443.5976 | 591.7325 | 329.3133 | 557.0178
1165.4759 | 981.4759 | 415.9079 | 507.4971 | 444.5082 | 591.9105 | 329.2016 | 557.6249
1166.4773 | 982.4773 | 415.4606 | 507.6419 | 445.3363 | 592.3218 | 328.8838 | 557.9691
1167.4788 | 983.4788 | 415.098 | 508.0334 | 446.195 | 592.7372 | 329.1931 | 558.1952
1168.4802 | 984.4802 | 414.7092 | 508.0994 | 446.954 | 593.4442 | 328.9804 | 558.654
1169.4716 | 985.4716 | 414.4281 | 508.4928 | 447.8077 | 593.811 | 329.0907 | 558.629
1170.5632 | 986.5632 | 413.9724 | 508.4641 | 448.5921 | 594.2092 | 329.5354 | 559.123
1171.4745 | 987.4745 | 413.5027 | 508.4627 | 449.3297 | 594.5183 | 329.4303 | 559.4917
1172.4759 | 988.4759 | 413.2273 | 509.1242 | 450.0724 | 594.899 | 329.2756 | 559.9405
1173.4774 | 989.4774 | 412.9271 | 509.8568 | 450.693 | 595.3086 | 329.9465 | 560.4054
1174.4788 | 990.4788 | 412.5108 | 510.3066 | 451.4553 | 595.4483 | 329.527 | 561.2104
1175.4803 | 991.4803 | 412.1725 | 510.6454 | 452.252 | 595.5616 | 329.6531 | 561.5879
1176.4817 | 992.4817 | 411.8671 | 511.0929 | 453.1988 | 595.7161 | 329.7892 | 562.4988
1177.4731 | 993.4731 | 411.6007 | 511.5333 | 454.1477 | 596.2356 | 330.4361 | 563.389
1178.4746 | 994.4746 | 411.2581 | 511.7695 | 455.2173 | 596.7785 | 330.4295 | 563.8381
1179.476 | 995.476 | 410.7892 | 512.4958 | 456.3886 | 597.4642 | 330.4002 | 564.4523
1180.4774 | 996.4774 | 410.2844 | 513.5851 | 458.0541 | 597.8444 | 330.7711 | 564.7222
1181.4789 | 997.4789 | 409.9485 | 514.777 | 460.3885 | 597.9213 | 330.5539 | 565.2369
1182.4803 | 998.4803 | 409.5953 | 515.8307 | 463.5312 | 596.9574 | 331.1544 | 565.6538
1183.4717 | 999.4717 | 409.1603 | 516.7936 | 467.8464 | 595.7805 | 331.2968 | 566.2657
1184.4732 | 1000.4732 | 408.8212 | 517.7725 | 471.2481 | 595.2532 | 331.2506 | 566.83
1185.4746 | 1001.4746 | 408.4901 | 518.7534 | 473.7101 | 595.5104 | 331.5755 | 567.4649
1186.4761 | 1002.4761 | 408.0872 | 519.6476 | 476.4381 | 596.0447 | 331.7498 | 567.9777
1187.4775 | 1003.4775 | 407.7469 | 520.51 | 479.0646 | 596.3263 | 331.7043 | 568.4768
1188.4789 | 1004.4789 | 407.4972 | 521.4414 | 481.1186 | 595.8427 | 331.5649 | 568.8822
1189.4804 | 1005.4804 | 407.173 | 522.3527 | 483.1568 | 595.3288 | 331.7816 | 569.4067
1190.4718 | 1006.4718 | 406.7474 | 523.3103 | 485.1292 | 594.7843 | 332.2876 | 569.8639
1191.4733 | 1007.4733 | 406.3553 | 524.2687 | 486.469 | 594.6116 | 332.8632 | 570.3189
1192.4747 | 1008.4747 | 406.0233 | 525.2513 | 487.8589 | 593.9949 | 332.5203 | 570.9786
1193.4761 | 1009.4761 | 405.6736 | 526.152 | 489.1305 | 593.1911 | 333.0929 | 571.5334
1194.4776 | 1010.4776 | 405.1214 | 527.093 | 490.2211 | 592.777 | 332.6562 | 571.25
1195.479 | 1011.479 | 404.5889 | 528.0581 | 491.2455 | 592.5042 | 332.1626 | 571.9928
1196.4805 | 1012.4805 | 404.1424 | 529.0723 | 492.3415 | 592.6023 | 331.47 | 572.2881
1197.4819 | 1013.4819 | 403.6857 | 530.0233 | 493.4308 | 592.9013 | 331.3015 | 572.4517
1198.4733 | 1014.4733 | 403.2138 | 530.9414 | 494.2877 | 593.3103 | 331.0909 | 573.1227
1199.4748 | 1015.4748 | 402.8443 | 531.8478 | 495.0705 | 593.6146 | 330.6089 | 573.5039
1200.4762 | 1016.4762 | 402.5439 | 532.7642 | 495.8031 | 594.1355 | 330.1844 | 573.866
1201.4776 | 1017.4776 | 402.1485 | 533.6816 | 496.5872 | 594.5955 | 329.6683 | 574.193
1202.4791 | 1018.4791 | 401.827 | 534.5165 | 497.3862 | 595.07 | 329.4825 | 574.9428
1203.4805 | 1019.4805 | 401.5653 | 535.3556 | 498.2441 | 595.5607 | 329.0355 | 575.2932
1204.482 | 1020.482 | 401.1439 | 536.3 | 498.9787 | 596.1156 | 328.3925 | 575.8057
1205.4734 | 1021.4734 | 400.7172 | 537.1792 | 499.5948 | 596.5809 | 327.796 | 576.2782
1206.4748 | 1022.4748 | 400.3087 | 538.1231 | 500.1803 | 596.7111 | 327.8628 | 577.184
1207.4763 | 1023.4763 | 400.1917 | 538.9984 | 500.8625 | 596.7197 | 328.1081 | 578.1144
1208.4777 | 1024.4777 | 400.0679 | 539.8629 | 501.6166 | 596.5633 | 328.4223 | 578.454
1209.4791 | 1025.4791 | 399.9046 | 540.7404 | 502.4008 | 596.6345 | 328.6782 | 578.979
1210.4706 | 1026.4706 | 399.5638 | 541.5253 | 503.1312 | 596.8802 | 329.1651 | 579.072
1211.472 | 1027.472 | 399.19 | 542.2688 | 503.8186 | 597.1585 | 329.4107 | 579.3891
1212.4735 | 1028.4735 | 398.8272 | 542.9963 | 504.5612 | 597.3625 | 329.5347 | 579.855
1213.4749 | 1029.4749 | 398.4803 | 543.7134 | 505.2554 | 597.5208 | 330.3765 | 579.9703
1214.4763 | 1030.4763 | 398.1729 | 544.397 | 506.1246 | 597.8016 | 330.3816 | 580.3721
1215.4778 | 1031.4778 | 397.8771 | 545.0373 | 506.8731 | 598.1965 | 330.2771 | 580.6855
1216.4792 | 1032.4792 | 397.5354 | 545.6739 | 507.5093 | 598.5444 | 330.1269 | 580.7984
1217.4807 | 1033.4807 | 397.1964 | 546.292 | 508.2108 | 599.185 | 329.9024 | 581.1323
1218.4821 | 1034.4821 | 396.9636 | 546.936 | 508.9385 | 599.5014 | 329.4841 | 581.2643
1219.4735 | 1035.4735 | 396.6882 | 547.5435 | 509.7375 | 599.4812 | 329.7728 | 581.4938
1220.475 | 1036.475 | 396.2567 | 548.1314 | 510.501 | 599.5532 | 329.5207 | 581.9727
1221.4764 | 1037.4764 | 395.8042 | 548.7468 | 511.2785 | 599.5306 | 329.6016 | 582.1034
1222.4778 | 1038.4778 | 395.405 | 549.363 | 512.0032 | 599.474 | 328.4953 | 582.1193
1223.4793 | 1039.4793 | 394.9984 | 549.9258 | 512.8169 | 599.1899 | 328 | 582.8693
1224.4807 | 1040.4807 | 394.481 | 550.5344 | 513.5744 | 598.9372 | 327.1846 | 583.339
1225.4822 | 1041.4822 | 394.0817 | 551.0527 | 514.3453 | 598.7204 | 325.6585 | 583.1271
1226.4736 | 1042.4736 | 393.6373 | 551.5279 | 515.1145 | 598.8836 | 324.3994 | 583.4099
1227.475 | 1043.475 | 393.1703 | 552.0937 | 515.9379 | 599.1576 | 323.2723 | 583.8046
1228.4765 | 1044.4765 | 392.6265 | 552.6643 | 516.7142 | 599.211 | 322.2492 | 584.0616
1229.4779 | 1045.4779 | 392.0928 | 553.3532 | 517.4751 | 599.3601 | 321.2548 | 584.5162
1230.4793 | 1046.4793 | 391.659 | 553.9974 | 518.2168 | 599.3857 | 320.2948 | 585.1231
1231.4708 | 1047.4708 | 391.2452 | 554.6536 | 518.9566 | 599.3148 | 319.5736 | 585.3108
1232.4722 | 1048.4722 | 390.7845 | 555.2229 | 519.6926 | 599.2034 | 319.0482 | 585.293
1233.4736 | 1049.4736 | 390.3463 | 555.8229 | 520.465 | 598.9867 | 318.0975 | 585.5539
1234.4751 | 1050.4751 | 389.9012 | 556.4233 | 521.1472 | 598.6412 | 316.9507 | 585.5413
1235.4765 | 1051.4765 | 389.5459 | 556.9732 | 521.9601 | 598.3994 | 315.6521 | 585.7417
1236.478 | 1052.478 | 389.2315 | 557.5942 | 522.7175 | 598.2656 | 314.787 | 586.5002
1237.4794 | 1053.4794 | 388.9417 | 558.2274 | 523.4371 | 598.3281 | 314.3648 | 586.9214
1238.4808 | 1054.4808 | 388.4484 | 558.9643 | 524.0786 | 598.252 | 314.3932 | 587.9129
1239.4823 | 1055.4823 | 387.9864 | 559.6598 | 524.7138 | 597.9627 | 313.9004 | 588.2744
1240.4737 | 1056.4737 | 387.6273 | 560.3098 | 525.3525 | 597.9572 | 313.6736 | 588.728
1241.4752 | 1057.4752 | 387.1753 | 560.9218 | 525.9573 | 597.8959 | 313.0333 | 589.2014
1242.4766 | 1058.4766 | 386.7016 | 561.5439 | 526.6126 | 597.9596 | 312.832 | 589.3257
1243.478 | 1059.478 | 386.2747 | 562.0797 | 527.2517 | 598.1867 | 312.7049 | 589.1589
1244.4795 | 1060.4795 | 385.8461 | 562.4646 | 527.9193 | 598.1784 | 312.9565 | 589.1954
1245.4809 | 1061.4809 | 385.4008 | 562.7422 | 528.5754 | 597.9383 | 312.579 | 588.9399
1246.4824 | 1062.4824 | 384.8851 | 562.9403 | 529.1824 | 597.9254 | 312.2394 | 588.5632
1247.4738 | 1063.4738 | 384.4843 | 563.0836 | 529.8606 | 597.5043 | 311.2229 | 588.5745
1248.4752 | 1064.4752 | 384.0055 | 563.1663 | 530.4853 | 597.1015 | 310.7421 | 588.9409
1249.4767 | 1065.4767 | 383.5115 | 563.2401 | 531.1104 | 596.8224 | 310.3258 | 589.4172
1250.4781 | 1066.4781 | 383.0276 | 563.3958 | 531.738 | 596.2151 | 309.4734 | 589.6431
1251.4795 | 1067.4795 | 382.5884 | 563.6847 | 532.3732 | 595.7191 | 309.1169 | 589.6101
1252.471 | 1068.471 | 382.1671 | 564.0286 | 532.9977 | 594.9774 | 308.337 | 590.0258
1253.4724 | 1069.4724 | 381.6978 | 564.3774 | 533.6322 | 594.3668 | 307.4727 | 589.8196
1254.4839 | 1070.4839 | 381.168 | 564.7902 | 534.4079 | 593.4379 | 306.9112 | 589.5315
1255.4753 | 1071.4753 | 380.7113 | 565.2515 | 535.0592 | 592.4051 | 306.4009 | 589.2001
1256.4767 | 1072.4767 | 380.2573 | 565.6237 | 535.6814 | 591.0903 | 305.7312 | 589.2591
1257.4782 | 1073.4782 | 379.8434 | 566.0267 | 536.3266 | 589.8604 | 305.6974 | 589.5782
1258.4796 | 1074.4796 | 379.3393 | 566.5013 | 537.0056 | 588.7676 | 305.0073 | 589.9049
1259.481 | 1075.481 | 378.9029 | 567.004 | 537.5976 | 587.608 | 304.0433 | 589.7878
1260.4725 | 1076.4725 | 378.4216 | 567.5721 | 538.1867 | 586.5811 | 302.837 | 589.9269
1261.4739 | 1077.4739 | 377.9529 | 568.1695 | 538.8406 | 585.8042 | 302.0959 | 590.8088
1262.4754 | 1078.4754 | 377.5672 | 568.7061 | 539.4062 | 585.1187 | 301.7926 | 591.4732
1263.4768 | 1079.4768 | 377.2028 | 569.1682 | 540.0058 | 584.4788 | 301.4217 | 592.3678
1264.4782 | 1080.4782 | 376.8901 | 569.5863 | 540.5919 | 583.8262 | 300.6641 | 592.4531
1265.4797 | 1081.4797 | 376.4216 | 569.9746 | 541.1369 | 583.1315 | 299.7682 | 592.0061
1266.4811 | 1082.4811 | 375.8858 | 570.3908 | 541.6926 | 582.4125 | 298.8322 | 591.6858
1267.4725 | 1083.4725 | 375.406 | 570.7844 | 542.2299 | 581.7583 | 297.8144 | 591.6644
1268.474 | 1084.474 | 375.11 | 571.1432 | 542.8254 | 581.316 | 297.2584 | 591.6784
1269.4754 | 1085.4754 | 374.7399 | 571.5498 | 543.4293 | 580.8867 | 296.2329 | 591.5509
1270.4769 | 1086.4769 | 374.2988 | 571.9652 | 544.1283 | 580.4849 | 295.4459 | 591.5414
1271.4783 | 1087.4783 | 373.8183 | 572.4082 | 544.7483 | 580.4652 | 294.7709 | 591.6236
1272.4797 | 1088.4797 | 373.3875 | 572.8292 | 545.3577 | 580.5196 | 294.0654 | 591.9564
1273.4712 | 1089.4712 | 372.9711 | 573.2674 | 545.9573 | 581.3147 | 293.4112 | 592.0908
1274.4726 | 1090.4726 | 372.5838 | 573.6901 | 546.6189 | 582.0894 | 292.8313 | 591.7899
1275.474 | 1091.474 | 372.1791 | 574.0882 | 547.1989 | 582.4809 | 292.8662 | 591.6356
1276.4755 | 1092.4755 | 371.8335 | 574.6105 | 547.8675 | 582.7536 | 292.3348 | 592.0364
1277.4769 | 1093.4769 | 371.4112 | 575.2305 | 548.5639 | 583.1283 | 292.3523 | 592.1989
1278.4784 | 1094.4784 | 370.9712 | 575.8487 | 549.089 | 583.2431 | 291.9248 | 591.982
1279.4798 | 1095.4798 | 370.5675 | 576.4875 | 549.646 | 583.3862 | 291.3304 | 592.2766
1280.4812 | 1096.4812 | 370.1101 | 577.2137 | 550.3527 | 583.476 | 290.8842 | 592.7358
1281.4827 | 1097.4827 | 369.7558 | 577.9219 | 550.9625 | 583.4417 | 290.3882 | 593.6376
1282.4741 | 1098.4741 | 369.3582 | 578.5683 | 551.6295 | 583.2643 | 290.1877 | 594.0581
1283.4755 | 1099.4755 | 368.9126 | 579.1804 | 552.2147 | 583.1461 | 290.002 | 594.0823
1284.477 | 1100.477 | 368.5555 | 579.805 | 552.8828 | 583.3095 | 289.5414 | 594.7858
1285.4784 | 1101.4784 | 368.1792 | 580.3786 | 553.4694 | 583.4047 | 288.7214 | 594.9741
1286.4799 | 1102.4799 | 367.7681 | 580.9439 | 554.0715 | 583.5752 | 288.5227 | 595.1329
1287.4813 | 1103.4813 | 367.2823 | 581.5601 | 554.746 | 583.6234 | 287.5523 | 595.8157
1288.4727 | 1104.4727 | 366.8967 | 582.1623 | 555.3117 | 583.8133 | 287.1545 | 596.1598
1289.4742 | 1105.4742 | 366.5335 | 582.7659 | 555.9176 | 583.8813 | 286.7649 | 596.0947
1290.4756 | 1106.4756 | 366.219 | 583.331 | 556.4544 | 584.0843 | 286.5113 | 595.9217
1291.4771 | 1107.4771 | 365.6972 | 583.8719 | 557.2228 | 584.4299 | 285.9732 | 595.7328
1292.4785 | 1108.4785 | 365.1072 | 584.3042 | 557.9837 | 584.8242 | 285.5035 | 595.4886
1293.4799 | 1109.4799 | 364.6005 | 584.7315 | 558.5754 | 585.1759 | 285.0569 | 595.0691
1294.4814 | 1110.4814 | 364.0927 | 585.1301 | 559.1152 | 585.315 | 284.5579 | 594.8223
1295.4728 | 1111.4728 | 363.6655 | 585.5569 | 559.7025 | 585.6245 | 283.8903 | 594.8445
1296.4742 | 1112.4742 | 363.2373 | 585.9287 | 560.3258 | 585.8402 | 283.7724 | 594.8631
1297.4757 | 1113.4757 | 362.781 | 586.3173 | 560.9849 | 585.8801 | 282.9153 | 594.558
1298.4771 | 1114.4771 | 362.4198 | 586.7314 | 561.594 | 586.3017 | 282.1333 | 594.3747
1299.4786 | 1115.4786 | 361.9775 | 587.2137 | 562.1632 | 586.747 | 281.4591 | 594.7274
1300.48 | 1116.48 | 361.5211 | 587.694 | 562.7411 | 587.0342 | 281.3827 | 594.7655
1301.4814 | 1117.4814 | 361.0587 | 588.2138 | 563.347 | 587.6924 | 280.5946 | 594.8173
1302.4829 | 1118.4829 | 360.6519 | 588.7068 | 563.8077 | 587.9622 | 280.1423 | 594.9888
1303.4743 | 1119.4743 | 360.1654 | 589.2128 | 564.4224 | 588.1447 | 279.3754 | 594.5748
1304.4757 | 1120.4757 | 359.6981 | 589.6849 | 565.059 | 588.445 | 279.0617 | 594.6309
1305.4772 | 1121.4772 | 359.2903 | 590.1317 | 565.6513 | 588.668 | 278.3542 | 594.162
1306.4786 | 1122.4786 | 358.8903 | 590.5349 | 566.2953 | 588.896 | 278.1162 | 593.5779
1307.4801 | 1123.4801 | 358.5656 | 590.9961 | 567.0589 | 589.1587 | 277.524 | 593.0178
1308.4715 | 1124.4715 | 358.234 | 591.4457 | 567.753 | 589.4818 | 277.4722 | 592.6878
1309.4729 | 1125.4729 | 357.8227 | 591.8129 | 568.271 | 589.4829 | 277.0244 | 592.4073
1310.4744 | 1126.4744 | 357.3488 | 592.1116 | 568.8193 | 589.9949 | 276.3919 | 591.9225
1311.4758 | 1127.4758 | 356.9105 | 592.4729 | 569.5078 | 590.0057 | 275.7558 | 591.4725
1312.4772 | 1128.4772 | 356.4542 | 592.8722 | 570.2071 | 590.3632 | 275.2345 | 591.4001
1313.4787 | 1129.4787 | 355.9821 | 593.4411 | 570.8531 | 590.6289 | 274.0317 | 591.3417
1314.4801 | 1130.4801 | 355.482 | 594.0282 | 571.6129 | 590.8982 | 273.1439 | 590.7529
1315.4716 | 1131.4716 | 355.0196 | 594.5991 | 572.2561 | 591.0412 | 271.9258 | 590.3827
1316.473 | 1132.473 | 354.5185 | 595.146 | 572.8705 | 591.1669 | 270.8466 | 590.4006
1317.4744 | 1133.4744 | 354.0578 | 595.7194 | 573.4587 | 591.5677 | 269.9696 | 589.9031
1318.4759 | 1134.4759 | 353.6099 | 596.263 | 574.0744 | 592.2633 | 269.4902 | 589.5208
1319.4773 | 1135.4773 | 353.1582 | 596.9088 | 574.7358 | 593.0808 | 269.2924 | 589.5075
1320.4788 | 1136.4788 | 352.7766 | 597.5225 | 575.2898 | 593.5811 | 269.0813 | 589.113
1321.4802 | 1137.4802 | 352.4455 | 598.0754 | 575.9269 | 594.0059 | 268.9057 | 589.4039
1322.4816 | 1138.4816 | 352.1419 | 598.6121 | 576.5747 | 594.7547 | 268.4598 | 589.9456
1323.4731 | 1139.4731 | 351.7145 | 599.1565 | 577.1213 | 595.2812 | 267.8151 | 590.0234
1324.4745 | 1140.4745 | 351.4034 | 599.6405 | 577.6891 | 595.5294 | 267.3947 | 589.063
1325.4759 | 1141.4759 | 350.9522 | 600.1036 | 578.264 | 595.8824 | 266.9769 | 588.6651
1326.4774 | 1142.4774 | 350.5963 | 600.563 | 578.7701 | 596.6573 | 266.222 | 588.3603
1327.4788 | 1143.4788 | 350.2052 | 601.0142 | 579.3105 | 597.0499 | 265.2358 | 587.6218
1328.4803 | 1144.4803 | 349.8096 | 601.4544 | 579.8869 | 597.5446 | 264.517 | 587.2303
1329.4817 | 1145.4817 | 349.5121 | 601.8962 | 580.4179 | 598.1519 | 264.5988 | 587.4238
1330.4731 | 1146.4731 | 349.2421 | 602.3772 | 580.9913 | 599.9023 | 264.6547 | 587.9651
1331.4746 | 1147.4746 | 348.8677 | 602.9239 | 581.575 | 601.7446 | 264.1017 | 587.8418
1332.476 | 1148.476 | 348.3889 | 603.4192 | 582.1006 | 602.3659 | 263.7887 | 587.1326
1333.4774 | 1149.4774 | 347.9028 | 603.9203 | 582.7128 | 602.8846 | 263.0221 | 587.1496
1334.4789 | 1150.4789 | 347.4504 | 604.3574 | 583.2545 | 603.3673 | 262.1194 | 586.3841
1335.4803 | 1151.4803 | 347.0851 | 604.7546 | 583.7659 | 603.7403 | 262.0513 | 585.7769
1336.4718 | 1152.4718 | 346.6589 | 605.2196 | 584.2945 | 604.1433 | 262.6696 | 585.3483
1337.4732 | 1153.4732 | 346.0914 | 605.6551 | 584.8829 | 604.8503 | 262.0854 | 584.8373
1338.4746 | 1154.4746 | 345.622 | 606.021 | 585.3569 | 604.9276 | 262.0603 | 584.4594
1339.4761 | 1155.4761 | 345.2038 | 606.491 | 585.9458 | 605.3678 | 261.4453 | 584.4333
1340.4775 | 1156.4775 | 344.8403 | 606.9584 | 586.4814 | 605.693 | 261.0649 | 583.4211
1341.479 | 1157.479 | 344.5048 | 607.4339 | 587.0413 | 605.64 | 260.5846 | 582.7402
1342.4804 | 1158.4804 | 344.0981 | 607.908 | 587.5777 | 605.3724 | 259.8791 | 582.3325
1343.4818 | 1159.4818 | 343.9227 | 608.4088 | 588.125 | 605.3511 | 259.2454 | 582.5343
1344.4733 | 1160.4733 | 343.6141 | 608.9763 | 588.6688 | 606.2161 | 258.9741 | 582.4363
1345.4747 | 1161.4747 | 343.1214 | 609.4943 | 589.2432 | 607.0138 | 258.3848 | 581.6307
1346.4761 | 1162.4761 | 342.6576 | 610.0531 | 589.828 | 607.4771 | 257.954 | 580.573
1347.4776 | 1163.4776 | 342.1816 | 610.6226 | 590.3943 | 607.5445 | 257.6025 | 579.8347
1348.479 | 1164.479 | 341.7745 | 611.2467 | 590.9161 | 607.7477 | 257.2429 | 578.8282
1349.4805 | 1165.4805 | 341.545 | 611.8416 | 591.4717 | 608.1474 | 257.0698 | 578.3888
1350.4919 | 1166.4919 | 341.2483 | 612.4141 | 592.0028 | 608.2958 | 257.2005 | 578.4522
1351.4733 | 1167.4733 | 340.9206 | 612.9756 | 592.5087 | 608.2064 | 256.8707 | 578.2938
1352.4748 | 1168.4748 | 340.5933 | 613.5339 | 593.0385 | 608.3903 | 256.8832 | 577.7448
1353.4762 | 1169.4762 | 340.2176 | 614.1071 | 593.5149 | 608.2062 | 256.5764 | 577.3826
1354.4776 | 1170.4776 | 339.8166 | 614.73 | 594.0036 | 608.3537 | 256.1857 | 577.0735
1355.4791 | 1171.4791 | 339.3994 | 615.3537 | 594.5038 | 608.6044 | 255.7798 | 576.5104
1356.4805 | 1172.4805 | 338.9378 | 615.936 | 594.9979 | 609.2305 | 255.3115 | 575.8684
1357.4719 | 1173.4719 | 338.4788 | 616.4285 | 595.4524 | 609.1516 | 254.8781 | 575.2242
1358.4734 | 1174.4734 | 338.0244 | 616.8919 | 595.9556 | 608.8406 | 254.6897 | 575.2318
1359.4748 | 1175.4748 | 337.581 | 617.3881 | 596.4517 | 608.8057 | 253.8772 | 574.4584
1360.4763 | 1176.4763 | 337.1726 | 617.9381 | 596.92 | 608.941 | 253.3285 | 573.7597
1361.4777 | 1177.4777 | 336.8174 | 618.5273 | 597.4269 | 608.8834 | 253.1019 | 573.6069
1362.4791 | 1178.4791 | 336.4304 | 619.0785 | 597.958 | 608.876 | 252.4607 | 573.3219
1363.4806 | 1179.4806 | 335.9129 | 619.6679 | 598.5086 | 608.8744 | 251.8568 | 572.8655
1364.472 | 1180.472 | 335.5095 | 620.257 | 599.0423 | 608.8696 | 251.1915 | 572.3803
1365.4735 | 1181.4735 | 335.111 | 620.838 | 599.5788 | 609.022 | 250.712 | 572.3308
1366.4749 | 1182.4749 | 334.815 | 621.4444 | 600.0871 | 609.1707 | 250.009 | 571.8753
1367.4763 | 1183.4763 | 334.4575 | 622.1221 | 600.5851 | 609.5768 | 249.876 | 571.4168
1368.4778 | 1184.4778 | 334.1184 | 622.8287 | 601.0847 | 610.0109 | 249.6827 | 571.2476
1369.4792 | 1185.4792 | 333.7407 | 623.4112 | 601.4693 | 610.165 | 249.492 | 570.7158
1370.4807 | 1186.4807 | 333.4179 | 623.9267 | 601.954 | 610.362 | 248.8852 | 570.1429
1371.4821 | 1187.4821 | 333.0615 | 624.4658 | 602.3883 | 610.9712 | 247.9789 | 569.7912
1372.4735 | 1188.4735 | 332.7224 | 625.075 | 602.8174 | 612.0465 | 247.4664 | 569.3508
1373.475 | 1189.475 | 332.2608 | 625.7469 | 603.2798 | 612.1999 | 247.2525 | 568.891
1374.4764 | 1190.4764 | 331.8195 | 626.3943 | 603.7516 | 611.8948 | 246.3087 | 569.0078
1375.4778 | 1191.4778 | 331.4021 | 627.0347 | 604.1863 | 612.1901 | 246.1783 | 568.4654
1376.4793 | 1192.4793 | 331.118 | 627.6646 | 604.667 | 612.3912 | 246.0369 | 568.1314
1377.4807 | 1193.4807 | 330.7461 | 628.2742 | 605.132 | 612.3216 | 245.981 | 567.5848
1378.4822 | 1194.4822 | 330.3856 | 628.8501 | 605.5754 | 612.4171 | 245.6212 | 566.9173
1379.4736 | 1195.4736 | 330.0847 | 629.483 | 606.0127 | 612.3684 | 245.1042 | 567.3222
1380.475 | 1196.475 | 329.7908 | 630.1644 | 606.4078 | 611.9489 | 244.9898 | 567.1712
1381.4765 | 1197.4765 | 329.4897 | 630.857 | 606.8431 | 612.0849 | 244.5726 | 566.7136
1382.4879 | 1198.4879 | 329.0995 | 631.4782 | 607.2604 | 613.3801 | 243.9084 | 566.0246
1383.4793 | 1199.4793 | 328.6817 | 631.9753 | 607.6779 | 614.8932 | 243.7454 | 565.2706
1384.4708 | 1200.4708 | 328.2548 | 632.3552 | 608.1407 | 615.4119 | 243.1371 | 564.5152
1385.4722 | 1201.4722 | 327.7522 | 632.6413 | 608.5755 | 615.3282 | 242.7069 | 563.5358
1386.4737 | 1202.4737 | 327.3063 | 632.9835 | 608.9623 | 615.3612 | 241.8418 | 562.8402
1387.4751 | 1203.4751 | 326.821 | 633.3696 | 609.4123 | 615.5259 | 241.1946 | 561.9447
1388.4765 | 1204.4765 | 326.3698 | 633.8428 | 609.8647 | 616.1238 | 241.0373 | 561.5697
1389.478 | 1205.478 | 325.902 | 634.3102 | 610.278 | 616.468 | 240.7902 | 560.8314
1390.4794 | 1206.4794 | 325.5086 | 634.7243 | 610.7319 | 617.1858 | 240.8958 | 560.1249
1391.4809 | 1207.4809 | 325.217 | 635.0664 | 611.1364 | 618.3741 | 240.3269 | 559.2442
1392.4723 | 1208.4723 | 324.8511 | 635.3666 | 611.5546 | 619.9323 | 239.7713 | 558.3984
1393.4737 | 1209.4737 | 324.4509 | 635.709 | 611.9188 | 620.9079 | 239.5837 | 557.851
1394.4752 | 1210.4752 | 324.0303 | 636.0608 | 612.3124 | 620.4053 | 239.1227 | 557.0643
1395.4766 | 1211.4766 | 323.7067 | 636.5343 | 612.6794 | 620.7792 | 238.9557 | 556.2805
1396.478 | 1212.478 | 323.3461 | 636.9838 | 613.091 | 621.1609 | 238.402 | 555.4618
1397.4795 | 1213.4795 | 322.8527 | 637.3818 | 613.4458 | 620.5129 | 238.3311 | 554.6057
1398.4809 | 1214.4809 | 322.4213 | 637.8571 | 613.8979 | 620.4457 | 237.5604 | 553.8749
1399.4723 | 1215.4723 | 322.0305 | 638.3133 | 614.3342 | 620.0572 | 237.7753 | 552.9692
1400.4738 | 1216.4738 | 321.7145 | 638.6997 | 614.748 | 619.6061 | 237.7041 | 551.9628
1401.4752 | 1217.4752 | 321.4236 | 638.9661 | 615.1896 | 619.3243 | 237.3444 | 551.1161
1402.4767 | 1218.4767 | 321.07 | 639.2028 | 615.5912 | 619.704 | 237.02 | 550.1312
1403.4781 | 1219.4781 | 320.73 | 639.5044 | 615.9788 | 619.9704 | 236.7785 | 549.2496
1404.4795 | 1220.4795 | 320.521 | 639.7997 | 616.3342 | 619.6174 | 236.2918 | 548.4429
1405.471 | 1221.471 | 320.2042 | 640.252 | 616.6861 | 619.5614 | 235.9351 | 547.8564
1406.4824 | 1222.4824 | 319.8696 | 640.7366 | 617.0511 | 620.3973 | 236.172 | 547.1673
1407.4738 | 1223.4738 | 319.5111 | 641.2891 | 617.3987 | 620.2108 | 236.1028 | 546.4799
1408.4753 | 1224.4753 | 319.0992 | 641.8191 | 617.7556 | 620.152 | 235.8837 | 545.6192
1409.4767 | 1225.4767 | 318.6346 | 642.2932 | 618.1474 | 620.1786 | 235.6852 | 544.7846
1410.4782 | 1226.4782 | 318.1344 | 642.7185 | 618.5468 | 620.0338 | 235.048 | 543.9622
1411.4796 | 1227.4796 | 317.7156 | 642.9681 | 619.0213 | 619.5874 | 234.596 | 543.1343
1412.481 | 1228.481 | 317.2639 | 643.2224 | 619.4412 | 618.9551 | 234.1326 | 542.48
1413.4825 | 1229.4825 | 316.8482 | 643.5467 | 619.8126 | 618.3932 | 233.8023 | 541.8403
1414.4739 | 1230.4739 | 316.4432 | 643.8727 | 620.1784 | 617.8032 | 233.4432 | 541.2663
1415.4754 | 1231.4754 | 316.0533 | 644.161 | 620.5029 | 617.1738 | 232.6662 | 540.6712
1416.4768 | 1232.4768 | 315.6494 | 644.375 | 620.8097 | 617.1468 | 232.4133 | 540.1555
1417.4782 | 1233.4782 | 315.2936 | 644.6648 | 621.1251 | 616.8701 | 232.5331 | 539.6217
1418.4797 | 1234.4797 | 314.8811 | 644.9325 | 621.4445 | 616.1695 | 231.9571 | 538.9634
1419.4811 | 1235.4811 | 314.479 | 645.1545 | 621.7474 | 616.2494 | 231.426 | 538.3319
1420.4826 | 1236.4826 | 313.9997 | 645.3641 | 622.049 | 616.5758 | 230.9628 | 537.7842
1421.474 | 1237.474 | 313.6249 | 645.6414 | 622.3563 | 616.4289 | 230.6348 | 537.2171
1422.4754 | 1238.4754 | 313.2552 | 645.9956 | 622.6544 | 616.2263 | 230.0422 | 536.5272
1423.4769 | 1239.4769 | 312.8584 | 646.4443 | 622.9027 | 616.5743 | 229.6438 | 535.7634
1424.4783 | 1240.4783 | 312.4965 | 646.8001 | 623.1704 | 616.9894 | 229.0909 | 535.1184
1425.4797 | 1241.4797 | 312.099 | 647.1092 | 623.4462 | 617.6459 | 228.5144 | 534.6762
1426.4812 | 1242.4812 | 311.6999 | 647.3811 | 623.7571 | 618.1157 | 228.5448 | 534.2307
1427.4726 | 1243.4726 | 311.3783 | 647.5614 | 624.0437 | 617.8238 | 228.3049 | 533.751
1428.474 | 1244.474 | 311.0462 | 647.7308 | 624.3268 | 617.9291 | 227.7 | 533.3364
1429.4755 | 1245.4755 | 310.7332 | 647.9732 | 624.6396 | 618.1446 | 227.4609 | 532.9999
1430.4769 | 1246.4769 | 310.3678 | 648.1965 | 625.0012 | 617.9665 | 227.0821 | 532.4993
1431.4784 | 1247.4784 | 309.9923 | 648.4315 | 625.2848 | 617.8219 | 226.0156 | 532.0814
1432.4798 | 1248.4798 | 309.5907 | 648.656 | 625.5838 | 617.5194 | 225.4406 | 531.4992
1433.4712 | 1249.4712 | 309.1899 | 648.8303 | 625.855 | 617.4658 | 224.8205 | 531.0214
1434.4827 | 1250.4827 | 308.7597 | 649.0807 | 626.1236 | 617.4206 | 224.1888 | 530.6421
1435.4741 | 1251.4741 | 308.352 | 649.4125 | 626.4609 | 617.6506 | 223.4812 | 530.2633
1436.4756 | 1252.4756 | 307.9766 | 649.5694 | 626.7536 | 618.1111 | 222.9334 | 529.9569
1437.477 | 1253.477 | 307.6055 | 649.8604 | 627.0379 | 617.9982 | 222.425 | 529.5332
1438.4784 | 1254.4784 | 307.3075 | 650.133 | 627.3124 | 617.8226 | 222.2189 | 529.1534
1439.4799 | 1255.4799 | 307.0239 | 650.4556 | 627.6187 | 617.5416 | 222.0028 | 528.7633
1440.4813 | 1256.4813 | 306.6715 | 650.6986 | 627.9096 | 617.3608 | 221.4712 | 528.3958
1441.4727 | 1257.4727 | 306.4267 | 651.0102 | 628.1838 | 617.211 | 221.2619 | 528.1723
1442.4742 | 1258.4742 | 306.1317 | 651.2738 | 628.4566 | 617.6367 | 220.9889 | 527.9387
1443.4756 | 1259.4756 | 305.8257 | 651.6296 | 628.7354 | 617.2802 | 220.4482 | 527.7114
1444.4771 | 1260.4771 | 305.4235 | 651.9683 | 629.0173 | 617.2655 | 220.1959 | 527.3125
1445.4785 | 1261.4785 | 305.0131 | 652.194 | 629.3267 | 617.4147 | 219.7915 | 526.7545
1446.4799 | 1262.4799 | 304.5786 | 652.4151 | 629.6284 | 616.9601 | 219.2538 | 526.2552
1447.4714 | 1263.4714 | 304.2022 | 652.575 | 629.9016 | 616.7489 | 219.326 | 525.8617
1448.4728 | 1264.4728 | 303.8479 | 652.6847 | 630.1677 | 616.1725 | 218.5576 | 525.4794
1449.4742 | 1265.4742 | 303.5197 | 652.8025 | 630.4267 | 615.6707 | 217.9998 | 525.1649
1450.4757 | 1266.4757 | 303.1006 | 652.92 | 630.6594 | 615.5178 | 216.8694 | 524.7291
1451.4771 | 1267.4771 | 302.7312 | 653.2103 | 630.9027 | 615.3274 | 216.4355 | 524.4698
1452.4786 | 1268.4786 | 302.4467 | 653.4928 | 631.1492 | 614.9398 | 216.0858 | 524.0714
1453.48 | 1269.48 | 302.1265 | 653.7052 | 631.3616 | 614.2386 | 215.3763 | 523.7659
1454.4814 | 1270.4814 | 301.793 | 653.8465 | 631.5638 | 613.8064 | 215.2216 | 523.5513
1455.4829 | 1271.4829 | 301.4319 | 653.9561 | 631.7671 | 613.719 | 215.0092 | 523.2391
1456.4743 | 1272.4743 | 301.1507 | 654.0434 | 631.9996 | 613.8728 | 214.6269 | 523.0822
1457.4757 | 1273.4757 | 300.7707 | 654.1498 | 632.2392 | 614.0593 | 214.1832 | 522.5931
1458.4772 | 1274.4772 | 300.3727 | 654.2677 | 632.4779 | 614.4868 | 213.4745 | 521.9674
1459.4786 | 1275.4786 | 300.0023 | 654.4727 | 632.6911 | 614.6009 | 213.2501 | 521.417
1460.4801 | 1276.4801 | 299.6807 | 654.6449 | 632.9429 | 614.2375 | 212.6481 | 520.978
1461.4815 | 1277.4815 | 299.477 | 654.7854 | 633.1929 | 613.9444 | 212.1882 | 520.5695
1462.4729 | 1278.4729 | 299.2159 | 654.9504 | 633.4639 | 613.5129 | 211.5311 | 519.9727
1463.4744 | 1279.4744 | 298.8607 | 655.2015 | 633.6952 | 613.0935 | 211.3944 | 519.4906
1464.4758 | 1280.4758 | 298.5454 | 655.3545 | 633.9367 | 612.9168 | 210.7642 | 519.0387
1465.4773 | 1281.4773 | 298.1423 | 655.5175 | 634.1702 | 612.5268 | 210.3978 | 518.6759
1466.4787 | 1282.4787 | 297.7114 | 655.6416 | 634.3745 | 612.1805 | 209.9248 | 518.2776
1467.4801 | 1283.4801 | 297.3706 | 655.8444 | 634.5839 | 611.8878 | 209.544 | 517.9309
1468.4716 | 1284.4716 | 297.0119 | 656.0104 | 634.7783 | 611.4863 | 209.0454 | 517.6075
1469.473 | 1285.473 | 296.6545 | 656.2445 | 634.9942 | 611.1293 | 208.6815 | 517.2692
1470.5145 | 1286.5145 | 296.2712 | 656.5888 | 635.1712 | 610.9446 | 208.2718 | 517.2369
1471.4759 | 1287.4759 | 295.9382 | 656.8063 | 635.3477 | 610.5774 | 208.0204 | 517.1889
1472.4773 | 1288.4773 | 295.5195 | 656.8752 | 635.5369 | 610.124 | 207.653 | 517.0493
1473.4788 | 1289.4788 | 295.1197 | 657.0764 | 635.6904 | 609.9952 | 207.1959 | 516.6422
1474.4802 | 1290.4802 | 294.7476 | 657.2808 | 635.8899 | 609.9644 | 207.2409 | 516.2708
1475.4816 | 1291.4816 | 294.3635 | 657.3898 | 636.0726 | 609.8285 | 206.6081 | 515.9684
1476.4731 | 1292.4731 | 293.9651 | 657.4925 | 636.2662 | 609.7926 | 206.9058 | 515.6186
1477.4745 | 1293.4745 | 293.6173 | 657.4843 | 636.5099 | 609.8613 | 206.9204 | 515.4182
1478.4759 | 1294.4759 | 293.3 | 657.6786 | 636.7556 | 610.1621 | 206.7338 | 515.1797
1479.4774 | 1295.4774 | 293.0298 | 657.8779 | 636.9744 | 610.1547 | 206.454 | 514.9777
1480.4788 | 1296.4788 | 292.7679 | 658.0747 | 637.1657 | 610.1868 | 206.6104 | 515.0597
1481.4803 | 1297.4803 | 292.5091 | 658.2819 | 637.3588 | 610.4278 | 206.2973 | 515.038
1482.4717 | 1298.4717 | 292.2452 | 658.4028 | 637.5436 | 610.022 | 206.3227 | 515.0196
1483.4731 | 1299.4731 | 291.8946 | 658.5573 | 637.7479 | 609.847 | 206.0455 | 514.7858
1484.4746 | 1300.4746 | 291.6181 | 658.7507 | 637.9249 | 609.8516 | 205.9148 | 514.5721
1485.476 | 1301.476 | 291.2886 | 659.1342 | 638.0923 | 609.2856 | 205.6295 | 514.3049
1486.4774 | 1302.4774 | 290.8707 | 659.4253 | 638.2415 | 608.7582 | 205.2863 | 514.1121
1487.4789 | 1303.4789 | 290.4517 | 659.7204 | 638.4095 | 608.2717 | 204.7854 | 513.9633
1488.4803 | 1304.4803 | 290.0495 | 659.7382 | 638.5564 | 607.7794 | 204.4556 | 513.7782
1489.4718 | 1305.4718 | 289.6965 | 659.7384 | 638.6932 | 607.4485 | 203.9332 | 513.6444
1490.4732 | 1306.4732 | 289.2643 | 659.7884 | 638.8343 | 606.9553 | 203.7866 | 513.5338
1491.4746 | 1307.4746 | 288.8624 | 659.8944 | 638.942 | 606.582 | 203.8121 | 513.4242
1492.4761 | 1308.4761 | 288.6038 | 659.9327 | 639.0503 | 605.9534 | 203.2711 | 513.325
1493.4775 | 1309.4775 | 288.3369 | 660.1207 | 639.1634 | 605.3532 | 203.1242 | 513.1405
1494.479 | 1310.479 | 287.9884 | 660.2951 | 639.3044 | 605.0862 | 202.8593 | 513.0202
1495.4804 | 1311.4804 | 287.7 | 660.4014 | 639.4402 | 604.7442 | 202.636 | 512.8399
1496.4818 | 1312.4818 | 287.4925 | 660.7411 | 639.5861 | 604.5256 | 202.7597 | 512.6253
1497.4733 | 1313.4733 | 287.2278 | 661.0734 | 639.683 | 604.2269 | 202.461 | 512.4141
1498.4747 | 1314.4747 | 286.9905 | 661.0814 | 639.7791 | 604.148 | 202.0731 | 512.1757
1499.4761 | 1315.4761 | 286.798 | 661.0067 | 639.8883 | 604.0051 | 202.0859 | 511.8917
1500.4776 | 1316.4776 | 286.5552 | 661.3221 | 640.0122 | 603.6546 | 202.0444 | 511.8002
1501.479 | 1317.479 | 286.3373 | 661.4537 | 640.1452 | 603.2412 | 202.0679 | 511.7092
1502.4805 | 1318.4805 | 286.0849 | 661.443 | 640.2655 | 603.0588 | 202.2536 | 511.58
1503.4819 | 1319.4819 | 285.8013 | 661.6325 | 640.3561 | 603.1999 | 201.9859 | 511.5257
1504.4733 | 1320.4733 | 285.5553 | 661.6911 | 640.4829 | 603.2239 | 201.7569 | 511.4475
1505.4748 | 1321.4748 | 285.3831 | 661.636 | 640.6049 | 603.0519 | 201.3646 | 511.2844
1506.4762 | 1322.4762 | 285.1949 | 661.7107 | 640.7177 | 602.8474 | 201.1328 | 511.2147
1507.4776 | 1323.4776 | 284.8783 | 661.5786 | 640.8329 | 602.4659 | 201.1916 | 511.1366
1508.4791 | 1324.4791 | 284.4944 | 661.5385 | 640.9332 | 602.1928 | 201.1615 | 511.0435
1509.4805 | 1325.4805 | 284.0491 | 661.8264 | 641.0554 | 601.8688 | 200.6168 | 510.9059
1510.472 | 1326.472 | 283.6722 | 662.0478 | 641.1228 | 601.3741 | 200.2163 | 510.8693
1511.4734 | 1327.4734 | 283.2581 | 662.1471 | 641.2292 | 600.7435 | 199.7593 | 510.8073
1512.4748 | 1328.4748 | 282.9097 | 662.2892 | 641.3407 | 600.1721 | 199.9561 | 510.7022
1513.4763 | 1329.4763 | 282.6489 | 662.3321 | 641.4761 | 599.5421 | 199.7829 | 510.6037
1514.4777 | 1330.4777 | 282.3834 | 662.2175 | 641.5932 | 598.8878 | 199.3614 | 510.5712
1515.4792 | 1331.4792 | 282.1699 | 662.1998 | 641.6822 | 598.4069 | 199.4956 | 510.5241
1516.4806 | 1332.4806 | 281.904 | 662.4852 | 641.7226 | 598.0503 | 199.6191 | 510.4566
1517.472 | 1333.472 | 281.6078 | 662.6422 | 641.8342 | 597.6406 | 199.6268 | 510.4728
1518.4735 | 1334.4735 | 281.3496 | 662.6086 | 641.923 | 597.1559 | 199.6939 | 510.4368
1519.4749 | 1335.4749 | 281.0552 | 662.5645 | 642.0052 | 596.7699 | 199.3632 | 510.2608
1520.4763 | 1336.4763 | 280.7273 | 662.623 | 642.0883 | 596.3114 | 198.993 | 510.1106
1521.4778 | 1337.4778 | 280.3987 | 662.8202 | 642.1518 | 595.8226 | 198.5104 | 510.0726
1522.4792 | 1338.4792 | 280.0719 | 662.9915 | 642.2116 | 595.4424 | 198.4258 | 509.9939
1523.4807 | 1339.4807 | 279.7792 | 663.1124 | 642.2532 | 595.0371 | 198.1905 | 509.9169
1524.4721 | 1340.4721 | 279.4676 | 663.5684 | 642.3157 | 594.7719 | 198.3254 | 509.8641
1525.4735 | 1341.4735 | 279.1837 | 663.5946 | 642.3903 | 594.6158 | 197.8733 | 509.927
1526.475 | 1342.475 | 278.9057 | 663.5835 | 642.4753 | 594.3506 | 197.7897 | 509.8681
1527.4764 | 1343.4764 | 278.603 | 663.7037 | 642.5439 | 593.9486 | 197.4172 | 509.8551
1528.4778 | 1344.4778 | 278.2336 | 664.095 | 642.6337 | 593.6124 | 197.338 | 509.9062
1529.4793 | 1345.4793 | 277.8536 | 664.2435 | 642.6933 | 593.2938 | 196.7461 | 509.9206
1530.4807 | 1346.4807 | 277.4708 | 664.3282 | 642.7626 | 592.9153 | 196.3977 | 509.8537
1531.4721 | 1347.4721 | 277.0626 | 664.2195 | 642.8143 | 592.4417 | 196.3918 | 509.8087
1532.4736 | 1348.4736 | 276.6908 | 664.1405 | 642.8759 | 591.9601 | 196.1015 | 509.7977
1533.475 | 1349.475 | 276.3264 | 664.1243 | 642.9062 | 591.5003 | 195.9413 | 509.6843
1534.4765 | 1350.4765 | 275.9181 | 664.2066 | 642.963 | 591.0667 | 195.6934 | 509.5379
1535.4779 | 1351.4779 | 275.5104 | 664.2446 | 643.018 | 590.6839 | 195.4677 | 509.4813
1536.4793 | 1352.4793 | 275.1401 | 664.1749 | 643.1012 | 590.2342 | 194.929 | 509.3566
1537.4708 | 1353.4708 | 274.8405 | 664.4363 | 643.1685 | 589.8643 | 194.6257 | 509.3132
1538.4722 | 1354.4722 | 274.5645 | 664.7813 | 643.2252 | 589.5956 | 194.1177 | 509.298
1539.4737 | 1355.4737 | 274.2315 | 664.8611 | 643.2613 | 589.329 | 194.0307 | 509.3037
1540.4751 | 1356.4751 | 273.9162 | 664.8107 | 643.3027 | 589.0964 | 193.5431 | 509.3266
1541.4765 | 1357.4765 | 273.6144 | 664.7906 | 643.3362 | 588.988 | 193.0039 | 509.4407
1542.478 | 1358.478 | 273.3006 | 664.7693 | 643.3676 | 588.8732 | 192.6196 | 509.4188
1543.4794 | 1359.4794 | 273.0507 | 664.9056 | 643.3758 | 588.629 | 192.4804 | 509.3902
1544.4809 | 1360.4809 | 272.7745 | 665.1197 | 643.3805 | 588.459 | 192.2028 | 509.3881
1545.4823 | 1361.4823 | 272.4918 | 665.1707 | 643.4182 | 588.3354 | 191.7717 | 509.2877
1546.4737 | 1362.4737 | 272.2233 | 665.1259 | 643.4315 | 588.0927 | 191.6938 | 509.1616
1547.4752 | 1363.4752 | 271.9979 | 665.1483 | 643.4719 | 587.9338 | 191.628 | 508.9446
1548.4766 | 1364.4766 | 271.7463 | 665.0969 | 643.5003 | 587.7581 | 191.4581 | 508.9288
1549.478 | 1365.478 | 271.4525 | 665.248 | 643.5218 | 587.449 | 191.2544 | 508.9604
1550.4795 | 1366.4795 | 271.0436 | 665.1929 | 643.556 | 587.1538 | 190.9448 | 508.882
1551.4809 | 1367.4809 | 270.6062 | 665.2494 | 643.593 | 586.7634 | 190.471 | 508.8313
1552.4824 | 1368.4824 | 270.2564 | 665.0977 | 643.6183 | 586.2899 | 190.2076 | 508.834
1553.4738 | 1369.4738 | 269.8843 | 664.9274 | 643.6215 | 585.9322 | 189.4737 | 508.8083
1554.4752 | 1370.4752 | 269.5651 | 664.7615 | 643.6373 | 585.6416 | 188.9931 | 508.8231
1555.4767 | 1371.4767 | 269.2359 | 664.5483 | 643.6923 | 585.2496 | 189.0538 | 508.8818
1556.4781 | 1372.4781 | 268.838 | 664.4201 | 643.674 | 584.8083 | 188.8362 | 508.8697
1557.4795 | 1373.4795 | 268.5255 | 664.2743 | 643.6574 | 584.3558 | 188.7666 | 508.7713
1558.481 | 1374.481 | 268.2383 | 664.1777 | 643.6612 | 583.8721 | 188.9112 | 508.6964
1559.4724 | 1375.4724 | 267.9944 | 664.1032 | 643.6639 | 583.3314 | 188.5584 | 508.6396
1560.4739 | 1376.4739 | 267.6433 | 664.223 | 643.6723 | 582.7477 | 188.3599 | 508.6448
1561.4753 | 1377.4753 | 267.3567 | 664.3621 | 643.6582 | 582.2708 | 187.8764 | 508.6496
1562.4767 | 1378.4767 | 267.0588 | 664.6621 | 643.6796 | 581.7942 | 187.575 | 508.6303
1563.5783 | 1379.5783 | 266.7109 | 664.7805 | 643.7241 | 581.2412 | 187.1734 | 508.568
1564.4796 | 1380.4796 | 266.3961 | 664.7799 | 643.7659 | 580.8169 | 186.9808 | 508.4891
1565.471 | 1381.471 | 266.0599 | 664.7744 | 643.8161 | 580.3252 | 186.5516 | 508.4052
1566.4725 | 1382.4725 | 265.7234 | 664.801 | 643.8424 | 579.8046 | 186.6095 | 508.3647
1567.4739 | 1383.4739 | 265.409 | 664.8267 | 643.8982 | 579.3321 | 186.0253 | 508.3009
1568.4754 | 1384.4754 | 265.1197 | 664.9092 | 643.9539 | 578.8685 | 186.0551 | 508.2531
1569.4768 | 1385.4768 | 264.7473 | 664.8878 | 643.9597 | 578.5299 | 185.2487 | 508.2173
1570.4782 | 1386.4782 | 264.4188 | 664.826 | 643.9415 | 578.2239 | 184.9983 | 508.2527
1571.4797 | 1387.4797 | 264.0956 | 664.7922 | 643.9514 | 577.868 | 184.7564 | 508.1958
1572.4811 | 1388.4811 | 263.8045 | 664.7956 | 643.9599 | 577.5235 | 184.5657 | 508.1223
1573.4725 | 1389.4725 | 263.5263 | 664.7349 | 643.954 | 577.2035 | 184.2625 | 508.0206
1574.474 | 1390.474 | 263.2907 | 664.6417 | 643.9498 | 576.9097 | 183.8503 | 507.9693
1575.4754 | 1391.4754 | 263.0173 | 664.494 | 643.9543 | 576.6636 | 183.3353 | 507.902
1576.4769 | 1392.4769 | 262.7908 | 664.423 | 643.9545 | 576.3303 | 183.0398 | 507.915
1577.4783 | 1393.4783 | 262.6806 | 664.361 | 643.9899 | 575.929 | 182.6954 | 507.9037
1578.4797 | 1394.4797 | 262.5759 | 664.3181 | 643.9914 | 575.4871 | 182.5318 | 507.842
1579.4712 | 1395.4712 | 262.4148 | 664.2314 | 643.9694 | 575.0233 | 182.4548 | 507.7732
1580.4826 | 1396.4826 | 262.2456 | 664.1603 | 643.984 | 574.5295 | 182.3884 | 507.8438
1581.474 | 1397.474 | 261.9315 | 664.2434 | 644.013 | 574.0291 | 182.5024 | 507.8829
1582.4755 | 1398.4755 | 261.5903 | 664.407 | 644.0448 | 573.5012 | 182.1365 | 507.8653
1583.4769 | 1399.4769 | 261.1892 | 664.4994 | 644.0276 | 572.9854 | 181.7789 | 507.7943
1584.4784 | 1400.4784 | 260.8672 | 664.3871 | 644.011 | 572.5196 | 181.3542 | 507.7305
1585.4798 | 1401.4798 | 260.5877 | 664.2935 | 643.9813 | 572.0544 | 181.1748 | 507.6366
1586.4812 | 1402.4812 | 260.3089 | 664.2774 | 643.9379 | 571.6939 | 180.8001 | 507.5793
1587.4827 | 1403.4827 | 260.0538 | 664.2436 | 643.9385 | 571.379 | 180.547 | 507.5372
1588.4741 | 1404.4741 | 259.8101 | 664.2897 | 643.9178 | 571.0765 | 180.0151 | 507.4359
1589.4756 | 1405.4756 | 259.4975 | 664.2148 | 643.8606 | 570.7612 | 179.6081 | 507.3781
1590.477 | 1406.477 | 259.2313 | 664.1745 | 643.8236 | 570.4702 | 179.5354 | 507.4035
1591.4784 | 1407.4784 | 259.0474 | 664.4 | 643.8438 | 570.1406 | 179.5668 | 507.4216
1592.4799 | 1408.4799 | 258.8527 | 664.5437 | 643.8333 | 569.8245 | 179.7067 | 507.46
1593.4813 | 1409.4813 | 258.6314 | 664.59 | 643.8428 | 569.4786 | 179.5664 | 507.4355
1594.4727 | 1410.4727 | 258.3487 | 664.4815 | 643.8417 | 569.1174 | 179.2243 | 507.3795
1595.4742 | 1411.4742 | 257.9985 | 664.3247 | 643.8344 | 568.6982 | 178.8233 | 507.3828
1596.4756 | 1412.4756 | 257.5906 | 664.2397 | 643.8521 | 568.2983 | 178.4361 | 507.3773
1597.4771 | 1413.4771 | 257.2409 | 664.3297 | 643.8726 | 567.8747 | 177.9795 | 507.3017
1598.4785 | 1414.4785 | 256.9526 | 664.5109 | 643.8382 | 567.4292 | 177.7909 | 507.2547
1599.4799 | 1415.4799 | 256.6263 | 664.5285 | 643.8326 | 567.0289 | 177.4155 | 507.202
1600.4714 | 1416.4714 | 256.4034 | 664.4032 | 643.7914 | 566.5748 | 176.8831 | 507.1457
1601.4728 | 1417.4728 | 256.1543 | 664.3641 | 643.7404 | 566.1255 | 176.5811 | 507.0396
1602.4742 | 1418.4742 | 255.921 | 664.3637 | 643.683 | 565.6967 | 176.3066 | 506.9594
1603.4757 | 1419.4757 | 255.7341 | 664.3709 | 643.6058 | 565.2566 | 175.7117 | 506.9645
1604.4771 | 1420.4771 | 255.4491 | 664.2875 | 643.5653 | 564.7857 | 175.2158 | 507.0113
1605.4786 | 1421.4786 | 255.1294 | 664.0338 | 643.518 | 564.3312 | 174.6022 | 507.0472
1606.48 | 1422.48 | 254.8573 | 663.7756 | 643.4633 | 563.8615 | 174.4392 | 507.0507
1607.4714 | 1423.4714 | 254.579 | 663.7372 | 643.4379 | 563.3766 | 174.1546 | 506.966
1608.4729 | 1424.4729 | 254.3456 | 663.6277 | 643.4322 | 562.8558 | 174.0037 | 506.8822
1609.4743 | 1425.4743 | 254.0669 | 663.4732 | 643.3672 | 562.3258 | 173.713 | 506.8302
1610.4758 | 1426.4758 | 253.7675 | 663.4113 | 643.3033 | 561.8008 | 173.3945 | 506.7183
1611.4772 | 1427.4772 | 253.4487 | 663.2577 | 643.2397 | 561.2959 | 173.2049 | 506.5698
1612.4786 | 1428.4786 | 253.1532 | 663.0383 | 643.2013 | 560.8648 | 173.0261 | 506.4435
1613.4801 | 1429.4801 | 252.8304 | 662.7959 | 643.1386 | 560.4235 | 172.8165 | 506.3282
1614.4715 | 1430.4715 | 252.4885 | 662.7344 | 643.1041 | 559.9364 | 172.6119 | 506.31
1615.4729 | 1431.4729 | 252.1891 | 662.7576 | 643.0712 | 559.4917 | 172.4168 | 506.2626
1616.4744 | 1432.4744 | 251.9207 | 662.6888 | 643.0393 | 559.0413 | 172.001 | 506.1491
1617.4758 | 1433.4758 | 251.6714 | 662.5502 | 642.9868 | 558.6065 | 172.0318 | 506.0207
1618.4773 | 1434.4773 | 251.4341 | 662.4206 | 642.9763 | 558.1583 | 171.6872 | 505.9372
1619.4787 | 1435.4787 | 251.1436 | 662.4441 | 642.9186 | 557.6937 | 171.5122 | 505.9325
1620.4801 | 1436.4801 | 250.8789 | 662.4479 | 642.9145 | 557.2084 | 171.3791 | 505.9526
1621.4716 | 1437.4716 | 250.5937 | 662.2952 | 642.8411 | 556.7328 | 171.4499 | 505.8754
1622.473 | 1438.473 | 250.2668 | 662.0647 | 642.8264 | 556.1936 | 171.4872 | 505.7714
1623.4744 | 1439.4744 | 250.0744 | 662.0406 | 642.7237 | 555.6922 | 171.7166 | 505.6602
1624.4759 | 1440.4759 | 249.8601 | 661.9867 | 642.6186 | 555.1837 | 171.5171 | 505.6221
1625.4773 | 1441.4773 | 249.6534 | 661.9103 | 642.4952 | 554.6588 | 171.3215 | 505.6092
1626.4788 | 1442.4788 | 249.4108 | 662.1546 | 642.386 | 554.1431 | 171.3494 | 505.5861
1627.4802 | 1443.4802 | 249.1743 | 662.1811 | 642.2933 | 553.5961 | 171.2998 | 505.5506
1628.4816 | 1444.4816 | 248.9796 | 662.0298 | 642.2117 | 553.0385 | 171.4476 | 505.4382
1629.4831 | 1445.4831 | 248.7808 | 661.9956 | 642.1306 | 552.4637 | 171.3705 | 505.3479
1630.4745 | 1446.4745 | 248.5229 | 661.8361 | 642.1463 | 551.8564 | 171.0898 | 505.2846
1631.4759 | 1447.4759 | 248.2177 | 661.6259 | 642.0696 | 551.2767 | 170.9646 | 505.3163
1632.4774 | 1448.4774 | 247.9024 | 661.4794 | 641.976 | 550.687 | 170.8797 | 505.2458
1633.4788 | 1449.4788 | 247.5938 | 661.2732 | 641.8653 | 550.0754 | 170.4712 | 505.1732
1634.4803 | 1450.4803 | 247.2862 | 661.3935 | 641.7036 | 549.4505 | 170.3546 | 505.1637
1635.4817 | 1451.4817 | 247.0909 | 661.2965 | 641.5981 | 548.8512 | 170.2312 | 505.0814
1636.4731 | 1452.4731 | 246.8877 | 661.1668 | 641.5006 | 548.2168 | 170.0695 | 505.0416
1637.4746 | 1453.4746 | 246.5786 | 661.0346 | 641.4257 | 547.5812 | 170.0418 | 504.9928
1638.476 | 1454.476 | 246.2868 | 660.9608 | 641.3403 | 547.0203 | 169.8063 | 504.9277
1639.4775 | 1455.4775 | 245.9668 | 660.8269 | 641.2297 | 546.3179 | 169.6513 | 504.8561
1640.4789 | 1456.4789 | 245.7113 | 660.6171 | 641.1152 | 544.8838 | 169.3008 | 504.7291
1641.4803 | 1457.4803 | 245.4024 | 660.5066 | 640.9908 | 543.4107 | 169.2038 | 504.6364
1642.4718 | 1458.4718 | 245.0874 | 660.1504 | 640.8644 | 542.0352 | 168.9382 | 504.5144
1643.4732 | 1459.4732 | 244.8454 | 659.9556 | 640.7479 | 540.8386 | 168.3653 | 504.3922
1644.4746 | 1460.4746 | 244.6887 | 659.8158 | 640.5666 | 539.7819 | 168.1932 | 504.1679
1645.4761 | 1461.4761 | 244.4662 | 659.9693 | 640.4209 | 538.8276 | 168.2122 | 503.9702
1646.4775 | 1462.4775 | 244.2217 | 659.6052 | 640.2778 | 537.9367 | 167.8742 | 503.7536
1647.479 | 1463.479 | 244.0531 | 659.1372 | 640.1039 | 537.0606 | 167.5582 | 503.515
1648.4804 | 1464.4804 | 243.8124 | 658.8721 | 639.9533 | 536.1618 | 167.5818 | 503.3805
1649.4718 | 1465.4718 | 243.4847 | 658.6505 | 639.7886 | 535.2797 | 167.5726 | 503.2388
1650.4933 | 1466.4933 | 243.156 | 658.4257 | 639.6299 | 534.4179 | 167.2921 | 503.0591
1651.4747 | 1467.4747 | 242.8539 | 658.2059 | 639.4593 | 533.7351 | 167.2891 | 502.8947
1652.4761 | 1468.4761 | 242.5924 | 657.7366 | 639.3099 | 533.0979 | 167.2422 | 502.7957
1653.4776 | 1469.4776 | 242.3719 | 657.7316 | 639.1169 | 532.5126 | 167.2612 | 502.6962
1654.479 | 1470.479 | 242.0915 | 657.6 | 638.9498 | 531.8746 | 167.1675 | 502.5996
1655.4805 | 1471.4805 | 241.7805 | 657.3239 | 638.7941 | 531.0789 | 166.7615 | 502.4433
1656.4819 | 1472.4819 | 241.5197 | 657.3252 | 638.5987 | 530.4057 | 166.5485 | 502.1893
1657.4733 | 1473.4733 | 241.3151 | 657.4635 | 638.4236 | 529.7198 | 166.4861 | 502.045
1658.4748 | 1474.4748 | 241.0528 | 657.4252 | 638.2556 | 529.2465 | 166.1714 | 501.923
1659.4762 | 1475.4762 | 240.7566 | 657.289 | 638.0839 | 528.7312 | 165.8168 | 501.7811
1660.4776 | 1476.4776 | 240.4605 | 657.0905 | 637.9292 | 528.0741 | 165.3296 | 501.5983
1661.4791 | 1477.4791 | 240.1956 | 656.8148 | 637.7387 | 527.4648 | 165.065 | 501.4148
1662.4805 | 1478.4805 | 239.9713 | 656.5525 | 637.6042 | 526.979 | 164.5908 | 501.2027
1663.472 | 1479.472 | 239.7173 | 656.2712 | 637.4273 | 526.4896 | 163.8544 | 501.0551
1664.4734 | 1480.4734 | 239.4422 | 655.892 | 637.2716 | 525.9985 | 163.6423 | 500.8655
1665.4748 | 1481.4748 | 239.1691 | 655.5521 | 637.0924 | 525.6124 | 163.1498 | 500.6969
1666.4763 | 1482.4763 | 238.9088 | 655.2486 | 636.8971 | 525.2178 | 162.9669 | 500.501
1667.4777 | 1483.4777 | 238.6839 | 654.9731 | 636.7043 | 524.7522 | 162.8421 | 500.3479
1668.4792 | 1484.4792 | 238.3613 | 654.5525 | 636.5244 | 524.1639 | 162.4775 | 500.1559
1669.4806 | 1485.4806 | 238.0242 | 654.553 | 636.3731 | 523.6585 | 161.9991 | 499.9761
1670.482 | 1486.482 | 237.7121 | 654.6397 | 636.2016 | 523.197 | 161.8566 | 499.9219
1671.4735 | 1487.4735 | 237.5371 | 654.6565 | 636.006 | 522.771 | 161.7564 | 499.868
1672.4749 | 1488.4749 | 237.415 | 654.5972 | 635.8217 | 522.2508 | 161.5421 | 499.7678
1673.4763 | 1489.4763 | 237.1996 | 654.4935 | 635.6672 | 521.6755 | 161.6955 | 499.6902
1674.4778 | 1490.4778 | 236.9136 | 654.2657 | 635.4845 | 521.1059 | 161.5695 | 499.5232
1675.4792 | 1491.4792 | 236.6379 | 653.8685 | 635.3546 | 520.4632 | 161.5075 | 499.4357
1676.4807 | 1492.4807 | 236.3104 | 653.46 | 635.1573 | 519.8026 | 161.2861 | 499.2992
1677.4821 | 1493.4821 | 235.981 | 653.2967 | 634.943 | 519.3316 | 160.9775 | 499.1453
1678.4735 | 1494.4735 | 235.666 | 652.9831 | 634.739 | 518.9277 | 160.7299 | 499.0214
1679.475 | 1495.475 | 235.3905 | 652.5866 | 634.5441 | 518.3732 | 160.4162 | 498.8696
1680.4764 | 1496.4764 | 235.1116 | 652.2928 | 634.356 | 517.9033 | 160.2294 | 498.7024
1681.4778 | 1497.4778 | 234.8652 | 652.0237 | 634.1474 | 517.6106 | 160.005 | 498.541
1682.4793 | 1498.4793 | 234.6545 | 651.5937 | 633.9408 | 517.2077 | 159.571 | 498.3618
1683.4807 | 1499.4807 | 234.3966 | 651.2661 | 633.731 | 516.6846 | 159.0605 | 498.1905
1684.4722 | 1500.4722 | 234.1662 | 650.9201 | 633.5283 | 516.2467 | 158.8206 | 498.0166
1685.4736 | 1501.4736 | 233.9742 | 650.6085 | 633.2884 | 515.9648 | 158.8043 | 497.849
1686.475 | 1502.475 | 233.7848 | 650.2031 | 633.0669 | 515.7538 | 158.54 | 497.2112
1687.4765 | 1503.4765 | 233.5874 | 649.9322 | 632.8334 | 515.4599 | 158.3843 | 496.6076
1688.4779 | 1504.4779 | 233.3788 | 649.6198 | 632.6137 | 514.9919 | 158.1568 | 496.1173
1689.4794 | 1505.4794 | 233.1779 | 649.1134 | 632.3428 | 514.6365 | 157.9714 | 495.7637
1690.4808 | 1506.4808 | 232.9449 | 648.8303 | 632.0946 | 514.2904 | 157.7617 | 495.4547
1691.4722 | 1507.4722 | 232.7201 | 648.5705 | 631.8426 | 513.9613 | 157.5816 | 495.2204
1692.4737 | 1508.4737 | 232.5127 | 648.4524 | 631.5745 | 513.5369 | 157.372 | 494.9624
1693.4751 | 1509.4751 | 232.2727 | 648.0276 | 631.3229 | 513.1955 | 157.2958 | 494.7124
1694.4765 | 1510.4765 | 231.9898 | 647.3987 | 631.0759 | 512.8547 | 156.8832 | 494.4912
1695.478 | 1511.478 | 231.7969 | 647.0775 | 630.8504 | 512.4639 | 156.5344 | 494.3254
1696.4794 | 1512.4794 | 231.6098 | 646.7749 | 630.6283 | 512.2054 | 156.5794 | 494.1033
1697.4809 | 1513.4809 | 231.312 | 646.5726 | 630.4098 | 511.8422 | 156.4332 | 493.9093
1698.4723 | 1514.4723 | 231.0287 | 645.973 | 630.1957 | 511.36 | 156.3869 | 493.7354
1699.4737 | 1515.4737 | 230.7687 | 645.4962 | 629.9566 | 510.9031 | 156.1064 | 493.539
1700.4752 | 1516.4752 | 230.5034 | 645.1518 | 629.7508 | 510.4273 | 156.022 | 493.3723
1701.4766 | 1517.4766 | 230.1966 | 644.7002 | 629.5135 | 509.9506 | 155.3653 | 493.2237
1702.478 | 1518.478 | 229.9407 | 644.2162 | 629.2572 | 509.6014 | 155.241 | 493.0258
1703.4795 | 1519.4795 | 229.7151 | 643.7 | 629.0296 | 509.1743 | 155.2141 | 492.8488
1704.4809 | 1520.4809 | 229.4131 | 643.1688 | 628.7847 | 508.8851 | 154.9179 | 492.6897
1705.4723 | 1521.4723 | 229.1254 | 642.737 | 628.5339 | 508.4657 | 154.6966 | 492.4967
1706.4738 | 1522.4738 | 228.9083 | 642.4357 | 628.2945 | 507.9621 | 154.574 | 492.3622
1707.4752 | 1523.4752 | 228.7142 | 642.0652 | 628.0466 | 507.5922 | 154.3087 | 492.2363
1708.4767 | 1524.4767 | 228.461 | 641.9182 | 627.8047 | 507.362 | 153.956 | 492.0313
1709.4781 | 1525.4781 | 228.221 | 641.3022 | 627.5506 | 507.0983 | 153.8743 | 491.8784
1710.4795 | 1526.4795 | 228.0265 | 640.7883 | 627.3004 | 506.8356 | 153.9537 | 491.7137
1711.481 | 1527.481 | 227.8287 | 640.3242 | 627.0496 | 506.5906 | 153.8879 | 491.5675
1712.4724 | 1528.4724 | 227.5737 | 639.7723 | 626.7973 | 506.0976 | 154.0361 | 491.3927
1713.4739 | 1529.4739 | 227.29 | 639.2928 | 626.5305 | 505.7423 | 153.8679 | 491.2423
1714.4753 | 1530.4753 | 227.0811 | 638.8494 | 626.261 | 505.4109 | 153.8715 | 491.0738
1715.4767 | 1531.4767 | 226.9144 | 638.2085 | 626.041 | 504.9841 | 153.8191 | 490.9156
1716.4782 | 1532.4782 | 226.7589 | 637.6371 | 625.7878 | 504.6168 | 153.6053 | 490.7763
1717.4796 | 1533.4796 | 226.5794 | 637.2523 | 625.5137 | 504.2717 | 153.5253 | 490.6794
1718.4811 | 1534.4811 | 226.366 | 636.8329 | 625.2341 | 503.95 | 153.3528 | 490.5929
1719.4825 | 1535.4825 | 226.1005 | 636.2823 | 624.9492 | 503.5885 | 153.1919 | 490.4682
1720.4739 | 1536.4739 | 225.8182 | 635.7033 | 624.6845 | 503.2197 | 152.7821 | 490.3189
1721.4754 | 1537.4754 | 225.5166 | 635.2717 | 624.4062 | 502.8527 | 152.6721 | 490.1425
1722.4768 | 1538.4768 | 225.2185 | 634.6286 | 624.1404 | 502.4589 | 152.4143 | 489.9621
1723.4782 | 1539.4782 | 224.9061 | 634.1215 | 623.837 | 502.1516 | 152.1092 | 489.8119
1724.4797 | 1540.4797 | 224.6916 | 633.4735 | 623.5423 | 501.8354 | 151.9107 | 489.6354
1725.4811 | 1541.4811 | 224.4942 | 632.7629 | 623.273 | 501.5285 | 151.5317 | 489.4808
1726.4725 | 1542.4725 | 224.2949 | 632.1975 | 622.9878 | 501.2016 | 151.3806 | 489.2865
1727.474 | 1543.474 | 224.0922 | 631.669 | 622.7153 | 500.7058 | 151.3121 | 489.1208
1728.4754 | 1544.4754 | 223.947 | 631.3081 | 622.4662 | 500.255 | 151.1835 | 488.9817
1729.4769 | 1545.4769 | 223.7562 | 630.83 | 622.1812 | 500.0058 | 151.2505 | 488.8616
1730.4783 | 1546.4783 | 223.5994 | 630.2468 | 621.9041 | 499.6326 | 150.9757 | 488.7234
1731.4797 | 1547.4797 | 223.3747 | 629.6278 | 621.5873 | 499.1714 | 150.9814 | 488.5499
1732.4712 | 1548.4712 | 223.2242 | 629.0586 | 621.2823 | 498.7372 | 150.8166 | 488.3618
1733.4726 | 1549.4726 | 223.0559 | 628.4852 | 620.9606 | 498.3203 | 150.5387 | 488.2226
1734.4741 | 1550.4741 | 222.8587 | 627.8894 | 620.6725 | 497.9696 | 150.7675 | 488.0813
1735.4755 | 1551.4755 | 222.5973 | 627.2173 | 620.3897 | 497.622 | 150.8035 | 487.9265
1736.4769 | 1552.4769 | 222.4197 | 626.4297 | 620.0501 | 497.1578 | 150.4963 | 487.7957
1737.4784 | 1553.4784 | 222.2638 | 625.8215 | 619.7437 | 496.6396 | 150.4653 | 487.6217
1738.4798 | 1554.4798 | 222.0698 | 625.0364 | 619.4175 | 496.2491 | 150.4807 | 487.4786
1739.4712 | 1555.4712 | 221.8211 | 624.3192 | 619.08 | 495.8844 | 150.4261 | 487.3089
1740.4727 | 1556.4727 | 221.5864 | 623.4787 | 618.7759 | 495.5849 | 150.0661 | 487.1521
1741.4741 | 1557.4741 | 221.2921 | 622.684 | 618.4594 | 495.2474 | 150.0198 | 486.9879
1742.4756 | 1558.4756 | 221.0237 | 621.8234 | 618.1188 | 494.784 | 149.635 | 486.8122
1743.477 | 1559.477 | 220.7832 | 620.8851 | 617.7719 | 494.3235 | 149.2862 | 486.6605
1744.4784 | 1560.4784 | 220.5294 | 619.9567 | 617.458 | 493.8216 | 148.8227 | 486.5744
1745.4799 | 1561.4799 | 220.2694 | 618.7389 | 617.1287 | 493.2868 | 149.0167 | 486.4051
1746.4813 | 1562.4813 | 220.0119 | 617.5251 | 616.8125 | 492.8423 | 149.0882 | 486.2389
1747.4727 | 1563.4727 | 219.7446 | 616.3268 | 616.4493 | 492.5046 | 148.6627 | 486.041
1748.4742 | 1564.4742 | 219.5249 | 615.2608 | 616.1206 | 492.1931 | 148.5829 | 485.9089
1749.4756 | 1565.4756 | 219.3067 | 613.9678 | 615.7858 | 491.8209 | 148.34 | 485.7016
1750.4771 | 1566.4771 | 219.1336 | 612.7358 | 615.4337 | 491.4042 | 148.1696 | 485.5572
1751.4785 | 1567.4785 | 218.9396 | 611.5488 | 615.0671 | 491.0387 | 147.8092 | 485.3865
1752.4799 | 1568.4799 | 218.7073 | 610.3405 | 614.7152 | 490.6871 | 147.2566 | 485.1473
1753.4814 | 1569.4814 | 218.5108 | 609.1448 | 614.3463 | 490.3219 | 146.8263 | 484.9261
1754.4728 | 1570.4728 | 218.3038 | 608.0134 | 613.9901 | 489.957 | 146.6993 | 484.7126
1755.4742 | 1571.4742 | 218.0928 | 606.8944 | 613.6333 | 489.5369 | 146.2321 | 484.5018
1756.4757 | 1572.4757 | 217.8627 | 605.7641 | 613.2556 | 489.0147 | 145.9314 | 484.3121
1757.4771 | 1573.4771 | 217.6096 | 604.6994 | 612.8665 | 488.4494 | 145.7103 | 484.1297
1758.4786 | 1574.4786 | 217.3224 | 603.7094 | 612.4501 | 487.868 | 145.4396 | 483.9414
1759.48 | 1575.48 | 217.0667 | 602.7301 | 612.0793 | 487.1777 | 145.1767 | 483.7258
1760.4814 | 1576.4814 | 216.826 | 601.7795 | 611.7123 | 486.7176 | 145.0503 | 483.5398
1761.4829 | 1577.4829 | 216.5699 | 600.8851 | 611.3465 | 486.3006 | 144.8969 | 483.3437
1762.4743 | 1578.4743 | 216.3603 | 600.0596 | 610.9711 | 485.7251 | 144.6283 | 483.2071
1763.4758 | 1579.4758 | 216.203 | 599.2712 | 610.5884 | 485.3488 | 144.4631 | 483.02
1764.4772 | 1580.4772 | 215.9963 | 598.5212 | 610.2067 | 484.9523 | 144.2355 | 482.8651
1765.4786 | 1581.4786 | 215.8385 | 597.7887 | 609.7976 | 484.6238 | 144.1401 | 482.68
1766.4801 | 1582.4801 | 215.7591 | 597.0832 | 609.4227 | 484.1656 | 143.9748 | 482.5352
1767.4815 | 1583.4815 | 215.6682 | 596.375 | 609.0347 | 483.7554 | 143.7946 | 482.3301
1768.4729 | 1584.4729 | 215.507 | 595.6536 | 608.6315 | 483.4099 | 143.942 | 482.1949
1769.4744 | 1585.4744 | 215.3593 | 595.0534 | 608.2238 | 483.078 | 144.0003 | 482.021
1770.5359 | 1586.5359 | 215.1172 | 594.3754 | 607.7809 | 482.7185 | 144.0467 | 481.8719
1771.4773 | 1587.4773 | 214.9465 | 593.7933 | 607.3816 | 482.2779 | 144.2386 | 481.7121
1772.4787 | 1588.4787 | 214.7485 | 593.1649 | 606.9488 | 481.9414 | 143.9031 | 481.5541
1773.4801 | 1589.4801 | 214.5384 | 592.6491 | 606.526 | 481.6874 | 144.0918 | 481.4081
1774.4816 | 1590.4816 | 214.2996 | 592.0427 | 606.1036 | 481.2333 | 144.0817 | 481.2331
1775.473 | 1591.473 | 214.1234 | 591.4068 | 605.6563 | 480.8798 | 143.9725 | 481.0926
1776.4744 | 1592.4744 | 213.9125 | 590.8103 | 605.24 | 480.5617 | 143.7476 | 480.9202
1777.4759 | 1593.4759 | 213.6818 | 590.2324 | 604.8149 | 480.2739 | 143.5121 | 480.7438
1778.4773 | 1594.4773 | 213.4095 | 589.635 | 604.3784 | 479.9037 | 143.2516 | 480.5472
1779.4788 | 1595.4788 | 213.1976 | 589.0936 | 603.9662 | 479.4716 | 143.3457 | 480.3491
1780.4802 | 1596.4802 | 212.9665 | 588.5455 | 603.5297 | 479.0279 | 142.98 | 480.1762
1781.4716 | 1597.4716 | 212.7033 | 587.978 | 603.0881 | 478.4722 | 142.6327 | 479.9908
1782.4731 | 1598.4731 | 212.422 | 587.4137 | 602.6584 | 478.0746 | 142.3593 | 479.7763
1783.4745 | 1599.4745 | 212.1249 | 586.8233 | 602.218 | 477.7332 | 142.3771 | 479.6024
1784.476 | 1600.476 | 211.8848 | 586.2374 | 601.764 | 477.3167 | 142.2018 | 479.4058
1785.4774 | 1601.4774 | 211.6524 | 585.6057 | 601.3054 | 476.8574 | 142.1057 | 479.1917
1786.4788 | 1602.4788 | 211.4266 | 584.9719 | 600.8687 | 476.3434 | 141.8265 | 479.0258
1787.4803 | 1603.4803 | 211.1826 | 584.3814 | 600.4238 | 475.8438 | 141.7965 | 478.8397
1788.4817 | 1604.4817 | 210.9746 | 583.7951 | 599.9781 | 475.3277 | 141.4919 | 478.6905
1789.4731 | 1605.4731 | 210.7888 | 583.2251 | 599.5063 | 474.7512 | 141.3208 | 478.4979
1790.4746 | 1606.4746 | 210.5556 | 582.6475 | 599.0294 | 474.1611 | 140.9501 | 478.3053
1791.476 | 1607.476 | 210.2907 | 582.054 | 598.4989 | 473.4501 | 140.7103 | 478.1532
1792.4775 | 1608.4775 | 209.9817 | 581.5069 | 597.9771 | 472.7503 | 140.5501 | 478.0104
1793.4789 | 1609.4789 | 209.7123 | 580.9385 | 597.4846 | 472.038 | 140.3025 | 477.8306
1794.4803 | 1610.4803 | 209.4988 | 580.3271 | 596.9743 | 471.3428 | 140.2102 | 477.626
1795.4718 | 1611.4718 | 209.2823 | 579.7501 | 596.4928 | 470.8582 | 139.9027 | 477.4783

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 1 |  |  | 2006-06-29 | 13:39
38897.568 | 1 | 0 | 1 | XLPE | 3-C | Tray
38897.5681 | 1 | 0 | 1 | 475 C | 17.7 kW/m2 |  | Conductors
38897.5683 | 1 | 0 | 1
38897.5684 | 1 | 0 | 1
38897.5685 | 1 | 0 | 1
38897.5686 | 1 | 0 | 1
38897.5688 | 1 | 0 | 1
38897.5689 | 1 | 0 | 1
38897.569 | 1 | 0 | 1
38897.5691 | 1 | 0 | 1
38897.5693 | 1 | 0 | 1
38897.5694 | 1 | 0 | 1
38897.5695 | 1 | 0 | 1
38897.5697 | 2 | 0 | 1
38897.5698 | 2 | 0 | 1
38897.5699 | 1 | 0 | 1
38897.57 | 1 | 0 | 1
38897.5702 | 1 | 1 | 1
38897.5703 | 1 | 0 | 1
38897.5704 | 1 | 0 | 1
38897.5705 | 1 | 0 | 1
38897.5706 | 1 | 0 | 1
38897.5708 | 1 | 0 | 1
38897.5709 | 1 | 0 | 1
38897.571 | 1 | 0 | 1
38897.5711 | 1 | 0 | 1
38897.5713 | 1 | 0 | 1
38897.5714 | 1 | 0 | 1
38897.5715 | 1 | 0 | 1
38897.5716 | 1 | 0 | 1
38897.5718 | 1 | 1 | 1
38897.5719 | 1 | 1 | 1
38897.572 | 1 | 0 | 1
38897.5723 | 1 | 1 | 1
38897.5724 | 1 | 0 | 1
38897.5725 | 1 | 0 | 1
38897.5727 | 1 | 0 | 1
38897.5728 | 1 | 0 | 1
38897.5729 | 1 | 0 | 1
38897.573 | 1 | 0 | 1
38897.5731 | 1 | 0 | 1
38897.5733 | 2 | 0 | 1
38897.5734 | 1 | 0 | 1
38897.5735 | 1 | 0 | 1
38897.5736 | 1 | 0 | 1
38897.5738 | 1 | 0 | 1
38897.5739 | 2 | 0 | 1
38897.574 | 1 | 0 | 1
38897.5741 | 1 | 0 | 1
38897.5743 | 1 | 0 | 1
38897.5744 | 1 | 0 | 1
38897.5745 | 1 | 0 | 1
38897.5747 | 1 | 0 | 1
38897.5748 | 1 | 0 | 1
38897.5749 | 1 | 0 | 1
38897.575 | 1 | 0 | 1
38897.5752 | 1 | 0 | 1
38897.5753 | 1 | 0 | 1
38897.5754 | 1 | 0 | 1
38897.5755 | 1 | 0 | 1
38897.5756 | 1 | 0 | 1
38897.5758 | 1 | 0 | 1
38897.5759 | 1 | 0 | 1
38897.576 | 1 | 0 | 1
38897.5761 | 1 | 0 | 1
38897.5763 | 1 | 0 | 1
38897.5764 | 1 | 0 | 1
38897.5765 | 1 | 0 | 1
38897.5766 | 1 | 0 | 1
38897.5768 | 1 | 0 | 1
38897.5769 | 1 | 0 | 1
38897.577 | 1 | 0 | 1
38897.5772 | 1 | 0 | 1
38897.5773 | 1 | 0 | 1
38897.5774 | 1 | 0 | 1
38897.5775 | 1 | 0 | 1
38897.5777 | 1 | 0 | 1
38897.5778 | 1 | 0 | 1
38897.5779 | 1 | 0 | 1
38897.578 | 1 | 0 | 1
38897.5781 | 1 | 0 | 1
38897.5783 | 1 | 0 | 1
38897.5784 | 1 | 0 | 1
38897.5785 | 1 | 0 | 1
38897.5786 | 1 | 0 | 1
38897.5788 | 1 | 0 | 1
38897.5789 | 1 | 0 | 1
38897.579 | 1 | 0 | 1
38897.5791 | 1 | 0 | 1
38897.5793 | 2 | 1 | 1
38897.5794 | 22 | 1 | 1
38897.5795 | 157 | 45 | 1
38897.5797 | 233 | 106 | 1
38897.5798 | 338 | 135 | 1
38897.5799 | 477 | 303 | 1
38897.58 | 544 | 374 | 1
38897.5802 | 628 | 423 | 1
38897.5803 | 594 | 396 | 1
38897.5804 | 1145 | 1020 | 1
38897.5805 | 1260 | 1042 | 1
38897.5806 | 1272 | 1025 | 1
38897.5808 | 1040 | 939 | 1
38897.5809 | 1384 | 771 | 1
38897.581 | 1267 | 715 | 1
38897.5811 | 1713 | 144 | 1
38897.5813 | 1467 | 417 | 1
38897.5814 | 1594 | 517 | 1
38897.5815 | 1603 | 547 | 1
38897.5816 | 1369 | 648 | 1
38897.5818 | 1425 | 687 | 1
38897.5819 | 2220 | 20 | 1
38897.582 | 1942 | 16 | 1
38897.5822 | 2120 | 15 | 1
38897.5823 | 2208 | 13 | 1
38897.5824 | 2058 | 8 | 1
38897.5825 | 2306 | 7 | 1
38897.5827 | 1969 | 6 | 1
38897.5828 | 1942 | 4 | 1
38897.5829 | 2020 | 4 | 1
38897.583 | 2199 | 6 | 1
38897.5831 | 2401 | 5 | 1
38897.5833 | 1906 | 4 | 1
38897.5834 | 2342 | 5 | 1
38897.5835 | 2254 | 4 | 1
38897.5836 | 1929 | 4 | 1
38897.5838 | 2299 | 6 | 1
38897.5839 | 1970 | 3 | 1
38897.584 | 2303 | 6 | 1
38897.5841 | 2404 | 6 | 1
38897.5843 | 2086 | 6 | 1
38897.5844 | 2335 | 8 | 1
38897.5845 | 2400 | 8 | 1
38897.5847 | 2358 | 9 | 1
38897.5848 | 2153 | 9 | 1
38897.5849 | 1845 | 7 | 1
38897.585 | 2393 | 12 | 1
38897.5852 | 1985 | 8 | 1
38897.5853 | 2051 | 8 | 1
38897.5854 | 2221 | 13 | 1
38897.5855 | 2111 | 12 | 1
38897.5856 | 2339 | 16 | 1
38897.5858 | 2341 | 15 | 1
38897.5859 | 2029 | 13 | 1
38897.586 | 2368 | 19 | 1
38897.5861 | 1960 | 19 | 1
38897.5863 | 1955 | 20 | 1
38897.5864 | 2214 | 27 | 1
38897.5865 | 1988 | 424 | 1
38897.5866 | 1497 | 378 | 1
38897.5868 | 2258 | 74 | 1
38897.5869 | 1914 | 63 | 1
38897.587 | 2102 | 70 | 1
38897.5871 | 1813 | 61 | 1
38897.568 | 1 | 0 | 2
38897.5682 | 1 | 0 | 2
38897.5683 | 1 | 0 | 2
38897.5684 | 1 | 0 | 2
38897.5685 | 1 | 0 | 2
38897.5687 | 2 | 0 | 2
38897.5688 | 1 | 0 | 2
38897.5689 | 1 | 0 | 2
38897.569 | 1 | 0 | 2
38897.5692 | 1 | 0 | 2
38897.5693 | 1 | 0 | 2
38897.5694 | 1 | 0 | 2
38897.5695 | 1 | 0 | 2
38897.5697 | 2 | 0 | 2
38897.5698 | 2 | 0 | 2
38897.5699 | 1 | 0 | 2
38897.57 | 2 | 0 | 2
38897.5702 | 1 | 0 | 2
38897.5703 | 1 | 0 | 2
38897.5704 | 1 | 0 | 2
38897.5705 | 1 | 0 | 2
38897.5707 | 1 | 0 | 2
38897.5708 | 1 | 0 | 2
38897.5709 | 1 | 0 | 2
38897.571 | 1 | 0 | 2
38897.5712 | 1 | 0 | 2
38897.5713 | 1 | 0 | 2
38897.5714 | 1 | 0 | 2
38897.5715 | 1 | 0 | 2
38897.5717 | 1 | 0 | 2
38897.5718 | 1 | 0 | 2
38897.5719 | 1 | 0 | 2
38897.572 | 1 | 0 | 2
38897.5722 | 2 | 0 | 2
38897.5723 | 2 | 0 | 2
38897.5724 | 2 | 0 | 2
38897.5725 | 1 | 0 | 2
38897.5727 | 1 | 0 | 2
38897.5728 | 1 | 0 | 2
38897.5729 | 1 | 0 | 2
38897.573 | 2 | 0 | 2
38897.5732 | 1 | 0 | 2
38897.5733 | 1 | 0 | 2
38897.5734 | 1 | 0 | 2
38897.5735 | 1 | 0 | 2
38897.5737 | 1 | 0 | 2
38897.5738 | 1 | 0 | 2
38897.5739 | 1 | 0 | 2
38897.574 | 1 | 0 | 2
38897.5742 | 1 | 0 | 2
38897.5743 | 1 | 0 | 2
38897.5744 | 1 | 0 | 2
38897.5745 | 1 | 0 | 2
38897.5747 | 1 | 0 | 2
38897.5748 | 1 | 0 | 2
38897.5749 | 1 | 0 | 2
38897.575 | 1 | 0 | 2
38897.5752 | 1 | 0 | 2
38897.5753 | 1 | 0 | 2
38897.5754 | 1 | 0 | 2
38897.5755 | 1 | 0 | 2
38897.5757 | 1 | 0 | 2
38897.5758 | 1 | 0 | 2
38897.5759 | 1 | 0 | 2
38897.576 | 1 | 0 | 2
38897.5762 | 1 | 0 | 2
38897.5763 | 1 | 0 | 2
38897.5764 | 1 | 0 | 2
38897.5765 | 2 | 0 | 2
38897.5767 | 1 | 0 | 2
38897.5768 | 1 | 0 | 2
38897.5769 | 1 | 0 | 2
38897.577 | 1 | 0 | 2
38897.5772 | 1 | 0 | 2
38897.5773 | 1 | 0 | 2
38897.5774 | 1 | 0 | 2
38897.5775 | 2 | 0 | 2
38897.5777 | 1 | 0 | 2
38897.5778 | 1 | 0 | 2
38897.5779 | 1 | 0 | 2
38897.578 | 1 | 0 | 2
38897.5782 | 1 | 0 | 2
38897.5783 | 1 | 0 | 2
38897.5784 | 1 | 0 | 2
38897.5785 | 1 | 0 | 2
38897.5787 | 1 | 0 | 2
38897.5788 | 1 | 0 | 2
38897.5789 | 1 | 0 | 2
38897.579 | 1 | 0 | 2
38897.5792 | 1 | 0 | 2
38897.5793 | 1 | 1 | 2
38897.5794 | 1 | 2 | 2
38897.5795 | 77 | 51 | 2
38897.5797 | 177 | 121 | 2
38897.5798 | 218 | 151 | 2
38897.5799 | 455 | 400 | 2
38897.58 | 513 | 449 | 2
38897.5802 | 492 | 385 | 2
38897.5803 | 605 | 487 | 2
38897.5804 | 1067 | 870 | 2
38897.5805 | 1057 | 854 | 2
38897.5807 | 1071 | 844 | 2
38897.5808 | 1094 | 851 | 2
38897.5809 | 1161 | 859 | 2
38897.581 | 1375 | 824 | 2
38897.5812 | 1918 | 164 | 2
38897.5813 | 1576 | 482 | 2
38897.5814 | 1634 | 640 | 2
38897.5815 | 1750 | 604 | 2
38897.5817 | 1459 | 578 | 2
38897.5818 | 1514 | 625 | 2
38897.5819 | 2393 | 19 | 2
38897.582 | 2220 | 17 | 2
38897.5822 | 2428 | 17 | 2
38897.5823 | 1872 | 12 | 2
38897.5824 | 2309 | 9 | 2
38897.5825 | 2422 | 7 | 2
38897.5827 | 2220 | 6 | 2
38897.5828 | 2337 | 7 | 2
38897.5829 | 2325 | 6 | 2
38897.583 | 2185 | 7 | 2
38897.5832 | 2074 | 4 | 2
38897.5833 | 2117 | 3 | 2
38897.5834 | 2004 | 2 | 2
38897.5835 | 1965 | 3 | 2
38897.5837 | 2257 | 4 | 2
38897.5838 | 2168 | 6 | 2
38897.5839 | 2236 | 6 | 2
38897.584 | 2406 | 7 | 2
38897.5842 | 1963 | 4 | 2
38897.5843 | 2338 | 9 | 2
38897.5844 | 2011 | 5 | 2
38897.5845 | 1925 | 5 | 2
38897.5847 | 2117 | 8 | 2
38897.5848 | 1883 | 8 | 2
38897.5849 | 2211 | 9 | 2
38897.585 | 1905 | 8 | 2
38897.5852 | 2415 | 11 | 2
38897.5853 | 2263 | 12 | 2
38897.5854 | 2417 | 9 | 2
38897.5855 | 2306 | 14 | 2
38897.5857 | 2291 | 14 | 2
38897.5858 | 2372 | 16 | 2
38897.5859 | 2264 | 15 | 2
38897.586 | 1897 | 14 | 2
38897.5862 | 2057 | 17 | 2
38897.5863 | 1967 | 19 | 2
38897.5864 | 2115 | 29 | 2
38897.5865 | 1875 | 344 | 2
38897.5867 | 1702 | 450 | 2
38897.5868 | 2259 | 72 | 2
38897.5869 | 2103 | 71 | 2
38897.587 | 2131 | 70 | 2
38897.5872 | 2086 | 75 | 2
38897.568 | 1 | 0 | 3
38897.5682 | 1 | 0 | 3
38897.5683 | 1 | 0 | 3
38897.5684 | 1 | 0 | 3
38897.5685 | 1 | 0 | 3
38897.5687 | 1 | 0 | 3
38897.5688 | 2 | 0 | 3
38897.5689 | 1 | 0 | 3
38897.569 | 1 | 0 | 3
38897.5692 | 1 | 0 | 3
38897.5693 | 1 | 0 | 3
38897.5694 | 1 | 0 | 3
38897.5695 | 1 | 0 | 3
38897.5697 | 2 | 0 | 3
38897.5698 | 1 | 0 | 3
38897.5699 | 1 | 0 | 3
38897.57 | 1 | 0 | 3
38897.5702 | 1 | 0 | 3
38897.5703 | 1 | 0 | 3
38897.5704 | 1 | 0 | 3
38897.5705 | 1 | 0 | 3
38897.5707 | 2 | 0 | 3
38897.5708 | 1 | 0 | 3
38897.5709 | 1 | 0 | 3
38897.571 | 1 | 0 | 3
38897.5712 | 1 | 0 | 3
38897.5713 | 1 | 0 | 3
38897.5714 | 1 | 0 | 3
38897.5715 | 2 | 0 | 3
38897.5717 | 1 | 0 | 3
38897.5718 | 1 | 0 | 3
38897.5719 | 1 | 0 | 3
38897.572 | 1 | 0 | 3
38897.5722 | 1 | 0 | 3
38897.5723 | 1 | 0 | 3
38897.5724 | 1 | 0 | 3
38897.5725 | 1 | 0 | 3
38897.5727 | 1 | 0 | 3
38897.5728 | 1 | 0 | 3
38897.5729 | 1 | 0 | 3
38897.573 | 1 | 0 | 3
38897.5732 | 1 | 0 | 3
38897.5733 | 1 | 0 | 3
38897.5734 | 2 | 0 | 3
38897.5735 | 1 | 0 | 3
38897.5737 | 1 | 0 | 3
38897.5738 | 1 | 0 | 3
38897.5739 | 1 | 0 | 3
38897.574 | 2 | 0 | 3
38897.5742 | 1 | 0 | 3
38897.5743 | 1 | 0 | 3
38897.5744 | 1 | 0 | 3
38897.5745 | 1 | 1 | 3
38897.5747 | 1 | 0 | 3
38897.5748 | 1 | 0 | 3
38897.5749 | 1 | 0 | 3
38897.575 | 1 | 0 | 3
38897.5752 | 1 | 0 | 3
38897.5753 | 1 | 0 | 3
38897.5754 | 1 | 0 | 3
38897.5755 | 1 | 0 | 3
38897.5757 | 1 | 0 | 3
38897.5758 | 2 | 0 | 3
38897.5759 | 1 | 0 | 3
38897.576 | 1 | 0 | 3
38897.5762 | 1 | 0 | 3
38897.5763 | 1 | 0 | 3
38897.5764 | 1 | 0 | 3
38897.5765 | 1 | 0 | 3
38897.5767 | 1 | 0 | 3
38897.5768 | 1 | 0 | 3
38897.5769 | 1 | 0 | 3
38897.577 | 1 | 0 | 3
38897.5772 | 1 | 0 | 3
38897.5773 | 1 | 0 | 3
38897.5774 | 1 | 0 | 3
38897.5775 | 1 | 0 | 3
38897.5777 | 1 | 0 | 3
38897.5778 | 1 | 0 | 3
38897.5779 | 1 | 0 | 3
38897.578 | 1 | 0 | 3
38897.5782 | 2 | 0 | 3
38897.5783 | 1 | 0 | 3
38897.5784 | 1 | 0 | 3
38897.5785 | 1 | 0 | 3
38897.5787 | 1 | 0 | 3
38897.5788 | 1 | 0 | 3
38897.5789 | 1 | 0 | 3
38897.579 | 1 | 0 | 3
38897.5792 | 1 | 0 | 3
38897.5793 | 6 | 1 | 3
38897.5794 | 93 | 13 | 3
38897.5795 | 161 | 39 | 3
38897.5797 | 172 | 69 | 3
38897.5798 | 321 | 159 | 3
38897.5799 | 906 | 749 | 3
38897.58 | 1011 | 851 | 3
38897.5802 | 1029 | 863 | 3
38897.5803 | 1162 | 976 | 3
38897.5804 | 1097 | 898 | 3
38897.5805 | 1096 | 957 | 3
38897.5807 | 1257 | 1071 | 3
38897.5808 | 1284 | 968 | 3
38897.5809 | 1297 | 867 | 3
38897.581 | 1380 | 903 | 3
38897.5812 | 2063 | 358 | 3
38897.5813 | 1761 | 515 | 3
38897.5814 | 1850 | 502 | 3
38897.5815 | 1751 | 601 | 3
38897.5817 | 1633 | 618 | 3
38897.5818 | 1611 | 754 | 3
38897.5819 | 2428 | 20 | 3
38897.582 | 2038 | 15 | 3
38897.5822 | 2088 | 14 | 3
38897.5823 | 1930 | 11 | 3
38897.5824 | 1936 | 6 | 3
38897.5825 | 1934 | 5 | 3
38897.5827 | 2351 | 6 | 3
38897.5828 | 1894 | 5 | 3
38897.5829 | 2347 | 7 | 3
38897.583 | 2434 | 6 | 3
38897.5832 | 1870 | 5 | 3
38897.5833 | 2256 | 5 | 3
38897.5834 | 2186 | 4 | 3
38897.5835 | 2132 | 4 | 3
38897.5837 | 2103 | 4 | 3
38897.5838 | 2257 | 6 | 3
38897.5839 | 2175 | 8 | 3
38897.584 | 1861 | 5 | 3
38897.5842 | 2260 | 7 | 3
38897.5843 | 1883 | 7 | 3
38897.5844 | 2250 | 8 | 3
38897.5845 | 2406 | 9 | 3
38897.5847 | 2265 | 8 | 3
38897.5848 | 1993 | 8 | 3
38897.5849 | 2288 | 12 | 3
38897.585 | 1850 | 8 | 3
38897.5852 | 1920 | 10 | 3
38897.5853 | 2351 | 12 | 3
38897.5854 | 1876 | 12 | 3
38897.5855 | 2018 | 13 | 3
38897.5857 | 2343 | 17 | 3
38897.5858 | 1848 | 13 | 3
38897.5859 | 2068 | 16 | 3
38897.586 | 1943 | 16 | 3
38897.5862 | 2372 | 25 | 3
38897.5863 | 2004 | 24 | 3
38897.5864 | 2226 | 31 | 3
38897.5865 | 1461 | 386 | 3
38897.5867 | 1625 | 366 | 3
38897.5868 | 1834 | 60 | 3
38897.5869 | 1961 | 64 | 3
38897.587 | 1910 | 67 | 3
38897.5872 | 1793 | 61 | 3
38897.5681 | 1 | 0 | 4
38897.5682 | 1 | 1 | 4
38897.5683 | 1 | 0 | 4
38897.5684 | 1 | 0 | 4
38897.5686 | 1 | 0 | 4
38897.5687 | 1 | 0 | 4
38897.5688 | 1 | 0 | 4
38897.5689 | 1 | 0 | 4
38897.5691 | 1 | 0 | 4
38897.5692 | 1 | 0 | 4
38897.5693 | 1 | 0 | 4
38897.5694 | 1 | 0 | 4
38897.5696 | 1 | 0 | 4
38897.5697 | 2 | 0 | 4
38897.5698 | 1 | 0 | 4
38897.5699 | 1 | 0 | 4
38897.5701 | 1 | 0 | 4
38897.5702 | 1 | 0 | 4
38897.5703 | 1 | 0 | 4
38897.5704 | 1 | 0 | 4
38897.5706 | 1 | 0 | 4
38897.5707 | 1 | 0 | 4
38897.5708 | 1 | 0 | 4
38897.5709 | 1 | 0 | 4
38897.5711 | 1 | 0 | 4
38897.5712 | 1 | 0 | 4
38897.5713 | 1 | 0 | 4
38897.5714 | 1 | 0 | 4
38897.5716 | 1 | 0 | 4
38897.5717 | 1 | 0 | 4
38897.5718 | 2 | 0 | 4
38897.5719 | 1 | 0 | 4
38897.5721 | 1 | 0 | 4
38897.5722 | 1 | 0 | 4
38897.5723 | 1 | 0 | 4
38897.5724 | 1 | 0 | 4
38897.5726 | 1 | 1 | 4
38897.5727 | 1 | 0 | 4
38897.5728 | 1 | 0 | 4
38897.5729 | 1 | 0 | 4
38897.5731 | 1 | 0 | 4
38897.5732 | 1 | 0 | 4
38897.5733 | 1 | 0 | 4
38897.5734 | 1 | 0 | 4
38897.5736 | 1 | 0 | 4
38897.5737 | 1 | 0 | 4
38897.5738 | 1 | 1 | 4
38897.5739 | 2 | 0 | 4
38897.5741 | 1 | 0 | 4
38897.5742 | 1 | 0 | 4
38897.5743 | 1 | 0 | 4
38897.5744 | 1 | 0 | 4
38897.5746 | 1 | 0 | 4
38897.5747 | 2 | 0 | 4
38897.5748 | 1 | 0 | 4
38897.5749 | 1 | 0 | 4
38897.5751 | 1 | 0 | 4
38897.5752 | 1 | 0 | 4
38897.5753 | 1 | 0 | 4
38897.5754 | 1 | 0 | 4
38897.5756 | 1 | 0 | 4
38897.5757 | 1 | 1 | 4
38897.5758 | 1 | 0 | 4
38897.5759 | 1 | 0 | 4
38897.5761 | 1 | 0 | 4
38897.5762 | 2 | 0 | 4
38897.5763 | 1 | 0 | 4
38897.5764 | 1 | 0 | 4
38897.5766 | 1 | 0 | 4
38897.5767 | 1 | 0 | 4
38897.5768 | 1 | 0 | 4
38897.5769 | 1 | 0 | 4
38897.5771 | 1 | 0 | 4
38897.5772 | 1 | 0 | 4
38897.5773 | 1 | 0 | 4
38897.5774 | 1 | 0 | 4
38897.5776 | 1 | 0 | 4
38897.5777 | 1 | 0 | 4
38897.5778 | 1 | 0 | 4
38897.5779 | 1 | 0 | 4
38897.5781 | 1 | 0 | 4
38897.5782 | 1 | 0 | 4
38897.5783 | 1 | 0 | 4
38897.5784 | 1 | 0 | 4
38897.5786 | 1 | 0 | 4
38897.5787 | 1 | 0 | 4
38897.5788 | 1 | 0 | 4
38897.5789 | 1 | 0 | 4
38897.5791 | 1 | 0 | 4
38897.5792 | 1 | 0 | 4
38897.5793 | 1 | 1 | 4
38897.5794 | 29 | 15 | 4
38897.5795 | 87 | 57 | 4
38897.5797 | 227 | 162 | 4
38897.5798 | 293 | 226 | 4
38897.5799 | 1025 | 866 | 4
38897.5801 | 1141 | 975 | 4
38897.5802 | 1165 | 992 | 4
38897.5803 | 931 | 808 | 4
38897.5804 | 1287 | 1077 | 4
38897.5806 | 1262 | 1038 | 4
38897.5807 | 1252 | 992 | 4
38897.5808 | 1113 | 846 | 4
38897.5809 | 1073 | 791 | 4
38897.5811 | 1226 | 755 | 4
38897.5812 | 1949 | 426 | 4
38897.5813 | 1628 | 707 | 4
38897.5814 | 1437 | 541 | 4
38897.5816 | 1459 | 566 | 4
38897.5817 | 1580 | 607 | 4
38897.5818 | 1586 | 692 | 4
38897.5819 | 2379 | 20 | 4
38897.582 | 2250 | 19 | 4
38897.5822 | 2309 | 17 | 4
38897.5823 | 2103 | 11 | 4
38897.5824 | 2376 | 9 | 4
38897.5826 | 2415 | 6 | 4
38897.5827 | 2382 | 7 | 4
38897.5828 | 2125 | 5 | 4
38897.5829 | 2125 | 7 | 4
38897.5831 | 1959 | 4 | 4
38897.5832 | 1936 | 4 | 4
38897.5833 | 2386 | 4 | 4
38897.5834 | 1883 | 3 | 4
38897.5836 | 2283 | 5 | 4
38897.5837 | 2185 | 6 | 4
38897.5838 | 2345 | 6 | 4
38897.5839 | 2076 | 6 | 4
38897.5841 | 2052 | 5 | 4
38897.5842 | 1884 | 5 | 4
38897.5843 | 1888 | 7 | 4
38897.5844 | 2189 | 8 | 4
38897.5845 | 1929 | 7 | 4
38897.5847 | 1877 | 7 | 4
38897.5848 | 1892 | 8 | 4
38897.5849 | 1895 | 9 | 4
38897.5851 | 2147 | 12 | 4
38897.5852 | 2102 | 12 | 4
38897.5853 | 1894 | 11 | 4
38897.5854 | 2296 | 15 | 4
38897.5856 | 1920 | 12 | 4
38897.5857 | 1988 | 12 | 4
38897.5858 | 1941 | 14 | 4
38897.5859 | 1983 | 14 | 4
38897.5861 | 2052 | 17 | 4
38897.5862 | 1889 | 17 | 4
38897.5863 | 2132 | 24 | 4
38897.5864 | 2007 | 26 | 4
38897.5866 | 1902 | 436 | 4
38897.5867 | 1640 | 444 | 4
38897.5868 | 1935 | 60 | 4
38897.5869 | 1958 | 68 | 4
38897.587 | 1866 | 63 | 4
38897.5872 | 2106 | 70 | 4
38897.5681 | 1 | 0 | 5
38897.5682 | 1 | 0 | 5
38897.5683 | 1 | 0 | 5
38897.5684 | 1 | 0 | 5
38897.5686 | 1 | 0 | 5
38897.5687 | 1 | 0 | 5
38897.5688 | 1 | 0 | 5
38897.5689 | 1 | 0 | 5
38897.5691 | 1 | 0 | 5
38897.5692 | 1 | 0 | 5
38897.5693 | 1 | 0 | 5
38897.5694 | 1 | 0 | 5
38897.5696 | 1 | 0 | 5
38897.5697 | 2 | 0 | 5
38897.5698 | 1 | 0 | 5
38897.5699 | 1 | 0 | 5
38897.5702 | 1 | 0 | 5
38897.5703 | 2 | 0 | 5
38897.5704 | 1 | 0 | 5
38897.5706 | 1 | 0 | 5
38897.5707 | 2 | 0 | 5
38897.5708 | 1 | 0 | 5
38897.5709 | 1 | 0 | 5
38897.5711 | 1 | 0 | 5
38897.5712 | 1 | 0 | 5
38897.5713 | 1 | 0 | 5
38897.5714 | 1 | 0 | 5
38897.5716 | 1 | 0 | 5
38897.5717 | 1 | 0 | 5
38897.5718 | 1 | 0 | 5
38897.5719 | 2 | 0 | 5
38897.5721 | 1 | 0 | 5
38897.5722 | 1 | 0 | 5
38897.5723 | 1 | 1 | 5
38897.5724 | 1 | 0 | 5
38897.5726 | 1 | 0 | 5
38897.5727 | 1 | 0 | 5
38897.5728 | 1 | 1 | 5
38897.5729 | 1 | 1 | 5
38897.5731 | 1 | 0 | 5
38897.5732 | 1 | 0 | 5
38897.5733 | 1 | 0 | 5
38897.5734 | 1 | 0 | 5
38897.5736 | 1 | 0 | 5
38897.5737 | 1 | 0 | 5
38897.5738 | 1 | 0 | 5
38897.5739 | 1 | 0 | 5
38897.5741 | 1 | 1 | 5
38897.5742 | 1 | 0 | 5
38897.5743 | 1 | 0 | 5
38897.5744 | 1 | 0 | 5
38897.5746 | 1 | 0 | 5
38897.5747 | 1 | 0 | 5
38897.5748 | 1 | 0 | 5
38897.5749 | 1 | 0 | 5
38897.5751 | 1 | 0 | 5
38897.5752 | 1 | 0 | 5
38897.5753 | 1 | 0 | 5
38897.5754 | 1 | 0 | 5
38897.5756 | 1 | 0 | 5
38897.5757 | 1 | 0 | 5
38897.5758 | 1 | 0 | 5
38897.5759 | 1 | 0 | 5
38897.5761 | 1 | 0 | 5
38897.5762 | 1 | 0 | 5
38897.5763 | 1 | 0 | 5
38897.5764 | 1 | 0 | 5
38897.5766 | 1 | 0 | 5
38897.5767 | 1 | 0 | 5
38897.5768 | 1 | 0 | 5
38897.5769 | 1 | 0 | 5
38897.5771 | 1 | 0 | 5
38897.5772 | 1 | 0 | 5
38897.5773 | 1 | 0 | 5
38897.5774 | 1 | 0 | 5
38897.5776 | 1 | 0 | 5
38897.5777 | 1 | 0 | 5
38897.5778 | 1 | 0 | 5
38897.5779 | 1 | 0 | 5
38897.5781 | 1 | 0 | 5
38897.5782 | 1 | 0 | 5
38897.5783 | 1 | 0 | 5
38897.5784 | 1 | 0 | 5
38897.5786 | 1 | 0 | 5
38897.5787 | 1 | 0 | 5
38897.5788 | 1 | 0 | 5
38897.5789 | 9 | 6 | 5
38897.5791 | 433 | 396 | 5
38897.5792 | 838 | 800 | 5
38897.5793 | 1007 | 799 | 5
38897.5794 | 900 | 788 | 5
38897.5796 | 781 | 813 | 5
38897.5797 | 533 | 437 | 5
38897.5798 | 1041 | 979 | 5
38897.5799 | 930 | 835 | 5
38897.5801 | 1043 | 807 | 5
38897.5802 | 972 | 807 | 5
38897.5803 | 1055 | 872 | 5
38897.5804 | 1157 | 951 | 5
38897.5806 | 1305 | 1084 | 5
38897.5807 | 1222 | 965 | 5
38897.5808 | 1181 | 865 | 5
38897.5809 | 1114 | 747 | 5
38897.5811 | 1408 | 904 | 5
38897.5812 | 1581 | 314 | 5
38897.5813 | 1462 | 548 | 5
38897.5814 | 1303 | 593 | 5
38897.5816 | 1622 | 545 | 5
38897.5817 | 1343 | 532 | 5
38897.5818 | 1352 | 495 | 5
38897.5819 | 1980 | 17 | 5
38897.5821 | 2086 | 17 | 5
38897.5822 | 1883 | 14 | 5
38897.5823 | 1932 | 11 | 5
38897.5824 | 2327 | 9 | 5
38897.5826 | 2034 | 5 | 5
38897.5827 | 2393 | 7 | 5
38897.5828 | 1870 | 4 | 5
38897.5829 | 2376 | 8 | 5
38897.5831 | 1926 | 5 | 5
38897.5832 | 2294 | 6 | 5
38897.5833 | 1938 | 4 | 5
38897.5834 | 2048 | 4 | 5
38897.5836 | 1849 | 4 | 5
38897.5837 | 2184 | 5 | 5
38897.5838 | 2256 | 7 | 5
38897.5839 | 2237 | 6 | 5
38897.5841 | 2276 | 7 | 5
38897.5842 | 2307 | 8 | 5
38897.5843 | 2242 | 9 | 5
38897.5844 | 2312 | 9 | 5
38897.5846 | 2024 | 8 | 5
38897.5847 | 2154 | 9 | 5
38897.5848 | 2041 | 9 | 5
38897.5849 | 2019 | 11 | 5
38897.5851 | 2363 | 12 | 5
38897.5852 | 2389 | 10 | 5
38897.5853 | 2147 | 13 | 5
38897.5854 | 1857 | 12 | 5
38897.5856 | 2181 | 15 | 5
38897.5857 | 2165 | 17 | 5
38897.5858 | 2277 | 17 | 5
38897.5859 | 2245 | 17 | 5
38897.5861 | 2340 | 23 | 5
38897.5862 | 2156 | 22 | 5
38897.5863 | 2182 | 30 | 5
38897.5864 | 2222 | 31 | 5
38897.5866 | 1901 | 386 | 5
38897.5867 | 1435 | 399 | 5
38897.5868 | 1805 | 59 | 5
38897.5869 | 2184 | 81 | 5
38897.5871 | 2075 | 71 | 5
38897.5872 | 2309 | 60 | 5
38897.5681 | 1 | 0 | 6
38897.5682 | 1 | 0 | 6
38897.5683 | 1 | 0 | 6
38897.5684 | 1 | 0 | 6
38897.5686 | 1 | 0 | 6
38897.5687 | 1 | 0 | 6
38897.5688 | 1 | 0 | 6
38897.5689 | 1 | 0 | 6
38897.5691 | 1 | 0 | 6
38897.5692 | 2 | 0 | 6
38897.5693 | 1 | 0 | 6
38897.5695 | 1 | 0 | 6
38897.5696 | 1 | 0 | 6
38897.5697 | 2 | 0 | 6
38897.5698 | 1 | 0 | 6
38897.57 | 1 | 0 | 6
38897.5701 | 1 | 0 | 6
38897.5702 | 1 | 0 | 6
38897.5703 | 1 | 0 | 6
38897.5705 | 1 | 0 | 6
38897.5706 | 1 | 0 | 6
38897.5707 | 1 | 0 | 6
38897.5708 | 1 | 0 | 6
38897.5709 | 2 | 0 | 6
38897.5711 | 1 | 0 | 6
38897.5712 | 2 | 0 | 6
38897.5713 | 1 | 0 | 6
38897.5714 | 2 | 0 | 6
38897.5716 | 1 | 0 | 6
38897.5717 | 1 | 0 | 6
38897.5718 | 1 | 0 | 6
38897.572 | 1 | 0 | 6
38897.5721 | 1 | 0 | 6
38897.5722 | 1 | 0 | 6
38897.5723 | 1 | 1 | 6
38897.5725 | 1 | 0 | 6
38897.5726 | 2 | 0 | 6
38897.5727 | 1 | 0 | 6
38897.5728 | 1 | 0 | 6
38897.573 | 1 | 0 | 6
38897.5731 | 1 | 0 | 6
38897.5732 | 1 | 0 | 6
38897.5733 | 1 | 0 | 6
38897.5734 | 1 | 0 | 6
38897.5736 | 1 | 0 | 6
38897.5737 | 1 | 0 | 6
38897.5738 | 1 | 0 | 6
38897.5739 | 1 | 0 | 6
38897.5741 | 1 | 0 | 6
38897.5742 | 1 | 0 | 6
38897.5743 | 2 | 0 | 6
38897.5745 | 1 | 0 | 6
38897.5746 | 1 | 1 | 6
38897.5747 | 1 | 0 | 6
38897.5748 | 1 | 0 | 6
38897.575 | 1 | 0 | 6
38897.5751 | 1 | 0 | 6
38897.5752 | 1 | 0 | 6
38897.5753 | 1 | 0 | 6
38897.5755 | 1 | 0 | 6
38897.5756 | 1 | 0 | 6
38897.5757 | 1 | 0 | 6
38897.5758 | 1 | 0 | 6
38897.5759 | 1 | 0 | 6
38897.5761 | 1 | 0 | 6
38897.5762 | 1 | 0 | 6
38897.5763 | 1 | 0 | 6
38897.5764 | 1 | 0 | 6
38897.5766 | 1 | 0 | 6
38897.5767 | 1 | 0 | 6
38897.5768 | 1 | 0 | 6
38897.577 | 1 | 0 | 6
38897.5771 | 1 | 0 | 6
38897.5772 | 1 | 0 | 6
38897.5773 | 1 | 0 | 6
38897.5775 | 1 | 0 | 6
38897.5776 | 1 | 0 | 6
38897.5777 | 1 | 0 | 6
38897.5778 | 1 | 0 | 6
38897.578 | 1 | 0 | 6
38897.5781 | 1 | 0 | 6
38897.5782 | 1 | 0 | 6
38897.5783 | 1 | 0 | 6
38897.5784 | 1 | 0 | 6
38897.5786 | 1 | 0 | 6
38897.5787 | 1 | 0 | 6
38897.5788 | 1 | 0 | 6
38897.5789 | 178 | 156 | 6
38897.5791 | 78 | 56 | 6
38897.5792 | 952 | 860 | 6
38897.5793 | 1006 | 900 | 6
38897.5794 | 1047 | 934 | 6
38897.5796 | 301 | 186 | 6
38897.5797 | 506 | 353 | 6
38897.5798 | 925 | 802 | 6
38897.58 | 1095 | 933 | 6
38897.5801 | 1015 | 845 | 6
38897.5802 | 1003 | 897 | 6
38897.5803 | 1074 | 960 | 6
38897.5805 | 1258 | 1047 | 6
38897.5806 | 1081 | 869 | 6
38897.5807 | 1277 | 803 | 6
38897.5808 | 1095 | 881 | 6
38897.5809 | 1353 | 874 | 6
38897.5811 | 1191 | 693 | 6
38897.5812 | 1696 | 435 | 6
38897.5813 | 1620 | 539 | 6
38897.5814 | 1559 | 697 | 6
38897.5816 | 1517 | 514 | 6
38897.5817 | 1422 | 484 | 6
38897.5818 | 1606 | 478 | 6
38897.5819 | 1991 | 16 | 6
38897.5821 | 2296 | 19 | 6
38897.5822 | 1881 | 15 | 6
38897.5823 | 2180 | 12 | 6
38897.5825 | 2334 | 9 | 6
38897.5826 | 2089 | 6 | 6
38897.5827 | 2001 | 5 | 6
38897.5828 | 2009 | 6 | 6
38897.583 | 2117 | 5 | 6
38897.5831 | 2217 | 7 | 6
38897.5832 | 2027 | 6 | 6
38897.5833 | 2078 | 4 | 6
38897.5834 | 2202 | 4 | 6
38897.5836 | 2311 | 6 | 6
38897.5837 | 2386 | 6 | 6
38897.5838 | 2429 | 7 | 6
38897.5839 | 2284 | 5 | 6
38897.5841 | 1908 | 4 | 6
38897.5842 | 1881 | 7 | 6
38897.5843 | 2402 | 10 | 6
38897.5844 | 1925 | 7 | 6
38897.5846 | 2140 | 9 | 6
38897.5847 | 1956 | 9 | 6
38897.5848 | 2340 | 11 | 6
38897.585 | 2300 | 12 | 6
38897.5851 | 2024 | 9 | 6
38897.5852 | 2112 | 12 | 6
38897.5853 | 1959 | 10 | 6
38897.5855 | 2382 | 15 | 6
38897.5856 | 1852 | 13 | 6
38897.5857 | 2303 | 17 | 6
38897.5858 | 2007 | 13 | 6
38897.5859 | 2338 | 17 | 6
38897.5861 | 1880 | 17 | 6
38897.5862 | 1960 | 18 | 6
38897.5863 | 2225 | 24 | 6
38897.5864 | 1984 | 25 | 6
38897.5866 | 1626 | 360 | 6
38897.5867 | 2020 | 65 | 6
38897.5868 | 2076 | 68 | 6
38897.5869 | 1786 | 67 | 6
38897.5871 | 1957 | 69 | 6
38897.5872 | 2146 | 70 | 6
38897.5681 | 1 | 0 | 7
38897.5682 | 1 | 0 | 7
38897.5683 | 1 | 0 | 7
38897.5685 | 1 | 0 | 7
38897.5686 | 1 | 0 | 7
38897.5687 | 1 | 0 | 7
38897.5688 | 1 | 0 | 7
38897.569 | 1 | 0 | 7
38897.5691 | 1 | 0 | 7
38897.5692 | 1 | 0 | 7
38897.5693 | 1 | 0 | 7
38897.5695 | 1 | 0 | 7
38897.5696 | 1 | 0 | 7
38897.5697 | 1 | 0 | 7
38897.5698 | 1 | 0 | 7
38897.57 | 1 | 0 | 7
38897.5701 | 2 | 0 | 7
38897.5702 | 1 | 0 | 7
38897.5703 | 2 | 0 | 7
38897.5705 | 1 | 0 | 7
38897.5706 | 1 | 0 | 7
38897.5707 | 1 | 0 | 7
38897.5708 | 1 | 0 | 7
38897.571 | 1 | 0 | 7
38897.5711 | 1 | 0 | 7
38897.5712 | 1 | 0 | 7
38897.5713 | 1 | 0 | 7
38897.5715 | 1 | 0 | 7
38897.5716 | 1 | 0 | 7
38897.5717 | 1 | 0 | 7
38897.5718 | 1 | 0 | 7
38897.572 | 1 | 0 | 7
38897.5721 | 2 | 0 | 7
38897.5722 | 1 | 0 | 7
38897.5723 | 1 | 1 | 7
38897.5725 | 1 | 0 | 7
38897.5726 | 1 | 0 | 7
38897.5727 | 1 | 0 | 7
38897.5728 | 1 | 0 | 7
38897.573 | 2 | 0 | 7
38897.5731 | 1 | 0 | 7
38897.5732 | 2 | 0 | 7
38897.5733 | 1 | 0 | 7
38897.5735 | 1 | 0 | 7
38897.5736 | 1 | 0 | 7
38897.5737 | 1 | 0 | 7
38897.5738 | 1 | 0 | 7
38897.574 | 1 | 0 | 7
38897.5741 | 1 | 0 | 7
38897.5742 | 1 | 0 | 7
38897.5743 | 2 | 0 | 7
38897.5745 | 1 | 0 | 7
38897.5746 | 1 | 0 | 7
38897.5747 | 1 | 0 | 7
38897.5748 | 1 | 0 | 7
38897.575 | 1 | 0 | 7
38897.5751 | 1 | 0 | 7
38897.5752 | 1 | 0 | 7
38897.5753 | 1 | 0 | 7
38897.5755 | 1 | 0 | 7
38897.5756 | 1 | 0 | 7
38897.5757 | 1 | 0 | 7
38897.5758 | 1 | 0 | 7
38897.576 | 1 | 0 | 7
38897.5761 | 1 | 0 | 7
38897.5762 | 1 | 0 | 7
38897.5763 | 1 | 0 | 7
38897.5765 | 1 | 0 | 7
38897.5766 | 1 | 0 | 7
38897.5767 | 1 | 0 | 7
38897.5768 | 1 | 0 | 7
38897.577 | 1 | 0 | 7
38897.5771 | 1 | 0 | 7
38897.5772 | 1 | 0 | 7
38897.5773 | 1 | 0 | 7
38897.5775 | 1 | 0 | 7
38897.5776 | 1 | 0 | 7
38897.5777 | 1 | 0 | 7
38897.5778 | 1 | 0 | 7
38897.578 | 1 | 0 | 7
38897.5781 | 1 | 0 | 7
38897.5782 | 1 | 0 | 7
38897.5783 | 1 | 0 | 7
38897.5785 | 1 | 0 | 7
38897.5786 | 1 | 0 | 7
38897.5787 | 1 | 0 | 7
38897.5788 | 1 | 0 | 7
38897.579 | 1 | 0 | 7
38897.5791 | 1 | 1 | 7
38897.5792 | 2 | 22 | 7
38897.5793 | 2 | 23 | 7
38897.5795 | 3 | 26 | 7
38897.5796 | 55 | 16 | 7
38897.5797 | 202 | 134 | 7
38897.5798 | 413 | 349 | 7
38897.58 | 494 | 406 | 7
38897.5801 | 426 | 387 | 7
38897.5802 | 658 | 542 | 7
38897.5803 | 625 | 506 | 7
38897.5805 | 1296 | 1094 | 7
38897.5806 | 1180 | 1038 | 7
38897.5807 | 1083 | 833 | 7
38897.5808 | 1034 | 664 | 7
38897.581 | 1309 | 936 | 7
38897.5811 | 1303 | 783 | 7
38897.5812 | 1866 | 480 | 7
38897.5813 | 1703 | 596 | 7
38897.5815 | 1741 | 576 | 7
38897.5816 | 1644 | 588 | 7
38897.5817 | 1567 | 621 | 7
38897.5818 | 1994 | 305 | 7
38897.582 | 1929 | 16 | 7
38897.5821 | 2421 | 16 | 7
38897.5822 | 2398 | 16 | 7
38897.5823 | 2230 | 13 | 7
38897.5825 | 2247 | 6 | 7
38897.5826 | 2336 | 8 | 7
38897.5827 | 2344 | 7 | 7
38897.5828 | 2276 | 8 | 7
38897.583 | 2391 | 6 | 7
38897.5831 | 1889 | 5 | 7
38897.5832 | 2212 | 6 | 7
38897.5833 | 1927 | 4 | 7
38897.5835 | 1872 | 6 | 7
38897.5836 | 1981 | 6 | 7
38897.5837 | 2102 | 5 | 7
38897.5838 | 1912 | 6 | 7
38897.584 | 1997 | 6 | 7
38897.5841 | 1990 | 6 | 7
38897.5842 | 2123 | 7 | 7
38897.5843 | 2238 | 9 | 7
38897.5845 | 2030 | 7 | 7
38897.5846 | 2349 | 11 | 7
38897.5847 | 2126 | 9 | 7
38897.5848 | 2220 | 10 | 7
38897.585 | 1952 | 9 | 7
38897.5851 | 2328 | 12 | 7
38897.5852 | 2316 | 14 | 7
38897.5853 | 2400 | 14 | 7
38897.5855 | 1965 | 11 | 7
38897.5856 | 1902 | 12 | 7
38897.5857 | 1999 | 12 | 7
38897.5858 | 2330 | 17 | 7
38897.586 | 2011 | 15 | 7
38897.5861 | 2023 | 17 | 7
38897.5862 | 2004 | 19 | 7
38897.5863 | 2098 | 28 | 7
38897.5865 | 2225 | 32 | 7
38897.5866 | 1851 | 553 | 7
38897.5867 | 2265 | 79 | 7
38897.5868 | 2099 | 83 | 7
38897.587 | 2233 | 88 | 7
38897.5871 | 2095 | 73 | 7
38897.5872 | 1794 | 64 | 7
38897.5681 | 1 | 0 | 8
38897.5682 | 1 | 0 | 8
38897.5683 | 1 | 0 | 8
38897.5685 | 1 | 0 | 8
38897.5686 | 1 | 1 | 8
38897.5687 | 1 | 0 | 8
38897.5688 | 1 | 0 | 8
38897.569 | 1 | 1 | 8
38897.5691 | 1 | 0 | 8
38897.5692 | 1 | 0 | 8
38897.5694 | 1 | 0 | 8
38897.5695 | 1 | 0 | 8
38897.5696 | 1 | 0 | 8
38897.5697 | 1 | 0 | 8
38897.5698 | 1 | 0 | 8
38897.57 | 1 | 0 | 8
38897.5701 | 1 | 0 | 8
38897.5702 | 1 | 0 | 8
38897.5703 | 1 | 0 | 8
38897.5705 | 1 | 1 | 8
38897.5706 | 1 | 0 | 8
38897.5707 | 1 | 0 | 8
38897.5708 | 1 | 0 | 8
38897.571 | 1 | 0 | 8
38897.5711 | 1 | 0 | 8
38897.5712 | 1 | 0 | 8
38897.5713 | 1 | 0 | 8
38897.5715 | 1 | 0 | 8
38897.5716 | 1 | 0 | 8
38897.5717 | 1 | 0 | 8
38897.5719 | 1 | 0 | 8
38897.572 | 1 | 0 | 8
38897.5721 | 2 | 0 | 8
38897.5722 | 1 | 0 | 8
38897.5723 | 1 | 0 | 8
38897.5725 | 1 | 0 | 8
38897.5726 | 1 | 0 | 8
38897.5727 | 1 | 0 | 8
38897.5728 | 1 | 0 | 8
38897.573 | 2 | 0 | 8
38897.5731 | 1 | 0 | 8
38897.5732 | 1 | 0 | 8
38897.5733 | 1 | 0 | 8
38897.5735 | 1 | 0 | 8
38897.5736 | 1 | 0 | 8
38897.5737 | 1 | 0 | 8
38897.5738 | 1 | 0 | 8
38897.574 | 1 | 0 | 8
38897.5741 | 1 | 1 | 8
38897.5742 | 1 | 0 | 8
38897.5744 | 1 | 0 | 8
38897.5745 | 1 | 0 | 8
38897.5746 | 1 | 0 | 8
38897.5747 | 1 | 0 | 8
38897.5748 | 1 | 0 | 8
38897.575 | 1 | 0 | 8
38897.5751 | 1 | 0 | 8
38897.5752 | 1 | 0 | 8
38897.5753 | 1 | 0 | 8
38897.5755 | 1 | 0 | 8
38897.5756 | 1 | 0 | 8
38897.5757 | 1 | 0 | 8
38897.5758 | 1 | 0 | 8
38897.576 | 1 | 0 | 8
38897.5761 | 2 | 0 | 8
38897.5762 | 1 | 0 | 8
38897.5763 | 1 | 0 | 8
38897.5765 | 1 | 0 | 8
38897.5766 | 1 | 0 | 8
38897.5767 | 1 | 0 | 8
38897.5768 | 1 | 0 | 8
38897.577 | 1 | 0 | 8
38897.5771 | 1 | 0 | 8
38897.5772 | 1 | 0 | 8
38897.5773 | 1 | 0 | 8
38897.5775 | 1 | 0 | 8
38897.5776 | 1 | 0 | 8
38897.5777 | 1 | 0 | 8
38897.5778 | 1 | 0 | 8
38897.578 | 1 | 0 | 8
38897.5781 | 1 | 0 | 8
38897.5782 | 1 | 0 | 8
38897.5783 | 1 | 0 | 8
38897.5785 | 1 | 0 | 8
38897.5786 | 1 | 0 | 8
38897.5787 | 1 | 1 | 8
38897.5788 | 1 | 0 | 8
38897.579 | 1 | 0 | 8
38897.5791 | 1 | 0 | 8
38897.5792 | 1 | 13 | 8
38897.5794 | 2 | 17 | 8
38897.5795 | 8 | 18 | 8
38897.5796 | 68 | 18 | 8
38897.5797 | 342 | 206 | 8
38897.5798 | 469 | 348 | 8
38897.58 | 457 | 290 | 8
38897.5801 | 532 | 350 | 8
38897.5802 | 748 | 547 | 8
38897.5803 | 1075 | 888 | 8
38897.5805 | 1036 | 839 | 8
38897.5806 | 1242 | 1016 | 8
38897.5807 | 1213 | 1018 | 8
38897.5808 | 1006 | 813 | 8
38897.581 | 1121 | 712 | 8
38897.5811 | 1415 | 829 | 8
38897.5812 | 1914 | 437 | 8
38897.5813 | 1475 | 429 | 8
38897.5815 | 1472 | 511 | 8
38897.5816 | 1546 | 503 | 8
38897.5817 | 1585 | 722 | 8
38897.5819 | 1683 | 274 | 8
38897.582 | 2056 | 17 | 8
38897.5821 | 2180 | 16 | 8
38897.5822 | 1997 | 13 | 8
38897.5823 | 2128 | 10 | 8
38897.5825 | 1946 | 6 | 8
38897.5826 | 2419 | 6 | 8
38897.5827 | 1911 | 5 | 8
38897.5828 | 2418 | 8 | 8
38897.583 | 2181 | 6 | 8
38897.5831 | 1864 | 6 | 8
38897.5832 | 2379 | 9 | 8
38897.5833 | 2242 | 6 | 8
38897.5835 | 2180 | 6 | 8
38897.5836 | 2188 | 6 | 8
38897.5837 | 2298 | 7 | 8
38897.5838 | 2157 | 7 | 8
38897.584 | 2025 | 6 | 8
38897.5841 | 2097 | 7 | 8
38897.5842 | 2398 | 10 | 8
38897.5843 | 2380 | 10 | 8
38897.5845 | 2183 | 8 | 8
38897.5846 | 2234 | 10 | 8
38897.5847 | 2243 | 11 | 8
38897.5848 | 2360 | 11 | 8
38897.585 | 2045 | 9 | 8
38897.5851 | 1927 | 10 | 8
38897.5852 | 2077 | 12 | 8
38897.5853 | 1871 | 12 | 8
38897.5855 | 2039 | 11 | 8
38897.5856 | 2144 | 13 | 8
38897.5857 | 2120 | 14 | 8
38897.5858 | 1879 | 14 | 8
38897.586 | 2105 | 17 | 8
38897.5861 | 1886 | 17 | 8
38897.5862 | 2350 | 23 | 8
38897.5863 | 1832 | 24 | 8
38897.5865 | 2129 | 30 | 8
38897.5866 | 1738 | 343 | 8
38897.5867 | 1804 | 82 | 8
38897.5868 | 2320 | 87 | 8
38897.587 | 1825 | 68 | 8
38897.5871 | 2013 | 76 | 8
38897.5872 | 2052 | 73 | 8
38897.5681 | 1 | 0 | 9
38897.5682 | 1 | 0 | 9
38897.5684 | 1 | 0 | 9
38897.5685 | 1 | 0 | 9
38897.5686 | 2 | 0 | 9
38897.5687 | 1 | 0 | 9
38897.5689 | 1 | 0 | 9
38897.569 | 1 | 0 | 9
38897.5691 | 1 | 0 | 9
38897.5692 | 1 | 0 | 9
38897.5694 | 1 | 0 | 9
38897.5695 | 1 | 0 | 9
38897.5696 | 1 | 0 | 9
38897.5697 | 1 | 0 | 9
38897.5699 | 1 | 0 | 9
38897.57 | 1 | 0 | 9
38897.5701 | 1 | 0 | 9
38897.5702 | 1 | 1 | 9
38897.5704 | 2 | 0 | 9
38897.5705 | 1 | 0 | 9
38897.5706 | 1 | 0 | 9
38897.5707 | 1 | 0 | 9
38897.5709 | 1 | 0 | 9
38897.571 | 1 | 0 | 9
38897.5711 | 1 | 0 | 9
38897.5712 | 1 | 0 | 9
38897.5714 | 1 | 0 | 9
38897.5715 | 1 | 0 | 9
38897.5716 | 1 | 0 | 9
38897.5717 | 1 | 1 | 9
38897.5719 | 1 | 0 | 9
38897.572 | 1 | 0 | 9
38897.5721 | 2 | 0 | 9
38897.5722 | 1 | 0 | 9
38897.5724 | 1 | 0 | 9
38897.5725 | 1 | 0 | 9
38897.5726 | 2 | 0 | 9
38897.5727 | 1 | 1 | 9
38897.5729 | 1 | 0 | 9
38897.573 | 1 | 0 | 9
38897.5731 | 1 | 0 | 9
38897.5732 | 1 | 0 | 9
38897.5734 | 1 | 0 | 9
38897.5735 | 1 | 0 | 9
38897.5736 | 1 | 0 | 9
38897.5737 | 1 | 0 | 9
38897.5739 | 1 | 0 | 9
38897.574 | 1 | 0 | 9
38897.5741 | 1 | 0 | 9
38897.5744 | 1 | 0 | 9
38897.5745 | 1 | 0 | 9
38897.5746 | 1 | 0 | 9
38897.5747 | 1 | 0 | 9
38897.5749 | 1 | 0 | 9
38897.575 | 1 | 0 | 9
38897.5751 | 1 | 0 | 9
38897.5752 | 1 | 1 | 9
38897.5754 | 1 | 0 | 9
38897.5755 | 1 | 0 | 9
38897.5756 | 1 | 0 | 9
38897.5757 | 1 | 0 | 9
38897.5759 | 1 | 0 | 9
38897.576 | 1 | 0 | 9
38897.5761 | 1 | 0 | 9
38897.5762 | 1 | 0 | 9
38897.5764 | 1 | 0 | 9
38897.5765 | 1 | 0 | 9
38897.5766 | 1 | 0 | 9
38897.5767 | 1 | 0 | 9
38897.5769 | 1 | 0 | 9
38897.577 | 1 | 0 | 9
38897.5771 | 1 | 0 | 9
38897.5772 | 1 | 0 | 9
38897.5774 | 1 | 0 | 9
38897.5775 | 1 | 0 | 9
38897.5776 | 1 | 0 | 9
38897.5777 | 1 | 0 | 9
38897.5779 | 1 | 0 | 9
38897.578 | 1 | 0 | 9
38897.5781 | 1 | 0 | 9
38897.5782 | 1 | 0 | 9
38897.5784 | 1 | 0 | 9
38897.5785 | 1 | 0 | 9
38897.5786 | 1 | 0 | 9
38897.5787 | 1 | 0 | 9
38897.5789 | 1 | 0 | 9
38897.579 | 1 | 0 | 9
38897.5791 | 1 | 0 | 9
38897.5792 | 1 | 5 | 9
38897.5794 | 2 | 11 | 9
38897.5795 | 68 | 53 | 9
38897.5796 | 153 | 112 | 9
38897.5797 | 255 | 219 | 9
38897.5799 | 404 | 373 | 9
38897.58 | 532 | 471 | 9
38897.5801 | 505 | 403 | 9
38897.5802 | 535 | 427 | 9
38897.5804 | 1254 | 825 | 9
38897.5805 | 1104 | 973 | 9
38897.5806 | 1054 | 843 | 9
38897.5807 | 1110 | 900 | 9
38897.5809 | 1118 | 847 | 9
38897.581 | 1203 | 731 | 9
38897.5812 | 1594 | 375 | 9
38897.5814 | 1491 | 499 | 9
38897.5815 | 1626 | 545 | 9
38897.5816 | 1479 | 488 | 9
38897.5817 | 1319 | 565 | 9
38897.5819 | 1811 | 142 | 9
38897.582 | 2275 | 20 | 9
38897.5821 | 2289 | 20 | 9
38897.5822 | 2087 | 15 | 9
38897.5824 | 2431 | 12 | 9
38897.5825 | 2339 | 9 | 9
38897.5826 | 2385 | 8 | 9
38897.5827 | 2022 | 5 | 9
38897.5829 | 2361 | 8 | 9
38897.583 | 2119 | 6 | 9
38897.5831 | 2084 | 7 | 9
38897.5832 | 2020 | 5 | 9
38897.5834 | 2429 | 8 | 9
38897.5835 | 2423 | 6 | 9
38897.5836 | 1907 | 5 | 9
38897.5837 | 1880 | 6 | 9
38897.5839 | 1874 | 7 | 9
38897.584 | 1867 | 7 | 9
38897.5841 | 2190 | 7 | 9
38897.5842 | 2085 | 7 | 9
38897.5844 | 2011 | 7 | 9
38897.5845 | 1872 | 8 | 9
38897.5846 | 2412 | 11 | 9
38897.5847 | 2024 | 10 | 9
38897.5849 | 1907 | 9 | 9
38897.585 | 2320 | 11 | 9
38897.5851 | 2168 | 12 | 9
38897.5852 | 2282 | 14 | 9
38897.5854 | 1936 | 11 | 9
38897.5855 | 1977 | 11 | 9
38897.5856 | 1893 | 12 | 9
38897.5857 | 2335 | 16 | 9
38897.5859 | 2200 | 18 | 9
38897.586 | 2257 | 21 | 9
38897.5861 | 1855 | 18 | 9
38897.5862 | 1868 | 22 | 9
38897.5864 | 2012 | 28 | 9
38897.5865 | 2277 | 35 | 9
38897.5866 | 1867 | 335 | 9
38897.5867 | 2277 | 100 | 9
38897.5869 | 2129 | 75 | 9
38897.587 | 1963 | 69 | 9
38897.5871 | 2221 | 76 | 9
38897.5872 | 2315 | 85 | 9
38897.5681 | 1 | 0 | 10
38897.5682 | 1 | 0 | 10
38897.5684 | 1 | 0 | 10
38897.5685 | 1 | 0 | 10
38897.5686 | 1 | 0 | 10
38897.5687 | 1 | 0 | 10
38897.5689 | 1 | 0 | 10
38897.569 | 1 | 0 | 10
38897.5691 | 2 | 0 | 10
38897.5692 | 1 | 0 | 10
38897.5694 | 1 | 0 | 10
38897.5695 | 1 | 0 | 10
38897.5696 | 2 | 0 | 10
38897.5697 | 1 | 0 | 10
38897.5699 | 1 | 0 | 10
38897.57 | 1 | 0 | 10
38897.5701 | 1 | 0 | 10
38897.5702 | 1 | 0 | 10
38897.5704 | 1 | 0 | 10
38897.5705 | 2 | 0 | 10
38897.5706 | 2 | 0 | 10
38897.5707 | 2 | 0 | 10
38897.5709 | 1 | 0 | 10
38897.571 | 1 | 0 | 10
38897.5711 | 1 | 0 | 10
38897.5712 | 1 | 0 | 10
38897.5714 | 1 | 0 | 10
38897.5715 | 1 | 0 | 10
38897.5716 | 1 | 0 | 10
38897.5717 | 1 | 0 | 10
38897.5719 | 1 | 0 | 10
38897.572 | 1 | 0 | 10
38897.5721 | 2 | 0 | 10
38897.5722 | 1 | 0 | 10
38897.5724 | 1 | 0 | 10
38897.5725 | 1 | 0 | 10
38897.5726 | 1 | 1 | 10
38897.5727 | 1 | 1 | 10
38897.5729 | 1 | 0 | 10
38897.573 | 2 | 0 | 10
38897.5731 | 1 | 0 | 10
38897.5732 | 1 | 0 | 10
38897.5734 | 1 | 0 | 10
38897.5735 | 1 | 0 | 10
38897.5736 | 1 | 0 | 10
38897.5737 | 2 | 0 | 10
38897.5739 | 1 | 0 | 10
38897.574 | 1 | 0 | 10
38897.5741 | 1 | 0 | 10
38897.5742 | 1 | 0 | 10
38897.5744 | 1 | 0 | 10
38897.5745 | 1 | 0 | 10
38897.5746 | 1 | 0 | 10
38897.5747 | 1 | 0 | 10
38897.5749 | 2 | 1 | 10
38897.575 | 1 | 0 | 10
38897.5751 | 1 | 0 | 10
38897.5752 | 1 | 0 | 10
38897.5754 | 1 | 0 | 10
38897.5755 | 1 | 0 | 10
38897.5756 | 1 | 0 | 10
38897.5757 | 2 | 0 | 10
38897.5759 | 2 | 0 | 10
38897.576 | 1 | 0 | 10
38897.5761 | 1 | 0 | 10
38897.5762 | 1 | 0 | 10
38897.5764 | 1 | 0 | 10
38897.5765 | 1 | 0 | 10
38897.5766 | 1 | 0 | 10
38897.5767 | 1 | 0 | 10
38897.5769 | 1 | 0 | 10
38897.577 | 1 | 0 | 10
38897.5771 | 1 | 0 | 10
38897.5772 | 1 | 0 | 10
38897.5774 | 1 | 0 | 10
38897.5775 | 1 | 0 | 10
38897.5776 | 1 | 0 | 10
38897.5777 | 1 | 0 | 10
38897.5779 | 1 | 0 | 10
38897.578 | 1 | 0 | 10
38897.5781 | 1 | 0 | 10
38897.5782 | 1 | 0 | 10
38897.5784 | 1 | 0 | 10
38897.5785 | 1 | 0 | 10
38897.5786 | 1 | 0 | 10
38897.5787 | 1 | 0 | 10
38897.5789 | 1 | 0 | 10
38897.579 | 1 | 0 | 10
38897.5791 | 1 | 0 | 10
38897.5792 | 2 | 3 | 10
38897.5794 | 14 | 5 | 10
38897.5795 | 143 | 40 | 10
38897.5796 | 286 | 138 | 10
38897.5797 | 392 | 224 | 10
38897.5799 | 443 | 322 | 10
38897.58 | 507 | 333 | 10
38897.5801 | 517 | 362 | 10
38897.5802 | 673 | 461 | 10
38897.5804 | 1125 | 1010 | 10
38897.5805 | 1015 | 820 | 10
38897.5806 | 1106 | 959 | 10
38897.5807 | 1228 | 993 | 10
38897.5809 | 1220 | 926 | 10
38897.581 | 1361 | 782 | 10
38897.5811 | 1957 | 461 | 10
38897.5812 | 1772 | 473 | 10
38897.5814 | 1692 | 666 | 10
38897.5815 | 1768 | 625 | 10
38897.5816 | 1378 | 543 | 10
38897.5817 | 1498 | 666 | 10
38897.5819 | 2180 | 48 | 10
38897.582 | 2055 | 17 | 10
38897.5821 | 1956 | 16 | 10
38897.5822 | 1989 | 13 | 10
38897.5824 | 1887 | 9 | 10
38897.5825 | 1992 | 6 | 10
38897.5826 | 1881 | 5 | 10
38897.5827 | 2370 | 8 | 10
38897.5829 | 2278 | 7 | 10
38897.583 | 1937 | 5 | 10
38897.5831 | 2236 | 7 | 10
38897.5832 | 2435 | 8 | 10
38897.5834 | 2029 | 5 | 10
38897.5835 | 1946 | 6 | 10
38897.5836 | 2274 | 7 | 10
38897.5837 | 1895 | 5 | 10
38897.5839 | 2130 | 8 | 10
38897.584 | 2243 | 8 | 10
38897.5841 | 1877 | 6 | 10
38897.5842 | 2276 | 10 | 10
38897.5844 | 2221 | 8 | 10
38897.5845 | 2049 | 9 | 10
38897.5846 | 2170 | 11 | 10
38897.5847 | 2146 | 11 | 10
38897.5849 | 2232 | 10 | 10
38897.585 | 2292 | 9 | 10
38897.5851 | 2394 | 15 | 10
38897.5852 | 1947 | 10 | 10
38897.5854 | 2300 | 14 | 10
38897.5855 | 2208 | 13 | 10
38897.5856 | 2252 | 14 | 10
38897.5857 | 1993 | 13 | 10
38897.5859 | 2391 | 17 | 10
38897.586 | 2400 | 22 | 10
38897.5861 | 2340 | 24 | 10
38897.5862 | 2393 | 28 | 10
38897.5864 | 2308 | 31 | 10
38897.5865 | 1918 | 28 | 10
38897.5866 | 2008 | 408 | 10
38897.5867 | 2150 | 98 | 10
38897.5869 | 2209 | 82 | 10
38897.587 | 1813 | 65 | 10
38897.5871 | 2292 | 85 | 10
38897.5872 | 1894 | 67 | 10
38897.5681 | 1 | 0 | 11
38897.5683 | 1 | 0 | 11
38897.5684 | 1 | 0 | 11
38897.5685 | 1 | 0 | 11
38897.5686 | 1 | 0 | 11
38897.5687 | 1 | 0 | 11
38897.5689 | 1 | 0 | 11
38897.569 | 1 | 0 | 11
38897.5691 | 1 | 0 | 11
38897.5692 | 1 | 0 | 11
38897.5694 | 1 | 0 | 11
38897.5695 | 1 | 0 | 11
38897.5696 | 2 | 0 | 11
38897.5698 | 1 | 0 | 11
38897.5699 | 1 | 0 | 11
38897.57 | 1 | 0 | 11
38897.5701 | 2 | 0 | 11
38897.5703 | 1 | 0 | 11
38897.5704 | 1 | 0 | 11
38897.5705 | 1 | 0 | 11
38897.5706 | 1 | 0 | 11
38897.5708 | 1 | 0 | 11
38897.5709 | 1 | 0 | 11
38897.571 | 1 | 0 | 11
38897.5711 | 1 | 0 | 11
38897.5713 | 1 | 0 | 11
38897.5714 | 1 | 0 | 11
38897.5715 | 1 | 0 | 11
38897.5716 | 1 | 1 | 11
38897.5717 | 1 | 0 | 11
38897.5719 | 1 | 0 | 11
38897.572 | 1 | 0 | 11
38897.5721 | 1 | 0 | 11
38897.5723 | 1 | 0 | 11
38897.5724 | 1 | 1 | 11
38897.5725 | 1 | 0 | 11
38897.5726 | 1 | 0 | 11
38897.5728 | 1 | 1 | 11
38897.5729 | 1 | 0 | 11
38897.573 | 1 | 0 | 11
38897.5731 | 1 | 0 | 11
38897.5733 | 1 | 0 | 11
38897.5734 | 1 | 0 | 11
38897.5735 | 1 | 0 | 11
38897.5736 | 1 | 0 | 11
38897.5738 | 1 | 0 | 11
38897.5739 | 2 | 0 | 11
38897.574 | 1 | 0 | 11
38897.5741 | 1 | 0 | 11
38897.5742 | 1 | 0 | 11
38897.5744 | 1 | 1 | 11
38897.5745 | 2 | 0 | 11
38897.5746 | 2 | 0 | 11
38897.5748 | 1 | 0 | 11
38897.5749 | 1 | 0 | 11
38897.575 | 1 | 0 | 11
38897.5751 | 1 | 0 | 11
38897.5753 | 1 | 0 | 11
38897.5754 | 1 | 0 | 11
38897.5755 | 1 | 0 | 11
38897.5756 | 1 | 0 | 11
38897.5758 | 1 | 0 | 11
38897.5759 | 1 | 0 | 11
38897.576 | 1 | 0 | 11
38897.5761 | 1 | 0 | 11
38897.5762 | 1 | 0 | 11
38897.5764 | 1 | 0 | 11
38897.5765 | 1 | 0 | 11
38897.5766 | 1 | 0 | 11
38897.5767 | 1 | 0 | 11
38897.5769 | 1 | 0 | 11
38897.577 | 1 | 0 | 11
38897.5771 | 1 | 1 | 11
38897.5773 | 1 | 0 | 11
38897.5774 | 1 | 0 | 11
38897.5775 | 1 | 0 | 11
38897.5776 | 1 | 0 | 11
38897.5778 | 1 | 0 | 11
38897.5779 | 1 | 0 | 11
38897.578 | 1 | 0 | 11
38897.5781 | 1 | 0 | 11
38897.5783 | 1 | 0 | 11
38897.5784 | 1 | 0 | 11
38897.5785 | 1 | 0 | 11
38897.5786 | 1 | 0 | 11
38897.5788 | 1 | 0 | 11
38897.5789 | 1 | 0 | 11
38897.579 | 1 | 0 | 11
38897.5791 | 1 | 0 | 11
38897.5792 | 1 | 2 | 11
38897.5794 | 42 | 29 | 11
38897.5795 | 78 | 56 | 11
38897.5796 | 174 | 120 | 11
38897.5798 | 653 | 543 | 11
38897.5799 | 1177 | 1028 | 11
38897.58 | 1061 | 899 | 11
38897.5801 | 1108 | 941 | 11
38897.5803 | 1176 | 998 | 11
38897.5804 | 1005 | 823 | 11
38897.5805 | 1203 | 992 | 11
38897.5806 | 1231 | 995 | 11
38897.5808 | 1174 | 888 | 11
38897.5809 | 947 | 730 | 11
38897.581 | 1299 | 764 | 11
38897.5811 | 1712 | 145 | 11
38897.5813 | 1930 | 555 | 11
38897.5814 | 1359 | 493 | 11
38897.5815 | 1342 | 498 | 11
38897.5816 | 1421 | 581 | 11
38897.5817 | 1246 | 658 | 11
38897.5819 | 2310 | 28 | 11
38897.582 | 2382 | 20 | 11
38897.5821 | 2055 | 16 | 11
38897.5823 | 2220 | 15 | 11
38897.5824 | 2173 | 12 | 11
38897.5825 | 2104 | 7 | 11
38897.5826 | 2047 | 6 | 11
38897.5828 | 1996 | 6 | 11
38897.5829 | 1928 | 5 | 11
38897.583 | 2150 | 6 | 11
38897.5831 | 2372 | 6 | 11
38897.5833 | 2371 | 5 | 11
38897.5834 | 2391 | 8 | 11
38897.5835 | 2117 | 6 | 11
38897.5836 | 1860 | 6 | 11
38897.5837 | 2135 | 7 | 11
38897.5839 | 1980 | 7 | 11
38897.584 | 2346 | 9 | 11
38897.5841 | 2107 | 8 | 11
38897.5842 | 2147 | 10 | 11
38897.5844 | 2404 | 9 | 11
38897.5845 | 2408 | 12 | 11
38897.5846 | 2379 | 10 | 11
38897.5848 | 2405 | 9 | 11
38897.5849 | 2370 | 11 | 11
38897.585 | 1844 | 12 | 11
38897.5851 | 2222 | 13 | 11
38897.5853 | 2075 | 12 | 11
38897.5854 | 2247 | 15 | 11
38897.5855 | 1855 | 13 | 11
38897.5856 | 2387 | 18 | 11
38897.5858 | 1975 | 16 | 11
38897.5859 | 2361 | 17 | 11
38897.586 | 1923 | 19 | 11
38897.5861 | 1857 | 20 | 11
38897.5863 | 1838 | 24 | 11
38897.5864 | 2050 | 31 | 11
38897.5865 | 1982 | 32 | 11
38897.5866 | 1821 | 461 | 11
38897.5867 | 2032 | 77 | 11
38897.5869 | 1859 | 68 | 11
38897.587 | 2096 | 75 | 11
38897.5871 | 1804 | 65 | 11
38897.5872 | 2127 | 78 | 11
38897.5681 | 1 | 0 | 12
38897.5683 | 1 | 0 | 12
38897.5684 | 1 | 0 | 12
38897.5685 | 1 | 0 | 12
38897.5686 | 1 | 0 | 12
38897.5688 | 1 | 0 | 12
38897.5689 | 1 | 0 | 12
38897.569 | 1 | 0 | 12
38897.5691 | 1 | 0 | 12
38897.5693 | 1 | 0 | 12
38897.5694 | 1 | 0 | 12
38897.5695 | 1 | 0 | 12
38897.5696 | 2 | 0 | 12
38897.5698 | 1 | 0 | 12
38897.5699 | 1 | 0 | 12
38897.57 | 1 | 0 | 12
38897.5701 | 1 | 0 | 12
38897.5703 | 1 | 0 | 12
38897.5704 | 1 | 0 | 12
38897.5705 | 1 | 0 | 12
38897.5706 | 1 | 0 | 12
38897.5708 | 1 | 0 | 12
38897.5709 | 1 | 0 | 12
38897.571 | 1 | 0 | 12
38897.5711 | 1 | 0 | 12
38897.5713 | 1 | 0 | 12
38897.5714 | 1 | 0 | 12
38897.5715 | 1 | 0 | 12
38897.5716 | 1 | 0 | 12
38897.5718 | 1 | 0 | 12
38897.5719 | 1 | 0 | 12
38897.572 | 1 | 0 | 12
38897.5721 | 1 | 0 | 12
38897.5723 | 1 | 0 | 12
38897.5724 | 1 | 0 | 12
38897.5725 | 2 | 0 | 12
38897.5726 | 1 | 0 | 12
38897.5728 | 1 | 0 | 12
38897.5729 | 1 | 0 | 12
38897.573 | 1 | 0 | 12
38897.5731 | 1 | 0 | 12
38897.5733 | 1 | 0 | 12
38897.5734 | 1 | 0 | 12
38897.5735 | 1 | 0 | 12
38897.5736 | 1 | 0 | 12
38897.5738 | 1 | 0 | 12
38897.5739 | 1 | 0 | 12
38897.574 | 1 | 0 | 12
38897.5741 | 1 | 0 | 12
38897.5743 | 1 | 0 | 12
38897.5744 | 1 | 0 | 12
38897.5745 | 1 | 0 | 12
38897.5746 | 1 | 0 | 12
38897.5748 | 1 | 0 | 12
38897.5749 | 1 | 0 | 12
38897.575 | 1 | 0 | 12
38897.5751 | 1 | 0 | 12
38897.5753 | 1 | 0 | 12
38897.5754 | 1 | 0 | 12
38897.5755 | 1 | 0 | 12
38897.5756 | 1 | 0 | 12
38897.5758 | 1 | 0 | 12
38897.5759 | 1 | 0 | 12
38897.576 | 1 | 0 | 12
38897.5761 | 1 | 0 | 12
38897.5763 | 1 | 0 | 12
38897.5764 | 2 | 0 | 12
38897.5765 | 1 | 0 | 12
38897.5766 | 1 | 0 | 12
38897.5768 | 1 | 0 | 12
38897.5769 | 1 | 0 | 12
38897.577 | 2 | 0 | 12
38897.5771 | 1 | 0 | 12
38897.5773 | 1 | 0 | 12
38897.5774 | 1 | 0 | 12
38897.5775 | 2 | 0 | 12
38897.5776 | 1 | 0 | 12
38897.5778 | 1 | 0 | 12
38897.5779 | 1 | 0 | 12
38897.578 | 1 | 0 | 12
38897.5781 | 1 | 0 | 12
38897.5783 | 1 | 0 | 12
38897.5784 | 1 | 0 | 12
38897.5785 | 1 | 0 | 12
38897.5786 | 1 | 0 | 12
38897.5788 | 1 | 0 | 12
38897.5789 | 1 | 0 | 12
38897.579 | 1 | 0 | 12
38897.5791 | 1 | 0 | 12
38897.5793 | 2 | 1 | 12
38897.5794 | 107 | 18 | 12
38897.5795 | 169 | 45 | 12
38897.5796 | 291 | 148 | 12
38897.5798 | 316 | 206 | 12
38897.5799 | 956 | 795 | 12
38897.58 | 964 | 801 | 12
38897.5801 | 1227 | 1033 | 12
38897.5803 | 1106 | 923 | 12
38897.5804 | 1060 | 867 | 12
38897.5805 | 1256 | 1096 | 12
38897.5806 | 1007 | 870 | 12
38897.5808 | 1301 | 1027 | 12
38897.5809 | 982 | 668 | 12
38897.581 | 1389 | 876 | 12
38897.5811 | 1973 | 130 | 12
38897.5813 | 1847 | 657 | 12
38897.5814 | 1738 | 506 | 12
38897.5815 | 1697 | 608 | 12
38897.5816 | 1461 | 594 | 12
38897.5818 | 1278 | 570 | 12
38897.5819 | 2042 | 20 | 12
38897.582 | 2149 | 19 | 12
38897.5821 | 1968 | 15 | 12
38897.5823 | 2298 | 16 | 12
38897.5824 | 2380 | 11 | 12
38897.5825 | 2440 | 9 | 12
38897.5826 | 2211 | 7 | 12
38897.5828 | 2410 | 8 | 12
38897.5829 | 2430 | 6 | 12
38897.583 | 2298 | 8 | 12
38897.5831 | 2386 | 9 | 12
38897.5833 | 2013 | 6 | 12
38897.5834 | 1909 | 6 | 12
38897.5835 | 2042 | 7 | 12
38897.5836 | 2436 | 8 | 12
38897.5838 | 1980 | 6 | 12
38897.5839 | 2350 | 9 | 12
38897.584 | 2233 | 8 | 12
38897.5841 | 2259 | 10 | 12
38897.5843 | 2033 | 8 | 12
38897.5844 | 2016 | 10 | 12
38897.5845 | 2252 | 10 | 12
38897.5846 | 1961 | 8 | 12
38897.5848 | 2336 | 12 | 12
38897.5849 | 1921 | 10 | 12
38897.585 | 2245 | 14 | 12
38897.5851 | 2421 | 15 | 12
38897.5853 | 1896 | 12 | 12
38897.5854 | 2054 | 13 | 12
38897.5855 | 1914 | 13 | 12
38897.5856 | 2011 | 15 | 12
38897.5858 | 2221 | 20 | 12
38897.5859 | 2293 | 16 | 12
38897.586 | 2226 | 22 | 12
38897.5861 | 2185 | 26 | 12
38897.5863 | 2024 | 26 | 12
38897.5864 | 2278 | 33 | 12
38897.5865 | 2094 | 40 | 12
38897.5866 | 1643 | 478 | 12
38897.5868 | 2222 | 80 | 12
38897.5869 | 2305 | 85 | 12
38897.587 | 2253 | 80 | 12
38897.5871 | 2284 | 78 | 12
38897.5873 | 2322 | 70 | 12

## Test Facts
Last row in IRMS data sheets: | 159
Time when Penlight power was initiated: | 184s
Conduit dimensions/material: | OD = 2 - 7/8" (2.875") (73.0 mm)
ID = 2-1/2" (2.5") (63 mm)
wall thickness = 3/16" (0.1875") (4.76 mm)
Material = Hot-dipped galvinized steel standard rigid metal conduit
Length = 5' (1524 mm)