## Test Facts
Last Row in IR Data sets: | 119
Power On | 104

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 64
Test conditions: Cable: 2-conductor plus shield and drain wire, 16AWG, XLPE insulated, CSPE (Hypalon) jacketed, Rockbestos Firewall III instrument cable (Cable Item #7). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. One thermocouple was attached to the inner surface of the center tray rung. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using three channels - one for each insulated conductor and a third for the un-insulated shield drain wire (the drain was treated as a third conductor and was not grounded), however the cable tray was grounded. Thermal response monitoring: Shroud temperature and one cable temperature (see maps). Shroud power: Initiated after 104 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
104 | 0 | Initiate Penlight Heating
322 | 218 | Cables ignite and burn
342 | 238 | Power to Penlight shutoff
452-455 | 348-351 | Conductor 2 shorts to Conductor 1 & the Shield (conductor 3) at less than 100 ohms (5 & 11) | First indication of failure is by conductor-conductor shorting
456-457 | 352-353 | Conductors 1 & 2 both short to ground intermittently at less than 100 ohms (30 & 37) | Intermittent shorting of cable signal conductors to ground
458 | 354 | Conductor 1 shorts to the Shield at less than 100 ohms (8) | All conductors have shorted together
459 | 355 | The Shield (conductor 3) shorts to ground intermittently at less than 1000 ohms (377) | All conductors have shorted to ground intermittently
Additional Observations
Observation 1 | Note: For an instrument cable of this type, the Shield wire would normally be grounded. Using the IRMS system, the Shield was treated as a third conductor independent of the external ground (the tray).
Observation 2 | Ignition of the cables occurred at 218 seconds (3.6 min.) after the start of heating.
Observation 3 | The initial shorting faults occurred between the insulated conductors and the Shield, and occurred 348 seconds (5.8 min.) after start of heating. The initial faults to ground occurred 352 seconds (5.9 min.) after start of heating.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Cable = XLPE/CSPE, 2-C with Shield (Cable Item #7)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | "Cable" | Within cable just below cable jacket, center position

## C-C
Conductor to Conductor Resistances
Penlight Test 64 |  |  | 2006-08-29 | 9:46
XLPE | 2-C & Shield | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C2-3 | Penlight Time | Minimums
-103 | 211201.9994 | -100.5 | 211201.9994 | -97.5 | 211201.9994 | -103 | 211201.9994
-94.5 | 211201.9994 | -92 | 211201.9994 | -89 | 211201.9994 | -94.5 | 211201.9994
-86.5 | 211201.9994 | -83.5 | 211201.9994 | -80.5 | 211201.9994 | -86.5 | 211201.9994
-78 | 211201.9994 | -75 | 211201.9994 | -72.5 | 211201.9994 | -78 | 211201.9994
-69.5 | 211201.9994 | -66.5 | 211201.9994 | -64 | 211201.9994 | -69.5 | 211201.9994
-61 | 211201.9994 | -58.5 | 211201.9994 | -55.5 | 211201.9994 | -61 | 211201.9994
-52.5 | 211201.9994 | -50 | 211201.9994 | -47 | 211201.9994 | -52.5 | 211201.9994
-44.5 | 211201.9994 | -41.5 | 211201.9994 | -38.5 | 211201.9994 | -44.5 | 211201.9994
-36 | 211201.9994 | -33 | 211201.9994 | -30.5 | 211201.9994 | -36 | 211201.9994
-27.5 | 211201.9994 | -24.5 | 211201.9994 | -22 | 211201.9994 | -27.5 | 211201.9994
-19 | 211201.9994 | -16.5 | 211201.9994 | -13.5 | 211201.9994 | -19 | 211201.9994
-10.5 | 211201.9994 | -8 | 211201.9994 | -5 | 211201.9994 | -10.5 | 211201.9994
-2.5 | 211201.9994 | 0.5 | 211201.9994 | 3.5 | 211201.9994 | -2.5 | 211201.9994
6 | 211201.9994 | 9 | 211201.9994 | 11.5 | 211201.9994 | 6 | 211201.9994
14.5 | 211201.9994 | 17.5 | 211201.9994 | 20 | 211201.9994 | 14.5 | 211201.9994
23 | 211201.9994 | 25.5 | 211201.9994 | 28.5 | 211201.9994 | 23 | 211201.9994
31.5 | 211201.9994 | 34 | 211201.9994 | 37 | 211201.9994 | 31.5 | 211201.9994
39.5 | 211201.9994 | 42.5 | 211201.9994 | 45.5 | 211201.9994 | 39.5 | 211201.9994
48.5 | 211201.9994 | 51 | 211201.9994 | 53.5 | 211201.9994 | 48.5 | 211201.9994
56.5 | 211201.9994 | 59.5 | 211201.9994 | 62 | 211201.9994 | 56.5 | 211201.9994
65 | 211201.9994 | 67.5 | 211201.9994 | 70.5 | 211201.9994 | 65 | 211201.9994
73.5 | 211201.9994 | 76 | 211201.9994 | 79 | 211201.9994 | 73.5 | 211201.9994
81.5 | 211201.9994 | 84.5 | 211201.9994 | 87.5 | 211201.9994 | 81.5 | 211201.9994
90 | 211201.9994 | 93 | 211201.9994 | 95.5 | 211201.9994 | 90 | 211201.9994
98.5 | 211201.9994 | 101.5 | 211201.9994 | 104 | 211201.9994 | 98.5 | 211201.9994
107 | 211201.9994 | 109.5 | 211201.9994 | 112.5 | 211201.9994 | 107 | 211201.9994
115.5 | 211201.9994 | 118 | 211201.9994 | 121 | 211201.9994 | 115.5 | 211201.9994
123.5 | 105550.9988 | 126.5 | 211201.9994 | 129.5 | 211201.9994 | 123.5 | 105550.9988
132 | 211201.9994 | 135 | 211201.9994 | 137.5 | 211201.9994 | 132 | 211201.9994
140.5 | 211201.9994 | 143.5 | 211201.9994 | 146 | 211201.9994 | 140.5 | 211201.9994
149 | 211201.9994 | 151.5 | 211201.9994 | 154.5 | 211201.9994 | 149 | 211201.9994
157.5 | 211201.9994 | 160 | 211201.9994 | 163 | 211201.9994 | 157.5 | 211201.9994
165.5 | 211201.9994 | 168.5 | 211201.9994 | 171.5 | 211201.9994 | 165.5 | 211201.9994
174 | 211201.9994 | 177 | 211201.9994 | 179.5 | 211201.9994 | 174 | 211201.9994
182.5 | 211201.9994 | 185.5 | 211201.9994 | 188 | 211201.9994 | 182.5 | 211201.9994
191 | 211201.9994 | 193.5 | 211201.9994 | 196.5 | 211201.9994 | 191 | 211201.9994
199.5 | 211201.9994 | 202 | 211201.9994 | 205 | 211201.9994 | 199.5 | 211201.9994
207.5 | 211201.9994 | 210.5 | 211201.9994 | 213.5 | 211201.9994 | 207.5 | 211201.9994
216 | 211201.9994 | 219 | 211201.9994 | 221.5 | 211201.9994 | 216 | 211201.9994
224.5 | 211201.9994 | 227.5 | 211201.9994 | 230 | 211201.9994 | 224.5 | 211201.9994
233 | 211201.9994 | 235.5 | 211201.9994 | 238.5 | 211201.9994 | 233 | 211201.9994
241.5 | 211201.9994 | 244 | 211201.9994 | 247 | 211201.9994 | 241.5 | 211201.9994
249.5 | 211201.9994 | 252.5 | 211201.9994 | 255.5 | 211201.9994 | 249.5 | 211201.9994
258 | 211201.9994 | 261 | 211201.9994 | 263.5 | 211201.9994 | 258 | 211201.9994
266.5 | 211201.9994 | 269.5 | 211201.9994 | 272 | 211201.9994 | 266.5 | 211201.9994
275 | 211201.9994 | 277.5 | 211201.9994 | 280.5 | 211201.9994 | 275 | 211201.9994
283.5 | 211201.9994 | 286 | 211201.9994 | 289 | 211201.9994 | 283.5 | 211201.9994
291.5 | 211201.9994 | 294.5 | 211201.9994 | 297.5 | 211201.9994 | 291.5 | 211201.9994
300 | 211201.9994 | 303 | 211201.9994 | 305.5 | 211201.9994 | 300 | 211201.9994
308.5 | 211201.9994 | 311.5 | 211201.9994 | 314 | 211201.9994 | 308.5 | 211201.9994
317 | 211201.9994 | 319.5 | 211201.9994 | 322.5 | 211201.9994 | 317 | 211201.9994
325 | 211201.9994 | 328 | 211201.9994 | 331 | 211201.9994 | 325 | 211201.9994
333.5 | 211201.9994 | 336.5 | 35000.428 | 339.5 | 211201.9994 | 333.5 | 35000.428
342 | 4940.024 | 345 | 1010.693 | 347.5 | 11.282 | 342 | 11.282
350.5 | 4.582 | 353.5 | 8.4328 | 356 | 20.168 | 350.5 | 4.582
359 | 9.3841 | 361.5 | 28.3207 | 364.5 | 9.288 | 359 | 9.288
367.5 | 4.1472 | 370 | 9.0289 | 373 | 10.1007 | 367.5 | 4.1472
375.5 | 11.6319 | 378.5 | 6.8656 | 381.5 | 12.7116 | 375.5 | 6.8656
384 | 20.4174 | 387 | 9.624 | 389.5 | 3.4992 | 384 | 3.4992
392.5 | 3.4651 | 395.5 | 8.589 | 398 | 1.2574 | 392.5 | 1.2574
401 | 5.2818 | 403.5 | 24.3748 | 406.5 | 2.7972 | 401 | 2.7972
409 | 14.9163 | 412 | 9.4714 | 415 | 14.9074 | 409 | 9.4714
417.5 | 12.9179 | 420.5 | 17.2437 | 423.5 | 19.7374 | 417.5 | 12.9179
426 | 9.91 | 429 | 11.1025 | 431.5 | 20.6878 | 426 | 9.91
434.5 | 3.2452 | 437.5 | 16.539 | 440 | 11.1447 | 434.5 | 3.2452
443 | 21.7396 | 445.5 | 24.6603 | 448.5 | 16.8454 | 443 | 16.8454
451.5 | 4.3766 | 454 | 24.3636 | 456.5 | 21.7709 | 451.5 | 4.3766
459.5 | 8.5205 | 462.5 | 14.4627 | 465 | 10.6445 | 459.5 | 8.5205
468.5 | 0.43914 | 470.5 | 19.7489 | 473.5 | 11.6788 | 468.5 | 0.43914
476.5 | 15.8422 | 479 | 5.7838 | 482 | 21.1456 | 476.5 | 5.7838
484.5 | 6.6166 | 487.5 | 19.5246 | 490.5 | 4.7342 | 484.5 | 4.7342
493 | 22.7749 | 496 | 12.3585 | 499 | 13.8766 | 493 | 12.3585
501.5 | 2.0969 | 504.5 | 1.7856 | 507.5 | 3.4113 | 501.5 | 1.7856
510 | 14.6839 | 513 | 18.9754 | 515.5 | 0.42817 | 510 | 0.42817
518.5 | 4.7717 | 521.5 | 20.2781 | 524 | 6.5172 | 518.5 | 4.7717
526 | 19.1744 | 529.5 | 0.17513 | 532.5 | 11.5965 | 526 | 0.17513
535.5 | 16.593 | 538 | 20.0507 | 541 | 2.399 | 535.5 | 2.399
543.5 | 9.6243 | 546.5 | 10.0848 | 549.5 | 0.082637 | 543.5 | 0.082637
552 | 11.6421 | 555 | 25.3786 | 557.5 | 2.9262 | 552 | 2.9262
560.5 | 0.00071127 | 563 | 17.5099 | 566 | 4.1444 | 560.5 | 0.00071127
568.5 | 17.7794 | 571.5 | 14.3944 | 574.5 | 28.6147 | 568.5 | 14.3944
577 | 8.3661 | 580 | 12.6483 | 583 | 6.225 | 577 | 6.225
585.5 | 10.8325 | 588.5 | 8.6648 | 591 | 21.8747 | 585.5 | 8.6648
594 | 19.1025 | 597 | 26.7996 | 599.5 | 10.6787 | 594 | 10.6787
602.5 | 4.5739 | 605.5 | 11.9928 | 608 | 20.4682 | 602.5 | 4.5739
611 | 2.1022 | 613.5 | 16.8166 | 616.5 | 18.0431 | 611 | 2.1022
619.5 | 16.9959 | 622 | 12.1196 | 625 | 10.8611 | 619.5 | 10.8611
627.5 | 19.5834 | 630.5 | 18.2492 | 633.5 | 6.9928 | 627.5 | 6.9928
636 | 17.3091 | 638.5 | 20.5325 | 641.5 | 1.6987 | 636 | 1.6987
644.5 | 19.2929 | 647.5 | 13.3993 | 650 | 1.6496 | 644.5 | 1.6496
652.5 | 2.6021 | 655.5 | 16.5059 | 658.5 | 27.8342 | 652.5 | 2.6021
661 | 8.3348 | 664 | 8.0787 | 666.5 | 9.5964 | 661 | 8.0787
669.5 | 5.5893 | 672.5 | 17.3242 | 675 | 7.1515 | 669.5 | 5.5893
678 | 6.7463 | 680.5 | 19.6334 | 683.5 | 3.5547 | 678 | 3.5547
686.5 | 9.3641 | 689.5 | 8.3823 | 692 | 30.4874 | 686.5 | 8.3823
695 | 5.6545 | 697.5 | 14.3658 | 700.5 | 17.8385 | 695 | 5.6545
703 | 19.2238 | 706 | 0.051189 | 709 | 10.4849 | 703 | 0.051189
711.5 | 32.4037 | 714.5 | 19.1946 | 717 | 18.4065 | 711.5 | 18.4065
720 | 0.38319 | 722.5 | 18.9425 | 725.5 | 10.8989 | 720 | 0.38319
728.5 | 2.397 | 731 | 1.5224 | 734 | 7.1124 | 728.5 | 1.5224
737 | 19.1732 | 739.5 | 0.46863 | 742.5 | 4.8831 | 737 | 0.46863
745.5 | 16.144 | 748 | 21.9956 | 751 | 14.6918 | 745.5 | 14.6918
753.5 | 11.7306 | 756.5 | 8.2185 | 759 | 11.7741 | 753.5 | 8.2185
762 | 33.415 | 764.5 | 1.1618 | 767.5 | 12.3927 | 762 | 1.1618
770.5 | 13.8884 | 773 | 5.5457 | 776 | 2.4956 | 770.5 | 2.4956
779 | 9.81 | 781.5 | 9.6283 | 784.5 | 20.9273 | 779 | 9.6283
787.5 | 20.2726 | 790 | 0.17929 | 793 | 5.4662 | 787.5 | 0.17929
795.5 | 12.3437 | 798.5 | 8.6118 | 801 | 0.6335 | 795.5 | 0.6335
804 | 2.5703 | 806.5 | 22.5931 | 809.5 | 6.1317 | 804 | 2.5703
812.5 | 18.3634 | 815 | 11.0465 | 818 | 20.6126 | 812.5 | 11.0465
821 | 14.0031 | 823.5 | 16.2333 | 826.5 | 23.5185 | 821 | 14.0031
829 | 14.838 | 832 | 9.3432 | 834.5 | 12.1542 | 829 | 9.3432
837.5 | 11.6099 | 840.5 | 0.76156 | 843 | 27.9925 | 837.5 | 0.76156
846 | 1.0682 | 848.5 | 12.1438 | 851.5 | 10.906 | 846 | 1.0682

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 64 |  |  | 2006-08-29 | 9:46
XLPE | 2-C & Shield | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | Minimums
-101.75 | 211202 |  | -100.25 | 211202 | -99 | 211202 | -101.75 | 211202
-93.25 | 211202 |  | -91.75 | 211202 | -90.5 | 211202 | -93.25 | 211202
-85 | 211202 |  | -83.5 | 211202 | -82 | 211202 | -85 | 211202
-76.5 | 211202 |  | -75.25 | 211202 | -73.75 | 211202 | -76.5 | 211202
-68 | 211202 |  | -66.75 | 211202 | -65.25 | 211202 | -68 | 211202
-59.75 | 211202 |  | -58.25 | 211202 | -57 | 211202 | -59.75 | 211202
-51.25 | 211202 |  | -49.75 | 211202 | -48.5 | 211202 | -51.25 | 211202
-43 | 211202 |  | -41.5 | 211202 | -40 | 211202 | -43 | 211202
-34.5 | 211202 |  | -33.25 | 211202 | -31.75 | 211202 | -34.5 | 211202
-26 | 211202 |  | -24.75 | 211202 | -23.25 | 211202 | -26 | 211202
-17.75 | 211202 |  | -16.25 | 211202 | -15 | 211202 | -17.75 | 211202
-9.25 | 211202 |  | -7.75 | 211202 | -6.5 | 211202 | -9.25 | 211202
-1 | 211202 |  | 0.5 | 211202 | 2 | 211202 | -1 | 211202
7.5 | 211202 |  | 8.75 | 211202 | 10.25 | 211202 | 7.5 | 211202
16 | 211202 |  | 17.25 | 211202 | 18.75 | 211202 | 16 | 211202
24.25 | 211202 |  | 25.75 | 211202 | 27 | 211202 | 24.25 | 211202
32.75 | 211202 |  | 34.25 | 211202 | 35.5 | 211202 | 32.75 | 211202
41 | 211202 |  | 42.5 | 211202 | 44 | 211202 | 41 | 211202
49.75 | 211202 |  | 51 | 211202 | 52.25 | 211202 | 49.75 | 211202
58 | 211202 |  | 59.25 | 211202 | 60.75 | 211202 | 58 | 211202
66.25 | 211202 |  | 67.75 | 211202 | 69 | 211202 | 66.25 | 211202
74.75 | 211202 |  | 76.25 | 211202 | 77.5 | 211202 | 74.75 | 211202
83 | 211202 |  | 84.5 | 211202 | 86 | 211202 | 83 | 211202
91.5 | 211202 |  | 92.75 | 211202 | 94.25 | 211202 | 91.5 | 211202
100 | 211202 |  | 101.25 | 211202 | 102.75 | 211202 | 100 | 211202
108.25 | 211202 |  | 109.75 | 211202 | 111 | 211202 | 108.25 | 211202
116.75 | 211202 |  | 118.25 | 211202 | 119.5 | 211202 | 116.75 | 211202
125 | 105551 |  | 126.5 | 211202 | 128 | 211202 | 125 | 105551
133.5 | 211202 |  | 134.75 | 211202 | 136.25 | 211202 | 133.5 | 211202
142 | 211202 |  | 143.25 | 211202 | 144.75 | 211202 | 142 | 211202
150.25 | 211202 |  | 151.75 | 211202 | 153 | 211202 | 150.25 | 211202
158.75 | 211202 |  | 160.25 | 211202 | 161.5 | 211202 | 158.75 | 211202
167 | 211202 |  | 168.5 | 211202 | 170 | 211202 | 167 | 211202
175.5 | 211202 |  | 176.75 | 211202 | 178.25 | 211202 | 175.5 | 211202
184 | 211202 |  | 185.25 | 211202 | 186.75 | 211202 | 184 | 211202
192.25 | 211202 |  | 193.75 | 211202 | 195 | 211202 | 192.25 | 211202
200.75 | 211202 |  | 202.25 | 211202 | 203.5 | 211202 | 200.75 | 211202
209 | 211202 |  | 210.5 | 211202 | 212 | 211202 | 209 | 211202
217.5 | 211202 |  | 218.75 | 211202 | 220.25 | 211202 | 217.5 | 211202
226 | 211202 |  | 227.25 | 211202 | 228.75 | 211202 | 226 | 211202
234.25 | 211202 |  | 235.75 | 211202 | 237 | 211202 | 234.25 | 211202
242.75 | 211202 |  | 244.25 | 211202 | 245.5 | 211202 | 242.75 | 211202
251 | 211202 |  | 252.5 | 211202 | 254 | 211202 | 251 | 211202
259.5 | 211202 |  | 260.75 | 211202 | 262.25 | 211202 | 259.5 | 211202
268 | 211202 |  | 269.25 | 211202 | 270.75 | 211202 | 268 | 211202
276.25 | 211202 |  | 277.75 | 211202 | 279 | 211202 | 276.25 | 211202
284.75 | 211202 |  | 286.25 | 211202 | 287.5 | 211202 | 284.75 | 211202
293 | 211202 |  | 294.5 | 211202 | 296 | 211202 | 293 | 211202
301.5 | 211202 |  | 302.75 | 211202 | 304.25 | 211202 | 301.5 | 211202
310 | 211202 |  | 311.25 | 211202 | 312.75 | 211202 | 310 | 211202
318.25 | 211202 |  | 319.75 | 211202 | 321 | 211202 | 318.25 | 211202
326.5 | 211202 |  | 328 | 211202 | 329.5 | 211202 | 326.5 | 211202
335 | 211202 |  | 336.5 | 211202 | 338 | 105551 | 335 | 105551
343.5 | 14324.1959 |  | 344.75 | 2408.5838 | 346.25 | 1420.7641 | 343.5 | 1420.7641
352 | 30.362 |  | 353.25 | 37.2787 | 354.75 | 376.6188 | 352 | 30.362
360.25 | 2242.4401 |  | 361.75 | 5354.4315 | 363 | 6943.4 | 360.25 | 2242.4401
368.75 | 399.4921 |  | 370.25 | 426.2739 | 371.5 | 1371.2523 | 368.75 | 399.4921
377 | 594.5399 |  | 378.5 | 450.7272 | 380 | 685.6537 | 377 | 450.7272
385.5 | 463.2707 |  | 386.75 | 418.2076 | 388.25 | 16784.6186 | 385.5 | 418.2076
394 | 27.8137 |  | 395.25 | 33.4731 | 396.75 | 427.4753 | 394 | 27.8137
402.25 | 24.8359 |  | 403.75 | 31.9109 | 405 | 3313.7742 | 402.25 | 24.8359
410.5 | 245.5895 |  | 412 | 334.7152 | 413.5 | 2718.1837 | 410.5 | 245.5895
419 | 1460.9196 |  | 420.5 | 1307.6829 | 422 | 1803.7872 | 419 | 1307.6829
427.5 | 1385.5093 |  | 428.75 | 824.8771 | 430.25 | 1401.6752 | 427.5 | 824.8771
436 | 2042.0474 |  | 437.25 | 2454.573 | 438.75 | 6397.4387 | 436 | 2042.0474
444.25 | 827.5582 |  | 445.75 | 335.9222 | 447 | 459.2671 | 444.25 | 335.9222
452.75 | 357.0728 |  | 454 | 400.5672 | 455.25 | 2757.8241 | 452.75 | 357.0728
461 | 174.8236 |  | 462.25 | 216.9707 | 463.75 | 2424.5834 | 461 | 174.8236
469.5 | 20.279 |  | 471 | 19.9184 | 472 | 2279.5607 | 469.5 | 19.9184
477.75 | 41.2536 |  | 479.25 | 509.3894 | 480.5 | 34.1614 | 477.75 | 34.1614
486 | 563.1795 |  | 487.5 | 68.7498 | 489 | 65.8651 | 486 | 65.8651
494.5 | 612.1297 |  | 496 | 397.1601 | 497.5 | 347.786 | 494.5 | 347.786
503 | 11.6928 |  | 504.5 | 9.4147 | 506 | 112.3878 | 503 | 9.4147
511.5 | 4211.6594 |  | 512.75 | 76.3458 | 514.25 | 98.9582 | 511.5 | 76.3458
520 | 78.3945 |  | 521.25 | 84.9487 | 522.75 | 2792.471 | 520 | 78.3945
527.75 | 5.5628 |  | 529.25 | 150.1066 | 531 | 5.3853 | 527.75 | 5.3853
536.75 | 470.5348 |  | 538.25 | 474.8771 | 539.5 | 1951.0629 | 536.75 | 470.5348
545 | 195.9504 |  | 546.5 | 4.328 | 548 | 4.4702 | 545 | 4.328
553.5 | 138.9798 |  | 554.75 | 16.9969 | 556.25 | 13.7791 | 553.5 | 13.7791
561.75 | 0.21969 |  | 563.25 | 0.22055 | 564.5 | 134.6433 | 561.75 | 0.21969
570 | 304.2958 |  | 571.5 | 1206.7338 | 573 | 439.9748 | 570 | 304.2958
578.5 | 135.0693 |  | 580 | 1636.3033 | 581.5 | 183.0073 | 578.5 | 135.0693
587 | 687.1871 |  | 588.25 | 960.0303 | 589.75 | 3832.7669 | 587 | 687.1871
595.5 | 1115.2594 |  | 596.75 | 1633.3706 | 598.25 | 2279.3555 | 595.5 | 1115.2594
604 | 487.5287 |  | 605.25 | 562.9692 | 606.75 | 3944.1704 | 604 | 487.5287
612.25 | 617.2547 |  | 613.75 | 1956.4622 | 615 | 1139.6487 | 612.25 | 617.2547
620.75 | 248.4816 |  | 622.25 | 5454.1289 | 623.5 | 293.1733 | 620.75 | 248.4816
629 | 906.2659 |  | 630.5 | 1426.3222 | 632 | 3098.9285 | 629 | 906.2659
637.25 | 516.6119 |  | 638.75 | 105.7896 | 640 | 108.6036 | 637.25 | 105.7896
646 | 222.9108 |  | 647.25 | 1132.4483 | 648.75 | 288.6833 | 646 | 222.9108
654 | 274.7293 |  | 655.5 | 305.571 | 657 | 431.6515 | 654 | 274.7293
662.5 | 70.8439 |  | 663.75 | 499.8415 | 665.25 | 88.0696 | 662.5 | 70.8439
671 | 92.9955 |  | 672.25 | 90.3982 | 673.75 | 3658.9844 | 671 | 90.3982
679.25 | 332.8762 |  | 680.75 | 44.4703 | 682 | 50.5824 | 679.25 | 44.4703
688 | 605.6275 |  | 689.25 | 1200.6317 | 690.75 | 3188.1934 | 688 | 605.6275
696.25 | 286.224 |  | 697.75 | 463.233 | 699 | 393.2751 | 696.25 | 286.224
704.5 | 0.19063 |  | 706 | 92.9349 | 707.5 | 0.24195 | 704.5 | 0.19063
713 | 1206.6872 |  | 714.25 | 1428.3906 | 715.75 | 1610.5594 | 713 | 1206.6872
721.25 | 258.3599 |  | 722.75 | 261.5045 | 724 | 224.9098 | 721.25 | 224.9098
729.75 | 344.8774 |  | 731.25 | 159.8759 | 732.5 | 232.6241 | 729.75 | 159.8759
738.25 | 88.5412 |  | 739.75 | 112.2955 | 741 | 116.8004 | 738.25 | 88.5412
746.75 | 1904.6357 |  | 748.25 | 180.353 | 749.5 | 155.5592 | 746.75 | 155.5592
755 | 166.5096 |  | 756.25 | 280.7625 | 757.75 | 173.4128 | 755 | 166.5096
763.25 | 5.4573 |  | 764.75 | 3613.2432 | 766 | 6.7054 | 763.25 | 5.4573
771.75 | 364.3982 |  | 773.25 | 351.4208 | 774.5 | 2297.6114 | 771.75 | 351.4208
780.25 | 1660.8561 |  | 781.75 | 1761.1063 | 783 | 3288.8156 | 780.25 | 1660.8561
788.75 | 299.4731 |  | 790.25 | 75.2363 | 791.5 | 89.9959 | 788.75 | 75.2363
797 | 142.2204 |  | 798.25 | 2.9042 | 799.75 | 3.5623 | 797 | 2.9042
805.25 | 24.5976 |  | 806.75 | 28.0571 | 808 | 635.0444 | 805.25 | 24.5976
813.75 | 1737.269 |  | 815.25 | 248.8724 | 816.5 | 210.536 | 813.75 | 210.536
822.25 | 306.2111 |  | 823.75 | 706.0719 | 825 | 275.8796 | 822.25 | 275.8796
830.5 | 116.5967 |  | 831.75 | 18458.2994 | 833.25 | 145.9327 | 830.5 | 116.5967
839 | 113.8573 |  | 840.25 | 143.0438 | 841.75 | 15006.1541 | 839 | 113.8573
847.25 | 305.6777 |  | 848.75 | 1365.446 | 850 | 294.3796 | 847.25 | 294.3796

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable | Tray Rung
0 | -104 | 18.2 | 26.2 | 22.3
1 | -103 | 18.2 | 26.2 | 22.3
2 | -102 | 18.2 | 26.2 | 22.3
3 | -101 | 18.2 | 26.2 | 22.3
4 | -100 | 18.2 | 26.2 | 22.4
5 | -99 | 18.2 | 26.1 | 22.4
6 | -98 | 18.2 | 26.1 | 22.4
7 | -97 | 18.3 | 26.1 | 22.4
8 | -96 | 18.2 | 26.1 | 22.4
9 | -95 | 18.3 | 26.1 | 22.4
10 | -94 | 18.3 | 26.1 | 22.4
11 | -93 | 18.3 | 26.1 | 22.5
12 | -92 | 18.2 | 26.1 | 22.4
13 | -91 | 18.3 | 26.1 | 22.4
14 | -90 | 18.3 | 26.1 | 22.5
15 | -89 | 18.3 | 26.1 | 22.4
16 | -88 | 18.3 | 26.1 | 22.4
17 | -87 | 18.3 | 26.1 | 22.5
18 | -86 | 18.3 | 26.1 | 22.4
19 | -85 | 18.3 | 26.1 | 22.4
20 | -84 | 18.2 | 26.1 | 22.4
21 | -83 | 18.2 | 26.1 | 22.4
22 | -82 | 18.2 | 26.1 | 22.4
23 | -81 | 18.2 | 26.1 | 22.4
24 | -80 | 18.2 | 26.1 | 22.4
25 | -79 | 18.2 | 26.1 | 22.4
26 | -78 | 18.3 | 26.1 | 22.4
27 | -77 | 18.2 | 26.1 | 22.4
28 | -76 | 18.3 | 26.1 | 22.4
29 | -75 | 18.2 | 26.1 | 22.4
30 | -74 | 18.2 | 26.1 | 22.4
31 | -73 | 18.2 | 26.1 | 22.4
32 | -72 | 18.2 | 26.1 | 22.4
33 | -71 | 18.2 | 26.1 | 22.4
34 | -70 | 18.2 | 26.1 | 22.4
35 | -69 | 18.3 | 26.1 | 22.4
36 | -68 | 18.2 | 26.1 | 22.4
37 | -67 | 18.2 | 26.2 | 22.4
38 | -66 | 18.2 | 26.2 | 22.3
39 | -65 | 18.2 | 26.1 | 22.3
40 | -64 | 18.2 | 26.2 | 22.3
41 | -63 | 18.2 | 26.2 | 22.3
42 | -62 | 18.2 | 26.2 | 22.3
43 | -61 | 18.2 | 26.2 | 22.3
44 | -60 | 18.2 | 26.2 | 22.3
45 | -59 | 18.3 | 26.1 | 22.5
46 | -58 | 18.3 | 26.1 | 22.5
47 | -57 | 18.3 | 26.1 | 22.5
48 | -56 | 18.3 | 26.1 | 22.5
49 | -55 | 18.3 | 26.1 | 22.5
50 | -54 | 18.3 | 26.1 | 22.5
51 | -53 | 18.3 | 26.1 | 22.5
52 | -52 | 18.3 | 26.1 | 22.5
53 | -51 | 18.2 | 26.1 | 22.4
54 | -50 | 18.2 | 26.1 | 22.5
55 | -49 | 18.2 | 26.1 | 22.4
56 | -48 | 18.2 | 26.2 | 22.3
57 | -47 | 18.2 | 26.2 | 22.3
58 | -46 | 18.2 | 26.2 | 22.3
59 | -45 | 18.2 | 26.2 | 22.3
60 | -44 | 18.2 | 26.1 | 22.3
61 | -43 | 18.2 | 26.1 | 22.3
62 | -42 | 18.2 | 26.2 | 22.3
63 | -41 | 18.2 | 26.1 | 22.3
64 | -40 | 18.2 | 26.2 | 22.3
65 | -39 | 18.2 | 26.2 | 22.3
66 | -38 | 18.2 | 26.2 | 22.3
67 | -37 | 18.2 | 26.2 | 22.3
68 | -36 | 18.2 | 26.2 | 22.3
69 | -35 | 18.2 | 26.2 | 22.3
70 | -34 | 18.2 | 26.2 | 22.3
71 | -33 | 18.2 | 26.2 | 22.3
72 | -32 | 18.2 | 26.2 | 22.3
73 | -31 | 18.2 | 26.2 | 22.3
74 | -30 | 18.2 | 26.2 | 22.3
75 | -29 | 18.2 | 26.2 | 22.3
76 | -28 | 18.2 | 26.2 | 22.3
77 | -27 | 18.2 | 26.2 | 22.3
78 | -26 | 18.2 | 26.2 | 22.3
79 | -25 | 18.2 | 26.2 | 22.3
80 | -24 | 18.2 | 26.2 | 22.3
81 | -23 | 18.2 | 26.2 | 22.3
82 | -22 | 18.2 | 26.2 | 22.3
83 | -21 | 18.2 | 26.2 | 22.3
84 | -20 | 18.2 | 26.2 | 22.3
85 | -19 | 18.2 | 26.2 | 22.3
86 | -18 | 18.2 | 26.2 | 22.3
87 | -17 | 18.2 | 26.1 | 22.4
88 | -16 | 18.2 | 26.2 | 22.3
89 | -15 | 18.2 | 26.3 | 22
90 | -14 | 18.1 | 26.5 | 21.7
91 | -13 | 18.1 | 26.5 | 21.7
92 | -12 | 18.1 | 26.5 | 21.7
93 | -11 | 18.1 | 26.5 | 21.7
94 | -10 | 18.1 | 26.5 | 21.7
95 | -9 | 18.1 | 26.5 | 21.7
96 | -8 | 18.1 | 26.5 | 21.7
97 | -7 | 18.1 | 26.5 | 21.7
98 | -6 | 18.1 | 26.5 | 21.6
99 | -5 | 18.1 | 26.5 | 21.6
100 | -4 | 18.1 | 26.4 | 21.8
101 | -3 | 18.1 | 26.3 | 21.9
102 | -2 | 18.2 | 26.4 | 21.9
103 | -1 | 18.5 | 26.4 | 21.9
104 | 0 | 19.4 | 26.4 | 21.9
105 | 1 | 20.9 | 26.4 | 21.9
106 | 2 | 23 | 26.4 | 22
107 | 3 | 25.4 | 26.4 | 21.9
108 | 4 | 28.3 | 26.4 | 22
109 | 5 | 31.5 | 26.4 | 22
110 | 6 | 34.9 | 26.4 | 22
111 | 7 | 38.6 | 26.4 | 22.1
112 | 8 | 42.6 | 26.4 | 22.1
113 | 9 | 46.7 | 26.5 | 22.1
114 | 10 | 51.1 | 26.5 | 22.2
115 | 11 | 55.6 | 26.5 | 22.3
116 | 12 | 60.3 | 26.6 | 22.3
117 | 13 | 65.1 | 26.6 | 22.4
118 | 14 | 69.9 | 26.7 | 22.5
119 | 15 | 75 | 26.8 | 22.6
120 | 16 | 80.1 | 26.8 | 22.7
121 | 17 | 85.4 | 27 | 22.9
122 | 18 | 90.7 | 27.1 | 23
123 | 19 | 96.2 | 27.2 | 23.1
124 | 20 | 101.7 | 27.3 | 23.3
125 | 21 | 107.3 | 27.5 | 23.5
126 | 22 | 112.9 | 27.6 | 23.7
127 | 23 | 118.5 | 27.8 | 23.9
128 | 24 | 124.4 | 28 | 24.1
129 | 25 | 130.2 | 28.2 | 24.3
130 | 26 | 136.1 | 28.5 | 24.6
131 | 27 | 142 | 28.7 | 24.8
132 | 28 | 148 | 29 | 25.1
133 | 29 | 153.9 | 29.3 | 25.4
134 | 30 | 159.8 | 29.6 | 25.7
135 | 31 | 165.8 | 29.9 | 26.1
136 | 32 | 171.7 | 30.3 | 26.5
137 | 33 | 177.6 | 30.7 | 26.8
138 | 34 | 183.6 | 31 | 27.2
139 | 35 | 189.5 | 31.5 | 27.7
140 | 36 | 195.5 | 31.9 | 28.1
141 | 37 | 201.5 | 32.4 | 28.6
142 | 38 | 207.5 | 32.9 | 29.1
143 | 39 | 213.4 | 33.4 | 29.6
144 | 40 | 219.3 | 34 | 30.2
145 | 41 | 225.3 | 34.6 | 30.7
146 | 42 | 231.1 | 35.2 | 31.3
147 | 43 | 237.1 | 35.8 | 32
148 | 44 | 243 | 36.5 | 32.7
149 | 45 | 248.7 | 37.2 | 33.3
150 | 46 | 254.5 | 37.9 | 34.1
151 | 47 | 260.2 | 38.7 | 34.8
152 | 48 | 266 | 39.5 | 35.6
153 | 49 | 271.8 | 40.2 | 36.4
154 | 50 | 277.4 | 41.1 | 37.2
155 | 51 | 282.9 | 41.9 | 38.1
156 | 52 | 288.5 | 42.8 | 39
157 | 53 | 294.1 | 43.7 | 40
158 | 54 | 299.7 | 44.7 | 40.9
159 | 55 | 305.2 | 45.7 | 41.9
160 | 56 | 310.6 | 46.7 | 42.9
161 | 57 | 316.1 | 47.7 | 43.9
162 | 58 | 321.6 | 48.8 | 45
163 | 59 | 327 | 49.8 | 46.1
164 | 60 | 332.2 | 51 | 47.2
165 | 61 | 337.5 | 52.1 | 48.4
166 | 62 | 342.7 | 53.3 | 49.7
167 | 63 | 348.1 | 54.5 | 51
168 | 64 | 353.2 | 55.7 | 52.4
169 | 65 | 358.3 | 56.9 | 53.7
170 | 66 | 363.4 | 58.2 | 55
171 | 67 | 368.6 | 59.6 | 56.4
172 | 68 | 373.8 | 61 | 57.9
173 | 69 | 378.9 | 62.4 | 59.3
174 | 70 | 384.1 | 63.8 | 60.9
175 | 71 | 389.3 | 65.2 | 62.4
176 | 72 | 394.4 | 66.7 | 64
177 | 73 | 399.3 | 68.3 | 65.7
178 | 74 | 404.2 | 69.9 | 67.4
179 | 75 | 409.1 | 71.6 | 69.1
180 | 76 | 414 | 73.3 | 70.9
181 | 77 | 418.7 | 75 | 72.7
182 | 78 | 423.5 | 76.7 | 74.5
183 | 79 | 428.4 | 78.5 | 76.3
184 | 80 | 433.2 | 80.3 | 78.3
185 | 81 | 437.8 | 82.1 | 80.2
186 | 82 | 442 | 83.9 | 82.2
187 | 83 | 445.7 | 85.8 | 84.3
188 | 84 | 449.1 | 87.7 | 86.4
189 | 85 | 452.4 | 89.8 | 88.2
190 | 86 | 455.6 | 91.8 | 90.2
191 | 87 | 458.6 | 93.8 | 92.4
192 | 88 | 461.5 | 95.9 | 94.5
193 | 89 | 464.2 | 97.9 | 96.7
194 | 90 | 466.7 | 99.8 | 99.1
195 | 91 | 469 | 101.8 | 101.4
196 | 92 | 471 | 103.8 | 103.8
197 | 93 | 472.7 | 105.7 | 106.2
198 | 94 | 474.3 | 107.7 | 108.6
199 | 95 | 475.5 | 109.7 | 110.9
200 | 96 | 476.5 | 111.7 | 113.2
201 | 97 | 477.3 | 113.8 | 115.4
202 | 98 | 477.9 | 115.9 | 117.7
203 | 99 | 478.3 | 118 | 119.9
204 | 100 | 478.5 | 120 | 122.3
205 | 101 | 478.6 | 121.9 | 124.5
206 | 102 | 478.5 | 123.9 | 126.8
207 | 103 | 478.1 | 125.8 | 129
208 | 104 | 477.7 | 127.7 | 131.3
209 | 105 | 477.1 | 129.7 | 133.4
210 | 106 | 476.6 | 131.6 | 135.7
211 | 107 | 476 | 133.6 | 137.8
212 | 108 | 475.3 | 135.6 | 140
213 | 109 | 474.8 | 137.5 | 142.2
214 | 110 | 474.2 | 139.5 | 144.3
215 | 111 | 473.5 | 141.5 | 146.4
216 | 112 | 472.7 | 143.4 | 148.5
217 | 113 | 472.1 | 145.4 | 150.6
218 | 114 | 471.4 | 147.3 | 152.7
219 | 115 | 470.6 | 149.2 | 154.8
220 | 116 | 469.9 | 151.2 | 156.8
221 | 117 | 469.2 | 153.2 | 158.9
222 | 118 | 468.7 | 155.2 | 160.8
223 | 119 | 468.1 | 157.2 | 162.8
224 | 120 | 467.6 | 159.2 | 164.7
225 | 121 | 467.1 | 161.2 | 166.7
226 | 122 | 466.6 | 163.2 | 168.6
227 | 123 | 466.2 | 165.2 | 170.6
228 | 124 | 465.9 | 167.2 | 172.5
229 | 125 | 465.6 | 169.2 | 174.5
230 | 126 | 465.4 | 171.1 | 176.4
231 | 127 | 465.3 | 173.1 | 178.4
232 | 128 | 465.2 | 175 | 180.4
233 | 129 | 465.2 | 177 | 182.3
234 | 130 | 465.3 | 178.9 | 184.3
235 | 131 | 465.2 | 180.8 | 186.3
236 | 132 | 465.4 | 182.7 | 188.2
237 | 133 | 465.6 | 184.6 | 190.2
238 | 134 | 465.8 | 186.5 | 192.1
239 | 135 | 466 | 188.4 | 194
240 | 136 | 466.3 | 190.2 | 196
241 | 137 | 466.6 | 192.1 | 197.9
242 | 138 | 467 | 193.9 | 199.9
243 | 139 | 467.4 | 195.8 | 201.8
244 | 140 | 467.9 | 197.6 | 203.8
245 | 141 | 468.2 | 199.4 | 205.7
246 | 142 | 468.5 | 201.2 | 207.7
247 | 143 | 468.9 | 202.9 | 209.7
248 | 144 | 469.1 | 204.7 | 211.6
249 | 145 | 469.3 | 206.5 | 213.5
250 | 146 | 469.5 | 208.3 | 215.4
251 | 147 | 469.8 | 210 | 217.3
252 | 148 | 470 | 211.7 | 219.1
253 | 149 | 470.1 | 213.4 | 221
254 | 150 | 470.1 | 215.2 | 222.8
255 | 151 | 470.3 | 216.8 | 224.7
256 | 152 | 470.4 | 218.5 | 226.6
257 | 153 | 470.4 | 220.2 | 228.4
258 | 154 | 470.4 | 221.9 | 230.2
259 | 155 | 470.4 | 223.5 | 232
260 | 156 | 470.5 | 225.2 | 233.8
261 | 157 | 470.5 | 226.8 | 235.6
262 | 158 | 470.5 | 228.4 | 237.4
263 | 159 | 470.5 | 230 | 239.2
264 | 160 | 470.5 | 231.6 | 240.9
265 | 161 | 470.4 | 233.2 | 242.7
266 | 162 | 470.4 | 234.7 | 244.4
267 | 163 | 470.4 | 236.2 | 246.2
268 | 164 | 470.3 | 237.8 | 247.9
269 | 165 | 470.3 | 239.2 | 249.6
270 | 166 | 470.1 | 240.6 | 251.3
271 | 167 | 470 | 242.1 | 252.9
272 | 168 | 470 | 243.5 | 254.6
273 | 169 | 470 | 244.8 | 256.3
274 | 170 | 470 | 246.1 | 257.9
275 | 171 | 469.9 | 247.3 | 259.5
276 | 172 | 469.8 | 248.3 | 261.1
277 | 173 | 469.7 | 249.3 | 262.7
278 | 174 | 469.6 | 250.1 | 264.4
279 | 175 | 469.6 | 250.7 | 265.9
280 | 176 | 469.6 | 251.5 | 267.5
281 | 177 | 469.6 | 252.4 | 269
282 | 178 | 469.7 | 253.4 | 270.6
283 | 179 | 469.7 | 254.5 | 272.2
284 | 180 | 469.6 | 256.1 | 273.7
285 | 181 | 469.7 | 257.8 | 275.2
286 | 182 | 469.7 | 259 | 276.7
287 | 183 | 469.8 | 260.1 | 278.3
288 | 184 | 469.8 | 261.1 | 279.8
289 | 185 | 469.7 | 262.1 | 281.2
290 | 186 | 469.6 | 263 | 282.7
291 | 187 | 469.6 | 264 | 284.2
292 | 188 | 469.6 | 265 | 285.7
293 | 189 | 469.6 | 266 | 287.2
294 | 190 | 469.6 | 267 | 288.7
295 | 191 | 469.5 | 267.9 | 290.1
296 | 192 | 469.4 | 268.9 | 291.6
297 | 193 | 469.4 | 269.7 | 293
298 | 194 | 469.4 | 270.6 | 294.4
299 | 195 | 469.3 | 271.5 | 295.8
300 | 196 | 469.2 | 272.3 | 297.3
301 | 197 | 469.2 | 273.2 | 298.7
302 | 198 | 469.2 | 274 | 300.2
303 | 199 | 469.2 | 274.8 | 301.6
304 | 200 | 469.2 | 275.7 | 303.1
305 | 201 | 469.2 | 276.5 | 304.5
306 | 202 | 469.3 | 277.4 | 305.9
307 | 203 | 469.3 | 278.3 | 307.3
308 | 204 | 469.4 | 279.1 | 308.7
309 | 205 | 469.4 | 280 | 310.1
310 | 206 | 469.3 | 280.8 | 311.5
311 | 207 | 469.2 | 281.7 | 312.9
312 | 208 | 469.1 | 282.5 | 314.2
313 | 209 | 469.1 | 283.3 | 315.6
314 | 210 | 469.2 | 284.2 | 317.2
315 | 211 | 469.4 | 285.3 | 318.9
316 | 212 | 469.5 | 286.4 | 320.8
317 | 213 | 469.7 | 287.1 | 323
318 | 214 | 470 | 287.8 | 325.3
319 | 215 | 470.2 | 288.8 | 327.8
320 | 216 | 470.4 | 289.8 | 330.5
321 | 217 | 470.7 | 291 | 333.2
322 | 218 | 470.8 | 292.5 | 336
323 | 219 | 471 | 294.1 | 338.8
324 | 220 | 471.2 | 295.6 | 341.6
325 | 221 | 471.3 | 297.1 | 344.3
326 | 222 | 471.5 | 298.2 | 346.9
327 | 223 | 471.5 | 298.7 | 349.3
328 | 224 | 471.5 | 299.6 | 351.8
329 | 225 | 471.3 | 300.8 | 354.1
330 | 226 | 471 | 302.2 | 356.4
331 | 227 | 470.8 | 303.3 | 358.6
332 | 228 | 470.5 | 304.3 | 360.7
333 | 229 | 470.2 | 305.5 | 362.8
334 | 230 | 469.9 | 306.8 | 364.9
335 | 231 | 469.6 | 308.1 | 366.9
336 | 232 | 469.2 | 309.5 | 368.9
337 | 233 | 468.9 | 311 | 370.9
338 | 234 | 468.5 | 312.5 | 372.8
339 | 235 | 468.1 | 313.9 | 374.8
340 | 236 | 467.7 | 315.1 | 376.7
341 | 237 | 467.3 | 316.4 | 378.6
342 | 238 | 467 | 317.7 | 380.5
343 | 239 | 466.6 | 319.1 | 382.4
344 | 240 | 466.2 | 320.7 | 384.2
345 | 241 | 465.8 | 322.5 | 386
346 | 242 | 465.5 | 324.5 | 387.9
347 | 243 | 465.3 | 326.7 | 389.9
348 | 244 | 465.1 | 329 | 391.9
349 | 245 | 465 | 331.4 | 393.9
350 | 246 | 464.7 | 334.1 | 395.7
351 | 247 | 464.3 | 337 | 397.5
352 | 248 | 463.9 | 339.8 | 399.3
353 | 249 | 463.4 | 342.8 | 401.1
354 | 250 | 462.9 | 345.8 | 402.8
355 | 251 | 462.3 | 348.9 | 404.6
356 | 252 | 461.8 | 352.2 | 406.3
357 | 253 | 461.3 | 355.7 | 408
358 | 254 | 460.7 | 359.4 | 409.7
359 | 255 | 460.1 | 363.1 | 411.3
360 | 256 | 459.6 | 367 | 413
361 | 257 | 459.1 | 370.8 | 414.6
362 | 258 | 458.6 | 374.7 | 416.2
363 | 259 | 458 | 378.4 | 417.8
364 | 260 | 457.4 | 382 | 419.4
365 | 261 | 456.8 | 385.6 | 421
366 | 262 | 456.1 | 389.2 | 422.6
367 | 263 | 455.4 | 392.7 | 424.1
368 | 264 | 454.7 | 396.1 | 425.6
369 | 265 | 454.1 | 399.4 | 427.1
370 | 266 | 453.5 | 402.8 | 428.6
371 | 267 | 452.8 | 405.9 | 430.1
372 | 268 | 452.2 | 408.9 | 431.5
373 | 269 | 451.6 | 411.7 | 432.9
374 | 270 | 450.9 | 414.3 | 434.2
375 | 271 | 450.3 | 416.9 | 435.5
376 | 272 | 449.6 | 419.2 | 436.8
377 | 273 | 449 | 421.4 | 438.1
378 | 274 | 448.4 | 423.6 | 439.4
379 | 275 | 447.8 | 425.2 | 440.6
380 | 276 | 447.2 | 426.3 | 441.9
381 | 277 | 446.5 | 427.9 | 443
382 | 278 | 445.8 | 429.6 | 444.2
383 | 279 | 445.1 | 431.5 | 445.3
384 | 280 | 444.5 | 433.3 | 446.4
385 | 281 | 443.9 | 435.1 | 447.5
386 | 282 | 443.3 | 436.5 | 448.6
387 | 283 | 442.7 | 437.8 | 449.6
388 | 284 | 442.1 | 439.2 | 450.6
389 | 285 | 441.4 | 440.7 | 451.6
390 | 286 | 440.8 | 442.3 | 452.5
391 | 287 | 440.2 | 443.8 | 453.5
392 | 288 | 439.6 | 445.2 | 454.4
393 | 289 | 439 | 446.6 | 455.2
394 | 290 | 438.3 | 447.9 | 456
395 | 291 | 437.7 | 449.3 | 456.7
396 | 292 | 437.1 | 451 | 457.5
397 | 293 | 436.4 | 453 | 458.1
398 | 294 | 435.8 | 455 | 458.7
399 | 295 | 435.2 | 457 | 459.4
400 | 296 | 434.6 | 459 | 459.9
401 | 297 | 433.9 | 460.9 | 460.4
402 | 298 | 433.2 | 462.8 | 460.9
403 | 299 | 432.6 | 464.4 | 461.2
404 | 300 | 431.9 | 465.8 | 461.6
405 | 301 | 431.2 | 467 | 461.9
406 | 302 | 430.6 | 468.1 | 462.2
407 | 303 | 429.9 | 469.1 | 462.4
408 | 304 | 429.3 | 470 | 462.6
409 | 305 | 428.7 | 470.8 | 462.8
410 | 306 | 428.1 | 471.6 | 463
411 | 307 | 427.4 | 472.5 | 463.1
412 | 308 | 426.9 | 473.6 | 463.2
413 | 309 | 426.3 | 474.7 | 463.2
414 | 310 | 425.7 | 475.7 | 463.3
415 | 311 | 425 | 476.7 | 463.3
416 | 312 | 424.4 | 477.5 | 463.3
417 | 313 | 423.7 | 478.3 | 463.2
418 | 314 | 423 | 479 | 463.2
419 | 315 | 422.4 | 479.6 | 463.1
420 | 316 | 421.8 | 480.2 | 463
421 | 317 | 421.2 | 480.8 | 462.9
422 | 318 | 420.5 | 481.5 | 462.8
423 | 319 | 420 | 482.1 | 462.7
424 | 320 | 419.4 | 482.7 | 462.6
425 | 321 | 418.7 | 483.1 | 462.5
426 | 322 | 418.1 | 483.5 | 462.5
427 | 323 | 417.5 | 483.8 | 462.4
428 | 324 | 416.9 | 484.2 | 462.3
429 | 325 | 416.2 | 484.5 | 462.2
430 | 326 | 415.6 | 484.9 | 462.2
431 | 327 | 415 | 485.3 | 462
432 | 328 | 414.4 | 485.7 | 461.9
433 | 329 | 413.8 | 486.3 | 461.8
434 | 330 | 413.1 | 486.9 | 461.7
435 | 331 | 412.4 | 487.5 | 461.5
436 | 332 | 411.8 | 488.1 | 461.4
437 | 333 | 411.3 | 488.7 | 461.3
438 | 334 | 410.6 | 489.4 | 461.1
439 | 335 | 410 | 490 | 460.9
440 | 336 | 409.4 | 490.6 | 460.8
441 | 337 | 408.8 | 491.2 | 460.6
442 | 338 | 408.2 | 491.8 | 460.5
443 | 339 | 407.7 | 492.2 | 460.3
444 | 340 | 407.1 | 492.7 | 460.1
445 | 341 | 406.6 | 493.1 | 460
446 | 342 | 406 | 493.5 | 459.8
447 | 343 | 405.4 | 493.8 | 459.7
448 | 344 | 404.8 | 494.2 | 459.5
449 | 345 | 404.2 | 494.5 | 459.4
450 | 346 | 403.6 | 494.8 | 459.2
451 | 347 | 403.1 | 495 | 459.1
452 | 348 | 402.6 | 495.2 | 459
453 | 349 | 402.1 | 495.3 | 458.9
454 | 350 | 401.5 | 495.5 | 458.8
455 | 351 | 401 | 495.7 | 458.7
456 | 352 | 400.5 | 495.9 | 458.6
457 | 353 | 399.9 | 496.1 | 458.5
458 | 354 | 399.4 | 496.4 | 458.5
459 | 355 | 398.9 | 496.7 | 458.4
460 | 356 | 398.4 | 496.9 | 458.3
461 | 357 | 397.8 | 497.2 | 458.3
462 | 358 | 397.3 | 497.5 | 458.2
463 | 359 | 396.8 | 497.8 | 458.2
464 | 360 | 396.3 | 498.1 | 458.2
465 | 361 | 395.8 | 498.4 | 458.1
466 | 362 | 395.2 | 498.7 | 458.1
467 | 363 | 394.7 | 499 | 458.1
468 | 364 | 394.2 | 499.3 | 458.1
469 | 365 | 393.7 | 499.6 | 458.1
470 | 366 | 393.3 | 500 | 458.1
471 | 367 | 392.8 | 500.3 | 458.2
472 | 368 | 392.4 | 500.6 | 458.3
473 | 369 | 391.9 | 501 | 458.3
474 | 370 | 391.4 | 501.3 | 458.4
475 | 371 | 390.9 | 501.7 | 458.5
476 | 372 | 390.4 | 502 | 458.5
477 | 373 | 389.9 | 502.3 | 458.6
478 | 374 | 389.4 | 502.6 | 458.7
479 | 375 | 388.9 | 503 | 458.8
480 | 376 | 388.4 | 503.4 | 458.8
481 | 377 | 388 | 503.9 | 458.9
482 | 378 | 387.5 | 504.4 | 459
483 | 379 | 387 | 505 | 459
484 | 380 | 386.5 | 505.6 | 459.1
485 | 381 | 386 | 506.3 | 459.1
486 | 382 | 385.5 | 507 | 459.2
487 | 383 | 385 | 507.7 | 459.2
488 | 384 | 384.5 | 508.4 | 459.2
489 | 385 | 384 | 509.2 | 459.2
490 | 386 | 383.6 | 509.9 | 459.3
491 | 387 | 383.1 | 510.8 | 459.3
492 | 388 | 382.6 | 511.6 | 459.3
493 | 389 | 382.1 | 512.5 | 459.3
494 | 390 | 381.6 | 513.4 | 459.4
495 | 391 | 381.1 | 514.3 | 459.4
496 | 392 | 380.6 | 515.3 | 459.5
497 | 393 | 380.1 | 516.2 | 459.5
498 | 394 | 379.6 | 517.3 | 459.6
499 | 395 | 379.2 | 518.3 | 459.6
500 | 396 | 378.8 | 519.4 | 459.7
501 | 397 | 378.3 | 520.5 | 459.8
502 | 398 | 377.9 | 521.6 | 459.8
503 | 399 | 377.4 | 522.7 | 459.8
504 | 400 | 377 | 523.9 | 459.8
505 | 401 | 376.5 | 525.1 | 459.8
506 | 402 | 375.9 | 526.3 | 459.8
507 | 403 | 375.5 | 527.6 | 459.8
508 | 404 | 374.9 | 528.9 | 459.8
509 | 405 | 374.5 | 530.2 | 459.7
510 | 406 | 374 | 531.5 | 459.7
511 | 407 | 373.6 | 532.7 | 459.6
512 | 408 | 373.2 | 534 | 459.6
513 | 409 | 372.7 | 535.2 | 459.5
514 | 410 | 372.3 | 536.5 | 459.5
515 | 411 | 371.8 | 537.8 | 459.4
516 | 412 | 371.3 | 539 | 459.3
517 | 413 | 370.8 | 540.2 | 459.2
518 | 414 | 370.3 | 541.5 | 459.1
519 | 415 | 369.9 | 542.8 | 459
520 | 416 | 369.5 | 544.1 | 458.8
521 | 417 | 369 | 545.4 | 458.6
522 | 418 | 368.5 | 546.7 | 458.4
523 | 419 | 368.1 | 547.8 | 458.2
524 | 420 | 367.6 | 549 | 458
525 | 421 | 367.2 | 550.1 | 457.8
526 | 422 | 366.7 | 551.3 | 457.6
527 | 423 | 366.2 | 552.4 | 457.3
528 | 424 | 365.8 | 553.6 | 457.1
529 | 425 | 365.3 | 554.8 | 456.9
530 | 426 | 364.8 | 556 | 456.6
531 | 427 | 364.3 | 557.3 | 456.4
532 | 428 | 363.9 | 558.5 | 456.1
533 | 429 | 363.4 | 559.8 | 455.9
534 | 430 | 363 | 561.1 | 455.6
535 | 431 | 362.5 | 562.4 | 455.3
536 | 432 | 362.1 | 563.6 | 455
537 | 433 | 361.6 | 564.8 | 454.7
538 | 434 | 361.2 | 566 | 454.4
539 | 435 | 360.7 | 567.2 | 454.1
540 | 436 | 360.2 | 568.4 | 453.8
541 | 437 | 359.8 | 569.6 | 453.6
542 | 438 | 359.3 | 570.9 | 453.3
543 | 439 | 358.8 | 572.1 | 452.9
544 | 440 | 358.4 | 573.4 | 452.6
545 | 441 | 358 | 574.6 | 452.3
546 | 442 | 357.5 | 575.9 | 452
547 | 443 | 357 | 577.1 | 451.7
548 | 444 | 356.6 | 578.3 | 451.3
549 | 445 | 356.2 | 579.6 | 451
550 | 446 | 355.7 | 580.9 | 450.7
551 | 447 | 355.2 | 582.3 | 450.4
552 | 448 | 354.7 | 583.8 | 450
553 | 449 | 354.2 | 585.2 | 449.7
554 | 450 | 353.8 | 586.4 | 449.3
555 | 451 | 353.5 | 587.6 | 449
556 | 452 | 353.1 | 588.9 | 448.6
557 | 453 | 352.6 | 590.2 | 448.3
558 | 454 | 352.2 | 591.5 | 447.9
559 | 455 | 351.8 | 592.8 | 447.5
560 | 456 | 351.4 | 594.1 | 447.2
561 | 457 | 351 | 595.5 | 446.8
562 | 458 | 350.6 | 596.9 | 446.4
563 | 459 | 350.2 | 598.1 | 446
564 | 460 | 349.7 | 599.2 | 445.5
565 | 461 | 349.2 | 600.2 | 445.1
566 | 462 | 348.8 | 601.4 | 444.7
567 | 463 | 348.4 | 602.6 | 444.3
568 | 464 | 347.9 | 603.8 | 443.9
569 | 465 | 347.4 | 605 | 443.5
570 | 466 | 347 | 606.2 | 443.1
571 | 467 | 346.6 | 607.5 | 442.7
572 | 468 | 346.1 | 608.7 | 442.3
573 | 469 | 345.7 | 609.9 | 441.8
574 | 470 | 345.3 | 611.1 | 441.4
575 | 471 | 344.9 | 612.3 | 440.9
576 | 472 | 344.5 | 613.4 | 440.5
577 | 473 | 344 | 614.5 | 440
578 | 474 | 343.6 | 615.5 | 439.6
579 | 475 | 343.2 | 616.6 | 439.1
580 | 476 | 342.8 | 617.8 | 438.7
581 | 477 | 342.3 | 619 | 438.3
582 | 478 | 342 | 620.2 | 437.8
583 | 479 | 341.6 | 621.4 | 437.4
584 | 480 | 341.1 | 622.6 | 436.9
585 | 481 | 340.7 | 623.9 | 436.5
586 | 482 | 340.4 | 625.2 | 436
587 | 483 | 340 | 626.4 | 435.6
588 | 484 | 339.5 | 627.6 | 435.2
589 | 485 | 339.1 | 628.7 | 434.7
590 | 486 | 338.7 | 629.8 | 434.3
591 | 487 | 338.3 | 630.7 | 433.8
592 | 488 | 337.9 | 631.7 | 433.4
593 | 489 | 337.5 | 632.7 | 432.9
594 | 490 | 337 | 634 | 432.4
595 | 491 | 336.7 | 635.3 | 432
596 | 492 | 336.2 | 636.5 | 431.5
597 | 493 | 335.8 | 637.7 | 431
598 | 494 | 335.4 | 638.8 | 430.6
599 | 495 | 335 | 640.1 | 430
600 | 496 | 334.6 | 641.3 | 429.5
601 | 497 | 334.2 | 642.5 | 429.1
602 | 498 | 333.8 | 643.6 | 428.6
603 | 499 | 333.4 | 644.8 | 428.1
604 | 500 | 333.1 | 645.8 | 427.6
605 | 501 | 332.7 | 646.8 | 427.2
606 | 502 | 332.4 | 647.8 | 426.7
607 | 503 | 332 | 648.8 | 426.2
608 | 504 | 331.5 | 649.8 | 425.7
609 | 505 | 331.1 | 650.9 | 425.2
610 | 506 | 330.8 | 652.1 | 424.8
611 | 507 | 330.3 | 653.1 | 424.3
612 | 508 | 329.9 | 654.2 | 423.8
613 | 509 | 329.5 | 655.3 | 423.3
614 | 510 | 329.1 | 656.3 | 422.8
615 | 511 | 328.7 | 657.2 | 422.3
616 | 512 | 328.3 | 658 | 421.9
617 | 513 | 327.9 | 658.8 | 421.4
618 | 514 | 327.6 | 659.6 | 420.9
619 | 515 | 327.2 | 660.3 | 420.5
620 | 516 | 326.7 | 660.9 | 420
621 | 517 | 326.3 | 661.6 | 419.5
622 | 518 | 325.8 | 662.2 | 419.1
623 | 519 | 325.4 | 662.8 | 418.6
624 | 520 | 325 | 663.5 | 418.1
625 | 521 | 324.7 | 664.1 | 417.6
626 | 522 | 324.3 | 664.7 | 417.2
627 | 523 | 323.9 | 665.3 | 416.7
628 | 524 | 323.6 | 666 | 416.2
629 | 525 | 323.1 | 666.7 | 415.7
630 | 526 | 322.7 | 667.3 | 415.2
631 | 527 | 322.4 | 668 | 414.7
632 | 528 | 322 | 668.8 | 414.2
633 | 529 | 321.6 | 669.5 | 413.8
634 | 530 | 321.3 | 670.2 | 413.3
635 | 531 | 320.9 | 670.8 | 412.8
636 | 532 | 320.5 | 671.6 | 412.3
637 | 533 | 320.1 | 672.3 | 411.8
638 | 534 | 319.7 | 673.1 | 411.3
639 | 535 | 319.3 | 673.9 | 410.8
640 | 536 | 319 | 674.7 | 410.3
641 | 537 | 318.6 | 675.5 | 409.8
642 | 538 | 318.2 | 676.4 | 409.3
643 | 539 | 317.8 | 677.2 | 408.8
644 | 540 | 317.3 | 678 | 408.3
645 | 541 | 317 | 678.9 | 407.8
646 | 542 | 316.6 | 679.9 | 407.3
647 | 543 | 316.2 | 681.1 | 406.8
648 | 544 | 315.8 | 682.2 | 406.3
649 | 545 | 315.5 | 683.4 | 405.8
650 | 546 | 315.1 | 684.5 | 405.4
651 | 547 | 314.7 | 685.5 | 404.9
652 | 548 | 314.4 | 686.4 | 404.4
653 | 549 | 314 | 687.5 | 403.9
654 | 550 | 313.6 | 688.5 | 403.4
655 | 551 | 313.3 | 689.6 | 402.9
656 | 552 | 312.9 | 690.7 | 402.4
657 | 553 | 312.6 | 691.8 | 401.9
658 | 554 | 312.2 | 692.9 | 401.4
659 | 555 | 311.8 | 694.1 | 400.9
660 | 556 | 311.4 | 695.3 | 400.4
661 | 557 | 311.1 | 696.5 | 399.9
662 | 558 | 310.8 | 697.5 | 399.4
663 | 559 | 310.4 | 698.5 | 398.9
664 | 560 | 310 | 699.2 | 398.4
665 | 561 | 309.6 | 700 | 397.9
666 | 562 | 309.3 | 700.7 | 397.4
667 | 563 | 309 | 701.5 | 396.9
668 | 564 | 308.6 | 702 | 396.4
669 | 565 | 308.3 | 702.6 | 395.9
670 | 566 | 307.9 | 703.5 | 395.4
671 | 567 | 307.4 | 704.4 | 394.8
672 | 568 | 307 | 705.4 | 394.4
673 | 569 | 306.7 | 706.5 | 393.8
674 | 570 | 306.3 | 707.5 | 393.3
675 | 571 | 306 | 708.3 | 392.8
676 | 572 | 305.6 | 708.9 | 392.3
677 | 573 | 305.2 | 709.4 | 391.8
678 | 574 | 304.9 | 709.8 | 391.3
679 | 575 | 304.5 | 710.3 | 390.8
680 | 576 | 304.2 | 710.7 | 390.3
681 | 577 | 303.8 | 711.1 | 389.7
682 | 578 | 303.5 | 711.6 | 389.2
683 | 579 | 303.2 | 712.1 | 388.7
684 | 580 | 302.8 | 712.4 | 388.2
685 | 581 | 302.5 | 712.8 | 387.7
686 | 582 | 302.2 | 713.2 | 387.2
687 | 583 | 301.8 | 713.7 | 386.6
688 | 584 | 301.4 | 714.2 | 386.1
689 | 585 | 301 | 714.6 | 385.6
690 | 586 | 300.6 | 714.9 | 385.1
691 | 587 | 300.3 | 715.4 | 384.6
692 | 588 | 300 | 715.9 | 384
693 | 589 | 299.6 | 716.4 | 383.5
694 | 590 | 299.2 | 716.5 | 383
695 | 591 | 298.9 | 716.7 | 382.4
696 | 592 | 298.5 | 716.7 | 381.9
697 | 593 | 298.2 | 716.8 | 381.4
698 | 594 | 297.9 | 717 | 380.9
699 | 595 | 297.5 | 717.2 | 380.3
700 | 596 | 297.1 | 717.5 | 379.8
701 | 597 | 296.7 | 717.8 | 379.3
702 | 598 | 296.4 | 718 | 378.7
703 | 599 | 296.1 | 718 | 378.2
704 | 600 | 295.7 | 718.1 | 377.7
705 | 601 | 295.4 | 718.3 | 377.2
706 | 602 | 295.1 | 718.4 | 376.6
707 | 603 | 294.7 | 718.7 | 376.1
708 | 604 | 294.3 | 718.8 | 375.6
709 | 605 | 294.1 | 719 | 375
710 | 606 | 293.8 | 719.1 | 374.5
711 | 607 | 293.4 | 719 | 373.9
712 | 608 | 293.1 | 719 | 373.4
713 | 609 | 292.7 | 718.9 | 372.9
714 | 610 | 292.4 | 719 | 372.3
715 | 611 | 292.1 | 719.2 | 371.8
716 | 612 | 291.8 | 719.3 | 371.2
717 | 613 | 291.5 | 719.4 | 370.7
718 | 614 | 291.1 | 719.4 | 370.1
719 | 615 | 290.8 | 719.3 | 369.6
720 | 616 | 290.5 | 719.1 | 369
721 | 617 | 290.1 | 719 | 368.5
722 | 618 | 289.8 | 719 | 368
723 | 619 | 289.5 | 718.9 | 367.4
724 | 620 | 289.2 | 718.6 | 366.9
725 | 621 | 288.9 | 718.4 | 366.3
726 | 622 | 288.6 | 718.3 | 365.8
727 | 623 | 288.3 | 718.3 | 365.3
728 | 624 | 288.1 | 718.1 | 364.7
729 | 625 | 287.8 | 717.6 | 364.2
730 | 626 | 287.5 | 717.5 | 363.6
731 | 627 | 287.2 | 717.3 | 363.1
732 | 628 | 286.9 | 717 | 362.6
733 | 629 | 286.5 | 716.4 | 362
734 | 630 | 286.2 | 715.7 | 361.5
735 | 631 | 285.9 | 715.2 | 361
736 | 632 | 285.6 | 714.8 | 360.5
737 | 633 | 285.3 | 714.5 | 359.9
738 | 634 | 285 | 714.1 | 359.4
739 | 635 | 284.7 | 713.4 | 358.9
740 | 636 | 284.4 | 712.9 | 358.4
741 | 637 | 284 | 712.7 | 357.8
742 | 638 | 283.7 | 712.3 | 357.3
743 | 639 | 283.4 | 711.6 | 356.8
744 | 640 | 283.1 | 710.8 | 356.2
745 | 641 | 282.8 | 710.1 | 355.7
746 | 642 | 282.5 | 709.3 | 355.2
747 | 643 | 282.2 | 708.2 | 354.7
748 | 644 | 281.8 | 707 | 354.2
749 | 645 | 281.5 | 706.1 | 353.6
750 | 646 | 281.2 | 705.2 | 353.1
751 | 647 | 280.8 | 704.6 | 352.6
752 | 648 | 280.4 | 703.7 | 352.1
753 | 649 | 280.1 | 702.4 | 351.6
754 | 650 | 279.8 | 701.3 | 351.1
755 | 651 | 279.5 | 700.1 | 350.6
756 | 652 | 279.2 | 698.9 | 350.1
757 | 653 | 278.9 | 697.3 | 349.6
758 | 654 | 278.6 | 695.5 | 349.1
759 | 655 | 278.3 | 693.8 | 348.6
760 | 656 | 278 | 692.3 | 348.1
761 | 657 | 277.7 | 690.6 | 347.6
762 | 658 | 277.4 | 689 | 347.1
763 | 659 | 277.1 | 687.2 | 346.6
764 | 660 | 276.8 | 684.9 | 346.1
765 | 661 | 276.5 | 682.4 | 345.6
766 | 662 | 276.2 | 679.6 | 345.1
767 | 663 | 275.9 | 676.7 | 344.6
768 | 664 | 275.6 | 673.1 | 344.1
769 | 665 | 275.3 | 668.5 | 343.6
770 | 666 | 275 | 663.4 | 343.1
771 | 667 | 274.7 | 657.7 | 342.5
772 | 668 | 274.4 | 652.1 | 342.1
773 | 669 | 274.1 | 646.1 | 341.6
774 | 670 | 273.8 | 639.9 | 341.1
775 | 671 | 273.5 | 633.9 | 340.6
776 | 672 | 273.2 | 628.2 | 340.1
777 | 673 | 272.9 | 622.7 | 339.6
778 | 674 | 272.6 | 617 | 339.1
779 | 675 | 272.3 | 611.2 | 338.6
780 | 676 | 272 | 605.5 | 338.1
781 | 677 | 271.7 | 600.1 | 337.6
782 | 678 | 271.5 | 594.8 | 337.1
783 | 679 | 271.1 | 589.7 | 336.6
784 | 680 | 270.8 | 584.5 | 336.1
785 | 681 | 270.5 | 579.1 | 335.6
786 | 682 | 270.2 | 573.5 | 335.2
787 | 683 | 269.9 | 567.9 | 334.7
788 | 684 | 269.6 | 562.4 | 334.2
789 | 685 | 269.3 | 557.2 | 333.7
790 | 686 | 269 | 552.2 | 333.2
791 | 687 | 268.8 | 547.5 | 332.7
792 | 688 | 268.5 | 542.9 | 332.2
793 | 689 | 268.2 | 538.5 | 331.8
794 | 690 | 267.9 | 534.3 | 331.3
795 | 691 | 267.7 | 530.2 | 330.8
796 | 692 | 267.4 | 526.3 | 330.4
797 | 693 | 267.1 | 522.6 | 329.9
798 | 694 | 266.9 | 519 | 329.4
799 | 695 | 266.6 | 515.5 | 328.9
800 | 696 | 266.3 | 512.1 | 328.4
801 | 697 | 266 | 508.9 | 328
802 | 698 | 265.7 | 505.7 | 327.5
803 | 699 | 265.4 | 502.6 | 327
804 | 700 | 265.1 | 499.6 | 326.5
805 | 701 | 264.8 | 496.6 | 326.1
806 | 702 | 264.5 | 493.6 | 325.6
807 | 703 | 264.2 | 490.7 | 325.1
808 | 704 | 264 | 487.8 | 324.6
809 | 705 | 263.7 | 485 | 324.1
810 | 706 | 263.4 | 482.2 | 323.6
811 | 707 | 263.1 | 479.4 | 323.1
812 | 708 | 262.8 | 476.7 | 322.7
813 | 709 | 262.5 | 474 | 322.2
814 | 710 | 262.2 | 471.3 | 321.7
815 | 711 | 261.9 | 468.6 | 321.2
816 | 712 | 261.7 | 466 | 320.7
817 | 713 | 261.4 | 463.3 | 320.2
818 | 714 | 261 | 460.7 | 319.7
819 | 715 | 260.8 | 458.1 | 319.2
820 | 716 | 260.5 | 455.4 | 318.7
821 | 717 | 260.2 | 452.6 | 318.1
822 | 718 | 260 | 449.8 | 317.6
823 | 719 | 259.7 | 446.9 | 317.1
824 | 720 | 259.4 | 443.9 | 316.6
825 | 721 | 259.1 | 440.9 | 316.1
826 | 722 | 258.9 | 437.9 | 315.6
827 | 723 | 258.6 | 434.9 | 315.1
828 | 724 | 258.4 | 431.9 | 314.6
829 | 725 | 258.1 | 428.9 | 314.1
830 | 726 | 257.8 | 426 | 313.6
831 | 727 | 257.6 | 423.2 | 313.1
832 | 728 | 257.3 | 420.3 | 312.6
833 | 729 | 257 | 417.6 | 312.2
834 | 730 | 256.7 | 414.9 | 311.7
835 | 731 | 256.5 | 412.3 | 311.2
836 | 732 | 256.3 | 409.8 | 310.7
837 | 733 | 256 | 407.3 | 310.2
838 | 734 | 255.7 | 404.9 | 309.7
839 | 735 | 255.5 | 402.5 | 309.3
840 | 736 | 255.2 | 400.2 | 308.8
841 | 737 | 254.9 | 397.9 | 308.3
842 | 738 | 254.7 | 395.7 | 307.8
843 | 739 | 254.3 | 393.5 | 307.4
844 | 740 | 254.1 | 391.4 | 306.9
845 | 741 | 253.8 | 389.4 | 306.4
846 | 742 | 253.5 | 387.3 | 306
847 | 743 | 253.3 | 385.4 | 305.5
848 | 744 | 253 | 383.4 | 305.1
849 | 745 | 252.7 | 381.5 | 304.6
850 | 746 | 252.4 | 379.7 | 304.2
851 | 747 | 252.1 | 377.9 | 303.7
852 | 748 | 251.9 | 376.1 | 303.3
853 | 749 | 251.6 | 374.4 | 302.8
854 | 750 | 251.4 | 372.8 | 302.4
855 | 751 | 251.1 | 371.1 | 301.9
856 | 752 | 250.9 | 369.5 | 301.5
857 | 753 | 250.6 | 368 | 301.1
858 | 754 | 250.4 | 366.5 | 300.7
859 | 755 | 250.1 | 365 | 300.2
860 | 756 | 249.9 | 363.6 | 299.8
861 | 757 | 249.6 | 362.1 | 299.4
862 | 758 | 249.4 | 360.7 | 299
863 | 759 | 249.1 | 359.4 | 298.6
864 | 760 | 248.9 | 358 | 298.1
865 | 761 | 248.6 | 356.7 | 297.7
866 | 762 | 248.3 | 355.4 | 297.3
867 | 763 | 248.1 | 354.2 | 296.9
868 | 764 | 247.8 | 352.9 | 296.5
869 | 765 | 247.5 | 351.7 | 296.1
870 | 766 | 247.3 | 350.5 | 295.7
871 | 767 | 247 | 349.3 | 295.2
872 | 768 | 246.7 | 348.1 | 294.9
873 | 769 | 246.4 | 346.9 | 294.4
874 | 770 | 246.2 | 345.7 | 294
875 | 771 | 245.9 | 344.6 | 293.7
876 | 772 | 245.7 | 343.4 | 293.2
877 | 773 | 245.4 | 342.3 | 292.8
878 | 774 | 245.2 | 341.2 | 292.4
879 | 775 | 244.9 | 340.1 | 292
880 | 776 | 244.6 | 339 | 291.6
881 | 777 | 244.4 | 337.9 | 291.3
882 | 778 | 244.1 | 336.9 | 290.9
883 | 779 | 243.9 | 335.8 | 290.5
884 | 780 | 243.6 | 334.8 | 290.1
885 | 781 | 243.3 | 333.8 | 289.7
886 | 782 | 243.1 | 332.8 | 289.3
887 | 783 | 242.8 | 331.9 | 288.9
888 | 784 | 242.6 | 330.9 | 288.5
889 | 785 | 242.3 | 330 | 288.1
890 | 786 | 242.1 | 329 | 287.7
891 | 787 | 241.8 | 328.1 | 287.4
892 | 788 | 241.6 | 327.2 | 287
893 | 789 | 241.3 | 326.2 | 286.6
894 | 790 | 241.1 | 325.3 | 286.2
895 | 791 | 240.9 | 324.4 | 285.9
896 | 792 | 240.6 | 323.5 | 285.5
897 | 793 | 240.4 | 322.6 | 285.1
898 | 794 | 240.1 | 321.7 | 284.7
899 | 795 | 239.8 | 320.9 | 284.3
900 | 796 | 239.6 | 320 | 284
901 | 797 | 239.3 | 319.1 | 283.6
902 | 798 | 239.1 | 318.2 | 283.2
903 | 799 | 238.8 | 317.3 | 282.9
904 | 800 | 238.6 | 316.5 | 282.5
905 | 801 | 238.3 | 315.6 | 282.1
906 | 802 | 238.1 | 314.7 | 281.7
907 | 803 | 237.8 | 313.9 | 281.3
908 | 804 | 237.6 | 313 | 281
909 | 805 | 237.3 | 312.2 | 280.6
910 | 806 | 237.1 | 311.3 | 280.2
911 | 807 | 236.8 | 310.5 | 279.8
912 | 808 | 236.6 | 309.7 | 279.5
913 | 809 | 236.4 | 308.8 | 279.1
914 | 810 | 236.2 | 308 | 278.8
915 | 811 | 235.9 | 307.1 | 278.4
916 | 812 | 235.6 | 306.6 | 278
917 | 813 | 235.3 | 306.2 | 277.7
918 | 814 | 235.1 | 305.8 | 277.3
919 | 815 | 234.8 | 305.3 | 276.9
920 | 816 | 234.6 | 304.7 | 276.6
921 | 817 | 234.3 | 304.1 | 276.2
922 | 818 | 234 | 303.5 | 275.9
923 | 819 | 233.8 | 302.8 | 275.5
924 | 820 | 233.5 | 302 | 275.2
925 | 821 | 233.3 | 301.3 | 274.8
926 | 822 | 233.1 | 300.6 | 274.4
927 | 823 | 232.9 | 299.8 | 274.1
928 | 824 | 232.7 | 299.1 | 273.7
929 | 825 | 232.5 | 298.3 | 273.3
930 | 826 | 232.3 | 297.5 | 273
931 | 827 | 232.1 | 296.8 | 272.7
932 | 828 | 231.9 | 296 | 272.3
933 | 829 | 231.6 | 295.2 | 272
934 | 830 | 231.4 | 294.5 | 271.6
935 | 831 | 231.1 | 293.7 | 271.2
936 | 832 | 230.9 | 292.9 | 270.9
937 | 833 | 230.7 | 292.2 | 270.6
938 | 834 | 230.4 | 291.4 | 270.2
939 | 835 | 230.2 | 290.7 | 269.9
940 | 836 | 230 | 289.9 | 269.5
941 | 837 | 229.8 | 289.1 | 269.2
942 | 838 | 229.6 | 288.4 | 268.8
943 | 839 | 229.3 | 287.6 | 268.5
944 | 840 | 229 | 286.9 | 268.1
945 | 841 | 228.8 | 286.1 | 267.8
946 | 842 | 228.6 | 285.4 | 267.5
947 | 843 | 228.4 | 284.7 | 267.1
948 | 844 | 228.1 | 284 | 266.8
949 | 845 | 227.9 | 283.2 | 266.5
950 | 846 | 227.7 | 282.5 | 266.2
951 | 847 | 227.5 | 281.8 | 265.8
952 | 848 | 227.2 | 281.1 | 265.5
953 | 849 | 227 | 280.5 | 265.2
954 | 850 | 226.8 | 279.8 | 264.9
955 | 851 | 226.6 | 279.1 | 264.5
956 | 852 | 226.4 | 278.4 | 264.2
957 | 853 | 226.2 | 277.7 | 263.9
958 | 854 | 226 | 277 | 263.5
959 | 855 | 225.8 | 276.4 | 263.2
960 | 856 | 225.6 | 275.7 | 262.9
961 | 857 | 225.4 | 275 | 262.6

## C2-3
Penlight Test 64 |  |  | 2006-08-29 | 9:46 |  | Vs = |  | 129 |  | R = | 100
XLPE | 2-C & Shield | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38958.406 | 1 | 0 | 38958.406 | 1 | 0 | -97.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4061 | 1 | 0 | 38958.4061 | 1 | 0 | -89 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4062 | 1 | 0 | 38958.4062 | 1 | 0 | -80.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4063 | 1 | 0 | 38958.4063 | 1 | 0 | -72.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4064 | 1 | 0 | 38958.4064 | 1 | 0 | -64 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4065 | 1 | 0 | 38958.4065 | 1 | 0 | -55.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4066 | 1 | 0 | 38958.4066 | 1 | 0 | -47 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4067 | 1 | 0 | 38958.4067 | 1 | 0 | -38.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4068 | 1 | 0 | 38958.4068 | 1 | 0 | -30.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4069 | 1 | 0 | 38958.4069 | 1 | 0 | -22 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.407 | 1 | 0 | 38958.407 | 1 | 0 | -13.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4071 | 1 | 0 | 38958.4071 | 1 | 0 | -5 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4072 | 1 | 0 | 38958.4072 | 1 | 0 | 3.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4073 | 1 | 0 | 38958.4073 | 1 | 0 | 11.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4073 | 1 | 0 | 38958.4074 | 1 | 0 | 20 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4075 | 1 | 0 | 38958.4075 | 1 | 0 | 28.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4075 | 1 | 0 | 38958.4076 | 1 | 0 | 37 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4077 | 1 | 0 | 38958.4077 | 1 | 0 | 45.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4077 | 1 | 0 | 38958.4078 | 1 | 0 | 53.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4078 | 1 | 0 | 38958.4079 | 1 | 0 | 62 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4079 | 1 | 0 | 38958.408 | 1 | 0 | 70.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.408 | 1 | 0 | 38958.4081 | 1 | 0 | 79 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4081 | 1 | 0 | 38958.4081 | 1 | 0 | 87.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4082 | 1 | 0 | 38958.4082 | 1 | 0 | 95.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4083 | 1 | 0 | 38958.4083 | 1 | 0 | 104 | 208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4084 | 1 | 0 | 38958.4084 | 1 | 0 | 112.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4085 | 1 | 0 | 38958.4085 | 1 | 0 | 121 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4086 | 1 | 0 | 38958.4086 | 1 | 0 | 129.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4087 | 1 | 0 | 38958.4087 | 1 | 0 | 137.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4088 | 1 | 0 | 38958.4088 | 1 | 0 | 146 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4089 | 1 | 0 | 38958.4089 | 1 | 0 | 154.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.409 | 1 | 0 | 38958.409 | 1 | 0 | 163 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4091 | 1 | 0 | 38958.4091 | 1 | 0 | 171.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4092 | 1 | 0 | 38958.4092 | 1 | 0 | 179.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4093 | 1 | 0 | 38958.4093 | 1 | 0 | 188 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4094 | 1 | 0 | 38958.4094 | 1 | 0 | 196.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4095 | 1 | 0 | 38958.4095 | 1 | 0 | 205 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4096 | 1 | 0 | 38958.4096 | 1 | 0 | 213.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4097 | 1 | 0 | 38958.4097 | 1 | 0 | 221.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4098 | 1 | 0 | 38958.4098 | 1 | 0 | 230 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4099 | 1 | 0 | 38958.4099 | 1 | 0 | 238.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.41 | 1 | 0 | 38958.41 | 1 | 0 | 247 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4101 | 1 | 0 | 38958.4101 | 1 | 0 | 255.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4102 | 1 | 0 | 38958.4102 | 1 | 0 | 263.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4103 | 1 | 0 | 38958.4103 | 1 | 0 | 272 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4104 | 1 | 0 | 38958.4104 | 1 | 0 | 280.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4105 | 1 | 0 | 38958.4105 | 1 | 0 | 289 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4106 | 1 | 0 | 38958.4106 | 1 | 0 | 297.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4107 | 1 | 0 | 38958.4107 | 1 | 0 | 305.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4108 | 1 | 0 | 38958.4108 | 1 | 0 | 314 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4109 | 1 | 0 | 38958.4109 | 1 | 0 | 322.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4109 | 1 | 0 | 38958.411 | 1 | 0 | 331 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4111 | 1 | 0 | 38958.4111 | 8 | 6 | 339.5 | 443.5 | 0.06105 | 0 | 0.4884 | 0.3663 | 0.0006105 | 0 | 0.004884 | 0.003663 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38958.4111 | 1134 | 1105 | 38958.4112 | 948 | 922 | 347.5 | 451.5 | 69.2308 | 67.4603 | 57.8755 | 56.2882 | 0.69231 | 0.6746 | 0.57875 | 0.56288 | 0.017705 | 0.015873 | 2408.5838 | 9487.322 | 11.282
38958.4112 | 972 | 946 | 38958.4113 | 941 | 911 | 356 | 460 | 59.3407 | 57.7534 | 57.4481 | 55.6166 | 0.59341 | 0.57753 | 0.57448 | 0.55617 | 0.015873 | 0.018315 | 22723.4273 | 4509.3437 | 20.168
38958.4113 | 1123 | 1093 | 38958.4114 | 1133 | 1103 | 364.5 | 468.5 | 68.5592 | 66.7277 | 69.1697 | 67.3382 | 0.68559 | 0.66728 | 0.6917 | 0.67338 | 0.018315 | 0.018315 | 6943.4 | 6943.4 | 9.288
38958.4114 | 1128 | 1098 | 38958.4115 | 1189 | 1167 | 373 | 477 | 68.8645 | 67.033 | 72.5885 | 71.2454 | 0.68864 | 0.67033 | 0.72589 | 0.71245 | 0.018315 | 0.013431 | 10413.1689 | 5345.5026 | 10.1007
38958.4115 | 1116 | 1167 | 38958.4116 | 1187 | 1082 | 381.5 | 485.5 | 68.1319 | 71.2454 | 72.4664 | 66.0562 | 0.68132 | 0.71245 | 0.72466 | 0.66056 | 0.031136 | 0.064103 | 450.7272 | 685.6537 | 12.7116
38958.4116 | 1019 | 1057 | 38958.4116 | 968 | 1003 | 389.5 | 493.5 | 62.21 | 64.5299 | 59.0965 | 61.2332 | 0.6221 | 0.6453 | 0.59096 | 0.61233 | 0.023199 | 0.021368 | 2954.4333 | 108943.8486 | 3.4992
38958.4117 | 999 | 1097 | 38958.4117 | 1162 | 1129 | 398 | 502 | 60.989 | 66.9719 | 70.9402 | 68.9255 | 0.60989 | 0.66972 | 0.7094 | 0.68926 | 0.059829 | 0.020147 | 314.142 | 427.4753 | 1.2574
38958.4118 | 1090 | 1053 | 38958.4118 | 1017 | 980 | 406.5 | 510.5 | 66.5446 | 64.2857 | 62.0879 | 59.8291 | 0.66545 | 0.64286 | 0.62088 | 0.59829 | 0.022589 | 0.022589 | 5610.8649 | 5610.8649 | 2.7972
38958.4119 | 1004 | 963 | 38958.4119 | 943 | 903 | 415 | 519 | 61.2943 | 58.7912 | 57.5702 | 55.1282 | 0.61294 | 0.58791 | 0.5757 | 0.55128 | 0.025031 | 0.02442 | 4528.5656 | 5832.628 | 14.9074
38958.412 | 1182 | 1176 | 38958.412 | 1190 | 1153 | 423.5 | 527.5 | 72.1612 | 71.7949 | 72.6496 | 70.3907 | 0.72161 | 0.71795 | 0.7265 | 0.70391 | 0.003663 | 0.022589 | 1307.6829 | 1803.7872 | 19.7374
38958.4121 | 1200 | 1173 | 38958.4121 | 1039 | 995 | 431.5 | 535.5 | 73.2601 | 71.6117 | 63.431 | 60.7448 | 0.7326 | 0.71612 | 0.63431 | 0.60745 | 0.016484 | 0.026862 | 824.8771 | 1401.6752 | 20.6878
38958.4122 | 1143 | 1093 | 38958.4122 | 1074 | 1130 | 440 | 544 | 69.7802 | 66.7277 | 65.5678 | 68.9866 | 0.6978 | 0.66728 | 0.65568 | 0.68987 | 0.030525 | 0.034188 | 2454.573 | 10428.2852 | 11.1447
38958.4123 | 1187 | 1165 | 38958.4123 | 1003 | 1084 | 448.5 | 552.5 | 72.4664 | 71.1233 | 61.2332 | 66.1783 | 0.72466 | 0.71123 | 0.61233 | 0.66178 | 0.013431 | 0.049451 | 335.9222 | 459.2671 | 16.8454
38958.4124 | 974 | 932 | 38958.4124 | 1188 | 1146 | 456.5 | 560.5 | 59.4628 | 56.8987 | 72.5275 | 69.9634 | 0.59463 | 0.56899 | 0.72527 | 0.69963 | 0.025641 | 0.025641 | 4931 | 4931 | 21.7709
38958.4125 | 1098 | 1136 | 38958.4125 | 1187 | 1144 | 465 | 569 | 67.033 | 69.3529 | 72.4664 | 69.8413 | 0.67033 | 0.69353 | 0.72466 | 0.69841 | 0.023199 | 0.026252 | 2633.0541 | 206864.822 | 10.6445
38958.4126 | 1148 | 1099 | 38958.4126 | 1200 | 1159 | 473.5 | 577.5 | 70.0855 | 67.094 | 73.2601 | 70.757 | 0.70085 | 0.67094 | 0.7326 | 0.70757 | 0.029915 | 0.025031 | 122315.8805 | 2279.5607 | 11.6788
38958.4127 | 934 | 933 | 38958.4127 | 1112 | 1138 | 482 | 586 | 57.0208 | 56.9597 | 67.8877 | 69.475 | 0.57021 | 0.5696 | 0.67888 | 0.69475 | 0.0006105 | 0.015873 | 509.3894 | 404.8469 | 21.1456
38958.4128 | 1052 | 948 | 38958.4128 | 1215 | 760 | 490.5 | 594.5 | 64.2247 | 57.8755 | 74.1758 | 46.398 | 0.64225 | 0.57875 | 0.74176 | 0.46398 | 0.063492 | 0.27778 | 68.7498 | 65.8651 | 4.7342
38958.4129 | 965 | 974 | 38958.4129 | 955 | 1046 | 499 | 603 | 58.9133 | 59.4628 | 58.3028 | 63.8584 | 0.58913 | 0.59463 | 0.58303 | 0.63858 | 0.0054945 | 0.055556 | 397.1601 | 347.786 | 13.8766
38958.413 | 1141 | 1039 | 38958.413 | 1073 | 1010 | 507.5 | 611.5 | 69.6581 | 63.431 | 65.5067 | 61.6606 | 0.69658 | 0.63431 | 0.65507 | 0.61661 | 0.062271 | 0.038462 | 94.6947 | 112.3878 | 3.4113
38958.4131 | 1194 | 927 | 38958.4131 | 971 | 920 | 515.5 | 619.5 | 72.8938 | 56.5934 | 59.2796 | 56.1661 | 0.72894 | 0.56593 | 0.5928 | 0.56166 | 0.163 | 0.031136 | 76.3458 | 98.9582 | 0.42817
38958.4132 | 1010 | 1035 | 38958.4132 | 940 | 901 | 524 | 628 | 61.6606 | 63.1868 | 57.3871 | 55.0061 | 0.61661 | 0.63187 | 0.57387 | 0.55006 | 0.015263 | 0.02381 | 3273.0606 | 11896.6106 | 6.5172
38958.4133 | 1179 | 1132 | 38958.4133 | 924 | 958 | 532.5 | 636.5 | 71.978 | 69.1087 | 56.4103 | 58.486 | 0.71978 | 0.69109 | 0.5641 | 0.58486 | 0.028694 | 0.020757 | 150.1066 | 196.7882 | 11.5965
38958.4134 | 1092 | 1047 | 38958.4134 | 1133 | 1159 | 541 | 645 | 66.6667 | 63.9194 | 69.1697 | 70.757 | 0.66667 | 0.63919 | 0.6917 | 0.70757 | 0.027473 | 0.015873 | 1261.0595 | 2911.1435 | 2.399
38958.4135 | 1200 | 931 | 38958.4135 | 1037 | 1042 | 549.5 | 653.5 | 73.2601 | 56.8376 | 63.3089 | 63.6142 | 0.7326 | 0.56838 | 0.63309 | 0.63614 | 0.16422 | 0.0030525 | 4.328 | 4.4702 | 0.082637
38958.4136 | 967 | 923 | 38958.4136 | 1176 | 1170 | 557.5 | 661.5 | 59.0354 | 56.3492 | 71.7949 | 71.4286 | 0.59035 | 0.56349 | 0.71795 | 0.71429 | 0.026862 | 0.003663 | 16.9969 | 13.7791 | 2.9262
38958.4137 | 1047 | 1118 | 38958.4137 | 935 | 903 | 566 | 670 | 63.9194 | 68.254 | 57.0818 | 55.1282 | 0.63919 | 0.68254 | 0.57082 | 0.55128 | 0.043346 | 0.019536 | 514.4615 | 820.7864 | 4.1444
38958.4138 | 941 | 899 | 38958.4138 | 994 | 1009 | 574.5 | 678.5 | 57.4481 | 54.884 | 60.6838 | 61.5995 | 0.57448 | 0.54884 | 0.60684 | 0.616 | 0.025641 | 0.0091575 | 1206.7338 | 1630.8884 | 28.6147
38958.4139 | 1115 | 1065 | 38958.4139 | 1152 | 1095 | 583 | 687 | 68.0708 | 65.0183 | 70.3297 | 66.8498 | 0.68071 | 0.65018 | 0.7033 | 0.6685 | 0.030525 | 0.034799 | 1636.3033 | 9688.5473 | 6.225
38958.414 | 927 | 969 | 38958.414 | 975 | 933 | 591 | 695 | 56.5934 | 59.1575 | 59.5238 | 56.9597 | 0.56593 | 0.59158 | 0.59524 | 0.5696 | 0.025641 | 0.025641 | 6277.6099 | 4193.5089 | 21.8747
38958.4141 | 1026 | 978 | 38958.4141 | 1000 | 944 | 599.5 | 703.5 | 62.6374 | 59.707 | 61.0501 | 57.6313 | 0.62637 | 0.59707 | 0.6105 | 0.57631 | 0.029304 | 0.034188 | 21342.8491 | 2279.3555 | 10.6787
38958.4142 | 983 | 934 | 38958.4142 | 929 | 981 | 608 | 712 | 60.0122 | 57.0208 | 56.7155 | 59.8901 | 0.60012 | 0.57021 | 0.56716 | 0.5989 | 0.029915 | 0.031746 | 4463.0455 | 3944.1704 | 20.4682
38958.4143 | 1194 | 1129 | 38958.4143 | 1083 | 1030 | 616.5 | 720.5 | 72.8938 | 68.9255 | 66.1172 | 62.8816 | 0.72894 | 0.68926 | 0.66117 | 0.62882 | 0.039683 | 0.032357 | 3039.8074 | 3247.3169 | 18.0431
38958.4144 | 1095 | 1146 | 38958.4144 | 1190 | 1143 | 625 | 729 | 66.8498 | 69.9634 | 72.6496 | 69.7802 | 0.6685 | 0.69963 | 0.7265 | 0.6978 | 0.031136 | 0.028694 | 5454.1289 | 3544.161 | 10.8611
38958.4145 | 1120 | 1069 | 38958.4145 | 1019 | 970 | 633.5 | 737.5 | 68.3761 | 65.2625 | 62.21 | 59.2186 | 0.68376 | 0.65263 | 0.6221 | 0.59219 | 0.031136 | 0.029915 | 1448.5486 | 6090.2121 | 6.9928
38958.4145 | 1068 | 1012 | 38958.4146 | 1076 | 1103 | 641.5 | 745.5 | 65.2015 | 61.7827 | 65.6899 | 67.3382 | 0.65201 | 0.61783 | 0.6569 | 0.67338 | 0.034188 | 0.016484 | 105.7896 | 108.6036 | 1.6987
38958.4146 | 1075 | 1021 | 38958.4147 | 1183 | 1142 | 650 | 754 | 65.6288 | 62.3321 | 72.2222 | 69.7192 | 0.65629 | 0.62332 | 0.72222 | 0.69719 | 0.032967 | 0.025031 | 2399.5301 | 9505.9002 | 1.6496
38958.4147 | 956 | 901 | 38958.4148 | 1014 | 961 | 658.5 | 762.5 | 58.3639 | 55.0061 | 61.9048 | 58.6691 | 0.58364 | 0.55006 | 0.61905 | 0.58669 | 0.033578 | 0.032357 | 3196.4384 | 4791.83 | 27.8342
38958.4148 | 1137 | 1096 | 38958.4148 | 992 | 938 | 666.5 | 770.5 | 69.4139 | 66.9109 | 60.5617 | 57.265 | 0.69414 | 0.66911 | 0.60562 | 0.57265 | 0.025031 | 0.032967 | 499.8415 | 710.4616 | 9.5964
38958.4149 | 1117 | 1075 | 38958.415 | 1178 | 1145 | 675 | 779 | 68.1929 | 65.6288 | 71.917 | 69.9023 | 0.68193 | 0.65629 | 0.71917 | 0.69902 | 0.025641 | 0.020147 | 7892.2289 | 3658.9844 | 7.1515
38958.415 | 1133 | 1096 | 38958.415 | 1190 | 928 | 683.5 | 787.5 | 69.1697 | 66.9109 | 72.6496 | 56.6545 | 0.6917 | 0.66911 | 0.7265 | 0.56654 | 0.022589 | 0.15995 | 44.4703 | 50.5824 | 3.5547
38958.4151 | 944 | 893 | 38958.4152 | 1005 | 958 | 692 | 796 | 57.6313 | 54.5177 | 61.3553 | 58.486 | 0.57631 | 0.54518 | 0.61355 | 0.58486 | 0.031136 | 0.028694 | 3025.1956 | 7226.5507 | 30.4874
38958.4152 | 1188 | 1164 | 38958.4152 | 1012 | 969 | 700.5 | 804.5 | 72.5275 | 71.0623 | 61.7827 | 59.1575 | 0.72527 | 0.71062 | 0.61783 | 0.59158 | 0.014652 | 0.026252 | 463.233 | 662.5388 | 17.8385
38958.4153 | 969 | 923 | 38958.4153 | 1189 | 1176 | 709 | 813 | 59.1575 | 56.3492 | 72.5885 | 71.7949 | 0.59158 | 0.56349 | 0.72589 | 0.71795 | 0.028083 | 0.0079365 | 92.9349 | 77.8909 | 10.4849
38958.4154 | 951 | 972 | 38958.4154 | 1057 | 1017 | 717 | 821 | 58.0586 | 59.3407 | 64.5299 | 62.0879 | 0.58059 | 0.59341 | 0.6453 | 0.62088 | 0.012821 | 0.02442 | 1428.3906 | 1610.5594 | 18.4065
38958.4155 | 1185 | 1071 | 38958.4155 | 1100 | 1063 | 725.5 | 829.5 | 72.3443 | 65.3846 | 67.1551 | 64.8962 | 0.72344 | 0.65385 | 0.67155 | 0.64896 | 0.069597 | 0.022589 | 261.5045 | 444.6247 | 10.8989
38958.4156 | 1127 | 895 | 38958.4156 | 930 | 885 | 734 | 838 | 68.8034 | 54.6398 | 56.7766 | 54.0293 | 0.68803 | 0.5464 | 0.56777 | 0.54029 | 0.14164 | 0.027473 | 159.8759 | 232.6241 | 7.1124
38958.4157 | 1148 | 892 | 38958.4157 | 958 | 920 | 742.5 | 846.5 | 70.0855 | 54.4567 | 58.486 | 56.1661 | 0.70085 | 0.54457 | 0.58486 | 0.56166 | 0.15629 | 0.023199 | 112.2955 | 147.8393 | 4.8831
38958.4158 | 966 | 924 | 38958.4158 | 1124 | 894 | 751 | 855 | 58.9744 | 56.4103 | 68.6203 | 54.5788 | 0.58974 | 0.5641 | 0.6862 | 0.54579 | 0.025641 | 0.14042 | 180.353 | 155.5592 | 14.6918
38958.4159 | 1102 | 1153 | 38958.4159 | 1061 | 1025 | 759 | 863 | 67.2772 | 70.3907 | 64.7741 | 62.5763 | 0.67277 | 0.70391 | 0.64774 | 0.62576 | 0.031136 | 0.021978 | 973.3351 | 2180.7494 | 11.7741
38958.416 | 1015 | 976 | 38958.416 | 1028 | 991 | 767.5 | 871.5 | 61.9658 | 59.5849 | 62.7595 | 60.5006 | 0.61966 | 0.59585 | 0.62759 | 0.60501 | 0.02381 | 0.022589 | 3613.2432 | 11334.0308 | 12.3927
38958.4161 | 1086 | 1054 | 38958.4161 | 1159 | 1131 | 776 | 880 | 66.3004 | 64.3468 | 70.757 | 69.0476 | 0.663 | 0.64347 | 0.70757 | 0.69048 | 0.019536 | 0.017094 | 20880.1916 | 3891.9749 | 2.4956
38958.4162 | 976 | 936 | 38958.4162 | 918 | 995 | 784.5 | 888.5 | 59.5849 | 57.1429 | 56.044 | 60.7448 | 0.59585 | 0.57143 | 0.56044 | 0.60745 | 0.02442 | 0.047009 | 1761.1063 | 3810.6366 | 20.9273
38958.4163 | 1086 | 1161 | 38958.4163 | 1025 | 986 | 793 | 897 | 66.3004 | 70.8791 | 62.5763 | 60.1954 | 0.663 | 0.70879 | 0.62576 | 0.60195 | 0.045788 | 0.02381 | 75.2363 | 89.9959 | 5.4662
38958.4164 | 1174 | 1151 | 38958.4164 | 918 | 974 | 801 | 905 | 71.6728 | 70.2686 | 56.044 | 59.4628 | 0.71673 | 0.70269 | 0.56044 | 0.59463 | 0.014042 | 0.034188 | 2.9042 | 3.5623 | 0.6335
38958.4165 | 1053 | 1141 | 38958.4165 | 946 | 902 | 809.5 | 913.5 | 64.2857 | 69.6581 | 57.7534 | 55.0672 | 0.64286 | 0.69658 | 0.57753 | 0.55067 | 0.053724 | 0.026862 | 396.0138 | 635.0444 | 6.1317
38958.4166 | 942 | 898 | 38958.4166 | 1159 | 1180 | 818 | 922 | 57.5092 | 54.823 | 70.757 | 72.0391 | 0.57509 | 0.54823 | 0.70757 | 0.72039 | 0.026862 | 0.012821 | 248.8724 | 210.536 | 20.6126
38958.4167 | 962 | 926 | 38958.4167 | 977 | 935 | 826.5 | 930.5 | 58.7302 | 56.5324 | 59.6459 | 57.0818 | 0.5873 | 0.56532 | 0.59646 | 0.57082 | 0.021978 | 0.025641 | 22036.5807 | 3008.7622 | 23.5185
38958.4168 | 977 | 1010 | 38958.4168 | 1012 | 1049 | 834.5 | 938.5 | 59.6459 | 61.6606 | 61.7827 | 64.0415 | 0.59646 | 0.61661 | 0.61783 | 0.64042 | 0.020147 | 0.022589 | 18458.2994 | 3762.2723 | 12.1542
38958.4169 | 953 | 905 | 38958.4169 | 1123 | 1172 | 843 | 947 | 58.1807 | 55.2503 | 68.5592 | 71.5507 | 0.58181 | 0.5525 | 0.68559 | 0.71551 | 0.029304 | 0.029915 | 2763.9832 | 15006.1541 | 27.9925
38958.417 | 1135 | 1102 | 38958.417 | 1064 | 1026 | 851.5 | 955.5 | 69.2918 | 67.2772 | 64.9573 | 62.6374 | 0.69292 | 0.67277 | 0.64957 | 0.62637 | 0.020147 | 0.023199 | 1442.3334 | 3165.9225 | 10.906

## C1-3
Penlight Test 64 |  |  | 2006-08-29 | 9:46 |  | Vs = |  | 129 |  | R = | 100
XLPE | 2-C & Shield | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38958.406 | 1 | 0 | 38958.406 | 1 | 0 | -100.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4061 | 1 | 0 | 38958.4061 | 1 | 0 | -92 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4062 | 1 | 0 | 38958.4062 | 1 | 0 | -83.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4062 | 1 | 0 | 38958.4063 | 1 | 0 | -75 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4064 | 1 | 0 | 38958.4064 | 1 | 0 | -66.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4064 | 1 | 0 | 38958.4065 | 1 | 0 | -58.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4065 | 1 | 0 | 38958.4066 | 1 | 0 | -50 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4066 | 1 | 0 | 38958.4067 | 1 | 0 | -41.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4067 | 1 | 0 | 38958.4068 | 1 | 0 | -33 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4068 | 1 | 0 | 38958.4069 | 1 | 0 | -24.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4069 | 1 | 0 | 38958.4069 | 1 | 0 | -16.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.407 | 1 | 0 | 38958.407 | 1 | 0 | -8 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4071 | 1 | 0 | 38958.4071 | 1 | 0 | 0.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4072 | 1 | 0 | 38958.4072 | 1 | 0 | 9 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4073 | 1 | 0 | 38958.4073 | 1 | 0 | 17.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4074 | 1 | 0 | 38958.4074 | 1 | 0 | 25.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4075 | 1 | 0 | 38958.4075 | 1 | 0 | 34 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4076 | 1 | 0 | 38958.4076 | 1 | 0 | 42.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4077 | 1 | 0 | 38958.4077 | 1 | 0 | 51 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4078 | 1 | 0 | 38958.4078 | 1 | 0 | 59.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4079 | 1 | 0 | 38958.4079 | 1 | 0 | 67.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.408 | 1 | 0 | 38958.408 | 1 | 0 | 76 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4081 | 1 | 0 | 38958.4081 | 1 | 0 | 84.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4082 | 1 | 0 | 38958.4082 | 1 | 0 | 93 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4083 | 1 | 0 | 38958.4083 | 1 | 0 | 101.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4084 | 1 | 0 | 38958.4084 | 1 | 0 | 109.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4085 | 1 | 0 | 38958.4085 | 1 | 0 | 118 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4086 | 1 | 0 | 38958.4086 | 1 | 0 | 126.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4087 | 1 | 0 | 38958.4087 | 1 | 0 | 135 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4088 | 1 | 0 | 38958.4088 | 1 | 0 | 143.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4089 | 1 | 0 | 38958.4089 | 1 | 0 | 151.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.409 | 1 | 0 | 38958.409 | 1 | 0 | 160 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4091 | 1 | 0 | 38958.4091 | 1 | 0 | 168.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4092 | 1 | 0 | 38958.4092 | 1 | 0 | 177 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4093 | 1 | 0 | 38958.4093 | 1 | 0 | 185.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4094 | 1 | 0 | 38958.4094 | 1 | 0 | 193.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4095 | 1 | 0 | 38958.4095 | 1 | 0 | 202 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4096 | 1 | 0 | 38958.4096 | 1 | 0 | 210.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4097 | 1 | 0 | 38958.4097 | 1 | 0 | 219 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4098 | 1 | 0 | 38958.4098 | 1 | 0 | 227.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4098 | 1 | 0 | 38958.4099 | 1 | 0 | 235.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4099 | 1 | 0 | 38958.41 | 1 | 0 | 244 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.41 | 1 | 0 | 38958.4101 | 1 | 0 | 252.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4101 | 1 | 0 | 38958.4102 | 1 | 0 | 261 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4102 | 1 | 0 | 38958.4103 | 1 | 0 | 269.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4103 | 1 | 0 | 38958.4103 | 1 | 0 | 277.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4104 | 1 | 0 | 38958.4105 | 1 | 0 | 286 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4105 | 1 | 0 | 38958.4105 | 1 | 0 | 294.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4106 | 1 | 0 | 38958.4106 | 1 | 0 | 303 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4107 | 1 | 0 | 38958.4107 | 1 | 0 | 311.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4108 | 1 | 0 | 38958.4108 | 1 | 0 | 319.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4109 | 1 | 0 | 38958.4109 | 1 | 0 | 328 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.411 | 6 | 6 | 38958.411 | 1 | 0 | 336.5 | 440.5 | 0.3663 | 0.3663 | 0.06105 | 0 | 0.003663 | 0.003663 | 0.0006105 | 0 | 0 | 0.0006105 | 74167806.34 | 211202 | 35000.428
38958.4111 | 163 | 165 | 38958.4111 | 1186 | 1106 | 345 | 449 | 9.9512 | 10.0733 | 72.4054 | 67.5214 | 0.099512 | 0.10073 | 0.72405 | 0.67521 | 0.001221 | 0.04884 | 14324.1959 | 1420.7641 | 1010.693
38958.4112 | 1092 | 1143 | 38958.4112 | 1040 | 1010 | 353.5 | 457.5 | 66.6667 | 69.7802 | 63.4921 | 61.6606 | 0.66667 | 0.6978 | 0.63492 | 0.61661 | 0.031136 | 0.018315 | 288.0252 | 376.6188 | 8.4328
38958.4113 | 928 | 923 | 38958.4113 | 1189 | 1184 | 361.5 | 465.5 | 56.6545 | 56.3492 | 72.5885 | 72.2833 | 0.56654 | 0.56349 | 0.72589 | 0.72283 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 28.3207
38958.4114 | 1125 | 1094 | 38958.4114 | 1111 | 1169 | 370 | 474 | 68.6813 | 66.7888 | 67.8266 | 71.3675 | 0.68681 | 0.66789 | 0.67827 | 0.71368 | 0.018926 | 0.035409 | 891.867 | 1371.2523 | 9.0289
38958.4115 | 1113 | 1084 | 38958.4115 | 1041 | 1086 | 378.5 | 482.5 | 67.9487 | 66.1783 | 63.5531 | 66.3004 | 0.67949 | 0.66178 | 0.63553 | 0.663 | 0.017705 | 0.027473 | 594.5399 | 778.7321 | 6.8656
38958.4116 | 1087 | 1136 | 38958.4116 | 1194 | 1173 | 387 | 491 | 66.3614 | 69.3529 | 72.8938 | 71.6117 | 0.66361 | 0.69353 | 0.72894 | 0.71612 | 0.029915 | 0.012821 | 1839.7973 | 16784.6186 | 9.624
38958.4117 | 1121 | 1090 | 38958.4117 | 1083 | 1128 | 395.5 | 499.5 | 68.4371 | 66.5446 | 66.1172 | 68.8645 | 0.68437 | 0.66545 | 0.66117 | 0.68864 | 0.018926 | 0.027473 | 1213.3591 | 2147.4383 | 8.589
38958.4118 | 957 | 924 | 38958.4118 | 1033 | 996 | 403.5 | 507.5 | 58.4249 | 56.4103 | 63.0647 | 60.8059 | 0.58425 | 0.5641 | 0.63065 | 0.60806 | 0.020147 | 0.022589 | 22594.4626 | 3313.7742 | 24.3748
38958.4119 | 1028 | 988 | 38958.4119 | 1095 | 1054 | 412 | 516 | 62.7595 | 60.3175 | 66.8498 | 64.3468 | 0.62759 | 0.60317 | 0.6685 | 0.64347 | 0.02442 | 0.025031 | 29708.675 | 2718.1837 | 9.4714
38958.412 | 994 | 953 | 38958.412 | 1085 | 1036 | 420.5 | 524.5 | 60.6838 | 58.1807 | 66.2393 | 63.2479 | 0.60684 | 0.58181 | 0.66239 | 0.63248 | 0.025031 | 0.029915 | 3585.3229 | 9735.5521 | 17.2437
38958.4121 | 1141 | 1095 | 38958.4121 | 1199 | 1173 | 429 | 533 | 69.6581 | 66.8498 | 73.199 | 71.6117 | 0.69658 | 0.6685 | 0.73199 | 0.71612 | 0.028083 | 0.015873 | 2917.0653 | 8636.904 | 11.1025
38958.4122 | 1172 | 1131 | 38958.4122 | 1094 | 1052 | 437.5 | 541.5 | 71.5507 | 69.0476 | 66.7888 | 64.2247 | 0.71551 | 0.69048 | 0.66789 | 0.64225 | 0.025031 | 0.025641 | 4035.067 | 6397.4387 | 16.539
38958.4123 | 945 | 919 | 38958.4123 | 972 | 883 | 445.5 | 549.5 | 57.6923 | 56.105 | 59.3407 | 53.9072 | 0.57692 | 0.56105 | 0.59341 | 0.53907 | 0.015873 | 0.054335 | 1000.0238 | 1012.1232 | 24.6603
38958.4124 | 962 | 919 | 38958.4124 | 1013 | 965 | 454 | 558 | 58.7302 | 56.105 | 61.8437 | 58.9133 | 0.5873 | 0.56105 | 0.61844 | 0.58913 | 0.026252 | 0.029304 | 11894.8471 | 2757.8241 | 24.3636
38958.4125 | 1005 | 963 | 38958.4125 | 927 | 948 | 462.5 | 566.5 | 61.3553 | 58.7912 | 56.5934 | 57.8755 | 0.61355 | 0.58791 | 0.56593 | 0.57875 | 0.025641 | 0.012821 | 1355.9042 | 2424.5834 | 14.4627
38958.4126 | 1193 | 1150 | 38958.4126 | 1188 | 1141 | 470.5 | 574.5 | 72.8327 | 70.2076 | 72.5275 | 69.6581 | 0.72833 | 0.70208 | 0.72527 | 0.69658 | 0.026252 | 0.028694 | 3230.409 | 7920.1022 | 19.7489
38958.4127 | 973 | 929 | 38958.4127 | 1170 | 1174 | 479 | 583 | 59.4017 | 56.7155 | 71.4286 | 71.6728 | 0.59402 | 0.56716 | 0.71429 | 0.71673 | 0.026862 | 0.002442 | 41.2536 | 34.1614 | 5.7838
38958.4128 | 1193 | 1160 | 38958.4128 | 1194 | 1124 | 487.5 | 591.5 | 72.8327 | 70.8181 | 72.8938 | 68.6203 | 0.72833 | 0.70818 | 0.72894 | 0.6862 | 0.020147 | 0.042735 | 900.9281 | 1678.2618 | 19.5246
38958.4129 | 1125 | 1147 | 38958.4129 | 1126 | 1071 | 496 | 600 | 68.6813 | 70.0244 | 68.7424 | 65.3846 | 0.68681 | 0.70024 | 0.68742 | 0.65385 | 0.013431 | 0.033578 | 612.1297 | 822.771 | 12.3585
38958.413 | 1004 | 1088 | 38958.413 | 975 | 924 | 504.5 | 608.5 | 61.2943 | 66.4225 | 59.5238 | 56.4103 | 0.61294 | 0.66422 | 0.59524 | 0.5641 | 0.051282 | 0.031136 | 640.2458 | 1219.487 | 1.7856
38958.4131 | 986 | 945 | 38958.4131 | 1050 | 1010 | 513 | 617 | 60.1954 | 57.6923 | 64.1026 | 61.6606 | 0.60195 | 0.57692 | 0.64103 | 0.61661 | 0.025031 | 0.02442 | 4211.6594 | 6636.014 | 18.9754
38958.4132 | 978 | 938 | 38958.4132 | 1075 | 1032 | 521.5 | 625.5 | 59.707 | 57.265 | 65.6288 | 63.0037 | 0.59707 | 0.57265 | 0.65629 | 0.63004 | 0.02442 | 0.026252 | 17707.9087 | 2792.471 | 20.2781
38958.4133 | 1026 | 1051 | 38958.4133 | 1097 | 1052 | 529.5 | 633.5 | 62.6374 | 64.1636 | 66.9719 | 64.2247 | 0.62637 | 0.64164 | 0.66972 | 0.64225 | 0.015263 | 0.027473 | 5.5628 | 5.3853 | 0.17513
38958.4133 | 1207 | 1148 | 38958.4134 | 1200 | 1153 | 538 | 642 | 73.6874 | 70.0855 | 73.2601 | 70.3907 | 0.73687 | 0.70085 | 0.7326 | 0.70391 | 0.03602 | 0.028694 | 565280.824 | 1951.0629 | 20.0507
38958.4134 | 937 | 1021 | 38958.4135 | 1180 | 1133 | 546.5 | 650.5 | 57.2039 | 62.3321 | 72.0391 | 69.1697 | 0.57204 | 0.62332 | 0.72039 | 0.6917 | 0.051282 | 0.028694 | 195.9504 | 197.8061 | 10.0848
38958.4135 | 958 | 914 | 38958.4136 | 1041 | 992 | 555 | 659 | 58.486 | 55.7998 | 63.5531 | 60.5617 | 0.58486 | 0.558 | 0.63553 | 0.60562 | 0.026862 | 0.029915 | 13912.4312 | 2560.3727 | 25.3786
38958.4136 | 941 | 898 | 38958.4137 | 1194 | 1074 | 563 | 667 | 57.4481 | 54.823 | 72.8938 | 65.5678 | 0.57448 | 0.54823 | 0.72894 | 0.65568 | 0.026252 | 0.07326 | 165.0854 | 134.6433 | 17.5099
38958.4137 | 1181 | 1132 | 38958.4137 | 995 | 1013 | 571.5 | 675.5 | 72.1001 | 69.1087 | 60.7448 | 61.8437 | 0.721 | 0.69109 | 0.60745 | 0.61844 | 0.029915 | 0.010989 | 304.2958 | 439.9748 | 14.3944
38958.4138 | 1196 | 1140 | 38958.4139 | 1207 | 978 | 580 | 684 | 73.0159 | 69.5971 | 73.6874 | 59.707 | 0.73016 | 0.69597 | 0.73687 | 0.59707 | 0.034188 | 0.1398 | 135.0693 | 183.0073 | 12.6483
38958.4139 | 1035 | 990 | 38958.4139 | 1016 | 962 | 588.5 | 692.5 | 63.1868 | 60.4396 | 62.0269 | 58.7302 | 0.63187 | 0.6044 | 0.62027 | 0.5873 | 0.027473 | 0.032967 | 5623.4459 | 3832.7669 | 8.6648
38958.414 | 953 | 907 | 38958.4141 | 994 | 941 | 597 | 701 | 58.1807 | 55.3724 | 60.6838 | 57.4481 | 0.58181 | 0.55372 | 0.60684 | 0.57448 | 0.028083 | 0.032357 | 13061.3698 | 2443.5126 | 26.7996
38958.4141 | 1106 | 1146 | 38958.4141 | 931 | 974 | 605.5 | 709.5 | 67.5214 | 69.9634 | 56.8376 | 59.4628 | 0.67521 | 0.69963 | 0.56838 | 0.59463 | 0.02442 | 0.026252 | 3710.8843 | 8909.225 | 11.9928
38958.4142 | 1020 | 924 | 38958.4142 | 975 | 925 | 613.5 | 717.5 | 62.2711 | 56.4103 | 59.5238 | 56.4713 | 0.62271 | 0.5641 | 0.59524 | 0.56471 | 0.058608 | 0.030525 | 617.2547 | 1139.6487 | 16.8166
38958.4143 | 1040 | 923 | 38958.4143 | 983 | 1000 | 622 | 726 | 63.4921 | 56.3492 | 60.0122 | 61.0501 | 0.63492 | 0.56349 | 0.60012 | 0.6105 | 0.071429 | 0.010379 | 248.4816 | 293.1733 | 12.1196
38958.4144 | 990 | 945 | 38958.4144 | 1011 | 963 | 630.5 | 734.5 | 60.4396 | 57.6923 | 61.7216 | 58.7912 | 0.6044 | 0.57692 | 0.61722 | 0.58791 | 0.027473 | 0.029304 | 7741.9816 | 3098.9285 | 18.2492
38958.4145 | 1193 | 1173 | 38958.4145 | 1171 | 1122 | 638.5 | 742.5 | 72.8327 | 71.6117 | 71.4896 | 68.4982 | 0.72833 | 0.71612 | 0.7149 | 0.68498 | 0.01221 | 0.029915 | 1163.2203 | 1985.0234 | 20.5325
38958.4146 | 1150 | 1175 | 38958.4146 | 1194 | 1044 | 647.5 | 751.5 | 70.2076 | 71.7338 | 72.8938 | 63.7363 | 0.70208 | 0.71734 | 0.72894 | 0.63736 | 0.015263 | 0.091575 | 222.9108 | 288.6833 | 13.3993
38958.4147 | 1200 | 1146 | 38958.4147 | 989 | 1004 | 655.5 | 759.5 | 73.2601 | 69.9634 | 60.3785 | 61.2943 | 0.7326 | 0.69963 | 0.60379 | 0.61294 | 0.032967 | 0.0091575 | 285.7725 | 431.6515 | 16.5059
38958.4148 | 1173 | 1136 | 38958.4148 | 1191 | 928 | 664 | 768 | 71.6117 | 69.3529 | 72.7106 | 56.6545 | 0.71612 | 0.69353 | 0.72711 | 0.56654 | 0.022589 | 0.16056 | 70.8439 | 88.0696 | 8.0787
38958.4149 | 1144 | 1178 | 38958.4149 | 1093 | 1050 | 672.5 | 776.5 | 69.8413 | 71.917 | 66.7277 | 64.1026 | 0.69841 | 0.71917 | 0.66728 | 0.64103 | 0.020757 | 0.026252 | 1555.5953 | 4163.6402 | 17.3242
38958.415 | 1185 | 1178 | 38958.415 | 1121 | 1082 | 680.5 | 784.5 | 72.3443 | 71.917 | 68.4371 | 66.0562 | 0.72344 | 0.71917 | 0.68437 | 0.66056 | 0.0042735 | 0.02381 | 907.6949 | 1236.8857 | 19.6334
38958.4151 | 1032 | 995 | 38958.4151 | 1019 | 1051 | 689.5 | 793.5 | 63.0037 | 60.7448 | 62.21 | 64.1636 | 0.63004 | 0.60745 | 0.6221 | 0.64164 | 0.022589 | 0.019536 | 1584.8665 | 3188.1934 | 8.3823
38958.4152 | 1144 | 1182 | 38958.4152 | 1000 | 1102 | 697.5 | 801.5 | 69.8413 | 72.1612 | 61.0501 | 67.2772 | 0.69841 | 0.72161 | 0.6105 | 0.67277 | 0.023199 | 0.062271 | 286.224 | 393.2751 | 14.3658
38958.4153 | 1188 | 1174 | 38958.4153 | 958 | 910 | 706 | 810 | 72.5275 | 71.6728 | 58.486 | 55.5556 | 0.72527 | 0.71673 | 0.58486 | 0.55556 | 0.008547 | 0.029304 | 0.19063 | 0.24195 | 0.051189
38958.4154 | 1184 | 1163 | 38958.4154 | 1074 | 1038 | 714.5 | 818.5 | 72.2833 | 71.0012 | 65.5678 | 63.37 | 0.72283 | 0.71001 | 0.65568 | 0.6337 | 0.012821 | 0.021978 | 1206.6872 | 2077.1826 | 19.1946
38958.4155 | 954 | 910 | 38958.4155 | 1173 | 1147 | 722.5 | 826.5 | 58.2418 | 55.5556 | 71.6117 | 70.0244 | 0.58242 | 0.55556 | 0.71612 | 0.70024 | 0.026862 | 0.015873 | 258.3599 | 224.9098 | 18.9425
38958.4156 | 1084 | 1049 | 38958.4156 | 1079 | 1154 | 731 | 835 | 66.1783 | 64.0415 | 65.873 | 70.4518 | 0.66178 | 0.64042 | 0.65873 | 0.70452 | 0.021368 | 0.045788 | 344.8774 | 398.2949 | 1.5224
38958.4157 | 1183 | 922 | 38958.4157 | 1179 | 1155 | 739.5 | 843.5 | 72.2222 | 56.2882 | 71.978 | 70.5128 | 0.72222 | 0.56288 | 0.71978 | 0.70513 | 0.15934 | 0.014652 | 88.5412 | 116.8004 | 0.46863
38958.4158 | 938 | 957 | 38958.4158 | 933 | 884 | 748 | 852 | 57.265 | 58.4249 | 56.9597 | 53.9683 | 0.57265 | 0.58425 | 0.5696 | 0.53968 | 0.0116 | 0.029915 | 2208.8322 | 2798.5372 | 21.9956
38958.4159 | 936 | 1042 | 38958.4159 | 1084 | 1048 | 756.5 | 860.5 | 57.1429 | 63.6142 | 66.1783 | 63.9805 | 0.57143 | 0.63614 | 0.66178 | 0.6398 | 0.064713 | 0.021978 | 166.5096 | 173.4128 | 8.2185
38958.416 | 1152 | 1179 | 38958.416 | 1001 | 910 | 764.5 | 868.5 | 70.3297 | 71.978 | 61.1111 | 55.5556 | 0.7033 | 0.71978 | 0.61111 | 0.55556 | 0.016484 | 0.055556 | 5.4573 | 6.7054 | 1.1618
38958.4161 | 1104 | 1071 | 38958.4161 | 1172 | 1178 | 773 | 877 | 67.3993 | 65.3846 | 71.5507 | 71.917 | 0.67399 | 0.65385 | 0.71551 | 0.71917 | 0.020147 | 0.003663 | 1267.3961 | 2297.6114 | 5.5457
38958.4162 | 1027 | 988 | 38958.4162 | 943 | 900 | 781.5 | 885.5 | 62.6984 | 60.3175 | 57.5702 | 54.9451 | 0.62698 | 0.60317 | 0.5757 | 0.54945 | 0.02381 | 0.026252 | 12122.3956 | 3288.8156 | 9.6283
38958.4163 | 1073 | 1038 | 38958.4163 | 1172 | 1176 | 790 | 894 | 65.5067 | 63.37 | 71.5507 | 71.7949 | 0.65507 | 0.6337 | 0.71551 | 0.71795 | 0.021368 | 0.002442 | 840.7827 | 1170.2811 | 0.17929
38958.4164 | 1002 | 964 | 38958.4164 | 1134 | 1109 | 798.5 | 902.5 | 61.1722 | 58.8523 | 69.2308 | 67.7045 | 0.61172 | 0.58852 | 0.69231 | 0.67705 | 0.023199 | 0.015263 | 142.2204 | 129.7101 | 8.6118
38958.4165 | 911 | 976 | 38958.4165 | 964 | 924 | 806.5 | 910.5 | 55.6166 | 59.5849 | 58.8523 | 56.4103 | 0.55617 | 0.59585 | 0.58852 | 0.5641 | 0.039683 | 0.02442 | 1344.6585 | 4001.2774 | 22.5931
38958.4166 | 1133 | 1103 | 38958.4166 | 989 | 1020 | 815 | 919 | 69.1697 | 67.3382 | 60.3785 | 62.2711 | 0.6917 | 0.67338 | 0.60379 | 0.62271 | 0.018315 | 0.018926 | 4974.1574 | 10711.0583 | 11.0465
38958.4167 | 970 | 936 | 38958.4167 | 1120 | 1170 | 823.5 | 927.5 | 59.2186 | 57.1429 | 68.3761 | 71.4286 | 0.59219 | 0.57143 | 0.68376 | 0.71429 | 0.020757 | 0.030525 | 306.2111 | 275.8796 | 16.2333
38958.4167 | 1166 | 1124 | 38958.4168 | 983 | 946 | 832 | 936 | 71.1844 | 68.6203 | 60.0122 | 57.7534 | 0.71184 | 0.6862 | 0.60012 | 0.57753 | 0.025641 | 0.022589 | 116.5967 | 145.9327 | 9.3432
38958.4169 | 1076 | 1045 | 38958.4169 | 925 | 880 | 840.5 | 944.5 | 65.6899 | 63.7973 | 56.4713 | 53.7241 | 0.6569 | 0.63797 | 0.56471 | 0.53724 | 0.018926 | 0.027473 | 3063.8374 | 36704.0554 | 0.76156
38958.4169 | 998 | 959 | 38958.417 | 1181 | 1172 | 848.5 | 952.5 | 60.928 | 58.547 | 72.1001 | 71.5507 | 0.60928 | 0.58547 | 0.721 | 0.71551 | 0.02381 | 0.0054945 | 305.6777 | 294.3796 | 12.1438

## C1-2
Penlight Test 64 |  |  | 2006-08-29 | 9:46 |  | Vs = |  | 129 |  | R = | 100
XLPE | 2-C & Shield | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38958.4059 | 1 | 0 | 38958.4059 | 1 | 0 | -103 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.406 | 1 | 0 | 38958.406 | 1 | 0 | -94.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4061 | 1 | 0 | 38958.4061 | 1 | 0 | -86.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4062 | 1 | 0 | 38958.4062 | 1 | 0 | -78 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4063 | 1 | 0 | 38958.4063 | 1 | 0 | -69.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4064 | 1 | 0 | 38958.4064 | 1 | 0 | -61 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4065 | 1 | 0 | 38958.4065 | 1 | 0 | -52.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4066 | 1 | 0 | 38958.4066 | 1 | 0 | -44.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4067 | 1 | 0 | 38958.4067 | 1 | 0 | -36 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4068 | 1 | 0 | 38958.4068 | 1 | 0 | -27.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4069 | 1 | 0 | 38958.4069 | 1 | 0 | -19 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.407 | 1 | 0 | 38958.407 | 1 | 0 | -10.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4071 | 1 | 0 | 38958.4071 | 1 | 0 | -2.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4072 | 1 | 0 | 38958.4072 | 1 | 0 | 6 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4073 | 1 | 0 | 38958.4073 | 1 | 0 | 14.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4074 | 1 | 0 | 38958.4074 | 1 | 0 | 23 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4075 | 1 | 0 | 38958.4075 | 1 | 0 | 31.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4076 | 1 | 0 | 38958.4076 | 1 | 0 | 39.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4077 | 1 | 0 | 38958.4077 | 1 | 0 | 48.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4078 | 1 | 0 | 38958.4078 | 1 | 0 | 56.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4079 | 1 | 0 | 38958.4079 | 1 | 0 | 65 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.408 | 1 | 0 | 38958.408 | 1 | 0 | 73.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4081 | 1 | 0 | 38958.4081 | 1 | 0 | 81.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4082 | 1 | 0 | 38958.4082 | 1 | 0 | 90 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4083 | 1 | 0 | 38958.4083 | 1 | 0 | 98.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4084 | 1 | 0 | 38958.4084 | 1 | 0 | 107 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4085 | 1 | 0 | 38958.4085 | 1 | 0 | 115.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4086 | 2 | 0 | 38958.4086 | 1 | 0 | 123.5 | 227.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38958.4086 | 1 | 0 | 38958.4087 | 1 | 0 | 132 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4088 | 1 | 0 | 38958.4088 | 1 | 0 | 140.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4088 | 1 | 0 | 38958.4089 | 1 | 0 | 149 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4089 | 1 | 0 | 38958.409 | 1 | 0 | 157.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.409 | 1 | 0 | 38958.4091 | 1 | 0 | 165.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4091 | 1 | 0 | 38958.4092 | 1 | 0 | 174 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4092 | 1 | 0 | 38958.4092 | 1 | 0 | 182.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4093 | 1 | 0 | 38958.4094 | 1 | 0 | 191 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4094 | 1 | 0 | 38958.4094 | 1 | 0 | 199.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4095 | 1 | 0 | 38958.4095 | 1 | 0 | 207.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4096 | 1 | 0 | 38958.4096 | 1 | 0 | 216 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4097 | 1 | 0 | 38958.4097 | 1 | 0 | 224.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4098 | 1 | 0 | 38958.4098 | 1 | 0 | 233 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4099 | 1 | 0 | 38958.4099 | 1 | 0 | 241.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.41 | 1 | 0 | 38958.41 | 1 | 0 | 249.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4101 | 1 | 0 | 38958.4101 | 1 | 0 | 258 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4102 | 1 | 0 | 38958.4102 | 1 | 0 | 266.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4103 | 1 | 0 | 38958.4103 | 1 | 0 | 275 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4104 | 1 | 0 | 38958.4104 | 1 | 0 | 283.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4105 | 1 | 0 | 38958.4105 | 1 | 0 | 291.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4106 | 1 | 0 | 38958.4106 | 1 | 0 | 300 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4107 | 1 | 0 | 38958.4107 | 1 | 0 | 308.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4108 | 1 | 0 | 38958.4108 | 1 | 0 | 317 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4109 | 1 | 0 | 38958.4109 | 1 | 0 | 325 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.411 | 1 | 0 | 38958.411 | 1 | 0 | 333.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.4111 | 40 | 41 | 38958.4111 | 314 | 308 | 342 | 446 | 2.442 | 2.5031 | 19.1697 | 18.8034 | 0.02442 | 0.025031 | 0.1917 | 0.18803 | 0.0006105 | 0.003663 | 239325.7293 | 30640.8876 | 4940.024
38958.4112 | 1182 | 1120 | 38958.4112 | 965 | 942 | 350.5 | 454.5 | 72.1612 | 68.3761 | 58.9133 | 57.5092 | 0.72161 | 0.68376 | 0.58913 | 0.57509 | 0.037851 | 0.014042 | 30.362 | 37.2787 | 4.582
38958.4113 | 1024 | 994 | 38958.4113 | 1086 | 1058 | 359 | 463 | 62.5153 | 60.6838 | 66.3004 | 64.591 | 0.62515 | 0.60684 | 0.663 | 0.64591 | 0.018315 | 0.017094 | 2242.4401 | 5354.4315 | 9.3841
38958.4114 | 1045 | 1016 | 38958.4114 | 1098 | 1147 | 367.5 | 471.5 | 63.7973 | 62.0269 | 67.033 | 70.0244 | 0.63797 | 0.62027 | 0.67033 | 0.70024 | 0.017705 | 0.029915 | 399.4921 | 426.2739 | 4.1472
38958.4115 | 978 | 1016 | 38958.4115 | 940 | 912 | 375.5 | 479.5 | 59.707 | 62.0269 | 57.3871 | 55.6777 | 0.59707 | 0.62027 | 0.57387 | 0.55678 | 0.023199 | 0.017094 | 2510.1704 | 14078.1641 | 11.6319
38958.4116 | 954 | 925 | 38958.4116 | 1138 | 1178 | 384 | 488 | 58.2418 | 56.4713 | 69.475 | 71.917 | 0.58242 | 0.56471 | 0.69475 | 0.71917 | 0.017705 | 0.02442 | 463.2707 | 418.2076 | 20.4174
38958.4117 | 1190 | 1071 | 38958.4117 | 973 | 1008 | 392.5 | 496.5 | 72.6496 | 65.3846 | 59.4017 | 61.5385 | 0.7265 | 0.65385 | 0.59402 | 0.61538 | 0.07265 | 0.021368 | 27.8137 | 33.4731 | 3.4651
38958.4118 | 1193 | 1177 | 38958.4118 | 929 | 923 | 401 | 505 | 72.8327 | 71.8559 | 56.7155 | 56.3492 | 0.72833 | 0.71856 | 0.56716 | 0.56349 | 0.009768 | 0.003663 | 24.8359 | 31.9109 | 5.2818
38958.4119 | 1185 | 1151 | 38958.4119 | 968 | 931 | 409 | 513 | 72.3443 | 70.2686 | 59.0965 | 56.8376 | 0.72344 | 0.70269 | 0.59096 | 0.56838 | 0.020757 | 0.022589 | 245.5895 | 334.7152 | 14.9163
38958.412 | 1116 | 1150 | 38958.412 | 963 | 924 | 417.5 | 521.5 | 68.1319 | 70.2076 | 58.7912 | 56.4103 | 0.68132 | 0.70208 | 0.58791 | 0.5641 | 0.020757 | 0.02381 | 1460.9196 | 3358.0508 | 12.9179
38958.412 | 1097 | 1132 | 38958.4121 | 1059 | 1021 | 426 | 530 | 66.9719 | 69.1087 | 64.652 | 62.3321 | 0.66972 | 0.69109 | 0.64652 | 0.62332 | 0.021368 | 0.023199 | 1385.5093 | 2953.1554 | 9.91
38958.4122 | 1057 | 1092 | 38958.4122 | 1095 | 1135 | 434.5 | 538.5 | 64.5299 | 66.6667 | 66.8498 | 69.2918 | 0.6453 | 0.66667 | 0.6685 | 0.69292 | 0.021368 | 0.02442 | 2042.0474 | 6533.5289 | 3.2452
38958.4122 | 934 | 945 | 38958.4123 | 1016 | 953 | 443 | 547 | 57.0208 | 57.6923 | 62.0269 | 58.1807 | 0.57021 | 0.57692 | 0.62027 | 0.58181 | 0.0067155 | 0.038462 | 827.5582 | 718.7966 | 21.7396
38958.4123 | 1052 | 1006 | 38958.4124 | 1034 | 925 | 451.5 | 555.5 | 64.2247 | 61.4164 | 63.1258 | 56.4713 | 0.64225 | 0.61416 | 0.63126 | 0.56471 | 0.028083 | 0.066545 | 357.0728 | 400.5672 | 4.3766
38958.4124 | 1083 | 916 | 38958.4125 | 947 | 957 | 459.5 | 563.5 | 66.1172 | 55.9219 | 57.8144 | 58.4249 | 0.66117 | 0.55922 | 0.57814 | 0.58425 | 0.10195 | 0.006105 | 174.8236 | 216.9707 | 8.5205
38958.4125 | 1064 | 1022 | 38958.4126 | 1094 | 1047 | 468.5 | 572.5 | 64.9573 | 62.3932 | 66.7888 | 63.9194 | 0.64957 | 0.62393 | 0.66789 | 0.63919 | 0.025641 | 0.028694 | 20.279 | 19.9184 | 0.43914
38958.4126 | 1152 | 1168 | 38958.4127 | 930 | 941 | 476.5 | 580.5 | 70.3297 | 71.3065 | 56.7766 | 57.4481 | 0.7033 | 0.71306 | 0.56777 | 0.57448 | 0.009768 | 0.0067155 | 621.9719 | 843.2494 | 15.8422
38958.4127 | 1044 | 994 | 38958.4127 | 934 | 934 | 484.5 | 588.5 | 63.7363 | 60.6838 | 57.0208 | 57.0208 | 0.63736 | 0.60684 | 0.57021 | 0.57021 | 0.030525 | 0 | 563.1795 | 710.9207 | 6.6166
38958.4128 | 1043 | 868 | 38958.4128 | 1134 | 971 | 493 | 597 | 63.6752 | 52.9915 | 69.2308 | 59.2796 | 0.63675 | 0.52991 | 0.69231 | 0.5928 | 0.10684 | 0.099512 | 686.0325 | 4561.7451 | 22.7749
38958.4129 | 934 | 948 | 38958.4129 | 1180 | 1161 | 501.5 | 605.5 | 57.0208 | 57.8755 | 72.0391 | 70.8791 | 0.57021 | 0.57875 | 0.72039 | 0.70879 | 0.008547 | 0.0116 | 11.6928 | 9.4147 | 2.0969
38958.413 | 1006 | 962 | 38958.413 | 948 | 902 | 510 | 614 | 61.4164 | 58.7302 | 57.8755 | 55.0672 | 0.61416 | 0.5873 | 0.57875 | 0.55067 | 0.026862 | 0.028083 | 6020.5973 | 3755.9363 | 14.6839
38958.4131 | 1114 | 905 | 38958.4131 | 1067 | 1010 | 518.5 | 622.5 | 68.0098 | 55.2503 | 65.1404 | 61.6606 | 0.6801 | 0.5525 | 0.6514 | 0.61661 | 0.12759 | 0.034799 | 78.3945 | 84.9487 | 4.7717
38958.4132 | 988 | 943 |  | 1130 | 1087 | 526 | 630 | 60.3175 | 57.5702 | 68.9866 | 66.3614 | 0.60317 | 0.5757 | 0.68987 | 0.66361 | 0.027473 | 0.026252 | 2193.6087 | 15000.9572 | 19.1744
38958.4133 | 983 | 941 | 38958.4133 | 1192 | 1163 | 535.5 | 639.5 | 60.0122 | 57.4481 | 72.7717 | 71.0012 | 0.60012 | 0.57448 | 0.72772 | 0.71001 | 0.025641 | 0.017705 | 470.5348 | 474.8771 | 16.593
38958.4134 | 1109 | 1139 | 38958.4134 | 1047 | 1001 | 543.5 | 647.5 | 67.7045 | 69.536 | 63.9194 | 61.1111 | 0.67705 | 0.69536 | 0.63919 | 0.61111 | 0.018315 | 0.028083 | 342.0969 | 432.2745 | 9.6243
38958.4135 | 1163 | 1165 | 38958.4135 | 941 | 896 | 552 | 656 | 71.0012 | 71.1233 | 57.4481 | 54.7009 | 0.71001 | 0.71123 | 0.57448 | 0.54701 | 0.001221 | 0.027473 | 138.9798 | 170.9297 | 11.6421
38958.4136 | 1194 | 922 | 38958.4136 | 1014 | 1096 | 560.5 | 664.5 | 72.8938 | 56.2882 | 61.9048 | 66.9109 | 0.72894 | 0.56288 | 0.61905 | 0.66911 | 0.16606 | 0.050061 | 0.21969 | 0.22055 | 0.00071127
38958.4137 | 1172 | 1149 | 38958.4137 | 1108 | 1143 | 568.5 | 672.5 | 71.5507 | 70.1465 | 67.6435 | 69.7802 | 0.71551 | 0.70147 | 0.67643 | 0.6978 | 0.014042 | 0.021368 | 2149.5495 | 5530.0086 | 17.7794
38958.4138 | 1040 | 990 | 38958.4138 | 1082 | 1034 | 577 | 681 | 63.4921 | 60.4396 | 66.0562 | 63.1258 | 0.63492 | 0.6044 | 0.66056 | 0.63126 | 0.030525 | 0.029304 | 2050.2377 | 42373.4005 | 8.3661
38958.4139 | 1027 | 970 | 38958.4139 | 926 | 939 | 585.5 | 689.5 | 62.6984 | 59.2186 | 56.5324 | 57.326 | 0.62698 | 0.59219 | 0.56532 | 0.57326 | 0.034799 | 0.0079365 | 687.1871 | 960.0303 | 10.8325
38958.414 | 1181 | 1169 | 38958.414 | 1204 | 1156 | 594 | 698 | 72.1001 | 71.3675 | 73.5043 | 70.5739 | 0.721 | 0.71368 | 0.73504 | 0.70574 | 0.007326 | 0.029304 | 1115.2594 | 1633.3706 | 19.1025
38958.4141 | 1077 | 1095 | 38958.4141 | 1179 | 1116 | 602.5 | 706.5 | 65.7509 | 66.8498 | 71.978 | 68.1319 | 0.65751 | 0.6685 | 0.71978 | 0.68132 | 0.010989 | 0.038462 | 487.5287 | 562.9692 | 4.5739
38958.4142 | 1096 | 1040 | 38958.4142 | 1177 | 1152 | 611 | 715 | 66.9109 | 63.4921 | 71.8559 | 70.3297 | 0.66911 | 0.63492 | 0.71856 | 0.7033 | 0.034188 | 0.015263 | 931.7024 | 1956.4622 | 2.1022
38958.4143 | 1148 | 1164 | 38958.4143 | 1165 | 1169 | 619.5 | 723.5 | 70.0855 | 71.0623 | 71.1233 | 71.3675 | 0.70085 | 0.71062 | 0.71123 | 0.71368 | 0.009768 | 0.002442 | 4241.2877 | 17236.7957 | 16.9959
38958.4144 | 1189 | 1169 | 38958.4144 | 1104 | 1058 | 627.5 | 731.5 | 72.5885 | 71.3675 | 67.3993 | 64.591 | 0.72589 | 0.71368 | 0.67399 | 0.64591 | 0.01221 | 0.028083 | 906.2659 | 1426.3222 | 19.5834
38958.4145 | 1190 | 1144 | 38958.4145 | 938 | 877 | 636 | 740 | 72.6496 | 69.8413 | 57.265 | 53.5409 | 0.7265 | 0.69841 | 0.57265 | 0.53541 | 0.028083 | 0.037241 | 516.6119 | 862.303 | 17.3091
38958.4146 | 1195 | 1162 | 38958.4146 | 1058 | 1003 | 644.5 | 748.5 | 72.9548 | 70.9402 | 64.591 | 61.2332 | 0.72955 | 0.7094 | 0.64591 | 0.61233 | 0.020147 | 0.033578 | 676.9583 | 1132.4483 | 19.2929
38958.4147 | 1064 | 1014 | 38958.4147 | 1016 | 1033 | 652.5 | 756.5 | 64.9573 | 61.9048 | 62.0269 | 63.0647 | 0.64957 | 0.61905 | 0.62027 | 0.63065 | 0.030525 | 0.010379 | 274.7293 | 305.571 | 2.6021
38958.4148 | 1040 | 988 | 38958.4148 | 978 | 924 | 661 | 765 | 63.4921 | 60.3175 | 59.707 | 56.4103 | 0.63492 | 0.60317 | 0.59707 | 0.5641 | 0.031746 | 0.032967 | 5379.8731 | 3082.2102 | 8.3348
38958.4149 | 945 | 1045 | 38958.4149 | 1110 | 1162 | 669.5 | 773.5 | 57.6923 | 63.7973 | 67.7656 | 70.9402 | 0.57692 | 0.63797 | 0.67766 | 0.7094 | 0.06105 | 0.031746 | 92.9955 | 90.3982 | 5.5893
38958.415 | 1000 | 1023 | 38958.415 | 1062 | 1099 | 678 | 782 | 61.0501 | 62.4542 | 64.8352 | 67.094 | 0.6105 | 0.62454 | 0.64835 | 0.67094 | 0.014042 | 0.022589 | 332.8762 | 328.5538 | 6.7463
38958.4151 | 951 | 1055 | 38958.4151 | 943 | 893 | 686.5 | 790.5 | 58.0586 | 64.4078 | 57.5702 | 54.5177 | 0.58059 | 0.64408 | 0.5757 | 0.54518 | 0.063492 | 0.030525 | 605.6275 | 1200.6317 | 9.3641
38958.4152 | 1050 | 1004 | 38958.4152 | 960 | 909 | 695 | 799 | 64.1026 | 61.2943 | 58.6081 | 55.4945 | 0.64103 | 0.61294 | 0.58608 | 0.55495 | 0.028083 | 0.031136 | 17060.5433 | 2524.5711 | 5.6545
38958.4153 | 919 | 928 | 38958.4153 | 1114 | 1169 | 703 | 807 | 56.105 | 56.6545 | 68.0098 | 71.3675 | 0.56105 | 0.56654 | 0.6801 | 0.71368 | 0.0054945 | 0.033578 | 256.8868 | 203.5963 | 19.2238
38958.4154 | 931 | 883 | 38958.4154 | 1113 | 1078 | 711.5 | 815.5 | 56.8376 | 53.9072 | 67.9487 | 65.812 | 0.56838 | 0.53907 | 0.67949 | 0.65812 | 0.029304 | 0.021368 | 1346.3394 | 2218.8661 | 32.4037
38958.4155 | 1074 | 1035 | 38958.4155 | 1139 | 1109 | 720 | 824 | 65.5678 | 63.1868 | 69.536 | 67.7045 | 0.65568 | 0.63187 | 0.69536 | 0.67705 | 0.02381 | 0.018315 | 1957.5183 | 7351.6718 | 0.38319
38958.4156 | 1062 | 1026 | 38958.4156 | 1050 | 1014 | 728.5 | 832.5 | 64.8352 | 62.6374 | 64.1026 | 61.9048 | 0.64835 | 0.62637 | 0.64103 | 0.61905 | 0.021978 | 0.021978 | 5769.5 | 5769.5 | 2.397
38958.4156 | 925 | 942 | 38958.4157 | 1158 | 1182 | 737 | 841 | 56.4713 | 57.5092 | 70.696 | 72.1612 | 0.56471 | 0.57509 | 0.70696 | 0.72161 | 0.010379 | 0.014652 | 331.7117 | 276.1262 | 19.1732
38958.4158 | 1168 | 1129 | 38958.4158 | 1009 | 1041 | 745.5 | 849.5 | 71.3065 | 68.9255 | 61.5995 | 63.5531 | 0.71306 | 0.68926 | 0.616 | 0.63553 | 0.02381 | 0.019536 | 1904.6357 | 10634.0526 | 16.144
38958.4158 | 1071 | 899 | 38958.4159 | 983 | 941 | 753.5 | 857.5 | 65.3846 | 54.884 | 60.0122 | 57.4481 | 0.65385 | 0.54884 | 0.60012 | 0.57448 | 0.10501 | 0.025641 | 211.7068 | 280.7625 | 11.7306
38958.4159 | 928 | 883 | 38958.416 | 976 | 1005 | 762 | 866 | 56.6545 | 53.9072 | 59.5849 | 61.3553 | 0.56654 | 0.53907 | 0.59585 | 0.61355 | 0.027473 | 0.017705 | 1799.6723 | 4235.7367 | 33.415
38958.416 | 990 | 953 | 38958.4161 | 994 | 1098 | 770.5 | 874.5 | 60.4396 | 58.1807 | 60.6838 | 67.033 | 0.6044 | 0.58181 | 0.60684 | 0.67033 | 0.022589 | 0.063492 | 364.3982 | 351.4208 | 13.8884
38958.4161 | 1024 | 989 | 38958.4162 | 954 | 977 | 779 | 883 | 62.5153 | 60.3785 | 58.2418 | 59.6459 | 0.62515 | 0.60379 | 0.58242 | 0.59646 | 0.021368 | 0.014042 | 1660.8561 | 3235.2191 | 9.81
38958.4162 | 951 | 908 | 38958.4163 | 1148 | 1173 | 787.5 | 891.5 | 58.0586 | 55.4335 | 70.0855 | 71.6117 | 0.58059 | 0.55433 | 0.70085 | 0.71612 | 0.026252 | 0.015263 | 299.4731 | 263.172 | 20.2726
38958.4163 | 1013 | 976 | 38958.4163 | 953 | 912 | 795.5 | 899.5 | 61.8437 | 59.5849 | 58.1807 | 55.6777 | 0.61844 | 0.59585 | 0.58181 | 0.55678 | 0.022589 | 0.025031 | 13286.3251 | 3398.2506 | 12.3437
38958.4164 | 1135 | 1108 | 38958.4164 | 1171 | 894 | 804 | 908 | 69.2918 | 67.6435 | 71.4896 | 54.5788 | 0.69292 | 0.67643 | 0.7149 | 0.54579 | 0.016484 | 0.16911 | 24.5976 | 28.0571 | 2.5703
38958.4165 | 986 | 948 | 38958.4165 | 1075 | 1123 | 812.5 | 916.5 | 60.1954 | 57.8755 | 65.6288 | 68.5592 | 0.60195 | 0.57875 | 0.65629 | 0.68559 | 0.023199 | 0.029304 | 1737.269 | 3527.6934 | 18.3634
38958.4166 | 923 | 1026 | 38958.4166 | 982 | 945 | 821 | 925 | 56.3492 | 62.6374 | 59.9512 | 57.6923 | 0.56349 | 0.62637 | 0.59951 | 0.57692 | 0.062882 | 0.022589 | 479.2458 | 706.0719 | 14.0031
38958.4167 | 1119 | 1168 | 38958.4167 | 1176 | 1156 | 829 | 933 | 68.315 | 71.3065 | 71.7949 | 70.5739 | 0.68315 | 0.71306 | 0.71795 | 0.70574 | 0.029915 | 0.01221 | 1856.8403 | 25767.3026 | 14.838
38958.4168 | 1169 | 1176 | 38958.4168 | 942 | 899 | 837.5 | 941.5 | 71.3675 | 71.7949 | 57.5092 | 54.884 | 0.71368 | 0.71795 | 0.57509 | 0.54884 | 0.0042735 | 0.026252 | 113.8573 | 143.0438 | 11.6099
38958.4169 | 1080 | 1045 | 38958.4169 | 1110 | 1162 | 846 | 950 | 65.9341 | 63.7973 | 67.7656 | 70.9402 | 0.65934 | 0.63797 | 0.67766 | 0.7094 | 0.021368 | 0.031746 | 926.2114 | 1365.446 | 1.0682

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 64 |  |  | 2006-08-29 | 9:46
38958.4059 | 1 | 0 | 1 | XLPE | 2-C & Shield | Tray
38958.406 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38958.4061 | 1 | 0 | 1
38958.4062 | 1 | 0 | 1
38958.4063 | 1 | 0 | 1
38958.4064 | 1 | 0 | 1
38958.4065 | 1 | 0 | 1
38958.4066 | 1 | 0 | 1
38958.4067 | 1 | 0 | 1
38958.4068 | 1 | 0 | 1
38958.4069 | 1 | 0 | 1
38958.407 | 1 | 0 | 1
38958.4071 | 1 | 0 | 1
38958.4072 | 1 | 0 | 1
38958.4073 | 1 | 0 | 1
38958.4074 | 1 | 0 | 1
38958.4075 | 1 | 0 | 1
38958.4076 | 1 | 0 | 1
38958.4077 | 1 | 0 | 1
38958.4078 | 1 | 0 | 1
38958.4079 | 1 | 0 | 1
38958.408 | 1 | 0 | 1
38958.4081 | 1 | 0 | 1
38958.4082 | 1 | 0 | 1
38958.4083 | 1 | 0 | 1
38958.4084 | 1 | 0 | 1
38958.4085 | 1 | 0 | 1
38958.4086 | 2 | 0 | 1
38958.4086 | 1 | 0 | 1
38958.4088 | 1 | 0 | 1
38958.4088 | 1 | 0 | 1
38958.4089 | 1 | 0 | 1
38958.409 | 1 | 0 | 1
38958.4091 | 1 | 0 | 1
38958.4092 | 1 | 0 | 1
38958.4093 | 1 | 0 | 1
38958.4094 | 1 | 0 | 1
38958.4095 | 1 | 0 | 1
38958.4096 | 1 | 0 | 1
38958.4097 | 1 | 0 | 1
38958.4098 | 1 | 0 | 1
38958.4099 | 1 | 0 | 1
38958.41 | 1 | 0 | 1
38958.4101 | 1 | 0 | 1
38958.4102 | 1 | 0 | 1
38958.4103 | 1 | 0 | 1
38958.4104 | 1 | 0 | 1
38958.4105 | 1 | 0 | 1
38958.4106 | 1 | 0 | 1
38958.4107 | 1 | 0 | 1
38958.4108 | 1 | 0 | 1
38958.4109 | 1 | 0 | 1
38958.411 | 1 | 0 | 1
38958.4111 | 40 | 41 | 1
38958.4112 | 1182 | 1120 | 1
38958.4113 | 1024 | 994 | 1
38958.4114 | 1045 | 1016 | 1
38958.4115 | 978 | 1016 | 1
38958.4116 | 954 | 925 | 1
38958.4117 | 1190 | 1071 | 1
38958.4118 | 1193 | 1177 | 1
38958.4119 | 1185 | 1151 | 1
38958.412 | 1116 | 1150 | 1
38958.412 | 1097 | 1132 | 1
38958.4122 | 1057 | 1092 | 1
38958.4122 | 934 | 945 | 1
38958.4123 | 1052 | 1006 | 1
38958.4124 | 1083 | 916 | 1
38958.4125 | 1064 | 1022 | 1
38958.4126 | 1152 | 1168 | 1
38958.4127 | 1044 | 994 | 1
38958.4128 | 1043 | 868 | 1
38958.4129 | 934 | 948 | 1
38958.413 | 1006 | 962 | 1
38958.4131 | 1114 | 905 | 1
38958.4132 | 988 | 943 | 1
38958.4133 | 983 | 941 | 1
38958.4134 | 1109 | 1139 | 1
38958.4135 | 1163 | 1165 | 1
38958.4136 | 1194 | 922 | 1
38958.4137 | 1172 | 1149 | 1
38958.4138 | 1040 | 990 | 1
38958.4139 | 1027 | 970 | 1
38958.414 | 1181 | 1169 | 1
38958.4141 | 1077 | 1095 | 1
38958.4142 | 1096 | 1040 | 1
38958.4143 | 1148 | 1164 | 1
38958.4144 | 1189 | 1169 | 1
38958.4145 | 1190 | 1144 | 1
38958.4146 | 1195 | 1162 | 1
38958.4147 | 1064 | 1014 | 1
38958.4148 | 1040 | 988 | 1
38958.4149 | 945 | 1045 | 1
38958.415 | 1000 | 1023 | 1
38958.4151 | 951 | 1055 | 1
38958.4152 | 1050 | 1004 | 1
38958.4153 | 919 | 928 | 1
38958.4154 | 931 | 883 | 1
38958.4155 | 1074 | 1035 | 1
38958.4156 | 1062 | 1026 | 1
38958.4156 | 925 | 942 | 1
38958.4158 | 1168 | 1129 | 1
38958.4158 | 1071 | 899 | 1
38958.4159 | 928 | 883 | 1
38958.416 | 990 | 953 | 1
38958.4161 | 1024 | 989 | 1
38958.4162 | 951 | 908 | 1
38958.4163 | 1013 | 976 | 1
38958.4164 | 1135 | 1108 | 1
38958.4165 | 986 | 948 | 1
38958.4166 | 923 | 1026 | 1
38958.4167 | 1119 | 1168 | 1
38958.4168 | 1169 | 1176 | 1
38958.4169 | 1080 | 1045 | 1
1
38958.4059 | 1 | 0 | 2
38958.406 | 1 | 0 | 2
38958.4061 | 1 | 0 | 2
38958.4062 | 1 | 0 | 2
38958.4063 | 1 | 0 | 2
38958.4064 | 1 | 0 | 2
38958.4065 | 1 | 0 | 2
38958.4066 | 1 | 0 | 2
38958.4067 | 1 | 0 | 2
38958.4068 | 1 | 0 | 2
38958.4069 | 1 | 0 | 2
38958.407 | 1 | 0 | 2
38958.4071 | 1 | 0 | 2
38958.4072 | 1 | 0 | 2
38958.4073 | 1 | 0 | 2
38958.4074 | 1 | 0 | 2
38958.4075 | 1 | 0 | 2
38958.4076 | 1 | 0 | 2
38958.4077 | 1 | 0 | 2
38958.4078 | 1 | 0 | 2
38958.4079 | 1 | 0 | 2
38958.408 | 1 | 0 | 2
38958.4081 | 1 | 0 | 2
38958.4082 | 1 | 0 | 2
38958.4083 | 1 | 0 | 2
38958.4084 | 1 | 0 | 2
38958.4085 | 1 | 0 | 2
38958.4086 | 1 | 0 | 2
38958.4087 | 1 | 0 | 2
38958.4088 | 1 | 0 | 2
38958.4089 | 1 | 0 | 2
38958.409 | 1 | 0 | 2
38958.4091 | 1 | 0 | 2
38958.4092 | 1 | 0 | 2
38958.4092 | 1 | 0 | 2
38958.4094 | 1 | 0 | 2
38958.4094 | 1 | 0 | 2
38958.4095 | 1 | 0 | 2
38958.4096 | 1 | 0 | 2
38958.4097 | 1 | 0 | 2
38958.4098 | 1 | 0 | 2
38958.4099 | 1 | 0 | 2
38958.41 | 1 | 0 | 2
38958.4101 | 1 | 0 | 2
38958.4102 | 1 | 0 | 2
38958.4103 | 1 | 0 | 2
38958.4104 | 1 | 0 | 2
38958.4105 | 1 | 0 | 2
38958.4106 | 1 | 0 | 2
38958.4107 | 1 | 0 | 2
38958.4108 | 1 | 0 | 2
38958.4109 | 1 | 0 | 2
38958.411 | 1 | 0 | 2
38958.4111 | 314 | 308 | 2
38958.4112 | 965 | 942 | 2
38958.4113 | 1086 | 1058 | 2
38958.4114 | 1098 | 1147 | 2
38958.4115 | 940 | 912 | 2
38958.4116 | 1138 | 1178 | 2
38958.4117 | 973 | 1008 | 2
38958.4118 | 929 | 923 | 2
38958.4119 | 968 | 931 | 2
38958.412 | 963 | 924 | 2
38958.4121 | 1059 | 1021 | 2
38958.4122 | 1095 | 1135 | 2
38958.4123 | 1016 | 953 | 2
38958.4124 | 1034 | 925 | 2
38958.4125 | 947 | 957 | 2
38958.4126 | 1094 | 1047 | 2
38958.4127 | 930 | 941 | 2
38958.4127 | 934 | 934 | 2
38958.4128 | 1134 | 971 | 2
38958.4129 | 1180 | 1161 | 2
38958.413 | 948 | 902 | 2
38958.4131 | 1067 | 1010 | 2
38958.4133 | 1192 | 1163 | 2
38958.4134 | 1047 | 1001 | 2
38958.4135 | 941 | 896 | 2
38958.4136 | 1014 | 1096 | 2
38958.4137 | 1108 | 1143 | 2
38958.4138 | 1082 | 1034 | 2
38958.4139 | 926 | 939 | 2
38958.414 | 1204 | 1156 | 2
38958.4141 | 1179 | 1116 | 2
38958.4142 | 1177 | 1152 | 2
38958.4143 | 1165 | 1169 | 2
38958.4144 | 1104 | 1058 | 2
38958.4145 | 938 | 877 | 2
38958.4146 | 1058 | 1003 | 2
38958.4147 | 1016 | 1033 | 2
38958.4148 | 978 | 924 | 2
38958.4149 | 1110 | 1162 | 2
38958.415 | 1062 | 1099 | 2
38958.4151 | 943 | 893 | 2
38958.4152 | 960 | 909 | 2
38958.4153 | 1114 | 1169 | 2
38958.4154 | 1113 | 1078 | 2
38958.4155 | 1139 | 1109 | 2
38958.4156 | 1050 | 1014 | 2
38958.4157 | 1158 | 1182 | 2
38958.4158 | 1009 | 1041 | 2
38958.4159 | 983 | 941 | 2
38958.416 | 976 | 1005 | 2
38958.4161 | 994 | 1098 | 2
38958.4162 | 954 | 977 | 2
38958.4163 | 1148 | 1173 | 2
38958.4163 | 953 | 912 | 2
38958.4164 | 1171 | 894 | 2
38958.4165 | 1075 | 1123 | 2
38958.4166 | 982 | 945 | 2
38958.4167 | 1176 | 1156 | 2
38958.4168 | 942 | 899 | 2
38958.4169 | 1110 | 1162 | 2
2
38958.406 | 1 | 0 | 3
38958.4061 | 1 | 0 | 3
38958.4062 | 1 | 0 | 3
38958.4062 | 1 | 0 | 3
38958.4064 | 1 | 0 | 3
38958.4064 | 1 | 0 | 3
38958.4065 | 1 | 0 | 3
38958.4066 | 1 | 0 | 3
38958.4067 | 1 | 0 | 3
38958.4068 | 1 | 0 | 3
38958.4069 | 1 | 0 | 3
38958.407 | 1 | 0 | 3
38958.4071 | 1 | 0 | 3
38958.4072 | 1 | 0 | 3
38958.4073 | 1 | 0 | 3
38958.4074 | 1 | 0 | 3
38958.4075 | 1 | 0 | 3
38958.4076 | 1 | 0 | 3
38958.4077 | 1 | 0 | 3
38958.4078 | 1 | 0 | 3
38958.4079 | 1 | 0 | 3
38958.408 | 1 | 0 | 3
38958.4081 | 1 | 0 | 3
38958.4082 | 1 | 0 | 3
38958.4083 | 1 | 0 | 3
38958.4084 | 1 | 0 | 3
38958.4085 | 1 | 0 | 3
38958.4086 | 1 | 0 | 3
38958.4087 | 1 | 0 | 3
38958.4088 | 1 | 0 | 3
38958.4089 | 1 | 0 | 3
38958.409 | 1 | 0 | 3
38958.4091 | 1 | 0 | 3
38958.4092 | 1 | 0 | 3
38958.4093 | 1 | 0 | 3
38958.4094 | 1 | 0 | 3
38958.4095 | 1 | 0 | 3
38958.4096 | 1 | 0 | 3
38958.4097 | 1 | 0 | 3
38958.4098 | 1 | 0 | 3
38958.4098 | 1 | 0 | 3
38958.4099 | 1 | 0 | 3
38958.41 | 1 | 0 | 3
38958.4101 | 1 | 0 | 3
38958.4102 | 1 | 0 | 3
38958.4103 | 1 | 0 | 3
38958.4104 | 1 | 0 | 3
38958.4105 | 1 | 0 | 3
38958.4106 | 1 | 0 | 3
38958.4107 | 1 | 0 | 3
38958.4108 | 1 | 0 | 3
38958.4109 | 1 | 0 | 3
38958.411 | 6 | 6 | 3
38958.4111 | 163 | 165 | 3
38958.4112 | 1092 | 1143 | 3
38958.4113 | 928 | 923 | 3
38958.4114 | 1125 | 1094 | 3
38958.4115 | 1113 | 1084 | 3
38958.4116 | 1087 | 1136 | 3
38958.4117 | 1121 | 1090 | 3
38958.4118 | 957 | 924 | 3
38958.4119 | 1028 | 988 | 3
38958.412 | 994 | 953 | 3
38958.4121 | 1141 | 1095 | 3
38958.4122 | 1172 | 1131 | 3
38958.4123 | 945 | 919 | 3
38958.4124 | 962 | 919 | 3
38958.4125 | 1005 | 963 | 3
38958.4126 | 1193 | 1150 | 3
38958.4127 | 973 | 929 | 3
38958.4128 | 1193 | 1160 | 3
38958.4129 | 1125 | 1147 | 3
38958.413 | 1004 | 1088 | 3
38958.4131 | 986 | 945 | 3
38958.4132 | 978 | 938 | 3
38958.4133 | 1026 | 1051 | 3
38958.4133 | 1207 | 1148 | 3
38958.4134 | 937 | 1021 | 3
38958.4135 | 958 | 914 | 3
38958.4136 | 941 | 898 | 3
38958.4137 | 1181 | 1132 | 3
38958.4138 | 1196 | 1140 | 3
38958.4139 | 1035 | 990 | 3
38958.414 | 953 | 907 | 3
38958.4141 | 1106 | 1146 | 3
38958.4142 | 1020 | 924 | 3
38958.4143 | 1040 | 923 | 3
38958.4144 | 990 | 945 | 3
38958.4145 | 1193 | 1173 | 3
38958.4146 | 1150 | 1175 | 3
38958.4147 | 1200 | 1146 | 3
38958.4148 | 1173 | 1136 | 3
38958.4149 | 1144 | 1178 | 3
38958.415 | 1185 | 1178 | 3
38958.4151 | 1032 | 995 | 3
38958.4152 | 1144 | 1182 | 3
38958.4153 | 1188 | 1174 | 3
38958.4154 | 1184 | 1163 | 3
38958.4155 | 954 | 910 | 3
38958.4156 | 1084 | 1049 | 3
38958.4157 | 1183 | 922 | 3
38958.4158 | 938 | 957 | 3
38958.4159 | 936 | 1042 | 3
38958.416 | 1152 | 1179 | 3
38958.4161 | 1104 | 1071 | 3
38958.4162 | 1027 | 988 | 3
38958.4163 | 1073 | 1038 | 3
38958.4164 | 1002 | 964 | 3
38958.4165 | 911 | 976 | 3
38958.4166 | 1133 | 1103 | 3
38958.4167 | 970 | 936 | 3
38958.4167 | 1166 | 1124 | 3
38958.4169 | 1076 | 1045 | 3
38958.4169 | 998 | 959 | 3
3
38958.406 | 1 | 0 | 4
38958.4061 | 1 | 0 | 4
38958.4062 | 1 | 0 | 4
38958.4063 | 1 | 0 | 4
38958.4064 | 1 | 0 | 4
38958.4065 | 1 | 0 | 4
38958.4066 | 1 | 0 | 4
38958.4067 | 1 | 0 | 4
38958.4068 | 1 | 0 | 4
38958.4069 | 1 | 0 | 4
38958.4069 | 1 | 0 | 4
38958.407 | 1 | 0 | 4
38958.4071 | 1 | 0 | 4
38958.4072 | 1 | 0 | 4
38958.4073 | 1 | 0 | 4
38958.4074 | 1 | 0 | 4
38958.4075 | 1 | 0 | 4
38958.4076 | 1 | 0 | 4
38958.4077 | 1 | 0 | 4
38958.4078 | 1 | 0 | 4
38958.4079 | 1 | 0 | 4
38958.408 | 1 | 0 | 4
38958.4081 | 1 | 0 | 4
38958.4082 | 1 | 0 | 4
38958.4083 | 1 | 0 | 4
38958.4084 | 1 | 0 | 4
38958.4085 | 1 | 0 | 4
38958.4086 | 1 | 0 | 4
38958.4087 | 1 | 0 | 4
38958.4088 | 1 | 0 | 4
38958.4089 | 1 | 0 | 4
38958.409 | 1 | 0 | 4
38958.4091 | 1 | 0 | 4
38958.4092 | 1 | 0 | 4
38958.4093 | 1 | 0 | 4
38958.4094 | 1 | 0 | 4
38958.4095 | 1 | 0 | 4
38958.4096 | 1 | 0 | 4
38958.4097 | 1 | 0 | 4
38958.4098 | 1 | 0 | 4
38958.4099 | 1 | 0 | 4
38958.41 | 1 | 0 | 4
38958.4101 | 1 | 0 | 4
38958.4102 | 1 | 0 | 4
38958.4103 | 1 | 0 | 4
38958.4103 | 1 | 0 | 4
38958.4105 | 1 | 0 | 4
38958.4105 | 1 | 0 | 4
38958.4106 | 1 | 0 | 4
38958.4107 | 1 | 0 | 4
38958.4108 | 1 | 0 | 4
38958.4109 | 1 | 0 | 4
38958.411 | 1 | 0 | 4
38958.4111 | 1186 | 1106 | 4
38958.4112 | 1040 | 1010 | 4
38958.4113 | 1189 | 1184 | 4
38958.4114 | 1111 | 1169 | 4
38958.4115 | 1041 | 1086 | 4
38958.4116 | 1194 | 1173 | 4
38958.4117 | 1083 | 1128 | 4
38958.4118 | 1033 | 996 | 4
38958.4119 | 1095 | 1054 | 4
38958.412 | 1085 | 1036 | 4
38958.4121 | 1199 | 1173 | 4
38958.4122 | 1094 | 1052 | 4
38958.4123 | 972 | 883 | 4
38958.4124 | 1013 | 965 | 4
38958.4125 | 927 | 948 | 4
38958.4126 | 1188 | 1141 | 4
38958.4127 | 1170 | 1174 | 4
38958.4128 | 1194 | 1124 | 4
38958.4129 | 1126 | 1071 | 4
38958.413 | 975 | 924 | 4
38958.4131 | 1050 | 1010 | 4
38958.4132 | 1075 | 1032 | 4
38958.4133 | 1097 | 1052 | 4
38958.4134 | 1200 | 1153 | 4
38958.4135 | 1180 | 1133 | 4
38958.4136 | 1041 | 992 | 4
38958.4137 | 1194 | 1074 | 4
38958.4137 | 995 | 1013 | 4
38958.4139 | 1207 | 978 | 4
38958.4139 | 1016 | 962 | 4
38958.4141 | 994 | 941 | 4
38958.4141 | 931 | 974 | 4
38958.4142 | 975 | 925 | 4
38958.4143 | 983 | 1000 | 4
38958.4144 | 1011 | 963 | 4
38958.4145 | 1171 | 1122 | 4
38958.4146 | 1194 | 1044 | 4
38958.4147 | 989 | 1004 | 4
38958.4148 | 1191 | 928 | 4
38958.4149 | 1093 | 1050 | 4
38958.415 | 1121 | 1082 | 4
38958.4151 | 1019 | 1051 | 4
38958.4152 | 1000 | 1102 | 4
38958.4153 | 958 | 910 | 4
38958.4154 | 1074 | 1038 | 4
38958.4155 | 1173 | 1147 | 4
38958.4156 | 1079 | 1154 | 4
38958.4157 | 1179 | 1155 | 4
38958.4158 | 933 | 884 | 4
38958.4159 | 1084 | 1048 | 4
38958.416 | 1001 | 910 | 4
38958.4161 | 1172 | 1178 | 4
38958.4162 | 943 | 900 | 4
38958.4163 | 1172 | 1176 | 4
38958.4164 | 1134 | 1109 | 4
38958.4165 | 964 | 924 | 4
38958.4166 | 989 | 1020 | 4
38958.4167 | 1120 | 1170 | 4
38958.4168 | 983 | 946 | 4
38958.4169 | 925 | 880 | 4
38958.417 | 1181 | 1172 | 4
4
38958.406 | 1 | 0 | 5
38958.4061 | 1 | 0 | 5
38958.4062 | 1 | 0 | 5
38958.4063 | 1 | 0 | 5
38958.4064 | 1 | 0 | 5
38958.4065 | 1 | 0 | 5
38958.4066 | 1 | 0 | 5
38958.4067 | 1 | 0 | 5
38958.4068 | 1 | 0 | 5
38958.4069 | 1 | 0 | 5
38958.407 | 1 | 0 | 5
38958.4071 | 1 | 0 | 5
38958.4072 | 1 | 0 | 5
38958.4073 | 1 | 0 | 5
38958.4073 | 1 | 0 | 5
38958.4075 | 1 | 0 | 5
38958.4075 | 1 | 0 | 5
38958.4077 | 1 | 0 | 5
38958.4077 | 1 | 0 | 5
38958.4078 | 1 | 0 | 5
38958.4079 | 1 | 0 | 5
38958.408 | 1 | 0 | 5
38958.4081 | 1 | 0 | 5
38958.4082 | 1 | 0 | 5
38958.4083 | 1 | 0 | 5
38958.4084 | 1 | 0 | 5
38958.4085 | 1 | 0 | 5
38958.4086 | 1 | 0 | 5
38958.4087 | 1 | 0 | 5
38958.4088 | 1 | 0 | 5
38958.4089 | 1 | 0 | 5
38958.409 | 1 | 0 | 5
38958.4091 | 1 | 0 | 5
38958.4092 | 1 | 0 | 5
38958.4093 | 1 | 0 | 5
38958.4094 | 1 | 0 | 5
38958.4095 | 1 | 0 | 5
38958.4096 | 1 | 0 | 5
38958.4097 | 1 | 0 | 5
38958.4098 | 1 | 0 | 5
38958.4099 | 1 | 0 | 5
38958.41 | 1 | 0 | 5
38958.4101 | 1 | 0 | 5
38958.4102 | 1 | 0 | 5
38958.4103 | 1 | 0 | 5
38958.4104 | 1 | 0 | 5
38958.4105 | 1 | 0 | 5
38958.4106 | 1 | 0 | 5
38958.4107 | 1 | 0 | 5
38958.4108 | 1 | 0 | 5
38958.4109 | 1 | 0 | 5
38958.4109 | 1 | 0 | 5
38958.4111 | 1 | 0 | 5
38958.4111 | 1134 | 1105 | 5
38958.4112 | 972 | 946 | 5
38958.4113 | 1123 | 1093 | 5
38958.4114 | 1128 | 1098 | 5
38958.4115 | 1116 | 1167 | 5
38958.4116 | 1019 | 1057 | 5
38958.4117 | 999 | 1097 | 5
38958.4118 | 1090 | 1053 | 5
38958.4119 | 1004 | 963 | 5
38958.412 | 1182 | 1176 | 5
38958.4121 | 1200 | 1173 | 5
38958.4122 | 1143 | 1093 | 5
38958.4123 | 1187 | 1165 | 5
38958.4124 | 974 | 932 | 5
38958.4125 | 1098 | 1136 | 5
38958.4126 | 1148 | 1099 | 5
38958.4127 | 934 | 933 | 5
38958.4128 | 1052 | 948 | 5
38958.4129 | 965 | 974 | 5
38958.413 | 1141 | 1039 | 5
38958.4131 | 1194 | 927 | 5
38958.4132 | 1010 | 1035 | 5
38958.4133 | 1179 | 1132 | 5
38958.4134 | 1092 | 1047 | 5
38958.4135 | 1200 | 931 | 5
38958.4136 | 967 | 923 | 5
38958.4137 | 1047 | 1118 | 5
38958.4138 | 941 | 899 | 5
38958.4139 | 1115 | 1065 | 5
38958.414 | 927 | 969 | 5
38958.4141 | 1026 | 978 | 5
38958.4142 | 983 | 934 | 5
38958.4143 | 1194 | 1129 | 5
38958.4144 | 1095 | 1146 | 5
38958.4145 | 1120 | 1069 | 5
38958.4145 | 1068 | 1012 | 5
38958.4146 | 1075 | 1021 | 5
38958.4147 | 956 | 901 | 5
38958.4148 | 1137 | 1096 | 5
38958.4149 | 1117 | 1075 | 5
38958.415 | 1133 | 1096 | 5
38958.4151 | 944 | 893 | 5
38958.4152 | 1188 | 1164 | 5
38958.4153 | 969 | 923 | 5
38958.4154 | 951 | 972 | 5
38958.4155 | 1185 | 1071 | 5
38958.4156 | 1127 | 895 | 5
38958.4157 | 1148 | 892 | 5
38958.4158 | 966 | 924 | 5
38958.4159 | 1102 | 1153 | 5
38958.416 | 1015 | 976 | 5
38958.4161 | 1086 | 1054 | 5
38958.4162 | 976 | 936 | 5
38958.4163 | 1086 | 1161 | 5
38958.4164 | 1174 | 1151 | 5
38958.4165 | 1053 | 1141 | 5
38958.4166 | 942 | 898 | 5
38958.4167 | 962 | 926 | 5
38958.4168 | 977 | 1010 | 5
38958.4169 | 953 | 905 | 5
38958.417 | 1135 | 1102 | 5
5
38958.406 | 1 | 0 | 6
38958.4061 | 1 | 0 | 6
38958.4062 | 1 | 0 | 6
38958.4063 | 1 | 0 | 6
38958.4064 | 1 | 0 | 6
38958.4065 | 1 | 0 | 6
38958.4066 | 1 | 0 | 6
38958.4067 | 1 | 0 | 6
38958.4068 | 1 | 0 | 6
38958.4069 | 1 | 0 | 6
38958.407 | 1 | 0 | 6
38958.4071 | 1 | 0 | 6
38958.4072 | 1 | 0 | 6
38958.4073 | 1 | 0 | 6
38958.4074 | 1 | 0 | 6
38958.4075 | 1 | 0 | 6
38958.4076 | 1 | 0 | 6
38958.4077 | 1 | 0 | 6
38958.4078 | 1 | 0 | 6
38958.4079 | 1 | 0 | 6
38958.408 | 1 | 0 | 6
38958.4081 | 1 | 0 | 6
38958.4081 | 1 | 0 | 6
38958.4082 | 1 | 0 | 6
38958.4083 | 1 | 0 | 6
38958.4084 | 1 | 0 | 6
38958.4085 | 1 | 0 | 6
38958.4086 | 1 | 0 | 6
38958.4087 | 1 | 0 | 6
38958.4088 | 1 | 0 | 6
38958.4089 | 1 | 0 | 6
38958.409 | 1 | 0 | 6
38958.4091 | 1 | 0 | 6
38958.4092 | 1 | 0 | 6
38958.4093 | 1 | 0 | 6
38958.4094 | 1 | 0 | 6
38958.4095 | 1 | 0 | 6
38958.4096 | 1 | 0 | 6
38958.4097 | 1 | 0 | 6
38958.4098 | 1 | 0 | 6
38958.4099 | 1 | 0 | 6
38958.41 | 1 | 0 | 6
38958.4101 | 1 | 0 | 6
38958.4102 | 1 | 0 | 6
38958.4103 | 1 | 0 | 6
38958.4104 | 1 | 0 | 6
38958.4105 | 1 | 0 | 6
38958.4106 | 1 | 0 | 6
38958.4107 | 1 | 0 | 6
38958.4108 | 1 | 0 | 6
38958.4109 | 1 | 0 | 6
38958.411 | 1 | 0 | 6
38958.4111 | 8 | 6 | 6
38958.4112 | 948 | 922 | 6
38958.4113 | 941 | 911 | 6
38958.4114 | 1133 | 1103 | 6
38958.4115 | 1189 | 1167 | 6
38958.4116 | 1187 | 1082 | 6
38958.4116 | 968 | 1003 | 6
38958.4117 | 1162 | 1129 | 6
38958.4118 | 1017 | 980 | 6
38958.4119 | 943 | 903 | 6
38958.412 | 1190 | 1153 | 6
38958.4121 | 1039 | 995 | 6
38958.4122 | 1074 | 1130 | 6
38958.4123 | 1003 | 1084 | 6
38958.4124 | 1188 | 1146 | 6
38958.4125 | 1187 | 1144 | 6
38958.4126 | 1200 | 1159 | 6
38958.4127 | 1112 | 1138 | 6
38958.4128 | 1215 | 760 | 6
38958.4129 | 955 | 1046 | 6
38958.413 | 1073 | 1010 | 6
38958.4131 | 971 | 920 | 6
38958.4132 | 940 | 901 | 6
38958.4133 | 924 | 958 | 6
38958.4134 | 1133 | 1159 | 6
38958.4135 | 1037 | 1042 | 6
38958.4136 | 1176 | 1170 | 6
38958.4137 | 935 | 903 | 6
38958.4138 | 994 | 1009 | 6
38958.4139 | 1152 | 1095 | 6
38958.414 | 975 | 933 | 6
38958.4141 | 1000 | 944 | 6
38958.4142 | 929 | 981 | 6
38958.4143 | 1083 | 1030 | 6
38958.4144 | 1190 | 1143 | 6
38958.4145 | 1019 | 970 | 6
38958.4146 | 1076 | 1103 | 6
38958.4147 | 1183 | 1142 | 6
38958.4148 | 1014 | 961 | 6
38958.4148 | 992 | 938 | 6
38958.415 | 1178 | 1145 | 6
38958.415 | 1190 | 928 | 6
38958.4152 | 1005 | 958 | 6
38958.4152 | 1012 | 969 | 6
38958.4153 | 1189 | 1176 | 6
38958.4154 | 1057 | 1017 | 6
38958.4155 | 1100 | 1063 | 6
38958.4156 | 930 | 885 | 6
38958.4157 | 958 | 920 | 6
38958.4158 | 1124 | 894 | 6
38958.4159 | 1061 | 1025 | 6
38958.416 | 1028 | 991 | 6
38958.4161 | 1159 | 1131 | 6
38958.4162 | 918 | 995 | 6
38958.4163 | 1025 | 986 | 6
38958.4164 | 918 | 974 | 6
38958.4165 | 946 | 902 | 6
38958.4166 | 1159 | 1180 | 6
38958.4167 | 977 | 935 | 6
38958.4168 | 1012 | 1049 | 6
38958.4169 | 1123 | 1172 | 6
38958.417 | 1064 | 1026 | 6
6