## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 50
Test conditions: Cable: 7-conductor, 12 AWG, one XLPE insulated control cable with one EPR insulated control cable and one PE insulated control cable (cable items #10, #2 & #15). Cable specimens present: Three lengths of cable were monitored for electrical performance, a fourth length of cable (EPR) was monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using six channels - two for each cable (see electrical connection map), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures and six cable temperatures (see thermocouple map). Shroud power: Initiated after 140 seconds of baseline data monitoring. Special Note: Test setup included three thermocouples on the outer surface of the conduit.
DAQ Time | Penlight Time | Event | Interpretation
140 | 0 | Initated Penlight Heating
1219 | 1079 | Conductors A1 & A2 short together intermittently at less than 100 ohms (14) | Cable A is shorted internally (intermittent)
1476-1485 | 1336-1345 | Conductors A1 & A2 both short to ground intermittently at less than 1000 ohms (174 & 190) | Cable A shorts to ground (intermittent)
1664-1666 | 1524-1526 | Conductors C5 & C6 both short to ground at less than 100 ohms (43 & 26) | Cable C shorts to ground
1720 | 1580 | Conductors C5 & C6 short together intermittenly at less than 100 ohms (41) | Cable C shorted internally (intermittent)
2058 | 1918 | Conductors A1 & A2 short together at less than 100 ohms (44) | Cable A is shorted internally
2335 | 2195 | Conductors B3 & B4 short together at less than 100 ohms (38) | Cable B is shorted internally
2372 | 2232 | Conductor B3 shorts to ground intermittently at less than 1000 ohms (832) | Cable B partially shorted to ground (intermittent)
2441-2451 | 2301-2311 | Conductors A1 & A2 both short to ground at less than 1000 ohms (487 & 142) | Cable A shorts to ground
2460-2540 | 2320-2400 | Conductors B3 & B4 short to ground at less than 1000 ohms (431 & 160) | Cable B shorts to ground
2686 | 2546 | Conductors C5 & C6 short together at less than 100 ohms (12) | Cable C is shorted internally
3121 | 2981 | Power to Penlight shutoff
Additional Observations
Observation 1 | Cable failures were initially intermittent in nature then progressed to "steady state" failure conditions
Observation 2 | It took 1079 seconds (18 min.) from the start of Penlight heating for the first internal short to occur, and it took 1336 s (22.3 min.) for the first short to ground failure.
Observation 3 | No cable to cable interations occurred prior to one or both cables shorting to ground or internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable and conduit
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Outer surface of conduit
| TC2 | = | Conduit 2 | Outer surface of conduit at mid-point
| TC3 | = | Conduit 3 | Outer surface of conduit
| TC4 | = | Cable 1 | Within cable just below cable jacket, center position
| TC5 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC6 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC7 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC8 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC9 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
Cable A = PE (item #15)
Cable B = XLPE (item #10)
Cable C = EPR (item #2)
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 50 |  |  | 2006-09-01 | 8:09
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | C5-C6 | Penlight Time | Minimums
-139.5 | 224137.9994 | -136.5 | 235437.9994 | -134 | 238537.9994 | -131 | 238637.9994 | -128.5 | 242537.9994 | -125.5 | 234337.9994 | -122.5 | 455175.9997 | -120 | 240037.9994 | -117 | 240937.9994 | -114.5 | 238537.9994 | -111.5 | 240037.9994 | -108.5 | 241037.9994 | -106 | 239437.9994 | -103 | 242437.9994 | -100.5 | 243037.9994 | -139.5 | 224137.9994
-97.5 | 224137.9994 | -94.5 | 235437.9994 | -92 | 238537.9994 | -89 | 238637.9994 | -86.5 | 242537.9994 | -83.5 | 234337.9994 | -80.5 | 227537.9994 | -78 | 240037.9994 | -75 | 240937.9994 | -72.5 | 238537.9994 | -69.5 | 240037.9994 | -66.5 | 241037.9994 | -64 | 239437.9994 | -61 | 242437.9994 | -58.5 | 243037.9994 | -97.5 | 224137.9994
-55.5 | 224137.9994 | -52.5 | 235437.9994 | -50 | 238537.9994 | -47 | 238637.9994 | -44.5 | 242537.9994 | -41.5 | 234337.9994 | -38.5 | 227537.9994 | -36 | 240037.9994 | -33 | 240937.9994 | -30.5 | 238537.9994 | -27.5 | 240037.9994 | -24.5 | 241037.9994 | -22 | 239437.9994 | -19 | 242437.9994 | -16.5 | 243037.9994 | -55.5 | 224137.9994
-13.5 | 224137.9994 | -10.5 | 235437.9994 | -8 | 238537.9994 | -5 | 47647.5969 | -2.5 | 242537.9994 | 0.5 | 234337.9994 | 3.5 | 227537.9994 | 6 | 240037.9994 | 9 | 240937.9994 | 11.5 | 238537.9994 | 14.5 | 240037.9994 | 17.5 | 241037.9994 | 20 | 239437.9994 | 23 | 242437.9994 | 25.5 | 243037.9994 | -13.5 | 47647.5969
28.5 | 224137.9994 | 31.5 | 235437.9994 | 34 | 238537.9994 | 37 | 238637.9994 | 39.5 | 242537.9994 | 42.5 | 234337.9994 | 45.5 | 227537.9994 | 48 | 240037.9994 | 51 | 240937.9994 | 53.5 | 238537.9994 | 56.5 | 240037.9994 | 59.5 | 241037.9994 | 62 | 239238.0835 | 65 | 242437.9994 | 67.5 | 243037.9994 | 28.5 | 224137.9994
70.5 | 224137.9994 | 73.5 | 235437.9994 | 76 | 238537.9994 | 79 | 238637.9994 | 81.5 | 242537.9994 | 84.5 | 234337.9994 | 87.5 | 227537.9994 | 90 | 240037.9994 | 93 | 240738.083 | 95.5 | 238537.9994 | 98.5 | 240037.9994 | 101.5 | 241037.9994 | 104 | 239437.9994 | 107 | 242437.9994 | 109.5 | 243037.9994 | 70.5 | 224137.9994
112.5 | 224137.9994 | 115.5 | 235437.9994 | 118 | 238537.9994 | 121 | 238637.9994 | 123.5 | 242537.9994 | 126.5 | 234337.9994 | 129.5 | 227537.9994 | 132 | 240037.9994 | 135 | 240937.9994 | 137.5 | 238537.9994 | 140.5 | 240037.9994 | 143.5 | 241037.9994 | 146 | 239437.9994 | 149 | 121168.9988 | 151.5 | 243037.9994 | 112.5 | 121168.9988
154.5 | 224137.9994 | 157.5 | 235437.9994 | 160 | 238338.0838 | 163 | 238637.9994 | 165.5 | 242537.9994 | 168.5 | 234337.9994 | 171.5 | 227537.9994 | 174 | 119968.9988 | 177 | 240937.9994 | 179.5 | 238537.9994 | 182.5 | 240037.9994 | 185.5 | 241037.9994 | 188 | 239437.9994 | 191 | 242437.9994 | 193.5 | 243037.9994 | 154.5 | 119968.9988
196.5 | 224137.9994 | 199.5 | 235437.9994 | 202 | 238537.9994 | 205 | 238637.9994 | 207.5 | 242537.9994 | 210.5 | 234337.9994 | 213.5 | 227537.9994 | 216 | 240037.9994 | 219 | 240937.9994 | 221.5 | 238537.9994 | 224.5 | 240037.9994 | 227.5 | 241037.9994 | 230 | 239437.9994 | 233 | 242437.9994 | 235.5 | 243037.9994 | 196.5 | 224137.9994
238.5 | 224137.9994 | 241.5 | 235437.9994 | 244 | 238537.9994 | 247 | 238637.9994 | 249.5 | 242537.9994 | 252.5 | 234337.9994 | 255.5 | 227537.9994 | 258 | 240037.9994 | 261 | 240937.9994 | 263.5 | 238537.9994 | 266.5 | 240037.9994 | 269.5 | 241037.9994 | 272 | 239437.9994 | 275 | 242437.9994 | 277.5 | 243037.9994 | 238.5 | 224137.9994
280.5 | 224137.9994 | 283.5 | 235437.9994 | 286 | 238537.9994 | 289 | 238637.9994 | 291.5 | 121218.9988 | 294.5 | 234337.9994 | 297.5 | 227537.9994 | 300 | 240037.9994 | 303 | 240937.9994 | 305.5 | 238537.9994 | 308.5 | 240037.9994 | 311.5 | 241037.9994 | 314 | 239437.9994 | 317 | 242437.9994 | 319.5 | 243037.9994 | 280.5 | 121218.9988
322.5 | 224137.9994 | 325.5 | 235437.9994 | 328 | 238537.9994 | 331 | 238637.9994 | 333.5 | 242537.9994 | 336.5 | 234337.9994 | 339.5 | 227537.9994 | 342 | 240037.9994 | 345 | 240937.9994 | 347.5 | 238537.9994 | 350.5 | 240037.9994 | 353.5 | 241037.9994 | 356 | 239437.9994 | 359 | 242437.9994 | 361.5 | 243037.9994 | 322.5 | 224137.9994
364.5 | 224137.9994 | 367.5 | 235437.9994 | 370 | 238537.9994 | 373 | 238637.9994 | 375.5 | 242537.9994 | 378.5 | 234337.9994 | 381.5 | 227537.9994 | 384 | 240037.9994 | 387 | 240738.083 | 389.5 | 238537.9994 | 392.5 | 240037.9994 | 395.5 | 241037.9994 | 398 | 239437.9994 | 401 | 242437.9994 | 403.5 | 243037.9994 | 364.5 | 224137.9994
406.5 | 224137.9994 | 409.5 | 235437.9994 | 412 | 238537.9994 | 415 | 238637.9994 | 417.5 | 242537.9994 | 420.5 | 234337.9994 | 423.5 | 227537.9994 | 426 | 240037.9994 | 428.5 | 240937.9994 | 431.5 | 238537.9994 | 434.5 | 240037.9994 | 437 | 241037.9994 | 440 | 239437.9994 | 443 | 242437.9994 | 445.5 | 243037.9994 | 406.5 | 224137.9994
448.5 | 224137.9994 | 451.5 | 235437.9994 | 454 | 238537.9994 | 457 | 238637.9994 | 459.5 | 242537.9994 | 462.5 | 234337.9994 | 465.5 | 227537.9994 | 468 | 240037.9994 | 471 | 240937.9994 | 473.5 | 238537.9994 | 476.5 | 240037.9994 | 479.5 | 241037.9994 | 482 | 239437.9994 | 485 | 242437.9994 | 487.5 | 243037.9994 | 448.5 | 224137.9994
490.5 | 224137.9994 | 493.5 | 235238.0849 | 496 | 238537.9994 | 499 | 238637.9994 | 501.5 | 242537.9994 | 504.5 | 234337.9994 | 507 | 227537.9994 | 510 | 240037.9994 | 512.5 | 240937.9994 | 515.5 | 238537.9994 | 518.5 | 240037.9994 | 521 | 120468.9988 | 524 | 239437.9994 | 527 | 242437.9994 | 529.5 | 243037.9994 | 490.5 | 120468.9988
532.5 | 224137.9994 | 535.5 | 235437.9994 | 538 | 238537.9994 | 541 | 238637.9994 | 543.5 | 242537.9994 | 546.5 | 234337.9994 | 549.5 | 227537.9994 | 552 | 240037.9994 | 554.5 | 240937.9994 | 557.5 | 238537.9994 | 560.5 | 240037.9994 | 563.5 | 241037.9994 | 566 | 239437.9994 | 568.5 | 242437.9994 | 571.5 | 243037.9994 | 532.5 | 224137.9994
574.5 | 224137.9994 | 577.5 | 235437.9994 | 580 | 238537.9994 | 582.5 | 238637.9994 | 585.5 | 242537.9994 | 588.5 | 234337.9994 | 591.5 | 227537.9994 | 594 | 240037.9994 | 597 | 240937.9994 | 599.5 | 238537.9994 | 602.5 | 240037.9994 | 605.5 | 241037.9994 | 608 | 239437.9994 | 610.5 | 242437.9994 | 613.5 | 243037.9994 | 574.5 | 224137.9994
616.5 | 224137.9994 | 619.5 | 235437.9994 | 622 | 238537.9994 | 625 | 238637.9994 | 627.5 | 242537.9994 | 631 | 234337.9994 | 633.5 | 227537.9994 | 636 | 240037.9994 | 639 | 240937.9994 | 641.5 | 238537.9994 | 644.5 | 240037.9994 | 647.5 | 241037.9994 | 650 | 239437.9994 | 652.5 | 242437.9994 | 655.5 | 243037.9994 | 616.5 | 224137.9994
658.5 | 224137.9994 | 661 | 235437.9994 | 664 | 238537.9994 | 667 | 238637.9994 | 669.5 | 242537.9994 | 672.5 | 234337.9994 | 675.5 | 227537.9994 | 678 | 240037.9994 | 680.5 | 240937.9994 | 683.5 | 238537.9994 | 686.5 | 240037.9994 | 689 | 120468.9988 | 692 | 239437.9994 | 695 | 242437.9994 | 697.5 | 243037.9994 | 658.5 | 120468.9988
700.5 | 224137.9994 | 703 | 235437.9994 | 706 | 238537.9994 | 708.5 | 238637.9994 | 711.5 | 242537.9994 | 714.5 | 234337.9994 | 717.5 | 227537.9994 | 720 | 240037.9994 | 723 | 240937.9994 | 725.5 | 238537.9994 | 728.5 | 239838.0833 | 731.5 | 241037.9994 | 734 | 239437.9994 | 736.5 | 242437.9994 | 739.5 | 243037.9994 | 700.5 | 224137.9994
742.5 | 224137.9994 | 745 | 235437.9994 | 748 | 238537.9994 | 751 | 238637.9994 | 753.5 | 242537.9994 | 756.5 | 234337.9994 | 759 | 227537.9994 | 762 | 240037.9994 | 764.5 | 240937.9994 | 767.5 | 238537.9994 | 770.5 | 240037.9994 | 773 | 241037.9994 | 776 | 239437.9994 | 779 | 242437.9994 | 781.5 | 243037.9994 | 742.5 | 224137.9994
784.5 | 112018.9988 | 787 | 235437.9994 | 790 | 238537.9994 | 793 | 238637.9994 | 795.5 | 242537.9994 | 798.5 | 234337.9994 | 801.5 | 227537.9994 | 804 | 240037.9994 | 807 | 240937.9994 | 809.5 | 238537.9994 | 812.5 | 240037.9994 | 815 | 241037.9994 | 818 | 239437.9994 | 821 | 242437.9994 | 823.5 | 243037.9994 | 784.5 | 112018.9988
826.5 | 224137.9994 | 829.5 | 235437.9994 | 832 | 238537.9994 | 835 | 238637.9994 | 837.5 | 242537.9994 | 840.5 | 234337.9994 | 843.5 | 227537.9994 | 846 | 240037.9994 | 849 | 240937.9994 | 851.5 | 238537.9994 | 854.5 | 240037.9994 | 857 | 241037.9994 | 860 | 239437.9994 | 862.5 | 242437.9994 | 865.5 | 243037.9994 | 826.5 | 224137.9994
868.5 | 224137.9994 | 871.5 | 235437.9994 | 874 | 238537.9994 | 877 | 238637.9994 | 879.5 | 242537.9994 | 882.5 | 234337.9994 | 885 | 227537.9994 | 888 | 240037.9994 | 890.5 | 240937.9994 | 893.5 | 238537.9994 | 896.5 | 240037.9994 | 899 | 241037.9994 | 902 | 239437.9994 | 904.5 | 242437.9994 | 907.5 | 243037.9994 | 868.5 | 224137.9994
910.5 | 224137.9994 | 913 | 235437.9994 | 916 | 238537.9994 | 918.5 | 238637.9994 | 921.5 | 242537.9994 | 924.5 | 234337.9994 | 927.5 | 227537.9994 | 930 | 240037.9994 | 933 | 240937.9994 | 935.5 | 238537.9994 | 938.5 | 240037.9994 | 941.5 | 241037.9994 | 944 | 239437.9994 | 947 | 242437.9994 | 949.5 | 243037.9994 | 910.5 | 224137.9994
952.5 | 224137.9994 | 955.5 | 235437.9994 | 958 | 238537.9994 | 960.5 | 238637.9994 | 963.5 | 242537.9994 | 966.5 | 234337.9994 | 969 | 227537.9994 | 972 | 240037.9994 | 974.5 | 240937.9994 | 977.5 | 238537.9994 | 980.5 | 240037.9994 | 983 | 241037.9994 | 986 | 239437.9994 | 989 | 242437.9994 | 991.5 | 243037.9994 | 952.5 | 224137.9994
994.5 | 224137.9994 | 997 | 235437.9994 | 1000 | 238537.9994 | 1002.5 | 238637.9994 | 1005.5 | 242537.9994 | 1008.5 | 234337.9994 | 1011 | 227537.9994 | 1014 | 240037.9994 | 1016.5 | 240937.9994 | 1019.5 | 238537.9994 | 1022.5 | 240037.9994 | 1025 | 241037.9994 | 1028 | 239437.9994 | 1030.5 | 242437.9994 | 1033.5 | 243037.9994 | 994.5 | 224137.9994
1036.5 | 224137.9994 | 1039 | 235437.9994 | 1042 | 238537.9994 | 1044.5 | 238637.9994 | 1047.5 | 242537.9994 | 1050.5 | 234337.9994 | 1053 | 227537.9994 | 1056 | 240037.9994 | 1058.5 | 240937.9994 | 1061.5 | 238537.9994 | 1064.5 | 240037.9994 | 1067 | 241037.9994 | 1070 | 239437.9994 | 1072.5 | 242437.9994 | 1075.5 | 243037.9994 | 1036.5 | 224137.9994
1078.5 | 13.6 | 1081 | 117618.9788 | 1084 | 238537.9994 | 1086.5 | 238438.0838 | 1089.5 | 242537.9994 | 1092.5 | 234337.9994 | 1095 | 227537.9994 | 1098 | 240037.9994 | 1100.5 | 240937.9994 | 1103.5 | 238537.9994 | 1106.5 | 240037.9994 | 1108 | 241037.9994 | 1112 | 239437.9994 | 1115 | 242437.9994 | 1117.5 | 243037.9994 | 1078.5 | 13.6
1120.5 | 224137.9994 | 1123 | 235437.9994 | 1126 | 238537.9994 | 1128.5 | 238637.9994 | 1131.5 | 242537.9994 | 1134.5 | 234337.9994 | 1137 | 227537.9994 | 1140 | 240037.9994 | 1142.5 | 240937.9994 | 1145.5 | 238537.9994 | 1148.5 | 240037.9994 | 1151.5 | 241037.9994 | 1154 | 239437.9994 | 1156.5 | 242437.9994 | 1159.5 | 243037.9994 | 1120.5 | 224137.9994
1162.5 | 224137.9994 | 1165 | 235437.9994 | 1168 | 238537.9994 | 1170.5 | 238637.9994 | 1173.5 | 242537.9994 | 1176.5 | 234337.9994 | 1179 | 227537.9994 | 1182 | 240037.9994 | 1184.5 | 240937.9994 | 1187.5 | 238537.9994 | 1190.5 | 240037.9994 | 1193 | 241037.9994 | 1196 | 239437.9994 | 1198.5 | 242437.9994 | 1201.5 | 243037.9994 | 1162.5 | 224137.9994
1204.5 | 224137.9994 | 1207 | 235437.9994 | 1210 | 238537.9994 | 1212.5 | 238637.9994 | 1215.5 | 242537.9994 | 1218.5 | 234337.9994 | 1221 | 227537.9994 | 1224 | 240037.9994 | 1226.5 | 240937.9994 | 1229.5 | 238537.9994 | 1232.5 | 240037.9994 | 1235 | 241037.9994 | 1238 | 239437.9994 | 1240.5 | 242437.9994 | 1243.5 | 243037.9994 | 1204.5 | 224137.9994
1246.5 | 224137.9994 | 1249 | 235437.9994 | 1252 | 238537.9994 | 1254.5 | 238637.9994 | 1257.5 | 242537.9994 | 1260.5 | 234337.9994 | 1263 | 227537.9994 | 1266 | 240037.9994 | 1268.5 | 240937.9994 | 1271.5 | 238537.9994 | 1274.5 | 240037.9994 | 1277 | 241037.9994 | 1280 | 239437.9994 | 1282.5 | 242437.9994 | 1285.5 | 243037.9994 | 1246.5 | 224137.9994
1288.5 | 224137.9994 | 1291 | 235437.9994 | 1294 | 238537.9994 | 1296.5 | 238637.9994 | 1299.5 | 242537.9994 | 1302.5 | 234337.9994 | 1305 | 227537.9994 | 1308 | 240037.9994 | 1310.5 | 240937.9994 | 1313.5 | 238537.9994 | 1316.5 | 240037.9994 | 1319 | 241037.9994 | 1322 | 239437.9994 | 1324.5 | 242437.9994 | 1327.5 | 243037.9994 | 1288.5 | 224137.9994
1330.5 | 3.9814 | 1333 | 117618.9788 | 1336 | 238537.9994 | 1338.5 | 238637.9994 | 1341.5 | 242537.9994 | 1344.5 | 234337.9994 | 1347 | 227537.9994 | 1350 | 240037.9994 | 1352.5 | 240937.9994 | 1355.5 | 238537.9994 | 1358.5 | 240037.9994 | 1361 | 241037.9994 | 1364 | 239437.9994 | 1366.5 | 242437.9994 | 1369.5 | 243037.9994 | 1330.5 | 3.9814
1372.5 | 30.3016 | 1375 | 235237.9575 | 1378 | 238537.9994 | 1380.5 | 119268.9988 | 1383.5 | 242537.9994 | 1386.5 | 234337.9994 | 1389 | 227537.9994 | 1392 | 240037.9994 | 1394.5 | 240937.9994 | 1397.5 | 238537.9994 | 1400.5 | 240037.9994 | 1403 | 241037.9994 | 1406 | 239437.9994 | 1408.5 | 242437.9994 | 1411.5 | 243037.9994 | 1372.5 | 30.3016
1414.5 | 6807.5253 | 1417 | 235437.9994 | 1420 | 238537.9994 | 1422.5 | 238637.9994 | 1425.5 | 242537.9994 | 1428.5 | 234337.9994 | 1431 | 227537.9994 | 1434 | 240037.9994 | 1436.5 | 240937.9994 | 1439.5 | 238537.9994 | 1442.5 | 240037.9994 | 1445 | 241037.9994 | 1448 | 239437.9994 | 1450.5 | 242437.9994 | 1453.5 | 243037.9994 | 1414.5 | 6807.5253
1456.5 | 224137.9994 | 1459 | 235437.9994 | 1462 | 238537.9994 | 1464.5 | 238637.9994 | 1467.5 | 242537.9994 | 1470.5 | 234337.9994 | 1473 | 227537.9994 | 1476 | 240037.9994 | 1478.5 | 240937.9994 | 1481.5 | 238537.9994 | 1484.5 | 240037.9994 | 1487 | 241037.9994 | 1490 | 239437.9994 | 1492.5 | 242437.9994 | 1495.5 | 80945.9982 | 1456.5 | 80945.9982
1498.5 | 224137.9994 | 1501 | 235437.9994 | 1504 | 238537.9994 | 1506.5 | 238637.9994 | 1509.5 | 121218.9988 | 1512.5 | 234337.9994 | 1515 | 227537.9994 | 1518 | 240037.9994 | 1520.5 | 120418.9988 | 1523.5 | 238537.9994 | 1526.5 | 240037.9994 | 1528 | 241037.9994 | 1532 | 119668.9988 | 1534.5 | 121168.9988 | 1537.5 | 25897.4905 | 1498.5 | 25897.4905
1540.5 | 39.718 | 1543 | 235038.2547 | 1546 | 119218.9988 | 1548.5 | 238637.9994 | 1551.5 | 121218.9988 | 1554.5 | 117118.9988 | 1557 | 227537.9994 | 1560 | 240037.9994 | 1562.5 | 120418.9988 | 1565.5 | 119218.9988 | 1568.5 | 240037.9994 | 1571 | 120468.9988 | 1574 | 119668.9988 | 1576.5 | 80745.9982 | 1579.5 | 40.8138 | 1540.5 | 39.718
1582.5 | 2.6023 | 1585 | 117519.0637 | 1588 | 238138.2514 | 1590.5 | 119268.9988 | 1593.5 | 80779.3315 | 1596.5 | 78045.9982 | 1599 | 113718.9988 | 1602 | 119968.9988 | 1604.5 | 120418.9988 | 1607.5 | 79445.9982 | 1610.5 | 119968.9988 | 1613 | 120468.9988 | 1616 | 119668.9988 | 1618.5 | 80745.9982 | 1621.5 | 94.5372 | 1582.5 | 2.6023
1624.5 | 223638.3568 | 1627 | 117668.9988 | 1630 | 119218.9988 | 1632.5 | 119268.9988 | 1635.5 | 121218.9988 | 1638.5 | 78045.9982 | 1641 | 113718.9988 | 1644 | 119968.9988 | 1646.5 | 80245.9982 | 1649.5 | 79445.9982 | 1652.5 | 119968.9988 | 1655 | 120468.9988 | 1658 | 119668.9988 | 1660.5 | 80745.9982 | 1663.5 | 398.8196 | 1624.5 | 398.8196
1666.5 | 74645.9982 | 1669 | 117668.9988 | 1672 | 119218.9988 | 1674.5 | 119268.9988 | 1677.5 | 121218.9988 | 1680.5 | 117118.9988 | 1683 | 113718.9988 | 1686 | 119968.9988 | 1688.5 | 120418.9988 | 1691.5 | 79445.9982 | 1694.5 | 119968.9988 | 1697 | 120468.9988 | 1700 | 79745.9982 | 1702.5 | 80745.9982 | 1705.5 | 619.8411 | 1666.5 | 619.8411
1708.5 | 112018.9988 | 1711 | 117668.9988 | 1714 | 119218.9988 | 1716.5 | 119268.9988 | 1719.5 | 80779.3315 | 1722.5 | 78045.9982 | 1725 | 113718.9988 | 1728 | 119968.9988 | 1730.5 | 120418.9988 | 1733.5 | 119218.9988 | 1736.5 | 119968.9988 | 1739 | 120468.9988 | 1742 | 79745.9982 | 1744.5 | 121168.9988 | 1747.5 | 297.5051 | 1708.5 | 297.5051
1750.5 | 637.5784 | 1753 | 78412.6648 | 1756 | 119218.9988 | 1758.5 | 238637.9994 | 1761.5 | 80779.3315 | 1764.5 | 117118.9988 | 1767 | 113718.9988 | 1770 | 119968.9988 | 1772.5 | 120418.9988 | 1775.5 | 119218.9988 | 1778.5 | 119968.9988 | 1781 | 80279.3315 | 1784 | 119668.9988 | 1786.5 | 121168.9988 | 1789.5 | 10.0028 | 1750.5 | 10.0028
1792.5 | 74645.9982 | 1795 | 117668.9988 | 1798 | 119218.9988 | 1800.5 | 119268.9988 | 1803.5 | 121218.9988 | 1806.5 | 78045.9982 | 1809 | 113718.9988 | 1812 | 240037.9994 | 1814.5 | 120418.9988 | 1817.5 | 79445.9982 | 1820.5 | 119968.9988 | 1823 | 120468.9988 | 1826 | 119668.9988 | 1828.5 | 121168.9988 | 1831.5 | 526.126 | 1792.5 | 526.126
1834.5 | 9109.9237 | 1837 | 117668.9988 | 1840 | 119218.9988 | 1842.5 | 119268.9988 | 1845.5 | 80779.3315 | 1848.5 | 78045.9982 | 1851 | 113718.9988 | 1854 | 119968.9988 | 1856.5 | 120418.9988 | 1859.5 | 79445.9982 | 1862.5 | 119968.9988 | 1865 | 120468.9988 | 1868 | 119668.9988 | 1870.5 | 121168.9988 | 1873.5 | 1827.1459 | 1834.5 | 1827.1459
1876.5 | 72759.3834 | 1879 | 235038.2547 | 1882 | 119218.9988 | 1884.5 | 119268.9988 | 1887.5 | 80779.3315 | 1890.5 | 78045.9982 | 1893 | 113718.9988 | 1896 | 119968.9988 | 1898.5 | 80245.9982 | 1901.5 | 237838.6286 | 1904.5 | 119968.9988 | 1907 | 120468.9988 | 1909.5 | 119668.9988 | 1912.5 | 121168.9988 | 1915.5 | 46.0135 | 1876.5 | 46.0135
1918.5 | 44.332 | 1921 | 235138.1274 | 1924 | 119218.9988 | 1926.5 | 119268.9988 | 1929.5 | 121218.9988 | 1932 | 117118.9988 | 1935 | 113718.9988 | 1937.5 | 119968.9988 | 1940.5 | 120418.9988 | 1943.5 | 237838.6705 | 1946.5 | 240037.9994 | 1949 | 120468.9988 | 1952 | 119668.9988 | 1954.5 | 121168.9988 | 1957.5 | 796.5255 | 1918.5 | 44.332
1960.5 | 0.80397 | 1963 | 117519.0637 | 1966 | 119218.9988 | 1968.5 | 119268.9988 | 1971.5 | 121218.9988 | 1974 | 117118.9988 | 1977 | 113718.9988 | 1979.5 | 119968.9988 | 1982.5 | 120418.9988 | 1985.5 | 237639.0477 | 1988 | 119968.9988 | 1991 | 120468.9988 | 1993.5 | 119668.9988 | 1996.5 | 121168.9988 | 1999.5 | 1981.8437 | 1960.5 | 0.80397
2002 | 2.6855 | 2005 | 117519.0637 | 2007.5 | 119218.9988 | 2010.5 | 119268.9988 | 2013.5 | 121218.9988 | 2016 | 117118.9988 | 2019 | 113718.9988 | 2021.5 | 240037.9994 | 2024.5 | 120418.9988 | 2027.5 | 118619.9219 | 2030.5 | 119968.9988 | 2033 | 80279.3315 | 2036 | 119668.9988 | 2038.5 | 121168.9988 | 2041.5 | 3498.5996 | 2002 | 2.6855
2044.5 | 20.1298 | 2047 | 117519.0637 | 2050 | 238138.2514 | 2052.5 | 119268.9988 | 2055.5 | 121218.9988 | 2058.5 | 117118.9988 | 2061 | 113718.9988 | 2064 | 119968.9988 | 2066.5 | 120418.9988 | 2069.5 | 118719.6705 | 2072 | 119968.9988 | 2075 | 120468.9988 | 2077.5 | 119668.9988 | 2080.5 | 121168.9988 | 2083.5 | 5304.2482 | 2044.5 | 20.1298
2086.5 | 14.7007 | 2089 | 235138.1274 | 2091.5 | 119218.9988 | 2094.5 | 119268.9988 | 2097.5 | 121218.9988 | 2100.5 | 117118.9988 | 2103 | 113718.9988 | 2106 | 119968.9988 | 2108.5 | 120418.9988 | 2111.5 | 39357.0945 | 2114.5 | 119968.9988 | 2117 | 120468.9988 | 2120 | 79745.9982 | 2122.5 | 121168.9988 | 2125.5 | 5089.5699 | 2086.5 | 14.7007
2128 | 3.9396 | 2131 | 117519.0637 | 2133.5 | 119218.9988 | 2136.5 | 119268.9988 | 2139.5 | 121218.9988 | 2142.5 | 117118.9988 | 2145 | 113718.9988 | 2147.5 | 119968.9988 | 2150.5 | 120418.9988 | 2153.5 | 25834.8443 | 2156 | 119968.9988 | 2159 | 120468.9988 | 2162 | 79745.9982 | 2164.5 | 121168.9988 | 2167.5 | 581.7142 | 2128 | 3.9396
2170.5 | 39.0404 | 2173 | 235138.1274 | 2175.5 | 119218.9988 | 2178.5 | 119268.9988 | 2181.5 | 121218.9988 | 2184.5 | 117118.9988 | 2187 | 113718.9988 | 2189.5 | 119968.9988 | 2192.5 | 80245.9982 | 2195.5 | 38.2847 | 2198.5 | 3213.6381 | 2201 | 80279.3315 | 2204 | 79745.9982 | 2206.5 | 80745.9982 | 2209.5 | 2334.8228 | 2170.5 | 38.2847
2212 | 18.8652 | 2215 | 117519.0637 | 2218 | 119218.9988 | 2220.5 | 119268.9988 | 2223.5 | 121218.9988 | 2226.5 | 78045.9982 | 2229 | 113718.9988 | 2231.5 | 119968.9988 | 2234.5 | 120418.9988 | 2237.5 | 43.1959 | 2240 | 833.9842 | 2243 | 40089.663 | 2246 | 47807.5969 | 2248.5 | 48407.5969 | 2251.5 | 426.9023 | 2212 | 18.8652
2254 | 19.9843 | 2257 | 117369.2548 | 2260 | 10025.6743 | 2262.5 | 26426.4389 | 2265.5 | 24163.7939 | 2268.5 | 3923.1702 | 2271 | 113718.9988 | 2273.5 | 119968.9988 | 2276.5 | 24003.7939 | 2279.5 | 45.969 | 2282 | 54198.5494 | 2285 | 9545.5047 | 2287.5 | 9481.5047 | 2290.5 | 9601.5047 | 2293.5 | 360.6398 | 2254 | 19.9843
2296.5 | 19.4237 | 2299 | 36.6064 | 2301.5 | 57.5855 | 2304.5 | 23599.0082 | 2307.5 | 41831.9366 | 2310 | 23.3859 | 2313 | 0.19035 | 2315.5 | 23452.2163 | 2318.5 | 51239.2023 | 2321.5 | 31.2346 | 2324 | 5403.734 | 2327 | 46316.2116 | 2330 | 6373.9774 | 2332.5 | 7249.6162 | 2335.5 | 6639.6888 | 2296.5 | 0.19035
2338 | 41.892 | 2341 | 7.3665 | 2344 | 10.2913 | 2346.5 | 18464.2333 | 2349.5 | 5827.8318 | 2352.5 | 8.4418 | 2355 | 16.5677 | 2357.5 | 11073.4837 | 2360.5 | 39778.1198 | 2363.5 | 34.0701 | 2366 | 11120.308 | 2369 | 21402.3374 | 2371.5 | 12375.6224 | 2374.5 | 2057.0279 | 2377.5 | 9077.1786 | 2338 | 7.3665
2380 | 8.6025 | 2383 | 22.0384 | 2386 | 20.1996 | 2388.5 | 8285.2119 | 2391.5 | 4921.1758 | 2394 | 8.6897 | 2397 | 30.4666 | 2399.5 | 15145.8359 | 2402.5 | 22215.9852 | 2405.5 | 1.7641 | 2408.5 | 24339.6528 | 2411 | 41344.1716 | 2413.5 | 10045.2782 | 2416.5 | 501.5852 | 2419.5 | 98.615 | 2380 | 1.7641
2422.5 | 0.53572 | 2425 | 47.5342 | 2427.5 | 22.8855 | 2430.5 | 7875.6404 | 2433.5 | 4435.0936 | 2436 | 44.2643 | 2439 | 34.9993 | 2441.5 | 3555.5038 | 2444.5 | 30447.4533 | 2447.5 | 49.496 | 2450 | 10705.7885 | 2453 | 30590.5309 | 2455.5 | 40067.3365 | 2458.5 | 3009.4139 | 2461.5 | 2986.0328 | 2422.5 | 0.53572
2464 | 3.148 | 2467 | 6.7373 | 2470 | 59.9574 | 2472.5 | 16521.7141 | 2475.5 | 26567.5782 | 2478.5 | 6.3852 | 2481 | 28.8634 | 2483.5 | 7659.7342 | 2486.5 | 10558.1313 | 2489.5 | 40.4629 | 2492.5 | 10257.7728 | 2495 | 19.2263 | 2497.5 | 16.3499 | 2500.5 | 48.6328 | 2503.5 | 7145.0018 | 2464 | 3.148
2506 | 36.7377 | 2509 | 11.0104 | 2511.5 | 39.7867 | 2514.5 | 42.4565 | 2517.5 | 22.5983 | 2520 | 18.9333 | 2523 | 35.3193 | 2525.5 | 19.213 | 2528.5 | 28.7365 | 2531.5 | 55.2136 | 2534 | 10.4321 | 2537 | 20.6402 | 2540 | 23.7185 | 2542.5 | 26.1535 | 2545.5 | 11.7749 | 2506 | 10.4321
2548 | 41.6736 | 2551 | 55.9129 | 2553.5 | 36.7608 | 2556.5 | 12.9528 | 2559.5 | 35.6915 | 2562 | 34.5237 | 2565 | 88.8169 | 2567.5 | 19.5801 | 2570.5 | 39.997 | 2573.5 | 9.701 | 2576 | 1985.5593 | 2579 | 30.2179 | 2581.5 | 9.5266 | 2584.5 | 9.7189 | 2587.5 | 2.2072 | 2548 | 2.2072
2590 | 43.4951 | 2593 | 22.3133 | 2595.5 | 83.1728 | 2598.5 | 29.7735 | 2601.5 | 12.2905 | 2604 | 15.3827 | 2607 | 10.0328 | 2609.5 | 19.152 | 2612.5 | 21.2772 | 2615.5 | 110.9885 | 2618 | 35.2895 | 2621 | 36.5662 | 2623.5 | 14.1732 | 2626.5 | 6.7129 | 2629.5 | 9.8905 | 2590 | 6.7129
2632 | 1.4514 | 2635 | 74.0993 | 2637.5 | 92.8968 | 2640.5 | 33.1118 | 2643.5 | 41.9445 | 2646 | 133.7711 | 2649 | 121.4816 | 2651.5 | 11.387 | 2654.5 | 13.0575 | 2657.5 | 87.9104 | 2660 | 15.257 | 2663 | 5.5101 | 2665.5 | 4.279 | 2668.5 | 5.3162 | 2671.5 | 10.0969 | 2632 | 1.4514
2674 | 17.8797 | 2677 | 15.5953 | 2679.5 | 31.6799 | 2682.5 | 32.2804 | 2685.5 | 27.915 | 2688 | 60.5217 | 2691 | 84.995 | 2693.5 | 25.3629 | 2696.5 | 8.5736 | 2699.5 | 18.0573 | 2702 | 10.3795 | 2705 | 34.6146 | 2707.5 | 27.7882 | 2710.5 | 7.5979 | 2713.5 | 4.215 | 2674 | 4.215
2716 | 28.5748 | 2719 | 27.7852 | 2721.5 | 44.3161 | 2724.5 | 19.1817 | 2727.5 | 32.2804 | 2730 | 20.4315 | 2733 | 5.0831 | 2735.5 | 36.3908 | 2738.5 | 22.4188 | 2741.5 | 95.8005 | 2744 | 8.8753 | 2747 | 13.8227 | 2749.5 | 27.7882 | 2752.5 | 18.5356 | 2755.5 | 1.3629 | 2716 | 1.3629
2758 | 5.1966 | 2761 | 114.5432 | 2763.5 | 79.9663 | 2766.5 | 28.5545 | 2769.5 | 14.9312 | 2772 | 44.8101 | 2775 | 12.1056 | 2777.5 | 22.2128 | 2780.5 | 7.8178 | 2783.5 | 37.9177 | 2786 | 16.586 | 2789 | 21.7697 | 2791.5 | 6.8408 | 2794.5 | 6.4696 | 2797.5 | 5.2949 | 2758 | 5.1966
2800 | 12.351 | 2803 | 60.7144 | 2805.5 | 55.8339 | 2808.5 | 8.3347 | 2811.5 | 24.5409 | 2814 | 122.6606 | 2817 | 190.076 | 2819.5 | 21.5125 | 2822.5 | 34.3279 | 2825.5 | 55.6278 | 2828 | 14.745 | 2831 | 11.4815 | 2833.5 | 8.9585 | 2836.5 | 22.166 | 2839.5 | 1.9837 | 2800 | 1.9837
2842 | 39.1226 | 2845 | 2.7189 | 2847.5 | 153.2278 | 2850.5 | 34.7277 | 2853.5 | 33.4739 | 2856 | 36.5598 | 2859 | 0.17375 | 2861.5 | 16.8202 | 2864.5 | 30.6702 | 2867.5 | 33.2671 | 2870 | 8.5181 | 2873 | 32.1947 | 2875.5 | 22.805 | 2878.5 | 30.6908 | 2881.5 | 1.4953 | 2842 | 0.17375
2884 | 9.972 | 2887 | 279.5809 | 2889.5 | 32.8383 | 2892.5 | 12.5123 | 2895.5 | 25.3348 | 2898 | 83.5573 | 2901 | 7.695 | 2903.5 | 20.3831 | 2906.5 | 21.3401 | 2909.5 | 183.481 | 2912 | 2.4089 | 2915 | 3.5772 | 2917.5 | 8.2437 | 2920.5 | 6.7129 | 2923.5 | 9.225 | 2884 | 2.4089
2926 | 36.49 | 2929 | 94.8458 | 2931.5 | 35.6924 | 2934.5 | 28.059 | 2937.5 | 37.1045 | 2940 | 8.0925 | 2943 | 0.64108 | 2945.5 | 5.6917 | 2948.5 | 28.9486 | 2951.5 | 20.1555 | 2954 | 12.9044 | 2957 | 29.1444 | 2959.5 | 1.1158 | 2962.5 | 22.7388 | 2965.5 | 28.4592 | 2926 | 0.64108
2968 | 2.2304 | 2971 | 122.9183 | 2973.5 | 1023.1905 | 2976.5 | 21.557 | 2979.5 | 23.2393 | 2982 | 21.8793 | 2985 | 34.0896 | 2987.5 | 9.3379 | 2990.5 | 27.6168 | 2993.5 | 24.073 | 2996 | 17.3504 | 2999 | 31.5293 | 3001.5 | 31.0891 | 3004.5 | 21.0357 | 3007.5 | 1.3189 | 2968 | 1.3189
3010 | 9.1769 | 3013 | 61.2476 | 3015.5 | 361.2601 | 3018.5 | 25.977 | 3021.5 | 16.47 | 3024 | 103.5835 | 3027 | 19.8881 | 3029.5 | 13.5671 | 3032.5 | 16.0966 | 3035.5 | 47.445 | 3038 | 12.3035 | 3041 | 31.0162 | 3043.5 | 25.5858 | 3046.5 | 28.979 | 3049.5 | 4.964 | 3010 | 4.964
3052 | 1.7996 | 3055 | 65.3121 | 3057.5 | 52.6224 | 3060.5 | 16.4828 | 3063 | 20.1593 | 3066 | 51.9422 | 3069 | 25.2135 | 3071.5 | 4.8284 | 3074.5 | 21.782 | 3077.5 | 37.8805 | 3080 | 9.7523 | 3083 | 9.3342 | 3085.5 | 29.4899 | 3088.5 | 1.6396 | 3091.5 | 6.0109 | 3052 | 1.6396
3094 | 42.5279 | 3097 | 31.2111 | 3099.5 | 53.6841 | 3102.5 | 5.2119 | 3105.5 | 11.8618 | 3108 | 25.8656 | 3111 | 178.0448 | 3113.5 | 20.8199 | 3116.5 | 5.4178 | 3119.5 | 41.8803 | 3122 | 20.1969 | 3125 | 23.96 | 3127.5 | 27.8582 | 3130.5 | 8.3462 | 3133 | 30.8722 | 3094 | 5.2119
3136 | 9.8321 | 3138.5 | 33.9137 | 3141.5 | 2.0553 | 3144.5 | 33.7229 | 3147.5 | 26.8161 | 3150 | 121.7924 | 3153 | 221.1303 | 3155.5 | 6.3238 | 3158.5 | 24.6993 | 3161.5 | 2.7397 | 3164 | 13.1245 | 3167 | 6.8213 | 3169.5 | 19.8317 | 3172.5 | 4.4201 | 3175.5 | 8.5673 | 3136 | 2.0553
3178 | 0.88702 | 3181 | 105.392 | 3183.5 | 138.821 | 3186.5 | 3.2247 | 3189.5 | 30.5287 | 3192 | 29.4938 | 3194.5 | 173.0281 | 3197.5 | 23.8997 | 3200.5 | 8.1189 | 3203 | 0.59287 | 3206 | 13.6782 | 3209 | 24.9509 | 3211.5 | 3.1112 | 3214.5 | 21.0357 | 3217.5 | 11.8281 | 3178 | 0.59287
3220 | 79.8704 | 3223 | 16.4355 | 3225.5 | 47.4897 | 3228.5 | 27.2182 | 3231.5 | 2171.5537 | 3234 | 66.9188 | 3237 | 23.2856 | 3239.5 | 5.6917 | 3242.5 | 18.5117 | 3245.5 | 87.2788 | 3248 | 7.4102 | 3251 | 8.0135 | 3253.5 | 11.2657 | 3256.5 | 27.1047 | 3259.5 | 28.3895 | 3220 | 5.6917
3262 | 4.5394 | 3265 | 60.2738 | 3267.5 | 11.8678 | 3270.5 | 4.4938 | 3273.5 | 25.8025 | 3276 | 179.2023 | 3278.5 | 1.084 | 3281.5 | 12.6305 | 3284.5 | 35.1767 | 3287 | 26.7831 | 3290 | 21.008 | 3293 | 23.8945 | 3295.5 | 4.4682 | 3298.5 | 2.1304 | 3301.5 | 718.3667 | 3262 | 1.084
3304 | 0.66301 | 3307 | 96.8932 | 3309.5 | 46.936 | 3312.5 | 22.8445 | 3315 | 20.0368 | 3318 | 27.6822 | 3320.5 | 210.6627 | 3323.5 | 10.2221 | 3326.5 | 9.9602 | 3329.5 | 208.8347 | 3332 | 4.1193 | 3335 | 5.1752 | 3337.5 | 5.1836 | 3340.5 | 12.6755 | 3343.5 | 1.7168 | 3304 | 0.66301
3346 | 70.0285 | 3348.5 | 3.8947 | 3351.5 | 9.503 | 3354.5 | 4.6367 | 3357.5 | 23.0463 | 3360 | 10.7797 | 3362.5 | 37.1177 | 3365.5 | 28.4629 | 3368.5 | 4.7983 | 3371 | 31.9215 | 3374 | 23.7683 | 3376.5 | 28.1579 | 3379.5 | 29.9223 | 3382.5 | 3.908 | 3385.5 | 30.7278 | 3346 | 3.8947
3388 | 40.3043 | 3391 | 3.4063 | 3393.5 | 124.2965 | 3396.5 | 12.1296 | 3399.5 | 8.4417 | 3402 | 44.3172 | 3405 | 89.8145 | 3407.5 | 17.4689 | 3410.5 | 23.2563 | 3413.5 | 45.3713 | 3416 | 16.2946 | 3419 | 1.8904 | 3421.5 | 14.9089 | 3424.5 | 13.6037 | 3427 | 852.8401 | 3388 | 1.8904
3430 | 19.7025 | 3432.5 | 52.1648 | 3435.5 | 16.1997 | 3438.5 | 10.3589 | 3441 | 14.427 | 3444 | 26.6888 | 3447 | 246.4716 | 3449.5 | 28.041 | 3452.5 | 30.6702 | 3455 | 142.4845 | 3458 | 22.8563 | 3461 | 1.0446 | 3463.5 | 19.5851 | 3466.5 | 8.1958 | 3469.5 | 5414.1946 | 3430 | 1.0446
3472 | 55.516 | 3474.5 | 54.2984 | 3477.5 | 195.6529 | 3480.5 | 5.3567 | 3483 | 30.9623 | 3486 | 319.3993 | 3489 | 150.5395 | 3491.5 | 7.7102 | 3494.5 | 4.8457 | 3497.5 | 305.5317 | 3500 | 11.8165 | 3503 | 28.7904 | 3505.5 | 14.852 | 3508.5 | 3.1259 | 3511 | 3071.3572 | 3472 | 3.1259

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 50 |  |  | 2006-09-01 | 8:09
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | Minimums Overall
-133.9 | 224138 |  | -124.9 | 224138 | -119.3 | 234338 | -116 | #DIV/0! | -113.8 | 238638 | -111.5 | 240938 | -133.9 | #DIV/0!
-91.9 | 224138 |  | -82.9 | 224138 | -77.3 | 234338 | -74 | 227538 | -71.8 | 238638 | -69.5 | 240938 | -91.9 | 224138
-49.9 | 224138 |  | -40.9 | 224138 | -35.3 | 234338 | -32 | 227538 | -29.8 | 238638 | -27.5 | 240938 | -49.9 | 224138
-7.9 | 47647.6 |  | 1.1 | 224138 | 6.7 | 234338 | 10 | 227538 | 12.2 | 238638 | 14.5 | 240938 | -7.9 | 47647.6
34.1 | 224138 |  | 43.1 | 224138 | 48.7 | 234338 | 52 | 227538 | 54.2 | 238638 | 56.5 | 240938 | 34.1 | 224138
76.1 | 224138 |  | 85.1 | 224138 | 90.7 | 234338 | 94 | 227538 | 96.2 | 238638 | 98.5 | 240938 | 76.1 | 224138
118.1 | 224138 |  | 127.1 | 224138 | 132.7 | 234338 | 136 | 121169 | 138.2 | 238638 | 140.5 | 240938 | 118.1 | 121169
160.1 | 224138 |  | 169.1 | 119969 | 174.7 | 234338 | 178 | 227538 | 180.2 | 238638 | 182.5 | 240938 | 160.1 | 119969
202.1 | 224138 |  | 211.1 | 224138 | 216.7 | 234338 | 220 | 119219 | 222.2 | 238638 | 224.5 | 240938 | 202.1 | 119219
244.1 | 224138 |  | 253.1 | 224138 | 258.7 | 234338 | 262 | 227538 | 264.2 | 238638 | 266.5 | 120419 | 244.1 | 120419
286.1 | 121219 |  | 295.1 | 224138 | 300.7 | 234338 | 304 | 227538 | 306.2 | 238638 | 308.5 | 240938 | 286.1 | 121219
328.1 | 224138 |  | 337.1 | 224138 | 342.7 | 234338 | 346 | 227538 | 348.2 | 238638 | 350.5 | 240938 | 328.1 | 224138
370.1 | 224138 |  | 379.1 | 224138 | 384.7 | 234338 | 388 | 227538 | 390.2 | 238638 | 392.5 | 240938 | 370.1 | 224138
412.1 | 224138 |  | 421 | 224138 | 426.6 | 234338 | 430 | 227538 | 432.2 | 238638 | 434.3 | 240938 | 412.1 | 224138
454.1 | 224138 |  | 463.1 | 224138 | 468.7 | 234338 | 472 | 227538 | 474.2 | 238638 | 476.5 | 240938 | 454.1 | 224138
496.1 | 224138 |  | 504.9 | 224138 | 510.6 | 120469 | 513.9 | 227538 | 516.2 | 238638 | 518.3 | 240938 | 496.1 | 120469
538.1 | 224138 |  | 547 | 224138 | 552.7 | 234338 | 555.9 | 227538 | 558.2 | 238638 | 560.3 | 240938 | 538.1 | 224138
580 | 224138 |  | 589.1 | 224138 | 594.7 | 234338 | 597.9 | 113719 | 600.1 | 238638 | 602.4 | 240938 | 580 | 113719
622.1 | 224138 |  | 631.2 | 224138 | 636.8 | 234338 | 639.9 | 227538 | 642.2 | 238638 | 644.4 | 240938 | 622.1 | 224138
664 | 224138 |  | 673 | 224138 | 678.5 | 120469 | 682 | 227538 | 684.2 | 238638 | 686.3 | 240938 | 664 | 120469
705.9 | 224138 |  | 715.1 | 224138 | 720.6 | 234338 | 723.9 | 227538 | 726.1 | 238638 | 728.4 | 240938 | 705.9 | 224138
748 | 224138 |  | 756.9 | 224138 | 762.5 | 234338 | 765.9 | 227538 | 768.2 | 238638 | 770.3 | 240938 | 748 | 224138
790 | 112019 |  | 799.1 | 224138 | 804.5 | 234338 | 808 | 227538 | 810.2 | 238638 | 812.4 | 240938 | 790 | 112019
832.1 | 224138 |  | 841.1 | 224138 | 846.6 | 234338 | 849.9 | 227538 | 852.2 | 238638 | 854.3 | 240938 | 832.1 | 224138
874.1 | 224138 |  | 882.9 | 224138 | 888.6 | 234338 | 891.8 | 227538 | 894.2 | 238638 | 896.2 | 240938 | 874.1 | 224138
915.9 | 224138 |  | 925.1 | 224138 | 930.6 | 234338 | 934 | 227538 | 936.1 | 238638 | 938.5 | 240938 | 915.9 | 224138
958 | 224138 |  | 966.9 | 224138 | 972.6 | 234338 | 975.9 | 227538 | 978.1 | 238638 | 980.3 | 240938 | 958 | 224138
999.9 | 224138 |  | 1008.9 | 224138 | 1014.5 | 234338 | 1017.8 | 227538 | 1020.1 | 238638 | 1022.2 | 240938 | 999.9 | 224138
1041.9 | 224138 |  | 1050.9 | 224138 | 1056.5 | 234338 | 1059.8 | 227538 | 1062.1 | 238638 | 1064.2 | 240938 | 1041.9 | 224138
1083.9 | 3586.8172 |  | 1092.9 | 11651.3456 | 1098.3 | 234338 | 1101.9 | 227538 | 1104.1 | 238638 | 1106.1 | 240938 | 1083.9 | 3586.8172
1125.9 | 224138 |  | 1134.9 | 224138 | 1140.6 | 234338 | 1143.8 | 227538 | 1146.1 | 238638 | 1148.3 | 240938 | 1125.9 | 224138
1167.9 | 224138 |  | 1176.9 | 224138 | 1182.5 | 234338 | 1185.8 | 227538 | 1188.1 | 238638 | 1190.2 | 240938 | 1167.9 | 224138
1209.9 | 224138 |  | 1218.9 | 224138 | 1224.5 | 234338 | 1227.8 | 227538 | 1230.1 | 238638 | 1232.2 | 240938 | 1209.9 | 224138
1251.9 | 224138 |  | 1260.9 | 224138 | 1266.5 | 234338 | 1269.8 | 227538 | 1272.1 | 238638 | 1274.2 | 240938 | 1251.9 | 224138
1293.9 | 224138 |  | 1302.9 | 224138 | 1308.5 | 234338 | 1311.8 | 227538 | 1314.1 | 238638 | 1316.2 | 240938 | 1293.9 | 224138
1335.9 | 173.8771 |  | 1344.9 | 190.6515 | 1350.5 | 234338 | 1353.8 | 227538 | 1356.1 | 238638 | 1358.2 | 240938 | 1335.9 | 173.8771
1377.9 | 749.0003 |  | 1386.9 | 1308.7436 | 1392.5 | 234338 | 1395.8 | 227538 | 1398.1 | 238638 | 1400.2 | 240938 | 1377.9 | 749.0003
1419.9 | 224340.8967 |  | 1428.9 | 224138 | 1434.5 | 234338 | 1437.8 | 227538 | 1440.1 | 238638 | 1442.2 | 240938 | 1419.9 | 224138
1461.9 | 224138 |  | 1470.9 | 224138 | 1476.5 | 234338 | 1479.8 | 227538 | 1482.1 | 80946 | 1484.2 | 240938 | 1461.9 | 80946
1503.9 | 121219 |  | 1512.9 | 120419 | 1518.3 | 234338 | 1521.8 | 119669 | 1524.1 | 42.7005 | 1526 | 26.3219 | 1503.9 | 26.3219
1545.9 | 2024.9266 |  | 1554.9 | 2229.5747 | 1560.5 | 117669 | 1563.8 | 80746 | 1566.1 | 6.4821 | 1568.2 | 4.5873 | 1545.9 | 4.5873
1587.9 | 303.5171 |  | 1596.9 | 314.6299 | 1602.5 | 79446 | 1605.8 | 80746 | 1608.1 | 1.9311 | 1610.2 | 6.2005 | 1587.9 | 1.9311
1629.9 | 112019 |  | 1638.9 | 78046 | 1644.5 | 79446 | 1647.8 | 80746 | 1650.1 | 4.3625 | 1652.2 | 9.3143 | 1629.9 | 4.3625
1671.9 | 74646 |  | 1680.9 | 112019 | 1686.5 | 79446 | 1689.8 | 79746 | 1692.1 | 0.68852 | 1694.2 | 13.3293 | 1671.9 | 0.68852
1713.9 | 80779.3333 |  | 1722.9 | 78046 | 1728.5 | 117669 | 1731.8 | 79746 | 1734.1 | 0.98318 | 1736.2 | 6.19 | 1713.9 | 0.98318
1755.9 | 6955.8894 |  | 1764.9 | 112019 | 1770.5 | 80279.3333 | 1773.8 | 113719 | 1776.1 | 0.69085 | 1778.2 | 3.4046 | 1755.9 | 0.69085
1797.9 | 74646 |  | 1806.9 | 78046 | 1812.5 | 79446 | 1815.8 | 113719 | 1818.1 | 4.3739 | 1820.2 | 11.0389 | 1797.9 | 4.3739
1839.9 | 75221.7233 |  | 1848.9 | 43742.3553 | 1854.5 | 79446 | 1857.8 | 119219 | 1860.1 | 2.3667 | 1862.2 | 4.7228 | 1839.9 | 2.3667
1881.9 | 76315.0393 |  | 1890.9 | 4313.9256 | 1896.5 | 79446 | 1899.7 | 79446 | 1902 | 2.931 | 1904.2 | 0.89748 | 1881.9 | 0.89748
1923.9 | 23628.7411 |  | 1932.7 | 4649.8231 | 1938.4 | 59546.9764 | 1941.8 | 113719 | 1944 | 5.7411 | 1946.2 | 13.966 | 1923.9 | 5.7411
1965.9 | 1185.9428 |  | 1974.7 | 1702.9093 | 1980.3 | 47619.5812 | 1983.7 | 79490.619 | 1985.8 | 4.6353 | 1988.2 | 2.7268 | 1965.9 | 2.7268
2007.7 | 120.9929 |  | 2016.6 | 118.9777 | 2022.4 | 39661.8546 | 2025.7 | 59584.6158 | 2028 | 1.7965 | 2030.2 | 4.4522 | 2007.7 | 1.7965
2049.9 | 328.8151 |  | 2058.9 | 451.8037 | 2064.4 | 59559.5 | 2067.7 | 59559.5 | 2069.9 | 0.98318 | 2072.2 | 4.7228 | 2049.9 | 0.98318
2091.8 | 6695.0909 |  | 2100.9 | 6695.0909 | 2106.5 | 29701.4858 | 2109.7 | 47663.8859 | 2112.1 | 5.1989 | 2114.2 | 1.746 | 2091.8 | 1.746
2133.7 | 137.8525 |  | 2142.7 | 185.3274 | 2148.4 | 13179.21 | 2151.7 | 9210.6439 | 2153.9 | 0.68679 | 2156.2 | 7.3145 | 2133.7 | 0.68679
2175.8 | 5676.8794 |  | 2184.8 | 8130.5006 | 2190.5 | 3304.9226 | 2193.7 | 5096.8585 | 2196 | 2.4627 | 2198.2 | 6.1374 | 2175.8 | 2.4627
2217.8 | 649.0496 |  | 2226.7 | 1137.018 | 2232.4 | 831.7836 | 2235.8 | 2560.5743 | 2237.9 | 0.7015 | 2240.2 | 0.67967 | 2217.8 | 0.67967
2259.8 | 5649.6923 |  | 2268.7 | 5649.6923 | 2274.4 | 1269.2875 | 2277.7 | 1143.9869 | 2279.8 | 7.9272 | 2282.2 | 0.67946 | 2259.8 | 0.67946
2301.8 | 487.1046 |  | 2310.7 | 141.7674 | 2316.3 | 797.3257 | 2319.7 | 159.7286 | 2321.9 | 1.4562 | 2324.2 | 5.0403 | 2301.8 | 1.4562
2343.8 | 709.662 |  | 2352.7 | 350.112 | 2358.4 | 1790.5389 | 2361.7 | 321.5137 | 2363.8 | 7.1758 | 2366.2 | 1.0154 | 2343.8 | 1.0154
2385.8 | 359.0453 |  | 2394.6 | 555.5336 | 2400.4 | 430.9455 | 2403.7 | 381.5307 | 2405.9 | 4.6017 | 2408.2 | 0.67826 | 2385.8 | 0.67826
2427.8 | 31.6271 |  | 2436.7 | 31.3434 | 2442.3 | 97.0197 | 2445.6 | 287.3634 | 2447.8 | 3.2422 | 2450.2 | 1.9067 | 2427.8 | 1.9067
2469.8 | 100.8488 |  | 2478.7 | 41.313 | 2484.5 | 20.4486 | 2487.7 | 17.5935 | 2489.9 | 4.7848 | 2492.2 | 0.67995 | 2469.8 | 0.67995
2511.7 | 23.7949 |  | 2520.6 | 20.4303 | 2526.3 | 11.7441 | 2529.7 | 22.5935 | 2531.9 | 8.3203 | 2534.2 | 1.1413 | 2511.7 | 1.1413
2553.7 | 14.2287 |  | 2562.6 | 20.7938 | 2568.3 | 9.4584 | 2571.6 | 10.8459 | 2573.8 | 3.6394 | 2576.2 | 4.7208 | 2553.7 | 3.6394
2595.7 | 12.1056 |  | 2604.6 | 9.4787 | 2610.3 | 23.4605 | 2613.6 | 8.0829 | 2615.8 | 2.1864 | 2618.2 | 0.68392 | 2595.7 | 0.68392
2637.7 | 7.9973 |  | 2646.6 | 12.6879 | 2652.3 | 6.8874 | 2655.6 | 5.663 | 2657.8 | 11.429 | 2660.2 | 1.6609 | 2637.7 | 1.6609
2679.7 | 11.0333 |  | 2688.6 | 9.9124 | 2694.3 | 9.4963 | 2697.6 | 4.8121 | 2699.8 | 4.2718 | 2702.2 | 1.9619 | 2679.7 | 1.9619
2721.7 | 7.6894 |  | 2730.6 | 1.7764 | 2736.3 | 9.5474 | 2739.6 | 8.2003 | 2741.8 | 2.8068 | 2744.2 | 6.1814 | 2721.7 | 1.7764
2763.7 | 16.2059 |  | 2772.6 | 4.7995 | 2778.3 | 5.9791 | 2781.6 | 7.8426 | 2783.8 | 6.6863 | 2786.2 | 12.3663 | 2763.7 | 4.7995
2805.7 | 9.6638 |  | 2814.6 | 22.7072 | 2820.3 | 6.4717 | 2823.6 | 4.9854 | 2825.8 | 1.2889 | 2828.2 | 1.0575 | 2805.7 | 1.0575
2847.7 | 2.8591 |  | 2856.6 | 1.5466 | 2862.3 | 1.8989 | 2865.6 | 5.5468 | 2867.8 | 2.9373 | 2870.2 | 1.181 | 2847.7 | 1.181
2889.7 | 11.3883 |  | 2898.6 | 1.1413 | 2904.3 | 3.821 | 2907.6 | 2.6429 | 2909.8 | 1.4132 | 2912.2 | 6.4697 | 2889.7 | 1.1413
2931.7 | 16.7026 |  | 2940.6 | 1.8705 | 2946.3 | 2.8229 | 2949.6 | 2.542 | 2951.8 | 3.1964 | 2954.2 | 1.2653 | 2931.7 | 1.2653
2973.7 | 3.0669 |  | 2982.6 | 2.1775 | 2988.3 | 3.8938 | 2991.6 | 3.2038 | 2993.8 | 1.3668 | 2996.2 | 0.68421 | 2973.7 | 0.68421
3015.7 | 6.9006 |  | 3024.6 | 2.7662 | 3030.3 | 7.7634 | 3033.6 | 3.3018 | 3035.8 | 5.4162 | 3038.2 | 1.2231 | 3015.7 | 1.2231
3057.6 | 3.6505 |  | 3066.6 | 2.2204 | 3072.3 | 10.6645 | 3075.6 | 3.0761 | 3077.8 | 1.4132 | 3080.1 | 1.0996 | 3057.6 | 1.0996
3099.7 | 6.5795 |  | 3108.6 | 6.7957 | 3114.3 | 3.3301 | 3117.6 | 4.0916 | 3119.7 | 10.7648 | 3122.1 | 2.7442 | 3099.7 | 2.7442
3141.6 | 1.9665 |  | 3150.6 | 7.6852 | 3156.2 | 2.87 | 3159.6 | 0.7396 | 3161.8 | 9.9177 | 3164.2 | 1.9496 | 3141.6 | 0.7396
3183.7 | 4.6179 |  | 3192.5 | 7.1592 | 3198.2 | 1.3983 | 3201.4 | 2.3528 | 3203.8 | 3.5078 | 3206.2 | 3.7721 | 3183.7 | 1.3983
3225.7 | 6.6744 |  | 3234.6 | 7.0611 | 3240.3 | 1.3013 | 3243.6 | 2.9822 | 3245.8 | 2.931 | 3248.2 | 12.7867 | 3225.7 | 1.3013
3267.7 | 5.2769 |  | 3276.5 | 0.5 | 3282.2 | 12.0289 | 3285.4 | 2.009 | 3287.8 | 1.7146 | 3290.2 | 3.1638 | 3267.7 | 0.5
3309.6 | 0.79411 |  | 3318.5 | 0.16092 | 3324.3 | 2.0286 | 3327.5 | 3.3251 | 3329.8 | 2.4981 | 3332.1 | 0.93719 | 3309.6 | 0.16092
3351.6 | 6.0115 |  | 3360.5 | 2.9368 | 3366 | 2.3441 | 3369.4 | 2.8759 | 3371.8 | 13.4713 | 3374.1 | 0.93134 | 3351.6 | 0.93134
3393.7 | 8.8841 |  | 3402.6 | 8.2732 | 3408.3 | 1.4873 | 3411.6 | 5.3279 | 3413.7 | 2.3309 | 3416.1 | 1.8212 | 3393.7 | 1.4873
3435.5 | 7.4828 |  | 3444.6 | 4.3683 | 3450.1 | 2.4811 | 3453.5 | 1.8224 | 3455.8 | 4.8016 | 3458.1 | 7.3652 | 3435.5 | 1.8224
3477.5 | 6.1164 |  | 3486.6 | 6.2309 | 3492.2 | 13.1126 | 3495.6 | 4.5422 | 3497.7 | 3.2852 | 3500 | 1.0214 | 3477.5 | 1.0214

## C5-C6
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 148.4359 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38961.339 | 1 | 0 | 38961.339 | 1 | 0 |  | -100.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3395 | 1 | 0 | 38961.3395 | 1 | 0 |  | -58.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.34 | 1 | 0 | 38961.34 | 1 | 0 |  | -16.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3405 | 1 | 0 | 38961.3405 | 1 | 0 |  | 25.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.341 | 1 | 0 | 38961.341 | 1 | 0 |  | 67.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3414 | 1 | 0 | 38961.3415 | 1 | 0 |  | 109.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3419 | 1 | 0 | 38961.3419 | 1 | 0 |  | 151.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3424 | 1 | 0 | 38961.3424 | 1 | 0 |  | 193.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3429 | 1 | 0 | 38961.3429 | 1 | 0 |  | 235.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3434 | 1 | 0 | 38961.3434 | 1 | 0 |  | 277.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3439 | 1 | 0 | 38961.3439 | 1 | 0 |  | 319.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3444 | 1 | 0 | 38961.3444 | 1 | 0 |  | 361.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3448 | 1 | 0 | 38961.3449 | 1 | 0 |  | 403.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3453 | 1 | 0 | 38961.3453 | 1 | 0 |  | 445.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3458 | 1 | 0 | 38961.3458 | 1 | 0 |  | 487.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3463 | 1 | 0 | 38961.3463 | 1 | 0 |  | 529.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3468 | 1 | 0 | 38961.3468 | 1 | 0 |  | 571.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3473 | 1 | 0 | 38961.3473 | 1 | 0 |  | 613.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3478 | 1 | 0 | 38961.3478 | 1 | 0 |  | 655.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3483 | 1 | 0 | 38961.3483 | 1 | 0 |  | 697.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3487 | 1 | 0 | 38961.3487 | 1 | 0 |  | 739.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3492 | 1 | 0 | 38961.3492 | 1 | 0 |  | 781.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3497 | 1 | 0 | 38961.3497 | 1 | 0 |  | 823.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3502 | 1 | 0 | 38961.3502 | 1 | 0 |  | 865.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3507 | 1 | 0 | 38961.3507 | 1 | 0 |  | 907.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3512 | 1 | 0 | 38961.3512 | 1 | 0 |  | 949.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3517 | 1 | 0 | 38961.3517 | 1 | 0 |  | 991.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3521 | 1 | 0 | 38961.3522 | 1 | 0 |  | 1033.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3526 | 1 | 0 | 38961.3526 | 1 | 0 |  | 1075.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3531 | 1 | 0 | 38961.3531 | 1 | 0 |  | 1117.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3536 | 1 | 0 | 38961.3536 | 1 | 0 |  | 1159.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3541 | 1 | 0 | 38961.3541 | 1 | 0 |  | 1201.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3546 | 1 | 0 | 38961.3546 | 1 | 0 |  | 1243.5 | 1383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3551 | 1 | 0 | 38961.3551 | 1 | 0 |  | 1285.5 | 1425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3555 | 1 | 0 | 38961.3556 | 1 | 0 |  | 1327.5 | 1467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.356 | 1 | 0 | 38961.356 | 1 | 0 |  | 1369.5 | 1509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3565 | 1 | 0 | 38961.3565 | 1 | 0 |  | 1411.5 | 1551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.357 | 1 | 0 | 38961.357 | 1 | 0 |  | 1453.5 | 1593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38961.3575 | 3 | 0 | 38961.3575 | 1 | 0 |  | 1495.5 | 1635.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 80946 | 243038 | 80945.9982
38961.358 | 1225 | 1 | 38961.358 | 1909 | 0 |  | 1537.5 | 1677.5 | 74.7863 | 0.06105 | 116.5446 | 0 | 0.74786 | 0.0006105 | 1.1654 | 0 | 0.74725 | 1.1654 | 98.8556 | 27.3641 | 25897.4905
38961.3585 | 2297 | 43 | 38961.3585 | 2078 | 36 |  | 1579.5 | 1719.5 | 140.232 | 2.6252 | 126.862 | 2.1978 | 1.4023 | 0.026252 | 1.2686 | 0.021978 | 1.3761 | 1.2466 | 6.4821 | 23.7707 | 40.8138
38961.3589 | 1950 | 28 | 38961.359 | 2297 | 32 |  | 1621.5 | 1761.5 | 119.0476 | 1.7094 | 140.232 | 1.9536 | 1.1905 | 0.017094 | 1.4023 | 0.019536 | 1.1734 | 1.3828 | 32.7375 | 6.2005 | 94.5372
38961.3594 | 1964 | 24 | 38961.3594 | 1929 | 21 |  | 1663.5 | 1803.5 | 119.9023 | 1.4652 | 117.7656 | 1.2821 | 1.199 | 0.014652 | 1.1777 | 0.012821 | 1.1844 | 1.1648 | 25.2252 | 27.5314 | 398.8196
38961.3599 | 1910 | 13 | 38961.3599 | 2056 | 14 |  | 1705.5 | 1845.5 | 116.6056 | 0.79365 | 125.5189 | 0.8547 | 1.1661 | 0.0079365 | 1.2552 | 0.008547 | 1.1581 | 1.2466 | 28.5222 | 18.8357 | 619.8411
38961.3604 | 2138 | 12 | 38961.3604 | 2133 | 10 |  | 1747.5 | 1887.5 | 130.525 | 0.7326 | 130.2198 | 0.6105 | 1.3053 | 0.007326 | 1.3022 | 0.006105 | 1.2979 | 1.2961 | 14.3573 | 14.5314 | 297.5051
38961.3609 | 2391 | 10 | 38961.3609 | 2360 | 5 |  | 1789.5 | 1929.5 | 145.9707 | 0.6105 | 144.0781 | 0.30525 | 1.4597 | 0.006105 | 1.4408 | 0.0030525 | 1.4536 | 1.4377 | 1.9346 | 3.4046 | 10.0028
38961.3614 | 2000 | 8 | 38961.3614 | 2194 | 8 |  | 1831.5 | 1971.5 | 122.1001 | 0.4884 | 133.9438 | 0.4884 | 1.221 | 0.004884 | 1.3394 | 0.004884 | 1.2161 | 1.3346 | 22.4732 | 11.0389 | 526.126
38961.3619 | 1922 | 6 | 38961.3619 | 1907 | 5 |  | 1873.5 | 2013.5 | 117.3382 | 0.3663 | 116.4225 | 0.30525 | 1.1734 | 0.003663 | 1.1642 | 0.0030525 | 1.1697 | 1.1612 | 26.888 | 27.8421 | 1827.1459
38961.3623 | 2115 | 6 | 38961.3624 | 2410 | 5 |  | 1915.5 | 2055.5 | 129.1209 | 0.3663 | 147.1306 | 0.30525 | 1.2912 | 0.003663 | 1.4713 | 0.0030525 | 1.2875 | 1.4683 | 21.9638 | 0.89748 | 46.0135
38961.3628 | 2198 | 6 | 38961.3628 | 1929 | 4 |  | 1957.5 | 2097.5 | 134.188 | 0.3663 | 117.7656 | 0.2442 | 1.3419 | 0.003663 | 1.1777 | 0.002442 | 1.3382 | 1.1752 | 10.7575 | 26.6117 | 796.5255
38961.3633 | 1948 | 2 | 38961.3633 | 2232 | 2 |  | 1999.5 | 2139.5 | 118.9255 | 0.1221 | 136.2637 | 0.1221 | 1.1893 | 0.001221 | 1.3626 | 0.001221 | 1.188 | 1.3614 | 25.1275 | 8.9728 | 1981.8437
38961.3638 | 2109 | 2 | 38961.3638 | 1902 | 1 |  | 2041.5 | 2181.5 | 128.7546 | 0.1221 | 116.1172 | 0.06105 | 1.2875 | 0.001221 | 1.1612 | 0.0006105 | 1.2863 | 1.1606 | 15.3526 | 27.9432 | 3498.5996
38961.3643 | 1920 | 2 | 38961.3643 | 1926 | 1 |  | 2083.5 | 2223.5 | 117.2161 | 0.1221 | 117.5824 | 0.06105 | 1.1722 | 0.001221 | 1.1758 | 0.0006105 | 1.1709 | 1.1752 | 26.7683 | 26.3046 | 5304.2482
38961.3648 | 2162 | 1 | 38961.3648 | 1972 | 1 |  | 2125.5 | 2265.5 | 131.9902 | 0.06105 | 120.3907 | 0.06105 | 1.3199 | 0.0006105 | 1.2039 | 0.0006105 | 1.3193 | 1.2033 | 12.4902 | 23.402 | 5089.5699
38961.3653 | 2345 | 2 | 38961.3653 | 2100 | 1 |  | 2167.5 | 2307.5 | 143.1624 | 0.1221 | 128.2051 | 0.06105 | 1.4316 | 0.001221 | 1.2821 | 0.0006105 | 1.4304 | 1.2814 | 3.7065 | 15.9931 | 581.7142
38961.3658 | 2123 | 2 | 38961.3658 | 2062 | 1 |  | 2209.5 | 2349.5 | 129.6093 | 0.1221 | 125.8852 | 0.06105 | 1.2961 | 0.001221 | 1.2589 | 0.0006105 | 1.2949 | 1.2582 | 14.616 | 17.9821 | 2334.8228
38961.3662 | 2383 | 2 | 38961.3662 | 1993 | 1 |  | 2251.5 | 2391.5 | 145.4823 | 0.1221 | 121.6728 | 0.06105 | 1.4548 | 0.001221 | 1.2167 | 0.0006105 | 1.4536 | 1.2161 | 2.0395 | 22.5624 | 426.9023
38961.3667 | 1896 | 1 | 38961.3667 | 2415 | 1 |  | 2293.5 | 2433.5 | 115.7509 | 0.06105 | 147.4359 | 0.06105 | 1.1575 | 0.0006105 | 1.4744 | 0.0006105 | 1.1569 | 1.4737 | 30.6312 | 0.67946 | 360.6398
38961.3672 | 1901 | 1 | 38961.3672 | 2127 | 1 |  | 2335.5 | 2475.5 | 116.0562 | 0.06105 | 129.8535 | 0.06105 | 1.1606 | 0.0006105 | 1.2985 | 0.0006105 | 1.16 | 1.2979 | 28.0176 | 14.3411 | 6639.6888
38961.3677 | 1845 | 1 | 38961.3677 | 2055 | 1 |  | 2377.5 | 2517.5 | 112.6374 | 0.06105 | 125.4579 | 0.06105 | 1.1264 | 0.0006105 | 1.2546 | 0.0006105 | 1.1258 | 1.254 | 31.8936 | 18.3523 | 9077.1786
38961.3682 | 2284 | 1 | 38961.3682 | 2415 | 0 |  | 2419.5 | 2559.5 | 139.4383 | 0.06105 | 147.4359 | 0 | 1.3944 | 0.0006105 | 1.4744 | 0 | 1.3938 | 1.4744 | 6.9012 | 0.67826 | 98.615
38961.3687 | 1987 | 1 | 38961.3687 | 2268 | 1 |  | 2461.5 | 2601.5 | 121.3065 | 0.06105 | 138.4615 | 0.06105 | 1.2131 | 0.0006105 | 1.3846 | 0.0006105 | 1.2125 | 1.384 | 22.5328 | 7.221 | 2986.0328
38961.3692 | 1921 | 1 | 38961.3692 | 2091 | 1 |  | 2503.5 | 2643.5 | 117.2772 | 0.06105 | 127.6557 | 0.06105 | 1.1728 | 0.0006105 | 1.2766 | 0.0006105 | 1.1722 | 1.2759 | 26.6674 | 16.3154 | 7145.0018
38961.3696 | 2150 | 0 | 38961.3697 | 2217 | 0 |  | 2545.5 | 2685.5 | 131.2576 | 0 | 135.348 | 0 | 1.3126 | 0 | 1.3535 | 0 | 1.3126 | 1.3535 | 13.0874 | 9.6698 | 11.7749
38961.3701 | 2346 | 0 | 38961.3701 | 2132 | 0 |  | 2587.5 | 2727.5 | 143.2234 | 0 | 130.1587 | 0 | 1.4322 | 0 | 1.3016 | 0 | 1.4322 | 1.3016 | 3.6394 | 14.0422 | 2.2072
38961.3706 | 2186 | 0 | 38961.3706 | 2061 | 0 |  | 2629.5 | 2769.5 | 133.4554 | 0 | 125.8242 | 0 | 1.3346 | 0 | 1.2582 | 0 | 1.3346 | 1.2582 | 11.2251 | 17.9709 | 9.8905
38961.3711 | 2182 | 0 | 38961.3711 | 2174 | 0 |  | 2671.5 | 2811.5 | 133.2112 | 0 | 132.7228 | 0 | 1.3321 | 0 | 1.3272 | 0 | 1.3321 | 1.3272 | 11.429 | 11.839 | 10.0969
38961.3716 | 2302 | 0 | 38961.3716 | 1875 | 0 |  | 2713.5 | 2853.5 | 140.5372 | 0 | 114.4689 | 0 | 1.4054 | 0 | 1.1447 | 0 | 1.4054 | 1.1447 | 5.6203 | 29.6736 | 4.215
38961.3721 | 2365 | 0 | 38961.3721 | 2069 | 0 |  | 2755.5 | 2895.5 | 144.3834 | 0 | 126.3126 | 0 | 1.4438 | 0 | 1.2631 | 0 | 1.4438 | 1.2631 | 2.8068 | 17.5147 | 1.3629
38961.3726 | 2279 | 0 | 38961.3726 | 2065 | 0 |  | 2797.5 | 2937.5 | 139.1331 | 0 | 126.0684 | 0 | 1.3913 | 0 | 1.2607 | 0 | 1.3913 | 1.2607 | 6.6863 | 17.7424 | 5.2949
38961.373 | 2351 | 0 | 38961.3731 | 1955 | 0 |  | 2839.5 | 2979.5 | 143.5287 | 0 | 119.3529 | 0 | 1.4353 | 0 | 1.1935 | 0 | 1.4353 | 1.1935 | 3.419 | 24.3673 | 1.9837
38961.3735 | 2362 | 0 | 38961.3735 | 2403 | 0 |  | 2881.5 | 3021.5 | 144.2002 | 0 | 146.7033 | 0 | 1.442 | 0 | 1.467 | 0 | 1.442 | 1.467 | 2.9373 | 1.181 | 1.4953
38961.374 | 2199 | 0 | 38961.374 | 2144 | 0 |  | 2923.5 | 3063.5 | 134.2491 | 0 | 130.8913 | 0 | 1.3425 | 0 | 1.3089 | 0 | 1.3425 | 1.3089 | 10.5675 | 13.4039 | 9.225
38961.3745 | 1876 | 0 | 38961.3745 | 2401 | 0 |  | 2965.5 | 3105.5 | 114.5299 | 0 | 146.5812 | 0 | 1.1453 | 0 | 1.4658 | 0 | 1.1453 | 1.4658 | 29.6045 | 1.2653 | 28.4592
38961.375 | 2366 | 0 | 38961.375 | 2193 | 0 |  | 3007.5 | 3147.5 | 144.4444 | 0 | 133.8828 | 0 | 1.4444 | 0 | 1.3388 | 0 | 1.4444 | 1.3388 | 2.7633 | 10.87 | 1.3189
38961.3755 | 2286 | 0 | 38961.3755 | 2402 | 0 |  | 3049.5 | 3189.5 | 139.5604 | 0 | 146.6422 | 0 | 1.3956 | 0 | 1.4664 | 0 | 1.3956 | 1.4664 | 6.3596 | 1.2231 | 4.964
38961.376 | 2264 | 0 | 38961.376 | 2181 | 0 |  | 3091.5 | 3231.5 | 138.2173 | 0 | 133.1502 | 0 | 1.3822 | 0 | 1.3315 | 0 | 1.3822 | 1.3315 | 7.3931 | 11.4801 | 6.0109
38961.3764 | 1842 | 0 | 38961.3765 | 2019 | 0 |  | 3133 | 3273 | 112.4542 | 0 | 123.2601 | 0 | 1.1245 | 0 | 1.2326 | 0 | 1.1245 | 1.2326 | 31.9967 | 20.425 | 30.8722
38961.3769 | 2212 | 0 | 38961.3769 | 1861 | 0 |  | 3175.5 | 3315.5 | 135.0427 | 0 | 113.6142 | 0 | 1.3504 | 0 | 1.1361 | 0 | 1.3504 | 1.1361 | 9.9177 | 30.6491 | 8.5673
38961.3774 | 2149 | 0 | 38961.3774 | 2343 | 0 |  | 3217.5 | 3357.5 | 131.1966 | 0 | 143.0403 | 0 | 1.312 | 0 | 1.4304 | 0 | 1.312 | 1.4304 | 13.1401 | 3.7721 | 11.8281
38961.3779 | 1877 | 0 | 38961.3779 | 1987 | 0 |  | 3259.5 | 3399.5 | 114.591 | 0 | 121.3065 | 0 | 1.1459 | 0 | 1.2131 | 0 | 1.1459 | 1.2131 | 29.5354 | 22.3644 | 28.3895
38961.3784 | 2315 | 1 | 38961.3784 | 2280 | 0 |  | 3301.5 | 3441.5 | 141.3309 | 0.06105 | 139.1941 | 0 | 1.4133 | 0.0006105 | 1.3919 | 0 | 1.4127 | 1.3919 | 5.0623 | 6.6395 | 718.3667
38961.3789 | 2357 | 0 | 38961.3789 | 1871 | 0 |  | 3343.5 | 3483.5 | 143.895 | 0 | 114.2247 | 0 | 1.4389 | 0 | 1.1422 | 0 | 1.4389 | 1.1422 | 3.1557 | 29.9508 | 1.7168
38961.3794 | 1844 | 0 | 38961.3794 | 2010 | 0 |  | 3385.5 | 3525.5 | 112.5763 | 0 | 122.7106 | 0 | 1.1258 | 0 | 1.2271 | 0 | 1.1258 | 1.2271 | 31.8536 | 20.9642 | 30.7278
38961.3798 | 2118 | 1 | 38961.3799 | 2365 | 0 |  | 3427 | 3567 | 129.304 | 0.06105 | 144.3834 | 0 | 1.293 | 0.0006105 | 1.4438 | 0 | 1.2924 | 1.4438 | 15.0564 | 2.8068 | 852.8401
38961.3803 | 2061 | 1 | 38961.3803 | 2075 | 0 |  | 3469.5 | 3609.5 | 125.8242 | 0.06105 | 126.6789 | 0 | 1.2582 | 0.0006105 | 1.2668 | 0 | 1.2576 | 1.2668 | 18.0306 | 17.1749 | 5414.1946
38961.3808 | 2065 | 1 | 38961.3808 | 2227 | 0 |  | 3511 | 3651 | 126.0684 | 0.06105 | 135.9585 | 0 | 1.2607 | 0.0006105 | 1.3596 | 0 | 1.2601 | 1.3596 | 17.8452 | 9.1774 | 3071.3572

## B4-C6
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 148.0696 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38961.339 | 1 | 0 | 38961.339 | 1 | 0 |  | -103 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3395 | 1 | 0 | 38961.3395 | 1 | 0 |  | -61 | 79 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.34 | 1 | 0 | 38961.34 | 1 | 0 |  | -19 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3404 | 1 | 0 | 38961.3405 | 1 | 0 |  | 23 | 163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3409 | 1 | 0 | 38961.3409 | 1 | 0 |  | 65 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3414 | 1 | 0 | 38961.3414 | 1 | 0 |  | 107 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3419 | 2 | 0 | 38961.3419 | 1 | 0 |  | 149 | 289 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121169 | 242438 | 121168.9988
38961.3424 | 1 | 0 | 38961.3424 | 1 | 0 |  | 191 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3429 | 1 | 0 | 38961.3429 | 1 | 0 |  | 233 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3434 | 1 | 0 | 38961.3434 | 1 | 0 |  | 275 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3438 | 1 | 0 | 38961.3439 | 1 | 0 |  | 317 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3443 | 1 | 0 | 38961.3444 | 1 | 0 |  | 359 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3448 | 1 | 0 | 38961.3448 | 1 | 0 |  | 401 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3453 | 1 | 0 | 38961.3453 | 1 | 0 |  | 443 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3458 | 1 | 0 | 38961.3458 | 1 | 0 |  | 485 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3463 | 1 | 0 | 38961.3463 | 1 | 0 |  | 527 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3468 | 1 | 0 | 38961.3468 | 1 | 0 |  | 568.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3472 | 1 | 0 | 38961.3473 | 1 | 0 |  | 610.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3477 | 1 | 0 | 38961.3477 | 1 | 0 |  | 652.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3482 | 1 | 0 | 38961.3482 | 1 | 0 |  | 695 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3487 | 1 | 0 | 38961.3487 | 1 | 0 |  | 736.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3492 | 1 | 0 | 38961.3492 | 1 | 0 |  | 779 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3497 | 1 | 0 | 38961.3497 | 1 | 0 |  | 821 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3502 | 1 | 0 | 38961.3502 | 1 | 0 |  | 862.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3506 | 1 | 0 | 38961.3507 | 1 | 0 |  | 904.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3511 | 1 | 0 | 38961.3512 | 1 | 0 |  | 947 | 1087 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3516 | 1 | 0 | 38961.3516 | 1 | 0 |  | 989 | 1129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3521 | 1 | 0 | 38961.3521 | 1 | 0 |  | 1030.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3526 | 1 | 0 | 38961.3526 | 1 | 0 |  | 1072.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3531 | 1 | 0 | 38961.3531 | 1 | 0 |  | 1115 | 1255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3536 | 1 | 0 | 38961.3536 | 1 | 0 |  | 1156.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3541 | 1 | 0 | 38961.3541 | 1 | 0 |  | 1198.5 | 1338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3545 | 1 | 0 | 38961.3545 | 1 | 0 |  | 1240.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.355 | 1 | 0 | 38961.355 | 1 | 0 |  | 1282.5 | 1422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3555 | 1 | 0 | 38961.3555 | 1 | 0 |  | 1324.5 | 1464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.356 | 1 | 0 | 38961.356 | 1 | 0 |  | 1366.5 | 1506.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3565 | 1 | 0 | 38961.3565 | 1 | 0 |  | 1408.5 | 1548.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.357 | 1 | 0 | 38961.357 | 1 | 0 |  | 1450.5 | 1590.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3575 | 1 | 0 | 38961.3575 | 1 | 0 |  | 1492.5 | 1632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38961.3579 | 2 | 0 | 38961.358 | 1920 | 0 |  | 1534.5 | 1674.5 | 0.1221 | 0 | 117.2161 | 0 | 0.001221 | 0 | 1.1722 | 0 | 0.001221 | 1.1722 | 121169 | 26.3219 | 121168.9988
38961.3584 | 3 | 0 | 38961.3584 | 2319 | 0 |  | 1576.5 | 1716.5 | 0.18315 | 0 | 141.5751 | 0 | 0.0018315 | 0 | 1.4158 | 0 | 0.0018315 | 1.4158 | 80746 | 4.5873 | 80745.9982
38961.3589 | 3 | 0 | 38961.3589 | 1915 | 0 |  | 1618.5 | 1758.5 | 0.18315 | 0 | 116.9109 | 0 | 0.0018315 | 0 | 1.1691 | 0 | 0.0018315 | 1.1691 | 80746 | 26.6517 | 80745.9982
38961.3594 | 3 | 0 | 38961.3594 | 2203 | 0 |  | 1660.5 | 1800.5 | 0.18315 | 0 | 134.4933 | 0 | 0.0018315 | 0 | 1.3449 | 0 | 0.0018315 | 1.3449 | 80746 | 10.0944 | 80745.9982
38961.3599 | 3 | 0 | 38961.3599 | 2130 | 0 |  | 1702.5 | 1842.5 | 0.18315 | 0 | 130.0366 | 0 | 0.0018315 | 0 | 1.3004 | 0 | 0.0018315 | 1.3004 | 80746 | 13.8676 | 80745.9982
38961.3604 | 2 | 0 | 38961.3604 | 2284 | 0 |  | 1744.5 | 1884.5 | 0.1221 | 0 | 139.4383 | 0 | 0.001221 | 0 | 1.3944 | 0 | 0.001221 | 1.3944 | 121169 | 6.19 | 121168.9988
38961.3609 | 2 | 0 | 38961.3609 | 2345 | 0 |  | 1786.5 | 1926.5 | 0.1221 | 0 | 143.1624 | 0 | 0.001221 | 0 | 1.4316 | 0 | 0.001221 | 1.4316 | 121169 | 3.4277 | 121168.9988
38961.3613 | 2 | 0 | 38961.3614 | 2109 | 0 |  | 1828.5 | 1968.5 | 0.1221 | 0 | 128.7546 | 0 | 0.001221 | 0 | 1.2875 | 0 | 0.001221 | 1.2875 | 121169 | 15.0014 | 121168.9988
38961.3618 | 2 | 0 | 38961.3618 | 2316 | 0 |  | 1870.5 | 2010.5 | 0.1221 | 0 | 141.3919 | 0 | 0.001221 | 0 | 1.4139 | 0 | 0.001221 | 1.4139 | 121169 | 4.7228 | 121168.9988
38961.3623 | 2 | 0 | 38961.3623 | 2042 | 0 |  | 1912.5 | 2052.5 | 0.1221 | 0 | 124.6642 | 0 | 0.001221 | 0 | 1.2466 | 0 | 0.001221 | 1.2466 | 121169 | 18.7747 | 121168.9988
38961.3628 | 2 | 0 | 38961.3628 | 1975 | 0 |  | 1954.5 | 2094.5 | 0.1221 | 0 | 120.5739 | 0 | 0.001221 | 0 | 1.2057 | 0 | 0.001221 | 1.2057 | 121169 | 22.8041 | 121168.9988
38961.3633 | 2 | 0 | 38961.3633 | 2361 | 0 |  | 1996.5 | 2136.5 | 0.1221 | 0 | 144.1392 | 0 | 0.001221 | 0 | 1.4414 | 0 | 0.001221 | 1.4414 | 121169 | 2.7268 | 121168.9988
38961.3638 | 2 | 0 | 38961.3638 | 2322 | 0 |  | 2038.5 | 2178.5 | 0.1221 | 0 | 141.7582 | 0 | 0.001221 | 0 | 1.4176 | 0 | 0.001221 | 1.4176 | 121169 | 4.4522 | 121168.9988
38961.3643 | 2 | 0 | 38961.3643 | 2316 | 0 |  | 2080.5 | 2220.5 | 0.1221 | 0 | 141.3919 | 0 | 0.001221 | 0 | 1.4139 | 0 | 0.001221 | 1.4139 | 121169 | 4.7228 | 121168.9988
38961.3647 | 2 | 0 | 38961.3648 | 2076 | 0 |  | 2122.5 | 2262.5 | 0.1221 | 0 | 126.7399 | 0 | 0.001221 | 0 | 1.2674 | 0 | 0.001221 | 1.2674 | 121169 | 16.8295 | 121168.9988
38961.3652 | 2 | 0 | 38961.3652 | 2156 | 0 |  | 2164.5 | 2304.5 | 0.1221 | 0 | 131.6239 | 0 | 0.001221 | 0 | 1.3162 | 0 | 0.001221 | 1.3162 | 121169 | 12.4944 | 121168.9988
38961.3657 | 3 | 0 | 38961.3657 | 1884 | 0 |  | 2206.5 | 2346.5 | 0.18315 | 0 | 115.0183 | 0 | 0.0018315 | 0 | 1.1502 | 0 | 0.0018315 | 1.1502 | 80746 | 28.7357 | 80745.9982
38961.3662 | 5 | 0 | 38961.3662 | 2190 | 0 |  | 2248.5 | 2388.5 | 0.30525 | 0 | 133.6996 | 0 | 0.0030525 | 0 | 1.337 | 0 | 0.0030525 | 1.337 | 48407.6 | 10.7479 | 48407.5969
38961.3667 | 25 | 0 | 38961.3667 | 2087 | 0 |  | 2290.5 | 2430.5 | 1.5263 | 0 | 127.4115 | 0 | 0.015263 | 0 | 1.2741 | 0 | 0.015263 | 1.2741 | 9601.52 | 16.2137 | 9601.5047
38961.3672 | 33 | 0 | 38961.3672 | 2309 | 0 |  | 2332.5 | 2472.5 | 2.0147 | 0 | 140.9646 | 0 | 0.020147 | 0 | 1.4096 | 0 | 0.020147 | 1.4096 | 7249.6364 | 5.0403 | 7249.6162
38961.3677 | 378 | 1 | 38961.3677 | 2401 | 0 |  | 2374.5 | 2514.5 | 23.0769 | 0.06105 | 146.5812 | 0 | 0.23077 | 0.0006105 | 1.4658 | 0 | 0.23016 | 1.4658 | 735.0989 | 1.0154 | 2057.0279
38961.3681 | 403 | 0 | 38961.3682 | 2081 | 0 |  | 2416.5 | 2556.5 | 24.6032 | 0 | 127.0452 | 0 | 0.24603 | 0 | 1.2705 | 0 | 0.24603 | 1.2705 | 501.8313 | 16.5488 | 501.5852
38961.3686 | 78 | 0 | 38961.3686 | 2145 | 0 |  | 2458.5 | 2598.5 | 4.7619 | 0 | 130.9524 | 0 | 0.047619 | 0 | 1.3095 | 0 | 0.047619 | 1.3095 | 3009.4615 | 13.0713 | 3009.4139
38961.3691 | 1621 | 0 | 38961.3691 | 2409 | 0 |  | 2500.5 | 2640.5 | 98.9621 | 0 | 147.0696 | 0 | 0.98962 | 0 | 1.4707 | 0 | 0.98962 | 1.4707 | 49.6225 | 0.67995 | 48.6328
38961.3696 | 1905 | 0 | 38961.3696 | 2080 | 0 |  | 2542.5 | 2682.5 | 116.3004 | 0 | 126.9841 | 0 | 1.163 | 0 | 1.2698 | 0 | 1.163 | 1.2698 | 27.3165 | 16.6048 | 26.1535
38961.3701 | 2184 | 0 | 38961.3701 | 2271 | 0 |  | 2584.5 | 2724.5 | 133.3333 | 0 | 138.6447 | 0 | 1.3333 | 0 | 1.3864 | 0 | 1.3333 | 1.3864 | 11.0522 | 6.7979 | 9.7189
38961.3706 | 2244 | 0 | 38961.3706 | 2286 | 0 |  | 2626.5 | 2766.5 | 136.9963 | 0 | 139.5604 | 0 | 1.37 | 0 | 1.3956 | 0 | 1.37 | 1.3956 | 8.0829 | 6.0971 | 6.7129
38961.3711 | 2273 | 0 | 38961.3711 | 1949 | 0 |  | 2668.5 | 2808.5 | 138.7668 | 0 | 118.9866 | 0 | 1.3877 | 0 | 1.1899 | 0 | 1.3877 | 1.1899 | 6.7039 | 24.4423 | 5.3162
38961.3716 | 2226 | 0 | 38961.3716 | 2065 | 0 |  | 2710.5 | 2850.5 | 135.8974 | 0 | 126.0684 | 0 | 1.359 | 0 | 1.2607 | 0 | 1.359 | 1.2607 | 8.9569 | 17.4518 | 7.5979
38961.372 | 2025 | 0 | 38961.372 | 2275 | 0 |  | 2752.5 | 2892.5 | 123.6264 | 0 | 138.8889 | 0 | 1.2363 | 0 | 1.3889 | 0 | 1.2363 | 1.3889 | 19.7719 | 6.6101 | 18.5356
38961.3725 | 2249 | 0 | 38961.3725 | 2027 | 0 |  | 2794.5 | 2934.5 | 137.3016 | 0 | 123.7485 | 0 | 1.373 | 0 | 1.2375 | 0 | 1.373 | 1.2375 | 7.8426 | 19.6537 | 6.4696
38961.373 | 1966 | 0 | 38961.373 | 2400 | 0 |  | 2836.5 | 2976.5 | 120.0244 | 0 | 146.5201 | 0 | 1.2002 | 0 | 1.4652 | 0 | 1.2002 | 1.4652 | 23.3662 | 1.0575 | 22.166
38961.3735 | 1840 | 0 | 38961.3735 | 2012 | 0 |  | 2878.5 | 3018.5 | 112.3321 | 0 | 122.8327 | 0 | 1.1233 | 0 | 1.2283 | 0 | 1.1233 | 1.2283 | 31.8141 | 20.5457 | 30.6908
38961.374 | 2244 | 0 | 38961.374 | 2278 | 0 |  | 2920.5 | 3060.5 | 136.9963 | 0 | 139.072 | 0 | 1.37 | 0 | 1.3907 | 0 | 1.37 | 1.3907 | 8.0829 | 6.4697 | 6.7129
38961.3745 | 1957 | 0 | 38961.3745 | 1975 | 0 |  | 2962.5 | 3102.5 | 119.475 | 0 | 120.5739 | 0 | 1.1947 | 0 | 1.2057 | 0 | 1.1947 | 1.2057 | 23.9336 | 22.8041 | 22.7388
38961.375 | 1984 | 0 | 38961.375 | 2157 | 0 |  | 3004.5 | 3144.5 | 121.1233 | 0 | 131.685 | 0 | 1.2112 | 0 | 1.3168 | 0 | 1.2112 | 1.3168 | 22.247 | 12.4423 | 21.0357
38961.3754 | 1864 | 0 | 38961.3755 | 2199 | 0 |  | 3046.5 | 3186.5 | 113.7973 | 0 | 134.2491 | 0 | 1.138 | 0 | 1.3425 | 0 | 1.138 | 1.3425 | 30.117 | 10.2947 | 28.979
38961.3759 | 2353 | 0 | 38961.3759 | 2399 | 0 |  | 3088.5 | 3228.5 | 143.6508 | 0 | 146.4591 | 0 | 1.4365 | 0 | 1.4646 | 0 | 1.4365 | 1.4646 | 3.0761 | 1.0996 | 1.6396
38961.3764 | 2211 | 0 | 38961.3764 | 2171 | 0 |  | 3130.5 | 3270.5 | 134.9817 | 0 | 132.5397 | 0 | 1.3498 | 0 | 1.3254 | 0 | 1.3498 | 1.3254 | 9.6961 | 11.7172 | 8.3462
38961.3769 | 2292 | 0 | 38961.3769 | 2379 | 0 |  | 3172.5 | 3312.5 | 139.9267 | 0 | 145.2381 | 0 | 1.3993 | 0 | 1.4524 | 0 | 1.3993 | 1.4524 | 5.8194 | 1.9496 | 4.4201
38961.3774 | 1984 | 0 | 38961.3774 | 1921 | 0 |  | 3214.5 | 3354.5 | 121.1233 | 0 | 117.2772 | 0 | 1.2112 | 0 | 1.1728 | 0 | 1.2112 | 1.1728 | 22.247 | 26.2561 | 21.0357
38961.3779 | 1891 | 0 | 38961.3779 | 1917 | 0 |  | 3256.5 | 3396.5 | 115.4457 | 0 | 117.033 | 0 | 1.1545 | 0 | 1.1703 | 0 | 1.1545 | 1.1703 | 28.2591 | 26.5196 | 27.1047
38961.3784 | 2342 | 0 | 38961.3784 | 2351 | 0 |  | 3298.5 | 3438.5 | 142.9792 | 0 | 143.5287 | 0 | 1.4298 | 0 | 1.4353 | 0 | 1.4298 | 1.4353 | 3.5602 | 3.1638 | 2.1304
38961.3788 | 2128 | 0 | 38961.3789 | 2085 | 0 |  | 3340.5 | 3480.5 | 129.9145 | 0 | 127.2894 | 0 | 1.2991 | 0 | 1.2729 | 0 | 1.2991 | 1.2729 | 13.9746 | 16.3252 | 12.6755
38961.3793 | 2303 | 0 | 38961.3793 | 2403 | 0 |  | 3382.5 | 3522.5 | 140.5983 | 0 | 146.7033 | 0 | 1.406 | 0 | 1.467 | 0 | 1.406 | 1.467 | 5.3139 | 0.93134 | 3.908
38961.3798 | 2111 | 0 | 38961.3798 | 2382 | 0 |  | 3424.5 | 3564.5 | 128.8767 | 0 | 145.4212 | 0 | 1.2888 | 0 | 1.4542 | 0 | 1.2888 | 1.4542 | 14.8925 | 1.8212 | 13.6037
38961.3803 | 2214 | 0 | 38961.3803 | 2259 | 0 |  | 3466.5 | 3606.5 | 135.1648 | 0 | 137.9121 | 0 | 1.3516 | 0 | 1.3791 | 0 | 1.3516 | 1.3791 | 9.5474 | 7.3652 | 8.1958
38961.3808 | 2320 | 0 | 38961.3808 | 2303 | 0 |  | 3508.5 | 3648.5 | 141.6361 | 0 | 140.5983 | 0 | 1.4164 | 0 | 1.406 | 0 | 1.4164 | 1.406 | 4.5422 | 5.3139 | 3.1259

## B4-C5
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 146.2381 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38961.3389 | 1 | 0 | 38961.339 | 1 | 0 |  | -106 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3394 | 1 | 0 | 38961.3395 | 1 | 0 |  | -64 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3399 | 1 | 0 | 38961.3399 | 1 | 0 |  | -22 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3404 | 1 | 0 | 38961.3404 | 1 | 0 |  | 20 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3409 | 1 | 1 | 38961.3409 | 1 | 0 |  | 62 | 202 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 573305558.44 | 239438 | 239238.0835
38961.3414 | 1 | 0 | 38961.3414 | 1 | 0 |  | 104 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3419 | 1 | 0 | 38961.3419 | 1 | 0 |  | 146 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3423 | 1 | 0 | 38961.3424 | 1 | 0 |  | 188 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3428 | 1 | 0 | 38961.3429 | 1 | 0 |  | 230 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3433 | 1 | 0 | 38961.3433 | 1 | 0 |  | 272 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3438 | 1 | 0 | 38961.3438 | 1 | 0 |  | 314 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3443 | 1 | 0 | 38961.3443 | 1 | 0 |  | 356 | 496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3448 | 1 | 0 | 38961.3448 | 1 | 0 |  | 398 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3453 | 1 | 0 | 38961.3453 | 1 | 0 |  | 440 | 580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3458 | 1 | 0 | 38961.3458 | 1 | 0 |  | 482 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3462 | 1 | 0 | 38961.3463 | 1 | 0 |  | 524 | 664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3467 | 1 | 0 | 38961.3467 | 1 | 0 |  | 566 | 706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3472 | 1 | 0 | 38961.3472 | 1 | 0 |  | 608 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3477 | 1 | 0 | 38961.3477 | 1 | 0 |  | 650 | 790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3482 | 1 | 0 | 38961.3482 | 1 | 0 |  | 692 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3487 | 1 | 0 | 38961.3487 | 1 | 0 |  | 734 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3492 | 1 | 0 | 38961.3492 | 1 | 0 |  | 776 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3496 | 1 | 0 | 38961.3497 | 1 | 0 |  | 818 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3501 | 1 | 0 | 38961.3502 | 1 | 0 |  | 860 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3506 | 1 | 0 | 38961.3506 | 1 | 0 |  | 902 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3511 | 1 | 0 | 38961.3511 | 1 | 0 |  | 944 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3516 | 1 | 0 | 38961.3516 | 1 | 0 |  | 986 | 1126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3521 | 1 | 0 | 38961.3521 | 1 | 0 |  | 1028 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3526 | 1 | 0 | 38961.3526 | 1 | 0 |  | 1070 | 1210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.353 | 1 | 0 | 38961.3531 | 1 | 0 |  | 1112 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3535 | 1 | 0 | 38961.3536 | 1 | 0 |  | 1154 | 1294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.354 | 1 | 0 | 38961.354 | 1 | 0 |  | 1196 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3545 | 1 | 0 | 38961.3545 | 1 | 0 |  | 1238 | 1378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.355 | 1 | 0 | 38961.355 | 1 | 0 |  | 1280 | 1420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3555 | 1 | 0 | 38961.3555 | 1 | 0 |  | 1322 | 1462 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.356 | 1 | 0 | 38961.356 | 1 | 0 |  | 1364 | 1504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3564 | 1 | 0 | 38961.3565 | 1 | 0 |  | 1406 | 1546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3569 | 1 | 0 | 38961.357 | 1 | 0 |  | 1448 | 1588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3574 | 1 | 0 | 38961.3574 | 1 | 0 |  | 1490 | 1630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239438 | 239438 | 239437.9994
38961.3579 | 2 | 0 | 38961.3579 | 1509 | 0 |  | 1532 | 1672 | 0.1221 | 0 | 92.1245 | 0 | 0.001221 | 0 | 0.92125 | 0 | 0.001221 | 0.92125 | 119669 | 58.7396 | 119668.9988
38961.3584 | 2 | 0 | 38961.3584 | 2164 | 0 |  | 1574 | 1714 | 0.1221 | 0 | 132.1123 | 0 | 0.001221 | 0 | 1.3211 | 0 | 0.001221 | 1.3211 | 119669 | 10.6922 | 119668.9988
38961.3589 | 2 | 0 | 38961.3589 | 2350 | 0 |  | 1616 | 1756 | 0.1221 | 0 | 143.4676 | 0 | 0.001221 | 0 | 1.4347 | 0 | 0.001221 | 1.4347 | 119669 | 1.9311 | 119668.9988
38961.3594 | 2 | 0 | 38961.3594 | 2148 | 0 |  | 1658 | 1798 | 0.1221 | 0 | 131.1355 | 0 | 0.001221 | 0 | 1.3114 | 0 | 0.001221 | 1.3114 | 119669 | 11.5168 | 119668.9988
38961.3598 | 3 | 0 | 38961.3599 | 2379 | 0 |  | 1700 | 1840 | 0.18315 | 0 | 145.2381 | 0 | 0.0018315 | 0 | 1.4524 | 0 | 0.0018315 | 1.4524 | 79746 | 0.68852 | 79745.9982
38961.3603 | 3 | 0 | 38961.3604 | 2332 | 0 |  | 1742 | 1882 | 0.18315 | 0 | 142.3687 | 0 | 0.0018315 | 0 | 1.4237 | 0 | 0.0018315 | 1.4237 | 79746 | 2.7178 | 79745.9982
38961.3608 | 2 | 0 | 38961.3608 | 2149 | 0 |  | 1784 | 1924 | 0.1221 | 0 | 131.1966 | 0 | 0.001221 | 0 | 1.312 | 0 | 0.001221 | 1.312 | 119669 | 11.4649 | 119668.9988
38961.3613 | 2 | 0 | 38961.3613 | 2295 | 0 |  | 1826 | 1966 | 0.1221 | 0 | 140.1099 | 0 | 0.001221 | 0 | 1.4011 | 0 | 0.001221 | 1.4011 | 119669 | 4.3739 | 119668.9988
38961.3618 | 2 | 0 | 38961.3618 | 2340 | 0 |  | 1868 | 2008 | 0.1221 | 0 | 142.8571 | 0 | 0.001221 | 0 | 1.4286 | 0 | 0.001221 | 1.4286 | 119669 | 2.3667 | 119668.9988
38961.3623 | 2 | 0 | 38961.3623 | 1952 | 0 |  | 1909.5 | 2049.5 | 0.1221 | 0 | 119.1697 | 0 | 0.001221 | 0 | 1.1917 | 0 | 0.001221 | 1.1917 | 119669 | 22.7141 | 119668.9988
38961.3628 | 2 | 0 | 38961.3628 | 1903 | 0 |  | 1952 | 2092 | 0.1221 | 0 | 116.1783 | 0 | 0.001221 | 0 | 1.1618 | 0 | 0.001221 | 1.1618 | 119669 | 25.8739 | 119668.9988
38961.3633 | 2 | 0 | 38961.3633 | 2254 | 0 |  | 1993.5 | 2133.5 | 0.1221 | 0 | 137.6068 | 0 | 0.001221 | 0 | 1.3761 | 0 | 0.001221 | 1.3761 | 119669 | 6.2724 | 119668.9988
38961.3637 | 2 | 0 | 38961.3638 | 2168 | 0 |  | 2036 | 2176 | 0.1221 | 0 | 132.3565 | 0 | 0.001221 | 0 | 1.3236 | 0 | 0.001221 | 1.3236 | 119669 | 10.488 | 119668.9988
38961.3642 | 2 | 0 | 38961.3642 | 1847 | 0 |  | 2077.5 | 2217.5 | 0.1221 | 0 | 112.7595 | 0 | 0.001221 | 0 | 1.1276 | 0 | 0.001221 | 1.1276 | 119669 | 29.6903 | 119668.9988
38961.3647 | 3 | 0 | 38961.3647 | 2277 | 0 |  | 2120 | 2260 | 0.18315 | 0 | 139.011 | 0 | 0.0018315 | 0 | 1.3901 | 0 | 0.0018315 | 1.3901 | 79746 | 5.1989 | 79745.9982
38961.3652 | 3 | 0 | 38961.3652 | 2263 | 0 |  | 2162 | 2302 | 0.18315 | 0 | 138.1563 | 0 | 0.0018315 | 0 | 1.3816 | 0 | 0.0018315 | 1.3816 | 79746 | 5.8498 | 79745.9982
38961.3657 | 3 | 0 | 38961.3657 | 2239 | 0 |  | 2204 | 2344 | 0.18315 | 0 | 136.6911 | 0 | 0.0018315 | 0 | 1.3669 | 0 | 0.0018315 | 1.3669 | 79746 | 6.9844 | 79745.9982
38961.3662 | 5 | 0 | 38961.3662 | 1865 | 0 |  | 2246 | 2386 | 0.30525 | 0 | 113.8584 | 0 | 0.0030525 | 0 | 1.1386 | 0 | 0.0030525 | 1.1386 | 47807.6 | 28.4386 | 47807.5969
38961.3667 | 25 | 0 | 38961.3667 | 1851 | 0 |  | 2287.5 | 2427.5 | 1.5263 | 0 | 113.0037 | 0 | 0.015263 | 0 | 1.13 | 0 | 0.015263 | 1.13 | 9481.52 | 29.41 | 9481.5047
38961.3671 | 37 | 0 | 38961.3672 | 2361 | 0 |  | 2330 | 2470 | 2.2589 | 0 | 144.1392 | 0 | 0.022589 | 0 | 1.4414 | 0 | 0.022589 | 1.4414 | 6374 | 1.4562 | 6373.9774
38961.3676 | 546 | 1 | 38961.3676 | 2235 | 0 |  | 2371.5 | 2511.5 | 33.3333 | 0.06105 | 136.4469 | 0 | 0.33333 | 0.0006105 | 1.3645 | 0 | 0.33272 | 1.3645 | 348.2403 | 7.1758 | 12375.6224
38961.3681 | 111 | 1 | 38961.3681 | 2290 | 0 |  | 2413.5 | 2553.5 | 6.7766 | 0.06105 | 139.8046 | 0 | 0.067766 | 0.0006105 | 1.398 | 0 | 0.067155 | 1.398 | 2587.9718 | 4.6017 | 10045.2782
38961.3686 | 67 | 1 | 38961.3686 | 1983 | 0 |  | 2455.5 | 2595.5 | 4.0904 | 0.06105 | 121.0623 | 0 | 0.040904 | 0.0006105 | 1.2106 | 0 | 0.040293 | 1.2106 | 3805.0816 | 20.7958 | 40067.3365
38961.3691 | 2037 | 0 | 38961.3691 | 2286 | 0 |  | 2497.5 | 2637.5 | 124.359 | 0 | 139.5604 | 0 | 1.2436 | 0 | 1.3956 | 0 | 1.2436 | 1.3956 | 17.5935 | 4.7848 | 16.3499
38961.3696 | 1918 | 0 | 38961.3696 | 2092 | 0 |  | 2540 | 2680 | 117.094 | 0 | 127.7167 | 0 | 1.1709 | 0 | 1.2772 | 0 | 1.1709 | 1.2772 | 24.8895 | 14.5019 | 23.7185
38961.3701 | 2161 | 0 | 38961.3701 | 1845 | 0 |  | 2581.5 | 2721.5 | 131.9292 | 0 | 112.6374 | 0 | 1.3193 | 0 | 1.1264 | 0 | 1.3193 | 1.1264 | 10.8459 | 29.8309 | 9.5266
38961.3705 | 2075 | 0 | 38961.3706 | 2168 | 0 |  | 2623.5 | 2763.5 | 126.6789 | 0 | 132.3565 | 0 | 1.2668 | 0 | 1.3236 | 0 | 1.2668 | 1.3236 | 15.44 | 10.488 | 14.1732
38961.371 | 2267 | 0 | 38961.371 | 1895 | 0 |  | 2665.5 | 2805.5 | 138.4005 | 0 | 115.6899 | 0 | 1.384 | 0 | 1.1569 | 0 | 1.384 | 1.1569 | 5.663 | 26.4053 | 4.279
38961.3715 | 1858 | 0 | 38961.3715 | 2004 | 0 |  | 2707.5 | 2847.5 | 113.431 | 0 | 122.3443 | 0 | 1.1343 | 0 | 1.2234 | 0 | 1.1343 | 1.2234 | 28.9225 | 19.5299 | 27.7882
38961.372 | 1858 | 0 | 38961.372 | 2043 | 0 |  | 2749.5 | 2889.5 | 113.431 | 0 | 124.7253 | 0 | 1.1343 | 0 | 1.2473 | 0 | 1.1343 | 1.2473 | 28.9225 | 17.2482 | 27.7882
38961.3725 | 2214 | 0 | 38961.3725 | 2057 | 0 |  | 2791.5 | 2931.5 | 135.1648 | 0 | 125.58 | 0 | 1.3516 | 0 | 1.2558 | 0 | 1.3516 | 1.2558 | 8.1924 | 16.4502 | 6.8408
38961.373 | 2172 | 0 | 38961.373 | 2153 | 0 |  | 2833.5 | 2973.5 | 132.6007 | 0 | 131.4408 | 0 | 1.326 | 0 | 1.3144 | 0 | 1.326 | 1.3144 | 10.2845 | 11.2578 | 8.9585
38961.3735 | 1932 | 0 | 38961.3735 | 2051 | 0 |  | 2875.5 | 3015.5 | 117.9487 | 0 | 125.2137 | 0 | 1.1795 | 0 | 1.2521 | 0 | 1.1795 | 1.2521 | 23.9845 | 16.7908 | 22.805
38961.3739 | 2186 | 0 | 38961.374 | 2362 | 0 |  | 2917.5 | 3057.5 | 133.4554 | 0 | 144.2002 | 0 | 1.3346 | 0 | 1.442 | 0 | 1.3346 | 1.442 | 9.5782 | 1.4132 | 8.2437
38961.3744 | 2336 | 0 | 38961.3744 | 2065 | 0 |  | 2959.5 | 3099.5 | 142.6129 | 0 | 126.0684 | 0 | 1.4261 | 0 | 1.2607 | 0 | 1.4261 | 1.2607 | 2.542 | 15.999 | 1.1158
38961.3749 | 1812 | 0 | 38961.3749 | 2038 | 0 |  | 3001.5 | 3141.5 | 110.6227 | 0 | 124.42 | 0 | 1.1062 | 0 | 1.2442 | 0 | 1.1062 | 1.2442 | 32.1954 | 17.5358 | 31.0891
38961.3754 | 1890 | 0 | 38961.3754 | 1833 | 0 |  | 3043.5 | 3183.5 | 115.3846 | 0 | 111.9048 | 0 | 1.1538 | 0 | 1.119 | 0 | 1.1538 | 1.119 | 26.7397 | 30.6809 | 25.5858
38961.3759 | 1834 | 0 | 38961.3759 | 2362 | 0 |  | 3085.5 | 3225.5 | 111.9658 | 0 | 144.2002 | 0 | 1.1197 | 0 | 1.442 | 0 | 1.1197 | 1.442 | 30.6096 | 1.4132 | 29.4899
38961.3764 | 1857 | 0 | 38961.3764 | 1848 | 0 |  | 3127.5 | 3267.5 | 113.37 | 0 | 112.8205 | 0 | 1.1337 | 0 | 1.1282 | 0 | 1.1337 | 1.1282 | 28.9919 | 29.6201 | 27.8582
38961.3769 | 1979 | 0 | 38961.3769 | 1941 | 0 |  | 3169.5 | 3309.5 | 120.8181 | 0 | 118.4982 | 0 | 1.2082 | 0 | 1.185 | 0 | 1.2082 | 1.185 | 21.0399 | 23.4096 | 19.8317
38961.3773 | 2292 | 0 | 38961.3774 | 1988 | 0 |  | 3211.5 | 3351.5 | 139.9267 | 0 | 121.3675 | 0 | 1.3993 | 0 | 1.2137 | 0 | 1.3993 | 1.2137 | 4.5105 | 20.492 | 3.1112
38961.3778 | 2128 | 0 | 38961.3778 | 1939 | 0 |  | 3253.5 | 3393.5 | 129.9145 | 0 | 118.3761 | 0 | 1.2991 | 0 | 1.1838 | 0 | 1.2991 | 1.1838 | 12.5648 | 23.5369 | 11.2657
38961.3783 | 2263 | 0 | 38961.3783 | 2355 | 0 |  | 3295.5 | 3435.5 | 138.1563 | 0 | 143.7729 | 0 | 1.3816 | 0 | 1.4377 | 0 | 1.3816 | 1.4377 | 5.8498 | 1.7146 | 4.4682
38961.3788 | 2248 | 0 | 38961.3788 | 2337 | 0 |  | 3337.5 | 3477.5 | 137.2405 | 0 | 142.674 | 0 | 1.3724 | 0 | 1.4267 | 0 | 1.3724 | 1.4267 | 6.556 | 2.4981 | 5.1836
38961.3793 | 1828 | 0 | 38961.3793 | 2111 | 0 |  | 3379.5 | 3519.5 | 111.5995 | 0 | 128.8767 | 0 | 1.116 | 0 | 1.2888 | 0 | 1.116 | 1.2888 | 31.0383 | 13.4713 | 29.9223
38961.3798 | 2062 | 0 | 38961.3798 | 2214 | 0 |  | 3421.5 | 3561.5 | 125.8852 | 0 | 135.1648 | 0 | 1.2589 | 0 | 1.3516 | 0 | 1.2589 | 1.3516 | 16.1678 | 8.1924 | 14.9089
38961.3803 | 1983 | 0 | 38961.3803 | 1906 | 0 |  | 3463.5 | 3603.5 | 121.0623 | 0 | 116.3614 | 0 | 1.2106 | 0 | 1.1636 | 0 | 1.2106 | 1.1636 | 20.7958 | 25.6758 | 19.5851
38961.3808 | 2063 | 0 | 38961.3808 | 1936 | 0 |  | 3505.5 | 3645.5 | 125.9463 | 0 | 118.1929 | 0 | 1.2595 | 0 | 1.1819 | 0 | 1.2595 | 1.1819 | 16.1115 | 23.7283 | 14.852

## B3-C6
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 147.2149 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38961.3389 | 1 | 0 | 38961.3389 | 1 | 0 |  | -108.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3394 | 1 | 0 | 38961.3394 | 1 | 0 |  | -66.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3399 | 1 | 0 | 38961.3399 | 1 | 0 |  | -24.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3404 | 1 | 0 | 38961.3404 | 1 | 0 |  | 17.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3409 | 1 | 0 | 38961.3409 | 1 | 0 |  | 59.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3414 | 1 | 0 | 38961.3414 | 1 | 0 |  | 101.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3418 | 1 | 0 | 38961.3419 | 1 | 0 |  | 143.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3423 | 1 | 0 | 38961.3423 | 1 | 0 |  | 185.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3428 | 1 | 0 | 38961.3428 | 1 | 0 |  | 227.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3433 | 1 | 0 | 38961.3433 | 1 | 0 |  | 269.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3438 | 1 | 0 | 38961.3438 | 1 | 0 |  | 311.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3443 | 1 | 0 | 38961.3443 | 1 | 0 |  | 353.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3448 | 1 | 0 | 38961.3448 | 1 | 0 |  | 395.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3452 | 1 | 0 | 38961.3453 | 1 | 0 |  | 437 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3457 | 1 | 0 | 38961.3457 | 1 | 0 |  | 479.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3462 | 2 | 0 | 38961.3462 | 1 | 0 |  | 521 | 661 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 120469 | 241038 | 120468.9988
38961.3467 | 1 | 0 | 38961.3467 | 1 | 0 |  | 563.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3472 | 1 | 0 | 38961.3472 | 1 | 0 |  | 605.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3477 | 1 | 0 | 38961.3477 | 1 | 0 |  | 647.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3481 | 2 | 0 | 38961.3482 | 1 | 0 |  | 689 | 829 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 120469 | 241038 | 120468.9988
38961.3486 | 1 | 0 | 38961.3487 | 1 | 0 |  | 731.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3491 | 1 | 0 | 38961.3491 | 1 | 0 |  | 773 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3496 | 1 | 0 | 38961.3496 | 1 | 0 |  | 815 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3501 | 1 | 0 | 38961.3501 | 1 | 0 |  | 857 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3506 | 1 | 0 | 38961.3506 | 1 | 0 |  | 899 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3511 | 1 | 0 | 38961.3511 | 1 | 0 |  | 941.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3516 | 1 | 0 | 38961.3516 | 1 | 0 |  | 983 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.352 | 1 | 0 | 38961.3521 | 1 | 0 |  | 1025 | 1165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3525 | 1 | 0 | 38961.3525 | 1 | 0 |  | 1067 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.353 | 1 | 0 |  | 1 | 0 |  | 1108 | 1248 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3535 | 1 | 0 | 38961.3535 | 1 | 0 |  | 1151.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.354 | 1 | 0 | 38961.354 | 1 | 0 |  | 1193 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3545 | 1 | 0 | 38961.3545 | 1 | 0 |  | 1235 | 1375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.355 | 1 | 0 | 38961.355 | 1 | 0 |  | 1277 | 1417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3554 | 1 | 0 | 38961.3555 | 1 | 0 |  | 1319 | 1459 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3559 | 1 | 0 | 38961.3559 | 1 | 0 |  | 1361 | 1501 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3564 | 1 | 0 | 38961.3564 | 1 | 0 |  | 1403 | 1543 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3569 | 1 | 0 | 38961.3569 | 1 | 0 |  | 1445 | 1585 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3574 | 1 | 0 | 38961.3574 | 1 | 0 |  | 1487 | 1627 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3579 | 1 | 0 |  | 1 | 0 |  | 1528 | 1668 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38961.3584 | 2 | 0 | 38961.3584 | 1865 | 0 |  | 1571 | 1711 | 0.1221 | 0 | 113.8584 | 0 | 0.001221 | 0 | 1.1386 | 0 | 0.001221 | 1.1386 | 120469 | 29.2965 | 120468.9988
38961.3588 | 2 | 0 | 38961.3589 | 1818 | 0 |  | 1613 | 1753 | 0.1221 | 0 | 110.989 | 0 | 0.001221 | 0 | 1.1099 | 0 | 0.001221 | 1.1099 | 120469 | 32.6392 | 120468.9988
38961.3593 | 2 | 0 | 38961.3594 | 1878 | 0 |  | 1655 | 1795 | 0.1221 | 0 | 114.652 | 0 | 0.001221 | 0 | 1.1465 | 0 | 0.001221 | 1.1465 | 120469 | 28.4015 | 120468.9988
38961.3598 | 2 | 0 | 38961.3598 | 1958 | 0 |  | 1697 | 1837 | 0.1221 | 0 | 119.536 | 0 | 0.001221 | 0 | 1.1954 | 0 | 0.001221 | 1.1954 | 120469 | 23.1553 | 120468.9988
38961.3603 | 2 | 0 | 38961.3603 | 2024 | 0 |  | 1739 | 1879 | 0.1221 | 0 | 123.5653 | 0 | 0.001221 | 0 | 1.2357 | 0 | 0.001221 | 1.2357 | 120469 | 19.1393 | 120468.9988
38961.3608 | 3 | 0 | 38961.3608 | 1842 | 0 |  | 1781 | 1921 | 0.18315 | 0 | 112.4542 | 0 | 0.0018315 | 0 | 1.1245 | 0 | 0.0018315 | 1.1245 | 80279.3333 | 30.911 | 80279.3315
38961.3613 | 2 | 0 | 38961.3613 | 2152 | 0 |  | 1823 | 1963 | 0.1221 | 0 | 131.3797 | 0 | 0.001221 | 0 | 1.3138 | 0 | 0.001221 | 1.3138 | 120469 | 12.053 | 120468.9988
38961.3618 | 2 | 0 | 38961.3618 | 2050 | 0 |  | 1865 | 2005 | 0.1221 | 0 | 125.1526 | 0 | 0.001221 | 0 | 1.2515 | 0 | 0.001221 | 1.2515 | 120469 | 17.6283 | 120468.9988
38961.3622 | 2 | 0 | 38961.3623 | 2287 | 0 |  | 1907 | 2047 | 0.1221 | 0 | 139.6215 | 0 | 0.001221 | 0 | 1.3962 | 0 | 0.001221 | 1.3962 | 120469 | 5.4386 | 120468.9988
38961.3627 | 2 | 0 | 38961.3628 | 2050 | 0 |  | 1949 | 2089 | 0.1221 | 0 | 125.1526 | 0 | 0.001221 | 0 | 1.2515 | 0 | 0.001221 | 1.2515 | 120469 | 17.6283 | 120468.9988
38961.3632 | 2 | 0 | 38961.3632 | 2283 | 0 |  | 1991 | 2131 | 0.1221 | 0 | 139.3773 | 0 | 0.001221 | 0 | 1.3938 | 0 | 0.001221 | 1.3938 | 120469 | 5.6233 | 120468.9988
38961.3637 | 3 | 0 | 38961.3637 | 2245 | 0 |  | 2033 | 2173 | 0.18315 | 0 | 137.0574 | 0 | 0.0018315 | 0 | 1.3706 | 0 | 0.0018315 | 1.3706 | 80279.3333 | 7.4111 | 80279.3315
38961.3642 | 2 | 0 | 38961.3642 | 1907 | 0 |  | 2075 | 2215 | 0.1221 | 0 | 116.4225 | 0 | 0.001221 | 0 | 1.1642 | 0 | 0.001221 | 1.1642 | 120469 | 26.4489 | 120468.9988
38961.3647 | 2 | 0 | 38961.3647 | 2370 | 0 |  | 2117 | 2257 | 0.1221 | 0 | 144.6886 | 0 | 0.001221 | 0 | 1.4469 | 0 | 0.001221 | 1.4469 | 120469 | 1.746 | 120468.9988
38961.3652 | 2 | 0 | 38961.3652 | 2052 | 0 |  | 2159 | 2299 | 0.1221 | 0 | 125.2747 | 0 | 0.001221 | 0 | 1.2527 | 0 | 0.001221 | 1.2527 | 120469 | 17.5136 | 120468.9988
38961.3656 | 3 | 0 | 38961.3657 | 2157 | 0 |  | 2201 | 2341 | 0.18315 | 0 | 131.685 | 0 | 0.0018315 | 0 | 1.3168 | 0 | 0.0018315 | 1.3168 | 80279.3333 | 11.7932 | 80279.3315
38961.3661 | 6 | 0 | 38961.3662 | 1874 | 0 |  | 2243 | 2383 | 0.3663 | 0 | 114.4078 | 0 | 0.003663 | 0 | 1.1441 | 0 | 0.003663 | 1.1441 | 40089.6667 | 28.6756 | 40089.663
38961.3666 | 25 | 0 | 38961.3666 | 2202 | 1 |  | 2285 | 2425 | 1.5263 | 0 | 134.4322 | 0.06105 | 0.015263 | 0 | 1.3443 | 0.0006105 | 0.015263 | 1.3437 | 9545.52 | 9.5584 | 9545.5047
38961.3671 | 37 | 1 | 38961.3671 | 1941 | 1 |  | 2327 | 2467 | 2.2589 | 0.06105 | 118.4982 | 0.06105 | 0.022589 | 0.0006105 | 1.185 | 0.0006105 | 0.021978 | 1.1844 | 7448.8709 | 24.2466 | 46316.2116
38961.3676 | 101 | 1 | 38961.3676 | 2188 | 1 |  | 2369 | 2509 | 6.1661 | 0.06105 | 133.5775 | 0.06105 | 0.061661 | 0.0006105 | 1.3358 | 0.0006105 | 0.06105 | 1.3352 | 2561.122 | 10.2142 | 21402.3374
38961.3681 | 458 | 1 | 38961.3681 | 1901 | 1 |  | 2411 | 2551 | 27.9609 | 0.06105 | 116.0562 | 0.06105 | 0.27961 | 0.0006105 | 1.1606 | 0.0006105 | 0.279 | 1.16 | 430.9455 | 26.8654 | 41344.1716
38961.3686 | 65 | 1 | 38961.3686 | 2097 | 1 |  | 2453 | 2593 | 3.9683 | 0.06105 | 128.022 | 0.06105 | 0.039683 | 0.0006105 | 1.2802 | 0.0006105 | 0.039072 | 1.2796 | 4092.548 | 14.9992 | 30590.5309
38961.3691 | 2002 | 0 | 38961.3691 | 2299 | 0 |  | 2495 | 2635 | 122.2222 | 0 | 140.3541 | 0 | 1.2222 | 0 | 1.4035 | 0 | 1.2222 | 1.4035 | 20.4486 | 4.8882 | 19.2263
38961.3695 | 1979 | 0 | 38961.3696 | 2227 | 0 |  | 2537 | 2677 | 120.8181 | 0 | 135.9585 | 0 | 1.2082 | 0 | 1.3596 | 0 | 1.2082 | 1.3596 | 21.8484 | 8.2793 | 20.6402
38961.37 | 1836 | 0 | 38961.37 | 2067 | 0 |  | 2579 | 2719 | 112.0879 | 0 | 126.1905 | 0 | 1.1209 | 0 | 1.2619 | 0 | 1.1209 | 1.2619 | 31.3388 | 16.6609 | 30.2179
38961.3705 | 1752 | 0 | 38961.3705 | 2395 | 0 |  | 2621 | 2761 | 106.9597 | 0 | 146.2149 | 0 | 1.0696 | 0 | 1.4621 | 0 | 1.0696 | 1.4621 | 37.6358 | 0.68392 | 36.5662
38961.371 | 2256 | 0 | 38961.371 | 2136 | 0 |  | 2663 | 2803 | 137.7289 | 0 | 130.4029 | 0 | 1.3773 | 0 | 1.304 | 0 | 1.3773 | 1.304 | 6.8874 | 12.8923 | 5.5101
38961.3715 | 1777 | 0 | 38961.3715 | 2292 | 0 |  | 2705 | 2845 | 108.486 | 0 | 139.9267 | 0 | 1.0849 | 0 | 1.3993 | 0 | 1.0849 | 1.3993 | 35.6995 | 5.2086 | 34.6146
38961.372 | 2095 | 0 | 38961.372 | 2271 | 0 |  | 2747 | 2887 | 127.8999 | 0 | 138.6447 | 0 | 1.279 | 0 | 1.3864 | 0 | 1.279 | 1.3864 | 15.1017 | 6.1814 | 13.8227
38961.3725 | 1961 | 0 | 38961.3725 | 2146 | 0 |  | 2789 | 2929 | 119.7192 | 0 | 131.0134 | 0 | 1.1972 | 0 | 1.3101 | 0 | 1.1972 | 1.3101 | 22.9669 | 12.3663 | 21.7697
38961.3729 | 2138 | 0 | 38961.373 | 1987 | 0 |  | 2831 | 2971 | 130.525 | 0 | 121.3065 | 0 | 1.3053 | 0 | 1.2131 | 0 | 1.3053 | 1.2131 | 12.7867 | 21.3578 | 11.4815
38961.3734 | 1809 | 0 | 38961.3734 | 2374 | 0 |  | 2873 | 3013 | 110.4396 | 0 | 144.9328 | 0 | 1.1044 | 0 | 1.4493 | 0 | 1.1044 | 1.4493 | 33.2991 | 1.5746 | 32.1947
38961.3739 | 2297 | 0 | 38961.3739 | 2103 | 0 |  | 2915 | 3055 | 140.232 | 0 | 128.3883 | 0 | 1.4023 | 0 | 1.2839 | 0 | 1.4023 | 1.2839 | 4.9795 | 14.6638 | 3.5772
38961.3744 | 1851 | 0 | 38961.3744 | 2381 | 0 |  | 2957 | 3097 | 113.0037 | 0 | 145.3602 | 0 | 1.13 | 0 | 1.4536 | 0 | 1.13 | 1.4536 | 30.2744 | 1.2759 | 29.1444
38961.3749 | 1818 | 0 | 38961.3749 | 2033 | 1 |  | 2999 | 3139 | 110.989 | 0 | 124.1148 | 0.06105 | 1.1099 | 0 | 1.2411 | 0.0006105 | 1.1099 | 1.2405 | 32.6392 | 18.6703 | 31.5293
38961.3754 | 1825 | 0 | 38961.3754 | 2367 | 0 |  | 3041 | 3181 | 111.4164 | 0 | 144.5055 | 0 | 1.1142 | 0 | 1.4451 | 0 | 1.1142 | 1.4451 | 32.1304 | 1.8749 | 31.0162
38961.3759 | 2179 | 0 | 38961.3759 | 2293 | 0 |  | 3083 | 3223 | 133.0281 | 0 | 139.9878 | 0 | 1.3303 | 0 | 1.3999 | 0 | 1.3303 | 1.3999 | 10.6645 | 5.1627 | 9.3342
38961.3763 | 1927 | 0 | 38961.3764 | 1882 | 0 |  | 3125 | 3265 | 117.6435 | 0 | 114.8962 | 0 | 1.1764 | 0 | 1.149 | 0 | 1.1764 | 1.149 | 25.1365 | 28.1286 | 23.96
38961.3768 | 2229 | 0 | 38961.3769 | 2158 | 0 |  | 3167 | 3307 | 136.0806 | 0 | 131.746 | 0 | 1.3608 | 0 | 1.3175 | 0 | 1.3608 | 1.3175 | 8.1821 | 11.7414 | 6.8213
38961.3773 | 1912 | 0 | 38961.3773 | 1953 | 0 |  | 3209 | 3349 | 116.7277 | 0 | 119.2308 | 0 | 1.1673 | 0 | 1.1923 | 0 | 1.1673 | 1.1923 | 26.1182 | 23.4706 | 24.9509
38961.3778 | 2205 | 0 | 38961.3778 | 2138 | 0 |  | 3251 | 3391 | 134.6154 | 0 | 130.525 | 0 | 1.3462 | 0 | 1.3053 | 0 | 1.3462 | 1.3053 | 9.3596 | 12.7867 | 8.0135
38961.3783 | 1928 | 0 | 38961.3783 | 2305 | 0 |  | 3293 | 3433 | 117.7045 | 0 | 140.7204 | 0 | 1.177 | 0 | 1.4072 | 0 | 1.177 | 1.4072 | 25.0716 | 4.6152 | 23.8945
38961.3788 | 2263 | 0 | 38961.3788 | 2200 | 0 |  | 3335 | 3475 | 138.1563 | 0 | 134.3101 | 0 | 1.3816 | 0 | 1.3431 | 0 | 1.3816 | 1.3431 | 6.5568 | 9.6082 | 5.1752
38961.3793 | 1865 | 0 | 38961.3793 | 2025 | 0 |  | 3376.5 | 3516.5 | 113.8584 | 0 | 123.6264 | 0 | 1.1386 | 0 | 1.2363 | 0 | 1.1386 | 1.2363 | 29.2965 | 19.0805 | 28.1579
38961.3797 | 2334 | 0 | 38961.3798 | 2215 | 0 |  | 3419 | 3559 | 142.4908 | 0 | 135.2259 | 0 | 1.4249 | 0 | 1.3523 | 0 | 1.4249 | 1.3523 | 3.3153 | 8.8659 | 1.8904
38961.3802 | 2353 | 0 | 38961.3803 | 1975 | 0 |  | 3461 | 3601 | 143.6508 | 0 | 120.5739 | 0 | 1.4365 | 0 | 1.2057 | 0 | 1.4365 | 1.2057 | 2.4811 | 22.0952 | 1.0446
38961.3807 | 1856 | 0 | 38961.3807 | 2387 | 0 |  | 3503 | 3643 | 113.3089 | 0 | 145.7265 | 0 | 1.1331 | 0 | 1.4573 | 0 | 1.1331 | 1.4573 | 29.9235 | 1.0214 | 28.7904

## B3-C5
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 146.6044 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38961.3389 | 1 | 0 | 38961.3389 | 1 | 0 |  | -111.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3394 | 1 | 0 | 38961.3394 | 1 | 0 |  | -69.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3399 | 1 | 0 | 38961.3399 | 1 | 0 |  | -27.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3403 | 1 | 0 | 38961.3404 | 1 | 0 |  | 14.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3408 | 1 | 0 | 38961.3408 | 1 | 0 |  | 56.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3413 | 1 | 0 | 38961.3413 | 1 | 0 |  | 98.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3418 | 1 | 0 | 38961.3418 | 1 | 0 |  | 140.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3423 | 1 | 0 | 38961.3423 | 1 | 0 |  | 182.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3428 | 1 | 0 | 38961.3428 | 1 | 0 |  | 224.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3433 | 1 | 0 | 38961.3433 | 1 | 0 |  | 266.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3438 | 1 | 0 | 38961.3438 | 1 | 0 |  | 308.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3442 | 1 | 0 | 38961.3442 | 1 | 0 |  | 350.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3447 | 1 | 0 | 38961.3447 | 1 | 0 |  | 392.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3452 | 1 | 0 | 38961.3452 | 1 | 0 |  | 434.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3457 | 1 | 0 | 38961.3457 | 1 | 0 |  | 476.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3462 | 1 | 0 | 38961.3462 | 1 | 0 |  | 518.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3467 | 1 | 0 | 38961.3467 | 1 | 0 |  | 560.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3472 | 1 | 0 | 38961.3472 | 1 | 0 |  | 602.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3476 | 1 | 0 | 38961.3477 | 1 | 0 |  | 644.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3481 | 1 | 0 | 38961.3481 | 1 | 0 |  | 686.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3486 | 1 | 1 | 38961.3486 | 1 | 0 |  | 728.5 | 868.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 576182414.44 | 240038 | 239838.0833
38961.3491 | 1 | 0 | 38961.3491 | 1 | 0 |  | 770.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3496 | 1 | 0 | 38961.3496 | 1 | 0 |  | 812.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3501 | 1 | 0 | 38961.3501 | 1 | 0 |  | 854.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3506 | 1 | 0 | 38961.3506 | 1 | 0 |  | 896.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.351 | 1 | 0 | 38961.3511 | 1 | 0 |  | 938.5 | 1078.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3515 | 1 | 0 | 38961.3515 | 1 | 0 |  | 980.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.352 | 1 | 0 | 38961.352 | 1 | 0 |  | 1022.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3525 | 1 | 0 | 38961.3525 | 1 | 0 |  | 1064.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.353 | 1 | 0 | 38961.353 | 1 | 0 |  | 1106.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3535 | 1 | 0 | 38961.3535 | 1 | 0 |  | 1148.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.354 | 1 | 0 | 38961.354 | 1 | 0 |  | 1190.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3544 | 1 | 0 | 38961.3545 | 1 | 0 |  | 1232.5 | 1372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3549 | 1 | 0 | 38961.3549 | 1 | 0 |  | 1274.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3554 | 1 | 0 | 38961.3554 | 1 | 0 |  | 1316.5 | 1456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3559 | 1 | 0 | 38961.3559 | 1 | 0 |  | 1358.5 | 1498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3564 | 1 | 0 | 38961.3564 | 1 | 0 |  | 1400.5 | 1540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3569 | 1 | 0 | 38961.3569 | 1 | 0 |  | 1442.5 | 1582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3574 | 1 | 0 | 38961.3574 | 1 | 0 |  | 1484.5 | 1624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3578 | 1 | 0 | 38961.3579 | 1438 | 0 |  | 1526.5 | 1666.5 | 0.06105 | 0 | 87.79 | 0 | 0.0006105 | 0 | 0.8779 | 0 | 0.0006105 | 0.8779 | 240038 | 66.9944 | 240037.9994
38961.3583 | 1 | 0 | 38961.3583 | 2015 | 0 |  | 1568.5 | 1708.5 | 0.06105 | 0 | 123.0159 | 0 | 0.0006105 | 0 | 1.2302 | 0 | 0.0006105 | 1.2302 | 240038 | 19.1752 | 240037.9994
38961.3588 | 2 | 0 | 38961.3588 | 2331 | 0 |  | 1610.5 | 1750.5 | 0.1221 | 0 | 142.3077 | 0 | 0.001221 | 0 | 1.4231 | 0 | 0.001221 | 1.4231 | 119969 | 3.0193 | 119968.9988
38961.3593 | 2 | 0 | 38961.3593 | 2301 | 0 |  | 1652.5 | 1792.5 | 0.1221 | 0 | 140.4762 | 0 | 0.001221 | 0 | 1.4048 | 0 | 0.001221 | 1.4048 | 119969 | 4.3625 | 119968.9988
38961.3598 | 2 | 0 | 38961.3598 | 1939 | 0 |  | 1694.5 | 1834.5 | 0.1221 | 0 | 118.3761 | 0 | 0.001221 | 0 | 1.1838 | 0 | 0.001221 | 1.1838 | 119969 | 23.8463 | 119968.9988
38961.3603 | 2 | 0 | 38961.3603 | 2378 | 0 |  | 1736.5 | 1876.5 | 0.1221 | 0 | 145.177 | 0 | 0.001221 | 0 | 1.4518 | 0 | 0.001221 | 1.4518 | 119969 | 0.98318 | 119968.9988
38961.3608 | 2 | 0 | 38961.3608 | 2108 | 0 |  | 1778.5 | 1918.5 | 0.1221 | 0 | 128.6935 | 0 | 0.001221 | 0 | 1.2869 | 0 | 0.001221 | 1.2869 | 119969 | 13.9175 | 119968.9988
38961.3613 | 2 | 0 | 38961.3613 | 2044 | 0 |  | 1820.5 | 1960.5 | 0.1221 | 0 | 124.7863 | 0 | 0.001221 | 0 | 1.2479 | 0 | 0.001221 | 1.2479 | 119969 | 17.4843 | 119968.9988
38961.3617 | 2 | 0 | 38961.3617 | 1881 | 0 |  | 1862.5 | 2002.5 | 0.1221 | 0 | 114.8352 | 0 | 0.001221 | 0 | 1.1484 | 0 | 0.001221 | 1.1484 | 119969 | 27.6651 | 119968.9988
38961.3622 | 2 | 0 | 38961.3622 | 2333 | 0 |  | 1904.5 | 2044.5 | 0.1221 | 0 | 142.4298 | 0 | 0.001221 | 0 | 1.4243 | 0 | 0.001221 | 1.4243 | 119969 | 2.931 | 119968.9988
38961.3627 | 1 | 0 | 38961.3627 | 2126 | 0 |  | 1946.5 | 2086.5 | 0.06105 | 0 | 129.7924 | 0 | 0.0006105 | 0 | 1.2979 | 0 | 0.0006105 | 1.2979 | 240038 | 12.953 | 240037.9994
38961.3632 | 2 | 0 | 38961.3632 | 2257 | 0 |  | 1988 | 2128 | 0.1221 | 0 | 137.79 | 0 | 0.001221 | 0 | 1.3779 | 0 | 0.001221 | 1.3779 | 119969 | 6.397 | 119968.9988
38961.3637 | 2 | 0 | 38961.3637 | 2359 | 0 |  | 2030.5 | 2170.5 | 0.1221 | 0 | 144.0171 | 0 | 0.001221 | 0 | 1.4402 | 0 | 0.001221 | 1.4402 | 119969 | 1.7965 | 119968.9988
38961.3642 | 2 | 0 | 38961.3642 | 1844 | 0 |  | 2072 | 2212 | 0.1221 | 0 | 112.5763 | 0 | 0.001221 | 0 | 1.1258 | 0 | 0.001221 | 1.1258 | 119969 | 30.2267 | 119968.9988
38961.3647 | 2 | 0 | 38961.3647 | 2282 | 0 |  | 2114.5 | 2254.5 | 0.1221 | 0 | 139.3162 | 0 | 0.001221 | 0 | 1.3932 | 0 | 0.001221 | 1.3932 | 119969 | 5.2314 | 119968.9988
38961.3651 | 2 | 0 | 38961.3652 | 2346 | 0 |  | 2156 | 2296 | 0.1221 | 0 | 143.2234 | 0 | 0.001221 | 0 | 1.4322 | 0 | 0.001221 | 1.4322 | 119969 | 2.3606 | 119968.9988
38961.3656 | 2 | 2 | 38961.3656 | 2337 | 0 |  | 2198.5 | 2338.5 | 0.1221 | 0.1221 | 142.674 | 0 | 0.001221 | 0.001221 | 1.4267 | 0 | 0 | 1.4267 | 3304.9226 | 2.7548 | 3213.6381
38961.3661 | 5 | 2 | 38961.3661 | 2385 | 1 |  | 2240 | 2380 | 0.30525 | 0.1221 | 145.6044 | 0.06105 | 0.0030525 | 0.001221 | 1.456 | 0.0006105 | 0.0018315 | 1.4554 | 831.7836 | 0.7015 | 833.9842
38961.3666 | 28 | 1 | 38961.3666 | 1853 | 1 |  | 2282 | 2422 | 1.7094 | 0.06105 | 113.1258 | 0.06105 | 0.017094 | 0.0006105 | 1.1313 | 0.0006105 | 0.016484 | 1.1306 | 10046.9894 | 29.6103 | 54198.5494
38961.3671 | 33 | 2 | 38961.3671 | 2356 | 1 |  | 2324 | 2464 | 2.0147 | 0.1221 | 143.8339 | 0.06105 | 0.020147 | 0.001221 | 1.4383 | 0.0006105 | 0.018926 | 1.4377 | 3253.646 | 4.7857 | 5403.734
38961.3676 | 72 | 2 | 38961.3676 | 2172 | 1 |  | 2366 | 2506 | 4.3956 | 0.1221 | 132.6007 | 0.06105 | 0.043956 | 0.001221 | 1.326 | 0.0006105 | 0.042735 | 1.3254 | 4561.0707 | 10.5657 | 11120.308
38961.3681 | 188 | 2 | 38961.3681 | 1873 | 1 |  | 2408.5 | 2548.5 | 11.4774 | 0.1221 | 114.3468 | 0.06105 | 0.11477 | 0.001221 | 1.1435 | 0.0006105 | 0.11355 | 1.1429 | 1237.1161 | 28.2266 | 24339.6528
38961.3685 | 63 | 2 | 38961.3686 | 2368 | 1 |  | 2450 | 2590 | 3.8462 | 0.1221 | 144.5665 | 0.06105 | 0.038462 | 0.001221 | 1.4457 | 0.0006105 | 0.037241 | 1.4451 | 2893.1924 | 10.089 | 10705.7885
38961.369 | 1913 | 1 | 38961.369 | 1897 | 1 |  | 2492.5 | 2632.5 | 116.7888 | 0.06105 | 115.812 | 0.06105 | 1.1679 | 0.0006105 | 1.1581 | 0.0006105 | 1.1673 | 1.1575 | 25.5931 | 26.6573 | 10257.7728
38961.3695 | 2149 | 0 | 38961.3695 | 1916 | 0 |  | 2534 | 2674 | 131.1966 | 0 | 116.9719 | 0 | 1.312 | 0 | 1.1697 | 0 | 1.312 | 1.1697 | 11.7441 | 25.333 | 10.4321
38961.37 | 2179 | 1 | 38961.37 | 2186 | 0 |  | 2576 | 2716 | 133.0281 | 0.06105 | 133.4554 | 0 | 1.3303 | 0.0006105 | 1.3346 | 0 | 1.3297 | 1.3346 | 10.2581 | 9.8527 | 1985.5593
38961.3705 | 1761 | 0 | 38961.3705 | 2039 | 0 |  | 2618 | 2758 | 107.5092 | 0 | 124.4811 | 0 | 1.0751 | 0 | 1.2448 | 0 | 1.0751 | 1.2448 | 36.3646 | 17.7724 | 35.2895
38961.371 | 2061 | 0 | 38961.371 | 2071 | 0 |  | 2660 | 2800 | 125.8242 | 0 | 126.4347 | 0 | 1.2582 | 0 | 1.2643 | 0 | 1.2582 | 1.2643 | 16.5153 | 15.9527 | 15.257
38961.3714 | 2150 | 0 | 38961.3715 | 1965 | 0 |  | 2702 | 2842 | 131.2576 | 0 | 119.9634 | 0 | 1.3126 | 0 | 1.1996 | 0 | 1.3126 | 1.1996 | 11.6921 | 22.2076 | 10.3795
38961.3719 | 2179 | 0 | 38961.372 | 1876 | 0 |  | 2744 | 2884 | 133.0281 | 0 | 114.5299 | 0 | 1.3303 | 0 | 1.1453 | 0 | 1.3303 | 1.1453 | 10.2056 | 28.0053 | 8.8753
38961.3724 | 2038 | 0 | 38961.3724 | 2058 | 0 |  | 2786 | 2926 | 124.42 | 0 | 125.641 | 0 | 1.2442 | 0 | 1.2564 | 0 | 1.2442 | 1.2564 | 17.8302 | 16.6851 | 16.586
38961.3729 | 2070 | 0 | 38961.3729 | 2360 | 0 |  | 2828 | 2968 | 126.3736 | 0 | 144.0781 | 0 | 1.2637 | 0 | 1.4408 | 0 | 1.2637 | 1.4408 | 16.0087 | 1.7534 | 14.745
38961.3734 | 2186 | 0 | 38961.3734 | 1934 | 0 |  | 2870 | 3010 | 133.4554 | 0 | 118.0708 | 0 | 1.3346 | 0 | 1.1807 | 0 | 1.3346 | 1.1807 | 9.8527 | 24.1665 | 8.5181
38961.3739 | 2313 | 0 | 38961.3739 | 2140 | 0 |  | 2912 | 3052 | 141.2088 | 0 | 130.6471 | 0 | 1.4121 | 0 | 1.3065 | 0 | 1.4121 | 1.3065 | 3.821 | 12.214 | 2.4089
38961.3744 | 2103 | 0 | 38961.3744 | 2327 | 0 |  | 2954 | 3094 | 128.3883 | 0 | 142.0635 | 0 | 1.2839 | 0 | 1.4206 | 0 | 1.2839 | 1.4206 | 14.1883 | 3.1964 | 12.9044
38961.3748 | 2025 | 0 | 38961.3749 | 2000 | 0 |  | 2996 | 3136 | 123.6264 | 0 | 122.1001 | 0 | 1.2363 | 0 | 1.221 | 0 | 1.2363 | 1.221 | 18.5867 | 20.069 | 17.3504
38961.3753 | 2114 | 0 | 38961.3754 | 2278 | 0 |  | 3038 | 3178 | 129.0598 | 0 | 139.072 | 0 | 1.2906 | 0 | 1.3907 | 0 | 1.2906 | 1.3907 | 13.5941 | 5.4162 | 12.3035
38961.3758 | 2162 | 0 | 38961.3758 | 2320 | 0 |  | 3080 | 3220 | 131.9902 | 0 | 141.6361 | 0 | 1.3199 | 0 | 1.4164 | 0 | 1.3199 | 1.4164 | 11.0722 | 3.5078 | 9.7523
38961.3763 | 1978 | 0 | 38961.3763 | 2006 | 0 |  | 3122 | 3262 | 120.757 | 0 | 122.4664 | 0 | 1.2076 | 0 | 1.2247 | 0 | 1.2076 | 1.2247 | 21.4044 | 19.7099 | 20.1969
38961.3768 | 2099 | 0 | 38961.3768 | 1973 | 0 |  | 3164 | 3304 | 128.1441 | 0 | 120.4518 | 0 | 1.2814 | 0 | 1.2045 | 0 | 1.2814 | 1.2045 | 14.4059 | 21.7121 | 13.1245
38961.3773 | 2089 | 0 | 38961.3773 | 2320 | 0 |  | 3206 | 3346 | 127.5336 | 0 | 141.6361 | 0 | 1.2753 | 0 | 1.4164 | 0 | 1.2753 | 1.4164 | 14.9536 | 3.5078 | 13.6782
38961.3778 | 2208 | 0 | 38961.3778 | 2231 | 0 |  | 3248 | 3388 | 134.7985 | 0 | 136.2027 | 0 | 1.348 | 0 | 1.362 | 0 | 1.348 | 1.362 | 8.7582 | 7.6369 | 7.4102
38961.3783 | 1965 | 0 | 38961.3783 | 2010 | 0 |  | 3290 | 3430 | 119.9634 | 0 | 122.7106 | 0 | 1.1996 | 0 | 1.2271 | 0 | 1.1996 | 1.2271 | 22.2076 | 19.4716 | 21.008
38961.3787 | 2276 | 0 | 38961.3788 | 2071 | 0 |  | 3332 | 3472 | 138.9499 | 0 | 126.4347 | 0 | 1.3895 | 0 | 1.2643 | 0 | 1.3895 | 1.2643 | 5.5088 | 15.9527 | 4.1193
38961.3792 | 1922 | 0 | 38961.3792 | 1921 | 0 |  | 3374 | 3514 | 117.3382 | 0 | 117.2772 | 0 | 1.1734 | 0 | 1.1728 | 0 | 1.1734 | 1.1728 | 24.9417 | 25.0068 | 23.7683
38961.3797 | 2043 | 0 | 38961.3797 | 1884 | 0 |  | 3416 | 3556 | 124.7253 | 0 | 115.0183 | 0 | 1.2473 | 0 | 1.1502 | 0 | 1.2473 | 1.1502 | 17.5419 | 27.4618 | 16.2946
38961.3802 | 1936 | 0 | 38961.3802 | 2186 | 0 |  | 3458 | 3598 | 118.1929 | 0 | 133.4554 | 0 | 1.1819 | 0 | 1.3346 | 0 | 1.1819 | 1.3346 | 24.0382 | 9.8527 | 22.8563
38961.3807 | 2123 | 0 | 38961.3807 | 2079 | 0 |  | 3500 | 3640 | 129.6093 | 0 | 126.9231 | 0 | 1.2961 | 0 | 1.2692 | 0 | 1.2961 | 1.2692 | 13.1126 | 15.5065 | 11.8165

## B3-B4
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 145.6886 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38961.3389 | 1 | 0 | 38961.3389 | 1 | 1 |  | -114.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0.06105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 238538 | #DIV/0! | 238537.9994
38961.3393 | 1 | 0 | 38961.3394 | 1 | 0 |  | -72.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3398 | 1 | 0 | 38961.3398 | 1 | 0 |  | -30.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3403 | 1 | 0 | 38961.3403 | 1 | 0 |  | 11.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3408 | 1 | 0 | 38961.3408 | 1 | 0 |  | 53.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3413 | 1 | 0 | 38961.3413 | 1 | 0 |  | 95.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3418 | 1 | 0 | 38961.3418 | 1 | 0 |  | 137.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3423 | 1 | 0 | 38961.3423 | 1 | 0 |  | 179.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3427 | 1 | 0 | 38961.3428 | 1 | 0 |  | 221.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3432 | 1 | 0 | 38961.3432 | 1 | 0 |  | 263.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3437 | 1 | 0 | 38961.3437 | 1 | 0 |  | 305.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3442 | 1 | 0 | 38961.3442 | 1 | 0 |  | 347.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3447 | 1 | 0 | 38961.3447 | 1 | 0 |  | 389.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3452 | 1 | 0 | 38961.3452 | 1 | 0 |  | 431.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3457 | 1 | 0 | 38961.3457 | 1 | 0 |  | 473.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3461 | 1 | 0 | 38961.3462 | 1 | 0 |  | 515.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3466 | 1 | 0 | 38961.3466 | 1 | 0 |  | 557.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3471 | 1 | 0 | 38961.3471 | 1 | 0 |  | 599.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3476 | 1 | 0 | 38961.3476 | 1 | 0 |  | 641.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3481 | 1 | 0 | 38961.3481 | 1 | 0 |  | 683.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3486 | 1 | 0 | 38961.3486 | 1 | 0 |  | 725.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3491 | 1 | 0 | 38961.3491 | 1 | 0 |  | 767.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3495 | 1 | 0 | 38961.3496 | 1 | 0 |  | 809.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.35 | 1 | 0 | 38961.35 | 1 | 0 |  | 851.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3505 | 1 | 0 | 38961.3505 | 1 | 0 |  | 893.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.351 | 1 | 0 | 38961.351 | 1 | 0 |  | 935.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3515 | 1 | 0 | 38961.3515 | 1 | 0 |  | 977.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.352 | 1 | 0 | 38961.352 | 1 | 0 |  | 1019.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3525 | 1 | 0 | 38961.3525 | 1 | 0 |  | 1061.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.353 | 1 | 0 | 38961.353 | 1 | 0 |  | 1103.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3534 | 1 | 0 | 38961.3534 | 1 | 0 |  | 1145.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3539 | 1 | 0 | 38961.3539 | 1 | 0 |  | 1187.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3544 | 1 | 0 | 38961.3544 | 1 | 0 |  | 1229.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3549 | 1 | 0 | 38961.3549 | 1 | 0 |  | 1271.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3554 | 1 | 0 | 38961.3554 | 1 | 0 |  | 1313.5 | 1453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3559 | 1 | 0 | 38961.3559 | 1 | 0 |  | 1355.5 | 1495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3564 | 1 | 0 | 38961.3564 | 1 | 0 |  | 1397.5 | 1537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3568 | 1 | 0 | 38961.3569 | 1 | 0 |  | 1439.5 | 1579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3573 | 1 | 0 | 38961.3573 | 1 | 0 |  | 1481.5 | 1621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3578 | 1 | 0 | 38961.3578 | 1 | 0 |  | 1523.5 | 1663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3583 | 2 | 0 | 38961.3583 | 1 | 0 |  | 1565.5 | 1705.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119219 | 238538 | 119218.9988
38961.3588 | 3 | 0 | 38961.3588 | 2 | 0 |  | 1607.5 | 1747.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 79446 | 119219 | 79445.9982
38961.3593 | 3 | 0 | 38961.3593 | 2 | 0 |  | 1649.5 | 1789.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 79446 | 119219 | 79445.9982
38961.3598 | 3 | 0 | 38961.3598 | 2 | 0 |  | 1691.5 | 1831.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 79446 | 119219 | 79445.9982
38961.3602 | 2 | 0 | 38961.3603 | 2 | 0 |  | 1733.5 | 1873.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3607 | 2 | 0 | 38961.3607 | 2 | 0 |  | 1775.5 | 1915.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3612 | 3 | 0 | 38961.3612 | 2 | 0 |  | 1817.5 | 1957.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 79446 | 119219 | 79445.9982
38961.3617 | 3 | 0 | 38961.3617 | 2 | 0 |  | 1859.5 | 1999.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 79446 | 119219 | 79445.9982
38961.3622 | 4 | 1 | 38961.3622 | 3 | 0 |  | 1901.5 | 2041.5 | 0.2442 | 0.06105 | 0.18315 | 0 | 0.002442 | 0.0006105 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 79446 | 79446 | 237838.6286
38961.3627 | 5 | 1 | 38961.3627 | 4 | 2 |  | 1943.5 | 2083.5 | 0.30525 | 0.06105 | 0.2442 | 0.1221 | 0.0030525 | 0.0006105 | 0.002442 | 0.001221 | 0.002442 | 0.001221 | 59546.9764 | 119319.3786 | 237838.6705
38961.3632 | 6 | 1 | 38961.3632 | 5 | 2 |  | 1985.5 | 2125.5 | 0.3663 | 0.06105 | 0.30525 | 0.1221 | 0.003663 | 0.0006105 | 0.0030525 | 0.001221 | 0.0030525 | 0.0018315 | 47619.5812 | 79490.619 | 237639.0477
38961.3636 | 8 | 2 | 38961.3637 | 6 | 2 |  | 2027.5 | 2167.5 | 0.4884 | 0.1221 | 0.3663 | 0.1221 | 0.004884 | 0.001221 | 0.003663 | 0.001221 | 0.003663 | 0.002442 | 39661.8546 | 59584.6158 | 118619.9219
38961.3641 | 6 | 2 | 38961.3641 | 6 | 2 |  | 2069.5 | 2209.5 | 0.3663 | 0.1221 | 0.3663 | 0.1221 | 0.003663 | 0.001221 | 0.003663 | 0.001221 | 0.002442 | 0.002442 | 59559.5 | 59559.5 | 118719.6705
38961.3646 | 14 | 6 | 38961.3646 | 8 | 3 |  | 2111.5 | 2251.5 | 0.8547 | 0.3663 | 0.4884 | 0.18315 | 0.008547 | 0.003663 | 0.004884 | 0.0018315 | 0.004884 | 0.0030525 | 29701.4858 | 47663.8859 | 39357.0945
38961.3651 | 27 | 9 | 38961.3651 | 220 | 195 |  | 2153.5 | 2293.5 | 1.6484 | 0.54945 | 13.431 | 11.9048 | 0.016484 | 0.0054945 | 0.13431 | 0.11905 | 0.010989 | 0.015263 | 13179.21 | 9210.6439 | 25834.8443
38961.3656 | 1028 | 977 | 38961.3656 | 1141 | 1091 |  | 2195.5 | 2335.5 | 62.7595 | 59.6459 | 69.6581 | 66.6056 | 0.62759 | 0.59646 | 0.69658 | 0.66606 | 0.031136 | 0.030525 | 4267.4309 | 5096.8585 | 38.2847
38961.3661 | 939 | 999 | 38961.3661 | 986 | 918 |  | 2237.5 | 2377.5 | 57.326 | 60.989 | 60.1954 | 56.044 | 0.57326 | 0.60989 | 0.60195 | 0.56044 | 0.03663 | 0.041514 | 6897.1089 | 2560.5743 | 43.1959
38961.3666 | 972 | 943 | 38961.3666 | 1144 | 1041 |  | 2279.5 | 2419.5 | 59.3407 | 57.5702 | 69.8413 | 63.5531 | 0.59341 | 0.5757 | 0.69841 | 0.63553 | 0.017705 | 0.062882 | 1269.2875 | 1143.9869 | 45.969
38961.367 | 1080 | 980 | 38961.3671 | 1224 | 1117 |  | 2321.5 | 2461.5 | 65.9341 | 59.8291 | 74.7253 | 68.1929 | 0.65934 | 0.59829 | 0.74725 | 0.68193 | 0.06105 | 0.065324 | 3725.1712 | 1509.2943 | 31.2346
38961.3675 | 1078 | 966 | 38961.3675 | 1013 | 907 |  | 2363.5 | 2503.5 | 65.812 | 58.9744 | 61.8437 | 55.3724 | 0.65812 | 0.58974 | 0.61844 | 0.55372 | 0.068376 | 0.064713 | 1790.5389 | 2481.4952 | 34.0701
38961.368 | 1260 | 1106 | 38961.368 | 1100 | 954 |  | 2405.5 | 2545.5 | 76.9231 | 67.5214 | 67.1551 | 58.2418 | 0.76923 | 0.67521 | 0.67155 | 0.58242 | 0.094017 | 0.089133 | 1075.2556 | 2245.8963 | 1.7641
38961.3685 | 981 | 936 | 38961.3685 | 1035 | 925 |  | 2447.5 | 2587.5 | 59.8901 | 57.1429 | 63.1868 | 56.4713 | 0.5989 | 0.57143 | 0.63187 | 0.56471 | 0.027473 | 0.067155 | 2451.848 | 7597.8867 | 49.496
38961.369 | 1806 | 301 | 38961.369 | 1690 | 270 |  | 2489.5 | 2629.5 | 110.2564 | 18.3761 | 103.1746 | 16.4835 | 1.1026 | 0.18376 | 1.0317 | 0.16484 | 0.9188 | 0.86691 | 52.0268 | 77.2865 | 40.4629
38961.3695 | 1891 | 175 | 38961.3695 | 1847 | 164 |  | 2531.5 | 2671.5 | 115.4457 | 10.6838 | 112.7595 | 10.0122 | 1.1545 | 0.10684 | 1.1276 | 0.10012 | 1.0476 | 1.0275 | 37.7938 | 43.1827 | 55.2136
38961.37 | 2172 | 160 | 38961.37 | 2048 | 141 |  | 2573.5 | 2713.5 | 132.6007 | 9.768 | 125.0305 | 8.6081 | 1.326 | 0.09768 | 1.2503 | 0.086081 | 1.2283 | 1.1642 | 13.3037 | 39.9438 | 9.701
38961.3705 | 1828 | 104 | 38961.3705 | 1871 | 101 |  | 2615.5 | 2755.5 | 111.5995 | 6.3492 | 114.2247 | 6.1661 | 1.116 | 0.063492 | 1.1422 | 0.061661 | 1.0525 | 1.0806 | 39.3612 | 34.0544 | 110.9885
38961.3709 | 1998 | 91 | 38961.3709 | 1865 | 85 |  | 2657.5 | 2797.5 | 121.978 | 5.5556 | 113.8584 | 5.1893 | 1.2198 | 0.055556 | 1.1386 | 0.051893 | 1.1642 | 1.0867 | 23.4003 | 36.801 | 87.9104
38961.3714 | 1972 | 84 | 38961.3714 | 2282 | 84 |  | 2699.5 | 2839.5 | 120.3907 | 5.1282 | 139.3162 | 5.1282 | 1.2039 | 0.051282 | 1.3932 | 0.051282 | 1.1526 | 1.3419 | 291.0324 | 4.8121 | 18.0573
38961.3719 | 2039 | 70 | 38961.3719 | 1897 | 60 |  | 2741.5 | 2881.5 | 124.4811 | 4.2735 | 115.812 | 3.663 | 1.2448 | 0.042735 | 1.1581 | 0.03663 | 1.2021 | 1.1215 | 19.8564 | 31.885 | 95.8005
38961.3724 | 2237 | 69 | 38961.3724 | 1856 | 52 |  | 2783.5 | 2923.5 | 136.569 | 4.2125 | 113.3089 | 3.1746 | 1.3657 | 0.042125 | 1.1331 | 0.031746 | 1.3236 | 1.1013 | 7.3767 | 48.2567 | 37.9177
38961.3729 | 2200 | 60 | 38961.3729 | 1903 | 48 |  | 2825.5 | 2965.5 | 134.3101 | 3.663 | 116.1783 | 2.9304 | 1.3431 | 0.03663 | 1.1618 | 0.029304 | 1.3065 | 1.1325 | 9.4474 | 35.8877 | 55.6278
38961.3734 | 2270 | 57 | 38961.3734 | 1903 | 46 |  | 2867.5 | 3007.5 | 138.5836 | 3.4799 | 116.1783 | 2.8083 | 1.3858 | 0.034799 | 1.1618 | 0.028083 | 1.351 | 1.1337 | 5.5644 | 46.9156 | 33.2671
38961.3739 | 1986 | 48 | 38961.3739 | 1842 | 38 |  | 2909.5 | 3049.5 | 121.2454 | 2.9304 | 112.4542 | 2.3199 | 1.2125 | 0.029304 | 1.1245 | 0.023199 | 1.1832 | 1.1013 | 22.3184 | 33.3212 | 183.481
38961.3743 | 2102 | 43 | 38961.3744 | 2307 | 42 |  | 2951.5 | 3091.5 | 128.3272 | 2.6252 | 140.8425 | 2.5641 | 1.2833 | 0.026252 | 1.4084 | 0.025641 | 1.257 | 1.3828 | 31.4437 | 3.7243 | 20.1555
38961.3748 | 2259 | 47 | 38961.3748 | 2148 | 43 |  | 2993.5 | 3133.5 | 137.9121 | 2.8694 | 131.1355 | 2.6252 | 1.3791 | 0.028694 | 1.3114 | 0.026252 | 1.3504 | 1.2851 | 6.6168 | 16.3819 | 24.073
38961.3753 | 1816 | 36 | 38961.3753 | 2313 | 41 |  | 3035.5 | 3175.5 | 110.8669 | 2.1978 | 141.2088 | 2.5031 | 1.1087 | 0.021978 | 1.4121 | 0.025031 | 1.0867 | 1.3871 | 82.7014 | 3.3018 | 47.445
38961.3758 | 2167 | 40 | 38961.3758 | 2215 | 41 |  | 3077.5 | 3217.5 | 132.2955 | 2.442 | 135.2259 | 2.5031 | 1.323 | 0.02442 | 1.3523 | 0.025031 | 1.2985 | 1.3272 | 12.9546 | 9.2263 | 37.8805
38961.3763 | 2280 | 45 | 38961.3763 | 1867 | 33 |  | 3119.5 | 3259.5 | 139.1941 | 2.7473 | 113.9805 | 2.0147 | 1.3919 | 0.027473 | 1.1398 | 0.020147 | 1.3645 | 1.1197 | 4.9863 | 44.3086 | 41.8803
38961.3768 | 2306 | 43 | 38961.3768 | 2328 | 42 |  | 3161.5 | 3301.5 | 140.7814 | 2.6252 | 142.1245 | 2.5641 | 1.4078 | 0.026252 | 1.4212 | 0.025641 | 1.3816 | 1.3956 | 8.5362 | 3.2542 | 2.7397
38961.3772 | 2326 | 48 | 38961.3773 | 2367 | 44 |  | 3203 | 3343 | 142.0024 | 2.9304 | 144.5055 | 2.6862 | 1.42 | 0.029304 | 1.4451 | 0.026862 | 1.3907 | 1.4182 | 1.3983 | 2.3528 | 0.59287
38961.3777 | 2187 | 43 | 38961.3778 | 1904 | 34 |  | 3245.5 | 3385.5 | 133.5165 | 2.6252 | 116.2393 | 2.0757 | 1.3352 | 0.026252 | 1.1624 | 0.020757 | 1.3089 | 1.1416 | 9.9301 | 31.5775 | 87.2788
38961.3782 | 1890 | 34 | 38961.3782 | 2370 | 38 |  | 3287 | 3427 | 115.3846 | 2.0757 | 144.6886 | 2.3199 | 1.1538 | 0.020757 | 1.4469 | 0.023199 | 1.1331 | 1.4237 | 13.9889 | 2.009 | 26.7831
38961.3787 | 1918 | 32 | 38961.3787 | 2043 | 31 |  | 3329.5 | 3469.5 | 117.094 | 1.9536 | 124.7253 | 1.8926 | 1.1709 | 0.019536 | 1.2473 | 0.018926 | 1.1514 | 1.2283 | 27.406 | 18.0832 | 208.8347
38961.3792 | 2043 | 33 | 38961.3792 | 2310 | 33 |  | 3371 | 3511 | 124.7253 | 2.0147 | 141.0256 | 2.0147 | 1.2473 | 0.020147 | 1.4103 | 0.020147 | 1.2271 | 1.3901 | 32.0713 | 3.5132 | 31.9215
38961.3797 | 2192 | 32 | 38961.3797 | 2201 | 30 |  | 3413.5 | 3553.5 | 133.8217 | 1.9536 | 134.3712 | 1.8315 | 1.3382 | 0.019536 | 1.3437 | 0.018315 | 1.3187 | 1.3254 | 10.5981 | 9.8192 | 45.3713
38961.3802 | 1950 | 29 | 38961.3802 | 2158 | 28 |  | 3455 | 3595 | 119.0476 | 1.7705 | 131.746 | 1.7094 | 1.1905 | 0.017705 | 1.3175 | 0.017094 | 1.1728 | 1.3004 | 26.2234 | 11.2879 | 142.4845
38961.3807 | 1911 | 27 | 38961.3807 | 1969 | 25 |  | 3497.5 | 3637.5 | 116.6667 | 1.6484 | 120.2076 | 1.5263 | 1.1667 | 0.016484 | 1.2021 | 0.015263 | 1.1502 | 1.1868 | 26.9452 | 22.5462 | 305.5317

## A2-C6
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 147.1538 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38961.3388 | 1 | 0 | 38961.3388 | 1 | 0 |  | -117 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3393 | 1 | 0 | 38961.3393 | 1 | 0 |  | -75 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3398 | 1 | 0 | 38961.3398 | 1 | 0 |  | -33 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3403 | 1 | 0 | 38961.3403 | 1 | 0 |  | 9 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3408 | 1 | 0 | 38961.3408 | 1 | 0 |  | 51 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3412 | 1 | 1 | 38961.3413 | 1 | 0 |  | 93 | 233 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 580511198.44 | 240938 | 240738.083
38961.3417 | 1 | 0 | 38961.3418 | 1 | 0 |  | 135 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3422 | 1 | 0 | 38961.3422 | 1 | 0 |  | 177 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3427 | 1 | 0 | 38961.3427 | 1 | 0 |  | 219 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3432 | 1 | 0 | 38961.3432 | 2 | 0 |  | 261 | 401 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 240938 | 120419 | 240937.9994
38961.3437 | 1 | 0 | 38961.3437 | 1 | 0 |  | 303 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3442 | 1 | 0 | 38961.3442 | 1 | 0 |  | 345 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3447 | 1 | 1 | 38961.3447 | 1 | 0 |  | 387 | 527 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 580511198.44 | 240938 | 240738.083
38961.3451 | 1 | 0 | 38961.3452 | 1 | 0 |  | 428.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3456 | 1 | 0 | 38961.3456 | 1 | 0 |  | 471 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3461 | 1 | 0 | 38961.3461 | 1 | 0 |  | 512.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3466 | 1 | 0 | 38961.3466 | 1 | 0 |  | 554.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3471 | 1 | 0 | 38961.3471 | 1 | 0 |  | 597 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3476 | 1 | 0 | 38961.3476 | 1 | 0 |  | 639 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3481 | 1 | 0 | 38961.3481 | 1 | 0 |  | 680.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3485 | 1 | 0 | 38961.3486 | 1 | 0 |  | 723 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.349 | 1 | 0 | 38961.349 | 1 | 0 |  | 764.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3495 | 1 | 0 | 38961.3495 | 1 | 0 |  | 807 | 947 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.35 | 1 | 0 | 38961.35 | 1 | 0 |  | 849 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3505 | 1 | 0 | 38961.3505 | 1 | 0 |  | 890.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.351 | 1 | 0 | 38961.351 | 1 | 0 |  | 933 | 1073 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3515 | 1 | 0 | 38961.3515 | 1 | 0 |  | 974.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3519 | 1 | 0 | 38961.352 | 1 | 0 |  | 1016.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3524 | 1 | 0 | 38961.3524 | 1 | 0 |  | 1058.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3529 | 1 | 0 | 38961.3529 | 1 | 0 |  | 1100.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3534 | 1 | 0 | 38961.3534 | 1 | 0 |  | 1142.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3539 | 1 | 0 | 38961.3539 | 1 | 0 |  | 1184.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3544 | 1 | 0 | 38961.3544 | 1 | 0 |  | 1226.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3549 | 1 | 0 | 38961.3549 | 1 | 0 |  | 1268.5 | 1408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3553 | 1 | 0 | 38961.3554 | 1 | 0 |  | 1310.5 | 1450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3558 | 1 | 0 | 38961.3558 | 1 | 0 |  | 1352.5 | 1492.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3563 | 1 | 0 | 38961.3563 | 1 | 0 |  | 1394.5 | 1534.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3568 | 1 | 0 | 38961.3568 | 1 | 0 |  | 1436.5 | 1576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3573 | 1 | 0 | 38961.3573 | 1 | 0 |  | 1478.5 | 1618.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38961.3578 | 2 | 0 | 38961.3578 | 86 | 0 |  | 1520.5 | 1660.5 | 0.1221 | 0 | 5.2503 | 0 | 0.001221 | 0 | 0.052503 | 0 | 0.001221 | 0.052503 | 120419 | 2702.7674 | 120418.9988
38961.3583 | 2 | 0 | 38961.3583 | 1181 | 0 |  | 1562.5 | 1702.5 | 0.1221 | 0 | 72.1001 | 0 | 0.001221 | 0 | 0.721 | 0 | 0.001221 | 0.721 | 120419 | 104.0965 | 120418.9988
38961.3587 | 2 | 0 | 38961.3588 | 2205 | 0 |  | 1604.5 | 1744.5 | 0.1221 | 0 | 134.6154 | 0 | 0.001221 | 0 | 1.3462 | 0 | 0.001221 | 1.3462 | 120419 | 9.3143 | 120418.9988
38961.3592 | 3 | 0 | 38961.3592 | 2205 | 0 |  | 1646.5 | 1786.5 | 0.18315 | 0 | 134.6154 | 0 | 0.0018315 | 0 | 1.3462 | 0 | 0.0018315 | 1.3462 | 80246 | 9.3143 | 80245.9982
38961.3597 | 2 | 0 | 38961.3597 | 1912 | 0 |  | 1688.5 | 1828.5 | 0.1221 | 0 | 116.7277 | 0 | 0.001221 | 0 | 1.1673 | 0 | 0.001221 | 1.1673 | 120419 | 26.0659 | 120418.9988
38961.3602 | 2 | 0 | 38961.3602 | 1882 | 0 |  | 1730.5 | 1870.5 | 0.1221 | 0 | 114.8962 | 0 | 0.001221 | 0 | 1.149 | 0 | 0.001221 | 1.149 | 120419 | 28.0755 | 120418.9988
38961.3607 | 2 | 0 | 38961.3607 | 2008 | 0 |  | 1772.5 | 1912.5 | 0.1221 | 0 | 122.5885 | 0 | 0.001221 | 0 | 1.2259 | 0 | 0.001221 | 1.2259 | 120419 | 20.0388 | 120418.9988
38961.3612 | 2 | 0 | 38961.3612 | 1916 | 0 |  | 1814.5 | 1954.5 | 0.1221 | 0 | 116.9719 | 0 | 0.001221 | 0 | 1.1697 | 0 | 0.001221 | 1.1697 | 120419 | 25.8027 | 120418.9988
38961.3617 | 2 | 0 | 38961.3617 | 2218 | 0 |  | 1856.5 | 1996.5 | 0.1221 | 0 | 135.409 | 0 | 0.001221 | 0 | 1.3541 | 0 | 0.001221 | 1.3541 | 120419 | 8.6736 | 120418.9988
38961.3622 | 3 | 0 | 38961.3622 | 2315 | 0 |  | 1898.5 | 2038.5 | 0.18315 | 0 | 141.3309 | 0 | 0.0018315 | 0 | 1.4133 | 0 | 0.0018315 | 1.4133 | 80246 | 4.1201 | 80245.9982
38961.3626 | 2 | 0 | 38961.3627 | 2115 | 0 |  | 1940.5 | 2080.5 | 0.1221 | 0 | 129.1209 | 0 | 0.001221 | 0 | 1.2912 | 0 | 0.001221 | 1.2912 | 120419 | 13.966 | 120418.9988
38961.3631 | 2 | 0 | 38961.3631 | 2120 | 0 |  | 1982.5 | 2122.5 | 0.1221 | 0 | 129.4261 | 0 | 0.001221 | 0 | 1.2943 | 0 | 0.001221 | 1.2943 | 120419 | 13.6972 | 120418.9988
38961.3636 | 2 | 0 | 38961.3636 | 2019 | 0 |  | 2024.5 | 2164.5 | 0.1221 | 0 | 123.2601 | 0 | 0.001221 | 0 | 1.2326 | 0 | 0.001221 | 1.2326 | 120419 | 19.3848 | 120418.9988
38961.3641 | 2 | 0 | 38961.3641 | 2167 | 0 |  | 2066.5 | 2206.5 | 0.1221 | 0 | 132.2955 | 0 | 0.001221 | 0 | 1.323 | 0 | 0.001221 | 1.323 | 120419 | 11.2312 | 120418.9988
38961.3646 | 2 | 0 | 38961.3646 | 1992 | 0 |  | 2108.5 | 2248.5 | 0.1221 | 0 | 121.6117 | 0 | 0.001221 | 0 | 1.2161 | 0 | 0.001221 | 1.2161 | 120419 | 21.003 | 120418.9988
38961.3651 | 2 | 0 | 38961.3651 | 2231 | 0 |  | 2150.5 | 2290.5 | 0.1221 | 0 | 136.2027 | 0 | 0.001221 | 0 | 1.362 | 0 | 0.001221 | 1.362 | 120419 | 8.0403 | 120418.9988
38961.3656 | 3 | 0 | 38961.3656 | 2271 | 0 |  | 2192.5 | 2332.5 | 0.18315 | 0 | 138.6447 | 0 | 0.0018315 | 0 | 1.3864 | 0 | 0.0018315 | 1.3864 | 80246 | 6.1374 | 80245.9982
38961.366 | 2 | 0 | 38961.3661 | 2022 | 0 |  | 2234.5 | 2374.5 | 0.1221 | 0 | 123.4432 | 0 | 0.001221 | 0 | 1.2344 | 0 | 0.001221 | 1.2344 | 120419 | 19.2077 | 120418.9988
38961.3665 | 10 | 0 | 38961.3665 | 2346 | 0 |  | 2276.5 | 2416.5 | 0.6105 | 0 | 143.2234 | 0 | 0.006105 | 0 | 1.4322 | 0 | 0.006105 | 1.4322 | 24003.8 | 2.7442 | 24003.7939
38961.367 | 36 | 1 | 38961.367 | 1890 | 0 |  | 2318.5 | 2458.5 | 2.1978 | 0.06105 | 115.3846 | 0 | 0.021978 | 0.0006105 | 1.1538 | 0 | 0.021368 | 1.1538 | 7569.4245 | 27.5333 | 51239.2023
38961.3675 | 51 | 1 | 38961.3675 | 2004 | 1 |  | 2360.5 | 2500.5 | 3.1136 | 0.06105 | 122.3443 | 0.06105 | 0.031136 | 0.0006105 | 1.2234 | 0.0006105 | 0.030525 | 1.2228 | 5234.7884 | 20.2888 | 39778.1198
38961.368 | 86 | 1 | 38961.368 | 2180 | 1 |  | 2402.5 | 2542.5 | 5.2503 | 0.06105 | 133.0891 | 0.06105 | 0.052503 | 0.0006105 | 1.3309 | 0.0006105 | 0.051893 | 1.3303 | 3076.9432 | 10.5729 | 22215.9852
38961.3685 | 60 | 1 | 38961.3685 | 2098 | 0 |  | 2444.5 | 2584.5 | 3.663 | 0.06105 | 128.083 | 0 | 0.03663 | 0.0006105 | 1.2808 | 0 | 0.03602 | 1.2808 | 4495.4251 | 14.8894 | 30447.4533
38961.369 | 1398 | 1 | 38961.369 | 2159 | 1 |  | 2486.5 | 2626.5 | 85.348 | 0.06105 | 131.8071 | 0.06105 | 0.85348 | 0.0006105 | 1.3181 | 0.0006105 | 0.85287 | 1.3175 | 72.9159 | 11.6562 | 10558.1313
38961.3694 | 1856 | 0 | 38961.3695 | 2215 | 0 |  | 2528.5 | 2668.5 | 113.3089 | 0 | 135.2259 | 0 | 1.1331 | 0 | 1.3523 | 0 | 1.1331 | 1.3523 | 29.8696 | 8.8208 | 28.7365
38961.3699 | 1709 | 0 | 38961.3699 | 2058 | 0 |  | 2570.5 | 2710.5 | 104.3346 | 0 | 125.641 | 0 | 1.0433 | 0 | 1.2564 | 0 | 1.0433 | 1.2564 | 41.0404 | 17.1224 | 39.997
38961.3704 | 1968 | 0 | 38961.3704 | 2286 | 0 |  | 2612.5 | 2752.5 | 120.1465 | 0 | 139.5604 | 0 | 1.2015 | 0 | 1.3956 | 0 | 1.2015 | 1.3956 | 22.4787 | 5.4409 | 21.2772
38961.3709 | 2108 | 0 | 38961.3709 | 2371 | 0 |  | 2654.5 | 2794.5 | 128.6935 | 0 | 144.7497 | 0 | 1.2869 | 0 | 1.4475 | 0 | 1.2869 | 1.4475 | 14.3444 | 1.6609 | 13.0575
38961.3714 | 2193 | 0 | 38961.3714 | 2364 | 0 |  | 2696.5 | 2836.5 | 133.8828 | 0 | 144.3223 | 0 | 1.3388 | 0 | 1.4432 | 0 | 1.3388 | 1.4432 | 9.9124 | 1.9619 | 8.5736
38961.3719 | 1950 | 0 | 38961.3719 | 1938 | 0 |  | 2738.5 | 2878.5 | 119.0476 | 0 | 118.315 | 0 | 1.1905 | 0 | 1.1832 | 0 | 1.1905 | 1.1832 | 23.6092 | 24.3746 | 22.4188
38961.3724 | 2208 | 0 | 38961.3724 | 2107 | 0 |  | 2780.5 | 2920.5 | 134.7985 | 0 | 128.6325 | 0 | 1.348 | 0 | 1.2863 | 0 | 1.348 | 1.2863 | 9.1658 | 14.3987 | 7.8178
38961.3728 | 1780 | 0 | 38961.3729 | 2058 | 0 |  | 2822.5 | 2962.5 | 108.6691 | 0 | 125.641 | 0 | 1.0867 | 0 | 1.2564 | 0 | 1.0867 | 1.2564 | 35.4146 | 17.1224 | 34.3279
38961.3733 | 1829 | 0 | 38961.3733 | 2176 | 0 |  | 2864.5 | 3004.5 | 111.6606 | 0 | 132.8449 | 0 | 1.1166 | 0 | 1.3284 | 0 | 1.1166 | 1.3284 | 31.7868 | 10.7711 | 30.6702
38961.3738 | 1967 | 0 | 38961.3738 | 1918 | 0 |  | 2906.5 | 3046.5 | 120.0855 | 0 | 117.094 | 0 | 1.2009 | 0 | 1.1709 | 0 | 1.2009 | 1.1709 | 22.5409 | 25.6715 | 21.3401
38961.3743 | 1853 | 0 | 38961.3743 | 2034 | 0 |  | 2948.5 | 3088.5 | 113.1258 | 0 | 124.1758 | 0 | 1.1313 | 0 | 1.2418 | 0 | 1.1313 | 1.2418 | 30.0799 | 18.5044 | 28.9486
38961.3748 | 1872 | 0 | 38961.3748 | 2394 | 0 |  | 2990.5 | 3130.5 | 114.2857 | 0 | 146.1538 | 0 | 1.1429 | 0 | 1.4615 | 0 | 1.1429 | 1.4615 | 28.7596 | 0.68421 | 27.6168
38961.3753 | 2054 | 0 | 38961.3753 | 1860 | 0 |  | 3032.5 | 3172.5 | 125.3968 | 0 | 113.5531 | 0 | 1.254 | 0 | 1.1355 | 0 | 1.254 | 1.1355 | 17.3505 | 29.5903 | 16.0966
38961.3758 | 1960 | 0 | 38961.3758 | 1860 | 0 |  | 3074.5 | 3214.5 | 119.6581 | 0 | 113.5531 | 0 | 1.1966 | 0 | 1.1355 | 0 | 1.1966 | 1.1355 | 22.9786 | 29.5903 | 21.782
38961.3763 | 2257 | 0 | 38961.3763 | 2346 | 0 |  | 3116.5 | 3256.5 | 137.79 | 0 | 143.2234 | 0 | 1.3779 | 0 | 1.4322 | 0 | 1.3779 | 1.4322 | 6.7957 | 2.7442 | 5.4178
38961.3767 | 1915 | 0 | 38961.3767 | 1872 | 0 |  | 3158.5 | 3298.5 | 116.9109 | 0 | 114.2857 | 0 | 1.1691 | 0 | 1.1429 | 0 | 1.1691 | 1.1429 | 25.8684 | 28.7596 | 24.6993
38961.3772 | 2202 | 0 | 38961.3772 | 1963 | 0 |  | 3200.5 | 3340.5 | 134.4322 | 0 | 119.8413 | 0 | 1.3443 | 0 | 1.1984 | 0 | 1.3443 | 1.1984 | 9.4632 | 22.7906 | 8.1189
38961.3777 | 2013 | 0 | 38961.3777 | 2019 | 0 |  | 3242.5 | 3382.5 | 122.8938 | 0 | 123.2601 | 0 | 1.2289 | 0 | 1.2326 | 0 | 1.2289 | 1.2326 | 19.7407 | 19.3848 | 18.5117
38961.3782 | 1769 | 0 | 38961.3782 | 2009 | 0 |  | 3284.5 | 3424.5 | 107.9976 | 0 | 122.6496 | 0 | 1.08 | 0 | 1.2265 | 0 | 1.08 | 1.2265 | 36.2566 | 19.9791 | 35.1767
38961.3787 | 2166 | 0 | 38961.3787 | 2388 | 0 |  | 3326.5 | 3466.5 | 132.2344 | 0 | 145.7875 | 0 | 1.3223 | 0 | 1.4579 | 0 | 1.3223 | 1.4579 | 11.2825 | 0.93719 | 9.9602
38961.3792 | 2270 | 0 | 38961.3792 | 1994 | 0 |  | 3368.5 | 3508.5 | 138.5836 | 0 | 121.7338 | 0 | 1.3858 | 0 | 1.2173 | 0 | 1.3858 | 1.2173 | 6.1841 | 20.8816 | 4.7983
38961.3797 | 1937 | 0 | 38961.3797 | 2353 | 0 |  | 3410.5 | 3550.5 | 118.254 | 0 | 143.6508 | 0 | 1.1825 | 0 | 1.4365 | 0 | 1.1825 | 1.4365 | 24.4388 | 2.4386 | 23.2563
38961.3801 | 1829 | 0 | 38961.3802 | 2205 | 0 |  | 3452.5 | 3592.5 | 111.6606 | 0 | 134.6154 | 0 | 1.1166 | 0 | 1.3462 | 0 | 1.1166 | 1.3462 | 31.7868 | 9.3143 | 30.6702
38961.3806 | 2269 | 0 | 38961.3806 | 2280 | 0 |  | 3494.5 | 3634.5 | 138.5226 | 0 | 139.1941 | 0 | 1.3852 | 0 | 1.3919 | 0 | 1.3852 | 1.3919 | 6.2309 | 5.7184 | 4.8457

## A2-C5
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 146.6044 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38961.3388 | 1 | 0 | 38961.3388 | 1 | 0 |  | -120 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3393 | 1 | 0 | 38961.3393 | 1 | 0 |  | -78 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3398 | 1 | 0 | 38961.3398 | 1 | 0 |  | -36 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3402 | 1 | 0 | 38961.3403 | 1 | 0 |  | 6 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3407 | 1 | 0 | 38961.3408 | 1 | 0 |  | 48 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3412 | 1 | 0 | 38961.3412 | 1 | 0 |  | 90 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3417 | 1 | 0 | 38961.3417 | 1 | 0 |  | 132 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3422 | 2 | 0 | 38961.3422 | 1 | 0 |  | 174 | 314 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119969 | 240038 | 119968.9988
38961.3427 | 1 | 0 | 38961.3427 | 1 | 0 |  | 216 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3432 | 1 | 0 | 38961.3432 | 1 | 0 |  | 258 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3436 | 1 | 0 | 38961.3437 | 1 | 0 |  | 300 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3441 | 1 | 0 | 38961.3442 | 1 | 0 |  | 342 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3446 | 1 | 0 | 38961.3446 | 1 | 0 |  | 384 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3451 | 1 | 0 | 38961.3451 | 1 | 0 |  | 426 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3456 | 1 | 0 | 38961.3456 | 1 | 0 |  | 468 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3461 | 1 | 0 | 38961.3461 | 1 | 0 |  | 510 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3466 | 1 | 0 | 38961.3466 | 1 | 0 |  | 552 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.347 | 1 | 0 | 38961.3471 | 1 | 0 |  | 594 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3475 | 1 | 0 | 38961.3476 | 1 | 0 |  | 636 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.348 | 1 | 0 | 38961.348 | 1 | 0 |  | 678 | 818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3485 | 1 | 0 | 38961.3485 | 1 | 0 |  | 720 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.349 | 1 | 0 | 38961.349 | 1 | 0 |  | 762 | 902 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3495 | 1 | 0 | 38961.3495 | 1 | 0 |  | 804 | 944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.35 | 1 | 0 | 38961.35 | 1 | 0 |  | 846 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3505 | 1 | 0 | 38961.3505 | 1 | 0 |  | 888 | 1028 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3509 | 1 | 0 | 38961.351 | 1 | 0 |  | 930 | 1070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3514 | 1 | 0 | 38961.3514 | 1 | 0 |  | 972 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3519 | 1 | 0 | 38961.3519 | 1 | 0 |  | 1014 | 1154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3524 | 1 | 0 | 38961.3524 | 1 | 0 |  | 1056 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3529 | 1 | 0 | 38961.3529 | 1 | 0 |  | 1098 | 1238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3534 | 1 | 0 | 38961.3534 | 1 | 0 |  | 1140 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3539 | 1 | 0 | 38961.3539 | 1 | 0 |  | 1182 | 1322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3543 | 1 | 0 | 38961.3544 | 1 | 0 |  | 1224 | 1364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3548 | 1 | 0 | 38961.3548 | 1 | 0 |  | 1266 | 1406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3553 | 1 | 0 | 38961.3553 | 1 | 0 |  | 1308 | 1448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3558 | 1 | 0 | 38961.3558 | 1 | 0 |  | 1350 | 1490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3563 | 1 | 0 | 38961.3563 | 1 | 0 |  | 1392 | 1532 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3568 | 1 | 0 | 38961.3568 | 1 | 0 |  | 1434 | 1574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3573 | 1 | 0 | 38961.3573 | 1 | 0 |  | 1476 | 1616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38961.3577 | 1 | 0 | 38961.3578 | 1518 | 0 |  | 1518 | 1658 | 0.06105 | 0 | 92.674 | 0 | 0.0006105 | 0 | 0.92674 | 0 | 0.0006105 | 0.92674 | 240038 | 58.1937 | 240037.9994
38961.3582 | 1 | 0 | 38961.3583 | 2184 | 0 |  | 1560 | 1700 | 0.06105 | 0 | 133.3333 | 0 | 0.0006105 | 0 | 1.3333 | 0 | 0.0006105 | 1.3333 | 240038 | 9.9533 | 240037.9994
38961.3587 | 2 | 0 | 38961.3587 | 1940 | 0 |  | 1602 | 1742 | 0.1221 | 0 | 118.4371 | 0 | 0.001221 | 0 | 1.1844 | 0 | 0.001221 | 1.1844 | 119969 | 23.7825 | 119968.9988
38961.3592 | 2 | 0 | 38961.3592 | 2272 | 0 |  | 1644 | 1784 | 0.1221 | 0 | 138.7057 | 0 | 0.001221 | 0 | 1.3871 | 0 | 0.001221 | 1.3871 | 119969 | 5.6945 | 119968.9988
38961.3597 | 2 | 0 | 38961.3597 | 2233 | 0 |  | 1686 | 1826 | 0.1221 | 0 | 136.3248 | 0 | 0.001221 | 0 | 1.3632 | 0 | 0.001221 | 1.3632 | 119969 | 7.5405 | 119968.9988
38961.3602 | 2 | 0 | 38961.3602 | 2214 | 0 |  | 1728 | 1868 | 0.1221 | 0 | 135.1648 | 0 | 0.001221 | 0 | 1.3516 | 0 | 0.001221 | 1.3516 | 119969 | 8.4634 | 119968.9988
38961.3607 | 2 | 0 | 38961.3607 | 2007 | 0 |  | 1770 | 1910 | 0.1221 | 0 | 122.5275 | 0 | 0.001221 | 0 | 1.2253 | 0 | 0.001221 | 1.2253 | 119969 | 19.6502 | 119968.9988
38961.3611 | 1 | 0 | 38961.3612 | 2281 | 0 |  | 1812 | 1952 | 0.06105 | 0 | 139.2552 | 0 | 0.0006105 | 0 | 1.3926 | 0 | 0.0006105 | 1.3926 | 240038 | 5.2775 | 240037.9994
38961.3616 | 2 | 0 | 38961.3617 | 1872 | 0 |  | 1854 | 1994 | 0.1221 | 0 | 114.2857 | 0 | 0.001221 | 0 | 1.1429 | 0 | 0.001221 | 1.1429 | 119969 | 28.2788 | 119968.9988
38961.3621 | 2 | 0 | 38961.3621 | 2230 | 0 |  | 1896 | 2036 | 0.1221 | 0 | 136.1416 | 0 | 0.001221 | 0 | 1.3614 | 0 | 0.001221 | 1.3614 | 119969 | 7.6852 | 119968.9988
38961.3626 | 2 | 0 | 38961.3626 | 2271 | 0 |  | 1937.5 | 2077.5 | 0.1221 | 0 | 138.6447 | 0 | 0.001221 | 0 | 1.3864 | 0 | 0.001221 | 1.3864 | 119969 | 5.7411 | 119968.9988
38961.3631 | 2 | 0 | 38961.3631 | 2295 | 0 |  | 1979.5 | 2119.5 | 0.1221 | 0 | 140.1099 | 0 | 0.001221 | 0 | 1.4011 | 0 | 0.001221 | 1.4011 | 119969 | 4.6353 | 119968.9988
38961.3636 | 1 | 0 | 38961.3636 | 2235 | 0 |  | 2021.5 | 2161.5 | 0.06105 | 0 | 136.4469 | 0 | 0.0006105 | 0 | 1.3645 | 0 | 0.0006105 | 1.3645 | 240038 | 7.4443 | 240037.9994
38961.3641 | 2 | 0 | 38961.3641 | 2378 | 0 |  | 2064 | 2204 | 0.1221 | 0 | 145.177 | 0 | 0.001221 | 0 | 1.4518 | 0 | 0.001221 | 1.4518 | 119969 | 0.98318 | 119968.9988
38961.3645 | 2 | 0 | 38961.3646 | 2133 | 0 |  | 2106 | 2246 | 0.1221 | 0 | 130.2198 | 0 | 0.001221 | 0 | 1.3022 | 0 | 0.001221 | 1.3022 | 119969 | 12.5823 | 119968.9988
38961.365 | 2 | 0 | 38961.365 | 2385 | 0 |  | 2147.5 | 2287.5 | 0.1221 | 0 | 145.6044 | 0 | 0.001221 | 0 | 1.456 | 0 | 0.001221 | 1.456 | 119969 | 0.68679 | 119968.9988
38961.3655 | 2 | 0 | 38961.3655 | 2188 | 0 |  | 2189.5 | 2329.5 | 0.1221 | 0 | 133.5775 | 0 | 0.001221 | 0 | 1.3358 | 0 | 0.001221 | 1.3358 | 119969 | 9.7523 | 119968.9988
38961.366 | 2 | 0 | 38961.366 | 2230 | 0 |  | 2231.5 | 2371.5 | 0.1221 | 0 | 136.1416 | 0 | 0.001221 | 0 | 1.3614 | 0 | 0.001221 | 1.3614 | 119969 | 7.6852 | 119968.9988
38961.3665 | 2 | 0 | 38961.3665 | 2225 | 0 |  | 2273.5 | 2413.5 | 0.1221 | 0 | 135.8364 | 0 | 0.001221 | 0 | 1.3584 | 0 | 0.001221 | 1.3584 | 119969 | 7.9272 | 119968.9988
38961.367 | 31 | 2 | 38961.367 | 1926 | 1 |  | 2315.5 | 2455.5 | 1.8926 | 0.1221 | 117.5824 | 0.06105 | 0.018926 | 0.001221 | 1.1758 | 0.0006105 | 0.017705 | 1.1752 | 11340.8512 | 24.6952 | 23452.2163
38961.3675 | 48 | 2 | 38961.3675 | 2359 | 2 |  | 2357.5 | 2497.5 | 2.9304 | 0.1221 | 144.0171 | 0.1221 | 0.029304 | 0.001221 | 1.4402 | 0.001221 | 0.028083 | 1.4389 | 3607.5791 | 10.3981 | 11073.4837
38961.368 | 257 | 2 | 38961.368 | 2062 | 1 |  | 2399.5 | 2539.5 | 15.6899 | 0.1221 | 125.8852 | 0.06105 | 0.1569 | 0.001221 | 1.2589 | 0.0006105 | 0.15568 | 1.2582 | 882.9878 | 16.4677 | 15145.8359
38961.3684 | 135 | 2 | 38961.3684 | 2326 | 1 |  | 2441.5 | 2581.5 | 8.2418 | 0.1221 | 142.0024 | 0.06105 | 0.082418 | 0.001221 | 1.42 | 0.0006105 | 0.081197 | 1.4194 | 3178.057 | 3.2422 | 3555.5038
38961.3689 | 1702 | 1 | 38961.3689 | 2138 | 0 |  | 2483.5 | 2623.5 | 103.9072 | 0.06105 | 130.525 | 0 | 1.0391 | 0.0006105 | 1.3053 | 0 | 1.0385 | 1.3053 | 41.313 | 12.319 | 7659.7342
38961.3694 | 1994 | 0 | 38961.3694 | 1821 | 0 |  | 2525.5 | 2665.5 | 121.7338 | 0 | 111.1722 | 0 | 1.2173 | 0 | 1.1117 | 0 | 1.2173 | 1.1117 | 20.4303 | 31.8715 | 19.213
38961.3699 | 1988 | 0 | 38961.3699 | 2012 | 0 |  | 2567.5 | 2707.5 | 121.3675 | 0 | 122.8327 | 0 | 1.2137 | 0 | 1.2283 | 0 | 1.2137 | 1.2283 | 20.7938 | 19.3529 | 19.5801
38961.3704 | 1995 | 0 | 38961.3704 | 2350 | 0 |  | 2609.5 | 2749.5 | 121.7949 | 0 | 143.4676 | 0 | 1.2179 | 0 | 1.4347 | 0 | 1.2179 | 1.4347 | 20.3699 | 2.1864 | 19.152
38961.3709 | 2131 | 0 | 38961.3709 | 2055 | 0 |  | 2651.5 | 2791.5 | 130.0977 | 0 | 125.4579 | 0 | 1.301 | 0 | 1.2546 | 0 | 1.301 | 1.2546 | 12.6879 | 16.8555 | 11.387
38961.3714 | 1898 | 0 | 38961.3714 | 2303 | 0 |  | 2693.5 | 2833.5 | 115.873 | 0 | 140.5983 | 0 | 1.1587 | 0 | 1.406 | 0 | 1.1587 | 1.406 | 26.5216 | 4.2718 | 25.3629
38961.3718 | 1747 | 0 | 38961.3719 | 1938 | 0 |  | 2735.5 | 2875.5 | 106.6545 | 0 | 118.315 | 0 | 1.0665 | 0 | 1.1832 | 0 | 1.0665 | 1.1832 | 37.4574 | 23.9102 | 36.3908
38961.3723 | 1946 | 0 | 38961.3723 | 2080 | 0 |  | 2777.5 | 2917.5 | 118.8034 | 0 | 126.9841 | 0 | 1.188 | 0 | 1.2698 | 0 | 1.188 | 1.2698 | 23.4008 | 15.451 | 22.2128
38961.3728 | 1957 | 0 | 38961.3728 | 2288 | 0 |  | 2819.5 | 2959.5 | 119.475 | 0 | 139.6825 | 0 | 1.1947 | 0 | 1.3968 | 0 | 1.1947 | 1.3968 | 22.7072 | 4.9554 | 21.5125
38961.3733 | 2034 | 0 | 38961.3733 | 1999 | 0 |  | 2861.5 | 3001.5 | 124.1758 | 0 | 122.0391 | 0 | 1.2418 | 0 | 1.2204 | 0 | 1.2418 | 1.2204 | 18.0619 | 20.1291 | 16.8202
38961.3738 | 1975 | 0 | 38961.3738 | 2166 | 0 |  | 2903.5 | 3043.5 | 120.5739 | 0 | 132.2344 | 0 | 1.2057 | 0 | 1.3223 | 0 | 1.2057 | 1.3223 | 21.5889 | 10.867 | 20.3831
38961.3743 | 2243 | 0 | 38961.3743 | 2236 | 0 |  | 2945.5 | 3085.5 | 136.9353 | 0 | 136.5079 | 0 | 1.3694 | 0 | 1.3651 | 0 | 1.3694 | 1.3651 | 7.0611 | 7.3962 | 5.6917
38961.3748 | 2170 | 0 | 38961.3748 | 2369 | 0 |  | 2987.5 | 3127.5 | 132.4786 | 0 | 144.6276 | 0 | 1.3248 | 0 | 1.4463 | 0 | 1.3248 | 1.4463 | 10.6627 | 1.3668 | 9.3379
38961.3752 | 2091 | 0 | 38961.3753 | 1843 | 0 |  | 3029.5 | 3169.5 | 127.6557 | 0 | 112.5153 | 0 | 1.2766 | 0 | 1.1252 | 0 | 1.2766 | 1.1252 | 14.8436 | 30.2973 | 13.5671
38961.3757 | 2261 | 0 | 38961.3757 | 1851 | 0 |  | 3071.5 | 3211.5 | 138.0342 | 0 | 113.0037 | 0 | 1.3803 | 0 | 1.13 | 0 | 1.3803 | 1.13 | 6.2088 | 29.7342 | 4.8284
38961.3762 | 1968 | 0 | 38961.3762 | 2168 | 0 |  | 3113.5 | 3253.5 | 120.1465 | 0 | 132.3565 | 0 | 1.2015 | 0 | 1.3236 | 0 | 1.2015 | 1.3236 | 22.0213 | 10.7648 | 20.8199
38961.3767 | 2230 | 0 | 38961.3767 | 1833 | 0 |  | 3155.5 | 3295.5 | 136.1416 | 0 | 111.9048 | 0 | 1.3614 | 0 | 1.119 | 0 | 1.3614 | 1.119 | 7.6852 | 31.0082 | 6.3238
38961.3772 | 1920 | 0 | 38961.3772 | 2085 | 0 |  | 3197.5 | 3337.5 | 117.2161 | 0 | 127.2894 | 0 | 1.1722 | 0 | 1.2729 | 0 | 1.1722 | 1.2729 | 25.0719 | 15.1741 | 23.8997
38961.3777 | 2243 | 0 | 38961.3777 | 2333 | 0 |  | 3239.5 | 3379.5 | 136.9353 | 0 | 142.4298 | 0 | 1.3694 | 0 | 1.4243 | 0 | 1.3694 | 1.4243 | 7.0611 | 2.931 | 5.6917
38961.3782 | 2108 | 0 | 38961.3782 | 2155 | 0 |  | 3281.5 | 3421.5 | 128.6935 | 0 | 131.5629 | 0 | 1.2869 | 0 | 1.3156 | 0 | 1.2869 | 1.3156 | 13.9175 | 11.4329 | 12.6305
38961.3786 | 2153 | 0 | 38961.3787 | 2195 | 0 |  | 3323.5 | 3463.5 | 131.4408 | 0 | 134.0049 | 0 | 1.3144 | 0 | 1.34 | 0 | 1.3144 | 1.34 | 11.5365 | 9.4023 | 10.2221
38961.3791 | 1853 | 0 | 38961.3791 | 1905 | 0 |  | 3365.5 | 3505.5 | 113.1258 | 0 | 116.3004 | 0 | 1.1313 | 0 | 1.163 | 0 | 1.1313 | 1.163 | 29.5942 | 26.0567 | 28.4629
38961.3796 | 2023 | 0 | 38961.3796 | 1843 | 0 |  | 3407.5 | 3547.5 | 123.5043 | 0 | 112.5153 | 0 | 1.235 | 0 | 1.1252 | 0 | 1.235 | 1.1252 | 18.7039 | 30.2973 | 17.4689
38961.3801 | 1859 | 0 | 38961.3801 | 2074 | 0 |  | 3449.5 | 3589.5 | 113.4921 | 0 | 126.6178 | 0 | 1.1349 | 0 | 1.2662 | 0 | 1.1349 | 1.2662 | 29.1759 | 15.785 | 28.041
38961.3806 | 2202 | 0 | 38961.3806 | 2325 | 0 |  | 3491.5 | 3631.5 | 134.4322 | 0 | 141.9414 | 0 | 1.3443 | 0 | 1.4194 | 0 | 1.3443 | 1.4194 | 9.0545 | 3.2852 | 7.7102

## A2-B4
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 138.9731 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38961.3388 | 0 | 0 | 38961.3388 | 1 | 0 |  | -122.5 | 17.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 455176 | 227538 | 455175.9997
38961.3392 | 1 | 0 | 38961.3393 | 1 | 0 |  | -80.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3397 | 1 | 0 | 38961.3397 | 1 | 0 |  | -38.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3402 | 1 | 0 | 38961.3402 | 1 | 0 |  | 3.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3407 | 1 | 0 | 38961.3407 | 1 | 0 |  | 45.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3412 | 1 | 0 | 38961.3412 | 1 | 0 |  | 87.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3417 | 1 | 0 | 38961.3417 | 1 | 0 |  | 129.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3422 | 1 | 0 | 38961.3422 | 1 | 0 |  | 171.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3427 | 1 | 0 | 38961.3427 | 1 | 0 |  | 213.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3431 | 1 | 0 | 38961.3431 | 1 | 0 |  | 255.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3436 | 1 | 0 | 38961.3436 | 1 | 0 |  | 297.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3441 | 1 | 0 | 38961.3441 | 1 | 0 |  | 339.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3446 | 1 | 0 | 38961.3446 | 1 | 0 |  | 381.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3451 | 1 | 0 | 38961.3451 | 1 | 0 |  | 423.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3456 | 1 | 0 | 38961.3456 | 1 | 0 |  | 465.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.346 | 1 | 0 | 38961.3461 | 1 | 0 |  | 507 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3465 | 1 | 0 | 38961.3466 | 1 | 0 |  | 549.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.347 | 1 | 0 | 38961.347 | 2 | 0 |  | 591.5 | 731.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 227538 | 113719 | 227537.9994
38961.3475 | 1 | 0 | 38961.3475 | 1 | 0 |  | 633.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.348 | 1 | 0 | 38961.348 | 1 | 0 |  | 675.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3485 | 1 | 0 | 38961.3485 | 1 | 0 |  | 717.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.349 | 1 | 0 | 38961.349 | 1 | 0 |  | 759 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3495 | 1 | 0 | 38961.3495 | 1 | 0 |  | 801.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3499 | 1 | 0 | 38961.35 | 1 | 0 |  | 843.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3504 | 1 | 0 | 38961.3504 | 1 | 0 |  | 885 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3509 | 1 | 0 | 38961.3509 | 1 | 0 |  | 927.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3514 | 1 | 0 | 38961.3514 | 1 | 0 |  | 969 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3519 | 1 | 0 | 38961.3519 | 1 | 0 |  | 1011 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3524 | 1 | 0 | 38961.3524 | 1 | 0 |  | 1053 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3528 | 1 | 0 | 38961.3529 | 1 | 0 |  | 1095 | 1235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3533 | 1 | 0 | 38961.3534 | 1 | 0 |  | 1137 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3538 | 1 | 0 | 38961.3538 | 1 | 0 |  | 1179 | 1319 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3543 | 1 | 0 | 38961.3543 | 1 | 0 |  | 1221 | 1361 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3548 | 1 | 0 | 38961.3548 | 1 | 0 |  | 1263 | 1403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3553 | 1 | 0 | 38961.3553 | 1 | 0 |  | 1305 | 1445 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3558 | 1 | 0 | 38961.3558 | 1 | 0 |  | 1347 | 1487 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3562 | 1 | 0 | 38961.3563 | 1 | 0 |  | 1389 | 1529 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3567 | 1 | 0 | 38961.3568 | 1 | 0 |  | 1431 | 1571 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3572 | 1 | 0 | 38961.3572 | 1 | 0 |  | 1473 | 1613 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3577 | 1 | 0 | 38961.3577 | 1 | 0 |  | 1515 | 1655 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227538 | 227538 | 227537.9994
38961.3582 | 1 | 0 | 38961.3582 | 2 | 0 |  | 1557 | 1697 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 227538 | 113719 | 227537.9994
38961.3587 | 2 | 0 | 38961.3587 | 2 | 0 |  | 1599 | 1739 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3592 | 2 | 0 | 38961.3592 | 2 | 0 |  | 1641 | 1781 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3597 | 2 | 0 | 38961.3597 | 2 | 0 |  | 1683 | 1823 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3601 | 2 | 0 | 38961.3602 | 2 | 0 |  | 1725 | 1865 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3606 | 2 | 0 | 38961.3606 | 2 | 0 |  | 1767 | 1907 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3611 | 2 | 0 | 38961.3611 | 2 | 0 |  | 1809 | 1949 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3616 | 2 | 0 | 38961.3616 | 1 | 0 |  | 1851 | 1991 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 113719 | 227538 | 113718.9988
38961.3621 | 2 | 0 | 38961.3621 | 2 | 0 |  | 1893 | 2033 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3626 | 2 | 0 | 38961.3626 | 2 | 0 |  | 1935 | 2075 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3631 | 2 | 0 | 38961.3631 | 2 | 0 |  | 1977 | 2117 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3635 | 2 | 0 | 38961.3636 | 2 | 0 |  | 2019 | 2159 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.364 | 2 | 0 | 38961.3641 | 2 | 0 |  | 2061 | 2201 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3645 | 2 | 0 | 38961.3645 | 2 | 0 |  | 2103 | 2243 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.365 | 2 | 0 | 38961.365 | 2 | 0 |  | 2145 | 2285 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3655 | 2 | 0 | 38961.3655 | 2 | 0 |  | 2187 | 2327 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.366 | 2 | 0 | 38961.366 | 2 | 0 |  | 2229 | 2369 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113719 | 113719 | 113718.9988
38961.3665 | 2 | 0 | 38961.3665 | 179 | 151 |  | 2271 | 2411 | 0.1221 | 0 | 10.928 | 9.2186 | 0.001221 | 0 | 0.10928 | 0.092186 | 0.001221 | 0.017094 | 113719 | 8029.9286 | 113718.9988
38961.3669 | 1181 | 1092 | 38961.367 | 1183 | 1087 |  | 2313 | 2453 | 72.1001 | 66.6667 | 72.2222 | 66.3614 | 0.721 | 0.66667 | 0.72222 | 0.66361 | 0.054335 | 0.058608 | 141.7674 | 159.7286 | 0.19035
38961.3674 | 1047 | 1010 | 38961.3675 | 1196 | 1093 |  | 2355 | 2495 | 63.9194 | 61.6606 | 73.0159 | 66.7277 | 0.63919 | 0.61661 | 0.73016 | 0.66728 | 0.022589 | 0.062882 | 350.112 | 321.5137 | 16.5677
38961.3679 | 1094 | 854 | 38961.3679 | 1149 | 842 |  | 2397 | 2537 | 66.7888 | 52.1368 | 70.1465 | 51.4042 | 0.66789 | 0.52137 | 0.70147 | 0.51404 | 0.14652 | 0.18742 | 7314.5352 | 381.5307 | 30.4666
38961.3684 | 946 | 958 | 38961.3684 | 946 | 840 |  | 2439 | 2579 | 57.7534 | 58.486 | 57.7534 | 51.2821 | 0.57753 | 0.58486 | 0.57753 | 0.51282 | 0.007326 | 0.064713 | 1127.7777 | 904.0743 | 34.9993
38961.3689 | 1479 | 480 | 38961.3689 | 1599 | 491 |  | 2481 | 2621 | 90.293 | 29.304 | 97.619 | 29.9756 | 0.90293 | 0.29304 | 0.97619 | 0.29976 | 0.60989 | 0.67643 | 210.1641 | 77.4704 | 28.8634
38961.3694 | 1801 | 163 | 38961.3694 | 1961 | 193 |  | 2523 | 2663 | 109.9512 | 9.9512 | 119.7192 | 11.7827 | 1.0995 | 0.099512 | 1.1972 | 0.11783 | 1 | 1.0794 | 51.866 | 22.5935 | 35.3193
38961.3699 | 1704 | 125 | 38961.3699 | 1816 | 136 |  | 2565 | 2705 | 104.0293 | 7.6313 | 110.8669 | 8.3028 | 1.0403 | 0.076313 | 1.1087 | 0.083028 | 0.96398 | 1.0256 | 47.6868 | 33.0067 | 88.8169
38961.3703 | 2115 | 120 | 38961.3704 | 1977 | 108 |  | 2607 | 2747 | 129.1209 | 7.326 | 120.696 | 6.5934 | 1.2912 | 0.07326 | 1.207 | 0.065934 | 1.2179 | 1.141 | 9.4787 | 41.0333 | 10.0328
38961.3708 | 1786 | 77 | 38961.3709 | 1839 | 87 |  | 2649 | 2789 | 109.0354 | 4.7009 | 112.2711 | 5.3114 | 1.0904 | 0.047009 | 1.1227 | 0.053114 | 1.0433 | 1.0696 | 33.9195 | 29.2462 | 121.4816
38961.3713 | 1887 | 68 | 38961.3713 | 1931 | 73 |  | 2691 | 2831 | 115.2015 | 4.1514 | 117.8877 | 4.4567 | 1.152 | 0.041514 | 1.1789 | 0.044567 | 1.1105 | 1.1343 | 25.8058 | 21.9272 | 84.995
38961.3718 | 2253 | 71 | 38961.3718 | 2153 | 71 |  | 2733 | 2873 | 137.5458 | 4.3346 | 131.4408 | 4.3346 | 1.3755 | 0.043346 | 1.3144 | 0.043346 | 1.3321 | 1.2711 | 1.7764 | 8.2003 | 5.0831
38961.3723 | 2184 | 61 | 38961.3723 | 2049 | 60 |  | 2775 | 2915 | 133.3333 | 3.7241 | 125.0916 | 3.663 | 1.3333 | 0.037241 | 1.2509 | 0.03663 | 1.2961 | 1.2143 | 4.7995 | 30.7739 | 12.1056
38961.3728 | 1882 | 46 | 38961.3728 | 1769 | 48 |  | 2817 | 2957 | 114.8962 | 2.8083 | 107.9976 | 2.9304 | 1.149 | 0.028083 | 1.08 | 0.029304 | 1.1209 | 1.0507 | 23.2164 | 33.507 | 190.076
38961.3733 | 2229 | 49 | 38961.3733 | 2198 | 55 |  | 2859 | 2999 | 136.0806 | 2.9915 | 134.188 | 3.3578 | 1.3608 | 0.029915 | 1.3419 | 0.033578 | 1.3309 | 1.3083 | 1.5466 | 5.5468 | 0.17375
38961.3737 | 2249 | 46 | 38961.3738 | 1833 | 42 |  | 2901 | 3041 | 137.3016 | 2.8083 | 111.9048 | 2.5641 | 1.373 | 0.028083 | 1.119 | 0.025641 | 1.3449 | 1.0934 | 1.1413 | 23.4723 | 7.695
38961.3742 | 2235 | 41 | 38961.3743 | 1805 | 37 |  | 2943 | 3083 | 136.4469 | 2.5031 | 110.1954 | 2.2589 | 1.3645 | 0.025031 | 1.102 | 0.022589 | 1.3394 | 1.0794 | 1.8705 | 224.3495 | 0.64108
38961.3747 | 1881 | 33 | 38961.3747 | 2210 | 45 |  | 2985 | 3125 | 114.8352 | 2.0147 | 134.9206 | 2.7473 | 1.1484 | 0.020147 | 1.3492 | 0.027473 | 1.1282 | 1.3217 | 48.3362 | 3.2038 | 34.0896
38961.3752 | 2218 | 37 | 38961.3752 | 1966 | 37 |  | 3027 | 3167 | 135.409 | 2.2589 | 120.0244 | 2.2589 | 1.3541 | 0.022589 | 1.2002 | 0.022589 | 1.3315 | 1.1777 | 2.7662 | 52.4813 | 19.8881
38961.3757 | 2228 | 36 | 38961.3757 | 1755 | 34 |  | 3069 | 3209 | 136.0195 | 2.1978 | 107.1429 | 2.0757 | 1.3602 | 0.021978 | 1.0714 | 0.020757 | 1.3382 | 1.0507 | 2.2204 | 274.793 | 25.2135
38961.3762 | 1890 | 30 | 38961.3762 | 1965 | 37 |  | 3111 | 3251 | 115.3846 | 1.8315 | 119.9634 | 2.2589 | 1.1538 | 0.018315 | 1.1996 | 0.022589 | 1.1355 | 1.177 | 22.8649 | 17.6301 | 178.0448
38961.3767 | 1777 | 31 | 38961.3767 | 1965 | 36 |  | 3153 | 3293 | 108.486 | 1.8926 | 119.9634 | 2.1978 | 1.0849 | 0.018926 | 1.1996 | 0.021978 | 1.0659 | 1.1777 | 31.9054 | 17.1449 | 221.1303
38961.3772 | 1899 | 34 | 38961.3772 | 1926 | 42 |  | 3194.5 | 3334.5 | 115.9341 | 2.0757 | 117.5824 | 2.5641 | 1.1593 | 0.020757 | 1.1758 | 0.025641 | 1.1386 | 1.1502 | 22.1917 | 20.6746 | 173.0281
38961.3776 | 2136 | 38 | 38961.3777 | 2126 | 41 |  | 3237 | 3377 | 130.4029 | 2.3199 | 129.7924 | 2.5031 | 1.304 | 0.023199 | 1.2979 | 0.025031 | 1.2808 | 1.2729 | 8.2755 | 9.4605 | 23.2856
38961.3781 | 2260 | 28 | 38961.3781 | 2112 | 41 |  | 3278.5 | 3418.5 | 137.9731 | 1.7094 | 128.9377 | 2.5031 | 1.3797 | 0.017094 | 1.2894 | 0.025031 | 1.3626 | 1.2643 | 0.5 | 2.682 | 1.084
38961.3786 | 1866 | 26 | 38961.3786 | 1976 | 33 |  | 3320.5 | 3460.5 | 113.9194 | 1.5873 | 120.6349 | 2.0147 | 1.1392 | 0.015873 | 1.2063 | 0.020147 | 1.1233 | 1.1862 | 24.3761 | 16.6174 | 210.6627
38961.3791 | 2214 | 29 | 38961.3791 | 1904 | 32 |  | 3362.5 | 3502.5 | 135.1648 | 1.7705 | 116.2393 | 1.9536 | 1.3516 | 0.017705 | 1.1624 | 0.019536 | 1.3339 | 1.1429 | 2.9368 | 47.5955 | 37.1177
38961.3796 | 1845 | 23 | 38961.3796 | 2167 | 27 |  | 3405 | 3545 | 112.6374 | 1.4042 | 132.2955 | 1.6484 | 1.1264 | 0.014042 | 1.323 | 0.016484 | 1.1123 | 1.3065 | 31.0277 | 5.3279 | 89.8145
38961.3801 | 1956 | 24 | 38961.3801 | 1861 | 29 |  | 3447 | 3587 | 119.4139 | 1.4652 | 113.6142 | 1.7705 | 1.1941 | 0.014652 | 1.1361 | 0.017705 | 1.1795 | 1.1184 | 17.4523 | 24.9353 | 246.4716
38961.3806 | 2055 | 25 | 38961.3806 | 1894 | 29 |  | 3489 | 3629 | 125.4579 | 1.5263 | 115.6288 | 1.7705 | 1.2546 | 0.015263 | 1.1563 | 0.017705 | 1.2393 | 1.1386 | 11.503 | 23.7077 | 150.5395

## A2-B3
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 143.1245 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38961.3387 | 1 | 0 | 38961.3387 | 1 | 0 |  | -125.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3392 | 1 | 0 | 38961.3392 | 1 | 0 |  | -83.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3397 | 1 | 0 | 38961.3397 | 1 | 0 |  | -41.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3402 | 1 | 0 | 38961.3402 | 1 | 0 |  | 0.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3407 | 1 | 0 | 38961.3407 | 1 | 0 |  | 42.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3412 | 1 | 0 | 38961.3412 | 1 | 0 |  | 84.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3416 | 1 | 0 | 38961.3417 | 1 | 0 |  | 126.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3421 | 1 | 0 | 38961.3421 | 1 | 0 |  | 168.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3426 | 1 | 0 | 38961.3426 | 1 | 0 |  | 210.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3431 | 1 | 0 | 38961.3431 | 1 | 0 |  | 252.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3436 | 1 | 0 | 38961.3436 | 1 | 0 |  | 294.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3441 | 1 | 0 | 38961.3441 | 1 | 0 |  | 336.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3446 | 1 | 0 | 38961.3446 | 1 | 0 |  | 378.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.345 | 1 | 0 | 38961.3451 | 1 | 0 |  | 420.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3455 | 1 | 0 | 38961.3455 | 1 | 0 |  | 462.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.346 | 1 | 0 | 38961.346 | 1 | 0 |  | 504.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3465 | 1 | 0 | 38961.3465 | 1 | 0 |  | 546.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.347 | 1 | 0 | 38961.347 | 1 | 0 |  | 588.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
| 1 | 0 | 38961.3475 | 1 | 0 |  | 631 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.348 | 1 | 0 | 38961.348 | 1 | 0 |  | 672.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3484 | 1 | 0 | 38961.3485 | 1 | 0 |  | 714.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3489 | 1 | 0 | 38961.3489 | 1 | 0 |  | 756.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3494 | 1 | 0 | 38961.3494 | 1 | 0 |  | 798.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3499 | 1 | 0 | 38961.3499 | 1 | 0 |  | 840.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3504 | 1 | 0 | 38961.3504 | 1 | 0 |  | 882.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3509 | 1 | 0 | 38961.3509 | 1 | 0 |  | 924.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3514 | 1 | 0 | 38961.3514 | 1 | 0 |  | 966.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3519 | 1 | 0 | 38961.3519 | 1 | 0 |  | 1008.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3523 | 1 | 0 | 38961.3523 | 1 | 0 |  | 1050.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3528 | 1 | 0 | 38961.3528 | 1 | 0 |  | 1092.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3533 | 1 | 0 | 38961.3533 | 1 | 0 |  | 1134.5 | 1274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3538 | 1 | 0 | 38961.3538 | 1 | 0 |  | 1176.5 | 1316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3543 | 1 | 0 | 38961.3543 | 1 | 0 |  | 1218.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3548 | 1 | 0 | 38961.3548 | 1 | 0 |  | 1260.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3553 | 1 | 0 | 38961.3553 | 1 | 0 |  | 1302.5 | 1442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3557 | 1 | 0 | 38961.3558 | 1 | 0 |  | 1344.5 | 1484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3562 | 1 | 0 | 38961.3562 | 1 | 0 |  | 1386.5 | 1526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3567 | 1 | 0 | 38961.3567 | 1 | 0 |  | 1428.5 | 1568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3572 | 1 | 0 | 38961.3572 | 1 | 0 |  | 1470.5 | 1610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3577 | 1 | 0 | 38961.3577 | 1 | 0 |  | 1512.5 | 1652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38961.3582 | 2 | 0 | 38961.3582 | 1 | 0 |  | 1554.5 | 1694.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117119 | 234338 | 117118.9988
38961.3587 | 3 | 0 | 38961.3587 | 2 | 0 |  | 1596.5 | 1736.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 78046 | 117119 | 78045.9982
38961.3591 | 3 | 0 | 38961.3592 | 2 | 0 |  | 1638.5 | 1778.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 78046 | 117119 | 78045.9982
38961.3596 | 2 | 0 | 38961.3596 | 2 | 0 |  | 1680.5 | 1820.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.3601 | 3 | 0 | 38961.3601 | 1 | 0 |  | 1722.5 | 1862.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 78046 | 234338 | 78045.9982
38961.3606 | 2 | 0 | 38961.3606 | 2 | 0 |  | 1764.5 | 1904.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.3611 | 3 | 0 | 38961.3611 | 2 | 0 |  | 1806.5 | 1946.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 78046 | 117119 | 78045.9982
38961.3616 | 3 | 0 | 38961.3616 | 2 | 0 |  | 1848.5 | 1988.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 78046 | 117119 | 78045.9982
38961.3621 | 3 | 0 | 38961.3621 | 2 | 0 |  | 1890.5 | 2030.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 78046 | 117119 | 78045.9982
38961.3625 | 2 | 0 | 38961.3626 | 2 | 0 |  | 1932 | 2072 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.363 | 2 | 0 | 38961.363 | 2 | 0 |  | 1974 | 2114 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.3635 | 2 | 0 | 38961.3635 | 2 | 0 |  | 2016 | 2156 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.364 | 2 | 0 | 38961.364 | 2 | 0 |  | 2058.5 | 2198.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.3645 | 2 | 0 | 38961.3645 | 2 | 0 |  | 2100.5 | 2240.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.365 | 2 | 0 | 38961.365 | 2 | 0 |  | 2142.5 | 2282.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.3655 | 2 | 0 | 38961.3655 | 2 | 0 |  | 2184.5 | 2324.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117119 | 117119 | 117118.9988
38961.3659 | 3 | 0 | 38961.366 | 4 | 0 |  | 2226.5 | 2366.5 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 78046 | 58509.5 | 78045.9982
38961.3664 | 82 | 56 | 38961.3664 | 11 | 1 |  | 2268.5 | 2408.5 | 5.0061 | 3.4188 | 0.67155 | 0.06105 | 0.050061 | 0.034188 | 0.0067155 | 0.0006105 | 0.015873 | 0.006105 | 8782.4363 | 23360.399 | 3923.1702
38961.3669 | 1050 | 1025 | 38961.3669 | 1088 | 987 |  | 2310 | 2450 | 64.1026 | 62.5763 | 66.4225 | 60.2564 | 0.64103 | 0.62576 | 0.66422 | 0.60256 | 0.015263 | 0.061661 | 852.1859 | 807.7902 | 23.3859
38961.3674 | 1149 | 1098 | 38961.3674 | 1031 | 925 |  | 2352.5 | 2492.5 | 70.1465 | 67.033 | 62.9426 | 56.4713 | 0.70147 | 0.67033 | 0.62943 | 0.56471 | 0.031136 | 0.064713 | 1122.0144 | 1976.9985 | 8.4418
38961.3679 | 1157 | 1090 | 38961.3679 | 1038 | 916 |  | 2394 | 2534 | 70.6349 | 66.5446 | 63.37 | 55.9219 | 0.70635 | 0.66545 | 0.6337 | 0.55922 | 0.040904 | 0.074481 | 1216.0585 | 3557.2459 | 8.6897
38961.3684 | 1036 | 899 | 38961.3684 | 982 | 869 |  | 2436 | 2576 | 63.2479 | 54.884 | 59.9512 | 53.0525 | 0.63248 | 0.54884 | 0.59951 | 0.53053 | 0.083639 | 0.068987 | 1177.1583 | 3477.3975 | 44.2643
38961.3689 | 1614 | 646 | 38961.3689 | 1156 | 738 |  | 2478.5 | 2618.5 | 98.5348 | 39.4383 | 70.5739 | 45.0549 | 0.98535 | 0.39438 | 0.70574 | 0.45055 | 0.59096 | 0.25519 | 44.4406 | 95.6331 | 6.3852
38961.3693 | 2011 | 203 | 38961.3694 | 1889 | 161 |  | 2520 | 2660 | 122.7717 | 12.3932 | 115.3236 | 9.8291 | 1.2277 | 0.12393 | 1.1532 | 0.098291 | 1.1038 | 1.0549 | 25.2107 | 41.8016 | 18.9333
38961.3698 | 1685 | 132 | 38961.3698 | 2157 | 142 |  | 2562 | 2702 | 102.8694 | 8.0586 | 131.685 | 8.6691 | 1.0287 | 0.080586 | 1.3168 | 0.086691 | 0.94811 | 1.2302 | 418.8883 | 9.4584 | 34.5237
38961.3703 | 2158 | 103 | 38961.3703 | 2090 | 104 |  | 2604 | 2744 | 131.746 | 6.2882 | 127.5946 | 6.3492 | 1.3175 | 0.062882 | 1.2759 | 0.063492 | 1.2546 | 1.2125 | 11.5337 | 23.4605 | 15.3827
38961.3708 | 1737 | 85 | 38961.3708 | 1888 | 77 |  | 2646 | 2786 | 106.044 | 5.1893 | 115.2625 | 4.7009 | 1.0604 | 0.051893 | 1.1526 | 0.047009 | 1.0085 | 1.1056 | 45.1082 | 27.823 | 133.7711
38961.3713 | 1746 | 75 | 38961.3713 | 2158 | 79 |  | 2688 | 2828 | 106.5934 | 4.5788 | 131.746 | 4.823 | 1.0659 | 0.045788 | 1.3175 | 0.04823 | 1.0201 | 1.2692 | 67.9037 | 9.4963 | 60.5217
38961.3718 | 2127 | 65 | 38961.3718 | 2183 | 67 |  | 2730 | 2870 | 129.8535 | 3.9683 | 133.2723 | 4.0904 | 1.2985 | 0.039683 | 1.3327 | 0.040904 | 1.2589 | 1.2918 | 15.7386 | 9.5474 | 20.4315
38961.3723 | 1781 | 63 | 38961.3723 | 2219 | 56 |  | 2772 | 2912 | 108.7302 | 3.8462 | 135.4701 | 3.4188 | 1.0873 | 0.038462 | 1.3547 | 0.034188 | 1.0488 | 1.3205 | 84.8039 | 5.9791 | 44.8101
38961.3727 | 1951 | 59 | 38961.3728 | 1886 | 43 |  | 2814 | 2954 | 119.1087 | 3.602 | 115.1404 | 2.6252 | 1.1911 | 0.03602 | 1.1514 | 0.026252 | 1.1551 | 1.1252 | 23.4379 | 27.621 | 122.6606
38961.3732 | 2232 | 49 | 38961.3733 | 1922 | 44 |  | 2856 | 2996 | 136.2637 | 2.9915 | 117.3382 | 2.6862 | 1.3626 | 0.029915 | 1.1734 | 0.026862 | 1.3327 | 1.1465 | 5.4589 | 39.4017 | 36.5598
38961.3737 | 2151 | 46 | 38961.3737 | 1847 | 39 |  | 2898 | 3038 | 131.3187 | 2.8083 | 112.7595 | 2.381 | 1.3132 | 0.028083 | 1.1276 | 0.02381 | 1.2851 | 1.1038 | 9.7933 | 35.281 | 83.5573
38961.3742 | 2147 | 50 | 38961.3742 | 2283 | 41 |  | 2940 | 3080 | 131.0745 | 3.0525 | 139.3773 | 2.5031 | 1.3107 | 0.030525 | 1.3938 | 0.025031 | 1.2802 | 1.3687 | 60.5831 | 2.8229 | 8.0925
38961.3747 | 2023 | 47 | 38961.3747 | 2304 | 39 |  | 2982 | 3122 | 123.5043 | 2.8694 | 140.6593 | 2.381 | 1.235 | 0.028694 | 1.4066 | 0.02381 | 1.2063 | 1.3828 | 41.7952 | 3.8938 | 21.8793
38961.3752 | 1760 | 38 | 38961.3752 | 2184 | 38 |  | 3024 | 3164 | 107.4481 | 2.3199 | 133.3333 | 2.3199 | 1.0745 | 0.023199 | 1.3333 | 0.023199 | 1.0513 | 1.3101 | 47.4133 | 7.7634 | 103.5835
38961.3757 | 2167 | 48 | 38961.3757 | 1970 | 34 |  | 3066 | 3206 | 132.2955 | 2.9304 | 120.2686 | 2.0757 | 1.323 | 0.029304 | 1.2027 | 0.020757 | 1.2937 | 1.1819 | 9.2486 | 23.8705 | 51.9422
38961.3761 | 2036 | 43 | 38961.3762 | 2310 | 40 |  | 3108 | 3248 | 124.2979 | 2.6252 | 141.0256 | 2.442 | 1.243 | 0.026252 | 1.4103 | 0.02442 | 1.2167 | 1.3858 | 30.5325 | 4.3744 | 25.8656
38961.3766 | 1908 | 41 | 38961.3767 | 2067 | 32 |  | 3150 | 3290 | 116.4835 | 2.5031 | 126.1905 | 1.9536 | 1.1648 | 0.025031 | 1.2619 | 0.019536 | 1.1398 | 1.2424 | 27.5603 | 14.4552 | 121.7924
38961.3771 | 2208 | 47 | 38961.3771 | 2069 | 38 |  | 3192 | 3332 | 134.7985 | 2.8694 | 126.3126 | 2.3199 | 1.348 | 0.028694 | 1.2631 | 0.023199 | 1.3193 | 1.2399 | 7.1592 | 18.356 | 29.4938
38961.3776 | 2059 | 48 | 38961.3776 | 2063 | 38 |  | 3234 | 3374 | 125.7021 | 2.9304 | 125.9463 | 2.3199 | 1.257 | 0.029304 | 1.2595 | 0.023199 | 1.2277 | 1.2363 | 16.745 | 15.649 | 66.9188
38961.3781 | 1964 | 42 | 38961.3781 | 1862 | 31 |  | 3276 | 3416 | 119.9023 | 2.5641 | 113.6752 | 1.8926 | 1.199 | 0.025641 | 1.1368 | 0.018926 | 1.1734 | 1.1178 | 21.4278 | 28.6054 | 179.2023
38961.3786 | 1837 | 34 | 38961.3786 | 2328 | 37 |  | 3318 | 3458 | 112.149 | 2.0757 | 142.1245 | 2.2589 | 1.1215 | 0.020757 | 1.4212 | 0.022589 | 1.1007 | 1.3987 | 14.5839 | 2.0286 | 27.6822
38961.3791 | 2099 | 43 | 38961.3791 | 2301 | 34 |  | 3360 | 3500 | 128.1441 | 2.6252 | 140.4762 | 2.0757 | 1.2814 | 0.026252 | 1.4048 | 0.020757 | 1.2552 | 1.384 | 110.744 | 2.3441 | 10.7797
38961.3795 | 2186 | 38 | 38961.3796 | 2075 | 32 |  | 3402 | 3542 | 133.4554 | 2.3199 | 126.6789 | 1.9536 | 1.3346 | 0.023199 | 1.2668 | 0.019536 | 1.3114 | 1.2473 | 8.2732 | 16.2648 | 44.3172
38961.38 | 2254 | 41 | 38961.3801 | 1989 | 31 |  | 3444 | 3584 | 137.6068 | 2.5031 | 121.4286 | 1.8926 | 1.3761 | 0.025031 | 1.2143 | 0.018926 | 1.351 | 1.1954 | 4.3683 | 28.468 | 26.6888
38961.3805 | 1867 | 32 | 38961.3805 | 1835 | 27 |  | 3486 | 3626 | 113.9805 | 1.9536 | 112.0269 | 1.6484 | 1.1398 | 0.019536 | 1.1203 | 0.016484 | 1.1203 | 1.1038 | 27.6332 | 29.7832 | 319.3993

## A1-C6
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 148.1306 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38961.3387 | 1 | 0 | 38961.3387 | 1 | 0 |  | -128.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3392 | 1 | 0 | 38961.3392 | 1 | 0 |  | -86.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3397 | 1 | 0 | 38961.3397 | 1 | 0 |  | -44.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3402 | 1 | 0 | 38961.3402 | 1 | 0 |  | -2.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3406 | 1 | 0 | 38961.3406 | 1 | 0 |  | 39.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3411 | 1 | 0 | 38961.3411 | 1 | 0 |  | 81.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3416 | 1 | 0 | 38961.3416 | 1 | 0 |  | 123.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3421 | 1 | 0 | 38961.3421 | 1 | 0 |  | 165.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3426 | 1 | 0 | 38961.3426 | 1 | 0 |  | 207.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3431 | 1 | 0 | 38961.3431 | 1 | 0 |  | 249.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3436 | 2 | 0 | 38961.3436 | 1 | 0 |  | 291.5 | 431.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121219 | 242538 | 121218.9988
38961.344 | 1 | 0 | 38961.3441 | 1 | 0 |  | 333.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3445 | 1 | 0 | 38961.3445 | 1 | 0 |  | 375.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.345 | 1 | 0 | 38961.345 | 1 | 0 |  | 417.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3455 | 1 | 0 | 38961.3455 | 1 | 0 |  | 459.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.346 | 1 | 0 | 38961.346 | 1 | 0 |  | 501.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3465 | 1 | 0 | 38961.3465 | 1 | 0 |  | 543.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.347 | 1 | 0 | 38961.347 | 1 | 0 |  | 585.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3474 | 1 | 0 | 38961.3475 | 1 | 0 |  | 627.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3479 | 1 | 0 | 38961.3479 | 1 | 0 |  | 669.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3484 | 1 | 0 | 38961.3484 | 1 | 0 |  | 711.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3489 | 1 | 0 | 38961.3489 | 1 | 0 |  | 753.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3494 | 1 | 0 | 38961.3494 | 1 | 0 |  | 795.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3499 | 1 | 0 | 38961.3499 | 1 | 0 |  | 837.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3504 | 1 | 0 | 38961.3504 | 1 | 0 |  | 879.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3508 | 1 | 0 | 38961.3509 | 1 | 0 |  | 921.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3513 | 1 | 0 | 38961.3513 | 1 | 0 |  | 963.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3518 | 1 | 0 | 38961.3518 | 1 | 0 |  | 1005.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3523 | 1 | 0 | 38961.3523 | 1 | 0 |  | 1047.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3528 | 1 | 0 | 38961.3528 | 1 | 0 |  | 1089.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3533 | 1 | 0 | 38961.3533 | 1 | 0 |  | 1131.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3538 | 1 | 0 | 38961.3538 | 1 | 0 |  | 1173.5 | 1313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3542 | 1 | 0 | 38961.3543 | 1 | 0 |  | 1215.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3547 | 1 | 0 | 38961.3547 | 1 | 0 |  | 1257.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3552 | 1 | 0 | 38961.3552 | 1 | 0 |  | 1299.5 | 1439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3557 | 1 | 0 | 38961.3557 | 1 | 0 |  | 1341.5 | 1481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3562 | 1 | 0 | 38961.3562 | 1 | 0 |  | 1383.5 | 1523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3567 | 1 | 0 | 38961.3567 | 1 | 0 |  | 1425.5 | 1565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3572 | 1 | 0 | 38961.3572 | 1 | 0 |  | 1467.5 | 1607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38961.3577 | 2 | 0 | 38961.3577 | 13 | 0 |  | 1509.5 | 1649.5 | 0.1221 | 0 | 0.79365 | 0 | 0.001221 | 0 | 0.0079365 | 0 | 0.001221 | 0.0079365 | 121219 | 18564.4615 | 121218.9988
38961.3581 | 2 | 0 | 38961.3581 | 969 | 0 |  | 1551.5 | 1691.5 | 0.1221 | 0 | 59.1575 | 0 | 0.001221 | 0 | 0.59158 | 0 | 0.001221 | 0.59158 | 121219 | 150.4004 | 121218.9988
38961.3586 | 3 | 0 | 38961.3586 | 2189 | 0 |  | 1593.5 | 1733.5 | 0.18315 | 0 | 133.6386 | 0 | 0.0018315 | 0 | 1.3364 | 0 | 0.0018315 | 1.3364 | 80779.3333 | 10.8442 | 80779.3315
38961.3591 | 2 | 0 | 38961.3591 | 1991 | 0 |  | 1635.5 | 1775.5 | 0.1221 | 0 | 121.5507 | 0 | 0.001221 | 0 | 1.2155 | 0 | 0.001221 | 1.2155 | 121219 | 21.8674 | 121218.9988
38961.3596 | 2 | 0 | 38961.3596 | 2141 | 0 |  | 1677.5 | 1817.5 | 0.1221 | 0 | 130.7082 | 0 | 0.001221 | 0 | 1.3071 | 0 | 0.001221 | 1.3071 | 121219 | 13.3293 | 121218.9988
38961.3601 | 3 | 0 | 38961.3601 | 2231 | 0 |  | 1719.5 | 1859.5 | 0.18315 | 0 | 136.2027 | 0 | 0.0018315 | 0 | 1.362 | 0 | 0.0018315 | 1.362 | 80779.3333 | 8.7575 | 80779.3315
38961.3606 | 3 | 0 | 38961.3606 | 2299 | 0 |  | 1761.5 | 1901.5 | 0.18315 | 0 | 140.3541 | 0 | 0.0018315 | 0 | 1.4035 | 0 | 0.0018315 | 1.4035 | 80779.3333 | 5.5407 | 80779.3315
38961.3611 | 2 | 0 | 38961.3611 | 1894 | 0 |  | 1803.5 | 1943.5 | 0.1221 | 0 | 115.6288 | 0 | 0.001221 | 0 | 1.1563 | 0 | 0.001221 | 1.1563 | 121219 | 28.1088 | 121218.9988
38961.3615 | 3 | 0 | 38961.3616 | 2011 | 0 |  | 1845.5 | 1985.5 | 0.18315 | 0 | 122.7717 | 0 | 0.0018315 | 0 | 1.2277 | 0 | 0.0018315 | 1.2277 | 80779.3333 | 20.6554 | 80779.3315
38961.362 | 3 | 0 | 38961.362 | 1906 | 0 |  | 1887.5 | 2027.5 | 0.18315 | 0 | 116.3614 | 0 | 0.0018315 | 0 | 1.1636 | 0 | 0.0018315 | 1.1636 | 80779.3333 | 27.3022 | 80779.3315
38961.3625 | 2 | 0 | 38961.3625 | 1888 | 0 |  | 1929.5 | 2069.5 | 0.1221 | 0 | 115.2625 | 0 | 0.001221 | 0 | 1.1526 | 0 | 0.001221 | 1.1526 | 121219 | 28.5159 | 121218.9988
38961.363 | 2 | 0 | 38961.363 | 1853 | 0 |  | 1971.5 | 2111.5 | 0.1221 | 0 | 113.1258 | 0 | 0.001221 | 0 | 1.1313 | 0 | 0.001221 | 1.1313 | 121219 | 30.9433 | 121218.9988
38961.3635 | 2 | 0 | 38961.3635 | 1856 | 0 |  | 2013.5 | 2153.5 | 0.1221 | 0 | 113.3089 | 0 | 0.001221 | 0 | 1.1331 | 0 | 0.001221 | 1.1331 | 121219 | 30.7317 | 121218.9988
38961.364 | 2 | 0 | 38961.364 | 1929 | 0 |  | 2055.5 | 2195.5 | 0.1221 | 0 | 117.7656 | 0 | 0.001221 | 0 | 1.1777 | 0 | 0.001221 | 1.1777 | 121219 | 25.7843 | 121218.9988
38961.3645 | 2 | 0 | 38961.3645 | 2012 | 0 |  | 2097.5 | 2237.5 | 0.1221 | 0 | 122.8327 | 0 | 0.001221 | 0 | 1.2283 | 0 | 0.001221 | 1.2283 | 121219 | 20.5954 | 121218.9988
38961.3649 | 2 | 0 | 38961.365 | 2261 | 0 |  | 2139.5 | 2279.5 | 0.1221 | 0 | 138.0342 | 0 | 0.001221 | 0 | 1.3803 | 0 | 0.001221 | 1.3803 | 121219 | 7.3145 | 121218.9988
38961.3654 | 2 | 0 | 38961.3654 | 2200 | 0 |  | 2181.5 | 2321.5 | 0.1221 | 0 | 134.3101 | 0 | 0.001221 | 0 | 1.3431 | 0 | 0.001221 | 1.3431 | 121219 | 10.29 | 121218.9988
38961.3659 | 2 | 0 | 38961.3659 | 2410 | 0 |  | 2223.5 | 2363.5 | 0.1221 | 0 | 147.1306 | 0 | 0.001221 | 0 | 1.4713 | 0 | 0.001221 | 1.4713 | 121219 | 0.67967 | 121218.9988
38961.3664 | 10 | 0 | 38961.3664 | 2290 | 0 |  | 2265.5 | 2405.5 | 0.6105 | 0 | 139.8046 | 0 | 0.006105 | 0 | 1.398 | 0 | 0.006105 | 1.398 | 24163.8 | 5.9555 | 24163.7939
38961.3669 | 29 | 1 | 38961.3669 | 2003 | 1 |  | 2307.5 | 2447.5 | 1.7705 | 0.06105 | 122.2833 | 0.06105 | 0.017705 | 0.0006105 | 1.2228 | 0.0006105 | 0.017094 | 1.2222 | 10301.8251 | 21.148 | 41831.9366
38961.3674 | 45 | 1 | 38961.3674 | 2367 | 1 |  | 2349.5 | 2489.5 | 2.7473 | 0.06105 | 144.5055 | 0.06105 | 0.027473 | 0.0006105 | 1.4451 | 0.0006105 | 0.026862 | 1.4444 | 57314.0987 | 2.5097 | 5827.8318
38961.3679 | 481 | 1 | 38961.3679 | 2365 | 1 |  | 2391.5 | 2531.5 | 29.3651 | 0.06105 | 144.3834 | 0.06105 | 0.29365 | 0.0006105 | 1.4438 | 0.0006105 | 0.29304 | 1.4432 | 440.6401 | 2.5967 | 4921.1758
38961.3683 | 55 | 1 | 38961.3684 | 2381 | 1 |  | 2433.5 | 2573.5 | 3.3578 | 0.06105 | 145.3602 | 0.06105 | 0.033578 | 0.0006105 | 1.4536 | 0.0006105 | 0.032967 | 1.453 | 152598.1628 | 1.9067 | 4435.0936
38961.3688 | 244 | 1 | 38961.3688 | 2131 | 1 |  | 2475.5 | 2615.5 | 14.8962 | 0.06105 | 130.0977 | 0.06105 | 0.14896 | 0.0006105 | 1.301 | 0.0006105 | 0.14835 | 1.3004 | 925.5636 | 13.8683 | 26567.5782
38961.3693 | 1960 | 0 | 38961.3693 | 2400 | 1 |  | 2517.5 | 2657.5 | 119.6581 | 0 | 146.5201 | 0.06105 | 1.1966 | 0 | 1.4652 | 0.0006105 | 1.1966 | 1.4646 | 23.7949 | 1.1413 | 22.5983
38961.3698 | 1774 | 0 | 38961.3698 | 2317 | 0 |  | 2559.5 | 2699.5 | 108.3028 | 0 | 141.453 | 0 | 1.083 | 0 | 1.4145 | 0 | 1.083 | 1.4145 | 36.7745 | 4.7208 | 35.6915
38961.3703 | 2136 | 0 | 38961.3703 | 1939 | 0 |  | 2601.5 | 2741.5 | 130.4029 | 0 | 118.3761 | 0 | 1.304 | 0 | 1.1838 | 0 | 1.304 | 1.1838 | 13.5946 | 25.1356 | 12.2905
38961.3708 | 1697 | 0 | 38961.3708 | 2052 | 0 |  | 2643.5 | 2783.5 | 103.602 | 0 | 125.2747 | 0 | 1.036 | 0 | 1.2527 | 0 | 1.036 | 1.2527 | 42.9806 | 18.2446 | 41.9445
38961.3713 | 1880 | 0 | 38961.3713 | 2376 | 0 |  | 2685.5 | 2825.5 | 114.7741 | 0 | 145.0549 | 0 | 1.1477 | 0 | 1.4505 | 0 | 1.1477 | 1.4505 | 29.0628 | 2.1204 | 27.915
38961.3717 | 1819 | 0 | 38961.3718 | 1968 | 0 |  | 2727.5 | 2867.5 | 111.0501 | 0 | 120.1465 | 0 | 1.1105 | 0 | 1.2015 | 0 | 1.1105 | 1.2015 | 33.3909 | 23.2917 | 32.2804
38961.3722 | 2088 | 0 | 38961.3722 | 2019 | 0 |  | 2769.5 | 2909.5 | 127.4725 | 0 | 123.2601 | 0 | 1.2747 | 0 | 1.2326 | 0 | 1.2747 | 1.2326 | 16.2059 | 20.1773 | 14.9312
38961.3727 | 1930 | 0 | 38961.3727 | 2111 | 0 |  | 2811.5 | 2951.5 | 117.8266 | 0 | 128.8767 | 0 | 1.1783 | 0 | 1.2888 | 0 | 1.1783 | 1.2888 | 25.7192 | 14.9398 | 24.5409
38961.3732 | 1803 | 0 | 38961.3732 | 2069 | 0 |  | 2853.5 | 2993.5 | 110.0733 | 0 | 126.3126 | 0 | 1.1007 | 0 | 1.2631 | 0 | 1.1007 | 1.2631 | 34.5746 | 17.2731 | 33.4739
38961.3737 | 1918 | 0 | 38961.3737 | 2161 | 0 |  | 2895.5 | 3035.5 | 117.094 | 0 | 131.9292 | 0 | 1.1709 | 0 | 1.3193 | 0 | 1.1709 | 1.3193 | 26.5057 | 12.2804 | 25.3348
38961.3742 | 1756 | 0 | 38961.3742 | 1934 | 0 |  | 2937.5 | 3077.5 | 107.2039 | 0 | 118.0708 | 0 | 1.072 | 0 | 1.1807 | 0 | 1.072 | 1.1807 | 38.1765 | 25.4592 | 37.1045
38961.3747 | 1950 | 0 | 38961.3747 | 2186 | 0 |  | 2979.5 | 3119.5 | 119.0476 | 0 | 133.4554 | 0 | 1.1905 | 0 | 1.3346 | 0 | 1.1905 | 1.3346 | 24.4297 | 10.9963 | 23.2393
38961.3752 | 2061 | 0 | 38961.3752 | 2359 | 0 |  | 3021.5 | 3161.5 | 125.8242 | 0 | 144.0171 | 0 | 1.2582 | 0 | 1.4402 | 0 | 1.2582 | 1.4402 | 17.7283 | 2.8563 | 16.47
38961.3756 | 1999 | 0 | 38961.3756 | 2034 | 0 |  | 3063 | 3203 | 122.0391 | 0 | 124.1758 | 0 | 1.2204 | 0 | 1.2418 | 0 | 1.2204 | 1.2418 | 21.3797 | 19.2911 | 20.1593
38961.3761 | 2144 | 0 | 38961.3761 | 1932 | 0 |  | 3105.5 | 3245.5 | 130.8913 | 0 | 117.9487 | 0 | 1.3089 | 0 | 1.1795 | 0 | 1.3089 | 1.1795 | 13.1707 | 25.589 | 11.8618
38961.3766 | 1896 | 0 | 38961.3766 | 2198 | 0 |  | 3147.5 | 3287.5 | 115.7509 | 0 | 134.188 | 0 | 1.1575 | 0 | 1.3419 | 0 | 1.1575 | 1.3419 | 27.9736 | 10.3904 | 26.8161
38961.3771 | 1843 | 0 | 38961.3771 | 2288 | 0 |  | 3189.5 | 3329.5 | 112.5153 | 0 | 139.6825 | 0 | 1.1252 | 0 | 1.3968 | 0 | 1.1252 | 1.3968 | 31.6538 | 6.0481 | 30.5287
38961.3776 | 2275 | 1 | 38961.3776 | 2076 | 0 |  | 3231.5 | 3371.5 | 138.8889 | 0.06105 | 126.7399 | 0 | 1.3889 | 0.0006105 | 1.2674 | 0 | 1.3883 | 1.2674 | 6.6744 | 16.8776 | 2171.5537
38961.3781 | 1911 | 0 | 38961.3781 | 2027 | 0 |  | 3273.5 | 3413.5 | 116.6667 | 0 | 123.7485 | 0 | 1.1667 | 0 | 1.2375 | 0 | 1.1667 | 1.2375 | 26.9691 | 19.703 | 25.8025
38961.3785 | 2001 | 0 | 38961.3786 | 1951 | 0 |  | 3315 | 3455 | 122.1612 | 0 | 119.1087 | 0 | 1.2216 | 0 | 1.1911 | 0 | 1.2216 | 1.1911 | 21.2584 | 24.366 | 20.0368
38961.379 | 1953 | 0 | 38961.3791 | 2246 | 0 |  | 3357.5 | 3497.5 | 119.2308 | 0 | 137.1184 | 0 | 1.1923 | 0 | 1.3712 | 0 | 1.1923 | 1.3712 | 24.2386 | 8.0312 | 23.0463
38961.3795 | 2210 | 0 | 38961.3795 | 1863 | 0 |  | 3399.5 | 3539.5 | 134.9206 | 0 | 113.7363 | 0 | 1.3492 | 0 | 1.1374 | 0 | 1.3492 | 1.1374 | 9.791 | 30.2405 | 8.4417
38961.38 | 2097 | 0 | 38961.38 | 2190 | 0 |  | 3441 | 3581 | 128.022 | 0 | 133.6996 | 0 | 1.2802 | 0 | 1.337 | 0 | 1.2802 | 1.337 | 15.7072 | 10.7936 | 14.427
38961.3805 | 1837 | 0 | 38961.3805 | 1900 | 0 |  | 3483 | 3623 | 112.149 | 0 | 115.9951 | 0 | 1.1215 | 0 | 1.16 | 0 | 1.1215 | 1.16 | 32.0838 | 27.7042 | 30.9623

## A1-C5
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 145.7497 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38961.3387 | 1 | 0 | 38961.3387 | 1 | 0 |  | -131 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3391 | 1 | 0 | 38961.3392 | 1 | 0 |  | -89 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3396 | 1 | 0 | 38961.3397 | 1 | 0 |  | -47 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3401 | 5 | 0 | 38961.3401 | 1 | 0 |  | -5 | 135 | 0.30525 | 0 | 0.06105 | 0 | 0.0030525 | 0 | 0.0006105 | 0 | 0.0030525 | 0.0006105 | 47647.6 | 238638 | 47647.5969
38961.3406 | 1 | 0 | 38961.3406 | 1 | 0 |  | 37 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3411 | 1 | 0 | 38961.3411 | 1 | 0 |  | 79 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3416 | 1 | 0 | 38961.3416 | 1 | 0 |  | 121 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3421 | 1 | 0 | 38961.3421 | 1 | 0 |  | 163 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3425 | 1 | 0 | 38961.3426 | 1 | 0 |  | 205 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.343 | 1 | 0 | 38961.3431 | 1 | 0 |  | 247 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3435 | 1 | 0 | 38961.3435 | 1 | 0 |  | 289 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.344 | 1 | 0 | 38961.344 | 1 | 0 |  | 331 | 471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3445 | 1 | 0 | 38961.3445 | 1 | 0 |  | 373 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.345 | 1 | 0 | 38961.345 | 1 | 0 |  | 415 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3455 | 1 | 0 | 38961.3455 | 1 | 0 |  | 457 | 597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3459 | 1 | 0 | 38961.346 | 1 | 0 |  | 499 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3464 | 1 | 0 | 38961.3465 | 1 | 0 |  | 541 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3469 | 1 | 0 | 38961.3469 | 1 | 0 |  | 582.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3474 | 1 | 0 | 38961.3474 | 1 | 0 |  | 625 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3479 | 1 | 0 | 38961.3479 | 1 | 0 |  | 667 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3484 | 1 | 0 | 38961.3484 | 1 | 0 |  | 708.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3489 | 1 | 0 | 38961.3489 | 1 | 0 |  | 751 | 891 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3494 | 1 | 0 | 38961.3494 | 1 | 0 |  | 793 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3498 | 1 | 0 | 38961.3499 | 1 | 0 |  | 835 | 975 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3503 | 1 | 0 | 38961.3503 | 1 | 0 |  | 877 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3508 | 1 | 0 | 38961.3508 | 1 | 0 |  | 918.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3513 | 1 | 0 | 38961.3513 | 1 | 0 |  | 960.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3518 | 1 | 0 | 38961.3518 | 1 | 0 |  | 1002.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3523 | 1 | 0 | 38961.3523 | 1 | 0 |  | 1044.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3528 | 1 | 1 | 38961.3528 | 1 | 0 |  | 1086.5 | 1226.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 569480950.44 | 238638 | 238438.0838
38961.3532 | 1 | 0 | 38961.3533 | 1 | 0 |  | 1128.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3537 | 1 | 0 | 38961.3537 | 1 | 0 |  | 1170.5 | 1310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3542 | 1 | 0 | 38961.3542 | 1 | 0 |  | 1212.5 | 1352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3547 | 1 | 0 | 38961.3547 | 1 | 0 |  | 1254.5 | 1394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3552 | 1 | 0 | 38961.3552 | 1 | 0 |  | 1296.5 | 1436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3557 | 1 | 0 | 38961.3557 | 1 | 0 |  | 1338.5 | 1478.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3562 | 2 | 0 | 38961.3562 | 1 | 0 |  | 1380.5 | 1520.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119269 | 238638 | 119268.9988
38961.3566 | 1 | 0 | 38961.3567 | 1 | 0 |  | 1422.5 | 1562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3571 | 1 | 0 | 38961.3571 | 1 | 0 |  | 1464.5 | 1604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38961.3576 | 1 | 0 | 38961.3576 | 1673 | 0 |  | 1506.5 | 1646.5 | 0.06105 | 0 | 102.1368 | 0 | 0.0006105 | 0 | 1.0214 | 0 | 0.0006105 | 1.0214 | 238638 | 42.7005 | 238637.9994
38961.3581 | 1 | 0 | 38961.3581 | 2120 | 0 |  | 1548.5 | 1688.5 | 0.06105 | 0 | 129.4261 | 0 | 0.0006105 | 0 | 1.2943 | 0 | 0.0006105 | 1.2943 | 238638 | 12.6123 | 238637.9994
38961.3586 | 2 | 0 | 38961.3586 | 2175 | 0 |  | 1590.5 | 1730.5 | 0.1221 | 0 | 132.7839 | 0 | 0.001221 | 0 | 1.3278 | 0 | 0.001221 | 1.3278 | 119269 | 9.7646 | 119268.9988
38961.3591 | 2 | 0 | 38961.3591 | 2242 | 0 |  | 1632.5 | 1772.5 | 0.1221 | 0 | 136.8742 | 0 | 0.001221 | 0 | 1.3687 | 0 | 0.001221 | 1.3687 | 119269 | 6.4844 | 119268.9988
38961.3596 | 2 | 0 | 38961.3596 | 2366 | 0 |  | 1674.5 | 1814.5 | 0.1221 | 0 | 144.4444 | 0 | 0.001221 | 0 | 1.4444 | 0 | 0.001221 | 1.4444 | 119269 | 0.90363 | 119268.9988
38961.36 | 2 | 0 | 38961.3601 | 2039 | 0 |  | 1716.5 | 1856.5 | 0.1221 | 0 | 124.4811 | 0 | 0.001221 | 0 | 1.2448 | 0 | 0.001221 | 1.2448 | 119269 | 17.0858 | 119268.9988
38961.3605 | 1 | 0 | 38961.3605 | 2371 | 0 |  | 1758.5 | 1898.5 | 0.06105 | 0 | 144.7497 | 0 | 0.0006105 | 0 | 1.4475 | 0 | 0.0006105 | 1.4475 | 238638 | 0.69085 | 238637.9994
38961.361 | 2 | 0 | 38961.361 | 1986 | 0 |  | 1800.5 | 1940.5 | 0.1221 | 0 | 121.2454 | 0 | 0.001221 | 0 | 1.2125 | 0 | 0.001221 | 1.2125 | 119269 | 20.2105 | 119268.9988
38961.3615 | 2 | 0 | 38961.3615 | 1915 | 0 |  | 1842.5 | 1982.5 | 0.1221 | 0 | 116.9109 | 0 | 0.001221 | 0 | 1.1691 | 0 | 0.001221 | 1.1691 | 119269 | 24.6674 | 119268.9988
38961.362 | 2 | 0 | 38961.362 | 2219 | 0 |  | 1884.5 | 2024.5 | 0.1221 | 0 | 135.4701 | 0 | 0.001221 | 0 | 1.3547 | 0 | 0.001221 | 1.3547 | 119269 | 7.5881 | 119268.9988
38961.3625 | 2 | 0 | 38961.3625 | 1961 | 0 |  | 1926.5 | 2066.5 | 0.1221 | 0 | 119.7192 | 0 | 0.001221 | 0 | 1.1972 | 0 | 0.001221 | 1.1972 | 119269 | 21.743 | 119268.9988
38961.363 | 2 | 0 | 38961.363 | 2130 | 0 |  | 1968.5 | 2108.5 | 0.1221 | 0 | 130.0366 | 0 | 0.001221 | 0 | 1.3004 | 0 | 0.001221 | 1.3004 | 119269 | 12.0836 | 119268.9988
38961.3634 | 2 | 0 | 38961.3635 | 1863 | 0 |  | 2010.5 | 2150.5 | 0.1221 | 0 | 113.7363 | 0 | 0.001221 | 0 | 1.1374 | 0 | 0.001221 | 1.1374 | 119269 | 28.1471 | 119268.9988
38961.3639 | 2 | 0 | 38961.3639 | 1931 | 0 |  | 2052.5 | 2192.5 | 0.1221 | 0 | 117.8877 | 0 | 0.001221 | 0 | 1.1789 | 0 | 0.001221 | 1.1789 | 119269 | 23.6344 | 119268.9988
38961.3644 | 2 | 0 | 38961.3644 | 1933 | 0 |  | 2094.5 | 2234.5 | 0.1221 | 0 | 118.0098 | 0 | 0.001221 | 0 | 1.1801 | 0 | 0.001221 | 1.1801 | 119269 | 23.5065 | 119268.9988
38961.3649 | 2 | 0 | 38961.3649 | 2172 | 0 |  | 2136.5 | 2276.5 | 0.1221 | 0 | 132.6007 | 0 | 0.001221 | 0 | 1.326 | 0 | 0.001221 | 1.326 | 119269 | 9.9162 | 119268.9988
38961.3654 | 2 | 0 | 38961.3654 | 2330 | 0 |  | 2178.5 | 2318.5 | 0.1221 | 0 | 142.2466 | 0 | 0.001221 | 0 | 1.4225 | 0 | 0.001221 | 1.4225 | 119269 | 2.4627 | 119268.9988
38961.3659 | 2 | 0 | 38961.3659 | 2367 | 0 |  | 2220.5 | 2360.5 | 0.1221 | 0 | 144.5055 | 0 | 0.001221 | 0 | 1.4451 | 0 | 0.001221 | 1.4451 | 119269 | 0.86101 | 119268.9988
38961.3664 | 9 | 0 | 38961.3664 | 2008 | 0 |  | 2262.5 | 2402.5 | 0.54945 | 0 | 122.5885 | 0 | 0.0054945 | 0 | 1.2259 | 0 | 0.0054945 | 1.2259 | 26426.4444 | 18.8934 | 26426.4389
38961.3669 | 26 | 2 | 38961.3669 | 1910 | 1 |  | 2304.5 | 2444.5 | 1.5873 | 0.1221 | 116.6056 | 0.06105 | 0.015873 | 0.001221 | 1.1661 | 0.0006105 | 0.014652 | 1.1654 | 14756.5896 | 25.0069 | 23599.0082
38961.3673 | 44 | 2 | 38961.3673 | 2011 | 1 |  | 2346.5 | 2486.5 | 2.6862 | 0.1221 | 122.7717 | 0.06105 | 0.026862 | 0.001221 | 1.2277 | 0.0006105 | 0.025641 | 1.2271 | 7482.2053 | 18.7255 | 18464.2333
38961.3678 | 181 | 2 | 38961.3678 | 2208 | 1 |  | 2388.5 | 2528.5 | 11.0501 | 0.1221 | 134.7985 | 0.06105 | 0.1105 | 0.001221 | 1.348 | 0.0006105 | 0.10928 | 1.3474 | 1429.06 | 8.128 | 8285.2119
38961.3683 | 105 | 1 | 38961.3683 | 2305 | 1 |  | 2430.5 | 2570.5 | 6.4103 | 0.06105 | 140.7204 | 0.06105 | 0.064103 | 0.0006105 | 1.4072 | 0.0006105 | 0.063492 | 1.4066 | 3001.8498 | 3.5756 | 7875.6404
38961.3688 | 89 | 2 | 38961.3688 | 2044 | 1 |  | 2472.5 | 2612.5 | 5.4335 | 0.1221 | 124.7863 | 0.06105 | 0.054335 | 0.001221 | 1.2479 | 0.0006105 | 0.053114 | 1.2473 | 3060.392 | 16.8079 | 16521.7141
38961.3693 | 1664 | 0 | 38961.3693 | 2204 | 0 |  | 2514.5 | 2654.5 | 101.5873 | 0 | 134.5543 | 0 | 1.0159 | 0 | 1.3455 | 0 | 1.0159 | 1.3455 | 43.4724 | 8.3203 | 42.4565
38961.3698 | 2090 | 0 | 38961.3698 | 1901 | 0 |  | 2556.5 | 2696.5 | 127.5946 | 0 | 116.0562 | 0 | 1.2759 | 0 | 1.1606 | 0 | 1.2759 | 1.1606 | 14.2287 | 25.5855 | 12.9528
38961.3703 | 1824 | 0 | 38961.3703 | 1912 | 0 |  | 2598.5 | 2738.5 | 111.3553 | 0 | 116.7277 | 0 | 1.1136 | 0 | 1.1673 | 0 | 1.1136 | 1.1673 | 30.8871 | 24.863 | 29.7735
38961.3707 | 1779 | 0 | 38961.3708 | 2094 | 0 |  | 2640.5 | 2780.5 | 108.6081 | 0 | 127.8388 | 0 | 1.0861 | 0 | 1.2784 | 0 | 1.0861 | 1.2784 | 34.1979 | 14.0105 | 33.1118
38961.3712 | 1790 | 0 | 38961.3712 | 2240 | 0 |  | 2682.5 | 2822.5 | 109.2796 | 0 | 136.7521 | 0 | 1.0928 | 0 | 1.3675 | 0 | 1.0928 | 1.3675 | 33.3732 | 6.5795 | 32.2804
38961.3717 | 1983 | 0 | 38961.3717 | 2023 | 0 |  | 2724.5 | 2864.5 | 121.0623 | 0 | 123.5043 | 0 | 1.2106 | 0 | 1.235 | 0 | 1.2106 | 1.235 | 20.3923 | 18.0119 | 19.1817
38961.3722 | 1841 | 0 | 38961.3722 | 1936 | 0 |  | 2766.5 | 2906.5 | 112.3932 | 0 | 118.1929 | 0 | 1.1239 | 0 | 1.1819 | 0 | 1.1239 | 1.1819 | 29.6784 | 23.3151 | 28.5545
38961.3727 | 2177 | 0 | 38961.3727 | 2357 | 0 |  | 2808.5 | 2948.5 | 132.906 | 0 | 143.895 | 0 | 1.3291 | 0 | 1.4389 | 0 | 1.3291 | 1.4389 | 9.6638 | 1.2889 | 8.3347
38961.3732 | 1758 | 0 | 38961.3732 | 1938 | 0 |  | 2850.5 | 2990.5 | 107.326 | 0 | 118.315 | 0 | 1.0733 | 0 | 1.1832 | 0 | 1.0733 | 1.1832 | 35.8009 | 23.1878 | 34.7277
38961.3737 | 2098 | 0 | 38961.3737 | 2149 | 0 |  | 2892.5 | 3032.5 | 128.083 | 0 | 131.1966 | 0 | 1.2808 | 0 | 1.312 | 0 | 1.2808 | 1.312 | 13.7931 | 11.0926 | 12.5123
38961.3741 | 1848 | 0 | 38961.3742 | 2199 | 0 |  | 2934.5 | 3074.5 | 112.8205 | 0 | 134.2491 | 0 | 1.1282 | 0 | 1.3425 | 0 | 1.1282 | 1.3425 | 29.1872 | 8.5666 | 28.059
38961.3746 | 1945 | 0 | 38961.3746 | 1941 | 0 |  | 2976.5 | 3116.5 | 118.7424 | 0 | 118.4982 | 0 | 1.1874 | 0 | 1.185 | 0 | 1.1874 | 1.185 | 22.7445 | 22.9974 | 21.557
38961.3751 | 1878 | 0 | 38961.3751 | 2104 | 0 |  | 3018.5 | 3158.5 | 114.652 | 0 | 128.4493 | 0 | 1.1465 | 0 | 1.2845 | 0 | 1.1465 | 1.2845 | 27.1235 | 13.4686 | 25.977
38961.3756 | 2028 | 0 | 38961.3756 | 2354 | 0 |  | 3060.5 | 3200.5 | 123.8095 | 0 | 143.7118 | 0 | 1.2381 | 0 | 1.4371 | 0 | 1.2381 | 1.4371 | 17.7209 | 1.418 | 16.4828
38961.3761 | 2240 | 0 | 38961.3761 | 1892 | 0 |  | 3102.5 | 3242.5 | 136.7521 | 0 | 115.5067 | 0 | 1.3675 | 0 | 1.1551 | 0 | 1.3675 | 1.1551 | 6.5795 | 26.1829 | 5.2119
38961.3766 | 1771 | 0 | 38961.3766 | 2089 | 0 |  | 3144.5 | 3284.5 | 108.1197 | 0 | 127.5336 | 0 | 1.0812 | 0 | 1.2753 | 0 | 1.0812 | 1.2753 | 34.8041 | 14.2834 | 33.7229
38961.3771 | 2282 | 0 | 38961.3771 | 2064 | 0 |  | 3186.5 | 3326.5 | 139.3162 | 0 | 126.0073 | 0 | 1.3932 | 0 | 1.2601 | 0 | 1.3932 | 1.2601 | 4.6179 | 15.6676 | 3.2247
38961.3775 | 1860 | 0 | 38961.3776 | 1983 | 0 |  | 3228.5 | 3368.5 | 113.5531 | 0 | 121.0623 | 0 | 1.1355 | 0 | 1.2106 | 0 | 1.1355 | 1.2106 | 28.3538 | 20.3923 | 27.2182
38961.378 | 2255 | 0 | 38961.378 | 1844 | 0 |  | 3270.5 | 3410.5 | 137.6679 | 0 | 112.5763 | 0 | 1.3767 | 0 | 1.1258 | 0 | 1.3767 | 1.1258 | 5.8705 | 29.4675 | 4.4938
38961.3785 | 1925 | 0 | 38961.3785 | 2210 | 0 |  | 3312.5 | 3452.5 | 117.5214 | 0 | 134.9206 | 0 | 1.1752 | 0 | 1.3492 | 0 | 1.1752 | 1.3492 | 24.0197 | 8.0262 | 22.8445
38961.379 | 2252 | 0 | 38961.379 | 2058 | 0 |  | 3354.5 | 3494.5 | 137.4847 | 0 | 125.641 | 0 | 1.3748 | 0 | 1.2564 | 0 | 1.3748 | 1.2564 | 6.0115 | 16.0049 | 4.6367
38961.3795 | 2105 | 0 | 38961.3795 | 2333 | 0 |  | 3396.5 | 3536.5 | 128.5104 | 0 | 142.4298 | 0 | 1.2851 | 0 | 1.4243 | 0 | 1.2851 | 1.4243 | 13.4147 | 2.3309 | 12.1296
38961.38 | 2138 | 0 | 38961.38 | 2278 | 0 |  | 3438.5 | 3578.5 | 130.525 | 0 | 139.072 | 0 | 1.3053 | 0 | 1.3907 | 0 | 1.3053 | 1.3907 | 11.6642 | 4.8016 | 10.3589
38961.3805 | 2237 | 0 | 38961.3805 | 2299 | 0 |  | 3480.5 | 3620.5 | 136.569 | 0 | 140.3541 | 0 | 1.3657 | 0 | 1.4035 | 0 | 1.3657 | 1.4035 | 6.7224 | 3.8443 | 5.3567

## A1-B4
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 145.6886 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38961.3386 | 1 | 0 | 38961.3386 | 1 | 0 |  | -134 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3391 | 1 | 0 | 38961.3391 | 1 | 0 |  | -92 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3396 | 1 | 0 | 38961.3396 | 1 | 0 |  | -50 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3401 | 1 | 0 | 38961.3401 | 1 | 0 |  | -8 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3406 | 1 | 0 | 38961.3406 | 1 | 0 |  | 34 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3411 | 1 | 0 | 38961.3411 | 1 | 0 |  | 76 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3415 | 1 | 0 | 38961.3416 | 1 | 0 |  | 118 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.342 | 1 | 1 | 38961.342 | 1 | 0 |  | 160 | 300 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 569003774.44 | 238538 | 238338.0838
38961.3425 | 1 | 0 | 38961.3425 | 2 | 0 |  | 202 | 342 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 238538 | 119219 | 238537.9994
38961.343 | 1 | 0 | 38961.343 | 1 | 0 |  | 244 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3435 | 1 | 0 | 38961.3435 | 1 | 0 |  | 286 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.344 | 1 | 0 | 38961.344 | 1 | 0 |  | 328 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3445 | 1 | 0 | 38961.3445 | 1 | 0 |  | 370 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3449 | 1 | 0 | 38961.345 | 1 | 0 |  | 412 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3454 | 1 | 0 | 38961.3455 | 1 | 0 |  | 454 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3459 | 1 | 0 | 38961.3459 | 1 | 0 |  | 496 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3464 | 1 | 0 | 38961.3464 | 1 | 0 |  | 538 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3469 | 1 | 0 | 38961.3469 | 1 | 0 |  | 580 | 720 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3474 | 1 | 0 | 38961.3474 | 1 | 0 |  | 622 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3479 | 1 | 0 | 38961.3479 | 1 | 0 |  | 664 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3483 | 1 | 0 | 38961.3484 | 1 | 0 |  | 706 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3488 | 1 | 0 | 38961.3489 | 1 | 0 |  | 748 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3493 | 1 | 0 | 38961.3493 | 1 | 0 |  | 790 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3498 | 1 | 0 | 38961.3498 | 1 | 0 |  | 832 | 972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3503 | 1 | 0 | 38961.3503 | 1 | 0 |  | 874 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3508 | 1 | 0 | 38961.3508 | 1 | 0 |  | 916 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3513 | 1 | 0 | 38961.3513 | 1 | 0 |  | 958 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3517 | 1 | 0 | 38961.3518 | 1 | 0 |  | 1000 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3522 | 1 | 0 | 38961.3523 | 1 | 0 |  | 1042 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3527 | 1 | 0 | 38961.3527 | 1 | 0 |  | 1084 | 1224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3532 | 1 | 0 | 38961.3532 | 1 | 0 |  | 1126 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3537 | 1 | 0 | 38961.3537 | 1 | 0 |  | 1168 | 1308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3542 | 1 | 0 | 38961.3542 | 1 | 0 |  | 1210 | 1350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3547 | 1 | 0 | 38961.3547 | 1 | 0 |  | 1252 | 1392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3552 | 1 | 0 | 38961.3552 | 1 | 0 |  | 1294 | 1434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3556 | 1 | 0 | 38961.3557 | 1 | 0 |  | 1336 | 1476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3561 | 1 | 0 | 38961.3561 | 1 | 0 |  | 1378 | 1518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3566 | 1 | 0 | 38961.3566 | 1 | 0 |  | 1420 | 1560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3571 | 1 | 0 | 38961.3571 | 1 | 0 |  | 1462 | 1602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3576 | 1 | 0 | 38961.3576 | 1 | 0 |  | 1504 | 1644 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38961.3581 | 2 | 0 | 38961.3581 | 1 | 0 |  | 1546 | 1686 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119219 | 238538 | 119218.9988
38961.3586 | 2 | 1 | 38961.3586 | 2 | 0 |  | 1588 | 1728 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 238638.1679 | 119219 | 238138.2514
38961.359 | 2 | 0 | 38961.3591 | 2 | 0 |  | 1630 | 1770 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3595 | 2 | 0 | 38961.3595 | 2 | 0 |  | 1672 | 1812 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.36 | 2 | 0 | 38961.36 | 2 | 0 |  | 1714 | 1854 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3605 | 2 | 0 | 38961.3605 | 2 | 0 |  | 1756 | 1896 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.361 | 2 | 0 | 38961.361 | 2 | 0 |  | 1798 | 1938 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3615 | 2 | 0 | 38961.3615 | 1 | 0 |  | 1840 | 1980 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119219 | 238538 | 119218.9988
38961.362 | 2 | 0 | 38961.362 | 2 | 0 |  | 1882 | 2022 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3624 | 2 | 0 | 38961.3625 | 2 | 0 |  | 1924 | 2064 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3629 | 2 | 0 | 38961.363 | 2 | 0 |  | 1966 | 2106 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3634 | 2 | 0 | 38961.3634 | 2 | 0 |  | 2007.5 | 2147.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3639 | 2 | 1 | 38961.3639 | 2 | 0 |  | 2050 | 2190 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 238638.1679 | 119219 | 238138.2514
38961.3644 | 2 | 0 | 38961.3644 | 2 | 0 |  | 2091.5 | 2231.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3649 | 2 | 0 | 38961.3649 | 2 | 0 |  | 2133.5 | 2273.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3654 | 2 | 0 | 38961.3654 | 2 | 0 |  | 2175.5 | 2315.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 119219 | 119219 | 119218.9988
38961.3658 | 2 | 0 | 38961.3659 | 3 | 0 |  | 2218 | 2358 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 119219 | 79446 | 119218.9988
38961.3663 | 37 | 23 | 38961.3664 | 22 | 1 |  | 2260 | 2400 | 2.2589 | 1.4042 | 1.3431 | 0.06105 | 0.022589 | 0.014042 | 0.013431 | 0.0006105 | 0.008547 | 0.012821 | 17029.7063 | 11262.1015 | 10025.6743
38961.3668 | 971 | 885 | 38961.3668 | 927 | 838 |  | 2301.5 | 2441.5 | 59.2796 | 54.0293 | 56.5934 | 51.16 | 0.5928 | 0.54029 | 0.56593 | 0.5116 | 0.052503 | 0.054335 | 2832.4768 | 2456.2655 | 57.5855
38961.3673 | 1185 | 1083 | 38961.3673 | 955 | 915 |  | 2344 | 2484 | 72.3443 | 66.1172 | 58.3028 | 55.8608 | 0.72344 | 0.66117 | 0.58303 | 0.55861 | 0.062271 | 0.02442 | 709.662 | 1609.4744 | 10.2913
38961.3678 | 1107 | 1060 | 38961.3678 | 1143 | 1081 |  | 2386 | 2526 | 67.5824 | 64.7131 | 69.7802 | 65.9951 | 0.67582 | 0.64713 | 0.6978 | 0.65995 | 0.028694 | 0.037851 | 6110.2452 | 4067.2674 | 20.1996
38961.3683 | 1265 | 857 | 38961.3683 | 1046 | 928 |  | 2427.5 | 2567.5 | 77.2283 | 52.3199 | 63.8584 | 56.6545 | 0.77228 | 0.5232 | 0.63858 | 0.56654 | 0.24908 | 0.072039 | 158.7843 | 287.3634 | 22.8855
38961.3688 | 932 | 890 | 38961.3688 | 1202 | 1092 |  | 2470 | 2610 | 56.8987 | 54.3346 | 73.3822 | 66.6667 | 0.56899 | 0.54335 | 0.73382 | 0.66667 | 0.025641 | 0.067155 | 1558.8046 | 1734.8597 | 59.9574
38961.3692 | 1968 | 196 | 38961.3693 | 1813 | 172 |  | 2511.5 | 2651.5 | 120.1465 | 11.9658 | 110.6838 | 10.5006 | 1.2015 | 0.11966 | 1.1068 | 0.10501 | 1.0818 | 1.0018 | 29.6919 | 54.0049 | 39.7867
38961.3697 | 1892 | 145 | 38961.3697 | 2087 | 146 |  | 2553.5 | 2693.5 | 115.5067 | 8.8523 | 127.4115 | 8.9133 | 1.1551 | 0.088523 | 1.2741 | 0.089133 | 1.0665 | 1.185 | 52.5051 | 18.0031 | 36.7608
38961.3702 | 1824 | 111 | 38961.3702 | 1964 | 98 |  | 2595.5 | 2735.5 | 111.3553 | 6.7766 | 119.9023 | 5.9829 | 1.1136 | 0.067766 | 1.199 | 0.059829 | 1.0458 | 1.1392 | 43.8914 | 25.7122 | 83.1728
38961.3707 | 1928 | 97 | 38961.3707 | 1875 | 77 |  | 2637.5 | 2777.5 | 117.7045 | 5.9219 | 114.4689 | 4.7009 | 1.177 | 0.059219 | 1.1447 | 0.047009 | 1.1178 | 1.0977 | 29.7845 | 33.2178 | 92.8968
38961.3712 | 2048 | 80 | 38961.3712 | 2186 | 74 |  | 2679.5 | 2819.5 | 125.0305 | 4.884 | 133.4554 | 4.5177 | 1.2503 | 0.04884 | 1.3346 | 0.045177 | 1.2015 | 1.2894 | 27.4569 | 10.8755 | 31.6799
38961.3717 | 1949 | 64 | 38961.3717 | 2222 | 63 |  | 2721.5 | 2861.5 | 118.9866 | 3.9072 | 135.6532 | 3.8462 | 1.1899 | 0.039072 | 1.3565 | 0.038462 | 1.1508 | 1.3181 | 39.5296 | 8.2205 | 44.3161
38961.3722 | 1906 | 55 | 38961.3722 | 2160 | 51 |  | 2763.5 | 2903.5 | 116.3614 | 3.3578 | 131.8681 | 3.1136 | 1.1636 | 0.033578 | 1.3187 | 0.031136 | 1.13 | 1.2875 | 34.9609 | 11.5316 | 79.9663
38961.3727 | 1774 | 48 | 38961.3727 | 2341 | 50 |  | 2805.5 | 2945.5 | 108.3028 | 2.9304 | 142.9182 | 3.0525 | 1.083 | 0.029304 | 1.4292 | 0.030525 | 1.0537 | 1.3987 | 80.2405 | 4.9854 | 55.8339
38961.3731 | 1801 | 41 | 38961.3731 | 2127 | 40 |  | 2847.5 | 2987.5 | 109.9512 | 2.5031 | 129.8535 | 2.442 | 1.0995 | 0.025031 | 1.2985 | 0.02442 | 1.0745 | 1.2741 | 40.4904 | 13.0459 | 153.2278
38961.3736 | 1850 | 39 | 38961.3736 | 2344 | 31 |  | 2889.5 | 3029.5 | 112.9426 | 2.381 | 143.1013 | 1.8926 | 1.1294 | 0.02381 | 1.431 | 0.018926 | 1.1056 | 1.4121 | 159.9396 | 2.6429 | 32.8383
38961.3741 | 2130 | 44 | 38961.3741 | 2228 | 35 |  | 2931.5 | 3071.5 | 130.0366 | 2.6862 | 136.0195 | 2.1368 | 1.3004 | 0.026862 | 1.3602 | 0.021368 | 1.2735 | 1.3388 | 16.7026 | 7.9851 | 35.6924
38961.3746 | 1947 | 36 | 38961.3746 | 2363 | 35 |  | 2973.5 | 3113.5 | 118.8645 | 2.1978 | 144.2613 | 2.1368 | 1.1886 | 0.021978 | 1.4426 | 0.021368 | 1.1667 | 1.4212 | 23.0334 | 1051.481 | 1023.1905
38961.3751 | 1850 | 33 | 38961.3751 | 1848 | 27 |  | 3015.5 | 3155.5 | 112.9426 | 2.0147 | 112.8205 | 1.6484 | 1.1294 | 0.020147 | 1.1282 | 0.016484 | 1.1093 | 1.1117 | 31.3552 | 31.0325 | 361.2601
38961.3756 | 2147 | 36 | 38961.3756 | 2189 | 32 |  | 3057.5 | 3197.5 | 131.0745 | 2.1978 | 133.6386 | 1.9536 | 1.3107 | 0.021978 | 1.3364 | 0.019536 | 1.2888 | 1.3168 | 13.5972 | 10.2713 | 52.6224
38961.3761 | 1932 | 31 | 38961.3761 | 2297 | 32 |  | 3099.5 | 3239.5 | 117.9487 | 1.8926 | 140.232 | 1.9536 | 1.1795 | 0.018926 | 1.4023 | 0.019536 | 1.1606 | 1.3828 | 39.7411 | 4.0916 | 53.6841
38961.3765 | 2242 | 38 | 38961.3766 | 2370 | 35 |  | 3141.5 | 3281.5 | 136.8742 | 2.3199 | 144.6886 | 2.1368 | 1.3687 | 0.023199 | 1.4469 | 0.021368 | 1.3455 | 1.4255 | 1.9665 | 0.7396 | 2.0553
38961.377 | 1913 | 34 | 38961.377 | 2146 | 34 |  | 3183.5 | 3323.5 | 116.7888 | 2.0757 | 131.0134 | 2.0757 | 1.1679 | 0.020757 | 1.3101 | 0.020757 | 1.1471 | 1.2894 | 29.6513 | 12.035 | 138.821
38961.3775 | 1847 | 31 | 38961.3775 | 2358 | 35 |  | 3225.5 | 3365.5 | 112.7595 | 1.8926 | 143.956 | 2.1368 | 1.1276 | 0.018926 | 1.4396 | 0.021368 | 1.1087 | 1.4182 | 69.4635 | 2.9822 | 47.4897
38961.378 | 2291 | 38 | 38961.378 | 2249 | 32 |  | 3267.5 | 3407.5 | 139.8657 | 2.3199 | 137.3016 | 1.9536 | 1.3987 | 0.023199 | 1.373 | 0.019536 | 1.3755 | 1.3535 | 5.2769 | 8.5298 | 11.8678
38961.3785 | 1950 | 28 | 38961.3785 | 2364 | 24 |  | 3309.5 | 3449.5 | 119.0476 | 1.7094 | 144.3223 | 1.4652 | 1.1905 | 0.017094 | 1.4432 | 0.014652 | 1.1734 | 1.4286 | 40.4085 | 3.3251 | 46.936
38961.379 | 2250 | 31 | 38961.379 | 2327 | 28 |  | 3351.5 | 3491.5 | 137.3626 | 1.8926 | 142.0635 | 1.7094 | 1.3736 | 0.018926 | 1.4206 | 0.017094 | 1.3547 | 1.4035 | 11.9518 | 2.8759 | 9.503
38961.3795 | 2202 | 27 | 38961.3795 | 1935 | 22 |  | 3393.5 | 3533.5 | 134.4322 | 1.6484 | 118.1319 | 1.3431 | 1.3443 | 0.016484 | 1.1813 | 0.013431 | 1.3278 | 1.1679 | 8.8841 | 27.1039 | 124.2965
38961.3799 | 2115 | 27 | 38961.38 | 2345 | 23 |  | 3435.5 | 3575.5 | 129.1209 | 1.6484 | 143.1624 | 1.4042 | 1.2912 | 0.016484 | 1.4316 | 0.014042 | 1.2747 | 1.4176 | 44.7484 | 1.8224 | 16.1997
38961.3804 | 2029 | 26 | 38961.3804 | 2041 | 22 |  | 3477.5 | 3617.5 | 123.8706 | 1.5873 | 124.6032 | 1.3431 | 1.2387 | 0.015873 | 1.246 | 0.013431 | 1.2228 | 1.2326 | 19.2178 | 18.1347 | 195.6529

## A1-B3
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 143.7961 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38961.3386 | 1 | 0 | 38961.3386 | 1 | 0 |  | -136.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3391 | 1 | 0 | 38961.3391 | 1 | 0 |  | -94.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3396 | 1 | 0 | 38961.3396 | 1 | 0 |  | -52.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3401 | 1 | 0 | 38961.3401 | 1 | 0 |  | -10.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3405 | 1 | 0 | 38961.3406 | 1 | 0 |  | 31.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.341 | 1 | 0 | 38961.341 | 1 | 0 |  | 73.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3415 | 1 | 0 | 38961.3415 | 1 | 0 |  | 115.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.342 | 1 | 0 | 38961.342 | 1 | 0 |  | 157.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3425 | 1 | 0 | 38961.3425 | 1 | 0 |  | 199.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.343 | 1 | 0 | 38961.343 | 1 | 0 |  | 241.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3435 | 1 | 0 | 38961.3435 | 1 | 0 |  | 283.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3439 | 1 | 0 | 38961.344 | 1 | 0 |  | 325.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3444 | 1 | 0 | 38961.3444 | 1 | 0 |  | 367.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3449 | 1 | 0 | 38961.3449 | 1 | 0 |  | 409.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3454 | 1 | 0 | 38961.3454 | 1 | 0 |  | 451.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3459 | 1 | 1 | 38961.3459 | 1 | 0 |  | 493.5 | 633.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 554310518.44 | 235438 | 235238.0849
38961.3464 | 1 | 0 | 38961.3464 | 1 | 0 |  | 535.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3469 | 1 | 0 | 38961.3469 | 1 | 0 |  | 577.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3473 | 1 | 0 | 38961.3474 | 1 | 0 |  | 619.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3478 | 1 | 0 | 38961.3478 | 1 | 0 |  | 661 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3483 | 1 | 0 | 38961.3483 | 1 | 0 |  | 703 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3488 | 1 | 0 | 38961.3488 | 1 | 0 |  | 745 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3493 | 1 | 0 | 38961.3493 | 1 | 0 |  | 787 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3498 | 1 | 0 | 38961.3498 | 1 | 0 |  | 829.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3503 | 1 | 0 | 38961.3503 | 1 | 0 |  | 871.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3507 | 1 | 0 | 38961.3508 | 1 | 0 |  | 913 | 1053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3512 | 1 | 0 | 38961.3512 | 1 | 0 |  | 955.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3517 | 1 | 0 | 38961.3517 | 1 | 0 |  | 997 | 1137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3522 | 1 | 0 | 38961.3522 | 1 | 0 |  | 1039 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3527 | 1 | 2 | 38961.3527 | 1 | 1 |  | 1081 | 1221 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 235437.9151 | 554310318.3778 | 117618.9788
38961.3532 | 1 | 0 | 38961.3532 | 1 | 0 |  | 1123 | 1263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3537 | 1 | 0 | 38961.3537 | 1 | 0 |  | 1165 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3541 | 1 | 0 | 38961.3542 | 1 | 0 |  | 1207 | 1347 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3546 | 1 | 0 | 38961.3547 | 1 | 0 |  | 1249 | 1389 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3551 | 1 | 0 | 38961.3551 | 1 | 0 |  | 1291 | 1431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3556 | 1 | 2 | 38961.3556 | 1 | 1 |  | 1333 | 1473 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 235437.9151 | 554310318.3778 | 117618.9788
38961.3561 | 2 | 1 | 38961.3561 | 1 | 1 |  | 1375 | 1515 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 235337.9575 | 554074980.273 | 235237.9575
38961.3566 | 1 | 0 | 38961.3566 | 1 | 0 |  | 1417 | 1557 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3571 | 1 | 0 | 38961.3571 | 1 | 0 |  | 1459 | 1599 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.3575 | 1 | 0 | 38961.3576 | 1 | 0 |  | 1501 | 1641 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235437.9994
38961.358 | 2 | 1 | 38961.3581 | 2 | 0 |  | 1543 | 1683 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235538.1701 | 117669 | 235038.2547
38961.3585 | 2 | 2 | 38961.3585 | 2 | 1 |  | 1585 | 1725 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 276919771.22 | 235337.915 | 117519.0637
38961.359 | 2 | 0 | 38961.359 | 2 | 0 |  | 1627 | 1767 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117669 | 117669 | 117668.9988
38961.3595 | 2 | 0 | 38961.3595 | 2 | 0 |  | 1669 | 1809 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117669 | 117669 | 117668.9988
38961.36 | 2 | 0 | 38961.36 | 2 | 0 |  | 1711 | 1851 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117669 | 117669 | 117668.9988
38961.3605 | 3 | 0 | 38961.3605 | 2 | 0 |  | 1753 | 1893 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 78412.6667 | 117669 | 78412.6648
38961.3609 | 2 | 0 | 38961.361 | 2 | 0 |  | 1795 | 1935 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117669 | 117669 | 117668.9988
38961.3614 | 2 | 0 | 38961.3615 | 2 | 0 |  | 1837 | 1977 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117669 | 117669 | 117668.9988
38961.3619 | 2 | 1 | 38961.3619 | 2 | 0 |  | 1879 | 2019 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235538.1701 | 117669 | 235038.2547
38961.3624 | 2 | 1 | 38961.3624 | 2 | 1 |  | 1921 | 2061 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235138.1274
38961.3629 | 2 | 2 | 38961.3629 | 2 | 1 |  | 1963 | 2103 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 276919771.22 | 235337.915 | 117519.0637
38961.3634 | 2 | 2 | 38961.3634 | 2 | 1 |  | 2005 | 2145 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 276919771.22 | 235337.915 | 117519.0637
38961.3639 | 2 | 2 | 38961.3639 | 2 | 1 |  | 2047 | 2187 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 276919771.22 | 235337.915 | 117519.0637
38961.3644 | 2 | 1 | 38961.3644 | 2 | 1 |  | 2089 | 2229 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235138.1274
38961.3648 | 2 | 2 | 38961.3649 | 2 | 1 |  | 2131 | 2271 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 276919771.22 | 235337.915 | 117519.0637
38961.3653 | 2 | 1 | 38961.3653 | 2 | 1 |  | 2173 | 2313 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 235438 | 235438 | 235138.1274
38961.3658 | 2 | 2 | 38961.3658 | 2 | 1 |  | 2215 | 2355 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 276919771.22 | 235337.915 | 117519.0637
38961.3663 | 2 | 2 | 38961.3663 | 5 | 1 |  | 2257 | 2397 | 0.1221 | 0.1221 | 0.30525 | 0.06105 | 0.001221 | 0.001221 | 0.0030525 | 0.0006105 | 0 | 0.002442 | 69141691.055 | 58759.4788 | 117369.2548
38961.3668 | 990 | 967 | 38961.3668 | 1122 | 1016 |  | 2299 | 2439 | 60.4396 | 59.0354 | 68.4982 | 62.0269 | 0.6044 | 0.59035 | 0.68498 | 0.62027 | 0.014042 | 0.064713 | 946.3376 | 797.3257 | 36.6064
38961.3673 | 1172 | 1100 | 38961.3673 | 1042 | 940 |  | 2341 | 2481 | 71.5507 | 67.1551 | 63.6142 | 57.3871 | 0.71551 | 0.67155 | 0.63614 | 0.57387 | 0.043956 | 0.062271 | 2949.698 | 3450.2966 | 7.3665
38961.3678 | 1117 | 998 | 38961.3678 | 1158 | 1025 |  | 2383 | 2523 | 68.1929 | 60.928 | 70.696 | 62.5763 | 0.68193 | 0.60928 | 0.70696 | 0.62576 | 0.07265 | 0.081197 | 4714.4871 | 1076.2144 | 22.0384
38961.3682 | 1188 | 594 | 38961.3683 | 1767 | 487 |  | 2425 | 2565 | 72.5275 | 36.2637 | 107.8755 | 29.7314 | 0.72527 | 0.36264 | 1.0788 | 0.29731 | 0.36264 | 0.78144 | 96.7779 | 97.0197 | 47.5342
38961.3687 | 1270 | 968 | 38961.3688 | 1105 | 1057 |  | 2467 | 2607 | 77.5336 | 59.0965 | 67.4603 | 64.5299 | 0.77534 | 0.59096 | 0.6746 | 0.6453 | 0.18437 | 0.029304 | 100.8488 | 125.025 | 6.7373
38961.3692 | 2009 | 227 | 38961.3692 | 2146 | 210 |  | 2509 | 2649 | 122.6496 | 13.8584 | 131.0134 | 12.8205 | 1.2265 | 0.13858 | 1.3101 | 0.12821 | 1.0879 | 1.1819 | 37.4566 | 26.48 | 11.0104
38961.3697 | 1702 | 148 | 38961.3697 | 2025 | 152 |  | 2551 | 2691 | 103.9072 | 9.0354 | 123.6264 | 9.2796 | 1.0391 | 0.090354 | 1.2363 | 0.092796 | 0.94872 | 1.1435 | 81.8638 | 19.5801 | 55.9129
38961.3702 | 2138 | 141 | 38961.3702 | 1759 | 98 |  | 2593 | 2733 | 130.525 | 8.6081 | 107.3871 | 5.9829 | 1.3053 | 0.086081 | 1.0739 | 0.059829 | 1.2192 | 1.014 | 12.1056 | 70.0421 | 22.3133
38961.3707 | 1948 | 104 | 38961.3707 | 1859 | 84 |  | 2635 | 2775 | 118.9255 | 6.3492 | 113.4921 | 5.1282 | 1.1893 | 0.063492 | 1.1349 | 0.051282 | 1.1258 | 1.0836 | 26.4777 | 34.0511 | 74.0993
38961.3712 | 2096 | 93 | 38961.3712 | 2186 | 83 |  | 2677 | 2817 | 127.9609 | 5.6777 | 133.4554 | 5.0672 | 1.2796 | 0.056777 | 1.3346 | 0.050672 | 1.2228 | 1.2839 | 25.2036 | 9.5496 | 15.5953
38961.3716 | 2204 | 86 | 38961.3717 | 1817 | 63 |  | 2719 | 2859 | 134.5543 | 5.2503 | 110.928 | 3.8462 | 1.3455 | 0.052503 | 1.1093 | 0.038462 | 1.293 | 1.0708 | 7.6894 | 57.6001 | 27.7852
38961.3721 | 1954 | 66 | 38961.3722 | 1887 | 54 |  | 2761 | 2901 | 119.2918 | 4.0293 | 115.2015 | 3.2967 | 1.1929 | 0.040293 | 1.152 | 0.032967 | 1.1526 | 1.119 | 24.162 | 29.1008 | 114.5432
38961.3726 | 1751 | 55 | 38961.3726 | 2305 | 59 |  | 2803 | 2943 | 106.8987 | 3.3578 | 140.7204 | 3.602 | 1.069 | 0.033578 | 1.4072 | 0.03602 | 1.0354 | 1.3712 | 71.4278 | 6.4717 | 60.7144
38961.3731 | 2198 | 64 | 38961.3731 | 2320 | 56 |  | 2845 | 2985 | 134.188 | 3.9072 | 141.6361 | 3.4188 | 1.3419 | 0.039072 | 1.4164 | 0.034188 | 1.3028 | 1.3822 | 2.8591 | 1.8989 | 2.7189
38961.3736 | 1778 | 47 | 38961.3736 | 1809 | 40 |  | 2887 | 3027 | 108.547 | 2.8694 | 110.4396 | 2.442 | 1.0855 | 0.028694 | 1.1044 | 0.02442 | 1.0568 | 1.08 | 36.3522 | 32.935 | 279.5809
38961.3741 | 1910 | 46 | 38961.3741 | 2118 | 42 |  | 2929 | 3069 | 116.6056 | 2.8083 | 129.304 | 2.5641 | 1.1661 | 0.028083 | 1.293 | 0.025641 | 1.138 | 1.2674 | 29.913 | 12.2639 | 94.8458
38961.3746 | 1963 | 47 | 38961.3746 | 1995 | 38 |  | 2971 | 3111 | 119.8413 | 2.8694 | 121.7949 | 2.3199 | 1.1984 | 0.028694 | 1.2179 | 0.023199 | 1.1697 | 1.1947 | 23.328 | 20.0869 | 122.9183
38961.375 | 2155 | 48 | 38961.3751 | 1976 | 37 |  | 3013 | 3153 | 131.5629 | 2.9304 | 120.6349 | 2.2589 | 1.3156 | 0.029304 | 1.2063 | 0.022589 | 1.2863 | 1.1838 | 10.512 | 23.9052 | 61.2476
38961.3755 | 2098 | 45 | 38961.3756 | 2072 | 39 |  | 3055 | 3195 | 128.083 | 2.7473 | 126.4957 | 2.381 | 1.2808 | 0.027473 | 1.265 | 0.02381 | 1.2534 | 1.2411 | 14.5181 | 16.0613 | 65.3121
38961.376 | 1928 | 40 | 38961.376 | 2283 | 42 |  | 3097 | 3237 | 117.7045 | 2.442 | 139.3773 | 2.5641 | 1.177 | 0.02442 | 1.3938 | 0.025641 | 1.1526 | 1.3681 | 62.2243 | 3.3301 | 31.2111
38961.3765 | 1816 | 41 | 38961.3765 | 2311 | 41 |  | 3138.5 | 3278.5 | 110.8669 | 2.5031 | 141.0867 | 2.5031 | 1.1087 | 0.025031 | 1.4109 | 0.025031 | 1.0836 | 1.3858 | 155.6901 | 2.87 | 33.9137
38961.377 | 1817 | 43 | 38961.377 | 2154 | 44 |  | 3181 | 3321 | 110.928 | 2.6252 | 131.5018 | 2.6862 | 1.1093 | 0.026252 | 1.315 | 0.026862 | 1.083 | 1.2882 | 39.9699 | 10.0694 | 105.392
38961.3775 | 1776 | 42 | 38961.3775 | 2339 | 36 |  | 3223 | 3363 | 108.4249 | 2.5641 | 142.7961 | 2.1978 | 1.0842 | 0.025641 | 1.428 | 0.021978 | 1.0586 | 1.406 | 11.6772 | 1.3013 | 16.4355
38961.378 | 2071 | 43 | 38961.378 | 2132 | 40 |  | 3265 | 3405 | 126.4347 | 2.6252 | 130.1587 | 2.442 | 1.2643 | 0.026252 | 1.3016 | 0.02442 | 1.2381 | 1.2772 | 17.0234 | 12.0289 | 60.2738
38961.3784 | 1910 | 36 | 38961.3785 | 2168 | 36 |  | 3307 | 3447 | 116.6056 | 2.1978 | 132.3565 | 2.1978 | 1.1661 | 0.021978 | 1.3236 | 0.021978 | 1.1441 | 1.3016 | 29.9416 | 9.3142 | 96.8932
38961.3789 | 2251 | 42 | 38961.3789 | 2301 | 39 |  | 3348.5 | 3488.5 | 137.4237 | 2.5641 | 140.4762 | 2.381 | 1.3742 | 0.025641 | 1.4048 | 0.02381 | 1.3486 | 1.381 | 16.0747 | 2.6929 | 3.8947
38961.3794 | 2249 | 32 | 38961.3794 | 2323 | 35 |  | 3391 | 3531 | 137.3016 | 1.9536 | 141.8193 | 2.1368 | 1.373 | 0.019536 | 1.4182 | 0.021368 | 1.3535 | 1.3968 | 162.6107 | 1.4873 | 3.4063
38961.3799 | 2206 | 40 | 38961.3799 | 1991 | 31 |  | 3432.5 | 3572.5 | 134.6764 | 2.442 | 121.5507 | 1.8926 | 1.3468 | 0.02442 | 1.2155 | 0.018926 | 1.3223 | 1.1966 | 7.4828 | 23.5736 | 52.1648
38961.3804 | 2229 | 38 | 38961.3804 | 1927 | 30 |  | 3474.5 | 3614.5 | 136.0806 | 2.3199 | 117.6435 | 1.8315 | 1.3608 | 0.023199 | 1.1764 | 0.018315 | 1.3376 | 1.1581 | 6.1164 | 30.4568 | 54.2984

## A1-A2
Penlight Test 50 |  |  | 2006-09-01 | 8:09 |  |  | Vs = |  | 136.8974 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38961.3386 | 1 | 0 | 38961.3386 | 1 | 0 |  | -139.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3391 | 1 | 0 | 38961.3391 | 1 | 0 |  | -97.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3395 | 1 | 0 | 38961.3395 | 1 | 0 |  | -55.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.34 | 1 | 0 | 38961.34 | 1 | 0 |  | -13.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3405 | 1 | 0 | 38961.3405 | 1 | 0 |  | 28.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.341 | 1 | 0 | 38961.341 | 1 | 0 |  | 70.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3415 | 1 | 0 | 38961.3415 | 1 | 0 |  | 112.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.342 | 1 | 0 | 38961.342 | 1 | 0 |  | 154.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3425 | 1 | 0 | 38961.3425 | 1 | 0 |  | 196.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3429 | 1 | 0 | 38961.343 | 1 | 0 |  | 238.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3434 | 1 | 0 | 38961.3434 | 1 | 0 |  | 280.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3439 | 1 | 0 | 38961.3439 | 1 | 0 |  | 322.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3444 | 1 | 0 | 38961.3444 | 1 | 0 |  | 364.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3449 | 1 | 0 | 38961.3449 | 1 | 0 |  | 406.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3454 | 1 | 0 | 38961.3454 | 1 | 0 |  | 448.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3459 | 1 | 0 | 38961.3459 | 1 | 0 |  | 490.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3463 | 1 | 0 | 38961.3464 | 1 | 0 |  | 532.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3468 | 1 | 0 | 38961.3468 | 1 | 0 |  | 574.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3473 | 1 | 0 | 38961.3473 | 1 | 0 |  | 616.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3478 | 1 | 0 | 38961.3478 | 1 | 0 |  | 658.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3483 | 1 | 0 | 38961.3483 | 1 | 0 |  | 700.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3488 | 1 | 0 | 38961.3488 | 1 | 0 |  | 742.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3493 | 2 | 0 | 38961.3493 | 1 | 0 |  | 784.5 | 924.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 112019 | 224138 | 112018.9988
38961.3497 | 1 | 0 | 38961.3498 | 1 | 0 |  | 826.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3502 | 1 | 0 | 38961.3502 | 1 | 0 |  | 868.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3507 | 1 | 0 | 38961.3507 | 1 | 0 |  | 910.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3512 | 1 | 0 | 38961.3512 | 1 | 0 |  | 952.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3517 | 1 | 0 | 38961.3517 | 1 | 0 |  | 994.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3522 | 1 | 0 | 38961.3522 | 1 | 0 |  | 1036.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3527 | 1062 | 1038 | 38961.3527 | 1148 | 1126 |  | 1078.5 | 1218.5 | 64.8352 | 63.37 | 70.0855 | 68.7424 | 0.64835 | 0.6337 | 0.70085 | 0.68742 | 0.014652 | 0.013431 | 3586.8172 | 11651.3456 | 13.6
38961.3531 | 1 | 0 | 38961.3532 | 1 | 0 |  | 1120.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3536 | 1 | 0 | 38961.3536 | 1 | 0 |  | 1162.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3541 | 1 | 0 | 38961.3541 | 1 | 0 |  | 1204.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3546 | 1 | 0 | 38961.3546 | 1 | 0 |  | 1246.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3551 | 1 | 0 | 38961.3551 | 1 | 0 |  | 1288.5 | 1428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3556 | 1165 | 1147 | 38961.3556 | 1167 | 1099 |  | 1330.5 | 1470.5 | 71.1233 | 70.0244 | 71.2454 | 67.094 | 0.71123 | 0.70024 | 0.71245 | 0.67094 | 0.010989 | 0.041514 | 173.8771 | 190.6515 | 3.9814
38961.3561 | 1017 | 924 | 38961.3561 | 935 | 913 |  | 1372.5 | 1512.5 | 62.0879 | 56.4103 | 57.0818 | 55.7387 | 0.62088 | 0.5641 | 0.57082 | 0.55739 | 0.056777 | 0.013431 | 749.0003 | 1308.7436 | 30.3016
38961.3566 | 31 | 32 | 38961.3566 | 1 | 0 |  | 1414.5 | 1554.5 | 1.8926 | 1.9536 | 0.06105 | 0 | 0.018926 | 0.019536 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224340.8967 | 224138 | 6807.5253
38961.357 | 1 | 0 | 38961.357 | 1 | 0 |  | 1456.5 | 1596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.3575 | 1 | 0 | 38961.3575 | 1 | 0 |  | 1498.5 | 1638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224138 | 224138 | 224137.9994
38961.358 | 942 | 919 | 38961.358 | 1104 | 1155 |  | 1540.5 | 1680.5 | 57.5092 | 56.105 | 67.3993 | 70.5128 | 0.57509 | 0.56105 | 0.67399 | 0.70513 | 0.014042 | 0.031136 | 2024.9266 | 2229.5747 | 39.718
38961.3585 | 1115 | 1090 | 38961.3585 | 956 | 1071 |  | 1582.5 | 1722.5 | 68.0708 | 66.5446 | 58.3639 | 65.3846 | 0.68071 | 0.66545 | 0.58364 | 0.65385 | 0.015263 | 0.070208 | 303.5171 | 314.6299 | 2.6023
38961.359 | 3 | 1 | 38961.359 | 2 | 0 |  | 1624.5 | 1764.5 | 0.18315 | 0.06105 | 0.1221 | 0 | 0.0018315 | 0.0006105 | 0.001221 | 0 | 0.001221 | 0.001221 | 112019 | 112019 | 223638.3568
38961.3595 | 3 | 0 | 38961.3595 | 2 | 0 |  | 1666.5 | 1806.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 74646 | 112019 | 74645.9982
38961.36 | 2 | 0 | 38961.36 | 2 | 0 |  | 1708.5 | 1848.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 112019 | 112019 | 112018.9988
38961.3604 | 242 | 271 | 38961.3605 | 2 | 0 |  | 1750.5 | 1890.5 | 14.7741 | 16.5446 | 0.1221 | 0 | 0.14774 | 0.16545 | 0.001221 | 0 | 0.017705 | 0.001221 | 6955.8894 | 112019 | 637.5784
38961.3609 | 3 | 0 | 38961.3609 | 2 | 0 |  | 1792.5 | 1932.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 74646 | 112019 | 74645.9982
38961.3614 | 27 | 24 | 38961.3614 | 139 | 144 |  | 1834.5 | 1974.5 | 1.6484 | 1.4652 | 8.486 | 8.7912 | 0.016484 | 0.014652 | 0.08486 | 0.087912 | 0.0018315 | 0.0030525 | 75221.7233 | 43742.3553 | 9109.9237
38961.3619 | 6 | 3 | 38961.3619 | 1049 | 1020 |  | 1876.5 | 2016.5 | 0.3663 | 0.18315 | 64.0415 | 62.2711 | 0.003663 | 0.0018315 | 0.64042 | 0.62271 | 0.0018315 | 0.017705 | 76315.0393 | 4313.9256 | 72759.3834
38961.3624 | 929 | 904 | 38961.3624 | 1148 | 1180 |  | 1918.5 | 2058.5 | 56.7155 | 55.1893 | 70.0855 | 72.0391 | 0.56716 | 0.55189 | 0.70085 | 0.72039 | 0.015263 | 0.019536 | 23628.7411 | 4649.8231 | 44.332
38961.3629 | 1131 | 1102 | 38961.3629 | 1151 | 1187 |  | 1960.5 | 2100.5 | 69.0476 | 67.2772 | 70.2686 | 72.4664 | 0.69048 | 0.67277 | 0.70269 | 0.72466 | 0.017705 | 0.021978 | 1185.9428 | 1702.9093 | 0.80397
38961.3633 | 1109 | 1080 | 38961.3634 | 1091 | 1161 |  | 2002 | 2142 | 67.7045 | 65.9341 | 66.6056 | 70.8791 | 0.67705 | 0.65934 | 0.66606 | 0.70879 | 0.017705 | 0.042735 | 120.9929 | 118.9777 | 2.6855
38961.3638 | 1080 | 933 | 38961.3639 | 1019 | 989 |  | 2044.5 | 2184.5 | 65.9341 | 56.9597 | 62.21 | 60.3785 | 0.65934 | 0.5696 | 0.6221 | 0.60379 | 0.089744 | 0.018315 | 328.8151 | 451.8037 | 20.1298
38961.3643 | 1061 | 1028 | 38961.3643 | 1117 | 1084 |  | 2086.5 | 2226.5 | 64.7741 | 62.7595 | 68.1929 | 66.1783 | 0.64774 | 0.62759 | 0.68193 | 0.66178 | 0.020147 | 0.020147 | 6695.0909 | 6695.0909 | 14.7007
38961.3648 | 1204 | 979 | 38961.3648 | 963 | 993 |  | 2128 | 2268 | 73.5043 | 59.768 | 58.7912 | 60.6227 | 0.73504 | 0.59768 | 0.58791 | 0.60623 | 0.13736 | 0.018315 | 137.8525 | 185.3274 | 3.9396
38961.3653 | 956 | 922 | 38961.3653 | 932 | 995 |  | 2170.5 | 2310.5 | 58.3639 | 56.2882 | 56.8987 | 60.7448 | 0.58364 | 0.56288 | 0.56899 | 0.60745 | 0.020757 | 0.038462 | 5676.8794 | 8130.5006 | 39.0404
38961.3658 | 960 | 1064 | 38961.3658 | 977 | 943 |  | 2212 | 2352 | 58.6081 | 64.9573 | 59.6459 | 57.5702 | 0.58608 | 0.64957 | 0.59646 | 0.5757 | 0.063492 | 0.020757 | 649.0496 | 1137.018 | 18.8652
38961.3663 | 1039 | 1000 | 38961.3663 | 1188 | 1149 |  | 2254 | 2394 | 63.431 | 61.0501 | 72.5275 | 70.1465 | 0.63431 | 0.6105 | 0.72527 | 0.70147 | 0.02381 | 0.02381 | 5649.6923 | 5649.6923 | 19.9843
38961.3668 | 1058 | 967 | 38961.3668 | 1222 | 1094 |  | 2296.5 | 2436.5 | 64.591 | 59.0354 | 74.6032 | 66.7888 | 0.64591 | 0.59035 | 0.74603 | 0.66789 | 0.055556 | 0.078144 | 487.1046 | 635.5698 | 19.4237
38961.3672 | 973 | 877 | 38961.3673 | 1078 | 971 |  | 2338 | 2478 | 59.4017 | 53.5409 | 65.812 | 59.2796 | 0.59402 | 0.53541 | 0.65812 | 0.5928 | 0.058608 | 0.065324 | 3491.7615 | 1470.3311 | 41.892
38961.3677 | 1219 | 1139 | 38961.3677 | 1003 | 959 |  | 2380 | 2520 | 74.42 | 69.536 | 61.2332 | 58.547 | 0.7442 | 0.69536 | 0.61233 | 0.58547 | 0.04884 | 0.026862 | 359.0453 | 555.5336 | 8.6025
38961.3682 | 1132 | 1086 | 38961.3682 | 1349 | 1009 |  | 2422.5 | 2562.5 | 69.1087 | 66.3004 | 82.3565 | 61.5995 | 0.69109 | 0.663 | 0.82357 | 0.616 | 0.028083 | 0.20757 | 31.6271 | 31.3434 | 0.53572
38961.3687 | 1472 | 806 | 38961.3687 | 1247 | 586 |  | 2464 | 2604 | 89.8657 | 49.2063 | 76.1294 | 35.7753 | 0.89866 | 0.49206 | 0.76129 | 0.35775 | 0.40659 | 0.40354 | 226.2688 | 247.5971 | 3.148
38961.3692 | 1662 | 246 | 38961.3692 | 1797 | 259 |  | 2506 | 2646 | 101.4652 | 15.0183 | 109.707 | 15.812 | 1.0147 | 0.15018 | 1.0971 | 0.15812 | 0.86447 | 0.93895 | 77.1969 | 37.038 | 36.7377
38961.3697 | 1734 | 212 | 38961.3697 | 1758 | 205 |  | 2548 | 2688 | 105.8608 | 12.9426 | 107.326 | 12.5153 | 1.0586 | 0.12943 | 1.0733 | 0.12515 | 0.92918 | 0.94811 | 49.7044 | 42.4686 | 41.6736
38961.3702 | 1823 | 177 | 38961.3702 | 1742 | 166 |  | 2590 | 2730 | 111.2943 | 10.8059 | 106.3492 | 10.1343 | 1.1129 | 0.10806 | 1.0635 | 0.10134 | 1.0049 | 0.96215 | 33.1331 | 46.5474 | 43.4951
38961.3706 | 2064 | 171 | 38961.3707 | 2146 | 173 |  | 2632 | 2772 | 126.0073 | 10.4396 | 131.0134 | 10.5617 | 1.2601 | 0.1044 | 1.3101 | 0.10562 | 1.1557 | 1.2045 | 7.9973 | 50.668 | 1.4514
38961.3711 | 2047 | 146 | 38961.3711 | 1706 | 122 |  | 2674 | 2814 | 124.9695 | 8.9133 | 104.1514 | 7.4481 | 1.2497 | 0.089133 | 1.0415 | 0.074481 | 1.1606 | 0.96703 | 11.0333 | 112.1532 | 17.8797
38961.3716 | 1801 | 122 | 38961.3716 | 2036 | 138 |  | 2716 | 2856 | 109.9512 | 7.4481 | 124.2979 | 8.4249 | 1.0995 | 0.074481 | 1.243 | 0.084249 | 1.025 | 1.1587 | 64.5951 | 12.2527 | 28.5748
38961.3721 | 2225 | 131 | 38961.3721 | 2104 | 122 |  | 2758 | 2898 | 135.8364 | 7.9976 | 128.4493 | 7.4481 | 1.3584 | 0.079976 | 1.2845 | 0.074481 | 1.2784 | 1.21 | 45.0677 | 6.3733 | 5.1966
38961.3726 | 2064 | 113 | 38961.3726 | 1981 | 106 |  | 2800 | 2940 | 126.0073 | 6.8987 | 120.9402 | 6.4713 | 1.2601 | 0.068987 | 1.2094 | 0.064713 | 1.1911 | 1.1447 | 11.6235 | 27.1408 | 12.351
38961.3731 | 1981 | 101 | 38961.3731 | 1854 | 95 |  | 2842 | 2982 | 120.9402 | 6.1661 | 113.1868 | 5.7998 | 1.2094 | 0.061661 | 1.1319 | 0.057998 | 1.1477 | 1.0739 | 16.6372 | 32.6922 | 39.1226
38961.3736 | 2074 | 109 | 38961.3736 | 2002 | 95 |  | 2884 | 3024 | 126.6178 | 6.6545 | 122.2222 | 5.7998 | 1.2662 | 0.066545 | 1.2222 | 0.057998 | 1.1996 | 1.1642 | 11.3883 | 22.4066 | 9.972
38961.374 | 1911 | 92 | 38961.3741 | 1989 | 91 |  | 2926 | 3066 | 116.6667 | 5.6166 | 121.4286 | 5.5556 | 1.1667 | 0.056166 | 1.2143 | 0.055556 | 1.1105 | 1.1587 | 26.4051 | 16.3116 | 36.49
38961.3745 | 2050 | 94 | 38961.3745 | 2181 | 101 |  | 2968 | 3108 | 125.1526 | 5.7387 | 133.1502 | 6.1661 | 1.2515 | 0.057387 | 1.3315 | 0.061661 | 1.1941 | 1.2698 | 3.0669 | 2.1775 | 2.2304
38961.375 | 2119 | 93 | 38961.375 | 1978 | 84 |  | 3010 | 3150 | 129.3651 | 5.6777 | 120.757 | 5.1282 | 1.2937 | 0.056777 | 1.2076 | 0.051282 | 1.2369 | 1.1563 | 6.9006 | 39.0679 | 9.1769
38961.3755 | 2130 | 92 | 38961.3755 | 2201 | 94 |  | 3052 | 3192 | 130.0366 | 5.6166 | 134.3712 | 5.7387 | 1.3004 | 0.056166 | 1.3437 | 0.057387 | 1.2442 | 1.2863 | 3.6505 | 8.842 | 1.7996
38961.376 | 1886 | 80 | 38961.376 | 2012 | 83 |  | 3094 | 3234 | 115.1404 | 4.884 | 122.8327 | 5.0672 | 1.1514 | 0.04884 | 1.2283 | 0.050672 | 1.1026 | 1.1777 | 28.8305 | 14.0381 | 42.5279
38961.3765 | 2133 | 90 | 38961.3765 | 1893 | 79 |  | 3136 | 3276 | 130.2198 | 5.4945 | 115.5678 | 4.823 | 1.3022 | 0.054945 | 1.1557 | 0.04823 | 1.2473 | 1.1074 | 5.6501 | 84.0265 | 9.8321
38961.377 | 2145 | 94 | 38961.377 | 2057 | 78 |  | 3178 | 3318 | 130.9524 | 5.7387 | 125.58 | 4.7619 | 1.3095 | 0.057387 | 1.2558 | 0.047619 | 1.2521 | 1.2082 | 5.5206 | 32.7467 | 0.88702
38961.3774 | 1788 | 77 | 38961.3775 | 1929 | 82 |  | 3220 | 3360 | 109.1575 | 4.7009 | 117.7656 | 5.0061 | 1.0916 | 0.047009 | 1.1777 | 0.050061 | 1.0446 | 1.1276 | 34.5402 | 19.4695 | 79.8704
38961.3779 | 2104 | 88 | 38961.378 | 2162 | 95 |  | 3262 | 3402 | 128.4493 | 5.3724 | 131.9902 | 5.7998 | 1.2845 | 0.053724 | 1.3199 | 0.057998 | 1.2308 | 1.2619 | 13.9194 | 8.6119 | 4.5394
38961.3784 | 1863 | 74 | 38961.3784 | 2226 | 70 |  | 3304 | 3444 | 113.7363 | 4.5177 | 135.8974 | 4.2735 | 1.1374 | 0.045177 | 1.359 | 0.042735 | 1.0922 | 1.3162 | 0.79411 | 0.16092 | 0.66301
38961.3789 | 1780 | 75 | 38961.3789 | 1976 | 76 |  | 3346 | 3486 | 108.6691 | 4.5788 | 120.6349 | 4.6398 | 1.0867 | 0.045788 | 1.2063 | 0.046398 | 1.0409 | 1.16 | 37.6892 | 15.6846 | 70.0285
38961.3794 | 2023 | 77 | 38961.3794 | 1885 | 70 |  | 3388 | 3528 | 123.5043 | 4.7009 | 115.0794 | 4.2735 | 1.235 | 0.047009 | 1.1508 | 0.042735 | 1.188 | 1.1081 | 13.1386 | 27.872 | 40.3043
38961.3799 | 2088 | 81 | 38961.3799 | 1947 | 73 |  | 3430 | 3570 | 127.4725 | 4.9451 | 118.8645 | 4.4567 | 1.2747 | 0.049451 | 1.1886 | 0.044567 | 1.2253 | 1.1441 | 8.9988 | 27.7931 | 19.7025
38961.3804 | 2000 | 75 | 38961.3804 | 1826 | 71 |  | 3472 | 3612 | 122.1001 | 4.5788 | 111.4774 | 4.3346 | 1.221 | 0.045788 | 1.1148 | 0.043346 | 1.1752 | 1.0714 | 14.2702 | 33.1128 | 55.516

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -140 | 18.4 | 26.4 | 21.8 | 26.1 | 28.1 | 26 | 24.8 | 26.8 | 23.3 | 24.2
1 | -139 | 18.4 | 26.4 | 21.8 | 26.1 | 28.1 | 26 | 24.8 | 26.8 | 23.3 | 24.2
2 | -138 | 18.4 | 26.4 | 21.7 | 26.1 | 28.1 | 26 | 24.8 | 26.8 | 23.3 | 24.2
3 | -137 | 18.4 | 26.3 | 21.8 | 26.1 | 28 | 26 | 24.8 | 26.8 | 23.3 | 24.2
4 | -136 | 18.4 | 26.3 | 21.8 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
5 | -135 | 18.4 | 26.3 | 21.8 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
6 | -134 | 18.4 | 26.3 | 21.8 | 26.1 | 28.1 | 26 | 24.8 | 26.9 | 23.3 | 24.2
7 | -133 | 18.4 | 26.3 | 21.8 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
8 | -132 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
9 | -131 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
10 | -130 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
11 | -129 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
12 | -128 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.8 | 23.3 | 24.2
13 | -127 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 26.8 | 23.3 | 24.2
14 | -126 | 18.4 | 26.2 | 22.1 | 26 | 27.8 | 25.9 | 24.8 | 26.8 | 23.3 | 24.2
15 | -125 | 18.4 | 26.3 | 22 | 26.1 | 27.9 | 26 | 24.8 | 26.8 | 23.3 | 24.2
16 | -124 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.8 | 23.3 | 24.2
17 | -123 | 18.4 | 26.3 | 22 | 26.1 | 27.9 | 26 | 24.8 | 26.8 | 23.3 | 24.2
18 | -122 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
19 | -121 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
20 | -120 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
21 | -119 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
22 | -118 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
23 | -117 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
24 | -116 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
25 | -115 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
26 | -114 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
27 | -113 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
28 | -112 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
29 | -111 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
30 | -110 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 26.9 | 23.3 | 24.2
31 | -109 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
32 | -108 | 18.4 | 26.2 | 22 | 26 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
33 | -107 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
34 | -106 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
35 | -105 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 27 | 23.3 | 24.2
36 | -104 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 27 | 23.3 | 24.2
37 | -103 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
38 | -102 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 27 | 23.3 | 24.2
39 | -101 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
40 | -100 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
41 | -99 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
42 | -98 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
43 | -97 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
44 | -96 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
45 | -95 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 26.9 | 23.3 | 24.2
46 | -94 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 27 | 23.3 | 24.2
47 | -93 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
48 | -92 | 18.4 | 26.3 | 21.9 | 26.1 | 28 | 26 | 24.8 | 27 | 23.3 | 24.2
49 | -91 | 18.4 | 26.2 | 22.1 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
50 | -90 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
51 | -89 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
52 | -88 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
53 | -87 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
54 | -86 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 26.9 | 23.3 | 24.2
55 | -85 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
56 | -84 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
57 | -83 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
58 | -82 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
59 | -81 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 27 | 23.3 | 24.2
60 | -80 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
61 | -79 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
62 | -78 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
63 | -77 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
64 | -76 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
65 | -75 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
66 | -74 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
67 | -73 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
68 | -72 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
69 | -71 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
70 | -70 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27 | 23.3 | 24.2
71 | -69 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
72 | -68 | 18.4 | 26.2 | 22 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
73 | -67 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
74 | -66 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
75 | -65 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
76 | -64 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
77 | -63 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
78 | -62 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
79 | -61 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
80 | -60 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
81 | -59 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
82 | -58 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
83 | -57 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27 | 23.3 | 24.2
84 | -56 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
85 | -55 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27 | 23.3 | 24.2
86 | -54 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27 | 23.3 | 24.2
87 | -53 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
88 | -52 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
89 | -51 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
90 | -50 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
91 | -49 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
92 | -48 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
93 | -47 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
94 | -46 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
95 | -45 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
96 | -44 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
97 | -43 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
98 | -42 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
99 | -41 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
100 | -40 | 18.4 | 26.2 | 21.9 | 26.1 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
101 | -39 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
102 | -38 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
103 | -37 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
104 | -36 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
105 | -35 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27 | 23.3 | 24.2
106 | -34 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
107 | -33 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
108 | -32 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
109 | -31 | 18.4 | 26.3 | 21.9 | 26 | 27.9 | 26 | 24.8 | 27.1 | 23.3 | 24.2
110 | -30 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.2 | 23.3 | 24.2
111 | -29 | 18.4 | 26.3 | 21.9 | 26.1 | 27.9 | 26 | 24.8 | 27.2 | 23.3 | 24.2
112 | -28 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
113 | -27 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
114 | -26 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
115 | -25 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
116 | -24 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
117 | -23 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
118 | -22 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
119 | -21 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
120 | -20 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
121 | -19 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
122 | -18 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
123 | -17 | 18.4 | 26.2 | 21.9 | 26 | 27.9 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
124 | -16 | 18.4 | 26.2 | 21.9 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
125 | -15 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
126 | -14 | 18.4 | 26.2 | 21.9 | 26 | 27.8 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
127 | -13 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
128 | -12 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
129 | -11 | 18.4 | 26.2 | 21.9 | 26 | 27.8 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
130 | -10 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
131 | -9 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
132 | -8 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
133 | -7 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.1 | 23.3 | 24.2
134 | -6 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
135 | -5 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
136 | -4 | 18.4 | 26.2 | 22 | 26 | 27.8 | 25.9 | 24.8 | 27.2 | 23.3 | 24.2
137 | -3 | 18.4 | 26.2 | 21.8 | 26 | 27.9 | 25.9 | 24.8 | 27.2 | 23.3 | 24.4
138 | -2 | 18.4 | 26.5 | 21.3 | 26.3 | 28.5 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
139 | -1 | 18.7 | 26.6 | 21.1 | 26.3 | 28.7 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
140 | 0 | 19.5 | 26.6 | 21.1 | 26.3 | 28.7 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
141 | 1 | 21.1 | 26.6 | 21.1 | 26.4 | 28.8 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
142 | 2 | 23.4 | 26.6 | 21.1 | 26.3 | 28.7 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
143 | 3 | 26.2 | 26.6 | 21.1 | 26.4 | 28.8 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
144 | 4 | 29.5 | 26.7 | 21.1 | 26.4 | 28.8 | 26.2 | 24.7 | 27 | 23.2 | 24.5
145 | 5 | 33.3 | 26.7 | 21.1 | 26.4 | 28.9 | 26.2 | 24.7 | 27 | 23.2 | 24.5
146 | 6 | 37.4 | 26.7 | 21.2 | 26.4 | 28.8 | 26.2 | 24.7 | 27 | 23.3 | 24.5
147 | 7 | 41.8 | 26.7 | 21.2 | 26.4 | 28.8 | 26.2 | 24.7 | 27 | 23.3 | 24.5
148 | 8 | 46.4 | 26.7 | 21.3 | 26.4 | 28.8 | 26.2 | 24.7 | 27 | 23.2 | 24.5
149 | 9 | 51.3 | 26.7 | 21.3 | 26.4 | 28.8 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
150 | 10 | 56.2 | 26.8 | 21.3 | 26.5 | 28.8 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
151 | 11 | 61.2 | 26.8 | 21.5 | 26.5 | 28.8 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
152 | 12 | 66.3 | 26.8 | 21.5 | 26.6 | 28.9 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
153 | 13 | 71.5 | 26.9 | 21.6 | 26.6 | 28.8 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
154 | 14 | 76.8 | 26.9 | 21.6 | 26.6 | 28.9 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
155 | 15 | 82.3 | 27 | 21.7 | 26.7 | 28.9 | 26.3 | 24.7 | 27.1 | 23.2 | 24.5
156 | 16 | 87.9 | 27 | 21.9 | 26.7 | 28.9 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
157 | 17 | 93.8 | 27.1 | 22 | 26.8 | 28.9 | 26.3 | 24.7 | 27.1 | 23.2 | 24.5
158 | 18 | 99.8 | 27.1 | 22.1 | 26.9 | 28.9 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
159 | 19 | 105.9 | 27.2 | 22.2 | 26.9 | 28.9 | 26.3 | 24.7 | 27.1 | 23.2 | 24.5
160 | 20 | 112 | 27.3 | 22.4 | 27 | 28.9 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
161 | 21 | 118.2 | 27.4 | 22.6 | 27.1 | 28.9 | 26.3 | 24.7 | 27.1 | 23.2 | 24.5
162 | 22 | 124.4 | 27.5 | 22.8 | 27.1 | 28.9 | 26.2 | 24.7 | 27 | 23.2 | 24.5
163 | 23 | 130.6 | 27.5 | 23 | 27.2 | 28.9 | 26.2 | 24.7 | 27 | 23.2 | 24.5
164 | 24 | 136.8 | 27.6 | 23.2 | 27.3 | 28.8 | 26.2 | 24.7 | 27 | 23.2 | 24.5
165 | 25 | 143 | 27.7 | 23.5 | 27.4 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
166 | 26 | 149.1 | 27.9 | 23.7 | 27.5 | 28.8 | 26.2 | 24.7 | 27.1 | 23.2 | 24.5
167 | 27 | 155.3 | 28 | 23.9 | 27.6 | 28.9 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
168 | 28 | 161.5 | 28.1 | 24.2 | 27.7 | 28.9 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
169 | 29 | 167.6 | 28.2 | 24.6 | 27.9 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
170 | 30 | 173.7 | 28.4 | 24.7 | 28 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
171 | 31 | 179.8 | 28.5 | 24.9 | 28.1 | 28.9 | 26.2 | 24.7 | 27.2 | 23.3 | 24.5
172 | 32 | 186 | 28.6 | 25.2 | 28.3 | 28.8 | 26.2 | 24.7 | 27.2 | 23.3 | 24.5
173 | 33 | 192.2 | 28.8 | 25.5 | 28.4 | 28.7 | 26.2 | 24.7 | 27.2 | 23.3 | 24.4
174 | 34 | 198.4 | 29 | 25.9 | 28.6 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
175 | 35 | 204.6 | 29.1 | 26.5 | 28.7 | 28.7 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
176 | 36 | 210.8 | 29.3 | 26.8 | 28.9 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
177 | 37 | 216.9 | 29.5 | 27.2 | 29.1 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.4
178 | 38 | 223.1 | 29.7 | 27.7 | 29.3 | 28.7 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
179 | 39 | 229.2 | 29.9 | 28.1 | 29.5 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
180 | 40 | 235.3 | 30.2 | 28.3 | 29.7 | 28.9 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
181 | 41 | 241.5 | 30.4 | 28.6 | 30 | 28.9 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
182 | 42 | 247.6 | 30.6 | 29.3 | 30.2 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
183 | 43 | 253.6 | 30.9 | 30.1 | 30.5 | 28.9 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
184 | 44 | 259.7 | 31.2 | 30.7 | 30.7 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
185 | 45 | 265.8 | 31.4 | 31.1 | 30.9 | 28.8 | 26.2 | 24.7 | 27.1 | 23.3 | 24.5
186 | 46 | 271.7 | 32.4 | 30.1 | 31.6 | 30.3 | 26.7 | 24.5 | 26.9 | 23.3 | 24.7
187 | 47 | 277.7 | 33.2 | 29.7 | 32.2 | 31.4 | 27.1 | 24.4 | 26.7 | 23.3 | 24.8
188 | 48 | 283.7 | 33.5 | 30.2 | 32.5 | 31.4 | 27.1 | 24.4 | 26.7 | 23.3 | 24.8
189 | 49 | 289.7 | 33.8 | 30.7 | 32.8 | 31.5 | 27.1 | 24.4 | 26.7 | 23.3 | 24.9
190 | 50 | 295.6 | 34.2 | 31.3 | 33.1 | 31.5 | 27.1 | 24.4 | 26.7 | 23.3 | 24.9
191 | 51 | 301.6 | 34.5 | 32.1 | 33.5 | 31.5 | 27.1 | 24.4 | 26.7 | 23.3 | 24.9
192 | 52 | 307.5 | 34.9 | 32.6 | 33.8 | 31.5 | 27.1 | 24.4 | 26.7 | 23.3 | 24.9
193 | 53 | 313.3 | 35.3 | 33.2 | 34.2 | 31.5 | 27.1 | 24.4 | 26.7 | 23.3 | 24.9
194 | 54 | 319 | 35.6 | 33.7 | 34.5 | 31.5 | 27.1 | 24.4 | 26.7 | 23.3 | 24.9
195 | 55 | 324.7 | 36.1 | 34.4 | 34.9 | 31.5 | 27.2 | 24.4 | 26.7 | 23.3 | 24.9
196 | 56 | 330.5 | 36.5 | 35.1 | 35.3 | 31.6 | 27.2 | 24.4 | 26.6 | 23.3 | 24.9
197 | 57 | 336.2 | 36.9 | 35.7 | 35.7 | 31.6 | 27.2 | 24.4 | 26.6 | 23.3 | 24.9
198 | 58 | 341.9 | 37.4 | 36.4 | 36.2 | 31.6 | 27.2 | 24.4 | 26.6 | 23.3 | 24.9
199 | 59 | 347.6 | 37.8 | 37.3 | 36.6 | 31.6 | 27.2 | 24.4 | 26.7 | 23.4 | 24.9
200 | 60 | 353.2 | 38.2 | 38 | 37.1 | 31.5 | 27.2 | 24.4 | 26.7 | 23.4 | 24.9
201 | 61 | 358.8 | 38.7 | 38.9 | 37.5 | 31.6 | 27.2 | 24.4 | 26.7 | 23.4 | 24.9
202 | 62 | 364.4 | 39.2 | 39.9 | 38 | 31.7 | 27.2 | 24.4 | 26.6 | 23.4 | 24.9
203 | 63 | 369.9 | 39.7 | 40.7 | 38.5 | 31.7 | 27.2 | 24.4 | 26.6 | 23.4 | 24.9
204 | 64 | 375.4 | 40.2 | 41.5 | 39 | 31.6 | 27.2 | 24.4 | 26.6 | 23.4 | 24.9
205 | 65 | 381 | 40.7 | 42.4 | 39.5 | 31.7 | 27.2 | 24.4 | 26.6 | 23.4 | 24.9
206 | 66 | 386.4 | 41.3 | 43.3 | 40 | 31.6 | 27.2 | 24.4 | 26.7 | 23.5 | 24.9
207 | 67 | 391.7 | 41.8 | 44.2 | 40.5 | 31.6 | 27.2 | 24.4 | 26.6 | 23.5 | 25
208 | 68 | 397 | 42.4 | 45.1 | 41.1 | 31.6 | 27.2 | 24.4 | 26.7 | 23.5 | 24.9
209 | 69 | 402.3 | 43 | 46.2 | 41.6 | 31.7 | 27.2 | 24.4 | 26.7 | 23.5 | 24.9
210 | 70 | 407.7 | 43.6 | 47.3 | 42.2 | 31.6 | 27.2 | 24.4 | 26.7 | 23.5 | 25
211 | 71 | 413.1 | 44.3 | 48.1 | 42.8 | 31.7 | 27.2 | 24.4 | 26.7 | 23.6 | 25
212 | 72 | 418.3 | 44.9 | 49.3 | 43.4 | 31.7 | 27.2 | 24.4 | 26.7 | 23.6 | 24.9
213 | 73 | 423.6 | 45.5 | 50.3 | 44 | 31.7 | 27.2 | 24.4 | 26.7 | 23.6 | 25
214 | 74 | 428.8 | 46.2 | 51.2 | 44.7 | 31.7 | 27.2 | 24.4 | 26.7 | 23.6 | 25
215 | 75 | 434 | 46.8 | 52.4 | 45.4 | 31.7 | 27.2 | 24.5 | 26.7 | 23.6 | 25
216 | 76 | 439.2 | 47.6 | 53.6 | 46.1 | 31.7 | 27.2 | 24.4 | 26.7 | 23.7 | 25
217 | 77 | 444.1 | 48.3 | 54.9 | 46.7 | 31.7 | 27.2 | 24.5 | 26.8 | 23.7 | 25
218 | 78 | 449.1 | 49.1 | 56.1 | 47.4 | 31.8 | 27.2 | 24.5 | 26.7 | 23.7 | 25
219 | 79 | 454.2 | 49.8 | 57.5 | 48.2 | 31.8 | 27.2 | 24.5 | 26.6 | 23.8 | 25
220 | 80 | 459.3 | 50.6 | 58.7 | 49 | 31.9 | 27.3 | 24.5 | 26.6 | 23.8 | 25.1
221 | 81 | 464.3 | 51.3 | 60.1 | 49.7 | 31.8 | 27.2 | 24.5 | 26.7 | 23.8 | 25.1
222 | 82 | 469.3 | 52.2 | 61.4 | 50.5 | 31.8 | 27.2 | 24.5 | 26.7 | 23.8 | 25.1
223 | 83 | 474.2 | 53 | 62.7 | 51.3 | 31.8 | 27.2 | 24.5 | 26.7 | 23.9 | 25.1
224 | 84 | 479.2 | 53.8 | 64 | 52.1 | 31.8 | 27.2 | 24.5 | 26.7 | 23.9 | 25.1
225 | 85 | 484.1 | 54.7 | 65.3 | 52.9 | 31.8 | 27.2 | 24.5 | 26.7 | 23.9 | 25.1
226 | 86 | 488.9 | 55.5 | 66.8 | 53.7 | 31.6 | 27.2 | 24.5 | 26.8 | 24 | 25.1
227 | 87 | 493.6 | 56 | 68.8 | 54.4 | 31 | 26.9 | 24.6 | 27 | 24 | 25
228 | 88 | 498.2 | 56.9 | 70.4 | 55.2 | 31 | 26.9 | 24.6 | 27 | 24.1 | 25.1
229 | 89 | 502.3 | 57.8 | 71.9 | 56.1 | 31.1 | 26.9 | 24.6 | 26.9 | 24.1 | 25.1
230 | 90 | 506 | 58.6 | 73.6 | 57 | 31 | 26.9 | 24.6 | 27 | 24.2 | 25.1
231 | 91 | 509.3 | 59.6 | 75 | 57.9 | 31.1 | 26.9 | 24.7 | 27 | 24.2 | 25.1
232 | 92 | 512.3 | 60.5 | 76.5 | 58.7 | 31 | 26.8 | 24.7 | 27 | 24.3 | 25.1
233 | 93 | 515.1 | 61.4 | 77.9 | 59.7 | 31.1 | 26.9 | 24.7 | 27 | 24.3 | 25.1
234 | 94 | 517.6 | 62.3 | 79.3 | 60.5 | 31 | 26.8 | 24.7 | 27.1 | 24.4 | 25.1
235 | 95 | 520.1 | 63.3 | 80.6 | 61.5 | 31 | 26.8 | 24.7 | 27.1 | 24.4 | 25.2
236 | 96 | 522.4 | 64.3 | 82 | 62.5 | 31.1 | 26.9 | 24.7 | 27.1 | 24.5 | 25.2
237 | 97 | 524.5 | 65.2 | 83.6 | 63.3 | 31 | 26.8 | 24.7 | 27.1 | 24.5 | 25.2
238 | 98 | 526.6 | 66 | 85.2 | 64.2 | 30.9 | 26.8 | 24.8 | 27.2 | 24.6 | 25.2
239 | 99 | 528.5 | 66.9 | 86.9 | 65.1 | 30.6 | 26.7 | 24.8 | 27.2 | 24.6 | 25.1
240 | 100 | 530 | 67.8 | 88.5 | 66 | 30.4 | 26.6 | 24.8 | 27.3 | 24.7 | 25.1
241 | 101 | 531.2 | 68.7 | 90 | 66.9 | 30.3 | 26.6 | 24.9 | 27.4 | 24.8 | 25.1
242 | 102 | 532.2 | 69.6 | 91.5 | 67.7 | 30.1 | 26.6 | 24.9 | 27.5 | 24.8 | 25.1
243 | 103 | 533.1 | 70.5 | 92.9 | 68.7 | 30 | 26.5 | 24.9 | 27.5 | 24.9 | 25.1
244 | 104 | 533.6 | 71.4 | 94.2 | 69.5 | 29.9 | 26.5 | 24.9 | 27.6 | 25 | 25.1
245 | 105 | 533.9 | 72.3 | 95.6 | 70.5 | 29.9 | 26.5 | 25 | 27.6 | 25 | 25.2
246 | 106 | 534 | 73.3 | 96.7 | 71.3 | 30 | 26.5 | 25 | 27.6 | 25.1 | 25.2
247 | 107 | 533.9 | 74.2 | 97.9 | 72.2 | 30.2 | 26.6 | 25 | 27.6 | 25.2 | 25.3
248 | 108 | 533.6 | 75.1 | 99.1 | 73.1 | 30.2 | 26.6 | 25 | 27.7 | 25.3 | 25.3
249 | 109 | 533.3 | 76.1 | 100.1 | 73.9 | 30.2 | 26.6 | 25 | 27.7 | 25.3 | 25.4
250 | 110 | 532.9 | 77 | 101.3 | 74.8 | 30.2 | 26.6 | 25 | 27.7 | 25.4 | 25.4
251 | 111 | 532.4 | 77.9 | 102.5 | 75.7 | 30.3 | 26.6 | 25.1 | 27.7 | 25.5 | 25.4
252 | 112 | 531.9 | 78.8 | 103.8 | 76.6 | 30.3 | 26.7 | 25.1 | 27.7 | 25.6 | 25.5
253 | 113 | 531.2 | 79.8 | 104.9 | 77.4 | 30.4 | 26.7 | 25.1 | 27.7 | 25.7 | 25.5
254 | 114 | 530.6 | 80.7 | 106 | 78.4 | 30.6 | 26.7 | 25.1 | 27.7 | 25.7 | 25.6
255 | 115 | 530 | 81.6 | 107.1 | 79.3 | 30.8 | 26.8 | 25.1 | 27.8 | 25.8 | 25.7
256 | 116 | 529.4 | 82.5 | 108.3 | 80.1 | 31 | 26.9 | 25.1 | 27.8 | 25.9 | 25.7
257 | 117 | 528.8 | 83.5 | 109.5 | 81 | 31.1 | 26.9 | 25.2 | 27.8 | 26 | 25.8
258 | 118 | 528.2 | 84.4 | 110.5 | 82 | 31.2 | 26.9 | 25.2 | 27.8 | 26.1 | 25.8
259 | 119 | 527.7 | 85.3 | 111.5 | 82.9 | 31.4 | 27 | 25.2 | 27.8 | 26.2 | 25.9
260 | 120 | 527.3 | 86.2 | 112.5 | 83.7 | 31.6 | 27 | 25.2 | 27.8 | 26.3 | 26
261 | 121 | 527 | 87.1 | 113.7 | 84.7 | 31.7 | 27.1 | 25.2 | 27.8 | 26.4 | 26
262 | 122 | 526.6 | 88 | 114.8 | 85.4 | 31.9 | 27.1 | 25.3 | 27.8 | 26.5 | 26.1
263 | 123 | 526.3 | 88.9 | 116 | 86.3 | 32 | 27.2 | 25.3 | 27.9 | 26.6 | 26.2
264 | 124 | 526.1 | 89.8 | 117.1 | 87.3 | 32 | 27.2 | 25.3 | 27.9 | 26.7 | 26.2
265 | 125 | 526.1 | 90.7 | 118.4 | 88.1 | 32.2 | 27.3 | 25.4 | 27.9 | 26.8 | 26.3
266 | 126 | 526 | 91.6 | 119.3 | 89 | 32.3 | 27.3 | 25.4 | 27.9 | 26.9 | 26.4
267 | 127 | 526 | 92.4 | 120.5 | 89.8 | 32.4 | 27.3 | 25.4 | 28 | 27 | 26.4
268 | 128 | 526 | 93.3 | 121.6 | 90.6 | 32.5 | 27.4 | 25.4 | 28.1 | 27.1 | 26.5
269 | 129 | 526 | 94.2 | 122.8 | 91.5 | 32.6 | 27.4 | 25.5 | 28.1 | 27.2 | 26.6
270 | 130 | 526.2 | 95 | 124 | 92.3 | 32.7 | 27.5 | 25.5 | 28.1 | 27.3 | 26.6
271 | 131 | 526.4 | 95.9 | 125.1 | 93.1 | 32.8 | 27.5 | 25.6 | 28.2 | 27.4 | 26.7
272 | 132 | 526.6 | 96.8 | 126.2 | 94 | 32.9 | 27.5 | 25.6 | 28.2 | 27.5 | 26.7
273 | 133 | 526.9 | 97.7 | 127.4 | 94.9 | 33 | 27.6 | 25.6 | 28.3 | 27.6 | 26.8
274 | 134 | 527.1 | 98.5 | 128.5 | 95.7 | 33.1 | 27.6 | 25.7 | 28.4 | 27.7 | 26.9
275 | 135 | 527.4 | 99.4 | 129.7 | 96.6 | 33.3 | 27.7 | 25.7 | 28.4 | 27.8 | 27
276 | 136 | 527.7 | 100.3 | 130.9 | 97.4 | 33.3 | 27.7 | 25.8 | 28.5 | 28 | 27
277 | 137 | 527.9 | 101.1 | 132 | 98.3 | 33.4 | 27.7 | 25.8 | 28.5 | 28.1 | 27.1
278 | 138 | 528.2 | 102 | 133.1 | 99.2 | 33.5 | 27.8 | 25.9 | 28.7 | 28.2 | 27.2
279 | 139 | 528.6 | 102.9 | 134.2 | 100 | 33.6 | 27.8 | 25.9 | 28.7 | 28.3 | 27.2
280 | 140 | 528.9 | 103.7 | 135.4 | 100.9 | 33.7 | 27.9 | 26 | 28.8 | 28.4 | 27.3
281 | 141 | 529.1 | 104.6 | 136.6 | 101.7 | 33.9 | 27.9 | 26 | 28.8 | 28.5 | 27.4
282 | 142 | 529.3 | 105.4 | 137.6 | 102.5 | 34 | 28 | 26.1 | 28.9 | 28.7 | 27.5
283 | 143 | 529.5 | 106.2 | 138.8 | 103.4 | 34.1 | 28 | 26.1 | 29 | 28.8 | 27.6
284 | 144 | 529.8 | 107.1 | 139.9 | 104.3 | 34.2 | 28.1 | 26.2 | 29.1 | 28.9 | 27.7
285 | 145 | 529.9 | 108 | 141.1 | 105.1 | 34.3 | 28.1 | 26.2 | 29.2 | 29.1 | 27.7
286 | 146 | 530.1 | 108.8 | 142.2 | 105.9 | 34.4 | 28.2 | 26.3 | 29.3 | 29.2 | 27.8
287 | 147 | 530.3 | 109.7 | 143.3 | 106.7 | 34.5 | 28.2 | 26.3 | 29.3 | 29.3 | 27.9
288 | 148 | 530.4 | 110.6 | 144.4 | 107.6 | 34.7 | 28.3 | 26.4 | 29.4 | 29.5 | 28
289 | 149 | 530.5 | 111.4 | 145.5 | 108.5 | 34.9 | 28.4 | 26.4 | 29.4 | 29.6 | 28.1
290 | 150 | 530.6 | 112.3 | 146.5 | 109.3 | 35 | 28.4 | 26.5 | 29.5 | 29.8 | 28.2
291 | 151 | 530.7 | 113.1 | 147.5 | 110.1 | 35.1 | 28.5 | 26.6 | 29.6 | 29.9 | 28.3
292 | 152 | 530.8 | 113.9 | 148.6 | 110.9 | 35.3 | 28.5 | 26.6 | 29.6 | 30.1 | 28.4
293 | 153 | 530.9 | 114.7 | 149.7 | 112 | 35.4 | 28.6 | 26.7 | 29.7 | 30.2 | 28.4
294 | 154 | 531.1 | 115.6 | 150.7 | 112.8 | 35.6 | 28.7 | 26.8 | 29.8 | 30.4 | 28.6
295 | 155 | 531.1 | 116.5 | 151.8 | 113.5 | 35.7 | 28.7 | 26.8 | 29.9 | 30.5 | 28.6
296 | 156 | 531.1 | 117.3 | 153 | 114.3 | 35.9 | 28.8 | 26.9 | 30 | 30.7 | 28.7
297 | 157 | 531.1 | 118.1 | 154.1 | 115.1 | 36 | 28.9 | 27 | 30.1 | 30.9 | 28.8
298 | 158 | 531.2 | 119 | 155.2 | 115.9 | 36.2 | 29 | 27.1 | 30.2 | 31 | 29
299 | 159 | 531.3 | 119.8 | 156.1 | 116.8 | 36.4 | 29 | 27.1 | 30.3 | 31.2 | 29.1
300 | 160 | 531.3 | 120.6 | 157.2 | 117.5 | 36.5 | 29.1 | 27.2 | 30.4 | 31.4 | 29.2
301 | 161 | 531.3 | 121.5 | 158.3 | 118.4 | 36.7 | 29.2 | 27.3 | 30.4 | 31.5 | 29.3
302 | 162 | 531.3 | 122.3 | 159.4 | 119.2 | 36.9 | 29.3 | 27.4 | 30.5 | 31.7 | 29.4
303 | 163 | 531.4 | 123.2 | 160.4 | 120 | 37 | 29.4 | 27.4 | 30.6 | 31.8 | 29.5
304 | 164 | 531.4 | 124 | 161.4 | 120.8 | 37.2 | 29.4 | 27.5 | 30.7 | 32 | 29.6
305 | 165 | 531.6 | 124.8 | 162.5 | 121.6 | 37.4 | 29.5 | 27.6 | 30.7 | 32.2 | 29.8
306 | 166 | 531.6 | 125.7 | 163.5 | 122.4 | 37.6 | 29.6 | 27.7 | 30.8 | 32.3 | 29.9
307 | 167 | 531.7 | 126.5 | 164.6 | 123.3 | 37.8 | 29.7 | 27.8 | 31 | 32.5 | 30
308 | 168 | 531.8 | 127.3 | 165.6 | 124.1 | 37.9 | 29.8 | 27.9 | 31.1 | 32.7 | 30.1
309 | 169 | 531.9 | 128.1 | 166.6 | 124.9 | 38.1 | 29.9 | 28 | 31.2 | 32.9 | 30.2
310 | 170 | 531.9 | 128.9 | 167.6 | 125.7 | 38.3 | 29.9 | 28 | 31.3 | 33 | 30.3
311 | 171 | 531.9 | 129.7 | 168.6 | 126.5 | 38.4 | 30 | 28.1 | 31.4 | 33.2 | 30.4
312 | 172 | 532 | 130.5 | 169.6 | 127.3 | 38.7 | 30.1 | 28.2 | 31.5 | 33.4 | 30.6
313 | 173 | 532 | 131.3 | 170.7 | 128.1 | 38.8 | 30.2 | 28.3 | 31.6 | 33.6 | 30.7
314 | 174 | 532.1 | 132.1 | 171.8 | 128.9 | 39 | 30.3 | 28.4 | 31.8 | 33.8 | 30.8
315 | 175 | 532.1 | 132.9 | 172.9 | 129.7 | 39.2 | 30.4 | 28.5 | 31.9 | 34 | 31
316 | 176 | 532.1 | 133.7 | 173.9 | 130.4 | 39.4 | 30.5 | 28.6 | 32 | 34.1 | 31.1
317 | 177 | 532.2 | 134.5 | 174.9 | 131.2 | 39.5 | 30.6 | 28.7 | 32.2 | 34.3 | 31.2
318 | 178 | 532.2 | 135.3 | 175.9 | 132.1 | 39.8 | 30.7 | 28.8 | 32.3 | 34.5 | 31.4
319 | 179 | 532.2 | 136.1 | 176.9 | 132.9 | 40 | 30.8 | 28.9 | 32.4 | 34.7 | 31.5
320 | 180 | 532.2 | 137 | 177.8 | 133.7 | 40.3 | 31 | 29 | 32.6 | 34.9 | 31.7
321 | 181 | 532.2 | 137.8 | 178.8 | 134.5 | 40.6 | 31.1 | 29.1 | 32.7 | 35.1 | 31.8
322 | 182 | 532.3 | 138.6 | 179.8 | 135.2 | 40.7 | 31.2 | 29.2 | 32.9 | 35.3 | 31.9
323 | 183 | 532.3 | 139.3 | 180.8 | 136 | 41 | 31.3 | 29.4 | 33.1 | 35.5 | 32.1
324 | 184 | 532.3 | 140.1 | 181.9 | 136.7 | 41.1 | 31.4 | 29.5 | 33.2 | 35.7 | 32.2
325 | 185 | 532.3 | 140.9 | 182.9 | 137.5 | 41.3 | 31.5 | 29.6 | 33.3 | 35.9 | 32.3
326 | 186 | 532.4 | 141.6 | 183.9 | 138.3 | 41.5 | 31.6 | 29.7 | 33.5 | 36.1 | 32.5
327 | 187 | 532.4 | 142.4 | 184.8 | 139.1 | 41.7 | 31.7 | 29.8 | 33.6 | 36.3 | 32.6
328 | 188 | 532.4 | 143.2 | 185.9 | 139.8 | 41.8 | 31.8 | 30 | 33.8 | 36.5 | 32.8
329 | 189 | 532.4 | 143.9 | 186.9 | 140.6 | 42 | 31.9 | 30.1 | 33.9 | 36.7 | 32.9
330 | 190 | 532.4 | 144.7 | 188 | 141.4 | 42.2 | 32 | 30.2 | 34.1 | 36.9 | 33.1
331 | 191 | 532.5 | 145.4 | 188.9 | 142.1 | 42.5 | 32.2 | 30.3 | 34.2 | 37.1 | 33.2
332 | 192 | 532.4 | 146.3 | 189.9 | 142.9 | 42.7 | 32.3 | 30.5 | 34.4 | 37.3 | 33.4
333 | 193 | 532.4 | 147 | 190.8 | 143.8 | 43 | 32.4 | 30.6 | 34.6 | 37.5 | 33.5
334 | 194 | 532.3 | 147.8 | 191.8 | 144.6 | 43.2 | 32.6 | 30.7 | 34.8 | 37.7 | 33.7
335 | 195 | 532.2 | 148.6 | 192.8 | 145.3 | 43.4 | 32.7 | 30.8 | 35 | 37.9 | 33.8
336 | 196 | 532.1 | 149.3 | 193.8 | 146.1 | 43.7 | 32.8 | 31 | 35.2 | 38.1 | 34
337 | 197 | 532.1 | 150.1 | 194.8 | 146.8 | 43.9 | 33 | 31.1 | 35.3 | 38.3 | 34.1
338 | 198 | 532.1 | 150.8 | 195.7 | 147.6 | 44.2 | 33.1 | 31.2 | 35.5 | 38.5 | 34.3
339 | 199 | 532.1 | 151.6 | 196.7 | 148.3 | 44.4 | 33.3 | 31.4 | 35.7 | 38.7 | 34.4
340 | 200 | 532.2 | 152.3 | 197.7 | 149.1 | 44.6 | 33.4 | 31.5 | 35.8 | 38.9 | 34.6
341 | 201 | 532.2 | 153.1 | 198.6 | 149.9 | 44.8 | 33.5 | 31.7 | 36 | 39.1 | 34.7
342 | 202 | 532.3 | 153.8 | 199.5 | 150.5 | 45 | 33.6 | 31.8 | 36.2 | 39.3 | 34.9
343 | 203 | 532.3 | 154.6 | 200.4 | 151.3 | 45.2 | 33.8 | 31.9 | 36.3 | 39.5 | 35.1
344 | 204 | 532.3 | 155.3 | 201.4 | 152.1 | 45.5 | 33.9 | 32.1 | 36.5 | 39.7 | 35.2
345 | 205 | 532.3 | 156.1 | 202.4 | 152.8 | 45.6 | 34.1 | 32.2 | 36.7 | 39.9 | 35.4
346 | 206 | 532.3 | 156.8 | 203.4 | 153.5 | 45.9 | 34.2 | 32.4 | 36.9 | 40.1 | 35.5
347 | 207 | 532.3 | 157.5 | 204.3 | 154.2 | 46.1 | 34.4 | 32.5 | 37.1 | 40.3 | 35.7
348 | 208 | 532.4 | 158.3 | 205.3 | 155 | 46.3 | 34.5 | 32.7 | 37.3 | 40.5 | 35.9
349 | 209 | 532.4 | 159 | 206.3 | 155.7 | 46.6 | 34.6 | 32.8 | 37.4 | 40.7 | 36
350 | 210 | 532.4 | 159.7 | 207.1 | 156.4 | 46.8 | 34.8 | 33 | 37.6 | 40.8 | 36.2
351 | 211 | 532.5 | 160.4 | 208 | 157.2 | 47 | 34.9 | 33.2 | 37.8 | 41 | 36.4
352 | 212 | 532.5 | 161.2 | 208.9 | 158 | 47.3 | 35.1 | 33.3 | 37.9 | 41.2 | 36.5
353 | 213 | 532.5 | 161.9 | 209.9 | 158.7 | 47.5 | 35.2 | 33.5 | 38.1 | 41.4 | 36.7
354 | 214 | 532.5 | 162.6 | 210.9 | 159.4 | 47.6 | 35.4 | 33.6 | 38.4 | 41.6 | 36.9
355 | 215 | 532.5 | 163.3 | 211.8 | 160.1 | 47.9 | 35.5 | 33.8 | 38.6 | 41.8 | 37
356 | 216 | 532.5 | 164.1 | 212.6 | 160.8 | 48.2 | 35.7 | 33.9 | 38.8 | 42 | 37.2
357 | 217 | 532.4 | 164.8 | 213.6 | 161.6 | 48.5 | 35.9 | 34.1 | 38.9 | 42.2 | 37.4
358 | 218 | 532.3 | 165.6 | 214.4 | 162.4 | 48.8 | 36.1 | 34.3 | 39.1 | 42.4 | 37.6
359 | 219 | 532.3 | 166.3 | 215.4 | 163 | 49 | 36.2 | 34.4 | 39.3 | 42.6 | 37.7
360 | 220 | 532.3 | 167 | 216.2 | 163.8 | 49.2 | 36.4 | 34.6 | 39.5 | 42.8 | 37.9
361 | 221 | 532.3 | 167.7 | 217 | 164.5 | 49.5 | 36.6 | 34.8 | 39.7 | 43 | 38.1
362 | 222 | 532.3 | 168.5 | 217.9 | 165.2 | 49.8 | 36.7 | 34.9 | 39.8 | 43.2 | 38.2
363 | 223 | 532.2 | 169.3 | 218.4 | 166.1 | 50.3 | 37 | 35.1 | 40 | 43.5 | 38.4
364 | 224 | 532.2 | 169.9 | 219.5 | 166.7 | 50.4 | 37.1 | 35.3 | 40.2 | 43.7 | 38.6
365 | 225 | 532.2 | 171.1 | 219.4 | 167.7 | 51.4 | 37.7 | 35.3 | 40.2 | 43.8 | 39
366 | 226 | 532.2 | 172.2 | 219.6 | 168.6 | 52.2 | 38.1 | 35.5 | 40.3 | 44 | 39.3
367 | 227 | 532.2 | 172.8 | 220.5 | 169.4 | 52.4 | 38.2 | 35.6 | 40.6 | 44.2 | 39.4
368 | 228 | 532.2 | 173.5 | 221.4 | 170.2 | 52.6 | 38.4 | 35.8 | 40.8 | 44.4 | 39.6
369 | 229 | 532.2 | 174.2 | 222.1 | 170.8 | 52.9 | 38.6 | 36 | 41 | 44.6 | 39.8
370 | 230 | 532.3 | 174.9 | 223 | 171.4 | 53.2 | 38.8 | 36.2 | 41.3 | 44.8 | 39.9
371 | 231 | 532.3 | 175.6 | 223.8 | 172.1 | 53.4 | 38.9 | 36.3 | 41.5 | 45 | 40.1
372 | 232 | 532.4 | 176.3 | 224.6 | 172.9 | 53.7 | 39.1 | 36.5 | 41.7 | 45.2 | 40.3
373 | 233 | 532.4 | 177 | 225.4 | 173.6 | 53.9 | 39.3 | 36.7 | 41.9 | 45.5 | 40.4
374 | 234 | 532.5 | 177.6 | 226.3 | 174.2 | 54.2 | 39.5 | 36.9 | 42.1 | 45.7 | 40.6
375 | 235 | 532.5 | 178.3 | 227.1 | 175 | 54.4 | 39.6 | 37.1 | 42.4 | 45.9 | 40.8
376 | 236 | 532.6 | 178.9 | 228 | 175.8 | 54.7 | 39.8 | 37.3 | 42.6 | 46.1 | 41
377 | 237 | 532.6 | 179.6 | 228.8 | 176.4 | 54.9 | 40 | 37.4 | 42.8 | 46.4 | 41.1
378 | 238 | 532.6 | 180.2 | 229.7 | 177 | 55.1 | 40.1 | 37.6 | 43 | 46.6 | 41.3
379 | 239 | 532.6 | 180.9 | 230.6 | 177.8 | 55.3 | 40.3 | 37.8 | 43.2 | 46.9 | 41.4
380 | 240 | 532.6 | 181.5 | 231.4 | 178.5 | 55.6 | 40.5 | 38 | 43.4 | 47.3 | 41.5
381 | 241 | 532.7 | 182.2 | 232.3 | 179.1 | 55.8 | 40.7 | 38.2 | 43.6 | 47.5 | 41.7
382 | 242 | 532.7 | 182.8 | 233.2 | 179.9 | 56.1 | 40.9 | 38.4 | 43.9 | 47.8 | 41.9
383 | 243 | 532.7 | 183.4 | 234 | 180.6 | 56.4 | 41 | 38.6 | 44.1 | 48 | 42
384 | 244 | 532.8 | 184.1 | 234.8 | 181.2 | 56.7 | 41.2 | 38.8 | 44.3 | 48.2 | 42.2
385 | 245 | 532.8 | 184.8 | 235.6 | 181.9 | 56.9 | 41.4 | 39 | 44.5 | 48.4 | 42.4
386 | 246 | 532.7 | 185.4 | 236.5 | 182.6 | 57.1 | 41.6 | 39.2 | 44.8 | 48.6 | 42.5
387 | 247 | 532.7 | 186 | 237.3 | 183.2 | 57.4 | 41.8 | 39.4 | 45 | 48.8 | 42.7
388 | 248 | 532.6 | 186.7 | 238.2 | 183.9 | 57.6 | 42 | 39.6 | 45.2 | 49 | 42.9
389 | 249 | 532.6 | 187.3 | 239 | 184.6 | 57.9 | 42.2 | 39.8 | 45.5 | 49.2 | 43.1
390 | 250 | 532.5 | 187.9 | 239.9 | 185.3 | 58.2 | 42.4 | 40 | 45.7 | 49.4 | 43.2
391 | 251 | 532.5 | 188.6 | 240.6 | 186 | 58.5 | 42.6 | 40.2 | 45.9 | 49.6 | 43.4
392 | 252 | 532.5 | 189.2 | 241.6 | 186.6 | 58.6 | 42.8 | 40.4 | 46.2 | 49.8 | 43.6
393 | 253 | 532.5 | 189.8 | 242.5 | 187.3 | 58.9 | 42.9 | 40.6 | 46.4 | 50 | 43.8
394 | 254 | 532.5 | 190.5 | 243.4 | 188 | 59.1 | 43.1 | 40.8 | 46.6 | 50.2 | 43.9
395 | 255 | 532.5 | 191.2 | 244.2 | 188.7 | 59.4 | 43.3 | 41 | 46.9 | 50.4 | 44.2
396 | 256 | 532.5 | 191.8 | 245.1 | 189.4 | 59.6 | 43.5 | 41.2 | 47.1 | 50.5 | 44.4
397 | 257 | 532.5 | 192.4 | 246 | 190 | 59.8 | 43.7 | 41.4 | 47.3 | 50.7 | 44.5
398 | 258 | 532.5 | 193 | 246.9 | 190.6 | 60 | 43.9 | 41.6 | 47.5 | 50.9 | 44.7
399 | 259 | 532.5 | 193.7 | 247.7 | 191.4 | 60.2 | 44.1 | 41.8 | 47.7 | 51.1 | 44.9
400 | 260 | 532.5 | 194.3 | 248.5 | 192 | 60.4 | 44.3 | 42.1 | 48 | 51.3 | 45.1
401 | 261 | 532.5 | 194.8 | 249.5 | 192.7 | 60.6 | 44.5 | 42.3 | 48.2 | 51.5 | 45.2
402 | 262 | 532.4 | 195.6 | 250.2 | 193.4 | 60.9 | 44.7 | 42.5 | 48.4 | 51.7 | 45.5
403 | 263 | 532.4 | 196.2 | 251 | 194.2 | 61.2 | 45 | 42.7 | 48.6 | 51.9 | 45.7
404 | 264 | 532.4 | 196.9 | 251.8 | 194.9 | 61.5 | 45.2 | 42.9 | 48.8 | 52.1 | 45.9
405 | 265 | 532.3 | 197.5 | 252.6 | 195.4 | 61.7 | 45.4 | 43.1 | 49.1 | 52.3 | 46.1
406 | 266 | 532.1 | 198.1 | 253.5 | 196 | 61.9 | 45.6 | 43.3 | 49.3 | 52.4 | 46.3
407 | 267 | 532.1 | 198.8 | 254.3 | 196.7 | 62.1 | 45.8 | 43.5 | 49.5 | 52.6 | 46.5
408 | 268 | 532 | 199.3 | 255.2 | 197.4 | 62.3 | 45.9 | 43.7 | 49.8 | 52.8 | 46.7
409 | 269 | 531.9 | 200 | 256 | 198.1 | 62.5 | 46.2 | 43.9 | 50 | 53 | 46.9
410 | 270 | 531.9 | 200.6 | 256.7 | 198.8 | 62.8 | 46.4 | 44.2 | 50.2 | 53.1 | 47.2
411 | 271 | 531.8 | 201.3 | 257.5 | 199.4 | 63 | 46.6 | 44.4 | 50.4 | 53.4 | 47.3
412 | 272 | 531.7 | 201.9 | 258.3 | 200 | 63.3 | 46.8 | 44.6 | 50.6 | 53.6 | 47.6
413 | 273 | 531.6 | 202.5 | 259.2 | 200.6 | 63.4 | 47 | 44.8 | 50.9 | 53.8 | 47.8
414 | 274 | 531.6 | 203.2 | 259.9 | 201.3 | 63.7 | 47.2 | 45 | 51.1 | 54 | 48
415 | 275 | 531.5 | 203.8 | 260.7 | 201.9 | 63.9 | 47.4 | 45.2 | 51.3 | 54.2 | 48.2
416 | 276 | 531.5 | 204.4 | 261.5 | 202.6 | 64.1 | 47.6 | 45.4 | 51.5 | 54.4 | 48.5
417 | 277 | 531.5 | 205 | 262.4 | 203.2 | 64.3 | 47.8 | 45.6 | 51.7 | 54.7 | 48.7
418 | 278 | 531.5 | 205.6 | 263.3 | 203.8 | 64.4 | 48 | 45.9 | 51.9 | 54.9 | 48.9
419 | 279 | 531.5 | 206.3 | 264.1 | 204.5 | 64.7 | 48.2 | 46.1 | 52.1 | 55.2 | 49.1
420 | 280 | 531.5 | 206.9 | 264.9 | 205.1 | 64.9 | 48.4 | 46.3 | 52.4 | 55.4 | 49.3
421 | 281 | 531.5 | 207.5 | 265.7 | 205.6 | 65 | 48.6 | 46.5 | 52.7 | 55.7 | 49.5
422 | 282 | 531.5 | 208.1 | 266.6 | 206.3 | 65.2 | 48.8 | 46.7 | 52.9 | 56 | 49.7
423 | 283 | 531.5 | 208.7 | 267.4 | 206.9 | 65.4 | 49 | 47 | 53.1 | 56.2 | 49.9
424 | 284 | 531.5 | 209.3 | 268.3 | 207.6 | 65.6 | 49.2 | 47.2 | 53.3 | 56.4 | 50.1
425 | 285 | 531.5 | 210 | 269 | 208.2 | 65.8 | 49.4 | 47.4 | 53.6 | 56.7 | 50.3
426 | 286 | 531.4 | 210.6 | 269.7 | 208.9 | 66.1 | 49.6 | 47.6 | 53.8 | 56.9 | 50.5
427 | 287 | 531.4 | 211.2 | 270.5 | 209.5 | 66.2 | 49.8 | 47.8 | 54 | 57.1 | 50.7
428 | 288 | 531.4 | 211.8 | 271.2 | 210.1 | 66.4 | 50 | 48 | 54.2 | 57.4 | 50.9
429 | 289 | 531.4 | 212.5 | 272 | 210.8 | 66.7 | 50.3 | 48.2 | 54.4 | 57.6 | 51.1
430 | 290 | 531.4 | 213.1 | 272.8 | 211.5 | 66.8 | 50.5 | 48.5 | 54.6 | 57.8 | 51.3
431 | 291 | 531.3 | 213.7 | 273.6 | 212.1 | 67 | 50.7 | 48.7 | 54.8 | 58 | 51.6
432 | 292 | 531.3 | 214.3 | 274.3 | 212.7 | 67.3 | 50.9 | 48.9 | 55.1 | 58.2 | 51.7
433 | 293 | 531.3 | 214.9 | 275.1 | 213.4 | 67.5 | 51.1 | 49.1 | 55.3 | 58.4 | 51.9
434 | 294 | 531.4 | 215.5 | 276 | 213.9 | 67.6 | 51.3 | 49.3 | 55.5 | 58.7 | 52.1
435 | 295 | 531.4 | 216.1 | 276.7 | 214.5 | 67.7 | 51.5 | 49.6 | 55.8 | 58.9 | 52.3
436 | 296 | 531.4 | 216.7 | 277.5 | 215.2 | 67.9 | 51.7 | 49.8 | 56 | 59.1 | 52.5
437 | 297 | 531.4 | 217.3 | 278.2 | 215.8 | 68.1 | 51.9 | 50 | 56.2 | 59.3 | 52.7
438 | 298 | 531.4 | 217.9 | 279 | 216.4 | 68.4 | 52.1 | 50.2 | 56.5 | 59.5 | 53
439 | 299 | 531.4 | 218.5 | 279.7 | 217 | 68.6 | 52.3 | 50.4 | 56.7 | 59.8 | 53.1
440 | 300 | 531.4 | 219.1 | 280.5 | 217.6 | 68.7 | 52.5 | 50.7 | 56.9 | 60 | 53.3
441 | 301 | 531.5 | 219.7 | 281.2 | 218.3 | 69 | 52.7 | 50.9 | 57.1 | 60.2 | 53.5
442 | 302 | 531.5 | 220.2 | 282.1 | 218.8 | 69.1 | 52.9 | 51.1 | 57.4 | 60.4 | 53.7
443 | 303 | 531.4 | 220.8 | 282.8 | 219.5 | 69.3 | 53.1 | 51.3 | 57.7 | 60.7 | 53.8
444 | 304 | 531.4 | 221.3 | 283.6 | 220 | 69.4 | 53.3 | 51.6 | 57.9 | 60.9 | 54
445 | 305 | 531.4 | 221.9 | 284.3 | 220.6 | 69.6 | 53.5 | 51.8 | 58.1 | 61.1 | 54.2
446 | 306 | 531.4 | 222.5 | 284.9 | 221.3 | 69.8 | 53.7 | 52 | 58.3 | 61.4 | 54.4
447 | 307 | 531.4 | 223.1 | 285.6 | 221.9 | 70.1 | 54 | 52.2 | 58.5 | 61.6 | 54.6
448 | 308 | 531.3 | 223.7 | 286.4 | 222.5 | 70.2 | 54.2 | 52.4 | 58.8 | 61.8 | 54.8
449 | 309 | 531.3 | 224.3 | 287.1 | 223.1 | 70.5 | 54.4 | 52.6 | 59 | 62.1 | 54.9
450 | 310 | 531.3 | 224.8 | 287.9 | 223.7 | 70.7 | 54.6 | 52.9 | 59.2 | 62.3 | 55.1
451 | 311 | 531.3 | 225.4 | 288.7 | 224.2 | 70.9 | 54.8 | 53.1 | 59.5 | 62.6 | 55.3
452 | 312 | 531.3 | 225.9 | 289.4 | 224.8 | 71.1 | 55 | 53.3 | 59.7 | 62.8 | 55.5
453 | 313 | 531.3 | 226.4 | 290 | 225.5 | 71.3 | 55.2 | 53.5 | 59.9 | 63 | 55.6
454 | 314 | 531.2 | 227 | 290.7 | 226.1 | 71.5 | 55.5 | 53.8 | 60.1 | 63.3 | 55.7
455 | 315 | 531.1 | 227.5 | 291.4 | 226.7 | 71.7 | 55.6 | 54 | 60.4 | 63.5 | 55.9
456 | 316 | 531.1 | 228 | 292.1 | 227.3 | 72 | 55.9 | 54.2 | 60.6 | 63.8 | 56.1
457 | 317 | 531.1 | 228.6 | 292.8 | 227.9 | 72.3 | 56.1 | 54.4 | 60.8 | 64 | 56.2
458 | 318 | 531.1 | 229.1 | 293.5 | 228.5 | 72.5 | 56.3 | 54.7 | 61.1 | 64.3 | 56.4
459 | 319 | 531 | 229.7 | 294.2 | 229.1 | 72.8 | 56.6 | 54.9 | 61.3 | 64.5 | 56.6
460 | 320 | 531 | 230.2 | 294.9 | 229.7 | 73 | 56.8 | 55.1 | 61.6 | 64.8 | 56.7
461 | 321 | 530.9 | 230.7 | 295.7 | 230.3 | 73.2 | 57 | 55.4 | 61.8 | 65 | 56.9
462 | 322 | 530.9 | 231.3 | 296.4 | 230.9 | 73.5 | 57.2 | 55.6 | 62 | 65.3 | 57.1
463 | 323 | 530.9 | 231.8 | 297 | 231.5 | 73.7 | 57.4 | 55.8 | 62.2 | 65.5 | 57.2
464 | 324 | 530.8 | 232.3 | 297.7 | 232 | 74 | 57.6 | 56 | 62.5 | 65.8 | 57.4
465 | 325 | 530.8 | 232.9 | 298.4 | 232.6 | 74.2 | 57.8 | 56.3 | 62.7 | 66 | 57.5
466 | 326 | 530.9 | 233.4 | 299 | 233.2 | 74.6 | 58.1 | 56.5 | 63 | 66.3 | 57.7
467 | 327 | 530.9 | 233.9 | 299.8 | 233.7 | 74.8 | 58.3 | 56.7 | 63.3 | 66.5 | 57.9
468 | 328 | 530.9 | 234.5 | 300.4 | 234.4 | 75 | 58.5 | 57 | 63.5 | 66.8 | 58
469 | 329 | 530.9 | 235 | 301.1 | 235 | 75.3 | 58.7 | 57.2 | 63.8 | 67 | 58.2
470 | 330 | 530.9 | 235.6 | 301.8 | 235.5 | 75.6 | 58.9 | 57.5 | 64 | 67.3 | 58.4
471 | 331 | 530.9 | 236.2 | 302.4 | 236.1 | 75.9 | 59.2 | 57.7 | 64.3 | 67.6 | 58.5
472 | 332 | 530.9 | 236.7 | 303.1 | 236.7 | 76.2 | 59.4 | 57.9 | 64.5 | 67.8 | 58.6
473 | 333 | 530.8 | 237.3 | 303.8 | 237.2 | 76.5 | 59.6 | 58.2 | 64.7 | 68.1 | 58.8
474 | 334 | 530.8 | 237.8 | 304.5 | 237.8 | 76.8 | 59.8 | 58.4 | 64.9 | 68.4 | 58.9
475 | 335 | 530.8 | 238.4 | 305.1 | 238.4 | 77.1 | 60.1 | 58.6 | 65.2 | 68.7 | 59.1
476 | 336 | 530.8 | 239 | 305.8 | 238.9 | 77.4 | 60.3 | 58.9 | 65.4 | 69 | 59.2
477 | 337 | 530.8 | 239.5 | 306.5 | 239.5 | 77.7 | 60.5 | 59.1 | 65.6 | 69.2 | 59.4
478 | 338 | 530.7 | 240.1 | 307.2 | 240.1 | 78 | 60.8 | 59.4 | 65.9 | 69.5 | 59.5
479 | 339 | 530.7 | 240.7 | 307.8 | 240.7 | 78.3 | 61 | 59.6 | 66.1 | 69.8 | 59.7
480 | 340 | 530.7 | 241.2 | 308.5 | 241.2 | 78.6 | 61.2 | 59.9 | 66.3 | 70.1 | 59.9
481 | 341 | 530.7 | 241.7 | 309.1 | 241.7 | 78.9 | 61.4 | 60.1 | 66.6 | 70.4 | 60
482 | 342 | 530.7 | 242.3 | 309.8 | 242.3 | 79.2 | 61.7 | 60.4 | 66.8 | 70.7 | 60.2
483 | 343 | 530.8 | 242.9 | 310.5 | 242.9 | 79.6 | 61.9 | 60.6 | 67.1 | 70.9 | 60.3
484 | 344 | 530.8 | 243.5 | 311.1 | 243.4 | 80 | 62.2 | 60.8 | 67.4 | 71.2 | 60.5
485 | 345 | 530.7 | 244 | 311.7 | 244 | 80.3 | 62.4 | 61.1 | 67.6 | 71.6 | 60.6
486 | 346 | 530.8 | 244.6 | 312.3 | 244.5 | 80.6 | 62.6 | 61.3 | 67.9 | 71.9 | 60.7
487 | 347 | 530.8 | 245.2 | 313 | 245.1 | 81 | 62.9 | 61.6 | 68.1 | 72.2 | 60.9
488 | 348 | 530.8 | 245.7 | 313.7 | 245.6 | 81.3 | 63.1 | 61.9 | 68.3 | 72.5 | 61
489 | 349 | 530.8 | 246.2 | 314.4 | 246.1 | 81.6 | 63.3 | 62.1 | 68.6 | 72.8 | 61.1
490 | 350 | 530.8 | 246.8 | 315 | 246.6 | 81.9 | 63.6 | 62.4 | 68.8 | 73.2 | 61.3
491 | 351 | 530.8 | 247.3 | 315.8 | 247.1 | 82.1 | 63.8 | 62.7 | 69.1 | 73.5 | 61.4
492 | 352 | 530.8 | 247.8 | 316.5 | 247.7 | 82.4 | 64 | 62.9 | 69.3 | 73.8 | 61.5
493 | 353 | 530.9 | 248.4 | 317.2 | 248.2 | 82.7 | 64.2 | 63.2 | 69.6 | 74.1 | 61.7
494 | 354 | 530.9 | 249 | 317.8 | 248.8 | 83.1 | 64.5 | 63.4 | 69.9 | 74.4 | 61.8
495 | 355 | 530.8 | 249.5 | 318.4 | 249.3 | 83.4 | 64.7 | 63.7 | 70.2 | 74.7 | 61.9
496 | 356 | 530.8 | 250.1 | 319 | 249.9 | 83.7 | 65 | 64 | 70.4 | 75.1 | 62
497 | 357 | 530.7 | 250.6 | 319.7 | 250.4 | 84.1 | 65.2 | 64.2 | 70.7 | 75.4 | 62.2
498 | 358 | 530.7 | 251.2 | 320.4 | 250.9 | 84.4 | 65.5 | 64.5 | 70.9 | 75.8 | 62.3
499 | 359 | 530.6 | 251.8 | 320.9 | 251.4 | 84.8 | 65.7 | 64.7 | 71.2 | 76.1 | 62.4
500 | 360 | 530.6 | 252.4 | 321.6 | 251.9 | 85.1 | 66 | 65 | 71.4 | 76.4 | 62.6
501 | 361 | 530.5 | 252.9 | 322.1 | 252.5 | 85.5 | 66.3 | 65.3 | 71.7 | 76.8 | 62.7
502 | 362 | 530.5 | 253.5 | 322.7 | 253 | 85.9 | 66.5 | 65.5 | 71.9 | 77.1 | 62.8
503 | 363 | 530.4 | 254.1 | 323.3 | 253.6 | 86.3 | 66.8 | 65.8 | 72.1 | 77.4 | 62.9
504 | 364 | 530.4 | 254.7 | 323.9 | 254.1 | 86.6 | 67.1 | 66.1 | 72.4 | 77.8 | 63.1
505 | 365 | 530.4 | 255.3 | 324.5 | 254.7 | 87 | 67.4 | 66.3 | 72.6 | 78.1 | 63.3
506 | 366 | 530.3 | 255.8 | 325.1 | 255.2 | 87.4 | 67.6 | 66.6 | 72.8 | 78.4 | 63.4
507 | 367 | 530.3 | 256.4 | 325.7 | 255.7 | 87.7 | 67.9 | 66.9 | 73.1 | 78.8 | 63.5
508 | 368 | 530.3 | 257 | 326.1 | 256.3 | 88.3 | 68.2 | 67.1 | 73.3 | 79.1 | 63.7
509 | 369 | 530.3 | 257.6 | 326.7 | 256.9 | 88.6 | 68.5 | 67.4 | 73.6 | 79.4 | 63.8
510 | 370 | 530.3 | 258.1 | 327.4 | 257.3 | 88.9 | 68.8 | 67.7 | 73.9 | 79.8 | 63.9
511 | 371 | 530.3 | 258.7 | 328 | 257.8 | 89.2 | 69 | 68 | 74.1 | 80.1 | 64.1
512 | 372 | 530.3 | 259.3 | 328.4 | 258.4 | 89.7 | 69.3 | 68.2 | 74.4 | 80.4 | 64.2
513 | 373 | 530.2 | 259.8 | 329.1 | 258.9 | 90 | 69.6 | 68.5 | 74.6 | 80.8 | 64.3
514 | 374 | 530.3 | 260.4 | 329.7 | 259.4 | 90.3 | 69.9 | 68.8 | 74.9 | 81.1 | 64.5
515 | 375 | 530.3 | 261 | 330.3 | 259.9 | 90.6 | 70.1 | 69.1 | 75.2 | 81.4 | 64.6
516 | 376 | 530.4 | 261.5 | 330.8 | 260.4 | 90.9 | 70.4 | 69.3 | 75.4 | 81.7 | 64.7
517 | 377 | 530.4 | 262.1 | 331.5 | 261 | 91.2 | 70.7 | 69.6 | 75.7 | 82.1 | 64.8
518 | 378 | 530.4 | 262.6 | 332 | 261.6 | 91.5 | 70.9 | 69.9 | 75.9 | 82.4 | 65
519 | 379 | 530.4 | 263.1 | 332.6 | 262.1 | 91.9 | 71.2 | 70.2 | 76.2 | 82.8 | 65.1
520 | 380 | 530.4 | 263.7 | 333.1 | 262.5 | 92.3 | 71.5 | 70.4 | 76.5 | 83.1 | 65.2
521 | 381 | 530.4 | 264.3 | 333.8 | 263 | 92.6 | 71.8 | 70.7 | 76.8 | 83.4 | 65.3
522 | 382 | 530.4 | 264.8 | 334.4 | 263.5 | 92.9 | 72 | 71 | 77.1 | 83.8 | 65.5
523 | 383 | 530.3 | 265.4 | 334.9 | 264 | 93.2 | 72.3 | 71.3 | 77.3 | 84.1 | 65.6
524 | 384 | 530.3 | 265.9 | 335.4 | 264.6 | 93.6 | 72.6 | 71.6 | 77.6 | 84.4 | 65.7
525 | 385 | 530.3 | 266.5 | 336 | 265.1 | 93.9 | 72.9 | 71.9 | 77.8 | 84.8 | 65.9
526 | 386 | 530.3 | 267 | 336.6 | 265.6 | 94.3 | 73.2 | 72.1 | 78.1 | 85.1 | 66
527 | 387 | 530.2 | 267.6 | 337.2 | 266.1 | 94.6 | 73.5 | 72.4 | 78.3 | 85.4 | 66.1
528 | 388 | 530.3 | 268.1 | 337.7 | 266.6 | 94.9 | 73.7 | 72.7 | 78.6 | 85.8 | 66.2
529 | 389 | 530.3 | 268.6 | 338.3 | 267.1 | 95.2 | 74 | 73 | 78.9 | 86.1 | 66.4
530 | 390 | 530.2 | 269.2 | 338.8 | 267.6 | 95.6 | 74.3 | 73.3 | 79.2 | 86.4 | 66.5
531 | 391 | 530.2 | 269.7 | 339.4 | 268.2 | 95.9 | 74.6 | 73.6 | 79.4 | 86.8 | 66.6
532 | 392 | 530.2 | 270.3 | 339.9 | 268.7 | 96.2 | 74.8 | 73.8 | 79.7 | 87.1 | 66.8
533 | 393 | 530.2 | 270.8 | 340.5 | 269.2 | 96.5 | 75.1 | 74.1 | 80 | 87.4 | 66.9
534 | 394 | 530.2 | 271.4 | 341 | 269.7 | 96.9 | 75.4 | 74.4 | 80.3 | 87.7 | 67
535 | 395 | 530.2 | 271.9 | 341.6 | 270.2 | 97.2 | 75.7 | 74.7 | 80.6 | 88.1 | 67.2
536 | 396 | 530.2 | 272.4 | 342.2 | 270.7 | 97.5 | 76 | 75 | 80.8 | 88.4 | 67.3
537 | 397 | 530.2 | 273 | 342.7 | 271.2 | 97.8 | 76.2 | 75.3 | 81.1 | 88.8 | 67.4
538 | 398 | 530.2 | 273.5 | 343.2 | 271.7 | 98.1 | 76.5 | 75.5 | 81.4 | 89.1 | 67.5
539 | 399 | 530.2 | 274 | 343.7 | 272.2 | 98.5 | 76.8 | 75.8 | 81.6 | 89.5 | 67.6
540 | 400 | 530.2 | 274.6 | 344.2 | 272.7 | 98.8 | 77.1 | 76.1 | 81.9 | 89.8 | 67.8
541 | 401 | 530.1 | 275.1 | 344.8 | 273.2 | 99.1 | 77.4 | 76.4 | 82.2 | 90.2 | 67.9
542 | 402 | 530.1 | 275.6 | 345.3 | 273.7 | 99.4 | 77.7 | 76.7 | 82.5 | 90.5 | 68
543 | 403 | 530 | 276.1 | 345.8 | 274.2 | 99.7 | 78 | 77 | 82.7 | 90.9 | 68.1
544 | 404 | 530 | 276.7 | 346.4 | 274.7 | 100 | 78.2 | 77.3 | 83 | 91.2 | 68.3
545 | 405 | 529.9 | 277.2 | 346.9 | 275.2 | 100.3 | 78.5 | 77.5 | 83.3 | 91.6 | 68.3
546 | 406 | 529.8 | 277.7 | 347.4 | 275.7 | 100.6 | 78.8 | 77.8 | 83.6 | 91.9 | 68.5
547 | 407 | 529.8 | 278.2 | 347.9 | 276.2 | 100.9 | 79.1 | 78.1 | 83.9 | 92.3 | 68.6
548 | 408 | 529.7 | 278.8 | 348.3 | 276.7 | 101.2 | 79.4 | 78.4 | 84.1 | 92.6 | 68.7
549 | 409 | 529.6 | 279.3 | 348.8 | 277.2 | 101.6 | 79.7 | 78.7 | 84.4 | 93 | 68.7
550 | 410 | 529.5 | 279.8 | 349.3 | 277.7 | 101.9 | 80 | 79 | 84.6 | 93.4 | 68.8
551 | 411 | 529.5 | 280.4 | 349.8 | 278.2 | 102.3 | 80.3 | 79.2 | 84.9 | 93.7 | 69
552 | 412 | 529.4 | 280.9 | 350.3 | 278.7 | 102.6 | 80.6 | 79.5 | 85.2 | 94.1 | 69.1
553 | 413 | 529.4 | 281.4 | 350.8 | 279.2 | 102.9 | 80.8 | 79.8 | 85.5 | 94.4 | 69.2
554 | 414 | 529.3 | 281.9 | 351.3 | 279.7 | 103.2 | 81.1 | 80.1 | 85.8 | 94.8 | 69.4
555 | 415 | 529.3 | 282.4 | 351.8 | 280.1 | 103.5 | 81.4 | 80.4 | 86 | 95.1 | 69.5
556 | 416 | 529.3 | 282.9 | 352.3 | 280.6 | 103.8 | 81.7 | 80.7 | 86.3 | 95.5 | 69.6
557 | 417 | 529.3 | 283.4 | 352.8 | 281.1 | 104.1 | 82 | 81 | 86.6 | 95.8 | 69.8
558 | 418 | 529.3 | 283.9 | 353.3 | 281.6 | 104.4 | 82.3 | 81.2 | 86.8 | 96.2 | 69.9
559 | 419 | 529.3 | 284.5 | 353.8 | 282.1 | 104.7 | 82.6 | 81.5 | 87.1 | 96.5 | 70
560 | 420 | 529.3 | 285 | 354.3 | 282.6 | 105 | 82.9 | 81.8 | 87.4 | 96.9 | 70.2
561 | 421 | 529.2 | 285.5 | 354.8 | 283.1 | 105.3 | 83.1 | 82.1 | 87.7 | 97.2 | 70.3
562 | 422 | 529.2 | 286 | 355.2 | 283.6 | 105.6 | 83.4 | 82.4 | 87.9 | 97.6 | 70.5
563 | 423 | 529.1 | 286.5 | 355.7 | 284.1 | 105.9 | 83.7 | 82.7 | 88.2 | 97.9 | 70.6
564 | 424 | 529.2 | 287 | 356.2 | 284.5 | 106.2 | 84 | 82.9 | 88.5 | 98.3 | 70.7
565 | 425 | 529.2 | 287.5 | 356.7 | 285 | 106.5 | 84.3 | 83.2 | 88.8 | 98.6 | 70.8
566 | 426 | 529.2 | 288 | 357.2 | 285.5 | 106.8 | 84.5 | 83.5 | 89 | 99 | 71
567 | 427 | 529.2 | 288.5 | 357.7 | 286.1 | 107.1 | 84.8 | 83.8 | 89.3 | 99.3 | 71.1
568 | 428 | 529.2 | 289 | 358.2 | 286.5 | 107.4 | 85.1 | 84.1 | 89.6 | 99.7 | 71.3
569 | 429 | 529.2 | 289.5 | 358.6 | 286.9 | 107.7 | 85.4 | 84.4 | 89.8 | 100 | 71.5
570 | 430 | 529.2 | 290 | 359.1 | 287.4 | 108 | 85.7 | 84.6 | 90.1 | 100.4 | 71.6
571 | 431 | 529.3 | 290.5 | 359.5 | 287.9 | 108.3 | 86 | 84.9 | 90.3 | 100.7 | 71.8
572 | 432 | 529.4 | 291 | 360 | 288.3 | 108.7 | 86.2 | 85.2 | 90.6 | 101 | 72
573 | 433 | 529.3 | 291.5 | 360.4 | 288.8 | 109.1 | 86.6 | 85.5 | 90.9 | 101.4 | 72.2
574 | 434 | 529.3 | 292 | 361 | 289.3 | 109.4 | 86.8 | 85.8 | 91.2 | 101.7 | 72.4
575 | 435 | 529.3 | 292.5 | 361.5 | 289.7 | 109.7 | 87.1 | 86 | 91.4 | 102.1 | 72.5
576 | 436 | 529.4 | 293 | 361.9 | 290.2 | 110 | 87.4 | 86.3 | 91.7 | 102.4 | 72.7
577 | 437 | 529.4 | 293.4 | 362.4 | 290.7 | 110.4 | 87.7 | 86.6 | 91.9 | 102.8 | 72.9
578 | 438 | 529.5 | 293.9 | 362.8 | 291.2 | 110.7 | 88 | 86.9 | 92.2 | 103.1 | 73.1
579 | 439 | 529.6 | 294.4 | 363.2 | 291.6 | 111.1 | 88.2 | 87.2 | 92.4 | 103.5 | 73.2
580 | 440 | 529.6 | 294.9 | 363.7 | 292.1 | 111.5 | 88.5 | 87.4 | 92.7 | 103.8 | 73.4
581 | 441 | 529.7 | 295.4 | 364.2 | 292.5 | 111.8 | 88.8 | 87.7 | 93 | 104.2 | 73.6
582 | 442 | 529.7 | 295.9 | 364.7 | 293.1 | 112.2 | 89.1 | 88 | 93.2 | 104.5 | 73.8
583 | 443 | 529.7 | 296.4 | 365 | 293.5 | 112.6 | 89.4 | 88.3 | 93.4 | 104.9 | 73.9
584 | 444 | 529.6 | 296.8 | 365.5 | 293.9 | 113 | 89.7 | 88.5 | 93.7 | 105.2 | 74.1
585 | 445 | 529.6 | 297.3 | 365.9 | 294.4 | 113.4 | 89.9 | 88.8 | 94 | 105.6 | 74.3
586 | 446 | 529.6 | 297.8 | 366.4 | 294.9 | 113.8 | 90.2 | 89.1 | 94.3 | 105.9 | 74.5
587 | 447 | 529.6 | 298.3 | 366.8 | 295.3 | 114.2 | 90.5 | 89.4 | 94.6 | 106.2 | 74.6
588 | 448 | 529.6 | 298.7 | 367.3 | 295.7 | 114.6 | 90.8 | 89.7 | 94.9 | 106.6 | 74.8
589 | 449 | 529.7 | 299.2 | 367.7 | 296.2 | 115.1 | 91.1 | 89.9 | 95.1 | 106.9 | 75
590 | 450 | 529.7 | 299.7 | 368.1 | 296.6 | 115.5 | 91.4 | 90.2 | 95.4 | 107.3 | 75.2
591 | 451 | 529.7 | 300.1 | 368.6 | 297.1 | 116 | 91.7 | 90.5 | 95.6 | 107.6 | 75.3
592 | 452 | 529.7 | 300.6 | 369.1 | 297.5 | 116.4 | 92 | 90.8 | 95.9 | 108 | 75.5
593 | 453 | 529.8 | 301.1 | 369.5 | 298 | 116.9 | 92.3 | 91.1 | 96.2 | 108.3 | 75.7
594 | 454 | 529.8 | 301.6 | 369.9 | 298.5 | 117.5 | 92.6 | 91.4 | 96.5 | 108.7 | 75.9
595 | 455 | 529.8 | 302 | 370.3 | 298.9 | 118 | 92.9 | 91.7 | 96.8 | 109.1 | 76
596 | 456 | 529.8 | 302.5 | 370.8 | 299.3 | 118.5 | 93.2 | 91.9 | 97 | 109.4 | 76.2
597 | 457 | 529.8 | 303 | 371.2 | 299.8 | 118.9 | 93.5 | 92.2 | 97.2 | 109.8 | 76.4
598 | 458 | 529.8 | 303.5 | 371.6 | 300.2 | 119.4 | 93.8 | 92.5 | 97.5 | 110.1 | 76.6
599 | 459 | 529.8 | 303.9 | 372.1 | 300.7 | 119.9 | 94.1 | 92.8 | 97.8 | 110.5 | 76.7
600 | 460 | 529.7 | 304.3 | 372.5 | 301.1 | 120.4 | 94.4 | 93.1 | 98.1 | 110.8 | 76.9
601 | 461 | 529.6 | 304.8 | 372.9 | 301.5 | 120.9 | 94.8 | 93.4 | 98.3 | 111.2 | 77.1
602 | 462 | 529.7 | 305.2 | 373.4 | 302 | 121.4 | 95.1 | 93.7 | 98.6 | 111.5 | 77.3
603 | 463 | 529.6 | 305.7 | 373.9 | 302.4 | 121.8 | 95.3 | 94 | 98.9 | 111.9 | 77.4
604 | 464 | 529.6 | 306.2 | 374.3 | 302.8 | 122.3 | 95.7 | 94.3 | 99.1 | 112.2 | 77.6
605 | 465 | 529.6 | 306.6 | 374.7 | 303.2 | 122.8 | 96 | 94.7 | 99.3 | 112.6 | 77.8
606 | 466 | 529.6 | 307.1 | 375.1 | 303.7 | 123.3 | 96.3 | 95 | 99.6 | 112.9 | 77.9
607 | 467 | 529.6 | 307.5 | 375.5 | 304.1 | 123.8 | 96.6 | 95.3 | 99.9 | 113.3 | 78.1
608 | 468 | 529.6 | 308 | 375.9 | 304.6 | 124.3 | 97 | 95.6 | 100.2 | 113.7 | 78.3
609 | 469 | 529.6 | 308.4 | 376.4 | 305 | 124.8 | 97.3 | 95.9 | 100.5 | 114 | 78.5
610 | 470 | 529.6 | 308.9 | 376.7 | 305.5 | 125.3 | 97.6 | 96.3 | 100.8 | 114.4 | 78.7
611 | 471 | 529.6 | 309.3 | 377.2 | 305.9 | 125.8 | 98 | 96.6 | 101 | 114.7 | 78.8
612 | 472 | 529.6 | 309.7 | 377.6 | 306.3 | 126.2 | 98.3 | 97 | 101.3 | 115.1 | 79
613 | 473 | 529.6 | 310.1 | 378.1 | 306.8 | 126.6 | 98.6 | 97.3 | 101.6 | 115.4 | 79.2
614 | 474 | 529.6 | 310.6 | 378.5 | 307.2 | 127.1 | 98.9 | 97.7 | 101.9 | 115.8 | 79.3
615 | 475 | 529.6 | 311 | 378.9 | 307.6 | 127.6 | 99.3 | 98 | 102.2 | 116.1 | 79.5
616 | 476 | 529.6 | 311.5 | 379.4 | 308.1 | 128.1 | 99.6 | 98.4 | 102.5 | 116.5 | 79.8
617 | 477 | 529.5 | 311.9 | 379.7 | 308.5 | 128.6 | 100 | 98.7 | 102.8 | 116.8 | 79.9
618 | 478 | 529.5 | 312.4 | 380.2 | 309 | 129.1 | 100.3 | 99.1 | 103.1 | 117.2 | 80.1
619 | 479 | 529.5 | 312.8 | 380.6 | 309.3 | 129.6 | 100.6 | 99.5 | 103.4 | 117.5 | 80.3
620 | 480 | 529.5 | 313.2 | 381 | 309.8 | 130.1 | 101 | 99.9 | 103.8 | 117.9 | 80.5
621 | 481 | 529.5 | 313.7 | 381.3 | 310.2 | 130.6 | 101.4 | 100.3 | 104.1 | 118.2 | 80.6
622 | 482 | 529.4 | 314.1 | 381.7 | 310.6 | 131.1 | 101.7 | 100.7 | 104.4 | 118.6 | 80.8
623 | 483 | 529.4 | 314.5 | 382.1 | 311 | 131.6 | 102.1 | 101.1 | 104.7 | 119 | 81.1
624 | 484 | 529.4 | 314.9 | 382.5 | 311.4 | 132 | 102.4 | 101.5 | 105.1 | 119.3 | 81.2
625 | 485 | 529.3 | 315.4 | 382.9 | 311.8 | 132.5 | 102.8 | 101.9 | 105.4 | 119.7 | 81.4
626 | 486 | 529.2 | 315.8 | 383.3 | 312.2 | 133 | 103.2 | 102.3 | 105.7 | 120 | 81.6
627 | 487 | 529.2 | 316.2 | 383.6 | 312.6 | 133.4 | 103.6 | 102.7 | 106.1 | 120.4 | 81.8
628 | 488 | 529.1 | 316.6 | 384 | 312.9 | 133.9 | 103.9 | 103.1 | 106.4 | 120.7 | 82
629 | 489 | 529 | 317.1 | 384.4 | 313.4 | 134.4 | 104.4 | 103.5 | 106.8 | 121.1 | 82.2
630 | 490 | 529 | 317.5 | 384.8 | 313.8 | 134.8 | 104.7 | 104 | 107.1 | 121.5 | 82.4
631 | 491 | 528.9 | 317.9 | 385.2 | 314.2 | 135.3 | 105.1 | 104.4 | 107.5 | 121.8 | 82.5
632 | 492 | 528.8 | 318.4 | 385.5 | 314.6 | 135.8 | 105.6 | 104.8 | 107.8 | 122.2 | 82.7
633 | 493 | 528.8 | 318.8 | 385.9 | 315 | 136.2 | 106 | 105.3 | 108.1 | 122.6 | 82.9
634 | 494 | 528.8 | 319.2 | 386.3 | 315.4 | 136.7 | 106.4 | 105.7 | 108.4 | 122.9 | 83.2
635 | 495 | 528.8 | 319.6 | 386.6 | 315.9 | 137.2 | 106.8 | 106.1 | 108.8 | 123.3 | 83.3
636 | 496 | 528.8 | 320 | 387 | 316.3 | 137.7 | 107.2 | 106.6 | 109.1 | 123.6 | 83.5
637 | 497 | 528.8 | 320.4 | 387.4 | 316.7 | 138.2 | 107.7 | 107 | 109.5 | 124 | 83.7
638 | 498 | 528.7 | 320.8 | 387.8 | 317.1 | 138.8 | 108.1 | 107.4 | 109.9 | 124.4 | 83.9
639 | 499 | 528.7 | 321.3 | 388.1 | 317.5 | 139.3 | 108.5 | 107.9 | 110.2 | 124.7 | 84.1
640 | 500 | 528.6 | 321.7 | 388.5 | 317.8 | 139.9 | 109 | 108.3 | 110.5 | 125.1 | 84.3
641 | 501 | 528.6 | 322.1 | 388.9 | 318.2 | 140.5 | 109.4 | 108.7 | 110.9 | 125.4 | 84.5
642 | 502 | 528.5 | 322.5 | 389.2 | 318.6 | 141.1 | 109.8 | 109.1 | 111.3 | 125.8 | 84.7
643 | 503 | 528.5 | 322.9 | 389.6 | 319 | 141.7 | 110.3 | 109.6 | 111.7 | 126.1 | 84.9
644 | 504 | 528.4 | 323.3 | 389.9 | 319.4 | 142.4 | 110.7 | 110 | 112.1 | 126.5 | 85.1
645 | 505 | 528.4 | 323.7 | 390.2 | 319.8 | 143 | 111.2 | 110.4 | 112.4 | 126.9 | 85.3
646 | 506 | 528.4 | 324.1 | 390.6 | 320.2 | 143.5 | 111.6 | 110.8 | 112.8 | 127.2 | 85.5
647 | 507 | 528.3 | 324.5 | 391 | 320.5 | 144.1 | 112 | 111.3 | 113.2 | 127.6 | 85.7
648 | 508 | 528.3 | 324.9 | 391.3 | 321 | 144.6 | 112.4 | 111.7 | 113.6 | 127.9 | 85.9
649 | 509 | 528.3 | 325.3 | 391.6 | 321.4 | 145.2 | 112.9 | 112.1 | 113.9 | 128.3 | 86.1
650 | 510 | 528.2 | 325.8 | 392 | 321.8 | 145.7 | 113.3 | 112.5 | 114.3 | 128.7 | 86.3
651 | 511 | 528.2 | 326.1 | 392.5 | 322.1 | 146.2 | 113.7 | 112.9 | 114.6 | 129 | 86.5
652 | 512 | 528.2 | 326.5 | 392.8 | 322.5 | 146.8 | 114.1 | 113.3 | 115 | 129.4 | 86.7
653 | 513 | 528.2 | 326.9 | 393 | 322.9 | 147.3 | 114.6 | 113.7 | 115.3 | 129.7 | 86.9
654 | 514 | 528.2 | 327.3 | 393.4 | 323.3 | 147.8 | 115 | 114.2 | 115.7 | 130.1 | 87.1
655 | 515 | 528.2 | 327.7 | 393.8 | 323.7 | 148.3 | 115.4 | 114.6 | 116 | 130.4 | 87.3
656 | 516 | 528.2 | 328.1 | 394.1 | 324.1 | 148.8 | 115.8 | 115 | 116.4 | 130.8 | 87.5
657 | 517 | 528.2 | 328.5 | 394.4 | 324.5 | 149.3 | 116.3 | 115.4 | 116.7 | 131.2 | 87.7
658 | 518 | 528.2 | 328.9 | 394.8 | 324.8 | 149.7 | 116.7 | 115.8 | 117.1 | 131.5 | 87.9
659 | 519 | 528.2 | 329.3 | 395.1 | 325.2 | 150.2 | 117.1 | 116.2 | 117.5 | 131.8 | 88.2
660 | 520 | 528.3 | 329.7 | 395.5 | 325.6 | 150.6 | 117.5 | 116.7 | 117.8 | 132.2 | 88.4
661 | 521 | 528.2 | 330.1 | 395.8 | 326 | 151.1 | 117.9 | 117.1 | 118.1 | 132.5 | 88.6
662 | 522 | 528.3 | 330.5 | 396.1 | 326.4 | 151.7 | 118.3 | 117.5 | 118.5 | 132.9 | 88.8
663 | 523 | 528.3 | 330.9 | 396.4 | 326.7 | 152.2 | 118.8 | 117.9 | 118.8 | 133.2 | 89.1
664 | 524 | 528.3 | 331.2 | 396.8 | 327.1 | 152.7 | 119.2 | 118.3 | 119.2 | 133.5 | 89.3
665 | 525 | 528.3 | 331.6 | 397.1 | 327.5 | 153.2 | 119.6 | 118.7 | 119.6 | 133.8 | 89.6
666 | 526 | 528.3 | 332 | 397.5 | 327.8 | 153.7 | 120 | 119.1 | 119.9 | 134.1 | 89.8
667 | 527 | 528.3 | 332.4 | 397.8 | 328.2 | 154.2 | 120.5 | 119.6 | 120.3 | 134.4 | 90
668 | 528 | 528.3 | 332.7 | 398.1 | 328.6 | 154.6 | 120.9 | 120 | 120.7 | 134.7 | 90.3
669 | 529 | 528.4 | 333.1 | 398.5 | 328.9 | 155.1 | 121.3 | 120.4 | 121.1 | 135.1 | 90.5
670 | 530 | 528.4 | 333.5 | 398.8 | 329.3 | 155.6 | 121.7 | 120.8 | 121.4 | 135.4 | 90.8
671 | 531 | 528.4 | 333.9 | 399.2 | 329.7 | 156.1 | 122.1 | 121.2 | 121.8 | 135.7 | 91
672 | 532 | 528.4 | 334.3 | 399.5 | 330 | 156.6 | 122.5 | 121.6 | 122.2 | 136 | 91.3
673 | 533 | 528.4 | 334.6 | 399.8 | 330.4 | 157.1 | 123 | 122 | 122.5 | 136.3 | 91.5
674 | 534 | 528.4 | 335 | 400.2 | 330.7 | 157.6 | 123.4 | 122.5 | 122.9 | 136.6 | 91.8
675 | 535 | 528.5 | 335.4 | 400.5 | 331.1 | 158.1 | 123.8 | 122.9 | 123.3 | 136.9 | 92
676 | 536 | 528.5 | 335.7 | 400.8 | 331.5 | 158.6 | 124.2 | 123.3 | 123.7 | 137.2 | 92.3
677 | 537 | 528.5 | 336.1 | 401.1 | 331.8 | 159.1 | 124.6 | 123.7 | 124.1 | 137.6 | 92.5
678 | 538 | 528.5 | 336.5 | 401.4 | 332.2 | 159.6 | 125.1 | 124.1 | 124.4 | 137.9 | 92.8
679 | 539 | 528.5 | 336.9 | 401.7 | 332.5 | 160.1 | 125.5 | 124.5 | 124.8 | 138.2 | 93
680 | 540 | 528.5 | 337.2 | 402.1 | 332.9 | 160.5 | 125.9 | 124.9 | 125.2 | 138.5 | 93.3
681 | 541 | 528.5 | 337.6 | 402.4 | 333.3 | 161 | 126.3 | 125.3 | 125.6 | 138.8 | 93.5
682 | 542 | 528.5 | 338 | 402.7 | 333.6 | 161.5 | 126.7 | 125.8 | 126 | 139.2 | 93.8
683 | 543 | 528.6 | 338.3 | 403.1 | 334 | 162 | 127.1 | 126.2 | 126.3 | 139.5 | 94.1
684 | 544 | 528.6 | 338.7 | 403.3 | 334.4 | 162.6 | 127.6 | 126.6 | 126.7 | 139.8 | 94.3
685 | 545 | 528.5 | 339.1 | 403.6 | 334.7 | 163 | 128 | 127 | 127 | 140.1 | 94.6
686 | 546 | 528.5 | 339.4 | 404 | 335.1 | 163.5 | 128.4 | 127.4 | 127.5 | 140.4 | 94.8
687 | 547 | 528.5 | 339.8 | 404.3 | 335.4 | 164 | 128.8 | 127.8 | 127.9 | 140.7 | 95.1
688 | 548 | 528.5 | 340.2 | 404.5 | 335.8 | 164.5 | 129.3 | 128.2 | 128.3 | 141.1 | 95.3
689 | 549 | 528.5 | 340.5 | 404.8 | 336.2 | 165 | 129.7 | 128.7 | 128.6 | 141.4 | 95.6
690 | 550 | 528.5 | 340.9 | 405.1 | 336.5 | 165.5 | 130.1 | 129.1 | 129 | 141.7 | 95.9
691 | 551 | 528.5 | 341.2 | 405.5 | 336.9 | 165.9 | 130.5 | 129.5 | 129.4 | 142 | 96.1
692 | 552 | 528.5 | 341.6 | 405.8 | 337.2 | 166.4 | 130.9 | 129.9 | 129.8 | 142.4 | 96.3
693 | 553 | 528.5 | 341.9 | 406.1 | 337.5 | 166.9 | 131.3 | 130.3 | 130.2 | 142.7 | 96.6
694 | 554 | 528.6 | 342.2 | 406.4 | 337.9 | 167.3 | 131.7 | 130.7 | 130.6 | 143 | 96.8
695 | 555 | 528.6 | 342.6 | 406.7 | 338.2 | 167.9 | 132.1 | 131.2 | 131 | 143.3 | 97.1
696 | 556 | 528.6 | 343 | 407 | 338.6 | 168.3 | 132.6 | 131.6 | 131.4 | 143.7 | 97.3
697 | 557 | 528.6 | 343.3 | 407.3 | 338.9 | 168.8 | 133 | 132 | 131.8 | 144 | 97.6
698 | 558 | 528.6 | 343.6 | 407.7 | 339.3 | 169.3 | 133.4 | 132.4 | 132.2 | 144.3 | 97.8
699 | 559 | 528.6 | 344 | 407.9 | 339.7 | 169.8 | 133.8 | 132.8 | 132.7 | 144.6 | 98.1
700 | 560 | 528.6 | 344.4 | 408.2 | 340 | 170.3 | 134.2 | 133.3 | 133.1 | 144.9 | 98.4
701 | 561 | 528.6 | 344.7 | 408.5 | 340.3 | 170.8 | 134.6 | 133.7 | 133.5 | 145.2 | 98.6
702 | 562 | 528.5 | 345 | 408.8 | 340.6 | 171.3 | 135 | 134.1 | 133.8 | 145.6 | 98.9
703 | 563 | 528.5 | 345.4 | 409.1 | 340.9 | 171.8 | 135.5 | 134.5 | 134.2 | 145.9 | 99.2
704 | 564 | 528.4 | 345.7 | 409.4 | 341.3 | 172.2 | 135.9 | 134.9 | 134.6 | 146.2 | 99.5
705 | 565 | 528.4 | 346.1 | 409.6 | 341.7 | 172.7 | 136.3 | 135.3 | 135 | 146.5 | 99.7
706 | 566 | 528.4 | 346.4 | 409.9 | 342 | 173.2 | 136.7 | 135.7 | 135.4 | 146.9 | 100
707 | 567 | 528.4 | 346.8 | 410.2 | 342.3 | 173.7 | 137.1 | 136.2 | 135.9 | 147.2 | 100.3
708 | 568 | 528.4 | 347.1 | 410.5 | 342.7 | 174.3 | 137.6 | 136.6 | 136.2 | 147.5 | 100.6
709 | 569 | 528.4 | 347.5 | 410.8 | 343 | 174.7 | 138 | 137 | 136.6 | 147.8 | 100.9
710 | 570 | 528.4 | 347.8 | 411 | 343.3 | 175.3 | 138.4 | 137.4 | 137 | 148.2 | 101.2
711 | 571 | 528.4 | 348.1 | 411.3 | 343.6 | 175.7 | 138.8 | 137.8 | 137.4 | 148.5 | 101.5
712 | 572 | 528.3 | 348.5 | 411.6 | 344 | 176.2 | 139.2 | 138.2 | 137.8 | 148.8 | 101.8
713 | 573 | 528.3 | 348.8 | 411.8 | 344.3 | 176.7 | 139.6 | 138.6 | 138.1 | 149.2 | 102.1
714 | 574 | 528.4 | 349.1 | 412.1 | 344.7 | 177.2 | 140.1 | 139 | 138.5 | 149.5 | 102.4
715 | 575 | 528.4 | 349.5 | 412.5 | 345 | 177.7 | 140.4 | 139.5 | 138.9 | 149.9 | 102.7
716 | 576 | 528.3 | 349.8 | 412.7 | 345.3 | 178.1 | 140.9 | 139.9 | 139.3 | 150.2 | 103
717 | 577 | 528.4 | 350.1 | 413 | 345.6 | 178.6 | 141.3 | 140.3 | 139.6 | 150.6 | 103.2
718 | 578 | 528.4 | 350.4 | 413.4 | 345.9 | 179 | 141.7 | 140.7 | 140 | 151 | 103.5
719 | 579 | 528.4 | 350.8 | 413.6 | 346.3 | 179.5 | 142.1 | 141.1 | 140.4 | 151.3 | 103.8
720 | 580 | 528.5 | 351.1 | 413.9 | 346.6 | 180 | 142.5 | 141.6 | 140.8 | 151.6 | 104.1
721 | 581 | 528.5 | 351.4 | 414.2 | 346.9 | 180.5 | 142.9 | 142 | 141.2 | 152 | 104.4
722 | 582 | 528.6 | 351.7 | 414.5 | 347.2 | 180.9 | 143.3 | 142.4 | 141.6 | 152.3 | 104.7
723 | 583 | 528.6 | 352.1 | 414.7 | 347.6 | 181.4 | 143.8 | 142.8 | 142 | 152.7 | 105
724 | 584 | 528.6 | 352.4 | 415 | 347.9 | 181.9 | 144.2 | 143.2 | 142.4 | 153.1 | 105.3
725 | 585 | 528.6 | 352.7 | 415.3 | 348.2 | 182.4 | 144.6 | 143.6 | 142.8 | 153.4 | 105.6
726 | 586 | 528.6 | 353.1 | 415.5 | 348.5 | 182.9 | 145 | 144 | 143.1 | 153.8 | 105.8
727 | 587 | 528.6 | 353.4 | 415.8 | 348.8 | 183.3 | 145.4 | 144.4 | 143.6 | 154.1 | 106.1
728 | 588 | 528.6 | 353.7 | 416.1 | 349.1 | 183.8 | 145.8 | 144.8 | 144 | 154.5 | 106.4
729 | 589 | 528.6 | 354 | 416.3 | 349.4 | 184.3 | 146.2 | 145.3 | 144.4 | 154.8 | 106.7
730 | 590 | 528.6 | 354.4 | 416.6 | 349.8 | 184.8 | 146.6 | 145.7 | 144.8 | 155.2 | 107
731 | 591 | 528.5 | 354.7 | 416.8 | 350.1 | 185.3 | 147.1 | 146.1 | 145.1 | 155.6 | 107.3
732 | 592 | 528.5 | 355 | 417.1 | 350.4 | 185.8 | 147.5 | 146.5 | 145.5 | 156 | 107.6
733 | 593 | 528.5 | 355.3 | 417.4 | 350.7 | 186.2 | 147.9 | 146.9 | 145.9 | 156.4 | 107.9
734 | 594 | 528.5 | 355.6 | 417.6 | 351 | 186.7 | 148.3 | 147.3 | 146.3 | 156.8 | 108.2
735 | 595 | 528.4 | 355.9 | 417.9 | 351.3 | 187.2 | 148.7 | 147.7 | 146.8 | 157.3 | 108.5
736 | 596 | 528.4 | 356.3 | 418.1 | 351.6 | 187.7 | 149.1 | 148.1 | 147.2 | 157.8 | 108.8
737 | 597 | 528.5 | 356.6 | 418.4 | 351.9 | 188.2 | 149.5 | 148.6 | 147.5 | 158.3 | 109.1
738 | 598 | 528.5 | 356.9 | 418.7 | 352.2 | 188.6 | 149.9 | 149 | 147.9 | 158.8 | 109.4
739 | 599 | 528.4 | 357.2 | 419 | 352.5 | 189.1 | 150.3 | 149.4 | 148.3 | 159.3 | 109.8
740 | 600 | 528.4 | 357.5 | 419.2 | 352.8 | 189.5 | 150.7 | 149.8 | 148.7 | 159.9 | 110.1
741 | 601 | 528.4 | 357.8 | 419.5 | 353.2 | 190 | 151.2 | 150.2 | 149.1 | 160.4 | 110.4
742 | 602 | 528.4 | 358.1 | 419.7 | 353.4 | 190.5 | 151.6 | 150.6 | 149.5 | 160.8 | 110.7
743 | 603 | 528.4 | 358.4 | 420 | 353.7 | 191 | 152 | 151 | 149.9 | 161.3 | 111.1
744 | 604 | 528.3 | 358.7 | 420.3 | 354 | 191.5 | 152.4 | 151.5 | 150.3 | 161.8 | 111.4
745 | 605 | 528.3 | 359.1 | 420.5 | 354.3 | 191.9 | 152.8 | 151.9 | 150.7 | 162.3 | 111.7
746 | 606 | 528.3 | 359.3 | 420.8 | 354.6 | 192.4 | 153.2 | 152.3 | 151.2 | 162.8 | 112.1
747 | 607 | 528.3 | 359.7 | 421 | 355 | 192.9 | 153.6 | 152.7 | 151.6 | 163.2 | 112.5
748 | 608 | 528.4 | 360 | 421.2 | 355.3 | 193.4 | 154 | 153.1 | 152 | 163.7 | 112.8
749 | 609 | 528.3 | 360.3 | 421.5 | 355.6 | 193.8 | 154.4 | 153.5 | 152.4 | 164.2 | 113.3
750 | 610 | 528.4 | 360.6 | 421.7 | 356 | 194.3 | 154.8 | 153.9 | 152.8 | 164.6 | 113.7
751 | 611 | 528.4 | 360.9 | 422 | 356.2 | 194.8 | 155.3 | 154.3 | 153.2 | 165.1 | 114.2
752 | 612 | 528.4 | 361.2 | 422.2 | 356.5 | 195.2 | 155.7 | 154.8 | 153.7 | 165.6 | 114.7
753 | 613 | 528.4 | 361.5 | 422.5 | 356.7 | 195.6 | 156 | 155.2 | 154.1 | 166 | 115.2
754 | 614 | 528.4 | 361.8 | 422.7 | 357 | 196.1 | 156.5 | 155.6 | 154.5 | 166.4 | 115.7
755 | 615 | 528.3 | 362.1 | 422.9 | 357.2 | 196.5 | 156.9 | 156 | 154.9 | 166.9 | 116.2
756 | 616 | 528.3 | 362.4 | 423.2 | 357.5 | 197 | 157.3 | 156.4 | 155.3 | 167.3 | 116.7
757 | 617 | 528.3 | 362.7 | 423.4 | 357.8 | 197.5 | 157.7 | 156.8 | 155.7 | 167.7 | 117.2
758 | 618 | 528.3 | 363 | 423.7 | 358.2 | 197.9 | 158.1 | 157.3 | 156.1 | 168.2 | 117.5
759 | 619 | 528.3 | 363.3 | 423.9 | 358.5 | 198.4 | 158.5 | 157.7 | 156.6 | 168.6 | 117.9
760 | 620 | 528.2 | 363.6 | 424.2 | 358.7 | 198.8 | 158.9 | 158.1 | 157 | 169 | 118.3
761 | 621 | 528.2 | 363.9 | 424.4 | 359 | 199.3 | 159.4 | 158.5 | 157.3 | 169.4 | 118.6
762 | 622 | 528.2 | 364.2 | 424.6 | 359.3 | 199.7 | 159.7 | 158.9 | 157.7 | 169.9 | 118.9
763 | 623 | 528.2 | 364.5 | 424.9 | 359.5 | 200.1 | 160.1 | 159.4 | 158.1 | 170.3 | 119.2
764 | 624 | 528.2 | 364.7 | 425.1 | 359.8 | 200.6 | 160.5 | 159.8 | 158.5 | 170.7 | 119.6
765 | 625 | 528.2 | 365 | 425.3 | 360.1 | 201 | 161 | 160.2 | 158.9 | 171.1 | 119.9
766 | 626 | 528.2 | 365.3 | 425.6 | 360.4 | 201.5 | 161.4 | 160.6 | 159.3 | 171.5 | 120.2
767 | 627 | 528.1 | 365.6 | 425.8 | 360.7 | 201.9 | 161.8 | 161 | 159.7 | 171.9 | 120.5
768 | 628 | 528.1 | 365.9 | 426.1 | 360.9 | 202.4 | 162.2 | 161.4 | 160.1 | 172.4 | 120.8
769 | 629 | 528.1 | 366.2 | 426.3 | 361.2 | 202.8 | 162.6 | 161.9 | 160.5 | 172.8 | 121.1
770 | 630 | 528.1 | 366.5 | 426.5 | 361.5 | 203.3 | 163 | 162.3 | 160.9 | 173.2 | 121.4
771 | 631 | 528.1 | 366.8 | 426.7 | 361.8 | 203.7 | 163.4 | 162.7 | 161.3 | 173.6 | 121.7
772 | 632 | 528 | 367.1 | 426.9 | 362.1 | 204.2 | 163.8 | 163.1 | 161.7 | 174 | 122
773 | 633 | 528 | 367.4 | 427.2 | 362.3 | 204.6 | 164.2 | 163.5 | 162.2 | 174.4 | 122.3
774 | 634 | 527.9 | 367.6 | 427.4 | 362.6 | 205 | 164.6 | 163.9 | 162.6 | 174.8 | 122.6
775 | 635 | 527.9 | 367.9 | 427.6 | 362.9 | 205.4 | 165 | 164.3 | 163 | 175.2 | 122.9
776 | 636 | 527.9 | 368.2 | 427.8 | 363.1 | 205.9 | 165.4 | 164.7 | 163.5 | 175.6 | 123.2
777 | 637 | 527.9 | 368.5 | 428.1 | 363.4 | 206.3 | 165.8 | 165.2 | 163.9 | 176 | 123.5
778 | 638 | 527.9 | 368.7 | 428.3 | 363.7 | 206.6 | 166.2 | 165.6 | 164.3 | 176.4 | 123.8
779 | 639 | 527.9 | 369 | 428.5 | 363.9 | 207.1 | 166.6 | 166 | 164.7 | 176.8 | 124
780 | 640 | 528 | 369.3 | 428.8 | 364.2 | 207.5 | 167 | 166.4 | 165.1 | 177.2 | 124.4
781 | 641 | 527.9 | 369.6 | 429 | 364.5 | 207.9 | 167.4 | 166.8 | 165.5 | 177.6 | 124.7
782 | 642 | 527.9 | 369.9 | 429.2 | 364.7 | 208.4 | 167.8 | 167.2 | 165.9 | 178 | 125
783 | 643 | 527.8 | 370.1 | 429.4 | 365 | 208.8 | 168.2 | 167.6 | 166.3 | 178.4 | 125.3
784 | 644 | 527.8 | 370.4 | 429.6 | 365.3 | 209.1 | 168.6 | 168.1 | 166.8 | 178.8 | 125.7
785 | 645 | 527.8 | 370.7 | 429.9 | 365.5 | 209.5 | 169 | 168.5 | 167.2 | 179.2 | 126
786 | 646 | 527.7 | 371 | 430.1 | 365.8 | 210 | 169.4 | 168.9 | 167.7 | 179.6 | 126.4
787 | 647 | 527.7 | 371.2 | 430.3 | 366.1 | 210.4 | 169.8 | 169.3 | 168 | 180 | 126.8
788 | 648 | 527.7 | 371.5 | 430.6 | 366.3 | 210.7 | 170.2 | 169.7 | 168.5 | 180.4 | 127.2
789 | 649 | 527.6 | 371.8 | 430.7 | 366.6 | 211.1 | 170.6 | 170.1 | 168.9 | 180.8 | 127.6
790 | 650 | 527.7 | 372.1 | 430.9 | 366.9 | 211.5 | 171 | 170.5 | 169.4 | 181.2 | 128
791 | 651 | 527.7 | 372.4 | 431.2 | 367.1 | 211.9 | 171.4 | 170.9 | 169.8 | 181.6 | 128.4
792 | 652 | 527.6 | 372.6 | 431.4 | 367.4 | 212.3 | 171.8 | 171.3 | 170.3 | 182 | 128.7
793 | 653 | 527.6 | 372.9 | 431.6 | 367.7 | 212.7 | 172.2 | 171.7 | 170.7 | 182.4 | 129.2
794 | 654 | 527.5 | 373.2 | 431.8 | 367.9 | 213.1 | 172.6 | 172.1 | 171.2 | 182.8 | 129.6
795 | 655 | 527.6 | 373.4 | 432 | 368.2 | 213.4 | 173 | 172.5 | 171.6 | 183.1 | 129.9
796 | 656 | 527.5 | 373.7 | 432.2 | 368.5 | 213.8 | 173.4 | 173 | 172.1 | 183.5 | 130.3
797 | 657 | 527.5 | 374 | 432.4 | 368.7 | 214.2 | 173.8 | 173.4 | 172.5 | 183.9 | 130.7
798 | 658 | 527.6 | 374.2 | 432.7 | 368.9 | 214.6 | 174.2 | 173.8 | 172.9 | 184.3 | 131.1
799 | 659 | 527.6 | 374.5 | 432.9 | 369.2 | 214.9 | 174.5 | 174.2 | 173.4 | 184.6 | 131.4
800 | 660 | 527.6 | 374.8 | 433.1 | 369.4 | 215.3 | 174.9 | 174.6 | 173.8 | 185 | 131.8
801 | 661 | 527.6 | 375 | 433.3 | 369.7 | 215.7 | 175.3 | 175 | 174.3 | 185.3 | 132.1
802 | 662 | 527.6 | 375.3 | 433.5 | 369.9 | 216 | 175.7 | 175.4 | 174.7 | 185.7 | 132.4
803 | 663 | 527.6 | 375.5 | 433.7 | 370.2 | 216.4 | 176.1 | 175.8 | 175.2 | 186 | 132.7
804 | 664 | 527.6 | 375.8 | 434 | 370.5 | 216.7 | 176.5 | 176.2 | 175.6 | 186.4 | 133
805 | 665 | 527.6 | 376 | 434.2 | 370.7 | 217 | 176.9 | 176.6 | 176.1 | 186.7 | 133.3
806 | 666 | 527.7 | 376.3 | 434.4 | 370.9 | 217.4 | 177.3 | 177 | 176.5 | 187.1 | 133.5
807 | 667 | 527.7 | 376.6 | 434.6 | 371.2 | 217.7 | 177.7 | 177.4 | 177 | 187.4 | 133.8
808 | 668 | 527.7 | 376.8 | 434.8 | 371.5 | 218.1 | 178.1 | 177.8 | 177.4 | 187.8 | 134.1
809 | 669 | 527.7 | 377.1 | 435 | 371.7 | 218.4 | 178.5 | 178.2 | 177.9 | 188.1 | 134.4
810 | 670 | 527.7 | 377.3 | 435.2 | 372 | 218.7 | 178.9 | 178.6 | 178.4 | 188.5 | 134.5
811 | 671 | 527.7 | 377.6 | 435.4 | 372.2 | 219.1 | 179.2 | 179 | 178.8 | 188.8 | 134.7
812 | 672 | 527.7 | 377.8 | 435.7 | 372.4 | 219.4 | 179.6 | 179.4 | 179.3 | 189.1 | 135
813 | 673 | 527.6 | 378.1 | 435.8 | 372.7 | 219.8 | 180 | 179.8 | 179.8 | 189.5 | 135.2
814 | 674 | 527.6 | 378.3 | 436 | 372.9 | 220.1 | 180.4 | 180.2 | 180.2 | 189.8 | 135.4
815 | 675 | 527.7 | 378.6 | 436.2 | 373.2 | 220.5 | 180.8 | 180.6 | 180.7 | 190.2 | 135.6
816 | 676 | 527.6 | 378.9 | 436.4 | 373.4 | 220.8 | 181.2 | 181 | 181.1 | 190.5 | 135.8
817 | 677 | 527.6 | 379.1 | 436.6 | 373.7 | 221.1 | 181.6 | 181.4 | 181.6 | 190.8 | 136
818 | 678 | 527.5 | 379.4 | 436.8 | 374 | 221.5 | 182 | 181.8 | 182 | 191.1 | 136.2
819 | 679 | 527.5 | 379.6 | 437 | 374.2 | 221.8 | 182.4 | 182.2 | 182.5 | 191.4 | 136.4
820 | 680 | 527.5 | 379.9 | 437.2 | 374.4 | 222.2 | 182.8 | 182.6 | 183 | 191.7 | 136.7
821 | 681 | 527.4 | 380.1 | 437.4 | 374.7 | 222.5 | 183.1 | 183 | 183.5 | 192.1 | 136.9
822 | 682 | 527.3 | 380.4 | 437.6 | 375 | 222.9 | 183.5 | 183.4 | 184 | 192.4 | 137.1
823 | 683 | 527.3 | 380.6 | 437.8 | 375.2 | 223.2 | 183.9 | 183.8 | 184.5 | 192.7 | 137.4
824 | 684 | 527.3 | 380.9 | 438 | 375.5 | 223.5 | 184.3 | 184.2 | 184.9 | 193 | 137.6
825 | 685 | 527.3 | 381.1 | 438.2 | 375.7 | 223.9 | 184.7 | 184.6 | 185.3 | 193.4 | 137.8
826 | 686 | 527.2 | 381.4 | 438.3 | 375.9 | 224.3 | 185.1 | 184.9 | 185.8 | 193.7 | 138
827 | 687 | 527.2 | 381.6 | 438.5 | 376.2 | 224.6 | 185.5 | 185.3 | 186.2 | 194 | 138.2
828 | 688 | 527.2 | 381.9 | 438.7 | 376.4 | 225 | 185.8 | 185.7 | 186.6 | 194.4 | 138.4
829 | 689 | 527.1 | 382.1 | 438.9 | 376.6 | 225.3 | 186.2 | 186.1 | 187.1 | 194.7 | 138.6
830 | 690 | 527.1 | 382.3 | 439.1 | 376.9 | 225.6 | 186.6 | 186.5 | 187.6 | 195 | 138.9
831 | 691 | 527 | 382.6 | 439.2 | 377.1 | 226 | 187 | 186.9 | 188 | 195.4 | 139.1
832 | 692 | 527 | 382.8 | 439.4 | 377.4 | 226.3 | 187.4 | 187.3 | 188.3 | 195.7 | 139.4
833 | 693 | 527 | 383.1 | 439.6 | 377.6 | 226.7 | 187.8 | 187.7 | 188.7 | 196 | 139.7
834 | 694 | 526.9 | 383.3 | 439.8 | 377.8 | 227 | 188.2 | 188.1 | 189.2 | 196.3 | 140.1
835 | 695 | 527 | 383.6 | 439.9 | 378 | 227.4 | 188.5 | 188.4 | 189.6 | 196.7 | 140.4
836 | 696 | 527 | 383.8 | 440.1 | 378.3 | 227.7 | 188.9 | 188.8 | 190 | 197 | 140.8
837 | 697 | 527 | 384 | 440.3 | 378.5 | 228 | 189.3 | 189.2 | 190.5 | 197.4 | 141.2
838 | 698 | 527 | 384.3 | 440.5 | 378.7 | 228.3 | 189.7 | 189.6 | 190.9 | 197.7 | 141.5
839 | 699 | 527 | 384.5 | 440.7 | 379 | 228.6 | 190.1 | 190 | 191.4 | 198.1 | 141.9
840 | 700 | 527.1 | 384.7 | 440.9 | 379.2 | 228.9 | 190.4 | 190.4 | 191.9 | 198.4 | 142.2
841 | 701 | 527.1 | 385 | 441.1 | 379.4 | 229.3 | 190.8 | 190.7 | 192.3 | 198.8 | 142.6
842 | 702 | 527.1 | 385.2 | 441.3 | 379.7 | 229.6 | 191.2 | 191.1 | 192.7 | 199.2 | 143
843 | 703 | 527.1 | 385.4 | 441.4 | 379.9 | 229.9 | 191.6 | 191.5 | 193.2 | 199.5 | 143.4
844 | 704 | 527.2 | 385.7 | 441.6 | 380.1 | 230.2 | 191.9 | 191.9 | 193.6 | 199.9 | 143.8
845 | 705 | 527.2 | 385.9 | 441.8 | 380.4 | 230.6 | 192.3 | 192.3 | 194 | 200.3 | 144.2
846 | 706 | 527.2 | 386.2 | 441.9 | 380.6 | 230.9 | 192.7 | 192.6 | 194.4 | 200.7 | 144.6
847 | 707 | 527.2 | 386.4 | 442.1 | 380.8 | 231.2 | 193.1 | 193 | 194.8 | 201.1 | 145.1
848 | 708 | 527.2 | 386.6 | 442.3 | 381 | 231.5 | 193.4 | 193.4 | 195.3 | 201.5 | 145.6
849 | 709 | 527.3 | 386.8 | 442.5 | 381.3 | 231.8 | 193.8 | 193.8 | 195.7 | 201.9 | 146
850 | 710 | 527.3 | 387.1 | 442.6 | 381.5 | 232.1 | 194.2 | 194.1 | 196.2 | 202.3 | 146.5
851 | 711 | 527.3 | 387.3 | 442.9 | 381.7 | 232.4 | 194.5 | 194.5 | 196.6 | 202.7 | 146.9
852 | 712 | 527.3 | 387.5 | 443 | 381.9 | 232.7 | 194.9 | 194.9 | 197 | 203.1 | 147.3
853 | 713 | 527.3 | 387.7 | 443.2 | 382.2 | 233.1 | 195.3 | 195.3 | 197.4 | 203.4 | 147.7
854 | 714 | 527.4 | 388 | 443.3 | 382.4 | 233.4 | 195.7 | 195.7 | 197.8 | 203.8 | 148.1
855 | 715 | 527.4 | 388.2 | 443.5 | 382.6 | 233.7 | 196 | 196 | 198.2 | 204.2 | 148.4
856 | 716 | 527.4 | 388.4 | 443.7 | 382.9 | 234.1 | 196.4 | 196.4 | 198.6 | 204.6 | 148.8
857 | 717 | 527.4 | 388.6 | 443.9 | 383.1 | 234.5 | 196.8 | 196.8 | 199 | 205.1 | 149.1
858 | 718 | 527.4 | 388.9 | 444 | 383.3 | 234.8 | 197.1 | 197.1 | 199.5 | 205.5 | 149.4
859 | 719 | 527.4 | 389.1 | 444.2 | 383.5 | 235.2 | 197.5 | 197.5 | 199.9 | 205.9 | 149.7
860 | 720 | 527.4 | 389.3 | 444.4 | 383.7 | 235.6 | 197.9 | 197.9 | 200.2 | 206.3 | 150
861 | 721 | 527.5 | 389.6 | 444.5 | 384 | 236 | 198.2 | 198.3 | 200.6 | 206.7 | 150.4
862 | 722 | 527.5 | 389.8 | 444.7 | 384.2 | 236.3 | 198.6 | 198.6 | 201.1 | 207.2 | 150.7
863 | 723 | 527.5 | 390 | 444.9 | 384.4 | 236.7 | 199 | 199 | 201.5 | 207.6 | 151.1
864 | 724 | 527.5 | 390.2 | 445 | 384.6 | 237.1 | 199.3 | 199.4 | 201.9 | 208 | 151.4
865 | 725 | 527.5 | 390.4 | 445.2 | 384.8 | 237.5 | 199.7 | 199.7 | 202.3 | 208.4 | 151.7
866 | 726 | 527.6 | 390.6 | 445.4 | 385 | 237.9 | 200.1 | 200.1 | 202.7 | 208.8 | 152
867 | 727 | 527.6 | 390.9 | 445.5 | 385.2 | 238.4 | 200.4 | 200.5 | 203.1 | 209.2 | 152.3
868 | 728 | 527.6 | 391.1 | 445.7 | 385.4 | 238.8 | 200.8 | 200.8 | 203.4 | 209.6 | 152.6
869 | 729 | 527.6 | 391.3 | 445.8 | 385.7 | 239.4 | 201.2 | 201.2 | 203.8 | 209.9 | 152.9
870 | 730 | 527.6 | 391.5 | 446 | 385.9 | 240 | 201.5 | 201.6 | 204.2 | 210.3 | 153.2
871 | 731 | 527.6 | 391.7 | 446.2 | 386.2 | 240.5 | 201.9 | 201.9 | 204.6 | 210.6 | 153.5
872 | 732 | 527.6 | 391.9 | 446.3 | 386.4 | 241.2 | 202.2 | 202.3 | 204.9 | 211 | 153.9
873 | 733 | 527.6 | 392.1 | 446.5 | 386.6 | 241.8 | 202.6 | 202.6 | 205.3 | 211.4 | 154.2
874 | 734 | 527.5 | 392.3 | 446.7 | 386.8 | 242.5 | 202.9 | 203 | 205.7 | 211.8 | 154.5
875 | 735 | 527.5 | 392.6 | 446.8 | 387 | 243.2 | 203.3 | 203.4 | 206.1 | 212.2 | 154.9
876 | 736 | 527.5 | 392.8 | 447 | 387.2 | 243.8 | 203.7 | 203.7 | 206.4 | 212.6 | 155.2
877 | 737 | 527.5 | 393 | 447.1 | 387.4 | 244.5 | 204 | 204.1 | 206.8 | 213 | 155.5
878 | 738 | 527.5 | 393.2 | 447.3 | 387.6 | 245.1 | 204.3 | 204.5 | 207.2 | 213.4 | 155.8
879 | 739 | 527.5 | 393.4 | 447.5 | 387.8 | 245.8 | 204.7 | 204.8 | 207.5 | 213.8 | 156.1
880 | 740 | 527.4 | 393.6 | 447.6 | 388.1 | 246.6 | 205.1 | 205.2 | 207.9 | 214.2 | 156.4
881 | 741 | 527.4 | 393.8 | 447.8 | 388.3 | 247.3 | 205.4 | 205.5 | 208.2 | 214.6 | 156.7
882 | 742 | 527.4 | 394 | 448 | 388.4 | 247.9 | 205.7 | 205.9 | 208.6 | 214.9 | 157
883 | 743 | 527.3 | 394.2 | 448.1 | 388.7 | 248.5 | 206.1 | 206.3 | 209 | 215.3 | 157.3
884 | 744 | 527.4 | 394.4 | 448.3 | 388.9 | 249.1 | 206.5 | 206.6 | 209.4 | 215.6 | 157.6
885 | 745 | 527.3 | 394.6 | 448.4 | 389.1 | 249.5 | 206.8 | 207 | 209.7 | 216 | 158
886 | 746 | 527.3 | 394.8 | 448.6 | 389.3 | 249.9 | 207.2 | 207.3 | 210.1 | 216.3 | 158.3
887 | 747 | 527.3 | 395 | 448.7 | 389.5 | 250.3 | 207.5 | 207.7 | 210.5 | 216.6 | 158.7
888 | 748 | 527.3 | 395.2 | 448.8 | 389.7 | 250.8 | 207.9 | 208.1 | 210.8 | 217 | 159.1
889 | 749 | 527.3 | 395.4 | 449 | 389.9 | 251.2 | 208.2 | 208.5 | 211.1 | 217.3 | 159.5
890 | 750 | 527.3 | 395.6 | 449.1 | 390.1 | 251.5 | 208.6 | 208.8 | 211.5 | 217.6 | 159.8
891 | 751 | 527.3 | 395.8 | 449.3 | 390.3 | 251.9 | 208.9 | 209.2 | 211.8 | 217.9 | 160.2
892 | 752 | 527.3 | 396 | 449.5 | 390.5 | 252.2 | 209.3 | 209.5 | 212.2 | 218.2 | 160.6
893 | 753 | 527.3 | 396.2 | 449.6 | 390.7 | 252.6 | 209.6 | 209.9 | 212.5 | 218.5 | 161
894 | 754 | 527.3 | 396.4 | 449.8 | 390.9 | 252.9 | 210 | 210.3 | 212.9 | 218.8 | 161.3
895 | 755 | 527.3 | 396.6 | 449.9 | 391.1 | 253.2 | 210.3 | 210.6 | 213.3 | 219.1 | 161.7
896 | 756 | 527.3 | 396.8 | 450.1 | 391.3 | 253.5 | 210.6 | 211 | 213.6 | 219.3 | 162
897 | 757 | 527.3 | 397 | 450.2 | 391.5 | 253.8 | 211 | 211.3 | 214 | 219.6 | 162.3
898 | 758 | 527.2 | 397.2 | 450.4 | 391.7 | 254.2 | 211.3 | 211.6 | 214.4 | 219.9 | 162.6
899 | 759 | 527.2 | 397.4 | 450.5 | 391.9 | 254.4 | 211.7 | 212 | 214.7 | 220.2 | 162.9
900 | 760 | 527.3 | 397.5 | 450.7 | 392.1 | 254.7 | 212 | 212.3 | 215 | 220.5 | 163.2
901 | 761 | 527.3 | 397.7 | 450.8 | 392.3 | 255 | 212.3 | 212.7 | 215.4 | 220.8 | 163.4
902 | 762 | 527.2 | 397.9 | 451 | 392.5 | 255.3 | 212.7 | 213 | 215.7 | 221.2 | 163.7
903 | 763 | 527.2 | 398.1 | 451.1 | 392.7 | 255.6 | 213 | 213.4 | 216.1 | 221.5 | 163.9
904 | 764 | 527.2 | 398.3 | 451.2 | 392.9 | 255.9 | 213.4 | 213.7 | 216.4 | 221.8 | 164.1
905 | 765 | 527.2 | 398.5 | 451.4 | 393.1 | 256.2 | 213.7 | 214.1 | 216.8 | 222.1 | 164.4
906 | 766 | 527.2 | 398.7 | 451.5 | 393.3 | 256.5 | 214.1 | 214.4 | 217.2 | 222.4 | 164.6
907 | 767 | 527.2 | 398.9 | 451.7 | 393.5 | 256.8 | 214.4 | 214.7 | 217.5 | 222.7 | 164.9
908 | 768 | 527.2 | 399.1 | 451.8 | 393.7 | 257.1 | 214.8 | 215.1 | 217.8 | 223 | 165.1
909 | 769 | 527.1 | 399.3 | 451.9 | 393.9 | 257.4 | 215.1 | 215.4 | 218.1 | 223.3 | 165.3
910 | 770 | 527.1 | 399.5 | 452.1 | 394.1 | 257.7 | 215.4 | 215.8 | 218.4 | 223.6 | 165.6
911 | 771 | 527.1 | 399.7 | 452.2 | 394.3 | 258 | 215.8 | 216.1 | 218.7 | 223.9 | 165.9
912 | 772 | 527.1 | 399.8 | 452.4 | 394.5 | 258.3 | 216.1 | 216.4 | 219.1 | 224.2 | 166.1
913 | 773 | 527.2 | 400 | 452.6 | 394.6 | 258.6 | 216.4 | 216.8 | 219.4 | 224.5 | 166.4
914 | 774 | 527.2 | 400.2 | 452.7 | 394.9 | 258.9 | 216.8 | 217.1 | 219.8 | 224.8 | 166.7
915 | 775 | 527.1 | 400.4 | 452.8 | 395.1 | 259.2 | 217.1 | 217.4 | 220.1 | 225.1 | 167
916 | 776 | 527.1 | 400.6 | 453 | 395.3 | 259.5 | 217.4 | 217.8 | 220.4 | 225.4 | 167.3
917 | 777 | 527.1 | 400.8 | 453.1 | 395.4 | 259.8 | 217.8 | 218.1 | 220.7 | 225.7 | 167.7
918 | 778 | 527.1 | 401 | 453.3 | 395.6 | 260.1 | 218.1 | 218.4 | 221.1 | 226 | 168
919 | 779 | 527.1 | 401.2 | 453.4 | 395.8 | 260.5 | 218.5 | 218.8 | 221.4 | 226.3 | 168.3
920 | 780 | 527.1 | 401.3 | 453.6 | 396 | 260.7 | 218.8 | 219.1 | 221.7 | 226.7 | 168.7
921 | 781 | 527.1 | 401.5 | 453.7 | 396.2 | 261 | 219.1 | 219.4 | 222.1 | 227 | 169
922 | 782 | 527.1 | 401.7 | 453.8 | 396.4 | 261.3 | 219.5 | 219.8 | 222.4 | 227.2 | 169.4
923 | 783 | 527 | 401.9 | 453.9 | 396.6 | 261.7 | 219.8 | 220.1 | 222.7 | 227.4 | 169.8
924 | 784 | 527.1 | 402.1 | 454.1 | 396.8 | 262 | 220.2 | 220.4 | 223.1 | 227.7 | 170.2
925 | 785 | 527.1 | 402.2 | 454.2 | 396.9 | 262.3 | 220.5 | 220.8 | 223.4 | 227.9 | 170.6
926 | 786 | 527.1 | 402.4 | 454.4 | 397.1 | 262.5 | 220.9 | 221.1 | 223.8 | 228.1 | 171
927 | 787 | 527 | 402.6 | 454.6 | 397.3 | 262.8 | 221.2 | 221.4 | 224.1 | 228.4 | 171.4
928 | 788 | 527 | 402.7 | 454.7 | 397.5 | 263.1 | 221.5 | 221.8 | 224.4 | 228.6 | 171.8
929 | 789 | 527 | 402.9 | 454.8 | 397.7 | 263.4 | 221.9 | 222.1 | 224.7 | 228.9 | 172.1
930 | 790 | 527 | 403.1 | 454.9 | 397.9 | 263.8 | 222.2 | 222.4 | 225 | 229.1 | 172.5
931 | 791 | 527 | 403.3 | 455.1 | 398 | 264.1 | 222.6 | 222.8 | 225.3 | 229.4 | 172.8
932 | 792 | 526.9 | 403.5 | 455.2 | 398.2 | 264.4 | 222.9 | 223.1 | 225.6 | 229.8 | 173.2
933 | 793 | 526.9 | 403.6 | 455.4 | 398.4 | 264.8 | 223.2 | 223.4 | 225.9 | 230.2 | 173.5
934 | 794 | 526.9 | 403.8 | 455.5 | 398.6 | 265.1 | 223.6 | 223.8 | 226.2 | 230.6 | 173.9
935 | 795 | 527 | 404 | 455.6 | 398.8 | 265.5 | 223.9 | 224.1 | 226.5 | 231 | 174.2
936 | 796 | 526.9 | 404.2 | 455.7 | 399 | 265.9 | 224.2 | 224.4 | 226.8 | 231.4 | 174.6
937 | 797 | 526.9 | 404.3 | 455.9 | 399.1 | 266.2 | 224.6 | 224.8 | 227.2 | 231.9 | 174.9
938 | 798 | 527 | 404.5 | 456.1 | 399.3 | 266.5 | 224.9 | 225.1 | 227.5 | 232.3 | 175.3
939 | 799 | 527 | 404.7 | 456.2 | 399.5 | 266.8 | 225.2 | 225.4 | 227.9 | 232.7 | 175.7
940 | 800 | 527 | 404.9 | 456.2 | 399.7 | 267.2 | 225.6 | 225.7 | 228.2 | 233.1 | 176.1
941 | 801 | 527 | 405 | 456.3 | 399.9 | 267.5 | 225.9 | 226.1 | 228.5 | 233.5 | 176.5
942 | 802 | 527 | 405.2 | 456.5 | 400.1 | 267.8 | 226.3 | 226.4 | 228.8 | 233.9 | 176.9
943 | 803 | 527 | 405.4 | 456.7 | 400.2 | 268.1 | 226.6 | 226.7 | 229.1 | 234.3 | 177.3
944 | 804 | 527 | 405.5 | 456.8 | 400.4 | 268.4 | 226.9 | 227.1 | 229.5 | 234.7 | 177.7
945 | 805 | 526.9 | 405.7 | 456.9 | 400.6 | 268.7 | 227.3 | 227.4 | 229.8 | 235.1 | 178.1
946 | 806 | 526.9 | 405.9 | 457.1 | 400.8 | 269.1 | 227.6 | 227.7 | 230 | 235.5 | 178.5
947 | 807 | 526.9 | 406.1 | 457.2 | 401 | 269.5 | 227.9 | 228 | 230.4 | 235.9 | 178.9
948 | 808 | 526.9 | 406.2 | 457.3 | 401.1 | 269.8 | 228.3 | 228.4 | 230.7 | 236.2 | 179.2
949 | 809 | 526.9 | 406.4 | 457.4 | 401.3 | 270.2 | 228.6 | 228.7 | 231 | 236.6 | 179.6
950 | 810 | 526.9 | 406.6 | 457.5 | 401.5 | 270.6 | 229 | 229 | 231.4 | 236.9 | 179.9
951 | 811 | 527 | 406.7 | 457.7 | 401.6 | 271 | 229.3 | 229.3 | 231.7 | 237.3 | 180.3
952 | 812 | 526.9 | 406.9 | 457.8 | 401.8 | 271.2 | 229.6 | 229.7 | 232 | 237.6 | 180.6
953 | 813 | 526.9 | 407.1 | 458 | 402 | 271.6 | 229.9 | 230 | 232.3 | 238 | 180.9
954 | 814 | 526.9 | 407.2 | 458.1 | 402.2 | 271.9 | 230.3 | 230.3 | 232.7 | 238.4 | 181.2
955 | 815 | 527 | 407.4 | 458.2 | 402.4 | 272.3 | 230.6 | 230.6 | 233 | 238.7 | 181.6
956 | 816 | 526.9 | 407.5 | 458.4 | 402.5 | 272.7 | 230.9 | 231 | 233.3 | 239.1 | 181.9
957 | 817 | 526.9 | 407.7 | 458.5 | 402.7 | 273.1 | 231.3 | 231.3 | 233.6 | 239.5 | 182.2
958 | 818 | 526.9 | 407.9 | 458.6 | 402.9 | 273.5 | 231.6 | 231.6 | 233.9 | 239.9 | 182.5
959 | 819 | 526.9 | 408 | 458.7 | 403.1 | 273.8 | 231.9 | 231.9 | 234.2 | 240.3 | 182.8
960 | 820 | 526.9 | 408.2 | 458.8 | 403.2 | 274.2 | 232.3 | 232.3 | 234.5 | 240.7 | 183.1
961 | 821 | 527 | 408.4 | 459 | 403.4 | 274.5 | 232.6 | 232.6 | 234.8 | 241.1 | 183.3
962 | 822 | 527 | 408.5 | 459.1 | 403.6 | 274.8 | 232.9 | 232.9 | 235.1 | 241.5 | 183.6
963 | 823 | 527 | 408.7 | 459.2 | 403.8 | 275.1 | 233.3 | 233.2 | 235.4 | 241.9 | 183.9
964 | 824 | 526.9 | 408.8 | 459.3 | 404 | 275.5 | 233.6 | 233.6 | 235.7 | 242.3 | 184.2
965 | 825 | 526.9 | 409 | 459.5 | 404.1 | 275.8 | 233.9 | 233.9 | 236 | 242.7 | 184.5
966 | 826 | 526.9 | 409.2 | 459.5 | 404.3 | 276.2 | 234.3 | 234.2 | 236.3 | 243.1 | 184.8
967 | 827 | 526.9 | 409.4 | 459.6 | 404.5 | 276.5 | 234.6 | 234.5 | 236.6 | 243.5 | 185.1
968 | 828 | 526.8 | 409.5 | 459.7 | 404.6 | 276.9 | 234.9 | 234.8 | 236.9 | 243.9 | 185.3
969 | 829 | 526.8 | 409.7 | 459.8 | 404.8 | 277.2 | 235.3 | 235.1 | 237.2 | 244.3 | 185.6
970 | 830 | 526.8 | 409.8 | 460 | 405 | 277.5 | 235.6 | 235.5 | 237.6 | 244.7 | 186
971 | 831 | 526.7 | 410 | 460.1 | 405.2 | 277.9 | 235.9 | 235.8 | 237.9 | 245.1 | 186.3
972 | 832 | 526.7 | 410.2 | 460.2 | 405.3 | 278.2 | 236.3 | 236.1 | 238.2 | 245.5 | 186.6
973 | 833 | 526.7 | 410.3 | 460.3 | 405.5 | 278.5 | 236.6 | 236.4 | 238.5 | 245.8 | 186.9
974 | 834 | 526.7 | 410.5 | 460.5 | 405.6 | 278.8 | 236.9 | 236.7 | 238.8 | 246.2 | 187.2
975 | 835 | 526.7 | 410.6 | 460.6 | 405.9 | 279.2 | 237.2 | 237.1 | 239.1 | 246.6 | 187.5
976 | 836 | 526.7 | 410.8 | 460.8 | 406.1 | 279.5 | 237.5 | 237.4 | 239.4 | 247 | 187.8
977 | 837 | 526.7 | 410.9 | 460.9 | 406.3 | 279.8 | 237.9 | 237.7 | 239.8 | 247.3 | 188.1
978 | 838 | 526.7 | 411.1 | 461 | 406.4 | 280.1 | 238.2 | 238 | 240.1 | 247.7 | 188.4
979 | 839 | 526.7 | 411.2 | 461.2 | 406.5 | 280.4 | 238.5 | 238.4 | 240.4 | 248.1 | 188.7
980 | 840 | 526.7 | 411.4 | 461.3 | 406.7 | 280.8 | 238.8 | 238.7 | 240.7 | 248.4 | 189
981 | 841 | 526.7 | 411.5 | 461.4 | 406.8 | 281.1 | 239.1 | 239 | 241 | 248.8 | 189.3
982 | 842 | 526.6 | 411.7 | 461.5 | 407 | 281.4 | 239.5 | 239.3 | 241.3 | 249.2 | 189.6
983 | 843 | 526.7 | 411.8 | 461.6 | 407.2 | 281.8 | 239.8 | 239.6 | 241.6 | 249.5 | 189.9
984 | 844 | 526.7 | 412 | 461.7 | 407.3 | 282.1 | 240.1 | 239.9 | 241.9 | 249.9 | 190.2
985 | 845 | 526.7 | 412.1 | 461.8 | 407.5 | 282.5 | 240.4 | 240.2 | 242.2 | 250.2 | 190.5
986 | 846 | 526.6 | 412.3 | 461.9 | 407.7 | 282.8 | 240.8 | 240.6 | 242.5 | 250.6 | 190.8
987 | 847 | 526.7 | 412.4 | 462 | 407.8 | 283.1 | 241.1 | 240.9 | 242.8 | 250.9 | 191.1
988 | 848 | 526.7 | 412.6 | 462.2 | 408 | 283.5 | 241.4 | 241.2 | 243 | 251.2 | 191.4
989 | 849 | 526.7 | 412.7 | 462.3 | 408.1 | 283.8 | 241.8 | 241.5 | 243.3 | 251.6 | 191.7
990 | 850 | 526.7 | 412.9 | 462.4 | 408.3 | 284 | 242.1 | 241.8 | 243.6 | 251.9 | 192
991 | 851 | 526.7 | 413 | 462.5 | 408.4 | 284.4 | 242.4 | 242.1 | 244 | 252.2 | 192.4
992 | 852 | 526.7 | 413.2 | 462.6 | 408.6 | 284.7 | 242.7 | 242.5 | 244.3 | 252.6 | 192.7
993 | 853 | 526.7 | 413.3 | 462.8 | 408.7 | 285.1 | 243.1 | 242.8 | 244.6 | 252.9 | 193
994 | 854 | 526.7 | 413.5 | 462.8 | 408.9 | 285.4 | 243.4 | 243.1 | 244.9 | 253.2 | 193.3
995 | 855 | 526.8 | 413.6 | 462.9 | 409.1 | 285.7 | 243.7 | 243.4 | 245.3 | 253.5 | 193.7
996 | 856 | 526.8 | 413.8 | 463 | 409.2 | 286 | 244 | 243.7 | 245.6 | 253.8 | 194
997 | 857 | 526.7 | 413.9 | 463.1 | 409.4 | 286.2 | 244.4 | 244 | 245.9 | 254.1 | 194.3
998 | 858 | 526.7 | 414.1 | 463.3 | 409.5 | 286.5 | 244.7 | 244.3 | 246.2 | 254.4 | 194.7
999 | 859 | 526.7 | 414.2 | 463.4 | 409.7 | 286.8 | 245 | 244.7 | 246.5 | 254.8 | 195
1000 | 860 | 526.8 | 414.4 | 463.5 | 409.8 | 287.1 | 245.4 | 245 | 246.8 | 255.1 | 195.3
1001 | 861 | 526.7 | 414.5 | 463.6 | 410 | 287.3 | 245.7 | 245.3 | 247.1 | 255.4 | 195.7
1002 | 862 | 526.7 | 414.7 | 463.7 | 410.1 | 287.6 | 246.1 | 245.6 | 247.4 | 255.7 | 196
1003 | 863 | 526.7 | 414.8 | 463.8 | 410.3 | 287.9 | 246.4 | 245.9 | 247.7 | 256 | 196.3
1004 | 864 | 526.7 | 414.9 | 463.9 | 410.4 | 288.1 | 246.7 | 246.3 | 248 | 256.3 | 196.6
1005 | 865 | 526.8 | 415.1 | 464 | 410.6 | 288.4 | 247.1 | 246.6 | 248.3 | 256.6 | 197
1006 | 866 | 526.8 | 415.2 | 464.1 | 410.8 | 288.8 | 247.4 | 246.9 | 248.5 | 257 | 197.3
1007 | 867 | 526.8 | 415.4 | 464.3 | 410.9 | 289.1 | 247.7 | 247.2 | 248.8 | 257.3 | 197.6
1008 | 868 | 526.8 | 415.5 | 464.3 | 411.1 | 289.3 | 248.1 | 247.5 | 249.1 | 257.6 | 198
1009 | 869 | 526.8 | 415.7 | 464.4 | 411.2 | 289.6 | 248.4 | 247.9 | 249.4 | 257.9 | 198.3
1010 | 870 | 526.8 | 415.8 | 464.5 | 411.4 | 290 | 248.7 | 248.2 | 249.7 | 258.2 | 198.6
1011 | 871 | 526.8 | 416 | 464.6 | 411.5 | 290.3 | 249.1 | 248.5 | 250 | 258.5 | 198.9
1012 | 872 | 526.7 | 416.1 | 464.8 | 411.6 | 290.7 | 249.4 | 248.8 | 250.3 | 258.9 | 199.2
1013 | 873 | 526.7 | 416.2 | 464.9 | 411.8 | 290.8 | 249.7 | 249.1 | 250.6 | 259.2 | 199.5
1014 | 874 | 526.7 | 416.4 | 465 | 412 | 291.3 | 250 | 249.4 | 250.9 | 259.5 | 199.8
1015 | 875 | 526.7 | 416.5 | 465.1 | 412.1 | 291.7 | 250.3 | 249.7 | 251.2 | 259.9 | 200.2
1016 | 876 | 526.7 | 416.7 | 465.2 | 412.3 | 292 | 250.6 | 250 | 251.5 | 260.2 | 200.5
1017 | 877 | 526.7 | 416.8 | 465.2 | 412.4 | 292.4 | 251 | 250.3 | 251.8 | 260.5 | 200.8
1018 | 878 | 526.7 | 417 | 465.4 | 412.5 | 292.8 | 251.3 | 250.6 | 252.1 | 260.9 | 201.1
1019 | 879 | 526.7 | 417.1 | 465.5 | 412.7 | 293 | 251.6 | 251 | 252.3 | 261.2 | 201.4
1020 | 880 | 526.7 | 417.2 | 465.6 | 412.8 | 293.3 | 251.9 | 251.3 | 252.6 | 261.5 | 201.7
1021 | 881 | 526.7 | 417.4 | 465.7 | 413 | 293.7 | 252.3 | 251.6 | 252.9 | 261.9 | 202
1022 | 882 | 526.7 | 417.5 | 465.8 | 413.2 | 294 | 252.6 | 251.9 | 253.1 | 262.2 | 202.4
1023 | 883 | 526.7 | 417.7 | 465.9 | 413.3 | 294.3 | 252.9 | 252.2 | 253.4 | 262.5 | 202.7
1024 | 884 | 526.7 | 417.8 | 466 | 413.5 | 294.7 | 253.2 | 252.5 | 253.8 | 262.8 | 203
1025 | 885 | 526.6 | 417.9 | 466.1 | 413.6 | 295 | 253.5 | 252.8 | 254.1 | 263.1 | 203.3
1026 | 886 | 526.6 | 418.1 | 466.2 | 413.7 | 295.4 | 253.9 | 253.1 | 254.4 | 263.4 | 203.6
1027 | 887 | 526.6 | 418.2 | 466.3 | 413.9 | 295.6 | 254.2 | 253.4 | 254.7 | 263.7 | 203.9
1028 | 888 | 526.6 | 418.4 | 466.4 | 414 | 296.1 | 254.5 | 253.8 | 255 | 263.9 | 204.2
1029 | 889 | 526.6 | 418.5 | 466.4 | 414.2 | 296.2 | 254.8 | 254.1 | 255.2 | 264.2 | 204.5
1030 | 890 | 526.5 | 418.6 | 466.6 | 414.3 | 296.6 | 255.1 | 254.4 | 255.6 | 264.5 | 204.8
1031 | 891 | 526.4 | 418.8 | 466.7 | 414.5 | 296.9 | 255.4 | 254.7 | 255.9 | 264.7 | 205.1
1032 | 892 | 526.4 | 418.9 | 466.8 | 414.6 | 297.3 | 255.8 | 255 | 256.2 | 265 | 205.4
1033 | 893 | 526.3 | 419.1 | 466.8 | 414.8 | 297.6 | 256.1 | 255.3 | 256.5 | 265.2 | 205.7
1034 | 894 | 526.3 | 419.2 | 467 | 414.9 | 298.1 | 256.4 | 255.6 | 256.8 | 265.5 | 206
1035 | 895 | 526.3 | 419.4 | 467 | 415 | 298.4 | 256.7 | 255.9 | 257.1 | 265.7 | 206.3
1036 | 896 | 526.3 | 419.5 | 467.1 | 415.2 | 298.6 | 257 | 256.2 | 257.4 | 266 | 206.6
1037 | 897 | 526.3 | 419.6 | 467.2 | 415.3 | 299 | 257.3 | 256.5 | 257.7 | 266.3 | 206.9
1038 | 898 | 526.3 | 419.8 | 467.3 | 415.5 | 299.4 | 257.6 | 256.8 | 258 | 266.5 | 207.2
1039 | 899 | 526.3 | 419.9 | 467.4 | 415.6 | 299.7 | 257.9 | 257.1 | 258.3 | 266.8 | 207.5
1040 | 900 | 526.3 | 420 | 467.5 | 415.8 | 300 | 258.2 | 257.5 | 258.6 | 267.1 | 207.8
1041 | 901 | 526.3 | 420.2 | 467.6 | 415.9 | 300.4 | 258.5 | 257.8 | 258.8 | 267.4 | 208.1
1042 | 902 | 526.3 | 420.3 | 467.7 | 416 | 300.8 | 258.8 | 258.1 | 259.2 | 267.6 | 208.4
1043 | 903 | 526.3 | 420.4 | 467.8 | 416.2 | 301.1 | 259.1 | 258.4 | 259.5 | 267.9 | 208.7
1044 | 904 | 526.4 | 420.6 | 467.9 | 416.3 | 301.4 | 259.4 | 258.7 | 259.8 | 268.2 | 209
1045 | 905 | 526.4 | 420.7 | 468 | 416.5 | 301.8 | 259.8 | 259 | 260 | 268.5 | 209.3
1046 | 906 | 526.4 | 420.8 | 468.1 | 416.6 | 302.1 | 260.1 | 259.3 | 260.4 | 268.8 | 209.6
1047 | 907 | 526.4 | 421 | 468.2 | 416.8 | 302.5 | 260.4 | 259.6 | 260.7 | 269.1 | 209.9
1048 | 908 | 526.5 | 421.1 | 468.2 | 416.9 | 302.8 | 260.7 | 259.9 | 261 | 269.3 | 210.2
1049 | 909 | 526.5 | 421.3 | 468.4 | 417 | 303.3 | 261.1 | 260.2 | 261.2 | 269.6 | 210.4
1050 | 910 | 526.5 | 421.4 | 468.5 | 417.2 | 303.5 | 261.4 | 260.6 | 261.5 | 269.9 | 210.7
1051 | 911 | 526.5 | 421.5 | 468.6 | 417.3 | 303.8 | 261.7 | 260.9 | 261.8 | 270.2 | 211
1052 | 912 | 526.6 | 421.6 | 468.6 | 417.4 | 304.3 | 262.1 | 261.2 | 262 | 270.5 | 211.3
1053 | 913 | 526.5 | 421.8 | 468.7 | 417.6 | 304.5 | 262.4 | 261.5 | 262.3 | 270.8 | 211.6
1054 | 914 | 526.6 | 421.9 | 468.9 | 417.7 | 304.8 | 262.8 | 261.8 | 262.6 | 271 | 211.9
1055 | 915 | 526.6 | 422 | 469 | 417.8 | 305.2 | 263.1 | 262.1 | 262.8 | 271.3 | 212.2
1056 | 916 | 526.5 | 422.2 | 469.1 | 418 | 305.6 | 263.5 | 262.4 | 263.1 | 271.6 | 212.4
1057 | 917 | 526.5 | 422.3 | 469.1 | 418.1 | 305.9 | 263.8 | 262.7 | 263.4 | 271.8 | 212.7
1058 | 918 | 526.5 | 422.4 | 469.2 | 418.2 | 306.3 | 264.1 | 263.1 | 263.6 | 272.1 | 213
1059 | 919 | 526.5 | 422.6 | 469.3 | 418.4 | 306.6 | 264.4 | 263.4 | 264 | 272.4 | 213.2
1060 | 920 | 526.5 | 422.7 | 469.4 | 418.5 | 306.9 | 264.8 | 263.7 | 264.3 | 272.7 | 213.5
1061 | 921 | 526.5 | 422.8 | 469.5 | 418.7 | 307.2 | 265.1 | 264 | 264.6 | 272.9 | 213.7
1062 | 922 | 526.6 | 423 | 469.5 | 418.8 | 307.6 | 265.4 | 264.3 | 264.9 | 273.2 | 214
1063 | 923 | 526.5 | 423.1 | 469.6 | 418.9 | 307.9 | 265.7 | 264.6 | 265.2 | 273.4 | 214.2
1064 | 924 | 526.5 | 423.2 | 469.7 | 419 | 308.2 | 266.1 | 265 | 265.5 | 273.7 | 214.5
1065 | 925 | 526.5 | 423.3 | 469.8 | 419.2 | 308.6 | 266.4 | 265.3 | 265.9 | 273.9 | 214.7
1066 | 926 | 526.5 | 423.5 | 469.9 | 419.3 | 308.9 | 266.7 | 265.6 | 266.2 | 274.2 | 214.9
1067 | 927 | 526.5 | 423.6 | 470 | 419.4 | 309.1 | 267 | 265.9 | 266.6 | 274.5 | 215.2
1068 | 928 | 526.5 | 423.7 | 470.1 | 419.6 | 309.5 | 267.4 | 266.2 | 266.9 | 274.7 | 215.4
1069 | 929 | 526.4 | 423.8 | 470.2 | 419.7 | 309.9 | 267.7 | 266.5 | 267.1 | 275 | 215.7
1070 | 930 | 526.4 | 423.9 | 470.3 | 419.9 | 310.2 | 268 | 266.8 | 267.4 | 275.3 | 215.9
1071 | 931 | 526.4 | 424.1 | 470.3 | 420 | 310.4 | 268.3 | 267.1 | 267.7 | 275.6 | 216.1
1072 | 932 | 526.4 | 424.2 | 470.4 | 420.1 | 310.8 | 268.6 | 267.4 | 268 | 275.9 | 216.4
1073 | 933 | 526.3 | 424.3 | 470.5 | 420.2 | 311.2 | 268.9 | 267.7 | 268.3 | 276.2 | 216.6
1074 | 934 | 526.3 | 424.4 | 470.6 | 420.3 | 311.5 | 269.2 | 268 | 268.6 | 276.4 | 216.8
1075 | 935 | 526.3 | 424.6 | 470.7 | 420.5 | 311.8 | 269.5 | 268.3 | 268.8 | 276.7 | 217.1
1076 | 936 | 526.3 | 424.7 | 470.8 | 420.6 | 312 | 269.8 | 268.6 | 269.1 | 277 | 217.3
1077 | 937 | 526.3 | 424.8 | 470.9 | 420.7 | 312.5 | 270.1 | 269 | 269.4 | 277.3 | 217.5
1078 | 938 | 526.3 | 424.9 | 471 | 420.8 | 312.8 | 270.4 | 269.3 | 269.7 | 277.5 | 217.7
1079 | 939 | 526.3 | 425.1 | 471 | 421 | 313.1 | 270.8 | 269.6 | 269.9 | 277.8 | 218
1080 | 940 | 526.3 | 425.2 | 471.2 | 421.1 | 313.6 | 271.1 | 269.9 | 270.2 | 278.1 | 218.2
1081 | 941 | 526.2 | 425.3 | 471.2 | 421.2 | 313.8 | 271.4 | 270.2 | 270.5 | 278.4 | 218.5
1082 | 942 | 526.2 | 425.4 | 471.3 | 421.3 | 314.2 | 271.7 | 270.5 | 270.7 | 278.7 | 218.7
1083 | 943 | 526.2 | 425.5 | 471.5 | 421.4 | 314.5 | 272 | 270.8 | 271 | 279 | 219
1084 | 944 | 526.2 | 425.7 | 471.5 | 421.6 | 314.7 | 272.3 | 271.1 | 271.3 | 279.3 | 219.2
1085 | 945 | 526.2 | 425.8 | 471.6 | 421.7 | 315.1 | 272.7 | 271.4 | 271.6 | 279.6 | 219.5
1086 | 946 | 526.3 | 425.9 | 471.6 | 421.8 | 315.5 | 273 | 271.7 | 271.9 | 279.8 | 219.8
1087 | 947 | 526.3 | 426 | 471.7 | 421.9 | 315.8 | 273.3 | 272 | 272.1 | 280.1 | 220
1088 | 948 | 526.3 | 426.2 | 471.8 | 422.1 | 316.1 | 273.6 | 272.3 | 272.4 | 280.4 | 220.3
1089 | 949 | 526.3 | 426.3 | 471.9 | 422.2 | 316.5 | 274 | 272.6 | 272.7 | 280.7 | 220.6
1090 | 950 | 526.3 | 426.4 | 471.9 | 422.3 | 316.8 | 274.3 | 272.9 | 273 | 281 | 220.9
1091 | 951 | 526.3 | 426.5 | 472 | 422.4 | 317.1 | 274.6 | 273.2 | 273.3 | 281.3 | 221.1
1092 | 952 | 526.3 | 426.6 | 472.1 | 422.5 | 317.5 | 274.9 | 273.6 | 273.6 | 281.6 | 221.4
1093 | 953 | 526.3 | 426.7 | 472.2 | 422.6 | 317.8 | 275.3 | 273.9 | 273.9 | 281.9 | 221.6
1094 | 954 | 526.3 | 426.9 | 472.3 | 422.8 | 318 | 275.6 | 274.2 | 274.2 | 282.2 | 221.9
1095 | 955 | 526.3 | 427 | 472.4 | 422.9 | 318.5 | 275.9 | 274.5 | 274.4 | 282.5 | 222.2
1096 | 956 | 526.3 | 427.1 | 472.5 | 423 | 318.8 | 276.2 | 274.8 | 274.7 | 282.9 | 222.4
1097 | 957 | 526.3 | 427.2 | 472.6 | 423.1 | 319.1 | 276.5 | 275.1 | 274.9 | 283.2 | 222.7
1098 | 958 | 526.3 | 427.3 | 472.7 | 423.3 | 319.4 | 276.8 | 275.4 | 275.3 | 283.5 | 223
1099 | 959 | 526.3 | 427.4 | 472.7 | 423.4 | 319.7 | 277.1 | 275.7 | 275.5 | 283.8 | 223.2
1100 | 960 | 526.3 | 427.6 | 472.8 | 423.5 | 320 | 277.5 | 276.1 | 275.8 | 284.1 | 223.5
1101 | 961 | 526.3 | 427.7 | 472.9 | 423.6 | 320.4 | 277.8 | 276.4 | 276.1 | 284.4 | 223.7
1102 | 962 | 526.3 | 427.8 | 472.9 | 423.7 | 320.8 | 278.2 | 276.7 | 276.4 | 284.7 | 224
1103 | 963 | 526.3 | 427.9 | 473 | 423.9 | 321.1 | 278.5 | 277 | 276.7 | 285 | 224.3
1104 | 964 | 526.3 | 428 | 473.1 | 424 | 321.4 | 278.8 | 277.3 | 276.9 | 285.3 | 224.5
1105 | 965 | 526.4 | 428.1 | 473.2 | 424.1 | 321.7 | 279.1 | 277.6 | 277.2 | 285.6 | 224.8
1106 | 966 | 526.4 | 428.3 | 473.3 | 424.2 | 322 | 279.5 | 277.9 | 277.4 | 285.9 | 225
1107 | 967 | 526.5 | 428.4 | 473.4 | 424.3 | 322.3 | 279.8 | 278.3 | 277.7 | 286.2 | 225.3
1108 | 968 | 526.5 | 428.5 | 473.5 | 424.4 | 322.8 | 280.1 | 278.6 | 278 | 286.5 | 225.5
1109 | 969 | 526.5 | 428.6 | 473.5 | 424.6 | 322.8 | 280.4 | 278.9 | 278.3 | 286.8 | 225.8
1110 | 970 | 526.5 | 428.7 | 473.6 | 424.7 | 323.3 | 280.8 | 279.2 | 278.6 | 287.1 | 226
1111 | 971 | 526.5 | 428.8 | 473.7 | 424.8 | 323.6 | 281.1 | 279.5 | 278.9 | 287.4 | 226.3
1112 | 972 | 526.4 | 428.9 | 473.8 | 424.9 | 323.9 | 281.4 | 279.8 | 279.2 | 287.7 | 226.5
1113 | 973 | 526.5 | 429 | 473.9 | 425 | 324.2 | 281.7 | 280.1 | 279.5 | 288 | 226.8
1114 | 974 | 526.4 | 429.1 | 474 | 425.1 | 324.6 | 282 | 280.4 | 279.7 | 288.3 | 227.1
1115 | 975 | 526.4 | 429.3 | 474 | 425.2 | 324.9 | 282.3 | 280.7 | 280 | 288.6 | 227.3
1116 | 976 | 526.4 | 429.4 | 474.1 | 425.4 | 325.3 | 282.6 | 281 | 280.3 | 288.9 | 227.6
1117 | 977 | 526.4 | 429.5 | 474.2 | 425.5 | 325.6 | 282.9 | 281.3 | 280.6 | 289.2 | 227.9
1118 | 978 | 526.4 | 429.6 | 474.2 | 425.6 | 325.9 | 283.3 | 281.6 | 280.9 | 289.5 | 228.1
1119 | 979 | 526.4 | 429.7 | 474.3 | 425.7 | 326.3 | 283.6 | 282 | 281.1 | 289.8 | 228.4
1120 | 980 | 526.5 | 429.8 | 474.4 | 425.8 | 326.6 | 283.9 | 282.3 | 281.4 | 290.1 | 228.7
1121 | 981 | 526.5 | 429.9 | 474.5 | 426 | 327 | 284.3 | 282.6 | 281.7 | 290.4 | 229
1122 | 982 | 526.5 | 430 | 474.5 | 426.1 | 327.3 | 284.6 | 282.9 | 282 | 290.7 | 229.3
1123 | 983 | 526.5 | 430.1 | 474.7 | 426.2 | 327.6 | 284.9 | 283.2 | 282.3 | 291 | 229.6
1124 | 984 | 526.5 | 430.2 | 474.8 | 426.3 | 327.9 | 285.2 | 283.5 | 282.6 | 291.3 | 229.9
1125 | 985 | 526.5 | 430.3 | 474.9 | 426.4 | 328.3 | 285.6 | 283.8 | 282.9 | 291.6 | 230.1
1126 | 986 | 526.5 | 430.4 | 475 | 426.5 | 328.6 | 285.9 | 284.1 | 283.2 | 291.9 | 230.4
1127 | 987 | 526.5 | 430.5 | 475 | 426.6 | 328.9 | 286.2 | 284.4 | 283.5 | 292.2 | 230.7
1128 | 988 | 526.5 | 430.7 | 475.1 | 426.8 | 329.3 | 286.5 | 284.7 | 283.7 | 292.5 | 231
1129 | 989 | 526.5 | 430.8 | 475.2 | 426.8 | 329.6 | 286.8 | 285 | 284 | 292.8 | 231.3
1130 | 990 | 526.6 | 430.9 | 475.2 | 427 | 329.9 | 287.1 | 285.3 | 284.2 | 293 | 231.6
1131 | 991 | 526.5 | 431 | 475.4 | 427.1 | 330.2 | 287.4 | 285.6 | 284.5 | 293.3 | 231.9
1132 | 992 | 526.5 | 431.1 | 475.4 | 427.2 | 330.6 | 287.7 | 285.8 | 284.8 | 293.6 | 232.2
1133 | 993 | 526.5 | 431.2 | 475.4 | 427.3 | 330.9 | 288 | 286.1 | 285.1 | 293.9 | 232.5
1134 | 994 | 526.4 | 431.3 | 475.5 | 427.4 | 331.3 | 288.3 | 286.4 | 285.4 | 294.2 | 232.9
1135 | 995 | 526.3 | 431.4 | 475.6 | 427.5 | 331.6 | 288.6 | 286.7 | 285.7 | 294.5 | 233.2
1136 | 996 | 526.3 | 431.5 | 475.7 | 427.7 | 331.9 | 288.9 | 287 | 286 | 294.8 | 233.4
1137 | 997 | 526.3 | 431.6 | 475.8 | 427.7 | 332.2 | 289.3 | 287.3 | 286.3 | 295.1 | 233.7
1138 | 998 | 526.3 | 431.7 | 475.9 | 427.9 | 332.5 | 289.6 | 287.6 | 286.6 | 295.4 | 234.1
1139 | 999 | 526.2 | 431.8 | 475.9 | 428 | 332.9 | 289.9 | 287.9 | 287 | 295.7 | 234.4
1140 | 1000 | 526.2 | 431.9 | 476 | 428.1 | 333.2 | 290.2 | 288.2 | 287.3 | 296 | 234.7
1141 | 1001 | 526.2 | 432 | 476.1 | 428.2 | 333.5 | 290.5 | 288.5 | 287.6 | 296.3 | 234.9
1142 | 1002 | 526.2 | 432.1 | 476.2 | 428.3 | 333.8 | 290.8 | 288.8 | 287.9 | 296.6 | 235.2
1143 | 1003 | 526.2 | 432.2 | 476.3 | 428.4 | 334.1 | 291.1 | 289 | 288.2 | 296.9 | 235.4
1144 | 1004 | 526.2 | 432.3 | 476.3 | 428.5 | 334.4 | 291.4 | 289.3 | 288.4 | 297.3 | 235.7
1145 | 1005 | 526.2 | 432.5 | 476.4 | 428.6 | 334.8 | 291.8 | 289.6 | 288.7 | 297.6 | 235.9
1146 | 1006 | 526.2 | 432.6 | 476.4 | 428.7 | 335.1 | 292.1 | 289.9 | 289 | 297.9 | 236.2
1147 | 1007 | 526.3 | 432.7 | 476.5 | 428.9 | 335.4 | 292.4 | 290.2 | 289.2 | 298.2 | 236.5
1148 | 1008 | 526.3 | 432.8 | 476.6 | 429 | 335.7 | 292.7 | 290.5 | 289.5 | 298.5 | 236.8
1149 | 1009 | 526.3 | 432.9 | 476.7 | 429.1 | 336 | 293 | 290.8 | 289.7 | 298.8 | 237
1150 | 1010 | 526.3 | 433 | 476.7 | 429.2 | 336.4 | 293.3 | 291.1 | 290 | 299.1 | 237.3
1151 | 1011 | 526.3 | 433.1 | 476.8 | 429.3 | 336.7 | 293.6 | 291.4 | 290.3 | 299.4 | 237.6
1152 | 1012 | 526.3 | 433.1 | 476.9 | 429.4 | 337 | 293.9 | 291.7 | 290.6 | 299.7 | 237.9
1153 | 1013 | 526.3 | 433.2 | 477 | 429.5 | 337.3 | 294.2 | 292 | 290.9 | 300 | 238.1
1154 | 1014 | 526.3 | 433.4 | 477 | 429.6 | 337.6 | 294.5 | 292.3 | 291.1 | 300.2 | 238.4
1155 | 1015 | 526.3 | 433.5 | 477.1 | 429.7 | 337.9 | 294.8 | 292.6 | 291.4 | 300.5 | 238.7
1156 | 1016 | 526.4 | 433.6 | 477.1 | 429.8 | 338.2 | 295 | 292.9 | 291.8 | 300.8 | 238.9
1157 | 1017 | 526.3 | 433.6 | 477.2 | 429.9 | 338.5 | 295.3 | 293.2 | 292.1 | 301.1 | 239.1
1158 | 1018 | 526.3 | 433.7 | 477.3 | 430 | 338.7 | 295.7 | 293.5 | 292.4 | 301.4 | 239.3
1159 | 1019 | 526.2 | 433.8 | 477.4 | 430.1 | 339 | 296 | 293.8 | 292.6 | 301.7 | 239.5
1160 | 1020 | 526.2 | 433.9 | 477.4 | 430.2 | 339.4 | 296.3 | 294.1 | 292.9 | 302 | 239.7
1161 | 1021 | 526.2 | 434 | 477.5 | 430.3 | 339.6 | 296.7 | 294.4 | 293.1 | 302.2 | 240
1162 | 1022 | 526.2 | 434.1 | 477.6 | 430.4 | 339.9 | 297 | 294.7 | 293.4 | 302.5 | 240.2
1163 | 1023 | 526.2 | 434.2 | 477.6 | 430.5 | 340.2 | 297.3 | 295 | 293.7 | 302.8 | 240.4
1164 | 1024 | 526.2 | 434.3 | 477.7 | 430.6 | 340.5 | 297.6 | 295.2 | 293.9 | 303.1 | 240.7
1165 | 1025 | 526.2 | 434.4 | 477.8 | 430.7 | 340.8 | 298 | 295.5 | 294.1 | 303.4 | 240.9
1166 | 1026 | 526.2 | 434.5 | 477.9 | 430.8 | 341.1 | 298.2 | 295.8 | 294.4 | 303.7 | 241.2
1167 | 1027 | 526.2 | 434.6 | 477.9 | 430.9 | 341.4 | 298.5 | 296.1 | 294.6 | 304 | 241.4
1168 | 1028 | 526.2 | 434.7 | 477.9 | 431 | 341.7 | 298.8 | 296.4 | 294.9 | 304.3 | 241.7
1169 | 1029 | 526.2 | 434.8 | 478 | 431.1 | 341.9 | 299.1 | 296.8 | 295.1 | 304.5 | 242
1170 | 1030 | 526.2 | 434.9 | 478.1 | 431.2 | 342.2 | 299.4 | 297 | 295.3 | 304.8 | 242.1
1171 | 1031 | 526.3 | 435 | 478.2 | 431.3 | 342.5 | 299.7 | 297.4 | 295.6 | 305 | 242.3
1172 | 1032 | 526.3 | 435.1 | 478.2 | 431.4 | 342.8 | 300 | 297.6 | 295.8 | 305.3 | 242.5
1173 | 1033 | 526.4 | 435.2 | 478.4 | 431.5 | 343 | 300.3 | 298 | 296.1 | 305.5 | 242.8
1174 | 1034 | 526.4 | 435.3 | 478.3 | 431.6 | 343.3 | 300.6 | 298.2 | 296.4 | 305.8 | 243
1175 | 1035 | 526.4 | 435.4 | 478.4 | 431.7 | 343.6 | 300.9 | 298.5 | 296.8 | 306 | 243.2
1176 | 1036 | 526.4 | 435.5 | 478.5 | 431.8 | 343.9 | 301.2 | 298.8 | 297 | 306.3 | 243.5
1177 | 1037 | 526.4 | 435.6 | 478.6 | 431.9 | 344.1 | 301.5 | 299.1 | 297.3 | 306.6 | 243.6
1178 | 1038 | 526.4 | 435.7 | 478.7 | 432 | 344.4 | 301.8 | 299.4 | 297.7 | 306.8 | 243.8
1179 | 1039 | 526.4 | 435.8 | 478.7 | 432.1 | 344.7 | 302.1 | 299.7 | 298 | 307.1 | 244.1
1180 | 1040 | 526.4 | 435.9 | 478.8 | 432.2 | 345 | 302.4 | 300 | 298.2 | 307.4 | 244.3
1181 | 1041 | 526.4 | 436 | 478.8 | 432.3 | 345.3 | 302.7 | 300.3 | 298.5 | 307.6 | 244.5
1182 | 1042 | 526.5 | 436.1 | 478.9 | 432.4 | 345.6 | 303 | 300.6 | 298.8 | 307.9 | 244.8
1183 | 1043 | 526.5 | 436.2 | 479 | 432.5 | 345.8 | 303.3 | 300.9 | 299.1 | 308.1 | 245
1184 | 1044 | 526.5 | 436.3 | 479.1 | 432.6 | 346.1 | 303.6 | 301.2 | 299.4 | 308.3 | 245.2
1185 | 1045 | 526.5 | 436.3 | 479.2 | 432.7 | 346.4 | 303.9 | 301.5 | 299.6 | 308.6 | 245.4
1186 | 1046 | 526.5 | 436.4 | 479.2 | 432.8 | 346.6 | 304.2 | 301.8 | 299.8 | 308.8 | 245.6
1187 | 1047 | 526.6 | 436.5 | 479.3 | 432.9 | 346.9 | 304.6 | 302.1 | 300.1 | 309.1 | 245.8
1188 | 1048 | 526.6 | 436.6 | 479.3 | 433 | 347.2 | 304.9 | 302.4 | 300.4 | 309.3 | 246
1189 | 1049 | 526.5 | 436.7 | 479.4 | 433.2 | 347.4 | 305.2 | 302.7 | 300.7 | 309.5 | 246.2
1190 | 1050 | 526.5 | 436.8 | 479.4 | 433.3 | 347.7 | 305.5 | 303 | 300.9 | 309.8 | 246.5
1191 | 1051 | 526.4 | 436.9 | 479.5 | 433.4 | 348 | 305.8 | 303.3 | 301.2 | 310 | 246.7
1192 | 1052 | 526.4 | 437 | 479.5 | 433.4 | 348.3 | 306.1 | 303.6 | 301.5 | 310.3 | 246.9
1193 | 1053 | 526.4 | 437.1 | 479.6 | 433.5 | 348.5 | 306.4 | 303.9 | 301.7 | 310.5 | 247.2
1194 | 1054 | 526.4 | 437.2 | 479.7 | 433.6 | 348.8 | 306.7 | 304.2 | 302 | 310.8 | 247.4
1195 | 1055 | 526.3 | 437.3 | 479.7 | 433.8 | 349.1 | 307 | 304.5 | 302.3 | 311.1 | 247.6
1196 | 1056 | 526.3 | 437.4 | 479.8 | 433.8 | 349.3 | 307.3 | 304.8 | 302.5 | 311.3 | 247.9
1197 | 1057 | 526.3 | 437.5 | 479.8 | 433.9 | 349.6 | 307.6 | 305.1 | 302.8 | 311.6 | 248.1
1198 | 1058 | 526.3 | 437.5 | 479.9 | 434 | 349.9 | 307.9 | 305.4 | 303.1 | 311.9 | 248.3
1199 | 1059 | 526.3 | 437.6 | 480 | 434.1 | 350.2 | 308.2 | 305.7 | 303.4 | 312.2 | 248.5
1200 | 1060 | 526.3 | 437.7 | 480 | 434.2 | 350.4 | 308.5 | 306 | 303.7 | 312.5 | 248.8
1201 | 1061 | 526.3 | 437.8 | 480 | 434.3 | 350.7 | 308.7 | 306.3 | 304 | 312.7 | 249
1202 | 1062 | 526.2 | 437.9 | 480.1 | 434.4 | 350.9 | 309 | 306.6 | 304.3 | 313 | 249.2
1203 | 1063 | 526.2 | 438 | 480.1 | 434.5 | 351.2 | 309.3 | 306.9 | 304.6 | 313.3 | 249.4
1204 | 1064 | 526.2 | 438.1 | 480.2 | 434.6 | 351.6 | 309.6 | 307.2 | 304.9 | 313.6 | 249.6
1205 | 1065 | 526.2 | 438.2 | 480.2 | 434.7 | 351.8 | 309.9 | 307.5 | 305.1 | 313.9 | 249.9
1206 | 1066 | 526.1 | 438.3 | 480.3 | 434.8 | 352.1 | 310.2 | 307.7 | 305.4 | 314.1 | 250.1
1207 | 1067 | 526.1 | 438.4 | 480.4 | 434.9 | 352.3 | 310.5 | 308 | 305.7 | 314.7 | 250.4
1208 | 1068 | 526.1 | 438.5 | 480.5 | 435 | 352.6 | 310.8 | 308.3 | 306 | 315 | 250.6
1209 | 1069 | 526.1 | 438.6 | 480.5 | 435.1 | 352.8 | 311.1 | 308.6 | 306.3 | 315.2 | 250.8
1210 | 1070 | 526 | 438.6 | 480.6 | 435.2 | 353.1 | 311.4 | 308.9 | 306.6 | 315.4 | 251.1
1211 | 1071 | 526.1 | 438.7 | 480.6 | 435.3 | 353.4 | 311.7 | 309.2 | 306.8 | 315.6 | 251.3
1212 | 1072 | 526.1 | 438.8 | 480.7 | 435.4 | 353.6 | 312 | 309.5 | 307.1 | 315.8 | 251.5
1213 | 1073 | 526.1 | 438.9 | 480.8 | 435.5 | 353.9 | 312.3 | 309.8 | 307.4 | 316 | 251.8
1214 | 1074 | 526.1 | 439 | 480.8 | 435.5 | 354.2 | 312.6 | 310.1 | 307.7 | 316.3 | 252
1215 | 1075 | 526.1 | 439.1 | 480.9 | 435.6 | 354.4 | 312.8 | 310.4 | 308 | 316.5 | 252.2
1216 | 1076 | 526.1 | 439.2 | 481 | 435.7 | 354.7 | 313.1 | 310.7 | 308.4 | 316.8 | 252.4
1217 | 1077 | 526.2 | 439.3 | 481 | 435.8 | 355 | 313.4 | 311 | 308.7 | 317 | 252.7
1218 | 1078 | 526.2 | 439.3 | 481.1 | 435.9 | 355.2 | 313.7 | 311.3 | 308.9 | 317.3 | 252.9
1219 | 1079 | 526.2 | 439.4 | 481.1 | 436 | 355.5 | 314 | 311.6 | 309.2 | 317.6 | 253.2
1220 | 1080 | 526.2 | 439.5 | 481.2 | 436.1 | 355.8 | 314.3 | 311.9 | 309.6 | 317.8 | 253.4
1221 | 1081 | 526.2 | 439.6 | 481.3 | 436.2 | 356 | 314.5 | 312.2 | 309.8 | 318.1 | 253.6
1222 | 1082 | 526.2 | 439.7 | 481.3 | 436.3 | 356.3 | 314.8 | 312.4 | 310.2 | 318.4 | 253.8
1223 | 1083 | 526.2 | 439.8 | 481.4 | 436.3 | 356.5 | 315.1 | 312.7 | 310.5 | 318.7 | 253.9
1224 | 1084 | 526.3 | 439.9 | 481.4 | 436.5 | 356.8 | 315.4 | 313 | 310.7 | 319 | 254.2
1225 | 1085 | 526.3 | 439.9 | 481.5 | 436.5 | 357.1 | 315.7 | 313.3 | 311 | 319.3 | 254.4
1226 | 1086 | 526.3 | 440 | 481.6 | 436.6 | 357.3 | 316 | 313.6 | 311.3 | 319.6 | 254.6
1227 | 1087 | 526.3 | 440.1 | 481.6 | 436.7 | 357.6 | 316.3 | 313.9 | 311.6 | 319.9 | 254.8
1228 | 1088 | 526.3 | 440.2 | 481.7 | 436.8 | 357.8 | 316.6 | 314.2 | 311.9 | 320.1 | 255
1229 | 1089 | 526.3 | 440.3 | 481.7 | 436.9 | 358 | 316.9 | 314.5 | 312.2 | 320.4 | 255.1
1230 | 1090 | 526.3 | 440.4 | 481.8 | 437 | 358.2 | 317.2 | 314.8 | 312.6 | 320.7 | 255.3
1231 | 1091 | 526.3 | 440.5 | 481.8 | 437.1 | 358.4 | 317.5 | 315.1 | 312.9 | 321 | 255.4
1232 | 1092 | 526.3 | 440.5 | 481.9 | 437.2 | 358.6 | 317.7 | 315.4 | 313.2 | 321.3 | 255.7
1233 | 1093 | 526.2 | 440.6 | 482 | 437.2 | 358.9 | 318 | 315.7 | 313.4 | 321.6 | 255.9
1234 | 1094 | 526.2 | 440.7 | 482 | 437.3 | 359.1 | 318.3 | 315.9 | 313.7 | 321.8 | 256
1235 | 1095 | 526.2 | 440.8 | 482.1 | 437.4 | 359.3 | 318.6 | 316.3 | 314 | 322.1 | 256.2
1236 | 1096 | 526.2 | 440.9 | 482.2 | 437.5 | 359.6 | 318.9 | 316.5 | 314.3 | 322.5 | 256.4
1237 | 1097 | 526.1 | 441 | 482.2 | 437.6 | 359.9 | 319.2 | 316.8 | 314.5 | 322.8 | 256.6
1238 | 1098 | 526.1 | 441 | 482.2 | 437.7 | 360.1 | 319.4 | 317.1 | 314.8 | 323.1 | 256.8
1239 | 1099 | 526.1 | 441.1 | 482.3 | 437.8 | 360.4 | 319.7 | 317.4 | 315.1 | 323.4 | 257
1240 | 1100 | 526 | 441.2 | 482.3 | 437.8 | 360.6 | 320 | 317.7 | 315.5 | 323.7 | 257.2
1241 | 1101 | 526 | 441.3 | 482.4 | 437.9 | 360.9 | 320.2 | 317.9 | 315.7 | 323.9 | 257.4
1242 | 1102 | 526 | 441.4 | 482.4 | 438 | 361.2 | 320.5 | 318.2 | 316 | 324.2 | 257.7
1243 | 1103 | 526 | 441.5 | 482.5 | 438.1 | 361.4 | 320.8 | 318.5 | 316.2 | 324.5 | 258
1244 | 1104 | 526 | 441.5 | 482.6 | 438.2 | 361.6 | 321.1 | 318.8 | 316.5 | 324.8 | 258.2
1245 | 1105 | 525.9 | 441.6 | 482.6 | 438.3 | 361.9 | 321.4 | 319.1 | 316.8 | 325.2 | 258.4
1246 | 1106 | 525.9 | 441.7 | 482.6 | 438.4 | 362.2 | 321.6 | 319.3 | 317 | 325.6 | 258.6
1247 | 1107 | 525.9 | 441.8 | 482.6 | 438.5 | 362.4 | 321.9 | 319.6 | 317.4 | 326 | 258.8
1248 | 1108 | 525.9 | 441.9 | 482.7 | 438.5 | 362.7 | 322.2 | 319.9 | 317.6 | 326.3 | 259
1249 | 1109 | 525.9 | 442 | 482.8 | 438.6 | 362.9 | 322.5 | 320.2 | 317.9 | 326.5 | 259.1
1250 | 1110 | 525.9 | 442 | 482.8 | 438.7 | 363.2 | 322.7 | 320.5 | 318.2 | 326.8 | 259.3
1251 | 1111 | 525.9 | 442.1 | 482.8 | 438.8 | 363.5 | 323 | 320.8 | 318.5 | 327.1 | 259.6
1252 | 1112 | 526 | 442.2 | 482.9 | 438.9 | 363.7 | 323.3 | 321.1 | 318.9 | 327.3 | 259.8
1253 | 1113 | 526 | 442.3 | 483 | 439 | 364 | 323.5 | 321.3 | 319.3 | 327.6 | 259.9
1254 | 1114 | 526 | 442.4 | 483 | 439.1 | 364.2 | 323.8 | 321.6 | 319.6 | 327.9 | 260.1
1255 | 1115 | 526 | 442.5 | 483.1 | 439.1 | 364.5 | 324.1 | 321.9 | 319.8 | 328.1 | 260.3
1256 | 1116 | 526.1 | 442.5 | 483.1 | 439.2 | 364.7 | 324.3 | 322.2 | 320.1 | 328.4 | 260.4
1257 | 1117 | 526.1 | 442.6 | 483.2 | 439.3 | 365 | 324.6 | 322.5 | 320.4 | 328.7 | 260.6
1258 | 1118 | 526.1 | 442.7 | 483.2 | 439.4 | 365.2 | 324.9 | 322.8 | 320.7 | 328.9 | 260.8
1259 | 1119 | 526.1 | 442.8 | 483.3 | 439.5 | 365.5 | 325.2 | 323 | 320.9 | 329.1 | 261
1260 | 1120 | 526.1 | 442.9 | 483.3 | 439.6 | 365.7 | 325.4 | 323.3 | 321.2 | 329.4 | 261.2
1261 | 1121 | 526.1 | 442.9 | 483.4 | 439.6 | 365.9 | 325.7 | 323.6 | 321.5 | 329.7 | 261.4
1262 | 1122 | 526.1 | 443 | 483.4 | 439.7 | 366.2 | 326 | 323.8 | 321.8 | 329.9 | 261.6
1263 | 1123 | 526 | 443.1 | 483.4 | 439.8 | 366.4 | 326.3 | 324.1 | 322.1 | 330.2 | 261.9
1264 | 1124 | 526 | 443.2 | 483.5 | 439.9 | 366.6 | 326.5 | 324.4 | 322.4 | 330.5 | 262.1
1265 | 1125 | 525.9 | 443.2 | 483.6 | 440 | 366.8 | 326.8 | 324.7 | 322.6 | 330.8 | 262.3
1266 | 1126 | 526 | 443.3 | 483.6 | 440.1 | 367 | 327.1 | 324.9 | 322.9 | 331.1 | 262.6
1267 | 1127 | 526 | 443.4 | 483.7 | 440.1 | 367.2 | 327.3 | 325.2 | 323.2 | 331.5 | 262.8
1268 | 1128 | 525.9 | 443.5 | 483.7 | 440.2 | 367.4 | 327.6 | 325.5 | 323.4 | 331.8 | 263
1269 | 1129 | 526 | 443.6 | 483.8 | 440.3 | 367.7 | 327.9 | 325.8 | 323.7 | 332.1 | 263.2
1270 | 1130 | 526 | 443.6 | 483.8 | 440.4 | 367.9 | 328.1 | 326.1 | 324 | 332.5 | 263.5
1271 | 1131 | 526.1 | 443.7 | 483.9 | 440.4 | 368.1 | 328.4 | 326.3 | 324.3 | 332.8 | 263.7
1272 | 1132 | 526.1 | 443.8 | 484 | 440.5 | 368.3 | 328.6 | 326.6 | 324.6 | 333.1 | 263.9
1273 | 1133 | 526.1 | 443.9 | 484 | 440.6 | 368.5 | 328.9 | 326.9 | 324.8 | 333.3 | 264.2
1274 | 1134 | 526.1 | 444 | 484 | 440.7 | 368.8 | 329.2 | 327.2 | 325.1 | 333.6 | 264.4
1275 | 1135 | 526.1 | 444 | 484.1 | 440.8 | 369 | 329.4 | 327.4 | 325.4 | 333.9 | 264.7
1276 | 1136 | 526.1 | 444.1 | 484.1 | 440.9 | 369.2 | 329.7 | 327.7 | 325.6 | 334.3 | 265
1277 | 1137 | 526.1 | 444.2 | 484.2 | 440.9 | 369.5 | 330 | 328 | 325.9 | 334.5 | 265.2
1278 | 1138 | 526.1 | 444.3 | 484.3 | 441 | 369.7 | 330.2 | 328.2 | 326.2 | 334.9 | 265.5
1279 | 1139 | 526.1 | 444.3 | 484.3 | 441.1 | 370 | 330.5 | 328.5 | 326.5 | 335.2 | 265.8
1280 | 1140 | 526.2 | 444.4 | 484.4 | 441.2 | 370.2 | 330.8 | 328.8 | 326.8 | 335.5 | 266
1281 | 1141 | 526.2 | 444.5 | 484.4 | 441.2 | 370.4 | 331 | 329.1 | 327.1 | 335.8 | 266.3
1282 | 1142 | 526.2 | 444.6 | 484.4 | 441.3 | 370.7 | 331.3 | 329.3 | 327.3 | 336.2 | 266.6
1283 | 1143 | 526.2 | 444.7 | 484.5 | 441.4 | 371 | 331.5 | 329.6 | 327.5 | 336.5 | 266.8
1284 | 1144 | 526.2 | 444.7 | 484.6 | 441.5 | 371.1 | 331.8 | 329.9 | 327.8 | 336.8 | 267
1285 | 1145 | 526.2 | 444.8 | 484.7 | 441.6 | 371.4 | 332 | 330.1 | 328.1 | 337.1 | 267.3
1286 | 1146 | 526.2 | 444.9 | 484.7 | 441.7 | 371.7 | 332.3 | 330.4 | 328.4 | 337.4 | 267.5
1287 | 1147 | 526.2 | 445 | 484.7 | 441.8 | 371.9 | 332.6 | 330.7 | 328.6 | 337.7 | 267.8
1288 | 1148 | 526.2 | 445 | 484.8 | 441.8 | 372.1 | 332.8 | 331 | 328.9 | 338 | 268
1289 | 1149 | 526.2 | 445.1 | 484.8 | 441.9 | 372.3 | 333.1 | 331.2 | 329.2 | 338.2 | 268.2
1290 | 1150 | 526.2 | 445.2 | 484.9 | 442 | 372.6 | 333.4 | 331.5 | 329.5 | 338.4 | 268.6
1291 | 1151 | 526.2 | 445.2 | 484.9 | 442 | 372.8 | 333.6 | 331.7 | 329.8 | 338.6 | 269.1
1292 | 1152 | 526.2 | 445.3 | 484.9 | 442.1 | 373 | 333.9 | 332 | 330.1 | 338.9 | 269.4
1293 | 1153 | 526.1 | 445.4 | 485 | 442.2 | 373.3 | 334.1 | 332.2 | 330.4 | 339.1 | 269.7
1294 | 1154 | 526.1 | 445.5 | 485.1 | 442.3 | 373.6 | 334.4 | 332.5 | 330.6 | 339.3 | 269.9
1295 | 1155 | 526.1 | 445.6 | 485.1 | 442.4 | 373.8 | 334.7 | 332.8 | 330.9 | 339.6 | 270.2
1296 | 1156 | 526.1 | 445.6 | 485.2 | 442.4 | 374 | 334.9 | 333 | 331.2 | 339.8 | 270.4
1297 | 1157 | 526.1 | 445.7 | 485.2 | 442.5 | 374.3 | 335.2 | 333.3 | 331.4 | 340.1 | 270.6
1298 | 1158 | 526.1 | 445.8 | 485.3 | 442.6 | 374.5 | 335.4 | 333.6 | 331.7 | 340.3 | 270.7
1299 | 1159 | 526.1 | 445.9 | 485.3 | 442.7 | 374.8 | 335.7 | 333.8 | 332 | 340.5 | 271
1300 | 1160 | 526.1 | 445.9 | 485.3 | 442.7 | 375 | 336 | 334.1 | 332.3 | 340.8 | 271.2
1301 | 1161 | 526.1 | 446 | 485.4 | 442.8 | 375.2 | 336.2 | 334.4 | 332.5 | 341 | 271.4
1302 | 1162 | 526 | 446.1 | 485.4 | 442.9 | 375.5 | 336.5 | 334.6 | 332.8 | 341.3 | 271.7
1303 | 1163 | 526 | 446.1 | 485.5 | 442.9 | 375.7 | 336.7 | 334.9 | 333.1 | 341.6 | 271.9
1304 | 1164 | 526 | 446.2 | 485.5 | 443 | 375.9 | 337 | 335.1 | 333.4 | 341.8 | 272.1
1305 | 1165 | 526 | 446.3 | 485.5 | 443.1 | 376.2 | 337.2 | 335.4 | 333.6 | 341.9 | 272.4
1306 | 1166 | 526 | 446.4 | 485.6 | 443.2 | 376.4 | 337.5 | 335.6 | 333.8 | 342.1 | 272.6
1307 | 1167 | 526 | 446.4 | 485.6 | 443.2 | 376.6 | 337.7 | 335.9 | 334.1 | 342.2 | 272.8
1308 | 1168 | 526 | 446.5 | 485.7 | 443.3 | 376.8 | 338 | 336.1 | 334.4 | 342.4 | 273
1309 | 1169 | 526 | 446.6 | 485.7 | 443.4 | 377.1 | 338.2 | 336.4 | 334.6 | 342.5 | 273.3
1310 | 1170 | 526 | 446.6 | 485.8 | 443.5 | 377.3 | 338.5 | 336.7 | 334.9 | 342.6 | 273.5
1311 | 1171 | 526.1 | 446.7 | 485.8 | 443.5 | 377.6 | 338.7 | 336.9 | 335.3 | 342.8 | 273.7
1312 | 1172 | 526 | 446.8 | 485.8 | 443.6 | 377.9 | 338.9 | 337.2 | 335.5 | 343 | 274
1313 | 1173 | 526 | 446.9 | 485.9 | 443.7 | 378.1 | 339.2 | 337.5 | 335.8 | 343.1 | 274.2
1314 | 1174 | 526 | 446.9 | 485.9 | 443.8 | 378.4 | 339.4 | 337.7 | 336.1 | 343.3 | 274.4
1315 | 1175 | 526 | 447 | 486 | 443.8 | 378.7 | 339.7 | 338 | 336.4 | 343.5 | 274.6
1316 | 1176 | 525.9 | 447.1 | 486 | 443.9 | 378.9 | 339.9 | 338.2 | 336.7 | 343.7 | 274.8
1317 | 1177 | 525.9 | 447.1 | 486.1 | 444 | 379.1 | 340.2 | 338.5 | 336.9 | 343.9 | 275
1318 | 1178 | 525.9 | 447.2 | 486.1 | 444 | 379.4 | 340.4 | 338.8 | 337.2 | 344.2 | 275.3
1319 | 1179 | 526 | 447.3 | 486.2 | 444.1 | 379.7 | 340.7 | 339.1 | 337.4 | 344.4 | 275.5
1320 | 1180 | 525.9 | 447.4 | 486.3 | 444.2 | 379.8 | 340.9 | 339.3 | 337.8 | 344.6 | 275.8
1321 | 1181 | 525.9 | 447.4 | 486.3 | 444.3 | 380.1 | 341.2 | 339.6 | 338 | 344.8 | 276
1322 | 1182 | 525.9 | 447.5 | 486.3 | 444.3 | 380.3 | 341.4 | 339.8 | 338.3 | 345 | 276.3
1323 | 1183 | 525.9 | 447.6 | 486.3 | 444.4 | 380.6 | 341.6 | 340.1 | 338.5 | 345.2 | 276.5
1324 | 1184 | 525.9 | 447.6 | 486.4 | 444.5 | 380.8 | 341.9 | 340.4 | 338.8 | 345.3 | 276.8
1325 | 1185 | 525.9 | 447.7 | 486.5 | 444.6 | 381 | 342.1 | 340.6 | 339 | 345.5 | 277
1326 | 1186 | 525.9 | 447.8 | 486.5 | 444.6 | 381.3 | 342.4 | 340.9 | 339.3 | 345.7 | 277.2
1327 | 1187 | 525.9 | 447.8 | 486.5 | 444.7 | 381.4 | 342.6 | 341.2 | 339.6 | 345.9 | 277.4
1328 | 1188 | 525.8 | 447.9 | 486.6 | 444.8 | 381.7 | 342.8 | 341.4 | 339.8 | 346 | 277.6
1329 | 1189 | 525.9 | 448 | 486.6 | 444.8 | 381.9 | 343.1 | 341.7 | 340.1 | 346.2 | 277.8
1330 | 1190 | 525.9 | 448.1 | 486.6 | 444.9 | 382.1 | 343.3 | 341.9 | 340.3 | 346.4 | 278
1331 | 1191 | 525.9 | 448.1 | 486.7 | 445 | 382.3 | 343.6 | 342.2 | 340.5 | 346.6 | 278.2
1332 | 1192 | 525.9 | 448.2 | 486.7 | 445.1 | 382.6 | 343.8 | 342.4 | 340.8 | 346.7 | 278.4
1333 | 1193 | 525.9 | 448.3 | 486.8 | 445.1 | 382.8 | 344.1 | 342.7 | 341.1 | 346.9 | 278.5
1334 | 1194 | 525.9 | 448.3 | 486.8 | 445.2 | 382.9 | 344.3 | 343 | 341.3 | 347 | 278.6
1335 | 1195 | 525.9 | 448.4 | 486.9 | 445.3 | 383.1 | 344.5 | 343.2 | 341.6 | 347.1 | 278.8
1336 | 1196 | 525.9 | 448.5 | 486.9 | 445.3 | 383.3 | 344.7 | 343.5 | 341.8 | 347.2 | 279
1337 | 1197 | 526 | 448.5 | 487 | 445.4 | 383.5 | 345 | 343.7 | 342.1 | 347.4 | 279.2
1338 | 1198 | 526 | 448.6 | 487 | 445.5 | 383.7 | 345.2 | 344 | 342.3 | 347.6 | 279.4
1339 | 1199 | 526 | 448.7 | 487 | 445.6 | 383.9 | 345.5 | 344.2 | 342.5 | 347.8 | 279.6
1340 | 1200 | 526 | 448.8 | 487.1 | 445.6 | 384.1 | 345.7 | 344.5 | 342.8 | 347.9 | 279.9
1341 | 1201 | 526.1 | 448.8 | 487.1 | 445.7 | 384.2 | 345.9 | 344.8 | 343 | 348.1 | 280.1
1342 | 1202 | 526.1 | 448.9 | 487.2 | 445.8 | 384.4 | 346.2 | 345 | 343.2 | 348.2 | 280.4
1343 | 1203 | 526.1 | 449 | 487.2 | 445.8 | 384.7 | 346.4 | 345.3 | 343.4 | 348.4 | 280.6
1344 | 1204 | 526.1 | 449 | 487.3 | 445.9 | 384.8 | 346.6 | 345.5 | 343.7 | 348.5 | 280.9
1345 | 1205 | 526.1 | 449.1 | 487.3 | 446 | 385 | 346.9 | 345.8 | 344 | 348.6 | 281.1
1346 | 1206 | 526.1 | 449.1 | 487.4 | 446 | 385.3 | 347.1 | 346 | 344.2 | 348.6 | 281.4
1347 | 1207 | 526.2 | 449.2 | 487.5 | 446.1 | 385.6 | 347.3 | 346.3 | 344.5 | 348.7 | 281.6
1348 | 1208 | 526.2 | 449.3 | 487.5 | 446.2 | 385.8 | 347.5 | 346.6 | 344.7 | 348.8 | 281.8
1349 | 1209 | 526.2 | 449.3 | 487.6 | 446.2 | 386.1 | 347.8 | 346.8 | 344.9 | 348.9 | 282.1
1350 | 1210 | 526.3 | 449.4 | 487.6 | 446.3 | 386.3 | 348 | 347.1 | 345.2 | 349 | 282.3
1351 | 1211 | 526.3 | 449.5 | 487.6 | 446.4 | 386.5 | 348.3 | 347.3 | 345.4 | 349.1 | 282.5
1352 | 1212 | 526.4 | 449.5 | 487.7 | 446.5 | 386.8 | 348.5 | 347.5 | 345.6 | 349.2 | 282.8
1353 | 1213 | 526.4 | 449.6 | 487.7 | 446.5 | 387 | 348.8 | 347.8 | 345.8 | 349.3 | 283.1
1354 | 1214 | 526.4 | 449.6 | 487.8 | 446.6 | 387.2 | 349 | 348.1 | 346.1 | 349.5 | 283.3
1355 | 1215 | 526.4 | 449.7 | 487.8 | 446.6 | 387.4 | 349.2 | 348.3 | 346.4 | 349.6 | 283.6
1356 | 1216 | 526.4 | 449.8 | 487.8 | 446.7 | 387.7 | 349.5 | 348.6 | 346.6 | 349.7 | 283.8
1357 | 1217 | 526.3 | 449.8 | 487.9 | 446.8 | 387.9 | 349.7 | 348.8 | 346.9 | 349.8 | 284.1
1358 | 1218 | 526.3 | 449.9 | 488 | 446.8 | 388.1 | 350 | 349.1 | 347.1 | 349.9 | 284.3
1359 | 1219 | 526.3 | 449.9 | 488 | 446.9 | 388.3 | 350.2 | 349.4 | 347.3 | 350.1 | 284.5
1360 | 1220 | 526.3 | 450 | 488 | 447 | 388.5 | 350.5 | 349.6 | 347.6 | 350.2 | 284.8
1361 | 1221 | 526.2 | 450.1 | 488.1 | 447 | 388.7 | 350.7 | 349.9 | 347.8 | 350.4 | 285.1
1362 | 1222 | 526.2 | 450.1 | 488.1 | 447.1 | 388.9 | 350.9 | 350.1 | 348.1 | 350.5 | 285.2
1363 | 1223 | 526.2 | 450.2 | 488.1 | 447.2 | 389.1 | 351.2 | 350.4 | 348.3 | 350.7 | 285.5
1364 | 1224 | 526.2 | 450.3 | 488.2 | 447.2 | 389.4 | 351.4 | 350.7 | 348.6 | 350.8 | 285.7
1365 | 1225 | 526.2 | 450.3 | 488.2 | 447.3 | 389.6 | 351.7 | 350.9 | 348.8 | 351 | 285.9
1366 | 1226 | 526.1 | 450.4 | 488.2 | 447.4 | 389.8 | 351.9 | 351.2 | 349.1 | 351.2 | 286.2
1367 | 1227 | 526.1 | 450.5 | 488.3 | 447.4 | 390 | 352.2 | 351.4 | 349.3 | 351.4 | 286.4
1368 | 1228 | 526.1 | 450.5 | 488.3 | 447.5 | 390.3 | 352.4 | 351.7 | 349.5 | 351.6 | 286.7
1369 | 1229 | 526 | 450.6 | 488.4 | 447.6 | 390.5 | 352.6 | 351.9 | 349.8 | 351.8 | 286.8
1370 | 1230 | 526 | 450.7 | 488.4 | 447.6 | 390.7 | 352.9 | 352.2 | 350 | 352 | 286.9
1371 | 1231 | 525.9 | 450.7 | 488.4 | 447.7 | 390.9 | 353.1 | 352.5 | 350.3 | 352.2 | 287
1372 | 1232 | 525.9 | 450.8 | 488.4 | 447.8 | 391.1 | 353.4 | 352.7 | 350.6 | 352.4 | 287.1
1373 | 1233 | 525.9 | 450.8 | 488.5 | 447.8 | 391.4 | 353.6 | 353 | 350.9 | 352.5 | 287.3
1374 | 1234 | 525.8 | 450.9 | 488.5 | 447.9 | 391.6 | 353.9 | 353.2 | 351.1 | 352.7 | 287.4
1375 | 1235 | 525.8 | 451 | 488.6 | 448 | 391.8 | 354.1 | 353.5 | 351.4 | 352.9 | 287.6
1376 | 1236 | 525.8 | 451 | 488.6 | 448 | 392 | 354.3 | 353.8 | 351.5 | 353 | 287.8
1377 | 1237 | 525.9 | 451.1 | 488.6 | 448.1 | 392.3 | 354.6 | 354 | 351.7 | 353.1 | 288
1378 | 1238 | 525.8 | 451.1 | 488.7 | 448.1 | 392.5 | 354.8 | 354.3 | 351.9 | 353.3 | 288.2
1379 | 1239 | 525.8 | 451.2 | 488.7 | 448.2 | 392.7 | 355.1 | 354.5 | 352.2 | 353.5 | 288.5
1380 | 1240 | 525.8 | 451.3 | 488.8 | 448.3 | 393 | 355.3 | 354.8 | 352.4 | 353.7 | 289.4
1381 | 1241 | 525.8 | 451.3 | 488.8 | 448.3 | 393.2 | 355.5 | 355 | 352.7 | 353.9 | 290
1382 | 1242 | 525.8 | 451.4 | 488.8 | 448.4 | 393.5 | 355.8 | 355.3 | 352.9 | 354.1 | 290.4
1383 | 1243 | 525.8 | 451.4 | 488.9 | 448.4 | 393.7 | 356 | 355.5 | 353.1 | 354.4 | 290.7
1384 | 1244 | 525.8 | 451.5 | 488.9 | 448.5 | 393.9 | 356.3 | 355.8 | 353.4 | 354.6 | 290.9
1385 | 1245 | 525.8 | 451.6 | 489 | 448.6 | 394.2 | 356.5 | 356 | 353.6 | 354.8 | 291.1
1386 | 1246 | 525.8 | 451.6 | 489 | 448.7 | 394.4 | 356.8 | 356.3 | 353.9 | 355 | 291.3
1387 | 1247 | 525.8 | 451.7 | 489 | 448.7 | 394.7 | 357 | 356.5 | 354.1 | 355.3 | 291.6
1388 | 1248 | 525.9 | 451.8 | 489.1 | 448.8 | 394.9 | 357.2 | 356.8 | 354.3 | 355.5 | 291.7
1389 | 1249 | 525.9 | 451.8 | 489.1 | 448.8 | 395.2 | 357.5 | 357 | 354.6 | 355.7 | 291.9
1390 | 1250 | 525.9 | 451.9 | 489.2 | 448.9 | 395.4 | 357.7 | 357.3 | 354.9 | 355.9 | 292.1
1391 | 1251 | 525.9 | 451.9 | 489.2 | 449 | 395.7 | 357.9 | 357.5 | 355.1 | 356 | 292.2
1392 | 1252 | 525.9 | 452 | 489.2 | 449 | 396 | 358.2 | 357.8 | 355.4 | 356.2 | 292.4
1393 | 1253 | 525.9 | 452 | 489.3 | 449.1 | 396.3 | 358.4 | 358.1 | 355.6 | 356.3 | 292.6
1394 | 1254 | 525.9 | 452.1 | 489.3 | 449.1 | 396.6 | 358.6 | 358.3 | 355.9 | 356.5 | 292.7
1395 | 1255 | 526 | 452.2 | 489.3 | 449.2 | 396.9 | 358.9 | 358.6 | 356.2 | 356.7 | 292.8
1396 | 1256 | 526 | 452.2 | 489.4 | 449.3 | 397.2 | 359.1 | 358.9 | 356.5 | 356.9 | 292.9
1397 | 1257 | 525.9 | 452.3 | 489.4 | 449.3 | 397.6 | 359.4 | 359.1 | 356.8 | 357.1 | 293
1398 | 1258 | 526 | 452.3 | 489.5 | 449.4 | 397.9 | 359.6 | 359.4 | 357 | 357.3 | 293.2
1399 | 1259 | 526 | 452.4 | 489.5 | 449.4 | 398.2 | 359.9 | 359.6 | 357.3 | 357.5 | 293.4
1400 | 1260 | 526 | 452.5 | 489.5 | 449.5 | 398.5 | 360.1 | 359.8 | 357.6 | 357.7 | 293.5
1401 | 1261 | 525.9 | 452.5 | 489.6 | 449.5 | 398.9 | 360.4 | 360.1 | 357.8 | 357.8 | 293.7
1402 | 1262 | 525.9 | 452.6 | 489.6 | 449.6 | 399.2 | 360.7 | 360.3 | 358.1 | 358 | 293.9
1403 | 1263 | 525.9 | 452.6 | 489.6 | 449.7 | 399.5 | 360.9 | 360.6 | 358.4 | 358.3 | 294
1404 | 1264 | 525.9 | 452.7 | 489.7 | 449.7 | 399.8 | 361.2 | 360.8 | 358.7 | 358.5 | 294.2
1405 | 1265 | 525.9 | 452.7 | 489.7 | 449.8 | 400.1 | 361.4 | 361 | 359 | 358.7 | 294.4
1406 | 1266 | 525.8 | 452.8 | 489.7 | 449.9 | 400.5 | 361.7 | 361.3 | 359.3 | 358.9 | 294.6
1407 | 1267 | 525.9 | 452.9 | 489.8 | 449.9 | 400.8 | 362 | 361.5 | 359.5 | 359.1 | 294.8
1408 | 1268 | 525.9 | 452.9 | 489.8 | 450 | 401.1 | 362.2 | 361.7 | 359.8 | 359.2 | 295
1409 | 1269 | 525.9 | 453 | 489.9 | 450.1 | 401.4 | 362.5 | 361.9 | 360 | 359.4 | 295.1
1410 | 1270 | 525.9 | 453 | 489.9 | 450.1 | 401.8 | 362.8 | 362.1 | 360.2 | 359.5 | 295.3
1411 | 1271 | 525.9 | 453.1 | 489.9 | 450.2 | 402.1 | 363 | 362.4 | 360.4 | 359.7 | 295.6
1412 | 1272 | 525.9 | 453.2 | 489.9 | 450.2 | 402.4 | 363.4 | 362.6 | 360.7 | 359.8 | 295.8
1413 | 1273 | 525.9 | 453.2 | 490 | 450.3 | 402.8 | 363.6 | 362.8 | 360.9 | 360 | 296
1414 | 1274 | 525.9 | 453.3 | 490 | 450.3 | 403.1 | 363.9 | 363 | 361.1 | 360.1 | 296.2
1415 | 1275 | 526 | 453.3 | 490 | 450.4 | 403.5 | 364.2 | 363.3 | 361.4 | 360.3 | 296.4
1416 | 1276 | 526 | 453.4 | 490 | 450.5 | 403.8 | 364.5 | 363.5 | 361.6 | 360.5 | 296.6
1417 | 1277 | 525.9 | 453.5 | 490.1 | 450.5 | 404.1 | 364.8 | 363.7 | 361.9 | 360.7 | 296.8
1418 | 1278 | 525.9 | 453.5 | 490.1 | 450.6 | 404.4 | 365.1 | 363.9 | 362.1 | 360.8 | 296.9
1419 | 1279 | 525.9 | 453.6 | 490.2 | 450.7 | 404.8 | 365.4 | 364.1 | 362.4 | 360.9 | 297.2
1420 | 1280 | 525.9 | 453.6 | 490.2 | 450.7 | 405.1 | 365.7 | 364.3 | 362.6 | 361.1 | 297.4
1421 | 1281 | 525.9 | 453.7 | 490.3 | 450.8 | 405.4 | 366 | 364.5 | 362.8 | 361.2 | 297.6
1422 | 1282 | 525.9 | 453.8 | 490.3 | 450.8 | 405.8 | 366.3 | 364.7 | 363.1 | 361.3 | 297.8
1423 | 1283 | 525.9 | 453.8 | 490.3 | 450.9 | 406.1 | 366.6 | 364.9 | 363.4 | 361.4 | 298
1424 | 1284 | 526 | 453.9 | 490.3 | 450.9 | 406.4 | 366.9 | 365.1 | 363.6 | 361.6 | 298.2
1425 | 1285 | 526 | 453.9 | 490.4 | 451 | 406.7 | 367.2 | 365.4 | 363.9 | 361.7 | 298.3
1426 | 1286 | 525.9 | 454 | 490.4 | 451.1 | 407 | 367.5 | 365.6 | 364.1 | 361.8 | 298.6
1427 | 1287 | 525.9 | 454 | 490.5 | 451.1 | 407.3 | 367.7 | 365.8 | 364.4 | 362 | 298.7
1428 | 1288 | 526 | 454.1 | 490.5 | 451.2 | 407.6 | 368 | 365.9 | 364.6 | 362 | 298.9
1429 | 1289 | 526 | 454.1 | 490.5 | 451.2 | 407.9 | 368.2 | 366.1 | 364.8 | 362.1 | 299.1
1430 | 1290 | 526 | 454.2 | 490.5 | 451.3 | 408.2 | 368.4 | 366.3 | 365.1 | 362.3 | 299.3
1431 | 1291 | 526 | 454.3 | 490.5 | 451.3 | 408.5 | 368.7 | 366.5 | 365.3 | 362.4 | 299.5
1432 | 1292 | 526 | 454.3 | 490.6 | 451.4 | 408.8 | 368.9 | 366.7 | 365.5 | 362.5 | 299.6
1433 | 1293 | 526 | 454.4 | 490.6 | 451.5 | 409 | 369.1 | 366.9 | 365.7 | 362.6 | 299.8
1434 | 1294 | 526 | 454.4 | 490.6 | 451.5 | 409.3 | 369.3 | 367 | 366 | 362.7 | 300
1435 | 1295 | 526 | 454.5 | 490.7 | 451.6 | 409.5 | 369.6 | 367.2 | 366.2 | 362.8 | 300.2
1436 | 1296 | 526 | 454.5 | 490.7 | 451.6 | 409.8 | 369.8 | 367.4 | 366.5 | 362.9 | 300.4
1437 | 1297 | 526.1 | 454.6 | 490.8 | 451.7 | 410.1 | 370 | 367.6 | 366.8 | 363.1 | 300.6
1438 | 1298 | 526.2 | 454.6 | 490.8 | 451.7 | 410.4 | 370.3 | 367.7 | 367 | 363.2 | 300.8
1439 | 1299 | 526.2 | 454.7 | 490.8 | 451.8 | 410.6 | 370.5 | 367.8 | 367.3 | 363.2 | 301
1440 | 1300 | 526.2 | 454.7 | 490.8 | 451.9 | 410.8 | 370.8 | 367.9 | 367.5 | 363.3 | 301.2
1441 | 1301 | 526.2 | 454.8 | 490.9 | 451.9 | 411.1 | 371.1 | 368.1 | 367.8 | 363.4 | 301.4
1442 | 1302 | 526.2 | 454.9 | 490.8 | 452 | 411.4 | 371.3 | 368.2 | 368 | 363.5 | 301.6
1443 | 1303 | 526.2 | 454.9 | 490.9 | 452.1 | 411.6 | 371.6 | 368.3 | 368.3 | 363.6 | 301.9
1444 | 1304 | 526.2 | 455 | 490.9 | 452.1 | 411.9 | 371.9 | 368.5 | 368.6 | 363.6 | 302.2
1445 | 1305 | 526.2 | 455 | 490.9 | 452.2 | 412.1 | 372.2 | 368.6 | 368.8 | 363.6 | 302.4
1446 | 1306 | 526.2 | 455.1 | 491 | 452.2 | 412.4 | 372.6 | 368.7 | 369.1 | 363.7 | 302.6
1447 | 1307 | 526.2 | 455.2 | 491 | 452.3 | 412.6 | 372.9 | 368.8 | 369.3 | 363.8 | 302.8
1448 | 1308 | 526.2 | 455.2 | 491.1 | 452.3 | 412.9 | 373.2 | 368.9 | 369.6 | 363.9 | 303
1449 | 1309 | 526.2 | 455.3 | 491.1 | 452.4 | 413.1 | 373.5 | 369 | 369.9 | 363.9 | 303.1
1450 | 1310 | 526.3 | 455.3 | 491.2 | 452.5 | 413.4 | 373.8 | 369.1 | 370.3 | 364 | 303.3
1451 | 1311 | 526.3 | 455.4 | 491.2 | 452.5 | 413.7 | 374.1 | 369.2 | 370.6 | 364.1 | 303.5
1452 | 1312 | 526.3 | 455.4 | 491.2 | 452.6 | 413.9 | 374.4 | 369.3 | 370.9 | 364.1 | 303.7
1453 | 1313 | 526.3 | 455.5 | 491.2 | 452.6 | 414.2 | 374.7 | 369.4 | 371.1 | 364.2 | 303.8
1454 | 1314 | 526.3 | 455.5 | 491.3 | 452.7 | 414.3 | 375 | 369.5 | 371.4 | 364.3 | 303.9
1455 | 1315 | 526.3 | 455.6 | 491.3 | 452.8 | 414.6 | 375.3 | 369.6 | 371.6 | 364.3 | 304.1
1456 | 1316 | 526.4 | 455.7 | 491.3 | 452.8 | 414.9 | 375.6 | 369.7 | 371.9 | 364.4 | 304.3
1457 | 1317 | 526.3 | 455.7 | 491.4 | 452.9 | 415.1 | 375.9 | 369.8 | 372.2 | 364.4 | 304.4
1458 | 1318 | 526.3 | 455.7 | 491.4 | 452.9 | 415.3 | 376.2 | 369.9 | 372.5 | 364.4 | 304.6
1459 | 1319 | 526.3 | 455.8 | 491.4 | 453 | 415.6 | 376.5 | 370 | 372.7 | 364.4 | 304.7
1460 | 1320 | 526.3 | 455.9 | 491.5 | 453 | 415.8 | 376.8 | 370.1 | 372.9 | 364.6 | 304.9
1461 | 1321 | 526.2 | 455.9 | 491.5 | 453.1 | 416.1 | 377.1 | 370.2 | 373.2 | 364.8 | 305
1462 | 1322 | 526.2 | 456 | 491.6 | 453.2 | 416.4 | 377.4 | 370.3 | 373.4 | 365 | 305.2
1463 | 1323 | 526.2 | 456 | 491.6 | 453.2 | 416.7 | 377.7 | 370.5 | 373.7 | 365.1 | 305.5
1464 | 1324 | 526.2 | 456.1 | 491.6 | 453.3 | 417 | 378 | 370.6 | 374 | 365.2 | 305.6
1465 | 1325 | 526.2 | 456.1 | 491.6 | 453.3 | 417.3 | 378.2 | 370.7 | 374.2 | 365.3 | 305.9
1466 | 1326 | 526.2 | 456.2 | 491.7 | 453.4 | 417.5 | 378.5 | 370.9 | 374.4 | 365.4 | 306.2
1467 | 1327 | 526.2 | 456.2 | 491.7 | 453.4 | 417.8 | 378.8 | 371 | 374.7 | 365.5 | 306.4
1468 | 1328 | 526.2 | 456.3 | 491.7 | 453.5 | 418.1 | 379.1 | 371.1 | 374.9 | 365.6 | 306.8
1469 | 1329 | 526.1 | 456.4 | 491.7 | 453.5 | 418.4 | 379.4 | 371.3 | 375.1 | 365.6 | 307.1
1470 | 1330 | 526.1 | 456.4 | 491.7 | 453.6 | 418.7 | 379.7 | 371.4 | 375.3 | 365.6 | 307.4
1471 | 1331 | 526.1 | 456.5 | 491.8 | 453.7 | 419 | 380 | 371.6 | 375.6 | 365.7 | 307.7
1472 | 1332 | 526 | 456.5 | 491.8 | 453.7 | 419.4 | 380.3 | 371.7 | 375.8 | 365.8 | 308
1473 | 1333 | 526 | 456.6 | 491.8 | 453.7 | 419.7 | 380.6 | 371.9 | 376.1 | 365.8 | 308.2
1474 | 1334 | 526 | 456.6 | 491.9 | 453.8 | 420 | 380.8 | 372.1 | 376.3 | 365.8 | 308.5
1475 | 1335 | 526 | 456.7 | 491.9 | 453.8 | 420.3 | 381.1 | 372.3 | 376.5 | 365.8 | 308.8
1476 | 1336 | 526 | 456.7 | 491.9 | 453.9 | 420.6 | 381.4 | 372.5 | 376.8 | 365.9 | 309.1
1477 | 1337 | 526 | 456.8 | 491.9 | 453.9 | 420.9 | 381.7 | 372.7 | 377 | 365.9 | 309.4
1478 | 1338 | 526 | 456.8 | 492 | 454 | 421.2 | 381.9 | 372.9 | 377.2 | 366.1 | 309.6
1479 | 1339 | 526 | 456.8 | 492 | 454 | 421.6 | 382.2 | 373.1 | 377.4 | 366.4 | 309.8
1480 | 1340 | 526 | 456.9 | 492 | 454.1 | 421.9 | 382.5 | 373.3 | 377.6 | 366.7 | 310
1481 | 1341 | 526 | 457 | 492 | 454.1 | 422.2 | 382.7 | 373.6 | 377.8 | 367.1 | 310.2
1482 | 1342 | 526 | 457 | 492.1 | 454.2 | 422.6 | 383 | 373.8 | 378 | 367.5 | 310.3
1483 | 1343 | 526 | 457.1 | 492.1 | 454.2 | 422.9 | 383.2 | 374 | 378.3 | 367.9 | 310.5
1484 | 1344 | 526 | 457.1 | 492.1 | 454.3 | 423.2 | 383.5 | 374.3 | 378.5 | 368.3 | 310.6
1485 | 1345 | 526 | 457.1 | 492.2 | 454.3 | 423.5 | 383.7 | 374.5 | 378.7 | 368.6 | 310.8
1486 | 1346 | 526 | 457.2 | 492.2 | 454.4 | 423.8 | 383.9 | 374.7 | 378.9 | 368.9 | 311
1487 | 1347 | 526.1 | 457.3 | 492.2 | 454.4 | 424.1 | 384.2 | 375 | 379.1 | 369.1 | 311.2
1488 | 1348 | 526.1 | 457.3 | 492.2 | 454.5 | 424.5 | 384.4 | 375.2 | 379.4 | 369.3 | 311.4
1489 | 1349 | 526.1 | 457.3 | 492.3 | 454.5 | 424.8 | 384.6 | 375.5 | 379.6 | 369.4 | 311.5
1490 | 1350 | 526.1 | 457.4 | 492.3 | 454.6 | 425.1 | 384.8 | 375.7 | 379.9 | 369.6 | 311.7
1491 | 1351 | 526 | 457.4 | 492.3 | 454.6 | 425.5 | 385.1 | 376 | 380.2 | 369.7 | 311.9
1492 | 1352 | 526 | 457.5 | 492.3 | 454.7 | 425.8 | 385.3 | 376.2 | 380.4 | 369.7 | 312.1
1493 | 1353 | 526 | 457.6 | 492.3 | 454.8 | 426.2 | 385.6 | 376.4 | 380.6 | 369.8 | 312.3
1494 | 1354 | 526 | 457.6 | 492.3 | 454.8 | 426.5 | 385.8 | 376.7 | 380.9 | 369.9 | 312.4
1495 | 1355 | 526 | 457.6 | 492.4 | 454.8 | 426.8 | 386.1 | 376.9 | 381.1 | 370 | 312.6
1496 | 1356 | 525.9 | 457.7 | 492.4 | 454.9 | 427.2 | 386.3 | 377.2 | 381.3 | 370.1 | 312.8
1497 | 1357 | 525.9 | 457.7 | 492.4 | 455 | 427.6 | 386.6 | 377.4 | 381.6 | 370.2 | 312.9
1498 | 1358 | 525.9 | 457.8 | 492.4 | 455 | 428.1 | 386.8 | 377.7 | 381.8 | 370.3 | 313.1
1499 | 1359 | 525.9 | 457.8 | 492.4 | 455 | 428.6 | 387.1 | 377.9 | 382 | 370.3 | 313.3
1500 | 1360 | 525.9 | 457.9 | 492.5 | 455.1 | 429.1 | 387.3 | 378.2 | 382.3 | 370.4 | 313.5
1501 | 1361 | 525.9 | 457.9 | 492.4 | 455.2 | 429.6 | 387.6 | 378.4 | 382.4 | 370.5 | 313.8
1502 | 1362 | 525.9 | 458 | 492.5 | 455.2 | 429.9 | 387.8 | 378.6 | 382.7 | 370.5 | 314
1503 | 1363 | 525.9 | 458 | 492.5 | 455.3 | 430.4 | 388 | 378.9 | 382.9 | 370.7 | 314.2
1504 | 1364 | 525.9 | 458.1 | 492.5 | 455.3 | 430.8 | 388.3 | 379.1 | 383.1 | 370.8 | 314.5
1505 | 1365 | 525.9 | 458.1 | 492.6 | 455.3 | 431.2 | 388.5 | 379.3 | 383.2 | 371 | 314.7
1506 | 1366 | 525.9 | 458.2 | 492.6 | 455.4 | 431.5 | 388.7 | 379.6 | 383.4 | 371.1 | 314.9
1507 | 1367 | 525.9 | 458.2 | 492.6 | 455.5 | 431.8 | 388.9 | 379.8 | 383.7 | 371.2 | 315.2
1508 | 1368 | 525.9 | 458.3 | 492.6 | 455.5 | 432.1 | 389.2 | 380 | 383.9 | 371.3 | 315.4
1509 | 1369 | 525.9 | 458.3 | 492.7 | 455.6 | 432.4 | 389.4 | 380.3 | 384.1 | 371.4 | 315.6
1510 | 1370 | 525.9 | 458.4 | 492.7 | 455.6 | 432.6 | 389.6 | 380.5 | 384.2 | 371.5 | 315.8
1511 | 1371 | 526 | 458.4 | 492.8 | 455.7 | 432.8 | 389.8 | 380.7 | 384.4 | 371.6 | 316
1512 | 1372 | 526 | 458.5 | 492.8 | 455.7 | 433 | 390.1 | 380.9 | 384.6 | 371.9 | 316.3
1513 | 1373 | 526 | 458.5 | 492.8 | 455.7 | 433.2 | 390.3 | 381.2 | 384.7 | 372.1 | 316.5
1514 | 1374 | 526 | 458.6 | 492.8 | 455.8 | 433.3 | 390.6 | 381.4 | 384.7 | 372.3 | 316.7
1515 | 1375 | 526 | 458.6 | 492.8 | 455.9 | 433.5 | 390.8 | 381.6 | 385 | 372.4 | 316.9
1516 | 1376 | 526 | 458.7 | 492.9 | 455.9 | 433.7 | 391 | 381.8 | 385.2 | 372.5 | 317.1
1517 | 1377 | 526 | 458.7 | 492.9 | 456 | 433.8 | 391.2 | 382 | 385.3 | 372.8 | 317.4
1518 | 1378 | 526 | 458.8 | 492.9 | 456 | 433.9 | 391.4 | 382.3 | 385.5 | 373.1 | 317.6
1519 | 1379 | 526 | 458.8 | 493 | 456.1 | 434 | 391.6 | 382.5 | 385.6 | 373.4 | 317.9
1520 | 1380 | 526 | 458.9 | 493 | 456.1 | 434.1 | 391.8 | 382.7 | 385.7 | 373.6 | 318.2
1521 | 1381 | 526 | 458.9 | 493 | 456.2 | 434.3 | 392 | 382.9 | 385.9 | 373.8 | 318.4
1522 | 1382 | 526 | 459 | 493 | 456.2 | 434.4 | 392.2 | 383.1 | 386.2 | 374.3 | 318.7
1523 | 1383 | 526.1 | 459 | 493.1 | 456.3 | 434.5 | 392.4 | 383.3 | 386.3 | 374.7 | 318.9
1524 | 1384 | 526.1 | 459.1 | 493.1 | 456.3 | 434.7 | 392.6 | 383.5 | 386.6 | 375.2 | 319.2
1525 | 1385 | 526.1 | 459.1 | 493.1 | 456.4 | 434.9 | 392.8 | 383.7 | 386.8 | 375.6 | 319.4
1526 | 1386 | 526.1 | 459.2 | 493.1 | 456.4 | 435 | 393.1 | 383.9 | 387 | 375.8 | 319.6
1527 | 1387 | 526.1 | 459.2 | 493.1 | 456.4 | 435.1 | 393.3 | 384.1 | 387.3 | 375.9 | 319.7
1528 | 1388 | 526.2 | 459.3 | 493.1 | 456.5 | 435.3 | 393.5 | 384.3 | 387.4 | 376 | 320
1529 | 1389 | 526.2 | 459.3 | 493.2 | 456.5 | 435.4 | 393.7 | 384.5 | 387.5 | 376 | 320.2
1530 | 1390 | 526.2 | 459.4 | 493.2 | 456.6 | 435.5 | 393.9 | 384.7 | 387.7 | 376 | 320.4
1531 | 1391 | 526.2 | 459.4 | 493.3 | 456.6 | 435.6 | 394.1 | 384.9 | 387.9 | 375.9 | 320.7
1532 | 1392 | 526.2 | 459.5 | 493.3 | 456.7 | 435.6 | 394.3 | 385.1 | 388.1 | 375.9 | 320.9
1533 | 1393 | 526.2 | 459.5 | 493.4 | 456.7 | 435.7 | 394.5 | 385.3 | 388.3 | 375.9 | 321.1
1534 | 1394 | 526.2 | 459.6 | 493.4 | 456.8 | 435.8 | 394.7 | 385.5 | 388.5 | 376 | 321.4
1535 | 1395 | 526.2 | 459.6 | 493.4 | 456.8 | 435.8 | 395 | 385.7 | 388.6 | 376.1 | 321.6
1536 | 1396 | 526.3 | 459.7 | 493.5 | 456.9 | 435.9 | 395.2 | 385.9 | 388.7 | 376.3 | 321.8
1537 | 1397 | 526.3 | 459.7 | 493.4 | 456.9 | 436 | 395.4 | 386.1 | 388.8 | 376.4 | 322.1
1538 | 1398 | 526.3 | 459.8 | 493.4 | 457 | 436 | 395.6 | 386.3 | 389 | 376.7 | 322.2
1539 | 1399 | 526.3 | 459.8 | 493.5 | 457 | 436.1 | 395.8 | 386.5 | 389.2 | 377 | 322.3
1540 | 1400 | 526.3 | 459.9 | 493.5 | 457.1 | 436.1 | 396 | 386.7 | 389.4 | 377.3 | 322.5
1541 | 1401 | 526.3 | 459.9 | 493.5 | 457.1 | 436.2 | 396.2 | 386.9 | 389.5 | 377.6 | 322.7
1542 | 1402 | 526.3 | 460 | 493.6 | 457.2 | 436.3 | 396.4 | 387.1 | 389.7 | 377.9 | 322.8
1543 | 1403 | 526.3 | 460 | 493.6 | 457.2 | 436.3 | 396.6 | 387.3 | 389.9 | 378 | 323.1
1544 | 1404 | 526.3 | 460.1 | 493.6 | 457.2 | 436.3 | 396.9 | 387.5 | 390 | 378.2 | 323.2
1545 | 1405 | 526.3 | 460.1 | 493.7 | 457.3 | 436.4 | 397.1 | 387.7 | 390.2 | 378.3 | 323.5
1546 | 1406 | 526.2 | 460.2 | 493.7 | 457.4 | 436.4 | 397.3 | 387.9 | 390.4 | 378.4 | 323.7
1547 | 1407 | 526.2 | 460.2 | 493.7 | 457.4 | 436.4 | 397.5 | 388.1 | 390.6 | 378.6 | 323.9
1548 | 1408 | 526.2 | 460.3 | 493.7 | 457.5 | 436.5 | 397.7 | 388.3 | 390.8 | 378.7 | 324.1
1549 | 1409 | 526.2 | 460.3 | 493.7 | 457.5 | 436.6 | 397.9 | 388.5 | 390.9 | 378.8 | 324.4
1550 | 1410 | 526.2 | 460.4 | 493.7 | 457.5 | 436.6 | 398.1 | 388.7 | 391.1 | 378.8 | 324.6
1551 | 1411 | 526.2 | 460.4 | 493.8 | 457.6 | 436.7 | 398.3 | 388.9 | 391.3 | 378.9 | 324.9
1552 | 1412 | 526.2 | 460.5 | 493.8 | 457.6 | 436.7 | 398.5 | 389.1 | 391.5 | 378.9 | 325.1
1553 | 1413 | 526.2 | 460.5 | 493.7 | 457.7 | 436.8 | 398.7 | 389.3 | 391.3 | 379 | 325.3
1554 | 1414 | 526.1 | 460.6 | 493.8 | 457.7 | 436.8 | 398.9 | 389.5 | 391.5 | 379.1 | 325.5
1555 | 1415 | 526.1 | 460.6 | 493.8 | 457.8 | 436.9 | 399.1 | 389.7 | 391.7 | 379.3 | 325.7
1556 | 1416 | 526 | 461.2 | 492.8 | 458.2 | 437.7 | 399.7 | 389.8 | 391.8 | 379.4 | 327.5
1557 | 1417 | 526.1 | 460.7 | 493.8 | 457.9 | 437 | 399.6 | 390.1 | 392.2 | 380 | 326.3
1558 | 1418 | 526.1 | 460.7 | 493.9 | 457.9 | 437 | 399.8 | 390.3 | 392.4 | 380.3 | 326.4
1559 | 1419 | 526.1 | 460.8 | 493.9 | 457.9 | 437.1 | 400 | 390.5 | 392.6 | 380.6 | 326.7
1560 | 1420 | 526.1 | 460.8 | 493.9 | 458 | 437.1 | 400.2 | 390.7 | 392.7 | 380.9 | 327
1561 | 1421 | 526.1 | 460.9 | 493.9 | 458 | 437.2 | 400.4 | 390.9 | 392.9 | 381 | 327.2
1562 | 1422 | 526.1 | 460.9 | 493.9 | 458.1 | 437.3 | 400.6 | 391.1 | 393.1 | 381 | 327.5
1563 | 1423 | 526.1 | 461 | 494 | 458.1 | 437.4 | 400.8 | 391.3 | 393.2 | 381 | 327.7
1564 | 1424 | 526.1 | 461 | 494 | 458.2 | 437.5 | 401 | 391.5 | 393.4 | 381.1 | 328
1565 | 1425 | 526.2 | 461.1 | 494 | 458.2 | 437.6 | 401.2 | 391.7 | 393.5 | 381.1 | 328.2
1566 | 1426 | 526.2 | 461.1 | 494.1 | 458.2 | 437.7 | 401.4 | 391.9 | 393.7 | 381.1 | 328.5
1567 | 1427 | 526.2 | 461.2 | 494.1 | 458.3 | 437.8 | 401.7 | 392.1 | 393.8 | 381.2 | 328.7
1568 | 1428 | 526.1 | 461.2 | 494.1 | 458.3 | 437.9 | 401.9 | 392.3 | 394 | 381.3 | 329
1569 | 1429 | 526.1 | 461.3 | 494.1 | 458.4 | 438 | 402.1 | 392.5 | 394.2 | 381.5 | 329.1
1570 | 1430 | 526.1 | 461.3 | 494.2 | 458.4 | 438 | 402.3 | 392.7 | 394.4 | 381.8 | 329.3
1571 | 1431 | 526.1 | 461.4 | 494.2 | 458.5 | 438.1 | 402.6 | 392.9 | 394.5 | 382.1 | 329.5
1572 | 1432 | 526.1 | 461.4 | 494.3 | 458.5 | 438.2 | 402.8 | 393.1 | 394.7 | 382.4 | 329.7
1573 | 1433 | 526.1 | 461.5 | 494.3 | 458.6 | 438.2 | 402.9 | 393.3 | 395 | 382.5 | 329.9
1574 | 1434 | 526 | 461.5 | 494.3 | 458.6 | 438.3 | 403 | 393.5 | 395.1 | 382.7 | 330.1
1575 | 1435 | 526 | 461.6 | 494.3 | 458.6 | 438.3 | 403.1 | 393.7 | 395.2 | 382.8 | 330.4
1576 | 1436 | 525.9 | 461.6 | 494.3 | 458.7 | 438.3 | 403.2 | 393.9 | 395.4 | 382.8 | 330.6
1577 | 1437 | 525.9 | 461.6 | 494.3 | 458.7 | 438.4 | 403.3 | 394.1 | 395.5 | 382.9 | 330.9
1578 | 1438 | 525.9 | 461.7 | 494.4 | 458.7 | 438.5 | 403.4 | 394.3 | 395.6 | 383 | 331.2
1579 | 1439 | 525.9 | 461.7 | 494.4 | 458.8 | 438.5 | 403.6 | 394.5 | 395.8 | 383.2 | 331.5
1580 | 1440 | 525.9 | 461.8 | 494.4 | 458.8 | 438.6 | 403.7 | 394.7 | 396 | 383.3 | 331.7
1581 | 1441 | 525.9 | 461.8 | 494.5 | 458.9 | 438.7 | 403.9 | 394.9 | 396.1 | 383.5 | 331.9
1582 | 1442 | 525.9 | 461.9 | 494.5 | 458.9 | 438.9 | 404 | 395.1 | 396.3 | 383.8 | 332.1
1583 | 1443 | 525.9 | 461.9 | 494.5 | 459 | 439 | 404.2 | 395.3 | 396.4 | 384.1 | 332.3
1584 | 1444 | 525.9 | 462 | 494.5 | 459 | 439.1 | 404.4 | 395.5 | 396.6 | 384.5 | 332.5
1585 | 1445 | 526 | 462 | 494.5 | 459 | 439.3 | 404.6 | 395.7 | 396.8 | 384.7 | 332.7
1586 | 1446 | 525.9 | 462 | 494.6 | 459.1 | 439.4 | 404.8 | 395.9 | 396.9 | 385 | 332.9
1587 | 1447 | 525.9 | 462.1 | 494.6 | 459.2 | 439.5 | 405 | 396.1 | 397.1 | 385.2 | 333.1
1588 | 1448 | 525.8 | 462.2 | 494.6 | 459.2 | 439.7 | 405.2 | 396.3 | 397.3 | 385.3 | 333.4
1589 | 1449 | 525.8 | 462.2 | 494.6 | 459.2 | 439.8 | 405.4 | 396.5 | 397.4 | 385.5 | 333.6
1590 | 1450 | 525.8 | 462.2 | 494.6 | 459.3 | 439.9 | 405.5 | 396.7 | 397.7 | 385.5 | 333.8
1591 | 1451 | 525.8 | 462.3 | 494.6 | 459.3 | 440 | 405.7 | 396.9 | 397.9 | 385.5 | 334
1592 | 1452 | 525.7 | 462.3 | 494.7 | 459.3 | 440.2 | 405.9 | 397.1 | 398 | 385.6 | 334.3
1593 | 1453 | 525.7 | 462.4 | 494.7 | 459.4 | 440.3 | 406.1 | 397.3 | 398.2 | 385.7 | 334.4
1594 | 1454 | 525.7 | 462.4 | 494.7 | 459.4 | 440.4 | 406.3 | 397.5 | 398.3 | 385.9 | 334.7
1595 | 1455 | 525.8 | 462.4 | 494.8 | 459.5 | 440.6 | 406.5 | 397.7 | 398.4 | 386.1 | 334.9
1596 | 1456 | 525.7 | 462.5 | 494.7 | 459.5 | 440.7 | 406.7 | 397.9 | 398.5 | 386.3 | 335.2
1597 | 1457 | 525.8 | 462.5 | 494.8 | 459.5 | 440.8 | 406.9 | 398.1 | 398.7 | 386.4 | 335.4
1598 | 1458 | 525.7 | 462.6 | 494.8 | 459.6 | 440.9 | 407.1 | 398.3 | 398.8 | 386.6 | 335.6
1599 | 1459 | 525.7 | 462.6 | 494.8 | 459.6 | 441.1 | 407.3 | 398.5 | 399 | 386.7 | 335.8
1600 | 1460 | 525.8 | 462.7 | 494.8 | 459.7 | 441.2 | 407.5 | 398.7 | 399.1 | 386.9 | 335.9
1601 | 1461 | 525.8 | 462.7 | 494.8 | 459.7 | 441.3 | 407.7 | 398.9 | 399.3 | 387 | 336.1
1602 | 1462 | 525.8 | 462.7 | 494.9 | 459.8 | 441.4 | 407.9 | 399.1 | 399.4 | 387.2 | 336.3
1603 | 1463 | 525.8 | 462.8 | 494.9 | 459.8 | 441.5 | 408.1 | 399.3 | 399.5 | 387.5 | 336.5
1604 | 1464 | 525.9 | 462.8 | 495 | 459.9 | 441.6 | 408.2 | 399.6 | 399.6 | 387.7 | 336.8
1605 | 1465 | 525.9 | 462.8 | 495 | 459.9 | 441.7 | 408.4 | 399.8 | 399.8 | 388 | 337
1606 | 1466 | 525.9 | 462.9 | 495 | 459.9 | 441.8 | 408.6 | 400 | 399.9 | 388.2 | 337.2
1607 | 1467 | 525.9 | 462.9 | 495 | 460 | 441.9 | 408.8 | 400.2 | 400.1 | 388.3 | 337.4
1608 | 1468 | 525.9 | 463 | 495 | 460 | 442 | 409 | 400.4 | 400.2 | 388.4 | 337.6
1609 | 1469 | 525.9 | 463 | 495 | 460.1 | 442.1 | 409.2 | 400.6 | 400.3 | 388.4 | 337.9
1610 | 1470 | 526 | 463 | 495.1 | 460.1 | 442.1 | 409.4 | 400.8 | 400.4 | 388.4 | 338.1
1611 | 1471 | 526 | 463.1 | 495.1 | 460.2 | 442.2 | 409.6 | 401 | 400.5 | 388.4 | 338.4
1612 | 1472 | 526 | 463.1 | 495.1 | 460.2 | 442.3 | 409.8 | 401.2 | 400.6 | 388.5 | 338.6
1613 | 1473 | 526 | 463.2 | 495.2 | 460.2 | 442.3 | 410 | 401.4 | 400.7 | 388.6 | 338.9
1614 | 1474 | 526 | 463.2 | 495.2 | 460.3 | 442.3 | 410.2 | 401.6 | 400.9 | 388.7 | 339.1
1615 | 1475 | 526 | 463.2 | 495.2 | 460.3 | 442.4 | 410.4 | 401.8 | 401 | 388.8 | 339.3
1616 | 1476 | 526.1 | 463.3 | 495.2 | 460.4 | 442.5 | 410.6 | 402 | 401.1 | 388.8 | 339.6
1617 | 1477 | 526.1 | 463.3 | 495.3 | 460.4 | 442.5 | 410.8 | 402.2 | 401.2 | 388.9 | 339.8
1618 | 1478 | 526.1 | 463.3 | 495.3 | 460.4 | 442.6 | 411 | 402.5 | 401.3 | 389.1 | 340
1619 | 1479 | 526.1 | 463.4 | 495.3 | 460.5 | 442.6 | 411.2 | 402.7 | 401.4 | 389.3 | 340.2
1620 | 1480 | 526.1 | 463.4 | 495.4 | 460.5 | 442.7 | 411.4 | 402.9 | 401.6 | 389.4 | 340.4
1621 | 1481 | 526.1 | 463.4 | 495.4 | 460.5 | 442.7 | 411.6 | 403.1 | 401.7 | 389.6 | 340.6
1622 | 1482 | 526.1 | 463.5 | 495.4 | 460.6 | 442.8 | 411.8 | 403.3 | 401.9 | 389.7 | 340.8
1623 | 1483 | 526.1 | 463.6 | 495.4 | 460.6 | 442.9 | 412 | 403.5 | 402 | 389.8 | 341
1624 | 1484 | 526.1 | 463.6 | 495.4 | 460.7 | 442.9 | 412.2 | 403.7 | 402.3 | 390 | 341.2
1625 | 1485 | 526.1 | 463.6 | 495.4 | 460.7 | 443 | 412.5 | 403.9 | 402.4 | 390 | 341.5
1626 | 1486 | 526.1 | 463.7 | 495.5 | 460.8 | 443.1 | 412.7 | 404.1 | 402.6 | 390.3 | 341.7
1627 | 1487 | 526.1 | 463.7 | 495.5 | 460.8 | 443.1 | 412.9 | 404.3 | 402.7 | 390.6 | 341.9
1628 | 1488 | 526.1 | 463.7 | 495.6 | 460.9 | 443.2 | 413.1 | 404.5 | 402.8 | 390.9 | 342.1
1629 | 1489 | 526.1 | 463.8 | 495.5 | 460.9 | 443.3 | 413.3 | 404.7 | 402.9 | 391.2 | 342.4
1630 | 1490 | 526.1 | 463.8 | 495.5 | 460.9 | 443.4 | 413.5 | 404.9 | 403.1 | 391.3 | 342.5
1631 | 1491 | 526.1 | 463.9 | 495.6 | 461 | 443.4 | 413.7 | 405.1 | 403.2 | 391.4 | 342.8
1632 | 1492 | 526.1 | 463.9 | 495.6 | 461 | 443.4 | 414 | 405.3 | 403.3 | 391.4 | 343
1633 | 1493 | 526.1 | 463.9 | 495.7 | 461 | 443.5 | 414.2 | 405.5 | 403.5 | 391.4 | 343.2
1634 | 1494 | 526.1 | 464 | 495.7 | 461.1 | 443.6 | 414.4 | 405.7 | 403.6 | 391.4 | 343.5
1635 | 1495 | 526.1 | 464 | 495.7 | 461.1 | 443.6 | 414.6 | 405.9 | 403.7 | 391.5 | 343.7
1636 | 1496 | 526.1 | 464.1 | 495.7 | 461.2 | 443.7 | 414.8 | 406.1 | 403.9 | 391.6 | 343.9
1637 | 1497 | 526.1 | 464.1 | 495.7 | 461.2 | 443.7 | 415.1 | 406.3 | 404.1 | 391.6 | 344.1
1638 | 1498 | 526.1 | 464.2 | 495.7 | 461.3 | 443.7 | 415.3 | 406.5 | 404.3 | 391.7 | 344.3
1639 | 1499 | 526.1 | 464.2 | 495.8 | 461.3 | 443.8 | 415.5 | 406.7 | 404.4 | 391.9 | 344.5
1640 | 1500 | 526.1 | 464.2 | 495.8 | 461.3 | 443.8 | 415.7 | 406.9 | 404.5 | 392.1 | 344.7
1641 | 1501 | 526 | 464.3 | 495.8 | 461.4 | 443.9 | 416 | 407.2 | 404.6 | 392.4 | 344.9
1642 | 1502 | 526.1 | 464.3 | 495.8 | 461.4 | 444 | 416.2 | 407.4 | 404.7 | 392.6 | 345.1
1643 | 1503 | 526.1 | 464.3 | 495.9 | 461.4 | 444.1 | 416.4 | 407.6 | 404.8 | 392.8 | 345.3
1644 | 1504 | 526.1 | 464.4 | 495.9 | 461.5 | 444.3 | 416.6 | 407.8 | 405 | 392.9 | 345.5
1645 | 1505 | 526 | 464.4 | 495.9 | 461.5 | 444.4 | 416.9 | 408 | 405.1 | 393.1 | 345.8
1646 | 1506 | 526 | 464.5 | 495.9 | 461.6 | 444.4 | 417.1 | 408.2 | 405.3 | 393.1 | 345.9
1647 | 1507 | 526 | 464.5 | 496 | 461.6 | 444.5 | 417.3 | 408.4 | 405.4 | 393.1 | 346.2
1648 | 1508 | 526 | 464.6 | 496 | 461.6 | 444.6 | 417.6 | 408.6 | 405.5 | 393.1 | 346.3
1649 | 1509 | 526 | 464.6 | 495.9 | 461.7 | 444.7 | 417.8 | 408.9 | 405.7 | 393 | 346.5
1650 | 1510 | 525.9 | 464.7 | 495.8 | 461.8 | 444.9 | 418.1 | 409 | 405.8 | 392.9 | 347
1651 | 1511 | 525.9 | 464.7 | 495.9 | 461.8 | 444.9 | 418.3 | 409.3 | 405.9 | 392.9 | 347
1652 | 1512 | 525.9 | 464.7 | 496 | 461.8 | 444.9 | 418.5 | 409.5 | 406 | 393 | 347.1
1653 | 1513 | 525.9 | 464.7 | 496 | 461.8 | 445 | 418.8 | 409.7 | 406.1 | 393.1 | 347.3
1654 | 1514 | 525.9 | 464.8 | 496.1 | 461.9 | 445 | 419 | 410 | 406.2 | 393.3 | 347.5
1655 | 1515 | 525.9 | 464.8 | 496.1 | 461.9 | 445 | 419.2 | 410.2 | 406.2 | 393.4 | 347.6
1656 | 1516 | 525.9 | 464.9 | 496.1 | 461.9 | 445.1 | 419.5 | 410.4 | 406.3 | 393.5 | 347.9
1657 | 1517 | 526 | 464.9 | 496.2 | 461.9 | 445.2 | 419.7 | 410.6 | 406.5 | 393.7 | 348.1
1658 | 1518 | 526 | 464.9 | 496.2 | 462 | 445.2 | 419.9 | 410.9 | 406.6 | 393.9 | 348.2
1659 | 1519 | 526.1 | 464.9 | 496.2 | 462 | 445.2 | 420.2 | 411.1 | 406.7 | 394.1 | 348.4
1660 | 1520 | 526 | 465 | 496.2 | 462 | 445.3 | 420.4 | 411.3 | 406.7 | 394.3 | 348.6
1661 | 1521 | 526.1 | 465.1 | 496.1 | 462.1 | 445.4 | 420.8 | 411.5 | 406.8 | 394.5 | 349
1662 | 1522 | 526.1 | 465.2 | 496.1 | 462.2 | 445.6 | 421 | 411.8 | 406.9 | 394.7 | 349.3
1663 | 1523 | 526.2 | 465.1 | 496.3 | 462.2 | 445.5 | 421.2 | 412 | 407 | 394.9 | 349.3
1664 | 1524 | 526.2 | 465.2 | 496.3 | 462.2 | 445.6 | 421.5 | 412.2 | 407 | 394.9 | 349.4
1665 | 1525 | 526.2 | 465.2 | 496.4 | 462.2 | 445.6 | 421.7 | 412.5 | 407.1 | 394.9 | 349.5
1666 | 1526 | 526.2 | 465.2 | 496.4 | 462.3 | 445.6 | 422 | 412.7 | 407.3 | 395 | 349.6
1667 | 1527 | 526.2 | 465.3 | 496.4 | 462.3 | 445.7 | 422.2 | 413 | 407.4 | 395.1 | 349.8
1668 | 1528 | 526.2 | 465.3 | 496.4 | 462.3 | 445.7 | 422.5 | 413.2 | 407.5 | 395.2 | 350
1669 | 1529 | 526.3 | 465.3 | 496.4 | 462.4 | 445.8 | 422.8 | 413.4 | 407.6 | 395.3 | 350.3
1670 | 1530 | 526.2 | 465.5 | 496.2 | 462.5 | 446 | 423.1 | 413.6 | 407.6 | 395.4 | 350.7
1671 | 1531 | 526.2 | 465.4 | 496.4 | 462.5 | 445.9 | 423.3 | 413.9 | 407.7 | 395.5 | 350.7
1672 | 1532 | 526.2 | 465.5 | 496.5 | 462.5 | 445.9 | 423.5 | 414.1 | 407.8 | 395.6 | 350.8
1673 | 1533 | 526.2 | 465.5 | 496.5 | 462.5 | 446 | 423.8 | 414.3 | 407.9 | 395.7 | 350.9
1674 | 1534 | 526.2 | 465.5 | 496.5 | 462.5 | 446.1 | 424.1 | 414.6 | 408 | 395.9 | 351
1675 | 1535 | 526.2 | 465.6 | 496.5 | 462.6 | 446.1 | 424.3 | 414.8 | 408.1 | 396.1 | 351.3
1676 | 1536 | 526.2 | 465.6 | 496.5 | 462.6 | 446.2 | 424.6 | 415 | 408.2 | 396.3 | 351.4
1677 | 1537 | 526.2 | 465.6 | 496.5 | 462.7 | 446.2 | 424.9 | 415.2 | 408.2 | 396.7 | 351.5
1678 | 1538 | 526.2 | 465.7 | 496.4 | 462.7 | 446.3 | 425.2 | 415.5 | 408.4 | 396.9 | 351.9
1679 | 1539 | 526.2 | 465.7 | 496.5 | 462.7 | 446.3 | 425.4 | 415.7 | 408.5 | 397.1 | 351.9
1680 | 1540 | 526.2 | 465.7 | 496.6 | 462.7 | 446.3 | 425.6 | 415.9 | 408.6 | 397.3 | 352
1681 | 1541 | 526.1 | 465.8 | 496.5 | 462.8 | 446.5 | 425.9 | 416.1 | 408.7 | 397.5 | 352.3
1682 | 1542 | 525.6 | 469.3 | 489.2 | 465.8 | 452.2 | 428.6 | 415.8 | 408.1 | 396.9 | 361.4
1683 | 1543 | 526 | 466.4 | 495.5 | 463.3 | 447.3 | 426.7 | 416.6 | 408.8 | 397.8 | 353.8
1684 | 1544 | 526.1 | 465.9 | 496.8 | 462.9 | 446.5 | 426.6 | 416.9 | 409 | 398.1 | 352.6
1685 | 1545 | 526 | 465.9 | 496.8 | 462.9 | 446.6 | 426.8 | 417.2 | 409.1 | 398.1 | 352.7
1686 | 1546 | 526 | 465.9 | 496.8 | 462.9 | 446.8 | 427.1 | 417.4 | 409.2 | 398.2 | 352.9
1687 | 1547 | 526 | 466 | 496.8 | 463 | 446.9 | 427.3 | 417.7 | 409.3 | 398.3 | 353.1
1688 | 1548 | 525.9 | 466 | 496.7 | 463 | 446.9 | 427.5 | 417.9 | 409.4 | 398.4 | 353.3
1689 | 1549 | 525.9 | 466.1 | 496.7 | 463.1 | 447 | 427.8 | 418.1 | 409.5 | 398.5 | 353.5
1690 | 1550 | 525.9 | 466.1 | 496.8 | 463.1 | 447.1 | 428 | 418.3 | 409.6 | 398.6 | 353.6
1691 | 1551 | 525.9 | 466.2 | 496.8 | 463.1 | 447.1 | 428.2 | 418.5 | 409.7 | 398.8 | 353.7
1692 | 1552 | 525.8 | 466.2 | 496.8 | 463.2 | 447.2 | 428.5 | 418.7 | 409.8 | 399 | 353.9
1693 | 1553 | 525.8 | 466.3 | 496.8 | 463.2 | 447.3 | 428.7 | 419 | 409.9 | 399.3 | 354.1
1694 | 1554 | 525.8 | 466.3 | 496.8 | 463.3 | 447.4 | 428.9 | 419.2 | 410 | 399.6 | 354.2
1695 | 1555 | 525.8 | 466.3 | 496.8 | 463.3 | 447.4 | 429.1 | 419.4 | 410.1 | 399.9 | 354.3
1696 | 1556 | 525.8 | 466.4 | 496.8 | 463.3 | 447.5 | 429.3 | 419.6 | 410.1 | 400.2 | 354.4
1697 | 1557 | 525.8 | 466.4 | 496.8 | 463.4 | 447.6 | 429.5 | 419.9 | 410.2 | 400.5 | 354.5
1698 | 1558 | 525.8 | 466.4 | 496.9 | 463.4 | 447.6 | 429.7 | 420.1 | 410.4 | 400.6 | 354.5
1699 | 1559 | 525.8 | 466.5 | 496.9 | 463.4 | 447.7 | 430 | 420.4 | 410.5 | 400.7 | 354.7
1700 | 1560 | 525.9 | 466.5 | 496.9 | 463.5 | 447.8 | 430.2 | 420.6 | 410.6 | 400.8 | 354.9
1701 | 1561 | 525.9 | 466.5 | 496.9 | 463.5 | 447.8 | 430.3 | 420.8 | 410.8 | 400.8 | 355
1702 | 1562 | 525.9 | 466.6 | 497 | 463.6 | 447.9 | 430.5 | 421 | 410.9 | 400.8 | 355.1
1703 | 1563 | 525.9 | 466.6 | 497 | 463.6 | 447.9 | 430.7 | 421.2 | 411 | 400.8 | 355.3
1704 | 1564 | 525.9 | 466.7 | 496.9 | 463.7 | 448 | 430.9 | 421.3 | 411.2 | 400.9 | 355.4
1705 | 1565 | 525.9 | 466.7 | 497 | 463.7 | 447.9 | 431 | 421.5 | 411.3 | 400.9 | 355.4
1706 | 1566 | 525.9 | 466.8 | 496.9 | 463.7 | 448.1 | 431.2 | 421.7 | 411.4 | 401 | 355.7
1707 | 1567 | 525.9 | 466.8 | 497 | 463.7 | 448.1 | 431.4 | 422 | 411.5 | 401.1 | 355.8
1708 | 1568 | 525.9 | 466.8 | 497.1 | 463.7 | 448 | 431.6 | 422.2 | 411.6 | 401.2 | 355.8
1709 | 1569 | 526 | 466.8 | 497.1 | 463.8 | 448.1 | 431.8 | 422.5 | 411.8 | 401.3 | 355.9
1710 | 1570 | 526 | 466.9 | 497.1 | 463.8 | 448.2 | 432 | 422.7 | 412 | 401.5 | 356.2
1711 | 1571 | 525.9 | 466.9 | 497.1 | 463.8 | 448.2 | 432.1 | 422.9 | 412.1 | 401.5 | 356.3
1712 | 1572 | 525.9 | 466.9 | 497.1 | 463.9 | 448.2 | 432.4 | 423.2 | 412.1 | 401.5 | 356.4
1713 | 1573 | 526 | 467 | 497.1 | 463.9 | 448.3 | 432.6 | 423.4 | 412.2 | 401.6 | 356.6
1714 | 1574 | 526 | 467 | 497.1 | 464 | 448.3 | 432.8 | 423.5 | 412.3 | 401.6 | 356.8
1715 | 1575 | 525.9 | 467 | 497.1 | 464 | 448.4 | 433.1 | 423.6 | 412.5 | 401.6 | 356.9
1716 | 1576 | 525.9 | 467.1 | 497.1 | 464 | 448.4 | 433.3 | 423.7 | 412.6 | 401.6 | 357
1717 | 1577 | 526 | 467.1 | 497.1 | 464.1 | 448.5 | 433.5 | 423.8 | 412.8 | 401.6 | 357.2
1718 | 1578 | 526 | 467.1 | 497.2 | 464.1 | 448.5 | 433.8 | 423.9 | 412.9 | 401.8 | 357.4
1719 | 1579 | 526 | 467.2 | 497.2 | 464.1 | 448.5 | 434 | 424 | 413 | 401.9 | 357.5
1720 | 1580 | 526 | 467.2 | 497.2 | 464.2 | 448.5 | 434.1 | 424.1 | 413.1 | 402 | 357.6
1721 | 1581 | 526.1 | 467.2 | 497.2 | 464.2 | 448.5 | 434.3 | 424.1 | 413.3 | 402.2 | 357.8
1722 | 1582 | 526.1 | 467.3 | 497.3 | 464.2 | 448.5 | 434.5 | 424.2 | 413.4 | 402.4 | 357.8
1723 | 1583 | 526.1 | 467.3 | 497.3 | 464.3 | 448.5 | 434.6 | 424.3 | 413.6 | 402.6 | 357.9
1724 | 1584 | 526.2 | 467.3 | 497.3 | 464.3 | 448.5 | 434.8 | 424.4 | 413.7 | 402.7 | 358
1725 | 1585 | 526.2 | 467.4 | 497.3 | 464.4 | 448.6 | 434.9 | 424.6 | 413.8 | 402.9 | 358.1
1726 | 1586 | 526.3 | 467.4 | 497.4 | 464.4 | 448.5 | 435 | 424.7 | 414 | 403.1 | 358.2
1727 | 1587 | 526.3 | 467.4 | 497.4 | 464.4 | 448.5 | 435.2 | 424.8 | 414.2 | 403.3 | 358.3
1728 | 1588 | 526.3 | 467.5 | 497.4 | 464.5 | 448.6 | 435.4 | 425 | 414.3 | 403.5 | 358.4
1729 | 1589 | 526.3 | 467.5 | 497.4 | 464.5 | 448.6 | 435.5 | 425.1 | 414.5 | 403.7 | 358.5
1730 | 1590 | 526.3 | 467.5 | 497.4 | 464.5 | 448.5 | 435.6 | 425.3 | 414.7 | 403.9 | 358.6
1731 | 1591 | 526.3 | 467.6 | 497.4 | 464.6 | 448.6 | 435.8 | 425.5 | 414.8 | 404 | 358.8
1732 | 1592 | 526.3 | 467.6 | 497.5 | 464.6 | 448.6 | 436 | 425.7 | 415 | 404.2 | 358.8
1733 | 1593 | 526.3 | 467.6 | 497.5 | 464.6 | 448.6 | 436.1 | 425.8 | 415.2 | 404.3 | 358.9
1734 | 1594 | 526.3 | 467.7 | 497.5 | 464.7 | 448.6 | 436.3 | 426 | 415.3 | 404.6 | 359.1
1735 | 1595 | 526.3 | 467.7 | 497.5 | 464.7 | 448.6 | 436.4 | 426.2 | 415.5 | 404.8 | 359.2
1736 | 1596 | 526.3 | 467.8 | 497.5 | 464.7 | 448.6 | 436.5 | 426.4 | 415.7 | 404.9 | 359.3
1737 | 1597 | 526.2 | 467.8 | 497.5 | 464.8 | 448.6 | 436.6 | 426.6 | 415.9 | 405 | 359.4
1738 | 1598 | 526.2 | 467.8 | 497.5 | 464.8 | 448.7 | 436.8 | 426.8 | 416 | 405 | 359.6
1739 | 1599 | 526.2 | 467.9 | 497.6 | 464.9 | 448.7 | 436.9 | 426.9 | 416.2 | 405 | 359.7
1740 | 1600 | 526.2 | 467.9 | 497.6 | 464.9 | 448.6 | 437.1 | 427.1 | 416.4 | 405.1 | 359.8
1741 | 1601 | 526.1 | 467.9 | 497.6 | 464.9 | 448.6 | 437.3 | 427.3 | 416.6 | 405.1 | 360
1742 | 1602 | 526.1 | 468 | 497.6 | 465 | 448.6 | 437.5 | 427.5 | 416.7 | 405.1 | 360.1
1743 | 1603 | 526 | 468 | 497.6 | 465 | 448.6 | 437.7 | 427.6 | 416.9 | 405.2 | 360.2
1744 | 1604 | 526 | 468.1 | 497.6 | 465 | 448.6 | 437.9 | 427.8 | 417 | 405.2 | 360.3
1745 | 1605 | 525.9 | 468.1 | 497.6 | 465.1 | 448.6 | 438.1 | 428 | 417.2 | 405.3 | 360.5
1746 | 1606 | 525.9 | 468.1 | 497.6 | 465.1 | 448.7 | 438.3 | 428.1 | 417.3 | 405.3 | 360.7
1747 | 1607 | 525.9 | 468.2 | 497.7 | 465.1 | 448.6 | 438.5 | 428.3 | 417.5 | 405.4 | 360.7
1748 | 1608 | 525.9 | 468.2 | 497.6 | 465.2 | 448.7 | 438.7 | 428.4 | 417.7 | 405.4 | 361.1
1749 | 1609 | 525.9 | 468.2 | 497.6 | 465.2 | 448.7 | 438.9 | 428.6 | 417.9 | 405.5 | 361.2
1750 | 1610 | 525.9 | 468.3 | 497.6 | 465.2 | 448.7 | 439.1 | 428.7 | 418.1 | 405.6 | 361.3
1751 | 1611 | 525.9 | 468.3 | 497.7 | 465.3 | 448.6 | 439.1 | 428.8 | 418.4 | 405.7 | 361.4
1752 | 1612 | 525.9 | 468.3 | 497.6 | 465.3 | 448.6 | 439.1 | 429 | 418.5 | 405.8 | 361.6
1753 | 1613 | 525.8 | 468.4 | 497.6 | 465.3 | 448.7 | 439.1 | 429.1 | 418.6 | 406 | 361.7
1754 | 1614 | 525.8 | 468.4 | 497.7 | 465.4 | 448.7 | 439.2 | 429.2 | 418.7 | 406.1 | 361.6
1755 | 1615 | 525.8 | 468.5 | 497.6 | 465.4 | 448.7 | 439.3 | 429.3 | 418.8 | 406.1 | 361.7
1756 | 1616 | 525.8 | 468.5 | 497.7 | 465.5 | 448.6 | 439.4 | 429.5 | 419 | 406.2 | 361.8
1757 | 1617 | 525.9 | 468.6 | 497.6 | 465.5 | 448.6 | 439.6 | 429.6 | 419.2 | 406.3 | 362
1758 | 1618 | 525.8 | 468.6 | 497.8 | 465.5 | 448.7 | 439.6 | 429.7 | 419.4 | 406.6 | 362.1
1759 | 1619 | 525.8 | 468.6 | 497.8 | 465.5 | 448.7 | 439.6 | 429.8 | 419.6 | 406.8 | 362.3
1760 | 1620 | 525.8 | 468.6 | 497.7 | 465.6 | 448.7 | 439.8 | 430 | 419.8 | 407 | 362.5
1761 | 1621 | 525.8 | 468.7 | 497.7 | 465.6 | 448.7 | 440 | 430.1 | 419.9 | 407.2 | 362.6
1762 | 1622 | 525.8 | 468.7 | 497.8 | 465.6 | 448.7 | 440.1 | 430.2 | 420.1 | 407.4 | 362.7
1763 | 1623 | 525.8 | 468.7 | 497.7 | 465.7 | 448.8 | 440.2 | 430.3 | 420.3 | 407.6 | 363
1764 | 1624 | 525.8 | 468.8 | 497.7 | 465.7 | 448.8 | 440.2 | 430.5 | 420.5 | 407.9 | 363.1
1765 | 1625 | 525.8 | 468.8 | 497.8 | 465.7 | 448.8 | 440.2 | 430.6 | 420.7 | 408.1 | 363.2
1766 | 1626 | 525.7 | 469.1 | 497.1 | 466 | 449.3 | 440.6 | 430.7 | 420.9 | 408.2 | 364.2
1767 | 1627 | 525.7 | 468.9 | 497.7 | 465.8 | 448.9 | 440.5 | 430.9 | 421.2 | 408.4 | 363.6
1768 | 1628 | 525.7 | 468.9 | 497.8 | 465.8 | 448.8 | 440.6 | 431 | 421.5 | 408.5 | 363.7
1769 | 1629 | 525.7 | 468.9 | 497.8 | 465.8 | 448.9 | 440.6 | 431.1 | 421.7 | 408.6 | 363.8
1770 | 1630 | 525.6 | 469 | 497.7 | 465.9 | 448.9 | 440.7 | 431.3 | 421.9 | 408.7 | 364.1
1771 | 1631 | 525.6 | 469 | 497.8 | 465.9 | 448.9 | 440.8 | 431.4 | 422.1 | 408.7 | 364.2
1772 | 1632 | 525.6 | 469 | 497.8 | 466 | 448.9 | 441 | 431.5 | 422.4 | 408.8 | 364.3
1773 | 1633 | 525.6 | 469 | 497.8 | 466 | 448.9 | 441.1 | 431.6 | 422.6 | 408.9 | 364.5
1774 | 1634 | 525.6 | 469.1 | 497.8 | 466.1 | 448.9 | 441.2 | 431.7 | 422.8 | 409.1 | 364.6
1775 | 1635 | 525.6 | 469.1 | 497.9 | 466.1 | 449 | 441.3 | 431.9 | 423 | 409.3 | 364.7
1776 | 1636 | 525.6 | 469.2 | 497.9 | 466.1 | 449 | 441.3 | 432 | 423.2 | 409.5 | 364.9
1777 | 1637 | 525.6 | 469.2 | 497.9 | 466.2 | 449.1 | 441.4 | 432.1 | 423.4 | 409.6 | 365.1
1778 | 1638 | 525.7 | 469.3 | 497.9 | 466.2 | 449 | 441.6 | 432.2 | 423.7 | 409.7 | 365.2
1779 | 1639 | 525.7 | 469.3 | 498 | 466.2 | 449 | 441.7 | 432.3 | 423.9 | 409.8 | 365.2
1780 | 1640 | 525.8 | 469.3 | 497.9 | 466.3 | 449.1 | 441.8 | 432.5 | 424.1 | 409.9 | 365.4
1781 | 1641 | 525.8 | 469.4 | 498 | 466.3 | 449.1 | 441.8 | 432.6 | 424.4 | 410.1 | 365.5
1782 | 1642 | 525.8 | 469.4 | 498 | 466.4 | 449.1 | 441.9 | 432.7 | 424.6 | 410.2 | 365.6
1783 | 1643 | 525.9 | 469.4 | 498 | 466.4 | 449.1 | 442 | 432.8 | 424.8 | 410.2 | 365.8
1784 | 1644 | 525.9 | 469.5 | 498 | 466.4 | 449.2 | 442.2 | 432.9 | 425 | 410.2 | 365.9
1785 | 1645 | 525.9 | 469.5 | 498 | 466.5 | 449.2 | 442.3 | 433 | 425.2 | 410.3 | 366
1786 | 1646 | 525.9 | 469.6 | 498 | 466.5 | 449.2 | 442.5 | 433.1 | 425.4 | 410.3 | 366.2
1787 | 1647 | 525.9 | 469.6 | 498.1 | 466.5 | 449.2 | 442.6 | 433.2 | 425.6 | 410.3 | 366.4
1788 | 1648 | 525.9 | 469.6 | 498.1 | 466.6 | 449.2 | 442.7 | 433.3 | 425.8 | 410.2 | 366.7
1789 | 1649 | 525.9 | 469.7 | 498.1 | 466.6 | 449.2 | 442.8 | 433.5 | 426 | 410.3 | 366.9
1790 | 1650 | 525.9 | 469.7 | 498.1 | 466.6 | 449.2 | 442.8 | 433.5 | 426.2 | 410.3 | 367.1
1791 | 1651 | 526 | 469.7 | 498.1 | 466.7 | 449.2 | 442.8 | 433.6 | 426.4 | 410.5 | 367.3
1792 | 1652 | 526 | 469.8 | 498.1 | 466.7 | 449.2 | 442.9 | 433.7 | 426.6 | 410.6 | 367.3
1793 | 1653 | 526 | 469.8 | 498.1 | 466.7 | 449.3 | 443 | 433.8 | 426.9 | 410.6 | 367.4
1794 | 1654 | 526 | 469.9 | 498.1 | 466.8 | 449.4 | 443.1 | 433.9 | 427.1 | 410.7 | 367.6
1795 | 1655 | 526 | 469.9 | 498.1 | 466.8 | 449.4 | 443.2 | 434 | 427.3 | 410.9 | 367.5
1796 | 1656 | 526 | 469.9 | 498.2 | 466.8 | 449.4 | 443.4 | 434.1 | 427.6 | 411 | 367.6
1797 | 1657 | 526 | 470 | 498.2 | 466.9 | 449.5 | 443.5 | 434.2 | 427.8 | 411 | 367.7
1798 | 1658 | 526 | 470 | 498.1 | 467 | 449.5 | 443.6 | 434.3 | 428 | 411 | 367.9
1799 | 1659 | 526 | 470 | 498.2 | 467 | 449.5 | 443.7 | 434.4 | 428.3 | 411.1 | 368
1800 | 1660 | 526 | 470.1 | 498.2 | 467 | 449.5 | 443.8 | 434.5 | 428.6 | 411.2 | 368.2
1801 | 1661 | 526 | 470.1 | 498.2 | 467 | 449.6 | 443.9 | 434.6 | 428.7 | 411.2 | 368.4
1802 | 1662 | 526 | 470.1 | 498.2 | 467 | 449.6 | 444 | 434.7 | 428.9 | 411.3 | 368.5
1803 | 1663 | 526 | 470.2 | 498.3 | 467.1 | 449.6 | 444 | 434.8 | 429.1 | 411.5 | 368.7
1804 | 1664 | 526 | 470.2 | 498.3 | 467.1 | 449.7 | 444.1 | 434.9 | 429.3 | 411.6 | 368.8
1805 | 1665 | 526 | 470.2 | 498.3 | 467.1 | 449.7 | 444.2 | 435 | 429.4 | 411.6 | 369
1806 | 1666 | 526 | 470.3 | 498.3 | 467.1 | 449.7 | 444.3 | 435.1 | 429.6 | 411.6 | 369.1
1807 | 1667 | 526 | 470.3 | 498.3 | 467.2 | 449.8 | 444.4 | 435.2 | 429.8 | 411.7 | 369.3
1808 | 1668 | 526 | 470.4 | 498.3 | 467.2 | 449.9 | 444.6 | 435.3 | 429.9 | 411.7 | 369.5
1809 | 1669 | 526 | 470.4 | 498.3 | 467.3 | 449.9 | 444.8 | 435.4 | 430.2 | 411.7 | 369.6
1810 | 1670 | 526 | 470.4 | 498.3 | 467.3 | 449.8 | 444.8 | 435.5 | 430.4 | 411.8 | 369.7
1811 | 1671 | 526 | 470.4 | 498.4 | 467.3 | 449.9 | 444.8 | 435.6 | 430.7 | 411.8 | 369.8
1812 | 1672 | 526 | 470.5 | 498.4 | 467.3 | 450 | 445 | 435.7 | 431 | 411.9 | 370.1
1813 | 1673 | 526 | 470.5 | 498.4 | 467.4 | 449.9 | 445 | 435.7 | 431.1 | 412 | 370.2
1814 | 1674 | 526 | 470.5 | 498.4 | 467.4 | 450 | 445 | 435.8 | 431.3 | 412.2 | 370.3
1815 | 1675 | 526 | 470.6 | 498.4 | 467.4 | 450.1 | 445.1 | 435.9 | 431.7 | 412.3 | 370.5
1816 | 1676 | 526 | 470.6 | 498.4 | 467.5 | 450.2 | 445.2 | 436 | 432.1 | 412.4 | 370.6
1817 | 1677 | 526 | 470.6 | 498.5 | 467.5 | 450.2 | 445.2 | 436.1 | 432.3 | 412.5 | 370.7
1818 | 1678 | 526 | 470.7 | 498.5 | 467.5 | 450.2 | 445.4 | 436.2 | 432.6 | 412.5 | 370.9
1819 | 1679 | 526 | 470.7 | 498.4 | 467.6 | 450.3 | 445.6 | 436.3 | 432.9 | 412.6 | 371.1
1820 | 1680 | 526 | 470.7 | 498.5 | 467.6 | 450.3 | 445.7 | 436.3 | 433.3 | 412.6 | 371.4
1821 | 1681 | 526 | 470.8 | 498.4 | 467.6 | 450.4 | 445.7 | 436.4 | 433.6 | 412.7 | 371.6
1822 | 1682 | 526 | 470.8 | 498.4 | 467.6 | 450.5 | 445.8 | 436.5 | 434 | 412.7 | 371.9
1823 | 1683 | 526 | 470.8 | 498.5 | 467.7 | 450.6 | 446 | 436.7 | 434.4 | 412.8 | 372
1824 | 1684 | 526 | 470.9 | 498.5 | 467.7 | 450.6 | 446.1 | 436.8 | 434.8 | 412.9 | 372
1825 | 1685 | 526 | 470.9 | 498.5 | 467.7 | 450.7 | 446.2 | 436.9 | 434.9 | 413 | 372.2
1826 | 1686 | 526 | 470.9 | 498.5 | 467.8 | 450.8 | 446.3 | 436.9 | 435.1 | 413.2 | 372.3
1827 | 1687 | 526 | 471 | 498.5 | 467.8 | 450.9 | 446.4 | 437 | 435.2 | 413.3 | 372.4
1828 | 1688 | 526.1 | 471 | 498.5 | 467.8 | 450.8 | 446.4 | 437.1 | 435.2 | 413.5 | 372.5
1829 | 1689 | 526 | 471.1 | 498.5 | 467.9 | 451 | 446.5 | 437.2 | 435.4 | 413.7 | 372.7
1830 | 1690 | 526 | 471.1 | 498.5 | 467.9 | 451 | 446.6 | 437.3 | 435.3 | 413.8 | 372.8
1831 | 1691 | 526 | 471.1 | 498.6 | 467.9 | 451 | 446.7 | 437.3 | 435.6 | 414 | 372.9
1832 | 1692 | 526 | 471.1 | 498.6 | 467.9 | 451.1 | 446.7 | 437.4 | 436.1 | 414 | 373
1833 | 1693 | 526 | 471.2 | 498.6 | 468 | 451.2 | 446.8 | 437.4 | 436.5 | 414.1 | 373.3
1834 | 1694 | 526 | 471.2 | 498.6 | 468 | 451.2 | 446.9 | 437.5 | 436.8 | 414.2 | 373.3
1835 | 1695 | 526 | 471.2 | 498.7 | 468 | 451.2 | 446.9 | 437.6 | 437 | 414.4 | 373.4
1836 | 1696 | 525.9 | 471.3 | 498.6 | 468.1 | 451.4 | 447 | 437.7 | 437 | 414.5 | 373.6
1837 | 1697 | 525.9 | 471.3 | 498.6 | 468.1 | 451.5 | 447.1 | 437.7 | 437.2 | 414.5 | 373.7
1838 | 1698 | 525.9 | 471.3 | 498.7 | 468.1 | 451.5 | 447.1 | 437.8 | 437.5 | 414.7 | 373.7
1839 | 1699 | 525.9 | 471.4 | 498.7 | 468.2 | 451.5 | 447.2 | 438 | 437.3 | 414.8 | 373.9
1840 | 1700 | 525.9 | 471.4 | 498.7 | 468.2 | 451.6 | 447.3 | 438 | 437.4 | 414.9 | 374
1841 | 1701 | 526 | 471.4 | 498.7 | 468.2 | 451.7 | 447.3 | 438 | 437.9 | 415 | 374.2
1842 | 1702 | 526 | 471.4 | 498.7 | 468.3 | 451.8 | 447.4 | 438.1 | 438.2 | 415 | 374.3
1843 | 1703 | 526 | 471.5 | 498.7 | 468.3 | 451.9 | 447.5 | 438.2 | 438 | 415.1 | 374.4
1844 | 1704 | 526 | 471.5 | 498.7 | 468.3 | 452 | 447.6 | 438.3 | 437.7 | 415.2 | 374.6
1845 | 1705 | 525.9 | 471.6 | 498.7 | 468.4 | 452 | 447.7 | 438.3 | 437.5 | 415.3 | 374.7
1846 | 1706 | 525.9 | 471.6 | 498.8 | 468.4 | 452.1 | 447.8 | 438.3 | 438 | 415.4 | 374.9
1847 | 1707 | 525.9 | 471.6 | 498.7 | 468.4 | 452.2 | 447.8 | 438.3 | 438 | 415.4 | 375.1
1848 | 1708 | 525.9 | 471.7 | 498.8 | 468.4 | 452.2 | 447.9 | 438.4 | 438.2 | 415.4 | 375.2
1849 | 1709 | 525.9 | 471.7 | 498.9 | 468.5 | 452.2 | 448 | 438.5 | 438.8 | 415.4 | 375.3
1850 | 1710 | 525.9 | 471.7 | 498.8 | 468.5 | 452.3 | 448.1 | 438.4 | 438.8 | 415.4 | 375.6
1851 | 1711 | 526 | 471.7 | 498.9 | 468.5 | 452.4 | 448.2 | 438.5 | 439 | 415.5 | 375.8
1852 | 1712 | 526 | 471.7 | 498.9 | 468.5 | 452.4 | 448.2 | 438.5 | 439.4 | 415.5 | 375.8
1853 | 1713 | 526 | 471.8 | 498.9 | 468.6 | 452.5 | 448.3 | 438.6 | 439.4 | 415.3 | 376
1854 | 1714 | 526 | 471.8 | 498.9 | 468.6 | 452.6 | 448.4 | 438.6 | 438.8 | 415.3 | 376.2
1855 | 1715 | 526 | 471.9 | 498.9 | 468.6 | 452.6 | 448.5 | 438.7 | 438 | 415.4 | 376.3
1856 | 1716 | 526 | 471.9 | 499 | 468.7 | 452.7 | 448.5 | 438.8 | 438.2 | 415.4 | 376.5
1857 | 1717 | 525.9 | 471.9 | 498.9 | 468.7 | 452.8 | 448.6 | 438.8 | 438.7 | 415.5 | 376.7
1858 | 1718 | 525.9 | 472 | 498.9 | 468.8 | 452.8 | 448.6 | 438.8 | 439.2 | 415.5 | 376.8
1859 | 1719 | 526 | 472 | 499 | 468.8 | 452.9 | 448.7 | 438.8 | 439.5 | 415.5 | 377
1860 | 1720 | 526 | 472 | 499 | 468.8 | 452.9 | 448.8 | 438.9 | 439.7 | 415.6 | 377.1
1861 | 1721 | 526 | 472.1 | 499 | 468.8 | 453 | 448.9 | 439 | 439.2 | 415.6 | 377.3
1862 | 1722 | 526 | 472.1 | 499 | 468.9 | 453.1 | 449 | 439.2 | 439 | 415.7 | 377.4
1863 | 1723 | 526 | 472.1 | 499.1 | 468.9 | 453.1 | 449 | 439.4 | 439.3 | 415.8 | 377.5
1864 | 1724 | 526.1 | 472.2 | 499.1 | 468.9 | 453.1 | 449.1 | 439.5 | 439 | 415.8 | 377.6
1865 | 1725 | 526.1 | 472.2 | 499.1 | 469 | 453.2 | 449.2 | 439.6 | 438.5 | 415.9 | 377.8
1866 | 1726 | 526.1 | 472.2 | 499.1 | 469 | 453.2 | 449.3 | 439.7 | 438.9 | 416 | 377.8
1867 | 1727 | 526.1 | 472.3 | 499.1 | 469 | 453.3 | 449.3 | 439.9 | 439.4 | 416.1 | 378
1868 | 1728 | 526.1 | 472.3 | 499.2 | 469.1 | 453.3 | 449.4 | 440 | 439.3 | 416.2 | 378.1
1869 | 1729 | 526.1 | 472.3 | 499.2 | 469.1 | 453.3 | 449.4 | 440.2 | 438.7 | 416.2 | 378.2
1870 | 1730 | 526.2 | 472.3 | 499.2 | 469.1 | 453.3 | 449.5 | 440.3 | 439.2 | 416.3 | 378.3
1871 | 1731 | 526.1 | 472.4 | 499.3 | 469.2 | 453.4 | 449.6 | 440.3 | 439.5 | 416.3 | 378.5
1872 | 1732 | 526.1 | 472.4 | 499.3 | 469.2 | 453.5 | 449.7 | 440.4 | 439.2 | 416.3 | 378.7
1873 | 1733 | 526.1 | 472.4 | 499.3 | 469.2 | 453.5 | 449.7 | 440.5 | 439.3 | 416.4 | 378.8
1874 | 1734 | 526.1 | 472.5 | 499.3 | 469.2 | 453.6 | 449.7 | 440.6 | 439 | 416.4 | 379
1875 | 1735 | 526.1 | 472.5 | 499.3 | 469.3 | 453.6 | 449.8 | 440.7 | 439.3 | 416.4 | 379.2
1876 | 1736 | 526.1 | 472.5 | 499.3 | 469.3 | 453.6 | 449.9 | 440.8 | 439.2 | 416.5 | 379.2
1877 | 1737 | 526.1 | 472.6 | 499.3 | 469.3 | 453.7 | 449.9 | 440.9 | 439.8 | 416.6 | 379.3
1878 | 1738 | 526.1 | 472.6 | 499.3 | 469.4 | 453.8 | 450 | 441 | 440.4 | 416.6 | 379.6
1879 | 1739 | 526.1 | 472.7 | 499.3 | 469.4 | 453.9 | 450.1 | 441 | 440.9 | 416.7 | 379.7
1880 | 1740 | 526.1 | 472.7 | 499.4 | 469.4 | 453.9 | 450.1 | 441 | 441.2 | 416.8 | 379.8
1881 | 1741 | 526.1 | 472.7 | 499.4 | 469.5 | 454 | 450.2 | 441.1 | 441.5 | 416.8 | 380
1882 | 1742 | 526.1 | 472.8 | 499.4 | 469.5 | 454 | 450.2 | 441.1 | 441.7 | 416.8 | 380.1
1883 | 1743 | 526.1 | 472.8 | 499.4 | 469.5 | 454 | 450.3 | 441.1 | 441.8 | 416.9 | 380.3
1884 | 1744 | 526 | 472.8 | 499.5 | 469.5 | 454 | 450.4 | 441.1 | 442 | 416.9 | 380.3
1885 | 1745 | 526 | 472.8 | 499.5 | 469.5 | 454.1 | 450.5 | 441.1 | 442.2 | 416.9 | 380.5
1886 | 1746 | 526 | 472.9 | 499.5 | 469.6 | 454.2 | 450.5 | 441.2 | 442.3 | 417 | 380.7
1887 | 1747 | 525.9 | 472.9 | 499.5 | 469.6 | 454.2 | 450.5 | 441.3 | 442.4 | 417 | 380.8
1888 | 1748 | 525.9 | 472.9 | 499.5 | 469.6 | 454.3 | 450.6 | 441.5 | 442 | 417.1 | 381
1889 | 1749 | 525.9 | 473 | 499.5 | 469.7 | 454.3 | 450.7 | 441.5 | 442.2 | 417.1 | 381.2
1890 | 1750 | 525.8 | 473 | 499.5 | 469.7 | 454.4 | 450.7 | 441.6 | 442.2 | 417.1 | 381.3
1891 | 1751 | 525.8 | 473 | 499.5 | 469.7 | 454.3 | 450.7 | 441.7 | 442.5 | 417.2 | 381.4
1892 | 1752 | 525.8 | 473 | 499.5 | 469.7 | 454.5 | 450.8 | 441.8 | 442.8 | 417.2 | 381.6
1893 | 1753 | 525.8 | 473.1 | 499.5 | 469.7 | 454.5 | 450.8 | 441.9 | 443 | 417.2 | 381.8
1894 | 1754 | 525.8 | 473.1 | 499.7 | 469.7 | 454.5 | 450.9 | 441.9 | 443.1 | 417.3 | 381.8
1895 | 1755 | 525.8 | 473.1 | 499.6 | 469.8 | 454.6 | 450.9 | 441.9 | 443.2 | 417.3 | 382
1896 | 1756 | 525.8 | 473.2 | 499.6 | 469.8 | 454.6 | 451 | 441.9 | 443.1 | 417.4 | 382.2
1897 | 1757 | 525.8 | 473.2 | 499.6 | 469.8 | 454.6 | 451 | 441.9 | 443.2 | 417.4 | 382.4
1898 | 1758 | 525.8 | 473.2 | 499.6 | 469.9 | 454.6 | 451 | 442 | 443.3 | 417.5 | 382.4
1899 | 1759 | 525.8 | 473.3 | 499.6 | 469.9 | 454.7 | 451.1 | 442.1 | 443.5 | 417.5 | 382.6
1900 | 1760 | 525.8 | 473.3 | 499.6 | 469.9 | 454.8 | 451.2 | 442.1 | 443.5 | 417.6 | 382.8
1901 | 1761 | 525.8 | 473.3 | 499.7 | 469.9 | 454.8 | 451.2 | 442.1 | 443.6 | 417.7 | 382.9
1902 | 1762 | 525.8 | 473.4 | 499.7 | 470 | 454.7 | 451.2 | 442.1 | 443.7 | 417.7 | 383.1
1903 | 1763 | 525.8 | 473.4 | 499.7 | 470 | 454.9 | 451.3 | 442.1 | 443.8 | 417.8 | 383.2
1904 | 1764 | 525.9 | 473.4 | 499.7 | 470 | 455 | 451.3 | 442.1 | 443.9 | 417.9 | 383.4
1905 | 1765 | 525.9 | 473.4 | 499.7 | 470.1 | 455 | 451.4 | 442.1 | 443.9 | 418 | 383.5
1906 | 1766 | 525.9 | 473.5 | 499.7 | 470.1 | 455.1 | 451.4 | 442.1 | 444.1 | 418 | 383.6
1907 | 1767 | 525.9 | 473.5 | 499.7 | 470.1 | 455.1 | 451.5 | 442.2 | 444.3 | 418.1 | 383.8
1908 | 1768 | 525.9 | 473.5 | 499.8 | 470.1 | 455.1 | 451.5 | 442.2 | 444.4 | 418.1 | 383.8
1909 | 1769 | 525.9 | 473.5 | 499.8 | 470.1 | 455.2 | 451.6 | 442.2 | 444.3 | 418.3 | 384
1910 | 1770 | 525.9 | 473.6 | 499.8 | 470.2 | 455.3 | 451.6 | 442.2 | 444.3 | 418.4 | 384.1
1911 | 1771 | 525.9 | 473.6 | 499.8 | 470.2 | 455.3 | 451.7 | 442.2 | 444.3 | 418.5 | 384.2
1912 | 1772 | 525.9 | 473.6 | 499.9 | 470.2 | 455.3 | 451.7 | 442.2 | 444.5 | 418.6 | 384.4
1913 | 1773 | 525.9 | 473.7 | 499.8 | 470.3 | 455.4 | 451.8 | 442.2 | 444.6 | 418.7 | 384.5
1914 | 1774 | 525.9 | 473.7 | 499.8 | 470.3 | 455.5 | 451.9 | 442.2 | 444.8 | 418.9 | 384.7
1915 | 1775 | 525.9 | 473.7 | 499.9 | 470.3 | 455.4 | 451.9 | 442.2 | 444.9 | 419 | 384.7
1916 | 1776 | 525.9 | 473.7 | 499.9 | 470.3 | 455.5 | 451.9 | 442.2 | 445 | 419.2 | 384.8
1917 | 1777 | 525.9 | 473.8 | 499.9 | 470.4 | 455.6 | 452 | 442.2 | 445 | 419.3 | 385
1918 | 1778 | 525.9 | 473.8 | 499.9 | 470.4 | 455.6 | 452 | 442.2 | 445.1 | 419.5 | 385.1
1919 | 1779 | 525.9 | 473.8 | 499.9 | 470.4 | 455.7 | 452.1 | 442.2 | 445.2 | 419.6 | 385.2
1920 | 1780 | 525.9 | 473.9 | 499.9 | 470.5 | 455.8 | 452.2 | 442.2 | 445.3 | 419.6 | 385.4
1921 | 1781 | 525.9 | 473.9 | 499.9 | 470.5 | 455.8 | 452.2 | 442.2 | 445.4 | 419.7 | 385.6
1922 | 1782 | 525.9 | 473.9 | 499.9 | 470.5 | 455.8 | 452.2 | 442.3 | 445.6 | 419.8 | 385.6
1923 | 1783 | 525.9 | 474 | 499.9 | 470.5 | 455.8 | 452.3 | 442.3 | 445.7 | 419.9 | 385.8
1924 | 1784 | 525.9 | 474 | 499.9 | 470.5 | 455.9 | 452.4 | 442.3 | 445.8 | 420.1 | 386
1925 | 1785 | 525.9 | 474 | 499.9 | 470.6 | 456 | 452.4 | 442.3 | 445.7 | 420.3 | 386.2
1926 | 1786 | 525.9 | 474 | 500 | 470.6 | 456 | 452.5 | 442.3 | 445.8 | 420.4 | 386.3
1927 | 1787 | 525.9 | 474.1 | 500 | 470.6 | 456 | 452.5 | 442.3 | 445.9 | 420.4 | 386.4
1928 | 1788 | 525.9 | 474.1 | 500 | 470.6 | 456.1 | 452.6 | 442.3 | 445.9 | 420.5 | 386.6
1929 | 1789 | 525.9 | 474.1 | 500 | 470.7 | 456.1 | 452.6 | 442.4 | 445.8 | 420.5 | 386.7
1930 | 1790 | 525.9 | 474.1 | 500 | 470.7 | 456.2 | 452.7 | 442.4 | 445.8 | 420.6 | 386.8
1931 | 1791 | 525.8 | 474.2 | 500 | 470.7 | 456.3 | 452.8 | 442.4 | 445.9 | 420.6 | 387
1932 | 1792 | 525.8 | 474.2 | 500 | 470.7 | 456.3 | 452.8 | 442.4 | 446 | 420.7 | 387.1
1933 | 1793 | 525.8 | 474.2 | 500.1 | 470.7 | 456.2 | 452.8 | 442.4 | 446.1 | 420.8 | 387.1
1934 | 1794 | 525.8 | 474.2 | 500.1 | 470.8 | 456.3 | 452.9 | 442.4 | 446.2 | 420.9 | 387.3
1935 | 1795 | 525.8 | 474.3 | 500.1 | 470.8 | 456.4 | 452.9 | 442.5 | 446.3 | 421 | 387.5
1936 | 1796 | 525.8 | 474.3 | 500 | 470.8 | 456.4 | 453 | 442.5 | 446.4 | 421.2 | 387.5
1937 | 1797 | 525.8 | 474.3 | 500 | 470.8 | 456.4 | 453 | 442.5 | 446.4 | 421.3 | 387.6
1938 | 1798 | 525.8 | 474.4 | 500 | 470.9 | 456.5 | 453.1 | 442.5 | 446.4 | 421.3 | 387.8
1939 | 1799 | 525.8 | 474.4 | 500 | 470.9 | 456.6 | 453.2 | 442.6 | 446.4 | 421.4 | 387.9
1940 | 1800 | 525.8 | 474.4 | 500.1 | 470.9 | 456.6 | 453.2 | 442.6 | 446.5 | 421.5 | 387.9
1941 | 1801 | 525.8 | 474.4 | 500 | 470.9 | 456.7 | 453.3 | 442.6 | 446.7 | 421.5 | 388.1
1942 | 1802 | 525.8 | 474.4 | 500.1 | 470.9 | 456.7 | 453.3 | 442.6 | 446.8 | 421.6 | 388.2
1943 | 1803 | 525.9 | 474.4 | 500.1 | 471 | 456.7 | 453.3 | 442.7 | 446.9 | 421.7 | 388.3
1944 | 1804 | 525.9 | 474.5 | 500.1 | 471 | 456.8 | 453.4 | 442.7 | 447 | 421.7 | 388.4
1945 | 1805 | 525.9 | 474.5 | 500.1 | 471 | 456.9 | 453.5 | 442.7 | 447.1 | 421.8 | 388.6
1946 | 1806 | 525.9 | 474.5 | 500.1 | 471 | 456.9 | 453.5 | 442.8 | 447.1 | 421.8 | 388.7
1947 | 1807 | 525.8 | 474.5 | 500.2 | 471.1 | 456.9 | 453.5 | 442.8 | 447 | 421.9 | 388.8
1948 | 1808 | 525.8 | 474.5 | 500.2 | 471.1 | 457 | 453.6 | 442.8 | 447 | 421.9 | 389
1949 | 1809 | 525.8 | 474.6 | 500.1 | 471.1 | 457.1 | 453.7 | 442.9 | 447 | 422 | 389.2
1950 | 1810 | 525.8 | 474.6 | 500.2 | 471.1 | 457.1 | 453.7 | 442.9 | 447 | 422.2 | 389.2
1951 | 1811 | 525.8 | 474.6 | 500.2 | 471.2 | 457.1 | 453.8 | 442.9 | 447.1 | 422.2 | 389.3
1952 | 1812 | 525.8 | 474.7 | 500.2 | 471.2 | 457.4 | 453.8 | 443 | 447.2 | 422.3 | 389.4
1953 | 1813 | 525.8 | 474.7 | 500.2 | 471.2 | 457.3 | 453.9 | 443 | 447.3 | 422.4 | 389.4
1954 | 1814 | 525.8 | 474.7 | 500.1 | 471.3 | 457.2 | 453.9 | 443.1 | 447.3 | 422.4 | 389.5
1955 | 1815 | 525.8 | 474.7 | 500.2 | 471.3 | 457.3 | 454 | 443.1 | 447.4 | 422.5 | 389.6
1956 | 1816 | 525.8 | 474.8 | 500.2 | 471.3 | 457.4 | 454 | 443.1 | 447.5 | 422.5 | 389.8
1957 | 1817 | 525.8 | 474.8 | 500.2 | 471.3 | 457.4 | 454 | 443.2 | 447.5 | 422.6 | 389.8
1958 | 1818 | 525.8 | 474.8 | 500.2 | 471.4 | 457.5 | 454.1 | 443.2 | 447.6 | 422.6 | 389.9
1959 | 1819 | 525.8 | 474.9 | 500.2 | 471.4 | 457.6 | 454.2 | 443.3 | 447.7 | 422.7 | 390.1
1960 | 1820 | 525.8 | 474.9 | 500.2 | 471.4 | 457.6 | 454.2 | 443.3 | 447.8 | 422.7 | 390.2
1961 | 1821 | 525.7 | 474.9 | 500.3 | 471.5 | 457.6 | 454.2 | 443.3 | 447.9 | 422.8 | 390.2
1962 | 1822 | 525.7 | 474.9 | 500.3 | 471.5 | 457.7 | 454.3 | 443.4 | 448 | 422.7 | 390.6
1963 | 1823 | 525.7 | 475 | 500.3 | 471.5 | 457.7 | 454.3 | 443.4 | 448.1 | 422.7 | 390.9
1964 | 1824 | 525.8 | 475 | 500.4 | 471.5 | 457.7 | 454.4 | 443.4 | 448.2 | 422.8 | 391
1965 | 1825 | 525.8 | 475 | 500.3 | 471.6 | 457.8 | 454.4 | 443.5 | 448.3 | 422.8 | 391.1
1966 | 1826 | 525.8 | 475 | 500.3 | 471.6 | 457.8 | 454.5 | 443.5 | 448.4 | 422.9 | 391.2
1967 | 1827 | 525.8 | 475.1 | 500.4 | 471.6 | 457.9 | 454.5 | 443.5 | 448.4 | 423 | 391.1
1968 | 1828 | 525.8 | 475.1 | 500.4 | 471.6 | 457.9 | 454.5 | 443.6 | 448.5 | 423.1 | 391.2
1969 | 1829 | 525.8 | 475.1 | 500.4 | 471.7 | 458 | 454.6 | 443.6 | 448.6 | 423.1 | 391.4
1970 | 1830 | 525.9 | 475.2 | 500.4 | 471.7 | 458.1 | 454.7 | 443.7 | 448.8 | 423.2 | 391.5
1971 | 1831 | 525.9 | 475.2 | 500.5 | 471.7 | 458 | 454.7 | 443.7 | 448.9 | 423.2 | 391.5
1972 | 1832 | 525.9 | 475.2 | 500.5 | 471.7 | 458.1 | 454.7 | 443.8 | 449 | 423.3 | 391.6
1973 | 1833 | 525.9 | 475.2 | 500.5 | 471.7 | 458.2 | 454.8 | 443.8 | 449 | 423.3 | 391.8
1974 | 1834 | 525.9 | 475.2 | 500.5 | 471.8 | 458.2 | 454.8 | 443.8 | 449.1 | 423.3 | 391.9
1975 | 1835 | 525.9 | 475.3 | 500.5 | 471.8 | 458.2 | 454.9 | 443.9 | 449.2 | 423.4 | 392
1976 | 1836 | 525.9 | 475.3 | 500.4 | 471.8 | 458.3 | 454.9 | 443.9 | 449.3 | 423.4 | 392.2
1977 | 1837 | 525.8 | 475.9 | 499.4 | 472.3 | 459.3 | 455.4 | 443.9 | 449.2 | 423.4 | 393.6
1978 | 1838 | 525.9 | 475.4 | 500.4 | 471.9 | 458.5 | 455.1 | 444 | 449.5 | 423.6 | 392.3
1979 | 1839 | 526 | 475.3 | 500.6 | 471.8 | 458.4 | 455 | 444.1 | 449.6 | 423.7 | 392.1
1980 | 1840 | 526 | 475.4 | 500.6 | 471.9 | 458.5 | 455.1 | 444.1 | 449.6 | 423.7 | 392.3
1981 | 1841 | 526 | 475.4 | 500.6 | 471.9 | 458.5 | 455.1 | 444.2 | 449.7 | 423.8 | 392.3
1982 | 1842 | 526 | 475.4 | 500.6 | 471.9 | 458.5 | 455.2 | 444.2 | 449.7 | 423.8 | 392.4
1983 | 1843 | 525.9 | 475.4 | 500.6 | 472 | 458.6 | 455.2 | 444.2 | 449.8 | 423.8 | 392.5
1984 | 1844 | 525.9 | 475.5 | 500.6 | 472 | 458.7 | 455.3 | 444.3 | 449.9 | 423.9 | 392.6
1985 | 1845 | 525.9 | 475.5 | 500.6 | 472 | 458.7 | 455.3 | 444.3 | 449.9 | 423.9 | 392.7
1986 | 1846 | 525.9 | 475.5 | 500.6 | 472 | 458.6 | 455.4 | 444.4 | 449.9 | 423.9 | 392.8
1987 | 1847 | 525.9 | 475.5 | 500.6 | 472.1 | 458.8 | 455.4 | 444.4 | 449.9 | 424 | 392.9
1988 | 1848 | 525.8 | 475.6 | 500.6 | 472.1 | 458.8 | 455.5 | 444.5 | 450 | 424 | 393
1989 | 1849 | 525.8 | 475.5 | 500.7 | 472.1 | 458.8 | 455.5 | 444.5 | 450.1 | 424.1 | 393
1990 | 1850 | 525.8 | 475.6 | 500.6 | 472.2 | 458.9 | 455.5 | 444.5 | 450.2 | 424.2 | 393.2
1991 | 1851 | 525.8 | 475.6 | 500.6 | 472.2 | 458.8 | 455.6 | 444.6 | 450.2 | 424.2 | 393.2
1992 | 1852 | 525.8 | 475.6 | 500.7 | 472.2 | 458.8 | 455.6 | 444.6 | 450.2 | 424.3 | 393.2
1993 | 1853 | 525.8 | 475.7 | 500.7 | 472.2 | 459 | 455.7 | 444.7 | 450.3 | 424.3 | 393.4
1994 | 1854 | 525.8 | 475.7 | 500.8 | 472.2 | 459.2 | 455.7 | 444.7 | 450.3 | 424.4 | 393.5
1995 | 1855 | 525.8 | 475.7 | 500.7 | 472.2 | 459.1 | 455.7 | 444.8 | 450.3 | 424.4 | 393.6
1996 | 1856 | 525.8 | 475.7 | 500.8 | 472.3 | 459.2 | 455.8 | 444.8 | 450.4 | 424.5 | 393.7
1997 | 1857 | 525.8 | 475.8 | 500.8 | 472.3 | 459.2 | 455.8 | 444.9 | 450.4 | 424.6 | 393.7
1998 | 1858 | 525.9 | 475.8 | 500.8 | 472.3 | 459.3 | 455.9 | 444.9 | 450.5 | 424.6 | 393.9
1999 | 1859 | 525.9 | 475.8 | 500.8 | 472.3 | 459.3 | 455.9 | 445 | 450.6 | 424.7 | 393.9
2000 | 1860 | 525.9 | 475.8 | 500.8 | 472.3 | 459.3 | 455.9 | 445 | 450.7 | 424.7 | 394
2001 | 1861 | 525.9 | 475.9 | 500.8 | 472.4 | 459.4 | 456 | 445.1 | 450.8 | 424.8 | 394.1
2002 | 1862 | 525.9 | 475.8 | 500.9 | 472.4 | 459.4 | 456 | 445.1 | 450.8 | 424.9 | 394.2
2003 | 1863 | 525.9 | 475.9 | 500.9 | 472.4 | 459.4 | 456.1 | 445.2 | 450.9 | 425 | 394.2
2004 | 1864 | 526 | 475.9 | 500.9 | 472.4 | 459.5 | 456.1 | 445.2 | 450.9 | 425 | 394.4
2005 | 1865 | 526 | 475.9 | 500.9 | 472.4 | 459.5 | 456.1 | 445.3 | 451 | 425.1 | 394.5
2006 | 1866 | 526 | 475.9 | 500.9 | 472.4 | 459.5 | 456.2 | 445.3 | 451 | 425.2 | 394.5
2007 | 1867 | 526 | 475.9 | 501 | 472.5 | 459.6 | 456.2 | 445.4 | 451 | 425.3 | 394.6
2008 | 1868 | 526 | 476 | 501 | 472.5 | 459.7 | 456.3 | 445.4 | 451.1 | 425.4 | 394.7
2009 | 1869 | 526 | 476 | 501 | 472.5 | 459.7 | 456.3 | 445.4 | 451.2 | 425.4 | 394.8
2010 | 1870 | 526 | 476 | 501 | 472.5 | 459.7 | 456.3 | 445.5 | 451.2 | 425.5 | 394.8
2011 | 1871 | 526 | 476 | 501 | 472.5 | 459.8 | 456.4 | 445.5 | 451.2 | 425.5 | 394.9
2012 | 1872 | 526 | 476.1 | 501 | 472.6 | 459.8 | 456.4 | 445.6 | 451.2 | 425.6 | 395
2013 | 1873 | 526 | 476.1 | 501 | 472.6 | 459.7 | 456.5 | 445.6 | 451.3 | 425.7 | 395.1
2014 | 1874 | 526.1 | 476.1 | 501 | 472.6 | 459.7 | 456.5 | 445.7 | 451.4 | 425.8 | 395.2
2015 | 1875 | 526.1 | 476.1 | 501 | 472.6 | 459.9 | 456.6 | 445.7 | 451.4 | 425.8 | 395.2
2016 | 1876 | 526.1 | 476.1 | 501.1 | 472.7 | 459.9 | 456.6 | 445.8 | 451.4 | 425.9 | 395.3
2017 | 1877 | 526.1 | 476.1 | 501.2 | 472.6 | 459.9 | 456.6 | 445.8 | 451.5 | 426 | 395.3
2018 | 1878 | 526 | 476.5 | 500.4 | 473 | 460.7 | 456.9 | 445.8 | 451.4 | 425.9 | 396.4
2019 | 1879 | 526 | 476.6 | 500.4 | 473 | 460.7 | 457 | 445.9 | 451.4 | 426 | 396.5
2020 | 1880 | 526 | 476.3 | 501 | 472.8 | 460.3 | 456.8 | 446 | 451.5 | 426.1 | 395.8
2021 | 1881 | 526 | 476.2 | 501.2 | 472.7 | 460.3 | 456.8 | 446 | 451.6 | 426.2 | 395.6
2022 | 1882 | 526 | 476.3 | 501.2 | 472.8 | 460.2 | 456.8 | 446.1 | 451.6 | 426.2 | 395.8
2023 | 1883 | 526 | 476.3 | 501.1 | 472.8 | 460.2 | 456.9 | 446.1 | 451.7 | 426.3 | 395.8
2024 | 1884 | 525.9 | 476.3 | 501.2 | 472.8 | 460.2 | 456.9 | 446.2 | 451.7 | 426.4 | 395.8
2025 | 1885 | 525.9 | 476.4 | 501.1 | 472.9 | 460.4 | 457 | 446.2 | 451.8 | 426.4 | 396
2026 | 1886 | 525.9 | 476.4 | 501.2 | 472.9 | 460.3 | 457 | 446.3 | 451.9 | 426.5 | 396.1
2027 | 1887 | 525.8 | 476.4 | 501.2 | 472.9 | 460.3 | 457 | 446.3 | 451.9 | 426.5 | 396.3
2028 | 1888 | 525.8 | 476.4 | 501.2 | 472.9 | 460.4 | 457 | 446.4 | 452 | 426.5 | 396.4
2029 | 1889 | 525.8 | 476.4 | 501.2 | 472.9 | 460.5 | 457.1 | 446.4 | 452.1 | 426.6 | 396.5
2030 | 1890 | 525.8 | 476.4 | 501.2 | 472.9 | 460.5 | 457.1 | 446.4 | 452.1 | 426.6 | 396.5
2031 | 1891 | 525.8 | 476.4 | 501.3 | 473 | 460.5 | 457.1 | 446.5 | 452.1 | 426.7 | 396.5
2032 | 1892 | 525.8 | 476.5 | 501.2 | 473 | 460.6 | 457.2 | 446.5 | 452.2 | 426.7 | 396.7
2033 | 1893 | 525.8 | 476.5 | 501.2 | 473 | 460.5 | 457.2 | 446.6 | 452.2 | 426.8 | 396.8
2034 | 1894 | 525.8 | 476.5 | 501.3 | 473 | 460.6 | 457.2 | 446.6 | 452.3 | 426.8 | 396.8
2035 | 1895 | 525.8 | 476.6 | 501.3 | 473 | 460.7 | 457.3 | 446.7 | 452.3 | 426.9 | 396.9
2036 | 1896 | 525.8 | 476.6 | 501.3 | 473.1 | 460.8 | 457.3 | 446.7 | 452.4 | 426.9 | 396.8
2037 | 1897 | 525.8 | 476.6 | 501.4 | 473.1 | 460.7 | 457.4 | 446.8 | 452.5 | 427 | 396.8
2038 | 1898 | 525.8 | 476.6 | 501.4 | 473.1 | 460.8 | 457.4 | 446.8 | 452.6 | 427 | 396.8
2039 | 1899 | 525.8 | 476.6 | 501.4 | 473.1 | 460.8 | 457.4 | 446.9 | 452.6 | 427.1 | 396.8
2040 | 1900 | 525.9 | 476.6 | 501.4 | 473.2 | 460.9 | 457.5 | 446.9 | 452.7 | 427.2 | 396.8
2041 | 1901 | 526 | 476.7 | 501.4 | 473.2 | 460.9 | 457.5 | 446.9 | 452.7 | 427.2 | 396.9
2042 | 1902 | 526 | 476.7 | 501.4 | 473.2 | 460.9 | 457.5 | 447 | 452.8 | 427.3 | 396.9
2043 | 1903 | 526.1 | 476.7 | 501.4 | 473.2 | 461 | 457.6 | 447 | 452.9 | 427.3 | 397
2044 | 1904 | 526.1 | 476.7 | 501.4 | 473.2 | 461.1 | 457.6 | 447.1 | 452.9 | 427.4 | 397
2045 | 1905 | 526.1 | 476.7 | 501.5 | 473.2 | 461 | 457.6 | 447.1 | 453 | 427.5 | 397
2046 | 1906 | 526.1 | 476.8 | 501.4 | 473.3 | 461 | 457.7 | 447.2 | 453.1 | 427.5 | 397.1
2047 | 1907 | 526.1 | 476.8 | 501.4 | 473.3 | 461.1 | 457.7 | 447.2 | 453.1 | 427.6 | 397.1
2048 | 1908 | 526 | 476.8 | 501.5 | 473.3 | 461.1 | 457.7 | 447.3 | 453.1 | 427.7 | 397.1
2049 | 1909 | 526 | 476.8 | 501.5 | 473.3 | 461.1 | 457.8 | 447.3 | 453.2 | 427.8 | 397.2
2050 | 1910 | 526 | 476.8 | 501.5 | 473.3 | 461.3 | 457.8 | 447.3 | 453.3 | 427.9 | 397.3
2051 | 1911 | 525.9 | 476.8 | 501.5 | 473.3 | 461.3 | 457.9 | 447.4 | 453.3 | 428 | 397.3
2052 | 1912 | 525.9 | 476.8 | 501.5 | 473.4 | 461.3 | 457.9 | 447.4 | 453.4 | 428.1 | 397.4
2053 | 1913 | 525.9 | 476.9 | 501.5 | 473.4 | 461.4 | 457.9 | 447.5 | 453.4 | 428.2 | 397.5
2054 | 1914 | 525.9 | 476.9 | 501.6 | 473.4 | 461.4 | 458 | 447.5 | 453.4 | 428.2 | 397.6
2055 | 1915 | 525.9 | 476.9 | 501.6 | 473.4 | 461.4 | 458 | 447.6 | 453.4 | 428.4 | 397.7
2056 | 1916 | 525.9 | 476.9 | 501.6 | 473.5 | 461.3 | 458 | 447.6 | 453.5 | 428.5 | 397.8
2057 | 1917 | 525.9 | 477 | 501.6 | 473.5 | 461.5 | 458.1 | 447.6 | 453.5 | 428.5 | 398.2
2058 | 1918 | 525.8 | 477 | 501.6 | 473.5 | 461.5 | 458.1 | 447.7 | 453.5 | 428.6 | 398.3
2059 | 1919 | 525.8 | 477 | 501.6 | 473.5 | 461.5 | 458.1 | 447.7 | 453.6 | 428.7 | 398.4
2060 | 1920 | 525.8 | 477 | 501.6 | 473.6 | 461.5 | 458.2 | 447.8 | 453.6 | 428.9 | 398.6
2061 | 1921 | 525.8 | 477 | 501.7 | 473.6 | 461.6 | 458.2 | 447.8 | 453.7 | 429 | 398.7
2062 | 1922 | 525.9 | 477 | 501.7 | 473.6 | 461.6 | 458.2 | 447.9 | 453.8 | 429.1 | 398.7
2063 | 1923 | 525.8 | 477 | 501.7 | 473.6 | 461.7 | 458.3 | 447.9 | 453.9 | 429.2 | 398.8
2064 | 1924 | 525.8 | 477.1 | 501.7 | 473.6 | 461.7 | 458.3 | 447.9 | 454.1 | 429.4 | 398.9
2065 | 1925 | 525.8 | 477.1 | 501.8 | 473.7 | 461.7 | 458.3 | 448 | 454.1 | 429.4 | 399
2066 | 1926 | 525.8 | 477.1 | 501.7 | 473.7 | 461.7 | 458.4 | 448 | 454.2 | 429.5 | 399
2067 | 1927 | 525.8 | 477.1 | 501.8 | 473.7 | 461.9 | 458.4 | 448.1 | 454.2 | 429.6 | 399.2
2068 | 1928 | 525.8 | 477.2 | 501.7 | 473.7 | 461.8 | 458.5 | 448.1 | 454.3 | 429.7 | 399.3
2069 | 1929 | 525.8 | 477.2 | 501.8 | 473.8 | 461.8 | 458.5 | 448.1 | 454.3 | 429.9 | 399.2
2070 | 1930 | 525.9 | 477.2 | 501.8 | 473.8 | 461.8 | 458.5 | 448.2 | 454.3 | 430.1 | 399.3
2071 | 1931 | 525.9 | 477.2 | 501.8 | 473.8 | 461.9 | 458.5 | 448.2 | 454.3 | 430.1 | 399.4
2072 | 1932 | 526 | 477.2 | 501.8 | 473.8 | 461.9 | 458.6 | 448.3 | 454.3 | 430.1 | 399.4
2073 | 1933 | 526 | 477.2 | 501.9 | 473.8 | 461.9 | 458.6 | 448.3 | 454.4 | 430.3 | 399.4
2074 | 1934 | 526 | 477.3 | 501.9 | 473.9 | 462 | 458.6 | 448.3 | 454.4 | 430.4 | 399.4
2075 | 1935 | 526 | 477.3 | 501.9 | 473.9 | 462 | 458.7 | 448.4 | 454.5 | 430.4 | 399.5
2076 | 1936 | 526 | 477.3 | 502 | 473.9 | 462 | 458.7 | 448.4 | 454.6 | 430.5 | 399.5
2077 | 1937 | 526 | 477.3 | 501.9 | 473.9 | 462 | 458.7 | 448.5 | 454.6 | 430.7 | 399.5
2078 | 1938 | 526 | 477.3 | 502 | 473.9 | 462.1 | 458.8 | 448.5 | 454.6 | 430.9 | 399.6
2079 | 1939 | 526 | 477.3 | 502 | 473.9 | 462.1 | 458.8 | 448.5 | 454.6 | 431 | 399.6
2080 | 1940 | 526 | 477.3 | 502 | 474 | 462.1 | 458.8 | 448.6 | 454.6 | 431.1 | 399.6
2081 | 1941 | 526 | 477.4 | 502 | 474 | 462.2 | 458.9 | 448.6 | 454.7 | 431.3 | 399.7
2082 | 1942 | 526 | 477.4 | 502 | 474 | 462.3 | 458.9 | 448.6 | 454.7 | 431.3 | 399.8
2083 | 1943 | 526 | 477.4 | 502 | 474 | 462.3 | 458.9 | 448.7 | 454.9 | 431.4 | 399.7
2084 | 1944 | 526 | 477.4 | 502 | 474.1 | 462.3 | 459 | 448.7 | 454.9 | 431.6 | 399.8
2085 | 1945 | 526 | 477.4 | 502 | 474.1 | 462.3 | 459 | 448.7 | 455 | 431.5 | 399.8
2086 | 1946 | 526 | 477.4 | 502 | 474.1 | 462.3 | 459 | 448.8 | 455.1 | 431.6 | 399.9
2087 | 1947 | 526 | 477.4 | 502.1 | 474.1 | 462.4 | 459 | 448.8 | 455.2 | 431.6 | 399.8
2088 | 1948 | 526 | 477.5 | 502.1 | 474.1 | 462.4 | 459.1 | 448.8 | 455.2 | 431.7 | 399.9
2089 | 1949 | 526 | 477.5 | 502.2 | 474.1 | 462.6 | 459.1 | 448.9 | 455.2 | 431.9 | 399.9
2090 | 1950 | 526 | 477.5 | 502.1 | 474.2 | 462.4 | 459.1 | 448.9 | 455.3 | 432 | 399.9
2091 | 1951 | 525.9 | 477.5 | 502.1 | 474.2 | 462.4 | 459.2 | 449 | 455.3 | 432 | 400
2092 | 1952 | 525.9 | 477.5 | 502.1 | 474.2 | 462.5 | 459.2 | 449 | 455.3 | 432.1 | 400
2093 | 1953 | 525.8 | 477.5 | 502.2 | 474.2 | 462.6 | 459.3 | 449 | 455.4 | 432.2 | 400.1
2094 | 1954 | 525.7 | 477.5 | 502.2 | 474.2 | 462.5 | 459.3 | 449.1 | 455.3 | 432.3 | 400
2095 | 1955 | 525.7 | 477.6 | 502.1 | 474.3 | 462.7 | 459.3 | 449.1 | 455.4 | 432.4 | 400.2
2096 | 1956 | 525.7 | 477.6 | 502.1 | 474.3 | 462.6 | 459.4 | 449.1 | 455.4 | 432.5 | 400.2
2097 | 1957 | 525.7 | 477.6 | 502.2 | 474.3 | 462.6 | 459.4 | 449.2 | 455.5 | 432.6 | 400.2
2098 | 1958 | 525.6 | 477.6 | 502.2 | 474.3 | 462.7 | 459.4 | 449.2 | 455.6 | 432.6 | 400.2
2099 | 1959 | 525.6 | 477.6 | 502.2 | 474.3 | 462.8 | 459.4 | 449.2 | 455.6 | 432.7 | 400.3
2100 | 1960 | 525.6 | 477.7 | 502.2 | 474.4 | 462.8 | 459.5 | 449.2 | 455.7 | 432.8 | 400.4
2101 | 1961 | 525.6 | 477.7 | 502.2 | 474.4 | 462.8 | 459.5 | 449.3 | 455.8 | 432.8 | 400.4
2102 | 1962 | 525.6 | 477.7 | 502.2 | 474.4 | 462.9 | 459.6 | 449.3 | 455.8 | 432.8 | 400.4
2103 | 1963 | 525.6 | 477.7 | 502.2 | 474.4 | 462.9 | 459.6 | 449.3 | 455.8 | 432.8 | 400.4
2104 | 1964 | 525.6 | 477.7 | 502.3 | 474.5 | 462.8 | 459.6 | 449.4 | 455.8 | 432.9 | 400.4
2105 | 1965 | 525.6 | 477.7 | 502.3 | 474.5 | 463 | 459.6 | 449.4 | 455.8 | 432.9 | 400.4
2106 | 1966 | 525.6 | 477.7 | 502.3 | 474.5 | 463 | 459.7 | 449.5 | 455.9 | 432.9 | 400.5
2107 | 1967 | 525.6 | 477.8 | 502.3 | 474.5 | 462.9 | 459.7 | 449.5 | 455.9 | 432.9 | 400.5
2108 | 1968 | 525.7 | 477.7 | 502.4 | 474.5 | 463 | 459.7 | 449.5 | 455.9 | 432.9 | 400.4
2109 | 1969 | 525.7 | 477.8 | 502.4 | 474.6 | 463 | 459.8 | 449.6 | 455.9 | 433 | 400.5
2110 | 1970 | 525.7 | 477.8 | 502.4 | 474.6 | 463.2 | 459.8 | 449.6 | 455.9 | 433.1 | 400.7
2111 | 1971 | 525.8 | 477.8 | 502.4 | 474.6 | 463.1 | 459.8 | 449.6 | 456 | 433.2 | 400.5
2112 | 1972 | 525.8 | 477.8 | 502.4 | 474.7 | 463.2 | 459.9 | 449.6 | 456 | 433.2 | 400.7
2113 | 1973 | 525.8 | 477.8 | 502.4 | 474.7 | 463.2 | 459.9 | 449.7 | 456 | 433.3 | 400.7
2114 | 1974 | 525.8 | 477.9 | 502.4 | 474.7 | 463.2 | 459.9 | 449.7 | 456 | 433.3 | 400.7
2115 | 1975 | 525.8 | 477.9 | 502.4 | 474.7 | 463.2 | 460 | 449.7 | 456 | 433.4 | 400.8
2116 | 1976 | 525.8 | 477.9 | 502.4 | 474.7 | 463.3 | 460 | 449.8 | 456.1 | 433.5 | 400.7
2117 | 1977 | 525.8 | 477.9 | 502.4 | 474.7 | 463.3 | 460 | 449.8 | 456.1 | 433.5 | 400.8
2118 | 1978 | 525.8 | 477.9 | 502.5 | 474.8 | 463.3 | 460 | 449.8 | 456.2 | 433.6 | 400.8
2119 | 1979 | 525.8 | 477.9 | 502.5 | 474.8 | 463.3 | 460.1 | 449.9 | 456.1 | 433.6 | 400.7
2120 | 1980 | 525.8 | 477.9 | 502.5 | 474.8 | 463.4 | 460.1 | 449.9 | 456.1 | 433.7 | 400.8
2121 | 1981 | 525.8 | 477.9 | 502.5 | 474.8 | 463.5 | 460.2 | 449.9 | 456.1 | 433.7 | 400.8
2122 | 1982 | 525.7 | 477.9 | 502.5 | 474.8 | 463.5 | 460.2 | 449.9 | 456 | 433.7 | 400.8
2123 | 1983 | 525.7 | 478 | 502.5 | 474.9 | 463.4 | 460.2 | 449.9 | 455.9 | 433.8 | 400.9
2124 | 1984 | 525.7 | 478 | 502.5 | 474.9 | 463.5 | 460.3 | 450 | 456 | 433.7 | 401
2125 | 1985 | 525.7 | 478 | 502.6 | 474.9 | 463.5 | 460.3 | 450 | 456 | 433.7 | 400.8
2126 | 1986 | 525.7 | 478 | 502.6 | 474.9 | 463.5 | 460.3 | 450 | 455.9 | 433.8 | 400.9
2127 | 1987 | 525.7 | 478 | 502.6 | 474.9 | 463.6 | 460.3 | 450 | 455.6 | 433.8 | 401
2128 | 1988 | 525.6 | 478 | 502.6 | 474.9 | 463.7 | 460.4 | 450.1 | 455.4 | 433.8 | 401
2129 | 1989 | 525.6 | 478 | 502.6 | 475 | 463.6 | 460.4 | 450.1 | 455.4 | 433.8 | 401
2130 | 1990 | 525.6 | 478.1 | 502.5 | 475 | 463.7 | 460.5 | 450.1 | 455.4 | 433.8 | 401.2
2131 | 1991 | 525.6 | 478.1 | 502.5 | 475 | 463.7 | 460.5 | 450.1 | 455.4 | 433.8 | 401.2
2132 | 1992 | 525.6 | 478.1 | 502.6 | 475 | 463.7 | 460.5 | 450.1 | 455.3 | 433.9 | 401.1
2133 | 1993 | 525.6 | 478.1 | 502.6 | 475 | 463.7 | 460.5 | 450.2 | 455.2 | 434 | 401.2
2134 | 1994 | 525.6 | 478.1 | 502.6 | 475.1 | 463.8 | 460.6 | 450.2 | 455 | 434 | 401.3
2135 | 1995 | 525.6 | 478.1 | 502.6 | 475.1 | 463.9 | 460.6 | 450.2 | 454.8 | 434.1 | 401.3
2136 | 1996 | 525.7 | 478.1 | 502.6 | 475.1 | 463.8 | 460.6 | 450.2 | 454.9 | 434.2 | 401.3
2137 | 1997 | 525.6 | 478.1 | 502.6 | 475.1 | 463.9 | 460.7 | 450.2 | 455.2 | 434.3 | 401.4
2138 | 1998 | 525.7 | 478.2 | 502.6 | 475.2 | 464 | 460.7 | 450.2 | 455.6 | 434.6 | 401.5
2139 | 1999 | 525.7 | 478.1 | 502.7 | 475.2 | 463.9 | 460.7 | 450.2 | 455.9 | 434.8 | 401.4
2140 | 2000 | 525.7 | 478.2 | 502.7 | 475.2 | 464 | 460.7 | 450.2 | 455.9 | 434.9 | 401.4
2141 | 2001 | 525.6 | 478.2 | 502.7 | 475.2 | 464 | 460.8 | 450.2 | 456.1 | 434.9 | 401.5
2142 | 2002 | 525.6 | 478.2 | 502.7 | 475.2 | 464.1 | 460.8 | 450.2 | 456.3 | 434.9 | 401.5
2143 | 2003 | 525.6 | 478.2 | 502.7 | 475.2 | 464 | 460.8 | 450.2 | 456.4 | 435 | 401.5
2144 | 2004 | 525.6 | 478.2 | 502.7 | 475.3 | 464.1 | 460.9 | 450.2 | 456.5 | 434.9 | 401.6
2145 | 2005 | 525.7 | 478.2 | 502.7 | 475.3 | 464.1 | 460.9 | 450.2 | 456.6 | 435 | 401.6
2146 | 2006 | 525.7 | 478.2 | 502.8 | 475.3 | 464.1 | 460.9 | 450.2 | 456.7 | 435 | 401.5
2147 | 2007 | 525.7 | 478.2 | 502.7 | 475.3 | 464.2 | 461 | 450.2 | 456.8 | 435 | 401.6
2148 | 2008 | 525.7 | 478.2 | 502.8 | 475.3 | 464.2 | 461 | 450.2 | 456.9 | 435.1 | 401.7
2149 | 2009 | 525.8 | 478.2 | 502.8 | 475.3 | 464.2 | 461 | 450.3 | 456.9 | 435.2 | 401.7
2150 | 2010 | 525.8 | 478.2 | 502.8 | 475.4 | 464.2 | 461 | 450.3 | 457 | 435.2 | 401.7
2151 | 2011 | 525.8 | 478.3 | 502.8 | 475.4 | 464.3 | 461.1 | 450.3 | 457 | 435.3 | 401.9
2152 | 2012 | 525.8 | 478.3 | 502.8 | 475.4 | 464.4 | 461.1 | 450.3 | 457.1 | 435.4 | 401.9
2153 | 2013 | 525.9 | 478.3 | 502.8 | 475.5 | 464.3 | 461.2 | 450.3 | 457.2 | 435.4 | 401.9
2154 | 2014 | 525.9 | 478.3 | 502.8 | 475.4 | 464.4 | 461.2 | 450.3 | 457.2 | 435.5 | 401.9
2155 | 2015 | 525.9 | 478.3 | 502.8 | 475.5 | 464.4 | 461.2 | 450.3 | 457.3 | 435.6 | 402
2156 | 2016 | 526 | 478.3 | 502.8 | 475.5 | 464.4 | 461.2 | 450.3 | 457.2 | 435.7 | 402
2157 | 2017 | 526 | 478.3 | 502.9 | 475.5 | 464.4 | 461.2 | 450.3 | 457.2 | 435.8 | 402
2158 | 2018 | 525.9 | 478.4 | 502.9 | 475.5 | 464.5 | 461.3 | 450.3 | 457 | 435.8 | 402.1
2159 | 2019 | 526 | 478.4 | 502.9 | 475.6 | 464.6 | 461.3 | 450.3 | 457 | 435.9 | 402.2
2160 | 2020 | 526 | 478.4 | 502.9 | 475.6 | 464.5 | 461.3 | 450.3 | 457.2 | 436 | 402.2
2161 | 2021 | 526 | 478.4 | 503 | 475.6 | 464.6 | 461.4 | 450.3 | 457.3 | 436.1 | 402.2
2162 | 2022 | 526 | 478.4 | 503 | 475.6 | 464.6 | 461.4 | 450.4 | 457.4 | 436.2 | 402.2
2163 | 2023 | 526 | 478.4 | 503 | 475.6 | 464.6 | 461.4 | 450.4 | 457.5 | 436.2 | 402.3
2164 | 2024 | 525.9 | 478.4 | 503 | 475.7 | 464.6 | 461.5 | 450.4 | 457.6 | 436.2 | 402.3
2165 | 2025 | 525.9 | 478.4 | 503 | 475.7 | 464.7 | 461.5 | 450.4 | 457.6 | 436.2 | 402.4
2166 | 2026 | 525.9 | 478.5 | 503 | 475.7 | 464.7 | 461.5 | 450.4 | 457.7 | 436.2 | 402.5
2167 | 2027 | 525.9 | 478.5 | 503 | 475.7 | 464.7 | 461.5 | 450.4 | 457.8 | 436.2 | 402.4
2168 | 2028 | 525.9 | 478.5 | 503 | 475.8 | 464.8 | 461.6 | 450.4 | 457.8 | 436.2 | 402.5
2169 | 2029 | 525.8 | 478.5 | 503 | 475.8 | 464.8 | 461.6 | 450.4 | 457.8 | 436.2 | 402.6
2170 | 2030 | 525.8 | 478.5 | 503.1 | 475.8 | 464.8 | 461.6 | 450.4 | 457.9 | 436.2 | 402.6
2171 | 2031 | 525.8 | 478.5 | 503.1 | 475.8 | 464.8 | 461.6 | 450.4 | 457.9 | 436.3 | 402.5
2172 | 2032 | 525.7 | 478.5 | 503.1 | 475.8 | 464.9 | 461.7 | 450.4 | 458 | 436.4 | 402.7
2173 | 2033 | 525.7 | 478.5 | 503.2 | 475.8 | 465 | 461.7 | 450.5 | 458 | 436.4 | 402.7
2174 | 2034 | 525.7 | 478.6 | 503.1 | 475.8 | 465 | 461.7 | 450.5 | 458 | 436.5 | 402.7
2175 | 2035 | 525.7 | 478.6 | 503.1 | 475.9 | 465 | 461.8 | 450.5 | 458 | 436.5 | 402.7
2176 | 2036 | 525.7 | 478.6 | 503.1 | 475.9 | 465 | 461.8 | 450.5 | 458.1 | 436.6 | 402.8
2177 | 2037 | 525.7 | 478.6 | 503.1 | 475.9 | 465 | 461.8 | 450.5 | 458.1 | 436.6 | 402.8
2178 | 2038 | 525.7 | 478.6 | 503.2 | 475.9 | 465 | 461.9 | 450.5 | 458.1 | 436.7 | 402.8
2179 | 2039 | 525.7 | 478.6 | 503.1 | 476 | 465.2 | 461.9 | 450.5 | 458.1 | 436.7 | 403
2180 | 2040 | 525.7 | 478.6 | 503.1 | 476 | 465.2 | 461.9 | 450.5 | 458.2 | 436.7 | 403
2181 | 2041 | 525.6 | 478.6 | 503.2 | 476 | 465.2 | 461.9 | 450.5 | 458.2 | 436.8 | 403
2182 | 2042 | 525.7 | 478.6 | 503.2 | 476 | 465.2 | 462 | 450.5 | 458.2 | 436.8 | 403
2183 | 2043 | 525.6 | 478.7 | 503.2 | 476 | 465.3 | 462 | 450.5 | 458.2 | 436.9 | 403.2
2184 | 2044 | 525.6 | 478.7 | 503.1 | 476.1 | 465.2 | 462.1 | 450.6 | 458.3 | 436.9 | 403.2
2185 | 2045 | 525.6 | 478.7 | 503.2 | 476.1 | 465.3 | 462.1 | 450.6 | 458.3 | 437 | 403.2
2186 | 2046 | 525.6 | 478.7 | 503.2 | 476.1 | 465.4 | 462.1 | 450.6 | 458.3 | 437 | 403.3
2187 | 2047 | 525.7 | 478.7 | 503.2 | 476.1 | 465.4 | 462.1 | 450.6 | 458.4 | 437 | 403.3
2188 | 2048 | 525.6 | 478.7 | 503.3 | 476.1 | 465.4 | 462.2 | 450.6 | 458.4 | 437 | 403.3
2189 | 2049 | 525.6 | 478.7 | 503.3 | 476.2 | 465.4 | 462.2 | 450.6 | 458.4 | 437 | 403.3
2190 | 2050 | 525.6 | 478.7 | 503.4 | 476.2 | 465.5 | 462.2 | 450.6 | 458.4 | 437.1 | 403.4
2191 | 2051 | 525.6 | 478.8 | 503.3 | 476.2 | 465.5 | 462.3 | 450.6 | 458.4 | 437.1 | 403.5
2192 | 2052 | 525.6 | 478.8 | 503.4 | 476.2 | 465.5 | 462.3 | 450.7 | 458.4 | 437.2 | 403.4
2193 | 2053 | 525.6 | 478.8 | 503.3 | 476.2 | 465.6 | 462.3 | 450.7 | 458.5 | 437.2 | 403.5
2194 | 2054 | 525.7 | 478.8 | 503.4 | 476.3 | 465.6 | 462.3 | 450.7 | 458.5 | 437.2 | 403.6
2195 | 2055 | 525.7 | 478.8 | 503.4 | 476.3 | 465.6 | 462.4 | 450.7 | 458.6 | 437.2 | 403.5
2196 | 2056 | 525.7 | 478.8 | 503.4 | 476.3 | 465.6 | 462.4 | 450.7 | 458.6 | 437.2 | 403.6
2197 | 2057 | 525.7 | 478.9 | 503.4 | 476.3 | 465.8 | 462.4 | 450.7 | 458.6 | 437.1 | 403.7
2198 | 2058 | 525.7 | 478.9 | 503.4 | 476.3 | 465.7 | 462.5 | 450.7 | 458.6 | 437.1 | 403.7
2199 | 2059 | 525.7 | 478.9 | 503.5 | 476.4 | 465.7 | 462.5 | 450.7 | 458.7 | 437.2 | 403.7
2200 | 2060 | 525.7 | 478.9 | 503.4 | 476.4 | 465.9 | 462.5 | 450.7 | 458.6 | 437.2 | 403.8
2201 | 2061 | 525.7 | 478.9 | 503.4 | 476.4 | 465.8 | 462.5 | 450.7 | 458.6 | 437.2 | 403.9
2202 | 2062 | 525.7 | 478.9 | 503.5 | 476.4 | 465.9 | 462.6 | 450.8 | 458.7 | 437.2 | 403.9
2203 | 2063 | 525.7 | 478.9 | 503.5 | 476.4 | 465.9 | 462.6 | 450.8 | 458.6 | 437.3 | 403.9
2204 | 2064 | 525.7 | 478.9 | 503.5 | 476.5 | 465.9 | 462.6 | 450.8 | 458.6 | 437.3 | 404
2205 | 2065 | 525.8 | 479 | 503.5 | 476.5 | 466 | 462.7 | 450.8 | 458.6 | 437.3 | 404
2206 | 2066 | 525.8 | 479 | 503.5 | 476.5 | 466 | 462.7 | 450.8 | 458.6 | 437.3 | 404
2207 | 2067 | 525.8 | 479 | 503.5 | 476.5 | 466 | 462.7 | 450.8 | 458.6 | 437.4 | 404.2
2208 | 2068 | 525.8 | 479 | 503.5 | 476.5 | 466.1 | 462.7 | 450.8 | 458.6 | 437.4 | 404.2
2209 | 2069 | 525.8 | 479 | 503.6 | 476.5 | 466 | 462.7 | 450.8 | 458.7 | 437.5 | 404.1
2210 | 2070 | 525.8 | 479 | 503.5 | 476.5 | 466 | 462.8 | 450.9 | 458.7 | 437.5 | 404.2
2211 | 2071 | 525.9 | 479 | 503.5 | 476.6 | 466.1 | 462.8 | 450.9 | 458.7 | 437.6 | 404.3
2212 | 2072 | 525.9 | 479 | 503.6 | 476.6 | 466.1 | 462.8 | 450.9 | 458.7 | 437.6 | 404.3
2213 | 2073 | 525.8 | 479 | 503.6 | 476.6 | 466.1 | 462.8 | 450.9 | 458.7 | 437.7 | 404.3
2214 | 2074 | 525.8 | 479.1 | 503.6 | 476.6 | 466.2 | 462.9 | 450.9 | 458.7 | 437.7 | 404.5
2215 | 2075 | 525.9 | 479.1 | 503.6 | 476.7 | 466.2 | 462.9 | 450.9 | 458.7 | 437.7 | 404.6
2216 | 2076 | 525.9 | 479.1 | 503.6 | 476.7 | 466.2 | 462.9 | 450.9 | 458.7 | 437.7 | 404.6
2217 | 2077 | 525.9 | 479.1 | 503.7 | 476.7 | 466.3 | 462.9 | 450.9 | 458.7 | 437.8 | 404.7
2218 | 2078 | 525.8 | 479.1 | 503.6 | 476.7 | 466.4 | 463 | 450.8 | 458.6 | 437.9 | 404.7
2219 | 2079 | 525.8 | 479.1 | 503.7 | 476.7 | 466.4 | 463 | 450.8 | 458.6 | 437.9 | 404.7
2220 | 2080 | 525.8 | 479.1 | 503.7 | 476.7 | 466.4 | 463 | 450.9 | 458.6 | 438 | 404.7
2221 | 2081 | 525.9 | 479.2 | 503.7 | 476.8 | 466.4 | 463.1 | 450.9 | 458.7 | 438 | 404.9
2222 | 2082 | 525.9 | 479.2 | 503.7 | 476.8 | 466.5 | 463.1 | 450.8 | 458.7 | 438 | 404.9
2223 | 2083 | 525.9 | 479.2 | 503.7 | 476.8 | 466.5 | 463.1 | 450.9 | 458.7 | 438.1 | 404.9
2224 | 2084 | 525.8 | 479.2 | 503.8 | 476.8 | 466.5 | 463.1 | 450.9 | 458.7 | 438.1 | 405
2225 | 2085 | 525.8 | 479.2 | 503.8 | 476.8 | 466.6 | 463.2 | 450.8 | 458.7 | 438.1 | 405
2226 | 2086 | 525.8 | 479.2 | 503.8 | 476.9 | 466.6 | 463.2 | 450.8 | 458.6 | 438.1 | 405.1
2227 | 2087 | 525.8 | 479.3 | 503.8 | 476.9 | 466.6 | 463.2 | 450.8 | 458.7 | 438.2 | 405.1
2228 | 2088 | 525.8 | 479.3 | 503.8 | 476.9 | 466.7 | 463.2 | 450.8 | 458.7 | 438.2 | 405.2
2229 | 2089 | 525.8 | 479.3 | 503.8 | 476.9 | 466.7 | 463.3 | 450.8 | 458.7 | 438.3 | 405.2
2230 | 2090 | 525.8 | 479.3 | 503.8 | 476.9 | 466.7 | 463.3 | 450.8 | 458.8 | 438.3 | 405.2
2231 | 2091 | 525.8 | 479.3 | 503.8 | 476.9 | 466.7 | 463.3 | 450.8 | 458.8 | 438.4 | 405.2
2232 | 2092 | 525.8 | 479.4 | 503.8 | 476.9 | 466.8 | 463.4 | 450.8 | 458.8 | 438.4 | 405.3
2233 | 2093 | 525.7 | 479.4 | 503.8 | 477 | 466.8 | 463.4 | 450.8 | 458.7 | 438.5 | 405.4
2234 | 2094 | 525.8 | 479.4 | 503.8 | 477 | 466.8 | 463.4 | 450.8 | 458.1 | 438.5 | 405.3
2235 | 2095 | 525.7 | 479.4 | 503.8 | 477 | 466.9 | 463.4 | 450.8 | 457.8 | 438.6 | 405.4
2236 | 2096 | 525.7 | 479.4 | 503.8 | 477 | 466.9 | 463.4 | 450.8 | 457.8 | 438.6 | 405.5
2237 | 2097 | 525.7 | 479.4 | 503.8 | 477 | 466.9 | 463.5 | 450.8 | 457.8 | 438.6 | 405.4
2238 | 2098 | 525.7 | 479.4 | 503.9 | 477.1 | 466.9 | 463.5 | 450.8 | 457.8 | 438.7 | 405.5
2239 | 2099 | 525.7 | 479.5 | 503.9 | 477.1 | 467 | 463.5 | 450.8 | 457.9 | 438.8 | 405.6
2240 | 2100 | 525.7 | 479.5 | 503.9 | 477.1 | 467 | 463.5 | 450.8 | 458 | 438.8 | 405.6
2241 | 2101 | 525.7 | 479.4 | 504 | 477.1 | 467 | 463.5 | 450.8 | 457.9 | 438.9 | 405.5
2242 | 2102 | 525.7 | 479.5 | 503.9 | 477.1 | 467.1 | 463.6 | 450.8 | 457.9 | 438.9 | 405.6
2243 | 2103 | 525.7 | 479.5 | 503.9 | 477.1 | 467.1 | 463.6 | 450.8 | 457.8 | 438.8 | 405.7
2244 | 2104 | 525.6 | 479.5 | 504 | 477.2 | 467.1 | 463.6 | 450.8 | 457.8 | 438.8 | 405.7
2245 | 2105 | 525.6 | 479.5 | 504 | 477.2 | 467.1 | 463.6 | 450.8 | 457.7 | 438.8 | 405.7
2246 | 2106 | 525.6 | 479.5 | 504 | 477.2 | 467.2 | 463.7 | 450.8 | 457.7 | 438.8 | 405.8
2247 | 2107 | 525.6 | 479.5 | 504 | 477.2 | 467.2 | 463.7 | 450.8 | 457.7 | 438.8 | 405.7
2248 | 2108 | 525.6 | 479.6 | 504.1 | 477.2 | 467.2 | 463.7 | 450.8 | 457.6 | 438.8 | 405.7
2249 | 2109 | 525.6 | 479.6 | 504 | 477.2 | 467.2 | 463.7 | 450.8 | 457.6 | 438.8 | 405.8
2250 | 2110 | 525.6 | 479.6 | 504 | 477.2 | 467.3 | 463.8 | 450.8 | 457.4 | 438.8 | 405.9
2251 | 2111 | 525.6 | 479.6 | 504 | 477.2 | 467.3 | 463.8 | 450.8 | 457.2 | 438.9 | 405.8
2252 | 2112 | 525.6 | 479.6 | 504.1 | 477.3 | 467.3 | 463.8 | 450.8 | 457 | 439 | 405.9
2253 | 2113 | 525.7 | 479.6 | 504.1 | 477.3 | 467.4 | 463.8 | 450.8 | 456.3 | 439 | 406
2254 | 2114 | 525.7 | 479.6 | 504.1 | 477.3 | 467.4 | 463.8 | 450.8 | 456.2 | 439.1 | 406
2255 | 2115 | 525.7 | 479.6 | 504.2 | 477.3 | 467.4 | 463.8 | 450.8 | 456.3 | 439.1 | 406
2256 | 2116 | 525.7 | 479.6 | 504.1 | 477.3 | 467.4 | 463.9 | 450.8 | 456.1 | 439.1 | 406.1
2257 | 2117 | 525.6 | 479.7 | 504.1 | 477.4 | 467.5 | 463.9 | 450.8 | 455.6 | 439.1 | 406.2
2258 | 2118 | 525.6 | 479.6 | 504.2 | 477.4 | 467.5 | 463.9 | 450.8 | 455 | 439.1 | 406.1
2259 | 2119 | 525.7 | 479.7 | 504.1 | 477.4 | 467.5 | 464 | 450.8 | 455 | 439.1 | 406.2
2260 | 2120 | 525.7 | 479.7 | 504.1 | 477.4 | 467.6 | 464 | 450.8 | 454.6 | 439 | 406.3
2261 | 2121 | 525.7 | 479.7 | 504.1 | 477.4 | 467.6 | 464 | 450.8 | 454.2 | 439 | 406.4
2262 | 2122 | 525.7 | 479.7 | 504.2 | 477.4 | 467.6 | 464 | 450.8 | 454.6 | 439 | 406.3
2263 | 2123 | 525.8 | 479.7 | 504.1 | 477.4 | 467.6 | 464.1 | 450.8 | 454.5 | 439 | 406.5
2264 | 2124 | 525.8 | 479.7 | 504.2 | 477.4 | 467.7 | 464.1 | 450.8 | 453.8 | 439 | 406.5
2265 | 2125 | 525.8 | 479.7 | 504.2 | 477.4 | 467.8 | 464.1 | 450.8 | 453.8 | 439 | 406.5
2266 | 2126 | 525.8 | 479.7 | 504.2 | 477.5 | 467.7 | 464.1 | 450.8 | 454.3 | 439.1 | 406.6
2267 | 2127 | 525.8 | 479.8 | 504.1 | 477.5 | 467.8 | 464.2 | 450.8 | 454.2 | 439.1 | 406.7
2268 | 2128 | 525.7 | 479.8 | 504.1 | 477.5 | 467.8 | 464.2 | 450.8 | 453.7 | 439.1 | 406.7
2269 | 2129 | 525.7 | 479.8 | 504.2 | 477.5 | 467.8 | 464.2 | 450.9 | 453.7 | 439.2 | 406.7
2270 | 2130 | 525.7 | 479.8 | 504.2 | 477.5 | 467.9 | 464.2 | 450.9 | 453.8 | 439.2 | 406.8
2271 | 2131 | 525.7 | 479.8 | 504.2 | 477.5 | 467.9 | 464.2 | 450.9 | 453.9 | 439.2 | 406.8
2272 | 2132 | 525.7 | 479.8 | 504.2 | 477.5 | 467.9 | 464.3 | 450.9 | 453.7 | 439.2 | 406.8
2273 | 2133 | 525.7 | 479.8 | 504.2 | 477.6 | 468 | 464.3 | 450.9 | 453 | 439.2 | 406.8
2274 | 2134 | 525.7 | 479.9 | 504.2 | 477.6 | 468 | 464.3 | 450.9 | 453.2 | 439.3 | 406.9
2275 | 2135 | 525.7 | 479.9 | 504.3 | 477.6 | 468 | 464.3 | 450.9 | 453.3 | 439.4 | 407
2276 | 2136 | 525.8 | 479.9 | 504.4 | 477.6 | 468 | 464.3 | 450.9 | 453.3 | 439.4 | 406.9
2277 | 2137 | 525.8 | 479.9 | 504.3 | 477.6 | 468.1 | 464.4 | 450.9 | 453.3 | 439.4 | 407
2278 | 2138 | 525.8 | 479.9 | 504.3 | 477.6 | 468.1 | 464.4 | 450.9 | 453.2 | 439.5 | 407.1
2279 | 2139 | 525.7 | 479.9 | 504.3 | 477.7 | 468.1 | 464.4 | 450.9 | 453.1 | 439.5 | 407.1
2280 | 2140 | 525.7 | 479.9 | 504.3 | 477.7 | 468.1 | 464.4 | 451 | 453.1 | 439.6 | 407.1
2281 | 2141 | 525.7 | 480 | 504.3 | 477.7 | 468.2 | 464.5 | 451 | 453 | 439.6 | 407.2
2282 | 2142 | 525.7 | 480 | 504.3 | 477.7 | 468.2 | 464.5 | 451 | 453.1 | 439.6 | 407.2
2283 | 2143 | 525.7 | 480 | 504.4 | 477.7 | 468.2 | 464.5 | 451 | 453.2 | 439.6 | 407.2
2284 | 2144 | 525.7 | 480 | 504.3 | 477.7 | 468.3 | 464.5 | 451 | 453.1 | 439.6 | 407.3
2285 | 2145 | 525.7 | 480 | 504.3 | 477.8 | 468.3 | 464.6 | 451.1 | 453 | 439.6 | 407.3
2286 | 2146 | 525.7 | 480 | 504.4 | 477.8 | 468.3 | 464.6 | 451.1 | 453 | 439.6 | 407.3
2287 | 2147 | 525.7 | 480 | 504.4 | 477.8 | 468.3 | 464.6 | 451.1 | 452.7 | 439.7 | 407.3
2288 | 2148 | 525.8 | 480 | 504.4 | 477.8 | 468.4 | 464.6 | 451.1 | 452.5 | 439.7 | 407.4
2289 | 2149 | 525.7 | 480 | 504.4 | 477.8 | 468.4 | 464.7 | 451.1 | 452.6 | 439.7 | 407.4
2290 | 2150 | 525.8 | 480.1 | 504.4 | 477.8 | 468.4 | 464.7 | 451.1 | 452.4 | 439.7 | 407.4
2291 | 2151 | 525.8 | 480.1 | 504.4 | 477.8 | 468.4 | 464.7 | 451.2 | 452.4 | 439.8 | 407.5
2292 | 2152 | 525.8 | 480.1 | 504.4 | 477.8 | 468.5 | 464.7 | 451.2 | 452.6 | 439.8 | 407.6
2293 | 2153 | 525.7 | 480.1 | 504.4 | 477.8 | 468.5 | 464.8 | 451.2 | 452.7 | 439.9 | 407.6
2294 | 2154 | 525.7 | 480.1 | 504.4 | 477.8 | 468.5 | 464.8 | 451.2 | 452.7 | 439.9 | 407.6
2295 | 2155 | 525.6 | 480.1 | 504.4 | 477.9 | 468.6 | 464.8 | 451.2 | 452.5 | 440 | 407.7
2296 | 2156 | 525.6 | 480.1 | 504.4 | 477.9 | 468.6 | 464.8 | 451.3 | 452.6 | 440 | 407.7
2297 | 2157 | 525.6 | 480.1 | 504.4 | 477.8 | 468.6 | 464.8 | 451.3 | 452.4 | 440 | 407.7
2298 | 2158 | 525.5 | 480.2 | 504.3 | 477.9 | 468.7 | 464.9 | 451.3 | 452.3 | 440 | 407.9
2299 | 2159 | 525.4 | 480.2 | 504.3 | 477.9 | 468.7 | 464.9 | 451.3 | 452.2 | 440.1 | 407.9
2300 | 2160 | 525.5 | 480.2 | 504.3 | 477.9 | 468.7 | 465 | 451.3 | 452.2 | 440.1 | 407.9
2301 | 2161 | 525.5 | 480.2 | 504.4 | 477.9 | 468.7 | 465 | 451.3 | 452.1 | 440.1 | 408
2302 | 2162 | 525.5 | 480.2 | 504.4 | 477.9 | 468.8 | 465 | 451.4 | 452 | 440.1 | 408.1
2303 | 2163 | 525.5 | 480.2 | 504.4 | 477.9 | 468.9 | 465.1 | 451.4 | 451.7 | 440.2 | 408.1
2304 | 2164 | 525.5 | 480.2 | 504.4 | 477.9 | 468.8 | 465.1 | 451.4 | 451.3 | 440.3 | 408.1
2305 | 2165 | 525.5 | 480.3 | 504.4 | 478 | 468.9 | 465.1 | 451.4 | 451.5 | 440.3 | 408.2
2306 | 2166 | 525.6 | 480.3 | 504.4 | 478 | 469 | 465.1 | 451.5 | 451.7 | 440.3 | 408.2
2307 | 2167 | 525.6 | 480.3 | 504.4 | 478 | 468.9 | 465.1 | 451.5 | 451.8 | 440.4 | 408.2
2308 | 2168 | 525.6 | 480.3 | 504.4 | 478 | 468.9 | 465.2 | 451.6 | 451.8 | 440.4 | 408.3
2309 | 2169 | 525.6 | 480.3 | 504.5 | 478 | 469.1 | 465.2 | 451.5 | 451.9 | 440.5 | 408.4
2310 | 2170 | 525.6 | 480.3 | 504.5 | 478.1 | 469 | 465.2 | 451.5 | 452 | 440.5 | 408.4
2311 | 2171 | 525.7 | 480.3 | 504.5 | 478.1 | 469 | 465.2 | 451.5 | 452.1 | 440.5 | 408.4
2312 | 2172 | 525.7 | 480.3 | 504.5 | 478.1 | 469.1 | 465.3 | 451.5 | 452.3 | 440.5 | 408.5
2313 | 2173 | 525.7 | 480.3 | 504.6 | 478.1 | 469.2 | 465.3 | 451.6 | 452.3 | 440.5 | 408.5
2314 | 2174 | 525.7 | 480.3 | 504.6 | 478.1 | 469.1 | 465.3 | 451.6 | 452.4 | 440.6 | 408.5
2315 | 2175 | 525.8 | 480.3 | 504.6 | 478.1 | 469 | 465.3 | 451.6 | 452.2 | 440.6 | 408.5
2316 | 2176 | 525.8 | 480.4 | 504.6 | 478.1 | 469.2 | 465.4 | 451.6 | 452.2 | 440.6 | 408.7
2317 | 2177 | 525.8 | 480.4 | 504.6 | 478.2 | 469.2 | 465.4 | 451.6 | 452.3 | 440.6 | 408.7
2318 | 2178 | 525.8 | 480.3 | 504.7 | 478.1 | 469.2 | 465.4 | 451.6 | 452.5 | 440.6 | 408.6
2319 | 2179 | 525.8 | 480.4 | 504.6 | 478.2 | 469.2 | 465.4 | 451.7 | 452.7 | 440.7 | 408.8
2320 | 2180 | 525.7 | 480.4 | 504.6 | 478.2 | 469.2 | 465.4 | 451.7 | 453 | 440.7 | 408.8
2321 | 2181 | 525.7 | 480.4 | 504.7 | 478.2 | 469.2 | 465.4 | 451.7 | 453.2 | 440.7 | 408.8
2322 | 2182 | 525.7 | 480.4 | 504.7 | 478.2 | 469.3 | 465.5 | 451.8 | 453.2 | 440.7 | 408.9
2323 | 2183 | 525.7 | 480.4 | 504.7 | 478.2 | 469.3 | 465.5 | 451.8 | 453.3 | 440.8 | 409
2324 | 2184 | 525.6 | 480.4 | 504.7 | 478.2 | 469.3 | 465.5 | 451.9 | 453.4 | 440.7 | 409
2325 | 2185 | 525.6 | 480.4 | 504.7 | 478.3 | 469.3 | 465.5 | 451.9 | 453.5 | 440.8 | 409
2326 | 2186 | 525.6 | 480.4 | 504.7 | 478.3 | 469.4 | 465.6 | 451.9 | 453.5 | 440.8 | 409.1
2327 | 2187 | 525.6 | 480.5 | 504.7 | 478.3 | 469.5 | 465.6 | 452 | 453.8 | 440.8 | 409.2
2328 | 2188 | 525.6 | 480.5 | 504.7 | 478.3 | 469.4 | 465.6 | 452 | 454 | 440.8 | 409.2
2329 | 2189 | 525.5 | 480.5 | 504.7 | 478.3 | 469.5 | 465.6 | 452.1 | 454 | 440.8 | 409.2
2330 | 2190 | 525.5 | 480.5 | 504.7 | 478.3 | 469.5 | 465.7 | 452.1 | 454.1 | 440.8 | 409.3
2331 | 2191 | 525.5 | 480.5 | 504.7 | 478.3 | 469.6 | 465.7 | 452.1 | 454.4 | 440.9 | 409.4
2332 | 2192 | 525.5 | 480.5 | 504.7 | 478.3 | 469.6 | 465.7 | 452.2 | 454.4 | 440.9 | 409.4
2333 | 2193 | 525.5 | 480.5 | 504.7 | 478.4 | 469.7 | 465.8 | 452.2 | 454.3 | 440.9 | 409.5
2334 | 2194 | 525.4 | 480.6 | 504.8 | 478.4 | 469.7 | 465.8 | 452.2 | 454.1 | 441 | 409.6
2335 | 2195 | 525.4 | 480.5 | 504.8 | 478.4 | 469.7 | 465.8 | 452.3 | 454 | 441 | 409.5
2336 | 2196 | 525.4 | 480.6 | 504.8 | 478.4 | 469.7 | 465.8 | 452.3 | 454.2 | 441 | 409.6
2337 | 2197 | 525.4 | 480.6 | 504.8 | 478.4 | 469.8 | 465.9 | 452.3 | 454.4 | 441.1 | 409.7
2338 | 2198 | 525.4 | 480.6 | 504.8 | 478.4 | 469.8 | 465.9 | 452.4 | 454.8 | 441.1 | 409.8
2339 | 2199 | 525.4 | 480.6 | 504.8 | 478.4 | 469.8 | 465.9 | 452.4 | 454.8 | 441.2 | 409.8
2340 | 2200 | 525.4 | 480.6 | 504.8 | 478.5 | 469.9 | 465.9 | 452.5 | 454.7 | 441.3 | 409.9
2341 | 2201 | 525.4 | 480.6 | 504.7 | 478.5 | 469.9 | 466 | 452.5 | 454.8 | 441.3 | 410
2342 | 2202 | 525.4 | 480.6 | 504.8 | 478.5 | 469.9 | 466 | 452.5 | 454.8 | 441.3 | 409.9
2343 | 2203 | 525.4 | 480.6 | 504.7 | 478.5 | 469.9 | 466 | 452.6 | 454.9 | 441.3 | 410
2344 | 2204 | 525.4 | 480.7 | 504.8 | 478.5 | 470 | 466.1 | 452.6 | 455.1 | 441.3 | 410.1
2345 | 2205 | 525.4 | 480.7 | 504.8 | 478.5 | 470 | 466.1 | 452.6 | 455.2 | 441.4 | 410.1
2346 | 2206 | 525.4 | 480.6 | 504.8 | 478.5 | 470 | 466.1 | 452.7 | 455.3 | 441.4 | 410.1
2347 | 2207 | 525.4 | 480.7 | 504.8 | 478.6 | 470.1 | 466.1 | 452.7 | 455.6 | 441.4 | 410.2
2348 | 2208 | 525.4 | 480.7 | 504.8 | 478.6 | 470.1 | 466.2 | 452.8 | 455.6 | 441.5 | 410.3
2349 | 2209 | 525.5 | 480.7 | 504.8 | 478.6 | 470.1 | 466.2 | 452.8 | 455.7 | 441.5 | 410.3
2350 | 2210 | 525.4 | 480.7 | 504.8 | 478.6 | 470.1 | 466.2 | 452.9 | 455.9 | 441.5 | 410.3
2351 | 2211 | 525.4 | 480.7 | 504.8 | 478.6 | 470.2 | 466.2 | 452.9 | 455.6 | 441.6 | 410.4
2352 | 2212 | 525.5 | 480.7 | 504.8 | 478.6 | 470.2 | 466.3 | 453 | 455.5 | 441.6 | 410.4
2353 | 2213 | 525.5 | 480.7 | 504.9 | 478.7 | 470.2 | 466.3 | 453 | 455.7 | 441.6 | 410.4
2354 | 2214 | 525.6 | 480.8 | 504.9 | 478.7 | 470.3 | 466.3 | 453.1 | 455.8 | 441.6 | 410.5
2355 | 2215 | 525.6 | 480.8 | 504.9 | 478.7 | 470.3 | 466.3 | 453.1 | 455.9 | 441.6 | 410.5
2356 | 2216 | 525.6 | 480.7 | 505 | 478.7 | 470.3 | 466.3 | 453.2 | 456.2 | 441.7 | 410.5
2357 | 2217 | 525.6 | 480.8 | 505 | 478.7 | 470.3 | 466.4 | 453.2 | 456.3 | 441.7 | 410.6
2358 | 2218 | 525.6 | 480.8 | 504.9 | 478.7 | 470.4 | 466.4 | 453.3 | 456.3 | 441.7 | 410.7
2359 | 2219 | 525.6 | 480.8 | 505 | 478.7 | 470.4 | 466.4 | 453.3 | 456.2 | 441.8 | 410.7
2360 | 2220 | 525.6 | 480.8 | 505 | 478.7 | 470.4 | 466.5 | 453.4 | 456.4 | 441.9 | 410.7
2361 | 2221 | 525.6 | 480.8 | 505 | 478.8 | 470.5 | 466.5 | 453.4 | 456.5 | 442 | 410.8
2362 | 2222 | 525.6 | 480.8 | 505 | 478.8 | 470.5 | 466.5 | 453.4 | 456.9 | 442 | 410.9
2363 | 2223 | 525.6 | 480.8 | 505 | 478.8 | 470.5 | 466.5 | 453.5 | 457.4 | 442.1 | 410.9
2364 | 2224 | 525.6 | 480.8 | 505 | 478.8 | 470.5 | 466.6 | 453.5 | 457.7 | 442.1 | 410.9
2365 | 2225 | 525.5 | 480.9 | 504.9 | 478.8 | 470.6 | 466.6 | 453.6 | 458 | 442.1 | 411
2366 | 2226 | 525.5 | 480.9 | 505 | 478.8 | 470.6 | 466.6 | 453.6 | 458.2 | 442 | 411
2367 | 2227 | 525.5 | 480.8 | 505 | 478.8 | 470.6 | 466.6 | 453.7 | 458.2 | 442 | 411
2368 | 2228 | 525.5 | 480.9 | 505 | 478.8 | 470.7 | 466.7 | 453.7 | 458.2 | 442 | 411.1
2369 | 2229 | 525.5 | 480.9 | 505 | 478.8 | 470.7 | 466.7 | 453.7 | 458.5 | 442.1 | 411.2
2370 | 2230 | 525.5 | 480.9 | 505 | 478.9 | 470.7 | 466.7 | 453.8 | 458.7 | 442.1 | 411.2
2371 | 2231 | 525.5 | 480.9 | 505 | 478.9 | 470.8 | 466.8 | 453.8 | 458.8 | 442.1 | 411.3
2372 | 2232 | 525.4 | 480.9 | 505 | 478.9 | 470.8 | 466.8 | 453.9 | 459 | 442.1 | 411.4
2373 | 2233 | 525.4 | 481 | 505.1 | 478.9 | 470.9 | 466.8 | 453.9 | 459.2 | 442.1 | 411.4
2374 | 2234 | 525.4 | 481 | 505.1 | 478.9 | 470.9 | 466.8 | 453.9 | 459.3 | 442.1 | 411.4
2375 | 2235 | 525.4 | 481 | 505 | 479 | 471 | 466.9 | 454 | 459.4 | 442.1 | 411.6
2376 | 2236 | 525.5 | 481 | 505 | 479 | 471 | 466.9 | 454 | 459.6 | 442.2 | 411.7
2377 | 2237 | 525.5 | 481 | 505 | 479 | 471 | 467 | 454.1 | 459.7 | 442.2 | 411.6
2378 | 2238 | 525.5 | 481 | 505.1 | 479 | 471 | 467 | 454.1 | 459.8 | 442.2 | 411.7
2379 | 2239 | 525.6 | 481 | 505.1 | 479.1 | 471.1 | 467 | 454.1 | 459.8 | 442.3 | 411.8
2380 | 2240 | 525.6 | 481.1 | 505.1 | 479.1 | 471.1 | 467 | 454.2 | 459.8 | 442.3 | 411.8
2381 | 2241 | 525.7 | 481 | 505.2 | 479.1 | 471.1 | 467 | 454.2 | 459.8 | 442.3 | 411.8
2382 | 2242 | 525.8 | 481.1 | 505.1 | 479.1 | 471.1 | 467.1 | 454.2 | 459.9 | 442.3 | 411.9
2383 | 2243 | 525.8 | 481.1 | 505.1 | 479.1 | 471.2 | 467.1 | 454.3 | 460 | 442.3 | 412
2384 | 2244 | 525.8 | 481.1 | 505.2 | 479.1 | 471.1 | 467.1 | 454.3 | 460 | 442.4 | 412
2385 | 2245 | 525.8 | 481.1 | 505.2 | 479.1 | 471.2 | 467.1 | 454.3 | 460.1 | 442.3 | 412
2386 | 2246 | 525.8 | 481.1 | 505.2 | 479.2 | 471.2 | 467.2 | 454.4 | 460.2 | 442.3 | 412.1
2387 | 2247 | 525.8 | 481.1 | 505.2 | 479.2 | 471.2 | 467.2 | 454.4 | 460.3 | 442.3 | 412.1
2388 | 2248 | 525.8 | 481.1 | 505.3 | 479.2 | 471.3 | 467.2 | 454.5 | 460.3 | 442.3 | 412.1
2389 | 2249 | 525.9 | 481.2 | 505.2 | 479.2 | 471.3 | 467.3 | 454.5 | 460.3 | 442.4 | 412.2
2390 | 2250 | 525.9 | 481.2 | 505.2 | 479.2 | 471.4 | 467.3 | 454.5 | 460.3 | 442.4 | 412.3
2391 | 2251 | 525.9 | 481.2 | 505.3 | 479.2 | 471.3 | 467.3 | 454.6 | 460.4 | 442.5 | 412.2
2392 | 2252 | 525.9 | 481.2 | 505.3 | 479.2 | 471.4 | 467.3 | 454.6 | 460.5 | 442.6 | 412.2
2393 | 2253 | 525.9 | 481.2 | 505.3 | 479.2 | 471.4 | 467.4 | 454.6 | 460.5 | 442.7 | 412.3
2394 | 2254 | 525.8 | 481.2 | 505.3 | 479.2 | 471.5 | 467.4 | 454.7 | 460.6 | 442.7 | 412.4
2395 | 2255 | 525.8 | 481.2 | 505.4 | 479.2 | 471.4 | 467.4 | 454.7 | 460.7 | 442.7 | 412.3
2396 | 2256 | 525.8 | 481.2 | 505.3 | 479.3 | 471.6 | 467.5 | 454.7 | 460.7 | 442.8 | 412.5
2397 | 2257 | 525.8 | 481.2 | 505.3 | 479.3 | 471.5 | 467.5 | 454.8 | 460.9 | 442.8 | 412.5
2398 | 2258 | 525.7 | 481.2 | 505.4 | 479.2 | 471.6 | 467.5 | 454.8 | 460.9 | 442.8 | 412.4
2399 | 2259 | 525.7 | 481.2 | 505.3 | 479.3 | 471.6 | 467.5 | 454.9 | 461 | 442.8 | 412.5
2400 | 2260 | 525.7 | 481.3 | 505.4 | 479.3 | 471.7 | 467.6 | 454.9 | 461 | 442.8 | 412.6
2401 | 2261 | 525.7 | 481.3 | 505.3 | 479.3 | 471.7 | 467.6 | 455 | 461 | 442.9 | 412.6
2402 | 2262 | 525.7 | 481.3 | 505.4 | 479.3 | 471.6 | 467.6 | 455 | 461 | 442.9 | 412.6
2403 | 2263 | 525.7 | 481.3 | 505.3 | 479.3 | 471.7 | 467.7 | 455 | 461.1 | 442.9 | 412.8
2404 | 2264 | 525.6 | 481.3 | 505.3 | 479.3 | 471.8 | 467.7 | 455 | 461.1 | 443 | 412.8
2405 | 2265 | 525.6 | 481.3 | 505.4 | 479.3 | 471.7 | 467.7 | 455.1 | 461.2 | 443 | 412.7
2406 | 2266 | 525.6 | 481.3 | 505.4 | 479.3 | 471.8 | 467.7 | 455.1 | 461.2 | 443 | 412.9
2407 | 2267 | 525.5 | 481.3 | 505.3 | 479.4 | 471.9 | 467.8 | 455.1 | 461.1 | 443.1 | 413
2408 | 2268 | 525.5 | 481.3 | 505.4 | 479.4 | 471.9 | 467.8 | 455.2 | 461.2 | 443.1 | 413
2409 | 2269 | 525.4 | 481.3 | 505.4 | 479.4 | 471.9 | 467.8 | 455.2 | 461.3 | 443.2 | 413
2410 | 2270 | 525.4 | 481.3 | 505.3 | 479.4 | 471.9 | 467.9 | 455.2 | 461.3 | 443.3 | 413.1
2411 | 2271 | 525.4 | 481.3 | 505.3 | 479.4 | 472.1 | 467.9 | 455.2 | 461.3 | 443.3 | 413.2
2412 | 2272 | 525.3 | 481.3 | 505.4 | 479.4 | 472 | 467.9 | 455.3 | 461.4 | 443.3 | 413.1
2413 | 2273 | 525.3 | 481.3 | 505.4 | 479.4 | 472.1 | 468 | 455.3 | 461.3 | 443.4 | 413.2
2414 | 2274 | 525.3 | 481.4 | 505.4 | 479.5 | 472.1 | 468 | 455.3 | 461.4 | 443.4 | 413.3
2415 | 2275 | 525.3 | 481.4 | 505.3 | 479.5 | 472.2 | 468 | 455.4 | 461.4 | 443.4 | 413.3
2416 | 2276 | 525.3 | 481.4 | 505.4 | 479.5 | 472.1 | 468.1 | 455.4 | 461.4 | 443.4 | 413.3
2417 | 2277 | 525.3 | 481.4 | 505.4 | 479.5 | 472.2 | 468.1 | 455.4 | 461.4 | 443.5 | 413.5
2418 | 2278 | 525.4 | 481.4 | 505.4 | 479.5 | 472.2 | 468.1 | 455.4 | 461.4 | 443.5 | 413.5
2419 | 2279 | 525.4 | 481.4 | 505.4 | 479.5 | 472.2 | 468.2 | 455.5 | 461.4 | 443.5 | 413.5
2420 | 2280 | 525.4 | 481.4 | 505.4 | 479.5 | 472.3 | 468.2 | 455.5 | 461.5 | 443.5 | 413.6
2421 | 2281 | 525.4 | 481.5 | 505.4 | 479.5 | 472.4 | 468.2 | 455.5 | 461.6 | 443.5 | 413.6
2422 | 2282 | 525.3 | 481.5 | 505.4 | 479.5 | 472.4 | 468.3 | 455.6 | 461.6 | 443.6 | 413.7
2423 | 2283 | 525.4 | 481.4 | 505.5 | 479.5 | 472.4 | 468.3 | 455.6 | 461.7 | 443.6 | 413.6
2424 | 2284 | 525.4 | 481.5 | 505.4 | 479.6 | 472.5 | 468.3 | 455.6 | 461.7 | 443.6 | 413.7
2425 | 2285 | 525.4 | 481.5 | 505.4 | 479.6 | 472.4 | 468.4 | 455.7 | 461.7 | 443.6 | 413.8
2426 | 2286 | 525.3 | 481.5 | 505.5 | 479.6 | 472.4 | 468.4 | 455.7 | 461.9 | 443.6 | 413.8
2427 | 2287 | 525.4 | 481.5 | 505.5 | 479.6 | 472.5 | 468.4 | 455.7 | 461.9 | 443.6 | 413.8
2428 | 2288 | 525.4 | 481.5 | 505.4 | 479.6 | 472.6 | 468.5 | 455.7 | 462 | 443.6 | 414
2429 | 2289 | 525.4 | 481.5 | 505.5 | 479.6 | 472.6 | 468.5 | 455.8 | 462 | 443.6 | 413.9
2430 | 2290 | 525.4 | 481.5 | 505.5 | 479.6 | 472.6 | 468.5 | 455.8 | 462 | 443.6 | 413.9
2431 | 2291 | 525.4 | 481.5 | 505.5 | 479.6 | 472.6 | 468.5 | 455.8 | 462 | 443.6 | 414
2432 | 2292 | 525.4 | 481.5 | 505.5 | 479.7 | 472.7 | 468.6 | 455.8 | 462 | 443.6 | 414.1
2433 | 2293 | 525.4 | 481.5 | 505.5 | 479.7 | 472.7 | 468.6 | 455.9 | 462 | 443.6 | 414.1
2434 | 2294 | 525.4 | 481.5 | 505.6 | 479.7 | 472.8 | 468.6 | 455.9 | 462.1 | 443.7 | 414.2
2435 | 2295 | 525.5 | 481.6 | 505.5 | 479.7 | 472.9 | 468.7 | 455.9 | 462.1 | 443.7 | 414.3
2436 | 2296 | 525.5 | 481.6 | 505.5 | 479.7 | 472.8 | 468.7 | 456 | 462.1 | 443.8 | 414.3
2437 | 2297 | 525.5 | 481.6 | 505.6 | 479.7 | 472.8 | 468.7 | 456 | 462.1 | 443.8 | 414.3
2438 | 2298 | 525.5 | 481.6 | 505.6 | 479.7 | 472.9 | 468.7 | 456 | 462.1 | 443.9 | 414.4
2439 | 2299 | 525.6 | 481.6 | 505.5 | 479.8 | 472.9 | 468.8 | 456 | 462.2 | 443.9 | 414.4
2440 | 2300 | 525.6 | 481.6 | 505.6 | 479.8 | 472.9 | 468.8 | 456.1 | 462.2 | 443.9 | 414.4
2441 | 2301 | 525.5 | 481.6 | 505.6 | 479.8 | 473 | 468.8 | 456.1 | 462.3 | 443.9 | 414.4
2442 | 2302 | 525.5 | 481.7 | 505.6 | 479.8 | 473 | 468.9 | 456.1 | 462.3 | 444 | 414.5
2443 | 2303 | 525.5 | 481.7 | 505.6 | 479.8 | 473.1 | 468.9 | 456.1 | 462.3 | 444 | 414.5
2444 | 2304 | 525.6 | 481.7 | 505.6 | 479.8 | 473.1 | 468.9 | 456.2 | 462.3 | 444 | 414.5
2445 | 2305 | 525.6 | 481.7 | 505.6 | 479.8 | 473.2 | 469 | 456.2 | 462.4 | 444 | 414.7
2446 | 2306 | 525.6 | 481.7 | 505.6 | 479.9 | 473.1 | 469 | 456.2 | 462.4 | 444.1 | 414.7
2447 | 2307 | 525.6 | 481.7 | 505.6 | 479.9 | 473.2 | 469 | 456.3 | 462.5 | 444.2 | 414.6
2448 | 2308 | 525.6 | 481.7 | 505.7 | 479.9 | 473.2 | 469.1 | 456.3 | 462.6 | 444.2 | 414.7
2449 | 2309 | 525.7 | 481.8 | 505.7 | 479.9 | 473.3 | 469.1 | 456.3 | 462.6 | 444.3 | 414.8
2450 | 2310 | 525.7 | 481.8 | 505.7 | 479.9 | 473.3 | 469.1 | 456.3 | 462.7 | 444.4 | 414.8
2451 | 2311 | 525.7 | 481.8 | 505.7 | 479.9 | 473.2 | 469.1 | 456.4 | 462.7 | 444.4 | 414.8
2452 | 2312 | 525.7 | 481.8 | 505.8 | 479.9 | 473.4 | 469.2 | 456.4 | 462.6 | 444.5 | 414.8
2453 | 2313 | 525.7 | 481.8 | 505.7 | 479.9 | 473.3 | 469.2 | 456.4 | 462.6 | 444.6 | 414.9
2454 | 2314 | 525.7 | 481.8 | 505.7 | 480 | 473.3 | 469.2 | 456.5 | 462.5 | 444.6 | 414.9
2455 | 2315 | 525.7 | 481.8 | 505.8 | 480 | 473.4 | 469.3 | 456.5 | 462.5 | 444.6 | 414.9
2456 | 2316 | 525.7 | 481.8 | 505.7 | 480 | 473.5 | 469.3 | 456.5 | 462.5 | 444.6 | 415
2457 | 2317 | 525.7 | 481.9 | 505.7 | 480 | 473.5 | 469.4 | 456.5 | 462.5 | 444.6 | 415.1
2458 | 2318 | 525.6 | 481.8 | 505.8 | 480 | 473.5 | 469.4 | 456.5 | 462.6 | 444.6 | 415
2459 | 2319 | 525.6 | 481.9 | 505.8 | 480 | 473.6 | 469.4 | 456.6 | 462.6 | 444.6 | 415.1
2460 | 2320 | 525.6 | 481.9 | 505.7 | 480 | 473.6 | 469.5 | 456.6 | 462.6 | 444.6 | 415.2
2461 | 2321 | 525.6 | 481.9 | 505.8 | 480 | 473.6 | 469.5 | 456.6 | 462.6 | 444.6 | 415.1
2462 | 2322 | 525.6 | 481.9 | 505.9 | 480 | 473.6 | 469.5 | 456.6 | 462.6 | 444.6 | 415.1
2463 | 2323 | 525.6 | 481.9 | 505.8 | 480.1 | 473.7 | 469.6 | 456.7 | 462.6 | 444.6 | 415.2
2464 | 2324 | 525.5 | 481.9 | 505.8 | 480.1 | 473.7 | 469.6 | 456.7 | 462.6 | 444.6 | 415.2
2465 | 2325 | 525.5 | 481.9 | 505.9 | 480 | 473.7 | 469.6 | 456.7 | 462.6 | 444.6 | 415.2
2466 | 2326 | 525.5 | 481.9 | 505.9 | 480.1 | 473.8 | 469.6 | 456.7 | 462.6 | 444.7 | 415.3
2467 | 2327 | 525.5 | 481.9 | 505.8 | 480.1 | 473.8 | 469.7 | 456.8 | 462.7 | 444.7 | 415.4
2468 | 2328 | 525.5 | 481.9 | 505.8 | 480.1 | 473.8 | 469.7 | 456.8 | 462.7 | 444.8 | 415.4
2469 | 2329 | 525.5 | 482 | 505.8 | 480.1 | 473.8 | 469.7 | 456.9 | 462.7 | 444.9 | 415.4
2470 | 2330 | 525.5 | 482 | 505.8 | 480.1 | 474 | 469.8 | 456.9 | 462.7 | 445 | 415.5
2471 | 2331 | 525.5 | 482 | 505.8 | 480.2 | 473.9 | 469.8 | 456.9 | 462.6 | 445.1 | 415.5
2472 | 2332 | 525.5 | 481.9 | 506 | 480.1 | 474 | 469.8 | 457 | 462.6 | 445.2 | 415.4
2473 | 2333 | 525.5 | 482 | 505.8 | 480.2 | 474 | 469.9 | 457 | 462.5 | 445.2 | 415.6
2474 | 2334 | 525.5 | 482 | 505.9 | 480.2 | 474 | 469.9 | 457 | 462.5 | 445.2 | 415.6
2475 | 2335 | 525.4 | 482 | 505.9 | 480.2 | 474.1 | 469.9 | 457.1 | 462.5 | 445.2 | 415.5
2476 | 2336 | 525.4 | 482 | 505.9 | 480.2 | 474.1 | 470 | 457.1 | 462.5 | 445.2 | 415.6
2477 | 2337 | 525.4 | 482 | 505.9 | 480.2 | 474.2 | 470 | 457.1 | 462.5 | 445.2 | 415.6
2478 | 2338 | 525.3 | 482 | 505.9 | 480.2 | 474.2 | 470 | 457.2 | 462.5 | 445.2 | 415.6
2479 | 2339 | 525.3 | 482 | 505.9 | 480.2 | 474.1 | 470.1 | 457.2 | 462.5 | 445.2 | 415.7
2480 | 2340 | 525.3 | 482 | 505.9 | 480.2 | 474.2 | 470.1 | 457.2 | 462.6 | 445.2 | 415.7
2481 | 2341 | 525.2 | 482 | 505.9 | 480.2 | 474.2 | 470.1 | 457.3 | 462.6 | 445.2 | 415.7
2482 | 2342 | 525.2 | 482 | 505.9 | 480.2 | 474.3 | 470.1 | 457.3 | 462.6 | 445.2 | 415.6
2483 | 2343 | 525.2 | 482 | 505.9 | 480.3 | 474.3 | 470.2 | 457.3 | 462.6 | 445.1 | 415.7
2484 | 2344 | 525.2 | 482.1 | 505.8 | 480.3 | 474.4 | 470.2 | 457.3 | 462.6 | 445.1 | 415.8
2485 | 2345 | 525.2 | 482 | 505.9 | 480.3 | 474.4 | 470.3 | 457.4 | 462.6 | 445 | 415.8
2486 | 2346 | 525.2 | 482 | 505.9 | 480.3 | 474.4 | 470.3 | 457.4 | 462.6 | 445 | 415.7
2487 | 2347 | 525.1 | 482.1 | 505.9 | 480.3 | 474.4 | 470.3 | 457.4 | 462.5 | 445 | 415.8
2488 | 2348 | 525.1 | 482.1 | 505.9 | 480.3 | 474.5 | 470.4 | 457.5 | 462.4 | 445 | 415.9
2489 | 2349 | 525.1 | 482.1 | 505.9 | 480.3 | 474.6 | 470.4 | 457.5 | 462.5 | 445 | 415.8
2490 | 2350 | 525.1 | 482.1 | 505.9 | 480.3 | 474.5 | 470.4 | 457.5 | 462.5 | 444.9 | 415.9
2491 | 2351 | 525.2 | 482.1 | 505.9 | 480.4 | 474.6 | 470.5 | 457.6 | 462.5 | 444.9 | 415.9
2492.1 | 2352.1 | 525.2 | 482.1 | 505.9 | 480.4 | 474.6 | 470.5 | 457.6 | 462.4 | 444.9 | 415.9
2493.1 | 2353.1 | 525.2 | 482.1 | 506 | 480.4 | 474.6 | 470.5 | 457.6 | 462.5 | 445 | 415.9
2494.1 | 2354.1 | 525.2 | 482.1 | 505.8 | 480.4 | 474.7 | 470.6 | 457.7 | 462.5 | 445 | 416
2495.1 | 2355.1 | 525.2 | 482.1 | 505.9 | 480.4 | 474.7 | 470.6 | 457.7 | 462.5 | 445 | 416
2496.1 | 2356.1 | 525.2 | 482.1 | 506 | 480.4 | 474.7 | 470.6 | 457.7 | 462.5 | 444.9 | 416
2497.1 | 2357.1 | 525.3 | 482.1 | 506 | 480.4 | 474.8 | 470.6 | 457.7 | 462.5 | 444.9 | 416
2498.1 | 2358.1 | 525.3 | 482.1 | 506 | 480.4 | 474.8 | 470.7 | 457.8 | 462.5 | 444.9 | 416.1
2499.1 | 2359.1 | 525.3 | 482.2 | 506 | 480.5 | 474.9 | 470.7 | 457.8 | 462.5 | 444.9 | 416.1
2500.1 | 2360.1 | 525.3 | 482.1 | 506 | 480.5 | 474.9 | 470.7 | 457.8 | 462.5 | 444.8 | 416.1
2501.1 | 2361.1 | 525.3 | 482.2 | 506 | 480.5 | 474.9 | 470.8 | 457.9 | 462.5 | 444.8 | 416.2
2502.1 | 2362.1 | 525.3 | 482.2 | 506 | 480.5 | 475 | 470.8 | 457.9 | 462.5 | 444.8 | 416.3
2503.1 | 2363.1 | 525.3 | 482.2 | 506 | 480.5 | 475 | 470.8 | 457.9 | 462.5 | 444.8 | 416.2
2504.1 | 2364.1 | 525.3 | 482.2 | 506.1 | 480.5 | 475 | 470.9 | 457.9 | 462.4 | 444.9 | 416.3
2505.1 | 2365.1 | 525.3 | 482.2 | 506.1 | 480.5 | 475.1 | 470.9 | 458 | 462.4 | 444.9 | 416.4
2506.1 | 2366.1 | 525.3 | 482.2 | 506.1 | 480.5 | 475.1 | 470.9 | 458 | 462.4 | 445 | 416.4
2507.1 | 2367.1 | 525.3 | 482.2 | 506.2 | 480.5 | 475.1 | 470.9 | 458 | 462.5 | 445 | 416.3
2508.1 | 2368.1 | 525.4 | 482.2 | 506.1 | 480.6 | 475.2 | 471 | 458.1 | 462.5 | 445 | 416.5
2509.1 | 2369.1 | 525.4 | 482.2 | 506.1 | 480.6 | 475.2 | 471 | 458.1 | 462.5 | 445.1 | 416.5
2510.1 | 2370.1 | 525.4 | 482.2 | 506.1 | 480.6 | 475.3 | 471.1 | 458.1 | 462.5 | 445.1 | 416.5
2511.1 | 2371.1 | 525.4 | 482.3 | 506.1 | 480.6 | 475.3 | 471.1 | 458.1 | 462.4 | 445.2 | 416.6
2512.1 | 2372.1 | 525.4 | 482.3 | 506.1 | 480.6 | 475.4 | 471.1 | 458.2 | 462.4 | 445.3 | 416.7
2513.1 | 2373.1 | 525.4 | 482.3 | 506.1 | 480.6 | 475.3 | 471.2 | 458.2 | 462.4 | 445.4 | 416.7
2514.1 | 2374.1 | 525.4 | 482.3 | 506.1 | 480.6 | 475.3 | 471.2 | 458.2 | 462.5 | 445.5 | 416.7
2515.1 | 2375.1 | 525.4 | 482.3 | 506.1 | 480.6 | 475.3 | 471.2 | 458.3 | 462.5 | 445.5 | 416.7
2516.1 | 2376.1 | 525.4 | 482.3 | 506.1 | 480.7 | 475.5 | 471.3 | 458.3 | 462.6 | 445.4 | 416.8
2517.1 | 2377.1 | 525.4 | 482.3 | 506.1 | 480.7 | 475.4 | 471.3 | 458.3 | 462.6 | 445.4 | 416.8
2518.1 | 2378.1 | 525.5 | 482.3 | 506.1 | 480.6 | 475.5 | 471.3 | 458.3 | 462.5 | 445.4 | 416.8
2519.1 | 2379.1 | 525.6 | 482.3 | 506.1 | 480.7 | 475.6 | 471.4 | 458.4 | 462.5 | 445.3 | 417
2520.1 | 2380.1 | 525.6 | 482.3 | 506.1 | 480.7 | 475.5 | 471.4 | 458.4 | 462.6 | 445.3 | 417
2521.1 | 2381.1 | 525.6 | 482.3 | 506.2 | 480.7 | 475.5 | 471.4 | 458.4 | 462.6 | 445.4 | 416.9
2522.1 | 2382.1 | 525.6 | 482.4 | 506.2 | 480.7 | 475.6 | 471.4 | 458.4 | 462.5 | 445.4 | 417
2523.1 | 2383.1 | 525.6 | 482.4 | 506.2 | 480.7 | 475.7 | 471.5 | 458.5 | 462.5 | 445.3 | 417.1
2524.1 | 2384.1 | 525.7 | 482.4 | 506.3 | 480.7 | 475.6 | 471.5 | 458.5 | 462.6 | 445.4 | 417
2525.1 | 2385.1 | 525.7 | 482.4 | 506.3 | 480.8 | 475.6 | 471.5 | 458.5 | 462.6 | 445.4 | 417.1
2526.1 | 2386.1 | 525.7 | 482.4 | 506.2 | 480.8 | 475.7 | 471.6 | 458.5 | 462.5 | 445.4 | 417.2
2527.1 | 2387.1 | 525.8 | 482.4 | 506.3 | 480.8 | 475.8 | 471.6 | 458.6 | 462.4 | 445.4 | 417.2
2528.1 | 2388.1 | 525.8 | 482.4 | 506.3 | 480.8 | 475.7 | 471.6 | 458.6 | 462.4 | 445.5 | 417.2
2529.1 | 2389.1 | 525.8 | 482.4 | 506.3 | 480.8 | 475.8 | 471.6 | 458.6 | 462.5 | 445.5 | 417.2
2530.1 | 2390.1 | 525.8 | 482.4 | 506.3 | 480.8 | 475.9 | 471.7 | 458.7 | 462.5 | 445.6 | 417.3
2531.1 | 2391.1 | 525.8 | 482.4 | 506.3 | 480.8 | 475.8 | 471.7 | 458.7 | 462.5 | 445.6 | 417.2
2532.1 | 2392.1 | 525.8 | 482.4 | 506.3 | 480.8 | 475.8 | 471.7 | 458.7 | 462.5 | 445.7 | 417.3
2533.1 | 2393.1 | 525.8 | 482.5 | 506.3 | 480.9 | 475.9 | 471.8 | 458.7 | 462.4 | 445.7 | 417.4
2534.1 | 2394.1 | 525.8 | 482.4 | 506.4 | 480.8 | 475.9 | 471.8 | 458.8 | 462.4 | 445.7 | 417.4
2535.1 | 2395.1 | 525.8 | 482.5 | 506.4 | 480.8 | 476 | 471.8 | 458.8 | 462.4 | 445.7 | 417.4
2536.1 | 2396.1 | 525.8 | 482.5 | 506.3 | 480.9 | 476 | 471.8 | 458.8 | 462.5 | 445.7 | 417.5
2537.1 | 2397.1 | 525.8 | 482.5 | 506.2 | 480.9 | 476 | 471.9 | 458.9 | 462.5 | 445.7 | 417.5
2538.1 | 2398.1 | 525.7 | 482.5 | 506.3 | 480.9 | 476 | 471.9 | 458.9 | 462.5 | 445.8 | 417.5
2539.1 | 2399.1 | 525.7 | 482.5 | 506.4 | 480.9 | 476 | 471.9 | 458.9 | 462.6 | 445.8 | 417.5
2540.1 | 2400.1 | 525.7 | 482.5 | 506.3 | 480.9 | 476.1 | 471.9 | 458.9 | 462.7 | 445.8 | 417.6
2541.1 | 2401.1 | 525.6 | 482.5 | 506.3 | 480.9 | 476.1 | 472 | 459 | 462.7 | 445.8 | 417.6
2542.1 | 2402.1 | 525.6 | 482.5 | 506.3 | 480.9 | 476.1 | 472 | 459 | 462.7 | 445.8 | 417.6
2543.1 | 2403.1 | 525.6 | 482.5 | 506.4 | 480.9 | 476.2 | 472 | 459 | 462.7 | 445.8 | 417.7
2544.1 | 2404.1 | 525.6 | 482.5 | 506.4 | 480.9 | 476.2 | 472.1 | 459 | 462.8 | 445.9 | 417.8
2545.1 | 2405.1 | 525.5 | 482.5 | 506.4 | 480.9 | 476.3 | 472.1 | 459.1 | 462.9 | 445.9 | 417.7
2546.1 | 2406.1 | 525.5 | 482.5 | 506.4 | 480.9 | 476.3 | 472.1 | 459.1 | 462.9 | 445.9 | 417.8
2547.1 | 2407.1 | 525.4 | 482.6 | 506.3 | 480.9 | 476.4 | 472.2 | 459.1 | 463 | 445.9 | 417.9
2548.1 | 2408.1 | 525.4 | 482.6 | 506.3 | 480.9 | 476.4 | 472.2 | 459.1 | 463 | 446 | 417.9
2549.1 | 2409.1 | 525.4 | 482.6 | 506.4 | 480.9 | 476.4 | 472.2 | 459.2 | 462.9 | 446 | 417.8
2550.1 | 2410.1 | 525.4 | 482.6 | 506.4 | 480.9 | 476.5 | 472.2 | 459.2 | 463 | 446 | 417.9
2551.1 | 2411.1 | 525.4 | 482.6 | 506.4 | 481 | 476.5 | 472.3 | 459.2 | 462.9 | 446.1 | 418
2552.1 | 2412.1 | 525.4 | 482.6 | 506.4 | 481 | 476.5 | 472.3 | 459.3 | 463 | 446.1 | 418
2553.1 | 2413.1 | 525.4 | 482.6 | 506.4 | 481 | 476.5 | 472.3 | 459.3 | 463 | 446.1 | 418
2554.1 | 2414.1 | 525.5 | 482.6 | 506.3 | 481 | 476.6 | 472.4 | 459.3 | 463.1 | 446.1 | 418.1
2555.1 | 2415.1 | 525.5 | 482.6 | 506.4 | 481 | 476.6 | 472.4 | 459.3 | 463.1 | 446.2 | 418.1
2556.1 | 2416.1 | 525.5 | 482.6 | 506.4 | 481 | 476.6 | 472.4 | 459.4 | 463.1 | 446.3 | 418.1
2557.1 | 2417.1 | 525.4 | 482.7 | 506.4 | 481 | 476.7 | 472.4 | 459.4 | 463.1 | 446.2 | 418.1
2558.1 | 2418.1 | 525.5 | 482.7 | 506.4 | 481 | 476.7 | 472.5 | 459.4 | 463 | 446.2 | 418.2
2559.1 | 2419.1 | 525.5 | 482.7 | 506.4 | 481 | 476.7 | 472.5 | 459.5 | 463 | 446.3 | 418.1
2560.1 | 2420.1 | 525.5 | 482.7 | 506.4 | 481 | 476.7 | 472.5 | 459.5 | 463 | 446.3 | 418.2
2561.1 | 2421.1 | 525.5 | 482.7 | 506.4 | 481 | 476.9 | 472.6 | 459.5 | 463 | 446.3 | 418.3
2562.1 | 2422.1 | 525.5 | 482.7 | 506.4 | 481 | 476.9 | 472.6 | 459.5 | 463.1 | 446.3 | 418.3
2563.1 | 2423.1 | 525.5 | 482.7 | 506.4 | 481 | 476.9 | 472.6 | 459.6 | 463.2 | 446.4 | 418.3
2564.1 | 2424.1 | 525.5 | 482.7 | 506.4 | 481 | 476.9 | 472.7 | 459.6 | 463.3 | 446.4 | 418.3
2565.1 | 2425.1 | 525.5 | 482.7 | 506.4 | 481.1 | 477 | 472.7 | 459.6 | 463.3 | 446.5 | 418.4
2566.1 | 2426.1 | 525.5 | 482.7 | 506.5 | 481.1 | 476.9 | 472.7 | 459.7 | 463.3 | 446.6 | 418.3
2567.1 | 2427.1 | 525.5 | 482.7 | 506.5 | 481.1 | 477 | 472.7 | 459.7 | 463.3 | 446.6 | 418.4
2568.1 | 2428.1 | 525.5 | 482.8 | 506.5 | 481.1 | 477 | 472.8 | 459.7 | 463.3 | 446.6 | 418.5
2569.1 | 2429.1 | 525.5 | 482.8 | 506.5 | 481.1 | 477.1 | 472.8 | 459.7 | 463.3 | 446.5 | 418.5
2570.1 | 2430.1 | 525.5 | 482.8 | 506.5 | 481.1 | 477.1 | 472.8 | 459.8 | 463.3 | 446.6 | 418.5
2571.1 | 2431.1 | 525.5 | 482.8 | 506.5 | 481.1 | 477.1 | 472.9 | 459.8 | 463.3 | 446.6 | 418.5
2572.1 | 2432.1 | 525.5 | 482.8 | 506.5 | 481.1 | 477.2 | 472.9 | 459.8 | 463.3 | 446.6 | 418.6
2573.1 | 2433.1 | 525.6 | 482.8 | 506.5 | 481.2 | 477.2 | 472.9 | 459.9 | 463.3 | 446.6 | 418.5
2574.1 | 2434.1 | 525.6 | 482.8 | 506.5 | 481.2 | 477.2 | 473 | 459.9 | 463.3 | 446.6 | 418.6
2575.1 | 2435.1 | 525.6 | 482.9 | 506.5 | 481.2 | 477.3 | 473 | 459.9 | 463.4 | 446.7 | 418.7
2576.1 | 2436.1 | 525.6 | 482.9 | 506.5 | 481.2 | 477.3 | 473 | 460 | 463.4 | 446.7 | 418.7
2577.1 | 2437.1 | 525.6 | 482.8 | 506.6 | 481.2 | 477.3 | 473 | 460 | 463.5 | 446.8 | 418.7
2578.1 | 2438.1 | 525.6 | 482.9 | 506.5 | 481.2 | 477.4 | 473.1 | 460 | 463.5 | 446.8 | 418.8
2579.1 | 2439.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.5 | 473.1 | 460 | 463.5 | 446.8 | 418.8
2580.1 | 2440.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.4 | 473.1 | 460.1 | 463.5 | 446.8 | 418.7
2581.1 | 2441.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.4 | 473.2 | 460.1 | 463.5 | 446.8 | 418.7
2582.1 | 2442.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.5 | 473.2 | 460.1 | 463.5 | 446.7 | 418.8
2583.1 | 2443.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.5 | 473.2 | 460.2 | 463.5 | 446.7 | 418.8
2584.1 | 2444.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.4 | 473.2 | 460.2 | 463.5 | 446.7 | 418.7
2585.1 | 2445.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.6 | 473.3 | 460.2 | 463.6 | 446.6 | 418.9
2586.1 | 2446.1 | 525.6 | 482.9 | 506.6 | 481.2 | 477.7 | 473.3 | 460.2 | 463.6 | 446.6 | 418.9
2587.1 | 2447.1 | 525.7 | 483 | 506.6 | 481.3 | 477.6 | 473.3 | 460.3 | 463.6 | 446.6 | 418.9
2588.1 | 2448.1 | 525.7 | 483 | 506.6 | 481.3 | 477.6 | 473.4 | 460.3 | 463.6 | 446.6 | 418.9
2589.1 | 2449.1 | 525.7 | 483 | 506.5 | 481.3 | 477.7 | 473.4 | 460.3 | 463.7 | 446.6 | 419
2590.1 | 2450.1 | 525.7 | 483 | 506.6 | 481.3 | 477.7 | 473.4 | 460.4 | 463.8 | 446.7 | 419
2591.1 | 2451.1 | 525.7 | 482.9 | 506.7 | 481.3 | 477.7 | 473.4 | 460.4 | 463.9 | 446.7 | 418.9
2592.1 | 2452.1 | 525.7 | 483 | 506.7 | 481.3 | 477.8 | 473.5 | 460.4 | 463.9 | 446.6 | 419
2593.1 | 2453.1 | 525.7 | 483 | 506.7 | 481.3 | 477.8 | 473.5 | 460.5 | 463.9 | 446.6 | 419
2594.1 | 2454.1 | 525.6 | 483 | 506.7 | 481.3 | 477.7 | 473.5 | 460.5 | 464 | 446.7 | 419
2595.1 | 2455.1 | 525.6 | 483 | 506.8 | 481.3 | 477.9 | 473.6 | 460.5 | 464 | 446.7 | 419
2596.1 | 2456.1 | 525.6 | 483 | 506.7 | 481.4 | 477.9 | 473.6 | 460.5 | 464 | 446.7 | 419.2
2597.1 | 2457.1 | 525.6 | 483 | 506.7 | 481.3 | 478 | 473.6 | 460.6 | 464 | 446.8 | 419.2
2598.1 | 2458.1 | 525.6 | 483 | 506.8 | 481.4 | 477.9 | 473.6 | 460.6 | 464 | 446.8 | 419.1
2599.1 | 2459.1 | 525.6 | 483 | 506.7 | 481.4 | 478 | 473.7 | 460.6 | 464 | 446.8 | 419.2
2600.1 | 2460.1 | 525.6 | 483 | 506.7 | 481.4 | 478.1 | 473.7 | 460.7 | 464.1 | 446.8 | 419.3
2601.1 | 2461.1 | 525.6 | 483 | 506.8 | 481.4 | 478.1 | 473.7 | 460.7 | 464.1 | 446.8 | 419.2
2602.1 | 2462.1 | 525.6 | 483 | 506.7 | 481.4 | 478.2 | 473.8 | 460.7 | 464.1 | 446.8 | 419.3
2603.1 | 2463.1 | 525.6 | 483.1 | 506.7 | 481.4 | 478.2 | 473.8 | 460.7 | 464.1 | 446.8 | 419.4
2604.1 | 2464.1 | 525.6 | 483.1 | 506.7 | 481.4 | 478.3 | 473.9 | 460.8 | 464.1 | 446.8 | 419.4
2605.1 | 2465.1 | 525.6 | 483.1 | 506.8 | 481.4 | 478.2 | 473.9 | 460.8 | 464.2 | 446.8 | 419.3
2606.1 | 2466.1 | 525.6 | 483.1 | 506.8 | 481.4 | 478.4 | 473.9 | 460.8 | 464.2 | 446.7 | 419.4
2607.1 | 2467.1 | 525.6 | 483.1 | 506.7 | 481.5 | 478.3 | 473.9 | 460.9 | 464.2 | 446.7 | 419.4
2608.1 | 2468.1 | 525.6 | 483.1 | 506.8 | 481.5 | 478.2 | 474 | 460.9 | 464.2 | 446.8 | 419.4
2609.1 | 2469.1 | 525.6 | 483.1 | 506.8 | 481.4 | 478.3 | 474 | 460.9 | 464.3 | 446.8 | 419.4
2610.1 | 2470.1 | 525.6 | 483.1 | 506.8 | 481.5 | 478.4 | 474 | 461 | 464.4 | 446.8 | 419.4
2611.1 | 2471.1 | 525.7 | 483.1 | 506.8 | 481.5 | 478.2 | 474 | 461 | 464.4 | 446.8 | 419.4
2612.1 | 2472.1 | 525.6 | 483.1 | 506.9 | 481.5 | 478.4 | 474.1 | 461 | 464.5 | 446.8 | 419.3
2613.1 | 2473.1 | 525.6 | 483.2 | 506.8 | 481.5 | 478.5 | 474.1 | 461.1 | 464.5 | 446.8 | 419.4
2614.1 | 2474.1 | 525.7 | 483.2 | 506.8 | 481.5 | 478.5 | 474.2 | 461.1 | 464.5 | 446.8 | 419.5
2615.1 | 2475.1 | 525.7 | 483.2 | 506.8 | 481.5 | 478.5 | 474.2 | 461.1 | 464.5 | 446.8 | 419.4
2616.1 | 2476.1 | 525.7 | 483.2 | 506.9 | 481.5 | 478.5 | 474.2 | 461.2 | 464.6 | 446.8 | 419.5
2617.1 | 2477.1 | 525.7 | 483.2 | 506.8 | 481.5 | 478.6 | 474.2 | 461.2 | 464.6 | 446.8 | 419.6
2618.1 | 2478.1 | 525.7 | 483.2 | 506.9 | 481.5 | 478.7 | 474.3 | 461.2 | 464.6 | 446.9 | 419.6
2619.1 | 2479.1 | 525.7 | 483.2 | 506.9 | 481.6 | 478.6 | 474.3 | 461.2 | 464.7 | 446.9 | 419.5
2620.1 | 2480.1 | 525.7 | 483.2 | 506.9 | 481.6 | 478.8 | 474.3 | 461.3 | 464.8 | 447 | 419.6
2621.1 | 2481.1 | 525.7 | 483.2 | 507 | 481.5 | 478.8 | 474.3 | 461.3 | 464.8 | 447 | 419.6
2622.1 | 2482.1 | 525.6 | 483.2 | 507 | 481.6 | 478.7 | 474.4 | 461.3 | 464.8 | 447.1 | 419.6
2623.1 | 2483.1 | 525.6 | 483.2 | 506.9 | 481.6 | 478.7 | 474.4 | 461.4 | 464.8 | 447.1 | 419.6
2624.1 | 2484.1 | 525.6 | 483.2 | 507 | 481.6 | 478.8 | 474.4 | 461.4 | 464.9 | 447.1 | 419.6
2625.1 | 2485.1 | 525.6 | 483.3 | 506.9 | 481.6 | 478.8 | 474.5 | 461.4 | 464.9 | 447.1 | 419.7
2626.1 | 2486.1 | 525.6 | 483.3 | 506.9 | 481.6 | 478.8 | 474.5 | 461.5 | 464.9 | 447.1 | 419.7
2627.1 | 2487.1 | 525.6 | 483.3 | 506.9 | 481.6 | 479 | 474.5 | 461.5 | 464.8 | 447 | 419.8
2628.1 | 2488.1 | 525.6 | 483.3 | 506.9 | 481.6 | 479 | 474.6 | 461.5 | 464.8 | 447 | 419.8
2629.1 | 2489.1 | 525.6 | 483.3 | 506.9 | 481.6 | 479 | 474.6 | 461.6 | 464.9 | 447 | 419.8
2630.1 | 2490.1 | 525.6 | 483.3 | 506.9 | 481.7 | 479 | 474.6 | 461.6 | 464.9 | 447 | 419.8
2631.1 | 2491.1 | 525.6 | 483.3 | 506.9 | 481.7 | 479.1 | 474.7 | 461.6 | 464.9 | 447 | 419.9
2632.1 | 2492.1 | 525.6 | 483.4 | 506.9 | 481.7 | 479.1 | 474.7 | 461.6 | 465 | 447 | 419.9
2633.1 | 2493.1 | 525.6 | 483.2 | 507.1 | 481.6 | 478.8 | 474.6 | 461.7 | 465.1 | 447.1 | 419.6
2634.1 | 2494.1 | 525.5 | 483.1 | 507.5 | 481.5 | 478.3 | 474.5 | 461.8 | 465.1 | 447.2 | 419.1
2635.1 | 2495.1 | 525.5 | 483.1 | 507.5 | 481.5 | 478.4 | 474.5 | 461.8 | 465 | 447.2 | 419.1
2636.1 | 2496.1 | 525.5 | 483.1 | 507.5 | 481.5 | 478.4 | 474.6 | 461.8 | 465.1 | 447.2 | 419.1
2637.1 | 2497.1 | 525.5 | 483.1 | 507.5 | 481.5 | 478.4 | 474.6 | 461.9 | 465.1 | 447.3 | 419.2
2638.1 | 2498.1 | 525.6 | 483.1 | 507.5 | 481.6 | 478.5 | 474.6 | 461.9 | 465.2 | 447.3 | 419.2
2639.1 | 2499.1 | 525.6 | 483.1 | 507.5 | 481.5 | 478.5 | 474.6 | 461.9 | 465.3 | 447.3 | 419.2
2640.1 | 2500.1 | 525.6 | 483.1 | 507.5 | 481.6 | 478.5 | 474.7 | 462 | 465.4 | 447.3 | 419.2
2641.1 | 2501.1 | 525.6 | 483.1 | 507.5 | 481.6 | 478.5 | 474.7 | 462 | 465.4 | 447.3 | 419.3
2642.1 | 2502.1 | 525.6 | 483.2 | 507.5 | 481.6 | 478.6 | 474.7 | 462 | 465.5 | 447.4 | 419.4
2643.1 | 2503.1 | 525.6 | 483.2 | 507.5 | 481.6 | 478.6 | 474.8 | 462.1 | 465.5 | 447.4 | 419.4
2644.1 | 2504.1 | 525.6 | 483.2 | 507.5 | 481.6 | 478.6 | 474.8 | 462.1 | 465.5 | 447.4 | 419.4
2645.1 | 2505.1 | 525.5 | 483.2 | 507.5 | 481.6 | 478.7 | 474.8 | 462.1 | 465.5 | 447.5 | 419.5
2646.1 | 2506.1 | 525.5 | 483.2 | 507.6 | 481.6 | 478.7 | 474.9 | 462.1 | 465.5 | 447.5 | 419.5
2647.1 | 2507.1 | 525.5 | 483.2 | 507.6 | 481.6 | 478.7 | 474.9 | 462.2 | 465.5 | 447.5 | 419.5
2648.1 | 2508.1 | 525.5 | 483.2 | 507.5 | 481.7 | 478.8 | 474.9 | 462.2 | 465.6 | 447.6 | 419.6
2649.1 | 2509.1 | 525.5 | 483.2 | 507.5 | 481.7 | 478.8 | 475 | 462.2 | 465.6 | 447.6 | 419.6
2650.1 | 2510.1 | 525.5 | 483.2 | 507.6 | 481.7 | 478.8 | 475 | 462.3 | 465.6 | 447.6 | 419.6
2651.1 | 2511.1 | 525.5 | 483.2 | 507.6 | 481.7 | 478.9 | 475 | 462.3 | 465.7 | 447.7 | 419.7
2652.1 | 2512.1 | 525.6 | 483.3 | 507.6 | 481.7 | 478.9 | 475 | 462.3 | 465.7 | 447.7 | 419.7
2653.1 | 2513.1 | 525.6 | 483.3 | 507.6 | 481.7 | 479 | 475.1 | 462.4 | 465.7 | 447.8 | 419.7
2654.1 | 2514.1 | 525.6 | 483.3 | 507.6 | 481.7 | 479 | 475.1 | 462.4 | 465.8 | 447.8 | 419.7
2655.1 | 2515.1 | 525.5 | 483.3 | 507.6 | 481.7 | 479 | 475.1 | 462.4 | 465.7 | 447.8 | 419.8
2656.1 | 2516.1 | 525.5 | 483.3 | 507.6 | 481.7 | 479.1 | 475.2 | 462.5 | 465.7 | 447.8 | 419.8
2657.1 | 2517.1 | 525.5 | 483.3 | 507.6 | 481.7 | 479.1 | 475.2 | 462.5 | 465.8 | 447.8 | 419.8
2658.1 | 2518.1 | 525.6 | 483.3 | 507.6 | 481.7 | 479.1 | 475.2 | 462.5 | 465.8 | 447.8 | 419.9
2659.1 | 2519.1 | 525.6 | 483.3 | 507.6 | 481.7 | 479.1 | 475.3 | 462.6 | 465.9 | 447.8 | 420
2660.1 | 2520.1 | 525.6 | 483.3 | 507.6 | 481.7 | 479.2 | 475.3 | 462.6 | 465.9 | 447.8 | 420
2661.1 | 2521.1 | 525.7 | 483.3 | 507.7 | 481.7 | 479.1 | 475.3 | 462.6 | 465.9 | 447.8 | 419.9
2662.1 | 2522.1 | 525.7 | 483.3 | 507.6 | 481.7 | 479.2 | 475.3 | 462.6 | 465.9 | 447.8 | 420
2663.1 | 2523.1 | 525.7 | 483.4 | 507.7 | 481.7 | 479.3 | 475.4 | 462.7 | 465.9 | 447.9 | 420
2664.1 | 2524.1 | 525.7 | 483.4 | 507.7 | 481.7 | 479.3 | 475.4 | 462.7 | 465.9 | 447.9 | 420
2665.1 | 2525.1 | 525.7 | 483.4 | 507.7 | 481.8 | 479.3 | 475.4 | 462.7 | 465.8 | 447.9 | 420
2666.1 | 2526.1 | 525.7 | 483.4 | 507.7 | 481.8 | 479.4 | 475.5 | 462.8 | 465.8 | 447.9 | 420.1
2667.1 | 2527.1 | 525.6 | 483.4 | 507.7 | 481.8 | 479.4 | 475.5 | 462.8 | 465.8 | 448 | 420.1
2668.1 | 2528.1 | 525.6 | 483.4 | 507.8 | 481.8 | 479.4 | 475.5 | 462.8 | 465.9 | 448 | 420.1
2669.1 | 2529.1 | 525.6 | 483.4 | 507.7 | 481.8 | 479.5 | 475.5 | 462.9 | 465.9 | 448 | 420.2
2670.1 | 2530.1 | 525.5 | 483.5 | 507.7 | 481.8 | 479.4 | 475.6 | 462.9 | 465.9 | 448 | 420.3
2671.1 | 2531.1 | 525.5 | 483.4 | 507.7 | 481.8 | 479.5 | 475.6 | 462.9 | 465.9 | 448.1 | 420.3
2672.1 | 2532.1 | 525.5 | 483.4 | 507.7 | 481.8 | 479.5 | 475.6 | 463 | 466 | 448.1 | 420.2
2673.1 | 2533.1 | 525.5 | 483.5 | 507.7 | 481.8 | 479.6 | 475.7 | 463 | 466 | 448.1 | 420.3
2674.1 | 2534.1 | 525.5 | 483.5 | 507.7 | 481.8 | 479.6 | 475.7 | 463 | 466.1 | 448.1 | 420.4
2675.1 | 2535.1 | 525.5 | 483.5 | 507.8 | 481.8 | 479.6 | 475.7 | 463.1 | 466.1 | 448.2 | 420.3
2676.1 | 2536.1 | 525.5 | 483.5 | 507.7 | 481.8 | 479.7 | 475.8 | 463.1 | 466.1 | 448.2 | 420.4
2677.1 | 2537.1 | 525.5 | 483.5 | 507.7 | 481.8 | 479.8 | 475.8 | 463.1 | 466.1 | 448.2 | 420.4
2678.1 | 2538.1 | 525.5 | 483.5 | 507.7 | 481.8 | 479.7 | 475.8 | 463.2 | 466.1 | 448.2 | 420.4
2679.1 | 2539.1 | 525.6 | 483.5 | 507.7 | 481.8 | 479.8 | 475.9 | 463.2 | 466 | 448.2 | 420.5
2680.1 | 2540.1 | 525.6 | 483.5 | 507.7 | 481.9 | 479.8 | 475.9 | 463.2 | 466.1 | 448.3 | 420.5
2681.1 | 2541.1 | 525.6 | 483.5 | 507.7 | 481.9 | 479.8 | 475.9 | 463.3 | 466.2 | 448.3 | 420.5
2682.1 | 2542.1 | 525.6 | 483.5 | 507.8 | 481.8 | 479.8 | 475.9 | 463.3 | 466.3 | 448.3 | 420.5
2683.1 | 2543.1 | 525.7 | 483.5 | 507.8 | 481.9 | 479.9 | 476 | 463.3 | 466.3 | 448.3 | 420.6
2684.1 | 2544.1 | 525.6 | 483.5 | 507.8 | 481.9 | 479.9 | 476 | 463.4 | 466.4 | 448.3 | 420.6
2685.1 | 2545.1 | 525.6 | 483.5 | 507.8 | 481.9 | 480 | 476 | 463.4 | 466.4 | 448.3 | 420.6
2686.1 | 2546.1 | 525.6 | 483.6 | 507.8 | 481.9 | 480 | 476.1 | 463.4 | 466.4 | 448.3 | 420.6
2687.1 | 2547.1 | 525.6 | 483.6 | 507.8 | 481.9 | 480.1 | 476.1 | 463.5 | 466.5 | 448.4 | 420.7
2688.1 | 2548.1 | 525.6 | 483.6 | 507.8 | 481.9 | 480.1 | 476.1 | 463.5 | 466.5 | 448.4 | 420.7
2689.1 | 2549.1 | 525.6 | 483.6 | 507.8 | 481.9 | 480 | 476.2 | 463.5 | 466.5 | 448.4 | 420.6
2690.1 | 2550.1 | 525.6 | 483.6 | 507.8 | 481.9 | 480.1 | 476.2 | 463.6 | 466.6 | 448.4 | 420.6
2691.1 | 2551.1 | 525.6 | 483.6 | 507.8 | 481.9 | 480.2 | 476.2 | 463.6 | 466.6 | 448.4 | 420.7
2692.1 | 2552.1 | 525.6 | 483.6 | 507.8 | 482 | 480.2 | 476.3 | 463.6 | 466.7 | 448.4 | 420.6
2693.1 | 2553.1 | 525.6 | 483.6 | 507.9 | 482 | 480.2 | 476.3 | 463.7 | 466.7 | 448.4 | 420.6
2694.1 | 2554.1 | 525.6 | 483.6 | 507.9 | 482 | 480.3 | 476.3 | 463.7 | 466.8 | 448.4 | 420.7
2695.1 | 2555.1 | 525.7 | 483.7 | 507.9 | 482 | 480.3 | 476.4 | 463.7 | 466.8 | 448.4 | 420.7
2696.1 | 2556.1 | 525.7 | 483.7 | 507.9 | 482 | 480.2 | 476.4 | 463.8 | 466.7 | 448.4 | 420.7
2697.1 | 2557.1 | 525.7 | 483.7 | 507.9 | 482 | 480.4 | 476.4 | 463.8 | 466.7 | 448.4 | 420.7
2698.1 | 2558.1 | 525.7 | 483.7 | 507.9 | 482 | 480.4 | 476.5 | 463.8 | 466.8 | 448.5 | 420.7
2699.1 | 2559.1 | 525.6 | 483.7 | 507.9 | 482 | 480.4 | 476.5 | 463.9 | 466.8 | 448.5 | 420.7
2700.1 | 2560.1 | 525.6 | 483.7 | 507.9 | 482 | 480.4 | 476.5 | 463.9 | 466.8 | 448.5 | 420.7
2701.1 | 2561.1 | 525.6 | 483.7 | 507.9 | 482 | 480.5 | 476.6 | 463.9 | 466.8 | 448.5 | 420.8
2702.1 | 2562.1 | 525.6 | 483.7 | 507.9 | 482 | 480.5 | 476.6 | 464 | 466.8 | 448.5 | 420.8
2703.1 | 2563.1 | 525.6 | 483.7 | 507.9 | 482 | 480.5 | 476.6 | 464 | 466.9 | 448.5 | 420.8
2704.1 | 2564.1 | 525.6 | 483.7 | 507.9 | 482 | 480.6 | 476.7 | 464 | 466.9 | 448.5 | 420.8
2705.1 | 2565.1 | 525.6 | 483.7 | 507.9 | 482.1 | 480.6 | 476.7 | 464.1 | 466.9 | 448.5 | 420.9
2706.1 | 2566.1 | 525.5 | 483.7 | 507.9 | 482.1 | 480.6 | 476.7 | 464.1 | 466.9 | 448.5 | 420.9
2707.1 | 2567.1 | 525.5 | 483.7 | 507.9 | 482.1 | 480.7 | 476.8 | 464.1 | 467 | 448.5 | 420.8
2708.1 | 2568.1 | 525.5 | 483.8 | 507.9 | 482.1 | 480.7 | 476.8 | 464.2 | 467 | 448.6 | 420.9
2709.1 | 2569.1 | 525.5 | 483.8 | 507.9 | 482.1 | 480.8 | 476.8 | 464.2 | 467 | 448.7 | 420.9
2710.1 | 2570.1 | 525.5 | 483.7 | 508 | 482.1 | 480.7 | 476.9 | 464.3 | 467 | 448.8 | 420.9
2711.1 | 2571.1 | 525.5 | 483.8 | 508 | 482.1 | 480.8 | 476.9 | 464.3 | 467 | 448.8 | 421
2712.1 | 2572.1 | 525.6 | 483.8 | 508 | 482.1 | 480.8 | 476.9 | 464.3 | 467 | 448.8 | 421
2713.1 | 2573.1 | 525.5 | 483.8 | 508 | 482.1 | 480.9 | 477 | 464.4 | 467.1 | 448.8 | 421
2714.1 | 2574.1 | 525.5 | 483.8 | 507.9 | 482.1 | 480.8 | 477 | 464.4 | 467.2 | 448.8 | 421
2715.1 | 2575.1 | 525.5 | 483.8 | 508 | 482.1 | 481 | 477 | 464.4 | 467.1 | 448.7 | 421
2716.1 | 2576.1 | 525.6 | 483.8 | 508 | 482.1 | 480.9 | 477.1 | 464.5 | 467.2 | 448.7 | 421
2717.1 | 2577.1 | 525.6 | 483.8 | 508 | 482.1 | 480.9 | 477.1 | 464.5 | 467.3 | 448.7 | 421
2718.1 | 2578.1 | 525.7 | 483.8 | 508 | 482.1 | 481 | 477.1 | 464.5 | 467.3 | 448.7 | 421.1
2719.1 | 2579.1 | 525.7 | 483.8 | 507.9 | 482.2 | 481 | 477.1 | 464.6 | 467.3 | 448.7 | 421.1
2720.1 | 2580.1 | 525.7 | 483.8 | 508 | 482.2 | 481 | 477.2 | 464.6 | 467.4 | 448.7 | 421.1
2721.1 | 2581.1 | 525.7 | 483.8 | 508 | 482.2 | 481.1 | 477.2 | 464.6 | 467.5 | 448.7 | 421.1
2722.1 | 2582.1 | 525.7 | 483.9 | 508 | 482.2 | 481.1 | 477.2 | 464.7 | 467.5 | 448.7 | 421.2
2723.1 | 2583.1 | 525.7 | 483.9 | 508.1 | 482.2 | 481.1 | 477.3 | 464.7 | 467.5 | 448.7 | 421.1
2724.1 | 2584.1 | 525.7 | 483.9 | 508.1 | 482.2 | 481.1 | 477.3 | 464.7 | 467.6 | 448.8 | 421.1
2725.1 | 2585.1 | 525.7 | 483.9 | 508.1 | 482.2 | 481.2 | 477.3 | 464.8 | 467.6 | 448.8 | 421.2
2726.1 | 2586.1 | 525.7 | 483.9 | 508.1 | 482.2 | 481.3 | 477.4 | 464.8 | 467.6 | 448.8 | 421.2
2727.1 | 2587.1 | 525.7 | 483.9 | 508.1 | 482.2 | 481.3 | 477.4 | 464.8 | 467.6 | 448.9 | 421.2
2728.1 | 2588.1 | 525.7 | 483.9 | 508.1 | 482.2 | 481.3 | 477.4 | 464.9 | 467.7 | 448.9 | 421.2
2729.1 | 2589.1 | 525.6 | 483.9 | 508.1 | 482.3 | 481.4 | 477.5 | 464.9 | 467.8 | 448.9 | 421.3
2730.1 | 2590.1 | 525.6 | 483.9 | 508.1 | 482.3 | 481.4 | 477.5 | 465 | 467.7 | 449 | 421.3
2731.1 | 2591.1 | 525.6 | 483.9 | 508.2 | 482.3 | 481.4 | 477.5 | 465 | 467.8 | 449.1 | 421.3
2732.1 | 2592.1 | 525.7 | 484 | 508.2 | 482.3 | 481.4 | 477.5 | 465 | 467.7 | 449.1 | 421.3
2733.1 | 2593.1 | 525.7 | 484 | 508.2 | 482.3 | 481.5 | 477.6 | 465.1 | 467.7 | 449.1 | 421.3
2734.1 | 2594.1 | 525.7 | 484 | 508.2 | 482.2 | 481.5 | 477.6 | 465.1 | 467.8 | 449.1 | 421.3
2735.1 | 2595.1 | 525.7 | 484 | 508.2 | 482.3 | 481.4 | 477.6 | 465.1 | 467.8 | 449.1 | 421.4
2736.1 | 2596.1 | 525.6 | 484 | 508.2 | 482.3 | 481.6 | 477.7 | 465.2 | 467.8 | 449.1 | 421.4
2737.1 | 2597.1 | 525.6 | 484 | 508.1 | 482.3 | 481.6 | 477.7 | 465.2 | 467.8 | 449.1 | 421.4
2738.1 | 2598.1 | 525.6 | 484 | 508.2 | 482.3 | 481.5 | 477.7 | 465.2 | 467.8 | 449.2 | 421.4
2739.1 | 2599.1 | 525.6 | 484 | 508.2 | 482.3 | 481.6 | 477.8 | 465.3 | 467.9 | 449.2 | 421.5
2740.1 | 2600.1 | 525.6 | 484 | 508.2 | 482.3 | 481.7 | 477.8 | 465.3 | 467.9 | 449.2 | 421.5
2741.1 | 2601.1 | 525.6 | 484 | 508.2 | 482.3 | 481.7 | 477.8 | 465.4 | 467.9 | 449.2 | 421.5
2742.1 | 2602.1 | 525.6 | 484 | 508.2 | 482.3 | 481.7 | 477.9 | 465.4 | 467.9 | 449.2 | 421.5
2743.1 | 2603.1 | 525.5 | 484.1 | 508.2 | 482.3 | 481.8 | 477.9 | 465.4 | 467.9 | 449.3 | 421.6
2744.1 | 2604.1 | 525.5 | 484.1 | 508.3 | 482.3 | 481.9 | 477.9 | 465.5 | 467.8 | 449.3 | 421.6
2745.1 | 2605.1 | 525.5 | 484.1 | 508.3 | 482.4 | 481.8 | 478 | 465.5 | 467.8 | 449.4 | 421.6
2746.1 | 2606.1 | 525.5 | 484.1 | 508.3 | 482.3 | 481.9 | 478 | 465.6 | 467.9 | 449.4 | 421.6
2747.1 | 2607.1 | 525.5 | 484.1 | 508.3 | 482.4 | 481.8 | 478.1 | 465.6 | 468 | 449.4 | 421.7
2748.1 | 2608.1 | 525.5 | 484.1 | 508.3 | 482.4 | 481.9 | 478.1 | 465.6 | 468 | 449.4 | 421.6
2749.1 | 2609.1 | 525.5 | 484.1 | 508.3 | 482.4 | 481.9 | 478.1 | 465.7 | 468 | 449.4 | 421.7
2750.1 | 2610.1 | 525.4 | 484.1 | 508.3 | 482.4 | 482 | 478.1 | 465.7 | 468.1 | 449.3 | 421.7
2751.1 | 2611.1 | 525.5 | 484.1 | 508.2 | 482.4 | 482 | 478.2 | 465.7 | 468.1 | 449.3 | 421.7
2752.1 | 2612.1 | 525.5 | 484.1 | 508.2 | 482.4 | 482 | 478.2 | 465.8 | 468.1 | 449.3 | 421.7
2753.1 | 2613.1 | 525.5 | 484.1 | 508.2 | 482.4 | 482.1 | 478.2 | 465.8 | 468.1 | 449.3 | 421.8
2754.1 | 2614.1 | 525.4 | 484.1 | 508.2 | 482.4 | 482.2 | 478.3 | 465.8 | 468.2 | 449.3 | 421.8
2755.1 | 2615.1 | 525.4 | 484.2 | 508.2 | 482.4 | 482.1 | 478.3 | 465.9 | 468.2 | 449.4 | 421.8
2756.1 | 2616.1 | 525.4 | 484.1 | 508.2 | 482.4 | 482.1 | 478.3 | 465.9 | 468.2 | 449.4 | 421.8
2757.1 | 2617.1 | 525.4 | 484.2 | 508.2 | 482.4 | 482.2 | 478.4 | 465.9 | 468.2 | 449.4 | 421.9
2758.1 | 2618.1 | 525.5 | 484.2 | 508.2 | 482.4 | 482.3 | 478.4 | 466 | 468.2 | 449.5 | 421.9
2759.1 | 2619.1 | 525.5 | 484.1 | 508.2 | 482.4 | 482.3 | 478.4 | 466 | 468.3 | 449.5 | 421.9
2760.1 | 2620.1 | 525.5 | 484.2 | 508.2 | 482.4 | 482.3 | 478.5 | 466.1 | 468.3 | 449.5 | 421.9
2761.1 | 2621.1 | 525.6 | 484.2 | 508.3 | 482.4 | 482.4 | 478.5 | 466.1 | 468.3 | 449.5 | 421.9
2762.1 | 2622.1 | 525.6 | 484.2 | 508.3 | 482.4 | 482.3 | 478.5 | 466.1 | 468.3 | 449.5 | 421.9
2763.1 | 2623.1 | 525.6 | 484.1 | 508.3 | 482.4 | 482.4 | 478.5 | 466.2 | 468.4 | 449.5 | 421.9
2764.1 | 2624.1 | 525.7 | 484.2 | 508.3 | 482.4 | 482.4 | 478.6 | 466.2 | 468.3 | 449.5 | 422
2765.1 | 2625.1 | 525.7 | 484.2 | 508.3 | 482.4 | 482.4 | 478.6 | 466.2 | 468.4 | 449.6 | 422
2766.1 | 2626.1 | 525.7 | 484.2 | 508.3 | 482.4 | 482.5 | 478.6 | 466.3 | 468.4 | 449.6 | 422
2767.1 | 2627.1 | 525.8 | 484.2 | 508.3 | 482.4 | 482.5 | 478.7 | 466.3 | 468.5 | 449.6 | 422
2768.1 | 2628.1 | 525.8 | 484.2 | 508.3 | 482.4 | 482.6 | 478.7 | 466.4 | 468.5 | 449.6 | 422.1
2769.1 | 2629.1 | 525.8 | 484.2 | 508.4 | 482.4 | 482.6 | 478.7 | 466.4 | 468.5 | 449.6 | 422
2770.1 | 2630.1 | 525.8 | 484.2 | 508.4 | 482.4 | 482.6 | 478.8 | 466.4 | 468.5 | 449.7 | 422
2771.1 | 2631.1 | 525.8 | 484.2 | 508.4 | 482.5 | 482.6 | 478.8 | 466.5 | 468.6 | 449.7 | 422.1
2772.1 | 2632.1 | 525.8 | 484.2 | 508.3 | 482.5 | 482.6 | 478.8 | 466.5 | 468.6 | 449.7 | 422.1
2773.1 | 2633.1 | 525.8 | 484.2 | 508.4 | 482.5 | 482.6 | 478.9 | 466.5 | 468.6 | 449.8 | 422.1
2774.1 | 2634.1 | 525.8 | 484.2 | 508.4 | 482.5 | 482.7 | 478.9 | 466.6 | 468.6 | 449.8 | 422.1
2775.1 | 2635.1 | 525.8 | 484.2 | 508.4 | 482.5 | 482.8 | 478.9 | 466.6 | 468.7 | 449.9 | 422.2
2776.1 | 2636.1 | 525.9 | 484.3 | 508.4 | 482.5 | 482.7 | 479 | 466.7 | 468.8 | 449.9 | 422.2
2777.1 | 2637.1 | 525.8 | 484.2 | 508.4 | 482.5 | 482.7 | 479 | 466.7 | 468.8 | 449.9 | 422.2
2778.1 | 2638.1 | 525.8 | 484.3 | 508.4 | 482.5 | 482.8 | 479 | 466.7 | 468.8 | 449.9 | 422.2
2779.1 | 2639.1 | 525.8 | 484.3 | 508.4 | 482.5 | 482.9 | 479.1 | 466.7 | 468.8 | 449.9 | 422.2
2780.1 | 2640.1 | 525.7 | 484.3 | 508.4 | 482.5 | 482.9 | 479.1 | 466.8 | 468.9 | 449.9 | 422.3
2781.1 | 2641.1 | 525.8 | 484.3 | 508.4 | 482.5 | 482.9 | 479.1 | 466.8 | 468.9 | 449.9 | 422.3
2782.1 | 2642.1 | 525.8 | 484.3 | 508.4 | 482.6 | 483 | 479.2 | 466.9 | 468.9 | 449.9 | 422.3
2783.1 | 2643.1 | 525.8 | 484.3 | 508.4 | 482.6 | 483 | 479.2 | 466.9 | 468.9 | 450 | 422.3
2784.1 | 2644.1 | 525.8 | 484.3 | 508.4 | 482.5 | 483 | 479.2 | 467 | 469 | 450 | 422.3
2785.1 | 2645.1 | 525.8 | 484.3 | 508.4 | 482.6 | 483.1 | 479.3 | 467 | 469 | 450.1 | 422.4
2786.1 | 2646.1 | 525.7 | 484.4 | 508.4 | 482.6 | 483.1 | 479.3 | 467 | 469.1 | 450.2 | 422.4
2787.1 | 2647.1 | 525.7 | 484.4 | 508.4 | 482.6 | 483.1 | 479.3 | 467.1 | 469.1 | 450.3 | 422.4
2788.1 | 2648.1 | 525.7 | 484.4 | 508.4 | 482.6 | 483.2 | 479.4 | 467.1 | 469.1 | 450.3 | 422.5
2789.1 | 2649.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.2 | 479.4 | 467.1 | 469.1 | 450.3 | 422.5
2790.1 | 2650.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.2 | 479.4 | 467.2 | 469.2 | 450.3 | 422.5
2791.1 | 2651.1 | 525.8 | 484.4 | 508.4 | 482.6 | 483.3 | 479.5 | 467.2 | 469.3 | 450.3 | 422.5
2792.1 | 2652.1 | 525.8 | 484.4 | 508.4 | 482.6 | 483.3 | 479.5 | 467.2 | 469.3 | 450.3 | 422.6
2793.1 | 2653.1 | 525.8 | 484.4 | 508.4 | 482.6 | 483.3 | 479.5 | 467.3 | 469.3 | 450.3 | 422.5
2794.1 | 2654.1 | 525.8 | 484.4 | 508.4 | 482.6 | 483.3 | 479.6 | 467.3 | 469.4 | 450.3 | 422.5
2795.1 | 2655.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.4 | 479.6 | 467.4 | 469.4 | 450.3 | 422.5
2796.1 | 2656.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.4 | 479.6 | 467.4 | 469.4 | 450.3 | 422.6
2797.1 | 2657.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.5 | 479.7 | 467.4 | 469.4 | 450.3 | 422.6
2798.1 | 2658.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.4 | 479.7 | 467.5 | 469.5 | 450.2 | 422.6
2799.1 | 2659.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.5 | 479.7 | 467.5 | 469.5 | 450.2 | 422.6
2800.1 | 2660.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.5 | 479.8 | 467.6 | 469.6 | 450.3 | 422.6
2801.1 | 2661.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.6 | 479.8 | 467.6 | 469.7 | 450.3 | 422.7
2802.1 | 2662.1 | 525.8 | 484.4 | 508.5 | 482.6 | 483.6 | 479.8 | 467.6 | 469.7 | 450.3 | 422.7
2803.1 | 2663.1 | 525.8 | 484.5 | 508.5 | 482.6 | 483.7 | 479.9 | 467.7 | 469.7 | 450.3 | 422.7
2804.1 | 2664.1 | 525.8 | 484.4 | 508.6 | 482.7 | 483.6 | 479.9 | 467.7 | 469.7 | 450.3 | 422.7
2805.1 | 2665.1 | 525.8 | 484.4 | 508.6 | 482.7 | 483.6 | 479.9 | 467.7 | 469.7 | 450.4 | 422.7
2806.1 | 2666.1 | 525.8 | 484.5 | 508.5 | 482.7 | 483.7 | 480 | 467.8 | 469.7 | 450.4 | 422.8
2807.1 | 2667.1 | 525.8 | 484.5 | 508.6 | 482.7 | 483.8 | 480 | 467.8 | 469.8 | 450.4 | 422.8
2808.1 | 2668.1 | 525.8 | 484.5 | 508.6 | 482.7 | 483.7 | 480 | 467.9 | 469.8 | 450.5 | 422.8
2809.1 | 2669.1 | 525.8 | 484.5 | 508.5 | 482.7 | 483.8 | 480 | 467.9 | 469.9 | 450.5 | 422.8
2810.1 | 2670.1 | 525.8 | 484.5 | 508.5 | 482.7 | 483.9 | 480.1 | 467.9 | 469.9 | 450.5 | 422.8
2811.1 | 2671.1 | 525.8 | 484.5 | 508.6 | 482.7 | 483.8 | 480.1 | 468 | 470 | 450.6 | 422.8
2812.1 | 2672.1 | 525.8 | 484.5 | 508.5 | 482.7 | 483.9 | 480.1 | 468 | 470 | 450.6 | 422.9
2813.1 | 2673.1 | 525.8 | 484.5 | 508.5 | 482.7 | 483.9 | 480.2 | 468 | 470 | 450.6 | 422.9
2814.1 | 2674.1 | 525.8 | 484.5 | 508.5 | 482.7 | 483.9 | 480.2 | 468.1 | 470.1 | 450.6 | 422.9
2815.1 | 2675.1 | 525.8 | 484.5 | 508.5 | 482.7 | 484 | 480.2 | 468.1 | 470.1 | 450.6 | 422.9
2816.1 | 2676.1 | 525.8 | 484.6 | 508.5 | 482.7 | 484 | 480.3 | 468.2 | 470.1 | 450.7 | 423
2817.1 | 2677.1 | 525.8 | 484.6 | 508.5 | 482.7 | 484.1 | 480.3 | 468.2 | 470.2 | 450.7 | 423
2818.1 | 2678.1 | 525.8 | 484.6 | 508.6 | 482.7 | 484 | 480.3 | 468.3 | 470.2 | 450.7 | 423
2819.1 | 2679.1 | 525.8 | 484.6 | 508.6 | 482.7 | 484.1 | 480.4 | 468.3 | 470.3 | 450.7 | 423.1
2820.1 | 2680.1 | 525.8 | 484.6 | 508.6 | 482.7 | 484.1 | 480.4 | 468.3 | 470.3 | 450.7 | 423.1
2821.1 | 2681.1 | 525.8 | 484.6 | 508.6 | 482.7 | 484.2 | 480.4 | 468.4 | 470.3 | 450.8 | 423.2
2822.1 | 2682.1 | 525.8 | 484.6 | 508.7 | 482.7 | 484.2 | 480.4 | 468.4 | 470.4 | 450.8 | 423.1
2823.1 | 2683.1 | 525.8 | 484.6 | 508.6 | 482.7 | 484.2 | 480.5 | 468.4 | 470.4 | 450.8 | 423.2
2824.1 | 2684.1 | 525.8 | 484.6 | 508.6 | 482.7 | 484.3 | 480.5 | 468.5 | 470.5 | 450.9 | 423.2
2825.1 | 2685.1 | 525.8 | 484.6 | 508.6 | 482.7 | 484.3 | 480.5 | 468.5 | 470.4 | 450.9 | 423.2
2826.1 | 2686.1 | 525.8 | 484.6 | 508.7 | 482.7 | 484.3 | 480.6 | 468.6 | 470.4 | 450.9 | 423.2
2827.1 | 2687.1 | 525.8 | 484.6 | 508.6 | 482.8 | 484.4 | 480.6 | 468.6 | 470.5 | 450.9 | 423.3
2828.1 | 2688.1 | 525.8 | 484.7 | 508.6 | 482.8 | 484.4 | 480.7 | 468.6 | 470.4 | 451 | 423.3
2829.1 | 2689.1 | 525.9 | 484.6 | 508.7 | 482.8 | 484.4 | 480.7 | 468.7 | 470.5 | 451 | 423.3
2830.1 | 2690.1 | 525.9 | 484.6 | 508.7 | 482.8 | 484.4 | 480.7 | 468.7 | 470.5 | 451 | 423.3
2831.1 | 2691.1 | 525.9 | 484.7 | 508.7 | 482.8 | 484.4 | 480.7 | 468.8 | 470.6 | 451.1 | 423.3
2832.1 | 2692.1 | 525.9 | 484.7 | 508.7 | 482.8 | 484.5 | 480.8 | 468.8 | 470.7 | 451.1 | 423.3
2833.1 | 2693.1 | 525.9 | 484.7 | 508.7 | 482.8 | 484.4 | 480.8 | 468.8 | 470.7 | 451.1 | 423.3
2834.1 | 2694.1 | 525.9 | 484.7 | 508.6 | 482.8 | 484.5 | 480.8 | 468.9 | 470.7 | 451.1 | 423.4
2835.1 | 2695.1 | 525.8 | 484.7 | 508.7 | 482.8 | 484.6 | 480.9 | 468.9 | 470.7 | 451.2 | 423.4
2836.1 | 2696.1 | 525.9 | 484.7 | 508.8 | 482.8 | 484.5 | 480.9 | 469 | 470.7 | 451.2 | 423.3
2837.1 | 2697.1 | 525.9 | 484.7 | 508.7 | 482.8 | 484.6 | 480.9 | 469 | 470.8 | 451.2 | 423.4
2838.1 | 2698.1 | 525.9 | 484.7 | 508.8 | 482.8 | 484.7 | 481 | 469 | 470.8 | 451.2 | 423.4
2839.1 | 2699.1 | 525.9 | 484.8 | 508.7 | 482.9 | 484.7 | 481 | 469.1 | 470.9 | 451.3 | 423.4
2840.1 | 2700.1 | 525.9 | 484.7 | 508.8 | 482.8 | 484.7 | 481 | 469.1 | 471 | 451.3 | 423.4
2841.1 | 2701.1 | 525.9 | 484.8 | 508.8 | 482.8 | 484.7 | 481 | 469.2 | 471 | 451.3 | 423.4
2842.1 | 2702.1 | 525.9 | 484.6 | 509 | 482.8 | 484.4 | 481 | 469.2 | 471.1 | 451.4 | 423.1
2843.1 | 2703.1 | 525.9 | 484.6 | 509 | 482.8 | 484.4 | 481 | 469.3 | 471.1 | 451.4 | 423.1
2844.1 | 2704.1 | 525.8 | 484.6 | 509 | 482.8 | 484.4 | 481 | 469.3 | 471.2 | 451.4 | 423.1
2845.1 | 2705.1 | 525.8 | 484.7 | 509 | 482.8 | 484.5 | 481.1 | 469.3 | 471.1 | 451.5 | 423.2
2846.1 | 2706.1 | 525.8 | 484.6 | 509 | 482.8 | 484.5 | 481.1 | 469.4 | 471.2 | 451.5 | 423.1
2847.1 | 2707.1 | 525.8 | 484.7 | 509 | 482.8 | 484.5 | 481.1 | 469.4 | 471.2 | 451.5 | 423.2
2848.1 | 2708.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.6 | 481.2 | 469.5 | 471.3 | 451.6 | 423.2
2849.1 | 2709.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.6 | 481.2 | 469.5 | 471.3 | 451.6 | 423.2
2850.1 | 2710.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.6 | 481.2 | 469.6 | 471.4 | 451.6 | 423.2
2851.1 | 2711.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.7 | 481.3 | 469.6 | 471.4 | 451.6 | 423.3
2852.1 | 2712.1 | 525.8 | 484.7 | 509 | 482.8 | 484.7 | 481.3 | 469.6 | 471.4 | 451.6 | 423.3
2853.1 | 2713.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.7 | 481.3 | 469.7 | 471.5 | 451.6 | 423.2
2854.1 | 2714.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.7 | 481.4 | 469.7 | 471.6 | 451.7 | 423.3
2855.1 | 2715.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.8 | 481.4 | 469.8 | 471.6 | 451.7 | 423.3
2856.1 | 2716.1 | 525.8 | 484.8 | 509.1 | 482.9 | 484.8 | 481.5 | 469.8 | 471.6 | 451.7 | 423.4
2857.1 | 2717.1 | 525.8 | 484.7 | 509.1 | 482.8 | 484.8 | 481.5 | 469.9 | 471.6 | 451.7 | 423.3
2858.1 | 2718.1 | 525.8 | 484.8 | 509.1 | 482.9 | 484.9 | 481.5 | 469.9 | 471.7 | 451.7 | 423.3
2859.1 | 2719.1 | 525.8 | 484.8 | 509.1 | 482.9 | 484.9 | 481.6 | 469.9 | 471.8 | 451.8 | 423.4
2860.1 | 2720.1 | 525.8 | 484.8 | 509.1 | 482.9 | 484.9 | 481.6 | 470 | 471.8 | 451.8 | 423.3
2861.1 | 2721.1 | 525.8 | 484.8 | 509.1 | 482.9 | 484.9 | 481.6 | 470 | 471.7 | 451.8 | 423.4
2862.1 | 2722.1 | 525.8 | 484.8 | 509.1 | 482.9 | 485 | 481.7 | 470.1 | 471.7 | 451.8 | 423.4
2863.1 | 2723.1 | 525.9 | 484.8 | 509.1 | 482.9 | 485 | 481.7 | 470.1 | 471.7 | 451.8 | 423.4
2864.1 | 2724.1 | 525.9 | 484.8 | 509.1 | 482.9 | 485 | 481.7 | 470.1 | 471.8 | 451.8 | 423.3
2865.1 | 2725.1 | 525.9 | 484.8 | 509.1 | 482.9 | 485.1 | 481.7 | 470.2 | 471.8 | 451.8 | 423.4
2866.1 | 2726.1 | 525.9 | 484.8 | 509.1 | 482.9 | 485.1 | 481.8 | 470.2 | 471.9 | 451.9 | 423.4
2867.1 | 2727.1 | 525.9 | 484.8 | 509.1 | 482.9 | 485.1 | 481.8 | 470.3 | 471.9 | 451.9 | 423.4
2868.1 | 2728.1 | 525.9 | 484.8 | 509.2 | 482.9 | 485.2 | 481.8 | 470.3 | 472 | 451.9 | 423.4
2869.1 | 2729.1 | 525.9 | 484.8 | 509.2 | 482.9 | 485.2 | 481.9 | 470.4 | 472 | 451.9 | 423.4
2870.1 | 2730.1 | 525.9 | 484.8 | 509.2 | 482.9 | 485.3 | 481.9 | 470.4 | 472.1 | 451.9 | 423.5
2871.1 | 2731.1 | 525.9 | 484.8 | 509.1 | 482.9 | 485.2 | 481.9 | 470.4 | 472.1 | 452 | 423.5
2872.1 | 2732.1 | 525.8 | 484.8 | 509.1 | 482.9 | 485.3 | 482 | 470.5 | 472.1 | 452 | 423.5
2873.1 | 2733.1 | 525.9 | 484.8 | 509.2 | 482.9 | 485.4 | 482 | 470.5 | 472.1 | 452 | 423.5
2874.1 | 2734.1 | 525.9 | 484.8 | 509.2 | 482.9 | 485.3 | 482 | 470.6 | 472.2 | 452 | 423.5
2875.1 | 2735.1 | 525.9 | 484.8 | 509.3 | 482.9 | 485.4 | 482.1 | 470.6 | 472.3 | 452 | 423.5
2876.1 | 2736.1 | 526 | 484.9 | 509.2 | 482.9 | 485.4 | 482.1 | 470.7 | 472.3 | 452.1 | 423.6
2877.1 | 2737.1 | 526 | 484.9 | 509.2 | 482.9 | 485.4 | 482.1 | 470.7 | 472.4 | 452.1 | 423.6
2878.1 | 2738.1 | 526 | 484.9 | 509.2 | 482.9 | 485.4 | 482.2 | 470.7 | 472.4 | 452.1 | 423.5
2879.1 | 2739.1 | 526 | 484.9 | 509.2 | 482.9 | 485.5 | 482.2 | 470.8 | 472.4 | 452.1 | 423.6
2880.1 | 2740.1 | 526 | 484.9 | 509.2 | 482.9 | 485.5 | 482.2 | 470.8 | 472.4 | 452.1 | 423.6
2881.1 | 2741.1 | 526 | 484.9 | 509.2 | 482.9 | 485.5 | 482.3 | 470.9 | 472.4 | 452.2 | 423.6
2882.1 | 2742.1 | 526 | 484.9 | 509.2 | 482.9 | 485.5 | 482.3 | 470.9 | 472.5 | 452.2 | 423.6
2883.1 | 2743.1 | 526 | 484.9 | 509.2 | 483 | 485.6 | 482.3 | 471 | 472.5 | 452.2 | 423.7
2884.1 | 2744.1 | 526 | 484.9 | 509.2 | 483 | 485.6 | 482.4 | 471 | 472.6 | 452.2 | 423.6
2885.1 | 2745.1 | 526 | 484.9 | 509.3 | 483 | 485.6 | 482.4 | 471.1 | 472.7 | 452.3 | 423.6
2886.1 | 2746.1 | 526 | 484.9 | 509.3 | 483 | 485.7 | 482.4 | 471.1 | 472.7 | 452.3 | 423.6
2887.1 | 2747.1 | 526.1 | 484.9 | 509.4 | 482.9 | 485.6 | 482.4 | 471.2 | 472.6 | 452.3 | 423.5
2888.1 | 2748.1 | 526.1 | 484.8 | 509.5 | 482.9 | 485.4 | 482.4 | 471.2 | 472.7 | 452.3 | 423.3
2889.1 | 2749.1 | 526.1 | 484.8 | 509.5 | 482.9 | 485.4 | 482.4 | 471.3 | 472.8 | 452.4 | 423.3
2890.1 | 2750.1 | 526.1 | 484.8 | 509.5 | 482.9 | 485.5 | 482.5 | 471.3 | 472.8 | 452.4 | 423.4
2891.1 | 2751.1 | 526.1 | 484.9 | 509.5 | 482.9 | 485.5 | 482.5 | 471.3 | 472.8 | 452.4 | 423.4
2892.1 | 2752.1 | 526.1 | 484.9 | 509.5 | 482.9 | 485.5 | 482.5 | 471.4 | 472.8 | 452.4 | 423.3
2893.1 | 2753.1 | 526.1 | 484.9 | 509.6 | 482.9 | 485.6 | 482.5 | 471.4 | 472.9 | 452.4 | 423.4
2894.1 | 2754.1 | 526.2 | 484.9 | 509.5 | 483 | 485.6 | 482.6 | 471.5 | 472.9 | 452.4 | 423.4
2895.1 | 2755.1 | 526.2 | 484.9 | 509.6 | 483 | 485.6 | 482.6 | 471.5 | 473 | 452.5 | 423.4
2896.1 | 2756.1 | 526.1 | 484.9 | 509.6 | 483 | 485.6 | 482.6 | 471.6 | 473 | 452.5 | 423.4
2897.1 | 2757.1 | 526.1 | 484.9 | 509.6 | 483 | 485.7 | 482.7 | 471.6 | 473.1 | 452.5 | 423.5
2898.1 | 2758.1 | 526 | 484.9 | 509.6 | 483 | 485.7 | 482.7 | 471.7 | 473.2 | 452.5 | 423.4
2899.1 | 2759.1 | 526 | 484.9 | 509.6 | 483 | 485.7 | 482.7 | 471.7 | 473.3 | 452.5 | 423.4
2900.1 | 2760.1 | 525.9 | 484.9 | 509.5 | 483 | 485.8 | 482.8 | 471.8 | 473.3 | 452.5 | 423.4
2901.1 | 2761.1 | 525.9 | 484.9 | 509.5 | 483 | 485.8 | 482.8 | 471.8 | 473.3 | 452.6 | 423.5
2902.1 | 2762.1 | 525.9 | 484.9 | 509.5 | 483 | 485.8 | 482.8 | 471.9 | 473.4 | 452.6 | 423.4
2903.1 | 2763.1 | 525.9 | 484.9 | 509.6 | 483 | 485.8 | 482.9 | 471.9 | 473.4 | 452.6 | 423.5
2904.1 | 2764.1 | 525.9 | 485 | 509.6 | 483 | 485.9 | 482.9 | 471.9 | 473.4 | 452.6 | 423.5
2905.1 | 2765.1 | 525.9 | 485 | 509.6 | 483 | 485.9 | 483 | 472 | 473.4 | 452.6 | 423.5
2906.1 | 2766.1 | 525.9 | 485 | 509.6 | 483 | 485.9 | 483 | 472 | 473.4 | 452.7 | 423.5
2907.1 | 2767.1 | 525.9 | 485 | 509.6 | 483 | 486 | 483 | 472.1 | 473.5 | 452.7 | 423.5
2908.1 | 2768.1 | 525.9 | 485 | 509.6 | 483 | 486 | 483 | 472.1 | 473.5 | 452.7 | 423.6
2909.1 | 2769.1 | 525.9 | 485 | 509.6 | 483 | 486 | 483.1 | 472.2 | 473.6 | 452.7 | 423.6
2910.1 | 2770.1 | 525.8 | 485 | 509.6 | 483 | 486.1 | 483.1 | 472.2 | 473.6 | 452.8 | 423.6
2911.1 | 2771.1 | 525.8 | 485 | 509.7 | 483 | 486.1 | 483.1 | 472.3 | 473.7 | 452.8 | 423.6
2912.1 | 2772.1 | 525.8 | 485 | 509.7 | 483 | 486.1 | 483.2 | 472.3 | 473.7 | 452.8 | 423.6
2913.1 | 2773.1 | 525.8 | 485 | 509.7 | 483 | 486.1 | 483.2 | 472.4 | 473.8 | 452.9 | 423.6
2914.1 | 2774.1 | 525.9 | 485 | 509.7 | 483 | 486.2 | 483.2 | 472.4 | 473.8 | 452.9 | 423.7
2915.1 | 2775.1 | 525.9 | 485 | 509.7 | 483 | 486.2 | 483.3 | 472.5 | 473.8 | 452.9 | 423.7
2916.1 | 2776.1 | 525.9 | 485 | 509.7 | 483 | 486.2 | 483.3 | 472.5 | 473.9 | 452.9 | 423.7
2917.1 | 2777.1 | 525.9 | 485 | 509.7 | 483 | 486.2 | 483.3 | 472.6 | 474 | 452.9 | 423.7
2918.1 | 2778.1 | 525.8 | 485 | 509.7 | 483 | 486.3 | 483.4 | 472.6 | 474 | 453 | 423.7
2919.1 | 2779.1 | 525.8 | 485.1 | 509.7 | 483 | 486.3 | 483.4 | 472.7 | 474 | 453 | 423.8
2920.1 | 2780.1 | 525.8 | 485 | 509.7 | 483 | 486.3 | 483.4 | 472.7 | 474.1 | 453 | 423.7
2921.1 | 2781.1 | 525.8 | 485.1 | 509.7 | 483 | 486.4 | 483.5 | 472.8 | 474.1 | 453 | 423.7
2922.1 | 2782.1 | 525.8 | 485.1 | 509.7 | 483 | 486.5 | 483.5 | 472.8 | 474.1 | 453.1 | 423.8
2923.1 | 2783.1 | 525.8 | 485.1 | 509.7 | 483 | 486.4 | 483.5 | 472.8 | 474.2 | 453.1 | 423.8
2924.1 | 2784.1 | 525.7 | 485.1 | 509.7 | 483.1 | 486.5 | 483.6 | 472.9 | 474.2 | 453.1 | 423.8
2925.1 | 2785.1 | 525.7 | 485.1 | 509.7 | 483.1 | 486.5 | 483.6 | 472.9 | 474.2 | 453.1 | 423.8
2926.1 | 2786.1 | 525.7 | 485.1 | 509.7 | 483.1 | 486.5 | 483.6 | 473 | 474.2 | 453.1 | 423.9
2927.1 | 2787.1 | 525.7 | 485.1 | 509.7 | 483.1 | 486.5 | 483.7 | 473 | 474.3 | 453.1 | 423.8
2928.1 | 2788.1 | 525.7 | 485.1 | 509.7 | 483.1 | 486.6 | 483.7 | 473.1 | 474.3 | 453.1 | 423.9
2929.1 | 2789.1 | 525.7 | 485.1 | 509.7 | 483.1 | 486.6 | 483.7 | 473.1 | 474.4 | 453.2 | 423.9
2930.1 | 2790.1 | 525.7 | 485.1 | 509.7 | 483.1 | 486.7 | 483.8 | 473.2 | 474.4 | 453.2 | 423.8
2931.1 | 2791.1 | 525.7 | 485.1 | 509.8 | 483.1 | 486.7 | 483.8 | 473.2 | 474.5 | 453.2 | 423.8
2932.1 | 2792.1 | 525.7 | 485.2 | 509.7 | 483.1 | 486.7 | 483.8 | 473.3 | 474.5 | 453.2 | 423.9
2933.1 | 2793.1 | 525.7 | 485.2 | 509.7 | 483.1 | 486.8 | 483.9 | 473.3 | 474.5 | 453.2 | 423.9
2934.1 | 2794.1 | 525.7 | 485.2 | 509.8 | 483.1 | 486.8 | 483.9 | 473.4 | 474.6 | 453.3 | 423.9
2935.1 | 2795.1 | 525.7 | 485.2 | 509.8 | 483.1 | 486.8 | 483.9 | 473.4 | 474.7 | 453.3 | 423.9
2936.1 | 2796.1 | 525.7 | 485.2 | 509.8 | 483.1 | 486.9 | 484 | 473.5 | 474.7 | 453.3 | 423.9
2937.1 | 2797.1 | 525.7 | 485.2 | 509.9 | 483.1 | 486.9 | 484 | 473.5 | 474.7 | 453.3 | 423.9
2938.1 | 2798.1 | 525.7 | 485.2 | 509.9 | 483.1 | 486.8 | 484 | 473.6 | 474.7 | 453.4 | 423.9
2939.1 | 2799.1 | 525.7 | 485.2 | 509.9 | 483.1 | 487 | 484.1 | 473.6 | 474.8 | 453.4 | 423.9
2940.1 | 2800.1 | 525.7 | 485.2 | 509.8 | 483.1 | 487 | 484.1 | 473.7 | 474.8 | 453.4 | 424
2941.1 | 2801.1 | 525.6 | 485.2 | 509.8 | 483.1 | 487 | 484.1 | 473.7 | 474.8 | 453.4 | 424
2942.1 | 2802.1 | 525.7 | 485.2 | 509.9 | 483.1 | 487 | 484.2 | 473.8 | 474.8 | 453.5 | 424
2943.1 | 2803.1 | 525.6 | 485.3 | 509.8 | 483.1 | 487.1 | 484.2 | 473.8 | 474.9 | 453.5 | 424
2944.1 | 2804.1 | 525.6 | 485.3 | 509.9 | 483.1 | 487.1 | 484.2 | 473.9 | 474.9 | 453.5 | 424
2945.1 | 2805.1 | 525.6 | 485.3 | 509.9 | 483.1 | 487.1 | 484.3 | 473.9 | 474.9 | 453.5 | 424
2946.1 | 2806.1 | 525.7 | 485.3 | 509.8 | 483.1 | 487.2 | 484.3 | 474 | 474.9 | 453.5 | 424.1
2947.1 | 2807.1 | 525.7 | 485.3 | 509.9 | 483.1 | 487.2 | 484.3 | 474 | 474.9 | 453.5 | 424
2948.1 | 2808.1 | 525.7 | 485.3 | 509.9 | 483.1 | 487.2 | 484.4 | 474.1 | 475 | 453.6 | 424
2949.1 | 2809.1 | 525.7 | 485.3 | 509.9 | 483.1 | 487.2 | 484.4 | 474.1 | 475.1 | 453.6 | 424
2950.1 | 2810.1 | 525.7 | 485.3 | 509.9 | 483.1 | 487.3 | 484.4 | 474.2 | 475.1 | 453.6 | 424.1
2951.1 | 2811.1 | 525.7 | 485.3 | 509.9 | 483.1 | 487.3 | 484.5 | 474.2 | 475.2 | 453.6 | 424
2952.1 | 2812.1 | 525.7 | 485.3 | 510 | 483.1 | 487.3 | 484.5 | 474.3 | 475.3 | 453.6 | 424
2953.1 | 2813.1 | 525.7 | 485.3 | 509.9 | 483.1 | 487.4 | 484.5 | 474.3 | 475.3 | 453.6 | 424.1
2954.1 | 2814.1 | 525.7 | 485.3 | 509.9 | 483.1 | 487.4 | 484.6 | 474.4 | 475.4 | 453.6 | 424.1
2955.1 | 2815.1 | 525.7 | 485.3 | 510 | 483.1 | 487.4 | 484.6 | 474.4 | 475.4 | 453.7 | 424.1
2956.1 | 2816.1 | 525.7 | 485.3 | 510 | 483.1 | 487.4 | 484.6 | 474.5 | 475.5 | 453.7 | 424.1
2957.1 | 2817.1 | 525.7 | 485.3 | 510 | 483.1 | 487.5 | 484.7 | 474.5 | 475.5 | 453.7 | 424.1
2958.1 | 2818.1 | 525.7 | 485.4 | 510 | 483.2 | 487.5 | 484.7 | 474.6 | 475.5 | 453.7 | 424.2
2959.1 | 2819.1 | 525.7 | 485.3 | 510 | 483.1 | 487.5 | 484.7 | 474.6 | 475.6 | 453.7 | 424.1
2960.1 | 2820.1 | 525.7 | 485.4 | 509.9 | 483.2 | 487.6 | 484.8 | 474.7 | 475.7 | 453.7 | 424.2
2961.1 | 2821.1 | 525.7 | 485.4 | 509.9 | 483.1 | 487.6 | 484.8 | 474.7 | 475.7 | 453.7 | 424.2
2962.1 | 2822.1 | 525.7 | 485.4 | 509.9 | 483.1 | 487.6 | 484.8 | 474.8 | 475.8 | 453.8 | 424.2
2963.1 | 2823.1 | 525.8 | 485.4 | 509.9 | 483.2 | 487.6 | 484.9 | 474.8 | 475.9 | 453.8 | 424.2
2964.1 | 2824.1 | 525.8 | 485.4 | 509.9 | 483.2 | 487.7 | 484.9 | 474.9 | 475.9 | 453.8 | 424.2
2965.1 | 2825.1 | 525.8 | 485.4 | 510 | 483.2 | 487.7 | 484.9 | 474.9 | 475.9 | 453.8 | 424.2
2966.1 | 2826.1 | 525.8 | 485.4 | 510 | 483.2 | 487.7 | 485 | 475 | 476 | 453.8 | 424.2
2967.1 | 2827.1 | 525.8 | 485.4 | 510 | 483.2 | 487.8 | 485 | 475 | 476 | 453.8 | 424.2
2968.1 | 2828.1 | 525.8 | 485.4 | 510 | 483.2 | 487.8 | 485 | 475.1 | 476 | 453.9 | 424.3
2969.1 | 2829.1 | 525.9 | 485.4 | 509.9 | 483.2 | 487.8 | 485.1 | 475.1 | 476.1 | 453.9 | 424.3
2970.1 | 2830.1 | 525.9 | 485.4 | 509.9 | 483.2 | 487.9 | 485.1 | 475.2 | 476.2 | 453.9 | 424.3
2971.1 | 2831.1 | 526 | 485.4 | 510 | 483.2 | 487.9 | 485.1 | 475.2 | 476.2 | 453.9 | 424.3
2972.1 | 2832.1 | 526 | 485.4 | 510 | 483.2 | 487.9 | 485.2 | 475.3 | 476.2 | 453.9 | 424.3
2973.1 | 2833.1 | 526 | 485.4 | 510 | 483.2 | 487.9 | 485.2 | 475.4 | 476.3 | 453.9 | 424.3
2974.1 | 2834.1 | 526 | 485.4 | 510 | 483.2 | 488 | 485.2 | 475.4 | 476.4 | 454 | 424.3
2975.1 | 2835.1 | 526 | 485.4 | 510 | 483.2 | 488 | 485.3 | 475.5 | 476.5 | 454 | 424.3
2976.1 | 2836.1 | 526.1 | 485.4 | 510 | 483.2 | 488 | 485.3 | 475.5 | 476.6 | 454 | 424.3
2977.1 | 2837.1 | 526 | 485.4 | 510 | 483.2 | 488.1 | 485.4 | 475.6 | 476.7 | 454 | 424.3
2978.1 | 2838.1 | 526 | 485.4 | 510 | 483.2 | 488.1 | 485.4 | 475.6 | 476.7 | 454 | 424.4
2979.1 | 2839.1 | 526 | 485.4 | 510 | 483.2 | 488.1 | 485.4 | 475.7 | 476.8 | 454.1 | 424.4
2980.1 | 2840.1 | 526 | 485.4 | 510 | 483.2 | 488.1 | 485.4 | 475.7 | 476.8 | 454.1 | 424.3
2981.1 | 2841.1 | 526 | 485.5 | 510 | 483.2 | 488.2 | 485.5 | 475.8 | 476.8 | 454.1 | 424.4
2982.1 | 2842.1 | 526 | 485.5 | 510 | 483.2 | 488.3 | 485.5 | 475.8 | 476.8 | 454.1 | 424.4
2983.1 | 2843.1 | 526 | 485.5 | 510.1 | 483.2 | 488.2 | 485.6 | 475.9 | 476.9 | 454.1 | 424.4
2984.1 | 2844.1 | 526 | 485.5 | 510.1 | 483.2 | 488.3 | 485.6 | 475.9 | 477 | 454.2 | 424.4
2985.1 | 2845.1 | 526 | 485.5 | 510.1 | 483.3 | 488.4 | 485.6 | 476 | 477 | 454.2 | 424.5
2986.1 | 2846.1 | 526 | 485.5 | 510.1 | 483.3 | 488.3 | 485.7 | 476 | 477 | 454.2 | 424.4
2987.1 | 2847.1 | 526 | 485.5 | 510.1 | 483.3 | 488.4 | 485.7 | 476.1 | 477.1 | 454.2 | 424.5
2988.1 | 2848.1 | 526 | 485.5 | 510.1 | 483.3 | 488.4 | 485.7 | 476.1 | 477.2 | 454.2 | 424.5
2989.1 | 2849.1 | 526 | 485.4 | 510.2 | 483.2 | 488.3 | 485.7 | 476.2 | 477.2 | 454.3 | 424.4
2990.1 | 2850.1 | 526.1 | 485.4 | 510.4 | 483.2 | 488.1 | 485.7 | 476.2 | 477.2 | 454.3 | 424.2
2991.1 | 2851.1 | 526.1 | 485.4 | 510.4 | 483.2 | 488.2 | 485.7 | 476.3 | 477.1 | 454.3 | 424.2
2992.1 | 2852.1 | 526 | 485.4 | 510.4 | 483.2 | 488.2 | 485.8 | 476.3 | 477.1 | 454.3 | 424.2
2993.1 | 2853.1 | 526 | 485.4 | 510.4 | 483.2 | 488.3 | 485.8 | 476.4 | 477.2 | 454.4 | 424.2
2994.1 | 2854.1 | 526 | 485.4 | 510.4 | 483.2 | 488.3 | 485.8 | 476.5 | 477.2 | 454.4 | 424.2
2995.1 | 2855.1 | 526 | 485.4 | 510.4 | 483.2 | 488.3 | 485.9 | 476.5 | 477.3 | 454.4 | 424.3
2996.1 | 2856.1 | 525.9 | 485.4 | 510.4 | 483.2 | 488.4 | 485.9 | 476.5 | 477.4 | 454.4 | 424.3
2997.1 | 2857.1 | 525.9 | 485.4 | 510.4 | 483.2 | 488.4 | 485.9 | 476.6 | 477.5 | 454.4 | 424.2
2998.1 | 2858.1 | 525.9 | 485.4 | 510.4 | 483.3 | 488.4 | 486 | 476.6 | 477.5 | 454.4 | 424.3
2999.1 | 2859.1 | 525.9 | 485.4 | 510.4 | 483.3 | 488.5 | 486 | 476.7 | 477.6 | 454.5 | 424.3
3000.1 | 2860.1 | 525.9 | 485.4 | 510.4 | 483.3 | 488.5 | 486 | 476.8 | 477.6 | 454.5 | 424.3
3001.1 | 2861.1 | 525.9 | 485.4 | 510.4 | 483.3 | 488.5 | 486.1 | 476.8 | 477.6 | 454.5 | 424.3
3002.1 | 2862.1 | 525.9 | 485.5 | 510.4 | 483.3 | 488.5 | 486.1 | 476.9 | 477.6 | 454.5 | 424.3
3003.1 | 2863.1 | 525.9 | 485.5 | 510.4 | 483.3 | 488.6 | 486.2 | 476.9 | 477.6 | 454.5 | 424.3
3004.1 | 2864.1 | 525.9 | 485.5 | 510.5 | 483.3 | 488.6 | 486.2 | 477 | 477.7 | 454.6 | 424.3
3005.1 | 2865.1 | 525.8 | 485.5 | 510.4 | 483.3 | 488.6 | 486.2 | 477 | 477.8 | 454.6 | 424.3
3006.1 | 2866.1 | 525.8 | 485.5 | 510.4 | 483.3 | 488.7 | 486.3 | 477.1 | 477.8 | 454.6 | 424.4
3007.1 | 2867.1 | 525.8 | 485.5 | 510.4 | 483.3 | 488.7 | 486.3 | 477.1 | 477.9 | 454.6 | 424.4
3008.1 | 2868.1 | 525.8 | 485.5 | 510.5 | 483.3 | 488.7 | 486.3 | 477.2 | 477.9 | 454.6 | 424.3
3009.1 | 2869.1 | 525.8 | 485.5 | 510.5 | 483.3 | 488.8 | 486.4 | 477.2 | 478 | 454.7 | 424.4
3010.1 | 2870.1 | 525.8 | 485.5 | 510.5 | 483.3 | 488.8 | 486.4 | 477.3 | 478 | 454.7 | 424.4
3011.1 | 2871.1 | 525.8 | 485.5 | 510.4 | 483.3 | 488.8 | 486.4 | 477.3 | 478.1 | 454.7 | 424.4
3012.1 | 2872.1 | 525.8 | 485.5 | 510.4 | 483.3 | 488.9 | 486.5 | 477.4 | 478.1 | 454.7 | 424.4
3013.1 | 2873.1 | 525.8 | 485.5 | 510.4 | 483.3 | 488.9 | 486.5 | 477.4 | 478.1 | 454.7 | 424.4
3014.1 | 2874.1 | 525.8 | 485.5 | 510.4 | 483.3 | 488.9 | 486.5 | 477.5 | 478.1 | 454.7 | 424.4
3015.1 | 2875.1 | 525.8 | 485.5 | 510.5 | 483.3 | 488.9 | 486.6 | 477.5 | 478.2 | 454.8 | 424.4
3016.1 | 2876.1 | 525.8 | 485.6 | 510.4 | 483.3 | 489 | 486.6 | 477.6 | 478.2 | 454.8 | 424.5
3017.1 | 2877.1 | 525.8 | 485.6 | 510.4 | 483.3 | 489 | 486.7 | 477.6 | 478.2 | 454.8 | 424.5
3018.1 | 2878.1 | 525.8 | 485.5 | 510.5 | 483.3 | 489 | 486.7 | 477.7 | 478.3 | 454.8 | 424.5
3019.1 | 2879.1 | 525.8 | 485.6 | 510.4 | 483.3 | 489.1 | 486.7 | 477.7 | 478.3 | 454.9 | 424.5
3020.1 | 2880.1 | 525.8 | 485.6 | 510.4 | 483.3 | 489.1 | 486.8 | 477.8 | 478.4 | 454.9 | 424.6
3021.1 | 2881.1 | 525.8 | 485.6 | 510.5 | 483.3 | 489.1 | 486.8 | 477.9 | 478.5 | 454.9 | 424.5
3022.1 | 2882.1 | 525.8 | 485.6 | 510.5 | 483.3 | 489.1 | 486.8 | 477.9 | 478.5 | 454.9 | 424.5
3023.1 | 2883.1 | 525.8 | 485.6 | 510.5 | 483.3 | 489.2 | 486.9 | 478 | 478.6 | 454.9 | 424.6
3024.1 | 2884.1 | 525.8 | 485.6 | 510.5 | 483.3 | 489.2 | 486.9 | 478 | 478.6 | 454.9 | 424.6
3025.1 | 2885.1 | 525.9 | 485.6 | 510.6 | 483.3 | 489.2 | 486.9 | 478.1 | 478.6 | 455 | 424.6
3026.1 | 2886.1 | 525.9 | 485.6 | 510.6 | 483.4 | 489.3 | 487 | 478.1 | 478.7 | 455 | 424.6
3027.1 | 2887.1 | 525.9 | 485.6 | 510.5 | 483.4 | 489.3 | 487 | 478.2 | 478.7 | 455 | 424.6
3028.1 | 2888.1 | 525.9 | 485.6 | 510.5 | 483.3 | 489.3 | 487 | 478.2 | 478.8 | 455 | 424.6
3029.1 | 2889.1 | 526 | 485.6 | 510.6 | 483.4 | 489.3 | 487.1 | 478.3 | 478.8 | 455.1 | 424.6
3030.1 | 2890.1 | 526 | 485.6 | 510.6 | 483.4 | 489.4 | 487.1 | 478.3 | 478.9 | 455.1 | 424.7
3031.1 | 2891.1 | 526.1 | 485.6 | 510.6 | 483.4 | 489.4 | 487.2 | 478.4 | 479 | 455.1 | 424.7
3032.1 | 2892.1 | 526.1 | 485.6 | 510.6 | 483.4 | 489.4 | 487.2 | 478.4 | 479.1 | 455.1 | 424.7
3033.1 | 2893.1 | 526.1 | 485.6 | 510.6 | 483.4 | 489.5 | 487.2 | 478.5 | 479.2 | 455.1 | 424.7
3034.1 | 2894.1 | 526.1 | 485.7 | 510.6 | 483.4 | 489.5 | 487.3 | 478.5 | 479.3 | 455.1 | 424.7
3035.1 | 2895.1 | 526.2 | 485.7 | 510.6 | 483.4 | 489.6 | 487.3 | 478.6 | 479.4 | 455.1 | 424.7
3036.1 | 2896.1 | 526.2 | 485.7 | 510.6 | 483.4 | 489.6 | 487.3 | 478.6 | 479.5 | 455.2 | 424.7
3037.1 | 2897.1 | 526.2 | 485.7 | 510.6 | 483.4 | 489.6 | 487.4 | 478.7 | 479.5 | 455.2 | 424.8
3038.1 | 2898.1 | 526.2 | 485.7 | 510.6 | 483.5 | 489.7 | 487.4 | 478.7 | 479.5 | 455.2 | 424.8
3039.1 | 2899.1 | 526.3 | 485.7 | 510.6 | 483.5 | 489.7 | 487.4 | 478.8 | 479.5 | 455.2 | 424.8
3040.1 | 2900.1 | 526.3 | 485.7 | 510.6 | 483.5 | 489.7 | 487.5 | 478.9 | 479.5 | 455.2 | 424.8
3041.1 | 2901.1 | 526.3 | 485.7 | 510.6 | 483.5 | 489.7 | 487.5 | 478.9 | 479.5 | 455.3 | 424.8
3042.1 | 2902.1 | 526.4 | 485.7 | 510.7 | 483.5 | 489.8 | 487.5 | 479 | 479.5 | 455.3 | 424.8
3043.1 | 2903.1 | 526.4 | 485.7 | 510.7 | 483.5 | 489.8 | 487.6 | 479 | 479.5 | 455.3 | 424.8
3044.1 | 2904.1 | 526.4 | 485.7 | 510.6 | 483.5 | 489.8 | 487.6 | 479.1 | 479.6 | 455.3 | 424.8
3045.1 | 2905.1 | 526.4 | 485.7 | 510.7 | 483.5 | 489.9 | 487.6 | 479.1 | 479.5 | 455.3 | 424.9
3046.1 | 2906.1 | 526.4 | 485.7 | 510.7 | 483.5 | 489.8 | 487.7 | 479.2 | 479.5 | 455.4 | 424.8
3047.1 | 2907.1 | 526.4 | 485.8 | 510.7 | 483.5 | 489.9 | 487.7 | 479.2 | 479.6 | 455.4 | 424.9
3048.1 | 2908.1 | 526.4 | 485.8 | 510.7 | 483.5 | 489.9 | 487.7 | 479.3 | 479.7 | 455.4 | 424.9
3049.1 | 2909.1 | 526.4 | 485.8 | 510.8 | 483.5 | 489.9 | 487.8 | 479.3 | 479.8 | 455.4 | 424.8
3050.1 | 2910.1 | 526.4 | 485.8 | 510.8 | 483.5 | 490 | 487.8 | 479.4 | 479.9 | 455.5 | 424.8
3051.1 | 2911.1 | 526.3 | 485.8 | 510.7 | 483.5 | 490 | 487.9 | 479.4 | 479.9 | 455.5 | 424.9
3052.1 | 2912.1 | 526.4 | 485.8 | 510.8 | 483.5 | 490.1 | 487.9 | 479.5 | 479.9 | 455.5 | 424.9
3053.1 | 2913.1 | 526.4 | 485.8 | 510.8 | 483.5 | 490.1 | 487.9 | 479.5 | 479.9 | 455.5 | 424.9
3054.1 | 2914.1 | 526.4 | 485.8 | 510.8 | 483.5 | 490.1 | 488 | 479.6 | 479.9 | 455.5 | 424.9
3055.1 | 2915.1 | 526.4 | 485.8 | 510.8 | 483.5 | 490.1 | 488 | 479.7 | 480 | 455.6 | 424.9
3056.1 | 2916.1 | 526.3 | 485.8 | 510.8 | 483.5 | 490.2 | 488 | 479.7 | 480.1 | 455.6 | 424.9
3057.1 | 2917.1 | 526.3 | 485.8 | 510.9 | 483.5 | 490.2 | 488.1 | 479.8 | 480.2 | 455.6 | 424.9
3058.1 | 2918.1 | 526.2 | 485.8 | 510.8 | 483.5 | 490.2 | 488.1 | 479.8 | 480.3 | 455.6 | 425
3059.1 | 2919.1 | 526.1 | 485.8 | 510.8 | 483.5 | 490.3 | 488.1 | 479.9 | 480.3 | 455.6 | 425
3060.1 | 2920.1 | 526.1 | 485.8 | 510.9 | 483.5 | 490.3 | 488.2 | 479.9 | 480.4 | 455.7 | 425
3061.1 | 2921.1 | 526 | 485.8 | 510.8 | 483.5 | 490.3 | 488.2 | 480 | 480.4 | 455.7 | 425
3062.1 | 2922.1 | 525.9 | 485.8 | 510.8 | 483.5 | 490.4 | 488.3 | 480 | 480.5 | 455.7 | 425
3063.1 | 2923.1 | 525.9 | 485.8 | 510.8 | 483.5 | 490.4 | 488.3 | 480.1 | 480.6 | 455.7 | 425
3064.1 | 2924.1 | 525.8 | 485.8 | 510.8 | 483.5 | 490.4 | 488.3 | 480.1 | 480.7 | 455.7 | 425
3065.1 | 2925.1 | 525.8 | 485.9 | 510.8 | 483.5 | 490.5 | 488.4 | 480.2 | 480.7 | 455.7 | 425
3066.1 | 2926.1 | 525.8 | 485.9 | 510.8 | 483.5 | 490.5 | 488.4 | 480.2 | 480.7 | 455.8 | 425.1
3067.1 | 2927.1 | 525.8 | 485.9 | 510.9 | 483.5 | 490.5 | 488.4 | 480.3 | 480.8 | 455.8 | 425
3068.1 | 2928.1 | 525.8 | 485.9 | 510.9 | 483.6 | 490.6 | 488.5 | 480.3 | 480.9 | 455.8 | 425.1
3069.1 | 2929.1 | 525.8 | 485.9 | 510.9 | 483.6 | 490.6 | 488.5 | 480.4 | 481 | 455.8 | 425.1
3070.1 | 2930.1 | 525.8 | 485.9 | 510.9 | 483.6 | 490.6 | 488.5 | 480.4 | 481 | 455.9 | 425.1
3071.1 | 2931.1 | 525.7 | 485.9 | 510.9 | 483.6 | 490.6 | 488.6 | 480.5 | 481 | 455.9 | 425.1
3072.1 | 2932.1 | 525.7 | 485.9 | 510.9 | 483.6 | 490.7 | 488.6 | 480.6 | 481.1 | 455.9 | 425.1
3073.1 | 2933.1 | 525.8 | 485.9 | 510.8 | 483.6 | 490.7 | 488.7 | 480.6 | 481.1 | 455.9 | 425.1
3074.1 | 2934.1 | 525.8 | 485.9 | 510.9 | 483.6 | 490.7 | 488.7 | 480.7 | 481.1 | 455.9 | 425.1
3075.1 | 2935.1 | 525.8 | 485.9 | 510.9 | 483.6 | 490.8 | 488.7 | 480.7 | 481.1 | 456 | 425.1
3076.1 | 2936.1 | 525.9 | 485.9 | 510.9 | 483.6 | 490.8 | 488.8 | 480.8 | 481.2 | 456 | 425.2
3077.1 | 2937.1 | 525.9 | 485.9 | 510.9 | 483.6 | 490.8 | 488.8 | 480.8 | 481.2 | 456 | 425.1
3078.1 | 2938.1 | 525.9 | 485.9 | 510.9 | 483.6 | 490.9 | 488.8 | 480.9 | 481.2 | 456 | 425.2
3079.1 | 2939.1 | 525.9 | 486 | 510.9 | 483.6 | 490.9 | 488.9 | 480.9 | 481.3 | 456 | 425.2
3080.1 | 2940.1 | 525.9 | 486 | 510.9 | 483.6 | 490.9 | 488.9 | 481 | 481.3 | 456.1 | 425.2
3081.1 | 2941.1 | 525.9 | 485.9 | 510.9 | 483.6 | 490.9 | 488.9 | 481 | 481.4 | 456.1 | 425.1
3082.1 | 2942.1 | 525.9 | 486 | 510.9 | 483.6 | 491 | 489 | 481.1 | 481.4 | 456.1 | 425.2
3083.1 | 2943.1 | 525.9 | 486 | 511 | 483.6 | 491 | 489 | 481.1 | 481.5 | 456.1 | 425.2
3084.1 | 2944.1 | 525.9 | 486 | 511 | 483.6 | 491.1 | 489.1 | 481.2 | 481.5 | 456.1 | 425.2
3085.1 | 2945.1 | 525.9 | 486 | 511 | 483.6 | 491.1 | 489.1 | 481.3 | 481.6 | 456.2 | 425.2
3086.1 | 2946.1 | 526 | 486 | 511 | 483.6 | 491.1 | 489.1 | 481.3 | 481.6 | 456.2 | 425.2
3087.1 | 2947.1 | 526 | 486 | 511 | 483.6 | 491.2 | 489.2 | 481.4 | 481.6 | 456.2 | 425.2
3088.1 | 2948.1 | 526 | 486 | 511 | 483.6 | 491.1 | 489.2 | 481.4 | 481.6 | 456.2 | 425.2
3089.1 | 2949.1 | 526 | 486 | 511 | 483.6 | 491.2 | 489.2 | 481.5 | 481.6 | 456.2 | 425.2
3090.1 | 2950.1 | 526 | 486 | 511 | 483.6 | 491.2 | 489.3 | 481.5 | 481.7 | 456.3 | 425.3
3091.1 | 2951.1 | 526 | 486 | 511 | 483.7 | 491.2 | 489.3 | 481.6 | 481.7 | 456.3 | 425.3
3092.1 | 2952.1 | 526.1 | 486 | 511.1 | 483.6 | 491.3 | 489.3 | 481.6 | 481.8 | 456.3 | 425.2
3093.1 | 2953.1 | 526.1 | 486 | 511.1 | 483.7 | 491.3 | 489.4 | 481.7 | 481.9 | 456.3 | 425.3
3094.1 | 2954.1 | 526.1 | 486 | 511.1 | 483.7 | 491.4 | 489.4 | 481.7 | 482 | 456.4 | 425.3
3095.1 | 2955.1 | 526.1 | 486 | 511.1 | 483.7 | 491.4 | 489.5 | 481.8 | 482.2 | 456.4 | 425.3
3096.1 | 2956.1 | 526 | 486 | 511.1 | 483.7 | 491.4 | 489.5 | 481.8 | 482.2 | 456.4 | 425.3
3097.1 | 2957.1 | 526 | 486 | 511 | 483.7 | 491.5 | 489.5 | 481.9 | 482.2 | 456.4 | 425.4
3098.1 | 2958.1 | 526.1 | 486 | 511 | 483.7 | 491.5 | 489.6 | 482 | 482.3 | 456.5 | 425.3
3099.1 | 2959.1 | 526.1 | 486 | 511.1 | 483.7 | 491.5 | 489.6 | 482 | 482.3 | 456.5 | 425.3
3100.1 | 2960.1 | 526 | 486 | 511.1 | 483.7 | 491.6 | 489.6 | 482.1 | 482.4 | 456.5 | 425.4
3101.1 | 2961.1 | 526.1 | 486.1 | 511.1 | 483.7 | 491.6 | 489.7 | 482.1 | 482.4 | 456.5 | 425.4
3102.1 | 2962.1 | 526.1 | 486 | 511.1 | 483.7 | 491.6 | 489.7 | 482.2 | 482.4 | 456.6 | 425.4
3103.1 | 2963.1 | 526.1 | 486.1 | 511.1 | 483.7 | 491.7 | 489.8 | 482.2 | 482.4 | 456.6 | 425.4
3104.1 | 2964.1 | 526.1 | 486.1 | 511.1 | 483.7 | 491.7 | 489.8 | 482.3 | 482.5 | 456.6 | 425.4
3105.1 | 2965.1 | 526.1 | 486.1 | 511.1 | 483.7 | 491.7 | 489.8 | 482.3 | 482.5 | 456.6 | 425.4
3106.1 | 2966.1 | 526.1 | 486.1 | 511.1 | 483.7 | 491.7 | 489.9 | 482.4 | 482.6 | 456.6 | 425.4
3107.1 | 2967.1 | 526.1 | 486.1 | 511.1 | 483.7 | 491.8 | 489.9 | 482.4 | 482.7 | 456.6 | 425.5
3108.1 | 2968.1 | 526.1 | 486.1 | 511.1 | 483.7 | 491.8 | 489.9 | 482.5 | 482.7 | 456.7 | 425.5
3109.1 | 2969.1 | 526 | 486.1 | 511.2 | 483.7 | 491.8 | 490 | 482.5 | 482.7 | 456.7 | 425.4
3110.1 | 2970.1 | 526 | 486.1 | 511.1 | 483.7 | 491.9 | 490 | 482.6 | 482.8 | 456.7 | 425.5
3111.1 | 2971.1 | 525.9 | 486.1 | 511.1 | 483.7 | 491.9 | 490.1 | 482.6 | 482.8 | 456.7 | 425.5
3112.1 | 2972.1 | 525.9 | 486.1 | 511.1 | 483.7 | 492 | 490.1 | 482.7 | 482.8 | 456.7 | 425.5
3113.1 | 2973.1 | 525.9 | 486.1 | 511.1 | 483.8 | 492 | 490.1 | 482.7 | 482.8 | 456.8 | 425.5
3114.1 | 2974.1 | 525.9 | 486.1 | 511.1 | 483.8 | 492 | 490.2 | 482.8 | 482.9 | 456.8 | 425.5
3115.1 | 2975.1 | 525.9 | 486 | 511.3 | 483.7 | 491.9 | 490.1 | 482.9 | 482.9 | 456.8 | 425.2
3116.1 | 2976.1 | 525.9 | 485.9 | 511.6 | 483.6 | 491.7 | 490.1 | 482.9 | 483 | 456.9 | 424.9
3117.1 | 2977.1 | 525.8 | 485.8 | 511.7 | 483.6 | 491.6 | 490.1 | 483 | 483.1 | 456.9 | 424.7
3118.1 | 2978.1 | 525.6 | 485.8 | 511.7 | 483.5 | 491.6 | 490.1 | 483 | 483.2 | 457 | 424.7
3119.1 | 2979.1 | 525.3 | 485.8 | 511.7 | 483.5 | 491.6 | 490.1 | 483.1 | 483.1 | 457 | 424.7
3120.1 | 2980.1 | 524.9 | 485.8 | 511.7 | 483.5 | 491.7 | 490.2 | 483.1 | 483.1 | 457 | 424.7
3121.1 | 2981.1 | 524.4 | 485.8 | 511.6 | 483.5 | 491.7 | 490.2 | 483.2 | 483.2 | 457 | 424.7
3122.1 | 2982.1 | 523.9 | 485.8 | 511.6 | 483.5 | 491.7 | 490.2 | 483.2 | 483.2 | 457 | 424.7
3123.1 | 2983.1 | 523.3 | 485.8 | 511.6 | 483.5 | 491.7 | 490.3 | 483.3 | 483.1 | 457.1 | 424.7
3124.1 | 2984.1 | 522.6 | 485.8 | 511.5 | 483.5 | 491.8 | 490.3 | 483.3 | 483.2 | 457.1 | 424.8
3125.1 | 2985.1 | 521.9 | 485.8 | 511.5 | 483.4 | 491.8 | 490.3 | 483.4 | 483.2 | 457.1 | 424.7
3126.1 | 2986.1 | 521.2 | 485.7 | 511.4 | 483.4 | 491.8 | 490.4 | 483.5 | 483.3 | 457.1 | 424.7
3127.1 | 2987.1 | 520.5 | 485.7 | 511.4 | 483.4 | 491.8 | 490.4 | 483.5 | 483.4 | 457.1 | 424.7
3128.1 | 2988.1 | 519.8 | 485.7 | 511.3 | 483.4 | 491.9 | 490.4 | 483.6 | 483.5 | 457.2 | 424.8
3129.1 | 2989.1 | 519 | 485.7 | 511.2 | 483.4 | 492 | 490.5 | 483.6 | 483.6 | 457.2 | 424.8
3130.1 | 2990.1 | 518.2 | 485.6 | 511.2 | 483.3 | 492 | 490.5 | 483.7 | 483.6 | 457.2 | 424.8
3131.1 | 2991.1 | 517.5 | 485.6 | 511.1 | 483.3 | 492 | 490.5 | 483.7 | 483.7 | 457.2 | 424.8
3132.1 | 2992.1 | 516.7 | 485.6 | 511 | 483.3 | 492 | 490.6 | 483.8 | 483.7 | 457.3 | 424.8
3133.1 | 2993.1 | 515.9 | 485.5 | 511 | 483.2 | 492 | 490.6 | 483.8 | 483.8 | 457.3 | 424.8
3134.1 | 2994.1 | 515.1 | 485.5 | 510.9 | 483.2 | 492.1 | 490.6 | 483.9 | 483.8 | 457.3 | 424.8
3135.1 | 2995.1 | 514.3 | 485.5 | 510.8 | 483.1 | 492.1 | 490.7 | 483.9 | 483.8 | 457.3 | 424.8
3136.1 | 2996.1 | 513.5 | 485.4 | 510.8 | 483.1 | 492.1 | 490.7 | 484 | 483.8 | 457.4 | 424.8
3137.1 | 2997.1 | 512.7 | 485.3 | 510.7 | 483 | 492.2 | 490.8 | 484 | 483.8 | 457.4 | 424.8
3138.1 | 2998.1 | 511.9 | 485.3 | 510.5 | 483 | 492.2 | 490.8 | 484.1 | 483.9 | 457.4 | 424.9
3139.1 | 2999.1 | 511.1 | 485.2 | 510.4 | 482.9 | 492.2 | 490.8 | 484.1 | 483.9 | 457.4 | 424.9
3140.1 | 3000.1 | 510.4 | 485.2 | 510.3 | 482.9 | 492.2 | 490.9 | 484.2 | 484 | 457.4 | 424.9
3141.1 | 3001.1 | 509.6 | 485.1 | 510.3 | 482.8 | 492.3 | 490.9 | 484.2 | 484.1 | 457.4 | 424.8
3142.1 | 3002.1 | 508.8 | 485.1 | 510.1 | 482.8 | 492.3 | 490.9 | 484.3 | 484.2 | 457.4 | 424.9
3143.1 | 3003.1 | 508 | 485 | 510 | 482.7 | 492.3 | 491 | 484.3 | 484.3 | 457.5 | 424.9
3144.1 | 3004.1 | 507.2 | 484.9 | 510 | 482.6 | 492.3 | 491 | 484.4 | 484.4 | 457.5 | 424.8
3145.1 | 3005.1 | 506.4 | 484.9 | 509.8 | 482.6 | 492.4 | 491 | 484.4 | 484.4 | 457.5 | 424.9
3146.1 | 3006.1 | 505.6 | 484.8 | 509.7 | 482.5 | 492.4 | 491 | 484.5 | 484.4 | 457.5 | 424.9
3147.1 | 3007.1 | 504.8 | 484.8 | 509.6 | 482.4 | 492.4 | 491.1 | 484.5 | 484.5 | 457.5 | 424.9
3148.1 | 3008.1 | 504 | 484.7 | 509.5 | 482.4 | 492.4 | 491.1 | 484.6 | 484.6 | 457.5 | 424.9
3149.1 | 3009.1 | 503.2 | 484.6 | 509.4 | 482.3 | 492.5 | 491.1 | 484.6 | 484.6 | 457.5 | 424.9
3150.1 | 3010.1 | 502.4 | 484.6 | 509.2 | 482.2 | 492.5 | 491.2 | 484.7 | 484.7 | 457.6 | 424.9
3151.1 | 3011.1 | 501.6 | 484.4 | 509.1 | 482.1 | 492.5 | 491.2 | 484.7 | 484.8 | 457.6 | 424.9
3152.1 | 3012.1 | 500.8 | 484.4 | 509 | 482.1 | 492.5 | 491.2 | 484.7 | 484.9 | 457.6 | 424.9
3153.1 | 3013.1 | 500 | 484.3 | 508.8 | 482 | 492.6 | 491.2 | 484.8 | 484.9 | 457.6 | 425
3154.1 | 3014.1 | 499.4 | 484.2 | 508.7 | 481.9 | 492.6 | 491.3 | 484.8 | 485 | 457.6 | 425
3155.1 | 3015.1 | 498.6 | 484.1 | 508.6 | 481.8 | 492.6 | 491.3 | 484.9 | 485 | 457.7 | 425
3156.1 | 3016.1 | 497.7 | 484 | 508.4 | 481.7 | 492.6 | 491.3 | 484.9 | 485 | 457.6 | 425
3157.1 | 3017.1 | 496.9 | 484 | 508.3 | 481.7 | 492.6 | 491.3 | 485 | 485 | 457.7 | 425
3158.1 | 3018.1 | 496.2 | 483.8 | 508.2 | 481.6 | 492.6 | 491.3 | 485 | 485 | 457.7 | 424.9
3159.1 | 3019.1 | 495.4 | 483.8 | 508 | 481.5 | 492.6 | 491.4 | 485.1 | 485.1 | 457.7 | 425
3160.1 | 3020.1 | 494.6 | 483.7 | 507.9 | 481.4 | 492.7 | 491.4 | 485.1 | 485.1 | 457.7 | 425
3161.1 | 3021.1 | 493.8 | 483.6 | 507.8 | 481.3 | 492.6 | 491.4 | 485.1 | 485.1 | 457.7 | 425
3162.1 | 3022.1 | 493 | 483.5 | 507.6 | 481.2 | 492.6 | 491.4 | 485.2 | 485.1 | 457.7 | 425
3163.1 | 3023.1 | 492.2 | 483.4 | 507.4 | 481.1 | 492.7 | 491.5 | 485.2 | 485.1 | 457.7 | 425
3164.1 | 3024.1 | 491.4 | 483.3 | 507.2 | 481 | 492.7 | 491.5 | 485.2 | 485.1 | 457.7 | 425.1
3165.1 | 3025.1 | 490.6 | 483.2 | 507 | 480.9 | 492.7 | 491.5 | 485.3 | 485.1 | 457.7 | 425
3166.1 | 3026.1 | 489.8 | 483.1 | 506.9 | 480.8 | 492.7 | 491.5 | 485.3 | 485.2 | 457.7 | 425.1
3167.1 | 3027.1 | 489 | 483 | 506.7 | 480.7 | 492.7 | 491.5 | 485.3 | 485.2 | 457.7 | 425.1
3168.1 | 3028.1 | 488.2 | 482.9 | 506.5 | 480.6 | 492.7 | 491.6 | 485.4 | 485.2 | 457.7 | 425.1
3169.1 | 3029.1 | 487.5 | 482.7 | 506.4 | 480.4 | 492.7 | 491.6 | 485.4 | 485.2 | 457.7 | 425.1
3170.1 | 3030.1 | 486.7 | 482.6 | 506.2 | 480.3 | 492.7 | 491.6 | 485.4 | 485.2 | 457.7 | 425.1
3171.1 | 3031.1 | 485.9 | 482.5 | 506 | 480.2 | 492.7 | 491.6 | 485.5 | 485.2 | 457.7 | 425.1
3172.1 | 3032.1 | 485.1 | 482.4 | 505.8 | 480.1 | 492.7 | 491.6 | 485.5 | 485.2 | 457.7 | 425.1
3173.1 | 3033.1 | 484.4 | 482.3 | 505.6 | 480 | 492.7 | 491.6 | 485.5 | 485.3 | 457.7 | 425.1
3174.1 | 3034.1 | 483.6 | 482.2 | 505.5 | 479.8 | 492.7 | 491.6 | 485.6 | 485.3 | 457.7 | 425.1
3175.1 | 3035.1 | 482.8 | 482.1 | 505.3 | 479.7 | 492.7 | 491.7 | 485.6 | 485.3 | 457.7 | 425.1
3176.1 | 3036.1 | 482 | 481.9 | 505.1 | 479.6 | 492.7 | 491.6 | 485.6 | 485.3 | 457.7 | 425.1
3177.1 | 3037.1 | 481.3 | 481.8 | 504.9 | 479.5 | 492.7 | 491.7 | 485.7 | 485.3 | 457.7 | 425.1
3178.1 | 3038.1 | 480.5 | 481.7 | 504.7 | 479.4 | 492.7 | 491.7 | 485.7 | 485.3 | 457.7 | 425.1
3179.1 | 3039.1 | 479.8 | 481.5 | 504.6 | 479.2 | 492.7 | 491.7 | 485.7 | 485.3 | 457.7 | 425.1
3180.1 | 3040.1 | 479 | 481.4 | 504.4 | 479.1 | 492.7 | 491.7 | 485.8 | 485.3 | 457.7 | 425.1
3181.1 | 3041.1 | 478.2 | 481.3 | 504.1 | 479 | 492.7 | 491.7 | 485.8 | 485.4 | 457.7 | 425.2
3182.1 | 3042.1 | 477.5 | 481.1 | 504 | 478.8 | 492.7 | 491.7 | 485.8 | 485.5 | 457.7 | 425.2
3183.1 | 3043.1 | 476.7 | 481 | 503.8 | 478.7 | 492.6 | 491.7 | 485.8 | 485.6 | 457.7 | 425.1
3184.1 | 3044.1 | 476 | 480.9 | 503.5 | 478.6 | 492.7 | 491.7 | 485.8 | 485.6 | 457.6 | 425.2
3185.1 | 3045.1 | 475.3 | 480.7 | 503.3 | 478.4 | 492.6 | 491.7 | 485.9 | 485.6 | 457.6 | 425.2
3186.1 | 3046.1 | 474.5 | 480.6 | 503.2 | 478.3 | 492.6 | 491.7 | 485.9 | 485.6 | 457.6 | 425.1
3187.1 | 3047.1 | 473.8 | 480.5 | 503 | 478.2 | 492.6 | 491.7 | 485.9 | 485.6 | 457.6 | 425.2
3188.1 | 3048.1 | 473.1 | 480.3 | 502.8 | 478 | 492.6 | 491.7 | 485.9 | 485.6 | 457.6 | 425.2
3189.1 | 3049.1 | 472.3 | 480.2 | 502.6 | 477.9 | 492.5 | 491.6 | 485.9 | 485.6 | 457.6 | 425.1
3190.1 | 3050.1 | 471.6 | 480 | 502.4 | 477.7 | 492.5 | 491.6 | 486 | 485.7 | 457.6 | 425.1
3191.1 | 3051.1 | 470.9 | 479.9 | 502.1 | 477.6 | 492.5 | 491.6 | 486 | 485.7 | 457.5 | 425.1
3192.1 | 3052.1 | 470.1 | 479.7 | 501.9 | 477.5 | 492.5 | 491.6 | 486 | 485.8 | 457.5 | 425.2
3193.1 | 3053.1 | 469.4 | 479.6 | 501.8 | 477.3 | 492.4 | 491.6 | 486 | 485.8 | 457.5 | 425.1
3194.1 | 3054.1 | 468.7 | 479.4 | 501.6 | 477.1 | 492.5 | 491.6 | 486 | 485.7 | 457.5 | 425.1
3195.1 | 3055.1 | 468 | 479.3 | 501.3 | 477 | 492.4 | 491.6 | 486 | 485.7 | 457.5 | 425.2
3196.1 | 3056.1 | 467.3 | 479.1 | 501.1 | 476.8 | 492.4 | 491.6 | 486 | 485.8 | 457.5 | 425.1
3197.1 | 3057.1 | 466.6 | 478.9 | 500.9 | 476.7 | 492.4 | 491.6 | 486 | 485.8 | 457.5 | 425.1
3198.1 | 3058.1 | 465.9 | 478.8 | 500.7 | 476.5 | 492.4 | 491.6 | 486 | 485.8 | 457.4 | 425.1
3199.1 | 3059.1 | 465.2 | 478.6 | 500.5 | 476.4 | 492.3 | 491.5 | 486.1 | 485.9 | 457.4 | 425.1
3200.1 | 3060.1 | 464.5 | 478.4 | 500.3 | 476.2 | 492.2 | 491.5 | 486.1 | 485.9 | 457.4 | 425
3201.1 | 3061.1 | 463.8 | 478.3 | 500 | 476 | 492.2 | 491.5 | 486.1 | 485.8 | 457.4 | 425.1
3202.1 | 3062.1 | 463 | 478.1 | 499.9 | 475.9 | 492.2 | 491.5 | 486.1 | 485.9 | 457.3 | 425.1
3203.1 | 3063.1 | 462.3 | 478 | 499.7 | 475.7 | 492.2 | 491.4 | 486.1 | 485.9 | 457.3 | 425.1
3204.1 | 3064.1 | 461.6 | 477.8 | 499.5 | 475.5 | 492.1 | 491.4 | 486.1 | 485.9 | 457.3 | 425
3205.1 | 3065.1 | 460.9 | 477.6 | 499.3 | 475.4 | 492.1 | 491.4 | 486.1 | 485.9 | 457.3 | 425.1
3206.1 | 3066.1 | 460.2 | 477.5 | 499 | 475.2 | 492 | 491.4 | 486.1 | 485.9 | 457.3 | 425.1
3207.1 | 3067.1 | 459.6 | 477.3 | 498.8 | 475.1 | 492 | 491.3 | 486.1 | 486 | 457.2 | 425
3208.1 | 3068.1 | 458.9 | 477.1 | 498.6 | 474.9 | 492 | 491.3 | 486 | 485.9 | 457.2 | 425
3209.1 | 3069.1 | 458.2 | 477 | 498.3 | 474.7 | 491.9 | 491.3 | 486 | 485.9 | 457.2 | 425.1
3210.1 | 3070.1 | 457.5 | 476.8 | 498.2 | 474.6 | 491.9 | 491.2 | 486 | 485.8 | 457.1 | 425
3211.1 | 3071.1 | 456.8 | 476.6 | 497.9 | 474.4 | 491.8 | 491.2 | 486 | 485.8 | 457.1 | 425
3212.1 | 3072.1 | 456.1 | 476.5 | 497.7 | 474.2 | 491.8 | 491.2 | 486 | 485.8 | 457.1 | 425
3213.1 | 3073.1 | 455.4 | 476.3 | 497.4 | 474 | 491.7 | 491.1 | 486 | 485.8 | 457.1 | 425
3214.1 | 3074.1 | 454.7 | 476.1 | 497.2 | 473.8 | 491.7 | 491.1 | 486 | 485.8 | 457 | 424.9
3215.1 | 3075.1 | 454 | 475.9 | 497 | 473.7 | 491.6 | 491.1 | 486 | 485.7 | 457 | 424.9
3216.1 | 3076.1 | 453.4 | 475.8 | 496.8 | 473.5 | 491.6 | 491 | 486 | 485.7 | 456.9 | 425
3217.1 | 3077.1 | 452.7 | 475.6 | 496.5 | 473.3 | 491.5 | 491 | 485.9 | 485.7 | 456.9 | 424.9
3218.1 | 3078.1 | 452 | 475.4 | 496.3 | 473.1 | 491.5 | 490.9 | 485.9 | 485.7 | 456.9 | 424.9
3219.1 | 3079.1 | 451.4 | 475.2 | 496 | 473 | 491.4 | 490.9 | 485.9 | 485.7 | 456.8 | 424.9
3220.1 | 3080.1 | 450.7 | 475.1 | 495.8 | 472.8 | 491.4 | 490.9 | 485.9 | 485.7 | 456.8 | 424.9
3221.1 | 3081.1 | 450 | 474.9 | 495.6 | 472.6 | 491.3 | 490.8 | 485.9 | 485.7 | 456.8 | 424.8
3222.1 | 3082.1 | 449.4 | 474.7 | 495.4 | 472.4 | 491.3 | 490.8 | 485.9 | 485.7 | 456.7 | 424.8
3223.1 | 3083.1 | 448.8 | 474.5 | 495.1 | 472.2 | 491.2 | 490.7 | 485.8 | 485.7 | 456.7 | 424.9
3224.1 | 3084.1 | 448.1 | 474.3 | 494.8 | 472.1 | 491.1 | 490.7 | 485.8 | 485.6 | 456.7 | 424.8
3225.1 | 3085.1 | 447.5 | 474.1 | 494.6 | 471.8 | 491.1 | 490.6 | 485.8 | 485.6 | 456.6 | 424.8
3226.1 | 3086.1 | 446.8 | 473.9 | 494.4 | 471.7 | 491 | 490.6 | 485.8 | 485.5 | 456.6 | 424.8
3227.1 | 3087.1 | 446.2 | 473.7 | 494.1 | 471.5 | 491 | 490.5 | 485.7 | 485.5 | 456.6 | 424.8
3228.1 | 3088.1 | 445.5 | 473.5 | 493.9 | 471.2 | 490.8 | 490.5 | 485.7 | 485.5 | 456.5 | 424.7
3229.1 | 3089.1 | 444.9 | 473.3 | 493.7 | 471.1 | 490.8 | 490.4 | 485.7 | 485.5 | 456.5 | 424.7
3230.1 | 3090.1 | 444.2 | 473.1 | 493.4 | 470.9 | 490.7 | 490.4 | 485.7 | 485.5 | 456.5 | 424.7
3231.1 | 3091.1 | 443.6 | 472.9 | 493.2 | 470.7 | 490.6 | 490.3 | 485.6 | 485.5 | 456.5 | 424.7
3232.1 | 3092.1 | 443 | 472.8 | 492.9 | 470.5 | 490.6 | 490.2 | 485.6 | 485.4 | 456.4 | 424.6
3233.1 | 3093.1 | 442.3 | 472.6 | 492.6 | 470.3 | 490.5 | 490.2 | 485.6 | 485.4 | 456.3 | 424.6
3234.1 | 3094.1 | 441.7 | 472.4 | 492.4 | 470.2 | 490.5 | 490.1 | 485.5 | 485.4 | 456.3 | 424.6
3235.1 | 3095.1 | 441 | 472.2 | 492.2 | 470 | 490.3 | 490.1 | 485.5 | 485.3 | 456.2 | 424.6
3236.1 | 3096.1 | 440.4 | 472 | 491.9 | 469.8 | 490.3 | 490 | 485.5 | 485.3 | 456.1 | 424.6
3237.1 | 3097.1 | 439.8 | 471.8 | 491.6 | 469.6 | 490.2 | 489.9 | 485.4 | 485.2 | 456.1 | 424.6
3238.1 | 3098.1 | 439.2 | 471.6 | 491.4 | 469.4 | 490.1 | 489.9 | 485.4 | 485.2 | 456 | 424.6
3239.1 | 3099.1 | 438.6 | 471.4 | 491.1 | 469.1 | 490 | 489.8 | 485.3 | 485.1 | 456 | 424.5
3240.1 | 3100.1 | 437.9 | 471.2 | 490.8 | 469 | 490 | 489.8 | 485.3 | 485 | 456 | 424.6
3241.1 | 3101.1 | 437.2 | 471 | 490.6 | 468.8 | 489.9 | 489.7 | 485.3 | 485 | 455.9 | 424.5
3242.1 | 3102.1 | 436.6 | 470.8 | 490.3 | 468.6 | 489.8 | 489.6 | 485.2 | 484.9 | 455.9 | 424.5
3243.1 | 3103.1 | 436 | 470.6 | 490.1 | 468.4 | 489.8 | 489.5 | 485.2 | 484.8 | 455.8 | 424.5
3244.1 | 3104.1 | 435.5 | 470.4 | 489.8 | 468.2 | 489.7 | 489.5 | 485.1 | 484.8 | 455.8 | 424.5
3245.1 | 3105.1 | 434.9 | 470.1 | 489.6 | 468 | 489.6 | 489.4 | 485.1 | 484.8 | 455.7 | 424.4
3246.1 | 3106.1 | 434.3 | 469.9 | 489.3 | 467.8 | 489.5 | 489.3 | 485 | 484.7 | 455.7 | 424.4
3247.1 | 3107.1 | 433.7 | 469.7 | 489 | 467.6 | 489.4 | 489.2 | 485 | 484.6 | 455.6 | 424.4
3248.1 | 3108.1 | 433.1 | 469.5 | 488.7 | 467.4 | 489.4 | 489.2 | 484.9 | 484.6 | 455.5 | 424.4
3249.1 | 3109.1 | 432.5 | 469.3 | 488.5 | 467.2 | 489.2 | 489.1 | 484.9 | 484.6 | 455.4 | 424.4
3250.1 | 3110.1 | 431.9 | 469.1 | 488.2 | 467 | 489.2 | 489 | 484.8 | 484.6 | 455.4 | 424.4
3251.1 | 3111.1 | 431.3 | 468.9 | 487.9 | 466.8 | 489.1 | 488.9 | 484.8 | 484.6 | 455.3 | 424.3
3252.1 | 3112.1 | 430.7 | 468.7 | 487.7 | 466.6 | 489 | 488.8 | 484.7 | 484.6 | 455.2 | 424.3
3253.1 | 3113.1 | 430.1 | 468.5 | 487.4 | 466.4 | 488.9 | 488.8 | 484.7 | 484.6 | 455.2 | 424.2
3254.1 | 3114.1 | 429.5 | 468.3 | 487.1 | 466.2 | 488.8 | 488.7 | 484.6 | 484.6 | 455.1 | 424.3
3255.1 | 3115.1 | 428.9 | 468.1 | 486.9 | 466 | 488.7 | 488.6 | 484.5 | 484.6 | 455 | 424.3
3256.1 | 3116.1 | 428.3 | 467.9 | 486.6 | 465.8 | 488.6 | 488.5 | 484.5 | 484.5 | 455 | 424.2
3257.1 | 3117.1 | 427.7 | 467.6 | 486.4 | 465.6 | 488.5 | 488.4 | 484.4 | 484.4 | 454.9 | 424.2
3258.1 | 3118.1 | 427.1 | 467.4 | 486 | 465.3 | 488.4 | 488.4 | 484.4 | 484.3 | 454.9 | 424.2
3259.1 | 3119.1 | 426.5 | 467.2 | 485.8 | 465.1 | 488.3 | 488.3 | 484.3 | 484.2 | 454.8 | 424.1
3260.1 | 3120.1 | 425.9 | 467 | 485.6 | 464.9 | 488.2 | 488.2 | 484.2 | 484.2 | 454.7 | 424
3261.1 | 3121.1 | 425.3 | 466.8 | 485.3 | 464.6 | 488.1 | 488.1 | 484.2 | 484.1 | 454.7 | 424
3262.1 | 3122.1 | 424.7 | 466.6 | 485 | 464.5 | 488 | 488 | 484.1 | 484 | 454.6 | 424
3263.1 | 3123.1 | 424.1 | 466.3 | 484.8 | 464.3 | 487.9 | 487.9 | 484 | 484 | 454.5 | 423.9
3264.1 | 3124.1 | 423.6 | 466.1 | 484.5 | 464.1 | 487.8 | 487.8 | 484 | 484 | 454.5 | 423.9
3265.1 | 3125.1 | 423 | 465.9 | 484.2 | 463.8 | 487.7 | 487.7 | 483.9 | 483.9 | 454.4 | 423.9
3266.1 | 3126.1 | 422.4 | 465.7 | 483.9 | 463.6 | 487.6 | 487.6 | 483.8 | 483.8 | 454.3 | 423.8
3267.1 | 3127.1 | 421.8 | 465.5 | 483.7 | 463.4 | 487.5 | 487.5 | 483.8 | 483.8 | 454.3 | 423.8
3268.1 | 3128.1 | 421.3 | 465.3 | 483.4 | 463.2 | 487.4 | 487.4 | 483.7 | 483.7 | 454.2 | 423.8
3269.1 | 3129.1 | 420.7 | 465 | 483.1 | 463 | 487.2 | 487.3 | 483.6 | 483.7 | 454.1 | 423.7
3270.1 | 3130.1 | 420.1 | 464.8 | 482.8 | 462.8 | 487.1 | 487.2 | 483.5 | 483.6 | 454.1 | 423.7
3271.1 | 3131.1 | 419.6 | 464.6 | 482.5 | 462.6 | 487.1 | 487.1 | 483.5 | 483.5 | 454 | 423.7
3272.1 | 3132.1 | 419 | 464.4 | 482.2 | 462.3 | 487 | 487 | 483.4 | 483.5 | 453.9 | 423.7
3273.1 | 3133.1 | 418.5 | 464.2 | 482 | 462.1 | 486.8 | 486.9 | 483.3 | 483.5 | 453.8 | 423.7
3274.1 | 3134.1 | 417.9 | 464 | 481.7 | 461.9 | 486.7 | 486.8 | 483.2 | 483.4 | 453.7 | 423.7
3275.1 | 3135.1 | 417.4 | 463.7 | 481.4 | 461.7 | 486.6 | 486.7 | 483.2 | 483.3 | 453.6 | 423.6
3276.1 | 3136.1 | 416.8 | 463.5 | 481.1 | 461.5 | 486.5 | 486.6 | 483.1 | 483.2 | 453.5 | 423.5
3277.1 | 3137.1 | 416.3 | 463.3 | 480.9 | 461.3 | 486.3 | 486.5 | 483 | 483.1 | 453.5 | 423.5
3278.1 | 3138.1 | 415.7 | 463.1 | 480.6 | 461 | 486.3 | 486.4 | 482.9 | 483.1 | 453.4 | 423.5
3279.1 | 3139.1 | 415.2 | 462.9 | 480.3 | 460.8 | 486.2 | 486.3 | 482.8 | 483 | 453.3 | 423.5
3280.1 | 3140.1 | 414.6 | 462.6 | 480.1 | 460.6 | 486 | 486.2 | 482.8 | 482.9 | 453.2 | 423.4
3281.1 | 3141.1 | 414.1 | 462.4 | 479.8 | 460.3 | 485.9 | 486.1 | 482.7 | 482.8 | 453.2 | 423.3
3282.1 | 3142.1 | 413.5 | 462.2 | 479.5 | 460.1 | 485.8 | 486 | 482.6 | 482.7 | 453.1 | 423.3
3283.1 | 3143.1 | 413 | 462 | 479.2 | 459.9 | 485.7 | 485.9 | 482.5 | 482.6 | 453 | 423.3
3284.1 | 3144.1 | 412.4 | 461.7 | 479 | 459.7 | 485.5 | 485.8 | 482.4 | 482.5 | 452.9 | 423.2
3285.1 | 3145.1 | 411.9 | 461.5 | 478.6 | 459.5 | 485.4 | 485.7 | 482.3 | 482.3 | 452.8 | 423.2
3286.1 | 3146.1 | 411.4 | 461.3 | 478.3 | 459.2 | 485.3 | 485.5 | 482.2 | 482.3 | 452.7 | 423.2
3287.1 | 3147.1 | 410.8 | 461 | 478.1 | 459 | 485.2 | 485.4 | 482.1 | 482.3 | 452.7 | 423.1
3288.1 | 3148.1 | 410.2 | 460.8 | 477.8 | 458.7 | 485 | 485.3 | 482.1 | 482.2 | 452.6 | 423
3289.1 | 3149.1 | 409.7 | 460.6 | 477.5 | 458.5 | 484.9 | 485.2 | 482 | 482.1 | 452.5 | 423
3290.1 | 3150.1 | 409.1 | 460.4 | 477.2 | 458.3 | 484.8 | 485.1 | 481.9 | 482 | 452.4 | 423
3291.1 | 3151.1 | 408.6 | 460.1 | 477 | 458.1 | 484.6 | 484.9 | 481.8 | 481.9 | 452.3 | 422.9
3292.1 | 3152.1 | 408 | 459.9 | 476.6 | 457.9 | 484.5 | 484.8 | 481.7 | 481.8 | 452.2 | 422.9
3293.1 | 3153.1 | 407.5 | 459.7 | 476.4 | 457.6 | 484.4 | 484.7 | 481.6 | 481.7 | 452.1 | 422.8
3294.1 | 3154.1 | 407 | 459.4 | 476.1 | 457.4 | 484.3 | 484.6 | 481.5 | 481.7 | 452 | 422.8
3295.1 | 3155.1 | 406.5 | 459.2 | 475.9 | 457.2 | 484.1 | 484.4 | 481.4 | 481.6 | 451.9 | 422.7
3296.1 | 3156.1 | 405.9 | 459 | 475.6 | 457 | 484 | 484.3 | 481.3 | 481.5 | 451.8 | 422.7
3297.1 | 3157.1 | 405.4 | 458.7 | 475.3 | 456.7 | 483.8 | 484.2 | 481.2 | 481.5 | 451.7 | 422.6
3298.1 | 3158.1 | 404.9 | 458.5 | 475.1 | 456.5 | 483.7 | 484.1 | 481.1 | 481.4 | 451.7 | 422.5
3299.1 | 3159.1 | 404.4 | 458.3 | 474.8 | 456.3 | 483.5 | 483.9 | 481 | 481.4 | 451.6 | 422.4
3300.1 | 3160.1 | 403.8 | 458.1 | 474.5 | 456 | 483.4 | 483.8 | 480.9 | 481.3 | 451.5 | 422.4
3301.1 | 3161.1 | 403.4 | 457.8 | 474.2 | 455.8 | 483.3 | 483.7 | 480.8 | 481.3 | 451.4 | 422.3
3302.1 | 3162.1 | 402.9 | 457.6 | 474 | 455.6 | 483.1 | 483.5 | 480.7 | 481.2 | 451.3 | 422.3
3303.1 | 3163.1 | 402.3 | 457.4 | 473.7 | 455.4 | 483 | 483.4 | 480.6 | 481.1 | 451.2 | 422.2
3304.1 | 3164.1 | 401.8 | 457.2 | 473.4 | 455.1 | 482.9 | 483.3 | 480.5 | 480.9 | 451.1 | 422.2
3305.1 | 3165.1 | 401.3 | 456.9 | 473.1 | 454.9 | 482.7 | 483.2 | 480.4 | 480.8 | 451 | 422.1
3306.1 | 3166.1 | 400.8 | 456.7 | 472.8 | 454.7 | 482.6 | 483 | 480.3 | 480.7 | 450.9 | 422.1
3307.1 | 3167.1 | 400.3 | 456.5 | 472.5 | 454.4 | 482.5 | 482.9 | 480.2 | 480.7 | 450.8 | 422.1
3308.1 | 3168.1 | 399.8 | 456.2 | 472.2 | 454.2 | 482.3 | 482.8 | 480.1 | 480.6 | 450.7 | 422
3309.1 | 3169.1 | 399.3 | 456 | 472 | 454 | 482.1 | 482.6 | 479.9 | 480.5 | 450.6 | 421.9
3310.1 | 3170.1 | 398.8 | 455.8 | 471.6 | 453.7 | 482 | 482.5 | 479.8 | 480.4 | 450.5 | 421.9
3311.1 | 3171.1 | 398.3 | 455.5 | 471.4 | 453.5 | 481.9 | 482.4 | 479.7 | 480.3 | 450.4 | 421.9
3312.1 | 3172.1 | 397.8 | 455.3 | 471.1 | 453.3 | 481.7 | 482.2 | 479.6 | 480.1 | 450.3 | 421.7
3313.1 | 3173.1 | 397.3 | 455.1 | 470.8 | 453 | 481.6 | 482.1 | 479.5 | 479.9 | 450.2 | 421.7
3314.1 | 3174.1 | 396.8 | 454.8 | 470.5 | 452.8 | 481.4 | 481.9 | 479.4 | 479.8 | 450.1 | 421.7
3315.1 | 3175.1 | 396.3 | 454.6 | 470.3 | 452.6 | 481.3 | 481.8 | 479.3 | 479.7 | 450 | 421.6
3316.1 | 3176.1 | 395.8 | 454.4 | 470 | 452.3 | 481.1 | 481.7 | 479.2 | 479.6 | 449.9 | 421.5
3317.1 | 3177.1 | 395.4 | 454.2 | 469.6 | 452.1 | 481 | 481.5 | 479 | 479.5 | 449.8 | 421.5
3318.1 | 3178.1 | 394.8 | 453.9 | 469.4 | 451.9 | 480.8 | 481.4 | 478.9 | 479.4 | 449.7 | 421.4
3319.1 | 3179.1 | 394.3 | 453.7 | 469.2 | 451.6 | 480.7 | 481.2 | 478.8 | 479.3 | 449.6 | 421.3
3320.1 | 3180.1 | 393.8 | 453.4 | 468.8 | 451.4 | 480.5 | 481.1 | 478.7 | 479.2 | 449.5 | 421.3
3321.1 | 3181.1 | 393.3 | 453.2 | 468.5 | 451.2 | 480.4 | 480.9 | 478.6 | 479.2 | 449.4 | 421.3
3322.1 | 3182.1 | 392.8 | 453 | 468.3 | 450.9 | 480.2 | 480.8 | 478.5 | 479.1 | 449.3 | 421.2
3323.1 | 3183.1 | 392.3 | 452.7 | 468 | 450.7 | 480 | 480.6 | 478.3 | 479 | 449.2 | 421.1
3324.1 | 3184.1 | 391.8 | 452.5 | 467.7 | 450.4 | 479.9 | 480.5 | 478.2 | 478.9 | 449.1 | 421.1
3325.1 | 3185.1 | 391.3 | 452.3 | 467.4 | 450.2 | 479.8 | 480.4 | 478.1 | 478.7 | 449 | 421
3326.1 | 3186.1 | 390.9 | 452 | 467.1 | 450 | 479.6 | 480.2 | 478 | 478.6 | 448.9 | 420.9
3327.1 | 3187.1 | 390.4 | 451.8 | 466.8 | 449.7 | 479.5 | 480.1 | 477.8 | 478.5 | 448.8 | 420.9
3328.1 | 3188.1 | 389.9 | 451.5 | 466.5 | 449.5 | 479.3 | 479.9 | 477.7 | 478.3 | 448.7 | 420.8
3329.1 | 3189.1 | 389.4 | 451.3 | 466.3 | 449.2 | 479.1 | 479.8 | 477.6 | 478.1 | 448.6 | 420.7
3330.1 | 3190.1 | 389 | 451 | 466 | 449 | 479 | 479.6 | 477.5 | 478 | 448.5 | 420.6
3331.1 | 3191.1 | 388.5 | 450.8 | 465.7 | 448.8 | 478.8 | 479.5 | 477.3 | 477.9 | 448.4 | 420.6
3332.1 | 3192.1 | 388 | 450.6 | 465.4 | 448.6 | 478.7 | 479.3 | 477.2 | 477.7 | 448.3 | 420.5
3333.1 | 3193.1 | 387.6 | 450.3 | 465.1 | 448.3 | 478.5 | 479.2 | 477.1 | 477.6 | 448.2 | 420.4
3334.1 | 3194.1 | 387.1 | 450.1 | 464.8 | 448.1 | 478.4 | 479 | 476.9 | 477.6 | 448.1 | 420.4
3335.1 | 3195.1 | 386.6 | 449.9 | 464.5 | 447.8 | 478.2 | 478.9 | 476.8 | 477.4 | 448.1 | 420.3
3336.1 | 3196.1 | 386.1 | 449.6 | 464.2 | 447.6 | 478.1 | 478.7 | 476.7 | 477.3 | 448 | 420.2
3337.1 | 3197.1 | 385.7 | 449.4 | 464 | 447.3 | 477.9 | 478.6 | 476.6 | 477.3 | 447.9 | 420.1
3338.1 | 3198.1 | 385.2 | 449.2 | 463.6 | 447.1 | 477.8 | 478.4 | 476.4 | 477.2 | 447.8 | 420.1
3339.1 | 3199.1 | 384.8 | 448.9 | 463.4 | 446.8 | 477.6 | 478.3 | 476.3 | 477 | 447.7 | 420
3340.1 | 3200.1 | 384.3 | 448.6 | 463.1 | 446.6 | 477.4 | 478.1 | 476.2 | 476.9 | 447.6 | 419.9
3341.1 | 3201.1 | 383.9 | 448.4 | 462.8 | 446.4 | 477.2 | 477.9 | 476 | 476.8 | 447.5 | 419.9
3342.1 | 3202.1 | 383.4 | 448.2 | 462.5 | 446.1 | 477.1 | 477.8 | 475.9 | 476.7 | 447.4 | 419.8
3343.1 | 3203.1 | 382.9 | 447.9 | 462.2 | 445.9 | 476.9 | 477.6 | 475.8 | 476.6 | 447.3 | 419.8
3344.1 | 3204.1 | 382.5 | 447.7 | 462 | 445.7 | 476.7 | 477.5 | 475.6 | 476.5 | 447.2 | 419.6
3345.1 | 3205.1 | 382 | 447.5 | 461.6 | 445.4 | 476.6 | 477.3 | 475.5 | 476.3 | 447.1 | 419.6
3346.1 | 3206.1 | 381.5 | 447.2 | 461.4 | 445.2 | 476.5 | 477.2 | 475.4 | 476.2 | 447 | 419.6
3347.1 | 3207.1 | 381.1 | 447 | 461.1 | 445 | 476.3 | 477 | 475.2 | 476 | 446.9 | 419.5
3348.1 | 3208.1 | 380.6 | 446.8 | 460.8 | 444.7 | 476.1 | 476.9 | 475.1 | 475.9 | 446.8 | 419.4
3349.1 | 3209.1 | 380.2 | 446.5 | 460.5 | 444.5 | 476 | 476.7 | 475 | 475.8 | 446.7 | 419.4
3350.1 | 3210.1 | 379.7 | 446.3 | 460.2 | 444.2 | 475.8 | 476.6 | 474.8 | 475.7 | 446.6 | 419.3
3351.1 | 3211.1 | 379.3 | 446 | 459.9 | 444 | 475.6 | 476.4 | 474.7 | 475.5 | 446.5 | 419.2
3352.1 | 3212.1 | 378.8 | 445.8 | 459.6 | 443.8 | 475.5 | 476.3 | 474.6 | 475.4 | 446.4 | 419.2
3353.1 | 3213.1 | 378.3 | 445.6 | 459.3 | 443.6 | 475.3 | 476.1 | 474.4 | 475.2 | 446.2 | 419.2
3354.1 | 3214.1 | 377.9 | 445.3 | 459.1 | 443.3 | 475.1 | 475.9 | 474.3 | 475 | 446.1 | 419
3355.1 | 3215.1 | 377.5 | 445.1 | 458.7 | 443.1 | 475 | 475.8 | 474.2 | 475 | 446 | 419
3356.1 | 3216.1 | 377 | 444.9 | 458.5 | 442.8 | 474.8 | 475.6 | 474 | 474.8 | 445.9 | 418.9
3357.1 | 3217.1 | 376.6 | 444.6 | 458.2 | 442.6 | 474.7 | 475.5 | 473.9 | 474.6 | 445.7 | 418.9
3358.1 | 3218.1 | 376.2 | 444.4 | 457.9 | 442.4 | 474.5 | 475.3 | 473.8 | 474.6 | 445.6 | 418.8
3359.1 | 3219.1 | 375.7 | 444.1 | 457.6 | 442.1 | 474.3 | 475.1 | 473.6 | 474.5 | 445.5 | 418.7
3360.1 | 3220.1 | 375.3 | 443.9 | 457.4 | 441.9 | 474.2 | 475 | 473.5 | 474.4 | 445.3 | 418.7
3361.1 | 3221.1 | 374.8 | 443.7 | 457.1 | 441.6 | 474 | 474.8 | 473.3 | 474.3 | 445.2 | 418.6
3362.1 | 3222.1 | 374.4 | 443.4 | 456.8 | 441.4 | 473.8 | 474.6 | 473.2 | 474 | 445.1 | 418.5
3363.1 | 3223.1 | 373.9 | 443.2 | 456.5 | 441.2 | 473.7 | 474.5 | 473 | 473.9 | 444.9 | 418.4
3364.1 | 3224.1 | 373.5 | 442.9 | 456.2 | 440.9 | 473.5 | 474.3 | 472.9 | 473.8 | 444.8 | 418.3
3365.1 | 3225.1 | 373 | 442.7 | 456 | 440.7 | 473.3 | 474.1 | 472.8 | 473.6 | 444.6 | 418.2
3366.1 | 3226.1 | 372.6 | 442.5 | 455.7 | 440.4 | 473.2 | 474 | 472.6 | 473.4 | 444.5 | 418.2
3367.1 | 3227.1 | 372.1 | 442.2 | 455.3 | 440.2 | 473 | 473.8 | 472.5 | 473.3 | 444.4 | 418.2
3368.1 | 3228.1 | 371.7 | 442 | 455.1 | 440 | 472.8 | 473.6 | 472.3 | 473.1 | 444.2 | 418
3369.1 | 3229.1 | 371.2 | 441.7 | 454.8 | 439.7 | 472.6 | 473.5 | 472.2 | 473 | 444.1 | 418
3370.1 | 3230.1 | 370.8 | 441.5 | 454.5 | 439.5 | 472.5 | 473.3 | 472 | 472.8 | 444 | 417.9
3371.1 | 3231.1 | 370.4 | 441.3 | 454.2 | 439.2 | 472.3 | 473.2 | 471.9 | 472.7 | 443.9 | 417.8
3372.1 | 3232.1 | 370 | 441 | 454 | 439 | 472.1 | 473 | 471.7 | 472.5 | 443.7 | 417.7
3373.1 | 3233.1 | 369.6 | 440.8 | 453.6 | 438.8 | 472 | 472.8 | 471.6 | 472.4 | 443.6 | 417.7
3374.1 | 3234.1 | 369.1 | 440.6 | 453.3 | 438.5 | 471.8 | 472.7 | 471.4 | 472.2 | 443.5 | 417.6
3375.1 | 3235.1 | 368.7 | 440.3 | 453.1 | 438.3 | 471.6 | 472.5 | 471.3 | 472 | 443.4 | 417.4
3376.1 | 3236.1 | 368.3 | 440.1 | 452.8 | 438.1 | 471.4 | 472.3 | 471.1 | 471.8 | 443.3 | 417.4
3377.1 | 3237.1 | 367.9 | 439.8 | 452.5 | 437.8 | 471.3 | 472.1 | 471 | 471.6 | 443.2 | 417.3
3378.1 | 3238.1 | 367.5 | 439.6 | 452.2 | 437.6 | 471.1 | 472 | 470.8 | 471.5 | 443 | 417.2
3379.1 | 3239.1 | 367 | 439.3 | 451.9 | 437.4 | 470.9 | 471.8 | 470.7 | 471.3 | 442.9 | 417.1
3380.1 | 3240.1 | 366.6 | 439.1 | 451.6 | 437.1 | 470.8 | 471.6 | 470.5 | 471.2 | 442.8 | 417.1
3381.1 | 3241.1 | 366.2 | 438.9 | 451.3 | 436.9 | 470.6 | 471.5 | 470.4 | 471.1 | 442.7 | 417
3382.1 | 3242.1 | 365.8 | 438.6 | 451.1 | 436.6 | 470.4 | 471.3 | 470.2 | 471 | 442.6 | 416.9
3383.1 | 3243.1 | 365.4 | 438.4 | 450.8 | 436.4 | 470.3 | 471.1 | 470.1 | 470.8 | 442.4 | 416.8
3384.1 | 3244.1 | 365 | 438.1 | 450.5 | 436.2 | 470.1 | 470.9 | 469.9 | 470.7 | 442.3 | 416.7
3385.1 | 3245.1 | 364.6 | 437.9 | 450.2 | 435.9 | 469.9 | 470.8 | 469.8 | 470.5 | 442.2 | 416.6
3386.1 | 3246.1 | 364.2 | 437.6 | 450 | 435.6 | 469.7 | 470.6 | 469.6 | 470.3 | 442.1 | 416.5
3387.1 | 3247.1 | 363.7 | 437.4 | 449.6 | 435.4 | 469.6 | 470.4 | 469.5 | 470.2 | 442 | 416.5
3388.1 | 3248.1 | 363.3 | 437.2 | 449.3 | 435.2 | 469.4 | 470.3 | 469.3 | 470 | 441.8 | 416.4
3389.1 | 3249.1 | 362.9 | 436.9 | 449.1 | 434.9 | 469.2 | 470.1 | 469.2 | 469.8 | 441.7 | 416.2
3390.1 | 3250.1 | 362.5 | 436.7 | 448.8 | 434.7 | 469 | 469.9 | 469.1 | 469.6 | 441.6 | 416.1
3391.1 | 3251.1 | 362.1 | 436.4 | 448.5 | 434.4 | 468.9 | 469.7 | 468.9 | 469.5 | 441.5 | 416.1
3392.1 | 3252.1 | 361.7 | 436.2 | 448.2 | 434.2 | 468.6 | 469.6 | 468.8 | 469.5 | 441.4 | 415.9
3393.1 | 3253.1 | 361.3 | 435.9 | 448 | 434 | 468.4 | 469.4 | 468.6 | 469.4 | 441.3 | 415.8
3394.1 | 3254.1 | 360.9 | 435.7 | 447.6 | 433.7 | 468.3 | 469.2 | 468.5 | 469.3 | 441.1 | 415.7
3395.1 | 3255.1 | 360.4 | 435.4 | 447.4 | 433.5 | 468.1 | 469 | 468.3 | 469.2 | 441 | 415.6
3396.1 | 3256.1 | 360 | 435.2 | 447.1 | 433.2 | 467.9 | 468.9 | 468.2 | 469 | 440.9 | 415.5
3397.1 | 3257.1 | 359.6 | 434.9 | 446.8 | 433 | 467.8 | 468.7 | 468 | 468.9 | 440.7 | 415.4
3398.1 | 3258.1 | 359.2 | 434.7 | 446.5 | 432.8 | 467.6 | 468.5 | 467.9 | 468.8 | 440.6 | 415.4
3399.1 | 3259.1 | 358.8 | 434.4 | 446.3 | 432.5 | 467.4 | 468.3 | 467.7 | 468.6 | 440.4 | 415.2
3400.1 | 3260.1 | 358.4 | 434.2 | 446 | 432.3 | 467.2 | 468.2 | 467.6 | 468.5 | 440.3 | 415.1
3401.1 | 3261.1 | 358 | 433.9 | 445.7 | 432 | 467 | 468 | 467.4 | 468.3 | 440.2 | 415
3402.1 | 3262.1 | 357.6 | 433.7 | 445.4 | 431.8 | 466.9 | 467.8 | 467.3 | 468.2 | 440 | 415
3403.1 | 3263.1 | 357.2 | 433.5 | 445.1 | 431.6 | 466.7 | 467.6 | 467.1 | 468 | 439.9 | 414.9
3404.1 | 3264.1 | 356.8 | 433.2 | 444.8 | 431.3 | 466.5 | 467.5 | 467 | 467.8 | 439.8 | 414.8
3405.1 | 3265.1 | 356.4 | 433 | 444.5 | 431.1 | 466.4 | 467.3 | 466.8 | 467.6 | 439.6 | 414.7
3406.1 | 3266.1 | 356 | 432.7 | 444.2 | 430.9 | 466.2 | 467.1 | 466.7 | 467.5 | 439.5 | 414.6
3407.1 | 3267.1 | 355.6 | 432.5 | 444 | 430.6 | 466 | 466.9 | 466.5 | 467.3 | 439.3 | 414.5
3408.1 | 3268.1 | 355.3 | 432.3 | 443.6 | 430.4 | 465.8 | 466.8 | 466.4 | 467.2 | 439.2 | 414.4
3409.1 | 3269.1 | 354.9 | 432 | 443.4 | 430.2 | 465.7 | 466.6 | 466.2 | 467 | 439 | 414.3
3410.1 | 3270.1 | 354.5 | 431.8 | 443.1 | 429.9 | 465.4 | 466.4 | 466.1 | 466.8 | 438.9 | 414.2
3411.1 | 3271.1 | 354.1 | 431.5 | 442.8 | 429.7 | 465.3 | 466.2 | 465.9 | 466.6 | 438.7 | 414.1
3412.1 | 3272.1 | 353.7 | 431.3 | 442.5 | 429.4 | 465.1 | 466.1 | 465.8 | 466.4 | 438.6 | 414
3413.1 | 3273.1 | 353.4 | 431 | 442.3 | 429.2 | 464.9 | 465.9 | 465.6 | 466.3 | 438.4 | 413.9
3414.1 | 3274.1 | 353 | 430.8 | 442 | 429 | 464.7 | 465.7 | 465.5 | 466.2 | 438.3 | 413.8
3415.1 | 3275.1 | 352.6 | 430.6 | 441.7 | 428.8 | 464.6 | 465.5 | 465.3 | 466 | 438.1 | 413.7
3416.1 | 3276.1 | 352.2 | 430.3 | 441.4 | 428.5 | 464.4 | 465.4 | 465.1 | 465.9 | 438 | 413.7
3417.1 | 3277.1 | 351.8 | 430.1 | 441.2 | 428.2 | 464.2 | 465.2 | 465 | 465.8 | 437.9 | 413.5
3418.1 | 3278.1 | 351.4 | 429.8 | 440.8 | 428 | 464 | 465 | 464.8 | 465.6 | 437.7 | 413.4
3419.1 | 3279.1 | 351 | 429.6 | 440.6 | 427.8 | 463.8 | 464.8 | 464.7 | 465.5 | 437.6 | 413.3
3420.1 | 3280.1 | 350.6 | 429.3 | 440.3 | 427.5 | 463.6 | 464.6 | 464.5 | 465.4 | 437.4 | 413.2
3421.1 | 3281.1 | 350.3 | 429.1 | 440.1 | 427.3 | 463.4 | 464.4 | 464.4 | 465.2 | 437.3 | 413
3422.1 | 3282.1 | 349.9 | 428.9 | 439.7 | 427.1 | 463.3 | 464.3 | 464.2 | 465.1 | 437.1 | 413
3423.1 | 3283.1 | 349.5 | 428.6 | 439.4 | 426.8 | 463.1 | 464.1 | 464.1 | 465 | 437 | 412.9
3424.1 | 3284.1 | 349.2 | 428.3 | 439.2 | 426.6 | 462.9 | 463.9 | 463.9 | 464.8 | 436.9 | 412.8
3425.1 | 3285.1 | 348.8 | 428.1 | 439 | 426.4 | 462.7 | 463.7 | 463.7 | 464.7 | 436.8 | 412.7
3426.1 | 3286.1 | 348.4 | 427.9 | 438.7 | 426.1 | 462.5 | 463.5 | 463.6 | 464.6 | 436.6 | 412.6
3427.1 | 3287.1 | 348.1 | 427.6 | 438.3 | 425.9 | 462.4 | 463.4 | 463.4 | 464.4 | 436.5 | 412.5
3428.1 | 3288.1 | 347.7 | 427.4 | 438.1 | 425.6 | 462.1 | 463.1 | 463.3 | 464.2 | 436.3 | 412.4
3429.1 | 3289.1 | 347.4 | 427.2 | 437.8 | 425.5 | 462 | 463 | 463.1 | 464.1 | 436.2 | 412.3
3430.1 | 3290.1 | 347 | 426.9 | 437.5 | 425.2 | 461.8 | 462.8 | 462.9 | 464 | 436.1 | 412.2
3431.1 | 3291.1 | 346.7 | 426.7 | 437.3 | 425 | 461.6 | 462.6 | 462.8 | 463.8 | 435.9 | 412.1
3432.1 | 3292.1 | 346.3 | 426.4 | 437 | 424.7 | 461.4 | 462.4 | 462.6 | 463.6 | 435.7 | 412
3433.1 | 3293.1 | 346 | 426.2 | 436.7 | 424.5 | 461.2 | 462.3 | 462.5 | 463.3 | 435.6 | 411.9
3434.1 | 3294.1 | 345.6 | 426 | 436.4 | 424.3 | 461.1 | 462.1 | 462.3 | 463.1 | 435.5 | 411.8
3435.1 | 3295.1 | 345.2 | 425.7 | 436.2 | 424 | 460.8 | 461.9 | 462.1 | 462.9 | 435.3 | 411.6
3436.1 | 3296.1 | 344.8 | 425.5 | 435.9 | 423.8 | 460.7 | 461.7 | 462 | 462.8 | 435.2 | 411.6
3437.1 | 3297.1 | 344.5 | 425.2 | 435.6 | 423.5 | 460.5 | 461.5 | 461.8 | 462.6 | 435 | 411.5
3438.1 | 3298.1 | 344.1 | 425 | 435.4 | 423.3 | 460.3 | 461.3 | 461.6 | 462.5 | 434.9 | 411.3
3439.1 | 3299.1 | 343.7 | 424.8 | 435.1 | 423.1 | 460.1 | 461.1 | 461.5 | 462.3 | 434.7 | 411.3
3440.1 | 3300.1 | 343.3 | 424.5 | 434.8 | 422.9 | 459.9 | 460.9 | 461.3 | 462.1 | 434.5 | 411.2
3441.1 | 3301.1 | 343 | 424.3 | 434.5 | 422.6 | 459.7 | 460.8 | 461.1 | 461.9 | 434.4 | 411
3442.1 | 3302.1 | 342.6 | 424 | 434.3 | 422.4 | 459.5 | 460.6 | 461 | 461.8 | 434.2 | 410.9
3443.1 | 3303.1 | 342.2 | 423.8 | 434 | 422.2 | 459.4 | 460.4 | 460.8 | 461.6 | 434.1 | 410.8
3444.1 | 3304.1 | 341.9 | 423.5 | 433.7 | 421.9 | 459.2 | 460.2 | 460.6 | 461.4 | 433.9 | 410.7
3445.1 | 3305.1 | 341.5 | 423.3 | 433.4 | 421.7 | 458.9 | 460 | 460.5 | 461.2 | 433.8 | 410.6
3446.1 | 3306.1 | 341.1 | 423.1 | 433.1 | 421.5 | 458.8 | 459.8 | 460.3 | 461.1 | 433.6 | 410.5
3447.1 | 3307.1 | 340.8 | 422.8 | 432.9 | 421.3 | 458.6 | 459.6 | 460.1 | 461 | 433.5 | 410.4
3448.1 | 3308.1 | 340.4 | 422.6 | 432.6 | 421 | 458.4 | 459.4 | 460 | 460.8 | 433.3 | 410.3
3449.1 | 3309.1 | 340.1 | 422.3 | 432.3 | 420.8 | 458.2 | 459.2 | 459.8 | 460.6 | 433.2 | 410.1
3450.1 | 3310.1 | 339.7 | 422.1 | 432 | 420.5 | 458 | 459.1 | 459.6 | 460.5 | 433 | 410.1
3451.1 | 3311.1 | 339.4 | 421.9 | 431.7 | 420.3 | 457.8 | 458.9 | 459.4 | 460.4 | 432.9 | 409.9
3452.1 | 3312.1 | 339 | 421.6 | 431.5 | 420.1 | 457.6 | 458.7 | 459.3 | 460.2 | 432.7 | 409.8
3453.1 | 3313.1 | 338.6 | 421.4 | 431.2 | 419.8 | 457.4 | 458.5 | 459.1 | 460.1 | 432.6 | 409.7
3454.1 | 3314.1 | 338.3 | 421.2 | 430.9 | 419.6 | 457.3 | 458.3 | 458.9 | 459.9 | 432.5 | 409.6
3455.1 | 3315.1 | 338 | 420.9 | 430.6 | 419.3 | 457.1 | 458.1 | 458.8 | 459.7 | 432.3 | 409.5
3456.1 | 3316.1 | 337.6 | 420.6 | 430.4 | 419.1 | 456.9 | 457.9 | 458.6 | 459.4 | 432.2 | 409.3
3457.1 | 3317.1 | 337.3 | 420.4 | 430.1 | 418.9 | 456.7 | 457.7 | 458.4 | 459.2 | 432.1 | 409.3
3458.1 | 3318.1 | 336.9 | 420.2 | 429.8 | 418.6 | 456.5 | 457.6 | 458.3 | 459.1 | 432 | 409.2
3459.1 | 3319.1 | 336.6 | 419.9 | 429.6 | 418.4 | 456.3 | 457.3 | 458.1 | 458.9 | 431.9 | 409
3460.1 | 3320.1 | 336.2 | 419.7 | 429.3 | 418.2 | 456.1 | 457.2 | 457.9 | 458.7 | 431.8 | 408.9
3461.1 | 3321.1 | 335.9 | 419.5 | 429 | 418 | 455.9 | 457 | 457.7 | 458.6 | 431.7 | 408.8
3462.1 | 3322.1 | 335.5 | 419.2 | 428.8 | 417.7 | 455.7 | 456.8 | 457.6 | 458.4 | 431.5 | 408.7
3463.1 | 3323.1 | 335.2 | 419 | 428.5 | 417.4 | 455.5 | 456.6 | 457.4 | 458.2 | 431.5 | 408.6
3464.1 | 3324.1 | 334.9 | 418.7 | 428.3 | 417.2 | 455.3 | 456.4 | 457.2 | 458 | 431.4 | 408.5
3465.1 | 3325.1 | 334.5 | 418.5 | 427.9 | 417 | 455.1 | 456.2 | 457 | 457.9 | 431.2 | 408.4
3466.1 | 3326.1 | 334.2 | 418.2 | 427.7 | 416.8 | 454.9 | 456 | 456.9 | 457.7 | 431.1 | 408.2
3467.1 | 3327.1 | 333.8 | 418 | 427.4 | 416.5 | 454.7 | 455.8 | 456.7 | 457.5 | 430.9 | 408.2
3468.1 | 3328.1 | 333.5 | 417.8 | 427.1 | 416.3 | 454.6 | 455.6 | 456.5 | 457.4 | 430.7 | 408.1
3469.1 | 3329.1 | 333.1 | 417.5 | 426.9 | 416.1 | 454.3 | 455.4 | 456.3 | 457.2 | 430.5 | 407.9
3470.1 | 3330.1 | 332.8 | 417.3 | 426.6 | 415.8 | 454.1 | 455.2 | 456.2 | 457.1 | 430.3 | 407.8
3471.1 | 3331.1 | 332.5 | 417.1 | 426.4 | 415.6 | 453.9 | 455 | 456 | 456.9 | 430.1 | 407.7
3472.1 | 3332.1 | 332.1 | 416.8 | 426.1 | 415.4 | 453.7 | 454.8 | 455.8 | 456.6 | 429.9 | 407.6
3473.1 | 3333.1 | 331.8 | 416.6 | 425.8 | 415.1 | 453.5 | 454.6 | 455.6 | 456.5 | 429.7 | 407.4
3474.1 | 3334.1 | 331.5 | 416.4 | 425.5 | 414.9 | 453.4 | 454.5 | 455.4 | 456.3 | 429.5 | 407.4
3475.1 | 3335.1 | 331.1 | 416.1 | 425.3 | 414.7 | 453.1 | 454.2 | 455.3 | 456.1 | 429.3 | 407.2
3476.1 | 3336.1 | 330.8 | 415.9 | 425 | 414.4 | 453 | 454 | 455.1 | 455.9 | 429.1 | 407.1
3477.1 | 3337.1 | 330.4 | 415.6 | 424.7 | 414.2 | 452.7 | 453.8 | 454.9 | 455.7 | 428.9 | 407
3478.1 | 3338.1 | 330.1 | 415.4 | 424.4 | 413.9 | 452.6 | 453.7 | 454.7 | 455.5 | 428.7 | 406.9
3479.1 | 3339.1 | 329.8 | 415.2 | 424.1 | 413.7 | 452.4 | 453.5 | 454.5 | 455.3 | 428.6 | 406.8
3480.1 | 3340.1 | 329.4 | 414.9 | 423.9 | 413.5 | 452.1 | 453.3 | 454.4 | 455.1 | 428.5 | 406.6
3481.1 | 3341.1 | 329.1 | 414.7 | 423.7 | 413.2 | 452 | 453.1 | 454.2 | 455 | 428.3 | 406.5
3482.1 | 3342.1 | 328.8 | 414.5 | 423.4 | 413 | 451.8 | 452.9 | 454 | 454.8 | 428.1 | 406.4
3483.1 | 3343.1 | 328.5 | 414.2 | 423.1 | 412.8 | 451.6 | 452.7 | 453.8 | 454.6 | 428 | 406.3
3484.1 | 3344.1 | 328.1 | 414 | 422.9 | 412.6 | 451.3 | 452.5 | 453.7 | 454.5 | 427.8 | 406.1
3485.1 | 3345.1 | 327.8 | 413.7 | 422.6 | 412.4 | 451.2 | 452.3 | 453.5 | 454.3 | 427.7 | 406
3486.1 | 3346.1 | 327.5 | 413.5 | 422.3 | 412.1 | 451 | 452.1 | 453.3 | 454.1 | 427.5 | 405.9
3487.1 | 3347.1 | 327.2 | 413.3 | 422.1 | 411.9 | 450.7 | 451.9 | 453.1 | 454.1 | 427.3 | 405.8
3488.1 | 3348.1 | 326.9 | 413 | 421.8 | 411.6 | 450.6 | 451.7 | 452.9 | 453.9 | 427.2 | 405.6
3489.1 | 3349.1 | 326.6 | 412.8 | 421.5 | 411.4 | 450.4 | 451.5 | 452.7 | 453.7 | 427.1 | 405.5
3490.1 | 3350.1 | 326.3 | 412.6 | 421.2 | 411.2 | 450.2 | 451.3 | 452.6 | 453.6 | 426.9 | 405.4
3491.1 | 3351.1 | 325.9 | 412.3 | 421 | 411 | 449.9 | 451.1 | 452.4 | 453.4 | 426.7 | 405.2
3492.1 | 3352.1 | 325.6 | 412.1 | 420.7 | 410.8 | 449.8 | 450.9 | 452.2 | 453.1 | 426.6 | 405.2
3493.1 | 3353.1 | 325.3 | 411.9 | 420.4 | 410.6 | 449.6 | 450.7 | 452 | 452.9 | 426.4 | 405.1
3494.1 | 3354.1 | 324.9 | 411.6 | 420.2 | 410.3 | 449.4 | 450.5 | 451.8 | 452.7 | 426.3 | 404.9
3495.1 | 3355.1 | 324.6 | 411.4 | 419.9 | 410.1 | 449.2 | 450.3 | 451.7 | 452.5 | 426.1 | 404.7
3496.1 | 3356.1 | 324.3 | 411.1 | 419.7 | 409.9 | 449 | 450.1 | 451.5 | 452.2 | 426 | 404.6
3497.1 | 3357.1 | 323.9 | 410.9 | 419.4 | 409.6 | 448.8 | 449.9 | 451.3 | 452.1 | 425.8 | 404.5
3498.1 | 3358.1 | 323.6 | 410.7 | 419.1 | 409.4 | 448.6 | 449.7 | 451.1 | 451.8 | 425.7 | 404.3
3499.1 | 3359.1 | 323.3 | 410.5 | 418.8 | 409.2 | 448.4 | 449.5 | 450.9 | 451.6 | 425.5 | 404.3
3500.1 | 3360.1 | 322.9 | 410.2 | 418.6 | 409 | 448.2 | 449.3 | 450.8 | 451.4 | 425.4 | 404.1
3501.1 | 3361.1 | 322.6 | 410 | 418.4 | 408.8 | 448 | 449.1 | 450.6 | 451.2 | 425.3 | 403.9
3502.1 | 3362.1 | 322.3 | 409.7 | 418.1 | 408.6 | 447.8 | 448.9 | 450.4 | 451 | 425.2 | 403.8
3503.1 | 3363.1 | 322 | 409.5 | 417.8 | 408.4 | 447.6 | 448.7 | 450.2 | 450.9 | 425.1 | 403.7
3504.1 | 3364.1 | 321.6 | 409.3 | 417.5 | 408.1 | 447.4 | 448.5 | 450 | 450.8 | 425 | 403.6
3505.1 | 3365.1 | 321.3 | 409 | 417.3 | 407.9 | 447.2 | 448.3 | 449.9 | 450.6 | 424.8 | 403.4
3506.1 | 3366.1 | 321 | 408.8 | 417 | 407.7 | 447 | 448.1 | 449.7 | 450.4 | 424.7 | 403.3
3507.1 | 3367.1 | 320.7 | 408.6 | 416.7 | 407.5 | 446.8 | 447.9 | 449.5 | 450.3 | 424.5 | 403.2
3508.1 | 3368.1 | 320.4 | 408.3 | 416.5 | 407.3 | 446.6 | 447.7 | 449.3 | 450.1 | 424.4 | 403
3509.1 | 3369.1 | 320.1 | 408.1 | 416.2 | 407 | 446.4 | 447.5 | 449.1 | 449.9 | 424.2 | 402.9
3510.1 | 3370.1 | 319.8 | 407.9 | 416 | 406.9 | 446.2 | 447.3 | 448.9 | 449.8 | 424 | 402.8
3511.1 | 3371.1 | 319.5 | 407.6 | 415.7 | 406.6 | 446 | 447.1 | 448.8 | 449.6 | 423.9 | 402.7
3512.1 | 3372.1 | 319.2 | 407.4 | 415.5 | 406.4 | 445.8 | 446.9 | 448.6 | 449.4 | 423.7 | 402.5
3513.1 | 3373.1 | 318.9 | 407.2 | 415.2 | 406.2 | 445.6 | 446.7 | 448.4 | 449.2 | 423.6 | 402.4
3514.1 | 3374.1 | 318.5 | 407 | 414.9 | 406 | 445.4 | 446.5 | 448.2 | 449 | 423.4 | 402.3
3515.1 | 3375.1 | 318.2 | 406.7 | 414.7 | 405.8 | 445.2 | 446.3 | 448 | 448.8 | 423.3 | 402.1
3516.1 | 3376.1 | 317.9 | 406.5 | 414.4 | 405.6 | 445 | 446.1 | 447.9 | 448.6 | 423.1 | 402
3517.1 | 3377.1 | 317.6 | 406.3 | 414.1 | 405.4 | 444.8 | 445.9 | 447.7 | 448.4 | 423 | 401.9
3518.1 | 3378.1 | 317.3 | 406 | 413.9 | 405.2 | 444.6 | 445.7 | 447.5 | 448.3 | 422.8 | 401.7
3519.1 | 3379.1 | 317 | 405.8 | 413.7 | 405 | 444.4 | 445.5 | 447.3 | 448.1 | 422.7 | 401.5
3520.1 | 3380.1 | 316.7 | 405.6 | 413.4 | 404.7 | 444.2 | 445.3 | 447.1 | 447.9 | 422.5 | 401.5
3521.1 | 3381.1 | 316.3 | 405.3 | 413.1 | 404.5 | 444 | 445.1 | 446.9 | 447.7 | 422.3 | 401.3
3522.1 | 3382.1 | 316 | 405.1 | 412.9 | 404.3 | 443.8 | 444.9 | 446.7 | 447.5 | 422.2 | 401.1
3523.1 | 3383.1 | 315.7 | 404.9 | 412.6 | 404.1 | 443.6 | 444.7 | 446.6 | 447.3 | 422 | 401
3524.1 | 3384.1 | 315.4 | 404.7 | 412.3 | 403.9 | 443.4 | 444.5 | 446.4 | 447.1 | 421.8 | 400.9
3525.1 | 3385.1 | 315.1 | 404.4 | 412.1 | 403.6 | 443.2 | 444.3 | 446.2 | 447 | 421.7 | 400.7
3526.1 | 3386.1 | 314.7 | 404.2 | 411.9 | 403.4 | 443 | 444.1 | 446 | 446.8 | 421.5 | 400.6
3527.1 | 3387.1 | 314.4 | 403.9 | 411.6 | 403.2 | 442.8 | 443.9 | 445.8 | 446.6 | 421.4 | 400.5
3528.1 | 3388.1 | 314.1 | 403.7 | 411.4 | 403 | 442.6 | 443.7 | 445.6 | 446.4 | 421.3 | 400.4
3529.1 | 3389.1 | 313.9 | 403.5 | 411.1 | 402.8 | 442.4 | 443.5 | 445.4 | 446.2 | 421.1 | 400.2
3530.1 | 3390.1 | 313.6 | 403.2 | 410.9 | 402.6 | 442.2 | 443.3 | 445.3 | 445.9 | 421 | 400
3531.1 | 3391.1 | 313.3 | 403 | 410.6 | 402.4 | 442 | 443.1 | 445.1 | 445.7 | 420.8 | 399.9
3532.1 | 3392.1 | 313 | 402.8 | 410.3 | 402.2 | 441.8 | 442.9 | 444.9 | 445.5 | 420.7 | 399.8
3533.1 | 3393.1 | 312.7 | 402.5 | 410.1 | 402 | 441.5 | 442.7 | 444.7 | 445.4 | 420.5 | 399.6
3534.1 | 3394.1 | 312.4 | 402.3 | 409.8 | 401.8 | 441.4 | 442.5 | 444.5 | 445.2 | 420.3 | 399.5
3535.1 | 3395.1 | 312.1 | 402.1 | 409.6 | 401.6 | 441.2 | 442.3 | 444.3 | 445 | 420.2 | 399.4
3536.1 | 3396.1 | 311.8 | 401.9 | 409.3 | 401.3 | 441 | 442.1 | 444.1 | 444.9 | 420.1 | 399.2
3537.1 | 3397.1 | 311.5 | 401.9 | 408.6 | 401.3 | 441.5 | 442.1 | 443.9 | 444.6 | 419.8 | 399.8
3538.1 | 3398.1 | 311.2 | 402 | 407.8 | 401.3 | 442.1 | 442.1 | 443.7 | 444.3 | 419.6 | 400.3
3539.1 | 3399.1 | 310.9 | 401.7 | 407.6 | 401.1 | 441.9 | 441.9 | 443.5 | 444.1 | 419.5 | 400.2
3540.1 | 3400.1 | 310.6 | 401.5 | 407.4 | 400.9 | 441.6 | 441.7 | 443.3 | 444 | 419.4 | 400
3541.1 | 3401.1 | 310.3 | 401.2 | 407.1 | 400.6 | 441.5 | 441.5 | 443.1 | 443.8 | 419.2 | 399.9
3542.1 | 3402.1 | 310 | 401 | 406.8 | 400.4 | 441.3 | 441.3 | 442.9 | 443.6 | 419.1 | 399.8
3543.1 | 3403.1 | 309.7 | 400.8 | 406.6 | 400.2 | 441.1 | 441.1 | 442.7 | 443.4 | 418.9 | 399.6
3544.1 | 3404.1 | 309.4 | 400.6 | 406.3 | 400 | 440.9 | 440.9 | 442.5 | 443.3 | 418.7 | 399.5
3545.1 | 3405.1 | 309.1 | 400.3 | 406 | 399.8 | 440.7 | 440.7 | 442.3 | 443.1 | 418.5 | 399.4
3546.1 | 3406.1 | 308.8 | 400.1 | 405.8 | 399.5 | 440.5 | 440.5 | 442.1 | 442.9 | 418.4 | 399.2
3547.1 | 3407.1 | 308.5 | 399.9 | 405.5 | 399.3 | 440.3 | 440.3 | 442 | 442.7 | 418.2 | 399.1
3548.1 | 3408.1 | 308.2 | 399.7 | 405.2 | 399.1 | 440.1 | 440.1 | 441.8 | 442.6 | 418 | 399
3549.1 | 3409.1 | 307.9 | 399.5 | 404.9 | 398.9 | 439.9 | 439.9 | 441.6 | 442.3 | 417.9 | 398.9
3550.1 | 3410.1 | 307.6 | 399.2 | 404.8 | 398.7 | 439.7 | 439.7 | 441.4 | 442.2 | 417.7 | 398.7
3551.1 | 3411.1 | 307.3 | 399 | 404.5 | 398.5 | 439.4 | 439.5 | 441.2 | 442 | 417.6 | 398.5
3552.1 | 3412.1 | 307.1 | 398.7 | 404.2 | 398.3 | 439.3 | 439.3 | 441 | 441.8 | 417.5 | 398.4
3553.1 | 3413.1 | 306.8 | 398.5 | 404 | 398 | 439.1 | 439.1 | 440.8 | 441.6 | 417.3 | 398.2
3554.1 | 3414.1 | 306.5 | 398.2 | 403.8 | 397.8 | 438.8 | 438.9 | 440.6 | 441.5 | 417.1 | 398.1
3555.1 | 3415.1 | 306.2 | 398.1 | 403.5 | 397.6 | 438.7 | 438.7 | 440.4 | 441.3 | 417 | 398
3556.1 | 3416.1 | 305.9 | 397.8 | 403.2 | 397.4 | 438.5 | 438.5 | 440.2 | 441.1 | 416.8 | 397.9
3557.1 | 3417.1 | 305.6 | 397.6 | 403 | 397.1 | 438.2 | 438.3 | 440 | 440.9 | 416.6 | 397.7
3558.1 | 3418.1 | 305.3 | 397.3 | 402.8 | 396.9 | 438 | 438.1 | 439.8 | 440.7 | 416.5 | 397.6
3559.1 | 3419.1 | 305 | 397.1 | 402.5 | 396.7 | 437.8 | 437.9 | 439.7 | 440.5 | 416.3 | 397.5
3560.1 | 3420.1 | 304.7 | 396.9 | 402.2 | 396.5 | 437.6 | 437.7 | 439.5 | 440.4 | 416.2 | 397.3
3561.1 | 3421.1 | 304.4 | 396.7 | 402 | 396.3 | 437.4 | 437.5 | 439.3 | 440.2 | 416 | 397.1
3562.1 | 3422.1 | 304.1 | 396.5 | 401.7 | 396.1 | 437.3 | 437.3 | 439.1 | 440 | 415.8 | 397.1
3563.1 | 3423.1 | 303.8 | 396.2 | 401.5 | 395.9 | 437 | 437.1 | 438.9 | 439.8 | 415.7 | 396.9
3564.1 | 3424.1 | 303.5 | 396 | 401.2 | 395.7 | 436.8 | 436.9 | 438.7 | 439.6 | 415.6 | 396.7
3565.1 | 3425.1 | 303.2 | 395.8 | 401 | 395.5 | 436.6 | 436.7 | 438.5 | 439.4 | 415.5 | 396.6
3566.1 | 3426.1 | 302.9 | 395.6 | 400.7 | 395.2 | 436.4 | 436.5 | 438.3 | 439.3 | 415.3 | 396.5
3567.1 | 3427.1 | 302.7 | 395.3 | 400.5 | 395 | 436.2 | 436.3 | 438.1 | 439 | 415.1 | 396.3
3568.1 | 3428.1 | 302.4 | 395.1 | 400.2 | 394.8 | 436 | 436.1 | 437.9 | 438.8 | 414.9 | 396.2
3569.1 | 3429.1 | 302.1 | 394.9 | 399.9 | 394.6 | 435.9 | 435.9 | 437.7 | 438.6 | 414.6 | 396.2
3570.1 | 3430.1 | 301.8 | 394.7 | 399.6 | 394.4 | 435.8 | 435.7 | 437.5 | 438.4 | 414.5 | 396.1
3571.1 | 3431.1 | 301.5 | 394.5 | 399.4 | 394.2 | 435.5 | 435.5 | 437.3 | 438.3 | 414.4 | 395.9
3572.1 | 3432.1 | 301.3 | 394.2 | 399.2 | 394 | 435.3 | 435.3 | 437.1 | 438.1 | 414.3 | 395.8
3573.1 | 3433.1 | 301 | 394.1 | 398.9 | 393.8 | 435.2 | 435.1 | 436.9 | 437.9 | 414.1 | 395.7
3574.1 | 3434.1 | 300.7 | 393.8 | 398.7 | 393.5 | 434.9 | 434.9 | 436.7 | 437.7 | 413.9 | 395.5
3575.1 | 3435.1 | 300.5 | 393.6 | 398.4 | 393.3 | 434.7 | 434.7 | 436.6 | 437.5 | 413.8 | 395.3
3576.1 | 3436.1 | 300.2 | 393.4 | 398.2 | 393.1 | 434.5 | 434.5 | 436.4 | 437.4 | 413.6 | 395.2
3577.1 | 3437.1 | 299.9 | 393.2 | 397.9 | 392.9 | 434.3 | 434.3 | 436.2 | 437.2 | 413.4 | 395.1
3578.1 | 3438.1 | 299.6 | 392.9 | 397.8 | 392.7 | 434 | 434 | 436 | 437 | 413.4 | 394.8
3579.1 | 3439.1 | 299.3 | 392.7 | 397.5 | 392.5 | 433.7 | 433.8 | 435.8 | 436.8 | 413.5 | 394.7
3580.1 | 3440.1 | 299.1 | 392.6 | 397.1 | 392.3 | 433.9 | 433.7 | 435.6 | 436.6 | 413.7 | 394.8
3581.1 | 3441.1 | 298.8 | 392.3 | 396.9 | 392.1 | 433.5 | 433.5 | 435.4 | 436.5 | 413.7 | 394.6
3582.1 | 3442.1 | 298.5 | 392 | 396.8 | 391.8 | 433.2 | 433.2 | 435.2 | 436.3 | 413.4 | 394.3
3583.1 | 3443.1 | 298.2 | 391.8 | 396.4 | 391.6 | 433.1 | 433.1 | 435 | 436 | 413 | 394.3
3584.1 | 3444.1 | 298 | 391.6 | 396.2 | 391.4 | 432.9 | 432.9 | 434.8 | 435.8 | 412.6 | 394.2
3585.1 | 3445.1 | 297.7 | 391.4 | 396 | 391.2 | 432.7 | 432.7 | 434.6 | 435.7 | 412.3 | 394
3586.1 | 3446.1 | 297.4 | 391.1 | 395.8 | 391 | 432.4 | 432.4 | 434.4 | 435.5 | 412.1 | 393.8
3587.1 | 3447.1 | 297.2 | 391 | 395.4 | 390.8 | 432.3 | 432.3 | 434.2 | 435.3 | 411.8 | 393.8
3588.1 | 3448.1 | 296.9 | 390.7 | 395.3 | 390.5 | 432 | 432 | 434 | 435.2 | 411.6 | 393.5
3589.1 | 3449.1 | 296.6 | 390.5 | 395 | 390.3 | 431.8 | 431.8 | 433.8 | 435 | 411.4 | 393.4
3590.1 | 3450.1 | 296.4 | 390.3 | 394.8 | 390.1 | 431.6 | 431.6 | 433.6 | 434.8 | 411.3 | 393.3
3591.1 | 3451.1 | 296.1 | 390.1 | 394.4 | 389.9 | 431.6 | 431.5 | 433.4 | 434.5 | 411.1 | 393.4
3592.1 | 3452.1 | 295.8 | 389.8 | 394.3 | 389.7 | 431.2 | 431.2 | 433.2 | 434.3 | 410.9 | 393
3593.1 | 3453.1 | 295.6 | 389.6 | 394 | 389.5 | 431.1 | 431 | 433 | 434.1 | 410.7 | 392.9
3594.1 | 3454.1 | 295.3 | 389.4 | 393.8 | 389.3 | 430.9 | 430.8 | 432.8 | 433.9 | 410.5 | 392.8
3595.1 | 3455.1 | 295 | 389.3 | 393.4 | 389.1 | 430.8 | 430.7 | 432.6 | 433.7 | 410.4 | 392.8
3596.1 | 3456.1 | 294.8 | 389 | 393.2 | 388.9 | 430.5 | 430.4 | 432.4 | 433.5 | 410.3 | 392.6
3597.1 | 3457.1 | 294.5 | 388.8 | 392.9 | 388.7 | 430.3 | 430.3 | 432.2 | 433.3 | 410.1 | 392.5
3598.1 | 3458.1 | 294.2 | 388.6 | 392.6 | 388.5 | 430.3 | 430.1 | 432 | 433 | 410 | 392.5
3599.1 | 3459.1 | 293.9 | 388.3 | 392.5 | 388.3 | 429.8 | 429.8 | 431.8 | 432.8 | 409.8 | 392.1
3600.1 | 3460.1 | 293.7 | 388.1 | 392.2 | 388.1 | 429.8 | 429.6 | 431.6 | 432.7 | 409.6 | 392.1
3601.1 | 3461.1 | 293.4 | 387.9 | 392.1 | 387.8 | 429.4 | 429.4 | 431.5 | 432.5 | 409.5 | 391.8
3602.1 | 3462.1 | 293.2 | 387.8 | 391.7 | 387.7 | 429.5 | 429.3 | 431.2 | 432.3 | 409.3 | 391.9
3603.1 | 3463.1 | 292.9 | 387.4 | 391.6 | 387.4 | 429 | 429 | 431.1 | 432.1 | 409.2 | 391.5
3604.1 | 3464.1 | 292.7 | 387.3 | 391.2 | 387.3 | 429 | 428.9 | 430.9 | 431.9 | 409 | 391.6
3605.1 | 3465.1 | 292.4 | 387 | 391 | 387 | 428.7 | 428.6 | 430.7 | 431.8 | 408.9 | 391.4
3606.1 | 3466.1 | 292.1 | 386.8 | 390.8 | 386.8 | 428.5 | 428.4 | 430.5 | 431.6 | 408.7 | 391.2
3607.1 | 3467.1 | 291.9 | 386.6 | 390.6 | 386.6 | 428.3 | 428.2 | 430.3 | 431.4 | 408.6 | 391.1
3608.1 | 3468.1 | 291.6 | 386.4 | 390.4 | 386.4 | 428.1 | 428 | 430.1 | 431.2 | 408.5 | 390.9
3609.1 | 3469.1 | 291.3 | 386.2 | 390 | 386.2 | 428 | 427.8 | 429.9 | 431 | 408.3 | 390.9
3610.1 | 3470.1 | 291.1 | 385.9 | 389.9 | 386 | 427.6 | 427.6 | 429.7 | 430.8 | 408.2 | 390.5
3611.1 | 3471.1 | 290.8 | 385.8 | 389.5 | 385.9 | 427.6 | 427.4 | 429.5 | 430.5 | 407.9 | 390.6
3612.1 | 3472.1 | 290.5 | 385.4 | 389.5 | 385.6 | 427.2 | 427.2 | 429.3 | 430.4 | 407.8 | 390.2
3613.1 | 3473.1 | 290.3 | 385.3 | 389.1 | 385.4 | 427.2 | 427 | 429.1 | 430.2 | 407.6 | 390.3
3614.1 | 3474.1 | 290 | 385 | 389 | 385.2 | 426.8 | 426.8 | 428.9 | 430 | 407.5 | 390
3615.1 | 3475.1 | 289.8 | 384.9 | 388.6 | 385 | 426.8 | 426.6 | 428.7 | 429.8 | 407.3 | 390
3616.1 | 3476.1 | 289.5 | 384.6 | 388.5 | 384.8 | 426.4 | 426.4 | 428.5 | 429.6 | 407.2 | 389.7
3617.1 | 3477.1 | 289.2 | 384.3 | 388.3 | 384.6 | 426.1 | 426.2 | 428.4 | 429.4 | 407.1 | 389.5
3618.1 | 3478.1 | 289 | 384.2 | 388 | 384.4 | 426.1 | 426 | 428.2 | 429.2 | 407 | 389.5
3619.1 | 3479.1 | 288.7 | 383.9 | 387.7 | 384.2 | 425.8 | 425.8 | 428 | 429.1 | 406.8 | 389.3
3620.1 | 3480.1 | 288.4 | 383.7 | 387.5 | 384 | 425.7 | 425.6 | 427.8 | 428.9 | 406.7 | 389.1
3621.1 | 3481.1 | 288.2 | 383.5 | 387.3 | 383.7 | 425.3 | 425.3 | 427.6 | 428.7 | 406.5 | 388.9
3622.1 | 3482.1 | 287.9 | 383.4 | 386.9 | 383.6 | 425.4 | 425.2 | 427.4 | 428.4 | 406.4 | 389
3623.1 | 3483.1 | 287.6 | 383 | 386.9 | 383.3 | 424.9 | 424.9 | 427.2 | 428.3 | 406.3 | 388.6
3624.1 | 3484.1 | 287.3 | 382.9 | 386.5 | 383.2 | 424.9 | 424.8 | 427 | 428.1 | 406.1 | 388.6
3625.1 | 3485.1 | 287.1 | 382.6 | 386.4 | 382.9 | 424.5 | 424.5 | 426.8 | 427.9 | 406 | 388.3
3626.1 | 3486.1 | 286.8 | 382.4 | 386 | 382.8 | 424.4 | 424.4 | 426.6 | 427.8 | 405.8 | 388.3
3627.1 | 3487.1 | 286.6 | 382.2 | 385.9 | 382.5 | 424.1 | 424.1 | 426.4 | 427.7 | 405.6 | 388
3628.1 | 3488.1 | 286.3 | 381.9 | 385.6 | 382.3 | 423.9 | 423.9 | 426.2 | 427.4 | 405.5 | 387.9
3629.1 | 3489.1 | 286.1 | 381.8 | 385.4 | 382.1 | 423.8 | 423.8 | 426 | 427.2 | 405.3 | 387.9
3630.1 | 3490.1 | 285.9 | 381.5 | 385.1 | 381.9 | 423.5 | 423.5 | 425.8 | 427 | 405.1 | 387.7
3631.1 | 3491.1 | 285.6 | 381.3 | 384.8 | 381.7 | 423.4 | 423.3 | 425.6 | 426.9 | 405 | 387.5
3632.1 | 3492.1 | 285.4 | 381.1 | 384.7 | 381.5 | 423.1 | 423.1 | 425.4 | 426.8 | 404.9 | 387.3
3633.1 | 3493.1 | 285.1 | 381 | 384.3 | 381.3 | 423.1 | 423 | 425.2 | 426.6 | 404.7 | 387.4
3634.1 | 3494.1 | 284.9 | 380.6 | 384.3 | 381 | 422.6 | 422.7 | 425 | 426.4 | 404.6 | 386.9
3635.1 | 3495.1 | 284.6 | 380.5 | 383.9 | 380.9 | 422.6 | 422.6 | 424.8 | 426.2 | 404.3 | 387
3636.1 | 3496.1 | 284.4 | 380.2 | 383.8 | 380.6 | 422.2 | 422.3 | 424.6 | 426 | 404.2 | 386.7
3637.1 | 3497.1 | 284.1 | 380 | 383.5 | 380.4 | 422.1 | 422.1 | 424.4 | 425.8 | 404 | 386.7
3638.1 | 3498.1 | 283.9 | 379.8 | 383.3 | 380.2 | 421.8 | 421.9 | 424.2 | 425.6 | 403.8 | 386.4
3639.1 | 3499.1 | 283.6 | 379.6 | 383.1 | 380 | 421.7 | 421.7 | 424 | 425.3 | 403.6 | 386.3
3640.1 | 3500.1 | 283.4 | 379.4 | 382.8 | 379.8 | 421.5 | 421.5 | 423.8 | 425.1 | 403.5 | 386.2
3641.1 | 3501.1 | 283.1 | 379.1 | 382.7 | 379.6 | 421.1 | 421.3 | 423.7 | 424.9 | 403.3 | 385.9
3642.1 | 3502.1 | 282.8 | 378.9 | 382.3 | 379.4 | 421.1 | 421.1 | 423.4 | 424.6 | 403.1 | 386
3643.1 | 3503.1 | 282.6 | 378.7 | 382.2 | 379.2 | 420.8 | 420.9 | 423.3 | 424.5 | 403.1 | 385.7
3644.1 | 3504.1 | 282.4 | 378.6 | 381.8 | 379.1 | 420.8 | 420.7 | 423 | 424.3 | 402.9 | 385.8
3645.1 | 3505.1 | 282.1 | 378.2 | 381.8 | 378.7 | 420.3 | 420.4 | 422.9 | 424.2 | 402.8 | 385.3
3646.1 | 3506.1 | 281.9 | 378.2 | 381.3 | 378.6 | 420.5 | 420.4 | 422.6 | 423.9 | 402.6 | 385.6
3647.1 | 3507.1 | 281.6 | 377.9 | 381.2 | 378.4 | 420.1 | 420.1 | 422.5 | 423.7 | 402.4 | 385.2
3648.1 | 3508.1 | 281.4 | 377.7 | 380.9 | 378.2 | 420 | 419.9 | 422.3 | 423.5 | 402.2 | 385.1
3649.1 | 3509.1 | 281.1 | 377.4 | 380.7 | 378 | 419.7 | 419.7 | 422.1 | 423.3 | 402 | 384.9
3650.1 | 3510.1 | 280.9 | 377.2 | 380.6 | 377.8 | 419.4 | 419.5 | 421.9 | 423.1 | 401.8 | 384.7
3651.1 | 3511.1 | 280.6 | 377 | 380.3 | 377.6 | 419.2 | 419.3 | 421.7 | 422.8 | 401.7 | 384.6
3652.1 | 3512.1 | 280.4 | 376.8 | 380.2 | 377.3 | 419 | 419 | 421.5 | 422.6 | 401.6 | 384.3
3653.1 | 3513.1 | 280.2 | 376.7 | 379.8 | 377.2 | 419 | 418.9 | 421.3 | 422.4 | 401.4 | 384.5

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 50 |  |  | 2006-09-01 | 8:09
38961.3386 | 1 | 0 | 1 | TS & TP Mix | 7-C | Conduit
38961.3391 | 1 | 0 | 1 | 525 C | 23 kW/m2 |  | Bundle
38961.3395 | 1 | 0 | 1
38961.34 | 1 | 0 | 1
38961.3405 | 1 | 0 | 1
38961.341 | 1 | 0 | 1
38961.3415 | 1 | 0 | 1
38961.342 | 1 | 0 | 1
38961.3425 | 1 | 0 | 1
38961.3429 | 1 | 0 | 1
38961.3434 | 1 | 0 | 1
38961.3439 | 1 | 0 | 1
38961.3444 | 1 | 0 | 1
38961.3449 | 1 | 0 | 1
38961.3454 | 1 | 0 | 1
38961.3459 | 1 | 0 | 1
38961.3463 | 1 | 0 | 1
38961.3468 | 1 | 0 | 1
38961.3473 | 1 | 0 | 1
38961.3478 | 1 | 0 | 1
38961.3483 | 1 | 0 | 1
38961.3488 | 1 | 0 | 1
38961.3493 | 2 | 0 | 1
38961.3497 | 1 | 0 | 1
38961.3502 | 1 | 0 | 1
38961.3507 | 1 | 0 | 1
38961.3512 | 1 | 0 | 1
38961.3517 | 1 | 0 | 1
38961.3522 | 1 | 0 | 1
38961.3527 | 1062 | 1038 | 1
38961.3531 | 1 | 0 | 1
38961.3536 | 1 | 0 | 1
38961.3541 | 1 | 0 | 1
38961.3546 | 1 | 0 | 1
38961.3551 | 1 | 0 | 1
38961.3556 | 1165 | 1147 | 1
38961.3561 | 1017 | 924 | 1
38961.3566 | 31 | 32 | 1
38961.357 | 1 | 0 | 1
38961.3575 | 1 | 0 | 1
38961.358 | 942 | 919 | 1
38961.3585 | 1115 | 1090 | 1
38961.359 | 3 | 1 | 1
38961.3595 | 3 | 0 | 1
38961.36 | 2 | 0 | 1
38961.3604 | 242 | 271 | 1
38961.3609 | 3 | 0 | 1
38961.3614 | 27 | 24 | 1
38961.3619 | 6 | 3 | 1
38961.3624 | 929 | 904 | 1
38961.3629 | 1131 | 1102 | 1
38961.3633 | 1109 | 1080 | 1
38961.3638 | 1080 | 933 | 1
38961.3643 | 1061 | 1028 | 1
38961.3648 | 1204 | 979 | 1
38961.3653 | 956 | 922 | 1
38961.3658 | 960 | 1064 | 1
38961.3663 | 1039 | 1000 | 1
38961.3668 | 1058 | 967 | 1
38961.3672 | 973 | 877 | 1
38961.3677 | 1219 | 1139 | 1
38961.3682 | 1132 | 1086 | 1
38961.3687 | 1472 | 806 | 1
38961.3692 | 1662 | 246 | 1
38961.3697 | 1734 | 212 | 1
38961.3702 | 1823 | 177 | 1
38961.3706 | 2064 | 171 | 1
38961.3711 | 2047 | 146 | 1
38961.3716 | 1801 | 122 | 1
38961.3721 | 2225 | 131 | 1
38961.3726 | 2064 | 113 | 1
38961.3731 | 1981 | 101 | 1
38961.3736 | 2074 | 109 | 1
38961.374 | 1911 | 92 | 1
38961.3745 | 2050 | 94 | 1
38961.375 | 2119 | 93 | 1
38961.3755 | 2130 | 92 | 1
38961.376 | 1886 | 80 | 1
38961.3765 | 2133 | 90 | 1
38961.377 | 2145 | 94 | 1
38961.3774 | 1788 | 77 | 1
38961.3779 | 2104 | 88 | 1
38961.3784 | 1863 | 74 | 1
38961.3789 | 1780 | 75 | 1
38961.3794 | 2023 | 77 | 1
38961.3799 | 2088 | 81 | 1
38961.3804 | 2000 | 75 | 1
1
38961.3386 | 1 | 0 | 2
38961.3391 | 1 | 0 | 2
38961.3395 | 1 | 0 | 2
38961.34 | 1 | 0 | 2
38961.3405 | 1 | 0 | 2
38961.341 | 1 | 0 | 2
38961.3415 | 1 | 0 | 2
38961.342 | 1 | 0 | 2
38961.3425 | 1 | 0 | 2
38961.343 | 1 | 0 | 2
38961.3434 | 1 | 0 | 2
38961.3439 | 1 | 0 | 2
38961.3444 | 1 | 0 | 2
38961.3449 | 1 | 0 | 2
38961.3454 | 1 | 0 | 2
38961.3459 | 1 | 0 | 2
38961.3464 | 1 | 0 | 2
38961.3468 | 1 | 0 | 2
38961.3473 | 1 | 0 | 2
38961.3478 | 1 | 0 | 2
38961.3483 | 1 | 0 | 2
38961.3488 | 1 | 0 | 2
38961.3493 | 1 | 0 | 2
38961.3498 | 1 | 0 | 2
38961.3502 | 1 | 0 | 2
38961.3507 | 1 | 0 | 2
38961.3512 | 1 | 0 | 2
38961.3517 | 1 | 0 | 2
38961.3522 | 1 | 0 | 2
38961.3527 | 1148 | 1126 | 2
38961.3532 | 1 | 0 | 2
38961.3536 | 1 | 0 | 2
38961.3541 | 1 | 0 | 2
38961.3546 | 1 | 0 | 2
38961.3551 | 1 | 0 | 2
38961.3556 | 1167 | 1099 | 2
38961.3561 | 935 | 913 | 2
38961.3566 | 1 | 0 | 2
38961.357 | 1 | 0 | 2
38961.3575 | 1 | 0 | 2
38961.358 | 1104 | 1155 | 2
38961.3585 | 956 | 1071 | 2
38961.359 | 2 | 0 | 2
38961.3595 | 2 | 0 | 2
38961.36 | 2 | 0 | 2
38961.3605 | 2 | 0 | 2
38961.3609 | 2 | 0 | 2
38961.3614 | 139 | 144 | 2
38961.3619 | 1049 | 1020 | 2
38961.3624 | 1148 | 1180 | 2
38961.3629 | 1151 | 1187 | 2
38961.3634 | 1091 | 1161 | 2
38961.3639 | 1019 | 989 | 2
38961.3643 | 1117 | 1084 | 2
38961.3648 | 963 | 993 | 2
38961.3653 | 932 | 995 | 2
38961.3658 | 977 | 943 | 2
38961.3663 | 1188 | 1149 | 2
38961.3668 | 1222 | 1094 | 2
38961.3673 | 1078 | 971 | 2
38961.3677 | 1003 | 959 | 2
38961.3682 | 1349 | 1009 | 2
38961.3687 | 1247 | 586 | 2
38961.3692 | 1797 | 259 | 2
38961.3697 | 1758 | 205 | 2
38961.3702 | 1742 | 166 | 2
38961.3707 | 2146 | 173 | 2
38961.3711 | 1706 | 122 | 2
38961.3716 | 2036 | 138 | 2
38961.3721 | 2104 | 122 | 2
38961.3726 | 1981 | 106 | 2
38961.3731 | 1854 | 95 | 2
38961.3736 | 2002 | 95 | 2
38961.3741 | 1989 | 91 | 2
38961.3745 | 2181 | 101 | 2
38961.375 | 1978 | 84 | 2
38961.3755 | 2201 | 94 | 2
38961.376 | 2012 | 83 | 2
38961.3765 | 1893 | 79 | 2
38961.377 | 2057 | 78 | 2
38961.3775 | 1929 | 82 | 2
38961.378 | 2162 | 95 | 2
38961.3784 | 2226 | 70 | 2
38961.3789 | 1976 | 76 | 2
38961.3794 | 1885 | 70 | 2
38961.3799 | 1947 | 73 | 2
38961.3804 | 1826 | 71 | 2
2
38961.3386 | 1 | 0 | 3
38961.3391 | 1 | 0 | 3
38961.3396 | 1 | 0 | 3
38961.3401 | 1 | 0 | 3
38961.3405 | 1 | 0 | 3
38961.341 | 1 | 0 | 3
38961.3415 | 1 | 0 | 3
38961.342 | 1 | 0 | 3
38961.3425 | 1 | 0 | 3
38961.343 | 1 | 0 | 3
38961.3435 | 1 | 0 | 3
38961.3439 | 1 | 0 | 3
38961.3444 | 1 | 0 | 3
38961.3449 | 1 | 0 | 3
38961.3454 | 1 | 0 | 3
38961.3459 | 1 | 1 | 3
38961.3464 | 1 | 0 | 3
38961.3469 | 1 | 0 | 3
38961.3473 | 1 | 0 | 3
38961.3478 | 1 | 0 | 3
38961.3483 | 1 | 0 | 3
38961.3488 | 1 | 0 | 3
38961.3493 | 1 | 0 | 3
38961.3498 | 1 | 0 | 3
38961.3503 | 1 | 0 | 3
38961.3507 | 1 | 0 | 3
38961.3512 | 1 | 0 | 3
38961.3517 | 1 | 0 | 3
38961.3522 | 1 | 0 | 3
38961.3527 | 1 | 2 | 3
38961.3532 | 1 | 0 | 3
38961.3537 | 1 | 0 | 3
38961.3541 | 1 | 0 | 3
38961.3546 | 1 | 0 | 3
38961.3551 | 1 | 0 | 3
38961.3556 | 1 | 2 | 3
38961.3561 | 2 | 2 | 3
38961.3566 | 1 | 0 | 3
38961.3571 | 1 | 0 | 3
38961.3575 | 1 | 0 | 3
38961.358 | 2 | 1 | 3
38961.3585 | 2 | 2 | 3
38961.359 | 2 | 0 | 3
38961.3595 | 2 | 0 | 3
38961.36 | 2 | 0 | 3
38961.3605 | 3 | 0 | 3
38961.3609 | 2 | 0 | 3
38961.3614 | 2 | 0 | 3
38961.3619 | 2 | 1 | 3
38961.3624 | 2 | 1 | 3
38961.3629 | 2 | 2 | 3
38961.3634 | 2 | 2 | 3
38961.3639 | 2 | 2 | 3
38961.3644 | 2 | 1 | 3
38961.3648 | 2 | 2 | 3
38961.3653 | 2 | 1 | 3
38961.3658 | 2 | 2 | 3
38961.3663 | 2 | 2 | 3
38961.3668 | 990 | 967 | 3
38961.3673 | 1172 | 1100 | 3
38961.3678 | 1117 | 998 | 3
38961.3682 | 1188 | 594 | 3
38961.3687 | 1270 | 968 | 3
38961.3692 | 2009 | 227 | 3
38961.3697 | 1702 | 148 | 3
38961.3702 | 2138 | 141 | 3
38961.3707 | 1948 | 104 | 3
38961.3712 | 2096 | 93 | 3
38961.3716 | 2204 | 86 | 3
38961.3721 | 1954 | 66 | 3
38961.3726 | 1751 | 55 | 3
38961.3731 | 2198 | 64 | 3
38961.3736 | 1778 | 47 | 3
38961.3741 | 1910 | 46 | 3
38961.3746 | 1963 | 47 | 3
38961.375 | 2155 | 48 | 3
38961.3755 | 2098 | 45 | 3
38961.376 | 1928 | 40 | 3
38961.3765 | 1816 | 41 | 3
38961.377 | 1817 | 43 | 3
38961.3775 | 1776 | 42 | 3
38961.378 | 2071 | 43 | 3
38961.3784 | 1910 | 36 | 3
38961.3789 | 2251 | 42 | 3
38961.3794 | 2249 | 32 | 3
38961.3799 | 2206 | 40 | 3
38961.3804 | 2229 | 38 | 3
3
38961.3386 | 1 | 0 | 4
38961.3391 | 1 | 0 | 4
38961.3396 | 1 | 0 | 4
38961.3401 | 1 | 0 | 4
38961.3406 | 1 | 1 | 4
38961.341 | 1 | 0 | 4
38961.3415 | 1 | 0 | 4
38961.342 | 1 | 0 | 4
38961.3425 | 1 | 0 | 4
38961.343 | 1 | 0 | 4
38961.3435 | 1 | 0 | 4
38961.344 | 1 | 0 | 4
38961.3444 | 1 | 0 | 4
38961.3449 | 1 | 0 | 4
38961.3454 | 1 | 0 | 4
38961.3459 | 1 | 0 | 4
38961.3464 | 1 | 0 | 4
38961.3469 | 1 | 0 | 4
38961.3474 | 1 | 0 | 4
38961.3478 | 1 | 0 | 4
38961.3483 | 1 | 0 | 4
38961.3488 | 1 | 0 | 4
38961.3493 | 1 | 0 | 4
38961.3498 | 1 | 0 | 4
38961.3503 | 1 | 0 | 4
38961.3508 | 1 | 0 | 4
38961.3512 | 1 | 0 | 4
38961.3517 | 1 | 0 | 4
38961.3522 | 1 | 0 | 4
38961.3527 | 1 | 1 | 4
38961.3532 | 1 | 0 | 4
38961.3537 | 1 | 0 | 4
38961.3542 | 1 | 0 | 4
38961.3547 | 1 | 0 | 4
38961.3551 | 1 | 0 | 4
38961.3556 | 1 | 1 | 4
38961.3561 | 1 | 1 | 4
38961.3566 | 1 | 0 | 4
38961.3571 | 1 | 0 | 4
38961.3576 | 1 | 0 | 4
38961.3581 | 2 | 0 | 4
38961.3585 | 2 | 1 | 4
38961.359 | 2 | 0 | 4
38961.3595 | 2 | 0 | 4
38961.36 | 2 | 0 | 4
38961.3605 | 2 | 0 | 4
38961.361 | 2 | 0 | 4
38961.3615 | 2 | 0 | 4
38961.3619 | 2 | 0 | 4
38961.3624 | 2 | 1 | 4
38961.3629 | 2 | 1 | 4
38961.3634 | 2 | 1 | 4
38961.3639 | 2 | 1 | 4
38961.3644 | 2 | 1 | 4
38961.3649 | 2 | 1 | 4
38961.3653 | 2 | 1 | 4
38961.3658 | 2 | 1 | 4
38961.3663 | 5 | 1 | 4
38961.3668 | 1122 | 1016 | 4
38961.3673 | 1042 | 940 | 4
38961.3678 | 1158 | 1025 | 4
38961.3683 | 1767 | 487 | 4
38961.3688 | 1105 | 1057 | 4
38961.3692 | 2146 | 210 | 4
38961.3697 | 2025 | 152 | 4
38961.3702 | 1759 | 98 | 4
38961.3707 | 1859 | 84 | 4
38961.3712 | 2186 | 83 | 4
38961.3717 | 1817 | 63 | 4
38961.3722 | 1887 | 54 | 4
38961.3726 | 2305 | 59 | 4
38961.3731 | 2320 | 56 | 4
38961.3736 | 1809 | 40 | 4
38961.3741 | 2118 | 42 | 4
38961.3746 | 1995 | 38 | 4
38961.3751 | 1976 | 37 | 4
38961.3756 | 2072 | 39 | 4
38961.376 | 2283 | 42 | 4
38961.3765 | 2311 | 41 | 4
38961.377 | 2154 | 44 | 4
38961.3775 | 2339 | 36 | 4
38961.378 | 2132 | 40 | 4
38961.3785 | 2168 | 36 | 4
38961.3789 | 2301 | 39 | 4
38961.3794 | 2323 | 35 | 4
38961.3799 | 1991 | 31 | 4
38961.3804 | 1927 | 30 | 4
4
38961.3386 | 1 | 0 | 5
38961.3391 | 1 | 0 | 5
38961.3396 | 1 | 0 | 5
38961.3401 | 1 | 0 | 5
38961.3406 | 1 | 0 | 5
38961.3411 | 1 | 0 | 5
38961.3415 | 1 | 0 | 5
38961.342 | 1 | 1 | 5
38961.3425 | 1 | 0 | 5
38961.343 | 1 | 0 | 5
38961.3435 | 1 | 0 | 5
38961.344 | 1 | 0 | 5
38961.3445 | 1 | 0 | 5
38961.3449 | 1 | 0 | 5
38961.3454 | 1 | 0 | 5
38961.3459 | 1 | 0 | 5
38961.3464 | 1 | 0 | 5
38961.3469 | 1 | 0 | 5
38961.3474 | 1 | 0 | 5
38961.3479 | 1 | 0 | 5
38961.3483 | 1 | 0 | 5
38961.3488 | 1 | 0 | 5
38961.3493 | 1 | 0 | 5
38961.3498 | 1 | 0 | 5
38961.3503 | 1 | 0 | 5
38961.3508 | 1 | 0 | 5
38961.3513 | 1 | 0 | 5
38961.3517 | 1 | 0 | 5
38961.3522 | 1 | 0 | 5
38961.3527 | 1 | 0 | 5
38961.3532 | 1 | 0 | 5
38961.3537 | 1 | 0 | 5
38961.3542 | 1 | 0 | 5
38961.3547 | 1 | 0 | 5
38961.3552 | 1 | 0 | 5
38961.3556 | 1 | 0 | 5
38961.3561 | 1 | 0 | 5
38961.3566 | 1 | 0 | 5
38961.3571 | 1 | 0 | 5
38961.3576 | 1 | 0 | 5
38961.3581 | 2 | 0 | 5
38961.3586 | 2 | 1 | 5
38961.359 | 2 | 0 | 5
38961.3595 | 2 | 0 | 5
38961.36 | 2 | 0 | 5
38961.3605 | 2 | 0 | 5
38961.361 | 2 | 0 | 5
38961.3615 | 2 | 0 | 5
38961.362 | 2 | 0 | 5
38961.3624 | 2 | 0 | 5
38961.3629 | 2 | 0 | 5
38961.3634 | 2 | 0 | 5
38961.3639 | 2 | 1 | 5
38961.3644 | 2 | 0 | 5
38961.3649 | 2 | 0 | 5
38961.3654 | 2 | 0 | 5
38961.3658 | 2 | 0 | 5
38961.3663 | 37 | 23 | 5
38961.3668 | 971 | 885 | 5
38961.3673 | 1185 | 1083 | 5
38961.3678 | 1107 | 1060 | 5
38961.3683 | 1265 | 857 | 5
38961.3688 | 932 | 890 | 5
38961.3692 | 1968 | 196 | 5
38961.3697 | 1892 | 145 | 5
38961.3702 | 1824 | 111 | 5
38961.3707 | 1928 | 97 | 5
38961.3712 | 2048 | 80 | 5
38961.3717 | 1949 | 64 | 5
38961.3722 | 1906 | 55 | 5
38961.3727 | 1774 | 48 | 5
38961.3731 | 1801 | 41 | 5
38961.3736 | 1850 | 39 | 5
38961.3741 | 2130 | 44 | 5
38961.3746 | 1947 | 36 | 5
38961.3751 | 1850 | 33 | 5
38961.3756 | 2147 | 36 | 5
38961.3761 | 1932 | 31 | 5
38961.3765 | 2242 | 38 | 5
38961.377 | 1913 | 34 | 5
38961.3775 | 1847 | 31 | 5
38961.378 | 2291 | 38 | 5
38961.3785 | 1950 | 28 | 5
38961.379 | 2250 | 31 | 5
38961.3795 | 2202 | 27 | 5
38961.3799 | 2115 | 27 | 5
38961.3804 | 2029 | 26 | 5
5
38961.3386 | 1 | 0 | 6
38961.3391 | 1 | 0 | 6
38961.3396 | 1 | 0 | 6
38961.3401 | 1 | 0 | 6
38961.3406 | 1 | 0 | 6
38961.3411 | 1 | 0 | 6
38961.3416 | 1 | 0 | 6
38961.342 | 1 | 0 | 6
38961.3425 | 2 | 0 | 6
38961.343 | 1 | 0 | 6
38961.3435 | 1 | 0 | 6
38961.344 | 1 | 0 | 6
38961.3445 | 1 | 0 | 6
38961.345 | 1 | 0 | 6
38961.3455 | 1 | 0 | 6
38961.3459 | 1 | 0 | 6
38961.3464 | 1 | 0 | 6
38961.3469 | 1 | 0 | 6
38961.3474 | 1 | 0 | 6
38961.3479 | 1 | 0 | 6
38961.3484 | 1 | 0 | 6
38961.3489 | 1 | 0 | 6
38961.3493 | 1 | 0 | 6
38961.3498 | 1 | 0 | 6
38961.3503 | 1 | 0 | 6
38961.3508 | 1 | 0 | 6
38961.3513 | 1 | 0 | 6
38961.3518 | 1 | 0 | 6
38961.3523 | 1 | 0 | 6
38961.3527 | 1 | 0 | 6
38961.3532 | 1 | 0 | 6
38961.3537 | 1 | 0 | 6
38961.3542 | 1 | 0 | 6
38961.3547 | 1 | 0 | 6
38961.3552 | 1 | 0 | 6
38961.3557 | 1 | 0 | 6
38961.3561 | 1 | 0 | 6
38961.3566 | 1 | 0 | 6
38961.3571 | 1 | 0 | 6
38961.3576 | 1 | 0 | 6
38961.3581 | 1 | 0 | 6
38961.3586 | 2 | 0 | 6
38961.3591 | 2 | 0 | 6
38961.3595 | 2 | 0 | 6
38961.36 | 2 | 0 | 6
38961.3605 | 2 | 0 | 6
38961.361 | 2 | 0 | 6
38961.3615 | 1 | 0 | 6
38961.362 | 2 | 0 | 6
38961.3625 | 2 | 0 | 6
38961.363 | 2 | 0 | 6
38961.3634 | 2 | 0 | 6
38961.3639 | 2 | 0 | 6
38961.3644 | 2 | 0 | 6
38961.3649 | 2 | 0 | 6
38961.3654 | 2 | 0 | 6
38961.3659 | 3 | 0 | 6
38961.3664 | 22 | 1 | 6
38961.3668 | 927 | 838 | 6
38961.3673 | 955 | 915 | 6
38961.3678 | 1143 | 1081 | 6
38961.3683 | 1046 | 928 | 6
38961.3688 | 1202 | 1092 | 6
38961.3693 | 1813 | 172 | 6
38961.3697 | 2087 | 146 | 6
38961.3702 | 1964 | 98 | 6
38961.3707 | 1875 | 77 | 6
38961.3712 | 2186 | 74 | 6
38961.3717 | 2222 | 63 | 6
38961.3722 | 2160 | 51 | 6
38961.3727 | 2341 | 50 | 6
38961.3731 | 2127 | 40 | 6
38961.3736 | 2344 | 31 | 6
38961.3741 | 2228 | 35 | 6
38961.3746 | 2363 | 35 | 6
38961.3751 | 1848 | 27 | 6
38961.3756 | 2189 | 32 | 6
38961.3761 | 2297 | 32 | 6
38961.3766 | 2370 | 35 | 6
38961.377 | 2146 | 34 | 6
38961.3775 | 2358 | 35 | 6
38961.378 | 2249 | 32 | 6
38961.3785 | 2364 | 24 | 6
38961.379 | 2327 | 28 | 6
38961.3795 | 1935 | 22 | 6
38961.38 | 2345 | 23 | 6
38961.3804 | 2041 | 22 | 6
6
38961.3387 | 1 | 0 | 7
38961.3391 | 1 | 0 | 7
38961.3396 | 1 | 0 | 7
38961.3401 | 5 | 0 | 7
38961.3406 | 1 | 0 | 7
38961.3411 | 1 | 0 | 7
38961.3416 | 1 | 0 | 7
38961.3421 | 1 | 0 | 7
38961.3425 | 1 | 0 | 7
38961.343 | 1 | 0 | 7
38961.3435 | 1 | 0 | 7
38961.344 | 1 | 0 | 7
38961.3445 | 1 | 0 | 7
38961.345 | 1 | 0 | 7
38961.3455 | 1 | 0 | 7
38961.3459 | 1 | 0 | 7
38961.3464 | 1 | 0 | 7
38961.3469 | 1 | 0 | 7
38961.3474 | 1 | 0 | 7
38961.3479 | 1 | 0 | 7
38961.3484 | 1 | 0 | 7
38961.3489 | 1 | 0 | 7
38961.3494 | 1 | 0 | 7
38961.3498 | 1 | 0 | 7
38961.3503 | 1 | 0 | 7
38961.3508 | 1 | 0 | 7
38961.3513 | 1 | 0 | 7
38961.3518 | 1 | 0 | 7
38961.3523 | 1 | 0 | 7
38961.3528 | 1 | 1 | 7
38961.3532 | 1 | 0 | 7
38961.3537 | 1 | 0 | 7
38961.3542 | 1 | 0 | 7
38961.3547 | 1 | 0 | 7
38961.3552 | 1 | 0 | 7
38961.3557 | 1 | 0 | 7
38961.3562 | 2 | 0 | 7
38961.3566 | 1 | 0 | 7
38961.3571 | 1 | 0 | 7
38961.3576 | 1 | 0 | 7
38961.3581 | 1 | 0 | 7
38961.3586 | 2 | 0 | 7
38961.3591 | 2 | 0 | 7
38961.3596 | 2 | 0 | 7
38961.36 | 2 | 0 | 7
38961.3605 | 1 | 0 | 7
38961.361 | 2 | 0 | 7
38961.3615 | 2 | 0 | 7
38961.362 | 2 | 0 | 7
38961.3625 | 2 | 0 | 7
38961.363 | 2 | 0 | 7
38961.3634 | 2 | 0 | 7
38961.3639 | 2 | 0 | 7
38961.3644 | 2 | 0 | 7
38961.3649 | 2 | 0 | 7
38961.3654 | 2 | 0 | 7
38961.3659 | 2 | 0 | 7
38961.3664 | 9 | 0 | 7
38961.3669 | 26 | 2 | 7
38961.3673 | 44 | 2 | 7
38961.3678 | 181 | 2 | 7
38961.3683 | 105 | 1 | 7
38961.3688 | 89 | 2 | 7
38961.3693 | 1664 | 0 | 7
38961.3698 | 2090 | 0 | 7
38961.3703 | 1824 | 0 | 7
38961.3707 | 1779 | 0 | 7
38961.3712 | 1790 | 0 | 7
38961.3717 | 1983 | 0 | 7
38961.3722 | 1841 | 0 | 7
38961.3727 | 2177 | 0 | 7
38961.3732 | 1758 | 0 | 7
38961.3737 | 2098 | 0 | 7
38961.3741 | 1848 | 0 | 7
38961.3746 | 1945 | 0 | 7
38961.3751 | 1878 | 0 | 7
38961.3756 | 2028 | 0 | 7
38961.3761 | 2240 | 0 | 7
38961.3766 | 1771 | 0 | 7
38961.3771 | 2282 | 0 | 7
38961.3775 | 1860 | 0 | 7
38961.378 | 2255 | 0 | 7
38961.3785 | 1925 | 0 | 7
38961.379 | 2252 | 0 | 7
38961.3795 | 2105 | 0 | 7
38961.38 | 2138 | 0 | 7
38961.3805 | 2237 | 0 | 7
7
38961.3387 | 1 | 0 | 8
38961.3392 | 1 | 0 | 8
38961.3397 | 1 | 0 | 8
38961.3401 | 1 | 0 | 8
38961.3406 | 1 | 0 | 8
38961.3411 | 1 | 0 | 8
38961.3416 | 1 | 0 | 8
38961.3421 | 1 | 0 | 8
38961.3426 | 1 | 0 | 8
38961.3431 | 1 | 0 | 8
38961.3435 | 1 | 0 | 8
38961.344 | 1 | 0 | 8
38961.3445 | 1 | 0 | 8
38961.345 | 1 | 0 | 8
38961.3455 | 1 | 0 | 8
38961.346 | 1 | 0 | 8
38961.3465 | 1 | 0 | 8
38961.3469 | 1 | 0 | 8
38961.3474 | 1 | 0 | 8
38961.3479 | 1 | 0 | 8
38961.3484 | 1 | 0 | 8
38961.3489 | 1 | 0 | 8
38961.3494 | 1 | 0 | 8
38961.3499 | 1 | 0 | 8
38961.3503 | 1 | 0 | 8
38961.3508 | 1 | 0 | 8
38961.3513 | 1 | 0 | 8
38961.3518 | 1 | 0 | 8
38961.3523 | 1 | 0 | 8
38961.3528 | 1 | 0 | 8
38961.3533 | 1 | 0 | 8
38961.3537 | 1 | 0 | 8
38961.3542 | 1 | 0 | 8
38961.3547 | 1 | 0 | 8
38961.3552 | 1 | 0 | 8
38961.3557 | 1 | 0 | 8
38961.3562 | 1 | 0 | 8
38961.3567 | 1 | 0 | 8
38961.3571 | 1 | 0 | 8
38961.3576 | 1673 | 0 | 8
38961.3581 | 2120 | 0 | 8
38961.3586 | 2175 | 0 | 8
38961.3591 | 2242 | 0 | 8
38961.3596 | 2366 | 0 | 8
38961.3601 | 2039 | 0 | 8
38961.3605 | 2371 | 0 | 8
38961.361 | 1986 | 0 | 8
38961.3615 | 1915 | 0 | 8
38961.362 | 2219 | 0 | 8
38961.3625 | 1961 | 0 | 8
38961.363 | 2130 | 0 | 8
38961.3635 | 1863 | 0 | 8
38961.3639 | 1931 | 0 | 8
38961.3644 | 1933 | 0 | 8
38961.3649 | 2172 | 0 | 8
38961.3654 | 2330 | 0 | 8
38961.3659 | 2367 | 0 | 8
38961.3664 | 2008 | 0 | 8
38961.3669 | 1910 | 1 | 8
38961.3673 | 2011 | 1 | 8
38961.3678 | 2208 | 1 | 8
38961.3683 | 2305 | 1 | 8
38961.3688 | 2044 | 1 | 8
38961.3693 | 2204 | 0 | 8
38961.3698 | 1901 | 0 | 8
38961.3703 | 1912 | 0 | 8
38961.3708 | 2094 | 0 | 8
38961.3712 | 2240 | 0 | 8
38961.3717 | 2023 | 0 | 8
38961.3722 | 1936 | 0 | 8
38961.3727 | 2357 | 0 | 8
38961.3732 | 1938 | 0 | 8
38961.3737 | 2149 | 0 | 8
38961.3742 | 2199 | 0 | 8
38961.3746 | 1941 | 0 | 8
38961.3751 | 2104 | 0 | 8
38961.3756 | 2354 | 0 | 8
38961.3761 | 1892 | 0 | 8
38961.3766 | 2089 | 0 | 8
38961.3771 | 2064 | 0 | 8
38961.3776 | 1983 | 0 | 8
38961.378 | 1844 | 0 | 8
38961.3785 | 2210 | 0 | 8
38961.379 | 2058 | 0 | 8
38961.3795 | 2333 | 0 | 8
38961.38 | 2278 | 0 | 8
38961.3805 | 2299 | 0 | 8
8
38961.3387 | 1 | 0 | 9
38961.3392 | 1 | 0 | 9
38961.3397 | 1 | 0 | 9
38961.3402 | 1 | 0 | 9
38961.3406 | 1 | 0 | 9
38961.3411 | 1 | 0 | 9
38961.3416 | 1 | 0 | 9
38961.3421 | 1 | 0 | 9
38961.3426 | 1 | 0 | 9
38961.3431 | 1 | 0 | 9
38961.3436 | 2 | 0 | 9
38961.344 | 1 | 0 | 9
38961.3445 | 1 | 0 | 9
38961.345 | 1 | 0 | 9
38961.3455 | 1 | 0 | 9
38961.346 | 1 | 0 | 9
38961.3465 | 1 | 0 | 9
38961.347 | 1 | 0 | 9
38961.3474 | 1 | 0 | 9
38961.3479 | 1 | 0 | 9
38961.3484 | 1 | 0 | 9
38961.3489 | 1 | 0 | 9
38961.3494 | 1 | 0 | 9
38961.3499 | 1 | 0 | 9
38961.3504 | 1 | 0 | 9
38961.3508 | 1 | 0 | 9
38961.3513 | 1 | 0 | 9
38961.3518 | 1 | 0 | 9
38961.3523 | 1 | 0 | 9
38961.3528 | 1 | 0 | 9
38961.3533 | 1 | 0 | 9
38961.3538 | 1 | 0 | 9
38961.3542 | 1 | 0 | 9
38961.3547 | 1 | 0 | 9
38961.3552 | 1 | 0 | 9
38961.3557 | 1 | 0 | 9
38961.3562 | 1 | 0 | 9
38961.3567 | 1 | 0 | 9
38961.3572 | 1 | 0 | 9
38961.3577 | 2 | 0 | 9
38961.3581 | 2 | 0 | 9
38961.3586 | 3 | 0 | 9
38961.3591 | 2 | 0 | 9
38961.3596 | 2 | 0 | 9
38961.3601 | 3 | 0 | 9
38961.3606 | 3 | 0 | 9
38961.3611 | 2 | 0 | 9
38961.3615 | 3 | 0 | 9
38961.362 | 3 | 0 | 9
38961.3625 | 2 | 0 | 9
38961.363 | 2 | 0 | 9
38961.3635 | 2 | 0 | 9
38961.364 | 2 | 0 | 9
38961.3645 | 2 | 0 | 9
38961.3649 | 2 | 0 | 9
38961.3654 | 2 | 0 | 9
38961.3659 | 2 | 0 | 9
38961.3664 | 10 | 0 | 9
38961.3669 | 29 | 1 | 9
38961.3674 | 45 | 1 | 9
38961.3679 | 481 | 1 | 9
38961.3683 | 55 | 1 | 9
38961.3688 | 244 | 1 | 9
38961.3693 | 1960 | 0 | 9
38961.3698 | 1774 | 0 | 9
38961.3703 | 2136 | 0 | 9
38961.3708 | 1697 | 0 | 9
38961.3713 | 1880 | 0 | 9
38961.3717 | 1819 | 0 | 9
38961.3722 | 2088 | 0 | 9
38961.3727 | 1930 | 0 | 9
38961.3732 | 1803 | 0 | 9
38961.3737 | 1918 | 0 | 9
38961.3742 | 1756 | 0 | 9
38961.3747 | 1950 | 0 | 9
38961.3752 | 2061 | 0 | 9
38961.3756 | 1999 | 0 | 9
38961.3761 | 2144 | 0 | 9
38961.3766 | 1896 | 0 | 9
38961.3771 | 1843 | 0 | 9
38961.3776 | 2275 | 1 | 9
38961.3781 | 1911 | 0 | 9
38961.3785 | 2001 | 0 | 9
38961.379 | 1953 | 0 | 9
38961.3795 | 2210 | 0 | 9
38961.38 | 2097 | 0 | 9
38961.3805 | 1837 | 0 | 9
9
38961.3387 | 1 | 0 | 10
38961.3392 | 1 | 0 | 10
38961.3397 | 1 | 0 | 10
38961.3402 | 1 | 0 | 10
38961.3406 | 1 | 0 | 10
38961.3411 | 1 | 0 | 10
38961.3416 | 1 | 0 | 10
38961.3421 | 1 | 0 | 10
38961.3426 | 1 | 0 | 10
38961.3431 | 1 | 0 | 10
38961.3436 | 1 | 0 | 10
38961.3441 | 1 | 0 | 10
38961.3445 | 1 | 0 | 10
38961.345 | 1 | 0 | 10
38961.3455 | 1 | 0 | 10
38961.346 | 1 | 0 | 10
38961.3465 | 1 | 0 | 10
38961.347 | 1 | 0 | 10
38961.3475 | 1 | 0 | 10
38961.3479 | 1 | 0 | 10
38961.3484 | 1 | 0 | 10
38961.3489 | 1 | 0 | 10
38961.3494 | 1 | 0 | 10
38961.3499 | 1 | 0 | 10
38961.3504 | 1 | 0 | 10
38961.3509 | 1 | 0 | 10
38961.3513 | 1 | 0 | 10
38961.3518 | 1 | 0 | 10
38961.3523 | 1 | 0 | 10
38961.3528 | 1 | 0 | 10
38961.3533 | 1 | 0 | 10
38961.3538 | 1 | 0 | 10
38961.3543 | 1 | 0 | 10
38961.3547 | 1 | 0 | 10
38961.3552 | 1 | 0 | 10
38961.3557 | 1 | 0 | 10
38961.3562 | 1 | 0 | 10
38961.3567 | 1 | 0 | 10
38961.3572 | 1 | 0 | 10
38961.3577 | 13 | 0 | 10
38961.3581 | 969 | 0 | 10
38961.3586 | 2189 | 0 | 10
38961.3591 | 1991 | 0 | 10
38961.3596 | 2141 | 0 | 10
38961.3601 | 2231 | 0 | 10
38961.3606 | 2299 | 0 | 10
38961.3611 | 1894 | 0 | 10
38961.3616 | 2011 | 0 | 10
38961.362 | 1906 | 0 | 10
38961.3625 | 1888 | 0 | 10
38961.363 | 1853 | 0 | 10
38961.3635 | 1856 | 0 | 10
38961.364 | 1929 | 0 | 10
38961.3645 | 2012 | 0 | 10
38961.365 | 2261 | 0 | 10
38961.3654 | 2200 | 0 | 10
38961.3659 | 2410 | 0 | 10
38961.3664 | 2290 | 0 | 10
38961.3669 | 2003 | 1 | 10
38961.3674 | 2367 | 1 | 10
38961.3679 | 2365 | 1 | 10
38961.3684 | 2381 | 1 | 10
38961.3688 | 2131 | 1 | 10
38961.3693 | 2400 | 1 | 10
38961.3698 | 2317 | 0 | 10
38961.3703 | 1939 | 0 | 10
38961.3708 | 2052 | 0 | 10
38961.3713 | 2376 | 0 | 10
38961.3718 | 1968 | 0 | 10
38961.3722 | 2019 | 0 | 10
38961.3727 | 2111 | 0 | 10
38961.3732 | 2069 | 0 | 10
38961.3737 | 2161 | 0 | 10
38961.3742 | 1934 | 0 | 10
38961.3747 | 2186 | 0 | 10
38961.3752 | 2359 | 0 | 10
38961.3756 | 2034 | 0 | 10
38961.3761 | 1932 | 0 | 10
38961.3766 | 2198 | 0 | 10
38961.3771 | 2288 | 0 | 10
38961.3776 | 2076 | 0 | 10
38961.3781 | 2027 | 0 | 10
38961.3786 | 1951 | 0 | 10
38961.3791 | 2246 | 0 | 10
38961.3795 | 1863 | 0 | 10
38961.38 | 2190 | 0 | 10
38961.3805 | 1900 | 0 | 10
10
38961.3387 | 1 | 0 | 11
38961.3392 | 1 | 0 | 11
38961.3397 | 1 | 0 | 11
38961.3402 | 1 | 0 | 11
38961.3407 | 1 | 0 | 11
38961.3412 | 1 | 0 | 11
38961.3416 | 1 | 0 | 11
38961.3421 | 1 | 0 | 11
38961.3426 | 1 | 0 | 11
38961.3431 | 1 | 0 | 11
38961.3436 | 1 | 0 | 11
38961.3441 | 1 | 0 | 11
38961.3446 | 1 | 0 | 11
38961.345 | 1 | 0 | 11
38961.3455 | 1 | 0 | 11
38961.346 | 1 | 0 | 11
38961.3465 | 1 | 0 | 11
38961.347 | 1 | 0 | 11
38961.348 | 1 | 0 | 11
38961.3484 | 1 | 0 | 11
38961.3489 | 1 | 0 | 11
38961.3494 | 1 | 0 | 11
38961.3499 | 1 | 0 | 11
38961.3504 | 1 | 0 | 11
38961.3509 | 1 | 0 | 11
38961.3514 | 1 | 0 | 11
38961.3519 | 1 | 0 | 11
38961.3523 | 1 | 0 | 11
38961.3528 | 1 | 0 | 11
38961.3533 | 1 | 0 | 11
38961.3538 | 1 | 0 | 11
38961.3543 | 1 | 0 | 11
38961.3548 | 1 | 0 | 11
38961.3553 | 1 | 0 | 11
38961.3557 | 1 | 0 | 11
38961.3562 | 1 | 0 | 11
38961.3567 | 1 | 0 | 11
38961.3572 | 1 | 0 | 11
38961.3577 | 1 | 0 | 11
38961.3582 | 2 | 0 | 11
38961.3587 | 3 | 0 | 11
38961.3591 | 3 | 0 | 11
38961.3596 | 2 | 0 | 11
38961.3601 | 3 | 0 | 11
38961.3606 | 2 | 0 | 11
38961.3611 | 3 | 0 | 11
38961.3616 | 3 | 0 | 11
38961.3621 | 3 | 0 | 11
38961.3625 | 2 | 0 | 11
38961.363 | 2 | 0 | 11
38961.3635 | 2 | 0 | 11
38961.364 | 2 | 0 | 11
38961.3645 | 2 | 0 | 11
38961.365 | 2 | 0 | 11
38961.3655 | 2 | 0 | 11
38961.3659 | 3 | 0 | 11
38961.3664 | 82 | 56 | 11
38961.3669 | 1050 | 1025 | 11
38961.3674 | 1149 | 1098 | 11
38961.3679 | 1157 | 1090 | 11
38961.3684 | 1036 | 899 | 11
38961.3689 | 1614 | 646 | 11
38961.3693 | 2011 | 203 | 11
38961.3698 | 1685 | 132 | 11
38961.3703 | 2158 | 103 | 11
38961.3708 | 1737 | 85 | 11
38961.3713 | 1746 | 75 | 11
38961.3718 | 2127 | 65 | 11
38961.3723 | 1781 | 63 | 11
38961.3727 | 1951 | 59 | 11
38961.3732 | 2232 | 49 | 11
38961.3737 | 2151 | 46 | 11
38961.3742 | 2147 | 50 | 11
38961.3747 | 2023 | 47 | 11
38961.3752 | 1760 | 38 | 11
38961.3757 | 2167 | 48 | 11
38961.3761 | 2036 | 43 | 11
38961.3766 | 1908 | 41 | 11
38961.3771 | 2208 | 47 | 11
38961.3776 | 2059 | 48 | 11
38961.3781 | 1964 | 42 | 11
38961.3786 | 1837 | 34 | 11
38961.3791 | 2099 | 43 | 11
38961.3795 | 2186 | 38 | 11
38961.38 | 2254 | 41 | 11
38961.3805 | 1867 | 32 | 11
11
38961.3387 | 1 | 0 | 12
38961.3392 | 1 | 0 | 12
38961.3397 | 1 | 0 | 12
38961.3402 | 1 | 0 | 12
38961.3407 | 1 | 0 | 12
38961.3412 | 1 | 0 | 12
38961.3417 | 1 | 0 | 12
38961.3421 | 1 | 0 | 12
38961.3426 | 1 | 0 | 12
38961.3431 | 1 | 0 | 12
38961.3436 | 1 | 0 | 12
38961.3441 | 1 | 0 | 12
38961.3446 | 1 | 0 | 12
38961.3451 | 1 | 0 | 12
38961.3455 | 1 | 0 | 12
38961.346 | 1 | 0 | 12
38961.3465 | 1 | 0 | 12
38961.347 | 1 | 0 | 12
38961.3475 | 1 | 0 | 12
38961.348 | 1 | 0 | 12
38961.3485 | 1 | 0 | 12
38961.3489 | 1 | 0 | 12
38961.3494 | 1 | 0 | 12
38961.3499 | 1 | 0 | 12
38961.3504 | 1 | 0 | 12
38961.3509 | 1 | 0 | 12
38961.3514 | 1 | 0 | 12
38961.3519 | 1 | 0 | 12
38961.3523 | 1 | 0 | 12
38961.3528 | 1 | 0 | 12
38961.3533 | 1 | 0 | 12
38961.3538 | 1 | 0 | 12
38961.3543 | 1 | 0 | 12
38961.3548 | 1 | 0 | 12
38961.3553 | 1 | 0 | 12
38961.3558 | 1 | 0 | 12
38961.3562 | 1 | 0 | 12
38961.3567 | 1 | 0 | 12
38961.3572 | 1 | 0 | 12
38961.3577 | 1 | 0 | 12
38961.3582 | 1 | 0 | 12
38961.3587 | 2 | 0 | 12
38961.3592 | 2 | 0 | 12
38961.3596 | 2 | 0 | 12
38961.3601 | 1 | 0 | 12
38961.3606 | 2 | 0 | 12
38961.3611 | 2 | 0 | 12
38961.3616 | 2 | 0 | 12
38961.3621 | 2 | 0 | 12
38961.3626 | 2 | 0 | 12
38961.363 | 2 | 0 | 12
38961.3635 | 2 | 0 | 12
38961.364 | 2 | 0 | 12
38961.3645 | 2 | 0 | 12
38961.365 | 2 | 0 | 12
38961.3655 | 2 | 0 | 12
38961.366 | 4 | 0 | 12
38961.3664 | 11 | 1 | 12
38961.3669 | 1088 | 987 | 12
38961.3674 | 1031 | 925 | 12
38961.3679 | 1038 | 916 | 12
38961.3684 | 982 | 869 | 12
38961.3689 | 1156 | 738 | 12
38961.3694 | 1889 | 161 | 12
38961.3698 | 2157 | 142 | 12
38961.3703 | 2090 | 104 | 12
38961.3708 | 1888 | 77 | 12
38961.3713 | 2158 | 79 | 12
38961.3718 | 2183 | 67 | 12
38961.3723 | 2219 | 56 | 12
38961.3728 | 1886 | 43 | 12
38961.3733 | 1922 | 44 | 12
38961.3737 | 1847 | 39 | 12
38961.3742 | 2283 | 41 | 12
38961.3747 | 2304 | 39 | 12
38961.3752 | 2184 | 38 | 12
38961.3757 | 1970 | 34 | 12
38961.3762 | 2310 | 40 | 12
38961.3767 | 2067 | 32 | 12
38961.3771 | 2069 | 38 | 12
38961.3776 | 2063 | 38 | 12
38961.3781 | 1862 | 31 | 12
38961.3786 | 2328 | 37 | 12
38961.3791 | 2301 | 34 | 12
38961.3796 | 2075 | 32 | 12
38961.3801 | 1989 | 31 | 12
38961.3805 | 1835 | 27 | 12
12
38961.3388 | 0 | 0 | 13
38961.3392 | 1 | 0 | 13
38961.3397 | 1 | 0 | 13
38961.3402 | 1 | 0 | 13
38961.3407 | 1 | 0 | 13
38961.3412 | 1 | 0 | 13
38961.3417 | 1 | 0 | 13
38961.3422 | 1 | 0 | 13
38961.3427 | 1 | 0 | 13
38961.3431 | 1 | 0 | 13
38961.3436 | 1 | 0 | 13
38961.3441 | 1 | 0 | 13
38961.3446 | 1 | 0 | 13
38961.3451 | 1 | 0 | 13
38961.3456 | 1 | 0 | 13
38961.346 | 1 | 0 | 13
38961.3465 | 1 | 0 | 13
38961.347 | 1 | 0 | 13
38961.3475 | 1 | 0 | 13
38961.348 | 1 | 0 | 13
38961.3485 | 1 | 0 | 13
38961.349 | 1 | 0 | 13
38961.3495 | 1 | 0 | 13
38961.3499 | 1 | 0 | 13
38961.3504 | 1 | 0 | 13
38961.3509 | 1 | 0 | 13
38961.3514 | 1 | 0 | 13
38961.3519 | 1 | 0 | 13
38961.3524 | 1 | 0 | 13
38961.3528 | 1 | 0 | 13
38961.3533 | 1 | 0 | 13
38961.3538 | 1 | 0 | 13
38961.3543 | 1 | 0 | 13
38961.3548 | 1 | 0 | 13
38961.3553 | 1 | 0 | 13
38961.3558 | 1 | 0 | 13
38961.3562 | 1 | 0 | 13
38961.3567 | 1 | 0 | 13
38961.3572 | 1 | 0 | 13
38961.3577 | 1 | 0 | 13
38961.3582 | 1 | 0 | 13
38961.3587 | 2 | 0 | 13
38961.3592 | 2 | 0 | 13
38961.3597 | 2 | 0 | 13
38961.3601 | 2 | 0 | 13
38961.3606 | 2 | 0 | 13
38961.3611 | 2 | 0 | 13
38961.3616 | 2 | 0 | 13
38961.3621 | 2 | 0 | 13
38961.3626 | 2 | 0 | 13
38961.3631 | 2 | 0 | 13
38961.3635 | 2 | 0 | 13
38961.364 | 2 | 0 | 13
38961.3645 | 2 | 0 | 13
38961.365 | 2 | 0 | 13
38961.3655 | 2 | 0 | 13
38961.366 | 2 | 0 | 13
38961.3665 | 2 | 0 | 13
38961.3669 | 1181 | 1092 | 13
38961.3674 | 1047 | 1010 | 13
38961.3679 | 1094 | 854 | 13
38961.3684 | 946 | 958 | 13
38961.3689 | 1479 | 480 | 13
38961.3694 | 1801 | 163 | 13
38961.3699 | 1704 | 125 | 13
38961.3703 | 2115 | 120 | 13
38961.3708 | 1786 | 77 | 13
38961.3713 | 1887 | 68 | 13
38961.3718 | 2253 | 71 | 13
38961.3723 | 2184 | 61 | 13
38961.3728 | 1882 | 46 | 13
38961.3733 | 2229 | 49 | 13
38961.3737 | 2249 | 46 | 13
38961.3742 | 2235 | 41 | 13
38961.3747 | 1881 | 33 | 13
38961.3752 | 2218 | 37 | 13
38961.3757 | 2228 | 36 | 13
38961.3762 | 1890 | 30 | 13
38961.3767 | 1777 | 31 | 13
38961.3772 | 1899 | 34 | 13
38961.3776 | 2136 | 38 | 13
38961.3781 | 2260 | 28 | 13
38961.3786 | 1866 | 26 | 13
38961.3791 | 2214 | 29 | 13
38961.3796 | 1845 | 23 | 13
38961.3801 | 1956 | 24 | 13
38961.3806 | 2055 | 25 | 13
13
38961.3388 | 1 | 0 | 14
38961.3393 | 1 | 0 | 14
38961.3397 | 1 | 0 | 14
38961.3402 | 1 | 0 | 14
38961.3407 | 1 | 0 | 14
38961.3412 | 1 | 0 | 14
38961.3417 | 1 | 0 | 14
38961.3422 | 1 | 1 | 14
38961.3427 | 1 | 0 | 14
38961.3431 | 1 | 0 | 14
38961.3436 | 1 | 0 | 14
38961.3441 | 1 | 0 | 14
38961.3446 | 1 | 0 | 14
38961.3451 | 1 | 0 | 14
38961.3456 | 1 | 0 | 14
38961.3461 | 1 | 0 | 14
38961.3466 | 1 | 0 | 14
38961.347 | 2 | 0 | 14
38961.3475 | 1 | 0 | 14
38961.348 | 1 | 0 | 14
38961.3485 | 1 | 0 | 14
38961.349 | 1 | 0 | 14
38961.3495 | 1 | 0 | 14
38961.35 | 1 | 0 | 14
38961.3504 | 1 | 0 | 14
38961.3509 | 1 | 0 | 14
38961.3514 | 1 | 0 | 14
38961.3519 | 1 | 0 | 14
38961.3524 | 1 | 0 | 14
38961.3529 | 1 | 0 | 14
38961.3534 | 1 | 0 | 14
38961.3538 | 1 | 0 | 14
38961.3543 | 1 | 0 | 14
38961.3548 | 1 | 0 | 14
38961.3553 | 1 | 0 | 14
38961.3558 | 1 | 0 | 14
38961.3563 | 1 | 0 | 14
38961.3568 | 1 | 0 | 14
38961.3572 | 1 | 0 | 14
38961.3577 | 1 | 0 | 14
38961.3582 | 2 | 0 | 14
38961.3587 | 2 | 0 | 14
38961.3592 | 2 | 0 | 14
38961.3597 | 2 | 0 | 14
38961.3602 | 2 | 0 | 14
38961.3606 | 2 | 0 | 14
38961.3611 | 2 | 0 | 14
38961.3616 | 1 | 0 | 14
38961.3621 | 2 | 0 | 14
38961.3626 | 2 | 0 | 14
38961.3631 | 2 | 0 | 14
38961.3636 | 2 | 0 | 14
38961.3641 | 2 | 0 | 14
38961.3645 | 2 | 0 | 14
38961.365 | 2 | 0 | 14
38961.3655 | 2 | 0 | 14
38961.366 | 2 | 0 | 14
38961.3665 | 179 | 151 | 14
38961.367 | 1183 | 1087 | 14
38961.3675 | 1196 | 1093 | 14
38961.3679 | 1149 | 842 | 14
38961.3684 | 946 | 840 | 14
38961.3689 | 1599 | 491 | 14
38961.3694 | 1961 | 193 | 14
38961.3699 | 1816 | 136 | 14
38961.3704 | 1977 | 108 | 14
38961.3709 | 1839 | 87 | 14
38961.3713 | 1931 | 73 | 14
38961.3718 | 2153 | 71 | 14
38961.3723 | 2049 | 60 | 14
38961.3728 | 1769 | 48 | 14
38961.3733 | 2198 | 55 | 14
38961.3738 | 1833 | 42 | 14
38961.3743 | 1805 | 37 | 14
38961.3747 | 2210 | 45 | 14
38961.3752 | 1966 | 37 | 14
38961.3757 | 1755 | 34 | 14
38961.3762 | 1965 | 37 | 14
38961.3767 | 1965 | 36 | 14
38961.3772 | 1926 | 42 | 14
38961.3777 | 2126 | 41 | 14
38961.3781 | 2112 | 41 | 14
38961.3786 | 1976 | 33 | 14
38961.3791 | 1904 | 32 | 14
38961.3796 | 2167 | 27 | 14
38961.3801 | 1861 | 29 | 14
38961.3806 | 1894 | 29 | 14
14
38961.3388 | 1 | 0 | 15
38961.3393 | 1 | 0 | 15
38961.3398 | 1 | 0 | 15
38961.3402 | 1 | 0 | 15
38961.3407 | 1 | 0 | 15
38961.3412 | 1 | 0 | 15
38961.3417 | 1 | 0 | 15
38961.3422 | 2 | 0 | 15
38961.3427 | 1 | 0 | 15
38961.3432 | 1 | 0 | 15
38961.3436 | 1 | 0 | 15
38961.3441 | 1 | 0 | 15
38961.3446 | 1 | 0 | 15
38961.3451 | 1 | 0 | 15
38961.3456 | 1 | 0 | 15
38961.3461 | 1 | 0 | 15
38961.3466 | 1 | 0 | 15
38961.347 | 1 | 0 | 15
38961.3475 | 1 | 0 | 15
38961.348 | 1 | 0 | 15
38961.3485 | 1 | 0 | 15
38961.349 | 1 | 0 | 15
38961.3495 | 1 | 0 | 15
38961.35 | 1 | 0 | 15
38961.3505 | 1 | 0 | 15
38961.3509 | 1 | 0 | 15
38961.3514 | 1 | 0 | 15
38961.3519 | 1 | 0 | 15
38961.3524 | 1 | 0 | 15
38961.3529 | 1 | 0 | 15
38961.3534 | 1 | 0 | 15
38961.3539 | 1 | 0 | 15
38961.3543 | 1 | 0 | 15
38961.3548 | 1 | 0 | 15
38961.3553 | 1 | 0 | 15
38961.3558 | 1 | 0 | 15
38961.3563 | 1 | 0 | 15
38961.3568 | 1 | 0 | 15
38961.3573 | 1 | 0 | 15
38961.3577 | 1 | 0 | 15
38961.3582 | 1 | 0 | 15
38961.3587 | 2 | 0 | 15
38961.3592 | 2 | 0 | 15
38961.3597 | 2 | 0 | 15
38961.3602 | 2 | 0 | 15
38961.3607 | 2 | 0 | 15
38961.3611 | 1 | 0 | 15
38961.3616 | 2 | 0 | 15
38961.3621 | 2 | 0 | 15
38961.3626 | 2 | 0 | 15
38961.3631 | 2 | 0 | 15
38961.3636 | 1 | 0 | 15
38961.3641 | 2 | 0 | 15
38961.3645 | 2 | 0 | 15
38961.365 | 2 | 0 | 15
38961.3655 | 2 | 0 | 15
38961.366 | 2 | 0 | 15
38961.3665 | 2 | 0 | 15
38961.367 | 31 | 2 | 15
38961.3675 | 48 | 2 | 15
38961.368 | 257 | 2 | 15
38961.3684 | 135 | 2 | 15
38961.3689 | 1702 | 1 | 15
38961.3694 | 1994 | 0 | 15
38961.3699 | 1988 | 0 | 15
38961.3704 | 1995 | 0 | 15
38961.3709 | 2131 | 0 | 15
38961.3714 | 1898 | 0 | 15
38961.3718 | 1747 | 0 | 15
38961.3723 | 1946 | 0 | 15
38961.3728 | 1957 | 0 | 15
38961.3733 | 2034 | 0 | 15
38961.3738 | 1975 | 0 | 15
38961.3743 | 2243 | 0 | 15
38961.3748 | 2170 | 0 | 15
38961.3752 | 2091 | 0 | 15
38961.3757 | 2261 | 0 | 15
38961.3762 | 1968 | 0 | 15
38961.3767 | 2230 | 0 | 15
38961.3772 | 1920 | 0 | 15
38961.3777 | 2243 | 0 | 15
38961.3782 | 2108 | 0 | 15
38961.3786 | 2153 | 0 | 15
38961.3791 | 1853 | 0 | 15
38961.3796 | 2023 | 0 | 15
38961.3801 | 1859 | 0 | 15
38961.3806 | 2202 | 0 | 15
15
38961.3388 | 1 | 0 | 16
38961.3393 | 1 | 0 | 16
38961.3398 | 1 | 0 | 16
38961.3403 | 1 | 0 | 16
38961.3408 | 1 | 0 | 16
38961.3412 | 1 | 0 | 16
38961.3417 | 1 | 0 | 16
38961.3422 | 1 | 0 | 16
38961.3427 | 1 | 0 | 16
38961.3432 | 1 | 1 | 16
38961.3437 | 1 | 0 | 16
38961.3442 | 1 | 0 | 16
38961.3446 | 1 | 0 | 16
38961.3451 | 1 | 0 | 16
38961.3456 | 1 | 0 | 16
38961.3461 | 1 | 0 | 16
38961.3466 | 1 | 0 | 16
38961.3471 | 1 | 0 | 16
38961.3476 | 1 | 0 | 16
38961.348 | 1 | 0 | 16
38961.3485 | 1 | 0 | 16
38961.349 | 1 | 0 | 16
38961.3495 | 1 | 0 | 16
38961.35 | 1 | 0 | 16
38961.3505 | 1 | 0 | 16
38961.351 | 1 | 0 | 16
38961.3514 | 1 | 0 | 16
38961.3519 | 1 | 0 | 16
38961.3524 | 1 | 0 | 16
38961.3529 | 1 | 0 | 16
38961.3534 | 1 | 0 | 16
38961.3539 | 1 | 0 | 16
38961.3544 | 1 | 0 | 16
38961.3548 | 1 | 0 | 16
38961.3553 | 1 | 0 | 16
38961.3558 | 1 | 0 | 16
38961.3563 | 1 | 0 | 16
38961.3568 | 1 | 0 | 16
38961.3573 | 1 | 0 | 16
38961.3578 | 1518 | 0 | 16
38961.3583 | 2184 | 0 | 16
38961.3587 | 1940 | 0 | 16
38961.3592 | 2272 | 0 | 16
38961.3597 | 2233 | 0 | 16
38961.3602 | 2214 | 0 | 16
38961.3607 | 2007 | 0 | 16
38961.3612 | 2281 | 0 | 16
38961.3617 | 1872 | 0 | 16
38961.3621 | 2230 | 0 | 16
38961.3626 | 2271 | 0 | 16
38961.3631 | 2295 | 0 | 16
38961.3636 | 2235 | 0 | 16
38961.3641 | 2378 | 0 | 16
38961.3646 | 2133 | 0 | 16
38961.365 | 2385 | 0 | 16
38961.3655 | 2188 | 0 | 16
38961.366 | 2230 | 0 | 16
38961.3665 | 2225 | 0 | 16
38961.367 | 1926 | 1 | 16
38961.3675 | 2359 | 2 | 16
38961.368 | 2062 | 1 | 16
38961.3684 | 2326 | 1 | 16
38961.3689 | 2138 | 0 | 16
38961.3694 | 1821 | 0 | 16
38961.3699 | 2012 | 0 | 16
38961.3704 | 2350 | 0 | 16
38961.3709 | 2055 | 0 | 16
38961.3714 | 2303 | 0 | 16
38961.3719 | 1938 | 0 | 16
38961.3723 | 2080 | 0 | 16
38961.3728 | 2288 | 0 | 16
38961.3733 | 1999 | 0 | 16
38961.3738 | 2166 | 0 | 16
38961.3743 | 2236 | 0 | 16
38961.3748 | 2369 | 0 | 16
38961.3753 | 1843 | 0 | 16
38961.3757 | 1851 | 0 | 16
38961.3762 | 2168 | 0 | 16
38961.3767 | 1833 | 0 | 16
38961.3772 | 2085 | 0 | 16
38961.3777 | 2333 | 0 | 16
38961.3782 | 2155 | 0 | 16
38961.3787 | 2195 | 0 | 16
38961.3791 | 1905 | 0 | 16
38961.3796 | 1843 | 0 | 16
38961.3801 | 2074 | 0 | 16
38961.3806 | 2325 | 0 | 16
16
38961.3388 | 1 | 0 | 17
38961.3393 | 1 | 0 | 17
38961.3398 | 1 | 0 | 17
38961.3403 | 1 | 0 | 17
38961.3408 | 1 | 0 | 17
38961.3412 | 1 | 1 | 17
38961.3417 | 1 | 0 | 17
38961.3422 | 1 | 0 | 17
38961.3427 | 1 | 0 | 17
38961.3432 | 1 | 0 | 17
38961.3437 | 1 | 0 | 17
38961.3442 | 1 | 0 | 17
38961.3447 | 1 | 1 | 17
38961.3451 | 1 | 0 | 17
38961.3456 | 1 | 0 | 17
38961.3461 | 1 | 0 | 17
38961.3466 | 1 | 0 | 17
38961.3471 | 1 | 0 | 17
38961.3476 | 1 | 0 | 17
38961.3481 | 1 | 0 | 17
38961.3485 | 1 | 0 | 17
38961.349 | 1 | 0 | 17
38961.3495 | 1 | 0 | 17
38961.35 | 1 | 0 | 17
38961.3505 | 1 | 0 | 17
38961.351 | 1 | 0 | 17
38961.3515 | 1 | 0 | 17
38961.3519 | 1 | 0 | 17
38961.3524 | 1 | 0 | 17
38961.3529 | 1 | 0 | 17
38961.3534 | 1 | 0 | 17
38961.3539 | 1 | 0 | 17
38961.3544 | 1 | 0 | 17
38961.3549 | 1 | 0 | 17
38961.3553 | 1 | 0 | 17
38961.3558 | 1 | 0 | 17
38961.3563 | 1 | 0 | 17
38961.3568 | 1 | 0 | 17
38961.3573 | 1 | 0 | 17
38961.3578 | 2 | 0 | 17
38961.3583 | 2 | 0 | 17
38961.3587 | 2 | 0 | 17
38961.3592 | 3 | 0 | 17
38961.3597 | 2 | 0 | 17
38961.3602 | 2 | 0 | 17
38961.3607 | 2 | 0 | 17
38961.3612 | 2 | 0 | 17
38961.3617 | 2 | 0 | 17
38961.3622 | 3 | 0 | 17
38961.3626 | 2 | 0 | 17
38961.3631 | 2 | 0 | 17
38961.3636 | 2 | 0 | 17
38961.3641 | 2 | 0 | 17
38961.3646 | 2 | 0 | 17
38961.3651 | 2 | 0 | 17
38961.3656 | 3 | 0 | 17
38961.366 | 2 | 0 | 17
38961.3665 | 10 | 0 | 17
38961.367 | 36 | 1 | 17
38961.3675 | 51 | 1 | 17
38961.368 | 86 | 1 | 17
38961.3685 | 60 | 1 | 17
38961.369 | 1398 | 1 | 17
38961.3694 | 1856 | 0 | 17
38961.3699 | 1709 | 0 | 17
38961.3704 | 1968 | 0 | 17
38961.3709 | 2108 | 0 | 17
38961.3714 | 2193 | 0 | 17
38961.3719 | 1950 | 0 | 17
38961.3724 | 2208 | 0 | 17
38961.3728 | 1780 | 0 | 17
38961.3733 | 1829 | 0 | 17
38961.3738 | 1967 | 0 | 17
38961.3743 | 1853 | 0 | 17
38961.3748 | 1872 | 0 | 17
38961.3753 | 2054 | 0 | 17
38961.3758 | 1960 | 0 | 17
38961.3763 | 2257 | 0 | 17
38961.3767 | 1915 | 0 | 17
38961.3772 | 2202 | 0 | 17
38961.3777 | 2013 | 0 | 17
38961.3782 | 1769 | 0 | 17
38961.3787 | 2166 | 0 | 17
38961.3792 | 2270 | 0 | 17
38961.3797 | 1937 | 0 | 17
38961.3801 | 1829 | 0 | 17
38961.3806 | 2269 | 0 | 17
17
38961.3388 | 1 | 0 | 18
38961.3393 | 1 | 0 | 18
38961.3398 | 1 | 0 | 18
38961.3403 | 1 | 0 | 18
38961.3408 | 1 | 0 | 18
38961.3413 | 1 | 0 | 18
38961.3418 | 1 | 0 | 18
38961.3422 | 1 | 0 | 18
38961.3427 | 1 | 0 | 18
38961.3432 | 2 | 0 | 18
38961.3437 | 1 | 0 | 18
38961.3442 | 1 | 0 | 18
38961.3447 | 1 | 0 | 18
38961.3452 | 1 | 0 | 18
38961.3456 | 1 | 0 | 18
38961.3461 | 1 | 0 | 18
38961.3466 | 1 | 0 | 18
38961.3471 | 1 | 0 | 18
38961.3476 | 1 | 0 | 18
38961.3481 | 1 | 0 | 18
38961.3486 | 1 | 1 | 18
38961.349 | 1 | 0 | 18
38961.3495 | 1 | 0 | 18
38961.35 | 1 | 0 | 18
38961.3505 | 1 | 0 | 18
38961.351 | 1 | 0 | 18
38961.3515 | 1 | 0 | 18
38961.352 | 1 | 0 | 18
38961.3524 | 1 | 0 | 18
38961.3529 | 1 | 0 | 18
38961.3534 | 1 | 0 | 18
38961.3539 | 1 | 0 | 18
38961.3544 | 1 | 0 | 18
38961.3549 | 1 | 0 | 18
38961.3554 | 1 | 0 | 18
38961.3558 | 1 | 0 | 18
38961.3563 | 1 | 0 | 18
38961.3568 | 1 | 0 | 18
38961.3573 | 1 | 0 | 18
38961.3578 | 86 | 0 | 18
38961.3583 | 1181 | 0 | 18
38961.3588 | 2205 | 0 | 18
38961.3592 | 2205 | 0 | 18
38961.3597 | 1912 | 0 | 18
38961.3602 | 1882 | 0 | 18
38961.3607 | 2008 | 0 | 18
38961.3612 | 1916 | 0 | 18
38961.3617 | 2218 | 0 | 18
38961.3622 | 2315 | 0 | 18
38961.3627 | 2115 | 0 | 18
38961.3631 | 2120 | 0 | 18
38961.3636 | 2019 | 0 | 18
38961.3641 | 2167 | 0 | 18
38961.3646 | 1992 | 0 | 18
38961.3651 | 2231 | 0 | 18
38961.3656 | 2271 | 0 | 18
38961.3661 | 2022 | 0 | 18
38961.3665 | 2346 | 0 | 18
38961.367 | 1890 | 0 | 18
38961.3675 | 2004 | 1 | 18
38961.368 | 2180 | 1 | 18
38961.3685 | 2098 | 0 | 18
38961.369 | 2159 | 1 | 18
38961.3695 | 2215 | 0 | 18
38961.3699 | 2058 | 0 | 18
38961.3704 | 2286 | 0 | 18
38961.3709 | 2371 | 0 | 18
38961.3714 | 2364 | 0 | 18
38961.3719 | 1938 | 0 | 18
38961.3724 | 2107 | 0 | 18
38961.3729 | 2058 | 0 | 18
38961.3733 | 2176 | 0 | 18
38961.3738 | 1918 | 0 | 18
38961.3743 | 2034 | 0 | 18
38961.3748 | 2394 | 0 | 18
38961.3753 | 1860 | 0 | 18
38961.3758 | 1860 | 0 | 18
38961.3763 | 2346 | 0 | 18
38961.3767 | 1872 | 0 | 18
38961.3772 | 1963 | 0 | 18
38961.3777 | 2019 | 0 | 18
38961.3782 | 2009 | 0 | 18
38961.3787 | 2388 | 0 | 18
38961.3792 | 1994 | 0 | 18
38961.3797 | 2353 | 0 | 18
38961.3802 | 2205 | 0 | 18
38961.3806 | 2280 | 0 | 18
18
38961.3389 | 1 | 0 | 19
38961.3393 | 1 | 0 | 19
38961.3398 | 1 | 0 | 19
38961.3403 | 1 | 0 | 19
38961.3408 | 1 | 0 | 19
38961.3413 | 1 | 0 | 19
38961.3418 | 1 | 0 | 19
38961.3423 | 1 | 0 | 19
38961.3427 | 1 | 0 | 19
38961.3432 | 1 | 0 | 19
38961.3437 | 1 | 0 | 19
38961.3442 | 1 | 0 | 19
38961.3447 | 1 | 0 | 19
38961.3452 | 1 | 0 | 19
38961.3457 | 1 | 0 | 19
38961.3461 | 1 | 0 | 19
38961.3466 | 1 | 0 | 19
38961.3471 | 1 | 0 | 19
38961.3476 | 1 | 0 | 19
38961.3481 | 1 | 0 | 19
38961.3486 | 1 | 0 | 19
38961.3491 | 1 | 0 | 19
38961.3495 | 1 | 0 | 19
38961.35 | 1 | 0 | 19
38961.3505 | 1 | 0 | 19
38961.351 | 1 | 0 | 19
38961.3515 | 1 | 0 | 19
38961.352 | 1 | 0 | 19
38961.3525 | 1 | 0 | 19
38961.353 | 1 | 0 | 19
38961.3534 | 1 | 0 | 19
38961.3539 | 1 | 0 | 19
38961.3544 | 1 | 0 | 19
38961.3549 | 1 | 0 | 19
38961.3554 | 1 | 0 | 19
38961.3559 | 1 | 0 | 19
38961.3564 | 1 | 0 | 19
38961.3568 | 1 | 0 | 19
38961.3573 | 1 | 0 | 19
38961.3578 | 1 | 0 | 19
38961.3583 | 2 | 0 | 19
38961.3588 | 3 | 0 | 19
38961.3593 | 3 | 0 | 19
38961.3598 | 3 | 0 | 19
38961.3602 | 2 | 0 | 19
38961.3607 | 2 | 0 | 19
38961.3612 | 3 | 0 | 19
38961.3617 | 3 | 0 | 19
38961.3622 | 4 | 1 | 19
38961.3627 | 5 | 1 | 19
38961.3632 | 6 | 1 | 19
38961.3636 | 8 | 2 | 19
38961.3641 | 6 | 2 | 19
38961.3646 | 14 | 6 | 19
38961.3651 | 27 | 9 | 19
38961.3656 | 1028 | 977 | 19
38961.3661 | 939 | 999 | 19
38961.3666 | 972 | 943 | 19
38961.367 | 1080 | 980 | 19
38961.3675 | 1078 | 966 | 19
38961.368 | 1260 | 1106 | 19
38961.3685 | 981 | 936 | 19
38961.369 | 1806 | 301 | 19
38961.3695 | 1891 | 175 | 19
38961.37 | 2172 | 160 | 19
38961.3705 | 1828 | 104 | 19
38961.3709 | 1998 | 91 | 19
38961.3714 | 1972 | 84 | 19
38961.3719 | 2039 | 70 | 19
38961.3724 | 2237 | 69 | 19
38961.3729 | 2200 | 60 | 19
38961.3734 | 2270 | 57 | 19
38961.3739 | 1986 | 48 | 19
38961.3743 | 2102 | 43 | 19
38961.3748 | 2259 | 47 | 19
38961.3753 | 1816 | 36 | 19
38961.3758 | 2167 | 40 | 19
38961.3763 | 2280 | 45 | 19
38961.3768 | 2306 | 43 | 19
38961.3772 | 2326 | 48 | 19
38961.3777 | 2187 | 43 | 19
38961.3782 | 1890 | 34 | 19
38961.3787 | 1918 | 32 | 19
38961.3792 | 2043 | 33 | 19
38961.3797 | 2192 | 32 | 19
38961.3802 | 1950 | 29 | 19
38961.3807 | 1911 | 27 | 19
19
38961.3389 | 1 | 1 | 20
38961.3394 | 1 | 0 | 20
38961.3398 | 1 | 0 | 20
38961.3403 | 1 | 0 | 20
38961.3408 | 1 | 0 | 20
38961.3413 | 1 | 0 | 20
38961.3418 | 1 | 0 | 20
38961.3423 | 1 | 0 | 20
38961.3428 | 1 | 0 | 20
38961.3432 | 1 | 0 | 20
38961.3437 | 1 | 0 | 20
38961.3442 | 1 | 0 | 20
38961.3447 | 1 | 0 | 20
38961.3452 | 1 | 0 | 20
38961.3457 | 1 | 0 | 20
38961.3462 | 1 | 0 | 20
38961.3466 | 1 | 0 | 20
38961.3471 | 1 | 0 | 20
38961.3476 | 1 | 0 | 20
38961.3481 | 1 | 0 | 20
38961.3486 | 1 | 0 | 20
38961.3491 | 1 | 0 | 20
38961.3496 | 1 | 0 | 20
38961.35 | 1 | 0 | 20
38961.3505 | 1 | 0 | 20
38961.351 | 1 | 0 | 20
38961.3515 | 1 | 0 | 20
38961.352 | 1 | 0 | 20
38961.3525 | 1 | 0 | 20
38961.353 | 1 | 0 | 20
38961.3534 | 1 | 0 | 20
38961.3539 | 1 | 0 | 20
38961.3544 | 1 | 0 | 20
38961.3549 | 1 | 0 | 20
38961.3554 | 1 | 0 | 20
38961.3559 | 1 | 0 | 20
38961.3564 | 1 | 0 | 20
38961.3569 | 1 | 0 | 20
38961.3573 | 1 | 0 | 20
38961.3578 | 1 | 0 | 20
38961.3583 | 1 | 0 | 20
38961.3588 | 2 | 0 | 20
38961.3593 | 2 | 0 | 20
38961.3598 | 2 | 0 | 20
38961.3603 | 2 | 0 | 20
38961.3607 | 2 | 0 | 20
38961.3612 | 2 | 0 | 20
38961.3617 | 2 | 0 | 20
38961.3622 | 3 | 0 | 20
38961.3627 | 4 | 2 | 20
38961.3632 | 5 | 2 | 20
38961.3637 | 6 | 2 | 20
38961.3641 | 6 | 2 | 20
38961.3646 | 8 | 3 | 20
38961.3651 | 220 | 195 | 20
38961.3656 | 1141 | 1091 | 20
38961.3661 | 986 | 918 | 20
38961.3666 | 1144 | 1041 | 20
38961.3671 | 1224 | 1117 | 20
38961.3675 | 1013 | 907 | 20
38961.368 | 1100 | 954 | 20
38961.3685 | 1035 | 925 | 20
38961.369 | 1690 | 270 | 20
38961.3695 | 1847 | 164 | 20
38961.37 | 2048 | 141 | 20
38961.3705 | 1871 | 101 | 20
38961.3709 | 1865 | 85 | 20
38961.3714 | 2282 | 84 | 20
38961.3719 | 1897 | 60 | 20
38961.3724 | 1856 | 52 | 20
38961.3729 | 1903 | 48 | 20
38961.3734 | 1903 | 46 | 20
38961.3739 | 1842 | 38 | 20
38961.3744 | 2307 | 42 | 20
38961.3748 | 2148 | 43 | 20
38961.3753 | 2313 | 41 | 20
38961.3758 | 2215 | 41 | 20
38961.3763 | 1867 | 33 | 20
38961.3768 | 2328 | 42 | 20
38961.3773 | 2367 | 44 | 20
38961.3778 | 1904 | 34 | 20
38961.3782 | 2370 | 38 | 20
38961.3787 | 2043 | 31 | 20
38961.3792 | 2310 | 33 | 20
38961.3797 | 2201 | 30 | 20
38961.3802 | 2158 | 28 | 20
38961.3807 | 1969 | 25 | 20
20
38961.3389 | 1 | 0 | 21
38961.3394 | 1 | 0 | 21
38961.3399 | 1 | 0 | 21
38961.3403 | 1 | 0 | 21
38961.3408 | 1 | 0 | 21
38961.3413 | 1 | 0 | 21
38961.3418 | 1 | 0 | 21
38961.3423 | 1 | 0 | 21
38961.3428 | 1 | 0 | 21
38961.3433 | 1 | 0 | 21
38961.3438 | 1 | 0 | 21
38961.3442 | 1 | 0 | 21
38961.3447 | 1 | 0 | 21
38961.3452 | 1 | 0 | 21
38961.3457 | 1 | 0 | 21
38961.3462 | 1 | 0 | 21
38961.3467 | 1 | 0 | 21
38961.3472 | 1 | 0 | 21
38961.3476 | 1 | 0 | 21
38961.3481 | 1 | 0 | 21
38961.3486 | 1 | 1 | 21
38961.3491 | 1 | 0 | 21
38961.3496 | 1 | 0 | 21
38961.3501 | 1 | 0 | 21
38961.3506 | 1 | 0 | 21
38961.351 | 1 | 0 | 21
38961.3515 | 1 | 0 | 21
38961.352 | 1 | 0 | 21
38961.3525 | 1 | 0 | 21
38961.353 | 1 | 0 | 21
38961.3535 | 1 | 0 | 21
38961.354 | 1 | 0 | 21
38961.3544 | 1 | 0 | 21
38961.3549 | 1 | 0 | 21
38961.3554 | 1 | 0 | 21
38961.3559 | 1 | 0 | 21
38961.3564 | 1 | 0 | 21
38961.3569 | 1 | 0 | 21
38961.3574 | 1 | 0 | 21
38961.3578 | 1 | 0 | 21
38961.3583 | 1 | 0 | 21
38961.3588 | 2 | 0 | 21
38961.3593 | 2 | 0 | 21
38961.3598 | 2 | 0 | 21
38961.3603 | 2 | 0 | 21
38961.3608 | 2 | 0 | 21
38961.3613 | 2 | 0 | 21
38961.3617 | 2 | 0 | 21
38961.3622 | 2 | 0 | 21
38961.3627 | 1 | 0 | 21
38961.3632 | 2 | 0 | 21
38961.3637 | 2 | 0 | 21
38961.3642 | 2 | 0 | 21
38961.3647 | 2 | 0 | 21
38961.3651 | 2 | 0 | 21
38961.3656 | 2 | 2 | 21
38961.3661 | 5 | 2 | 21
38961.3666 | 28 | 1 | 21
38961.3671 | 33 | 2 | 21
38961.3676 | 72 | 2 | 21
38961.3681 | 188 | 2 | 21
38961.3685 | 63 | 2 | 21
38961.369 | 1913 | 1 | 21
38961.3695 | 2149 | 0 | 21
38961.37 | 2179 | 1 | 21
38961.3705 | 1761 | 0 | 21
38961.371 | 2061 | 0 | 21
38961.3714 | 2150 | 0 | 21
38961.3719 | 2179 | 0 | 21
38961.3724 | 2038 | 0 | 21
38961.3729 | 2070 | 0 | 21
38961.3734 | 2186 | 0 | 21
38961.3739 | 2313 | 0 | 21
38961.3744 | 2103 | 0 | 21
38961.3748 | 2025 | 0 | 21
38961.3753 | 2114 | 0 | 21
38961.3758 | 2162 | 0 | 21
38961.3763 | 1978 | 0 | 21
38961.3768 | 2099 | 0 | 21
38961.3773 | 2089 | 0 | 21
38961.3778 | 2208 | 0 | 21
38961.3783 | 1965 | 0 | 21
38961.3787 | 2276 | 0 | 21
38961.3792 | 1922 | 0 | 21
38961.3797 | 2043 | 0 | 21
38961.3802 | 1936 | 0 | 21
38961.3807 | 2123 | 0 | 21
21
38961.3389 | 1 | 0 | 22
38961.3394 | 1 | 0 | 22
38961.3399 | 1 | 0 | 22
38961.3404 | 1 | 0 | 22
38961.3408 | 1 | 0 | 22
38961.3413 | 1 | 0 | 22
38961.3418 | 1 | 0 | 22
38961.3423 | 1 | 0 | 22
38961.3428 | 1 | 1 | 22
38961.3433 | 1 | 0 | 22
38961.3438 | 1 | 0 | 22
38961.3442 | 1 | 0 | 22
38961.3447 | 1 | 0 | 22
38961.3452 | 1 | 0 | 22
38961.3457 | 1 | 0 | 22
38961.3462 | 1 | 0 | 22
38961.3467 | 1 | 0 | 22
38961.3472 | 1 | 0 | 22
38961.3477 | 1 | 0 | 22
38961.3481 | 1 | 0 | 22
38961.3486 | 1 | 0 | 22
38961.3491 | 1 | 0 | 22
38961.3496 | 1 | 0 | 22
38961.3501 | 1 | 0 | 22
38961.3506 | 1 | 0 | 22
38961.3511 | 1 | 0 | 22
38961.3515 | 1 | 0 | 22
38961.352 | 1 | 0 | 22
38961.3525 | 1 | 0 | 22
38961.353 | 1 | 0 | 22
38961.3535 | 1 | 0 | 22
38961.354 | 1 | 0 | 22
38961.3545 | 1 | 0 | 22
38961.3549 | 1 | 0 | 22
38961.3554 | 1 | 0 | 22
38961.3559 | 1 | 0 | 22
38961.3564 | 1 | 0 | 22
38961.3569 | 1 | 0 | 22
38961.3574 | 1 | 0 | 22
38961.3579 | 1438 | 0 | 22
38961.3583 | 2015 | 0 | 22
38961.3588 | 2331 | 0 | 22
38961.3593 | 2301 | 0 | 22
38961.3598 | 1939 | 0 | 22
38961.3603 | 2378 | 0 | 22
38961.3608 | 2108 | 0 | 22
38961.3613 | 2044 | 0 | 22
38961.3617 | 1881 | 0 | 22
38961.3622 | 2333 | 0 | 22
38961.3627 | 2126 | 0 | 22
38961.3632 | 2257 | 0 | 22
38961.3637 | 2359 | 0 | 22
38961.3642 | 1844 | 0 | 22
38961.3647 | 2282 | 0 | 22
38961.3652 | 2346 | 0 | 22
38961.3656 | 2337 | 0 | 22
38961.3661 | 2385 | 1 | 22
38961.3666 | 1853 | 1 | 22
38961.3671 | 2356 | 1 | 22
38961.3676 | 2172 | 1 | 22
38961.3681 | 1873 | 1 | 22
38961.3686 | 2368 | 1 | 22
38961.369 | 1897 | 1 | 22
38961.3695 | 1916 | 0 | 22
38961.37 | 2186 | 0 | 22
38961.3705 | 2039 | 0 | 22
38961.371 | 2071 | 0 | 22
38961.3715 | 1965 | 0 | 22
38961.372 | 1876 | 0 | 22
38961.3724 | 2058 | 0 | 22
38961.3729 | 2360 | 0 | 22
38961.3734 | 1934 | 0 | 22
38961.3739 | 2140 | 0 | 22
38961.3744 | 2327 | 0 | 22
38961.3749 | 2000 | 0 | 22
38961.3754 | 2278 | 0 | 22
38961.3758 | 2320 | 0 | 22
38961.3763 | 2006 | 0 | 22
38961.3768 | 1973 | 0 | 22
38961.3773 | 2320 | 0 | 22
38961.3778 | 2231 | 0 | 22
38961.3783 | 2010 | 0 | 22
38961.3788 | 2071 | 0 | 22
38961.3792 | 1921 | 0 | 22
38961.3797 | 1884 | 0 | 22
38961.3802 | 2186 | 0 | 22
38961.3807 | 2079 | 0 | 22
22
38961.3389 | 1 | 0 | 23
38961.3394 | 1 | 0 | 23
38961.3399 | 1 | 0 | 23
38961.3404 | 1 | 0 | 23
38961.3409 | 1 | 0 | 23
38961.3414 | 1 | 0 | 23
38961.3418 | 1 | 0 | 23
38961.3423 | 1 | 0 | 23
38961.3428 | 1 | 0 | 23
38961.3433 | 1 | 0 | 23
38961.3438 | 1 | 0 | 23
38961.3443 | 1 | 0 | 23
38961.3448 | 1 | 0 | 23
38961.3452 | 1 | 0 | 23
38961.3457 | 1 | 0 | 23
38961.3462 | 2 | 0 | 23
38961.3467 | 1 | 0 | 23
38961.3472 | 1 | 0 | 23
38961.3477 | 1 | 0 | 23
38961.3481 | 2 | 0 | 23
38961.3486 | 1 | 0 | 23
38961.3491 | 1 | 0 | 23
38961.3496 | 1 | 0 | 23
38961.3501 | 1 | 0 | 23
38961.3506 | 1 | 0 | 23
38961.3511 | 1 | 0 | 23
38961.3516 | 1 | 0 | 23
38961.352 | 1 | 0 | 23
38961.3525 | 1 | 0 | 23
38961.353 | 1 | 0 | 23
38961.3535 | 1 | 0 | 23
38961.354 | 1 | 0 | 23
38961.3545 | 1 | 0 | 23
38961.355 | 1 | 0 | 23
38961.3554 | 1 | 0 | 23
38961.3559 | 1 | 0 | 23
38961.3564 | 1 | 0 | 23
38961.3569 | 1 | 0 | 23
38961.3574 | 1 | 0 | 23
38961.3579 | 1 | 0 | 23
38961.3584 | 2 | 0 | 23
38961.3588 | 2 | 0 | 23
38961.3593 | 2 | 0 | 23
38961.3598 | 2 | 0 | 23
38961.3603 | 2 | 0 | 23
38961.3608 | 3 | 0 | 23
38961.3613 | 2 | 0 | 23
38961.3618 | 2 | 0 | 23
38961.3622 | 2 | 0 | 23
38961.3627 | 2 | 0 | 23
38961.3632 | 2 | 0 | 23
38961.3637 | 3 | 0 | 23
38961.3642 | 2 | 0 | 23
38961.3647 | 2 | 0 | 23
38961.3652 | 2 | 0 | 23
38961.3656 | 3 | 0 | 23
38961.3661 | 6 | 0 | 23
38961.3666 | 25 | 0 | 23
38961.3671 | 37 | 1 | 23
38961.3676 | 101 | 1 | 23
38961.3681 | 458 | 1 | 23
38961.3686 | 65 | 1 | 23
38961.3691 | 2002 | 0 | 23
38961.3695 | 1979 | 0 | 23
38961.37 | 1836 | 0 | 23
38961.3705 | 1752 | 0 | 23
38961.371 | 2256 | 0 | 23
38961.3715 | 1777 | 0 | 23
38961.372 | 2095 | 0 | 23
38961.3725 | 1961 | 0 | 23
38961.3729 | 2138 | 0 | 23
38961.3734 | 1809 | 0 | 23
38961.3739 | 2297 | 0 | 23
38961.3744 | 1851 | 0 | 23
38961.3749 | 1818 | 0 | 23
38961.3754 | 1825 | 0 | 23
38961.3759 | 2179 | 0 | 23
38961.3763 | 1927 | 0 | 23
38961.3768 | 2229 | 0 | 23
38961.3773 | 1912 | 0 | 23
38961.3778 | 2205 | 0 | 23
38961.3783 | 1928 | 0 | 23
38961.3788 | 2263 | 0 | 23
38961.3793 | 1865 | 0 | 23
38961.3797 | 2334 | 0 | 23
38961.3802 | 2353 | 0 | 23
38961.3807 | 1856 | 0 | 23
23
38961.3389 | 1 | 0 | 24
38961.3394 | 1 | 0 | 24
38961.3399 | 1 | 0 | 24
38961.3404 | 1 | 0 | 24
38961.3409 | 1 | 0 | 24
38961.3414 | 1 | 0 | 24
38961.3419 | 1 | 0 | 24
38961.3423 | 1 | 0 | 24
38961.3428 | 1 | 0 | 24
38961.3433 | 1 | 0 | 24
38961.3438 | 1 | 0 | 24
38961.3443 | 1 | 0 | 24
38961.3448 | 1 | 0 | 24
38961.3453 | 1 | 0 | 24
38961.3457 | 1 | 0 | 24
38961.3462 | 1 | 0 | 24
38961.3467 | 1 | 0 | 24
38961.3472 | 1 | 0 | 24
38961.3477 | 1 | 0 | 24
38961.3482 | 1 | 0 | 24
38961.3487 | 1 | 0 | 24
38961.3491 | 1 | 0 | 24
38961.3496 | 1 | 0 | 24
38961.3501 | 1 | 0 | 24
38961.3506 | 1 | 0 | 24
38961.3511 | 1 | 0 | 24
38961.3516 | 1 | 0 | 24
38961.3521 | 1 | 0 | 24
38961.3525 | 1 | 0 | 24
38961.3535 | 1 | 0 | 24
38961.354 | 1 | 0 | 24
38961.3545 | 1 | 0 | 24
38961.355 | 1 | 0 | 24
38961.3555 | 1 | 0 | 24
38961.3559 | 1 | 0 | 24
38961.3564 | 1 | 0 | 24
38961.3569 | 1 | 0 | 24
38961.3574 | 1 | 0 | 24
38961.3584 | 1865 | 0 | 24
38961.3589 | 1818 | 0 | 24
38961.3594 | 1878 | 0 | 24
38961.3598 | 1958 | 0 | 24
38961.3603 | 2024 | 0 | 24
38961.3608 | 1842 | 0 | 24
38961.3613 | 2152 | 0 | 24
38961.3618 | 2050 | 0 | 24
38961.3623 | 2287 | 0 | 24
38961.3628 | 2050 | 0 | 24
38961.3632 | 2283 | 0 | 24
38961.3637 | 2245 | 0 | 24
38961.3642 | 1907 | 0 | 24
38961.3647 | 2370 | 0 | 24
38961.3652 | 2052 | 0 | 24
38961.3657 | 2157 | 0 | 24
38961.3662 | 1874 | 0 | 24
38961.3666 | 2202 | 1 | 24
38961.3671 | 1941 | 1 | 24
38961.3676 | 2188 | 1 | 24
38961.3681 | 1901 | 1 | 24
38961.3686 | 2097 | 1 | 24
38961.3691 | 2299 | 0 | 24
38961.3696 | 2227 | 0 | 24
38961.37 | 2067 | 0 | 24
38961.3705 | 2395 | 0 | 24
38961.371 | 2136 | 0 | 24
38961.3715 | 2292 | 0 | 24
38961.372 | 2271 | 0 | 24
38961.3725 | 2146 | 0 | 24
38961.373 | 1987 | 0 | 24
38961.3734 | 2374 | 0 | 24
38961.3739 | 2103 | 0 | 24
38961.3744 | 2381 | 0 | 24
38961.3749 | 2033 | 1 | 24
38961.3754 | 2367 | 0 | 24
38961.3759 | 2293 | 0 | 24
38961.3764 | 1882 | 0 | 24
38961.3769 | 2158 | 0 | 24
38961.3773 | 1953 | 0 | 24
38961.3778 | 2138 | 0 | 24
38961.3783 | 2305 | 0 | 24
38961.3788 | 2200 | 0 | 24
38961.3793 | 2025 | 0 | 24
38961.3798 | 2215 | 0 | 24
38961.3803 | 1975 | 0 | 24
38961.3807 | 2387 | 0 | 24
24
38961.3389 | 1 | 0 | 25
38961.3394 | 1 | 0 | 25
38961.3399 | 1 | 0 | 25
38961.3404 | 1 | 0 | 25
38961.3409 | 1 | 1 | 25
38961.3414 | 1 | 0 | 25
38961.3419 | 1 | 0 | 25
38961.3423 | 1 | 0 | 25
38961.3428 | 1 | 0 | 25
38961.3433 | 1 | 0 | 25
38961.3438 | 1 | 0 | 25
38961.3443 | 1 | 0 | 25
38961.3448 | 1 | 0 | 25
38961.3453 | 1 | 0 | 25
38961.3458 | 1 | 0 | 25
38961.3462 | 1 | 0 | 25
38961.3467 | 1 | 0 | 25
38961.3472 | 1 | 0 | 25
38961.3477 | 1 | 0 | 25
38961.3482 | 1 | 0 | 25
38961.3487 | 1 | 0 | 25
38961.3492 | 1 | 0 | 25
38961.3496 | 1 | 0 | 25
38961.3501 | 1 | 0 | 25
38961.3506 | 1 | 0 | 25
38961.3511 | 1 | 0 | 25
38961.3516 | 1 | 0 | 25
38961.3521 | 1 | 0 | 25
38961.3526 | 1 | 0 | 25
38961.353 | 1 | 0 | 25
38961.3535 | 1 | 0 | 25
38961.354 | 1 | 0 | 25
38961.3545 | 1 | 0 | 25
38961.355 | 1 | 0 | 25
38961.3555 | 1 | 0 | 25
38961.356 | 1 | 0 | 25
38961.3564 | 1 | 0 | 25
38961.3569 | 1 | 0 | 25
38961.3574 | 1 | 0 | 25
38961.3579 | 2 | 0 | 25
38961.3584 | 2 | 0 | 25
38961.3589 | 2 | 0 | 25
38961.3594 | 2 | 0 | 25
38961.3598 | 3 | 0 | 25
38961.3603 | 3 | 0 | 25
38961.3608 | 2 | 0 | 25
38961.3613 | 2 | 0 | 25
38961.3618 | 2 | 0 | 25
38961.3623 | 2 | 0 | 25
38961.3628 | 2 | 0 | 25
38961.3633 | 2 | 0 | 25
38961.3637 | 2 | 0 | 25
38961.3642 | 2 | 0 | 25
38961.3647 | 3 | 0 | 25
38961.3652 | 3 | 0 | 25
38961.3657 | 3 | 0 | 25
38961.3662 | 5 | 0 | 25
38961.3667 | 25 | 0 | 25
38961.3671 | 37 | 0 | 25
38961.3676 | 546 | 1 | 25
38961.3681 | 111 | 1 | 25
38961.3686 | 67 | 1 | 25
38961.3691 | 2037 | 0 | 25
38961.3696 | 1918 | 0 | 25
38961.3701 | 2161 | 0 | 25
38961.3705 | 2075 | 0 | 25
38961.371 | 2267 | 0 | 25
38961.3715 | 1858 | 0 | 25
38961.372 | 1858 | 0 | 25
38961.3725 | 2214 | 0 | 25
38961.373 | 2172 | 0 | 25
38961.3735 | 1932 | 0 | 25
38961.3739 | 2186 | 0 | 25
38961.3744 | 2336 | 0 | 25
38961.3749 | 1812 | 0 | 25
38961.3754 | 1890 | 0 | 25
38961.3759 | 1834 | 0 | 25
38961.3764 | 1857 | 0 | 25
38961.3769 | 1979 | 0 | 25
38961.3773 | 2292 | 0 | 25
38961.3778 | 2128 | 0 | 25
38961.3783 | 2263 | 0 | 25
38961.3788 | 2248 | 0 | 25
38961.3793 | 1828 | 0 | 25
38961.3798 | 2062 | 0 | 25
38961.3803 | 1983 | 0 | 25
38961.3808 | 2063 | 0 | 25
25
38961.339 | 1 | 0 | 26
38961.3395 | 1 | 0 | 26
38961.3399 | 1 | 0 | 26
38961.3404 | 1 | 0 | 26
38961.3409 | 1 | 0 | 26
38961.3414 | 1 | 0 | 26
38961.3419 | 1 | 0 | 26
38961.3424 | 1 | 0 | 26
38961.3429 | 1 | 0 | 26
38961.3433 | 1 | 0 | 26
38961.3438 | 1 | 0 | 26
38961.3443 | 1 | 0 | 26
38961.3448 | 1 | 0 | 26
38961.3453 | 1 | 0 | 26
38961.3458 | 1 | 0 | 26
38961.3463 | 1 | 0 | 26
38961.3467 | 1 | 0 | 26
38961.3472 | 1 | 0 | 26
38961.3477 | 1 | 0 | 26
38961.3482 | 1 | 0 | 26
38961.3487 | 1 | 0 | 26
38961.3492 | 1 | 0 | 26
38961.3497 | 1 | 0 | 26
38961.3502 | 1 | 0 | 26
38961.3506 | 1 | 0 | 26
38961.3511 | 1 | 0 | 26
38961.3516 | 1 | 0 | 26
38961.3521 | 1 | 0 | 26
38961.3526 | 1 | 0 | 26
38961.3531 | 1 | 0 | 26
38961.3536 | 1 | 0 | 26
38961.354 | 1 | 0 | 26
38961.3545 | 1 | 0 | 26
38961.355 | 1 | 0 | 26
38961.3555 | 1 | 0 | 26
38961.356 | 1 | 0 | 26
38961.3565 | 1 | 0 | 26
38961.357 | 1 | 0 | 26
38961.3574 | 1 | 0 | 26
38961.3579 | 1509 | 0 | 26
38961.3584 | 2164 | 0 | 26
38961.3589 | 2350 | 0 | 26
38961.3594 | 2148 | 0 | 26
38961.3599 | 2379 | 0 | 26
38961.3604 | 2332 | 0 | 26
38961.3608 | 2149 | 0 | 26
38961.3613 | 2295 | 0 | 26
38961.3618 | 2340 | 0 | 26
38961.3623 | 1952 | 0 | 26
38961.3628 | 1903 | 0 | 26
38961.3633 | 2254 | 0 | 26
38961.3638 | 2168 | 0 | 26
38961.3642 | 1847 | 0 | 26
38961.3647 | 2277 | 0 | 26
38961.3652 | 2263 | 0 | 26
38961.3657 | 2239 | 0 | 26
38961.3662 | 1865 | 0 | 26
38961.3667 | 1851 | 0 | 26
38961.3672 | 2361 | 0 | 26
38961.3676 | 2235 | 0 | 26
38961.3681 | 2290 | 0 | 26
38961.3686 | 1983 | 0 | 26
38961.3691 | 2286 | 0 | 26
38961.3696 | 2092 | 0 | 26
38961.3701 | 1845 | 0 | 26
38961.3706 | 2168 | 0 | 26
38961.371 | 1895 | 0 | 26
38961.3715 | 2004 | 0 | 26
38961.372 | 2043 | 0 | 26
38961.3725 | 2057 | 0 | 26
38961.373 | 2153 | 0 | 26
38961.3735 | 2051 | 0 | 26
38961.374 | 2362 | 0 | 26
38961.3744 | 2065 | 0 | 26
38961.3749 | 2038 | 0 | 26
38961.3754 | 1833 | 0 | 26
38961.3759 | 2362 | 0 | 26
38961.3764 | 1848 | 0 | 26
38961.3769 | 1941 | 0 | 26
38961.3774 | 1988 | 0 | 26
38961.3778 | 1939 | 0 | 26
38961.3783 | 2355 | 0 | 26
38961.3788 | 2337 | 0 | 26
38961.3793 | 2111 | 0 | 26
38961.3798 | 2214 | 0 | 26
38961.3803 | 1906 | 0 | 26
38961.3808 | 1936 | 0 | 26
26
38961.339 | 1 | 0 | 27
38961.3395 | 1 | 0 | 27
38961.34 | 1 | 0 | 27
38961.3404 | 1 | 0 | 27
38961.3409 | 1 | 0 | 27
38961.3414 | 1 | 0 | 27
38961.3419 | 2 | 0 | 27
38961.3424 | 1 | 0 | 27
38961.3429 | 1 | 0 | 27
38961.3434 | 1 | 0 | 27
38961.3438 | 1 | 0 | 27
38961.3443 | 1 | 0 | 27
38961.3448 | 1 | 0 | 27
38961.3453 | 1 | 0 | 27
38961.3458 | 1 | 0 | 27
38961.3463 | 1 | 0 | 27
38961.3468 | 1 | 0 | 27
38961.3472 | 1 | 0 | 27
38961.3477 | 1 | 0 | 27
38961.3482 | 1 | 0 | 27
38961.3487 | 1 | 0 | 27
38961.3492 | 1 | 0 | 27
38961.3497 | 1 | 0 | 27
38961.3502 | 1 | 0 | 27
38961.3506 | 1 | 0 | 27
38961.3511 | 1 | 0 | 27
38961.3516 | 1 | 0 | 27
38961.3521 | 1 | 0 | 27
38961.3526 | 1 | 0 | 27
38961.3531 | 1 | 0 | 27
38961.3536 | 1 | 0 | 27
38961.3541 | 1 | 0 | 27
38961.3545 | 1 | 0 | 27
38961.355 | 1 | 0 | 27
38961.3555 | 1 | 0 | 27
38961.356 | 1 | 0 | 27
38961.3565 | 1 | 0 | 27
38961.357 | 1 | 0 | 27
38961.3575 | 1 | 0 | 27
38961.3579 | 2 | 0 | 27
38961.3584 | 3 | 0 | 27
38961.3589 | 3 | 0 | 27
38961.3594 | 3 | 0 | 27
38961.3599 | 3 | 0 | 27
38961.3604 | 2 | 0 | 27
38961.3609 | 2 | 0 | 27
38961.3613 | 2 | 0 | 27
38961.3618 | 2 | 0 | 27
38961.3623 | 2 | 0 | 27
38961.3628 | 2 | 0 | 27
38961.3633 | 2 | 0 | 27
38961.3638 | 2 | 0 | 27
38961.3643 | 2 | 0 | 27
38961.3647 | 2 | 0 | 27
38961.3652 | 2 | 0 | 27
38961.3657 | 3 | 0 | 27
38961.3662 | 5 | 0 | 27
38961.3667 | 25 | 0 | 27
38961.3672 | 33 | 0 | 27
38961.3677 | 378 | 1 | 27
38961.3681 | 403 | 0 | 27
38961.3686 | 78 | 0 | 27
38961.3691 | 1621 | 0 | 27
38961.3696 | 1905 | 0 | 27
38961.3701 | 2184 | 0 | 27
38961.3706 | 2244 | 0 | 27
38961.3711 | 2273 | 0 | 27
38961.3716 | 2226 | 0 | 27
38961.372 | 2025 | 0 | 27
38961.3725 | 2249 | 0 | 27
38961.373 | 1966 | 0 | 27
38961.3735 | 1840 | 0 | 27
38961.374 | 2244 | 0 | 27
38961.3745 | 1957 | 0 | 27
38961.375 | 1984 | 0 | 27
38961.3754 | 1864 | 0 | 27
38961.3759 | 2353 | 0 | 27
38961.3764 | 2211 | 0 | 27
38961.3769 | 2292 | 0 | 27
38961.3774 | 1984 | 0 | 27
38961.3779 | 1891 | 0 | 27
38961.3784 | 2342 | 0 | 27
38961.3788 | 2128 | 0 | 27
38961.3793 | 2303 | 0 | 27
38961.3798 | 2111 | 0 | 27
38961.3803 | 2214 | 0 | 27
38961.3808 | 2320 | 0 | 27
27
38961.339 | 1 | 0 | 28
38961.3395 | 1 | 0 | 28
38961.34 | 1 | 0 | 28
38961.3405 | 1 | 0 | 28
38961.3409 | 1 | 0 | 28
38961.3414 | 1 | 1 | 28
38961.3419 | 1 | 0 | 28
38961.3424 | 1 | 0 | 28
38961.3429 | 1 | 0 | 28
38961.3434 | 1 | 0 | 28
38961.3439 | 1 | 0 | 28
38961.3444 | 1 | 0 | 28
38961.3448 | 1 | 0 | 28
38961.3453 | 1 | 0 | 28
38961.3458 | 1 | 0 | 28
38961.3463 | 1 | 0 | 28
38961.3468 | 1 | 0 | 28
38961.3473 | 1 | 0 | 28
38961.3477 | 1 | 0 | 28
38961.3482 | 1 | 0 | 28
38961.3487 | 1 | 0 | 28
38961.3492 | 1 | 0 | 28
38961.3497 | 1 | 0 | 28
38961.3502 | 1 | 0 | 28
38961.3507 | 1 | 0 | 28
38961.3512 | 1 | 0 | 28
38961.3516 | 1 | 0 | 28
38961.3521 | 1 | 0 | 28
38961.3526 | 1 | 0 | 28
38961.3531 | 1 | 0 | 28
38961.3536 | 1 | 0 | 28
38961.3541 | 1 | 0 | 28
38961.3545 | 1 | 0 | 28
38961.355 | 1 | 0 | 28
38961.3555 | 1 | 0 | 28
38961.356 | 1 | 0 | 28
38961.3565 | 1 | 0 | 28
38961.357 | 1 | 0 | 28
38961.3575 | 1 | 0 | 28
38961.358 | 1920 | 0 | 28
38961.3584 | 2319 | 0 | 28
38961.3589 | 1915 | 0 | 28
38961.3594 | 2203 | 0 | 28
38961.3599 | 2130 | 0 | 28
38961.3604 | 2284 | 0 | 28
38961.3609 | 2345 | 0 | 28
38961.3614 | 2109 | 0 | 28
38961.3618 | 2316 | 0 | 28
38961.3623 | 2042 | 0 | 28
38961.3628 | 1975 | 0 | 28
38961.3633 | 2361 | 0 | 28
38961.3638 | 2322 | 0 | 28
38961.3643 | 2316 | 0 | 28
38961.3648 | 2076 | 0 | 28
38961.3652 | 2156 | 0 | 28
38961.3657 | 1884 | 0 | 28
38961.3662 | 2190 | 0 | 28
38961.3667 | 2087 | 0 | 28
38961.3672 | 2309 | 0 | 28
38961.3677 | 2401 | 0 | 28
38961.3682 | 2081 | 0 | 28
38961.3686 | 2145 | 0 | 28
38961.3691 | 2409 | 0 | 28
38961.3696 | 2080 | 0 | 28
38961.3701 | 2271 | 0 | 28
38961.3706 | 2286 | 0 | 28
38961.3711 | 1949 | 0 | 28
38961.3716 | 2065 | 0 | 28
38961.372 | 2275 | 0 | 28
38961.3725 | 2027 | 0 | 28
38961.373 | 2400 | 0 | 28
38961.3735 | 2012 | 0 | 28
38961.374 | 2278 | 0 | 28
38961.3745 | 1975 | 0 | 28
38961.375 | 2157 | 0 | 28
38961.3755 | 2199 | 0 | 28
38961.3759 | 2399 | 0 | 28
38961.3764 | 2171 | 0 | 28
38961.3769 | 2379 | 0 | 28
38961.3774 | 1921 | 0 | 28
38961.3779 | 1917 | 0 | 28
38961.3784 | 2351 | 0 | 28
38961.3789 | 2085 | 0 | 28
38961.3793 | 2403 | 0 | 28
38961.3798 | 2382 | 0 | 28
38961.3803 | 2259 | 0 | 28
38961.3808 | 2303 | 0 | 28
28
38961.339 | 1 | 0 | 29
38961.3395 | 1 | 0 | 29
38961.34 | 1 | 0 | 29
38961.3405 | 1 | 0 | 29
38961.341 | 1 | 0 | 29
38961.3414 | 1 | 0 | 29
38961.3419 | 1 | 0 | 29
38961.3424 | 1 | 0 | 29
38961.3429 | 1 | 0 | 29
38961.3434 | 1 | 0 | 29
38961.3439 | 1 | 0 | 29
38961.3444 | 1 | 0 | 29
38961.3448 | 1 | 0 | 29
38961.3453 | 1 | 0 | 29
38961.3458 | 1 | 0 | 29
38961.3463 | 1 | 0 | 29
38961.3468 | 1 | 0 | 29
38961.3473 | 1 | 0 | 29
38961.3478 | 1 | 0 | 29
38961.3483 | 1 | 0 | 29
38961.3487 | 1 | 0 | 29
38961.3492 | 1 | 0 | 29
38961.3497 | 1 | 0 | 29
38961.3502 | 1 | 0 | 29
38961.3507 | 1 | 0 | 29
38961.3512 | 1 | 0 | 29
38961.3517 | 1 | 0 | 29
38961.3521 | 1 | 0 | 29
38961.3526 | 1 | 0 | 29
38961.3531 | 1 | 0 | 29
38961.3536 | 1 | 0 | 29
38961.3541 | 1 | 0 | 29
38961.3546 | 1 | 0 | 29
38961.3551 | 1 | 0 | 29
38961.3555 | 1 | 0 | 29
38961.356 | 1 | 0 | 29
38961.3565 | 1 | 0 | 29
38961.357 | 1 | 0 | 29
38961.3575 | 3 | 0 | 29
38961.358 | 1225 | 1 | 29
38961.3585 | 2297 | 43 | 29
38961.3589 | 1950 | 28 | 29
38961.3594 | 1964 | 24 | 29
38961.3599 | 1910 | 13 | 29
38961.3604 | 2138 | 12 | 29
38961.3609 | 2391 | 10 | 29
38961.3614 | 2000 | 8 | 29
38961.3619 | 1922 | 6 | 29
38961.3623 | 2115 | 6 | 29
38961.3628 | 2198 | 6 | 29
38961.3633 | 1948 | 2 | 29
38961.3638 | 2109 | 2 | 29
38961.3643 | 1920 | 2 | 29
38961.3648 | 2162 | 1 | 29
38961.3653 | 2345 | 2 | 29
38961.3658 | 2123 | 2 | 29
38961.3662 | 2383 | 2 | 29
38961.3667 | 1896 | 1 | 29
38961.3672 | 1901 | 1 | 29
38961.3677 | 1845 | 1 | 29
38961.3682 | 2284 | 1 | 29
38961.3687 | 1987 | 1 | 29
38961.3692 | 1921 | 1 | 29
38961.3696 | 2150 | 0 | 29
38961.3701 | 2346 | 0 | 29
38961.3706 | 2186 | 0 | 29
38961.3711 | 2182 | 0 | 29
38961.3716 | 2302 | 0 | 29
38961.3721 | 2365 | 0 | 29
38961.3726 | 2279 | 0 | 29
38961.373 | 2351 | 0 | 29
38961.3735 | 2362 | 0 | 29
38961.374 | 2199 | 0 | 29
38961.3745 | 1876 | 0 | 29
38961.375 | 2366 | 0 | 29
38961.3755 | 2286 | 0 | 29
38961.376 | 2264 | 0 | 29
38961.3764 | 1842 | 0 | 29
38961.3769 | 2212 | 0 | 29
38961.3774 | 2149 | 0 | 29
38961.3779 | 1877 | 0 | 29
38961.3784 | 2315 | 1 | 29
38961.3789 | 2357 | 0 | 29
38961.3794 | 1844 | 0 | 29
38961.3798 | 2118 | 1 | 29
38961.3803 | 2061 | 1 | 29
38961.3808 | 2065 | 1 | 29
29
38961.339 | 1 | 0 | 30
38961.3395 | 1 | 0 | 30
38961.34 | 1 | 0 | 30
38961.3405 | 1 | 1 | 30
38961.341 | 1 | 0 | 30
38961.3415 | 1 | 0 | 30
38961.3419 | 1 | 0 | 30
38961.3424 | 1 | 0 | 30
38961.3429 | 1 | 0 | 30
38961.3434 | 1 | 0 | 30
38961.3439 | 1 | 0 | 30
38961.3444 | 1 | 0 | 30
38961.3449 | 1 | 0 | 30
38961.3453 | 1 | 1 | 30
38961.3458 | 1 | 0 | 30
38961.3463 | 1 | 0 | 30
38961.3468 | 1 | 0 | 30
38961.3473 | 1 | 0 | 30
38961.3478 | 1 | 0 | 30
38961.3483 | 1 | 0 | 30
38961.3487 | 1 | 0 | 30
38961.3492 | 1 | 0 | 30
38961.3497 | 1 | 0 | 30
38961.3502 | 1 | 0 | 30
38961.3507 | 1 | 0 | 30
38961.3512 | 1 | 0 | 30
38961.3517 | 1 | 0 | 30
38961.3522 | 1 | 0 | 30
38961.3526 | 1 | 0 | 30
38961.3531 | 1 | 0 | 30
38961.3536 | 1 | 0 | 30
38961.3541 | 1 | 0 | 30
38961.3546 | 1 | 0 | 30
38961.3551 | 1 | 0 | 30
38961.3556 | 1 | 0 | 30
38961.356 | 1 | 0 | 30
38961.3565 | 1 | 0 | 30
38961.357 | 1 | 0 | 30
38961.3575 | 1 | 0 | 30
38961.358 | 1909 | 0 | 30
38961.3585 | 2078 | 36 | 30
38961.359 | 2297 | 32 | 30
38961.3594 | 1929 | 21 | 30
38961.3599 | 2056 | 14 | 30
38961.3604 | 2133 | 10 | 30
38961.3609 | 2360 | 5 | 30
38961.3614 | 2194 | 8 | 30
38961.3619 | 1907 | 5 | 30
38961.3624 | 2410 | 5 | 30
38961.3628 | 1929 | 4 | 30
38961.3633 | 2232 | 2 | 30
38961.3638 | 1902 | 1 | 30
38961.3643 | 1926 | 1 | 30
38961.3648 | 1972 | 1 | 30
38961.3653 | 2100 | 1 | 30
38961.3658 | 2062 | 1 | 30
38961.3662 | 1993 | 1 | 30
38961.3667 | 2415 | 1 | 30
38961.3672 | 2127 | 1 | 30
38961.3677 | 2055 | 1 | 30
38961.3682 | 2415 | 0 | 30
38961.3687 | 2268 | 1 | 30
38961.3692 | 2091 | 1 | 30
38961.3697 | 2217 | 0 | 30
38961.3701 | 2132 | 0 | 30
38961.3706 | 2061 | 0 | 30
38961.3711 | 2174 | 0 | 30
38961.3716 | 1875 | 0 | 30
38961.3721 | 2069 | 0 | 30
38961.3726 | 2065 | 0 | 30
38961.3731 | 1955 | 0 | 30
38961.3735 | 2403 | 0 | 30
38961.374 | 2144 | 0 | 30
38961.3745 | 2401 | 0 | 30
38961.375 | 2193 | 0 | 30
38961.3755 | 2402 | 0 | 30
38961.376 | 2181 | 0 | 30
38961.3765 | 2019 | 0 | 30
38961.3769 | 1861 | 0 | 30
38961.3774 | 2343 | 0 | 30
38961.3779 | 1987 | 0 | 30
38961.3784 | 2280 | 0 | 30
38961.3789 | 1871 | 0 | 30
38961.3794 | 2010 | 0 | 30
38961.3799 | 2365 | 0 | 30
38961.3803 | 2075 | 0 | 30
38961.3808 | 2227 | 0 | 30
30

## Test Facts
Last row in IRMS data sheets: | 92
Time when Penlight power was initiated: | 140