## Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Test Summary
Supplemental Penlight Thermal Bundle Test 1
This test was added to the Penlight matrix at the request of the fire modeling teams. The objective of the test was to provide a test involving a single cable plus a cable bundle where the cable bundle is more fully instrumented for thermal response. Due to limitations on the quantity of combustible material that we could place in Penlight, most of the bundle tests had the bundle monitored for electrical performance, and a single cable monitored for thermal response. This "special" test is a direct analog to these other bundle tests, except that the bundle is also monitored for temperature response. There was no electrical performance data gathered in this test.

## TempData
DAQ Time | Penlight Time | Shroud | Cable A | Cable B | Cable E | Single Cable | Tray Rung
0 | -100 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
1 | -99 | 18.8 | 23.8 | 23.7 | 24.2 | 23.5 | 27
2 | -98 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
3 | -97 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
4 | -96 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
5 | -95 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
6 | -94 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
7 | -93 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
8 | -92 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
9 | -91 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
10 | -90 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
11 | -89 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
12 | -88 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
13 | -87 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
14 | -86 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
15 | -85 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
16 | -84 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
17 | -83 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
18 | -82 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
19 | -81 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
20 | -80 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
21 | -79 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
22 | -78 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
23 | -77 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
24 | -76 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
25 | -75 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
26 | -74 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
27 | -73 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
28 | -72 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
29 | -71 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
30 | -70 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
31 | -69 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
32 | -68 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
33 | -67 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
34 | -66 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
35 | -65 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
36 | -64 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
37 | -63 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
38 | -62 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
39 | -61 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
40 | -60 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
41 | -59 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
42 | -58 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
43 | -57 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
44 | -56 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
45 | -55 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
46 | -54 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
47 | -53 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
48 | -52 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
49 | -51 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
50 | -50 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
51 | -49 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
52 | -48 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
53 | -47 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
54 | -46 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
55 | -45 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27
56 | -44 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
57 | -43 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
58 | -42 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
59 | -41 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
60 | -40 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
61 | -39 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
62 | -38 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
63 | -37 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
64 | -36 | 18.7 | 23.7 | 23.7 | 24.2 | 23.6 | 27
65 | -35 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
66 | -34 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
67 | -33 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
68 | -32 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
69 | -31 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
70 | -30 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
71 | -29 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
72 | -28 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
73 | -27 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27
74 | -26 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
75 | -25 | 18.8 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
76 | -24 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
77 | -23 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
78 | -22 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
79 | -21 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
80 | -20 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
81 | -19 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
82 | -18 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
83 | -17 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
84 | -16 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
85 | -15 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
86 | -14 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
87 | -13 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
88 | -12 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
89 | -11 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
90 | -10 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
91 | -9 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
92 | -8 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
93 | -7 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
94 | -6 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
95 | -5 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
96 | -4 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
97 | -3 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
98 | -2 | 18.7 | 23.8 | 23.7 | 24.2 | 23.6 | 27.1
99 | -1 | 18.8 | 23.8 | 23.5 | 24.3 | 23.8 | 27.6
100 | 0 | 18.8 | 23.9 | 23.5 | 24.3 | 23.9 | 28.3
101 | 1 | 19 | 23.9 | 23.5 | 24.3 | 23.9 | 28.5
102 | 2 | 19.8 | 23.8 | 23.5 | 24.3 | 23.9 | 28.6
103 | 3 | 21.6 | 23.8 | 23.5 | 24.3 | 23.9 | 28.6
104 | 4 | 24.1 | 23.8 | 23.5 | 24.3 | 23.9 | 28.6
105 | 5 | 27.3 | 23.8 | 23.5 | 24.3 | 23.9 | 28.6
106 | 6 | 31 | 23.8 | 23.5 | 24.3 | 23.9 | 28.7
107 | 7 | 35.1 | 23.8 | 23.6 | 24.2 | 23.9 | 28.7
108 | 8 | 39.4 | 23.8 | 23.6 | 24.2 | 23.9 | 28.7
109 | 9 | 43.8 | 23.8 | 23.6 | 24.2 | 23.9 | 28.8
110 | 10 | 48.4 | 23.8 | 23.6 | 24.2 | 23.9 | 28.8
111 | 11 | 53.1 | 23.9 | 23.6 | 24.2 | 23.9 | 28.9
112 | 12 | 58 | 23.9 | 23.6 | 24.2 | 23.9 | 28.9
113 | 13 | 62.9 | 23.9 | 23.6 | 24.2 | 23.9 | 29
114 | 14 | 67.9 | 23.9 | 23.7 | 24.3 | 23.9 | 29.1
115 | 15 | 72.9 | 23.9 | 23.7 | 24.3 | 24 | 29.1
116 | 16 | 78 | 24 | 23.7 | 24.3 | 24 | 29.3
117 | 17 | 83 | 24 | 23.8 | 24.3 | 24.1 | 29.4
118 | 18 | 88 | 24 | 23.8 | 24.3 | 24.1 | 29.5
119 | 19 | 92.9 | 24.1 | 23.9 | 24.3 | 24.1 | 29.6
120 | 20 | 98 | 24.1 | 23.9 | 24.3 | 24.2 | 29.7
121 | 21 | 103.1 | 24.2 | 24 | 24.3 | 24.3 | 29.8
122 | 22 | 108.4 | 24.3 | 24 | 24.3 | 24.3 | 30
123 | 23 | 113.7 | 24.3 | 24.1 | 24.3 | 24.4 | 30.1
124 | 24 | 119.1 | 24.4 | 24.2 | 24.3 | 24.5 | 30.3
125 | 25 | 124.5 | 24.5 | 24.2 | 24.3 | 24.6 | 30.5
126 | 26 | 130 | 24.6 | 24.3 | 24.3 | 24.7 | 30.7
127 | 27 | 135.5 | 24.7 | 24.4 | 24.3 | 24.7 | 30.9
128 | 28 | 140.9 | 24.8 | 24.5 | 24.3 | 24.9 | 31.1
129 | 29 | 146.4 | 24.9 | 24.6 | 24.3 | 25 | 31.4
130 | 30 | 151.8 | 25 | 24.7 | 24.3 | 25.1 | 31.6
131 | 31 | 157.2 | 25.1 | 24.9 | 24.3 | 25.2 | 31.9
132 | 32 | 162.6 | 25.3 | 25 | 24.4 | 25.3 | 32.2
133 | 33 | 168 | 25.4 | 25.1 | 24.4 | 25.5 | 32.5
134 | 34 | 173.4 | 25.6 | 25.3 | 24.4 | 25.7 | 32.8
135 | 35 | 178.9 | 25.7 | 25.4 | 24.4 | 25.8 | 33.2
136 | 36 | 184.4 | 25.9 | 25.6 | 24.4 | 26 | 33.5
137 | 37 | 189.9 | 26.1 | 25.8 | 24.4 | 26.2 | 33.8
138 | 38 | 195.2 | 26.3 | 26 | 24.4 | 26.4 | 34.2
139 | 39 | 200.7 | 26.5 | 26.2 | 24.5 | 26.7 | 34.7
140 | 40 | 206.1 | 26.7 | 26.4 | 24.5 | 26.9 | 35.1
141 | 41 | 211.4 | 27 | 26.6 | 24.5 | 27.1 | 35.5
142 | 42 | 216.8 | 27.2 | 26.8 | 24.5 | 27.4 | 36
143 | 43 | 222.1 | 27.5 | 27.1 | 24.5 | 27.7 | 36.5
144 | 44 | 227.5 | 27.8 | 27.4 | 24.6 | 28 | 37
145 | 45 | 232.8 | 28 | 27.6 | 24.6 | 28.2 | 37.5
146 | 46 | 238 | 28.3 | 27.9 | 24.6 | 28.6 | 38
147 | 47 | 243.2 | 28.7 | 28.2 | 24.6 | 28.9 | 38.6
148 | 48 | 248.5 | 29 | 28.5 | 24.7 | 29.2 | 39.2
149 | 49 | 253.6 | 29.3 | 28.8 | 24.7 | 29.6 | 39.8
150 | 50 | 258.8 | 29.7 | 29.2 | 24.7 | 29.9 | 40.4
151 | 51 | 264.1 | 30.1 | 29.5 | 24.7 | 30.3 | 41.1
152 | 52 | 269.3 | 30.5 | 29.9 | 24.8 | 30.7 | 41.8
153 | 53 | 274.4 | 30.9 | 30.2 | 24.8 | 31.1 | 42.5
154 | 54 | 279.3 | 31.3 | 30.6 | 24.8 | 31.6 | 43.2
155 | 55 | 284.3 | 31.7 | 31 | 24.9 | 32 | 44
156 | 56 | 289.3 | 32.2 | 31.4 | 24.9 | 32.5 | 44.8
157 | 57 | 294.4 | 32.6 | 31.9 | 24.9 | 33 | 45.7
158 | 58 | 299.3 | 33.1 | 32.3 | 25 | 33.5 | 46.5
159 | 59 | 304.2 | 33.6 | 32.8 | 25 | 34 | 47.4
160 | 60 | 309 | 34.1 | 33.2 | 25.1 | 34.5 | 48.3
161 | 61 | 313.9 | 34.6 | 33.7 | 25.1 | 35.1 | 49.2
162 | 62 | 318.6 | 35.2 | 34.1 | 25.2 | 35.6 | 49.8
163 | 63 | 323.3 | 35.7 | 34.6 | 25.3 | 36.2 | 50.9
164 | 64 | 328.1 | 36.3 | 35.2 | 25.4 | 36.8 | 51.9
165 | 65 | 332.2 | 36.9 | 35.7 | 25.4 | 37.4 | 52.9
166 | 66 | 336 | 37.5 | 36.3 | 25.5 | 38.1 | 54
167 | 67 | 339.5 | 38.1 | 36.8 | 25.6 | 38.7 | 55
168 | 68 | 342.7 | 38.7 | 37.4 | 25.6 | 39.4 | 56
169 | 69 | 345.7 | 39.3 | 37.9 | 25.7 | 40.1 | 57.1
170 | 70 | 348.7 | 40 | 38.5 | 25.8 | 40.8 | 58.2
171 | 71 | 351.3 | 40.6 | 39.2 | 25.9 | 41.5 | 59.2
172 | 72 | 353.9 | 41.2 | 39.8 | 25.9 | 42.2 | 60.2
173 | 73 | 356.3 | 41.9 | 40.4 | 26 | 42.9 | 60.9
174 | 74 | 358.5 | 42.6 | 41.1 | 26.1 | 43.6 | 61.8
175 | 75 | 360.4 | 43.2 | 41.7 | 26.2 | 44.4 | 62.9
176 | 76 | 361.9 | 43.9 | 42.3 | 26.3 | 45.1 | 63.8
177 | 77 | 363.1 | 44.6 | 43 | 26.4 | 45.9 | 64.8
178 | 78 | 364.1 | 45.3 | 43.7 | 26.5 | 46.7 | 65.9
179 | 79 | 365 | 46 | 44.3 | 26.6 | 47.5 | 67
180 | 80 | 365.6 | 46.7 | 45.1 | 26.7 | 48.3 | 68
181 | 81 | 366.1 | 47.4 | 45.8 | 26.8 | 49.1 | 69.1
182 | 82 | 366.4 | 48.1 | 46.4 | 26.9 | 50 | 70.1
183 | 83 | 366.7 | 48.8 | 47.1 | 27 | 50.8 | 71.1
184 | 84 | 366.9 | 49.5 | 47.8 | 27.1 | 51.7 | 72.1
185 | 85 | 366.9 | 50.2 | 48.4 | 27.2 | 52.5 | 73.2
186 | 86 | 366.9 | 50.9 | 49 | 27.3 | 53.4 | 74.2
187 | 87 | 366.8 | 51.6 | 49.7 | 27.5 | 54.3 | 75.2
188 | 88 | 366.5 | 52.3 | 50.3 | 27.6 | 55.2 | 76.3
189 | 89 | 366.1 | 53 | 51 | 27.7 | 56.1 | 77.3
190 | 90 | 365.7 | 53.7 | 51.6 | 27.8 | 57 | 78.3
191 | 91 | 365.2 | 54.3 | 52.2 | 28 | 57.9 | 79.3
192 | 92 | 364.8 | 55 | 52.8 | 28.1 | 58.7 | 80.3
193 | 93 | 364.4 | 55.7 | 53.4 | 28.3 | 59.6 | 81.2
194 | 94 | 363.9 | 56.3 | 54 | 28.4 | 60.5 | 82.2
195 | 95 | 363.4 | 57 | 54.6 | 28.5 | 61.4 | 83.1
196 | 96 | 362.9 | 57.6 | 55.2 | 28.7 | 62.2 | 84.1
197 | 97 | 362.3 | 58.2 | 55.8 | 28.8 | 63.1 | 85.1
198 | 98 | 361.7 | 58.9 | 56.3 | 29 | 63.9 | 86
199 | 99 | 361.1 | 59.5 | 56.9 | 29.1 | 64.7 | 86.9
200 | 100 | 360.6 | 60.1 | 57.4 | 29.3 | 65.6 | 87.8
201 | 101 | 360.2 | 60.7 | 58 | 29.4 | 66.4 | 88.7
202 | 102 | 359.8 | 61.3 | 58.5 | 29.6 | 67.2 | 89.6
203 | 103 | 359.3 | 61.9 | 59 | 29.7 | 68.1 | 90.5
204 | 104 | 358.8 | 62.4 | 59.5 | 29.9 | 68.9 | 91.4
205 | 105 | 358 | 63 | 60 | 30 | 69.7 | 92.2
206 | 106 | 357.2 | 63.6 | 60.5 | 30.2 | 70.4 | 93.1
207 | 107 | 356.6 | 64.1 | 61 | 30.4 | 71.2 | 93.9
208 | 108 | 356 | 64.7 | 61.5 | 30.5 | 72 | 94.8
209 | 109 | 355.4 | 65.2 | 61.9 | 30.7 | 72.7 | 95.6
210 | 110 | 354.8 | 65.7 | 62.4 | 30.8 | 73.5 | 96.4
211 | 111 | 354.2 | 66.3 | 62.8 | 31 | 74.2 | 97.2
212 | 112 | 353.4 | 66.8 | 63.3 | 31.2 | 75 | 98
213 | 113 | 352.7 | 67.3 | 63.7 | 31.3 | 75.7 | 98.7
214 | 114 | 352.2 | 67.8 | 64.1 | 31.5 | 76.4 | 99.6
215 | 115 | 351.6 | 68.2 | 64.5 | 31.7 | 77.1 | 100.3
216 | 116 | 350.9 | 68.7 | 64.9 | 31.8 | 77.8 | 101.1
217 | 117 | 350.1 | 69.2 | 65.3 | 32 | 78.5 | 101.8
218 | 118 | 349.4 | 69.7 | 65.7 | 32.2 | 79.2 | 102.6
219 | 119 | 348.8 | 70.1 | 66.1 | 32.3 | 79.8 | 103.3
220 | 120 | 348 | 70.6 | 66.5 | 32.5 | 80.5 | 104
221 | 121 | 347.2 | 71 | 66.9 | 32.7 | 81.1 | 104.7
222 | 122 | 346.5 | 71.5 | 67.1 | 32.9 | 81.9 | 105.5
223 | 123 | 345.9 | 71.9 | 67.5 | 33.1 | 82.5 | 106.2
224 | 124 | 345.3 | 72.4 | 67.8 | 33.2 | 83.1 | 106.9
225 | 125 | 344.8 | 72.8 | 68.1 | 33.4 | 83.7 | 107.6
226 | 126 | 344.2 | 73.2 | 68.5 | 33.6 | 84.3 | 108.3
227 | 127 | 343.7 | 73.6 | 68.8 | 33.8 | 84.9 | 109
228 | 128 | 343 | 74 | 69.1 | 33.9 | 85.5 | 109.7
229 | 129 | 342.3 | 74.4 | 69.5 | 34.1 | 86 | 110.4
230 | 130 | 341.7 | 74.8 | 69.8 | 34.3 | 86.6 | 111.2
231 | 131 | 341.1 | 75.1 | 70.1 | 34.5 | 87.1 | 112
232 | 132 | 340.5 | 75.5 | 70.4 | 34.7 | 87.7 | 112.5
233 | 133 | 340.1 | 75.9 | 70.7 | 34.8 | 88.2 | 113.1
234 | 134 | 339.6 | 76.2 | 71 | 35 | 88.7 | 113.9
235 | 135 | 339.2 | 76.6 | 71.3 | 35.2 | 89.3 | 114.7
236 | 136 | 338.8 | 77 | 71.5 | 35.4 | 89.8 | 115.5
237 | 137 | 338.5 | 77.3 | 71.8 | 35.6 | 90.3 | 116.2
238 | 138 | 338.3 | 77.7 | 72.1 | 35.8 | 90.9 | 116.9
239 | 139 | 338.1 | 78 | 72.3 | 35.9 | 91.4 | 117.5
240 | 140 | 338.2 | 78.3 | 72.6 | 36.1 | 91.8 | 118.1
241 | 141 | 338.2 | 78.7 | 72.9 | 36.3 | 92.3 | 118.8
242 | 142 | 338.4 | 79 | 73.1 | 36.5 | 92.8 | 119.4
243 | 143 | 338.8 | 79.3 | 73.4 | 36.7 | 93.3 | 120
244 | 144 | 339.3 | 79.7 | 73.6 | 36.8 | 93.8 | 120.7
245 | 145 | 339.8 | 80 | 73.9 | 37 | 94.3 | 121.3
246 | 146 | 340.2 | 80.3 | 74.1 | 37.2 | 94.7 | 121.9
247 | 147 | 340.7 | 80.6 | 74.4 | 37.4 | 95.2 | 122.6
248 | 148 | 341.3 | 80.9 | 74.6 | 37.6 | 95.7 | 123.2
249 | 149 | 342 | 81.2 | 74.9 | 37.8 | 96.2 | 123.8
250 | 150 | 342.7 | 81.6 | 75.1 | 38 | 96.6 | 124.4
251 | 151 | 343.4 | 81.9 | 75.4 | 38.1 | 97.1 | 125
252 | 152 | 344 | 82.2 | 75.7 | 38.3 | 97.5 | 125.7
253 | 153 | 344.7 | 82.5 | 75.9 | 38.5 | 98 | 126.3
254 | 154 | 345.4 | 82.8 | 76.2 | 38.7 | 98.5 | 126.9
255 | 155 | 346.2 | 83.2 | 76.4 | 38.9 | 98.9 | 127.5
256 | 156 | 346.8 | 83.5 | 76.7 | 39.1 | 99.4 | 128.1
257 | 157 | 347.4 | 83.8 | 77 | 39.2 | 99.8 | 128.7
258 | 158 | 348.1 | 84.1 | 77.3 | 39.4 | 100.3 | 129.2
259 | 159 | 348.7 | 84.4 | 77.5 | 39.6 | 100.8 | 129.8
260 | 160 | 349.4 | 84.8 | 77.8 | 39.8 | 101.3 | 130.5
261 | 161 | 349.9 | 85.1 | 78.1 | 40 | 101.7 | 131
262 | 162 | 350.4 | 85.4 | 78.4 | 40.2 | 102.2 | 131.5
263 | 163 | 350.7 | 85.8 | 78.7 | 40.3 | 102.7 | 132
264 | 164 | 351.1 | 86.1 | 79 | 40.5 | 103.2 | 132.5
265 | 165 | 351.5 | 86.4 | 79.2 | 40.7 | 103.6 | 133.1
266 | 166 | 352 | 86.8 | 79.5 | 40.9 | 104.1 | 133.7
267 | 167 | 352.5 | 87.1 | 79.8 | 41.1 | 104.6 | 134.3
268 | 168 | 352.8 | 87.5 | 80.1 | 41.3 | 105.1 | 134.9
269 | 169 | 353.1 | 87.8 | 80.4 | 41.4 | 105.6 | 135.4
270 | 170 | 353.3 | 88.2 | 80.7 | 41.6 | 106.1 | 136.1
271 | 171 | 353.4 | 88.5 | 81 | 41.8 | 106.6 | 136.7
272 | 172 | 353.6 | 88.8 | 81.2 | 42 | 107 | 137.3
273 | 173 | 353.7 | 89.2 | 81.5 | 42.2 | 107.5 | 137.9
274 | 174 | 353.8 | 89.5 | 81.8 | 42.4 | 108 | 138.5
275 | 175 | 353.9 | 89.9 | 82.1 | 42.6 | 108.5 | 139.1
276 | 176 | 353.8 | 90.2 | 82.4 | 42.8 | 109 | 139.7
277 | 177 | 353.8 | 90.6 | 82.7 | 42.9 | 109.5 | 140.3
278 | 178 | 353.9 | 90.9 | 83 | 43.1 | 110 | 140.9
279 | 179 | 353.9 | 91.3 | 83.2 | 43.3 | 110.4 | 141.4
280 | 180 | 353.8 | 91.6 | 83.5 | 43.5 | 110.9 | 141.9
281 | 181 | 353.7 | 92 | 83.8 | 43.7 | 111.4 | 142.5
282 | 182 | 353.5 | 92.3 | 84.1 | 43.9 | 111.9 | 143
283 | 183 | 353.5 | 92.6 | 84.4 | 44.1 | 112.4 | 143.5
284 | 184 | 353.4 | 93 | 84.7 | 44.3 | 112.9 | 144.1
285 | 185 | 353.4 | 93.3 | 85 | 44.4 | 113.4 | 144.6
286 | 186 | 353.4 | 93.7 | 85.2 | 44.6 | 113.9 | 145.2
287 | 187 | 353.2 | 94 | 85.5 | 44.8 | 114.4 | 145.7
288 | 188 | 353.1 | 94.3 | 85.8 | 45 | 114.8 | 146.2
289 | 189 | 353.2 | 94.6 | 86.1 | 45.2 | 115.3 | 146.7
290 | 190 | 353.2 | 95 | 86.3 | 45.4 | 115.8 | 147.3
291 | 191 | 353.4 | 95.3 | 86.6 | 45.6 | 116.3 | 147.8
292 | 192 | 353.4 | 95.6 | 86.9 | 45.7 | 116.8 | 148.3
293 | 193 | 353.4 | 95.9 | 87.2 | 45.9 | 117.3 | 148.8
294 | 194 | 353.5 | 96.2 | 87.4 | 46.1 | 117.8 | 149.3
295 | 195 | 353.4 | 96.5 | 87.7 | 46.3 | 118.3 | 149.8
296 | 196 | 353.4 | 96.8 | 88 | 46.5 | 118.8 | 150.3
297 | 197 | 353.3 | 97.1 | 88.2 | 46.7 | 119.3 | 150.9
298 | 198 | 353.2 | 97.4 | 88.5 | 46.9 | 119.8 | 151.4
299 | 199 | 353.1 | 97.7 | 88.7 | 47.1 | 120.3 | 151.9
300 | 200 | 353.1 | 98 | 89 | 47.3 | 120.8 | 152.4
301 | 201 | 353 | 98.3 | 89.3 | 47.4 | 121.3 | 152.9
302 | 202 | 352.8 | 98.6 | 89.5 | 47.6 | 121.7 | 153.4
303 | 203 | 352.7 | 98.9 | 89.8 | 47.8 | 122.2 | 153.8
304 | 204 | 352.7 | 99.2 | 90 | 48 | 122.7 | 154.3
305 | 205 | 352.6 | 99.5 | 90.3 | 48.2 | 123.2 | 154.8
306 | 206 | 352.5 | 99.8 | 90.5 | 48.4 | 123.6 | 155.3
307 | 207 | 352.3 | 100.1 | 90.8 | 48.6 | 124.1 | 155.7
308 | 208 | 352.1 | 100.4 | 91 | 48.7 | 124.5 | 156.1
309 | 209 | 352 | 100.7 | 91.3 | 48.9 | 125 | 156.6
310 | 210 | 352 | 101 | 91.5 | 49.1 | 125.5 | 157
311 | 211 | 351.8 | 101.2 | 91.8 | 49.3 | 126 | 157.5
312 | 212 | 351.6 | 101.5 | 92 | 49.5 | 126.4 | 157.9
313 | 213 | 351.5 | 101.8 | 92.3 | 49.7 | 126.9 | 158.4
314 | 214 | 351.6 | 102.1 | 92.5 | 49.9 | 127.3 | 158.9
315 | 215 | 351.6 | 102.4 | 92.8 | 50.1 | 127.8 | 159.3
316 | 216 | 351.5 | 102.6 | 93 | 50.3 | 128.3 | 159.8
317 | 217 | 351.5 | 102.9 | 93.2 | 50.4 | 128.7 | 160.2
318 | 218 | 351.7 | 103.2 | 93.5 | 50.6 | 129.1 | 160.6
319 | 219 | 351.8 | 103.4 | 93.7 | 50.8 | 129.6 | 161
320 | 220 | 351.8 | 103.7 | 93.9 | 51 | 130 | 161.5
321 | 221 | 351.9 | 103.9 | 94.2 | 51.2 | 130.4 | 161.9
322 | 222 | 351.9 | 104.2 | 94.4 | 51.4 | 130.9 | 162.3
323 | 223 | 352 | 104.5 | 94.6 | 51.6 | 131.3 | 162.8
324 | 224 | 352 | 104.8 | 94.9 | 51.8 | 131.7 | 163.2
325 | 225 | 352 | 105 | 95.1 | 51.9 | 132.1 | 163.6
326 | 226 | 352.1 | 105.3 | 95.3 | 52.1 | 132.5 | 164
327 | 227 | 352.1 | 105.6 | 95.6 | 52.3 | 132.9 | 164.4
328 | 228 | 351.9 | 105.8 | 95.8 | 52.5 | 133.3 | 164.9
329 | 229 | 351.9 | 106.1 | 96 | 52.7 | 133.7 | 165.3
330 | 230 | 352 | 106.4 | 96.3 | 52.9 | 134.1 | 165.7
331 | 231 | 352.1 | 106.7 | 96.5 | 53.1 | 134.5 | 166.2
332 | 232 | 352.1 | 106.9 | 96.7 | 53.3 | 134.9 | 166.5
333 | 233 | 352.1 | 107.2 | 97 | 53.5 | 135.3 | 166.9
334 | 234 | 352.2 | 107.5 | 97.2 | 53.6 | 135.7 | 167.3
335 | 235 | 352.3 | 107.7 | 97.4 | 53.8 | 136.1 | 167.7
336 | 236 | 352.3 | 108 | 97.7 | 54 | 136.4 | 168.2
337 | 237 | 352.3 | 108.3 | 97.9 | 54.2 | 136.8 | 168.6
338 | 238 | 352.5 | 108.5 | 98.1 | 54.4 | 137.2 | 169
339 | 239 | 352.5 | 108.8 | 98.4 | 54.6 | 137.6 | 169.4
340 | 240 | 352.5 | 109.1 | 98.6 | 54.8 | 137.9 | 169.8
341 | 241 | 352.5 | 109.4 | 98.8 | 54.9 | 138.3 | 170.2
342 | 242 | 352.4 | 109.6 | 99.1 | 55.1 | 138.6 | 170.5
343 | 243 | 352.3 | 109.9 | 99.3 | 55.3 | 139 | 170.9
344 | 244 | 352.4 | 110.2 | 99.5 | 55.5 | 139.3 | 171.3
345 | 245 | 352.4 | 110.5 | 99.7 | 55.7 | 139.7 | 171.7
346 | 246 | 352.5 | 110.7 | 100 | 55.9 | 140 | 172.1
347 | 247 | 352.5 | 111 | 100.2 | 56 | 140.4 | 172.5
348 | 248 | 352.5 | 111.3 | 100.4 | 56.2 | 140.7 | 172.9
349 | 249 | 352.5 | 111.6 | 100.6 | 56.4 | 141.1 | 173.2
350 | 250 | 352.5 | 111.8 | 100.8 | 56.6 | 141.4 | 173.6
351 | 251 | 352.5 | 112.1 | 101.1 | 56.8 | 141.8 | 174
352 | 252 | 352.6 | 112.4 | 101.3 | 57 | 142.1 | 174.3
353 | 253 | 352.6 | 112.6 | 101.5 | 57.1 | 142.5 | 174.7
354 | 254 | 352.7 | 112.9 | 101.7 | 57.3 | 142.9 | 175.1
355 | 255 | 352.7 | 113.2 | 101.9 | 57.5 | 143.3 | 175.5
356 | 256 | 352.8 | 113.4 | 102.1 | 57.7 | 143.6 | 175.8
357 | 257 | 352.8 | 113.7 | 102.4 | 57.9 | 144 | 176.2
358 | 258 | 352.9 | 113.9 | 102.6 | 58 | 144.4 | 176.6
359 | 259 | 352.8 | 114.2 | 102.8 | 58.2 | 144.7 | 176.9
360 | 260 | 352.8 | 114.4 | 103 | 58.4 | 145.1 | 177.3
361 | 261 | 352.7 | 114.7 | 103.2 | 58.6 | 145.4 | 177.7
362 | 262 | 352.7 | 114.9 | 103.4 | 58.8 | 145.8 | 178
363 | 263 | 352.7 | 115.2 | 103.6 | 59 | 146.1 | 178.3
364 | 264 | 352.7 | 115.4 | 103.9 | 59.1 | 146.5 | 178.7
365 | 265 | 352.7 | 115.7 | 104.1 | 59.3 | 146.8 | 179
366 | 266 | 352.7 | 115.9 | 104.3 | 59.5 | 147.1 | 179.4
367 | 267 | 352.6 | 116.2 | 104.5 | 59.7 | 147.5 | 179.7
368 | 268 | 352.5 | 116.4 | 104.7 | 59.8 | 147.8 | 180
369 | 269 | 352.5 | 116.6 | 104.9 | 60 | 148.1 | 180.3
370 | 270 | 352.5 | 116.9 | 105.1 | 60.2 | 148.4 | 180.7
371 | 271 | 352.5 | 117.1 | 105.4 | 60.4 | 148.7 | 181
372 | 272 | 352.5 | 117.4 | 105.6 | 60.6 | 149.1 | 181.4
373 | 273 | 352.5 | 117.6 | 105.8 | 60.7 | 149.4 | 181.7
374 | 274 | 352.5 | 117.8 | 106 | 60.9 | 149.7 | 182
375 | 275 | 352.6 | 118.1 | 106.2 | 61.1 | 149.9 | 182.4
376 | 276 | 352.6 | 118.3 | 106.4 | 61.3 | 150.3 | 182.7
377 | 277 | 352.5 | 118.6 | 106.6 | 61.5 | 150.5 | 183
378 | 278 | 352.4 | 118.8 | 106.9 | 61.6 | 150.8 | 183.3
379 | 279 | 352.4 | 119 | 107.1 | 61.8 | 151.1 | 183.7
380 | 280 | 352.4 | 119.3 | 107.3 | 62 | 151.4 | 184
381 | 281 | 352.5 | 119.5 | 107.5 | 62.2 | 151.7 | 184.3
382 | 282 | 352.5 | 119.8 | 107.7 | 62.3 | 152 | 184.6
383 | 283 | 352.5 | 120 | 107.9 | 62.5 | 152.3 | 184.9
384 | 284 | 352.4 | 120.3 | 108.1 | 62.7 | 152.6 | 185.2
385 | 285 | 352.5 | 120.5 | 108.3 | 62.9 | 152.8 | 185.5
386 | 286 | 352.5 | 120.8 | 108.5 | 63 | 153.1 | 185.9
387 | 287 | 352.5 | 121 | 108.7 | 63.2 | 153.4 | 186.2
388 | 288 | 352.5 | 121.3 | 109 | 63.4 | 153.6 | 186.4
389 | 289 | 352.5 | 121.5 | 109.2 | 63.6 | 153.8 | 186.7
390 | 290 | 352.5 | 121.7 | 109.4 | 63.7 | 154.1 | 187
391 | 291 | 352.5 | 122 | 109.6 | 63.9 | 154.3 | 187.3
392 | 292 | 352.4 | 122.2 | 109.8 | 64.1 | 154.6 | 187.6
393 | 293 | 352.2 | 122.4 | 110 | 64.3 | 154.9 | 187.9
394 | 294 | 352.1 | 122.7 | 110.2 | 64.4 | 155.1 | 188.2
395 | 295 | 352 | 122.9 | 110.4 | 64.6 | 155.4 | 188.5
396 | 296 | 352 | 123.1 | 110.6 | 64.8 | 155.6 | 188.8
397 | 297 | 352 | 123.3 | 110.8 | 65 | 155.9 | 189
398 | 298 | 352 | 123.6 | 111 | 65.1 | 156.1 | 189.3
399 | 299 | 352 | 123.8 | 111.2 | 65.3 | 156.4 | 189.6
400 | 300 | 352.1 | 124 | 111.4 | 65.5 | 156.6 | 189.9
401 | 301 | 352.2 | 124.2 | 111.6 | 65.7 | 156.9 | 190.2
402 | 302 | 352.3 | 124.4 | 111.8 | 65.9 | 157.1 | 190.5
403 | 303 | 352.3 | 124.6 | 112 | 66 | 157.4 | 190.8
404 | 304 | 352.3 | 124.8 | 112.2 | 66.2 | 157.6 | 191.1
405 | 305 | 352.3 | 125 | 112.4 | 66.4 | 157.8 | 191.4
406 | 306 | 352.4 | 125.2 | 112.6 | 66.6 | 158.1 | 191.6
407 | 307 | 352.4 | 125.4 | 112.7 | 66.8 | 158.3 | 191.9
408 | 308 | 352.3 | 125.6 | 112.9 | 66.9 | 158.5 | 192.2
409 | 309 | 352.2 | 125.8 | 113.1 | 67.1 | 158.7 | 192.4
410 | 310 | 352.1 | 126 | 113.3 | 67.3 | 158.9 | 192.7
411 | 311 | 352.1 | 126.2 | 113.5 | 67.4 | 159.1 | 193
412 | 312 | 351.8 | 126.4 | 113.7 | 67.6 | 159.3 | 193.2
413 | 313 | 351.8 | 126.6 | 113.9 | 67.8 | 159.5 | 193.5
414 | 314 | 351.9 | 126.8 | 114.1 | 68 | 159.7 | 193.7
415 | 315 | 351.8 | 127 | 114.3 | 68.1 | 159.9 | 193.9
416 | 316 | 351.8 | 127.2 | 114.5 | 68.3 | 160.1 | 194.2
417 | 317 | 351.8 | 127.4 | 114.7 | 68.5 | 160.3 | 194.5
418 | 318 | 351.8 | 127.6 | 114.9 | 68.7 | 160.5 | 194.7
419 | 319 | 351.7 | 127.8 | 115.1 | 68.8 | 160.7 | 195
420 | 320 | 351.6 | 128 | 115.2 | 69 | 160.9 | 195.2
421 | 321 | 351.5 | 128.2 | 115.4 | 69.2 | 161.1 | 195.5
422 | 322 | 351.5 | 128.5 | 115.6 | 69.4 | 161.3 | 195.8
423 | 323 | 351.5 | 128.7 | 115.8 | 69.5 | 161.4 | 196
424 | 324 | 351.6 | 128.9 | 116 | 69.7 | 161.6 | 196.3
425 | 325 | 351.6 | 129.1 | 116.2 | 69.9 | 161.8 | 196.5
426 | 326 | 351.7 | 129.3 | 116.3 | 70.1 | 162 | 196.7
427 | 327 | 351.8 | 129.4 | 116.5 | 70.2 | 162.2 | 196.9
428 | 328 | 351.7 | 129.6 | 116.7 | 70.4 | 162.3 | 197.1
429 | 329 | 351.6 | 129.8 | 116.9 | 70.6 | 162.5 | 197.3
430 | 330 | 351.6 | 130 | 117.1 | 70.8 | 162.7 | 197.6
431 | 331 | 351.5 | 130.2 | 117.3 | 70.9 | 162.9 | 197.9
432 | 332 | 351.6 | 130.4 | 117.4 | 71.1 | 163.1 | 198.1
433 | 333 | 351.6 | 130.6 | 117.6 | 71.3 | 163.3 | 198.3
434 | 334 | 351.7 | 130.8 | 117.8 | 71.5 | 163.5 | 198.5
435 | 335 | 351.7 | 131 | 118 | 71.6 | 163.7 | 198.7
436 | 336 | 351.7 | 131.2 | 118.2 | 71.8 | 163.9 | 199
437 | 337 | 351.8 | 131.3 | 118.4 | 72 | 164.2 | 199.2
438 | 338 | 351.9 | 131.5 | 118.5 | 72.2 | 164.4 | 199.4
439 | 339 | 351.9 | 131.7 | 118.7 | 72.3 | 164.6 | 199.7
440 | 340 | 352 | 131.9 | 118.9 | 72.5 | 164.8 | 199.9
441 | 341 | 352.1 | 132.1 | 119.1 | 72.7 | 165 | 200.1
442 | 342 | 352.2 | 132.3 | 119.3 | 72.9 | 165.2 | 200.4
443 | 343 | 352.2 | 132.4 | 119.5 | 73 | 165.4 | 200.6
444 | 344 | 352.3 | 132.6 | 119.7 | 73.2 | 165.6 | 200.8
445 | 345 | 352.3 | 132.8 | 119.8 | 73.4 | 165.8 | 201
446 | 346 | 352.2 | 133 | 120 | 73.6 | 166 | 201.3
447 | 347 | 352.3 | 133.2 | 120.2 | 73.7 | 166.2 | 201.5
448 | 348 | 352.3 | 133.3 | 120.4 | 73.9 | 166.4 | 201.7
449 | 349 | 352.4 | 133.5 | 120.6 | 74.1 | 166.6 | 202
450 | 350 | 352.5 | 133.7 | 120.8 | 74.2 | 166.8 | 202.2
451 | 351 | 352.7 | 133.9 | 121 | 74.4 | 167 | 202.4
452 | 352 | 352.7 | 134.1 | 121.1 | 74.6 | 167.2 | 202.6
453 | 353 | 352.7 | 134.2 | 121.3 | 74.7 | 167.4 | 202.8
454 | 354 | 352.7 | 134.4 | 121.5 | 74.9 | 167.6 | 203
455 | 355 | 352.7 | 134.6 | 121.7 | 75.1 | 167.8 | 203.3
456 | 356 | 352.6 | 134.7 | 121.9 | 75.3 | 168 | 203.5
457 | 357 | 352.6 | 134.9 | 122 | 75.4 | 168.2 | 203.7
458 | 358 | 352.6 | 135.1 | 122.2 | 75.6 | 168.5 | 203.9
459 | 359 | 352.6 | 135.2 | 122.4 | 75.8 | 168.7 | 204.1
460 | 360 | 352.8 | 135.4 | 122.6 | 75.9 | 168.9 | 204.3
461 | 361 | 352.9 | 135.6 | 122.8 | 76.1 | 169.1 | 204.5
462 | 362 | 353.1 | 135.7 | 122.9 | 76.3 | 169.3 | 204.7
463 | 363 | 353 | 135.9 | 123.1 | 76.4 | 169.5 | 204.9
464 | 364 | 353 | 136 | 123.3 | 76.6 | 169.7 | 205.1
465 | 365 | 352.8 | 136.2 | 123.5 | 76.8 | 169.9 | 205.3
466 | 366 | 352.8 | 136.4 | 123.6 | 76.9 | 170.1 | 205.5
467 | 367 | 352.7 | 136.5 | 123.8 | 77.1 | 170.3 | 205.7
468 | 368 | 352.6 | 136.7 | 124 | 77.2 | 170.5 | 205.9
469 | 369 | 352.4 | 136.9 | 124.1 | 77.4 | 170.7 | 206
470 | 370 | 352.2 | 137 | 124.3 | 77.6 | 170.8 | 206.2
471 | 371 | 352.1 | 137.2 | 124.5 | 77.7 | 171 | 206.4
472 | 372 | 352 | 137.4 | 124.7 | 77.9 | 171.2 | 206.6
473 | 373 | 352.1 | 137.5 | 124.8 | 78.1 | 171.4 | 206.7
474 | 374 | 352.2 | 137.7 | 125 | 78.2 | 171.6 | 206.9
475 | 375 | 352.2 | 137.9 | 125.2 | 78.4 | 171.8 | 207.1
476 | 376 | 352.2 | 138 | 125.4 | 78.5 | 172 | 207.2
477 | 377 | 352.1 | 138.2 | 125.5 | 78.7 | 172.2 | 207.4
478 | 378 | 352.1 | 138.4 | 125.7 | 78.9 | 172.4 | 207.6
479 | 379 | 352 | 138.5 | 125.9 | 79 | 172.6 | 207.7
480 | 380 | 352 | 138.7 | 126 | 79.2 | 172.9 | 207.9
481 | 381 | 352 | 138.9 | 126.2 | 79.4 | 173.1 | 208.1
482 | 382 | 351.9 | 139 | 126.4 | 79.5 | 173.3 | 208.3
483 | 383 | 351.9 | 139.2 | 126.6 | 79.7 | 173.5 | 208.4
484 | 384 | 351.7 | 139.3 | 126.7 | 79.8 | 173.8 | 208.6
485 | 385 | 351.6 | 139.5 | 126.9 | 80 | 174 | 208.7
486 | 386 | 351.6 | 139.6 | 127.1 | 80.2 | 174.2 | 208.9
487 | 387 | 351.5 | 139.8 | 127.2 | 80.3 | 174.5 | 209
488 | 388 | 351.5 | 139.9 | 127.4 | 80.5 | 174.7 | 209.2
489 | 389 | 351.4 | 140.1 | 127.6 | 80.6 | 175 | 209.3
490 | 390 | 351.5 | 140.2 | 127.7 | 80.8 | 175.2 | 209.4
491 | 391 | 351.5 | 140.4 | 127.9 | 81 | 175.5 | 209.6
492 | 392 | 351.4 | 140.5 | 128.1 | 81.1 | 175.7 | 209.8
493 | 393 | 351.4 | 140.6 | 128.2 | 81.3 | 175.9 | 210
494 | 394 | 351.3 | 140.8 | 128.4 | 81.5 | 176.2 | 210.1
495 | 395 | 351.2 | 140.9 | 128.5 | 81.6 | 176.4 | 210.3
496 | 396 | 351.1 | 141 | 128.7 | 81.8 | 176.6 | 210.4
497 | 397 | 350.9 | 141.2 | 128.8 | 81.9 | 176.8 | 210.6
498 | 398 | 350.9 | 141.3 | 129 | 82.1 | 177 | 210.7
499 | 399 | 350.9 | 141.4 | 129.1 | 82.3 | 177.2 | 210.9
500 | 400 | 350.9 | 141.6 | 129.3 | 82.4 | 177.5 | 211
501 | 401 | 350.8 | 141.7 | 129.4 | 82.6 | 177.7 | 211.1
502 | 402 | 350.7 | 141.9 | 129.6 | 82.8 | 178 | 211.3
503 | 403 | 350.6 | 142 | 129.7 | 82.9 | 178.2 | 211.4
504 | 404 | 350.6 | 142.2 | 129.9 | 83.1 | 178.4 | 211.5
505 | 405 | 350.6 | 142.4 | 130 | 83.2 | 178.6 | 211.7
506 | 406 | 350.6 | 142.5 | 130.2 | 83.4 | 178.8 | 211.9
507 | 407 | 350.7 | 142.7 | 130.3 | 83.6 | 179 | 212
508 | 408 | 350.6 | 142.8 | 130.5 | 83.7 | 179.2 | 212.1
509 | 409 | 350.6 | 143 | 130.6 | 83.9 | 179.4 | 212.2
510 | 410 | 350.7 | 143.2 | 130.8 | 84 | 179.6 | 212.3
511 | 411 | 350.8 | 143.4 | 130.9 | 84.2 | 179.8 | 212.5
512 | 412 | 350.8 | 143.5 | 131.1 | 84.4 | 180 | 212.6
513 | 413 | 350.8 | 143.7 | 131.2 | 84.5 | 180.2 | 212.8
514 | 414 | 350.8 | 143.9 | 131.4 | 84.7 | 180.4 | 212.9
515 | 415 | 350.7 | 144.1 | 131.5 | 84.8 | 180.6 | 213
516 | 416 | 350.6 | 144.2 | 131.6 | 85 | 180.8 | 213.2
517 | 417 | 350.5 | 144.4 | 131.8 | 85.2 | 181 | 213.3
518 | 418 | 350.6 | 144.6 | 131.9 | 85.3 | 181.1 | 213.4
519 | 419 | 350.7 | 144.8 | 132.1 | 85.5 | 181.3 | 213.5
520 | 420 | 350.6 | 145 | 132.3 | 85.6 | 181.6 | 213.6
521 | 421 | 350.6 | 145.1 | 132.4 | 85.8 | 181.7 | 213.7
522 | 422 | 350.6 | 145.3 | 132.5 | 86 | 181.9 | 213.8
523 | 423 | 350.7 | 145.5 | 132.7 | 86.1 | 182.1 | 213.9
524 | 424 | 350.8 | 145.7 | 132.8 | 86.3 | 182.3 | 214.1
525 | 425 | 350.6 | 145.9 | 132.9 | 86.4 | 182.5 | 214.2
526 | 426 | 350.6 | 146.1 | 133.1 | 86.6 | 182.7 | 214.4
527 | 427 | 350.5 | 146.3 | 133.2 | 86.8 | 182.9 | 214.5
528 | 428 | 350.5 | 146.5 | 133.3 | 86.9 | 183.1 | 214.6
529 | 429 | 350.4 | 146.7 | 133.5 | 87.1 | 183.2 | 214.7
530 | 430 | 350.3 | 146.9 | 133.6 | 87.2 | 183.4 | 214.8
531 | 431 | 350.3 | 147.1 | 133.7 | 87.4 | 183.5 | 214.9
532 | 432 | 350.2 | 147.3 | 133.9 | 87.6 | 183.6 | 215
533 | 433 | 350 | 147.5 | 134 | 87.7 | 183.8 | 215.1
534 | 434 | 349.9 | 147.6 | 134.1 | 87.9 | 183.9 | 215.2
535 | 435 | 349.8 | 147.8 | 134.3 | 88 | 184 | 215.2
536 | 436 | 349.7 | 148 | 134.4 | 88.2 | 184.1 | 215.3
537 | 437 | 349.7 | 148.2 | 134.5 | 88.4 | 184.2 | 215.4
538 | 438 | 349.6 | 148.4 | 134.6 | 88.5 | 184.3 | 215.5
539 | 439 | 349.5 | 148.6 | 134.8 | 88.7 | 184.4 | 215.6
540 | 440 | 349.4 | 148.8 | 134.9 | 88.8 | 184.5 | 215.7
541 | 441 | 349.4 | 149 | 135 | 89 | 184.6 | 215.8
542 | 442 | 349.5 | 149.2 | 135.1 | 89.1 | 184.8 | 215.9
543 | 443 | 349.5 | 149.4 | 135.3 | 89.3 | 184.9 | 216
544 | 444 | 349.3 | 149.5 | 135.4 | 89.5 | 185.1 | 216.1
545 | 445 | 349.2 | 149.7 | 135.5 | 89.6 | 185.2 | 216.2
546 | 446 | 349.3 | 149.9 | 135.6 | 89.8 | 185.4 | 216.3
547 | 447 | 349.3 | 150.1 | 135.7 | 89.9 | 185.5 | 216.4
548 | 448 | 349.2 | 150.3 | 135.8 | 90.1 | 185.6 | 216.4
549 | 449 | 349.2 | 150.5 | 135.9 | 90.2 | 185.8 | 216.6
550 | 450 | 349.3 | 150.6 | 136 | 90.4 | 186 | 216.7
551 | 451 | 349.3 | 150.8 | 136.2 | 90.6 | 186.1 | 216.8
552 | 452 | 349.4 | 151 | 136.3 | 90.7 | 186.2 | 216.9
553 | 453 | 349.4 | 151.2 | 136.4 | 90.9 | 186.4 | 217
554 | 454 | 349.4 | 151.4 | 136.5 | 91 | 186.5 | 217.1
555 | 455 | 349.5 | 151.5 | 136.7 | 91.2 | 186.7 | 217.2
556 | 456 | 349.6 | 151.7 | 136.8 | 91.4 | 186.9 | 217.3
557 | 457 | 349.8 | 151.9 | 136.9 | 91.5 | 187 | 217.4
558 | 458 | 349.8 | 152.1 | 137 | 91.7 | 187.2 | 217.5
559 | 459 | 349.9 | 152.3 | 137.2 | 91.8 | 187.3 | 217.6
560 | 460 | 349.9 | 152.5 | 137.3 | 92 | 187.5 | 217.6
561 | 461 | 350.1 | 152.6 | 137.4 | 92.1 | 187.7 | 217.7
562 | 462 | 350.2 | 152.8 | 137.5 | 92.3 | 187.8 | 217.8
563 | 463 | 350.2 | 153 | 137.7 | 92.5 | 188 | 217.9
564 | 464 | 350.2 | 153.2 | 137.8 | 92.6 | 188.2 | 218
565 | 465 | 350.1 | 153.4 | 137.9 | 92.8 | 188.4 | 218.1
566 | 466 | 350.2 | 153.5 | 138.1 | 92.9 | 188.6 | 218.2
567 | 467 | 350.2 | 153.7 | 138.2 | 93.1 | 188.8 | 218.3
568 | 468 | 350.3 | 153.9 | 138.3 | 93.2 | 189 | 218.4
569 | 469 | 350.3 | 154 | 138.5 | 93.4 | 189.2 | 218.5
570 | 470 | 350.2 | 154.2 | 138.6 | 93.5 | 189.4 | 218.6
571 | 471 | 350.2 | 154.4 | 138.8 | 93.7 | 189.5 | 218.7
572 | 472 | 350.1 | 154.5 | 138.9 | 93.8 | 189.7 | 218.8
573 | 473 | 350.2 | 154.7 | 139 | 94 | 189.9 | 218.9
574 | 474 | 350.3 | 154.9 | 139.2 | 94.2 | 190.1 | 219
575 | 475 | 350.2 | 155 | 139.3 | 94.3 | 190.3 | 219.1
576 | 476 | 350.1 | 155.2 | 139.5 | 94.5 | 190.5 | 219.2
577 | 477 | 350.2 | 155.4 | 139.6 | 94.6 | 190.6 | 219.3
578 | 478 | 350.3 | 155.6 | 139.8 | 94.8 | 190.8 | 219.4
579 | 479 | 350.2 | 155.7 | 139.9 | 94.9 | 191 | 219.5
580 | 480 | 350 | 155.9 | 140.1 | 95.1 | 191.1 | 219.6
581 | 481 | 349.9 | 156.1 | 140.2 | 95.2 | 191.3 | 219.7
582 | 482 | 350.1 | 156.2 | 140.4 | 95.4 | 191.4 | 219.8
583 | 483 | 350.2 | 156.4 | 140.5 | 95.6 | 191.5 | 219.9
584 | 484 | 350.2 | 156.6 | 140.7 | 95.7 | 191.7 | 220
585 | 485 | 350.2 | 156.8 | 140.8 | 95.9 | 191.8 | 220.1
586 | 486 | 350.2 | 156.9 | 141 | 96 | 192 | 220.2
587 | 487 | 350.2 | 157.1 | 141.1 | 96.2 | 192.1 | 220.3
588 | 488 | 350.2 | 157.3 | 141.3 | 96.3 | 192.3 | 220.3
589 | 489 | 350.2 | 157.5 | 141.5 | 96.5 | 192.4 | 220.5
590 | 490 | 350.1 | 157.6 | 141.6 | 96.6 | 192.5 | 220.6
591 | 491 | 350.1 | 157.8 | 141.8 | 96.8 | 192.7 | 220.6
592 | 492 | 350.1 | 158 | 141.9 | 96.9 | 192.8 | 220.7
593 | 493 | 350.1 | 158.2 | 142.1 | 97.1 | 193 | 220.9
594 | 494 | 350.1 | 158.3 | 142.3 | 97.2 | 193.1 | 220.9
595 | 495 | 350.1 | 158.5 | 142.4 | 97.4 | 193.2 | 221
596 | 496 | 350.1 | 158.7 | 142.6 | 97.5 | 193.4 | 221.1
597 | 497 | 350.1 | 158.9 | 142.8 | 97.7 | 193.5 | 221.2
598 | 498 | 350.2 | 159.1 | 142.9 | 97.8 | 193.6 | 221.3
599 | 499 | 350.1 | 159.3 | 143.1 | 98 | 193.8 | 221.4
600 | 500 | 350 | 159.4 | 143.2 | 98.1 | 193.9 | 221.5
601 | 501 | 350 | 159.6 | 143.4 | 98.3 | 194.1 | 221.5
602 | 502 | 350 | 159.8 | 143.6 | 98.4 | 194.2 | 221.6
603 | 503 | 350 | 160 | 143.7 | 98.6 | 194.4 | 221.7
604 | 504 | 350 | 160.2 | 143.9 | 98.7 | 194.6 | 221.8
605 | 505 | 350.1 | 160.3 | 144.1 | 98.9 | 194.7 | 221.9
606 | 506 | 350.3 | 160.5 | 144.2 | 99 | 194.8 | 222
607 | 507 | 350.3 | 160.7 | 144.4 | 99.2 | 195 | 222.1
608 | 508 | 350.2 | 160.9 | 144.6 | 99.3 | 195.1 | 222.1
609 | 509 | 350.1 | 161 | 144.7 | 99.5 | 195.3 | 222.2
610 | 510 | 350.1 | 161.2 | 144.9 | 99.6 | 195.5 | 222.3
611 | 511 | 350.1 | 161.4 | 145.1 | 99.8 | 195.7 | 222.4
612 | 512 | 350.1 | 161.5 | 145.2 | 99.9 | 195.9 | 222.4
613 | 513 | 350.1 | 161.7 | 145.4 | 100.1 | 196 | 222.5
614 | 514 | 350.1 | 161.8 | 145.5 | 100.2 | 196.2 | 222.6
615 | 515 | 350.1 | 162 | 145.7 | 100.4 | 196.4 | 222.7
616 | 516 | 350.2 | 162.2 | 145.9 | 100.5 | 196.6 | 222.7
617 | 517 | 350.2 | 162.3 | 146 | 100.7 | 196.8 | 222.8
618 | 518 | 350.2 | 162.5 | 146.2 | 100.8 | 196.9 | 222.8
619 | 519 | 350.2 | 162.6 | 146.3 | 100.9 | 197.1 | 222.9
620 | 520 | 350.2 | 162.8 | 146.5 | 101.1 | 197.3 | 223
621 | 521 | 350.2 | 163 | 146.6 | 101.2 | 197.4 | 223.1
622 | 522 | 350.4 | 163.1 | 146.8 | 101.4 | 197.5 | 223.1
623 | 523 | 350.5 | 163.3 | 147 | 101.5 | 197.6 | 223.2
624 | 524 | 350.4 | 163.5 | 147.1 | 101.7 | 197.8 | 223.3
625 | 525 | 350.5 | 163.6 | 147.3 | 101.8 | 197.9 | 223.4
626 | 526 | 350.6 | 163.8 | 147.4 | 102 | 198 | 223.4
627 | 527 | 350.6 | 163.9 | 147.6 | 102.1 | 198.1 | 223.5
628 | 528 | 350.7 | 164.1 | 147.7 | 102.3 | 198.3 | 223.6
629 | 529 | 350.7 | 164.3 | 147.9 | 102.4 | 198.4 | 223.7
630 | 530 | 350.8 | 164.4 | 148.1 | 102.5 | 198.5 | 223.8
631 | 531 | 350.8 | 164.6 | 148.2 | 102.7 | 198.6 | 223.8
632 | 532 | 350.7 | 164.7 | 148.4 | 102.8 | 198.7 | 223.9
633 | 533 | 350.7 | 164.9 | 148.5 | 103 | 198.8 | 224
634 | 534 | 350.6 | 165 | 148.7 | 103.1 | 198.9 | 224.1
635 | 535 | 350.5 | 165.2 | 148.8 | 103.3 | 199 | 224.2
636 | 536 | 350.4 | 165.3 | 149 | 103.4 | 199.1 | 224.3
637 | 537 | 350.4 | 165.5 | 149.2 | 103.6 | 199.2 | 224.3
638 | 538 | 350.3 | 165.6 | 149.3 | 103.7 | 199.3 | 224.4
639 | 539 | 350.3 | 165.8 | 149.5 | 103.9 | 199.4 | 224.4
640 | 540 | 350.2 | 165.9 | 149.6 | 104 | 199.5 | 224.5
641 | 541 | 350.2 | 166.1 | 149.8 | 104.2 | 199.6 | 224.6
642 | 542 | 350.1 | 166.2 | 149.9 | 104.3 | 199.7 | 224.6
643 | 543 | 350 | 166.4 | 150.1 | 104.4 | 199.7 | 224.7
644 | 544 | 350 | 166.5 | 150.2 | 104.6 | 199.8 | 224.8
645 | 545 | 350 | 166.7 | 150.4 | 104.7 | 199.9 | 224.9
646 | 546 | 349.9 | 166.8 | 150.5 | 104.9 | 200 | 224.9
647 | 547 | 349.8 | 167 | 150.7 | 105 | 200.1 | 225
648 | 548 | 349.8 | 167.1 | 150.8 | 105.2 | 200.1 | 225.1
649 | 549 | 349.8 | 167.3 | 151 | 105.3 | 200.2 | 225.1
650 | 550 | 349.7 | 167.4 | 151.1 | 105.4 | 200.3 | 225.2
651 | 551 | 349.6 | 167.6 | 151.3 | 105.6 | 200.5 | 225.2
652 | 552 | 349.6 | 167.8 | 151.4 | 105.7 | 200.6 | 225.3
653 | 553 | 349.5 | 167.9 | 151.6 | 105.9 | 200.7 | 225.3
654 | 554 | 349.4 | 168.1 | 151.7 | 106 | 200.8 | 225.4
655 | 555 | 349.4 | 168.2 | 151.9 | 106.1 | 201 | 225.5
656 | 556 | 349.4 | 168.4 | 152 | 106.3 | 201.1 | 225.5
657 | 557 | 349.3 | 168.6 | 152.2 | 106.4 | 201.3 | 225.5
658 | 558 | 349.3 | 168.7 | 152.4 | 106.6 | 201.4 | 225.6
659 | 559 | 349.3 | 168.9 | 152.5 | 106.7 | 201.6 | 225.6
660 | 560 | 349.3 | 169.1 | 152.7 | 106.8 | 201.7 | 225.7
661 | 561 | 349.3 | 169.2 | 152.8 | 107 | 201.8 | 225.7
662 | 562 | 349.2 | 169.4 | 153 | 107.1 | 202 | 225.7
663 | 563 | 349.1 | 169.5 | 153.1 | 107.2 | 202 | 225.8
664 | 564 | 348.9 | 169.7 | 153.3 | 107.4 | 202.1 | 225.8
665 | 565 | 349 | 169.8 | 153.4 | 107.5 | 202.2 | 225.9
666 | 566 | 349.1 | 169.9 | 153.6 | 107.7 | 202.3 | 225.9
667 | 567 | 349 | 170.1 | 153.8 | 107.8 | 202.4 | 225.9
668 | 568 | 348.9 | 170.2 | 153.9 | 107.9 | 202.5 | 226
669 | 569 | 349 | 170.4 | 154.1 | 108.1 | 202.6 | 226
670 | 570 | 349 | 170.5 | 154.2 | 108.2 | 202.7 | 226.1
671 | 571 | 348.9 | 170.7 | 154.4 | 108.4 | 202.8 | 226.1
672 | 572 | 348.9 | 170.8 | 154.5 | 108.5 | 202.9 | 226.2
673 | 573 | 348.9 | 171 | 154.7 | 108.6 | 203 | 226.2
674 | 574 | 348.9 | 171.1 | 154.9 | 108.8 | 203.1 | 226.3
675 | 575 | 348.9 | 171.2 | 155 | 108.9 | 203.2 | 226.3
676 | 576 | 349 | 171.4 | 155.2 | 109 | 203.3 | 226.4
677 | 577 | 349.1 | 171.5 | 155.3 | 109.2 | 203.4 | 226.4
678 | 578 | 349.2 | 171.7 | 155.5 | 109.3 | 203.5 | 226.5
679 | 579 | 349.3 | 171.8 | 155.6 | 109.4 | 203.6 | 226.5
680 | 580 | 349.3 | 171.9 | 155.8 | 109.6 | 203.7 | 226.5
681 | 581 | 349.4 | 172.1 | 156 | 109.7 | 203.8 | 226.5
682 | 582 | 349.4 | 172.2 | 156.1 | 109.8 | 203.9 | 226.5
683 | 583 | 349.5 | 172.4 | 156.3 | 110 | 204 | 226.6
684 | 584 | 349.8 | 172.5 | 156.4 | 110.1 | 204.2 | 226.6
685 | 585 | 349.9 | 172.6 | 156.6 | 110.2 | 204.3 | 226.7
686 | 586 | 349.9 | 172.8 | 156.8 | 110.4 | 204.4 | 226.8
687 | 587 | 350 | 172.9 | 156.9 | 110.5 | 204.5 | 226.8
688 | 588 | 350.1 | 173.1 | 157.1 | 110.6 | 204.6 | 226.9
689 | 589 | 350.1 | 173.2 | 157.2 | 110.8 | 204.6 | 226.9
690 | 590 | 350 | 173.3 | 157.4 | 110.9 | 204.8 | 226.9
691 | 591 | 349.9 | 173.5 | 157.6 | 111 | 204.9 | 227
692 | 592 | 349.8 | 173.6 | 157.7 | 111.2 | 205 | 227
693 | 593 | 349.7 | 173.8 | 157.9 | 111.3 | 205.2 | 227
694 | 594 | 349.7 | 173.9 | 158 | 111.4 | 205.3 | 227
695 | 595 | 349.6 | 174 | 158.2 | 111.6 | 205.4 | 227.1
696 | 596 | 349.6 | 174.2 | 158.3 | 111.7 | 205.6 | 227.1
697 | 597 | 349.6 | 174.3 | 158.5 | 111.8 | 205.7 | 227.2
698 | 598 | 349.6 | 174.5 | 158.6 | 112 | 205.8 | 227.2
699 | 599 | 349.6 | 174.6 | 158.8 | 112.1 | 206 | 227.2
700 | 600 | 349.5 | 174.8 | 158.9 | 112.2 | 206.2 | 227.3
701 | 601 | 349.3 | 174.9 | 159.1 | 112.3 | 206.3 | 227.3
702 | 602 | 349.2 | 175.1 | 159.3 | 112.5 | 206.5 | 227.3
703 | 603 | 349 | 175.2 | 159.4 | 112.6 | 206.6 | 227.3
704 | 604 | 349 | 175.3 | 159.6 | 112.7 | 206.7 | 227.3
705 | 605 | 349.1 | 175.5 | 159.7 | 112.9 | 206.8 | 227.4
706 | 606 | 349.1 | 175.6 | 159.9 | 113 | 206.9 | 227.4
707 | 607 | 349 | 175.8 | 160 | 113.1 | 207 | 227.4
708 | 608 | 348.9 | 175.9 | 160.2 | 113.2 | 207 | 227.5
709 | 609 | 348.9 | 176 | 160.4 | 113.4 | 207.1 | 227.5
710 | 610 | 348.9 | 176.2 | 160.5 | 113.5 | 207.2 | 227.5
711 | 611 | 348.9 | 176.3 | 160.7 | 113.6 | 207.3 | 227.5
712 | 612 | 348.9 | 176.5 | 160.8 | 113.7 | 207.3 | 227.6
713 | 613 | 348.9 | 176.6 | 161 | 113.9 | 207.3 | 227.6
714 | 614 | 348.9 | 176.7 | 161.2 | 114 | 207.3 | 227.6
715 | 615 | 348.9 | 176.9 | 161.3 | 114.1 | 207.4 | 227.6
716 | 616 | 349 | 177 | 161.5 | 114.2 | 207.4 | 227.7
717 | 617 | 349.2 | 177.1 | 161.6 | 114.4 | 207.5 | 227.7
718 | 618 | 349.2 | 177.3 | 161.8 | 114.5 | 207.5 | 227.8
719 | 619 | 349.2 | 177.4 | 161.9 | 114.6 | 207.6 | 227.8
720 | 620 | 349.3 | 177.6 | 162.1 | 114.7 | 207.6 | 227.8
721 | 621 | 349.4 | 177.7 | 162.3 | 114.9 | 207.7 | 227.8
722 | 622 | 349.5 | 177.8 | 162.4 | 115 | 207.7 | 227.8
723 | 623 | 349.7 | 178 | 162.6 | 115.1 | 207.7 | 227.9
724 | 624 | 349.9 | 178.1 | 162.8 | 115.2 | 207.8 | 227.9
725 | 625 | 349.9 | 178.2 | 162.9 | 115.4 | 207.8 | 228
726 | 626 | 350 | 178.4 | 163.1 | 115.5 | 207.8 | 228
727 | 627 | 350.1 | 178.5 | 163.3 | 115.6 | 207.8 | 228.1
728 | 628 | 350.2 | 178.6 | 163.4 | 115.7 | 207.8 | 228.1
729 | 629 | 350.3 | 178.8 | 163.6 | 115.9 | 207.9 | 228.2
730 | 630 | 350.3 | 178.9 | 163.7 | 116 | 207.9 | 228.3
731 | 631 | 350.4 | 179 | 163.9 | 116.1 | 208 | 228.3
732 | 632 | 350.2 | 179.2 | 164.1 | 116.2 | 208 | 228.3
733 | 633 | 350.2 | 179.3 | 164.2 | 116.4 | 208.1 | 228.4
734 | 634 | 350.2 | 179.4 | 164.4 | 116.5 | 208.2 | 228.4
735 | 635 | 350.1 | 179.6 | 164.6 | 116.6 | 208.3 | 228.5
736 | 636 | 350.1 | 179.7 | 164.7 | 116.8 | 208.5 | 228.5
737 | 637 | 350.1 | 179.8 | 164.9 | 116.9 | 208.6 | 228.6
738 | 638 | 350.1 | 180 | 165.1 | 117 | 208.7 | 228.6
739 | 639 | 350.1 | 180.1 | 165.2 | 117.1 | 208.8 | 228.6
740 | 640 | 349.9 | 180.2 | 165.4 | 117.3 | 208.9 | 228.7
741 | 641 | 349.8 | 180.4 | 165.6 | 117.4 | 209.1 | 228.7
742 | 642 | 349.7 | 180.5 | 165.8 | 117.5 | 209.2 | 228.7
743 | 643 | 349.6 | 180.6 | 165.9 | 117.7 | 209.3 | 228.7
744 | 644 | 349.6 | 180.8 | 166.1 | 117.8 | 209.4 | 228.8
745 | 645 | 349.7 | 180.9 | 166.2 | 117.9 | 209.5 | 228.8
746 | 646 | 349.7 | 181 | 166.4 | 118 | 209.6 | 228.9
747 | 647 | 349.7 | 181.2 | 166.6 | 118.2 | 209.8 | 228.9
748 | 648 | 349.7 | 181.3 | 166.8 | 118.3 | 209.9 | 229
749 | 649 | 349.7 | 181.4 | 166.9 | 118.4 | 210 | 229
750 | 650 | 349.8 | 181.5 | 167.1 | 118.6 | 210.1 | 229.1
751 | 651 | 349.8 | 181.7 | 167.3 | 118.7 | 210.3 | 229.1
752 | 652 | 349.8 | 181.8 | 167.4 | 118.8 | 210.4 | 229.2
753 | 653 | 349.8 | 181.9 | 167.6 | 119 | 210.6 | 229.2
754 | 654 | 349.8 | 182.1 | 167.8 | 119.1 | 210.8 | 229.3
755 | 655 | 349.7 | 182.2 | 168 | 119.2 | 210.9 | 229.3
756 | 656 | 349.8 | 182.3 | 168.1 | 119.4 | 211 | 229.4
757 | 657 | 349.9 | 182.5 | 168.3 | 119.5 | 211.1 | 229.4
758 | 658 | 350 | 182.6 | 168.5 | 119.6 | 211.2 | 229.5
759 | 659 | 350.1 | 182.7 | 168.7 | 119.8 | 211.3 | 229.5
760 | 660 | 350.2 | 182.8 | 168.8 | 119.9 | 211.4 | 229.5
761 | 661 | 350.3 | 183 | 169 | 120 | 211.5 | 229.6
762 | 662 | 350.4 | 183.1 | 169.2 | 120.2 | 211.6 | 229.6
763 | 663 | 350.2 | 183.2 | 169.3 | 120.3 | 211.7 | 229.7
764 | 664 | 350.2 | 183.4 | 169.5 | 120.4 | 211.8 | 229.7
765 | 665 | 350.1 | 183.5 | 169.7 | 120.6 | 211.9 | 229.8
766 | 666 | 350.1 | 183.6 | 169.8 | 120.7 | 212 | 229.8
767 | 667 | 350.1 | 183.7 | 170 | 120.9 | 212.1 | 229.8
768 | 668 | 350.1 | 183.9 | 170.2 | 121 | 212.2 | 229.8
769 | 669 | 350.1 | 184 | 170.3 | 121.1 | 212.2 | 229.9
770 | 670 | 350 | 184.1 | 170.5 | 121.3 | 212.3 | 229.9
771 | 671 | 349.8 | 184.2 | 170.7 | 121.4 | 212.3 | 229.9
772 | 672 | 349.6 | 184.4 | 170.8 | 121.5 | 212.3 | 229.9
773 | 673 | 349.4 | 184.5 | 171 | 121.7 | 212.4 | 229.9
774 | 674 | 349.4 | 184.6 | 171.1 | 121.8 | 212.3 | 230
775 | 675 | 349.3 | 184.7 | 171.3 | 122 | 212.4 | 230
776 | 676 | 349.2 | 184.9 | 171.5 | 122.1 | 212.4 | 230.1
777 | 677 | 349.1 | 185 | 171.6 | 122.3 | 212.5 | 230.1
778 | 678 | 349.1 | 185.1 | 171.8 | 122.4 | 212.6 | 230.1
779 | 679 | 349.1 | 185.2 | 172 | 122.5 | 212.7 | 230.2
780 | 680 | 348.9 | 185.3 | 172.1 | 122.7 | 212.7 | 230.2
781 | 681 | 348.8 | 185.5 | 172.3 | 122.8 | 212.7 | 230.3
782 | 682 | 348.8 | 185.6 | 172.4 | 123 | 212.7 | 230.3
783 | 683 | 348.8 | 185.7 | 172.6 | 123.1 | 212.8 | 230.3
784 | 684 | 348.9 | 185.8 | 172.7 | 123.3 | 212.9 | 230.3
785 | 685 | 348.9 | 185.9 | 172.9 | 123.5 | 212.9 | 230.4
786 | 686 | 348.9 | 186 | 173 | 123.6 | 212.9 | 230.4
787 | 687 | 349 | 186.1 | 173.2 | 123.8 | 212.8 | 230.4
788 | 688 | 349 | 186.2 | 173.4 | 123.9 | 212.9 | 230.4
789 | 689 | 349 | 186.3 | 173.5 | 124.1 | 212.9 | 230.5
790 | 690 | 349 | 186.5 | 173.7 | 124.2 | 212.9 | 230.5
791 | 691 | 349.1 | 186.6 | 173.8 | 124.4 | 212.9 | 230.5
792 | 692 | 349.2 | 186.7 | 173.9 | 124.6 | 213 | 230.5
793 | 693 | 349.3 | 186.8 | 174.1 | 124.7 | 213.1 | 230.5
794 | 694 | 349.4 | 186.9 | 174.3 | 124.9 | 213.3 | 230.5
795 | 695 | 349.5 | 187 | 174.4 | 125 | 213.5 | 230.5
796 | 696 | 349.5 | 187.2 | 174.5 | 125.2 | 213.6 | 230.6
797 | 697 | 349.5 | 187.3 | 174.7 | 125.3 | 213.7 | 230.6
798 | 698 | 349.4 | 187.4 | 174.8 | 125.5 | 213.8 | 230.6
799 | 699 | 349.4 | 187.5 | 175 | 125.6 | 213.8 | 230.7
800 | 700 | 349.5 | 187.6 | 175.1 | 125.8 | 213.8 | 230.7
801 | 701 | 349.5 | 187.7 | 175.2 | 126 | 213.8 | 230.7
802 | 702 | 349.4 | 187.9 | 175.4 | 126.1 | 213.9 | 230.7
803 | 703 | 349.4 | 188 | 175.6 | 126.3 | 214 | 230.7
804 | 704 | 349.3 | 188.1 | 175.7 | 126.4 | 214 | 230.7
805 | 705 | 349.3 | 188.2 | 175.8 | 126.6 | 214 | 230.7
806 | 706 | 349.3 | 188.3 | 176 | 126.7 | 214.1 | 230.8
807 | 707 | 349.3 | 188.4 | 176.1 | 126.9 | 214 | 230.8
808 | 708 | 349.3 | 188.5 | 176.2 | 127 | 214 | 230.8
809 | 709 | 349.2 | 188.7 | 176.3 | 127.2 | 214 | 230.8
810 | 710 | 349.2 | 188.8 | 176.5 | 127.3 | 214.1 | 230.8
811 | 711 | 349.3 | 188.9 | 176.6 | 127.5 | 214 | 230.8
812 | 712 | 349.4 | 189 | 176.7 | 127.6 | 213.8 | 230.8
813 | 713 | 349.4 | 189.1 | 176.9 | 127.8 | 213.8 | 230.8
814 | 714 | 349.3 | 189.2 | 177 | 127.9 | 213.8 | 230.9
815 | 715 | 349.3 | 189.3 | 177.2 | 128.1 | 213.9 | 230.9
816 | 716 | 349.2 | 189.4 | 177.3 | 128.2 | 213.9 | 230.9
817 | 717 | 349.3 | 189.6 | 177.4 | 128.4 | 213.9 | 230.9
818 | 718 | 349.4 | 189.7 | 177.6 | 128.5 | 213.9 | 230.9
819 | 719 | 349.4 | 189.8 | 177.7 | 128.7 | 214 | 231
820 | 720 | 349.4 | 189.9 | 177.9 | 128.8 | 214.1 | 231
821 | 721 | 349.4 | 190 | 178 | 129 | 214.2 | 231.1
822 | 722 | 349.4 | 190.1 | 178.1 | 129.1 | 214.4 | 231.1
823 | 723 | 349.3 | 190.2 | 178.3 | 129.3 | 214.5 | 231.1
824 | 724 | 349.3 | 190.4 | 178.4 | 129.4 | 214.6 | 231.1
825 | 725 | 349.2 | 190.5 | 178.5 | 129.6 | 214.7 | 231.1
826 | 726 | 349.2 | 190.6 | 178.6 | 129.7 | 214.8 | 231.1
827 | 727 | 349.2 | 190.7 | 178.8 | 129.8 | 214.9 | 231.2
828 | 728 | 349.3 | 190.8 | 178.9 | 130 | 214.9 | 231.2
829 | 729 | 349.2 | 191 | 179.1 | 130.1 | 214.8 | 231.3
830 | 730 | 349.2 | 191.1 | 179.2 | 130.3 | 214.7 | 231.3
831 | 731 | 349.4 | 191.2 | 179.3 | 130.4 | 214.6 | 231.4
832 | 732 | 349.5 | 191.3 | 179.5 | 130.6 | 214.7 | 231.4
833 | 733 | 349.5 | 191.4 | 179.6 | 130.7 | 214.7 | 231.4
834 | 734 | 349.6 | 191.6 | 179.7 | 130.8 | 214.6 | 231.4
835 | 735 | 349.6 | 191.7 | 179.9 | 131 | 214.3 | 231.5
836 | 736 | 349.7 | 191.8 | 180 | 131.1 | 214.1 | 231.5
837 | 737 | 349.7 | 191.9 | 180.1 | 131.3 | 214.2 | 231.6
838 | 738 | 349.7 | 192 | 180.3 | 131.4 | 214.3 | 231.6
839 | 739 | 349.6 | 192.1 | 180.4 | 131.5 | 214.4 | 231.7
840 | 740 | 349.6 | 192.2 | 180.6 | 131.7 | 214.7 | 231.7
841 | 741 | 349.7 | 192.3 | 180.7 | 131.8 | 214.8 | 231.7
842 | 742 | 349.7 | 192.4 | 180.8 | 132 | 214.8 | 231.8
843 | 743 | 349.7 | 192.5 | 181 | 132.1 | 214.9 | 231.8
844 | 744 | 349.8 | 192.6 | 181.1 | 132.2 | 215 | 231.9
845 | 745 | 349.8 | 192.7 | 181.3 | 132.4 | 215.2 | 231.9
846 | 746 | 349.7 | 192.8 | 181.4 | 132.5 | 215.4 | 231.9
847 | 747 | 349.7 | 192.9 | 181.5 | 132.7 | 215.5 | 232
848 | 748 | 349.8 | 193 | 181.7 | 132.8 | 215.6 | 232
849 | 749 | 349.8 | 193.1 | 181.8 | 132.9 | 215.9 | 232
850 | 750 | 349.7 | 193.2 | 182 | 133.1 | 216.3 | 232
851 | 751 | 349.8 | 193.3 | 182.1 | 133.2 | 216.7 | 232.1
852 | 752 | 349.9 | 193.5 | 182.2 | 133.4 | 216.9 | 232.1
853 | 753 | 350 | 193.6 | 182.4 | 133.5 | 217.2 | 232.2
854 | 754 | 349.9 | 193.7 | 182.5 | 133.6 | 217.4 | 232.2
855 | 755 | 349.9 | 193.8 | 182.7 | 133.8 | 217.2 | 232.3
856 | 756 | 349.8 | 193.9 | 182.8 | 133.9 | 217.1 | 232.3
857 | 757 | 349.7 | 194 | 182.9 | 134 | 217.5 | 232.3
858 | 758 | 349.6 | 194.1 | 183.1 | 134.2 | 217.9 | 232.3
859 | 759 | 349.7 | 194.2 | 183.2 | 134.3 | 218.2 | 232.3
860 | 760 | 349.8 | 194.3 | 183.4 | 134.4 | 218.4 | 232.4
861 | 761 | 349.9 | 194.4 | 183.5 | 134.6 | 218.6 | 232.4
862 | 762 | 350 | 194.5 | 183.6 | 134.7 | 218.7 | 232.4
863 | 763 | 350 | 194.6 | 183.8 | 134.8 | 218.7 | 232.5
864 | 764 | 350 | 194.8 | 183.9 | 135 | 218.9 | 232.6
865 | 765 | 349.9 | 194.9 | 184.1 | 135.1 | 218.9 | 232.6
866 | 766 | 349.9 | 195 | 184.2 | 135.2 | 218.6 | 232.6
867 | 767 | 349.9 | 195.1 | 184.4 | 135.4 | 218.5 | 232.6
868 | 768 | 349.9 | 195.2 | 184.5 | 135.5 | 218.5 | 232.7
869 | 769 | 349.8 | 195.3 | 184.7 | 135.6 | 218.8 | 232.7
870 | 770 | 349.7 | 195.4 | 184.8 | 135.8 | 219 | 232.7
871 | 771 | 349.7 | 195.6 | 184.9 | 135.9 | 219.3 | 232.7
872 | 772 | 349.7 | 195.7 | 185.1 | 136 | 219.7 | 232.8
873 | 773 | 349.7 | 195.8 | 185.2 | 136.2 | 219.9 | 232.8
874 | 774 | 349.7 | 195.9 | 185.4 | 136.3 | 220.1 | 232.8
875 | 775 | 349.8 | 196 | 185.5 | 136.4 | 220.3 | 232.9
876 | 776 | 349.7 | 196.1 | 185.7 | 136.6 | 220.4 | 232.9
877 | 777 | 349.7 | 196.2 | 185.8 | 136.7 | 220.2 | 232.9
878 | 778 | 349.6 | 196.4 | 185.9 | 136.8 | 220.3 | 232.9
879 | 779 | 349.6 | 196.5 | 186.1 | 137 | 220.2 | 232.9
880 | 780 | 349.7 | 196.6 | 186.2 | 137.1 | 220 | 232.9
881 | 781 | 349.8 | 196.7 | 186.3 | 137.2 | 219.9 | 232.9
882 | 782 | 349.8 | 196.8 | 186.5 | 137.4 | 219.7 | 233
883 | 783 | 349.9 | 196.9 | 186.6 | 137.5 | 219.7 | 233
884 | 784 | 349.9 | 197 | 186.7 | 137.6 | 219.9 | 233
885 | 785 | 350 | 197.1 | 186.9 | 137.8 | 220.1 | 233
886 | 786 | 350 | 197.3 | 187 | 137.9 | 220 | 233.1
887 | 787 | 350 | 197.4 | 187.1 | 138 | 220 | 233.1
888 | 788 | 350 | 197.5 | 187.2 | 138.2 | 219.8 | 233.1
889 | 789 | 349.8 | 197.6 | 187.4 | 138.3 | 219.6 | 233.1
890 | 790 | 349.8 | 197.7 | 187.5 | 138.4 | 219.6 | 233.1
891 | 791 | 349.9 | 197.8 | 187.6 | 138.6 | 219.7 | 233.1
892 | 792 | 349.9 | 197.9 | 187.8 | 138.7 | 219.9 | 233.2
893 | 793 | 350 | 198.1 | 187.9 | 138.8 | 220.1 | 233.2
894 | 794 | 349.9 | 198.2 | 188 | 138.9 | 220.5 | 233.2
895 | 795 | 349.7 | 198.3 | 188.2 | 139.1 | 220.7 | 233.2
896 | 796 | 349.7 | 198.4 | 188.3 | 139.2 | 220.6 | 233.2
897 | 797 | 349.7 | 198.5 | 188.4 | 139.3 | 220.5 | 233.3
898 | 798 | 349.7 | 198.6 | 188.6 | 139.5 | 220.6 | 233.3
899 | 799 | 349.6 | 198.7 | 188.7 | 139.6 | 220.8 | 233.4
900 | 800 | 349.6 | 198.8 | 188.8 | 139.7 | 220.9 | 233.4
901 | 801 | 349.5 | 199 | 189 | 139.9 | 221.1 | 233.5
902 | 802 | 349.5 | 199.1 | 189.1 | 140 | 221.1 | 233.5
903 | 803 | 349.5 | 199.2 | 189.2 | 140.1 | 221.2 | 233.5
904 | 804 | 349.4 | 199.3 | 189.4 | 140.3 | 221.5 | 233.6
905 | 805 | 349.3 | 199.4 | 189.5 | 140.4 | 221.7 | 233.6
906 | 806 | 349.2 | 199.5 | 189.6 | 140.5 | 222 | 233.6
907 | 807 | 349.2 | 199.6 | 189.8 | 140.6 | 222.1 | 233.6
908 | 808 | 349.2 | 199.7 | 189.9 | 140.8 | 222.2 | 233.6
909 | 809 | 349 | 199.8 | 190 | 140.9 | 222.3 | 233.6
910 | 810 | 348.9 | 199.9 | 190.1 | 141 | 222.1 | 233.6
911 | 811 | 348.9 | 200 | 190.3 | 141.2 | 222.2 | 233.7
912 | 812 | 348.8 | 200.1 | 190.4 | 141.3 | 222.3 | 233.7
913 | 813 | 348.8 | 200.3 | 190.5 | 141.4 | 222.4 | 233.7
914 | 814 | 348.7 | 200.4 | 190.7 | 141.6 | 222.3 | 233.8
915 | 815 | 348.7 | 200.5 | 190.8 | 141.7 | 222.3 | 233.8
916 | 816 | 348.6 | 200.6 | 190.9 | 141.8 | 222.3 | 233.8
917 | 817 | 348.7 | 200.7 | 191.1 | 142 | 222.2 | 233.8
918 | 818 | 348.7 | 200.9 | 191.2 | 142.1 | 222.1 | 233.8
919 | 819 | 348.7 | 201 | 191.3 | 142.2 | 222.1 | 233.8
920 | 820 | 348.6 | 201.1 | 191.4 | 142.3 | 221.9 | 233.9
921 | 821 | 348.5 | 201.2 | 191.6 | 142.5 | 221.5 | 233.9
922 | 822 | 348.5 | 201.3 | 191.7 | 142.6 | 221 | 233.9
923 | 823 | 348.5 | 201.4 | 191.8 | 142.7 | 221 | 233.9
924 | 824 | 348.5 | 201.6 | 191.9 | 142.9 | 220.5 | 234
925 | 825 | 348.5 | 201.7 | 192.1 | 143 | 220.1 | 234
926 | 826 | 348.6 | 201.8 | 192.2 | 143.1 | 220.1 | 234
927 | 827 | 348.6 | 201.9 | 192.3 | 143.3 | 219.8 | 234
928 | 828 | 348.7 | 202 | 192.5 | 143.4 | 219.9 | 234
929 | 829 | 348.7 | 202.1 | 192.6 | 143.5 | 220 | 234
930 | 830 | 348.6 | 202.2 | 192.7 | 143.6 | 219.7 | 234.1
931 | 831 | 348.6 | 202.3 | 192.8 | 143.8 | 219.4 | 234.1
932 | 832 | 348.7 | 202.4 | 193 | 143.9 | 218.9 | 234.1
933 | 833 | 348.8 | 202.5 | 193.1 | 144 | 218.8 | 234.1
934 | 834 | 348.8 | 202.6 | 193.2 | 144.2 | 218.6 | 234.1
935 | 835 | 348.8 | 202.7 | 193.4 | 144.3 | 218.7 | 234.1
936 | 836 | 348.7 | 202.7 | 193.5 | 144.4 | 218.7 | 234.2
937 | 837 | 348.6 | 202.8 | 193.6 | 144.6 | 219.1 | 234.2
938 | 838 | 348.7 | 202.9 | 193.7 | 144.7 | 219.6 | 234.2
939 | 839 | 348.7 | 203 | 193.8 | 144.8 | 219.7 | 234.2
940 | 840 | 348.6 | 203.1 | 194 | 144.9 | 219.9 | 234.2
941 | 841 | 348.8 | 203.1 | 194.1 | 145.1 | 219.8 | 234.2
942 | 842 | 348.9 | 203.2 | 194.2 | 145.2 | 219.7 | 234.3
943 | 843 | 349.1 | 203.3 | 194.3 | 145.3 | 219.5 | 234.3
944 | 844 | 349.1 | 203.4 | 194.4 | 145.5 | 219.7 | 234.3
945 | 845 | 349.2 | 203.5 | 194.5 | 145.6 | 219.7 | 234.3
946 | 846 | 349.2 | 203.5 | 194.6 | 145.7 | 219.5 | 234.3
947 | 847 | 349.3 | 203.6 | 194.7 | 145.8 | 219.3 | 234.4
948 | 848 | 349.5 | 203.7 | 194.8 | 146 | 219.4 | 234.4
949 | 849 | 349.6 | 203.8 | 195 | 146.1 | 219.7 | 234.4
950 | 850 | 349.8 | 203.9 | 195.1 | 146.2 | 219.7 | 234.5
951 | 851 | 349.9 | 204 | 195.2 | 146.3 | 220 | 234.5
952 | 852 | 350.1 | 204.1 | 195.3 | 146.5 | 220.3 | 234.5
953 | 853 | 350.2 | 204.2 | 195.4 | 146.6 | 220.3 | 234.5
954 | 854 | 350.3 | 204.3 | 195.6 | 146.7 | 220.6 | 234.5
955 | 855 | 350.2 | 204.4 | 195.7 | 146.8 | 220.9 | 234.6
956 | 856 | 350.2 | 204.5 | 195.8 | 147 | 221.1 | 234.6
957 | 857 | 350.1 | 204.6 | 195.9 | 147.1 | 221.3 | 234.7
958 | 858 | 350 | 204.7 | 196 | 147.2 | 221.4 | 234.7
959 | 859 | 350 | 204.8 | 196.1 | 147.3 | 221.5 | 234.7
960 | 860 | 350 | 204.9 | 196.2 | 147.5 | 221.2 | 234.7
961 | 861 | 349.9 | 205 | 196.4 | 147.6 | 220.6 | 234.8
962 | 862 | 349.9 | 205.1 | 196.5 | 147.7 | 220.4 | 234.8
963 | 863 | 350 | 205.3 | 196.6 | 147.8 | 220 | 234.9
964 | 864 | 349.9 | 205.4 | 196.7 | 148 | 220.1 | 234.9
965 | 865 | 349.8 | 205.5 | 196.8 | 148.1 | 219.8 | 234.9
966 | 866 | 349.6 | 205.6 | 196.9 | 148.2 | 219.9 | 234.8
967 | 867 | 349.4 | 205.7 | 197.1 | 148.3 | 219.7 | 234.8
968 | 868 | 349.3 | 205.8 | 197.2 | 148.4 | 219.4 | 234.8
969 | 869 | 349.1 | 205.9 | 197.3 | 148.6 | 218.8 | 234.8
970 | 870 | 349.1 | 206 | 197.4 | 148.7 | 218.8 | 234.9
971 | 871 | 349 | 206 | 197.5 | 148.8 | 218.5 | 234.9
972 | 872 | 349.1 | 206.2 | 197.7 | 148.9 | 218.2 | 234.9
973 | 873 | 349.2 | 206.3 | 197.8 | 149 | 218.4 | 234.9
974 | 874 | 349.2 | 206.4 | 197.9 | 149.2 | 218.9 | 235
975 | 875 | 349.3 | 206.5 | 198 | 149.3 | 219 | 235
976 | 876 | 349.3 | 206.6 | 198.2 | 149.4 | 218.7 | 235
977 | 877 | 349.3 | 206.7 | 198.3 | 149.5 | 218.3 | 235
978 | 878 | 349.5 | 206.7 | 198.4 | 149.6 | 218.2 | 235
979 | 879 | 349.5 | 206.8 | 198.5 | 149.8 | 217.9 | 235
980 | 880 | 349.4 | 206.9 | 198.7 | 149.9 | 218.3 | 235.1
981 | 881 | 349.4 | 207 | 198.8 | 150 | 218.7 | 235.1
982 | 882 | 349.5 | 207.1 | 198.9 | 150.1 | 218.9 | 235.1
983 | 883 | 349.5 | 207.2 | 199 | 150.2 | 218.8 | 235.1
984 | 884 | 349.4 | 207.3 | 199.1 | 150.4 | 218.9 | 235.1
985 | 885 | 349.3 | 207.4 | 199.3 | 150.5 | 219.1 | 235.2
986 | 886 | 349.4 | 207.5 | 199.4 | 150.6 | 219 | 235.2
987 | 887 | 349.4 | 207.6 | 199.5 | 150.7 | 219.1 | 235.2
988 | 888 | 349.5 | 207.7 | 199.6 | 150.8 | 218.7 | 235.3
989 | 889 | 349.6 | 207.8 | 199.7 | 151 | 218.7 | 235.3
990 | 890 | 349.7 | 207.9 | 199.8 | 151.1 | 218.8 | 235.3
991 | 891 | 349.7 | 208 | 200 | 151.2 | 219.1 | 235.3
992 | 892 | 349.6 | 208.1 | 200.1 | 151.3 | 219.4 | 235.4
993 | 893 | 349.6 | 208.2 | 200.2 | 151.4 | 219.8 | 235.4
994 | 894 | 349.7 | 208.3 | 200.3 | 151.6 | 220.1 | 235.4
995 | 895 | 349.8 | 208.4 | 200.4 | 151.7 | 219.9 | 235.4
996 | 896 | 349.8 | 208.5 | 200.5 | 151.8 | 220 | 235.4
997 | 897 | 349.7 | 208.6 | 200.6 | 151.9 | 220.1 | 235.4
998 | 898 | 349.7 | 208.7 | 200.8 | 152 | 220.3 | 235.4
999 | 899 | 349.5 | 208.8 | 200.9 | 152.1 | 220.1 | 235.5
1000 | 900 | 349.5 | 208.9 | 201 | 152.2 | 220.3 | 235.4
1001 | 901 | 349.5 | 209 | 201.1 | 152.4 | 220.4 | 235.4
1002 | 902 | 349.5 | 209.1 | 201.2 | 152.5 | 220.3 | 235.4
1003 | 903 | 349.5 | 209.2 | 201.3 | 152.6 | 220.5 | 235.4
1004 | 904 | 349.4 | 209.3 | 201.4 | 152.7 | 220.7 | 235.4
1005 | 905 | 349.3 | 209.4 | 201.6 | 152.8 | 220.6 | 235.4
1006 | 906 | 349.3 | 209.5 | 201.7 | 152.9 | 220.7 | 235.4
1007 | 907 | 349.3 | 209.6 | 201.8 | 153.1 | 221 | 235.4
1008 | 908 | 349.1 | 209.7 | 201.9 | 153.2 | 221.3 | 235.4
1009 | 909 | 349.1 | 209.8 | 202 | 153.3 | 221.3 | 235.4
1010 | 910 | 349.1 | 209.9 | 202.1 | 153.4 | 221.5 | 235.4
1011 | 911 | 349.2 | 210 | 202.2 | 153.5 | 221.8 | 235.3
1012 | 912 | 349.3 | 210.1 | 202.3 | 153.6 | 222.2 | 235.3
1013 | 913 | 349.2 | 210.2 | 202.4 | 153.7 | 222.5 | 235.3
1014 | 914 | 349.2 | 210.3 | 202.5 | 153.9 | 222.4 | 235.3
1015 | 915 | 349.1 | 210.5 | 202.7 | 154 | 222.4 | 235.3
1016 | 916 | 349.2 | 210.6 | 202.8 | 154.1 | 222.5 | 235.3
1017 | 917 | 349.2 | 210.7 | 202.9 | 154.2 | 222.7 | 235.4
1018 | 918 | 349.3 | 210.7 | 203 | 154.3 | 223.2 | 235.4
1019 | 919 | 349.3 | 210.8 | 203.1 | 154.4 | 223.2 | 235.5
1020 | 920 | 349.3 | 210.9 | 203.2 | 154.5 | 222.7 | 235.5
1021 | 921 | 349.3 | 211 | 203.3 | 154.7 | 222.7 | 235.5
1022 | 922 | 349.4 | 211.1 | 203.4 | 154.8 | 223.1 | 235.5
1023 | 923 | 349.3 | 211.3 | 203.5 | 154.9 | 223.3 | 235.5
1024 | 924 | 349.3 | 211.4 | 203.6 | 155 | 223.3 | 235.5
1025 | 925 | 349.2 | 211.4 | 203.8 | 155.1 | 223.2 | 235.5
1026 | 926 | 349.3 | 211.5 | 203.9 | 155.2 | 222.7 | 235.5
1027 | 927 | 349.4 | 211.6 | 204 | 155.3 | 222.9 | 235.5
1028 | 928 | 349.5 | 211.7 | 204.1 | 155.5 | 222.9 | 235.5
1029 | 929 | 349.5 | 211.8 | 204.2 | 155.6 | 222.6 | 235.5
1030 | 930 | 349.4 | 211.9 | 204.3 | 155.7 | 222.7 | 235.6
1031 | 931 | 349.3 | 212 | 204.4 | 155.8 | 222.8 | 235.6
1032 | 932 | 349.3 | 212.1 | 204.5 | 155.9 | 223.1 | 235.6
1033 | 933 | 349.3 | 212.2 | 204.7 | 156 | 222.8 | 235.7
1034 | 934 | 349.3 | 212.3 | 204.8 | 156.1 | 222.5 | 235.7
1035 | 935 | 349.3 | 212.3 | 204.9 | 156.3 | 222.7 | 235.7
1036 | 936 | 349.2 | 212.4 | 205 | 156.4 | 222.4 | 235.7
1037 | 937 | 349.2 | 212.5 | 205.1 | 156.5 | 221.8 | 235.7
1038 | 938 | 349.4 | 212.6 | 205.2 | 156.6 | 221.6 | 235.7
1039 | 939 | 349.5 | 212.7 | 205.4 | 156.7 | 221.7 | 235.7
1040 | 940 | 349.6 | 212.7 | 205.5 | 156.8 | 221.8 | 235.7
1041 | 941 | 349.8 | 212.8 | 205.6 | 156.9 | 222.2 | 235.8
1042 | 942 | 349.9 | 212.9 | 205.7 | 157 | 222.1 | 235.8
1043 | 943 | 350.1 | 213 | 205.8 | 157.1 | 221.5 | 235.8
1044 | 944 | 350 | 213.1 | 205.9 | 157.3 | 221.2 | 235.8
1045 | 945 | 350 | 213.1 | 206 | 157.4 | 221 | 235.8
1046 | 946 | 350 | 213.2 | 206.2 | 157.5 | 220.9 | 235.9
1047 | 947 | 350 | 213.3 | 206.3 | 157.6 | 221.1 | 235.9
1048 | 948 | 350 | 213.3 | 206.4 | 157.7 | 220.7 | 235.9
1049 | 949 | 350 | 213.4 | 206.5 | 157.8 | 220.2 | 236
1050 | 950 | 350.1 | 213.5 | 206.6 | 157.9 | 220.1 | 236
1051 | 951 | 350.2 | 213.5 | 206.7 | 158.1 | 220.1 | 236
1052 | 952 | 350.3 | 213.6 | 206.8 | 158.2 | 220.3 | 236
1053 | 953 | 350.3 | 213.6 | 206.9 | 158.3 | 220.5 | 236
1054 | 954 | 350.3 | 213.7 | 207 | 158.4 | 220.7 | 236
1055 | 955 | 350.2 | 213.8 | 207.1 | 158.5 | 221 | 236
1056 | 956 | 350.2 | 213.8 | 207.2 | 158.6 | 221.1 | 236
1057 | 957 | 350.1 | 213.9 | 207.3 | 158.7 | 221.3 | 236.1
1058 | 958 | 350.3 | 214 | 207.4 | 158.8 | 221.3 | 236.1
1059 | 959 | 350.3 | 214 | 207.5 | 158.9 | 221.2 | 236.1
1060 | 960 | 350.2 | 214.1 | 207.6 | 159.1 | 220.7 | 236.1
1061 | 961 | 350.1 | 214.2 | 207.7 | 159.2 | 221.2 | 236.1
1062 | 962 | 349.9 | 214.2 | 207.8 | 159.3 | 221.7 | 236.1
1063 | 963 | 349.7 | 214.3 | 208 | 159.4 | 222 | 236.2
1064 | 964 | 349.6 | 214.4 | 208.1 | 159.5 | 222.2 | 236.2
1065 | 965 | 349.5 | 214.4 | 208.2 | 159.6 | 222.4 | 236.2
1066 | 966 | 349.4 | 214.5 | 208.3 | 159.7 | 222.8 | 236.2
1067 | 967 | 349.3 | 214.6 | 208.4 | 159.8 | 223.1 | 236.2
1068 | 968 | 349.2 | 214.7 | 208.5 | 159.9 | 223.3 | 236.2
1069 | 969 | 349.1 | 214.7 | 208.6 | 160 | 223.6 | 236.2
1070 | 970 | 349 | 214.8 | 208.7 | 160.2 | 223.8 | 236.2
1071 | 971 | 349 | 214.9 | 208.8 | 160.3 | 224.2 | 236.2
1072 | 972 | 348.9 | 215 | 208.9 | 160.4 | 224.6 | 236.2
1073 | 973 | 348.9 | 215.1 | 209 | 160.5 | 224.6 | 236.3
1074 | 974 | 348.9 | 215.2 | 209.1 | 160.6 | 224.5 | 236.3
1075 | 975 | 348.8 | 215.3 | 209.2 | 160.7 | 224.8 | 236.3
1076 | 976 | 348.8 | 215.4 | 209.3 | 160.8 | 224.7 | 236.3
1077 | 977 | 348.7 | 215.5 | 209.4 | 160.9 | 224.8 | 236.3
1078 | 978 | 348.6 | 215.5 | 209.5 | 161 | 225 | 236.3
1079 | 979 | 348.6 | 215.6 | 209.6 | 161.1 | 225.2 | 236.3
1080 | 980 | 348.6 | 215.7 | 209.6 | 161.2 | 225.1 | 236.3
1081 | 981 | 348.7 | 215.8 | 209.7 | 161.3 | 225 | 236.3
1082 | 982 | 348.7 | 215.9 | 209.8 | 161.5 | 225.2 | 236.3
1083 | 983 | 348.7 | 216 | 209.9 | 161.6 | 225.4 | 236.4
1084 | 984 | 348.6 | 216.1 | 210 | 161.7 | 225.6 | 236.4
1085 | 985 | 348.6 | 216.2 | 210.1 | 161.8 | 225.7 | 236.4
1086 | 986 | 348.8 | 216.3 | 210.1 | 161.9 | 225.6 | 236.4
1087 | 987 | 348.8 | 216.4 | 210.2 | 162 | 225.9 | 236.4
1088 | 988 | 348.8 | 216.4 | 210.3 | 162.1 | 226 | 236.4
1089 | 989 | 348.8 | 216.5 | 210.4 | 162.2 | 226.2 | 236.4
1090 | 990 | 348.8 | 216.6 | 210.5 | 162.3 | 226.2 | 236.5
1091 | 991 | 348.8 | 216.7 | 210.6 | 162.4 | 226.2 | 236.5
1092 | 992 | 348.9 | 216.7 | 210.7 | 162.5 | 225.9 | 236.5
1093 | 993 | 348.9 | 216.8 | 210.7 | 162.6 | 225.6 | 236.4
1094 | 994 | 348.9 | 216.9 | 210.8 | 162.7 | 225.7 | 236.5
1095 | 995 | 348.8 | 216.9 | 210.9 | 162.8 | 225.9 | 236.5
1096 | 996 | 348.7 | 217 | 211 | 163 | 225.9 | 236.5
1097 | 997 | 348.7 | 217 | 211.1 | 163 | 225.2 | 236.5
1098 | 998 | 348.8 | 217.1 | 211.1 | 163.2 | 225.7 | 236.5
1099 | 999 | 348.7 | 217.2 | 211.2 | 163.3 | 225.9 | 236.5
1100 | 1000 | 348.8 | 217.3 | 211.3 | 163.4 | 225.6 | 236.5
1101 | 1001 | 348.8 | 217.3 | 211.4 | 163.5 | 225.7 | 236.5
1102 | 1002 | 348.8 | 217.4 | 211.5 | 163.6 | 225.9 | 236.5
1103 | 1003 | 348.8 | 217.5 | 211.5 | 163.7 | 226.1 | 236.5
1104 | 1004 | 348.8 | 217.5 | 211.6 | 163.8 | 226.3 | 236.6
1105 | 1005 | 348.8 | 217.6 | 211.7 | 163.9 | 226.6 | 236.6
1106 | 1006 | 348.8 | 217.7 | 211.8 | 164 | 226.8 | 236.6
1107 | 1007 | 348.9 | 217.8 | 211.8 | 164.1 | 226.5 | 236.6
1108 | 1008 | 349 | 217.8 | 211.9 | 164.2 | 226.8 | 236.6
1109 | 1009 | 349 | 217.9 | 212 | 164.3 | 227 | 236.6
1110 | 1010 | 349 | 218 | 212.1 | 164.4 | 227 | 236.6
1111 | 1011 | 348.9 | 218.1 | 212.1 | 164.5 | 226.8 | 236.6
1112 | 1012 | 349 | 218.2 | 212.2 | 164.6 | 226.7 | 236.7
1113 | 1013 | 349.1 | 218.3 | 212.3 | 164.7 | 226.4 | 236.6
1114 | 1014 | 349 | 218.4 | 212.4 | 164.8 | 226.2 | 236.6
1115 | 1015 | 349 | 218.5 | 212.5 | 164.9 | 226.4 | 236.6
1116 | 1016 | 349.1 | 218.6 | 212.5 | 165.1 | 226.5 | 236.6
1117 | 1017 | 349.1 | 218.7 | 212.6 | 165.2 | 226.7 | 236.7
1118 | 1018 | 349.1 | 218.8 | 212.7 | 165.3 | 226.9 | 236.7
1119 | 1019 | 349.1 | 218.9 | 212.8 | 165.4 | 227 | 236.7
1120 | 1020 | 349.2 | 219 | 212.8 | 165.5 | 227.4 | 236.8
1121 | 1021 | 349.2 | 219.1 | 212.9 | 165.6 | 227.6 | 236.8
1122 | 1022 | 349.1 | 219.2 | 213 | 165.7 | 227.8 | 236.8
1123 | 1023 | 349 | 219.3 | 213.1 | 165.8 | 227.6 | 236.8
1124 | 1024 | 349.1 | 219.4 | 213.1 | 165.9 | 227.1 | 236.9
1125 | 1025 | 349.1 | 219.4 | 213.2 | 166 | 226.9 | 236.8
1126 | 1026 | 349 | 219.5 | 213.3 | 166.1 | 226.3 | 236.9
1127 | 1027 | 349 | 219.6 | 213.4 | 166.2 | 225.8 | 236.9
1128 | 1028 | 348.9 | 219.7 | 213.4 | 166.3 | 226 | 236.9
1129 | 1029 | 348.9 | 219.8 | 213.5 | 166.4 | 226.1 | 236.9
1130 | 1030 | 348.9 | 219.8 | 213.6 | 166.5 | 225.8 | 236.9
1131 | 1031 | 348.8 | 219.9 | 213.7 | 166.6 | 225.9 | 237
1132 | 1032 | 348.9 | 220 | 213.7 | 166.7 | 225.7 | 237
1133 | 1033 | 349 | 220 | 213.8 | 166.9 | 225.4 | 237.1
1134 | 1034 | 349 | 220.1 | 213.9 | 167 | 225.8 | 237.1
1135 | 1035 | 349 | 220.1 | 213.9 | 167.1 | 225.6 | 237.1
1136 | 1036 | 349 | 220.2 | 214 | 167.2 | 225.6 | 237.1
1137 | 1037 | 349 | 220.3 | 214.1 | 167.3 | 225.9 | 237.1
1138 | 1038 | 349 | 220.3 | 214.2 | 167.4 | 226.4 | 237.2
1139 | 1039 | 349.1 | 220.4 | 214.2 | 167.5 | 226.3 | 237.2
1140 | 1040 | 349.2 | 220.5 | 214.3 | 167.6 | 226.3 | 237.2
1141 | 1041 | 349.3 | 220.5 | 214.4 | 167.7 | 226.2 | 237.2
1142 | 1042 | 349.3 | 220.6 | 214.5 | 167.8 | 226 | 237.3
1143 | 1043 | 349.4 | 220.7 | 214.5 | 167.9 | 225.8 | 237.3
1144 | 1044 | 349.5 | 220.7 | 214.6 | 168 | 226.1 | 237.3
1145 | 1045 | 349.5 | 220.8 | 214.7 | 168.1 | 225.8 | 237.3
1146 | 1046 | 349.5 | 220.8 | 214.7 | 168.2 | 225.5 | 237.3
1147 | 1047 | 349.4 | 220.9 | 214.8 | 168.3 | 226 | 237.4
1148 | 1048 | 349.5 | 221 | 214.8 | 168.4 | 225.9 | 237.4
1149 | 1049 | 349.5 | 221 | 214.9 | 168.5 | 226.2 | 237.4
1150 | 1050 | 349.6 | 221.1 | 215 | 168.6 | 226.7 | 237.4
1151 | 1051 | 349.5 | 221.2 | 215 | 168.7 | 227 | 237.4
1152 | 1052 | 349.6 | 221.2 | 215.1 | 168.9 | 227 | 237.4
1153 | 1053 | 349.6 | 221.3 | 215.1 | 169 | 226.8 | 237.4
1154 | 1054 | 349.6 | 221.4 | 215.2 | 169.1 | 226.7 | 237.4
1155 | 1055 | 349.7 | 221.4 | 215.3 | 169.2 | 226.6 | 237.5
1156 | 1056 | 349.6 | 221.5 | 215.3 | 169.3 | 226.9 | 237.5
1157 | 1057 | 349.6 | 221.6 | 215.3 | 169.4 | 227.3 | 237.5
1158 | 1058 | 349.6 | 221.7 | 215.4 | 169.5 | 227.7 | 237.6
1159 | 1059 | 349.6 | 221.7 | 215.4 | 169.6 | 228.2 | 237.6
1160 | 1060 | 349.6 | 221.8 | 215.5 | 169.7 | 228.5 | 237.6
1161 | 1061 | 349.7 | 221.9 | 215.5 | 169.8 | 228.7 | 237.5
1162 | 1062 | 349.6 | 222 | 215.6 | 169.9 | 229.1 | 237.5
1163 | 1063 | 349.5 | 222.1 | 215.7 | 170 | 229.3 | 237.6
1164 | 1064 | 349.5 | 222.1 | 215.7 | 170.1 | 229.2 | 237.6
1165 | 1065 | 349.4 | 222.2 | 215.8 | 170.2 | 229.6 | 237.7
1166 | 1066 | 349.3 | 222.3 | 215.9 | 170.3 | 229.8 | 237.7
1167 | 1067 | 349.2 | 222.4 | 215.9 | 170.4 | 229.9 | 237.7
1168 | 1068 | 349.1 | 222.5 | 216 | 170.5 | 230.2 | 237.7
1169 | 1069 | 349 | 222.5 | 216 | 170.6 | 230.1 | 237.7
1170 | 1070 | 348.9 | 222.6 | 216.1 | 170.7 | 230.3 | 237.8
1171 | 1071 | 348.9 | 222.7 | 216.2 | 170.8 | 230.4 | 237.8
1172 | 1072 | 348.8 | 222.7 | 216.3 | 170.9 | 230 | 237.8
1173 | 1073 | 348.7 | 222.8 | 216.3 | 171 | 229.9 | 237.8
1174 | 1074 | 348.7 | 222.9 | 216.4 | 171.1 | 229.9 | 237.7
1175 | 1075 | 348.7 | 222.9 | 216.4 | 171.2 | 229.9 | 237.7
1176 | 1076 | 348.5 | 223 | 216.5 | 171.3 | 230 | 237.7
1177 | 1077 | 348.2 | 223.1 | 216.5 | 171.4 | 229.7 | 237.7
1178 | 1078 | 348 | 223.2 | 216.6 | 171.5 | 229.7 | 237.7
1179 | 1079 | 348 | 223.2 | 216.7 | 171.7 | 229.5 | 237.7
1180 | 1080 | 347.9 | 223.3 | 216.7 | 171.7 | 229.3 | 237.7
1181 | 1081 | 347.8 | 223.4 | 216.8 | 171.9 | 229.2 | 237.7
1182 | 1082 | 347.8 | 223.4 | 216.9 | 172 | 229.2 | 237.7
1183 | 1083 | 347.8 | 223.5 | 216.9 | 172.1 | 228.4 | 237.7
1184 | 1084 | 347.8 | 223.5 | 217 | 172.2 | 228.5 | 237.7
1185 | 1085 | 348 | 223.6 | 217 | 172.3 | 228.5 | 237.7
1186 | 1086 | 348 | 223.6 | 217.1 | 172.4 | 228.1 | 237.7
1187 | 1087 | 348 | 223.7 | 217.2 | 172.5 | 228.1 | 237.7
1188 | 1088 | 348 | 223.7 | 217.2 | 172.6 | 227.7 | 237.8
1189 | 1089 | 348 | 223.7 | 217.3 | 172.7 | 227.6 | 237.8
1190 | 1090 | 348 | 223.8 | 217.4 | 172.8 | 227.7 | 237.8
1191 | 1091 | 348 | 223.8 | 217.4 | 172.9 | 227.3 | 237.8
1192 | 1092 | 348 | 223.9 | 217.5 | 173 | 226.9 | 237.9
1193 | 1093 | 347.9 | 223.9 | 217.6 | 173.1 | 227.4 | 237.9
1194 | 1094 | 348 | 224 | 217.6 | 173.2 | 227.9 | 237.9
1195 | 1095 | 348 | 224 | 217.7 | 173.3 | 227.9 | 237.9
1196 | 1096 | 348.1 | 224.1 | 217.8 | 173.4 | 227.8 | 237.9
1197 | 1097 | 348.2 | 224.1 | 217.9 | 173.5 | 228.3 | 237.9
1198 | 1098 | 348.4 | 224.2 | 217.9 | 173.6 | 228.6 | 237.9
1199 | 1099 | 348.4 | 224.2 | 218 | 173.7 | 228.9 | 237.9
1200 | 1100 | 348.5 | 224.2 | 218.1 | 173.8 | 229.2 | 237.9
1201 | 1101 | 348.5 | 224.3 | 218.1 | 173.9 | 229.4 | 238
1202 | 1102 | 348.5 | 224.4 | 218.2 | 174 | 229.7 | 238
1203 | 1103 | 348.5 | 224.4 | 218.3 | 174.1 | 229.9 | 238
1204 | 1104 | 348.5 | 224.5 | 218.3 | 174.2 | 230.2 | 238
1205 | 1105 | 348.5 | 224.5 | 218.4 | 174.3 | 230.4 | 238.1
1206 | 1106 | 348.5 | 224.6 | 218.5 | 174.4 | 230.3 | 238.1
1207 | 1107 | 348.6 | 224.6 | 218.6 | 174.5 | 230.4 | 238.1
1208 | 1108 | 348.6 | 224.7 | 218.6 | 174.6 | 230.6 | 238.1
1209 | 1109 | 348.6 | 224.7 | 218.7 | 174.7 | 230.4 | 238.2
1210 | 1110 | 348.6 | 224.8 | 218.8 | 174.8 | 230.5 | 238.2
1211 | 1111 | 348.7 | 224.8 | 218.8 | 174.9 | 230.4 | 238.2
1212 | 1112 | 348.8 | 224.9 | 218.9 | 175 | 230.3 | 238.3
1213 | 1113 | 348.7 | 225 | 218.9 | 175.1 | 230.4 | 238.3
1214 | 1114 | 348.6 | 225 | 219 | 175.2 | 230.4 | 238.3
1215 | 1115 | 348.7 | 225.1 | 219.1 | 175.3 | 230.4 | 238.4
1216 | 1116 | 348.8 | 225.2 | 219.1 | 175.4 | 229.8 | 238.4
1217 | 1117 | 349 | 225.2 | 219.2 | 175.5 | 229.9 | 238.4
1218 | 1118 | 349 | 225.3 | 219.3 | 175.6 | 229.7 | 238.5
1219 | 1119 | 349 | 225.4 | 219.4 | 175.7 | 229.6 | 238.5
1220 | 1120 | 349.1 | 225.4 | 219.4 | 175.8 | 229.5 | 238.6
1221 | 1121 | 349.1 | 225.5 | 219.5 | 175.9 | 228.8 | 238.7
1222 | 1122 | 349.1 | 225.6 | 219.6 | 176 | 229.2 | 238.7
1223 | 1123 | 349 | 225.6 | 219.6 | 176.1 | 228.8 | 238.8
1224 | 1124 | 349.1 | 225.7 | 219.7 | 176.2 | 228.7 | 238.8
1225 | 1125 | 349.1 | 225.7 | 219.8 | 176.3 | 228.7 | 238.8
1226 | 1126 | 349.1 | 225.7 | 219.9 | 176.4 | 228.6 | 238.8
1227 | 1127 | 349.1 | 225.8 | 220 | 176.5 | 228.8 | 238.9
1228 | 1128 | 349.1 | 225.8 | 220.1 | 176.6 | 228.8 | 238.9
1229 | 1129 | 349.1 | 225.9 | 220.1 | 176.7 | 228.8 | 238.9
1230 | 1130 | 349.2 | 225.9 | 220.2 | 176.8 | 228.5 | 239
1231 | 1131 | 349.2 | 226 | 220.3 | 176.9 | 228.3 | 239
1232 | 1132 | 349.2 | 226 | 220.4 | 177 | 228.5 | 239
1233 | 1133 | 349.2 | 226.1 | 220.5 | 177.1 | 228.7 | 239
1234 | 1134 | 349.2 | 226.2 | 220.5 | 177.2 | 229.1 | 239
1235 | 1135 | 349.2 | 226.2 | 220.6 | 177.3 | 228.9 | 239
1236 | 1136 | 349.2 | 226.3 | 220.7 | 177.4 | 229.3 | 239
1237 | 1137 | 349.2 | 226.3 | 220.8 | 177.5 | 229 | 239
1238 | 1138 | 349.1 | 226.4 | 220.8 | 177.6 | 228.8 | 239
1239 | 1139 | 349.1 | 226.5 | 220.9 | 177.7 | 229.1 | 239
1240 | 1140 | 349.2 | 226.5 | 221 | 177.8 | 229.3 | 239.1
1241 | 1141 | 349.3 | 226.6 | 221 | 177.9 | 229.5 | 239.1
1242 | 1142 | 349.5 | 226.6 | 221.1 | 178 | 229.7 | 239.1
1243 | 1143 | 349.6 | 226.7 | 221.2 | 178.1 | 230 | 239.1
1244 | 1144 | 349.6 | 226.8 | 221.3 | 178.2 | 229.9 | 239.1
1245 | 1145 | 349.7 | 226.8 | 221.3 | 178.3 | 229.9 | 239.1
1246 | 1146 | 349.8 | 226.9 | 221.4 | 178.4 | 230.2 | 239.1
1247 | 1147 | 349.8 | 226.9 | 221.4 | 178.5 | 230.2 | 239.1
1248 | 1148 | 349.8 | 227 | 221.5 | 178.6 | 230.4 | 239.2
1249 | 1149 | 349.8 | 227 | 221.6 | 178.7 | 230.5 | 239.2
1250 | 1150 | 349.8 | 227.1 | 221.6 | 178.8 | 230.2 | 239.2
1251 | 1151 | 349.8 | 227.1 | 221.7 | 178.9 | 230.6 | 239.3
1252 | 1152 | 349.8 | 227.2 | 221.8 | 179 | 230.7 | 239.3
1253 | 1153 | 349.8 | 227.3 | 221.8 | 179.1 | 230.6 | 239.3
1254 | 1154 | 349.9 | 227.3 | 221.9 | 179.2 | 230.3 | 239.4
1255 | 1155 | 349.8 | 227.4 | 221.9 | 179.3 | 230.2 | 239.4
1256 | 1156 | 349.8 | 227.4 | 222 | 179.4 | 230 | 239.4
1257 | 1157 | 349.8 | 227.5 | 222 | 179.5 | 229.6 | 239.4
1258 | 1158 | 349.8 | 227.5 | 222.1 | 179.6 | 229.5 | 239.4
1259 | 1159 | 349.9 | 227.6 | 222.2 | 179.7 | 229.8 | 239.5
1260 | 1160 | 349.9 | 227.7 | 222.2 | 179.8 | 229.8 | 239.5
1261 | 1161 | 349.9 | 227.7 | 222.3 | 179.9 | 229.6 | 239.5
1262 | 1162 | 349.8 | 227.8 | 222.3 | 179.9 | 229.5 | 239.5
1263 | 1163 | 349.7 | 227.8 | 222.4 | 180 | 229.6 | 239.5
1264 | 1164 | 349.6 | 227.9 | 222.5 | 180.2 | 229.9 | 239.5
1265 | 1165 | 349.5 | 227.9 | 222.5 | 180.2 | 230 | 239.6
1266 | 1166 | 349.4 | 228 | 222.6 | 180.3 | 229.8 | 239.5
1267 | 1167 | 349.4 | 228 | 222.6 | 180.4 | 229.8 | 239.6
1268 | 1168 | 349.3 | 228 | 222.7 | 180.5 | 229.9 | 239.6
1269 | 1169 | 349.2 | 228.1 | 222.8 | 180.6 | 230.3 | 239.6
1270 | 1170 | 349.1 | 228.1 | 222.8 | 180.7 | 230.6 | 239.6
1271 | 1171 | 349 | 228.1 | 222.9 | 180.8 | 230.9 | 239.6
1272 | 1172 | 348.9 | 228.1 | 223 | 180.9 | 230.8 | 239.6
1273 | 1173 | 348.8 | 228.1 | 223 | 181 | 230.5 | 239.7
1274 | 1174 | 348.9 | 228.1 | 223.1 | 181.1 | 229.9 | 239.7
1275 | 1175 | 348.8 | 228.2 | 223.1 | 181.2 | 229.7 | 239.7
1276 | 1176 | 348.8 | 228.2 | 223.2 | 181.3 | 229.8 | 239.7
1277 | 1177 | 348.7 | 228.2 | 223.3 | 181.4 | 230 | 239.7
1278 | 1178 | 348.6 | 228.2 | 223.3 | 181.5 | 230.1 | 239.7
1279 | 1179 | 348.5 | 228.3 | 223.4 | 181.6 | 230.2 | 239.7
1280 | 1180 | 348.5 | 228.3 | 223.5 | 181.7 | 230.3 | 239.7
1281 | 1181 | 348.6 | 228.4 | 223.5 | 181.8 | 230 | 239.7
1282 | 1182 | 348.5 | 228.4 | 223.6 | 181.9 | 229.9 | 239.7
1283 | 1183 | 348.4 | 228.5 | 223.7 | 182 | 230 | 239.7
1284 | 1184 | 348.3 | 228.5 | 223.7 | 182.1 | 229.9 | 239.7
1285 | 1185 | 348.1 | 228.6 | 223.8 | 182.2 | 230.2 | 239.7
1286 | 1186 | 348.1 | 228.6 | 223.8 | 182.2 | 230.1 | 239.7
1287 | 1187 | 348.1 | 228.7 | 223.9 | 182.3 | 229.8 | 239.6
1288 | 1188 | 348.1 | 228.7 | 223.9 | 182.4 | 229.7 | 239.5
1289 | 1189 | 348 | 228.7 | 224 | 182.5 | 229.8 | 239.5
1290 | 1190 | 348 | 228.8 | 224 | 182.6 | 229.3 | 239.5
1291 | 1191 | 347.9 | 228.8 | 224 | 182.7 | 229.4 | 239.5
1292 | 1192 | 347.9 | 228.9 | 224.1 | 182.8 | 229.5 | 239.5
1293 | 1193 | 347.9 | 228.9 | 224.1 | 182.9 | 229.3 | 239.5
1294 | 1194 | 347.9 | 229 | 224.2 | 183 | 229.2 | 239.5
1295 | 1195 | 347.8 | 229.1 | 224.2 | 183.1 | 229.1 | 239.5
1296 | 1196 | 347.8 | 229.1 | 224.3 | 183.2 | 229.1 | 239.5
1297 | 1197 | 347.8 | 229.1 | 224.3 | 183.3 | 229.1 | 239.5
1298 | 1198 | 347.8 | 229.2 | 224.4 | 183.4 | 229.2 | 239.5
1299 | 1199 | 347.8 | 229.2 | 224.4 | 183.5 | 229.4 | 239.5
1300 | 1200 | 347.8 | 229.3 | 224.4 | 183.6 | 229.5 | 239.5
1301 | 1201 | 347.8 | 229.3 | 224.5 | 183.7 | 229.7 | 239.5
1302 | 1202 | 347.9 | 229.4 | 224.5 | 183.8 | 229.7 | 239.5
1303 | 1203 | 347.9 | 229.4 | 224.5 | 183.8 | 229.9 | 239.5
1304 | 1204 | 348 | 229.5 | 224.6 | 183.9 | 230.1 | 239.6
1305 | 1205 | 348.1 | 229.5 | 224.6 | 184 | 230 | 239.6
1306 | 1206 | 348.2 | 229.6 | 224.7 | 184.1 | 229.6 | 239.6
1307 | 1207 | 348.3 | 229.6 | 224.7 | 184.2 | 228.8 | 239.6
1308 | 1208 | 348.3 | 229.7 | 224.7 | 184.3 | 228.5 | 239.6
1309 | 1209 | 348.3 | 229.7 | 224.8 | 184.4 | 228.8 | 239.6
1310 | 1210 | 348.2 | 229.8 | 224.8 | 184.5 | 229 | 239.6
1311 | 1211 | 348.3 | 229.8 | 224.9 | 184.6 | 229 | 239.6
1312 | 1212 | 348.5 | 229.9 | 224.9 | 184.7 | 229 | 239.7
1313 | 1213 | 348.6 | 229.9 | 224.9 | 184.8 | 228.6 | 239.7
1314 | 1214 | 348.6 | 229.9 | 225 | 184.9 | 228.2 | 239.8
1315 | 1215 | 348.7 | 230 | 225 | 185 | 228.4 | 239.8
1316 | 1216 | 348.7 | 230 | 225 | 185.1 | 228.5 | 239.8
1317 | 1217 | 348.8 | 230 | 225 | 185.2 | 228.7 | 239.9
1318 | 1218 | 348.9 | 230 | 225.1 | 185.2 | 228.8 | 239.9
1319 | 1219 | 349 | 230 | 225.1 | 185.3 | 228.8 | 239.9
1320 | 1220 | 349.2 | 230.1 | 225.1 | 185.4 | 229.2 | 240
1321 | 1221 | 349.3 | 230.1 | 225.2 | 185.5 | 229.1 | 240
1322 | 1222 | 349.3 | 230.1 | 225.2 | 185.6 | 228.9 | 240.1
1323 | 1223 | 349.4 | 230.1 | 225.2 | 185.7 | 228.6 | 240.1
1324 | 1224 | 349.5 | 230.2 | 225.3 | 185.8 | 228.3 | 240.1
1325 | 1225 | 349.6 | 230.2 | 225.3 | 185.9 | 227.9 | 240.1
1326 | 1226 | 349.7 | 230.3 | 225.3 | 186 | 227.5 | 240.1
1327 | 1227 | 349.8 | 230.3 | 225.4 | 186 | 227.2 | 240.2
1328 | 1228 | 349.9 | 230.4 | 225.4 | 186.1 | 227 | 240.2
1329 | 1229 | 349.9 | 230.4 | 225.4 | 186.2 | 226.7 | 240.3
1330 | 1230 | 349.9 | 230.5 | 225.4 | 186.3 | 226.7 | 240.3
1331 | 1231 | 350 | 230.5 | 225.5 | 186.4 | 226.7 | 240.3
1332 | 1232 | 350.1 | 230.6 | 225.5 | 186.5 | 226.5 | 240.4
1333 | 1233 | 350.1 | 230.6 | 225.5 | 186.6 | 226.9 | 240.3
1334 | 1234 | 350.1 | 230.6 | 225.6 | 186.7 | 227 | 240.3
1335 | 1235 | 350 | 230.6 | 225.6 | 186.8 | 227.3 | 240.3
1336 | 1236 | 349.9 | 230.6 | 225.6 | 186.8 | 228 | 240.4
1337 | 1237 | 349.9 | 230.6 | 225.6 | 186.9 | 228.1 | 240.4
1338 | 1238 | 349.9 | 230.6 | 225.7 | 187 | 227.7 | 240.4
1339 | 1239 | 349.9 | 230.7 | 225.7 | 187.1 | 227.7 | 240.4
1340 | 1240 | 349.9 | 230.7 | 225.7 | 187.2 | 228.3 | 240.3
1341 | 1241 | 349.8 | 230.7 | 225.7 | 187.3 | 228.6 | 240.3
1342 | 1242 | 349.8 | 230.7 | 225.8 | 187.3 | 228.6 | 240.4
1343 | 1243 | 349.7 | 230.8 | 225.8 | 187.4 | 229 | 240.4
1344 | 1244 | 349.7 | 230.8 | 225.8 | 187.5 | 229 | 240.4
1345 | 1245 | 349.7 | 230.9 | 225.8 | 187.6 | 229 | 240.4
1346 | 1246 | 349.6 | 230.9 | 225.8 | 187.7 | 229.3 | 240.4
1347 | 1247 | 349.6 | 231 | 225.8 | 187.8 | 229.7 | 240.4
1348 | 1248 | 349.7 | 231 | 225.8 | 187.9 | 230 | 240.4
1349 | 1249 | 349.6 | 231.1 | 225.8 | 188 | 230.3 | 240.4
1350 | 1250 | 349.5 | 231.1 | 225.8 | 188 | 230.5 | 240.4
1351 | 1251 | 349.5 | 231.2 | 225.8 | 188.1 | 230.6 | 240.4
1352 | 1252 | 349.4 | 231.2 | 225.8 | 188.2 | 230.5 | 240.4
1353 | 1253 | 349.3 | 231.3 | 225.8 | 188.3 | 230.3 | 240.5
1354 | 1254 | 349.2 | 231.3 | 225.7 | 188.4 | 230.5 | 240.5
1355 | 1255 | 349.2 | 231.3 | 225.7 | 188.5 | 230.5 | 240.5
1356 | 1256 | 349.2 | 231.4 | 225.7 | 188.6 | 230.7 | 240.5
1357 | 1257 | 349.3 | 231.4 | 225.7 | 188.6 | 230.8 | 240.5
1358 | 1258 | 349.3 | 231.5 | 225.7 | 188.7 | 231 | 240.5
1359 | 1259 | 349.2 | 231.6 | 225.7 | 188.8 | 231.3 | 240.5
1360 | 1260 | 349.2 | 231.6 | 225.6 | 188.9 | 231.4 | 240.5
1361 | 1261 | 349.2 | 231.6 | 225.6 | 189 | 231.6 | 240.6
1362 | 1262 | 349.2 | 231.7 | 225.6 | 189 | 231.9 | 240.6
1363 | 1263 | 349.3 | 231.7 | 225.6 | 189.1 | 231.9 | 240.6
1364 | 1264 | 349.3 | 231.8 | 225.5 | 189.2 | 232.1 | 240.6
1365 | 1265 | 349.2 | 231.8 | 225.5 | 189.3 | 232.3 | 240.6
1366 | 1266 | 349.2 | 231.9 | 225.5 | 189.4 | 232.2 | 240.6
1367 | 1267 | 349.1 | 232 | 225.5 | 189.5 | 231.9 | 240.6
1368 | 1268 | 349 | 232 | 225.5 | 189.6 | 232.1 | 240.6
1369 | 1269 | 348.9 | 232.1 | 225.4 | 189.6 | 232.4 | 240.6
1370 | 1270 | 348.8 | 232.2 | 225.4 | 189.7 | 232.3 | 240.5
1371 | 1271 | 348.7 | 232.2 | 225.4 | 189.8 | 231.8 | 240.5
1372 | 1272 | 348.5 | 232.3 | 225.4 | 189.9 | 231.4 | 240.6
1373 | 1273 | 348.5 | 232.3 | 225.3 | 190 | 231.7 | 240.6
1374 | 1274 | 348.6 | 232.4 | 225.3 | 190 | 231.8 | 240.6
1375 | 1275 | 348.4 | 232.4 | 225.3 | 190.1 | 232 | 240.6
1376 | 1276 | 348.4 | 232.5 | 225.2 | 190.2 | 232.2 | 240.6
1377 | 1277 | 348.4 | 232.5 | 225.2 | 190.3 | 232.3 | 240.6
1378 | 1278 | 348.4 | 232.6 | 225.2 | 190.4 | 232.1 | 240.6
1379 | 1279 | 348.3 | 232.6 | 225.2 | 190.5 | 232.2 | 240.6
1380 | 1280 | 348.3 | 232.7 | 225.2 | 190.5 | 232.4 | 240.7
1381 | 1281 | 348.3 | 232.7 | 225.1 | 190.6 | 232.6 | 240.7
1382 | 1282 | 348.4 | 232.8 | 225.1 | 190.7 | 232.6 | 240.6
1383 | 1283 | 348.5 | 232.9 | 225.1 | 190.8 | 232.5 | 240.6
1384 | 1284 | 348.6 | 232.9 | 225 | 190.9 | 232.3 | 240.7
1385 | 1285 | 348.7 | 232.9 | 225 | 191 | 232.2 | 240.6
1386 | 1286 | 348.7 | 233 | 225 | 191 | 231.8 | 240.3
1387 | 1287 | 348.7 | 233 | 225 | 191.1 | 232 | 240.3
1388 | 1288 | 348.6 | 233 | 225 | 191.2 | 231.9 | 240.3
1389 | 1289 | 348.6 | 233.1 | 225 | 191.3 | 232 | 240.3
1390 | 1290 | 348.6 | 233.1 | 224.9 | 191.3 | 232.2 | 240.3
1391 | 1291 | 348.7 | 233.2 | 224.9 | 191.4 | 232.3 | 240.3
1392 | 1292 | 348.8 | 233.3 | 224.9 | 191.5 | 232.4 | 240.3
1393 | 1293 | 348.7 | 233.3 | 224.9 | 191.6 | 232.3 | 240.3
1394 | 1294 | 348.7 | 233.4 | 224.9 | 191.7 | 232.3 | 240.4
1395 | 1295 | 348.8 | 233.4 | 224.9 | 191.8 | 232.2 | 240.4
1396 | 1296 | 349 | 233.5 | 224.8 | 191.8 | 232.1 | 240.4
1397 | 1297 | 349.1 | 233.5 | 224.8 | 191.9 | 231.9 | 240.4
1398 | 1298 | 349.2 | 233.6 | 224.8 | 192 | 232.2 | 240.4
1399 | 1299 | 349.2 | 233.6 | 224.8 | 192.1 | 232.3 | 240.4
1400 | 1300 | 349.3 | 233.6 | 224.8 | 192.2 | 232 | 240.4
1401 | 1301 | 349.4 | 233.6 | 224.8 | 192.2 | 231.5 | 240.4
1402 | 1302 | 349.6 | 233.6 | 224.8 | 192.3 | 231.5 | 240.4
1403 | 1303 | 349.7 | 233.6 | 224.8 | 192.4 | 231.3 | 240.4
1404 | 1304 | 349.7 | 233.6 | 224.8 | 192.5 | 231.2 | 240.4
1405 | 1305 | 349.6 | 233.7 | 224.8 | 192.6 | 231.2 | 240.5
1406 | 1306 | 349.7 | 233.7 | 224.8 | 192.6 | 231 | 240.5
1407 | 1307 | 349.8 | 233.7 | 224.8 | 192.7 | 231.1 | 240.5
1408 | 1308 | 349.9 | 233.8 | 224.8 | 192.8 | 231.2 | 240.5
1409 | 1309 | 350 | 233.9 | 224.9 | 192.9 | 231 | 240.5
1410 | 1310 | 350 | 233.9 | 224.9 | 193 | 231.2 | 240.6
1411 | 1311 | 350.1 | 234 | 224.9 | 193 | 230.6 | 240.6
1412 | 1312 | 350.2 | 234 | 224.9 | 193.1 | 230.7 | 240.6
1413 | 1313 | 350.3 | 234.1 | 224.9 | 193.2 | 231.2 | 240.6
1414 | 1314 | 350.2 | 234.2 | 224.9 | 193.3 | 231.1 | 240.6
1415 | 1315 | 350.2 | 234.2 | 225 | 193.4 | 231.2 | 240.6
1416 | 1316 | 350.3 | 234.3 | 225 | 193.4 | 231.4 | 240.6
1417 | 1317 | 350.4 | 234.3 | 225 | 193.5 | 231.8 | 240.6
1418 | 1318 | 350.5 | 234.4 | 225.1 | 193.6 | 232 | 240.6
1419 | 1319 | 350.3 | 234.4 | 225.1 | 193.7 | 232.2 | 240.7
1420 | 1320 | 350.2 | 234.5 | 225.1 | 193.8 | 232.2 | 240.6
1421 | 1321 | 350.1 | 234.6 | 225.2 | 193.8 | 232.2 | 240.6
1422 | 1322 | 350 | 234.7 | 225.2 | 193.9 | 232.3 | 240.6
1423 | 1323 | 349.8 | 234.7 | 225.2 | 194 | 232.2 | 240.6
1424 | 1324 | 349.6 | 234.8 | 225.3 | 194.1 | 232.3 | 240.6
1425 | 1325 | 349.4 | 234.9 | 225.3 | 194.2 | 232.8 | 240.6
1426 | 1326 | 349.3 | 234.9 | 225.3 | 194.2 | 233 | 240.6
1427 | 1327 | 349.2 | 235 | 225.4 | 194.3 | 232.9 | 240.6
1428 | 1328 | 349.1 | 235.1 | 225.4 | 194.4 | 233.1 | 240.6
1429 | 1329 | 349 | 235.2 | 225.5 | 194.5 | 233.2 | 240.6
1430 | 1330 | 349 | 235.2 | 225.5 | 194.5 | 232.9 | 240.7
1431 | 1331 | 348.9 | 235.3 | 225.5 | 194.6 | 232.8 | 240.7
1432 | 1332 | 348.9 | 235.3 | 225.6 | 194.7 | 232.6 | 240.7
1433 | 1333 | 348.8 | 235.4 | 225.6 | 194.8 | 232.4 | 240.7
1434 | 1334 | 348.7 | 235.4 | 225.6 | 194.9 | 232.3 | 240.7
1435 | 1335 | 348.6 | 235.5 | 225.7 | 194.9 | 232.6 | 240.6
1436 | 1336 | 348.5 | 235.5 | 225.7 | 195 | 232.8 | 240.6
1437 | 1337 | 348.5 | 235.6 | 225.7 | 195.1 | 232.8 | 240.6
1438 | 1338 | 348.5 | 235.6 | 225.8 | 195.2 | 232.6 | 240.6
1439 | 1339 | 348.6 | 235.7 | 225.8 | 195.2 | 232.5 | 240.7
1440 | 1340 | 348.6 | 235.7 | 225.8 | 195.3 | 232.3 | 240.7
1441 | 1341 | 348.5 | 235.8 | 225.8 | 195.4 | 232.5 | 240.7
1442 | 1342 | 348.5 | 235.8 | 225.9 | 195.5 | 232.7 | 240.7
1443 | 1343 | 348.6 | 235.9 | 225.9 | 195.5 | 232.8 | 240.7
1444 | 1344 | 348.7 | 236 | 225.9 | 195.6 | 232.8 | 240.7
1445 | 1345 | 348.8 | 236 | 226 | 195.7 | 232.7 | 240.7
1446 | 1346 | 348.9 | 236.1 | 226 | 195.8 | 232.6 | 240.8
1447 | 1347 | 349 | 236.2 | 226 | 195.8 | 233.2 | 240.8
1448 | 1348 | 349.1 | 236.3 | 226 | 195.9 | 233.6 | 240.8
1449 | 1349 | 349.4 | 236.4 | 226.1 | 196 | 233.5 | 240.8
1450 | 1350 | 349.5 | 236.5 | 226.1 | 196.1 | 233.1 | 240.8
1451 | 1351 | 349.5 | 236.5 | 226.1 | 196.2 | 232.9 | 240.9
1452 | 1352 | 349.7 | 236.6 | 226.1 | 196.2 | 232.6 | 240.9
1453 | 1353 | 349.8 | 236.7 | 226.2 | 196.3 | 232.3 | 240.9
1454 | 1354 | 349.8 | 236.8 | 226.2 | 196.4 | 232.6 | 240.9
1455 | 1355 | 349.8 | 236.9 | 226.3 | 196.4 | 233 | 241
1456 | 1356 | 350 | 237 | 226.3 | 196.5 | 232.6 | 241
1457 | 1357 | 350 | 237.1 | 226.3 | 196.6 | 232.7 | 241
1458 | 1358 | 350.2 | 237.1 | 226.3 | 196.7 | 232.8 | 241.1
1459 | 1359 | 350.3 | 237.2 | 226.4 | 196.7 | 232.6 | 241.1
1460 | 1360 | 350.4 | 237.3 | 226.4 | 196.8 | 232 | 241.1
1461 | 1361 | 350.4 | 237.4 | 226.4 | 196.9 | 231.6 | 241.2
1462 | 1362 | 350.3 | 237.5 | 226.5 | 197 | 231.4 | 241.2
1463 | 1363 | 350.2 | 237.5 | 226.5 | 197 | 231 | 241.2
1464 | 1364 | 350.2 | 237.6 | 226.5 | 197.1 | 230.8 | 241.2
1465 | 1365 | 350.2 | 237.7 | 226.5 | 197.2 | 230.3 | 241.2
1466 | 1366 | 350.2 | 237.8 | 226.6 | 197.2 | 229.9 | 241.2
1467 | 1367 | 350.2 | 237.8 | 226.6 | 197.3 | 229.5 | 241.2
1468 | 1368 | 350.3 | 237.9 | 226.7 | 197.4 | 230 | 241.1
1469 | 1369 | 350.4 | 238 | 226.7 | 197.5 | 230.4 | 241.1
1470 | 1370 | 350.4 | 238 | 226.7 | 197.5 | 230.6 | 241.1
1471 | 1371 | 350.3 | 238 | 226.7 | 197.6 | 231.1 | 241.1
1472 | 1372 | 350.3 | 238.1 | 226.8 | 197.7 | 231.6 | 241.1
1473 | 1373 | 350.3 | 238.2 | 226.8 | 197.8 | 232.3 | 241.1
1474 | 1374 | 350.3 | 238.2 | 226.9 | 197.8 | 232.4 | 241
1475 | 1375 | 350.2 | 238.3 | 226.9 | 197.9 | 232.9 | 241
1476 | 1376 | 350.3 | 238.4 | 226.9 | 198 | 233.2 | 241
1477 | 1377 | 350.3 | 238.5 | 227 | 198 | 233.1 | 241
1478 | 1378 | 350.4 | 238.6 | 227 | 198.1 | 233.1 | 241
1479 | 1379 | 350.4 | 238.6 | 227 | 198.2 | 233.3 | 241
1480 | 1380 | 350.5 | 238.7 | 227.1 | 198.3 | 233.3 | 241
1481 | 1381 | 350.6 | 238.8 | 227.1 | 198.3 | 233.1 | 241
1482 | 1382 | 350.6 | 238.9 | 227.1 | 198.4 | 233 | 241
1483 | 1383 | 350.6 | 239 | 227.2 | 198.5 | 233.2 | 241
1484 | 1384 | 350.6 | 239.1 | 227.2 | 198.5 | 233.3 | 241
1485 | 1385 | 350.6 | 239.1 | 227.2 | 198.6 | 233.2 | 241
1486 | 1386 | 350.6 | 239.2 | 227.2 | 198.7 | 232.8 | 240.9
1487 | 1387 | 350.5 | 239.2 | 227.3 | 198.7 | 232.5 | 240.9
1488 | 1388 | 350.5 | 239.3 | 227.3 | 198.8 | 232 | 240.9
1489 | 1389 | 350.5 | 239.4 | 227.3 | 198.9 | 231.8 | 240.9
1490 | 1390 | 350.5 | 239.5 | 227.4 | 199 | 231.5 | 240.9
1491 | 1391 | 350.4 | 239.5 | 227.4 | 199 | 231.2 | 240.9
1492 | 1392 | 350.3 | 239.6 | 227.4 | 199.1 | 231 | 241
1493 | 1393 | 350.2 | 239.6 | 227.4 | 199.2 | 231 | 241
1494 | 1394 | 350.2 | 239.7 | 227.5 | 199.2 | 230.7 | 241
1495 | 1395 | 350.3 | 239.7 | 227.5 | 199.3 | 230.3 | 241
1496 | 1396 | 350.3 | 239.8 | 227.5 | 199.4 | 230.8 | 241
1497 | 1397 | 350.2 | 239.9 | 227.6 | 199.5 | 231.1 | 241
1498 | 1398 | 350.1 | 240 | 227.6 | 199.5 | 231.3 | 241
1499 | 1399 | 350 | 240 | 227.6 | 199.6 | 230.9 | 241.1
1500 | 1400 | 349.8 | 240.1 | 227.6 | 199.7 | 230.3 | 241
1501 | 1401 | 349.7 | 240.2 | 227.7 | 199.7 | 230.1 | 241
1502 | 1402 | 349.6 | 240.3 | 227.7 | 199.8 | 230 | 241
1503 | 1403 | 349.6 | 240.4 | 227.7 | 199.9 | 229.7 | 241
1504 | 1404 | 349.4 | 240.4 | 227.8 | 199.9 | 229.3 | 241
1505 | 1405 | 349.4 | 240.4 | 227.8 | 200 | 229.3 | 241
1506 | 1406 | 349.2 | 240.5 | 227.9 | 200.1 | 229.1 | 241
1507 | 1407 | 349.1 | 240.6 | 227.9 | 200.1 | 228.7 | 241
1508 | 1408 | 349 | 240.6 | 227.9 | 200.2 | 228.7 | 241
1509 | 1409 | 349 | 240.7 | 228 | 200.3 | 228.3 | 241
1510 | 1410 | 349 | 240.8 | 228 | 200.3 | 228.3 | 241
1511 | 1411 | 349 | 240.8 | 228 | 200.4 | 228.6 | 241
1512 | 1412 | 349 | 240.9 | 228.1 | 200.5 | 228.9 | 241
1513 | 1413 | 349.1 | 241 | 228.1 | 200.6 | 229 | 241
1514 | 1414 | 349 | 241 | 228.2 | 200.6 | 229.1 | 240.9
1515 | 1415 | 348.9 | 241.1 | 228.2 | 200.7 | 228.9 | 240.9
1516 | 1416 | 348.8 | 241.1 | 228.3 | 200.8 | 228.8 | 240.9
1517 | 1417 | 348.7 | 241.1 | 228.3 | 200.8 | 228.9 | 240.9
1518 | 1418 | 348.7 | 241.2 | 228.3 | 200.9 | 228.5 | 240.9
1519 | 1419 | 348.7 | 241.2 | 228.4 | 201 | 228.6 | 240.9
1520 | 1420 | 348.8 | 241.2 | 228.4 | 201 | 229 | 240.9
1521 | 1421 | 348.8 | 241.2 | 228.4 | 201.1 | 229 | 240.9
1522 | 1422 | 348.8 | 241.2 | 228.5 | 201.2 | 228.6 | 241
1523 | 1423 | 348.8 | 241.2 | 228.5 | 201.2 | 228.4 | 240.9
1524 | 1424 | 348.8 | 241.3 | 228.6 | 201.3 | 228.5 | 241
1525 | 1425 | 348.9 | 241.3 | 228.6 | 201.4 | 228.6 | 240.9
1526 | 1426 | 349.1 | 241.4 | 228.6 | 201.4 | 228.4 | 240.9
1527 | 1427 | 349.2 | 241.4 | 228.7 | 201.5 | 228.8 | 240.9
1528 | 1428 | 349.4 | 241.5 | 228.7 | 201.6 | 228.8 | 240.9
1529 | 1429 | 349.6 | 241.5 | 228.7 | 201.6 | 228.6 | 240.9
1530 | 1430 | 349.7 | 241.5 | 228.8 | 201.7 | 228.4 | 240.9
1531 | 1431 | 349.9 | 241.5 | 228.8 | 201.8 | 228.1 | 240.9
1532 | 1432 | 350.2 | 241.6 | 228.8 | 201.8 | 227.9 | 240.9
1533 | 1433 | 350.3 | 241.6 | 228.8 | 201.9 | 228.2 | 240.9
1534 | 1434 | 350.2 | 241.6 | 228.9 | 202 | 228.4 | 241
1535 | 1435 | 350.1 | 241.6 | 228.9 | 202 | 228.4 | 241
1536 | 1436 | 350.1 | 241.6 | 229 | 202.1 | 228.1 | 241
1537 | 1437 | 350.3 | 241.6 | 229 | 202.2 | 227.7 | 241
1538 | 1438 | 350.3 | 241.6 | 229 | 202.2 | 227.2 | 241
1539 | 1439 | 350.2 | 241.7 | 229 | 202.3 | 227.4 | 241
1540 | 1440 | 350.2 | 241.7 | 229.1 | 202.4 | 227.3 | 241
1541 | 1441 | 350.4 | 241.8 | 229.1 | 202.4 | 226.8 | 241.1
1542 | 1442 | 350.5 | 241.8 | 229.1 | 202.5 | 226.7 | 241.1
1543 | 1443 | 350.7 | 241.9 | 229.1 | 202.6 | 226.6 | 241.1
1544 | 1444 | 350.7 | 242 | 229.2 | 202.6 | 226.7 | 241.1
1545 | 1445 | 350.6 | 242 | 229.2 | 202.7 | 226.9 | 241.1
1546 | 1446 | 350.5 | 242.1 | 229.2 | 202.8 | 227 | 241.1
1547 | 1447 | 350.4 | 242.1 | 229.3 | 202.8 | 227.2 | 241.1
1548 | 1448 | 350.5 | 242.2 | 229.3 | 202.9 | 227.2 | 241.1
1549 | 1449 | 350.5 | 242.2 | 229.3 | 203 | 227.1 | 241.1
1550 | 1450 | 350.5 | 242.3 | 229.4 | 203 | 227.1 | 241.1
1551 | 1451 | 350.3 | 242.3 | 229.4 | 203.1 | 227 | 241.1
1552 | 1452 | 350.1 | 242.4 | 229.4 | 203.2 | 226.9 | 241.1
1553 | 1453 | 350 | 242.4 | 229.5 | 203.2 | 226.9 | 241.1
1554 | 1454 | 349.9 | 242.5 | 229.5 | 203.3 | 226.7 | 241.1
1555 | 1455 | 349.9 | 242.5 | 229.5 | 203.4 | 226.5 | 241
1556 | 1456 | 349.8 | 242.6 | 229.6 | 203.4 | 226.9 | 241
1557 | 1457 | 349.6 | 242.6 | 229.6 | 203.5 | 226.8 | 241
1558 | 1458 | 349.5 | 242.7 | 229.7 | 203.5 | 226.8 | 241
1559 | 1459 | 349.3 | 242.7 | 229.7 | 203.6 | 226.6 | 241.1
1560 | 1460 | 349.1 | 242.8 | 229.7 | 203.7 | 226.6 | 241.1
1561 | 1461 | 349 | 242.8 | 229.8 | 203.7 | 226.6 | 241.1
1562 | 1462 | 348.7 | 242.9 | 229.8 | 203.8 | 227.2 | 241
1563 | 1463 | 348.5 | 242.9 | 229.9 | 203.9 | 226.8 | 241
1564 | 1464 | 348.4 | 243 | 229.9 | 203.9 | 226.5 | 241
1565 | 1465 | 348.3 | 243 | 230 | 204 | 226.6 | 241
1566 | 1466 | 348.1 | 243 | 230 | 204.1 | 226.6 | 241
1567 | 1467 | 348.1 | 243.1 | 230.1 | 204.1 | 226.5 | 241
1568 | 1468 | 348.1 | 243.1 | 230.1 | 204.2 | 226.4 | 240.9
1569 | 1469 | 348.1 | 243.1 | 230.1 | 204.2 | 226.1 | 240.9
1570 | 1470 | 348.2 | 243.1 | 230.2 | 204.3 | 225.7 | 240.9
1571 | 1471 | 348.2 | 243.1 | 230.3 | 204.4 | 225.9 | 240.9
1572 | 1472 | 348.2 | 243.1 | 230.3 | 204.4 | 226.4 | 240.9
1573 | 1473 | 348.1 | 243.1 | 230.3 | 204.5 | 226.8 | 240.9
1574 | 1474 | 348.2 | 243.1 | 230.4 | 204.6 | 226.6 | 240.9
1575 | 1475 | 348.4 | 243.1 | 230.4 | 204.6 | 226.3 | 240.9
1576 | 1476 | 348.5 | 243.1 | 230.5 | 204.7 | 226.4 | 240.9
1577 | 1477 | 348.5 | 243.2 | 230.5 | 204.8 | 226.1 | 240.9
1578 | 1478 | 348.4 | 243.2 | 230.6 | 204.8 | 226 | 240.9
1579 | 1479 | 348.3 | 243.3 | 230.6 | 204.9 | 226.1 | 240.9
1580 | 1480 | 348.3 | 243.3 | 230.7 | 204.9 | 226.2 | 240.9
1581 | 1481 | 348.4 | 243.3 | 230.7 | 205 | 226.6 | 240.9
1582 | 1482 | 348.5 | 243.4 | 230.8 | 205.1 | 226.2 | 240.9
1583 | 1483 | 348.6 | 243.4 | 230.8 | 205.1 | 226.2 | 240.8
1584 | 1484 | 348.7 | 243.4 | 230.9 | 205.2 | 226.3 | 240.8
1585 | 1485 | 348.8 | 243.5 | 230.9 | 205.2 | 226.3 | 240.8
1586 | 1486 | 348.8 | 243.5 | 231 | 205.3 | 226.3 | 240.8
1587 | 1487 | 348.8 | 243.5 | 231 | 205.4 | 226.9 | 240.8
1588 | 1488 | 348.8 | 243.5 | 231.1 | 205.4 | 226.7 | 240.8
1589 | 1489 | 348.8 | 243.5 | 231.1 | 205.5 | 226.8 | 240.8
1590 | 1490 | 348.8 | 243.5 | 231.2 | 205.5 | 226.9 | 240.8
1591 | 1491 | 348.8 | 243.6 | 231.2 | 205.6 | 226.7 | 240.8
1592 | 1492 | 348.8 | 243.6 | 231.3 | 205.7 | 226.8 | 240.9
1593 | 1493 | 348.8 | 243.6 | 231.3 | 205.7 | 226.7 | 240.9
1594 | 1494 | 348.9 | 243.6 | 231.4 | 205.8 | 227.2 | 240.7
1595 | 1495 | 348.9 | 243.7 | 231.4 | 205.8 | 227.6 | 240.7
1596 | 1496 | 348.9 | 243.7 | 231.5 | 205.9 | 227.8 | 240.7
1597 | 1497 | 348.9 | 243.8 | 231.5 | 205.9 | 228.2 | 240.7
1598 | 1498 | 348.9 | 243.8 | 231.6 | 206 | 228.1 | 240.7
1599 | 1499 | 348.9 | 243.9 | 231.6 | 206.1 | 227.9 | 240.7
1600 | 1500 | 348.8 | 244 | 231.7 | 206.1 | 227.7 | 240.7
1601 | 1501 | 348.8 | 244 | 231.7 | 206.2 | 227.8 | 240.7
1602 | 1502 | 348.8 | 244.1 | 231.8 | 206.2 | 227.7 | 240.7
1603 | 1503 | 348.8 | 244.2 | 231.8 | 206.3 | 227.6 | 240.6
1604 | 1504 | 348.8 | 244.2 | 231.8 | 206.4 | 227.8 | 240.6
1605 | 1505 | 348.7 | 244.3 | 231.9 | 206.4 | 227.9 | 240.6
1606 | 1506 | 348.8 | 244.4 | 231.9 | 206.5 | 228.2 | 240.6
1607 | 1507 | 348.8 | 244.4 | 232 | 206.5 | 228 | 240.6
1608 | 1508 | 348.8 | 244.4 | 232 | 206.6 | 227.9 | 240.6
1609 | 1509 | 348.8 | 244.5 | 232 | 206.6 | 227.9 | 240.6
1610 | 1510 | 348.8 | 244.5 | 232.1 | 206.7 | 228.1 | 240.6
1611 | 1511 | 348.8 | 244.5 | 232.1 | 206.8 | 228.4 | 240.6
1612 | 1512 | 348.8 | 244.6 | 232.2 | 206.8 | 228.4 | 240.5
1613 | 1513 | 348.9 | 244.6 | 232.2 | 206.9 | 228.3 | 240.5
1614 | 1514 | 349 | 244.6 | 232.2 | 206.9 | 227.9 | 240.6
1615 | 1515 | 349 | 244.7 | 232.3 | 207 | 228.3 | 240.6
1616 | 1516 | 349 | 244.7 | 232.3 | 207.1 | 228.1 | 240.6
1617 | 1517 | 349.2 | 244.8 | 232.3 | 207.1 | 227.9 | 240.6
1618 | 1518 | 349.4 | 244.9 | 232.4 | 207.2 | 227.7 | 240.6
1619 | 1519 | 349.6 | 244.9 | 232.4 | 207.2 | 227.6 | 240.6
1620 | 1520 | 349.6 | 245 | 232.5 | 207.3 | 227.5 | 240.6
1621 | 1521 | 349.6 | 245 | 232.5 | 207.3 | 227.3 | 240.6
1622 | 1522 | 349.6 | 245.1 | 232.5 | 207.4 | 227.3 | 240.6
1623 | 1523 | 349.7 | 245.2 | 232.6 | 207.4 | 227.5 | 240.6
1624 | 1524 | 349.7 | 245.2 | 232.6 | 207.5 | 227.7 | 240.6
1625 | 1525 | 349.9 | 245.2 | 232.6 | 207.6 | 228 | 240.6
1626 | 1526 | 350 | 245.3 | 232.7 | 207.6 | 228 | 240.6
1627 | 1527 | 350.2 | 245.4 | 232.7 | 207.7 | 228.3 | 240.5
1628 | 1528 | 350.4 | 245.4 | 232.8 | 207.7 | 228.6 | 240.4
1629 | 1529 | 350.5 | 245.5 | 232.8 | 207.8 | 228.6 | 240.4
1630 | 1530 | 350.5 | 245.6 | 232.9 | 207.8 | 228.8 | 240.5
1631 | 1531 | 350.5 | 245.6 | 232.9 | 207.9 | 229.1 | 240.5
1632 | 1532 | 350.5 | 245.7 | 232.9 | 207.9 | 229.1 | 240.5
1633 | 1533 | 350.5 | 245.7 | 233 | 208 | 228.9 | 240.5
1634 | 1534 | 350.5 | 245.8 | 233 | 208.1 | 228.9 | 240.5
1635 | 1535 | 350.4 | 245.9 | 233 | 208.1 | 229.6 | 240.5
1636 | 1536 | 350.3 | 245.9 | 233.1 | 208.2 | 230 | 240.5
1637 | 1537 | 350.2 | 246 | 233.1 | 208.2 | 230.3 | 240.5
1638 | 1538 | 350 | 246.1 | 233.1 | 208.3 | 229.8 | 240.5
1639 | 1539 | 350 | 246.2 | 233.2 | 208.3 | 229.2 | 240.5
1640 | 1540 | 349.9 | 246.3 | 233.2 | 208.4 | 229.3 | 240.5
1641 | 1541 | 349.8 | 246.4 | 233.2 | 208.4 | 229 | 240.5
1642 | 1542 | 349.7 | 246.5 | 233.2 | 208.5 | 228.4 | 240.5
1643 | 1543 | 349.7 | 246.5 | 233.3 | 208.6 | 228.6 | 240.5
1644 | 1544 | 349.5 | 246.6 | 233.3 | 208.6 | 228.4 | 240.4
1645 | 1545 | 349.3 | 246.7 | 233.3 | 208.7 | 227.9 | 240.5
1646 | 1546 | 349.2 | 246.8 | 233.4 | 208.7 | 227.3 | 240.4
1647 | 1547 | 349 | 246.9 | 233.4 | 208.8 | 226.9 | 240.4
1648 | 1548 | 348.9 | 247 | 233.4 | 208.8 | 226.6 | 240.4
1649 | 1549 | 348.8 | 247.1 | 233.4 | 208.9 | 226.9 | 240.4
1650 | 1550 | 348.6 | 247.2 | 233.5 | 208.9 | 227.1 | 240.4
1651 | 1551 | 348.5 | 247.2 | 233.5 | 209 | 226.9 | 240.5
1652 | 1552 | 348.5 | 247.3 | 233.5 | 209 | 226.6 | 240.4
1653 | 1553 | 348.6 | 247.4 | 233.6 | 209.1 | 226.7 | 240.4
1654 | 1554 | 348.7 | 247.4 | 233.6 | 209.2 | 226.5 | 240.3
1655 | 1555 | 348.9 | 247.5 | 233.6 | 209.2 | 226.3 | 240.3
1656 | 1556 | 349 | 247.5 | 233.7 | 209.3 | 225.6 | 240.3
1657 | 1557 | 349.1 | 247.6 | 233.7 | 209.3 | 225.7 | 240.4
1658 | 1558 | 349 | 247.6 | 233.7 | 209.4 | 225.8 | 240.4
1659 | 1559 | 349 | 247.6 | 233.7 | 209.4 | 225.7 | 240.3
1660 | 1560 | 348.9 | 247.7 | 233.7 | 209.5 | 225.5 | 240.3
1661 | 1561 | 348.8 | 247.7 | 233.8 | 209.5 | 225.5 | 240.3
1662 | 1562 | 348.7 | 247.7 | 233.8 | 209.6 | 225.8 | 240.3
1663 | 1563 | 348.7 | 247.7 | 233.8 | 209.6 | 226.1 | 240.3
1664 | 1564 | 348.8 | 247.8 | 233.8 | 209.7 | 225.9 | 240.3
1665 | 1565 | 348.7 | 247.8 | 233.9 | 209.7 | 226.3 | 240.3
1666 | 1566 | 348.7 | 247.8 | 233.9 | 209.8 | 226.4 | 240.2
1667 | 1567 | 348.8 | 247.8 | 233.9 | 209.8 | 226.6 | 240.2
1668 | 1568 | 348.8 | 247.8 | 233.9 | 209.9 | 226.6 | 240.2
1669 | 1569 | 348.8 | 247.8 | 233.9 | 209.9 | 226.6 | 240.2
1670 | 1570 | 348.8 | 247.9 | 234 | 210 | 226.4 | 240.2
1671 | 1571 | 348.7 | 247.9 | 234 | 210.1 | 226.8 | 240.2
1672 | 1572 | 348.6 | 247.9 | 234 | 210.1 | 226.7 | 240.2
1673 | 1573 | 348.5 | 248 | 234 | 210.2 | 227.1 | 240.2
1674 | 1574 | 348.5 | 248 | 234 | 210.2 | 227.5 | 240.2
1675 | 1575 | 348.4 | 248 | 234.1 | 210.3 | 227.1 | 240.2
1676 | 1576 | 348.4 | 248.1 | 234.1 | 210.3 | 227.4 | 240.2
1677 | 1577 | 348.3 | 248.1 | 234.1 | 210.4 | 227.5 | 240.2
1678 | 1578 | 348.3 | 248.2 | 234.1 | 210.4 | 227.4 | 240.2
1679 | 1579 | 348.2 | 248.2 | 234.1 | 210.5 | 227.8 | 240.2
1680 | 1580 | 348.3 | 248.3 | 234.2 | 210.5 | 227.8 | 240.2
1681 | 1581 | 348.3 | 248.4 | 234.2 | 210.6 | 228.2 | 240.2
1682 | 1582 | 348.1 | 248.5 | 234.2 | 210.6 | 228.4 | 240.2
1683 | 1583 | 348.2 | 248.6 | 234.2 | 210.7 | 228.8 | 240.2
1684 | 1584 | 348.3 | 248.6 | 234.3 | 210.7 | 229.3 | 240.1
1685 | 1585 | 348.4 | 248.7 | 234.3 | 210.8 | 229.7 | 240.1
1686 | 1586 | 348.4 | 248.8 | 234.3 | 210.8 | 229.7 | 240.1
1687 | 1587 | 348.4 | 248.9 | 234.3 | 210.9 | 230.1 | 240.1
1688 | 1588 | 348.4 | 249 | 234.3 | 210.9 | 230.2 | 240.1
1689 | 1589 | 348.4 | 249 | 234.4 | 211 | 230.3 | 240.1
1690 | 1590 | 348.5 | 249.1 | 234.4 | 211 | 230.6 | 240.1
1691 | 1591 | 348.4 | 249.2 | 234.4 | 211.1 | 230.4 | 240.1
1692 | 1592 | 348.4 | 249.2 | 234.5 | 211.1 | 230.4 | 240.1
1693 | 1593 | 348.5 | 249.2 | 234.5 | 211.2 | 230.4 | 240.1
1694 | 1594 | 348.7 | 249.3 | 234.5 | 211.2 | 230.8 | 240.1
1695 | 1595 | 348.8 | 249.3 | 234.6 | 211.3 | 231.1 | 240.1
1696 | 1596 | 348.9 | 249.3 | 234.6 | 211.3 | 231.5 | 240.1
1697 | 1597 | 349 | 249.4 | 234.6 | 211.4 | 231.8 | 240.1
1698 | 1598 | 349 | 249.4 | 234.7 | 211.4 | 231.6 | 240.1
1699 | 1599 | 349.1 | 249.5 | 234.7 | 211.5 | 231.4 | 240.1
1700 | 1600 | 349.2 | 249.6 | 234.8 | 211.5 | 231.3 | 240.1
1701 | 1601 | 349.3 | 249.6 | 234.8 | 211.6 | 231.4 | 240.1
1702 | 1602 | 349.4 | 249.7 | 234.8 | 211.6 | 231.3 | 240.1
1703 | 1603 | 349.6 | 249.8 | 234.9 | 211.7 | 231.7 | 240.1
1704 | 1604 | 349.8 | 249.8 | 234.9 | 211.7 | 231.8 | 240.1
1705 | 1605 | 350 | 249.9 | 235 | 211.8 | 231.5 | 240.1
1706 | 1606 | 350.2 | 249.9 | 235 | 211.8 | 231.4 | 240.1
1707 | 1607 | 350.4 | 249.9 | 235 | 211.9 | 231.5 | 240.1
1708 | 1608 | 350.4 | 249.9 | 235.1 | 211.9 | 231.9 | 240.1
1709 | 1609 | 350.4 | 250 | 235.1 | 212 | 232.1 | 240.1
1710 | 1610 | 350.4 | 250 | 235.1 | 212 | 232.4 | 240.1
1711 | 1611 | 350.5 | 250 | 235.2 | 212.1 | 232.2 | 240.1
1712 | 1612 | 350.5 | 250.1 | 235.2 | 212.1 | 232.2 | 240.1
1713 | 1613 | 350.5 | 250.1 | 235.2 | 212.1 | 232.2 | 240.1
1714 | 1614 | 350.5 | 250.2 | 235.3 | 212.2 | 231.7 | 240.1
1715 | 1615 | 350.7 | 250.3 | 235.3 | 212.2 | 231.6 | 240.2
1716 | 1616 | 350.8 | 250.3 | 235.4 | 212.3 | 231.4 | 240.2
1717 | 1617 | 350.8 | 250.4 | 235.4 | 212.3 | 231.4 | 240.2
1718 | 1618 | 350.8 | 250.5 | 235.4 | 212.4 | 231.2 | 240.2
1719 | 1619 | 350.8 | 250.6 | 235.5 | 212.4 | 230.9 | 240.2
1720 | 1620 | 350.6 | 250.7 | 235.6 | 212.5 | 230.7 | 240.2
1721 | 1621 | 350.5 | 250.8 | 235.6 | 212.5 | 230.5 | 240.2
1722 | 1622 | 350.4 | 250.9 | 235.7 | 212.6 | 229.9 | 240.2
1723 | 1623 | 350.3 | 251 | 235.7 | 212.6 | 229.5 | 240.2
1724 | 1624 | 350.3 | 251.1 | 235.7 | 212.6 | 229.5 | 240.2
1725 | 1625 | 350.2 | 251.2 | 235.8 | 212.7 | 229.6 | 240.2
1726 | 1626 | 349.9 | 251.2 | 235.9 | 212.7 | 229.2 | 240.2
1727 | 1627 | 349.7 | 251.3 | 235.9 | 212.8 | 229.2 | 240.1
1728 | 1628 | 349.6 | 251.3 | 236 | 212.8 | 229.2 | 240.2
1729 | 1629 | 349.5 | 251.4 | 236 | 212.9 | 229.3 | 240.1
1730 | 1630 | 349.4 | 251.4 | 236 | 212.9 | 229.3 | 240.1
1731 | 1631 | 349.3 | 251.4 | 236.1 | 213 | 229.4 | 240.1
1732 | 1632 | 349.1 | 251.5 | 236.2 | 213 | 229.3 | 240.1
1733 | 1633 | 348.9 | 251.6 | 236.2 | 213.1 | 229.4 | 240.1
1734 | 1634 | 348.8 | 251.6 | 236.3 | 213.1 | 229.8 | 240.1
1735 | 1635 | 348.6 | 251.7 | 236.3 | 213.1 | 230.1 | 240.1
1736 | 1636 | 348.6 | 251.8 | 236.4 | 213.2 | 230.2 | 240.1
1737 | 1637 | 348.5 | 251.9 | 236.4 | 213.2 | 230.2 | 240
1738 | 1638 | 348.5 | 251.9 | 236.5 | 213.3 | 230.3 | 240
1739 | 1639 | 348.5 | 252 | 236.5 | 213.3 | 230.3 | 240
1740 | 1640 | 348.4 | 252.1 | 236.6 | 213.4 | 230 | 240
1741 | 1641 | 348.4 | 252.1 | 236.7 | 213.4 | 230.6 | 240
1742 | 1642 | 348.5 | 252.2 | 236.7 | 213.4 | 230.5 | 239.8
1743 | 1643 | 348.5 | 252.2 | 236.8 | 213.5 | 230.9 | 239.8
1744 | 1644 | 348.6 | 252.3 | 236.8 | 213.5 | 230.8 | 239.8
1745 | 1645 | 348.7 | 252.3 | 236.9 | 213.6 | 230.3 | 239.8
1746 | 1646 | 348.9 | 252.4 | 236.9 | 213.6 | 229.9 | 239.8
1747 | 1647 | 349.1 | 252.4 | 237 | 213.6 | 229.8 | 239.9
1748 | 1648 | 349.2 | 252.4 | 237.1 | 213.7 | 230 | 239.9
1749 | 1649 | 349.2 | 252.4 | 237.1 | 213.7 | 230.4 | 239.9
1750 | 1650 | 349.2 | 252.5 | 237.2 | 213.8 | 230.3 | 239.9
1751 | 1651 | 349.4 | 252.5 | 237.2 | 213.8 | 230.6 | 239.9
1752 | 1652 | 349.5 | 252.5 | 237.3 | 213.9 | 230.6 | 239.9
1753 | 1653 | 349.6 | 252.6 | 237.3 | 213.9 | 230.8 | 239.9
1754 | 1654 | 349.7 | 252.6 | 237.4 | 214 | 230.9 | 239.9
1755 | 1655 | 349.7 | 252.6 | 237.5 | 214 | 230.6 | 239.9
1756 | 1656 | 349.9 | 252.7 | 237.5 | 214 | 230.3 | 240
1757 | 1657 | 349.9 | 252.7 | 237.6 | 214.1 | 229.7 | 240
1758 | 1658 | 350 | 252.7 | 237.6 | 214.1 | 229.2 | 240
1759 | 1659 | 350.2 | 252.8 | 237.7 | 214.2 | 228.8 | 240
1760 | 1660 | 350.5 | 252.8 | 237.8 | 214.2 | 228.8 | 240
1761 | 1661 | 350.6 | 252.8 | 237.8 | 214.2 | 228.8 | 240
1762 | 1662 | 350.7 | 252.8 | 237.8 | 214.3 | 228.4 | 240
1763 | 1663 | 350.8 | 252.9 | 237.9 | 214.3 | 228.4 | 240
1764 | 1664 | 350.7 | 252.9 | 238 | 214.4 | 228.3 | 240.1
1765 | 1665 | 350.7 | 253 | 238 | 214.4 | 228.7 | 240.1
1766 | 1666 | 350.7 | 253 | 238.1 | 214.4 | 228.1 | 240.1
1767 | 1667 | 350.7 | 253.1 | 238.1 | 214.5 | 228.2 | 240.1
1768 | 1668 | 350.6 | 253.1 | 238.2 | 214.5 | 228.4 | 240.1
1769 | 1669 | 350.6 | 253.2 | 238.2 | 214.6 | 228.5 | 240.1
1770 | 1670 | 350.4 | 253.2 | 238.3 | 214.6 | 228 | 240.1
1771 | 1671 | 350.2 | 253.2 | 238.3 | 214.7 | 227.5 | 240.1
1772 | 1672 | 350 | 253.3 | 238.4 | 214.7 | 227.1 | 240.1
1773 | 1673 | 349.9 | 253.3 | 238.4 | 214.7 | 226.8 | 240.1
1774 | 1674 | 349.8 | 253.3 | 238.5 | 214.8 | 226.8 | 240.1
1775 | 1675 | 349.8 | 253.3 | 238.5 | 214.8 | 226.6 | 240.1
1776 | 1676 | 349.7 | 253.4 | 238.6 | 214.8 | 226.6 | 240.1
1777 | 1677 | 349.7 | 253.4 | 238.6 | 214.9 | 226.5 | 240.1
1778 | 1678 | 349.5 | 253.4 | 238.7 | 214.9 | 226.4 | 240.1
1779 | 1679 | 349.4 | 253.5 | 238.7 | 215 | 226.2 | 240.1
1780 | 1680 | 349.2 | 253.5 | 238.8 | 215 | 226 | 240.1
1781 | 1681 | 349 | 253.5 | 238.8 | 215 | 226.2 | 240.1
1782 | 1682 | 348.9 | 253.6 | 238.8 | 215.1 | 225.9 | 240.1
1783 | 1683 | 348.9 | 253.6 | 238.9 | 215.1 | 225.9 | 240.1
1784 | 1684 | 348.8 | 253.6 | 239 | 215.2 | 226.4 | 240.1
1785 | 1685 | 348.8 | 253.7 | 239 | 215.2 | 226.6 | 240.1
1786 | 1686 | 348.7 | 253.7 | 239.1 | 215.2 | 227.1 | 240.1
1787 | 1687 | 348.7 | 253.8 | 239.1 | 215.3 | 227.3 | 240.1
1788 | 1688 | 348.8 | 253.8 | 239.1 | 215.3 | 227.9 | 240
1789 | 1689 | 348.9 | 253.9 | 239.2 | 215.4 | 228.4 | 240
1790 | 1690 | 349 | 253.9 | 239.3 | 215.4 | 228.1 | 240
1791 | 1691 | 349 | 254 | 239.3 | 215.4 | 228.4 | 240
1792 | 1692 | 349 | 254.1 | 239.4 | 215.5 | 228.8 | 240
1793 | 1693 | 349.1 | 254.1 | 239.4 | 215.5 | 228.6 | 240
1794 | 1694 | 349.1 | 254.2 | 239.5 | 215.5 | 228.6 | 240
1795 | 1695 | 349.2 | 254.2 | 239.5 | 215.6 | 228.6 | 240
1796 | 1696 | 349.2 | 254.2 | 239.6 | 215.6 | 228.7 | 240
1797 | 1697 | 349.2 | 254.3 | 239.6 | 215.7 | 228.8 | 240
1798 | 1698 | 349.2 | 254.3 | 239.6 | 215.7 | 228.8 | 240
1799 | 1699 | 349.3 | 254.3 | 239.7 | 215.7 | 228.7 | 240
1800 | 1700 | 349.3 | 254.3 | 239.8 | 215.8 | 228.6 | 240
1801 | 1701 | 349.3 | 254.3 | 239.8 | 215.8 | 228.4 | 240
1802 | 1702 | 349.4 | 254.3 | 239.8 | 215.8 | 228.1 | 240
1803 | 1703 | 349.5 | 254.3 | 239.9 | 215.9 | 227.9 | 240
1804 | 1704 | 349.6 | 254.3 | 239.9 | 215.9 | 228.6 | 240.1
1805 | 1705 | 349.8 | 254.4 | 240 | 216 | 228.9 | 240.1
1806 | 1706 | 349.8 | 254.4 | 240 | 216 | 228.8 | 240.1
1807 | 1707 | 349.9 | 254.4 | 240.1 | 216 | 228 | 240.1
1808 | 1708 | 349.9 | 254.5 | 240.2 | 216.1 | 227.2 | 240.1
1809 | 1709 | 350 | 254.6 | 240.2 | 216.1 | 227.4 | 240.2
1810 | 1710 | 349.9 | 254.6 | 240.3 | 216.1 | 227.4 | 240.2
1811 | 1711 | 349.7 | 254.7 | 240.3 | 216.2 | 226.8 | 240.2
1812 | 1712 | 349.7 | 254.8 | 240.4 | 216.2 | 226.2 | 240.2
1813 | 1713 | 349.8 | 254.8 | 240.4 | 216.3 | 226 | 240.2
1814 | 1714 | 349.9 | 254.9 | 240.5 | 216.3 | 226.6 | 240.3
1815 | 1715 | 349.9 | 254.9 | 240.5 | 216.3 | 226.7 | 240.3
1816 | 1716 | 349.7 | 255 | 240.6 | 216.4 | 226.8 | 240.3
1817 | 1717 | 349.7 | 255.1 | 240.6 | 216.4 | 227.3 | 240.3
1818 | 1718 | 349.6 | 255.1 | 240.7 | 216.4 | 227.5 | 240.3
1819 | 1719 | 349.5 | 255.2 | 240.8 | 216.5 | 227.7 | 240.4
1820 | 1720 | 349.4 | 255.2 | 240.8 | 216.5 | 228.3 | 240.4
1821 | 1721 | 349.3 | 255.3 | 240.9 | 216.5 | 228.5 | 240.4
1822 | 1722 | 349.1 | 255.3 | 240.9 | 216.6 | 228.5 | 240.4
1823 | 1723 | 349 | 255.3 | 241 | 216.6 | 228.6 | 240.4
1824 | 1724 | 348.9 | 255.2 | 241 | 216.7 | 228.5 | 240.4
1825 | 1725 | 349.1 | 255.2 | 241.1 | 216.7 | 228.2 | 240.4
1826 | 1726 | 349.1 | 255.2 | 241.1 | 216.7 | 227.5 | 240.5
1827 | 1727 | 349.3 | 255.2 | 241.2 | 216.8 | 227.2 | 240.5
1828 | 1728 | 349.3 | 255.1 | 241.3 | 216.8 | 226.1 | 240.5
1829 | 1729 | 349.2 | 255.1 | 241.3 | 216.8 | 225.6 | 240.5
1830 | 1730 | 349.1 | 255.1 | 241.4 | 216.9 | 225.9 | 240.5
1831 | 1731 | 349 | 255.2 | 241.5 | 216.9 | 225.7 | 240.5
1832 | 1732 | 348.9 | 255.2 | 241.6 | 217 | 224.9 | 240.5
1833 | 1733 | 348.8 | 255.2 | 241.7 | 217 | 224.8 | 240.4
1834 | 1734 | 348.7 | 255.2 | 241.7 | 217 | 225.3 | 240.4
1835 | 1735 | 348.5 | 255.2 | 241.8 | 217.1 | 225.7 | 240.4
1836 | 1736 | 348.3 | 255.3 | 241.9 | 217.1 | 226.3 | 240.4
1837 | 1737 | 348.1 | 255.3 | 242 | 217.2 | 226.1 | 240.4
1838 | 1738 | 348.1 | 255.3 | 242 | 217.2 | 226.9 | 240.3
1839 | 1739 | 348.1 | 255.4 | 242.1 | 217.2 | 227.4 | 240.3
1840 | 1740 | 348 | 255.4 | 242.2 | 217.3 | 227.4 | 240.3
1841 | 1741 | 347.8 | 255.4 | 242.3 | 217.3 | 227.2 | 240.3
1842 | 1742 | 347.8 | 255.5 | 242.4 | 217.3 | 227 | 240.3
1843 | 1743 | 347.8 | 255.5 | 242.4 | 217.4 | 227 | 240.3
1844 | 1744 | 347.8 | 255.5 | 242.5 | 217.4 | 227.2 | 240.3
1845 | 1745 | 347.8 | 255.5 | 242.6 | 217.4 | 227.3 | 240.3
1846 | 1746 | 347.8 | 255.5 | 242.7 | 217.5 | 227.4 | 240.4
1847 | 1747 | 347.8 | 255.5 | 242.8 | 217.5 | 227.3 | 240.4
1848 | 1748 | 347.9 | 255.5 | 242.9 | 217.6 | 227.7 | 240.4
1849 | 1749 | 348.1 | 255.6 | 243 | 217.6 | 227.8 | 240.5
1850 | 1750 | 348.2 | 255.6 | 243 | 217.6 | 227.5 | 240.5
1851 | 1751 | 348.3 | 255.7 | 243.1 | 217.6 | 226.5 | 240.5
1852 | 1752 | 348.4 | 255.7 | 243.2 | 217.7 | 226 | 240.5
1853 | 1753 | 348.4 | 255.8 | 243.3 | 217.7 | 226.5 | 240.5
1854 | 1754 | 348.5 | 255.8 | 243.4 | 217.7 | 226.4 | 240.5
1855 | 1755 | 348.7 | 255.8 | 243.4 | 217.8 | 226 | 240.6
1856 | 1756 | 348.9 | 255.8 | 243.5 | 217.8 | 226.3 | 240.6
1857 | 1757 | 349.1 | 255.8 | 243.5 | 217.9 | 226 | 240.6
1858 | 1758 | 349.3 | 255.8 | 243.6 | 217.9 | 225.6 | 240.6
1859 | 1759 | 349.3 | 255.8 | 243.7 | 217.9 | 225.2 | 240.6
1860 | 1760 | 349.3 | 255.8 | 243.7 | 217.9 | 225.2 | 240.6
1861 | 1761 | 349.3 | 255.8 | 243.8 | 218 | 225.4 | 240.7
1862 | 1762 | 349.3 | 255.8 | 243.9 | 218 | 225.5 | 240.7
1863 | 1763 | 349.3 | 255.8 | 243.9 | 218 | 225.7 | 240.7
1864 | 1764 | 349.3 | 255.8 | 244 | 218.1 | 225.5 | 240.7
1865 | 1765 | 349.4 | 255.8 | 244.1 | 218.1 | 225.3 | 240.7
1866 | 1766 | 349.4 | 255.7 | 244.1 | 218.1 | 225.8 | 240.8
1867 | 1767 | 349.4 | 255.7 | 244.2 | 218.2 | 225.4 | 240.8
1868 | 1768 | 349.4 | 255.7 | 244.2 | 218.2 | 225.3 | 240.8
1869 | 1769 | 349.4 | 255.7 | 244.3 | 218.2 | 225.2 | 240.8
1870 | 1770 | 349.5 | 255.6 | 244.4 | 218.2 | 224.9 | 240.8
1871 | 1771 | 349.4 | 255.6 | 244.4 | 218.3 | 224.6 | 240.8
1872 | 1772 | 349.2 | 255.6 | 244.5 | 218.3 | 225.4 | 240.9
1873 | 1773 | 349.2 | 255.6 | 244.5 | 218.3 | 225.7 | 240.9
1874 | 1774 | 349.1 | 255.6 | 244.6 | 218.4 | 225.7 | 240.9
1875 | 1775 | 348.9 | 255.6 | 244.6 | 218.4 | 226.1 | 240.9
1876 | 1776 | 348.8 | 255.6 | 244.7 | 218.4 | 225.7 | 240.8
1877 | 1777 | 348.7 | 255.6 | 244.8 | 218.5 | 225.5 | 240.9
1878 | 1778 | 348.6 | 255.6 | 244.8 | 218.5 | 224.9 | 240.9
1879 | 1779 | 348.5 | 255.6 | 244.9 | 218.5 | 224.8 | 240.9
1880 | 1780 | 348.6 | 255.6 | 244.9 | 218.6 | 224.4 | 240.9
1881 | 1781 | 348.6 | 255.6 | 245 | 218.6 | 224 | 240.9
1882 | 1782 | 348.4 | 255.6 | 245.1 | 218.6 | 223.6 | 240.9
1883 | 1783 | 348.2 | 255.6 | 245.2 | 218.7 | 223.4 | 240.9
1884 | 1784 | 348.1 | 255.7 | 245.2 | 218.7 | 223.2 | 240.9
1885 | 1785 | 348.1 | 255.7 | 245.3 | 218.7 | 222.9 | 240.9
1886 | 1786 | 348 | 255.8 | 245.3 | 218.8 | 222.9 | 240.9
1887 | 1787 | 348 | 255.8 | 245.4 | 218.8 | 223.3 | 240.9
1888 | 1788 | 348 | 255.8 | 245.5 | 218.8 | 223 | 240.9
1889 | 1789 | 348 | 255.9 | 245.5 | 218.8 | 223.2 | 240.9
1890 | 1790 | 348 | 255.9 | 245.6 | 218.9 | 223.2 | 240.9
1891 | 1791 | 348.1 | 256 | 245.6 | 218.9 | 223.1 | 240.9
1892 | 1792 | 348.2 | 256 | 245.6 | 218.9 | 223.9 | 240.9
1893 | 1793 | 348.3 | 256 | 245.7 | 219 | 224.3 | 240.9
1894 | 1794 | 348.4 | 255.9 | 245.7 | 219 | 224.4 | 240.9
1895 | 1795 | 348.4 | 255.9 | 245.8 | 219 | 223.8 | 240.9
1896 | 1796 | 348.4 | 255.9 | 245.8 | 219.1 | 223.5 | 240.9
1897 | 1797 | 348.2 | 255.9 | 245.9 | 219.1 | 223.5 | 240.9
1898 | 1798 | 348.2 | 255.8 | 245.9 | 219.1 | 223.5 | 240.9
1899 | 1799 | 348.2 | 255.8 | 245.9 | 219.1 | 223.5 | 240.9
1900 | 1800 | 348.3 | 255.8 | 246 | 219.2 | 223 | 240.9
1901 | 1801 | 348.4 | 255.8 | 246.1 | 219.2 | 223.7 | 240.9
1902 | 1802 | 348.4 | 255.9 | 246.1 | 219.2 | 224.4 | 240.9
1903 | 1803 | 348.5 | 255.9 | 246.2 | 219.3 | 224.6 | 240.9
1904 | 1804 | 348.5 | 255.9 | 246.2 | 219.3 | 224.9 | 241
1905 | 1805 | 348.4 | 255.9 | 246.3 | 219.3 | 224.9 | 241
1906 | 1806 | 348.4 | 255.8 | 246.3 | 219.3 | 225.3 | 241
1907 | 1807 | 348.3 | 255.8 | 246.4 | 219.4 | 225.9 | 240.9
1908 | 1808 | 348.4 | 255.8 | 246.4 | 219.4 | 225.9 | 240.9
1909 | 1809 | 348.4 | 255.8 | 246.5 | 219.4 | 225.8 | 240.9
1910 | 1810 | 348.3 | 255.8 | 246.5 | 219.5 | 225.7 | 240.9
1911 | 1811 | 348.3 | 255.8 | 246.6 | 219.5 | 225.5 | 240.9
1912 | 1812 | 348.3 | 255.8 | 246.6 | 219.5 | 225.1 | 240.9
1913 | 1813 | 348.2 | 255.8 | 246.7 | 219.5 | 224.8 | 240.9
1914 | 1814 | 348.3 | 255.8 | 246.8 | 219.6 | 225.6 | 240.9
1915 | 1815 | 348.4 | 255.9 | 246.8 | 219.6 | 225.7 | 240.9
1916 | 1816 | 348.3 | 255.9 | 246.9 | 219.6 | 225.3 | 240.8
1917 | 1817 | 348.1 | 255.9 | 246.9 | 219.7 | 225.2 | 240.8
1918 | 1818 | 348 | 255.9 | 247 | 219.7 | 225 | 240.8
1919 | 1819 | 347.9 | 255.9 | 247 | 219.7 | 224.9 | 240.8
1920 | 1820 | 347.9 | 256 | 247.1 | 219.7 | 224.6 | 240.8
1921 | 1821 | 347.9 | 256 | 247.1 | 219.8 | 224.4 | 240.8
1922 | 1822 | 347.8 | 256.1 | 247.2 | 219.8 | 224.3 | 240.8
1923 | 1823 | 347.8 | 256.1 | 247.2 | 219.8 | 223.9 | 240.9
1924 | 1824 | 347.9 | 256.1 | 247.3 | 219.9 | 223.9 | 240.9
1925 | 1825 | 347.9 | 256.1 | 247.3 | 219.9 | 223.5 | 240.9
1926 | 1826 | 347.9 | 256.1 | 247.4 | 219.9 | 223.2 | 240.8
1927 | 1827 | 348 | 256.1 | 247.4 | 219.9 | 223.1 | 240.8
1928 | 1828 | 348.2 | 256.2 | 247.5 | 220 | 222.7 | 240.8
1929 | 1829 | 348.3 | 256.2 | 247.6 | 220 | 222.7 | 240.8
1930 | 1830 | 348.4 | 256.2 | 247.6 | 220 | 223.1 | 240.8
1931 | 1831 | 348.5 | 256.2 | 247.7 | 220.1 | 223.3 | 240.7
1932 | 1832 | 348.7 | 256.2 | 247.7 | 220.1 | 223.1 | 240.7
1933 | 1833 | 348.9 | 256.2 | 247.8 | 220.1 | 222.3 | 240.7
1934 | 1834 | 349.2 | 256.2 | 247.9 | 220.1 | 222.8 | 240.7
1935 | 1835 | 349.3 | 256.2 | 247.9 | 220.2 | 222.9 | 240.7
1936 | 1836 | 349.5 | 256.2 | 248 | 220.2 | 222.5 | 240.7
1937 | 1837 | 349.6 | 256.2 | 248 | 220.2 | 223 | 240.7
1938 | 1838 | 349.6 | 256.2 | 248.1 | 220.2 | 223.3 | 240.7
1939 | 1839 | 349.7 | 256.3 | 248.2 | 220.3 | 223.1 | 240.7
1940 | 1840 | 349.7 | 256.3 | 248.2 | 220.3 | 223.5 | 240.7
1941 | 1841 | 349.7 | 256.4 | 248.3 | 220.3 | 223.6 | 240.7
1942 | 1842 | 349.6 | 256.5 | 248.3 | 220.4 | 223.3 | 240.7
1943 | 1843 | 349.6 | 256.5 | 248.4 | 220.4 | 223.9 | 240.7
1944 | 1844 | 349.5 | 256.6 | 248.5 | 220.4 | 223.7 | 240.7
1945 | 1845 | 349.3 | 256.7 | 248.5 | 220.4 | 222.9 | 240.8
1946 | 1846 | 349.3 | 256.7 | 248.6 | 220.5 | 222.8 | 240.8
1947 | 1847 | 349.2 | 256.8 | 248.6 | 220.5 | 222.9 | 241.1
1948 | 1848 | 349.3 | 256.8 | 248.7 | 220.5 | 222.7 | 241.3
1949 | 1849 | 349.8 | 256.9 | 248.8 | 220.5 | 222.4 | 241.3
1950 | 1850 | 350.8 | 256.9 | 248.9 | 220.6 | 222.6 | 241.4
1951 | 1851 | 352.5 | 256.9 | 248.9 | 220.6 | 222.6 | 241.4
1952 | 1852 | 354.7 | 257 | 249 | 220.6 | 222.5 | 241.5
1953 | 1853 | 357.2 | 257 | 249.1 | 220.6 | 222.5 | 241.6
1954 | 1854 | 360 | 257.1 | 249.2 | 220.7 | 222.8 | 241.8
1955 | 1855 | 363 | 257.2 | 249.2 | 220.7 | 223.1 | 241.9
1956 | 1856 | 366.3 | 257.4 | 249.3 | 220.7 | 223.6 | 242
1957 | 1857 | 369.5 | 257.6 | 249.3 | 220.8 | 224.1 | 242.3
1958 | 1858 | 372.6 | 257.8 | 249.4 | 220.8 | 224.7 | 242.6
1959 | 1859 | 375.5 | 258.1 | 249.5 | 220.8 | 225.2 | 242.8
1960 | 1860 | 378.2 | 258.3 | 249.6 | 220.9 | 225.5 | 243.1
1961 | 1861 | 380.7 | 258.6 | 249.7 | 220.9 | 226.2 | 243.3
1962 | 1862 | 382.8 | 258.8 | 249.8 | 220.9 | 227.1 | 243.4
1963 | 1863 | 384.6 | 259.1 | 250 | 220.9 | 228.1 | 243.6
1964 | 1864 | 386.1 | 259.4 | 250.1 | 220.9 | 228.2 | 243.9
1965 | 1865 | 387.5 | 259.7 | 250.2 | 221 | 228.3 | 244.1
1966 | 1866 | 388.4 | 260 | 250.3 | 221 | 228.7 | 244.3
1967 | 1867 | 389.2 | 260.2 | 250.5 | 221 | 228.9 | 244.6
1968 | 1868 | 389.7 | 260.5 | 250.6 | 221 | 229.5 | 244.8
1969 | 1869 | 390.2 | 260.8 | 250.7 | 221.1 | 230.1 | 245.1
1970 | 1870 | 390.4 | 261.2 | 250.9 | 221.1 | 230.1 | 245.3
1971 | 1871 | 390.4 | 261.4 | 251 | 221.1 | 230.1 | 245.5
1972 | 1872 | 390.5 | 261.7 | 251.2 | 221.1 | 230.3 | 245.7
1973 | 1873 | 390.5 | 261.9 | 251.4 | 221.1 | 231 | 245.9
1974 | 1874 | 390.4 | 262.1 | 251.6 | 221.1 | 231.5 | 246.1
1975 | 1875 | 390 | 262.4 | 251.8 | 221.2 | 231.4 | 246.3
1976 | 1876 | 389.6 | 262.7 | 251.9 | 221.2 | 231.7 | 246.5
1977 | 1877 | 389.1 | 262.9 | 252 | 221.2 | 231.5 | 246.6
1978 | 1878 | 388.5 | 263.1 | 252.2 | 221.2 | 231.4 | 246.8
1979 | 1879 | 388.1 | 263.3 | 252.4 | 221.3 | 231.1 | 247
1980 | 1880 | 387.6 | 263.4 | 252.5 | 221.3 | 231 | 247.1
1981 | 1881 | 387 | 263.6 | 252.7 | 221.3 | 231 | 247.2
1982 | 1882 | 386.3 | 263.8 | 252.9 | 221.4 | 230.9 | 247.3
1983 | 1883 | 385.5 | 264 | 253.1 | 221.4 | 231 | 247.4
1984 | 1884 | 384.9 | 264.2 | 253.2 | 221.4 | 231 | 247.5
1985 | 1885 | 384.2 | 264.3 | 253.4 | 221.4 | 231.1 | 247.6
1986 | 1886 | 383.5 | 264.5 | 253.6 | 221.5 | 231.3 | 247.8
1987 | 1887 | 382.8 | 264.6 | 253.8 | 221.5 | 231.3 | 247.9
1988 | 1888 | 382.2 | 264.8 | 253.9 | 221.5 | 231.1 | 248
1989 | 1889 | 381.7 | 264.9 | 254.1 | 221.6 | 231.5 | 248.1
1990 | 1890 | 381.1 | 265 | 254.3 | 221.6 | 231.3 | 248.2
1991 | 1891 | 380.3 | 265 | 254.5 | 221.6 | 231.2 | 248.3
1992 | 1892 | 379.6 | 265.1 | 254.6 | 221.7 | 231.5 | 248.4
1993 | 1893 | 378.9 | 265.2 | 254.8 | 221.7 | 232.1 | 248.4
1994 | 1894 | 378.3 | 265.3 | 255 | 221.8 | 232 | 248.5
1995 | 1895 | 377.7 | 265.5 | 255 | 221.8 | 232 | 248.7
1996 | 1896 | 376.9 | 265.5 | 255.2 | 221.9 | 231.7 | 248.7
1997 | 1897 | 376.1 | 265.6 | 255.4 | 221.9 | 231.4 | 248.8
1998 | 1898 | 375.3 | 265.6 | 255.6 | 221.9 | 231.7 | 248.9
1999 | 1899 | 374.6 | 265.6 | 255.7 | 222 | 231.5 | 248.9
2000 | 1900 | 373.9 | 265.6 | 255.9 | 222 | 231.6 | 249
2001 | 1901 | 373.3 | 265.7 | 256 | 222 | 231.2 | 249
2002 | 1902 | 372.5 | 265.7 | 256.2 | 222.1 | 231.2 | 249.1
2003 | 1903 | 371.7 | 265.7 | 256.4 | 222.1 | 231 | 249.1
2004 | 1904 | 370.9 | 265.7 | 256.5 | 222.1 | 230.7 | 249.2
2005 | 1905 | 370.1 | 265.8 | 256.6 | 222.2 | 230.8 | 249.3
2006 | 1906 | 369.3 | 265.8 | 256.8 | 222.2 | 231.2 | 249.3
2007 | 1907 | 368.7 | 265.8 | 256.9 | 222.3 | 230.9 | 249.3
2008 | 1908 | 368.1 | 265.8 | 257 | 222.3 | 230.7 | 249.3
2009 | 1909 | 367.5 | 265.8 | 257.1 | 222.3 | 231 | 249.4
2010 | 1910 | 367.1 | 265.9 | 257.2 | 222.4 | 231.2 | 249.4
2011 | 1911 | 366.6 | 265.9 | 257.3 | 222.4 | 231.1 | 249.5
2012 | 1912 | 366.3 | 266 | 257.5 | 222.5 | 230.8 | 249.6
2013 | 1913 | 366.1 | 266.1 | 257.6 | 222.5 | 230.6 | 249.6
2014 | 1914 | 366.1 | 266.1 | 257.7 | 222.5 | 230.7 | 249.6
2015 | 1915 | 366 | 266.1 | 257.8 | 222.6 | 230.8 | 249.7
2016 | 1916 | 365.9 | 266.1 | 258 | 222.6 | 230.8 | 249.7
2017 | 1917 | 365.9 | 266.1 | 258.1 | 222.7 | 230.3 | 249.7
2018 | 1918 | 365.9 | 266.2 | 258.2 | 222.7 | 229.6 | 249.7
2019 | 1919 | 366.1 | 266.2 | 258.3 | 222.8 | 229.3 | 249.7
2020 | 1920 | 366.4 | 266.2 | 258.4 | 222.8 | 229.7 | 249.8
2021 | 1921 | 366.6 | 266.2 | 258.5 | 222.8 | 230.3 | 249.8
2022 | 1922 | 366.9 | 266.2 | 258.6 | 222.9 | 230.4 | 249.9
2023 | 1923 | 367.2 | 266.2 | 258.7 | 222.9 | 230.7 | 249.9
2024 | 1924 | 367.5 | 266.1 | 258.8 | 223 | 231.2 | 250
2025 | 1925 | 368 | 266.1 | 258.9 | 223 | 231.3 | 250
2026 | 1926 | 368.5 | 266.1 | 259 | 223 | 231.2 | 250.1
2027 | 1927 | 369.1 | 266.1 | 259.1 | 223.1 | 231.7 | 250.1
2028 | 1928 | 369.6 | 266.1 | 259.2 | 223.1 | 232.4 | 250.2
2029 | 1929 | 370 | 266.1 | 259.3 | 223.2 | 232.2 | 250.2
2030 | 1930 | 370.5 | 266.1 | 259.4 | 223.2 | 231.5 | 250.3
2031 | 1931 | 371 | 266.1 | 259.5 | 223.2 | 231.2 | 250.3
2032 | 1932 | 371.4 | 266.1 | 259.6 | 223.3 | 231 | 250.4
2033 | 1933 | 371.9 | 266.1 | 259.7 | 223.3 | 230.8 | 250.4
2034 | 1934 | 372.2 | 266.1 | 259.8 | 223.3 | 231.2 | 250.5
2035 | 1935 | 372.5 | 266.1 | 260 | 223.4 | 231.6 | 250.5
2036 | 1936 | 372.8 | 266.2 | 260 | 223.4 | 232.1 | 250.5
2037 | 1937 | 373.1 | 266.2 | 260.2 | 223.5 | 232.1 | 250.6
2038 | 1938 | 373.4 | 266.3 | 260.3 | 223.5 | 232 | 250.7
2039 | 1939 | 373.7 | 266.3 | 260.4 | 223.5 | 232.3 | 250.7
2040 | 1940 | 373.8 | 266.4 | 260.5 | 223.6 | 232.9 | 250.8
2041 | 1941 | 374 | 266.4 | 260.6 | 223.6 | 232.8 | 250.9
2042 | 1942 | 374.2 | 266.4 | 260.7 | 223.7 | 232.5 | 251
2043 | 1943 | 374.3 | 266.4 | 260.8 | 223.7 | 232.6 | 251
2044 | 1944 | 374.5 | 266.4 | 261 | 223.7 | 232.8 | 251.1
2045 | 1945 | 374.7 | 266.4 | 261.1 | 223.8 | 232.7 | 251.2
2046 | 1946 | 374.8 | 266.4 | 261.2 | 223.8 | 233 | 251.3
2047 | 1947 | 374.8 | 266.5 | 261.3 | 223.9 | 232.8 | 251.3
2048 | 1948 | 374.7 | 266.5 | 261.4 | 223.9 | 232.5 | 251.4
2049 | 1949 | 374.7 | 266.6 | 261.5 | 223.9 | 232.2 | 251.5
2050 | 1950 | 374.7 | 266.6 | 261.6 | 224 | 232.3 | 251.7
2051 | 1951 | 374.8 | 266.7 | 261.6 | 224 | 232.2 | 251.8
2052 | 1952 | 374.7 | 266.8 | 261.7 | 224.1 | 232.6 | 251.9
2053 | 1953 | 374.6 | 266.9 | 261.8 | 224.1 | 233.4 | 251.9
2054 | 1954 | 374.5 | 266.9 | 261.9 | 224.1 | 233.7 | 252
2055 | 1955 | 374.5 | 267 | 262 | 224.2 | 234.5 | 252
2056 | 1956 | 374.3 | 267 | 262.1 | 224.2 | 234.2 | 252.1
2057 | 1957 | 374.3 | 267 | 262.2 | 224.3 | 234 | 252.2
2058 | 1958 | 374.5 | 267 | 262.3 | 224.3 | 234.5 | 252.2
2059 | 1959 | 374.5 | 267 | 262.4 | 224.3 | 234.5 | 252.3
2060 | 1960 | 374.6 | 267 | 262.5 | 224.4 | 234.9 | 252.4
2061 | 1961 | 374.6 | 267 | 262.6 | 224.4 | 234.9 | 252.5
2062 | 1962 | 374.6 | 267 | 262.7 | 224.5 | 235.1 | 252.6
2063 | 1963 | 374.5 | 267 | 262.8 | 224.5 | 235.2 | 252.6
2064 | 1964 | 374.4 | 267 | 262.9 | 224.6 | 235.8 | 252.7
2065 | 1965 | 374.2 | 267.1 | 263 | 224.6 | 235.8 | 252.8
2066 | 1966 | 374.1 | 267.1 | 263 | 224.6 | 235.7 | 252.8
2067 | 1967 | 374 | 267.1 | 263.1 | 224.7 | 236 | 252.9
2068 | 1968 | 374.2 | 267.1 | 263.2 | 224.7 | 236 | 252.9
2069 | 1969 | 374.2 | 267.2 | 263.3 | 224.7 | 235.7 | 253
2070 | 1970 | 374.1 | 267.2 | 263.4 | 224.8 | 235.1 | 253.1
2071 | 1971 | 374.2 | 267.2 | 263.4 | 224.8 | 235.2 | 253.1
2072 | 1972 | 374.2 | 267.2 | 263.5 | 224.9 | 235.7 | 253.2
2073 | 1973 | 374.2 | 267.3 | 263.6 | 224.9 | 235.8 | 253.3
2074 | 1974 | 374.3 | 267.3 | 263.7 | 225 | 235.9 | 253.4
2075 | 1975 | 374.3 | 267.3 | 263.8 | 225 | 235.7 | 253.4
2076 | 1976 | 374.4 | 267.3 | 263.9 | 225 | 235.8 | 253.5
2077 | 1977 | 374.6 | 267.4 | 263.9 | 225.1 | 235.7 | 253.6
2078 | 1978 | 374.6 | 267.4 | 264 | 225.1 | 235.7 | 253.7
2079 | 1979 | 374.6 | 267.5 | 264.1 | 225.2 | 236.4 | 253.7
2080 | 1980 | 374.6 | 267.6 | 264.2 | 225.2 | 236.8 | 253.7
2081 | 1981 | 374.6 | 267.7 | 264.3 | 225.2 | 236.8 | 253.7
2082 | 1982 | 374.4 | 267.7 | 264.4 | 225.3 | 236.4 | 253.8
2083 | 1983 | 374.4 | 267.8 | 264.5 | 225.3 | 236.5 | 253.8
2084 | 1984 | 374.4 | 267.8 | 264.5 | 225.3 | 236.9 | 253.9
2085 | 1985 | 374.4 | 267.9 | 264.6 | 225.4 | 237.2 | 253.9
2086 | 1986 | 374.5 | 267.9 | 264.7 | 225.4 | 237.7 | 254
2087 | 1987 | 374.5 | 267.9 | 264.7 | 225.5 | 237.4 | 254.1
2088 | 1988 | 374.3 | 268 | 264.8 | 225.5 | 237.6 | 254.2
2089 | 1989 | 374.2 | 268 | 264.9 | 225.5 | 237.2 | 254.3
2090 | 1990 | 374.2 | 268 | 265 | 225.6 | 237.6 | 254.3
2091 | 1991 | 374.2 | 268 | 265.1 | 225.6 | 237.4 | 254.3
2092 | 1992 | 374.4 | 268 | 265.2 | 225.7 | 237.6 | 254.4
2093 | 1993 | 374.5 | 268.1 | 265.3 | 225.7 | 238.1 | 254.5
2094 | 1994 | 374.5 | 268.1 | 265.4 | 225.8 | 238.3 | 254.6
2095 | 1995 | 374.4 | 268.2 | 265.4 | 225.8 | 238.1 | 254.6
2096 | 1996 | 374.4 | 268.3 | 265.5 | 225.8 | 238 | 254.7
2097 | 1997 | 374.5 | 268.3 | 265.6 | 225.9 | 238.1 | 254.8
2098 | 1998 | 374.7 | 268.4 | 265.7 | 225.9 | 237.4 | 254.8
2099 | 1999 | 374.7 | 268.5 | 265.8 | 226 | 237.6 | 254.8
2100 | 2000 | 374.9 | 268.6 | 265.8 | 226 | 237.8 | 254.9
2101 | 2001 | 374.8 | 268.7 | 265.9 | 226 | 238 | 254.9
2102 | 2002 | 374.8 | 268.8 | 266 | 226.1 | 238.2 | 255
2103 | 2003 | 374.8 | 268.9 | 266.1 | 226.1 | 238.2 | 255.1
2104 | 2004 | 374.7 | 269 | 266.2 | 226.1 | 238 | 255.1
2105 | 2005 | 374.6 | 269.1 | 266.2 | 226.2 | 238.2 | 255.2
2106 | 2006 | 374.6 | 269.1 | 266.3 | 226.2 | 238.5 | 255.2
2107 | 2007 | 374.7 | 269.2 | 266.4 | 226.3 | 238.5 | 255.2
2108 | 2008 | 374.9 | 269.2 | 266.5 | 226.3 | 238.3 | 255.3
2109 | 2009 | 374.9 | 269.3 | 266.6 | 226.4 | 238.1 | 255.3
2110 | 2010 | 374.8 | 269.4 | 266.6 | 226.4 | 238.1 | 255.4
2111 | 2011 | 374.7 | 269.5 | 266.7 | 226.4 | 238 | 255.4
2112 | 2012 | 374.7 | 269.6 | 266.7 | 226.5 | 237.7 | 255.5
2113 | 2013 | 374.7 | 269.7 | 266.8 | 226.5 | 237.7 | 255.5
2114 | 2014 | 374.7 | 269.7 | 266.9 | 226.6 | 237.6 | 255.5
2115 | 2015 | 374.7 | 269.8 | 267 | 226.6 | 237.4 | 255.5
2116 | 2016 | 374.7 | 269.9 | 267 | 226.7 | 237.3 | 255.6
2117 | 2017 | 374.9 | 269.9 | 267.1 | 226.7 | 237.6 | 255.6
2118 | 2018 | 374.8 | 269.9 | 267.2 | 226.7 | 238.1 | 255.7
2119 | 2019 | 374.8 | 270 | 267.3 | 226.8 | 237.9 | 255.7
2120 | 2020 | 374.7 | 270 | 267.4 | 226.8 | 238.3 | 255.7
2121 | 2021 | 374.6 | 270.1 | 267.4 | 226.9 | 238.8 | 255.7
2122 | 2022 | 374.6 | 270.2 | 267.5 | 226.9 | 239 | 255.8
2123 | 2023 | 374.7 | 270.2 | 267.6 | 226.9 | 239.4 | 255.9
2124 | 2024 | 374.7 | 270.3 | 267.7 | 227 | 239.7 | 255.9
2125 | 2025 | 374.6 | 270.4 | 267.7 | 227 | 240.1 | 255.9
2126 | 2026 | 374.5 | 270.5 | 267.8 | 227.1 | 239.9 | 255.9
2127 | 2027 | 374.5 | 270.5 | 267.9 | 227.1 | 239.9 | 256
2128 | 2028 | 374.3 | 270.6 | 268 | 227.2 | 240.5 | 256
2129 | 2029 | 374.2 | 270.6 | 268 | 227.2 | 240.9 | 256
2130 | 2030 | 374.2 | 270.6 | 268.1 | 227.2 | 240.6 | 256.1
2131 | 2031 | 374.3 | 270.6 | 268.2 | 227.3 | 239.9 | 256.1
2132 | 2032 | 374.3 | 270.7 | 268.2 | 227.3 | 240.2 | 256.2
2133 | 2033 | 374.3 | 270.7 | 268.3 | 227.4 | 240.6 | 256.2
2134 | 2034 | 374.3 | 270.8 | 268.3 | 227.4 | 241.2 | 256.2
2135 | 2035 | 374.2 | 270.8 | 268.4 | 227.5 | 240.4 | 256.3
2136 | 2036 | 374 | 270.9 | 268.5 | 227.5 | 239.6 | 256.3
2137 | 2037 | 374 | 270.9 | 268.5 | 227.5 | 239.5 | 256.3
2138 | 2038 | 374 | 271 | 268.6 | 227.6 | 239.4 | 256.3
2139 | 2039 | 374.2 | 271.1 | 268.6 | 227.6 | 238.7 | 256.3
2140 | 2040 | 374.3 | 271.1 | 268.7 | 227.7 | 238.4 | 256.4
2141 | 2041 | 374.4 | 271.2 | 268.7 | 227.7 | 238.8 | 256.4
2142 | 2042 | 374.4 | 271.3 | 268.8 | 227.8 | 239.3 | 256.4
2143 | 2043 | 374.4 | 271.4 | 268.8 | 227.8 | 239.6 | 256.5
2144 | 2044 | 374.5 | 271.5 | 268.9 | 227.9 | 240.2 | 256.5
2145 | 2045 | 374.7 | 271.6 | 268.9 | 227.9 | 240.2 | 256.5
2146 | 2046 | 374.8 | 271.7 | 269 | 228 | 239.9 | 256.5
2147 | 2047 | 374.8 | 271.7 | 269.1 | 228 | 240.2 | 256.5
2148 | 2048 | 374.8 | 271.8 | 269.1 | 228 | 240.2 | 256.6
2149 | 2049 | 374.9 | 271.9 | 269.2 | 228.1 | 240.3 | 256.6
2150 | 2050 | 375.1 | 272 | 269.2 | 228.1 | 240.5 | 256.6
2151 | 2051 | 375.1 | 272.1 | 269.3 | 228.2 | 240.4 | 256.6
2152 | 2052 | 375 | 272.1 | 269.4 | 228.2 | 240.3 | 256.7
2153 | 2053 | 375.1 | 272.2 | 269.4 | 228.3 | 240.8 | 256.8
2154 | 2054 | 375.1 | 272.3 | 269.5 | 228.3 | 240.9 | 256.8
2155 | 2055 | 375.2 | 272.3 | 269.6 | 228.3 | 240.7 | 256.9
2156 | 2056 | 375.1 | 272.3 | 269.6 | 228.4 | 241 | 257
2157 | 2057 | 374.9 | 272.3 | 269.7 | 228.4 | 241.4 | 257.1
2158 | 2058 | 374.8 | 272.3 | 269.8 | 228.5 | 241.5 | 257.1
2159 | 2059 | 374.8 | 272.3 | 269.9 | 228.5 | 241.7 | 257.1
2160 | 2060 | 374.9 | 272.4 | 270 | 228.6 | 241.9 | 257.2
2161 | 2061 | 374.8 | 272.5 | 270.1 | 228.6 | 240.9 | 257.2
2162 | 2062 | 374.7 | 272.6 | 270.1 | 228.7 | 241 | 257.3
2163 | 2063 | 374.7 | 272.7 | 270.2 | 228.7 | 240.4 | 257.4
2164 | 2064 | 374.8 | 272.7 | 270.3 | 228.7 | 240 | 257.4
2165 | 2065 | 374.8 | 272.8 | 270.3 | 228.8 | 240 | 257.4
2166 | 2066 | 374.8 | 272.9 | 270.4 | 228.8 | 240.2 | 257.5
2167 | 2067 | 374.7 | 273 | 270.4 | 228.9 | 240 | 257.5
2168 | 2068 | 374.6 | 273 | 270.5 | 228.9 | 240.2 | 257.6
2169 | 2069 | 374.5 | 273.1 | 270.5 | 229 | 240.5 | 257.6
2170 | 2070 | 374.5 | 273.2 | 270.6 | 229 | 240.3 | 257.7
2171 | 2071 | 374.4 | 273.4 | 270.6 | 229.1 | 240.6 | 257.7
2172 | 2072 | 374.2 | 273.5 | 270.7 | 229.1 | 241 | 257.8
2173 | 2073 | 374.1 | 273.6 | 270.7 | 229.2 | 241 | 257.8
2174 | 2074 | 374 | 273.7 | 270.8 | 229.2 | 241 | 257.9
2175 | 2075 | 374 | 273.8 | 270.8 | 229.2 | 241.5 | 257.9
2176 | 2076 | 374 | 273.9 | 270.9 | 229.3 | 241.8 | 257.9
2177 | 2077 | 374.1 | 273.9 | 270.9 | 229.3 | 241.4 | 257.9
2178 | 2078 | 374.2 | 274 | 271 | 229.4 | 241 | 257.9
2179 | 2079 | 374.1 | 274 | 271 | 229.4 | 240.8 | 258
2180 | 2080 | 374.1 | 274.1 | 271 | 229.5 | 241.2 | 258
2181 | 2081 | 374 | 274.2 | 271.1 | 229.5 | 241.1 | 258
2182 | 2082 | 374 | 274.2 | 271.1 | 229.6 | 240.5 | 258
2183 | 2083 | 373.8 | 274.3 | 271.2 | 229.6 | 239.9 | 258
2184 | 2084 | 373.7 | 274.3 | 271.2 | 229.6 | 239.7 | 258
2185 | 2085 | 373.6 | 274.4 | 271.3 | 229.7 | 239.7 | 258
2186 | 2086 | 373.5 | 274.4 | 271.3 | 229.7 | 239.9 | 257.9
2187 | 2087 | 373.4 | 274.5 | 271.4 | 229.8 | 240 | 257.9
2188 | 2088 | 373.1 | 274.5 | 271.4 | 229.8 | 240.3 | 257.9
2189 | 2089 | 373 | 274.6 | 271.5 | 229.9 | 240.7 | 257.9
2190 | 2090 | 373 | 274.7 | 271.5 | 229.9 | 240.9 | 257.9
2191 | 2091 | 373 | 274.8 | 271.5 | 229.9 | 241.2 | 257.9
2192 | 2092 | 372.9 | 274.9 | 271.6 | 230 | 242.1 | 257.9
2193 | 2093 | 372.8 | 275 | 271.6 | 230 | 242 | 257.9
2194 | 2094 | 372.7 | 275.1 | 271.7 | 230.1 | 242 | 257.9
2195 | 2095 | 372.7 | 275.2 | 271.7 | 230.1 | 242 | 257.9
2196 | 2096 | 372.7 | 275.2 | 271.7 | 230.2 | 242.2 | 257.8
2197 | 2097 | 372.7 | 275.3 | 271.8 | 230.2 | 242.2 | 257.8
2198 | 2098 | 372.6 | 275.4 | 271.8 | 230.2 | 242.1 | 257.8
2199 | 2099 | 372.7 | 275.5 | 271.8 | 230.3 | 241.3 | 257.8
2200 | 2100 | 372.6 | 275.5 | 271.9 | 230.3 | 240.9 | 257.8
2201 | 2101 | 372.6 | 275.6 | 271.9 | 230.4 | 240.5 | 257.8
2202 | 2102 | 372.5 | 275.6 | 271.9 | 230.4 | 240.7 | 257.8
2203 | 2103 | 372.5 | 275.6 | 272 | 230.4 | 240.8 | 257.8
2204 | 2104 | 372.5 | 275.7 | 272 | 230.5 | 240.8 | 257.8
2205 | 2105 | 372.6 | 275.7 | 272 | 230.5 | 240.5 | 257.8
2206 | 2106 | 372.6 | 275.7 | 272 | 230.5 | 240.1 | 257.8
2207 | 2107 | 372.6 | 275.8 | 272.1 | 230.6 | 240.2 | 257.9
2208 | 2108 | 372.7 | 275.8 | 272.1 | 230.6 | 240.1 | 257.9
2209 | 2109 | 372.8 | 275.7 | 272.1 | 230.6 | 240 | 257.9
2210 | 2110 | 373 | 275.8 | 272.2 | 230.7 | 239.9 | 257.9
2211 | 2111 | 373.2 | 275.7 | 272.2 | 230.7 | 240.2 | 257.9
2212 | 2112 | 373.3 | 275.7 | 272.2 | 230.7 | 240.7 | 258
2213 | 2113 | 373.2 | 275.7 | 272.2 | 230.8 | 241 | 258
2214 | 2114 | 373.1 | 275.8 | 272.3 | 230.8 | 240.8 | 258
2215 | 2115 | 373.1 | 275.8 | 272.3 | 230.9 | 241.2 | 258
2216 | 2116 | 373.1 | 275.8 | 272.3 | 230.9 | 242 | 258
2217 | 2117 | 373.1 | 275.8 | 272.4 | 230.9 | 241.7 | 258.1
2218 | 2118 | 373.2 | 275.8 | 272.4 | 231 | 241.3 | 258.1
2219 | 2119 | 373.2 | 275.9 | 272.4 | 231 | 241.2 | 258.1
2220 | 2120 | 373.2 | 275.9 | 272.5 | 231.1 | 241.2 | 258.1
2221 | 2121 | 373.3 | 275.9 | 272.5 | 231.1 | 241.3 | 258.1
2222 | 2122 | 373.4 | 275.9 | 272.5 | 231.1 | 240.7 | 258.1
2223 | 2123 | 373.6 | 275.9 | 272.5 | 231.2 | 240.8 | 258.1
2224 | 2124 | 373.7 | 275.9 | 272.6 | 231.2 | 240.8 | 258.2
2225 | 2125 | 373.9 | 276 | 272.6 | 231.2 | 240.7 | 258.2
2226 | 2126 | 373.9 | 276 | 272.7 | 231.3 | 241.1 | 258.1
2227 | 2127 | 373.9 | 276.1 | 272.7 | 231.3 | 241.5 | 258.1
2228 | 2128 | 374 | 276.1 | 272.8 | 231.3 | 241.9 | 258.1
2229 | 2129 | 374.3 | 276.1 | 272.8 | 231.4 | 242.3 | 258.2
2230 | 2130 | 374.4 | 276.2 | 272.8 | 231.4 | 242.3 | 258.2
2231 | 2131 | 374.5 | 276.2 | 272.9 | 231.4 | 242.7 | 258.2
2232 | 2132 | 374.5 | 276.3 | 272.9 | 231.5 | 243 | 258.1
2233 | 2133 | 374.6 | 276.4 | 273 | 231.5 | 243.2 | 258.2
2234 | 2134 | 374.6 | 276.5 | 273.1 | 231.5 | 243.3 | 258.2
2235 | 2135 | 374.6 | 276.6 | 273.1 | 231.6 | 242.9 | 258.2
2236 | 2136 | 374.5 | 276.7 | 273.2 | 231.6 | 242.7 | 258.2
2237 | 2137 | 374.6 | 276.8 | 273.2 | 231.6 | 242.8 | 258.2
2238 | 2138 | 374.7 | 276.8 | 273.3 | 231.7 | 243.1 | 258.2
2239 | 2139 | 374.7 | 276.9 | 273.3 | 231.7 | 243.2 | 258.2
2240 | 2140 | 374.8 | 277 | 273.4 | 231.7 | 243.1 | 258.3
2241 | 2141 | 374.7 | 277 | 273.4 | 231.8 | 242.8 | 258.3
2242 | 2142 | 374.6 | 277.1 | 273.5 | 231.8 | 242.7 | 258.3
2243 | 2143 | 374.6 | 277.1 | 273.5 | 231.9 | 242.7 | 258.3
2244 | 2144 | 374.7 | 277.2 | 273.6 | 231.9 | 242.4 | 258.3
2245 | 2145 | 374.6 | 277.2 | 273.6 | 231.9 | 242.8 | 258.3
2246 | 2146 | 374.6 | 277.3 | 273.7 | 232 | 242.8 | 258.3
2247 | 2147 | 374.5 | 277.4 | 273.7 | 232 | 242.4 | 258.3
2248 | 2148 | 374.4 | 277.5 | 273.8 | 232 | 242.4 | 258.3
2249 | 2149 | 374.4 | 277.5 | 273.8 | 232.1 | 243.1 | 258.3
2250 | 2150 | 374.3 | 277.6 | 273.9 | 232.1 | 243 | 258.3
2251 | 2151 | 374.3 | 277.7 | 273.9 | 232.1 | 243 | 258.3
2252 | 2152 | 374.2 | 277.7 | 274 | 232.2 | 243.4 | 258.3
2253 | 2153 | 374.2 | 277.8 | 274 | 232.2 | 243.1 | 258.3
2254 | 2154 | 374.3 | 277.8 | 274 | 232.3 | 243.4 | 258.4
2255 | 2155 | 374.1 | 277.8 | 274.1 | 232.3 | 243.3 | 258.4
2256 | 2156 | 374.1 | 277.8 | 274.1 | 232.3 | 243.4 | 258.4
2257 | 2157 | 374 | 277.8 | 274.1 | 232.4 | 242.9 | 258.4
2258 | 2158 | 374.1 | 277.8 | 274.2 | 232.4 | 242.7 | 258.4
2259 | 2159 | 374.2 | 277.7 | 274.2 | 232.4 | 243 | 258.4
2260 | 2160 | 374.1 | 277.7 | 274.3 | 232.5 | 244 | 258.4
2261 | 2161 | 374.1 | 277.7 | 274.3 | 232.5 | 243.8 | 258.5
2262 | 2162 | 374 | 277.7 | 274.4 | 232.6 | 243.8 | 258.5
2263 | 2163 | 373.9 | 277.7 | 274.4 | 232.6 | 243.6 | 258.5
2264 | 2164 | 374 | 277.7 | 274.5 | 232.6 | 243.4 | 258.6
2265 | 2165 | 373.9 | 277.7 | 274.5 | 232.7 | 242.9 | 258.6
2266 | 2166 | 373.9 | 277.8 | 274.6 | 232.7 | 242.5 | 258.6
2267 | 2167 | 374.1 | 277.8 | 274.6 | 232.7 | 242.4 | 258.6
2268 | 2168 | 374.2 | 277.9 | 274.7 | 232.8 | 242.8 | 258.6
2269 | 2169 | 374.3 | 277.9 | 274.7 | 232.8 | 243 | 258.7
2270 | 2170 | 374.4 | 278 | 274.8 | 232.9 | 243.3 | 258.7
2271 | 2171 | 374.4 | 278 | 274.8 | 232.9 | 243.8 | 258.7
2272 | 2172 | 374.5 | 278.1 | 274.8 | 232.9 | 243.9 | 258.7
2273 | 2173 | 374.6 | 278.2 | 274.9 | 233 | 244.2 | 258.7
2274 | 2174 | 374.7 | 278.2 | 274.9 | 233 | 244 | 258.7
2275 | 2175 | 374.9 | 278.3 | 274.9 | 233 | 243.2 | 258.7
2276 | 2176 | 375.1 | 278.3 | 275 | 233.1 | 242.9 | 258.7
2277 | 2177 | 375.3 | 278.4 | 275 | 233.1 | 243.4 | 258.7
2278 | 2178 | 375.4 | 278.4 | 275.1 | 233.1 | 243.7 | 258.7
2279 | 2179 | 375.4 | 278.4 | 275.1 | 233.2 | 243.4 | 258.7
2280 | 2180 | 375.5 | 278.4 | 275.2 | 233.2 | 243.6 | 258.7
2281 | 2181 | 375.4 | 278.4 | 275.2 | 233.2 | 243.9 | 258.7
2282 | 2182 | 375.4 | 278.5 | 275.3 | 233.3 | 243.8 | 258.7
2283 | 2183 | 375.6 | 278.5 | 275.3 | 233.3 | 244 | 258.8
2284 | 2184 | 375.5 | 278.6 | 275.4 | 233.3 | 244.1 | 258.8
2285 | 2185 | 375.5 | 278.7 | 275.4 | 233.4 | 244.1 | 258.8
2286 | 2186 | 375.6 | 278.8 | 275.4 | 233.4 | 244.3 | 258.8
2287 | 2187 | 375.6 | 278.8 | 275.5 | 233.4 | 243.9 | 258.8
2288 | 2188 | 375.7 | 278.8 | 275.5 | 233.5 | 243.8 | 258.8
2289 | 2189 | 375.8 | 278.8 | 275.6 | 233.5 | 243.5 | 258.8
2290 | 2190 | 375.9 | 278.8 | 275.6 | 233.5 | 243.1 | 258.8
2291 | 2191 | 376 | 278.8 | 275.7 | 233.6 | 243 | 258.8
2292 | 2192 | 376.1 | 278.9 | 275.7 | 233.6 | 243.4 | 258.8
2293 | 2193 | 376.2 | 278.9 | 275.7 | 233.7 | 243.7 | 258.8
2294 | 2194 | 376.2 | 279 | 275.8 | 233.7 | 243.9 | 258.8
2295 | 2195 | 376.1 | 279 | 275.8 | 233.7 | 243.8 | 258.8
2296 | 2196 | 376.1 | 279 | 275.9 | 233.8 | 244.1 | 258.8
2297 | 2197 | 376.1 | 279 | 275.9 | 233.8 | 244.2 | 258.8
2298 | 2198 | 376.1 | 279 | 276 | 233.9 | 244.4 | 258.9
2299 | 2199 | 376.1 | 279 | 276 | 233.9 | 244.7 | 258.9
2300 | 2200 | 376.1 | 279 | 276.1 | 233.9 | 244.4 | 258.9
2301 | 2201 | 376 | 279 | 276.1 | 234 | 244.6 | 258.9
2302 | 2202 | 375.8 | 279.1 | 276.2 | 234 | 244.4 | 258.9
2303 | 2203 | 375.8 | 279.1 | 276.2 | 234 | 244.2 | 258.9
2304 | 2204 | 376 | 279.1 | 276.3 | 234.1 | 244.4 | 258.9
2305 | 2205 | 376.1 | 279.1 | 276.3 | 234.1 | 244.5 | 258.9
2306 | 2206 | 376 | 279.1 | 276.4 | 234.1 | 244.3 | 258.9
2307 | 2207 | 375.9 | 279.1 | 276.4 | 234.2 | 244.7 | 258.9
2308 | 2208 | 375.9 | 279.1 | 276.5 | 234.2 | 244.3 | 258.9
2309 | 2209 | 375.8 | 279.1 | 276.6 | 234.2 | 243.8 | 258.9
2310 | 2210 | 375.7 | 279.2 | 276.6 | 234.3 | 244.2 | 258.9
2311 | 2211 | 375.6 | 279.2 | 276.7 | 234.3 | 244.3 | 259
2312 | 2212 | 375.7 | 279.2 | 276.8 | 234.4 | 244.1 | 259
2313 | 2213 | 375.8 | 279.2 | 276.8 | 234.4 | 243.8 | 259
2314 | 2214 | 375.8 | 279.2 | 276.9 | 234.4 | 244.3 | 259
2315 | 2215 | 375.7 | 279.2 | 276.9 | 234.4 | 244.4 | 259
2316 | 2216 | 375.9 | 279.3 | 277 | 234.5 | 244.6 | 259
2317 | 2217 | 375.9 | 279.4 | 277 | 234.5 | 244.4 | 259
2318 | 2218 | 376 | 279.4 | 277.1 | 234.5 | 244.1 | 259
2319 | 2219 | 375.8 | 279.5 | 277.1 | 234.6 | 243.7 | 259
2320 | 2220 | 375.8 | 279.6 | 277.2 | 234.6 | 243.7 | 259
2321 | 2221 | 375.8 | 279.6 | 277.2 | 234.6 | 244.5 | 259
2322 | 2222 | 375.8 | 279.6 | 277.3 | 234.7 | 244.2 | 259
2323 | 2223 | 375.9 | 279.6 | 277.3 | 234.7 | 244.3 | 259
2324 | 2224 | 375.9 | 279.5 | 277.4 | 234.7 | 244.6 | 259
2325 | 2225 | 375.8 | 279.5 | 277.4 | 234.8 | 244.5 | 259
2326 | 2226 | 375.8 | 279.6 | 277.5 | 234.8 | 244.5 | 259
2327 | 2227 | 375.8 | 279.6 | 277.5 | 234.8 | 244.6 | 259
2328 | 2228 | 376 | 279.7 | 277.6 | 234.9 | 244.8 | 259
2329 | 2229 | 376.1 | 279.7 | 277.7 | 234.9 | 244.6 | 259
2330 | 2230 | 376.1 | 279.8 | 277.7 | 234.9 | 244.2 | 259.1
2331 | 2231 | 376 | 279.8 | 277.8 | 235 | 244.4 | 259.1
2332 | 2232 | 375.9 | 279.9 | 277.8 | 235 | 244.7 | 259.6
2333 | 2233 | 375.8 | 280 | 277.8 | 235.1 | 244.7 | 260.1
2334 | 2234 | 375.7 | 280 | 277.9 | 235.1 | 244.6 | 260.2
2335 | 2235 | 375.8 | 280.1 | 277.9 | 235.1 | 245 | 260.1
2336 | 2236 | 375.8 | 280.1 | 278 | 235.2 | 245.2 | 260.1
2337 | 2237 | 375.7 | 280.2 | 278 | 235.2 | 245.3 | 260.1
2338 | 2238 | 375.7 | 280.3 | 278 | 235.2 | 245.7 | 260.1
2339 | 2239 | 375.7 | 280.4 | 278.1 | 235.3 | 246.4 | 260.2
2340 | 2240 | 375.7 | 280.4 | 278.2 | 235.3 | 246.3 | 260.2
2341 | 2241 | 375.8 | 280.4 | 278.2 | 235.3 | 246.1 | 260.2
2342 | 2242 | 375.6 | 280.5 | 278.3 | 235.4 | 246 | 260.2
2343 | 2243 | 375.7 | 280.5 | 278.3 | 235.4 | 245.3 | 260.2
2344 | 2244 | 375.7 | 280.5 | 278.4 | 235.4 | 245.3 | 260.3
2345 | 2245 | 375.7 | 280.5 | 278.4 | 235.5 | 244.9 | 260.3
2346 | 2246 | 375.7 | 280.5 | 278.5 | 235.5 | 245 | 260.3
2347 | 2247 | 375.8 | 280.6 | 278.5 | 235.6 | 244.8 | 260.3
2348 | 2248 | 376.1 | 280.7 | 278.6 | 235.6 | 245.4 | 260.2
2349 | 2249 | 376.2 | 280.6 | 278.7 | 235.6 | 246.3 | 260.2
2350 | 2250 | 376.3 | 280.6 | 278.7 | 235.6 | 246.1 | 260.1
2351 | 2251 | 376.4 | 280.6 | 278.8 | 235.7 | 246.5 | 260.1
2352 | 2252 | 376.4 | 280.6 | 278.8 | 235.7 | 247.4 | 260.1
2353 | 2253 | 376.5 | 280.6 | 278.9 | 235.7 | 248 | 260.2
2354 | 2254 | 376.7 | 280.6 | 278.9 | 235.8 | 248.9 | 260.2
2355 | 2255 | 376.6 | 280.5 | 279 | 235.8 | 248.8 | 260.2
2356 | 2256 | 376.5 | 280.5 | 279.1 | 235.8 | 248.8 | 260.2
2357 | 2257 | 376.4 | 280.6 | 279.1 | 235.9 | 248.9 | 260.2
2358 | 2258 | 376.4 | 280.6 | 279.2 | 235.9 | 249.4 | 260.2
2359 | 2259 | 376.5 | 280.6 | 279.2 | 235.9 | 249.4 | 260.2
2360 | 2260 | 376.5 | 280.6 | 279.3 | 236 | 249.7 | 260.2
2361 | 2261 | 376.6 | 280.5 | 279.3 | 236 | 250 | 260.2
2362 | 2262 | 376.8 | 280.5 | 279.4 | 236 | 250.6 | 260.2
2363 | 2263 | 376.8 | 280.5 | 279.4 | 236.1 | 251.3 | 260.3
2364 | 2264 | 376.8 | 280.5 | 279.4 | 236.1 | 251.2 | 260.3
2365 | 2265 | 376.8 | 280.6 | 279.5 | 236.1 | 251.2 | 260.3
2366 | 2266 | 376.8 | 280.6 | 279.5 | 236.2 | 251.7 | 260.3
2367 | 2267 | 376.7 | 280.6 | 279.6 | 236.2 | 251.7 | 260.3
2368 | 2268 | 376.6 | 280.6 | 279.6 | 236.2 | 251.9 | 260.3
2369 | 2269 | 376.6 | 280.5 | 279.6 | 236.3 | 252 | 260.3
2370 | 2270 | 376.7 | 280.5 | 279.6 | 236.3 | 251.8 | 260.3
2371 | 2271 | 376.8 | 280.6 | 279.7 | 236.3 | 251.5 | 260.3
2372 | 2272 | 376.7 | 280.7 | 279.7 | 236.3 | 251.3 | 260.4
2373 | 2273 | 376.6 | 280.7 | 279.8 | 236.4 | 251 | 260.4
2374 | 2274 | 376.7 | 280.7 | 279.8 | 236.4 | 250.6 | 260.4
2375 | 2275 | 376.7 | 280.7 | 279.9 | 236.5 | 251 | 260.4
2376 | 2276 | 376.8 | 280.6 | 279.9 | 236.5 | 250.7 | 260.5
2377 | 2277 | 376.8 | 280.5 | 280 | 236.5 | 250.6 | 260.5
2378 | 2278 | 376.9 | 280.5 | 280 | 236.5 | 250.1 | 260.5
2379 | 2279 | 377 | 280.5 | 280.1 | 236.6 | 250.1 | 260.5
2380 | 2280 | 377 | 280.4 | 280.2 | 236.6 | 249.8 | 260.5
2381 | 2281 | 377.1 | 280.5 | 280.2 | 236.6 | 249.8 | 260.5
2382 | 2282 | 377.2 | 280.5 | 280.3 | 236.7 | 249.5 | 260.5
2383 | 2283 | 377.2 | 280.6 | 280.3 | 236.7 | 249 | 260.5
2384 | 2284 | 377.1 | 280.6 | 280.3 | 236.7 | 249.2 | 260.5
2385 | 2285 | 377.1 | 280.6 | 280.4 | 236.8 | 249 | 260.5
2386 | 2286 | 377.2 | 280.7 | 280.4 | 236.8 | 248.8 | 260.5
2387 | 2287 | 377.4 | 280.7 | 280.5 | 236.8 | 248.3 | 260.5
2388 | 2288 | 377.3 | 280.8 | 280.5 | 236.9 | 248.3 | 260.5
2389 | 2289 | 377.3 | 280.9 | 280.6 | 236.9 | 248.3 | 260.5
2390 | 2290 | 377.3 | 280.9 | 280.7 | 236.9 | 247.9 | 260.5
2391 | 2291 | 377.2 | 281 | 280.7 | 237 | 247.3 | 260.5
2392 | 2292 | 376.9 | 281.1 | 280.8 | 237 | 247.4 | 260.5
2393 | 2293 | 376.9 | 281.2 | 280.8 | 237 | 247.7 | 260.5
2394 | 2294 | 376.9 | 281.2 | 280.8 | 237.1 | 247.7 | 260.5
2395 | 2295 | 377.1 | 281.2 | 280.8 | 237.1 | 247.4 | 260.4
2396 | 2296 | 377.2 | 281.3 | 280.8 | 237.1 | 247.9 | 260.5
2397 | 2297 | 377 | 281.3 | 280.8 | 237.1 | 248.1 | 260.5
2398 | 2298 | 376.9 | 281.3 | 280.9 | 237.2 | 248.6 | 260.5
2399 | 2299 | 376.8 | 281.4 | 280.9 | 237.2 | 249.3 | 260.5
2400 | 2300 | 376.6 | 281.5 | 280.9 | 237.2 | 249.6 | 260.4
2401 | 2301 | 376.6 | 281.5 | 281 | 237.3 | 249.3 | 260.4
2402 | 2302 | 376.5 | 281.5 | 281 | 237.3 | 249.6 | 260.4
2403 | 2303 | 376.4 | 281.4 | 281 | 237.3 | 249.6 | 260.4
2404 | 2304 | 376.4 | 281.4 | 281 | 237.4 | 248.9 | 260.4
2405 | 2305 | 376.3 | 281.5 | 281.1 | 237.4 | 248.4 | 260.3
2406 | 2306 | 376.1 | 281.5 | 281.1 | 237.4 | 248.2 | 260.3
2407 | 2307 | 376 | 281.6 | 281.1 | 237.5 | 248.5 | 260.3
2408 | 2308 | 376 | 281.6 | 281.2 | 237.5 | 248.9 | 260.2
2409 | 2309 | 375.9 | 281.6 | 281.2 | 237.5 | 249.1 | 260.2
2410 | 2310 | 375.9 | 281.7 | 281.2 | 237.6 | 248.9 | 260.3
2411 | 2311 | 375.7 | 281.7 | 281.3 | 237.6 | 249.2 | 260.3
2412 | 2312 | 375.6 | 281.6 | 281.3 | 237.6 | 249.5 | 260.3
2413 | 2313 | 375.7 | 281.6 | 281.3 | 237.7 | 249.6 | 260.3
2414 | 2314 | 375.7 | 281.6 | 281.4 | 237.7 | 249.4 | 260.2
2415 | 2315 | 375.7 | 281.5 | 281.4 | 237.7 | 249.5 | 260.2
2416 | 2316 | 375.6 | 281.5 | 281.4 | 237.8 | 249.3 | 260.2
2417 | 2317 | 375.7 | 281.6 | 281.4 | 237.8 | 249.4 | 260.2
2418 | 2318 | 375.6 | 281.6 | 281.4 | 237.8 | 249.4 | 260.2
2419 | 2319 | 375.6 | 281.5 | 281.4 | 237.8 | 249.4 | 260.2
2420 | 2320 | 375.6 | 281.5 | 281.4 | 237.9 | 249.5 | 260.1
2421 | 2321 | 375.9 | 281.5 | 281.4 | 237.9 | 249.9 | 260.2
2422 | 2322 | 376 | 281.6 | 281.4 | 237.9 | 250.3 | 260.1
2423 | 2323 | 375.9 | 281.6 | 281.4 | 238 | 250.1 | 260.1
2424 | 2324 | 375.8 | 281.6 | 281.4 | 238 | 249.8 | 260.1
2425 | 2325 | 375.8 | 281.7 | 281.5 | 238 | 249.4 | 260.1
2426 | 2326 | 375.8 | 281.8 | 281.5 | 238 | 249.4 | 260.1
2427 | 2327 | 375.8 | 281.8 | 281.5 | 238.1 | 250 | 260.1
2428 | 2328 | 375.6 | 281.9 | 281.5 | 238.1 | 249.8 | 260.1
2429 | 2329 | 375.6 | 282 | 281.6 | 238.1 | 249.7 | 260.1
2430 | 2330 | 375.7 | 282.1 | 281.6 | 238.2 | 250.1 | 260
2431 | 2331 | 375.6 | 282.3 | 281.6 | 238.2 | 250.3 | 260
2432 | 2332 | 375.4 | 282.3 | 281.6 | 238.2 | 250.7 | 260
2433 | 2333 | 375.4 | 282.4 | 281.6 | 238.2 | 251 | 259.9
2434 | 2334 | 375.4 | 282.5 | 281.6 | 238.3 | 251.2 | 260
2435 | 2335 | 375.4 | 282.5 | 281.7 | 238.3 | 251.8 | 259.9
2436 | 2336 | 375.4 | 282.5 | 281.7 | 238.3 | 252 | 259.9
2437 | 2337 | 375.3 | 282.5 | 281.7 | 238.3 | 252.4 | 260
2438 | 2338 | 375.3 | 282.6 | 281.7 | 238.4 | 252.9 | 260
2439 | 2339 | 375.3 | 282.6 | 281.7 | 238.4 | 253.2 | 260
2440 | 2340 | 375.3 | 282.7 | 281.7 | 238.4 | 253.5 | 260.1
2441 | 2341 | 375.3 | 282.7 | 281.7 | 238.5 | 254 | 260.1
2442 | 2342 | 375.2 | 282.8 | 281.7 | 238.5 | 253.9 | 260.1
2443 | 2343 | 375.3 | 282.8 | 281.7 | 238.5 | 254 | 260.1
2444 | 2344 | 375.3 | 282.9 | 281.8 | 238.5 | 253.9 | 260.1
2445 | 2345 | 375.3 | 282.9 | 281.8 | 238.6 | 254.2 | 260.1
2446 | 2346 | 375.3 | 283 | 281.8 | 238.6 | 254.5 | 260.2
2447 | 2347 | 375.4 | 283 | 281.8 | 238.6 | 254.5 | 260.2
2448 | 2348 | 375.5 | 283.1 | 281.9 | 238.7 | 254.5 | 260.2
2449 | 2349 | 375.5 | 283.2 | 281.9 | 238.7 | 254.2 | 260.2
2450 | 2350 | 375.6 | 283.3 | 281.9 | 238.7 | 254 | 260.3
2451 | 2351 | 375.7 | 283.3 | 282 | 238.7 | 253.9 | 260.3
2452 | 2352 | 375.7 | 283.4 | 282 | 238.8 | 253.8 | 260.3
2453 | 2353 | 375.9 | 283.4 | 282 | 238.8 | 253.7 | 260.3
2454 | 2354 | 376 | 283.4 | 282.1 | 238.8 | 253.2 | 260.3
2455 | 2355 | 376 | 283.4 | 282.1 | 238.8 | 253.1 | 260.3
2456 | 2356 | 376 | 283.4 | 282.1 | 238.9 | 252.9 | 260.3
2457 | 2357 | 376 | 283.4 | 282.2 | 238.9 | 252.8 | 260.3
2458 | 2358 | 376.1 | 283.3 | 282.2 | 238.9 | 252.7 | 260.4
2459 | 2359 | 376.3 | 283.3 | 282.2 | 238.9 | 252.6 | 260.4
2460 | 2360 | 376.4 | 283.3 | 282.3 | 239 | 252.6 | 260.5
2461 | 2361 | 376.6 | 283.3 | 282.3 | 239 | 252.5 | 260.5
2462 | 2362 | 376.7 | 283.4 | 282.4 | 239 | 251.9 | 260.5
2463 | 2363 | 376.7 | 283.5 | 282.4 | 239.1 | 251.8 | 260.6
2464 | 2364 | 376.7 | 283.5 | 282.4 | 239.1 | 251.6 | 260.6
2465 | 2365 | 376.7 | 283.6 | 282.5 | 239.1 | 251.3 | 260.6
2466 | 2366 | 376.8 | 283.7 | 282.5 | 239.1 | 251.5 | 260.6
2467 | 2367 | 376.7 | 283.7 | 282.6 | 239.2 | 251.7 | 260.6
2468 | 2368 | 376.6 | 283.8 | 282.6 | 239.2 | 251.7 | 260.6
2469 | 2369 | 376.5 | 283.9 | 282.7 | 239.2 | 251.1 | 260.6
2470 | 2370 | 376.4 | 284 | 282.8 | 239.2 | 250.5 | 260.7
2471 | 2371 | 376.2 | 284.1 | 282.8 | 239.3 | 250.7 | 260.7
2472 | 2372 | 376 | 284.1 | 282.8 | 239.3 | 250.3 | 260.8
2473 | 2373 | 375.9 | 284.2 | 282.9 | 239.3 | 250.3 | 260.8
2474 | 2374 | 375.7 | 284.2 | 282.9 | 239.4 | 250.1 | 260.8
2475 | 2375 | 375.7 | 284.3 | 283 | 239.4 | 249.8 | 260.8
2476 | 2376 | 375.7 | 284.4 | 283 | 239.4 | 250.1 | 260.8
2477 | 2377 | 375.7 | 284.4 | 283 | 239.4 | 250.2 | 260.9
2478 | 2378 | 375.7 | 284.5 | 283.1 | 239.5 | 250.1 | 260.9
2479 | 2379 | 375.6 | 284.5 | 283.1 | 239.5 | 250 | 260.9
2480 | 2380 | 375.7 | 284.5 | 283.1 | 239.5 | 250 | 260.8
2481 | 2381 | 375.6 | 284.5 | 283.2 | 239.6 | 250 | 260.9
2482 | 2382 | 375.4 | 284.5 | 283.2 | 239.6 | 250 | 260.9
2483 | 2383 | 375.3 | 284.5 | 283.3 | 239.6 | 249.7 | 260.9
2484 | 2384 | 375.3 | 284.4 | 283.3 | 239.6 | 249.9 | 260.9
2485 | 2385 | 375.2 | 284.4 | 283.3 | 239.7 | 250.4 | 260.9
2486 | 2386 | 375.1 | 284.4 | 283.3 | 239.7 | 250.4 | 260.9
2487 | 2387 | 374.9 | 284.3 | 283.4 | 239.7 | 250.7 | 260.9
2488 | 2388 | 374.8 | 284.3 | 283.4 | 239.8 | 251 | 260.9
2489 | 2389 | 374.6 | 284.3 | 283.4 | 239.8 | 250.9 | 260.9
2490 | 2390 | 374.6 | 284.3 | 283.4 | 239.8 | 250.7 | 260.9
2491 | 2391 | 374.8 | 284.3 | 283.4 | 239.8 | 250.9 | 260.9
2492.1 | 2392.1 | 374.9 | 284.3 | 283.4 | 239.9 | 250.8 | 261
2493.1 | 2393.1 | 375 | 284.4 | 283.5 | 239.9 | 250.9 | 261
2494.1 | 2394.1 | 375 | 284.5 | 283.5 | 239.9 | 251 | 261.1
2495.1 | 2395.1 | 375.3 | 284.7 | 283.5 | 240 | 250.6 | 261.1
2496.1 | 2396.1 | 375.6 | 284.8 | 283.6 | 240 | 250.4 | 261.2
2497.1 | 2397.1 | 375.7 | 284.8 | 283.6 | 240 | 250.2 | 261.2
2498.1 | 2398.1 | 375.7 | 284.9 | 283.7 | 240 | 250.2 | 261.2
2499.1 | 2399.1 | 375.9 | 284.9 | 283.8 | 240.1 | 250.2 | 261.1
2500.1 | 2400.1 | 376 | 285 | 283.9 | 240.1 | 250.7 | 261.1
2501.1 | 2401.1 | 376.1 | 285.1 | 283.9 | 240.1 | 250.9 | 261.1
2502.1 | 2402.1 | 376 | 285.2 | 284 | 240.1 | 251.2 | 261
2503.1 | 2403.1 | 376.2 | 285.3 | 284.1 | 240.2 | 251 | 261
2504.1 | 2404.1 | 376.3 | 285.3 | 284.2 | 240.2 | 251 | 261
2505.1 | 2405.1 | 376.4 | 285.3 | 284.2 | 240.2 | 251.1 | 261.1
2506.1 | 2406.1 | 376.4 | 285.4 | 284.3 | 240.3 | 251 | 261.1
2507.1 | 2407.1 | 376.7 | 285.5 | 284.4 | 240.3 | 251.1 | 261.1
2508.1 | 2408.1 | 376.8 | 285.5 | 284.5 | 240.3 | 251.4 | 261.1
2509.1 | 2409.1 | 377 | 285.5 | 284.6 | 240.3 | 251.6 | 261.1
2510.1 | 2410.1 | 377 | 285.5 | 284.6 | 240.4 | 251.8 | 261.2
2511.1 | 2411.1 | 376.9 | 285.5 | 284.7 | 240.4 | 251.6 | 261.2
2512.1 | 2412.1 | 377 | 285.6 | 284.7 | 240.4 | 251.4 | 261.2
2513.1 | 2413.1 | 377.1 | 285.7 | 284.8 | 240.4 | 251.6 | 261.1
2514.1 | 2414.1 | 377.1 | 285.9 | 284.8 | 240.5 | 251.5 | 261.1
2515.1 | 2415.1 | 376.9 | 286 | 284.8 | 240.5 | 251.3 | 261
2516.1 | 2416.1 | 376.9 | 286.1 | 284.8 | 240.5 | 251 | 261.1
2517.1 | 2417.1 | 376.9 | 286.1 | 284.8 | 240.5 | 251.1 | 261.1
2518.1 | 2418.1 | 376.9 | 286.1 | 284.9 | 240.6 | 251.2 | 261.1
2519.1 | 2419.1 | 376.9 | 286.2 | 284.9 | 240.6 | 251.3 | 261.1
2520.1 | 2420.1 | 376.8 | 286.2 | 285 | 240.6 | 250.9 | 261.1
2521.1 | 2421.1 | 376.6 | 286.2 | 285.1 | 240.7 | 250.4 | 261.1
2522.1 | 2422.1 | 376.6 | 286.2 | 285.1 | 240.7 | 250.4 | 261.1
2523.1 | 2423.1 | 376.7 | 286.3 | 285.2 | 240.7 | 250.2 | 261.1
2524.1 | 2424.1 | 376.8 | 286.4 | 285.2 | 240.7 | 250.1 | 261.1
2525.1 | 2425.1 | 376.9 | 286.4 | 285.3 | 240.8 | 250.5 | 261.1
2526.1 | 2426.1 | 376.9 | 286.4 | 285.3 | 240.8 | 250.4 | 261.1
2527.1 | 2427.1 | 376.8 | 286.5 | 285.4 | 240.8 | 250.5 | 261.1
2528.1 | 2428.1 | 376.8 | 286.6 | 285.4 | 240.8 | 250.4 | 261.1
2529.1 | 2429.1 | 376.8 | 286.7 | 285.5 | 240.9 | 250.3 | 261.1
2530.1 | 2430.1 | 376.7 | 286.7 | 285.5 | 240.9 | 250.4 | 261.1
2531.1 | 2431.1 | 376.8 | 286.7 | 285.5 | 240.9 | 250.6 | 261.1
2532.1 | 2432.1 | 376.8 | 286.9 | 285.6 | 240.9 | 250.8 | 261
2533.1 | 2433.1 | 376.9 | 286.9 | 285.6 | 241 | 250.7 | 261.1
2534.1 | 2434.1 | 377 | 286.9 | 285.6 | 241 | 250.9 | 261.1
2535.1 | 2435.1 | 376.9 | 287 | 285.6 | 241 | 251.3 | 261.1
2536.1 | 2436.1 | 377 | 287 | 285.6 | 241 | 251 | 261.1
2537.1 | 2437.1 | 377 | 287 | 285.7 | 241.1 | 251.1 | 261.1
2538.1 | 2438.1 | 377.1 | 287.1 | 285.8 | 241.1 | 251.4 | 261.1
2539.1 | 2439.1 | 376.9 | 287.2 | 285.9 | 241.1 | 251.1 | 261.1
2540.1 | 2440.1 | 377 | 287.3 | 286 | 241.1 | 250.7 | 261.1
2541.1 | 2441.1 | 376.8 | 287.4 | 286.1 | 241.1 | 250.2 | 261.1
2542.1 | 2442.1 | 376.7 | 287.5 | 286.1 | 241.2 | 249.9 | 261
2543.1 | 2443.1 | 376.6 | 287.5 | 286.2 | 241.2 | 250.2 | 261
2544.1 | 2444.1 | 376.5 | 287.5 | 286.2 | 241.2 | 250.4 | 261
2545.1 | 2445.1 | 376.4 | 287.6 | 286.2 | 241.2 | 250.9 | 261
2546.1 | 2446.1 | 376.3 | 287.6 | 286.3 | 241.3 | 251.3 | 261
2547.1 | 2447.1 | 376.1 | 287.6 | 286.3 | 241.3 | 251.1 | 261
2548.1 | 2448.1 | 376 | 287.6 | 286.3 | 241.3 | 251 | 261
2549.1 | 2449.1 | 376 | 287.6 | 286.4 | 241.3 | 250.8 | 261
2550.1 | 2450.1 | 376 | 287.6 | 286.4 | 241.3 | 250.9 | 261
2551.1 | 2451.1 | 375.9 | 287.6 | 286.4 | 241.4 | 250.5 | 261
2552.1 | 2452.1 | 375.8 | 287.7 | 286.5 | 241.4 | 250.9 | 260.9
2553.1 | 2453.1 | 375.8 | 287.7 | 286.6 | 241.4 | 251.3 | 260.9
2554.1 | 2454.1 | 375.7 | 287.7 | 286.6 | 241.4 | 251.7 | 260.9
2555.1 | 2455.1 | 375.7 | 287.7 | 286.6 | 241.5 | 251.5 | 260.9
2556.1 | 2456.1 | 375.6 | 287.8 | 286.6 | 241.5 | 251.7 | 260.9
2557.1 | 2457.1 | 375.6 | 287.8 | 286.6 | 241.5 | 251.7 | 260.9
2558.1 | 2458.1 | 375.6 | 287.8 | 286.7 | 241.5 | 251.9 | 260.9
2559.1 | 2459.1 | 375.5 | 287.7 | 286.7 | 241.6 | 251.9 | 260.9
2560.1 | 2460.1 | 375.4 | 287.6 | 286.7 | 241.6 | 252.1 | 260.9
2561.1 | 2461.1 | 375.4 | 287.5 | 286.7 | 241.6 | 252 | 260.9
2562.1 | 2462.1 | 375.5 | 287.4 | 286.7 | 241.6 | 251.4 | 260.9
2563.1 | 2463.1 | 375.6 | 287.3 | 286.7 | 241.6 | 251.1 | 260.9
2564.1 | 2464.1 | 375.5 | 287.2 | 286.8 | 241.7 | 250.9 | 260.9
2565.1 | 2465.1 | 375.6 | 287.2 | 286.9 | 241.7 | 251.1 | 260.9
2566.1 | 2466.1 | 375.6 | 287.2 | 286.9 | 241.7 | 251.1 | 260.9
2567.1 | 2467.1 | 375.5 | 287.3 | 287 | 241.7 | 251.2 | 260.9
2568.1 | 2468.1 | 375.4 | 287.3 | 287 | 241.7 | 251.4 | 260.9
2569.1 | 2469.1 | 375.3 | 287.4 | 287 | 241.8 | 251.6 | 261
2570.1 | 2470.1 | 375.2 | 287.3 | 287 | 241.8 | 251.8 | 261
2571.1 | 2471.1 | 375 | 287.3 | 287 | 241.8 | 251.5 | 261
2572.1 | 2472.1 | 374.9 | 287.3 | 287 | 241.8 | 251.6 | 261
2573.1 | 2473.1 | 374.8 | 287.3 | 287.1 | 241.9 | 251.9 | 261
2574.1 | 2474.1 | 374.8 | 287.3 | 287.1 | 241.9 | 252.3 | 261.1
2575.1 | 2475.1 | 374.9 | 287.3 | 287.1 | 241.9 | 252.5 | 261.1
2576.1 | 2476.1 | 375 | 287.3 | 287.2 | 241.9 | 252.3 | 261.2
2577.1 | 2477.1 | 375.1 | 287.3 | 287.2 | 241.9 | 252.3 | 261.2
2578.1 | 2478.1 | 375.1 | 287.3 | 287.2 | 241.9 | 252.4 | 261.1
2579.1 | 2479.1 | 375 | 287.3 | 287.2 | 242 | 252.5 | 261.1
2580.1 | 2480.1 | 375 | 287.4 | 287.2 | 242 | 252.5 | 261.1
2581.1 | 2481.1 | 374.9 | 287.4 | 287.2 | 242 | 252.4 | 261.1
2582.1 | 2482.1 | 374.9 | 287.4 | 287.2 | 242 | 252.3 | 261.2
2583.1 | 2483.1 | 374.8 | 287.5 | 287.2 | 242 | 252.3 | 261.2
2584.1 | 2484.1 | 374.8 | 287.5 | 287.2 | 242.1 | 252.7 | 261.2
2585.1 | 2485.1 | 374.8 | 287.6 | 287.2 | 242.1 | 252.8 | 261.2
2586.1 | 2486.1 | 375 | 287.6 | 287.2 | 242.1 | 253.1 | 261.2
2587.1 | 2487.1 | 375.1 | 287.7 | 287.3 | 242.1 | 253 | 261.2
2588.1 | 2488.1 | 375.1 | 287.7 | 287.3 | 242.1 | 253.1 | 261.3
2589.1 | 2489.1 | 375.1 | 287.7 | 287.3 | 242.2 | 252.9 | 261.3
2590.1 | 2490.1 | 375.1 | 287.7 | 287.3 | 242.2 | 252.9 | 261.3
2591.1 | 2491.1 | 375.2 | 287.7 | 287.3 | 242.2 | 253 | 261.3
2592.1 | 2492.1 | 375.2 | 287.7 | 287.3 | 242.2 | 253.3 | 261.3
2593.1 | 2493.1 | 375.2 | 287.7 | 287.3 | 242.3 | 253.2 | 261.3
2594.1 | 2494.1 | 375.3 | 287.7 | 287.4 | 242.3 | 252.7 | 261.5
2595.1 | 2495.1 | 375.3 | 287.8 | 287.4 | 242.3 | 252.8 | 261.5
2596.1 | 2496.1 | 375.4 | 287.8 | 287.4 | 242.3 | 253.2 | 261.6
2597.1 | 2497.1 | 375.4 | 287.8 | 287.5 | 242.3 | 253.4 | 261.6
2598.1 | 2498.1 | 375.5 | 287.9 | 287.5 | 242.4 | 253.4 | 261.5
2599.1 | 2499.1 | 375.7 | 287.9 | 287.5 | 242.4 | 253.4 | 261.5
2600.1 | 2500.1 | 375.9 | 287.9 | 287.6 | 242.4 | 253.8 | 261.5
2601.1 | 2501.1 | 376 | 288 | 287.6 | 242.4 | 254 | 261.5
2602.1 | 2502.1 | 376 | 288 | 287.6 | 242.4 | 254.3 | 261.5
2603.1 | 2503.1 | 376 | 288 | 287.6 | 242.5 | 254.1 | 261.5
2604.1 | 2504.1 | 376.1 | 288 | 287.7 | 242.5 | 254.1 | 261.5
2605.1 | 2505.1 | 376 | 288.1 | 287.7 | 242.5 | 254.3 | 261.5
2606.1 | 2506.1 | 376.1 | 288.1 | 287.7 | 242.5 | 254.4 | 261.6
2607.1 | 2507.1 | 376.2 | 288.1 | 287.7 | 242.5 | 254.4 | 261.6
2608.1 | 2508.1 | 376.3 | 288.1 | 287.7 | 242.6 | 254 | 261.6
2609.1 | 2509.1 | 376.4 | 288.2 | 287.7 | 242.6 | 254 | 261.6
2610.1 | 2510.1 | 376.4 | 288.4 | 287.7 | 242.6 | 253.9 | 261.6
2611.1 | 2511.1 | 376.4 | 288.6 | 287.7 | 242.6 | 253.8 | 261.7
2612.1 | 2512.1 | 376.4 | 288.7 | 287.7 | 242.7 | 253.6 | 261.7
2613.1 | 2513.1 | 376.5 | 288.8 | 287.8 | 242.7 | 253.6 | 261.7
2614.1 | 2514.1 | 376.4 | 288.8 | 287.8 | 242.7 | 253.5 | 261.8
2615.1 | 2515.1 | 376.2 | 288.8 | 287.8 | 242.7 | 253.3 | 261.8
2616.1 | 2516.1 | 376.1 | 288.8 | 287.9 | 242.7 | 253.5 | 261.8
2617.1 | 2517.1 | 376 | 288.8 | 287.9 | 242.8 | 253.4 | 261.8
2618.1 | 2518.1 | 375.8 | 288.8 | 288 | 242.8 | 253.5 | 261.8
2619.1 | 2519.1 | 375.7 | 288.9 | 288 | 242.8 | 254 | 261.8
2620.1 | 2520.1 | 375.6 | 288.8 | 288 | 242.9 | 254.5 | 261.8
2621.1 | 2521.1 | 375.5 | 288.9 | 288 | 242.9 | 254.6 | 261.8
2622.1 | 2522.1 | 375.5 | 289 | 288 | 242.9 | 254.5 | 261.8
2623.1 | 2523.1 | 375.5 | 289 | 288.1 | 242.9 | 254.4 | 261.8
2624.1 | 2524.1 | 375.4 | 289 | 288.1 | 242.9 | 254.6 | 261.8
2625.1 | 2525.1 | 375.3 | 289 | 288.1 | 243 | 254.6 | 261.9
2626.1 | 2526.1 | 375.1 | 289 | 288.1 | 243 | 255 | 261.9
2627.1 | 2527.1 | 375 | 289.1 | 288.2 | 243 | 255 | 261.9
2628.1 | 2528.1 | 375 | 289.1 | 288.2 | 243 | 254.9 | 261.9
2629.1 | 2529.1 | 375 | 289.1 | 288.3 | 243.1 | 254.9 | 261.9
2630.1 | 2530.1 | 374.9 | 289.1 | 288.3 | 243.1 | 255 | 261.9
2631.1 | 2531.1 | 374.8 | 289.2 | 288.3 | 243.1 | 255.4 | 262
2632.1 | 2532.1 | 374.6 | 289.2 | 288.3 | 243.2 | 255.4 | 262
2633.1 | 2533.1 | 374.5 | 289.2 | 288.4 | 243.2 | 255.2 | 262
2634.1 | 2534.1 | 374.4 | 289.2 | 288.4 | 243.2 | 255.1 | 262
2635.1 | 2535.1 | 374.3 | 289.2 | 288.4 | 243.2 | 255.2 | 262
2636.1 | 2536.1 | 374.1 | 289.2 | 288.5 | 243.3 | 255.4 | 262
2637.1 | 2537.1 | 374 | 289.2 | 288.5 | 243.3 | 255.5 | 262
2638.1 | 2538.1 | 374 | 289.2 | 288.6 | 243.3 | 255.4 | 262
2639.1 | 2539.1 | 373.9 | 289.2 | 288.6 | 243.3 | 255.3 | 262.1
2640.1 | 2540.1 | 374 | 289.1 | 288.7 | 243.4 | 254.7 | 262.1
2641.1 | 2541.1 | 374 | 289.1 | 288.7 | 243.4 | 254.5 | 262.2
2642.1 | 2542.1 | 374 | 289.1 | 288.8 | 243.4 | 254.9 | 262.2
2643.1 | 2543.1 | 373.9 | 289 | 288.8 | 243.4 | 254.8 | 262.3
2644.1 | 2544.1 | 374 | 288.9 | 288.8 | 243.4 | 254.7 | 262.4
2645.1 | 2545.1 | 374.2 | 288.9 | 288.8 | 243.5 | 254.9 | 262.4
2646.1 | 2546.1 | 374.3 | 288.9 | 288.9 | 243.5 | 255 | 262.3
2647.1 | 2547.1 | 374.4 | 288.9 | 288.9 | 243.5 | 255 | 262.2
2648.1 | 2548.1 | 374.4 | 288.9 | 289 | 243.5 | 255 | 262.2
2649.1 | 2549.1 | 374.4 | 288.9 | 289 | 243.5 | 254.8 | 262.2
2650.1 | 2550.1 | 374.5 | 289 | 289 | 243.6 | 254.8 | 262.3
2651.1 | 2551.1 | 374.7 | 289 | 289 | 243.6 | 255.1 | 262.3
2652.1 | 2552.1 | 374.9 | 289.1 | 289 | 243.6 | 255.3 | 262.3
2653.1 | 2553.1 | 375.1 | 289.1 | 289.1 | 243.6 | 255.1 | 262.4
2654.1 | 2554.1 | 375.1 | 289.1 | 289.1 | 243.7 | 254.6 | 262.3
2655.1 | 2555.1 | 375.3 | 289.1 | 289.1 | 243.7 | 254.4 | 262.3
2656.1 | 2556.1 | 375.4 | 289.2 | 289.2 | 243.7 | 254 | 262.3
2657.1 | 2557.1 | 375.5 | 289.2 | 289.2 | 243.7 | 253.8 | 262.3
2658.1 | 2558.1 | 375.6 | 289.2 | 289.3 | 243.7 | 253.9 | 262.4
2659.1 | 2559.1 | 375.6 | 289.3 | 289.4 | 243.7 | 254 | 262.3
2660.1 | 2560.1 | 375.6 | 289.3 | 289.4 | 243.8 | 254.1 | 262.3
2661.1 | 2561.1 | 375.6 | 289.3 | 289.5 | 243.8 | 254.2 | 262.3
2662.1 | 2562.1 | 375.6 | 289.3 | 289.6 | 243.8 | 253.9 | 262.3
2663.1 | 2563.1 | 375.7 | 289.4 | 289.7 | 243.8 | 253.8 | 262.3
2664.1 | 2564.1 | 375.7 | 289.4 | 289.7 | 243.9 | 253.9 | 262.3
2665.1 | 2565.1 | 375.8 | 289.5 | 289.8 | 243.9 | 254.2 | 262.3
2666.1 | 2566.1 | 375.9 | 289.6 | 289.9 | 243.9 | 254.2 | 262.3
2667.1 | 2567.1 | 376 | 289.7 | 290 | 243.9 | 254.2 | 262.3
2668.1 | 2568.1 | 375.9 | 289.8 | 290 | 243.9 | 254.6 | 262.3
2669.1 | 2569.1 | 375.9 | 290 | 290 | 244 | 254.5 | 262.2
2670.1 | 2570.1 | 375.7 | 290 | 290.1 | 244 | 254.8 | 262.2
2671.1 | 2571.1 | 375.6 | 290 | 290.1 | 244 | 255.1 | 262.2
2672.1 | 2572.1 | 375.7 | 290 | 290.1 | 244.1 | 255.1 | 262.2
2673.1 | 2573.1 | 375.7 | 290 | 290.2 | 244.1 | 255.3 | 262.3
2674.1 | 2574.1 | 375.8 | 290.1 | 290.2 | 244.1 | 255.7 | 262.3
2675.1 | 2575.1 | 375.6 | 290.1 | 290.3 | 244.1 | 255.8 | 262.3
2676.1 | 2576.1 | 375.4 | 290.2 | 290.3 | 244.2 | 255.7 | 262.3
2677.1 | 2577.1 | 375.4 | 290.2 | 290.4 | 244.2 | 255.6 | 262.3
2678.1 | 2578.1 | 375.3 | 290.2 | 290.3 | 244.2 | 255.8 | 262.3
2679.1 | 2579.1 | 375.3 | 290.2 | 290.3 | 244.2 | 256.1 | 262.3
2680.1 | 2580.1 | 375.2 | 290.2 | 290.4 | 244.3 | 255.8 | 262.3
2681.1 | 2581.1 | 375.2 | 290.2 | 290.4 | 244.3 | 255.8 | 262.4
2682.1 | 2582.1 | 375.1 | 290.2 | 290.4 | 244.3 | 255.7 | 262.4
2683.1 | 2583.1 | 375 | 290.2 | 290.5 | 244.3 | 255.9 | 262.4
2684.1 | 2584.1 | 374.9 | 290.1 | 290.5 | 244.4 | 255.8 | 262.4
2685.1 | 2585.1 | 374.7 | 290.1 | 290.6 | 244.4 | 255.7 | 262.4
2686.1 | 2586.1 | 374.5 | 290 | 290.7 | 244.4 | 255.9 | 262.4
2687.1 | 2587.1 | 374.5 | 290 | 290.7 | 244.4 | 256.1 | 262.4
2688.1 | 2588.1 | 374.5 | 290 | 290.8 | 244.5 | 256.2 | 262.4
2689.1 | 2589.1 | 374.3 | 290 | 290.8 | 244.5 | 256.3 | 262.4
2690.1 | 2590.1 | 374.2 | 290.1 | 290.8 | 244.5 | 256 | 262.4
2691.1 | 2591.1 | 374 | 290.1 | 290.9 | 244.5 | 255.7 | 262.4
2692.1 | 2592.1 | 374 | 290.1 | 290.9 | 244.5 | 255.9 | 262.4
2693.1 | 2593.1 | 373.9 | 290.1 | 291 | 244.6 | 256.1 | 262.4
2694.1 | 2594.1 | 373.9 | 290.1 | 291 | 244.6 | 256.1 | 262.4
2695.1 | 2595.1 | 373.9 | 290.2 | 291.1 | 244.6 | 256 | 262.3
2696.1 | 2596.1 | 373.9 | 290.1 | 291.1 | 244.6 | 255.7 | 262.3
2697.1 | 2597.1 | 374 | 290.1 | 291.1 | 244.7 | 255.1 | 262.3
2698.1 | 2598.1 | 374.1 | 290.1 | 291.1 | 244.7 | 255.2 | 262.4
2699.1 | 2599.1 | 374.1 | 290.1 | 291.2 | 244.7 | 255.3 | 262.4
2700.1 | 2600.1 | 373.9 | 290 | 291.2 | 244.7 | 255.6 | 262.3
2701.1 | 2601.1 | 373.9 | 290.1 | 291.2 | 244.8 | 255.8 | 262.4
2702.1 | 2602.1 | 373.9 | 290.2 | 291.2 | 244.8 | 255.7 | 262.4
2703.1 | 2603.1 | 373.8 | 290.3 | 291.2 | 244.8 | 255.5 | 262.4
2704.1 | 2604.1 | 373.8 | 290.3 | 291.3 | 244.8 | 255.6 | 262.4
2705.1 | 2605.1 | 373.7 | 290.3 | 291.3 | 244.9 | 255.8 | 262.4
2706.1 | 2606.1 | 373.6 | 290.3 | 291.4 | 244.9 | 255.9 | 262.4
2707.1 | 2607.1 | 373.7 | 290.4 | 291.4 | 244.9 | 255.7 | 262.4
2708.1 | 2608.1 | 373.7 | 290.4 | 291.5 | 244.9 | 255.9 | 262.4
2709.1 | 2609.1 | 373.7 | 290.4 | 291.5 | 245 | 256.1 | 262.4
2710.1 | 2610.1 | 373.9 | 290.4 | 291.5 | 245 | 256.4 | 262.4
2711.1 | 2611.1 | 373.9 | 290.4 | 291.5 | 245 | 256.3 | 262.4
2712.1 | 2612.1 | 374 | 290.4 | 291.6 | 245 | 256.3 | 262.4
2713.1 | 2613.1 | 374 | 290.4 | 291.6 | 245.1 | 256.1 | 262.4
2714.1 | 2614.1 | 374 | 290.4 | 291.6 | 245.1 | 255.9 | 262.3
2715.1 | 2615.1 | 373.9 | 290.4 | 291.7 | 245.1 | 255.9 | 262.3
2716.1 | 2616.1 | 373.8 | 290.4 | 291.7 | 245.1 | 255.9 | 262.3
2717.1 | 2617.1 | 373.8 | 290.5 | 291.7 | 245.1 | 256.1 | 262.3
2718.1 | 2618.1 | 373.8 | 290.5 | 291.8 | 245.2 | 256.2 | 262.3
2719.1 | 2619.1 | 373.8 | 290.6 | 291.8 | 245.2 | 256.3 | 262.3
2720.1 | 2620.1 | 373.7 | 290.7 | 291.9 | 245.2 | 256.3 | 262.3
2721.1 | 2621.1 | 373.7 | 290.8 | 291.9 | 245.2 | 256.2 | 262.2
2722.1 | 2622.1 | 373.8 | 291 | 291.9 | 245.3 | 256.3 | 262.2
2723.1 | 2623.1 | 373.7 | 291.1 | 291.9 | 245.3 | 256.4 | 262.2
2724.1 | 2624.1 | 373.6 | 291.1 | 291.9 | 245.3 | 256.1 | 262.2
2725.1 | 2625.1 | 373.5 | 291.2 | 291.8 | 245.3 | 255.7 | 262.2
2726.1 | 2626.1 | 373.4 | 291.3 | 291.9 | 245.4 | 255.7 | 262.1
2727.1 | 2627.1 | 373.4 | 291.5 | 292 | 245.4 | 255.3 | 262.1
2728.1 | 2628.1 | 373.4 | 291.6 | 292 | 245.4 | 255.1 | 262.1
2729.1 | 2629.1 | 373.5 | 291.6 | 292.1 | 245.4 | 255.2 | 262
2730.1 | 2630.1 | 373.6 | 291.7 | 292.1 | 245.4 | 255.4 | 262
2731.1 | 2631.1 | 373.6 | 291.9 | 292.2 | 245.5 | 255.4 | 261.9
2732.1 | 2632.1 | 373.6 | 292 | 292.2 | 245.5 | 255.3 | 261.9
2733.1 | 2633.1 | 373.6 | 292 | 292.3 | 245.5 | 255.2 | 261.9
2734.1 | 2634.1 | 373.6 | 292 | 292.3 | 245.5 | 255.2 | 261.9
2735.1 | 2635.1 | 373.6 | 292.1 | 292.3 | 245.6 | 255.3 | 261.9
2736.1 | 2636.1 | 373.5 | 292.1 | 292.3 | 245.6 | 255.5 | 261.9
2737.1 | 2637.1 | 373.5 | 292.1 | 292.3 | 245.6 | 255.2 | 261.9
2738.1 | 2638.1 | 373.7 | 292.1 | 292.3 | 245.6 | 255.5 | 261.9
2739.1 | 2639.1 | 373.8 | 292.1 | 292.4 | 245.6 | 255.4 | 261.8
2740.1 | 2640.1 | 373.7 | 292 | 292.4 | 245.7 | 255.3 | 261.8
2741.1 | 2641.1 | 373.7 | 292 | 292.4 | 245.7 | 255.2 | 261.8
2742.1 | 2642.1 | 373.8 | 292.1 | 292.5 | 245.7 | 254.9 | 261.8
2743.1 | 2643.1 | 374 | 292.1 | 292.5 | 245.7 | 254.6 | 261.8
2744.1 | 2644.1 | 374 | 292.1 | 292.6 | 245.7 | 254.6 | 261.8
2745.1 | 2645.1 | 374.1 | 292.1 | 292.6 | 245.7 | 254.7 | 261.7
2746.1 | 2646.1 | 374.2 | 292.1 | 292.6 | 245.8 | 254.9 | 261.7
2747.1 | 2647.1 | 374.2 | 292.1 | 292.7 | 245.8 | 255.2 | 261.7
2748.1 | 2648.1 | 374.2 | 292.1 | 292.7 | 245.8 | 255.2 | 261.7
2749.1 | 2649.1 | 374.2 | 292.1 | 292.7 | 245.8 | 255.4 | 261.7
2750.1 | 2650.1 | 374.2 | 292.1 | 292.7 | 245.8 | 255.3 | 261.7
2751.1 | 2651.1 | 374.2 | 292.2 | 292.7 | 245.9 | 255.3 | 261.7
2752.1 | 2652.1 | 374.1 | 292.2 | 292.7 | 245.9 | 255.1 | 261.6
2753.1 | 2653.1 | 374 | 292.3 | 292.7 | 245.9 | 255.1 | 261.6
2754.1 | 2654.1 | 373.9 | 292.3 | 292.7 | 245.9 | 255.1 | 261.6
2755.1 | 2655.1 | 373.8 | 292.3 | 292.7 | 246 | 255.1 | 261.7
2756.1 | 2656.1 | 373.7 | 292.2 | 292.7 | 246 | 255.2 | 261.7
2757.1 | 2657.1 | 373.7 | 292.2 | 292.7 | 246 | 255.6 | 261.7
2758.1 | 2658.1 | 373.6 | 292.1 | 292.7 | 246 | 256 | 261.7
2759.1 | 2659.1 | 373.6 | 292.1 | 292.7 | 246 | 255.9 | 261.7
2760.1 | 2660.1 | 373.7 | 292.1 | 292.6 | 246.1 | 255.6 | 261.7
2761.1 | 2661.1 | 373.9 | 292.1 | 292.6 | 246.1 | 255.5 | 261.7
2762.1 | 2662.1 | 373.9 | 292.1 | 292.6 | 246.1 | 255.6 | 261.7
2763.1 | 2663.1 | 373.8 | 292.2 | 292.6 | 246.1 | 255.3 | 261.7
2764.1 | 2664.1 | 373.7 | 292.2 | 292.6 | 246.1 | 255 | 261.7
2765.1 | 2665.1 | 373.6 | 292.3 | 292.6 | 246.2 | 255.3 | 261.7
2766.1 | 2666.1 | 373.5 | 292.3 | 292.7 | 246.2 | 255.3 | 261.6
2767.1 | 2667.1 | 373.5 | 292.3 | 292.7 | 246.2 | 255.3 | 261.6
2768.1 | 2668.1 | 373.6 | 292.4 | 292.8 | 246.2 | 255 | 261.6
2769.1 | 2669.1 | 373.6 | 292.4 | 292.8 | 246.3 | 254.6 | 261.6
2770.1 | 2670.1 | 373.4 | 292.4 | 292.8 | 246.3 | 254.7 | 261.6
2771.1 | 2671.1 | 373.4 | 292.5 | 292.8 | 246.3 | 254.8 | 261.6
2772.1 | 2672.1 | 373.5 | 292.5 | 292.8 | 246.3 | 254.7 | 261.6
2773.1 | 2673.1 | 373.6 | 292.5 | 292.8 | 246.4 | 254.7 | 261.6
2774.1 | 2674.1 | 373.6 | 292.5 | 292.9 | 246.4 | 254.7 | 261.6
2775.1 | 2675.1 | 373.7 | 292.5 | 292.9 | 246.4 | 254.9 | 261.6
2776.1 | 2676.1 | 373.8 | 292.5 | 292.9 | 246.4 | 254.9 | 261.5
2777.1 | 2677.1 | 373.8 | 292.5 | 292.9 | 246.4 | 254.8 | 261.4
2778.1 | 2678.1 | 373.9 | 292.5 | 292.9 | 246.5 | 254.8 | 261.4
2779.1 | 2679.1 | 374.1 | 292.4 | 292.9 | 246.5 | 254.9 | 261.3
2780.1 | 2680.1 | 374.3 | 292.4 | 292.9 | 246.5 | 255.1 | 261.3
2781.1 | 2681.1 | 374.5 | 292.4 | 293 | 246.5 | 255.3 | 261.2
2782.1 | 2682.1 | 374.7 | 292.4 | 293 | 246.5 | 255.4 | 261.2
2783.1 | 2683.1 | 374.7 | 292.5 | 293 | 246.6 | 255.5 | 261.2
2784.1 | 2684.1 | 374.8 | 292.6 | 293 | 246.6 | 255.6 | 261.3
2785.1 | 2685.1 | 374.7 | 292.6 | 293 | 246.6 | 255.7 | 261.3
2786.1 | 2686.1 | 374.7 | 292.6 | 293.1 | 246.6 | 255.7 | 261.3
2787.1 | 2687.1 | 374.7 | 292.7 | 293.1 | 246.6 | 255.8 | 261.3
2788.1 | 2688.1 | 374.7 | 292.7 | 293.1 | 246.6 | 256.2 | 261.3
2789.1 | 2689.1 | 374.7 | 292.7 | 293.1 | 246.7 | 256.6 | 261.4
2790.1 | 2690.1 | 374.7 | 292.7 | 293.1 | 246.7 | 256.8 | 261.5
2791.1 | 2691.1 | 374.8 | 292.8 | 293 | 246.7 | 257.2 | 261.5
2792.1 | 2692.1 | 374.8 | 292.8 | 293 | 246.7 | 257.6 | 261.5
2793.1 | 2693.1 | 374.9 | 292.9 | 293 | 246.7 | 257.7 | 261.5
2794.1 | 2694.1 | 375.1 | 293 | 293 | 246.7 | 257.8 | 261.5
2795.1 | 2695.1 | 375.1 | 293 | 293 | 246.8 | 258 | 261.5
2796.1 | 2696.1 | 375.2 | 293.1 | 292.9 | 246.8 | 258.2 | 261.5
2797.1 | 2697.1 | 375.2 | 293.1 | 292.9 | 246.8 | 258.6 | 261.5
2798.1 | 2698.1 | 375.2 | 293.2 | 292.9 | 246.8 | 258.8 | 261.5
2799.1 | 2699.1 | 375.1 | 293.3 | 292.9 | 246.9 | 259 | 261.5
2800.1 | 2700.1 | 375.1 | 293.3 | 292.9 | 246.9 | 258.9 | 261.5
2801.1 | 2701.1 | 375 | 293.3 | 292.9 | 246.9 | 259.1 | 261.6
2802.1 | 2702.1 | 375.1 | 293.3 | 293 | 246.9 | 259.3 | 261.6
2803.1 | 2703.1 | 375.2 | 293.3 | 293 | 246.9 | 259.5 | 261.6
2804.1 | 2704.1 | 375.1 | 293.3 | 293 | 246.9 | 259.5 | 261.6
2805.1 | 2705.1 | 375 | 293.3 | 293.1 | 247 | 259.3 | 261.6
2806.1 | 2706.1 | 374.8 | 293.3 | 293.1 | 247 | 259.4 | 261.6
2807.1 | 2707.1 | 374.7 | 293.3 | 293.2 | 247 | 259.7 | 261.6
2808.1 | 2708.1 | 374.6 | 293.3 | 293.2 | 247 | 260 | 261.6
2809.1 | 2709.1 | 374.5 | 293.3 | 293.2 | 247 | 259.9 | 261.6
2810.1 | 2710.1 | 374.3 | 293.3 | 293.3 | 247.1 | 259.9 | 261.6
2811.1 | 2711.1 | 374.3 | 293.4 | 293.3 | 247.1 | 259.8 | 261.6
2812.1 | 2712.1 | 374.2 | 293.5 | 293.3 | 247.1 | 259.8 | 261.5
2813.1 | 2713.1 | 374 | 293.5 | 293.4 | 247.1 | 259.8 | 261.6
2814.1 | 2714.1 | 373.8 | 293.5 | 293.4 | 247.1 | 259.8 | 261.5
2815.1 | 2715.1 | 373.7 | 293.6 | 293.4 | 247.2 | 260 | 261.5
2816.1 | 2716.1 | 373.6 | 293.6 | 293.4 | 247.2 | 260.2 | 261.5
2817.1 | 2717.1 | 373.5 | 293.6 | 293.4 | 247.2 | 260.2 | 261.5
2818.1 | 2718.1 | 373.4 | 293.6 | 293.5 | 247.2 | 260.4 | 261.5
2819.1 | 2719.1 | 373.3 | 293.6 | 293.5 | 247.2 | 260.4 | 261.5
2820.1 | 2720.1 | 373.2 | 293.6 | 293.6 | 247.3 | 260.4 | 261.5
2821.1 | 2721.1 | 373.1 | 293.6 | 293.6 | 247.3 | 260.3 | 261.5
2822.1 | 2722.1 | 373 | 293.5 | 293.6 | 247.3 | 259.7 | 261.5
2823.1 | 2723.1 | 372.9 | 293.5 | 293.6 | 247.3 | 259.7 | 261.5
2824.1 | 2724.1 | 372.9 | 293.5 | 293.6 | 247.4 | 259.5 | 261.5
2825.1 | 2725.1 | 372.9 | 293.4 | 293.6 | 247.4 | 259.7 | 261.5
2826.1 | 2726.1 | 372.8 | 293.4 | 293.6 | 247.4 | 259.9 | 261.5
2827.1 | 2727.1 | 372.7 | 293.3 | 293.6 | 247.4 | 260.1 | 261.5
2828.1 | 2728.1 | 372.6 | 293.3 | 293.6 | 247.4 | 260 | 261.5
2829.1 | 2729.1 | 372.5 | 293.2 | 293.6 | 247.4 | 259.8 | 261.5
2830.1 | 2730.1 | 372.3 | 293.2 | 293.7 | 247.5 | 259.5 | 261.5
2831.1 | 2731.1 | 372.2 | 293.1 | 293.7 | 247.5 | 259.2 | 261.5
2832.1 | 2732.1 | 372.3 | 293.1 | 293.7 | 247.5 | 259.6 | 261.5
2833.1 | 2733.1 | 372.4 | 293.1 | 293.7 | 247.5 | 259.5 | 261.5
2834.1 | 2734.1 | 372.4 | 293.1 | 293.8 | 247.5 | 259.4 | 261.5
2835.1 | 2735.1 | 372.5 | 293.1 | 293.8 | 247.6 | 259.5 | 261.4
2836.1 | 2736.1 | 372.5 | 293 | 293.9 | 247.6 | 259.3 | 261.4
2837.1 | 2737.1 | 372.5 | 293 | 293.9 | 247.6 | 259.1 | 261.3
2838.1 | 2738.1 | 372.6 | 293 | 293.9 | 247.6 | 259.4 | 261.4
2839.1 | 2739.1 | 372.6 | 293 | 293.9 | 247.6 | 259.2 | 261.4
2840.1 | 2740.1 | 372.8 | 293 | 294 | 247.6 | 259.2 | 261.4
2841.1 | 2741.1 | 372.8 | 293 | 294 | 247.7 | 259.4 | 261.3
2842.1 | 2742.1 | 372.7 | 292.9 | 294 | 247.7 | 259.3 | 261.3
2843.1 | 2743.1 | 372.7 | 292.9 | 294.1 | 247.7 | 259.3 | 261.4
2844.1 | 2744.1 | 372.8 | 292.8 | 294.1 | 247.7 | 259.6 | 261.5
2845.1 | 2745.1 | 373.1 | 292.8 | 294.1 | 247.7 | 259.7 | 261.4
2846.1 | 2746.1 | 373.2 | 292.9 | 294.1 | 247.8 | 259.8 | 261.4
2847.1 | 2747.1 | 373.2 | 292.9 | 294.1 | 247.8 | 260 | 261.4
2848.1 | 2748.1 | 373.3 | 292.9 | 294 | 247.8 | 260.1 | 261.4
2849.1 | 2749.1 | 373.3 | 292.8 | 294.1 | 247.8 | 260.1 | 261.3
2850.1 | 2750.1 | 373.4 | 292.8 | 294.1 | 247.8 | 260.2 | 261.3
2851.1 | 2751.1 | 373.5 | 292.9 | 294.1 | 247.8 | 260.3 | 261.3
2852.1 | 2752.1 | 373.7 | 293 | 294.1 | 247.9 | 260.5 | 261.3
2853.1 | 2753.1 | 373.9 | 293.1 | 294.1 | 247.9 | 260.7 | 261.3
2854.1 | 2754.1 | 374.1 | 293.3 | 294.1 | 247.9 | 260.7 | 261.3
2855.1 | 2755.1 | 374.2 | 293.5 | 294.1 | 247.9 | 260.7 | 261.3
2856.1 | 2756.1 | 374.4 | 293.6 | 294.1 | 247.9 | 260.8 | 261.3
2857.1 | 2757.1 | 374.5 | 293.6 | 294.1 | 247.9 | 260.8 | 261.3
2858.1 | 2758.1 | 374.6 | 293.7 | 294.1 | 248 | 260.7 | 261.3
2859.1 | 2759.1 | 374.7 | 293.7 | 294.1 | 248 | 260.7 | 261.3
2860.1 | 2760.1 | 374.8 | 293.7 | 294.2 | 248 | 260.7 | 261.3
2861.1 | 2761.1 | 374.8 | 293.8 | 294.2 | 248 | 260.8 | 261.3
2862.1 | 2762.1 | 374.7 | 293.8 | 294.3 | 248 | 261 | 261.3
2863.1 | 2763.1 | 374.7 | 293.8 | 294.3 | 248 | 260.8 | 261.4
2864.1 | 2764.1 | 374.7 | 293.8 | 294.4 | 248 | 260.6 | 261.4
2865.1 | 2765.1 | 374.8 | 293.8 | 294.4 | 248.1 | 260.6 | 261.4
2866.1 | 2766.1 | 375 | 293.8 | 294.4 | 248.1 | 260.4 | 261.3
2867.1 | 2767.1 | 375.1 | 294 | 294.5 | 248.1 | 260.3 | 261.3
2868.1 | 2768.1 | 374.9 | 294 | 294.5 | 248.1 | 260.2 | 261.3
2869.1 | 2769.1 | 375 | 293.9 | 294.5 | 248.2 | 260.2 | 261.6
2870.1 | 2770.1 | 375 | 293.9 | 294.5 | 248.2 | 260.2 | 262.1
2871.1 | 2771.1 | 375.1 | 293.9 | 294.5 | 248.2 | 260.1 | 262.3
2872.1 | 2772.1 | 375.9 | 294 | 294.5 | 248.2 | 260.1 | 262.4
2873.1 | 2773.1 | 377.2 | 294 | 294.5 | 248.2 | 260.2 | 262.4
2874.1 | 2774.1 | 379.2 | 294.1 | 294.6 | 248.2 | 260.4 | 262
2875.1 | 2775.1 | 381.6 | 294.1 | 294.6 | 248.2 | 260.5 | 262
2876.1 | 2776.1 | 384.3 | 294.2 | 294.6 | 248.3 | 260.8 | 262.2
2877.1 | 2777.1 | 387.2 | 294.5 | 294.7 | 248.3 | 261.2 | 262.4
2878.1 | 2778.1 | 390.3 | 294.7 | 294.7 | 248.3 | 261.6 | 262.4
2879.1 | 2779.1 | 393.6 | 294.9 | 294.7 | 248.3 | 262.1 | 262.4
2880.1 | 2780.1 | 396.9 | 295.1 | 294.7 | 248.3 | 262.5 | 262.9
2881.1 | 2781.1 | 400.2 | 295.3 | 294.8 | 248.4 | 263.1 | 263.2
2882.1 | 2782.1 | 403.3 | 295.6 | 294.9 | 248.4 | 263.4 | 263.5
2883.1 | 2783.1 | 406 | 296 | 294.9 | 248.4 | 263.9 | 263.7
2884.1 | 2784.1 | 408.3 | 296.5 | 295 | 248.4 | 264.4 | 263.8
2885.1 | 2785.1 | 410.2 | 296.9 | 295.2 | 248.4 | 264.9 | 263.8
2886.1 | 2786.1 | 411.8 | 297.3 | 295.3 | 248.4 | 265.2 | 264.1
2887.1 | 2787.1 | 413.1 | 297.7 | 295.4 | 248.5 | 265.5 | 264.2
2888.1 | 2788.1 | 414.2 | 298.1 | 295.5 | 248.5 | 266.1 | 264.4
2889.1 | 2789.1 | 415 | 298.5 | 295.7 | 248.5 | 266.7 | 264.7
2890.1 | 2790.1 | 415.5 | 298.8 | 295.9 | 248.5 | 267.1 | 264.9
2891.1 | 2791.1 | 415.8 | 299.1 | 296.1 | 248.5 | 267.8 | 265.2
2892.1 | 2792.1 | 416 | 299.3 | 296.3 | 248.5 | 268.1 | 265.4
2893.1 | 2793.1 | 416 | 299.6 | 296.5 | 248.6 | 268.2 | 265.7
2894.1 | 2794.1 | 415.9 | 299.9 | 296.7 | 248.6 | 268.4 | 265.9
2895.1 | 2795.1 | 415.7 | 300.2 | 296.9 | 248.6 | 268.6 | 266.1
2896.1 | 2796.1 | 415.4 | 300.4 | 297.2 | 248.6 | 268.5 | 266.2
2897.1 | 2797.1 | 414.9 | 300.6 | 297.5 | 248.6 | 268.8 | 266.3
2898.1 | 2798.1 | 414.5 | 301 | 297.7 | 248.6 | 269 | 266.5
2899.1 | 2799.1 | 414 | 301.4 | 297.9 | 248.6 | 269.1 | 266.7
2900.1 | 2800.1 | 413.5 | 301.5 | 298.2 | 248.7 | 269.4 | 266.9
2901.1 | 2801.1 | 412.8 | 301.7 | 298.4 | 248.7 | 269.6 | 267.1
2902.1 | 2802.1 | 412.2 | 302 | 298.7 | 248.7 | 269.8 | 267.2
2903.1 | 2803.1 | 411.5 | 302.2 | 298.9 | 248.7 | 270.1 | 267.3
2904.1 | 2804.1 | 410.8 | 302.4 | 299.1 | 248.8 | 270 | 267.5
2905.1 | 2805.1 | 410.2 | 302.6 | 299.4 | 248.8 | 270.1 | 267.6
2906.1 | 2806.1 | 409.5 | 302.7 | 299.5 | 248.8 | 270.2 | 267.7
2907.1 | 2807.1 | 408.8 | 302.9 | 299.7 | 248.8 | 270.5 | 267.8
2908.1 | 2808.1 | 408.1 | 303 | 299.7 | 248.9 | 270.9 | 268.1
2909.1 | 2809.1 | 407.3 | 303.1 | 299.9 | 248.9 | 270.7 | 268.3
2910.1 | 2810.1 | 406.5 | 303.3 | 300 | 249 | 270.5 | 268.4
2911.1 | 2811.1 | 405.7 | 303.5 | 300.1 | 249 | 270.5 | 268.5
2912.1 | 2812.1 | 404.8 | 303.6 | 300.2 | 249 | 270.8 | 268.6
2913.1 | 2813.1 | 404 | 303.5 | 300.4 | 249 | 271 | 268.7
2914.1 | 2814.1 | 403.1 | 303.5 | 300.5 | 249.1 | 271.4 | 268.8
2915.1 | 2815.1 | 402.3 | 303.7 | 300.7 | 249.1 | 271.5 | 268.9
2916.1 | 2816.1 | 401.5 | 303.8 | 300.9 | 249.1 | 271.8 | 269
2917.1 | 2817.1 | 400.7 | 303.8 | 301 | 249.1 | 271.9 | 269.2
2918.1 | 2818.1 | 399.8 | 303.9 | 301.2 | 249.2 | 271.6 | 269.2
2919.1 | 2819.1 | 399 | 304 | 301.3 | 249.2 | 271.8 | 269.3
2920.1 | 2820.1 | 398.3 | 304 | 301.5 | 249.2 | 271.9 | 269.3
2921.1 | 2821.1 | 397.6 | 304.1 | 301.6 | 249.2 | 272 | 269.5
2922.1 | 2822.1 | 396.9 | 304.1 | 301.7 | 249.3 | 272.1 | 269.6
2923.1 | 2823.1 | 396.1 | 304.1 | 301.8 | 249.3 | 272 | 269.8
2924.1 | 2824.1 | 395.3 | 304.1 | 301.9 | 249.3 | 271.7 | 269.8
2925.1 | 2825.1 | 394.6 | 304 | 302.1 | 249.3 | 271.6 | 269.8
2926.1 | 2826.1 | 394.1 | 304 | 302.2 | 249.4 | 271.8 | 269.9
2927.1 | 2827.1 | 393.6 | 304 | 302.3 | 249.4 | 272.2 | 270.1
2928.1 | 2828.1 | 393.2 | 304 | 302.4 | 249.5 | 272.4 | 270.3
2929.1 | 2829.1 | 392.9 | 304 | 302.5 | 249.5 | 272.3 | 270.4
2930.1 | 2830.1 | 392.6 | 304 | 302.5 | 249.5 | 272.4 | 270.5
2931.1 | 2831.1 | 392.5 | 304 | 302.6 | 249.6 | 272.5 | 270.6
2932.1 | 2832.1 | 392.5 | 304 | 302.7 | 249.6 | 272.6 | 270.6
2933.1 | 2833.1 | 392.6 | 304 | 302.7 | 249.6 | 272.7 | 270.7
2934.1 | 2834.1 | 392.6 | 303.9 | 302.8 | 249.7 | 272.9 | 270.7
2935.1 | 2835.1 | 392.8 | 303.9 | 302.9 | 249.7 | 273 | 270.8
2936.1 | 2836.1 | 392.9 | 303.9 | 303 | 249.7 | 273.3 | 270.9
2937.1 | 2837.1 | 393.1 | 304 | 303 | 249.8 | 273.5 | 271
2938.1 | 2838.1 | 393.3 | 304 | 303 | 249.8 | 273.7 | 271.1
2939.1 | 2839.1 | 393.6 | 304 | 303.1 | 249.8 | 274 | 271.2
2940.1 | 2840.1 | 393.9 | 304 | 303.1 | 249.9 | 274.4 | 271.3
2941.1 | 2841.1 | 394.2 | 304 | 303.2 | 249.9 | 274.4 | 271.4
2942.1 | 2842.1 | 394.6 | 304 | 303.2 | 249.9 | 274.5 | 271.4
2943.1 | 2843.1 | 394.9 | 304 | 303.2 | 250 | 274.2 | 271.5
2944.1 | 2844.1 | 395.3 | 303.9 | 303.2 | 250 | 274 | 271.5
2945.1 | 2845.1 | 395.6 | 303.9 | 303.2 | 250.1 | 273.8 | 271.6
2946.1 | 2846.1 | 396 | 303.9 | 303.2 | 250.1 | 273.8 | 271.7
2947.1 | 2847.1 | 396.4 | 303.9 | 303.2 | 250.1 | 273.8 | 271.7
2948.1 | 2848.1 | 396.8 | 303.9 | 303.2 | 250.2 | 273.7 | 271.8
2949.1 | 2849.1 | 397.1 | 303.9 | 303.2 | 250.2 | 273.7 | 271.9
2950.1 | 2850.1 | 397.5 | 304 | 303.2 | 250.3 | 273.7 | 272
2951.1 | 2851.1 | 398 | 304.1 | 303.3 | 250.3 | 273.8 | 272.1
2952.1 | 2852.1 | 398.5 | 304.1 | 303.3 | 250.3 | 273.9 | 272.2
2953.1 | 2853.1 | 399 | 304.2 | 303.3 | 250.4 | 274 | 272.2
2954.1 | 2854.1 | 399.3 | 304.3 | 303.3 | 250.4 | 273.9 | 272.2
2955.1 | 2855.1 | 399.7 | 304.4 | 303.3 | 250.4 | 274 | 272.2
2956.1 | 2856.1 | 400.1 | 304.5 | 303.3 | 250.5 | 274.1 | 272.3
2957.1 | 2857.1 | 400.4 | 304.7 | 303.4 | 250.5 | 274.1 | 272.4
2958.1 | 2858.1 | 400.6 | 304.9 | 303.4 | 250.6 | 274.2 | 272.4
2959.1 | 2859.1 | 400.7 | 305 | 303.5 | 250.6 | 274.5 | 272.5
2960.1 | 2860.1 | 400.9 | 305.1 | 303.6 | 250.6 | 274.4 | 272.5
2961.1 | 2861.1 | 401.2 | 305.2 | 303.7 | 250.7 | 274.7 | 272.6
2962.1 | 2862.1 | 401.3 | 305.2 | 303.8 | 250.7 | 275 | 272.7
2963.1 | 2863.1 | 401.4 | 305.3 | 303.9 | 250.8 | 275.3 | 272.8
2964.1 | 2864.1 | 401.3 | 305.2 | 304 | 250.8 | 275.5 | 272.9
2965.1 | 2865.1 | 401.2 | 305.2 | 304.1 | 250.8 | 275.7 | 273
2966.1 | 2866.1 | 401.2 | 305.2 | 304.2 | 250.9 | 275.7 | 273.1
2967.1 | 2867.1 | 401.2 | 305.2 | 304.3 | 250.9 | 275.8 | 273.2
2968.1 | 2868.1 | 401.1 | 305.2 | 304.4 | 250.9 | 275.8 | 273.3
2969.1 | 2869.1 | 401 | 305.2 | 304.5 | 251 | 275.9 | 273.3
2970.1 | 2870.1 | 400.9 | 305.3 | 304.6 | 251 | 276 | 273.5
2971.1 | 2871.1 | 401 | 305.3 | 304.6 | 251.1 | 276.2 | 273.5
2972.1 | 2872.1 | 400.9 | 305.4 | 304.7 | 251.1 | 276.4 | 273.6
2973.1 | 2873.1 | 400.8 | 305.4 | 304.8 | 251.1 | 276.7 | 273.7
2974.1 | 2874.1 | 400.7 | 305.5 | 304.9 | 251.2 | 276.6 | 273.8
2975.1 | 2875.1 | 400.7 | 305.6 | 304.9 | 251.2 | 276.5 | 273.8
2976.1 | 2876.1 | 400.8 | 305.7 | 305 | 251.2 | 276.7 | 273.9
2977.1 | 2877.1 | 400.6 | 305.8 | 305.1 | 251.3 | 276.7 | 273.9
2978.1 | 2878.1 | 400.5 | 305.9 | 305.2 | 251.3 | 276.5 | 274
2979.1 | 2879.1 | 400.4 | 306 | 305.2 | 251.4 | 276.6 | 274
2980.1 | 2880.1 | 400.3 | 306 | 305.3 | 251.4 | 276.7 | 274.1
2981.1 | 2881.1 | 400.2 | 306.1 | 305.4 | 251.4 | 277 | 274.1
2982.1 | 2882.1 | 400.1 | 306.2 | 305.4 | 251.5 | 277 | 274.1
2983.1 | 2883.1 | 400.1 | 306.2 | 305.5 | 251.5 | 277 | 274.3
2984.1 | 2884.1 | 400 | 306.3 | 305.6 | 251.6 | 277 | 274.3
2985.1 | 2885.1 | 399.9 | 306.3 | 305.6 | 251.6 | 277.2 | 274.4
2986.1 | 2886.1 | 399.8 | 306.4 | 305.7 | 251.6 | 277.4 | 274.5
2987.1 | 2887.1 | 399.7 | 306.4 | 305.7 | 251.7 | 277.6 | 274.6
2988.1 | 2888.1 | 399.7 | 306.3 | 305.8 | 251.7 | 277.5 | 274.7
2989.1 | 2889.1 | 399.6 | 306.3 | 305.9 | 251.8 | 277.8 | 274.7
2990.1 | 2890.1 | 399.6 | 306.3 | 305.9 | 251.8 | 278.1 | 274.8
2991.1 | 2891.1 | 399.6 | 306.3 | 306 | 251.8 | 278.2 | 274.8
2992.1 | 2892.1 | 399.7 | 306.3 | 306 | 251.9 | 278.3 | 274.9
2993.1 | 2893.1 | 399.7 | 306.3 | 306.1 | 251.9 | 278.4 | 275
2994.1 | 2894.1 | 399.8 | 306.3 | 306.1 | 252 | 278.4 | 275.1
2995.1 | 2895.1 | 399.9 | 306.3 | 306.1 | 252 | 278.5 | 275.2
2996.1 | 2896.1 | 400 | 306.3 | 306.1 | 252 | 278.3 | 275.3
2997.1 | 2897.1 | 400.1 | 306.2 | 306.2 | 252.1 | 278.2 | 275.4
2998.1 | 2898.1 | 400.1 | 306.3 | 306.2 | 252.1 | 278.2 | 275.4
2999.1 | 2899.1 | 400 | 306.3 | 306.3 | 252.1 | 278.2 | 275.4
3000.1 | 2900.1 | 399.9 | 306.3 | 306.3 | 252.2 | 278.3 | 275.5
3001.1 | 2901.1 | 399.8 | 306.4 | 306.3 | 252.2 | 278.6 | 275.6
3002.1 | 2902.1 | 399.8 | 306.4 | 306.4 | 252.3 | 278.9 | 275.6
3003.1 | 2903.1 | 399.8 | 306.6 | 306.5 | 252.3 | 278.9 | 275.6
3004.1 | 2904.1 | 399.8 | 306.7 | 306.5 | 252.3 | 278.9 | 275.7
3005.1 | 2905.1 | 399.8 | 306.8 | 306.6 | 252.4 | 278.9 | 275.7
3006.1 | 2906.1 | 399.7 | 306.9 | 306.6 | 252.4 | 279.1 | 275.9
3007.1 | 2907.1 | 399.7 | 307 | 306.7 | 252.5 | 279.3 | 276
3008.1 | 2908.1 | 399.8 | 307 | 306.7 | 252.5 | 279.5 | 276.1
3009.1 | 2909.1 | 399.9 | 307.1 | 306.7 | 252.6 | 279.7 | 276.1
3010.1 | 2910.1 | 400 | 307.1 | 306.7 | 252.6 | 279.8 | 276.2
3011.1 | 2911.1 | 400.2 | 307.2 | 306.8 | 252.6 | 279.7 | 276.3
3012.1 | 2912.1 | 400.2 | 307.3 | 306.8 | 252.7 | 279.8 | 276.3
3013.1 | 2913.1 | 400.3 | 307.4 | 306.8 | 252.7 | 279.7 | 276.3
3014.1 | 2914.1 | 400.4 | 307.5 | 306.9 | 252.7 | 279.9 | 276.4
3015.1 | 2915.1 | 400.2 | 307.6 | 306.9 | 252.8 | 279.9 | 276.5
3016.1 | 2916.1 | 400.1 | 307.7 | 307 | 252.8 | 280 | 276.5
3017.1 | 2917.1 | 400 | 307.8 | 307 | 252.9 | 279.8 | 276.6
3018.1 | 2918.1 | 400 | 307.9 | 307.1 | 252.9 | 279.8 | 276.6
3019.1 | 2919.1 | 400.2 | 308.1 | 307.2 | 252.9 | 279.8 | 276.7
3020.1 | 2920.1 | 400.3 | 308.2 | 307.3 | 253 | 279.9 | 276.7
3021.1 | 2921.1 | 400.2 | 308.3 | 307.4 | 253 | 279.9 | 276.8
3022.1 | 2922.1 | 400.4 | 308.4 | 307.5 | 253.1 | 280 | 276.9
3023.1 | 2923.1 | 400.4 | 308.5 | 307.6 | 253.1 | 280 | 277
3024.1 | 2924.1 | 400.6 | 308.5 | 307.7 | 253.2 | 280.1 | 277.2
3025.1 | 2925.1 | 400.6 | 308.6 | 307.8 | 253.2 | 280.2 | 277.3
3026.1 | 2926.1 | 400.3 | 308.6 | 307.9 | 253.2 | 280.4 | 277.3
3027.1 | 2927.1 | 400.2 | 308.6 | 308 | 253.3 | 280.5 | 277.3
3028.1 | 2928.1 | 400.2 | 308.6 | 308.1 | 253.3 | 280.7 | 277.4
3029.1 | 2929.1 | 400.1 | 308.6 | 308.2 | 253.4 | 280.6 | 277.4
3030.1 | 2930.1 | 400 | 308.7 | 308.2 | 253.4 | 280.2 | 277.5
3031.1 | 2931.1 | 399.9 | 308.7 | 308.3 | 253.5 | 280.1 | 277.5
3032.1 | 2932.1 | 399.9 | 308.7 | 308.4 | 253.5 | 280.1 | 277.5
3033.1 | 2933.1 | 399.8 | 308.8 | 308.4 | 253.5 | 280 | 277.5
3034.1 | 2934.1 | 399.6 | 308.7 | 308.5 | 253.6 | 280 | 277.6
3035.1 | 2935.1 | 399.5 | 308.7 | 308.6 | 253.6 | 280 | 277.6
3036.1 | 2936.1 | 399.3 | 308.7 | 308.6 | 253.7 | 280.1 | 277.6
3037.1 | 2937.1 | 399.3 | 308.7 | 308.6 | 253.7 | 280.1 | 277.7
3038.1 | 2938.1 | 399.2 | 308.8 | 308.7 | 253.7 | 280.1 | 277.7
3039.1 | 2939.1 | 399.2 | 308.9 | 308.7 | 253.8 | 280 | 277.6
3040.1 | 2940.1 | 399.1 | 308.9 | 308.7 | 253.8 | 279.9 | 277.6
3041.1 | 2941.1 | 398.9 | 309 | 308.7 | 253.9 | 280 | 277.7
3042.1 | 2942.1 | 398.8 | 309.1 | 308.7 | 253.9 | 279.8 | 277.8
3043.1 | 2943.1 | 398.7 | 309.2 | 308.8 | 254 | 279.9 | 277.9
3044.1 | 2944.1 | 398.7 | 309.2 | 308.8 | 254 | 280 | 277.9
3045.1 | 2945.1 | 398.9 | 309.2 | 308.9 | 254.1 | 279.9 | 277.9
3046.1 | 2946.1 | 398.9 | 309.2 | 308.9 | 254.1 | 279.9 | 277.9
3047.1 | 2947.1 | 398.7 | 309.2 | 309 | 254.2 | 279.9 | 278
3048.1 | 2948.1 | 398.7 | 309.1 | 309 | 254.2 | 280.2 | 278.1
3049.1 | 2949.1 | 398.8 | 309.1 | 309 | 254.2 | 280.2 | 278.1
3050.1 | 2950.1 | 398.8 | 309 | 309.1 | 254.3 | 280 | 278.1
3051.1 | 2951.1 | 398.7 | 309 | 309.2 | 254.3 | 279.9 | 278.1
3052.1 | 2952.1 | 398.7 | 309.1 | 309.2 | 254.4 | 279.8 | 278.1
3053.1 | 2953.1 | 398.7 | 309.1 | 309.3 | 254.4 | 279.7 | 278.1
3054.1 | 2954.1 | 398.8 | 309.1 | 309.3 | 254.4 | 279.8 | 278.1
3055.1 | 2955.1 | 398.8 | 309.1 | 309.3 | 254.5 | 280 | 278.1
3056.1 | 2956.1 | 398.8 | 309.1 | 309.4 | 254.5 | 280 | 278.2
3057.1 | 2957.1 | 398.9 | 309.1 | 309.4 | 254.6 | 280.2 | 278.2
3058.1 | 2958.1 | 398.8 | 309.1 | 309.4 | 254.6 | 280.1 | 278.3
3059.1 | 2959.1 | 398.7 | 309.2 | 309.5 | 254.7 | 280 | 278.3
3060.1 | 2960.1 | 398.7 | 309.3 | 309.5 | 254.7 | 280.1 | 278.4
3061.1 | 2961.1 | 398.7 | 309.3 | 309.6 | 254.8 | 280 | 278.4
3062.1 | 2962.1 | 398.7 | 309.4 | 309.6 | 254.8 | 280 | 278.4
3063.1 | 2963.1 | 398.8 | 309.4 | 309.7 | 254.8 | 280.1 | 278.3
3064.1 | 2964.1 | 398.9 | 309.4 | 309.7 | 254.9 | 280.3 | 278.3
3065.1 | 2965.1 | 398.9 | 309.4 | 309.8 | 254.9 | 280.3 | 278.2
3066.1 | 2966.1 | 399 | 309.4 | 309.8 | 255 | 280.3 | 278.2
3067.1 | 2967.1 | 399.1 | 309.4 | 309.9 | 255 | 280.1 | 278.2
3068.1 | 2968.1 | 399.1 | 309.5 | 309.9 | 255 | 279.9 | 278.3
3069.1 | 2969.1 | 399.1 | 309.5 | 310 | 255.1 | 279.9 | 278.4
3070.1 | 2970.1 | 399 | 309.6 | 310.1 | 255.1 | 280.1 | 278.4
3071.1 | 2971.1 | 398.9 | 309.7 | 310.1 | 255.2 | 280.2 | 278.4
3072.1 | 2972.1 | 398.9 | 309.8 | 310.2 | 255.2 | 280.4 | 278.5
3073.1 | 2973.1 | 399 | 309.9 | 310.3 | 255.2 | 280.6 | 278.6
3074.1 | 2974.1 | 399 | 310.1 | 310.3 | 255.3 | 280.7 | 278.7
3075.1 | 2975.1 | 399 | 310.2 | 310.3 | 255.3 | 280.8 | 278.7
3076.1 | 2976.1 | 399.1 | 310.3 | 310.4 | 255.4 | 281 | 278.7
3077.1 | 2977.1 | 399.2 | 310.5 | 310.4 | 255.4 | 280.9 | 278.7
3078.1 | 2978.1 | 399.3 | 310.7 | 310.4 | 255.5 | 281 | 278.7
3079.1 | 2979.1 | 399.5 | 310.8 | 310.5 | 255.5 | 281 | 278.8
3080.1 | 2980.1 | 399.6 | 310.9 | 310.5 | 255.5 | 281 | 278.8
3081.1 | 2981.1 | 399.8 | 311 | 310.6 | 255.6 | 280.8 | 278.8
3082.1 | 2982.1 | 399.7 | 311.1 | 310.6 | 255.6 | 280.9 | 278.8
3083.1 | 2983.1 | 399.7 | 311.2 | 310.7 | 255.6 | 280.6 | 278.7
3084.1 | 2984.1 | 399.7 | 311.3 | 310.7 | 255.7 | 280.2 | 278.8
3085.1 | 2985.1 | 399.7 | 311.3 | 310.8 | 255.7 | 279.9 | 278.8
3086.1 | 2986.1 | 399.6 | 311.4 | 310.9 | 255.8 | 279.8 | 278.8
3087.1 | 2987.1 | 399.6 | 311.4 | 310.9 | 255.8 | 280.1 | 278.9
3088.1 | 2988.1 | 399.5 | 311.5 | 311 | 255.8 | 280 | 279
3089.1 | 2989.1 | 399.4 | 311.5 | 311 | 255.9 | 279.8 | 279
3090.1 | 2990.1 | 399.4 | 311.5 | 311 | 255.9 | 279.7 | 279
3091.1 | 2991.1 | 399.5 | 311.5 | 311.1 | 256 | 279.3 | 279
3092.1 | 2992.1 | 399.7 | 311.5 | 311.1 | 256 | 279.2 | 279.1
3093.1 | 2993.1 | 399.9 | 311.5 | 311.2 | 256 | 279.3 | 279.1
3094.1 | 2994.1 | 399.8 | 311.5 | 311.2 | 256.1 | 279.5 | 279.1
3095.1 | 2995.1 | 399.9 | 311.6 | 311.3 | 256.1 | 279.7 | 279.1
3096.1 | 2996.1 | 400.1 | 311.6 | 311.3 | 256.2 | 279.9 | 279.1
3097.1 | 2997.1 | 400.1 | 311.7 | 311.4 | 256.2 | 280.2 | 279
3098.1 | 2998.1 | 400.1 | 311.8 | 311.5 | 256.2 | 280.5 | 279
3099.1 | 2999.1 | 399.9 | 311.9 | 311.6 | 256.3 | 280.6 | 279
3100.1 | 3000.1 | 399.9 | 311.9 | 311.6 | 256.3 | 280.7 | 279
3101.1 | 3001.1 | 399.8 | 311.9 | 311.8 | 256.3 | 280.8 | 279.1
3102.1 | 3002.1 | 399.8 | 311.9 | 311.8 | 256.4 | 280.5 | 279.1
3103.1 | 3003.1 | 399.9 | 311.9 | 311.9 | 256.4 | 280.8 | 279.1
3104.1 | 3004.1 | 400.1 | 311.9 | 312 | 256.5 | 281 | 279.1
3105.1 | 3005.1 | 400.1 | 312 | 312 | 256.5 | 281.1 | 279.1
3106.1 | 3006.1 | 400.2 | 312.1 | 312.1 | 256.5 | 281 | 279.1
3107.1 | 3007.1 | 400.3 | 312.1 | 312.2 | 256.6 | 280.8 | 279.2
3108.1 | 3008.1 | 400.1 | 312.2 | 312.2 | 256.6 | 281 | 279.2
3109.1 | 3009.1 | 400 | 312.2 | 312.3 | 256.7 | 281.1 | 279.3
3110.1 | 3010.1 | 400 | 312.2 | 312.4 | 256.7 | 281 | 279.3
3111.1 | 3011.1 | 400 | 312.1 | 312.4 | 256.8 | 281.4 | 279.4
3112.1 | 3012.1 | 400 | 312.1 | 312.5 | 256.8 | 281.7 | 279.4
3113.1 | 3013.1 | 400 | 312 | 312.6 | 256.8 | 281.9 | 279.5
3114.1 | 3014.1 | 400 | 312 | 312.7 | 256.9 | 282 | 279.5
3115.1 | 3015.1 | 400 | 312 | 312.7 | 256.9 | 281.9 | 279.6
3116.1 | 3016.1 | 400 | 312 | 312.8 | 257 | 281.8 | 279.7
3117.1 | 3017.1 | 399.9 | 312 | 312.8 | 257 | 281.9 | 279.8
3118.1 | 3018.1 | 399.7 | 312 | 312.9 | 257 | 281.9 | 279.8
3119.1 | 3019.1 | 399.6 | 312.1 | 312.9 | 257.1 | 282 | 279.8
3120.1 | 3020.1 | 399.6 | 312.2 | 313 | 257.1 | 282 | 279.8
3121.1 | 3021.1 | 399.6 | 312.2 | 313.1 | 257.2 | 282.2 | 279.9
3122.1 | 3022.1 | 399.7 | 312.3 | 313.1 | 257.2 | 282.4 | 279.9
3123.1 | 3023.1 | 399.8 | 312.4 | 313.2 | 257.2 | 282.6 | 280
3124.1 | 3024.1 | 399.8 | 312.5 | 313.3 | 257.3 | 282.5 | 280
3125.1 | 3025.1 | 399.8 | 312.5 | 313.3 | 257.3 | 282.3 | 280.1
3126.1 | 3026.1 | 399.9 | 312.5 | 313.4 | 257.3 | 282 | 280.1
3127.1 | 3027.1 | 400.1 | 312.5 | 313.4 | 257.4 | 282 | 280.1
3128.1 | 3028.1 | 400.2 | 312.5 | 313.5 | 257.4 | 281.8 | 280.1
3129.1 | 3029.1 | 400.3 | 312.5 | 313.6 | 257.4 | 281.6 | 280.1
3130.1 | 3030.1 | 400.4 | 312.4 | 313.6 | 257.5 | 281.9 | 280.1
3131.1 | 3031.1 | 400.5 | 312.3 | 313.7 | 257.5 | 282.1 | 280.1
3132.1 | 3032.1 | 400.5 | 312.3 | 313.7 | 257.5 | 282.3 | 280.1
3133.1 | 3033.1 | 400.5 | 312.2 | 313.8 | 257.6 | 282 | 280.1
3134.1 | 3034.1 | 400.5 | 312.1 | 313.8 | 257.6 | 282 | 280.1
3135.1 | 3035.1 | 400.5 | 312 | 313.9 | 257.6 | 282 | 280.2
3136.1 | 3036.1 | 400.3 | 311.9 | 313.9 | 257.7 | 282.3 | 280.2
3137.1 | 3037.1 | 400.2 | 311.9 | 314 | 257.7 | 282.5 | 280.2
3138.1 | 3038.1 | 400.1 | 311.8 | 314 | 257.8 | 282.7 | 280.3
3139.1 | 3039.1 | 400.1 | 311.8 | 314.1 | 257.8 | 282.5 | 280.3
3140.1 | 3040.1 | 400.3 | 311.7 | 314.1 | 257.8 | 282.7 | 280.3
3141.1 | 3041.1 | 400.2 | 311.7 | 314.1 | 257.9 | 282.7 | 280.3
3142.1 | 3042.1 | 400.1 | 311.6 | 314.2 | 257.9 | 282.7 | 280.4
3143.1 | 3043.1 | 400 | 311.6 | 314.2 | 258 | 282.4 | 280.4
3144.1 | 3044.1 | 399.8 | 311.6 | 314.3 | 258 | 282.6 | 280.4
3145.1 | 3045.1 | 399.7 | 311.6 | 314.3 | 258 | 282.8 | 280.4
3146.1 | 3046.1 | 399.7 | 311.5 | 314.3 | 258.1 | 283 | 280.4
3147.1 | 3047.1 | 399.7 | 311.5 | 314.4 | 258.1 | 283.2 | 280.4
3148.1 | 3048.1 | 399.8 | 311.5 | 314.5 | 258.1 | 283.2 | 280.4
3149.1 | 3049.1 | 399.7 | 311.6 | 314.5 | 258.2 | 283.3 | 280.3
3150.1 | 3050.1 | 399.7 | 311.7 | 314.6 | 258.2 | 283.2 | 280.3
3151.1 | 3051.1 | 399.7 | 311.9 | 314.6 | 258.3 | 282.9 | 280.3
3152.1 | 3052.1 | 399.7 | 312 | 314.7 | 258.3 | 283.1 | 280.3
3153.1 | 3053.1 | 399.6 | 312 | 314.7 | 258.3 | 283.2 | 280.4
3154.1 | 3054.1 | 399.6 | 312.1 | 314.8 | 258.4 | 283.5 | 280.5
3155.1 | 3055.1 | 399.6 | 312.1 | 314.8 | 258.4 | 283.5 | 280.5
3156.1 | 3056.1 | 399.6 | 312.2 | 314.9 | 258.5 | 283.4 | 280.5
3157.1 | 3057.1 | 399.5 | 312.2 | 315 | 258.5 | 283.5 | 280.5
3158.1 | 3058.1 | 399.3 | 312.2 | 315 | 258.5 | 283.4 | 280.6
3159.1 | 3059.1 | 399.4 | 312.3 | 315.1 | 258.6 | 283.6 | 280.6
3160.1 | 3060.1 | 399.5 | 312.3 | 315.1 | 258.6 | 283.6 | 280.6
3161.1 | 3061.1 | 399.4 | 312.3 | 315.2 | 258.6 | 283.7 | 280.6
3162.1 | 3062.1 | 399.2 | 312.3 | 315.2 | 258.7 | 283.9 | 280.6
3163.1 | 3063.1 | 399.1 | 312.4 | 315.3 | 258.7 | 284 | 280.6
3164.1 | 3064.1 | 399.1 | 312.4 | 315.3 | 258.7 | 284.2 | 280.7
3165.1 | 3065.1 | 399 | 312.5 | 315.4 | 258.8 | 284.4 | 280.8
3166.1 | 3066.1 | 399 | 312.5 | 315.4 | 258.8 | 284.3 | 280.8
3167.1 | 3067.1 | 398.8 | 312.6 | 315.5 | 258.8 | 284.1 | 280.9
3168.1 | 3068.1 | 398.7 | 312.7 | 315.6 | 258.9 | 284.1 | 281
3169.1 | 3069.1 | 398.7 | 312.8 | 315.6 | 258.9 | 284.4 | 281
3170.1 | 3070.1 | 398.9 | 312.9 | 315.6 | 259 | 284.3 | 281
3171.1 | 3071.1 | 399.2 | 313 | 315.7 | 259 | 284.5 | 280.9
3172.1 | 3072.1 | 399.4 | 313 | 315.7 | 259 | 284.9 | 280.9
3173.1 | 3073.1 | 399.4 | 313.1 | 315.8 | 259.1 | 285 | 281
3174.1 | 3074.1 | 399.4 | 313.2 | 315.9 | 259.1 | 285.3 | 281
3175.1 | 3075.1 | 399.4 | 313.3 | 316 | 259.1 | 285.4 | 281
3176.1 | 3076.1 | 399.3 | 313.4 | 316.1 | 259.2 | 285.3 | 281
3177.1 | 3077.1 | 399.2 | 313.4 | 316.1 | 259.2 | 285.4 | 281
3178.1 | 3078.1 | 399.3 | 313.5 | 316.2 | 259.2 | 285.6 | 281.1
3179.1 | 3079.1 | 399.2 | 313.6 | 316.3 | 259.3 | 285.9 | 281.1
3180.1 | 3080.1 | 399.1 | 313.7 | 316.4 | 259.3 | 285.7 | 281.1
3181.1 | 3081.1 | 399.1 | 313.9 | 316.4 | 259.4 | 285.5 | 281
3182.1 | 3082.1 | 399.2 | 313.9 | 316.5 | 259.4 | 285.6 | 281
3183.1 | 3083.1 | 399.3 | 313.9 | 316.6 | 259.4 | 285.8 | 281.1
3184.1 | 3084.1 | 399.3 | 314 | 316.6 | 259.5 | 285.7 | 281.1
3185.1 | 3085.1 | 399.2 | 314 | 316.7 | 259.5 | 285.7 | 281.2
3186.1 | 3086.1 | 399.1 | 313.9 | 316.8 | 259.5 | 285.7 | 281.1
3187.1 | 3087.1 | 399 | 313.9 | 316.9 | 259.6 | 285.8 | 281.1
3188.1 | 3088.1 | 398.9 | 314 | 316.9 | 259.6 | 285.6 | 281.1
3189.1 | 3089.1 | 399 | 314 | 317 | 259.6 | 285.4 | 281.1
3190.1 | 3090.1 | 398.9 | 314.1 | 317 | 259.7 | 285.1 | 281.1
3191.1 | 3091.1 | 398.8 | 314.2 | 317 | 259.7 | 285 | 281.2
3192.1 | 3092.1 | 398.7 | 314.2 | 317.1 | 259.8 | 285.2 | 281.2
3193.1 | 3093.1 | 398.6 | 314.2 | 317.1 | 259.8 | 285.3 | 281.2
3194.1 | 3094.1 | 398.6 | 314.2 | 317.2 | 259.8 | 285.1 | 281.2
3195.1 | 3095.1 | 398.7 | 314.3 | 317.2 | 259.9 | 285 | 281.2
3196.1 | 3096.1 | 398.9 | 314.3 | 317.3 | 259.9 | 284.8 | 281.3
3197.1 | 3097.1 | 399 | 314.3 | 317.4 | 259.9 | 284.7 | 281.3
3198.1 | 3098.1 | 399 | 314.3 | 317.4 | 260 | 284.5 | 281.3
3199.1 | 3099.1 | 399 | 314.3 | 317.5 | 260 | 284.5 | 281.3
3200.1 | 3100.1 | 399.2 | 314.2 | 317.6 | 260 | 284.7 | 281.3
3201.1 | 3101.1 | 399.3 | 314.2 | 317.6 | 260.1 | 284.7 | 281.3
3202.1 | 3102.1 | 399.4 | 314.2 | 317.7 | 260.1 | 284.7 | 281.3
3203.1 | 3103.1 | 399.4 | 314.1 | 317.7 | 260.1 | 284.6 | 281.3
3204.1 | 3104.1 | 399.4 | 314.1 | 317.8 | 260.2 | 284.7 | 281.3
3205.1 | 3105.1 | 399.4 | 314.2 | 317.8 | 260.2 | 284.7 | 281.3
3206.1 | 3106.1 | 399.5 | 314.3 | 317.8 | 260.2 | 284.5 | 281.3
3207.1 | 3107.1 | 399.6 | 314.4 | 317.8 | 260.3 | 284.4 | 281.2
3208.1 | 3108.1 | 399.5 | 314.4 | 317.9 | 260.3 | 284.5 | 281.3
3209.1 | 3109.1 | 399.4 | 314.5 | 317.9 | 260.3 | 284.4 | 281.3
3210.1 | 3110.1 | 399.5 | 314.4 | 318 | 260.4 | 284.3 | 281.2
3211.1 | 3111.1 | 399.5 | 314.4 | 318 | 260.4 | 284.4 | 281.2
3212.1 | 3112.1 | 399.6 | 314.5 | 318 | 260.5 | 284.4 | 281.2
3213.1 | 3113.1 | 399.8 | 314.6 | 318 | 260.5 | 284.6 | 281.3
3214.1 | 3114.1 | 399.9 | 314.6 | 318.1 | 260.5 | 284.6 | 281.3
3215.1 | 3115.1 | 399.9 | 314.7 | 318.1 | 260.6 | 284.5 | 281.2
3216.1 | 3116.1 | 399.9 | 314.8 | 318.2 | 260.6 | 284.6 | 281.3
3217.1 | 3117.1 | 399.9 | 314.9 | 318.2 | 260.6 | 284.5 | 281.3
3218.1 | 3118.1 | 400 | 315.1 | 318.3 | 260.7 | 284.6 | 281.4
3219.1 | 3119.1 | 400 | 315.1 | 318.3 | 260.7 | 284.8 | 281.4
3220.1 | 3120.1 | 399.9 | 315.2 | 318.3 | 260.7 | 284.9 | 281.4
3221.1 | 3121.1 | 399.8 | 315.2 | 318.3 | 260.8 | 285.1 | 281.4
3222.1 | 3122.1 | 399.8 | 315.3 | 318.3 | 260.8 | 285 | 281.4
3223.1 | 3123.1 | 399.9 | 315.3 | 318.4 | 260.8 | 285 | 281.3
3224.1 | 3124.1 | 399.8 | 315.4 | 318.4 | 260.9 | 285 | 281.2
3225.1 | 3125.1 | 399.9 | 315.4 | 318.4 | 260.9 | 284.9 | 281.3
3226.1 | 3126.1 | 399.8 | 315.4 | 318.4 | 260.9 | 285.1 | 281.4
3227.1 | 3127.1 | 399.6 | 315.5 | 318.5 | 260.9 | 285.4 | 281.3
3228.1 | 3128.1 | 399.5 | 315.5 | 318.5 | 261 | 285.6 | 281.4
3229.1 | 3129.1 | 399.4 | 315.5 | 318.5 | 261 | 285.7 | 281.4
3230.1 | 3130.1 | 399.2 | 315.6 | 318.5 | 261 | 285.7 | 281.2
3231.1 | 3131.1 | 399.3 | 315.6 | 318.6 | 261.1 | 285.6 | 281.2
3232.1 | 3132.1 | 399.3 | 315.6 | 318.6 | 261.1 | 285.8 | 281.3
3233.1 | 3133.1 | 399.2 | 315.7 | 318.6 | 261.2 | 285.8 | 281.3
3234.1 | 3134.1 | 399.2 | 315.8 | 318.6 | 261.2 | 286.1 | 281.3
3235.1 | 3135.1 | 399.2 | 315.8 | 318.6 | 261.2 | 286.2 | 281.4
3236.1 | 3136.1 | 399.3 | 315.9 | 318.7 | 261.3 | 286.4 | 281.4
3237.1 | 3137.1 | 399.3 | 316 | 318.7 | 261.3 | 286.5 | 281.3
3238.1 | 3138.1 | 399.2 | 316 | 318.7 | 261.3 | 286.5 | 281.4
3239.1 | 3139.1 | 399.2 | 316.1 | 318.7 | 261.4 | 286.8 | 281.4
3240.1 | 3140.1 | 399.2 | 316.1 | 318.8 | 261.4 | 286.9 | 281.5
3241.1 | 3141.1 | 399.2 | 316.2 | 318.8 | 261.4 | 287.1 | 281.5
3242.1 | 3142.1 | 399.4 | 316.2 | 318.8 | 261.5 | 287.2 | 281.5
3243.1 | 3143.1 | 399.5 | 316.1 | 318.8 | 261.5 | 287.2 | 281.5
3244.1 | 3144.1 | 399.5 | 316.2 | 318.8 | 261.5 | 287.2 | 281.6
3245.1 | 3145.1 | 399.5 | 316.2 | 318.8 | 261.6 | 287.1 | 281.6
3246.1 | 3146.1 | 399.5 | 316.3 | 318.8 | 261.6 | 287.1 | 281.6
3247.1 | 3147.1 | 399.6 | 316.3 | 318.8 | 261.6 | 287.1 | 281.7
3248.1 | 3148.1 | 399.8 | 316.4 | 318.9 | 261.7 | 287 | 281.8
3249.1 | 3149.1 | 399.9 | 316.4 | 318.9 | 261.7 | 287 | 281.8
3250.1 | 3150.1 | 399.8 | 316.4 | 318.9 | 261.7 | 287.3 | 281.9
3251.1 | 3151.1 | 399.8 | 316.5 | 319 | 261.7 | 287.4 | 282
3252.1 | 3152.1 | 400 | 316.5 | 319.1 | 261.8 | 287.4 | 282
3253.1 | 3153.1 | 400 | 316.5 | 319.1 | 261.8 | 287.5 | 282
3254.1 | 3154.1 | 399.9 | 316.5 | 319.1 | 261.8 | 287.6 | 282.1
3255.1 | 3155.1 | 399.8 | 316.5 | 319.2 | 261.9 | 287.6 | 282.1
3256.1 | 3156.1 | 399.7 | 316.6 | 319.2 | 261.9 | 287.6 | 282.1
3257.1 | 3157.1 | 399.5 | 316.6 | 319.3 | 261.9 | 287.6 | 282.1
3258.1 | 3158.1 | 399.5 | 316.7 | 319.3 | 262 | 287.6 | 282.1
3259.1 | 3159.1 | 399.3 | 316.8 | 319.3 | 262 | 287.6 | 282
3260.1 | 3160.1 | 399.2 | 316.7 | 319.4 | 262.1 | 287.1 | 282
3261.1 | 3161.1 | 399.1 | 316.7 | 319.4 | 262.1 | 286.9 | 282
3262.1 | 3162.1 | 399 | 316.8 | 319.5 | 262.1 | 286.9 | 282
3263.1 | 3163.1 | 398.9 | 316.8 | 319.6 | 262.1 | 287.1 | 282.1
3264.1 | 3164.1 | 398.9 | 316.9 | 319.6 | 262.2 | 287.3 | 282.1
3265.1 | 3165.1 | 398.9 | 316.9 | 319.7 | 262.2 | 287.2 | 282.1
3266.1 | 3166.1 | 398.8 | 316.9 | 319.8 | 262.2 | 287.1 | 282.1
3267.1 | 3167.1 | 398.7 | 316.9 | 319.9 | 262.2 | 287.1 | 282
3268.1 | 3168.1 | 398.6 | 317 | 319.9 | 262.3 | 287.1 | 282
3269.1 | 3169.1 | 398.6 | 317 | 320 | 262.3 | 287 | 282
3270.1 | 3170.1 | 398.6 | 317 | 320 | 262.4 | 287 | 282
3271.1 | 3171.1 | 398.5 | 316.9 | 320.1 | 262.4 | 286.9 | 282
3272.1 | 3172.1 | 398.5 | 317 | 320.1 | 262.4 | 286.9 | 282
3273.1 | 3173.1 | 398.4 | 316.9 | 320.2 | 262.4 | 286.7 | 281.8
3274.1 | 3174.1 | 398.4 | 316.8 | 320.2 | 262.5 | 286.6 | 281.8
3275.1 | 3175.1 | 398.4 | 316.8 | 320.3 | 262.5 | 286.6 | 281.9
3276.1 | 3176.1 | 398.3 | 316.8 | 320.3 | 262.5 | 286.4 | 281.9
3277.1 | 3177.1 | 398.4 | 316.8 | 320.4 | 262.6 | 286.3 | 281.9
3278.1 | 3178.1 | 398.5 | 316.7 | 320.4 | 262.6 | 286.1 | 281.9
3279.1 | 3179.1 | 398.6 | 316.7 | 320.4 | 262.6 | 285.5 | 282
3280.1 | 3180.1 | 398.5 | 316.7 | 320.5 | 262.7 | 285.6 | 281.9
3281.1 | 3181.1 | 398.6 | 316.6 | 320.5 | 262.7 | 285.8 | 282
3282.1 | 3182.1 | 398.8 | 316.5 | 320.6 | 262.7 | 286 | 281.9
3283.1 | 3183.1 | 398.8 | 316.6 | 320.6 | 262.7 | 286 | 281.9
3284.1 | 3184.1 | 398.8 | 316.6 | 320.7 | 262.8 | 286.1 | 281.9
3285.1 | 3185.1 | 398.8 | 316.6 | 320.7 | 262.8 | 286.1 | 281.9
3286.1 | 3186.1 | 399 | 316.5 | 320.8 | 262.8 | 286.4 | 281.9
3287.1 | 3187.1 | 399 | 316.6 | 320.8 | 262.9 | 286.6 | 282
3288.1 | 3188.1 | 399 | 316.5 | 320.8 | 262.9 | 286.7 | 282
3289.1 | 3189.1 | 398.9 | 316.6 | 320.9 | 262.9 | 287.1 | 281.9
3290.1 | 3190.1 | 399 | 316.6 | 320.9 | 262.9 | 287.4 | 282
3291.1 | 3191.1 | 399 | 316.6 | 321 | 263 | 287.4 | 282.1
3292.1 | 3192.1 | 399 | 316.6 | 321 | 263 | 287.5 | 282.1
3293.1 | 3193.1 | 399 | 316.6 | 321 | 263 | 287.5 | 282.2
3294.1 | 3194.1 | 398.9 | 316.7 | 321 | 263.1 | 287.7 | 282.3
3295.1 | 3195.1 | 398.9 | 316.8 | 321 | 263.1 | 288 | 282.3
3296.1 | 3196.1 | 398.8 | 316.7 | 321.1 | 263.1 | 288.4 | 282.4
3297.1 | 3197.1 | 398.8 | 316.8 | 321.1 | 263.1 | 288.5 | 282.3
3298.1 | 3198.1 | 398.7 | 316.8 | 321.1 | 263.2 | 288.8 | 282.3
3299.1 | 3199.1 | 398.6 | 316.9 | 321.2 | 263.2 | 289.1 | 282.4
3300.1 | 3200.1 | 398.6 | 317 | 321.2 | 263.2 | 289.2 | 282.4
3301.1 | 3201.1 | 398.6 | 317 | 321.3 | 263.3 | 289.1 | 282.4
3302.1 | 3202.1 | 398.5 | 317 | 321.4 | 263.3 | 289 | 282.4
3303.1 | 3203.1 | 398.4 | 317 | 321.4 | 263.3 | 289.2 | 282.4
3304.1 | 3204.1 | 398.5 | 317 | 321.4 | 263.4 | 289.3 | 282.4
3305.1 | 3205.1 | 398.5 | 317.1 | 321.4 | 263.4 | 289.5 | 282.5
3306.1 | 3206.1 | 398.5 | 317.1 | 321.5 | 263.4 | 289.5 | 282.5
3307.1 | 3207.1 | 398.6 | 317.2 | 321.5 | 263.4 | 289.6 | 282.5
3308.1 | 3208.1 | 398.7 | 317.2 | 321.5 | 263.5 | 289.6 | 282.5
3309.1 | 3209.1 | 398.5 | 317.3 | 321.5 | 263.5 | 289.5 | 282.5
3310.1 | 3210.1 | 398.5 | 317.3 | 321.4 | 263.5 | 289.4 | 282.4
3311.1 | 3211.1 | 398.5 | 317.3 | 321.4 | 263.6 | 289.2 | 282.4
3312.1 | 3212.1 | 398.4 | 317.2 | 321.4 | 263.6 | 289 | 282.4
3313.1 | 3213.1 | 398.4 | 317.2 | 321.3 | 263.6 | 288.9 | 282.5
3314.1 | 3214.1 | 398.3 | 317.3 | 321.3 | 263.7 | 288.9 | 282.5
3315.1 | 3215.1 | 398.3 | 317.3 | 321.3 | 263.7 | 288.9 | 282.6
3316.1 | 3216.1 | 398.4 | 317.3 | 321.3 | 263.7 | 288.9 | 282.3
3317.1 | 3217.1 | 398.3 | 317.4 | 321.2 | 263.8 | 288.9 | 282.4
3318.1 | 3218.1 | 398.2 | 317.5 | 321.1 | 263.8 | 288.9 | 282.5
3319.1 | 3219.1 | 398.2 | 317.6 | 321.1 | 263.8 | 288.8 | 282.5
3320.1 | 3220.1 | 398.4 | 317.6 | 321.1 | 263.8 | 288.9 | 282.4
3321.1 | 3221.1 | 398.5 | 317.7 | 321.1 | 263.9 | 288.8 | 282.4
3322.1 | 3222.1 | 398.5 | 317.7 | 321.1 | 263.9 | 288.7 | 282.4
3323.1 | 3223.1 | 398.7 | 317.9 | 321.1 | 263.9 | 288.7 | 282.4
3324.1 | 3224.1 | 398.8 | 318 | 321.1 | 264 | 288.7 | 282.4
3325.1 | 3225.1 | 398.9 | 318.2 | 321.1 | 264 | 288.9 | 282.3
3326.1 | 3226.1 | 398.8 | 318.2 | 321.1 | 264 | 289 | 282.3
3327.1 | 3227.1 | 398.7 | 318.4 | 321.2 | 264 | 289.2 | 282.3
3328.1 | 3228.1 | 398.7 | 318.5 | 321.2 | 264.1 | 289.3 | 282.3
3329.1 | 3229.1 | 398.6 | 318.6 | 321.2 | 264.1 | 289.3 | 282.2
3330.1 | 3230.1 | 398.7 | 318.6 | 321.3 | 264.1 | 289.3 | 282.2
3331.1 | 3231.1 | 398.8 | 318.5 | 321.3 | 264.2 | 289.3 | 282.1
3332.1 | 3232.1 | 399 | 318.6 | 321.3 | 264.2 | 289.4 | 282
3333.1 | 3233.1 | 399 | 318.5 | 321.3 | 264.2 | 289.2 | 282.1
3334.1 | 3234.1 | 399.1 | 318.4 | 321.4 | 264.2 | 288.9 | 282.1
3335.1 | 3235.1 | 399.2 | 318.3 | 321.4 | 264.3 | 288.7 | 282
3336.1 | 3236.1 | 399.2 | 318.3 | 321.4 | 264.3 | 288.8 | 282
3337.1 | 3237.1 | 399.2 | 318.3 | 321.4 | 264.3 | 288.9 | 282
3338.1 | 3238.1 | 399.1 | 318.3 | 321.4 | 264.4 | 288.7 | 282
3339.1 | 3239.1 | 398.9 | 318.3 | 321.5 | 264.4 | 288.5 | 282
3340.1 | 3240.1 | 398.7 | 318.2 | 321.5 | 264.4 | 288.4 | 282
3341.1 | 3241.1 | 398.6 | 318.1 | 321.5 | 264.4 | 288.3 | 281.9
3342.1 | 3242.1 | 398.6 | 318.1 | 321.5 | 264.5 | 288 | 281.9
3343.1 | 3243.1 | 398.6 | 318.1 | 321.5 | 264.5 | 288 | 281.7
3344.1 | 3244.1 | 398.6 | 318 | 321.5 | 264.5 | 287.8 | 281.7
3345.1 | 3245.1 | 398.5 | 318 | 321.5 | 264.6 | 287.7 | 281.7
3346.1 | 3246.1 | 398.4 | 318 | 321.6 | 264.6 | 287.6 | 281.7
3347.1 | 3247.1 | 398.2 | 318 | 321.6 | 264.6 | 287.4 | 281.7
3348.1 | 3248.1 | 398 | 318.1 | 321.6 | 264.7 | 287.2 | 281.7
3349.1 | 3249.1 | 397.9 | 318.1 | 321.7 | 264.7 | 287.2 | 281.6
3350.1 | 3250.1 | 397.9 | 318.1 | 321.7 | 264.7 | 287.1 | 281.7
3351.1 | 3251.1 | 397.9 | 318.2 | 321.8 | 264.8 | 287.3 | 281.6
3352.1 | 3252.1 | 397.8 | 318.2 | 321.8 | 264.8 | 287.3 | 281.5
3353.1 | 3253.1 | 397.9 | 318.3 | 321.8 | 264.8 | 287.2 | 281.5
3354.1 | 3254.1 | 398 | 318.4 | 321.9 | 264.8 | 287.1 | 281.5
3355.1 | 3255.1 | 398.1 | 318.4 | 321.9 | 264.9 | 287 | 281.5
3356.1 | 3256.1 | 398.2 | 318.5 | 322 | 264.9 | 287.1 | 281.5
3357.1 | 3257.1 | 398.3 | 318.5 | 322.1 | 264.9 | 287.4 | 281.4
3358.1 | 3258.1 | 398.3 | 318.6 | 322.2 | 264.9 | 287.3 | 281.4
3359.1 | 3259.1 | 398.2 | 318.6 | 322.3 | 265 | 287.1 | 281.5
3360.1 | 3260.1 | 398.3 | 318.6 | 322.4 | 265 | 287.2 | 281.5
3361.1 | 3261.1 | 398.3 | 318.6 | 322.4 | 265 | 287.4 | 281.5
3362.1 | 3262.1 | 398.3 | 318.7 | 322.5 | 265.1 | 287.6 | 281.5
3363.1 | 3263.1 | 398.2 | 318.7 | 322.6 | 265.1 | 287.8 | 281.6
3364.1 | 3264.1 | 398.1 | 318.7 | 322.7 | 265.1 | 288 | 281.6
3365.1 | 3265.1 | 398 | 318.7 | 322.8 | 265.2 | 288.3 | 281.6
3366.1 | 3266.1 | 397.9 | 318.8 | 322.8 | 265.2 | 288.6 | 281.6
3367.1 | 3267.1 | 398 | 318.8 | 322.9 | 265.2 | 288.4 | 281.7
3368.1 | 3268.1 | 398 | 318.8 | 322.9 | 265.3 | 288.3 | 281.7
3369.1 | 3269.1 | 398.1 | 318.7 | 323 | 265.3 | 288.3 | 281.7
3370.1 | 3270.1 | 398.1 | 318.6 | 323 | 265.3 | 288.2 | 281.7
3371.1 | 3271.1 | 398 | 318.6 | 323.1 | 265.3 | 287.9 | 281.7
3372.1 | 3272.1 | 398 | 318.7 | 323.1 | 265.4 | 287.5 | 281.7
3373.1 | 3273.1 | 398 | 318.7 | 323.1 | 265.4 | 287.5 | 281.7
3374.1 | 3274.1 | 398.1 | 318.7 | 323.1 | 265.4 | 287.6 | 281.8
3375.1 | 3275.1 | 398.3 | 318.7 | 323.2 | 265.5 | 287.5 | 281.8
3376.1 | 3276.1 | 398.3 | 318.7 | 323.2 | 265.5 | 287.3 | 281.7
3377.1 | 3277.1 | 398.1 | 318.7 | 323.2 | 265.5 | 287.2 | 281.7
3378.1 | 3278.1 | 398 | 318.8 | 323.3 | 265.5 | 287.3 | 281.7
3379.1 | 3279.1 | 398.1 | 318.9 | 323.3 | 265.6 | 287.5 | 281.6
3380.1 | 3280.1 | 398 | 318.9 | 323.3 | 265.6 | 287.6 | 281.5
3381.1 | 3281.1 | 398.1 | 319 | 323.3 | 265.6 | 287.6 | 281.4
3382.1 | 3282.1 | 398.1 | 319.2 | 323.4 | 265.6 | 287.7 | 281.3
3383.1 | 3283.1 | 398 | 319.3 | 323.4 | 265.7 | 287.6 | 281.3
3384.1 | 3284.1 | 397.8 | 319.4 | 323.5 | 265.7 | 287.7 | 281.3
3385.1 | 3285.1 | 397.7 | 319.4 | 323.5 | 265.7 | 287.7 | 281.3
3386.1 | 3286.1 | 397.6 | 319.4 | 323.5 | 265.8 | 287.6 | 281.3
3387.1 | 3287.1 | 397.6 | 319.5 | 323.5 | 265.8 | 287.4 | 281.4
3388.1 | 3288.1 | 397.4 | 319.5 | 323.6 | 265.8 | 287.6 | 281.2
3389.1 | 3289.1 | 397.3 | 319.5 | 323.6 | 265.8 | 287.6 | 281.2
3390.1 | 3290.1 | 397.2 | 319.5 | 323.7 | 265.9 | 287.6 | 281.2
3391.1 | 3291.1 | 397.3 | 319.5 | 323.7 | 265.9 | 287.4 | 281.2
3392.1 | 3292.1 | 397.4 | 319.5 | 323.7 | 265.9 | 287.3 | 281.1
3393.1 | 3293.1 | 397.6 | 319.5 | 323.8 | 266 | 287.4 | 281.1
3394.1 | 3294.1 | 397.7 | 319.5 | 323.8 | 266 | 287.5 | 281.1
3395.1 | 3295.1 | 397.8 | 319.6 | 323.8 | 266 | 287.4 | 281.1
3396.1 | 3296.1 | 397.9 | 319.6 | 323.8 | 266.1 | 287.5 | 281
3397.1 | 3297.1 | 398 | 319.6 | 323.9 | 266.1 | 287.5 | 281
3398.1 | 3298.1 | 398 | 319.6 | 323.9 | 266.1 | 287.4 | 281.1
3399.1 | 3299.1 | 398.3 | 319.5 | 323.9 | 266.1 | 287.4 | 281.1
3400.1 | 3300.1 | 398.4 | 319.6 | 323.9 | 266.2 | 287.5 | 281.1
3401.1 | 3301.1 | 398.3 | 319.7 | 324 | 266.2 | 287.5 | 281.1
3402.1 | 3302.1 | 398 | 319.7 | 324 | 266.2 | 287.6 | 281
3403.1 | 3303.1 | 398 | 319.8 | 324.1 | 266.3 | 287.6 | 280.8
3404.1 | 3304.1 | 398.1 | 319.8 | 324.1 | 266.3 | 287.6 | 280.8
3405.1 | 3305.1 | 398.3 | 319.8 | 324.1 | 266.3 | 287.3 | 280.8
3406.1 | 3306.1 | 398.4 | 319.9 | 324.2 | 266.3 | 287.1 | 280.8
3407.1 | 3307.1 | 398.4 | 319.9 | 324.2 | 266.4 | 287 | 280.9
3408.1 | 3308.1 | 398.6 | 320 | 324.3 | 266.4 | 287.1 | 280.9
3409.1 | 3309.1 | 398.6 | 320 | 324.3 | 266.4 | 287.2 | 280.8
3410.1 | 3310.1 | 398.6 | 320 | 324.4 | 266.5 | 287.3 | 280.8
3411.1 | 3311.1 | 398.7 | 320 | 324.4 | 266.5 | 287.3 | 280.8
3412.1 | 3312.1 | 398.7 | 320 | 324.5 | 266.5 | 287.3 | 280.7
3413.1 | 3313.1 | 398.9 | 320 | 324.5 | 266.6 | 287.5 | 280.8
3414.1 | 3314.1 | 398.9 | 320 | 324.5 | 266.6 | 287.5 | 280.8
3415.1 | 3315.1 | 399 | 320.1 | 324.6 | 266.6 | 287.7 | 280.9
3416.1 | 3316.1 | 399.1 | 320.1 | 324.6 | 266.6 | 287.5 | 280.8
3417.1 | 3317.1 | 399.2 | 320.1 | 324.6 | 266.7 | 287.1 | 280.8
3418.1 | 3318.1 | 399.5 | 320.2 | 324.7 | 266.7 | 287.2 | 280.8
3419.1 | 3319.1 | 399.7 | 320.2 | 324.7 | 266.7 | 287.1 | 280.8
3420.1 | 3320.1 | 399.8 | 320.2 | 324.7 | 266.8 | 286.9 | 280.8
3421.1 | 3321.1 | 399.9 | 320.3 | 324.8 | 266.8 | 286.9 | 280.9
3422.1 | 3322.1 | 399.8 | 320.4 | 324.8 | 266.8 | 287.2 | 280.9
3423.1 | 3323.1 | 399.7 | 320.5 | 324.8 | 266.8 | 287.1 | 280.9
3424.1 | 3324.1 | 399.6 | 320.5 | 324.9 | 266.9 | 286.9 | 281
3425.1 | 3325.1 | 399.8 | 320.5 | 324.9 | 266.9 | 286.7 | 281.1
3426.1 | 3326.1 | 399.9 | 320.6 | 325 | 266.9 | 286.7 | 281.1
3427.1 | 3327.1 | 399.9 | 320.7 | 325 | 267 | 286.7 | 281.1
3428.1 | 3328.1 | 400.1 | 320.7 | 325.1 | 267 | 286.5 | 281.1
3429.1 | 3329.1 | 400.3 | 320.7 | 325.2 | 267 | 286.1 | 281.1
3430.1 | 3330.1 | 400.4 | 320.6 | 325.2 | 267 | 286 | 281.1
3431.1 | 3331.1 | 400.2 | 320.6 | 325.3 | 267 | 285.9 | 281.2
3432.1 | 3332.1 | 400 | 320.6 | 325.3 | 267.1 | 286.3 | 281.2
3433.1 | 3333.1 | 400 | 320.7 | 325.4 | 267.1 | 286.8 | 281.3
3434.1 | 3334.1 | 399.9 | 320.7 | 325.5 | 267.1 | 287 | 281.3
3435.1 | 3335.1 | 399.6 | 320.7 | 325.5 | 267.2 | 287.4 | 281.4
3436.1 | 3336.1 | 399.6 | 320.7 | 325.6 | 267.2 | 287.6 | 281.5
3437.1 | 3337.1 | 399.3 | 320.8 | 325.6 | 267.2 | 288 | 281.5
3438.1 | 3338.1 | 399.2 | 320.8 | 325.7 | 267.2 | 288.2 | 281.5
3439.1 | 3339.1 | 399.1 | 320.9 | 325.7 | 267.3 | 288.6 | 281.5
3440.1 | 3340.1 | 399 | 321 | 325.8 | 267.3 | 289.1 | 281.6
3441.1 | 3341.1 | 398.7 | 321.1 | 325.8 | 267.3 | 289.5 | 281.7
3442.1 | 3342.1 | 398.5 | 321.1 | 325.8 | 267.4 | 289.9 | 281.8
3443.1 | 3343.1 | 398.4 | 321.1 | 325.8 | 267.4 | 290.1 | 281.9
3444.1 | 3344.1 | 398.4 | 321.2 | 325.9 | 267.4 | 290.2 | 281.9
3445.1 | 3345.1 | 398.3 | 321.2 | 325.9 | 267.5 | 290.4 | 282
3446.1 | 3346.1 | 398.2 | 321.2 | 325.9 | 267.5 | 290.5 | 282
3447.1 | 3347.1 | 398 | 321.3 | 325.9 | 267.5 | 290.7 | 282
3448.1 | 3348.1 | 397.9 | 321.3 | 325.9 | 267.5 | 291 | 282
3449.1 | 3349.1 | 397.9 | 321.3 | 326 | 267.6 | 291.3 | 282
3450.1 | 3350.1 | 398.1 | 321.4 | 326 | 267.6 | 291.5 | 282.1
3451.1 | 3351.1 | 398.2 | 321.4 | 326 | 267.7 | 291.8 | 282.2
3452.1 | 3352.1 | 398.3 | 321.4 | 326 | 267.7 | 292.2 | 282.2
3453.1 | 3353.1 | 398.1 | 321.4 | 326 | 267.7 | 292.4 | 282.3
3454.1 | 3354.1 | 398 | 321.5 | 326 | 267.8 | 292.8 | 282.3
3455.1 | 3355.1 | 397.8 | 321.4 | 326.1 | 267.8 | 292.7 | 282.4
3456.1 | 3356.1 | 397.9 | 321.4 | 326.1 | 267.8 | 292.7 | 282.4
3457.1 | 3357.1 | 398 | 321.5 | 326.1 | 267.8 | 292.8 | 282.4
3458.1 | 3358.1 | 397.9 | 321.5 | 326.1 | 267.9 | 292.9 | 282.5
3459.1 | 3359.1 | 397.9 | 321.5 | 326.1 | 267.9 | 292.9 | 282.5
3460.1 | 3360.1 | 398 | 321.5 | 326.1 | 267.9 | 292.8 | 282.5
3461.1 | 3361.1 | 398.1 | 321.6 | 326.1 | 268 | 292.8 | 282.6
3462.1 | 3362.1 | 398.1 | 321.5 | 326.1 | 268 | 292.9 | 282.6
3463.1 | 3363.1 | 398.1 | 321.5 | 326.1 | 268 | 292.9 | 282.7
3464.1 | 3364.1 | 398.3 | 321.5 | 326.1 | 268 | 292.8 | 282.7
3465.1 | 3365.1 | 398.3 | 321.5 | 326.1 | 268.1 | 292.4 | 282.8
3466.1 | 3366.1 | 398.4 | 321.5 | 326.1 | 268.1 | 292 | 282.8
3467.1 | 3367.1 | 398.6 | 321.5 | 326.1 | 268.1 | 292 | 282.8
3468.1 | 3368.1 | 398.6 | 321.5 | 326 | 268.2 | 291.8 | 282.8
3469.1 | 3369.1 | 398.7 | 321.5 | 326 | 268.2 | 291.6 | 282.8
3470.1 | 3370.1 | 398.6 | 321.5 | 326 | 268.2 | 291.5 | 282.8
3471.1 | 3371.1 | 398.6 | 321.5 | 326 | 268.2 | 291.2 | 282.8
3472.1 | 3372.1 | 398.5 | 321.4 | 326 | 268.3 | 291.1 | 282.8
3473.1 | 3373.1 | 398.4 | 321.5 | 326 | 268.3 | 290.8 | 282.8
3474.1 | 3374.1 | 398.3 | 321.6 | 326 | 268.3 | 290.7 | 282.8
3475.1 | 3375.1 | 398.2 | 321.6 | 326 | 268.4 | 290.7 | 282.8
3476.1 | 3376.1 | 398.2 | 321.6 | 326 | 268.4 | 290.9 | 282.9
3477.1 | 3377.1 | 398.3 | 321.7 | 326 | 268.4 | 290.7 | 282.9
3478.1 | 3378.1 | 398.3 | 321.8 | 326.1 | 268.5 | 290.8 | 283
3479.1 | 3379.1 | 398.3 | 321.8 | 326.1 | 268.5 | 290.8 | 283
3480.1 | 3380.1 | 398.4 | 321.8 | 326.1 | 268.5 | 291 | 283
3481.1 | 3381.1 | 398.4 | 321.9 | 326.1 | 268.6 | 290.6 | 283
3482.1 | 3382.1 | 398.4 | 321.9 | 326.2 | 268.6 | 290.3 | 283
3483.1 | 3383.1 | 398.5 | 321.9 | 326.2 | 268.6 | 290.3 | 283
3484.1 | 3384.1 | 398.6 | 322 | 326.2 | 268.6 | 290.1 | 283.1
3485.1 | 3385.1 | 398.6 | 322 | 326.3 | 268.7 | 290.1 | 283.1
3486.1 | 3386.1 | 398.6 | 322 | 326.3 | 268.7 | 290.1 | 283.2
3487.1 | 3387.1 | 398.7 | 322 | 326.3 | 268.7 | 289.9 | 283.2
3488.1 | 3388.1 | 398.7 | 322 | 326.4 | 268.7 | 290.1 | 283.2
3489.1 | 3389.1 | 398.6 | 322 | 326.4 | 268.8 | 290.2 | 283.3
3490.1 | 3390.1 | 398.6 | 322 | 326.5 | 268.8 | 290.3 | 283.3
3491.1 | 3391.1 | 398.6 | 322 | 326.5 | 268.8 | 290.1 | 283.3
3492.1 | 3392.1 | 398.5 | 322 | 326.5 | 268.8 | 290.2 | 283.3
3493.1 | 3393.1 | 398.4 | 322 | 326.5 | 268.9 | 290.2 | 283.4
3494.1 | 3394.1 | 398.4 | 322.1 | 326.6 | 268.9 | 290.3 | 283.4
3495.1 | 3395.1 | 398.3 | 322.1 | 326.6 | 268.9 | 290.2 | 283.4
3496.1 | 3396.1 | 398.3 | 322.2 | 326.6 | 268.9 | 290.1 | 283.5
3497.1 | 3397.1 | 398.2 | 322.2 | 326.6 | 269 | 290.3 | 283.5
3498.1 | 3398.1 | 398.2 | 322.2 | 326.6 | 269 | 290.3 | 283.6
3499.1 | 3399.1 | 398.1 | 322.2 | 326.6 | 269 | 290 | 283.7
3500.1 | 3400.1 | 398.1 | 322.2 | 326.7 | 269.1 | 289.7 | 283.8
3501.1 | 3401.1 | 398.2 | 322.2 | 326.7 | 269.1 | 289.8 | 283.8
3502.1 | 3402.1 | 398.2 | 322.2 | 326.7 | 269.1 | 289.6 | 283.8
3503.1 | 3403.1 | 398.2 | 322.2 | 326.7 | 269.2 | 289.5 | 283.8
3504.1 | 3404.1 | 398.3 | 322.2 | 326.8 | 269.2 | 289.2 | 283.8
3505.1 | 3405.1 | 398.4 | 322.2 | 326.8 | 269.2 | 288.9 | 283.8
3506.1 | 3406.1 | 398.6 | 322.2 | 326.8 | 269.2 | 288.7 | 283.7
3507.1 | 3407.1 | 398.6 | 322.2 | 326.8 | 269.2 | 288.9 | 283.7
3508.1 | 3408.1 | 398.6 | 322.2 | 326.9 | 269.3 | 289 | 283.7
3509.1 | 3409.1 | 398.7 | 322.3 | 326.9 | 269.3 | 288.9 | 283.7
3510.1 | 3410.1 | 398.9 | 322.4 | 326.9 | 269.3 | 288.9 | 283.8
3511.1 | 3411.1 | 398.8 | 322.4 | 326.9 | 269.4 | 288.8 | 283.8
3512.1 | 3412.1 | 398.8 | 322.4 | 326.9 | 269.4 | 288.7 | 283.9
3513.1 | 3413.1 | 398.9 | 322.3 | 327 | 269.4 | 288.6 | 283.9
3514.1 | 3414.1 | 398.9 | 322.2 | 327 | 269.4 | 288.4 | 283.8
3515.1 | 3415.1 | 399.1 | 322.2 | 327 | 269.5 | 288.4 | 283.9
3516.1 | 3416.1 | 399.1 | 322.2 | 327.1 | 269.5 | 288.2 | 283.9
3517.1 | 3417.1 | 399.1 | 322.2 | 327.1 | 269.5 | 288.2 | 283.9
3518.1 | 3418.1 | 399.1 | 322.2 | 327.1 | 269.6 | 288.1 | 283.9
3519.1 | 3419.1 | 399.1 | 322.1 | 327.2 | 269.6 | 287.9 | 283.9
3520.1 | 3420.1 | 399.1 | 322.1 | 327.2 | 269.6 | 288.1 | 284
3521.1 | 3421.1 | 399.4 | 322.1 | 327.3 | 269.6 | 288.3 | 284
3522.1 | 3422.1 | 399.5 | 322.1 | 327.3 | 269.7 | 288.1 | 284
3523.1 | 3423.1 | 399.5 | 322 | 327.3 | 269.7 | 288.1 | 284.1
3524.1 | 3424.1 | 399.6 | 322.1 | 327.4 | 269.7 | 288.2 | 284.1
3525.1 | 3425.1 | 399.6 | 322.1 | 327.4 | 269.8 | 288.2 | 284.1
3526.1 | 3426.1 | 399.6 | 322.2 | 327.5 | 269.8 | 288.3 | 284.2
3527.1 | 3427.1 | 399.5 | 322.2 | 327.5 | 269.8 | 288.3 | 284.2
3528.1 | 3428.1 | 399.5 | 322.2 | 327.6 | 269.8 | 288.3 | 284.2
3529.1 | 3429.1 | 399.3 | 322.3 | 327.6 | 269.9 | 288.2 | 284.2
3530.1 | 3430.1 | 399.1 | 322.3 | 327.6 | 269.9 | 288.3 | 284.2
3531.1 | 3431.1 | 399.1 | 322.4 | 327.7 | 269.9 | 288.3 | 284.3
3532.1 | 3432.1 | 399 | 322.4 | 327.7 | 270 | 288.4 | 284.3
3533.1 | 3433.1 | 398.8 | 322.5 | 327.7 | 270 | 288.5 | 284.3
3534.1 | 3434.1 | 398.6 | 322.5 | 327.8 | 270 | 288.5 | 284.4
3535.1 | 3435.1 | 398.4 | 322.6 | 327.8 | 270 | 288.5 | 284.4
3536.1 | 3436.1 | 398.4 | 322.7 | 327.9 | 270.1 | 288.6 | 284.4
3537.1 | 3437.1 | 398.5 | 322.8 | 327.9 | 270.1 | 288.7 | 284.5
3538.1 | 3438.1 | 398.4 | 322.9 | 327.9 | 270.1 | 288.9 | 284.5
3539.1 | 3439.1 | 398.3 | 322.9 | 328 | 270.2 | 288.7 | 284.5
3540.1 | 3440.1 | 398.3 | 322.9 | 328 | 270.2 | 288.7 | 284.5
3541.1 | 3441.1 | 398.2 | 322.9 | 328.1 | 270.2 | 288.7 | 284.6
3542.1 | 3442.1 | 398.2 | 323.1 | 328.1 | 270.2 | 288.5 | 284.6
3543.1 | 3443.1 | 398.2 | 323.2 | 328.1 | 270.3 | 288.4 | 284.6
3544.1 | 3444.1 | 398.2 | 323.2 | 328.2 | 270.3 | 288.5 | 284.6
3545.1 | 3445.1 | 398 | 323.3 | 328.2 | 270.3 | 288.6 | 284.6
3546.1 | 3446.1 | 398 | 323.3 | 328.2 | 270.3 | 288.6 | 284.6
3547.1 | 3447.1 | 398 | 323.3 | 328.3 | 270.4 | 288.4 | 284.6
3548.1 | 3448.1 | 397.9 | 323.2 | 328.3 | 270.4 | 287.9 | 284.6
3549.1 | 3449.1 | 397.7 | 323.2 | 328.3 | 270.4 | 287.8 | 284.7
3550.1 | 3450.1 | 397.6 | 323.1 | 328.4 | 270.4 | 287.9 | 284.7
3551.1 | 3451.1 | 397.5 | 323 | 328.4 | 270.5 | 287.4 | 284.8
3552.1 | 3452.1 | 397.5 | 322.9 | 328.4 | 270.5 | 287.2 | 284.8
3553.1 | 3453.1 | 397.5 | 322.9 | 328.5 | 270.5 | 287.2 | 284.8
3554.1 | 3454.1 | 397.6 | 322.8 | 328.5 | 270.6 | 287.3 | 284.8
3555.1 | 3455.1 | 397.8 | 322.8 | 328.5 | 270.6 | 287.3 | 284.8
3556.1 | 3456.1 | 397.8 | 322.9 | 328.6 | 270.6 | 287.4 | 284.8
3557.1 | 3457.1 | 397.7 | 322.9 | 328.6 | 270.6 | 287.1 | 284.9
3558.1 | 3458.1 | 397.5 | 322.9 | 328.6 | 270.7 | 287 | 284.9
3559.1 | 3459.1 | 397.4 | 322.8 | 328.7 | 270.7 | 287 | 284.9
3560.1 | 3460.1 | 397.4 | 322.8 | 328.7 | 270.7 | 287.1 | 284.9
3561.1 | 3461.1 | 397.4 | 322.8 | 328.7 | 270.7 | 286.9 | 284.9
3562.1 | 3462.1 | 397.6 | 322.8 | 328.8 | 270.8 | 286.6 | 284.9
3563.1 | 3463.1 | 397.7 | 322.8 | 328.8 | 270.8 | 286.6 | 284.9
3564.1 | 3464.1 | 397.8 | 322.8 | 328.8 | 270.8 | 286.4 | 284.9
3565.1 | 3465.1 | 397.8 | 322.9 | 328.8 | 270.8 | 286.2 | 284.9
3566.1 | 3466.1 | 397.8 | 322.9 | 328.9 | 270.9 | 286.1 | 284.9
3567.1 | 3467.1 | 397.8 | 322.9 | 328.9 | 270.9 | 286.3 | 284.8
3568.1 | 3468.1 | 398 | 323 | 328.9 | 270.9 | 286.6 | 284.8
3569.1 | 3469.1 | 398.2 | 323 | 329 | 270.9 | 286.4 | 284.8
3570.1 | 3470.1 | 398.3 | 323.1 | 329 | 271 | 286.4 | 284.8
3571.1 | 3471.1 | 398.3 | 323.1 | 329 | 271 | 286.7 | 284.8
3572.1 | 3472.1 | 398.3 | 323.1 | 329.1 | 271 | 286.9 | 284.8
3573.1 | 3473.1 | 398.4 | 323.1 | 329.1 | 271.1 | 287.2 | 284.8
3574.1 | 3474.1 | 398.5 | 323.1 | 329.1 | 271.1 | 287 | 284.8
3575.1 | 3475.1 | 398.5 | 323 | 329.2 | 271.1 | 287.1 | 284.8
3576.1 | 3476.1 | 398.4 | 323 | 329.2 | 271.2 | 287.2 | 284.8
3577.1 | 3477.1 | 398.5 | 322.9 | 329.3 | 271.2 | 287.3 | 284.8
3578.1 | 3478.1 | 398.6 | 322.9 | 329.3 | 271.2 | 287.4 | 284.7
3579.1 | 3479.1 | 398.6 | 323 | 329.3 | 271.2 | 287.4 | 284.7
3580.1 | 3480.1 | 398.7 | 322.9 | 329.4 | 271.3 | 287.3 | 284.7
3581.1 | 3481.1 | 398.6 | 323 | 329.4 | 271.3 | 287.5 | 284.7
3582.1 | 3482.1 | 398.5 | 323 | 329.4 | 271.3 | 287.7 | 284.6
3583.1 | 3483.1 | 398.4 | 323.1 | 329.4 | 271.4 | 287.6 | 284.6
3584.1 | 3484.1 | 398.3 | 323.1 | 329.4 | 271.4 | 287.7 | 284.6
3585.1 | 3485.1 | 398.1 | 323.3 | 329.5 | 271.4 | 287.8 | 284.6
3586.1 | 3486.1 | 398.1 | 323.4 | 329.5 | 271.4 | 287.8 | 284.5
3587.1 | 3487.1 | 398 | 323.5 | 329.5 | 271.5 | 287.8 | 284.4
3588.1 | 3488.1 | 397.9 | 323.6 | 329.5 | 271.5 | 287.9 | 284.4
3589.1 | 3489.1 | 397.8 | 323.7 | 329.6 | 271.5 | 287.7 | 284.4
3590.1 | 3490.1 | 397.6 | 323.7 | 329.6 | 271.5 | 287.4 | 284.3
3591.1 | 3491.1 | 397.6 | 323.7 | 329.6 | 271.5 | 287.2 | 284.3
3592.1 | 3492.1 | 397.6 | 323.6 | 329.6 | 271.5 | 287.3 | 284.3
3593.1 | 3493.1 | 397.9 | 323.5 | 329.6 | 271.6 | 287.4 | 284.3
3594.1 | 3494.1 | 398.1 | 323.6 | 329.6 | 271.6 | 287.6 | 284.2
3595.1 | 3495.1 | 398.1 | 323.7 | 329.6 | 271.6 | 287.5 | 284.2
3596.1 | 3496.1 | 398 | 323.6 | 329.7 | 271.7 | 287.4 | 284.2
3597.1 | 3497.1 | 398 | 323.5 | 329.7 | 271.7 | 287.4 | 284.2
3598.1 | 3498.1 | 398.2 | 323.4 | 329.7 | 271.7 | 287.5 | 284.2
3599.1 | 3499.1 | 398.5 | 323.4 | 329.7 | 271.7 | 287.1 | 284.2
3600.1 | 3500.1 | 398.7 | 323.4 | 329.7 | 271.8 | 287 | 284.2
3601.1 | 3501.1 | 398.8 | 323.4 | 329.8 | 271.8 | 287.1 | 284.2
3602.1 | 3502.1 | 398.9 | 323.3 | 329.8 | 271.8 | 286.8 | 284.2
3603.1 | 3503.1 | 399.1 | 323.3 | 329.8 | 271.8 | 286.7 | 284.2
3604.1 | 3504.1 | 399 | 323.3 | 329.8 | 271.9 | 286.8 | 284.2
3605.1 | 3505.1 | 398.9 | 323.3 | 329.8 | 271.9 | 286.9 | 284.2
3606.1 | 3506.1 | 398.8 | 323.3 | 329.8 | 271.9 | 286.9 | 284.2
3607.1 | 3507.1 | 398.7 | 323.3 | 329.8 | 272 | 286.8 | 284.3
3608.1 | 3508.1 | 398.6 | 323.3 | 329.8 | 272 | 286.9 | 284.2
3609.1 | 3509.1 | 398.7 | 323.4 | 329.8 | 272 | 287.1 | 284.1
3610.1 | 3510.1 | 398.8 | 323.5 | 329.8 | 272 | 287.3 | 284.1
3611.1 | 3511.1 | 398.7 | 323.4 | 329.8 | 272.1 | 287.3 | 284.2
3612.1 | 3512.1 | 398.6 | 323.4 | 329.8 | 272.1 | 287.4 | 284.2
3613.1 | 3513.1 | 398.6 | 323.3 | 329.8 | 272.1 | 287.7 | 284.2
3614.1 | 3514.1 | 398.6 | 323.3 | 329.8 | 272.1 | 287.5 | 284.2
3615.1 | 3515.1 | 398.6 | 323.4 | 329.8 | 272.2 | 287.7 | 284.2
3616.1 | 3516.1 | 398.6 | 323.3 | 329.8 | 272.2 | 287.7 | 284.2
3617.1 | 3517.1 | 398.6 | 323.3 | 329.8 | 272.2 | 287.8 | 284.2
3618.1 | 3518.1 | 398.4 | 323.3 | 329.8 | 272.2 | 288.2 | 284.2
3619.1 | 3519.1 | 398.2 | 323.4 | 329.8 | 272.3 | 288.6 | 284.3
3620.1 | 3520.1 | 398 | 323.4 | 329.9 | 272.3 | 288.7 | 284.3
3621.1 | 3521.1 | 398.1 | 323.3 | 329.9 | 272.3 | 288.9 | 284.4
3622.1 | 3522.1 | 398 | 323.3 | 329.9 | 272.4 | 288.8 | 284.4
3623.1 | 3523.1 | 397.9 | 323.2 | 329.9 | 272.4 | 288.8 | 284.4
3624.1 | 3524.1 | 397.8 | 323.2 | 329.9 | 272.4 | 288.9 | 284.3
3625.1 | 3525.1 | 397.7 | 323.4 | 329.9 | 272.4 | 288.7 | 284.3
3626.1 | 3526.1 | 397.6 | 323.3 | 329.9 | 272.5 | 288.8 | 284.4
3627.1 | 3527.1 | 397.5 | 323.4 | 329.9 | 272.5 | 288.9 | 284.4
3628.1 | 3528.1 | 397.3 | 323.4 | 329.9 | 272.5 | 288.7 | 284.4
3629.1 | 3529.1 | 397.2 | 323.4 | 329.9 | 272.6 | 288.8 | 284.5
3630.1 | 3530.1 | 397.1 | 323.5 | 329.9 | 272.6 | 289.1 | 284.5
3631.1 | 3531.1 | 397.1 | 323.6 | 329.9 | 272.6 | 289.2 | 284.5
3632.1 | 3532.1 | 397 | 323.7 | 329.9 | 272.6 | 289 | 284.3
3633.1 | 3533.1 | 396.9 | 323.6 | 329.9 | 272.7 | 288.6 | 284.3
3634.1 | 3534.1 | 396.8 | 323.6 | 329.9 | 272.7 | 288.6 | 284.3
3635.1 | 3535.1 | 396.8 | 323.6 | 329.9 | 272.7 | 288.7 | 284.3
3636.1 | 3536.1 | 396.6 | 323.7 | 330 | 272.8 | 288.8 | 284.3
3637.1 | 3537.1 | 396.5 | 323.6 | 330 | 272.8 | 288.6 | 284.3
3638.1 | 3538.1 | 396.6 | 323.6 | 330 | 272.8 | 288.3 | 284.3
3639.1 | 3539.1 | 396.8 | 323.7 | 330 | 272.8 | 288.5 | 284.3
3640.1 | 3540.1 | 396.9 | 323.8 | 330 | 272.9 | 288.5 | 284.3
3641.1 | 3541.1 | 397 | 323.8 | 330 | 272.9 | 288.6 | 284.3
3642.1 | 3542.1 | 397.1 | 323.8 | 330.1 | 272.9 | 288.7 | 284.3
3643.1 | 3543.1 | 397 | 323.8 | 330.1 | 272.9 | 288.9 | 284.3
3644.1 | 3544.1 | 397.1 | 323.9 | 330.1 | 273 | 288.9 | 284.3
3645.1 | 3545.1 | 397.3 | 323.8 | 330.1 | 273 | 288.8 | 284.3
3646.1 | 3546.1 | 397.5 | 323.8 | 330.1 | 273 | 288.9 | 284.4
3647.1 | 3547.1 | 397.5 | 323.8 | 330.1 | 273 | 288.8 | 284.4
3648.1 | 3548.1 | 397.6 | 323.8 | 330.1 | 273.1 | 289 | 284.5
3649.1 | 3549.1 | 397.8 | 323.7 | 330.1 | 273.1 | 288.8 | 284.5
3650.1 | 3550.1 | 398 | 323.7 | 330.1 | 273.1 | 289 | 284.5
3651.1 | 3551.1 | 398.3 | 323.7 | 330.2 | 273.1 | 289.4 | 284.5
3652.1 | 3552.1 | 398.5 | 323.8 | 330.2 | 273.2 | 289.8 | 284.5
3653.1 | 3553.1 | 398.7 | 323.8 | 330.2 | 273.2 | 290 | 284.5
3654.1 | 3554.1 | 399 | 323.8 | 330.3 | 273.2 | 289.9 | 284.6
3655.1 | 3555.1 | 399.1 | 323.9 | 330.3 | 273.3 | 290 | 284.6
3656.1 | 3556.1 | 399.1 | 323.9 | 330.3 | 273.3 | 290.1 | 284.6
3657.1 | 3557.1 | 399.1 | 323.8 | 330.4 | 273.3 | 290.4 | 284.6
3658.1 | 3558.1 | 399 | 323.9 | 330.4 | 273.3 | 290.4 | 284.6
3659.1 | 3559.1 | 399.1 | 324 | 330.4 | 273.3 | 290.1 | 284.6
3660.1 | 3560.1 | 399.1 | 323.9 | 330.5 | 273.4 | 289.9 | 284.4
3661.1 | 3561.1 | 399 | 323.9 | 330.5 | 273.4 | 289.8 | 284.4
3662.1 | 3562.1 | 399.1 | 323.9 | 330.5 | 273.4 | 289.9 | 284.4
3663.1 | 3563.1 | 399.1 | 323.9 | 330.5 | 273.4 | 289.7 | 284.4
3664.1 | 3564.1 | 399 | 324 | 330.5 | 273.5 | 289.7 | 284.4
3665.1 | 3565.1 | 399.1 | 323.9 | 330.5 | 273.5 | 289.6 | 284.4
3666.1 | 3566.1 | 399.1 | 323.9 | 330.6 | 273.5 | 289.6 | 284.4
3667.1 | 3567.1 | 399 | 323.9 | 330.6 | 273.5 | 289.4 | 284.4
3668.1 | 3568.1 | 399 | 323.9 | 330.6 | 273.6 | 289.2 | 284.5
3669.1 | 3569.1 | 399.1 | 323.9 | 330.6 | 273.6 | 289.3 | 284.5
3670.1 | 3570.1 | 399 | 324 | 330.6 | 273.6 | 289.2 | 284.5
3671.1 | 3571.1 | 398.9 | 324.1 | 330.7 | 273.7 | 289.1 | 284.5
3672.1 | 3572.1 | 398.9 | 324.1 | 330.7 | 273.7 | 288.8 | 284.5
3673.1 | 3573.1 | 398.8 | 323.9 | 330.7 | 273.7 | 288.8 | 284.6
3674.1 | 3574.1 | 398.7 | 324 | 330.8 | 273.7 | 288.8 | 284.6
3675.1 | 3575.1 | 398.6 | 324 | 330.8 | 273.8 | 288.4 | 284.5
3676.1 | 3576.1 | 398.6 | 324.1 | 330.8 | 273.8 | 288 | 284.5
3677.1 | 3577.1 | 398.6 | 324.1 | 330.8 | 273.8 | 288 | 284.5
3678.1 | 3578.1 | 398.6 | 324.2 | 330.8 | 273.9 | 288 | 284.5
3679.1 | 3579.1 | 398.7 | 324.2 | 330.8 | 273.9 | 288.1 | 284.6
3680.1 | 3580.1 | 398.7 | 324.2 | 330.9 | 273.9 | 288 | 284.5
3681.1 | 3581.1 | 398.7 | 324.3 | 330.9 | 273.9 | 287.9 | 284.5
3682.1 | 3582.1 | 398.6 | 324.4 | 330.9 | 274 | 287.9 | 284.6
3683.1 | 3583.1 | 398.5 | 324.4 | 330.9 | 274 | 288 | 284.6
3684.1 | 3584.1 | 398.5 | 324.5 | 330.9 | 274 | 288.2 | 284.5
3685.1 | 3585.1 | 398.5 | 324.5 | 330.9 | 274 | 288.2 | 284.5
3686.1 | 3586.1 | 398.4 | 324.6 | 330.9 | 274.1 | 288 | 284.6
3687.1 | 3587.1 | 398.4 | 324.7 | 331 | 274.1 | 287.8 | 284.6
3688.1 | 3588.1 | 398.5 | 324.7 | 331 | 274.1 | 287.8 | 284.6
3689.1 | 3589.1 | 398.5 | 324.7 | 331 | 274.2 | 288 | 284.6
3690.1 | 3590.1 | 398.5 | 324.8 | 331 | 274.2 | 288.1 | 284.6
3691.1 | 3591.1 | 398.6 | 324.9 | 331 | 274.2 | 287.9 | 284.5
3692.1 | 3592.1 | 398.7 | 325 | 331 | 274.2 | 288.2 | 284.5
3693.1 | 3593.1 | 398.6 | 325.1 | 331 | 274.3 | 288.1 | 284.5
3694.1 | 3594.1 | 398.5 | 325.2 | 331 | 274.3 | 288 | 284.4
3695.1 | 3595.1 | 398.5 | 325.1 | 331 | 274.3 | 287.9 | 284.4
3696.1 | 3596.1 | 398.6 | 325.1 | 331 | 274.3 | 287.8 | 284.4
3697.1 | 3597.1 | 398.8 | 325.2 | 331 | 274.4 | 287.9 | 284.3
3698.1 | 3598.1 | 398.9 | 325.2 | 331 | 274.4 | 287.8 | 284.2
3699.1 | 3599.1 | 398.9 | 325.2 | 331.1 | 274.4 | 287.8 | 284.2
3700.1 | 3600.1 | 399 | 325.2 | 331 | 274.4 | 287.7 | 284.3
3701.1 | 3601.1 | 399.1 | 325.2 | 331 | 274.5 | 287.6 | 284.3
3702.1 | 3602.1 | 399 | 325.2 | 331 | 274.5 | 287.6 | 284.1
3703.1 | 3603.1 | 398.9 | 325.1 | 331.1 | 274.5 | 287.6 | 284.1
3704.1 | 3604.1 | 398.9 | 325 | 331.1 | 274.5 | 287.2 | 284.1
3705.1 | 3605.1 | 398.9 | 325 | 331.1 | 274.6 | 286.8 | 284.1
3706.1 | 3606.1 | 399 | 325 | 331.1 | 274.6 | 286.7 | 284.1
3707.1 | 3607.1 | 398.8 | 325 | 331.1 | 274.6 | 286.7 | 284.1
3708.1 | 3608.1 | 398.7 | 325 | 331.1 | 274.6 | 286.7 | 284
3709.1 | 3609.1 | 398.8 | 325 | 331.2 | 274.7 | 286.7 | 284
3710.1 | 3610.1 | 398.8 | 325 | 331.2 | 274.7 | 286.8 | 284.1
3711.1 | 3611.1 | 398.7 | 324.9 | 331.2 | 274.7 | 287.1 | 284.1
3712.1 | 3612.1 | 398.6 | 324.8 | 331.2 | 274.7 | 287.1 | 284.1
3713.1 | 3613.1 | 398.5 | 324.8 | 331.2 | 274.8 | 287.1 | 284.1
3714.1 | 3614.1 | 398.4 | 324.8 | 331.3 | 274.8 | 286.7 | 284
3715.1 | 3615.1 | 398.2 | 324.6 | 331.3 | 274.8 | 286.8 | 284
3716.1 | 3616.1 | 398.2 | 324.5 | 331.3 | 274.9 | 287 | 284.1
3717.1 | 3617.1 | 398.1 | 324.5 | 331.3 | 274.9 | 287.1 | 284.1
3718.1 | 3618.1 | 398 | 324.3 | 331.3 | 274.9 | 287.1 | 284.1
3719.1 | 3619.1 | 398 | 324.4 | 331.3 | 274.9 | 287.1 | 284.1
3720.1 | 3620.1 | 398.1 | 324.4 | 331.3 | 275 | 287.1 | 284.1
3721.1 | 3621.1 | 398.1 | 324.5 | 331.3 | 275 | 286.9 | 284.1
3722.1 | 3622.1 | 397.9 | 324.6 | 331.4 | 275 | 287 | 284.1
3723.1 | 3623.1 | 397.7 | 324.7 | 331.4 | 275 | 287.1 | 284.2
3724.1 | 3624.1 | 397.7 | 324.7 | 331.4 | 275.1 | 287.3 | 284.2
3725.1 | 3625.1 | 397.7 | 324.7 | 331.4 | 275.1 | 287.5 | 284.2
3726.1 | 3626.1 | 397.7 | 324.8 | 331.4 | 275.1 | 287.5 | 284.2
3727.1 | 3627.1 | 397.7 | 324.8 | 331.4 | 275.2 | 287.6 | 284.2
3728.1 | 3628.1 | 397.6 | 324.8 | 331.4 | 275.2 | 287.8 | 284.2
3729.1 | 3629.1 | 397.5 | 324.9 | 331.5 | 275.2 | 287.9 | 284.2
3730.1 | 3630.1 | 397.4 | 324.8 | 331.5 | 275.2 | 288 | 284.3
3731.1 | 3631.1 | 397.4 | 324.8 | 331.5 | 275.3 | 288.3 | 284.3
3732.1 | 3632.1 | 397.4 | 324.9 | 331.5 | 275.3 | 288.4 | 284.2
3733.1 | 3633.1 | 397.4 | 324.9 | 331.6 | 275.3 | 288.2 | 284.1
3734.1 | 3634.1 | 397.4 | 324.9 | 331.7 | 275.3 | 288.2 | 284.1
3735.1 | 3635.1 | 397.4 | 324.9 | 331.7 | 275.3 | 288.2 | 284
3736.1 | 3636.1 | 397.2 | 325.1 | 331.7 | 275.3 | 287.9 | 284
3737.1 | 3637.1 | 396.8 | 325.2 | 331.7 | 275.3 | 287.6 | 284
3738.1 | 3638.1 | 396.3 | 325.2 | 331.8 | 275.4 | 287.6 | 284
3739.1 | 3639.1 | 395.8 | 325.3 | 331.8 | 275.4 | 287.7 | 284
3740.1 | 3640.1 | 395.2 | 325.3 | 331.8 | 275.4 | 287.7 | 283.9
3741.1 | 3641.1 | 394.5 | 325.3 | 331.8 | 275.4 | 287.6 | 283.9
3742.1 | 3642.1 | 393.8 | 325.4 | 331.8 | 275.5 | 287.6 | 283.8
3743.1 | 3643.1 | 393 | 325.3 | 331.8 | 275.5 | 287.4 | 283.8
3744.1 | 3644.1 | 392.4 | 325.2 | 331.8 | 275.5 | 287.2 | 283.7
3745.1 | 3645.1 | 391.7 | 325.2 | 331.8 | 275.5 | 287 | 283.7
3746.1 | 3646.1 | 391 | 325.1 | 331.8 | 275.6 | 286.7 | 283.6
3747.1 | 3647.1 | 390.4 | 325 | 331.7 | 275.6 | 286.5 | 283.5
3748.1 | 3648.1 | 389.9 | 324.9 | 331.7 | 275.6 | 286.4 | 283.4
3749.1 | 3649.1 | 389.2 | 324.8 | 331.7 | 275.6 | 286.5 | 283.3
3750.1 | 3650.1 | 388.4 | 324.6 | 331.7 | 275.7 | 286 | 283.1
3751.1 | 3651.1 | 387.6 | 324.5 | 331.7 | 275.7 | 285.7 | 283.1
3752.1 | 3652.1 | 386.9 | 324.4 | 331.6 | 275.7 | 285.4 | 283
3753.1 | 3653.1 | 386.2 | 324.3 | 331.6 | 275.7 | 285 | 282.9
3754.1 | 3654.1 | 385.5 | 324.2 | 331.6 | 275.8 | 284.8 | 282.8
3755.1 | 3655.1 | 384.7 | 324.1 | 331.5 | 275.8 | 284.6 | 282.7
3756.1 | 3656.1 | 383.9 | 324 | 331.4 | 275.8 | 284.5 | 282.5
3757.1 | 3657.1 | 383.2 | 323.9 | 331.4 | 275.8 | 284.7 | 282.4
3758.1 | 3658.1 | 382.6 | 323.7 | 331.3 | 275.9 | 284.1 | 282.2
3759.1 | 3659.1 | 381.8 | 323.6 | 331.2 | 275.9 | 283.8 | 282
3760.1 | 3660.1 | 381 | 323.4 | 331.2 | 275.9 | 283.6 | 281.8
3761.1 | 3661.1 | 380.1 | 323.3 | 331.1 | 275.9 | 283.5 | 281.7
3762.1 | 3662.1 | 379.2 | 323.3 | 331 | 276 | 283.4 | 281.5
3763.1 | 3663.1 | 378.3 | 323.2 | 330.9 | 276 | 283 | 281.3
3764.1 | 3664.1 | 377.5 | 323.1 | 330.8 | 276 | 282.8 | 281.2
3765.1 | 3665.1 | 376.7 | 323.1 | 330.8 | 276 | 282.5 | 280.9
3766.1 | 3666.1 | 375.9 | 322.9 | 330.7 | 276.1 | 282.3 | 280.6
3767.1 | 3667.1 | 375.1 | 322.8 | 330.6 | 276.1 | 282 | 280.5
3768.1 | 3668.1 | 374.2 | 322.6 | 330.4 | 276.1 | 281.6 | 280.3
3769.1 | 3669.1 | 373.4 | 322.5 | 330.3 | 276.1 | 281.3 | 280.2
3770.1 | 3670.1 | 372.6 | 322.4 | 330.2 | 276.2 | 281.1 | 280.2
3771.1 | 3671.1 | 371.7 | 322.3 | 330.1 | 276.2 | 281 | 280.1
3772.1 | 3672.1 | 371 | 322 | 329.9 | 276.2 | 280.6 | 279.9
3773.1 | 3673.1 | 370.2 | 321.9 | 329.8 | 276.3 | 280.3 | 279.6
3774.1 | 3674.1 | 369.2 | 321.7 | 329.7 | 276.3 | 279.9 | 279.3
3775.1 | 3675.1 | 368.3 | 321.4 | 329.5 | 276.3 | 279.6 | 279.2
3776.1 | 3676.1 | 367.4 | 321.4 | 329.4 | 276.3 | 279.5 | 279.1
3777.1 | 3677.1 | 366.7 | 321.2 | 329.2 | 276.4 | 279.3 | 278.9
3778.1 | 3678.1 | 366 | 321 | 329.1 | 276.4 | 278.8 | 278.7
3779.1 | 3679.1 | 365.3 | 320.9 | 328.9 | 276.4 | 278.8 | 278.5
3780.1 | 3680.1 | 364.4 | 320.7 | 328.7 | 276.4 | 278.9 | 278.3
3781.1 | 3681.1 | 363.6 | 320.5 | 328.5 | 276.5 | 278.5 | 278
3782.1 | 3682.1 | 362.9 | 320.4 | 328.4 | 276.5 | 278.1 | 277.8
3783.1 | 3683.1 | 362.1 | 320.2 | 328.2 | 276.5 | 278.1 | 277.5
3784.1 | 3684.1 | 361.5 | 320 | 328 | 276.5 | 277.7 | 277.3
3785.1 | 3685.1 | 360.8 | 319.7 | 327.8 | 276.5 | 277.1 | 277.1
3786.1 | 3686.1 | 360 | 319.4 | 327.6 | 276.6 | 276.7 | 277
3787.1 | 3687.1 | 359.3 | 319.2 | 327.4 | 276.6 | 276.2 | 276.7
3788.1 | 3688.1 | 358.6 | 318.9 | 327.3 | 276.6 | 275.9 | 276.5
3789.1 | 3689.1 | 358 | 318.7 | 327.1 | 276.6 | 275.8 | 276.2
3790.1 | 3690.1 | 357.3 | 318.4 | 326.9 | 276.6 | 275.6 | 275.9
3791.1 | 3691.1 | 356.6 | 318.2 | 326.7 | 276.6 | 275.1 | 275.7
3792.1 | 3692.1 | 355.8 | 318 | 326.5 | 276.7 | 274.6 | 275.5
3793.1 | 3693.1 | 355 | 317.6 | 326.3 | 276.7 | 274.1 | 275.3
3794.1 | 3694.1 | 354.2 | 317.3 | 326.1 | 276.7 | 273.9 | 275.1
3795.1 | 3695.1 | 353.4 | 317.1 | 325.9 | 276.7 | 273.7 | 274.8
3796.1 | 3696.1 | 352.6 | 316.9 | 325.7 | 276.7 | 273.5 | 274.6
3797.1 | 3697.1 | 351.9 | 316.7 | 325.5 | 276.7 | 273.1 | 274.3
3798.1 | 3698.1 | 351 | 316.5 | 325.3 | 276.7 | 272.7 | 274
3799.1 | 3699.1 | 350.2 | 316.3 | 325.1 | 276.8 | 272.4 | 273.8
3800.1 | 3700.1 | 349.6 | 316.1 | 324.9 | 276.8 | 272.2 | 273.6
3801.1 | 3701.1 | 349.2 | 315.8 | 324.7 | 276.8 | 272 | 273.4
3802.1 | 3702.1 | 348.6 | 315.5 | 324.5 | 276.8 | 271.7 | 273.1
3803.1 | 3703.1 | 347.9 | 315.2 | 324.3 | 276.8 | 271.5 | 272.7
3804.1 | 3704.1 | 347.1 | 314.8 | 324.1 | 276.8 | 271.4 | 272.4
3805.1 | 3705.1 | 346.4 | 314.6 | 323.9 | 276.8 | 270.9 | 272.3
3806.1 | 3706.1 | 345.6 | 314.4 | 323.7 | 276.8 | 270.7 | 272.1
3807.1 | 3707.1 | 344.9 | 314.1 | 323.5 | 276.8 | 270.6 | 271.8
3808.1 | 3708.1 | 344 | 313.9 | 323.2 | 276.8 | 270.4 | 271.5
3809.1 | 3709.1 | 343.1 | 313.7 | 323 | 276.8 | 270.2 | 271.3
3810.1 | 3710.1 | 342.3 | 313.5 | 322.8 | 276.8 | 269.9 | 271
3811.1 | 3711.1 | 341.5 | 313.3 | 322.6 | 276.8 | 269.4 | 270.8
3812.1 | 3712.1 | 340.7 | 313 | 322.4 | 276.8 | 269.1 | 270.5
3813.1 | 3713.1 | 339.9 | 312.7 | 322.2 | 276.8 | 268.8 | 270.3
3814.1 | 3714.1 | 339.1 | 312.5 | 322 | 276.9 | 268.6 | 270.1
3815.1 | 3715.1 | 338.4 | 312.2 | 321.8 | 276.8 | 268.3 | 269.8
3816.1 | 3716.1 | 337.7 | 311.9 | 321.6 | 276.8 | 268 | 269.5
3817.1 | 3717.1 | 337 | 311.7 | 321.3 | 276.8 | 267.6 | 269.2
3818.1 | 3718.1 | 336.4 | 311.5 | 321.1 | 276.8 | 267.3 | 268.9
3819.1 | 3719.1 | 335.8 | 311.3 | 320.9 | 276.8 | 267.5 | 268.6
3820.1 | 3720.1 | 335 | 311.1 | 320.7 | 276.8 | 267.5 | 268.4
3821.1 | 3721.1 | 334.3 | 311 | 320.4 | 276.8 | 267.2 | 268.1
3822.1 | 3722.1 | 333.8 | 310.7 | 320.2 | 276.8 | 266.8 | 267.8
3823.1 | 3723.1 | 333.3 | 310.4 | 320 | 276.8 | 266.6 | 267.6
3824.1 | 3724.1 | 332.6 | 310.3 | 319.7 | 276.8 | 266.2 | 267.3
3825.1 | 3725.1 | 332 | 310 | 319.5 | 276.8 | 266.1 | 267
3826.1 | 3726.1 | 331.4 | 309.8 | 319.3 | 276.8 | 265.8 | 266.8
3827.1 | 3727.1 | 330.6 | 309.6 | 319 | 276.8 | 265.5 | 266.4
3828.1 | 3728.1 | 329.8 | 309.3 | 318.8 | 276.8 | 265 | 265.9
3829.1 | 3729.1 | 329.2 | 309.1 | 318.6 | 276.8 | 264.7 | 265.5
3830.1 | 3730.1 | 328.5 | 308.8 | 318.3 | 276.8 | 264.4 | 265.2
3831.1 | 3731.1 | 327.8 | 308.6 | 318.1 | 276.8 | 263.8 | 264.9
3832.1 | 3732.1 | 327.1 | 308.3 | 317.9 | 276.8 | 263.4 | 264.5
3833.1 | 3733.1 | 326.5 | 308 | 317.6 | 276.7 | 262.9 | 264.3
3834.1 | 3734.1 | 325.8 | 307.9 | 317.4 | 276.7 | 262.5 | 264
3835.1 | 3735.1 | 325 | 307.7 | 317.2 | 276.7 | 262.5 | 263.8
3836.1 | 3736.1 | 324.2 | 307.5 | 316.9 | 276.7 | 262.6 | 263.5
3837.1 | 3737.1 | 323.5 | 307.2 | 316.7 | 276.7 | 262.6 | 263.2
3838.1 | 3738.1 | 322.9 | 307 | 316.4 | 276.7 | 262.3 | 262.9
3839.1 | 3739.1 | 322.3 | 306.7 | 316.2 | 276.7 | 262 | 262.6
3840.1 | 3740.1 | 321.6 | 306.6 | 316 | 276.7 | 261.9 | 262.4
3841.1 | 3741.1 | 320.9 | 306.5 | 315.7 | 276.7 | 261.9 | 262.1
3842.1 | 3742.1 | 320.3 | 306.3 | 315.5 | 276.6 | 261.7 | 261.8
3843.1 | 3743.1 | 319.8 | 306.1 | 315.2 | 276.6 | 261.4 | 261.5
3844.1 | 3744.1 | 319.2 | 306 | 315 | 276.6 | 261.3 | 261.3
3845.1 | 3745.1 | 318.4 | 305.9 | 314.8 | 276.6 | 261.2 | 261
3846.1 | 3746.1 | 317.7 | 305.8 | 314.5 | 276.6 | 261.2 | 260.8
3847.1 | 3747.1 | 317 | 305.6 | 314.3 | 276.6 | 261.2 | 260.5
3848.1 | 3748.1 | 316.3 | 305.3 | 314 | 276.5 | 261.3 | 260.1
3849.1 | 3749.1 | 315.6 | 305.1 | 313.8 | 276.5 | 261.4 | 259.8
3850.1 | 3750.1 | 314.9 | 304.9 | 313.5 | 276.5 | 261.4 | 259.5
3851.1 | 3751.1 | 314.3 | 304.7 | 313.2 | 276.5 | 261.4 | 259.2
3852.1 | 3752.1 | 313.7 | 304.5 | 313 | 276.5 | 261.2 | 259
3853.1 | 3753.1 | 313 | 304.2 | 312.7 | 276.4 | 261.1 | 258.8
3854.1 | 3754.1 | 312.5 | 304 | 312.4 | 276.4 | 261.1 | 258.5
3855.1 | 3755.1 | 311.9 | 303.9 | 312.2 | 276.4 | 260.8 | 258.2
3856.1 | 3756.1 | 311.4 | 303.7 | 311.9 | 276.4 | 260.5 | 258
3857.1 | 3757.1 | 310.8 | 303.6 | 311.6 | 276.3 | 260.1 | 257.7
3858.1 | 3758.1 | 310.2 | 303.4 | 311.4 | 276.3 | 259.4 | 257.5
3859.1 | 3759.1 | 309.6 | 303.2 | 311.1 | 276.3 | 258.8 | 257.2
3860.1 | 3760.1 | 309 | 303 | 310.8 | 276.3 | 258.3 | 257
3861.1 | 3761.1 | 308.5 | 302.8 | 310.6 | 276.2 | 257.9 | 256.7
3862.1 | 3762.1 | 308 | 302.6 | 310.3 | 276.2 | 257.4 | 256.4
3863.1 | 3763.1 | 307.5 | 302.3 | 310.1 | 276.2 | 256.5 | 256.1
3864.1 | 3764.1 | 306.9 | 302.1 | 309.8 | 276.1 | 255.6 | 255.8
3865.1 | 3765.1 | 306.4 | 301.9 | 309.5 | 276.1 | 254.6 | 255.5
3866.1 | 3766.1 | 305.8 | 301.6 | 309.3 | 276.1 | 254.1 | 255.3
3867.1 | 3767.1 | 305.1 | 301.3 | 309.1 | 276 | 253.6 | 255
3868.1 | 3768.1 | 304.5 | 301.1 | 308.8 | 276 | 253.2 | 254.7
3869.1 | 3769.1 | 303.8 | 300.8 | 308.5 | 276 | 252.8 | 254.4
3870.1 | 3770.1 | 303.1 | 300.4 | 308.3 | 275.9 | 251.9 | 254.1
3871.1 | 3771.1 | 302.4 | 300.1 | 308.1 | 275.9 | 251.2 | 253.8
3872.1 | 3772.1 | 301.8 | 299.8 | 307.8 | 275.9 | 250.7 | 253.6
3873.1 | 3773.1 | 301.2 | 299.7 | 307.6 | 275.8 | 250.3 | 253.3
3874.1 | 3774.1 | 300.5 | 299.4 | 307.3 | 275.8 | 250.2 | 253
3875.1 | 3775.1 | 299.9 | 299.2 | 307.1 | 275.7 | 250 | 252.7
3876.1 | 3776.1 | 299.3 | 298.9 | 306.8 | 275.7 | 249.8 | 252.4
3877.1 | 3777.1 | 298.7 | 298.7 | 306.6 | 275.7 | 249.4 | 252.1
3878.1 | 3778.1 | 298 | 298.5 | 306.3 | 275.6 | 249.1 | 251.8
3879.1 | 3779.1 | 297.5 | 298.3 | 306.1 | 275.6 | 249 | 251.5
3880.1 | 3780.1 | 297 | 298.1 | 305.8 | 275.5 | 248.7 | 251.2
3881.1 | 3781.1 | 296.4 | 297.8 | 305.6 | 275.5 | 248.1 | 250.9
3882.1 | 3782.1 | 295.9 | 297.6 | 305.4 | 275.4 | 247.8 | 250.6
3883.1 | 3783.1 | 295.4 | 297.3 | 305.1 | 275.4 | 247.4 | 250.2
3884.1 | 3784.1 | 294.8 | 297 | 304.9 | 275.3 | 247.1 | 249.8
3885.1 | 3785.1 | 294.3 | 296.7 | 304.6 | 275.3 | 246.9 | 249.5
3886.1 | 3786.1 | 293.6 | 296.5 | 304.4 | 275.3 | 246.7 | 249.3
3887.1 | 3787.1 | 293 | 296.3 | 304.1 | 275.2 | 246.5 | 248.9
3888.1 | 3788.1 | 292.5 | 296.1 | 303.9 | 275.2 | 246 | 248.6
3889.1 | 3789.1 | 292 | 295.8 | 303.7 | 275.1 | 245.5 | 248.3
3890.1 | 3790.1 | 291.4 | 295.5 | 303.4 | 275.1 | 245.1 | 248
3891.1 | 3791.1 | 290.9 | 295.3 | 303.2 | 275 | 244.9 | 247.7
3892.1 | 3792.1 | 290.3 | 295.2 | 302.9 | 275 | 244.7 | 247.3
3893.1 | 3793.1 | 289.7 | 294.9 | 302.7 | 274.9 | 244.4 | 247
3894.1 | 3794.1 | 289.1 | 294.7 | 302.5 | 274.9 | 243.8 | 246.7
3895.1 | 3795.1 | 288.4 | 294.4 | 302.2 | 274.8 | 243.3 | 246.4
3896.1 | 3796.1 | 287.8 | 294.2 | 302 | 274.8 | 242.7 | 246.1
3897.1 | 3797.1 | 287.3 | 294.1 | 301.7 | 274.7 | 242.1 | 245.8
3898.1 | 3798.1 | 286.7 | 293.8 | 301.5 | 274.7 | 241.5 | 245.5
3899.1 | 3799.1 | 286.1 | 293.4 | 301.2 | 274.6 | 241.3 | 245.2
3900.1 | 3800.1 | 285.5 | 293.3 | 301 | 274.5 | 241.4 | 244.9
3901.1 | 3801.1 | 285.1 | 293 | 300.8 | 274.5 | 241 | 244.5
3902.1 | 3802.1 | 284.7 | 292.8 | 300.5 | 274.4 | 240.6 | 244.2
3903.1 | 3803.1 | 284.3 | 292.5 | 300.3 | 274.4 | 240.3 | 243.9
3904.1 | 3804.1 | 283.9 | 292.4 | 300.1 | 274.3 | 239.9 | 243.6
3905.1 | 3805.1 | 283.4 | 292.1 | 299.8 | 274.3 | 239.3 | 243.3
3906.1 | 3806.1 | 282.9 | 291.8 | 299.6 | 274.2 | 238.6 | 243
3907.1 | 3807.1 | 282.3 | 291.6 | 299.4 | 274.2 | 238.5 | 242.7
3908.1 | 3808.1 | 281.6 | 291.3 | 299.1 | 274.1 | 238.4 | 242.4
3909.1 | 3809.1 | 281 | 291 | 298.9 | 274 | 238.1 | 242.1
3910.1 | 3810.1 | 280.4 | 290.8 | 298.7 | 274 | 237.8 | 241.7
3911.1 | 3811.1 | 279.8 | 290.7 | 298.4 | 273.9 | 237.6 | 241.5
3912.1 | 3812.1 | 279.3 | 290.6 | 298.2 | 273.9 | 237.4 | 241.1
3913.1 | 3813.1 | 278.8 | 290.4 | 298 | 273.8 | 237.4 | 240.8
3914.1 | 3814.1 | 278.3 | 290.3 | 297.7 | 273.7 | 237.4 | 240.5
3915.1 | 3815.1 | 277.8 | 290.1 | 297.5 | 273.7 | 237.2 | 240.2
3916.1 | 3816.1 | 277.2 | 290 | 297.3 | 273.6 | 237.2 | 239.9
3917.1 | 3817.1 | 276.7 | 289.8 | 297 | 273.6 | 237.3 | 239.6
3918.1 | 3818.1 | 276.2 | 289.6 | 296.8 | 273.5 | 237.2 | 239.3
3919.1 | 3819.1 | 275.7 | 289.4 | 296.5 | 273.4 | 237 | 239
3920.1 | 3820.1 | 275.1 | 289.2 | 296.3 | 273.4 | 236.9 | 238.7
3921.1 | 3821.1 | 274.6 | 289 | 296 | 273.3 | 236.9 | 238.4
3922.1 | 3822.1 | 274.1 | 288.7 | 295.8 | 273.3 | 236.7 | 238.1
3923.1 | 3823.1 | 273.5 | 288.4 | 295.6 | 273.2 | 236.6 | 237.8
3924.1 | 3824.1 | 273.1 | 288.2 | 295.3 | 273.1 | 236.4 | 237.5
3925.1 | 3825.1 | 272.7 | 288 | 295.1 | 273 | 236.1 | 237.2
3926.1 | 3826.1 | 272.3 | 287.8 | 294.8 | 273 | 235.6 | 236.9
3927.1 | 3827.1 | 271.8 | 287.6 | 294.6 | 272.9 | 235.5 | 236.6
3928.1 | 3828.1 | 271.3 | 287.4 | 294.3 | 272.8 | 235.3 | 236.4
3929.1 | 3829.1 | 270.7 | 287.1 | 294.1 | 272.8 | 235.1 | 236.1
3930.1 | 3830.1 | 270.2 | 286.9 | 293.8 | 272.7 | 234.9 | 235.8
3931.1 | 3831.1 | 269.7 | 286.7 | 293.6 | 272.6 | 234.9 | 235.5
3932.1 | 3832.1 | 269.2 | 286.5 | 293.4 | 272.6 | 234.7 | 235.2
3933.1 | 3833.1 | 268.7 | 286.3 | 293.1 | 272.5 | 234.4 | 234.9
3934.1 | 3834.1 | 268.1 | 286.1 | 292.9 | 272.4 | 234.2 | 234.6
3935.1 | 3835.1 | 267.5 | 285.9 | 292.6 | 272.3 | 233.9 | 234.3
3936.1 | 3836.1 | 267 | 285.7 | 292.4 | 272.3 | 233.8 | 234
3937.1 | 3837.1 | 266.4 | 285.6 | 292.1 | 272.2 | 233.8 | 233.8
3938.1 | 3838.1 | 265.9 | 285.3 | 291.9 | 272.1 | 233.3 | 233.5
3939.1 | 3839.1 | 265.5 | 285.1 | 291.6 | 272 | 232.9 | 233.2
3940.1 | 3840.1 | 265 | 284.9 | 291.4 | 271.9 | 232.7 | 232.9
3941.1 | 3841.1 | 264.5 | 284.7 | 291.1 | 271.9 | 232.2 | 232.6
3942.1 | 3842.1 | 263.9 | 284.5 | 290.9 | 271.8 | 231.9 | 232.3
3943.1 | 3843.1 | 263.3 | 284.2 | 290.6 | 271.7 | 231.8 | 232
3944.1 | 3844.1 | 262.9 | 283.9 | 290.4 | 271.6 | 231.6 | 231.7
3945.1 | 3845.1 | 262.4 | 283.7 | 290.1 | 271.6 | 231.5 | 231.5
3946.1 | 3846.1 | 261.9 | 283.5 | 289.9 | 271.5 | 231.2 | 231.2
3947.1 | 3847.1 | 261.4 | 283.2 | 289.6 | 271.4 | 230.9 | 230.9
3948.1 | 3848.1 | 260.8 | 282.8 | 289.3 | 271.3 | 230.7 | 230.6
3949.1 | 3849.1 | 260.2 | 282.5 | 289.1 | 271.2 | 230.2 | 230.3
3950.1 | 3850.1 | 259.6 | 282.2 | 288.8 | 271.1 | 230 | 230
3951.1 | 3851.1 | 259.2 | 282.1 | 288.6 | 271.1 | 229.7 | 229.7
3952.1 | 3852.1 | 258.7 | 281.8 | 288.3 | 271 | 229.4 | 229.4
3953.1 | 3853.1 | 258.2 | 281.5 | 288 | 270.9 | 229.2 | 229.1
3954.1 | 3854.1 | 257.9 | 281.2 | 287.8 | 270.8 | 229 | 228.8
3955.1 | 3855.1 | 257.5 | 281 | 287.5 | 270.7 | 228.9 | 228.5
3956.1 | 3856.1 | 257 | 280.8 | 287.2 | 270.6 | 228.7 | 228.2
3957.1 | 3857.1 | 256.5 | 280.5 | 287 | 270.5 | 228.6 | 227.9
3958.1 | 3858.1 | 256 | 280.2 | 286.7 | 270.5 | 228.4 | 227.6
3959.1 | 3859.1 | 255.5 | 280 | 286.4 | 270.4 | 228.3 | 227.3
3960.1 | 3860.1 | 255 | 279.7 | 286.2 | 270.3 | 228.2 | 227.1
3961.1 | 3861.1 | 254.6 | 279.4 | 285.9 | 270.2 | 228.1 | 226.8
3962.1 | 3862.1 | 254.2 | 279.1 | 285.6 | 270.1 | 227.9 | 226.5
3963.1 | 3863.1 | 253.7 | 278.9 | 285.4 | 270 | 227.7 | 226.2
3964.1 | 3864.1 | 253.2 | 278.7 | 285.1 | 269.9 | 227.4 | 225.9
3965.1 | 3865.1 | 252.8 | 278.5 | 284.8 | 269.8 | 227.3 | 225.6
3966.1 | 3866.1 | 252.4 | 278.2 | 284.6 | 269.7 | 227.2 | 225.3
3967.1 | 3867.1 | 252 | 278 | 284.3 | 269.7 | 227 | 225
3968.1 | 3868.1 | 251.5 | 277.8 | 284 | 269.6 | 226.9 | 224.7
3969.1 | 3869.1 | 251.2 | 277.7 | 283.8 | 269.5 | 226.7 | 224.4
3970.1 | 3870.1 | 250.8 | 277.5 | 283.5 | 269.4 | 226.5 | 224.1
3971.1 | 3871.1 | 250.4 | 277.3 | 283.2 | 269.3 | 226.3 | 223.8
3972.1 | 3872.1 | 249.9 | 277.2 | 283 | 269.2 | 226 | 223.5
3973.1 | 3873.1 | 249.5 | 277 | 282.7 | 269.1 | 225.8 | 223.2
3974.1 | 3874.1 | 249.1 | 276.8 | 282.4 | 269 | 225.6 | 222.9
3975.1 | 3875.1 | 248.7 | 276.6 | 282.2 | 268.9 | 225.4 | 222.6
3976.1 | 3876.1 | 248.2 | 276.4 | 281.9 | 268.8 | 225.1 | 222.3
3977.1 | 3877.1 | 247.7 | 276.3 | 281.7 | 268.7 | 225 | 222
3978.1 | 3878.1 | 247.2 | 276.1 | 281.4 | 268.6 | 224.8 | 221.7
3979.1 | 3879.1 | 246.7 | 275.9 | 281.1 | 268.5 | 224.5 | 221.4
3980.1 | 3880.1 | 246.3 | 275.7 | 280.9 | 268.4 | 224.2 | 221.1
3981.1 | 3881.1 | 245.8 | 275.6 | 280.6 | 268.3 | 223.9 | 220.8
3982.1 | 3882.1 | 245.5 | 275.3 | 280.4 | 268.2 | 223.5 | 220.5
3983.1 | 3883.1 | 245.1 | 275 | 280.1 | 268.2 | 223.1 | 220.2
3984.1 | 3884.1 | 244.7 | 274.8 | 279.9 | 268 | 222.8 | 220
3985.1 | 3885.1 | 244.2 | 274.6 | 279.6 | 268 | 222.5 | 219.7
3986.1 | 3886.1 | 243.7 | 274.3 | 279.4 | 267.9 | 222.3 | 219.4
3987.1 | 3887.1 | 243.3 | 274.1 | 279.1 | 267.8 | 222.2 | 219.2
3988.1 | 3888.1 | 242.9 | 273.9 | 278.8 | 267.6 | 221.9 | 218.9
3989.1 | 3889.1 | 242.5 | 273.7 | 278.6 | 267.6 | 221.7 | 218.6
3990.1 | 3890.1 | 242 | 273.4 | 278.3 | 267.4 | 221.2 | 218.3
3991.1 | 3891.1 | 241.6 | 273.1 | 278.1 | 267.3 | 220.7 | 218
3992.1 | 3892.1 | 241.2 | 272.9 | 277.8 | 267.2 | 220.2 | 217.8
3993.1 | 3893.1 | 240.9 | 272.8 | 277.6 | 267.1 | 219.7 | 217.5
3994.1 | 3894.1 | 240.6 | 272.5 | 277.3 | 267 | 219.1 | 217.2
3995.1 | 3895.1 | 240.2 | 272.3 | 277.1 | 266.9 | 218.8 | 216.9
3996.1 | 3896.1 | 239.7 | 272.1 | 276.8 | 266.8 | 218.2 | 216.6
3997.1 | 3897.1 | 239.3 | 272 | 276.6 | 266.7 | 217.5 | 216.3
3998.1 | 3898.1 | 238.9 | 271.8 | 276.3 | 266.6 | 217.2 | 216
3999.1 | 3899.1 | 238.5 | 271.7 | 276.1 | 266.5 | 216.7 | 215.7
4000.1 | 3900.1 | 238 | 271.5 | 275.8 | 266.4 | 216.3 | 215.5
4001.1 | 3901.1 | 237.6 | 271.2 | 275.6 | 266.3 | 215.6 | 215.2
4002.1 | 3902.1 | 237.2 | 271.1 | 275.4 | 266.2 | 215.4 | 214.9
4003.1 | 3903.1 | 236.8 | 270.9 | 275.1 | 266.1 | 215 | 214.7
4004.1 | 3904.1 | 236.4 | 270.7 | 274.8 | 266 | 214.4 | 214.4
4005.1 | 3905.1 | 235.9 | 270.5 | 274.6 | 265.9 | 213.7 | 214.1
4006.1 | 3906.1 | 235.5 | 270.3 | 274.3 | 265.8 | 213.2 | 213.8
4007.1 | 3907.1 | 235.2 | 269.9 | 274.1 | 265.7 | 212.6 | 213.6
4008.1 | 3908.1 | 234.8 | 269.7 | 273.8 | 265.6 | 211.9 | 213.3
4009.1 | 3909.1 | 234.5 | 269.4 | 273.6 | 265.4 | 211.3 | 213
4010.1 | 3910.1 | 234.1 | 269.1 | 273.4 | 265.3 | 210.6 | 212.7
4011.1 | 3911.1 | 233.6 | 268.8 | 273.1 | 265.2 | 210 | 212.4
4012.1 | 3912.1 | 233.1 | 268.6 | 272.9 | 265.1 | 209.3 | 212.1
4013.1 | 3913.1 | 232.8 | 268.3 | 272.6 | 265 | 209.1 | 211.9
4014.1 | 3914.1 | 232.4 | 268.1 | 272.4 | 264.9 | 208.8 | 211.6
4015.1 | 3915.1 | 232 | 267.9 | 272.1 | 264.8 | 208.4 | 211.3
4016.1 | 3916.1 | 231.7 | 267.6 | 271.9 | 264.7 | 208 | 211
4017.1 | 3917.1 | 231.3 | 267.3 | 271.7 | 264.6 | 207.4 | 210.7
4018.1 | 3918.1 | 230.9 | 267.1 | 271.4 | 264.5 | 207.1 | 210.4
4019.1 | 3919.1 | 230.6 | 266.8 | 271.2 | 264.4 | 206.8 | 210.1
4020.1 | 3920.1 | 230.2 | 266.6 | 270.9 | 264.3 | 206.1 | 209.9
4021.1 | 3921.1 | 229.8 | 266.4 | 270.7 | 264.1 | 205.4 | 209.6
4022.1 | 3922.1 | 229.3 | 266.1 | 270.5 | 264 | 204.9 | 209.2
4023.1 | 3923.1 | 228.9 | 265.9 | 270.2 | 263.9 | 204.4 | 208.9
4024.1 | 3924.1 | 228.5 | 265.6 | 270 | 263.8 | 203.9 | 208.6
4025.1 | 3925.1 | 228.1 | 265.5 | 269.8 | 263.7 | 203.6 | 208.4
4026.1 | 3926.1 | 227.7 | 265.2 | 269.6 | 263.6 | 203 | 208
4027.1 | 3927.1 | 227.3 | 264.9 | 269.3 | 263.5 | 202.5 | 207.7
4028.1 | 3928.1 | 226.9 | 264.8 | 269.1 | 263.3 | 202.1 | 207.4
4029.1 | 3929.1 | 226.4 | 264.6 | 268.9 | 263.2 | 201.9 | 207.1
4030.1 | 3930.1 | 226 | 264.4 | 268.6 | 263.1 | 201.4 | 206.8
4031.1 | 3931.1 | 225.7 | 264.2 | 268.4 | 263 | 201 | 206.5
4032.1 | 3932.1 | 225.4 | 264.1 | 268.2 | 262.9 | 200.7 | 206.3
4033.1 | 3933.1 | 225 | 263.9 | 268 | 262.8 | 200.3 | 206
4034.1 | 3934.1 | 224.7 | 263.7 | 267.7 | 262.7 | 199.9 | 205.7
4035.1 | 3935.1 | 224.3 | 263.5 | 267.5 | 262.5 | 199.7 | 205.4
4036.1 | 3936.1 | 223.9 | 263.3 | 267.3 | 262.4 | 199.2 | 205.1
4037.1 | 3937.1 | 223.6 | 263.1 | 267.1 | 262.3 | 199.2 | 204.8
4038.1 | 3938.1 | 223.3 | 262.8 | 266.9 | 262.2 | 199 | 204.5
4039.1 | 3939.1 | 223 | 262.7 | 266.6 | 262.1 | 198.7 | 204.2
4040.1 | 3940.1 | 222.6 | 262.4 | 266.4 | 261.9 | 198.1 | 203.9
4041.1 | 3941.1 | 222.2 | 262.3 | 266.2 | 261.8 | 197.7 | 203.6
4042.1 | 3942.1 | 221.8 | 262.1 | 266 | 261.7 | 197.2 | 203.3
4043.1 | 3943.1 | 221.3 | 261.8 | 265.8 | 261.6 | 196.6 | 203
4044.1 | 3944.1 | 220.9 | 261.7 | 265.6 | 261.5 | 196.6 | 202.7
4045.1 | 3945.1 | 220.5 | 261.5 | 265.3 | 261.3 | 196.2 | 202.5
4046.1 | 3946.1 | 220.1 | 261.4 | 265.1 | 261.2 | 196.2 | 202.2
4047.1 | 3947.1 | 219.7 | 261.1 | 264.9 | 261.1 | 196.1 | 201.9
4048.1 | 3948.1 | 219.3 | 260.9 | 264.7 | 261 | 195.9 | 201.7
4049.1 | 3949.1 | 219 | 260.8 | 264.4 | 260.9 | 195.8 | 201.4
4050.1 | 3950.1 | 218.7 | 260.6 | 264.2 | 260.7 | 195.5 | 201.1
4051.1 | 3951.1 | 218.3 | 260.2 | 264 | 260.6 | 195.2 | 200.9
4052.1 | 3952.1 | 217.9 | 260 | 263.8 | 260.5 | 194.8 | 200.6
4053.1 | 3953.1 | 217.5 | 259.8 | 263.6 | 260.4 | 194.4 | 200.3
4054.1 | 3954.1 | 217.1 | 259.6 | 263.3 | 260.2 | 194.2 | 200
4055.1 | 3955.1 | 216.7 | 259.4 | 263.1 | 260.1 | 193.9 | 199.8
4056.1 | 3956.1 | 216.3 | 259 | 262.9 | 260 | 193.8 | 199.5
4057.1 | 3957.1 | 216 | 258.9 | 262.7 | 259.9 | 193.7 | 199.3
4058.1 | 3958.1 | 215.7 | 258.7 | 262.5 | 259.7 | 193.5 | 199
4059.1 | 3959.1 | 215.4 | 258.4 | 262.3 | 259.6 | 193.5 | 198.7
4060.1 | 3960.1 | 215 | 258.1 | 262 | 259.5 | 193.4 | 198.5
4061.1 | 3961.1 | 214.6 | 258 | 261.8 | 259.4 | 193.5 | 198.2
4062.1 | 3962.1 | 214.2 | 257.8 | 261.6 | 259.2 | 193.5 | 197.9
4063.1 | 3963.1 | 213.9 | 257.7 | 261.4 | 259.1 | 193.5 | 197.7
4064.1 | 3964.1 | 213.5 | 257.6 | 261.1 | 259 | 193.4 | 197.4
4065.1 | 3965.1 | 213.2 | 257.4 | 260.9 | 258.9 | 193.1 | 197.1
4066.1 | 3966.1 | 212.9 | 257.1 | 260.7 | 258.7 | 192.8 | 196.9
4067.1 | 3967.1 | 212.6 | 256.9 | 260.5 | 258.6 | 192.6 | 196.7
4068.1 | 3968.1 | 212.2 | 256.8 | 260.2 | 258.5 | 192.4 | 196.4
4069.1 | 3969.1 | 211.7 | 256.6 | 260 | 258.4 | 192.4 | 196.1
4070.1 | 3970.1 | 211.4 | 256.3 | 259.8 | 258.2 | 192.3 | 195.9
4071.1 | 3971.1 | 211.1 | 256.1 | 259.5 | 258.1 | 192.1 | 195.7
4072.1 | 3972.1 | 210.7 | 255.9 | 259.3 | 258 | 191.9 | 195.4
4073.1 | 3973.1 | 210.3 | 255.7 | 259.1 | 257.9 | 191.4 | 195.2
4074.1 | 3974.1 | 210 | 255.5 | 258.8 | 257.7 | 190.9 | 195
4075.1 | 3975.1 | 209.7 | 255.3 | 258.6 | 257.6 | 190.4 | 194.7
4076.1 | 3976.1 | 209.4 | 255.1 | 258.4 | 257.5 | 190.1 | 194.5
4077.1 | 3977.1 | 209 | 254.9 | 258.1 | 257.3 | 189.7 | 194.3
4078.1 | 3978.1 | 208.7 | 254.7 | 257.9 | 257.2 | 189.6 | 194
4079.1 | 3979.1 | 208.4 | 254.5 | 257.7 | 257.1 | 189.4 | 193.8
4080.1 | 3980.1 | 208.1 | 254.4 | 257.4 | 256.9 | 189 | 193.5
4081.1 | 3981.1 | 207.7 | 254.2 | 257.2 | 256.8 | 188.8 | 193.3
4082.1 | 3982.1 | 207.4 | 254.1 | 257 | 256.7 | 188.6 | 193
4083.1 | 3983.1 | 207.1 | 253.9 | 256.7 | 256.5 | 188.3 | 192.8
4084.1 | 3984.1 | 206.7 | 253.6 | 256.5 | 256.4 | 188.3 | 192.6
4085.1 | 3985.1 | 206.4 | 253.5 | 256.3 | 256.3 | 188.3 | 192.3
4086.1 | 3986.1 | 206.1 | 253.3 | 256 | 256.1 | 188.3 | 192.1
4087.1 | 3987.1 | 205.7 | 253 | 255.8 | 256 | 188.3 | 191.9
4088.1 | 3988.1 | 205.3 | 252.8 | 255.6 | 255.9 | 188.1 | 191.6
4089.1 | 3989.1 | 205.1 | 252.6 | 255.4 | 255.7 | 187.8 | 191.4
4090.1 | 3990.1 | 204.7 | 252.5 | 255.1 | 255.6 | 187.3 | 191.1
4091.1 | 3991.1 | 204.4 | 252.3 | 254.9 | 255.5 | 187.2 | 190.9
4092.1 | 3992.1 | 204.1 | 252.1 | 254.7 | 255.3 | 187.2 | 190.6
4093.1 | 3993.1 | 203.9 | 251.9 | 254.5 | 255.2 | 186.8 | 190.4
4094.1 | 3994.1 | 203.6 | 251.7 | 254.3 | 255.1 | 186.6 | 190.2
4095.1 | 3995.1 | 203.2 | 251.6 | 254.1 | 254.9 | 186.2 | 190
4096.1 | 3996.1 | 202.8 | 251.4 | 253.8 | 254.8 | 185.9 | 189.8
4097.1 | 3997.1 | 202.5 | 251.1 | 253.6 | 254.7 | 185.8 | 189.5
4098.1 | 3998.1 | 202.1 | 251 | 253.4 | 254.5 | 185.4 | 189.3
4099.1 | 3999.1 | 201.8 | 250.8 | 253.2 | 254.4 | 184.8 | 189.1
4100.1 | 4000.1 | 201.7 | 250.6 | 253 | 254.3 | 184.4 | 188.8
4101.1 | 4001.1 | 201.5 | 250.4 | 252.8 | 254.1 | 184.2 | 188.6
4102.1 | 4002.1 | 201.3 | 250.3 | 252.5 | 254 | 183.9 | 188.4
4103.1 | 4003.1 | 200.9 | 250.1 | 252.3 | 253.9 | 183.7 | 188.1
4104.1 | 4004.1 | 200.6 | 250 | 252.1 | 253.7 | 183.3 | 187.9
4105.1 | 4005.1 | 200.3 | 249.9 | 251.9 | 253.6 | 183 | 187.6
4106.1 | 4006.1 | 199.9 | 249.7 | 251.7 | 253.5 | 182.6 | 187.4
4107.1 | 4007.1 | 199.6 | 249.4 | 251.5 | 253.3 | 182 | 187.1
4108.1 | 4008.1 | 199.2 | 249.2 | 251.2 | 253.2 | 181.6 | 186.8
4109.1 | 4009.1 | 198.7 | 249 | 251 | 253 | 181.2 | 186.6
4110.1 | 4010.1 | 198.4 | 248.8 | 250.8 | 252.9 | 180.9 | 186.4
4111.1 | 4011.1 | 198.1 | 248.6 | 250.6 | 252.8 | 180.5 | 186.1
4112.1 | 4012.1 | 197.8 | 248.4 | 250.4 | 252.6 | 180.1 | 185.9
4113.1 | 4013.1 | 197.5 | 248.2 | 250.1 | 252.5 | 179.8 | 185.6
4114.1 | 4014.1 | 197.3 | 248 | 249.9 | 252.3 | 179.6 | 185.4
4115.1 | 4015.1 | 197.1 | 247.8 | 249.7 | 252.2 | 179.3 | 185.2
4116.1 | 4016.1 | 196.9 | 247.6 | 249.5 | 252.1 | 178.9 | 185
4117.1 | 4017.1 | 196.5 | 247.3 | 249.3 | 251.9 | 178.7 | 184.7
4118.1 | 4018.1 | 196.2 | 246.9 | 249 | 251.8 | 178.5 | 184.5
4119.1 | 4019.1 | 195.8 | 246.6 | 248.8 | 251.6 | 178.3 | 184.3
4120.1 | 4020.1 | 195.5 | 246.4 | 248.6 | 251.5 | 178.1 | 184
4121.1 | 4021.1 | 195.2 | 246.2 | 248.4 | 251.4 | 177.8 | 183.8
4122.1 | 4022.1 | 195 | 245.9 | 248.1 | 251.2 | 177.5 | 183.6
4123.1 | 4023.1 | 194.7 | 245.8 | 247.9 | 251.1 | 177.2 | 183.4
4124.1 | 4024.1 | 194.4 | 245.6 | 247.7 | 250.9 | 177.2 | 183.2
4125.1 | 4025.1 | 194 | 245.4 | 247.5 | 250.8 | 177.1 | 183
4126.1 | 4026.1 | 193.7 | 245.1 | 247.2 | 250.6 | 176.9 | 182.8
4127.1 | 4027.1 | 193.3 | 244.8 | 247 | 250.5 | 176.6 | 182.5
4128.1 | 4028.1 | 193 | 244.7 | 246.8 | 250.4 | 176.3 | 182.3
4129.1 | 4029.1 | 192.6 | 244.5 | 246.5 | 250.2 | 175.9 | 182.1
4130.1 | 4030.1 | 192.3 | 244.3 | 246.3 | 250.1 | 175.5 | 181.8
4131.1 | 4031.1 | 191.9 | 244.1 | 246.1 | 249.9 | 175.2 | 181.6
4132.1 | 4032.1 | 191.6 | 243.9 | 245.9 | 249.8 | 175.1 | 181.3
4133.1 | 4033.1 | 191.3 | 243.8 | 245.6 | 249.6 | 174.8 | 181.1
4134.1 | 4034.1 | 191 | 243.6 | 245.4 | 249.5 | 174.6 | 180.9
4135.1 | 4035.1 | 190.7 | 243.4 | 245.2 | 249.4 | 174.2 | 180.7
4136.1 | 4036.1 | 190.4 | 243.2 | 245 | 249.2 | 173.8 | 180.5
4137.1 | 4037.1 | 190.1 | 243 | 244.7 | 249.1 | 173.5 | 180.3
4138.1 | 4038.1 | 189.7 | 242.8 | 244.5 | 248.9 | 173.3 | 180.1
4139.1 | 4039.1 | 189.4 | 242.6 | 244.3 | 248.8 | 173.1 | 179.9
4140.1 | 4040.1 | 189.1 | 242.4 | 244.1 | 248.6 | 172.8 | 179.7
4141.1 | 4041.1 | 188.9 | 242.2 | 243.9 | 248.5 | 172.5 | 179.4
4142.1 | 4042.1 | 188.7 | 242 | 243.6 | 248.3 | 172.4 | 179.2
4143.1 | 4043.1 | 188.4 | 241.7 | 243.4 | 248.2 | 172 | 178.9
4144.1 | 4044.1 | 188.1 | 241.4 | 243.2 | 248.1 | 171.6 | 178.7
4145.1 | 4045.1 | 187.8 | 241.3 | 243 | 247.9 | 171.4 | 178.5
4146.1 | 4046.1 | 187.5 | 241.2 | 242.8 | 247.8 | 171.1 | 178.3
4147.1 | 4047.1 | 187.2 | 241 | 242.6 | 247.6 | 171 | 178
4148.1 | 4048.1 | 186.9 | 240.8 | 242.4 | 247.5 | 170.9 | 177.8
4149.1 | 4049.1 | 186.7 | 240.6 | 242.1 | 247.3 | 170.8 | 177.6
4150.1 | 4050.1 | 186.4 | 240.4 | 241.9 | 247.2 | 170.6 | 177.4
4151.1 | 4051.1 | 186.2 | 240.3 | 241.7 | 247 | 170.2 | 177.1
4152.1 | 4052.1 | 185.9 | 240.1 | 241.5 | 246.9 | 170.1 | 177
4153.1 | 4053.1 | 185.7 | 240 | 241.3 | 246.8 | 169.8 | 176.8
4154.1 | 4054.1 | 185.4 | 239.8 | 241.1 | 246.6 | 169.3 | 176.6
4155.1 | 4055.1 | 185.1 | 239.7 | 240.9 | 246.5 | 169.2 | 176.3
4156.1 | 4056.1 | 184.8 | 239.5 | 240.7 | 246.3 | 169 | 176.1
4157.1 | 4057.1 | 184.6 | 239.4 | 240.5 | 246.2 | 168.8 | 175.9
4158.1 | 4058.1 | 184.3 | 239.2 | 240.3 | 246 | 168.8 | 175.7
4159.1 | 4059.1 | 184 | 239.1 | 240.1 | 245.9 | 168.6 | 175.5
4160.1 | 4060.1 | 183.7 | 239 | 239.9 | 245.7 | 168.4 | 175.3
4161.1 | 4061.1 | 183.4 | 238.9 | 239.6 | 245.6 | 168.2 | 175
4162.1 | 4062.1 | 183.1 | 238.7 | 239.4 | 245.4 | 168 | 174.8
4163.1 | 4063.1 | 182.8 | 238.6 | 239.2 | 245.3 | 167.8 | 174.6
4164.1 | 4064.1 | 182.5 | 238.4 | 239 | 245.1 | 167.7 | 174.4
4165.1 | 4065.1 | 182.2 | 238.2 | 238.8 | 245 | 167.3 | 174.2
4166.1 | 4066.1 | 181.9 | 238 | 238.6 | 244.8 | 166.9 | 174
4167.1 | 4067.1 | 181.7 | 237.9 | 238.4 | 244.7 | 166.6 | 173.8
4168.1 | 4068.1 | 181.4 | 237.7 | 238.2 | 244.5 | 166.4 | 173.6
4169.1 | 4069.1 | 181.2 | 237.5 | 238 | 244.4 | 166 | 173.4
4170.1 | 4070.1 | 181 | 237.3 | 237.8 | 244.2 | 165.6 | 173.2
4171.1 | 4071.1 | 180.7 | 237.1 | 237.6 | 244.1 | 165.3 | 172.9
4172.1 | 4072.1 | 180.4 | 237 | 237.4 | 244 | 165.3 | 172.7
4173.1 | 4073.1 | 180.1 | 236.7 | 237.2 | 243.8 | 165.1 | 172.5
4174.1 | 4074.1 | 179.9 | 236.6 | 237 | 243.7 | 164.8 | 172.3
4175.1 | 4075.1 | 179.6 | 236.4 | 236.8 | 243.5 | 164.4 | 172.1
4176.1 | 4076.1 | 179.4 | 236.2 | 236.6 | 243.4 | 164.1 | 171.9
4177.1 | 4077.1 | 179.3 | 236 | 236.4 | 243.2 | 163.8 | 171.7
4178.1 | 4078.1 | 179 | 235.9 | 236.2 | 243.1 | 163.6 | 171.5
4179.1 | 4079.1 | 178.7 | 235.7 | 236 | 242.9 | 163.5 | 171.3
4180.1 | 4080.1 | 178.4 | 235.5 | 235.8 | 242.8 | 163.5 | 171
4181.1 | 4081.1 | 178.1 | 235.3 | 235.6 | 242.6 | 163.5 | 170.8
4182.1 | 4082.1 | 177.9 | 235.1 | 235.4 | 242.5 | 163.3 | 170.6
4183.1 | 4083.1 | 177.7 | 234.9 | 235.1 | 242.3 | 163.1 | 170.5
4184.1 | 4084.1 | 177.4 | 234.7 | 235 | 242.2 | 162.9 | 170.3
4185.1 | 4085.1 | 177.2 | 234.6 | 234.8 | 242 | 162.8 | 170.1
4186.1 | 4086.1 | 176.9 | 234.4 | 234.5 | 241.9 | 162.8 | 169.9
4187.1 | 4087.1 | 176.5 | 234.2 | 234.3 | 241.7 | 162.5 | 169.7
4188.1 | 4088.1 | 176.2 | 234 | 234.1 | 241.6 | 162.4 | 169.5
4189.1 | 4089.1 | 176 | 233.8 | 233.9 | 241.4 | 161.9 | 169.2
4190.1 | 4090.1 | 175.9 | 233.7 | 233.7 | 241.3 | 161.9 | 169.1
4191.1 | 4091.1 | 175.7 | 233.4 | 233.5 | 241.1 | 161.8 | 168.9
4192.1 | 4092.1 | 175.4 | 233.3 | 233.3 | 241 | 161.6 | 168.7
4193.1 | 4093.1 | 175.2 | 233.1 | 233.1 | 240.8 | 161.5 | 168.5
4194.1 | 4094.1 | 174.9 | 233.1 | 232.9 | 240.7 | 161.3 | 168.3
4195.1 | 4095.1 | 174.6 | 232.9 | 232.7 | 240.5 | 161.2 | 168.1
4196.1 | 4096.1 | 174.3 | 232.7 | 232.5 | 240.4 | 161 | 167.9
4197.1 | 4097.1 | 174 | 232.6 | 232.3 | 240.2 | 161 | 167.7
4198.1 | 4098.1 | 173.6 | 232.5 | 232.1 | 240.1 | 160.9 | 167.5
4199.1 | 4099.1 | 173.3 | 232.4 | 231.9 | 239.9 | 160.7 | 167.3
4200.1 | 4100.1 | 173 | 232.2 | 231.7 | 239.8 | 160.5 | 167.1
4201.1 | 4101.1 | 172.8 | 232 | 231.5 | 239.6 | 160.3 | 166.9
4202.1 | 4102.1 | 172.5 | 231.8 | 231.3 | 239.5 | 160.2 | 166.7
4203.1 | 4103.1 | 172.3 | 231.6 | 231.2 | 239.3 | 159.9 | 166.6
4204.1 | 4104.1 | 172 | 231.5 | 230.9 | 239.2 | 159.5 | 166.4
4205.1 | 4105.1 | 171.8 | 231.3 | 230.7 | 239 | 159.4 | 166.2
4206.1 | 4106.1 | 171.6 | 231.2 | 230.5 | 238.9 | 159.2 | 166
4207.1 | 4107.1 | 171.3 | 231.1 | 230.3 | 238.7 | 159 | 165.8
4208.1 | 4108.1 | 171.2 | 230.9 | 230.1 | 238.5 | 158.7 | 165.6
4209.1 | 4109.1 | 171 | 230.7 | 230 | 238.4 | 158.5 | 165.4
4210.1 | 4110.1 | 170.7 | 230.4 | 229.8 | 238.2 | 158.3 | 165.3
4211.1 | 4111.1 | 170.4 | 230.3 | 229.6 | 238.1 | 158.1 | 165.1
4212.1 | 4112.1 | 170.1 | 230.1 | 229.4 | 237.9 | 158.1 | 164.9
4213.1 | 4113.1 | 169.9 | 229.9 | 229.2 | 237.8 | 158 | 164.7
4214.1 | 4114.1 | 169.6 | 229.7 | 229 | 237.6 | 157.9 | 164.5
4215.1 | 4115.1 | 169.4 | 229.6 | 228.8 | 237.5 | 157.7 | 164.3
4216.1 | 4116.1 | 169.2 | 229.4 | 228.6 | 237.3 | 157.5 | 164.1
4217.1 | 4117.1 | 168.9 | 229.2 | 228.4 | 237.2 | 157.5 | 163.9
4218.1 | 4118.1 | 168.8 | 228.9 | 228.2 | 237 | 157.2 | 163.8
4219.1 | 4119.1 | 168.7 | 228.8 | 228 | 236.9 | 157.1 | 163.6
4220.1 | 4120.1 | 168.5 | 228.6 | 227.8 | 236.7 | 156.9 | 163.4
4221.1 | 4121.1 | 168.2 | 228.4 | 227.6 | 236.6 | 156.7 | 163.2
4222.1 | 4122.1 | 167.9 | 228.3 | 227.5 | 236.4 | 156.5 | 163
4223.1 | 4123.1 | 167.7 | 228.1 | 227.3 | 236.2 | 156.3 | 162.9
4224.1 | 4124.1 | 167.4 | 227.9 | 227.1 | 236.1 | 156.1 | 162.7
4225.1 | 4125.1 | 167.2 | 227.7 | 226.9 | 235.9 | 155.9 | 162.5
4226.1 | 4126.1 | 167.1 | 227.5 | 226.7 | 235.8 | 155.6 | 162.3
4227.1 | 4127.1 | 166.8 | 227.3 | 226.5 | 235.6 | 155.4 | 162.2
4228.1 | 4128.1 | 166.5 | 227.1 | 226.3 | 235.5 | 155.3 | 162
4229.1 | 4129.1 | 166.3 | 226.9 | 226.1 | 235.3 | 155.1 | 161.8
4230.1 | 4130.1 | 166 | 226.7 | 226 | 235.2 | 154.8 | 161.6
4231.1 | 4131.1 | 165.7 | 226.6 | 225.8 | 235 | 154.6 | 161.4
4232.1 | 4132.1 | 165.5 | 226.4 | 225.6 | 234.8 | 154.3 | 161.2
4233.1 | 4133.1 | 165.3 | 226.2 | 225.4 | 234.7 | 153.9 | 161.1
4234.1 | 4134.1 | 165.2 | 226 | 225.2 | 234.5 | 153.5 | 160.9
4235.1 | 4135.1 | 165 | 226 | 225.1 | 234.4 | 153.3 | 160.7
4236.1 | 4136.1 | 164.7 | 225.8 | 224.9 | 234.2 | 153.1 | 160.5
4237.1 | 4137.1 | 164.4 | 225.7 | 224.7 | 234.1 | 152.6 | 160.3
4238.1 | 4138.1 | 164.1 | 225.5 | 224.5 | 233.9 | 152.3 | 160.2
4239.1 | 4139.1 | 163.9 | 225.3 | 224.3 | 233.7 | 152.2 | 159.9
4240.1 | 4140.1 | 163.7 | 225.2 | 224.1 | 233.6 | 152.1 | 159.8
4241.1 | 4141.1 | 163.5 | 225 | 223.9 | 233.4 | 152 | 159.6
4242.1 | 4142.1 | 163.2 | 224.9 | 223.8 | 233.3 | 151.9 | 159.4
4243.1 | 4143.1 | 163 | 224.7 | 223.6 | 233.1 | 151.8 | 159.3
4244.1 | 4144.1 | 162.8 | 224.6 | 223.4 | 233 | 151.6 | 159.1
4245.1 | 4145.1 | 162.7 | 224.5 | 223.2 | 232.8 | 151.4 | 158.9
4246.1 | 4146.1 | 162.4 | 224.3 | 223 | 232.6 | 151.4 | 158.7
4247.1 | 4147.1 | 162.2 | 224 | 222.8 | 232.5 | 151.3 | 158.6
4248.1 | 4148.1 | 161.9 | 223.9 | 222.6 | 232.3 | 151.2 | 158.4
4249.1 | 4149.1 | 161.7 | 223.7 | 222.4 | 232.2 | 151.1 | 158.2
4250.1 | 4150.1 | 161.4 | 223.5 | 222.2 | 232 | 150.9 | 158
4251.1 | 4151.1 | 161.2 | 223.3 | 222 | 231.9 | 150.8 | 157.9
4252.1 | 4152.1 | 161 | 223.2 | 221.8 | 231.7 | 150.8 | 157.7
4253.1 | 4153.1 | 160.8 | 223 | 221.6 | 231.5 | 150.6 | 157.5
4254.1 | 4154.1 | 160.5 | 222.9 | 221.4 | 231.4 | 150.4 | 157.3
4255.1 | 4155.1 | 160.3 | 222.7 | 221.3 | 231.2 | 150.3 | 157.2
4256.1 | 4156.1 | 160 | 222.5 | 221.1 | 231.1 | 150.2 | 157
4257.1 | 4157.1 | 159.7 | 222.3 | 220.9 | 230.9 | 150 | 156.8
4258.1 | 4158.1 | 159.5 | 222.1 | 220.7 | 230.8 | 150 | 156.7
4259.1 | 4159.1 | 159.3 | 221.9 | 220.5 | 230.6 | 149.9 | 156.5
4260.1 | 4160.1 | 159.2 | 221.8 | 220.3 | 230.5 | 149.7 | 156.3
4261.1 | 4161.1 | 159 | 221.6 | 220.1 | 230.3 | 149.4 | 156.2
4262.1 | 4162.1 | 158.7 | 221.4 | 219.9 | 230.1 | 149.3 | 156
4263.1 | 4163.1 | 158.5 | 221.2 | 219.7 | 230 | 149.2 | 155.8
4264.1 | 4164.1 | 158.2 | 221.1 | 219.5 | 229.8 | 149.1 | 155.6
4265.1 | 4165.1 | 157.9 | 220.9 | 219.3 | 229.7 | 148.9 | 155.5
4266.1 | 4166.1 | 157.7 | 220.7 | 219.2 | 229.5 | 148.9 | 155.3
4267.1 | 4167.1 | 157.5 | 220.5 | 219 | 229.4 | 148.9 | 155.1
4268.1 | 4168.1 | 157.3 | 220.4 | 218.8 | 229.2 | 148.8 | 155
4269.1 | 4169.1 | 157.1 | 220.2 | 218.6 | 229 | 148.7 | 154.8
4270.1 | 4170.1 | 156.9 | 220.1 | 218.4 | 228.9 | 148.5 | 154.7
4271.1 | 4171.1 | 156.7 | 219.9 | 218.2 | 228.7 | 148.4 | 154.5
4272.1 | 4172.1 | 156.5 | 219.8 | 218 | 228.6 | 148.4 | 154.3
4273.1 | 4173.1 | 156.3 | 219.6 | 217.9 | 228.4 | 148.1 | 154.2
4274.1 | 4174.1 | 156.1 | 219.5 | 217.7 | 228.2 | 148.1 | 154
4275.1 | 4175.1 | 155.9 | 219.3 | 217.5 | 228.1 | 148 | 153.8
4276.1 | 4176.1 | 155.6 | 219.2 | 217.3 | 227.9 | 147.9 | 153.6
4277.1 | 4177.1 | 155.4 | 219.1 | 217.1 | 227.8 | 147.7 | 153.4
4278.1 | 4178.1 | 155.3 | 219 | 216.9 | 227.6 | 147.4 | 153.3
4279.1 | 4179.1 | 155.1 | 218.8 | 216.7 | 227.5 | 147.2 | 153.1
4280.1 | 4180.1 | 154.8 | 218.7 | 216.5 | 227.3 | 147 | 152.9
4281.1 | 4181.1 | 154.5 | 218.6 | 216.3 | 227.1 | 146.8 | 152.8
4282.1 | 4182.1 | 154.3 | 218.4 | 216.1 | 227 | 146.6 | 152.6
4283.1 | 4183.1 | 154.1 | 218.3 | 215.9 | 226.8 | 146.5 | 152.5
4284.1 | 4184.1 | 153.9 | 218.1 | 215.8 | 226.7 | 146.2 | 152.3
4285.1 | 4185.1 | 153.7 | 218 | 215.6 | 226.5 | 146 | 152.1
4286.1 | 4186.1 | 153.5 | 217.7 | 215.4 | 226.4 | 145.9 | 151.9
4287.1 | 4187.1 | 153.2 | 217.6 | 215.2 | 226.2 | 145.7 | 151.8
4288.1 | 4188.1 | 153 | 217.4 | 215 | 226.1 | 145.5 | 151.6
4289.1 | 4189.1 | 152.8 | 217.2 | 214.8 | 225.9 | 145.2 | 151.5
4290.1 | 4190.1 | 152.6 | 217 | 214.7 | 225.8 | 145 | 151.3
4291.1 | 4191.1 | 152.4 | 216.9 | 214.5 | 225.6 | 144.8 | 151.1
4292.1 | 4192.1 | 152.2 | 216.7 | 214.3 | 225.4 | 144.7 | 151
4293.1 | 4193.1 | 152 | 216.5 | 214.1 | 225.3 | 144.6 | 150.8
4294.1 | 4194.1 | 151.8 | 216.3 | 213.9 | 225.1 | 144.5 | 150.6
4295.1 | 4195.1 | 151.6 | 216.1 | 213.8 | 225 | 144.3 | 150.5
4296.1 | 4196.1 | 151.4 | 215.9 | 213.6 | 224.8 | 144.1 | 150.3
4297.1 | 4197.1 | 151.1 | 215.8 | 213.4 | 224.7 | 144 | 150.1
4298.1 | 4198.1 | 151 | 215.6 | 213.2 | 224.5 | 143.8 | 150
4299.1 | 4199.1 | 150.8 | 215.4 | 213.1 | 224.3 | 143.7 | 149.8
4300.1 | 4200.1 | 150.6 | 215.3 | 212.9 | 224.2 | 143.5 | 149.6
4301.1 | 4201.1 | 150.4 | 215.2 | 212.7 | 224 | 143.4 | 149.5
4302.1 | 4202.1 | 150.2 | 215 | 212.5 | 223.9 | 143.3 | 149.3
4303.1 | 4203.1 | 150 | 214.9 | 212.3 | 223.7 | 143.2 | 149.1
4304.1 | 4204.1 | 149.8 | 214.8 | 212.2 | 223.6 | 142.8 | 149
4305.1 | 4205.1 | 149.6 | 214.7 | 212 | 223.4 | 142.7 | 148.8
4306.1 | 4206.1 | 149.5 | 214.5 | 211.8 | 223.3 | 142.5 | 148.6
4307.1 | 4207.1 | 149.2 | 214.4 | 211.6 | 223.1 | 142.3 | 148.4
4308.1 | 4208.1 | 149 | 214.3 | 211.4 | 222.9 | 142.1 | 148.3
4309.1 | 4209.1 | 148.8 | 214.2 | 211.3 | 222.8 | 142 | 148.1
4310.1 | 4210.1 | 148.7 | 214.1 | 211.1 | 222.6 | 141.6 | 148
4311.1 | 4211.1 | 148.5 | 213.9 | 210.9 | 222.5 | 141.5 | 147.8
4312.1 | 4212.1 | 148.3 | 213.8 | 210.7 | 222.3 | 141.2 | 147.6
4313.1 | 4213.1 | 148 | 213.6 | 210.5 | 222.2 | 141.1 | 147.5
4314.1 | 4214.1 | 147.8 | 213.5 | 210.3 | 222 | 141 | 147.3
4315.1 | 4215.1 | 147.7 | 213.3 | 210.1 | 221.9 | 140.9 | 147.2
4316.1 | 4216.1 | 147.5 | 213.2 | 209.9 | 221.7 | 140.7 | 147
4317.1 | 4217.1 | 147.3 | 213 | 209.8 | 221.6 | 140.6 | 146.8
4318.1 | 4218.1 | 147.1 | 212.9 | 209.6 | 221.4 | 140.4 | 146.7
4319.1 | 4219.1 | 146.9 | 212.7 | 209.4 | 221.2 | 140.2 | 146.5
4320.1 | 4220.1 | 146.7 | 212.5 | 209.2 | 221.1 | 140 | 146.4
4321.1 | 4221.1 | 146.5 | 212.4 | 209 | 220.9 | 139.8 | 146.2
4322.1 | 4222.1 | 146.3 | 212.3 | 208.8 | 220.8 | 139.6 | 146
4323.1 | 4223.1 | 146.1 | 212.1 | 208.6 | 220.6 | 139.4 | 145.9
4324.1 | 4224.1 | 145.9 | 212 | 208.4 | 220.5 | 139.2 | 145.7
4325.1 | 4225.1 | 145.7 | 211.9 | 208.2 | 220.3 | 139.1 | 145.6
4326.1 | 4226.1 | 145.5 | 211.7 | 208 | 220.2 | 139.1 | 145.4
4327.1 | 4227.1 | 145.3 | 211.5 | 207.9 | 220 | 138.9 | 145.3
4328.1 | 4228.1 | 145.1 | 211.3 | 207.6 | 219.9 | 138.7 | 145.1
4329.1 | 4229.1 | 144.9 | 211.2 | 207.5 | 219.7 | 138.4 | 145
4330.1 | 4230.1 | 144.7 | 211.1 | 207.3 | 219.5 | 138.3 | 144.8
4331.1 | 4231.1 | 144.4 | 211 | 207.1 | 219.4 | 138.2 | 144.7
4332.1 | 4232.1 | 144.2 | 210.9 | 206.9 | 219.2 | 138 | 144.5
4333.1 | 4233.1 | 144.1 | 210.7 | 206.7 | 219.1 | 137.9 | 144.4
4334.1 | 4234.1 | 144 | 210.6 | 206.5 | 218.9 | 137.7 | 144.2
4335.1 | 4235.1 | 143.8 | 210.5 | 206.3 | 218.8 | 137.4 | 144.1
4336.1 | 4236.1 | 143.7 | 210.4 | 206.1 | 218.6 | 137.4 | 143.9
4337.1 | 4237.1 | 143.6 | 210.2 | 206 | 218.5 | 137.2 | 143.8
4338.1 | 4238.1 | 143.4 | 210.1 | 205.8 | 218.3 | 137.1 | 143.6
4339.1 | 4239.1 | 143.2 | 209.9 | 205.6 | 218.2 | 136.9 | 143.5
4340.1 | 4240.1 | 142.9 | 209.7 | 205.4 | 218 | 136.7 | 143.3
4341.1 | 4241.1 | 142.7 | 209.6 | 205.2 | 217.9 | 136.4 | 143.2
4342.1 | 4242.1 | 142.6 | 209.4 | 205 | 217.7 | 136.1 | 143
4343.1 | 4243.1 | 142.4 | 209.3 | 204.8 | 217.6 | 135.9 | 142.9
4344.1 | 4244.1 | 142.2 | 209.2 | 204.7 | 217.4 | 135.7 | 142.8
4345.1 | 4245.1 | 142 | 209.1 | 204.5 | 217.3 | 135.5 | 142.6
4346.1 | 4246.1 | 141.8 | 208.9 | 204.3 | 217.1 | 135.1 | 142.4
4347.1 | 4247.1 | 141.6 | 208.7 | 204.1 | 217 | 134.9 | 142.3
4348.1 | 4248.1 | 141.4 | 208.6 | 203.9 | 216.8 | 134.7 | 142.2
4349.1 | 4249.1 | 141.2 | 208.4 | 203.7 | 216.7 | 134.6 | 142
4350.1 | 4250.1 | 141.1 | 208.2 | 203.6 | 216.5 | 134.5 | 141.9
4351.1 | 4251.1 | 140.9 | 208 | 203.4 | 216.4 | 134.4 | 141.7
4352.1 | 4252.1 | 140.8 | 207.8 | 203.2 | 216.2 | 134.2 | 141.6
4353.1 | 4253.1 | 140.6 | 207.6 | 203 | 216 | 134.1 | 141.4
4354.1 | 4254.1 | 140.4 | 207.5 | 202.8 | 215.9 | 134 | 141.3
4355.1 | 4255.1 | 140.2 | 207.3 | 202.7 | 215.7 | 133.9 | 141.1
4356.1 | 4256.1 | 140 | 207.1 | 202.5 | 215.6 | 133.7 | 141
4357.1 | 4257.1 | 139.8 | 207 | 202.3 | 215.4 | 133.5 | 140.8
4358.1 | 4258.1 | 139.7 | 206.7 | 202.2 | 215.3 | 133.4 | 140.7
4359.1 | 4259.1 | 139.5 | 206.5 | 202 | 215.1 | 133.1 | 140.6
4360.1 | 4260.1 | 139.4 | 206.3 | 201.8 | 215 | 132.9 | 140.4
4361.1 | 4261.1 | 139.2 | 206.1 | 201.7 | 214.8 | 132.5 | 140.3
4362.1 | 4262.1 | 139 | 206 | 201.5 | 214.7 | 132.2 | 140.1
4363.1 | 4263.1 | 138.8 | 205.7 | 201.3 | 214.5 | 132 | 140
4364.1 | 4264.1 | 138.6 | 205.5 | 201.1 | 214.4 | 131.7 | 139.9
4365.1 | 4265.1 | 138.4 | 205.2 | 201 | 214.2 | 131.4 | 139.7
4366.1 | 4266.1 | 138.2 | 205 | 200.8 | 214.1 | 131 | 139.5
4367.1 | 4267.1 | 138 | 204.8 | 200.6 | 213.9 | 130.8 | 139.4
4368.1 | 4268.1 | 137.9 | 204.6 | 200.4 | 213.8 | 130.5 | 139.3
4369.1 | 4269.1 | 137.7 | 204.4 | 200.3 | 213.6 | 130.2 | 139.1
4370.1 | 4270.1 | 137.5 | 204.2 | 200.1 | 213.5 | 129.8 | 139
4371.1 | 4271.1 | 137.3 | 204 | 199.9 | 213.3 | 129.5 | 138.8
4372.1 | 4272.1 | 137.1 | 203.8 | 199.8 | 213.2 | 129.2 | 138.7
4373.1 | 4273.1 | 136.9 | 203.6 | 199.6 | 213 | 129.2 | 138.5
4374.1 | 4274.1 | 136.7 | 203.4 | 199.5 | 212.9 | 129 | 138.4
4375.1 | 4275.1 | 136.5 | 203.2 | 199.3 | 212.7 | 128.7 | 138.2
4376.1 | 4276.1 | 136.3 | 203 | 199.1 | 212.6 | 128.5 | 138.1
4377.1 | 4277.1 | 136.1 | 202.9 | 199 | 212.4 | 128.4 | 137.9
4378.1 | 4278.1 | 136 | 202.7 | 198.8 | 212.2 | 128.2 | 137.8
4379.1 | 4279.1 | 135.8 | 202.6 | 198.6 | 212.1 | 128.2 | 137.6
4380.1 | 4280.1 | 135.6 | 202.4 | 198.5 | 211.9 | 128.1 | 137.5
4381.1 | 4281.1 | 135.4 | 202.2 | 198.3 | 211.8 | 127.9 | 137.3
4382.1 | 4282.1 | 135.3 | 202 | 198.1 | 211.6 | 127.8 | 137.2
4383.1 | 4283.1 | 135.1 | 201.9 | 198 | 211.5 | 127.8 | 137
4384.1 | 4284.1 | 135 | 201.8 | 197.8 | 211.3 | 127.9 | 136.9
4385.1 | 4285.1 | 134.8 | 201.6 | 197.6 | 211.2 | 127.7 | 136.7
4386.1 | 4286.1 | 134.6 | 201.5 | 197.5 | 211 | 127.7 | 136.6
4387.1 | 4287.1 | 134.4 | 201.4 | 197.3 | 210.9 | 127.7 | 136.4
4388.1 | 4288.1 | 134.2 | 201.2 | 197.2 | 210.7 | 127.6 | 136.3
4389.1 | 4289.1 | 134 | 201.1 | 197 | 210.6 | 127.6 | 136.2
4390.1 | 4290.1 | 133.9 | 200.9 | 196.8 | 210.4 | 127.6 | 136
4391.1 | 4291.1 | 133.7 | 200.8 | 196.7 | 210.3 | 127.5 | 135.9
4392.1 | 4292.1 | 133.5 | 200.7 | 196.5 | 210.1 | 127.3 | 135.7
4393.1 | 4293.1 | 133.3 | 200.5 | 196.4 | 210 | 127.3 | 135.6
4394.1 | 4294.1 | 133.1 | 200.4 | 196.2 | 209.8 | 127.2 | 135.4
4395.1 | 4295.1 | 132.9 | 200.2 | 196 | 209.7 | 127.2 | 135.3
4396.1 | 4296.1 | 132.7 | 200.1 | 195.9 | 209.5 | 127.1 | 135.1
4397.1 | 4297.1 | 132.5 | 200 | 195.7 | 209.4 | 127 | 135
4398.1 | 4298.1 | 132.4 | 199.8 | 195.5 | 209.2 | 126.9 | 134.8
4399.1 | 4299.1 | 132.2 | 199.7 | 195.4 | 209.1 | 126.9 | 134.7
4400.1 | 4300.1 | 132.1 | 199.5 | 195.2 | 208.9 | 126.8 | 134.5
4401.1 | 4301.1 | 131.9 | 199.4 | 195.1 | 208.8 | 126.7 | 134.4
4402.1 | 4302.1 | 131.8 | 199.3 | 194.9 | 208.6 | 126.6 | 134.3
4403.1 | 4303.1 | 131.6 | 199.2 | 194.8 | 208.5 | 126.4 | 134.1
4404.1 | 4304.1 | 131.4 | 199.1 | 194.6 | 208.3 | 126.3 | 134
4405.1 | 4305.1 | 131.3 | 198.9 | 194.4 | 208.1 | 126.2 | 133.8
4406.1 | 4306.1 | 131.1 | 198.8 | 194.3 | 208 | 126.1 | 133.7
4407.1 | 4307.1 | 131 | 198.7 | 194.1 | 207.9 | 126 | 133.6
4408.1 | 4308.1 | 130.8 | 198.6 | 194 | 207.7 | 125.9 | 133.4
4409.1 | 4309.1 | 130.7 | 198.4 | 193.8 | 207.6 | 125.8 | 133.3
4410.1 | 4310.1 | 130.5 | 198.2 | 193.6 | 207.4 | 125.6 | 133.1
4411.1 | 4311.1 | 130.3 | 198.1 | 193.5 | 207.2 | 125.4 | 133
4412.1 | 4312.1 | 130.2 | 197.9 | 193.3 | 207.1 | 125.3 | 132.9
4413.1 | 4313.1 | 130.1 | 197.8 | 193.1 | 206.9 | 125.1 | 132.7
4414.1 | 4314.1 | 129.9 | 197.7 | 193 | 206.8 | 124.8 | 132.6
4415.1 | 4315.1 | 129.7 | 197.6 | 192.8 | 206.6 | 124.7 | 132.5
4416.1 | 4316.1 | 129.5 | 197.5 | 192.7 | 206.5 | 124.7 | 132.3
4417.1 | 4317.1 | 129.4 | 197.3 | 192.5 | 206.3 | 124.6 | 132.2
4418.1 | 4318.1 | 129.2 | 197.2 | 192.3 | 206.2 | 124.4 | 132.1
4419.1 | 4319.1 | 129 | 197 | 192.2 | 206 | 124.3 | 131.9
4420.1 | 4320.1 | 128.8 | 196.9 | 192 | 205.9 | 124.2 | 131.8
4421.1 | 4321.1 | 128.6 | 196.8 | 191.9 | 205.7 | 124.1 | 131.6
4422.1 | 4322.1 | 128.5 | 196.7 | 191.7 | 205.6 | 124 | 131.5
4423.1 | 4323.1 | 128.2 | 196.5 | 191.5 | 205.4 | 123.9 | 131.4
4424.1 | 4324.1 | 128 | 196.3 | 191.4 | 205.3 | 123.8 | 131.2
4425.1 | 4325.1 | 127.9 | 196.2 | 191.2 | 205.1 | 123.6 | 131.1
4426.1 | 4326.1 | 127.8 | 196 | 191.1 | 205 | 123.4 | 131
4427.1 | 4327.1 | 127.7 | 195.9 | 190.9 | 204.8 | 123.3 | 130.8
4428.1 | 4328.1 | 127.5 | 195.7 | 190.8 | 204.7 | 123.2 | 130.7
4429.1 | 4329.1 | 127.4 | 195.5 | 190.6 | 204.6 | 123.1 | 130.6
4430.1 | 4330.1 | 127.2 | 195.4 | 190.4 | 204.4 | 122.9 | 130.4
4431.1 | 4331.1 | 127 | 195.2 | 190.3 | 204.3 | 122.7 | 130.3
4432.1 | 4332.1 | 126.8 | 195.1 | 190.1 | 204.1 | 122.6 | 130.2
4433.1 | 4333.1 | 126.7 | 195 | 190 | 204 | 122.5 | 130
4434.1 | 4334.1 | 126.6 | 194.8 | 189.8 | 203.8 | 122.3 | 129.9
4435.1 | 4335.1 | 126.5 | 194.6 | 189.6 | 203.7 | 122.2 | 129.8
4436.1 | 4336.1 | 126.4 | 194.5 | 189.5 | 203.5 | 122 | 129.6
4437.1 | 4337.1 | 126.2 | 194.4 | 189.3 | 203.4 | 121.9 | 129.5
4438.1 | 4338.1 | 126.1 | 194.3 | 189.2 | 203.2 | 121.8 | 129.4
4439.1 | 4339.1 | 125.9 | 194.1 | 189 | 203.1 | 121.6 | 129.2
4440.1 | 4340.1 | 125.8 | 194 | 188.8 | 202.9 | 121.5 | 129.1
4441.1 | 4341.1 | 125.6 | 193.9 | 188.7 | 202.8 | 121.5 | 129
4442.1 | 4342.1 | 125.5 | 193.8 | 188.5 | 202.6 | 121.3 | 128.8
4443.1 | 4343.1 | 125.4 | 193.7 | 188.3 | 202.5 | 121 | 128.7
4444.1 | 4344.1 | 125.2 | 193.5 | 188.2 | 202.3 | 120.9 | 128.6
4445.1 | 4345.1 | 125 | 193.4 | 188 | 202.2 | 120.7 | 128.5
4446.1 | 4346.1 | 124.9 | 193.2 | 187.8 | 202 | 120.5 | 128.4
4447.1 | 4347.1 | 124.8 | 193.1 | 187.7 | 201.9 | 120.4 | 128.2
4448.1 | 4348.1 | 124.6 | 193 | 187.5 | 201.7 | 120.3 | 128.1
4449.1 | 4349.1 | 124.5 | 192.9 | 187.4 | 201.6 | 120.1 | 128
4450.1 | 4350.1 | 124.4 | 192.7 | 187.2 | 201.4 | 119.9 | 127.9
4451.1 | 4351.1 | 124.2 | 192.5 | 187.1 | 201.3 | 119.9 | 127.7
4452.1 | 4352.1 | 124.1 | 192.4 | 186.9 | 201.2 | 119.8 | 127.6
4453.1 | 4353.1 | 123.9 | 192.2 | 186.7 | 201 | 119.7 | 127.5
4454.1 | 4354.1 | 123.7 | 192.1 | 186.6 | 200.9 | 119.5 | 127.3
4455.1 | 4355.1 | 123.5 | 192 | 186.4 | 200.7 | 119.4 | 127.2
4456.1 | 4356.1 | 123.4 | 191.8 | 186.3 | 200.6 | 119.2 | 127.1
4457.1 | 4357.1 | 123.2 | 191.7 | 186.1 | 200.4 | 119.1 | 126.9
4458.1 | 4358.1 | 123.1 | 191.5 | 186 | 200.3 | 118.7 | 126.8
4459.1 | 4359.1 | 122.9 | 191.3 | 185.8 | 200.1 | 118.5 | 126.7
4460.1 | 4360.1 | 122.8 | 191.2 | 185.7 | 200 | 118.5 | 126.6
4461.1 | 4361.1 | 122.6 | 191.1 | 185.5 | 199.8 | 118.3 | 126.4
4462.1 | 4362.1 | 122.5 | 190.9 | 185.4 | 199.7 | 118 | 126.3
4463.1 | 4363.1 | 122.3 | 190.8 | 185.2 | 199.6 | 117.9 | 126.2
4464.1 | 4364.1 | 122.1 | 190.6 | 185.1 | 199.4 | 117.8 | 126.1
4465.1 | 4365.1 | 122 | 190.5 | 184.9 | 199.3 | 117.7 | 126
4466.1 | 4366.1 | 121.8 | 190.4 | 184.7 | 199.1 | 117.6 | 125.8
4467.1 | 4367.1 | 121.7 | 190.3 | 184.6 | 198.9 | 117.5 | 125.7
4468.1 | 4368.1 | 121.5 | 190.1 | 184.5 | 198.8 | 117.3 | 125.5
4469.1 | 4369.1 | 121.4 | 190 | 184.3 | 198.7 | 117.2 | 125.4
4470.1 | 4370.1 | 121.3 | 189.9 | 184.1 | 198.5 | 117.1 | 125.3
4471.1 | 4371.1 | 121.1 | 189.7 | 184 | 198.4 | 117 | 125.2
4472.1 | 4372.1 | 120.9 | 189.6 | 183.8 | 198.2 | 116.8 | 125.1
4473.1 | 4373.1 | 120.8 | 189.4 | 183.7 | 198.1 | 116.6 | 125
4474.1 | 4374.1 | 120.6 | 189.3 | 183.5 | 197.9 | 116.5 | 124.9
4475.1 | 4375.1 | 120.5 | 189.2 | 183.4 | 197.8 | 116.2 | 124.7
4476.1 | 4376.1 | 120.3 | 189 | 183.2 | 197.7 | 116 | 124.6
4477.1 | 4377.1 | 120.2 | 188.9 | 183.1 | 197.5 | 115.9 | 124.5
4478.1 | 4378.1 | 120.1 | 188.7 | 182.9 | 197.4 | 115.8 | 124.3
4479.1 | 4379.1 | 120 | 188.6 | 182.8 | 197.2 | 115.8 | 124.2
4480.1 | 4380.1 | 119.9 | 188.4 | 182.6 | 197.1 | 115.6 | 124.1
4481.1 | 4381.1 | 119.7 | 188.3 | 182.5 | 196.9 | 115.5 | 124
4482.1 | 4382.1 | 119.6 | 188.1 | 182.3 | 196.8 | 115.4 | 123.9
4483.1 | 4383.1 | 119.5 | 188 | 182.2 | 196.6 | 115.2 | 123.8
4484.1 | 4384.1 | 119.3 | 187.9 | 182 | 196.5 | 115 | 123.6
4485.1 | 4385.1 | 119.2 | 187.8 | 181.9 | 196.4 | 114.9 | 123.5
4486.1 | 4386.1 | 119.1 | 187.6 | 181.7 | 196.2 | 114.8 | 123.4
4487.1 | 4387.1 | 118.9 | 187.5 | 181.6 | 196.1 | 114.7 | 123.3
4488.1 | 4388.1 | 118.7 | 187.4 | 181.4 | 195.9 | 114.6 | 123.2
4489.1 | 4389.1 | 118.5 | 187.2 | 181.3 | 195.8 | 114.4 | 123.1
4490.1 | 4390.1 | 118.4 | 187.1 | 181.1 | 195.6 | 114.3 | 122.9
4491.1 | 4391.1 | 118.2 | 186.9 | 181 | 195.5 | 114.3 | 122.8
4492.1 | 4392.1 | 118.1 | 186.8 | 180.8 | 195.4 | 114.2 | 122.7
4493.1 | 4393.1 | 117.9 | 186.7 | 180.7 | 195.2 | 114 | 122.6
4494.1 | 4394.1 | 117.8 | 186.5 | 180.5 | 195.1 | 113.7 | 122.4
4495.1 | 4395.1 | 117.7 | 186.4 | 180.4 | 194.9 | 113.5 | 122.3
4496.1 | 4396.1 | 117.6 | 186.2 | 180.2 | 194.8 | 113.5 | 122.2
4497.1 | 4397.1 | 117.5 | 186 | 180.1 | 194.6 | 113.4 | 122.1
4498.1 | 4398.1 | 117.4 | 185.9 | 180 | 194.5 | 113.2 | 122
4499.1 | 4399.1 | 117.3 | 185.7 | 179.8 | 194.3 | 113.1 | 121.8
4500.1 | 4400.1 | 117.1 | 185.6 | 179.7 | 194.2 | 113 | 121.7
4501.1 | 4401.1 | 117 | 185.4 | 179.5 | 194.1 | 112.7 | 121.6
4502.1 | 4402.1 | 116.9 | 185.3 | 179.4 | 193.9 | 112.5 | 121.4
4503.1 | 4403.1 | 116.8 | 185.1 | 179.2 | 193.8 | 112.5 | 121.3
4504.1 | 4404.1 | 116.6 | 185 | 179.1 | 193.6 | 112.4 | 121.2
4505.1 | 4405.1 | 116.4 | 184.8 | 178.9 | 193.5 | 112.3 | 121.1
4506.1 | 4406.1 | 116.3 | 184.7 | 178.8 | 193.3 | 112.2 | 120.9
4507.1 | 4407.1 | 116.2 | 184.5 | 178.6 | 193.2 | 112.2 | 120.8
4508.1 | 4408.1 | 116.1 | 184.4 | 178.5 | 193.1 | 112.1 | 120.7
4509.1 | 4409.1 | 116 | 184.3 | 178.3 | 192.9 | 111.9 | 120.5
4510.1 | 4410.1 | 115.9 | 184.2 | 178.2 | 192.8 | 111.7 | 120.4
4511.1 | 4411.1 | 115.8 | 184 | 178.1 | 192.6 | 111.6 | 120.3
4512.1 | 4412.1 | 115.6 | 183.8 | 177.9 | 192.5 | 111.5 | 120.2
4513.1 | 4413.1 | 115.5 | 183.7 | 177.8 | 192.3 | 111.4 | 120.1
4514.1 | 4414.1 | 115.3 | 183.6 | 177.6 | 192.2 | 111.3 | 119.9
4515.1 | 4415.1 | 115.1 | 183.5 | 177.5 | 192.1 | 111 | 119.8
4516.1 | 4416.1 | 115 | 183.3 | 177.3 | 191.9 | 111 | 119.7
4517.1 | 4417.1 | 114.9 | 183.2 | 177.2 | 191.8 | 110.9 | 119.6
4518.1 | 4418.1 | 114.8 | 183.1 | 177.1 | 191.6 | 110.7 | 119.5
4519.1 | 4419.1 | 114.6 | 183 | 176.9 | 191.5 | 110.6 | 119.4
4520.1 | 4420.1 | 114.5 | 182.9 | 176.8 | 191.4 | 110.5 | 119.3
4521.1 | 4421.1 | 114.3 | 182.7 | 176.6 | 191.2 | 110.4 | 119.2
4522.1 | 4422.1 | 114.2 | 182.6 | 176.5 | 191.1 | 110.3 | 119
4523.1 | 4423.1 | 114.1 | 182.5 | 176.4 | 190.9 | 110.2 | 118.9
4524.1 | 4424.1 | 113.9 | 182.3 | 176.2 | 190.8 | 110.1 | 118.8
4525.1 | 4425.1 | 113.8 | 182.2 | 176.1 | 190.7 | 110.1 | 118.7
4526.1 | 4426.1 | 113.6 | 182 | 175.9 | 190.5 | 110 | 118.5
4527.1 | 4427.1 | 113.4 | 181.9 | 175.8 | 190.4 | 110 | 118.5
4528.1 | 4428.1 | 113.3 | 181.8 | 175.7 | 190.3 | 110 | 118.4
4529.1 | 4429.1 | 113.1 | 181.7 | 175.5 | 190.1 | 109.9 | 118.2
4530.1 | 4430.1 | 113 | 181.5 | 175.4 | 190 | 109.6 | 118.1
4531.1 | 4431.1 | 113 | 181.4 | 175.2 | 189.8 | 109.5 | 118
4532.1 | 4432.1 | 112.9 | 181.3 | 175.1 | 189.7 | 109.4 | 117.9
4533.1 | 4433.1 | 112.9 | 181.2 | 175 | 189.5 | 109.2 | 117.8
4534.1 | 4434.1 | 112.8 | 181.1 | 174.8 | 189.4 | 109.1 | 117.7
4535.1 | 4435.1 | 112.6 | 180.9 | 174.7 | 189.3 | 109.1 | 117.5
4536.1 | 4436.1 | 112.5 | 180.8 | 174.5 | 189.1 | 109 | 117.4
4537.1 | 4437.1 | 112.3 | 180.6 | 174.4 | 189 | 108.9 | 117.3
4538.1 | 4438.1 | 112.2 | 180.4 | 174.3 | 188.9 | 108.8 | 117.2
4539.1 | 4439.1 | 112.1 | 180.3 | 174.1 | 188.7 | 108.6 | 117.1
4540.1 | 4440.1 | 111.9 | 180.1 | 174 | 188.6 | 108.5 | 117
4541.1 | 4441.1 | 111.7 | 180 | 173.8 | 188.4 | 108.4 | 116.9
4542.1 | 4442.1 | 111.6 | 179.8 | 173.7 | 188.3 | 108.2 | 116.8
4543.1 | 4443.1 | 111.5 | 179.6 | 173.5 | 188.2 | 108.2 | 116.7
4544.1 | 4444.1 | 111.3 | 179.4 | 173.4 | 188 | 108.1 | 116.6
4545.1 | 4445.1 | 111.2 | 179.3 | 173.2 | 187.9 | 107.9 | 116.5
4546.1 | 4446.1 | 111.1 | 179.2 | 173.1 | 187.7 | 107.8 | 116.4
4547.1 | 4447.1 | 110.9 | 179 | 173 | 187.6 | 107.8 | 116.3
4548.1 | 4448.1 | 110.8 | 178.8 | 172.8 | 187.5 | 107.7 | 116.1
4549.1 | 4449.1 | 110.7 | 178.7 | 172.7 | 187.3 | 107.5 | 116
4550.1 | 4450.1 | 110.5 | 178.5 | 172.6 | 187.2 | 107.4 | 115.9
4551.1 | 4451.1 | 110.4 | 178.3 | 172.4 | 187 | 107.3 | 115.8
4552.1 | 4452.1 | 110.3 | 178.2 | 172.3 | 186.9 | 107.2 | 115.7
4553.1 | 4453.1 | 110.2 | 178 | 172.1 | 186.8 | 107.2 | 115.6
4554.1 | 4454.1 | 110.1 | 177.9 | 172 | 186.6 | 107.1 | 115.5
4555.1 | 4455.1 | 110 | 177.7 | 171.9 | 186.5 | 106.9 | 115.4
4556.1 | 4456.1 | 109.9 | 177.6 | 171.7 | 186.4 | 106.9 | 115.3
4557.1 | 4457.1 | 109.7 | 177.5 | 171.6 | 186.2 | 106.7 | 115.2
4558.1 | 4458.1 | 109.6 | 177.4 | 171.5 | 186.1 | 106.6 | 115.1
4559.1 | 4459.1 | 109.5 | 177.2 | 171.3 | 186 | 106.5 | 115
4560.1 | 4460.1 | 109.4 | 177.1 | 171.2 | 185.8 | 106.4 | 114.9
4561.1 | 4461.1 | 109.3 | 177 | 171.1 | 185.7 | 106.3 | 114.7
4562.1 | 4462.1 | 109.2 | 176.9 | 170.9 | 185.5 | 106.2 | 114.6
4563.1 | 4463.1 | 109 | 176.7 | 170.8 | 185.4 | 106.1 | 114.5
4564.1 | 4464.1 | 108.9 | 176.7 | 170.6 | 185.3 | 106 | 114.4
4565.1 | 4465.1 | 108.8 | 176.6 | 170.5 | 185.1 | 106 | 114.3
4566.1 | 4466.1 | 108.7 | 176.4 | 170.4 | 185 | 106 | 114.2
4567.1 | 4467.1 | 108.5 | 176.4 | 170.2 | 184.9 | 105.9 | 114.1
4568.1 | 4468.1 | 108.4 | 176.2 | 170.1 | 184.7 | 105.7 | 114
4569.1 | 4469.1 | 108.3 | 176.1 | 170 | 184.6 | 105.5 | 113.9
4570.1 | 4470.1 | 108.2 | 176 | 169.8 | 184.5 | 105.4 | 113.8
4571.1 | 4471.1 | 108.1 | 175.9 | 169.7 | 184.3 | 105.3 | 113.7
4572.1 | 4472.1 | 108.1 | 175.8 | 169.5 | 184.2 | 105.1 | 113.6
4573.1 | 4473.1 | 108 | 175.7 | 169.4 | 184 | 104.9 | 113.5
4574.1 | 4474.1 | 107.9 | 175.5 | 169.3 | 183.9 | 104.9 | 113.4
4575.1 | 4475.1 | 107.8 | 175.4 | 169.1 | 183.8 | 104.9 | 113.3
4576.1 | 4476.1 | 107.7 | 175.3 | 169 | 183.6 | 104.7 | 113.2
4577.1 | 4477.1 | 107.5 | 175.2 | 168.8 | 183.5 | 104.6 | 113.1
4578.1 | 4478.1 | 107.4 | 175.1 | 168.7 | 183.4 | 104.6 | 113
4579.1 | 4479.1 | 107.3 | 174.9 | 168.6 | 183.2 | 104.5 | 112.9
4580.1 | 4480.1 | 107.2 | 174.8 | 168.4 | 183.1 | 104.4 | 112.8
4581.1 | 4481.1 | 107.1 | 174.7 | 168.3 | 183 | 104.3 | 112.7
4582.1 | 4482.1 | 106.9 | 174.5 | 168.1 | 182.8 | 104.2 | 112.6
4583.1 | 4483.1 | 106.8 | 174.4 | 168 | 182.7 | 104.1 | 112.4
4584.1 | 4484.1 | 106.7 | 174.2 | 167.9 | 182.6 | 103.9 | 112.3
4585.1 | 4485.1 | 106.6 | 174.1 | 167.7 | 182.4 | 103.9 | 112.3
4586.1 | 4486.1 | 106.5 | 174 | 167.6 | 182.3 | 103.9 | 112.1
4587.1 | 4487.1 | 106.3 | 173.8 | 167.5 | 182.1 | 103.9 | 112.1
4588.1 | 4488.1 | 106.2 | 173.7 | 167.3 | 182 | 103.8 | 111.9
4589.1 | 4489.1 | 106 | 173.6 | 167.2 | 181.9 | 103.7 | 111.8
4590.1 | 4490.1 | 105.9 | 173.5 | 167 | 181.7 | 103.7 | 111.7
4591.1 | 4491.1 | 105.8 | 173.3 | 166.9 | 181.6 | 103.6 | 111.6
4592.1 | 4492.1 | 105.7 | 173.2 | 166.8 | 181.5 | 103.4 | 111.6
4593.1 | 4493.1 | 105.6 | 173 | 166.6 | 181.3 | 103.3 | 111.4
4594.1 | 4494.1 | 105.4 | 172.9 | 166.5 | 181.2 | 103.3 | 111.3
4595.1 | 4495.1 | 105.4 | 172.7 | 166.3 | 181.1 | 103.3 | 111.3
4596.1 | 4496.1 | 105.3 | 172.6 | 166.2 | 180.9 | 103.2 | 111.2
4597.1 | 4497.1 | 105.2 | 172.4 | 166.1 | 180.8 | 103.1 | 111
4598.1 | 4498.1 | 105.1 | 172.3 | 165.9 | 180.7 | 103.1 | 111
4599.1 | 4499.1 | 104.9 | 172.1 | 165.8 | 180.5 | 103 | 110.8
4600.1 | 4500.1 | 104.8 | 172 | 165.7 | 180.4 | 102.9 | 110.7
4601.1 | 4501.1 | 104.7 | 171.8 | 165.5 | 180.3 | 102.7 | 110.6
4602.1 | 4502.1 | 104.6 | 171.7 | 165.4 | 180.1 | 102.6 | 110.5
4603.1 | 4503.1 | 104.5 | 171.5 | 165.3 | 180 | 102.6 | 110.4
4604.1 | 4504.1 | 104.4 | 171.3 | 165.2 | 179.9 | 102.5 | 110.4
4605.1 | 4505.1 | 104.3 | 171.2 | 165 | 179.7 | 102.5 | 110.2
4606.1 | 4506.1 | 104.2 | 171.1 | 164.9 | 179.6 | 102.3 | 110.1
4607.1 | 4507.1 | 104.1 | 171 | 164.8 | 179.5 | 102.2 | 110.1
4608.1 | 4508.1 | 103.9 | 170.8 | 164.6 | 179.3 | 102.1 | 110
4609.1 | 4509.1 | 103.8 | 170.7 | 164.5 | 179.2 | 102 | 109.9
4610.1 | 4510.1 | 103.7 | 170.6 | 164.4 | 179.1 | 102 | 109.8
4611.1 | 4511.1 | 103.5 | 170.4 | 164.3 | 178.9 | 101.9 | 109.7
4612.1 | 4512.1 | 103.4 | 170.3 | 164.1 | 178.8 | 101.8 | 109.5
4613.1 | 4513.1 | 103.3 | 170.1 | 164 | 178.7 | 101.8 | 109.4
4614.1 | 4514.1 | 103.2 | 170 | 163.9 | 178.5 | 101.8 | 109.4
4615.1 | 4515.1 | 103.1 | 169.8 | 163.8 | 178.4 | 101.8 | 109.3
4616.1 | 4516.1 | 102.9 | 169.7 | 163.7 | 178.3 | 101.7 | 109.2
4617.1 | 4517.1 | 102.8 | 169.6 | 163.5 | 178.1 | 101.7 | 109.1
4618.1 | 4518.1 | 102.7 | 169.5 | 163.4 | 178 | 101.7 | 109

## Test Facts
Date: | 2006-08-18
Supplemental Penlight Test 1
Thermal response of 6-cable bundle compared to a single cable
Penlight Ignition Time | 100
Cables: | PE insulated, PVC jacketed, #12 AWG, 7-conductor (Item #15)
Shroud temperatures: |  | 350 C initially, increased to 375 C at ~1950 s, increased again to 400 C at ~2875 s
Cable response: |  | Only smoking and dripping, no ignition or fire occurred
Cable arrangement:
Tray Rung
Shaded cables were instrumented with a single thermocouple
located just below the outer jacket. All thermocouples were
placed at center of cable length within the Penlight shroud.