## Test Facts
Last row in IRMS data sheets: | 13
Time when Penlight power was initiated: | 158

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 63
Test conditions: Cable: 12-conductor, 18 AWG, PVC insulated, PVC jacketed, instrument cable (Cable Item #6). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 325C, nominal 7.2 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using twelve channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and two cable temperatures (see thermocouple map). One thermocouple was attached to the inside of the center tray rung. Shroud power: Initiated after 158 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
158 | 0 | Initated Penlight Heating
491 | 333 | Conductor 10 shorts to ground at less than 100 ohms (10)
547-550 | 389-392 | Conductor 10 shorts to conductors 11 & 12 at less than 100 ohms (19 & 8)
569-681 | 411-523 | Conductors 1 through 9, and conductors 11 & 12 all short to ground at less than 100 ohms | All conductors are shorted to ground
575-584 | 417-426 | Conductor 1 shorts to conductors 9 through 12 at less than 100 ohms
586-612 | 428-454 | Conductor 2 shorts to conductors 3 through 12 at less than 100 ohms
614-637 | 456-479 | Conductor 3 shorts to conductors 4 through 12 at less than 100 ohms
640-659 | 482-501 | Conductor 4 shorts to conductors 5 through 12 at less than 100 ohms
665-679 | 507-521 | Conductor 5 shorts to conductors 7 through 12 at less than 100 ohms
682-696 | 524-538 | Conductor 6 shorts to conductors 7 through 12 at less than 100 ohms
698-710 | 540-552 | Conductor 7 shorts to conductors 8 through 12 at less than 1000 ohms
712-721 | 554-563 | Conductor 8 shorts to conductors 9 through 12 at less than 100 ohms
724-729 | 566-571 | Conductor 9 shorts to conductors 10 through 12 at less than 100 ohms
738 | 580 | Conductors 11 & 12 short together at less than 100 ohms (25)
740-757 | 582-599 | Conductor 1 shorts to conductors 2 through 8 at less than 100 ohms
847 | 689 | Conductors 5 & 6 short together at less than 100 ohms (16) | All conductors are shorted together
Additional Observations
Observation 1 | It took 333 s (5.6 min.) for the initial short to ground failure to occur, and 389 s (6.5 min.) for the first internal shorts.
Observation 2 | The progression of conductor failures -- to ground and among conductors -- occurred rapidly once started.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | "Cable 1" | Within cable just below cable jacket, center position
| TC2 | = | "Cable 2" | Within cable just below cable jacket, center position

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 63 |  |  | 2006-08-28 | 14:47
PVC | 12-C | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C1-8 | Penlight Time | C1-9 | Penlight Time | C1-10 | Penlight Time | C1-11 | Penlight Time | C1-12 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C2-8 | Penlight Time | C2-9 | Penlight Time | C2-10 | Penlight Time | C2-11 | Penlight Time | C2-12 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C3-8 | Penlight Time | C3-9 | Penlight Time | C3-10 | Penlight Time | C3-11 | Penlight Time | C3-12 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C4-8 | Penlight Time | C4-9 | Penlight Time | C4-10 | Penlight Time | C4-11 | Penlight Time | C4-12 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C5-8 | Penlight Time | C5-9 | Penlight Time | C5-10 | Penlight Time | C5-11 | Penlight Time | C5-12 | Penlight Time | C6-7 | Penlight Time | C6-8 | Penlight Time | C6-9 | Penlight Time | C6-10 | Penlight Time | C6-11 | Penlight Time | C6-12 | Penlight Time | C7-8 | Penlight Time | C7-9 | Penlight Time | C7-10 | Penlight Time | C7-11 | Penlight Time | C7-12 | Penlight Time | C8-9 | Penlight Time | C8-10 | Penlight Time | C8-11 | Penlight Time | C8-12 | Penlight Time | C9-10 | Penlight Time | C9-11 | Penlight Time | C9-12 | Penlight Time | C10-11 | Penlight Time | C10-12 | Penlight Time | C11-12
-157 | 236237.9994 | -154 | 237037.9994 | -151.5 | 254537.9994 | -148.5 | 239737.9994 | -145.5 | 238637.9994 | -143 | 211201.9994 | -140 | 228937.9994 | -137.5 | 240637.9994 | -134.5 | 257537.9994 | -131.5 | 257437.9994 | -129 | 257337.9994 | -126 | 221537.9994 | -123.5 | 244037.9994 | -120.5 | 244737.9994 | -117.5 | 254837.9994 | -115 | 257137.9994 | -112 | 245437.9994 | -109.5 | 226237.9994 | -106.5 | 256437.9994 | -104 | 236737.9994 | -101 | 241237.9994 | -98 | 256437.9994 | -95.5 | 257037.9994 | -92.5 | 256837.9994 | -90 | 247037.9994 | -87 | 254737.9994 | -84 | 242137.9994 | -81.5 | 253037.9994 | -78.5 | 254737.9994 | -75.5 | 244037.9994 | -73 | 238037.9994 | -70.5 | 252537.9994 | -67.5 | 250237.9994 | -64.5 | 255637.9994 | -61.5 | 256337.9994 | -59 | 218137.9994 | -56 | 256937.9994 | -53.5 | 256937.9994 | -50.5 | 256537.9994 | -47.5 | 256437.9994 | -45 | 245837.9994 | -42 | 246737.9994 | -39.5 | 242137.9994 | -36.5 | 221637.9994 | -34 | 253737.9994 | -31 | 242537.9994 | -28 | 250937.9994 | -25.5 | 251537.9994 | -22.5 | 244037.9994 | -19.5 | 250437.9994 | -17 | 243137.9994 | -14.5 | 240837.9994 | -11.5 | 218337.9994 | -8.5 | 256537.9994 | -5.5 | 247137.9994 | -3 | 252237.9994 | -1.5553e-07 | 236537.9994 | 2.5 | 249537.9994 | 5.5 | 257137.9994 | 8.5 | 257437.9994 | 11 | 257437.9994 | 14 | 249737.9994 | 16.5 | 252737.9994 | 19.5 | 248237.9994 | 22.5 | 243137.9994 | 25 | 258837.9994
28 | 236237.9994 | 30.5 | 237037.9994 | 33.5 | 254537.9994 | 36 | 239737.9994 | 39 | 238637.9994 | 42 | 211201.9994 | 44.5 | 228937.9994 | 47.5 | 240637.9994 | 50.5 | 257537.9994 | 53 | 257437.9994 | 55.5 | 257337.9994 | 58.5 | 221537.9994 | 61.5 | 244037.9994 | 64 | 244737.9994 | 67 | 254837.9994 | 70 | 257137.9994 | 72.5 | 245437.9994 | 75.5 | 226237.9994 | 78 | 256437.9994 | 81 | 236737.9994 | 83.5 | 241237.9994 | 86.5 | 256437.9994 | 89.5 | 257037.9994 | 92 | 256837.9994 | 95 | 247037.9994 | 98 | 254737.9994 | 100.5 | 242137.9994 | 103.5 | 253037.9994 | 106.5 | 254737.9994 | 109 | 244037.9994 | 112 | 238037.9994 | 114.5 | 252537.9994 | 117.5 | 250237.9994 | 120 | 255637.9994 | 123 | 256337.9994 | 125.5 | 218137.9994 | 128.5 | 256937.9994 | 131.5 | 256937.9994 | 134.5 | 256537.9994 | 137 | 256437.9994 | 140 | 245837.9994 | 142.5 | 246737.9994 | 145.5 | 242137.9994 | 148.5 | 221637.9994 | 151 | 253737.9994 | 153.5 | 242537.9994 | 156.5 | 250937.9994 | 159.5 | 251537.9994 | 162 | 244037.9994 | 165 | 250437.9994 | 168 | 243137.9994 | 170.5 | 240837.9994 | 173.5 | 218337.9994 | 176 | 256537.9994 | 179 | 247137.9994 | 181.5 | 252237.9994 | 184.5 | 236537.9994 | 187.5 | 249537.9994 | 190.5 | 257137.9994 | 193 | 257437.9994 | 196 | 257437.9994 | 198.5 | 249737.9994 | 201.5 | 252737.9994 | 204.5 | 248237.9994 | 207 | 243137.9994 | 210 | 258837.9994
212.5 | 236237.9994 | 215.5 | 237037.9994 | 218.5 | 254537.9994 | 221 | 239737.9994 | 224 | 238637.9994 | 226.5 | 211201.9994 | 229.5 | 228937.9994 | 232 | 240637.9994 | 235 | 257537.9994 | 237.5 | 257437.9994 | 240.5 | 257337.9994 | 243.5 | 221537.9994 | 246 | 244037.9994 | 249 | 244737.9994 | 251.5 | 254837.9994 | 254 | 257137.9994 | 257.5 | 245437.9994 | 260 | 226237.9994 | 263 | 256437.9994 | 266 | 236737.9994 | 268.5 | 241237.9994 | 271.5 | 256437.9994 | 274.5 | 257037.9994 | 277 | 256837.9994 | 280 | 247037.9994 | 282.5 | 254737.9994 | 285.5 | 242137.9994 | 288 | 253037.9994 | 291 | 254737.9994 | 293.5 | 244037.9994 | 296.5 | 238037.9994 | 299.5 | 252537.9994 | 302 | 250237.9994 | 305 | 255637.9994 | 307.5 | 256337.9994 | 310.5 | 218137.9994 | 313.5 | 256937.9994 | 316.5 | 256937.9994 | 319 | 256537.9994 | 321.5 | 256437.9994 | 324.5 | 245837.9994 | 327.5 | 246737.9994 | 330 | 242137.9994 | 333 | 221637.9994 | 336 | 253737.9994 | 338.5 | 242537.9994 | 341.5 | 250937.9994 | 344 | 251537.9994 | 347 | 244037.9994 | 349.5 | 250437.9994 | 352.5 | 243137.9994 | 355.5 | 240837.9994 | 358.5 | 218337.9994 | 361 | 256537.9994 | 363.5 | 247137.9994 | 366.5 | 252237.9994 | 369.5 | 236537.9994 | 372 | 249537.9994 | 375 | 257137.9994 | 378 | 257437.9994 | 380.5 | 257437.9994 | 383.5 | 249737.9994 | 386.5 | 252737.9994 | 389 | 18.9998 | 392 | 8.3114 | 394.5 | 258837.9994
397.5 | 236237.9994 | 400.5 | 237037.9994 | 403 | 254537.9994 | 405.5 | 239737.9994 | 408.5 | 238637.9994 | 411.5 | 211201.9994 | 414 | 228937.9994 | 417 | 0.64632 | 419.5 | 0.37042 | 422.5 | 0.49475 | 425.5 | 10.8714 | 428 | 8.9114 | 431 | 0.805 | 433.5 | 22.9624 | 436.5 | 0.89973 | 439.5 | 1.8304 | 442 | 0.81742 | 445 | 2.2532 | 448 | 0.91356 | 450.5 | 11.7156 | 453.5 | 15.8393 | 456 | 22.1257 | 459 | 0.91873 | 461.5 | 0.91701 | 464.5 | 11.8775 | 467.5 | 0.37152 | 470 | 0.78807 | 473 | 12.6708 | 475.5 | 26.5204 | 478.5 | 8.4165 | 481.5 | 3.6145 | 484.5 | 0.87977 | 487 | 10.6943 | 489.5 | 0.5839 | 492.5 | 0.83242 | 495.5 | 4.9548 | 498 | 3.7663 | 501 | 0.19741 | 503.5 | 3971.1775 | 506.5 | 0.057694 | 509.5 | 5.5804 | 512 | 10.3422 | 515 | 19.7758 | 518 | 8.3735 | 520.5 | 9.1549 | 523.5 | 0.79164 | 526 | 1.9971 | 529 | 8.3904 | 531.5 | 10.348 | 534.5 | 0.86144 | 537.5 | 5.9591 | 540 | 12.7365 | 543 | 5.779 | 545.5 | 6.149 | 548.5 | 1.6143 | 551.5 | 101.3825 | 554 | 15.1573 | 557 | 10.4823 | 559.5 | 27.398 | 562.5 | 4.4108 | 565.5 | 7.8732 | 568 | 21.2242 | 571 | 12.0189 | 573.5 | 12.6385 | 576.5 | 0.79699 | 579.5 | 24.5638
582 | 0.73493 | 585 | 0.74219 | 587.5 | 18.5323 | 590.5 | 0.76656 | 593.5 | 0.75665 | 596 | 4.0572 | 599 | 7.5215 | 601.5 | 11.6685 | 604.5 | 0.92304 | 607.5 | 0.92218 | 610 | 7.7838 | 613 | 9.9915 | 615.5 | 2.8136 | 618.5 | 14.3609 | 621.5 | 65.3095 | 624 | 0.91959 | 627 | 5.0701 | 629.5 | 0.64282 | 632.5 | 26.7251 | 635.5 | 0.73947 | 638 | 18.7812 | 641 | 0.064706 | 643.5 | 17.7824 | 646.5 | 3.5509 | 649.5 | 13.4733 | 652 | 0.41227 | 655 | 5.3746 | 657.5 | 21.0252 | 660.5 | 9.2002 | 663.5 | 13.8103 | 666 | 4.0856 | 669 | 11.5704 | 671.5 | 0.19815 | 674.5 | 20.6153 | 677.5 | 0.63117 | 680 | 8.9562 | 683 | 3.0714 | 685.5 | 29.1399 | 688.5 | 16.2838 | 691.5 | 2.868 | 694 | 17.9543 | 697 | 5.5398 | 699.5 | 20.8224 | 702.5 | 9.648 | 705.5 | 9.1062 | 708 | 12.6683 | 711 | 0.86581 | 713.5 | 9.0246 | 716.5 | 20.418 | 719.5 | 16.1002 | 722 | 11.3443 | 725 | 4.1888 | 727.5 | 0.56803 | 730.5 | 13.4624 | 733.5 | 20.8566 | 737 | 22.919 | 739 | 0.73766 | 742 | 8.7834 | 744.5 | 0.75941 | 747.5 | 0.03603 | 750 | 1.9931 | 753 | 0.85531 | 756 | 0.39105 | 758.5 | 0.84214 | 761.5 | 17.4597 | 764 | 0.93421

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 63 |  |  | 2006-08-28 | 14:47
PVC | 12-C | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | C8-G | Penlight Time | C9-G | Penlight Time | C10-G | Penlight Time | C11-G | Penlight Time | C12-G
-142.9091 | 211202 |  | -117.5 | 221538 | -96.5909 | 221538 | -79.8636 | 218138 | -66.5909 | 221638 | -56.3636 | 238638 | -48.8182 | 211202 | -43.1364 | 228938 | -39.0909 | 218338 | -36.0455 | 36562.5714 | -33.4091 | 221638 | -30.9545 | 241238
41.8182 | 211202 |  | 67.2273 | 221538 | 88.1364 | 221538 | 104.9091 | 218138 | 118.2273 | 221638 | 128.3182 | 238638 | 135.9545 | 211202 | 141.5909 | 228938 | 145.6818 | 218338 | 148.7273 | 218138 | 151.3636 | 110769 | 153.7727 | 241238
226.5909 | 211202 |  | 251.9545 | 221538 | 272.9545 | 221538 | 289.7273 | 218138 | 302.9545 | 221638 | 313.0909 | 238638 | 320.6818 | 211202 | 326.4091 | 228938 | 330.4545 | 218338 | 333.4545 | 9.6655 | 336 | 221638 | 338.6364 | 121519
411.3636 | 0.81156 |  | 436.8182 | 0.6426 | 457.6364 | 0.6411 | 474.5 | 0.6426 | 487.6818 | 0.6926 | 497.8636 | 0.6581 | 505.5455 | 1.5529 | 511.0455 | 0.64692 | 515.1818 | 0.64286 | 518.2273 | 0.37008 | 520.7273 | 0.64135 | 523.4091 | 0.59763
596.0909 | 0.63984 |  | 621.5455 | 0.64085 | 642.4545 | 0.74455 | 659.1818 | 0.64743 | 672.4545 | 0.67352 | 682.6818 | 0.64235 | 690.3636 | 0.6426 | 695.9545 | 0.64463 | 699.9545 | 0.6552 | 703 | 0.66048 | 705.6364 | 0.63661 | 708.2273 | 0.64034

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Tray Rung
0 | -158 | 28.6 | 34.5 | 34.3 | 38.8
1 | -157 | 28.6 | 34.5 | 34.3 | 38.8
2 | -156 | 28.6 | 34.5 | 34.3 | 38.8
3 | -155 | 28.6 | 34.5 | 34.3 | 38.8
4 | -154 | 28.6 | 34.5 | 34.3 | 38.8
5 | -153 | 28.6 | 34.5 | 34.3 | 38.8
6 | -152 | 28.6 | 34.5 | 34.3 | 38.8
7 | -151 | 28.6 | 34.5 | 34.3 | 38.8
8 | -150 | 28.6 | 34.5 | 34.3 | 38.8
9 | -149 | 28.6 | 34.5 | 34.3 | 38.8
10 | -148 | 28.5 | 34.5 | 34.2 | 38.8
11 | -147 | 28.5 | 34.5 | 34.3 | 38.8
12 | -146 | 28.5 | 34.5 | 34.2 | 38.8
13 | -145 | 28.5 | 34.5 | 34.2 | 38.8
14 | -144 | 28.5 | 34.5 | 34.2 | 38.8
15 | -143 | 28.5 | 34.5 | 34.2 | 38.8
16 | -142 | 28.5 | 34.5 | 34.2 | 38.8
17 | -141 | 28.5 | 34.5 | 34.2 | 38.8
18 | -140 | 28.5 | 34.5 | 34.2 | 38.8
19 | -139 | 28.5 | 34.5 | 34.2 | 38.8
20 | -138 | 28.5 | 34.5 | 34.2 | 38.8
21 | -137 | 28.5 | 34.5 | 34.2 | 38.8
22 | -136 | 28.5 | 34.5 | 34.2 | 38.8
23 | -135 | 28.5 | 34.5 | 34.2 | 38.8
24 | -134 | 28.5 | 34.5 | 34.2 | 38.8
25 | -133 | 28.5 | 34.5 | 34.2 | 38.8
26 | -132 | 28.5 | 34.5 | 34.2 | 38.8
27 | -131 | 28.5 | 34.5 | 34.2 | 38.8
28 | -130 | 28.5 | 34.4 | 34.2 | 38.8
29 | -129 | 28.5 | 34.5 | 34.2 | 38.8
30 | -128 | 28.5 | 34.4 | 34.2 | 38.8
31 | -127 | 28.5 | 34.4 | 34.2 | 38.8
32 | -126 | 28.5 | 34.4 | 34.2 | 38.8
33 | -125 | 28.4 | 34.4 | 34.1 | 38.8
34 | -124 | 28.4 | 34.4 | 34.2 | 38.7
35 | -123 | 28.4 | 34.4 | 34.2 | 38.7
36 | -122 | 28.4 | 34.4 | 34.2 | 38.7
37 | -121 | 28.4 | 34.4 | 34.1 | 38.7
38 | -120 | 28.4 | 34.4 | 34.2 | 38.7
39 | -119 | 28.4 | 34.4 | 34.1 | 38.7
40 | -118 | 28.4 | 34.4 | 34.1 | 38.7
41 | -117 | 28.4 | 34.4 | 34.2 | 38.7
42 | -116 | 28.4 | 34.4 | 34.1 | 38.7
43 | -115 | 28.4 | 34.4 | 34.1 | 38.7
44 | -114 | 28.4 | 34.4 | 34.1 | 38.7
45 | -113 | 28.4 | 34.4 | 34.1 | 38.7
46 | -112 | 28.4 | 34.4 | 34.1 | 38.7
47 | -111 | 28.4 | 34.4 | 34.1 | 38.7
48 | -110 | 28.4 | 34.4 | 34.1 | 38.7
49 | -109 | 28.4 | 34.4 | 34.1 | 38.7
50 | -108 | 28.4 | 34.4 | 34.1 | 38.7
51 | -107 | 28.4 | 34.4 | 34.1 | 38.7
52 | -106 | 28.4 | 34.4 | 34.1 | 38.7
53 | -105 | 28.3 | 34.4 | 34.1 | 38.8
54 | -104 | 28.3 | 34.4 | 34.1 | 38.8
55 | -103 | 28.3 | 34.4 | 34.1 | 38.8
56 | -102 | 28.3 | 34.4 | 34.1 | 38.8
57 | -101 | 28.3 | 34.4 | 34.1 | 38.8
58 | -100 | 28.3 | 34.4 | 34.1 | 38.8
59 | -99 | 28.3 | 34.4 | 34.1 | 38.8
60 | -98 | 28.3 | 34.4 | 34.1 | 38.8
61 | -97 | 28.3 | 34.4 | 34 | 38.8
62 | -96 | 28.3 | 34.3 | 34 | 38.8
63 | -95 | 28.3 | 34.3 | 34.1 | 38.8
64 | -94 | 28.3 | 34.3 | 34 | 38.8
65 | -93 | 28.3 | 34.3 | 34 | 38.8
66 | -92 | 28.3 | 34.3 | 34 | 38.8
67 | -91 | 28.3 | 34.3 | 34 | 38.8
68 | -90 | 28.3 | 34.3 | 34 | 38.8
69 | -89 | 28.3 | 34.3 | 34 | 38.7
70 | -88 | 28.3 | 34.3 | 34 | 38.7
71 | -87 | 28.3 | 34.3 | 34 | 38.8
72 | -86 | 28.3 | 34.3 | 34 | 38.8
73 | -85 | 28.3 | 34.3 | 34 | 38.8
74 | -84 | 28.3 | 34.3 | 34 | 38.7
75 | -83 | 28.3 | 34.3 | 34 | 38.7
76 | -82 | 28.2 | 34.3 | 34 | 38.7
77 | -81 | 28.2 | 34.3 | 34 | 38.7
78 | -80 | 28.2 | 34.3 | 34 | 38.7
79 | -79 | 28.2 | 34.3 | 34 | 38.7
80 | -78 | 28.2 | 34.3 | 34 | 38.6
81 | -77 | 28.2 | 34.3 | 34 | 38.6
82 | -76 | 28.2 | 34.3 | 34 | 38.7
83 | -75 | 28.2 | 34.3 | 34 | 38.6
84 | -74 | 28.2 | 34.3 | 34 | 38.6
85 | -73 | 28.2 | 34.3 | 34 | 38.6
86 | -72 | 28.2 | 34.3 | 34 | 38.6
87 | -71 | 28.2 | 34.3 | 34 | 38.6
88 | -70 | 28.2 | 34.3 | 34 | 38.6
89 | -69 | 28.2 | 34.3 | 34 | 38.6
90 | -68 | 28.2 | 34.3 | 34 | 38.6
91 | -67 | 28.2 | 34.2 | 34 | 38.6
92 | -66 | 28.2 | 34.2 | 33.9 | 38.6
93 | -65 | 28.2 | 34.2 | 33.9 | 38.6
94 | -64 | 28.2 | 34.2 | 33.9 | 38.6
95 | -63 | 28.2 | 34.2 | 33.9 | 38.6
96 | -62 | 28.2 | 34.2 | 33.9 | 38.6
97 | -61 | 28.1 | 34.2 | 33.9 | 38.6
98 | -60 | 28.1 | 34.2 | 33.9 | 38.6
99 | -59 | 28.1 | 34.2 | 33.9 | 38.6
100 | -58 | 28.1 | 34.2 | 33.9 | 38.6
101 | -57 | 28.1 | 34.2 | 33.9 | 38.6
102 | -56 | 28.1 | 34.2 | 33.9 | 38.6
103 | -55 | 28.1 | 34.2 | 33.9 | 38.6
104 | -54 | 28.1 | 34.2 | 33.9 | 38.6
105 | -53 | 28.1 | 34.2 | 33.9 | 38.6
106 | -52 | 28.1 | 34.2 | 33.9 | 38.6
107 | -51 | 28.1 | 34.2 | 33.9 | 38.6
108 | -50 | 28.1 | 34.2 | 33.9 | 38.6
109 | -49 | 28.1 | 34.2 | 33.9 | 38.6
110 | -48 | 28.1 | 34.2 | 33.8 | 38.6
111 | -47 | 28.1 | 34.2 | 33.8 | 38.6
112 | -46 | 28.1 | 34.1 | 33.8 | 38.5
113 | -45 | 28.1 | 34.1 | 33.8 | 38.6
114 | -44 | 28.1 | 34.1 | 33.8 | 38.5
115 | -43 | 28 | 34.1 | 33.8 | 38.5
116 | -42 | 28.1 | 34.1 | 33.8 | 38.6
117 | -41 | 28 | 34.1 | 33.8 | 38.5
118 | -40 | 28 | 34.1 | 33.8 | 38.5
119 | -39 | 28 | 34.1 | 33.8 | 38.5
120 | -38 | 28 | 34.1 | 33.8 | 38.5
121 | -37 | 28 | 34.1 | 33.8 | 38.5
122 | -36 | 28 | 34.1 | 33.8 | 38.5
123 | -35 | 28 | 34.1 | 33.8 | 38.5
124 | -34 | 28 | 34.1 | 33.8 | 38.5
125 | -33 | 28 | 34.1 | 33.8 | 38.5
126 | -32 | 28 | 34.1 | 33.8 | 38.5
127 | -31 | 28 | 34.1 | 33.8 | 38.5
128 | -30 | 28 | 34.1 | 33.8 | 38.5
129 | -29 | 28 | 34.1 | 33.8 | 38.5
130 | -28 | 28 | 34.1 | 33.8 | 38.5
131 | -27 | 28 | 34.1 | 33.8 | 38.5
132 | -26 | 28 | 34.1 | 33.8 | 38.5
133 | -25 | 28 | 34.1 | 33.7 | 38.5
134 | -24 | 28 | 34.1 | 33.7 | 38.5
135 | -23 | 28 | 34.1 | 33.7 | 38.5
136 | -22 | 28 | 34 | 33.7 | 38.5
137 | -21 | 28 | 34 | 33.7 | 38.5
138 | -20 | 28 | 34 | 33.7 | 38.4
139 | -19 | 28 | 34 | 33.7 | 38.4
140 | -18 | 28 | 34 | 33.7 | 38.4
141 | -17 | 27.9 | 34 | 33.7 | 38.4
142 | -16 | 27.9 | 34 | 33.7 | 38.4
143 | -15 | 27.9 | 34 | 33.7 | 38.4
144 | -14 | 27.9 | 34 | 33.7 | 38.4
145 | -13 | 27.9 | 34 | 33.7 | 38.4
146 | -12 | 27.9 | 34 | 33.7 | 38.4
147 | -11 | 27.9 | 34 | 33.7 | 38.4
148 | -10 | 27.9 | 34 | 33.7 | 38.4
149 | -9 | 27.9 | 34 | 33.7 | 38.4
150 | -8 | 27.9 | 34 | 33.7 | 38.4
151 | -7 | 27.9 | 34 | 33.7 | 38.4
152 | -6 | 27.9 | 34 | 33.7 | 38.4
153 | -5 | 27.9 | 34 | 33.6 | 38.7
154 | -4 | 27.8 | 34.2 | 33.3 | 40
155 | -3 | 27.8 | 34.2 | 33.2 | 40.3
156 | -2 | 28 | 34.2 | 33.2 | 40.4
157 | -1 | 28.7 | 34.2 | 33.2 | 40.4
158 | 0 | 29.9 | 34.1 | 33.2 | 40.4
159 | 1 | 31.7 | 34.1 | 33.3 | 40.4
160 | 2 | 33.8 | 34.1 | 33.2 | 40.4
161 | 3 | 36.4 | 34.2 | 33.3 | 40.5
162 | 4 | 39.4 | 34.2 | 33.3 | 40.5
163 | 5 | 42.7 | 34.2 | 33.3 | 40.5
164 | 6 | 46.2 | 34.2 | 33.3 | 40.5
165 | 7 | 50 | 34.2 | 33.3 | 40.6
166 | 8 | 54 | 34.3 | 33.4 | 40.6
167 | 9 | 58.2 | 34.3 | 33.4 | 40.7
168 | 10 | 62.7 | 34.4 | 33.5 | 40.7
169 | 11 | 67.3 | 34.4 | 33.5 | 40.8
170 | 12 | 72 | 34.5 | 33.6 | 40.9
171 | 13 | 76.9 | 34.6 | 33.7 | 40.9
172 | 14 | 82 | 34.6 | 33.7 | 41
173 | 15 | 87.1 | 34.7 | 33.8 | 41.1
174 | 16 | 92.3 | 34.9 | 33.9 | 41.2
175 | 17 | 97.7 | 35 | 34.1 | 41.4
176 | 18 | 103.1 | 35.1 | 34.2 | 41.6
177 | 19 | 108.6 | 35.3 | 34.3 | 41.8
178 | 20 | 114.2 | 35.5 | 34.5 | 41.9
179 | 21 | 119.9 | 35.7 | 34.7 | 42.1
180 | 22 | 125.6 | 35.9 | 34.9 | 42.3
181 | 23 | 131.5 | 36.1 | 35.1 | 42.5
182 | 24 | 137.4 | 36.3 | 35.3 | 42.8
183 | 25 | 143.3 | 36.6 | 35.6 | 43
184 | 26 | 149.2 | 36.9 | 35.8 | 43.3
185 | 27 | 155 | 37.1 | 36.1 | 43.6
186 | 28 | 160.7 | 37.5 | 36.4 | 43.9
187 | 29 | 166.6 | 37.8 | 36.7 | 44.3
188 | 30 | 172.4 | 38.1 | 37.1 | 44.7
189 | 31 | 178.3 | 38.5 | 37.4 | 45
190 | 32 | 184.2 | 38.9 | 37.8 | 45.3
191 | 33 | 190.2 | 39.3 | 38.2 | 45.7
192 | 34 | 196.1 | 39.8 | 38.6 | 46.2
193 | 35 | 202 | 40.2 | 39.1 | 46.6
194 | 36 | 207.9 | 40.7 | 39.6 | 47.1
195 | 37 | 213.8 | 41.2 | 40.1 | 47.6
196 | 38 | 219.8 | 41.8 | 40.6 | 48.1
197 | 39 | 225.7 | 42.3 | 41.1 | 48.7
198 | 40 | 231.6 | 42.9 | 41.7 | 49.3
199 | 41 | 237.4 | 43.5 | 42.3 | 49.9
200 | 42 | 243.2 | 44.1 | 42.9 | 50.6
201 | 43 | 249 | 44.8 | 43.5 | 51.2
202 | 44 | 254.8 | 45.5 | 44.2 | 51.9
203 | 45 | 260.7 | 46.2 | 44.8 | 52.6
204 | 46 | 266.5 | 46.9 | 45.5 | 53.4
205 | 47 | 272.2 | 47.6 | 46.2 | 54.1
206 | 48 | 278 | 48.4 | 47 | 54.9
207 | 49 | 283.9 | 49.1 | 47.7 | 55.8
208 | 50 | 289.6 | 49.9 | 48.5 | 56.4
209 | 51 | 295.4 | 50.8 | 49.3 | 57.4
210 | 52 | 301 | 51.6 | 50.1 | 58.4
211 | 53 | 306.2 | 52.5 | 51 | 59.3
212 | 54 | 311 | 53.4 | 51.9 | 60.2
213 | 55 | 315.5 | 54.3 | 52.8 | 61.2
214 | 56 | 319.6 | 55.3 | 53.7 | 62.3
215 | 57 | 323.6 | 56.2 | 54.7 | 63.3
216 | 58 | 327.4 | 57.2 | 55.7 | 64.4
217 | 59 | 331 | 58.2 | 56.7 | 65.3
218 | 60 | 334.6 | 59.2 | 57.8 | 66.2
219 | 61 | 337.8 | 60.3 | 59 | 66.6
220 | 62 | 340.5 | 61.3 | 60.1 | 67.7
221 | 63 | 343.1 | 62.4 | 61.3 | 68.5
222 | 64 | 345.3 | 63.4 | 62.5 | 69.6
223 | 65 | 347.1 | 64.5 | 63.7 | 70.6
224 | 66 | 348.8 | 65.6 | 65 | 71.6
225 | 67 | 350.3 | 66.7 | 66.2 | 72.7
226 | 68 | 351.5 | 67.8 | 67.3 | 73.9
227 | 69 | 352.4 | 69 | 68.6 | 75.1
228 | 70 | 353.2 | 70.1 | 69.7 | 76.1
229 | 71 | 354 | 71.2 | 70.9 | 77.2
230 | 72 | 354.5 | 72.3 | 72.1 | 78.4
231 | 73 | 354.7 | 73.4 | 73.3 | 79.4
232 | 74 | 354.9 | 74.4 | 74.5 | 80.5
233 | 75 | 355 | 75.5 | 75.6 | 81.5
234 | 76 | 355 | 76.5 | 76.8 | 82.6
235 | 77 | 355 | 77.6 | 77.9 | 83.8
236 | 78 | 355 | 78.6 | 79.1 | 84.9
237 | 79 | 355 | 79.6 | 80.2 | 85.9
238 | 80 | 354.8 | 80.7 | 81.3 | 87.1
239 | 81 | 354.7 | 81.6 | 82.4 | 88.2
240 | 82 | 354.6 | 82.6 | 83.5 | 89.2
241 | 83 | 354.3 | 83.6 | 84.6 | 90.4
242 | 84 | 354.1 | 84.6 | 85.7 | 91.4
243 | 85 | 353.9 | 85.5 | 86.7 | 92.5
244 | 86 | 353.5 | 86.4 | 87.8 | 93.6
245 | 87 | 353.1 | 87.4 | 88.8 | 94.7
246 | 88 | 352.7 | 88.3 | 89.8 | 95.8
247 | 89 | 352.3 | 89.2 | 90.8 | 96.8
248 | 90 | 351.9 | 90.1 | 91.9 | 97.9
249 | 91 | 351.4 | 91 | 92.9 | 98.9
250 | 92 | 351 | 91.9 | 93.8 | 99.9
251 | 93 | 350.6 | 92.8 | 94.8 | 101
252 | 94 | 350.1 | 93.6 | 95.8 | 102
253 | 95 | 349.5 | 94.5 | 96.8 | 102.9
254 | 96 | 348.8 | 95.3 | 97.7 | 104
255 | 97 | 348.2 | 96.2 | 98.6 | 105
256 | 98 | 347.6 | 97 | 99.6 | 105.9
257 | 99 | 346.8 | 97.8 | 100.5 | 106.9
258 | 100 | 346.1 | 98.7 | 101.4 | 107.9
259 | 101 | 345.5 | 99.5 | 102.3 | 108.8
260 | 102 | 344.9 | 100.3 | 103.1 | 109.8
261 | 103 | 344.3 | 101.1 | 104 | 110.8
262 | 104 | 343.8 | 101.9 | 104.9 | 111.7
263 | 105 | 343.2 | 102.6 | 105.7 | 112.6
264 | 106 | 342.6 | 103.4 | 106.6 | 113.6
265 | 107 | 341.9 | 104.2 | 107.4 | 114.6
266 | 108 | 341.3 | 104.9 | 108.2 | 115.4
267 | 109 | 340.8 | 105.7 | 109 | 116.4
268 | 110 | 340.2 | 106.4 | 109.8 | 117.3
269 | 111 | 339.6 | 107.2 | 110.6 | 118.2
270 | 112 | 339 | 107.9 | 111.4 | 119.1
271 | 113 | 338.5 | 108.6 | 112.2 | 120
272 | 114 | 338 | 109.3 | 112.9 | 120.8
273 | 115 | 337.5 | 110.1 | 113.7 | 121.7
274 | 116 | 337 | 110.8 | 114.4 | 122.6
275 | 117 | 336.4 | 111.5 | 115.2 | 123.5
276 | 118 | 335.7 | 112.2 | 115.9 | 124.3
277 | 119 | 335 | 112.9 | 116.6 | 125.1
278 | 120 | 334.3 | 113.6 | 117.4 | 126
279 | 121 | 333.7 | 114.2 | 118.1 | 126.8
280 | 122 | 333.1 | 114.9 | 118.8 | 127.6
281 | 123 | 332.4 | 115.6 | 119.5 | 128.4
282 | 124 | 331.8 | 116.3 | 120.2 | 129.2
283 | 125 | 331.2 | 116.9 | 120.9 | 130
284 | 126 | 330.6 | 117.6 | 121.5 | 130.8
285 | 127 | 330.1 | 118.2 | 122.2 | 131.6
286 | 128 | 329.6 | 118.8 | 122.9 | 132.4
287 | 129 | 329 | 119.5 | 123.5 | 133.2
288 | 130 | 328.4 | 120.1 | 124.2 | 134
289 | 131 | 327.8 | 120.7 | 124.8 | 134.7
290 | 132 | 327.2 | 121.4 | 125.3 | 135.6
291 | 133 | 326.6 | 122 | 126 | 136.4
292 | 134 | 326 | 122.6 | 126.6 | 137.2
293 | 135 | 325.5 | 123.2 | 127.2 | 137.9
294 | 136 | 325 | 123.7 | 127.8 | 138.7
295 | 137 | 324.5 | 124.3 | 128.4 | 139.4
296 | 138 | 324 | 124.9 | 129 | 140.1
297 | 139 | 323.4 | 125.5 | 129.6 | 140.9
298 | 140 | 322.9 | 126 | 130.2 | 141.8
299 | 141 | 322.3 | 126.6 | 130.7 | 142.8
300 | 142 | 321.8 | 127.1 | 131.3 | 143.4
301 | 143 | 321.2 | 127.7 | 131.9 | 144
302 | 144 | 320.7 | 128.2 | 132.4 | 144.7
303 | 145 | 320.3 | 128.7 | 133 | 145.4
304 | 146 | 319.9 | 129.3 | 133.5 | 146.2
305 | 147 | 319.6 | 129.8 | 134.1 | 147.1
306 | 148 | 319.3 | 130.4 | 134.5 | 148
307 | 149 | 319.1 | 130.9 | 135.1 | 148.8
308 | 150 | 319 | 131.4 | 135.7 | 149
309 | 151 | 319 | 131.9 | 136.3 | 149.3
310 | 152 | 319.1 | 132.4 | 136.8 | 149.9
311 | 153 | 319.2 | 132.9 | 137.3 | 150.6
312 | 154 | 319.3 | 133.4 | 137.9 | 151.3
313 | 155 | 319.4 | 133.9 | 138.4 | 151.9
314 | 156 | 319.5 | 134.4 | 138.9 | 152.6
315 | 157 | 319.7 | 134.9 | 139.4 | 153.3
316 | 158 | 320 | 135.5 | 139.9 | 153.9
317 | 159 | 320.4 | 135.9 | 140.4 | 154.6
318 | 160 | 320.7 | 136.4 | 140.9 | 155.2
319 | 161 | 321 | 136.9 | 141.5 | 155.9
320 | 162 | 321.3 | 137.5 | 142 | 156.6
321 | 163 | 321.8 | 137.9 | 142.5 | 157.2
322 | 164 | 322.2 | 138.4 | 143 | 157.8
323 | 165 | 322.6 | 139 | 143.5 | 158.4
324 | 166 | 323 | 139.4 | 144 | 159.1
325 | 167 | 323.5 | 139.9 | 144.6 | 159.8
326 | 168 | 324 | 140.4 | 145.1 | 160.4
327 | 169 | 324.5 | 140.9 | 145.6 | 161
328 | 170 | 325 | 141.4 | 146.1 | 161.7
329 | 171 | 325.5 | 141.8 | 146.7 | 162.3
330 | 172 | 326 | 142.3 | 147.2 | 162.9
331 | 173 | 326.5 | 142.8 | 147.7 | 163.5
332 | 174 | 326.9 | 143.2 | 148.3 | 164
333 | 175 | 327.5 | 143.7 | 148.8 | 164.5
334 | 176 | 328 | 144.2 | 149.4 | 165.1
335 | 177 | 328.5 | 144.7 | 149.9 | 165.6
336 | 178 | 328.9 | 145.2 | 150.4 | 166.2
337 | 179 | 329.3 | 145.7 | 150.9 | 166.9
338 | 180 | 329.7 | 146.2 | 151.5 | 167.5
339 | 181 | 330 | 146.7 | 152 | 168.2
340 | 182 | 330.2 | 147.2 | 152.5 | 168.8
341 | 183 | 330.4 | 147.8 | 153 | 169.5
342 | 184 | 330.5 | 148.3 | 153.5 | 170.1
343 | 185 | 330.8 | 148.8 | 154 | 170.8
344 | 186 | 330.9 | 149.3 | 154.5 | 171.4
345 | 187 | 330.9 | 149.8 | 155.1 | 172.1
346 | 188 | 331 | 150.4 | 155.6 | 172.7
347 | 189 | 331 | 150.9 | 156.1 | 173.3
348 | 190 | 331.1 | 151.4 | 156.6 | 173.9
349 | 191 | 331.1 | 151.9 | 157.1 | 174.5
350 | 192 | 331.1 | 152.4 | 157.6 | 175.2
351 | 193 | 331.1 | 152.9 | 158.1 | 175.8
352 | 194 | 331 | 153.4 | 158.5 | 176.3
353 | 195 | 330.9 | 153.8 | 159.1 | 177
354 | 196 | 330.8 | 154.3 | 159.5 | 177.6
355 | 197 | 330.7 | 154.8 | 160 | 178.2
356 | 198 | 330.6 | 155.3 | 160.5 | 178.8
357 | 199 | 330.6 | 155.7 | 160.9 | 179.4
358 | 200 | 330.5 | 156.2 | 161.4 | 180
359 | 201 | 330.5 | 156.7 | 161.8 | 180.5
360 | 202 | 330.3 | 157.1 | 162.3 | 181.1
361 | 203 | 330.2 | 157.6 | 162.8 | 181.7
362 | 204 | 330 | 158.1 | 163.2 | 182.3
363 | 205 | 329.9 | 158.5 | 163.6 | 182.8
364 | 206 | 329.7 | 159 | 164.1 | 183.4
365 | 207 | 329.4 | 159.5 | 164.5 | 183.9
366 | 208 | 329.3 | 160 | 164.9 | 184.4
367 | 209 | 329.1 | 160.4 | 165.4 | 185
368 | 210 | 329 | 160.9 | 165.8 | 185.5
369 | 211 | 329 | 161.4 | 166.2 | 186.1
370 | 212 | 328.9 | 161.9 | 166.6 | 186.6
371 | 213 | 328.7 | 162.3 | 167.1 | 187.2
372 | 214 | 328.5 | 162.8 | 167.5 | 187.7
373 | 215 | 328.4 | 163.3 | 167.9 | 188.2
374 | 216 | 328.4 | 163.8 | 168.3 | 188.8
375 | 217 | 328.3 | 164.2 | 168.7 | 189.4
376 | 218 | 328.3 | 164.7 | 169.1 | 189.9
377 | 219 | 328.2 | 165.2 | 169.5 | 190.5
378 | 220 | 328.2 | 165.6 | 169.9 | 191
379 | 221 | 328.3 | 166.1 | 170.3 | 191.5
380 | 222 | 328.3 | 166.5 | 170.7 | 192
381 | 223 | 328.3 | 167 | 171.1 | 192.6
382 | 224 | 328.3 | 167.4 | 171.5 | 193.1
383 | 225 | 328.2 | 167.8 | 171.8 | 193.6
384 | 226 | 328.1 | 168.2 | 172.2 | 194.1
385 | 227 | 328.1 | 168.6 | 172.6 | 194.6
386 | 228 | 328.1 | 169 | 173 | 195.1
387 | 229 | 328.1 | 169.4 | 173.4 | 195.6
388 | 230 | 328.2 | 169.8 | 173.8 | 196.1
389 | 231 | 328.2 | 170.2 | 174.2 | 196.6
390 | 232 | 328.1 | 170.6 | 174.5 | 197.2
391 | 233 | 328.1 | 171 | 175 | 197.7
392 | 234 | 328.1 | 171.4 | 175.3 | 198.1
393 | 235 | 328.1 | 171.7 | 175.7 | 198.6
394 | 236 | 328.2 | 172.1 | 176.1 | 199.1
395 | 237 | 328.2 | 172.5 | 176.5 | 199.5
396 | 238 | 328.2 | 172.9 | 176.9 | 200
397 | 239 | 328.2 | 173.3 | 177.3 | 200.5
398 | 240 | 328.2 | 173.6 | 177.7 | 201
399 | 241 | 328.2 | 174 | 178.1 | 201.5
400 | 242 | 328.3 | 174.4 | 178.4 | 201.9
401 | 243 | 328.4 | 174.8 | 178.8 | 202.4
402 | 244 | 328.5 | 175.1 | 179.2 | 202.9
403 | 245 | 328.7 | 175.5 | 179.6 | 203.3
404 | 246 | 328.8 | 175.9 | 180 | 203.8
405 | 247 | 328.9 | 176.2 | 180.4 | 204.3
406 | 248 | 328.9 | 176.6 | 180.8 | 204.7
407 | 249 | 328.9 | 177 | 181.2 | 205.1
408 | 250 | 329 | 177.4 | 181.5 | 205.6
409 | 251 | 329 | 177.7 | 181.9 | 206
410 | 252 | 329 | 178.1 | 182.3 | 206.5
411 | 253 | 329.2 | 178.5 | 182.7 | 206.9
412 | 254 | 329.3 | 178.8 | 183.1 | 207.4
413 | 255 | 329.5 | 179.2 | 183.5 | 207.9
414 | 256 | 329.5 | 179.5 | 183.9 | 208.3
415 | 257 | 329.6 | 179.9 | 184.3 | 208.7
416 | 258 | 329.6 | 180.3 | 184.6 | 209.2
417 | 259 | 329.7 | 180.6 | 185 | 209.6
418 | 260 | 329.7 | 181 | 185.4 | 210
419 | 261 | 329.8 | 181.3 | 185.8 | 210.5
420 | 262 | 329.8 | 181.7 | 186.2 | 210.9
421 | 263 | 329.7 | 182.1 | 186.6 | 211.3
422 | 264 | 329.6 | 182.4 | 186.9 | 211.7
423 | 265 | 329.5 | 182.8 | 187.3 | 212.1
424 | 266 | 329.4 | 183.1 | 187.7 | 212.6
425 | 267 | 329.4 | 183.5 | 188.1 | 213
426 | 268 | 329.4 | 183.8 | 188.5 | 213.4
427 | 269 | 329.4 | 184.2 | 188.9 | 213.8
428 | 270 | 329.4 | 184.5 | 189.2 | 214.2
429 | 271 | 329.4 | 184.9 | 189.6 | 214.6
430 | 272 | 329.3 | 185.2 | 190 | 215
431 | 273 | 329.2 | 185.6 | 190.4 | 215.3
432 | 274 | 329.1 | 185.9 | 190.7 | 215.7
433 | 275 | 329 | 186.3 | 191.1 | 216.1
434 | 276 | 329 | 186.7 | 191.5 | 216.5
435 | 277 | 329 | 187 | 191.9 | 216.9
436 | 278 | 328.8 | 187.4 | 192.3 | 217.3
437 | 279 | 328.7 | 187.7 | 192.6 | 217.6
438 | 280 | 328.7 | 188.1 | 193 | 218
439 | 281 | 328.6 | 188.4 | 193.4 | 218.4
440 | 282 | 328.5 | 188.8 | 193.7 | 218.8
441 | 283 | 328.5 | 189.1 | 194.1 | 219.2
442 | 284 | 328.4 | 189.4 | 194.5 | 219.5
443 | 285 | 328.3 | 189.8 | 194.8 | 219.9
444 | 286 | 328.3 | 190.1 | 195.2 | 220.3
445 | 287 | 328.2 | 190.5 | 195.6 | 220.7
446 | 288 | 328.1 | 190.8 | 195.9 | 221
447 | 289 | 328.1 | 191.1 | 196.3 | 221.4
448 | 290 | 328 | 191.5 | 196.6 | 221.7
449 | 291 | 328.1 | 191.8 | 197 | 222.1
450 | 292 | 328.1 | 192.1 | 197.3 | 222.4
451 | 293 | 328.1 | 192.4 | 197.7 | 222.8
452 | 294 | 328.2 | 192.8 | 198 | 223.2
453 | 295 | 328.2 | 193.1 | 198.3 | 223.5
454 | 296 | 328.1 | 193.4 | 198.7 | 223.9
455 | 297 | 328.1 | 193.7 | 199 | 224.2
456 | 298 | 328 | 194 | 199.3 | 224.5
457 | 299 | 327.9 | 194.4 | 199.6 | 224.9
458 | 300 | 327.8 | 194.7 | 200 | 225.3
459 | 301 | 327.7 | 195 | 200.3 | 225.6
460 | 302 | 327.8 | 195.3 | 200.6 | 226
461 | 303 | 327.9 | 195.6 | 200.9 | 226.3
462 | 304 | 328 | 195.9 | 201.2 | 226.7
463 | 305 | 328.1 | 196.3 | 201.5 | 227
464 | 306 | 328.1 | 196.6 | 201.8 | 227.3
465 | 307 | 328.2 | 196.9 | 202.1 | 227.7
466 | 308 | 328.3 | 197.3 | 202.4 | 228
467 | 309 | 328.3 | 197.6 | 202.7 | 228.3
468 | 310 | 328.4 | 197.9 | 202.9 | 228.7
469 | 311 | 328.4 | 198.3 | 203.2 | 229
470 | 312 | 328.5 | 198.6 | 203.5 | 229.4
471 | 313 | 328.6 | 199 | 203.8 | 229.7
472 | 314 | 328.6 | 199.3 | 204 | 230
473 | 315 | 328.6 | 199.7 | 204.3 | 230.3
474 | 316 | 328.6 | 200 | 204.6 | 230.6
475 | 317 | 328.5 | 200.3 | 204.8 | 230.9
476 | 318 | 328.5 | 200.7 | 205.1 | 231.2
477 | 319 | 328.5 | 201 | 205.3 | 231.5
478 | 320 | 328.5 | 201.4 | 205.6 | 231.8
479 | 321 | 328.4 | 201.7 | 205.8 | 232.1
480 | 322 | 328.4 | 202 | 206 | 232.4
481 | 323 | 328.4 | 202.3 | 206.2 | 232.6
482 | 324 | 328.4 | 202.7 | 206.5 | 232.9
483 | 325 | 328.3 | 203 | 206.7 | 233.2
484 | 326 | 328.2 | 203.3 | 206.9 | 233.5
485 | 327 | 328.1 | 203.6 | 207.1 | 233.7
486 | 328 | 328 | 203.9 | 207.3 | 234
487 | 329 | 327.9 | 204.2 | 207.6 | 234.3
488 | 330 | 327.8 | 204.6 | 207.8 | 234.5
489 | 331 | 327.8 | 204.9 | 208 | 234.8
490 | 332 | 327.7 | 205.2 | 208.2 | 235.1
491 | 333 | 327.7 | 205.5 | 208.4 | 235.3 | Time of first failure
492 | 334 | 327.6 | 205.8 | 208.6 | 235.6 | 333 | 0
493 | 335 | 327.5 | 206.1 | 208.8 | 235.8 | 333 | 900
494 | 336 | 327.5 | 206.3 | 209.1 | 236.1
495 | 337 | 327.5 | 206.7 | 209.3 | 236.4
496 | 338 | 327.6 | 207 | 209.5 | 236.6
497 | 339 | 327.7 | 207.3 | 209.7 | 236.9
498 | 340 | 327.8 | 207.6 | 209.9 | 237.1
499 | 341 | 327.9 | 207.9 | 210.2 | 237.4
500 | 342 | 328 | 208.2 | 210.4 | 237.6
501 | 343 | 328.1 | 208.4 | 210.6 | 237.9
502 | 344 | 328.2 | 208.7 | 210.9 | 238.1
503 | 345 | 328.3 | 209 | 211.1 | 238.4
504 | 346 | 328.4 | 209.3 | 211.4 | 238.6
505 | 347 | 328.4 | 209.6 | 211.6 | 238.9
506 | 348 | 328.4 | 209.9 | 211.9 | 239.1
507 | 349 | 328.5 | 210.1 | 212.1 | 239.3
508 | 350 | 328.6 | 210.4 | 212.4 | 239.6
509 | 351 | 328.7 | 210.7 | 212.7 | 239.8
510 | 352 | 328.8 | 210.9 | 212.9 | 240.1
511 | 353 | 328.9 | 211.2 | 213.2 | 240.3
512 | 354 | 328.9 | 211.5 | 213.5 | 240.5
513 | 355 | 329 | 211.8 | 213.8 | 240.8
514 | 356 | 329.1 | 212.1 | 214.2 | 241
515 | 357 | 329.2 | 212.3 | 214.6 | 241.2
516 | 358 | 329.2 | 212.6 | 215 | 241.5
517 | 359 | 329.4 | 212.9 | 215.4 | 241.8
518 | 360 | 329.6 | 213.2 | 215.7 | 242.1
519 | 361 | 329.7 | 213.5 | 216 | 242.3
520 | 362 | 329.7 | 213.8 | 216.2 | 242.6
521 | 363 | 329.8 | 214.1 | 216.5 | 242.9
522 | 364 | 329.9 | 214.4 | 216.7 | 243.1
523 | 365 | 329.9 | 214.7 | 216.9 | 243.4
524 | 366 | 330 | 215 | 217.1 | 243.6
525 | 367 | 330 | 215.2 | 217.3 | 243.8
526 | 368 | 330 | 215.5 | 217.5 | 244.1
527 | 369 | 329.9 | 215.7 | 217.7 | 244.3
528 | 370 | 329.8 | 216 | 217.9 | 244.5
529 | 371 | 329.8 | 216.2 | 218.1 | 244.8
530 | 372 | 329.8 | 216.5 | 218.3 | 245
531 | 373 | 329.8 | 216.7 | 218.4 | 245.2
532 | 374 | 329.8 | 216.9 | 218.7 | 245.4
533 | 375 | 329.7 | 217.2 | 219 | 245.6
534 | 376 | 329.6 | 217.4 | 219.3 | 245.8
535 | 377 | 329.6 | 217.6 | 219.6 | 246
536 | 378 | 329.6 | 217.8 | 219.8 | 246.2
537 | 379 | 329.5 | 218 | 220.1 | 246.5
538 | 380 | 329.5 | 218.2 | 220.4 | 246.7
539 | 381 | 329.4 | 218.4 | 220.6 | 246.9
540 | 382 | 329.3 | 218.5 | 220.9 | 247.1
541 | 383 | 329.2 | 218.7 | 221.2 | 247.3
542 | 384 | 329.1 | 218.9 | 221.4 | 247.5
543 | 385 | 329.1 | 219.1 | 221.6 | 247.8
544 | 386 | 329.1 | 219.2 | 221.9 | 247.9
545 | 387 | 329.1 | 219.4 | 222.2 | 248.2
546 | 388 | 329.1 | 219.5 | 222.5 | 248.4
547 | 389 | 329 | 219.6 | 222.8 | 248.5
548 | 390 | 328.9 | 219.9 | 223.1 | 248.7
549 | 391 | 328.9 | 220.2 | 223.3 | 249
550 | 392 | 328.7 | 220.3 | 223.6 | 249.2
551 | 393 | 328.5 | 220.6 | 223.7 | 249.7
552 | 394 | 328.3 | 220.5 | 224 | 249.9
553 | 395 | 328.2 | 220.6 | 224.2 | 250.2
554 | 396 | 328.1 | 220.9 | 224.5 | 250.2
555 | 397 | 327.9 | 221 | 224.8 | 250.4
556 | 398 | 327.9 | 221.2 | 225 | 250.6
557 | 399 | 327.7 | 221.4 | 225.3 | 250.7
558 | 400 | 327.7 | 221.6 | 225.6 | 250.9
559 | 401 | 327.7 | 221.8 | 225.8 | 251.1
560 | 402 | 327.6 | 222 | 226.1 | 251.3
561 | 403 | 327.6 | 222 | 226.3 | 251.4
562 | 404 | 327.7 | 222.1 | 226.6 | 251.5
563 | 405 | 327.7 | 222.2 | 226.8 | 251.7
564 | 406 | 327.7 | 222.3 | 227 | 251.9
565 | 407 | 327.6 | 222.2 | 227.3 | 251.9
566 | 408 | 327.6 | 222.2 | 227.6 | 252.2
567 | 409 | 327.6 | 222.6 | 227.8 | 252.3
568 | 410 | 327.6 | 222.7 | 228 | 252.4
569 | 411 | 327.6 | 222.7 | 228.3 | 252.6
570 | 412 | 327.5 | 222.9 | 228.5 | 252.8
571 | 413 | 327.6 | 223.1 | 228.7 | 252.9
572 | 414 | 327.7 | 223.2 | 228.9 | 253
573 | 415 | 327.7 | 223.4 | 229.1 | 253.2
574 | 416 | 327.8 | 223.5 | 229.3 | 253.4
575 | 417 | 327.9 | 223.6 | 229.5 | 253.5
576 | 418 | 327.9 | 223.8 | 229.7 | 253.7
577 | 419 | 328 | 224 | 229.9 | 253.8
578 | 420 | 328.1 | 224.2 | 230 | 254
579 | 421 | 328.2 | 224.3 | 230.2 | 254.1
580 | 422 | 328.3 | 224.5 | 230.3 | 254.3
581 | 423 | 328.4 | 224.6 | 230.4 | 254.5
582 | 424 | 328.4 | 224.7 | 230.5 | 254.6
583 | 425 | 328.5 | 224.9 | 230.6 | 254.7
584 | 426 | 328.5 | 225.2 | 230.7 | 255
585 | 427 | 328.6 | 225.4 | 230.9 | 255.1
586 | 428 | 328.6 | 225.5 | 231 | 255.2
587 | 429 | 328.7 | 225.7 | 231.2 | 255.5
588 | 430 | 328.7 | 225.9 | 231.3 | 255.6
589 | 431 | 328.8 | 226.1 | 231.5 | 255.7
590 | 432 | 328.8 | 226.3 | 231.7 | 255.8
591 | 433 | 328.7 | 226.5 | 231.8 | 256.1
592 | 434 | 328.7 | 226.6 | 232 | 256.2
593 | 435 | 328.7 | 226.8 | 232.2 | 256.2
594 | 436 | 328.7 | 227.1 | 232.3 | 256.5
595 | 437 | 328.7 | 227.3 | 232.5 | 256.7
596 | 438 | 328.6 | 227.5 | 232.7 | 256.7
597 | 439 | 328.6 | 227.8 | 232.8 | 256.8
598 | 440 | 328.7 | 228 | 233 | 257.1
599 | 441 | 328.7 | 228.3 | 233.1 | 257.2
600 | 442 | 328.7 | 228.5 | 233.3 | 257.2
601 | 443 | 328.7 | 228.8 | 233.4 | 257.5
602 | 444 | 328.6 | 228.9 | 233.6 | 257.7
603 | 445 | 328.6 | 229.2 | 233.7 | 257.6
604 | 446 | 328.6 | 229.4 | 233.9 | 257.8
605 | 447 | 328.6 | 229.7 | 234 | 258.1
606 | 448 | 328.6 | 230 | 234.1 | 258.2
607 | 449 | 328.7 | 230.2 | 234.3 | 258.2
608 | 450 | 328.7 | 230.5 | 234.4 | 258.5
609 | 451 | 328.7 | 230.8 | 234.6 | 258.6
610 | 452 | 328.6 | 231 | 234.8 | 258.7
611 | 453 | 328.6 | 231.2 | 234.9 | 258.8
612 | 454 | 328.5 | 231.5 | 235.1 | 259
613 | 455 | 328.4 | 231.8 | 235.2 | 259.1
614 | 456 | 328.3 | 232 | 235.4 | 259.1
615 | 457 | 328.2 | 232.2 | 235.6 | 259.3
616 | 458 | 328.2 | 232.5 | 235.7 | 259.5
617 | 459 | 328.1 | 232.7 | 235.9 | 259.6
618 | 460 | 328 | 233 | 236.1 | 259.7
619 | 461 | 328 | 233.2 | 236.2 | 259.9
620 | 462 | 327.9 | 233.5 | 236.4 | 260.1
621 | 463 | 327.9 | 233.7 | 236.6 | 260.1
622 | 464 | 327.8 | 234 | 236.7 | 260.3
623 | 465 | 327.8 | 234.2 | 236.9 | 260.5
624 | 466 | 327.7 | 234.4 | 237.1 | 260.5
625 | 467 | 327.7 | 234.7 | 237.3 | 260.6
626 | 468 | 327.7 | 234.9 | 237.4 | 260.8
627 | 469 | 327.7 | 235.2 | 237.6 | 260.9
628 | 470 | 327.7 | 235.4 | 237.8 | 260.9
629 | 471 | 327.8 | 235.7 | 238 | 261.2
630 | 472 | 327.9 | 235.9 | 238.1 | 261.4
631 | 473 | 327.9 | 236.1 | 238.3 | 261.4
632 | 474 | 327.9 | 236.4 | 238.5 | 261.5
633 | 475 | 327.9 | 236.7 | 238.7 | 261.8
634 | 476 | 327.9 | 236.9 | 238.9 | 261.9
635 | 477 | 327.9 | 237.1 | 239.1 | 261.9
636 | 478 | 327.9 | 237.4 | 239.2 | 262.2
637 | 479 | 328 | 237.6 | 239.4 | 262.3
638 | 480 | 328.1 | 237.9 | 239.6 | 262.4
639 | 481 | 328.1 | 238.1 | 239.8 | 262.5
640 | 482 | 328.1 | 238.4 | 239.9 | 262.8
641 | 483 | 328 | 238.6 | 240.1 | 262.9
642 | 484 | 328 | 238.8 | 240.3 | 262.9
643 | 485 | 328 | 239.1 | 240.5 | 263.1
644 | 486 | 328 | 239.3 | 240.7 | 263.3
645 | 487 | 328 | 239.5 | 240.9 | 263.3
646 | 488 | 327.9 | 239.7 | 241.1 | 263.4
647 | 489 | 327.9 | 240 | 241.2 | 263.7
648 | 490 | 327.8 | 240.2 | 241.4 | 263.8
649 | 491 | 327.8 | 240.4 | 241.6 | 263.8
650 | 492 | 327.9 | 240.7 | 241.8 | 264
651 | 493 | 328 | 240.9 | 242 | 264.2
652 | 494 | 328 | 241.2 | 242.2 | 264.3
653 | 495 | 328 | 241.4 | 242.4 | 264.4
654 | 496 | 328 | 241.7 | 242.6 | 264.6
655 | 497 | 328 | 241.9 | 242.8 | 264.6
656 | 498 | 328 | 242.1 | 243 | 264.7
657 | 499 | 328.1 | 242.3 | 243.2 | 264.8
658 | 500 | 328.1 | 242.6 | 243.3 | 265
659 | 501 | 328.2 | 242.9 | 243.5 | 265.2
660 | 502 | 328.3 | 243.1 | 243.7 | 265.3
661 | 503 | 328.3 | 243.4 | 243.9 | 265.6
662 | 504 | 328.4 | 243.6 | 244.1 | 265.6
663 | 505 | 328.4 | 243.8 | 244.3 | 265.7
664 | 506 | 328.5 | 244 | 244.5 | 265.8
665 | 507 | 328.5 | 244.3 | 244.6 | 266
666 | 508 | 328.5 | 244.5 | 244.9 | 266.1
667 | 509 | 328.6 | 244.8 | 245.1 | 266.2
668 | 510 | 328.5 | 245 | 245.2 | 266.5
669 | 511 | 328.5 | 245.3 | 245.4 | 266.6
670 | 512 | 328.5 | 245.5 | 245.6 | 266.7
671 | 513 | 328.6 | 245.7 | 245.9 | 266.7
672 | 514 | 328.6 | 246 | 246 | 267
673 | 515 | 328.6 | 246.2 | 246.2 | 267.1
674 | 516 | 328.4 | 246.5 | 246.4 | 267.2
675 | 517 | 328.4 | 246.8 | 246.6 | 267.5
676 | 518 | 328.4 | 247 | 246.8 | 267.6
677 | 519 | 328.3 | 247.2 | 247 | 267.6
678 | 520 | 328.2 | 247.5 | 247.2 | 267.9
679 | 521 | 328.2 | 247.7 | 247.4 | 268
680 | 522 | 328.1 | 247.9 | 247.6 | 268
681 | 523 | 328 | 248.2 | 247.8 | 268.2
682 | 524 | 327.9 | 248.5 | 248 | 268.4
683 | 525 | 327.7 | 248.7 | 248.2 | 268.5
684 | 526 | 327.6 | 248.9 | 248.4 | 268.5
685 | 527 | 327.4 | 249.2 | 248.6 | 268.7
686 | 528 | 327.3 | 249.4 | 248.8 | 268.8
687 | 529 | 327.3 | 249.7 | 249.1 | 268.8
688 | 530 | 327.2 | 249.9 | 249.2 | 268.9
689 | 531 | 327.1 | 250.2 | 249.4 | 269.1
690 | 532 | 327.1 | 250.4 | 249.6 | 269.1
691 | 533 | 327.1 | 250.6 | 249.9 | 269.2
692 | 534 | 327.1 | 250.9 | 250 | 269.3
693 | 535 | 327.1 | 251.1 | 250.2 | 269.4
694 | 536 | 327.1 | 251.3 | 250.5 | 269.5
695 | 537 | 327.2 | 251.6 | 250.7 | 269.6
696 | 538 | 327.2 | 251.8 | 250.9 | 269.8
697 | 539 | 327.2 | 252.1 | 251.1 | 269.9
698 | 540 | 327.2 | 252.3 | 251.3 | 269.9
699 | 541 | 327.1 | 252.6 | 251.5 | 270.1
700 | 542 | 327.2 | 252.8 | 251.7 | 270.2
701 | 543 | 327.2 | 253 | 251.9 | 270.3
702 | 544 | 327.1 | 253.3 | 252.1 | 270.4
703 | 545 | 327.2 | 253.6 | 252.3 | 270.5
704 | 546 | 327.3 | 253.8 | 252.5 | 270.6
705 | 547 | 327.5 | 254 | 252.7 | 270.7
706 | 548 | 327.6 | 254.3 | 252.9 | 270.9
707 | 549 | 327.6 | 254.6 | 253.1 | 271
708 | 550 | 327.7 | 254.8 | 253.3 | 271
709 | 551 | 327.8 | 255 | 253.5 | 271.2
710 | 552 | 327.9 | 255.3 | 253.6 | 271.3
711 | 553 | 328 | 255.4 | 253.9 | 271.3
712 | 554 | 328 | 255.7 | 254 | 271.5
713 | 555 | 328.1 | 255.9 | 254.3 | 271.5
714 | 556 | 328.2 | 256.2 | 254.5 | 271.7
715 | 557 | 328.4 | 256.4 | 254.7 | 271.9
716 | 558 | 328.5 | 256.6 | 254.8 | 272
717 | 559 | 328.7 | 256.9 | 255 | 272.2
718 | 560 | 328.8 | 257.1 | 255.2 | 272.4
719 | 561 | 328.9 | 257.3 | 255.5 | 272.4
720 | 562 | 328.9 | 257.6 | 255.6 | 272.6
721 | 563 | 329 | 257.8 | 255.8 | 272.8
722 | 564 | 328.9 | 258 | 256 | 272.8
723 | 565 | 328.9 | 258.2 | 256.3 | 272.9
724 | 566 | 328.9 | 258.5 | 256.4 | 273.1
725 | 567 | 328.8 | 258.7 | 256.6 | 273.2
726 | 568 | 328.8 | 258.9 | 256.9 | 273.2
727 | 569 | 328.9 | 259.2 | 257.1 | 273.4
728 | 570 | 328.8 | 259.4 | 257.2 | 273.5
729 | 571 | 328.8 | 259.6 | 257.5 | 273.6
730 | 572 | 328.8 | 259.8 | 257.7 | 273.6
731 | 573 | 328.8 | 260.1 | 257.9 | 273.8
732 | 574 | 328.7 | 260.3 | 258.1 | 273.9
733 | 575 | 328.5 | 260.5 | 258.3 | 273.9
734 | 576 | 328.4 | 260.7 | 258.5 | 274.1
735 | 577 | 328.3 | 261 | 258.6 | 274.3
736 | 578 | 328.3 | 261.1 | 258.9 | 274.3
737 | 579 | 328.2 | 261.4 | 259.1 | 274.3
738 | 580 | 328.1 | 261.7 | 259.2 | 274.5
739 | 581 | 328 | 261.9 | 259.4 | 274.6
740 | 582 | 328 | 262 | 259.7 | 274.6
741 | 583 | 328 | 262.4 | 259.8 | 274.8
742 | 584 | 328 | 262.6 | 260 | 274.9
743 | 585 | 328.1 | 262.3 | 260.3 | 275
744 | 586 | 328 | 262.1 | 260.5 | 275.1
745 | 587 | 328 | 262.5 | 260.6 | 275.3
746 | 588 | 328 | 263.4 | 260.8 | 275.3
747 | 589 | 328 | 263.5 | 261 | 275.3
748 | 590 | 327.9 | 263.8 | 261.2 | 275.5
749 | 591 | 327.8 | 264.1 | 261.3 | 275.6
750 | 592 | 327.8 | 264.2 | 261.5 | 275.6
751 | 593 | 327.7 | 264.5 | 261.8 | 275.6
752 | 594 | 327.7 | 264.7 | 261.9 | 275.8
753 | 595 | 327.7 | 264.9 | 262.1 | 275.9
754 | 596 | 327.6 | 265.1 | 262.3 | 275.8
755 | 597 | 327.7 | 265.3 | 262.5 | 276
756 | 598 | 327.7 | 265.6 | 262.7 | 276.2
757 | 599 | 327.8 | 265.1 | 263 | 276.2
758 | 600 | 327.8 | 265 | 263.2 | 276.3
759 | 601 | 327.8 | 265.2 | 263.4 | 276.5
760 | 602 | 327.7 | 265.4 | 263.6 | 276.6
761 | 603 | 327.7 | 265.6 | 263.8 | 276.6
762 | 604 | 327.7 | 265.9 | 264 | 276.8
763 | 605 | 327.7 | 266.1 | 264.1 | 276.9
764 | 606 | 327.7 | 266.3 | 264.4 | 276.9
765 | 607 | 327.7 | 266.5 | 264.6 | 277
766 | 608 | 327.7 | 266.7 | 264.7 | 277.2
767 | 609 | 327.7 | 266.9 | 265 | 277.2
768 | 610 | 327.6 | 267.1 | 265.2 | 277.2
769 | 611 | 327.6 | 267.3 | 265.3 | 277.4
770 | 612 | 327.7 | 267.5 | 265.5 | 277.5
771 | 613 | 327.9 | 267.7 | 265.7 | 277.6
772 | 614 | 327.9 | 267.9 | 266 | 277.6
773 | 615 | 327.9 | 268.2 | 266.1 | 277.8
774 | 616 | 327.8 | 268.4 | 266.4 | 277.9
775 | 617 | 327.7 | 268.6 | 266.6 | 277.9
776 | 618 | 327.7 | 268.8 | 266.8 | 278
777 | 619 | 327.7 | 269 | 266.9 | 278.2
778 | 620 | 327.7 | 269.2 | 267.2 | 278.2
779 | 621 | 327.8 | 269.4 | 267.4 | 278.2
780 | 622 | 327.9 | 269.6 | 267.6 | 278.4
781 | 623 | 327.9 | 269.8 | 267.8 | 278.5
782 | 624 | 327.9 | 270 | 268 | 278.5
783 | 625 | 327.9 | 270.3 | 268.2 | 278.7
784 | 626 | 328 | 270.5 | 268.4 | 278.8
785 | 627 | 328.1 | 270.7 | 268.6 | 278.9
786 | 628 | 328.2 | 270.9 | 268.8 | 279
787 | 629 | 328.2 | 271.1 | 269 | 279.2
788 | 630 | 328.2 | 271.3 | 269.2 | 279.3
789 | 631 | 328.2 | 271.5 | 269.4 | 279.3
790 | 632 | 328.3 | 271.8 | 269.6 | 279.5
791 | 633 | 328.4 | 272 | 269.8 | 279.6
792 | 634 | 328.5 | 272.2 | 270 | 279.6
793 | 635 | 328.4 | 272.4 | 270.2 | 279.7
794 | 636 | 328.4 | 272.6 | 270.4 | 279.9
795 | 637 | 328.5 | 272.9 | 270.6 | 280
796 | 638 | 328.5 | 273.1 | 270.8 | 280
797 | 639 | 328.4 | 273.3 | 271 | 280.2
798 | 640 | 328.4 | 273.6 | 271.2 | 280.3
799 | 641 | 328.5 | 273.8 | 271.4 | 280.3
800 | 642 | 328.5 | 274 | 271.6 | 280.4
801 | 643 | 328.5 | 274.2 | 271.8 | 280.6
802 | 644 | 328.5 | 274.5 | 272 | 280.7
803 | 645 | 328.5 | 274.7 | 272.3 | 280.7
804 | 646 | 328.4 | 275 | 272.5 | 280.9
805 | 647 | 328.3 | 275.2 | 272.7 | 281
806 | 648 | 328.2 | 275.4 | 272.9 | 281.1
807 | 649 | 328.1 | 275.7 | 273.1 | 281.2
808 | 650 | 328.1 | 275.9 | 273.3 | 281.3
809 | 651 | 327.9 | 276.1 | 273.5 | 281.4
810 | 652 | 327.8 | 276.4 | 273.8 | 281.4
811 | 653 | 327.7 | 276.6 | 274 | 281.6
812 | 654 | 327.6 | 276.9 | 274.2 | 281.7
813 | 655 | 327.6 | 277.1 | 274.4 | 281.7
814 | 656 | 327.7 | 277.3 | 274.7 | 281.8
815 | 657 | 327.7 | 277.6 | 274.9 | 282
816 | 658 | 327.6 | 277.8 | 275.1 | 282.1
817 | 659 | 327.5 | 278 | 275.4 | 282.1
818 | 660 | 327.5 | 278.3 | 275.5 | 282.3
819 | 661 | 327.4 | 278.5 | 275.8 | 282.4
820 | 662 | 327.4 | 278.7 | 276 | 282.4
821 | 663 | 327.4 | 279 | 276.3 | 282.5
822 | 664 | 327.3 | 279.2 | 276.5 | 282.7
823 | 665 | 327.3 | 279.5 | 276.7 | 282.8
824 | 666 | 327.3 | 279.7 | 277 | 282.7
825 | 667 | 327.3 | 279.9 | 277.2 | 282.9
826 | 668 | 327.4 | 280.1 | 277.5 | 283.1
827 | 669 | 327.4 | 280.4 | 277.7 | 283.1
828 | 670 | 327.4 | 280.6 | 277.9 | 283.2
829 | 671 | 327.5 | 280.8 | 278.1 | 283.4
830 | 672 | 327.5 | 281 | 278.3 | 283.5
831 | 673 | 327.6 | 281.2 | 278.5 | 283.5
832 | 674 | 327.7 | 281.4 | 278.7 | 283.7
833 | 675 | 327.8 | 281.6 | 278.9 | 283.8
834 | 676 | 327.8 | 281.8 | 279.1 | 283.8
835 | 677 | 327.8 | 282 | 279.3 | 283.9
836 | 678 | 327.8 | 282.2 | 279.4 | 284.1
837 | 679 | 327.8 | 282.4 | 279.6 | 284.2
838 | 680 | 327.7 | 282.6 | 279.8 | 284.1
839 | 681 | 327.7 | 282.8 | 280 | 284.3
840 | 682 | 327.6 | 283 | 280.1 | 284.5
841 | 683 | 327.6 | 283.2 | 280.3 | 284.5
842 | 684 | 327.5 | 283.3 | 280.5 | 284.6
843 | 685 | 327.5 | 283.5 | 280.6 | 284.7
844 | 686 | 327.5 | 283.7 | 280.8 | 284.8
845 | 687 | 327.6 | 283.8 | 281 | 284.8
846 | 688 | 327.6 | 283.9 | 281.1 | 285
847 | 689 | 327.7 | 284.1 | 281.2 | 285.2
848 | 690 | 327.7 | 284.2 | 281.4 | 285.2
849 | 691 | 327.7 | 284.4 | 281.5 | 285.3
850 | 692 | 327.8 | 284.5 | 281.6 | 285.5
851 | 693 | 327.8 | 284.7 | 281.8 | 285.6
852 | 694 | 327.8 | 284.8 | 282 | 285.5
853 | 695 | 327.7 | 285 | 282 | 285.7
854 | 696 | 327.7 | 285.2 | 282.1 | 285.9
855 | 697 | 327.7 | 285.3 | 282.3 | 285.9
856 | 698 | 327.7 | 285.4 | 282.4 | 285.9
857 | 699 | 327.7 | 285.6 | 282.5 | 286.1
858 | 700 | 327.7 | 285.9 | 282.6 | 286.2
859 | 701 | 327.7 | 286 | 282.7 | 286.2
860 | 702 | 327.7 | 286.8 | 282.7 | 286.4
861 | 703 | 327.6 | 287.2 | 282.7 | 286.5
862 | 704 | 327.5 | 287.6 | 282.8 | 286.5
863 | 705 | 327.6 | 287.8 | 282.9 | 286.6
864 | 706 | 327.6 | 288.5 | 282.9 | 286.8
865 | 707 | 327.6 | 288.9 | 283 | 286.9
866 | 708 | 327.6 | 288.9 | 283.1 | 286.8
867 | 709 | 327.6 | 289.2 | 283.2 | 287
868 | 710 | 327.7 | 289.3 | 283.2 | 287.2
869 | 711 | 327.7 | 289.3 | 283.3 | 287.2
870 | 712 | 327.6 | 289.3 | 283.4 | 287.2
871 | 713 | 327.6 | 289.5 | 283.4 | 287.4
872 | 714 | 327.5 | 289.5 | 283.5 | 287.5
873 | 715 | 327.4 | 289.4 | 283.6 | 287.4
874 | 716 | 327.4 | 289.6 | 283.7 | 287.6
875 | 717 | 327.4 | 289.6 | 283.7 | 287.7
876 | 718 | 327.4 | 289.6 | 283.8 | 287.7

## C11-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 158.0818 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 11 & 12
Time-131 | N11 | N12 | Time-132 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38957.6166 | 1 | 0 | 38957.6166 | 1 | 0 | 25 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38957.6187 | 1 | 0 | 38957.6187 | 1 | 0 | 210 | 368 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38957.6208 | 1 | 0 | 38957.6208 | 1 | 0 | 394.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
38957.623 | 2058 | 0 | 38957.623 | 2510 | 0 | 579.5 | 737.5 | 125.641 | 0 | 153.2357 | 0 | 1.2564 | 0 | 1.5324 | 0 | 1.2564 | 1.5324 | 25.8202 | 3.1625 | 24.5638
38957.6251 | 2573 | 0 | 38957.6251 | 2471 | 0 | 764 | 922 | 157.0818 | 0 | 150.8547 | 0 | 1.5708 | 0 | 1.5085 | 0 | 1.5708 | 1.5085 | 0.63661 | 4.7908 | 0.93421

## C10-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 148.4969 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 10 & 12
Time-129 | N11 | N12 | Time-130 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38957.6165 | 1 | 0 | 38957.6165 | 1 | 0 | 22.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38957.6187 | 1 | 0 | 38957.6187 | 1 | 0 | 207 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38957.6208 | 2218 | 0 | 38957.6208 | 2 | 0 | 392 | 550 | 135.409 | 0 | 0.1221 | 0 | 1.3541 | 0 | 0.001221 | 0 | 1.3541 | 0.001221 | 9.6655 | 121519 | 8.3114
38957.6229 | 2416 | 0 | 38957.623 | 2106 | 0 | 576.5 | 734.5 | 147.4969 | 0 | 128.5714 | 0 | 1.475 | 0 | 1.2857 | 0 | 1.475 | 1.2857 | 0.67798 | 15.4976 | 0.79699
38957.6251 | 2049 | 0 | 38957.6251 | 2048 | 0 | 761.5 | 919.5 | 125.0916 | 0 | 125.0305 | 0 | 1.2509 | 0 | 1.2503 | 0 | 1.2509 | 1.2503 | 18.7106 | 18.7686 | 17.4597

## C10-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 151.6105 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 10 & 11
Time-127 | N11 | N12 | Time-128 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38957.6165 | 1 | 0 | 38957.6165 | 1 | 0 | 19.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38957.6186 | 1 | 0 | 38957.6186 | 1 | 0 | 204.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38957.6208 | 2065 | 0 | 38957.6208 | 1 | 0 | 389 | 547 | 126.0684 | 0 | 0.06105 | 0 | 1.2607 | 0 | 0.0006105 | 0 | 1.2607 | 0.0006105 | 20.2605 | 248238 | 18.9998
38957.6229 | 2179 | 0 | 38957.6229 | 2165 | 0 | 573.5 | 731.5 | 133.0281 | 0 | 132.1734 | 0 | 1.3303 | 0 | 1.3217 | 0 | 1.3303 | 1.3217 | 13.9688 | 14.7058 | 12.6385
38957.625 | 2467 | 0 | 38957.6251 | 2396 | 0 | 758.5 | 916.5 | 150.6105 | 0 | 146.2759 | 0 | 1.5061 | 0 | 1.4628 | 0 | 1.5061 | 1.4628 | 0.66396 | 3.6469 | 0.84214

## C9-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 154.3578 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 9 & 12
Time-125 | N11 | N12 | Time-126 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38957.6165 | 1 | 0 | 38957.6165 | 1 | 0 | 16.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38957.6186 | 1 | 0 | 38957.6186 | 1 | 0 | 201.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38957.6207 | 1 | 0 | 38957.6208 | 1 | 0 | 386.5 | 544.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38957.6229 | 2230 | 0 | 38957.6229 | 2160 | 0 | 571 | 729 | 136.1416 | 0 | 131.8681 | 0 | 1.3614 | 0 | 1.3187 | 0 | 1.3614 | 1.3187 | 13.3803 | 17.0546 | 12.0189
38957.625 | 2500 | 0 | 38957.625 | 2512 | 0 | 756 | 914 | 152.6252 | 0 | 153.3578 | 0 | 1.5263 | 0 | 1.5336 | 0 | 1.5263 | 1.5336 | 1.1352 | 0.65207 | 0.39105

## C9-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 152.5263 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 9 & 11
Time-123 | N11 | N12 | Time-124 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38957.6164 | 1 | 0 | 38957.6164 | 1 | 0 | 14 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38957.6186 | 1 | 0 | 38957.6186 | 1 | 0 | 198.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38957.6207 | 1 | 0 | 38957.6207 | 1 | 0 | 383.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38957.6228 | 2040 | 0 | 38957.6229 | 2141 | 0 | 568 | 726 | 124.5421 | 0 | 130.7082 | 0 | 1.2454 | 0 | 1.3071 | 0 | 1.2454 | 1.3071 | 22.4696 | 16.6922 | 21.2242
38957.625 | 2482 | 0 | 38957.625 | 2420 | 0 | 753 | 911 | 151.5263 | 0 | 147.7411 | 0 | 1.5153 | 0 | 1.4774 | 0 | 1.5153 | 1.4774 | 0.65995 | 3.2388 | 0.85531

## C9-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 157.2271 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 9 & 10
Time-121 | N11 | N12 | Time-122 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38957.6164 | 1 | 0 | 38957.6164 | 1 | 0 | 11 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.6185 | 1 | 0 | 38957.6186 | 1 | 0 | 196 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.6207 | 1 | 0 | 38957.6207 | 1979 | 0 | 380.5 | 538.5 | 0.06105 | 0 | 120.8181 | 0 | 0.0006105 | 0 | 1.2082 | 0 | 0.0006105 | 1.2082 | 257438 | 30.1354 | 257437.9994
38957.6228 | 2356 | 0 | 38957.6228 | 2559 | 0 | 565.5 | 723.5 | 143.8339 | 0 | 156.2271 | 0 | 1.4383 | 0 | 1.5623 | 0 | 1.4383 | 1.5623 | 9.3115 | 0.64009 | 7.8732
38957.6249 | 2488 | 0 | 38957.625 | 2535 | 0 | 750 | 908 | 151.8926 | 0 | 154.7619 | 0 | 1.5189 | 0 | 1.5476 | 0 | 1.5189 | 1.5476 | 3.5121 | 1.5929 | 1.9931

## C8-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 157.2271 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 8 & 12
Time-119 | N11 | N12 | Time-120 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R12-G | R8-12
38957.6164 | 1 | 0 | 38957.6164 | 1 | 0 | 8.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.6185 | 1 | 0 | 38957.6185 | 1 | 0 | 193 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.6206 | 1 | 0 | 38957.6207 | 1 | 0 | 378 | 536 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.6228 | 2432 | 0 | 38957.6228 | 2559 | 0 | 562.5 | 720.5 | 148.4737 | 0 | 156.2271 | 0 | 1.4847 | 0 | 1.5623 | 0 | 1.4847 | 1.5623 | 5.8956 | 0.64009 | 4.4108
38957.6249 | 2537 | 0 | 38957.6249 | 2437 | 0 | 747.5 | 905.5 | 154.884 | 0 | 148.779 | 0 | 1.5488 | 0 | 1.4878 | 0 | 1.5488 | 1.4878 | 1.5128 | 5.6783 | 0.03603

## C8-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 157.044 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 8 & 11
Time-117 | N11 | N12 | Time-118 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R11-G | R8-11
38957.6163 | 1 | 0 | 38957.6163 | 1 | 0 | 5.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38957.6185 | 1 | 0 | 38957.6185 | 1 | 0 | 190.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38957.6206 | 1 | 0 | 38957.6206 | 1 | 0 | 375 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38957.6227 | 2000 | 0 | 38957.6228 | 2484 | 0 | 559.5 | 717.5 | 122.1001 | 0 | 151.6484 | 0 | 1.221 | 0 | 1.5165 | 0 | 1.221 | 1.5165 | 28.619 | 3.558 | 27.398
38957.6249 | 2552 | 0 | 38957.6249 | 2556 | 0 | 744.5 | 902.5 | 155.7998 | 0 | 156.044 | 0 | 1.558 | 0 | 1.5604 | 0 | 1.558 | 1.5604 | 0.79859 | 0.64085 | 0.75941

## C8-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 152.4042 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 8 & 10
Time-115 | N11 | N12 | Time-116 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38957.6163 | 1 | 0 | 38957.6163 | 1 | 0 | 2.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38957.6184 | 1 | 0 | 38957.6184 | 1 | 0 | 187.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38957.6206 | 1 | 0 | 38957.6206 | 1 | 0 | 372 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38957.6227 | 2232 | 0 | 38957.6227 | 2427 | 0 | 557 | 715 | 136.2637 | 0 | 148.1685 | 0 | 1.3626 | 0 | 1.4817 | 0 | 1.3626 | 1.4817 | 11.845 | 2.8587 | 10.4823
38957.6248 | 2266 | 0 | 38957.6249 | 2480 | 0 | 742 | 900 | 138.3394 | 0 | 151.4042 | 0 | 1.3834 | 0 | 1.514 | 0 | 1.3834 | 1.514 | 10.1668 | 0.66048 | 8.7834

## C8-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 144.4676 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 8 & 9
Time-113 | N11 | N12 | Time-114 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38957.6163 | 1 | 0 | 38957.6163 | 1 | 0 | -1.5553e-07 | 158 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38957.6184 | 1 | 0 | 38957.6184 | 1 | 0 | 184.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38957.6205 | 1 | 0 | 38957.6206 | 1 | 0 | 369.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236538 | 236538 | 236537.9994
38957.6227 | 2033 | 0 | 38957.6227 | 2297 | 38 | 554 | 712 | 124.1148 | 0 | 140.232 | 2.3199 | 1.2411 | 0 | 1.4023 | 0.023199 | 1.2411 | 1.3791 | 16.3984 | 4.7534 | 15.1573
38957.6248 | 2350 | 0 | 38957.6248 | 2329 | 0 | 739 | 897 | 143.4676 | 0 | 142.1856 | 0 | 1.4347 | 0 | 1.4219 | 0 | 1.4347 | 1.4219 | 0.69702 | 1.605 | 0.73766

## C7-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 154.0525 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 7 & 12
Time-111 | N11 | N12 | Time-112 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R12-G | R7-12
38957.6162 | 1 | 0 | 38957.6162 | 1 | 0 | -3 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38957.6184 | 1 | 0 | 38957.6184 | 1 | 0 | 181.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38957.6205 | 1 | 0 | 38957.6205 | 1 | 0 | 366.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38957.6227 | 2124 | 11 | 38957.6227 | 2452 | 7 | 551.5 | 709.5 | 129.6703 | 0.67155 | 149.6947 | 0.42735 | 1.2967 | 0.0067155 | 1.4969 | 0.0042735 | 1.29 | 1.4927 | 22.9408 | 2.9563 | 101.3825
| 2124 | 11 | 38957.6248 | 2507 | 0 | 737 | 895 | 129.6703 | 0.67155 | 153.0525 | 0 | 1.2967 | 0.0067155 | 1.5305 | 0 | 1.29 | 1.5305 | 93.004 | 0.65337 | 22.919

## C7-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 150.9389 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 7 & 11
Time-109 | N11 | N12 | Time-110 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R11-G | R7-11
38957.6162 | 1 | 0 | 38957.6162 | 1 | 0 | -5.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38957.6183 | 1 | 0 | 38957.6184 | 1 | 0 | 179 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38957.6205 | 1 | 0 | 38957.6205 | 1 | 0 | 363.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247138 | 247138 | 247137.9994
38957.6226 | 2456 | 39 | 38957.6226 | 2359 | 122 | 548.5 | 706.5 | 149.9389 | 2.381 | 144.0171 | 7.4481 | 1.4994 | 0.02381 | 1.4402 | 0.074481 | 1.4756 | 1.3657 | 1.5529 | 2.863 | 1.6143
38957.6248 | 2025 | 0 | 38957.6248 | 2236 | 0 | 733.5 | 891.5 | 123.6264 | 0 | 136.5079 | 0 | 1.2363 | 0 | 1.3651 | 0 | 1.2363 | 1.3651 | 22.0928 | 10.5716 | 20.8566

## C7-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.6777 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 7 & 10
Time-107 | N11 | N12 | Time-108 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38957.6162 | 1 | 0 | 38957.6162 | 7 | 0 | -8.5 | 149.5 | 0.06105 | 0 | 0.42735 | 0 | 0.0006105 | 0 | 0.0042735 | 0 | 0.0006105 | 0.0042735 | 256538 | 36562.5714 | 256537.9994
38957.6183 | 1 | 0 | 38957.6183 | 1 | 0 | 176 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38957.6204 | 1 | 0 | 38957.6205 | 1 | 0 | 361 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38957.6226 | 2385 | 0 | 38957.6226 | 2550 | 0 | 545.5 | 703.5 | 145.6044 | 0 | 155.6777 | 0 | 1.456 | 0 | 1.5568 | 0 | 1.456 | 1.5568 | 7.605 | 0.64235 | 6.149
38957.6247 | 2235 | 0 | 38957.6247 | 2388 | 0 | 730.5 | 888.5 | 136.4469 | 0 | 145.7875 | 0 | 1.3645 | 0 | 1.4579 | 0 | 1.3645 | 1.4579 | 14.8268 | 7.4698 | 13.4624

## C7-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 133.3565 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 7 & 9
Time-105 | N11 | N12 | Time-106 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38957.6161 | 1 | 0 | 38957.6161 | 1 | 0 | -11.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218338 | 218338 | 218337.9994
38957.6183 | 1 | 0 | 38957.6183 | 1 | 0 | 173.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218338 | 218338 | 218337.9994
38957.6204 | 1 | 0 | 38957.6204 | 1 | 0 | 358.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218338 | 218338 | 218337.9994
38957.6225 | 2041 | 0 | 38957.6226 | 2024 | 0 | 543 | 701 | 124.6032 | 0 | 123.5653 | 0 | 1.246 | 0 | 1.2357 | 0 | 1.246 | 1.2357 | 7.025 | 7.9239 | 5.779
38957.6247 | 2168 | 0 | 38957.6247 | 2073 | 0 | 727.5 | 885.5 | 132.3565 | 0 | 126.5568 | 0 | 1.3236 | 0 | 1.2656 | 0 | 1.3236 | 1.2656 | 0.75554 | 5.3729 | 0.56803

## C7-8
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 147.0928 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 7 & 8
Time-103 | N11 | N12 | Time-104 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38957.6161 | 1 | 0 | 38957.6161 | 1 | 0 | -14.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38957.6182 | 1 | 0 | 38957.6183 | 1 | 0 | 170.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38957.6204 | 1 | 0 | 38957.6204 | 1 | 0 | 355.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38957.6225 | 2113 | 0 | 38957.6225 | 2393 | 0 | 540 | 698 | 128.9988 | 0 | 146.0928 | 0 | 1.29 | 0 | 1.4609 | 0 | 1.29 | 1.4609 | 14.0265 | 0.6845 | 12.7365
38957.6247 | 2282 | 0 | 38957.6247 | 2287 | 0 | 725 | 883 | 139.3162 | 0 | 139.6215 | 0 | 1.3932 | 0 | 1.3962 | 0 | 1.3932 | 1.3962 | 5.5819 | 5.3511 | 4.1888

## C6-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 148.4969 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 12
Time-101 | N11 | N12 | Time-102 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38957.6161 | 1 | 0 | 38957.6161 | 1 | 0 | -17 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38957.6182 | 1 | 0 | 38957.6182 | 1 | 0 | 168 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38957.6203 | 1 | 0 | 38957.6204 | 1 | 0 | 352.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243138 | 243138 | 243137.9994
38957.6225 | 2266 | 0 | 38957.6225 | 2187 | 0 | 537.5 | 695.5 | 138.3394 | 0 | 133.5165 | 0 | 1.3834 | 0 | 1.3352 | 0 | 1.3834 | 1.3352 | 7.3425 | 11.2199 | 5.9591
38957.6246 | 2159 | 0 | 38957.6246 | 2416 | 0 | 722 | 880 | 131.8071 | 0 | 147.4969 | 0 | 1.3181 | 0 | 1.475 | 0 | 1.3181 | 1.475 | 12.6623 | 0.67798 | 11.3443

## C6-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 152.9536 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 11
Time-99 | N11 | N12 | Time-100 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38957.616 | 1 | 0 | 38957.6161 | 1 | 0 | -19.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250438 | 250438 | 250437.9994
38957.6182 | 1 | 0 | 38957.6182 | 1 | 0 | 165 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250438 | 250438 | 250437.9994
38957.6203 | 1 | 0 | 38957.6203 | 1 | 0 | 349.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250438 | 250438 | 250437.9994
38957.6225 | 2489 | 0 | 38957.6225 | 2301 | 0 | 534.5 | 692.5 | 151.9536 | 0 | 140.4762 | 0 | 1.5195 | 0 | 1.4048 | 0 | 1.5195 | 1.4048 | 0.6581 | 8.8822 | 0.86144
38957.6246 | 2134 | 0 | 38957.6246 | 1989 | 0 | 719.5 | 877.5 | 130.2808 | 0 | 121.4286 | 0 | 1.3028 | 0 | 1.2143 | 0 | 1.3028 | 1.2143 | 17.403 | 25.9618 | 16.1002

## C6-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 149.0464 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 10
Time-97 | N11 | N12 | Time-98 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38957.616 | 1 | 0 | 38957.616 | 1 | 0 | -22.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6181 | 1 | 0 | 38957.6182 | 1 | 0 | 162 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6203 | 1 | 0 | 38957.6203 | 1 | 0 | 347 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6224 | 2186 | 0 | 38957.6224 | 2425 | 0 | 531.5 | 689.5 | 133.4554 | 0 | 148.0464 | 0 | 1.3346 | 0 | 1.4805 | 0 | 1.3346 | 1.4805 | 11.6825 | 0.67546 | 10.348
38957.6246 | 2007 | 0 | 38957.6246 | 2070 | 0 | 716.5 | 874.5 | 122.5275 | 0 | 126.3736 | 0 | 1.2253 | 0 | 1.2637 | 0 | 1.2253 | 1.2637 | 21.6432 | 17.9411 | 20.418

## C6-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 153.6252 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 9
Time-95 | N11 | N12 | Time-96 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38957.616 | 1 | 0 | 38957.616 | 1 | 0 | -25.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38957.6181 | 1 | 0 | 38957.6181 | 1 | 0 | 159.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38957.6202 | 1 | 0 | 38957.6203 | 1 | 0 | 344 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38957.6224 | 2292 | 0 | 38957.6224 | 2439 | 1 | 529 | 687 | 139.9267 | 0 | 148.9011 | 0.06105 | 1.3993 | 0 | 1.489 | 0.0006105 | 1.3993 | 1.4884 | 9.7897 | 3.2149 | 8.3904
38957.6245 | 2279 | 0 | 38957.6245 | 2500 | 0 | 713.5 | 871.5 | 139.1331 | 0 | 152.6252 | 0 | 1.3913 | 0 | 1.5263 | 0 | 1.3913 | 1.5263 | 10.416 | 0.6552 | 9.0246

## C6-8
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 153.2589 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 8
Time-93 | N11 | N12 | Time-94 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R8-G | R6-8
38957.6159 | 1 | 0 | 38957.616 | 1 | 0 | -28 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38957.6181 | 1 | 0 | 38957.6181 | 1 | 0 | 156.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38957.6202 | 1 | 0 | 38957.6202 | 1 | 0 | 341.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38957.6223 | 2426 | 0 | 38957.6224 | 2386 | 0 | 526 | 684 | 148.1074 | 0 | 145.6654 | 0 | 1.4811 | 0 | 1.4567 | 0 | 1.4811 | 1.4567 | 3.4782 | 5.2129 | 1.9971
38957.6245 | 2494 | 0 | 38957.6245 | 2389 | 0 | 711 | 869 | 152.2589 | 0 | 145.8486 | 0 | 1.5226 | 0 | 1.4585 | 0 | 1.5226 | 1.4585 | 0.65678 | 5.0808 | 0.86581

## C6-7
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 148.1306 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 7
Time-91 | N11 | N12 | Time-92 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38957.6159 | 1 | 0 | 38957.6159 | 1 | 0 | -31 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38957.618 | 1 | 0 | 38957.6181 | 1 | 0 | 153.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38957.6202 | 1 | 0 | 38957.6202 | 1 | 0 | 338.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38957.6223 | 2410 | 0 | 38957.6223 | 2094 | 0 | 523.5 | 681.5 | 147.1306 | 0 | 127.8388 | 0 | 1.4713 | 0 | 1.2784 | 0 | 1.4713 | 1.2784 | 0.67967 | 15.873 | 0.79164
38957.6245 | 2129 | 0 | 38957.6245 | 2360 | 0 | 708 | 866 | 129.9756 | 0 | 144.0781 | 0 | 1.2998 | 0 | 1.4408 | 0 | 1.2998 | 1.4408 | 13.9681 | 2.8127 | 12.6683

## C5-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 154.9683 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 12
Time-89 | N11 | N12 | Time-90 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38957.6159 | 1 | 0 | 38957.6159 | 1 | 0 | -34 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38957.618 | 1 | 0 | 38957.618 | 1 | 0 | 151 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38957.6202 | 1 | 0 | 38957.6202 | 1 | 0 | 336 | 494 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38957.6223 | 2296 | 0 | 38957.6223 | 2079 | 0 | 520.5 | 678.5 | 140.1709 | 0 | 126.9231 | 0 | 1.4017 | 0 | 1.2692 | 0 | 1.4017 | 1.2692 | 10.5566 | 22.0962 | 9.1549
38957.6244 | 2297 | 0 | 38957.6244 | 2522 | 0 | 705.5 | 863.5 | 140.232 | 0 | 153.9683 | 0 | 1.4023 | 0 | 1.5397 | 0 | 1.4023 | 1.5397 | 10.5085 | 0.64948 | 9.1062

## C5-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 135.3712 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 11
Time-87 | N11 | N12 | Time-88 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38957.6158 | 1 | 0 | 38957.6159 | 1 | 0 | -36.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221638 | 221638 | 221637.9994
38957.618 | 1 | 0 | 38957.618 | 2 | 0 | 148.5 | 306.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 221638 | 110769 | 221637.9994
38957.6201 | 1 | 0 | 38957.6201 | 1 | 0 | 333 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221638 | 221638 | 221637.9994
38957.6223 | 2023 | 0 | 38957.6223 | 2201 | 0 | 518 | 676 | 123.5043 | 0 | 134.3712 | 0 | 1.235 | 0 | 1.3437 | 0 | 1.235 | 1.3437 | 9.6085 | 0.74421 | 8.3735
38957.6244 | 2000 | 0 | 38957.6244 | 1990 | 0 | 702.5 | 860.5 | 122.1001 | 0 | 121.4896 | 0 | 1.221 | 0 | 1.2149 | 0 | 1.221 | 1.2149 | 10.869 | 11.4261 | 9.648

## C5-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 147.8864 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 10
Time-85 | N11 | N12 | Time-86 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38957.6158 | 1 | 0 | 38957.6158 | 1 | 0 | -39.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38957.618 | 1 | 0 | 38957.618 | 1 | 0 | 145.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38957.6201 | 1 | 0 | 38957.6201 | 1 | 0 | 330 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38957.6222 | 2002 | 0 | 38957.6222 | 2406 | 0 | 515 | 673 | 122.2222 | 0 | 146.8864 | 0 | 1.2222 | 0 | 1.4689 | 0 | 1.2222 | 1.4689 | 20.998 | 0.6808 | 19.7758
38957.6244 | 1985 | 0 | 38957.6244 | 2239 | 0 | 699.5 | 857.5 | 121.1844 | 0 | 136.6911 | 0 | 1.2118 | 0 | 1.3669 | 0 | 1.2118 | 1.3669 | 22.0343 | 8.1903 | 20.8224

## C5-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 150.6947 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 9
Time-83 | N11 | N12 | Time-84 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38957.6158 | 1 | 0 | 38957.6158 | 1 | 0 | -42 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246738 | 246738 | 246737.9994
38957.6179 | 1 | 0 | 38957.6179 | 1 | 0 | 142.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246738 | 246738 | 246737.9994
38957.6201 | 1 | 0 | 38957.6201 | 1 | 0 | 327.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246738 | 246738 | 246737.9994
38957.6222 | 2210 | 0 | 38957.6222 | 2452 | 0 | 512 | 670 | 134.9206 | 0 | 149.6947 | 0 | 1.3492 | 0 | 1.4969 | 0 | 1.3492 | 1.4969 | 11.6914 | 0.66803 | 10.3422
38957.6243 | 2308 | 0 | 38957.6244 | 1988 | 0 | 697 | 855 | 140.9035 | 0 | 121.3675 | 0 | 1.409 | 0 | 1.2137 | 0 | 1.409 | 1.2137 | 6.9489 | 24.164 | 5.5398

## C5-8
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 150.1453 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 8
Time-81 | N11 | N12 | Time-82 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R8-G | R5-8
38957.6157 | 1 | 0 | 38957.6158 | 1 | 0 | -45 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245838 | 245838 | 245837.9994
38957.6179 | 1 | 0 | 38957.6179 | 1 | 0 | 140 | 298 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245838 | 245838 | 245837.9994
38957.62 | 1 | 0 | 38957.62 | 1 | 0 | 324.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245838 | 245838 | 245837.9994
38957.6222 | 2014 | 334 | 38957.6222 | 2048 | 1 | 509.5 | 667.5 | 122.9548 | 20.3907 | 125.0305 | 0.06105 | 1.2295 | 0.20391 | 1.2503 | 0.0006105 | 1.0256 | 1.2497 | 2464.6437 | 20.0971 | 5.5804
38957.6243 | 2063 | 0 | 38957.6243 | 2443 | 0 | 694 | 852 | 125.9463 | 0 | 149.1453 | 0 | 1.2595 | 0 | 1.4915 | 0 | 1.2595 | 1.4915 | 19.2138 | 0.67049 | 17.9543

## C5-7
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.6166 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 7
Time-79 | N11 | N12 | Time-80 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38957.6157 | 1 | 0 | 38957.6157 | 1 | 0 | -47.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6178 | 1 | 0 | 38957.6179 | 1 | 0 | 137 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.62 | 1 | 0 | 38957.62 | 1 | 0 | 321.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6221 | 2525 | 0 | 38957.6221 | 2317 | 0 | 506.5 | 664.5 | 154.1514 | 0 | 141.453 | 0 | 1.5415 | 0 | 1.4145 | 0 | 1.5415 | 1.4145 | 1.5992 | 10.7199 | 0.057694
38957.6243 | 2458 | 0 | 38957.6243 | 2549 | 0 | 691.5 | 849.5 | 150.0611 | 0 | 155.6166 | 0 | 1.5006 | 0 | 1.5562 | 0 | 1.5006 | 1.5562 | 4.3686 | 0.6426 | 2.868

## C5-6
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.6777 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 6
Time-77 | N11 | N12 | Time-78 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38957.6157 | 1 | 0 | 38957.6157 | 1 | 0 | -50.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38957.6178 | 1 | 0 | 38957.6178 | 1 | 0 | 134.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38957.62 | 1 | 0 | 38957.62 | 1 | 0 | 319 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38957.6221 | 2335 | 1 | 38957.6221 | 2124 | 0 | 503.5 | 661.5 | 142.5519 | 0.06105 | 129.6703 | 0 | 1.4255 | 0.0006105 | 1.2967 | 0 | 1.4249 | 1.2967 | 9.9339 | 20.8277 | 3971.1775
38957.6242 | 2182 | 0 | 38957.6242 | 2550 | 0 | 688.5 | 846.5 | 133.2112 | 0 | 155.6777 | 0 | 1.3321 | 0 | 1.5568 | 0 | 1.3321 | 1.5568 | 17.6159 | 0.64235 | 16.2838

## C4-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.9219 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 12
Time-75 | N11 | N12 | Time-76 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R12-G | R4-12
38957.6156 | 1 | 0 | 38957.6157 | 1 | 0 | -53.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38957.6178 | 1 | 0 | 38957.6178 | 1 | 0 | 131.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38957.6199 | 1 | 0 | 38957.6199 | 1 | 0 | 316.5 | 474.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38957.6221 | 1779 | 594 | 38957.6221 | 2554 | 2 | 501 | 659 | 108.6081 | 36.2637 | 155.9219 | 0.1221 | 1.0861 | 0.36264 | 1.5592 | 0.001221 | 0.72344 | 1.558 | 0.78683 | 0.59763 | 0.19741
38957.6242 | 1972 | 0 | 38957.6242 | 2243 | 0 | 685.5 | 843.5 | 120.3907 | 0 | 136.9353 | 0 | 1.2039 | 0 | 1.3694 | 0 | 1.2039 | 1.3694 | 30.3438 | 14.5956 | 29.1399

## C4-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.9219 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 11
Time-73 | N11 | N12 | Time-74 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R11-G | R4-11
38957.6156 | 1 | 0 | 38957.6156 | 1 | 0 | -56 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38957.6178 | 1 | 0 | 38957.6178 | 1 | 0 | 128.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38957.6199 | 1 | 0 | 38957.6199 | 1 | 0 | 313.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38957.622 | 2442 | 0 | 38957.622 | 2554 | 0 | 498 | 656 | 149.0842 | 0 | 155.9219 | 0 | 1.4908 | 0 | 1.5592 | 0 | 1.4908 | 1.5592 | 5.2572 | 0.64135 | 3.7663
38957.6242 | 2458 | 0 | 38957.6242 | 2182 | 0 | 683 | 841 | 150.0611 | 0 | 133.2112 | 0 | 1.5006 | 0 | 1.3321 | 0 | 1.5006 | 1.3321 | 4.572 | 17.7993 | 3.0714

## C4-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 133.2344 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 10
Time-71 | N11 | N12 | Time-72 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38957.6156 | 1 | 0 | 38957.6156 | 1 | 0 | -59 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218138 | 218138 | 218137.9994
38957.6177 | 1 | 0 | 38957.6177 | 1 | 0 | 125.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218138 | 218138 | 218137.9994
38957.6199 | 1 | 0 | 38957.6199 | 1 | 0 | 310.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218138 | 218138 | 218137.9994
38957.622 | 2038 | 10 | 38957.622 | 2118 | 578 | 495.5 | 653.5 | 124.42 | 0.6105 | 129.304 | 35.2869 | 1.2442 | 0.006105 | 1.293 | 0.35287 | 1.2381 | 0.94017 | 3.0524 | 0.37008 | 4.9548
38957.6241 | 1981 | 0 | 38957.6242 | 2166 | 0 | 680 | 838 | 120.9402 | 0 | 132.2344 | 0 | 1.2094 | 0 | 1.3223 | 0 | 1.2094 | 1.3223 | 10.1656 | 0.75623 | 8.9562

## C4-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.5556 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 9
Time-69 | N11 | N12 | Time-70 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38957.6156 | 1 | 0 | 38957.6156 | 1 | 0 | -61.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38957.6177 | 1 | 0 | 38957.6177 | 1 | 0 | 123 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38957.6198 | 1 | 0 | 38957.6198 | 1 | 0 | 307.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38957.622 | 2546 | 0 | 38957.622 | 2548 | 0 | 492.5 | 650.5 | 155.4335 | 0 | 155.5556 | 0 | 1.5543 | 0 | 1.5556 | 0 | 1.5543 | 1.5556 | 0.72192 | 0.64286 | 0.83242
38957.6241 | 2541 | 0 | 38957.6241 | 2518 | 0 | 677.5 | 835.5 | 155.1282 | 0 | 153.7241 | 0 | 1.5513 | 0 | 1.5372 | 0 | 1.5513 | 1.5372 | 0.92011 | 1.8419 | 0.63117

## C4-8
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.1282 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 8
Time-67 | N11 | N12 | Time-68 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38957.6155 | 1 | 0 | 38957.6155 | 1 | 0 | -64.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255638 | 255638 | 255637.9994
38957.6177 | 1 | 0 | 38957.6177 | 1 | 0 | 120 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255638 | 255638 | 255637.9994
38957.6198 | 1 | 0 | 38957.6198 | 1 | 0 | 305 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255638 | 255638 | 255637.9994
38957.6219 | 2533 | 0 | 38957.6219 | 2516 | 0 | 489.5 | 647.5 | 154.6398 | 0 | 153.602 | 0 | 1.5464 | 0 | 1.536 | 0 | 1.5464 | 1.536 | 0.9625 | 1.6447 | 0.5839
38957.6241 | 2098 | 0 | 38957.6241 | 2541 | 0 | 674.5 | 832.5 | 128.083 | 0 | 155.1282 | 0 | 1.2808 | 0 | 1.5513 | 0 | 1.2808 | 1.5513 | 21.8961 | 0.64463 | 20.6153

## C4-7
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 152.8315 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 7
Time-65 | N11 | N12 | Time-66 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38957.6155 | 1 | 0 | 38957.6155 | 1 | 0 | -67.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38957.6176 | 1 | 0 | 38957.6176 | 1 | 0 | 117.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38957.6198 | 1 | 0 | 38957.6198 | 1 | 0 | 302 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38957.6219 | 2234 | 0 | 38957.6219 | 2487 | 24 | 487 | 645 | 136.3858 | 0 | 151.8315 | 1.4652 | 1.3639 | 0 | 1.5183 | 0.014652 | 1.3639 | 1.5037 | 12.0582 | 1.6395 | 10.6943
38957.624 | 2471 | 0 | 38957.6241 | 2038 | 0 | 671.5 | 829.5 | 150.8547 | 0 | 124.42 | 0 | 1.5085 | 0 | 1.2442 | 0 | 1.5085 | 1.2442 | 1.3104 | 22.8351 | 0.19815

## C4-6
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 154.2357 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 6
Time-63 | N11 | N12 | Time-64 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38957.6155 | 1 | 0 | 38957.6155 | 1 | 0 | -70.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
38957.6176 | 1 | 0 | 38957.6176 | 1 | 0 | 114.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
38957.6197 | 1 | 0 | 38957.6197 | 1 | 0 | 299.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
38957.6219 | 2510 | 0 | 38957.6219 | 2017 | 0 | 484.5 | 642.5 | 153.2357 | 0 | 123.138 | 0 | 1.5324 | 0 | 1.2314 | 0 | 1.5324 | 1.2314 | 0.65259 | 25.2543 | 0.87977
38957.624 | 2237 | 0 | 38957.624 | 2500 | 0 | 669 | 827 | 136.569 | 0 | 152.6252 | 0 | 1.3657 | 0 | 1.5263 | 0 | 1.3657 | 1.5263 | 12.9361 | 1.0552 | 11.5704

## C4-5
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 145.3834 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 5
Time-61 | N11 | N12 | Time-62 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38957.6154 | 1 | 0 | 38957.6154 | 1 | 0 | -73 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238038 | 238038 | 238037.9994
38957.6176 | 1 | 0 | 38957.6176 | 1 | 0 | 112 | 270 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238038 | 238038 | 238037.9994
38957.6197 | 1 | 0 | 38957.6197 | 1 | 0 | 296.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238038 | 238038 | 238037.9994
38957.6218 | 2268 | 0 | 38957.6219 | 2365 | 0 | 481.5 | 639.5 | 138.4615 | 0 | 144.3834 | 0 | 1.3846 | 0 | 1.4438 | 0 | 1.3846 | 1.4438 | 4.9991 | 0.6926 | 3.6145
38957.624 | 2258 | 0 | 38957.624 | 2185 | 0 | 666 | 824 | 137.851 | 0 | 133.3944 | 0 | 1.3785 | 0 | 1.3339 | 0 | 1.3785 | 1.3339 | 5.4641 | 8.9876 | 4.0856

## C3-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 149.0464 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 12
Time-59 | N11 | N12 | Time-60 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R12-G | R3-12
38957.6154 | 1 | 0 | 38957.6154 | 1 | 0 | -75.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6175 | 1 | 0 | 38957.6175 | 1 | 0 | 109 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6197 | 1 | 0 | 38957.6197 | 1 | 0 | 293.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6218 | 2224 | 0 | 38957.6218 | 2159 | 0 | 478.5 | 636.5 | 135.7753 | 0 | 131.8071 | 0 | 1.3578 | 0 | 1.3181 | 0 | 1.3578 | 1.3181 | 9.7743 | 13.0792 | 8.4165
38957.6239 | 2121 | 0 | 38957.624 | 2425 | 0 | 663.5 | 821.5 | 129.4872 | 0 | 148.0464 | 0 | 1.2949 | 0 | 1.4805 | 0 | 1.2949 | 1.4805 | 15.1051 | 0.67546 | 13.8103

## C3-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 155.5788 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 11
Time-57 | N11 | N12 | Time-58 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R11-G | R3-11
38957.6154 | 1 | 0 | 38957.6154 | 1 | 0 | -78.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38957.6175 | 1 | 0 | 38957.6175 | 1 | 0 | 106.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38957.6196 | 1 | 0 | 38957.6197 | 1 | 0 | 291 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38957.6218 | 1995 | 0 | 38957.6218 | 2022 | 0 | 475.5 | 633.5 | 121.7949 | 0 | 123.4432 | 0 | 1.2179 | 0 | 1.2344 | 0 | 1.2179 | 1.2344 | 27.7383 | 26.0326 | 26.5204
38957.6239 | 2304 | 0 | 38957.6239 | 2532 | 0 | 660.5 | 818.5 | 140.6593 | 0 | 154.5788 | 0 | 1.4066 | 0 | 1.5458 | 0 | 1.4066 | 1.5458 | 10.6068 | 0.64692 | 9.2002

## C3-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 154.5409 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 10
Time-55 | N11 | N12 | Time-56 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38957.6153 | 1 | 0 | 38957.6153 | 1 | 0 | -81.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38957.6175 | 1 | 0 | 38957.6175 | 1 | 0 | 103.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38957.6196 | 1 | 0 | 38957.6196 | 1 | 0 | 288 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38957.6217 | 2220 | 0 | 38957.6218 | 2515 | 0 | 473 | 631 | 135.5311 | 0 | 153.5409 | 0 | 1.3553 | 0 | 1.5354 | 0 | 1.3553 | 1.5354 | 14.0261 | 0.65129 | 12.6708
38957.6239 | 2070 | 0 | 38957.6239 | 2289 | 0 | 657.5 | 815.5 | 126.3736 | 0 | 139.7436 | 0 | 1.2637 | 0 | 1.3974 | 0 | 1.2637 | 1.3974 | 22.2889 | 10.5889 | 21.0252

## C3-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 147.8864 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 9
Time-53 | N11 | N12 | Time-54 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38957.6153 | 1 | 0 | 38957.6153 | 1 | 0 | -84 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38957.6174 | 1 | 0 | 38957.6174 | 1 | 0 | 100.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38957.6196 | 1 | 0 | 38957.6196 | 1 | 0 | 285.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38957.6217 | 2406 | 0 | 38957.6217 | 2176 | 0 | 470 | 628 | 146.8864 | 0 | 132.8449 | 0 | 1.4689 | 0 | 1.3284 | 0 | 1.4689 | 1.3284 | 0.6808 | 11.3226 | 0.78807
38957.6238 | 2269 | 0 | 38957.6239 | 2027 | 0 | 655 | 813 | 138.5226 | 0 | 123.7485 | 0 | 1.3852 | 0 | 1.2375 | 0 | 1.3852 | 1.2375 | 6.7598 | 19.5057 | 5.3746

## C3-8
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 155.5788 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 8
Time-51 | N11 | N12 | Time-52 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38957.6153 | 1 | 0 | 38957.6153 | 1 | 0 | -87 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38957.6174 | 1 | 0 | 38957.6174 | 1 | 0 | 98 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38957.6195 | 1 | 0 | 38957.6195 | 1 | 0 | 282.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38957.6217 | 2519 | 0 | 38957.6217 | 2532 | 0 | 467.5 | 625.5 | 153.7851 | 0 | 154.5788 | 0 | 1.5379 | 0 | 1.5458 | 0 | 1.5379 | 1.5458 | 1.1663 | 0.64692 | 0.37152
38957.6238 | 2520 | 0 | 38957.6238 | 2108 | 0 | 652 | 810 | 153.8462 | 0 | 128.6935 | 0 | 1.5385 | 0 | 1.2869 | 0 | 1.5385 | 1.2869 | 1.1262 | 20.8909 | 0.41227

## C3-7
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 150.8779 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 7
Time-49 | N11 | N12 | Time-50 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38957.6152 | 1 | 0 | 38957.6152 | 1 | 0 | -90 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247038 | 247038 | 247037.9994
38957.6174 | 1 | 0 | 38957.6174 | 1 | 0 | 95 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247038 | 247038 | 247037.9994
38957.6195 | 1 | 0 | 38957.6195 | 1 | 0 | 280 | 438 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247038 | 247038 | 247037.9994
38957.6216 | 2183 | 0 | 38957.6217 | 2071 | 0 | 464.5 | 622.5 | 133.2723 | 0 | 126.4347 | 0 | 1.3327 | 0 | 1.2643 | 0 | 1.3327 | 1.2643 | 13.2103 | 19.3327 | 11.8775
38957.6238 | 2153 | 0 | 38957.6238 | 2455 | 0 | 649.5 | 807.5 | 131.4408 | 0 | 149.8779 | 0 | 1.3144 | 0 | 1.4988 | 0 | 1.3144 | 1.4988 | 14.7877 | 0.66721 | 13.4733

## C3-6
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.8608 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 6
Time-47 | N11 | N12 | Time-48 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38957.6152 | 1 | 0 | 38957.6152 | 1 | 0 | -92.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256838 | 256838 | 256837.9994
38957.6173 | 1 | 0 | 38957.6173 | 1 | 0 | 92 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256838 | 256838 | 256837.9994
38957.6195 | 1 | 0 | 38957.6195 | 1 | 0 | 277 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256838 | 256838 | 256837.9994
38957.6216 | 2553 | 0 | 38957.6216 | 2359 | 0 | 461.5 | 619.5 | 155.8608 | 0 | 144.0171 | 0 | 1.5586 | 0 | 1.4402 | 0 | 1.5586 | 1.4402 | 0.6416 | 8.9182 | 0.91701
38957.6237 | 2446 | 0 | 38957.6238 | 1991 | 0 | 646.5 | 804.5 | 149.3284 | 0 | 121.5507 | 0 | 1.4933 | 0 | 1.2155 | 0 | 1.4933 | 1.2155 | 5.0442 | 29.0497 | 3.5509

## C3-5
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.9829 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 5
Time-45 | N11 | N12 | Time-46 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38957.6152 | 1 | 0 | 38957.6152 | 1 | 0 | -95.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38957.6173 | 1 | 0 | 38957.6173 | 1 | 0 | 89.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38957.6194 | 1 | 0 | 38957.6195 | 1 | 0 | 274.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38957.6216 | 2555 | 0 | 38957.6216 | 2495 | 0 | 459 | 617 | 155.9829 | 0 | 152.3199 | 0 | 1.5598 | 0 | 1.5232 | 0 | 1.5598 | 1.5232 | 0.6411 | 3.0613 | 0.91873
38957.6237 | 2159 | 0 | 38957.6237 | 2386 | 0 | 643.5 | 801.5 | 131.8071 | 0 | 145.6654 | 0 | 1.3181 | 0 | 1.4567 | 0 | 1.3181 | 1.4567 | 19.1005 | 7.7695 | 17.7824

## C3-4
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.6166 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 4
Time-43 | N11 | N12 | Time-44 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38957.6151 | 1 | 0 | 38957.6152 | 1 | 0 | -98 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6173 | 1 | 0 | 38957.6173 | 1 | 0 | 86.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6194 | 1 | 0 | 38957.6194 | 1 | 0 | 271.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6215 | 2079 | 0 | 38957.6216 | 2549 | 0 | 456 | 614 | 126.9231 | 0 | 155.6166 | 0 | 1.2692 | 0 | 1.5562 | 0 | 1.2692 | 1.5562 | 23.3949 | 0.6426 | 22.1257
38957.6237 | 2528 | 0 | 38957.6237 | 2478 | 0 | 641 | 799 | 154.3346 | 0 | 151.2821 | 0 | 1.5433 | 0 | 1.5128 | 0 | 1.5433 | 1.5128 | 1.4786 | 3.5262 | 0.064706

## C2-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 147.337 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 12
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R12-G | R2-12
38957.6151 | 1 | 0 | 38957.6151 | 1 | 0 | -101 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241238 | 241238 | 241237.9994
38957.6172 | 1 | 0 | 38957.6172 | 1 | 0 | 83.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241238 | 241238 | 241237.9994
38957.6194 | 1 | 0 | 38957.6194 | 1 | 0 | 268.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241238 | 241238 | 241237.9994
38957.6215 | 2061 | 0 | 38957.6215 | 2005 | 0 | 453.5 | 611.5 | 125.8242 | 0 | 122.4054 | 0 | 1.2582 | 0 | 1.2241 | 0 | 1.2582 | 1.2241 | 17.0975 | 20.3681 | 15.8393
38957.6236 | 2011 | 0 | 38957.6237 | 2397 | 0 | 638 | 796 | 122.7717 | 0 | 146.337 | 0 | 1.2277 | 0 | 1.4634 | 0 | 1.2277 | 1.4634 | 20.009 | 0.68335 | 18.7812

## C2-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 144.5897 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 11
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R11-G | R2-11
38957.6151 | 1 | 0 | 38957.6151 | 1 | 0 | -104 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38957.6172 | 1 | 0 | 38957.6172 | 1 | 0 | 81 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38957.6193 | 1 | 0 | 38957.6194 | 1 | 0 | 266 | 424 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38957.6215 | 2096 | 0 | 38957.6215 | 2033 | 0 | 450.5 | 608.5 | 127.9609 | 0 | 124.1148 | 0 | 1.2796 | 0 | 1.2411 | 0 | 1.2796 | 1.2411 | 12.9952 | 16.4968 | 11.7156
38957.6236 | 2352 | 0 | 38957.6236 | 2247 | 0 | 635.5 | 793.5 | 143.5897 | 0 | 137.1795 | 0 | 1.4359 | 0 | 1.3718 | 0 | 1.4359 | 1.3718 | 0.69643 | 5.4019 | 0.73947

## C2-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 156.6166 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 10
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R10-G | R2-10
38957.615 | 1 | 0 | 38957.615 | 1 | 0 | -106.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6172 | 1 | 0 | 38957.6172 | 1 | 0 | 78 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6193 | 1 | 0 | 38957.6193 | 1 | 0 | 263 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38957.6214 | 2549 | 0 | 38957.6215 | 2038 | 0 | 448 | 606 | 155.6166 | 0 | 124.42 | 0 | 1.5562 | 0 | 1.2442 | 0 | 1.5562 | 1.2442 | 0.6426 | 25.8773 | 0.91356
38957.6236 | 2005 | 0 | 38957.6236 | 2031 | 0 | 632.5 | 790.5 | 122.4054 | 0 | 123.9927 | 0 | 1.2241 | 0 | 1.2399 | 0 | 1.2241 | 1.2399 | 27.9491 | 26.3112 | 26.7251

## C2-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 138.1795 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 9
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R9-G | R2-9
38957.615 | 1 | 0 | 38957.615 | 1 | 0 | -109.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226238 | 226238 | 226237.9994
38957.6171 | 1 | 0 | 38957.6172 | 1 | 0 | 75.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226238 | 226238 | 226237.9994
38957.6193 | 1 | 0 | 38957.6193 | 1 | 0 | 260 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226238 | 226238 | 226237.9994
38957.6214 | 2185 | 0 | 38957.6214 | 1990 | 0 | 445 | 603 | 133.3944 | 0 | 121.4896 | 0 | 1.3339 | 0 | 1.2149 | 0 | 1.3339 | 1.2149 | 3.5872 | 13.7377 | 2.2532
38957.6236 | 2247 | 0 | 38957.6236 | 2132 | 0 | 629.5 | 787.5 | 137.1795 | 0 | 130.1587 | 0 | 1.3718 | 0 | 1.3016 | 0 | 1.3718 | 1.3016 | 0.72897 | 6.1623 | 0.64282

## C2-8
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 149.9011 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 8
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R8-G | R2-8
38957.615 | 1 | 0 | 38957.615 | 1 | 0 | -112 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38957.6171 | 1 | 0 | 38957.6171 | 1 | 0 | 72.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38957.6192 | 1 | 0 | 38957.6193 | 1 | 0 | 257.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38957.6214 | 2439 | 0 | 38957.6214 | 2380 | 0 | 442 | 600 | 148.9011 | 0 | 145.2991 | 0 | 1.489 | 0 | 1.453 | 0 | 1.489 | 1.453 | 0.67159 | 3.1672 | 0.81742
38957.6235 | 2306 | 0 | 38957.6235 | 2070 | 0 | 627 | 785 | 140.7814 | 0 | 126.3736 | 0 | 1.4078 | 0 | 1.2637 | 0 | 1.4078 | 1.2637 | 6.4779 | 18.6174 | 5.0701

## C2-7
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 157.044 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 7
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38957.6149 | 1 | 0 | 38957.615 | 1 | 0 | -115 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38957.6171 | 1 | 0 | 38957.6171 | 1 | 0 | 70 | 228 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38957.6192 | 1 | 0 |  | 1 | 0 | 254 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38957.6214 | 2489 | 0 | 38957.6214 | 1986 | 0 | 439.5 | 597.5 | 151.9536 | 0 | 121.2454 | 0 | 1.5195 | 0 | 1.2125 | 0 | 1.5195 | 1.2125 | 3.3499 | 29.5257 | 1.8304
38957.6235 | 2556 | 0 | 38957.6235 | 2021 | 0 | 624 | 782 | 156.044 | 0 | 123.3822 | 0 | 1.5604 | 0 | 1.2338 | 0 | 1.5604 | 1.2338 | 0.64085 | 27.2825 | 0.91959

## C2-6
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 155.6398 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 6
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38957.6149 | 1 | 0 | 38957.6149 | 1 | 0 | -117.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
38957.617 | 1 | 0 | 38957.6171 | 1 | 0 | 67 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
38957.6192 | 1 | 0 | 38957.6192 | 1 | 0 | 251.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
38957.6213 | 2533 | 0 | 38957.6213 | 2027 | 0 | 436.5 | 594.5 | 154.6398 | 0 | 123.7485 | 0 | 1.5464 | 0 | 1.2375 | 0 | 1.5464 | 1.2375 | 0.64666 | 25.7711 | 0.89973
38957.6235 | 2368 | 45 | 38957.6235 | 2000 | 0 | 621.5 | 779.5 | 144.5665 | 2.7473 | 122.1001 | 0 | 1.4457 | 0.027473 | 1.221 | 0 | 1.4182 | 1.221 | 8.4004 | 27.469 | 65.3095

## C2-5
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 149.4737 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 5
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38957.6149 | 1 | 0 | 38957.6149 | 1 | 0 | -120.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244738 | 244738 | 244737.9994
38957.617 | 1 | 0 | 38957.617 | 1 | 0 | 64 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244738 | 244738 | 244737.9994
38957.6191 | 1 | 0 | 38957.6192 | 1 | 0 | 249 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244738 | 244738 | 244737.9994
38957.6213 | 2345 | 43 | 38957.6213 | 2048 | 0 | 433.5 | 591.5 | 143.1624 | 2.6252 | 125.0305 | 0 | 1.4316 | 0.026252 | 1.2503 | 0 | 1.4054 | 1.2503 | 4.9653 | 19.5498 | 22.9624
38957.6234 | 2117 | 0 | 38957.6234 | 2432 | 0 | 618.5 | 776.5 | 129.243 | 0 | 148.4737 | 0 | 1.2924 | 0 | 1.4847 | 0 | 1.2924 | 1.4847 | 15.6533 | 0.67352 | 14.3609

## C2-4
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 149.0464 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 4
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38957.6148 | 1 | 0 | 38957.6148 | 1 | 0 | -123.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.617 | 1 | 0 | 38957.617 | 1 | 0 | 61.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6191 | 1 | 0 | 38957.6191 | 1 | 0 | 246 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38957.6212 | 2425 | 0 | 38957.6213 | 988 | 949 | 431 | 589 | 148.0464 | 0 | 60.3175 | 57.9365 | 1.4805 | 0 | 0.60317 | 0.57937 | 1.4805 | 0.02381 | 0.67546 | 6159.9487 | 0.805
38957.6234 | 2342 | 0 | 38957.6234 | 2312 | 0 | 615.5 | 773.5 | 142.9792 | 0 | 141.1477 | 0 | 1.4298 | 0 | 1.4115 | 0 | 1.4298 | 1.4115 | 4.2434 | 5.596 | 2.8136

## C2-3
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 135.3101 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 3
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38957.6148 | 1 | 0 | 38957.6148 | 1 | 0 | -126 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221538 | 221538 | 221537.9994
38957.6169 | 1 | 0 | 38957.617 | 1 | 0 | 58.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221538 | 221538 | 221537.9994
38957.6191 | 1 | 0 | 38957.6191 | 1 | 0 | 243.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221538 | 221538 | 221537.9994
38957.6212 | 1147 | 1174 | 38957.6212 | 934 | 911 | 428 | 586 | 70.0244 | 71.6728 | 57.0208 | 55.6166 | 0.70024 | 0.71673 | 0.57021 | 0.55617 | 0.016484 | 0.014042 | 3959.9479 | 23955359.0799 | 8.9114
38957.6234 | 1993 | 0 | 38957.6234 | 2200 | 0 | 613 | 771 | 121.6728 | 0 | 134.3101 | 0 | 1.2167 | 0 | 1.3431 | 0 | 1.2167 | 1.3431 | 11.2082 | 0.74455 | 9.9915

## C1-12
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 157.1661 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 12
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R12-G | R1-12
38957.6148 | 1 | 0 | 38957.6148 | 1 | 0 | -129 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
38957.6169 | 1 | 0 | 38957.6169 | 1 | 0 | 55.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
38957.6191 | 1 | 0 | 38957.6191 | 1 | 0 | 240.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
38957.6212 | 2293 | 0 | 38957.6212 | 1 | 0 | 425.5 | 583.5 | 139.9878 | 0 | 0.06105 | 0 | 1.3999 | 0 | 0.0006105 | 0 | 1.3999 | 0.0006105 | 12.2713 | 257338 | 10.8714
38957.6233 | 2357 | 0 | 38957.6233 | 2558 | 0 | 610 | 768 | 143.895 | 0 | 156.1661 | 0 | 1.4389 | 0 | 1.5617 | 0 | 1.4389 | 1.5617 | 9.2227 | 0.64034 | 7.7838

## C1-11
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 157.2271 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 11
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R11-G | R1-11
38957.6147 | 1 | 0 | 38957.6148 | 1 | 0 | -131.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.6169 | 1 | 0 | 38957.6169 | 1 | 0 | 53 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.619 | 1 | 0 | 38957.619 | 1 | 0 | 237.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
38957.6212 | 2524 | 0 | 38957.6212 | 2301 | 0 | 422.5 | 580.5 | 154.0904 | 0 | 140.4762 | 0 | 1.5409 | 0 | 1.4048 | 0 | 1.5409 | 1.4048 | 2.0357 | 11.9244 | 0.49475
38957.6233 | 2559 | 0 | 38957.6233 | 2063 | 0 | 607.5 | 765.5 | 156.2271 | 0 | 125.9463 | 0 | 1.5623 | 0 | 1.2595 | 0 | 1.5623 | 1.2595 | 0.64009 | 24.8366 | 0.92218

## C1-10
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 157.2882 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 10
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R10-G | R1-10
38957.6147 | 1 | 0 | 38957.6147 | 1 | 0 | -134.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38957.6169 | 1 | 0 | 38957.6169 | 1 | 0 | 50.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38957.619 | 1 | 0 | 38957.619 | 1 | 0 | 235 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38957.6211 | 2528 | 0 | 38957.6211 | 2306 | 0 | 419.5 | 577.5 | 154.3346 | 0 | 140.7814 | 0 | 1.5433 | 0 | 1.4078 | 0 | 1.5433 | 1.4078 | 1.9138 | 11.7251 | 0.37042
38957.6233 | 2560 | 0 | 38957.6233 | 2468 | 0 | 604.5 | 762.5 | 156.2882 | 0 | 150.6716 | 0 | 1.5629 | 0 | 1.5067 | 0 | 1.5629 | 1.5067 | 0.63984 | 4.3914 | 0.92304

## C1-9
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 146.9707 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 9
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R9-G | R1-9
38957.6147 | 1 | 0 | 38957.6147 | 1 | 0 | -137.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38957.6168 | 1 | 0 | 38957.6168 | 1 | 0 | 47.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38957.6189 | 1 | 0 | 38957.619 | 1 | 0 | 232 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
38957.6211 | 2388 | 0 | 38957.6211 | 1 | 0 | 417 | 575 | 145.7875 | 0 | 0.06105 | 0 | 1.4579 | 0 | 0.0006105 | 0 | 1.4579 | 0.0006105 | 0.81156 | 240638 | 0.64632
38957.6232 | 2131 | 0 | 38957.6232 | 2391 | 0 | 601.5 | 759.5 | 130.0977 | 0 | 145.9707 | 0 | 1.301 | 0 | 1.4597 | 0 | 1.301 | 1.4597 | 12.9695 | 0.68507 | 11.6685

## C1-8
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 139.8278 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 8
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R8-G | R1-8
38957.6146 | 1 | 0 | 38957.6147 | 1 | 0 | -140 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228938 | 228938 | 228937.9994
38957.6168 | 1 | 0 | 38957.6168 | 1 | 0 | 44.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228938 | 228938 | 228937.9994
38957.6189 | 1 | 0 | 38957.6189 | 1 | 0 | 229.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228938 | 228938 | 228937.9994
38957.6211 | 1 | 0 | 38957.6211 | 1 | 0 | 414 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228938 | 228938 | 228937.9994
38957.6232 | 2105 | 0 | 38957.6232 | 2274 | 0 | 599 | 757 | 128.5104 | 0 | 138.8278 | 0 | 1.2851 | 0 | 1.3883 | 0 | 1.2851 | 1.3883 | 8.8067 | 0.72032 | 7.5215

## C1-7
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 129 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38957.6146 | 1 | 0 | 38957.6146 | 1 | 0 | -143 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.6167 | 1 | 0 | 38957.6168 | 1 | 0 | 42 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.6189 | 1 | 0 | 38957.6189 | 1 | 0 | 226.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.621 | 1 | 0 | 38957.621 | 1 | 0 | 411.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.6232 | 2007 | 0 | 38957.6232 | 1979 | 0 | 596 | 754 | 122.5275 | 0 | 120.8181 | 0 | 1.2253 | 0 | 1.2082 | 0 | 1.2253 | 1.2082 | 5.2825 | 6.7721 | 4.0572

## C1-6
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 145.7497 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38957.6146 | 1 | 0 | 38957.6146 | 1 | 0 | -145.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38957.6167 | 1 | 0 | 38957.6167 | 1 | 0 | 39 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38957.6189 | 1 | 0 | 38957.6189 | 1 | 0 | 224 | 382 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38957.621 | 1 | 0 | 38957.621 | 1 | 0 | 408.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238638 | 238638 | 238637.9994
38957.6231 | 2371 | 0 | 38957.6231 | 2024 | 0 | 593.5 | 751.5 | 144.7497 | 0 | 123.5653 | 0 | 1.4475 | 0 | 1.2357 | 0 | 1.4475 | 1.2357 | 0.69085 | 17.9536 | 0.75665

## C1-5
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 146.4212 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38957.6145 | 1 | 0 | 38957.6146 | 1 | 0 | -148.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38957.6167 | 1 | 0 | 38957.6167 | 1 | 0 | 36 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38957.6188 | 1 | 0 | 38957.6188 | 1 | 0 | 221 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38957.621 | 1 | 0 | 38957.621 | 1 | 0 | 405.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
38957.6231 | 2382 | 0 | 38957.6231 | 2198 | 0 | 590.5 | 748.5 | 145.4212 | 0 | 134.188 | 0 | 1.4542 | 0 | 1.3419 | 0 | 1.4542 | 1.3419 | 0.68766 | 9.1165 | 0.76656

## C1-4
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 155.4567 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38957.6145 | 1 | 0 | 38957.6145 | 1 | 0 | -151.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38957.6167 | 1 | 0 | 38957.6167 | 1 | 0 | 33.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38957.6188 | 1 | 0 | 38957.6188 | 1 | 0 | 218.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38957.6209 | 1 | 0 | 38957.6209 | 1 | 0 | 403 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38957.6231 | 2125 | 0 | 38957.6231 | 2530 | 0 | 587.5 | 745.5 | 129.7314 | 0 | 154.4567 | 0 | 1.2973 | 0 | 1.5446 | 0 | 1.2973 | 1.5446 | 19.8296 | 0.64743 | 18.5323

## C1-3
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 144.7729 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38957.6145 | 1 | 0 | 38957.6145 | 1 | 0 | -154 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237038 | 237038 | 237037.9994
38957.6166 | 1 | 0 | 38957.6166 | 1 | 0 | 30.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237038 | 237038 | 237037.9994
38957.6188 | 1 | 0 | 38957.6188 | 1 | 0 | 215.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237038 | 237038 | 237037.9994
38957.6209 | 1 | 0 | 38957.6209 | 1 | 0 | 400.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237038 | 237038 | 237037.9994
38957.623 | 2355 | 0 | 38957.6231 | 1993 | 0 | 585 | 743 | 143.7729 | 0 | 121.6728 | 0 | 1.4377 | 0 | 1.2167 | 0 | 1.4377 | 1.2167 | 0.69554 | 18.9854 | 0.74219

## C1-2
Penlight Test 63 |  |  | 2006-08-28 | 14:47 |  | Vs = |  | 144.2845 |  | R = | 100
PVC | 12-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38957.6144 | 1 | 0 | 38957.6145 | 1 | 0 | -157 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38957.6166 | 1 | 0 | 38957.6166 | 1 | 0 | 28 | 186 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38957.6187 | 1 | 0 | 38957.6187 | 1 | 0 | 212.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38957.6209 | 1 | 0 | 38957.6209 | 1 | 0 | 397.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38957.623 | 2347 | 0 | 38957.623 | 2303 | 0 | 582 | 740 | 143.2845 | 0 | 140.5983 | 0 | 1.4328 | 0 | 1.406 | 0 | 1.4328 | 1.406 | 0.69791 | 2.6218 | 0.73493

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 63 |  |  | 2006-08-28 | 14:47
38957.6144 | 1 | 0 | 1 | PVC | 12-C | Tray
38957.6166 | 1 | 0 | 1 | 325 C | 7.2 kW/m2 |  | Conductors
38957.6187 | 1 | 0 | 1
38957.6209 | 1 | 0 | 1
38957.623 | 2347 | 0 | 1
1
38957.6145 | 1 | 0 | 2
38957.6166 | 1 | 0 | 2
38957.6187 | 1 | 0 | 2
38957.6209 | 1 | 0 | 2
38957.623 | 2303 | 0 | 2
2
38957.6145 | 1 | 0 | 3
38957.6166 | 1 | 0 | 3
38957.6188 | 1 | 0 | 3
38957.6209 | 1 | 0 | 3
38957.623 | 2355 | 0 | 3
3
38957.6145 | 1 | 0 | 4
38957.6166 | 1 | 0 | 4
38957.6188 | 1 | 0 | 4
38957.6209 | 1 | 0 | 4
38957.6231 | 1993 | 0 | 4
4
38957.6145 | 1 | 0 | 5
38957.6167 | 1 | 0 | 5
38957.6188 | 1 | 0 | 5
38957.6209 | 1 | 0 | 5
38957.6231 | 2125 | 0 | 5
5
38957.6145 | 1 | 0 | 6
38957.6167 | 1 | 0 | 6
38957.6188 | 1 | 0 | 6
38957.6209 | 1 | 0 | 6
38957.6231 | 2530 | 0 | 6
6
38957.6145 | 1 | 0 | 7
38957.6167 | 1 | 0 | 7
38957.6188 | 1 | 0 | 7
38957.621 | 1 | 0 | 7
38957.6231 | 2382 | 0 | 7
7
38957.6146 | 1 | 0 | 8
38957.6167 | 1 | 0 | 8
38957.6188 | 1 | 0 | 8
38957.621 | 1 | 0 | 8
38957.6231 | 2198 | 0 | 8
8
38957.6146 | 1 | 0 | 9
38957.6167 | 1 | 0 | 9
38957.6189 | 1 | 0 | 9
38957.621 | 1 | 0 | 9
38957.6231 | 2371 | 0 | 9
9
38957.6146 | 1 | 0 | 10
38957.6167 | 1 | 0 | 10
38957.6189 | 1 | 0 | 10
38957.621 | 1 | 0 | 10
38957.6231 | 2024 | 0 | 10
10
38957.6146 | 1 | 0 | 11
38957.6167 | 1 | 0 | 11
38957.6189 | 1 | 0 | 11
38957.621 | 1 | 0 | 11
38957.6232 | 2007 | 0 | 11
11
38957.6146 | 1 | 0 | 12
38957.6168 | 1 | 0 | 12
38957.6189 | 1 | 0 | 12
38957.621 | 1 | 0 | 12
38957.6232 | 1979 | 0 | 12
12
38957.6146 | 1 | 0 | 13
38957.6168 | 1 | 0 | 13
38957.6189 | 1 | 0 | 13
38957.6211 | 1 | 0 | 13
38957.6232 | 2105 | 0 | 13
13
38957.6147 | 1 | 0 | 14
38957.6168 | 1 | 0 | 14
38957.6189 | 1 | 0 | 14
38957.6211 | 1 | 0 | 14
38957.6232 | 2274 | 0 | 14
14
38957.6147 | 1 | 0 | 15
38957.6168 | 1 | 0 | 15
38957.6189 | 1 | 0 | 15
38957.6211 | 2388 | 0 | 15
38957.6232 | 2131 | 0 | 15
15
38957.6147 | 1 | 0 | 16
38957.6168 | 1 | 0 | 16
38957.619 | 1 | 0 | 16
38957.6211 | 1 | 0 | 16
38957.6232 | 2391 | 0 | 16
16
38957.6147 | 1 | 0 | 17
38957.6169 | 1 | 0 | 17
38957.619 | 1 | 0 | 17
38957.6211 | 2528 | 0 | 17
38957.6233 | 2560 | 0 | 17
17
38957.6147 | 1 | 0 | 18
38957.6169 | 1 | 0 | 18
38957.619 | 1 | 0 | 18
38957.6211 | 2306 | 0 | 18
38957.6233 | 2468 | 0 | 18
18
38957.6147 | 1 | 0 | 19
38957.6169 | 1 | 0 | 19
38957.619 | 1 | 0 | 19
38957.6212 | 2524 | 0 | 19
38957.6233 | 2559 | 0 | 19
19
38957.6148 | 1 | 0 | 20
38957.6169 | 1 | 0 | 20
38957.619 | 1 | 0 | 20
38957.6212 | 2301 | 0 | 20
38957.6233 | 2063 | 0 | 20
20
38957.6148 | 1 | 0 | 21
38957.6169 | 1 | 0 | 21
38957.6191 | 1 | 0 | 21
38957.6212 | 2293 | 0 | 21
38957.6233 | 2357 | 0 | 21
21
38957.6148 | 1 | 0 | 22
38957.6169 | 1 | 0 | 22
38957.6191 | 1 | 0 | 22
38957.6212 | 1 | 0 | 22
38957.6233 | 2558 | 0 | 22
22
38957.6148 | 1 | 0 | 23
38957.6169 | 1 | 0 | 23
38957.6191 | 1 | 0 | 23
38957.6212 | 1147 | 1174 | 23
38957.6234 | 1993 | 0 | 23
23
38957.6148 | 1 | 0 | 24
38957.617 | 1 | 0 | 24
38957.6191 | 1 | 0 | 24
38957.6212 | 934 | 911 | 24
38957.6234 | 2200 | 0 | 24
24
38957.6148 | 1 | 0 | 25
38957.617 | 1 | 0 | 25
38957.6191 | 1 | 0 | 25
38957.6212 | 2425 | 0 | 25
38957.6234 | 2342 | 0 | 25
25
38957.6148 | 1 | 0 | 26
38957.617 | 1 | 0 | 26
38957.6191 | 1 | 0 | 26
38957.6213 | 988 | 949 | 26
38957.6234 | 2312 | 0 | 26
26
38957.6149 | 1 | 0 | 27
38957.617 | 1 | 0 | 27
38957.6191 | 1 | 0 | 27
38957.6213 | 2345 | 43 | 27
38957.6234 | 2117 | 0 | 27
27
38957.6149 | 1 | 0 | 28
38957.617 | 1 | 0 | 28
38957.6192 | 1 | 0 | 28
38957.6213 | 2048 | 0 | 28
38957.6234 | 2432 | 0 | 28
28
38957.6149 | 1 | 0 | 29
38957.617 | 1 | 0 | 29
38957.6192 | 1 | 0 | 29
38957.6213 | 2533 | 0 | 29
38957.6235 | 2368 | 45 | 29
29
38957.6149 | 1 | 0 | 30
38957.6171 | 1 | 0 | 30
38957.6192 | 1 | 0 | 30
38957.6213 | 2027 | 0 | 30
38957.6235 | 2000 | 0 | 30
30
38957.6149 | 1 | 0 | 31
38957.6171 | 1 | 0 | 31
38957.6192 | 1 | 0 | 31
38957.6214 | 2489 | 0 | 31
38957.6235 | 2556 | 0 | 31
31
38957.615 | 1 | 0 | 32
38957.6171 | 1 | 0 | 32
38957.6214 | 1986 | 0 | 32
38957.6235 | 2021 | 0 | 32
32
38957.615 | 1 | 0 | 33
38957.6171 | 1 | 0 | 33
38957.6192 | 1 | 0 | 33
38957.6214 | 2439 | 0 | 33
38957.6235 | 2306 | 0 | 33
33
38957.615 | 1 | 0 | 34
38957.6171 | 1 | 0 | 34
38957.6193 | 1 | 0 | 34
38957.6214 | 2380 | 0 | 34
38957.6235 | 2070 | 0 | 34
34
38957.615 | 1 | 0 | 35
38957.6171 | 1 | 0 | 35
38957.6193 | 1 | 0 | 35
38957.6214 | 2185 | 0 | 35
38957.6236 | 2247 | 0 | 35
35
38957.615 | 1 | 0 | 36
38957.6172 | 1 | 0 | 36
38957.6193 | 1 | 0 | 36
38957.6214 | 1990 | 0 | 36
38957.6236 | 2132 | 0 | 36
36
38957.615 | 1 | 0 | 37
38957.6172 | 1 | 0 | 37
38957.6193 | 1 | 0 | 37
38957.6214 | 2549 | 0 | 37
38957.6236 | 2005 | 0 | 37
37
38957.615 | 1 | 0 | 38
38957.6172 | 1 | 0 | 38
38957.6193 | 1 | 0 | 38
38957.6215 | 2038 | 0 | 38
38957.6236 | 2031 | 0 | 38
38
38957.6151 | 1 | 0 | 39
38957.6172 | 1 | 0 | 39
38957.6193 | 1 | 0 | 39
38957.6215 | 2096 | 0 | 39
38957.6236 | 2352 | 0 | 39
39
38957.6151 | 1 | 0 | 40
38957.6172 | 1 | 0 | 40
38957.6194 | 1 | 0 | 40
38957.6215 | 2033 | 0 | 40
38957.6236 | 2247 | 0 | 40
40
38957.6151 | 1 | 0 | 41
38957.6172 | 1 | 0 | 41
38957.6194 | 1 | 0 | 41
38957.6215 | 2061 | 0 | 41
38957.6236 | 2011 | 0 | 41
41
38957.6151 | 1 | 0 | 42
38957.6172 | 1 | 0 | 42
38957.6194 | 1 | 0 | 42
38957.6215 | 2005 | 0 | 42
38957.6237 | 2397 | 0 | 42
42
38957.6151 | 1 | 0 | 43
38957.6173 | 1 | 0 | 43
38957.6194 | 1 | 0 | 43
38957.6215 | 2079 | 0 | 43
38957.6237 | 2528 | 0 | 43
43
38957.6152 | 1 | 0 | 44
38957.6173 | 1 | 0 | 44
38957.6194 | 1 | 0 | 44
38957.6216 | 2549 | 0 | 44
38957.6237 | 2478 | 0 | 44
44
38957.6152 | 1 | 0 | 45
38957.6173 | 1 | 0 | 45
38957.6194 | 1 | 0 | 45
38957.6216 | 2555 | 0 | 45
38957.6237 | 2159 | 0 | 45
45
38957.6152 | 1 | 0 | 46
38957.6173 | 1 | 0 | 46
38957.6195 | 1 | 0 | 46
38957.6216 | 2495 | 0 | 46
38957.6237 | 2386 | 0 | 46
46
38957.6152 | 1 | 0 | 47
38957.6173 | 1 | 0 | 47
38957.6195 | 1 | 0 | 47
38957.6216 | 2553 | 0 | 47
38957.6237 | 2446 | 0 | 47
47
38957.6152 | 1 | 0 | 48
38957.6173 | 1 | 0 | 48
38957.6195 | 1 | 0 | 48
38957.6216 | 2359 | 0 | 48
38957.6238 | 1991 | 0 | 48
48
38957.6152 | 1 | 0 | 49
38957.6174 | 1 | 0 | 49
38957.6195 | 1 | 0 | 49
38957.6216 | 2183 | 0 | 49
38957.6238 | 2153 | 0 | 49
49
38957.6152 | 1 | 0 | 50
38957.6174 | 1 | 0 | 50
38957.6195 | 1 | 0 | 50
38957.6217 | 2071 | 0 | 50
38957.6238 | 2455 | 0 | 50
50
38957.6153 | 1 | 0 | 51
38957.6174 | 1 | 0 | 51
38957.6195 | 1 | 0 | 51
38957.6217 | 2519 | 0 | 51
38957.6238 | 2520 | 0 | 51
51
38957.6153 | 1 | 0 | 52
38957.6174 | 1 | 0 | 52
38957.6195 | 1 | 0 | 52
38957.6217 | 2532 | 0 | 52
38957.6238 | 2108 | 0 | 52
52
38957.6153 | 1 | 0 | 53
38957.6174 | 1 | 0 | 53
38957.6196 | 1 | 0 | 53
38957.6217 | 2406 | 0 | 53
38957.6238 | 2269 | 0 | 53
53
38957.6153 | 1 | 0 | 54
38957.6174 | 1 | 0 | 54
38957.6196 | 1 | 0 | 54
38957.6217 | 2176 | 0 | 54
38957.6239 | 2027 | 0 | 54
54
38957.6153 | 1 | 0 | 55
38957.6175 | 1 | 0 | 55
38957.6196 | 1 | 0 | 55
38957.6217 | 2220 | 0 | 55
38957.6239 | 2070 | 0 | 55
55
38957.6153 | 1 | 0 | 56
38957.6175 | 1 | 0 | 56
38957.6196 | 1 | 0 | 56
38957.6218 | 2515 | 0 | 56
38957.6239 | 2289 | 0 | 56
56
38957.6154 | 1 | 0 | 57
38957.6175 | 1 | 0 | 57
38957.6196 | 1 | 0 | 57
38957.6218 | 1995 | 0 | 57
38957.6239 | 2304 | 0 | 57
57
38957.6154 | 1 | 0 | 58
38957.6175 | 1 | 0 | 58
38957.6197 | 1 | 0 | 58
38957.6218 | 2022 | 0 | 58
38957.6239 | 2532 | 0 | 58
58
38957.6154 | 1 | 0 | 59
38957.6175 | 1 | 0 | 59
38957.6197 | 1 | 0 | 59
38957.6218 | 2224 | 0 | 59
38957.6239 | 2121 | 0 | 59
59
38957.6154 | 1 | 0 | 60
38957.6175 | 1 | 0 | 60
38957.6197 | 1 | 0 | 60
38957.6218 | 2159 | 0 | 60
38957.624 | 2425 | 0 | 60
60
38957.6154 | 1 | 0 | 61
38957.6176 | 1 | 0 | 61
38957.6197 | 1 | 0 | 61
38957.6218 | 2268 | 0 | 61
38957.624 | 2258 | 0 | 61
61
38957.6154 | 1 | 0 | 62
38957.6176 | 1 | 0 | 62
38957.6197 | 1 | 0 | 62
38957.6219 | 2365 | 0 | 62
38957.624 | 2185 | 0 | 62
62
38957.6155 | 1 | 0 | 63
38957.6176 | 1 | 0 | 63
38957.6197 | 1 | 0 | 63
38957.6219 | 2510 | 0 | 63
38957.624 | 2237 | 0 | 63
63
38957.6155 | 1 | 0 | 64
38957.6176 | 1 | 0 | 64
38957.6197 | 1 | 0 | 64
38957.6219 | 2017 | 0 | 64
38957.624 | 2500 | 0 | 64
64
38957.6155 | 1 | 0 | 65
38957.6176 | 1 | 0 | 65
38957.6198 | 1 | 0 | 65
38957.6219 | 2234 | 0 | 65
38957.624 | 2471 | 0 | 65
65
38957.6155 | 1 | 0 | 66
38957.6176 | 1 | 0 | 66
38957.6198 | 1 | 0 | 66
38957.6219 | 2487 | 24 | 66
38957.6241 | 2038 | 0 | 66
66
38957.6155 | 1 | 0 | 67
38957.6177 | 1 | 0 | 67
38957.6198 | 1 | 0 | 67
38957.6219 | 2533 | 0 | 67
38957.6241 | 2098 | 0 | 67
67
38957.6155 | 1 | 0 | 68
38957.6177 | 1 | 0 | 68
38957.6198 | 1 | 0 | 68
38957.6219 | 2516 | 0 | 68
38957.6241 | 2541 | 0 | 68
68
38957.6156 | 1 | 0 | 69
38957.6177 | 1 | 0 | 69
38957.6198 | 1 | 0 | 69
38957.622 | 2546 | 0 | 69
38957.6241 | 2541 | 0 | 69
69
38957.6156 | 1 | 0 | 70
38957.6177 | 1 | 0 | 70
38957.6198 | 1 | 0 | 70
38957.622 | 2548 | 0 | 70
38957.6241 | 2518 | 0 | 70
70
38957.6156 | 1 | 0 | 71
38957.6177 | 1 | 0 | 71
38957.6199 | 1 | 0 | 71
38957.622 | 2038 | 10 | 71
38957.6241 | 1981 | 0 | 71
71
38957.6156 | 1 | 0 | 72
38957.6177 | 1 | 0 | 72
38957.6199 | 1 | 0 | 72
38957.622 | 2118 | 578 | 72
38957.6242 | 2166 | 0 | 72
72
38957.6156 | 1 | 0 | 73
38957.6178 | 1 | 0 | 73
38957.6199 | 1 | 0 | 73
38957.622 | 2442 | 0 | 73
38957.6242 | 2458 | 0 | 73
73
38957.6156 | 1 | 0 | 74
38957.6178 | 1 | 0 | 74
38957.6199 | 1 | 0 | 74
38957.622 | 2554 | 0 | 74
38957.6242 | 2182 | 0 | 74
74
38957.6156 | 1 | 0 | 75
38957.6178 | 1 | 0 | 75
38957.6199 | 1 | 0 | 75
38957.6221 | 1779 | 594 | 75
38957.6242 | 1972 | 0 | 75
75
38957.6157 | 1 | 0 | 76
38957.6178 | 1 | 0 | 76
38957.6199 | 1 | 0 | 76
38957.6221 | 2554 | 2 | 76
38957.6242 | 2243 | 0 | 76
76
38957.6157 | 1 | 0 | 77
38957.6178 | 1 | 0 | 77
38957.62 | 1 | 0 | 77
38957.6221 | 2335 | 1 | 77
38957.6242 | 2182 | 0 | 77
77
38957.6157 | 1 | 0 | 78
38957.6178 | 1 | 0 | 78
38957.62 | 1 | 0 | 78
38957.6221 | 2124 | 0 | 78
38957.6242 | 2550 | 0 | 78
78
38957.6157 | 1 | 0 | 79
38957.6178 | 1 | 0 | 79
38957.62 | 1 | 0 | 79
38957.6221 | 2525 | 0 | 79
38957.6243 | 2458 | 0 | 79
79
38957.6157 | 1 | 0 | 80
38957.6179 | 1 | 0 | 80
38957.62 | 1 | 0 | 80
38957.6221 | 2317 | 0 | 80
38957.6243 | 2549 | 0 | 80
80
38957.6157 | 1 | 0 | 81
38957.6179 | 1 | 0 | 81
38957.62 | 1 | 0 | 81
38957.6222 | 2014 | 334 | 81
38957.6243 | 2063 | 0 | 81
81
38957.6158 | 1 | 0 | 82
38957.6179 | 1 | 0 | 82
38957.62 | 1 | 0 | 82
38957.6222 | 2048 | 1 | 82
38957.6243 | 2443 | 0 | 82
82
38957.6158 | 1 | 0 | 83
38957.6179 | 1 | 0 | 83
38957.6201 | 1 | 0 | 83
38957.6222 | 2210 | 0 | 83
38957.6243 | 2308 | 0 | 83
83
38957.6158 | 1 | 0 | 84
38957.6179 | 1 | 0 | 84
38957.6201 | 1 | 0 | 84
38957.6222 | 2452 | 0 | 84
38957.6244 | 1988 | 0 | 84
84
38957.6158 | 1 | 0 | 85
38957.618 | 1 | 0 | 85
38957.6201 | 1 | 0 | 85
38957.6222 | 2002 | 0 | 85
38957.6244 | 1985 | 0 | 85
85
38957.6158 | 1 | 0 | 86
38957.618 | 1 | 0 | 86
38957.6201 | 1 | 0 | 86
38957.6222 | 2406 | 0 | 86
38957.6244 | 2239 | 0 | 86
86
38957.6158 | 1 | 0 | 87
38957.618 | 1 | 0 | 87
38957.6201 | 1 | 0 | 87
38957.6223 | 2023 | 0 | 87
38957.6244 | 2000 | 0 | 87
87
38957.6159 | 1 | 0 | 88
38957.618 | 2 | 0 | 88
38957.6201 | 1 | 0 | 88
38957.6223 | 2201 | 0 | 88
38957.6244 | 1990 | 0 | 88
88
38957.6159 | 1 | 0 | 89
38957.618 | 1 | 0 | 89
38957.6202 | 1 | 0 | 89
38957.6223 | 2296 | 0 | 89
38957.6244 | 2297 | 0 | 89
89
38957.6159 | 1 | 0 | 90
38957.618 | 1 | 0 | 90
38957.6202 | 1 | 0 | 90
38957.6223 | 2079 | 0 | 90
38957.6244 | 2522 | 0 | 90
90
38957.6159 | 1 | 0 | 91
38957.618 | 1 | 0 | 91
38957.6202 | 1 | 0 | 91
38957.6223 | 2410 | 0 | 91
38957.6245 | 2129 | 0 | 91
91
38957.6159 | 1 | 0 | 92
38957.6181 | 1 | 0 | 92
38957.6202 | 1 | 0 | 92
38957.6223 | 2094 | 0 | 92
38957.6245 | 2360 | 0 | 92
92
38957.6159 | 1 | 0 | 93
38957.6181 | 1 | 0 | 93
38957.6202 | 1 | 0 | 93
38957.6223 | 2426 | 0 | 93
38957.6245 | 2494 | 0 | 93
93
38957.616 | 1 | 0 | 94
38957.6181 | 1 | 0 | 94
38957.6202 | 1 | 0 | 94
38957.6224 | 2386 | 0 | 94
38957.6245 | 2389 | 0 | 94
94
38957.616 | 1 | 0 | 95
38957.6181 | 1 | 0 | 95
38957.6202 | 1 | 0 | 95
38957.6224 | 2292 | 0 | 95
38957.6245 | 2279 | 0 | 95
95
38957.616 | 1 | 0 | 96
38957.6181 | 1 | 0 | 96
38957.6203 | 1 | 0 | 96
38957.6224 | 2439 | 1 | 96
38957.6245 | 2500 | 0 | 96
96
38957.616 | 1 | 0 | 97
38957.6181 | 1 | 0 | 97
38957.6203 | 1 | 0 | 97
38957.6224 | 2186 | 0 | 97
38957.6246 | 2007 | 0 | 97
97
38957.616 | 1 | 0 | 98
38957.6182 | 1 | 0 | 98
38957.6203 | 1 | 0 | 98
38957.6224 | 2425 | 0 | 98
38957.6246 | 2070 | 0 | 98
98
38957.616 | 1 | 0 | 99
38957.6182 | 1 | 0 | 99
38957.6203 | 1 | 0 | 99
38957.6225 | 2489 | 0 | 99
38957.6246 | 2134 | 0 | 99
99
38957.6161 | 1 | 0 | 100
38957.6182 | 1 | 0 | 100
38957.6203 | 1 | 0 | 100
38957.6225 | 2301 | 0 | 100
38957.6246 | 1989 | 0 | 100
100
38957.6161 | 1 | 0 | 101
38957.6182 | 1 | 0 | 101
38957.6203 | 1 | 0 | 101
38957.6225 | 2266 | 0 | 101
38957.6246 | 2159 | 0 | 101
101
38957.6161 | 1 | 0 | 102
38957.6182 | 1 | 0 | 102
38957.6204 | 1 | 0 | 102
38957.6225 | 2187 | 0 | 102
38957.6246 | 2416 | 0 | 102
102
38957.6161 | 1 | 0 | 103
38957.6182 | 1 | 0 | 103
38957.6204 | 1 | 0 | 103
38957.6225 | 2113 | 0 | 103
38957.6247 | 2282 | 0 | 103
103
38957.6161 | 1 | 0 | 104
38957.6183 | 1 | 0 | 104
38957.6204 | 1 | 0 | 104
38957.6225 | 2393 | 0 | 104
38957.6247 | 2287 | 0 | 104
104
38957.6161 | 1 | 0 | 105
38957.6183 | 1 | 0 | 105
38957.6204 | 1 | 0 | 105
38957.6225 | 2041 | 0 | 105
38957.6247 | 2168 | 0 | 105
105
38957.6161 | 1 | 0 | 106
38957.6183 | 1 | 0 | 106
38957.6204 | 1 | 0 | 106
38957.6226 | 2024 | 0 | 106
38957.6247 | 2073 | 0 | 106
106
38957.6162 | 1 | 0 | 107
38957.6183 | 1 | 0 | 107
38957.6204 | 1 | 0 | 107
38957.6226 | 2385 | 0 | 107
38957.6247 | 2235 | 0 | 107
107
38957.6162 | 7 | 0 | 108
38957.6183 | 1 | 0 | 108
38957.6205 | 1 | 0 | 108
38957.6226 | 2550 | 0 | 108
38957.6247 | 2388 | 0 | 108
108
38957.6162 | 1 | 0 | 109
38957.6183 | 1 | 0 | 109
38957.6205 | 1 | 0 | 109
38957.6226 | 2456 | 39 | 109
38957.6248 | 2025 | 0 | 109
109
38957.6162 | 1 | 0 | 110
38957.6184 | 1 | 0 | 110
38957.6205 | 1 | 0 | 110
38957.6226 | 2359 | 122 | 110
38957.6248 | 2236 | 0 | 110
110
38957.6162 | 1 | 0 | 111
38957.6184 | 1 | 0 | 111
38957.6205 | 1 | 0 | 111
38957.6227 | 2124 | 11 | 111
111
38957.6162 | 1 | 0 | 112
38957.6184 | 1 | 0 | 112
38957.6205 | 1 | 0 | 112
38957.6227 | 2452 | 7 | 112
38957.6248 | 2507 | 0 | 112
112
38957.6163 | 1 | 0 | 113
38957.6184 | 1 | 0 | 113
38957.6205 | 1 | 0 | 113
38957.6227 | 2033 | 0 | 113
38957.6248 | 2350 | 0 | 113
113
38957.6163 | 1 | 0 | 114
38957.6184 | 1 | 0 | 114
38957.6206 | 1 | 0 | 114
38957.6227 | 2297 | 38 | 114
38957.6248 | 2329 | 0 | 114
114
38957.6163 | 1 | 0 | 115
38957.6184 | 1 | 0 | 115
38957.6206 | 1 | 0 | 115
38957.6227 | 2232 | 0 | 115
38957.6248 | 2266 | 0 | 115
115
38957.6163 | 1 | 0 | 116
38957.6184 | 1 | 0 | 116
38957.6206 | 1 | 0 | 116
38957.6227 | 2427 | 0 | 116
38957.6249 | 2480 | 0 | 116
116
38957.6163 | 1 | 0 | 117
38957.6185 | 1 | 0 | 117
38957.6206 | 1 | 0 | 117
38957.6227 | 2000 | 0 | 117
38957.6249 | 2552 | 0 | 117
117
38957.6163 | 1 | 0 | 118
38957.6185 | 1 | 0 | 118
38957.6206 | 1 | 0 | 118
38957.6228 | 2484 | 0 | 118
38957.6249 | 2556 | 0 | 118
118
38957.6164 | 1 | 0 | 119
38957.6185 | 1 | 0 | 119
38957.6206 | 1 | 0 | 119
38957.6228 | 2432 | 0 | 119
38957.6249 | 2537 | 0 | 119
119
38957.6164 | 1 | 0 | 120
38957.6185 | 1 | 0 | 120
38957.6207 | 1 | 0 | 120
38957.6228 | 2559 | 0 | 120
38957.6249 | 2437 | 0 | 120
120
38957.6164 | 1 | 0 | 121
38957.6185 | 1 | 0 | 121
38957.6207 | 1 | 0 | 121
38957.6228 | 2356 | 0 | 121
38957.6249 | 2488 | 0 | 121
121
38957.6164 | 1 | 0 | 122
38957.6186 | 1 | 0 | 122
38957.6207 | 1979 | 0 | 122
38957.6228 | 2559 | 0 | 122
38957.625 | 2535 | 0 | 122
122
38957.6164 | 1 | 0 | 123
38957.6186 | 1 | 0 | 123
38957.6207 | 1 | 0 | 123
38957.6228 | 2040 | 0 | 123
38957.625 | 2482 | 0 | 123
123
38957.6164 | 1 | 0 | 124
38957.6186 | 1 | 0 | 124
38957.6207 | 1 | 0 | 124
38957.6229 | 2141 | 0 | 124
38957.625 | 2420 | 0 | 124
124
38957.6165 | 1 | 0 | 125
38957.6186 | 1 | 0 | 125
38957.6207 | 1 | 0 | 125
38957.6229 | 2230 | 0 | 125
38957.625 | 2500 | 0 | 125
125
38957.6165 | 1 | 0 | 126
38957.6186 | 1 | 0 | 126
38957.6208 | 1 | 0 | 126
38957.6229 | 2160 | 0 | 126
38957.625 | 2512 | 0 | 126
126
38957.6165 | 1 | 0 | 127
38957.6186 | 1 | 0 | 127
38957.6208 | 2065 | 0 | 127
38957.6229 | 2179 | 0 | 127
38957.625 | 2467 | 0 | 127
127
38957.6165 | 1 | 0 | 128
38957.6186 | 1 | 0 | 128
38957.6208 | 1 | 0 | 128
38957.6229 | 2165 | 0 | 128
38957.6251 | 2396 | 0 | 128
128
38957.6165 | 1 | 0 | 129
38957.6187 | 1 | 0 | 129
38957.6208 | 2218 | 0 | 129
38957.6229 | 2416 | 0 | 129
38957.6251 | 2049 | 0 | 129
129
38957.6165 | 1 | 0 | 130
38957.6187 | 1 | 0 | 130
38957.6208 | 2 | 0 | 130
38957.623 | 2106 | 0 | 130
38957.6251 | 2048 | 0 | 130
130
38957.6166 | 1 | 0 | 131
38957.6187 | 1 | 0 | 131
38957.6208 | 1 | 0 | 131
38957.623 | 2058 | 0 | 131
38957.6251 | 2573 | 0 | 131
131
38957.6166 | 1 | 0 | 132
38957.6187 | 1 | 0 | 132
38957.6208 | 1 | 0 | 132
38957.623 | 2510 | 0 | 132
38957.6251 | 2471 | 0 | 132
132