## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 62
Test conditions: Cable: 12-conductor, 18 AWG, XLPE insulated, CSPE ("Hypalon") jacketed, Rockbestos Firewall III instrument cable (Cable Item #13). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using twelve channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and two cable temperatures (see thermocouple map). One thermocouple was attached to the inside of the center tray rung. Shroud power: Initiated after 160 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
160 |  | Initated Penlight Heating
417 |  | Cables ignite and burn
457 |  | Power to Penlight is shutoff
662-680 |  | Conductors 7, 11 & 12 all short to ground at less than 1000 ohms
700-709 |  | Conductor 7 shorts to conductors 9, 10, 11 & 12 (505, 39, 13 & 574)
714-720 |  | Conductor 8 shorts to conductors 10, 11 & 12 at less than 100 ohms (32, 44 & 9)
722-728 |  | Conductor 9 shorts to conductors 10, 11 & 12 at less than 100 ohms (1, 2 & 6)
731-734 |  | Conductor 10 shorts to conductors 11 & 12 at less than 100 ohms (3 & 15)
737 |  | Conductors 11 & 12 short together at less than 100 ohms (14)
740-768 |  | Conductor 1 shorts to conductors 2 through 12 at less than 100 ohms
753-860 |  | Conductors 1, 2, 3, 4, 6, 8, 9 & 10 all short to ground
771-796 |  | Conductor 2 shorts to conductors 3 through 12 at less than 100 ohms
798-821 |  | Conductor 3 shorts to conductors 4 through 12 at less than 100 ohms
824-843 |  | Conductor 4 shorts to conductors 5 through 12 at less than 100 ohms
846-863 |  | Conductor 5 shorts to conductors 6 through 12 at less than 100 ohms
866-880 |  | Conductor 6 shorts to conductors 7 through 12 at less than 100 ohms
882 |  | Conductors 7 & 8 short together at less than 100 ohms (20)
896 |  | Conductors 8 & 9 short together at less than 100 ohms (12) | All conductors are shorted together
1014 |  | Conductor 5 shorts to ground at much less than 100 ohms (<1) | All conductors are shorted to ground
Additional Observations
Observation 1 | It took 257 s (4.3 min.) from the start of Penlight heating for the cables to ignite and burn, and it took 502 s (8.4 min.) for the initial short to ground failures to occur, and 540 s (9 min.) for the first internal shorts.
Observation 2 | The progression of failures started with shorting to ground of a few of the conductors in the outer ring, followed by shorting among more of the outer conductors. After this failure progression rapidly developed to affect all of the conductors.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | "Cable 1" | Within cable just below cable jacket, center position
| TC2 | = | "Cable 2" | Within cable just below cable jacket, center position

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 62 |  |  | 2006-08-28 | 13:17
XLPE | 12-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C1-8 | Penlight Time | C1-9 | Penlight Time | C1-10 | Penlight Time | C1-11 | Penlight Time | C1-12 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C2-8 | Penlight Time | C2-9 | Penlight Time | C2-10 | Penlight Time | C2-11 | Penlight Time | C2-12 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C3-8 | Penlight Time | C3-9 | Penlight Time | C3-10 | Penlight Time | C3-11 | Penlight Time | C3-12 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C4-8 | Penlight Time | C4-9 | Penlight Time | C4-10 | Penlight Time | C4-11 | Penlight Time | C4-12 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C5-8 | Penlight Time | C5-9 | Penlight Time | C5-10 | Penlight Time | C5-11 | Penlight Time | C5-12 | Penlight Time | C6-7 | Penlight Time | C6-8 | Penlight Time | C6-9 | Penlight Time | C6-10 | Penlight Time | C6-11 | Penlight Time | C6-12 | Penlight Time | C7-8 | Penlight Time | C7-9 | Penlight Time | C7-10 | Penlight Time | C7-11 | Penlight Time | C7-12 | Penlight Time | C8-9 | Penlight Time | C8-10 | Penlight Time | C8-11 | Penlight Time | C8-12 | Penlight Time | C9-10 | Penlight Time | C9-11 | Penlight Time | C9-12 | Penlight Time | C10-11 | Penlight Time | C10-12 | Penlight Time | C11-12
-159.5 | 211201.9994 | -157 | 211201.9994 | -154 | 211201.9994 | -151.5 | 211201.9994 | -148.5 | 211201.9994 | -145.5 | 211201.9994 | -143 | 211201.9994 | -140 | 211201.9994 | -137.5 | 211201.9994 | -134.5 | 211201.9994 | -131.5 | 211201.9994 | -129 | 211201.9994 | -126 | 211201.9994 | -123.5 | 211201.9994 | -120.5 | 211201.9994 | -117.5 | 211201.9994 | -115 | 211201.9994 | -112 | 211201.9994 | -109.5 | 211201.9994 | -106.5 | 211201.9994 | -103.5 | 211201.9994 | -101 | 211201.9994 | -98 | 211201.9994 | -95.5 | 211201.9994 | -92.5 | 211201.9994 | -89.5 | 211201.9994 | -87 | 211201.9994 | -84 | 211201.9994 | -81.5 | 211201.9994 | -78.5 | 211201.9994 | -75.5 | 211201.9994 | -73 | 211201.9994 | -70 | 211201.9994 | -67.5 | 211201.9994 | -64.5 | 211201.9994 | -61.5 | 211201.9994 | -59 | 211201.9994 | -56 | 211201.9994 | -53.5 | 211201.9994 | -50.5 | 211201.9994 | -47.5 | 211201.9994 | -45 | 211201.9994 | -42 | 230237.9994 | -39.5 | 211201.9994 | -36.5 | 239037.9994 | -33.5 | 238137.9994 | -31 | 216837.9994 | -28 | 229137.9994 | -25.5 | 211201.9994 | -22.5 | 211837.9994 | -19.5 | 211201.9994 | -17 | 238837.9994 | -14.5 | 237337.9994 | -11.5 | 229537.9994 | -8.5 | 211337.9994 | -5.5 | 232537.9994 | -3 | 226437.9994 | -3.1665e-07 | 214937.9994 | 2.5 | 224237.9994 | 5.5 | 211201.9994 | 8 | 211201.9994 | 11 | 211201.9994 | 14 | 211201.9994 | 16.5 | 211201.9994 | 19.5 | 211201.9994 | 22 | 211201.9994
25 | 211201.9994 | 27.5 | 211201.9994 | 30.5 | 211201.9994 | 33.5 | 211201.9994 | 36.5 | 211201.9994 | 39 | 211201.9994 | 42 | 211201.9994 | 44.5 | 211201.9994 | 47.5 | 211201.9994 | 50.5 | 211201.9994 | 53 | 211201.9994 | 56 | 211201.9994 | 58.5 | 211201.9994 | 61.5 | 211201.9994 | 64 | 211201.9994 | 67 | 211201.9994 | 70 | 211201.9994 | 72.5 | 211201.9994 | 75.5 | 105550.9988 | 78.5 | 211201.9994 | 81 | 105550.9988 | 84 | 211201.9994 | 86.5 | 211201.9994 | 89.5 | 211201.9994 | 92.5 | 211201.9994 | 95 | 211201.9994 | 98 | 211201.9994 | 100.5 | 211201.9994 | 103.5 | 211201.9994 | 106.5 | 211201.9994 | 109 | 211201.9994 | 111.5 | 211201.9994 | 114.5 | 211201.9994 | 117.5 | 211201.9994 | 120 | 211201.9994 | 123 | 211201.9994 | 126 | 211201.9994 | 128.5 | 211201.9994 | 131.5 | 211201.9994 | 134.5 | 211201.9994 | 137 | 211201.9994 | 140 | 211201.9994 | 142.5 | 230237.9994 | 145.5 | 211201.9994 | 148 | 239037.9994 | 151 | 238137.9994 | 154 | 216837.9994 | 156.5 | 229137.9994 | 159.5 | 211201.9994 | 162.5 | 211837.9994 | 165 | 211201.9994 | 167.5 | 238837.9994 | 170.5 | 237337.9994 | 173.5 | 229537.9994 | 176 | 211337.9994 | 179 | 232537.9994 | 182 | 226437.9994 | 184.5 | 214937.9994 | 187.5 | 224237.9994 | 190.5 | 211201.9994 | 193 | 211201.9994 | 196 | 211201.9994 | 198.5 | 211201.9994 | 201.5 | 211201.9994 | 204 | 211201.9994 | 207 | 211201.9994
210 | 211201.9994 | 212.5 | 211201.9994 | 215.5 | 211201.9994 | 218 | 211201.9994 | 221 | 211201.9994 | 223.5 | 211201.9994 | 226.5 | 211201.9994 | 229.5 | 211201.9994 | 232.5 | 211201.9994 | 235 | 211201.9994 | 237.5 | 211201.9994 | 240.5 | 211201.9994 | 243.5 | 211201.9994 | 246 | 211201.9994 | 249 | 211201.9994 | 252 | 211201.9994 | 254.5 | 211201.9994 | 257.5 | 211201.9994 | 260 | 211201.9994 | 263 | 211201.9994 | 265.5 | 211201.9994 | 268.5 | 211201.9994 | 271.5 | 211201.9994 | 274.5 | 211201.9994 | 277 | 211201.9994 | 280 | 211201.9994 | 282.5 | 211201.9994 | 285.5 | 211201.9994 | 288 | 211201.9994 | 291 | 211201.9994 | 293.5 | 211201.9994 | 296.5 | 211201.9994 | 299.5 | 211201.9994 | 302 | 211201.9994 | 305 | 211201.9994 | 307.5 | 211201.9994 | 310.5 | 211201.9994 | 313.5 | 211201.9994 | 316 | 211201.9994 | 319 | 211201.9994 | 321.5 | 211201.9994 | 324.5 | 211201.9994 | 327.5 | 230237.9994 | 330 | 211201.9994 | 333 | 239037.9994 | 335.5 | 238137.9994 | 338.5 | 216837.9994 | 341.5 | 229137.9994 | 344 | 211201.9994 | 347 | 211837.9994 | 349.5 | 211201.9994 | 352.5 | 238837.9994 | 355.5 | 237337.9994 | 358 | 229537.9994 | 361 | 211337.9994 | 364 | 232537.9994 | 366.5 | 226437.9994 | 369.5 | 214937.9994 | 372.5 | 224237.9994 | 375 | 211201.9994 | 377.5 | 211201.9994 | 380.5 | 211201.9994 | 383.5 | 211201.9994 | 386 | 211201.9994 | 389 | 211201.9994 | 391.5 | 211201.9994
394.5 | 211201.9994 | 397.5 | 211201.9994 | 400.5 | 211201.9994 | 403 | 211201.9994 | 406 | 211201.9994 | 408.5 | 211201.9994 | 411.5 | 211201.9994 | 414 | 211201.9994 | 417 | 211201.9994 | 419.5 | 211201.9994 | 422.5 | 211201.9994 | 425.5 | 211201.9994 | 428.5 | 211201.9994 | 431 | 211201.9994 | 433.5 | 211201.9994 | 436.5 | 211201.9994 | 439.5 | 211201.9994 | 442 | 211201.9994 | 445 | 211201.9994 | 447.5 | 211201.9994 | 450.5 | 211201.9994 | 453.5 | 211201.9994 | 456 | 211201.9994 | 459 | 211201.9994 | 461.5 | 211201.9994 | 464.5 | 211201.9994 | 467.5 | 211201.9994 | 470 | 211201.9994 | 473 | 211201.9994 | 475.5 | 211201.9994 | 478.5 | 211201.9994 | 481.5 | 211201.9994 | 484 | 211201.9994 | 487 | 211201.9994 | 489.5 | 211201.9994 | 492.5 | 211201.9994 | 495.5 | 211201.9994 | 498 | 211201.9994 | 501 | 211201.9994 | 503.5 | 211201.9994 | 506.5 | 211201.9994 | 509.5 | 211201.9994 | 512 | 230237.9994 | 515 | 211201.9994 | 517.5 | 239037.9994 | 520.5 | 238137.9994 | 523.5 | 216837.9994 | 526 | 229137.9994 | 529 | 211201.9994 | 531.5 | 105319.3232 | 534.5 | 15876.6347 | 537.5 | 2745.4958 | 540 | 505.1345 | 543 | 39.0177 | 545.5 | 13.1073 | 548.5 | 573.5527 | 551.5 | 15888.9853 | 554 | 32.1926 | 557 | 44.3446 | 559.5 | 9.2542 | 562.5 | 1.0662 | 565.5 | 2.3849 | 568 | 5.9114 | 571 | 3.4924 | 573.5 | 15.2695 | 576.5 | 13.9518
579.5 | 11.33 | 582 | 7.1856 | 585 | 8.4403 | 587.5 | 8.5362 | 590.5 | 15.1589 | 593.5 | 20.1683 | 596 | 10.5701 | 599 | 3.0815 | 601.5 | 12.3286 | 604.5 | 10.1964 | 607.5 | 17.6842 | 610.5 | 21.6258 | 613 | 18.8749 | 615.5 | 20.8588 | 618.5 | 18.3089 | 621.5 | 3.7334 | 624 | 2.6016 | 627 | 9.4131 | 629.5 | 22.0778 | 632.5 | 3.3759 | 635.5 | 10.6888 | 638 | 17.2989 | 641 | 16.7207 | 643.5 | 23.4998 | 646.5 | 11.784 | 649.5 | 3.9025 | 652 | 7.2861 | 655 | 26.464 | 657.5 | 27.0353 | 660.5 | 1.7122 | 663.5 | 14.4664 | 666 | 18.3795 | 669 | 19.1617 | 671.5 | 6.0761 | 674.5 | 14.6402 | 677.5 | 21.8691 | 680 | 0.28196 | 683 | 7.7743 | 685.5 | 6.4777 | 688.5 | 19.0049 | 691.5 | 26.5914 | 694 | 23.1191 | 697 | 32.1633 | 699.5 | 19.2045 | 702.5 | 10.1454 | 705.5 | 39.7535 | 708 | 2.7657 | 711 | 5.4462 | 713.5 | 10.7779 | 716.5 | 18.7399 | 719.5 | 1.4969 | 722 | 20.4356 | 725 | 35.2047 | 727.5 | 0.031102 | 730.5 | 8.8367 | 733.5 | 3.381 | 736 | 12.4351 | 739 | 6.9889 | 741.5 | 5.7766 | 744.5 | 14.8346 | 747.5 | 12.7673 | 750 | 8.3233 | 753 | 18.6978 | 755.5 | 6.8742 | 758.5 | 10.7698 | 761.5 | 6.3198
764 | 8.0506 | 767 | 1.7087 | 769.5 | 15.0182 | 772.5 | 7.3185 | 775.5 | 12.0557 | 778 | 19.2815 | 781 | 10.2302 | 783.5 | 2.6481 | 786.5 | 20.2909 | 789.5 | 7.6259 | 792 | 13.5013 | 795 | 0.084447 | 797.5 | 4.472 | 800.5 | 13.5019 | 803.5 | 15.2217 | 806 | 28.4843 | 809 | 17.9106 | 811.5 | 20.3915 | 814.5 | 20.9756 | 817.5 | 5.3436 | 820 | 3.158 | 823 | 15.6446 | 825.5 | 14.1458 | 828.5 | 9.7779 | 831.5 | 19.9117 | 834 | 1.1093 | 837 | 3.7998 | 839.5 | 17.8572 | 842.5 | 12.7037 | 845.5 | 43.354 | 848 | 10.6979 | 851 | 3.319 | 853.5 | 2.2049 | 856.5 | 6.0589 | 859.5 | 3.5063 | 862 | 10.8182 | 865 | 3.058 | 867.5 | 16.3352 | 870.5 | 2.1562 | 873.5 | 1.1142 | 876 | 46.9276 | 879 | 0.71442 | 881.5 | 13.8709 | 884.5 | 23.6906 | 887.5 | 0.3514 | 890 | 7.5226 | 893 | 4.2434 | 895.5 | 8.9982 | 898.5 | 12.9706 | 901.5 | 25.0709 | 904 | 6.4113 | 907 | 9.0024 | 909.5 | 6.407 | 912.5 | 3.2379 | 915.5 | 0.82087 | 918 | 0.017985 | 921 | 0.72843 | 923.5 | 10.4245 | 926.5 | 9.6601 | 929.5 | 18.3946 | 932 | 1.4206 | 935 | 26.1222 | 937.5 | 4.1917 | 940.5 | 3.4717 | 943.5 | 5.854 | 946 | 7.6992
949 | 14.3278 | 951.5 | 21.2327 | 954.5 | 14.3929 | 957.5 | 1.6812 | 960 | 33.1188 | 963 | 1.0038 | 965.5 | 2.8063 | 968.5 | 12.0947 | 971.5 | 13.6592 | 974 | 7.8242 | 977 | 19.2145 | 979.5 | 9.7986 | 982.5 | 5.027 | 985.5 | 17.41 | 988 | 5.7885 | 991 | 21.8706 | 993.5 | 17.8528 | 996.5 | 10.6929 | 999.5 | 22.7425 | 1002 | 9.5258 | 1005 | 24.1165 | 1007.5 | 3.8332 | 1010.5 | 21.3001 | 1013.5 | 3.1155 | 1016 | 0.96668 | 1019 | 6.1115 | 1021.5 | 14.4679 | 1024.5 | 11.9658 | 1027.5 | 0.26026 | 1030 | 8.7612 | 1033 | 20.4356 | 1035.5 | 12.9373 | 1038.5 | 1.03 | 1041.5 | 2.0767 | 1044 | 7.2694 | 1047 | 13.4942 | 1049.5 | 19.5431 | 1052.5 | 10.1109 | 1055.5 | 5.5905 | 1058 | 0.8029 | 1061 | 10.3961 | 1063.5 | 3.1771 | 1066.5 | 0.60961 | 1069 | 3.4808 | 1072 | 20.2778 | 1075 | 31.6013 | 1077.5 | 12.4265 | 1080.5 | 0.38327 | 1083.5 | 21.0339 | 1086 | 20.6927 | 1089 | 1.2072 | 1091.5 | 15.8349 | 1094.5 | 41.9113 | 1097.5 | 31.8564 | 1100 | 3.6445 | 1103 | 35.8339 | 1105.5 | 35.6641 | 1108.5 | 14.2948 | 1111.5 | 34.6364 | 1114 | 4.3576 | 1117 | 22.1338 | 1119.5 | 0.28671 | 1122.5 | 2.0904 | 1125.5 | 13.7687 | 1128 | 21.9088 | 1131 | 3.6557
1133.5 | 10.5911 | 1136.5 | 1.0979 | 1139.5 | 6.1419 | 1142 | 7.9215 | 1145 | 24.5868 | 1147.5 | 17.7266 | 1150.5 | 5.5987 | 1153.5 | 19.7722 | 1156 | 7.9873 | 1159 | 2.2225 | 1161.5 | 23.0742 | 1164.5 | 0.20618 | 1167.5 | 22.23 | 1170 | 0.66385 | 1173 | 21.3881 | 1175.5 | 18.3597 | 1178.5 | 4.4024 | 1181.5 | 3.0758 | 1184 | 4.4712 | 1187 | 1.2635 | 1189.5 | 14.2138 | 1192.5 | 5.0856 | 1195.5 | 2.2032 | 1198 | 4.7386 | 1201 | 10.9531 | 1203.5 | 1.2006 | 1206.5 | 1.4707 | 1209.5 | 16.6756 | 1212 | 3.6884 | 1215 | 1.3668 | 1217.5 | 20.679 | 1220.5 | 5.8303 | 1223.5 | 15.841 | 1226 | 19.1221 | 1229 | 17.4054 | 1231.5 | 22.1286 | 1234.5 | 18.1659 | 1237.5 | 5.5875 | 1240 | 15.1074 | 1243 | 15.8494 | 1245.5 | 7.0622 | 1248.5 | 1.381 | 1251.5 | 19.9976 | 1254 | 22.4313 | 1257 | 24.1665 | 1259.5 | 17.7444 | 1262.5 | 15.6526 | 1265.5 | 7.4733 | 1268 | 20.851 | 1271 | 7.2994 | 1273.5 | 16.3677 | 1276.5 | 38.6424 | 1279.5 | 32.692 | 1282 | 36.1573 | 1285 | 7.7482 | 1287.5 | 14.8413 | 1290.5 | 6.2713 | 1293.5 | 0.42594 | 1296 | 6.1576 | 1299 | 10.5269 | 1301.5 | 12.3178 | 1304.5 | 8.2044 | 1307.5 | 12.3536 | 1310 | 10.2469 | 1313 | 15.1451 | 1315.5 | 7.5913

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 62 |  |  | 2006-08-28 | 13:17
XLPE | 12-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | C8-G | Penlight Time | C9-G | Penlight Time | C10-G | Penlight Time | C11-G | Penlight Time | C12-G
-145.6818 | 211202 |  | -120.2273 | 211202 | -99.4091 | 211202 | -82.5455 | 211202 | -69.3636 | 211202 | -59.1818 | 211202 | -51.5 | 211202 | -45.9545 | 211202 | -41.9091 | 211202 | -38.8636 | 115069 | -36.3636 | 211202 | -33.6364 | 211202
39.0455 | 211202 |  | 64.5 | 105551 | 85.4091 | 211202 | 102.0909 | 211202 | 115.4091 | 211202 | 125.5909 | 211202 | 133.1818 | 211202 | 138.8636 | 211202 | 142.8636 | 211202 | 145.9091 | 211202 | 148.5909 | 211202 | 151 | 211202
223.7727 | 211202 |  | 249.2273 | 211202 | 270.1364 | 211202 | 286.8636 | 211202 | 300.0455 | 211202 | 310.2727 | 211202 | 317.9545 | 211202 | 323.5455 | 211202 | 327.6364 | 211202 | 330.6364 | 211202 | 333.1818 | 211202 | 335.7273 | 211202
408.5909 | 211202 |  | 434 | 211202 | 454.8636 | 211202 | 471.7273 | 211202 | 484.8636 | 211202 | 495.0909 | 26463.9824 | 502.6364 | 956.443 | 508.3636 | 4444.152 | 512.3636 | 1099.4409 | 515.4091 | 3091.6778 | 517.9545 | 569.1963 | 520.4091 | 822.7699
593.3182 | 17.6507 |  | 618.8182 | 40.1637 | 639.6364 | 41.17 | 656.4545 | 472.0721 | 669.6364 | 1066.9331 | 679.8182 | 187.9555 | 687.5455 | 153.535 | 693.0455 | 54.3903 | 697.1818 | 21.6015 | 700.1818 | 84.9647 | 702.6818 | 35.9859 | 705.4091 | 39.0689
778.0909 | 53.3596 |  | 803.5455 | 33.8231 | 824.4545 | 5.6089 | 841.1818 | 46.5397 | 854.4545 | 0.58554 | 864.6818 | 0.64976 | 872.2727 | 0.0256 | 877.9091 | 0.15931 | 881.9091 | 0.93726 | 884.9545 | 1.0167 | 887.6364 | 1.4639 | 890.0909 | 0.0077049
962.9091 | 24.835 |  | 988.3636 | 205.0842 | 1009.1818 | 19.2415 | 1026 | 92.9709 | 1039.2727 | 23.4258 | 1049.4545 | 4.8541 | 1057.0909 | 211.1953 | 1062.6364 | 29.054 | 1066.6818 | 5.2827 | 1069.9091 | 517.3893 | 1072.3182 | 19.5738 | 1074.9091 | 71.4503
1147.6818 | 21.0517 |  | 1173.1364 | 51.8857 | 1194.0455 | 22.5432 | 1210.8636 | 486.0208 | 1224.0455 | 68.9037 | 1234.2273 | 691.4243 | 1241.8636 | 167.7937 | 1247.4545 | 142.3404 | 1251.6364 | 29.9274 | 1254.5909 | 377.5333 | 1257.1364 | 240.376 | 1259.6818 | 23.9861

## C11-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 11 & 12
Time-131 | N11 | N12 | Time-132 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38957.5543 | 1 | 0 | 38957.5543 | 1 | 0 | 22 | 182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5564 | 1 | 0 | 38957.5565 | 1 | 0 | 207 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5586 | 1 | 0 | 38957.5586 | 1 | 0 | 391.5 | 551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5607 | 1132 | 1163 | 38957.5607 | 1046 | 1000 | 576.5 | 736.5 | 69.1087 | 71.0012 | 63.8584 | 61.0501 | 0.69109 | 0.71001 | 0.63858 | 0.6105 | 0.018926 | 0.028083 | 569.1963 | 822.7699 | 13.9518
38957.5629 | 1106 | 1076 | 38957.5629 | 1181 | 1151 | 761.5 | 921.5 | 67.5214 | 65.6899 | 72.1001 | 70.2686 | 0.67521 | 0.6569 | 0.721 | 0.70269 | 0.018315 | 0.018315 | 6943.4 | 6943.4 | 6.3198
38957.565 | 1251 | 657 | 38957.565 | 1325 | 929 | 946 | 1106 | 76.3736 | 40.1099 | 80.8913 | 56.7155 | 0.76374 | 0.4011 | 0.80891 | 0.56716 | 0.36264 | 0.24176 | 33.1564 | 32.754 | 7.6992
38957.5671 | 1096 | 935 | 38957.5672 | 1068 | 1035 | 1131 | 1291 | 66.9109 | 57.0818 | 65.2015 | 63.1868 | 0.66911 | 0.57082 | 0.65201 | 0.63187 | 0.098291 | 0.020147 | 69.2037 | 71.4503 | 3.6557
38957.5693 | 950 | 1068 | 38957.5693 | 930 | 981 | 1315.5 | 1475.5 | 57.9976 | 65.2015 | 56.7766 | 59.8901 | 0.57998 | 0.65201 | 0.56777 | 0.5989 | 0.072039 | 0.031136 | 385.4978 | 581.4046 | 7.5913

## C10-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 10 & 12
Time-129 | N11 | N12 | Time-130 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38957.5543 | 1 | 0 | 38957.5543 | 1 | 0 | 19.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5564 | 1 | 0 | 38957.5564 | 1 | 0 | 204 | 364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5586 | 1 | 0 | 38957.5586 | 1 | 0 | 389 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5607 | 1167 | 1121 | 38957.5607 | 1191 | 1145 | 573.5 | 733.5 | 71.2454 | 68.4371 | 72.7106 | 69.9023 | 0.71245 | 0.68437 | 0.72711 | 0.69902 | 0.028083 | 0.028083 | 4493.5217 | 4493.5217 | 15.2695
38957.5628 | 1099 | 1166 | 38957.5628 | 1009 | 1046 | 758.5 | 918.5 | 67.094 | 71.1844 | 61.5995 | 63.8584 | 0.67094 | 0.71184 | 0.616 | 0.63858 | 0.040904 | 0.022589 | 324.8339 | 475.5967 | 10.7698
38957.565 | 1406 | 753 | 38957.565 | 1549 | 812 | 943.5 | 1103.5 | 85.8364 | 45.9707 | 94.5665 | 49.5726 | 0.85836 | 0.45971 | 0.94567 | 0.49573 | 0.39866 | 0.44994 | 113.9329 | 2321.0712 | 5.854
38957.5671 | 1210 | 1167 | 38957.5671 | 1137 | 1103 | 1128 | 1288 | 73.8706 | 71.2454 | 69.4139 | 67.3382 | 0.73871 | 0.71245 | 0.69414 | 0.67338 | 0.026252 | 0.020757 | 17715.4178 | 3078.9418 | 21.9088
38957.5692 | 993 | 971 | 38957.5693 | 950 | 927 | 1313 | 1473 | 60.6227 | 59.2796 | 57.9976 | 56.5934 | 0.60623 | 0.5928 | 0.57998 | 0.56593 | 0.013431 | 0.014042 | 12371.1721 | 7500.0775 | 15.1451

## C10-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 10 & 11
Time-127 | N11 | N12 | Time-128 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38957.5542 | 1 | 0 | 38957.5543 | 1 | 0 | 16.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5564 | 1 | 0 | 38957.5564 | 1 | 0 | 201.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5585 | 1 | 0 | 38957.5585 | 1 | 0 | 386 | 546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5607 | 1097 | 1054 | 38957.5607 | 1014 | 970 | 571 | 731 | 66.9719 | 64.3468 | 61.9048 | 59.2186 | 0.66972 | 0.64347 | 0.61905 | 0.59219 | 0.026252 | 0.026862 | 10687.218 | 3146.9141 | 3.4924
38957.5628 | 1116 | 1085 | 38957.5628 | 1025 | 995 | 755.5 | 915.5 | 68.1319 | 66.2393 | 62.5763 | 60.7448 | 0.68132 | 0.66239 | 0.62576 | 0.60745 | 0.018926 | 0.018315 | 441.4231 | 556.7958 | 6.8742
38957.5649 | 1469 | 720 | 38957.565 | 1329 | 659 | 940.5 | 1100.5 | 89.6825 | 43.956 | 81.1355 | 40.232 | 0.89683 | 0.43956 | 0.81136 | 0.40232 | 0.45726 | 0.40904 | 29.0416 | 49.027 | 3.4717
38957.5671 | 1013 | 965 | 38957.5671 | 948 | 914 | 1125.5 | 1285.5 | 61.8437 | 58.9133 | 57.8755 | 55.7998 | 0.61844 | 0.58913 | 0.57875 | 0.558 | 0.029304 | 0.020757 | 1728.7698 | 6173.9382 | 13.7687
38957.5692 | 1018 | 993 | 38957.5692 | 948 | 926 | 1310 | 1470 | 62.149 | 60.6227 | 57.8755 | 56.5324 | 0.62149 | 0.60623 | 0.57875 | 0.56532 | 0.015263 | 0.013431 | 4893.2234 | 37876.1219 | 10.2469

## C9-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 9 & 12
Time-125 | N11 | N12 | Time-126 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38957.5542 | 1 | 0 | 38957.5542 | 1 | 0 | 14 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5564 | 1 | 0 | 38957.5564 | 1 | 0 | 198.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5585 | 1 | 0 | 38957.5585 | 1 | 0 | 383.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5606 | 1111 | 1068 | 38957.5606 | 1037 | 995 | 568 | 728 | 67.8266 | 65.2015 | 63.3089 | 60.7448 | 0.67827 | 0.65201 | 0.63309 | 0.60745 | 0.026252 | 0.025641 | 1099.4409 | 2218.573 | 5.9114
38957.5628 | 1195 | 1195 | 38957.5628 | 987 | 958 | 753 | 913 | 72.9548 | 72.9548 | 60.2564 | 58.486 | 0.72955 | 0.72955 | 0.60256 | 0.58486 | 0 | 0.017705 | 320.5919 | 417.3191 | 18.6978
38957.5649 | 1386 | 696 | 38957.5649 | 1314 | 679 | 937.5 | 1097.5 | 84.6154 | 42.4908 | 80.2198 | 41.453 | 0.84615 | 0.42491 | 0.8022 | 0.41453 | 0.42125 | 0.38767 | 99.0451 | 1580.7761 | 4.1917
38957.567 | 1059 | 1020 | 38957.5671 | 983 | 1080 | 1122.5 | 1282.5 | 64.652 | 62.2711 | 60.0122 | 65.9341 | 0.64652 | 0.62271 | 0.60012 | 0.65934 | 0.02381 | 0.059219 | 163.0489 | 167.9167 | 2.0904
38957.5692 | 968 | 1007 | 38957.5692 | 1073 | 1050 | 1307.5 | 1467.5 | 59.0965 | 61.4774 | 65.5067 | 64.1026 | 0.59096 | 0.61477 | 0.65507 | 0.64103 | 0.02381 | 0.014042 | 767.2149 | 913.4307 | 12.3536

## C9-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 9 & 11
Time-123 | N11 | N12 | Time-124 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38957.5542 | 1 | 0 | 38957.5542 | 1 | 0 | 11 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5563 | 1 | 0 | 38957.5563 | 1 | 0 | 196 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5585 | 1 | 0 | 38957.5585 | 1 | 0 | 380.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5606 | 1056 | 1084 | 38957.5606 | 1185 | 1144 | 565.5 | 725.5 | 64.4689 | 66.1783 | 72.3443 | 69.8413 | 0.64469 | 0.66178 | 0.72344 | 0.69841 | 0.017094 | 0.025031 | 1403.9445 | 2292.2734 | 2.3849
38957.5627 | 973 | 1007 | 38957.5628 | 1088 | 1136 | 750 | 910 | 59.4017 | 61.4774 | 66.4225 | 69.3529 | 0.59402 | 0.61477 | 0.66422 | 0.69353 | 0.020757 | 0.029304 | 182.3561 | 170.3426 | 8.3233
38957.5649 | 1638 | 773 | 38957.5649 | 1337 | 653 | 935 | 1095 | 100 | 47.1917 | 81.6239 | 39.8657 | 1 | 0.47192 | 0.81624 | 0.39866 | 0.52808 | 0.41758 | 95.5227 | 210.2172 | 26.1222
38957.567 | 1075 | 1035 | 38957.567 | 1108 | 1144 | 1119.5 | 1279.5 | 65.6288 | 63.1868 | 67.6435 | 69.8413 | 0.65629 | 0.63187 | 0.67643 | 0.69841 | 0.02442 | 0.021978 | 4788.1236 | 5649.2722 | 0.28671
38957.5692 | 1026 | 1003 | 38957.5692 | 1006 | 981 | 1304.5 | 1464.5 | 62.6374 | 61.2332 | 61.4164 | 59.8901 | 0.62637 | 0.61233 | 0.61416 | 0.5989 | 0.014042 | 0.015263 | 56774.2795 | 4756.8538 | 8.2044

## C9-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 9 & 10
Time-121 | N11 | N12 | Time-122 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38957.5541 | 1 | 0 | 38957.5542 | 1 | 0 | 8 | 168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5563 | 1 | 0 | 38957.5563 | 1 | 0 | 193 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5584 | 1 | 0 | 38957.5584 | 1 | 0 | 377.5 | 537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5606 | 1072 | 1030 | 38957.5606 | 990 | 951 | 562.5 | 722.5 | 65.4457 | 62.8816 | 60.4396 | 58.0586 | 0.65446 | 0.62882 | 0.6044 | 0.58059 | 0.025641 | 0.02381 | 2709.1699 | 28817.5804 | 1.0662
38957.5627 | 971 | 1005 | 38957.5627 | 1119 | 1089 | 747.5 | 907.5 | 59.2796 | 61.3553 | 68.315 | 66.4835 | 0.5928 | 0.61355 | 0.68315 | 0.66484 | 0.020757 | 0.018315 | 1117.3374 | 1473.4115 | 12.7673
38957.5648 | 1340 | 736 | 38957.5649 | 1617 | 685 | 932 | 1092 | 81.8071 | 44.9328 | 98.7179 | 41.8193 | 0.81807 | 0.44933 | 0.98718 | 0.41819 | 0.36874 | 0.56899 | 31.2475 | 39.3612 | 1.4206
38957.567 | 959 | 922 | 38957.567 | 1095 | 1153 | 1117 | 1277 | 58.547 | 56.2882 | 66.8498 | 70.3907 | 0.58547 | 0.56288 | 0.6685 | 0.70391 | 0.022589 | 0.035409 | 706.8607 | 730.2398 | 22.1338
38957.5691 | 972 | 1011 | 38957.5691 | 986 | 965 | 1301.5 | 1461.5 | 59.3407 | 61.7216 | 60.1954 | 58.9133 | 0.59341 | 0.61722 | 0.60195 | 0.58913 | 0.02381 | 0.012821 | 1365.7544 | 2269.6131 | 12.3178

## C8-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 8 & 12
Time-119 | N11 | N12 | Time-120 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R12-G | R8-12
38957.5541 | 1 | 0 | 38957.5541 | 1 | 0 | 5.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5563 | 1 | 0 | 38957.5563 | 1 | 0 | 190.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5584 | 1 | 0 | 38957.5584 | 1 | 0 | 375 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5605 | 1129 | 1087 | 38957.5605 | 1166 | 1125 | 559.5 | 719.5 | 68.9255 | 66.3614 | 71.1844 | 68.6813 | 0.68926 | 0.66361 | 0.71184 | 0.68681 | 0.025641 | 0.025031 | 6072.1758 | 4214.0593 | 9.2542
38957.5627 | 1199 | 1193 | 38957.5627 | 949 | 921 | 744.5 | 904.5 | 73.199 | 72.8327 | 57.9365 | 56.2271 | 0.73199 | 0.72833 | 0.57937 | 0.56227 | 0.003663 | 0.017094 | 131.7774 | 173.4998 | 14.8346
38957.5648 | 1722 | 684 | 38957.5648 | 1585 | 664 | 929.5 | 1089.5 | 105.1282 | 41.7582 | 96.7643 | 40.5372 | 1.0513 | 0.41758 | 0.96764 | 0.40537 | 0.6337 | 0.56227 | 302.5304 | 75.2682 | 18.3946
38957.5669 | 1102 | 1064 | 38957.567 | 1200 | 1120 | 1114 | 1274 | 67.2772 | 64.9573 | 73.2601 | 68.3761 | 0.67277 | 0.64957 | 0.7326 | 0.68376 | 0.023199 | 0.04884 | 532.6668 | 700.9063 | 4.3576
38957.5691 | 977 | 954 | 38957.5691 | 1073 | 1156 | 1299 | 1459 | 59.6459 | 58.2418 | 65.5067 | 70.5739 | 0.59646 | 0.58242 | 0.65507 | 0.70574 | 0.014042 | 0.050672 | 142.3404 | 123.0808 | 10.5269

## C8-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 136.9585 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 8 & 11
Time-117 | N11 | N12 | Time-118 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R11-G | R8-11
38957.5541 | 1 | 0 | 38957.5541 | 1 | 0 | 2.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224238 | 224238 | 224237.9994
38957.5562 | 1 | 0 | 38957.5562 | 1 | 0 | 187.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224238 | 224238 | 224237.9994
38957.5584 | 1 | 0 | 38957.5584 | 1 | 0 | 372.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224238 | 224238 | 224237.9994
38957.5605 | 939 | 901 | 38957.5605 | 831 | 864 | 557 | 717 | 57.326 | 55.0061 | 50.7326 | 52.7473 | 0.57326 | 0.55006 | 0.50733 | 0.52747 | 0.023199 | 0.020147 | 4444.152 | 10416.7643 | 44.3446
38957.5626 | 1104 | 1076 | 38957.5627 | 1094 | 1065 | 741.5 | 901.5 | 67.3993 | 65.6899 | 66.7888 | 65.0183 | 0.67399 | 0.6569 | 0.66789 | 0.65018 | 0.017094 | 0.017705 | 16721.2238 | 5078.8196 | 5.7766
38957.5648 | 2227 | 168 | 38957.5648 | 1748 | 160 | 926.5 | 1086.5 | 135.9585 | 10.2564 | 106.7155 | 9.768 | 1.3596 | 0.10256 | 1.0672 | 0.09768 | 1.257 | 0.96947 | 2.4914 | 11.9867 | 9.6601
38957.5669 | 943 | 952 | 38957.5669 | 1060 | 1020 | 1111.5 | 1271.5 | 57.5702 | 58.1197 | 64.7131 | 62.2711 | 0.5757 | 0.5812 | 0.64713 | 0.62271 | 0.0054945 | 0.02442 | 2070.0415 | 1768.891 | 34.6364
38957.5691 | 1190 | 1154 | 38957.5691 | 1068 | 1045 | 1296 | 1456 | 72.6496 | 70.4518 | 65.2015 | 63.7973 | 0.7265 | 0.70452 | 0.65201 | 0.63797 | 0.021978 | 0.014042 | 204.1113 | 240.376 | 6.1576

## C8-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 131.2808 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 8 & 10
Time-115 | N11 | N12 | Time-116 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38957.5541 | 1 | 0 | 38957.5541 | 1 | 0 | -3.1665e-07 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214938 | 214938 | 214937.9994
38957.5562 | 1 | 0 | 38957.5562 | 1 | 0 | 184.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214938 | 214938 | 214937.9994
38957.5583 | 1 | 0 | 38957.5583 | 1 | 0 | 369.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214938 | 214938 | 214937.9994
38957.5605 | 946 | 907 | 38957.5605 | 1046 | 1007 | 554 | 714 | 57.7534 | 55.3724 | 63.8584 | 61.4774 | 0.57753 | 0.55372 | 0.63858 | 0.61477 | 0.02381 | 0.02381 | 5413.7949 | 5413.7949 | 32.1926
38957.5626 | 1194 | 1128 | 38957.5626 | 986 | 959 | 739 | 899 | 72.8938 | 68.8645 | 60.1954 | 58.547 | 0.72894 | 0.68864 | 0.60195 | 0.58547 | 0.040293 | 0.016484 | 68.6261 | 84.9647 | 6.9889
38957.5647 | 1969 | 112 | 38957.5648 | 2134 | 155 | 923.5 | 1083.5 | 120.2076 | 6.8376 | 130.2808 | 9.4628 | 1.2021 | 0.068376 | 1.3028 | 0.094628 | 1.1337 | 1.2082 | 7.5244 | 20.2331 | 10.4245
38957.5669 | 979 | 1005 | 38957.5669 | 1208 | 1172 | 1108.5 | 1268.5 | 59.768 | 61.3553 | 73.7485 | 71.5507 | 0.59768 | 0.61355 | 0.73748 | 0.71551 | 0.015873 | 0.021978 | 633.4488 | 632.3896 | 14.2948
38957.569 | 1089 | 1066 | 38957.569 | 1121 | 1096 | 1293.5 | 1453.5 | 66.4835 | 65.0794 | 68.4371 | 66.9109 | 0.66484 | 0.65079 | 0.68437 | 0.66911 | 0.014042 | 0.015263 | 2547.6137 | 5712.2243 | 0.42594

## C8-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 138.3016 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 8 & 9
Time-113 | N11 | N12 | Time-114 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38957.554 | 1 | 0 | 38957.554 | 1 | 0 | -3 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226438 | 226438 | 226437.9994
38957.5562 | 1 | 0 | 38957.5562 | 1 | 0 | 182 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226438 | 226438 | 226437.9994
38957.5583 | 1 | 0 | 38957.5583 | 1 | 0 | 366.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226438 | 226438 | 226437.9994
38957.5604 | 26 | 14 | 38957.5605 | 507 | 509 | 551.5 | 711.5 | 1.5873 | 0.8547 | 30.9524 | 31.0745 | 0.015873 | 0.008547 | 0.30952 | 0.31074 | 0.007326 | 0.001221 | 18652.4798 | 241250.8289 | 15888.9853
38957.5626 | 1042 | 1085 | 38957.5626 | 1088 | 1057 | 736 | 896 | 63.6142 | 66.2393 | 66.4225 | 64.5299 | 0.63614 | 0.66239 | 0.66422 | 0.6453 | 0.026252 | 0.018926 | 1727.4733 | 3900.2068 | 12.4351
38957.5647 | 2249 | 76 | 38957.5647 | 1805 | 81 | 921 | 1081 | 137.3016 | 4.6398 | 110.1954 | 4.9451 | 1.373 | 0.046398 | 1.102 | 0.049451 | 1.3266 | 1.0525 | 0.15931 | 0.93726 | 0.72843
38957.5669 | 979 | 942 | 38957.5669 | 1048 | 1007 | 1105.5 | 1265.5 | 59.768 | 57.5092 | 63.9805 | 61.4774 | 0.59768 | 0.57509 | 0.6398 | 0.61477 | 0.022589 | 0.025031 | 9615.5352 | 3987.832 | 35.6641
38957.569 | 1111 | 1086 | 38957.569 | 1106 | 1082 | 1290.5 | 1450.5 | 67.8266 | 66.3004 | 67.5214 | 66.0562 | 0.67827 | 0.663 | 0.67521 | 0.66056 | 0.015263 | 0.014652 | 5591.9563 | 24928.7282 | 6.2713

## C7-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 142.0256 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 7 & 12
Time-111 | N11 | N12 | Time-112 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R12-G | R7-12
38957.554 | 1 | 0 | 38957.554 | 1 | 0 | -5.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232538 | 232538 | 232537.9994
38957.5561 | 1 | 0 | 38957.5561 | 1 | 0 | 179 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232538 | 232538 | 232537.9994
38957.5583 | 1 | 0 | 38957.5583 | 1 | 0 | 364 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232538 | 232538 | 232537.9994
38957.5604 | 98 | 330 | 38957.5604 | 116 | 111 | 548.5 | 708.5 | 5.9829 | 20.1465 | 7.0818 | 6.7766 | 0.059829 | 0.20147 | 0.070818 | 0.067766 | 0.14164 | 0.0030525 | 956.443 | 33462.7181 | 573.5527
38957.5625 | 1180 | 1189 | 38957.5626 | 961 | 994 | 733.5 | 893.5 | 72.0391 | 72.5885 | 58.6691 | 60.6838 | 0.72039 | 0.72589 | 0.58669 | 0.60684 | 0.0054945 | 0.020147 | 1422.629 | 1661.0369 | 3.381
38957.5647 | 2173 | 46 | 38957.5647 | 2310 | 55 | 918 | 1078 | 132.6618 | 2.8083 | 141.0256 | 3.3578 | 1.3266 | 0.028083 | 1.4103 | 0.033578 | 1.2985 | 1.3767 | 0.0256 | 0.0077049 | 0.017985
38957.5668 | 1009 | 967 | 38957.5668 | 951 | 914 | 1103 | 1263 | 61.5995 | 59.0354 | 58.0586 | 55.7998 | 0.616 | 0.59035 | 0.58059 | 0.558 | 0.025641 | 0.022589 | 4220.9569 | 8962.3827 | 35.8339
38957.569 | 1094 | 1070 | 38957.569 | 1024 | 1070 | 1287.5 | 1447.5 | 66.7888 | 65.3236 | 62.5153 | 65.3236 | 0.66789 | 0.65324 | 0.62515 | 0.65324 | 0.014652 | 0.028083 | 2561.5439 | 4437.8401 | 14.8413

## C7-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129.083 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 7 & 11
Time-109 | N11 | N12 | Time-110 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R11-G | R7-11
38957.554 | 1 | 0 | 38957.554 | 1 | 0 | -8.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211338 | 211338 | 211337.9994
38957.5561 | 1 | 0 | 38957.5561 | 1 | 0 | 176 | 336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211338 | 211338 | 211337.9994
38957.5582 | 1 | 0 | 38957.5583 | 1 | 0 | 361 | 521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211338 | 211338 | 211337.9994
38957.5604 | 1145 | 1118 | 38957.5604 | 250 | 221 | 545.5 | 705.5 | 69.9023 | 68.254 | 15.2625 | 13.4921 | 0.69902 | 0.68254 | 0.15263 | 0.13492 | 0.016484 | 0.017705 | 8708.3726 | 7045.4427 | 13.1073
38957.5625 | 944 | 1051 | 38957.5625 | 1017 | 987 | 730.5 | 890.5 | 57.6313 | 64.1636 | 62.0879 | 60.2564 | 0.57631 | 0.64164 | 0.62088 | 0.60256 | 0.065324 | 0.018315 | 287.5953 | 350.3873 | 8.8367
38957.5647 | 2098 | 38 | 38957.5647 | 1989 | 37 | 915.5 | 1075.5 | 128.083 | 2.3199 | 121.4286 | 2.2589 | 1.2808 | 0.023199 | 1.2143 | 0.022589 | 1.2576 | 1.1917 | 0.35182 | 1.4639 | 0.82087
38957.5668 | 1021 | 1050 | 38957.5668 | 1061 | 1020 | 1100 | 1260 | 62.3321 | 64.1026 | 64.7741 | 62.2711 | 0.62332 | 0.64103 | 0.64774 | 0.62271 | 0.017705 | 0.025031 | 645.8547 | 748.4392 | 3.6445
38957.5689 | 992 | 1037 | 38957.5689 | 975 | 953 | 1285 | 1445 | 60.5617 | 63.3089 | 59.5238 | 58.1807 | 0.60562 | 0.63309 | 0.59524 | 0.58181 | 0.027473 | 0.013431 | 1020.9969 | 1597.1092 | 7.7482

## C7-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 140.1941 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 7 & 10
Time-107 | N11 | N12 | Time-108 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38957.5539 | 1 | 0 | 38957.5539 | 1 | 0 | -11.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229538 | 229538 | 229537.9994
38957.5561 | 1 | 0 | 38957.5561 | 1 | 0 | 173.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229538 | 229538 | 229537.9994
38957.5582 | 1 | 0 | 38957.5582 | 1 | 0 | 358 | 518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229538 | 229538 | 229537.9994
38957.5603 | 902 | 994 | 38957.5604 | 908 | 875 | 543 | 703 | 55.0672 | 60.6838 | 55.4335 | 53.4188 | 0.55067 | 0.60684 | 0.55433 | 0.53419 | 0.056166 | 0.020147 | 1123.1339 | 3091.6778 | 39.0177
38957.5625 | 1188 | 1108 | 38957.5625 | 964 | 937 | 727.5 | 887.5 | 72.5275 | 67.6435 | 58.8523 | 57.2039 | 0.72527 | 0.67643 | 0.58852 | 0.57204 | 0.04884 | 0.016484 | 572.0128 | 973.9083 | 0.031102
38957.5646 | 2153 | 34 | 38957.5646 | 2280 | 37 | 912.5 | 1072.5 | 131.4408 | 2.0757 | 139.1941 | 2.2589 | 1.3144 | 0.020757 | 1.3919 | 0.022589 | 1.2937 | 1.3694 | 2.6245 | 1.0167 | 3.2379
38957.5668 | 1012 | 970 | 38957.5668 | 1024 | 1050 | 1097.5 | 1257.5 | 61.7827 | 59.2186 | 62.5153 | 64.1026 | 0.61783 | 0.59219 | 0.62515 | 0.64103 | 0.025641 | 0.015873 | 2181.8579 | 5751.0977 | 31.8564
38957.5689 | 947 | 985 | 38957.5689 | 947 | 959 | 1282 | 1442 | 57.8144 | 60.1343 | 57.8144 | 58.547 | 0.57814 | 0.60134 | 0.57814 | 0.58547 | 0.023199 | 0.007326 | 2220.7056 | 4327.0895 | 36.1573

## C7-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 144.956 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 7 & 9
Time-105 | N11 | N12 | Time-106 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38957.5539 | 1 | 0 | 38957.5539 | 1 | 0 | -14.5 | 145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38957.556 | 1 | 0 | 38957.556 | 1 | 0 | 170.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38957.5582 | 1 | 0 | 38957.5582 | 1 | 0 | 355.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38957.5603 | 343 | 334 | 38957.5603 | 133 | 119 | 540 | 700 | 20.9402 | 20.3907 | 8.1197 | 7.265 | 0.2094 | 0.20391 | 0.081197 | 0.07265 | 0.0054945 | 0.008547 | 29125.1044 | 16491.142 | 505.1345
38957.5624 | 1024 | 995 | 38957.5625 | 1112 | 1082 | 725 | 885 | 62.5153 | 60.7448 | 67.8877 | 66.0562 | 0.62515 | 0.60745 | 0.67888 | 0.66056 | 0.017705 | 0.018315 | 9292.8073 | 6876.9867 | 35.2047
38957.5646 | 2358 | 36 | 38957.5646 | 2005 | 30 | 909.5 | 1069.5 | 143.956 | 2.1978 | 122.4054 | 1.8315 | 1.4396 | 0.021978 | 1.2241 | 0.018315 | 1.4176 | 1.2057 | 0.63189 | 13.3222 | 6.407
38957.5667 | 962 | 981 | 38957.5667 | 1092 | 1150 | 1094.5 | 1254.5 | 58.7302 | 59.8901 | 66.6667 | 70.2076 | 0.5873 | 0.5989 | 0.66667 | 0.70208 | 0.0116 | 0.035409 | 2099.5988 | 2032.3586 | 41.9113
38957.5689 | 1033 | 1009 | 38957.5689 | 985 | 1028 | 1279.5 | 1439.5 | 63.0647 | 61.5995 | 60.1343 | 62.7595 | 0.63065 | 0.616 | 0.60134 | 0.62759 | 0.014652 | 0.026252 | 8229.8787 | 13102.0306 | 32.692

## C7-8
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 145.8718 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 7 & 8
Time-103 | N11 | N12 | Time-104 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38957.5539 | 1 | 0 | 38957.5539 | 1 | 0 | -17 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38957.556 | 1 | 0 | 38957.556 | 1 | 0 | 167.5 | 327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38957.5581 | 1 | 0 | 38957.5581 | 1 | 0 | 352.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
38957.5603 | 93 | 80 | 38957.5603 | 167 | 146 | 537.5 | 697.5 | 5.6777 | 4.884 | 10.1954 | 8.9133 | 0.056777 | 0.04884 | 0.10195 | 0.089133 | 0.0079365 | 0.012821 | 18712.1393 | 10991.1306 | 2745.4958
38957.5624 | 1183 | 914 | 38957.5624 | 1151 | 1121 | 722 | 882 | 72.2222 | 55.7998 | 70.2686 | 68.4371 | 0.72222 | 0.558 | 0.70269 | 0.68437 | 0.16422 | 0.018315 | 153.535 | 176.8794 | 20.4356
38957.5645 | 2373 | 33 | 38957.5646 | 1904 | 27 | 907 | 1067 | 144.8718 | 2.0147 | 116.2393 | 1.6484 | 1.4487 | 0.020147 | 1.1624 | 0.016484 | 1.4286 | 1.1459 | 0.6574 | 21.7653 | 9.0024
38957.5667 | 1090 | 1120 | 38957.5667 | 1052 | 1009 | 1091.5 | 1251.5 | 66.5446 | 68.3761 | 64.2247 | 61.5995 | 0.66545 | 0.68376 | 0.64225 | 0.616 | 0.018315 | 0.026252 | 7559.5853 | 8742.1519 | 15.8349
38957.5688 | 977 | 1017 | 38957.5688 | 987 | 964 | 1276.5 | 1436.5 | 59.6459 | 62.0879 | 60.2564 | 58.8523 | 0.59646 | 0.62088 | 0.60256 | 0.58852 | 0.02442 | 0.014042 | 3058.6453 | 16465.2289 | 38.6424

## C6-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 12
Time-101 | N11 | N12 | Time-102 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38957.5538 | 1 | 0 | 38957.5538 | 1 | 0 | -19.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.556 | 1 | 0 | 38957.556 | 1 | 0 | 165 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5581 | 1 | 0 | 38957.5581 | 1 | 0 | 349.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5602 | 21 | 13 | 38957.5603 | 102 | 87 | 534.5 | 694.5 | 1.2821 | 0.79365 | 6.2271 | 5.3114 | 0.012821 | 0.0079365 | 0.062271 | 0.053114 | 0.004884 | 0.0091575 | 26463.9824 | 13707.2153 | 15876.6347
38957.5624 | 1021 | 1116 | 38957.5624 | 968 | 1003 | 719.5 | 879.5 | 62.3321 | 68.1319 | 59.0965 | 61.2332 | 0.62332 | 0.68132 | 0.59096 | 0.61233 | 0.057998 | 0.021368 | 187.9555 | 229.63 | 1.4969
38957.5645 | 2083 | 27 | 38957.5645 | 1888 | 25 | 904 | 1064 | 127.1673 | 1.6484 | 115.2625 | 1.5263 | 1.2717 | 0.016484 | 1.1526 | 0.015263 | 1.2552 | 1.1374 | 1.4745 | 134.2998 | 6.4113
38957.5667 | 1087 | 1039 | 38957.5667 | 1204 | 1159 | 1089 | 1249 | 66.3614 | 63.431 | 73.5043 | 70.757 | 0.66361 | 0.63431 | 0.73504 | 0.70757 | 0.029304 | 0.027473 | 8697.1435 | 2869.9443 | 1.2072
38957.5688 | 987 | 965 | 38957.5688 | 1027 | 1003 | 1273.5 | 1433.5 | 60.2564 | 58.9133 | 62.6984 | 61.2332 | 0.60256 | 0.58913 | 0.62698 | 0.61233 | 0.013431 | 0.014652 | 34813.1233 | 5142.4074 | 16.3677

## C6-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129.3883 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 11
Time-99 | N11 | N12 | Time-100 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38957.5538 | 1 | 0 | 38957.5538 | 1 | 0 | -22.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38957.5559 | 1 | 0 | 38957.5559 | 1 | 0 | 162.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38957.5581 | 1 | 0 | 38957.5581 | 1 | 0 | 347 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211838 | 211838 | 211837.9994
38957.5602 | 6 | 2 | 38957.5602 | 31 | 26 | 531.5 | 691.5 | 0.3663 | 0.1221 | 1.8926 | 1.5873 | 0.003663 | 0.001221 | 0.018926 | 0.015873 | 0.002442 | 0.0030525 | 52897.2008 | 42182.2681 | 105319.3232
38957.5623 | 1160 | 1186 | 38957.5624 | 971 | 945 | 716.5 | 876.5 | 70.8181 | 72.4054 | 59.2796 | 57.6923 | 0.70818 | 0.72405 | 0.5928 | 0.57692 | 0.015873 | 0.015873 | 1946.3047 | 5091.793 | 18.7399
38957.5645 | 1971 | 24 | 38957.5645 | 2103 | 26 | 901.5 | 1061.5 | 120.3297 | 1.4652 | 128.3883 | 1.5873 | 1.2033 | 0.014652 | 1.2839 | 0.015873 | 1.1886 | 1.268 | 10.0604 | 5.0835 | 25.0709
38957.5666 | 946 | 945 | 38957.5666 | 974 | 902 | 1086 | 1246 | 57.7534 | 57.6923 | 59.4628 | 55.0672 | 0.57753 | 0.57692 | 0.59463 | 0.55067 | 0.0006105 | 0.043956 | 734.8513 | 595.5538 | 20.6927
38957.5688 | 1061 | 1147 | 38957.5688 | 706 | 689 | 1271 | 1431 | 64.7741 | 70.0244 | 43.1013 | 42.0635 | 0.64774 | 0.70024 | 0.43101 | 0.42063 | 0.052503 | 0.010379 | 691.4243 | 1710.0916 | 7.2994

## C6-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 10
Time-97 | N11 | N12 | Time-98 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38957.5538 | 1 | 0 | 38957.5538 | 1 | 0 | -25.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5559 | 1 | 0 | 38957.5559 | 1 | 0 | 159.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.558 | 1 | 0 | 38957.5581 | 1 | 0 | 344 | 504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5602 | 1 | 0 | 38957.5602 | 1 | 0 | 529 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5623 | 1139 | 1108 | 38957.5623 | 969 | 947 | 713.5 | 873.5 | 69.536 | 67.6435 | 59.1575 | 57.8144 | 0.69536 | 0.67643 | 0.59158 | 0.57814 | 0.018926 | 0.013431 | 586.3882 | 820.103 | 10.7779
38957.5645 | 1983 | 24 | 38957.5645 | 2058 | 24 | 898.5 | 1058.5 | 121.0623 | 1.4652 | 125.641 | 1.4652 | 1.2106 | 0.014652 | 1.2564 | 0.014652 | 1.196 | 1.2418 | 11.1547 | 3.025 | 12.9706
38957.5666 | 1207 | 1154 | 38957.5666 | 1180 | 1125 | 1083.5 | 1243.5 | 73.6874 | 70.4518 | 72.0391 | 68.6813 | 0.73687 | 0.70452 | 0.72039 | 0.68681 | 0.032357 | 0.033578 | 3230.5075 | 4624.4624 | 21.0339
38957.5687 | 1196 | 1177 | 38957.5687 | 1109 | 1162 | 1268 | 1428 | 73.0159 | 71.8559 | 67.7045 | 70.9402 | 0.73016 | 0.71856 | 0.67705 | 0.7094 | 0.0116 | 0.032357 | 1032.1476 | 1685.1401 | 20.851

## C6-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 139.9499 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 9
Time-95 | N11 | N12 | Time-96 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38957.5537 | 1 | 0 | 38957.5537 | 1 | 0 | -28 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38957.5559 | 1 | 0 | 38957.5559 | 1 | 0 | 156.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38957.558 | 1 | 0 | 38957.558 | 1 | 0 | 341.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38957.5601 | 1 | 0 | 38957.5602 | 1 | 0 | 526 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229138 | 229138 | 229137.9994
38957.5623 | 1191 | 1166 | 38957.5623 | 978 | 951 | 711 | 871 | 72.7106 | 71.1844 | 59.707 | 58.0586 | 0.72711 | 0.71184 | 0.59707 | 0.58059 | 0.015263 | 0.016484 | 24592.8018 | 5681.8362 | 5.4462
38957.5644 | 2276 | 29 | 38957.5644 | 1925 | 23 | 895.5 | 1055.5 | 138.9499 | 1.7705 | 117.5214 | 1.4042 | 1.3895 | 0.017705 | 1.1752 | 0.014042 | 1.3718 | 1.1612 | 0.69458 | 26.0675 | 8.9982
38957.5666 | 1245 | 1134 | 38957.5666 | 1096 | 1110 | 1080.5 | 1240.5 | 76.0073 | 69.2308 | 66.9109 | 67.7656 | 0.76007 | 0.69231 | 0.66911 | 0.67766 | 0.067766 | 0.008547 | 4.8541 | 5.2827 | 0.38327
38957.5687 | 1189 | 1200 | 38957.5687 | 1181 | 1158 | 1265.5 | 1425.5 | 72.5885 | 73.2601 | 72.1001 | 70.696 | 0.72589 | 0.7326 | 0.721 | 0.70696 | 0.0067155 | 0.014042 | 1062.2923 | 1292.159 | 7.4733

## C6-8
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 132.4408 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 8
Time-93 | N11 | N12 | Time-94 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R8-G | R6-8
38957.5537 | 1 | 0 | 38957.5537 | 1 | 0 | -31 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216838 | 216838 | 216837.9994
38957.5558 | 1 | 0 | 38957.5559 | 1 | 0 | 154 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216838 | 216838 | 216837.9994
38957.558 | 1 | 0 | 38957.558 | 1 | 0 | 338.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216838 | 216838 | 216837.9994
38957.5601 | 1 | 0 | 38957.5601 | 1 | 0 | 523.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216838 | 216838 | 216837.9994
38957.5622 | 1084 | 1056 | 38957.5623 | 1092 | 1062 | 708 | 868 | 66.1783 | 64.4689 | 66.6667 | 64.8352 | 0.66178 | 0.64469 | 0.66667 | 0.64835 | 0.017094 | 0.018315 | 3164.7925 | 16774.0062 | 2.7657
38957.5644 | 2153 | 25 | 38957.5644 | 1968 | 24 | 893 | 1053 | 131.4408 | 1.5263 | 120.1465 | 1.4652 | 1.3144 | 0.015263 | 1.2015 | 0.014652 | 1.2991 | 1.1868 | 0.71028 | 14.0338 | 4.2434
38957.5665 | 1209 | 1156 | 38957.5665 | 1190 | 1036 | 1077.5 | 1237.5 | 73.8095 | 70.5739 | 72.6496 | 63.2479 | 0.7381 | 0.70574 | 0.7265 | 0.63248 | 0.032357 | 0.094017 | 203.8102 | 276.4142 | 12.4265
38957.5687 | 1159 | 1200 | 38957.5687 | 1184 | 1160 | 1262.5 | 1422.5 | 70.757 | 73.2601 | 72.2833 | 70.8181 | 0.70757 | 0.7326 | 0.72283 | 0.70818 | 0.025031 | 0.014652 | 3416.9995 | 10497.9689 | 15.6526

## C6-7
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 145.4444 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 7
Time-91 | N11 | N12 | Time-92 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38957.5537 | 1 | 0 | 38957.5537 | 1 | 0 | -33.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238138 | 238138 | 238137.9994
38957.5558 | 1 | 0 | 38957.5558 | 1 | 0 | 151 | 311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238138 | 238138 | 238137.9994
38957.5579 | 1 | 0 | 38957.558 | 1 | 0 | 335.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238138 | 238138 | 238137.9994
38957.5601 | 1 | 0 | 38957.5601 | 1 | 0 | 520.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238138 | 238138 | 238137.9994
38957.5622 | 1006 | 977 | 38957.5622 | 1005 | 1045 | 705.5 | 865.5 | 61.4164 | 59.6459 | 61.3553 | 63.7973 | 0.61416 | 0.59646 | 0.61355 | 0.63797 | 0.017705 | 0.02442 | 101251.5086 | 3534.6514 | 39.7535
38957.5644 | 2366 | 33 | 38957.5644 | 1933 | 29 | 890 | 1050 | 144.4444 | 2.0147 | 118.0098 | 1.7705 | 1.4444 | 0.020147 | 1.1801 | 0.017705 | 1.4243 | 1.1624 | 0.64976 | 17.5595 | 7.5226
38957.5665 | 1055 | 998 | 38957.5665 | 1176 | 1066 | 1075 | 1235 | 64.4078 | 60.928 | 71.7949 | 65.0794 | 0.64408 | 0.60928 | 0.71795 | 0.65079 | 0.034799 | 0.067155 | 1310.3477 | 2252.8304 | 31.6013
38957.5686 | 1106 | 1082 | 38957.5686 | 1058 | 1033 | 1259.5 | 1419.5 | 67.5214 | 66.0562 | 64.591 | 63.0647 | 0.67521 | 0.66056 | 0.64591 | 0.63065 | 0.014652 | 0.015263 | 12094.8602 | 8046.4509 | 17.7444

## C5-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 145.9939 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 12
Time-89 | N11 | N12 | Time-90 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38957.5536 | 1 | 0 | 38957.5536 | 1 | 0 | -36.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239038 | 239038 | 239037.9994
38957.5558 | 1 | 0 | 38957.5558 | 1 | 0 | 148 | 308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239038 | 239038 | 239037.9994
38957.5579 | 1 | 0 | 38957.5579 | 1 | 0 | 333 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239038 | 239038 | 239037.9994
38957.56 | 1 | 0 | 38957.5601 | 1 | 0 | 517.5 | 677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239038 | 239038 | 239037.9994
38957.5622 | 1153 | 1123 | 38957.5622 | 1080 | 1050 | 702.5 | 862.5 | 70.3907 | 68.5592 | 65.9341 | 64.1026 | 0.70391 | 0.68559 | 0.65934 | 0.64103 | 0.018315 | 0.018315 | 7871.2667 | 7871.2667 | 10.1454
38957.5643 | 2189 | 88 | 38957.5643 | 2375 | 49 | 887.5 | 1047.5 | 133.6386 | 5.3724 | 144.9939 | 2.9915 | 1.3364 | 0.053724 | 1.4499 | 0.029915 | 1.2827 | 1.42 | 0.58554 | 0.27109 | 0.3514
38957.5665 | 1117 | 1057 | 38957.5665 | 991 | 938 | 1072 | 1232 | 68.1929 | 64.5299 | 60.5006 | 57.265 | 0.68193 | 0.6453 | 0.60501 | 0.57265 | 0.03663 | 0.032357 | 2832.4974 | 7042.6248 | 20.2778
38957.5686 | 1038 | 1084 | 38957.5686 | 1120 | 1094 | 1257 | 1417 | 63.37 | 66.1783 | 68.3761 | 66.7888 | 0.6337 | 0.66178 | 0.68376 | 0.66789 | 0.028083 | 0.015873 | 1764.9289 | 3533.034 | 24.1665

## C5-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 11
Time-87 | N11 | N12 | Time-88 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38957.5536 | 1 | 0 | 38957.5536 | 1 | 0 | -39.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5557 | 1 | 0 | 38957.5558 | 1 | 0 | 145.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5579 | 1 | 0 | 38957.5579 | 1 | 0 | 330 | 490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.56 | 1 | 0 | 38957.56 | 1 | 0 | 515 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5622 | 1183 | 1154 | 38957.5622 | 1098 | 1068 | 699.5 | 859.5 | 72.2222 | 70.4518 | 67.033 | 65.2015 | 0.72222 | 0.70452 | 0.67033 | 0.65201 | 0.017705 | 0.018315 | 5564.4238 | 9392.5604 | 19.2045
38957.5643 | 1996 | 80 | 38957.5643 | 1913 | 103 | 884.5 | 1044.5 | 121.8559 | 4.884 | 116.7888 | 6.2882 | 1.2186 | 0.04884 | 1.1679 | 0.062882 | 1.1697 | 1.105 | 6.3607 | 104.8978 | 23.6906
38957.5664 | 1117 | 1049 |  | 1088 | 1079 | 1069 | 1229 | 68.1929 | 64.0415 | 66.4225 | 65.873 | 0.68193 | 0.64042 | 0.66422 | 0.65873 | 0.041514 | 0.0054945 | 184.0855 | 221.746 | 3.4808
38957.5686 | 962 | 940 | 38957.5686 | 933 | 970 | 1254 | 1414 | 58.7302 | 57.3871 | 56.9597 | 59.2186 | 0.5873 | 0.57387 | 0.5696 | 0.59219 | 0.013431 | 0.022589 | 5061.7788 | 127123.7667 | 22.4313

## C5-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 140.6215 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 10
Time-85 | N11 | N12 | Time-86 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38957.5536 | 1 | 0 | 38957.5536 | 2 | 0 | -42 | 118 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230238 | 115069 | 230237.9994
38957.5557 | 1 | 0 | 38957.5557 | 1 | 0 | 142.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38957.5578 | 1 | 0 | 38957.5579 | 1 | 0 | 327.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38957.56 | 1 | 0 | 38957.56 | 1 | 0 | 512 | 672 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38957.5621 | 1008 | 978 | 38957.5621 | 1051 | 1023 | 697 | 857 | 61.5385 | 59.707 | 64.1636 | 62.4542 | 0.61538 | 0.59707 | 0.64164 | 0.62454 | 0.018315 | 0.017094 | 6103.7557 | 11142.3422 | 32.1633
38957.5643 | 2242 | 111 | 38957.5643 | 2287 | 71 | 881.5 | 1041.5 | 136.8742 | 6.7766 | 139.6215 | 4.3346 | 1.3687 | 0.067766 | 1.3962 | 0.043346 | 1.301 | 1.3529 | 3.2575 | 44.9888 | 13.8709
38957.5664 | 1143 | 1152 | 38957.5664 | 1025 | 947 | 1066.5 | 1226.5 | 69.7802 | 70.3297 | 62.5763 | 57.8144 | 0.6978 | 0.7033 | 0.62576 | 0.57814 | 0.0054945 | 0.047619 | 500.9058 | 517.3893 | 0.60961
38957.5685 | 1022 | 1066 | 38957.5686 | 984 | 1024 | 1251.5 | 1411.5 | 62.3932 | 65.0794 | 60.0733 | 62.5153 | 0.62393 | 0.65079 | 0.60073 | 0.62515 | 0.026862 | 0.02442 | 3886.6803 | 9663.2331 | 19.9976

## C5-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 9
Time-83 | N11 | N12 | Time-84 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38957.5535 | 1 | 0 | 38957.5536 | 1 | 0 | -45 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5557 | 1 | 0 | 38957.5557 | 1 | 0 | 140 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5578 | 1 | 0 | 38957.5578 | 1 | 0 | 324.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.56 | 1 | 0 | 38957.56 | 1 | 0 | 509.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5621 | 1206 | 1184 | 38957.5621 | 1070 | 1041 | 694 | 854 | 73.6264 | 72.2833 | 65.3236 | 63.5531 | 0.73626 | 0.72283 | 0.65324 | 0.63553 | 0.013431 | 0.017705 | 2515.4966 | 8422.6742 | 23.1191
38957.5642 | 1905 | 148 | 38957.5642 | 2035 | 130 | 879 | 1039 | 116.3004 | 9.0354 | 124.2369 | 7.9365 | 1.163 | 0.090354 | 1.2424 | 0.079365 | 1.0726 | 1.163 | 2.0781 | 1.7932 | 0.71442
38957.5664 | 949 | 976 | 38957.5664 | 1146 | 1157 | 1063.5 | 1223.5 | 57.9365 | 59.5849 | 69.9634 | 70.6349 | 0.57937 | 0.59585 | 0.69963 | 0.70635 | 0.016484 | 0.0067155 | 23.4258 | 19.7493 | 3.1771
38957.5685 | 1019 | 1064 | 38957.5685 | 1092 | 1068 | 1248.5 | 1408.5 | 62.21 | 64.9573 | 66.6667 | 65.2015 | 0.6221 | 0.64957 | 0.66667 | 0.65201 | 0.027473 | 0.014652 | 94.7369 | 95.8733 | 1.381

## C5-8
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 8
Time-81 | N11 | N12 | Time-82 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R8-G | R5-8
38957.5535 | 1 | 0 | 38957.5535 | 1 | 0 | -47.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5556 | 1 | 0 | 38957.5557 | 1 | 0 | 137 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5578 | 1 | 0 | 38957.5578 | 1 | 0 | 321.5 | 481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5599 | 1 | 0 | 38957.5599 | 1 | 0 | 506.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5621 | 948 | 919 | 38957.5621 | 943 | 923 | 691.5 | 851.5 | 57.8755 | 56.105 | 57.5702 | 56.3492 | 0.57875 | 0.56105 | 0.5757 | 0.56349 | 0.017705 | 0.01221 | 3310.8714 | 14852.0077 | 26.5914
38957.5642 | 1940 | 429 | 38957.5642 | 1318 | 576 | 876 | 1036 | 118.4371 | 26.1905 | 80.464 | 35.1648 | 1.1844 | 0.2619 | 0.80464 | 0.35165 | 0.92247 | 0.45299 | 12.4071 | 368.3063 | 46.9276
38957.5663 | 1194 | 1120 | 38957.5664 | 957 | 914 | 1061 | 1221 | 72.8938 | 68.3761 | 58.4249 | 55.7998 | 0.72894 | 0.68376 | 0.58425 | 0.558 | 0.045177 | 0.026252 | 103.5843 | 137.7243 | 10.3961
38957.5685 | 996 | 1038 | 38957.5685 | 1012 | 989 | 1245.5 | 1405.5 | 60.8059 | 63.37 | 61.7827 | 60.3785 | 0.60806 | 0.6337 | 0.61783 | 0.60379 | 0.025641 | 0.014042 | 908.7613 | 1282.7997 | 7.0622

## C5-7
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 7
Time-79 | N11 | N12 | Time-80 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38957.5535 | 1 | 0 | 38957.5535 | 1 | 0 | -50.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5556 | 1 | 0 | 38957.5556 | 1 | 0 | 134.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5577 | 1 | 0 | 38957.5578 | 1 | 0 | 319 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5599 | 1 | 0 | 38957.5599 | 1 | 0 | 503.5 | 663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.562 | 1177 | 1176 | 38957.562 | 1146 | 1113 | 688.5 | 848.5 | 71.8559 | 71.7949 | 69.9634 | 67.9487 | 0.71856 | 0.71795 | 0.69963 | 0.67949 | 0.0006105 | 0.020147 | 1066.9331 | 1355.9328 | 19.0049
38957.5642 | 1205 | 668 | 38957.5642 | 1662 | 641 | 873.5 | 1033.5 | 73.5653 | 40.7814 | 101.4652 | 39.1331 | 0.73565 | 0.40781 | 1.0147 | 0.39133 | 0.32784 | 0.62332 | 4.2409 | 3.2002 | 1.1142
38957.5663 | 1085 | 1016 | 38957.5663 | 992 | 992 | 1058 | 1218 | 66.2393 | 62.0269 | 60.5617 | 60.5617 | 0.66239 | 0.62027 | 0.60562 | 0.60562 | 0.042125 | 0 | 186.8885 | 211.1953 | 0.8029
38957.5684 | 1196 | 1199 | 38957.5685 | 1027 | 949 | 1243 | 1403 | 73.0159 | 73.199 | 62.6984 | 57.9365 | 0.73016 | 0.73199 | 0.62698 | 0.57937 | 0.0018315 | 0.047619 | 157.2599 | 206.6799 | 15.8494

## C5-6
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 6
Time-77 | N11 | N12 | Time-78 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38957.5534 | 1 | 0 | 38957.5534 | 1 | 0 | -53.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5556 | 1 | 0 | 38957.5556 | 1 | 0 | 131.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5577 | 1 | 0 | 38957.5577 | 1 | 0 | 316 | 476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5598 | 1 | 0 | 38957.5599 | 1 | 0 | 501 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.562 | 1038 | 1007 | 38957.562 | 1032 | 1071 | 685.5 | 845.5 | 63.37 | 61.4774 | 63.0037 | 65.3846 | 0.6337 | 0.61477 | 0.63004 | 0.65385 | 0.018926 | 0.02381 | 1451.4078 | 2338.1956 | 6.4777
38957.5641 | 1485 | 802 | 38957.5641 | 1206 | 690 | 870.5 | 1030.5 | 90.6593 | 48.9621 | 73.6264 | 42.1245 | 0.90659 | 0.48962 | 0.73626 | 0.42125 | 0.41697 | 0.31502 | 7.8997 | 11.0363 | 2.1562
38957.5663 | 1204 | 1125 | 38957.5663 | 971 | 938 | 1055.5 | 1215.5 | 73.5043 | 68.6813 | 59.2796 | 57.265 | 0.73504 | 0.68681 | 0.5928 | 0.57265 | 0.04823 | 0.020147 | 32.265 | 41.0831 | 5.5905
38957.5684 | 1155 | 1132 | 38957.5684 | 1199 | 1179 | 1240 | 1400 | 70.5128 | 69.1087 | 73.199 | 71.978 | 0.70513 | 0.69109 | 0.73199 | 0.71978 | 0.014042 | 0.01221 | 28375.098 | 5768.5262 | 15.1074

## C4-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 12
Time-75 | N11 | N12 | Time-76 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R12-G | R4-12
38957.5534 | 1 | 0 | 38957.5534 | 1 | 0 | -56 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5555 | 1 | 0 | 38957.5556 | 1 | 0 | 128.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5577 | 1 | 0 | 38957.5577 | 1 | 0 | 313.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5598 | 1 | 0 | 38957.5598 | 1 | 0 | 498 | 658 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.562 | 1032 | 1002 | 38957.562 | 1017 | 987 | 683 | 843 | 63.0037 | 61.1722 | 62.0879 | 60.2564 | 0.63004 | 0.61172 | 0.62088 | 0.60256 | 0.018315 | 0.018315 | 6943.4 | 6943.4 | 7.7743
38957.5641 | 1597 | 730 | 38957.5641 | 1651 | 825 | 867.5 | 1027.5 | 97.4969 | 44.5665 | 100.7937 | 50.3663 | 0.97497 | 0.44567 | 1.0079 | 0.50366 | 0.5293 | 0.50427 | 179.7544 | 125.8772 | 16.3352
38957.5662 | 1044 | 968 | 38957.5663 | 1039 | 964 | 1052.5 | 1212.5 | 63.7363 | 59.0965 | 63.431 | 58.8523 | 0.63736 | 0.59096 | 0.63431 | 0.58852 | 0.046398 | 0.045788 | 2382.0994 | 3110.262 | 10.1109
38957.5684 | 1099 | 1075 | 38957.5684 | 1169 | 1146 | 1237.5 | 1397.5 | 67.094 | 65.6288 | 71.3675 | 69.9634 | 0.67094 | 0.65629 | 0.71368 | 0.69963 | 0.014652 | 0.014042 | 13279.7768 | 6569.2266 | 5.5875

## C4-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 11
Time-73 | N11 | N12 | Time-74 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R11-G | R4-11
38957.5534 | 1 | 0 | 38957.5534 | 1 | 0 | -59 | 101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5555 | 1 | 0 | 38957.5555 | 1 | 0 | 126 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5577 | 1 | 0 | 38957.5577 | 1 | 0 | 310.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5598 | 1 | 0 | 38957.5598 | 1 | 0 | 495.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5619 | 1074 | 1042 | 38957.5619 | 1151 | 1191 | 680 | 840 | 65.5678 | 63.6142 | 70.2686 | 72.7106 | 0.65568 | 0.63614 | 0.70269 | 0.72711 | 0.019536 | 0.02442 | 2216.2093 | 7001.3912 | 0.28196
38957.5641 | 1389 | 774 | 38957.5641 | 1394 | 722 | 865 | 1025 | 84.7985 | 47.2527 | 85.1038 | 44.0781 | 0.84799 | 0.47253 | 0.85104 | 0.44078 | 0.37546 | 0.41026 | 49.0733 | 89.9596 | 3.058
38957.5662 | 1217 | 1131 | 38957.5662 | 1007 | 1059 | 1049.5 | 1209.5 | 74.2979 | 69.0476 | 61.4774 | 64.652 | 0.74298 | 0.69048 | 0.61477 | 0.64652 | 0.052503 | 0.031746 | 569.3675 | 1584.6744 | 19.5431
38957.5683 | 1173 | 1150 | 38957.5684 | 1119 | 1094 | 1234.5 | 1394.5 | 71.6117 | 70.2076 | 68.315 | 66.7888 | 0.71612 | 0.70208 | 0.68315 | 0.66789 | 0.014042 | 0.015263 | 5498.0742 | 19482.4748 | 18.1659

## C4-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 10
Time-71 | N11 | N12 | Time-72 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38957.5533 | 1 | 0 | 38957.5534 | 1 | 0 | -61.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5555 | 1 | 0 | 38957.5555 | 1 | 0 | 123 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5576 | 1 | 0 | 38957.5576 | 1 | 0 | 307.5 | 467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5598 | 1 | 0 | 38957.5598 | 1 | 0 | 492.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5619 | 934 | 965 | 38957.5619 | 974 | 944 | 677.5 | 837.5 | 57.0208 | 58.9133 | 59.4628 | 57.6313 | 0.57021 | 0.58913 | 0.59463 | 0.57631 | 0.018926 | 0.018315 | 6792.3455 | 7073.7785 | 21.8691
38957.564 | 1196 | 726 | 38957.5641 | 1479 | 902 | 862 | 1022 | 73.0159 | 44.3223 | 90.293 | 55.0672 | 0.73016 | 0.44322 | 0.90293 | 0.55067 | 0.28694 | 0.35226 | 60.7406 | 69.8256 | 10.8182
38957.5662 | 1180 | 1091 | 38957.5662 | 1102 | 1018 | 1047 | 1207 | 72.0391 | 66.6056 | 67.2772 | 62.149 | 0.72039 | 0.66606 | 0.67277 | 0.62149 | 0.054335 | 0.051282 | 10060.9733 | 1368.431 | 13.4942
38957.5683 | 1196 | 1196 | 38957.5683 | 1163 | 1196 | 1231.5 | 1391.5 | 73.0159 | 73.0159 | 71.0012 | 73.0159 | 0.73016 | 0.73016 | 0.71001 | 0.73016 | 0 | 0.020147 | 1416.9166 | 1847.9775 | 22.1286

## C4-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 9
Time-69 | N11 | N12 | Time-70 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38957.5533 | 1 | 0 | 38957.5533 | 1 | 0 | -64.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5554 | 1 | 0 | 38957.5555 | 1 | 0 | 120 | 280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5576 | 1 | 0 | 38957.5576 | 1 | 0 | 305 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5597 | 1 | 0 | 38957.5597 | 1 | 0 | 489.5 | 649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5619 | 1204 | 1076 | 38957.5619 | 1187 | 1156 | 674.5 | 834.5 | 73.5043 | 65.6899 | 72.4664 | 70.5739 | 0.73504 | 0.6569 | 0.72466 | 0.70574 | 0.078144 | 0.018926 | 472.0721 | 1666.6774 | 14.6402
38957.564 | 1252 | 785 | 38957.564 | 1605 | 794 | 859.5 | 1019.5 | 76.4347 | 47.9243 | 97.9853 | 48.4737 | 0.76435 | 0.47924 | 0.97985 | 0.48474 | 0.2851 | 0.49512 | 46.5397 | 56.7575 | 3.5063
38957.5661 | 1135 | 1137 | 38957.5662 | 981 | 904 | 1044 | 1204 | 69.2918 | 69.4139 | 59.8901 | 55.1893 | 0.69292 | 0.69414 | 0.5989 | 0.55189 | 0.001221 | 0.047009 | 92.9709 | 108.2895 | 7.2694
38957.5683 | 1169 | 1145 | 38957.5683 | 1120 | 1095 | 1229 | 1389 | 71.3675 | 69.9023 | 68.3761 | 66.8498 | 0.71368 | 0.69902 | 0.68376 | 0.6685 | 0.014652 | 0.015263 | 6600.7916 | 11806.0929 | 17.4054

## C4-8
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 8
Time-67 | N11 | N12 | Time-68 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38957.5533 | 1 | 0 | 38957.5533 | 1 | 0 | -67.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5554 | 1 | 0 | 38957.5554 | 1 | 0 | 117.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5575 | 1 | 0 | 38957.5576 | 1 | 0 | 302 | 462 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5597 | 1 | 0 | 38957.5597 | 1 | 0 | 487 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5618 | 1040 | 1011 | 38957.5618 | 980 | 952 | 671.5 | 831.5 | 63.4921 | 61.7216 | 59.8291 | 58.1197 | 0.63492 | 0.61722 | 0.59829 | 0.5812 | 0.017705 | 0.017094 | 5567.1319 | 10395.0291 | 6.0761
38957.564 | 1280 | 743 | 38957.564 | 1227 | 833 | 856.5 | 1016.5 | 78.1441 | 45.3602 | 74.9084 | 50.8547 | 0.78144 | 0.4536 | 0.74908 | 0.50855 | 0.32784 | 0.24054 | 65.0931 | 100.0355 | 6.0589
38957.5661 | 1080 | 1065 | 38957.5661 | 1007 | 918 | 1041.5 | 1201.5 | 65.9341 | 65.0183 | 61.4774 | 56.044 | 0.65934 | 0.65018 | 0.61477 | 0.56044 | 0.0091575 | 0.054335 | 210.8465 | 224.2391 | 2.0767
38957.5682 | 1191 | 1143 | 38957.5683 | 1186 | 1163 | 1226 | 1386 | 72.7106 | 69.7802 | 72.4054 | 71.0012 | 0.72711 | 0.6978 | 0.72405 | 0.71001 | 0.029304 | 0.014042 | 2606.4316 | 9053.3231 | 19.1221

## C4-7
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 7
Time-65 | N11 | N12 | Time-66 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38957.5532 | 1 | 0 | 38957.5533 | 1 | 0 | -70 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5554 | 1 | 0 | 38957.5554 | 1 | 0 | 114.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5575 | 1 | 0 | 38957.5575 | 1 | 0 | 299.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5597 | 1 | 0 | 38957.5597 | 1 | 0 | 484 | 644 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5618 | 1167 | 1183 | 38957.5618 | 1085 | 1054 | 669 | 829 | 71.2454 | 72.2222 | 66.2393 | 64.3468 | 0.71245 | 0.72222 | 0.66239 | 0.64347 | 0.009768 | 0.018926 | 1356.5333 | 2201.4193 | 19.1617
38957.5639 | 1432 | 706 | 38957.5639 | 1461 | 917 | 853.5 | 1013.5 | 87.4237 | 43.1013 | 89.1941 | 55.9829 | 0.87424 | 0.43101 | 0.89194 | 0.55983 | 0.44322 | 0.33211 | 227.7241 | 165.3608 | 2.2049
38957.5661 | 1100 | 1002 | 38957.5661 | 1030 | 929 | 1038.5 | 1198.5 | 67.1551 | 61.1722 | 62.8816 | 56.7155 | 0.67155 | 0.61172 | 0.62882 | 0.56716 | 0.059829 | 0.061661 | 3369.7663 | 1474.8747 | 1.03
38957.5682 | 1164 | 1140 | 38957.5682 | 1116 | 1169 | 1223.5 | 1383.5 | 71.0623 | 69.5971 | 68.1319 | 71.3675 | 0.71062 | 0.69597 | 0.68132 | 0.71368 | 0.014652 | 0.032357 | 1059.0627 | 1737.5552 | 15.841

## C4-6
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 6
Time-63 | N11 | N12 | Time-64 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38957.5532 | 1 | 0 | 38957.5532 | 1 | 0 | -73 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5553 | 1 | 0 | 38957.5554 | 1 | 0 | 111.5 | 271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5575 | 1 | 0 | 38957.5575 | 1 | 0 | 296.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5596 | 1 | 0 | 38957.5596 | 1 | 0 | 481.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5618 | 1185 | 1151 | 38957.5618 | 1053 | 1006 | 666 | 826 | 72.3443 | 70.2686 | 64.2857 | 61.4164 | 0.72344 | 0.70269 | 0.64286 | 0.61416 | 0.020757 | 0.028694 | 964.6829 | 1850.4977 | 18.3795
38957.5639 | 1309 | 836 | 38957.5639 | 1292 | 856 | 851 | 1011 | 79.9145 | 51.0379 | 78.8767 | 52.2589 | 0.79915 | 0.51038 | 0.78877 | 0.52259 | 0.28877 | 0.26618 | 232.7368 | 655.4967 | 3.319
38957.566 | 1182 | 1087 | 38957.5661 | 1095 | 981 | 1035.5 | 1195.5 | 72.1612 | 66.3614 | 66.8498 | 59.8901 | 0.72161 | 0.66361 | 0.6685 | 0.5989 | 0.057998 | 0.069597 | 435.7479 | 916.061 | 12.9373
38957.5682 | 1043 | 1140 | 38957.5682 | 1159 | 1196 | 1220.5 | 1380.5 | 63.6752 | 69.5971 | 70.757 | 73.0159 | 0.63675 | 0.69597 | 0.70757 | 0.73016 | 0.059219 | 0.022589 | 680.3414 | 1891.2711 | 5.8303

## C4-5
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 5
Time-61 | N11 | N12 | Time-62 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38957.5532 | 1 | 0 | 38957.5532 | 1 | 0 | -75.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5553 | 1 | 0 | 38957.5553 | 1 | 0 | 109 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5575 | 1 | 0 | 38957.5575 | 1 | 0 | 293.5 | 453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5596 | 1 | 0 | 38957.5596 | 1 | 0 | 478.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5617 | 1008 | 960 | 38957.5617 | 946 | 1030 | 663.5 | 823.5 | 61.5385 | 58.6081 | 57.7534 | 62.8816 | 0.61538 | 0.58608 | 0.57753 | 0.62882 | 0.029304 | 0.051282 | 1221.5406 | 2260.889 | 14.4664
38957.5639 | 1276 | 734 | 38957.5639 | 1150 | 755 | 848 | 1008 | 77.8999 | 44.8107 | 70.2076 | 46.0928 | 0.779 | 0.44811 | 0.70208 | 0.46093 | 0.33089 | 0.24115 | 108.5637 | 320.5323 | 10.6979
38957.566 | 1003 | 916 | 38957.566 | 1019 | 934 | 1033 | 1193 | 61.2332 | 55.9219 | 62.21 | 57.0208 | 0.61233 | 0.55922 | 0.6221 | 0.57021 | 0.053114 | 0.051893 | 2071.856 | 2740.5552 | 20.4356
38957.5681 | 1190 | 1167 | 38957.5682 | 1159 | 1136 | 1217.5 | 1377.5 | 72.6496 | 71.2454 | 70.757 | 69.3529 | 0.7265 | 0.71245 | 0.70757 | 0.69353 | 0.014042 | 0.014042 | 9087.0435 | 9087.0435 | 20.679

## C3-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 12
Time-59 | N11 | N12 | Time-60 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R12-G | R3-12
38957.5531 | 1 | 0 | 38957.5532 | 1 | 0 | -78.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5553 | 1 | 0 | 38957.5553 | 1 | 0 | 106.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5574 | 1 | 0 | 38957.5574 | 1 | 0 | 291 | 451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5596 | 1 | 0 | 38957.5596 | 1 | 0 | 475.5 | 635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5617 | 1016 | 1034 | 38957.5617 | 1161 | 916 | 660.5 | 820.5 | 62.0269 | 63.1258 | 70.8791 | 55.9219 | 0.62027 | 0.63126 | 0.70879 | 0.55922 | 0.010989 | 0.14957 | 41.17 | 39.0689 | 1.7122
38957.5638 | 1856 | 538 | 38957.5639 | 1269 | 667 | 845.5 | 1005.5 | 113.3089 | 32.8449 | 77.4725 | 40.7204 | 1.1331 | 0.32845 | 0.77473 | 0.4072 | 0.80464 | 0.36752 | 17.9973 | 488.6171 | 43.354
38957.566 | 1045 | 938 | 38957.566 | 1040 | 1069 | 1030 | 1190 | 63.7973 | 57.265 | 63.4921 | 65.2625 | 0.63797 | 0.57265 | 0.63492 | 0.65263 | 0.065324 | 0.017705 | 163.5463 | 171.7829 | 8.7612
38957.5681 | 961 | 1076 | 38957.5681 | 1196 | 943 | 1215 | 1375 | 58.6691 | 65.6899 | 73.0159 | 57.5702 | 0.58669 | 0.6569 | 0.73016 | 0.5757 | 0.070208 | 0.15446 | 25.0388 | 23.9861 | 1.3668

## C3-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 11
Time-57 | N11 | N12 | Time-58 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R11-G | R3-11
38957.5531 | 1 | 0 | 38957.5531 | 1 | 0 | -81.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5553 | 1 | 0 | 38957.5553 | 1 | 0 | 103.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5574 | 1 | 0 | 38957.5574 | 1 | 0 | 288 | 448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5595 | 1 | 0 | 38957.5595 | 1 | 0 | 473 | 633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5617 | 953 | 908 | 38957.5617 | 971 | 924 | 657.5 | 817.5 | 58.1807 | 55.4335 | 59.2796 | 56.4103 | 0.58181 | 0.55433 | 0.5928 | 0.5641 | 0.027473 | 0.028694 | 5574.0633 | 3753.7771 | 27.0353
38957.5638 | 1429 | 518 | 38957.5638 | 1530 | 447 | 842.5 | 1002.5 | 87.2405 | 31.6239 | 93.4066 | 27.2894 | 0.87241 | 0.31624 | 0.93407 | 0.27289 | 0.55617 | 0.66117 | 560.0662 | 65.6637 | 12.7037
38957.5659 | 1062 | 1068 | 38957.566 | 1110 | 1006 | 1027.5 | 1187.5 | 64.8352 | 65.2015 | 67.7656 | 61.4164 | 0.64835 | 0.65201 | 0.67766 | 0.61416 | 0.003663 | 0.063492 | 19.2415 | 19.5738 | 0.26026
38957.5681 | 1203 | 960 | 38957.5681 | 1194 | 1173 | 1212 | 1372 | 73.4432 | 58.6081 | 72.8938 | 71.6117 | 0.73443 | 0.58608 | 0.72894 | 0.71612 | 0.14835 | 0.012821 | 142.622 | 242.9983 | 3.6884

## C3-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 10
Time-55 | N11 | N12 | Time-56 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38957.5531 | 1 | 0 | 38957.5531 | 1 | 0 | -84 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5552 | 1 | 0 | 38957.5552 | 1 | 0 | 100.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5574 | 1 | 0 | 38957.5574 | 1 | 0 | 285.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5595 | 1 | 0 | 38957.5595 | 1 | 0 | 470 | 630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5616 | 957 | 909 | 38957.5617 | 1180 | 1127 | 655 | 815 | 58.4249 | 55.4945 | 72.0391 | 68.8034 | 0.58425 | 0.55495 | 0.72039 | 0.68803 | 0.029304 | 0.032357 | 1596.2896 | 3722.4819 | 26.464
38957.5638 | 1937 | 465 | 38957.5638 | 1577 | 601 | 839.5 | 999.5 | 118.254 | 28.3883 | 96.2759 | 36.6911 | 1.1825 | 0.28388 | 0.96276 | 0.36691 | 0.89866 | 0.59585 | 55.2282 | 40.3196 | 17.8572
38957.5659 | 1156 | 1116 | 38957.5659 | 1264 | 1128 | 1024.5 | 1184.5 | 70.5739 | 68.1319 | 77.1673 | 68.8645 | 0.70574 | 0.68132 | 0.77167 | 0.68864 | 0.02442 | 0.083028 | 378.8296 | 524.8666 | 11.9658
38957.5681 | 936 | 972 | 38957.5681 | 969 | 1086 | 1209.5 | 1369.5 | 57.1429 | 59.3407 | 59.1575 | 66.3004 | 0.57143 | 0.59341 | 0.59158 | 0.663 | 0.021978 | 0.071429 | 401.0826 | 377.5333 | 16.6756

## C3-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 9
Time-53 | N11 | N12 | Time-54 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38957.553 | 1 | 0 | 38957.5531 | 1 | 0 | -87 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5552 | 1 | 0 | 38957.5552 | 1 | 0 | 98 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5573 | 1 | 0 | 38957.5573 | 1 | 0 | 282.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5595 | 1 | 0 | 38957.5595 | 1 | 0 | 467.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5616 | 1101 | 1098 | 38957.5616 | 1213 | 1181 | 652 | 812 | 67.2161 | 67.033 | 74.0537 | 72.1001 | 0.67216 | 0.67033 | 0.74054 | 0.721 | 0.0018315 | 0.019536 | 1189.7289 | 1337.9952 | 7.2861
38957.5637 | 1449 | 555 | 38957.5638 | 1653 | 456 | 837 | 997 | 88.4615 | 33.8828 | 100.9158 | 27.8388 | 0.88462 | 0.33883 | 1.0092 | 0.27839 | 0.54579 | 0.73077 | 20.6982 | 23.9834 | 3.7998
38957.5659 | 1052 | 907 | 38957.5659 | 1122 | 1007 | 1021.5 | 1181.5 | 64.2247 | 55.3724 | 68.4982 | 61.4774 | 0.64225 | 0.55372 | 0.68498 | 0.61477 | 0.088523 | 0.070208 | 350.68 | 575.6512 | 14.4679
38957.568 | 963 | 1081 | 38957.568 | 1194 | 926 | 1206.5 | 1366.5 | 58.7912 | 65.9951 | 72.8938 | 56.5324 | 0.58791 | 0.65995 | 0.72894 | 0.56532 | 0.072039 | 0.16361 | 30.831 | 29.9274 | 1.4707

## C3-8
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 8
Time-51 | N11 | N12 | Time-52 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38957.553 | 1 | 0 | 38957.553 | 1 | 0 | -89.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5552 | 1 | 0 | 38957.5552 | 1 | 0 | 95 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5573 | 1 | 0 | 38957.5573 | 1 | 0 | 280 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5594 | 1 | 0 | 38957.5594 | 1 | 0 | 464.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5616 | 1182 | 1047 | 38957.5616 | 1086 | 880 | 649.5 | 809.5 | 72.1612 | 63.9194 | 66.3004 | 53.7241 | 0.72161 | 0.63919 | 0.663 | 0.53724 | 0.082418 | 0.12576 | 45.1957 | 54.3903 | 3.9025
38957.5637 | 1224 | 711 | 38957.5637 | 1730 | 421 | 834 | 994 | 74.7253 | 43.4066 | 105.6166 | 25.7021 | 0.74725 | 0.43407 | 1.0562 | 0.25702 | 0.31319 | 0.79915 | 5.6089 | 4.6358 | 1.1093
38957.5658 | 1140 | 1041 | 38957.5659 | 1226 | 1133 | 1019 | 1179 | 69.5971 | 63.5531 | 74.8474 | 69.1697 | 0.69597 | 0.63553 | 0.74847 | 0.6917 | 0.06044 | 0.056777 | 3515.9379 | 1459.5071 | 6.1115
38957.568 | 992 | 1104 | 38957.568 | 938 | 974 | 1203.5 | 1363.5 | 60.5617 | 67.3993 | 57.265 | 59.4628 | 0.60562 | 0.67399 | 0.57265 | 0.59463 | 0.068376 | 0.021978 | 263.3677 | 351.9866 | 1.2006

## C3-7
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 7
Time-49 | N11 | N12 | Time-50 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38957.553 | 1 | 0 | 38957.553 | 1 | 0 | -92.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5551 | 1 | 0 | 38957.5551 | 1 | 0 | 92.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5573 | 1 | 0 | 38957.5573 | 1 | 0 | 277 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5594 | 1 | 0 | 38957.5594 | 1 | 0 | 461.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5615 | 1052 | 922 | 38957.5616 | 1263 | 1099 | 646.5 | 806.5 | 64.2247 | 56.2882 | 77.1062 | 67.094 | 0.64225 | 0.56288 | 0.77106 | 0.67094 | 0.079365 | 0.10012 | 273.6487 | 357.7377 | 11.784
38957.5637 | 989 | 908 | 38957.5637 | 1092 | 1050 | 831.5 | 991.5 | 60.3785 | 55.4335 | 66.6667 | 64.1026 | 0.60379 | 0.55433 | 0.66667 | 0.64103 | 0.049451 | 0.025641 | 435.8574 | 513.3217 | 19.9117
38957.5658 | 1183 | 941 | 38957.5658 | 1294 | 1098 | 1016 | 1176 | 72.2222 | 57.4481 | 78.9988 | 67.033 | 0.72222 | 0.57448 | 0.78999 | 0.67033 | 0.14774 | 0.11966 | 1972.2247 | 482.9502 | 0.96668
38957.568 | 1169 | 1144 | 38957.568 | 958 | 1073 | 1201 | 1361 | 71.3675 | 69.8413 | 58.486 | 65.5067 | 0.71368 | 0.69841 | 0.58486 | 0.65507 | 0.015263 | 0.070208 | 133.5645 | 167.7937 | 10.9531

## C3-6
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 6
Time-47 | N11 | N12 | Time-48 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38957.553 | 1 | 0 | 38957.553 | 1 | 0 | -95.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5551 | 1 | 0 | 38957.5551 | 1 | 0 | 89.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5572 | 1 | 0 | 38957.5572 | 1 | 0 | 274.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5594 | 1 | 0 | 38957.5594 | 1 | 0 | 459 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5615 | 980 | 913 | 38957.5615 | 1046 | 994 | 643.5 | 803.5 | 59.8291 | 55.7387 | 63.8584 | 60.6838 | 0.59829 | 0.55739 | 0.63858 | 0.60684 | 0.040904 | 0.031746 | 1255.2208 | 3924.4183 | 23.4998
38957.5636 | 1053 | 940 | 38957.5637 | 948 | 951 | 828.5 | 988.5 | 64.2857 | 57.3871 | 57.8755 | 58.0586 | 0.64286 | 0.57387 | 0.57875 | 0.58059 | 0.068987 | 0.0018315 | 264.699 | 326.9993 | 9.7779
38957.5658 | 1236 | 906 | 38957.5658 | 1278 | 1086 | 1013.5 | 1173.5 | 75.4579 | 55.3114 | 78.022 | 66.3004 | 0.75458 | 0.55311 | 0.78022 | 0.663 | 0.20147 | 0.11722 | 247.6136 | 3745.502 | 3.1155
38957.5679 | 1095 | 1069 | 38957.5679 | 1126 | 1099 | 1198 | 1358 | 66.8498 | 65.2625 | 68.7424 | 67.094 | 0.6685 | 0.65263 | 0.68742 | 0.67094 | 0.015873 | 0.016484 | 5312.4812 | 15635.0486 | 4.7386

## C3-5
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 5
Time-45 | N11 | N12 | Time-46 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38957.5529 | 1 | 0 | 38957.5529 | 1 | 0 | -98 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5551 | 1 | 0 | 38957.5551 | 1 | 0 | 86.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5572 | 1 | 0 | 38957.5572 | 1 | 0 | 271.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5593 | 1 | 0 | 38957.5594 | 1 | 0 | 456 | 616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5615 | 1220 | 1089 | 38957.5615 | 1121 | 1061 | 641 | 801 | 74.4811 | 66.4835 | 68.4371 | 64.7741 | 0.74481 | 0.66484 | 0.68437 | 0.64774 | 0.079976 | 0.03663 | 417.1429 | 1310.783 | 16.7207
38957.5636 | 980 | 936 | 38957.5636 | 1104 | 926 | 825.5 | 985.5 | 59.8291 | 57.1429 | 67.3993 | 56.5324 | 0.59829 | 0.57143 | 0.67399 | 0.56532 | 0.026862 | 0.10867 | 226.251 | 204.9126 | 14.1458
38957.5658 | 1268 | 1082 | 38957.5658 | 1282 | 1063 | 1010.5 | 1170.5 | 77.4115 | 66.0562 | 78.2662 | 64.8962 | 0.77411 | 0.66056 | 0.78266 | 0.64896 | 0.11355 | 0.1337 | 543.6908 | 3538.5965 | 21.3001
38957.5679 | 1058 | 1032 | 38957.5679 | 1130 | 1104 | 1195.5 | 1355.5 | 64.591 | 63.0037 | 68.9866 | 67.3993 | 0.64591 | 0.63004 | 0.68987 | 0.67399 | 0.015873 | 0.015873 | 8027 | 8027 | 2.2032

## C3-4
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-43 | N11 | N12 | Time-44 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38957.5529 | 1 | 0 | 38957.5529 | 1 | 0 | -101 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.555 | 1 | 0 | 38957.555 | 1 | 0 | 84 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5572 | 1 | 0 | 38957.5572 | 1 | 0 | 268.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5593 | 1 | 0 | 38957.5593 | 1 | 0 | 453.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5614 | 1022 | 928 | 38957.5615 | 1241 | 1144 | 638 | 798 | 62.3932 | 56.6545 | 75.7631 | 69.8413 | 0.62393 | 0.56654 | 0.75763 | 0.69841 | 0.057387 | 0.059219 | 1370.1106 | 6457.93 | 17.2989
38957.5636 | 1171 | 1121 | 38957.5636 | 1175 | 1186 | 823 | 983 | 71.4896 | 68.4371 | 71.7338 | 72.4054 | 0.7149 | 0.68437 | 0.71734 | 0.72405 | 0.030525 | 0.0067155 | 1289.7668 | 4865.8723 | 15.6446
38957.5657 | 1209 | 952 | 38957.5657 | 1227 | 932 | 1007.5 | 1167.5 | 73.8095 | 58.1197 | 74.9084 | 56.8987 | 0.7381 | 0.5812 | 0.74908 | 0.56899 | 0.1569 | 0.1801 | 162.3933 | 317.6663 | 3.8332
38957.5679 | 1103 | 1076 | 38957.5679 | 1036 | 1080 | 1192.5 | 1352.5 | 67.3382 | 65.6899 | 63.2479 | 65.9341 | 0.67338 | 0.6569 | 0.63248 | 0.65934 | 0.016484 | 0.026862 | 406.6272 | 486.0208 | 5.0856

## C2-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 12
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R12-G | R2-12
38957.5529 | 1 | 0 | 38957.5529 | 1 | 0 | -103.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.555 | 2 | 0 | 38957.555 | 1 | 0 | 81 | 241 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38957.5571 | 1 | 0 | 38957.5571 | 1 | 0 | 265.5 | 425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5593 | 1 | 0 | 38957.5593 | 1 | 0 | 450.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5614 | 1023 | 929 | 38957.5614 | 1065 | 1077 | 635.5 | 795.5 | 62.4542 | 56.7155 | 65.0183 | 65.7509 | 0.62454 | 0.56716 | 0.65018 | 0.65751 | 0.057387 | 0.007326 | 162.34 | 160.8818 | 10.6888
38957.5635 | 1103 | 1046 | 38957.5636 | 1094 | 1048 | 820 | 980 | 67.3382 | 63.8584 | 66.7888 | 63.9805 | 0.67338 | 0.63858 | 0.66789 | 0.6398 | 0.034799 | 0.028083 | 671.9149 | 1120.8789 | 3.158
38957.5657 | 1313 | 1056 | 38957.5657 | 1312 | 995 | 1005 | 1165 | 80.1587 | 64.4689 | 80.0977 | 60.7448 | 0.80159 | 0.64469 | 0.80098 | 0.60745 | 0.1569 | 0.19353 | 318.0141 | 19438.3153 | 24.1165
38957.5678 | 1154 | 1126 | 38957.5678 | 952 | 928 | 1189.5 | 1349.5 | 70.4518 | 68.7424 | 58.1197 | 56.6545 | 0.70452 | 0.68742 | 0.5812 | 0.56654 | 0.017094 | 0.014652 | 1249.205 | 2308.7764 | 14.2138

## C2-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 11
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R11-G | R2-11
38957.5528 | 1 | 0 | 38957.5528 | 1 | 0 | -106.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.555 | 1 | 0 | 38957.555 | 1 | 0 | 78.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5571 | 1 | 0 | 38957.5571 | 1 | 0 | 263 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5592 | 1 | 0 | 38957.5592 | 1 | 0 | 447.5 | 607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5614 | 1008 | 980 | 38957.5614 | 1154 | 1051 | 632.5 | 792.5 | 61.5385 | 59.8291 | 70.4518 | 64.1636 | 0.61538 | 0.59829 | 0.70452 | 0.64164 | 0.017094 | 0.062882 | 40.1637 | 35.9859 | 3.3759
38957.5635 | 941 | 937 | 38957.5635 | 1196 | 1124 | 817.5 | 977.5 | 57.4481 | 57.2039 | 73.0159 | 68.6203 | 0.57448 | 0.57204 | 0.73016 | 0.6862 | 0.002442 | 0.043956 | 33.8231 | 27.072 | 5.3436
38957.5656 | 1094 | 919 | 38957.5657 | 1047 | 858 | 1002 | 1162 | 66.7888 | 56.105 | 63.9194 | 52.381 | 0.66789 | 0.56105 | 0.63919 | 0.52381 | 0.10684 | 0.11538 | 2315.2086 | 701.6026 | 9.5258
38957.5678 | 1041 | 1086 | 38957.5678 | 1121 | 1174 | 1187 | 1347 | 63.5531 | 66.3004 | 68.4371 | 71.6728 | 0.63553 | 0.663 | 0.68437 | 0.71673 | 0.027473 | 0.032357 | 1637.3545 | 5304.6285 | 1.2635

## C2-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 10
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R10-G | R2-10
38957.5528 | 1 | 0 | 38957.5528 | 1 | 0 | -109.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5549 | 2 | 0 | 38957.5549 | 1 | 0 | 75.5 | 235.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38957.5571 | 1 | 0 | 38957.5571 | 1 | 0 | 260 | 420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5592 | 1 | 0 | 38957.5592 | 1 | 0 | 445 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5613 | 1243 | 1134 | 38957.5614 | 1101 | 992 | 629.5 | 789.5 | 75.8852 | 69.2308 | 67.2161 | 60.5617 | 0.75885 | 0.69231 | 0.67216 | 0.60562 | 0.066545 | 0.066545 | 1838.5505 | 1838.5505 | 22.0778
38957.5635 | 936 | 954 | 38957.5635 | 1147 | 1162 | 814.5 | 974.5 | 57.1429 | 58.2418 | 70.0244 | 70.9402 | 0.57143 | 0.58242 | 0.70024 | 0.7094 | 0.010989 | 0.0091575 | 925.066 | 873.3358 | 20.9756
38957.5656 | 976 | 917 | 38957.5656 | 1012 | 896 | 999.5 | 1159.5 | 59.5849 | 55.9829 | 61.7827 | 54.7009 | 0.59585 | 0.55983 | 0.61783 | 0.54701 | 0.03602 | 0.070818 | 1038.954 | 1818.0406 | 22.7425
38957.5678 | 1008 | 1050 | 38957.5678 | 1125 | 1097 | 1184 | 1344 | 61.5385 | 64.1026 | 68.6813 | 66.9719 | 0.61538 | 0.64103 | 0.68681 | 0.66972 | 0.025641 | 0.017094 | 496.5606 | 581.6054 | 4.4712

## C2-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 9
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R9-G | R2-9
38957.5528 | 1 | 0 | 38957.5528 | 1 | 0 | -112 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5549 | 1 | 0 | 38957.5549 | 1 | 0 | 72.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.557 | 1 | 0 | 38957.557 | 1 | 0 | 257.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5592 | 1 | 0 | 38957.5592 | 1 | 0 | 442 | 602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5613 | 1132 | 1130 | 38957.5613 | 1149 | 1049 | 627 | 787 | 69.1087 | 68.9866 | 70.1465 | 64.0415 | 0.69109 | 0.68987 | 0.70147 | 0.64042 | 0.001221 | 0.06105 | 215.7584 | 249.622 | 9.4131
38957.5634 | 1182 | 1186 | 38957.5635 | 1101 | 1129 | 811.5 | 971.5 | 72.1612 | 72.4054 | 67.2161 | 68.9255 | 0.72161 | 0.72405 | 0.67216 | 0.68926 | 0.002442 | 0.017094 | 1360.7141 | 1841.0024 | 20.3915
38957.5656 | 1230 | 995 | 38957.5656 | 1242 | 1105 | 996.5 | 1156.5 | 75.0916 | 60.7448 | 75.8242 | 67.4603 | 0.75092 | 0.60745 | 0.75824 | 0.6746 | 0.14347 | 0.083639 | 483.142 | 1904.8942 | 10.6929
38957.5677 | 1087 | 1059 | 38957.5677 | 1090 | 1064 | 1181.5 | 1341.5 | 66.3614 | 64.652 | 66.5446 | 64.9573 | 0.66361 | 0.64652 | 0.66545 | 0.64957 | 0.017094 | 0.015873 | 6945.7769 | 8005.6569 | 3.0758

## C2-8
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 8
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R8-G | R2-8
38957.5527 | 1 | 0 | 38957.5527 | 1 | 0 | -115 | 45 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5549 | 1 | 0 | 38957.5549 | 1 | 0 | 70 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.557 | 1 | 0 | 38957.557 | 1 | 0 | 254.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5591 | 1 | 0 | 38957.5592 | 1 | 0 | 439.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5613 | 1044 | 1029 | 38957.5613 | 1202 | 1109 | 624 | 784 | 63.7363 | 62.8205 | 73.3822 | 67.7045 | 0.63736 | 0.62821 | 0.73382 | 0.67705 | 0.0091575 | 0.056777 | 203.8997 | 202.0471 | 2.6016
38957.5634 | 1147 | 1177 | 38957.5634 | 1135 | 1171 | 809 | 969 | 70.0244 | 71.8559 | 69.2918 | 71.4896 | 0.70024 | 0.71856 | 0.69292 | 0.7149 | 0.018315 | 0.021978 | 3326.4279 | 122701.5737 | 17.9106
38957.5656 | 1243 | 1086 | 38957.5656 | 1097 | 1015 | 993.5 | 1153.5 | 75.8852 | 66.3004 | 66.9719 | 61.9658 | 0.75885 | 0.663 | 0.66972 | 0.61966 | 0.095849 | 0.050061 | 309.8532 | 877.3305 | 17.8528
38957.5677 | 1049 | 1019 | 38957.5677 | 1006 | 979 | 1178.5 | 1338.5 | 64.0415 | 62.21 | 61.4164 | 59.768 | 0.64042 | 0.6221 | 0.61416 | 0.59768 | 0.018315 | 0.016484 | 3164.3222 | 28106.2608 | 4.4024

## C2-7
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 7
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38957.5527 | 1 | 0 | 38957.5527 | 1 | 0 | -117.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5548 | 1 | 0 | 38957.5548 | 1 | 0 | 67 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.557 | 1 | 0 | 38957.557 | 1 | 0 | 252 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5591 | 1 | 0 | 38957.5591 | 1 | 0 | 436.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5612 | 1034 | 1022 | 38957.5613 | 1055 | 974 | 621.5 | 781.5 | 63.1258 | 62.3932 | 64.4078 | 59.4628 | 0.63126 | 0.62393 | 0.64408 | 0.59463 | 0.007326 | 0.049451 | 208.5969 | 202.266 | 3.7334
38957.5634 | 969 | 882 | 38957.5634 | 1014 | 927 | 806 | 966 | 59.1575 | 53.8462 | 61.9048 | 56.5934 | 0.59158 | 0.53846 | 0.61905 | 0.56593 | 0.053114 | 0.053114 | 2328.7586 | 2328.7586 | 28.4843
38957.5655 | 1266 | 1120 | 38957.5655 | 1227 | 1121 | 991 | 1151 | 77.2894 | 68.3761 | 74.9084 | 68.4371 | 0.77289 | 0.68376 | 0.74908 | 0.68437 | 0.089133 | 0.064713 | 4747.1298 | 873.9266 | 21.8706
38957.5677 | 981 | 954 | 38957.5677 | 932 | 961 | 1175.5 | 1335.5 | 59.8901 | 58.2418 | 56.8987 | 58.6691 | 0.5989 | 0.58242 | 0.56899 | 0.58669 | 0.016484 | 0.017705 | 9952.3932 | 6105.3459 | 18.3597

## C2-6
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 6
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38957.5527 | 1 | 0 | 38957.5527 | 1 | 0 | -120.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5548 | 1 | 0 | 38957.5548 | 1 | 0 | 64 | 224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5569 | 1 | 0 | 38957.557 | 1 | 0 | 249 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5591 | 1 | 0 | 38957.5591 | 1 | 0 | 433.5 | 593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5612 | 1216 | 1152 | 38957.5612 | 983 | 910 | 618.5 | 778.5 | 74.2369 | 70.3297 | 60.0122 | 55.5556 | 0.74237 | 0.7033 | 0.60012 | 0.55556 | 0.039072 | 0.044567 | 294.4398 | 478.6973 | 18.3089
38957.5634 | 959 | 979 | 38957.5634 | 1090 | 1042 | 803.5 | 963.5 | 58.547 | 59.768 | 66.5446 | 63.6142 | 0.58547 | 0.59768 | 0.66545 | 0.63614 | 0.01221 | 0.029304 | 604.8167 | 573.1685 | 15.2217
38957.5655 | 1087 | 950 | 38957.5655 | 1121 | 889 | 988 | 1148 | 66.3614 | 57.9976 | 68.4371 | 54.2735 | 0.66361 | 0.57998 | 0.68437 | 0.54274 | 0.083639 | 0.14164 | 205.0842 | 261.4977 | 5.7885
38957.5676 | 967 | 940 | 38957.5677 | 973 | 1007 | 1173 | 1333 | 59.0354 | 57.3871 | 59.4017 | 61.4774 | 0.59035 | 0.57387 | 0.59402 | 0.61477 | 0.016484 | 0.020757 | 30514.449 | 4043.9958 | 21.3881

## C2-5
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 5
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38957.5526 | 1 | 0 | 38957.5526 | 1 | 0 | -123.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5548 | 1 | 0 | 38957.5548 | 1 | 0 | 61.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5569 | 1 | 0 | 38957.5569 | 1 | 0 | 246 | 406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.559 | 1 | 0 | 38957.5591 | 1 | 0 | 431 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5612 | 1221 | 1142 | 38957.5612 | 1141 | 1066 | 615.5 | 775.5 | 74.5421 | 69.7192 | 69.6581 | 65.0794 | 0.74542 | 0.69719 | 0.69658 | 0.65079 | 0.04823 | 0.045788 | 3953.6582 | 2023.4554 | 20.8588
38957.5633 | 954 | 975 | 38957.5633 | 1192 | 1152 | 800.5 | 960.5 | 58.2418 | 59.5238 | 72.7717 | 70.3297 | 0.58242 | 0.59524 | 0.72772 | 0.7033 | 0.012821 | 0.02442 | 283.4355 | 251.3415 | 13.5019
38957.5655 | 1238 | 1086 | 38957.5655 | 1039 | 888 | 985.5 | 1145.5 | 75.58 | 66.3004 | 63.431 | 54.2125 | 0.7558 | 0.663 | 0.63431 | 0.54212 | 0.092796 | 0.092186 | 3344.2663 | 863.0334 | 17.41
38957.5676 | 1175 | 923 | 38957.5676 | 981 | 973 | 1170 | 1330 | 71.7338 | 56.3492 | 59.8901 | 59.4017 | 0.71734 | 0.56349 | 0.5989 | 0.59402 | 0.15385 | 0.004884 | 58.9375 | 68.9037 | 0.66385

## C2-4
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38957.5526 | 1 | 0 | 38957.5526 | 1 | 0 | -126 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5547 | 1 | 0 | 38957.5547 | 1 | 0 | 58.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5569 | 1 | 0 | 38957.5569 | 1 | 0 | 243.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.559 | 1 | 0 | 38957.559 | 1 | 0 | 428.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5611 | 1207 | 1127 | 38957.5612 | 1171 | 1159 | 613 | 773 | 73.6874 | 68.8034 | 71.4896 | 70.757 | 0.73687 | 0.68803 | 0.7149 | 0.70757 | 0.04884 | 0.007326 | 732.0854 | 2575.4828 | 18.8749
38957.5633 | 1052 | 1014 | 38957.5633 | 1209 | 1175 | 797.5 | 957.5 | 64.2247 | 61.9048 | 73.8095 | 71.7338 | 0.64225 | 0.61905 | 0.7381 | 0.71734 | 0.023199 | 0.020757 | 188466.9747 | 2708.5485 | 4.472
38957.5654 | 1097 | 961 | 38957.5654 | 1118 | 977 | 982.5 | 1142.5 | 66.9719 | 58.6691 | 68.254 | 59.6459 | 0.66972 | 0.58669 | 0.68254 | 0.59646 | 0.083028 | 0.086081 | 40421.3711 | 719.9234 | 5.027
38957.5676 | 965 | 936 | 38957.5676 | 957 | 926 | 1167.5 | 1327.5 | 58.9133 | 57.1429 | 58.4249 | 56.5324 | 0.58913 | 0.57143 | 0.58425 | 0.56532 | 0.017705 | 0.018926 | 10211.5983 | 5270.9572 | 22.23

## C2-3
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38957.5526 | 1 | 0 | 38957.5526 | 1 | 0 | -129 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5547 | 1 | 0 | 38957.5547 | 1 | 0 | 56 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5568 | 1 | 0 | 38957.5569 | 1 | 0 | 240.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.559 | 1 | 0 | 38957.559 | 1 | 0 | 425.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5611 | 984 | 919 | 38957.5611 | 1038 | 966 | 610.5 | 770.5 | 60.0733 | 56.105 | 63.37 | 58.9744 | 0.60073 | 0.56105 | 0.6337 | 0.58974 | 0.039683 | 0.043956 | 8790.1486 | 1762.0267 | 21.6258
38957.5633 | 1039 | 1073 | 38957.5633 | 951 | 948 | 795 | 955 | 63.431 | 65.5067 | 58.0586 | 57.8755 | 0.63431 | 0.65507 | 0.58059 | 0.57875 | 0.020757 | 0.0018315 | 636.0726 | 795.6884 | 0.084447
38957.5654 | 1185 | 1029 | 38957.5654 | 1196 | 1104 | 979.5 | 1139.5 | 72.3443 | 62.8205 | 73.0159 | 67.3993 | 0.72344 | 0.62821 | 0.73016 | 0.67399 | 0.095238 | 0.056166 | 589.0061 | 66091.3518 | 9.7986
38957.5675 | 1196 | 922 | 38957.5675 | 988 | 960 | 1164.5 | 1324.5 | 73.0159 | 56.2882 | 60.3175 | 58.6081 | 0.73016 | 0.56288 | 0.60317 | 0.58608 | 0.16728 | 0.017094 | 51.8857 | 61.739 | 0.20618

## C1-12
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 12
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R12-G | R1-12
38957.5525 | 1 | 0 | 38957.5525 | 1 | 0 | -131.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5547 | 1 | 0 | 38957.5547 | 1 | 0 | 53 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5568 | 1 | 0 | 38957.5568 | 1 | 0 | 237.5 | 397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5589 | 1 | 0 | 38957.559 | 1 | 0 | 422.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5611 | 948 | 977 | 38957.5611 | 1006 | 1008 | 607.5 | 767.5 | 57.8755 | 59.6459 | 61.4164 | 61.5385 | 0.57875 | 0.59646 | 0.61416 | 0.61538 | 0.017705 | 0.001221 | 1011.2394 | 1133.3168 | 17.6842
38957.5632 | 1174 | 1111 | 38957.5632 | 1043 | 1007 | 792 | 952 | 71.6728 | 67.8266 | 63.6752 | 61.4774 | 0.71673 | 0.67827 | 0.63675 | 0.61477 | 0.038462 | 0.021978 | 415.8517 | 682.4053 | 13.5013
38957.5654 | 1014 | 877 | 38957.5654 | 1170 | 926 | 977 | 1137 | 61.9048 | 53.5409 | 71.4286 | 56.5324 | 0.61905 | 0.53541 | 0.71429 | 0.56532 | 0.083639 | 0.14896 | 264.5177 | 314.9231 | 19.2145
38957.5675 | 1205 | 1195 | 38957.5675 | 951 | 956 | 1161.5 | 1321.5 | 73.5653 | 72.9548 | 58.0586 | 58.3639 | 0.73565 | 0.72955 | 0.58059 | 0.58364 | 0.006105 | 0.0030525 | 1546.1383 | 2452.3761 | 23.0742

## C1-11
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 11
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R11-G | R1-11
38957.5525 | 1 | 0 | 38957.5525 | 1 | 0 | -134.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5546 | 1 | 0 | 38957.5547 | 1 | 0 | 50.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5568 | 1 | 0 | 38957.5568 | 1 | 0 | 235 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5589 | 1 | 0 | 38957.5589 | 1 | 0 | 419.5 | 579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5611 | 1207 | 1141 | 38957.5611 | 1213 | 904 | 604.5 | 764.5 | 73.6874 | 69.6581 | 74.0537 | 55.1893 | 0.73687 | 0.69658 | 0.74054 | 0.55189 | 0.040293 | 0.18864 | 73.6875 | 98.0625 | 10.1964
38957.5632 | 1120 | 1077 | 38957.5632 | 1135 | 1169 | 789.5 | 949.5 | 68.3761 | 65.7509 | 69.2918 | 71.3675 | 0.68376 | 0.65751 | 0.69292 | 0.71368 | 0.026252 | 0.020757 | 5293.8567 | 4442.697 | 7.6259
38957.5653 | 998 | 871 | 38957.5653 | 1289 | 954 | 974 | 1134 | 60.928 | 53.1746 | 78.6935 | 58.2418 | 0.60928 | 0.53175 | 0.78694 | 0.58242 | 0.077534 | 0.20452 | 46.9528 | 38.7495 | 7.8242
38957.5675 | 989 | 1095 | 38957.5675 | 1066 | 1147 | 1159 | 1319 | 60.3785 | 66.8498 | 65.0794 | 70.0244 | 0.60379 | 0.6685 | 0.65079 | 0.70024 | 0.064713 | 0.049451 | 354.8529 | 519.5566 | 2.2225

## C1-10
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 10
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R10-G | R1-10
38957.5525 | 1 | 0 | 38957.5525 | 1 | 0 | -137.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5546 | 1 | 0 | 38957.5546 | 1 | 0 | 47.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5567 | 1 | 0 | 38957.5568 | 1 | 0 | 232.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5589 | 1 | 0 | 38957.5589 | 1 | 0 | 417 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.561 | 974 | 978 | 38957.561 | 1074 | 1012 | 601.5 | 761.5 | 59.4628 | 59.707 | 65.5678 | 61.7827 | 0.59463 | 0.59707 | 0.65568 | 0.61783 | 0.002442 | 0.037851 | 343.0043 | 298.1056 | 12.3286
38957.5632 | 1192 | 1189 | 38957.5632 | 1100 | 1157 | 786.5 | 946.5 | 72.7717 | 72.5885 | 67.1551 | 70.6349 | 0.72772 | 0.72589 | 0.67155 | 0.70635 | 0.0018315 | 0.034799 | 683.8164 | 902.8904 | 20.2909
38957.5653 | 1185 | 1101 | 38957.5653 | 1224 | 1070 | 971.5 | 1131.5 | 72.3443 | 67.2161 | 74.7253 | 65.3236 | 0.72344 | 0.67216 | 0.74725 | 0.65324 | 0.051282 | 0.094017 | 372.1072 | 665.6757 | 13.6592
38957.5674 | 999 | 1031 | 38957.5675 | 1186 | 1154 | 1156 | 1316 | 60.989 | 62.9426 | 72.4054 | 70.4518 | 0.60989 | 0.62943 | 0.72405 | 0.70452 | 0.019536 | 0.019536 | 4720.1138 | 12276.0739 | 7.9873

## C1-9
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 9
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R9-G | R1-9
38957.5524 | 1 | 0 | 38957.5525 | 1 | 0 | -140 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5546 | 1 | 0 | 38957.5546 | 1 | 0 | 44.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5567 | 1 | 0 | 38957.5567 | 1 | 0 | 229.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5588 | 1 | 0 | 38957.5589 | 1 | 0 | 414 | 574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.561 | 1184 | 1124 | 38957.561 | 947 | 954 | 599 | 759 | 72.2833 | 68.6203 | 57.8144 | 58.2418 | 0.72283 | 0.6862 | 0.57814 | 0.58242 | 0.03663 | 0.0042735 | 17.6507 | 21.6015 | 3.0815
38957.5631 | 1065 | 1102 | 38957.5631 | 1208 | 1025 | 783.5 | 943.5 | 65.0183 | 67.2772 | 73.7485 | 62.5763 | 0.65018 | 0.67277 | 0.73748 | 0.62576 | 0.022589 | 0.11172 | 107.6648 | 117.6835 | 2.6481
38957.5653 | 1105 | 883 | 38957.5653 | 1147 | 889 | 968.5 | 1128.5 | 67.4603 | 53.9072 | 70.0244 | 54.2735 | 0.6746 | 0.53907 | 0.70024 | 0.54274 | 0.13553 | 0.15751 | 1413.2857 | 586.0279 | 12.0947
38957.5674 | 977 | 918 | 38957.5674 | 1102 | 1144 | 1153.5 | 1313.5 | 59.6459 | 56.044 | 67.2772 | 69.8413 | 0.59646 | 0.56044 | 0.67277 | 0.69841 | 0.03602 | 0.025641 | 466.2278 | 497.1245 | 19.7722

## C1-8
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 8
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R8-G | R1-8
38957.5524 | 1 | 0 | 38957.5524 | 1 | 0 | -143 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5545 | 1 | 0 | 38957.5546 | 1 | 0 | 42 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5567 | 1 | 0 | 38957.5567 | 1 | 0 | 226.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5588 | 1 | 0 | 38957.5588 | 1 | 0 | 411.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5609 | 1015 | 962 | 38957.561 | 1060 | 1074 | 596 | 756 | 61.9658 | 58.7302 | 64.7131 | 65.5678 | 0.61966 | 0.5873 | 0.64713 | 0.65568 | 0.032357 | 0.008547 | 290.6071 | 296.1489 | 10.5701
38957.5631 | 1022 | 989 | 38957.5631 | 1169 | 1134 | 781 | 941 | 62.3932 | 60.3785 | 71.3675 | 69.2308 | 0.62393 | 0.60379 | 0.71368 | 0.69231 | 0.020147 | 0.021368 | 2645.0695 | 11991.7899 | 10.2302
38957.5652 | 1373 | 658 | 38957.5652 | 1283 | 1116 | 965.5 | 1125.5 | 83.8217 | 40.1709 | 78.3272 | 68.1319 | 0.83822 | 0.40171 | 0.78327 | 0.68132 | 0.43651 | 0.10195 | 24.835 | 29.054 | 2.8063
38957.5674 | 1102 | 1071 | 38957.5674 | 1075 | 1043 | 1150.5 | 1310.5 | 67.2772 | 65.3846 | 65.6288 | 63.6752 | 0.67277 | 0.65385 | 0.65629 | 0.63675 | 0.018926 | 0.019536 | 3228.9417 | 344165.0692 | 5.5987

## C1-7
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38957.5524 | 1 | 0 | 38957.5524 | 1 | 0 | -145.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5545 | 1 | 0 | 38957.5545 | 1 | 0 | 39 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5566 | 1 | 0 | 38957.5567 | 1 | 0 | 223.5 | 383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5588 | 1 | 0 | 38957.5588 | 1 | 0 | 408.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5609 | 983 | 933 | 38957.5609 | 1089 | 1033 | 593.5 | 753.5 | 60.0122 | 56.9597 | 66.4835 | 63.0647 | 0.60012 | 0.5696 | 0.66484 | 0.63065 | 0.030525 | 0.034188 | 18469.3487 | 2126.1736 | 20.1683
38957.5631 | 1169 | 1181 | 38957.5631 | 1171 | 1137 | 778 | 938 | 71.3675 | 72.1001 | 71.4896 | 69.4139 | 0.71368 | 0.721 | 0.7149 | 0.69414 | 0.007326 | 0.020757 | 1571.9759 | 2457.6987 | 19.2815
38957.5652 | 1207 | 896 | 38957.5652 | 1248 | 1009 | 963 | 1123 | 73.6874 | 54.7009 | 76.1905 | 61.5995 | 0.73687 | 0.54701 | 0.7619 | 0.616 | 0.18987 | 0.14591 | 219.2869 | 877.0006 | 1.0038
38957.5673 | 1143 | 1186 | 38957.5673 | 1027 | 996 | 1147.5 | 1307.5 | 69.7802 | 72.4054 | 62.6984 | 60.8059 | 0.6978 | 0.72405 | 0.62698 | 0.60806 | 0.026252 | 0.018926 | 1286.5869 | 3661.0783 | 17.7266

## C1-6
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38957.5523 | 1 | 0 | 38957.5523 | 1 | 0 | -148.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5545 | 1 | 0 | 38957.5545 | 1 | 0 | 36.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5566 | 1 | 0 | 38957.5566 | 1 | 0 | 221 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5587 | 1 | 0 | 38957.5588 | 1 | 0 | 406 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5609 | 1149 | 1161 | 38957.5609 | 1142 | 1088 | 590.5 | 750.5 | 70.1465 | 70.8791 | 69.7192 | 66.4225 | 0.70147 | 0.70879 | 0.69719 | 0.66422 | 0.007326 | 0.032967 | 640.819 | 838.657 | 15.1589
38957.563 | 1013 | 980 | 38957.563 | 1001 | 968 | 775.5 | 935.5 | 61.8437 | 59.8291 | 61.1111 | 59.0965 | 0.61844 | 0.59829 | 0.61111 | 0.59096 | 0.020147 | 0.020147 | 6303.0909 | 6303.0909 | 12.0557
38957.5652 | 1566 | 925 | 38957.5652 | 1109 | 912 | 960 | 1120 | 95.6044 | 56.4713 | 67.7045 | 55.6777 | 0.95604 | 0.56471 | 0.67705 | 0.55678 | 0.39133 | 0.12027 | 63.8083 | 427.6746 | 33.1188
38957.5673 | 958 | 926 | 38957.5673 | 947 | 919 | 1145 | 1305 | 58.486 | 56.5324 | 57.8144 | 56.105 | 0.58486 | 0.56532 | 0.57814 | 0.56105 | 0.019536 | 0.017094 | 4354.8362 | 16906.1305 | 24.5868

## C1-5
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38957.5523 | 1 | 0 | 38957.5523 | 1 | 0 | -151.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5544 | 1 | 0 | 38957.5545 | 1 | 0 | 33.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5566 | 1 | 0 | 38957.5566 | 1 | 0 | 218 | 378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5587 | 1 | 0 | 38957.5587 | 1 | 0 | 403 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5609 | 1078 | 1137 | 38957.5609 | 1216 | 1169 | 587.5 | 747.5 | 65.812 | 69.4139 | 74.2369 | 71.3675 | 0.65812 | 0.69414 | 0.74237 | 0.71368 | 0.03602 | 0.028694 | 77836.7895 | 1971.5531 | 8.5362
38957.563 | 1177 | 1146 | 38957.563 | 934 | 964 | 772.5 | 932.5 | 71.8559 | 69.9634 | 57.0208 | 58.8523 | 0.71856 | 0.69963 | 0.57021 | 0.58852 | 0.018926 | 0.018315 | 53.3596 | 66.5051 | 7.3185
38957.5651 | 1248 | 848 | 38957.5652 | 1101 | 785 | 957.5 | 1117.5 | 76.1905 | 51.7705 | 67.2161 | 47.9243 | 0.7619 | 0.5177 | 0.67216 | 0.47924 | 0.2442 | 0.19292 | 153.2721 | 515.9128 | 1.6812
38957.5673 | 1119 | 1085 | 38957.5673 | 1014 | 982 | 1142 | 1302 | 68.315 | 66.2393 | 61.9048 | 59.9512 | 0.68315 | 0.66239 | 0.61905 | 0.59951 | 0.020757 | 0.019536 | 1019.3095 | 1708.1514 | 7.9215

## C1-4
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38957.5523 | 1 | 0 | 38957.5523 | 1 | 0 | -154 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5544 | 1 | 0 | 38957.5544 | 1 | 0 | 30.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5566 | 1 | 0 | 38957.5566 | 1 | 0 | 215.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5587 | 1 | 0 | 38957.5587 | 1 | 0 | 400.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5608 | 1129 | 1078 | 38957.5608 | 1213 | 1165 | 585 | 745 | 68.9255 | 65.812 | 74.0537 | 71.1233 | 0.68926 | 0.65812 | 0.74054 | 0.71123 | 0.031136 | 0.029304 | 6336.3612 | 3039.1652 | 8.4403
38957.563 | 1125 | 1169 | 38957.563 | 996 | 1031 | 769.5 | 929.5 | 68.6813 | 71.3675 | 60.8059 | 62.9426 | 0.68681 | 0.71368 | 0.60806 | 0.62943 | 0.026862 | 0.021368 | 1233.9371 | 3240.8726 | 15.0182
38957.5651 | 1327 | 925 | 38957.5651 | 1376 | 901 | 954.5 | 1114.5 | 81.0134 | 56.4713 | 84.0049 | 55.0061 | 0.81013 | 0.56471 | 0.84005 | 0.55006 | 0.24542 | 0.28999 | 177.5856 | 2277.5043 | 14.3929
38957.5672 | 1107 | 1073 | 38957.5673 | 1085 | 1051 | 1139.5 | 1299.5 | 67.5824 | 65.5067 | 66.2393 | 64.1636 | 0.67582 | 0.65507 | 0.66239 | 0.64164 | 0.020757 | 0.020757 | 6114.7647 | 6114.7647 | 6.1419

## C1-3
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38957.5522 | 1 | 0 | 38957.5523 | 1 | 0 | -157 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5544 | 1 | 0 | 38957.5544 | 1 | 0 | 27.5 | 187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5565 | 1 | 0 | 38957.5565 | 1 | 0 | 212.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5587 | 1 | 0 | 38957.5587 | 1 | 0 | 397.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5608 | 1121 | 1071 | 38957.5608 | 1160 | 1181 | 582 | 742 | 68.4371 | 65.3846 | 70.8181 | 72.1001 | 0.68437 | 0.65385 | 0.70818 | 0.721 | 0.030525 | 0.012821 | 1269.6188 | 3806.6111 | 7.1856
38957.5629 | 1153 | 924 | 38957.563 | 1120 | 1167 | 767 | 927 | 70.3907 | 56.4103 | 68.3761 | 71.2454 | 0.70391 | 0.5641 | 0.68376 | 0.71245 | 0.1398 | 0.028694 | 67.9385 | 78.0358 | 1.7087
38957.5651 | 1114 | 787 | 38957.5651 | 1189 | 757 | 951.5 | 1111.5 | 68.0098 | 48.0464 | 72.5885 | 46.2149 | 0.6801 | 0.48046 | 0.72589 | 0.46215 | 0.19963 | 0.26374 | 865.3453 | 372.0118 | 21.2327
38957.5672 | 1105 | 1072 | 38957.5672 | 1190 | 919 | 1136.5 | 1296.5 | 67.4603 | 65.4457 | 72.6496 | 56.105 | 0.6746 | 0.65446 | 0.7265 | 0.56105 | 0.020147 | 0.16545 | 21.0517 | 22.5432 | 1.0979

## C1-2
Penlight Test 62 |  |  | 2006-08-28 | 13:17 |  | Vs = |  | 129 |  | R = | 100
XLPE | 12-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38957.5522 | 1 | 0 | 38957.5522 | 1 | 0 | -159.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5543 | 1 | 0 | 38957.5544 | 1 | 0 | 25 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5565 | 1 | 0 | 38957.5565 | 1 | 0 | 210 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5586 | 1 | 0 | 38957.5586 | 1 | 0 | 394.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38957.5608 | 944 | 919 | 38957.5608 | 1210 | 1166 | 579.5 | 739.5 | 57.6313 | 56.105 | 73.8706 | 71.1844 | 0.57631 | 0.56105 | 0.73871 | 0.71184 | 0.015263 | 0.026862 | 89.0544 | 71.3674 | 11.33
38957.5629 | 1118 | 1085 | 38957.5629 | 1109 | 1155 | 764 | 924 | 68.254 | 66.2393 | 67.7045 | 70.5128 | 0.68254 | 0.66239 | 0.67705 | 0.70513 | 0.020147 | 0.028083 | 1514.8708 | 3319.7189 | 8.0506
38957.565 | 1370 | 888 | 38957.5651 | 1476 | 936 | 949 | 1109 | 83.6386 | 54.2125 | 90.1099 | 57.1429 | 0.83639 | 0.54212 | 0.9011 | 0.57143 | 0.29426 | 0.32967 | 207.4774 | 716.8285 | 14.3278
38957.5672 | 1131 | 1099 | 38957.5672 | 990 | 959 | 1133.5 | 1293.5 | 69.0476 | 67.094 | 60.4396 | 58.547 | 0.69048 | 0.67094 | 0.6044 | 0.58547 | 0.019536 | 0.018926 | 2617.5869 | 19923.0175 | 10.5911

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Tray Rung
0 | -160 | 18.2 | 28.1 | 19.4 | 27.4
1 | -159 | 18.2 | 28.1 | 19.4 | 27.5
2 | -158 | 18.2 | 28.2 | 19.3 | 27.5
3 | -157 | 18.2 | 28.1 | 19.3 | 27.5
4 | -156 | 18.2 | 28.1 | 19.4 | 27.5
5 | -155 | 18.2 | 28.1 | 19.4 | 27.5
6 | -154 | 18.2 | 28.1 | 19.4 | 27.5
7 | -153 | 18.2 | 28.2 | 19.3 | 27.5
8 | -152 | 18.2 | 28.2 | 19.4 | 27.5
9 | -151 | 18.2 | 28.1 | 19.4 | 27.4
10 | -150 | 18.2 | 28.1 | 19.4 | 27.4
11 | -149 | 18.2 | 28.1 | 19.5 | 27.4
12 | -148 | 18.2 | 28.1 | 19.4 | 27.4
13 | -147 | 18.2 | 28.1 | 19.4 | 27.4
14 | -146 | 18.2 | 28.1 | 19.4 | 27.4
15 | -145 | 18.2 | 28.1 | 19.4 | 27.4
16 | -144 | 18.2 | 28.1 | 19.4 | 27.4
17 | -143 | 18.2 | 28.1 | 19.4 | 27.4
18 | -142 | 18.3 | 28 | 19.6 | 27.4
19 | -141 | 18.3 | 28 | 19.6 | 27.4
20 | -140 | 18.3 | 28 | 19.6 | 27.4
21 | -139 | 18.3 | 28 | 19.6 | 27.4
22 | -138 | 18.3 | 28 | 19.6 | 27.4
23 | -137 | 18.3 | 28 | 19.6 | 27.4
24 | -136 | 18.3 | 28 | 19.6 | 27.4
25 | -135 | 18.3 | 28 | 19.6 | 27.4
26 | -134 | 18.3 | 28 | 19.6 | 27.4
27 | -133 | 18.3 | 28 | 19.6 | 27.4
28 | -132 | 18.3 | 28 | 19.6 | 27.4
29 | -131 | 18.3 | 28 | 19.5 | 27.4
30 | -130 | 18.3 | 28 | 19.5 | 27.4
31 | -129 | 18.3 | 28 | 19.5 | 27.4
32 | -128 | 18.3 | 28 | 19.5 | 27.4
33 | -127 | 18.3 | 28 | 19.5 | 27.4
34 | -126 | 18.3 | 28.1 | 19.5 | 27.4
35 | -125 | 18.3 | 28 | 19.5 | 27.4
36 | -124 | 18.3 | 28 | 19.5 | 27.4
37 | -123 | 18.3 | 28 | 19.5 | 27.4
38 | -122 | 18.3 | 28 | 19.5 | 27.4
39 | -121 | 18.3 | 28 | 19.5 | 27.4
40 | -120 | 18.3 | 28 | 19.5 | 27.4
41 | -119 | 18.3 | 28 | 19.5 | 27.4
42 | -118 | 18.3 | 28 | 19.6 | 27.4
43 | -117 | 18.3 | 28 | 19.6 | 27.4
44 | -116 | 18.3 | 28 | 19.5 | 27.4
45 | -115 | 18.3 | 28 | 19.5 | 27.4
46 | -114 | 18.3 | 28 | 19.5 | 27.4
47 | -113 | 18.3 | 28 | 19.5 | 27.4
48 | -112 | 18.3 | 28 | 19.5 | 27.4
49 | -111 | 18.3 | 28 | 19.5 | 27.4
50 | -110 | 18.3 | 28 | 19.5 | 27.4
51 | -109 | 18.3 | 28 | 19.6 | 27.4
52 | -108 | 18.3 | 28 | 19.6 | 27.4
53 | -107 | 18.3 | 28 | 19.6 | 27.4
54 | -106 | 18.3 | 28 | 19.6 | 27.4
55 | -105 | 18.3 | 28 | 19.6 | 27.4
56 | -104 | 18.3 | 28 | 19.6 | 27.4
57 | -103 | 18.3 | 28 | 19.5 | 27.4
58 | -102 | 18.3 | 28.1 | 19.4 | 27.4
59 | -101 | 18.3 | 28.1 | 19.4 | 27.4
60 | -100 | 18.3 | 28.1 | 19.4 | 27.4
61 | -99 | 18.3 | 28.1 | 19.4 | 27.4
62 | -98 | 18.3 | 28.1 | 19.5 | 27.4
63 | -97 | 18.3 | 28 | 19.5 | 27.4
64 | -96 | 18.3 | 28 | 19.5 | 27.4
65 | -95 | 18.3 | 28 | 19.5 | 27.4
66 | -94 | 18.3 | 28 | 19.5 | 27.4
67 | -93 | 18.3 | 28.1 | 19.5 | 27.4
68 | -92 | 18.3 | 28.1 | 19.4 | 27.4
69 | -91 | 18.3 | 28.1 | 19.4 | 27.4
70 | -90 | 18.3 | 28 | 19.5 | 27.4
71 | -89 | 18.3 | 28 | 19.5 | 27.4
72 | -88 | 18.3 | 28 | 19.5 | 27.4
73 | -87 | 18.3 | 28 | 19.5 | 27.4
74 | -86 | 18.3 | 28 | 19.5 | 27.4
75 | -85 | 18.3 | 28 | 19.5 | 27.4
76 | -84 | 18.3 | 28 | 19.5 | 27.4
77 | -83 | 18.3 | 28.1 | 19.5 | 27.4
78 | -82 | 18.3 | 28 | 19.5 | 27.4
79 | -81 | 18.3 | 28 | 19.5 | 27.4
80 | -80 | 18.3 | 28.1 | 19.4 | 27.4
81 | -79 | 18.3 | 28.1 | 19.4 | 27.4
82 | -78 | 18.3 | 28.1 | 19.4 | 27.4
83 | -77 | 18.3 | 28.1 | 19.4 | 27.4
84 | -76 | 18.3 | 28.1 | 19.4 | 27.4
85 | -75 | 18.3 | 28.1 | 19.4 | 27.4
86 | -74 | 18.3 | 28 | 19.5 | 27.4
87 | -73 | 18.3 | 28 | 19.5 | 27.4
88 | -72 | 18.3 | 28 | 19.5 | 27.4
89 | -71 | 18.3 | 28 | 19.5 | 27.4
90 | -70 | 18.3 | 28 | 19.5 | 27.4
91 | -69 | 18.3 | 28 | 19.5 | 27.4
92 | -68 | 18.3 | 28 | 19.5 | 27.4
93 | -67 | 18.3 | 28 | 19.5 | 27.4
94 | -66 | 18.3 | 28 | 19.5 | 27.4
95 | -65 | 18.3 | 28 | 19.5 | 27.4
96 | -64 | 18.3 | 28 | 19.5 | 27.4
97 | -63 | 18.3 | 28 | 19.5 | 27.4
98 | -62 | 18.3 | 28 | 19.5 | 27.4
99 | -61 | 18.3 | 28.1 | 19.4 | 27.4
100 | -60 | 18.3 | 28.1 | 19.5 | 27.4
101 | -59 | 18.3 | 28 | 19.5 | 27.4
102 | -58 | 18.3 | 28 | 19.5 | 27.4
103 | -57 | 18.3 | 28 | 19.5 | 27.4
104 | -56 | 18.3 | 28 | 19.5 | 27.4
105 | -55 | 18.3 | 28 | 19.5 | 27.4
106 | -54 | 18.3 | 28 | 19.5 | 27.4
107 | -53 | 18.3 | 28 | 19.5 | 27.4
108 | -52 | 18.3 | 28 | 19.5 | 27.4
109 | -51 | 18.3 | 28 | 19.5 | 27.4
110 | -50 | 18.3 | 28 | 19.5 | 27.4
111 | -49 | 18.3 | 28 | 19.5 | 27.4
112 | -48 | 18.3 | 28 | 19.5 | 27.4
113 | -47 | 18.3 | 28 | 19.5 | 27.4
114 | -46 | 18.3 | 28 | 19.5 | 27.4
115 | -45 | 18.3 | 28 | 19.5 | 27.4
116 | -44 | 18.3 | 28 | 19.5 | 27.4
117 | -43 | 18.3 | 28.1 | 19.4 | 27.4
118 | -42 | 18.3 | 28 | 19.5 | 27.4
119 | -41 | 18.3 | 28 | 19.5 | 27.4
120 | -40 | 18.3 | 28.1 | 19.4 | 27.4
121 | -39 | 18.3 | 28.1 | 19.4 | 27.4
122 | -38 | 18.3 | 28.1 | 19.4 | 27.4
123 | -37 | 18.3 | 28.1 | 19.4 | 27.4
124 | -36 | 18.3 | 28.1 | 19.4 | 27.4
125 | -35 | 18.3 | 28.1 | 19.4 | 27.4
126 | -34 | 18.3 | 28.1 | 19.4 | 27.4
127 | -33 | 18.3 | 28.1 | 19.4 | 27.4
128 | -32 | 18.3 | 28.1 | 19.4 | 27.4
129 | -31 | 18.3 | 28.1 | 19.4 | 27.4
130 | -30 | 18.3 | 28.1 | 19.4 | 27.4
131 | -29 | 18.3 | 28.1 | 19.4 | 27.4
132 | -28 | 18.3 | 28.1 | 19.4 | 27.4
133 | -27 | 18.3 | 28 | 19.5 | 27.4
134 | -26 | 18.3 | 28 | 19.5 | 27.3
135 | -25 | 18.3 | 28 | 19.6 | 27.3
136 | -24 | 18.3 | 28 | 19.5 | 27.4
137 | -23 | 18.3 | 28 | 19.5 | 27.4
138 | -22 | 18.3 | 28 | 19.5 | 27.4
139 | -21 | 18.3 | 28 | 19.5 | 27.4
140 | -20 | 18.3 | 28 | 19.6 | 27.4
141 | -19 | 18.3 | 28 | 19.5 | 27.4
142 | -18 | 18.3 | 28 | 19.5 | 27.4
143 | -17 | 18.3 | 28 | 19.5 | 27.4
144 | -16 | 18.3 | 28 | 19.5 | 27.4
145 | -15 | 18.3 | 28 | 19.5 | 27.4
146 | -14 | 18.3 | 28 | 19.5 | 27.4
147 | -13 | 18.3 | 28 | 19.5 | 27.4
148 | -12 | 18.3 | 28 | 19.5 | 27.4
149 | -11 | 18.3 | 28 | 19.5 | 27.4
150 | -10 | 18.3 | 28 | 19.5 | 27.4
151 | -9 | 18.3 | 28 | 19.5 | 27.4
152 | -8 | 18.3 | 28 | 19.5 | 27.4
153 | -7 | 18.3 | 28 | 19.5 | 27.4
154 | -6 | 18.3 | 28 | 19.5 | 27.4
155 | -5 | 18.3 | 28 | 19.5 | 27.4
156 | -4 | 17.9 | 29.3 | 16.8 | 28.3
157 | -3 | 17.7 | 30 | 15.2 | 28.8
158 | -2 | 17.9 | 30.3 | 14.7 | 29
159 | -1 | 18.7 | 30.3 | 14.7 | 29
160 | 0 | 20.1 | 30.3 | 14.7 | 29
161 | 1 | 22 | 30.2 | 14.9 | 29
162 | 2 | 24.4 | 30.3 | 14.6 | 29.1
163 | 3 | 27.2 | 30.3 | 14.7 | 29.1
164 | 4 | 30.3 | 30.3 | 14.6 | 29.1
165 | 5 | 33.8 | 30.3 | 14.7 | 29.1
166 | 6 | 37.5 | 30.3 | 14.8 | 29.1
167 | 7 | 41.4 | 30.4 | 14.7 | 29.2
168 | 8 | 45.4 | 30.4 | 14.8 | 29.3
169 | 9 | 49.7 | 30.4 | 14.8 | 29.3
170 | 10 | 54.1 | 30.4 | 14.9 | 29.4
171 | 11 | 58.7 | 30.4 | 15.3 | 29.3
172 | 12 | 63.4 | 30.3 | 15.5 | 29.4
173 | 13 | 68.3 | 30.4 | 15.5 | 29.5
174 | 14 | 73.3 | 30.5 | 15.7 | 29.6
175 | 15 | 78.4 | 30.5 | 15.9 | 29.6
176 | 16 | 83.6 | 30.6 | 15.9 | 29.8
177 | 17 | 88.8 | 30.7 | 16 | 30
178 | 18 | 94.2 | 30.8 | 16.2 | 30.1
179 | 19 | 99.6 | 30.9 | 16.3 | 30.3
180 | 20 | 105.1 | 31 | 16.6 | 30.4
181 | 21 | 110.7 | 31.2 | 16.8 | 30.6
182 | 22 | 116.4 | 31.3 | 17 | 30.8
183 | 23 | 122.1 | 31.4 | 17.3 | 31
184 | 24 | 127.9 | 31.7 | 17.5 | 31.3
185 | 25 | 133.8 | 31.9 | 17.7 | 31.6
186 | 26 | 139.7 | 32 | 18 | 31.9
187 | 27 | 145.6 | 32.2 | 18.4 | 32.1
188 | 28 | 151.6 | 32.5 | 18.7 | 32.5
189 | 29 | 157.6 | 32.8 | 18.9 | 32.9
190 | 30 | 163.5 | 32.9 | 19.4 | 33.2
191 | 31 | 169.4 | 33.2 | 19.8 | 33.5
192 | 32 | 175.3 | 33.6 | 20.1 | 34
193 | 33 | 181.2 | 33.8 | 20.6 | 34.3
194 | 34 | 187.2 | 34.1 | 21.1 | 34.7
195 | 35 | 193.2 | 34.5 | 21.5 | 35.2
196 | 36 | 199.2 | 34.8 | 22.1 | 35.7
197 | 37 | 205.2 | 35.3 | 22.5 | 36.2
198 | 38 | 211.2 | 35.6 | 23.2 | 36.7
199 | 39 | 217 | 36.1 | 23.7 | 37.3
200 | 40 | 222.8 | 36.6 | 24.2 | 37.9
201 | 41 | 228.7 | 37.1 | 24.7 | 38.6
202 | 42 | 234.7 | 37.6 | 25.3 | 39.2
203 | 43 | 240.6 | 38.1 | 26 | 39.9
204 | 44 | 246.5 | 38.6 | 26.8 | 40.6
205 | 45 | 252.4 | 39.1 | 27.4 | 41.3
206 | 46 | 258.1 | 39.7 | 28.2 | 42
207 | 47 | 263.8 | 40.3 | 29 | 42.8
208 | 48 | 269.5 | 40.9 | 29.8 | 43.5
209 | 49 | 275.2 | 41.5 | 30.5 | 44.5
210 | 50 | 280.8 | 42.1 | 31.4 | 45.3
211 | 51 | 286.3 | 42.7 | 32.4 | 46.2
212 | 52 | 291.9 | 43.4 | 33.4 | 47.1
213 | 53 | 297.5 | 44 | 34.4 | 48
214 | 54 | 302.9 | 44.9 | 35.2 | 49.1
215 | 55 | 308.4 | 45.6 | 36.3 | 50
216 | 56 | 313.9 | 46.4 | 37.3 | 51.1
217 | 57 | 319.3 | 47.2 | 38.4 | 52.1
218 | 58 | 324.8 | 48.1 | 39.4 | 53.2
219 | 59 | 330.1 | 49 | 40.4 | 54.3
220 | 60 | 335.4 | 49.9 | 41.7 | 55.5
221 | 61 | 340.7 | 50.9 | 42.9 | 56.7
222 | 62 | 346 | 51.9 | 44.1 | 58
223 | 63 | 351.3 | 52.8 | 45.4 | 59.2
224 | 64 | 356.6 | 53.9 | 46.6 | 60.6
225 | 65 | 361.9 | 55 | 47.9 | 61.9
226 | 66 | 367 | 56 | 49.3 | 63.3
227 | 67 | 372.1 | 57.1 | 50.7 | 64.8
228 | 68 | 377.1 | 58.3 | 52 | 66.3
229 | 69 | 382.1 | 59.6 | 53.4 | 67.9
230 | 70 | 387.1 | 60.8 | 54.9 | 69.5
231 | 71 | 392.1 | 62 | 56.4 | 71.1
232 | 72 | 397.1 | 63.3 | 58.1 | 72.8
233 | 73 | 402 | 64.6 | 59.8 | 74.4
234 | 74 | 406.7 | 65.8 | 61.5 | 76.2
235 | 75 | 411.5 | 67.2 | 63.2 | 78
236 | 76 | 416.4 | 68.6 | 64.8 | 79.8
237 | 77 | 421.4 | 70 | 66.4 | 81.7
238 | 78 | 426.2 | 71.1 | 68.9 | 83.3
239 | 79 | 431 | 72.4 | 70.8 | 85.2
240 | 80 | 435.4 | 73.9 | 72.6 | 87.3
241 | 81 | 439.4 | 75.4 | 74.5 | 89.3
242 | 82 | 443.1 | 77 | 76.4 | 91.3
243 | 83 | 446.6 | 78.5 | 78.4 | 93.3
244 | 84 | 449.9 | 80.1 | 80.3 | 95.4
245 | 85 | 453 | 81.7 | 82.2 | 97.5
246 | 86 | 456 | 83.3 | 84.1 | 99.6
247 | 87 | 458.7 | 84.9 | 86 | 101.7
248 | 88 | 461.4 | 86.4 | 88 | 103.9
249 | 89 | 463.9 | 87.9 | 90.1 | 106
250 | 90 | 466.1 | 89.5 | 92.2 | 108.1
251 | 91 | 468.2 | 90.7 | 94.9 | 110
252 | 92 | 470 | 92.1 | 97.3 | 112.1
253 | 93 | 471.4 | 93.4 | 99.7 | 114.2
254 | 94 | 472.6 | 94.8 | 102 | 116.2
255 | 95 | 473.4 | 96.6 | 103.5 | 118.6
256 | 96 | 473.7 | 100.1 | 101.4 | 122.3
257 | 97 | 474.1 | 101.8 | 102.8 | 124.6
258 | 98 | 474.3 | 103.5 | 104.4 | 126.8
259 | 99 | 474.4 | 104.8 | 106.8 | 128.7
260 | 100 | 474.5 | 106.3 | 108.7 | 130.9
261 | 101 | 474.5 | 107.9 | 110.3 | 133.1
262 | 102 | 474.3 | 109.4 | 111.9 | 135.3
263 | 103 | 473.9 | 110.9 | 113.7 | 137.5
264 | 104 | 473.5 | 112.2 | 115.8 | 139.5
265 | 105 | 473 | 113.4 | 118 | 141.4
266 | 106 | 472.5 | 114.7 | 119.9 | 143.4
267 | 107 | 472 | 116 | 121.7 | 145.4
268 | 108 | 471.5 | 117.3 | 123.6 | 147.5
269 | 109 | 470.9 | 118.5 | 125.5 | 149.5
270 | 110 | 470.4 | 120 | 127 | 151.6
271 | 111 | 469.8 | 121.3 | 128.7 | 153.5
272 | 112 | 469.3 | 122.6 | 130.2 | 155.6
273 | 113 | 468.8 | 124.1 | 131.6 | 157.7
274 | 114 | 468.2 | 125.6 | 132.7 | 159.9
275 | 115 | 467.7 | 127 | 133.9 | 162
276 | 116 | 467.2 | 128.3 | 135.3 | 164
277 | 117 | 466.7 | 129.6 | 136.5 | 166
278 | 118 | 466.4 | 130.8 | 138 | 168
279 | 119 | 466.1 | 132 | 139.2 | 170
280 | 120 | 465.8 | 133.1 | 140.6 | 171.9
281 | 121 | 465.4 | 134.3 | 141.9 | 173.9
282 | 122 | 465.1 | 135.3 | 143.2 | 175.9
283 | 123 | 465 | 136.5 | 144.4 | 177.8
284 | 124 | 464.9 | 137.4 | 145.9 | 179.7
285 | 125 | 464.9 | 138.4 | 147.3 | 181.6
286 | 126 | 465 | 139.5 | 148.5 | 183.5
287 | 127 | 464.9 | 140.5 | 149.9 | 185.4
288 | 128 | 465 | 141.5 | 151.3 | 187.3
289 | 129 | 465.1 | 142.5 | 152.7 | 189.1
290 | 130 | 465.2 | 143.6 | 154.1 | 191
291 | 131 | 465.4 | 144.7 | 155.4 | 192.9
292 | 132 | 465.6 | 145.9 | 156.7 | 194.8
293 | 133 | 465.9 | 147 | 158.1 | 196.7
294 | 134 | 466.2 | 148.1 | 159.7 | 198.4
295 | 135 | 466.5 | 149.1 | 161.4 | 200.2
296 | 136 | 466.9 | 150.2 | 162.9 | 202
297 | 137 | 467.1 | 151.5 | 164.1 | 203.9
298 | 138 | 467.4 | 152.8 | 165.3 | 205.7
299 | 139 | 467.6 | 153.9 | 166.9 | 207.5
300 | 140 | 467.9 | 155.1 | 168.4 | 209.2
301 | 141 | 468 | 156.2 | 169.8 | 211
302 | 142 | 468.2 | 157.6 | 171 | 212.9
303 | 143 | 468.3 | 158.8 | 172.3 | 214.6
304 | 144 | 468.4 | 160.1 | 173.6 | 216.4
305 | 145 | 468.4 | 161.4 | 174.8 | 218.2
306 | 146 | 468.4 | 162.7 | 175.9 | 220
307 | 147 | 468.5 | 164 | 177.1 | 221.8
308 | 148 | 468.7 | 165.3 | 178.4 | 223.5
309 | 149 | 468.7 | 166.6 | 179.7 | 225.3
310 | 150 | 468.8 | 167.9 | 181 | 227
311 | 151 | 468.8 | 169.3 | 182 | 228.8
312 | 152 | 468.8 | 170.6 | 183.4 | 230.5
313 | 153 | 468.9 | 172 | 184.4 | 232.2
314 | 154 | 468.9 | 173.3 | 185.7 | 233.9
315 | 155 | 468.9 | 174.6 | 187 | 235.6
316 | 156 | 469 | 176 | 188.1 | 237.3
317 | 157 | 469 | 177.4 | 189.4 | 239
318 | 158 | 469 | 178.7 | 190.6 | 240.7
319 | 159 | 468.9 | 180.2 | 191.7 | 242.3
320 | 160 | 468.8 | 181.6 | 192.8 | 244
321 | 161 | 468.9 | 182.9 | 194.1 | 245.7
322 | 162 | 469 | 184.2 | 195.4 | 247.3
323 | 163 | 468.9 | 185.5 | 196.7 | 248.8
324 | 164 | 468.8 | 186.8 | 198 | 250.4
325 | 165 | 468.8 | 188.2 | 199.2 | 252
326 | 166 | 468.7 | 189.6 | 200.3 | 253.7
327 | 167 | 468.7 | 190.9 | 201.5 | 255.2
328 | 168 | 468.7 | 192.2 | 202.7 | 256.8
329 | 169 | 468.7 | 193.6 | 203.9 | 258.4
330 | 170 | 468.7 | 194.9 | 205 | 260
331 | 171 | 468.6 | 196.3 | 206 | 261.6
332 | 172 | 468.5 | 197.5 | 207.4 | 263
333 | 173 | 468.5 | 198.7 | 208.7 | 264.5
334 | 174 | 468.5 | 200 | 209.8 | 266
335 | 175 | 468.5 | 201.4 | 210.7 | 267.6
336 | 176 | 468.4 | 202.8 | 211.8 | 269.2
337 | 177 | 468.4 | 204 | 213 | 270.6
338 | 178 | 468.4 | 205.2 | 214.1 | 272.1
339 | 179 | 468.3 | 206.5 | 215.1 | 273.6
340 | 180 | 468.3 | 207.8 | 216.2 | 275
341 | 181 | 468.2 | 209.1 | 217.2 | 276.5
342 | 182 | 468.1 | 210.4 | 218.2 | 278
343 | 183 | 468.3 | 211.5 | 219.4 | 279.4
344 | 184 | 468.3 | 212.7 | 220.7 | 280.8
345 | 185 | 468.3 | 213.9 | 221.8 | 282.2
346 | 186 | 468.3 | 215.2 | 222.8 | 283.6
347 | 187 | 468.3 | 216.4 | 223.9 | 285
348 | 188 | 468.3 | 217.5 | 225.3 | 286.3
349 | 189 | 468.4 | 218.7 | 226.5 | 287.6
350 | 190 | 468.5 | 220 | 227.5 | 289
351 | 191 | 468.5 | 221.1 | 228.8 | 290.3
352 | 192 | 468.5 | 222.4 | 229.8 | 291.7
353 | 193 | 468.5 | 223.6 | 231 | 293
354 | 194 | 468.4 | 225 | 231.9 | 294.4
355 | 195 | 468.3 | 226.2 | 232.9 | 295.7
356 | 196 | 468.2 | 227.6 | 233.7 | 297
357 | 197 | 468.1 | 228.9 | 234.6 | 298.3
358 | 198 | 468.1 | 230.4 | 235.4 | 299.7
359 | 199 | 468 | 231.9 | 236.4 | 300.9
360 | 200 | 467.9 | 233.3 | 237.3 | 302.2
361 | 201 | 467.7 | 234.7 | 238 | 303.4
362 | 202 | 467.6 | 236.3 | 238.1 | 304.8
363 | 203 | 467.5 | 237.8 | 238.3 | 306.1
364 | 204 | 467.4 | 239.2 | 238.5 | 307.4
365 | 205 | 467.3 | 240.7 | 238.1 | 308.7
366 | 206 | 467.2 | 242.2 | 237.7 | 310
367 | 207 | 467.2 | 243.7 | 238.1 | 311.2
368 | 208 | 467.3 | 245.1 | 238.8 | 312.4
369 | 209 | 467.2 | 246.5 | 239.3 | 313.6
370 | 210 | 467.2 | 248 | 240 | 314.7
371 | 211 | 467.1 | 249.5 | 240.4 | 315.9
372 | 212 | 467.1 | 251.2 | 240.7 | 317.1
373 | 213 | 467.1 | 253 | 241.2 | 318.2
374 | 214 | 466.9 | 254.8 | 241.8 | 319.4
375 | 215 | 466.8 | 256.7 | 242.6 | 320.6
376 | 216 | 466.7 | 258.3 | 243.8 | 321.7
377 | 217 | 466.7 | 259.9 | 244.8 | 322.8
378 | 218 | 466.7 | 261.5 | 245.3 | 324
379 | 219 | 466.5 | 263 | 245.8 | 325.2
380 | 220 | 466.4 | 264.5 | 246.4 | 326.4
381 | 221 | 466.3 | 265.9 | 246.9 | 327.6
382 | 222 | 466.3 | 267.2 | 247.7 | 328.6
383 | 223 | 466.3 | 268.5 | 248.2 | 329.8
384 | 224 | 466.2 | 269.6 | 249.2 | 330.8
385 | 225 | 466.1 | 270.6 | 250.1 | 331.9
386 | 226 | 466.2 | 271.6 | 250.9 | 332.9
387 | 227 | 466 | 272.5 | 251.3 | 334
388 | 228 | 465.8 | 272.8 | 251.8 | 335.1
389 | 229 | 465.7 | 273 | 252.2 | 336.1
390 | 230 | 465.8 | 273.7 | 252.6 | 337.2
391 | 231 | 465.8 | 274.6 | 252.9 | 338.3
392 | 232 | 465.8 | 275.6 | 253.1 | 339.3
393 | 233 | 465.8 | 276.2 | 253 | 340.3
394 | 234 | 465.7 | 276.5 | 252.9 | 341.4
395 | 235 | 465.7 | 276.3 | 252.8 | 342.5
396 | 236 | 465.8 | 276 | 252.9 | 343.4
397 | 237 | 465.7 | 275.8 | 253 | 344.4
398 | 238 | 465.7 | 275.7 | 253 | 345.5
399 | 239 | 465.8 | 275.8 | 253 | 346.5
400 | 240 | 465.9 | 276.1 | 253.3 | 347.5
401 | 241 | 465.9 | 276.2 | 253.8 | 348.3
402 | 242 | 466 | 276.4 | 254.3 | 349.3
403 | 243 | 466.1 | 276.6 | 254.7 | 350.2
404 | 244 | 466.2 | 277 | 255.1 | 351.1
405 | 245 | 466.2 | 277.6 | 255 | 352.1
406 | 246 | 466.3 | 278.3 | 255.1 | 352.9
407 | 247 | 466.4 | 279.1 | 255.1 | 353.8
408 | 248 | 466.5 | 279.8 | 255 | 354.7
409 | 249 | 466.7 | 280.4 | 255.2 | 355.8
410 | 250 | 466.9 | 280.4 | 255.5 | 357.3
411 | 251 | 467.2 | 280.1 | 255.9 | 359.9
412 | 252 | 467.5 | 279.9 | 256.2 | 363.2
413 | 253 | 467.9 | 279.6 | 256.9 | 366.7
414 | 254 | 468.3 | 279.5 | 257.7 | 370.4
415 | 255 | 468.6 | 279.8 | 258.1 | 374.5
416 | 256 | 468.8 | 280.9 | 258.8 | 378.4
417 | 257 | 468.9 | 285.6 | 259.3 | 382.2
418 | 258 | 469 | 289.7 | 260 | 385.8
419 | 259 | 468.9 | 292.2 | 260.4 | 389.4
420 | 260 | 469 | 294.2 | 260.7 | 392.8
421 | 261 | 469.1 | 295.7 | 262 | 395.9
422 | 262 | 469.1 | 296.8 | 263 | 398.8
423 | 263 | 469.2 | 297.8 | 264.2 | 401.4
424 | 264 | 469.2 | 298.7 | 265.5 | 403.9
425 | 265 | 469.3 | 299.7 | 266.5 | 406.4
426 | 266 | 469.2 | 300.7 | 267.5 | 408.6
427 | 267 | 469.1 | 301.7 | 268.8 | 410.7
428 | 268 | 468.9 | 302.5 | 270.2 | 412.7
429 | 269 | 468.7 | 303.3 | 271 | 414.7
430 | 270 | 468.6 | 304.1 | 271.9 | 416.8
431 | 271 | 468.3 | 305 | 272.8 | 418.8
432 | 272 | 468.1 | 306 | 273.6 | 420.7
433 | 273 | 467.9 | 307.1 | 274.3 | 422.7
434 | 274 | 467.5 | 308.2 | 275.5 | 424.6
435 | 275 | 467.3 | 309.2 | 276.5 | 426.5
436 | 276 | 467 | 310.2 | 277.2 | 428.3
437 | 277 | 466.5 | 311.5 | 277.9 | 430.2
438 | 278 | 466 | 312.6 | 278.5 | 432
439 | 279 | 465.6 | 313.7 | 279.5 | 433.7
440 | 280 | 465.2 | 314.9 | 280.6 | 435.4
441 | 281 | 464.8 | 316.3 | 281.3 | 437.2
442 | 282 | 464.4 | 317.6 | 281.9 | 439.1
443 | 283 | 463.8 | 318.8 | 282.7 | 440.8
444 | 284 | 463.4 | 320 | 284.1 | 442.1
445 | 285 | 463 | 321 | 285.8 | 443.4
446 | 286 | 462.6 | 322 | 287.3 | 444.9
447 | 287 | 462.1 | 322.9 | 288.7 | 446.5
448 | 288 | 461.7 | 323.8 | 290.1 | 447.9
449 | 289 | 461.3 | 324.8 | 291.6 | 449.4
450 | 290 | 460.9 | 326.1 | 292.7 | 451.1
451 | 291 | 460.6 | 327.4 | 293.7 | 452.7
452 | 292 | 460.3 | 328.9 | 295.1 | 454.2
453 | 293 | 460.1 | 330.4 | 296.7 | 455.6
454 | 294 | 460.2 | 331.3 | 299.4 | 456.6
455 | 295 | 460.2 | 332.2 | 302 | 457.6
456 | 296 | 460.1 | 333.3 | 303.7 | 458.9
457 | 297 | 460 | 334.6 | 305.3 | 460.2
458 | 298 | 459.7 | 335.8 | 307.1 | 461.5
459 | 299 | 459.3 | 337.2 | 308.8 | 462.8
460 | 300 | 458.9 | 338.3 | 310.6 | 464.1
461 | 301 | 458.5 | 339.5 | 312.4 | 465.1
462 | 302 | 458 | 340.8 | 314.1 | 466
463 | 303 | 457.5 | 342.2 | 315.9 | 467.1
464 | 304 | 457.1 | 343.5 | 317.5 | 468.2
465 | 305 | 456.6 | 344.8 | 319.3 | 469
466 | 306 | 456 | 346 | 321.3 | 469.8
467 | 307 | 455.5 | 347.4 | 323.1 | 470.8
468 | 308 | 455 | 348.8 | 324.8 | 471.9
469 | 309 | 454.4 | 350.2 | 326.5 | 472.8
470 | 310 | 453.8 | 351.5 | 328.5 | 473.7
471 | 311 | 453.2 | 352.9 | 330 | 474.5
472 | 312 | 452.6 | 354.4 | 331.9 | 475.2
473 | 313 | 452 | 355.9 | 333.6 | 475.9
474 | 314 | 451.4 | 357.4 | 335.6 | 476.6
475 | 315 | 450.8 | 358.9 | 337.4 | 477.3
476 | 316 | 450.2 | 360.3 | 339.2 | 477.9
477 | 317 | 449.6 | 361.8 | 341.1 | 478.4
478 | 318 | 448.9 | 363.4 | 342.6 | 478.9
479 | 319 | 448.3 | 364.8 | 344.2 | 479.4
480 | 320 | 447.6 | 366.2 | 345.8 | 479.7
481 | 321 | 446.8 | 367.7 | 347.4 | 479.9
482 | 322 | 446.1 | 369.1 | 349.1 | 480.4
483 | 323 | 445.5 | 370.5 | 350.8 | 480.8
484 | 324 | 444.9 | 371.8 | 352.8 | 481.2
485 | 325 | 444.3 | 373.1 | 354.3 | 481.3
486 | 326 | 443.6 | 374.3 | 355.9 | 481.3
487 | 327 | 442.9 | 375.6 | 357.6 | 481.3
488 | 328 | 442.3 | 377 | 358.9 | 481.3
489 | 329 | 441.6 | 378.3 | 359.8 | 481.3
490 | 330 | 440.9 | 379.6 | 361.1 | 481.1
491 | 331 | 440.2 | 380.9 | 362.3 | 481
492 | 332 | 439.6 | 382.2 | 363.4 | 480.9
493 | 333 | 438.9 | 383.5 | 364.6 | 480.8
494 | 334 | 438.3 | 384.7 | 365.6 | 480.7
495 | 335 | 437.6 | 385.9 | 366.5 | 480.5
496 | 336 | 437 | 387 | 367.6 | 480.3
497 | 337 | 436.3 | 388.1 | 368.4 | 480.2
498 | 338 | 435.7 | 389.1 | 369.3 | 479.9
499 | 339 | 435.1 | 390 | 370.4 | 479.6
500 | 340 | 434.5 | 390.8 | 371.7 | 479.3
501 | 341 | 433.8 | 391.6 | 372.7 | 479
502 | 342 | 433.2 | 392.4 | 373.8 | 478.8
503 | 343 | 432.5 | 393.1 | 374.9 | 478.5
504 | 344 | 431.9 | 393.8 | 375.9 | 478.4
505 | 345 | 431.2 | 394.5 | 376.8 | 478.1
506 | 346 | 430.5 | 395.1 | 378.1 | 477.8
507 | 347 | 429.8 | 396 | 379.3 | 477.5
508 | 348 | 429.2 | 396.7 | 380.4 | 477.2
509 | 349 | 428.5 | 397.6 | 381.6 | 477
510 | 350 | 428 | 398.4 | 382.7 | 477.4
511 | 351 | 427.4 | 399.2 | 383.6 | 477.3
512 | 352 | 426.8 | 400 | 384.6 | 477.2
513 | 353 | 426.2 | 400.9 | 385.7 | 477
514 | 354 | 425.5 | 401.8 | 386.7 | 476.8
515 | 355 | 424.9 | 402.7 | 387.7 | 476.5
516 | 356 | 424.2 | 403.7 | 388.8 | 476.2
517 | 357 | 423.5 | 404.8 | 389.7 | 475.9
518 | 358 | 422.9 | 405.9 | 390.8 | 475.7
519 | 359 | 422.2 | 407 | 391.9 | 475.4
520 | 360 | 421.6 | 408 | 393.1 | 475
521 | 361 | 420.9 | 408.9 | 394.4 | 474.7
522 | 362 | 420.2 | 409.8 | 395.7 | 474.3
523 | 363 | 419.6 | 410.6 | 397 | 474
524 | 364 | 418.9 | 411.4 | 398.1 | 473.7
525 | 365 | 418.3 | 412.2 | 399.1 | 473.4
526 | 366 | 417.7 | 413 | 400.1 | 473.1
527 | 367 | 417.2 | 413.2 | 402.3 | 472.4
528 | 368 | 416.6 | 414.5 | 402.4 | 472.5
529 | 369 | 416.1 | 415.3 | 403.4 | 472.4
530 | 370 | 415.4 | 416.2 | 404.4 | 472.3
531 | 371 | 414.8 | 417.2 | 405.5 | 472
532 | 372 | 414.1 | 418.2 | 406.5 | 471.8
533 | 373 | 413.6 | 419.2 | 407.4 | 471.6
534 | 374 | 413 | 420 | 408.4 | 471.3
535 | 375 | 412.4 | 420.9 | 409.3 | 471
536 | 376 | 411.8 | 421.9 | 409.9 | 470.9
537 | 377 | 411.2 | 422.8 | 410.8 | 470.7
538 | 378 | 410.6 | 423.8 | 411.7 | 470.6
539 | 379 | 410 | 424.7 | 412.5 | 470.4
540 | 380 | 409.4 | 425.8 | 413.1 | 470.3
541 | 381 | 409 | 426.6 | 414 | 470
542 | 382 | 408.4 | 427.7 | 414.5 | 469.9
543 | 383 | 407.8 | 428.7 | 415.2 | 469.7
544 | 384 | 407.2 | 429.7 | 416.1 | 469.4
545 | 385 | 406.6 | 430.6 | 416.9 | 469.1
546 | 386 | 406 | 431.4 | 417.6 | 468.8
547 | 387 | 405.4 | 432.2 | 418.2 | 468.6
548 | 388 | 404.8 | 432.8 | 418.8 | 468.3
549 | 389 | 404.3 | 433.4 | 419.5 | 468
550 | 390 | 403.7 | 434 | 420.2 | 467.7
551 | 391 | 403.2 | 434.7 | 420.9 | 467.5
552 | 392 | 402.6 | 435.3 | 421.6 | 467.3
553 | 393 | 402 | 436 | 422.4 | 467
554 | 394 | 401.5 | 436.6 | 423.3 | 466.7
555 | 395 | 400.9 | 437.4 | 424 | 466.4
556 | 396 | 400.4 | 438.3 | 424.3 | 466.3
557 | 397 | 399.8 | 439.1 | 424.9 | 466
558 | 398 | 399.3 | 439.8 | 425.6 | 465.7
559 | 399 | 398.8 | 440.6 | 426.3 | 465.4
560 | 400 | 398.2 | 441.3 | 427.1 | 465.1
561 | 401 | 397.6 | 442.1 | 427.8 | 464.8
562 | 402 | 397.1 | 443 | 428.2 | 464.6
563 | 403 | 396.6 | 443.8 | 428.8 | 464.3
564 | 404 | 396 | 444.7 | 429.5 | 464
565 | 405 | 395.5 | 445.5 | 430.3 | 463.7
566 | 406 | 394.9 | 446.3 | 431.1 | 463.3
567 | 407 | 394.3 | 447.1 | 432 | 463
568 | 408 | 393.8 | 448 | 432.8 | 462.7
569 | 409 | 393.3 | 448.7 | 433.7 | 462.4
570 | 410 | 392.7 | 449.3 | 434.7 | 462.1
571 | 411 | 392.2 | 449.8 | 436 | 461.6
572 | 412 | 391.7 | 450.4 | 437.1 | 461.3
573 | 413 | 391.1 | 451 | 438.2 | 460.9
574 | 414 | 390.6 | 451.9 | 439 | 460.7
575 | 415 | 390.1 | 452.7 | 440.2 | 460.3
576 | 416 | 389.5 | 454 | 441.1 | 460
577 | 417 | 389 | 456 | 442.1 | 459.7
578 | 418 | 388.5 | 458 | 442.8 | 459.4
579 | 419 | 387.9 | 459.9 | 443.8 | 459.1
580 | 420 | 387.4 | 461.7 | 444.9 | 458.8
581 | 421 | 386.8 | 463.5 | 445.9 | 458.5
582 | 422 | 386.2 | 465.2 | 446.5 | 458.3
583 | 423 | 385.7 | 466.6 | 447.5 | 457.9
584 | 424 | 385.1 | 468.1 | 448.3 | 457.7
585 | 425 | 384.5 | 469.5 | 449.1 | 457.4
586 | 426 | 383.9 | 470.9 | 450 | 457.1
587 | 427 | 383.4 | 472.3 | 450.5 | 456.9
588 | 428 | 382.8 | 473.5 | 451.3 | 456.5
589 | 429 | 382.3 | 474.7 | 452.2 | 456.2
590 | 430 | 381.7 | 475.8 | 453 | 455.8
591 | 431 | 381.2 | 477 | 453.3 | 455.6
592 | 432 | 380.6 | 478.1 | 453.7 | 455.4
593 | 433 | 380.1 | 479.1 | 454.2 | 455.1
594 | 434 | 379.6 | 480 | 454.7 | 454.8
595 | 435 | 379 | 480.8 | 455.3 | 454.5
596 | 436 | 378.5 | 481.5 | 455.7 | 454.2
597 | 437 | 378 | 482.2 | 456 | 453.9
598 | 438 | 377.5 | 482.9 | 456.2 | 453.6
599 | 439 | 377 | 483.8 | 456.4 | 453.3
600 | 440 | 376.6 | 484.6 | 456.4 | 453
601 | 441 | 376.1 | 485.3 | 456.4 | 452.7
602 | 442 | 375.6 | 486 | 456.6 | 452.4
603 | 443 | 375.1 | 486.7 | 456.9 | 452.1
604 | 444 | 374.6 | 487.2 | 457.5 | 451.7
605 | 445 | 374.1 | 487.8 | 457.9 | 451.3
606 | 446 | 373.6 | 488.5 | 458.1 | 451
607 | 447 | 373 | 488.9 | 458.5 | 450.7
608 | 448 | 372.5 | 489.6 | 458.3 | 450.5
609 | 449 | 372 | 490.2 | 458.2 | 450.2
610 | 450 | 371.5 | 490.8 | 458.4 | 449.8
611 | 451 | 371 | 491.4 | 458.5 | 449.5
612 | 452 | 370.5 | 491.9 | 458.6 | 449.2
613 | 453 | 370 | 492.6 | 458.6 | 448.9
614 | 454 | 369.5 | 493.2 | 458.8 | 448.6
615 | 455 | 369 | 493.7 | 459 | 448.2
616 | 456 | 368.5 | 494.4 | 459.1 | 447.9
617 | 457 | 368 | 495.1 | 459.2 | 447.6
618 | 458 | 367.5 | 495.8 | 459.2 | 447.3
619 | 459 | 366.9 | 496.5 | 458.9 | 447.1
620 | 460 | 366.5 | 497.1 | 458.9 | 446.8
621 | 461 | 365.9 | 497.6 | 459.1 | 446.5
622 | 462 | 365.4 | 498 | 459.4 | 446.1
623 | 463 | 364.9 | 498.4 | 459.6 | 445.7
624 | 464 | 364.5 | 498.8 | 459.3 | 445.4
625 | 465 | 364 | 499.3 | 459 | 445.1
626 | 466 | 363.5 | 499.6 | 458.8 | 444.8
627 | 467 | 363.1 | 500.1 | 458.4 | 444.5
628 | 468 | 362.6 | 500.9 | 458.2 | 444.2
629 | 469 | 362.1 | 501.7 | 458.1 | 443.9
630 | 470 | 361.7 | 502.4 | 458.1 | 443.6
631 | 471 | 361.2 | 502.9 | 458 | 443.2
632 | 472 | 360.7 | 503.4 | 458.1 | 442.9
633 | 473 | 360.3 | 504.2 | 458.2 | 442.6
634 | 474 | 359.7 | 504.9 | 457.8 | 442.3
635 | 475 | 359.3 | 505.3 | 457.5 | 441.9
636 | 476 | 358.7 | 505.8 | 457.4 | 441.6
637 | 477 | 358.2 | 506.6 | 457.5 | 441.2
638 | 478 | 357.9 | 507.1 | 457.2 | 440.9
639 | 479 | 357.4 | 507.6 | 457 | 440.5
640 | 480 | 357 | 508.2 | 456.9 | 440.2
641 | 481 | 356.5 | 508.7 | 456.7 | 439.9
642 | 482 | 356 | 509.4 | 456.8 | 439.5
643 | 483 | 355.5 | 510.1 | 457 | 439.2
644 | 484 | 355 | 510.6 | 457.1 | 438.9
645 | 485 | 354.6 | 510.9 | 457.1 | 438.5
646 | 486 | 354.1 | 511.1 | 457.2 | 438.2
647 | 487 | 353.7 | 511.6 | 456.9 | 437.9
648 | 488 | 353.2 | 511.8 | 457.1 | 437.5
649 | 489 | 352.8 | 512.4 | 457.3 | 437.2
650 | 490 | 352.3 | 512.9 | 457.4 | 436.8
651 | 491 | 351.9 | 513.2 | 457.6 | 436.5
652 | 492 | 351.5 | 513.6 | 457.7 | 436.2
653 | 493 | 351.1 | 514.3 | 457.9 | 436.2
654 | 494 | 350.7 | 514.8 | 458.1 | 436.2
655 | 495 | 350.3 | 515.6 | 458.6 | 436.2
656 | 496 | 349.9 | 516.3 | 459 | 436.2
657 | 497 | 349.5 | 517 | 459.4 | 436.3
658 | 498 | 349.1 | 517.7 | 459.9 | 436.4
659 | 499 | 348.8 | 518.3 | 459.8 | 436.6
660 | 500 | 348.4 | 519.1 | 459.9 | 436.9
661 | 501 | 348 | 519.8 | 460.3 | 437.2
662 | 502 | 347.6 | 520.4 | 460.5 | 437.6
663 | 503 | 347.2 | 520.8 | 460.4 | 438.1
664 | 504 | 346.9 | 521.5 | 460.3 | 438.7
665 | 505 | 346.6 | 522.1 | 460.4 | 439.4
666 | 506 | 346.2 | 523.3 | 460.1 | 440.2
667 | 507 | 345.9 | 523.8 | 459.8 | 441
668 | 508 | 345.6 | 524.4 | 459.5 | 441.8
669 | 509 | 345.3 | 524.3 | 459.4 | 442.7
670 | 510 | 345 | 524.6 | 459.5 | 443.6
671 | 511 | 344.7 | 524.8 | 459.4 | 444.7
672 | 512 | 344.4 | 525 | 459.4 | 445.8
673 | 513 | 344 | 525.4 | 459.6 | 446.8
674 | 514 | 343.7 | 525.8 | 460 | 447.9
675 | 515 | 343.3 | 526.3 | 460.1 | 448.9
676 | 516 | 343.1 | 526.8 | 460.5 | 450
677 | 517 | 342.9 | 527.6 | 461 | 451.2
678 | 518 | 342.6 | 528.2 | 461.4 | 452.4
679 | 519 | 342.4 | 527.8 | 462 | 453.5
680 | 520 | 342.3 | 527.7 | 462.6 | 454.7
681 | 521 | 342.1 | 527.7 | 463 | 455.9
682 | 522 | 341.9 | 528.2 | 463.5 | 457.1
683 | 523 | 341.7 | 528.8 | 464 | 458.3
684 | 524 | 341.5 | 529.4 | 464.8 | 459.4
685 | 525 | 341.3 | 529 | 465.6 | 460.5
686 | 526 | 341 | 528.8 | 466.1 | 461.7
687 | 527 | 340.8 | 528.6 | 466.7 | 462.8
688 | 528 | 340.6 | 528.3 | 467.5 | 464
689 | 529 | 340.5 | 528.6 | 468.3 | 465.1
690 | 530 | 340.4 | 529.2 | 469.3 | 466.3
691 | 531 | 340.2 | 529.7 | 470.3 | 467.4
692 | 532 | 340 | 529.9 | 471.4 | 468.5
693 | 533 | 339.8 | 530.5 | 472.7 | 469.5
694 | 534 | 339.7 | 531 | 474.1 | 470.5
695 | 535 | 339.6 | 531.2 | 475.2 | 471.5
696 | 536 | 339.5 | 532.1 | 476.1 | 472.6
697 | 537 | 339.4 | 534.1 | 476.8 | 473.6
698 | 538 | 339.3 | 533.8 | 477.7 | 474.7
699 | 539 | 339.2 | 533.7 | 478.5 | 475.8
700 | 540 | 339.1 | 533.6 | 479.1 | 477
701 | 541 | 339 | 533.6 | 479.9 | 478.1
702 | 542 | 338.8 | 533.3 | 480.7 | 479.1
703 | 543 | 338.8 | 533.5 | 481.3 | 480.2
704 | 544 | 338.8 | 533.9 | 481.6 | 481.1
705 | 545 | 338.8 | 533.4 | 481.6 | 481.9
706 | 546 | 338.9 | 533.8 | 482.2 | 482.9
707 | 547 | 338.8 | 533.5 | 483 | 483.8
708 | 548 | 338.6 | 533.3 | 483.9 | 484.6
709 | 549 | 338.5 | 533.7 | 484.7 | 485.5
710 | 550 | 338.4 | 533.7 | 485.3 | 486.3
711 | 551 | 338.4 | 533.4 | 485.6 | 487.1
712 | 552 | 338.4 | 533.4 | 486 | 487.9
713 | 553 | 338.2 | 533.2 | 486.3 | 488.8
714 | 554 | 338.1 | 533.3 | 486.8 | 489.5
715 | 555 | 337.9 | 533.5 | 487.5 | 490.2
716 | 556 | 337.8 | 533.8 | 488 | 491
717 | 557 | 337.6 | 533.3 | 488.6 | 491.8
718 | 558 | 337.5 | 532.8 | 489.2 | 492.5
719 | 559 | 337.4 | 533.8 | 489.7 | 493.1
720 | 560 | 337.2 | 533.1 | 490.2 | 493.9
721 | 561 | 337.1 | 532.7 | 490.7 | 494.6
722 | 562 | 336.9 | 532.8 | 491.3 | 495.3
723 | 563 | 336.9 | 532 | 492 | 496
724 | 564 | 336.8 | 531.6 | 492.3 | 496.7
725 | 565 | 336.7 | 531.3 | 492.8 | 497.4
726 | 566 | 336.7 | 530.7 | 493.5 | 498
727 | 567 | 336.6 | 530.1 | 494.2 | 498.4
728 | 568 | 336.5 | 529.6 | 494.7 | 498.9
729 | 569 | 336.3 | 528.8 | 495.3 | 499.3
730 | 570 | 336.2 | 528.1 | 496.1 | 499.7
731 | 571 | 336.1 | 528 | 496.9 | 499.7
732 | 572 | 335.9 | 528.2 | 497.2 | 500.1
733 | 573 | 335.8 | 528.5 | 497.8 | 500.6
734 | 574 | 335.7 | 529.2 | 498.3 | 501.3
735 | 575 | 335.7 | 529.5 | 498.9 | 501.9
736 | 576 | 335.6 | 529.4 | 499.6 | 502.5
737 | 577 | 335.5 | 529.8 | 499.9 | 503.2
738 | 578 | 335.3 | 530.3 | 500.4 | 503.8
739 | 579 | 335.3 | 530.5 | 501.1 | 504.3
740 | 580 | 335.4 | 530.9 | 501.9 | 504.7
741 | 581 | 335.3 | 531.5 | 502.4 | 504.9
742 | 582 | 335.3 | 532 | 503 | 505.1
743 | 583 | 335.2 | 532.4 | 503.6 | 505.3
744 | 584 | 335.1 | 532.8 | 504.3 | 505.7
745 | 585 | 335 | 533.1 | 505 | 506.1
746 | 586 | 334.8 | 533.4 | 505.9 | 506.4
747 | 587 | 334.8 | 533.8 | 506.5 | 506.6
748 | 588 | 334.6 | 533.6 | 507.2 | 506.9
749 | 589 | 334.5 | 533.5 | 508 | 507.1
750 | 590 | 334.3 | 533.9 | 508.7 | 507.3
751 | 591 | 334.1 | 534.2 | 509.3 | 507.6
752 | 592 | 333.9 | 534.4 | 509.9 | 507.7
753 | 593 | 333.7 | 534.5 | 510.7 | 507.9
754 | 594 | 333.6 | 534.4 | 511.9 | 508.1
755 | 595 | 333.4 | 535.2 | 513 | 508.4
756 | 596 | 333.3 | 536.3 | 513.7 | 508.6
757 | 597 | 333 | 536.2 | 514.5 | 509
758 | 598 | 332.8 | 536.4 | 515.4 | 509.3
759 | 599 | 332.6 | 537.1 | 515.9 | 509.7
760 | 600 | 332.6 | 537.5 | 516.7 | 510
761 | 601 | 332.5 | 538 | 517.4 | 510.3
762 | 602 | 332.4 | 539.1 | 518.1 | 510.3
763 | 603 | 332.3 | 541.1 | 518.7 | 510.5
764 | 604 | 332.1 | 541.5 | 519.6 | 510.5
765 | 605 | 331.9 | 542.1 | 520.4 | 510.5
766 | 606 | 331.7 | 542.4 | 521.3 | 510.4
767 | 607 | 331.5 | 543.4 | 522.2 | 510.3
768 | 608 | 331.2 | 544.5 | 522.6 | 510.3
769 | 609 | 331 | 545.5 | 523.2 | 510.3
770 | 610 | 330.9 | 546.4 | 523.8 | 510.2
771 | 611 | 330.7 | 547.6 | 524.5 | 510.1
772 | 612 | 330.5 | 549.5 | 525.2 | 509.9
773 | 613 | 330.3 | 549.2 | 525.7 | 509.6
774 | 614 | 330 | 549.1 | 526.2 | 509.2
775 | 615 | 329.7 | 548.9 | 526.6 | 508.9
776 | 616 | 329.5 | 548.1 | 527.3 | 508.6
777 | 617 | 329.1 | 547.4 | 527.7 | 508.3
778 | 618 | 328.8 | 547.1 | 527.8 | 507.9
779 | 619 | 328.5 | 546.9 | 528.1 | 507.3
780 | 620 | 328.1 | 547.5 | 528.6 | 506.6
781 | 621 | 327.8 | 548 | 528.8 | 505.9
782 | 622 | 327.4 | 548.4 | 528.9 | 505.1
783 | 623 | 327 | 548.7 | 529.1 | 504.4
784 | 624 | 326.8 | 548.9 | 529.3 | 503.7
785 | 625 | 326.5 | 549.3 | 529.2 | 503.1
786 | 626 | 326.1 | 549.5 | 529.4 | 502.4
787 | 627 | 325.8 | 549.7 | 529.7 | 501.7
788 | 628 | 325.5 | 550.6 | 529.9 | 500.9
789 | 629 | 325.3 | 551.7 | 530.2 | 500
790 | 630 | 324.9 | 552.8 | 530 | 499.3
791 | 631 | 324.6 | 553.5 | 529.9 | 498.3
792 | 632 | 324.3 | 554.7 | 530.1 | 497.4
793 | 633 | 324 | 556.2 | 530.3 | 496.5
794 | 634 | 323.6 | 557.8 | 530.5 | 495.7
795 | 635 | 323.3 | 559.5 | 530.7 | 494.7
796 | 636 | 323 | 561.1 | 530.7 | 493.8
797 | 637 | 322.6 | 563 | 530.8 | 492.8
798 | 638 | 322.3 | 563.7 | 530.9 | 491.8
799 | 639 | 322.1 | 565.7 | 531 | 490.9
800 | 640 | 321.8 | 567.8 | 531.1 | 489.9
801 | 641 | 321.6 | 569.3 | 531.5 | 488.9
802 | 642 | 321.3 | 569.9 | 531.8 | 488
803 | 643 | 320.9 | 570.7 | 531.8 | 487.1
804 | 644 | 320.6 | 571.3 | 532 | 486.2
805 | 645 | 320.4 | 571.8 | 532.3 | 485.2
806 | 646 | 320.1 | 572.3 | 532.6 | 484.3
807 | 647 | 319.9 | 573 | 532.9 | 483.4
808 | 648 | 319.6 | 574.2 | 532.9 | 482.5
809 | 649 | 319.3 | 574.7 | 533 | 481.7
810 | 650 | 319.1 | 575 | 533.2 | 480.8
811 | 651 | 318.8 | 575.2 | 533.5 | 479.9
812 | 652 | 318.5 | 575.3 | 533.8 | 479
813 | 653 | 318.1 | 575.7 | 534.1 | 478.1
814 | 654 | 317.8 | 575.7 | 534.4 | 477.3
815 | 655 | 317.5 | 576.3 | 534.7 | 476.4
816 | 656 | 317.3 | 577.1 | 535.1 | 475.5
817 | 657 | 317 | 577.7 | 535.3 | 474.7
818 | 658 | 316.7 | 578.2 | 535.5 | 473.9
819 | 659 | 316.4 | 578.9 | 535.7 | 473.1
820 | 660 | 316.1 | 579.8 | 536 | 472.3
821 | 661 | 315.8 | 580.5 | 536.3 | 471.5
822 | 662 | 315.6 | 581 | 536.7 | 470.6
823 | 663 | 315.4 | 581.2 | 537.1 | 469.8
824 | 664 | 315.2 | 581.4 | 537.6 | 469
825 | 665 | 315 | 582.2 | 537.9 | 468.2
826 | 666 | 314.7 | 583 | 538.3 | 467.5
827 | 667 | 314.5 | 583.7 | 538.6 | 466.7
828 | 668 | 314.3 | 584.1 | 539 | 466
829 | 669 | 314 | 584.9 | 539.4 | 465.2
830 | 670 | 313.8 | 585.7 | 539.8 | 464.4
831 | 671 | 313.5 | 586.6 | 540.2 | 463.7
832 | 672 | 313.3 | 587.7 | 540.5 | 463
833 | 673 | 313.1 | 588.4 | 540.9 | 462.2
834 | 674 | 312.9 | 589.1 | 541.4 | 461.4
835 | 675 | 312.6 | 589.7 | 541.8 | 460.7
836 | 676 | 312.3 | 590.2 | 542.1 | 460
837 | 677 | 312 | 591 | 542.5 | 459.3
838 | 678 | 311.8 | 591.8 | 543 | 458.5
839 | 679 | 311.5 | 592.8 | 543.5 | 457.8
840 | 680 | 311.2 | 593.9 | 543.9 | 457
841 | 681 | 311 | 594.9 | 544.3 | 456.3
842 | 682 | 310.8 | 595.6 | 544.5 | 455.7
843 | 683 | 310.5 | 596.1 | 544.6 | 455
844 | 684 | 310.3 | 596.8 | 545 | 454.3
845 | 685 | 310.1 | 597.7 | 545.4 | 453.5
846 | 686 | 309.8 | 598.5 | 545.8 | 452.8
847 | 687 | 309.6 | 599.5 | 546.2 | 452.1
848 | 688 | 309.3 | 600.7 | 546.6 | 451.4
849 | 689 | 309 | 602 | 547 | 450.8
850 | 690 | 308.7 | 603 | 547.3 | 450.1
851 | 691 | 308.5 | 603.8 | 547.7 | 449.4
852 | 692 | 308.2 | 604.6 | 548.2 | 448.7
853 | 693 | 307.9 | 605.6 | 548.7 | 448.1
854 | 694 | 307.7 | 607 | 549 | 447.4
855 | 695 | 307.4 | 608 | 549.4 | 446.8
856 | 696 | 307.1 | 608.8 | 549.7 | 446.2
857 | 697 | 306.8 | 609.5 | 550.3 | 445.5
858 | 698 | 306.5 | 610.3 | 550.9 | 444.9
859 | 699 | 306.2 | 611.1 | 551.5 | 444.2
860 | 700 | 306 | 611.5 | 552 | 443.6
861 | 701 | 305.8 | 611.5 | 552.4 | 442.9
862 | 702 | 305.6 | 611.7 | 552.9 | 442.3
863 | 703 | 305.3 | 612.3 | 553.3 | 441.7
864 | 704 | 305.1 | 613.2 | 553.8 | 441.1
865 | 705 | 304.8 | 614 | 554.3 | 440.5
866 | 706 | 304.6 | 614.9 | 554.9 | 439.8
867 | 707 | 304.3 | 616.1 | 555.3 | 439.3
868 | 708 | 304 | 617.4 | 555.8 | 438.7
869 | 709 | 303.8 | 618.5 | 556.3 | 438.1
870 | 710 | 303.5 | 619.5 | 556.7 | 437.5
871 | 711 | 303.3 | 620.2 | 557.2 | 436.9
872 | 712 | 303 | 621.1 | 557.6 | 436.3
873 | 713 | 302.7 | 622.2 | 558.1 | 435.7
874 | 714 | 302.4 | 623.5 | 558.5 | 435.1
875 | 715 | 302.2 | 624.5 | 558.9 | 434.6
876 | 716 | 301.9 | 625.5 | 559.4 | 434
877 | 717 | 301.7 | 626.6 | 559.8 | 433.4
878 | 718 | 301.4 | 627.5 | 560.2 | 432.8
879 | 719 | 301.1 | 628 | 560.7 | 432.2
880 | 720 | 300.9 | 629.1 | 561.3 | 431.6
881 | 721 | 300.6 | 630.1 | 561.9 | 431.1
882 | 722 | 300.4 | 631.3 | 562.4 | 430.5
883 | 723 | 300.2 | 632.4 | 562.9 | 429.9
884 | 724 | 299.9 | 633.7 | 563.5 | 429.4
885 | 725 | 299.7 | 635.2 | 564.2 | 428.8
886 | 726 | 299.4 | 636.9 | 564.7 | 428.2
887 | 727 | 299.1 | 638.3 | 565.4 | 427.7
888 | 728 | 298.9 | 639.7 | 566.3 | 427
889 | 729 | 298.6 | 641.3 | 566.9 | 426.5
890 | 730 | 298.4 | 642.5 | 567.3 | 426
891 | 731 | 298.1 | 643.9 | 567.8 | 425.4
892 | 732 | 297.9 | 645.3 | 568.3 | 424.9
893 | 733 | 297.6 | 647.2 | 569 | 424.4
894 | 734 | 297.4 | 648.8 | 569.7 | 423.8
895 | 735 | 297.1 | 649.9 | 570.3 | 423.3
896 | 736 | 296.8 | 650.9 | 570.8 | 422.8
897 | 737 | 296.5 | 651.6 | 571.4 | 422.3
898 | 738 | 296.3 | 652.1 | 571.9 | 421.8
899 | 739 | 296.1 | 653.2 | 572.6 | 421.2
900 | 740 | 295.9 | 654 | 573.2 | 420.7
901 | 741 | 295.7 | 655.2 | 573.7 | 420.2
902 | 742 | 295.4 | 656.5 | 574.2 | 419.6
903 | 743 | 295.2 | 657 | 574.9 | 419.1
904 | 744 | 294.9 | 657.2 | 575.8 | 418.5
905 | 745 | 294.7 | 657.6 | 576.5 | 418
906 | 746 | 294.4 | 658.1 | 576.8 | 417.6
907 | 747 | 294.2 | 658.3 | 577.3 | 417.1
908 | 748 | 293.9 | 657.8 | 577.9 | 416.6
909 | 749 | 293.7 | 657.6 | 578.3 | 416.1
910 | 750 | 293.4 | 657 | 578.9 | 415.6
911 | 751 | 293.2 | 656.7 | 579.6 | 415.1
912 | 752 | 293 | 656.8 | 580 | 414.6
913 | 753 | 292.7 | 657.2 | 580.5 | 414.1
914 | 754 | 292.5 | 657.3 | 581 | 413.6
915 | 755 | 292.3 | 656.5 | 581.6 | 413.1
916 | 756 | 292 | 655 | 582 | 412.7
917 | 757 | 291.7 | 653.5 | 582.5 | 412.2
918 | 758 | 291.5 | 653.1 | 583.1 | 411.7
919 | 759 | 291.2 | 652.7 | 583.7 | 411.2
920 | 760 | 290.9 | 651.9 | 584.4 | 410.7
921 | 761 | 290.6 | 651.1 | 585.1 | 410.3
922 | 762 | 290.3 | 650.4 | 586 | 409.8
923 | 763 | 290 | 649.1 | 586.9 | 409.3
924 | 764 | 289.7 | 647.6 | 587.7 | 408.9
925 | 765 | 289.4 | 646.5 | 588.2 | 408.4
926 | 766 | 289.2 | 645.3 | 588.8 | 407.9
927 | 767 | 288.9 | 644.5 | 589.4 | 407.5
928 | 768 | 288.7 | 643.5 | 590.1 | 407
929 | 769 | 288.4 | 642.3 | 590.7 | 406.5
930 | 770 | 288.1 | 640.9 | 591.2 | 406.1
931 | 771 | 287.8 | 638.9 | 591.7 | 405.7
932 | 772 | 287.6 | 637.2 | 592.4 | 405.2
933 | 773 | 287.3 | 635.3 | 593.3 | 404.7
934 | 774 | 287.1 | 633.6 | 593.5 | 404.4
935 | 775 | 286.8 | 631.9 | 593.9 | 403.9
936 | 776 | 286.6 | 629.5 | 594.4 | 403.5
937 | 777 | 286.4 | 627.4 | 594.8 | 403
938 | 778 | 286.1 | 625.6 | 595.3 | 402.5
939 | 779 | 285.8 | 623.9 | 595.4 | 402.2
940 | 780 | 285.6 | 622.3 | 595.9 | 401.8
941 | 781 | 285.4 | 620.3 | 596.3 | 401.3
942 | 782 | 285.1 | 618.9 | 596.8 | 400.9
943 | 783 | 284.9 | 617.2 | 597.5 | 400.4
944 | 784 | 284.7 | 615.4 | 598.2 | 400
945 | 785 | 284.4 | 613.7 | 598.8 | 399.6
946 | 786 | 284.2 | 611.9 | 599.5 | 399.1
947 | 787 | 283.9 | 610.5 | 599.8 | 398.7
948 | 788 | 283.7 | 608.6 | 600.2 | 398.3
949 | 789 | 283.5 | 606.9 | 600.7 | 397.9
950 | 790 | 283.2 | 605.1 | 601.4 | 397.5
951 | 791 | 283 | 603.7 | 602.1 | 397.1
952 | 792 | 282.7 | 602.3 | 602.8 | 396.6
953 | 793 | 282.5 | 601 | 603.3 | 396.2
954 | 794 | 282.2 | 599.8 | 603.5 | 395.8
955 | 795 | 282 | 598.3 | 604 | 395.4
956 | 796 | 281.7 | 596.2 | 604.8 | 394.9
957 | 797 | 281.5 | 594.4 | 605.4 | 394.5
958 | 798 | 281.2 | 592.9 | 605.9 | 394.1
959 | 799 | 281 | 591.2 | 606.1 | 393.7
960 | 800 | 280.8 | 590 | 606.4 | 393.3
961 | 801 | 280.5 | 588.7 | 606.7 | 392.9
962 | 802 | 280.3 | 587.6 | 607 | 392.5
963 | 803 | 280.1 | 586.2 | 607.1 | 392.1
964 | 804 | 279.9 | 584.8 | 607.4 | 391.7
965 | 805 | 279.6 | 583.5 | 607.7 | 391.3
966 | 806 | 279.4 | 582.8 | 607.9 | 391
967 | 807 | 279.2 | 581.5 | 608.3 | 390.6
968 | 808 | 278.9 | 580.5 | 608.8 | 390.2
969 | 809 | 278.7 | 579.5 | 609.4 | 389.8
970 | 810 | 278.4 | 578.6 | 609.8 | 389.4
971 | 811 | 278.2 | 577.6 | 609.9 | 389
972 | 812 | 278 | 576 | 610.4 | 388.6
973 | 813 | 277.8 | 574.8 | 610.9 | 388.2
974 | 814 | 277.6 | 573.6 | 611.4 | 387.8
975 | 815 | 277.3 | 572.5 | 611.8 | 387.5
976 | 816 | 277.1 | 571.1 | 612.3 | 387.1
977 | 817 | 276.9 | 570 | 613 | 386.7
978 | 818 | 276.7 | 568.5 | 613.7 | 386.3
979 | 819 | 276.4 | 567.2 | 614.2 | 385.9
980 | 820 | 276.2 | 566.1 | 614.7 | 385.6
981 | 821 | 275.9 | 565.1 | 615.3 | 385.2
982 | 822 | 275.7 | 564.1 | 615.8 | 384.8
983 | 823 | 275.4 | 562.8 | 616 | 384.5
984 | 824 | 275.2 | 561.9 | 616.3 | 384.1
985 | 825 | 275 | 560.7 | 616.6 | 383.7
986 | 826 | 274.8 | 559.8 | 617 | 383.3
987 | 827 | 274.6 | 558.8 | 617.6 | 382.9
988 | 828 | 274.3 | 558.4 | 617.8 | 382.6
989 | 829 | 274.1 | 557.6 | 618.1 | 382.1
990 | 830 | 273.9 | 556.6 | 618 | 381.8
991 | 831 | 273.7 | 555.5 | 618.3 | 381.5
992 | 832 | 273.4 | 554.4 | 618.8 | 381.1
993 | 833 | 273.2 | 553.5 | 619.3 | 380.7
994 | 834 | 273 | 552.5 | 619.7 | 380.3
995 | 835 | 272.7 | 551.6 | 619.9 | 380
996 | 836 | 272.5 | 550.5 | 620.2 | 379.7
997 | 837 | 272.3 | 549.4 | 620.6 | 379.2
998 | 838 | 272.1 | 548.6 | 620.7 | 379
999 | 839 | 271.8 | 547.7 | 621 | 378.6
1000 | 840 | 271.6 | 546.5 | 621.3 | 378.2
1001 | 841 | 271.4 | 545.5 | 621.5 | 377.9
1002 | 842 | 271.2 | 544.8 | 621.5 | 377.6
1003 | 843 | 271 | 543.9 | 622 | 377.2
1004 | 844 | 270.7 | 542.9 | 622.5 | 376.8
1005 | 845 | 270.5 | 542.2 | 622.6 | 376.6
1006 | 846 | 270.3 | 541.5 | 622.9 | 376.4
1007 | 847 | 270.1 | 541.3 | 623.1 | 376
1008 | 848 | 269.8 | 540.7 | 623.3 | 375.8
1009 | 849 | 269.6 | 539.9 | 623.4 | 375.5
1010 | 850 | 269.4 | 539.3 | 623.5 | 375.4
1011 | 851 | 269.2 | 538.1 | 623.8 | 375.2
1012 | 852 | 268.9 | 537.6 | 623.6 | 375.1
1013 | 853 | 268.7 | 536.4 | 623.6 | 374.9
1014 | 854 | 268.5 | 535.3 | 623.5 | 374.8
1015 | 855 | 268.3 | 534.2 | 623.6 | 374.6
1016 | 856 | 268.1 | 533 | 623.6 | 374.5
1017 | 857 | 267.9 | 532.3 | 624 | 374.2
1018 | 858 | 267.6 | 531.2 | 624.2 | 374
1019 | 859 | 267.3 | 530.1 | 624.1 | 373.9
1020 | 860 | 267.1 | 529.3 | 624.2 | 373.7
1021 | 861 | 266.9 | 527.7 | 624.5 | 373.4
1022 | 862 | 266.7 | 526.5 | 624.4 | 373.2
1023 | 863 | 266.4 | 525.7 | 624.5 | 373.1
1024 | 864 | 266.2 | 524.8 | 624.8 | 372.7
1025 | 865 | 266.1 | 523.6 | 624.9 | 372.4
1026 | 866 | 265.8 | 522.5 | 624.8 | 372.2
1027 | 867 | 265.6 | 521.3 | 625.2 | 371.9
1028 | 868 | 265.4 | 520.4 | 625.4 | 371.7
1029 | 869 | 265.2 | 519.5 | 625.8 | 371.4
1030 | 870 | 264.9 | 518.5 | 626 | 371.2
1031 | 871 | 264.7 | 517.6 | 626.7 | 370.9
1032 | 872 | 264.5 | 516.7 | 626.6 | 370.7
1033 | 873 | 264.2 | 515.6 | 626.4 | 370.4
1034 | 874 | 264 | 514.5 | 626.5 | 370.1
1035 | 875 | 263.9 | 513.1 | 627 | 369.6
1036 | 876 | 263.6 | 512.1 | 626.8 | 369.5
1037 | 877 | 263.3 | 511.3 | 626.6 | 369.3
1038 | 878 | 263.2 | 510.1 | 627 | 368.9
1039 | 879 | 262.9 | 509.1 | 626.7 | 368.8
1040 | 880 | 262.6 | 508.1 | 626.6 | 368.6
1041 | 881 | 262.4 | 506.5 | 626.8 | 368.3
1042 | 882 | 262.2 | 504.9 | 627 | 368.1
1043 | 883 | 262 | 503.7 | 627 | 367.9
1044 | 884 | 261.8 | 502.6 | 627.3 | 367.6
1045 | 885 | 261.6 | 501.7 | 627.4 | 367.4
1046 | 886 | 261.3 | 500.7 | 627.4 | 367.3
1047 | 887 | 261.1 | 499.5 | 627.7 | 367.1
1048 | 888 | 260.9 | 498.2 | 627.9 | 366.9
1049 | 889 | 260.7 | 497.5 | 627.8 | 366.8
1050 | 890 | 260.5 | 496.7 | 627.8 | 366.6
1051 | 891 | 260.2 | 495.1 | 627.8 | 366.4
1052 | 892 | 260 | 494 | 627.7 | 366.3
1053 | 893 | 259.8 | 493.1 | 627.8 | 366.1
1054 | 894 | 259.6 | 492.2 | 627.9 | 365.9
1055 | 895 | 259.3 | 491.4 | 627.7 | 365.8
1056 | 896 | 259.1 | 490.6 | 627.6 | 365.8
1057 | 897 | 258.9 | 489.6 | 627.9 | 365.6
1058 | 898 | 258.7 | 488.7 | 628.2 | 365.3
1059 | 899 | 258.5 | 487.9 | 628.1 | 365.2
1060 | 900 | 258.3 | 487.6 | 628.1 | 365
1061 | 901 | 258 | 486.9 | 628.2 | 364.8
1062 | 902 | 257.8 | 485.8 | 628.5 | 364.5
1063 | 903 | 257.6 | 485.1 | 629 | 364.2
1064 | 904 | 257.4 | 484.3 | 629.2 | 364
1065 | 905 | 257.2 | 483.4 | 629.3 | 363.8
1066 | 906 | 257 | 482.4 | 629.5 | 363.5
1067 | 907 | 256.8 | 481.2 | 629.6 | 363.3
1068 | 908 | 256.5 | 480.4 | 629.6 | 363.1
1069 | 909 | 256.3 | 479.6 | 629.9 | 362.8
1070 | 910 | 256.1 | 478.8 | 630 | 362.6
1071 | 911 | 255.9 | 478.1 | 630.1 | 362.4
1072 | 912 | 255.7 | 477.1 | 630.3 | 362.1
1073 | 913 | 255.5 | 476.4 | 630 | 361.9
1074 | 914 | 255.2 | 475.6 | 629.9 | 361.7
1075 | 915 | 255 | 474.4 | 630 | 361.5
1076 | 916 | 254.8 | 473.4 | 629.9 | 361.3
1077 | 917 | 254.6 | 472.7 | 629.8 | 361.1
1078 | 918 | 254.4 | 472.1 | 629.9 | 360.9
1079 | 919 | 254.2 | 471.4 | 630.2 | 360.6
1080 | 920 | 254 | 471 | 630 | 360.4
1081 | 921 | 253.8 | 470.5 | 629.8 | 360.2
1082 | 922 | 253.6 | 469.8 | 630.2 | 359.9
1083 | 923 | 253.4 | 469.2 | 630.6 | 359.5
1084 | 924 | 253.2 | 468.6 | 630.3 | 359.3
1085 | 925 | 253 | 467.8 | 630.3 | 359.1
1086 | 926 | 252.8 | 466.7 | 630.4 | 358.8
1087 | 927 | 252.6 | 466.3 | 630.2 | 358.6
1088 | 928 | 252.4 | 466 | 630.1 | 358.4
1089 | 929 | 252.2 | 465.5 | 629.9 | 358.1
1090 | 930 | 251.9 | 464.8 | 629.9 | 357.9
1091 | 931 | 251.7 | 464.2 | 629.8 | 357.6
1092 | 932 | 251.5 | 463.8 | 629.6 | 357.5
1093 | 933 | 251.3 | 463.2 | 629.5 | 357.2
1094 | 934 | 251.1 | 462.4 | 629.5 | 357
1095 | 935 | 250.9 | 461.5 | 629.5 | 356.7
1096 | 936 | 250.6 | 461.4 | 629.1 | 356.6
1097 | 937 | 250.4 | 460.9 | 629.2 | 356.3
1098 | 938 | 250.2 | 460.5 | 629 | 356.2
1099 | 939 | 250 | 460.1 | 628.7 | 356.1
1100 | 940 | 249.7 | 459.4 | 628.5 | 356
1101 | 941 | 249.6 | 458.7 | 628.4 | 355.8
1102 | 942 | 249.4 | 458.2 | 628.2 | 355.7
1103 | 943 | 249.2 | 457.6 | 627.9 | 355.6
1104 | 944 | 249 | 456.7 | 628 | 355.4
1105 | 945 | 248.8 | 456 | 627.9 | 355.3
1106 | 946 | 248.6 | 455.1 | 627.8 | 355.2
1107 | 947 | 248.3 | 454.9 | 627.5 | 355.1
1108 | 948 | 248.1 | 454.1 | 627.6 | 354.9
1109 | 949 | 247.9 | 453.3 | 627.7 | 354.8
1110 | 950 | 247.7 | 453 | 627.6 | 354.7
1111 | 951 | 247.4 | 452.3 | 627.5 | 354.5
1112 | 952 | 247.3 | 451.3 | 627.6 | 354.3
1113 | 953 | 247.1 | 450.2 | 627.5 | 354.1
1114 | 954 | 246.8 | 449.2 | 627.2 | 353.9
1115 | 955 | 246.7 | 448.4 | 627.2 | 353.6
1116 | 956 | 246.4 | 447.9 | 627 | 353.4
1117 | 957 | 246.2 | 447.3 | 626.8 | 353.1
1118 | 958 | 246 | 446.7 | 626.5 | 352.9
1119 | 959 | 245.8 | 446 | 626.3 | 352.6
1120 | 960 | 245.7 | 445.5 | 625.9 | 352.4
1121 | 961 | 245.4 | 444.8 | 625.4 | 352.2
1122 | 962 | 245.3 | 444.1 | 625.3 | 351.9
1123 | 963 | 245.1 | 443.9 | 625.1 | 351.6
1124 | 964 | 244.9 | 443.4 | 624.5 | 351.4
1125 | 965 | 244.7 | 442.8 | 624.2 | 351.1
1126 | 966 | 244.5 | 441.7 | 624 | 350.8
1127 | 967 | 244.3 | 440.9 | 623.8 | 350.5
1128 | 968 | 244.1 | 440.1 | 623.6 | 350.2
1129 | 969 | 243.9 | 439.3 | 623.3 | 349.9
1130 | 970 | 243.7 | 438.5 | 623 | 349.6
1131 | 971 | 243.5 | 437.8 | 622.6 | 349.3
1132 | 972 | 243.3 | 437.1 | 622.3 | 348.9
1133 | 973 | 243.1 | 436.4 | 622 | 348.6
1134 | 974 | 242.9 | 435.5 | 621.7 | 348.2
1135 | 975 | 242.7 | 434.7 | 621.1 | 348
1136 | 976 | 242.5 | 434.5 | 620.6 | 347.7
1137 | 977 | 242.3 | 434 | 620.2 | 347.4
1138 | 978 | 242.1 | 433 | 619.7 | 347.1
1139 | 979 | 241.9 | 431.7 | 619.3 | 346.7
1140 | 980 | 241.7 | 430.7 | 619 | 346.4
1141 | 981 | 241.5 | 429.7 | 618.6 | 346
1142 | 982 | 241.3 | 428.9 | 618.2 | 345.7
1143 | 983 | 241.1 | 428.3 | 617.8 | 345.3
1144 | 984 | 240.9 | 427.6 | 617.4 | 345
1145 | 985 | 240.7 | 426.7 | 616.9 | 344.6
1146 | 986 | 240.5 | 425.9 | 616.5 | 344.2
1147 | 987 | 240.4 | 425.1 | 616.2 | 343.9
1148 | 988 | 240.2 | 424.2 | 615.6 | 343.6
1149 | 989 | 240 | 423.5 | 615.1 | 343.3
1150 | 990 | 239.8 | 422.6 | 614.7 | 342.9
1151 | 991 | 239.6 | 421.9 | 614.2 | 342.6
1152 | 992 | 239.5 | 420.8 | 613.8 | 342.2
1153 | 993 | 239.3 | 419.7 | 613.4 | 341.8
1154 | 994 | 239.1 | 418.9 | 613.2 | 341.5
1155 | 995 | 238.9 | 418.3 | 612.6 | 341.1
1156 | 996 | 238.7 | 417.8 | 612.1 | 340.8
1157 | 997 | 238.5 | 417 | 611.5 | 340.4
1158 | 998 | 238.4 | 416.1 | 611 | 340.1
1159 | 999 | 238.2 | 415.2 | 610.4 | 339.8
1160 | 1000 | 238 | 414.3 | 609.9 | 339.4
1161 | 1001 | 237.8 | 413.5 | 609.3 | 339
1162 | 1002 | 237.6 | 412.7 | 608.7 | 338.7
1163 | 1003 | 237.4 | 411.6 | 608.1 | 338.3
1164 | 1004 | 237.1 | 410.7 | 607.5 | 338
1165 | 1005 | 236.9 | 409.9 | 606.9 | 337.6
1166 | 1006 | 236.7 | 409.5 | 606.2 | 337.2
1167 | 1007 | 236.5 | 408.7 | 605.6 | 336.9
1168 | 1008 | 236.3 | 408 | 605.1 | 336.6
1169 | 1009 | 236.1 | 407.5 | 604.5 | 336.2
1170 | 1010 | 235.9 | 406.3 | 603.9 | 335.8
1171 | 1011 | 235.7 | 404.8 | 603.5 | 335.4
1172 | 1012 | 235.5 | 403.7 | 602.8 | 335.1
1173 | 1013 | 235.3 | 402.8 | 602.1 | 334.8
1174 | 1014 | 235.1 | 401.8 | 601.6 | 334.5
1175 | 1015 | 235 | 400.7 | 601 | 334.1
1176 | 1016 | 234.7 | 399.5 | 600.5 | 333.7
1177 | 1017 | 234.5 | 398.6 | 599.8 | 333.5
1178 | 1018 | 234.4 | 397.5 | 599.3 | 333.1
1179 | 1019 | 234.2 | 396.3 | 598.8 | 332.7
1180 | 1020 | 234 | 395.6 | 598.3 | 332.4
1181 | 1021 | 233.8 | 394.6 | 597.7 | 332
1182 | 1022 | 233.6 | 393.5 | 597 | 331.7
1183 | 1023 | 233.4 | 392.7 | 596.3 | 331.4
1184 | 1024 | 233.2 | 391.5 | 595.7 | 331
1185 | 1025 | 232.9 | 390.3 | 594.9 | 330.8
1186 | 1026 | 232.7 | 389.4 | 594.2 | 330.4
1187 | 1027 | 232.5 | 388.6 | 593.3 | 330.2
1188 | 1028 | 232.3 | 387.8 | 592.5 | 329.9
1189 | 1029 | 232.1 | 387.1 | 592 | 329.5
1190 | 1030 | 231.9 | 386.1 | 591.3 | 329.1
1191 | 1031 | 231.7 | 385 | 590.5 | 328.8
1192 | 1032 | 231.5 | 383.5 | 589.9 | 328.5
1193 | 1033 | 231.3 | 382.2 | 589.3 | 328.1
1194 | 1034 | 231.2 | 381.2 | 588.6 | 327.8
1195 | 1035 | 231 | 380.3 | 587.9 | 327.4
1196 | 1036 | 230.8 | 379.5 | 587.1 | 327.1
1197 | 1037 | 230.6 | 378.6 | 586.3 | 326.8
1198 | 1038 | 230.5 | 377.8 | 585.6 | 326.4
1199 | 1039 | 230.3 | 377.2 | 584.7 | 326.1
1200 | 1040 | 230.1 | 376.6 | 583.8 | 325.7
1201 | 1041 | 229.9 | 375.9 | 582.9 | 325.4
1202 | 1042 | 229.8 | 375.2 | 582.2 | 325.1
1203 | 1043 | 229.6 | 374.6 | 581.4 | 324.7
1204 | 1044 | 229.4 | 373.9 | 580.4 | 324.4
1205 | 1045 | 229.2 | 373 | 579.5 | 324.1
1206 | 1046 | 229 | 372.2 | 578.6 | 323.7
1207 | 1047 | 228.9 | 371.3 | 577.8 | 323.3
1208 | 1048 | 228.7 | 370.4 | 576.8 | 323
1209 | 1049 | 228.4 | 369.7 | 575.8 | 322.7
1210 | 1050 | 228.2 | 368.8 | 574.7 | 322.4
1211 | 1051 | 228 | 368 | 573.7 | 322
1212 | 1052 | 227.9 | 367.3 | 572.6 | 321.7
1213 | 1053 | 227.7 | 366.5 | 571.7 | 321.3
1214 | 1054 | 227.5 | 365.9 | 570.5 | 321
1215 | 1055 | 227.3 | 365.1 | 569.5 | 320.7
1216 | 1056 | 227.2 | 364.2 | 568.6 | 320.2
1217 | 1057 | 227 | 363.4 | 567.6 | 319.9
1218 | 1058 | 226.8 | 362.8 | 566.4 | 319.5
1219 | 1059 | 226.6 | 362.4 | 565.3 | 319.2
1220 | 1060 | 226.5 | 361.6 | 564.1 | 318.9
1221 | 1061 | 226.3 | 360.8 | 562.9 | 318.5
1222 | 1062 | 226.2 | 359.9 | 561.8 | 318.1
1223 | 1063 | 226 | 359.2 | 560.6 | 317.8
1224 | 1064 | 225.9 | 358.4 | 559.3 | 317.4
1225 | 1065 | 225.7 | 357.7 | 558.1 | 317.1
1226 | 1066 | 225.5 | 356.8 | 556.9 | 316.7
1227 | 1067 | 225.3 | 355.9 | 555.6 | 316.4
1228 | 1068 | 225.1 | 355.3 | 554.2 | 316
1229 | 1069 | 225 | 354.9 | 552.8 | 315.7
1230 | 1070 | 224.8 | 354.3 | 551.4 | 315.3
1231 | 1071 | 224.6 | 353.7 | 550 | 315
1232 | 1072 | 224.4 | 352.8 | 548.5 | 314.6
1233 | 1073 | 224.2 | 352.1 | 547 | 314.3
1234 | 1074 | 224 | 351.5 | 545.5 | 313.9
1235 | 1075 | 223.8 | 350.9 | 543.9 | 313.6
1236 | 1076 | 223.6 | 350.2 | 542.4 | 313.2
1237 | 1077 | 223.4 | 349.4 | 540.8 | 312.9
1238 | 1078 | 223.2 | 348.6 | 539.2 | 312.5
1239 | 1079 | 223 | 348 | 537.6 | 312.2
1240 | 1080 | 222.8 | 347.3 | 535.9 | 311.9
1241 | 1081 | 222.6 | 346.7 | 534.2 | 311.6
1242 | 1082 | 222.4 | 346.2 | 532.6 | 311.2
1243 | 1083 | 222.2 | 345.5 | 530.9 | 310.9
1244 | 1084 | 222 | 344.6 | 529.4 | 310.5
1245 | 1085 | 221.9 | 343.7 | 527.9 | 310.1
1246 | 1086 | 221.7 | 343.1 | 526.1 | 309.8
1247 | 1087 | 221.5 | 342.5 | 524.3 | 309.5
1248 | 1088 | 221.3 | 341.9 | 522.7 | 309.1
1249 | 1089 | 221.1 | 341.2 | 521 | 308.8
1250 | 1090 | 221 | 340.5 | 519.3 | 308.4
1251 | 1091 | 220.8 | 339.7 | 517.5 | 308.1
1252 | 1092 | 220.6 | 338.9 | 515.8 | 307.7
1253 | 1093 | 220.4 | 338.3 | 514 | 307.4
1254 | 1094 | 220.3 | 337.7 | 512.2 | 307
1255 | 1095 | 220.1 | 337 | 510.4 | 306.6
1256 | 1096 | 219.9 | 336.1 | 508.6 | 306.2
1257 | 1097 | 219.7 | 335.2 | 506.9 | 305.8
1258 | 1098 | 219.5 | 334.5 | 504.9 | 305.5
1259 | 1099 | 219.4 | 333.9 | 502.9 | 305.2
1260 | 1100 | 219.1 | 333.3 | 500.8 | 304.9
1261 | 1101 | 219 | 332.5 | 499.1 | 304.5
1262 | 1102 | 218.8 | 331.9 | 497.1 | 304.1
1263 | 1103 | 218.7 | 331.5 | 495.1 | 303.8
1264 | 1104 | 218.5 | 330.9 | 493.2 | 303.4
1265 | 1105 | 218.3 | 330.2 | 491.2 | 303.1
1266 | 1106 | 218.1 | 329.7 | 489.3 | 302.7
1267 | 1107 | 218 | 329.1 | 487.6 | 302.3
1268 | 1108 | 217.8 | 328.6 | 485.6 | 302
1269 | 1109 | 217.6 | 327.9 | 483.7 | 301.6
1270 | 1110 | 217.5 | 327.2 | 481.9 | 301.2
1271 | 1111 | 217.3 | 326.7 | 480 | 300.9
1272 | 1112 | 217.1 | 326.2 | 478 | 300.6
1273 | 1113 | 216.9 | 325.4 | 476.3 | 300.2
1274 | 1114 | 216.8 | 324.6 | 474.7 | 299.7
1275 | 1115 | 216.5 | 324.2 | 472.6 | 299.5
1276 | 1116 | 216.4 | 323.8 | 470.6 | 299.2
1277 | 1117 | 216.2 | 323.1 | 468.7 | 298.8
1278 | 1118 | 216 | 322.6 | 466.7 | 298.5
1279 | 1119 | 215.8 | 322 | 465 | 298.1
1280 | 1120 | 215.7 | 321.3 | 463.3 | 297.8
1281 | 1121 | 215.5 | 320.5 | 461.5 | 297.3
1282 | 1122 | 215.3 | 319.8 | 459.7 | 297
1283 | 1123 | 215.1 | 319.1 | 458.1 | 296.6
1284 | 1124 | 214.9 | 318.4 | 456.2 | 296.3
1285 | 1125 | 214.8 | 317.8 | 454.4 | 295.9
1286 | 1126 | 214.6 | 316.9 | 452.7 | 295.5
1287 | 1127 | 214.5 | 316.2 | 451 | 295.1
1288 | 1128 | 214.3 | 315.5 | 449.1 | 294.8
1289 | 1129 | 214.1 | 314.8 | 447.2 | 294.4
1290 | 1130 | 213.9 | 314.2 | 445.4 | 294.1
1291 | 1131 | 213.7 | 313.5 | 443.6 | 293.7
1292 | 1132 | 213.5 | 312.6 | 441.8 | 293.4
1293 | 1133 | 213.3 | 311.9 | 440.1 | 293
1294 | 1134 | 213.2 | 311.1 | 438.4 | 292.6
1295 | 1135 | 213 | 310.3 | 436.6 | 292.2
1296 | 1136 | 212.8 | 309.4 | 434.8 | 291.9
1297 | 1137 | 212.7 | 308.5 | 433.1 | 291.5
1298 | 1138 | 212.5 | 307.7 | 431.3 | 291.1
1299 | 1139 | 212.4 | 307 | 429.6 | 290.7
1300 | 1140 | 212.2 | 306.3 | 427.8 | 290.4
1301 | 1141 | 212 | 305.7 | 426.1 | 290
1302 | 1142 | 211.8 | 305 | 424.3 | 289.6
1303 | 1143 | 211.6 | 304.2 | 422.6 | 289.3
1304 | 1144 | 211.5 | 303.4 | 420.8 | 288.9
1305 | 1145 | 211.3 | 302.6 | 419.1 | 288.6
1306 | 1146 | 211.1 | 301.9 | 417.4 | 288.2
1307 | 1147 | 211 | 301.3 | 415.6 | 287.9
1308 | 1148 | 210.8 | 300.6 | 413.9 | 287.5
1309 | 1149 | 210.7 | 299.9 | 412.1 | 287.2
1310 | 1150 | 210.5 | 299.1 | 410.4 | 286.8
1311 | 1151 | 210.3 | 298.5 | 408.7 | 286.4
1312 | 1152 | 210.2 | 297.8 | 407.1 | 286
1313 | 1153 | 210 | 297.1 | 405.4 | 285.7
1314 | 1154 | 209.9 | 296.5 | 403.6 | 285.3
1315 | 1155 | 209.7 | 295.8 | 401.9 | 284.9
1316 | 1156 | 209.6 | 295.1 | 400.2 | 284.5
1317 | 1157 | 209.4 | 294.3 | 398.5 | 284.2
1318 | 1158 | 209.2 | 293.6 | 396.8 | 283.8
1319 | 1159 | 209.1 | 292.9 | 395.2 | 283.4

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 62 |  |  | 2006-08-28 | 13:17
38957.5522 | 1 | 0 | 1 | XLPE | 12-C | Tray
38957.5543 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38957.5565 | 1 | 0 | 1
38957.5586 | 1 | 0 | 1
38957.5608 | 944 | 919 | 1
38957.5629 | 1118 | 1085 | 1
38957.565 | 1370 | 888 | 1
38957.5672 | 1131 | 1099 | 1
1
38957.5522 | 1 | 0 | 2
38957.5544 | 1 | 0 | 2
38957.5565 | 1 | 0 | 2
38957.5586 | 1 | 0 | 2
38957.5608 | 1210 | 1166 | 2
38957.5629 | 1109 | 1155 | 2
38957.5651 | 1476 | 936 | 2
38957.5672 | 990 | 959 | 2
2
38957.5522 | 1 | 0 | 3
38957.5544 | 1 | 0 | 3
38957.5565 | 1 | 0 | 3
38957.5587 | 1 | 0 | 3
38957.5608 | 1121 | 1071 | 3
38957.5629 | 1153 | 924 | 3
38957.5651 | 1114 | 787 | 3
38957.5672 | 1105 | 1072 | 3
3
38957.5523 | 1 | 0 | 4
38957.5544 | 1 | 0 | 4
38957.5565 | 1 | 0 | 4
38957.5587 | 1 | 0 | 4
38957.5608 | 1160 | 1181 | 4
38957.563 | 1120 | 1167 | 4
38957.5651 | 1189 | 757 | 4
38957.5672 | 1190 | 919 | 4
4
38957.5523 | 1 | 0 | 5
38957.5544 | 1 | 0 | 5
38957.5566 | 1 | 0 | 5
38957.5587 | 1 | 0 | 5
38957.5608 | 1129 | 1078 | 5
38957.563 | 1125 | 1169 | 5
38957.5651 | 1327 | 925 | 5
38957.5672 | 1107 | 1073 | 5
5
38957.5523 | 1 | 0 | 6
38957.5544 | 1 | 0 | 6
38957.5566 | 1 | 0 | 6
38957.5587 | 1 | 0 | 6
38957.5608 | 1213 | 1165 | 6
38957.563 | 996 | 1031 | 6
38957.5651 | 1376 | 901 | 6
38957.5673 | 1085 | 1051 | 6
6
38957.5523 | 1 | 0 | 7
38957.5544 | 1 | 0 | 7
38957.5566 | 1 | 0 | 7
38957.5587 | 1 | 0 | 7
38957.5609 | 1078 | 1137 | 7
38957.563 | 1177 | 1146 | 7
38957.5651 | 1248 | 848 | 7
38957.5673 | 1119 | 1085 | 7
7
38957.5523 | 1 | 0 | 8
38957.5545 | 1 | 0 | 8
38957.5566 | 1 | 0 | 8
38957.5587 | 1 | 0 | 8
38957.5609 | 1216 | 1169 | 8
38957.563 | 934 | 964 | 8
38957.5652 | 1101 | 785 | 8
38957.5673 | 1014 | 982 | 8
8
38957.5523 | 1 | 0 | 9
38957.5545 | 1 | 0 | 9
38957.5566 | 1 | 0 | 9
38957.5587 | 1 | 0 | 9
38957.5609 | 1149 | 1161 | 9
38957.563 | 1013 | 980 | 9
38957.5652 | 1566 | 925 | 9
38957.5673 | 958 | 926 | 9
9
38957.5523 | 1 | 0 | 10
38957.5545 | 1 | 0 | 10
38957.5566 | 1 | 0 | 10
38957.5588 | 1 | 0 | 10
38957.5609 | 1142 | 1088 | 10
38957.563 | 1001 | 968 | 10
38957.5652 | 1109 | 912 | 10
38957.5673 | 947 | 919 | 10
10
38957.5524 | 1 | 0 | 11
38957.5545 | 1 | 0 | 11
38957.5566 | 1 | 0 | 11
38957.5588 | 1 | 0 | 11
38957.5609 | 983 | 933 | 11
38957.5631 | 1169 | 1181 | 11
38957.5652 | 1207 | 896 | 11
38957.5673 | 1143 | 1186 | 11
11
38957.5524 | 1 | 0 | 12
38957.5545 | 1 | 0 | 12
38957.5567 | 1 | 0 | 12
38957.5588 | 1 | 0 | 12
38957.5609 | 1089 | 1033 | 12
38957.5631 | 1171 | 1137 | 12
38957.5652 | 1248 | 1009 | 12
38957.5673 | 1027 | 996 | 12
12
38957.5524 | 1 | 0 | 13
38957.5545 | 1 | 0 | 13
38957.5567 | 1 | 0 | 13
38957.5588 | 1 | 0 | 13
38957.5609 | 1015 | 962 | 13
38957.5631 | 1022 | 989 | 13
38957.5652 | 1373 | 658 | 13
38957.5674 | 1102 | 1071 | 13
13
38957.5524 | 1 | 0 | 14
38957.5546 | 1 | 0 | 14
38957.5567 | 1 | 0 | 14
38957.5588 | 1 | 0 | 14
38957.561 | 1060 | 1074 | 14
38957.5631 | 1169 | 1134 | 14
38957.5652 | 1283 | 1116 | 14
38957.5674 | 1075 | 1043 | 14
14
38957.5524 | 1 | 0 | 15
38957.5546 | 1 | 0 | 15
38957.5567 | 1 | 0 | 15
38957.5588 | 1 | 0 | 15
38957.561 | 1184 | 1124 | 15
38957.5631 | 1065 | 1102 | 15
38957.5653 | 1105 | 883 | 15
38957.5674 | 977 | 918 | 15
15
38957.5525 | 1 | 0 | 16
38957.5546 | 1 | 0 | 16
38957.5567 | 1 | 0 | 16
38957.5589 | 1 | 0 | 16
38957.561 | 947 | 954 | 16
38957.5631 | 1208 | 1025 | 16
38957.5653 | 1147 | 889 | 16
38957.5674 | 1102 | 1144 | 16
16
38957.5525 | 1 | 0 | 17
38957.5546 | 1 | 0 | 17
38957.5567 | 1 | 0 | 17
38957.5589 | 1 | 0 | 17
38957.561 | 974 | 978 | 17
38957.5632 | 1192 | 1189 | 17
38957.5653 | 1185 | 1101 | 17
38957.5674 | 999 | 1031 | 17
17
38957.5525 | 1 | 0 | 18
38957.5546 | 1 | 0 | 18
38957.5568 | 1 | 0 | 18
38957.5589 | 1 | 0 | 18
38957.561 | 1074 | 1012 | 18
38957.5632 | 1100 | 1157 | 18
38957.5653 | 1224 | 1070 | 18
38957.5675 | 1186 | 1154 | 18
18
38957.5525 | 1 | 0 | 19
38957.5546 | 1 | 0 | 19
38957.5568 | 1 | 0 | 19
38957.5589 | 1 | 0 | 19
38957.5611 | 1207 | 1141 | 19
38957.5632 | 1120 | 1077 | 19
38957.5653 | 998 | 871 | 19
38957.5675 | 989 | 1095 | 19
19
38957.5525 | 1 | 0 | 20
38957.5547 | 1 | 0 | 20
38957.5568 | 1 | 0 | 20
38957.5589 | 1 | 0 | 20
38957.5611 | 1213 | 904 | 20
38957.5632 | 1135 | 1169 | 20
38957.5653 | 1289 | 954 | 20
38957.5675 | 1066 | 1147 | 20
20
38957.5525 | 1 | 0 | 21
38957.5547 | 1 | 0 | 21
38957.5568 | 1 | 0 | 21
38957.5589 | 1 | 0 | 21
38957.5611 | 948 | 977 | 21
38957.5632 | 1174 | 1111 | 21
38957.5654 | 1014 | 877 | 21
38957.5675 | 1205 | 1195 | 21
21
38957.5525 | 1 | 0 | 22
38957.5547 | 1 | 0 | 22
38957.5568 | 1 | 0 | 22
38957.559 | 1 | 0 | 22
38957.5611 | 1006 | 1008 | 22
38957.5632 | 1043 | 1007 | 22
38957.5654 | 1170 | 926 | 22
38957.5675 | 951 | 956 | 22
22
38957.5526 | 1 | 0 | 23
38957.5547 | 1 | 0 | 23
38957.5568 | 1 | 0 | 23
38957.559 | 1 | 0 | 23
38957.5611 | 984 | 919 | 23
38957.5633 | 1039 | 1073 | 23
38957.5654 | 1185 | 1029 | 23
38957.5675 | 1196 | 922 | 23
23
38957.5526 | 1 | 0 | 24
38957.5547 | 1 | 0 | 24
38957.5569 | 1 | 0 | 24
38957.559 | 1 | 0 | 24
38957.5611 | 1038 | 966 | 24
38957.5633 | 951 | 948 | 24
38957.5654 | 1196 | 1104 | 24
38957.5675 | 988 | 960 | 24
24
38957.5526 | 1 | 0 | 25
38957.5547 | 1 | 0 | 25
38957.5569 | 1 | 0 | 25
38957.559 | 1 | 0 | 25
38957.5611 | 1207 | 1127 | 25
38957.5633 | 1052 | 1014 | 25
38957.5654 | 1097 | 961 | 25
38957.5676 | 965 | 936 | 25
25
38957.5526 | 1 | 0 | 26
38957.5547 | 1 | 0 | 26
38957.5569 | 1 | 0 | 26
38957.559 | 1 | 0 | 26
38957.5612 | 1171 | 1159 | 26
38957.5633 | 1209 | 1175 | 26
38957.5654 | 1118 | 977 | 26
38957.5676 | 957 | 926 | 26
26
38957.5526 | 1 | 0 | 27
38957.5548 | 1 | 0 | 27
38957.5569 | 1 | 0 | 27
38957.559 | 1 | 0 | 27
38957.5612 | 1221 | 1142 | 27
38957.5633 | 954 | 975 | 27
38957.5655 | 1238 | 1086 | 27
38957.5676 | 1175 | 923 | 27
27
38957.5526 | 1 | 0 | 28
38957.5548 | 1 | 0 | 28
38957.5569 | 1 | 0 | 28
38957.5591 | 1 | 0 | 28
38957.5612 | 1141 | 1066 | 28
38957.5633 | 1192 | 1152 | 28
38957.5655 | 1039 | 888 | 28
38957.5676 | 981 | 973 | 28
28
38957.5527 | 1 | 0 | 29
38957.5548 | 1 | 0 | 29
38957.5569 | 1 | 0 | 29
38957.5591 | 1 | 0 | 29
38957.5612 | 1216 | 1152 | 29
38957.5634 | 959 | 979 | 29
38957.5655 | 1087 | 950 | 29
38957.5676 | 967 | 940 | 29
29
38957.5527 | 1 | 0 | 30
38957.5548 | 1 | 0 | 30
38957.557 | 1 | 0 | 30
38957.5591 | 1 | 0 | 30
38957.5612 | 983 | 910 | 30
38957.5634 | 1090 | 1042 | 30
38957.5655 | 1121 | 889 | 30
38957.5677 | 973 | 1007 | 30
30
38957.5527 | 1 | 0 | 31
38957.5548 | 1 | 0 | 31
38957.557 | 1 | 0 | 31
38957.5591 | 1 | 0 | 31
38957.5612 | 1034 | 1022 | 31
38957.5634 | 969 | 882 | 31
38957.5655 | 1266 | 1120 | 31
38957.5677 | 981 | 954 | 31
31
38957.5527 | 1 | 0 | 32
38957.5548 | 1 | 0 | 32
38957.557 | 1 | 0 | 32
38957.5591 | 1 | 0 | 32
38957.5613 | 1055 | 974 | 32
38957.5634 | 1014 | 927 | 32
38957.5655 | 1227 | 1121 | 32
38957.5677 | 932 | 961 | 32
32
38957.5527 | 1 | 0 | 33
38957.5549 | 1 | 0 | 33
38957.557 | 1 | 0 | 33
38957.5591 | 1 | 0 | 33
38957.5613 | 1044 | 1029 | 33
38957.5634 | 1147 | 1177 | 33
38957.5656 | 1243 | 1086 | 33
38957.5677 | 1049 | 1019 | 33
33
38957.5527 | 1 | 0 | 34
38957.5549 | 1 | 0 | 34
38957.557 | 1 | 0 | 34
38957.5592 | 1 | 0 | 34
38957.5613 | 1202 | 1109 | 34
38957.5634 | 1135 | 1171 | 34
38957.5656 | 1097 | 1015 | 34
38957.5677 | 1006 | 979 | 34
34
38957.5528 | 1 | 0 | 35
38957.5549 | 1 | 0 | 35
38957.557 | 1 | 0 | 35
38957.5592 | 1 | 0 | 35
38957.5613 | 1132 | 1130 | 35
38957.5634 | 1182 | 1186 | 35
38957.5656 | 1230 | 995 | 35
38957.5677 | 1087 | 1059 | 35
35
38957.5528 | 1 | 0 | 36
38957.5549 | 1 | 0 | 36
38957.557 | 1 | 0 | 36
38957.5592 | 1 | 0 | 36
38957.5613 | 1149 | 1049 | 36
38957.5635 | 1101 | 1129 | 36
38957.5656 | 1242 | 1105 | 36
38957.5677 | 1090 | 1064 | 36
36
38957.5528 | 1 | 0 | 37
38957.5549 | 2 | 0 | 37
38957.5571 | 1 | 0 | 37
38957.5592 | 1 | 0 | 37
38957.5613 | 1243 | 1134 | 37
38957.5635 | 936 | 954 | 37
38957.5656 | 976 | 917 | 37
38957.5678 | 1008 | 1050 | 37
37
38957.5528 | 1 | 0 | 38
38957.5549 | 1 | 0 | 38
38957.5571 | 1 | 0 | 38
38957.5592 | 1 | 0 | 38
38957.5614 | 1101 | 992 | 38
38957.5635 | 1147 | 1162 | 38
38957.5656 | 1012 | 896 | 38
38957.5678 | 1125 | 1097 | 38
38
38957.5528 | 1 | 0 | 39
38957.555 | 1 | 0 | 39
38957.5571 | 1 | 0 | 39
38957.5592 | 1 | 0 | 39
38957.5614 | 1008 | 980 | 39
38957.5635 | 941 | 937 | 39
38957.5656 | 1094 | 919 | 39
38957.5678 | 1041 | 1086 | 39
39
38957.5528 | 1 | 0 | 40
38957.555 | 1 | 0 | 40
38957.5571 | 1 | 0 | 40
38957.5592 | 1 | 0 | 40
38957.5614 | 1154 | 1051 | 40
38957.5635 | 1196 | 1124 | 40
38957.5657 | 1047 | 858 | 40
38957.5678 | 1121 | 1174 | 40
40
38957.5529 | 1 | 0 | 41
38957.555 | 2 | 0 | 41
38957.5571 | 1 | 0 | 41
38957.5593 | 1 | 0 | 41
38957.5614 | 1023 | 929 | 41
38957.5635 | 1103 | 1046 | 41
38957.5657 | 1313 | 1056 | 41
38957.5678 | 1154 | 1126 | 41
41
38957.5529 | 1 | 0 | 42
38957.555 | 1 | 0 | 42
38957.5571 | 1 | 0 | 42
38957.5593 | 1 | 0 | 42
38957.5614 | 1065 | 1077 | 42
38957.5636 | 1094 | 1048 | 42
38957.5657 | 1312 | 995 | 42
38957.5678 | 952 | 928 | 42
42
38957.5529 | 1 | 0 | 43
38957.555 | 1 | 0 | 43
38957.5572 | 1 | 0 | 43
38957.5593 | 1 | 0 | 43
38957.5614 | 1022 | 928 | 43
38957.5636 | 1171 | 1121 | 43
38957.5657 | 1209 | 952 | 43
38957.5679 | 1103 | 1076 | 43
43
38957.5529 | 1 | 0 | 44
38957.555 | 1 | 0 | 44
38957.5572 | 1 | 0 | 44
38957.5593 | 1 | 0 | 44
38957.5615 | 1241 | 1144 | 44
38957.5636 | 1175 | 1186 | 44
38957.5657 | 1227 | 932 | 44
38957.5679 | 1036 | 1080 | 44
44
38957.5529 | 1 | 0 | 45
38957.5551 | 1 | 0 | 45
38957.5572 | 1 | 0 | 45
38957.5593 | 1 | 0 | 45
38957.5615 | 1220 | 1089 | 45
38957.5636 | 980 | 936 | 45
38957.5658 | 1268 | 1082 | 45
38957.5679 | 1058 | 1032 | 45
45
38957.5529 | 1 | 0 | 46
38957.5551 | 1 | 0 | 46
38957.5572 | 1 | 0 | 46
38957.5594 | 1 | 0 | 46
38957.5615 | 1121 | 1061 | 46
38957.5636 | 1104 | 926 | 46
38957.5658 | 1282 | 1063 | 46
38957.5679 | 1130 | 1104 | 46
46
38957.553 | 1 | 0 | 47
38957.5551 | 1 | 0 | 47
38957.5572 | 1 | 0 | 47
38957.5594 | 1 | 0 | 47
38957.5615 | 980 | 913 | 47
38957.5636 | 1053 | 940 | 47
38957.5658 | 1236 | 906 | 47
38957.5679 | 1095 | 1069 | 47
47
38957.553 | 1 | 0 | 48
38957.5551 | 1 | 0 | 48
38957.5572 | 1 | 0 | 48
38957.5594 | 1 | 0 | 48
38957.5615 | 1046 | 994 | 48
38957.5637 | 948 | 951 | 48
38957.5658 | 1278 | 1086 | 48
38957.5679 | 1126 | 1099 | 48
48
38957.553 | 1 | 0 | 49
38957.5551 | 1 | 0 | 49
38957.5573 | 1 | 0 | 49
38957.5594 | 1 | 0 | 49
38957.5615 | 1052 | 922 | 49
38957.5637 | 989 | 908 | 49
38957.5658 | 1183 | 941 | 49
38957.568 | 1169 | 1144 | 49
49
38957.553 | 1 | 0 | 50
38957.5551 | 1 | 0 | 50
38957.5573 | 1 | 0 | 50
38957.5594 | 1 | 0 | 50
38957.5616 | 1263 | 1099 | 50
38957.5637 | 1092 | 1050 | 50
38957.5658 | 1294 | 1098 | 50
38957.568 | 958 | 1073 | 50
50
38957.553 | 1 | 0 | 51
38957.5552 | 1 | 0 | 51
38957.5573 | 1 | 0 | 51
38957.5594 | 1 | 0 | 51
38957.5616 | 1182 | 1047 | 51
38957.5637 | 1224 | 711 | 51
38957.5658 | 1140 | 1041 | 51
38957.568 | 992 | 1104 | 51
51
38957.553 | 1 | 0 | 52
38957.5552 | 1 | 0 | 52
38957.5573 | 1 | 0 | 52
38957.5594 | 1 | 0 | 52
38957.5616 | 1086 | 880 | 52
38957.5637 | 1730 | 421 | 52
38957.5659 | 1226 | 1133 | 52
38957.568 | 938 | 974 | 52
52
38957.553 | 1 | 0 | 53
38957.5552 | 1 | 0 | 53
38957.5573 | 1 | 0 | 53
38957.5595 | 1 | 0 | 53
38957.5616 | 1101 | 1098 | 53
38957.5637 | 1449 | 555 | 53
38957.5659 | 1052 | 907 | 53
38957.568 | 963 | 1081 | 53
53
38957.5531 | 1 | 0 | 54
38957.5552 | 1 | 0 | 54
38957.5573 | 1 | 0 | 54
38957.5595 | 1 | 0 | 54
38957.5616 | 1213 | 1181 | 54
38957.5638 | 1653 | 456 | 54
38957.5659 | 1122 | 1007 | 54
38957.568 | 1194 | 926 | 54
54
38957.5531 | 1 | 0 | 55
38957.5552 | 1 | 0 | 55
38957.5574 | 1 | 0 | 55
38957.5595 | 1 | 0 | 55
38957.5616 | 957 | 909 | 55
38957.5638 | 1937 | 465 | 55
38957.5659 | 1156 | 1116 | 55
38957.5681 | 936 | 972 | 55
55
38957.5531 | 1 | 0 | 56
38957.5552 | 1 | 0 | 56
38957.5574 | 1 | 0 | 56
38957.5595 | 1 | 0 | 56
38957.5617 | 1180 | 1127 | 56
38957.5638 | 1577 | 601 | 56
38957.5659 | 1264 | 1128 | 56
38957.5681 | 969 | 1086 | 56
56
38957.5531 | 1 | 0 | 57
38957.5553 | 1 | 0 | 57
38957.5574 | 1 | 0 | 57
38957.5595 | 1 | 0 | 57
38957.5617 | 953 | 908 | 57
38957.5638 | 1429 | 518 | 57
38957.5659 | 1062 | 1068 | 57
38957.5681 | 1203 | 960 | 57
57
38957.5531 | 1 | 0 | 58
38957.5553 | 1 | 0 | 58
38957.5574 | 1 | 0 | 58
38957.5595 | 1 | 0 | 58
38957.5617 | 971 | 924 | 58
38957.5638 | 1530 | 447 | 58
38957.566 | 1110 | 1006 | 58
38957.5681 | 1194 | 1173 | 58
58
38957.5531 | 1 | 0 | 59
38957.5553 | 1 | 0 | 59
38957.5574 | 1 | 0 | 59
38957.5596 | 1 | 0 | 59
38957.5617 | 1016 | 1034 | 59
38957.5638 | 1856 | 538 | 59
38957.566 | 1045 | 938 | 59
38957.5681 | 961 | 1076 | 59
59
38957.5532 | 1 | 0 | 60
38957.5553 | 1 | 0 | 60
38957.5574 | 1 | 0 | 60
38957.5596 | 1 | 0 | 60
38957.5617 | 1161 | 916 | 60
38957.5639 | 1269 | 667 | 60
38957.566 | 1040 | 1069 | 60
38957.5681 | 1196 | 943 | 60
60
38957.5532 | 1 | 0 | 61
38957.5553 | 1 | 0 | 61
38957.5575 | 1 | 0 | 61
38957.5596 | 1 | 0 | 61
38957.5617 | 1008 | 960 | 61
38957.5639 | 1276 | 734 | 61
38957.566 | 1003 | 916 | 61
38957.5681 | 1190 | 1167 | 61
61
38957.5532 | 1 | 0 | 62
38957.5553 | 1 | 0 | 62
38957.5575 | 1 | 0 | 62
38957.5596 | 1 | 0 | 62
38957.5617 | 946 | 1030 | 62
38957.5639 | 1150 | 755 | 62
38957.566 | 1019 | 934 | 62
38957.5682 | 1159 | 1136 | 62
62
38957.5532 | 1 | 0 | 63
38957.5553 | 1 | 0 | 63
38957.5575 | 1 | 0 | 63
38957.5596 | 1 | 0 | 63
38957.5618 | 1185 | 1151 | 63
38957.5639 | 1309 | 836 | 63
38957.566 | 1182 | 1087 | 63
38957.5682 | 1043 | 1140 | 63
63
38957.5532 | 1 | 0 | 64
38957.5554 | 1 | 0 | 64
38957.5575 | 1 | 0 | 64
38957.5596 | 1 | 0 | 64
38957.5618 | 1053 | 1006 | 64
38957.5639 | 1292 | 856 | 64
38957.5661 | 1095 | 981 | 64
38957.5682 | 1159 | 1196 | 64
64
38957.5532 | 1 | 0 | 65
38957.5554 | 1 | 0 | 65
38957.5575 | 1 | 0 | 65
38957.5597 | 1 | 0 | 65
38957.5618 | 1167 | 1183 | 65
38957.5639 | 1432 | 706 | 65
38957.5661 | 1100 | 1002 | 65
38957.5682 | 1164 | 1140 | 65
65
38957.5533 | 1 | 0 | 66
38957.5554 | 1 | 0 | 66
38957.5575 | 1 | 0 | 66
38957.5597 | 1 | 0 | 66
38957.5618 | 1085 | 1054 | 66
38957.5639 | 1461 | 917 | 66
38957.5661 | 1030 | 929 | 66
38957.5682 | 1116 | 1169 | 66
66
38957.5533 | 1 | 0 | 67
38957.5554 | 1 | 0 | 67
38957.5575 | 1 | 0 | 67
38957.5597 | 1 | 0 | 67
38957.5618 | 1040 | 1011 | 67
38957.564 | 1280 | 743 | 67
38957.5661 | 1080 | 1065 | 67
38957.5682 | 1191 | 1143 | 67
67
38957.5533 | 1 | 0 | 68
38957.5554 | 1 | 0 | 68
38957.5576 | 1 | 0 | 68
38957.5597 | 1 | 0 | 68
38957.5618 | 980 | 952 | 68
38957.564 | 1227 | 833 | 68
38957.5661 | 1007 | 918 | 68
38957.5683 | 1186 | 1163 | 68
68
38957.5533 | 1 | 0 | 69
38957.5554 | 1 | 0 | 69
38957.5576 | 1 | 0 | 69
38957.5597 | 1 | 0 | 69
38957.5619 | 1204 | 1076 | 69
38957.564 | 1252 | 785 | 69
38957.5661 | 1135 | 1137 | 69
38957.5683 | 1169 | 1145 | 69
69
38957.5533 | 1 | 0 | 70
38957.5555 | 1 | 0 | 70
38957.5576 | 1 | 0 | 70
38957.5597 | 1 | 0 | 70
38957.5619 | 1187 | 1156 | 70
38957.564 | 1605 | 794 | 70
38957.5662 | 981 | 904 | 70
38957.5683 | 1120 | 1095 | 70
70
38957.5533 | 1 | 0 | 71
38957.5555 | 1 | 0 | 71
38957.5576 | 1 | 0 | 71
38957.5598 | 1 | 0 | 71
38957.5619 | 934 | 965 | 71
38957.564 | 1196 | 726 | 71
38957.5662 | 1180 | 1091 | 71
38957.5683 | 1196 | 1196 | 71
71
38957.5534 | 1 | 0 | 72
38957.5555 | 1 | 0 | 72
38957.5576 | 1 | 0 | 72
38957.5598 | 1 | 0 | 72
38957.5619 | 974 | 944 | 72
38957.5641 | 1479 | 902 | 72
38957.5662 | 1102 | 1018 | 72
38957.5683 | 1163 | 1196 | 72
72
38957.5534 | 1 | 0 | 73
38957.5555 | 1 | 0 | 73
38957.5577 | 1 | 0 | 73
38957.5598 | 1 | 0 | 73
38957.5619 | 1074 | 1042 | 73
38957.5641 | 1389 | 774 | 73
38957.5662 | 1217 | 1131 | 73
38957.5683 | 1173 | 1150 | 73
73
38957.5534 | 1 | 0 | 74
38957.5555 | 1 | 0 | 74
38957.5577 | 1 | 0 | 74
38957.5598 | 1 | 0 | 74
38957.5619 | 1151 | 1191 | 74
38957.5641 | 1394 | 722 | 74
38957.5662 | 1007 | 1059 | 74
38957.5684 | 1119 | 1094 | 74
74
38957.5534 | 1 | 0 | 75
38957.5555 | 1 | 0 | 75
38957.5577 | 1 | 0 | 75
38957.5598 | 1 | 0 | 75
38957.562 | 1032 | 1002 | 75
38957.5641 | 1597 | 730 | 75
38957.5662 | 1044 | 968 | 75
38957.5684 | 1099 | 1075 | 75
75
38957.5534 | 1 | 0 | 76
38957.5556 | 1 | 0 | 76
38957.5577 | 1 | 0 | 76
38957.5598 | 1 | 0 | 76
38957.562 | 1017 | 987 | 76
38957.5641 | 1651 | 825 | 76
38957.5663 | 1039 | 964 | 76
38957.5684 | 1169 | 1146 | 76
76
38957.5534 | 1 | 0 | 77
38957.5556 | 1 | 0 | 77
38957.5577 | 1 | 0 | 77
38957.5598 | 1 | 0 | 77
38957.562 | 1038 | 1007 | 77
38957.5641 | 1485 | 802 | 77
38957.5663 | 1204 | 1125 | 77
38957.5684 | 1155 | 1132 | 77
77
38957.5534 | 1 | 0 | 78
38957.5556 | 1 | 0 | 78
38957.5577 | 1 | 0 | 78
38957.5599 | 1 | 0 | 78
38957.562 | 1032 | 1071 | 78
38957.5641 | 1206 | 690 | 78
38957.5663 | 971 | 938 | 78
38957.5684 | 1199 | 1179 | 78
78
38957.5535 | 1 | 0 | 79
38957.5556 | 1 | 0 | 79
38957.5577 | 1 | 0 | 79
38957.5599 | 1 | 0 | 79
38957.562 | 1177 | 1176 | 79
38957.5642 | 1205 | 668 | 79
38957.5663 | 1085 | 1016 | 79
38957.5684 | 1196 | 1199 | 79
79
38957.5535 | 1 | 0 | 80
38957.5556 | 1 | 0 | 80
38957.5578 | 1 | 0 | 80
38957.5599 | 1 | 0 | 80
38957.562 | 1146 | 1113 | 80
38957.5642 | 1662 | 641 | 80
38957.5663 | 992 | 992 | 80
38957.5685 | 1027 | 949 | 80
80
38957.5535 | 1 | 0 | 81
38957.5556 | 1 | 0 | 81
38957.5578 | 1 | 0 | 81
38957.5599 | 1 | 0 | 81
38957.5621 | 948 | 919 | 81
38957.5642 | 1940 | 429 | 81
38957.5663 | 1194 | 1120 | 81
38957.5685 | 996 | 1038 | 81
81
38957.5535 | 1 | 0 | 82
38957.5557 | 1 | 0 | 82
38957.5578 | 1 | 0 | 82
38957.5599 | 1 | 0 | 82
38957.5621 | 943 | 923 | 82
38957.5642 | 1318 | 576 | 82
38957.5664 | 957 | 914 | 82
38957.5685 | 1012 | 989 | 82
82
38957.5535 | 1 | 0 | 83
38957.5557 | 1 | 0 | 83
38957.5578 | 1 | 0 | 83
38957.56 | 1 | 0 | 83
38957.5621 | 1206 | 1184 | 83
38957.5642 | 1905 | 148 | 83
38957.5664 | 949 | 976 | 83
38957.5685 | 1019 | 1064 | 83
83
38957.5536 | 1 | 0 | 84
38957.5557 | 1 | 0 | 84
38957.5578 | 1 | 0 | 84
38957.56 | 1 | 0 | 84
38957.5621 | 1070 | 1041 | 84
38957.5642 | 2035 | 130 | 84
38957.5664 | 1146 | 1157 | 84
38957.5685 | 1092 | 1068 | 84
84
38957.5536 | 1 | 0 | 85
38957.5557 | 1 | 0 | 85
38957.5578 | 1 | 0 | 85
38957.56 | 1 | 0 | 85
38957.5621 | 1008 | 978 | 85
38957.5643 | 2242 | 111 | 85
38957.5664 | 1143 | 1152 | 85
38957.5685 | 1022 | 1066 | 85
85
38957.5536 | 2 | 0 | 86
38957.5557 | 1 | 0 | 86
38957.5579 | 1 | 0 | 86
38957.56 | 1 | 0 | 86
38957.5621 | 1051 | 1023 | 86
38957.5643 | 2287 | 71 | 86
38957.5664 | 1025 | 947 | 86
38957.5686 | 984 | 1024 | 86
86
38957.5536 | 1 | 0 | 87
38957.5557 | 1 | 0 | 87
38957.5579 | 1 | 0 | 87
38957.56 | 1 | 0 | 87
38957.5622 | 1183 | 1154 | 87
38957.5643 | 1996 | 80 | 87
38957.5664 | 1117 | 1049 | 87
38957.5686 | 962 | 940 | 87
87
38957.5536 | 1 | 0 | 88
38957.5558 | 1 | 0 | 88
38957.5579 | 1 | 0 | 88
38957.56 | 1 | 0 | 88
38957.5622 | 1098 | 1068 | 88
38957.5643 | 1913 | 103 | 88
38957.5686 | 933 | 970 | 88
88
38957.5536 | 1 | 0 | 89
38957.5558 | 1 | 0 | 89
38957.5579 | 1 | 0 | 89
38957.56 | 1 | 0 | 89
38957.5622 | 1153 | 1123 | 89
38957.5643 | 2189 | 88 | 89
38957.5665 | 1117 | 1057 | 89
38957.5686 | 1038 | 1084 | 89
89
38957.5536 | 1 | 0 | 90
38957.5558 | 1 | 0 | 90
38957.5579 | 1 | 0 | 90
38957.5601 | 1 | 0 | 90
38957.5622 | 1080 | 1050 | 90
38957.5643 | 2375 | 49 | 90
38957.5665 | 991 | 938 | 90
38957.5686 | 1120 | 1094 | 90
90
38957.5537 | 1 | 0 | 91
38957.5558 | 1 | 0 | 91
38957.5579 | 1 | 0 | 91
38957.5601 | 1 | 0 | 91
38957.5622 | 1006 | 977 | 91
38957.5644 | 2366 | 33 | 91
38957.5665 | 1055 | 998 | 91
38957.5686 | 1106 | 1082 | 91
91
38957.5537 | 1 | 0 | 92
38957.5558 | 1 | 0 | 92
38957.558 | 1 | 0 | 92
38957.5601 | 1 | 0 | 92
38957.5622 | 1005 | 1045 | 92
38957.5644 | 1933 | 29 | 92
38957.5665 | 1176 | 1066 | 92
38957.5686 | 1058 | 1033 | 92
92
38957.5537 | 1 | 0 | 93
38957.5558 | 1 | 0 | 93
38957.558 | 1 | 0 | 93
38957.5601 | 1 | 0 | 93
38957.5622 | 1084 | 1056 | 93
38957.5644 | 2153 | 25 | 93
38957.5665 | 1209 | 1156 | 93
38957.5687 | 1159 | 1200 | 93
93
38957.5537 | 1 | 0 | 94
38957.5559 | 1 | 0 | 94
38957.558 | 1 | 0 | 94
38957.5601 | 1 | 0 | 94
38957.5623 | 1092 | 1062 | 94
38957.5644 | 1968 | 24 | 94
38957.5665 | 1190 | 1036 | 94
38957.5687 | 1184 | 1160 | 94
94
38957.5537 | 1 | 0 | 95
38957.5559 | 1 | 0 | 95
38957.558 | 1 | 0 | 95
38957.5601 | 1 | 0 | 95
38957.5623 | 1191 | 1166 | 95
38957.5644 | 2276 | 29 | 95
38957.5666 | 1245 | 1134 | 95
38957.5687 | 1189 | 1200 | 95
95
38957.5537 | 1 | 0 | 96
38957.5559 | 1 | 0 | 96
38957.558 | 1 | 0 | 96
38957.5602 | 1 | 0 | 96
38957.5623 | 978 | 951 | 96
38957.5644 | 1925 | 23 | 96
38957.5666 | 1096 | 1110 | 96
38957.5687 | 1181 | 1158 | 96
96
38957.5538 | 1 | 0 | 97
38957.5559 | 1 | 0 | 97
38957.558 | 1 | 0 | 97
38957.5602 | 1 | 0 | 97
38957.5623 | 1139 | 1108 | 97
38957.5645 | 1983 | 24 | 97
38957.5666 | 1207 | 1154 | 97
38957.5687 | 1196 | 1177 | 97
97
38957.5538 | 1 | 0 | 98
38957.5559 | 1 | 0 | 98
38957.5581 | 1 | 0 | 98
38957.5602 | 1 | 0 | 98
38957.5623 | 969 | 947 | 98
38957.5645 | 2058 | 24 | 98
38957.5666 | 1180 | 1125 | 98
38957.5687 | 1109 | 1162 | 98
98
38957.5538 | 1 | 0 | 99
38957.5559 | 1 | 0 | 99
38957.5581 | 1 | 0 | 99
38957.5602 | 6 | 2 | 99
38957.5623 | 1160 | 1186 | 99
38957.5645 | 1971 | 24 | 99
38957.5666 | 946 | 945 | 99
38957.5688 | 1061 | 1147 | 99
99
38957.5538 | 1 | 0 | 100
38957.5559 | 1 | 0 | 100
38957.5581 | 1 | 0 | 100
38957.5602 | 31 | 26 | 100
38957.5624 | 971 | 945 | 100
38957.5645 | 2103 | 26 | 100
38957.5666 | 974 | 902 | 100
38957.5688 | 706 | 689 | 100
100
38957.5538 | 1 | 0 | 101
38957.556 | 1 | 0 | 101
38957.5581 | 1 | 0 | 101
38957.5602 | 21 | 13 | 101
38957.5624 | 1021 | 1116 | 101
38957.5645 | 2083 | 27 | 101
38957.5667 | 1087 | 1039 | 101
38957.5688 | 987 | 965 | 101
101
38957.5538 | 1 | 0 | 102
38957.556 | 1 | 0 | 102
38957.5581 | 1 | 0 | 102
38957.5603 | 102 | 87 | 102
38957.5624 | 968 | 1003 | 102
38957.5645 | 1888 | 25 | 102
38957.5667 | 1204 | 1159 | 102
38957.5688 | 1027 | 1003 | 102
102
38957.5539 | 1 | 0 | 103
38957.556 | 1 | 0 | 103
38957.5581 | 1 | 0 | 103
38957.5603 | 93 | 80 | 103
38957.5624 | 1183 | 914 | 103
38957.5645 | 2373 | 33 | 103
38957.5667 | 1090 | 1120 | 103
38957.5688 | 977 | 1017 | 103
103
38957.5539 | 1 | 0 | 104
38957.556 | 1 | 0 | 104
38957.5581 | 1 | 0 | 104
38957.5603 | 167 | 146 | 104
38957.5624 | 1151 | 1121 | 104
38957.5646 | 1904 | 27 | 104
38957.5667 | 1052 | 1009 | 104
38957.5688 | 987 | 964 | 104
104
38957.5539 | 1 | 0 | 105
38957.556 | 1 | 0 | 105
38957.5582 | 1 | 0 | 105
38957.5603 | 343 | 334 | 105
38957.5624 | 1024 | 995 | 105
38957.5646 | 2358 | 36 | 105
38957.5667 | 962 | 981 | 105
38957.5689 | 1033 | 1009 | 105
105
38957.5539 | 1 | 0 | 106
38957.556 | 1 | 0 | 106
38957.5582 | 1 | 0 | 106
38957.5603 | 133 | 119 | 106
38957.5625 | 1112 | 1082 | 106
38957.5646 | 2005 | 30 | 106
38957.5667 | 1092 | 1150 | 106
38957.5689 | 985 | 1028 | 106
106
38957.5539 | 1 | 0 | 107
38957.5561 | 1 | 0 | 107
38957.5582 | 1 | 0 | 107
38957.5603 | 902 | 994 | 107
38957.5625 | 1188 | 1108 | 107
38957.5646 | 2153 | 34 | 107
38957.5668 | 1012 | 970 | 107
38957.5689 | 947 | 985 | 107
107
38957.5539 | 1 | 0 | 108
38957.5561 | 1 | 0 | 108
38957.5582 | 1 | 0 | 108
38957.5604 | 908 | 875 | 108
38957.5625 | 964 | 937 | 108
38957.5646 | 2280 | 37 | 108
38957.5668 | 1024 | 1050 | 108
38957.5689 | 947 | 959 | 108
108
38957.554 | 1 | 0 | 109
38957.5561 | 1 | 0 | 109
38957.5582 | 1 | 0 | 109
38957.5604 | 1145 | 1118 | 109
38957.5625 | 944 | 1051 | 109
38957.5647 | 2098 | 38 | 109
38957.5668 | 1021 | 1050 | 109
38957.5689 | 992 | 1037 | 109
109
38957.554 | 1 | 0 | 110
38957.5561 | 1 | 1 | 110
38957.5583 | 1 | 0 | 110
38957.5604 | 250 | 221 | 110
38957.5625 | 1017 | 987 | 110
38957.5647 | 1989 | 37 | 110
38957.5668 | 1061 | 1020 | 110
38957.5689 | 975 | 953 | 110
110
38957.554 | 1 | 0 | 111
38957.5561 | 1 | 0 | 111
38957.5583 | 1 | 0 | 111
38957.5604 | 98 | 330 | 111
38957.5625 | 1180 | 1189 | 111
38957.5647 | 2173 | 46 | 111
38957.5668 | 1009 | 967 | 111
38957.569 | 1094 | 1070 | 111
111
38957.554 | 1 | 0 | 112
38957.5561 | 1 | 0 | 112
38957.5583 | 1 | 0 | 112
38957.5604 | 116 | 111 | 112
38957.5626 | 961 | 994 | 112
38957.5647 | 2310 | 55 | 112
38957.5668 | 951 | 914 | 112
38957.569 | 1024 | 1070 | 112
112
38957.554 | 1 | 0 | 113
38957.5562 | 1 | 0 | 113
38957.5583 | 1 | 0 | 113
38957.5604 | 26 | 14 | 113
38957.5626 | 1042 | 1085 | 113
38957.5647 | 2249 | 76 | 113
38957.5669 | 979 | 942 | 113
38957.569 | 1111 | 1086 | 113
113
38957.554 | 1 | 0 | 114
38957.5562 | 1 | 0 | 114
38957.5583 | 1 | 0 | 114
38957.5605 | 507 | 509 | 114
38957.5626 | 1088 | 1057 | 114
38957.5647 | 1805 | 81 | 114
38957.5669 | 1048 | 1007 | 114
38957.569 | 1106 | 1082 | 114
114
38957.5541 | 1 | 0 | 115
38957.5562 | 1 | 0 | 115
38957.5583 | 1 | 0 | 115
38957.5605 | 946 | 907 | 115
38957.5626 | 1194 | 1128 | 115
38957.5647 | 1969 | 112 | 115
38957.5669 | 979 | 1005 | 115
38957.569 | 1089 | 1066 | 115
115
38957.5541 | 1 | 0 | 116
38957.5562 | 1 | 0 | 116
38957.5583 | 1 | 0 | 116
38957.5605 | 1046 | 1007 | 116
38957.5626 | 986 | 959 | 116
38957.5648 | 2134 | 155 | 116
38957.5669 | 1208 | 1172 | 116
38957.569 | 1121 | 1096 | 116
116
38957.5541 | 1 | 0 | 117
38957.5562 | 1 | 0 | 117
38957.5584 | 1 | 0 | 117
38957.5605 | 939 | 901 | 117
38957.5626 | 1104 | 1076 | 117
38957.5648 | 2227 | 168 | 117
38957.5669 | 943 | 952 | 117
38957.5691 | 1190 | 1154 | 117
117
38957.5541 | 1 | 0 | 118
38957.5562 | 1 | 0 | 118
38957.5584 | 1 | 0 | 118
38957.5605 | 831 | 864 | 118
38957.5627 | 1094 | 1065 | 118
38957.5648 | 1748 | 160 | 118
38957.5669 | 1060 | 1020 | 118
38957.5691 | 1068 | 1045 | 118
118
38957.5541 | 1 | 0 | 119
38957.5563 | 1 | 0 | 119
38957.5584 | 1 | 0 | 119
38957.5605 | 1129 | 1087 | 119
38957.5627 | 1199 | 1193 | 119
38957.5648 | 1722 | 684 | 119
38957.5669 | 1102 | 1064 | 119
38957.5691 | 977 | 954 | 119
119
38957.5541 | 1 | 0 | 120
38957.5563 | 1 | 0 | 120
38957.5584 | 1 | 0 | 120
38957.5605 | 1166 | 1125 | 120
38957.5627 | 949 | 921 | 120
38957.5648 | 1585 | 664 | 120
38957.567 | 1200 | 1120 | 120
38957.5691 | 1073 | 1156 | 120
120
38957.5541 | 1 | 0 | 121
38957.5563 | 1 | 0 | 121
38957.5584 | 1 | 0 | 121
38957.5606 | 1072 | 1030 | 121
38957.5627 | 971 | 1005 | 121
38957.5648 | 1340 | 736 | 121
38957.567 | 959 | 922 | 121
38957.5691 | 972 | 1011 | 121
121
38957.5542 | 1 | 0 | 122
38957.5563 | 1 | 0 | 122
38957.5584 | 1 | 0 | 122
38957.5606 | 990 | 951 | 122
38957.5627 | 1119 | 1089 | 122
38957.5649 | 1617 | 685 | 122
38957.567 | 1095 | 1153 | 122
38957.5691 | 986 | 965 | 122
122
38957.5542 | 1 | 0 | 123
38957.5563 | 1 | 0 | 123
38957.5585 | 1 | 0 | 123
38957.5606 | 1056 | 1084 | 123
38957.5627 | 973 | 1007 | 123
38957.5649 | 1638 | 773 | 123
38957.567 | 1075 | 1035 | 123
38957.5692 | 1026 | 1003 | 123
123
38957.5542 | 1 | 0 | 124
38957.5563 | 1 | 0 | 124
38957.5585 | 1 | 0 | 124
38957.5606 | 1185 | 1144 | 124
38957.5628 | 1088 | 1136 | 124
38957.5649 | 1337 | 653 | 124
38957.567 | 1108 | 1144 | 124
38957.5692 | 1006 | 981 | 124
124
38957.5542 | 1 | 0 | 125
38957.5564 | 1 | 0 | 125
38957.5585 | 1 | 0 | 125
38957.5606 | 1111 | 1068 | 125
38957.5628 | 1195 | 1195 | 125
38957.5649 | 1386 | 696 | 125
38957.567 | 1059 | 1020 | 125
38957.5692 | 968 | 1007 | 125
125
38957.5542 | 1 | 0 | 126
38957.5564 | 1 | 0 | 126
38957.5585 | 1 | 0 | 126
38957.5606 | 1037 | 995 | 126
38957.5628 | 987 | 958 | 126
38957.5649 | 1314 | 679 | 126
38957.5671 | 983 | 1080 | 126
38957.5692 | 1073 | 1050 | 126
126
38957.5542 | 1 | 0 | 127
38957.5564 | 1 | 0 | 127
38957.5585 | 1 | 0 | 127
38957.5607 | 1097 | 1054 | 127
38957.5628 | 1116 | 1085 | 127
38957.5649 | 1469 | 720 | 127
38957.5671 | 1013 | 965 | 127
38957.5692 | 1018 | 993 | 127
127
38957.5543 | 1 | 0 | 128
38957.5564 | 1 | 0 | 128
38957.5585 | 1 | 0 | 128
38957.5607 | 1014 | 970 | 128
38957.5628 | 1025 | 995 | 128
38957.565 | 1329 | 659 | 128
38957.5671 | 948 | 914 | 128
38957.5692 | 948 | 926 | 128
128
38957.5543 | 1 | 0 | 129
38957.5564 | 1 | 0 | 129
38957.5586 | 1 | 0 | 129
38957.5607 | 1167 | 1121 | 129
38957.5628 | 1099 | 1166 | 129
38957.565 | 1406 | 753 | 129
38957.5671 | 1210 | 1167 | 129
38957.5692 | 993 | 971 | 129
129
38957.5543 | 1 | 0 | 130
38957.5564 | 1 | 0 | 130
38957.5586 | 1 | 0 | 130
38957.5607 | 1191 | 1145 | 130
38957.5628 | 1009 | 1046 | 130
38957.565 | 1549 | 812 | 130
38957.5671 | 1137 | 1103 | 130
38957.5693 | 950 | 927 | 130
130
38957.5543 | 1 | 0 | 131
38957.5564 | 1 | 0 | 131
38957.5586 | 1 | 0 | 131
38957.5607 | 1132 | 1163 | 131
38957.5629 | 1106 | 1076 | 131
38957.565 | 1251 | 657 | 131
38957.5671 | 1096 | 935 | 131
38957.5693 | 950 | 1068 | 131
131
38957.5543 | 1 | 0 | 132
38957.5565 | 1 | 0 | 132
38957.5586 | 1 | 0 | 132
38957.5607 | 1046 | 1000 | 132
38957.5629 | 1181 | 1151 | 132
38957.565 | 1325 | 929 | 132
38957.5672 | 1068 | 1035 | 132
38957.5693 | 930 | 981 | 132
132

## Test Facts
Last row in IRMS data sheets: | 13
Time when Penlight power was initiated: | 160