## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 60
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, TS/TP (XLPE Ins. with PVC Jacket) control cables (Item #3). Cable specimens present: Six lengths of cable were monitored for electrical performance. A seventh length of cable was monitored for temperature response. No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 160 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
160 | 0 | Initated Penlight Heating
1082-1084 | 922-924 | Conductors F11 & F12 short to ground at much less than 100 ohms (<1 & <1) | TS/TP Cable F shorts to ground
1105 | 945 | Cables ignite and burn
1106-1109 | 946-949 | Conductors F11 & F12 short together at less than 100 ohms (23); conductors A1 & A2 short together at less than 100 ohms (8) | TS/TP Cables F & A short internally
1118 | 958 | Power to Penlight shutoff
1195-1204 | 1035-1044 | Conductors C5 & C6 short to ground at less than 1000 ohms (214 & 197) | TS/TP Cable C shorts to ground for ~369 seconds then recovers
1216 | 1056 | Conductors C5 & C6 short together at less than 100 ohms (8) | TS/TP Cable C shorts internally
1227-1233 | 1067-1073 | Conductors D7 & D8 both short to ground at much less than 100 ohms (<1 & <1) | TS/TP Cable D shorts to ground
1244-1246 | 1084-1086 | Conductor C6 shorts to conductors E10 & F12 at less than 1000 ohms (346 & 196) | Interaction between cables C, E & F lasts for ~184 s, while conductors C6 and F12 are both grounded
1245-1249 | 1085-1089 | Conductors E9 & E10 both short to ground at much less than 100 ohms (<1 & <1) | TS/TP Cable E shorts to ground for ~555 seconds then recovers
1252 | 1092 | Conductors D7 & D8 short together at less than 100 ohms (1) | TS/TP Cable D shorts internally
1255-1269 | 1095-1109 | Conductors D7 & D8 both short to conductors E9 & E10 at less than 100 ohms (<1, 7, <1 & 4) | Interaction between cables D & E lasts for ~383 s, while conductors D7, D8, E9 & E10 are all grounded
1277 | 1117 | Conductors E9 & E10 short together at less than 100 ohms (5) | TS/TP Cable E shorts internally
1280-1288 | 1120-1128 | Conductors E9 & E10 short to conductors F11 & F12 at less than 100 ohms (14, 31, 15 & 9) | Interaction between cables E & F lasts for 370 s, while conductors E9, E10, F11 & F12 are all grounded
1297-1300 | 1137-1140 | Conductor A1 shorts to conductors B3 & B4 at less than 1000 ohms (140 & 86) | Interaction between cables A & B occurs after Cable A is shorted internally, and lasts for ~2 s prior to Cable A shorting to ground
1299-1322 | 1139-1162 | Conductors A1 & A2 both short to ground at less than 1000 ohms (263 & 284) | TS/TP Cable A shorts to ground for ~185 seconds then recovers
1324-1328 | 1164-1168 | Conductor A2 shorts to conductors B3 & B4 at less than 1000 ohms (104 & 141) | Interaction between cables A & B occurs after Cable A is shorted to ground, and lasts for ~185 s prior to recovery
1349 | 1189 | Conductor B3 shorts to ground at less than 100 ohms (91) | TS/TP Cable B partially shorts to ground for ~369 seconds then recovers
1353 | 1193 | Conductors B3 & B4 short together at less than 1000 ohms (149) | TS/TP Cable B shorts internally for ~369 seconds then recovers
1358 | 1198 | Conductor B3 shorts to conductor C6 at less than 1000 ohms (199) | Interaction between cables B & C occurs after cable B & C are both shorted internally, and while cables B & C are grounded
1365 | 1205 | Conductor B4 shorts to ground at less than 1000 ohms (353) | TS/TP Cable B shorted to ground for ~369 seconds then recovers
Additional Observations
Observation 1 | The cables on the tray rung tended to short to ground prior to shorting internally. Other cables shorted to ground for relatively short durations then recovered.
Observation 2 | It took 922 s (15.4 min.) from the start of Penlight heating for a short to ground to occur, 945 s (15.8 min.) for the cable bundle to ignite, and 946 s (15.8 min.) for the initial internal short.
Observation 3 | It appears that one cable to cable interaction briefly took place between cables A & B prior to either cable shorting to ground. However, one of the cables involved was shorted internally prior to this interaction.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A, B, C, D, E, F = TS/TP Cable, Item #3
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## A-B mins
0

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 60 |  |  | 2006-08-23 | 10:44
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-159.5 | 211201.9994 | -157 | 211201.9994 | -154 | 211201.9994 | -151.5 | 211201.9994 | -148.5 | 211201.9994 | -128.5 | 211002.0947 | -126 | 211201.9994 | -123.5 | 211201.9994 | -120.5 | 211201.9994 | -101 | 211201.9994 | -98 | 211201.9994 | -95.5 | 211201.9994 | -92.5 | 261437.9994 | -89.5 | 257037.9994 | -87 | 211201.9994 | -84 | 211201.9994 | -75.5 | 211201.9994 | -73 | 211201.9994 | -70 | 257837.9994 | -67.5 | 252437.9994 | -64.5 | 211002.0947 | -61.5 | 261037.9994 | -53.5 | 211201.9994 | -45 | 258637.9994 | -42 | 216337.9994 | -39.5 | 253837.9994 | -36.5 | 260137.9994 | -28 | 229637.9994 | -25.5 | 219037.9994 | -22.5 | 249037.9994 | -19.5 | 260937.9994 | -17 | 256238.078 | -14 | 261537.9994 | -11.5 | 256537.9994 | -3 | 241037.9994 | 3.1199e-07 | 255038.0783 | 8.5 | 212337.9994 | 11 | 234937.9994 | 14 | 259237.9994 | 16.5 | 235137.9994 | 19.5 | 255437.9994 | 22.5 | 261537.9994 | -141.375 | 211002.0947 | -136 | 211201.9994 | -85.5 | 211201.9994 | -79.875 | 252437.9994 | -74.25 | 211002.0947 | -35.125 | 216337.9994 | -29.5 | 249037.9994 | -7.125 | 241037.9994 | 15.25 | 234937.9994
25 | 211201.9994 | 28 | 211201.9994 | 30.5 | 211201.9994 | 33.5 | 211201.9994 | 36.5 | 211201.9994 | 56 | 211201.9994 | 58.5 | 211201.9994 | 61.5 | 211201.9994 | 64.5 | 211201.9994 | 84 | 211201.9994 | 86.5 | 211201.9994 | 89.5 | 211201.9994 | 92.5 | 261437.9994 | 95 | 257037.9994 | 98 | 211201.9994 | 100.5 | 211201.9994 | 109 | 211201.9994 | 112 | 211201.9994 | 114.5 | 257837.9994 | 117.5 | 252437.9994 | 120.5 | 211201.9994 | 123 | 261037.9994 | 131.5 | 211201.9994 | 140 | 129268.9988 | 142.5 | 216337.9994 | 145.5 | 253837.9994 | 148.5 | 259938.0769 | 156.5 | 229637.9994 | 159.5 | 219037.9994 | 162.5 | 249037.9994 | 165 | 260937.9994 | 168 | 256437.9994 | 170.5 | 261537.9994 | 173.5 | 256537.9994 | 182 | 241037.9994 | 184.5 | 255237.9994 | 193 | 212337.9994 | 196 | 234937.9994 | 198.5 | 259237.9994 | 201.5 | 235137.9994 | 204.5 | 255437.9994 | 207 | 261537.9994 | 43.25 | 211201.9994 | 49 | 211201.9994 | 99.25 | 211201.9994 | 104.875 | 252437.9994 | 110.5 | 211201.9994 | 149.625 | 129268.9988 | 155.375 | 249037.9994 | 177.625 | 241037.9994 | 200.125 | 234937.9994
210 | 211201.9994 | 212.5 | 211201.9994 | 215.5 | 211201.9994 | 218.5 | 211201.9994 | 221 | 211201.9994 | 240.5 | 211002.0947 | 243.5 | 211201.9994 | 246.5 | 211201.9994 | 249 | 211201.9994 | 268.5 | 211201.9994 | 271.5 | 211201.9994 | 274.5 | 211201.9994 | 277 | 261437.9994 | 280 | 257037.9994 | 282.5 | 211201.9994 | 285.5 | 211201.9994 | 294 | 211201.9994 | 296.5 | 211201.9994 | 299.5 | 257837.9994 | 302.5 | 252437.9994 | 305 | 211201.9994 | 308 | 261037.9994 | 316.5 | 211201.9994 | 324.5 | 258637.9994 | 327.5 | 216337.9994 | 330.5 | 253837.9994 | 333 | 260137.9994 | 341.5 | 229637.9994 | 344.5 | 219037.9994 | 347 | 249037.9994 | 350 | 260937.9994 | 352.5 | 256437.9994 | 355.5 | 261537.9994 | 358.5 | 256537.9994 | 366.5 | 241037.9994 | 369.5 | 255237.9994 | 378 | 212337.9994 | 380.5 | 234937.9994 | 383.5 | 259237.9994 | 386.5 | 235137.9994 | 389 | 255437.9994 | 392 | 261537.9994 | 228 | 211002.0947 | 233.75 | 211201.9994 | 284.125 | 211201.9994 | 289.75 | 252437.9994 | 295.25 | 211201.9994 | 334.5 | 216337.9994 | 340.125 | 249037.9994 | 362.5 | 241037.9994 | 384.875 | 234937.9994
394.5 | 211201.9994 | 397.5 | 211201.9994 | 400.5 | 211201.9994 | 403 | 211201.9994 | 406 | 211201.9994 | 425.5 | 211201.9994 | 428.5 | 211201.9994 | 431 | 211201.9994 | 434 | 211201.9994 | 453.5 | 211201.9994 | 456.5 | 211201.9994 | 459 | 211201.9994 | 462 | 261437.9994 | 464.5 | 257037.9994 | 467.5 | 211201.9994 | 470.5 | 211201.9994 | 478.5 | 211201.9994 | 481.5 | 211201.9994 | 484.5 | 257837.9994 | 487 | 252437.9994 | 490 | 211201.9994 | 492.5 | 261037.9994 | 501 | 211002.0947 | 509.5 | 258637.9994 | 512.5 | 216337.9994 | 515 | 253638.0788 | 518 | 260137.9994 | 526 | 229637.9994 | 529 | 219037.9994 | 532 | 249037.9994 | 534.5 | 260937.9994 | 537.5 | 256437.9994 | 540.5 | 261537.9994 | 543 | 256537.9994 | 551.5 | 241037.9994 | 554.5 | 255237.9994 | 562.5 | 212337.9994 | 565.5 | 234937.9994 | 568.5 | 259237.9994 | 571 | 235137.9994 | 574 | 255437.9994 | 576.5 | 261537.9994 | 413 | 211201.9994 | 418.5 | 211201.9994 | 468.875 | 211201.9994 | 474.5 | 252437.9994 | 480.125 | 211201.9994 | 519.25 | 216337.9994 | 524.875 | 249037.9994 | 547.375 | 241037.9994 | 569.75 | 234937.9994
579.5 | 211201.9994 | 582.5 | 211201.9994 | 585 | 211201.9994 | 588 | 211201.9994 | 590.5 | 211201.9994 | 610 | 211201.9994 | 613 | 211201.9994 | 616 | 211201.9994 | 618.5 | 211201.9994 | 638.5 | 211201.9994 | 641 | 211201.9994 | 644 | 211201.9994 | 646.5 | 261437.9994 | 649.5 | 257037.9994 | 652 | 211201.9994 | 655 | 211201.9994 | 663.5 | 211201.9994 | 666.5 | 211201.9994 | 669 | 257837.9994 | 672 | 252437.9994 | 674.5 | 211201.9994 | 677.5 | 261037.9994 | 686 | 211201.9994 | 694.5 | 258637.9994 | 697 | 216337.9994 | 700 | 253837.9994 | 702.5 | 260137.9994 | 711 | 229637.9994 | 714 | 219037.9994 | 716.5 | 249037.9994 | 719.5 | 260937.9994 | 722 | 256437.9994 | 725 | 261537.9994 | 727.5 | 256537.9994 | 736 | 241037.9994 | 739 | 255237.9994 | 747.5 | 212337.9994 | 750 | 234937.9994 | 753 | 259237.9994 | 755.5 | 235137.9994 | 758.5 | 255437.9994 | 761.5 | 261537.9994 | 597.625 | 211201.9994 | 603.25 | 211201.9994 | 653.75 | 211201.9994 | 659.25 | 252437.9994 | 664.75 | 211201.9994 | 704.125 | 216337.9994 | 709.625 | 249037.9994 | 731.875 | 241037.9994 | 754.25 | 234937.9994
764.5 | 211201.9994 | 767 | 211201.9994 | 770 | 211201.9994 | 772.5 | 211201.9994 | 775.5 | 211201.9994 | 795 | 211201.9994 | 798 | 211201.9994 | 800.5 | 211201.9994 | 803.5 | 211201.9994 | 823 | 211201.9994 | 826 | 211201.9994 | 828.5 | 211201.9994 | 831.5 | 261437.9994 | 834.5 | 257037.9994 | 837 | 211201.9994 | 839.5 | 211201.9994 | 848.5 | 211201.9994 | 851 | 211201.9994 | 853.5 | 257837.9994 | 856.5 | 252437.9994 | 859.5 | 211201.9994 | 862 | 261037.9994 | 870.5 | 211201.9994 | 879 | 258637.9994 | 882 | 216337.9994 | 884.5 | 253837.9994 | 887.5 | 260137.9994 | 895.5 | 229637.9994 | 898.5 | 219037.9994 | 901.5 | 249037.9994 | 904 | 260937.9994 | 907 | 128168.9988 | 909.5 | 261238.1529 | 912.5 | 256338.0779 | 921 | 120468.9988 | 923.5 | 255237.9994 | 932.5 | 106118.9988 | 935 | 117418.9988 | 938 | 86345.9982 | 940.5 | 78312.6648 | 943.5 | 85079.3315 | 946 | 23.3674 | 782.5 | 211201.9994 | 788 | 211201.9994 | 838.5 | 211201.9994 | 844 | 252437.9994 | 849.5 | 211201.9994 | 888.75 | 216337.9994 | 894.375 | 249037.9994 | 916.625 | 120468.9988 | 939.25 | 78312.6648
949 | 7.8474 | 952 | 35050.4358 | 954.5 | 210702.3786 | 957.5 | 210802.2366 | 960.5 | 105550.9988 | 979.5 | 70333.9982 | 982.5 | 105550.9988 | 985.5 | 105550.9988 | 988.5 | 105550.9988 | 1007.5 | 52725.4976 | 1010.5 | 105550.9988 | 1013.5 | 105550.9988 | 1016.5 | 130668.9988 | 1019 | 85612.6648 | 1021.5 | 70333.9982 | 1024.5 | 70333.9982 | 1033 | 70333.9982 | 1035.5 | 105550.9988 | 1038.5 | 257837.9994 | 1041.5 | 84079.3315 | 1044.5 | 70333.9982 | 1047 | 130468.9988 | 1055.5 | 8.2859 | 1063.5 | 1678.5842 | 1066.5 | 72045.9982 | 1069.5 | 63384.4976 | 1072 | 51947.5969 | 1080.5 | 1814.4101 | 1083.5 | 346.0098 | 1086 | 196.4342 | 1089 | 1663.6799 | 1091.5 | 0.91356 | 1094.5 | 0.9573 | 1097.5 | 6.8392 | 1105.5 | 0.77822 | 1108.5 | 3.7256 | 1117 | 5.2673 | 1119.5 | 14.0836 | 1122.5 | 30.8468 | 1125.5 | 14.6992 | 1128 | 8.8256 | 1131 | 0.43718 | 967.125 | 35050.4358 | 973 | 105550.9988 | 1023.125 | 70333.9982 | 1028.875 | 84079.3315 | 1034.375 | 70333.9982 | 1073.5 | 346.0098 | 1079.125 | 196.4342 | 1101.5 | 0.77822 | 1123.875 | 8.8256
1133.5 | 15.428 | 1136.5 | 139.719 | 1139.5 | 85.763 | 1142 | 45470.4425 | 1145 | 92123.3358 | 1164.5 | 103.5782 | 1167.5 | 140.9437 | 1170 | 59692.2944 | 1173 | 114738.8184 | 1192.5 | 149.2927 | 1195.5 | 64819.8356 | 1198 | 199.2887 | 1201 | 1881.2679 | 1203.5 | 8766.8099 | 1206.5 | 2328.7055 | 1209.5 | 13986.7908 | 1217.5 | 3481.3538 | 1220.5 | 2147.8362 | 1223.5 | 14229.8779 | 1226 | 3908.5012 | 1229 | 2385.854 | 1231.5 | 26013.7939 | 1240 | 25.1076 | 1248.5 | 101741.0092 | 1251.5 | 72045.9982 | 1254 | 84545.9982 | 1257 | 86645.9982 | 1265.5 | 57334.4976 | 1268 | 109468.9988 | 1271 | 82945.9982 | 1273.5 | 86912.6648 | 1276.5 | 20.7028 | 1279.5 | 30.0617 | 1282 | 5.332 | 1290.5 | 4.2764 | 1293.5 | 15.0944 | 1301.5 | 3.6393 | 1304.5 | 2165.7438 | 1307.5 | 7359.8726 | 1310 | 26.7234 | 1313 | 109.9256 | 1315.5 | 32.4987 | 1152 | 85.763 | 1157.5 | 45470.4425 | 1207.875 | 199.2887 | 1213.5 | 1881.2679 | 1219.125 | 2328.7055 | 1258.375 | 57334.4976 | 1263.875 | 82945.9982 | 1286.375 | 4.2764 | 1308.75 | 26.7234
1318.5 | 84.7106 | 1321.5 | 55209.4392 | 1324 | 201524.0064 | 1327 | 9087.0294 | 1329.5 | 52725.4976 | 1349.5 | 14992.9915 | 1352 | 6943.3817 | 1355 | 7186.2582 | 1357.5 | 7725.9835 | 1377.5 | 260.6911 | 1380 | 105301.213 | 1383 | 210602.5679 | 1385.5 | 130668.9988 | 1388.5 | 85612.6648 | 1391.5 | 70333.9982 | 1394 | 70333.9982 | 1402.5 | 70333.9982 | 1405.5 | 70333.9982 | 1408 | 85879.3315 | 1411 | 84079.3315 | 1413.5 | 70333.9982 | 1416.5 | 86945.9982 | 1425 | 51.8957 | 1433.5 | 218883.8765 | 1436 | 72045.9982 | 1439 | 84545.9982 | 1442 | 86645.9982 | 1450 | 76479.3315 | 1453 | 72945.9982 | 1455.5 | 82945.9982 | 1458.5 | 86912.6648 | 1461.5 | 0.22134 | 1464 | 58880.0466 | 1467 | 1536.2021 | 1475.5 | 15.9146 | 1478 | 48281.207 | 1486.5 | 10.4091 | 1489.5 | 6379.5064 | 1492 | 89670.1966 | 1495 | 71158.3248 | 1497.5 | 85079.3315 | 1500.5 | 21.5927 | 1336.75 | 6943.3817 | 1342.25 | 7186.2582 | 1392.75 | 70333.9982 | 1398.25 | 84079.3315 | 1403.875 | 70333.9982 | 1443.125 | 72045.9982 | 1448.75 | 82945.9982 | 1471.125 | 15.9146 | 1493.5 | 6379.5064
1503.5 | 60.1583 | 1506 | 52625.5828 | 1509 | 210702.3786 | 1511.5 | 210602.5679 | 1514.5 | 105550.9988 | 1534 | 70333.9982 | 1537 | 105550.9988 | 1539.5 | 105550.9988 | 1542.5 | 105550.9988 | 1562 | 14821.4558 | 1565 | 210602.5679 | 1567.5 | 70333.9982 | 1570.5 | 87079.3315 | 1573.5 | 85612.6648 | 1576 | 70333.9982 | 1579 | 70333.9982 | 1587.5 | 70333.9982 | 1590 | 70333.9982 | 1593 | 85879.3315 | 1595.5 | 84079.3315 | 1598.5 | 70333.9982 | 1601.5 | 130468.9988 | 1609.5 | 1.0272 | 1618 | 86145.9982 | 1621 | 108118.9988 | 1623.5 | 84545.9982 | 1626.5 | 86645.9982 | 1635 | 76479.3315 | 1637.5 | 72945.9982 | 1640.5 | 82945.9982 | 1643.5 | 86912.6648 | 1646 | 4.5745 | 1649 | 58448.5054 | 1651.5 | 31900.6657 | 1660 | 55024.1772 | 1663 | 62914.5597 | 1671.5 | 21.4253 | 1674 | 2000.6796 | 1677 | 69426.2345 | 1679.5 | 10806.095 | 1682.5 | 85079.3315 | 1685.5 | 15.4879 | 1521.5 | 52625.5828 | 1527 | 105550.9988 | 1577.5 | 70333.9982 | 1583.125 | 84079.3315 | 1588.75 | 70333.9982 | 1627.875 | 72945.9982 | 1633.5 | 82945.9982 | 1655.875 | 31900.6657 | 1678.25 | 2000.6796
1688 | 1.1696 | 1691 | 42080.4946 | 1693.5 | 210802.2366 | 1696.5 | 210702.4259 | 1699.5 | 105550.9988 | 1719 | 70333.9982 | 1721.5 | 70333.9982 | 1724.5 | 70333.9982 | 1727.5 | 70333.9982 | 1746.5 | 70333.9982 | 1749.5 | 70333.9982 | 1752.5 | 70333.9982 | 1755.5 | 130668.9988 | 1758 | 85612.6648 | 1761 | 70333.9982 | 1763.5 | 70333.9982 | 1772 | 70333.9982 | 1775 | 70333.9982 | 1777.5 | 85879.3315 | 1780.5 | 84079.3315 | 1783.5 | 70333.9982 | 1786 | 86945.9982 | 1794.5 | 70333.9982 | 1803 | 86145.9982 | 1805.5 | 72045.9982 | 1808.5 | 126868.9988 | 1811.5 | 86645.9982 | 1819.5 | 76479.3315 | 1822.5 | 109468.9988 | 1825.5 | 82945.9982 | 1828 | 86912.6648 | 1831 | 0.098558 | 1833.5 | 50879.5933 | 1836.5 | 26706.7443 | 1845 | 45780.9729 | 1847.5 | 55272.9827 | 1856 | 11.0134 | 1858.5 | 328.6096 | 1862 | 239909.5666 | 1864.5 | 62133.8698 | 1867.5 | 85079.3315 | 1870 | 27.3267 | 1706.25 | 42080.4946 | 1712 | 70333.9982 | 1762.25 | 70333.9982 | 1767.875 | 84079.3315 | 1773.5 | 70333.9982 | 1812.625 | 72045.9982 | 1818.375 | 82945.9982 | 1840.625 | 26706.7443 | 1863.125 | 328.6096
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 60 |  |  | 2006-08-23 | 10:44
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-154.1 | 211202 |  | -131.6 | 211202 | -103.6667 | 211202 | -88.1111 | 211202 | -73.8889 | 211202 | -65.1667 | 211202 | -41 | 256538 | -35.4 | 241038 | -23.1111 | 211202 | -20 | 211202 | -2.4 | 234938 | 6.0536e-08 | 255438 | -154.1 | 211202 | -103.6667 | 211202 | -73.8889 | 211202 | -67.0444 | 211202 | -58.7222 | 211202 | -29.8778 | 211202 | -45.5417 | 211202 | -35.3639 | 211202 | -11.3778 | 211202 | -142.85 | 211202 | -95.8889 | 211202 | -69.5278 | 211202 | -38.2 | 241038 | -21.5556 | 211202 | -1.2 | 234938
30.7 | 211202 |  | 53.1 | 211202 | 81.1111 | 211202 | 96.6111 | 211202 | 110.9444 | 129269 | 119.7222 | 211202 | 143.8 | 256438 | 149.4 | 241038 | 161.6667 | 211202 | 164.7222 | 211202 | 182.5 | 234938 | 184.7 | 255438 | 30.7 | 129269 | 81.1111 | 211202 | 110.9444 | 129269 | 117.7306 | 211202 | 126.0278 | 211202 | 154.8972 | 211202 | 139.2639 | 129269 | 149.4667 | 129269 | 173.3972 | 211202 | 41.9 | 211202 | 88.8611 | 211202 | 115.3333 | 129269 | 146.6 | 241038 | 163.1944 | 211202 | 183.6 | 234938
215.5 | 211202 |  | 237.9 | 211202 | 265.8333 | 211202 | 281.4444 | 211202 | 295.8333 | 211202 | 304.5 | 105551 | 328.6 | 256438 | 334.2 | 241038 | 346.3889 | 211202 | 349.6667 | 211202 | 367.3 | 234938 | 369.5 | 255438 | 215.5 | 105551 | 265.8333 | 211202 | 295.8333 | 105551 | 302.5194 | 211202 | 310.8333 | 211202 | 339.7139 | 211202 | 324.0972 | 105551 | 334.2833 | 105551 | 358.2139 | 211202 | 226.7 | 211202 | 273.6389 | 211202 | 300.1667 | 105551 | 331.4 | 241038 | 348.0278 | 211202 | 368.4 | 234938
400.3 | 211202 |  | 422.7 | 211202 | 450.7222 | 211202 | 466.2778 | 211202 | 480.5556 | 211202 | 489.2222 | 211202 | 513.5 | 256438 | 519 | 126169 | 531.2778 | 211202 | 534.3889 | 211202 | 552 | 234938 | 554.3 | 255438 | 400.3 | 211202 | 450.7222 | 126169 | 480.5556 | 211202 | 487.375 | 126169 | 495.6667 | 211202 | 524.5417 | 126169 | 508.8611 | 211202 | 519.0194 | 211202 | 542.9917 | 211202 | 411.5 | 211202 | 458.5 | 211202 | 484.8889 | 211202 | 516.25 | 126169 | 532.8333 | 211202 | 553.15 | 234938
585.1 | 211202 |  | 607.4 | 211202 | 635.4444 | 211202 | 651.0556 | 211202 | 665.3889 | 211202 | 674.0556 | 211202 | 698 | 256438 | 703.7 | 241038 | 715.9444 | 211202 | 719.0556 | 105551 | 736.7 | 234938 | 739 | 255438 | 585.1 | 211202 | 635.4444 | 105551 | 665.3889 | 105551 | 672.05 | 211202 | 680.375 | 105551 | 709.175 | 105551 | 693.6111 | 105551 | 703.7861 | 211202 | 727.675 | 105551 | 596.25 | 211202 | 643.25 | 211202 | 669.7222 | 211202 | 700.85 | 241038 | 717.5 | 105551 | 737.85 | 234938
769.9 | 211202 |  | 792.3 | 211202 | 820.2222 | 211202 | 835.7778 | 211202 | 850.1111 | 211202 | 858.7222 | 211202 | 882.8 | 128169 | 888.5 | 14990.4706 | 900.7778 | 86346 | 903.8333 | 78312.6667 | 921.5 | 0.7012 | 923.8 | 0.63562 | 769.9 | 211202 | 820.2222 | 14990.4706 | 850.1111 | 0.63562 | 856.825 | 14990.4706 | 865.1528 | 78312.6667 | 893.9778 | 14990.4706 | 878.3611 | 78312.6667 | 888.5333 | 0.63562 | 912.4778 | 0.63562 | 781.1 | 211202 | 828 | 211202 | 854.4167 | 211202 | 885.65 | 14990.4706 | 902.3056 | 78312.6667 | 922.65 | 0.63562
954.7 | 1488.1654 |  | 977 | 5461.4433 | 1004.9444 | 52725.5 | 1020.5 | 70334 | 1034.8333 | 213.5266 | 1043.6111 | 196.9464 | 1067.7 | 0.63 | 1073.2 | 0.6411 | 1085.4444 | 0.65401 | 1088.6667 | 0.63121 | 1106.3 | 2.0031 | 1108.5 | 3.9431 | 954.7 | 196.9464 | 1004.9444 | 0.63 | 1034.8333 | 0.63121 | 1041.5861 | 0.63 | 1049.8889 | 0.63121 | 1078.7528 | 0.63 | 1063.1389 | 0.63121 | 1073.3111 | 2.0031 | 1097.2278 | 0.63121 | 965.85 | 1488.1654 | 1012.7222 | 52725.5 | 1039.2222 | 196.9464 | 1070.45 | 0.63 | 1087.0556 | 0.63121 | 1107.4 | 2.0031
1139.3 | 262.5396 |  | 1161.7 | 284.1097 | 1189.7222 | 90.9616 | 1205.2778 | 352.9412 | 1219.5556 | 463.6226 | 1228.2778 | 119.3168 | 1252.5 | 0.63024 | 1258 | 0.65285 | 1270.3333 | 12.1561 | 1273.3889 | 17.1835 | 1291 | 8.4786 | 1293.3 | 0.63 | 1139.3 | 90.9616 | 1189.7222 | 0.63024 | 1219.5556 | 0.63 | 1226.375 | 0.63024 | 1234.6806 | 12.1561 | 1263.5556 | 0.63024 | 1247.8889 | 12.1561 | 1258.0333 | 0.63 | 1282.0056 | 0.63 | 1150.5 | 262.5396 | 1197.5 | 90.9616 | 1223.9167 | 119.3168 | 1255.25 | 0.63024 | 1271.8611 | 12.1561 | 1292.15 | 0.63
1324.1 | 2068.3858 |  | 1346.5 | 1954.048 | 1374.5556 | 423.8871 | 1390.0556 | 4702.3182 | 1404.4444 | 1644.9305 | 1413.0556 | 2060.5959 | 1437.2 | 0.64261 | 1442.9 | 5.3998 | 1455.1111 | 9.4829 | 1458.1667 | 30.3058 | 1475.9 | 0.66182 | 1478.1 | 0.63146 | 1324.1 | 423.8871 | 1374.5556 | 0.64261 | 1404.4444 | 0.63146 | 1411.1778 | 0.64261 | 1419.4722 | 9.4829 | 1448.3444 | 0.64261 | 1432.6944 | 9.4829 | 1442.875 | 0.63146 | 1466.8194 | 0.63146 | 1335.3 | 1954.048 | 1382.3056 | 423.8871 | 1408.75 | 1644.9305 | 1440.05 | 0.64261 | 1456.6389 | 9.4829 | 1477 | 0.63146
1508.9 | 41633.4268 |  | 1531.3 | 4846.5761 | 1559.2778 | 52912.4438 | 1574.8889 | 34490.3072 | 1589.1111 | 438.6881 | 1597.8333 | 494.3111 | 1622 | 6.0513 | 1627.6 | 15.3142 | 1639.8889 | 2094.4773 | 1643 | 10335.1247 | 1660.6 | 4.4651 | 1663 | 1.7349 | 1508.9 | 438.6881 | 1559.2778 | 6.0513 | 1589.1111 | 1.7349 | 1595.9417 | 6.0513 | 1604.2639 | 2094.4773 | 1633.1222 | 6.0513 | 1617.4583 | 438.6881 | 1627.6361 | 1.7349 | 1651.6222 | 1.7349 | 1520.1 | 4846.5761 | 1567.0833 | 34490.3072 | 1593.4722 | 438.6881 | 1624.8 | 6.0513 | 1641.4444 | 2094.4773 | 1661.8 | 1.7349
1693.7 | 9.5039 |  | 1716.1 | 10.8532 | 1744.0556 | 52725.5 | 1759.5556 | 70334 | 1773.9444 | 70334 | 1782.7222 | 70334 | 1806.8 | 1.5504 | 1812.4 | 23.5459 | 1824.6667 | 174.4182 | 1827.7222 | 3493.7295 | 1845.4 | 0.64923 | 1847.8 | 20.1832 | 1693.7 | 9.5039 | 1744.0556 | 1.5504 | 1773.9444 | 0.64923 | 1780.7028 | 1.5504 | 1789 | 174.4182 | 1817.8972 | 1.5504 | 1802.2639 | 174.4182 | 1812.4667 | 0.64923 | 1836.3972 | 0.64923 | 1704.9 | 9.5039 | 1751.8056 | 52725.5 | 1778.3333 | 70334 | 1809.6 | 1.5504 | 1826.1944 | 174.4182 | 1846.6 | 0.64923
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0

## F11-F12
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 159.7302 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38952.4477 | 1 | 0 | 38952.4477 | 1 | 0 |  | 22.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4499 | 1 | 0 | 38952.4499 | 1 | 0 |  | 207 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.452 | 1 | 0 | 38952.452 | 1 | 0 |  | 392 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4541 | 1 | 0 | 38952.4542 | 1 | 0 |  | 576.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4563 | 1 | 0 | 38952.4563 | 1 | 0 |  | 761.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4584 | 2099 | 0 | 38952.4584 | 2217 | 0 |  | 946 | 1106 | 128.1441 | 0 | 135.348 | 0 | 1.2814 | 0 | 1.3535 | 0 | 1.2814 | 1.3535 | 24.6489 | 18.0144 | 23.3674
38952.4606 | 2565 | 0 | 38952.4606 | 2055 | 0 |  | 1131 | 1291 | 156.5934 | 0 | 125.4579 | 0 | 1.5659 | 0 | 1.2546 | 0 | 1.5659 | 1.2546 | 2.0031 | 27.3178 | 0.43718
38952.4627 | 1957 | 0 | 38952.4627 | 2600 | 0 |  | 1315.5 | 1475.5 | 119.475 | 0 | 158.7302 | 0 | 1.1947 | 0 | 1.5873 | 0 | 1.1947 | 1.5873 | 33.6934 | 0.63 | 32.4987
38952.4648 | 2129 | 0 | 38952.4648 | 2543 | 0 |  | 1500.5 | 1660.5 | 129.9756 | 0 | 155.2503 | 0 | 1.2998 | 0 | 1.5525 | 0 | 1.2998 | 1.5525 | 22.8924 | 2.8856 | 21.5927
38952.467 | 2239 | 0 | 38952.467 | 2094 | 0 |  | 1685.5 | 1845.5 | 136.6911 | 0 | 127.8388 | 0 | 1.3669 | 0 | 1.2784 | 0 | 1.3669 | 1.2784 | 16.8548 | 24.9465 | 15.4879
38952.4691 | 2035 | 0 | 38952.4691 | 2164 | 0 |  | 1870 | 2030 | 124.2369 | 0 | 132.1123 | 0 | 1.2424 | 0 | 1.3211 | 0 | 1.2424 | 1.3211 | 28.569 | 20.9048 | 27.3267

## E10-F12
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 156.0061 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38952.4477 | 1 | 0 | 38952.4477 | 1 | 0 |  | 19.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38952.4498 | 1 | 0 | 38952.4498 | 1 | 0 |  | 204.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38952.452 | 1 | 0 | 38952.452 | 1 | 0 |  | 389 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38952.4541 | 1 | 0 | 38952.4541 | 1 | 0 |  | 574 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38952.4563 | 1 | 0 | 38952.4563 | 1 | 0 |  | 758.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38952.4584 | 3 | 0 | 38952.4584 | 2214 | 0 |  | 943.5 | 1103.5 | 0.18315 | 0 | 135.1648 | 0 | 0.0018315 | 0 | 1.3516 | 0 | 0.0018315 | 1.3516 | 85079.3333 | 15.4192 | 85079.3315
38952.4605 | 2318 | 0 | 38952.4605 | 2408 | 0 |  | 1128 | 1288 | 141.514 | 0 | 147.0085 | 0 | 1.4151 | 0 | 1.4701 | 0 | 1.4151 | 1.4701 | 10.2407 | 6.1204 | 8.8256
38952.4627 | 1213 | 0 | 38952.4627 | 2065 | 0 |  | 1313 | 1473 | 74.0537 | 0 | 126.0684 | 0 | 0.74054 | 0 | 1.2607 | 0 | 0.74054 | 1.2607 | 110.6661 | 23.7472 | 109.9256
38952.4648 | 3 | 0 | 38952.4648 | 2539 | 0 |  | 1497.5 | 1657.5 | 0.18315 | 0 | 155.0061 | 0 | 0.0018315 | 0 | 1.5501 | 0 | 0.0018315 | 1.5501 | 85079.3333 | 0.64514 | 85079.3315
38952.4669 | 3 | 0 | 38952.467 | 2064 | 0 |  | 1682.5 | 1842.5 | 0.18315 | 0 | 126.0073 | 0 | 0.0018315 | 0 | 1.2601 | 0 | 0.0018315 | 1.2601 | 85079.3333 | 23.8072 | 85079.3315
38952.4691 | 3 | 0 | 38952.4691 | 2011 | 0 |  | 1867.5 | 2027.5 | 0.18315 | 0 | 122.7717 | 0 | 0.0018315 | 0 | 1.2277 | 0 | 0.0018315 | 1.2277 | 85079.3333 | 27.0701 | 85079.3315

## E10-F11
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 143.6129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38952.4477 | 1 | 0 | 38952.4477 | 1 | 0 |  | 16.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38952.4498 | 1 | 0 | 38952.4498 | 1 | 0 |  | 201.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38952.4519 | 1 | 0 | 38952.452 | 1 | 0 |  | 386.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38952.4541 | 1 | 0 | 38952.4541 | 1 | 0 |  | 571 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38952.4562 | 1 | 0 | 38952.4562 | 1 | 0 |  | 755.5 | 915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38952.4584 | 3 | 0 | 38952.4584 | 2336 | 0 |  | 940.5 | 1100.5 | 0.18315 | 0 | 142.6129 | 0 | 0.0018315 | 0 | 1.4261 | 0 | 0.0018315 | 1.4261 | 78312.6667 | 0.7012 | 78312.6648
38952.4605 | 2029 | 0 | 38952.4605 | 2176 | 0 |  | 1125.5 | 1285.5 | 123.8706 | 0 | 132.8449 | 0 | 1.2387 | 0 | 1.3284 | 0 | 1.2387 | 1.3284 | 15.9379 | 8.1057 | 14.6992
38952.4626 | 1840 | 0 | 38952.4627 | 1901 | 0 |  | 1310 | 1470 | 112.3321 | 0 | 116.0562 | 0 | 1.1233 | 0 | 1.1606 | 0 | 1.1233 | 1.1606 | 27.8467 | 23.7443 | 26.7234
38952.4648 | 4 | 1 | 38952.4648 | 1852 | 0 |  | 1495 | 1655 | 0.2442 | 0.06105 | 113.0647 | 0 | 0.002442 | 0.0006105 | 1.1306 | 0 | 0.0018315 | 1.1306 | 334914.8904 | 43.5007 | 71158.3248
38952.4669 | 3 | 1 | 38952.4669 | 2261 | 1 |  | 1679.5 | 1839.5 | 0.18315 | 0.06105 | 138.0342 | 0.06105 | 0.0018315 | 0.0006105 | 1.3803 | 0.0006105 | 0.001221 | 1.3797 | 10335.1247 | 4.8235 | 10806.095
38952.4691 | 3 | 1 | 38952.4691 | 2050 | 0 |  | 1864.5 | 2024.5 | 0.18315 | 0.06105 | 125.1526 | 0 | 0.0018315 | 0.0006105 | 1.2515 | 0 | 0.001221 | 1.2515 | 49154.8479 | 35.9771 | 62133.8698

## E9-F12
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 158.326 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38952.4476 | 1 | 0 | 38952.4477 | 1 | 0 |  | 14 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38952.4498 | 1 | 0 | 38952.4498 | 1 | 0 |  | 198.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38952.4519 | 1 | 0 | 38952.4519 | 1 | 0 |  | 383.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38952.4541 | 1 | 0 | 38952.4541 | 1 | 0 |  | 568.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38952.4562 | 1 | 0 | 38952.4562 | 1 | 0 |  | 753 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
38952.4583 | 3 | 0 | 38952.4583 | 2577 | 0 |  | 938 | 1098 | 0.18315 | 0 | 157.326 | 0 | 0.0018315 | 0 | 1.5733 | 0 | 0.0018315 | 1.5733 | 86346 | 0.63562 | 86345.9982
38952.4605 | 1964 | 0 | 38952.4605 | 2495 | 0 |  | 1122.5 | 1282.5 | 119.9023 | 0 | 152.3199 | 0 | 1.199 | 0 | 1.5232 | 0 | 1.199 | 1.5232 | 32.0458 | 3.9431 | 30.8468
38952.4626 | 1828 | 1 | 38952.4626 | 2344 | 1 |  | 1307.5 | 1467.5 | 111.5995 | 0.06105 | 143.1013 | 0.06105 | 1.116 | 0.0006105 | 1.431 | 0.0006105 | 1.1154 | 1.4304 | 42.109 | 10.6544 | 7359.8726
38952.4647 | 3 | 1 | 38952.4648 | 2217 | 1 |  | 1492 | 1652 | 0.18315 | 0.06105 | 135.348 | 0.06105 | 0.0018315 | 0.0006105 | 1.3535 | 0.0006105 | 0.001221 | 1.3529 | 66630.6433 | 52.9753 | 89670.1966
38952.4669 | 3 | 1 | 38952.4669 | 2258 | 1 |  | 1677 | 1837 | 0.18315 | 0.06105 | 137.851 | 0.06105 | 0.0018315 | 0.0006105 | 1.3785 | 0.0006105 | 0.001221 | 1.3779 | 54768.5498 | 36.6343 | 69426.2345
| 3 | 1 | 38952.469 | 2083 | 1 |  | 1862 | 2022 | 0.18315 | 0.06105 | 127.1673 | 0.06105 | 0.0018315 | 0.0006105 | 1.2717 | 0.0006105 | 0.001221 | 1.2711 | 124578.5255 | 1260.7952 | 239909.5666

## E9-F11
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 143.4908 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38952.4476 | 1 | 0 | 38952.4476 | 1 | 0 |  | 11 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234938 | 234938 | 234937.9994
38952.4497 | 1 | 0 | 38952.4498 | 1 | 0 |  | 196 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234938 | 234938 | 234937.9994
38952.4519 | 1 | 0 | 38952.4519 | 1 | 0 |  | 380.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234938 | 234938 | 234937.9994
38952.454 | 1 | 0 | 38952.454 | 1 | 0 |  | 565.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234938 | 234938 | 234937.9994
38952.4561 | 1 | 0 | 38952.4562 | 1 | 0 |  | 750 | 910 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234938 | 234938 | 234937.9994
38952.4583 | 2 | 0 | 38952.4583 | 2043 | 0 |  | 935 | 1095 | 0.1221 | 0 | 124.7253 | 0 | 0.001221 | 0 | 1.2473 | 0 | 0.001221 | 1.2473 | 117419 | 15.0455 | 117418.9988
38952.4604 | 2038 | 0 | 38952.4604 | 2226 | 0 |  | 1119.5 | 1279.5 | 124.42 | 0 | 135.8974 | 0 | 1.2442 | 0 | 1.359 | 0 | 1.2442 | 1.359 | 15.3278 | 5.5876 | 14.0836
38952.4626 | 1238 | 4 | 38952.4626 | 2167 | 2 |  | 1304.5 | 1464.5 | 75.58 | 0.2442 | 132.2955 | 0.1221 | 0.7558 | 0.002442 | 1.323 | 0.001221 | 0.75336 | 1.3217 | 93.7276 | 8.4786 | 2165.7438
38952.4647 | 3 | 5 | 38952.4647 | 2062 | 2 |  | 1489.5 | 1649.5 | 0.18315 | 0.30525 | 125.8852 | 0.1221 | 0.0018315 | 0.0030525 | 1.2589 | 0.001221 | 0.001221 | 1.2576 | 6961.9535 | 15.7643 | 6379.5064
38952.4668 | 5 | 5 | 38952.4669 | 2250 | 2 |  | 1674 | 1834 | 0.30525 | 0.30525 | 137.3626 | 0.1221 | 0.0030525 | 0.0030525 | 1.3736 | 0.001221 | 0 | 1.3724 | 2094.4773 | 4.4651 | 2000.6796
38952.469 | 3 | 5 | 38952.469 | 2334 | 3 |  | 1858.5 | 2018.5 | 0.18315 | 0.30525 | 142.4908 | 0.18315 | 0.0018315 | 0.0030525 | 1.4249 | 0.0018315 | 0.001221 | 1.4231 | 330.7029 | 0.7064 | 328.6096

## E9-E10
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129.6935 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38952.4476 | 1 | 0 | 38952.4476 | 1 | 0 |  | 8.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212338 | 212338 | 212337.9994
38952.4497 | 1 | 0 | 38952.4497 | 1 | 0 |  | 193 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212338 | 212338 | 212337.9994
38952.4518 | 1 | 0 | 38952.4519 | 1 | 0 |  | 378 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212338 | 212338 | 212337.9994
38952.454 | 1 | 0 | 38952.454 | 1 | 0 |  | 562.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212338 | 212338 | 212337.9994
38952.4561 | 1 | 0 | 38952.4561 | 1 | 0 |  | 747.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 212338 | 212338 | 212337.9994
38952.4583 | 2 | 0 | 38952.4583 | 2 | 0 |  | 932.5 | 1092.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 106119 | 106119 | 106118.9988
38952.4604 | 1995 | 0 | 38952.4604 | 2108 | 0 |  | 1117 | 1277 | 121.7949 | 0 | 128.6935 | 0 | 1.2179 | 0 | 1.2869 | 0 | 1.2179 | 1.2869 | 6.4852 | 0.77704 | 5.2673
38952.4625 | 1326 | 1058 | 38952.4625 | 1038 | 828 |  | 1301.5 | 1461.5 | 80.9524 | 64.591 | 63.37 | 50.5495 | 0.80952 | 0.64591 | 0.6337 | 0.50549 | 0.16361 | 0.12821 | 12.5851 | 17.4132 | 3.6393
38952.4647 | 1143 | 1097 | 38952.4647 | 1157 | 1187 |  | 1486.5 | 1646.5 | 69.7802 | 66.9719 | 70.6349 | 72.4664 | 0.6978 | 0.66972 | 0.70635 | 0.72466 | 0.028083 | 0.018315 | 3043.8951 | 7972.9208 | 10.4091
38952.4668 | 1200 | 1179 | 38952.4668 | 1097 | 1070 |  | 1671.5 | 1831.5 | 73.2601 | 71.978 | 66.9719 | 65.3236 | 0.7326 | 0.71978 | 0.66972 | 0.65324 | 0.012821 | 0.016484 | 3039.9675 | 12532.4715 | 21.4253
38952.4689 | 1020 | 992 | 38952.469 | 1106 | 1080 |  | 1856 | 2016 | 62.2711 | 60.5617 | 67.5214 | 65.9341 | 0.62271 | 0.60562 | 0.67521 | 0.65934 | 0.017094 | 0.015873 | 1958.3384 | 3493.7295 | 11.0134

## D8-E10
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 155.884 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38952.4475 | 1 | 1 | 38952.4475 | 1 | 0 |  | 3.1199e-07 | 160 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 651464366.44 | 255238 | 255038.0783
38952.4496 | 1 | 0 | 38952.4496 | 1 | 0 |  | 184.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38952.4517 | 1 | 0 | 38952.4518 | 1 | 0 |  | 369.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38952.4539 | 1 | 0 | 38952.4539 | 1 | 0 |  | 554.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38952.456 | 1 | 0 | 38952.456 | 1 | 0 |  | 739 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255238 | 255238 | 255237.9994
38952.4582 | 1 | 0 | 38952.4582 | 2 | 0 |  | 923.5 | 1083.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255238 | 127569 | 255237.9994
38952.4603 | 2427 | 0 | 38952.4603 | 2537 | 0 |  | 1108.5 | 1268.5 | 148.1685 | 0 | 154.884 | 0 | 1.4817 | 0 | 1.5488 | 0 | 1.4817 | 1.5488 | 5.2073 | 0.64564 | 3.7256
38952.4624 | 2193 | 0 | 38952.4625 | 907 | 0 |  | 1293.5 | 1453.5 | 133.8828 | 0 | 55.3724 | 0 | 1.3388 | 0 | 0.55372 | 0 | 1.3388 | 0.55372 | 16.4332 | 181.5193 | 15.0944
38952.4646 | 2069 | 1 | 38952.4646 | 3 | 0 |  | 1478 | 1638 | 126.3126 | 0.06105 | 0.18315 | 0 | 1.2631 | 0.0006105 | 0.0018315 | 0 | 1.2625 | 0.0018315 | 23.4226 | 85012.6667 | 48281.207
38952.4667 | 1922 | 1 | 38952.4667 | 5 | 0 |  | 1663 | 1823 | 117.3382 | 0.06105 | 0.30525 | 0 | 1.1734 | 0.0006105 | 0.0030525 | 0 | 1.1728 | 0.0030525 | 32.8673 | 50967.6 | 62914.5597
38952.4689 | 1999 | 1 | 38952.4689 | 3 | 0 |  | 1847.5 | 2007.5 | 122.0391 | 0.06105 | 0.18315 | 0 | 1.2204 | 0.0006105 | 0.0018315 | 0 | 1.2198 | 0.0018315 | 27.7468 | 85012.6667 | 55272.9827

## D8-E9
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 147.2149 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38952.4474 | 1 | 0 | 38952.4475 | 1 | 0 |  | -3 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38952.4496 | 1 | 0 | 38952.4496 | 1 | 0 |  | 182 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38952.4517 | 1 | 0 | 38952.4517 | 1 | 0 |  | 366.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38952.4539 | 1 | 0 | 38952.4539 | 1 | 0 |  | 551.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38952.456 | 1 | 0 | 38952.456 | 1 | 0 |  | 736 | 896 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
38952.4581 | 2 | 0 | 38952.4581 | 1 | 0 |  | 921 | 1081 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 120469 | 241038 | 120468.9988
38952.4603 | 2395 | 0 | 38952.4603 | 2103 | 0 |  | 1105.5 | 1265.5 | 146.2149 | 0 | 128.3883 | 0 | 1.4621 | 0 | 1.2839 | 0 | 1.4621 | 1.2839 | 0.68392 | 14.6638 | 0.77822
38952.4624 | 2282 | 0 | 38952.4624 | 907 | 0 |  | 1290.5 | 1450.5 | 139.3162 | 0 | 55.3724 | 0 | 1.3932 | 0 | 0.55372 | 0 | 1.3932 | 0.55372 | 5.6696 | 165.8633 | 4.2764
38952.4645 | 2058 | 0 | 38952.4646 | 1383 | 0 |  | 1475.5 | 1635.5 | 125.641 | 0 | 84.4322 | 0 | 1.2564 | 0 | 0.84432 | 0 | 1.2564 | 0.84432 | 17.171 | 74.3586 | 15.9146
38952.4667 | 1856 | 1 | 38952.4667 | 18 | 0 |  | 1660 | 1820 | 113.3089 | 0.06105 | 1.0989 | 0 | 1.1331 | 0.0006105 | 0.010989 | 0 | 1.1325 | 0.010989 | 29.9397 | 13296.5556 | 55024.1772
38952.4688 | 1952 | 1 | 38952.4688 | 3 | 0 |  | 1845 | 2005 | 119.1697 | 0.06105 | 0.18315 | 0 | 1.1917 | 0.0006105 | 0.0018315 | 0 | 1.1911 | 0.0018315 | 23.5459 | 80279.3333 | 45780.9729

## D7-E10
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 156.6777 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38952.4473 | 1 | 0 | 38952.4473 | 1 | 0 |  | -11.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38952.4495 | 1 | 0 | 38952.4495 | 1 | 0 |  | 173.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38952.4516 | 1 | 0 | 38952.4516 | 1 | 0 |  | 358.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38952.4538 | 1 | 0 | 38952.4538 | 1 | 0 |  | 543 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38952.4559 | 1 | 0 | 38952.4559 | 1 | 0 |  | 727.5 | 887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
38952.458 | 1 | 1 | 38952.458 | 1 | 0 |  | 912.5 | 1072.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 658117454.44 | 256538 | 256338.0779
38952.4602 | 2370 | 0 | 38952.4602 | 2285 | 0 |  | 1097.5 | 1257.5 | 144.6886 | 0 | 139.4994 | 0 | 1.4469 | 0 | 1.395 | 0 | 1.4469 | 1.395 | 8.2861 | 12.3142 | 6.8392
38952.4623 | 2403 | 0 | 38952.4623 | 1391 | 0 |  | 1282 | 1442 | 146.7033 | 0 | 84.9206 | 0 | 1.467 | 0 | 0.84921 | 0 | 1.467 | 0.84921 | 6.799 | 84.4989 | 5.332
38952.4644 | 2550 | 1 | 38952.4645 | 3 | 0 |  | 1467 | 1627 | 155.6777 | 0.06105 | 0.18315 | 0 | 1.5568 | 0.0006105 | 0.0018315 | 0 | 1.5562 | 0.0018315 | 0.64261 | 85446 | 1536.2021
38952.4666 | 2246 | 1 | 38952.4666 | 3 | 0 |  | 1651.5 | 1811.5 | 137.1184 | 0.06105 | 0.18315 | 0 | 1.3712 | 0.0006105 | 0.0018315 | 0 | 1.3706 | 0.0018315 | 14.2708 | 85446 | 31900.6657
38952.4687 | 2298 | 1 | 38952.4687 | 3 | 0 |  | 1836.5 | 1996.5 | 140.293 | 0.06105 | 0.18315 | 0 | 1.4029 | 0.0006105 | 0.0018315 | 0 | 1.4023 | 0.0018315 | 11.6839 | 85446 | 26706.7443

## D7-E9
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 159.7302 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38952.4473 | 1 | 0 | 38952.4473 | 1 | 0 |  | -14 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4494 | 1 | 0 | 38952.4495 | 1 | 0 |  | 170.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4516 | 1 | 0 | 38952.4516 | 1 | 0 |  | 355.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4537 | 1 | 0 | 38952.4537 | 1 | 0 |  | 540.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.4559 | 1 | 0 | 38952.4559 | 1 | 0 |  | 725 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
38952.458 | 1 | 1 | 38952.458 | 2 | 0 |  | 909.5 | 1069.5 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 341879858.22 | 130719 | 261238.1529
38952.4601 | 2600 | 0 | 38952.4602 | 2171 | 0 |  | 1094.5 | 1254.5 | 158.7302 | 0 | 132.5397 | 0 | 1.5873 | 0 | 1.3254 | 0 | 1.5873 | 1.3254 | 0.63 | 20.515 | 0.9573
38952.4623 | 1993 | 0 | 38952.4623 | 1015 | 0 |  | 1279.5 | 1439.5 | 121.6728 | 0 | 61.9658 | 0 | 1.2167 | 0 | 0.61966 | 0 | 1.2167 | 0.61966 | 31.2785 | 157.7714 | 30.0617
38952.4644 | 2025 | 1 | 38952.4644 | 7 | 0 |  | 1464 | 1624 | 123.6264 | 0.06105 | 0.42735 | 0 | 1.2363 | 0.0006105 | 0.0042735 | 0 | 1.2357 | 0.0042735 | 29.2184 | 37276.8571 | 58880.0466
38952.4666 | 2030 | 1 | 38952.4666 | 4 | 0 |  | 1649 | 1809 | 123.9316 | 0.06105 | 0.2442 | 0 | 1.2393 | 0.0006105 | 0.002442 | 0 | 1.2387 | 0.002442 | 28.9 | 65309.5 | 58448.5054
38952.4687 | 2106 | 1 | 38952.4687 | 3 | 0 |  | 1833.5 | 1993.5 | 128.5714 | 0.06105 | 0.18315 | 0 | 1.2857 | 0.0006105 | 0.0018315 | 0 | 1.2851 | 0.0018315 | 24.2461 | 87112.6667 | 50879.5933

## D7-D8
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 156.6166 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38952.4473 | 1 | 1 | 38952.4473 | 1 | 0 |  | -17 | 143 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 657604478.44 | 256438 | 256238.078
38952.4494 | 1 | 0 | 38952.4494 | 1 | 0 |  | 168 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38952.4516 | 1 | 0 | 38952.4516 | 1 | 0 |  | 352.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38952.4537 | 1 | 0 | 38952.4537 | 1 | 0 |  | 537.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38952.4558 | 1 | 0 | 38952.4558 | 1 | 0 |  | 722 | 882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38952.458 | 2 | 0 | 38952.458 | 698 | 681 |  | 907 | 1067 | 0.1221 | 0 | 42.6129 | 41.5751 | 0.001221 | 0 | 0.42613 | 0.41575 | 0.001221 | 0.010379 | 128169 | 14990.4706 | 128168.9988
38952.4601 | 2549 | 0 | 38952.4601 | 2515 | 0 |  | 1091.5 | 1251.5 | 155.6166 | 0 | 153.5409 | 0 | 1.5562 | 0 | 1.5354 | 0 | 1.5562 | 1.5354 | 0.6426 | 2.0032 | 0.91356
38952.4622 | 2103 | 0 | 38952.4623 | 2319 | 0 |  | 1276.5 | 1436.5 | 128.3883 | 0 | 141.5751 | 0 | 1.2839 | 0 | 1.4158 | 0 | 1.2839 | 1.4158 | 21.9867 | 10.6244 | 20.7028
38952.4644 | 2521 | 0 | 38952.4644 | 1794 | 0 |  | 1461.5 | 1621.5 | 153.9072 | 0 | 109.5238 | 0 | 1.5391 | 0 | 1.0952 | 0 | 1.5391 | 1.0952 | 1.7604 | 42.9978 | 0.22134
38952.4665 | 2419 | 0 | 38952.4665 | 1831 | 0 |  | 1646 | 1806 | 147.6801 | 0 | 111.7827 | 0 | 1.4768 | 0 | 1.1178 | 0 | 1.4768 | 1.1178 | 6.0513 | 40.1081 | 4.5745
38952.4687 | 2524 | 0 | 38952.4687 | 1967 | 0 |  | 1831 | 1991 | 154.0904 | 0 | 120.0855 | 0 | 1.5409 | 0 | 1.2009 | 0 | 1.5409 | 1.2009 | 1.6395 | 30.4209 | 0.098558

## C6-F12
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 159.3639 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38952.4472 | 1 | 0 | 38952.4473 | 1 | 0 |  | -19.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
38952.4494 | 1 | 0 | 38952.4494 | 1 | 0 |  | 165 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
38952.4515 | 1 | 0 | 38952.4515 | 1 | 0 |  | 350 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
38952.4537 | 1 | 0 | 38952.4537 | 1 | 0 |  | 534.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
38952.4558 | 1 | 0 | 38952.4558 | 1 | 0 |  | 719.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
38952.4579 | 1 | 0 | 38952.458 | 1 | 0 |  | 904 | 1064 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
38952.4601 | 148 | 0 | 38952.4601 | 2286 | 0 |  | 1089 | 1249 | 9.0354 | 0 | 139.5604 | 0 | 0.090354 | 0 | 1.3956 | 0 | 0.090354 | 1.3956 | 1663.7703 | 14.1899 | 1663.6799
38952.4622 | 3 | 0 | 38952.4622 | 2214 | 0 |  | 1273.5 | 1433.5 | 0.18315 | 0 | 135.1648 | 0 | 0.0018315 | 0 | 1.3516 | 0 | 0.0018315 | 1.3516 | 86912.6667 | 17.9033 | 86912.6648
38952.4644 | 3 | 0 | 38952.4644 | 2594 | 0 |  | 1458.5 | 1618.5 | 0.18315 | 0 | 158.3639 | 0 | 0.0018315 | 0 | 1.5836 | 0 | 0.0018315 | 1.5836 | 86912.6667 | 0.63146 | 86912.6648
38952.4665 | 3 | 0 | 38952.4665 | 2556 | 0 |  | 1643.5 | 1803.5 | 0.18315 | 0 | 156.044 | 0 | 0.0018315 | 0 | 1.5604 | 0 | 0.0018315 | 1.5604 | 86912.6667 | 2.1275 | 86912.6648
38952.4686 | 3 | 0 | 38952.4686 | 2172 | 0 |  | 1828 | 1988 | 0.18315 | 0 | 132.6007 | 0 | 0.0018315 | 0 | 1.326 | 0 | 0.0018315 | 1.326 | 86912.6667 | 20.1832 | 86912.6648

## C6-F11
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 152.0989 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38952.4472 | 1 | 0 | 38952.4472 | 1 | 0 |  | -22.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38952.4494 | 1 | 0 | 38952.4494 | 1 | 0 |  | 162.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38952.4515 | 1 | 0 | 38952.4515 | 1 | 0 |  | 347 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38952.4536 | 1 | 0 | 38952.4536 | 1 | 0 |  | 532 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38952.4558 | 1 | 0 | 38952.4558 | 1 | 0 |  | 716.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38952.4579 | 1 | 0 | 38952.4579 | 1 | 0 |  | 901.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38952.46 | 839 | 0 | 38952.4601 | 2086 | 0 |  | 1086 | 1246 | 51.221 | 0 | 127.3504 | 0 | 0.51221 | 0 | 1.2735 | 0 | 0.51221 | 1.2735 | 196.9464 | 19.4334 | 196.4342
38952.4622 | 3 | 0 | 38952.4622 | 2266 | 0 |  | 1271 | 1431 | 0.18315 | 0 | 138.3394 | 0 | 0.0018315 | 0 | 1.3834 | 0 | 0.0018315 | 1.3834 | 82946 | 9.9462 | 82945.9982
38952.4643 | 3 | 0 | 38952.4643 | 2475 | 0 |  | 1455.5 | 1615.5 | 0.18315 | 0 | 151.0989 | 0 | 0.0018315 | 0 | 1.511 | 0 | 0.0018315 | 1.511 | 82946 | 0.66182 | 82945.9982
38952.4665 | 3 | 0 | 38952.4665 | 2060 | 0 |  | 1640.5 | 1800.5 | 0.18315 | 0 | 125.7631 | 0 | 0.0018315 | 0 | 1.2576 | 0 | 0.0018315 | 1.2576 | 82946 | 20.9408 | 82945.9982
38952.4686 | 3 | 0 | 38952.4686 | 2460 | 0 |  | 1825.5 | 1985.5 | 0.18315 | 0 | 150.1832 | 0 | 0.0018315 | 0 | 1.5018 | 0 | 0.0018315 | 1.5018 | 82946 | 1.2756 | 82945.9982

## C6-E10
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 133.7839 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38952.4472 | 1 | 0 | 38952.4472 | 1 | 0 |  | -25.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219038 | 219038 | 219037.9994
38952.4493 | 1 | 0 | 38952.4493 | 1 | 0 |  | 159.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219038 | 219038 | 219037.9994
38952.4515 | 1 | 0 | 38952.4515 | 1 | 0 |  | 344.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219038 | 219038 | 219037.9994
38952.4536 | 1 | 0 | 38952.4536 | 1 | 0 |  | 529 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219038 | 219038 | 219037.9994
38952.4557 | 1 | 0 | 38952.4558 | 1 | 0 |  | 714 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219038 | 219038 | 219037.9994
38952.4579 | 1 | 0 | 38952.4579 | 1 | 0 |  | 898.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219038 | 219038 | 219037.9994
38952.46 | 491 | 0 | 38952.46 | 2175 | 0 |  | 1083.5 | 1243.5 | 29.9756 | 0 | 132.7839 | 0 | 0.29976 | 0 | 1.3278 | 0 | 0.29976 | 1.3278 | 346.3096 | 0.7531 | 346.0098
38952.4621 | 2 | 0 | 38952.4622 | 1227 | 0 |  | 1268 | 1428 | 0.1221 | 0 | 74.9084 | 0 | 0.001221 | 0 | 0.74908 | 0 | 0.001221 | 0.74908 | 109469 | 78.5966 | 109468.9988
38952.4643 | 3 | 0 | 38952.4643 | 4 | 0 |  | 1453 | 1613 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 72946 | 54684.5 | 72945.9982
38952.4664 | 3 | 0 | 38952.4664 | 3 | 0 |  | 1637.5 | 1797.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 72946 | 72946 | 72945.9982
38952.4686 | 2 | 0 | 38952.4686 | 2 | 0 |  | 1822.5 | 1982.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 109469 | 109469 | 109468.9988

## C6-E9
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 140.2552 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38952.4471 | 1 | 0 | 38952.4472 | 1 | 0 |  | -28 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38952.4493 | 1 | 0 | 38952.4493 | 1 | 0 |  | 156.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38952.4514 | 1 | 0 | 38952.4514 | 1 | 0 |  | 341.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38952.4536 | 1 | 0 | 38952.4536 | 1 | 0 |  | 526 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38952.4557 | 1 | 0 | 38952.4557 | 1 | 0 |  | 711 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38952.4578 | 1 | 0 | 38952.4578 | 1 | 0 |  | 895.5 | 1055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38952.46 | 120 | 0 | 38952.46 | 2281 | 0 |  | 1080.5 | 1240.5 | 7.326 | 0 | 139.2552 | 0 | 0.07326 | 0 | 1.3926 | 0 | 0.07326 | 1.3926 | 1814.4833 | 0.71811 | 1814.4101
38952.4621 | 4 | 0 | 38952.4621 | 973 | 0 |  | 1265.5 | 1425.5 | 0.2442 | 0 | 59.4017 | 0 | 0.002442 | 0 | 0.59402 | 0 | 0.002442 | 0.59402 | 57334.5 | 136.1131 | 57334.4976
38952.4642 | 3 | 0 | 38952.4643 | 295 | 0 |  | 1450 | 1610 | 0.18315 | 0 | 18.0098 | 0 | 0.0018315 | 0 | 0.1801 | 0 | 0.0018315 | 0.1801 | 76479.3333 | 678.7729 | 76479.3315
38952.4664 | 3 | 0 | 38952.4664 | 2 | 0 |  | 1635 | 1795 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76479.3333 | 114769 | 76479.3315
38952.4685 | 3 | 0 | 38952.4685 | 3 | 0 |  | 1819.5 | 1979.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 76479.3333 | 76479.3333 | 76479.3315

## C5-F12
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 158.8755 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38952.447 | 1 | 0 | 38952.4471 | 1 | 0 |  | -36.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38952.4492 | 1 | 1 | 38952.4492 | 1 | 0 |  | 148.5 | 308.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 676717790.44 | 260138 | 259938.0769
38952.4513 | 1 | 0 | 38952.4513 | 1 | 0 |  | 333 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38952.4535 | 1 | 0 | 38952.4535 | 1 | 0 |  | 518 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38952.4556 | 1 | 0 | 38952.4556 | 1 | 0 |  | 702.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38952.4577 | 1 | 0 | 38952.4578 | 1 | 0 |  | 887.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38952.4599 | 5 | 0 | 38952.4599 | 1997 | 0 |  | 1072 | 1232 | 0.30525 | 0 | 121.917 | 0 | 0.0030525 | 0 | 1.2192 | 0 | 0.0030525 | 1.2192 | 51947.6 | 30.3145 | 51947.5969
38952.462 | 3 | 0 | 38952.462 | 2257 | 0 |  | 1257 | 1417 | 0.18315 | 0 | 137.79 | 0 | 0.0018315 | 0 | 1.3779 | 0 | 0.0018315 | 1.3779 | 86646 | 15.3026 | 86645.9982
| 3 | 0 | 38952.4642 | 2586 | 0 |  | 1442 | 1602 | 0.18315 | 0 | 157.8755 | 0 | 0.0018315 | 0 | 1.5788 | 0 | 0.0018315 | 1.5788 | 86646 | 0.63341 | 86645.9982
38952.4663 | 3 | 0 | 38952.4663 | 2558 | 0 |  | 1626.5 | 1786.5 | 0.18315 | 0 | 156.1661 | 0 | 0.0018315 | 0 | 1.5617 | 0 | 0.0018315 | 1.5617 | 86646 | 1.7349 | 86645.9982
38952.4684 | 3 | 0 | 38952.4684 | 2038 | 0 |  | 1811.5 | 1971.5 | 0.18315 | 0 | 124.42 | 0 | 0.0018315 | 0 | 1.2442 | 0 | 0.0018315 | 1.2442 | 86646 | 27.6928 | 86645.9982

## C5-F11
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 155.0293 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38952.447 | 1 | 0 | 38952.447 | 1 | 0 |  | -39.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38952.4492 | 1 | 0 | 38952.4492 | 1 | 0 |  | 145.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38952.4513 | 1 | 0 | 38952.4513 | 1 | 0 |  | 330.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38952.4534 | 1 | 1 | 38952.4534 | 1 | 0 |  | 515 | 675 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 644337302.44 | 253838 | 253638.0788
38952.4556 | 1 | 0 | 38952.4556 | 1 | 0 |  | 700 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38952.4577 | 1 | 0 | 38952.4577 | 2 | 0 |  | 884.5 | 1044.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253838 | 126869 | 253837.9994
38952.4598 | 4 | 0 | 38952.4599 | 2396 | 0 |  | 1069.5 | 1229.5 | 0.2442 | 0 | 146.2759 | 0 | 0.002442 | 0 | 1.4628 | 0 | 0.002442 | 1.4628 | 63384.5 | 5.9841 | 63384.4976
38952.462 | 3 | 0 | 38952.462 | 2173 | 0 |  | 1254 | 1414 | 0.18315 | 0 | 132.6618 | 0 | 0.0018315 | 0 | 1.3266 | 0 | 0.0018315 | 1.3266 | 84546 | 16.8606 | 84545.9982
38952.4641 | 3 | 0 | 38952.4641 | 1622 | 0 |  | 1439 | 1599 | 0.18315 | 0 | 99.0232 | 0 | 0.0018315 | 0 | 0.99023 | 0 | 0.0018315 | 0.99023 | 84546 | 56.5586 | 84545.9982
38952.4663 | 3 | 0 | 38952.4663 | 2127 | 0 |  | 1623.5 | 1783.5 | 0.18315 | 0 | 129.8535 | 0 | 0.0018315 | 0 | 1.2985 | 0 | 0.0018315 | 1.2985 | 84546 | 19.3879 | 84545.9982
38952.4684 | 2 | 0 | 38952.4684 | 2523 | 0 |  | 1808.5 | 1968.5 | 0.1221 | 0 | 154.0293 | 0 | 0.001221 | 0 | 1.5403 | 0 | 0.001221 | 1.5403 | 126869 | 0.64923 | 126868.9988

## C5-E10
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 132.1355 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38952.447 | 1 | 0 | 38952.447 | 1 | 0 |  | -42 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216338 | 216338 | 216337.9994
38952.4491 | 1 | 0 | 38952.4491 | 1 | 0 |  | 142.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216338 | 216338 | 216337.9994
38952.4513 | 1 | 0 | 38952.4513 | 1 | 0 |  | 327.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216338 | 216338 | 216337.9994
38952.4534 | 1 | 0 | 38952.4534 | 1 | 0 |  | 512.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216338 | 216338 | 216337.9994
38952.4555 | 1 | 0 | 38952.4556 | 1 | 0 |  | 697 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216338 | 216338 | 216337.9994
38952.4577 | 1 | 0 | 38952.4577 | 1 | 0 |  | 882 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 216338 | 216338 | 216337.9994
38952.4598 | 3 | 0 | 38952.4598 | 2148 | 0 |  | 1066.5 | 1226.5 | 0.18315 | 0 | 131.1355 | 0 | 0.0018315 | 0 | 1.3114 | 0 | 0.0018315 | 1.3114 | 72046 | 0.76257 | 72045.9982
38952.462 | 3 | 0 | 38952.462 | 1847 | 0 |  | 1251.5 | 1411.5 | 0.18315 | 0 | 112.7595 | 0 | 0.0018315 | 0 | 1.1276 | 0 | 0.0018315 | 1.1276 | 72046 | 17.1835 | 72045.9982
38952.4641 | 3 | 0 | 38952.4641 | 1661 | 0 |  | 1436 | 1596 | 0.18315 | 0 | 101.4042 | 0 | 0.0018315 | 0 | 1.014 | 0 | 0.0018315 | 1.014 | 72046 | 30.3058 | 72045.9982
38952.4662 | 2 | 0 | 38952.4662 | 2 | 0 |  | 1621 | 1781 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 108119 | 108119 | 108118.9988
38952.4684 | 3 | 0 | 38952.4684 | 2 | 0 |  | 1805.5 | 1965.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 72046 | 108119 | 72045.9982

## C5-E9
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 157.9597 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38952.4469 | 1 | 0 | 38952.447 | 1 | 0 |  | -45 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38952.4491 | 2 | 0 | 38952.4491 | 1 | 0 |  | 140 | 300 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129269 | 258638 | 129268.9988
38952.4512 | 1 | 0 | 38952.4512 | 1 | 0 |  | 324.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38952.4534 | 1 | 0 | 38952.4534 | 1 | 0 |  | 509.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38952.4555 | 1 | 0 | 38952.4555 | 1 | 0 |  | 694.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38952.4576 | 1 | 0 | 38952.4577 | 1 | 0 |  | 879 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38952.4598 | 3 | 1 | 38952.4598 | 2571 | 1 |  | 1063.5 | 1223.5 | 0.18315 | 0.06105 | 156.9597 | 0.06105 | 0.0018315 | 0.0006105 | 1.5696 | 0.0006105 | 0.001221 | 1.569 | 1668.3934 | 0.65401 | 1678.5842
38952.4619 | 4 | 1 | 38952.4619 | 1568 | 0 |  | 1248.5 | 1408.5 | 0.2442 | 0.06105 | 95.7265 | 0 | 0.002442 | 0.0006105 | 0.95726 | 0 | 0.0018315 | 0.95726 | 176724.7309 | 65.0115 | 101741.0092
38952.4641 | 3 | 1 | 38952.4641 | 396 | 1 |  | 1433.5 | 1593.5 | 0.18315 | 0.06105 | 24.1758 | 0.06105 | 0.0018315 | 0.0006105 | 0.24176 | 0.0006105 | 0.001221 | 0.24115 | 142018.5178 | 554.7807 | 218883.8765
38952.4662 | 3 | 0 | 38952.4662 | 2 | 0 |  | 1618 | 1778 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 86146 | 129269 | 86145.9982
38952.4683 | 3 | 0 | 38952.4684 | 2 | 0 |  | 1803 | 1963 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 86146 | 129269 | 86145.9982

## C5-C6
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38952.4469 | 1 | 0 | 38952.4469 | 1 | 0 |  | -53.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.449 | 1 | 0 | 38952.449 | 1 | 0 |  | 131.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4511 | 1 | 0 | 38952.4511 | 1 | 0 |  | 316.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4533 | 1 | 1 | 38952.4533 | 1 | 0 |  | 501 | 661 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38952.4554 | 1 | 0 | 38952.4554 | 1 | 0 |  | 686 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4575 | 1 | 0 | 38952.4576 | 1 | 0 |  | 870.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4597 | 1021 | 973 | 38952.4597 | 1086 | 932 |  | 1055.5 | 1215.5 | 62.3321 | 59.4017 | 66.3004 | 56.8987 | 0.62332 | 0.59402 | 0.663 | 0.56899 | 0.029304 | 0.094017 | 213.5266 | 209.9602 | 8.2859
38952.4618 | 938 | 927 | 38952.4618 | 1029 | 1061 |  | 1240 | 1400 | 57.265 | 56.5934 | 62.8205 | 64.7741 | 0.57265 | 0.56593 | 0.62821 | 0.64774 | 0.0067155 | 0.019536 | 1635.8612 | 1523.9484 | 25.1076
38952.464 | 853 | 816 | 38952.464 | 951 | 1049 |  | 1425 | 1585 | 52.0757 | 49.8168 | 58.0586 | 64.0415 | 0.52076 | 0.49817 | 0.58059 | 0.64042 | 0.022589 | 0.059829 | 1644.9305 | 2060.5959 | 51.8957
38952.4661 | 1075 | 1051 | 38952.4661 | 861 | 954 |  | 1609.5 | 1769.5 | 65.6288 | 64.1636 | 52.5641 | 58.2418 | 0.65629 | 0.64164 | 0.52564 | 0.58242 | 0.014652 | 0.056777 | 438.6881 | 494.3111 | 1.0272
38952.4682 | 3 | 0 | 38952.4683 | 3 | 0 |  | 1794.5 | 1954.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## B4-E10
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 159.4249 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38952.4468 | 1 | 0 | 38952.4468 | 1 | 0 |  | -61.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
38952.4489 | 1 | 0 | 38952.4489 | 1 | 0 |  | 123 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
38952.451 | 1 | 0 | 38952.4511 | 1 | 0 |  | 308 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
38952.4532 | 1 | 0 | 38952.4532 | 1 | 0 |  | 492.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
38952.4553 | 1 | 0 | 38952.4553 | 1 | 0 |  | 677.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
38952.4574 | 1 | 0 | 38952.4575 | 1 | 0 |  | 862 | 1022 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261038 | 261038 | 261037.9994
38952.4596 | 2 | 0 | 38952.4596 | 2595 | 0 |  | 1047 | 1207 | 0.1221 | 0 | 158.4249 | 0 | 0.001221 | 0 | 1.5842 | 0 | 0.001221 | 1.5842 | 130469 | 0.63121 | 130468.9988
38952.4617 | 10 | 0 | 38952.4617 | 1695 | 0 |  | 1231.5 | 1391.5 | 0.6105 | 0 | 103.4799 | 0 | 0.006105 | 0 | 1.0348 | 0 | 0.006105 | 1.0348 | 26013.8 | 54.0637 | 26013.7939
38952.4639 | 3 | 0 | 38952.4639 | 1692 | 0 |  | 1416.5 | 1576.5 | 0.18315 | 0 | 103.2967 | 0 | 0.0018315 | 0 | 1.033 | 0 | 0.0018315 | 1.033 | 86946 | 54.3369 | 86945.9982
38952.466 | 2 | 0 | 38952.466 | 3 | 0 |  | 1601.5 | 1761.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 130469 | 86946 | 130468.9988
38952.4681 | 3 | 0 | 38952.4682 | 3 | 0 |  | 1786 | 1946 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 86946 | 86946 | 86945.9982

## B4-E9
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38952.4467 | 1 | 1 | 38952.4467 | 1 | 0 |  | -64.5 | 95.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38952.4489 | 1 | 0 | 38952.4489 | 1 | 0 |  | 120.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.451 | 1 | 0 | 38952.451 | 1 | 0 |  | 305 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4531 | 1 | 0 | 38952.4532 | 1 | 0 |  | 490 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4553 | 1 | 0 | 38952.4553 | 1 | 0 |  | 674.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4574 | 1 | 0 | 38952.4574 | 1 | 0 |  | 859.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4596 | 3 | 0 | 38952.4596 | 2 | 0 |  | 1044.5 | 1204.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.4617 | 85 | 0 | 38952.4617 | 1454 | 0 |  | 1229 | 1389 | 5.1893 | 0 | 88.7668 | 0 | 0.051893 | 0 | 0.88767 | 0 | 0.051893 | 0.88767 | 2385.9059 | 45.3246 | 2385.854
38952.4638 | 3 | 0 | 38952.4638 | 1930 | 0 |  | 1413.5 | 1573.5 | 0.18315 | 0 | 117.8266 | 0 | 0.0018315 | 0 | 1.1783 | 0 | 0.0018315 | 1.1783 | 70334 | 9.4829 | 70333.9982
38952.466 | 3 | 0 | 38952.466 | 3 | 0 |  | 1598.5 | 1758.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.4681 | 3 | 0 | 38952.4681 | 770 | 0 |  | 1783.5 | 1943.5 | 0.18315 | 0 | 47.0085 | 0 | 0.0018315 | 0 | 0.47009 | 0 | 0.0018315 | 0.47009 | 70334 | 174.4182 | 70333.9982

## B4-D8
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 154.1746 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38952.4467 | 1 | 0 | 38952.4467 | 1 | 0 |  | -67.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38952.4488 | 1 | 0 | 38952.4488 | 1 | 0 |  | 117.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38952.451 | 1 | 0 | 38952.451 | 1 | 0 |  | 302.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38952.4531 | 1 | 0 | 38952.4531 | 2 | 0 |  | 487 | 647 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252438 | 126169 | 252437.9994
38952.4552 | 1 | 0 | 38952.4553 | 1 | 0 |  | 672 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38952.4574 | 1 | 0 | 38952.4574 | 1 | 0 |  | 856.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38952.4595 | 3 | 0 | 38952.4595 | 2181 | 0 |  | 1041.5 | 1201.5 | 0.18315 | 0 | 133.1502 | 0 | 0.0018315 | 0 | 1.3315 | 0 | 0.0018315 | 1.3315 | 84079.3333 | 15.79 | 84079.3315
38952.4617 | 63 | 0 | 38952.4617 | 2509 | 0 |  | 1226 | 1386 | 3.8462 | 0 | 153.1746 | 0 | 0.038462 | 0 | 1.5317 | 0 | 0.038462 | 1.5317 | 3908.5397 | 0.65285 | 3908.5012
38952.4638 | 3 | 0 | 38952.4638 | 2396 | 0 |  | 1411 | 1571 | 0.18315 | 0 | 146.2759 | 0 | 0.0018315 | 0 | 1.4628 | 0 | 0.0018315 | 1.4628 | 84079.3333 | 5.3998 | 84079.3315
38952.4659 | 3 | 0 | 38952.4659 | 2190 | 0 |  | 1595.5 | 1755.5 | 0.18315 | 0 | 133.6996 | 0 | 0.0018315 | 0 | 1.337 | 0 | 0.0018315 | 1.337 | 84079.3333 | 15.3142 | 84079.3315
38952.4681 | 3 | 0 | 38952.4681 | 1983 | 0 |  | 1780.5 | 1940.5 | 0.18315 | 0 | 121.0623 | 0 | 0.0018315 | 0 | 1.2106 | 0 | 0.0018315 | 1.2106 | 84079.3333 | 27.3515 | 84079.3315

## B4-D7
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 157.4713 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38952.4467 | 1 | 0 | 38952.4467 | 1 | 0 |  | -70 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38952.4488 | 1 | 0 | 38952.4488 | 1 | 0 |  | 114.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38952.4509 | 1 | 0 | 38952.4509 | 1 | 0 |  | 299.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38952.4531 | 1 | 0 | 38952.4531 | 1 | 0 |  | 484.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38952.4552 | 1 | 0 | 38952.4552 | 1 | 0 |  | 669 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38952.4573 | 1 | 0 | 38952.4574 | 1 | 0 |  | 853.5 | 1013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
38952.4595 | 1 | 0 | 38952.4595 | 2509 | 0 |  | 1038.5 | 1198.5 | 0.06105 | 0 | 153.1746 | 0 | 0.0006105 | 0 | 1.5317 | 0 | 0.0006105 | 1.5317 | 257838 | 2.8051 | 257837.9994
38952.4616 | 18 | 0 | 38952.4616 | 2563 | 0 |  | 1223.5 | 1383.5 | 1.0989 | 0 | 156.4713 | 0 | 0.010989 | 0 | 1.5647 | 0 | 0.010989 | 1.5647 | 14229.8889 | 0.63909 | 14229.8779
38952.4638 | 3 | 0 | 38952.4638 | 2113 | 0 |  | 1408 | 1568 | 0.18315 | 0 | 128.9988 | 0 | 0.0018315 | 0 | 1.29 | 0 | 0.0018315 | 1.29 | 85879.3333 | 22.0719 | 85879.3315
38952.4659 | 3 | 0 | 38952.4659 | 2047 | 0 |  | 1593 | 1753 | 0.18315 | 0 | 124.9695 | 0 | 0.0018315 | 0 | 1.2497 | 0 | 0.0018315 | 1.2497 | 85879.3333 | 26.0078 | 85879.3315
38952.468 | 3 | 0 | 38952.4681 | 2540 | 0 |  | 1777.5 | 1937.5 | 0.18315 | 0 | 155.0672 | 0 | 0.0018315 | 0 | 1.5507 | 0 | 0.0018315 | 1.5507 | 85879.3333 | 1.5504 | 85879.3315

## B4-C6
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38952.4466 | 1 | 0 | 38952.4466 | 1 | 0 |  | -73 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4488 | 1 | 0 | 38952.4488 | 1 | 0 |  | 112 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4509 | 1 | 0 | 38952.4509 | 1 | 0 |  | 296.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.453 | 1 | 0 | 38952.4531 | 1 | 0 |  | 481.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4552 | 1 | 0 | 38952.4552 | 1 | 0 |  | 666.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4573 | 1 | 0 | 38952.4573 | 1 | 0 |  | 851 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4595 | 2 | 0 | 38952.4595 | 2 | 0 |  | 1035.5 | 1195.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.4616 | 94 | 0 | 38952.4616 | 3 | 0 |  | 1220.5 | 1380.5 | 5.7387 | 0 | 0.18315 | 0 | 0.057387 | 0 | 0.0018315 | 0 | 0.057387 | 0.0018315 | 2147.8936 | 70334 | 2147.8362
38952.4637 | 3 | 0 | 38952.4638 | 2 | 0 |  | 1405.5 | 1565.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.4659 | 3 | 0 | 38952.4659 | 3 | 0 |  | 1590 | 1750 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.468 | 3 | 0 | 38952.468 | 2 | 0 |  | 1775 | 1935 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982

## B4-C5
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38952.4466 | 1 | 0 | 38952.4466 | 1 | 0 |  | -75.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4487 | 1 | 0 | 38952.4488 | 1 | 0 |  | 109 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4509 | 1 | 0 | 38952.4509 | 1 | 0 |  | 294 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.453 | 1 | 0 | 38952.453 | 1 | 0 |  | 478.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4552 | 1 | 0 | 38952.4552 | 1 | 0 |  | 663.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4573 | 1 | 0 | 38952.4573 | 1 | 0 |  | 848.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4594 | 3 | 0 | 38952.4594 | 2 | 0 |  | 1033 | 1193 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.4616 | 59 | 0 | 38952.4616 | 3 | 0 |  | 1217.5 | 1377.5 | 3.602 | 0 | 0.18315 | 0 | 0.03602 | 0 | 0.0018315 | 0 | 0.03602 | 0.0018315 | 3481.3898 | 70334 | 3481.3538
38952.4637 | 3 | 0 | 38952.4637 | 3 | 0 |  | 1402.5 | 1562.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.4658 | 3 | 0 | 38952.4659 | 2 | 0 |  | 1587.5 | 1747.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.468 | 3 | 0 | 38952.468 | 3 | 0 |  | 1772 | 1932 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## B3-E10
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38952.4465 | 1 | 0 | 38952.4465 | 1 | 0 |  | -84 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4486 | 1 | 0 | 38952.4486 | 1 | 0 |  | 100.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4508 | 1 | 0 | 38952.4508 | 1 | 0 |  | 285.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4529 | 1 | 0 | 38952.4529 | 1 | 0 |  | 470.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.455 | 1 | 0 | 38952.4551 | 2 | 0 |  | 655 | 815 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.4572 | 1 | 0 | 38952.4572 | 1 | 0 |  | 839.5 | 999.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4593 | 3 | 0 | 38952.4593 | 2 | 0 |  | 1024.5 | 1184.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.4615 | 15 | 0 | 38952.4615 | 1747 | 0 |  | 1209.5 | 1369.5 | 0.91575 | 0 | 106.6545 | 0 | 0.0091575 | 0 | 1.0665 | 0 | 0.0091575 | 1.0665 | 13986.8 | 20.9513 | 13986.7908
38952.4636 | 3 | 0 | 38952.4636 | 1277 | 0 |  | 1394 | 1554 | 0.18315 | 0 | 77.9609 | 0 | 0.0018315 | 0 | 0.77961 | 0 | 0.0018315 | 0.77961 | 70334 | 65.4675 | 70333.9982
38952.4657 | 3 | 0 | 38952.4658 | 3 | 0 |  | 1579 | 1739 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.4679 | 3 | 0 | 38952.4679 | 2 | 0 |  | 1763.5 | 1923.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982

## B3-E9
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38952.4465 | 1 | 0 | 38952.4465 | 1 | 0 |  | -87 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4486 | 1 | 0 | 38952.4486 | 1 | 0 |  | 98 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4507 | 1 | 0 | 38952.4508 | 1 | 0 |  | 282.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4529 | 1 | 0 | 38952.4529 | 1 | 0 |  | 467.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.455 | 1 | 0 | 38952.455 | 1 | 0 |  | 652 | 812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4572 | 1 | 0 | 38952.4572 | 1 | 0 |  | 837 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4593 | 3 | 0 | 38952.4593 | 3 | 0 |  | 1021.5 | 1181.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.4614 | 87 | 0 | 38952.4614 | 1884 | 0 |  | 1206.5 | 1366.5 | 5.3114 | 0 | 115.0183 | 0 | 0.053114 | 0 | 1.1502 | 0 | 0.053114 | 1.1502 | 2328.7586 | 12.1561 | 2328.7055
38952.4636 | 3 | 0 | 38952.4636 | 1613 | 0 |  | 1391.5 | 1551.5 | 0.18315 | 0 | 98.4737 | 0 | 0.0018315 | 0 | 0.98474 | 0 | 0.0018315 | 0.98474 | 70334 | 30.9994 | 70333.9982
38952.4657 | 3 | 0 | 38952.4657 | 2 | 0 |  | 1576 | 1736 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.4678 | 3 | 0 | 38952.4679 | 3 | 0 |  | 1761 | 1921 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## B3-D8
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 156.9829 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38952.4464 | 1 | 0 | 38952.4464 | 1 | 0 |  | -89.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38952.4486 | 1 | 0 | 38952.4486 | 1 | 0 |  | 95 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38952.4507 | 1 | 0 | 38952.4507 | 1 | 0 |  | 280 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38952.4528 | 1 | 0 | 38952.4529 | 1 | 0 |  | 464.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38952.455 | 1 | 0 | 38952.455 | 1 | 0 |  | 649.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38952.4571 | 1 | 0 | 38952.4571 | 1 | 0 |  | 834.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38952.4593 | 3 | 0 | 38952.4593 | 2555 | 0 |  | 1019 | 1179 | 0.18315 | 0 | 155.9829 | 0 | 0.0018315 | 0 | 1.5598 | 0 | 0.0018315 | 1.5598 | 85612.6667 | 0.6411 | 85612.6648
38952.4614 | 29 | 0 | 38952.4614 | 2522 | 0 |  | 1203.5 | 1363.5 | 1.7705 | 0 | 153.9683 | 0 | 0.017705 | 0 | 1.5397 | 0 | 0.017705 | 1.5397 | 8766.8276 | 1.958 | 8766.8099
38952.4635 | 3 | 0 | 38952.4636 | 2347 | 0 |  | 1388.5 | 1548.5 | 0.18315 | 0 | 143.2845 | 0 | 0.0018315 | 0 | 1.4328 | 0 | 0.0018315 | 1.4328 | 85612.6667 | 9.5603 | 85612.6648
38952.4657 | 3 | 0 | 38952.4657 | 2207 | 0 |  | 1573.5 | 1733.5 | 0.18315 | 0 | 134.7375 | 0 | 0.0018315 | 0 | 1.3474 | 0 | 0.0018315 | 1.3474 | 85612.6667 | 16.5102 | 85612.6648
38952.4678 | 3 | 0 | 38952.4678 | 1956 | 0 |  | 1758 | 1918 | 0.18315 | 0 | 119.4139 | 0 | 0.0018315 | 0 | 1.1941 | 0 | 0.0018315 | 1.1941 | 85612.6667 | 31.4611 | 85612.6648

## B3-D7
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 159.6691 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38952.4464 | 1 | 0 | 38952.4464 | 1 | 0 |  | -92.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38952.4485 | 1 | 0 | 38952.4486 | 1 | 0 |  | 92.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38952.4507 | 1 | 0 | 38952.4507 | 1 | 0 |  | 277 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38952.4528 | 1 | 0 | 38952.4528 | 1 | 0 |  | 462 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38952.455 | 1 | 0 | 38952.455 | 1 | 0 |  | 646.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38952.4571 | 1 | 0 | 38952.4571 | 1 | 0 |  | 831.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261438 | 261438 | 261437.9994
38952.4592 | 2 | 0 | 38952.4592 | 2100 | 0 |  | 1016.5 | 1176.5 | 0.1221 | 0 | 128.2051 | 0 | 0.001221 | 0 | 1.2821 | 0 | 0.001221 | 1.2821 | 130669 | 24.5419 | 130668.9988
38952.4614 | 132 | 0 | 38952.4614 | 2599 | 0 |  | 1201 | 1361 | 8.0586 | 0 | 158.6691 | 0 | 0.080586 | 0 | 1.5867 | 0 | 0.080586 | 1.5867 | 1881.3485 | 0.63024 | 1881.2679
38952.4635 | 2 | 0 | 38952.4635 | 2218 | 0 |  | 1385.5 | 1545.5 | 0.1221 | 0 | 135.409 | 0 | 0.001221 | 0 | 1.3541 | 0 | 0.001221 | 1.3541 | 130669 | 17.9161 | 130668.9988
38952.4656 | 3 | 0 | 38952.4657 | 2219 | 0 |  | 1570.5 | 1730.5 | 0.18315 | 0 | 135.4701 | 0 | 0.0018315 | 0 | 1.3547 | 0 | 0.0018315 | 1.3547 | 87079.3333 | 17.863 | 87079.3315
38952.4678 | 2 | 0 | 38952.4678 | 2019 | 0 |  | 1755.5 | 1915.5 | 0.1221 | 0 | 123.2601 | 0 | 0.001221 | 0 | 1.2326 | 0 | 0.001221 | 1.2326 | 130669 | 29.5384 | 130668.9988

## B3-C6
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38952.4464 | 1 | 0 | 38952.4464 | 1 | 0 |  | -95.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4485 | 1 | 0 | 38952.4485 | 1 | 0 |  | 89.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4506 | 1 | 0 | 38952.4507 | 1 | 0 |  | 274.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4528 | 1 | 0 | 38952.4528 | 1 | 0 |  | 459 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4549 | 1 | 0 | 38952.4549 | 1 | 0 |  | 644 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4571 | 1 | 0 | 38952.4571 | 1 | 0 |  | 828.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4592 | 2 | 0 | 38952.4592 | 1 | 0 |  | 1013.5 | 1173.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.4613 | 705 | 0 | 38952.4614 | 125 | 0 |  | 1198 | 1358 | 43.0403 | 0 | 7.6313 | 0 | 0.4304 | 0 | 0.076313 | 0 | 0.4304 | 0.076313 | 199.7191 | 1590.416 | 199.2887
38952.4635 | 3 | 1 | 38952.4635 | 3 | 0 |  | 1383 | 1543 | 0.18315 | 0.06105 | 0.18315 | 0 | 0.0018315 | 0.0006105 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105576.0534 | 70334 | 210602.5679
38952.4656 | 3 | 0 | 38952.4656 | 3 | 0 |  | 1567.5 | 1727.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.4678 | 3 | 0 | 38952.4678 | 3 | 0 |  | 1752.5 | 1912.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## B3-C5
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38952.4463 | 1 | 0 | 38952.4464 | 1 | 0 |  | -98 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4485 | 1 | 0 | 38952.4485 | 1 | 0 |  | 86.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4506 | 1 | 0 | 38952.4506 | 1 | 0 |  | 271.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4528 | 1 | 0 | 38952.4528 | 1 | 0 |  | 456.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4549 | 1 | 0 | 38952.4549 | 1 | 0 |  | 641 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.457 | 1 | 0 | 38952.457 | 1 | 0 |  | 826 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4592 | 2 | 0 | 38952.4592 | 2 | 0 |  | 1010.5 | 1170.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.4613 | 535 | 2 | 38952.4613 | 376 | 1 |  | 1195.5 | 1355.5 | 32.6618 | 0.1221 | 22.9548 | 0.06105 | 0.32662 | 0.001221 | 0.22955 | 0.0006105 | 0.3254 | 0.22894 | 296.3036 | 463.6226 | 64819.8356
38952.4634 | 3 | 2 | 38952.4635 | 3 | 1 |  | 1380 | 1540 | 0.18315 | 0.1221 | 0.18315 | 0.06105 | 0.0018315 | 0.001221 | 0.0018315 | 0.0006105 | 0.0006105 | 0.001221 | 211402.6648 | 105525.9585 | 105301.213
38952.4656 | 3 | 1 | 38952.4656 | 3 | 0 |  | 1565 | 1725 | 0.18315 | 0.06105 | 0.18315 | 0 | 0.0018315 | 0.0006105 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105576.0534 | 70334 | 210602.5679
38952.4677 | 3 | 0 | 38952.4677 | 3 | 0 |  | 1749.5 | 1909.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## B3-B4
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38952.4463 | 1 | 0 | 38952.4463 | 1 | 0 |  | -101 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4484 | 1 | 0 | 38952.4485 | 1 | 0 |  | 84 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4506 | 1 | 0 | 38952.4506 | 1 | 0 |  | 268.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4527 | 1 | 0 | 38952.4527 | 1 | 0 |  | 453.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4549 | 1 | 0 | 38952.4549 | 1 | 0 |  | 638.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.457 | 1 | 0 | 38952.457 | 1 | 0 |  | 823 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4591 | 4 | 0 | 38952.4591 | 3 | 0 |  | 1007.5 | 1167.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.4613 | 1212 | 309 | 38952.4613 | 600 | 490 |  | 1192.5 | 1352.5 | 73.9927 | 18.8645 | 36.63 | 29.9145 | 0.73993 | 0.18864 | 0.3663 | 0.29915 | 0.55128 | 0.067155 | 90.9616 | 352.9412 | 149.2927
38952.4634 | 487 | 449 | 38952.4634 | 738 | 749 |  | 1377.5 | 1537.5 | 29.7314 | 27.4115 | 45.0549 | 45.7265 | 0.29731 | 0.27411 | 0.45055 | 0.45726 | 0.023199 | 0.0067155 | 4014.8771 | 17960.9355 | 260.6911
38952.4655 | 18 | 14 | 38952.4656 | 114 | 108 |  | 1562 | 1722 | 1.0989 | 0.8547 | 6.9597 | 6.5934 | 0.010989 | 0.008547 | 0.069597 | 0.065934 | 0.002442 | 0.003663 | 52912.4438 | 34490.3072 | 14821.4558
38952.4677 | 3 | 0 | 38952.4677 | 3 | 0 |  | 1746.5 | 1906.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## A2-C6
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38952.4461 | 1 | 0 | 38952.4461 | 1 | 0 |  | -120.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4482 | 1 | 0 | 38952.4482 | 1 | 0 |  | 64.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4503 | 1 | 0 | 38952.4504 | 2 | 0 |  | 249 | 409 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.4525 | 1 | 0 | 38952.4525 | 1 | 0 |  | 434 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4546 | 1 | 0 | 38952.4546 | 1 | 0 |  | 618.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4568 | 1 | 0 | 38952.4568 | 1 | 0 |  | 803.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4589 | 2 | 0 | 38952.4589 | 2 | 0 |  | 988.5 | 1148.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.461 | 3 | 1 | 38952.4611 | 964 | 1 |  | 1173 | 1333 | 0.18315 | 0.06105 | 58.8523 | 0.06105 | 0.0018315 | 0.0006105 | 0.58852 | 0.0006105 | 0.001221 | 0.58791 | 181601.6135 | 119.3168 | 114738.8184
38952.4632 | 27 | 0 | 38952.4632 | 3 | 0 |  | 1357.5 | 1517.5 | 1.6484 | 0 | 0.18315 | 0 | 0.016484 | 0 | 0.0018315 | 0 | 0.016484 | 0.0018315 | 7726 | 70334 | 7725.9835
38952.4653 | 2 | 0 | 38952.4653 | 3 | 0 |  | 1542.5 | 1702.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.4675 | 3 | 0 | 38952.4675 | 2 | 0 |  | 1727.5 | 1887.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982

## A2-C5
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38952.446 | 1 | 0 | 38952.4461 | 1 | 0 |  | -123.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4482 | 1 | 0 | 38952.4482 | 1 | 0 |  | 61.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4503 | 1 | 0 | 38952.4503 | 1 | 0 |  | 246.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4525 | 1 | 0 | 38952.4525 | 1 | 0 |  | 431 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4546 | 1 | 0 | 38952.4546 | 1 | 0 |  | 616 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4567 | 1 | 0 | 38952.4567 | 1 | 0 |  | 800.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4589 | 2 | 0 | 38952.4589 | 2 | 1 |  | 985.5 | 1145.5 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.461 | 4 | 3 | 38952.461 | 318 | 2 |  | 1170 | 1330 | 0.2442 | 0.18315 | 19.4139 | 0.1221 | 0.002442 | 0.0018315 | 0.19414 | 0.001221 | 0.0006105 | 0.19292 | 446946.5987 | 568.0451 | 59692.2944
38952.4631 | 29 | 0 | 38952.4632 | 3 | 0 |  | 1355 | 1515 | 1.7705 | 0 | 0.18315 | 0 | 0.017705 | 0 | 0.0018315 | 0 | 0.017705 | 0.0018315 | 7186.2759 | 70334 | 7186.2582
38952.4653 | 2 | 0 | 38952.4653 | 3 | 0 |  | 1539.5 | 1699.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.4674 | 3 | 0 | 38952.4674 | 3 | 0 |  | 1724.5 | 1884.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## A2-B4
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38952.446 | 1 | 0 | 38952.446 | 1 | 0 |  | -126 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4481 | 1 | 0 | 38952.4482 | 1 | 0 |  | 58.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4503 | 1 | 0 | 38952.4503 | 1 | 0 |  | 243.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4524 | 1 | 0 | 38952.4524 | 1 | 0 |  | 428.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4546 | 1 | 0 | 38952.4546 | 1 | 0 |  | 613 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4567 | 1 | 0 | 38952.4567 | 1 | 0 |  | 798 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4588 | 2 | 0 | 38952.4589 | 2 | 0 |  | 982.5 | 1142.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.461 | 675 | 579 | 38952.461 | 795 | 694 |  | 1167.5 | 1327.5 | 41.2088 | 35.348 | 48.5348 | 42.3687 | 0.41209 | 0.35348 | 0.48535 | 0.42369 | 0.058608 | 0.061661 | 2194.6994 | 1899.7567 | 140.9437
38952.4631 | 30 | 0 | 38952.4631 | 44 | 0 |  | 1352 | 1512 | 1.8315 | 0 | 2.6862 | 0 | 0.018315 | 0 | 0.026862 | 0 | 0.018315 | 0.026862 | 6943.4 | 4702.3182 | 6943.3817
38952.4653 | 2 | 0 | 38952.4653 | 2 | 0 |  | 1537 | 1697 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.4674 | 3 | 0 | 38952.4674 | 2 | 0 |  | 1721.5 | 1881.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982

## A2-B3
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38952.446 | 1 | 1 | 38952.446 | 1 | 0 |  | -128.5 | 31.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38952.4481 | 1 | 0 | 38952.4481 | 1 | 0 |  | 56 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4503 | 1 | 1 | 38952.4503 | 1 | 0 |  | 240.5 | 400.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38952.4524 | 1 | 0 | 38952.4524 | 1 | 0 |  | 425.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4545 | 1 | 0 | 38952.4545 | 1 | 0 |  | 610 | 770 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4567 | 1 | 0 | 38952.4567 | 1 | 0 |  | 795 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4588 | 3 | 0 | 38952.4588 | 2 | 0 |  | 979.5 | 1139.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.4609 | 935 | 559 | 38952.461 | 1005 | 800 |  | 1164.5 | 1324.5 | 57.0818 | 34.127 | 61.3553 | 48.84 | 0.57082 | 0.34127 | 0.61355 | 0.4884 | 0.22955 | 0.12515 | 284.1097 | 1446.8539 | 103.5782
38952.4631 | 14 | 0 | 38952.4631 | 6 | 0 |  | 1349.5 | 1509.5 | 0.8547 | 0 | 0.3663 | 0 | 0.008547 | 0 | 0.003663 | 0 | 0.008547 | 0.003663 | 14993 | 35117 | 14992.9915
38952.4652 | 3 | 0 | 38952.4652 | 2 | 0 |  | 1534 | 1694 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.4674 | 3 | 0 | 38952.4674 | 4 | 0 |  | 1719 | 1879 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 70334 | 52725.5 | 70333.9982

## A1-C6
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38952.4458 | 1 | 0 | 38952.4458 | 1 | 0 |  | -148.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4479 | 1 | 0 | 38952.4479 | 1 | 0 |  | 36.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.45 | 1 | 0 | 38952.45 | 1 | 0 |  | 221 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4522 | 1 | 0 | 38952.4522 | 1 | 0 |  | 406 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4543 | 1 | 0 | 38952.4543 | 1 | 0 |  | 590.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4564 | 1 | 0 | 38952.4565 | 1 | 0 |  | 775.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4586 | 2 | 0 | 38952.4586 | 2 | 0 |  | 960.5 | 1120.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.4607 | 235 | 2 | 38952.4607 | 40 | 2 |  | 1145 | 1305 | 14.3468 | 0.1221 | 2.442 | 0.1221 | 0.14347 | 0.001221 | 0.02442 | 0.001221 | 0.14225 | 0.023199 | 806.1432 | 5491.1666 | 92123.3358
38952.4629 | 4 | 0 | 38952.4629 | 3 | 0 |  | 1329.5 | 1489.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.465 | 2 | 0 | 38952.465 | 2 | 0 |  | 1514.5 | 1674.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.4671 | 2 | 0 | 38952.4672 | 3 | 0 |  | 1699.5 | 1859.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988

## A1-C5
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38952.4457 | 1 | 0 | 38952.4457 | 1 | 0 |  | -151.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4479 | 1 | 0 | 38952.4479 | 1 | 0 |  | 33.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.45 | 1 | 0 | 38952.45 | 1 | 0 |  | 218.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4521 | 1 | 0 | 38952.4522 | 1 | 0 |  | 403 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4543 | 1 | 0 | 38952.4543 | 1 | 0 |  | 588 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4564 | 1 | 0 | 38952.4564 | 1 | 0 |  | 772.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4586 | 3 | 1 | 38952.4586 | 2 | 1 |  | 957.5 | 1117.5 | 0.18315 | 0.06105 | 0.1221 | 0.06105 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 105525.9704 | 211302.2372 | 210802.2366
38952.4607 | 267 | 4 | 38952.4607 | 30 | 3 |  | 1142 | 1302 | 16.3004 | 0.2442 | 1.8315 | 0.18315 | 0.163 | 0.002442 | 0.018315 | 0.0018315 | 0.16056 | 0.016484 | 702.045 | 7838.9543 | 45470.4425
38952.4628 | 23 | 0 | 38952.4628 | 3 | 0 |  | 1327 | 1487 | 1.4042 | 0 | 0.18315 | 0 | 0.014042 | 0 | 0.0018315 | 0 | 0.014042 | 0.0018315 | 9087.0435 | 70334 | 9087.0294
38952.465 | 3 | 1 | 38952.465 | 3 | 0 |  | 1511.5 | 1671.5 | 0.18315 | 0.06105 | 0.18315 | 0 | 0.0018315 | 0.0006105 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105576.0534 | 70334 | 210602.5679
38952.4671 | 2 | 1 | 38952.4671 | 3 | 0 |  | 1696.5 | 1856.5 | 0.1221 | 0.06105 | 0.18315 | 0 | 0.001221 | 0.0006105 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 211402.5695 | 70334 | 210702.4259

## A1-B4
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38952.4457 | 1 | 0 | 38952.4457 | 1 | 0 |  | -154 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4478 | 1 | 0 | 38952.4478 | 1 | 0 |  | 30.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.45 | 1 | 0 | 38952.45 | 1 | 0 |  | 215.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4521 | 1 | 0 | 38952.4521 | 1 | 0 |  | 400.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4542 | 1 | 0 | 38952.4543 | 1 | 0 |  | 585 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4564 | 1 | 0 | 38952.4564 | 1 | 0 |  | 770 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4585 | 3 | 1 | 38952.4585 | 3 | 1 |  | 954.5 | 1114.5 | 0.18315 | 0.06105 | 0.18315 | 0.06105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.0006105 | 0.001221 | 0.001221 | 105551 | 105551 | 210702.3786
38952.4607 | 777 | 687 | 38952.4607 | 909 | 775 |  | 1139.5 | 1299.5 | 47.4359 | 41.9414 | 55.4945 | 47.3138 | 0.47436 | 0.41941 | 0.55495 | 0.47314 | 0.054945 | 0.081807 | 6600.7299 | 984.8119 | 85.763
38952.4628 | 92 | 1 | 38952.4628 | 5 | 0 |  | 1324 | 1484 | 5.6166 | 0.06105 | 0.30525 | 0 | 0.056166 | 0.0006105 | 0.0030525 | 0 | 0.055556 | 0.0030525 | 2220.959 | 42160.4 | 201524.0064
38952.4649 | 3 | 1 | 38952.465 | 3 | 1 |  | 1509 | 1669 | 0.18315 | 0.06105 | 0.18315 | 0.06105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.0006105 | 0.001221 | 0.001221 | 105551 | 105551 | 210702.3786
38952.4671 | 3 | 1 | 38952.4671 | 2 | 1 |  | 1693.5 | 1853.5 | 0.18315 | 0.06105 | 0.1221 | 0.06105 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 105525.9704 | 211302.2372 | 210802.2366

## A1-B3
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38952.4456 | 1 | 0 | 38952.4457 | 1 | 0 |  | -157 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4478 | 1 | 0 | 38952.4478 | 1 | 0 |  | 28 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4499 | 1 | 0 | 38952.4499 | 1 | 0 |  | 212.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4521 | 1 | 0 | 38952.4521 | 1 | 0 |  | 397.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4542 | 1 | 0 | 38952.4542 | 1 | 0 |  | 582.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4563 | 1 | 0 | 38952.4564 | 1 | 0 |  | 767 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4585 | 3 | 6 | 38952.4585 | 3 | 2 |  | 952 | 1112 | 0.18315 | 0.3663 | 0.18315 | 0.1221 | 0.0018315 | 0.003663 | 0.0018315 | 0.001221 | 0.0018315 | 0.0006105 | 70400.5402 | 211603.1407 | 35050.4358
38952.4606 | 892 | 479 | 38952.4606 | 771 | 664 |  | 1136.5 | 1296.5 | 54.4567 | 29.243 | 47.0696 | 40.5372 | 0.54457 | 0.29243 | 0.4707 | 0.40537 | 0.25214 | 0.065324 | 262.5396 | 919.7318 | 139.719
38952.4628 | 63 | 3 | 38952.4628 | 405 | 2 |  | 1321.5 | 1481.5 | 3.8462 | 0.18315 | 24.7253 | 0.1221 | 0.038462 | 0.0018315 | 0.24725 | 0.001221 | 0.03663 | 0.24603 | 3457.4831 | 423.8871 | 55209.4392
38952.4649 | 3 | 4 | 38952.4649 | 3 | 2 |  | 1506 | 1666 | 0.18315 | 0.2442 | 0.18315 | 0.1221 | 0.0018315 | 0.002442 | 0.0018315 | 0.001221 | 0.0006105 | 0.0006105 | 211402.3799 | 211201.8102 | 52625.5828
38952.467 | 3 | 5 | 38952.4671 | 3 | 2 |  | 1691 | 1851 | 0.18315 | 0.30525 | 0.18315 | 0.1221 | 0.0018315 | 0.0030525 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 105625.911 | 211402.2849 | 42080.4946

## A1-A2
Penlight Test 60 |  |  | 2006-08-23 | 10:44 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38952.4456 | 1 | 0 | 38952.4456 | 1 | 0 |  | -159.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4478 | 1 | 0 | 38952.4478 | 1 | 0 |  | 25 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4499 | 1 | 0 | 38952.4499 | 1 | 0 |  | 210 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.452 | 1 | 0 | 38952.452 | 1 | 0 |  | 394.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4542 | 1 | 0 | 38952.4542 | 1 | 0 |  | 579.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4563 | 1 | 0 | 38952.4563 | 1 | 0 |  | 764.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.4584 | 1077 | 1126 | 38952.4585 | 1209 | 1194 |  | 949 | 1109 | 65.7509 | 68.7424 | 73.8095 | 72.8938 | 0.65751 | 0.68742 | 0.7381 | 0.72894 | 0.029915 | 0.0091575 | 1488.1654 | 5461.4433 | 7.8474
38952.4606 | 1191 | 1094 | 38952.4606 | 1119 | 1009 |  | 1133.5 | 1293.5 | 72.7106 | 66.7888 | 68.315 | 61.5995 | 0.72711 | 0.66789 | 0.68315 | 0.616 | 0.059219 | 0.067155 | 783.1907 | 5278.3636 | 15.428
38952.4627 | 750 | 721 | 38952.4627 | 1006 | 904 |  | 1318.5 | 1478.5 | 45.7875 | 44.0171 | 61.4164 | 55.1893 | 0.45788 | 0.44017 | 0.61416 | 0.55189 | 0.017705 | 0.062271 | 2068.3858 | 1954.048 | 84.7106
38952.4649 | 796 | 816 | 38952.4649 | 1004 | 1033 |  | 1503.5 | 1663.5 | 48.5958 | 49.8168 | 61.2943 | 63.0647 | 0.48596 | 0.49817 | 0.61294 | 0.63065 | 0.01221 | 0.017705 | 41633.4268 | 4846.5761 | 60.1583
38952.467 | 1096 | 1155 | 38952.467 | 1004 | 974 |  | 1688 | 1848 | 66.9109 | 70.5128 | 61.2943 | 59.4628 | 0.66911 | 0.70513 | 0.61294 | 0.59463 | 0.03602 | 0.018315 | 9.5039 | 10.8532 | 1.1696

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 60 |  |  | 2006-08-23 | 10:44
38952.4456 | 1 | 0 | 1 | TS/TP | 7-C | Tray
38952.4478 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38952.4499 | 1 | 0 | 1
38952.452 | 1 | 0 | 1
38952.4542 | 1 | 0 | 1
38952.4563 | 1 | 0 | 1
38952.4584 | 1077 | 1126 | 1
38952.4606 | 1191 | 1094 | 1
38952.4627 | 750 | 721 | 1
38952.4649 | 796 | 816 | 1
38952.467 | 1096 | 1155 | 1
1
38952.4456 | 1 | 0 | 2
38952.4478 | 1 | 0 | 2
38952.4499 | 1 | 0 | 2
38952.452 | 1 | 0 | 2
38952.4542 | 1 | 0 | 2
38952.4563 | 1 | 0 | 2
38952.4585 | 1209 | 1194 | 2
38952.4606 | 1119 | 1009 | 2
38952.4627 | 1006 | 904 | 2
38952.4649 | 1004 | 1033 | 2
38952.467 | 1004 | 974 | 2
2
38952.4456 | 1 | 0 | 3
38952.4478 | 1 | 0 | 3
38952.4499 | 1 | 0 | 3
38952.4521 | 1 | 0 | 3
38952.4542 | 1 | 0 | 3
38952.4563 | 1 | 0 | 3
38952.4585 | 3 | 6 | 3
38952.4606 | 892 | 479 | 3
38952.4628 | 63 | 3 | 3
38952.4649 | 3 | 4 | 3
38952.467 | 3 | 5 | 3
3
38952.4457 | 1 | 0 | 4
38952.4478 | 1 | 0 | 4
38952.4499 | 1 | 0 | 4
38952.4521 | 1 | 0 | 4
38952.4542 | 1 | 0 | 4
38952.4564 | 1 | 0 | 4
38952.4585 | 3 | 2 | 4
38952.4606 | 771 | 664 | 4
38952.4628 | 405 | 2 | 4
38952.4649 | 3 | 2 | 4
38952.4671 | 3 | 2 | 4
4
38952.4457 | 1 | 0 | 5
38952.4478 | 1 | 0 | 5
38952.45 | 1 | 0 | 5
38952.4521 | 1 | 0 | 5
38952.4542 | 1 | 0 | 5
38952.4564 | 1 | 0 | 5
38952.4585 | 3 | 1 | 5
38952.4607 | 777 | 687 | 5
38952.4628 | 92 | 1 | 5
38952.4649 | 3 | 1 | 5
38952.4671 | 3 | 1 | 5
5
38952.4457 | 1 | 0 | 6
38952.4478 | 1 | 0 | 6
38952.45 | 1 | 0 | 6
38952.4521 | 1 | 0 | 6
38952.4543 | 1 | 0 | 6
38952.4564 | 1 | 0 | 6
38952.4585 | 3 | 1 | 6
38952.4607 | 909 | 775 | 6
38952.4628 | 5 | 0 | 6
38952.465 | 3 | 1 | 6
38952.4671 | 2 | 1 | 6
6
38952.4457 | 1 | 0 | 7
38952.4479 | 1 | 0 | 7
38952.45 | 1 | 0 | 7
38952.4521 | 1 | 0 | 7
38952.4543 | 1 | 0 | 7
38952.4564 | 1 | 0 | 7
38952.4586 | 3 | 1 | 7
38952.4607 | 267 | 4 | 7
38952.4628 | 23 | 0 | 7
38952.465 | 3 | 1 | 7
38952.4671 | 2 | 1 | 7
7
38952.4457 | 1 | 0 | 8
38952.4479 | 1 | 0 | 8
38952.45 | 1 | 0 | 8
38952.4522 | 1 | 0 | 8
38952.4543 | 1 | 0 | 8
38952.4564 | 1 | 0 | 8
38952.4586 | 2 | 1 | 8
38952.4607 | 30 | 3 | 8
38952.4628 | 3 | 0 | 8
38952.465 | 3 | 0 | 8
38952.4671 | 3 | 0 | 8
8
38952.4458 | 1 | 0 | 9
38952.4479 | 1 | 0 | 9
38952.45 | 1 | 0 | 9
38952.4522 | 1 | 0 | 9
38952.4543 | 1 | 0 | 9
38952.4564 | 1 | 0 | 9
38952.4586 | 2 | 0 | 9
38952.4607 | 235 | 2 | 9
38952.4629 | 4 | 0 | 9
38952.465 | 2 | 0 | 9
38952.4671 | 2 | 0 | 9
9
38952.4458 | 1 | 0 | 10
38952.4479 | 1 | 0 | 10
38952.45 | 1 | 0 | 10
38952.4522 | 1 | 0 | 10
38952.4543 | 1 | 0 | 10
38952.4565 | 1 | 0 | 10
38952.4586 | 2 | 0 | 10
38952.4607 | 40 | 2 | 10
38952.4629 | 3 | 0 | 10
38952.465 | 2 | 0 | 10
38952.4672 | 3 | 0 | 10
10
38952.4458 | 1 | 0 | 11
38952.4479 | 1 | 0 | 11
38952.4501 | 1 | 0 | 11
38952.4522 | 1 | 0 | 11
38952.4543 | 1 | 0 | 11
38952.4565 | 1 | 0 | 11
38952.4586 | 2 | 0 | 11
38952.4608 | 732 | 1 | 11
38952.4629 | 4 | 0 | 11
38952.465 | 3 | 0 | 11
38952.4672 | 3 | 0 | 11
11
38952.4458 | 1 | 0 | 12
38952.4479 | 1 | 0 | 12
38952.4501 | 1 | 1 | 12
38952.4522 | 1 | 0 | 12
38952.4544 | 1 | 0 | 12
38952.4565 | 1 | 0 | 12
38952.4586 | 2 | 0 | 12
38952.4608 | 2079 | 1 | 12
38952.4629 | 2246 | 0 | 12
38952.465 | 2307 | 0 | 12
38952.4672 | 1988 | 0 | 12
12
38952.4458 | 1 | 0 | 13
38952.448 | 1 | 0 | 13
38952.4501 | 1 | 0 | 13
38952.4522 | 1 | 0 | 13
38952.4544 | 1 | 0 | 13
38952.4565 | 1 | 0 | 13
38952.4586 | 2 | 0 | 13
38952.4608 | 66 | 1 | 13
38952.4629 | 7 | 0 | 13
38952.4651 | 3 | 0 | 13
38952.4672 | 3 | 0 | 13
13
38952.4458 | 1 | 0 | 14
38952.448 | 1 | 0 | 14
38952.4501 | 1 | 0 | 14
38952.4522 | 1 | 0 | 14
38952.4544 | 1 | 0 | 14
38952.4565 | 1 | 0 | 14
38952.4587 | 2 | 0 | 14
38952.4608 | 2521 | 0 | 14
38952.4629 | 2466 | 0 | 14
38952.4651 | 1987 | 0 | 14
38952.4672 | 1662 | 0 | 14
14
38952.4458 | 1 | 0 | 15
38952.448 | 1 | 0 | 15
38952.4501 | 1 | 0 | 15
38952.4523 | 1 | 0 | 15
38952.4544 | 1 | 0 | 15
38952.4565 | 1 | 0 | 15
38952.4587 | 2 | 0 | 15
38952.4608 | 201 | 0 | 15
38952.463 | 11 | 0 | 15
38952.4651 | 3 | 0 | 15
38952.4672 | 3 | 0 | 15
15
38952.4459 | 1 | 0 | 16
38952.448 | 1 | 0 | 16
38952.4501 | 1 | 0 | 16
38952.4523 | 1 | 0 | 16
38952.4544 | 1 | 0 | 16
38952.4566 | 1 | 0 | 16
38952.4587 | 2 | 0 | 16
38952.4608 | 2233 | 0 | 16
38952.463 | 839 | 0 | 16
38952.4651 | 3 | 0 | 16
38952.4672 | 3 | 0 | 16
16
38952.4459 | 1 | 0 | 17
38952.448 | 1 | 0 | 17
38952.4502 | 1 | 0 | 17
38952.4523 | 1 | 0 | 17
38952.4544 | 1 | 0 | 17
38952.4566 | 1 | 0 | 17
38952.4587 | 2 | 0 | 17
38952.4608 | 550 | 0 | 17
38952.463 | 18 | 0 | 17
38952.4651 | 2 | 0 | 17
38952.4673 | 3 | 0 | 17
17
38952.4459 | 1 | 0 | 18
38952.448 | 1 | 1 | 18
38952.4502 | 1 | 0 | 18
38952.4523 | 1 | 0 | 18
38952.4544 | 1 | 0 | 18
38952.4566 | 1 | 0 | 18
38952.4587 | 2 | 0 | 18
38952.4609 | 2089 | 0 | 18
38952.463 | 1370 | 0 | 18
38952.4651 | 3 | 1 | 18
38952.4673 | 3 | 0 | 18
18
38952.4459 | 1 | 0 | 19
38952.4481 | 1 | 0 | 19
38952.4502 | 1 | 0 | 19
38952.4523 | 1 | 0 | 19
38952.4545 | 1 | 0 | 19
38952.4566 | 1 | 0 | 19
38952.4587 | 2 | 0 | 19
38952.4609 | 418 | 0 | 19
38952.463 | 7 | 0 | 19
38952.4652 | 3 | 0 | 19
38952.4673 | 3 | 0 | 19
19
38952.4459 | 1 | 0 | 20
38952.4481 | 1 | 0 | 20
38952.4502 | 1 | 0 | 20
38952.4523 | 1 | 0 | 20
38952.4545 | 1 | 0 | 20
38952.4566 | 1 | 0 | 20
38952.4588 | 2253 | 0 | 20
38952.4609 | 2169 | 0 | 20
38952.463 | 1571 | 0 | 20
38952.4652 | 1993 | 0 | 20
38952.4673 | 2106 | 0 | 20
20
38952.4459 | 1 | 0 | 21
38952.4481 | 1 | 0 | 21
38952.4502 | 1 | 0 | 21
38952.4524 | 1 | 0 | 21
38952.4545 | 1 | 0 | 21
38952.4566 | 1 | 0 | 21
38952.4588 | 3 | 0 | 21
38952.4609 | 404 | 0 | 21
38952.4631 | 17 | 0 | 21
38952.4652 | 3 | 0 | 21
38952.4673 | 3 | 0 | 21
21
38952.446 | 1 | 0 | 22
38952.4481 | 1 | 0 | 22
38952.4502 | 1 | 0 | 22
38952.4524 | 1 | 0 | 22
38952.4545 | 1 | 0 | 22
38952.4567 | 1 | 0 | 22
38952.4588 | 2012 | 0 | 22
38952.4609 | 2335 | 0 | 22
38952.4631 | 2422 | 0 | 22
38952.4652 | 2339 | 0 | 22
38952.4673 | 2061 | 0 | 22
22
38952.446 | 1 | 1 | 23
38952.4481 | 1 | 0 | 23
38952.4503 | 1 | 1 | 23
38952.4524 | 1 | 0 | 23
38952.4545 | 1 | 0 | 23
38952.4567 | 1 | 0 | 23
38952.4588 | 3 | 0 | 23
38952.4609 | 935 | 559 | 23
38952.4631 | 14 | 0 | 23
38952.4652 | 3 | 0 | 23
38952.4674 | 3 | 0 | 23
23
38952.446 | 1 | 0 | 24
38952.4481 | 1 | 0 | 24
38952.4503 | 1 | 0 | 24
38952.4524 | 1 | 0 | 24
38952.4545 | 1 | 0 | 24
38952.4567 | 1 | 0 | 24
38952.4588 | 2 | 0 | 24
38952.461 | 1005 | 800 | 24
38952.4631 | 6 | 0 | 24
38952.4652 | 2 | 0 | 24
38952.4674 | 4 | 0 | 24
24
38952.446 | 1 | 0 | 25
38952.4481 | 1 | 0 | 25
38952.4503 | 1 | 0 | 25
38952.4524 | 1 | 0 | 25
38952.4546 | 1 | 0 | 25
38952.4567 | 1 | 0 | 25
38952.4588 | 2 | 0 | 25
38952.461 | 675 | 579 | 25
38952.4631 | 30 | 0 | 25
38952.4653 | 2 | 0 | 25
38952.4674 | 3 | 0 | 25
25
38952.446 | 1 | 0 | 26
38952.4482 | 1 | 0 | 26
38952.4503 | 1 | 0 | 26
38952.4524 | 1 | 0 | 26
38952.4546 | 1 | 0 | 26
38952.4567 | 1 | 0 | 26
38952.4589 | 2 | 0 | 26
38952.461 | 795 | 694 | 26
38952.4631 | 44 | 0 | 26
38952.4653 | 2 | 0 | 26
38952.4674 | 2 | 0 | 26
26
38952.446 | 1 | 0 | 27
38952.4482 | 1 | 0 | 27
38952.4503 | 1 | 0 | 27
38952.4525 | 1 | 0 | 27
38952.4546 | 1 | 0 | 27
38952.4567 | 1 | 0 | 27
38952.4589 | 2 | 0 | 27
38952.461 | 4 | 3 | 27
38952.4631 | 29 | 0 | 27
38952.4653 | 2 | 0 | 27
38952.4674 | 3 | 0 | 27
27
38952.4461 | 1 | 0 | 28
38952.4482 | 1 | 0 | 28
38952.4503 | 1 | 0 | 28
38952.4525 | 1 | 0 | 28
38952.4546 | 1 | 0 | 28
38952.4567 | 1 | 0 | 28
38952.4589 | 2 | 1 | 28
38952.461 | 318 | 2 | 28
38952.4632 | 3 | 0 | 28
38952.4653 | 3 | 0 | 28
38952.4674 | 3 | 0 | 28
28
38952.4461 | 1 | 0 | 29
38952.4482 | 1 | 0 | 29
38952.4503 | 1 | 0 | 29
38952.4525 | 1 | 0 | 29
38952.4546 | 1 | 0 | 29
38952.4568 | 1 | 0 | 29
38952.4589 | 2 | 0 | 29
38952.461 | 3 | 1 | 29
38952.4632 | 27 | 0 | 29
38952.4653 | 2 | 0 | 29
38952.4675 | 3 | 0 | 29
29
38952.4461 | 1 | 0 | 30
38952.4482 | 1 | 0 | 30
38952.4504 | 2 | 0 | 30
38952.4525 | 1 | 0 | 30
38952.4546 | 1 | 0 | 30
38952.4568 | 1 | 0 | 30
38952.4589 | 2 | 0 | 30
38952.4611 | 964 | 1 | 30
38952.4632 | 3 | 0 | 30
38952.4653 | 3 | 0 | 30
38952.4675 | 2 | 0 | 30
30
38952.4461 | 1 | 0 | 31
38952.4482 | 1 | 0 | 31
38952.4504 | 1 | 0 | 31
38952.4525 | 1 | 0 | 31
38952.4547 | 1 | 0 | 31
38952.4568 | 1 | 0 | 31
38952.4589 | 2 | 0 | 31
38952.4611 | 6 | 1 | 31
38952.4632 | 4 | 0 | 31
38952.4654 | 2 | 0 | 31
38952.4675 | 3 | 0 | 31
31
38952.4461 | 1 | 0 | 32
38952.4483 | 1 | 0 | 32
38952.4504 | 1 | 1 | 32
38952.4525 | 1 | 0 | 32
38952.4547 | 1 | 0 | 32
38952.4568 | 1 | 0 | 32
38952.459 | 2533 | 0 | 32
38952.4611 | 2477 | 1 | 32
38952.4632 | 1984 | 0 | 32
38952.4654 | 2211 | 0 | 32
38952.4675 | 2502 | 0 | 32
32
38952.4461 | 0 | 0 | 33
38952.4483 | 1 | 0 | 33
38952.4504 | 1 | 0 | 33
38952.4526 | 1 | 0 | 33
38952.4547 | 1 | 0 | 33
38952.4568 | 1 | 0 | 33
38952.459 | 3 | 0 | 33
38952.4611 | 10 | 0 | 33
38952.4633 | 6 | 0 | 33
38952.4654 | 3 | 0 | 33
38952.4675 | 3 | 0 | 33
33
38952.4462 | 1 | 0 | 34
38952.4483 | 1 | 0 | 34
38952.4504 | 1 | 0 | 34
38952.4526 | 1 | 0 | 34
38952.4547 | 1 | 0 | 34
38952.4569 | 1 | 0 | 34
38952.459 | 2102 | 0 | 34
38952.4611 | 2378 | 0 | 34
38952.4633 | 2082 | 0 | 34
38952.4654 | 2164 | 0 | 34
38952.4675 | 2204 | 0 | 34
34
38952.4462 | 1 | 0 | 35
38952.4483 | 1 | 0 | 35
38952.4505 | 1 | 0 | 35
38952.4526 | 1 | 0 | 35
38952.4547 | 1 | 0 | 35
38952.4569 | 1 | 0 | 35
38952.459 | 3 | 0 | 35
38952.4611 | 5 | 0 | 35
38952.4633 | 9 | 0 | 35
38952.4654 | 3 | 0 | 35
38952.4676 | 3 | 0 | 35
35
38952.4462 | 1 | 0 | 36
38952.4483 | 1 | 0 | 36
38952.4505 | 1 | 0 | 36
38952.4526 | 1 | 0 | 36
38952.4547 | 1 | 0 | 36
38952.4569 | 1 | 0 | 36
38952.459 | 2 | 0 | 36
38952.4612 | 1918 | 0 | 36
38952.4633 | 2109 | 0 | 36
38952.4654 | 3 | 0 | 36
38952.4676 | 3 | 0 | 36
36
38952.4462 | 1 | 0 | 37
38952.4483 | 1 | 0 | 37
38952.4505 | 1 | 0 | 37
38952.4526 | 1 | 0 | 37
38952.4548 | 1 | 0 | 37
38952.4569 | 1 | 0 | 37
38952.459 | 2 | 0 | 37
38952.4612 | 449 | 0 | 37
38952.4633 | 8 | 0 | 37
38952.4655 | 3 | 0 | 37
38952.4676 | 3 | 0 | 37
37
38952.4462 | 1 | 0 | 38
38952.4484 | 1 | 0 | 38
38952.4505 | 1 | 0 | 38
38952.4526 | 1 | 0 | 38
38952.4548 | 1 | 0 | 38
38952.4569 | 1 | 0 | 38
38952.4591 | 2 | 0 | 38
38952.4612 | 1546 | 0 | 38
38952.4633 | 1840 | 0 | 38
38952.4655 | 3 | 0 | 38
38952.4676 | 2 | 0 | 38
38
38952.4462 | 1 | 0 | 39
38952.4484 | 1 | 0 | 39
38952.4505 | 2 | 0 | 39
38952.4527 | 1 | 0 | 39
38952.4548 | 1 | 0 | 39
38952.4569 | 1 | 0 | 39
38952.4591 | 2 | 0 | 39
38952.4612 | 304 | 0 | 39
38952.4633 | 4 | 0 | 39
38952.4655 | 2 | 0 | 39
38952.4676 | 3 | 0 | 39
39
38952.4463 | 1 | 0 | 40
38952.4484 | 1 | 0 | 40
38952.4505 | 1 | 0 | 40
38952.4527 | 1 | 0 | 40
38952.4548 | 1 | 0 | 40
38952.4569 | 1 | 0 | 40
38952.4591 | 2272 | 0 | 40
38952.4612 | 2177 | 0 | 40
38952.4634 | 2131 | 0 | 40
38952.4655 | 2541 | 0 | 40
38952.4676 | 2383 | 0 | 40
40
38952.4463 | 0 | 0 | 41
38952.4484 | 1 | 0 | 41
38952.4505 | 1 | 0 | 41
38952.4527 | 1 | 0 | 41
38952.4548 | 1 | 0 | 41
38952.457 | 1 | 0 | 41
38952.4591 | 3 | 0 | 41
38952.4612 | 33 | 0 | 41
38952.4634 | 5 | 0 | 41
38952.4655 | 3 | 0 | 41
38952.4677 | 3 | 0 | 41
41
38952.4463 | 1 | 0 | 42
38952.4484 | 1 | 0 | 42
38952.4506 | 1 | 0 | 42
38952.4527 | 1 | 0 | 42
38952.4548 | 1 | 0 | 42
38952.457 | 1 | 0 | 42
38952.4591 | 2316 | 0 | 42
38952.4613 | 2240 | 0 | 42
38952.4634 | 2399 | 0 | 42
38952.4655 | 2592 | 0 | 42
38952.4677 | 2509 | 0 | 42
42
38952.4463 | 1 | 0 | 43
38952.4484 | 1 | 0 | 43
38952.4506 | 1 | 0 | 43
38952.4527 | 1 | 0 | 43
38952.4549 | 1 | 0 | 43
38952.457 | 1 | 0 | 43
38952.4591 | 4 | 0 | 43
38952.4613 | 1212 | 309 | 43
38952.4634 | 487 | 449 | 43
38952.4655 | 18 | 14 | 43
38952.4677 | 3 | 0 | 43
43
38952.4463 | 1 | 0 | 44
38952.4485 | 1 | 0 | 44
38952.4506 | 1 | 0 | 44
38952.4527 | 1 | 1 | 44
38952.4549 | 1 | 0 | 44
38952.457 | 1 | 0 | 44
38952.4591 | 3 | 0 | 44
38952.4613 | 600 | 490 | 44
38952.4634 | 738 | 749 | 44
38952.4656 | 114 | 108 | 44
38952.4677 | 3 | 0 | 44
44
38952.4463 | 1 | 0 | 45
38952.4485 | 1 | 0 | 45
38952.4506 | 1 | 0 | 45
38952.4528 | 1 | 0 | 45
38952.4549 | 1 | 0 | 45
38952.457 | 1 | 0 | 45
38952.4592 | 2 | 0 | 45
38952.4613 | 535 | 2 | 45
38952.4634 | 3 | 2 | 45
38952.4656 | 3 | 1 | 45
38952.4677 | 3 | 0 | 45
45
38952.4464 | 1 | 0 | 46
38952.4485 | 1 | 0 | 46
38952.4506 | 1 | 0 | 46
38952.4528 | 1 | 0 | 46
38952.4549 | 1 | 0 | 46
38952.457 | 1 | 0 | 46
38952.4592 | 2 | 0 | 46
38952.4613 | 376 | 1 | 46
38952.4635 | 3 | 1 | 46
38952.4656 | 3 | 0 | 46
38952.4677 | 3 | 0 | 46
46
38952.4464 | 1 | 0 | 47
38952.4485 | 1 | 0 | 47
38952.4506 | 1 | 0 | 47
38952.4528 | 1 | 0 | 47
38952.4549 | 1 | 0 | 47
38952.4571 | 1 | 0 | 47
38952.4592 | 2 | 0 | 47
38952.4613 | 705 | 0 | 47
38952.4635 | 3 | 1 | 47
38952.4656 | 3 | 0 | 47
38952.4678 | 3 | 0 | 47
47
38952.4464 | 1 | 0 | 48
38952.4485 | 1 | 0 | 48
38952.4507 | 1 | 0 | 48
38952.4528 | 1 | 0 | 48
38952.4549 | 1 | 0 | 48
38952.4571 | 1 | 0 | 48
38952.4592 | 1 | 0 | 48
38952.4614 | 125 | 0 | 48
38952.4635 | 3 | 0 | 48
38952.4656 | 3 | 0 | 48
38952.4678 | 3 | 0 | 48
48
38952.4464 | 1 | 0 | 49
38952.4485 | 1 | 0 | 49
38952.4507 | 1 | 0 | 49
38952.4528 | 1 | 0 | 49
38952.455 | 1 | 0 | 49
38952.4571 | 1 | 0 | 49
38952.4592 | 2 | 0 | 49
38952.4614 | 132 | 0 | 49
38952.4635 | 2 | 0 | 49
38952.4656 | 3 | 0 | 49
38952.4678 | 2 | 0 | 49
49
38952.4464 | 1 | 0 | 50
38952.4486 | 1 | 0 | 50
38952.4507 | 1 | 0 | 50
38952.4528 | 1 | 0 | 50
38952.455 | 1 | 0 | 50
38952.4571 | 1 | 0 | 50
38952.4592 | 2100 | 0 | 50
38952.4614 | 2599 | 0 | 50
38952.4635 | 2218 | 0 | 50
38952.4657 | 2219 | 0 | 50
38952.4678 | 2019 | 0 | 50
50
38952.4464 | 1 | 0 | 51
38952.4486 | 1 | 0 | 51
38952.4507 | 1 | 0 | 51
38952.4528 | 1 | 0 | 51
38952.455 | 1 | 0 | 51
38952.4571 | 1 | 0 | 51
38952.4593 | 3 | 0 | 51
38952.4614 | 29 | 0 | 51
38952.4635 | 3 | 0 | 51
38952.4657 | 3 | 0 | 51
38952.4678 | 3 | 0 | 51
51
38952.4464 | 1 | 0 | 52
38952.4486 | 1 | 0 | 52
38952.4507 | 1 | 0 | 52
38952.4529 | 1 | 0 | 52
38952.455 | 1 | 0 | 52
38952.4571 | 1 | 0 | 52
38952.4593 | 2555 | 0 | 52
38952.4614 | 2522 | 0 | 52
38952.4636 | 2347 | 0 | 52
38952.4657 | 2207 | 0 | 52
38952.4678 | 1956 | 0 | 52
52
38952.4465 | 1 | 0 | 53
38952.4486 | 1 | 0 | 53
38952.4507 | 1 | 0 | 53
38952.4529 | 1 | 0 | 53
38952.455 | 1 | 0 | 53
38952.4572 | 1 | 0 | 53
38952.4593 | 3 | 0 | 53
38952.4614 | 87 | 0 | 53
38952.4636 | 3 | 0 | 53
38952.4657 | 3 | 0 | 53
38952.4678 | 3 | 0 | 53
53
38952.4465 | 1 | 0 | 54
38952.4486 | 1 | 0 | 54
38952.4508 | 1 | 0 | 54
38952.4529 | 1 | 0 | 54
38952.455 | 1 | 0 | 54
38952.4572 | 1 | 0 | 54
38952.4593 | 3 | 0 | 54
38952.4614 | 1884 | 0 | 54
38952.4636 | 1613 | 0 | 54
38952.4657 | 2 | 0 | 54
38952.4679 | 3 | 0 | 54
54
38952.4465 | 1 | 0 | 55
38952.4486 | 1 | 0 | 55
38952.4508 | 1 | 0 | 55
38952.4529 | 1 | 0 | 55
38952.455 | 1 | 0 | 55
38952.4572 | 1 | 0 | 55
38952.4593 | 3 | 0 | 55
38952.4615 | 15 | 0 | 55
38952.4636 | 3 | 0 | 55
38952.4657 | 3 | 0 | 55
38952.4679 | 3 | 0 | 55
55
38952.4465 | 1 | 0 | 56
38952.4486 | 1 | 0 | 56
38952.4508 | 1 | 0 | 56
38952.4529 | 1 | 0 | 56
38952.4551 | 2 | 0 | 56
38952.4572 | 1 | 0 | 56
38952.4593 | 2 | 0 | 56
38952.4615 | 1747 | 0 | 56
38952.4636 | 1277 | 0 | 56
38952.4658 | 3 | 0 | 56
38952.4679 | 2 | 0 | 56
56
38952.4465 | 1 | 0 | 57
38952.4487 | 1 | 0 | 57
38952.4508 | 1 | 0 | 57
38952.4529 | 1 | 0 | 57
38952.4551 | 1 | 0 | 57
38952.4572 | 1 | 0 | 57
38952.4594 | 2 | 0 | 57
38952.4615 | 26 | 0 | 57
38952.4636 | 3 | 0 | 57
38952.4658 | 2 | 0 | 57
38952.4679 | 2 | 0 | 57
57
38952.4465 | 1 | 0 | 58
38952.4487 | 1 | 0 | 58
38952.4508 | 1 | 0 | 58
38952.453 | 1 | 0 | 58
38952.4551 | 1 | 0 | 58
38952.4572 | 1 | 0 | 58
38952.4594 | 2476 | 0 | 58
38952.4615 | 2533 | 0 | 58
38952.4637 | 2143 | 0 | 58
38952.4658 | 2307 | 0 | 58
38952.4679 | 2056 | 0 | 58
58
38952.4466 | 1 | 0 | 59
38952.4487 | 1 | 0 | 59
38952.4508 | 1 | 0 | 59
38952.453 | 1 | 0 | 59
38952.4551 | 1 | 0 | 59
38952.4573 | 1 | 0 | 59
38952.4594 | 4 | 0 | 59
38952.4615 | 61 | 0 | 59
38952.4637 | 3 | 0 | 59
38952.4658 | 3 | 0 | 59
38952.468 | 3 | 0 | 59
59
38952.4466 | 1 | 0 | 60
38952.4487 | 1 | 0 | 60
38952.4509 | 1 | 0 | 60
38952.453 | 1 | 0 | 60
38952.4551 | 1 | 0 | 60
38952.4573 | 1 | 0 | 60
38952.4594 | 1894 | 0 | 60
38952.4616 | 2134 | 0 | 60
38952.4637 | 2571 | 0 | 60
38952.4658 | 2156 | 0 | 60
38952.468 | 2495 | 0 | 60
60
38952.4466 | 1 | 0 | 61
38952.4487 | 1 | 0 | 61
38952.4509 | 1 | 0 | 61
38952.453 | 1 | 0 | 61
38952.4552 | 1 | 0 | 61
38952.4573 | 1 | 0 | 61
38952.4594 | 3 | 0 | 61
38952.4616 | 59 | 0 | 61
38952.4637 | 3 | 0 | 61
38952.4658 | 3 | 0 | 61
38952.468 | 3 | 0 | 61
61
38952.4466 | 1 | 0 | 62
38952.4488 | 1 | 0 | 62
38952.4509 | 1 | 0 | 62
38952.453 | 1 | 0 | 62
38952.4552 | 1 | 0 | 62
38952.4573 | 1 | 0 | 62
38952.4594 | 2 | 0 | 62
38952.4616 | 3 | 0 | 62
38952.4637 | 3 | 0 | 62
38952.4659 | 2 | 0 | 62
38952.468 | 3 | 0 | 62
62
38952.4466 | 1 | 0 | 63
38952.4488 | 1 | 0 | 63
38952.4509 | 1 | 0 | 63
38952.453 | 1 | 0 | 63
38952.4552 | 1 | 0 | 63
38952.4573 | 1 | 0 | 63
38952.4595 | 2 | 0 | 63
38952.4616 | 94 | 0 | 63
38952.4637 | 3 | 0 | 63
38952.4659 | 3 | 0 | 63
38952.468 | 3 | 0 | 63
63
38952.4466 | 1 | 0 | 64
38952.4488 | 1 | 0 | 64
38952.4509 | 1 | 0 | 64
38952.4531 | 1 | 0 | 64
38952.4552 | 1 | 0 | 64
38952.4573 | 1 | 0 | 64
38952.4595 | 2 | 0 | 64
38952.4616 | 3 | 0 | 64
38952.4638 | 2 | 0 | 64
38952.4659 | 3 | 0 | 64
38952.468 | 2 | 0 | 64
64
38952.4467 | 1 | 0 | 65
38952.4488 | 1 | 0 | 65
38952.4509 | 1 | 0 | 65
38952.4531 | 1 | 0 | 65
38952.4552 | 1 | 0 | 65
38952.4573 | 1 | 0 | 65
38952.4595 | 1 | 0 | 65
38952.4616 | 18 | 0 | 65
38952.4638 | 3 | 0 | 65
38952.4659 | 3 | 0 | 65
38952.468 | 3 | 0 | 65
65
38952.4467 | 1 | 0 | 66
38952.4488 | 1 | 1 | 66
38952.4509 | 1 | 0 | 66
38952.4531 | 1 | 0 | 66
38952.4552 | 1 | 0 | 66
38952.4574 | 1 | 0 | 66
38952.4595 | 2509 | 0 | 66
38952.4616 | 2563 | 0 | 66
38952.4638 | 2113 | 0 | 66
38952.4659 | 2047 | 0 | 66
38952.4681 | 2540 | 0 | 66
66
38952.4467 | 1 | 0 | 67
38952.4488 | 1 | 0 | 67
38952.451 | 1 | 0 | 67
38952.4531 | 1 | 0 | 67
38952.4552 | 1 | 0 | 67
38952.4574 | 1 | 0 | 67
38952.4595 | 3 | 0 | 67
38952.4617 | 63 | 0 | 67
38952.4638 | 3 | 0 | 67
38952.4659 | 3 | 0 | 67
38952.4681 | 3 | 0 | 67
67
38952.4467 | 1 | 0 | 68
38952.4488 | 1 | 0 | 68
38952.451 | 1 | 0 | 68
38952.4531 | 2 | 0 | 68
38952.4553 | 1 | 0 | 68
38952.4574 | 1 | 0 | 68
38952.4595 | 2181 | 0 | 68
38952.4617 | 2509 | 0 | 68
38952.4638 | 2396 | 0 | 68
38952.4659 | 2190 | 0 | 68
38952.4681 | 1983 | 0 | 68
68
38952.4467 | 1 | 1 | 69
38952.4489 | 1 | 0 | 69
38952.451 | 1 | 0 | 69
38952.4531 | 1 | 0 | 69
38952.4553 | 1 | 0 | 69
38952.4574 | 1 | 0 | 69
38952.4596 | 3 | 0 | 69
38952.4617 | 85 | 0 | 69
38952.4638 | 3 | 0 | 69
38952.466 | 3 | 0 | 69
38952.4681 | 3 | 0 | 69
69
38952.4467 | 1 | 0 | 70
38952.4489 | 1 | 0 | 70
38952.451 | 1 | 0 | 70
38952.4532 | 1 | 0 | 70
38952.4553 | 1 | 0 | 70
38952.4574 | 1 | 0 | 70
38952.4596 | 2 | 0 | 70
38952.4617 | 1454 | 0 | 70
38952.4638 | 1930 | 0 | 70
38952.466 | 3 | 0 | 70
38952.4681 | 770 | 0 | 70
70
38952.4468 | 1 | 0 | 71
38952.4489 | 1 | 0 | 71
38952.451 | 1 | 0 | 71
38952.4532 | 1 | 0 | 71
38952.4553 | 1 | 0 | 71
38952.4574 | 1 | 0 | 71
38952.4596 | 2 | 0 | 71
38952.4617 | 10 | 0 | 71
38952.4639 | 3 | 0 | 71
38952.466 | 2 | 0 | 71
38952.4681 | 3 | 0 | 71
71
38952.4468 | 1 | 0 | 72
38952.4489 | 1 | 0 | 72
38952.4511 | 1 | 0 | 72
38952.4532 | 1 | 0 | 72
38952.4553 | 1 | 0 | 72
38952.4575 | 1 | 0 | 72
38952.4596 | 2595 | 0 | 72
38952.4617 | 1695 | 0 | 72
38952.4639 | 1692 | 0 | 72
38952.466 | 3 | 0 | 72
38952.4682 | 3 | 0 | 72
72
38952.4468 | 1 | 0 | 73
38952.4489 | 2 | 0 | 73
38952.4511 | 1 | 0 | 73
38952.4532 | 1 | 0 | 73
38952.4553 | 1 | 0 | 73
38952.4575 | 1 | 0 | 73
38952.4596 | 2 | 0 | 73
38952.4618 | 11 | 0 | 73
38952.4639 | 3 | 0 | 73
38952.466 | 3 | 0 | 73
38952.4682 | 3 | 0 | 73
73
38952.4468 | 1 | 0 | 74
38952.4489 | 1 | 0 | 74
38952.4511 | 1 | 0 | 74
38952.4532 | 1 | 0 | 74
38952.4554 | 1 | 0 | 74
38952.4575 | 2132 | 0 | 74
38952.4596 | 2185 | 0 | 74
38952.4618 | 2489 | 0 | 74
38952.4639 | 2042 | 0 | 74
38952.4661 | 2020 | 0 | 74
38952.4682 | 2477 | 0 | 74
74
38952.4468 | 1 | 0 | 75
38952.449 | 1 | 0 | 75
38952.4511 | 1 | 0 | 75
38952.4532 | 1 | 0 | 75
38952.4554 | 1 | 0 | 75
38952.4575 | 3 | 0 | 75
38952.4597 | 3 | 0 | 75
38952.4618 | 124 | 0 | 75
38952.4639 | 3 | 0 | 75
38952.4661 | 3 | 0 | 75
38952.4682 | 3 | 0 | 75
75
38952.4468 | 1 | 0 | 76
38952.449 | 1 | 0 | 76
38952.4511 | 1 | 0 | 76
38952.4533 | 1 | 0 | 76
38952.4554 | 1 | 0 | 76
38952.4575 | 2 | 0 | 76
38952.4597 | 2062 | 0 | 76
38952.4618 | 2180 | 0 | 76
38952.4639 | 2275 | 0 | 76
38952.4661 | 2411 | 0 | 76
38952.4682 | 2027 | 0 | 76
76
38952.4469 | 1 | 0 | 77
38952.449 | 1 | 0 | 77
38952.4511 | 1 | 0 | 77
38952.4533 | 1 | 1 | 77
38952.4554 | 1 | 0 | 77
38952.4575 | 1 | 0 | 77
38952.4597 | 1021 | 973 | 77
38952.4618 | 938 | 927 | 77
38952.464 | 853 | 816 | 77
38952.4661 | 1075 | 1051 | 77
38952.4682 | 3 | 0 | 77
77
38952.4469 | 1 | 0 | 78
38952.449 | 1 | 0 | 78
38952.4511 | 1 | 0 | 78
38952.4533 | 1 | 0 | 78
38952.4554 | 1 | 0 | 78
38952.4576 | 1 | 0 | 78
38952.4597 | 1086 | 932 | 78
38952.4618 | 1029 | 1061 | 78
38952.464 | 951 | 1049 | 78
38952.4661 | 861 | 954 | 78
38952.4683 | 3 | 0 | 78
78
38952.4469 | 1 | 0 | 79
38952.449 | 1 | 0 | 79
38952.4512 | 1 | 1 | 79
38952.4533 | 1 | 0 | 79
38952.4554 | 1 | 0 | 79
38952.4576 | 1 | 0 | 79
38952.4597 | 3 | 5 | 79
38952.4619 | 3 | 5 | 79
38952.464 | 3 | 4 | 79
38952.4661 | 3 | 3 | 79
38952.4683 | 3 | 0 | 79
79
38952.4469 | 1 | 0 | 80
38952.449 | 1 | 0 | 80
38952.4512 | 1 | 0 | 80
38952.4533 | 1 | 0 | 80
38952.4555 | 1 | 0 | 80
38952.4576 | 1 | 0 | 80
38952.4597 | 2296 | 3 | 80
38952.4619 | 2587 | 2 | 80
38952.464 | 2131 | 2 | 80
38952.4661 | 2253 | 2 | 80
38952.4683 | 2369 | 0 | 80
80
38952.4469 | 1 | 0 | 81
38952.4491 | 1 | 0 | 81
38952.4512 | 1 | 0 | 81
38952.4533 | 1 | 0 | 81
38952.4555 | 1 | 0 | 81
38952.4576 | 2 | 0 | 81
38952.4597 | 3 | 1 | 81
38952.4619 | 3 | 1 | 81
38952.464 | 3 | 1 | 81
38952.4662 | 3 | 1 | 81
38952.4683 | 3 | 0 | 81
81
38952.4469 | 1 | 1 | 82
38952.4491 | 1 | 0 | 82
38952.4512 | 1 | 0 | 82
38952.4533 | 1 | 0 | 82
38952.4555 | 1 | 0 | 82
38952.4576 | 1 | 0 | 82
38952.4598 | 1827 | 1 | 82
38952.4619 | 2096 | 1 | 82
38952.464 | 1851 | 0 | 82
38952.4662 | 2014 | 0 | 82
38952.4683 | 1706 | 0 | 82
82
38952.4469 | 1 | 0 | 83
38952.4491 | 2 | 0 | 83
38952.4512 | 1 | 0 | 83
38952.4534 | 1 | 0 | 83
38952.4555 | 1 | 0 | 83
38952.4576 | 1 | 0 | 83
38952.4598 | 3 | 1 | 83
38952.4619 | 4 | 1 | 83
38952.4641 | 3 | 1 | 83
38952.4662 | 3 | 0 | 83
38952.4683 | 3 | 0 | 83
83
38952.447 | 1 | 0 | 84
38952.4491 | 1 | 0 | 84
38952.4512 | 1 | 0 | 84
38952.4534 | 1 | 0 | 84
38952.4555 | 1 | 0 | 84
38952.4577 | 1 | 0 | 84
38952.4598 | 2571 | 1 | 84
38952.4619 | 1568 | 0 | 84
38952.4641 | 396 | 1 | 84
38952.4662 | 2 | 0 | 84
38952.4684 | 2 | 0 | 84
84
38952.447 | 1 | 0 | 85
38952.4491 | 1 | 0 | 85
38952.4513 | 1 | 0 | 85
38952.4534 | 1 | 0 | 85
38952.4555 | 1 | 0 | 85
38952.4577 | 1 | 0 | 85
38952.4598 | 3 | 0 | 85
38952.462 | 3 | 0 | 85
38952.4641 | 3 | 0 | 85
38952.4662 | 2 | 0 | 85
38952.4684 | 3 | 0 | 85
85
38952.447 | 1 | 0 | 86
38952.4491 | 1 | 0 | 86
38952.4513 | 1 | 0 | 86
38952.4534 | 1 | 0 | 86
38952.4556 | 1 | 0 | 86
38952.4577 | 1 | 0 | 86
38952.4598 | 2148 | 0 | 86
38952.462 | 1847 | 0 | 86
38952.4641 | 1661 | 0 | 86
38952.4662 | 2 | 0 | 86
38952.4684 | 2 | 0 | 86
86
38952.447 | 1 | 0 | 87
38952.4492 | 1 | 0 | 87
38952.4513 | 1 | 0 | 87
38952.4534 | 1 | 1 | 87
38952.4556 | 1 | 0 | 87
38952.4577 | 1 | 0 | 87
38952.4598 | 4 | 0 | 87
38952.462 | 3 | 0 | 87
38952.4641 | 3 | 0 | 87
38952.4663 | 3 | 0 | 87
38952.4684 | 2 | 0 | 87
87
38952.447 | 1 | 0 | 88
38952.4492 | 1 | 0 | 88
38952.4513 | 1 | 0 | 88
38952.4534 | 1 | 0 | 88
38952.4556 | 1 | 0 | 88
38952.4577 | 2 | 0 | 88
38952.4599 | 2396 | 0 | 88
38952.462 | 2173 | 0 | 88
38952.4641 | 1622 | 0 | 88
38952.4663 | 2127 | 0 | 88
38952.4684 | 2523 | 0 | 88
88
38952.447 | 1 | 0 | 89
38952.4492 | 1 | 1 | 89
38952.4513 | 1 | 0 | 89
38952.4535 | 1 | 0 | 89
38952.4556 | 1 | 0 | 89
38952.4577 | 1 | 0 | 89
38952.4599 | 5 | 0 | 89
38952.462 | 3 | 0 | 89
38952.4663 | 3 | 0 | 89
38952.4684 | 3 | 0 | 89
89
38952.4471 | 1 | 0 | 90
38952.4492 | 1 | 0 | 90
38952.4513 | 1 | 0 | 90
38952.4535 | 1 | 0 | 90
38952.4556 | 1 | 0 | 90
38952.4578 | 1 | 0 | 90
38952.4599 | 1997 | 0 | 90
38952.462 | 2257 | 0 | 90
38952.4642 | 2586 | 0 | 90
38952.4663 | 2558 | 0 | 90
38952.4684 | 2038 | 0 | 90
90
38952.4471 | 1 | 0 | 91
38952.4492 | 1 | 0 | 91
38952.4514 | 1 | 0 | 91
38952.4535 | 1 | 0 | 91
38952.4556 | 1 | 0 | 91
38952.4578 | 1 | 0 | 91
38952.4599 | 194 | 0 | 91
38952.462 | 3 | 0 | 91
38952.4642 | 3 | 0 | 91
38952.4663 | 3 | 0 | 91
38952.4685 | 3 | 0 | 91
91
38952.4471 | 1 | 0 | 92
38952.4492 | 1 | 0 | 92
38952.4514 | 1 | 0 | 92
38952.4535 | 1 | 0 | 92
38952.4556 | 1 | 0 | 92
38952.4578 | 1 | 0 | 92
38952.4599 | 2461 | 0 | 92
38952.4621 | 2434 | 0 | 92
38952.4642 | 1992 | 0 | 92
38952.4663 | 2512 | 0 | 92
38952.4685 | 2301 | 0 | 92
92
38952.4471 | 1 | 0 | 93
38952.4492 | 1 | 0 | 93
38952.4514 | 1 | 0 | 93
38952.4535 | 1 | 0 | 93
38952.4557 | 1 | 0 | 93
38952.4578 | 1 | 0 | 93
38952.4599 | 75 | 0 | 93
38952.4621 | 3 | 0 | 93
38952.4642 | 3 | 0 | 93
38952.4664 | 3 | 0 | 93
38952.4685 | 3 | 0 | 93
93
38952.4471 | 1 | 0 | 94
38952.4493 | 1 | 0 | 94
38952.4514 | 1 | 0 | 94
38952.4535 | 1 | 0 | 94
38952.4557 | 1 | 0 | 94
38952.4578 | 1 | 0 | 94
38952.46 | 1979 | 0 | 94
38952.4621 | 2187 | 0 | 94
38952.4642 | 2014 | 0 | 94
38952.4664 | 2132 | 0 | 94
38952.4685 | 1882 | 0 | 94
94
38952.4471 | 1 | 0 | 95
38952.4493 | 1 | 0 | 95
38952.4514 | 1 | 0 | 95
38952.4536 | 1 | 0 | 95
38952.4557 | 1 | 0 | 95
38952.4578 | 1 | 0 | 95
38952.46 | 120 | 0 | 95
38952.4621 | 4 | 0 | 95
38952.4642 | 3 | 0 | 95
38952.4664 | 3 | 0 | 95
38952.4685 | 3 | 0 | 95
95
38952.4472 | 1 | 0 | 96
38952.4493 | 1 | 1 | 96
38952.4514 | 1 | 0 | 96
38952.4536 | 1 | 0 | 96
38952.4557 | 1 | 0 | 96
38952.4578 | 1 | 0 | 96
38952.46 | 2281 | 0 | 96
38952.4621 | 973 | 0 | 96
38952.4643 | 295 | 0 | 96
38952.4664 | 2 | 0 | 96
38952.4685 | 3 | 0 | 96
96
38952.4472 | 1 | 0 | 97
38952.4493 | 1 | 0 | 97
38952.4515 | 1 | 0 | 97
38952.4536 | 1 | 0 | 97
38952.4557 | 1 | 0 | 97
38952.4579 | 1 | 0 | 97
38952.46 | 491 | 0 | 97
38952.4621 | 2 | 0 | 97
38952.4643 | 3 | 0 | 97
38952.4664 | 3 | 0 | 97
38952.4686 | 2 | 0 | 97
97
38952.4472 | 1 | 0 | 98
38952.4493 | 1 | 0 | 98
38952.4515 | 1 | 0 | 98
38952.4536 | 1 | 0 | 98
38952.4558 | 1 | 0 | 98
38952.4579 | 1 | 0 | 98
38952.46 | 2175 | 0 | 98
38952.4622 | 1227 | 0 | 98
38952.4643 | 4 | 0 | 98
38952.4664 | 3 | 0 | 98
38952.4686 | 2 | 0 | 98
98
38952.4472 | 1 | 0 | 99
38952.4494 | 1 | 0 | 99
38952.4515 | 1 | 0 | 99
38952.4536 | 1 | 0 | 99
38952.4558 | 1 | 0 | 99
38952.4579 | 1 | 0 | 99
38952.46 | 839 | 0 | 99
38952.4622 | 3 | 0 | 99
38952.4643 | 3 | 0 | 99
38952.4665 | 3 | 0 | 99
38952.4686 | 3 | 0 | 99
99
38952.4472 | 1 | 0 | 100
38952.4494 | 1 | 0 | 100
38952.4515 | 1 | 0 | 100
38952.4536 | 1 | 0 | 100
38952.4558 | 1 | 0 | 100
38952.4579 | 1 | 0 | 100
38952.4601 | 2086 | 0 | 100
38952.4622 | 2266 | 0 | 100
38952.4643 | 2475 | 0 | 100
38952.4665 | 2060 | 0 | 100
38952.4686 | 2460 | 0 | 100
100
38952.4472 | 1 | 0 | 101
38952.4494 | 1 | 0 | 101
38952.4515 | 1 | 0 | 101
38952.4537 | 1 | 0 | 101
38952.4558 | 1 | 0 | 101
38952.4579 | 1 | 0 | 101
38952.4601 | 148 | 0 | 101
38952.4622 | 3 | 0 | 101
38952.4644 | 3 | 0 | 101
38952.4665 | 3 | 0 | 101
38952.4686 | 3 | 0 | 101
101
38952.4473 | 1 | 0 | 102
38952.4494 | 1 | 0 | 102
38952.4515 | 1 | 0 | 102
38952.4537 | 1 | 0 | 102
38952.4558 | 1 | 0 | 102
38952.458 | 1 | 0 | 102
38952.4601 | 2286 | 0 | 102
38952.4622 | 2214 | 0 | 102
38952.4644 | 2594 | 0 | 102
38952.4665 | 2556 | 0 | 102
38952.4686 | 2172 | 0 | 102
102
38952.4473 | 1 | 1 | 103
38952.4494 | 1 | 0 | 103
38952.4516 | 1 | 0 | 103
38952.4537 | 1 | 0 | 103
38952.4558 | 1 | 0 | 103
38952.458 | 2 | 0 | 103
38952.4601 | 2549 | 0 | 103
38952.4622 | 2103 | 0 | 103
38952.4644 | 2521 | 0 | 103
38952.4665 | 2419 | 0 | 103
38952.4687 | 2524 | 0 | 103
103
38952.4473 | 1 | 0 | 104
38952.4494 | 1 | 0 | 104
38952.4516 | 1 | 0 | 104
38952.4537 | 1 | 0 | 104
38952.4558 | 1 | 0 | 104
38952.458 | 698 | 681 | 104
38952.4601 | 2515 | 0 | 104
38952.4623 | 2319 | 0 | 104
38952.4644 | 1794 | 0 | 104
38952.4665 | 1831 | 0 | 104
38952.4687 | 1967 | 0 | 104
104
38952.4473 | 1 | 0 | 105
38952.4494 | 1 | 0 | 105
38952.4516 | 1 | 0 | 105
38952.4537 | 1 | 0 | 105
38952.4559 | 1 | 0 | 105
38952.458 | 1 | 1 | 105
38952.4601 | 2600 | 0 | 105
38952.4623 | 1993 | 0 | 105
38952.4644 | 2025 | 0 | 105
38952.4666 | 2030 | 0 | 105
38952.4687 | 2106 | 0 | 105
105
38952.4473 | 1 | 0 | 106
38952.4495 | 1 | 0 | 106
38952.4516 | 1 | 0 | 106
38952.4537 | 1 | 0 | 106
38952.4559 | 1 | 0 | 106
38952.458 | 2 | 0 | 106
38952.4602 | 2171 | 0 | 106
38952.4623 | 1015 | 0 | 106
38952.4644 | 7 | 0 | 106
38952.4666 | 4 | 0 | 106
38952.4687 | 3 | 0 | 106
106
38952.4473 | 1 | 0 | 107
38952.4495 | 1 | 0 | 107
38952.4516 | 1 | 0 | 107
38952.4538 | 1 | 0 | 107
38952.4559 | 1 | 0 | 107
38952.458 | 1 | 1 | 107
38952.4602 | 2370 | 0 | 107
38952.4623 | 2403 | 0 | 107
38952.4644 | 2550 | 0 | 107
38952.4666 | 2246 | 0 | 107
38952.4687 | 2298 | 0 | 107
107
38952.4473 | 1 | 0 | 108
38952.4495 | 1 | 0 | 108
38952.4516 | 1 | 0 | 108
38952.4538 | 1 | 0 | 108
38952.4559 | 1 | 0 | 108
38952.458 | 1 | 0 | 108
38952.4602 | 2285 | 0 | 108
38952.4623 | 1391 | 0 | 108
38952.4645 | 3 | 0 | 108
38952.4666 | 3 | 0 | 108
38952.4687 | 3 | 0 | 108
108
38952.4474 | 1 | 0 | 109
38952.4495 | 1 | 0 | 109
38952.4516 | 1 | 0 | 109
38952.4538 | 1 | 0 | 109
38952.4559 | 1 | 0 | 109
38952.4581 | 1 | 0 | 109
38952.4602 | 2015 | 0 | 109
38952.4623 | 2031 | 0 | 109
38952.4645 | 2188 | 0 | 109
38952.4666 | 2507 | 0 | 109
38952.4688 | 2456 | 0 | 109
109
38952.4474 | 1 | 0 | 110
38952.4495 | 1 | 0 | 110
38952.4517 | 1 | 0 | 110
38952.4538 | 1 | 0 | 110
38952.4559 | 1 | 0 | 110
38952.4581 | 2467 | 0 | 110
38952.4602 | 2368 | 0 | 110
38952.4624 | 2516 | 0 | 110
38952.4645 | 2242 | 0 | 110
38952.4666 | 2548 | 0 | 110
38952.4688 | 2155 | 0 | 110
110
38952.4474 | 1 | 0 | 111
38952.4495 | 1 | 0 | 111
38952.4517 | 1 | 0 | 111
38952.4538 | 1 | 0 | 111
38952.456 | 1 | 0 | 111
38952.4581 | 2 | 0 | 111
38952.4602 | 2022 | 0 | 111
38952.4624 | 2027 | 0 | 111
38952.4645 | 2245 | 0 | 111
38952.4667 | 2104 | 0 | 111
38952.4688 | 2302 | 0 | 111
111
38952.4474 | 1 | 0 | 112
38952.4496 | 1 | 0 | 112
38952.4517 | 1 | 0 | 112
38952.4538 | 1 | 0 | 112
38952.456 | 1 | 0 | 112
38952.4581 | 2 | 0 | 112
38952.4603 | 2057 | 0 | 112
38952.4624 | 2139 | 0 | 112
38952.4645 | 2227 | 0 | 112
38952.4667 | 2333 | 0 | 112
38952.4688 | 2077 | 0 | 112
112
38952.4474 | 1 | 0 | 113
38952.4496 | 1 | 0 | 113
38952.4517 | 1 | 0 | 113
38952.4539 | 1 | 0 | 113
38952.456 | 1 | 0 | 113
38952.4581 | 2 | 0 | 113
38952.4603 | 2395 | 0 | 113
38952.4624 | 2282 | 0 | 113
38952.4645 | 2058 | 0 | 113
38952.4667 | 1856 | 0 | 113
38952.4688 | 1952 | 0 | 113
113
38952.4475 | 1 | 0 | 114
38952.4496 | 1 | 0 | 114
38952.4517 | 1 | 0 | 114
38952.4539 | 1 | 0 | 114
38952.456 | 1 | 0 | 114
38952.4581 | 1 | 0 | 114
38952.4603 | 2103 | 0 | 114
38952.4624 | 907 | 0 | 114
38952.4646 | 1383 | 0 | 114
38952.4667 | 18 | 0 | 114
38952.4688 | 3 | 0 | 114
114
38952.4475 | 1 | 1 | 115
38952.4496 | 1 | 0 | 115
38952.4517 | 1 | 0 | 115
38952.4539 | 1 | 0 | 115
38952.456 | 1 | 0 | 115
38952.4582 | 1 | 0 | 115
38952.4603 | 2427 | 0 | 115
38952.4624 | 2193 | 0 | 115
38952.4646 | 2069 | 0 | 115
38952.4667 | 1922 | 0 | 115
38952.4689 | 1999 | 0 | 115
115
38952.4475 | 1 | 0 | 116
38952.4496 | 1 | 0 | 116
38952.4518 | 1 | 0 | 116
38952.4539 | 1 | 0 | 116
38952.456 | 1 | 0 | 116
38952.4582 | 2 | 0 | 116
38952.4603 | 2537 | 0 | 116
38952.4625 | 907 | 0 | 116
38952.4646 | 3 | 0 | 116
38952.4667 | 5 | 0 | 116
38952.4689 | 3 | 0 | 116
116
38952.4475 | 1 | 0 | 117
38952.4496 | 1 | 0 | 117
38952.4518 | 1 | 0 | 117
38952.4539 | 1 | 0 | 117
38952.4561 | 1 | 0 | 117
38952.4582 | 1 | 0 | 117
38952.4603 | 1993 | 0 | 117
38952.4625 | 1622 | 0 | 117
38952.4646 | 1719 | 0 | 117
38952.4667 | 2045 | 0 | 117
38952.4689 | 2113 | 0 | 117
117
38952.4475 | 1 | 0 | 118
38952.4497 | 1 | 0 | 118
38952.4518 | 1 | 0 | 118
38952.4539 | 1 | 0 | 118
38952.4561 | 2 | 0 | 118
38952.4582 | 2011 | 0 | 118
38952.4603 | 2072 | 0 | 118
38952.4625 | 2502 | 0 | 118
38952.4646 | 2096 | 0 | 118
38952.4668 | 2237 | 0 | 118
38952.4689 | 2236 | 0 | 118
118
38952.4475 | 1 | 0 | 119
38952.4497 | 1 | 1 | 119
38952.4518 | 1 | 0 | 119
38952.4539 | 1 | 0 | 119
38952.4561 | 1 | 0 | 119
38952.4582 | 3 | 0 | 119
38952.4604 | 1975 | 0 | 119
38952.4625 | 2306 | 0 | 119
38952.4646 | 1739 | 0 | 119
38952.4668 | 1791 | 0 | 119
38952.4689 | 542 | 0 | 119
119
38952.4475 | 1 | 0 | 120
38952.4497 | 1 | 0 | 120
38952.4518 | 1 | 0 | 120
38952.454 | 1 | 0 | 120
38952.4561 | 2 | 0 | 120
38952.4582 | 14 | 1 | 120
38952.4604 | 2350 | 0 | 120
38952.4625 | 1682 | 0 | 120
38952.4647 | 2198 | 0 | 120
38952.4668 | 2314 | 0 | 120
38952.4689 | 2574 | 0 | 120
120
38952.4476 | 1 | 0 | 121
38952.4497 | 1 | 0 | 121
38952.4518 | 1 | 0 | 121
38952.454 | 1 | 0 | 121
38952.4561 | 1 | 0 | 121
38952.4583 | 2 | 0 | 121
38952.4604 | 1995 | 0 | 121
38952.4625 | 1326 | 1058 | 121
38952.4647 | 1143 | 1097 | 121
38952.4668 | 1200 | 1179 | 121
38952.4689 | 1020 | 992 | 121
121
38952.4476 | 1 | 0 | 122
38952.4497 | 1 | 0 | 122
38952.4519 | 1 | 0 | 122
38952.454 | 1 | 0 | 122
38952.4561 | 1 | 0 | 122
38952.4583 | 2 | 0 | 122
38952.4604 | 2108 | 0 | 122
38952.4625 | 1038 | 828 | 122
38952.4647 | 1157 | 1187 | 122
38952.4668 | 1097 | 1070 | 122
38952.469 | 1106 | 1080 | 122
122
38952.4476 | 0 | 0 | 123
38952.4497 | 1 | 0 | 123
38952.4519 | 1 | 0 | 123
38952.454 | 1 | 0 | 123
38952.4561 | 1 | 0 | 123
38952.4583 | 2 | 0 | 123
38952.4604 | 2038 | 0 | 123
38952.4626 | 1238 | 4 | 123
38952.4647 | 3 | 5 | 123
38952.4668 | 5 | 5 | 123
38952.469 | 3 | 5 | 123
123
38952.4476 | 1 | 0 | 124
38952.4498 | 1 | 0 | 124
38952.4519 | 1 | 0 | 124
38952.454 | 1 | 0 | 124
38952.4562 | 1 | 0 | 124
38952.4583 | 2043 | 0 | 124
38952.4604 | 2226 | 0 | 124
38952.4626 | 2167 | 2 | 124
38952.4647 | 2062 | 2 | 124
38952.4669 | 2250 | 2 | 124
38952.469 | 2334 | 3 | 124
124
38952.4476 | 1 | 0 | 125
38952.4498 | 1 | 0 | 125
38952.4519 | 1 | 0 | 125
38952.4541 | 1 | 0 | 125
38952.4562 | 1 | 0 | 125
38952.4583 | 3 | 0 | 125
38952.4605 | 1964 | 0 | 125
38952.4626 | 1828 | 1 | 125
38952.4647 | 3 | 1 | 125
38952.4669 | 3 | 1 | 125
125
38952.4477 | 1 | 0 | 126
38952.4498 | 1 | 0 | 126
38952.4519 | 1 | 0 | 126
38952.4541 | 1 | 0 | 126
38952.4562 | 1 | 0 | 126
38952.4583 | 2577 | 0 | 126
38952.4605 | 2495 | 0 | 126
38952.4626 | 2344 | 1 | 126
38952.4648 | 2217 | 1 | 126
38952.4669 | 2258 | 1 | 126
38952.469 | 2083 | 1 | 126
126
38952.4477 | 1 | 0 | 127
38952.4498 | 1 | 0 | 127
38952.4519 | 1 | 0 | 127
38952.4541 | 1 | 0 | 127
38952.4562 | 1 | 0 | 127
38952.4584 | 3 | 0 | 127
38952.4605 | 2029 | 0 | 127
38952.4626 | 1840 | 0 | 127
38952.4648 | 4 | 1 | 127
38952.4669 | 3 | 1 | 127
38952.4691 | 3 | 1 | 127
127
38952.4477 | 1 | 0 | 128
38952.4498 | 1 | 0 | 128
38952.452 | 1 | 0 | 128
38952.4541 | 1 | 0 | 128
38952.4562 | 1 | 0 | 128
38952.4584 | 2336 | 0 | 128
38952.4605 | 2176 | 0 | 128
38952.4627 | 1901 | 0 | 128
38952.4648 | 1852 | 0 | 128
38952.4669 | 2261 | 1 | 128
38952.4691 | 2050 | 0 | 128
128
38952.4477 | 1 | 0 | 129
38952.4498 | 1 | 0 | 129
38952.452 | 1 | 0 | 129
38952.4541 | 1 | 0 | 129
38952.4563 | 1 | 0 | 129
38952.4584 | 3 | 0 | 129
38952.4605 | 2318 | 0 | 129
38952.4627 | 1213 | 0 | 129
38952.4648 | 3 | 0 | 129
38952.4669 | 3 | 0 | 129
38952.4691 | 3 | 0 | 129
129
38952.4477 | 1 | 0 | 130
38952.4498 | 1 | 0 | 130
38952.452 | 1 | 0 | 130
38952.4541 | 1 | 0 | 130
38952.4563 | 1 | 0 | 130
38952.4584 | 2214 | 0 | 130
38952.4605 | 2408 | 0 | 130
38952.4627 | 2065 | 0 | 130
38952.4648 | 2539 | 0 | 130
38952.467 | 2064 | 0 | 130
38952.4691 | 2011 | 0 | 130
130
38952.4477 | 1 | 0 | 131
38952.4499 | 1 | 0 | 131
38952.452 | 1 | 0 | 131
38952.4541 | 1 | 0 | 131
38952.4563 | 1 | 0 | 131
38952.4584 | 2099 | 0 | 131
38952.4606 | 2565 | 0 | 131
38952.4627 | 1957 | 0 | 131
38952.4648 | 2129 | 0 | 131
38952.467 | 2239 | 0 | 131
38952.4691 | 2035 | 0 | 131
131
38952.4477 | 1 | 0 | 132
38952.4499 | 1 | 0 | 132
38952.452 | 1 | 0 | 132
38952.4542 | 1 | 0 | 132
38952.4563 | 1 | 0 | 132
38952.4584 | 2217 | 0 | 132
38952.4606 | 2055 | 0 | 132
38952.4627 | 2600 | 0 | 132
38952.4648 | 2543 | 0 | 132
38952.467 | 2094 | 0 | 132
38952.4691 | 2164 | 0 | 132
132

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -160 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
1 | -159 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
2 | -158 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
3 | -157 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
4 | -156 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
5 | -155 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
6 | -154 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
7 | -153 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
8 | -152 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
9 | -151 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
10 | -150 | 19.3 | 26.4 | 22.4 | 26.2 | 28.6 | 24 | 23.9 | 27
11 | -149 | 19.3 | 26.4 | 22.4 | 26.2 | 28.6 | 24 | 23.9 | 27
12 | -148 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27
13 | -147 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27
14 | -146 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
15 | -145 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
16 | -144 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27
17 | -143 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
18 | -142 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
19 | -141 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
20 | -140 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
21 | -139 | 19.3 | 26.4 | 22.4 | 26.2 | 28.6 | 24 | 23.9 | 26.9
22 | -138 | 19.3 | 26.4 | 22.4 | 26.2 | 28.6 | 24 | 23.9 | 26.9
23 | -137 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
24 | -136 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
25 | -135 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
26 | -134 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
27 | -133 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
28 | -132 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 26.9
29 | -131 | 19.3 | 26.4 | 22.4 | 26.2 | 28.6 | 24 | 23.9 | 27
30 | -130 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
31 | -129 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
32 | -128 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
33 | -127 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
34 | -126 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27
35 | -125 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
36 | -124 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
37 | -123 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
38 | -122 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
39 | -121 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
40 | -120 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
41 | -119 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
42 | -118 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
43 | -117 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
44 | -116 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.1
45 | -115 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
46 | -114 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
47 | -113 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
48 | -112 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
49 | -111 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.1
50 | -110 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
51 | -109 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27
52 | -108 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
53 | -107 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
54 | -106 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
55 | -105 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27
56 | -104 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
57 | -103 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
58 | -102 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
59 | -101 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
60 | -100 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
61 | -99 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27
62 | -98 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
63 | -97 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27
64 | -96 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
65 | -95 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
66 | -94 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.1
67 | -93 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
68 | -92 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
69 | -91 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
70 | -90 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
71 | -89 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
72 | -88 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
73 | -87 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
74 | -86 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
75 | -85 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.1
76 | -84 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.1
77 | -83 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
78 | -82 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
79 | -81 | 19.3 | 26.4 | 22.4 | 26.2 | 28.5 | 24 | 23.9 | 27.1
80 | -80 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.2
81 | -79 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.2
82 | -78 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
83 | -77 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.2
84 | -76 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
85 | -75 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.2
86 | -74 | 19.3 | 26.4 | 22.3 | 26.2 | 28.5 | 24 | 23.9 | 27.1
87 | -73 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
88 | -72 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
89 | -71 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
90 | -70 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
91 | -69 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
92 | -68 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
93 | -67 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
94 | -66 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
95 | -65 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
96 | -64 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
97 | -63 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
98 | -62 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
99 | -61 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
100 | -60 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
101 | -59 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
102 | -58 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
103 | -57 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
104 | -56 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
105 | -55 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
106 | -54 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
107 | -53 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
108 | -52 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
109 | -51 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
110 | -50 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
111 | -49 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
112 | -48 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
113 | -47 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
114 | -46 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
115 | -45 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
116 | -44 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
117 | -43 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
118 | -42 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27
119 | -41 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
120 | -40 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
121 | -39 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
122 | -38 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
123 | -37 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
124 | -36 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
125 | -35 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
126 | -34 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
127 | -33 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
128 | -32 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
129 | -31 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
130 | -30 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
131 | -29 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
132 | -28 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
133 | -27 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
134 | -26 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
135 | -25 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.1
136 | -24 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
137 | -23 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
138 | -22 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
139 | -21 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
140 | -20 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
141 | -19 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
142 | -18 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
143 | -17 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.2
144 | -16 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
145 | -15 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
146 | -14 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
147 | -13 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
148 | -12 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
149 | -11 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
150 | -10 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
151 | -9 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
152 | -8 | 19.3 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
153 | -7 | 19.2 | 26.3 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
154 | -6 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
155 | -5 | 19.2 | 26.4 | 22.3 | 26.2 | 28.6 | 24 | 23.9 | 27.3
156 | -4 | 19.2 | 26.4 | 22.2 | 26.2 | 28.6 | 24 | 23.9 | 27.3
157 | -3 | 19.2 | 27 | 21 | 26.6 | 29.8 | 24.1 | 23.9 | 27.2
158 | -2 | 19.2 | 27.2 | 20.7 | 26.7 | 30.3 | 24.2 | 23.8 | 27.1
159 | -1 | 19.4 | 27.3 | 20.5 | 26.8 | 30.4 | 24.2 | 23.9 | 27.1
160 | 0 | 20.2 | 27.3 | 20.5 | 26.8 | 30.4 | 24.2 | 23.9 | 27.1
161 | 1 | 21.5 | 27.3 | 20.5 | 26.8 | 30.4 | 24.2 | 23.9 | 27.1
162 | 2 | 23.4 | 27.3 | 20.5 | 26.8 | 30.4 | 24.2 | 23.9 | 27.1
163 | 3 | 25.7 | 27.3 | 20.5 | 26.8 | 30.4 | 24.2 | 23.9 | 27.1
164 | 4 | 28.4 | 27.3 | 20.5 | 26.8 | 30.5 | 24.2 | 23.9 | 27.2
165 | 5 | 31.5 | 27.3 | 20.5 | 26.8 | 30.4 | 24.3 | 24 | 27.2
166 | 6 | 34.8 | 27.3 | 20.5 | 26.8 | 30.4 | 24.3 | 24 | 27.2
167 | 7 | 38.4 | 27.3 | 20.5 | 26.8 | 30.4 | 24.4 | 24.1 | 27.3
168 | 8 | 42.2 | 27.3 | 20.5 | 26.8 | 30.5 | 24.5 | 24.2 | 27.3
169 | 9 | 46.2 | 27.3 | 20.5 | 26.8 | 30.5 | 24.5 | 24.2 | 27.3
170 | 10 | 50.4 | 27.3 | 20.5 | 26.8 | 30.5 | 24.6 | 24.3 | 27.3
171 | 11 | 54.8 | 27.3 | 20.5 | 26.8 | 30.5 | 24.7 | 24.4 | 27.4
172 | 12 | 59.3 | 27.3 | 20.5 | 26.8 | 30.5 | 24.8 | 24.5 | 27.5
173 | 13 | 63.9 | 27.3 | 20.5 | 26.8 | 30.5 | 24.9 | 24.6 | 27.5
174 | 14 | 68.7 | 27.4 | 20.5 | 26.8 | 30.6 | 25.1 | 24.7 | 27.6
175 | 15 | 73.6 | 27.4 | 20.5 | 26.8 | 30.6 | 25.2 | 24.8 | 27.7
176 | 16 | 78.6 | 27.4 | 20.5 | 26.8 | 30.6 | 25.4 | 25 | 27.8
177 | 17 | 83.7 | 27.4 | 20.5 | 26.8 | 30.7 | 25.6 | 25.1 | 27.8
178 | 18 | 88.9 | 27.4 | 20.5 | 26.8 | 30.7 | 25.8 | 25.3 | 27.9
179 | 19 | 94.2 | 27.4 | 20.5 | 26.8 | 30.8 | 25.9 | 25.4 | 28.1
180 | 20 | 99.5 | 27.4 | 20.5 | 26.8 | 30.8 | 26.1 | 25.6 | 28.2
181 | 21 | 104.9 | 27.4 | 20.5 | 26.8 | 30.9 | 26.3 | 25.8 | 28.3
182 | 22 | 110.4 | 27.5 | 20.5 | 26.8 | 31 | 26.5 | 26 | 28.4
183 | 23 | 115.9 | 27.5 | 20.6 | 26.8 | 31 | 26.7 | 26.2 | 28.6
184 | 24 | 121.5 | 27.5 | 20.6 | 26.8 | 31.1 | 27 | 26.4 | 28.7
185 | 25 | 127.1 | 27.5 | 20.6 | 26.9 | 31.2 | 27.3 | 26.7 | 28.9
186 | 26 | 132.8 | 27.6 | 20.6 | 26.9 | 31.3 | 27.5 | 26.9 | 29.1
187 | 27 | 138.4 | 27.6 | 20.6 | 26.9 | 31.4 | 27.8 | 27.2 | 29.3
188 | 28 | 144 | 27.6 | 20.6 | 26.9 | 31.5 | 28.1 | 27.5 | 29.5
189 | 29 | 149.7 | 27.7 | 20.6 | 26.9 | 31.6 | 28.4 | 27.8 | 29.7
190 | 30 | 155.3 | 27.7 | 20.7 | 26.9 | 31.7 | 28.7 | 28.1 | 29.9
191 | 31 | 161 | 27.7 | 20.8 | 26.9 | 31.8 | 29.2 | 28.4 | 30.1
192 | 32 | 166.6 | 27.8 | 20.8 | 27 | 31.9 | 29.6 | 28.7 | 30.3
193 | 33 | 172.3 | 27.9 | 20.8 | 27 | 32.1 | 29.9 | 29.1 | 30.6
194 | 34 | 177.9 | 27.9 | 20.8 | 27 | 32.2 | 30.3 | 29.4 | 30.8
195 | 35 | 183.6 | 28 | 20.9 | 27 | 32.4 | 30.6 | 29.8 | 31.1
196 | 36 | 189.2 | 28 | 20.9 | 27.1 | 32.5 | 31 | 30.1 | 31.5
197 | 37 | 194.9 | 28.1 | 21 | 27.1 | 32.7 | 31.4 | 30.6 | 31.8
198 | 38 | 200.6 | 28.2 | 21 | 27.1 | 32.9 | 31.9 | 31 | 32.1
199 | 39 | 206.4 | 28.3 | 21.1 | 27.2 | 33.1 | 32.4 | 31.4 | 32.4
200 | 40 | 212 | 28.4 | 21.1 | 27.2 | 33.3 | 32.9 | 31.9 | 32.8
201 | 41 | 217.7 | 28.4 | 21.2 | 27.3 | 33.5 | 33.3 | 32.4 | 33.3
202 | 42 | 223.4 | 28.5 | 21.3 | 27.3 | 33.7 | 33.9 | 32.9 | 33.7
203 | 43 | 229.1 | 28.6 | 21.4 | 27.4 | 34 | 34.4 | 33.4 | 34.2
204 | 44 | 234.6 | 28.8 | 21.4 | 27.4 | 34.2 | 35 | 33.9 | 34.6
205 | 45 | 240.1 | 28.9 | 21.5 | 27.5 | 34.5 | 35.5 | 34.5 | 35.1
206 | 46 | 245.8 | 29 | 21.6 | 27.6 | 34.8 | 36.1 | 35 | 35.6
207 | 47 | 251.3 | 29.1 | 21.7 | 27.6 | 35 | 36.8 | 35.6 | 36.1
208 | 48 | 256.8 | 29.2 | 21.8 | 27.7 | 35.3 | 37.5 | 36.2 | 36.6
209 | 49 | 262.2 | 29.4 | 21.9 | 27.8 | 35.6 | 38.1 | 36.9 | 37.2
210 | 50 | 267.6 | 29.5 | 22 | 27.9 | 36 | 38.8 | 37.5 | 37.8
211 | 51 | 273.1 | 29.7 | 22.2 | 27.9 | 36.3 | 39.5 | 38.1 | 38.4
212 | 52 | 278.4 | 29.8 | 22.3 | 28 | 36.6 | 40.1 | 38.8 | 39.1
213 | 53 | 283.7 | 30 | 22.4 | 28.1 | 37 | 40.8 | 39.5 | 39.7
214 | 54 | 288.9 | 30.2 | 22.5 | 28.2 | 37.3 | 41.5 | 40.2 | 40.4
215 | 55 | 294.3 | 30.4 | 22.6 | 28.3 | 37.7 | 42.3 | 41 | 41
216 | 56 | 299.7 | 30.6 | 22.8 | 28.5 | 38.1 | 43 | 41.7 | 41.7
217 | 57 | 305 | 30.8 | 23 | 28.6 | 38.5 | 43.8 | 42.4 | 42.5
218 | 58 | 310.2 | 31 | 23.1 | 28.7 | 38.9 | 44.6 | 43.2 | 43.3
219 | 59 | 315.4 | 31.2 | 23.3 | 28.8 | 39.3 | 45.4 | 44 | 44.1
220 | 60 | 320.6 | 31.4 | 23.5 | 29 | 39.8 | 46.2 | 44.8 | 44.9
221 | 61 | 325.7 | 31.7 | 23.6 | 29.1 | 40.2 | 47.1 | 45.6 | 45.8
222 | 62 | 330.8 | 31.9 | 23.8 | 29.3 | 40.7 | 48 | 46.3 | 46.6
223 | 63 | 335.9 | 32.2 | 24 | 29.4 | 41.2 | 48.9 | 47.2 | 47.5
224 | 64 | 341.1 | 32.5 | 24.2 | 29.6 | 41.7 | 49.9 | 48.1 | 48.4
225 | 65 | 346.2 | 32.8 | 24.4 | 29.8 | 42.2 | 51 | 48.9 | 49.3
226 | 66 | 351.4 | 33 | 24.6 | 30 | 42.7 | 52 | 49.9 | 50.3
227 | 67 | 356.7 | 33.3 | 24.8 | 30.2 | 43.2 | 53 | 50.8 | 51.3
228 | 68 | 361.6 | 33.6 | 25 | 30.3 | 43.8 | 54.1 | 51.9 | 52.3
229 | 69 | 366.3 | 34 | 25.3 | 30.5 | 44.4 | 55.2 | 52.9 | 53.3
230 | 70 | 371.1 | 34.3 | 25.5 | 30.7 | 45 | 56.3 | 54 | 54.5
231 | 71 | 375.8 | 34.6 | 25.8 | 31 | 45.6 | 57.4 | 55.2 | 55.6
232 | 72 | 380.4 | 35 | 26.1 | 31.2 | 46.2 | 58.4 | 56.4 | 56.7
233 | 73 | 385 | 35.3 | 26.4 | 31.4 | 46.8 | 59.5 | 57.5 | 57.9
234 | 74 | 389.6 | 35.7 | 26.7 | 31.7 | 47.5 | 60.6 | 58.6 | 59.1
235 | 75 | 394.3 | 36.1 | 27 | 31.9 | 48.2 | 61.7 | 59.8 | 60.3
236 | 76 | 398.8 | 36.5 | 27.3 | 32.2 | 48.8 | 62.9 | 60.9 | 61.6
237 | 77 | 403.3 | 36.9 | 27.6 | 32.4 | 49.6 | 64.2 | 62.1 | 62.8
238 | 78 | 407.9 | 37.3 | 27.9 | 32.7 | 50.3 | 65.3 | 63.3 | 64.2
239 | 79 | 412.3 | 37.7 | 28.2 | 33 | 51.1 | 66.5 | 64.6 | 65.5
240 | 80 | 416.5 | 38.1 | 28.6 | 33.3 | 51.8 | 67.9 | 65.9 | 66.9
241 | 81 | 421 | 38.6 | 29 | 33.6 | 52.6 | 69.3 | 67.1 | 68.3
242 | 82 | 425.5 | 39 | 29.3 | 33.9 | 53.4 | 70.7 | 68.4 | 69.8
243 | 83 | 430 | 39.5 | 29.7 | 34.2 | 54.2 | 72.1 | 69.7 | 71.2
244 | 84 | 434.5 | 39.9 | 30.1 | 34.5 | 55.1 | 73.4 | 70.8 | 72.7
245 | 85 | 438.6 | 40.4 | 30.5 | 34.8 | 56 | 74.7 | 72.2 | 74.3
246 | 86 | 443 | 41 | 30.8 | 35.2 | 56.9 | 76.2 | 73.6 | 75.9
247 | 87 | 447.5 | 41.5 | 31.1 | 35.6 | 57.9 | 77.5 | 75 | 77.5
248 | 88 | 451.7 | 42.3 | 31.2 | 36.1 | 59.1 | 79 | 76.3 | 79.1
249 | 89 | 455.8 | 42.9 | 31.4 | 36.5 | 60.2 | 80.5 | 77.7 | 80.8
250 | 90 | 459.7 | 43.5 | 31.8 | 36.9 | 61.2 | 82 | 79 | 82.5
251 | 91 | 463.7 | 44 | 32.4 | 37.3 | 62.1 | 83.4 | 80.6 | 84.2
252 | 92 | 467.5 | 44.6 | 32.8 | 37.7 | 63.1 | 85 | 82 | 86
253 | 93 | 471.4 | 44.9 | 33.9 | 37.9 | 63.7 | 86.6 | 83.5 | 87.9
254 | 94 | 475.3 | 45.3 | 34.6 | 38.3 | 64.6 | 88.1 | 85 | 89.8
255 | 95 | 479.4 | 45.8 | 35.2 | 38.6 | 65.5 | 89.7 | 86.6 | 91.7
256 | 96 | 483.4 | 46.5 | 35.7 | 39.1 | 66.7 | 91.2 | 88.1 | 93.6
257 | 97 | 486.9 | 47.2 | 36 | 39.6 | 68 | 92.7 | 89.7 | 95.5
258 | 98 | 490.1 | 48 | 36.4 | 40.1 | 69.2 | 94.4 | 91.2 | 97.5
259 | 99 | 492.9 | 48.6 | 37 | 40.6 | 70.2 | 95.9 | 92.8 | 99.4
260 | 100 | 495.5 | 49 | 38.1 | 40.9 | 70.9 | 97.6 | 94.2 | 101.4
261 | 101 | 498.2 | 49.7 | 38.6 | 41.4 | 72.1 | 99.3 | 95.5 | 103.4
262 | 102 | 500.5 | 50.4 | 39.3 | 41.8 | 73.2 | 100.9 | 97.1 | 105.4
263 | 103 | 502.9 | 51.1 | 39.9 | 42.3 | 74.4 | 102.4 | 98.5 | 107.5
264 | 104 | 505 | 51.8 | 40.4 | 42.9 | 75.6 | 104.1 | 99.7 | 109.5
265 | 105 | 507.2 | 52.6 | 40.9 | 43.4 | 76.9 | 105.6 | 101.1 | 111.5
266 | 106 | 509.2 | 53.4 | 41.5 | 44 | 78.1 | 107.3 | 102.7 | 113.6
267 | 107 | 511.2 | 54.2 | 42.1 | 44.5 | 79.4 | 109 | 104 | 115.7
268 | 108 | 513.2 | 55 | 42.7 | 45.1 | 80.5 | 110.6 | 105.3 | 117.8
269 | 109 | 514.8 | 55.7 | 43.4 | 45.6 | 81.7 | 112.1 | 106.7 | 119.9
270 | 110 | 516.3 | 56.5 | 44.1 | 46.2 | 82.9 | 113.5 | 108.1 | 122
271 | 111 | 517.4 | 57.3 | 44.8 | 46.7 | 84 | 115.1 | 109.6 | 124.2
272 | 112 | 518.4 | 58.1 | 45.5 | 47.3 | 85.2 | 116.6 | 111.1 | 126.2
273 | 113 | 519.4 | 58.9 | 46.3 | 47.9 | 86.3 | 118 | 112.4 | 128.3
274 | 114 | 519.9 | 59.7 | 47 | 48.5 | 87.4 | 119.6 | 113.8 | 130.3
275 | 115 | 520 | 60.6 | 47.7 | 49.1 | 88.5 | 120.9 | 115 | 132.3
276 | 116 | 520.2 | 61.4 | 48.4 | 49.7 | 89.6 | 122.3 | 115.9 | 134.4
277 | 117 | 520.4 | 62.3 | 49.1 | 50.3 | 90.7 | 123.7 | 117.1 | 136.4
278 | 118 | 520.6 | 63.1 | 49.8 | 51 | 91.8 | 125.2 | 118.4 | 138.4
279 | 119 | 520.6 | 64 | 50.5 | 51.6 | 92.8 | 126.4 | 119.3 | 140.4
280 | 120 | 520.6 | 64.9 | 51.2 | 52.3 | 93.9 | 127.6 | 120.6 | 142.4
281 | 121 | 520.6 | 65.8 | 51.9 | 53 | 94.9 | 128.7 | 121.9 | 144.4
282 | 122 | 520.6 | 66.7 | 52.6 | 53.6 | 95.9 | 129.8 | 123 | 146.4
283 | 123 | 520.6 | 67.6 | 53.4 | 54.3 | 96.9 | 131 | 124.2 | 148.4
284 | 124 | 520.5 | 68.5 | 54.1 | 55 | 97.9 | 132.2 | 125.3 | 150.4
285 | 125 | 520.6 | 69.4 | 54.9 | 55.7 | 98.9 | 133.5 | 126.3 | 152.4
286 | 126 | 520.7 | 70.3 | 55.7 | 56.3 | 99.9 | 134.7 | 127.4 | 154.4
287 | 127 | 520.5 | 71.2 | 56.4 | 57 | 100.9 | 135.9 | 128.5 | 156.4
288 | 128 | 520.2 | 72.1 | 57.2 | 57.7 | 101.9 | 137 | 129.1 | 158.3
289 | 129 | 520 | 73.1 | 58 | 58.5 | 102.9 | 138.3 | 129.7 | 160.2
290 | 130 | 519.9 | 74.1 | 58.7 | 59.2 | 103.9 | 139.5 | 130.8 | 162.2
291 | 131 | 520 | 75 | 59.5 | 59.9 | 105 | 140.4 | 131.6 | 164.1
292 | 132 | 520 | 76 | 60.3 | 60.7 | 106 | 141.2 | 132.4 | 165.9
293 | 133 | 520 | 76.9 | 61 | 61.4 | 106.9 | 142.1 | 133.3 | 167.8
294 | 134 | 520.1 | 77.9 | 61.9 | 62.1 | 107.9 | 143.2 | 134.2 | 169.7
295 | 135 | 520.4 | 78.8 | 62.7 | 62.9 | 108.8 | 144.1 | 135 | 171.6
296 | 136 | 520.5 | 79.8 | 63.5 | 63.6 | 109.7 | 145 | 136.2 | 173.5
297 | 137 | 520.7 | 80.8 | 64.3 | 64.4 | 110.6 | 146 | 136.9 | 175.4
298 | 138 | 520.8 | 81.7 | 65.2 | 65.2 | 111.5 | 146.9 | 137.8 | 177.2
299 | 139 | 520.4 | 82.7 | 66 | 65.9 | 112.5 | 148 | 138.7 | 179.1
300 | 140 | 520.6 | 83.7 | 66.8 | 66.7 | 113.3 | 149.1 | 139.4 | 180.8
301 | 141 | 521 | 84.7 | 67.7 | 67.5 | 114.2 | 150 | 140.3 | 182.6
302 | 142 | 521.4 | 85.7 | 68.5 | 68.3 | 115.1 | 150.9 | 141.1 | 184.4
303 | 143 | 521.6 | 86.7 | 69.4 | 69.1 | 115.9 | 151.9 | 142 | 186.3
304 | 144 | 521.9 | 87.7 | 70.3 | 69.9 | 116.7 | 152.9 | 143 | 188.1
305 | 145 | 522 | 88.7 | 71.1 | 70.7 | 117.6 | 153.9 | 143.5 | 189.9
306 | 146 | 522.1 | 89.6 | 72 | 71.5 | 118.5 | 154.9 | 144.3 | 191.8
307 | 147 | 522.3 | 90.6 | 72.9 | 72.3 | 119.3 | 155.8 | 145.4 | 193.6
308 | 148 | 522.3 | 91.6 | 73.8 | 73.1 | 120.1 | 156.8 | 146.2 | 195.5
309 | 149 | 522.3 | 92.5 | 74.6 | 73.9 | 121 | 157.9 | 146.8 | 197.3
310 | 150 | 522.6 | 93.5 | 75.4 | 74.8 | 121.8 | 159 | 147.5 | 199.1
311 | 151 | 522.7 | 94.5 | 76.3 | 75.6 | 122.6 | 159.9 | 147.9 | 200.9
312 | 152 | 523 | 95.4 | 77.2 | 76.4 | 123.4 | 160.8 | 148.3 | 202.6
313 | 153 | 523.2 | 96.4 | 78 | 77.2 | 124.2 | 161.6 | 149 | 204.4
314 | 154 | 523.3 | 97.3 | 78.9 | 78 | 124.9 | 162.6 | 149.8 | 206.2
315 | 155 | 523.3 | 98.2 | 79.7 | 78.9 | 125.6 | 163.4 | 150.6 | 207.9
316 | 156 | 523.5 | 99.2 | 80.6 | 79.7 | 126.2 | 164.4 | 151.4 | 209.7
317 | 157 | 523.7 | 100 | 81.5 | 80.5 | 126.9 | 165.3 | 152.1 | 211.4
318 | 158 | 523.6 | 100.9 | 82.4 | 81.3 | 127.4 | 166.1 | 153.1 | 213.1
319 | 159 | 523.6 | 101.8 | 83.3 | 82.1 | 127.9 | 166.9 | 154 | 214.8
320 | 160 | 523.6 | 102.7 | 84.2 | 82.9 | 128.4 | 167.8 | 154.9 | 216.5
321 | 161 | 523.8 | 103.6 | 85.1 | 83.8 | 128.9 | 168.6 | 155.7 | 218.2
322 | 162 | 523.8 | 104.5 | 85.9 | 84.6 | 129.2 | 169.1 | 156.4 | 219.9
323 | 163 | 523.6 | 105.4 | 86.9 | 85.4 | 129.7 | 169.9 | 157.3 | 221.5
324 | 164 | 523.5 | 106.3 | 87.7 | 86.2 | 130.1 | 170.6 | 157.8 | 223.1
325 | 165 | 523.4 | 107.2 | 88.6 | 87 | 130.7 | 171.1 | 158.5 | 224.7
326 | 166 | 523.3 | 108.1 | 89.5 | 87.9 | 131.1 | 172 | 158.9 | 226.3
327 | 167 | 523.1 | 109 | 90.5 | 88.7 | 131.6 | 172.7 | 159.5 | 227.9
328 | 168 | 522.7 | 109.9 | 91.4 | 89.5 | 132 | 173.4 | 160.2 | 229.4
329 | 169 | 522.6 | 110.9 | 92.4 | 90.3 | 132.5 | 173.9 | 160.9 | 230.9
330 | 170 | 522.6 | 111.9 | 93.4 | 91.2 | 133.1 | 174.7 | 161.6 | 232.5
331 | 171 | 522.4 | 112.9 | 94.3 | 92 | 133.6 | 175.3 | 162.2 | 234.1
332 | 172 | 522.3 | 113.9 | 95.3 | 92.9 | 134.2 | 176.1 | 162.8 | 235.5
333 | 173 | 522.3 | 114.9 | 96.3 | 93.8 | 134.8 | 176.9 | 163.4 | 237
334 | 174 | 522.1 | 115.9 | 97.3 | 94.7 | 135.4 | 177.7 | 163.8 | 238.5
335 | 175 | 521.9 | 116.9 | 98.2 | 95.6 | 135.9 | 178.3 | 164.4 | 239.9
336 | 176 | 521.7 | 117.9 | 99.3 | 96.4 | 136.5 | 179 | 165 | 241.3
337 | 177 | 521.5 | 118.9 | 100.2 | 97.4 | 137.1 | 179.9 | 165.5 | 242.8
338 | 178 | 521.4 | 119.9 | 101.2 | 98.3 | 137.7 | 180.6 | 166.2 | 244.2
339 | 179 | 521.3 | 120.9 | 102.1 | 99.2 | 138.2 | 181.1 | 166.7 | 245.6
340 | 180 | 521.4 | 121.9 | 103.1 | 100.1 | 138.7 | 181.7 | 167.8 | 247
341 | 181 | 521.2 | 122.9 | 104.1 | 101 | 139.2 | 182.3 | 168.7 | 248.4
342 | 182 | 521.3 | 123.9 | 105 | 101.9 | 139.7 | 182.9 | 168.9 | 249.9
343 | 183 | 521.5 | 124.9 | 106 | 102.8 | 140.2 | 183.3 | 169.6 | 251.2
344 | 184 | 521.5 | 125.8 | 107 | 103.8 | 140.7 | 183.9 | 170.1 | 252.6
345 | 185 | 521.5 | 126.8 | 108.1 | 104.7 | 141.2 | 184.5 | 170.7 | 254
346 | 186 | 521.4 | 127.7 | 109.1 | 105.7 | 141.7 | 185.1 | 171.4 | 255.2
347 | 187 | 521.3 | 128.7 | 110.1 | 106.7 | 142.2 | 185.7 | 172 | 256.5
348 | 188 | 521.4 | 129.6 | 111.1 | 107.7 | 142.6 | 186.2 | 172.7 | 257.8
349 | 189 | 521.5 | 130.5 | 112.1 | 108.8 | 143.1 | 186.8 | 173.3 | 259.1
350 | 190 | 521.5 | 131.5 | 113 | 109.8 | 143.6 | 187.2 | 173.5 | 260.3
351 | 191 | 521.3 | 132.4 | 114.1 | 110.9 | 144.1 | 187.7 | 173.9 | 261.6
352 | 192 | 521.2 | 133.3 | 115.1 | 111.9 | 144.6 | 188 | 174.6 | 262.8
353 | 193 | 521.2 | 134.2 | 116.2 | 113 | 145.1 | 188.5 | 175.1 | 264
354 | 194 | 521.2 | 135.1 | 117.2 | 114 | 145.7 | 189 | 175.5 | 265.1
355 | 195 | 521.5 | 136.1 | 118.2 | 115 | 146.2 | 189.5 | 175.8 | 266.3
356 | 196 | 521.6 | 137 | 119.4 | 116.1 | 146.9 | 190.1 | 176.5 | 267.4
357 | 197 | 521.6 | 138 | 120.4 | 117.1 | 147.6 | 190.6 | 176.8 | 268.5
358 | 198 | 521.5 | 139 | 121.4 | 118.1 | 148.2 | 191 | 177.4 | 269.7
359 | 199 | 521.5 | 139.9 | 122.4 | 119.2 | 148.7 | 191.6 | 177.9 | 270.8
360 | 200 | 521.7 | 140.9 | 123.4 | 120.2 | 149.4 | 192.1 | 178.2 | 271.9
361 | 201 | 521.8 | 141.9 | 124.4 | 121.2 | 150 | 192.6 | 179 | 273
362 | 202 | 521.8 | 142.8 | 125.4 | 122.2 | 150.7 | 193.1 | 179.6 | 274
363 | 203 | 521.8 | 143.8 | 126.4 | 123.2 | 151.4 | 193.6 | 179.9 | 275.1
364 | 204 | 521.6 | 144.8 | 127.3 | 124.3 | 152.2 | 194 | 180.6 | 276.2
365 | 205 | 521.4 | 145.7 | 128.4 | 125.3 | 152.9 | 194.5 | 181 | 277.3
366 | 206 | 521.5 | 146.7 | 129.3 | 126.3 | 153.7 | 194.8 | 181.5 | 278.3
367 | 207 | 521.5 | 147.7 | 130.3 | 127.3 | 154.4 | 195.2 | 182 | 279.3
368 | 208 | 521.3 | 148.7 | 131.3 | 128.3 | 155.2 | 195.7 | 182.5 | 280.3
369 | 209 | 521.6 | 149.7 | 132.2 | 129.2 | 156 | 196.2 | 183.3 | 281.3
370 | 210 | 521.9 | 150.6 | 133.2 | 130.2 | 156.8 | 196.4 | 183.6 | 282.2
371 | 211 | 522 | 151.6 | 134.1 | 131.1 | 157.5 | 196.9 | 183.9 | 283.2
372 | 212 | 522.1 | 152.5 | 135.1 | 132.1 | 158.3 | 197.3 | 184.2 | 284.1
373 | 213 | 522.3 | 153.5 | 136 | 133 | 159 | 197.7 | 184.9 | 285
374 | 214 | 522.1 | 154.5 | 136.9 | 133.9 | 160 | 198.1 | 185.1 | 285.9
375 | 215 | 522 | 155.5 | 137.8 | 134.8 | 161.1 | 198.5 | 185.4 | 286.8
376 | 216 | 522 | 156.4 | 138.7 | 135.7 | 161.9 | 198.9 | 185.7 | 287.7
377 | 217 | 521.7 | 157.5 | 139.6 | 136.6 | 162.8 | 199.3 | 185.9 | 288.6
378 | 218 | 521.4 | 158.5 | 140.5 | 137.5 | 163.7 | 199.7 | 186.3 | 289.4
379 | 219 | 521.4 | 159.5 | 141.4 | 138.4 | 164.7 | 200.1 | 186.5 | 290.3
380 | 220 | 521.5 | 160.5 | 142.3 | 139.3 | 165.7 | 200.5 | 186.6 | 291.2
381 | 221 | 521.7 | 161.5 | 143.1 | 140.2 | 166.6 | 201 | 186.6 | 292
382 | 222 | 521.8 | 162.4 | 144 | 141 | 167.6 | 201.5 | 186.5 | 292.8
383 | 223 | 521.8 | 163.4 | 144.9 | 141.9 | 168.7 | 201.9 | 186.5 | 293.6
384 | 224 | 521.9 | 164.3 | 145.8 | 142.8 | 169.7 | 202.2 | 186.9 | 294.3
385 | 225 | 522.1 | 165.3 | 146.7 | 143.6 | 170.8 | 202.5 | 187.5 | 295.1
386 | 226 | 522.5 | 166.2 | 147.6 | 144.5 | 171.8 | 203 | 187.8 | 295.8
387 | 227 | 522.5 | 167.1 | 148.4 | 145.4 | 172.8 | 203.4 | 187.9 | 296.5
388 | 228 | 522.5 | 168 | 149.2 | 146.2 | 173.6 | 203.7 | 188 | 297.2
389 | 229 | 522.2 | 168.9 | 150.1 | 147.1 | 174.3 | 204 | 188.3 | 297.8
390 | 230 | 521.9 | 169.7 | 151 | 147.9 | 174.9 | 204.3 | 188.4 | 298.5
391 | 231 | 521.7 | 170.6 | 151.8 | 148.8 | 175.4 | 204.6 | 188.5 | 299.2
392 | 232 | 521.7 | 171.4 | 152.7 | 149.6 | 175.9 | 205 | 188.7 | 299.8
393 | 233 | 521.7 | 172.2 | 153.5 | 150.5 | 176.4 | 205.5 | 189 | 300.4
394 | 234 | 521.6 | 173 | 154.4 | 151.3 | 176.9 | 205.9 | 189.3 | 301
395 | 235 | 521.5 | 173.7 | 155.2 | 152.2 | 177.4 | 206.3 | 189.7 | 301.7
396 | 236 | 521.7 | 174.5 | 156 | 153 | 178.1 | 206.8 | 190.1 | 302.3
397 | 237 | 521.6 | 175.3 | 156.8 | 153.8 | 178.7 | 207.1 | 190.3 | 302.9
398 | 238 | 521.6 | 176 | 157.7 | 154.7 | 179.4 | 207.4 | 190.9 | 303.6
399 | 239 | 521.5 | 176.8 | 158.5 | 155.5 | 180 | 207.8 | 191 | 304.2
400 | 240 | 521.6 | 177.5 | 159.2 | 156.3 | 180.9 | 208.2 | 191.2 | 304.8
401 | 241 | 521.7 | 178.3 | 160.1 | 157.1 | 181.7 | 208.7 | 191.5 | 305.5
402 | 242 | 521.9 | 179 | 160.8 | 157.9 | 182.6 | 209 | 191.9 | 306.1
403 | 243 | 522 | 179.7 | 161.6 | 158.7 | 183.4 | 209.5 | 192.1 | 306.7
404 | 244 | 521.9 | 180.4 | 162.4 | 159.5 | 184.2 | 209.8 | 192.3 | 307.3
405 | 245 | 521.7 | 181.1 | 163.2 | 160.3 | 185.1 | 210.2 | 192.6 | 308
406 | 246 | 521.4 | 181.9 | 164 | 161.1 | 186 | 210.5 | 193.1 | 308.6
407 | 247 | 521.4 | 182.6 | 164.7 | 161.9 | 186.8 | 210.9 | 193.4 | 309.2
408 | 248 | 521.4 | 183.3 | 165.5 | 162.7 | 187.7 | 211.4 | 193.8 | 309.9
409 | 249 | 521.4 | 184 | 166.3 | 163.5 | 188.5 | 211.9 | 194.1 | 310.5
410 | 250 | 521.4 | 184.7 | 167 | 164.2 | 189.4 | 212.4 | 194 | 311.1
411 | 251 | 521.3 | 185.4 | 167.8 | 165 | 190.3 | 212.9 | 194.1 | 311.8
412 | 252 | 521.5 | 186.1 | 168.5 | 165.7 | 191 | 213.3 | 194.1 | 312.4
413 | 253 | 521.4 | 186.9 | 169.3 | 166.5 | 191.9 | 213.7 | 194.4 | 313.1
414 | 254 | 521.3 | 187.7 | 170.1 | 167.2 | 192.8 | 214.2 | 194.6 | 313.7
415 | 255 | 521.1 | 188.4 | 170.8 | 168 | 193.7 | 214.7 | 194.8 | 314.3
416 | 256 | 521 | 189.2 | 171.4 | 168.8 | 194.5 | 215.1 | 195.4 | 314.9
417 | 257 | 520.7 | 190 | 172.2 | 169.5 | 195.4 | 215.5 | 195.7 | 315.5
418 | 258 | 520.5 | 190.8 | 172.9 | 170.3 | 196.2 | 215.9 | 196.1 | 316.1
419 | 259 | 520.6 | 191.6 | 173.6 | 171 | 197.1 | 216.2 | 196.6 | 316.7
420 | 260 | 520.5 | 192.3 | 174.3 | 171.7 | 197.9 | 216.6 | 196.8 | 317.3
421 | 261 | 520.4 | 193 | 175.1 | 172.4 | 198.7 | 217 | 197.4 | 317.9
422 | 262 | 520.6 | 193.6 | 175.8 | 173.2 | 199.5 | 217.5 | 197.7 | 318.5
423 | 263 | 520.5 | 194.3 | 176.5 | 173.9 | 200.3 | 217.9 | 198.1 | 319
424 | 264 | 520.6 | 194.9 | 177.2 | 174.6 | 201.1 | 218.4 | 198.3 | 319.6
425 | 265 | 520.7 | 195.5 | 177.9 | 175.3 | 201.9 | 218.8 | 198.4 | 320.2
426 | 266 | 520.5 | 196.1 | 178.6 | 176 | 202.6 | 219.2 | 198.8 | 320.8
427 | 267 | 520.4 | 196.7 | 179.3 | 176.7 | 203.4 | 219.7 | 198.9 | 321.4
428 | 268 | 520.1 | 197.4 | 180 | 177.4 | 204.2 | 220.1 | 199.3 | 322
429 | 269 | 519.9 | 198.1 | 180.6 | 178.1 | 204.9 | 220.6 | 199.5 | 322.6
430 | 270 | 519.8 | 198.8 | 181.3 | 178.8 | 205.8 | 221 | 199.9 | 323.1
431 | 271 | 519.8 | 199.5 | 181.9 | 179.5 | 206.5 | 221.4 | 200.1 | 323.6
432 | 272 | 519.7 | 200.2 | 182.6 | 180.2 | 207.3 | 221.8 | 200.4 | 324.2
433 | 273 | 519.6 | 200.8 | 183.2 | 180.9 | 208 | 222.2 | 200.7 | 324.7
434 | 274 | 519.6 | 201.5 | 183.9 | 181.6 | 208.7 | 222.5 | 201 | 325.2
435 | 275 | 519.6 | 202.1 | 184.5 | 182.3 | 209.4 | 223 | 201.2 | 325.7
436 | 276 | 519.6 | 202.7 | 185.2 | 182.9 | 210 | 223.5 | 201.6 | 326.2
437 | 277 | 519.7 | 203.3 | 185.9 | 183.6 | 210.7 | 224 | 201.9 | 326.7
438 | 278 | 519.9 | 203.9 | 186.6 | 184.3 | 211.3 | 224.4 | 202 | 327.2
439 | 279 | 520.1 | 204.5 | 187.3 | 184.9 | 211.9 | 225 | 202.4 | 327.8
440 | 280 | 520.3 | 205.1 | 188 | 185.6 | 212.5 | 225.5 | 202.8 | 328.4
441 | 281 | 520.5 | 205.7 | 188.5 | 186.3 | 213.1 | 226 | 202.9 | 328.9
442 | 282 | 520.6 | 206.2 | 189.3 | 186.9 | 213.7 | 226.5 | 203.2 | 329.5
443 | 283 | 520.6 | 206.8 | 189.9 | 187.6 | 214.3 | 227 | 203.2 | 330
444 | 284 | 520.7 | 207.3 | 190.6 | 188.3 | 214.8 | 227.4 | 203.2 | 330.6
445 | 285 | 520.9 | 207.8 | 191.3 | 188.9 | 215.6 | 227.9 | 203.2 | 331
446 | 286 | 521 | 208.4 | 191.9 | 189.6 | 216.2 | 228.3 | 203.4 | 331.6
447 | 287 | 521.2 | 208.9 | 192.5 | 190.3 | 216.8 | 228.8 | 203.6 | 332.1
448 | 288 | 521.4 | 209.4 | 193.3 | 190.9 | 217.3 | 229.3 | 204.2 | 332.5
449 | 289 | 521.5 | 209.9 | 193.9 | 191.6 | 217.8 | 229.7 | 204.4 | 333
450 | 290 | 521.6 | 210.4 | 194.5 | 192.2 | 218.4 | 230.2 | 204.6 | 333.5
451 | 291 | 521.8 | 210.9 | 195.2 | 192.9 | 219 | 230.6 | 204.7 | 334
452 | 292 | 522 | 211.5 | 195.8 | 193.5 | 219.5 | 231.1 | 204.5 | 334.5
453 | 293 | 522.1 | 212 | 196.5 | 194.2 | 220.2 | 231.5 | 204.8 | 335
454 | 294 | 522 | 212.5 | 197.2 | 194.8 | 220.8 | 231.9 | 205.2 | 335.5
455 | 295 | 522 | 213 | 197.9 | 195.5 | 221.4 | 232.3 | 205.6 | 335.9
456 | 296 | 521.9 | 213.5 | 198.6 | 196.1 | 222.1 | 232.8 | 205.9 | 336.3
457 | 297 | 521.8 | 214.1 | 199.3 | 196.7 | 222.6 | 233.2 | 206.1 | 336.8
458 | 298 | 521.7 | 214.7 | 199.9 | 197.4 | 223.2 | 233.6 | 206.5 | 337.2
459 | 299 | 521.6 | 215.2 | 200.5 | 198.1 | 223.7 | 234 | 206.6 | 337.6
460 | 300 | 521.3 | 215.8 | 201.1 | 198.7 | 224.3 | 234.4 | 206.6 | 338
461 | 301 | 521.2 | 216.4 | 201.8 | 199.3 | 224.9 | 234.9 | 207 | 338.5
462 | 302 | 521.2 | 216.9 | 202.4 | 200 | 225.5 | 235.3 | 207.2 | 338.9
463 | 303 | 521.2 | 217.5 | 203.1 | 200.7 | 226.1 | 235.7 | 207.6 | 339.3
464 | 304 | 521.1 | 218 | 203.8 | 201.3 | 226.6 | 236.1 | 207.9 | 339.7
465 | 305 | 521.2 | 218.5 | 204.4 | 201.9 | 227.3 | 236.6 | 208.3 | 340.2
466 | 306 | 521.5 | 219.1 | 205.1 | 202.5 | 227.7 | 237 | 208.6 | 340.6
467 | 307 | 521.6 | 219.6 | 205.8 | 203.2 | 228.1 | 237.5 | 208.8 | 341.1
468 | 308 | 521.8 | 220.2 | 206.4 | 203.8 | 228.6 | 237.9 | 209.1 | 341.6
469 | 309 | 521.9 | 220.8 | 207 | 204.5 | 229.2 | 238.4 | 209.1 | 342
470 | 310 | 521.9 | 221.4 | 207.7 | 205.1 | 229.6 | 238.9 | 209.3 | 342.4
471 | 311 | 521.9 | 221.9 | 208.4 | 205.7 | 230.1 | 239.3 | 209.6 | 342.8
472 | 312 | 521.8 | 222.6 | 209 | 206.3 | 230.7 | 239.7 | 209.8 | 343.2
473 | 313 | 521.8 | 223.2 | 209.7 | 206.9 | 231.2 | 240.1 | 210 | 343.6
474 | 314 | 522 | 223.9 | 210.3 | 207.5 | 231.7 | 240.6 | 210.3 | 344
475 | 315 | 522.2 | 224.7 | 210.9 | 208.2 | 232.1 | 241 | 210.6 | 344.3
476 | 316 | 522.4 | 225.5 | 211.6 | 208.8 | 232.6 | 241.5 | 210.8 | 344.7
477 | 317 | 522.3 | 226.2 | 212.3 | 209.4 | 233.2 | 241.9 | 211 | 345.1
478 | 318 | 522.3 | 226.9 | 213 | 209.9 | 233.8 | 242.3 | 211.3 | 345.5
479 | 319 | 522.4 | 227.6 | 213.6 | 210.6 | 234.2 | 242.9 | 211.5 | 346
480 | 320 | 522.4 | 228.2 | 214.4 | 211.2 | 234.7 | 243.3 | 211.8 | 346.4
481 | 321 | 522.2 | 228.8 | 215.1 | 211.8 | 235.2 | 243.8 | 212.1 | 346.8
482 | 322 | 522.1 | 229.4 | 215.8 | 212.3 | 235.7 | 244.2 | 212.3 | 347.2
483 | 323 | 522.1 | 230.1 | 216.5 | 213 | 236.3 | 244.7 | 212.5 | 347.6
484 | 324 | 522.2 | 230.7 | 217.2 | 213.6 | 237 | 245.2 | 212.8 | 348
485 | 325 | 522.2 | 231.3 | 217.8 | 214.1 | 237.5 | 245.6 | 212.8 | 348.4
486 | 326 | 522.1 | 231.9 | 218.6 | 214.7 | 238.2 | 246.1 | 212.6 | 348.9
487 | 327 | 521.9 | 232.6 | 219.2 | 215.3 | 238.9 | 246.5 | 212.7 | 349.3
488 | 328 | 521.8 | 233.3 | 219.8 | 215.9 | 239.8 | 246.9 | 212.8 | 349.7
489 | 329 | 521.5 | 234 | 220.5 | 216.5 | 240.6 | 247.4 | 213.1 | 350.1
490 | 330 | 521.2 | 234.7 | 221.1 | 217.1 | 241.5 | 247.9 | 213.1 | 350.5
491 | 331 | 520.8 | 235.4 | 221.7 | 217.7 | 242.3 | 248.3 | 213.4 | 350.9
492 | 332 | 520.7 | 236 | 222.4 | 218.3 | 243.1 | 248.7 | 213.7 | 351.3
493 | 333 | 520.6 | 236.7 | 223 | 218.9 | 243.9 | 249.1 | 213.9 | 351.7
494 | 334 | 520.5 | 237.4 | 223.6 | 219.5 | 244.8 | 249.5 | 214 | 352
495 | 335 | 520.3 | 238.1 | 224.2 | 220.1 | 245.8 | 249.9 | 214.3 | 352.3
496 | 336 | 520.2 | 238.8 | 224.8 | 220.7 | 246.5 | 250.4 | 214.4 | 352.7
497 | 337 | 520.1 | 239.5 | 225.4 | 221.3 | 247.2 | 250.8 | 214.7 | 353
498 | 338 | 519.9 | 240.2 | 226.1 | 221.8 | 248 | 251.2 | 215 | 353.5
499 | 339 | 519.9 | 240.9 | 226.7 | 222.5 | 248.6 | 251.7 | 215.2 | 353.8
500 | 340 | 520 | 241.6 | 227.3 | 223 | 249.3 | 252.1 | 215.3 | 354.2
501 | 341 | 520.1 | 242.3 | 228 | 223.6 | 250.1 | 252.5 | 215.3 | 354.6
502 | 342 | 520.3 | 242.9 | 228.6 | 224.2 | 250.8 | 253 | 215.2 | 355
503 | 343 | 520.3 | 243.6 | 229.2 | 224.8 | 251.4 | 253.5 | 215 | 355.4
504 | 344 | 520.3 | 244.3 | 229.8 | 225.4 | 252.2 | 253.9 | 215.2 | 355.8
505 | 345 | 520.4 | 245 | 230.5 | 226 | 252.9 | 254.4 | 215.4 | 356.1
506 | 346 | 520.3 | 245.7 | 231.2 | 226.5 | 253.5 | 254.8 | 215.5 | 356.5
507 | 347 | 520.3 | 246.3 | 231.8 | 227.1 | 254.2 | 255.2 | 215.7 | 356.9
508 | 348 | 520.5 | 247 | 232.5 | 227.7 | 254.8 | 255.6 | 215.8 | 357.3
509 | 349 | 520.5 | 247.7 | 233.2 | 228.2 | 255.5 | 255.9 | 216 | 357.7
510 | 350 | 520.5 | 248.3 | 233.8 | 228.8 | 256.1 | 256.3 | 216.3 | 358.1
511 | 351 | 520.6 | 248.9 | 234.4 | 229.4 | 256.6 | 256.7 | 216.5 | 358.5
512 | 352 | 520.6 | 249.5 | 235.1 | 229.9 | 257.1 | 257 | 216.8 | 358.9
513 | 353 | 520.6 | 250.2 | 235.7 | 230.5 | 257.6 | 257.3 | 217.2 | 359.3
514 | 354 | 520.6 | 250.8 | 236.4 | 231.1 | 258.2 | 257.6 | 217.4 | 359.7
515 | 355 | 520.6 | 251.4 | 237.1 | 231.6 | 258.7 | 257.8 | 217.7 | 360.1
516 | 356 | 520.6 | 252.1 | 237.7 | 232.2 | 259.2 | 258.1 | 218 | 360.5
517 | 357 | 520.5 | 252.7 | 238.3 | 232.7 | 259.6 | 258.3 | 218.5 | 360.9
518 | 358 | 520.4 | 253.3 | 238.9 | 233.3 | 260 | 258.4 | 218.9 | 361.3
519 | 359 | 520.4 | 253.9 | 239.5 | 233.9 | 260.5 | 258.6 | 219.5 | 361.7
520 | 360 | 520.3 | 254.4 | 240.1 | 234.4 | 260.9 | 258.8 | 219.9 | 362.1
521 | 361 | 520.3 | 254.8 | 240.7 | 235 | 261.3 | 259 | 220.3 | 362.5
522 | 362 | 520.4 | 255.2 | 241.3 | 235.5 | 261.8 | 259.3 | 220.5 | 362.9
523 | 363 | 520.5 | 255.7 | 241.9 | 236.1 | 262.2 | 259.5 | 220.9 | 363.3
524 | 364 | 520.6 | 256.2 | 242.5 | 236.6 | 262.6 | 259.8 | 221.3 | 363.7
525 | 365 | 520.6 | 256.7 | 243.1 | 237.2 | 263.1 | 260 | 221.8 | 364
526 | 366 | 520.8 | 257.3 | 243.7 | 237.8 | 263.5 | 260.3 | 222.3 | 364.4
527 | 367 | 520.9 | 257.8 | 244.3 | 238.3 | 264 | 260.6 | 222.8 | 364.8
528 | 368 | 521.1 | 258.4 | 244.9 | 238.9 | 264.5 | 260.9 | 223.3 | 365.2
529 | 369 | 521.3 | 259 | 245.4 | 239.4 | 264.9 | 261.3 | 223.6 | 365.6
530 | 370 | 521.6 | 259.6 | 246 | 240 | 265.4 | 261.6 | 223.9 | 365.9
531 | 371 | 521.6 | 260.2 | 246.6 | 240.5 | 265.9 | 262 | 224.3 | 366.3
532 | 372 | 521.6 | 260.8 | 247.2 | 241.1 | 266.3 | 262.4 | 224.6 | 366.6
533 | 373 | 521.6 | 261.3 | 247.9 | 241.6 | 266.9 | 262.6 | 225.1 | 367
534 | 374 | 521.6 | 261.9 | 248.6 | 242.1 | 267.5 | 263 | 225.8 | 367.3
535 | 375 | 521.5 | 262.5 | 249.1 | 242.7 | 268 | 263.4 | 226.3 | 367.7
536 | 376 | 521.4 | 263.1 | 249.7 | 243.2 | 268.5 | 263.7 | 226.8 | 368.1
537 | 377 | 521.4 | 263.6 | 250.2 | 243.8 | 269.1 | 264 | 227.3 | 368.4
538 | 378 | 521.4 | 264.2 | 250.8 | 244.3 | 269.7 | 264.3 | 227.9 | 368.8
539 | 379 | 521.3 | 264.7 | 251.4 | 244.9 | 270.2 | 264.7 | 228.6 | 369.1
540 | 380 | 521.3 | 265.3 | 252 | 245.4 | 270.8 | 264.9 | 229.2 | 369.4
541 | 381 | 521.1 | 265.8 | 252.5 | 246 | 271.4 | 265.2 | 229.8 | 369.7
542 | 382 | 520.8 | 266.4 | 253 | 246.6 | 271.9 | 265.5 | 230.4 | 370
543 | 383 | 520.6 | 267 | 253.6 | 247.2 | 272.4 | 265.7 | 231 | 370.3
544 | 384 | 520.6 | 267.5 | 254.2 | 247.7 | 273 | 266 | 231.4 | 370.6
545 | 385 | 520.7 | 268.1 | 254.8 | 248.3 | 273.5 | 266.3 | 231.7 | 370.9
546 | 386 | 520.8 | 268.7 | 255.4 | 248.9 | 273.9 | 266.6 | 232 | 371.2
547 | 387 | 520.7 | 269.3 | 255.9 | 249.5 | 274.4 | 266.9 | 232.2 | 371.5
548 | 388 | 520.9 | 269.8 | 256.5 | 250.1 | 274.9 | 267.3 | 232.4 | 371.9
549 | 389 | 521.1 | 270.4 | 257.1 | 250.7 | 275.4 | 267.6 | 232.7 | 372.2
550 | 390 | 521 | 270.9 | 257.7 | 251.3 | 275.9 | 268 | 232.8 | 372.5
551 | 391 | 521 | 271.5 | 258.2 | 251.9 | 276.4 | 268.5 | 233 | 372.9
552 | 392 | 521.1 | 272.1 | 258.8 | 252.5 | 276.9 | 268.9 | 232.7 | 373.2
553 | 393 | 521 | 272.7 | 259.3 | 253.1 | 277.3 | 269.3 | 232.5 | 373.5
554 | 394 | 521 | 273.3 | 259.9 | 253.7 | 277.9 | 269.7 | 232.5 | 373.9
555 | 395 | 520.9 | 273.9 | 260.4 | 254.3 | 278.5 | 270.1 | 232.7 | 374.2
556 | 396 | 520.7 | 274.5 | 260.9 | 254.8 | 279 | 270.5 | 233 | 374.5
557 | 397 | 520.5 | 275.1 | 261.5 | 255.3 | 279.5 | 270.9 | 233.4 | 374.7
558 | 398 | 520.4 | 275.7 | 261.9 | 255.9 | 280.2 | 271.3 | 233.6 | 375
559 | 399 | 520.4 | 276.2 | 262.5 | 256.4 | 280.7 | 271.8 | 233.8 | 375.2
560 | 400 | 520.3 | 276.8 | 263 | 257 | 281.3 | 272.2 | 234 | 375.5
561 | 401 | 520 | 277.3 | 263.5 | 257.5 | 281.9 | 272.6 | 234.1 | 375.7
562 | 402 | 520 | 277.8 | 264.1 | 258.1 | 282.4 | 273 | 234.3 | 376
563 | 403 | 520.1 | 278.4 | 264.6 | 258.6 | 283 | 273.4 | 234.5 | 376.3
564 | 404 | 520 | 278.9 | 265.1 | 259.1 | 283.6 | 273.7 | 234.8 | 376.5
565 | 405 | 520.1 | 279.4 | 265.7 | 259.7 | 284.2 | 274 | 235.1 | 376.8
566 | 406 | 520.2 | 280 | 266.2 | 260.2 | 284.8 | 274.4 | 235.5 | 377.1
567 | 407 | 520.3 | 280.5 | 266.8 | 260.8 | 285.3 | 274.7 | 235.7 | 377.3
568 | 408 | 520.3 | 281.1 | 267.3 | 261.3 | 285.8 | 275.1 | 236 | 377.5
569 | 409 | 520.4 | 281.6 | 267.9 | 261.9 | 286.3 | 275.4 | 236.3 | 377.8
570 | 410 | 520.6 | 282.2 | 268.4 | 262.4 | 286.7 | 275.7 | 236.7 | 378
571 | 411 | 520.8 | 282.7 | 268.9 | 263 | 287.3 | 276.1 | 237.1 | 378.2
572 | 412 | 521.1 | 283.3 | 269.5 | 263.5 | 287.8 | 276.4 | 237.5 | 378.5
573 | 413 | 521.2 | 283.8 | 270 | 264.1 | 288.4 | 276.7 | 238 | 378.7
574 | 414 | 521.4 | 284.3 | 270.6 | 264.6 | 289 | 277.1 | 238.6 | 378.9
575 | 415 | 521.4 | 284.9 | 271.2 | 265.2 | 289.5 | 277.5 | 239.3 | 379.2
576 | 416 | 521.5 | 285.4 | 271.7 | 265.7 | 290 | 277.8 | 239.9 | 379.4
577 | 417 | 521.6 | 285.9 | 272.3 | 266.2 | 290.5 | 278.2 | 240.3 | 379.5
578 | 418 | 521.6 | 286.4 | 272.9 | 266.7 | 291.1 | 278.5 | 240.7 | 379.8
579 | 419 | 521.6 | 287 | 273.4 | 267.3 | 291.7 | 278.9 | 241.3 | 380
580 | 420 | 521.5 | 287.5 | 273.9 | 267.9 | 292.3 | 279.3 | 241.7 | 380.3
581 | 421 | 521.3 | 288.1 | 274.5 | 268.4 | 293 | 279.6 | 242.1 | 380.5
582 | 422 | 521.2 | 288.7 | 275 | 269 | 293.7 | 280 | 242.6 | 380.7
583 | 423 | 521.2 | 289.3 | 275.5 | 269.5 | 294.4 | 280.3 | 243.1 | 381
584 | 424 | 521 | 289.8 | 276 | 270.1 | 295 | 280.7 | 243.7 | 381.2
585 | 425 | 521 | 290.5 | 276.6 | 270.6 | 295.6 | 281 | 244.1 | 381.4
586 | 426 | 520.9 | 291.1 | 277 | 271.2 | 296.2 | 281.4 | 244.5 | 381.6
587 | 427 | 520.9 | 291.6 | 277.6 | 271.7 | 296.8 | 281.8 | 244.9 | 381.8
588 | 428 | 520.9 | 292.2 | 278.1 | 272.2 | 297.4 | 282.2 | 245.4 | 382
589 | 429 | 520.8 | 292.8 | 278.7 | 272.8 | 298 | 282.5 | 245.8 | 382.3
590 | 430 | 521 | 293.4 | 279.3 | 273.3 | 298.5 | 282.9 | 246.1 | 382.5
591 | 431 | 521 | 294 | 279.8 | 273.8 | 299.1 | 283.3 | 246.4 | 382.7
592 | 432 | 521.1 | 294.6 | 280.3 | 274.4 | 299.7 | 283.7 | 246.8 | 383
593 | 433 | 521 | 295.2 | 280.8 | 274.9 | 300.2 | 284.1 | 247.1 | 383.2
594 | 434 | 521 | 295.7 | 281.4 | 275.4 | 300.7 | 284.5 | 247.6 | 383.5
595 | 435 | 520.9 | 296.3 | 281.9 | 276 | 301.3 | 284.9 | 248 | 383.7
596 | 436 | 521 | 296.9 | 282.4 | 276.5 | 301.8 | 285.3 | 248.4 | 384
597 | 437 | 521.2 | 297.5 | 282.9 | 277.1 | 302.3 | 285.7 | 248.9 | 384.2
598 | 438 | 521.1 | 298.1 | 283.4 | 277.6 | 302.8 | 286 | 249.4 | 384.4
599 | 439 | 520.9 | 298.7 | 283.9 | 278.2 | 303.4 | 286.4 | 249.8 | 384.6
600 | 440 | 520.8 | 299.3 | 284.4 | 278.7 | 303.9 | 286.8 | 250.2 | 384.9
601 | 441 | 520.8 | 299.9 | 285 | 279.2 | 304.5 | 287.2 | 250.7 | 385.1
602 | 442 | 520.6 | 300.5 | 285.4 | 279.8 | 305 | 287.6 | 251.2 | 385.3
603 | 443 | 520.5 | 301.1 | 286 | 280.3 | 305.5 | 288 | 251.6 | 385.6
604 | 444 | 520.6 | 301.6 | 286.5 | 280.9 | 306.1 | 288.4 | 252.1 | 385.9
605 | 445 | 520.8 | 302.2 | 287 | 281.4 | 306.6 | 288.7 | 252.5 | 386.1
606 | 446 | 520.9 | 302.8 | 287.5 | 281.9 | 307.2 | 289 | 253 | 386.4
607 | 447 | 520.9 | 303.4 | 288 | 282.5 | 307.7 | 289.3 | 253.4 | 386.6
608 | 448 | 520.9 | 304 | 288.5 | 283 | 308.4 | 289.6 | 253.8 | 386.8
609 | 449 | 520.8 | 304.6 | 289 | 283.5 | 308.9 | 289.9 | 254.2 | 387
610 | 450 | 520.8 | 305.2 | 289.5 | 284.1 | 309.5 | 290.2 | 254.5 | 387.2
611 | 451 | 520.6 | 305.8 | 290 | 284.6 | 310.2 | 290.5 | 254.9 | 387.5
612 | 452 | 520.5 | 306.3 | 290.5 | 285.2 | 310.7 | 290.8 | 255.2 | 387.7
613 | 453 | 520.4 | 306.8 | 291 | 285.7 | 311.4 | 291.1 | 255.5 | 387.9
614 | 454 | 520.2 | 307.4 | 291.5 | 286.2 | 312 | 291.4 | 255.8 | 388
615 | 455 | 520.4 | 307.9 | 292 | 286.8 | 312.5 | 291.7 | 256 | 388.3
616 | 456 | 520.4 | 308.4 | 292.5 | 287.3 | 313.1 | 292.1 | 256.2 | 388.4
617 | 457 | 520.6 | 309 | 293 | 287.9 | 313.7 | 292.4 | 256.5 | 388.6
618 | 458 | 520.8 | 309.5 | 293.5 | 288.4 | 314.3 | 292.7 | 256.7 | 388.9
619 | 459 | 520.8 | 310 | 294.1 | 288.9 | 314.9 | 293 | 256.9 | 389.1
620 | 460 | 520.9 | 310.6 | 294.6 | 289.5 | 315.6 | 293.3 | 257.2 | 389.3
621 | 461 | 521.2 | 311.1 | 295.2 | 290 | 316.2 | 293.7 | 257.6 | 389.5
622 | 462 | 521.4 | 311.6 | 295.7 | 290.5 | 316.8 | 293.9 | 257.9 | 389.7
623 | 463 | 521.4 | 312.2 | 296.2 | 291 | 317.5 | 294.2 | 258.2 | 389.9
624 | 464 | 521.2 | 312.7 | 296.8 | 291.6 | 318.1 | 294.4 | 258.4 | 390.1
625 | 465 | 521.2 | 313.2 | 297.3 | 292.1 | 318.8 | 294.8 | 258.6 | 390.3
626 | 466 | 521 | 313.7 | 297.9 | 292.6 | 319.4 | 295.1 | 258.8 | 390.5
627 | 467 | 520.9 | 314.2 | 298.4 | 293.2 | 320 | 295.4 | 259 | 390.7
628 | 468 | 520.9 | 314.7 | 298.9 | 293.7 | 320.8 | 295.6 | 259.2 | 390.9
629 | 469 | 521 | 315.2 | 299.4 | 294.2 | 321.4 | 295.9 | 259.4 | 391.1
630 | 470 | 521.1 | 315.8 | 300 | 294.8 | 322.1 | 296.1 | 259.6 | 391.3
631 | 471 | 521 | 316.3 | 300.5 | 295.3 | 322.8 | 296.3 | 259.8 | 391.5
632 | 472 | 520.9 | 316.8 | 301 | 295.8 | 323.5 | 296.5 | 260 | 391.6
633 | 473 | 520.8 | 317.3 | 301.6 | 296.4 | 324.1 | 296.7 | 260.3 | 391.8
634 | 474 | 520.9 | 317.7 | 302.1 | 296.9 | 324.8 | 296.9 | 260.5 | 391.9
635 | 475 | 520.7 | 318.3 | 302.7 | 297.5 | 325.5 | 297 | 260.7 | 392.1
636 | 476 | 520.5 | 318.8 | 303.2 | 298 | 326.1 | 297.2 | 260.9 | 392.2
637 | 477 | 520.5 | 319.3 | 303.8 | 298.6 | 326.8 | 297.4 | 261.1 | 392.4
638 | 478 | 520.5 | 319.8 | 304.3 | 299.1 | 327.4 | 297.6 | 261.3 | 392.6
639 | 479 | 520.4 | 320.3 | 304.8 | 299.6 | 328 | 297.8 | 261.4 | 392.7
640 | 480 | 520.3 | 320.9 | 305.3 | 300.2 | 328.6 | 298 | 261.6 | 392.9
641 | 481 | 520.1 | 321.3 | 305.9 | 300.7 | 329.3 | 298.2 | 261.8 | 393
642 | 482 | 520 | 321.9 | 306.4 | 301.3 | 330 | 298.5 | 261.9 | 393.2
643 | 483 | 519.9 | 322.3 | 306.9 | 301.8 | 330.6 | 298.7 | 262.1 | 393.4
644 | 484 | 519.8 | 322.7 | 307.5 | 302.4 | 331.2 | 298.9 | 262.2 | 393.5
645 | 485 | 519.7 | 323.1 | 308 | 302.9 | 331.9 | 299.1 | 262.4 | 393.7
646 | 486 | 519.4 | 323.5 | 308.5 | 303.5 | 332.5 | 299.3 | 262.5 | 393.8
647 | 487 | 519.4 | 323.9 | 309.1 | 304 | 333.1 | 299.5 | 262.7 | 393.9
648 | 488 | 519.5 | 324.3 | 309.6 | 304.6 | 333.8 | 299.7 | 262.8 | 394
649 | 489 | 519.7 | 324.7 | 310.1 | 305.1 | 334.5 | 299.9 | 262.9 | 394.2
650 | 490 | 519.6 | 325.2 | 310.6 | 305.6 | 335.2 | 300.1 | 263.1 | 394.4
651 | 491 | 519.8 | 325.6 | 311.1 | 306.2 | 335.9 | 300.4 | 263.2 | 394.6
652 | 492 | 520 | 326 | 311.7 | 306.7 | 336.6 | 300.7 | 263.3 | 394.7
653 | 493 | 520.2 | 326.4 | 312.2 | 307.3 | 337.3 | 300.9 | 263.5 | 394.9
654 | 494 | 520.6 | 326.8 | 312.8 | 307.8 | 338 | 301.2 | 263.7 | 395.1
655 | 495 | 520.9 | 327.3 | 313.3 | 308.4 | 338.7 | 301.5 | 263.8 | 395.2
656 | 496 | 521.1 | 327.8 | 313.9 | 308.9 | 339.4 | 301.7 | 264 | 395.4
657 | 497 | 521.3 | 328.3 | 314.5 | 309.5 | 340.1 | 302.1 | 264.1 | 395.5
658 | 498 | 521.4 | 328.7 | 315 | 310 | 340.9 | 302.3 | 264.3 | 395.7
659 | 499 | 521.6 | 329.1 | 315.5 | 310.6 | 341.6 | 302.5 | 264.5 | 395.9
660 | 500 | 521.6 | 329.6 | 316 | 311.1 | 342.3 | 302.7 | 264.6 | 396.1
661 | 501 | 521.5 | 330 | 316.5 | 311.7 | 343.1 | 302.8 | 264.8 | 396.3
662 | 502 | 521.7 | 330.5 | 317 | 312.2 | 343.8 | 303.1 | 264.9 | 396.4
663 | 503 | 521.6 | 330.9 | 317.5 | 312.8 | 344.4 | 303.4 | 265.1 | 396.6
664 | 504 | 521.6 | 331.3 | 318.1 | 313.3 | 345 | 303.6 | 265.3 | 396.8
665 | 505 | 521.7 | 331.8 | 318.6 | 313.9 | 345.6 | 303.8 | 265.4 | 396.9
666 | 506 | 521.7 | 332.2 | 319.1 | 314.4 | 346.2 | 304.1 | 265.6 | 397.1
667 | 507 | 521.6 | 332.7 | 319.6 | 315 | 346.8 | 304.3 | 265.8 | 397.3
668 | 508 | 521.6 | 333.1 | 320.1 | 315.5 | 347.5 | 304.6 | 266 | 397.4
669 | 509 | 521.7 | 333.6 | 320.6 | 316.1 | 348.1 | 304.8 | 266.2 | 397.5
670 | 510 | 521.6 | 334.1 | 321.1 | 316.6 | 348.8 | 305.1 | 266.4 | 397.7
671 | 511 | 521.5 | 334.4 | 321.6 | 317.2 | 349.4 | 305.3 | 266.6 | 397.8
672 | 512 | 521.4 | 334.9 | 322.1 | 317.7 | 350.1 | 305.5 | 266.8 | 397.9
673 | 513 | 521.5 | 335.3 | 322.6 | 318.3 | 350.7 | 305.7 | 267 | 398
674 | 514 | 521.5 | 335.7 | 323.1 | 318.8 | 351.4 | 305.8 | 267.1 | 398.1
675 | 515 | 521.4 | 336.2 | 323.6 | 319.4 | 352.1 | 306 | 267.3 | 398.3
676 | 516 | 521.3 | 336.5 | 324.1 | 320 | 352.7 | 306.2 | 267.5 | 398.4
677 | 517 | 521.3 | 337 | 324.7 | 320.5 | 353.5 | 306.4 | 267.7 | 398.5
678 | 518 | 521.4 | 337.4 | 325.1 | 321.1 | 354.1 | 306.6 | 267.8 | 398.7
679 | 519 | 521.5 | 337.9 | 325.6 | 321.7 | 354.8 | 306.9 | 268 | 398.8
680 | 520 | 521.3 | 338.3 | 326.1 | 322.2 | 355.5 | 307.2 | 268.2 | 398.9
681 | 521 | 521.1 | 338.7 | 326.6 | 322.8 | 356.2 | 307.4 | 268.4 | 399.1
682 | 522 | 520.8 | 339.1 | 327.1 | 323.4 | 356.8 | 307.7 | 268.5 | 399.2
683 | 523 | 520.8 | 339.4 | 327.6 | 323.9 | 357.4 | 307.9 | 268.7 | 399.4
684 | 524 | 520.8 | 339.8 | 328.1 | 324.5 | 358 | 308.1 | 268.9 | 399.5
685 | 525 | 520.8 | 340.2 | 328.6 | 325.1 | 358.5 | 308.3 | 269.1 | 399.7
686 | 526 | 520.8 | 340.6 | 329.2 | 325.6 | 359 | 308.6 | 269.3 | 399.8
687 | 527 | 520.6 | 341 | 329.7 | 326.2 | 359.5 | 308.8 | 269.5 | 400
688 | 528 | 520.8 | 341.4 | 330.2 | 326.7 | 359.9 | 309.1 | 269.7 | 400.1
689 | 529 | 520.6 | 341.9 | 330.6 | 327.3 | 360.4 | 309.3 | 269.9 | 400.2
690 | 530 | 520.5 | 342.3 | 331.1 | 327.9 | 360.8 | 309.6 | 270.1 | 400.4
691 | 531 | 520.4 | 342.7 | 331.6 | 328.5 | 361.3 | 309.9 | 270.3 | 400.5
692 | 532 | 520.3 | 343.1 | 332 | 329 | 361.9 | 310.1 | 270.6 | 400.6
693 | 533 | 520.5 | 343.5 | 332.5 | 329.6 | 362.4 | 310.4 | 270.8 | 400.8
694 | 534 | 520.5 | 343.8 | 333 | 330.1 | 362.8 | 310.7 | 271 | 400.9
695 | 535 | 520.5 | 344.3 | 333.5 | 330.7 | 363.2 | 310.9 | 271.2 | 401
696 | 536 | 520.5 | 344.7 | 333.9 | 331.2 | 363.7 | 311.2 | 271.5 | 401.1
697 | 537 | 520.5 | 345 | 334.4 | 331.8 | 364.1 | 311.4 | 271.7 | 401.2
698 | 538 | 520.3 | 345.3 | 334.9 | 332.3 | 364.6 | 311.7 | 271.9 | 401.3
699 | 539 | 520.3 | 345.8 | 335.4 | 332.9 | 365 | 312 | 272.2 | 401.4
700 | 540 | 520.4 | 346.2 | 336 | 333.4 | 365.4 | 312.3 | 272.4 | 401.5
701 | 541 | 520.4 | 346.7 | 336.4 | 334 | 365.8 | 312.5 | 272.7 | 401.6
702 | 542 | 520.5 | 347.1 | 337 | 334.5 | 366.2 | 312.8 | 272.9 | 401.7
703 | 543 | 520.5 | 347.5 | 337.4 | 335.1 | 366.6 | 313.1 | 273.2 | 401.8
704 | 544 | 520.6 | 347.8 | 337.8 | 335.6 | 366.9 | 313.3 | 273.4 | 401.9
705 | 545 | 520.8 | 348.2 | 338.4 | 336.1 | 367.3 | 313.5 | 273.7 | 402
706 | 546 | 520.9 | 348.7 | 338.8 | 336.6 | 367.6 | 313.8 | 274 | 402.1
707 | 547 | 521.1 | 349 | 339.2 | 337.2 | 367.9 | 314 | 274.2 | 402.2
708 | 548 | 521 | 349.5 | 339.7 | 337.7 | 368.3 | 314.1 | 274.5 | 402.3
709 | 549 | 521.1 | 349.9 | 340.3 | 338.2 | 368.6 | 314.3 | 274.8 | 402.4
710 | 550 | 521.1 | 350.3 | 340.8 | 338.6 | 368.9 | 314.4 | 275.1 | 402.6
711 | 551 | 521.1 | 350.7 | 341.3 | 339.1 | 369.2 | 314.6 | 275.4 | 402.7
712 | 552 | 521.3 | 351.1 | 341.8 | 339.6 | 369.5 | 314.7 | 275.6 | 402.8
713 | 553 | 521.3 | 351.6 | 342.3 | 340.1 | 369.9 | 314.8 | 275.9 | 403
714 | 554 | 521.3 | 352.1 | 342.7 | 340.7 | 370.3 | 315 | 276.2 | 403.1
715 | 555 | 521.2 | 352.5 | 343.2 | 341.2 | 370.6 | 315.2 | 276.5 | 403.2
716 | 556 | 521.2 | 352.9 | 343.7 | 341.6 | 371 | 315.4 | 276.8 | 403.3
717 | 557 | 521.2 | 353.4 | 344.2 | 342.1 | 371.4 | 315.6 | 277.1 | 403.3
718 | 558 | 521.2 | 353.8 | 344.6 | 342.6 | 371.7 | 315.8 | 277.3 | 403.5
719 | 559 | 521 | 354.2 | 345.1 | 343.1 | 372.1 | 316 | 277.6 | 403.6
720 | 560 | 521.1 | 354.6 | 345.6 | 343.6 | 372.4 | 316.2 | 277.9 | 403.7
721 | 561 | 521.2 | 355 | 346.1 | 344.1 | 372.7 | 316.3 | 278.3 | 403.8
722 | 562 | 521 | 355.5 | 346.5 | 344.6 | 373.1 | 316.5 | 278.6 | 403.9
723 | 563 | 520.8 | 355.9 | 346.9 | 345.1 | 373.5 | 316.8 | 278.9 | 404
724 | 564 | 520.9 | 356.4 | 347.4 | 345.5 | 373.9 | 317 | 279.2 | 404.1
725 | 565 | 520.9 | 356.9 | 347.8 | 346 | 374.4 | 317.2 | 279.6 | 404.1
726 | 566 | 520.9 | 357.3 | 348.3 | 346.5 | 374.9 | 317.4 | 279.9 | 404.2
727 | 567 | 520.6 | 357.8 | 348.9 | 346.9 | 375.3 | 317.6 | 280.3 | 404.2
728 | 568 | 520.7 | 358.2 | 349.3 | 347.4 | 375.9 | 317.9 | 280.6 | 404.3
729 | 569 | 520.9 | 358.7 | 349.8 | 347.9 | 376.5 | 318.1 | 280.9 | 404.4
730 | 570 | 521.1 | 359.1 | 350.3 | 348.3 | 377 | 318.4 | 281.3 | 404.4
731 | 571 | 521.3 | 359.6 | 350.9 | 348.8 | 377.6 | 318.6 | 281.6 | 404.5
732 | 572 | 521.4 | 360.1 | 351.4 | 349.2 | 378.2 | 318.8 | 282 | 404.6
733 | 573 | 521.5 | 360.6 | 352 | 349.6 | 378.8 | 319.1 | 282.3 | 404.6
734 | 574 | 521.6 | 361 | 352.5 | 350.1 | 379.4 | 319.3 | 282.7 | 404.7
735 | 575 | 521.8 | 361.5 | 353.1 | 350.5 | 380.1 | 319.6 | 283 | 404.7
736 | 576 | 522 | 362 | 353.6 | 351 | 380.7 | 319.8 | 283.4 | 404.8
737 | 577 | 521.9 | 362.6 | 354.1 | 351.4 | 381.3 | 320 | 283.7 | 404.9
738 | 578 | 521.9 | 363.1 | 354.7 | 351.9 | 381.9 | 320.2 | 284 | 405
739 | 579 | 521.8 | 363.7 | 355.3 | 352.3 | 382.6 | 320.5 | 284.4 | 405.2
740 | 580 | 521.7 | 364.4 | 355.8 | 352.8 | 383.3 | 320.7 | 284.7 | 405.3
741 | 581 | 521.6 | 365 | 356.4 | 353.2 | 384 | 320.8 | 285 | 405.4
742 | 582 | 521.5 | 365.7 | 357 | 353.7 | 384.8 | 321 | 285.3 | 405.4
743 | 583 | 521.4 | 366.4 | 357.5 | 354.1 | 385.7 | 321.1 | 285.6 | 405.5
744 | 584 | 521.3 | 367.2 | 358 | 354.6 | 386.4 | 321.3 | 285.8 | 405.5
745 | 585 | 521.3 | 367.9 | 358.5 | 355 | 387.4 | 321.5 | 286.1 | 405.6
746 | 586 | 521.3 | 368.7 | 359.1 | 355.5 | 388.3 | 321.6 | 286.4 | 405.7
747 | 587 | 521 | 369.5 | 359.7 | 355.9 | 389.2 | 321.8 | 286.6 | 405.7
748 | 588 | 520.9 | 370.3 | 360.2 | 356.3 | 390.1 | 322 | 286.8 | 405.8
749 | 589 | 520.9 | 371.2 | 360.8 | 356.8 | 391.1 | 322.2 | 287.1 | 405.9
750 | 590 | 520.8 | 372 | 361.4 | 357.2 | 392 | 322.4 | 287.3 | 406
751 | 591 | 520.9 | 372.9 | 362 | 357.7 | 393 | 322.6 | 287.5 | 406.1
752 | 592 | 521.2 | 373.8 | 362.6 | 358.1 | 394.1 | 322.8 | 287.7 | 406.2
753 | 593 | 521.2 | 374.5 | 363.2 | 358.6 | 395.1 | 323 | 288 | 406.3
754 | 594 | 520.9 | 375.2 | 363.9 | 359 | 396.3 | 323.2 | 288.2 | 406.3
755 | 595 | 520.8 | 375.9 | 364.5 | 359.5 | 397.3 | 323.5 | 288.3 | 406.4
756 | 596 | 520.4 | 376.5 | 365 | 359.9 | 398.5 | 323.7 | 288.5 | 406.4
757 | 597 | 520.4 | 377.1 | 365.6 | 360.5 | 399.6 | 324 | 288.7 | 406.5
758 | 598 | 520.5 | 377.7 | 366.3 | 361.2 | 400.7 | 324.2 | 288.9 | 406.6
759 | 599 | 520.5 | 378.3 | 367 | 361.8 | 401.9 | 324.5 | 289.1 | 406.6
760 | 600 | 520.3 | 379 | 367.6 | 362.4 | 403.1 | 324.7 | 289.3 | 406.7
761 | 601 | 520.4 | 379.8 | 368.2 | 363 | 404.4 | 325 | 289.5 | 406.8
762 | 602 | 520.4 | 380.5 | 368.9 | 363.6 | 405.6 | 325.3 | 289.7 | 406.8
763 | 603 | 520.4 | 381.2 | 369.5 | 364.1 | 406.9 | 325.5 | 289.9 | 406.9
764 | 604 | 520.5 | 382 | 370.2 | 364.6 | 408.4 | 325.8 | 290.1 | 406.9
765 | 605 | 520.7 | 382.8 | 370.9 | 365.1 | 409.8 | 326.1 | 290.3 | 407
766 | 606 | 520.8 | 383.7 | 371.7 | 365.6 | 411.4 | 326.4 | 290.5 | 407
767 | 607 | 520.6 | 384.6 | 372.6 | 366.1 | 413 | 326.7 | 290.7 | 407.1
768 | 608 | 520.5 | 385.4 | 373.4 | 366.6 | 414.7 | 327 | 290.9 | 407.1
769 | 609 | 520.6 | 386.3 | 374.2 | 367.1 | 416.5 | 327.3 | 291.1 | 407.2
770 | 610 | 520.7 | 387.2 | 375 | 367.6 | 418.2 | 327.5 | 291.3 | 407.2
771 | 611 | 520.7 | 388 | 375.9 | 368.1 | 419.9 | 327.7 | 291.5 | 407.3
772 | 612 | 520.6 | 388.9 | 376.7 | 368.6 | 421.5 | 327.9 | 291.7 | 407.3
773 | 613 | 520.7 | 389.8 | 377.7 | 369.1 | 423.2 | 328.1 | 291.9 | 407.4
774 | 614 | 520.8 | 390.7 | 378.6 | 369.6 | 424.8 | 328.3 | 292.1 | 407.5
775 | 615 | 520.8 | 391.6 | 379.5 | 370.1 | 426.4 | 328.5 | 292.3 | 407.6
776 | 616 | 520.7 | 392.5 | 380.5 | 370.6 | 428 | 328.7 | 292.5 | 407.7
777 | 617 | 520.7 | 393.5 | 381.4 | 371.2 | 429.5 | 328.9 | 292.7 | 407.8
778 | 618 | 520.7 | 394.4 | 382.5 | 371.7 | 431 | 329.1 | 293 | 407.9
779 | 619 | 520.9 | 395.4 | 383.7 | 372.2 | 432.4 | 329.4 | 293.2 | 408
780 | 620 | 521 | 396.3 | 384.8 | 372.7 | 433.9 | 329.6 | 293.4 | 408.1
781 | 621 | 521.1 | 397.3 | 385.8 | 373.3 | 435.3 | 329.9 | 293.6 | 408.2
782 | 622 | 521 | 398.3 | 386.8 | 373.9 | 436.7 | 330.1 | 293.9 | 408.3
783 | 623 | 521 | 399.3 | 387.8 | 374.5 | 438.1 | 330.4 | 294.1 | 408.3
784 | 624 | 521.1 | 400.3 | 388.8 | 375.1 | 439.5 | 330.7 | 294.4 | 408.4
785 | 625 | 521.2 | 401.3 | 389.9 | 375.8 | 440.8 | 330.9 | 294.6 | 408.5
786 | 626 | 521.4 | 402.3 | 391 | 376.5 | 442.1 | 331.2 | 294.9 | 408.6
787 | 627 | 521.6 | 403.4 | 392 | 377.2 | 443.2 | 331.5 | 295.1 | 408.7
788 | 628 | 521.8 | 404.4 | 393 | 378 | 444.3 | 331.7 | 295.3 | 408.7
789 | 629 | 521.8 | 405.5 | 393.9 | 378.8 | 445.1 | 332 | 295.6 | 408.8
790 | 630 | 521.6 | 406.5 | 395 | 379.5 | 445.9 | 332.3 | 295.8 | 408.9
791 | 631 | 521.4 | 407.6 | 396.3 | 380.3 | 446.5 | 332.6 | 296 | 409
792 | 632 | 521.2 | 408.7 | 397.4 | 381.2 | 446.8 | 332.8 | 296.3 | 409.1
793 | 633 | 521.1 | 409.8 | 398.5 | 382.1 | 446.7 | 333.1 | 296.5 | 409.3
794 | 634 | 521.1 | 410.9 | 399.6 | 382.9 | 446.6 | 333.4 | 296.7 | 409.4
795 | 635 | 521 | 412 | 400.6 | 383.9 | 446.6 | 333.7 | 296.9 | 409.4
796 | 636 | 521 | 413.2 | 401.6 | 384.9 | 446.6 | 334 | 297.2 | 409.5
797 | 637 | 521 | 414.3 | 402.6 | 385.9 | 446.9 | 334.3 | 297.4 | 409.5
798 | 638 | 521.1 | 415.5 | 403.6 | 386.9 | 447.1 | 334.6 | 297.6 | 409.6
799 | 639 | 521.3 | 416.6 | 404.6 | 388 | 447.1 | 334.9 | 297.9 | 409.7
800 | 640 | 521.3 | 417.7 | 405.5 | 389.2 | 447.1 | 335.2 | 298.1 | 409.8
801 | 641 | 521.2 | 421.4 | 406.3 | 390.4 | 446.9 | 335.5 | 298.3 | 409.9
802 | 642 | 521.3 | 425.6 | 407.1 | 391.5 | 445.8 | 335.8 | 298.6 | 410
803 | 643 | 521.3 | 429 | 407.9 | 392.8 | 444.3 | 336.1 | 298.8 | 410.1
804 | 644 | 521.4 | 431.7 | 408.8 | 394 | 442.7 | 336.4 | 299.1 | 410.2
805 | 645 | 521.5 | 434 | 409.7 | 395.3 | 440.8 | 336.7 | 299.3 | 410.2
806 | 646 | 521.6 | 436.1 | 410.6 | 396.5 | 439.4 | 336.9 | 299.5 | 410.3
807 | 647 | 521.6 | 437.9 | 411.5 | 397.8 | 437.3 | 337.2 | 299.8 | 410.4
808 | 648 | 521.6 | 439.5 | 412.4 | 399.2 | 434.6 | 337.5 | 300 | 410.5
809 | 649 | 521.5 | 440.9 | 413.4 | 400.5 | 433.9 | 337.7 | 300.2 | 410.6
810 | 650 | 521.7 | 442.1 | 414.3 | 401.8 | 433 | 338 | 300.5 | 410.7
811 | 651 | 521.8 | 443 | 415.1 | 403.1 | 432.5 | 338.3 | 300.7 | 410.8
812 | 652 | 521.7 | 443.7 | 416.1 | 404.4 | 432.2 | 338.5 | 300.9 | 410.9
813 | 653 | 521.8 | 443.9 | 416.9 | 405.7 | 431.9 | 338.8 | 301.1 | 411
814 | 654 | 522 | 443.3 | 417.7 | 407 | 431.1 | 339.1 | 301.3 | 411.1
815 | 655 | 522 | 441.6 | 418.6 | 408.3 | 431.1 | 339.4 | 301.6 | 411.1
816 | 656 | 521.9 | 439.7 | 419.4 | 409.7 | 431.1 | 339.7 | 301.8 | 411.1
817 | 657 | 521.9 | 438.2 | 420.3 | 411.1 | 430.7 | 340.1 | 302 | 411.2
818 | 658 | 522 | 437.4 | 421.1 | 412.5 | 430.2 | 340.4 | 302.3 | 411.3
819 | 659 | 522 | 436.6 | 421.9 | 414 | 431.3 | 340.7 | 302.5 | 411.3
820 | 660 | 521.8 | 435.7 | 422.9 | 415.5 | 433.9 | 341 | 302.8 | 411.3
821 | 661 | 521.8 | 434.8 | 423.7 | 417 | 436.4 | 341.3 | 303 | 411.4
822 | 662 | 521.9 | 434.3 | 424.7 | 418.6 | 437.3 | 341.6 | 303.3 | 411.4
823 | 663 | 522.1 | 434.2 | 425.5 | 420.3 | 436.8 | 341.9 | 303.6 | 411.5
824 | 664 | 522.3 | 434.5 | 426.4 | 422.1 | 435 | 342.3 | 304 | 411.6
825 | 665 | 522.5 | 435.1 | 427.3 | 424.1 | 432.1 | 342.6 | 304.3 | 411.6
826 | 666 | 522.5 | 436.1 | 428.3 | 426.1 | 432.3 | 342.9 | 304.6 | 411.7
827 | 667 | 522.6 | 437.3 | 429.3 | 428.2 | 431.8 | 343.2 | 305 | 411.7
828 | 668 | 522.7 | 438.7 | 430.3 | 430.2 | 430.3 | 343.5 | 305.3 | 411.7
829 | 669 | 522.8 | 440.1 | 431.3 | 432.3 | 426.6 | 343.9 | 305.7 | 411.8
830 | 670 | 522.6 | 441.6 | 432.4 | 434.4 | 423.7 | 344.2 | 306.1 | 411.8
831 | 671 | 522.6 | 443.2 | 433.5 | 436.5 | 420 | 344.5 | 306.4 | 411.9
832 | 672 | 522.8 | 444.7 | 434.7 | 438.5 | 417 | 344.8 | 306.8 | 411.8
833 | 673 | 522.7 | 446 | 435.8 | 440.7 | 414.5 | 345.2 | 307.2 | 411.8
834 | 674 | 522.6 | 447.2 | 437.1 | 442.7 | 413.1 | 345.5 | 307.5 | 411.8
835 | 675 | 522.5 | 448.3 | 438.4 | 444.8 | 412.9 | 345.8 | 307.9 | 411.8
836 | 676 | 522.3 | 449.4 | 439.7 | 446.9 | 414.1 | 346.1 | 308.3 | 411.8
837 | 677 | 522.2 | 450.4 | 441.2 | 448.9 | 416.5 | 346.4 | 308.6 | 411.8
838 | 678 | 522.1 | 451.4 | 442.6 | 448 | 418.2 | 346.7 | 309 | 411.8
839 | 679 | 522.2 | 452.4 | 444.2 | 441.5 | 419.9 | 347 | 309.3 | 411.8
840 | 680 | 522.2 | 453.3 | 445.7 | 434.6 | 421.7 | 347.3 | 309.7 | 411.9
841 | 681 | 522.2 | 454.2 | 447.2 | 427.9 | 424.2 | 347.6 | 310 | 411.9
842 | 682 | 522.2 | 455.1 | 448.7 | 421.4 | 426.9 | 347.9 | 310.3 | 411.9
843 | 683 | 522.1 | 455.9 | 450 | 415.2 | 429.4 | 348.1 | 310.6 | 411.9
844 | 684 | 522 | 456.7 | 451.3 | 408.3 | 431.7 | 348.4 | 310.9 | 412
845 | 685 | 522 | 457.2 | 452.3 | 401.7 | 433.7 | 348.6 | 311.2 | 412
846 | 686 | 521.9 | 457.7 | 453.1 | 395.7 | 436.2 | 348.9 | 311.5 | 412.1
847 | 687 | 521.9 | 458 | 453.7 | 390.1 | 439 | 349.2 | 311.8 | 412.2
848 | 688 | 521.8 | 458.4 | 454.2 | 384.7 | 440.6 | 349.4 | 312.1 | 412.2
849 | 689 | 521.7 | 458.7 | 454.6 | 379.3 | 442.1 | 349.7 | 312.4 | 412.3
850 | 690 | 521.6 | 458.9 | 454.9 | 374.4 | 443.8 | 350.1 | 312.7 | 412.4
851 | 691 | 521.6 | 459.1 | 455 | 370.6 | 445.2 | 350.4 | 312.9 | 412.4
852 | 692 | 521.5 | 459.2 | 454.8 | 366.4 | 447 | 350.7 | 313.2 | 412.5
853 | 693 | 521.4 | 459.2 | 454.3 | 362.2 | 448.7 | 351 | 313.5 | 412.5
854 | 694 | 521.3 | 459.2 | 453.9 | 358.3 | 450.2 | 351.3 | 313.7 | 412.5
855 | 695 | 521.3 | 459.2 | 453.9 | 354.9 | 451.7 | 351.6 | 314 | 412.5
856 | 696 | 521.3 | 459 | 453.9 | 351.8 | 453.2 | 352 | 314.2 | 412.5
857 | 697 | 521.3 | 458.5 | 454.2 | 348.2 | 454.4 | 352.3 | 314.5 | 412.6
858 | 698 | 521.3 | 458.1 | 454.5 | 345.8 | 455.5 | 352.6 | 314.7 | 412.6
859 | 699 | 521.2 | 458.1 | 455 | 343.2 | 456.7 | 352.9 | 314.9 | 412.7
860 | 700 | 521.1 | 458.2 | 455.5 | 341.7 | 457.9 | 353.2 | 315.1 | 412.7
861 | 701 | 521.2 | 458.7 | 456.1 | 340.5 | 459.2 | 353.5 | 315.3 | 412.7
862 | 702 | 521.3 | 459.4 | 456.7 | 341.1 | 460.4 | 353.8 | 315.6 | 412.8
863 | 703 | 521.3 | 460.2 | 457.4 | 341.4 | 461.7 | 354.1 | 315.8 | 412.9
864 | 704 | 521.4 | 461 | 457.9 | 341.3 | 462.8 | 354.3 | 316 | 413
865 | 705 | 521.4 | 461.7 | 458.7 | 340.5 | 463.7 | 354.6 | 316.3 | 413
866 | 706 | 521.4 | 462.3 | 459.4 | 339.6 | 464.7 | 354.8 | 316.5 | 413.1
867 | 707 | 521.5 | 462.8 | 460.1 | 339.3 | 465.8 | 355 | 316.7 | 413.2
868 | 708 | 521.5 | 463.2 | 460.7 | 339.1 | 466.8 | 355.3 | 317 | 413.2
869 | 709 | 521.4 | 463.4 | 461.3 | 339.8 | 467.9 | 355.5 | 317.2 | 413.4
870 | 710 | 521.2 | 463.5 | 461.9 | 342.4 | 468.8 | 355.8 | 317.4 | 413.5
871 | 711 | 521.2 | 463.6 | 462.4 | 342.3 | 469.8 | 356 | 317.6 | 413.6
872 | 712 | 521 | 463.7 | 462.9 | 341.8 | 470.8 | 356.3 | 317.8 | 413.6
873 | 713 | 521.1 | 463.7 | 463.2 | 343.5 | 471.7 | 356.5 | 318.1 | 413.7
874 | 714 | 521.2 | 463.9 | 463.6 | 343 | 472.6 | 356.8 | 318.3 | 413.8
875 | 715 | 521.1 | 464.1 | 463.9 | 343.9 | 473.1 | 357 | 318.5 | 413.8
876 | 716 | 521.3 | 464.3 | 464.3 | 346.5 | 473.7 | 357.3 | 318.8 | 413.9
877 | 717 | 521.2 | 464.4 | 464.7 | 345.2 | 474.3 | 357.5 | 319.1 | 414
878 | 718 | 521.2 | 464.2 | 465.1 | 343.9 | 474.8 | 357.7 | 319.3 | 414
879 | 719 | 521.2 | 464 | 465.5 | 342.7 | 475.4 | 358 | 319.6 | 414.1
880 | 720 | 521.3 | 463.7 | 466 | 341.7 | 475.9 | 358.2 | 319.9 | 414.1
881 | 721 | 521.3 | 463.3 | 466.5 | 344.7 | 476.3 | 358.5 | 320.2 | 414.1
882 | 722 | 521.2 | 462.7 | 467 | 347.4 | 476.5 | 358.8 | 320.5 | 414.2
883 | 723 | 521.3 | 461.6 | 467.5 | 348 | 476.7 | 359 | 320.8 | 414.2
884 | 724 | 521.5 | 460.1 | 468.1 | 347.2 | 476.7 | 359.3 | 321.1 | 414.3
885 | 725 | 521.7 | 458.4 | 468.6 | 346.4 | 476.9 | 359.5 | 321.4 | 414.4
886 | 726 | 521.8 | 457.2 | 469.1 | 345.6 | 477 | 359.7 | 321.7 | 414.5
887 | 727 | 521.8 | 456.6 | 469.5 | 345.3 | 477.1 | 360 | 322 | 414.5
888 | 728 | 521.9 | 456.3 | 470.1 | 345.5 | 477.3 | 360.2 | 322.3 | 414.6
889 | 729 | 521.8 | 456.4 | 470.9 | 345.6 | 477.6 | 360.5 | 322.6 | 414.7
890 | 730 | 521.9 | 456.5 | 471.6 | 342.9 | 477.8 | 360.7 | 322.9 | 414.7
891 | 731 | 521.9 | 456.5 | 472.3 | 344.8 | 478 | 361 | 323.2 | 414.8
892 | 732 | 522.1 | 456.4 | 473 | 348.4 | 478.1 | 361.3 | 323.5 | 414.8
893 | 733 | 522.2 | 456.3 | 473.6 | 354.8 | 478.4 | 361.5 | 323.8 | 414.9
894 | 734 | 522.4 | 456.2 | 474.3 | 360.3 | 478.8 | 361.8 | 324.1 | 414.9
895 | 735 | 522.6 | 456.4 | 474.8 | 361.9 | 479.2 | 362 | 324.5 | 415
896 | 736 | 522.5 | 456.6 | 475.4 | 362.3 | 479.5 | 362.3 | 324.8 | 415.1
897 | 737 | 522.5 | 456.6 | 476.1 | 368.6 | 479.7 | 362.5 | 325.2 | 415.3
898 | 738 | 522.5 | 456.7 | 477.1 | 375.1 | 479.7 | 362.6 | 325.5 | 415.4
899 | 739 | 522.5 | 456.9 | 478 | 376.5 | 479.8 | 362.8 | 325.8 | 415.5
900 | 740 | 522.6 | 457.2 | 478.8 | 375.1 | 480 | 362.9 | 326.1 | 415.6
901 | 741 | 522.5 | 457.4 | 479.6 | 378.5 | 480.2 | 363 | 326.5 | 415.8
902 | 742 | 522.7 | 457.5 | 480.2 | 384.7 | 480.5 | 363.1 | 326.8 | 415.9
903 | 743 | 522.8 | 457.7 | 480.7 | 392.6 | 480.8 | 363.2 | 327.1 | 416
904 | 744 | 522.8 | 458.1 | 481.4 | 399.1 | 481.1 | 363.2 | 327.5 | 416.1
905 | 745 | 522.7 | 458.6 | 482.2 | 400.9 | 481.4 | 363.3 | 327.9 | 416.3
906 | 746 | 522.5 | 459 | 483.1 | 401.3 | 481.7 | 363.4 | 328.3 | 416.4
907 | 747 | 522.3 | 459.5 | 484 | 401.5 | 482.1 | 363.5 | 328.7 | 416.5
908 | 748 | 522.2 | 460 | 484.9 | 398.8 | 482.4 | 363.6 | 329.1 | 416.7
909 | 749 | 522 | 460.5 | 485.9 | 399 | 482.8 | 363.8 | 329.6 | 416.8
910 | 750 | 521.8 | 461.1 | 486.7 | 402.9 | 483.4 | 363.9 | 330 | 416.9
911 | 751 | 521.7 | 461.3 | 487.5 | 407.6 | 484.1 | 364.1 | 330.5 | 417.1
912 | 752 | 521.6 | 461.5 | 488.4 | 410.1 | 484.8 | 364.3 | 331 | 417.2
913 | 753 | 521.5 | 461.8 | 489.3 | 409.1 | 485.3 | 364.5 | 331.5 | 417.4
914 | 754 | 521.4 | 462 | 490.4 | 407.4 | 486 | 364.7 | 332 | 417.5
915 | 755 | 521.2 | 462.3 | 491.9 | 409.2 | 486.7 | 364.9 | 332.5 | 417.7
916 | 756 | 521 | 462.6 | 493 | 408.9 | 487.6 | 365.1 | 332.9 | 417.8
917 | 757 | 521 | 462.9 | 494.1 | 409.2 | 488.5 | 365.3 | 333.4 | 417.9
918 | 758 | 521 | 463.3 | 495.1 | 409.8 | 489.5 | 365.5 | 333.8 | 418
919 | 759 | 521.1 | 463.9 | 496.5 | 409.5 | 490.5 | 365.7 | 334.2 | 418.2
920 | 760 | 521 | 464.7 | 497.9 | 408.1 | 491.3 | 366 | 334.7 | 418.3
921 | 761 | 521.1 | 465.6 | 499.7 | 407.6 | 492.2 | 366.2 | 335.1 | 418.5
922 | 762 | 520.9 | 466.2 | 501.5 | 405.4 | 493 | 366.4 | 335.5 | 418.6
923 | 763 | 520.9 | 466.7 | 503.5 | 404.4 | 493.9 | 366.7 | 336 | 418.7
924 | 764 | 521 | 467.2 | 505.1 | 406.3 | 494.7 | 366.9 | 336.4 | 418.9
925 | 765 | 521.2 | 467.6 | 506.4 | 407 | 495.5 | 367.1 | 336.8 | 419.1
926 | 766 | 521.4 | 468.1 | 508 | 407.7 | 496.4 | 367.3 | 337.3 | 419.2
927 | 767 | 521.5 | 468.6 | 510.2 | 407.1 | 497.5 | 367.5 | 337.7 | 419.4
928 | 768 | 521.6 | 469.1 | 511.6 | 409.5 | 498.8 | 367.7 | 338.2 | 419.5
929 | 769 | 521.6 | 469.6 | 512.4 | 413.1 | 500 | 367.9 | 338.7 | 419.7
930 | 770 | 521.7 | 470 | 513.7 | 416.2 | 501.3 | 368 | 339.1 | 419.9
931 | 771 | 521.7 | 470.6 | 515.7 | 418.9 | 502.5 | 368.2 | 339.6 | 420.1
932 | 772 | 521.7 | 471.2 | 517 | 421 | 503.9 | 368.4 | 340.1 | 420.3
933 | 773 | 521.8 | 471.8 | 518.3 | 423.1 | 505.5 | 368.5 | 340.5 | 420.4
934 | 774 | 521.7 | 472.5 | 520.6 | 424 | 507.4 | 368.7 | 341 | 420.6
935 | 775 | 521.7 | 473.2 | 523.5 | 424.3 | 509.5 | 368.9 | 341.5 | 420.8
936 | 776 | 521.6 | 473.8 | 526.2 | 424.7 | 512 | 369.1 | 342 | 420.9
937 | 777 | 521.5 | 474.4 | 529.1 | 426.7 | 514.5 | 369.3 | 342.5 | 421.1
938 | 778 | 521.6 | 475 | 531.9 | 428.9 | 516.7 | 369.5 | 343 | 421.3
939 | 779 | 521.6 | 475.6 | 534.6 | 429.3 | 519.1 | 369.7 | 343.4 | 421.4
940 | 780 | 521.7 | 476.2 | 537.4 | 429.5 | 521.7 | 369.9 | 343.9 | 421.6
941 | 781 | 521.9 | 476.8 | 539.1 | 429.7 | 524.7 | 370 | 344.3 | 421.7
942 | 782 | 521.9 | 477.4 | 539.9 | 430.5 | 527.8 | 370.1 | 344.8 | 421.9
943 | 783 | 521.6 | 477.9 | 540.9 | 430.9 | 531.2 | 370.2 | 345.2 | 422.1
944 | 784 | 521.4 | 478.4 | 542.2 | 431.6 | 534.8 | 370.2 | 345.6 | 422.2
945 | 785 | 521.5 | 478.7 | 543.7 | 433.6 | 537.9 | 370.2 | 345.9 | 422.4
946 | 786 | 521.5 | 479.2 | 545.8 | 434.2 | 541.1 | 370.2 | 346.3 | 422.6
947 | 787 | 521.3 | 479.7 | 548.1 | 434.5 | 544.2 | 370.2 | 346.6 | 422.7
948 | 788 | 521.2 | 480.1 | 549.9 | 435.8 | 547.3 | 370.2 | 346.9 | 422.9
949 | 789 | 521.1 | 480.5 | 551.6 | 436.4 | 550.1 | 370.3 | 347.3 | 423.1
950 | 790 | 521.2 | 481 | 554.5 | 434.2 | 553.2 | 370.3 | 347.6 | 423.2
951 | 791 | 521.1 | 481.6 | 558.5 | 431.9 | 556.5 | 370.5 | 347.9 | 423.3
952 | 792 | 521 | 482.2 | 560.6 | 429.8 | 558.8 | 370.6 | 348.2 | 423.4
953 | 793 | 521 | 482.7 | 562 | 429.1 | 561.1 | 370.8 | 348.4 | 423.6
954 | 794 | 521 | 483.4 | 563.9 | 427.9 | 563.7 | 370.9 | 348.7 | 423.8
955 | 795 | 520.8 | 484 | 566.8 | 425.2 | 566.8 | 371 | 348.9 | 423.9
956 | 796 | 520.7 | 484.7 | 570.5 | 420.8 | 570.6 | 371.2 | 349.1 | 424.1
957 | 797 | 520.9 | 485.5 | 574.3 | 416.5 | 575.5 | 371.5 | 349.4 | 424.2
958 | 798 | 521.3 | 486.2 | 576.5 | 413.1 | 579.7 | 371.7 | 350.1 | 424.3
959 | 799 | 521.4 | 486.9 | 578.4 | 411.5 | 582.5 | 372 | 350.9 | 424.4
960 | 800 | 521.5 | 487.7 | 579.6 | 410.4 | 584.6 | 372.2 | 351.6 | 424.5
961 | 801 | 521.6 | 488.3 | 579.4 | 410.3 | 586.2 | 372.4 | 352.4 | 424.7
962 | 802 | 521.5 | 489.1 | 579.2 | 411.7 | 587.8 | 372.6 | 353.2 | 424.8
963 | 803 | 521.7 | 489.8 | 580.9 | 411.5 | 589.4 | 372.8 | 354 | 425
964 | 804 | 521.8 | 490.5 | 582.7 | 410.5 | 591 | 373 | 354.8 | 425.1
965 | 805 | 521.8 | 491.2 | 584.4 | 407.8 | 592.9 | 373.1 | 355.5 | 425.2
966 | 806 | 521.7 | 491.9 | 585.9 | 407.3 | 594.2 | 373.3 | 356.3 | 425.4
967 | 807 | 521.6 | 492.7 | 588.2 | 407.7 | 595.3 | 373.5 | 357.1 | 425.5
968 | 808 | 521.5 | 493.4 | 590.1 | 408.3 | 596.7 | 373.6 | 357.8 | 425.7
969 | 809 | 521.7 | 494.1 | 590.6 | 407.7 | 598 | 373.8 | 358.5 | 425.9
970 | 810 | 521.9 | 494.8 | 591.3 | 407.8 | 599.2 | 373.9 | 359.1 | 426.1
971 | 811 | 522.1 | 495.4 | 592.4 | 406.7 | 599.3 | 373.9 | 359.7 | 426.2
972 | 812 | 522.2 | 496.1 | 593.4 | 406.8 | 599.4 | 374 | 360.5 | 426.4
973 | 813 | 522.4 | 496.7 | 594.8 | 407.6 | 600.5 | 374.1 | 361.2 | 426.6
974 | 814 | 522.3 | 497.3 | 596.2 | 407.2 | 602.3 | 374.3 | 361.8 | 426.7
975 | 815 | 522.3 | 498 | 597.7 | 406.9 | 604.1 | 374.4 | 362.4 | 426.9
976 | 816 | 522.4 | 498.6 | 598.9 | 406.3 | 605.5 | 374.6 | 362.9 | 427.1
977 | 817 | 522.5 | 499.3 | 600 | 407.4 | 606.2 | 374.8 | 363.5 | 427.3
978 | 818 | 522.4 | 500 | 603.8 | 407.7 | 607.2 | 375 | 364.1 | 427.5
979 | 819 | 522.3 | 500.6 | 606.9 | 407.1 | 608 | 375.2 | 364.6 | 427.6
980 | 820 | 522.5 | 501.4 | 609.3 | 405.3 | 609.1 | 375.5 | 364.9 | 427.8
981 | 821 | 522.5 | 502.1 | 611.9 | 404.5 | 610.2 | 375.7 | 365.4 | 428
982 | 822 | 522.6 | 502.9 | 614.7 | 403 | 611.7 | 376 | 365.8 | 428.1
983 | 823 | 522.7 | 503.6 | 617.5 | 401.7 | 612.4 | 376.2 | 366.2 | 428.3
984 | 824 | 522.8 | 504.4 | 619.2 | 401.4 | 613.1 | 376.5 | 366.5 | 428.4
985 | 825 | 522.5 | 505.2 | 620.8 | 400.7 | 614.2 | 376.7 | 366.8 | 428.6
986 | 826 | 522.1 | 506 | 622.9 | 398.5 | 616.1 | 377 | 367.1 | 428.7
987 | 827 | 522.1 | 506.8 | 624.4 | 396.5 | 618.3 | 377.2 | 367.4 | 428.9
988 | 828 | 522 | 507.6 | 625.7 | 394.7 | 620.2 | 377.4 | 367.6 | 429
989 | 829 | 522.1 | 508.4 | 628.3 | 392.9 | 621.6 | 377.7 | 367.9 | 429.2
990 | 830 | 522.1 | 509.1 | 629.9 | 391.7 | 622.9 | 377.9 | 368.2 | 429.3
991 | 831 | 522.1 | 510 | 630.7 | 390.4 | 624.1 | 378.2 | 368.4 | 429.4
992 | 832 | 522.1 | 510.8 | 631.8 | 388.7 | 624.6 | 378.4 | 368.6 | 429.6
993 | 833 | 522.1 | 511.6 | 634.3 | 387.1 | 625.4 | 378.6 | 368.9 | 429.8
994 | 834 | 522.1 | 512.4 | 636.3 | 386.6 | 626.7 | 378.9 | 369.1 | 429.9
995 | 835 | 522.1 | 513.2 | 638.9 | 385.2 | 627.6 | 379.1 | 369.2 | 430
996 | 836 | 522 | 514.1 | 639.7 | 383.3 | 629.2 | 379.4 | 369.2 | 430.3
997 | 837 | 522 | 514.8 | 640.5 | 381.6 | 630.8 | 379.6 | 369.4 | 430.5
998 | 838 | 522.1 | 515.6 | 640.3 | 379.9 | 632.2 | 379.9 | 369.5 | 430.6
999 | 839 | 522.1 | 516.5 | 641.3 | 380.6 | 633.9 | 380.2 | 369.6 | 430.8
1000 | 840 | 522.1 | 517.3 | 642.3 | 380.5 | 635.8 | 380.5 | 369.9 | 431
1001 | 841 | 522.4 | 518 | 642.2 | 379.9 | 637.7 | 380.7 | 370.1 | 431.1
1002 | 842 | 522.3 | 518.8 | 641.4 | 379.2 | 639.3 | 381 | 370.2 | 431.2
1003 | 843 | 522.3 | 519.6 | 640.7 | 379.1 | 640.4 | 381.2 | 370.3 | 431.4
1004 | 844 | 522.3 | 520.2 | 641.1 | 379.4 | 641.7 | 381.4 | 370.2 | 431.5
1005 | 845 | 522.2 | 521 | 641.4 | 379.1 | 643 | 381.6 | 370.1 | 431.7
1006 | 846 | 522 | 521.7 | 642.8 | 378.7 | 645.2 | 381.8 | 370.4 | 431.8
1007 | 847 | 521.9 | 522.5 | 645 | 378.8 | 646.7 | 381.9 | 370.4 | 432
1008 | 848 | 522 | 523.3 | 646.1 | 379.8 | 647.6 | 382.1 | 370.5 | 432.1
1009 | 849 | 521.9 | 524.1 | 647 | 379.3 | 649.1 | 382.3 | 370.5 | 432.2
1010 | 850 | 521.7 | 524.9 | 648.2 | 378.8 | 650.9 | 382.4 | 370.6 | 432.3
1011 | 851 | 521.7 | 525.7 | 649.4 | 379.6 | 652 | 382.6 | 370.8 | 432.5
1012 | 852 | 521.5 | 526.5 | 649.8 | 380 | 653.1 | 382.7 | 370.9 | 432.6
1013 | 853 | 521.3 | 527.2 | 650.5 | 380 | 653.5 | 382.9 | 371 | 432.8
1014 | 854 | 521.1 | 527.8 | 651.7 | 379.8 | 654.7 | 383 | 371.1 | 432.9
1015 | 855 | 520.9 | 528.5 | 652.7 | 380 | 655.1 | 383.2 | 371.3 | 433
1016 | 856 | 520.7 | 529.2 | 653.3 | 380.1 | 655.4 | 383.4 | 371.5 | 433.1
1017 | 857 | 520.6 | 529.9 | 655 | 380.5 | 655.9 | 383.6 | 371.8 | 433.3
1018 | 858 | 520.5 | 530.6 | 656.6 | 381 | 656.3 | 383.8 | 372 | 433.4
1019 | 859 | 520.7 | 531.4 | 657.7 | 381.9 | 656.3 | 384 | 372.2 | 433.6
1020 | 860 | 520.9 | 532.2 | 658 | 382.8 | 656.4 | 384.1 | 372.4 | 433.7
1021 | 861 | 521 | 532.9 | 658.4 | 384.5 | 656.6 | 384.2 | 372.7 | 433.9
1022 | 862 | 520.9 | 533.5 | 659.5 | 385.1 | 656.3 | 384.3 | 372.8 | 434
1023 | 863 | 520.8 | 534.3 | 660.9 | 385.9 | 655.9 | 384.4 | 372.9 | 434.1
1024 | 864 | 520.7 | 535 | 663.3 | 385.5 | 655.5 | 384.5 | 373.1 | 434.3
1025 | 865 | 520.7 | 535.9 | 666 | 384.7 | 655.3 | 384.6 | 373.3 | 434.3
1026 | 866 | 520.7 | 536.6 | 667.7 | 385.8 | 654.5 | 384.8 | 373.5 | 434.4
1027 | 867 | 520.7 | 537.4 | 668.9 | 386.5 | 653.5 | 384.9 | 373.9 | 434.5
1028 | 868 | 520.8 | 538 | 669.6 | 386.2 | 652.5 | 385.1 | 374.2 | 434.5
1029 | 869 | 520.8 | 538.7 | 670 | 385.9 | 651.6 | 385.3 | 374.6 | 434.6
1030 | 870 | 520.8 | 539.3 | 670.3 | 385.9 | 650.8 | 385.4 | 374.8 | 434.7
1031 | 871 | 521 | 540 | 670.6 | 385.8 | 649.7 | 385.6 | 375.1 | 434.8
1032 | 872 | 521.1 | 540.6 | 670.8 | 386.6 | 648.4 | 385.8 | 375.4 | 435
1033 | 873 | 521.1 | 541.1 | 670.9 | 387.4 | 646.9 | 385.9 | 375.7 | 435.1
1034 | 874 | 521 | 541.7 | 671.2 | 387.8 | 645.7 | 386 | 376 | 435.2
1035 | 875 | 520.8 | 542.4 | 671.6 | 387.7 | 644.9 | 386 | 376.3 | 435.4
1036 | 876 | 520.7 | 543.4 | 671.4 | 388.5 | 643.8 | 386.1 | 376.4 | 435.5
1037 | 877 | 520.7 | 544.3 | 670.8 | 390.4 | 642.3 | 386.1 | 376.7 | 435.6
1038 | 878 | 520.4 | 545.3 | 669.9 | 392.8 | 640.7 | 386 | 376.9 | 435.7
1039 | 879 | 520.3 | 546 | 669.1 | 395.6 | 639.2 | 386 | 377.1 | 435.8
1040 | 880 | 520.3 | 546.8 | 668.7 | 399.3 | 638.2 | 385.9 | 377.4 | 435.9
1041 | 881 | 520.4 | 547.6 | 668.4 | 401.8 | 637.1 | 385.9 | 377.6 | 436.1
1042 | 882 | 520.4 | 548.3 | 668.2 | 404.7 | 636.1 | 385.7 | 377.8 | 436.3
1043 | 883 | 520.3 | 548.8 | 668.4 | 406.2 | 635.2 | 385.6 | 377.9 | 436.4
1044 | 884 | 520.3 | 549.2 | 668.9 | 406.2 | 634.4 | 385.4 | 378.2 | 436.6
1045 | 885 | 520.4 | 549.7 | 669.6 | 406.3 | 633.7 | 385.3 | 378.3 | 436.7
1046 | 886 | 520.3 | 550.2 | 669.9 | 406.2 | 632.9 | 385.2 | 378.6 | 436.8
1047 | 887 | 520.3 | 550.7 | 669.9 | 406.4 | 632.1 | 385.2 | 378.8 | 437
1048 | 888 | 520.3 | 551.2 | 669.9 | 407 | 631.2 | 385.1 | 379 | 437.1
1049 | 889 | 519.9 | 551.6 | 669.4 | 406.8 | 630.4 | 385.2 | 379.2 | 437.2
1050 | 890 | 519.8 | 552.1 | 669.1 | 406.1 | 629.7 | 385.2 | 379.4 | 437.4
1051 | 891 | 519.8 | 552.5 | 668.7 | 405 | 629 | 385.3 | 379.6 | 437.5
1052 | 892 | 519.9 | 553 | 668.3 | 403.6 | 628.4 | 385.4 | 379.8 | 437.6
1053 | 893 | 519.8 | 553.6 | 667.7 | 402 | 627.5 | 385.5 | 380 | 437.8
1054 | 894 | 519.8 | 554.1 | 666.5 | 400.3 | 626.5 | 385.6 | 380.1 | 438
1055 | 895 | 519.8 | 554.6 | 665.5 | 399.1 | 625.8 | 385.7 | 380.2 | 438.1
1056 | 896 | 519.8 | 555.2 | 664 | 396.7 | 625 | 385.9 | 380.3 | 438.2
1057 | 897 | 519.7 | 555.8 | 662.6 | 394.8 | 624.7 | 386.1 | 380.4 | 438.3
1058 | 898 | 519.9 | 556.6 | 660.9 | 393.8 | 624.1 | 386.4 | 380.5 | 438.5
1059 | 899 | 519.8 | 557.3 | 659.2 | 392.1 | 623.2 | 386.6 | 380.7 | 438.6
1060 | 900 | 519.7 | 558.1 | 657.8 | 390 | 622.1 | 386.9 | 380.7 | 438.8
1061 | 901 | 519.6 | 558.9 | 656.4 | 387.5 | 621 | 387.2 | 380.7 | 438.9
1062 | 902 | 519.6 | 559.7 | 655 | 386.4 | 620.3 | 387.5 | 380.9 | 438.9
1063 | 903 | 519.5 | 560.6 | 653.7 | 385.6 | 619.6 | 387.8 | 381 | 439.1
1064 | 904 | 519.6 | 561.5 | 652.6 | 385.2 | 618.8 | 388.1 | 381 | 439.2
1065 | 905 | 519.8 | 562.5 | 651.4 | 384.5 | 617.6 | 388.3 | 381.2 | 439.4
1066 | 906 | 520.1 | 563.5 | 650 | 383.2 | 616.3 | 388.6 | 381.2 | 439.6
1067 | 907 | 520.5 | 564.5 | 648.3 | 381.1 | 615.2 | 388.8 | 381.4 | 439.7
1068 | 908 | 520.6 | 565.6 | 646.7 | 379.4 | 614.2 | 389 | 381.6 | 439.9
1069 | 909 | 520.8 | 566.7 | 645.3 | 377.8 | 613 | 389.2 | 381.7 | 440
1070 | 910 | 521.1 | 567.9 | 643.9 | 376.4 | 611.9 | 389.4 | 381.9 | 440.2
1071 | 911 | 521.3 | 569.1 | 642.6 | 374.9 | 611 | 389.7 | 382.1 | 440.4
1072 | 912 | 521.4 | 570.2 | 641.4 | 373.4 | 610.3 | 390 | 382.4 | 440.6
1073 | 913 | 521.6 | 571.4 | 640 | 372.4 | 609.4 | 390.3 | 382.6 | 440.8
1074 | 914 | 521.7 | 572.6 | 638.7 | 372.9 | 608.8 | 390.6 | 382.8 | 441
1075 | 915 | 521.7 | 573.8 | 637.6 | 373.1 | 608.5 | 391 | 383.1 | 441.1
1076 | 916 | 521.8 | 574.9 | 636.1 | 373.2 | 608.1 | 391.3 | 383.3 | 441.3
1077 | 917 | 521.7 | 576 | 634.6 | 373.2 | 607.7 | 391.6 | 383.5 | 441.4
1078 | 918 | 521.7 | 577.1 | 633.3 | 372.8 | 607.3 | 391.8 | 383.8 | 441.6
1079 | 919 | 521.6 | 578.2 | 631.9 | 372.4 | 607.3 | 392.1 | 384 | 441.7
1080 | 920 | 521.5 | 579.2 | 631 | 372.6 | 606.7 | 392.3 | 384.3 | 441.9
1081 | 921 | 521.4 | 580.2 | 630.1 | 373 | 606.3 | 392.5 | 384.5 | 442.1
1082 | 922 | 521.5 | 581.2 | 629.2 | 372.2 | 605.6 | 392.7 | 384.8 | 442.3
1083 | 923 | 521.5 | 582.2 | 628.3 | 371.1 | 605 | 392.9 | 385 | 442.6
1084 | 924 | 521.4 | 583.2 | 627.6 | 372 | 605 | 393.1 | 385.4 | 442.8
1085 | 925 | 521.3 | 584.2 | 626.9 | 374.3 | 605.5 | 393.2 | 385.7 | 443.1
1086 | 926 | 521.3 | 585.3 | 626.5 | 377.6 | 605.8 | 393.4 | 386.1 | 443.4
1087 | 927 | 521.3 | 586.3 | 626.2 | 382.5 | 606.3 | 393.6 | 386.4 | 443.7
1088 | 928 | 521.2 | 587.5 | 626.1 | 391 | 606.9 | 393.7 | 386.8 | 444.1
1089 | 929 | 521.3 | 588.8 | 626.4 | 402.6 | 607.5 | 394 | 387.2 | 444.5
1090 | 930 | 521.5 | 590.4 | 627.1 | 439.6 | 608.2 | 394.2 | 387.6 | 445
1091 | 931 | 521.7 | 592.1 | 628.1 | 514 | 609.1 | 394.4 | 388.1 | 445.6
1092 | 932 | 521.9 | 594 | 629.6 | 595.4 | 610 | 394.6 | 388.7 | 446.2
1093 | 933 | 522 | 596.5 | 630.2 | 656.3 | 611.8 | 395 | 389.5 | 446.8
1094 | 934 | 521.7 | 598.8 | 630.7 | 664.9 | 613.4 | 395.3 | 391.5 | 447.4
1095 | 935 | 521.9 | 600.6 | 632.7 | 672.2 | 614.3 | 395.5 | 393.5 | 448.1
1096 | 936 | 522 | 603 | 633.6 | 682.4 | 615.4 | 395.8 | 395.3 | 448.7
1097 | 937 | 522.3 | 605.5 | 634 | 694.7 | 616 | 396.1 | 397.2 | 449.4
1098 | 938 | 522.4 | 608 | 634.2 | 703.5 | 616 | 396.6 | 399.2 | 450.1
1099 | 939 | 522.3 | 610.5 | 635.1 | 703.4 | 616.6 | 397 | 401.3 | 450.8
1100 | 940 | 522.3 | 612.9 | 636.2 | 699.2 | 617.5 | 397.5 | 403.7 | 451.6
1101 | 941 | 522.2 | 615.4 | 637.7 | 687.8 | 618.5 | 398 | 406.1 | 452.4
1102 | 942 | 522.3 | 617.5 | 639.2 | 662.6 | 619.3 | 398.5 | 408.8 | 453.2
1103 | 943 | 522.4 | 619.3 | 640.7 | 636.9 | 620.2 | 399 | 411.6 | 454
1104 | 944 | 522.4 | 621 | 642.1 | 611.5 | 621.1 | 399.5 | 414.4 | 454.8
1105 | 945 | 522.4 | 623.1 | 643.4 | 590.9 | 621.8 | 400.2 | 417.2 | 455.7
1106 | 946 | 522.4 | 625.8 | 645.2 | 577.8 | 623.2 | 401 | 420.1 | 456.6
1107 | 947 | 522.3 | 629.5 | 646.7 | 561.4 | 624.4 | 402.2 | 423.4 | 457.5
1108 | 948 | 522.2 | 633.4 | 648.1 | 548.5 | 625.1 | 404.2 | 426.7 | 458.4
1109 | 949 | 522 | 637.6 | 649.4 | 537.3 | 625.4 | 406.9 | 430.2 | 459.2
1110 | 950 | 521.8 | 641.6 | 650.4 | 526.3 | 625.8 | 410.3 | 433.8 | 460.1
1111 | 951 | 521.9 | 645.6 | 651.7 | 518.8 | 626.6 | 414.1 | 437.4 | 461
1112 | 952 | 521.8 | 649.7 | 652.9 | 518.5 | 627.8 | 418.4 | 441.1 | 461.9
1113 | 953 | 521.8 | 653.7 | 653.7 | 526.9 | 629.6 | 423.1 | 444.2 | 462.8
1114 | 954 | 521.8 | 657.3 | 654.2 | 535.1 | 632 | 427.9 | 447.9 | 463.7
1115 | 955 | 521.7 | 661.1 | 654.5 | 542.4 | 635.2 | 432.7 | 451.5 | 464.7
1116 | 956 | 521.3 | 665.7 | 654.5 | 543.7 | 641.7 | 437.7 | 455.1 | 465.6
1117 | 957 | 521.1 | 670.1 | 654.5 | 542.8 | 649 | 442.6 | 458.7 | 466.5
1118 | 958 | 521 | 674.3 | 654.3 | 550 | 656.5 | 447.3 | 462.2 | 467.5
1119 | 959 | 520.8 | 679.8 | 654.2 | 557.8 | 662.7 | 451.2 | 466 | 468.5
1120 | 960 | 520.7 | 687 | 654 | 550.9 | 664.6 | 454.7 | 469.7 | 469.4
1121 | 961 | 520.5 | 693.8 | 653.9 | 544.6 | 665 | 457.9 | 473.1 | 470.4
1122 | 962 | 520.3 | 699.3 | 653.9 | 545.4 | 664.5 | 460.8 | 475.6 | 471.3
1123 | 963 | 520 | 704.4 | 653.9 | 544.5 | 663.6 | 463.5 | 477.7 | 472.3
1124 | 964 | 519.9 | 708.3 | 653.9 | 548 | 662.1 | 466 | 479.4 | 473.3
1125 | 965 | 519.8 | 711.5 | 653.9 | 561 | 660.4 | 468.3 | 480.7 | 474.2
1126 | 966 | 519.8 | 714.6 | 654.7 | 561.7 | 657.8 | 470.6 | 481.9 | 475
1127 | 967 | 519.8 | 717.9 | 655 | 552.2 | 655.4 | 472.8 | 482.9 | 475.9
1128 | 968 | 519.7 | 721.2 | 655.1 | 539.6 | 652.7 | 475 | 483.9 | 476.8
1129 | 969 | 519.2 | 723.5 | 655.3 | 526.7 | 650.1 | 477 | 484.8 | 477.6
1130 | 970 | 518.7 | 726.1 | 655.8 | 521.4 | 648.7 | 478.8 | 485.7 | 478.4
1131 | 971 | 517.9 | 728.9 | 656.1 | 525.4 | 647.9 | 480.3 | 486.7 | 479.1
1132 | 972 | 517.2 | 733.5 | 656.4 | 526.6 | 647 | 481.5 | 487.7 | 479.9
1133 | 973 | 516.5 | 736.6 | 657.2 | 537.9 | 647 | 482.7 | 488.9 | 480.6
1134 | 974 | 515.7 | 737.3 | 657.8 | 549.4 | 648.4 | 483.7 | 490.2 | 481.4
1135 | 975 | 514.9 | 736 | 658.1 | 564.9 | 649 | 484.4 | 491.4 | 482.1
1136 | 976 | 513.9 | 736.5 | 658.3 | 595.1 | 649.3 | 485.4 | 492.7 | 482.9
1137 | 977 | 513.1 | 738.9 | 658.4 | 611.6 | 648 | 486.6 | 494 | 483.8
1138 | 978 | 512.4 | 740.3 | 658.9 | 619.6 | 646 | 488 | 495.3 | 484.5
1139 | 979 | 511.6 | 742.9 | 659.2 | 626.9 | 644.5 | 489.2 | 496.6 | 485.3
1140 | 980 | 510.7 | 744.5 | 659.4 | 615.9 | 643 | 490.3 | 498 | 486.1
1141 | 981 | 509.8 | 745 | 659.6 | 625.2 | 642.2 | 491.3 | 499.2 | 486.8
1142 | 982 | 508.9 | 745.2 | 659.7 | 626.6 | 641.1 | 492.3 | 500.1 | 487.5
1143 | 983 | 507.8 | 744 | 660.2 | 621.1 | 640.6 | 493.2 | 501 | 488.2
1144 | 984 | 506.7 | 743.6 | 660.3 | 622 | 640.4 | 494.1 | 501.9 | 488.9
1145 | 985 | 505.5 | 743.9 | 660 | 612.4 | 639.8 | 495 | 502.8 | 489.5
1146 | 986 | 504.1 | 742.8 | 659.7 | 601.3 | 639 | 495.7 | 503.3 | 490.1
1147 | 987 | 503 | 741.7 | 659.6 | 592.6 | 638.5 | 496.5 | 503.9 | 490.7
1148 | 988 | 501.9 | 741 | 659.1 | 577.7 | 638.4 | 497.1 | 504.4 | 491.3
1149 | 989 | 500.8 | 740.8 | 658.6 | 572.8 | 637.8 | 497.8 | 505.1 | 491.9
1150 | 990 | 499.9 | 739.8 | 658.2 | 572.2 | 637 | 498.5 | 505.7 | 492.5
1151 | 991 | 498.9 | 738.4 | 658 | 572.9 | 636.6 | 499.3 | 506.3 | 493
1152 | 992 | 497.6 | 736.3 | 657.9 | 568.9 | 636.3 | 500 | 507.1 | 493.5
1153 | 993 | 496.4 | 734.6 | 657.7 | 566.7 | 635.7 | 500.5 | 508 | 494
1154 | 994 | 495.2 | 732.6 | 657.3 | 562.2 | 634.9 | 501.2 | 508.7 | 494.5
1155 | 995 | 494.1 | 731.4 | 656.6 | 549.9 | 634.3 | 502 | 509.2 | 495
1156 | 996 | 493 | 730.4 | 656 | 538.1 | 633.5 | 502.9 | 509.7 | 495.5
1157 | 997 | 491.9 | 729.6 | 655.3 | 534.6 | 631.9 | 503.7 | 510.1 | 496
1158 | 998 | 490.8 | 728.8 | 654.8 | 530.7 | 630.3 | 504.8 | 510.6 | 496.4
1159 | 999 | 489.6 | 727.7 | 654.5 | 524.4 | 629.5 | 506 | 511.2 | 496.9
1160 | 1000 | 488.4 | 726.3 | 654.7 | 525.1 | 628.6 | 507.2 | 511.8 | 497.4
1161 | 1001 | 487.3 | 724.6 | 654.8 | 529 | 627.6 | 508.6 | 512.5 | 497.9
1162 | 1002 | 486.4 | 722.8 | 654.4 | 521.9 | 626.5 | 510.2 | 513.2 | 498.3
1163 | 1003 | 485.4 | 720.9 | 653.9 | 513.3 | 625.8 | 511.9 | 513.9 | 498.7
1164 | 1004 | 484.3 | 719 | 653.6 | 507.8 | 625.5 | 513.7 | 514.7 | 499.1
1165 | 1005 | 483.4 | 717.3 | 653.2 | 504.7 | 624.7 | 515.5 | 515.6 | 499.5
1166 | 1006 | 482.4 | 715.6 | 652.6 | 500.6 | 624.1 | 517.5 | 516.6 | 499.9
1167 | 1007 | 481.3 | 713.7 | 652 | 495.9 | 622.6 | 519.5 | 517.6 | 500.1
1168 | 1008 | 480.1 | 712.1 | 651.4 | 494.4 | 621.1 | 522.1 | 518.7 | 500.5
1169 | 1009 | 479 | 710.5 | 650.7 | 490.3 | 619.2 | 525 | 519.8 | 500.8
1170 | 1010 | 477.8 | 708.9 | 649.8 | 482.4 | 616.3 | 528.3 | 521.1 | 501.1
1171 | 1011 | 476.8 | 707.1 | 649.1 | 478.9 | 614.3 | 532.3 | 522.5 | 501.4
1172 | 1012 | 475.7 | 705.2 | 648.6 | 475.3 | 612.3 | 537.1 | 524 | 501.7
1173 | 1013 | 474.6 | 703.8 | 648.1 | 473.5 | 610 | 542.3 | 525.8 | 502
1174 | 1014 | 473.4 | 702.9 | 647.8 | 469.3 | 608.4 | 548.1 | 527.8 | 502.3
1175 | 1015 | 472.3 | 702 | 647.4 | 465.6 | 607 | 554.5 | 529.9 | 502.5
1176 | 1016 | 471.3 | 701.1 | 646.9 | 461.7 | 604.5 | 561.2 | 532.4 | 502.7
1177 | 1017 | 470.4 | 700.3 | 646.4 | 462.5 | 601.2 | 568.2 | 535.7 | 502.8
1178 | 1018 | 469.4 | 699.3 | 645.6 | 462.8 | 599 | 575.6 | 539.4 | 503
1179 | 1019 | 468.6 | 698.3 | 645.1 | 462.1 | 597.2 | 582.8 | 543.2 | 503.2
1180 | 1020 | 467.7 | 697.2 | 644.5 | 463.8 | 595.1 | 589.5 | 547.1 | 503.4
1181 | 1021 | 466.7 | 695.9 | 643.6 | 463.7 | 593.1 | 596.1 | 551.3 | 503.5
1182 | 1022 | 465.7 | 694.2 | 642.3 | 462.8 | 590.9 | 602.8 | 555.6 | 503.6
1183 | 1023 | 464.6 | 693 | 641.2 | 460.7 | 588.4 | 609.1 | 559.8 | 503.6
1184 | 1024 | 463.8 | 691.8 | 640.2 | 463.8 | 586.3 | 614.6 | 564.3 | 503.7
1185 | 1025 | 462.8 | 690.5 | 639.3 | 466.6 | 585.1 | 620.1 | 568.6 | 503.9
1186 | 1026 | 461.9 | 689.2 | 637.2 | 464.9 | 583.8 | 625.3 | 573 | 504
1187 | 1027 | 460.9 | 687.7 | 633.4 | 463 | 581.7 | 630.4 | 577.2 | 504.2
1188 | 1028 | 459.7 | 686.3 | 630.3 | 462.2 | 581.5 | 635.6 | 581.5 | 504.3
1189 | 1029 | 458.6 | 685 | 627.2 | 461 | 580.4 | 641 | 586 | 504.4
1190 | 1030 | 457.7 | 683.3 | 624.5 | 461.9 | 578.6 | 646.1 | 590.2 | 504.6
1191 | 1031 | 456.9 | 681.9 | 622.1 | 462.2 | 576.4 | 651.5 | 594.2 | 504.7
1192 | 1032 | 456 | 680.3 | 620.2 | 461.6 | 575.6 | 656.5 | 598.1 | 504.8
1193 | 1033 | 455 | 678.3 | 618.3 | 460 | 574.3 | 660.8 | 601.6 | 504.9
1194 | 1034 | 453.9 | 676.4 | 616.8 | 455 | 574.2 | 664.5 | 604.8 | 505.1
1195 | 1035 | 453 | 674.4 | 615.9 | 450.8 | 574.1 | 668.6 | 607.7 | 505.2
1196 | 1036 | 452.1 | 672.6 | 615.6 | 448.3 | 575.6 | 671.6 | 610.7 | 505.4
1197 | 1037 | 451.2 | 670.7 | 614.9 | 449.1 | 576 | 673.9 | 613.8 | 505.6
1198 | 1038 | 450 | 669 | 614.4 | 450 | 576.8 | 676.6 | 616.7 | 505.8
1199 | 1039 | 449.1 | 667.7 | 614 | 448.8 | 577.7 | 679.1 | 619.4 | 505.9
1200 | 1040 | 448.2 | 666.3 | 613.6 | 448.3 | 578 | 680.5 | 622.1 | 506.1
1201 | 1041 | 447.2 | 664.8 | 612 | 444.1 | 576.8 | 681.8 | 624.4 | 506.2
1202 | 1042 | 446.4 | 663.2 | 610.1 | 440.3 | 576 | 683.3 | 626.6 | 506.3
1203 | 1043 | 445.4 | 661.3 | 607.8 | 436.7 | 573.9 | 685 | 628.4 | 506.5
1204 | 1044 | 444.5 | 659 | 605.2 | 433.4 | 569.9 | 686.4 | 629.6 | 506.6
1205 | 1045 | 443.6 | 656.8 | 603.7 | 431.8 | 568.8 | 686.5 | 630.2 | 506.7
1206 | 1046 | 442.8 | 654.7 | 601.3 | 434 | 568 | 685.7 | 631.4 | 506.9
1207 | 1047 | 442.1 | 652.6 | 598.7 | 435.8 | 566.8 | 684.3 | 632.9 | 507.1
1208 | 1048 | 441.3 | 650.6 | 596.8 | 435 | 563.8 | 682.2 | 634.2 | 507.2
1209 | 1049 | 440.2 | 648.5 | 595.3 | 434.7 | 560.2 | 680.2 | 635.5 | 507.4
1210 | 1050 | 439.3 | 646.2 | 593.2 | 437.4 | 557 | 678.3 | 636.8 | 507.6
1211 | 1051 | 438.5 | 644.1 | 591.6 | 439.5 | 556.6 | 676.2 | 637.9 | 507.7
1212 | 1052 | 437.7 | 642 | 590.8 | 437.9 | 557.8 | 674.2 | 638.7 | 507.9
1213 | 1053 | 436.7 | 640.1 | 590.8 | 437.3 | 558.6 | 671.9 | 639.7 | 508.1
1214 | 1054 | 435.9 | 638 | 589.7 | 436.9 | 556.9 | 669.7 | 640.7 | 508.2
1215 | 1055 | 435.1 | 635.6 | 588.9 | 434.5 | 556.3 | 667.4 | 641.8 | 508.4
1216 | 1056 | 434.3 | 633.5 | 588.3 | 433.3 | 556.7 | 664.8 | 643.1 | 508.6
1217 | 1057 | 433.5 | 631.2 | 587.3 | 433.8 | 556.9 | 662 | 644.3 | 508.8
1218 | 1058 | 432.6 | 629 | 586.4 | 435.8 | 557.2 | 659.4 | 645.6 | 508.9
1219 | 1059 | 431.7 | 627.2 | 586.2 | 441 | 556.3 | 657.1 | 646.4 | 509.1
1220 | 1060 | 430.7 | 625.4 | 585.3 | 444.2 | 553.3 | 654.8 | 647.4 | 509.3
1221 | 1061 | 429.9 | 623.2 | 583.7 | 445.1 | 549.8 | 652.5 | 648.5 | 509.4
1222 | 1062 | 429 | 620.3 | 581.3 | 443.8 | 548.3 | 650.2 | 649.7 | 509.5
1223 | 1063 | 428.2 | 618.2 | 580.3 | 443.1 | 547.8 | 648.2 | 651.1 | 509.7
1224 | 1064 | 427.5 | 616 | 579.8 | 443.3 | 548.7 | 646.2 | 653 | 509.9
1225 | 1065 | 426.6 | 611 | 579 | 444.7 | 548.4 | 644.2 | 655 | 510.1
1226 | 1066 | 425.7 | 606.2 | 577.8 | 442.6 | 547.5 | 642.4 | 656.7 | 510.3
1227 | 1067 | 424.8 | 602.7 | 577.4 | 441 | 548.2 | 640.5 | 658.5 | 510.5
1228 | 1068 | 424 | 598.4 | 576.1 | 439.2 | 547.8 | 638.8 | 660 | 510.7
1229 | 1069 | 423.2 | 594.9 | 574.9 | 434.7 | 546.1 | 636.9 | 661.6 | 510.9
1230 | 1070 | 422.4 | 590.3 | 573.1 | 429.8 | 544.7 | 635 | 663.2 | 511
1231 | 1071 | 421.5 | 586.2 | 571.6 | 425.3 | 544.1 | 633.3 | 664.6 | 511.2
1232 | 1072 | 420.9 | 585.9 | 571.4 | 424 | 544.7 | 631.4 | 665.7 | 511.4
1233 | 1073 | 420.1 | 582.9 | 570.3 | 424 | 544.8 | 629.6 | 667 | 511.6
1234 | 1074 | 419.5 | 579.2 | 569.2 | 425.9 | 546.5 | 627.9 | 667.8 | 511.8
1235 | 1075 | 418.7 | 577 | 568.4 | 428.6 | 549.3 | 626.2 | 668.8 | 512
1236 | 1076 | 417.8 | 575.8 | 567.1 | 431.3 | 552 | 624.5 | 669.8 | 512.3
1237 | 1077 | 416.9 | 575.6 | 566.1 | 435.9 | 554.6 | 622.8 | 670.6 | 512.4
1238 | 1078 | 416 | 573.6 | 564.5 | 440.1 | 556.3 | 621.3 | 671.3 | 512.6
1239 | 1079 | 415.1 | 571.3 | 562.6 | 441.9 | 555.5 | 619.7 | 672 | 512.8
1240 | 1080 | 414.4 | 567.6 | 559.8 | 438.8 | 553.1 | 618 | 672.6 | 513
1241 | 1081 | 413.7 | 565.4 | 556.6 | 435.7 | 548.6 | 616 | 672.6 | 513.2
1242 | 1082 | 412.8 | 562.9 | 554.1 | 431.9 | 545.8 | 614 | 672.3 | 513.4
1243 | 1083 | 412 | 561.6 | 552.6 | 429.8 | 546 | 612 | 672.1 | 513.6
1244 | 1084 | 411.3 | 562.2 | 551.4 | 430.4 | 547 | 609.8 | 671.9 | 513.8
1245 | 1085 | 410.7 | 562.2 | 549.9 | 428.6 | 545.9 | 607.6 | 671.6 | 514
1246 | 1086 | 410.1 | 561.2 | 548.1 | 427.8 | 542.3 | 605.4 | 671.1 | 514.2
1247 | 1087 | 409.5 | 559.9 | 546.2 | 425.3 | 542 | 603.3 | 670.3 | 514.3
1248 | 1088 | 408.7 | 558.9 | 544.5 | 423.1 | 541.8 | 601.3 | 669.4 | 514.5
1249 | 1089 | 407.9 | 556.9 | 542.7 | 421.4 | 541.2 | 599.3 | 668.3 | 514.6
1250 | 1090 | 407.2 | 553.7 | 540.7 | 420.5 | 541 | 597.3 | 667 | 514.7
1251 | 1091 | 406.6 | 552 | 538.4 | 419.2 | 541.2 | 595.1 | 665.6 | 514.8
1252 | 1092 | 405.8 | 549.8 | 536.1 | 417.4 | 539.4 | 593 | 663.8 | 515
1253 | 1093 | 405.2 | 547.6 | 534.6 | 417.5 | 539.2 | 590.8 | 662 | 515.1
1254 | 1094 | 404.6 | 546.6 | 533.6 | 417.7 | 541 | 588.7 | 660.5 | 515.2
1255 | 1095 | 404 | 545.3 | 532.1 | 416.8 | 539.9 | 586.3 | 659 | 515.3
1256 | 1096 | 403.4 | 545.5 | 531.1 | 416.4 | 540.5 | 584 | 657.5 | 515.4
1257 | 1097 | 402.6 | 543.1 | 529.3 | 415.6 | 541.9 | 581.6 | 656.2 | 515.6
1258 | 1098 | 402.1 | 541.6 | 528.3 | 417 | 541.6 | 579.3 | 654.9 | 515.7
1259 | 1099 | 401.6 | 540.5 | 527.6 | 417.5 | 541.1 | 577 | 653.6 | 515.7
1260 | 1100 | 400.7 | 541.4 | 526.9 | 419.9 | 542 | 574.7 | 652.4 | 515.8
1261 | 1101 | 400 | 541.2 | 526.1 | 421 | 542.4 | 572.4 | 651.1 | 515.8
1262 | 1102 | 399.2 | 538.9 | 524.3 | 420.1 | 541.6 | 570.1 | 650 | 515.8
1263 | 1103 | 398.4 | 535.5 | 522.1 | 418.2 | 539.8 | 567.6 | 648.7 | 515.8
1264 | 1104 | 397.7 | 533.7 | 519.9 | 416.1 | 536.1 | 565.1 | 647.2 | 515.9
1265 | 1105 | 396.9 | 532 | 518 | 414.9 | 532.7 | 562.5 | 645.6 | 515.9
1266 | 1106 | 396.2 | 530.1 | 515.4 | 412 | 529.3 | 559.9 | 643.9 | 515.9
1267 | 1107 | 395.6 | 528.8 | 513.7 | 410.7 | 527.3 | 557.2 | 642.1 | 515.8
1268 | 1108 | 395 | 526.8 | 511.9 | 410.8 | 524.8 | 554.4 | 640.3 | 515.8
1269 | 1109 | 394.4 | 525.1 | 510.3 | 409.1 | 523.2 | 551.8 | 638.5 | 515.8
1270 | 1110 | 393.7 | 523.9 | 508.9 | 409 | 519.6 | 549.2 | 636.6 | 515.7
1271 | 1111 | 392.9 | 522 | 507.8 | 407.9 | 521 | 546.5 | 634.7 | 515.6
1272 | 1112 | 392.1 | 520.4 | 506.9 | 405.4 | 522.1 | 543.6 | 632.8 | 515.5
1273 | 1113 | 391.6 | 519.3 | 506.6 | 402.8 | 523 | 540.5 | 630.9 | 515.5
1274 | 1114 | 391.2 | 519 | 506.6 | 405.4 | 524 | 537.5 | 628.4 | 515.3
1275 | 1115 | 390.5 | 518.7 | 506 | 408.1 | 523 | 534.1 | 625.4 | 515.2
1276 | 1116 | 389.9 | 516.6 | 504.3 | 409.2 | 521.2 | 530.7 | 622.6 | 514.9
1277 | 1117 | 389.2 | 514.1 | 502.2 | 409.6 | 517.7 | 527.3 | 619.7 | 514.8
1278 | 1118 | 388.4 | 512.9 | 500.4 | 410.8 | 516.3 | 523.9 | 616.9 | 514.6
1279 | 1119 | 387.7 | 511.3 | 499.1 | 412 | 515.2 | 520.3 | 613.9 | 514.5
1280 | 1120 | 387.1 | 510.5 | 497.6 | 411.8 | 510.9 | 516.5 | 610.9 | 514.3
1281 | 1121 | 386.4 | 508.3 | 495.8 | 411.9 | 505.8 | 512.9 | 608 | 514
1282 | 1122 | 385.8 | 505.8 | 493.9 | 411.4 | 498.8 | 509.3 | 603.5 | 513.8
1283 | 1123 | 385.2 | 504.2 | 492.9 | 410.3 | 495 | 505.5 | 596.7 | 513.6
1284 | 1124 | 384.5 | 501.9 | 491.6 | 409.3 | 494.2 | 501.3 | 591.2 | 513.4
1285 | 1125 | 383.7 | 500.1 | 490.8 | 411.8 | 494.7 | 497.2 | 586.4 | 513.2
1286 | 1126 | 383.1 | 499.3 | 490.1 | 413.4 | 495.1 | 493.3 | 581.7 | 513
1287 | 1127 | 382.4 | 498.9 | 488.9 | 412.4 | 493.6 | 489.6 | 577.4 | 512.7
1288 | 1128 | 382 | 497.5 | 487.5 | 413.1 | 491.9 | 486.2 | 573.3 | 512.5
1289 | 1129 | 381.4 | 496.9 | 486 | 414.7 | 486.6 | 482.6 | 569.5 | 512.3
1290 | 1130 | 380.9 | 496.8 | 484.3 | 419 | 479.3 | 479.1 | 565.5 | 512
1291 | 1131 | 380.2 | 497 | 483 | 423.8 | 474.5 | 475.6 | 561 | 511.6
1292 | 1132 | 379.7 | 495.7 | 481 | 425 | 470.3 | 472.2 | 556.3 | 511.3
1293 | 1133 | 379.3 | 493.4 | 478.4 | 423 | 467.2 | 468.9 | 553.9 | 511
1294 | 1134 | 378.7 | 493.3 | 477.5 | 422.2 | 463.8 | 465.9 | 550.4 | 510.6
1295 | 1135 | 377.9 | 492.3 | 476.2 | 420.6 | 459.8 | 463.1 | 548.1 | 510.5
1296 | 1136 | 377.2 | 490.8 | 474.2 | 419.4 | 453.2 | 460.6 | 547.1 | 510.2
1297 | 1137 | 376.6 | 489.7 | 472.7 | 417.7 | 447.8 | 458.3 | 544.1 | 510
1298 | 1138 | 375.8 | 488.2 | 470.8 | 416.6 | 443.7 | 456 | 541.1 | 509.8
1299 | 1139 | 375.2 | 487.1 | 469.2 | 415 | 441.6 | 453.5 | 538.6 | 509.5
1300 | 1140 | 374.6 | 486.4 | 467.9 | 416.3 | 439.4 | 450.9 | 535.9 | 509.2
1301 | 1141 | 373.8 | 486.2 | 466.8 | 415.5 | 436.9 | 448.4 | 533.4 | 509
1302 | 1142 | 373.2 | 486 | 465.5 | 414.9 | 431.9 | 446 | 531.2 | 508.7
1303 | 1143 | 372.7 | 485.3 | 464.1 | 412.1 | 426.7 | 443.7 | 528.8 | 508.4
1304 | 1144 | 371.8 | 483.3 | 462.2 | 412.3 | 423.2 | 441.5 | 526.1 | 508.1
1305 | 1145 | 371.1 | 480.2 | 460 | 414.7 | 421.7 | 439.4 | 523.5 | 507.8
1306 | 1146 | 370.3 | 476.9 | 458.2 | 413.9 | 422.2 | 437.5 | 520.8 | 507.5
1307 | 1147 | 369.6 | 474.3 | 456.2 | 412.6 | 418.9 | 435.5 | 518.4 | 507.2
1308 | 1148 | 369.1 | 473.3 | 454.8 | 411.3 | 416.3 | 433.4 | 516.3 | 506.8
1309 | 1149 | 368.4 | 472.3 | 454 | 410 | 413.4 | 431.3 | 514.2 | 506.4
1310 | 1150 | 367.8 | 471.4 | 452.4 | 408.8 | 409.1 | 429.2 | 512 | 506
1311 | 1151 | 367.1 | 470.1 | 450.9 | 407.7 | 405.1 | 426.9 | 509.8 | 505.5
1312 | 1152 | 366.3 | 469.2 | 450.1 | 406.6 | 403.7 | 424.5 | 507.9 | 505.1
1313 | 1153 | 365.7 | 468 | 448.5 | 404.8 | 400.9 | 422.2 | 505.6 | 504.6
1314 | 1154 | 365 | 467.9 | 447.8 | 401.6 | 397.9 | 420.1 | 503.2 | 504.3
1315 | 1155 | 364.4 | 468.4 | 446.8 | 401.2 | 395.4 | 417.9 | 501.3 | 503.9
1316 | 1156 | 363.7 | 466.5 | 445 | 400.6 | 394.2 | 415.8 | 499.7 | 503.5
1317 | 1157 | 363.1 | 465.1 | 443.6 | 401.1 | 392.6 | 413.9 | 497.7 | 502.9
1318 | 1158 | 362.6 | 463 | 442.5 | 404.2 | 392.7 | 412.1 | 496.1 | 502.5
1319 | 1159 | 361.9 | 461.6 | 440.8 | 406.6 | 392.5 | 410.5 | 498.3 | 502.1
1320 | 1160 | 361.4 | 459.4 | 438.4 | 408 | 391.1 | 409 | 495.9 | 501.7
1321 | 1161 | 360.8 | 457.6 | 436.4 | 407.9 | 387.2 | 407.7 | 493.6 | 501.3
1322 | 1162 | 360.1 | 455.3 | 434 | 408.8 | 383.2 | 406.6 | 491.2 | 500.9
1323 | 1163 | 359.4 | 453.4 | 432.4 | 408.3 | 380.6 | 405.4 | 489.2 | 500.5
1324 | 1164 | 358.7 | 452.9 | 431.3 | 407.9 | 378.7 | 404.1 | 487.6 | 500
1325 | 1165 | 358.2 | 450 | 429.5 | 405.8 | 376.5 | 403.1 | 486.4 | 499.8
1326 | 1166 | 357.7 | 448 | 427.6 | 404.3 | 374.2 | 402 | 485 | 499.4
1327 | 1167 | 357.2 | 446.5 | 426.2 | 403.7 | 370.5 | 401 | 483.3 | 499
1328 | 1168 | 356.6 | 445.6 | 425.2 | 404.3 | 369.2 | 399.8 | 481.6 | 498.6
1329 | 1169 | 356.1 | 443.3 | 423.5 | 403 | 367.2 | 398.5 | 480.2 | 498.2
1330 | 1170 | 355.7 | 441.3 | 421.8 | 401.6 | 365.3 | 397 | 478.3 | 497.8
1331 | 1171 | 355 | 439.9 | 420.5 | 400 | 363.4 | 395.4 | 476.5 | 497.4
1332 | 1172 | 354.4 | 437.4 | 418.5 | 399.5 | 361.4 | 394 | 474.4 | 497
1333 | 1173 | 353.7 | 435.3 | 416.8 | 397.9 | 356.9 | 392.7 | 472.4 | 496.5
1334 | 1174 | 353.2 | 433.8 | 415.5 | 394.5 | 355 | 391.4 | 470.6 | 496.1
1335 | 1175 | 352.6 | 433.6 | 414.4 | 392.9 | 353.7 | 390 | 469.2 | 495.6
1336 | 1176 | 352 | 433.1 | 413.4 | 392.2 | 352.1 | 388.4 | 468.2 | 495.1
1337 | 1177 | 351.4 | 432.1 | 412.3 | 390.7 | 347.5 | 386.8 | 466.8 | 494.7
1338 | 1178 | 350.7 | 430.5 | 410.9 | 389.8 | 342.5 | 385.4 | 465.5 | 494.2
1339 | 1179 | 350.1 | 427.5 | 409.2 | 387.4 | 341.4 | 384 | 463.7 | 493.7
1340 | 1180 | 349.6 | 425.5 | 407.2 | 384.8 | 341.4 | 382.8 | 462.2 | 493.3
1341 | 1181 | 349.1 | 423.7 | 405.7 | 381.2 | 341.3 | 381.6 | 460.6 | 492.9
1342 | 1182 | 348.5 | 421.4 | 403.9 | 378 | 340.7 | 380.4 | 459.1 | 492.4
1343 | 1183 | 348 | 419.6 | 402.2 | 375.4 | 340.2 | 379.4 | 457.8 | 492
1344 | 1184 | 347.4 | 417.5 | 400.6 | 374.5 | 341.7 | 378.5 | 456.1 | 491.5
1345 | 1185 | 346.8 | 416.5 | 399.4 | 375.6 | 341.5 | 377.6 | 454.5 | 490.9
1346 | 1186 | 346.2 | 415.6 | 398.6 | 378.5 | 340.4 | 376.8 | 453 | 490.3
1347 | 1187 | 345.6 | 415.1 | 398 | 381 | 338.6 | 376 | 451.8 | 489.8
1348 | 1188 | 345.1 | 413.7 | 397 | 382.6 | 334.8 | 375 | 450.7 | 489.2
1349 | 1189 | 344.4 | 412.2 | 395.9 | 381.5 | 333.5 | 374.1 | 449.4 | 488.7
1350 | 1190 | 343.7 | 410.9 | 394.4 | 379.3 | 329.8 | 373.4 | 447.9 | 488.1
1351 | 1191 | 343.1 | 410.6 | 393.6 | 376.3 | 325.2 | 372.8 | 446.4 | 487.7
1352 | 1192 | 342.5 | 410.4 | 393.3 | 373 | 323.1 | 372 | 444.8 | 487.2
1353 | 1193 | 341.9 | 409.1 | 392.7 | 372.1 | 322.2 | 371.3 | 443.2 | 486.9
1354 | 1194 | 341.4 | 407.4 | 391.1 | 372.7 | 319.6 | 370.5 | 441.8 | 486.4
1355 | 1195 | 340.9 | 406.3 | 389.7 | 371.6 | 318.2 | 369.6 | 440.2 | 486
1356 | 1196 | 340.4 | 405.4 | 388.6 | 371.3 | 319 | 368.6 | 438.1 | 485.5
1357 | 1197 | 339.9 | 404.8 | 387.8 | 375 | 318.9 | 367.7 | 436.3 | 485
1358 | 1198 | 339.3 | 403.5 | 386.9 | 376.7 | 318.7 | 366.6 | 434.5 | 484.5
1359 | 1199 | 338.8 | 403.3 | 386.4 | 377 | 317.6 | 365.4 | 432.5 | 484.1
1360 | 1200 | 338.4 | 402.7 | 385.7 | 375.5 | 316.4 | 364.2 | 430.6 | 483.6
1361 | 1201 | 337.9 | 404.1 | 385.4 | 373.5 | 313.9 | 362.9 | 428.2 | 483.1
1362 | 1202 | 337.3 | 404.3 | 384.4 | 372.4 | 311.8 | 361.8 | 425.4 | 482.5
1363 | 1203 | 336.9 | 404.9 | 383.9 | 372.3 | 310.2 | 360.7 | 423 | 481.9
1364 | 1204 | 336.4 | 406.1 | 383.6 | 370.7 | 309.4 | 359.6 | 420.7 | 481.3
1365 | 1205 | 335.7 | 407.1 | 383 | 369.1 | 308.5 | 358.6 | 418.6 | 480.7
1366 | 1206 | 335.1 | 407.5 | 382.4 | 368.3 | 307.3 | 357.5 | 416.9 | 480.2
1367 | 1207 | 334.6 | 407.4 | 381.7 | 366.2 | 307.7 | 356.5 | 415.1 | 479.6
1368 | 1208 | 334.1 | 406.9 | 380.9 | 364.9 | 307.1 | 355.4 | 413.6 | 479.1
1369 | 1209 | 333.5 | 406.4 | 380.1 | 367.1 | 307.1 | 354.1 | 411.8 | 478.6
1370 | 1210 | 333 | 405.8 | 379.2 | 369.7 | 303.7 | 352.9 | 409.1 | 477.9
1371 | 1211 | 332.4 | 404.1 | 378.3 | 371.5 | 300.3 | 351.5 | 406.3 | 477.3
1372 | 1212 | 332 | 403.8 | 377.4 | 372.2 | 298.7 | 350.1 | 405.1 | 476.7
1373 | 1213 | 331.5 | 402.5 | 376.1 | 370.8 | 297.1 | 348.8 | 403 | 476.1
1374 | 1214 | 331.1 | 400.9 | 375.2 | 366.8 | 295 | 347.5 | 401 | 475.4
1375 | 1215 | 330.4 | 398.2 | 374.2 | 364.7 | 293.3 | 346.3 | 398.8 | 474.7
1376 | 1216 | 329.8 | 397.3 | 373.2 | 363.9 | 292.6 | 345 | 396.6 | 473.8
1377 | 1217 | 329.3 | 396 | 372.1 | 364.6 | 291.8 | 343.7 | 394.6 | 473
1378 | 1218 | 328.9 | 394.1 | 371 | 366.5 | 291 | 342.3 | 393 | 472.3
1379 | 1219 | 328.6 | 392.4 | 370.1 | 368.8 | 290.5 | 341 | 391.2 | 471.8
1380 | 1220 | 328 | 392.4 | 369.6 | 370.2 | 288.5 | 339.8 | 389 | 471.3
1381 | 1221 | 327.5 | 390.3 | 368.5 | 371.5 | 287.9 | 338.6 | 387 | 470.8
1382 | 1222 | 327 | 389.2 | 367.5 | 373.4 | 285.3 | 337.5 | 385.1 | 470.4
1383 | 1223 | 326.3 | 388.6 | 366.2 | 374.7 | 282.2 | 336.3 | 383.3 | 469.8
1384 | 1224 | 325.6 | 385.7 | 365.5 | 375 | 280.6 | 335.2 | 382 | 469.2
1385 | 1225 | 325 | 385.8 | 365 | 375.4 | 279.5 | 334.1 | 380.1 | 468.6
1386 | 1226 | 324.5 | 384.8 | 364.1 | 375.9 | 278.6 | 333 | 377.7 | 467.9
1387 | 1227 | 324.1 | 382.7 | 363 | 375 | 277.4 | 331.9 | 376.2 | 467.2
1388 | 1228 | 323.7 | 382.8 | 362.4 | 373.5 | 277.3 | 330.8 | 375 | 466.6
1389 | 1229 | 323.2 | 383 | 362.1 | 367.8 | 276.5 | 329.7 | 373.6 | 466
1390 | 1230 | 322.7 | 382.5 | 361.8 | 363.6 | 276.1 | 328.7 | 372 | 465.3
1391 | 1231 | 322.3 | 380.4 | 360.4 | 360.7 | 273.3 | 327.6 | 370.2 | 464.7
1392 | 1232 | 321.8 | 378.5 | 359.4 | 357.9 | 271.4 | 326.6 | 368.3 | 463.9
1393 | 1233 | 321.2 | 376 | 358.4 | 355 | 269.9 | 325.5 | 366.8 | 463.3
1394 | 1234 | 320.5 | 373.2 | 357.4 | 352.6 | 269.7 | 324.5 | 365.4 | 462.7
1395 | 1235 | 320 | 371.8 | 356.2 | 348 | 267.3 | 323.4 | 363.5 | 462
1396 | 1236 | 319.5 | 371.5 | 355.2 | 343.3 | 264.3 | 322.3 | 361.5 | 461.4
1397 | 1237 | 319.1 | 370.4 | 354.3 | 339.3 | 261.7 | 321.3 | 359.8 | 460.8
1398 | 1238 | 318.6 | 369.3 | 353.2 | 334.9 | 258.1 | 320.2 | 358.1 | 460.2
1399 | 1239 | 318 | 367.3 | 352.3 | 332.6 | 259.7 | 319 | 356.6 | 459.7
1400 | 1240 | 317.4 | 364.6 | 351.5 | 332.1 | 264.2 | 317.7 | 355.1 | 459
1401 | 1241 | 316.9 | 362.3 | 350.6 | 330.2 | 267.8 | 316.4 | 353.6 | 458.5
1402 | 1242 | 316.4 | 361.4 | 349.9 | 327.2 | 268.9 | 315.2 | 352.3 | 458
1403 | 1243 | 315.8 | 359.2 | 349.3 | 326.4 | 272.1 | 314.2 | 351 | 457.6
1404 | 1244 | 315.2 | 357.3 | 348.3 | 326.1 | 275.1 | 313.2 | 349.6 | 457.2
1405 | 1245 | 314.6 | 354.8 | 347.4 | 325.4 | 276.1 | 312.4 | 348.3 | 456.7
1406 | 1246 | 314.1 | 352.9 | 346.5 | 324.6 | 278.6 | 311.5 | 346.9 | 456.2
1407 | 1247 | 313.5 | 351.2 | 345.2 | 323.8 | 280.1 | 310.6 | 345.5 | 455.7
1408 | 1248 | 312.9 | 349.9 | 344.1 | 321.3 | 281.4 | 309.7 | 344.1 | 455.1
1409 | 1249 | 312.3 | 348.2 | 343 | 317.4 | 280.5 | 308.9 | 342.8 | 454.6
1410 | 1250 | 311.7 | 346.4 | 341.8 | 316.5 | 280.6 | 308.1 | 341.4 | 454
1411 | 1251 | 311.1 | 344.6 | 341.2 | 316 | 282.3 | 307.1 | 340.2 | 453.5
1412 | 1252 | 310.5 | 342.8 | 340.3 | 313.9 | 282.7 | 306.3 | 339 | 453
1413 | 1253 | 309.9 | 341 | 339.2 | 313.2 | 282.1 | 305.5 | 338 | 452.5
1414 | 1254 | 309.5 | 338.9 | 338.4 | 313.3 | 282.7 | 304.7 | 336.8 | 451.9
1415 | 1255 | 309.1 | 337.2 | 337.4 | 312.7 | 283.4 | 303.9 | 335.7 | 451.2
1416 | 1256 | 308.6 | 335.8 | 336.7 | 311.9 | 284.6 | 303 | 334.5 | 450.7
1417 | 1257 | 308.1 | 334.8 | 336.2 | 311.2 | 284.9 | 302.1 | 333.1 | 450.1
1418 | 1258 | 307.7 | 332.8 | 335.2 | 311.5 | 284.7 | 301.1 | 331.9 | 449.5
1419 | 1259 | 307.1 | 331.2 | 334.1 | 311.4 | 284.7 | 300.2 | 330.8 | 449
1420 | 1260 | 306.7 | 330.8 | 333.5 | 311.1 | 284.7 | 299.4 | 329.9 | 448.5
1421 | 1261 | 306.1 | 330.2 | 332.9 | 310.3 | 285.2 | 298.6 | 329 | 448.1
1422 | 1262 | 305.6 | 329.1 | 332.1 | 309.5 | 285.3 | 297.9 | 327.9 | 447.7
1423 | 1263 | 305 | 327.5 | 331 | 308.2 | 285 | 297.2 | 326.5 | 447.3
1424 | 1264 | 304.5 | 325.9 | 330.2 | 306.2 | 284.6 | 296.5 | 325.2 | 446.9
1425 | 1265 | 304.1 | 324.3 | 329.4 | 304.2 | 284.1 | 295.8 | 323.9 | 446.5
1426 | 1266 | 303.5 | 322.5 | 328.4 | 303.6 | 284.2 | 295.1 | 322.9 | 446
1427 | 1267 | 303 | 320.7 | 327.6 | 302.8 | 284.3 | 294.5 | 321.8 | 445.5
1428 | 1268 | 302.4 | 318.8 | 326.3 | 301.2 | 284 | 294 | 320.8 | 445.1
1429 | 1269 | 301.8 | 316.7 | 324.9 | 297.9 | 283.8 | 293.5 | 319.7 | 444.5
1430 | 1270 | 301.3 | 315 | 323.6 | 295.4 | 283.3 | 292.9 | 318.5 | 444
1431 | 1271 | 300.9 | 313.4 | 322.4 | 292.3 | 283.1 | 292.3 | 317.8 | 443.4
1432 | 1272 | 300.4 | 311.8 | 321.6 | 288.6 | 283.6 | 291.7 | 317.2 | 442.8
1433 | 1273 | 300 | 310.5 | 320.7 | 284.5 | 283.4 | 291.2 | 316.4 | 442.3
1434 | 1274 | 299.5 | 308.8 | 319.5 | 279.7 | 281 | 290.7 | 315.8 | 441.7
1435 | 1275 | 299.2 | 307.5 | 318.6 | 276.6 | 278.4 | 290.2 | 315.7 | 441.2
1436 | 1276 | 298.8 | 306.8 | 317.7 | 273.1 | 275.2 | 289.6 | 315.5 | 440.6
1437 | 1277 | 298.4 | 305.4 | 316.8 | 270.8 | 273.4 | 289.1 | 314.3 | 440.1
1438 | 1278 | 297.9 | 303.8 | 315.7 | 267.4 | 272.3 | 288.8 | 313.4 | 439.7
1439 | 1279 | 297.4 | 303.3 | 315.2 | 264.5 | 268.6 | 288.7 | 312.5 | 439.2
1440 | 1280 | 297 | 304 | 314.8 | 262.1 | 266.5 | 288.5 | 311.7 | 438.8
1441 | 1281 | 296.5 | 303.1 | 314.1 | 260.3 | 266.2 | 288.2 | 311.2 | 438.4
1442 | 1282 | 296 | 301.6 | 313.7 | 259.9 | 267.2 | 288 | 310.3 | 438
1443 | 1283 | 295.5 | 300.1 | 312.8 | 259.3 | 267.1 | 287.9 | 309.5 | 437.4
1444 | 1284 | 295 | 298.6 | 311.6 | 257.1 | 264.3 | 287.6 | 308.5 | 436.8
1445 | 1285 | 294.5 | 297.2 | 310.5 | 254.7 | 261.4 | 287.3 | 307.8 | 436.2
1446 | 1286 | 294.1 | 295.9 | 309.4 | 252.9 | 260 | 286.9 | 307.1 | 435.7
1447 | 1287 | 293.7 | 294.7 | 308.4 | 251.4 | 260 | 286.4 | 306.5 | 435.1
1448 | 1288 | 293.2 | 293.8 | 307.5 | 249.9 | 260.7 | 285.8 | 305.4 | 434.4
1449 | 1289 | 292.7 | 292.6 | 306.6 | 249 | 261.4 | 285 | 304.5 | 433.8
1450 | 1290 | 292.3 | 291.1 | 306.1 | 249.6 | 261.5 | 284.1 | 303.7 | 433.2
1451 | 1291 | 291.8 | 290.5 | 305.9 | 250.8 | 261.9 | 283.2 | 302.9 | 432.6
1452 | 1292 | 291.3 | 290.2 | 305.6 | 251.5 | 262.2 | 282.4 | 302.2 | 432.1
1453 | 1293 | 290.8 | 290 | 305.2 | 251.6 | 261.9 | 281.5 | 301.5 | 431.5
1454 | 1294 | 290.3 | 290.2 | 304.6 | 251.1 | 261.8 | 280.6 | 300.7 | 431.1
1455 | 1295 | 289.8 | 291 | 304 | 250.9 | 262.1 | 279.7 | 300 | 430.6
1456 | 1296 | 289.3 | 291.4 | 303.4 | 250.5 | 262 | 278.8 | 299.1 | 430.1
1457 | 1297 | 288.8 | 290.5 | 302.7 | 250 | 261.9 | 277.9 | 298.3 | 429.6
1458 | 1298 | 288.4 | 289.3 | 301.9 | 249.1 | 261.3 | 277 | 297.5 | 429
1459 | 1299 | 288 | 288.3 | 300.9 | 247.9 | 260.9 | 276.1 | 296.6 | 428.5
1460 | 1300 | 287.5 | 287.1 | 299.9 | 247.3 | 261.2 | 275.1 | 295.7 | 427.8
1461 | 1301 | 287 | 285.5 | 299 | 247 | 261.2 | 274.1 | 294.8 | 427.2
1462 | 1302 | 286.6 | 284.7 | 298.2 | 247 | 261.1 | 273.2 | 294 | 426.6
1463 | 1303 | 286.2 | 283.1 | 296.8 | 246.5 | 260.8 | 272.3 | 293.1 | 426.1
1464 | 1304 | 285.7 | 281.7 | 295.8 | 245.5 | 260 | 271.4 | 292.3 | 425.7
1465 | 1305 | 285.2 | 279.7 | 294.6 | 244.1 | 258.9 | 270.4 | 291.5 | 425.3
1466 | 1306 | 284.7 | 278 | 293.6 | 243.5 | 258.4 | 269.5 | 290.7 | 424.9
1467 | 1307 | 284.2 | 276.6 | 292.6 | 243.1 | 257.5 | 268.5 | 289.8 | 424.6
1468 | 1308 | 283.7 | 275.3 | 291.8 | 242.6 | 256.9 | 267.6 | 289 | 424.2
1469 | 1309 | 283.3 | 273.8 | 290.9 | 242.7 | 256.5 | 266.6 | 284.6 | 423.7
1470 | 1310 | 282.9 | 272.4 | 290.2 | 241.9 | 255.5 | 265.6 | 287.1 | 423.2
1471 | 1311 | 282.4 | 271.2 | 289.1 | 239.7 | 252.8 | 264.7 | 286.3 | 422.8
1472 | 1312 | 281.9 | 270 | 287.9 | 237.3 | 250.1 | 263.8 | 284.2 | 422.5
1473 | 1313 | 281.5 | 268.9 | 287 | 235.9 | 249.8 | 262.9 | 284.6 | 422.1
1474 | 1314 | 281.1 | 267.9 | 286.5 | 235.7 | 250.3 | 262.1 | 284.1 | 421.6
1475 | 1315 | 280.6 | 267 | 286.1 | 235.5 | 250.3 | 261.1 | 283.3 | 421
1476 | 1316 | 280.2 | 266.1 | 285.4 | 234.5 | 250.3 | 260.2 | 282.6 | 420.4
1477 | 1317 | 279.8 | 265.2 | 284.8 | 233 | 250.4 | 259.4 | 281.8 | 419.8
1478 | 1318 | 279.3 | 264.3 | 284 | 231 | 250 | 258.6 | 281.2 | 419.2
1479 | 1319 | 278.9 | 263.3 | 283.3 | 229.7 | 249.8 | 257.8 | 280.2 | 418.5
1480 | 1320 | 278.4 | 262 | 282 | 228 | 248.4 | 257 | 279.2 | 417.9
1481 | 1321 | 278 | 260.8 | 280.7 | 226.1 | 245.4 | 256.3 | 278.1 | 417.3
1482 | 1322 | 277.6 | 259.5 | 280 | 224.5 | 244.8 | 255.5 | 277.2 | 416.7
1483 | 1323 | 277.2 | 258.8 | 279.5 | 223.9 | 244.3 | 254.7 | 276.5 | 416.1
1484 | 1324 | 276.7 | 257.6 | 278.6 | 222.9 | 244.1 | 253.9 | 275.9 | 415.5
1485 | 1325 | 276.2 | 256.6 | 277.7 | 221.8 | 244.7 | 253.1 | 275.3 | 414.9
1486 | 1326 | 275.8 | 256.3 | 277.2 | 221.3 | 245.2 | 252.3 | 274.6 | 414.2
1487 | 1327 | 275.5 | 255.7 | 276.8 | 221.2 | 245 | 251.5 | 274 | 413.5
1488 | 1328 | 275.2 | 255.3 | 276.1 | 220.7 | 244 | 250.8 | 273.3 | 412.9
1489 | 1329 | 274.8 | 254 | 275.1 | 220.2 | 243.3 | 250 | 272.6 | 412.2
1490 | 1330 | 274.2 | 253 | 274.2 | 219 | 243 | 249.2 | 272 | 411.6
1491 | 1331 | 273.7 | 251.6 | 273.1 | 216.8 | 243 | 248.2 | 271.7 | 411
1492 | 1332 | 273.2 | 250.2 | 272.4 | 216.7 | 242.9 | 247.3 | 271 | 410.4
1493 | 1333 | 272.7 | 248.9 | 271.5 | 216.8 | 242.8 | 246.3 | 270.1 | 409.8
1494 | 1334 | 272.3 | 247.7 | 270.4 | 216.1 | 242.2 | 245.3 | 269 | 409.1
1495 | 1335 | 271.8 | 247.1 | 269.7 | 214.8 | 241.2 | 244.3 | 268.3 | 408.4
1496 | 1336 | 271.4 | 246.6 | 269 | 213 | 240.1 | 243.4 | 267.7 | 407.8
1497 | 1337 | 271.1 | 246.1 | 268.2 | 212.3 | 239.2 | 242.5 | 267.2 | 407.2
1498 | 1338 | 270.7 | 245.4 | 267.7 | 212.7 | 238.5 | 241.6 | 266.4 | 406.5
1499 | 1339 | 270.2 | 244.5 | 267.1 | 212.4 | 237.1 | 240.7 | 265.6 | 405.9
1500 | 1340 | 269.8 | 243.3 | 266.3 | 210.7 | 236.3 | 239.6 | 265 | 405.2
1501 | 1341 | 269.3 | 242.2 | 265.4 | 209.6 | 235.4 | 238.6 | 264.2 | 404.6
1502 | 1342 | 268.9 | 241.1 | 264.2 | 207.5 | 234.4 | 237.7 | 263.5 | 403.9
1503 | 1343 | 268.5 | 239.8 | 263 | 205.2 | 232.2 | 236.9 | 262.6 | 403.2
1504 | 1344 | 268.1 | 238.6 | 262 | 203.4 | 231.4 | 236 | 261.8 | 402.5
1505 | 1345 | 267.8 | 237.6 | 261.2 | 202.1 | 229.7 | 235.1 | 261.2 | 401.8
1506 | 1346 | 267.4 | 236.7 | 260.5 | 201.1 | 227.5 | 234.1 | 260.7 | 401.1
1507 | 1347 | 267 | 235.9 | 259.7 | 198.9 | 226.5 | 233.3 | 260 | 400.4
1508 | 1348 | 266.7 | 235.3 | 258.9 | 196.4 | 226 | 232.5 | 253.1 | 399.7
1509 | 1349 | 266.4 | 234.3 | 258 | 194.7 | 225.3 | 231.8 | 258.9 | 398.9
1510 | 1350 | 266.1 | 233.3 | 257.3 | 193.5 | 223.4 | 231.1 | 258.5 | 398.3
1511 | 1351 | 265.7 | 232.3 | 256.4 | 192 | 220.9 | 230.4 | 257.7 | 397.6
1512 | 1352 | 265.4 | 231.3 | 255.7 | 190.7 | 219.7 | 229.6 | 256.8 | 397
1513 | 1353 | 264.9 | 230.2 | 255.1 | 190.9 | 219 | 229 | 256.3 | 396.3
1514 | 1354 | 264.5 | 229.2 | 254.3 | 191.1 | 217.3 | 228.3 | 255.6 | 395.6
1515 | 1355 | 264 | 228.1 | 253.6 | 190.8 | 213.8 | 227.5 | 254.9 | 394.9
1516 | 1356 | 263.5 | 227.2 | 252.9 | 190.6 | 212.4 | 226.7 | 254.2 | 394.2
1517 | 1357 | 263.1 | 226.6 | 252.3 | 189.2 | 212 | 225.8 | 253.6 | 393.6
1518 | 1358 | 262.7 | 225.7 | 251.4 | 187.6 | 210.7 | 225 | 253 | 392.9
1519 | 1359 | 262.3 | 224.9 | 250.6 | 186.1 | 209.2 | 224.3 | 252.5 | 392.2
1520 | 1360 | 261.9 | 224.5 | 249.8 | 184.2 | 208.1 | 223.6 | 252 | 391.4
1521 | 1361 | 261.5 | 223.6 | 249.3 | 182.5 | 206.4 | 222.8 | 251.5 | 390.8
1522 | 1362 | 261 | 222.7 | 248.6 | 181.4 | 204.8 | 222.1 | 251 | 390.1
1523 | 1363 | 260.5 | 221.9 | 248 | 181.1 | 204.2 | 221.3 | 250.3 | 389.5
1524 | 1364 | 260.2 | 221.3 | 247.6 | 180.9 | 204.3 | 220.4 | 249.6 | 388.8
1525 | 1365 | 259.9 | 221 | 247.1 | 180.8 | 204.1 | 219.7 | 249.1 | 388.2
1526 | 1366 | 259.6 | 221.1 | 246.7 | 179.9 | 203.5 | 219.1 | 248.7 | 387.6
1527 | 1367 | 259.2 | 220.5 | 246 | 178.8 | 202.8 | 218.5 | 248.2 | 386.9
1528 | 1368 | 258.8 | 220.2 | 245.2 | 177.8 | 200.2 | 217.9 | 247.6 | 386.2
1529 | 1369 | 258.4 | 219.2 | 244.4 | 177.7 | 197.9 | 217.3 | 246.8 | 385.5
1530 | 1370 | 258.1 | 218.4 | 243.8 | 177.1 | 196.1 | 216.8 | 246.3 | 384.8
1531 | 1371 | 257.7 | 217.6 | 243 | 176.8 | 194.1 | 216.2 | 245.9 | 384.1
1532 | 1372 | 257.2 | 216.6 | 242.3 | 176.6 | 193.2 | 215.7 | 245.4 | 383.6
1533 | 1373 | 256.8 | 215.6 | 241.8 | 176.2 | 193.6 | 215.1 | 244.9 | 383.1
1534 | 1374 | 256.4 | 215.2 | 241.3 | 176.2 | 193.8 | 214.6 | 244.4 | 382.5
1535 | 1375 | 256.2 | 215.7 | 240.7 | 175.5 | 193 | 214 | 243.8 | 381.9
1536 | 1376 | 255.9 | 215.9 | 240.4 | 175.3 | 193.3 | 213.4 | 216.3 | 381.3
1537 | 1377 | 255.5 | 216 | 240 | 174.2 | 193.7 | 212.7 | 242.4 | 380.6
1538 | 1378 | 255.1 | 216.2 | 239.5 | 173 | 193.3 | 212.1 | 241.9 | 380
1539 | 1379 | 254.8 | 215.9 | 239 | 172.1 | 191.5 | 211.5 | 241.3 | 379.4
1540 | 1380 | 254.4 | 216.6 | 238.7 | 171.8 | 191.1 | 210.9 | 240.9 | 378.8
1541 | 1381 | 254 | 217.5 | 238.2 | 171.6 | 190.8 | 210.2 | 240.5 | 378.2
1542 | 1382 | 253.5 | 218.4 | 237.6 | 171.2 | 189 | 209.6 | 240 | 377.6
1543 | 1383 | 253 | 218.1 | 237.2 | 171 | 186.7 | 209 | 239.9 | 376.9
1544 | 1384 | 252.6 | 217.4 | 236.4 | 170.5 | 184.3 | 208.2 | 239.5 | 375.9
1545 | 1385 | 252.2 | 217.6 | 236 | 170.7 | 182.9 | 207.5 | 239 | 375.2
1546 | 1386 | 251.8 | 217.8 | 235.6 | 170.2 | 182.3 | 206.8 | 238.5 | 374.5
1547 | 1387 | 251.4 | 218.3 | 235.1 | 169.7 | 181.9 | 206.2 | 237.9 | 373.6
1548 | 1388 | 251 | 218.9 | 234.5 | 170.3 | 180.6 | 205.6 | 237.1 | 372.9
1549 | 1389 | 250.6 | 219.1 | 234 | 171.2 | 180.4 | 204.9 | 236.4 | 372.1
1550 | 1390 | 250.3 | 219.3 | 233.4 | 172.9 | 180.4 | 204.2 | 236 | 371.4
1551 | 1391 | 250 | 219.4 | 232.9 | 174.6 | 179.9 | 203.6 | 234.7 | 370.7
1552 | 1392 | 249.6 | 219.8 | 232.3 | 175.5 | 180.3 | 203 | 233.6 | 370
1553 | 1393 | 249.2 | 220.3 | 231.8 | 176.3 | 180.6 | 202.4 | 233.2 | 369.2
1554 | 1394 | 248.8 | 220.7 | 231.4 | 177.1 | 180.5 | 201.9 | 232.7 | 368.5
1555 | 1395 | 248.4 | 221 | 231 | 178.6 | 180 | 201.4 | 232.3 | 367.9
1556 | 1396 | 248.1 | 221.2 | 230.6 | 180.4 | 179.5 | 200.9 | 231.3 | 367.2
1557 | 1397 | 247.8 | 221.4 | 230.2 | 182 | 178.5 | 200.4 | 230.3 | 366.5
1558 | 1398 | 247.5 | 221.6 | 229.8 | 183.4 | 177.5 | 199.8 | 229.5 | 365.7
1559 | 1399 | 247.1 | 221.6 | 229.3 | 184.8 | 176.3 | 199.3 | 229.1 | 365
1560 | 1400 | 246.7 | 221.7 | 229 | 185.3 | 174.9 | 198.8 | 228.3 | 364.3
1561 | 1401 | 246.4 | 221.8 | 228.6 | 185.2 | 173.7 | 198.4 | 205.9 | 363.5
1562 | 1402 | 246.1 | 221.2 | 228.1 | 185.4 | 171.6 | 197.8 | 226 | 362.7
1563 | 1403 | 245.8 | 220.5 | 227.7 | 185.8 | 170.6 | 197.3 | 227.6 | 362.1
1564 | 1404 | 245.4 | 220.4 | 227.3 | 185.2 | 169.4 | 196.7 | 227.6 | 361.4
1565 | 1405 | 245 | 220.2 | 227 | 183.6 | 168.7 | 196.2 | 227.4 | 360.8
1566 | 1406 | 244.6 | 219.1 | 226.5 | 182.5 | 168.8 | 195.7 | 227.1 | 360.1
1567 | 1407 | 244.2 | 218.1 | 225.8 | 180.7 | 167.9 | 195.2 | 227 | 359.4
1568 | 1408 | 243.8 | 216.6 | 225.3 | 179.6 | 168.3 | 194.7 | 226.6 | 358.7
1569 | 1409 | 243.3 | 215.3 | 224.9 | 177.9 | 167.4 | 194.2 | 226.4 | 357.9
1570 | 1410 | 242.9 | 213.9 | 224.5 | 176.7 | 166 | 193.8 | 226.1 | 357.1
1571 | 1411 | 242.5 | 213.6 | 224.2 | 176.2 | 165.1 | 193.3 | 225.9 | 356.4
1572 | 1412 | 242.2 | 213.2 | 223.7 | 176.7 | 164.8 | 192.8 | 225.5 | 355.6
1573 | 1413 | 241.8 | 212.7 | 223.3 | 177.2 | 164.6 | 192.3 | 225.2 | 354.7
1574 | 1414 | 241.4 | 211.8 | 222.8 | 176.8 | 164.2 | 191.8 | 224.9 | 354
1575 | 1415 | 241 | 210.3 | 222.2 | 176.1 | 164.2 | 191.1 | 224.9 | 353.3
1576 | 1416 | 240.8 | 209.5 | 221.8 | 174.8 | 164.4 | 190.6 | 224.7 | 352.6
1577 | 1417 | 240.4 | 209.2 | 221.5 | 173.2 | 165 | 190.1 | 224.4 | 351.8
1578 | 1418 | 240.1 | 208.8 | 221.2 | 172.6 | 165.3 | 189.6 | 224.2 | 351.1
1579 | 1419 | 239.8 | 208 | 220.9 | 171.8 | 165.5 | 189.2 | 223.9 | 350.4
1580 | 1420 | 239.4 | 207.4 | 220.6 | 171.1 | 163.9 | 188.7 | 223.8 | 349.7
1581 | 1421 | 239.1 | 207.1 | 220.1 | 171.7 | 162.8 | 188.3 | 223.2 | 349
1582 | 1422 | 238.8 | 206.3 | 219.8 | 170.7 | 161.4 | 187.8 | 223.1 | 348.4
1583 | 1423 | 238.5 | 206.1 | 219.6 | 170.1 | 161.9 | 187.5 | 222.8 | 347.8
1584 | 1424 | 238.2 | 205.3 | 219.1 | 169.2 | 161.4 | 187.1 | 208.6 | 347.1
1585 | 1425 | 237.9 | 204.7 | 218.6 | 168.7 | 159.7 | 186.6 | 222.5 | 346.4
1586 | 1426 | 237.7 | 204.8 | 218.3 | 167.5 | 159.6 | 186.2 | 222.2 | 345.8
1587 | 1427 | 237.4 | 204.2 | 218 | 166.2 | 159.2 | 185.7 | 221.8 | 345.1
1588 | 1428 | 237.1 | 203.5 | 217.6 | 164.8 | 160 | 185.2 | 221.4 | 344.4
1589 | 1429 | 236.8 | 202.6 | 217.1 | 164.5 | 160.5 | 184.8 | 220.9 | 343.9
1590 | 1430 | 236.4 | 201.1 | 216.5 | 164.6 | 159 | 184.4 | 220.7 | 343.3
1591 | 1431 | 236 | 200.1 | 216.1 | 164.2 | 158.2 | 184 | 220.3 | 342.7
1592 | 1432 | 235.6 | 200.3 | 215.8 | 163.6 | 158.2 | 183.6 | 220 | 342
1593 | 1433 | 235.3 | 199.9 | 215.3 | 162.7 | 156.9 | 183.2 | 219.6 | 341.3
1594 | 1434 | 234.8 | 200 | 215 | 162.2 | 156.1 | 182.8 | 218.9 | 340.7
1595 | 1435 | 234.4 | 199.6 | 214.5 | 161.8 | 155.4 | 182.4 | 218.4 | 339.9
1596 | 1436 | 234 | 198.1 | 213.8 | 161 | 154.3 | 182 | 218 | 339.2
1597 | 1437 | 233.7 | 197.1 | 213.1 | 160.5 | 152.3 | 181.6 | 217.6 | 338.6
1598 | 1438 | 233.4 | 196 | 212.4 | 160.3 | 150.2 | 181.2 | 217.6 | 337.9
1599 | 1439 | 233 | 194.6 | 211.8 | 160.2 | 149.2 | 180.7 | 217.8 | 337.3
1600 | 1440 | 232.6 | 193.8 | 211.4 | 159.9 | 149.1 | 180.3 | 217.4 | 336.6
1601 | 1441 | 232.2 | 193.4 | 211 | 159.1 | 148 | 179.8 | 217.4 | 335.9
1602 | 1442 | 232 | 192.8 | 210.6 | 158.2 | 147.4 | 179.4 | 217.4 | 335.2
1603 | 1443 | 231.7 | 191.7 | 210.2 | 158.2 | 147.9 | 179 | 204.8 | 334.4
1604 | 1444 | 231.3 | 191.2 | 210 | 159.4 | 149.4 | 178.7 | 213 | 333.7
1605 | 1445 | 231 | 191.5 | 209.7 | 160.2 | 150.7 | 178.4 | 217 | 333.1
1606 | 1446 | 230.4 | 191.5 | 209.5 | 160.5 | 152.6 | 178 | 217.1 | 332.5
1607 | 1447 | 230 | 190.6 | 209.3 | 160.5 | 154.3 | 177.6 | 216.8 | 332
1608 | 1448 | 229.7 | 189.9 | 209.1 | 160.8 | 156.3 | 177.2 | 216.6 | 331.4
1609 | 1449 | 229.5 | 189.2 | 208.8 | 161.1 | 157.6 | 176.8 | 216.5 | 330.8
1610 | 1450 | 229.2 | 188.4 | 208.3 | 161.8 | 157.9 | 176.4 | 216.1 | 330.1
1611 | 1451 | 229 | 188.3 | 208 | 162.3 | 157.7 | 176 | 216.3 | 329.4
1612 | 1452 | 228.8 | 188.3 | 207.7 | 162.7 | 158.5 | 175.6 | 216.3 | 328.7
1613 | 1453 | 228.4 | 187.5 | 207.3 | 163.3 | 159.2 | 175.1 | 215.9 | 328
1614 | 1454 | 228.1 | 186.4 | 206.7 | 163.8 | 158.8 | 174.7 | 216.1 | 327.3
1615 | 1455 | 227.8 | 185.4 | 206.2 | 164 | 158.6 | 174.2 | 216.8 | 326.5
1616 | 1456 | 227.5 | 184.9 | 205.9 | 164.4 | 159.1 | 173.8 | 217 | 325.8
1617 | 1457 | 227.1 | 184.8 | 205.6 | 164.3 | 160.2 | 173.4 | 216.7 | 325
1618 | 1458 | 226.8 | 184 | 205.2 | 164.3 | 161.2 | 172.9 | 216.2 | 324.3
1619 | 1459 | 226.4 | 183.1 | 204.5 | 163.2 | 160.3 | 172.5 | 215.8 | 323.6
1620 | 1460 | 226.1 | 182.3 | 203.5 | 161.9 | 158.7 | 172.1 | 199.8 | 322.9
1621 | 1461 | 225.8 | 182 | 203.5 | 161.2 | 158.1 | 171.6 | 215.7 | 322.3
1622 | 1462 | 225.5 | 182.1 | 203.3 | 160.5 | 158.3 | 171.2 | 216.1 | 321.8
1623 | 1463 | 225.1 | 181.6 | 202.8 | 159 | 158.1 | 170.7 | 215.7 | 321.4
1624 | 1464 | 224.8 | 181 | 202.2 | 157.3 | 156.7 | 170.3 | 215.5 | 320.8
1625 | 1465 | 224.4 | 180.7 | 201.7 | 155.5 | 156.1 | 169.8 | 215.3 | 320.3
1626 | 1466 | 224.1 | 179.9 | 201 | 153.7 | 156 | 169.3 | 214.8 | 319.6
1627 | 1467 | 223.7 | 179.5 | 200.4 | 152.5 | 155.4 | 168.8 | 214.6 | 319
1628 | 1468 | 223.3 | 178.7 | 200 | 151.4 | 154.5 | 168.4 | 214.3 | 318.4
1629 | 1469 | 223.1 | 178.3 | 199.5 | 151.2 | 153.4 | 167.9 | 213.8 | 317.7
1630 | 1470 | 222.8 | 178.6 | 199.2 | 151 | 152.4 | 167.5 | 213.4 | 317
1631 | 1471 | 222.4 | 178.4 | 198.8 | 149.5 | 152.1 | 167.1 | 213.1 | 316.3
1632 | 1472 | 222.2 | 177.7 | 198.4 | 148.2 | 151 | 166.7 | 212.9 | 315.6
1633 | 1473 | 221.8 | 177.4 | 198 | 148.2 | 150.5 | 166.3 | 212.2 | 314.9
1634 | 1474 | 221.5 | 176.8 | 197.5 | 147.9 | 150.8 | 165.9 | 211.8 | 314.2
1635 | 1475 | 221.1 | 176.4 | 196.9 | 147.2 | 150.1 | 165.6 | 211.2 | 313.6
1636 | 1476 | 220.7 | 176.6 | 196.6 | 146.5 | 148.3 | 165.2 | 210.7 | 313
1637 | 1477 | 220.4 | 176.3 | 196.3 | 145.6 | 147.3 | 164.7 | 210.6 | 312.3
1638 | 1478 | 220 | 176.1 | 196 | 145.3 | 147.1 | 164.3 | 210.1 | 311.6
1639 | 1479 | 219.6 | 175.7 | 195.6 | 144.8 | 147.2 | 163.9 | 209.7 | 310.9
1640 | 1480 | 219.4 | 174.6 | 195.1 | 144.2 | 145.8 | 163.5 | 209.1 | 310.2
1641 | 1481 | 219.1 | 174 | 194.4 | 144.3 | 144.7 | 163.1 | 208.8 | 309.4
1642 | 1482 | 218.8 | 173.7 | 194 | 144.9 | 143.6 | 162.7 | 208.5 | 308.8
1643 | 1483 | 218.5 | 173 | 193.5 | 145.4 | 142.4 | 162.3 | 208 | 308.1
1644 | 1484 | 218.2 | 172.5 | 193.1 | 145 | 142.2 | 161.9 | 207.7 | 307.3
1645 | 1485 | 217.8 | 171.7 | 192.5 | 144.7 | 140.9 | 161.5 | 207.8 | 306.6
1646 | 1486 | 217.5 | 170.6 | 191.9 | 145.1 | 140 | 161.2 | 207.4 | 306
1647 | 1487 | 217.2 | 169.5 | 191.5 | 145.7 | 140.3 | 160.9 | 206.8 | 305.3
1648 | 1488 | 216.9 | 168.7 | 191.3 | 146.3 | 140.5 | 160.6 | 206.2 | 304.7
1649 | 1489 | 216.6 | 167.8 | 190.8 | 147.3 | 139.5 | 160.3 | 206.1 | 304.1
1650 | 1490 | 216.4 | 166.9 | 190.2 | 148.1 | 138.5 | 160 | 206 | 303.4
1651 | 1491 | 216 | 166.7 | 189.9 | 148.5 | 139.2 | 159.7 | 205.7 | 302.8
1652 | 1492 | 215.6 | 167 | 189.7 | 148.3 | 141 | 159.4 | 205.3 | 302.2
1653 | 1493 | 215.3 | 167 | 189.5 | 148.3 | 142.7 | 159 | 205 | 301.5
1654 | 1494 | 215 | 166.7 | 189 | 148.4 | 144.3 | 158.7 | 198.4 | 300.9
1655 | 1495 | 214.7 | 166.6 | 188.8 | 148.3 | 145.7 | 158.3 | 203.9 | 300.2
1656 | 1496 | 214.4 | 166 | 188.5 | 148.6 | 146.6 | 158 | 203.6 | 299.5
1657 | 1497 | 214.1 | 165.4 | 188.1 | 148.7 | 146.3 | 157.7 | 203.2 | 298.9
1658 | 1498 | 213.8 | 164.7 | 187.6 | 148.6 | 145.3 | 157.3 | 203.2 | 298.3
1659 | 1499 | 213.6 | 164.2 | 186.5 | 147.9 | 144 | 157.1 | 191 | 297.6
1660 | 1500 | 213.3 | 163.5 | 186.2 | 147.1 | 143 | 156.6 | 198.2 | 297
1661 | 1501 | 213 | 163 | 185.8 | 146.8 | 142.9 | 156.3 | 202.6 | 296.4
1662 | 1502 | 212.6 | 162.5 | 185.5 | 146.8 | 141.7 | 156 | 202 | 295.8
1663 | 1503 | 212.2 | 162.1 | 185.1 | 146.7 | 140.7 | 155.6 | 194 | 295.2
1664 | 1504 | 211.9 | 161.7 | 184.7 | 146.2 | 139.6 | 155.3 | 193.6 | 294.7
1665 | 1505 | 211.6 | 161.7 | 184.4 | 145.6 | 139.6 | 155 | 201.6 | 294.1
1666 | 1506 | 211.3 | 161.9 | 184.1 | 145.4 | 140.2 | 154.7 | 200.9 | 293.5
1667 | 1507 | 211 | 162.2 | 183.8 | 144.6 | 140.5 | 154.3 | 200.3 | 292.8
1668 | 1508 | 210.6 | 161.9 | 183.4 | 143.4 | 139.4 | 153.9 | 199.9 | 292.3
1669 | 1509 | 210.3 | 161.5 | 183 | 141.9 | 139.6 | 153.5 | 199.7 | 291.6
1670 | 1510 | 209.9 | 160.8 | 182.4 | 140.5 | 138.7 | 153.1 | 199.1 | 291
1671 | 1511 | 209.6 | 160.9 | 182 | 139.6 | 137.5 | 152.7 | 198.4 | 290.4
1672 | 1512 | 209.4 | 160.9 | 181.7 | 138.7 | 136.7 | 152.3 | 198.1 | 289.8
1673 | 1513 | 209.2 | 160.2 | 181.2 | 137.8 | 136.6 | 152 | 197.6 | 289.2
1674 | 1514 | 209 | 159.7 | 180.8 | 137.2 | 135.2 | 151.6 | 197 | 288.6
1675 | 1515 | 208.8 | 159.1 | 180.2 | 136.7 | 134.1 | 151.3 | 196.3 | 287.9
1676 | 1516 | 208.5 | 158.5 | 179.8 | 136.5 | 133.1 | 151 | 195.6 | 287.3
1677 | 1517 | 208.1 | 157.8 | 179.3 | 136 | 131.9 | 150.7 | 195.1 | 286.6
1678 | 1518 | 207.9 | 157.1 | 178.7 | 136.2 | 130.5 | 150.5 | 194.5 | 286
1679 | 1519 | 207.5 | 156.5 | 178.4 | 136.7 | 129.6 | 150.2 | 193.7 | 285.4
1680 | 1520 | 207.2 | 156 | 177.7 | 136.6 | 129.9 | 149.9 | 193.3 | 284.7
1681 | 1521 | 206.9 | 155.4 | 177.3 | 136.2 | 129.6 | 149.6 | 192.9 | 284.2
1682 | 1522 | 206.5 | 154.7 | 177 | 136.4 | 129 | 149.3 | 192.5 | 283.5
1683 | 1523 | 206.2 | 154.1 | 176.7 | 137.2 | 129.4 | 149 | 192.2 | 282.9
1684 | 1524 | 206 | 153.7 | 176.5 | 138.4 | 130.1 | 148.6 | 192.1 | 282.3
1685 | 1525 | 205.8 | 153.5 | 176.4 | 139.3 | 131 | 148.3 | 191.7 | 281.7
1686 | 1526 | 205.5 | 153.2 | 176.2 | 139.5 | 131.8 | 147.9 | 191.6 | 281.1
1687 | 1527 | 205.3 | 153.2 | 176 | 139.9 | 131.4 | 147.6 | 191.2 | 280.5
1688 | 1528 | 205.1 | 152.8 | 175.8 | 140.3 | 130.1 | 147.3 | 190.9 | 279.8
1689 | 1529 | 205 | 152.2 | 175.4 | 140.7 | 130.1 | 147 | 190.6 | 279.2
1690 | 1530 | 204.8 | 152.1 | 175.1 | 141.1 | 131.3 | 146.7 | 190.3 | 278.7
1691 | 1531 | 204.5 | 152.2 | 174.9 | 141 | 132 | 146.4 | 190.5 | 278.1
1692 | 1532 | 204.2 | 152.7 | 174.6 | 140.6 | 132.5 | 146.2 | 188.9 | 277.5
1693 | 1533 | 203.9 | 152.6 | 174 | 140.4 | 131.7 | 146 | 184.2 | 276.9
1694 | 1534 | 203.7 | 151.8 | 173.8 | 139.9 | 130 | 145.6 | 189.1 | 276.4
1695 | 1535 | 203.4 | 151 | 173.3 | 139.5 | 128.8 | 145.3 | 188.9 | 275.9
1696 | 1536 | 203.1 | 150.6 | 172.9 | 139.1 | 128.7 | 144.9 | 188.7 | 275.4
1697 | 1537 | 202.9 | 150 | 172.6 | 139 | 128.7 | 144.5 | 188.5 | 274.9
1698 | 1538 | 202.6 | 149.4 | 172.1 | 138.7 | 128.7 | 144.2 | 188 | 274.5
1699 | 1539 | 202.3 | 148.8 | 171.7 | 138 | 128 | 143.9 | 187.4 | 274
1700 | 1540 | 202 | 148.4 | 171.3 | 137.1 | 126.6 | 143.6 | 187.2 | 273.3
1701 | 1541 | 201.7 | 148.6 | 171 | 136.4 | 126.9 | 143.3 | 186.9 | 272.8
1702 | 1542 | 201.4 | 148.7 | 170.8 | 135.9 | 126.8 | 142.9 | 186.4 | 272.2
1703 | 1543 | 201 | 149 | 170.5 | 134.6 | 125.8 | 142.6 | 185.8 | 271.7
1704 | 1544 | 200.6 | 149.4 | 170.1 | 133.4 | 125.5 | 142.2 | 185.3 | 271.2
1705 | 1545 | 200.3 | 149.5 | 169.9 | 132.6 | 125.3 | 141.8 | 184.7 | 270.6
1706 | 1546 | 200 | 149.7 | 169.5 | 131.4 | 124.9 | 141.5 | 184.3 | 270
1707 | 1547 | 199.8 | 149.8 | 169.2 | 130.1 | 124.1 | 141.1 | 184 | 269.5
1708 | 1548 | 199.5 | 149.4 | 168.8 | 128.9 | 123.8 | 140.7 | 183.6 | 268.9
1709 | 1549 | 199.2 | 149.5 | 168.4 | 127.5 | 124.1 | 140.4 | 183.1 | 268.3
1710 | 1550 | 198.9 | 150.1 | 168 | 126.7 | 123.7 | 140.1 | 182.4 | 267.8
1711 | 1551 | 198.6 | 150.7 | 167.6 | 126.6 | 123.1 | 139.7 | 181.8 | 267.2
1712 | 1552 | 198.3 | 151.2 | 167.2 | 126.5 | 123.3 | 139.3 | 181.3 | 266.6
1713 | 1553 | 198 | 151.6 | 166.7 | 126.1 | 122.6 | 138.9 | 180.6 | 266
1714 | 1554 | 197.8 | 151.9 | 166.2 | 125.7 | 122.1 | 138.5 | 180 | 265.3
1715 | 1555 | 197.5 | 152.1 | 165.7 | 125.2 | 122.5 | 138.2 | 179.6 | 264.8
1716 | 1556 | 197.1 | 152.3 | 165.2 | 124.4 | 123.1 | 137.9 | 179.2 | 264.2
1717 | 1557 | 196.8 | 152.5 | 164.7 | 123.2 | 122.7 | 137.6 | 179 | 263.6
1718 | 1558 | 196.6 | 152.7 | 164.3 | 121.6 | 122.6 | 137.3 | 178.4 | 263
1719 | 1559 | 196.4 | 152.9 | 163.8 | 120.5 | 122.4 | 137 | 178.1 | 262.5
1720 | 1560 | 196.2 | 152.9 | 163.3 | 119.4 | 122 | 136.7 | 177.5 | 262
1721 | 1561 | 196 | 152.9 | 162.8 | 118.6 | 121.8 | 136.5 | 176.6 | 261.3
1722 | 1562 | 195.8 | 152.8 | 162.5 | 117.9 | 121.6 | 136.1 | 176.4 | 260.7
1723 | 1563 | 195.5 | 152.9 | 162.1 | 117.4 | 121.2 | 135.8 | 175.8 | 260.2
1724 | 1564 | 195.2 | 153 | 161.8 | 117.3 | 120.8 | 135.5 | 175.3 | 259.6
1725 | 1565 | 194.9 | 152.7 | 161.4 | 117.6 | 119.2 | 135.2 | 174.7 | 259
1726 | 1566 | 194.7 | 151.8 | 161 | 117.8 | 117.6 | 134.9 | 174.2 | 258.4
1727 | 1567 | 194.4 | 151.7 | 160.6 | 117.7 | 117.3 | 134.6 | 173.6 | 257.9
1728 | 1568 | 194.1 | 151.7 | 160.4 | 117.3 | 117.4 | 134.4 | 173 | 257.3
1729 | 1569 | 193.8 | 151.5 | 160.2 | 116.4 | 116.2 | 134.1 | 172.8 | 256.7
1730 | 1570 | 193.5 | 151.4 | 159.9 | 115.3 | 115.6 | 133.8 | 172.3 | 256.1
1731 | 1571 | 193.2 | 151.3 | 159.6 | 114.4 | 115.3 | 133.5 | 171.9 | 255.5
1732 | 1572 | 193 | 150.7 | 159.2 | 113.7 | 114.9 | 133.3 | 171.5 | 255
1733 | 1573 | 192.7 | 149.5 | 158.8 | 112.6 | 115.1 | 133 | 171.2 | 254.4
1734 | 1574 | 192.4 | 148.5 | 158.5 | 111.7 | 115.9 | 132.8 | 171.1 | 253.8
1735 | 1575 | 192.2 | 148.3 | 158.2 | 111.4 | 116.5 | 132.6 | 170.7 | 253.3
1736 | 1576 | 192 | 148.1 | 157.9 | 110.6 | 117 | 132.4 | 170.5 | 252.8
1737 | 1577 | 191.7 | 147.5 | 157.6 | 110.1 | 117.3 | 132.2 | 170.2 | 252.3
1738 | 1578 | 191.5 | 146.8 | 157.4 | 109.7 | 116.9 | 132 | 169.8 | 251.7
1739 | 1579 | 191.3 | 146.5 | 157 | 108.7 | 117 | 131.8 | 169.4 | 251.1
1740 | 1580 | 191.1 | 146.5 | 156.7 | 108.5 | 117.1 | 131.6 | 169 | 250.6
1741 | 1581 | 190.9 | 146.1 | 156.5 | 108.5 | 116.3 | 131.4 | 168.6 | 250.1
1742 | 1582 | 190.5 | 145.5 | 156.1 | 108.3 | 114.2 | 131.1 | 168 | 249.6
1743 | 1583 | 190.2 | 144.9 | 155.7 | 107.7 | 112.6 | 130.9 | 167.7 | 249.1
1744 | 1584 | 189.9 | 144.7 | 155.5 | 107.2 | 111.9 | 130.6 | 167.5 | 248.5
1745 | 1585 | 189.7 | 144.7 | 155.4 | 106.6 | 111.3 | 130.4 | 167.4 | 247.9
1746 | 1586 | 189.5 | 144.4 | 155.3 | 106.6 | 111.5 | 130.1 | 167.3 | 247.3
1747 | 1587 | 189.2 | 143.8 | 155 | 107 | 111 | 129.9 | 167.1 | 246.8
1748 | 1588 | 189 | 143.4 | 154.7 | 107.2 | 110.1 | 129.6 | 166.7 | 246.3
1749 | 1589 | 188.6 | 143.3 | 154.5 | 106.8 | 109.3 | 129.4 | 166.5 | 245.8
1750 | 1590 | 188.4 | 143.6 | 154.3 | 107.5 | 108.2 | 129.2 | 166.1 | 245.3
1751 | 1591 | 188.1 | 143.8 | 154.2 | 108.5 | 107.4 | 129 | 165.3 | 244.8
1752 | 1592 | 187.8 | 143.8 | 154 | 109.5 | 106 | 128.8 | 165 | 244.2
1753 | 1593 | 187.5 | 144.1 | 153.9 | 109.9 | 104.8 | 128.5 | 164.8 | 243.6
1754 | 1594 | 187.2 | 144.4 | 153.6 | 110.1 | 104 | 128.3 | 164.2 | 243.1
1755 | 1595 | 187 | 144.6 | 153.4 | 110.3 | 103.2 | 128.1 | 163.8 | 242.6
1756 | 1596 | 186.8 | 144.3 | 153.2 | 110.4 | 102 | 127.9 | 163.4 | 242.1
1757 | 1597 | 186.6 | 143.8 | 152.8 | 109.5 | 100.9 | 127.7 | 163.2 | 241.6
1758 | 1598 | 186.4 | 143.4 | 152.6 | 108.7 | 100.4 | 127.5 | 162.8 | 241
1759 | 1599 | 186.1 | 143.4 | 152.4 | 107.8 | 100.1 | 127.3 | 162.2 | 240.5
1760 | 1600 | 185.8 | 143.4 | 152.1 | 107.1 | 99.1 | 127.1 | 162.2 | 240
1761 | 1601 | 185.6 | 143.3 | 151.8 | 106.2 | 98.1 | 126.9 | 162 | 239.4
1762 | 1602 | 185.4 | 143.3 | 151.6 | 105.5 | 97 | 126.7 | 161.5 | 238.9
1763 | 1603 | 185.1 | 143.3 | 151.4 | 105.3 | 96.3 | 126.5 | 161.3 | 238.4
1764 | 1604 | 184.7 | 142.4 | 151 | 104.8 | 95.3 | 126.3 | 160.9 | 237.9
1765 | 1605 | 184.5 | 141.5 | 150.7 | 104.3 | 94.4 | 126.2 | 160.5 | 237.4
1766 | 1606 | 184.2 | 141.2 | 150.6 | 104.2 | 93.8 | 126 | 160 | 236.9
1767 | 1607 | 183.9 | 141.5 | 150.2 | 104.5 | 93.4 | 125.9 | 159.6 | 236.4
1768 | 1608 | 183.6 | 141.5 | 149.9 | 104.2 | 93 | 125.7 | 159.3 | 235.9
1769 | 1609 | 183.3 | 141.1 | 149.6 | 103.3 | 92.6 | 125.6 | 159 | 235.4
1770 | 1610 | 183 | 140.7 | 149.2 | 102.5 | 92.4 | 125.5 | 158.6 | 235
1771 | 1611 | 182.7 | 139.9 | 148.7 | 102.1 | 92.7 | 125.3 | 158.2 | 234.4
1772 | 1612 | 182.5 | 139.2 | 148.3 | 101.8 | 92.7 | 125 | 158 | 233.9
1773 | 1613 | 182.2 | 138.6 | 148 | 101.5 | 92.7 | 124.8 | 157.5 | 233.4
1774 | 1614 | 182 | 138 | 147.7 | 100.8 | 93 | 124.6 | 157.2 | 232.9
1775 | 1615 | 181.7 | 138.1 | 147.5 | 100.2 | 92.2 | 124.4 | 156.8 | 232.4
1776 | 1616 | 181.5 | 138.1 | 147.3 | 99.5 | 91.6 | 124.1 | 156.3 | 231.9
1777 | 1617 | 181.2 | 137.9 | 147.2 | 98.9 | 91.4 | 123.9 | 155.9 | 231.5
1778 | 1618 | 181 | 138 | 147 | 98.4 | 91.5 | 123.6 | 155.5 | 231
1779 | 1619 | 180.7 | 138.3 | 146.7 | 98.3 | 91.2 | 123.4 | 155.1 | 230.5
1780 | 1620 | 180.5 | 138.4 | 146.3 | 98.5 | 90.8 | 123.2 | 154.7 | 230.1
1781 | 1621 | 180.3 | 138.5 | 145.7 | 98.6 | 90.5 | 123 | 154.2 | 229.5
1782 | 1622 | 180.1 | 138.6 | 145.5 | 98.6 | 90.1 | 122.8 | 154 | 228.9
1783 | 1623 | 179.9 | 138.7 | 145.2 | 98.4 | 89.8 | 122.6 | 153.7 | 228.5
1784 | 1624 | 179.7 | 138.6 | 144.8 | 98.1 | 90 | 122.3 | 153.2 | 228
1785 | 1625 | 179.5 | 138.2 | 144.5 | 97.9 | 90 | 122.1 | 153 | 227.5
1786 | 1626 | 179.3 | 137.9 | 144.1 | 97.6 | 89.4 | 121.8 | 152.8 | 227
1787 | 1627 | 179 | 137.8 | 143.8 | 97.2 | 89.3 | 121.5 | 152.4 | 226.5
1788 | 1628 | 178.8 | 137.6 | 143.6 | 96.6 | 89.2 | 121.2 | 152.1 | 226.1
1789 | 1629 | 178.5 | 137.4 | 143.4 | 96.3 | 89.4 | 120.9 | 151.8 | 225.6
1790 | 1630 | 178.3 | 137.4 | 143.1 | 96.9 | 89.5 | 120.6 | 151.4 | 225.2
1791 | 1631 | 178.1 | 137.4 | 142.9 | 97.5 | 89.5 | 120.4 | 151.2 | 224.7
1792 | 1632 | 177.8 | 137.1 | 142.7 | 97.5 | 89.2 | 120.3 | 150.8 | 224.3
1793 | 1633 | 177.6 | 136.8 | 142.5 | 97.1 | 89.1 | 120.1 | 150.5 | 223.9
1794 | 1634 | 177.3 | 136.4 | 142.3 | 96.8 | 89.2 | 120 | 150.4 | 223.4
1795 | 1635 | 177.1 | 135.8 | 142 | 96.5 | 88.9 | 119.9 | 150.2 | 222.9
1796 | 1636 | 177 | 135.3 | 141.6 | 96.3 | 88.3 | 119.8 | 149.9 | 222.5
1797 | 1637 | 176.7 | 134.1 | 141.3 | 95.9 | 88 | 119.6 | 149.9 | 222
1798 | 1638 | 176.5 | 133.1 | 141 | 95.5 | 87.8 | 119.4 | 149.8 | 221.6
1799 | 1639 | 176.2 | 132.2 | 140.8 | 95.3 | 88.1 | 119.3 | 149.7 | 221.1
1800 | 1640 | 176 | 131.7 | 140.7 | 96 | 89.2 | 119.1 | 149.9 | 220.7
1801 | 1641 | 175.8 | 131.4 | 140.5 | 96.6 | 89.7 | 118.9 | 149.7 | 220.2
1802 | 1642 | 175.6 | 131 | 140.5 | 97.1 | 90 | 118.7 | 149.5 | 219.7
1803 | 1643 | 175.4 | 130.4 | 140.3 | 97.5 | 90.1 | 118.6 | 149.3 | 219.3
1804 | 1644 | 175.3 | 129.8 | 140 | 97.2 | 89.5 | 118.4 | 149.2 | 218.8
1805 | 1645 | 175 | 129.2 | 139.7 | 97.3 | 89.1 | 118.2 | 149.4 | 218.4
1806 | 1646 | 174.8 | 128.6 | 139.5 | 98.1 | 89.4 | 118 | 149.3 | 218
1807 | 1647 | 174.5 | 128.2 | 139.4 | 98.6 | 89.6 | 117.8 | 149.1 | 217.6
1808 | 1648 | 174.2 | 127.6 | 139.3 | 98.9 | 89.9 | 117.6 | 149 | 217.2
1809 | 1649 | 174 | 127.4 | 139.2 | 99.6 | 90.3 | 117.4 | 149 | 216.8
1810 | 1650 | 173.8 | 127.6 | 139.1 | 99.8 | 90.7 | 117.3 | 149.3 | 216.4
1811 | 1651 | 173.6 | 127.4 | 139 | 99.9 | 90.9 | 117.1 | 149.1 | 215.9
1812 | 1652 | 173.4 | 126.9 | 138.9 | 100.1 | 91.1 | 117 | 148.9 | 215.5
1813 | 1653 | 173.3 | 126.6 | 138.7 | 100.2 | 91.4 | 116.8 | 148.8 | 215.1
1814 | 1654 | 173.1 | 126.8 | 138.5 | 99.9 | 91.4 | 116.6 | 148.5 | 214.7
1815 | 1655 | 172.9 | 126.6 | 138.3 | 99.6 | 91.4 | 116.4 | 148.4 | 214.2
1816 | 1656 | 172.7 | 126 | 138.1 | 98.9 | 91.2 | 116.2 | 148.4 | 213.8
1817 | 1657 | 172.4 | 126 | 137.9 | 98.5 | 90.3 | 116.1 | 148.4 | 213.5
1818 | 1658 | 172.2 | 125.9 | 137.7 | 97.9 | 89.8 | 115.9 | 148.5 | 213.1
1819 | 1659 | 171.9 | 125.3 | 137.4 | 97.6 | 89.4 | 115.7 | 148.4 | 212.8
1820 | 1660 | 171.7 | 124.9 | 137.1 | 97.1 | 89 | 115.6 | 148.4 | 212.4
1821 | 1661 | 171.5 | 124.7 | 136.8 | 96.2 | 88.3 | 115.4 | 148.4 | 212
1822 | 1662 | 171.3 | 125 | 136.6 | 95.4 | 87.5 | 115.2 | 148.1 | 211.7
1823 | 1663 | 171 | 125.3 | 136.5 | 94.7 | 86.8 | 115 | 147.9 | 211.2
1824 | 1664 | 170.8 | 125.7 | 136.1 | 94 | 86 | 114.8 | 147.5 | 210.7
1825 | 1665 | 170.6 | 126.1 | 135.7 | 93.6 | 85.6 | 114.6 | 146.9 | 210.3
1826 | 1666 | 170.4 | 126.5 | 135.4 | 94.1 | 85.2 | 114.4 | 146.5 | 209.9
1827 | 1667 | 170.2 | 126.7 | 135.2 | 94.5 | 84.5 | 114.2 | 146 | 209.4
1828 | 1668 | 169.9 | 126.9 | 134.7 | 94.4 | 84.2 | 114 | 145.5 | 208.9
1829 | 1669 | 169.7 | 127 | 134.5 | 94.1 | 83.8 | 113.8 | 145.1 | 208.4
1830 | 1670 | 169.5 | 127.1 | 134.1 | 94.4 | 83.6 | 113.6 | 144.7 | 208
1831 | 1671 | 169.3 | 127.3 | 133.8 | 94.7 | 83.3 | 113.5 | 144.1 | 207.6
1832 | 1672 | 169.1 | 127.5 | 133.6 | 95.1 | 82.9 | 113.3 | 143.9 | 207.1
1833 | 1673 | 168.8 | 127.6 | 133.4 | 95.1 | 82.2 | 113.1 | 143.7 | 206.6
1834 | 1674 | 168.5 | 127.6 | 133.1 | 94.8 | 82.2 | 112.9 | 143.2 | 206.2
1835 | 1675 | 168.3 | 127.7 | 132.9 | 94.2 | 81.9 | 112.6 | 142.7 | 205.7
1836 | 1676 | 168 | 127.5 | 132.7 | 93.8 | 81.3 | 112.4 | 142.2 | 205.3
1837 | 1677 | 167.8 | 127.5 | 132.4 | 93.5 | 81.2 | 112.2 | 141.5 | 204.8
1838 | 1678 | 167.7 | 127.6 | 132.2 | 93.4 | 81.1 | 111.9 | 141 | 204.4
1839 | 1679 | 167.5 | 127.7 | 131.9 | 93.4 | 81.3 | 111.7 | 140.6 | 203.8
1840 | 1680 | 167.3 | 127.7 | 131.6 | 93.2 | 81.1 | 111.6 | 139.9 | 203.4
1841 | 1681 | 167.1 | 127.5 | 131.4 | 92.9 | 80.9 | 111.3 | 139.4 | 202.9
1842 | 1682 | 166.9 | 127.6 | 131.1 | 92.7 | 80.7 | 111.2 | 139.1 | 202.5
1843 | 1683 | 166.7 | 127.7 | 130.8 | 92.6 | 80.8 | 111 | 138.6 | 202
1844 | 1684 | 166.5 | 127.6 | 130.6 | 92.4 | 80.5 | 110.8 | 138.2 | 201.5
1845 | 1685 | 166.2 | 127.3 | 130.4 | 92 | 80.3 | 110.7 | 137.8 | 201.1
1846 | 1686 | 165.9 | 127.2 | 130.2 | 91.9 | 80.2 | 110.5 | 137.5 | 200.6
1847 | 1687 | 165.7 | 127.1 | 130 | 92.1 | 80 | 110.4 | 137.1 | 200.2
1848 | 1688 | 165.5 | 127 | 129.8 | 91.5 | 79.5 | 110.3 | 136.7 | 199.8
1849 | 1689 | 165.2 | 126.8 | 129.6 | 90.8 | 79 | 110.1 | 136.3 | 199.4
1850 | 1690 | 165 | 126.7 | 129.4 | 90.2 | 79 | 109.9 | 136 | 199.1
1851 | 1691 | 164.8 | 126.8 | 129.2 | 89.7 | 79.1 | 109.7 | 135.6 | 198.7
1852 | 1692 | 164.5 | 126.8 | 128.8 | 89.2 | 79.3 | 109.4 | 135.1 | 198.3
1853 | 1693 | 164.3 | 126.8 | 128.6 | 88.6 | 79.2 | 109.1 | 134.7 | 197.9
1854 | 1694 | 164.1 | 126.7 | 128.4 | 88.5 | 78.5 | 108.9 | 134.3 | 197.4
1855 | 1695 | 164 | 126.8 | 128.1 | 89.1 | 77.7 | 108.7 | 133.8 | 197
1856 | 1696 | 163.8 | 126.8 | 127.8 | 89.2 | 77.2 | 108.5 | 133.1 | 196.5
1857 | 1697 | 163.5 | 126.7 | 127.6 | 88.8 | 77.2 | 108.3 | 132.8 | 196
1858 | 1698 | 163.3 | 126.2 | 127.3 | 88.3 | 77.1 | 108.1 | 132.5 | 195.6
1859 | 1699 | 163.1 | 125.6 | 127.1 | 87.7 | 77.2 | 107.9 | 132.3 | 195.1
1860 | 1700 | 162.9 | 125.3 | 126.9 | 87.8 | 77.4 | 107.7 | 132 | 194.7
1861 | 1701 | 162.7 | 125 | 126.8 | 87.9 | 77.3 | 107.6 | 131.6 | 194.3
1862 | 1702 | 162.5 | 124.5 | 126.6 | 88.1 | 77.4 | 107.4 | 131.1 | 193.9
1863 | 1703 | 162.3 | 124.4 | 126.4 | 88.5 | 77.3 | 107.2 | 130.7 | 193.3
1864 | 1704 | 162.1 | 124.3 | 126.3 | 89 | 76.9 | 107 | 130.2 | 192.9
1865 | 1705 | 161.9 | 124.2 | 126.1 | 89.1 | 76.6 | 106.9 | 130 | 192.5
1866 | 1706 | 161.8 | 124.1 | 126 | 89.2 | 76.6 | 106.8 | 129.7 | 192.1
1867 | 1707 | 161.5 | 123.5 | 125.9 | 88.9 | 76.6 | 106.7 | 129.2 | 191.6
1868 | 1708 | 161.3 | 122.9 | 125.8 | 88.7 | 76.3 | 106.6 | 128.8 | 191.2
1869 | 1709 | 161.1 | 122.2 | 125.6 | 88.2 | 76.1 | 106.5 | 128.5 | 190.9
1870 | 1710 | 160.9 | 122 | 125.4 | 87.6 | 75.6 | 106.4 | 128.1 | 190.5
1871 | 1711 | 160.8 | 122.3 | 125.3 | 87.3 | 75.3 | 106.3 | 127.8 | 190.1
1872 | 1712 | 160.6 | 122.4 | 125.2 | 87.2 | 75 | 106.1 | 127.3 | 189.7
1873 | 1713 | 160.4 | 122.4 | 125 | 87.6 | 74.4 | 106 | 126.7 | 189.3
1874 | 1714 | 160.3 | 122.4 | 124.9 | 88.1 | 74.4 | 105.8 | 126.4 | 188.9
1875 | 1715 | 160.1 | 122.2 | 124.7 | 88.2 | 74.5 | 105.6 | 126.2 | 188.5
1876 | 1716 | 159.8 | 121.3 | 124.5 | 88.2 | 74.6 | 105.4 | 125.9 | 188.1
1877 | 1717 | 159.6 | 120.3 | 124.3 | 87.9 | 74.5 | 105.2 | 125.8 | 187.7
1878 | 1718 | 159.3 | 120.1 | 124.2 | 87.2 | 74.5 | 105 | 125.7 | 187.3
1879 | 1719 | 159.2 | 120.1 | 124 | 86.4 | 74.6 | 104.8 | 125.4 | 186.9
1880 | 1720 | 159.1 | 120 | 123.9 | 85.9 | 74.4 | 104.6 | 125.1 | 186.5
1881 | 1721 | 158.9 | 119.5 | 123.7 | 85.3 | 74.2 | 104.5 | 124.7 | 186.1
1882 | 1722 | 158.8 | 119 | 123.6 | 85.1 | 74.1 | 104.4 | 124.3 | 185.6
1883 | 1723 | 158.6 | 118.9 | 123.4 | 85.1 | 73.9 | 104.2 | 124 | 185.3
1884 | 1724 | 158.4 | 118.9 | 123.2 | 84.8 | 73.8 | 104.1 | 123.7 | 184.9
1885 | 1725 | 158.1 | 118.7 | 123 | 84.4 | 73.5 | 104.1 | 123.5 | 184.5
1886 | 1726 | 157.9 | 118.2 | 122.8 | 84.3 | 73.3 | 104 | 123.2 | 184.1
1887 | 1727 | 157.6 | 117.8 | 122.6 | 84.4 | 73 | 103.9 | 122.8 | 183.8
1888 | 1728 | 157.4 | 117.4 | 122.5 | 84.6 | 72.9 | 103.7 | 122.4 | 183.3
1889 | 1729 | 157.1 | 117.4 | 122.3 | 85.2 | 72.6 | 103.6 | 122.2 | 182.9
1890 | 1730 | 156.9 | 117.2 | 122.1 | 85.5 | 72.2 | 103.5 | 122 | 182.5
1891 | 1731 | 156.7 | 117 | 122 | 85.6 | 72.2 | 103.3 | 121.8 | 182.2
1892 | 1732 | 156.5 | 116.9 | 121.9 | 85.9 | 72 | 103.2 | 121.6 | 181.9
1893 | 1733 | 156.3 | 117 | 121.8 | 86.2 | 71.9 | 103 | 121.3 | 181.4
1894 | 1734 | 156.2 | 116.5 | 121.6 | 86.1 | 71.7 | 102.9 | 121.3 | 181.1
1895 | 1735 | 156 | 115.9 | 121.4 | 85.5 | 71.5 | 102.8 | 121.1 | 180.8
1896 | 1736 | 155.9 | 115.1 | 121.2 | 84.8 | 71 | 102.6 | 120.9 | 180.4
1897 | 1737 | 155.7 | 115.2 | 121.1 | 84.4 | 70.8 | 102.5 | 120.5 | 180.1
1898 | 1738 | 155.5 | 115 | 120.9 | 83.9 | 71.2 | 102.3 | 120.2 | 179.8
1899 | 1739 | 155.3 | 114.5 | 120.8 | 83.7 | 71.3 | 102.2 | 119.9 | 179.4
1900 | 1740 | 155.1 | 113.9 | 120.7 | 84.2 | 71.2 | 102.1 | 119.6 | 179
1901 | 1741 | 155 | 113.6 | 120.5 | 84.3 | 71.4 | 102 | 119.4 | 178.7
1902 | 1742 | 154.8 | 113.3 | 120.4 | 84.3 | 72.2 | 101.8 | 119.2 | 178.4
1903 | 1743 | 154.7 | 113.1 | 120.4 | 84.4 | 73.1 | 101.7 | 119.2 | 178
1904 | 1744 | 154.6 | 113.1 | 120.3 | 84.6 | 73.7 | 101.6 | 119.1 | 177.6
1905 | 1745 | 154.5 | 112.9 | 120.2 | 85.1 | 74.9 | 101.4 | 118.9 | 177.3
1906 | 1746 | 154.3 | 112.7 | 120 | 85.6 | 75.4 | 101.3 | 118.7 | 177
1907 | 1747 | 154 | 112.5 | 119.9 | 85.7 | 76 | 101.2 | 118.5 | 176.6
1908 | 1748 | 153.8 | 112.3 | 119.7 | 85.6 | 76.4 | 101.1 | 118.4 | 176.3
1909 | 1749 | 153.6 | 112.3 | 119.5 | 85.6 | 76.8 | 101 | 118.2 | 176
1910 | 1750 | 153.5 | 112.2 | 119.4 | 85.9 | 77.6 | 100.8 | 118.1 | 175.7
1911 | 1751 | 153.4 | 112.1 | 119.3 | 86.1 | 78.4 | 100.7 | 118 | 175.4
1912 | 1752 | 153.3 | 111.6 | 119 | 85.9 | 78.8 | 100.6 | 117.8 | 175
1913 | 1753 | 153.2 | 111 | 118.8 | 85.6 | 79.1 | 100.4 | 117.5 | 174.7
1914 | 1754 | 153 | 110.4 | 118.6 | 85.5 | 79.2 | 100.3 | 117.3 | 174.4
1915 | 1755 | 152.9 | 110.2 | 118.4 | 85.5 | 79.5 | 100.2 | 117.2 | 174.1
1916 | 1756 | 152.6 | 110.1 | 118.3 | 85.6 | 79.9 | 100.1 | 117 | 173.8
1917 | 1757 | 152.4 | 110 | 118.1 | 85.5 | 80.1 | 100 | 116.8 | 173.6
1918 | 1758 | 152.2 | 110.2 | 118 | 85.6 | 80.3 | 99.8 | 116.8 | 173.2
1919 | 1759 | 152.1 | 110.5 | 117.8 | 85.9 | 81 | 99.7 | 116.6 | 173
1920 | 1760 | 151.9 | 110.8 | 117.6 | 86.3 | 81.2 | 99.5 | 116.4 | 172.7
1921 | 1761 | 151.6 | 111 | 117.5 | 86.4 | 81.7 | 99.4 | 116.1 | 172.4
1922 | 1762 | 151.4 | 111 | 117.3 | 86.4 | 81.9 | 99.2 | 116 | 172.1
1923 | 1763 | 151.2 | 110.8 | 117.2 | 86.7 | 82.1 | 99 | 115.8 | 171.9
1924 | 1764 | 151 | 110.3 | 117 | 86.9 | 81.5 | 98.9 | 115.7 | 171.6
1925 | 1765 | 150.8 | 109.9 | 116.9 | 87.4 | 81.6 | 98.7 | 115.5 | 171.4
1926 | 1766 | 150.6 | 109.5 | 116.7 | 88 | 82 | 98.5 | 115.2 | 171.1
1927 | 1767 | 150.5 | 109 | 116.6 | 88.2 | 82.3 | 98.3 | 115.1 | 170.7
1928 | 1768 | 150.4 | 108.5 | 116.5 | 88.1 | 82.6 | 98.1 | 115 | 170.5
1929 | 1769 | 150.2 | 108 | 116.4 | 88.1 | 82.9 | 98 | 114.7 | 170.2
1930 | 1770 | 150 | 107.7 | 116.3 | 87.9 | 83.2 | 97.8 | 114.5 | 169.9
1931 | 1771 | 149.9 | 107.9 | 116.2 | 87.7 | 82.7 | 97.7 | 114.3 | 169.6
1932 | 1772 | 149.7 | 108.1 | 116.1 | 87.4 | 82.2 | 97.5 | 114.1 | 169.3
1933 | 1773 | 149.5 | 107.9 | 116.1 | 87.4 | 82.5 | 97.3 | 114 | 169.1
1934 | 1774 | 149.3 | 107.9 | 116 | 87.5 | 83.1 | 97.1 | 113.8 | 168.8
1935 | 1775 | 149.1 | 107.7 | 115.9 | 87.5 | 83.2 | 97 | 113.5 | 168.4
1936 | 1776 | 148.9 | 107.4 | 115.8 | 87.4 | 83.8 | 96.8 | 113.4 | 168.1
1937 | 1777 | 148.7 | 107 | 115.7 | 87.1 | 84.1 | 96.6 | 113.2 | 167.8
1938 | 1778 | 148.5 | 106.6 | 115.6 | 86.7 | 84.1 | 96.3 | 113 | 167.4
1939 | 1779 | 148.3 | 106.4 | 115.4 | 86.5 | 83.7 | 96.1 | 112.8 | 167.1
1940 | 1780 | 148.1 | 106.3 | 115.3 | 86.2 | 83.4 | 95.9 | 112.6 | 166.8
1941 | 1781 | 148 | 106.3 | 115.2 | 86 | 83.1 | 95.7 | 112.4 | 166.5
1942 | 1782 | 147.8 | 106.1 | 115.1 | 85.7 | 83.2 | 95.5 | 112.3 | 166.2
1943 | 1783 | 147.7 | 105.8 | 115 | 85.5 | 83 | 95.3 | 112.1 | 166
1944 | 1784 | 147.6 | 105.3 | 114.9 | 85.5 | 82.7 | 95.2 | 112.1 | 165.7
1945 | 1785 | 147.4 | 105.3 | 114.8 | 85.8 | 82.8 | 95 | 111.8 | 165.5
1946 | 1786 | 147.2 | 105.1 | 114.7 | 85.9 | 82.8 | 94.8 | 111.5 | 165.2
1947 | 1787 | 147 | 104.7 | 114.6 | 85.8 | 82.8 | 94.7 | 111.3 | 165
1948 | 1788 | 146.8 | 104.6 | 114.5 | 85.8 | 83.5 | 94.5 | 111.2 | 164.7
1949 | 1789 | 146.7 | 104.9 | 114.4 | 86.2 | 84.1 | 94.3 | 111.1 | 164.4
1950 | 1790 | 146.6 | 104.9 | 114.2 | 86.5 | 84.6 | 94.2 | 110.9 | 164.2
1951 | 1791 | 146.4 | 104.3 | 114.1 | 86.7 | 84.3 | 94.1 | 110.7 | 164
1952 | 1792 | 146.2 | 103.9 | 114 | 86.9 | 83.9 | 94 | 110.4 | 163.8
1953 | 1793 | 146.1 | 103.6 | 113.9 | 86.9 | 83.3 | 93.9 | 110.3 | 163.5
1954 | 1794 | 145.9 | 103.2 | 113.8 | 87.1 | 83 | 93.8 | 110.1 | 163.3
1955 | 1795 | 145.7 | 103 | 113.6 | 87.5 | 83.3 | 93.7 | 109.9 | 163.1
1956 | 1796 | 145.5 | 102.8 | 113.5 | 87.5 | 82.9 | 93.5 | 109.9 | 162.8
1957 | 1797 | 145.4 | 102.9 | 113.4 | 87.3 | 82.7 | 93.3 | 109.9 | 162.5
1958 | 1798 | 145.2 | 103 | 113.3 | 87.5 | 82.6 | 93.1 | 109.7 | 162.3
1959 | 1799 | 145.1 | 102.8 | 113.2 | 87.8 | 82.6 | 93 | 109.4 | 162.1
1960 | 1800 | 144.9 | 102.2 | 113 | 87.9 | 82.4 | 92.8 | 109.3 | 161.8
1961 | 1801 | 144.8 | 102.1 | 112.9 | 87.9 | 82.8 | 92.6 | 109.2 | 161.4
1962 | 1802 | 144.6 | 101.8 | 112.8 | 88.1 | 82.8 | 92.4 | 109.1 | 161.2
1963 | 1803 | 144.4 | 101.3 | 112.7 | 88.4 | 83.2 | 92.2 | 109.1 | 161
1964 | 1804 | 144.3 | 101.1 | 112.5 | 88.8 | 83.4 | 92 | 109 | 160.8
1965 | 1805 | 144.1 | 101.5 | 112.2 | 89.2 | 83.2 | 91.9 | 108.9 | 160.5
1966 | 1806 | 144 | 101.9 | 112.1 | 89.4 | 83.1 | 91.7 | 108.8 | 160.3
1967 | 1807 | 143.8 | 102 | 111.9 | 89.3 | 83.1 | 91.6 | 108.7 | 160
1968 | 1808 | 143.6 | 101.8 | 111.8 | 89.2 | 83.3 | 91.5 | 108.6 | 159.8
1969 | 1809 | 143.5 | 101.8 | 111.5 | 88.9 | 83.5 | 91.4 | 108.6 | 159.6
1970 | 1810 | 143.2 | 102 | 111.3 | 89 | 83.5 | 91.2 | 108.5 | 159.3
1971 | 1811 | 143 | 101.9 | 111.1 | 89.3 | 83.5 | 91.1 | 108.4 | 158.9
1972 | 1812 | 142.8 | 102 | 110.8 | 89.4 | 83.4 | 90.9 | 108.3 | 158.6
1973 | 1813 | 142.7 | 101.9 | 110.7 | 89.1 | 83.3 | 90.8 | 108.2 | 158.4
1974 | 1814 | 142.5 | 102.2 | 110.5 | 88.7 | 83.2 | 90.6 | 108.1 | 158.1
1975 | 1815 | 142.3 | 102.4 | 110.3 | 88.3 | 83.4 | 90.5 | 107.9 | 157.8
1976 | 1816 | 142.1 | 102.6 | 109.9 | 88 | 83.6 | 90.4 | 107.8 | 157.6
1977 | 1817 | 141.9 | 102.7 | 109.7 | 87.6 | 83 | 90.2 | 107.6 | 157.4
1978 | 1818 | 141.8 | 102.6 | 109.5 | 87.1 | 83.1 | 90.1 | 107.6 | 157.1
1979 | 1819 | 141.6 | 102.5 | 109.1 | 86.8 | 83.3 | 89.9 | 107.4 | 156.9
1980 | 1820 | 141.4 | 102.3 | 108.9 | 86.5 | 83.1 | 89.7 | 107.3 | 156.6
1981 | 1821 | 141.2 | 102.1 | 108.7 | 86.3 | 82.6 | 89.5 | 107.2 | 156.4
1982 | 1822 | 141 | 102.1 | 108.5 | 86.1 | 82.6 | 89.4 | 107.1 | 156.1
1983 | 1823 | 140.8 | 101.8 | 108.3 | 85.7 | 82.5 | 89.2 | 106.9 | 155.9
1984 | 1824 | 140.6 | 101.5 | 108.1 | 85.3 | 82.2 | 89 | 106.7 | 155.7
1985 | 1825 | 140.4 | 101.2 | 108 | 84.7 | 82.3 | 88.8 | 106.5 | 155.4
1986 | 1826 | 140.2 | 100.6 | 107.7 | 84.1 | 82 | 88.7 | 106.2 | 155.2
1987 | 1827 | 140.1 | 99.8 | 107.6 | 83.5 | 81.7 | 88.5 | 106 | 155
1988 | 1828 | 140 | 99.2 | 107.4 | 83 | 81.2 | 88.4 | 105.8 | 154.7
1989 | 1829 | 139.8 | 98.7 | 107.3 | 82.6 | 80.9 | 88.2 | 105.5 | 154.5
1990 | 1830 | 139.6 | 98.2 | 107.1 | 82.2 | 80.6 | 88.1 | 105.2 | 154.3
1991 | 1831 | 139.4 | 97.8 | 107 | 81.8 | 80.2 | 88 | 104.9 | 154.1
1992 | 1832 | 139.3 | 97.4 | 107 | 81.7 | 80 | 87.9 | 104.6 | 153.9
1993 | 1833 | 139.1 | 97.1 | 107 | 81.6 | 79.6 | 87.7 | 104.4 | 153.6
1994 | 1834 | 138.9 | 96.8 | 106.9 | 81.4 | 79.1 | 87.6 | 104.1 | 153.4
1995 | 1835 | 138.7 | 96.5 | 106.8 | 81.3 | 78.7 | 87.5 | 103.8 | 153
1996 | 1836 | 138.5 | 96.3 | 106.7 | 81.2 | 78.4 | 87.4 | 103.5 | 152.7
1997 | 1837 | 138.3 | 96.1 | 106.6 | 80.8 | 78.1 | 87.3 | 103.2 | 152.4
1998 | 1838 | 138.1 | 95.8 | 106.4 | 80.5 | 77.7 | 87.2 | 102.9 | 152.2
1999 | 1839 | 137.9 | 95.6 | 106.2 | 80.2 | 77.5 | 87.1 | 102.6 | 152
2000 | 1840 | 137.7 | 95.4 | 106.1 | 79.9 | 77.1 | 86.9 | 102.4 | 151.8
2001 | 1841 | 137.6 | 95.2 | 106 | 79.5 | 76.8 | 86.8 | 102.1 | 151.6
2002 | 1842 | 137.4 | 94.9 | 105.8 | 79.2 | 76.9 | 86.7 | 101.9 | 151.4
2003 | 1843 | 137.2 | 94.5 | 105.6 | 78.9 | 76.5 | 86.6 | 101.8 | 151.2
2004 | 1844 | 137 | 94.2 | 105.5 | 78.5 | 76 | 86.5 | 101.6 | 150.9
2005 | 1845 | 136.9 | 94.2 | 105.4 | 78.4 | 75.7 | 86.4 | 101.4 | 150.8
2006 | 1846 | 136.7 | 94.2 | 105.3 | 78.2 | 75.4 | 86.3 | 101.2 | 150.5
2007 | 1847 | 136.6 | 94.1 | 105.2 | 77.9 | 74.9 | 86.2 | 101 | 150.3
2008 | 1848 | 136.4 | 94.1 | 105 | 77.4 | 74.3 | 86.1 | 100.7 | 150.1
2009 | 1849 | 136.4 | 94.4 | 104.9 | 77.1 | 73.6 | 86 | 100.6 | 149.9
2010 | 1850 | 136.2 | 94.6 | 104.7 | 77.1 | 73.7 | 85.9 | 100.4 | 149.7
2011 | 1851 | 136.1 | 94.5 | 104.5 | 77.3 | 74.4 | 85.8 | 100.2 | 149.5
2012 | 1852 | 135.9 | 94.5 | 104.4 | 77.4 | 74.8 | 85.7 | 100.2 | 149.3
2013 | 1853 | 135.8 | 94.8 | 104.2 | 77.8 | 75.6 | 85.6 | 100 | 149.1
2014 | 1854 | 135.6 | 94.7 | 104 | 78.4 | 75.7 | 85.5 | 99.7 | 148.8
2015 | 1855 | 135.4 | 94.5 | 103.9 | 78.6 | 75.7 | 85.4 | 99.6 | 148.6
2016 | 1856 | 135.3 | 94.5 | 103.7 | 78.6 | 76.3 | 85.3 | 99.4 | 148.3
2017 | 1857 | 135.1 | 94.4 | 103.5 | 78.5 | 76.7 | 85.2 | 99.3 | 148
2018 | 1858 | 134.9 | 94.3 | 103.3 | 78.6 | 76.6 | 85.2 | 99.1 | 147.9
2019 | 1859 | 134.7 | 94.2 | 103.2 | 78.5 | 76.6 | 85.1 | 99 | 147.7
2020 | 1860 | 134.6 | 94.2 | 103.1 | 78.4 | 76.9 | 85 | 98.9 | 147.5
2021 | 1861 | 134.4 | 94 | 102.9 | 78.3 | 77.2 | 84.8 | 98.7 | 147.2
2022 | 1862 | 134.3 | 94 | 102.8 | 78.5 | 77.5 | 84.7 | 98.6 | 147
2023 | 1863 | 134.1 | 94.1 | 102.7 | 78.6 | 77.7 | 84.5 | 98.4 | 146.7
2024 | 1864 | 134 | 94.1 | 102.5 | 79.1 | 77.9 | 84.4 | 98.2 | 146.6
2025 | 1865 | 133.8 | 93.8 | 102.4 | 79.3 | 78 | 84.2 | 98 | 146.4
2026 | 1866 | 133.6 | 93.7 | 102.3 | 79.6 | 78.2 | 84 | 97.8 | 146.2
2027 | 1867 | 133.4 | 93.5 | 102.1 | 79.8 | 78.4 | 83.8 | 97.7 | 146
2028 | 1868 | 133.2 | 93.5 | 102 | 79.9 | 78.4 | 83.5 | 97.6 | 145.8
2029 | 1869 | 133.1 | 93.5 | 101.8 | 79.9 | 78.7 | 83.3 | 97.6 | 145.6

## Test Facts
Last row in IRMS data sheets: | 16
Time when Penlight power was initiated: | 160