## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 61
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, PVC jacketed ("TS/TP") control cables (cable item #3). Cable specimens present: Three lengths of cable were monitored for electrical performance, a fourth length of cable was monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using six channels - two for each cable (see electrical connection map), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures and six cable temperatures (see thermocouple map). Shroud power: Initiated after 98 seconds of baseline data monitoring. Special Note: Test setup included three thermocouples on the outer surface of the conduit.
DAQ Time | Penlight Time | Event | Interpretation
98 | 0 | Initated Penlight Heating
1639 | 1541 | Conductors A1 & A2 short together at less than 100 ohms (44) | Cable A is shorted internally
1645-1654 | 1547-1556 | Conductors A1 & A2 both short to ground intermittently at less than 1000 ohms (490 & 355) | Cable A shorts to ground (intermittent)
1833-1835 | 1735-1737 | Conductors C5 & C6 both short to ground at less than 100 ohms (23 & 36) | Cable C shorts to ground
1846 | 1748 | Conductors C5 & C6 short together at less than 100 ohms (27) | Cable C is shorted internally
1995-1998 | 1897-1900 | Conductors B3 & B4 short to ground intermittently at less than 1000 ohms (195 & 206) | Cable B shorts to ground (intermittent)
2000 | 1902 | Conductors B3 & B4 short together at less than 100 ohms (2) | Cable B is shorted internally
2023-2032 | 1925-1934 | Conductors A1 & A2 both short to ground at less than 100 ohms (6 & 7) | Cable A shorts to ground
2040 | 1942 | Conductor B4 shorts to ground at less than 100 ohms (4) | Cable B partially shorted to ground
2415 | 2317 | Conductor B3 shorts to ground at less than 1000 ohms (373) | Cable B shorts to ground
2844 | 2746 | Power to Penlight shutoff
Additional Observations
Observation 1 | Cable ground failures were initially intermittent in nature then progressed to "steady state" failure conditions
Observation 2 | It took 1541 seconds (25.7 min.) from the start of Penlight heating for the first internal short to occur, and it took 1547 s (25.8 min.) for the first short to ground failure.
Observation 3 | No cable to cable interations occurred prior to one or both cables shorting to ground or internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable and conduit
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Outer surface of conduit
| TC2 | = | Conduit 2 | Outer surface of conduit at mid-point
| TC3 | = | Conduit 3 | Outer surface of conduit
| TC4 | = | Cable 1 | Within cable just below cable jacket, center position
| TC5 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC6 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC7 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC8 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC9 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
Cables A, B & C = XLPE/PVC (item #3, "TS/TP")
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 61 |  |  | 2006-09-01 | 12:30
TS/TP | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | C5-C6 | Penlight Time | Minimums
-97 | 246337.9994 | -94 | 240837.9994 | -91.5 | 246037.9994 | -88.5 | 248437.9994 | -85.5 | 248537.9994 | -83 | 247537.9994 | -80 | 248837.9994 | -77 | 249737.9994 | -74.5 | 249637.9994 | -71.5 | 232337.9994 | -69 | 245237.9994 | -66 | 244237.9994 | -63 | 245137.9994 | -60.5 | 248137.9994 | -57.5 | 248737.9994 | -97 | 232337.9994
-54.5 | 246337.9994 | -52 | 240837.9994 | -49 | 246037.9994 | -46.5 | 248437.9994 | -43.5 | 248537.9994 | -41 | 123718.9988 | -38 | 248837.9994 | -35.5 | 249737.9994 | -32.5 | 249637.9994 | -29.5 | 232337.9994 | -27 | 245237.9994 | -24 | 244237.9994 | -21.5 | 245137.9994 | -18.5 | 248137.9994 | -15.5 | 248737.9994 | -54.5 | 123718.9988
-13 | 246337.9994 | -10 | 240837.9994 | -7.5 | 246037.9994 | -4.5 | 62034.4976 | -1.5 | 248537.9994 | 1 | 247537.9994 | 4 | 248837.9994 | 6.5 | 249737.9994 | 9.5 | 249637.9994 | 12.5 | 232337.9994 | 15.5 | 245237.9994 | 18 | 244237.9994 | 20.5 | 245137.9994 | 23.5 | 248137.9994 | 26.5 | 248737.9994 | -13 | 62034.4976
29 | 246337.9994 | 32 | 240837.9994 | 34.5 | 246037.9994 | 37.5 | 248437.9994 | 40.5 | 248537.9994 | 43 | 247537.9994 | 46 | 248837.9994 | 48.5 | 249737.9994 | 51.5 | 249637.9994 | 54.5 | 232337.9994 | 57.5 | 245237.9994 | 60 | 244237.9994 | 63 | 245137.9994 | 65.5 | 248137.9994 | 68.5 | 248737.9994 | 29 | 232337.9994
71.5 | 246337.9994 | 74 | 240837.9994 | 77 | 246037.9994 | 79.5 | 124168.9988 | 82.5 | 248537.9994 | 85 | 247537.9994 | 88 | 248837.9994 | 90.5 | 249737.9994 | 93.5 | 249637.9994 | 96.5 | 232337.9994 | 99 | 245237.9994 | 102 | 244237.9994 | 104.5 | 245137.9994 | 107.5 | 248137.9994 | 110.5 | 248737.9994 | 71.5 | 124168.9988
113 | 246337.9994 | 116 | 240837.9994 | 118.5 | 246037.9994 | 121.5 | 248437.9994 | 124.5 | 248537.9994 | 127 | 247537.9994 | 130 | 248837.9994 | 132.5 | 249737.9994 | 135.5 | 249637.9994 | 138.5 | 232337.9994 | 141 | 245237.9994 | 144 | 244237.9994 | 146.5 | 245137.9994 | 149.5 | 248137.9994 | 152.5 | 248737.9994 | 113 | 232337.9994
155 | 246337.9994 | 158 | 240837.9994 | 160.5 | 246037.9994 | 163.5 | 248437.9994 | 166.5 | 248537.9994 | 169 | 247537.9994 | 172 | 248837.9994 | 175 | 249737.9994 | 177.5 | 249637.9994 | 180.5 | 232337.9994 | 183 | 245237.9994 | 186 | 244237.9994 | 188.5 | 245137.9994 | 191.5 | 248137.9994 | 194.5 | 248737.9994 | 155 | 232337.9994
197 | 246337.9994 | 200 | 240837.9994 | 202.5 | 246037.9994 | 205.5 | 248437.9994 | 208.5 | 248537.9994 | 211 | 247537.9994 | 214 | 248837.9994 | 216.5 | 249737.9994 | 219.5 | 249637.9994 | 222.5 | 232337.9994 | 225 | 245237.9994 | 228 | 244237.9994 | 230.5 | 245137.9994 | 233.5 | 247938.0806 | 236.5 | 248737.9994 | 197 | 232337.9994
239 | 246337.9994 | 242 | 240837.9994 | 244.5 | 246037.9994 | 247.5 | 248437.9994 | 250.5 | 248537.9994 | 253 | 247537.9994 | 256 | 248837.9994 | 258.5 | 249737.9994 | 261.5 | 249637.9994 | 264.5 | 232337.9994 | 267 | 245237.9994 | 270 | 244237.9994 | 272.5 | 245137.9994 | 275.5 | 248137.9994 | 278.5 | 248737.9994 | 239 | 232337.9994
281 | 246337.9994 | 284 | 240837.9994 | 286.5 | 246037.9994 | 289.5 | 248437.9994 | 292.5 | 248537.9994 | 295 | 247537.9994 | 298 | 248837.9994 | 300.5 | 249737.9994 | 303.5 | 249637.9994 | 306.5 | 232337.9994 | 309 | 245237.9994 | 312 | 244237.9994 | 314.5 | 245137.9994 | 317.5 | 248137.9994 | 320.5 | 248737.9994 | 281 | 232337.9994
323 | 246337.9994 | 326 | 240837.9994 | 328.5 | 246037.9994 | 331.5 | 248437.9994 | 334.5 | 248537.9994 | 337 | 247537.9994 | 340 | 248837.9994 | 342.5 | 249737.9994 | 345.5 | 249637.9994 | 348.5 | 232337.9994 | 351 | 245237.9994 | 354 | 244237.9994 | 356.5 | 245137.9994 | 359.5 | 248137.9994 | 362.5 | 248538.0804 | 323 | 232337.9994
365 | 246337.9994 | 368 | 240837.9994 | 370.5 | 246037.9994 | 373.5 | 248437.9994 | 376.5 | 248537.9994 | 379 | 247537.9994 | 382 | 248837.9994 | 384.5 | 249737.9994 | 387.5 | 249637.9994 | 390.5 | 232337.9994 | 393 | 245237.9994 | 396 | 244237.9994 | 398.5 | 245137.9994 | 401.5 | 248137.9994 | 404.5 | 248737.9994 | 365 | 232337.9994
407 | 246337.9994 | 410 | 240837.9994 | 412.5 | 246037.9994 | 415.5 | 248437.9994 | 418.5 | 248537.9994 | 421 | 247537.9994 | 424 | 248837.9994 | 426.5 | 249737.9994 | 429.5 | 249637.9994 | 432.5 | 232337.9994 | 435 | 245237.9994 | 438 | 244237.9994 | 440.5 | 245137.9994 | 443.5 | 248137.9994 | 446.5 | 248737.9994 | 407 | 232337.9994
449 | 246337.9994 | 452 | 240837.9994 | 454.5 | 246037.9994 | 457.5 | 248437.9994 | 460.5 | 248537.9994 | 463 | 247537.9994 | 466 | 248837.9994 | 468.5 | 249737.9994 | 471.5 | 249637.9994 | 474.5 | 232337.9994 | 477 | 245237.9994 | 480 | 244237.9994 | 482.5 | 245137.9994 | 485.5 | 248137.9994 | 488.5 | 248737.9994 | 449 | 232337.9994
491 | 246337.9994 | 494 | 240837.9994 | 496.5 | 246037.9994 | 499.5 | 248437.9994 | 502.5 | 248537.9994 | 505 | 247537.9994 | 508 | 248837.9994 | 510.5 | 249737.9994 | 513.5 | 249637.9994 | 516.5 | 232337.9994 | 519 | 245237.9994 | 522 | 244237.9994 | 524.5 | 245137.9994 | 527.5 | 248137.9994 | 530.5 | 248737.9994 | 491 | 232337.9994
533 | 246337.9994 | 536 | 240837.9994 | 538.5 | 246037.9994 | 541.5 | 248437.9994 | 544.5 | 248537.9994 | 547 | 247537.9994 | 550 | 248837.9994 | 552.5 | 249737.9994 | 555.5 | 249637.9994 | 558.5 | 232337.9994 | 561 | 245237.9994 | 564 | 244237.9994 | 566.5 | 245137.9994 | 569.5 | 248137.9994 | 572.5 | 248737.9994 | 533 | 232337.9994
575 | 246337.9994 | 578 | 240837.9994 | 580.5 | 246037.9994 | 583.5 | 248437.9994 | 586.5 | 248537.9994 | 589 | 247537.9994 | 592 | 248837.9994 | 594.5 | 249737.9994 | 597.5 | 249637.9994 | 600.5 | 232337.9994 | 603 | 245237.9994 | 606 | 244237.9994 | 608.5 | 245137.9994 | 611.5 | 248137.9994 | 614.5 | 248737.9994 | 575 | 232337.9994
617 | 246337.9994 | 620 | 240837.9994 | 622.5 | 246037.9994 | 625.5 | 248437.9994 | 628.5 | 248537.9994 | 631 | 247537.9994 | 634 | 248837.9994 | 636.5 | 249737.9994 | 639.5 | 249637.9994 | 642.5 | 232337.9994 | 645 | 245237.9994 | 648 | 244237.9994 | 650.5 | 245137.9994 | 653.5 | 248137.9994 | 656.5 | 248737.9994 | 617 | 232337.9994
659 | 246337.9994 | 662 | 240837.9994 | 664.5 | 246037.9994 | 667.5 | 248437.9994 | 670.5 | 248537.9994 | 673 | 247537.9994 | 676 | 248837.9994 | 678.5 | 249737.9994 | 681.5 | 249637.9994 | 684.5 | 232337.9994 | 687 | 245237.9994 | 690 | 244237.9994 | 692.5 | 245137.9994 | 695.5 | 248137.9994 | 698.5 | 248737.9994 | 659 | 232337.9994
701 | 246337.9994 | 704 | 240837.9994 | 706.5 | 246037.9994 | 709.5 | 248437.9994 | 712.5 | 248537.9994 | 715 | 247537.9994 | 718 | 248837.9994 | 720.5 | 249737.9994 | 723.5 | 249637.9994 | 726.5 | 232337.9994 | 729 | 245237.9994 | 732 | 244237.9994 | 734.5 | 245137.9994 | 737.5 | 248137.9994 | 740.5 | 248737.9994 | 701 | 232337.9994
743 | 246337.9994 | 746 | 240837.9994 | 748.5 | 246037.9994 | 751.5 | 248437.9994 | 754.5 | 248537.9994 | 757 | 247537.9994 | 760 | 248837.9994 | 762.5 | 249737.9994 | 765.5 | 249637.9994 | 768.5 | 232337.9994 | 771 | 245237.9994 | 774 | 244237.9994 | 776.5 | 245137.9994 | 779.5 | 248137.9994 | 782.5 | 248737.9994 | 743 | 232337.9994
785 | 246337.9994 | 788 | 240837.9994 | 790.5 | 246037.9994 | 793.5 | 248437.9994 | 796.5 | 248537.9994 | 799 | 247537.9994 | 801.5 | 248837.9994 | 804.5 | 249737.9994 | 807.5 | 249637.9994 | 810.5 | 232337.9994 | 813 | 245237.9994 | 816 | 244237.9994 | 818.5 | 245137.9994 | 821.5 | 248137.9994 | 824 | 248737.9994 | 785 | 232337.9994
827 | 246337.9994 | 829.5 | 240837.9994 | 832.5 | 246037.9994 | 835.5 | 248437.9994 | 838 | 248537.9994 | 841 | 247537.9994 | 844 | 248837.9994 | 846.5 | 249737.9994 | 849.5 | 249637.9994 | 852 | 232337.9994 | 855 | 245237.9994 | 858 | 244237.9994 | 860.5 | 245137.9994 | 863.5 | 248137.9994 | 866 | 248737.9994 | 827 | 232337.9994
869 | 246337.9994 | 872 | 240837.9994 | 874.5 | 246037.9994 | 877.5 | 248437.9994 | 880 | 248537.9994 | 883 | 247537.9994 | 886 | 248837.9994 | 888.5 | 249737.9994 | 891.5 | 249637.9994 | 894.5 | 232337.9994 | 897 | 245237.9994 | 900 | 244237.9994 | 902.5 | 245137.9994 | 905.5 | 248137.9994 | 908.5 | 248737.9994 | 869 | 232337.9994
911 | 246337.9994 | 914 | 240837.9994 | 916.5 | 246037.9994 | 919.5 | 248437.9994 | 922.5 | 248537.9994 | 925 | 247537.9994 | 928 | 248837.9994 | 930.5 | 249737.9994 | 933.5 | 249637.9994 | 936 | 232337.9994 | 939 | 245237.9994 | 941.5 | 244237.9994 | 944.5 | 245137.9994 | 947.5 | 248137.9994 | 950.5 | 248737.9994 | 911 | 232337.9994
953 | 246337.9994 | 955.5 | 240837.9994 | 958.5 | 246037.9994 | 961.5 | 248437.9994 | 964.5 | 248537.9994 | 967 | 247537.9994 | 969.5 | 248837.9994 | 972.5 | 249737.9994 | 975.5 | 249637.9994 | 978.5 | 232337.9994 | 981 | 245237.9994 | 984 | 244237.9994 | 986.5 | 245137.9994 | 989.5 | 248137.9994 | 992.5 | 248737.9994 | 953 | 232337.9994
995 | 246337.9994 | 998 | 240837.9994 | 1000.5 | 246037.9994 | 1003.5 | 248437.9994 | 1006.5 | 248537.9994 | 1009 | 247537.9994 | 1011.5 | 248837.9994 | 1014.5 | 249737.9994 | 1017.5 | 249637.9994 | 1020 | 232337.9994 | 1023 | 245237.9994 | 1026 | 244237.9994 | 1028.5 | 245137.9994 | 1031.5 | 248137.9994 | 1034.5 | 248737.9994 | 995 | 232337.9994
1037 | 246337.9994 | 1040 | 240837.9994 | 1042.5 | 246037.9994 | 1045.5 | 248437.9994 | 1048.5 | 248537.9994 | 1051 | 247537.9994 | 1053.5 | 248837.9994 | 1056.5 | 249737.9994 | 1059.5 | 249637.9994 | 1062.5 | 232337.9994 | 1065 | 245237.9994 | 1068 | 244237.9994 | 1070.5 | 245137.9994 | 1073.5 | 248137.9994 | 1076 | 248737.9994 | 1037 | 232337.9994
1079 | 246337.9994 | 1081.5 | 240837.9994 | 1084.5 | 246037.9994 | 1087.5 | 248437.9994 | 1090 | 248537.9994 | 1093 | 247537.9994 | 1096 | 248837.9994 | 1098.5 | 249737.9994 | 1101.5 | 249637.9994 | 1104.5 | 232337.9994 | 1107 | 245237.9994 | 1109.5 | 244237.9994 | 1112.5 | 245137.9994 | 1115.5 | 248137.9994 | 1118 | 248737.9994 | 1079 | 232337.9994
1121 | 246337.9994 | 1124 | 240837.9994 | 1126.5 | 246037.9994 | 1129.5 | 248437.9994 | 1132.5 | 248537.9994 | 1135 | 247537.9994 | 1138 | 248837.9994 | 1140.5 | 249737.9994 | 1143.5 | 249637.9994 | 1146.5 | 232337.9994 | 1149 | 245237.9994 | 1152 | 244237.9994 | 1154.5 | 245137.9994 | 1157.5 | 248137.9994 | 1160.5 | 248737.9994 | 1121 | 232337.9994
1163 | 246337.9994 | 1166 | 240837.9994 | 1168.5 | 246037.9994 | 1171.5 | 248437.9994 | 1174.5 | 248537.9994 | 1177 | 247537.9994 | 1179.5 | 248837.9994 | 1182.5 | 249737.9994 | 1185.5 | 249637.9994 | 1188 | 232337.9994 | 1191 | 245237.9994 | 1193.5 | 244237.9994 | 1196.5 | 245137.9994 | 1199.5 | 248137.9994 | 1202 | 248737.9994 | 1163 | 232337.9994
1205 | 246337.9994 | 1207.5 | 240837.9994 | 1210.5 | 246037.9994 | 1213.5 | 248437.9994 | 1216.5 | 248537.9994 | 1219 | 247537.9994 | 1221.5 | 248837.9994 | 1224.5 | 249737.9994 | 1227.5 | 249637.9994 | 1230 | 232337.9994 | 1233 | 245237.9994 | 1236 | 244237.9994 | 1238.5 | 245137.9994 | 1241.5 | 248137.9994 | 1244.5 | 248737.9994 | 1205 | 232337.9994
1247 | 246337.9994 | 1250 | 240837.9994 | 1252.5 | 246037.9994 | 1255.5 | 248437.9994 | 1258 | 248537.9994 | 1261 | 247537.9994 | 1263.5 | 248837.9994 | 1266.5 | 249737.9994 | 1269.5 | 249637.9994 | 1272 | 232337.9994 | 1275 | 245237.9994 | 1277.5 | 244237.9994 | 1280.5 | 245137.9994 | 1283.5 | 248137.9994 | 1286 | 248737.9994 | 1247 | 232337.9994
1289 | 246337.9994 | 1291.5 | 240837.9994 | 1294.5 | 246037.9994 | 1297.5 | 248437.9994 | 1300 | 248537.9994 | 1303 | 247537.9994 | 1305.5 | 248837.9994 | 1308.5 | 249737.9994 | 1311.5 | 249637.9994 | 1314 | 232337.9994 | 1317 | 245237.9994 | 1319.5 | 244237.9994 | 1322.5 | 245137.9994 | 1325.5 | 248137.9994 | 1328 | 248737.9994 | 1289 | 232337.9994
1331 | 246337.9994 | 1333.5 | 240837.9994 | 1336.5 | 246037.9994 | 1339.5 | 248437.9994 | 1342.5 | 248537.9994 | 1345 | 247537.9994 | 1347.5 | 248837.9994 | 1350.5 | 249737.9994 | 1353.5 | 249637.9994 | 1356 | 232337.9994 | 1359 | 245237.9994 | 1362 | 244237.9994 | 1364.5 | 245137.9994 | 1367.5 | 248137.9994 | 1370 | 248737.9994 | 1331 | 232337.9994
1373 | 246337.9994 | 1375.5 | 240837.9994 | 1378.5 | 246037.9994 | 1381.5 | 248437.9994 | 1384 | 248537.9994 | 1387 | 247537.9994 | 1389.5 | 248837.9994 | 1392.5 | 249737.9994 | 1395.5 | 249637.9994 | 1398 | 232337.9994 | 1401 | 245237.9994 | 1404 | 244237.9994 | 1406.5 | 245137.9994 | 1409.5 | 248137.9994 | 1412 | 248737.9994 | 1373 | 232337.9994
1415 | 246337.9994 | 1417.5 | 240837.9994 | 1420.5 | 246037.9994 | 1423.5 | 248437.9994 | 1426 | 248537.9994 | 1429 | 247537.9994 | 1431.5 | 248837.9994 | 1434.5 | 249737.9994 | 1437.5 | 249637.9994 | 1440 | 232337.9994 | 1443 | 245237.9994 | 1446 | 244237.9994 | 1448.5 | 245137.9994 | 1451.5 | 248137.9994 | 1454 | 248737.9994 | 1415 | 232337.9994
1457 | 246337.9994 | 1459.5 | 240837.9994 | 1462.5 | 246037.9994 | 1465.5 | 248437.9994 | 1468 | 248537.9994 | 1471 | 247537.9994 | 1473.5 | 248837.9994 | 1476.5 | 249737.9994 | 1479.5 | 249637.9994 | 1482 | 232337.9994 | 1485 | 245237.9994 | 1488 | 244237.9994 | 1490.5 | 245137.9994 | 1493.5 | 248137.9994 | 1496 | 248737.9994 | 1457 | 232337.9994
1499 | 246337.9994 | 1501.5 | 240837.9994 | 1504.5 | 246037.9994 | 1507.5 | 248437.9994 | 1510 | 248537.9994 | 1513 | 247537.9994 | 1515.5 | 248837.9994 | 1518.5 | 249737.9994 | 1521.5 | 249637.9994 | 1524 | 232337.9994 | 1527 | 245237.9994 | 1529.5 | 244237.9994 | 1532.5 | 245137.9994 | 1535.5 | 248137.9994 | 1538 | 248737.9994 | 1499 | 232337.9994
1541 | 44.3158 | 1543.5 | 240637.9585 | 1546.5 | 246037.9994 | 1549.5 | 248437.9994 | 1552 | 248537.9994 | 1555 | 247537.9994 | 1557.5 | 248837.9994 | 1560.5 | 249737.9994 | 1563.5 | 249637.9994 | 1566 | 232337.9994 | 1569 | 245237.9994 | 1571.5 | 244237.9994 | 1574.5 | 245137.9994 | 1577.5 | 248137.9994 | 1580 | 248737.9994 | 1541 | 44.3158
1583 | 48.5668 | 1585.5 | 240637.9585 | 1588.5 | 246037.9994 | 1591.5 | 248437.9994 | 1594 | 248537.9994 | 1597 | 247537.9994 | 1599.5 | 248837.9994 | 1602.5 | 249737.9994 | 1605.5 | 249637.9994 | 1608 | 232337.9994 | 1611 | 245237.9994 | 1613.5 | 244237.9994 | 1616.5 | 245137.9994 | 1619.5 | 248137.9994 | 1622 | 248737.9994 | 1583 | 48.5668
1625 | 33.7142 | 1627.5 | 120318.9793 | 1630.5 | 246037.9994 | 1633.5 | 248437.9994 | 1636 | 248537.9994 | 1639 | 247537.9994 | 1641.5 | 248837.9994 | 1644.5 | 249737.9994 | 1647.5 | 249637.9994 | 1650 | 232337.9994 | 1652 | 245237.9994 | 1655.5 | 244237.9994 | 1658.5 | 245137.9994 | 1661.5 | 248137.9994 | 1664 | 248737.9994 | 1625 | 33.7142
1667 | 22.927 | 1669.5 | 240637.9585 | 1672.5 | 246037.9994 | 1675.5 | 248437.9994 | 1678 | 248537.9994 | 1681 | 247537.9994 | 1683.5 | 248837.9994 | 1686.5 | 249737.9994 | 1689.5 | 249637.9994 | 1692 | 232337.9994 | 1695 | 245237.9994 | 1697.5 | 244237.9994 | 1700.5 | 245137.9994 | 1703.5 | 248137.9994 | 1706 | 248737.9994 | 1667 | 22.927
1709 | 18.9034 | 1711.5 | 240638.083 | 1714.5 | 122968.9988 | 1717.5 | 248437.9994 | 1720 | 248537.9994 | 1723 | 247537.9994 | 1725.5 | 248837.9994 | 1728.5 | 249737.9994 | 1731.5 | 249637.9994 | 1734 | 232337.9994 | 1737 | 245237.9994 | 1739.5 | 244237.9994 | 1742.5 | 245137.9994 | 1745.5 | 124018.9988 | 1748 | 26.9493 | 1709 | 18.9034
1751 | 65.9456 | 1753.5 | 120219.0623 | 1756.5 | 122968.9988 | 1759.5 | 248437.9994 | 1762 | 124218.9988 | 1765 | 123718.9988 | 1767.5 | 124368.9988 | 1770.5 | 249737.9994 | 1773.5 | 124768.9988 | 1776 | 116118.9988 | 1779 | 245237.9994 | 1781.5 | 122068.9988 | 1784.5 | 81645.9982 | 1787.5 | 124018.9988 | 1790 | 25.827 | 1751 | 25.827
1793 | 44.8264 | 1795.5 | 240538.1245 | 1798.5 | 122968.9988 | 1801.5 | 124168.9988 | 1804 | 124218.9988 | 1807 | 123718.9988 | 1809.5 | 124368.9988 | 1812.5 | 124818.9988 | 1815.5 | 124768.9988 | 1818 | 116118.9988 | 1821 | 245237.9994 | 1823.5 | 81345.9982 | 1826.5 | 122518.9988 | 1829.5 | 124018.9988 | 1832 | 174.6002 | 1793 | 44.8264
1835 | 57.6156 | 1837.5 | 120169.166 | 1840.5 | 122968.9988 | 1843.5 | 124168.9988 | 1846 | 124218.9988 | 1849 | 123718.9988 | 1851.5 | 124368.9988 | 1854.5 | 124818.9988 | 1857.5 | 124768.9988 | 1860 | 116118.9988 | 1863 | 122568.9988 | 1865.5 | 122068.9988 | 1868.5 | 122518.9988 | 1871.5 | 124018.9988 | 1874 | 234.1105 | 1835 | 57.6156
1877 | 213.505 | 1879.5 | 120169.166 | 1882.5 | 122968.9988 | 1885.5 | 5188.0139 | 1888 | 62059.4976 | 1891 | 61809.4976 | 1893.5 | 124368.9988 | 1896.5 | 124818.9988 | 1899.5 | 124768.9988 | 1902 | 2.4711 | 1905 | 24788.6064 | 1907.5 | 122068.9988 | 1910.5 | 122518.9988 | 1913.5 | 124018.9988 | 1916 | 184.6306 | 1877 | 2.4711
1919 | 219.4834 | 1921.5 | 238639.7017 | 1924.5 | 18.8158 | 1927.5 | 104.3622 | 1930 | 58.9773 | 1933 | 5.9807 | 1935.5 | 29.9297 | 1938.5 | 538.2218 | 1941.5 | 782.8165 | 1944 | 0.81845 | 1947 | 11854.4438 | 1949.5 | 27153.321 | 1952.5 | 122518.9988 | 1955.5 | 124018.9988 | 1958 | 114.7142 | 1919 | 0.81845
1961 | 308.3184 | 1963.5 | 108.4443 | 1966.5 | 28.5931 | 1969.5 | 229.9972 | 1972 | 1099.6825 | 1975 | 7.852 | 1977.5 | 26.6686 | 1980.5 | 168.6085 | 1983.5 | 619.651 | 1986 | 7.0686 | 1989 | 2665.6952 | 1991.5 | 81345.9982 | 1994.5 | 122518.9988 | 1997.5 | 82645.9982 | 2000 | 1460.2363 | 1961 | 7.0686
2003 | 48.8961 | 2005.5 | 240438.2075 | 2008.5 | 122968.9988 | 2011.5 | 124168.9988 | 2014 | 124218.9988 | 2017 | 82445.9982 | 2019.5 | 124368.9988 | 2022.5 | 124818.9988 | 2025.5 | 83145.9982 | 2028 | 32.8859 | 2031 | 53647.0797 | 2033.5 | 1179.1399 | 2036.5 | 81645.9982 | 2039.5 | 869.5234 | 2042 | 160.8792 | 2003 | 32.8859
2045 | 38.4377 | 2047.5 | 117971.8642 | 2050.5 | 122968.9988 | 2053.5 | 124168.9988 | 2056 | 124218.9988 | 2059 | 123718.9988 | 2061.5 | 124368.9988 | 2064.5 | 124818.9988 | 2067.5 | 27648.6612 | 2070 | 6.3136 | 2072 | 86481.3236 | 2075.5 | 27302.7459 | 2078.5 | 122518.9988 | 2081.5 | 124018.9988 | 2084 | 206.9183 | 2045 | 6.3136
2086.5 | 72.5582 | 2089.5 | 98.2186 | 2092.5 | 5.143 | 2095.5 | 341.7797 | 2098 | 295.25 | 2101 | 1.0242 | 2103.5 | 32.196 | 2106.5 | 448.1054 | 2109.5 | 284.1704 | 2112 | 34.8284 | 2115 | 45475.7398 | 2117.5 | 3905.5037 | 2120.5 | 273.4379 | 2123.5 | 61959.4976 | 2126 | 113.5414 | 2086.5 | 1.0242
2129 | 1807.8314 | 2131.5 | 1.3138 | 2134.5 | 28.5241 | 2137.5 | 1181.579 | 2140 | 831.8791 | 2143 | 28.4189 | 2145.5 | 4.1775 | 2148.5 | 1220.5091 | 2151.5 | 1624.3461 | 2154 | 288.4646 | 2157 | 29533.9093 | 2159.5 | 81345.9982 | 2162.5 | 122518.9988 | 2165.5 | 124018.9988 | 2168 | 671.3064 | 2129 | 1.3138
2171 | 687.8577 | 2173.5 | 0.77643 | 2176.5 | 0.70365 | 2179.5 | 2230.3157 | 2182 | 1045.4498 | 2185 | 0.25521 | 2187.5 | 12.755 | 2190.5 | 593.7541 | 2193 | 542.8992 | 2196 | 37.1136 | 2198.5 | 1658.7822 | 2201.5 | 81345.9982 | 2204.5 | 122518.9988 | 2207.5 | 124018.9988 | 2210 | 1711.834 | 2171 | 0.25521
2213 | 831.6612 | 2215.5 | 25.9872 | 2218.5 | 11.6813 | 2221.5 | 6294.7715 | 2224 | 2547.8802 | 2226.5 | 12.4229 | 2229.5 | 30.6297 | 2232.5 | 1451.4499 | 2235.5 | 1625.5521 | 2238 | 13.9767 | 2241 | 80274.5943 | 2243.5 | 122068.9988 | 2246.5 | 122518.9988 | 2249.5 | 124018.9988 | 2252 | 585.5965 | 2213 | 11.6813
2255 | 113.9606 | 2257.5 | 20.4771 | 2260.5 | 2.0987 | 2263.5 | 160.9179 | 2266 | 89.9659 | 2269 | 3.626 | 2271.5 | 20.602 | 2274.5 | 3412.3677 | 2277.5 | 105.091 | 2280 | 32.1528 | 2282.5 | 1658.7822 | 2285.5 | 122068.9988 | 2288.5 | 122518.9988 | 2291 | 124018.9988 | 2294 | 1116.422 | 2255 | 2.0987
2296.5 | 2254.2377 | 2299.5 | 16.92 | 2302.5 | 22.9767 | 2305 | 6004.0337 | 2308 | 727.5466 | 2310.5 | 0.41899 | 2313.5 | 9.0667 | 2316.5 | 1516.554 | 2319.5 | 919.5518 | 2322 | 7.6133 | 2325 | 1761.5095 | 2327.5 | 122068.9988 | 2330.5 | 122518.9988 | 2333.5 | 124018.9988 | 2336 | 259.927 | 2296.5 | 0.41899
2339 | 807.0294 | 2341.5 | 17.9834 | 2344.5 | 1536.1254 | 2347.5 | 4171.2529 | 2350 | 4703.9142 | 2352.5 | 17.9607 | 2355.5 | 1066.391 | 2358.5 | 500.7552 | 2361 | 2577.7876 | 2364 | 173.7944 | 2367 | 39268.7012 | 2369.5 | 223.1656 | 2372.5 | 57.9938 | 2375 | 22.0267 | 2378 | 1402.6219 | 2339 | 17.9607
2381 | 3560.7277 | 2383.5 | 13.1748 | 2386.5 | 33.9052 | 2389.5 | 861.2471 | 2392 | 8032.4554 | 2394.5 | 11.7397 | 2397.5 | 46.3567 | 2400.5 | 10259.6284 | 2403.5 | 3712.7789 | 2406 | 3.9677 | 2409 | 5.8313 | 2411.5 | 13.7948 | 2414.5 | 12.7516 | 2417 | 2.9376 | 2420 | 40.2664 | 2381 | 2.9376
2422.5 | 383.5302 | 2425.5 | 5.2778 | 2428.5 | 27.2272 | 2431.5 | 82.0517 | 2434 | 3015.1269 | 2436.5 | 9.687 | 2439.5 | 20.4215 | 2442.5 | 455.3202 | 2445.5 | 768.7443 | 2448 | 99.4297 | 2451 | 31.7029 | 2453.5 | 3.1252 | 2456.5 | 31.2152 | 2459 | 28.4591 | 2462 | 2975.7309 | 2422.5 | 3.1252
2464.5 | 79.7827 | 2467.5 | 16.6279 | 2470.5 | 20.4955 | 2473 | 1622.3172 | 2476 | 7.2386 | 2479 | 16.9824 | 2481.5 | 0.098372 | 2484.5 | 4283.8251 | 2487 | 8224.8518 | 2490 | 18.7281 | 2492.5 | 8230.8238 | 2495.5 | 33.4387 | 2498.5 | 41.7811 | 2501 | 38.6894 | 2504 | 3324.127 | 2464.5 | 0.098372
2507 | 1147.4395 | 2509.5 | 1.8945 | 2512.5 | 14.4772 | 2515 | 147.3434 | 2518 | 4175.0071 | 2521 | 2.5966 | 2523.5 | 29.2369 | 2526.5 | 6165.9642 | 2529 | 1150.7773 | 2532 | 3.4066 | 2535 | 11679.8247 | 2537.5 | 6165.0531 | 2540.5 | 839.4499 | 2543 | 387.3867 | 2546 | 1650.2645 | 2507 | 1.8945
2548.5 | 1815.654 | 2551.5 | 16.0479 | 2555 | 40.3963 | 2557 | 9974.9827 | 2560 | 1415.9852 | 2563 | 24.6309 | 2565.5 | 1071.7923 | 2568.5 | 133.162 | 2571.5 | 17.2983 | 2574 | 5.2607 | 2577 | 33001.8605 | 2579.5 | 7304.1617 | 2582.5 | 5603.1831 | 2585 | 5954.5603 | 2588 | 4736.6117 | 2548.5 | 5.2607
2590.5 | 69.9008 | 2593.5 | 50.8509 | 2596.5 | 81.0942 | 2599 | 436.5165 | 2602 | 6241.3958 | 2604.5 | 24.7601 | 2607.5 | 4.6794 | 2610.5 | 3311.7341 | 2613.5 | 2279.0478 | 2616 | 191.8232 | 2619 | 3215.3332 | 2621.5 | 2343.3189 | 2624.5 | 2280.8886 | 2627.5 | 2264.1073 | 2630 | 3413.1827 | 2590.5 | 4.6794
2632.5 | 92.6586 | 2635.5 | 62.336 | 2638.5 | 12.6875 | 2641.5 | 149.6951 | 2644 | 2328.696 | 2647 | 26.5305 | 2649.5 | 10.0172 | 2652.5 | 810.4543 | 2655 | 2430.7372 | 2658 | 2.6515 | 2660.5 | 4644.1409 | 2663.5 | 23463.6309 | 2666.5 | 281.5987 | 2669 | 107.5256 | 2672 | 2123.1333 | 2632.5 | 2.6515
2675 | 2190.961 | 2677.5 | 1.4027 | 2680.5 | 13.1164 | 2683 | 2245.0516 | 2686 | 8069.4473 | 2688.5 | 26.797 | 2691.5 | 5.8377 | 2694.5 | 3012.1633 | 2697 | 2704.3183 | 2700 | 17.8845 | 2703 | 14188.3371 | 2705.5 | 144.9584 | 2708.5 | 828.7706 | 2711 | 75.5717 | 2714 | 7975.3512 | 2675 | 1.4027
2716.5 | 631.1041 | 2719.5 | 7.7225 | 2722.5 | 0.1473 | 2725 | 504.5556 | 2728 | 872.3233 | 2730.5 | 19.3691 | 2733.5 | 9.2655 | 2736.5 | 1715.7776 | 2739 | 137.9343 | 2742 | 51.888 | 2744.5 | 21917.3681 | 2747.5 | 491.3653 | 2750.5 | 512.8508 | 2753 | 344.5303 | 2756 | 547.6071 | 2716.5 | 0.1473
2758.5 | 1407.1127 | 2761.5 | 14.2849 | 2764.5 | 15.1418 | 2767 | 5344.2751 | 2770 | 199.1183 | 2772.5 | 28.0777 | 2775.5 | 1.2603 | 2778.5 | 558.1827 | 2781 | 350.4531 | 2784 | 3.0552 | 2786.5 | 5433.5384 | 2789.5 | 273.2062 | 2792.5 | 352.9747 | 2795 | 271.7637 | 2798 | 387.9249 | 2758.5 | 1.2603
2800.5 | 8898.9508 | 2803.5 | 10.279 | 2806.5 | 12.1558 | 2809 | 6369.1815 | 2812 | 293.1184 | 2814.5 | 9.3352 | 2817.5 | 62.1994 | 2820.5 | 4504.8265 | 2823 | 7096.0673 | 2826 | 46.0829 | 2828.5 | 13995.2655 | 2831.5 | 332.8791 | 2834.5 | 326.1498 | 2837 | 247.2364 | 2840 | 3873.7397 | 2800.5 | 9.3352
2842.5 | 76.5732 | 2845.5 | 210.4146 | 2848.5 | 2490.8683 | 2851 | 3006.6762 | 2854 | 116.8333 | 2856.5 | 14.9064 | 2859.5 | 2.0839 | 2862.5 | 119.4075 | 2865 | 2352.8436 | 2868 | 23.9074 | 2870.5 | 38525.7858 | 2873.5 | 262.1078 | 2876.5 | 266.1656 | 2879 | 300.0054 | 2882 | 2085.1592 | 2842.5 | 2.0839
2884.5 | 1887.3275 | 2887.5 | 246.7492 | 2890.5 | 199.6677 | 2893 | 3501.9579 | 2896 | 2932.1207 | 2898.5 | 0.83598 | 2901.5 | 963.6947 | 2904.5 | 3089.0307 | 2907 | 8195.7509 | 2910 | 46.009 | 2912.5 | 11145.4012 | 2915.5 | 264.2745 | 2918.5 | 260.7607 | 2921 | 298.0755 | 2924 | 3042.3812 | 2884.5 | 0.83598

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 61 |  |  | 2006-09-01 | 12:30
TS/TP | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | Minimums Overall
-91.3 | 240838 |  | -82.3 | 246338 | -76.7 | 232338 | -73.3 | 232338 | -71 | 245138 | -68.8 | 244238 | -91.3 | 232338
-49.1 | 240838 |  | -40.3 | 123719 | -34.7 | 232338 | -31.3 | 232338 | -29.2 | 245138 | -26.8 | 244238 | -49.1 | 123719
-7.3 | 62034.5 |  | 1.6 | 246338 | 7.4 | 232338 | 10.6 | 232338 | 12.9 | 245138 | 15.2 | 244238 | -7.3 | 62034.5
34.7 | 240838 |  | 43.6 | 246338 | 49.4 | 232338 | 52.7 | 232338 | 55 | 245138 | 57.2 | 244238 | 34.7 | 232338
76.9 | 124169 |  | 85.7 | 246338 | 91.3 | 232338 | 94.7 | 232338 | 96.8 | 245138 | 99.2 | 244238 | 76.9 | 124169
118.7 | 240838 |  | 127.6 | 246338 | 133.3 | 232338 | 136.6 | 232338 | 138.8 | 245138 | 141.2 | 244238 | 118.7 | 232338
160.7 | 240838 |  | 169.7 | 246338 | 175.3 | 232338 | 178.6 | 232338 | 180.9 | 245138 | 183.2 | 244238 | 160.7 | 232338
202.7 | 240838 |  | 211.6 | 246338 | 217.3 | 232338 | 220.6 | 232338 | 222.8 | 245138 | 225.2 | 244238 | 202.7 | 232338
244.7 | 240838 |  | 253.6 | 246338 | 259.3 | 232338 | 262.6 | 232338 | 264.8 | 245138 | 267.2 | 244238 | 244.7 | 232338
286.7 | 240838 |  | 295.6 | 246338 | 301.3 | 232338 | 304.6 | 232338 | 306.8 | 245138 | 309.2 | 244238 | 286.7 | 232338
328.7 | 240838 |  | 337.6 | 246338 | 343.3 | 232338 | 346.6 | 232338 | 348.8 | 245138 | 351.2 | 244238 | 328.7 | 232338
370.7 | 240838 |  | 379.6 | 246338 | 385.3 | 232338 | 388.6 | 232338 | 390.8 | 245138 | 393.2 | 244238 | 370.7 | 232338
412.7 | 240838 |  | 421.6 | 246338 | 427.3 | 232338 | 430.6 | 232338 | 432.8 | 245138 | 435.2 | 244238 | 412.7 | 232338
454.7 | 240838 |  | 463.6 | 246338 | 469.3 | 232338 | 472.6 | 232338 | 474.8 | 245138 | 477.2 | 244238 | 454.7 | 232338
496.7 | 240838 |  | 505.6 | 246338 | 511.3 | 232338 | 514.6 | 232338 | 516.8 | 245138 | 519.2 | 244238 | 496.7 | 232338
538.7 | 240838 |  | 547.6 | 246338 | 553.3 | 232338 | 556.6 | 232338 | 558.8 | 245138 | 561.2 | 244238 | 538.7 | 232338
580.7 | 240838 |  | 589.6 | 123119 | 595.3 | 232338 | 598.6 | 232338 | 600.8 | 245138 | 603.2 | 244238 | 580.7 | 123119
622.7 | 240838 |  | 631.6 | 246338 | 637.3 | 232338 | 640.6 | 232338 | 642.8 | 245138 | 645.2 | 244238 | 622.7 | 232338
664.7 | 240838 |  | 673.6 | 246338 | 679.3 | 232338 | 682.6 | 232338 | 684.8 | 245138 | 687.2 | 244238 | 664.7 | 232338
706.7 | 240838 |  | 715.6 | 246338 | 721.3 | 232338 | 724.6 | 232338 | 726.8 | 245138 | 729.2 | 244238 | 706.7 | 232338
748.7 | 240838 |  | 757.6 | 246338 | 763.3 | 232338 | 766.6 | 232338 | 768.8 | 245138 | 771.2 | 244238 | 748.7 | 232338
790.7 | 240838 |  | 799.5 | 246338 | 805.3 | 232338 | 808.5 | 232338 | 810.7 | 245138 | 813.1 | 244238 | 790.7 | 232338
832.5 | 240838 |  | 841.6 | 246338 | 847.1 | 232338 | 850.5 | 232338 | 852.7 | 245138 | 855 | 244238 | 832.5 | 232338
874.6 | 240838 |  | 883.6 | 246338 | 889.3 | 232338 | 892.6 | 232338 | 894.8 | 245138 | 897.1 | 244238 | 874.6 | 232338
916.7 | 240838 |  | 925.6 | 246338 | 931.1 | 232338 | 934.5 | 232338 | 936.8 | 245138 | 939.1 | 244238 | 916.7 | 232338
958.6 | 240838 |  | 967.5 | 246338 | 973.2 | 232338 | 976.5 | 232338 | 978.8 | 245138 | 981.2 | 244238 | 958.6 | 232338
1000.7 | 240838 |  | 1009.5 | 246338 | 1015.2 | 232338 | 1018.4 | 232338 | 1020.8 | 245138 | 1023.2 | 244238 | 1000.7 | 232338
1042.7 | 240838 |  | 1051.5 | 246338 | 1057.3 | 232338 | 1060.5 | 232338 | 1062.7 | 245138 | 1065.1 | 244238 | 1042.7 | 232338
1084.5 | 240838 |  | 1093.6 | 246338 | 1099.1 | 232338 | 1102.6 | 232338 | 1104.7 | 245138 | 1106.9 | 244238 | 1084.5 | 232338
1126.7 | 240838 |  | 1135.6 | 246338 | 1141.3 | 232338 | 1144.6 | 232338 | 1146.8 | 245138 | 1149.2 | 244238 | 1126.7 | 232338
1168.7 | 240838 |  | 1177.5 | 246338 | 1183.1 | 232338 | 1186.4 | 232338 | 1188.7 | 245138 | 1191 | 244238 | 1168.7 | 232338
1210.6 | 240838 |  | 1219.5 | 246338 | 1225.1 | 232338 | 1228.4 | 232338 | 1230.8 | 245138 | 1233.2 | 244238 | 1210.6 | 232338
1252.6 | 240838 |  | 1261.5 | 246338 | 1267.1 | 232338 | 1270.4 | 232338 | 1272.7 | 245138 | 1274.9 | 244238 | 1252.6 | 232338
1294.5 | 240838 |  | 1303.5 | 246338 | 1309 | 232338 | 1312.4 | 232338 | 1314.7 | 245138 | 1316.9 | 244238 | 1294.5 | 232338
1336.6 | 240838 |  | 1345.5 | 246338 | 1351.1 | 232338 | 1354.4 | 232338 | 1356.7 | 245138 | 1359.1 | 244238 | 1336.6 | 232338
1378.5 | 240838 |  | 1387.5 | 246338 | 1393.1 | 232338 | 1396.4 | 232338 | 1398.7 | 245138 | 1401 | 244238 | 1378.5 | 232338
1420.5 | 240838 |  | 1429.5 | 246338 | 1435.1 | 232338 | 1438.4 | 232338 | 1440.7 | 245138 | 1443 | 244238 | 1420.5 | 232338
1462.5 | 240838 |  | 1471.5 | 246338 | 1477.1 | 232338 | 1480.4 | 232338 | 1482.7 | 245138 | 1485 | 244238 | 1462.5 | 232338
1504.5 | 240838 |  | 1513.5 | 246338 | 1519 | 232338 | 1522.4 | 232338 | 1524.7 | 245138 | 1526.9 | 244238 | 1504.5 | 232338
1546.5 | 489.9868 |  | 1555.5 | 354.5446 | 1561 | 232338 | 1564.4 | 232338 | 1566.7 | 245138 | 1568.9 | 244238 | 1546.5 | 354.5446
1588.5 | 1677.4478 |  | 1597.5 | 12076.5942 | 1603 | 232338 | 1606.4 | 232338 | 1608.7 | 245138 | 1610.9 | 244238 | 1588.5 | 1677.4478
1630.5 | 2406.7159 |  | 1639.5 | 6811.3697 | 1644.8 | 232338 | 1648.4 | 232338 | 1650.5 | 245138 | 1652.9 | 244238 | 1630.5 | 2406.7159
1672.5 | 531.0237 |  | 1681.5 | 634.4286 | 1687 | 232338 | 1690.4 | 232338 | 1692.7 | 245138 | 1694.9 | 244238 | 1672.5 | 531.0237
1714.5 | 1364.8064 |  | 1723.5 | 1595.0022 | 1729 | 232338 | 1732.4 | 124019 | 1734.7 | 23.1114 | 1736.9 | 36.1258 | 1714.5 | 23.1114
1756.5 | 15424.8234 |  | 1765.5 | 8253.8069 | 1771 | 116119 | 1774.4 | 81646 | 1776.7 | 26.6927 | 1778.9 | 14.8187 | 1756.5 | 14.8187
1798.5 | 7392.5166 |  | 1807.5 | 10465.1378 | 1813 | 81346 | 1816.4 | 116119 | 1818.7 | 7.8748 | 1820.9 | 11.7424 | 1798.5 | 7.8748
1840.5 | 6174.8352 |  | 1849.5 | 5456.1128 | 1855 | 116119 | 1858.4 | 116119 | 1860.7 | 14.5336 | 1862.9 | 15.9099 | 1840.5 | 14.5336
1882.5 | 5188.0426 |  | 1891.5 | 26798.7379 | 1897 | 195.3884 | 1900.4 | 206.3495 | 1902.7 | 6.9512 | 1904.9 | 5.8133 | 1882.5 | 5.8133
1924.5 | 6.2799 |  | 1933.5 | 7.3886 | 1939 | 3709.4683 | 1942.4 | 4.1146 | 1944.7 | 10.7169 | 1946.9 | 3.3832 | 1924.5 | 3.3832
1966.5 | 10.2894 |  | 1975.5 | 2.1716 | 1981 | 2727.2335 | 1984.4 | 26.1084 | 1986.7 | 2.2251 | 1988.9 | 4.4333 | 1966.5 | 2.1716
2008.5 | 7914.9341 |  | 2017.5 | 6677.1967 | 2023 | 1179.2565 | 2026.4 | 869.6797 | 2028.7 | 2.2677 | 2030.9 | 5.5718 | 2008.5 | 2.2677
2050.5 | 7148.1765 |  | 2059.5 | 7148.1765 | 2064.8 | 378.1579 | 2068.4 | 424.9423 | 2070.5 | 1.7163 | 2072.9 | 4.6505 | 2050.5 | 1.7163
2092.4 | 3.641 |  | 2101.4 | 2.4992 | 2107 | 2615.5076 | 2110.4 | 11.4315 | 2112.7 | 2.696 | 2114.9 | 2.5892 | 2092.4 | 2.4992
2134.5 | 2.7454 |  | 2143.5 | 5.6165 | 2149 | 714.5987 | 2152.4 | 22.3283 | 2154.7 | 6.7722 | 2156.9 | 4.6265 | 2134.5 | 2.7454
2176.5 | 0.6845 |  | 2185.4 | 1.7412 | 2190.9 | 1659.4591 | 2194.4 | 9.9549 | 2196.6 | 0.68156 | 2198.8 | 11.4116 | 2176.5 | 0.68156
2218.5 | 3.0367 |  | 2227.4 | 13.752 | 2232.9 | 635.3278 | 2236.4 | 20.2018 | 2238.7 | 6.7357 | 2240.9 | 6.1589 | 2218.5 | 3.0367
2260.5 | 1.6887 |  | 2269.5 | 2.055 | 2274.9 | 1659.4591 | 2278.3 | 27.0092 | 2280.6 | 0.68156 | 2282.8 | 1.8203 | 2260.5 | 0.68156
2302.3 | 11.6711 |  | 2311.3 | 1.0767 | 2316.9 | 373.3372 | 2320.4 | 27.2039 | 2322.6 | 0.72408 | 2324.9 | 1.4081 | 2302.3 | 0.72408
2344.5 | 0.67021 |  | 2353.3 | 1.9822 | 2358.9 | 223.6265 | 2362.3 | 3.4655 | 2364.7 | 13.4405 | 2366.7 | 0.66423 | 2344.5 | 0.66423
2386.5 | 14.4599 |  | 2395.4 | 13.0767 | 2400.9 | 3.1275 | 2404.3 | 4.3894 | 2406.7 | 1.4855 | 2408.8 | 2.035 | 2386.5 | 1.4855
2428.4 | 6.6569 |  | 2437.3 | 3.7108 | 2442.9 | 4.552 | 2446.3 | 0.66235 | 2448.7 | 0.90733 | 2450.8 | 1.1153 | 2428.4 | 0.66235
2470.3 | 0.67373 |  | 2479.3 | 1.4004 | 2484.9 | 21.9939 | 2488.3 | 24.1867 | 2490.5 | 12.9886 | 2492.7 | 0.67491 | 2470.3 | 0.67373
2512.4 | 3.3182 |  | 2521.4 | 4.0496 | 2527 | 69.914 | 2530.3 | 16.5986 | 2532.6 | 0.66606 | 2534.7 | 20.4526 | 2512.4 | 0.66606
2554.4 | 17.3019 |  | 2563.4 | 10.202 | 2569 | 496.9922 | 2572.4 | 0.98905 | 2574.6 | 1.0751 | 2576.8 | 10.1143 | 2554.4 | 0.98905
2596.3 | 25.1069 |  | 2605.3 | 6.1117 | 2610.9 | 1310.3156 | 2614.4 | 8.281 | 2616.6 | 12.3914 | 2618.9 | 7.9523 | 2596.3 | 6.1117
2638.4 | 2.5306 |  | 2647.3 | 6.0156 | 2652.9 | 214.4514 | 2656.3 | 3.5516 | 2658.6 | 2.0541 | 2660.7 | 5.3192 | 2638.4 | 2.0541
2680.4 | 2.8331 |  | 2689.3 | 7.2546 | 2694.9 | 125.8088 | 2698.3 | 16.9272 | 2700.6 | 6.0718 | 2702.7 | 4.9409 | 2680.4 | 2.8331
2722.3 | 1.6259 |  | 2731.2 | 4.0962 | 2736.8 | 491.6174 | 2740.3 | 12.3874 | 2742.5 | 0.67241 | 2744.7 | 0.95127 | 2722.3 | 0.67241
2764.3 | 7.2186 |  | 2773.2 | 0.66139 | 2778.8 | 216.6457 | 2782.3 | 12.4889 | 2784.5 | 0.66369 | 2786.7 | 23.1334 | 2764.3 | 0.66139
2806.3 | 11.597 |  | 2815.2 | 10.7009 | 2820.8 | 286.3307 | 2824.3 | 5.4375 | 2826.5 | 6.9507 | 2828.7 | 7.4958 | 2806.3 | 5.4375
2848.3 | 77.4212 |  | 2857.2 | 3.5516 | 2862.8 | 254.8898 | 2866.3 | 26.8151 | 2868.5 | 0.66155 | 2870.7 | 4.6078 | 2848.3 | 0.66155
2890.3 | 200.1683 |  | 2899.2 | 0.66585 | 2904.8 | 228.2426 | 2908.3 | 24.781 | 2910.5 | 2.8717 | 2912.7 | 2.1101 | 2890.3 | 0.66585

## TempPlot
All cable thermocouples fail (interaction with IRMS?)

## C5-C6
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 151.9158 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38961.5207 | 1 | 0 | 38961.5207 | 1 | 0 |  | -57.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5212 | 1 | 0 | 38961.5212 | 1 | 0 |  | -15.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5217 | 1 | 0 | 38961.5217 | 1 | 0 |  | 26.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5222 | 1 | 0 | 38961.5222 | 1 | 0 |  | 68.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5227 | 1 | 0 | 38961.5227 | 1 | 0 |  | 110.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5232 | 1 | 0 | 38961.5232 | 1 | 0 |  | 152.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5236 | 1 | 0 | 38961.5237 | 1 | 0 |  | 194.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5241 | 1 | 0 | 38961.5241 | 1 | 0 |  | 236.5 | 334.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5246 | 1 | 0 | 38961.5246 | 1 | 0 |  | 278.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5251 | 1 | 0 | 38961.5251 | 1 | 0 |  | 320.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5256 | 1 | 1 | 38961.5256 | 1 | 0 |  | 362.5 | 460.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 618705926.44 | 248738 | 248538.0804
38961.5261 | 1 | 0 | 38961.5261 | 1 | 0 |  | 404.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5266 | 1 | 0 | 38961.5266 | 1 | 0 |  | 446.5 | 544.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.527 | 1 | 0 | 38961.5271 | 1 | 0 |  | 488.5 | 586.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5275 | 1 | 0 | 38961.5275 | 1 | 0 |  | 530.5 | 628.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.528 | 1 | 0 | 38961.528 | 1 | 0 |  | 572.5 | 670.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5285 | 1 | 0 | 38961.5285 | 1 | 0 |  | 614.5 | 712.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.529 | 1 | 0 | 38961.529 | 1 | 0 |  | 656.5 | 754.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5295 | 1 | 0 | 38961.5295 | 1 | 0 |  | 698.5 | 796.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.53 | 1 | 0 | 38961.53 | 1 | 0 |  | 740.5 | 838.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5305 | 1 | 0 | 38961.5305 | 1 | 0 |  | 782.5 | 880.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5309 | 1 | 0 | 38961.5309 | 1 | 0 |  | 824 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5314 | 1 | 0 | 38961.5314 | 1 | 0 |  | 866 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5319 | 1 | 0 | 38961.5319 | 1 | 0 |  | 908.5 | 1006.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5324 | 1 | 0 | 38961.5324 | 1 | 0 |  | 950.5 | 1048.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5329 | 1 | 0 | 38961.5329 | 1 | 0 |  | 992.5 | 1090.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5334 | 1 | 0 | 38961.5334 | 1 | 0 |  | 1034.5 | 1132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5338 | 1 | 0 | 38961.5339 | 1 | 0 |  | 1076 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5343 | 1 | 0 | 38961.5344 | 1 | 0 |  | 1118 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5348 | 1 | 0 | 38961.5348 | 1 | 0 |  | 1160.5 | 1258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5353 | 1 | 0 | 38961.5353 | 1 | 0 |  | 1202 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5358 | 1 | 0 | 38961.5358 | 1 | 0 |  | 1244.5 | 1342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5363 | 1 | 0 | 38961.5363 | 1 | 0 |  | 1286 | 1384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5368 | 1 | 0 | 38961.5368 | 1 | 0 |  | 1328 | 1426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5372 | 1 | 0 | 38961.5373 | 1 | 0 |  | 1370 | 1468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5377 | 1 | 0 | 38961.5378 | 1 | 0 |  | 1412 | 1510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5382 | 1 | 0 | 38961.5382 | 1 | 0 |  | 1454 | 1552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5387 | 1 | 0 | 38961.5387 | 1 | 0 |  | 1496 | 1594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5392 | 1 | 0 | 38961.5392 | 1 | 0 |  | 1538 | 1636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5397 | 1 | 0 | 38961.5397 | 1 | 0 |  | 1580 | 1678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5402 | 1 | 0 | 38961.5402 | 1 | 0 |  | 1622 | 1720 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5406 | 1 | 0 | 38961.5407 | 1 | 0 |  | 1664 | 1762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5411 | 1 | 0 | 38961.5412 | 1 | 0 |  | 1706 | 1804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38961.5416 | 1942 | 0 | 38961.5416 | 1828 | 0 |  | 1748 | 1846 | 118.5592 | 0 | 111.5995 | 0 | 1.1856 | 0 | 1.116 | 0 | 1.1856 | 1.116 | 28.1349 | 36.1258 | 26.9493
38961.5421 | 1959 | 0 | 38961.5421 | 2085 | 0 |  | 1790 | 1888 | 119.5971 | 0 | 127.2894 | 0 | 1.196 | 0 | 1.2729 | 0 | 1.196 | 1.2729 | 27.023 | 19.3468 | 25.827
38961.5426 | 2048 | 25 | 38961.5426 | 2243 | 30 |  | 1832 | 1930 | 125.0305 | 1.5263 | 136.9353 | 1.8315 | 1.2503 | 0.015263 | 1.3694 | 0.018315 | 1.235 | 1.351 | 24.3291 | 11.7424 | 174.6002
38961.5431 | 2080 | 43 | 38961.5431 | 1850 | 30 |  | 1874 | 1972 | 126.9841 | 2.6252 | 112.9426 | 1.8315 | 1.2698 | 0.026252 | 1.1294 | 0.018315 | 1.2436 | 1.1111 | 21.2264 | 38.029 | 234.1105
38961.5436 | 1917 | 18 | 38961.5436 | 2344 | 22 |  | 1916 | 2014 | 117.033 | 1.0989 | 143.1013 | 1.3431 | 1.1703 | 0.010989 | 1.431 | 0.013431 | 1.1593 | 1.4176 | 35.3297 | 6.3893 | 184.6306
38961.5441 | 2262 | 13 | 38961.5441 | 2323 | 12 |  | 1958 | 2056 | 138.0952 | 0.79365 | 141.8193 | 0.7326 | 1.381 | 0.0079365 | 1.4182 | 0.007326 | 1.373 | 1.4109 | 10.9047 | 7.514 | 114.7142
38961.5445 | 1912 | 7 | 38961.5446 | 2047 | 7 |  | 2000 | 2098 | 116.7277 | 0.42735 | 124.9695 | 0.42735 | 1.1673 | 0.0042735 | 1.2497 | 0.0042735 | 1.163 | 1.2454 | 30.773 | 21.8803 | 1460.2363
38961.545 | 2268 | 7 | 38961.545 | 2361 | 7 |  | 2042 | 2140 | 138.4615 | 0.42735 | 144.1392 | 0.42735 | 1.3846 | 0.0042735 | 1.4414 | 0.0042735 | 1.3803 | 1.4371 | 10.3205 | 5.5718 | 160.8792
38961.5455 | 2203 | 6 | 38961.5455 | 2380 | 6 |  | 2084 | 2182 | 134.4933 | 0.3663 | 145.2991 | 0.3663 | 1.3449 | 0.003663 | 1.453 | 0.003663 | 1.3413 | 1.4493 | 13.7999 | 4.6505 | 206.9183
38961.546 | 2351 | 4 | 38961.546 | 2406 | 4 |  | 2126 | 2224 | 143.5287 | 0.2442 | 146.8864 | 0.2442 | 1.4353 | 0.002442 | 1.4689 | 0.002442 | 1.4328 | 1.4664 | 6.1508 | 3.5251 | 113.5414
38961.5465 | 2332 | 3 | 38961.5465 | 2172 | 5 |  | 2168 | 2266 | 142.3687 | 0.18315 | 132.6007 | 0.30525 | 1.4237 | 0.0018315 | 1.326 | 0.0030525 | 1.4219 | 1.323 | 6.7722 | 15.1149 | 671.3064
38961.547 | 1984 | 3 | 38961.547 | 2235 | 3 |  | 2210 | 2308 | 121.1233 | 0.18315 | 136.4469 | 0.18315 | 1.2112 | 0.0018315 | 1.3645 | 0.0018315 | 1.2094 | 1.3626 | 25.8033 | 11.4116 | 1711.834
38961.5475 | 2333 | 2 | 38961.5475 | 2302 | 3 |  | 2252 | 2350 | 142.4298 | 0.1221 | 140.5372 | 0.18315 | 1.4243 | 0.001221 | 1.4054 | 0.0018315 | 1.4231 | 1.4035 | 6.7357 | 8.2672 | 585.5965
38961.5479 | 2224 | 2 | 38961.548 | 2279 | 3 |  | 2294 | 2392 | 135.7753 | 0.1221 | 139.1331 | 0.18315 | 1.3578 | 0.001221 | 1.3913 | 0.0018315 | 1.3565 | 1.3895 | 12.0146 | 9.3015 | 1116.422
38961.5484 | 2112 | 2 | 38961.5484 | 2454 | 2 |  | 2336 | 2434 | 128.9377 | 0.1221 | 149.8168 | 0.1221 | 1.2894 | 0.001221 | 1.4982 | 0.001221 | 1.2882 | 1.4969 | 19.1253 | 1.4081 | 259.927
38961.5489 | 2196 | 3 | 38961.5489 | 2129 | 2 |  | 2378 | 2476 | 134.0659 | 0.18315 | 129.9756 | 0.1221 | 1.3407 | 0.0018315 | 1.2998 | 0.001221 | 1.3388 | 1.2985 | 13.4405 | 17.0151 | 1402.6219
38961.5494 | 2446 | 2 | 38961.5494 | 2441 | 2 |  | 2420 | 2518 | 149.3284 | 0.1221 | 149.0232 | 0.1221 | 1.4933 | 0.001221 | 1.4902 | 0.001221 | 1.4921 | 1.489 | 1.8067 | 2.035 | 40.2664
38961.5499 | 2053 | 2 | 38961.5499 | 2149 | 3 |  | 2462 | 2560 | 125.3358 | 0.1221 | 131.1966 | 0.18315 | 1.2534 | 0.001221 | 1.312 | 0.0018315 | 1.2521 | 1.3101 | 21.3585 | 15.9187 | 2975.7309
38961.5504 | 1972 | 2 | 38961.5504 | 2168 | 2 |  | 2504 | 2602 | 120.3907 | 0.1221 | 132.3565 | 0.1221 | 1.2039 | 0.001221 | 1.3236 | 0.001221 | 1.2027 | 1.3223 | 26.3927 | 14.8433 | 3324.127
38961.5509 | 2292 | 2 | 38961.5509 | 2068 | 1 |  | 2546 | 2644 | 139.9267 | 0.1221 | 126.2515 | 0.06105 | 1.3993 | 0.001221 | 1.2625 | 0.0006105 | 1.398 | 1.2619 | 8.6123 | 20.4526 | 1650.2645
38961.5513 | 1997 | 1 | 38961.5514 | 2249 | 2 |  | 2588 | 2686 | 121.917 | 0.06105 | 137.3016 | 0.1221 | 1.2192 | 0.0006105 | 1.373 | 0.001221 | 1.2186 | 1.3718 | 24.7341 | 10.6918 | 4736.6117
38961.5518 | 2120 | 2 | 38961.5519 | 2026 | 1 |  | 2630 | 2728 | 129.4261 | 0.1221 | 123.6874 | 0.06105 | 1.2943 | 0.001221 | 1.2369 | 0.0006105 | 1.293 | 1.2363 | 17.4648 | 22.8983 | 3413.1827
38961.5523 | 2067 | 1 | 38961.5523 | 2363 | 1 |  | 2672 | 2770 | 126.1905 | 0.06105 | 144.2613 | 0.06105 | 1.2619 | 0.0006105 | 1.4426 | 0.0006105 | 1.2613 | 1.442 | 20.5832 | 5.3192 | 2123.1333
38961.5528 | 2117 | 1 | 38961.5528 | 1954 | 1 |  | 2714 | 2812 | 129.243 | 0.06105 | 119.2918 | 0.06105 | 1.2924 | 0.0006105 | 1.1929 | 0.0006105 | 1.2918 | 1.1923 | 17.5813 | 27.4419 | 7975.3512
38961.5533 | 2454 | 1 | 38961.5533 | 2092 | 1 |  | 2756 | 2854 | 149.8168 | 0.06105 | 127.7167 | 0.06105 | 1.4982 | 0.0006105 | 1.2772 | 0.0006105 | 1.4976 | 1.2766 | 1.4045 | 19.6247 | 547.6071
38961.5538 | 2472 | 1 | 38961.5538 | 1899 | 1 |  | 2798 | 2896 | 150.9158 | 0.06105 | 115.9341 | 0.06105 | 1.5092 | 0.0006105 | 1.1593 | 0.0006105 | 1.5085 | 1.1587 | 0.66369 | 33.7304 | 387.9249
38961.5543 | 2028 | 1 | 38961.5543 | 2279 | 1 |  | 2840 | 2938 | 123.8095 | 0.06105 | 139.1331 | 0.06105 | 1.2381 | 0.0006105 | 1.3913 | 0.0006105 | 1.2375 | 1.3907 | 22.8347 | 9.2091 | 3873.7397
38961.5547 | 2014 | 1 | 38961.5548 | 2379 | 1 |  | 2882 | 2980 | 122.9548 | 0.06105 | 145.2381 | 0.06105 | 1.2295 | 0.0006105 | 1.4524 | 0.0006105 | 1.2289 | 1.4518 | 23.8227 | 4.6078 | 2085.1592
38961.5552 | 1925 | 1 | 38961.5553 | 2354 | 1 |  | 2924 | 3022 | 117.5214 | 0.06105 | 143.7118 | 0.06105 | 1.1752 | 0.0006105 | 1.4371 | 0.0006105 | 1.1746 | 1.4365 | 29.5503 | 5.7192 | 3042.3812

## B4-C6
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 151.5495 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38961.5207 | 1 | 0 | 38961.5207 | 1 | 0 |  | -60.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5212 | 1 | 0 | 38961.5212 | 1 | 0 |  | -18.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5217 | 1 | 0 | 38961.5217 | 1 | 0 |  | 23.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5222 | 1 | 0 | 38961.5222 | 1 | 0 |  | 65.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5226 | 1 | 0 | 38961.5227 | 1 | 0 |  | 107.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5231 | 1 | 0 | 38961.5231 | 1 | 0 |  | 149.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5236 | 1 | 0 | 38961.5236 | 1 | 0 |  | 191.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5241 | 1 | 1 | 38961.5241 | 1 | 0 |  | 233.5 | 331.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 615724670.44 | 248138 | 247938.0806
38961.5246 | 1 | 0 | 38961.5246 | 1 | 0 |  | 275.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5251 | 1 | 0 | 38961.5251 | 1 | 0 |  | 317.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5256 | 1 | 0 | 38961.5256 | 1 | 0 |  | 359.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.526 | 1 | 0 | 38961.5261 | 1 | 0 |  | 401.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5265 | 1 | 0 | 38961.5265 | 1 | 0 |  | 443.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.527 | 1 | 0 | 38961.527 | 1 | 0 |  | 485.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5275 | 1 | 0 | 38961.5275 | 1 | 0 |  | 527.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.528 | 1 | 0 | 38961.528 | 1 | 0 |  | 569.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5285 | 1 | 0 | 38961.5285 | 1 | 0 |  | 611.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.529 | 1 | 0 | 38961.529 | 1 | 0 |  | 653.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5294 | 1 | 0 | 38961.5295 | 1 | 0 |  | 695.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5299 | 1 | 0 | 38961.5299 | 1 | 0 |  | 737.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5304 | 1 | 0 | 38961.5304 | 1 | 0 |  | 779.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5309 | 1 | 0 | 38961.5309 | 1 | 0 |  | 821.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5314 | 1 | 0 | 38961.5314 | 1 | 0 |  | 863.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5319 | 1 | 0 | 38961.5319 | 1 | 0 |  | 905.5 | 1003.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5324 | 1 | 0 | 38961.5324 | 1 | 0 |  | 947.5 | 1045.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5328 | 1 | 0 | 38961.5329 | 1 | 0 |  | 989.5 | 1087.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5333 | 1 | 0 | 38961.5333 | 1 | 0 |  | 1031.5 | 1129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5338 | 1 | 0 | 38961.5338 | 1 | 0 |  | 1073.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5343 | 1 | 0 | 38961.5343 | 1 | 0 |  | 1115.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5348 | 1 | 0 | 38961.5348 | 1 | 0 |  | 1157.5 | 1255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5353 | 1 | 0 | 38961.5353 | 1 | 0 |  | 1199.5 | 1297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5358 | 1 | 0 | 38961.5358 | 1 | 0 |  | 1241.5 | 1339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5362 | 1 | 0 | 38961.5363 | 1 | 0 |  | 1283.5 | 1381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5367 | 1 | 0 | 38961.5367 | 1 | 0 |  | 1325.5 | 1423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5372 | 1 | 0 | 38961.5372 | 1 | 0 |  | 1367.5 | 1465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5377 | 1 | 0 | 38961.5377 | 1 | 0 |  | 1409.5 | 1507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5382 | 1 | 0 | 38961.5382 | 1 | 0 |  | 1451.5 | 1549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5387 | 1 | 0 | 38961.5387 | 1 | 0 |  | 1493.5 | 1591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5392 | 1 | 0 | 38961.5392 | 1 | 0 |  | 1535.5 | 1633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5397 | 1 | 0 | 38961.5397 | 1 | 0 |  | 1577.5 | 1675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5401 | 1 | 0 | 38961.5402 | 1 | 0 |  | 1619.5 | 1717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5406 | 1 | 0 | 38961.5406 | 1 | 0 |  | 1661.5 | 1759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5411 | 1 | 0 | 38961.5411 | 1 | 0 |  | 1703.5 | 1801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38961.5416 | 2 | 0 | 38961.5416 | 1811 | 0 |  | 1745.5 | 1843.5 | 0.1221 | 0 | 110.5617 | 0 | 0.001221 | 0 | 1.1056 | 0 | 0.001221 | 1.1056 | 124019 | 37.0723 | 124018.9988
38961.5421 | 2 | 0 | 38961.5421 | 2162 | 0 |  | 1787.5 | 1885.5 | 0.1221 | 0 | 131.9902 | 0 | 0.001221 | 0 | 1.3199 | 0 | 0.001221 | 1.3199 | 124019 | 14.8187 | 124018.9988
38961.5426 | 2 | 0 | 38961.5426 | 1889 | 0 |  | 1829.5 | 1927.5 | 0.1221 | 0 | 115.3236 | 0 | 0.001221 | 0 | 1.1532 | 0 | 0.001221 | 1.1532 | 124019 | 31.4124 | 124018.9988
38961.5431 | 2 | 0 | 38961.5431 | 1859 | 0 |  | 1871.5 | 1969.5 | 0.1221 | 0 | 113.4921 | 0 | 0.001221 | 0 | 1.1349 | 0 | 0.001221 | 1.1349 | 124019 | 33.5331 | 124018.9988
38961.5435 | 2 | 0 | 38961.5436 | 2346 | 0 |  | 1913.5 | 2011.5 | 0.1221 | 0 | 143.2234 | 0 | 0.001221 | 0 | 1.4322 | 0 | 0.001221 | 1.4322 | 124019 | 5.8133 | 124018.9988
38961.544 | 2 | 0 | 38961.544 | 2106 | 0 |  | 1955.5 | 2053.5 | 0.1221 | 0 | 128.5714 | 0 | 0.001221 | 0 | 1.2857 | 0 | 0.001221 | 1.2857 | 124019 | 17.8718 | 124018.9988
38961.5445 | 3 | 0 | 38961.5445 | 2377 | 0 |  | 1997.5 | 2095.5 | 0.18315 | 0 | 145.116 | 0 | 0.0018315 | 0 | 1.4512 | 0 | 0.0018315 | 1.4512 | 82646 | 4.4333 | 82645.9982
38961.545 | 256 | 0 | 38961.545 | 2068 | 0 |  | 2039.5 | 2137.5 | 15.6288 | 0 | 126.2515 | 0 | 0.15629 | 0 | 1.2625 | 0 | 0.15629 | 1.2625 | 869.6797 | 20.0377 | 869.5234
38961.5455 | 2 | 0 | 38961.5455 | 1981 | 0 |  | 2081.5 | 2179.5 | 0.1221 | 0 | 120.9402 | 0 | 0.001221 | 0 | 1.2094 | 0 | 0.001221 | 1.2094 | 124019 | 25.3094 | 124018.9988
38961.546 | 4 | 0 | 38961.546 | 1953 | 0 |  | 2123.5 | 2221.5 | 0.2442 | 0 | 119.2308 | 0 | 0.002442 | 0 | 1.1923 | 0 | 0.002442 | 1.1923 | 61959.5 | 27.106 | 61959.4976
38961.5465 | 2 | 0 | 38961.5465 | 2034 | 0 |  | 2165.5 | 2263.5 | 0.1221 | 0 | 124.1758 | 0 | 0.001221 | 0 | 1.2418 | 0 | 0.001221 | 1.2418 | 124019 | 22.0442 | 124018.9988
38961.5469 | 2 | 0 | 38961.547 | 2081 | 0 |  | 2207.5 | 2305.5 | 0.1221 | 0 | 127.0452 | 0 | 0.001221 | 0 | 1.2705 | 0 | 0.001221 | 1.2705 | 124019 | 19.2878 | 124018.9988
38961.5474 | 2 | 0 | 38961.5474 | 2134 | 0 |  | 2249.5 | 2347.5 | 0.1221 | 0 | 130.2808 | 0 | 0.001221 | 0 | 1.3028 | 0 | 0.001221 | 1.3028 | 124019 | 16.3252 | 124018.9988
38961.5479 | 2 | 0 | 38961.5479 | 2438 | 0 |  | 2291 | 2389 | 0.1221 | 0 | 148.84 | 0 | 0.001221 | 0 | 1.4884 | 0 | 0.001221 | 1.4884 | 124019 | 1.8203 | 124018.9988
38961.5484 | 2 | 0 | 38961.5484 | 2433 | 0 |  | 2333.5 | 2431.5 | 0.1221 | 0 | 148.5348 | 0 | 0.001221 | 0 | 1.4853 | 0 | 0.001221 | 1.4853 | 124019 | 2.0296 | 124018.9988
38961.5489 | 2014 | 0 | 38961.5489 | 2466 | 0 |  | 2375 | 2473 | 122.9548 | 0 | 150.5495 | 0 | 1.2295 | 0 | 1.5055 | 0 | 1.2295 | 1.5055 | 23.2562 | 0.66423 | 22.0267
38961.5494 | 2378 | 0 | 38961.5494 | 1916 | 0 |  | 2417 | 2515 | 145.177 | 0 | 116.9719 | 0 | 1.4518 | 0 | 1.1697 | 0 | 1.4518 | 1.1697 | 4.3894 | 29.5605 | 2.9376
38961.5498 | 1915 | 0 | 38961.5499 | 2455 | 0 |  | 2459 | 2557 | 116.9109 | 0 | 149.8779 | 0 | 1.1691 | 0 | 1.4988 | 0 | 1.1691 | 1.4988 | 29.6282 | 1.1153 | 28.4591
38961.5503 | 1776 | 0 | 38961.5504 | 1916 | 1 |  | 2501 | 2599 | 108.4249 | 0 | 116.9719 | 0.06105 | 1.0842 | 0 | 1.1697 | 0.0006105 | 1.0842 | 1.1691 | 39.7736 | 29.6282 | 38.6894
38961.5508 | 509 | 0 | 38961.5508 | 1988 | 0 |  | 2543 | 2641 | 31.0745 | 0 | 121.3675 | 0 | 0.31074 | 0 | 1.2137 | 0 | 0.31074 | 1.2137 | 387.6974 | 24.8682 | 387.3867
38961.5513 | 41 | 0 | 38961.5513 | 2177 | 0 |  | 2585 | 2683 | 2.5031 | 0 | 132.906 | 0 | 0.025031 | 0 | 1.3291 | 0 | 0.025031 | 1.3291 | 5954.5854 | 14.0276 | 5954.5603
38961.5518 | 105 | 0 | 38961.5518 | 1946 | 0 |  | 2627.5 | 2725.5 | 6.4103 | 0 | 118.8034 | 0 | 0.064103 | 0 | 1.188 | 0 | 0.064103 | 1.188 | 2264.1714 | 27.5632 | 2264.1073
38961.5523 | 1192 | 0 | 38961.5523 | 1938 | 0 |  | 2669 | 2767 | 72.7717 | 0 | 118.315 | 0 | 0.72772 | 0 | 1.1832 | 0 | 0.72772 | 1.1832 | 108.2534 | 28.0898 | 107.5256
38961.5528 | 1407 | 0 | 38961.5528 | 2159 | 0 |  | 2711 | 2809 | 85.8974 | 0 | 131.8071 | 0 | 0.85897 | 0 | 1.3181 | 0 | 0.85897 | 1.3181 | 76.4307 | 14.9782 | 75.5717
38961.5533 | 558 | 0 | 38961.5533 | 2452 | 0 |  | 2753 | 2851 | 34.0659 | 0 | 149.6947 | 0 | 0.34066 | 0 | 1.4969 | 0 | 0.34066 | 1.4969 | 344.871 | 1.239 | 344.5303
38961.5537 | 667 | 0 | 38961.5538 | 1878 | 0 |  | 2795 | 2893 | 40.7204 | 0 | 114.652 | 0 | 0.4072 | 0 | 1.1465 | 0 | 0.4072 | 1.1465 | 272.1709 | 32.1821 | 271.7637
38961.5542 | 714 | 0 | 38961.5542 | 1880 | 0 |  | 2837 | 2935 | 43.5897 | 0 | 114.7741 | 0 | 0.4359 | 0 | 1.1477 | 0 | 0.4359 | 1.1477 | 247.6723 | 32.0415 | 247.2364
38961.5547 | 620 | 0 | 38961.5547 | 2119 | 0 |  | 2879 | 2977 | 37.851 | 0 | 129.3651 | 0 | 0.37851 | 0 | 1.2937 | 0 | 0.37851 | 1.2937 | 300.3839 | 17.1487 | 300.0054
38961.5552 | 623 | 0 | 38961.5552 | 1973 | 0 |  | 2921 | 3019 | 38.0342 | 0 | 120.4518 | 0 | 0.38034 | 0 | 1.2045 | 0 | 0.38034 | 1.2045 | 298.4559 | 25.8175 | 298.0755

## B4-C5
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 149.7179 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38961.5207 | 1 | 0 | 38961.5207 | 1 | 0 |  | -63 | 35 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5211 | 1 | 0 | 38961.5212 | 1 | 0 |  | -21.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5216 | 1 | 0 | 38961.5216 | 1 | 0 |  | 20.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5221 | 1 | 0 | 38961.5221 | 1 | 0 |  | 63 | 161 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5226 | 1 | 0 | 38961.5226 | 1 | 0 |  | 104.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5231 | 1 | 0 | 38961.5231 | 1 | 0 |  | 146.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5236 | 1 | 0 | 38961.5236 | 1 | 0 |  | 188.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5241 | 1 | 0 | 38961.5241 | 1 | 0 |  | 230.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5245 | 1 | 0 | 38961.5246 | 1 | 0 |  | 272.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.525 | 1 | 0 | 38961.525 | 1 | 0 |  | 314.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5255 | 1 | 0 | 38961.5255 | 1 | 0 |  | 356.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.526 | 1 | 0 | 38961.526 | 1 | 0 |  | 398.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5265 | 1 | 0 | 38961.5265 | 1 | 0 |  | 440.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.527 | 1 | 0 | 38961.527 | 1 | 0 |  | 482.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5275 | 1 | 0 | 38961.5275 | 1 | 0 |  | 524.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.528 | 1 | 0 | 38961.528 | 1 | 0 |  | 566.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5284 | 1 | 0 | 38961.5284 | 1 | 0 |  | 608.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5289 | 1 | 0 | 38961.5289 | 1 | 0 |  | 650.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5294 | 1 | 0 | 38961.5294 | 1 | 0 |  | 692.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5299 | 1 | 0 | 38961.5299 | 1 | 0 |  | 734.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5304 | 1 | 0 | 38961.5304 | 1 | 0 |  | 776.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5309 | 1 | 0 | 38961.5309 | 1 | 0 |  | 818.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5314 | 1 | 0 | 38961.5314 | 1 | 0 |  | 860.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5318 | 1 | 0 | 38961.5319 | 1 | 0 |  | 902.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5323 | 1 | 0 | 38961.5323 | 1 | 0 |  | 944.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5328 | 1 | 0 | 38961.5328 | 1 | 0 |  | 986.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5333 | 1 | 0 | 38961.5333 | 1 | 0 |  | 1028.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5338 | 1 | 0 | 38961.5338 | 1 | 0 |  | 1070.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5343 | 1 | 0 | 38961.5343 | 1 | 0 |  | 1112.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5348 | 1 | 0 | 38961.5348 | 1 | 0 |  | 1154.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5352 | 1 | 0 | 38961.5353 | 1 | 0 |  | 1196.5 | 1294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5357 | 1 | 0 | 38961.5357 | 1 | 0 |  | 1238.5 | 1336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5362 | 1 | 0 | 38961.5362 | 1 | 0 |  | 1280.5 | 1378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5367 | 1 | 0 | 38961.5367 | 1 | 0 |  | 1322.5 | 1420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5372 | 1 | 0 | 38961.5372 | 1 | 0 |  | 1364.5 | 1462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5377 | 1 | 0 | 38961.5377 | 1 | 0 |  | 1406.5 | 1504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5382 | 1 | 0 | 38961.5382 | 1 | 0 |  | 1448.5 | 1546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5386 | 1 | 0 | 38961.5387 | 1 | 0 |  | 1490.5 | 1588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5391 | 1 | 0 | 38961.5391 | 1 | 0 |  | 1532.5 | 1630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5396 | 1 | 0 | 38961.5396 | 1 | 0 |  | 1574.5 | 1672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5401 | 1 | 0 | 38961.5401 | 1 | 0 |  | 1616.5 | 1714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5406 | 1 | 0 | 38961.5406 | 1 | 0 |  | 1658.5 | 1756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5411 | 1 | 0 | 38961.5411 | 1 | 0 |  | 1700.5 | 1798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38961.5416 | 1 | 0 | 38961.5416 | 1992 | 0 |  | 1742.5 | 1840.5 | 0.06105 | 0 | 121.6117 | 0 | 0.0006105 | 0 | 1.2161 | 0 | 0.0006105 | 1.2161 | 245138 | 23.1114 | 245137.9994
38961.542 | 3 | 0 | 38961.5421 | 1701 | 0 |  | 1784.5 | 1882.5 | 0.18315 | 0 | 103.8462 | 0 | 0.0018315 | 0 | 1.0385 | 0 | 0.0018315 | 1.0385 | 81646 | 44.1728 | 81645.9982
38961.5425 | 2 | 0 | 38961.5425 | 1850 | 0 |  | 1826.5 | 1924.5 | 0.1221 | 0 | 112.9426 | 0 | 0.001221 | 0 | 1.1294 | 0 | 0.001221 | 1.1294 | 122519 | 32.5611 | 122518.9988
38961.543 | 2 | 0 | 38961.543 | 1848 | 0 |  | 1868.5 | 1966.5 | 0.1221 | 0 | 112.8205 | 0 | 0.001221 | 0 | 1.1282 | 0 | 0.001221 | 1.1282 | 122519 | 32.7045 | 122518.9988
38961.5435 | 2 | 0 | 38961.5435 | 2148 | 0 |  | 1910.5 | 2008.5 | 0.1221 | 0 | 131.1355 | 0 | 0.001221 | 0 | 1.3114 | 0 | 0.001221 | 1.3114 | 122519 | 14.1704 | 122518.9988
38961.544 | 2 | 0 | 38961.544 | 1919 | 0 |  | 1952.5 | 2050.5 | 0.1221 | 0 | 117.1551 | 0 | 0.001221 | 0 | 1.1716 | 0 | 0.001221 | 1.1716 | 122519 | 27.7947 | 122518.9988
38961.5445 | 2 | 0 | 38961.5445 | 1905 | 1 |  | 1994.5 | 2092.5 | 0.1221 | 0 | 116.3004 | 0.06105 | 0.001221 | 0 | 1.163 | 0.0006105 | 0.001221 | 1.1624 | 122519 | 28.8015 | 122518.9988
38961.545 | 3 | 0 | 38961.545 | 2398 | 0 |  | 2036.5 | 2134.5 | 0.18315 | 0 | 146.398 | 0 | 0.0018315 | 0 | 1.464 | 0 | 0.0018315 | 1.464 | 81646 | 2.2677 | 81645.9982
38961.5455 | 2 | 0 | 38961.5455 | 2411 | 0 |  | 2078.5 | 2176.5 | 0.1221 | 0 | 147.1917 | 0 | 0.001221 | 0 | 1.4719 | 0 | 0.001221 | 1.4719 | 122519 | 1.7163 | 122518.9988
38961.5459 | 656 | 0 | 38961.5459 | 2388 | 0 |  | 2120.5 | 2218.5 | 40.0488 | 0 | 145.7875 | 0 | 0.40049 | 0 | 1.4579 | 0 | 0.40049 | 1.4579 | 273.8384 | 2.696 | 273.4379
38961.5464 | 2 | 0 | 38961.5464 | 2135 | 0 |  | 2162.5 | 2260.5 | 0.1221 | 0 | 130.3419 | 0 | 0.001221 | 0 | 1.3034 | 0 | 0.001221 | 1.3034 | 122519 | 14.8656 | 122518.9988
38961.5469 | 2 | 0 | 38961.5469 | 2302 | 1 |  | 2204.5 | 2302.5 | 0.1221 | 0 | 140.5372 | 0.06105 | 0.001221 | 0 | 1.4054 | 0.0006105 | 0.001221 | 1.4048 | 122519 | 6.5789 | 122518.9988
38961.5474 | 2 | 0 | 38961.5474 | 2142 | 0 |  | 2246.5 | 2344.5 | 0.1221 | 0 | 130.7692 | 0 | 0.001221 | 0 | 1.3077 | 0 | 0.001221 | 1.3077 | 122519 | 14.4902 | 122518.9988
38961.5479 | 2 | 0 | 38961.5479 | 2137 | 0 |  | 2288.5 | 2386.5 | 0.1221 | 0 | 130.464 | 0 | 0.001221 | 0 | 1.3046 | 0 | 0.001221 | 1.3046 | 122519 | 14.7581 | 122518.9988
38961.5484 | 2 | 0 | 38961.5484 | 2078 | 0 |  | 2330.5 | 2428.5 | 0.1221 | 0 | 126.862 | 0 | 0.001221 | 0 | 1.2686 | 0 | 0.001221 | 1.2686 | 122519 | 18.0164 | 122518.9988
38961.5489 | 1543 | 0 | 38961.5489 | 1927 | 0 |  | 2372.5 | 2470.5 | 94.2002 | 0 | 117.6435 | 0 | 0.942 | 0 | 1.1764 | 0 | 0.942 | 1.1764 | 58.9358 | 27.2641 | 57.9938
38961.5493 | 2150 | 0 | 38961.5494 | 2409 | 0 |  | 2414.5 | 2512.5 | 131.2576 | 0 | 147.0696 | 0 | 1.3126 | 0 | 1.4707 | 0 | 1.3126 | 1.4707 | 14.0642 | 1.8007 | 12.7516
38961.5498 | 1853 | 0 | 38961.5498 | 2409 | 0 |  | 2456.5 | 2554.5 | 113.1258 | 0 | 147.0696 | 0 | 1.1313 | 0 | 1.4707 | 0 | 1.1313 | 1.4707 | 32.3465 | 1.8007 | 31.2152
38961.5503 | 1717 | 0 | 38961.5503 | 2079 | 0 |  | 2498.5 | 2596.5 | 104.823 | 0 | 126.9231 | 0 | 1.0482 | 0 | 1.2692 | 0 | 1.0482 | 1.2692 | 42.8294 | 17.9596 | 41.7811
38961.5508 | 261 | 0 | 38961.5508 | 1915 | 0 |  | 2540.5 | 2638.5 | 15.9341 | 0 | 116.9109 | 0 | 0.15934 | 0 | 1.1691 | 0 | 0.15934 | 1.1691 | 839.6092 | 28.0616 | 839.4499
38961.5513 | 43 | 0 | 38961.5513 | 2032 | 0 |  | 2582.5 | 2680.5 | 2.6252 | 0 | 124.0537 | 0 | 0.026252 | 0 | 1.2405 | 0 | 0.026252 | 1.2405 | 5603.2093 | 20.688 | 5603.1831
38961.5518 | 103 | 0 | 38961.5518 | 2182 | 0 |  | 2624.5 | 2722.5 | 6.2882 | 0 | 133.2112 | 0 | 0.062882 | 0 | 1.3321 | 0 | 0.062882 | 1.3321 | 2280.9515 | 12.3914 | 2280.8886
38961.5523 | 642 | 0 | 38961.5523 | 1962 | 0 |  | 2666.5 | 2764.5 | 39.1941 | 0 | 119.7802 | 0 | 0.39194 | 0 | 1.1978 | 0 | 0.39194 | 1.1978 | 281.9907 | 24.9939 | 281.5987
38961.5527 | 264 | 0 | 38961.5528 | 2312 | 0 |  | 2708.5 | 2806.5 | 16.1172 | 0 | 141.1477 | 0 | 0.16117 | 0 | 1.4115 | 0 | 0.16117 | 1.4115 | 828.9318 | 6.0718 | 828.7706
38961.5532 | 400 | 0 | 38961.5532 | 2436 | 0 |  | 2750.5 | 2848.5 | 24.42 | 0 | 148.7179 | 0 | 0.2442 | 0 | 1.4872 | 0 | 0.2442 | 1.4872 | 513.095 | 0.67241 | 512.8508
38961.5537 | 541 | 0 | 38961.5537 | 1931 | 0 |  | 2792.5 | 2890.5 | 33.0281 | 0 | 117.8877 | 0 | 0.33028 | 0 | 1.1789 | 0 | 0.33028 | 1.1789 | 353.305 | 27.0005 | 352.9747
38961.5542 | 575 | 0 | 38961.5542 | 2293 | 0 |  | 2834.5 | 2932.5 | 35.1038 | 0 | 139.9878 | 0 | 0.35104 | 0 | 1.3999 | 0 | 0.35104 | 1.3999 | 326.5009 | 6.9507 | 326.1498
38961.5547 | 669 | 0 | 38961.5547 | 2083 | 0 |  | 2876.5 | 2974.5 | 40.8425 | 0 | 127.1673 | 0 | 0.40842 | 0 | 1.2717 | 0 | 0.40842 | 1.2717 | 266.574 | 17.7331 | 266.1656
38961.5552 | 679 | 0 | 38961.5552 | 2096 | 0 |  | 2918.5 | 3016.5 | 41.453 | 0 | 127.9609 | 0 | 0.41453 | 0 | 1.2796 | 0 | 0.41453 | 1.2796 | 261.1753 | 17.0029 | 260.7607

## B3-C6
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 149.1685 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38961.5206 | 1 | 0 | 38961.5206 | 1 | 0 |  | -66 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5211 | 1 | 0 | 38961.5211 | 1 | 0 |  | -24 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5216 | 1 | 0 | 38961.5216 | 1 | 0 |  | 18 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5221 | 1 | 0 | 38961.5221 | 1 | 0 |  | 60 | 158 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5226 | 1 | 0 | 38961.5226 | 1 | 0 |  | 102 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5231 | 1 | 0 | 38961.5231 | 1 | 0 |  | 144 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5235 | 1 | 0 | 38961.5236 | 1 | 0 |  | 186 | 284 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.524 | 1 | 0 | 38961.5241 | 1 | 0 |  | 228 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5245 | 1 | 0 | 38961.5245 | 1 | 0 |  | 270 | 368 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.525 | 1 | 0 | 38961.525 | 1 | 0 |  | 312 | 410 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5255 | 1 | 0 | 38961.5255 | 1 | 0 |  | 354 | 452 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.526 | 1 | 0 | 38961.526 | 1 | 0 |  | 396 | 494 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5265 | 1 | 0 | 38961.5265 | 1 | 0 |  | 438 | 536 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5269 | 1 | 0 | 38961.527 | 1 | 0 |  | 480 | 578 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5274 | 1 | 0 | 38961.5275 | 1 | 0 |  | 522 | 620 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5279 | 1 | 0 | 38961.5279 | 1 | 0 |  | 564 | 662 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5284 | 1 | 0 | 38961.5284 | 1 | 0 |  | 606 | 704 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5289 | 1 | 0 | 38961.5289 | 1 | 0 |  | 648 | 746 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5294 | 1 | 0 | 38961.5294 | 1 | 0 |  | 690 | 788 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5299 | 1 | 0 | 38961.5299 | 1 | 0 |  | 732 | 830 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5303 | 1 | 0 | 38961.5304 | 1 | 0 |  | 774 | 872 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5308 | 1 | 0 | 38961.5309 | 1 | 0 |  | 816 | 914 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5313 | 1 | 0 | 38961.5313 | 1 | 0 |  | 858 | 956 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5318 | 1 | 0 | 38961.5318 | 1 | 0 |  | 900 | 998 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5323 | 1 | 0 | 38961.5323 | 1 | 0 |  | 941.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5328 | 1 | 0 | 38961.5328 | 1 | 0 |  | 984 | 1082 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5333 | 1 | 0 | 38961.5333 | 1 | 0 |  | 1026 | 1124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5338 | 1 | 0 | 38961.5338 | 1 | 0 |  | 1068 | 1166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5342 | 1 | 0 | 38961.5342 | 1 | 0 |  | 1109.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5347 | 1 | 0 | 38961.5347 | 1 | 0 |  | 1152 | 1250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5352 | 1 | 0 | 38961.5352 | 1 | 0 |  | 1193.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5357 | 1 | 0 | 38961.5357 | 1 | 0 |  | 1236 | 1334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5362 | 1 | 0 | 38961.5362 | 1 | 0 |  | 1277.5 | 1375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5367 | 1 | 0 | 38961.5367 | 1 | 0 |  | 1319.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5372 | 1 | 0 | 38961.5372 | 1 | 0 |  | 1362 | 1460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5376 | 1 | 0 | 38961.5377 | 1 | 0 |  | 1404 | 1502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5381 | 1 | 0 | 38961.5381 | 1 | 0 |  | 1446 | 1544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5386 | 1 | 0 | 38961.5386 | 1 | 0 |  | 1488 | 1586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5391 | 1 | 0 | 38961.5391 | 1 | 0 |  | 1529.5 | 1627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5396 | 1 | 0 | 38961.5396 | 1 | 0 |  | 1571.5 | 1669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5401 | 1 | 0 | 38961.5401 | 1 | 0 |  | 1613.5 | 1711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5406 | 1 | 0 | 38961.5406 | 1 | 0 |  | 1655.5 | 1753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.541 | 1 | 0 | 38961.5411 | 1 | 0 |  | 1697.5 | 1795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
38961.5415 | 1 | 0 | 38961.5415 | 4 | 0 |  | 1739.5 | 1837.5 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 244238 | 60984.5 | 244237.9994
38961.542 | 2 | 0 | 38961.542 | 2089 | 0 |  | 1781.5 | 1879.5 | 0.1221 | 0 | 127.5336 | 0 | 0.001221 | 0 | 1.2753 | 0 | 0.001221 | 1.2753 | 122069 | 16.9641 | 122068.9988
38961.5425 | 3 | 0 | 38961.5425 | 2161 | 0 |  | 1823.5 | 1921.5 | 0.18315 | 0 | 131.9292 | 0 | 0.0018315 | 0 | 1.3193 | 0 | 0.0018315 | 1.3193 | 81346 | 13.0671 | 81345.9982
38961.543 | 2 | 0 | 38961.543 | 2108 | 0 |  | 1865.5 | 1963.5 | 0.1221 | 0 | 128.6935 | 0 | 0.001221 | 0 | 1.2869 | 0 | 0.001221 | 1.2869 | 122069 | 15.9099 | 122068.9988
38961.5435 | 2 | 0 | 38961.5435 | 2305 | 0 |  | 1907.5 | 2005.5 | 0.1221 | 0 | 140.7204 | 0 | 0.001221 | 0 | 1.4072 | 0 | 0.001221 | 1.4072 | 122069 | 6.0035 | 122068.9988
38961.544 | 2 | 1 | 38961.544 | 2221 | 0 |  | 1949.5 | 2047.5 | 0.1221 | 0.06105 | 135.5922 | 0 | 0.001221 | 0.0006105 | 1.3559 | 0 | 0.0006105 | 1.3559 | 27164.4477 | 12.5197 | 27153.321
38961.5444 | 3 | 0 | 38961.5445 | 2205 | 0 |  | 1991.5 | 2089.5 | 0.18315 | 0 | 134.6154 | 0 | 0.0018315 | 0 | 1.3462 | 0 | 0.0018315 | 1.3462 | 81346 | 10.8109 | 81345.9982
38961.5449 | 191 | 0 | 38961.5449 | 1982 | 0 |  | 2033.5 | 2131.5 | 11.6606 | 0 | 121.0012 | 0 | 0.11661 | 0 | 1.21 | 0 | 0.11661 | 1.21 | 1179.2565 | 23.2785 | 1179.1399
38961.5454 | 2 | 1 | 38961.5454 | 2220 | 0 |  | 2075.5 | 2173.5 | 0.1221 | 0.06105 | 135.5311 | 0 | 0.001221 | 0.0006105 | 1.3553 | 0 | 0.0006105 | 1.3553 | 27313.9338 | 12.5973 | 27302.7459
38961.5459 | 61 | 0 | 38961.5459 | 1887 | 0 |  | 2117.5 | 2215.5 | 3.7241 | 0 | 115.2015 | 0 | 0.037241 | 0 | 1.152 | 0 | 0.037241 | 1.152 | 3905.541 | 29.4849 | 3905.5037
38961.5464 | 3 | 0 | 38961.5464 | 2085 | 0 |  | 2159.5 | 2257.5 | 0.18315 | 0 | 127.2894 | 0 | 0.0018315 | 0 | 1.2729 | 0 | 0.0018315 | 1.2729 | 81346 | 17.1885 | 81345.9982
38961.5469 | 3 | 0 | 38961.5469 | 2049 | 0 |  | 2201.5 | 2299.5 | 0.18315 | 0 | 125.0916 | 0 | 0.0018315 | 0 | 1.2509 | 0 | 0.0018315 | 1.2509 | 81346 | 19.2474 | 81345.9982
38961.5474 | 2 | 0 | 38961.5474 | 1948 | 0 |  | 2243.5 | 2341.5 | 0.1221 | 0 | 118.9255 | 0 | 0.001221 | 0 | 1.1893 | 0 | 0.001221 | 1.1893 | 122069 | 25.4302 | 122068.9988
38961.5478 | 2 | 0 | 38961.5479 | 2332 | 0 |  | 2285.5 | 2383.5 | 0.1221 | 0 | 142.3687 | 0 | 0.001221 | 0 | 1.4237 | 0 | 0.001221 | 1.4237 | 122069 | 4.7762 | 122068.9988
38961.5483 | 2 | 0 | 38961.5483 | 2064 | 1 |  | 2327.5 | 2425.5 | 0.1221 | 0 | 126.0073 | 0.06105 | 0.001221 | 0 | 1.2601 | 0.0006105 | 0.001221 | 1.2595 | 122069 | 18.4382 | 122068.9988
38961.5488 | 755 | 0 | 38961.5488 | 2277 | 0 |  | 2369.5 | 2467.5 | 46.0928 | 0 | 139.011 | 0 | 0.46093 | 0 | 1.3901 | 0 | 0.46093 | 1.3901 | 223.6265 | 7.307 | 223.1656
38961.5493 | 2123 | 0 | 38961.5493 | 1958 | 0 |  | 2411.5 | 2509.5 | 129.6093 | 0 | 119.536 | 0 | 1.2961 | 0 | 1.1954 | 0 | 1.2961 | 1.1954 | 15.0909 | 24.7896 | 13.7948
38961.5498 | 2337 | 0 | 38961.5498 | 2346 | 0 |  | 2453.5 | 2551.5 | 142.674 | 0 | 143.2234 | 0 | 1.4267 | 0 | 1.4322 | 0 | 1.4267 | 1.4322 | 4.552 | 4.1509 | 3.1252
38961.5503 | 1816 | 0 | 38961.5503 | 2427 | 0 |  | 2495.5 | 2593.5 | 110.8669 | 0 | 148.1685 | 0 | 1.1087 | 0 | 1.4817 | 0 | 1.1087 | 1.4817 | 34.5474 | 0.67491 | 33.4387
38961.5508 | 39 | 0 | 38961.5508 | 2026 | 0 |  | 2537.5 | 2635.5 | 2.381 | 0 | 123.6874 | 0 | 0.02381 | 0 | 1.2369 | 0 | 0.02381 | 1.2369 | 6165.0769 | 20.6012 | 6165.0531
38961.5512 | 33 | 0 | 38961.5513 | 1909 | 0 |  | 2579.5 | 2677.5 | 2.0147 | 0 | 116.5446 | 0 | 0.020147 | 0 | 1.1654 | 0 | 0.020147 | 1.1654 | 7304.1818 | 27.9927 | 7304.1617
38961.5517 | 100 | 0 | 38961.5517 | 1970 | 0 |  | 2621.5 | 2719.5 | 6.105 | 0 | 120.2686 | 0 | 0.06105 | 0 | 1.2027 | 0 | 0.06105 | 1.2027 | 2343.38 | 24.0294 | 2343.3189
38961.5522 | 249 | 1 | 38961.5522 | 2182 | 0 |  | 2663.5 | 2761.5 | 15.2015 | 0.06105 | 133.2112 | 0 | 0.15201 | 0.0006105 | 1.3321 | 0 | 0.1514 | 1.3321 | 915.6527 | 11.9789 | 23463.6309
38961.5527 | 995 | 0 | 38961.5527 | 1917 | 0 |  | 2705.5 | 2803.5 | 60.7448 | 0 | 117.033 | 0 | 0.60745 | 0 | 1.1703 | 0 | 0.60745 | 1.1703 | 145.5658 | 27.4585 | 144.9584
38961.5532 | 413 | 0 | 38961.5532 | 1913 | 0 |  | 2747.5 | 2845.5 | 25.2137 | 0 | 116.7888 | 0 | 0.25214 | 0 | 1.1679 | 0 | 0.25214 | 1.1679 | 491.6174 | 27.725 | 491.3653
38961.5537 | 654 | 0 | 38961.5537 | 1962 | 0 |  | 2789.5 | 2887.5 | 39.9267 | 0 | 119.7802 | 0 | 0.39927 | 0 | 1.1978 | 0 | 0.39927 | 1.1978 | 273.6055 | 24.5352 | 273.2062
38961.5542 | 564 | 0 | 38961.5542 | 2273 | 0 |  | 2831.5 | 2929.5 | 34.4322 | 0 | 138.7668 | 0 | 0.34432 | 0 | 1.3877 | 0 | 0.34432 | 1.3877 | 333.2234 | 7.4958 | 332.8791
38961.5547 | 674 | 0 | 38961.5547 | 2036 | 0 |  | 2873.5 | 2971.5 | 41.1477 | 0 | 124.2979 | 0 | 0.41148 | 0 | 1.243 | 0 | 0.41148 | 1.243 | 262.5193 | 20.0088 | 262.1078
38961.5551 | 670 | 0 | 38961.5552 | 1961 | 0 |  | 2915.5 | 3013.5 | 40.9035 | 0 | 119.7192 | 0 | 0.40904 | 0 | 1.1972 | 0 | 0.40904 | 1.1972 | 264.6836 | 24.5987 | 264.2745

## B3-C5
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 149.779 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38961.5206 | 1 | 0 | 38961.5206 | 1 | 0 |  | -69 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5211 | 1 | 0 | 38961.5211 | 1 | 0 |  | -27 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5216 | 1 | 0 | 38961.5216 | 1 | 0 |  | 15.5 | 113.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5221 | 1 | 0 | 38961.5221 | 1 | 0 |  | 57.5 | 155.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5225 | 1 | 0 | 38961.5226 | 1 | 0 |  | 99 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.523 | 1 | 0 | 38961.523 | 1 | 0 |  | 141 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5235 | 1 | 0 | 38961.5235 | 1 | 0 |  | 183 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.524 | 1 | 0 | 38961.524 | 1 | 0 |  | 225 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5245 | 1 | 0 | 38961.5245 | 1 | 0 |  | 267 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.525 | 1 | 0 | 38961.525 | 1 | 0 |  | 309 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5255 | 1 | 0 | 38961.5255 | 1 | 0 |  | 351 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5259 | 1 | 0 | 38961.526 | 1 | 0 |  | 393 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5264 | 1 | 0 | 38961.5264 | 1 | 0 |  | 435 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5269 | 1 | 0 | 38961.5269 | 1 | 0 |  | 477 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5274 | 1 | 0 | 38961.5274 | 1 | 0 |  | 519 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5279 | 1 | 0 | 38961.5279 | 1 | 0 |  | 561 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5284 | 1 | 0 | 38961.5284 | 1 | 0 |  | 603 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5289 | 1 | 0 | 38961.5289 | 1 | 0 |  | 645 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5293 | 1 | 0 | 38961.5294 | 1 | 0 |  | 687 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5298 | 1 | 0 | 38961.5298 | 1 | 0 |  | 729 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5303 | 1 | 0 | 38961.5303 | 1 | 0 |  | 771 | 869 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5308 | 1 | 0 | 38961.5308 | 1 | 0 |  | 813 | 911 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5313 | 1 | 0 | 38961.5313 | 1 | 0 |  | 855 | 953 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5318 | 1 | 0 | 38961.5318 | 1 | 0 |  | 897 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5323 | 1 | 0 | 38961.5323 | 1 | 0 |  | 939 | 1037 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5327 | 1 | 0 | 38961.5328 | 1 | 0 |  | 981 | 1079 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5332 | 1 | 0 | 38961.5333 | 1 | 0 |  | 1023 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5337 | 1 | 0 | 38961.5337 | 1 | 0 |  | 1065 | 1163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5342 | 1 | 0 | 38961.5342 | 1 | 0 |  | 1107 | 1205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5347 | 1 | 0 | 38961.5347 | 1 | 0 |  | 1149 | 1247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5352 | 1 | 0 | 38961.5352 | 1 | 0 |  | 1191 | 1289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5357 | 1 | 0 | 38961.5357 | 1 | 0 |  | 1233 | 1331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5361 | 1 | 0 | 38961.5362 | 1 | 0 |  | 1275 | 1373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5366 | 1 | 0 | 38961.5367 | 1 | 0 |  | 1317 | 1415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5371 | 1 | 0 | 38961.5371 | 1 | 0 |  | 1359 | 1457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5376 | 1 | 0 | 38961.5376 | 1 | 0 |  | 1401 | 1499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5381 | 1 | 0 | 38961.5381 | 1 | 0 |  | 1443 | 1541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5386 | 1 | 0 | 38961.5386 | 1 | 0 |  | 1485 | 1583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5391 | 1 | 0 | 38961.5391 | 1 | 0 |  | 1527 | 1625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5395 | 1 | 0 | 38961.5396 | 1 | 0 |  | 1569 | 1667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.54 | 1 | 0 | 38961.5401 | 1 | 0 |  | 1611 | 1709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5405 | 1 | 0 |  | 1 | 0 |  | 1652 | 1750 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.541 | 1 | 0 | 38961.541 | 1 | 0 |  | 1695 | 1793 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245238 | 245238 | 245237.9994
38961.5415 | 1 | 0 | 38961.5415 | 1281 | 0 |  | 1737 | 1835 | 0.06105 | 0 | 78.2051 | 0 | 0.0006105 | 0 | 0.78205 | 0 | 0.0006105 | 0.78205 | 245238 | 91.5207 | 245237.9994
38961.542 | 1 | 0 | 38961.542 | 1658 | 0 |  | 1779 | 1877 | 0.06105 | 0 | 101.221 | 0 | 0.0006105 | 0 | 1.0122 | 0 | 0.0006105 | 1.0122 | 245238 | 47.9723 | 245237.9994
38961.5425 | 1 | 0 | 38961.5425 | 1862 | 0 |  | 1821 | 1919 | 0.06105 | 0 | 113.6752 | 0 | 0.0006105 | 0 | 1.1368 | 0 | 0.0006105 | 1.1368 | 245238 | 31.7605 | 245237.9994
38961.543 | 2 | 0 | 38961.543 | 2051 | 0 |  | 1863 | 1961 | 0.1221 | 0 | 125.2137 | 0 | 0.001221 | 0 | 1.2521 | 0 | 0.001221 | 1.2521 | 122569 | 19.6187 | 122568.9988
38961.5434 | 2 | 2 | 38961.5435 | 1957 | 1 |  | 1905 | 2003 | 0.1221 | 0.1221 | 119.475 | 0.06105 | 0.001221 | 0.001221 | 1.1947 | 0.0006105 | 0 | 1.1941 | 31104.6525 | 25.3773 | 24788.6064
38961.5439 | 2 | 2 | 38961.5439 | 2216 | 1 |  | 1947 | 2045 | 0.1221 | 0.1221 | 135.2869 | 0.06105 | 0.001221 | 0.001221 | 1.3529 | 0.0006105 | 0 | 1.3523 | 13135.5888 | 10.7169 | 11854.4438
38961.5444 | 2 | 2 | 38961.5444 | 2400 | 1 |  | 1989 | 2087 | 0.1221 | 0.1221 | 146.5201 | 0.06105 | 0.001221 | 0.001221 | 1.4652 | 0.0006105 | 0 | 1.4646 | 2727.2335 | 2.2251 | 2665.6952
38961.5449 | 62 | 1 | 38961.5449 | 1903 | 1 |  | 2031 | 2129 | 3.7851 | 0.06105 | 116.1783 | 0.06105 | 0.037851 | 0.0006105 | 1.1618 | 0.0006105 | 0.037241 | 1.1612 | 4155.7237 | 28.9373 | 53647.0797
38961.5454 | 2 | 1 |  | 1946 | 1 |  | 2072 | 2170 | 0.1221 | 0.06105 | 118.8034 | 0.06105 | 0.001221 | 0.0006105 | 1.188 | 0.0006105 | 0.0006105 | 1.1874 | 86516.6167 | 54.5428 | 86481.3236
38961.5459 | 55 | 1 | 38961.5459 | 1988 | 0 |  | 2115 | 2213 | 3.3578 | 0.06105 | 121.3675 | 0 | 0.033578 | 0.0006105 | 1.2137 | 0 | 0.032967 | 1.2137 | 4822.9756 | 23.4095 | 45475.7398
38961.5464 | 25 | 1 | 38961.5464 | 2155 | 1 |  | 2157 | 2255 | 1.5263 | 0.06105 | 131.5629 | 0.06105 | 0.015263 | 0.0006105 | 1.3156 | 0.0006105 | 0.014652 | 1.315 | 14470.9738 | 13.8524 | 29533.9093
38961.5468 | 2 | 1 | 38961.5469 | 2437 | 1 |  | 2198.5 | 2296.5 | 0.1221 | 0.06105 | 148.779 | 0.06105 | 0.001221 | 0.0006105 | 1.4878 | 0.0006105 | 0.0006105 | 1.4872 | 1659.4591 | 0.68156 | 1658.7822
38961.5473 | 2 | 1 | 38961.5473 | 1968 | 1 |  | 2241 | 2339 | 0.1221 | 0.06105 | 120.1465 | 0.06105 | 0.001221 | 0.0006105 | 1.2015 | 0.0006105 | 0.0006105 | 1.2009 | 80307.3544 | 48.7211 | 80274.5943
38961.5478 | 2 | 1 | 38961.5478 | 2437 | 1 |  | 2282.5 | 2380.5 | 0.1221 | 0.06105 | 148.779 | 0.06105 | 0.001221 | 0.0006105 | 1.4878 | 0.0006105 | 0.0006105 | 1.4872 | 1659.4591 | 0.68156 | 1658.7822
38961.5483 | 2 | 1 | 38961.5483 | 2436 | 1 |  | 2325 | 2423 | 0.1221 | 0.06105 | 148.7179 | 0.06105 | 0.001221 | 0.0006105 | 1.4872 | 0.0006105 | 0.0006105 | 1.4866 | 1762.2283 | 0.72408 | 1761.5095
38961.5488 | 5 | 1 | 38961.5488 | 2281 | 0 |  | 2367 | 2465 | 0.30525 | 0.06105 | 139.2552 | 0 | 0.0030525 | 0.0006105 | 1.3926 | 0 | 0.002442 | 1.3926 | 26519.4501 | 19.1117 | 39268.7012
38961.5493 | 2288 | 0 | 38961.5493 | 2034 | 0 |  | 2409 | 2507 | 139.6825 | 0 | 124.1758 | 0 | 1.3968 | 0 | 1.2418 | 0 | 1.3968 | 1.2418 | 7.2281 | 20.6185 | 5.8313
38961.5498 | 1847 | 0 | 38961.5498 | 1916 | 0 |  | 2451 | 2549 | 112.7595 | 0 | 116.9719 | 0 | 1.1276 | 0 | 1.1697 | 0 | 1.1276 | 1.1697 | 32.8305 | 28.047 | 31.7029
38961.5502 | 2006 | 1 | 38961.5503 | 2001 | 0 |  | 2492.5 | 2590.5 | 122.4664 | 0.06105 | 122.1612 | 0 | 1.2247 | 0.0006105 | 1.2216 | 0 | 1.2241 | 1.2216 | 22.3626 | 22.6077 | 8230.8238
38961.5507 | 186 | 1 | 38961.5508 | 2327 | 1 |  | 2535 | 2633 | 11.3553 | 0.06105 | 142.0635 | 0.06105 | 0.11355 | 0.0006105 | 1.4206 | 0.0006105 | 0.11294 | 1.42 | 1361.0069 | 5.4335 | 11679.8247
38961.5512 | 31 | 1 | 38961.5512 | 2119 | 0 |  | 2577 | 2675 | 1.8926 | 0.06105 | 129.3651 | 0 | 0.018926 | 0.0006105 | 1.2937 | 0 | 0.018315 | 1.2937 | 10237.0384 | 15.7801 | 33001.8605
38961.5517 | 74 | 0 | 38961.5517 | 2051 | 0 |  | 2619 | 2717 | 4.5177 | 0 | 125.2137 | 0 | 0.045177 | 0 | 1.2521 | 0 | 0.045177 | 1.2521 | 3215.3784 | 19.6187 | 3215.3332
38961.5522 | 145 | 1 | 38961.5522 | 2404 | 0 |  | 2660.5 | 2758.5 | 8.8523 | 0.06105 | 146.7643 | 0 | 0.088523 | 0.0006105 | 1.4676 | 0 | 0.087912 | 1.4676 | 2421.8098 | 2.0541 | 4644.1409
38961.5527 | 168 | 1 | 38961.5527 | 2301 | 0 |  | 2703 | 2801 | 10.2564 | 0.06105 | 140.4762 | 0 | 0.10256 | 0.0006105 | 1.4048 | 0 | 0.10195 | 1.4048 | 1504.5333 | 6.6223 | 14188.3371
38961.5532 | 403 | 1 | 38961.5532 | 2191 | 0 |  | 2744.5 | 2842.5 | 24.6032 | 0.06105 | 133.7607 | 0 | 0.24603 | 0.0006105 | 1.3376 | 0 | 0.24542 | 1.3376 | 520.8644 | 11.9754 | 21917.3681
38961.5536 | 531 | 1 | 38961.5537 | 2384 | 0 |  | 2786.5 | 2884.5 | 32.4176 | 0.06105 | 145.5433 | 0 | 0.32418 | 0.0006105 | 1.4554 | 0 | 0.32357 | 1.4554 | 387.8593 | 2.9102 | 5433.5384
38961.5541 | 580 | 1 | 38961.5541 | 2270 | 0 |  | 2828.5 | 2926.5 | 35.409 | 0.06105 | 138.5836 | 0 | 0.35409 | 0.0006105 | 1.3858 | 0 | 0.35348 | 1.3858 | 330.6229 | 8.0784 | 13995.2655
38961.5546 | 643 | 1 | 38961.5546 | 1931 | 0 |  | 2870.5 | 2968.5 | 39.2552 | 0.06105 | 117.8877 | 0 | 0.39255 | 0.0006105 | 1.1789 | 0 | 0.39194 | 1.1789 | 283.6237 | 27.0523 | 38525.7858
38961.5551 | 758 | 1 | 38961.5551 | 2292 | 0 |  | 2912.5 | 3010.5 | 46.2759 | 0.06105 | 139.9267 | 0 | 0.46276 | 0.0006105 | 1.3993 | 0 | 0.46215 | 1.3993 | 228.2426 | 7.041 | 11145.4012

## B3-B4
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 141.9035 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38961.5206 | 1 | 0 | 38961.5206 | 1 | 0 |  | -71.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5211 | 1 | 0 | 38961.5211 | 1 | 0 |  | -29.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5215 | 1 | 0 | 38961.5216 | 1 | 0 |  | 12.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.522 | 1 | 0 | 38961.522 | 1 | 0 |  | 54.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5225 | 1 | 0 | 38961.5225 | 1 | 0 |  | 96.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.523 | 1 | 0 | 38961.523 | 1 | 0 |  | 138.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5235 | 1 | 0 | 38961.5235 | 1 | 0 |  | 180.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.524 | 1 | 0 | 38961.524 | 1 | 0 |  | 222.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5245 | 1 | 0 | 38961.5245 | 1 | 0 |  | 264.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5249 | 1 | 0 | 38961.525 | 1 | 0 |  | 306.5 | 404.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5254 | 1 | 0 | 38961.5254 | 1 | 0 |  | 348.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5259 | 1 | 0 | 38961.5259 | 1 | 0 |  | 390.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5264 | 1 | 0 | 38961.5264 | 1 | 0 |  | 432.5 | 530.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5269 | 1 | 0 | 38961.5269 | 1 | 0 |  | 474.5 | 572.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5274 | 1 | 0 | 38961.5274 | 1 | 0 |  | 516.5 | 614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5279 | 1 | 0 | 38961.5279 | 1 | 0 |  | 558.5 | 656.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5283 | 1 | 0 | 38961.5284 | 1 | 0 |  | 600.5 | 698.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5288 | 1 | 0 | 38961.5288 | 1 | 0 |  | 642.5 | 740.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5293 | 1 | 0 | 38961.5293 | 1 | 0 |  | 684.5 | 782.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5298 | 1 | 0 | 38961.5298 | 1 | 0 |  | 726.5 | 824.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5303 | 1 | 0 | 38961.5303 | 1 | 0 |  | 768.5 | 866.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5308 | 1 | 0 | 38961.5308 | 1 | 0 |  | 810.5 | 908.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5312 | 1 | 0 | 38961.5313 | 1 | 0 |  | 852 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5317 | 1 | 0 | 38961.5318 | 1 | 0 |  | 894.5 | 992.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5322 | 1 | 0 | 38961.5322 | 1 | 0 |  | 936 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5327 | 1 | 0 | 38961.5327 | 1 | 0 |  | 978.5 | 1076.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5332 | 1 | 0 | 38961.5332 | 1 | 0 |  | 1020 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5337 | 1 | 0 | 38961.5337 | 1 | 0 |  | 1062.5 | 1160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5342 | 1 | 0 | 38961.5342 | 1 | 0 |  | 1104.5 | 1202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5347 | 1 | 0 | 38961.5347 | 1 | 0 |  | 1146.5 | 1244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5351 | 1 | 0 | 38961.5352 | 1 | 0 |  | 1188 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5356 | 1 | 0 | 38961.5356 | 1 | 0 |  | 1230 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5361 | 1 | 0 | 38961.5361 | 1 | 0 |  | 1272 | 1370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5366 | 1 | 0 | 38961.5366 | 1 | 0 |  | 1314 | 1412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5371 | 1 | 0 | 38961.5371 | 1 | 0 |  | 1356 | 1454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5376 | 1 | 0 | 38961.5376 | 1 | 0 |  | 1398 | 1496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5381 | 1 | 0 | 38961.5381 | 1 | 0 |  | 1440 | 1538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5385 | 1 | 0 | 38961.5386 | 1 | 0 |  | 1482 | 1580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.539 | 1 | 0 | 38961.5391 | 1 | 0 |  | 1524 | 1622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5395 | 1 | 0 | 38961.5395 | 1 | 0 |  | 1566 | 1664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.54 | 1 | 0 | 38961.54 | 1 | 0 |  | 1608 | 1706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5405 | 1 | 0 | 38961.5405 | 1 | 0 |  | 1650 | 1748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.541 | 1 | 0 | 38961.541 | 1 | 0 |  | 1692 | 1790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5415 | 1 | 0 | 38961.5415 | 1 | 0 |  | 1734 | 1832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232338 | 232338 | 232337.9994
38961.5419 | 2 | 0 | 38961.542 | 2 | 0 |  | 1776 | 1874 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 116119 | 116119 | 116118.9988
38961.5424 | 2 | 0 | 38961.5425 | 2 | 0 |  | 1818 | 1916 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 116119 | 116119 | 116118.9988
38961.5429 | 2 | 0 | 38961.5429 | 2 | 0 |  | 1860 | 1958 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 116119 | 116119 | 116118.9988
38961.5434 | 1179 | 1189 | 38961.5434 | 1019 | 1107 |  | 1902 | 2000 | 71.978 | 72.5885 | 62.21 | 67.5824 | 0.71978 | 0.72589 | 0.6221 | 0.67582 | 0.006105 | 0.053724 | 195.3884 | 206.3495 | 2.4711
38961.5439 | 1177 | 1138 | 38961.5439 | 1083 | 1046 |  | 1944 | 2042 | 71.8559 | 69.475 | 66.1172 | 63.8584 | 0.71856 | 0.69475 | 0.66117 | 0.63858 | 0.02381 | 0.022589 | 3709.4683 | 14103.5637 | 0.81845
38961.5444 | 1144 | 1102 | 38961.5444 | 1004 | 967 |  | 1986 | 2084 | 69.8413 | 67.2772 | 61.2943 | 59.0354 | 0.69841 | 0.67277 | 0.61294 | 0.59035 | 0.025641 | 0.022589 | 3357.2912 | 16108.0549 | 7.0686
38961.5449 | 1017 | 975 | 38961.5449 | 1206 | 1177 |  | 2028 | 2126 | 62.0879 | 59.5238 | 73.6264 | 71.8559 | 0.62088 | 0.59524 | 0.73626 | 0.71856 | 0.025641 | 0.017705 | 1682.4802 | 2730.6701 | 32.8859
38961.5453 | 1089 | 1146 | 38961.5454 | 1198 | 1116 |  | 2070 | 2168 | 66.4835 | 69.9634 | 73.138 | 68.1319 | 0.66484 | 0.69963 | 0.73138 | 0.68132 | 0.034799 | 0.050061 | 378.1579 | 424.9423 | 6.3136
38961.5458 | 1012 | 971 | 38961.5459 | 1004 | 915 |  | 2112 | 2210 | 61.7827 | 59.2796 | 61.2943 | 55.8608 | 0.61783 | 0.5928 | 0.61294 | 0.55861 | 0.025031 | 0.054335 | 2615.5076 | 10580.9431 | 34.8284
38961.5463 | 472 | 472 | 38961.5463 | 927 | 943 |  | 2154 | 2252 | 28.8156 | 28.8156 | 56.5934 | 57.5702 | 0.28816 | 0.28816 | 0.56593 | 0.5757 | 0 | 0.009768 | 28381.6574 | 7231.8543 | 288.4646
38961.5468 | 1000 | 961 | 38961.5468 | 1031 | 991 |  | 2196 | 2294 | 61.0501 | 58.6691 | 62.9426 | 60.5006 | 0.6105 | 0.58669 | 0.62943 | 0.60501 | 0.02381 | 0.02442 | 6337.1689 | 5308.9836 | 37.1136
38961.5473 | 1100 | 1056 | 38961.5473 | 1183 | 1161 |  | 2238 | 2336 | 67.1551 | 64.4689 | 72.2222 | 70.8791 | 0.67155 | 0.64469 | 0.72222 | 0.70879 | 0.026862 | 0.013431 | 635.3278 | 710.077 | 13.9767
38961.5478 | 1023 | 979 | 38961.5478 | 1107 | 1061 |  | 2280 | 2378 | 62.4542 | 59.768 | 67.5824 | 64.7741 | 0.62454 | 0.59768 | 0.67582 | 0.64774 | 0.026862 | 0.028083 | 6395.181 | 4139.4272 | 32.1528
38961.5483 | 1094 | 1122 | 38961.5483 | 1171 | 1176 |  | 2322 | 2420 | 66.7888 | 68.4982 | 71.4896 | 71.7949 | 0.66789 | 0.68498 | 0.7149 | 0.71795 | 0.017094 | 0.0030525 | 373.3372 | 372.062 | 7.6133
38961.5488 | 629 | 619 | 38961.5488 | 949 | 944 |  | 2364 | 2462 | 38.4005 | 37.79 | 57.9365 | 57.6313 | 0.384 | 0.3779 | 0.57937 | 0.57631 | 0.006105 | 0.0030525 | 16394.4885 | 181440.7377 | 173.7944
38961.5492 | 2275 | 77 | 38961.5493 | 2308 | 66 |  | 2406 | 2504 | 138.8889 | 4.7009 | 140.9035 | 4.0293 | 1.3889 | 0.047009 | 1.409 | 0.040293 | 1.3419 | 1.3687 | 3.1275 | 12.4371 | 3.9677
38961.5497 | 1927 | 41 | 38961.5497 | 2080 | 38 |  | 2448 | 2546 | 117.6435 | 2.5031 | 126.9841 | 2.3199 | 1.1764 | 0.025031 | 1.2698 | 0.023199 | 1.1514 | 1.2466 | 25.3338 | 12.9165 | 99.4297
38961.5502 | 1866 | 684 | 38961.5502 | 1607 | 737 |  | 2490 | 2588 | 113.9194 | 41.7582 | 98.1074 | 44.9939 | 1.1392 | 0.41758 | 0.98107 | 0.44994 | 0.72161 | 0.53114 | 69.3163 | 131.3585 | 18.7281
38961.5507 | 1203 | 1164 | 38961.5507 | 1115 | 1063 |  | 2532 | 2630 | 73.4432 | 71.0623 | 68.0708 | 64.8962 | 0.73443 | 0.71062 | 0.68071 | 0.64896 | 0.02381 | 0.031746 | 889.3949 | 1336.6485 | 3.4066
38961.5512 | 1239 | 1153 | 38961.5512 | 1255 | 1147 |  | 2574 | 2672 | 75.641 | 70.3907 | 76.6178 | 70.0244 | 0.75641 | 0.70391 | 0.76618 | 0.70024 | 0.052503 | 0.065934 | 496.9922 | 870.9133 | 5.2607
38961.5517 | 691 | 547 | 38961.5517 | 437 | 344 |  | 2616 | 2714 | 42.1856 | 33.3944 | 26.6789 | 21.0012 | 0.42186 | 0.33394 | 0.26679 | 0.21001 | 0.087912 | 0.056777 | 1310.3156 | 2827.6719 | 191.8232
38961.5522 | 1237 | 1051 | 38961.5522 | 1198 | 853 |  | 2658 | 2756 | 75.5189 | 64.1636 | 73.138 | 52.0757 | 0.75519 | 0.64164 | 0.73138 | 0.52076 | 0.11355 | 0.21062 | 214.4514 | 327.3614 | 2.6515
38961.5526 | 1234 | 870 | 38961.5527 | 1329 | 912 |  | 2700 | 2798 | 75.3358 | 53.1136 | 81.1355 | 55.6777 | 0.75336 | 0.53114 | 0.81136 | 0.55678 | 0.22222 | 0.25458 | 61885.6946 | 240.1735 | 17.8845
38961.5531 | 1054 | 797 | 38961.5531 | 1125 | 856 |  | 2742 | 2840 | 64.3468 | 48.6569 | 68.6813 | 52.2589 | 0.64347 | 0.48657 | 0.68681 | 0.52259 | 0.1569 | 0.16422 | 896.5981 | 691.1737 | 51.888
38961.5536 | 1392 | 903 | 38961.5536 | 1344 | 876 |  | 2784 | 2882 | 84.9817 | 55.1282 | 82.0513 | 53.4799 | 0.84982 | 0.55128 | 0.82051 | 0.5348 | 0.29853 | 0.28571 | 216.6457 | 1540.1898 | 3.0552
38961.5541 | 1158 | 743 | 38961.5541 | 1351 | 930 |  | 2826 | 2924 | 70.696 | 45.3602 | 82.4786 | 56.7766 | 0.70696 | 0.4536 | 0.82479 | 0.56777 | 0.25336 | 0.25702 | 487.4848 | 422.7954 | 46.0829
38961.5546 | 1302 | 807 | 38961.5546 | 1139 | 719 |  | 2868 | 2966 | 79.4872 | 49.2674 | 69.536 | 43.895 | 0.79487 | 0.49267 | 0.69536 | 0.43895 | 0.3022 | 0.25641 | 254.8898 | 859.486 | 23.9074
38961.5551 | 1116 | 724 | 38961.5551 | 1400 | 864 |  | 2910 | 3008 | 68.1319 | 44.2002 | 85.4701 | 52.7473 | 0.68132 | 0.442 | 0.8547 | 0.52747 | 0.23932 | 0.32723 | 1911.7966 | 220.199 | 46.009

## A2-C6
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 152.4652 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38961.5205 | 1 | 0 | 38961.5205 | 1 | 0 |  | -74.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.521 | 1 | 0 | 38961.521 | 1 | 0 |  | -32.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5215 | 1 | 0 | 38961.5215 | 1 | 0 |  | 9.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.522 | 1 | 0 | 38961.522 | 1 | 0 |  | 51.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5225 | 1 | 0 | 38961.5225 | 1 | 0 |  | 93.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.523 | 1 | 0 | 38961.523 | 1 | 0 |  | 135.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5234 | 1 | 0 | 38961.5235 | 1 | 0 |  | 177.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5239 | 1 | 0 | 38961.5239 | 1 | 0 |  | 219.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5244 | 1 | 0 | 38961.5244 | 1 | 0 |  | 261.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5249 | 1 | 0 | 38961.5249 | 1 | 0 |  | 303.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5254 | 1 | 0 | 38961.5254 | 1 | 0 |  | 345.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5259 | 1 | 0 | 38961.5259 | 1 | 0 |  | 387.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5264 | 1 | 0 | 38961.5264 | 1 | 0 |  | 429.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5269 | 1 | 0 | 38961.5269 | 1 | 0 |  | 471.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5273 | 1 | 0 | 38961.5273 | 1 | 0 |  | 513.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5278 | 1 | 0 | 38961.5278 | 1 | 0 |  | 555.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5283 | 1 | 0 | 38961.5283 | 1 | 0 |  | 597.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5288 | 1 | 0 | 38961.5288 | 1 | 0 |  | 639.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5293 | 1 | 0 | 38961.5293 | 1 | 0 |  | 681.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5298 | 1 | 0 | 38961.5298 | 1 | 0 |  | 723.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5303 | 1 | 0 | 38961.5303 | 1 | 0 |  | 765.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5307 | 1 | 0 | 38961.5308 | 1 | 0 |  | 807.5 | 905.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5312 | 1 | 0 | 38961.5312 | 1 | 0 |  | 849.5 | 947.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5317 | 1 | 0 | 38961.5317 | 1 | 0 |  | 891.5 | 989.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5322 | 1 | 0 | 38961.5322 | 1 | 0 |  | 933.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5327 | 1 | 0 | 38961.5327 | 1 | 0 |  | 975.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5332 | 1 | 0 | 38961.5332 | 1 | 0 |  | 1017.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5337 | 1 | 0 | 38961.5337 | 1 | 0 |  | 1059.5 | 1157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5341 | 1 | 0 | 38961.5342 | 1 | 0 |  | 1101.5 | 1199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5346 | 1 | 0 | 38961.5346 | 1 | 0 |  | 1143.5 | 1241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5351 | 1 | 0 | 38961.5351 | 1 | 0 |  | 1185.5 | 1283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5356 | 1 | 0 | 38961.5356 | 1 | 0 |  | 1227.5 | 1325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5361 | 1 | 0 | 38961.5361 | 1 | 0 |  | 1269.5 | 1367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5366 | 1 | 0 | 38961.5366 | 1 | 0 |  | 1311.5 | 1409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5371 | 1 | 0 | 38961.5371 | 1 | 0 |  | 1353.5 | 1451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5375 | 1 | 0 | 38961.5376 | 1 | 0 |  | 1395.5 | 1493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.538 | 1 | 0 | 38961.538 | 1 | 0 |  | 1437.5 | 1535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5385 | 1 | 0 | 38961.5385 | 1 | 0 |  | 1479.5 | 1577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.539 | 1 | 0 | 38961.539 | 1 | 0 |  | 1521.5 | 1619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5395 | 1 | 0 | 38961.5395 | 1 | 0 |  | 1563.5 | 1661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.54 | 1 | 0 | 38961.54 | 1 | 0 |  | 1605.5 | 1703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5405 | 1 | 0 | 38961.5405 | 1 | 0 |  | 1647.5 | 1745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5409 | 1 | 0 | 38961.541 | 1 | 0 |  | 1689.5 | 1787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5414 | 1 | 0 | 38961.5414 | 1 | 0 |  | 1731.5 | 1829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38961.5419 | 2 | 0 | 38961.5419 | 2050 | 0 |  | 1773.5 | 1871.5 | 0.1221 | 0 | 125.1526 | 0 | 0.001221 | 0 | 1.2515 | 0 | 0.001221 | 1.2515 | 124769 | 21.8234 | 124768.9988
38961.5424 | 2 | 0 | 38961.5424 | 1972 | 0 |  | 1815.5 | 1913.5 | 0.1221 | 0 | 120.3907 | 0 | 0.001221 | 0 | 1.2039 | 0 | 0.001221 | 1.2039 | 124769 | 26.642 | 124768.9988
38961.5429 | 2 | 0 | 38961.5429 | 1980 | 0 |  | 1857.5 | 1955.5 | 0.1221 | 0 | 120.8791 | 0 | 0.001221 | 0 | 1.2088 | 0 | 0.001221 | 1.2088 | 124769 | 26.1303 | 124768.9988
38961.5434 | 2 | 0 | 38961.5434 | 2128 | 0 |  | 1899.5 | 1997.5 | 0.1221 | 0 | 129.9145 | 0 | 0.001221 | 0 | 1.2991 | 0 | 0.001221 | 1.2991 | 124769 | 17.3581 | 124768.9988
38961.5439 | 1951 | 11 | 38961.5439 | 2105 | 13 |  | 1941.5 | 2039.5 | 119.1087 | 0.67155 | 128.5104 | 0.79365 | 1.1911 | 0.0067155 | 1.2851 | 0.0079365 | 1.1844 | 1.2772 | 29.0225 | 19.1666 | 782.8165
38961.5444 | 1987 | 7 | 38961.5444 | 2283 | 2 |  | 1983.5 | 2081.5 | 121.3065 | 0.42735 | 139.3773 | 0.1221 | 1.2131 | 0.0042735 | 1.3938 | 0.001221 | 1.2088 | 1.3926 | 26.7809 | 9.4294 | 619.651
38961.5448 | 3 | 0 | 38961.5448 | 1874 | 0 |  | 2025.5 | 2123.5 | 0.18315 | 0 | 114.4078 | 0 | 0.0018315 | 0 | 1.1441 | 0 | 0.0018315 | 1.1441 | 83146 | 33.2647 | 83145.9982
38961.5453 | 9 | 0 | 38961.5453 | 1915 | 0 |  | 2067.5 | 2165.5 | 0.54945 | 0 | 116.9109 | 0 | 0.0054945 | 0 | 1.1691 | 0 | 0.0054945 | 1.1691 | 27648.6667 | 30.4115 | 27648.6612
38961.5458 | 2043 | 4 | 38961.5458 | 2435 | 5 |  | 2109.5 | 2207.5 | 124.7253 | 0.2442 | 148.6569 | 0.30525 | 1.2473 | 0.002442 | 1.4866 | 0.0030525 | 1.2448 | 1.4835 | 24.1113 | 2.5892 | 284.1704
38961.5463 | 2295 | 3 | 38961.5463 | 1896 | 3 |  | 2151.5 | 2249.5 | 140.1099 | 0.18315 | 115.7509 | 0.18315 | 1.4011 | 0.0018315 | 1.1575 | 0.0018315 | 1.3993 | 1.1557 | 8.8657 | 32.3468 | 1624.3461
38961.5468 | 2395 | 3 | 38961.5468 | 2100 | 3 |  | 2193 | 2291 | 146.2149 | 0.18315 | 128.2051 | 0.18315 | 1.4621 | 0.0018315 | 1.2821 | 0.0018315 | 1.4603 | 1.2802 | 4.3077 | 19.6009 | 542.8992
38961.5473 | 1935 | 2 | 38961.5473 | 2353 | 2 |  | 2235.5 | 2333.5 | 118.1319 | 0.1221 | 143.6508 | 0.1221 | 1.1813 | 0.001221 | 1.4365 | 0.001221 | 1.1801 | 1.4353 | 29.5907 | 6.1589 | 1625.5521
38961.5478 | 2448 | 2 | 38961.5478 | 2391 | 2 |  | 2277.5 | 2375.5 | 149.4505 | 0.1221 | 145.9707 | 0.1221 | 1.4945 | 0.001221 | 1.4597 | 0.001221 | 1.4933 | 1.4585 | 2.055 | 4.642 | 105.091
38961.5482 | 2153 | 2 | 38961.5483 | 2364 | 2 |  | 2319.5 | 2417.5 | 131.4408 | 0.1221 | 144.3223 | 0.1221 | 1.3144 | 0.001221 | 1.4432 | 0.001221 | 1.3132 | 1.442 | 16.2768 | 5.6764 | 919.5518
38961.5487 | 2057 | 2 | 38961.5487 | 2205 | 2 |  | 2361 | 2459 | 125.58 | 0.1221 | 134.6154 | 0.1221 | 1.2558 | 0.001221 | 1.3462 | 0.001221 | 1.2546 | 1.3449 | 21.5873 | 13.328 | 2577.7876
38961.5492 | 2051 | 2 | 38961.5492 | 2081 | 1 |  | 2403.5 | 2501.5 | 125.2137 | 0.1221 | 127.0452 | 0.06105 | 1.2521 | 0.001221 | 1.2705 | 0.0006105 | 1.2509 | 1.2698 | 21.8918 | 20.0623 | 3712.7789
38961.5497 | 2326 | 2 | 38961.5497 | 2272 | 1 |  | 2445.5 | 2543.5 | 142.0024 | 0.1221 | 138.7057 | 0.06105 | 1.42 | 0.001221 | 1.3871 | 0.0006105 | 1.4188 | 1.3864 | 7.4385 | 9.9834 | 768.7443
38961.5502 | 2068 | 1 | 38961.5502 | 2019 | 1 |  | 2487 | 2585 | 126.2515 | 0.06105 | 123.2601 | 0.06105 | 1.2625 | 0.0006105 | 1.2326 | 0.0006105 | 1.2619 | 1.232 | 20.8155 | 23.7622 | 8224.8518
38961.5507 | 2390 | 2 | 38961.5507 | 1957 | 1 |  | 2529 | 2627 | 145.9096 | 0.1221 | 119.475 | 0.06105 | 1.4591 | 0.001221 | 1.1947 | 0.0006105 | 1.4579 | 1.1941 | 4.5102 | 27.9435 | 1150.7773
38961.5512 | 2106 | 0 | 38961.5512 | 2192 | 2 |  | 2571.5 | 2669.5 | 128.5714 | 0 | 133.8217 | 0.1221 | 1.2857 | 0 | 1.3382 | 0.001221 | 1.2857 | 1.337 | 18.584 | 14.0356 | 17.2983
38961.5516 | 2187 | 1 | 38961.5517 | 2314 | 1 |  | 2613.5 | 2711.5 | 133.5165 | 0.06105 | 141.2698 | 0.06105 | 1.3352 | 0.0006105 | 1.4127 | 0.0006105 | 1.3346 | 1.4121 | 14.2807 | 7.9523 | 2279.0478
38961.5521 | 2356 | 1 | 38961.5521 | 2068 | 1 |  | 2655 | 2753 | 143.8339 | 0.06105 | 126.2515 | 0.06105 | 1.4383 | 0.0006105 | 1.2625 | 0.0006105 | 1.4377 | 1.2619 | 6.0156 | 20.9415 | 2430.7372
38961.5526 | 1922 | 1 | 38961.5526 | 2380 | 1 |  | 2697 | 2795 | 117.3382 | 0.06105 | 145.2991 | 0.06105 | 1.1734 | 0.0006105 | 1.453 | 0.0006105 | 1.1728 | 1.4524 | 30.271 | 4.9409 | 2704.3183
38961.5531 | 2350 | 1 | 38961.5531 | 2474 | 1 |  | 2739 | 2837 | 143.4676 | 0.06105 | 151.0379 | 0.06105 | 1.4347 | 0.0006105 | 1.5104 | 0.0006105 | 1.4341 | 1.5098 | 6.5681 | 0.95127 | 137.9343
38961.5536 | 2481 | 1 | 38961.5536 | 1963 | 1 |  | 2781 | 2879 | 151.4652 | 0.06105 | 119.8413 | 0.06105 | 1.5147 | 0.0006105 | 1.1984 | 0.0006105 | 1.514 | 1.1978 | 0.66139 | 29.5107 | 350.4531
38961.5541 | 2015 | 1 | 38961.5541 | 2130 | 1 |  | 2823 | 2921 | 123.0159 | 0.06105 | 130.0366 | 0.06105 | 1.2302 | 0.0006105 | 1.3004 | 0.0006105 | 1.2295 | 1.2998 | 24.0203 | 17.2898 | 7096.0673
38961.5545 | 2397 | 1 | 38961.5546 | 1912 | 1 |  | 2865 | 2963 | 146.337 | 0.06105 | 116.7277 | 0.06105 | 1.4634 | 0.0006105 | 1.1673 | 0.0006105 | 1.4628 | 1.1667 | 4.1951 | 31.0191 | 2352.8436
38961.555 | 2065 | 1 | 38961.5551 | 2024 | 1 |  | 2907 | 3005 | 126.0684 | 0.06105 | 123.5653 | 0.06105 | 1.2607 | 0.0006105 | 1.2357 | 0.0006105 | 1.2601 | 1.235 | 20.992 | 23.4551 | 8195.7509

## A2-C5
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 152.5263 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38961.5205 | 1 | 0 | 38961.5205 | 1 | 0 |  | -77 | 21 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.521 | 1 | 0 | 38961.521 | 1 | 0 |  | -35.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5215 | 1 | 0 | 38961.5215 | 1 | 0 |  | 6.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.522 | 1 | 0 | 38961.522 | 1 | 0 |  | 48.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5224 | 1 | 0 | 38961.5225 | 1 | 0 |  | 90.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5229 | 1 | 0 | 38961.5229 | 1 | 0 |  | 132.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5234 | 1 | 0 | 38961.5234 | 1 | 0 |  | 175 | 273 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5239 | 1 | 0 | 38961.5239 | 1 | 0 |  | 216.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5244 | 1 | 0 | 38961.5244 | 1 | 0 |  | 258.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5249 | 1 | 0 | 38961.5249 | 1 | 0 |  | 300.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5254 | 1 | 0 | 38961.5254 | 1 | 0 |  | 342.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5258 | 1 | 0 | 38961.5259 | 1 | 0 |  | 384.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5263 | 1 | 0 | 38961.5263 | 1 | 0 |  | 426.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5268 | 1 | 0 | 38961.5268 | 1 | 0 |  | 468.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5273 | 1 | 0 | 38961.5273 | 1 | 0 |  | 510.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5278 | 1 | 0 | 38961.5278 | 1 | 0 |  | 552.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5283 | 1 | 0 | 38961.5283 | 1 | 0 |  | 594.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5288 | 1 | 0 | 38961.5288 | 1 | 0 |  | 636.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5292 | 1 | 0 | 38961.5293 | 1 | 0 |  | 678.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5297 | 1 | 0 | 38961.5297 | 1 | 0 |  | 720.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5302 | 1 | 0 | 38961.5302 | 1 | 0 |  | 762.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5307 | 1 | 0 | 38961.5307 | 1 | 0 |  | 804.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5312 | 1 | 0 | 38961.5312 | 1 | 0 |  | 846.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5317 | 1 | 0 | 38961.5317 | 1 | 0 |  | 888.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5322 | 1 | 0 | 38961.5322 | 1 | 0 |  | 930.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5327 | 1 | 0 | 38961.5327 | 1 | 0 |  | 972.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5331 | 1 | 0 | 38961.5331 | 1 | 0 |  | 1014.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5336 | 1 | 0 | 38961.5336 | 1 | 0 |  | 1056.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5341 | 1 | 0 | 38961.5341 | 1 | 0 |  | 1098.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5346 | 1 | 0 | 38961.5346 | 1 | 0 |  | 1140.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5351 | 1 | 0 | 38961.5351 | 1 | 0 |  | 1182.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5356 | 1 | 0 | 38961.5356 | 1 | 0 |  | 1224.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5361 | 1 | 0 | 38961.5361 | 1 | 0 |  | 1266.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5365 | 1 | 0 | 38961.5366 | 1 | 0 |  | 1308.5 | 1406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.537 | 1 | 0 | 38961.537 | 1 | 0 |  | 1350.5 | 1448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5375 | 1 | 0 | 38961.5375 | 1 | 0 |  | 1392.5 | 1490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.538 | 1 | 0 | 38961.538 | 1 | 0 |  | 1434.5 | 1532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5385 | 1 | 0 | 38961.5385 | 1 | 0 |  | 1476.5 | 1574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.539 | 1 | 0 | 38961.539 | 1 | 0 |  | 1518.5 | 1616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5395 | 1 | 0 | 38961.5395 | 1 | 0 |  | 1560.5 | 1658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5399 | 1 | 0 | 38961.54 | 1 | 0 |  | 1602.5 | 1700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5404 | 1 | 0 | 38961.5404 | 1 | 0 |  | 1644.5 | 1742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5409 | 1 | 0 | 38961.5409 | 1 | 0 |  | 1686.5 | 1784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38961.5414 | 1 | 0 | 38961.5414 | 303 | 0 |  | 1728.5 | 1826.5 | 0.06105 | 0 | 18.4982 | 0 | 0.0006105 | 0 | 0.18498 | 0 | 0.0006105 | 0.18498 | 249738 | 724.5479 | 249737.9994
38961.5419 | 1 | 0 | 38961.5419 | 1972 | 0 |  | 1770.5 | 1868.5 | 0.06105 | 0 | 120.3907 | 0 | 0.0006105 | 0 | 1.2039 | 0 | 0.0006105 | 1.2039 | 249738 | 26.6927 | 249737.9994
38961.5424 | 2 | 0 | 38961.5424 | 2316 | 0 |  | 1812.5 | 1910.5 | 0.1221 | 0 | 141.3919 | 0 | 0.001221 | 0 | 1.4139 | 0 | 0.001221 | 1.4139 | 124819 | 7.8748 | 124818.9988
38961.5429 | 2 | 0 | 38961.5429 | 1974 | 0 |  | 1854.5 | 1952.5 | 0.1221 | 0 | 120.5128 | 0 | 0.001221 | 0 | 1.2051 | 0 | 0.001221 | 1.2051 | 124819 | 26.5643 | 124818.9988
38961.5433 | 2 | 0 | 38961.5434 | 2348 | 12 |  | 1896.5 | 1994.5 | 0.1221 | 0 | 143.3455 | 0.7326 | 0.001221 | 0 | 1.4335 | 0.007326 | 0.001221 | 1.4261 | 124819 | 6.9512 | 124818.9988
38961.5438 | 2031 | 13 | 38961.5438 | 2124 | 13 |  | 1938.5 | 2036.5 | 123.9927 | 0.79365 | 129.6703 | 0.79365 | 1.2399 | 0.0079365 | 1.2967 | 0.0079365 | 1.232 | 1.2888 | 24.0103 | 18.2016 | 538.2218
38961.5443 | 2396 | 8 | 38961.5443 | 2172 | 9 |  | 1980.5 | 2078.5 | 146.2759 | 0.4884 | 132.6007 | 0.54945 | 1.4628 | 0.004884 | 1.326 | 0.0054945 | 1.4579 | 1.3205 | 4.3752 | 16.6751 | 168.6085
38961.5448 | 2 | 0 | 38961.5448 | 2271 | 0 |  | 2022.5 | 2120.5 | 0.1221 | 0 | 138.6447 | 0 | 0.001221 | 0 | 1.3864 | 0 | 0.001221 | 1.3864 | 124819 | 10.0123 | 124818.9988
38961.5453 | 2 | 0 | 38961.5453 | 2138 | 0 |  | 2064.5 | 2162.5 | 0.1221 | 0 | 130.525 | 0 | 0.001221 | 0 | 1.3053 | 0 | 0.001221 | 1.3053 | 124819 | 16.8559 | 124818.9988
38961.5458 | 2251 | 5 | 38961.5458 | 2272 | 5 |  | 2106.5 | 2204.5 | 137.4237 | 0.30525 | 138.7057 | 0.30525 | 1.3742 | 0.0030525 | 1.3871 | 0.0030525 | 1.3712 | 1.384 | 11.2604 | 10.1854 | 448.1054
38961.5463 | 2221 | 4 | 38961.5463 | 2057 | 3 |  | 2148.5 | 2246.5 | 135.5922 | 0.2442 | 125.58 | 0.18315 | 1.3559 | 0.002442 | 1.2558 | 0.0018315 | 1.3535 | 1.254 | 12.6162 | 21.7405 | 1220.5091
38961.5467 | 2172 | 3 | 38961.5468 | 2362 | 3 |  | 2190.5 | 2288.5 | 132.6007 | 0.18315 | 144.2002 | 0.18315 | 1.326 | 0.0018315 | 1.442 | 0.0018315 | 1.3242 | 1.4402 | 15.4132 | 5.8294 | 593.7541
38961.5472 | 2175 | 4 | 38961.5472 | 2047 | 2 |  | 2232.5 | 2330.5 | 132.7839 | 0.2442 | 124.9695 | 0.1221 | 1.3278 | 0.002442 | 1.2497 | 0.001221 | 1.3254 | 1.2485 | 15.02 | 22.217 | 1451.4499
38961.5477 | 2200 | 2 | 38961.5477 | 1925 | 1 |  | 2274.5 | 2372.5 | 134.3101 | 0.1221 | 117.5214 | 0.06105 | 1.3431 | 0.001221 | 1.1752 | 0.0006105 | 1.3419 | 1.1746 | 13.6165 | 29.9156 | 3412.3677
38961.5482 | 2168 | 2 | 38961.5482 | 2269 | 2 |  | 2316.5 | 2414.5 | 132.3565 | 0.1221 | 138.5226 | 0.1221 | 1.3236 | 0.001221 | 1.3852 | 0.001221 | 1.3223 | 1.384 | 15.3927 | 10.1765 | 1516.554
38961.5487 | 2450 | 2 | 38961.5487 | 1970 | 1 |  | 2358.5 | 2456.5 | 149.5726 | 0.1221 | 120.2686 | 0.06105 | 1.4957 | 0.001221 | 1.2027 | 0.0006105 | 1.4945 | 1.2021 | 1.9822 | 27.5406 | 500.7552
38961.5492 | 2059 | 1 | 38961.5492 | 1915 | 1 |  | 2400.5 | 2498.5 | 125.7021 | 0.06105 | 116.9109 | 0.06105 | 1.257 | 0.0006105 | 1.1691 | 0.0006105 | 1.2564 | 1.1685 | 21.3839 | 30.5543 | 10259.6284
38961.5497 | 1991 | 1 | 38961.5497 | 2476 | 2 |  | 2442.5 | 2540.5 | 121.5507 | 0.06105 | 151.16 | 0.1221 | 1.2155 | 0.0006105 | 1.5116 | 0.001221 | 1.2149 | 1.5104 | 26.9914 | 0.90733 | 455.3202
38961.5502 | 2126 | 2 | 38961.5502 | 1922 | 1 |  | 2484.5 | 2582.5 | 129.7924 | 0.1221 | 117.3382 | 0.06105 | 1.2979 | 0.001221 | 1.1734 | 0.0006105 | 1.2967 | 1.1728 | 17.587 | 30.0932 | 4283.8251
38961.5506 | 2014 | 1 | 38961.5506 | 2181 | 2 |  | 2526.5 | 2624.5 | 122.9548 | 0.06105 | 133.1502 | 0.1221 | 1.2295 | 0.0006105 | 1.3315 | 0.001221 | 1.2289 | 1.3303 | 24.1446 | 14.621 | 6165.9642
38961.5511 | 2246 | 2 | 38961.5511 | 2472 | 2 |  | 2568.5 | 2666.5 | 137.1184 | 0.1221 | 150.9158 | 0.1221 | 1.3712 | 0.001221 | 1.5092 | 0.001221 | 1.37 | 1.5079 | 12.2635 | 1.0751 | 133.162
38961.5516 | 2031 | 3 | 38961.5516 | 1965 | 1 |  | 2610.5 | 2708.5 | 123.9927 | 0.18315 | 119.9634 | 0.06105 | 1.2399 | 0.0018315 | 1.1996 | 0.0006105 | 1.2381 | 1.199 | 23.1723 | 27.2176 | 3311.7341
38961.5521 | 2333 | 2 | 38961.5521 | 2252 | 1 |  | 2652.5 | 2750.5 | 142.4298 | 0.1221 | 137.4847 | 0.06105 | 1.4243 | 0.001221 | 1.3748 | 0.0006105 | 1.4231 | 1.3742 | 7.1505 | 11.0138 | 810.4543
38961.5526 | 2259 | 1 | 38961.5526 | 2184 | 1 |  | 2694.5 | 2792.5 | 137.9121 | 0.06105 | 133.3333 | 0.06105 | 1.3791 | 0.0006105 | 1.3333 | 0.0006105 | 1.3785 | 1.3327 | 10.634 | 14.4636 | 3012.1633
38961.5531 | 2335 | 1 | 38961.5531 | 2236 | 1 |  | 2736.5 | 2834.5 | 142.5519 | 0.06105 | 136.5079 | 0.06105 | 1.4255 | 0.0006105 | 1.3651 | 0.0006105 | 1.4249 | 1.3645 | 7.0255 | 11.8148 | 1715.7776
38961.5536 | 2460 | 1 | 38961.5536 | 2135 | 1 |  | 2778.5 | 2876.5 | 150.1832 | 0.06105 | 130.3419 | 0.06105 | 1.5018 | 0.0006105 | 1.3034 | 0.0006105 | 1.5012 | 1.3028 | 1.5644 | 17.5539 | 558.1827
38961.554 | 1983 | 1 | 38961.5541 | 2280 | 1 |  | 2820.5 | 2918.5 | 121.0623 | 0.06105 | 139.1941 | 0.06105 | 1.2106 | 0.0006105 | 1.3919 | 0.0006105 | 1.21 | 1.3913 | 26.1404 | 9.5984 | 4504.8265
38961.5545 | 2133 | 2 | 38961.5545 | 2482 | 1 |  | 2862.5 | 2960.5 | 130.2198 | 0.1221 | 151.5263 | 0.06105 | 1.3022 | 0.001221 | 1.5153 | 0.0006105 | 1.301 | 1.5147 | 19.9805 | 0.66155 | 119.4075
38961.555 | 2104 | 2 | 38961.555 | 2106 | 1 |  | 2904.5 | 3002.5 | 128.4493 | 0.1221 | 128.5714 | 0.06105 | 1.2845 | 0.001221 | 1.2857 | 0.0006105 | 1.2833 | 1.2851 | 18.8581 | 18.6875 | 3089.0307

## A2-B4
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 151.9768 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38961.5205 | 1 | 0 | 38961.5205 | 1 | 0 |  | -80 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5209 | 1 | 0 | 38961.521 | 1 | 0 |  | -38 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5214 | 1 | 0 | 38961.5215 | 1 | 0 |  | 4 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5219 | 1 | 0 | 38961.5219 | 1 | 0 |  | 46 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5224 | 1 | 0 | 38961.5224 | 1 | 0 |  | 88 | 186 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5229 | 1 | 0 | 38961.5229 | 1 | 0 |  | 130 | 228 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5234 | 1 | 0 | 38961.5234 | 1 | 0 |  | 172 | 270 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5239 | 1 | 0 | 38961.5239 | 1 | 0 |  | 214 | 312 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5244 | 1 | 0 | 38961.5244 | 1 | 0 |  | 256 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5248 | 1 | 0 | 38961.5249 | 1 | 0 |  | 298 | 396 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5253 | 1 | 0 | 38961.5253 | 1 | 0 |  | 340 | 438 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5258 | 1 | 0 | 38961.5258 | 1 | 0 |  | 382 | 480 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5263 | 1 | 0 | 38961.5263 | 1 | 0 |  | 424 | 522 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5268 | 1 | 0 | 38961.5268 | 1 | 0 |  | 466 | 564 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5273 | 1 | 0 | 38961.5273 | 1 | 0 |  | 508 | 606 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5278 | 1 | 0 | 38961.5278 | 1 | 0 |  | 550 | 648 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5282 | 1 | 0 | 38961.5283 | 1 | 0 |  | 592 | 690 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5287 | 1 | 0 | 38961.5287 | 1 | 0 |  | 634 | 732 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5292 | 1 | 0 | 38961.5292 | 1 | 0 |  | 676 | 774 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5297 | 1 | 0 | 38961.5297 | 1 | 0 |  | 718 | 816 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5302 | 1 | 0 | 38961.5302 | 1 | 0 |  | 760 | 858 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5307 | 1 | 0 | 38961.5307 | 1 | 0 |  | 801.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5312 | 1 | 0 | 38961.5312 | 1 | 0 |  | 844 | 942 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5316 | 1 | 0 | 38961.5317 | 1 | 0 |  | 886 | 984 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5321 | 1 | 0 | 38961.5322 | 1 | 0 |  | 928 | 1026 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5326 | 1 | 0 | 38961.5326 | 1 | 0 |  | 969.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5331 | 1 | 0 | 38961.5331 | 1 | 0 |  | 1011.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5336 | 1 | 0 | 38961.5336 | 1 | 0 |  | 1053.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5341 | 1 | 0 | 38961.5341 | 1 | 0 |  | 1096 | 1194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5346 | 1 | 0 | 38961.5346 | 1 | 0 |  | 1138 | 1236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.535 | 1 | 0 | 38961.5351 | 1 | 0 |  | 1179.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5355 | 1 | 0 | 38961.5355 | 1 | 0 |  | 1221.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.536 | 1 | 0 | 38961.536 | 1 | 0 |  | 1263.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5365 | 1 | 0 | 38961.5365 | 1 | 0 |  | 1305.5 | 1403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.537 | 1 | 0 | 38961.537 | 1 | 0 |  | 1347.5 | 1445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5375 | 1 | 0 | 38961.5375 | 1 | 0 |  | 1389.5 | 1487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.538 | 1 | 0 | 38961.538 | 1 | 0 |  | 1431.5 | 1529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5384 | 1 | 0 | 38961.5385 | 1 | 0 |  | 1473.5 | 1571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5389 | 1 | 0 | 38961.5389 | 1 | 0 |  | 1515.5 | 1613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5394 | 1 | 0 | 38961.5394 | 1 | 0 |  | 1557.5 | 1655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5399 | 1 | 0 | 38961.5399 | 1 | 0 |  | 1599.5 | 1697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5404 | 1 | 0 | 38961.5404 | 1 | 0 |  | 1641.5 | 1739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5409 | 1 | 0 | 38961.5409 | 1 | 0 |  | 1683.5 | 1781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5414 | 1 | 0 | 38961.5414 | 1 | 0 |  | 1725.5 | 1823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
38961.5419 | 2 | 0 | 38961.5419 | 1 | 0 |  | 1767.5 | 1865.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124369 | 248838 | 124368.9988
38961.5423 | 2 | 0 | 38961.5423 | 1 | 0 |  | 1809.5 | 1907.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124369 | 248838 | 124368.9988
38961.5428 | 2 | 0 | 38961.5428 | 2 | 0 |  | 1851.5 | 1949.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124369 | 124369 | 124368.9988
38961.5433 | 2 | 0 | 38961.5433 | 2 | 0 |  | 1893.5 | 1991.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124369 | 124369 | 124368.9988
38961.5438 | 1899 | 0 | 38961.5438 | 2391 | 0 |  | 1935.5 | 2033.5 | 115.9341 | 0 | 145.9707 | 0 | 1.1593 | 0 | 1.4597 | 0 | 1.1593 | 1.4597 | 31.089 | 4.1146 | 29.9297
38961.5443 | 1947 | 0 | 38961.5443 | 1974 | 0 |  | 1977.5 | 2075.5 | 118.8645 | 0 | 120.5128 | 0 | 1.1886 | 0 | 1.2051 | 0 | 1.1886 | 1.2051 | 27.8572 | 26.1084 | 26.6686
38961.5448 | 2 | 0 | 38961.5448 | 2 | 0 |  | 2019.5 | 2117.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124369 | 124369 | 124368.9988
38961.5453 | 2 | 0 | 38961.5453 | 2 | 0 |  | 2061.5 | 2159.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124369 | 124369 | 124368.9988
38961.5457 | 1867 | 0 | 38961.5458 | 2234 | 0 |  | 2103.5 | 2201.5 | 113.9805 | 0 | 136.3858 | 0 | 1.1398 | 0 | 1.3639 | 0 | 1.1398 | 1.3639 | 33.3358 | 11.4315 | 32.196
38961.5462 | 2357 | 0 | 38961.5462 | 2035 | 0 |  | 2145.5 | 2243.5 | 143.895 | 0 | 124.2369 | 0 | 1.4389 | 0 | 1.2424 | 0 | 1.4389 | 1.2424 | 5.6165 | 22.3283 | 4.1775
38961.5467 | 2182 | 0 | 38961.5467 | 2264 | 0 |  | 2187.5 | 2285.5 | 133.2112 | 0 | 138.2173 | 0 | 1.3321 | 0 | 1.3822 | 0 | 1.3321 | 1.3822 | 14.0871 | 9.9549 | 12.755
38961.5472 | 1889 | 0 | 38961.5472 | 2071 | 0 |  | 2229.5 | 2327.5 | 115.3236 | 0 | 126.4347 | 0 | 1.1532 | 0 | 1.2643 | 0 | 1.1532 | 1.2643 | 31.783 | 20.2018 | 30.6297
38961.5477 | 2043 | 0 | 38961.5477 | 1960 | 0 |  | 2271.5 | 2369.5 | 124.7253 | 0 | 119.6581 | 0 | 1.2473 | 0 | 1.1966 | 0 | 1.2473 | 1.1966 | 21.8492 | 27.0092 | 20.602
38961.5482 | 2254 | 0 | 38961.5482 | 1957 | 0 |  | 2313.5 | 2411.5 | 137.6068 | 0 | 119.475 | 0 | 1.3761 | 0 | 1.1947 | 0 | 1.3761 | 1.1947 | 10.4428 | 27.2039 | 9.0667
38961.5487 | 2170 | 1 | 38961.5487 | 2406 | 0 |  | 2355.5 | 2453.5 | 132.4786 | 0.06105 | 146.8864 | 0 | 1.3248 | 0.0006105 | 1.4689 | 0 | 1.3242 | 1.4689 | 14.9233 | 3.4655 | 1066.391
38961.5491 | 1689 | 0 | 38961.5492 | 2139 | 0 |  | 2397.5 | 2495.5 | 103.1136 | 0 | 130.5861 | 0 | 1.0311 | 0 | 1.3059 | 0 | 1.0311 | 1.3059 | 47.3878 | 16.3806 | 46.3567
38961.5496 | 2046 | 0 | 38961.5496 | 2473 | 0 |  | 2439.5 | 2537.5 | 124.9084 | 0 | 150.9768 | 0 | 1.2491 | 0 | 1.5098 | 0 | 1.2491 | 1.5098 | 21.6706 | 0.66235 | 20.4215
38961.5501 | 2455 | 0 | 38961.5501 | 1994 | 1 |  | 2481.5 | 2579.5 | 149.8779 | 0 | 121.7338 | 0.06105 | 1.4988 | 0 | 1.2173 | 0.0006105 | 1.4988 | 1.2167 | 1.4004 | 24.9062 | 0.098372
38961.5506 | 1909 | 0 | 38961.5506 | 2135 | 0 |  | 2523.5 | 2621.5 | 116.5446 | 0 | 130.3419 | 0 | 1.1654 | 0 | 1.3034 | 0 | 1.1654 | 1.3034 | 30.4023 | 16.5986 | 29.2369
38961.5511 | 1394 | 1 | 38961.5511 | 2465 | 0 |  | 2565.5 | 2663.5 | 85.1038 | 0.06105 | 150.4884 | 0 | 0.85104 | 0.0006105 | 1.5049 | 0 | 0.85043 | 1.5049 | 84.7888 | 0.98905 | 1071.7923
38961.5516 | 2346 | 0 | 38961.5516 | 2299 | 0 |  | 2607.5 | 2705.5 | 143.2234 | 0 | 140.3541 | 0 | 1.4322 | 0 | 1.4035 | 0 | 1.4322 | 1.4035 | 6.1117 | 8.281 | 4.6794
38961.5521 | 2235 | 0 | 38961.5521 | 2404 | 0 |  | 2649.5 | 2747.5 | 136.4469 | 0 | 146.7643 | 0 | 1.3645 | 0 | 1.4676 | 0 | 1.3645 | 1.4676 | 11.3817 | 3.5516 | 10.0172
38961.5525 | 2321 | 0 | 38961.5526 | 2129 | 0 |  | 2691.5 | 2789.5 | 141.6972 | 0 | 129.9756 | 0 | 1.417 | 0 | 1.2998 | 0 | 1.417 | 1.2998 | 7.2546 | 16.9272 | 5.8377
38961.553 | 2250 | 0 | 38961.553 | 2215 | 0 |  | 2733.5 | 2831.5 | 137.3626 | 0 | 135.2259 | 0 | 1.3736 | 0 | 1.3523 | 0 | 1.3736 | 1.3523 | 10.6391 | 12.3874 | 9.2655
38961.5535 | 2423 | 0 | 38961.5535 | 2213 | 0 |  | 2775.5 | 2873.5 | 147.9243 | 0 | 135.1038 | 0 | 1.4792 | 0 | 1.351 | 0 | 1.4792 | 1.351 | 2.7396 | 12.4889 | 1.2603
38961.554 | 1526 | 0 | 38961.554 | 2361 | 0 |  | 2817.5 | 2915.5 | 93.1624 | 0 | 144.1392 | 0 | 0.93162 | 0 | 1.4414 | 0 | 0.93162 | 1.4414 | 63.1311 | 5.4375 | 62.1994
38961.5545 | 2404 | 0 | 38961.5545 | 1963 | 0 |  | 2859.5 | 2957.5 | 146.7643 | 0 | 119.8413 | 0 | 1.4676 | 0 | 1.1984 | 0 | 1.4676 | 1.1984 | 3.5516 | 26.8151 | 2.0839
38961.555 | 234 | 0 | 38961.555 | 1995 | 0 |  | 2901.5 | 2999.5 | 14.2857 | 0 | 121.7949 | 0 | 0.14286 | 0 | 1.2179 | 0 | 0.14286 | 1.2179 | 963.8376 | 24.781 | 963.6947

## A2-B3
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 151.1832 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38961.5204 | 1 | 0 | 38961.5205 | 1 | 0 |  | -83 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5209 | 2 | 0 | 38961.5209 | 1 | 0 |  | -41 | 57 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123719 | 247538 | 123718.9988
38961.5214 | 1 | 0 | 38961.5214 | 1 | 0 |  | 1 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5219 | 1 | 0 | 38961.5219 | 1 | 0 |  | 43 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5224 | 1 | 0 | 38961.5224 | 1 | 0 |  | 85 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5229 | 1 | 0 | 38961.5229 | 1 | 0 |  | 127 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5233 | 1 | 0 | 38961.5234 | 1 | 0 |  | 169 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5238 | 1 | 0 | 38961.5239 | 1 | 0 |  | 211 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5243 | 1 | 0 | 38961.5243 | 1 | 0 |  | 253 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5248 | 1 | 0 | 38961.5248 | 1 | 0 |  | 295 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5253 | 1 | 0 | 38961.5253 | 1 | 0 |  | 337 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5258 | 1 | 0 | 38961.5258 | 1 | 0 |  | 379 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5263 | 1 | 0 | 38961.5263 | 1 | 0 |  | 421 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5267 | 1 | 0 | 38961.5268 | 1 | 0 |  | 463 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5272 | 1 | 0 | 38961.5273 | 1 | 0 |  | 505 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5277 | 1 | 0 | 38961.5277 | 1 | 0 |  | 547 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5282 | 1 | 0 | 38961.5282 | 1 | 0 |  | 589 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5287 | 1 | 0 | 38961.5287 | 1 | 0 |  | 631 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5292 | 1 | 0 | 38961.5292 | 1 | 0 |  | 673 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5297 | 1 | 0 | 38961.5297 | 1 | 0 |  | 715 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5302 | 1 | 0 | 38961.5302 | 1 | 0 |  | 757 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5306 | 1 | 0 | 38961.5307 | 1 | 0 |  | 799 | 897 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5311 | 1 | 0 | 38961.5311 | 1 | 0 |  | 841 | 939 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5316 | 1 | 0 | 38961.5316 | 1 | 0 |  | 883 | 981 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5321 | 1 | 0 | 38961.5321 | 1 | 0 |  | 925 | 1023 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5326 | 1 | 0 | 38961.5326 | 1 | 0 |  | 967 | 1065 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5331 | 1 | 0 | 38961.5331 | 1 | 0 |  | 1009 | 1107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5336 | 1 | 0 | 38961.5336 | 1 | 0 |  | 1051 | 1149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.534 | 1 | 0 | 38961.5341 | 1 | 0 |  | 1093 | 1191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5345 | 1 | 0 | 38961.5345 | 1 | 0 |  | 1135 | 1233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.535 | 1 | 0 | 38961.535 | 1 | 0 |  | 1177 | 1275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5355 | 1 | 0 | 38961.5355 | 1 | 0 |  | 1219 | 1317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.536 | 1 | 0 | 38961.536 | 1 | 0 |  | 1261 | 1359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5365 | 1 | 0 | 38961.5365 | 1 | 0 |  | 1303 | 1401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.537 | 1 | 0 | 38961.537 | 1 | 0 |  | 1345 | 1443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5374 | 1 | 0 | 38961.5375 | 1 | 0 |  | 1387 | 1485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5379 | 1 | 0 | 38961.538 | 1 | 0 |  | 1429 | 1527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5384 | 1 | 0 | 38961.5384 | 1 | 0 |  | 1471 | 1569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5389 | 1 | 0 | 38961.5389 | 1 | 0 |  | 1513 | 1611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5394 | 1 | 0 | 38961.5394 | 1 | 0 |  | 1555 | 1653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5399 | 1 | 0 | 38961.5399 | 1 | 0 |  | 1597 | 1695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5404 | 1 | 0 | 38961.5404 | 1 | 0 |  | 1639 | 1737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5408 | 1 | 0 | 38961.5409 | 1 | 0 |  | 1681 | 1779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5413 | 1 | 0 | 38961.5414 | 1 | 0 |  | 1723 | 1821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38961.5418 | 2 | 0 | 38961.5418 | 2 | 0 |  | 1765 | 1863 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 123719 | 123719 | 123718.9988
38961.5423 | 2 | 0 | 38961.5423 | 2 | 0 |  | 1807 | 1905 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 123719 | 123719 | 123718.9988
38961.5428 | 2 | 0 | 38961.5428 | 2 | 0 |  | 1849 | 1947 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 123719 | 123719 | 123718.9988
38961.5433 | 4 | 0 | 38961.5433 | 2 | 0 |  | 1891 | 1989 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 61809.5 | 123719 | 61809.4976
38961.5438 | 2306 | 0 | 38961.5438 | 2 | 0 |  | 1933 | 2031 | 140.7814 | 0 | 0.1221 | 0 | 1.4078 | 0 | 0.001221 | 0 | 1.4078 | 0.001221 | 7.3886 | 123719 | 5.9807
38961.5442 | 2267 | 0 | 38961.5443 | 76 | 0 |  | 1975 | 2073 | 138.4005 | 0 | 4.6398 | 0 | 1.384 | 0 | 0.046398 | 0 | 1.384 | 0.046398 | 9.236 | 3158.3947 | 7.852
38961.5447 | 3 | 0 | 38961.5448 | 152 | 0 |  | 2017 | 2115 | 0.18315 | 0 | 9.2796 | 0 | 0.0018315 | 0 | 0.092796 | 0 | 0.0018315 | 0.092796 | 82446 | 1529.1974 | 82445.9982
38961.5452 | 2 | 0 | 38961.5452 | 236 | 0 |  | 2059 | 2157 | 0.1221 | 0 | 14.4078 | 0 | 0.001221 | 0 | 0.14408 | 0 | 0.001221 | 0.14408 | 123719 | 949.3136 | 123718.9988
38961.5457 | 2416 | 0 | 38961.5457 | 3 | 0 |  | 2101 | 2199 | 147.4969 | 0 | 0.18315 | 0 | 1.475 | 0 | 0.0018315 | 0 | 1.475 | 0.0018315 | 2.4992 | 82446 | 1.0242
38961.5462 | 1911 | 0 | 38961.5462 | 304 | 0 |  | 2143 | 2241 | 116.6667 | 0 | 18.5592 | 0 | 1.1667 | 0 | 0.18559 | 0 | 1.1667 | 0.18559 | 29.5856 | 714.5987 | 28.4189
38961.5467 | 2434 | 0 | 38961.5467 | 2 | 0 |  | 2185 | 2283 | 148.5958 | 0 | 0.1221 | 0 | 1.486 | 0 | 0.001221 | 0 | 1.486 | 0.001221 | 1.7412 | 123719 | 0.25521
38961.5472 | 2177 | 0 | 38961.5472 | 2 | 0 |  | 2226.5 | 2324.5 | 132.906 | 0 | 0.1221 | 0 | 1.3291 | 0 | 0.001221 | 0 | 1.3291 | 0.001221 | 13.752 | 123719 | 12.4229
38961.5477 | 2357 | 0 | 38961.5477 | 2 | 0 |  | 2269 | 2367 | 143.895 | 0 | 0.1221 | 0 | 1.4389 | 0 | 0.001221 | 0 | 1.4389 | 0.001221 | 5.0649 | 123719 | 3.626
38961.5481 | 2450 | 0 | 38961.5481 | 2 | 0 |  | 2310.5 | 2408.5 | 149.5726 | 0 | 0.1221 | 0 | 1.4957 | 0 | 0.001221 | 0 | 1.4957 | 0.001221 | 1.0767 | 123719 | 0.41899
38961.5486 | 2077 | 0 | 38961.5486 | 2 | 0 |  | 2352.5 | 2450.5 | 126.801 | 0 | 0.1221 | 0 | 1.268 | 0 | 0.001221 | 0 | 1.268 | 0.001221 | 19.2287 | 123719 | 17.9607
38961.5491 | 2190 | 0 | 38961.5491 | 1963 | 0 |  | 2394.5 | 2492.5 | 133.6996 | 0 | 119.8413 | 0 | 1.337 | 0 | 1.1984 | 0 | 1.337 | 1.1984 | 13.0767 | 26.1528 | 11.7397
38961.5496 | 2230 | 0 | 38961.5496 | 1960 | 0 |  | 2436.5 | 2534.5 | 136.1416 | 0 | 119.6581 | 0 | 1.3614 | 0 | 1.1966 | 0 | 1.3614 | 1.1966 | 11.0484 | 26.3459 | 9.687
38961.5501 | 2094 | 0 | 38961.5501 | 1980 | 0 |  | 2479 | 2577 | 127.8388 | 0 | 120.8791 | 0 | 1.2784 | 0 | 1.2088 | 0 | 1.2784 | 1.2088 | 18.2607 | 25.0697 | 16.9824
38961.5506 | 2380 | 0 | 38961.5506 | 1392 | 0 |  | 2521 | 2619 | 145.2991 | 0 | 84.9817 | 0 | 1.453 | 0 | 0.84982 | 0 | 1.453 | 0.84982 | 4.0496 | 77.9009 | 2.5966
38961.5511 | 1968 | 0 | 38961.5511 | 27 | 1 |  | 2563 | 2661 | 120.1465 | 0 | 1.6484 | 0.06105 | 1.2015 | 0 | 0.016484 | 0.0006105 | 1.2015 | 0.015873 | 25.8323 | 9424.5385 | 24.6309
38961.5515 | 1966 | 0 | 38961.5516 | 70 | 0 |  | 2604.5 | 2702.5 | 120.0244 | 0 | 4.2735 | 0 | 1.2002 | 0 | 0.042735 | 0 | 1.2002 | 0.042735 | 25.9603 | 3437.6857 | 24.7601
38961.552 | 1939 | 0 | 38961.552 | 131 | 0 |  | 2647 | 2745 | 118.3761 | 0 | 7.9976 | 0 | 1.1838 | 0 | 0.079976 | 0 | 1.1838 | 0.079976 | 27.7143 | 1790.3664 | 26.5305
38961.5525 | 1935 | 0 | 38961.5525 | 219 | 0 |  | 2688.5 | 2786.5 | 118.1319 | 0 | 13.37 | 0 | 1.1813 | 0 | 0.1337 | 0 | 1.1813 | 0.1337 | 27.9783 | 1030.7671 | 26.797
38961.553 | 2053 | 0 | 38961.553 | 297 | 0 |  | 2730.5 | 2828.5 | 125.3358 | 0 | 18.1319 | 0 | 1.2534 | 0 | 0.18132 | 0 | 1.2534 | 0.18132 | 20.6225 | 733.798 | 19.3691
38961.5535 | 1916 | 0 | 38961.5535 | 642 | 0 |  | 2772.5 | 2870.5 | 116.9719 | 0 | 39.1941 | 0 | 1.1697 | 0 | 0.39194 | 0 | 1.1697 | 0.39194 | 29.2474 | 285.729 | 28.0777
38961.554 | 2237 | 0 | 38961.554 | 641 | 0 |  | 2814.5 | 2912.5 | 136.569 | 0 | 39.1331 | 0 | 1.3657 | 0 | 0.39133 | 0 | 1.3657 | 0.39133 | 10.7009 | 286.3307 | 9.3352
38961.5545 | 2131 | 0 | 38961.5545 | 625 | 0 |  | 2856.5 | 2954.5 | 130.0977 | 0 | 38.1563 | 0 | 1.301 | 0 | 0.38156 | 0 | 1.301 | 0.38156 | 16.2074 | 296.2208 | 14.9064
38961.5549 | 2460 | 0 | 38961.555 | 589 | 0 |  | 2898.5 | 2996.5 | 150.1832 | 0 | 35.9585 | 0 | 1.5018 | 0 | 0.35958 | 0 | 1.5018 | 0.35958 | 0.66585 | 320.438 | 0.83598

## A1-C6
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 151.7937 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38961.5204 | 1 | 0 | 38961.5204 | 1 | 0 |  | -85.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5209 | 1 | 0 | 38961.5209 | 1 | 0 |  | -43.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5214 | 1 | 0 | 38961.5214 | 1 | 0 |  | -1.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5219 | 1 | 0 | 38961.5219 | 1 | 0 |  | 40.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5223 | 1 | 0 | 38961.5224 | 1 | 0 |  | 82.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5228 | 1 | 0 | 38961.5228 | 1 | 0 |  | 124.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5233 | 1 | 0 | 38961.5233 | 1 | 0 |  | 166.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5238 | 1 | 0 | 38961.5238 | 1 | 0 |  | 208.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5243 | 1 | 0 | 38961.5243 | 1 | 0 |  | 250.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5248 | 1 | 0 | 38961.5248 | 1 | 0 |  | 292.5 | 390.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5253 | 1 | 0 | 38961.5253 | 1 | 0 |  | 334.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5258 | 1 | 0 | 38961.5258 | 1 | 0 |  | 376.5 | 474.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5262 | 1 | 0 | 38961.5263 | 1 | 0 |  | 418.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5267 | 1 | 0 | 38961.5267 | 1 | 0 |  | 460.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5272 | 1 | 0 | 38961.5272 | 1 | 0 |  | 502.5 | 600.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5277 | 1 | 0 | 38961.5277 | 1 | 0 |  | 544.5 | 642.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5282 | 1 | 0 | 38961.5282 | 1 | 0 |  | 586.5 | 684.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5287 | 1 | 0 | 38961.5287 | 1 | 0 |  | 628.5 | 726.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5292 | 1 | 0 | 38961.5292 | 1 | 0 |  | 670.5 | 768.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5296 | 1 | 0 | 38961.5297 | 1 | 0 |  | 712.5 | 810.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5301 | 1 | 0 | 38961.5301 | 1 | 0 |  | 754.5 | 852.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5306 | 1 | 0 | 38961.5306 | 1 | 0 |  | 796.5 | 894.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5311 | 1 | 0 | 38961.5311 | 1 | 0 |  | 838 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5316 | 1 | 0 | 38961.5316 | 1 | 0 |  | 880 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5321 | 1 | 0 | 38961.5321 | 1 | 0 |  | 922.5 | 1020.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5326 | 1 | 0 | 38961.5326 | 1 | 0 |  | 964.5 | 1062.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.533 | 1 | 0 | 38961.5331 | 1 | 0 |  | 1006.5 | 1104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5335 | 1 | 0 | 38961.5335 | 1 | 0 |  | 1048.5 | 1146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.534 | 1 | 0 | 38961.534 | 1 | 0 |  | 1090 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5345 | 1 | 0 | 38961.5345 | 1 | 0 |  | 1132.5 | 1230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.535 | 1 | 0 | 38961.535 | 1 | 0 |  | 1174.5 | 1272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5355 | 1 | 0 | 38961.5355 | 1 | 0 |  | 1216.5 | 1314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5359 | 1 | 0 | 38961.536 | 1 | 0 |  | 1258 | 1356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5364 | 1 | 0 | 38961.5365 | 1 | 0 |  | 1300 | 1398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5369 | 1 | 0 | 38961.5369 | 1 | 0 |  | 1342.5 | 1440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5374 | 1 | 0 | 38961.5374 | 1 | 0 |  | 1384 | 1482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5379 | 1 | 0 | 38961.5379 | 1 | 0 |  | 1426 | 1524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5384 | 1 | 0 | 38961.5384 | 1 | 0 |  | 1468 | 1566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5389 | 1 | 0 | 38961.5389 | 1 | 0 |  | 1510 | 1608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5394 | 1 | 0 | 38961.5394 | 1 | 0 |  | 1552 | 1650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5398 | 1 | 0 | 38961.5399 | 1 | 0 |  | 1594 | 1692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5403 | 1 | 0 | 38961.5403 | 1 | 0 |  | 1636 | 1734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5408 | 1 | 0 | 38961.5408 | 1 | 0 |  | 1678 | 1776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5413 | 1 | 0 | 38961.5413 | 1 | 0 |  | 1720 | 1818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38961.5418 | 2 | 0 | 38961.5418 | 2165 | 0 |  | 1762 | 1860 | 0.1221 | 0 | 132.1734 | 0 | 0.001221 | 0 | 1.3217 | 0 | 0.001221 | 1.3217 | 124219 | 14.8443 | 124218.9988
38961.5423 | 2 | 0 | 38961.5423 | 1929 | 0 |  | 1804 | 1902 | 0.1221 | 0 | 117.7656 | 0 | 0.001221 | 0 | 1.1777 | 0 | 0.001221 | 1.1777 | 124219 | 28.8948 | 124218.9988
38961.5428 | 2 | 0 | 38961.5428 | 16 | 0 |  | 1846 | 1944 | 0.1221 | 0 | 0.9768 | 0 | 0.001221 | 0 | 0.009768 | 0 | 0.001221 | 0.009768 | 124219 | 15439.875 | 124218.9988
38961.5432 | 4 | 0 | 38961.5433 | 2038 | 7 |  | 1888 | 1986 | 0.2442 | 0 | 124.42 | 0.42735 | 0.002442 | 0 | 1.2442 | 0.0042735 | 0.002442 | 1.2399 | 62059.5 | 22.4215 | 62059.4976
38961.5437 | 2163 | 17 | 38961.5437 | 2408 | 15 |  | 1930 | 2028 | 132.0513 | 1.0379 | 147.0085 | 0.91575 | 1.3205 | 0.010379 | 1.4701 | 0.0091575 | 1.3101 | 1.4609 | 19.6762 | 3.3832 | 58.9773
38961.5442 | 1888 | 9 | 38961.5442 | 2075 | 9 |  | 1972 | 2070 | 115.2625 | 0.54945 | 126.6789 | 0.54945 | 1.1526 | 0.0054945 | 1.2668 | 0.0054945 | 1.1471 | 1.2613 | 32.6198 | 20.1814 | 1099.6825
38961.5447 | 2 | 0 | 38961.5447 | 2350 | 0 |  | 2014 | 2112 | 0.1221 | 0 | 143.4676 | 0 | 0.001221 | 0 | 1.4347 | 0 | 0.001221 | 1.4347 | 124219 | 5.8034 | 124218.9988
38961.5452 | 2 | 0 | 38961.5452 | 2206 | 0 |  | 2056 | 2154 | 0.1221 | 0 | 134.6764 | 0 | 0.001221 | 0 | 1.3468 | 0 | 0.001221 | 1.3468 | 124219 | 12.7099 | 124218.9988
38961.5457 | 2400 | 5 | 38961.5457 | 2056 | 4 |  | 2098 | 2196 | 146.5201 | 0.30525 | 125.5189 | 0.2442 | 1.4652 | 0.0030525 | 1.2552 | 0.002442 | 1.4621 | 1.2527 | 3.641 | 22.1601 | 295.25
38961.5462 | 1919 | 3 | 38961.5462 | 2377 | 3 |  | 2140 | 2238 | 117.1551 | 0.18315 | 145.116 | 0.18315 | 1.1716 | 0.0018315 | 1.4512 | 0.0018315 | 1.1697 | 1.4493 | 30.65 | 4.6265 | 831.8791
38961.5466 | 2225 | 3 | 38961.5467 | 2188 | 3 |  | 2182 | 2280 | 135.8364 | 0.18315 | 133.5775 | 0.18315 | 1.3584 | 0.0018315 | 1.3358 | 0.0018315 | 1.3565 | 1.3339 | 11.8794 | 13.8155 | 1045.4498
38961.5471 | 1997 | 2 | 38961.5472 | 2228 | 3 |  | 2224 | 2322 | 121.917 | 0.1221 | 136.0195 | 0.18315 | 1.2192 | 0.001221 | 1.3602 | 0.0018315 | 1.2179 | 1.3584 | 24.7428 | 11.6762 | 2547.8802
38961.5476 | 2436 | 3 | 38961.5476 | 2353 | 3 |  | 2266 | 2364 | 148.7179 | 0.18315 | 143.6508 | 0.18315 | 1.4872 | 0.0018315 | 1.4365 | 0.0018315 | 1.4853 | 1.4347 | 2.1138 | 6.0405 | 89.9659
38961.5481 | 2223 | 2 | 38961.5481 | 2349 | 2 |  | 2308 | 2406 | 135.7143 | 0.1221 | 143.4066 | 0.1221 | 1.3571 | 0.001221 | 1.4341 | 0.001221 | 1.3559 | 1.4328 | 12.0426 | 5.8951 | 727.5466
38961.5486 | 2036 | 2 | 38961.5486 | 1967 | 2 |  | 2350 | 2448 | 124.2979 | 0.1221 | 120.0855 | 0.1221 | 1.243 | 0.001221 | 1.2009 | 0.001221 | 1.2418 | 1.1996 | 22.2249 | 26.5532 | 4703.9142
38961.5491 | 1917 | 1 | 38961.5491 | 2135 | 0 |  | 2392 | 2490 | 117.033 | 0.06105 | 130.3419 | 0 | 1.1703 | 0.0006105 | 1.3034 | 0 | 1.1697 | 1.3034 | 29.8117 | 16.4581 | 8032.4554
38961.5496 | 2068 | 2 | 38961.5496 | 2128 | 2 |  | 2434 | 2532 | 126.2515 | 0.1221 | 129.9145 | 0.1221 | 1.2625 | 0.001221 | 1.2991 | 0.001221 | 1.2613 | 1.2979 | 20.3671 | 16.9352 | 3015.1269
38961.55 | 2452 | 3 | 38961.5501 | 2470 | 2 |  | 2476 | 2574 | 149.6947 | 0.18315 | 150.7937 | 0.1221 | 1.4969 | 0.0018315 | 1.5079 | 0.001221 | 1.4951 | 1.5067 | 1.7033 | 0.69685 | 7.2386
38961.5505 | 2063 | 2 | 38961.5506 | 1996 | 2 |  | 2518 | 2616 | 125.9463 | 0.1221 | 121.8559 | 0.1221 | 1.2595 | 0.001221 | 1.2186 | 0.001221 | 1.2582 | 1.2173 | 20.6234 | 24.713 | 4175.0071
38961.551 | 164 | 0 | 38961.551 | 2258 | 0 |  | 2560 | 2658 | 10.0122 | 0 | 137.851 | 0 | 0.10012 | 0 | 1.3785 | 0 | 0.10012 | 1.3785 | 1416.0854 | 10.1143 | 1415.9852
38961.5515 | 1989 | 1 | 38961.5515 | 2175 | 2 |  | 2602 | 2700 | 121.4286 | 0.06105 | 132.7839 | 0.1221 | 1.2143 | 0.0006105 | 1.3278 | 0.001221 | 1.2137 | 1.3266 | 25.1069 | 14.3822 | 6241.3958
38961.552 | 2092 | 2 | 38961.552 | 2192 | 1 |  | 2644 | 2742 | 127.7167 | 0.1221 | 133.8217 | 0.06105 | 1.2772 | 0.001221 | 1.3382 | 0.0006105 | 1.2759 | 1.3376 | 19.0049 | 13.4682 | 2328.696
38961.5525 | 1917 | 1 | 38961.5525 | 2134 | 1 |  | 2686 | 2784 | 117.033 | 0.06105 | 130.2808 | 0.06105 | 1.1703 | 0.0006105 | 1.3028 | 0.0006105 | 1.1697 | 1.3022 | 29.8112 | 16.5464 | 8069.4473
38961.553 | 2366 | 2 | 38961.553 | 2126 | 2 |  | 2728 | 2826 | 144.4444 | 0.1221 | 129.7924 | 0.1221 | 1.4444 | 0.001221 | 1.2979 | 0.001221 | 1.4432 | 1.2967 | 5.1173 | 17.2851 | 872.3233
38961.5534 | 2324 | 14 | 38961.5535 | 2036 | 6 |  | 2770 | 2868 | 141.8803 | 0.8547 | 124.2979 | 0.3663 | 1.4188 | 0.008547 | 1.243 | 0.003663 | 1.4103 | 1.2393 | 7.2186 | 23.1334 | 199.1183
38961.5539 | 2164 | 10 | 38961.554 | 2260 | 10 |  | 2812 | 2910 | 132.1123 | 0.6105 | 137.9731 | 0.6105 | 1.3211 | 0.006105 | 1.3797 | 0.006105 | 1.315 | 1.3736 | 15.6691 | 10.355 | 293.1184
38961.5544 | 1143 | 0 | 38961.5544 | 2322 | 0 |  | 2854 | 2952 | 69.7802 | 0 | 141.7582 | 0 | 0.6978 | 0 | 1.4176 | 0 | 0.6978 | 1.4176 | 117.5311 | 7.0792 | 116.8333
38961.5549 | 82 | 0 | 38961.5549 | 2435 | 0 |  | 2896 | 2994 | 5.0061 | 0 | 148.6569 | 0 | 0.050061 | 0 | 1.4866 | 0 | 0.050061 | 1.4866 | 2932.1707 | 2.1101 | 2932.1207

## A1-C5
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 151.7326 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38961.5204 | 1 | 0 | 38961.5204 | 1 | 0 |  | -88.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5209 | 1 | 0 | 38961.5209 | 1 | 0 |  | -46.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5213 | 4 | 0 | 38961.5214 | 1 | 0 |  | -4.5 | 93.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 62034.5 | 248438 | 62034.4976
38961.5218 | 1 | 0 | 38961.5218 | 1 | 0 |  | 37.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5223 | 2 | 0 | 38961.5223 | 1 | 0 |  | 79.5 | 177.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124169 | 248438 | 124168.9988
38961.5228 | 1 | 0 | 38961.5228 | 1 | 0 |  | 121.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5233 | 1 | 0 | 38961.5233 | 1 | 0 |  | 163.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5238 | 1 | 0 | 38961.5238 | 1 | 0 |  | 205.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5243 | 1 | 0 | 38961.5243 | 1 | 0 |  | 247.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5247 | 1 | 0 | 38961.5248 | 1 | 0 |  | 289.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5252 | 1 | 0 | 38961.5252 | 1 | 0 |  | 331.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5257 | 1 | 0 | 38961.5257 | 1 | 0 |  | 373.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5262 | 1 | 0 | 38961.5262 | 1 | 0 |  | 415.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5267 | 1 | 0 | 38961.5267 | 1 | 0 |  | 457.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5272 | 1 | 0 | 38961.5272 | 1 | 0 |  | 499.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5277 | 1 | 0 | 38961.5277 | 1 | 0 |  | 541.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5281 | 1 | 0 | 38961.5282 | 1 | 0 |  | 583.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5286 | 1 | 0 | 38961.5286 | 1 | 0 |  | 625.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5291 | 1 | 0 | 38961.5291 | 1 | 0 |  | 667.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5296 | 1 | 0 | 38961.5296 | 1 | 0 |  | 709.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5301 | 1 | 0 | 38961.5301 | 1 | 0 |  | 751.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5306 | 1 | 0 | 38961.5306 | 1 | 0 |  | 793.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5311 | 1 | 0 | 38961.5311 | 1 | 0 |  | 835.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5316 | 1 | 0 | 38961.5316 | 1 | 0 |  | 877.5 | 975.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.532 | 1 | 0 | 38961.532 | 1 | 0 |  | 919.5 | 1017.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5325 | 1 | 0 | 38961.5325 | 1 | 0 |  | 961.5 | 1059.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.533 | 1 | 0 | 38961.533 | 1 | 0 |  | 1003.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5335 | 1 | 0 | 38961.5335 | 1 | 0 |  | 1045.5 | 1143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.534 | 1 | 0 | 38961.534 | 1 | 0 |  | 1087.5 | 1185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5345 | 1 | 0 | 38961.5345 | 1 | 0 |  | 1129.5 | 1227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.535 | 1 | 0 | 38961.535 | 1 | 0 |  | 1171.5 | 1269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5354 | 1 | 0 | 38961.5355 | 1 | 0 |  | 1213.5 | 1311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5359 | 1 | 0 | 38961.5359 | 1 | 0 |  | 1255.5 | 1353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5364 | 1 | 0 | 38961.5364 | 1 | 0 |  | 1297.5 | 1395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5369 | 1 | 0 | 38961.5369 | 1 | 0 |  | 1339.5 | 1437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5374 | 1 | 0 | 38961.5374 | 1 | 0 |  | 1381.5 | 1479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5379 | 1 | 0 | 38961.5379 | 1 | 0 |  | 1423.5 | 1521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5384 | 1 | 0 | 38961.5384 | 1 | 0 |  | 1465.5 | 1563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5388 | 1 | 0 | 38961.5389 | 1 | 0 |  | 1507.5 | 1605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5393 | 1 | 0 | 38961.5393 | 1 | 0 |  | 1549.5 | 1647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5398 | 1 | 0 | 38961.5398 | 1 | 0 |  | 1591.5 | 1689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5403 | 1 | 0 | 38961.5403 | 1 | 0 |  | 1633.5 | 1731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5408 | 1 | 0 | 38961.5408 | 1 | 0 |  | 1675.5 | 1773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38961.5413 | 1 | 0 | 38961.5413 | 231 | 0 |  | 1717.5 | 1815.5 | 0.06105 | 0 | 14.1026 | 0 | 0.0006105 | 0 | 0.14103 | 0 | 0.0006105 | 0.14103 | 248438 | 975.9221 | 248437.9994
38961.5418 | 1 | 0 | 38961.5418 | 1784 | 0 |  | 1759.5 | 1857.5 | 0.06105 | 0 | 108.9133 | 0 | 0.0006105 | 0 | 1.0891 | 0 | 0.0006105 | 1.0891 | 248438 | 39.315 | 248437.9994
38961.5422 | 2 | 0 | 38961.5423 | 2095 | 0 |  | 1801.5 | 1899.5 | 0.1221 | 0 | 127.8999 | 0 | 0.001221 | 0 | 1.279 | 0 | 0.001221 | 1.279 | 124169 | 18.6339 | 124168.9988
38961.5427 | 2 | 0 | 38961.5427 | 2170 | 0 |  | 1843.5 | 1941.5 | 0.1221 | 0 | 132.4786 | 0 | 0.001221 | 0 | 1.3248 | 0 | 0.001221 | 1.3248 | 124169 | 14.5336 | 124168.9988
38961.5432 | 47 | 0 | 38961.5432 | 1962 | 0 |  | 1885.5 | 1983.5 | 2.8694 | 0 | 119.7802 | 0 | 0.028694 | 0 | 1.1978 | 0 | 0.028694 | 1.1978 | 5188.0426 | 26.6758 | 5188.0139
38961.5437 | 2345 | 26 | 38961.5437 | 1956 | 15 |  | 1927.5 | 2025.5 | 143.1624 | 1.5873 | 119.4139 | 0.91575 | 1.4316 | 0.015873 | 1.1941 | 0.0091575 | 1.4158 | 1.185 | 6.2799 | 31.1008 | 104.3622
38961.5442 | 2262 | 14 | 38961.5442 | 2118 | 9 |  | 1969.5 | 2067.5 | 138.0952 | 0.8547 | 129.304 | 0.54945 | 1.381 | 0.008547 | 1.293 | 0.0054945 | 1.3724 | 1.2875 | 10.2894 | 18.1733 | 229.9972
38961.5447 | 2 | 0 | 38961.5447 | 2323 | 0 |  | 2011.5 | 2109.5 | 0.1221 | 0 | 141.8193 | 0 | 0.001221 | 0 | 1.4182 | 0 | 0.001221 | 1.4182 | 124169 | 6.9901 | 124168.9988
38961.5452 | 2 | 0 | 38961.5452 | 2395 | 0 |  | 2053.5 | 2151.5 | 0.1221 | 0 | 146.2149 | 0 | 0.001221 | 0 | 1.4621 | 0 | 0.001221 | 1.4621 | 124169 | 3.7737 | 124168.9988
38961.5456 | 2379 | 5 | 38961.5457 | 2082 | 4 |  | 2095.5 | 2193.5 | 145.2381 | 0.30525 | 127.1062 | 0.2442 | 1.4524 | 0.0030525 | 1.2711 | 0.002442 | 1.4493 | 1.2686 | 4.5281 | 20.2738 | 341.7797
38961.5461 | 2216 | 4 | 38961.5461 | 2046 | 2 |  | 2137.5 | 2235.5 | 135.2869 | 0.2442 | 124.9084 | 0.1221 | 1.3529 | 0.002442 | 1.2491 | 0.001221 | 1.3504 | 1.2479 | 12.2806 | 21.6687 | 1181.579
38961.5466 | 2172 | 3 | 38961.5466 | 1953 | 2 |  | 2179.5 | 2277.5 | 132.6007 | 0.18315 | 119.2308 | 0.1221 | 1.326 | 0.0018315 | 1.1923 | 0.001221 | 1.3242 | 1.1911 | 14.5212 | 27.4815 | 2230.3157
38961.5471 | 1928 | 2 | 38961.5471 | 1924 | 2 |  | 2221.5 | 2319.5 | 117.7045 | 0.1221 | 117.4603 | 0.1221 | 1.177 | 0.001221 | 1.1746 | 0.001221 | 1.1758 | 1.1734 | 29.0427 | 29.3131 | 6294.7715
38961.5476 | 2146 | 3 | 38961.5476 | 2450 | 3 |  | 2263.5 | 2361.5 | 131.0134 | 0.18315 | 149.5726 | 0.18315 | 1.3101 | 0.0018315 | 1.4957 | 0.0018315 | 1.3083 | 1.4939 | 17.5213 | 1.456 | 160.9179
38961.5481 | 1930 | 2 | 38961.5481 | 1948 | 2 |  | 2305 | 2403 | 117.8266 | 0.1221 | 118.9255 | 0.1221 | 1.1783 | 0.001221 | 1.1893 | 0.001221 | 1.177 | 1.188 | 28.9142 | 27.7131 | 6004.0337
38961.5486 | 2024 | 2 | 38961.5486 | 2035 | 1 |  | 2347.5 | 2445.5 | 123.5653 | 0.1221 | 124.2369 | 0.06105 | 1.2357 | 0.001221 | 1.2424 | 0.0006105 | 1.2344 | 1.2418 | 22.9202 | 22.1902 | 4171.2529
38961.5491 | 1896 | 1 | 38961.5491 | 2449 | 0 |  | 2389.5 | 2487.5 | 115.7509 | 0.06105 | 149.5116 | 0 | 1.1575 | 0.0006105 | 1.4951 | 0 | 1.1569 | 1.4951 | 32.2474 | 1.4855 | 861.2471
38961.5495 | 2317 | 2 | 38961.5495 | 2461 | 1 |  | 2431.5 | 2529.5 | 141.453 | 0.1221 | 150.2442 | 0.06105 | 1.4145 | 0.001221 | 1.5024 | 0.0006105 | 1.4133 | 1.5018 | 7.9641 | 0.99614 | 82.0517
38961.55 | 2059 | 3 | 38961.55 | 2201 | 2 |  | 2473 | 2571 | 125.7021 | 0.18315 | 134.3712 | 0.1221 | 1.257 | 0.0018315 | 1.3437 | 0.001221 | 1.2552 | 1.3425 | 20.9739 | 12.9886 | 1622.3172
38961.5505 | 2038 | 2 | 38961.5505 | 2469 | 2 |  | 2515 | 2613 | 124.42 | 0.1221 | 150.7326 | 0.1221 | 1.2442 | 0.001221 | 1.5073 | 0.001221 | 1.243 | 1.5061 | 25.7748 | 0.66606 | 147.3434
38961.551 | 1597 | 1 | 38961.551 | 2206 | 0 |  | 2557 | 2655 | 97.4969 | 0.06105 | 134.6764 | 0 | 0.97497 | 0.0006105 | 1.3468 | 0 | 0.97436 | 1.3468 | 55.9397 | 12.6646 | 9974.9827
38961.5515 | 463 | 0 | 38961.5515 | 2063 | 0 |  | 2599 | 2697 | 28.2662 | 0 | 125.9463 | 0 | 0.28266 | 0 | 1.2595 | 0 | 0.28266 | 1.2595 | 436.7991 | 20.4741 | 436.5165
38961.552 | 2425 | 2 | 38961.552 | 2360 | 1 |  | 2641.5 | 2739.5 | 148.0464 | 0.1221 | 144.0781 | 0.06105 | 1.4805 | 0.001221 | 1.4408 | 0.0006105 | 1.4792 | 1.4402 | 2.5306 | 5.4055 | 149.6951
38961.5524 | 1971 | 2 | 38961.5525 | 2268 | 1 |  | 2683 | 2781 | 120.3297 | 0.1221 | 138.4615 | 0.06105 | 1.2033 | 0.001221 | 1.3846 | 0.0006105 | 1.2021 | 1.384 | 26.4031 | 9.6049 | 2245.0516
38961.5529 | 2325 | 2 | 38961.553 | 2328 | 1 |  | 2725 | 2823 | 141.9414 | 0.1221 | 142.1245 | 0.06105 | 1.4194 | 0.001221 | 1.4212 | 0.0006105 | 1.4182 | 1.4206 | 6.9925 | 6.805 | 504.5556
38961.5534 | 2146 | 1 | 38961.5534 | 2094 | 1 |  | 2767 | 2865 | 131.0134 | 0.06105 | 127.8388 | 0.06105 | 1.3101 | 0.0006105 | 1.2784 | 0.0006105 | 1.3095 | 1.2778 | 15.8613 | 18.756 | 5344.2751
38961.5539 | 1977 | 1 | 38961.5539 | 2174 | 1 |  | 2809 | 2907 | 120.696 | 0.06105 | 132.7228 | 0.06105 | 1.207 | 0.0006105 | 1.3272 | 0.0006105 | 1.2063 | 1.3266 | 25.8188 | 14.3551 | 6369.1815
38961.5544 | 80 | 0 | 38961.5544 | 2466 | 0 |  | 2851 | 2949 | 4.884 | 0 | 150.5495 | 0 | 0.04884 | 0 | 1.5055 | 0 | 0.04884 | 1.5055 | 3006.725 | 0.78589 | 3006.6762
38961.5549 | 69 | 0 | 38961.5549 | 2416 | 0 |  | 2893 | 2991 | 4.2125 | 0 | 147.4969 | 0 | 0.042125 | 0 | 1.475 | 0 | 0.042125 | 1.475 | 3502 | 2.8717 | 3501.9579

## A1-B4
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 150.2674 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38961.5203 | 1 | 0 | 38961.5203 | 1 | 0 |  | -91.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5208 | 1 | 0 | 38961.5208 | 1 | 0 |  | -49 | 49 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5213 | 1 | 0 | 38961.5213 | 1 | 0 |  | -7.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5218 | 1 | 0 | 38961.5218 | 1 | 0 |  | 34.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5223 | 1 | 0 | 38961.5223 | 1 | 0 |  | 77 | 175 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5228 | 1 | 0 | 38961.5228 | 1 | 0 |  | 118.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5233 | 1 | 0 | 38961.5233 | 1 | 0 |  | 160.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5237 | 1 | 0 | 38961.5238 | 1 | 0 |  | 202.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5242 | 1 | 0 | 38961.5242 | 1 | 0 |  | 244.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5247 | 1 | 0 | 38961.5247 | 1 | 0 |  | 286.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5252 | 1 | 0 | 38961.5252 | 1 | 0 |  | 328.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5257 | 1 | 0 | 38961.5257 | 1 | 0 |  | 370.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5262 | 1 | 0 | 38961.5262 | 1 | 0 |  | 412.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5267 | 1 | 0 | 38961.5267 | 1 | 0 |  | 454.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5271 | 1 | 0 | 38961.5272 | 1 | 0 |  | 496.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5276 | 1 | 0 | 38961.5276 | 1 | 0 |  | 538.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5281 | 1 | 0 | 38961.5281 | 1 | 0 |  | 580.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5286 | 1 | 0 | 38961.5286 | 1 | 0 |  | 622.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5291 | 1 | 0 | 38961.5291 | 1 | 0 |  | 664.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5296 | 1 | 0 | 38961.5296 | 1 | 0 |  | 706.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5301 | 1 | 0 | 38961.5301 | 1 | 0 |  | 748.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5305 | 1 | 0 | 38961.5306 | 1 | 0 |  | 790.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.531 | 1 | 0 | 38961.531 | 1 | 0 |  | 832.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5315 | 1 | 0 | 38961.5315 | 1 | 0 |  | 874.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.532 | 1 | 0 | 38961.532 | 1 | 0 |  | 916.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5325 | 1 | 0 | 38961.5325 | 1 | 0 |  | 958.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.533 | 1 | 0 | 38961.533 | 1 | 0 |  | 1000.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5335 | 1 | 0 | 38961.5335 | 1 | 0 |  | 1042.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5339 | 1 | 0 | 38961.534 | 1 | 0 |  | 1084.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5344 | 1 | 0 | 38961.5344 | 1 | 0 |  | 1126.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5349 | 1 | 0 | 38961.5349 | 1 | 0 |  | 1168.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5354 | 1 | 0 | 38961.5354 | 1 | 0 |  | 1210.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5359 | 1 | 0 | 38961.5359 | 1 | 0 |  | 1252.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5364 | 1 | 0 | 38961.5364 | 1 | 0 |  | 1294.5 | 1392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5369 | 1 | 0 | 38961.5369 | 1 | 0 |  | 1336.5 | 1434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5373 | 1 | 0 | 38961.5374 | 1 | 0 |  | 1378.5 | 1476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5378 | 1 | 0 | 38961.5378 | 1 | 0 |  | 1420.5 | 1518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5383 | 1 | 0 | 38961.5383 | 1 | 0 |  | 1462.5 | 1560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5388 | 1 | 0 | 38961.5388 | 1 | 0 |  | 1504.5 | 1602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5393 | 1 | 0 | 38961.5393 | 1 | 0 |  | 1546.5 | 1644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5398 | 1 | 0 | 38961.5398 | 1 | 0 |  | 1588.5 | 1686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5403 | 1 | 0 | 38961.5403 | 1 | 0 |  | 1630.5 | 1728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5408 | 1 | 0 | 38961.5408 | 1 | 0 |  | 1672.5 | 1770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246038 | 246038 | 246037.9994
38961.5412 | 2 | 0 | 38961.5413 | 1 | 0 |  | 1714.5 | 1812.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122969 | 246038 | 122968.9988
38961.5417 | 2 | 0 | 38961.5417 | 1 | 0 |  | 1756.5 | 1854.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122969 | 246038 | 122968.9988
38961.5422 | 2 | 0 | 38961.5422 | 1 | 0 |  | 1798.5 | 1896.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122969 | 246038 | 122968.9988
38961.5427 | 2 | 0 | 38961.5427 | 2 | 0 |  | 1840.5 | 1938.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122969 | 122969 | 122968.9988
38961.5432 | 2 | 0 | 38961.5432 | 2 | 0 |  | 1882.5 | 1980.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122969 | 122969 | 122968.9988
38961.5437 | 2050 | 0 | 38961.5437 | 2 | 0 |  | 1924.5 | 2022.5 | 125.1526 | 0 | 0.1221 | 0 | 1.2515 | 0 | 0.001221 | 0 | 1.2515 | 0.001221 | 20.0673 | 122969 | 18.8158
38961.5442 | 1897 | 0 | 38961.5442 | 153 | 0 |  | 1966.5 | 2064.5 | 115.812 | 0 | 9.3407 | 0 | 1.1581 | 0 | 0.093407 | 0 | 1.1581 | 0.093407 | 29.7512 | 1508.7451 | 28.5931
38961.5446 | 2 | 0 | 38961.5447 | 5 | 0 |  | 2008.5 | 2106.5 | 0.1221 | 0 | 0.30525 | 0 | 0.001221 | 0 | 0.0030525 | 0 | 0.001221 | 0.0030525 | 122969 | 49127.6 | 122968.9988
38961.5451 | 2 | 0 | 38961.5451 | 32 | 0 |  | 2050.5 | 2148.5 | 0.1221 | 0 | 1.9536 | 0 | 0.001221 | 0 | 0.019536 | 0 | 0.001221 | 0.019536 | 122969 | 7591.8125 | 122968.9988
38961.5456 | 2310 | 0 | 38961.5456 | 2 | 0 |  | 2092.5 | 2190.5 | 141.0256 | 0 | 0.1221 | 0 | 1.4103 | 0 | 0.001221 | 0 | 1.4103 | 0.001221 | 6.5532 | 122969 | 5.143
38961.5461 | 1898 | 0 | 38961.5461 | 91 | 0 |  | 2134.5 | 2232.5 | 115.873 | 0 | 5.5556 | 0 | 1.1587 | 0 | 0.055556 | 0 | 1.1587 | 0.055556 | 29.6828 | 2604.8132 | 28.5241
38961.5466 | 2409 | 0 | 38961.5466 | 2 | 0 |  | 2176.5 | 2274.5 | 147.0696 | 0 | 0.1221 | 0 | 1.4707 | 0 | 0.001221 | 0 | 1.4707 | 0.001221 | 2.1743 | 122969 | 0.70365
38961.5471 | 2178 | 0 | 38961.5471 | 2 | 0 |  | 2218.5 | 2316.5 | 132.967 | 0 | 0.1221 | 0 | 1.3297 | 0 | 0.001221 | 0 | 1.3297 | 0.001221 | 13.011 | 122969 | 11.6813
38961.5476 | 2377 | 0 | 38961.5476 | 2 | 0 |  | 2260.5 | 2358.5 | 145.116 | 0 | 0.1221 | 0 | 1.4512 | 0 | 0.001221 | 0 | 1.4512 | 0.001221 | 3.5499 | 122969 | 2.0987
38961.548 | 1982 | 0 | 38961.5481 | 2 | 0 |  | 2302.5 | 2400.5 | 121.0012 | 0 | 0.1221 | 0 | 1.21 | 0 | 0.001221 | 0 | 1.21 | 0.001221 | 24.1867 | 122969 | 22.9767
38961.5485 | 2445 | 1 | 38961.5485 | 3 | 0 |  | 2344.5 | 2442.5 | 149.2674 | 0.06105 | 0.18315 | 0 | 1.4927 | 0.0006105 | 0.0018315 | 0 | 1.4921 | 0.0018315 | 0.67021 | 81946 | 1536.1254
38961.549 | 1823 | 0 | 38961.549 | 2049 | 0 |  | 2386.5 | 2484.5 | 111.2943 | 0 | 125.0916 | 0 | 1.1129 | 0 | 1.2509 | 0 | 1.1129 | 1.2509 | 35.0181 | 20.1259 | 33.9052
38961.5495 | 1917 | 0 | 38961.5495 | 1955 | 0 |  | 2428.5 | 2526.5 | 117.033 | 0 | 119.3529 | 0 | 1.1703 | 0 | 1.1935 | 0 | 1.1703 | 1.1935 | 28.3975 | 25.9018 | 27.2272
38961.55 | 2022 | 0 | 38961.55 | 1982 | 0 |  | 2470.5 | 2568.5 | 123.4432 | 0 | 121.0012 | 0 | 1.2344 | 0 | 1.21 | 0 | 1.2344 | 1.21 | 21.73 | 24.1867 | 20.4955
38961.5505 | 2126 | 0 | 38961.5505 | 1838 | 0 |  | 2512.5 | 2610.5 | 129.7924 | 0 | 112.21 | 0 | 1.2979 | 0 | 1.1221 | 0 | 1.2979 | 1.1221 | 15.7752 | 33.9162 | 14.4772
| 1740 | 0 | 38961.551 | 22 | 0 |  | 2555 | 2653 | 106.2271 | 0 | 1.3431 | 0 | 1.0623 | 0 | 0.013431 | 0 | 1.0623 | 0.013431 | 41.4586 | 11088.0909 | 40.3963
38961.5514 | 1353 | 0 | 38961.5515 | 49 | 0 |  | 2596.5 | 2694.5 | 82.6007 | 0 | 2.9915 | 0 | 0.82601 | 0 | 0.029915 | 0 | 0.82601 | 0.029915 | 81.9202 | 4923.2245 | 81.0942
38961.5519 | 2159 | 0 | 38961.5519 | 206 | 0 |  | 2638.5 | 2736.5 | 131.8071 | 0 | 12.5763 | 0 | 1.3181 | 0 | 0.12576 | 0 | 1.3181 | 0.12576 | 14.0056 | 1094.8447 | 12.6875
38961.5524 | 2151 | 0 | 38961.5524 | 187 | 0 |  | 2680.5 | 2778.5 | 131.3187 | 0 | 11.4164 | 0 | 1.3132 | 0 | 0.11416 | 0 | 1.3132 | 0.11416 | 14.4296 | 1216.246 | 13.1164
38961.5529 | 2422 | 0 | 38961.5529 | 207 | 0 |  | 2722.5 | 2820.5 | 147.8632 | 0 | 12.6374 | 0 | 1.4786 | 0 | 0.12637 | 0 | 1.4786 | 0.12637 | 1.6259 | 1089.0725 | 0.1473
38961.5534 | 2114 | 0 | 38961.5534 | 562 | 0 |  | 2764.5 | 2862.5 | 129.0598 | 0 | 34.3101 | 0 | 1.2906 | 0 | 0.3431 | 0 | 1.2906 | 0.3431 | 16.4324 | 337.968 | 15.1418
38961.5539 | 2169 | 0 | 38961.5539 | 679 | 0 |  | 2806.5 | 2904.5 | 132.4176 | 0 | 41.453 | 0 | 1.3242 | 0 | 0.41453 | 0 | 1.3242 | 0.41453 | 13.4799 | 262.5007 | 12.1558
38961.5544 | 95 | 0 | 38961.5544 | 612 | 0 |  | 2848.5 | 2946.5 | 5.7998 | 0 | 37.3626 | 0 | 0.057998 | 0 | 0.37363 | 0 | 0.057998 | 0.37363 | 2490.9263 | 302.1863 | 2490.8683
38961.5548 | 820 | 0 | 38961.5549 | 735 | 0 |  | 2890.5 | 2988.5 | 50.0611 | 0 | 44.8718 | 0 | 0.50061 | 0 | 0.44872 | 0 | 0.50061 | 0.44872 | 200.1683 | 234.8816 | 199.6677

## A1-B3
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 147.0928 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38961.5203 | 1 | 0 | 38961.5203 | 1 | 0 |  | -94 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5208 | 1 | 0 | 38961.5208 | 1 | 0 |  | -52 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5213 | 1 | 0 | 38961.5213 | 1 | 0 |  | -10 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5218 | 1 | 0 | 38961.5218 | 1 | 0 |  | 32 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5222 | 1 | 0 | 38961.5223 | 1 | 0 |  | 74 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5227 | 1 | 0 | 38961.5228 | 1 | 0 |  | 116 | 214 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5232 | 1 | 0 | 38961.5232 | 1 | 0 |  | 158 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5237 | 1 | 0 | 38961.5237 | 1 | 0 |  | 200 | 298 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5242 | 1 | 0 | 38961.5242 | 1 | 0 |  | 242 | 340 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5247 | 1 | 0 | 38961.5247 | 1 | 0 |  | 284 | 382 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5252 | 1 | 0 | 38961.5252 | 1 | 0 |  | 326 | 424 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5256 | 1 | 0 | 38961.5257 | 1 | 0 |  | 368 | 466 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5261 | 1 | 0 | 38961.5262 | 1 | 0 |  | 410 | 508 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5266 | 1 | 0 | 38961.5266 | 1 | 0 |  | 452 | 550 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5271 | 1 | 0 | 38961.5271 | 1 | 0 |  | 494 | 592 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5276 | 1 | 0 | 38961.5276 | 1 | 0 |  | 536 | 634 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5281 | 1 | 0 | 38961.5281 | 1 | 0 |  | 578 | 676 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5286 | 1 | 0 | 38961.5286 | 1 | 0 |  | 620 | 718 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5291 | 1 | 0 | 38961.5291 | 1 | 0 |  | 662 | 760 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5295 | 1 | 0 | 38961.5296 | 1 | 0 |  | 704 | 802 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.53 | 1 | 0 | 38961.53 | 1 | 0 |  | 746 | 844 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5305 | 1 | 0 | 38961.5305 | 1 | 0 |  | 788 | 886 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.531 | 1 | 0 | 38961.531 | 1 | 0 |  | 829.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5315 | 1 | 0 | 38961.5315 | 1 | 0 |  | 872 | 970 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.532 | 1 | 0 | 38961.532 | 1 | 0 |  | 914 | 1012 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5325 | 1 | 0 | 38961.5325 | 1 | 0 |  | 955.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5329 | 1 | 0 | 38961.533 | 1 | 0 |  | 998 | 1096 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5334 | 1 | 0 | 38961.5334 | 1 | 0 |  | 1040 | 1138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5339 | 1 | 0 | 38961.5339 | 1 | 0 |  | 1081.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5344 | 1 | 0 | 38961.5344 | 1 | 0 |  | 1124 | 1222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5349 | 1 | 0 | 38961.5349 | 1 | 0 |  | 1166 | 1264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5354 | 1 | 0 | 38961.5354 | 1 | 0 |  | 1207.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5359 | 1 | 0 | 38961.5359 | 1 | 0 |  | 1250 | 1348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5363 | 1 | 0 | 38961.5364 | 1 | 0 |  | 1291.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5368 | 1 | 0 | 38961.5368 | 1 | 0 |  | 1333.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5373 | 1 | 0 | 38961.5373 | 1 | 0 |  | 1375.5 | 1473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5378 | 1 | 0 | 38961.5378 | 1 | 0 |  | 1417.5 | 1515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5383 | 1 | 0 | 38961.5383 | 1 | 0 |  | 1459.5 | 1557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5388 | 1 | 0 | 38961.5388 | 1 | 0 |  | 1501.5 | 1599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240837.9994
38961.5393 | 2 | 1 | 38961.5393 | 1 | 1 |  | 1543.5 | 1641.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 240737.9585 | 579788484.8724 | 240637.9585
38961.5397 | 2 | 1 | 38961.5398 | 1 | 1 |  | 1585.5 | 1683.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 240737.9585 | 579788484.8724 | 240637.9585
38961.5402 | 1 | 2 | 38961.5402 | 1 | 1 |  | 1627.5 | 1725.5 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 240837.917 | 580029222.8332 | 120318.9793
38961.5407 | 2 | 1 | 38961.5407 | 1 | 1 |  | 1669.5 | 1767.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 240737.9585 | 579788484.8724 | 240637.9585
38961.5412 | 1 | 1 | 38961.5412 | 1 | 0 |  | 1711.5 | 1809.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 580029422.44 | 240838 | 240638.083
38961.5417 | 2 | 2 | 38961.5417 | 2 | 1 |  | 1753.5 | 1851.5 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 289773823.22 | 240737.9169 | 120219.0623
38961.5422 | 2 | 1 | 38961.5422 | 2 | 1 |  | 1795.5 | 1893.5 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 240838 | 240838 | 240538.1245
38961.5427 | 2 | 2 | 38961.5427 | 2 | 0 |  | 1837.5 | 1935.5 | 0.1221 | 0.1221 | 0.1221 | 0 | 0.001221 | 0.001221 | 0.001221 | 0 | 0 | 0.001221 | 144886961.61 | 120369 | 120169.166
38961.5431 | 2 | 2 | 38961.5432 | 2 | 0 |  | 1879.5 | 1977.5 | 0.1221 | 0.1221 | 0.1221 | 0 | 0.001221 | 0.001221 | 0.001221 | 0 | 0 | 0.001221 | 144886961.61 | 120369 | 120169.166
38961.5436 | 21 | 1 | 38961.5436 | 2 | 1 |  | 1921.5 | 2019.5 | 1.2821 | 0.06105 | 0.1221 | 0.06105 | 0.012821 | 0.0006105 | 0.001221 | 0.0006105 | 0.01221 | 0.0006105 | 11942.146 | 242770.8917 | 238639.7017
38961.5441 | 1152 | 0 | 38961.5441 | 3 | 0 |  | 1963.5 | 2061.5 | 70.3297 | 0 | 0.18315 | 0 | 0.7033 | 0 | 0.0018315 | 0 | 0.7033 | 0.0018315 | 109.1476 | 80212.6667 | 108.4443
38961.5446 | 3 | 1 | 38961.5446 | 2 | 1 |  | 2005.5 | 2103.5 | 0.18315 | 0.06105 | 0.1221 | 0.06105 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 120343.974 | 240938.208 | 240438.2075
38961.5451 | 2 | 2 | 38961.5451 | 47 | 1 |  | 2047.5 | 2145.5 | 0.1221 | 0.1221 | 2.8694 | 0.06105 | 0.001221 | 0.001221 | 0.028694 | 0.0006105 | 0 | 0.028083 | 6181678.657 | 5135.6069 | 117971.8642
38961.5456 | 1211 | 0 | 38961.5456 | 2 | 0 |  | 2089.5 | 2187.5 | 73.9316 | 0 | 0.1221 | 0 | 0.73932 | 0 | 0.001221 | 0 | 0.73932 | 0.001221 | 98.9579 | 120369 | 98.2186
38961.5461 | 2345 | 0 | 38961.5461 | 70 | 0 |  | 2131.5 | 2229.5 | 143.1624 | 0 | 4.2735 | 0 | 1.4316 | 0 | 0.042735 | 0 | 1.4316 | 0.042735 | 2.7454 | 3341.9714 | 1.3138
38961.5466 | 2393 | 0 | 38961.5466 | 2 | 0 |  | 2173.5 | 2271.5 | 146.0928 | 0 | 0.1221 | 0 | 1.4609 | 0 | 0.001221 | 0 | 1.4609 | 0.001221 | 0.6845 | 120369 | 0.77643
38961.547 | 1895 | 0 | 38961.547 | 3 | 0 |  | 2215.5 | 2313.5 | 115.6899 | 0 | 0.18315 | 0 | 1.1569 | 0 | 0.0018315 | 0 | 1.1569 | 0.0018315 | 27.1441 | 80212.6667 | 25.9872
38961.5475 | 1980 | 0 | 38961.5475 | 2 | 0 |  | 2257.5 | 2355.5 | 120.8791 | 0 | 0.1221 | 0 | 1.2088 | 0 | 0.001221 | 0 | 1.2088 | 0.001221 | 21.6859 | 120369 | 20.4771
38961.548 | 2039 | 0 | 38961.548 | 2 | 0 |  | 2299.5 | 2397.5 | 124.4811 | 0 | 0.1221 | 0 | 1.2448 | 0 | 0.001221 | 0 | 1.2448 | 0.001221 | 18.1648 | 120369 | 16.92
38961.5485 | 2021 | 0 | 38961.5485 | 2 | 1 |  | 2341.5 | 2439.5 | 123.3822 | 0 | 0.1221 | 0.06105 | 1.2338 | 0 | 0.001221 | 0.0006105 | 1.2338 | 0.0006105 | 19.2172 | 240838 | 17.9834
38961.549 | 2105 | 0 | 38961.549 | 2045 | 0 |  | 2383.5 | 2481.5 | 128.5104 | 0 | 124.8474 | 0 | 1.2851 | 0 | 1.2485 | 0 | 1.2851 | 1.2485 | 14.4599 | 17.8181 | 13.1748
38961.5495 | 2259 | 0 | 38961.5495 | 1986 | 0 |  | 2425.5 | 2523.5 | 137.9121 | 0 | 121.2454 | 0 | 1.3791 | 0 | 1.2125 | 0 | 1.3791 | 1.2125 | 6.6569 | 21.3182 | 5.2778
38961.55 | 2044 | 0 | 38961.55 | 1975 | 0 |  | 2467.5 | 2565.5 | 124.7863 | 0 | 120.5739 | 0 | 1.2479 | 0 | 1.2057 | 0 | 1.2479 | 1.2057 | 17.8757 | 21.9939 | 16.6279
38961.5504 | 2332 | 0 | 38961.5505 | 1418 | 0 |  | 2509.5 | 2607.5 | 142.3687 | 0 | 86.569 | 0 | 1.4237 | 0 | 0.86569 | 0 | 1.4237 | 0.86569 | 3.3182 | 69.914 | 1.8945
38961.5509 | 2054 | 0 | 38961.5509 | 19 | 0 |  | 2551.5 | 2649.5 | 125.3968 | 0 | 1.16 | 0 | 1.254 | 0 | 0.0116 | 0 | 1.254 | 0.0116 | 17.3019 | 12580.9474 | 16.0479
38961.5514 | 1587 | 0 | 38961.5514 | 54 | 0 |  | 2593.5 | 2691.5 | 96.8864 | 0 | 3.2967 | 0 | 0.96886 | 0 | 0.032967 | 0 | 0.96886 | 0.032967 | 51.8198 | 4361.8148 | 50.8509
38961.5519 | 1476 | 0 | 38961.5519 | 116 | 0 |  | 2635.5 | 2733.5 | 90.1099 | 0 | 7.0818 | 0 | 0.9011 | 0 | 0.070818 | 0 | 0.9011 | 0.070818 | 63.2371 | 1977.0517 | 62.336
38961.5524 | 2343 | 0 | 38961.5524 | 1067 | 0 |  | 2677.5 | 2775.5 | 143.0403 | 0 | 65.1404 | 0 | 1.4304 | 0 | 0.6514 | 0 | 1.4304 | 0.6514 | 2.8331 | 125.8088 | 1.4027
38961.5529 | 2209 | 0 | 38961.5529 | 192 | 0 |  | 2719.5 | 2817.5 | 134.8596 | 0 | 11.7216 | 0 | 1.3486 | 0 | 0.11722 | 0 | 1.3486 | 0.11722 | 9.0711 | 1154.8854 | 7.7225
38961.5534 | 2085 | 0 | 38961.5534 | 624 | 0 |  | 2761.5 | 2859.5 | 127.2894 | 0 | 38.0952 | 0 | 1.2729 | 0 | 0.38095 | 0 | 1.2729 | 0.38095 | 15.5578 | 286.1186 | 14.2849
38961.5538 | 2159 | 0 | 38961.5539 | 554 | 0 |  | 2803.5 | 2901.5 | 131.8071 | 0 | 33.8217 | 0 | 1.3181 | 0 | 0.33822 | 0 | 1.3181 | 0.33822 | 11.597 | 334.9061 | 10.279
38961.5543 | 775 | 0 | 38961.5543 | 667 | 0 |  | 2845.5 | 2943.5 | 47.3138 | 0 | 40.7204 | 0 | 0.47314 | 0 | 0.4072 | 0 | 0.47314 | 0.4072 | 210.8877 | 261.2264 | 210.4146
38961.5548 | 694 | 0 | 38961.5548 | 710 | 0 |  | 2887.5 | 2985.5 | 42.3687 | 0 | 43.3455 | 0 | 0.42369 | 0 | 0.43346 | 0 | 0.42369 | 0.43346 | 247.1729 | 239.3493 | 246.7492

## A1-A2
Penlight Test 61 |  |  | 2006-09-01 | 12:30 |  |  | Vs = |  | 150.4505 |  | R = | 100
TS/TP | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38961.5203 | 1 | 0 | 38961.5203 | 1 | 0 |  | -97 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5208 | 1 | 0 | 38961.5208 | 1 | 0 | 42.5 | -54.5 | 43.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5212 | 1 | 0 | 38961.5213 | 1 | 0 | 41.5 | -13 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5217 | 1 | 0 | 38961.5217 | 1 | 0 | 42 | 29 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5222 | 1 | 0 | 38961.5222 | 1 | 0 | 42.5 | 71.5 | 169.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5227 | 1 | 0 | 38961.5227 | 1 | 0 | 41.5 | 113 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5232 | 1 | 0 | 38961.5232 | 1 | 0 | 42 | 155 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5237 | 1 | 0 | 38961.5237 | 1 | 0 | 42 | 197 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5242 | 1 | 0 | 38961.5242 | 1 | 0 | 42 | 239 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5246 | 1 | 0 | 38961.5247 | 1 | 0 | 42 | 281 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5251 | 1 | 0 | 38961.5252 | 1 | 0 | 42 | 323 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5256 | 1 | 0 | 38961.5256 | 1 | 0 | 42 | 365 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5261 | 1 | 0 | 38961.5261 | 1 | 0 | 42 | 407 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5266 | 1 | 0 | 38961.5266 | 1 | 0 | 42 | 449 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5271 | 1 | 0 | 38961.5271 | 1 | 0 | 42 | 491 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5276 | 1 | 0 | 38961.5276 | 1 | 0 | 42 | 533 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.528 | 1 | 0 | 38961.5281 | 2 | 0 | 42 | 575 | 673 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 246338 | 123119 | 246337.9994
38961.5285 | 1 | 0 | 38961.5286 | 1 | 0 | 42 | 617 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.529 | 1 | 0 | 38961.529 | 1 | 0 | 42 | 659 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5295 | 1 | 0 | 38961.5295 | 1 | 0 | 42 | 701 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.53 | 1 | 0 | 38961.53 | 1 | 0 | 42 | 743 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5305 | 1 | 0 | 38961.5305 | 1 | 0 | 42 | 785 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.531 | 1 | 0 | 38961.531 | 1 | 0 | 42 | 827 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5314 | 1 | 0 | 38961.5315 | 1 | 0 | 42 | 869 | 967 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5319 | 1 | 0 | 38961.532 | 1 | 0 | 42 | 911 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5324 | 1 | 0 | 38961.5324 | 1 | 0 | 42 | 953 | 1051 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5329 | 1 | 0 | 38961.5329 | 1 | 0 | 42 | 995 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5334 | 1 | 0 | 38961.5334 | 1 | 0 | 42 | 1037 | 1135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5339 | 1 | 0 | 38961.5339 | 1 | 0 | 42 | 1079 | 1177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5344 | 1 | 0 | 38961.5344 | 1 | 0 | 42 | 1121 | 1219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5348 | 1 | 0 | 38961.5349 | 1 | 0 | 42 | 1163 | 1261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5353 | 1 | 0 | 38961.5354 | 1 | 0 | 42 | 1205 | 1303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5358 | 1 | 0 | 38961.5358 | 1 | 0 | 42 | 1247 | 1345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5363 | 1 | 0 | 38961.5363 | 1 | 0 | 42 | 1289 | 1387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5368 | 1 | 0 | 38961.5368 | 1 | 0 | 42 | 1331 | 1429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5373 | 1 | 0 | 38961.5373 | 1 | 0 | 42 | 1373 | 1471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5378 | 1 | 0 | 38961.5378 | 1 | 0 | 42 | 1415 | 1513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5383 | 1 | 0 | 38961.5383 | 1 | 0 | 42 | 1457 | 1555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5387 | 1 | 0 | 38961.5388 | 1 | 0 | 42 | 1499 | 1597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246338 | 246338 | 246337.9994
38961.5392 | 937 | 974 | 38961.5392 | 1193 | 927 | 42 | 1541 | 1639 | 57.2039 | 59.4628 | 72.8327 | 56.5934 | 0.57204 | 0.59463 | 0.72833 | 0.56593 | 0.022589 | 0.16239 | 489.9868 | 354.5446 | 44.3158
38961.5397 | 930 | 1030 | 38961.5397 | 1068 | 1148 | 42 | 1583 | 1681 | 56.7766 | 62.8816 | 65.2015 | 70.0855 | 0.56777 | 0.62882 | 0.65201 | 0.70085 | 0.06105 | 0.04884 | 1677.4478 | 12076.5942 | 48.5668
38961.5402 | 1027 | 1071 | 38961.5402 | 1125 | 1099 | 42 | 1625 | 1723 | 62.6984 | 65.3846 | 68.6813 | 67.094 | 0.62698 | 0.65385 | 0.68681 | 0.67094 | 0.026862 | 0.015873 | 2406.7159 | 6811.3697 | 33.7142
38961.5407 | 1037 | 1128 | 38961.5407 | 1195 | 1174 | 42 | 1667 | 1765 | 63.3089 | 68.8645 | 72.9548 | 71.6728 | 0.63309 | 0.68864 | 0.72955 | 0.71673 | 0.055556 | 0.012821 | 531.0237 | 634.4286 | 22.927
38961.5412 | 1135 | 1107 | 38961.5412 | 1088 | 1159 | 42 | 1709 | 1807 | 69.2918 | 67.5824 | 66.4225 | 70.757 | 0.69292 | 0.67582 | 0.66422 | 0.70757 | 0.017094 | 0.043346 | 1364.8064 | 1595.0022 | 18.9034
38961.5417 | 937 | 916 | 38961.5417 | 1191 | 1168 | 42 | 1751 | 1849 | 57.2039 | 55.9219 | 72.7106 | 71.3065 | 0.57204 | 0.55922 | 0.72711 | 0.71306 | 0.012821 | 0.014042 | 15424.8234 | 8253.8069 | 65.9456
38961.5421 | 1022 | 993 | 38961.5422 | 961 | 934 | 42 | 1793 | 1891 | 62.3932 | 60.6227 | 58.6691 | 57.0208 | 0.62393 | 0.60623 | 0.58669 | 0.57021 | 0.017705 | 0.016484 | 7392.5166 | 10465.1378 | 44.8264
38961.5426 | 957 | 950 | 38961.5427 | 1075 | 1046 | 42 | 1835 | 1933 | 58.4249 | 57.9976 | 65.6288 | 63.8584 | 0.58425 | 0.57998 | 0.65629 | 0.63858 | 0.0042735 | 0.017705 | 6174.8352 | 5456.1128 | 57.6156
38961.5431 | 610 | 590 | 38961.5431 | 1186 | 1170 | 42 | 1877 | 1975 | 37.2405 | 36.0195 | 72.4054 | 71.4286 | 0.37241 | 0.3602 | 0.72405 | 0.71429 | 0.01221 | 0.009768 | 10418.7995 | 26798.7379 | 213.505
38961.5436 | 568 | 580 | 38961.5436 | 925 | 1024 | 42 | 1919 | 2017 | 34.6764 | 35.409 | 56.4713 | 62.5153 | 0.34676 | 0.35409 | 0.56471 | 0.62515 | 0.007326 | 0.06044 | 5970.4295 | 2934.7958 | 219.4834
38961.5441 | 603 | 0 | 38961.5441 | 2413 | 1 | 42 | 1961 | 2059 | 36.8132 | 0 | 147.3138 | 0.06105 | 0.36813 | 0 | 1.4731 | 0.0006105 | 0.36813 | 1.4725 | 308.6866 | 2.1716 | 308.3184
38961.5446 | 1007 | 974 | 38961.5446 | 1058 | 1024 | 42 | 2003 | 2101 | 61.4774 | 59.4628 | 64.591 | 62.5153 | 0.61477 | 0.59463 | 0.64591 | 0.62515 | 0.020147 | 0.020757 | 7914.9341 | 6677.1967 | 48.8961
38961.5451 | 1051 | 1017 | 38961.5451 | 1058 | 1024 | 42 | 2045 | 2143 | 64.1636 | 62.0879 | 64.591 | 62.5153 | 0.64164 | 0.62088 | 0.64591 | 0.62515 | 0.020757 | 0.020757 | 7148.1765 | 7148.1765 | 38.4377
38961.5455 | 1421 | 0 | 38961.5456 | 2110 | 1 | 41.5 | 2086.5 | 2184.5 | 86.7521 | 0 | 128.8156 | 0.06105 | 0.86752 | 0 | 1.2882 | 0.0006105 | 0.86752 | 1.2875 | 73.4258 | 16.8506 | 72.5582
38961.546 | 1953 | 3 | 38961.5461 | 2203 | 3 | 42.5 | 2129 | 2227 | 119.2308 | 0.18315 | 134.4933 | 0.18315 | 1.1923 | 0.0018315 | 1.3449 | 0.0018315 | 1.1905 | 1.3431 | 26.5669 | 11.9422 | 1807.8314
38961.5465 | 2320 | 4 | 38961.5465 | 1988 | 2 | 42 | 2171 | 2269 | 141.6361 | 0.2442 | 121.3675 | 0.1221 | 1.4164 | 0.002442 | 1.2137 | 0.001221 | 1.4139 | 1.2125 | 6.2785 | 24.3779 | 687.8577
38961.547 | 2392 | 2 | 38961.547 | 1898 | 2 | 42 | 2213 | 2311 | 146.0317 | 0.1221 | 115.873 | 0.1221 | 1.4603 | 0.001221 | 1.1587 | 0.001221 | 1.4591 | 1.1575 | 3.0367 | 30.9474 | 831.6612
38961.5475 | 2424 | 3 | 38961.5475 | 2250 | 2 | 42 | 2255 | 2353 | 147.9853 | 0.18315 | 137.3626 | 0.1221 | 1.4799 | 0.0018315 | 1.3736 | 0.001221 | 1.478 | 1.3724 | 1.6887 | 10.0668 | 113.9606
38961.548 | 2208 | 2 | 38961.548 | 2031 | 2 | 41.5 | 2296.5 | 2394.5 | 134.7985 | 0.1221 | 123.9927 | 0.1221 | 1.348 | 0.001221 | 1.2399 | 0.001221 | 1.3468 | 1.2387 | 11.6711 | 21.5412 | 2254.2377
38961.5485 | 2326 | 2 | 38961.5485 | 2179 | 3 | 42.5 | 2339 | 2437 | 142.0024 | 0.1221 | 133.0281 | 0.18315 | 1.42 | 0.001221 | 1.3303 | 0.0018315 | 1.4188 | 1.3284 | 5.9928 | 13.4237 | 807.0294
38961.5489 | 2001 | 2 | 38961.549 | 2084 | 0 | 42 | 2381 | 2479 | 122.1612 | 0.1221 | 127.2283 | 0 | 1.2216 | 0.001221 | 1.2723 | 0 | 1.2204 | 1.2723 | 23.3084 | 18.2524 | 3560.7277
38961.5494 | 2248 | 2 | 38961.5494 | 2377 | 2 | 41.5 | 2422.5 | 2520.5 | 137.2405 | 0.1221 | 145.116 | 0.1221 | 1.3724 | 0.001221 | 1.4512 | 0.001221 | 1.3712 | 1.4499 | 9.8709 | 3.7108 | 383.5302
38961.5499 | 2448 | 3 | 38961.5499 | 2077 | 2 | 42 | 2464.5 | 2562.5 | 149.4505 | 0.18315 | 126.801 | 0.1221 | 1.4945 | 0.0018315 | 1.268 | 0.001221 | 1.4927 | 1.2668 | 0.67373 | 21.7856 | 79.7827
38961.5504 | 2275 | 3 | 38961.5504 | 2014 | 2 | 42.5 | 2507 | 2605 | 138.8889 | 0.18315 | 122.9548 | 0.1221 | 1.3889 | 0.0018315 | 1.2295 | 0.001221 | 1.3871 | 1.2283 | 8.3843 | 22.6533 | 1147.4395
38961.5509 | 1873 | 3 | 38961.5509 | 2237 | 2 | 41.5 | 2548.5 | 2646.5 | 114.3468 | 0.18315 | 136.569 | 0.1221 | 1.1435 | 0.0018315 | 1.3657 | 0.001221 | 1.1416 | 1.3645 | 32.1298 | 10.202 | 1815.654
38961.5514 | 1443 | 0 | 38961.5514 | 2203 | 0 | 42 | 2590.5 | 2688.5 | 88.0952 | 0 | 134.4933 | 0 | 0.88095 | 0 | 1.3449 | 0 | 0.88095 | 1.3449 | 70.7817 | 11.8647 | 69.9008
38961.5519 | 1274 | 0 | 38961.5519 | 2317 | 0 | 42 | 2632.5 | 2730.5 | 77.7778 | 0 | 141.453 | 0 | 0.77778 | 0 | 1.4145 | 0 | 0.77778 | 1.4145 | 93.4364 | 6.3608 | 92.6586
38961.5523 | 2359 | 1 | 38961.5524 | 1952 | 1 | 42.5 | 2675 | 2773 | 144.0171 | 0.06105 | 119.1697 | 0.06105 | 1.4402 | 0.0006105 | 1.1917 | 0.0006105 | 1.4396 | 1.1911 | 4.4762 | 26.5666 | 2190.961
38961.5528 | 2303 | 1 | 38961.5528 | 2368 | 1 | 41.5 | 2716.5 | 2814.5 | 140.5983 | 0.06105 | 144.5665 | 0.06105 | 1.406 | 0.0006105 | 1.4457 | 0.0006105 | 1.4054 | 1.4451 | 7.0856 | 4.0962 | 631.1041
38961.5533 | 2089 | 1 | 38961.5533 | 2372 | 1 | 42 | 2758.5 | 2856.5 | 127.5336 | 0.06105 | 144.8107 | 0.06105 | 1.2753 | 0.0006105 | 1.4481 | 0.0006105 | 1.2747 | 1.4475 | 18.2012 | 3.9053 | 1407.1127
38961.5538 | 2033 | 1 | 38961.5538 | 1956 | 1 | 42 | 2800.5 | 2898.5 | 124.1148 | 0.06105 | 119.4139 | 0.06105 | 1.2411 | 0.0006105 | 1.1941 | 0.0006105 | 1.2405 | 1.1935 | 21.2695 | 26.0668 | 8898.9508
38961.5543 | 1389 | 0 | 38961.5543 | 2126 | 0 | 42 | 2842.5 | 2940.5 | 84.7985 | 0 | 129.7924 | 0 | 0.84799 | 0 | 1.2979 | 0 | 0.84799 | 1.2979 | 77.4212 | 15.9163 | 76.5732
38961.5548 | 124 | 0 | 38961.5548 | 2303 | 0 | 42 | 2884.5 | 2982.5 | 7.5702 | 0 | 140.5983 | 0 | 0.075702 | 0 | 1.406 | 0 | 0.075702 | 1.406 | 1887.4032 | 7.0074 | 1887.3275

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -98 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
1 | -97 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
2 | -96 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
3 | -95 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
4 | -94 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
5 | -93 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
6 | -92 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
7 | -91 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
8 | -90 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
9 | -89 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
10 | -88 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
11 | -87 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
12 | -86 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
13 | -85 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 31 | 26.4 | 27.2
14 | -84 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
15 | -83 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
16 | -82 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
17 | -81 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
18 | -80 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.8 | 26.4 | 27.2
19 | -79 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.8 | 26.4 | 27.2
20 | -78 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.8 | 26.4 | 27.2
21 | -77 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.8 | 26.4 | 27.2
22 | -76 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.8 | 26.4 | 27.2
23 | -75 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.8 | 26.4 | 27.2
24 | -74 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.8 | 26.4 | 27.2
25 | -73 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.6 | 30.9 | 26.4 | 27.2
26 | -72 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.8 | 26.4 | 27.2
27 | -71 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.9 | 26.4 | 27.2
28 | -70 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.9 | 26.4 | 27.2
29 | -69 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.2
30 | -68 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.2
31 | -67 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.8 | 26.4 | 27.2
32 | -66 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.3 | 27.5 | 30.8 | 26.4 | 27.2
33 | -65 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
34 | -64 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.2
35 | -63 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.2
36 | -62 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
37 | -61 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
38 | -60 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
39 | -59 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.2
40 | -58 | 18.9 | 28.3 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
41 | -57 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
42 | -56 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.2
43 | -55 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
44 | -54 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
45 | -53 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
46 | -52 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
47 | -51 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
48 | -50 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
49 | -49 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
50 | -48 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
51 | -47 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
52 | -46 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
53 | -45 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
54 | -44 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
55 | -43 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
56 | -42 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
57 | -41 | 18.9 | 28.2 | 25.8 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
58 | -40 | 18.9 | 28.2 | 25.9 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
59 | -39 | 18.9 | 28.2 | 25.9 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
60 | -38 | 18.9 | 28.2 | 25.8 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
61 | -37 | 18.9 | 28.2 | 25.9 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
62 | -36 | 18.9 | 28.2 | 25.8 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
63 | -35 | 18.9 | 28.2 | 25.8 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
64 | -34 | 18.9 | 28.2 | 25.8 | 28.1 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
65 | -33 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
66 | -32 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
67 | -31 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
68 | -30 | 18.9 | 28.2 | 25.9 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
69 | -29 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
70 | -28 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
71 | -27 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
72 | -26 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
73 | -25 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
74 | -24 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
75 | -23 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 31 | 26.4 | 27.1
76 | -22 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
77 | -21 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
78 | -20 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
79 | -19 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
80 | -18 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
81 | -17 | 18.9 | 28.2 | 25.8 | 28 | 27.2 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
82 | -16 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
83 | -15 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
84 | -14 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.8 | 26.4 | 27.1
85 | -13 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
86 | -12 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
87 | -11 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.9 | 26.3 | 27.1
88 | -10 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.9 | 26.4 | 27.1
89 | -9 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 31 | 26.3 | 27.1
90 | -8 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 31 | 26.3 | 27.1
91 | -7 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.4 | 31 | 26.3 | 27.1
92 | -6 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.4 | 31 | 26.3 | 27.1
93 | -5 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 30.9 | 26.3 | 27.1
94 | -4 | 18.9 | 28.2 | 25.8 | 28 | 27.1 | 27.2 | 27.5 | 31 | 26.3 | 27.1
95 | -3 | 18.9 | 28.5 | 25.1 | 28.2 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.3
96 | -2 | 18.9 | 28.7 | 24.7 | 28.4 | 27.4 | 27.3 | 27.4 | 30.9 | 26.3 | 27.3
97 | -1 | 18.9 | 28.7 | 24.7 | 28.4 | 27.3 | 27.2 | 27.4 | 30.8 | 26.3 | 27.3
98 | 0 | 19.4 | 28.7 | 24.7 | 28.4 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.3
99 | 1 | 20.3 | 28.7 | 24.7 | 28.4 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
100 | 2 | 21.9 | 28.7 | 24.7 | 28.4 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
101 | 3 | 23.9 | 28.7 | 24.7 | 28.4 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
102 | 4 | 26.4 | 28.8 | 24.7 | 28.5 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
103 | 5 | 29.3 | 28.8 | 24.8 | 28.5 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
104 | 6 | 32.6 | 28.8 | 24.8 | 28.5 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
105 | 7 | 36.2 | 28.8 | 24.8 | 28.5 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
106 | 8 | 40 | 28.8 | 24.8 | 28.5 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
107 | 9 | 44.1 | 28.8 | 24.9 | 28.5 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
108 | 10 | 48.3 | 28.8 | 24.9 | 28.6 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
109 | 11 | 52.8 | 28.9 | 25 | 28.6 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
110 | 12 | 57.4 | 28.9 | 25 | 28.6 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
111 | 13 | 62.2 | 28.9 | 25.1 | 28.6 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
112 | 14 | 67.1 | 29 | 25.2 | 28.7 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
113 | 15 | 72.2 | 29 | 25.3 | 28.7 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
114 | 16 | 77.5 | 29.1 | 25.4 | 28.8 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
115 | 17 | 82.8 | 29.1 | 25.5 | 28.8 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
116 | 18 | 88.3 | 29.2 | 25.7 | 28.9 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
117 | 19 | 93.8 | 29.2 | 25.8 | 28.9 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
118 | 20 | 99.4 | 29.3 | 26 | 29 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
119 | 21 | 105.1 | 29.4 | 26.2 | 29.1 | 27.3 | 27.2 | 27.4 | 31 | 26.3 | 27.2
120 | 22 | 110.9 | 29.5 | 26.4 | 29.2 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
121 | 23 | 116.8 | 29.6 | 26.6 | 29.2 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
122 | 24 | 122.7 | 29.6 | 26.7 | 29.3 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
123 | 25 | 128.6 | 29.7 | 26.9 | 29.4 | 27.3 | 27.2 | 27.4 | 30.9 | 26.3 | 27.2
124 | 26 | 134.6 | 29.9 | 27.1 | 29.5 | 27.3 | 27.2 | 27.4 | 30.8 | 26.4 | 27.2
125 | 27 | 140.6 | 30 | 27.4 | 29.6 | 27.3 | 27.2 | 27.4 | 30.8 | 26.4 | 27.2
126 | 28 | 146.7 | 30.1 | 27.6 | 29.7 | 27.3 | 27.2 | 27.4 | 30.9 | 26.4 | 27.2
127 | 29 | 152.8 | 30.2 | 27.9 | 29.9 | 27.3 | 27.2 | 27.4 | 30.9 | 26.4 | 27.2
128 | 30 | 158.8 | 30.3 | 28.2 | 30 | 27.3 | 27.2 | 27.4 | 30.9 | 26.4 | 27.2
129 | 31 | 164.9 | 30.5 | 28.6 | 30.1 | 27.3 | 27.2 | 27.4 | 30.9 | 26.4 | 27.2
130 | 32 | 171 | 30.7 | 28.8 | 30.2 | 27.3 | 27.2 | 27.4 | 30.9 | 26.4 | 27.2
131 | 33 | 177.1 | 30.8 | 29.1 | 30.4 | 27.3 | 27.2 | 27.4 | 30.8 | 26.4 | 27.2
132 | 34 | 183.3 | 31 | 29.4 | 30.6 | 27.3 | 27.2 | 27.4 | 30.8 | 26.4 | 27.2
133 | 35 | 189.5 | 31.1 | 29.6 | 30.7 | 27.3 | 27.2 | 27.4 | 30.8 | 26.5 | 27.2
134 | 36 | 195.7 | 31.3 | 30 | 30.9 | 27.3 | 27.2 | 27.4 | 30.7 | 26.5 | 27.2
135 | 37 | 201.9 | 31.5 | 30.5 | 31.1 | 27.3 | 27.2 | 27.4 | 30.7 | 26.5 | 27.2
136 | 38 | 208 | 31.7 | 31 | 31.3 | 27.3 | 27.2 | 27.4 | 30.7 | 26.5 | 27.2
137 | 39 | 214.2 | 31.9 | 31.5 | 31.5 | 27.3 | 27.2 | 27.4 | 30.7 | 26.5 | 27.2
138 | 40 | 220.4 | 32.2 | 31.8 | 31.6 | 27.3 | 27.2 | 27.4 | 30.7 | 26.6 | 27.2
139 | 41 | 226.5 | 32.4 | 32 | 31.9 | 27.3 | 27.2 | 27.4 | 30.7 | 26.6 | 27.2
140 | 42 | 232.7 | 32.7 | 32.4 | 32.1 | 27.3 | 27.2 | 27.4 | 30.7 | 26.6 | 27.2
141 | 43 | 238.8 | 32.9 | 32.8 | 32.4 | 27.3 | 27.2 | 27.4 | 30.7 | 26.6 | 27.2
142 | 44 | 244.9 | 33.2 | 33.2 | 32.6 | 27.3 | 27.2 | 27.4 | 30.7 | 26.7 | 27.2
143 | 45 | 251.1 | 33.4 | 33.6 | 32.9 | 27.3 | 27.2 | 27.4 | 30.8 | 26.7 | 27.2
144 | 46 | 257.1 | 33.7 | 34.2 | 33.1 | 27.3 | 27.2 | 27.4 | 30.8 | 26.7 | 27.2
145 | 47 | 263.2 | 34 | 34.8 | 33.4 | 27.3 | 27.2 | 27.4 | 30.8 | 26.8 | 27.2
146 | 48 | 269.1 | 34.3 | 35.2 | 33.7 | 27.3 | 27.2 | 27.4 | 30.8 | 26.8 | 27.2
147 | 49 | 275.2 | 34.6 | 35.6 | 34 | 27.3 | 27.2 | 27.4 | 30.9 | 26.8 | 27.2
148 | 50 | 281.3 | 35 | 36.3 | 34.3 | 27.3 | 27.2 | 27.4 | 30.9 | 26.9 | 27.2
149 | 51 | 287.3 | 35.3 | 37 | 34.6 | 27.3 | 27.2 | 27.4 | 30.9 | 26.9 | 27.2
150 | 52 | 293.2 | 35.7 | 37.6 | 35 | 27.3 | 27.2 | 27.4 | 30.8 | 27 | 27.2
151 | 53 | 299.2 | 36 | 38.1 | 35.3 | 27.3 | 27.2 | 27.4 | 30.8 | 27 | 27.2
152 | 54 | 305.1 | 36.4 | 38.8 | 35.6 | 27.3 | 27.2 | 27.4 | 30.9 | 27 | 27.2
153 | 55 | 311 | 36.8 | 39.4 | 36 | 27.3 | 27.2 | 27.4 | 31 | 27.1 | 27.2
154 | 56 | 316.9 | 37.2 | 40.1 | 36.5 | 27.3 | 27.2 | 27.4 | 31 | 27.2 | 27.3
155 | 57 | 322.8 | 37.6 | 40.8 | 36.8 | 27.3 | 27.2 | 27.4 | 30.9 | 27.2 | 27.3
156 | 58 | 328.7 | 38 | 41.5 | 37.2 | 27.3 | 27.2 | 27.4 | 31 | 27.3 | 27.3
157 | 59 | 334.5 | 38.5 | 42.2 | 37.6 | 27.3 | 27.2 | 27.4 | 30.9 | 27.3 | 27.3
158 | 60 | 340.3 | 38.9 | 43 | 38.1 | 27.4 | 27.2 | 27.4 | 30.9 | 27.4 | 27.3
159 | 61 | 345.9 | 39.4 | 43.8 | 38.6 | 27.3 | 27.2 | 27.4 | 30.9 | 27.5 | 27.3
160 | 62 | 351.6 | 39.9 | 44.7 | 39 | 27.4 | 27.2 | 27.4 | 30.9 | 27.5 | 27.3
161 | 63 | 357.2 | 40.4 | 45.6 | 39.5 | 27.4 | 27.2 | 27.4 | 30.9 | 27.6 | 27.3
162 | 64 | 362.9 | 40.9 | 46.4 | 40 | 27.4 | 27.2 | 27.4 | 31 | 27.7 | 27.3
163 | 65 | 368.6 | 41.4 | 47.2 | 40.4 | 27.4 | 27.2 | 27.4 | 31 | 27.7 | 27.3
164 | 66 | 374.2 | 41.9 | 48 | 40.9 | 27.4 | 27.2 | 27.4 | 31 | 27.8 | 27.3
165 | 67 | 379.7 | 42.5 | 49 | 41.5 | 27.4 | 27.2 | 27.5 | 30.9 | 27.9 | 27.4
166 | 68 | 385.2 | 43.1 | 50 | 42 | 27.4 | 27.2 | 27.5 | 30.9 | 28 | 27.4
167 | 69 | 390.8 | 43.7 | 51 | 42.6 | 27.4 | 27.2 | 27.5 | 31 | 28.1 | 27.4
168 | 70 | 396.3 | 44.3 | 52 | 43.2 | 27.4 | 27.3 | 27.5 | 31.1 | 28.2 | 27.4
169 | 71 | 401.8 | 44.9 | 53.1 | 43.8 | 27.5 | 27.3 | 27.5 | 31 | 28.3 | 27.4
170 | 72 | 407.1 | 45.6 | 54.1 | 44.5 | 27.5 | 27.3 | 27.5 | 31 | 28.4 | 27.4
171 | 73 | 412.4 | 46.2 | 55.1 | 45.1 | 27.5 | 27.3 | 27.5 | 31.1 | 28.5 | 27.4
172 | 74 | 417.8 | 46.9 | 56.2 | 45.6 | 27.5 | 27.3 | 27.5 | 31.1 | 28.6 | 27.4
173 | 75 | 423.2 | 47.6 | 57.3 | 46.3 | 27.5 | 27.3 | 27.5 | 31.1 | 28.7 | 27.4
174 | 76 | 428.5 | 48.3 | 58.5 | 47 | 27.5 | 27.3 | 27.5 | 31.1 | 28.8 | 27.5
175 | 77 | 433.7 | 49 | 59.7 | 47.7 | 27.5 | 27.3 | 27.5 | 31.1 | 28.9 | 27.5
176 | 78 | 438.9 | 49.7 | 60.9 | 48.4 | 27.6 | 27.3 | 27.5 | 31.1 | 29.1 | 27.5
177 | 79 | 444.1 | 50.5 | 62.1 | 49.1 | 27.6 | 27.3 | 27.6 | 31.1 | 29.2 | 27.5
178 | 80 | 449.3 | 51.3 | 63.4 | 49.9 | 27.6 | 27.3 | 27.6 | 31.2 | 29.3 | 27.6
179 | 81 | 454.3 | 52.1 | 64.6 | 50.6 | 27.6 | 27.4 | 27.6 | 31.2 | 29.5 | 27.6
180 | 82 | 459.3 | 52.9 | 65.9 | 51.5 | 27.6 | 27.4 | 27.6 | 31.2 | 29.6 | 27.6
181 | 83 | 464.2 | 53.7 | 67.2 | 52.3 | 27.7 | 27.4 | 27.6 | 31.2 | 29.8 | 27.6
182 | 84 | 469.1 | 54.5 | 68.5 | 53.1 | 27.7 | 27.4 | 27.6 | 31.3 | 29.9 | 27.7
183 | 85 | 474 | 55.4 | 69.9 | 53.9 | 27.7 | 27.4 | 27.6 | 31.3 | 30.1 | 27.7
184 | 86 | 478.9 | 56.3 | 71.3 | 54.7 | 27.7 | 27.4 | 27.6 | 31.3 | 30.2 | 27.7
185 | 87 | 483.8 | 57.1 | 72.8 | 55.5 | 27.8 | 27.5 | 27.7 | 31.3 | 30.4 | 27.8
186 | 88 | 488.7 | 58.1 | 74.2 | 56.4 | 27.9 | 27.5 | 27.7 | 31.3 | 30.6 | 27.9
187 | 89 | 493.2 | 59 | 75.7 | 57.3 | 27.9 | 27.5 | 27.7 | 31.2 | 30.7 | 27.9
188 | 90 | 497.3 | 59.9 | 77.1 | 58.2 | 27.9 | 27.5 | 27.7 | 31.2 | 30.9 | 28
189 | 91 | 500.9 | 60.9 | 78.5 | 59 | 28 | 27.5 | 27.7 | 31.3 | 31.1 | 28
190 | 92 | 504.3 | 61.8 | 79.9 | 59.9 | 28 | 27.6 | 27.7 | 31.3 | 31.3 | 28.1
191 | 93 | 507.6 | 62.8 | 81.4 | 60.7 | 28 | 27.6 | 27.8 | 31.3 | 31.5 | 28.1
192 | 94 | 510.6 | 63.7 | 82.9 | 61.7 | 28.1 | 27.6 | 27.8 | 31.3 | 31.7 | 28.1
193 | 95 | 513.4 | 64.7 | 84.2 | 62.8 | 28.1 | 27.6 | 27.8 | 31.3 | 31.9 | 28.2
194 | 96 | 516.1 | 65.6 | 85.6 | 63.6 | 28.1 | 27.6 | 27.8 | 31.4 | 32.2 | 28.2
195 | 97 | 518.8 | 66.6 | 87.1 | 64.5 | 28.2 | 27.7 | 27.9 | 31.4 | 32.4 | 28.3
196 | 98 | 521.2 | 67.5 | 88.6 | 65.4 | 28.2 | 27.7 | 27.9 | 31.4 | 32.6 | 28.3
197 | 99 | 523.3 | 68.4 | 90.1 | 66.2 | 28.2 | 27.7 | 27.9 | 31.5 | 32.8 | 28.4
198 | 100 | 525.1 | 69.4 | 91.6 | 67.2 | 28.3 | 27.7 | 27.9 | 31.5 | 33.1 | 28.4
199 | 101 | 526.7 | 70.4 | 93 | 68.1 | 28.3 | 27.7 | 28 | 31.6 | 33.3 | 28.5
200 | 102 | 528 | 71.3 | 94.4 | 68.9 | 28.3 | 27.8 | 28 | 31.7 | 33.6 | 28.5
201 | 103 | 529.1 | 72.2 | 95.7 | 69.8 | 28.4 | 27.8 | 28 | 31.8 | 33.8 | 28.5
202 | 104 | 529.9 | 73.1 | 97.1 | 70.8 | 28.4 | 27.8 | 28.1 | 31.8 | 34.1 | 28.6
203 | 105 | 530.5 | 74.1 | 98.4 | 71.7 | 28.5 | 27.8 | 28.1 | 31.9 | 34.4 | 28.7
204 | 106 | 530.9 | 75 | 99.7 | 72.6 | 28.5 | 27.9 | 28.1 | 31.9 | 34.6 | 28.8
205 | 107 | 531.2 | 76 | 100.9 | 73.5 | 28.6 | 27.9 | 28.1 | 32 | 34.9 | 28.8
206 | 108 | 531.2 | 76.9 | 102.2 | 74.4 | 28.6 | 27.9 | 28.2 | 32 | 35.2 | 28.9
207 | 109 | 531.1 | 77.9 | 103.5 | 75.3 | 28.7 | 28 | 28.2 | 32 | 35.5 | 29
208 | 110 | 530.9 | 78.8 | 104.7 | 76.2 | 28.7 | 28 | 28.3 | 32.1 | 35.8 | 29.1
209 | 111 | 530.7 | 79.8 | 105.8 | 77 | 28.8 | 28 | 28.3 | 32.2 | 36 | 29.2
210 | 112 | 530.3 | 80.7 | 107 | 77.9 | 28.9 | 28.1 | 28.3 | 32.2 | 36.3 | 29.3
211 | 113 | 529.8 | 81.6 | 108.2 | 78.8 | 28.9 | 28.1 | 28.4 | 32.2 | 36.6 | 29.4
212 | 114 | 529.4 | 82.6 | 109.3 | 79.7 | 29 | 28.2 | 28.4 | 32.3 | 36.9 | 29.5
213 | 115 | 529 | 83.5 | 110.5 | 80.6 | 29.1 | 28.2 | 28.5 | 32.3 | 37.2 | 29.6
214 | 116 | 528.6 | 84.4 | 111.7 | 81.6 | 29.2 | 28.2 | 28.5 | 32.4 | 37.5 | 29.8
215 | 117 | 528.1 | 85.3 | 112.9 | 82.5 | 29.2 | 28.3 | 28.6 | 32.4 | 37.8 | 29.9
216 | 118 | 527.6 | 86.3 | 113.9 | 83.3 | 29.3 | 28.3 | 28.6 | 32.4 | 38.2 | 30
217 | 119 | 527.2 | 87.2 | 115 | 84.2 | 29.4 | 28.4 | 28.7 | 32.5 | 38.5 | 30.2
218 | 120 | 526.7 | 88.1 | 116.1 | 85.1 | 29.5 | 28.4 | 28.7 | 32.6 | 38.8 | 30.3
219 | 121 | 526.3 | 88.9 | 117.3 | 86 | 29.6 | 28.5 | 28.8 | 32.7 | 39.1 | 30.4
220 | 122 | 525.9 | 89.9 | 118.5 | 86.8 | 29.7 | 28.5 | 28.8 | 32.8 | 39.4 | 30.6
221 | 123 | 525.6 | 90.7 | 119.6 | 87.6 | 29.8 | 28.6 | 28.9 | 32.8 | 39.7 | 30.7
222 | 124 | 525.4 | 91.6 | 120.7 | 88.5 | 29.8 | 28.6 | 28.9 | 32.9 | 40.1 | 30.9
223 | 125 | 525.2 | 92.6 | 121.9 | 89.3 | 29.9 | 28.7 | 29 | 33 | 40.4 | 31
224 | 126 | 525 | 93.5 | 123.1 | 90.1 | 30 | 28.8 | 29 | 33.1 | 40.7 | 31.2
225 | 127 | 524.9 | 94.3 | 124.2 | 91 | 30.1 | 28.8 | 29.1 | 33.2 | 41.1 | 31.3
226 | 128 | 524.8 | 95.3 | 125.3 | 91.9 | 30.2 | 28.9 | 29.2 | 33.3 | 41.4 | 31.5
227 | 129 | 524.7 | 96.1 | 126.5 | 92.8 | 30.3 | 28.9 | 29.2 | 33.4 | 41.8 | 31.7
228 | 130 | 524.7 | 97 | 127.7 | 93.6 | 30.4 | 29 | 29.3 | 33.4 | 42.1 | 31.9
229 | 131 | 524.7 | 97.9 | 128.8 | 94.5 | 30.5 | 29 | 29.4 | 33.5 | 42.4 | 32
230 | 132 | 524.8 | 98.8 | 129.9 | 95.4 | 30.6 | 29.1 | 29.4 | 33.6 | 42.8 | 32.2
231 | 133 | 525 | 99.6 | 131 | 96.2 | 30.7 | 29.2 | 29.5 | 33.6 | 43.1 | 32.4
232 | 134 | 525.2 | 100.5 | 132.2 | 97 | 30.8 | 29.2 | 29.6 | 33.7 | 43.5 | 32.5
233 | 135 | 525.4 | 101.4 | 133.4 | 97.9 | 30.9 | 29.3 | 29.6 | 33.8 | 43.9 | 32.7
234 | 136 | 525.7 | 102.3 | 134.5 | 98.8 | 31 | 29.4 | 29.7 | 33.9 | 44.2 | 32.9
235 | 137 | 526 | 103.2 | 135.7 | 99.6 | 31.2 | 29.5 | 29.8 | 34 | 44.6 | 33.1
236 | 138 | 526.3 | 104.1 | 136.9 | 100.4 | 31.3 | 29.5 | 29.8 | 34.2 | 44.9 | 33.3
237 | 139 | 526.6 | 105 | 138 | 101.2 | 31.4 | 29.6 | 29.9 | 34.3 | 45.3 | 33.5
238 | 140 | 526.8 | 105.9 | 139.2 | 102.1 | 31.5 | 29.7 | 30 | 34.4 | 45.7 | 33.7
239 | 141 | 527.1 | 106.7 | 140.3 | 103.1 | 31.6 | 29.8 | 30.1 | 34.5 | 46 | 33.9
240 | 142 | 527.4 | 107.6 | 141.4 | 103.8 | 31.7 | 29.8 | 30.2 | 34.6 | 46.4 | 34.1
241 | 143 | 527.6 | 108.5 | 142.5 | 104.7 | 31.9 | 29.9 | 30.2 | 34.8 | 46.8 | 34.3
242 | 144 | 527.9 | 109.3 | 143.6 | 105.4 | 32 | 30 | 30.3 | 34.9 | 47.1 | 34.5
243 | 145 | 528.1 | 110.2 | 144.8 | 106.3 | 32.1 | 30.1 | 30.4 | 35 | 47.5 | 34.7
244 | 146 | 528.3 | 111.1 | 146 | 107.2 | 32.2 | 30.2 | 30.5 | 35.1 | 47.9 | 34.9
245 | 147 | 528.4 | 111.9 | 147.1 | 108 | 32.4 | 30.2 | 30.6 | 35.3 | 48.2 | 35.2
246 | 148 | 528.6 | 112.8 | 148.2 | 108.9 | 32.5 | 30.3 | 30.7 | 35.4 | 48.6 | 35.4
247 | 149 | 528.7 | 113.7 | 149.4 | 109.8 | 32.6 | 30.4 | 30.7 | 35.5 | 49 | 35.6
248 | 150 | 528.8 | 114.5 | 150.5 | 110.6 | 32.7 | 30.5 | 30.8 | 35.6 | 49.4 | 35.8
249 | 151 | 528.9 | 115.4 | 151.6 | 111.4 | 32.9 | 30.6 | 30.9 | 35.7 | 49.8 | 36
250 | 152 | 529 | 116.3 | 152.6 | 112.2 | 33 | 30.7 | 31 | 35.8 | 50.1 | 36.2
251 | 153 | 529.2 | 117.1 | 153.8 | 113 | 33.2 | 30.8 | 31.1 | 36 | 50.5 | 36.5
252 | 154 | 529.3 | 118 | 154.9 | 113.9 | 33.3 | 30.9 | 31.2 | 36.1 | 50.9 | 36.7
253 | 155 | 529.4 | 118.8 | 156 | 114.7 | 33.5 | 31 | 31.3 | 36.3 | 51.3 | 36.9
254 | 156 | 529.5 | 119.7 | 157.1 | 115.5 | 33.6 | 31.1 | 31.4 | 36.4 | 51.7 | 37.2
255 | 157 | 529.5 | 120.6 | 158.2 | 116.3 | 33.7 | 31.2 | 31.5 | 36.5 | 52.1 | 37.4
256 | 158 | 529.5 | 121.4 | 159.3 | 117.1 | 33.9 | 31.3 | 31.6 | 36.7 | 52.4 | 37.6
257 | 159 | 529.6 | 122.2 | 160.4 | 118 | 34.1 | 31.4 | 31.7 | 36.8 | 52.8 | 37.9
258 | 160 | 529.6 | 123.1 | 161.4 | 118.8 | 34.2 | 31.5 | 31.8 | 36.9 | 53.2 | 38.1
259 | 161 | 529.6 | 123.9 | 162.5 | 119.7 | 34.4 | 31.6 | 31.9 | 37 | 53.6 | 38.3
260 | 162 | 529.7 | 124.8 | 163.5 | 120.4 | 34.5 | 31.7 | 32 | 37.2 | 54 | 38.6
261 | 163 | 529.7 | 125.6 | 164.6 | 121.2 | 34.7 | 31.8 | 32.1 | 37.3 | 54.4 | 38.8
262 | 164 | 529.8 | 126.4 | 165.7 | 122 | 34.8 | 31.9 | 32.2 | 37.5 | 54.8 | 39
263 | 165 | 529.8 | 127.3 | 166.8 | 122.8 | 35 | 32.1 | 32.3 | 37.6 | 55.2 | 39.3
264 | 166 | 529.9 | 128.1 | 168 | 123.7 | 35.2 | 32.2 | 32.4 | 37.7 | 55.6 | 39.5
265 | 167 | 529.9 | 128.9 | 169 | 124.5 | 35.3 | 32.3 | 32.5 | 37.8 | 56 | 39.7
266 | 168 | 529.9 | 129.8 | 170 | 125.3 | 35.5 | 32.4 | 32.6 | 38 | 56.4 | 40
267 | 169 | 529.9 | 130.6 | 171 | 126.2 | 35.7 | 32.5 | 32.8 | 38.1 | 56.8 | 40.2
268 | 170 | 529.9 | 131.4 | 171.9 | 127 | 35.9 | 32.6 | 32.9 | 38.2 | 57.2 | 40.5
269 | 171 | 530 | 132.3 | 173 | 127.8 | 36 | 32.8 | 33 | 38.4 | 57.6 | 40.7
270 | 172 | 530 | 133.1 | 174 | 128.6 | 36.2 | 32.9 | 33.1 | 38.5 | 58 | 41
271 | 173 | 530 | 133.9 | 175.1 | 129.4 | 36.4 | 33 | 33.2 | 38.7 | 58.4 | 41.2
272 | 174 | 530.1 | 134.7 | 176.2 | 130.3 | 36.6 | 33.1 | 33.3 | 38.9 | 58.8 | 41.4
273 | 175 | 530.2 | 135.5 | 177.3 | 131 | 36.8 | 33.3 | 33.5 | 39.1 | 59.2 | 41.7
274 | 176 | 530.2 | 136.4 | 178.3 | 131.7 | 36.9 | 33.4 | 33.6 | 39.2 | 59.5 | 42
275 | 177 | 530.2 | 137.2 | 179.3 | 132.5 | 37.1 | 33.5 | 33.7 | 39.3 | 60 | 42.2
276 | 178 | 530.3 | 138 | 180.4 | 133.4 | 37.3 | 33.7 | 33.8 | 39.5 | 60.4 | 42.4
277 | 179 | 530.3 | 138.8 | 181.4 | 134.3 | 37.5 | 33.8 | 34 | 39.7 | 60.8 | 42.7
278 | 180 | 530.3 | 139.6 | 182.4 | 135 | 37.7 | 33.9 | 34.1 | 39.8 | 61.1 | 42.9
279 | 181 | 530.4 | 140.4 | 183.5 | 135.8 | 37.9 | 34.1 | 34.2 | 40 | 61.6 | 43.1
280 | 182 | 530.4 | 141.2 | 184.4 | 136.6 | 38.1 | 34.2 | 34.4 | 40.2 | 62 | 43.3
281 | 183 | 530.5 | 142 | 185.5 | 137.4 | 38.3 | 34.3 | 34.5 | 40.3 | 62.4 | 43.6
282 | 184 | 530.6 | 142.8 | 186.5 | 138.1 | 38.5 | 34.5 | 34.6 | 40.5 | 62.8 | 43.8
283 | 185 | 530.6 | 143.7 | 187.5 | 138.9 | 38.7 | 34.6 | 34.8 | 40.6 | 63.2 | 44
284 | 186 | 530.6 | 144.4 | 188.5 | 139.7 | 38.9 | 34.8 | 34.9 | 40.8 | 63.6 | 44.3
285 | 187 | 530.7 | 145.2 | 189.5 | 140.5 | 39.1 | 34.9 | 35 | 41 | 64 | 44.5
286 | 188 | 530.7 | 146 | 190.5 | 141.3 | 39.3 | 35.1 | 35.2 | 41.2 | 64.4 | 44.7
287 | 189 | 530.8 | 146.8 | 191.6 | 142 | 39.5 | 35.2 | 35.3 | 41.4 | 64.8 | 45
288 | 190 | 530.8 | 147.6 | 192.6 | 142.8 | 39.7 | 35.4 | 35.5 | 41.6 | 65.2 | 45.2
289 | 191 | 530.9 | 148.4 | 193.5 | 143.6 | 39.9 | 35.5 | 35.6 | 41.7 | 65.6 | 45.4
290 | 192 | 530.8 | 149.2 | 194.5 | 144.3 | 40.1 | 35.7 | 35.8 | 41.9 | 66 | 45.6
291 | 193 | 530.8 | 149.9 | 195.5 | 145.1 | 40.4 | 35.9 | 35.9 | 42 | 66.4 | 45.9
292 | 194 | 530.8 | 150.7 | 196.5 | 145.9 | 40.6 | 36 | 36.1 | 42.2 | 66.8 | 46.1
293 | 195 | 530.9 | 151.5 | 197.5 | 146.7 | 40.8 | 36.2 | 36.2 | 42.3 | 67.2 | 46.3
294 | 196 | 531 | 152.3 | 198.5 | 147.5 | 41 | 36.3 | 36.4 | 42.5 | 67.7 | 46.6
295 | 197 | 531 | 153.1 | 199.4 | 148.3 | 41.2 | 36.5 | 36.5 | 42.7 | 68.1 | 46.8
296 | 198 | 531.1 | 153.8 | 200.4 | 149 | 41.5 | 36.7 | 36.7 | 42.9 | 68.5 | 47
297 | 199 | 531.1 | 154.6 | 201.4 | 149.8 | 41.7 | 36.8 | 36.8 | 43.1 | 68.9 | 47.2
298 | 200 | 531.1 | 155.4 | 202.4 | 150.6 | 41.9 | 37 | 37 | 43.3 | 69.3 | 47.4
299 | 201 | 531.1 | 156.2 | 203.4 | 151.3 | 42.1 | 37.2 | 37.1 | 43.5 | 69.7 | 47.6
300 | 202 | 531.1 | 156.9 | 204.4 | 152.1 | 42.4 | 37.3 | 37.3 | 43.7 | 70.1 | 47.9
301 | 203 | 531.1 | 157.7 | 205.4 | 152.9 | 42.6 | 37.5 | 37.5 | 43.9 | 70.5 | 48.1
302 | 204 | 531.1 | 158.5 | 206.3 | 153.6 | 42.8 | 37.7 | 37.6 | 44.1 | 71 | 48.3
303 | 205 | 531.1 | 159.3 | 207.3 | 154.3 | 43.1 | 37.8 | 37.8 | 44.3 | 71.4 | 48.5
304 | 206 | 531.2 | 160 | 208.2 | 155.1 | 43.3 | 38 | 37.9 | 44.5 | 71.8 | 48.7
305 | 207 | 531.2 | 160.8 | 209.2 | 155.9 | 43.6 | 38.2 | 38.1 | 44.7 | 72.2 | 48.9
306 | 208 | 531.3 | 161.5 | 210.1 | 156.6 | 43.8 | 38.4 | 38.3 | 44.8 | 72.6 | 49.1
307 | 209 | 531.2 | 162.2 | 211 | 157.4 | 44 | 38.6 | 38.5 | 45 | 73 | 49.4
308 | 210 | 531.2 | 163 | 211.9 | 158.1 | 44.3 | 38.8 | 38.6 | 45.2 | 73.4 | 49.6
309 | 211 | 531.2 | 163.8 | 212.9 | 158.9 | 44.6 | 38.9 | 38.8 | 45.4 | 73.9 | 49.8
310 | 212 | 531.1 | 164.5 | 213.8 | 159.6 | 44.8 | 39.1 | 39 | 45.7 | 74.3 | 50
311 | 213 | 531.1 | 165.2 | 214.8 | 160.3 | 45 | 39.3 | 39.1 | 45.9 | 74.7 | 50.2
312 | 214 | 531 | 166 | 215.8 | 161 | 45.3 | 39.5 | 39.3 | 46.1 | 75.1 | 50.5
313 | 215 | 531 | 166.8 | 216.7 | 161.8 | 45.6 | 39.7 | 39.5 | 46.3 | 75.5 | 50.7
314 | 216 | 531.1 | 167.5 | 217.6 | 162.5 | 45.8 | 39.9 | 39.7 | 46.5 | 75.9 | 50.9
315 | 217 | 531 | 168.3 | 218.5 | 163.3 | 46.1 | 40.1 | 39.9 | 46.7 | 76.4 | 51.2
316 | 218 | 531 | 169 | 219.4 | 164.1 | 46.3 | 40.3 | 40 | 46.9 | 76.8 | 51.4
317 | 219 | 531.1 | 169.8 | 220.3 | 164.8 | 46.6 | 40.5 | 40.2 | 47.1 | 77.2 | 51.6
318 | 220 | 531.1 | 170.5 | 221.2 | 165.6 | 46.9 | 40.7 | 40.4 | 47.3 | 77.6 | 51.8
319 | 221 | 531 | 171.3 | 222.1 | 166.3 | 47.1 | 40.9 | 40.6 | 47.5 | 78 | 52.1
320 | 222 | 531 | 172 | 223 | 167.1 | 47.4 | 41.1 | 40.8 | 47.7 | 78.4 | 52.3
321 | 223 | 531 | 172.7 | 223.9 | 167.7 | 47.6 | 41.3 | 41 | 48 | 78.9 | 52.5
322 | 224 | 530.9 | 173.5 | 224.9 | 168.5 | 47.9 | 41.5 | 41.2 | 48.2 | 79.3 | 52.7
323 | 225 | 530.9 | 174.2 | 225.8 | 169.3 | 48.2 | 41.7 | 41.4 | 48.4 | 79.7 | 52.9
324 | 226 | 530.9 | 175 | 226.6 | 170 | 48.4 | 41.9 | 41.6 | 48.7 | 80.1 | 53.1
325 | 227 | 530.9 | 175.7 | 227.5 | 170.7 | 48.7 | 42.1 | 41.7 | 48.9 | 80.5 | 53.4
326 | 228 | 530.9 | 176.4 | 228.5 | 171.5 | 49 | 42.3 | 41.9 | 49.1 | 80.9 | 53.6
327 | 229 | 530.9 | 177.1 | 229.3 | 172.2 | 49.3 | 42.5 | 42.1 | 49.3 | 81.3 | 53.8
328 | 230 | 530.8 | 177.9 | 230.2 | 172.9 | 49.5 | 42.7 | 42.3 | 49.6 | 81.8 | 54
329 | 231 | 530.9 | 178.6 | 231.1 | 173.5 | 49.8 | 43 | 42.5 | 49.8 | 82.2 | 54.2
330 | 232 | 530.9 | 179.3 | 232 | 174.2 | 50.1 | 43.2 | 42.7 | 50 | 82.6 | 54.4
331 | 233 | 530.9 | 180 | 232.8 | 175 | 50.4 | 43.4 | 42.9 | 50.2 | 83 | 54.6
332 | 234 | 530.9 | 180.8 | 233.7 | 175.8 | 50.7 | 43.6 | 43.1 | 50.5 | 83.4 | 54.8
333 | 235 | 530.8 | 181.5 | 234.6 | 176.4 | 51 | 43.8 | 43.3 | 50.7 | 83.9 | 55
334 | 236 | 530.8 | 182.2 | 235.4 | 177.1 | 51.2 | 44.1 | 43.5 | 50.9 | 84.3 | 55.2
335 | 237 | 530.8 | 182.9 | 236.4 | 177.8 | 51.5 | 44.3 | 43.8 | 51.1 | 84.7 | 55.4
336 | 238 | 530.7 | 183.6 | 237.2 | 178.6 | 51.8 | 44.5 | 44 | 51.4 | 85.1 | 55.6
337 | 239 | 530.7 | 184.3 | 238.1 | 179.3 | 52.1 | 44.7 | 44.2 | 51.6 | 85.5 | 55.8
338 | 240 | 530.7 | 185 | 239 | 180 | 52.4 | 45 | 44.4 | 51.9 | 85.9 | 56
339 | 241 | 530.7 | 185.7 | 239.9 | 180.8 | 52.7 | 45.2 | 44.6 | 52.2 | 86.4 | 56.1
340 | 242 | 530.7 | 186.5 | 240.7 | 181.5 | 53 | 45.4 | 44.8 | 52.4 | 86.8 | 56.3
341 | 243 | 530.6 | 187.2 | 241.6 | 182.1 | 53.3 | 45.7 | 45 | 52.6 | 87.2 | 56.5
342 | 244 | 530.6 | 187.9 | 242.5 | 182.7 | 53.6 | 45.9 | 45.2 | 52.9 | 87.6 | 56.6
343 | 245 | 530.5 | 188.6 | 243.3 | 183.5 | 53.9 | 46.1 | 45.5 | 53.1 | 88 | 56.8
344 | 246 | 530.5 | 189.3 | 244.1 | 184.1 | 54.2 | 46.4 | 45.7 | 53.4 | 88.5 | 56.9
345 | 247 | 530.5 | 190 | 245 | 184.9 | 54.5 | 46.6 | 45.9 | 53.7 | 88.9 | 57
346 | 248 | 530.4 | 190.7 | 245.8 | 185.6 | 54.8 | 46.8 | 46.1 | 54 | 89.3 | 57.1
347 | 249 | 530.4 | 191.4 | 246.7 | 186.3 | 55.1 | 47.1 | 46.3 | 54.2 | 89.7 | 57.3
348 | 250 | 530.3 | 192.1 | 247.5 | 187 | 55.4 | 47.3 | 46.6 | 54.5 | 90.1 | 57.3
349 | 251 | 530.3 | 192.8 | 248.4 | 187.7 | 55.7 | 47.6 | 46.8 | 54.7 | 90.6 | 57.5
350 | 252 | 530.3 | 193.5 | 249.3 | 188.4 | 56 | 47.8 | 47 | 55 | 91 | 57.6
351 | 253 | 530.4 | 194.2 | 250.1 | 189 | 56.3 | 48.1 | 47.2 | 55.2 | 91.4 | 57.7
352 | 254 | 530.4 | 194.9 | 250.9 | 189.7 | 56.6 | 48.3 | 47.5 | 55.5 | 91.9 | 57.8
353 | 255 | 530.5 | 195.6 | 251.8 | 190.5 | 56.9 | 48.6 | 47.7 | 55.7 | 92.3 | 57.9
354 | 256 | 530.5 | 196.2 | 252.7 | 191.1 | 57.2 | 48.8 | 47.9 | 56 | 92.7 | 58
355 | 257 | 530.5 | 196.9 | 253.5 | 191.7 | 57.5 | 49 | 48.1 | 56.2 | 93.1 | 58.1
356 | 258 | 530.5 | 197.6 | 254.4 | 192.5 | 57.8 | 49.3 | 48.4 | 56.5 | 93.6 | 58.1
357 | 259 | 530.5 | 198.3 | 255.2 | 193.2 | 58.1 | 49.5 | 48.6 | 56.7 | 94 | 58.2
358 | 260 | 530.5 | 198.9 | 256 | 193.9 | 58.5 | 49.8 | 48.8 | 56.9 | 94.4 | 58.3
359 | 261 | 530.4 | 199.6 | 256.8 | 194.6 | 58.8 | 50.1 | 49.1 | 57.2 | 94.9 | 58.4
360 | 262 | 530.4 | 200.3 | 257.6 | 195.3 | 59.1 | 50.3 | 49.3 | 57.5 | 95.3 | 58.5
361 | 263 | 530.3 | 201 | 258.4 | 195.9 | 59.4 | 50.6 | 49.5 | 57.7 | 95.7 | 58.6
362 | 264 | 530.3 | 201.7 | 259.3 | 196.6 | 59.7 | 50.8 | 49.8 | 58 | 96.1 | 58.6
363 | 265 | 530.3 | 202.3 | 260.1 | 197.3 | 60 | 51.1 | 50 | 58.2 | 96.6 | 58.7
364 | 266 | 530.3 | 203 | 260.9 | 197.9 | 60.4 | 51.3 | 50.3 | 58.5 | 97 | 58.8
365 | 267 | 530.2 | 203.7 | 261.7 | 198.5 | 60.7 | 51.6 | 50.5 | 58.8 | 97.4 | 58.9
366 | 268 | 530.2 | 204.3 | 262.5 | 199.3 | 61 | 51.8 | 50.7 | 59.1 | 97.9 | 59
367 | 269 | 530.1 | 205 | 263.2 | 200 | 61.3 | 52.1 | 51 | 59.4 | 98.3 | 59
368 | 270 | 530.1 | 205.7 | 264 | 200.6 | 61.7 | 52.4 | 51.2 | 59.7 | 98.7 | 59.1
369 | 271 | 530.1 | 206.3 | 264.8 | 201.3 | 62 | 52.6 | 51.5 | 60 | 99.1 | 59.2
370 | 272 | 530 | 207 | 265.7 | 202 | 62.3 | 52.9 | 51.7 | 60.3 | 99.6 | 59.3
371 | 273 | 530 | 207.6 | 266.5 | 202.7 | 62.6 | 53.1 | 52 | 60.6 | 100 | 59.3
372 | 274 | 529.9 | 208.3 | 267.3 | 203.3 | 63 | 53.4 | 52.2 | 60.9 | 100.4 | 59.4
373 | 275 | 529.9 | 209 | 268 | 203.9 | 63.3 | 53.7 | 52.5 | 61.2 | 100.8 | 59.5
374 | 276 | 529.9 | 209.6 | 268.9 | 204.7 | 63.6 | 53.9 | 52.7 | 61.5 | 101.3 | 59.6
375 | 277 | 529.9 | 210.3 | 269.7 | 205.3 | 63.9 | 54.2 | 53 | 61.8 | 101.7 | 59.6
376 | 278 | 529.9 | 210.9 | 270.4 | 206 | 64.2 | 54.5 | 53.2 | 62 | 102.1 | 59.7
377 | 279 | 529.9 | 211.6 | 271.2 | 206.6 | 64.6 | 54.7 | 53.5 | 62.3 | 102.5 | 59.8
378 | 280 | 529.9 | 212.2 | 272 | 207.2 | 64.9 | 55 | 53.7 | 62.5 | 103 | 59.8
379 | 281 | 529.8 | 212.9 | 272.7 | 207.8 | 65.2 | 55.3 | 54 | 62.8 | 103.4 | 59.9
380 | 282 | 529.8 | 213.5 | 273.5 | 208.5 | 65.6 | 55.5 | 54.2 | 63 | 103.9 | 60
381 | 283 | 529.8 | 214.1 | 274.3 | 209.2 | 65.9 | 55.8 | 54.5 | 63.3 | 104.3 | 60.1
382 | 284 | 529.7 | 214.8 | 275 | 209.9 | 66.2 | 56.1 | 54.7 | 63.7 | 104.7 | 60.2
383 | 285 | 529.7 | 215.5 | 275.8 | 210.5 | 66.6 | 56.4 | 55 | 64 | 105.2 | 60.3
384 | 286 | 529.7 | 216.1 | 276.6 | 211.2 | 66.9 | 56.6 | 55.3 | 64.3 | 105.6 | 60.4
385 | 287 | 529.7 | 216.7 | 277.3 | 211.8 | 67.2 | 56.9 | 55.5 | 64.6 | 106 | 60.5
386 | 288 | 529.7 | 217.3 | 278.1 | 212.5 | 67.6 | 57.2 | 55.8 | 64.9 | 106.5 | 60.6
387 | 289 | 529.7 | 218 | 278.8 | 213.1 | 67.9 | 57.4 | 56.1 | 65.2 | 106.9 | 60.7
388 | 290 | 529.7 | 218.6 | 279.6 | 213.7 | 68.2 | 57.7 | 56.3 | 65.4 | 107.3 | 60.8
389 | 291 | 529.7 | 219.2 | 280.3 | 214.3 | 68.6 | 58 | 56.6 | 65.8 | 107.8 | 61
390 | 292 | 529.7 | 219.9 | 281.1 | 215 | 68.9 | 58.3 | 56.8 | 66.1 | 108.2 | 61.2
391 | 293 | 529.7 | 220.5 | 281.8 | 215.6 | 69.2 | 58.6 | 57.1 | 66.4 | 108.6 | 61.3
392 | 294 | 529.6 | 221.1 | 282.6 | 216.3 | 69.6 | 58.8 | 57.4 | 66.7 | 109.1 | 61.5
393 | 295 | 529.5 | 221.8 | 283.3 | 216.9 | 69.9 | 59.1 | 57.6 | 67 | 109.5 | 61.6
394 | 296 | 529.5 | 222.4 | 284.1 | 217.5 | 70.2 | 59.4 | 57.9 | 67.3 | 110 | 61.7
395 | 297 | 529.5 | 223 | 284.8 | 218.3 | 70.6 | 59.7 | 58.2 | 67.6 | 110.4 | 61.9
396 | 298 | 529.4 | 223.6 | 285.6 | 218.9 | 70.9 | 60 | 58.4 | 67.9 | 110.8 | 62
397 | 299 | 529.4 | 224.3 | 286.3 | 219.5 | 71.3 | 60.3 | 58.7 | 68.2 | 111.3 | 62.2
398 | 300 | 529.4 | 224.9 | 287 | 220 | 71.6 | 60.5 | 59 | 68.5 | 111.7 | 62.3
399 | 301 | 529.4 | 225.5 | 287.7 | 220.6 | 72 | 60.8 | 59.3 | 68.8 | 112.2 | 62.5
400 | 302 | 529.4 | 226.2 | 288.5 | 221.2 | 72.3 | 61.1 | 59.5 | 69.1 | 112.6 | 62.6
401 | 303 | 529.4 | 226.8 | 289.2 | 221.8 | 72.6 | 61.4 | 59.8 | 69.5 | 113.1 | 62.8
402 | 304 | 529.4 | 227.4 | 289.9 | 222.5 | 73 | 61.7 | 60.1 | 69.8 | 113.5 | 63
403 | 305 | 529.4 | 228 | 290.6 | 223.1 | 73.3 | 62 | 60.4 | 70.1 | 114 | 63.2
404 | 306 | 529.4 | 228.6 | 291.3 | 223.7 | 73.7 | 62.3 | 60.6 | 70.4 | 114.4 | 63.4
405 | 307 | 529.5 | 229.3 | 292 | 224.4 | 74 | 62.6 | 60.9 | 70.7 | 114.8 | 63.7
406 | 308 | 529.5 | 229.9 | 292.7 | 224.9 | 74.4 | 62.9 | 61.2 | 71 | 115.3 | 63.9
407 | 309 | 529.5 | 230.5 | 293.5 | 225.5 | 74.7 | 63.2 | 61.5 | 71.3 | 115.7 | 64.1
408 | 310 | 529.5 | 231.1 | 294.2 | 226.1 | 75.1 | 63.4 | 61.8 | 71.6 | 116.2 | 64.3
409 | 311 | 529.5 | 231.7 | 294.9 | 226.9 | 75.4 | 63.7 | 62.1 | 72 | 116.6 | 64.5
410 | 312 | 529.5 | 232.3 | 295.6 | 227.5 | 75.8 | 64 | 62.3 | 72.3 | 117.1 | 64.7
411 | 313 | 529.5 | 232.9 | 296.3 | 228 | 76.1 | 64.3 | 62.6 | 72.6 | 117.5 | 64.8
412 | 314 | 529.5 | 233.5 | 297 | 228.6 | 76.5 | 64.6 | 62.9 | 72.9 | 118 | 65
413 | 315 | 529.6 | 234.1 | 297.7 | 229.3 | 76.8 | 64.9 | 63.2 | 73.2 | 118.4 | 65.2
414 | 316 | 529.6 | 234.7 | 298.4 | 229.9 | 77.2 | 65.2 | 63.5 | 73.5 | 118.8 | 65.3
415 | 317 | 529.6 | 235.3 | 299.1 | 230.5 | 77.5 | 65.5 | 63.8 | 73.8 | 119.3 | 65.5
416 | 318 | 529.6 | 236 | 299.8 | 231.1 | 77.9 | 65.8 | 64.1 | 74.2 | 119.7 | 65.7
417 | 319 | 529.6 | 236.6 | 300.5 | 231.6 | 78.2 | 66.1 | 64.4 | 74.5 | 120.2 | 65.9
418 | 320 | 529.6 | 237.2 | 301.2 | 232.2 | 78.6 | 66.4 | 64.6 | 74.9 | 120.6 | 66.1
419 | 321 | 529.6 | 237.8 | 301.9 | 232.8 | 78.9 | 66.7 | 64.9 | 75.2 | 121.1 | 66.3
420 | 322 | 529.6 | 238.4 | 302.6 | 233.4 | 79.3 | 67.1 | 65.2 | 75.5 | 121.5 | 66.6
421 | 323 | 529.7 | 239 | 303.3 | 234.1 | 79.6 | 67.4 | 65.5 | 75.8 | 122 | 66.8
422 | 324 | 529.7 | 239.6 | 304 | 234.6 | 80 | 67.7 | 65.8 | 76.2 | 122.4 | 67.1
423 | 325 | 529.6 | 240.2 | 304.7 | 235.2 | 80.3 | 68 | 66.1 | 76.5 | 122.8 | 67.4
424 | 326 | 529.6 | 240.8 | 305.3 | 235.8 | 80.7 | 68.3 | 66.4 | 76.9 | 123.3 | 67.8
425 | 327 | 529.6 | 241.4 | 305.9 | 236.4 | 81.1 | 68.6 | 66.7 | 77.2 | 123.7 | 68.1
426 | 328 | 529.7 | 242 | 306.6 | 237 | 81.4 | 68.9 | 67 | 77.6 | 124.2 | 68.4
427 | 329 | 529.7 | 242.5 | 307.3 | 237.6 | 81.8 | 69.2 | 67.3 | 77.9 | 124.6 | 68.8
428 | 330 | 529.6 | 243.1 | 308 | 238.2 | 82.1 | 69.5 | 67.6 | 78.2 | 125.1 | 69.1
429 | 331 | 529.6 | 243.7 | 308.6 | 238.7 | 82.5 | 69.9 | 67.9 | 78.6 | 125.5 | 69.4
430 | 332 | 529.6 | 244.3 | 309.3 | 239.2 | 82.9 | 70.2 | 68.2 | 78.9 | 125.9 | 69.7
431 | 333 | 529.6 | 244.9 | 310 | 239.9 | 83.2 | 70.5 | 68.6 | 79.3 | 126.4 | 70
432 | 334 | 529.6 | 245.5 | 310.6 | 240.4 | 83.6 | 70.8 | 68.9 | 79.7 | 126.8 | 70.2
433 | 335 | 529.6 | 246.1 | 311.3 | 241 | 83.9 | 71.1 | 69.2 | 80 | 127.3 | 70.5
434 | 336 | 529.5 | 246.7 | 311.9 | 241.6 | 84.3 | 71.5 | 69.5 | 80.3 | 127.7 | 70.8
435 | 337 | 529.5 | 247.3 | 312.6 | 242.2 | 84.7 | 71.8 | 69.8 | 80.6 | 128.2 | 71.1
436 | 338 | 529.4 | 247.8 | 313.2 | 242.8 | 85 | 72.1 | 70.1 | 81 | 128.6 | 71.4
437 | 339 | 529.3 | 248.4 | 313.9 | 243.3 | 85.4 | 72.4 | 70.4 | 81.3 | 129 | 71.7
438 | 340 | 529.4 | 249 | 314.5 | 243.9 | 85.8 | 72.8 | 70.7 | 81.6 | 129.5 | 72
439 | 341 | 529.3 | 249.6 | 315.1 | 244.5 | 86.1 | 73.1 | 71 | 82 | 129.9 | 72.3
440 | 342 | 529.3 | 250.1 | 315.7 | 245.1 | 86.5 | 73.4 | 71.4 | 82.3 | 130.3 | 72.6
441 | 343 | 529.2 | 250.7 | 316.3 | 245.7 | 86.9 | 73.8 | 71.7 | 82.6 | 130.8 | 72.9
442 | 344 | 529.2 | 251.3 | 317 | 246.2 | 87.3 | 74.1 | 72 | 83 | 131.2 | 73.2
443 | 345 | 529.2 | 251.9 | 317.6 | 246.8 | 87.6 | 74.4 | 72.3 | 83.3 | 131.7 | 73.5
444 | 346 | 529.2 | 252.5 | 318.3 | 247.4 | 88 | 74.7 | 72.6 | 83.6 | 132.1 | 73.8
445 | 347 | 529.1 | 253 | 318.9 | 247.9 | 88.3 | 75.1 | 73 | 84 | 132.5 | 74.2
446 | 348 | 529.1 | 253.6 | 319.6 | 248.5 | 88.7 | 75.4 | 73.3 | 84.3 | 133 | 74.5
447 | 349 | 529.2 | 254.1 | 320.2 | 249.1 | 89.1 | 75.7 | 73.6 | 84.6 | 133.4 | 74.8
448 | 350 | 529.2 | 254.7 | 320.8 | 249.7 | 89.4 | 76.1 | 73.9 | 85 | 133.8 | 75.1
449 | 351 | 529.3 | 255.3 | 321.5 | 250.3 | 89.8 | 76.4 | 74.3 | 85.3 | 134.3 | 75.5
450 | 352 | 529.3 | 255.9 | 322.1 | 250.8 | 90.2 | 76.7 | 74.6 | 85.6 | 134.7 | 75.8
451 | 353 | 529.3 | 256.4 | 322.7 | 251.3 | 90.5 | 77.1 | 74.9 | 86 | 135.1 | 76.1
452 | 354 | 529.4 | 257 | 323.2 | 251.9 | 90.9 | 77.4 | 75.2 | 86.3 | 135.6 | 76.5
453 | 355 | 529.4 | 257.5 | 323.9 | 252.5 | 91.3 | 77.7 | 75.6 | 86.6 | 136 | 76.8
454 | 356 | 529.5 | 258.1 | 324.6 | 253 | 91.6 | 78.1 | 75.9 | 87 | 136.4 | 77.2
455 | 357 | 529.5 | 258.6 | 325.2 | 253.5 | 92 | 78.4 | 76.2 | 87.4 | 136.8 | 77.5
456 | 358 | 529.5 | 259.2 | 325.8 | 254.1 | 92.4 | 78.8 | 76.6 | 87.8 | 137.3 | 77.8
457 | 359 | 529.5 | 259.8 | 326.4 | 254.7 | 92.7 | 79.1 | 76.9 | 88.1 | 137.7 | 78.2
458 | 360 | 529.5 | 260.3 | 327 | 255.3 | 93.1 | 79.4 | 77.2 | 88.5 | 138.1 | 78.5
459 | 361 | 529.5 | 260.9 | 327.6 | 255.8 | 93.5 | 79.8 | 77.5 | 88.8 | 138.6 | 78.9
460 | 362 | 529.4 | 261.4 | 328.2 | 256.4 | 93.8 | 80.1 | 77.9 | 89.1 | 139 | 79.2
461 | 363 | 529.4 | 262 | 328.8 | 257 | 94.2 | 80.5 | 78.2 | 89.5 | 139.4 | 79.5
462 | 364 | 529.3 | 262.5 | 329.4 | 257.5 | 94.6 | 80.8 | 78.5 | 89.8 | 139.8 | 79.9
463 | 365 | 529.3 | 263.1 | 330 | 258 | 94.9 | 81.1 | 78.9 | 90.1 | 140.2 | 80.2
464 | 366 | 529.3 | 263.7 | 330.5 | 258.5 | 95.3 | 81.5 | 79.2 | 90.5 | 140.7 | 80.5
465 | 367 | 529.2 | 264.2 | 331.1 | 259.1 | 95.7 | 81.8 | 79.5 | 90.9 | 141.1 | 80.9
466 | 368 | 529.2 | 264.7 | 331.7 | 259.7 | 96 | 82.2 | 79.9 | 91.2 | 141.5 | 81.2
467 | 369 | 529.2 | 265.3 | 332.3 | 260.2 | 96.4 | 82.5 | 80.2 | 91.6 | 141.9 | 81.6
468 | 370 | 529.1 | 265.8 | 332.9 | 260.7 | 96.8 | 82.9 | 80.6 | 91.9 | 142.4 | 81.9
469 | 371 | 529.1 | 266.4 | 333.4 | 261.4 | 97.1 | 83.2 | 80.9 | 92.3 | 142.8 | 82.3
470 | 372 | 529.1 | 266.9 | 334 | 262 | 97.5 | 83.6 | 81.2 | 92.6 | 143.2 | 82.6
471 | 373 | 529.1 | 267.5 | 334.6 | 262.7 | 97.8 | 83.9 | 81.6 | 92.9 | 143.6 | 83
472 | 374 | 529.1 | 268 | 335.2 | 263.1 | 98.2 | 84.3 | 81.9 | 93.3 | 144 | 83.3
473 | 375 | 529.1 | 268.5 | 335.8 | 263.5 | 98.6 | 84.6 | 82.3 | 93.7 | 144.5 | 83.7
474 | 376 | 529 | 269.1 | 336.3 | 264.1 | 98.9 | 85 | 82.6 | 94 | 144.9 | 84
475 | 377 | 529 | 269.6 | 336.9 | 264.6 | 99.3 | 85.3 | 82.9 | 94.4 | 145.3 | 84.3
476 | 378 | 529 | 270.2 | 337.4 | 265.1 | 99.6 | 85.7 | 83.3 | 94.7 | 145.7 | 84.7
477 | 379 | 529 | 270.7 | 338 | 265.6 | 100 | 86 | 83.6 | 95.1 | 146.1 | 85
478 | 380 | 529 | 271.2 | 338.6 | 266.1 | 100.4 | 86.4 | 84 | 95.4 | 146.5 | 85.3
479 | 381 | 529 | 271.8 | 339.1 | 266.6 | 100.7 | 86.7 | 84.3 | 95.7 | 147 | 85.6
480 | 382 | 529 | 272.3 | 339.7 | 267.1 | 101.1 | 87.1 | 84.7 | 96.1 | 147.4 | 86
481 | 383 | 529 | 272.8 | 340.3 | 267.7 | 101.4 | 87.4 | 85 | 96.5 | 147.8 | 86.3
482 | 384 | 529 | 273.3 | 340.9 | 268.3 | 101.8 | 87.7 | 85.4 | 96.8 | 148.2 | 86.7
483 | 385 | 529.1 | 273.9 | 341.4 | 268.8 | 102.2 | 88.1 | 85.7 | 97.2 | 148.6 | 87
484 | 386 | 529.1 | 274.4 | 342 | 269.3 | 102.5 | 88.4 | 86 | 97.5 | 149 | 87.4
485 | 387 | 529 | 274.9 | 342.5 | 269.8 | 102.9 | 88.8 | 86.4 | 97.8 | 149.5 | 87.7
486 | 388 | 529 | 275.4 | 343 | 270.3 | 103.2 | 89.1 | 86.7 | 98.2 | 149.9 | 88.1
487 | 389 | 529 | 275.9 | 343.6 | 270.9 | 103.6 | 89.5 | 87.1 | 98.5 | 150.3 | 88.4
488 | 390 | 529 | 276.5 | 344.1 | 271.4 | 104 | 89.8 | 87.4 | 98.9 | 150.7 | 88.8
489 | 391 | 528.9 | 277 | 344.7 | 271.9 | 104.3 | 90.2 | 87.8 | 99.2 | 151.1 | 89.1
490 | 392 | 528.9 | 277.5 | 345.2 | 272.3 | 104.7 | 90.5 | 88.1 | 99.5 | 151.5 | 89.5
491 | 393 | 528.8 | 278 | 345.7 | 272.8 | 105.1 | 90.9 | 88.5 | 99.9 | 151.9 | 89.8
492 | 394 | 528.8 | 278.5 | 346.3 | 273.4 | 105.5 | 91.2 | 88.8 | 100.2 | 152.3 | 90.1
493 | 395 | 528.8 | 279 | 346.8 | 273.9 | 105.8 | 91.6 | 89.2 | 100.5 | 152.7 | 90.4
494 | 396 | 528.8 | 279.6 | 347.4 | 274.4 | 106.2 | 91.9 | 89.5 | 100.8 | 153.1 | 90.7
495 | 397 | 528.8 | 280.1 | 347.9 | 274.9 | 106.6 | 92.3 | 89.9 | 101.2 | 153.5 | 91
496 | 398 | 528.8 | 280.6 | 348.4 | 275.4 | 107 | 92.6 | 90.2 | 101.6 | 153.9 | 91.4
497 | 399 | 528.7 | 281.1 | 348.9 | 275.9 | 107.4 | 93 | 90.5 | 101.9 | 154.4 | 91.7
498 | 400 | 528.7 | 281.6 | 349.4 | 276.5 | 107.8 | 93.3 | 90.9 | 102.2 | 154.8 | 92
499 | 401 | 528.7 | 282.1 | 350 | 277 | 108.2 | 93.7 | 91.2 | 102.5 | 155.2 | 92.4
500 | 402 | 528.7 | 282.6 | 350.5 | 277.4 | 108.5 | 94 | 91.6 | 102.8 | 155.6 | 92.7
501 | 403 | 528.7 | 283.1 | 351 | 277.9 | 108.9 | 94.4 | 91.9 | 103.1 | 156 | 93
502 | 404 | 528.7 | 283.6 | 351.5 | 278.4 | 109.3 | 94.7 | 92.3 | 103.5 | 156.4 | 93.4
503 | 405 | 528.7 | 284.1 | 352.1 | 278.9 | 109.7 | 95 | 92.6 | 103.8 | 156.8 | 93.7
504 | 406 | 528.6 | 284.6 | 352.6 | 279.5 | 110.1 | 95.4 | 93 | 104.1 | 157.2 | 94.1
505 | 407 | 528.6 | 285.1 | 353.1 | 279.9 | 110.5 | 95.8 | 93.3 | 104.4 | 157.6 | 94.5
506 | 408 | 528.5 | 285.6 | 353.6 | 280.4 | 110.9 | 96.1 | 93.7 | 104.7 | 158 | 94.8
507 | 409 | 528.5 | 286.1 | 354 | 280.9 | 111.3 | 96.5 | 94 | 105 | 158.4 | 95.2
508 | 410 | 528.4 | 286.6 | 354.5 | 281.4 | 111.8 | 96.8 | 94.4 | 105.3 | 158.8 | 95.5
509 | 411 | 528.4 | 287.1 | 355 | 281.9 | 112.2 | 97.2 | 94.7 | 105.7 | 159.2 | 95.8
510 | 412 | 528.3 | 287.6 | 355.6 | 282.3 | 112.6 | 97.5 | 95.1 | 106 | 159.7 | 96.2
511 | 413 | 528.2 | 288.1 | 356.1 | 283 | 113 | 97.9 | 95.4 | 106.3 | 160.1 | 96.5
512 | 414 | 528.2 | 288.6 | 356.6 | 283.5 | 113.4 | 98.2 | 95.8 | 106.6 | 160.5 | 96.9
513 | 415 | 528.2 | 289.1 | 357.1 | 283.9 | 113.8 | 98.6 | 96.1 | 107 | 160.9 | 97.2
514 | 416 | 528.2 | 289.5 | 357.6 | 284.4 | 114.2 | 99 | 96.5 | 107.3 | 161.3 | 97.5
515 | 417 | 528.3 | 290 | 358 | 284.8 | 114.7 | 99.3 | 96.8 | 107.6 | 161.7 | 97.9
516 | 418 | 528.4 | 290.5 | 358.5 | 285.3 | 115.1 | 99.7 | 97.2 | 107.9 | 162.1 | 98.2
517 | 419 | 528.4 | 291 | 359 | 285.8 | 115.5 | 100 | 97.5 | 108.2 | 162.5 | 98.5
518 | 420 | 528.4 | 291.5 | 359.5 | 286.3 | 115.9 | 100.4 | 97.9 | 108.5 | 162.9 | 98.9
519 | 421 | 528.4 | 292 | 360 | 286.8 | 116.3 | 100.8 | 98.3 | 108.8 | 163.3 | 99.2
520 | 422 | 528.4 | 292.4 | 360.5 | 287.3 | 116.7 | 101.1 | 98.6 | 109.1 | 163.7 | 99.6
521 | 423 | 528.5 | 292.9 | 361 | 287.7 | 117.2 | 101.5 | 99 | 109.4 | 164.1 | 99.9
522 | 424 | 528.5 | 293.4 | 361.5 | 288.2 | 117.6 | 101.9 | 99.3 | 109.8 | 164.5 | 100.2
523 | 425 | 528.6 | 293.9 | 362 | 288.8 | 118 | 102.3 | 99.7 | 110.1 | 164.9 | 100.6
524 | 426 | 528.6 | 294.3 | 362.5 | 289.2 | 118.4 | 102.6 | 100 | 110.4 | 165.3 | 100.9
525 | 427 | 528.6 | 294.8 | 362.9 | 289.7 | 118.9 | 103 | 100.4 | 110.8 | 165.7 | 101.2
526 | 428 | 528.6 | 295.3 | 363.3 | 290.2 | 119.3 | 103.4 | 100.8 | 111.1 | 166.1 | 101.6
527 | 429 | 528.6 | 295.7 | 363.8 | 290.7 | 119.7 | 103.8 | 101.1 | 111.4 | 166.5 | 101.9
528 | 430 | 528.6 | 296.2 | 364.3 | 291.1 | 120.1 | 104.2 | 101.5 | 111.8 | 166.9 | 102.2
529 | 431 | 528.6 | 296.7 | 364.8 | 291.6 | 120.6 | 104.6 | 101.8 | 112.1 | 167.3 | 102.6
530 | 432 | 528.6 | 297.2 | 365.3 | 292 | 121 | 105 | 102.2 | 112.4 | 167.7 | 102.9
531 | 433 | 528.5 | 297.6 | 365.7 | 292.5 | 121.4 | 105.3 | 102.6 | 112.7 | 168.1 | 103.2
532 | 434 | 528.5 | 298.1 | 366.2 | 292.9 | 121.9 | 105.7 | 102.9 | 113 | 168.5 | 103.6
533 | 435 | 528.5 | 298.6 | 366.6 | 293.4 | 122.3 | 106.1 | 103.3 | 113.4 | 168.9 | 103.9
534 | 436 | 528.5 | 299 | 367.1 | 293.9 | 122.7 | 106.5 | 103.7 | 113.7 | 169.4 | 104.2
535 | 437 | 528.6 | 299.5 | 367.6 | 294.3 | 123.2 | 106.9 | 104 | 114 | 169.8 | 104.6
536 | 438 | 528.6 | 300 | 368 | 294.8 | 123.6 | 107.3 | 104.4 | 114.4 | 170.2 | 104.9
537 | 439 | 528.6 | 300.4 | 368.5 | 295.2 | 124 | 107.7 | 104.8 | 114.7 | 170.6 | 105.2
538 | 440 | 528.6 | 300.9 | 368.9 | 295.7 | 124.5 | 108.1 | 105.2 | 115 | 171 | 105.5
539 | 441 | 528.5 | 301.3 | 369.4 | 296.2 | 124.9 | 108.5 | 105.5 | 115.3 | 171.4 | 105.9
540 | 442 | 528.5 | 301.8 | 369.8 | 296.7 | 125.3 | 108.9 | 105.9 | 115.6 | 171.8 | 106.2
541 | 443 | 528.5 | 302.2 | 370.3 | 297.1 | 125.7 | 109.3 | 106.3 | 115.9 | 172.2 | 106.6
542 | 444 | 528.5 | 302.7 | 370.7 | 297.6 | 126.2 | 109.7 | 106.7 | 116.3 | 172.6 | 106.9
543 | 445 | 528.4 | 303.1 | 371.1 | 298 | 126.6 | 110.1 | 107 | 116.6 | 173 | 107.3
544 | 446 | 528.4 | 303.6 | 371.6 | 298.4 | 127.1 | 110.5 | 107.4 | 116.9 | 173.4 | 107.6
545 | 447 | 528.3 | 304.1 | 372.1 | 298.9 | 127.5 | 111 | 107.8 | 117.2 | 173.8 | 108
546 | 448 | 528.3 | 304.5 | 372.5 | 299.3 | 127.9 | 111.4 | 108.2 | 117.6 | 174.2 | 108.3
547 | 449 | 528.3 | 305 | 372.9 | 299.7 | 128.4 | 111.8 | 108.5 | 117.9 | 174.6 | 108.6
548 | 450 | 528.3 | 305.4 | 373.3 | 300.2 | 128.8 | 112.2 | 108.9 | 118.2 | 175 | 108.9
549 | 451 | 528.2 | 305.8 | 373.7 | 300.7 | 129.2 | 112.7 | 109.3 | 118.6 | 175.4 | 109.3
550 | 452 | 528.2 | 306.3 | 374.2 | 301.1 | 129.7 | 113.1 | 109.7 | 118.9 | 175.8 | 109.6
551 | 453 | 528.2 | 306.7 | 374.6 | 301.6 | 130.1 | 113.5 | 110.1 | 119.3 | 176.2 | 109.9
552 | 454 | 528.2 | 307.2 | 375.1 | 302 | 130.5 | 113.9 | 110.4 | 119.6 | 176.6 | 110.2
553 | 455 | 528.2 | 307.6 | 375.5 | 302.4 | 131 | 114.4 | 110.8 | 120 | 177 | 110.6
554 | 456 | 528.2 | 308 | 375.9 | 302.9 | 131.4 | 114.8 | 111.2 | 120.4 | 177.4 | 110.9
555 | 457 | 528.2 | 308.5 | 376.4 | 303.4 | 131.8 | 115.2 | 111.6 | 120.7 | 177.8 | 111.2
556 | 458 | 528.2 | 308.9 | 376.8 | 303.8 | 132.3 | 115.6 | 111.9 | 121.1 | 178.2 | 111.6
557 | 459 | 528.1 | 309.4 | 377.2 | 304.2 | 132.7 | 116.1 | 112.3 | 121.4 | 178.6 | 111.9
558 | 460 | 528.1 | 309.8 | 377.6 | 304.7 | 133.1 | 116.5 | 112.7 | 121.7 | 179 | 112.2
559 | 461 | 528.1 | 310.2 | 378.1 | 305.3 | 133.5 | 116.9 | 113.1 | 122 | 179.4 | 112.6
560 | 462 | 528.2 | 310.7 | 378.5 | 305.7 | 134 | 117.4 | 113.5 | 122.4 | 179.8 | 112.9
561 | 463 | 528.1 | 311.1 | 378.9 | 306.2 | 134.4 | 117.8 | 113.8 | 122.7 | 180.2 | 113.2
562 | 464 | 528.1 | 311.5 | 379.3 | 306.5 | 134.8 | 118.2 | 114.2 | 123.1 | 180.6 | 113.6
563 | 465 | 528.1 | 312 | 379.7 | 306.9 | 135.2 | 118.7 | 114.6 | 123.5 | 181 | 113.9
564 | 466 | 528.1 | 312.4 | 380.1 | 307.3 | 135.7 | 119.1 | 115 | 123.8 | 181.4 | 114.3
565 | 467 | 528.2 | 312.8 | 380.5 | 307.8 | 136.1 | 119.6 | 115.3 | 124.2 | 181.8 | 114.6
566 | 468 | 528.2 | 313.2 | 380.9 | 308.2 | 136.5 | 120 | 115.7 | 124.6 | 182.2 | 114.9
567 | 469 | 528.2 | 313.7 | 381.3 | 308.6 | 137 | 120.4 | 116.1 | 124.9 | 182.6 | 115.2
568 | 470 | 528.2 | 314.1 | 381.8 | 309.1 | 137.4 | 120.9 | 116.5 | 125.3 | 183 | 115.5
569 | 471 | 528.2 | 314.5 | 382.2 | 309.5 | 137.9 | 121.3 | 116.9 | 125.7 | 183.4 | 115.8
570 | 472 | 528.3 | 314.9 | 382.6 | 309.9 | 138.3 | 121.7 | 117.3 | 126.1 | 183.8 | 116.1
571 | 473 | 528.3 | 315.3 | 383 | 310.3 | 138.8 | 122.2 | 117.6 | 126.5 | 184.1 | 116.4
572 | 474 | 528.2 | 315.8 | 383.4 | 310.8 | 139.2 | 122.6 | 118 | 126.8 | 184.5 | 116.8
573 | 475 | 528.3 | 316.2 | 383.8 | 311.3 | 139.7 | 123 | 118.4 | 127.1 | 184.9 | 117.1
574 | 476 | 528.3 | 316.6 | 384.2 | 311.7 | 140.1 | 123.5 | 118.8 | 127.5 | 185.3 | 117.4
575 | 477 | 528.3 | 317 | 384.6 | 312.2 | 140.6 | 123.9 | 119.2 | 127.8 | 185.7 | 117.7
576 | 478 | 528.3 | 317.4 | 385 | 312.6 | 141.1 | 124.4 | 119.6 | 128.2 | 186 | 118
577 | 479 | 528.2 | 317.8 | 385.4 | 313 | 141.5 | 124.8 | 120 | 128.6 | 186.4 | 118.4
578 | 480 | 528.2 | 318.3 | 385.7 | 313.4 | 142 | 125.2 | 120.4 | 129 | 186.8 | 118.7
579 | 481 | 528.2 | 318.7 | 386.1 | 313.8 | 142.5 | 125.7 | 120.8 | 129.3 | 187.1 | 119
580 | 482 | 528.2 | 319.1 | 386.5 | 314.2 | 143 | 126.1 | 121.2 | 129.7 | 187.5 | 119.3
581 | 483 | 528.2 | 319.5 | 386.9 | 314.6 | 143.5 | 126.6 | 121.6 | 130.1 | 187.9 | 119.6
582 | 484 | 528.2 | 319.9 | 387.3 | 315 | 144 | 127 | 122 | 130.4 | 188.2 | 119.9
583 | 485 | 528.2 | 320.3 | 387.7 | 315.5 | 144.5 | 127.5 | 122.4 | 130.8 | 188.6 | 120.2
584 | 486 | 528.2 | 320.7 | 388.1 | 315.9 | 145 | 127.9 | 122.8 | 131.3 | 189 | 120.5
585 | 487 | 528.2 | 321.1 | 388.4 | 316.4 | 145.5 | 128.4 | 123.2 | 131.7 | 189.3 | 120.8
586 | 488 | 528.1 | 321.5 | 388.8 | 316.9 | 146 | 128.8 | 123.6 | 132.1 | 189.7 | 121.1
587 | 489 | 528.1 | 322 | 389.2 | 317.2 | 146.6 | 129.3 | 124 | 132.5 | 190 | 121.4
588 | 490 | 528.1 | 322.3 | 389.6 | 317.6 | 147.1 | 129.7 | 124.5 | 132.9 | 190.4 | 121.7
589 | 491 | 528.2 | 322.8 | 390 | 318 | 147.6 | 130.2 | 124.9 | 133.2 | 190.7 | 122
590 | 492 | 528.3 | 323.2 | 390.4 | 318.4 | 148.2 | 130.6 | 125.3 | 133.6 | 191.1 | 122.3
591 | 493 | 528.3 | 323.6 | 390.8 | 318.7 | 148.7 | 131.1 | 125.7 | 134 | 191.4 | 122.6
592 | 494 | 528.4 | 323.9 | 391.1 | 319.1 | 149.3 | 131.5 | 126.1 | 134.4 | 191.8 | 122.9
593 | 495 | 528.4 | 324.3 | 391.5 | 319.5 | 149.8 | 132 | 126.5 | 134.8 | 192.1 | 123.3
594 | 496 | 528.4 | 324.8 | 391.9 | 320 | 150.3 | 132.5 | 127 | 135.2 | 192.5 | 123.6
595 | 497 | 528.4 | 325.2 | 392.2 | 320.4 | 150.9 | 132.9 | 127.4 | 135.6 | 192.8 | 123.9
596 | 498 | 528.4 | 325.5 | 392.6 | 320.8 | 151.4 | 133.4 | 127.8 | 136 | 193.2 | 124.2
597 | 499 | 528.4 | 325.9 | 393 | 321.1 | 151.9 | 133.8 | 128.2 | 136.4 | 193.5 | 124.6
598 | 500 | 528.4 | 326.3 | 393.3 | 321.5 | 152.5 | 134.3 | 128.7 | 136.7 | 193.8 | 124.9
599 | 501 | 528.4 | 326.7 | 393.7 | 321.9 | 153.1 | 134.8 | 129.1 | 137.2 | 194.2 | 125.2
600 | 502 | 528.4 | 327.1 | 394.1 | 322.4 | 153.6 | 135.2 | 129.5 | 137.6 | 194.5 | 125.5
601 | 503 | 528.4 | 327.5 | 394.4 | 322.7 | 154.1 | 135.7 | 130 | 137.9 | 194.8 | 125.8
602 | 504 | 528.3 | 327.9 | 394.8 | 323.2 | 154.7 | 136.1 | 130.4 | 138.3 | 195.2 | 126.2
603 | 505 | 528.3 | 328.3 | 395.1 | 323.5 | 155.2 | 136.6 | 130.9 | 138.7 | 195.5 | 126.5
604 | 506 | 528.3 | 328.7 | 395.5 | 323.9 | 155.7 | 137.1 | 131.3 | 139.1 | 195.8 | 126.8
605 | 507 | 528.2 | 329.1 | 395.8 | 324.3 | 156.3 | 137.5 | 131.7 | 139.4 | 196.2 | 127.1
606 | 508 | 528.2 | 329.4 | 396.2 | 324.7 | 156.8 | 138 | 132.2 | 139.8 | 196.5 | 127.4
607 | 509 | 528.1 | 329.8 | 396.6 | 325.1 | 157.4 | 138.5 | 132.6 | 140.2 | 196.8 | 127.7
608 | 510 | 528.1 | 330.2 | 396.9 | 325.5 | 157.9 | 139 | 133.1 | 140.5 | 197.2 | 128
609 | 511 | 528.1 | 330.6 | 397.2 | 325.9 | 158.4 | 139.4 | 133.5 | 140.9 | 197.5 | 128.3
610 | 512 | 528.1 | 331 | 397.6 | 326.2 | 159 | 139.9 | 134 | 141.3 | 197.8 | 128.6
611 | 513 | 528 | 331.3 | 397.9 | 326.6 | 159.5 | 140.4 | 134.5 | 141.7 | 198.1 | 128.9
612 | 514 | 527.9 | 331.7 | 398.3 | 327 | 160.1 | 140.9 | 134.9 | 142.1 | 198.5 | 129.3
613 | 515 | 527.9 | 332.1 | 398.6 | 327.4 | 160.6 | 141.4 | 135.4 | 142.5 | 198.8 | 129.6
614 | 516 | 527.9 | 332.5 | 399 | 327.8 | 161.1 | 141.9 | 135.8 | 142.9 | 199.1 | 129.9
615 | 517 | 527.9 | 332.8 | 399.3 | 328.2 | 161.7 | 142.3 | 136.3 | 143.3 | 199.4 | 130.2
616 | 518 | 527.9 | 333.2 | 399.7 | 328.5 | 162.2 | 142.8 | 136.8 | 143.7 | 199.7 | 130.5
617 | 519 | 527.9 | 333.6 | 400 | 328.9 | 162.8 | 143.3 | 137.2 | 144.1 | 200 | 130.8
618 | 520 | 527.9 | 334 | 400.3 | 329.3 | 163.3 | 143.8 | 137.7 | 144.5 | 200.3 | 131.1
619 | 521 | 527.9 | 334.3 | 400.6 | 329.7 | 163.9 | 144.3 | 138.2 | 144.9 | 200.6 | 131.4
620 | 522 | 527.9 | 334.7 | 401 | 330.1 | 164.4 | 144.8 | 138.6 | 145.3 | 200.9 | 131.7
621 | 523 | 527.8 | 335.1 | 401.3 | 330.5 | 165 | 145.3 | 139.1 | 145.7 | 201.2 | 132
622 | 524 | 527.8 | 335.4 | 401.6 | 330.9 | 165.5 | 145.8 | 139.6 | 146.1 | 201.5 | 132.3
623 | 525 | 527.8 | 335.8 | 401.9 | 331.2 | 166 | 146.3 | 140.1 | 146.5 | 201.8 | 132.6
624 | 526 | 527.9 | 336.2 | 402.3 | 331.6 | 166.5 | 146.8 | 140.5 | 146.8 | 202.1 | 132.9
625 | 527 | 527.9 | 336.5 | 402.6 | 331.9 | 167 | 147.2 | 141 | 147.2 | 202.4 | 133.1
626 | 528 | 527.9 | 336.9 | 402.9 | 332.3 | 167.5 | 147.7 | 141.5 | 147.6 | 202.7 | 133.4
627 | 529 | 527.9 | 337.3 | 403.3 | 332.7 | 168 | 148.2 | 141.9 | 148 | 203 | 133.7
628 | 530 | 527.9 | 337.6 | 403.6 | 333 | 168.5 | 148.7 | 142.4 | 148.4 | 203.3 | 134
629 | 531 | 527.9 | 338 | 403.9 | 333.4 | 169 | 149.2 | 142.9 | 148.8 | 203.5 | 134.3
630 | 532 | 528 | 338.3 | 404.2 | 333.8 | 169.5 | 149.7 | 143.3 | 149.1 | 203.8 | 134.6
631 | 533 | 528 | 338.7 | 404.6 | 334.2 | 170 | 150.2 | 143.8 | 149.5 | 204.1 | 134.9
632 | 534 | 528 | 339 | 404.9 | 334.5 | 170.5 | 150.7 | 144.3 | 149.9 | 204.3 | 135.2
633 | 535 | 528 | 339.4 | 405.2 | 334.8 | 171 | 151.2 | 144.7 | 150.4 | 204.6 | 135.5
634 | 536 | 528 | 339.8 | 405.5 | 335.2 | 171.5 | 151.7 | 145.2 | 150.8 | 204.9 | 135.8
635 | 537 | 528 | 340.1 | 405.8 | 335.6 | 172 | 152.1 | 145.6 | 151.2 | 205.1 | 136
636 | 538 | 528 | 340.5 | 406.1 | 335.9 | 172.5 | 152.6 | 146.1 | 151.6 | 205.4 | 136.3
637 | 539 | 528 | 340.8 | 406.4 | 336.3 | 173 | 153.1 | 146.6 | 152 | 205.7 | 136.6
638 | 540 | 528 | 341.2 | 406.7 | 336.7 | 173.5 | 153.6 | 147 | 152.5 | 205.9 | 136.9
639 | 541 | 528 | 341.5 | 407 | 337 | 174 | 154.1 | 147.5 | 152.9 | 206.1 | 137.2
640 | 542 | 528 | 341.9 | 407.4 | 337.4 | 174.5 | 154.6 | 148 | 153.3 | 206.4 | 137.5
641 | 543 | 528 | 342.2 | 407.7 | 337.8 | 175.1 | 155.1 | 148.4 | 153.8 | 206.6 | 137.7
642 | 544 | 528 | 342.6 | 408 | 338.1 | 175.6 | 155.6 | 148.9 | 154.2 | 206.9 | 138
643 | 545 | 528 | 342.9 | 408.3 | 338.5 | 176.2 | 156.1 | 149.3 | 154.7 | 207.1 | 138.3
644 | 546 | 528 | 343.3 | 408.6 | 338.8 | 176.8 | 156.6 | 149.8 | 155.1 | 207.3 | 138.5
645 | 547 | 528 | 343.6 | 408.9 | 339.2 | 177.4 | 157.1 | 150.2 | 155.6 | 207.5 | 138.8
646 | 548 | 528 | 344 | 409.2 | 339.6 | 178.1 | 157.6 | 150.7 | 156 | 207.7 | 139.1
647 | 549 | 528 | 344.3 | 409.5 | 339.9 | 178.8 | 158.1 | 151.2 | 156.5 | 207.9 | 139.4
648 | 550 | 528 | 344.6 | 409.8 | 340.2 | 179.6 | 158.6 | 151.6 | 157 | 208.1 | 139.6
649 | 551 | 528.1 | 345 | 410.1 | 340.6 | 180.4 | 159.1 | 152.1 | 157.4 | 208.3 | 139.9
650 | 552 | 528.1 | 345.3 | 410.4 | 341 | 181.1 | 159.6 | 152.5 | 157.9 | 208.4 | 140.2
651 | 553 | 528.1 | 345.7 | 410.7 | 341.4 | 181.9 | 160 | 153 | 158.4 | 208.6 | 140.5
652 | 554 | 528.1 | 346 | 411 | 341.7 | 182.6 | 160.5 | 153.4 | 158.9 | 208.8 | 140.7
653 | 555 | 528.1 | 346.3 | 411.3 | 342 | 183.2 | 161 | 153.9 | 159.5 | 208.9 | 141
654 | 556 | 528 | 346.7 | 411.6 | 342.3 | 183.7 | 161.5 | 154.3 | 159.9 | 209.1 | 141.3
655 | 557 | 528 | 347 | 411.9 | 342.7 | 184.2 | 162 | 154.8 | 160.4 | 209.2 | 141.6
656 | 558 | 528 | 347.3 | 412.2 | 343.1 | 184.7 | 162.5 | 155.2 | 160.9 | 209.3 | 141.8
657 | 559 | 528 | 347.7 | 412.5 | 343.4 | 185.1 | 163 | 155.7 | 161.5 | 209.4 | 142.1
658 | 560 | 528 | 348 | 412.8 | 343.7 | 185.4 | 163.5 | 156.1 | 162 | 209.6 | 142.4
659 | 561 | 528 | 348.3 | 413.1 | 344 | 185.8 | 164 | 156.6 | 162.5 | 209.7 | 142.7
660 | 562 | 528 | 348.7 | 413.4 | 344.4 | 186 | 164.4 | 157 | 163 | 209.8 | 142.9
661 | 563 | 528 | 349 | 413.7 | 344.7 | 186.4 | 164.9 | 157.4 | 163.5 | 209.9 | 143.2
662 | 564 | 528 | 349.3 | 414 | 345.1 | 186.7 | 165.4 | 157.9 | 164 | 209.9 | 143.5
663 | 565 | 528.1 | 349.7 | 414.3 | 345.4 | 187 | 165.9 | 158.3 | 164.4 | 210 | 143.8
664 | 566 | 528 | 350 | 414.5 | 345.7 | 187.3 | 166.4 | 158.8 | 164.9 | 210.1 | 144
665 | 567 | 528 | 350.3 | 414.8 | 346.1 | 187.7 | 166.8 | 159.2 | 165.4 | 210.1 | 144.3
666 | 568 | 528 | 350.7 | 415.1 | 346.4 | 188 | 167.3 | 159.6 | 165.9 | 210.2 | 144.6
667 | 569 | 528 | 351 | 415.4 | 346.7 | 188.3 | 167.8 | 160.1 | 166.4 | 210.2 | 144.8
668 | 570 | 528 | 351.3 | 415.7 | 347 | 188.7 | 168.2 | 160.5 | 166.9 | 210.2 | 145.1
669 | 571 | 528 | 351.6 | 416 | 347.4 | 189 | 168.7 | 161 | 167.4 | 210.3 | 145.4
670 | 572 | 528 | 352 | 416.3 | 347.8 | 189.4 | 169.2 | 161.4 | 167.9 | 210.3 | 145.6
671 | 573 | 528 | 352.3 | 416.6 | 348.1 | 189.8 | 169.6 | 161.8 | 168.4 | 210.3 | 145.9
672 | 574 | 528 | 352.6 | 416.8 | 348.4 | 190.2 | 170 | 162.2 | 168.9 | 210.3 | 146.2
673 | 575 | 528 | 352.9 | 417.1 | 348.7 | 190.7 | 170.5 | 162.7 | 169.4 | 210.3 | 146.4
674 | 576 | 528 | 353.2 | 417.4 | 349.1 | 191.1 | 170.9 | 163.1 | 169.9 | 210.3 | 146.7
675 | 577 | 528 | 353.6 | 417.6 | 349.4 | 191.6 | 171.4 | 163.5 | 170.4 | 210.3 | 147
676 | 578 | 528 | 353.9 | 417.9 | 349.8 | 192 | 171.8 | 164 | 170.9 | 210.3 | 147.2
677 | 579 | 528 | 354.2 | 418.2 | 350.1 | 192.5 | 172.2 | 164.4 | 171.3 | 210.4 | 147.5
678 | 580 | 528 | 354.5 | 418.5 | 350.4 | 193 | 172.7 | 164.9 | 171.8 | 210.4 | 147.8
679 | 581 | 528 | 354.8 | 418.8 | 350.7 | 193.4 | 173.1 | 165.3 | 172.2 | 210.4 | 148.1
680 | 582 | 528 | 355.1 | 419 | 351 | 193.8 | 173.6 | 165.7 | 172.7 | 210.4 | 148.3
681 | 583 | 528.1 | 355.4 | 419.3 | 351.3 | 194.2 | 174.1 | 166.2 | 173.1 | 210.5 | 148.6
682 | 584 | 528.1 | 355.8 | 419.6 | 351.6 | 194.6 | 174.6 | 166.6 | 173.6 | 210.5 | 148.9
683 | 585 | 528.1 | 356.1 | 419.8 | 352 | 194.9 | 175 | 167 | 174 | 210.5 | 149.2
684 | 586 | 528.1 | 356.4 | 420.1 | 352.3 | 195.3 | 175.5 | 167.4 | 174.4 | 210.6 | 149.4
685 | 587 | 528.1 | 356.7 | 420.4 | 352.6 | 195.6 | 176 | 167.8 | 174.8 | 210.6 | 149.7
686 | 588 | 528 | 357 | 420.7 | 352.9 | 196 | 176.5 | 168.3 | 175.3 | 210.6 | 150
687 | 589 | 528 | 357.3 | 420.9 | 353.2 | 196.3 | 177 | 168.7 | 175.7 | 210.7 | 150.3
688 | 590 | 528 | 357.6 | 421.2 | 353.5 | 196.6 | 177.5 | 169.1 | 176.2 | 210.7 | 150.5
689 | 591 | 528 | 357.9 | 421.5 | 353.8 | 196.9 | 177.9 | 169.5 | 176.7 | 210.7 | 150.8
690 | 592 | 528 | 358.2 | 421.7 | 354.2 | 197.2 | 178.4 | 169.9 | 177.1 | 210.8 | 151.1
691 | 593 | 527.9 | 358.5 | 422 | 354.5 | 197.5 | 178.9 | 170.3 | 177.5 | 210.8 | 151.4
692 | 594 | 527.9 | 358.8 | 422.3 | 354.7 | 197.8 | 179.4 | 170.7 | 178 | 210.9 | 151.7
693 | 595 | 527.9 | 359.1 | 422.5 | 355 | 198.2 | 179.8 | 171.1 | 178.4 | 210.9 | 151.9
694 | 596 | 527.9 | 359.4 | 422.8 | 355.3 | 198.5 | 180.3 | 171.5 | 178.8 | 211 | 152.2
695 | 597 | 527.8 | 359.7 | 423 | 355.7 | 198.8 | 180.8 | 171.9 | 179.3 | 211 | 152.5
696 | 598 | 527.7 | 360 | 423.3 | 356 | 199.1 | 181.2 | 172.4 | 179.7 | 211.1 | 152.8
697 | 599 | 527.7 | 360.3 | 423.6 | 356.3 | 199.4 | 181.7 | 172.8 | 180.1 | 211.1 | 153.1
698 | 600 | 527.7 | 360.6 | 423.9 | 356.6 | 199.7 | 182.1 | 173.2 | 180.5 | 211.2 | 153.3
699 | 601 | 527.7 | 360.9 | 424.1 | 356.9 | 200.1 | 182.6 | 173.6 | 180.9 | 211.3 | 153.6
700 | 602 | 527.6 | 361.2 | 424.3 | 357.2 | 200.4 | 183.1 | 174 | 181.3 | 211.4 | 153.9
701 | 603 | 527.6 | 361.5 | 424.6 | 357.5 | 200.8 | 183.5 | 174.4 | 181.7 | 211.4 | 154.2
702 | 604 | 527.5 | 361.8 | 424.9 | 357.8 | 201.1 | 184 | 174.8 | 182.1 | 211.5 | 154.4
703 | 605 | 527.5 | 362.1 | 425.1 | 358.1 | 201.4 | 184.4 | 175.2 | 182.5 | 211.7 | 154.7
704 | 606 | 527.5 | 362.4 | 425.4 | 358.4 | 201.8 | 184.9 | 175.6 | 182.9 | 211.8 | 155
705 | 607 | 527.4 | 362.7 | 425.6 | 358.7 | 202.1 | 185.3 | 176 | 183.4 | 211.9 | 155.3
706 | 608 | 527.4 | 363 | 425.9 | 359 | 202.4 | 185.7 | 176.4 | 183.8 | 212 | 155.6
707 | 609 | 527.3 | 363.3 | 426.1 | 359.3 | 202.7 | 186.2 | 176.9 | 184.2 | 212.2 | 155.9
708 | 610 | 527.3 | 363.6 | 426.4 | 359.7 | 202.9 | 186.6 | 177.3 | 184.6 | 212.3 | 156.1
709 | 611 | 527.3 | 363.9 | 426.6 | 360 | 203.2 | 187 | 177.7 | 185 | 212.4 | 156.4
710 | 612 | 527.3 | 364.2 | 426.9 | 360.3 | 203.6 | 187.5 | 178.1 | 185.3 | 212.5 | 156.7
711 | 613 | 527.3 | 364.4 | 427.1 | 360.7 | 203.9 | 187.9 | 178.5 | 185.7 | 212.6 | 157
712 | 614 | 527.2 | 364.7 | 427.4 | 360.9 | 204.3 | 188.4 | 178.9 | 186 | 212.7 | 157.2
713 | 615 | 527.2 | 365 | 427.6 | 361.2 | 204.6 | 188.8 | 179.3 | 186.4 | 212.9 | 157.5
714 | 616 | 527.2 | 365.3 | 427.9 | 361.5 | 205 | 189.2 | 179.7 | 186.8 | 213.1 | 157.8
715 | 617 | 527.2 | 365.6 | 428.1 | 361.8 | 205.3 | 189.6 | 180.1 | 187.2 | 213.2 | 158.1
716 | 618 | 527.3 | 365.9 | 428.3 | 362.1 | 205.6 | 190.1 | 180.5 | 187.6 | 213.4 | 158.3
717 | 619 | 527.3 | 366.2 | 428.6 | 362.5 | 205.9 | 190.5 | 180.9 | 187.9 | 213.5 | 158.6
718 | 620 | 527.3 | 366.5 | 428.8 | 362.8 | 206.2 | 190.9 | 181.3 | 188.3 | 213.6 | 158.9
719 | 621 | 527.3 | 366.8 | 429.1 | 363 | 206.6 | 191.3 | 181.7 | 188.7 | 213.7 | 159.2
720 | 622 | 527.3 | 367 | 429.3 | 363.3 | 206.9 | 191.7 | 182.1 | 189.1 | 213.9 | 159.5
721 | 623 | 527.3 | 367.3 | 429.6 | 363.7 | 207.2 | 192.1 | 182.5 | 189.5 | 214.1 | 159.7
722 | 624 | 527.3 | 367.6 | 429.8 | 364 | 207.6 | 192.6 | 182.9 | 189.9 | 214.4 | 160
723 | 625 | 527.3 | 367.9 | 430.1 | 364.3 | 208 | 192.9 | 183.3 | 190.3 | 214.7 | 160.3
724 | 626 | 527.4 | 368.2 | 430.3 | 364.5 | 208.4 | 193.3 | 183.7 | 190.7 | 215 | 160.6
725 | 627 | 527.4 | 368.5 | 430.6 | 364.9 | 208.7 | 193.7 | 184.1 | 191 | 215.3 | 160.9
726 | 628 | 527.4 | 368.7 | 430.8 | 365.2 | 209.1 | 194.1 | 184.5 | 191.4 | 215.6 | 161.1
727 | 629 | 527.4 | 369 | 431.1 | 365.5 | 209.5 | 194.5 | 184.9 | 191.7 | 215.8 | 161.4
728 | 630 | 527.4 | 369.3 | 431.3 | 365.8 | 209.9 | 194.9 | 185.3 | 192.1 | 216.2 | 161.7
729 | 631 | 527.4 | 369.6 | 431.6 | 366.1 | 210.2 | 195.3 | 185.7 | 192.5 | 216.7 | 161.9
730 | 632 | 527.5 | 369.8 | 431.8 | 366.4 | 210.5 | 195.7 | 186.1 | 192.9 | 217.1 | 162.2
731 | 633 | 527.5 | 370.1 | 432.1 | 366.7 | 210.8 | 196.1 | 186.5 | 193.2 | 217.5 | 162.5
732 | 634 | 527.5 | 370.4 | 432.3 | 367 | 211.1 | 196.4 | 186.9 | 193.6 | 217.7 | 162.8
733 | 635 | 527.5 | 370.7 | 432.6 | 367.3 | 211.5 | 196.8 | 187.2 | 194 | 218 | 163
734 | 636 | 527.5 | 371 | 432.8 | 367.5 | 211.8 | 197.2 | 187.7 | 194.3 | 218.3 | 163.3
735 | 637 | 527.5 | 371.2 | 433 | 367.8 | 212.2 | 197.6 | 188 | 194.7 | 218.6 | 163.6
736 | 638 | 527.4 | 371.5 | 433.3 | 368.1 | 212.5 | 198 | 188.5 | 195.1 | 218.7 | 163.8
737 | 639 | 527.4 | 371.8 | 433.5 | 368.4 | 212.9 | 198.4 | 188.8 | 195.5 | 218.8 | 164.1
738 | 640 | 527.4 | 372.1 | 433.8 | 368.6 | 213.2 | 198.8 | 189.2 | 195.9 | 219 | 164.4
739 | 641 | 527.4 | 372.3 | 434 | 368.9 | 213.6 | 199.2 | 189.6 | 196.2 | 219.1 | 164.7
740 | 642 | 527.4 | 372.6 | 434.2 | 369.2 | 213.9 | 199.6 | 190 | 196.6 | 219.3 | 164.9
741 | 643 | 527.4 | 372.9 | 434.4 | 369.5 | 214.2 | 200 | 190.4 | 197 | 219.5 | 165.2
742 | 644 | 527.4 | 373.1 | 434.7 | 369.8 | 214.6 | 200.4 | 190.8 | 197.4 | 219.8 | 165.5
743 | 645 | 527.4 | 373.4 | 434.9 | 370.1 | 214.9 | 200.8 | 191.2 | 197.7 | 220.1 | 165.8
744 | 646 | 527.3 | 373.7 | 435.1 | 370.3 | 215.3 | 201.2 | 191.6 | 198.1 | 220.4 | 166
745 | 647 | 527.3 | 373.9 | 435.4 | 370.6 | 215.6 | 201.6 | 192 | 198.5 | 220.7 | 166.3
746 | 648 | 527.3 | 374.2 | 435.6 | 370.9 | 215.9 | 201.9 | 192.3 | 198.8 | 221.1 | 166.6
747 | 649 | 527.3 | 374.5 | 435.8 | 371.2 | 216.2 | 202.3 | 192.7 | 199.2 | 221.4 | 166.8
748 | 650 | 527.2 | 374.8 | 436.1 | 371.5 | 216.5 | 202.7 | 193.1 | 199.6 | 221.7 | 167.1
749 | 651 | 527.2 | 375 | 436.3 | 371.8 | 216.9 | 203.1 | 193.5 | 200 | 222 | 167.4
750 | 652 | 527.2 | 375.3 | 436.5 | 372 | 217.2 | 203.5 | 193.9 | 200.3 | 222.4 | 167.6
751 | 653 | 527.2 | 375.5 | 436.7 | 372.3 | 217.6 | 203.9 | 194.3 | 200.6 | 222.7 | 167.9
752 | 654 | 527.2 | 375.8 | 436.9 | 372.6 | 218 | 204.2 | 194.7 | 200.9 | 223.1 | 168.2
753 | 655 | 527.2 | 376.1 | 437.2 | 372.8 | 218.4 | 204.6 | 195.1 | 201.2 | 223.4 | 168.5
754 | 656 | 527.2 | 376.3 | 437.4 | 373.1 | 218.7 | 205 | 195.4 | 201.5 | 223.6 | 168.7
755 | 657 | 527.2 | 376.6 | 437.6 | 373.4 | 219.1 | 205.4 | 195.8 | 201.9 | 223.9 | 169
756 | 658 | 527.2 | 376.9 | 437.8 | 373.6 | 219.4 | 205.8 | 196.2 | 202.2 | 224.2 | 169.3
757 | 659 | 527.2 | 377.1 | 438 | 373.9 | 219.8 | 206.1 | 196.6 | 202.6 | 224.6 | 169.5
758 | 660 | 527.2 | 377.4 | 438.3 | 374.2 | 220.1 | 206.5 | 197 | 203 | 224.9 | 169.8
759 | 661 | 527.3 | 377.6 | 438.5 | 374.4 | 220.5 | 206.9 | 197.4 | 203.3 | 225.2 | 170.1
760 | 662 | 527.3 | 377.9 | 438.7 | 374.7 | 220.8 | 207.3 | 197.7 | 203.7 | 225.5 | 170.3
761 | 663 | 527.3 | 378.2 | 438.9 | 375 | 221.2 | 207.7 | 198.1 | 204 | 225.9 | 170.6
762 | 664 | 527.3 | 378.4 | 439.2 | 375.3 | 221.5 | 208 | 198.5 | 204.4 | 226.3 | 170.9
763 | 665 | 527.3 | 378.7 | 439.4 | 375.5 | 221.9 | 208.4 | 198.9 | 204.8 | 226.6 | 171.1
764 | 666 | 527.3 | 378.9 | 439.6 | 375.8 | 222.2 | 208.8 | 199.2 | 205.2 | 226.9 | 171.4
765 | 667 | 527.4 | 379.2 | 439.8 | 376 | 222.6 | 209.2 | 199.6 | 205.6 | 227.2 | 171.6
766 | 668 | 527.4 | 379.4 | 440.1 | 376.3 | 222.9 | 209.5 | 200 | 206.1 | 227.5 | 171.9
767 | 669 | 527.5 | 379.7 | 440.3 | 376.6 | 223.2 | 209.9 | 200.3 | 206.5 | 227.9 | 172.2
768 | 670 | 527.5 | 379.9 | 440.5 | 376.8 | 223.5 | 210.3 | 200.7 | 207 | 228.3 | 172.4
769 | 671 | 527.5 | 380.2 | 440.7 | 377.1 | 223.8 | 210.6 | 201.1 | 207.5 | 228.7 | 172.7
770 | 672 | 527.6 | 380.5 | 440.9 | 377.3 | 224.1 | 211 | 201.4 | 207.8 | 229.1 | 173
771 | 673 | 527.6 | 380.7 | 441.1 | 377.6 | 224.5 | 211.4 | 201.8 | 208.2 | 229.6 | 173.2
772 | 674 | 527.7 | 381 | 441.3 | 377.8 | 224.8 | 211.7 | 202.2 | 208.5 | 230.1 | 173.5
773 | 675 | 527.7 | 381.2 | 441.5 | 378.1 | 225.2 | 212.1 | 202.5 | 208.8 | 230.5 | 173.8
774 | 676 | 527.8 | 381.5 | 441.7 | 378.4 | 225.6 | 212.5 | 202.9 | 209.1 | 230.9 | 174
775 | 677 | 527.8 | 381.7 | 442 | 378.6 | 226 | 212.9 | 203.3 | 209.5 | 231.3 | 174.3
776 | 678 | 527.8 | 381.9 | 442.2 | 378.9 | 226.3 | 213.2 | 203.6 | 209.8 | 231.8 | 174.5
777 | 679 | 527.8 | 382.2 | 442.4 | 379.1 | 226.6 | 213.6 | 204 | 210.1 | 232.2 | 174.8
778 | 680 | 527.8 | 382.5 | 442.6 | 379.4 | 227 | 214 | 204.4 | 210.4 | 232.6 | 175
779 | 681 | 527.8 | 382.7 | 442.7 | 379.7 | 227.4 | 214.4 | 204.8 | 210.8 | 232.9 | 175.3
780 | 682 | 527.9 | 382.9 | 443 | 379.9 | 227.7 | 214.7 | 205.2 | 211.1 | 233.4 | 175.5
781 | 683 | 527.9 | 383.2 | 443.2 | 380.2 | 228.1 | 215.1 | 205.5 | 211.3 | 233.7 | 175.8
782 | 684 | 527.9 | 383.4 | 443.4 | 380.5 | 228.5 | 215.5 | 205.9 | 211.6 | 234.1 | 176
783 | 685 | 527.9 | 383.7 | 443.6 | 380.7 | 228.8 | 215.8 | 206.3 | 211.9 | 234.4 | 176.3
784 | 686 | 527.9 | 383.9 | 443.8 | 380.9 | 229.2 | 216.2 | 206.7 | 212.1 | 234.7 | 176.6
785 | 687 | 528 | 384.2 | 444 | 381.2 | 229.5 | 216.6 | 207.1 | 212.4 | 235.1 | 176.8
786 | 688 | 527.9 | 384.4 | 444.1 | 381.5 | 229.9 | 217 | 207.4 | 212.7 | 235.4 | 177
787 | 689 | 527.9 | 384.6 | 444.5 | 381.7 | 230.2 | 217.3 | 207.8 | 213.1 | 235.8 | 177.3
788 | 690 | 527.9 | 384.8 | 444.7 | 381.9 | 230.6 | 217.7 | 208.2 | 213.5 | 236.1 | 177.5
789 | 691 | 527.9 | 385 | 444.9 | 382.1 | 231 | 218.1 | 208.5 | 213.9 | 236.4 | 177.7
790 | 692 | 527.9 | 385.3 | 445.1 | 382.4 | 231.3 | 218.4 | 208.9 | 214.2 | 236.8 | 178
791 | 693 | 527.9 | 385.5 | 445.3 | 382.6 | 231.7 | 218.8 | 209.3 | 214.5 | 237.2 | 178.2
792 | 694 | 527.9 | 385.7 | 445.5 | 382.9 | 232.1 | 219.2 | 209.6 | 214.8 | 237.5 | 178.5
793 | 695 | 527.9 | 386 | 445.7 | 383.1 | 232.4 | 219.5 | 210 | 215.1 | 237.9 | 178.7
794 | 696 | 527.9 | 386.2 | 445.9 | 383.4 | 232.8 | 219.9 | 210.4 | 215.4 | 238.2 | 178.9
795 | 697 | 527.9 | 386.4 | 446.1 | 383.6 | 233.1 | 220.2 | 210.7 | 215.7 | 238.6 | 179.1
796 | 698 | 527.9 | 386.7 | 446.3 | 383.8 | 233.5 | 220.6 | 211.1 | 216 | 238.9 | 179.4
797 | 699 | 527.9 | 386.9 | 446.5 | 384.1 | 233.8 | 221 | 211.5 | 216.3 | 239.2 | 179.6
798 | 700 | 527.9 | 387.2 | 446.7 | 384.3 | 234.2 | 221.3 | 211.8 | 216.6 | 239.5 | 179.8
799 | 701 | 527.9 | 387.4 | 446.9 | 384.6 | 234.5 | 221.7 | 212.2 | 216.9 | 239.9 | 180
800 | 702 | 527.9 | 387.6 | 447 | 384.8 | 234.8 | 222 | 212.6 | 217.2 | 240.2 | 180.3
801 | 703 | 527.8 | 387.9 | 447.2 | 385 | 235.2 | 222.4 | 213 | 217.5 | 240.5 | 180.5
802 | 704 | 527.7 | 388.1 | 447.4 | 385.3 | 235.5 | 222.7 | 213.3 | 217.8 | 240.9 | 180.7
803 | 705 | 527.7 | 388.3 | 447.5 | 385.5 | 235.8 | 223.1 | 213.7 | 218.2 | 241.2 | 180.9
804 | 706 | 527.7 | 388.6 | 447.7 | 385.7 | 236.2 | 223.4 | 214.1 | 218.5 | 241.5 | 181.1
805 | 707 | 527.7 | 388.8 | 447.9 | 386 | 236.5 | 223.8 | 214.4 | 218.9 | 241.9 | 181.3
806 | 708 | 527.7 | 389 | 448.1 | 386.2 | 236.8 | 224.1 | 214.8 | 219.2 | 242.2 | 181.5
807 | 709 | 527.7 | 389.3 | 448.3 | 386.4 | 237.1 | 224.5 | 215.1 | 219.6 | 242.6 | 181.7
808 | 710 | 527.7 | 389.5 | 448.4 | 386.7 | 237.4 | 224.8 | 215.5 | 219.8 | 242.9 | 181.8
809 | 711 | 527.7 | 389.7 | 448.6 | 386.9 | 237.8 | 225.2 | 215.8 | 220.1 | 243.2 | 182
810 | 712 | 527.6 | 389.9 | 448.8 | 387.2 | 238.1 | 225.5 | 216.1 | 220.4 | 243.6 | 182.2
811 | 713 | 527.6 | 390.2 | 448.9 | 387.4 | 238.4 | 225.9 | 216.5 | 220.8 | 244 | 182.3
812 | 714 | 527.6 | 390.4 | 449.1 | 387.7 | 238.8 | 226.2 | 216.8 | 221.1 | 244.3 | 182.5
813 | 715 | 527.6 | 390.6 | 449.3 | 387.9 | 239.1 | 226.6 | 217.2 | 221.4 | 244.7 | 182.7
814 | 716 | 527.7 | 390.8 | 449.5 | 388.1 | 239.5 | 226.9 | 217.5 | 221.7 | 245.1 | 182.8
815 | 717 | 527.6 | 391.1 | 449.6 | 388.3 | 239.8 | 227.3 | 217.9 | 222 | 245.5 | 183
816 | 718 | 527.6 | 391.3 | 449.8 | 388.6 | 240.2 | 227.6 | 218.2 | 222.3 | 245.8 | 183.2
817 | 719 | 527.6 | 391.5 | 450 | 388.8 | 240.6 | 228 | 218.6 | 222.7 | 246.2 | 183.3
818 | 720 | 527.6 | 391.7 | 450.2 | 389.1 | 241 | 228.3 | 218.9 | 223 | 246.6 | 183.4
819 | 721 | 527.6 | 392 | 450.3 | 389.3 | 241.3 | 228.7 | 219.3 | 223.3 | 247 | 183.6
820 | 722 | 527.6 | 392.2 | 450.5 | 389.5 | 241.7 | 229 | 219.6 | 223.7 | 247.3 | 183.7
821 | 723 | 527.6 | 392.4 | 450.6 | 389.7 | 242.1 | 229.4 | 220 | 224 | 247.7 | 183.9
822 | 724 | 527.6 | 392.6 | 450.8 | 389.9 | 242.5 | 229.7 | 220.3 | 224.4 | 248.1 | 184
823 | 725 | 527.6 | 392.8 | 451 | 390.1 | 242.9 | 230.1 | 220.7 | 224.8 | 248.4 | 184.2
824 | 726 | 527.6 | 393.1 | 451.1 | 390.4 | 243.3 | 230.4 | 221 | 225.1 | 248.7 | 184.3
825 | 727 | 527.5 | 393.3 | 451.3 | 390.7 | 243.7 | 230.8 | 221.4 | 225.4 | 249 | 184.4
826 | 728 | 527.5 | 393.5 | 451.5 | 390.9 | 244.1 | 231.1 | 221.7 | 225.8 | 249.3 | 184.6
827 | 729 | 527.4 | 393.7 | 451.6 | 391.1 | 244.5 | 231.5 | 222.1 | 226.1 | 249.6 | 184.8
828 | 730 | 527.4 | 393.9 | 451.8 | 391.3 | 244.9 | 231.8 | 222.4 | 226.5 | 249.9 | 184.9
829 | 731 | 527.3 | 394.1 | 451.9 | 391.5 | 245.4 | 232.1 | 222.8 | 226.9 | 250.3 | 185
830 | 732 | 527.3 | 394.4 | 452.1 | 391.7 | 245.9 | 232.5 | 223.1 | 227.2 | 250.5 | 185.2
831 | 733 | 527.3 | 394.6 | 452.2 | 391.9 | 246.4 | 232.8 | 223.5 | 227.5 | 250.8 | 185.3
832 | 734 | 527.3 | 394.8 | 452.4 | 392.2 | 246.8 | 233.2 | 223.8 | 227.8 | 251.1 | 185.5
833 | 735 | 527.3 | 395 | 452.6 | 392.4 | 247.3 | 233.5 | 224.2 | 228.1 | 251.4 | 185.6
834 | 736 | 527.2 | 395.2 | 452.7 | 392.6 | 247.8 | 233.9 | 224.5 | 228.4 | 251.8 | 185.8
835 | 737 | 527.2 | 395.4 | 452.9 | 392.8 | 248.3 | 234.2 | 224.8 | 228.7 | 252.1 | 185.9
836 | 738 | 527.2 | 395.6 | 453 | 393 | 248.9 | 234.6 | 225.2 | 229 | 252.5 | 186.1
837 | 739 | 527.2 | 395.8 | 453.2 | 393.2 | 249.4 | 234.9 | 225.5 | 229.3 | 252.8 | 186.2
838 | 740 | 527.2 | 396 | 453.3 | 393.4 | 250 | 235.3 | 225.8 | 229.6 | 253.1 | 186.3
839 | 741 | 527.2 | 396.2 | 453.5 | 393.7 | 250.8 | 235.6 | 226.2 | 229.8 | 253.4 | 186.5
840 | 742 | 527.2 | 396.4 | 453.6 | 393.9 | 251.8 | 236 | 226.5 | 230.1 | 253.8 | 186.6
841 | 743 | 527.2 | 396.7 | 453.8 | 394.1 | 252.8 | 236.3 | 226.8 | 230.4 | 254.1 | 186.8
842 | 744 | 527.2 | 396.9 | 453.9 | 394.3 | 253.7 | 236.6 | 227.2 | 230.7 | 254.4 | 186.9
843 | 745 | 527.2 | 397.1 | 454.1 | 394.5 | 254.4 | 237 | 227.5 | 231 | 254.7 | 187.1
844 | 746 | 527.2 | 397.3 | 454.2 | 394.7 | 255 | 237.3 | 227.9 | 231.4 | 254.9 | 187.2
845 | 747 | 527.2 | 397.5 | 454.4 | 394.9 | 255.5 | 237.6 | 228.2 | 231.6 | 255.2 | 187.3
846 | 748 | 527.2 | 397.7 | 454.5 | 395.2 | 256.1 | 238 | 228.5 | 231.9 | 255.5 | 187.5
847 | 749 | 527.2 | 397.9 | 454.7 | 395.4 | 256.6 | 238.4 | 228.9 | 232.3 | 255.8 | 187.7
848 | 750 | 527.2 | 398.1 | 454.8 | 395.6 | 257.1 | 238.7 | 229.2 | 232.6 | 256.1 | 187.8
849 | 751 | 527.2 | 398.3 | 455 | 395.8 | 257.6 | 239.1 | 229.5 | 232.9 | 256.4 | 187.9
850 | 752 | 527.2 | 398.5 | 455.1 | 396 | 258.1 | 239.5 | 229.9 | 233.1 | 256.6 | 188.1
851 | 753 | 527.1 | 398.7 | 455.3 | 396.2 | 258.5 | 239.8 | 230.2 | 233.5 | 256.9 | 188.3
852 | 754 | 527.1 | 398.9 | 455.4 | 396.4 | 259 | 240.2 | 230.5 | 233.8 | 257.2 | 188.4
853 | 755 | 527 | 399.1 | 455.5 | 396.6 | 259.4 | 240.5 | 230.9 | 234.1 | 257.4 | 188.5
854 | 756 | 527 | 399.3 | 455.7 | 396.8 | 259.8 | 240.9 | 231.2 | 234.6 | 257.7 | 188.7
855 | 757 | 527 | 399.5 | 455.8 | 397 | 260.1 | 241.2 | 231.5 | 234.9 | 257.9 | 188.8
856 | 758 | 527 | 399.7 | 456 | 397.2 | 260.4 | 241.5 | 231.9 | 235.3 | 258.2 | 188.9
857 | 759 | 527.1 | 399.9 | 456.1 | 397.4 | 260.8 | 241.9 | 232.2 | 235.7 | 258.4 | 189.1
858 | 760 | 527.2 | 400.1 | 456.3 | 397.6 | 261.1 | 242.2 | 232.5 | 236.1 | 258.7 | 189.2
859 | 761 | 527.2 | 400.3 | 456.5 | 397.8 | 261.4 | 242.6 | 232.8 | 236.5 | 259 | 189.4
860 | 762 | 527.2 | 400.5 | 456.6 | 398 | 261.6 | 242.9 | 233.2 | 236.8 | 259.2 | 189.5
861 | 763 | 527.3 | 400.7 | 456.7 | 398.2 | 261.9 | 243.2 | 233.5 | 237.1 | 259.5 | 189.7
862 | 764 | 527.3 | 400.9 | 456.9 | 398.4 | 262.2 | 243.5 | 233.8 | 237.4 | 259.8 | 189.8
863 | 765 | 527.4 | 401.1 | 457 | 398.7 | 262.5 | 243.9 | 234.1 | 237.7 | 260 | 189.9
864 | 766 | 527.4 | 401.3 | 457.2 | 398.8 | 262.7 | 244.2 | 234.4 | 238 | 260.3 | 190.1
865 | 767 | 527.4 | 401.5 | 457.3 | 399 | 263 | 244.6 | 234.7 | 238.3 | 260.6 | 190.2
866 | 768 | 527.4 | 401.7 | 457.5 | 399.2 | 263.3 | 244.9 | 235 | 238.7 | 260.8 | 190.3
867 | 769 | 527.5 | 401.8 | 457.6 | 399.4 | 263.5 | 245.2 | 235.3 | 239.1 | 261 | 190.5
868 | 770 | 527.5 | 402 | 457.7 | 399.6 | 263.8 | 245.6 | 235.6 | 239.5 | 261.3 | 190.6
869 | 771 | 527.5 | 402.2 | 457.8 | 399.8 | 264 | 246 | 235.9 | 239.8 | 261.5 | 190.7
870 | 772 | 527.5 | 402.4 | 458 | 400 | 264.3 | 246.3 | 236.3 | 240.1 | 261.8 | 190.8
871 | 773 | 527.5 | 402.6 | 458.1 | 400.2 | 264.6 | 246.7 | 236.6 | 240.6 | 262.1 | 190.9
872 | 774 | 527.6 | 402.8 | 458.3 | 400.4 | 264.9 | 247 | 236.9 | 241.1 | 262.4 | 191.1
873 | 775 | 527.6 | 403 | 458.4 | 400.6 | 265.1 | 247.4 | 237.2 | 241.4 | 262.7 | 191.2
874 | 776 | 527.6 | 403.2 | 458.6 | 400.8 | 265.4 | 247.7 | 237.5 | 241.8 | 263 | 191.3
875 | 777 | 527.5 | 403.4 | 458.7 | 401 | 265.7 | 248 | 237.8 | 242.2 | 263.3 | 191.4
876 | 778 | 527.5 | 403.5 | 458.9 | 401.2 | 266 | 248.3 | 238.1 | 242.6 | 263.6 | 191.6
877 | 779 | 527.5 | 403.7 | 459 | 401.4 | 266.3 | 248.6 | 238.4 | 242.9 | 263.8 | 191.7
878 | 780 | 527.5 | 403.9 | 459.1 | 401.6 | 266.5 | 248.9 | 238.7 | 243.2 | 264.1 | 191.8
879 | 781 | 527.4 | 404.1 | 459.2 | 401.8 | 266.9 | 249.3 | 239 | 243.4 | 264.4 | 191.9
880 | 782 | 527.4 | 404.3 | 459.4 | 402 | 267.1 | 249.6 | 239.4 | 243.7 | 264.6 | 192
881 | 783 | 527.3 | 404.5 | 459.5 | 402.2 | 267.4 | 249.9 | 239.7 | 243.9 | 264.9 | 192.2
882 | 784 | 527.3 | 404.6 | 459.6 | 402.4 | 267.7 | 250.2 | 240 | 244.3 | 265.1 | 192.3
883 | 785 | 527.2 | 404.8 | 459.8 | 402.6 | 267.9 | 250.5 | 240.4 | 244.6 | 265.4 | 192.4
884 | 786 | 527.2 | 405 | 459.9 | 402.8 | 268.2 | 250.7 | 240.7 | 244.9 | 265.7 | 192.5
885 | 787 | 527.2 | 405.2 | 460 | 403 | 268.4 | 250.9 | 241 | 245.3 | 266 | 192.6
886 | 788 | 527.2 | 405.3 | 460.1 | 403.2 | 268.5 | 251.2 | 241.4 | 245.6 | 266.4 | 192.8
887 | 789 | 527.1 | 405.5 | 460.2 | 403.4 | 268.7 | 251.4 | 241.8 | 245.9 | 266.7 | 192.9
888 | 790 | 527.1 | 405.7 | 460.4 | 403.6 | 268.8 | 251.7 | 242.1 | 246.1 | 267.1 | 193
889 | 791 | 527 | 405.9 | 460.5 | 403.7 | 269 | 251.9 | 242.5 | 246.4 | 267.4 | 193.1
890 | 792 | 527 | 406 | 460.6 | 403.9 | 269.2 | 252.1 | 242.8 | 246.7 | 267.7 | 193.2
891 | 793 | 527 | 406.2 | 460.8 | 404.1 | 269.4 | 252.3 | 243.1 | 247 | 268.1 | 193.3
892 | 794 | 527 | 406.4 | 460.9 | 404.3 | 269.7 | 252.5 | 243.5 | 247.3 | 268.4 | 193.3
893 | 795 | 526.9 | 406.5 | 461 | 404.5 | 270 | 252.8 | 243.8 | 247.6 | 268.7 | 193.4
894 | 796 | 526.8 | 406.7 | 461.1 | 404.7 | 270.2 | 253 | 244.1 | 247.9 | 269 | 193.5
895 | 797 | 526.8 | 406.9 | 461.3 | 404.9 | 270.5 | 253.2 | 244.4 | 248.2 | 269.2 | 193.5
896 | 798 | 526.8 | 407 | 461.4 | 405 | 270.8 | 253.5 | 244.8 | 248.4 | 269.6 | 193.6
897 | 799 | 526.8 | 407.2 | 461.5 | 405.2 | 271.1 | 253.7 | 245.1 | 248.6 | 269.9 | 193.7
898 | 800 | 526.7 | 407.4 | 461.7 | 405.4 | 271.4 | 253.9 | 245.4 | 248.9 | 270.2 | 193.8
899 | 801 | 526.7 | 407.5 | 461.8 | 405.6 | 271.7 | 254.2 | 245.7 | 249.2 | 270.5 | 193.9
900 | 802 | 526.7 | 407.7 | 461.9 | 405.8 | 272 | 254.4 | 246 | 249.5 | 270.7 | 194
901 | 803 | 526.7 | 407.9 | 462 | 405.9 | 272.3 | 254.7 | 246.3 | 249.7 | 271 | 194.1
902 | 804 | 526.8 | 408 | 462.1 | 406.1 | 272.5 | 254.9 | 246.6 | 250 | 271.2 | 194.3
903 | 805 | 526.8 | 408.2 | 462.3 | 406.3 | 272.7 | 255.1 | 246.8 | 250.3 | 271.4 | 194.4
904 | 806 | 526.7 | 408.4 | 462.4 | 406.5 | 272.9 | 255.4 | 247.1 | 250.6 | 271.7 | 194.6
905 | 807 | 526.7 | 408.5 | 462.5 | 406.6 | 273.1 | 255.6 | 247.4 | 250.8 | 271.9 | 194.7
906 | 808 | 526.7 | 408.7 | 462.6 | 406.8 | 273.4 | 255.8 | 247.7 | 251.1 | 272.2 | 194.9
907 | 809 | 526.7 | 408.8 | 462.7 | 407 | 273.7 | 256 | 248 | 251.5 | 272.5 | 195.1
908 | 810 | 526.7 | 409 | 462.8 | 407.1 | 273.9 | 256.2 | 248.2 | 251.8 | 272.8 | 195.2
909 | 811 | 526.6 | 409.2 | 463 | 407.3 | 274.2 | 256.4 | 248.5 | 252 | 273.1 | 195.4
910 | 812 | 526.6 | 409.3 | 463.1 | 407.5 | 274.5 | 256.6 | 248.7 | 252.3 | 273.4 | 195.7
911 | 813 | 526.7 | 409.5 | 463.2 | 407.7 | 274.7 | 256.8 | 249 | 252.7 | 273.7 | 195.9
912 | 814 | 526.7 | 409.7 | 463.4 | 407.8 | 275 | 257 | 249.3 | 252.9 | 274 | 196.1
913 | 815 | 526.7 | 409.8 | 463.5 | 408 | 275.3 | 257.3 | 249.6 | 253.2 | 274.3 | 196.2
914 | 816 | 526.7 | 410 | 463.6 | 408.2 | 275.6 | 257.5 | 249.9 | 253.5 | 274.6 | 196.5
915 | 817 | 526.7 | 410.1 | 463.7 | 408.4 | 275.9 | 257.7 | 250.2 | 253.8 | 274.9 | 196.7
916 | 818 | 526.7 | 410.3 | 463.8 | 408.5 | 276.2 | 257.8 | 250.5 | 254 | 275.3 | 196.9
917 | 819 | 526.7 | 410.4 | 463.9 | 408.7 | 276.6 | 258 | 250.7 | 254.3 | 275.6 | 197.1
918 | 820 | 526.8 | 410.6 | 464 | 408.9 | 276.9 | 258.2 | 251 | 254.6 | 275.8 | 197.3
919 | 821 | 526.8 | 410.8 | 464.2 | 409.1 | 277.2 | 258.4 | 251.3 | 254.9 | 276.1 | 197.4
920 | 822 | 526.8 | 410.9 | 464.3 | 409.2 | 277.5 | 258.5 | 251.5 | 255.2 | 276.4 | 197.5
921 | 823 | 526.8 | 411.1 | 464.4 | 409.4 | 277.8 | 258.8 | 251.8 | 255.5 | 276.7 | 197.6
922 | 824 | 526.9 | 411.2 | 464.5 | 409.6 | 278 | 258.9 | 252.1 | 255.7 | 277 | 197.7
923 | 825 | 526.9 | 411.4 | 464.6 | 409.7 | 278.3 | 259.1 | 252.4 | 256 | 277.3 | 197.9
924 | 826 | 526.8 | 411.5 | 464.7 | 409.9 | 278.6 | 259.4 | 252.6 | 256.3 | 277.5 | 198
925 | 827 | 526.9 | 411.7 | 464.8 | 410.1 | 278.9 | 259.6 | 252.9 | 256.6 | 277.8 | 198.2
926 | 828 | 526.9 | 411.9 | 465 | 410.2 | 279.2 | 259.7 | 253.2 | 256.9 | 278 | 198.4
927 | 829 | 526.9 | 412 | 465.1 | 410.4 | 279.5 | 259.9 | 253.5 | 257.1 | 278.3 | 198.6
928 | 830 | 526.9 | 412.2 | 465.2 | 410.6 | 279.8 | 260.1 | 253.8 | 257.4 | 278.5 | 198.8
929 | 831 | 526.9 | 412.3 | 465.3 | 410.7 | 280.1 | 260.3 | 254.1 | 257.7 | 278.7 | 199
930 | 832 | 526.8 | 412.5 | 465.4 | 410.9 | 280.4 | 260.5 | 254.4 | 258 | 278.9 | 199.2
931 | 833 | 526.8 | 412.6 | 465.5 | 411 | 280.7 | 260.7 | 254.7 | 258.2 | 279 | 199.4
932 | 834 | 526.8 | 412.8 | 465.6 | 411.2 | 281 | 260.9 | 254.9 | 258.5 | 279.1 | 199.6
933 | 835 | 526.8 | 412.9 | 465.7 | 411.4 | 281.3 | 261.1 | 255.3 | 258.8 | 279.3 | 199.8
934 | 836 | 526.8 | 413.1 | 465.8 | 411.6 | 281.5 | 261.3 | 255.5 | 259 | 279.4 | 200.1
935 | 837 | 526.8 | 413.3 | 465.9 | 411.7 | 281.8 | 261.6 | 255.8 | 259.2 | 279.6 | 200.3
936 | 838 | 526.8 | 413.4 | 466 | 411.9 | 282.1 | 261.8 | 256.1 | 259.4 | 279.8 | 200.6
937 | 839 | 526.8 | 413.6 | 466.1 | 412 | 282.4 | 262 | 256.4 | 259.7 | 280 | 200.9
938 | 840 | 526.8 | 413.7 | 466.2 | 412.2 | 282.7 | 262.2 | 256.7 | 260 | 280.1 | 201.3
939 | 841 | 526.8 | 413.9 | 466.3 | 412.3 | 282.9 | 262.4 | 257 | 260.2 | 280.3 | 201.6
940 | 842 | 526.8 | 414 | 466.5 | 412.5 | 283 | 262.7 | 257.3 | 260.5 | 280.5 | 201.9
941 | 843 | 526.9 | 414.2 | 466.5 | 412.7 | 283.2 | 262.9 | 257.6 | 260.7 | 280.7 | 202.3
942 | 844 | 526.9 | 414.3 | 466.7 | 412.8 | 283.5 | 263.1 | 257.9 | 261 | 280.9 | 202.6
943 | 845 | 526.9 | 414.5 | 466.8 | 413 | 283.6 | 263.4 | 258.1 | 261.3 | 281.1 | 203
944 | 846 | 526.9 | 414.6 | 466.9 | 413.1 | 283.7 | 263.5 | 258.4 | 261.5 | 281.4 | 203.4
945 | 847 | 526.9 | 414.8 | 467 | 413.3 | 283.8 | 263.7 | 258.7 | 261.8 | 281.6 | 203.8
946 | 848 | 526.8 | 414.9 | 467.1 | 413.4 | 284 | 263.8 | 259 | 262.1 | 281.8 | 204.1
947 | 849 | 526.8 | 415.1 | 467.2 | 413.6 | 284.4 | 263.9 | 259.3 | 262.4 | 282 | 204.5
948 | 850 | 526.9 | 415.2 | 467.3 | 413.8 | 284.7 | 264 | 259.6 | 262.6 | 282.3 | 204.9
949 | 851 | 526.9 | 415.4 | 467.4 | 413.9 | 284.8 | 264.3 | 259.9 | 262.8 | 282.5 | 205.3
950 | 852 | 526.9 | 415.5 | 467.5 | 414.1 | 284.8 | 264.5 | 260.2 | 263.1 | 282.7 | 205.6
951 | 853 | 526.9 | 415.7 | 467.6 | 414.3 | 285.2 | 264.7 | 260.5 | 263.4 | 282.9 | 205.9
952 | 854 | 527 | 415.8 | 467.7 | 414.4 | 285.5 | 264.9 | 260.8 | 263.7 | 283.2 | 206.2
953 | 855 | 527 | 416 | 467.8 | 414.5 | 285.8 | 265.2 | 261 | 264.1 | 283.4 | 206.5
954 | 856 | 527 | 416.2 | 467.9 | 414.7 | 286.1 | 265.3 | 261.3 | 264.3 | 283.6 | 206.8
955 | 857 | 527 | 416.3 | 468 | 414.9 | 286.5 | 265.5 | 261.6 | 264.6 | 283.8 | 207.1
956 | 858 | 527 | 416.5 | 468.1 | 415 | 286.8 | 265.8 | 261.9 | 264.9 | 284 | 207.4
957 | 859 | 527.1 | 416.6 | 468.2 | 415.2 | 287.1 | 266 | 262.2 | 265.2 | 284.2 | 207.7
958 | 860 | 527.1 | 416.8 | 468.3 | 415.3 | 287.4 | 266.2 | 262.5 | 265.5 | 284.4 | 207.9
959 | 861 | 527.2 | 416.9 | 468.4 | 415.5 | 287.8 | 266.5 | 262.7 | 265.7 | 284.6 | 208.2
960 | 862 | 527.2 | 417.1 | 468.5 | 415.6 | 287.8 | 266.7 | 263 | 266 | 284.9 | 208.5
961 | 863 | 527.2 | 417.2 | 468.6 | 415.8 | 287.9 | 267 | 263.3 | 266.2 | 285.1 | 208.6
962 | 864 | 527.2 | 417.4 | 468.8 | 415.9 | 288.3 | 267.3 | 263.6 | 266.4 | 285.3 | 208.8
963 | 865 | 527.2 | 417.5 | 468.8 | 416.1 | 288.7 | 267.5 | 263.9 | 266.7 | 285.5 | 209
964 | 866 | 527.3 | 417.7 | 468.9 | 416.2 | 288.8 | 267.8 | 264.2 | 266.9 | 285.7 | 209.2
965 | 867 | 527.3 | 417.8 | 469 | 416.4 | 289.3 | 268.2 | 264.5 | 267.2 | 285.9 | 209.5
966 | 868 | 527.3 | 418 | 469.1 | 416.5 | 289.8 | 268.5 | 264.7 | 267.5 | 286.1 | 209.7
967 | 869 | 527.2 | 418.1 | 469.2 | 416.7 | 290.2 | 268.8 | 265 | 267.7 | 286.4 | 210
968 | 870 | 527.2 | 418.3 | 469.3 | 416.8 | 290.4 | 269.1 | 265.3 | 268 | 286.6 | 210.2
969 | 871 | 527.2 | 418.4 | 469.4 | 417 | 290.6 | 269.4 | 265.6 | 268.2 | 286.8 | 210.5
970 | 872 | 527.2 | 418.6 | 469.5 | 417.1 | 291.1 | 269.7 | 265.9 | 268.5 | 287 | 210.7
971 | 873 | 527.2 | 418.7 | 469.6 | 417.3 | 291.4 | 270.1 | 266.2 | 268.8 | 287.3 | 210.9
972 | 874 | 527.2 | 418.8 | 469.7 | 417.4 | 291.7 | 270.4 | 266.5 | 269.1 | 287.5 | 211
973 | 875 | 527.1 | 419 | 469.8 | 417.6 | 292 | 270.7 | 266.8 | 269.3 | 287.7 | 211.2
974 | 876 | 527.1 | 419.2 | 469.8 | 417.7 | 292.5 | 271 | 267 | 269.6 | 287.9 | 211.4
975 | 877 | 527.1 | 419.3 | 469.9 | 417.9 | 292.8 | 271.3 | 267.3 | 270 | 288.2 | 211.5
976 | 878 | 527.1 | 419.4 | 470 | 418 | 293.2 | 271.6 | 267.6 | 270.4 | 288.4 | 211.7
977 | 879 | 527 | 419.6 | 470.1 | 418.2 | 293.5 | 271.9 | 267.9 | 270.6 | 288.6 | 211.9
978 | 880 | 527 | 419.7 | 470.2 | 418.3 | 293.9 | 272.2 | 268.2 | 270.9 | 288.9 | 212
979 | 881 | 526.9 | 419.9 | 470.3 | 418.5 | 294.1 | 272.6 | 268.5 | 271.1 | 289 | 212.1
980 | 882 | 526.9 | 420 | 470.4 | 418.6 | 294.5 | 272.9 | 268.8 | 271.4 | 289.3 | 212.3
981 | 883 | 526.9 | 420.2 | 470.5 | 418.7 | 294.9 | 273.2 | 269.1 | 271.7 | 289.5 | 212.5
982 | 884 | 526.8 | 420.3 | 470.5 | 418.9 | 295.3 | 273.5 | 269.4 | 272 | 289.8 | 212.6
983 | 885 | 526.8 | 420.5 | 470.6 | 419 | 295.7 | 273.7 | 269.7 | 272.3 | 290 | 212.8
984 | 886 | 526.8 | 420.6 | 470.7 | 419.2 | 296 | 274 | 270 | 272.6 | 290.2 | 213
985 | 887 | 526.9 | 420.7 | 470.8 | 419.3 | 296.5 | 274.3 | 270.3 | 272.9 | 290.4 | 213.2
986 | 888 | 526.9 | 420.9 | 470.9 | 419.5 | 296.9 | 274.7 | 270.6 | 273.1 | 290.7 | 213.4
987 | 889 | 526.8 | 421 | 471 | 419.6 | 297.3 | 275 | 270.9 | 273.4 | 290.9 | 213.6
988 | 890 | 526.9 | 421.2 | 471 | 419.7 | 297.7 | 275.3 | 271.1 | 273.6 | 291.1 | 213.7
989 | 891 | 526.9 | 421.3 | 471.2 | 419.9 | 298.1 | 275.6 | 271.4 | 273.9 | 291.3 | 213.9
990 | 892 | 526.9 | 421.4 | 471.3 | 420 | 298.5 | 275.8 | 271.7 | 274.1 | 291.5 | 214.1
991 | 893 | 526.9 | 421.6 | 471.4 | 420.2 | 298.9 | 276.2 | 272 | 274.3 | 291.7 | 214.4
992 | 894 | 526.9 | 421.7 | 471.4 | 420.3 | 299.3 | 276.4 | 272.3 | 274.5 | 291.9 | 214.5
993 | 895 | 526.9 | 421.8 | 471.5 | 420.4 | 299.7 | 276.8 | 272.5 | 274.8 | 292.2 | 214.7
994 | 896 | 526.9 | 422 | 471.6 | 420.6 | 300.1 | 277.1 | 272.8 | 275 | 292.4 | 214.9
995 | 897 | 526.9 | 422.1 | 471.8 | 420.7 | 300.5 | 277.3 | 273 | 275.3 | 292.6 | 215.1
996 | 898 | 526.9 | 422.2 | 471.9 | 420.8 | 301 | 277.5 | 273.3 | 275.5 | 292.8 | 215.3
997 | 899 | 526.9 | 422.3 | 472 | 420.9 | 301.5 | 277.9 | 273.5 | 275.8 | 293 | 215.5
998 | 900 | 526.9 | 422.5 | 472.1 | 421.1 | 302 | 278.3 | 273.8 | 276.1 | 293.2 | 215.7
999 | 901 | 526.9 | 422.6 | 472.2 | 421.2 | 302.5 | 278.5 | 274 | 276.3 | 293.5 | 215.9
1000 | 902 | 526.8 | 422.7 | 472.2 | 421.4 | 303.1 | 278.7 | 274.3 | 276.6 | 293.7 | 216.1
1001 | 903 | 526.8 | 422.9 | 472.3 | 421.5 | 303.7 | 279 | 274.5 | 276.8 | 293.9 | 216.3
1002 | 904 | 526.7 | 423 | 472.3 | 421.6 | 304.1 | 279.3 | 274.8 | 277.1 | 294.1 | 216.5
1003 | 905 | 526.7 | 423.2 | 472.4 | 421.8 | 304.6 | 279.8 | 274.9 | 277.3 | 294.3 | 216.7
1004 | 906 | 526.7 | 423.3 | 472.5 | 421.9 | 305 | 280.2 | 274.6 | 277.6 | 294.5 | 216.9
1005 | 907 | 526.6 | 423.4 | 472.6 | 422.1 | 305.4 | 280.6 | 274.7 | 277.8 | 294.7 | 217.2
1006 | 908 | 526.6 | 423.6 | 472.7 | 422.2 | 305.9 | 280.8 | 274.8 | 278.1 | 294.9 | 217.4
1007 | 909 | 526.6 | 423.7 | 472.7 | 422.3 | 306.2 | 281 | 274.9 | 278.4 | 295.1 | 217.7
1008 | 910 | 526.6 | 423.8 | 472.8 | 422.5 | 306.6 | 281.4 | 275 | 278.7 | 295.3 | 217.9
1009 | 911 | 526.6 | 424 | 472.9 | 422.6 | 307 | 281.8 | 275.3 | 278.9 | 295.5 | 218.2
1010 | 912 | 526.6 | 424.1 | 473 | 422.7 | 307.4 | 281.9 | 275.6 | 279.1 | 295.7 | 218.4
1011 | 913 | 526.6 | 424.2 | 473.1 | 422.9 | 307.7 | 282.2 | 275.9 | 279.3 | 295.9 | 218.7
1012 | 914 | 526.6 | 424.3 | 473.1 | 423 | 308.1 | 282.6 | 276.2 | 279.5 | 296.1 | 219
1013 | 915 | 526.6 | 424.5 | 473.2 | 423.1 | 308.5 | 282.8 | 276.4 | 279.7 | 296.3 | 219.2
1014 | 916 | 526.5 | 424.6 | 473.3 | 423.3 | 308.9 | 283.1 | 276.7 | 280 | 296.5 | 219.5
1015 | 917 | 526.5 | 424.7 | 473.3 | 423.4 | 309.3 | 283.4 | 276.9 | 280.3 | 296.7 | 219.7
1016 | 918 | 526.5 | 424.9 | 473.5 | 423.5 | 309.6 | 283.8 | 277.2 | 280.5 | 296.9 | 220
1017 | 919 | 526.5 | 425 | 473.5 | 423.6 | 310 | 284 | 277.4 | 280.8 | 297.1 | 220.1
1018 | 920 | 526.4 | 425.1 | 473.6 | 423.8 | 310.3 | 284.3 | 277.7 | 281 | 297.3 | 220.3
1019 | 921 | 526.4 | 425.2 | 473.7 | 423.9 | 310.7 | 284.5 | 277.9 | 281.2 | 297.5 | 220.6
1020 | 922 | 526.4 | 425.3 | 473.8 | 424 | 311.1 | 284.7 | 278.2 | 281.5 | 297.7 | 220.8
1021 | 923 | 526.4 | 425.4 | 473.9 | 424.1 | 311.5 | 285 | 278.5 | 281.7 | 297.9 | 221.1
1022 | 924 | 526.3 | 425.6 | 474 | 424.3 | 311.9 | 285.5 | 278.7 | 281.9 | 298.1 | 221.3
1023 | 925 | 526.3 | 425.7 | 474.1 | 424.4 | 312.2 | 285.9 | 278.9 | 282.2 | 298.3 | 221.5
1024 | 926 | 526.3 | 425.8 | 474.2 | 424.5 | 312.6 | 286.2 | 279.2 | 282.4 | 298.5 | 221.8
1025 | 927 | 526.3 | 425.9 | 474.2 | 424.6 | 312.9 | 286.5 | 279.4 | 282.6 | 298.7 | 222.1
1026 | 928 | 526.3 | 426.1 | 474.3 | 424.7 | 313.3 | 286.9 | 279.6 | 282.9 | 298.9 | 222.4
1027 | 929 | 526.3 | 426.2 | 474.4 | 424.9 | 313.6 | 287.2 | 279.9 | 283.2 | 299.2 | 222.6
1028 | 930 | 526.3 | 426.3 | 474.4 | 425 | 314 | 287.5 | 280.1 | 283.4 | 299.4 | 222.9
1029 | 931 | 526.3 | 426.4 | 474.5 | 425.1 | 314.3 | 287.8 | 280.3 | 283.6 | 299.6 | 223.1
1030 | 932 | 526.3 | 426.6 | 474.6 | 425.3 | 314.7 | 288 | 280.5 | 283.9 | 299.8 | 223.4
1031 | 933 | 526.3 | 426.7 | 474.7 | 425.4 | 315 | 288.2 | 280.8 | 284.2 | 300 | 223.6
1032 | 934 | 526.3 | 426.8 | 474.7 | 425.5 | 315.4 | 288.4 | 281 | 284.4 | 300.2 | 223.9
1033 | 935 | 526.4 | 426.9 | 474.7 | 425.6 | 315.7 | 288.7 | 281.2 | 284.5 | 300.4 | 224.2
1034 | 936 | 526.4 | 427 | 474.8 | 425.8 | 316 | 288.9 | 281.5 | 284.7 | 300.6 | 224.5
1035 | 937 | 526.4 | 427.2 | 474.9 | 425.9 | 316.4 | 289.2 | 281.7 | 284.9 | 300.8 | 224.7
1036 | 938 | 526.4 | 427.3 | 475 | 426 | 316.7 | 289.5 | 281.9 | 285.1 | 301 | 225
1037 | 939 | 526.5 | 427.4 | 475.1 | 426.1 | 317 | 289.8 | 282.1 | 285.3 | 301.2 | 225.3
1038 | 940 | 526.5 | 427.5 | 475.2 | 426.3 | 317.3 | 290.1 | 282.3 | 285.6 | 301.4 | 225.5
1039 | 941 | 526.6 | 427.6 | 475.3 | 426.4 | 317.6 | 290.3 | 282.6 | 285.7 | 301.6 | 225.8
1040 | 942 | 526.6 | 427.8 | 475.3 | 426.5 | 317.9 | 290.7 | 282.8 | 286 | 301.8 | 226.1
1041 | 943 | 526.6 | 427.9 | 475.4 | 426.6 | 318.2 | 290.8 | 283 | 286.2 | 302 | 226.3
1042 | 944 | 526.6 | 428 | 475.5 | 426.7 | 318.6 | 291.1 | 283.3 | 286.4 | 302.2 | 226.6
1043 | 945 | 526.7 | 428.1 | 475.5 | 426.9 | 318.9 | 291.5 | 283.5 | 286.6 | 302.4 | 226.8
1044 | 946 | 526.7 | 428.2 | 475.6 | 427 | 319.2 | 291.7 | 283.7 | 286.8 | 302.6 | 227.1
1045 | 947 | 526.8 | 428.4 | 475.7 | 427.1 | 319.5 | 292 | 283.9 | 286.9 | 302.8 | 227.3
1046 | 948 | 526.8 | 428.5 | 475.8 | 427.2 | 319.8 | 292.4 | 284.1 | 287.1 | 303.1 | 227.6
1047 | 949 | 526.8 | 428.6 | 475.8 | 427.3 | 320.1 | 292.7 | 284.3 | 287.3 | 303.3 | 227.9
1048 | 950 | 526.8 | 428.7 | 475.9 | 427.4 | 320.4 | 293 | 284.6 | 287.5 | 303.4 | 228.1
1049 | 951 | 526.8 | 428.8 | 476 | 427.6 | 320.7 | 293.3 | 284.8 | 287.7 | 303.6 | 228.4
1050 | 952 | 526.8 | 428.9 | 476 | 427.7 | 321 | 293.7 | 285 | 287.9 | 303.9 | 228.6
1051 | 953 | 526.8 | 429.1 | 476.1 | 427.8 | 321.3 | 294 | 285.2 | 288.2 | 304.1 | 228.9
1052 | 954 | 526.8 | 429.2 | 476.1 | 427.9 | 321.7 | 294.2 | 285.4 | 288.4 | 304.3 | 229.1
1053 | 955 | 526.8 | 429.3 | 476.2 | 428 | 322 | 294.5 | 285.7 | 288.7 | 304.5 | 229.4
1054 | 956 | 526.8 | 429.4 | 476.3 | 428.2 | 322.3 | 294.9 | 285.9 | 288.8 | 304.7 | 229.7
1055 | 957 | 526.8 | 429.5 | 476.3 | 428.3 | 322.7 | 295.1 | 286.2 | 289 | 304.9 | 229.9
1056 | 958 | 526.8 | 429.6 | 476.4 | 428.4 | 323 | 295.4 | 286.4 | 289.2 | 305.1 | 230.1
1057 | 959 | 526.8 | 429.7 | 476.5 | 428.5 | 323.3 | 295.6 | 286.7 | 289.5 | 305.3 | 230.4
1058 | 960 | 526.8 | 429.9 | 476.5 | 428.6 | 323.7 | 295.9 | 286.9 | 289.7 | 305.5 | 230.6
1059 | 961 | 526.8 | 430 | 476.6 | 428.7 | 324 | 296.2 | 287.2 | 289.9 | 305.7 | 230.8
1060 | 962 | 526.8 | 430.1 | 476.7 | 428.8 | 324.3 | 296.5 | 287.5 | 290.1 | 306 | 231
1061 | 963 | 526.8 | 430.2 | 476.7 | 429 | 324.7 | 296.7 | 287.7 | 290 | 306.2 | 231.4
1062 | 964 | 526.8 | 430.3 | 476.8 | 429.1 | 325 | 297.1 | 288 | 290.6 | 306.4 | 231.5
1063 | 965 | 526.8 | 430.4 | 476.8 | 429.2 | 325.4 | 297.5 | 288.2 | 290.8 | 306.5 | 231.8
1064 | 966 | 526.8 | 430.5 | 477 | 429.3 | 325.7 | 297.9 | 288.5 | 291 | 306.7 | 232.1
1065 | 967 | 526.8 | 430.6 | 477 | 429.4 | 326.1 | 298.2 | 288.7 | 291.3 | 306.9 | 232.3
1066 | 968 | 526.9 | 430.8 | 477.1 | 429.5 | 326.4 | 298.6 | 289 | 291.5 | 307.1 | 232.5
1067 | 969 | 526.9 | 430.9 | 477.2 | 429.6 | 326.8 | 298.9 | 289.3 | 291.8 | 307.3 | 232.8
1068 | 970 | 526.8 | 431 | 477.3 | 429.8 | 327.1 | 299.2 | 289.6 | 292 | 307.5 | 233
1069 | 971 | 526.8 | 431.1 | 477.3 | 429.9 | 327.4 | 299.4 | 289.8 | 292.2 | 307.8 | 233.3
1070 | 972 | 526.8 | 431.2 | 477.4 | 430 | 327.8 | 300 | 290 | 292.5 | 308 | 233.5
1071 | 973 | 526.8 | 431.3 | 477.5 | 430.1 | 328.1 | 300.7 | 290.3 | 292.7 | 308.2 | 233.8
1072 | 974 | 526.8 | 431.4 | 477.5 | 430.2 | 328.4 | 301.2 | 290.4 | 293 | 308.5 | 234
1073 | 975 | 526.8 | 431.5 | 477.6 | 430.3 | 328.8 | 301.8 | 290.7 | 293.2 | 308.7 | 234.2
1074 | 976 | 526.7 | 431.6 | 477.6 | 430.4 | 329.1 | 302.2 | 291 | 293.4 | 309 | 234.4
1075 | 977 | 526.7 | 431.7 | 477.7 | 430.5 | 329.5 | 302.4 | 291.2 | 293.7 | 309.3 | 234.8
1076 | 978 | 526.7 | 431.8 | 477.8 | 430.7 | 329.8 | 302.7 | 291.5 | 294 | 309.5 | 234.9
1077 | 979 | 526.7 | 431.9 | 477.9 | 430.8 | 330.1 | 302.8 | 291.8 | 294.2 | 309.8 | 235.1
1078 | 980 | 526.7 | 432 | 477.9 | 430.9 | 330.4 | 303 | 292.1 | 294.5 | 310.1 | 235.4
1079 | 981 | 526.7 | 432.1 | 478 | 431 | 330.8 | 303.2 | 292.3 | 294.8 | 310.4 | 235.6
1080 | 982 | 526.6 | 432.3 | 478 | 431.1 | 331.1 | 303.6 | 292.6 | 295 | 310.6 | 235.8
1081 | 983 | 526.6 | 432.4 | 478.1 | 431.2 | 331.4 | 304 | 292.9 | 295.3 | 310.9 | 236.1
1082 | 984 | 526.6 | 432.5 | 478.2 | 431.3 | 331.7 | 304.5 | 293.1 | 295.5 | 311.2 | 236.3
1083 | 985 | 526.6 | 432.6 | 478.2 | 431.4 | 332 | 304.8 | 293.4 | 295.7 | 311.4 | 236.5
1084 | 986 | 526.6 | 432.7 | 478.3 | 431.5 | 332.3 | 305.1 | 293.6 | 296 | 311.7 | 236.8
1085 | 987 | 526.6 | 432.8 | 478.3 | 431.6 | 332.7 | 305.4 | 293.9 | 296.2 | 312 | 237
1086 | 988 | 526.5 | 432.9 | 478.4 | 431.8 | 333 | 305.7 | 294.1 | 296.4 | 312.2 | 237.2
1087 | 989 | 526.5 | 433 | 478.4 | 431.9 | 333.3 | 305.8 | 294.3 | 296.6 | 312.5 | 237.4
1088 | 990 | 526.5 | 433.1 | 478.5 | 432 | 333.6 | 306 | 294.6 | 296.8 | 312.8 | 237.7
1089 | 991 | 526.5 | 433.2 | 478.6 | 432.1 | 334 | 306.1 | 294.9 | 297.1 | 313 | 237.9
1090 | 992 | 526.5 | 433.3 | 478.7 | 432.2 | 334.2 | 306.3 | 295.2 | 297.4 | 313.3 | 238.1
1091 | 993 | 526.5 | 433.4 | 478.7 | 432.3 | 334.6 | 306.5 | 295.4 | 297.6 | 313.5 | 238.4
1092 | 994 | 526.5 | 433.5 | 478.8 | 432.4 | 334.9 | 306.7 | 295.7 | 297.8 | 313.8 | 238.6
1093 | 995 | 526.4 | 433.6 | 478.8 | 432.5 | 335.2 | 307 | 296 | 298.1 | 314 | 238.8
1094 | 996 | 526.4 | 433.7 | 478.9 | 432.6 | 335.5 | 307.3 | 296.2 | 298.4 | 314.2 | 239
1095 | 997 | 526.4 | 433.8 | 478.9 | 432.7 | 335.8 | 307.6 | 296.5 | 298.7 | 314.5 | 239.3
1096 | 998 | 526.5 | 433.9 | 479 | 432.8 | 336.1 | 307.9 | 296.8 | 299 | 314.7 | 239.5
1097 | 999 | 526.5 | 434 | 479.1 | 432.9 | 336.4 | 308.2 | 297 | 299.2 | 314.9 | 239.8
1098 | 1000 | 526.5 | 434.2 | 479.2 | 433 | 336.7 | 308.3 | 297.3 | 299.5 | 315.2 | 240
1099 | 1001 | 526.5 | 434.3 | 479.2 | 433.2 | 337.1 | 308.5 | 297.6 | 299.7 | 315.5 | 240.2
1100 | 1002 | 526.5 | 434.4 | 479.3 | 433.3 | 337.4 | 294.5 | 297.9 | 295.7 | 315.8 | 240.5
1101 | 1003 | 526.5 | 434.5 | 479.4 | 433.4 | 337.7 | 306 | 298.2 | 299.3 | 316.1 | 240.7
1102 | 1004 | 526.5 | 434.5 | 479.4 | 433.5 | 338 | 309.2 | 298.5 | 300.5 | 316.3 | 241
1103 | 1005 | 526.5 | 434.7 | 479.5 | 433.6 | 338.4 | 263.6 | 298.7 | 282.6 | 316.6 | 241.3
1104 | 1006 | 526.5 | 434.7 | 479.5 | 433.7 | 338.7 | 309.3 | 298.9 | 300.9 | 316.9 | 241.5
1105 | 1007 | 526.5 | 434.8 | 479.6 | 433.8 | 339 | 298.9 | 299.2 | 294.4 | 317.2 | 241.8
1106 | 1008 | 526.5 | 434.9 | 479.6 | 433.9 | 339.4 | 257.6 | 299.4 | 268.4 | 317.5 | 242.1
1107 | 1009 | 526.5 | 435 | 479.7 | 434 | 339.7 | 311 | 299.6 | 301.9 | 317.8 | 242.3
1108 | 1010 | 526.5 | 435.1 | 479.8 | 434.1 | 340 | 310.2 | 299.9 | 302.1 | 318.1 | 242.6
1109 | 1011 | 526.6 | 435.2 | 479.8 | 434.2 | 340.3 | 309.5 | 300.2 | 302.2 | 318.4 | 242.8
1110 | 1012 | 526.6 | 435.3 | 479.9 | 434.3 | 340.6 | 312.4 | 300.5 | 302.7 | 318.7 | 243
1111 | 1013 | 526.6 | 435.4 | 479.9 | 434.4 | 340.9 | 269.4 | 300.2 | 274.7 | 319 | 243.3
1112 | 1014 | 526.6 | 435.5 | 480 | 434.5 | 341.1 | 282 | 300.6 | 283.9 | 319.3 | 243.5
1113 | 1015 | 526.6 | 435.6 | 480 | 434.6 | 341.5 | 296.6 | 301.1 | 298.3 | 319.5 | 243.8
1114 | 1016 | 526.6 | 435.7 | 480.1 | 434.7 | 341.8 | 265.5 | 301.4 | 280 | 319.8 | 244
1115 | 1017 | 526.7 | 435.8 | 480.2 | 434.8 | 342 | 304.5 | 301.8 | 299.7 | 320.1 | 244.2
1116 | 1018 | 526.7 | 435.9 | 480.2 | 434.9 | 342.3 | 313.7 | 302.1 | 304.1 | 320.3 | 244.5
1117 | 1019 | 526.7 | 436 | 480.3 | 435 | 342.6 | 258.6 | 302.3 | 281.6 | 320.6 | 244.8
1118 | 1020 | 526.8 | 436.1 | 480.3 | 435.1 | 342.9 | 313.9 | 302.6 | 304.6 | 320.9 | 245
1119 | 1021 | 526.8 | 436.2 | 480.4 | 435.2 | 343.2 | 314.6 | 302.9 | 305.2 | 321.2 | 245.2
1120 | 1022 | 526.8 | 436.3 | 480.4 | 435.3 | 343.5 | 314.8 | 303 | 305.5 | 321.4 | 245.5
1121 | 1023 | 526.9 | 436.4 | 480.5 | 435.4 | 343.8 | 315.1 | 303.3 | 305.8 | 321.7 | 245.7
1122 | 1024 | 526.9 | 436.5 | 480.6 | 435.5 | 344.2 | 315.6 | 303.6 | 306.1 | 322 | 246
1123 | 1025 | 526.9 | 436.6 | 480.6 | 435.7 | 344.5 | 315.9 | 303.8 | 306.4 | 322.2 | 246.2
1124 | 1026 | 526.9 | 436.7 | 480.7 | 435.7 | 344.9 | 316.1 | 304.1 | 306.6 | 322.5 | 246.5
1125 | 1027 | 526.9 | 436.8 | 480.8 | 435.8 | 345.2 | 316.2 | 304.4 | 306.9 | 322.8 | 246.8
1126 | 1028 | 526.9 | 436.9 | 480.8 | 435.9 | 345.5 | 316.4 | 304.6 | 307.1 | 323.1 | 247
1127 | 1029 | 526.9 | 437 | 480.9 | 436 | 345.9 | 316.9 | 304.9 | 307.4 | 323.4 | 247.3
1128 | 1030 | 526.8 | 437.1 | 480.9 | 436.1 | 346.2 | 317.3 | 305.2 | 307.7 | 323.7 | 247.5
1129 | 1031 | 526.8 | 437.2 | 481 | 436.2 | 346.6 | 317.5 | 305.5 | 308 | 323.9 | 247.8
1130 | 1032 | 526.8 | 437.3 | 481 | 436.3 | 346.9 | 317.9 | 305.8 | 308.3 | 324.2 | 248
1131 | 1033 | 526.8 | 437.3 | 481.1 | 436.4 | 347.3 | 318.1 | 306 | 308.6 | 324.5 | 248.3
1132 | 1034 | 526.9 | 437.4 | 481.2 | 436.5 | 347.6 | 318.3 | 306.3 | 308.9 | 324.8 | 248.5
1133 | 1035 | 526.9 | 437.5 | 481.3 | 436.6 | 348 | 318.6 | 306.6 | 309.2 | 325 | 248.8
1134 | 1036 | 526.9 | 437.6 | 481.3 | 436.7 | 348.3 | 318.8 | 306.8 | 309.4 | 325.3 | 249
1135 | 1037 | 526.9 | 437.7 | 481.3 | 436.8 | 348.6 | 319.1 | 307.1 | 309.7 | 325.6 | 249.3
1136 | 1038 | 526.9 | 437.8 | 481.4 | 436.9 | 349 | 319.4 | 307.4 | 310 | 325.9 | 249.5
1137 | 1039 | 526.9 | 437.9 | 481.5 | 437 | 349.3 | 319.6 | 307.7 | 310.2 | 326.2 | 249.8
1138 | 1040 | 527 | 438 | 481.5 | 437.1 | 349.6 | 319.9 | 307.9 | 310.4 | 326.5 | 250.1
1139 | 1041 | 527 | 438.1 | 481.6 | 437.2 | 350 | 270.9 | 308.1 | 278.7 | 326.8 | 250.4
1140 | 1042 | 527 | 438.2 | 481.7 | 437.2 | 350.3 | 291 | 308.5 | 292.1 | 327.2 | 250.6
1141 | 1043 | 527 | 438.3 | 481.7 | 437.3 | 350.7 | 320.8 | 308.8 | 311.4 | 327.5 | 250.8
1142 | 1044 | 527 | 438.4 | 481.8 | 437.4 | 351 | 247.7 | 308.5 | 262.4 | 327.8 | 251.1
1143 | 1045 | 527 | 438.4 | 482 | 437.5 | 351.3 | 307.8 | 309.3 | 303 | 328.1 | 251.3
1144 | 1046 | 527 | 438.5 | 482 | 437.6 | 351.7 | 321.1 | 309.5 | 312 | 328.4 | 251.5
1145 | 1047 | 526.9 | 438.6 | 482 | 437.7 | 352 | 233.4 | 309.9 | 254.1 | 328.7 | 251.9
1146 | 1048 | 526.8 | 438.7 | 482.1 | 437.8 | 352.3 | 321 | 310.1 | 312.1 | 329 | 252
1147 | 1049 | 526.8 | 438.7 | 482.1 | 437.9 | 352.6 | 306.6 | 310.3 | 302.8 | 329.3 | 252.3
1148 | 1050 | 526.8 | 438.8 | 482.2 | 437.9 | 352.9 | 250.1 | 310.6 | 265.4 | 329.6 | 252.6
1149 | 1051 | 526.8 | 438.9 | 482.3 | 438 | 353.2 | 322.9 | 310.9 | 313.6 | 329.8 | 252.7
1150 | 1052 | 526.8 | 439 | 482.3 | 438.1 | 353.5 | 312.9 | 311.1 | 311.6 | 330.1 | 253
1151 | 1053 | 526.8 | 439.1 | 482.4 | 438.2 | 353.8 | 313 | 311.5 | 312.2 | 330.4 | 253.3
1152 | 1054 | 526.8 | 439.2 | 482.5 | 438.3 | 354.2 | 323.7 | 311.8 | 314.4 | 330.7 | 253.5
1153 | 1055 | 526.7 | 439.3 | 482.5 | 438.4 | 354.5 | 275.8 | 312.1 | 285.7 | 330.9 | 253.8
1154 | 1056 | 526.7 | 439.4 | 482.6 | 438.5 | 354.8 | 294.4 | 312.4 | 298.8 | 331.2 | 254
1155 | 1057 | 526.7 | 439.4 | 482.6 | 438.6 | 355.1 | 322.2 | 312.6 | 315.1 | 331.4 | 254.3
1156 | 1058 | 526.7 | 439.5 | 482.6 | 438.7 | 355.4 | 325.1 | 312.8 | 315.4 | 331.7 | 254.6
1157 | 1059 | 526.7 | 439.6 | 482.7 | 438.8 | 355.7 | 325.4 | 313.1 | 315.7 | 331.9 | 254.8
1158 | 1060 | 526.7 | 439.7 | 482.8 | 438.8 | 356 | 325.5 | 313.4 | 315.9 | 332.2 | 255.1
1159 | 1061 | 526.8 | 439.8 | 482.9 | 438.9 | 356.3 | 325.9 | 313.6 | 316.2 | 332.4 | 255.4
1160 | 1062 | 526.8 | 439.9 | 482.9 | 439 | 356.6 | 326.2 | 313.8 | 316.4 | 332.7 | 255.6
1161 | 1063 | 526.7 | 440 | 483 | 439.1 | 356.9 | 326.4 | 314.1 | 316.7 | 332.9 | 255.8
1162 | 1064 | 526.7 | 440.1 | 483 | 439.2 | 357.2 | 326.6 | 314.4 | 316.9 | 333.2 | 256.1
1163 | 1065 | 526.6 | 440.1 | 483 | 439.3 | 357.5 | 327 | 314.7 | 317.2 | 333.5 | 256.3
1164 | 1066 | 526.6 | 440.2 | 483.1 | 439.4 | 357.8 | 327.3 | 315 | 317.4 | 333.7 | 256.6
1165 | 1067 | 526.6 | 440.3 | 483.2 | 439.5 | 358.1 | 327.5 | 315.2 | 317.7 | 334 | 256.9
1166 | 1068 | 526.6 | 440.4 | 483.2 | 439.5 | 358.5 | 327.9 | 315.5 | 318 | 334.3 | 257.1
1167 | 1069 | 526.6 | 440.5 | 483.3 | 439.6 | 358.8 | 328.2 | 315.7 | 318.3 | 334.6 | 257.3
1168 | 1070 | 526.7 | 440.5 | 483.3 | 439.7 | 359 | 328.6 | 316 | 318.6 | 334.9 | 257.6
1169 | 1071 | 526.7 | 440.6 | 483.4 | 439.8 | 359.3 | 328.8 | 316.3 | 318.8 | 335.2 | 257.8
1170 | 1072 | 526.7 | 440.7 | 483.4 | 439.9 | 359.6 | 329.2 | 316.5 | 319 | 335.4 | 258.1
1171 | 1073 | 526.8 | 440.8 | 483.5 | 440 | 360 | 329.5 | 316.8 | 319.2 | 335.7 | 258.3
1172 | 1074 | 526.8 | 440.9 | 483.5 | 440 | 360.3 | 329.7 | 317.1 | 319.5 | 336 | 258.6
1173 | 1075 | 526.8 | 441 | 483.6 | 440.1 | 360.6 | 330 | 317.4 | 319.8 | 336.3 | 258.9
1174 | 1076 | 526.8 | 441 | 483.7 | 440.2 | 360.9 | 330.4 | 317.7 | 320 | 336.6 | 259.2
1175 | 1077 | 526.8 | 441.1 | 483.7 | 440.3 | 361.2 | 330.7 | 318 | 320.3 | 336.9 | 259.4
1176 | 1078 | 526.8 | 441.2 | 483.7 | 440.4 | 361.5 | 331.1 | 318.3 | 320.6 | 337.2 | 259.7
1177 | 1079 | 526.7 | 441.3 | 483.8 | 440.5 | 361.8 | 331.5 | 318.6 | 320.9 | 337.5 | 260
1178 | 1080 | 526.7 | 441.4 | 483.8 | 440.6 | 362.1 | 331.7 | 318.9 | 321.2 | 337.8 | 260.2
1179 | 1081 | 526.8 | 441.4 | 483.9 | 440.6 | 362.4 | 331.9 | 319.1 | 321.5 | 338 | 260.5
1180 | 1082 | 526.8 | 441.5 | 483.9 | 440.7 | 362.7 | 332.2 | 319.4 | 321.7 | 338.3 | 260.7
1181 | 1083 | 526.8 | 441.6 | 484 | 440.8 | 363 | 332.6 | 319.6 | 322 | 338.6 | 261
1182 | 1084 | 526.8 | 441.7 | 484 | 440.9 | 363.3 | 332.9 | 319.9 | 322.2 | 338.9 | 261.2
1183 | 1085 | 526.9 | 441.7 | 484.1 | 441 | 363.6 | 333.2 | 320.2 | 322.4 | 339.2 | 261.5
1184 | 1086 | 526.9 | 441.8 | 484.1 | 441.1 | 363.9 | 333.5 | 320.4 | 322.7 | 339.4 | 261.7
1185 | 1087 | 526.9 | 441.9 | 484.2 | 441.2 | 364.1 | 333.9 | 320.7 | 323 | 339.7 | 261.9
1186 | 1088 | 526.9 | 442 | 484.2 | 441.2 | 364.4 | 334.2 | 321 | 323.3 | 340 | 262.2
1187 | 1089 | 526.9 | 442 | 484.3 | 441.3 | 364.7 | 334.5 | 321.2 | 323.5 | 340.3 | 262.5
1188 | 1090 | 526.9 | 442.1 | 484.3 | 441.4 | 365 | 334.7 | 321.5 | 323.8 | 340.5 | 262.7
1189 | 1091 | 526.9 | 442.2 | 484.4 | 441.5 | 365.3 | 335.1 | 321.8 | 324.1 | 340.8 | 262.9
1190 | 1092 | 526.9 | 442.3 | 484.4 | 441.5 | 365.6 | 335.2 | 322.1 | 324.3 | 341.1 | 263.2
1191 | 1093 | 526.9 | 442.4 | 484.5 | 441.6 | 365.9 | 335.4 | 322.4 | 324.6 | 341.4 | 263.4
1192 | 1094 | 526.9 | 442.4 | 484.6 | 441.7 | 366.2 | 335.7 | 322.6 | 324.8 | 341.6 | 263.7
1193 | 1095 | 526.9 | 442.5 | 484.6 | 441.8 | 366.5 | 336.1 | 322.9 | 325 | 341.9 | 264
1194 | 1096 | 526.8 | 442.6 | 484.7 | 441.9 | 366.8 | 336.4 | 323.2 | 325.3 | 342.2 | 264.2
1195 | 1097 | 526.8 | 442.7 | 484.7 | 441.9 | 367.1 | 336.6 | 323.4 | 325.6 | 342.4 | 264.5
1196 | 1098 | 526.8 | 442.7 | 484.8 | 442 | 367.4 | 336.8 | 323.7 | 325.8 | 342.7 | 264.7
1197 | 1099 | 526.8 | 442.8 | 484.8 | 442.1 | 367.7 | 337.1 | 323.9 | 326.1 | 342.9 | 265
1198 | 1100 | 526.9 | 442.9 | 484.9 | 442.2 | 368 | 337.5 | 324.2 | 326.3 | 343.2 | 265.3
1199 | 1101 | 526.9 | 442.9 | 485 | 442.3 | 368.3 | 337.8 | 324.5 | 326.6 | 343.5 | 265.5
1200 | 1102 | 526.9 | 443 | 485 | 442.4 | 368.6 | 338 | 324.8 | 326.9 | 343.7 | 265.7
1201 | 1103 | 526.8 | 443.1 | 485 | 442.4 | 368.9 | 338.2 | 325 | 327.1 | 344 | 266
1202 | 1104 | 526.8 | 443.2 | 485.1 | 442.5 | 369.2 | 338.5 | 325.3 | 327.3 | 344.3 | 266.2
1203 | 1105 | 526.8 | 443.2 | 485.1 | 442.6 | 369.4 | 338.8 | 325.6 | 327.6 | 344.5 | 266.4
1204 | 1106 | 526.7 | 443.3 | 485.2 | 442.7 | 369.7 | 339.2 | 325.9 | 327.8 | 344.8 | 266.7
1205 | 1107 | 526.7 | 443.4 | 485.2 | 442.8 | 370 | 339.4 | 326.2 | 328 | 345 | 266.9
1206 | 1108 | 526.7 | 443.5 | 485.3 | 442.8 | 370.3 | 339.7 | 326.5 | 328.3 | 345.3 | 267.1
1207 | 1109 | 526.6 | 443.5 | 485.3 | 442.9 | 370.7 | 340 | 326.7 | 328.5 | 345.5 | 267.3
1208 | 1110 | 526.6 | 443.6 | 485.4 | 443 | 371 | 340.3 | 327 | 328.8 | 345.8 | 267.5
1209 | 1111 | 526.6 | 443.7 | 485.4 | 443 | 371.3 | 340.5 | 327.2 | 329 | 346 | 267.7
1210 | 1112 | 526.6 | 443.7 | 485.5 | 443.1 | 371.7 | 340.7 | 327.5 | 329.2 | 346.3 | 268
1211 | 1113 | 526.6 | 443.8 | 485.5 | 443.2 | 372 | 341 | 327.8 | 329.5 | 346.5 | 268.2
1212 | 1114 | 526.6 | 443.9 | 485.6 | 443.3 | 372.4 | 341.2 | 328 | 329.7 | 346.8 | 268.4
1213 | 1115 | 526.6 | 444 | 485.6 | 443.3 | 372.7 | 341.3 | 328.3 | 330 | 347.1 | 268.6
1214 | 1116 | 526.6 | 444 | 485.7 | 443.4 | 373.1 | 341.6 | 328.5 | 330.2 | 347.3 | 268.9
1215 | 1117 | 526.7 | 444.1 | 485.7 | 443.5 | 373.5 | 341.8 | 328.7 | 330.5 | 347.6 | 269.1
1216 | 1118 | 526.7 | 444.2 | 485.7 | 443.6 | 373.9 | 342 | 328.9 | 330.8 | 347.9 | 269.3
1217 | 1119 | 526.7 | 444.2 | 485.8 | 443.7 | 374.3 | 342.4 | 329.2 | 331 | 348.1 | 269.5
1218 | 1120 | 526.7 | 444.3 | 485.9 | 443.7 | 374.7 | 342.7 | 329.5 | 331.2 | 348.4 | 269.7
1219 | 1121 | 526.7 | 444.4 | 485.9 | 443.8 | 375.1 | 343 | 329.7 | 331.4 | 348.6 | 269.9
1220 | 1122 | 526.8 | 444.4 | 486 | 443.9 | 375.5 | 343.1 | 330 | 331.6 | 348.9 | 270.1
1221 | 1123 | 526.8 | 444.5 | 486 | 443.9 | 375.8 | 343.5 | 330.3 | 331.8 | 349.2 | 270.3
1222 | 1124 | 526.8 | 444.6 | 486.1 | 444 | 376.2 | 343.8 | 330.5 | 332 | 349.4 | 270.6
1223 | 1125 | 526.7 | 444.7 | 486.1 | 444.1 | 376.7 | 344.1 | 330.8 | 332.3 | 349.7 | 270.8
1224 | 1126 | 526.7 | 444.7 | 486.2 | 444.2 | 377.1 | 344.3 | 331.1 | 332.5 | 350 | 271
1225 | 1127 | 526.7 | 444.8 | 486.2 | 444.2 | 377.5 | 344.6 | 331.4 | 332.8 | 350.2 | 271.2
1226 | 1128 | 526.7 | 444.9 | 486.3 | 444.3 | 377.9 | 345 | 331.6 | 333 | 350.5 | 271.4
1227 | 1129 | 526.7 | 444.9 | 486.3 | 444.4 | 378.3 | 345.2 | 331.9 | 333.2 | 350.8 | 271.6
1228 | 1130 | 526.7 | 445 | 486.3 | 444.5 | 378.7 | 345.5 | 332.1 | 333.3 | 351.1 | 271.8
1229 | 1131 | 526.7 | 445.1 | 486.4 | 444.5 | 379.1 | 345.9 | 332.4 | 333.6 | 351.3 | 272.1
1230 | 1132 | 526.7 | 445.1 | 486.4 | 444.6 | 379.5 | 346.2 | 332.6 | 333.8 | 351.6 | 272.2
1231 | 1133 | 526.7 | 445.2 | 486.5 | 444.7 | 379.9 | 346.4 | 332.9 | 334 | 351.9 | 272.4
1232 | 1134 | 526.7 | 445.3 | 486.5 | 444.7 | 380.3 | 346.7 | 333.1 | 334.3 | 352.1 | 272.7
1233 | 1135 | 526.7 | 445.3 | 486.6 | 444.8 | 380.8 | 347 | 333.4 | 334.5 | 352.4 | 272.9
1234 | 1136 | 526.7 | 445.4 | 486.6 | 444.9 | 381.2 | 347.2 | 333.7 | 334.7 | 352.6 | 273.1
1235 | 1137 | 526.7 | 445.5 | 486.7 | 445 | 381.6 | 347.4 | 333.9 | 334.9 | 352.9 | 273.3
1236 | 1138 | 526.7 | 445.5 | 486.7 | 445 | 382 | 347.8 | 334.1 | 335.1 | 353.1 | 273.5
1237 | 1139 | 526.7 | 445.6 | 486.7 | 445.1 | 382.4 | 348.2 | 334.4 | 335.3 | 353.4 | 273.8
1238 | 1140 | 526.7 | 445.7 | 486.8 | 445.2 | 382.9 | 348.7 | 334.6 | 335.6 | 353.6 | 274
1239 | 1141 | 526.7 | 445.7 | 486.8 | 445.3 | 383.3 | 349.2 | 334.8 | 335.8 | 353.9 | 274.2
1240 | 1142 | 526.7 | 445.8 | 486.9 | 445.3 | 383.7 | 349.7 | 335.1 | 336 | 354.1 | 274.5
1241 | 1143 | 526.7 | 445.9 | 486.9 | 445.4 | 384.1 | 350.1 | 335.3 | 336.2 | 354.4 | 274.7
1242 | 1144 | 526.7 | 445.9 | 487 | 445.4 | 384.5 | 350.4 | 335.6 | 336.5 | 354.6 | 274.9
1243 | 1145 | 526.7 | 446 | 487 | 445.5 | 384.9 | 350.9 | 335.8 | 336.7 | 354.8 | 275.1
1244 | 1146 | 526.7 | 446 | 487.1 | 445.6 | 385.3 | 351.3 | 336.1 | 336.9 | 355.1 | 275.3
1245 | 1147 | 526.7 | 446.1 | 487.1 | 445.6 | 385.7 | 351.7 | 336.3 | 337.2 | 355.3 | 275.6
1246 | 1148 | 526.7 | 446.2 | 487.2 | 445.7 | 386.1 | 352.1 | 336.6 | 337.4 | 355.5 | 275.8
1247 | 1149 | 526.7 | 446.2 | 487.2 | 445.8 | 386.5 | 352.5 | 336.8 | 337.7 | 355.7 | 276
1248 | 1150 | 526.7 | 446.3 | 487.3 | 445.9 | 386.9 | 352.8 | 337 | 337.9 | 356 | 276.2
1249 | 1151 | 526.7 | 446.4 | 487.3 | 445.9 | 387.3 | 353.1 | 337.2 | 338.2 | 356.2 | 276.3
1250 | 1152 | 526.7 | 446.4 | 487.4 | 446 | 387.7 | 353.4 | 337.5 | 338.4 | 356.5 | 276.5
1251 | 1153 | 526.7 | 446.5 | 487.4 | 446.1 | 388.1 | 353.8 | 337.7 | 338.6 | 356.7 | 276.7
1252 | 1154 | 526.7 | 446.5 | 487.4 | 446.2 | 388.5 | 354.2 | 337.9 | 338.8 | 357 | 276.9
1253 | 1155 | 526.7 | 446.6 | 487.5 | 446.2 | 388.9 | 354.7 | 338.2 | 339 | 357.2 | 277
1254 | 1156 | 526.7 | 446.7 | 487.5 | 446.3 | 389.3 | 355 | 338.4 | 339.2 | 357.4 | 277.2
1255 | 1157 | 526.6 | 446.7 | 487.5 | 446.3 | 389.6 | 355.4 | 338.6 | 339.4 | 357.7 | 277.4
1256 | 1158 | 526.6 | 446.8 | 487.6 | 446.4 | 390 | 355.7 | 338.9 | 339.6 | 357.9 | 277.6
1257 | 1159 | 526.5 | 446.8 | 487.6 | 446.5 | 390.4 | 356.1 | 339.1 | 339.8 | 358.1 | 277.9
1258 | 1160 | 526.5 | 446.9 | 487.7 | 446.5 | 390.7 | 356.4 | 339.3 | 340 | 358.3 | 278
1259 | 1161 | 526.5 | 447 | 487.7 | 446.6 | 391.1 | 356.6 | 339.5 | 340.2 | 358.5 | 278.3
1260 | 1162 | 526.5 | 447 | 487.7 | 446.7 | 391.4 | 357 | 339.7 | 340.4 | 358.8 | 278.5
1261 | 1163 | 526.5 | 447.1 | 487.8 | 446.8 | 391.7 | 357.3 | 340 | 340.7 | 359 | 278.7
1262 | 1164 | 526.5 | 447.1 | 487.8 | 446.8 | 392.1 | 357.6 | 340.3 | 340.9 | 359.2 | 278.9
1263 | 1165 | 526.5 | 447.2 | 487.9 | 446.9 | 392.4 | 357.8 | 340.5 | 341.1 | 359.4 | 279.1
1264 | 1166 | 526.5 | 447.3 | 487.9 | 447 | 392.7 | 358.1 | 340.7 | 341.4 | 359.6 | 279.4
1265 | 1167 | 526.5 | 447.3 | 488 | 447 | 393.1 | 358.4 | 340.9 | 341.6 | 359.8 | 279.6
1266 | 1168 | 526.5 | 447.4 | 488 | 447.1 | 393.4 | 358.7 | 341.1 | 341.8 | 360 | 279.8
1267 | 1169 | 526.5 | 447.4 | 488 | 447.1 | 393.7 | 359 | 341.3 | 342 | 360.3 | 280
1268 | 1170 | 526.5 | 447.5 | 488.1 | 447.2 | 394 | 359.2 | 341.6 | 342.2 | 360.5 | 280.2
1269 | 1171 | 526.5 | 447.5 | 488.1 | 447.3 | 394.3 | 359.3 | 341.8 | 342.5 | 360.7 | 280.4
1270 | 1172 | 526.5 | 447.6 | 488.2 | 447.4 | 394.6 | 359.5 | 342.1 | 342.7 | 360.9 | 280.6
1271 | 1173 | 526.5 | 447.7 | 488.2 | 447.4 | 395 | 359.9 | 342.4 | 342.9 | 361.1 | 280.9
1272 | 1174 | 526.5 | 447.7 | 488.3 | 447.5 | 395.3 | 360 | 342.6 | 343.1 | 361.3 | 281.1
1273 | 1175 | 526.5 | 447.8 | 488.3 | 447.5 | 395.6 | 360.3 | 342.9 | 343.3 | 361.5 | 281.3
1274 | 1176 | 526.5 | 447.8 | 488.4 | 447.6 | 395.9 | 360.5 | 343.1 | 343.5 | 361.7 | 281.5
1275 | 1177 | 526.5 | 447.9 | 488.4 | 447.7 | 396.2 | 360.7 | 343.3 | 343.8 | 361.9 | 281.8
1276 | 1178 | 526.5 | 448 | 488.5 | 447.7 | 396.5 | 360.9 | 343.6 | 343.9 | 362.1 | 282
1277 | 1179 | 526.5 | 448 | 488.5 | 447.8 | 396.8 | 361.1 | 343.8 | 344.1 | 362.3 | 282.2
1278 | 1180 | 526.4 | 448.1 | 488.6 | 447.9 | 397 | 361.4 | 344.1 | 344.3 | 362.5 | 282.4
1279 | 1181 | 526.4 | 448.1 | 488.6 | 447.9 | 397.3 | 361.8 | 344.3 | 344.5 | 362.7 | 282.6
1280 | 1182 | 526.4 | 448.2 | 488.7 | 448 | 397.6 | 362 | 344.5 | 344.7 | 363 | 282.8
1281 | 1183 | 526.4 | 448.2 | 488.7 | 448 | 397.9 | 362.3 | 344.7 | 345 | 363.2 | 283.1
1282 | 1184 | 526.4 | 448.3 | 488.7 | 448.1 | 398.2 | 362.5 | 345 | 345.2 | 363.4 | 283.3
1283 | 1185 | 526.4 | 448.4 | 488.7 | 448.2 | 398.5 | 362.7 | 345.2 | 345.4 | 363.7 | 283.5
1284 | 1186 | 526.4 | 448.4 | 488.8 | 448.2 | 398.7 | 363 | 345.4 | 345.6 | 363.9 | 283.7
1285 | 1187 | 526.5 | 448.5 | 488.9 | 448.3 | 399 | 363.3 | 345.6 | 345.9 | 364.1 | 283.9
1286 | 1188 | 526.5 | 448.5 | 488.9 | 448.4 | 399.3 | 363.3 | 345.9 | 346.1 | 364.3 | 284.1
1287 | 1189 | 526.6 | 448.6 | 489 | 448.4 | 399.5 | 363.5 | 346.1 | 346.3 | 364.6 | 284.3
1288 | 1190 | 526.6 | 448.7 | 489 | 448.5 | 399.8 | 363.6 | 346.4 | 346.5 | 364.8 | 284.5
1289 | 1191 | 526.6 | 448.7 | 489.1 | 448.6 | 400.1 | 363.8 | 346.6 | 346.7 | 365 | 284.7
1290 | 1192 | 526.6 | 448.8 | 489.1 | 448.6 | 400.3 | 364 | 346.8 | 346.9 | 365.2 | 284.9
1291 | 1193 | 526.5 | 448.8 | 489.2 | 448.7 | 400.6 | 364 | 347.1 | 347.1 | 365.4 | 285.1
1292 | 1194 | 526.5 | 448.9 | 489.2 | 448.8 | 400.8 | 363.9 | 347.4 | 347.3 | 365.6 | 285.3
1293 | 1195 | 526.5 | 448.9 | 489.2 | 448.8 | 401.1 | 362.9 | 347.5 | 347.6 | 365.9 | 285.5
1294 | 1196 | 526.5 | 449 | 489.3 | 448.9 | 401.3 | 362.4 | 347.7 | 347.8 | 366.1 | 285.7
1295 | 1197 | 526.5 | 449 | 489.3 | 448.9 | 401.6 | 362.2 | 347.9 | 348.1 | 366.3 | 285.9
1296 | 1198 | 526.5 | 449.1 | 489.4 | 449 | 401.8 | 362.2 | 348.1 | 348.4 | 366.5 | 286.1
1297 | 1199 | 526.5 | 449.2 | 489.4 | 449.1 | 402 | 362.1 | 348.4 | 348.6 | 366.7 | 286.3
1298 | 1200 | 526.5 | 449.2 | 489.5 | 449.1 | 402.3 | 362.2 | 348.6 | 348.8 | 366.9 | 286.5
1299 | 1201 | 526.5 | 449.3 | 489.5 | 449.2 | 402.5 | 362.4 | 348.9 | 349 | 367.1 | 286.7
1300 | 1202 | 526.6 | 449.3 | 489.5 | 449.3 | 402.8 | 362.5 | 349.1 | 349.2 | 367.3 | 286.8
1301 | 1203 | 526.6 | 449.4 | 489.6 | 449.3 | 403 | 362.7 | 349.3 | 349.5 | 367.5 | 287
1302 | 1204 | 526.6 | 449.4 | 489.6 | 449.4 | 403.2 | 362.8 | 349.5 | 349.7 | 367.6 | 287.2
1303 | 1205 | 526.6 | 449.5 | 489.7 | 449.4 | 403.4 | 363 | 349.8 | 350 | 367.8 | 287.4
1304 | 1206 | 526.6 | 449.5 | 489.7 | 449.5 | 403.6 | 363.2 | 350 | 350.2 | 368 | 287.6
1305 | 1207 | 526.6 | 449.6 | 489.7 | 449.6 | 403.8 | 363.3 | 350.3 | 350.4 | 368.2 | 287.8
1306 | 1208 | 526.6 | 449.7 | 489.8 | 449.6 | 404 | 363.5 | 350.5 | 350.6 | 368.4 | 288
1307 | 1209 | 526.7 | 449.7 | 489.8 | 449.7 | 404.1 | 363.6 | 350.8 | 350.9 | 368.6 | 288.1
1308 | 1210 | 526.7 | 449.7 | 489.8 | 449.8 | 404.3 | 363.8 | 351 | 351.1 | 368.8 | 288.3
1309 | 1211 | 526.7 | 449.8 | 489.9 | 449.8 | 404.5 | 364 | 351.2 | 351.4 | 369 | 288.5
1310 | 1212 | 526.8 | 449.9 | 489.9 | 449.8 | 404.7 | 364.2 | 351.4 | 351.6 | 369.1 | 288.7
1311 | 1213 | 526.8 | 449.9 | 490 | 449.9 | 404.9 | 364.3 | 351.7 | 351.8 | 369.3 | 288.9
1312 | 1214 | 526.8 | 450 | 490 | 450 | 405 | 364.5 | 351.9 | 351.9 | 369.5 | 289
1313 | 1215 | 526.9 | 450 | 490 | 450.1 | 405.2 | 364.7 | 352.1 | 352.1 | 369.7 | 289.2
1314 | 1216 | 526.9 | 450.1 | 490.1 | 450.1 | 405.4 | 364.9 | 352.3 | 352.3 | 369.9 | 289.4
1315 | 1217 | 526.9 | 450.1 | 490.1 | 450.2 | 405.5 | 365.1 | 352.5 | 352.4 | 370 | 289.6
1316 | 1218 | 526.9 | 450.2 | 490.2 | 450.3 | 405.7 | 365.3 | 352.8 | 352.7 | 370.2 | 289.8
1317 | 1219 | 526.9 | 450.2 | 490.2 | 450.3 | 405.9 | 365.4 | 353 | 352.9 | 370.4 | 289.9
1318 | 1220 | 526.9 | 450.3 | 490.3 | 450.4 | 406.1 | 365.6 | 353.3 | 353.1 | 370.5 | 290.1
1319 | 1221 | 526.9 | 450.3 | 490.3 | 450.4 | 406.4 | 365.8 | 353.5 | 353.4 | 370.7 | 290.3
1320 | 1222 | 526.9 | 450.4 | 490.4 | 450.5 | 406.7 | 366 | 353.7 | 353.6 | 370.9 | 290.4
1321 | 1223 | 526.9 | 450.4 | 490.4 | 450.5 | 406.9 | 366.2 | 354 | 353.8 | 371 | 290.6
1322 | 1224 | 526.9 | 450.5 | 490.4 | 450.6 | 407.2 | 366.4 | 354.2 | 354 | 371.1 | 290.8
1323 | 1225 | 527 | 450.6 | 490.5 | 450.6 | 407.4 | 366.6 | 354.4 | 354.3 | 371.2 | 290.9
1324 | 1226 | 527 | 450.6 | 490.6 | 450.7 | 407.6 | 366.8 | 354.7 | 354.5 | 371.3 | 291
1325 | 1227 | 527 | 450.6 | 490.6 | 450.8 | 407.8 | 367 | 354.9 | 354.7 | 371.4 | 291
1326 | 1228 | 527 | 450.7 | 490.6 | 450.8 | 407.9 | 367.2 | 355.1 | 355 | 371.6 | 291.1
1327 | 1229 | 527.1 | 450.7 | 490.7 | 450.9 | 408.1 | 367.4 | 355.4 | 355.2 | 371.7 | 291.3
1328 | 1230 | 527.1 | 450.7 | 490.7 | 450.9 | 408.3 | 367.6 | 355.6 | 355.4 | 371.8 | 291.4
1329 | 1231 | 527.1 | 450.8 | 490.7 | 451 | 408.5 | 367.8 | 355.9 | 355.7 | 371.9 | 291.5
1330 | 1232 | 527.1 | 450.8 | 490.8 | 451 | 408.6 | 368 | 356.1 | 355.9 | 372 | 291.7
1331 | 1233 | 527 | 450.9 | 490.8 | 451.1 | 408.8 | 368.2 | 356.3 | 356.1 | 372.1 | 292
1332 | 1234 | 527 | 450.9 | 490.8 | 451.2 | 409 | 368.4 | 356.5 | 356.4 | 372.3 | 292.1
1333 | 1235 | 527 | 451 | 490.9 | 451.2 | 409.1 | 368.6 | 356.8 | 356.6 | 372.4 | 292.3
1334 | 1236 | 527 | 451 | 490.9 | 451.3 | 409.3 | 368.9 | 357 | 356.8 | 372.5 | 292.5
1335 | 1237 | 527 | 451.1 | 491 | 451.3 | 409.4 | 369.1 | 357.3 | 357 | 372.7 | 292.6
1336 | 1238 | 526.9 | 451.1 | 491 | 451.4 | 409.6 | 369.3 | 357.5 | 357.2 | 372.8 | 292.7
1337 | 1239 | 526.9 | 451.2 | 491 | 451.4 | 409.7 | 369.5 | 357.8 | 357.5 | 372.9 | 292.9
1338 | 1240 | 526.9 | 451.2 | 491 | 451.5 | 409.9 | 369.8 | 358 | 357.7 | 373.1 | 293.1
1339 | 1241 | 526.9 | 451.3 | 491.1 | 451.5 | 410 | 370 | 358.3 | 358 | 373.2 | 293.2
1340 | 1242 | 526.9 | 451.3 | 491.1 | 451.6 | 410.1 | 370.2 | 358.5 | 358.2 | 373.3 | 293.3
1341 | 1243 | 526.9 | 451.4 | 491.2 | 451.6 | 410.3 | 370.5 | 358.7 | 358.4 | 373.5 | 293.4
1342 | 1244 | 526.9 | 451.4 | 491.2 | 451.7 | 410.4 | 370.7 | 359 | 358.6 | 373.6 | 293.5
1343 | 1245 | 526.9 | 451.5 | 491.3 | 451.7 | 410.5 | 371 | 359.2 | 358.8 | 373.7 | 293.7
1344 | 1246 | 526.9 | 451.5 | 491.3 | 451.8 | 410.7 | 371.4 | 359.4 | 359 | 373.9 | 293.9
1345 | 1247 | 526.9 | 451.6 | 491.4 | 451.9 | 410.8 | 371.7 | 359.7 | 359.2 | 374 | 294
1346 | 1248 | 526.8 | 451.6 | 491.4 | 451.9 | 410.9 | 371.9 | 359.9 | 359.4 | 374.2 | 294
1347 | 1249 | 526.8 | 451.7 | 491.4 | 452 | 411 | 372.3 | 360.1 | 359.7 | 374.3 | 294.2
1348 | 1250 | 526.8 | 451.7 | 491.5 | 452 | 411.2 | 372.6 | 360.4 | 359.9 | 374.4 | 294.3
1349 | 1251 | 526.8 | 451.8 | 491.5 | 452.1 | 411.3 | 372.9 | 360.6 | 360.2 | 374.6 | 294.5
1350 | 1252 | 526.8 | 451.8 | 491.6 | 452.1 | 411.4 | 373.2 | 360.9 | 360.4 | 374.7 | 294.6
1351 | 1253 | 526.7 | 451.9 | 491.6 | 452.2 | 411.5 | 373.7 | 361.1 | 360.6 | 374.8 | 294.8
1352 | 1254 | 526.7 | 451.9 | 491.6 | 452.2 | 411.6 | 374.4 | 361.4 | 360.9 | 375 | 295
1353 | 1255 | 526.6 | 452 | 491.6 | 452.3 | 411.7 | 375.1 | 361.6 | 361.1 | 375.1 | 295.2
1354 | 1256 | 526.6 | 452 | 491.7 | 452.3 | 411.8 | 375.8 | 361.9 | 361.4 | 375.2 | 295.3
1355 | 1257 | 526.5 | 452.1 | 491.7 | 452.4 | 411.9 | 376.6 | 362.1 | 361.6 | 375.4 | 295.5
1356 | 1258 | 526.5 | 452.1 | 491.7 | 452.4 | 412 | 377.1 | 362.4 | 361.8 | 375.5 | 295.6
1357 | 1259 | 526.5 | 452.2 | 491.8 | 452.5 | 412.1 | 377.4 | 362.7 | 362 | 375.6 | 295.8
1358 | 1260 | 526.4 | 452.2 | 491.8 | 452.5 | 412.2 | 377.1 | 362.9 | 362.2 | 375.8 | 295.9
1359 | 1261 | 526.4 | 452.3 | 491.9 | 452.6 | 412.3 | 377 | 363.2 | 362.4 | 375.9 | 296.1
1360 | 1262 | 526.4 | 452.3 | 491.9 | 452.6 | 412.4 | 377.2 | 363.5 | 362.7 | 376 | 296.3
1361 | 1263 | 526.4 | 452.3 | 491.9 | 452.7 | 412.4 | 377.5 | 363.8 | 362.9 | 376.1 | 296.5
1362 | 1264 | 526.3 | 452.4 | 492 | 452.7 | 412.5 | 377.9 | 364 | 363.2 | 376.2 | 296.7
1363 | 1265 | 526.3 | 452.4 | 492 | 452.8 | 412.6 | 378.3 | 364.2 | 363.5 | 376.4 | 296.8
1364 | 1266 | 526.3 | 452.5 | 492.1 | 452.8 | 412.7 | 378.6 | 364.5 | 363.7 | 376.5 | 296.9
1365 | 1267 | 526.3 | 452.5 | 492.1 | 452.9 | 412.8 | 378.8 | 364.7 | 363.9 | 376.6 | 297.1
1366 | 1268 | 526.3 | 452.6 | 492.1 | 452.9 | 412.8 | 379.1 | 365 | 364.1 | 376.8 | 297.3
1367 | 1269 | 526.4 | 452.6 | 492.2 | 453 | 412.9 | 379.5 | 365.3 | 364.4 | 376.9 | 297.5
1368 | 1270 | 526.4 | 452.7 | 492.2 | 453 | 413 | 379.9 | 365.5 | 364.7 | 377 | 297.6
1369 | 1271 | 526.4 | 452.7 | 492.3 | 453.1 | 413.1 | 380.2 | 365.8 | 365 | 377.1 | 297.8
1370 | 1272 | 526.4 | 452.8 | 492.3 | 453.2 | 413.1 | 380.7 | 366 | 365.3 | 377.2 | 298
1371 | 1273 | 526.4 | 452.8 | 492.4 | 453.2 | 413.2 | 381.1 | 366.3 | 365.5 | 377.4 | 298.2
1372 | 1274 | 526.4 | 452.9 | 492.4 | 453.3 | 413.2 | 381.5 | 366.6 | 365.7 | 377.5 | 298.4
1373 | 1275 | 526.4 | 452.9 | 492.4 | 453.3 | 413.3 | 381.8 | 366.8 | 366 | 377.6 | 298.6
1374 | 1276 | 526.4 | 453 | 492.5 | 453.4 | 413.3 | 382.2 | 367.1 | 366.3 | 377.7 | 298.7
1375 | 1277 | 526.4 | 453 | 492.5 | 453.4 | 413.4 | 382.5 | 367.4 | 366.5 | 377.8 | 298.9
1376 | 1278 | 526.3 | 453.1 | 492.5 | 453.5 | 413.4 | 382.9 | 367.6 | 366.8 | 378 | 299.1
1377 | 1279 | 526.3 | 453.1 | 492.5 | 453.5 | 413.4 | 383.3 | 367.9 | 367 | 378.1 | 299.2
1378 | 1280 | 526.3 | 453.2 | 492.6 | 453.6 | 413.4 | 383.6 | 368.2 | 367.3 | 378.2 | 299.2
1379 | 1281 | 526.3 | 453.2 | 492.6 | 453.6 | 413.3 | 384 | 368.5 | 367.6 | 378.3 | 299.4
1380 | 1282 | 526.4 | 453.3 | 492.6 | 453.7 | 413.2 | 384.3 | 368.8 | 367.8 | 378.4 | 299.6
1381 | 1283 | 526.4 | 453.3 | 492.7 | 453.7 | 413 | 384.6 | 369.1 | 368.1 | 378.5 | 299.8
1382 | 1284 | 526.4 | 453.4 | 492.7 | 453.8 | 412.9 | 384.9 | 369.4 | 368.3 | 378.6 | 300
1383 | 1285 | 526.4 | 453.4 | 492.7 | 453.9 | 412.9 | 385.3 | 369.7 | 368.6 | 378.7 | 300.2
1384 | 1286 | 526.4 | 453.5 | 492.8 | 453.9 | 412.9 | 385.6 | 370 | 368.9 | 378.8 | 300.4
1385 | 1287 | 526.4 | 453.5 | 492.9 | 453.9 | 412.9 | 385.9 | 370.3 | 369.2 | 378.9 | 300.6
1386 | 1288 | 526.4 | 453.6 | 492.9 | 454 | 412.9 | 386.2 | 370.6 | 369.5 | 379 | 300.8
1387 | 1289 | 526.5 | 453.6 | 493 | 454.1 | 413 | 386.5 | 370.9 | 369.7 | 379.1 | 301
1388 | 1290 | 526.5 | 453.6 | 493 | 454.1 | 413.1 | 386.8 | 371.2 | 370 | 379.2 | 301.2
1389 | 1291 | 526.5 | 453.7 | 493 | 454.2 | 413.2 | 387.1 | 371.5 | 370.2 | 379.3 | 301.4
1390 | 1292 | 526.6 | 453.7 | 493.1 | 454.2 | 413.3 | 387.4 | 371.8 | 370.5 | 379.4 | 301.6
1391 | 1293 | 526.6 | 453.8 | 493.1 | 454.3 | 413.4 | 387.7 | 372.1 | 370.7 | 379.5 | 301.8
1392 | 1294 | 526.6 | 453.8 | 493.2 | 454.3 | 413.6 | 388 | 372.4 | 371 | 379.6 | 302.1
1393 | 1295 | 526.6 | 453.9 | 493.2 | 454.4 | 413.7 | 388.3 | 372.6 | 371.2 | 379.7 | 302.3
1394 | 1296 | 526.7 | 453.9 | 493.3 | 454.4 | 413.8 | 388.5 | 372.9 | 371.5 | 379.8 | 302.5
1395 | 1297 | 526.7 | 454 | 493.3 | 454.5 | 414 | 388.8 | 373.2 | 371.7 | 379.9 | 302.7
1396 | 1298 | 526.7 | 454 | 493.4 | 454.5 | 414.1 | 389.1 | 373.5 | 372 | 380 | 302.9
1397 | 1299 | 526.6 | 454.1 | 493.4 | 454.6 | 414.3 | 389.4 | 373.8 | 372.2 | 380.2 | 303.2
1398 | 1300 | 526.6 | 454.1 | 493.4 | 454.6 | 414.4 | 389.6 | 374.1 | 372.5 | 380.2 | 303.3
1399 | 1301 | 526.6 | 454.2 | 493.4 | 454.7 | 414.5 | 389.9 | 374.3 | 372.8 | 380.3 | 303.6
1400 | 1302 | 526.6 | 454.2 | 493.5 | 454.7 | 414.7 | 390.2 | 374.6 | 373 | 380.5 | 303.8
1401 | 1303 | 526.7 | 454.2 | 493.5 | 454.8 | 414.8 | 390.4 | 374.9 | 373.3 | 380.6 | 304
1402 | 1304 | 526.7 | 454.3 | 493.5 | 454.8 | 414.9 | 390.6 | 375.2 | 373.5 | 380.7 | 304.2
1403 | 1305 | 526.7 | 454.4 | 493.6 | 454.9 | 415.1 | 390.9 | 375.5 | 373.9 | 380.8 | 304.3
1404 | 1306 | 526.7 | 454.4 | 493.6 | 454.9 | 415.2 | 391.2 | 375.8 | 374.2 | 380.9 | 304.5
1405 | 1307 | 526.6 | 454.4 | 493.6 | 455 | 415.3 | 391.4 | 376.1 | 374.4 | 381.1 | 304.7
1406 | 1308 | 526.6 | 454.5 | 493.7 | 455 | 415.4 | 391.6 | 376.4 | 374.7 | 381.2 | 304.9
1407 | 1309 | 526.6 | 454.5 | 493.7 | 455.1 | 415.6 | 391.9 | 376.7 | 375 | 381.4 | 305.1
1408 | 1310 | 526.6 | 454.6 | 493.7 | 455.1 | 415.8 | 392.1 | 376.9 | 375.2 | 381.5 | 305.3
1409 | 1311 | 526.6 | 454.6 | 493.8 | 455.2 | 416 | 392.3 | 377.2 | 375.5 | 381.7 | 305.5
1410 | 1312 | 526.6 | 454.7 | 493.8 | 455.2 | 416.2 | 392.5 | 377.5 | 375.8 | 381.9 | 305.6
1411 | 1313 | 526.6 | 454.7 | 493.8 | 455.3 | 416.4 | 392.7 | 377.8 | 376.1 | 382.1 | 305.8
1412 | 1314 | 526.6 | 454.8 | 493.8 | 455.3 | 416.5 | 392.8 | 378.1 | 376.3 | 382.3 | 306
1413 | 1315 | 526.5 | 454.8 | 493.8 | 455.4 | 416.7 | 393 | 378.3 | 376.6 | 382.4 | 306.2
1414 | 1316 | 526.6 | 454.9 | 493.9 | 455.5 | 416.9 | 393.2 | 378.6 | 376.8 | 382.6 | 306.4
1415 | 1317 | 526.6 | 454.9 | 494 | 455.5 | 417.1 | 393.4 | 378.9 | 377.2 | 382.7 | 306.6
1416 | 1318 | 526.6 | 455 | 494 | 455.5 | 417.1 | 393.5 | 379.2 | 377.4 | 382.9 | 306.7
1417 | 1319 | 526.6 | 455 | 494 | 455.6 | 417.2 | 393.7 | 379.5 | 377.7 | 383 | 306.9
1418 | 1320 | 526.6 | 455.1 | 494 | 455.6 | 417.3 | 393.8 | 379.7 | 378 | 383.2 | 307.1
1419 | 1321 | 526.5 | 455.1 | 494 | 455.7 | 417.2 | 394 | 380 | 378.2 | 383.4 | 307.3
1420 | 1322 | 526.5 | 455.2 | 494.1 | 455.7 | 417.2 | 394.2 | 380.3 | 378.4 | 383.5 | 307.4
1421 | 1323 | 526.5 | 455.2 | 494.1 | 455.8 | 417.3 | 394.3 | 380.6 | 378.7 | 383.7 | 307.6
1422 | 1324 | 526.5 | 455.3 | 494.1 | 455.8 | 417.3 | 394.5 | 380.9 | 379 | 383.9 | 307.8
1423 | 1325 | 526.5 | 455.3 | 494.1 | 455.9 | 417.3 | 394.7 | 381.1 | 379.4 | 384 | 307.9
1424 | 1326 | 526.5 | 455.3 | 494.2 | 455.9 | 417.4 | 394.9 | 381.4 | 379.7 | 384.2 | 308.1
1425 | 1327 | 526.5 | 455.4 | 494.2 | 456 | 417.5 | 395.2 | 381.7 | 380.1 | 384.3 | 308.3
1426 | 1328 | 526.5 | 455.4 | 494.3 | 456 | 417.5 | 395.4 | 382 | 380.3 | 384.5 | 308.4
1427 | 1329 | 526.5 | 455.5 | 494.3 | 456.1 | 417.6 | 395.6 | 382.2 | 380.7 | 384.7 | 308.6
1428 | 1330 | 526.5 | 455.5 | 494.3 | 456.1 | 417.6 | 395.9 | 382.5 | 381 | 384.8 | 308.8
1429 | 1331 | 526.6 | 455.6 | 494.3 | 456.2 | 417.7 | 396.1 | 382.7 | 381.4 | 385 | 308.9
1430 | 1332 | 526.6 | 455.6 | 494.3 | 456.2 | 417.7 | 396.3 | 383 | 381.7 | 385.2 | 309.1
1431 | 1333 | 526.6 | 455.7 | 494.3 | 456.3 | 417.8 | 396.5 | 383.2 | 382 | 385.4 | 309.2
1432 | 1334 | 526.6 | 455.7 | 494.4 | 456.3 | 417.9 | 396.8 | 383.4 | 382.4 | 385.6 | 309.4
1433 | 1335 | 526.6 | 455.8 | 494.5 | 456.4 | 418 | 397 | 383.6 | 382.8 | 385.8 | 309.6
1434 | 1336 | 526.6 | 455.8 | 494.5 | 456.4 | 418.1 | 397.2 | 383.7 | 383.1 | 386 | 309.8
1435 | 1337 | 526.6 | 455.9 | 494.5 | 456.5 | 418.2 | 397.4 | 383.9 | 383.4 | 386.3 | 310
1436 | 1338 | 526.6 | 455.9 | 494.5 | 456.5 | 418.3 | 397.6 | 384.1 | 383.8 | 386.5 | 310.2
1437 | 1339 | 526.6 | 455.9 | 494.5 | 456.5 | 418.4 | 397.8 | 384.3 | 384.2 | 386.7 | 310.3
1438 | 1340 | 526.6 | 456 | 494.5 | 456.6 | 418.5 | 398.1 | 384.5 | 384.6 | 386.9 | 310.5
1439 | 1341 | 526.7 | 456 | 494.6 | 456.6 | 418.6 | 398.3 | 384.6 | 385 | 387.1 | 310.7
1440 | 1342 | 526.7 | 456.1 | 494.6 | 456.7 | 418.8 | 398.5 | 384.8 | 385.4 | 387.3 | 310.8
1441 | 1343 | 526.7 | 456.1 | 494.6 | 456.7 | 418.9 | 398.7 | 384.9 | 385.8 | 387.5 | 311
1442 | 1344 | 526.7 | 456.2 | 494.6 | 456.8 | 419.1 | 398.9 | 385.1 | 386.3 | 387.7 | 311.2
1443 | 1345 | 526.7 | 456.2 | 494.6 | 456.8 | 419.2 | 399.1 | 385.2 | 386.7 | 387.9 | 311.3
1444 | 1346 | 526.7 | 456.2 | 494.7 | 456.9 | 419.4 | 399.3 | 385.3 | 387.1 | 388.2 | 311.5
1445 | 1347 | 526.8 | 456.3 | 494.7 | 456.9 | 419.6 | 399.5 | 385.5 | 387.4 | 388.4 | 311.7
1446 | 1348 | 526.8 | 456.3 | 494.7 | 456.9 | 419.7 | 399.7 | 385.7 | 387.8 | 388.6 | 311.9
1447 | 1349 | 526.8 | 456.4 | 494.8 | 457 | 419.9 | 400 | 385.8 | 388.1 | 388.8 | 312
1448 | 1350 | 526.8 | 456.4 | 494.8 | 457.1 | 420.1 | 400.2 | 386 | 388.4 | 389 | 312.2
1449 | 1351 | 526.7 | 456.5 | 494.8 | 457.1 | 420.3 | 400.4 | 386.2 | 388.8 | 389.3 | 312.4
1450 | 1352 | 526.7 | 456.5 | 494.8 | 457.1 | 420.5 | 400.6 | 386.3 | 389.2 | 389.5 | 312.6
1451 | 1353 | 526.7 | 456.6 | 494.9 | 457.1 | 420.6 | 400.8 | 386.5 | 389.5 | 389.7 | 312.7
1452 | 1354 | 526.7 | 456.6 | 494.9 | 457.2 | 420.8 | 401 | 386.6 | 389.8 | 389.9 | 312.9
1453 | 1355 | 526.7 | 456.7 | 494.9 | 457.2 | 421 | 401.2 | 386.8 | 390.2 | 390.1 | 313.1
1454 | 1356 | 526.7 | 456.7 | 494.9 | 457.3 | 421.2 | 401.4 | 387 | 390.5 | 390.3 | 313.2
1455 | 1357 | 526.7 | 456.7 | 495 | 457.3 | 421.4 | 401.6 | 387.1 | 390.8 | 390.5 | 313.4
1456 | 1358 | 526.7 | 456.8 | 494.9 | 457.4 | 421.6 | 401.9 | 387.3 | 391.1 | 390.7 | 313.6
1457 | 1359 | 526.7 | 456.8 | 495 | 457.4 | 421.7 | 402.1 | 387.5 | 391.4 | 390.9 | 313.7
1458 | 1360 | 526.7 | 456.9 | 495 | 457.4 | 421.9 | 402.3 | 387.7 | 391.7 | 391.1 | 313.9
1459 | 1361 | 526.7 | 456.9 | 495.1 | 457.5 | 422.2 | 402.5 | 387.8 | 392.1 | 391.3 | 314
1460 | 1362 | 526.7 | 457 | 495.1 | 457.5 | 422.4 | 402.7 | 388 | 392.4 | 391.6 | 314.2
1461 | 1363 | 526.7 | 457 | 495.1 | 457.5 | 422.5 | 402.9 | 388.2 | 392.8 | 391.8 | 314.4
1462 | 1364 | 526.7 | 457 | 495.1 | 457.6 | 422.7 | 403.1 | 388.3 | 393 | 392 | 314.5
1463 | 1365 | 526.7 | 457.1 | 495.1 | 457.6 | 422.9 | 403.4 | 388.5 | 393.3 | 392.2 | 314.7
1464 | 1366 | 526.7 | 457.1 | 495.1 | 457.7 | 423 | 403.6 | 388.7 | 393.5 | 392.4 | 314.8
1465 | 1367 | 526.7 | 457.2 | 495.2 | 457.7 | 423.1 | 403.8 | 388.9 | 393.8 | 392.6 | 315
1466 | 1368 | 526.7 | 457.2 | 495.2 | 457.7 | 423.2 | 404 | 389 | 394.2 | 392.8 | 315.2
1467 | 1369 | 526.7 | 457.2 | 495.2 | 457.8 | 423.4 | 404.2 | 389.2 | 394.6 | 393 | 315.3
1468 | 1370 | 526.7 | 457.3 | 495.2 | 457.8 | 423.6 | 404.4 | 389.3 | 394.9 | 393.2 | 315.5
1469 | 1371 | 526.7 | 457.3 | 495.3 | 457.9 | 423.7 | 404.6 | 389.5 | 395.1 | 393.4 | 315.7
1470 | 1372 | 526.7 | 457.4 | 495.3 | 457.9 | 423.8 | 404.9 | 389.7 | 395.4 | 393.6 | 315.8
1471 | 1373 | 526.7 | 457.4 | 495.3 | 457.9 | 424 | 405.1 | 389.9 | 395.8 | 393.8 | 316
1472 | 1374 | 526.7 | 457.5 | 495.3 | 458 | 424.1 | 405.3 | 390 | 396 | 394 | 316.2
1473 | 1375 | 526.6 | 457.5 | 495.4 | 458 | 424.3 | 405.5 | 390.2 | 396.3 | 394.2 | 316.3
1474 | 1376 | 526.6 | 457.5 | 495.4 | 458.1 | 424.5 | 405.7 | 390.4 | 396.6 | 394.4 | 316.5
1475 | 1377 | 526.6 | 457.6 | 495.4 | 458.1 | 424.6 | 405.9 | 390.5 | 396.9 | 394.6 | 316.7
1476 | 1378 | 526.6 | 457.6 | 495.4 | 458.1 | 424.8 | 406.1 | 390.7 | 397.1 | 394.7 | 316.8
1477 | 1379 | 526.6 | 457.7 | 495.5 | 458.2 | 424.9 | 406.4 | 390.9 | 397.3 | 394.8 | 317
1478 | 1380 | 526.6 | 457.7 | 495.5 | 458.2 | 425.1 | 406.6 | 391.1 | 397.7 | 394.9 | 317.2
1479 | 1381 | 526.6 | 457.8 | 495.5 | 458.3 | 425.2 | 406.8 | 391.3 | 398 | 395 | 317.3
1480 | 1382 | 526.6 | 457.8 | 495.5 | 458.3 | 425.4 | 407 | 391.5 | 398.2 | 395.1 | 317.5
1481 | 1383 | 526.5 | 457.8 | 495.6 | 458.4 | 425.5 | 407.2 | 391.6 | 398.5 | 395.2 | 317.7
1482 | 1384 | 526.5 | 457.9 | 495.6 | 458.4 | 425.6 | 407.4 | 391.8 | 398.8 | 395.3 | 317.8
1483 | 1385 | 526.5 | 457.9 | 495.6 | 458.4 | 425.8 | 407.6 | 392 | 399 | 395.4 | 318
1484 | 1386 | 526.5 | 458 | 495.6 | 458.5 | 425.9 | 407.9 | 392.2 | 399.3 | 395.5 | 318.1
1485 | 1387 | 526.4 | 458 | 495.7 | 458.5 | 426.1 | 408.1 | 392.4 | 399.6 | 395.6 | 318.3
1486 | 1388 | 526.4 | 458 | 495.7 | 458.5 | 426.3 | 408.3 | 392.6 | 399.8 | 395.7 | 318.5
1487 | 1389 | 526.4 | 458.1 | 495.7 | 458.6 | 426.4 | 408.5 | 392.8 | 400 | 395.8 | 318.6
1488 | 1390 | 526.4 | 458.1 | 495.7 | 458.6 | 426.6 | 408.7 | 393 | 400.2 | 395.9 | 318.8
1489 | 1391 | 526.4 | 458.2 | 495.8 | 458.7 | 426.8 | 408.9 | 393.2 | 400.4 | 396.1 | 319
1490 | 1392 | 526.4 | 458.2 | 495.8 | 458.7 | 427 | 409.1 | 393.4 | 400.7 | 396.1 | 319.1
1491 | 1393 | 526.4 | 458.2 | 495.8 | 458.7 | 427.2 | 409.4 | 393.6 | 400.9 | 396.2 | 319.3
1492 | 1394 | 526.3 | 458.3 | 495.9 | 458.8 | 427.4 | 409.6 | 393.8 | 401.2 | 396.3 | 319.5
1493 | 1395 | 526.3 | 458.3 | 495.9 | 458.8 | 427.5 | 409.8 | 394 | 401.4 | 396.4 | 319.6
1494 | 1396 | 526.3 | 458.4 | 495.9 | 458.9 | 427.7 | 410 | 394.3 | 401.6 | 396.5 | 319.8
1495 | 1397 | 526.4 | 458.4 | 496 | 458.9 | 427.8 | 410.2 | 394.4 | 401.9 | 396.6 | 320
1496 | 1398 | 526.4 | 458.4 | 495.9 | 458.9 | 428 | 410.4 | 394.7 | 402.1 | 396.7 | 320.1
1497 | 1399 | 526.4 | 458.5 | 495.9 | 459 | 428.1 | 410.6 | 394.9 | 402.3 | 396.8 | 320.3
1498 | 1400 | 526.4 | 458.5 | 495.9 | 459 | 428.2 | 410.9 | 395 | 402.5 | 396.9 | 320.4
1499 | 1401 | 526.3 | 458.6 | 496 | 459.1 | 428.4 | 411.1 | 395.3 | 402.7 | 396.9 | 320.6
1500 | 1402 | 526.3 | 458.6 | 496 | 459.1 | 428.5 | 411.3 | 395.5 | 402.9 | 397 | 320.7
1501 | 1403 | 526.3 | 458.6 | 496.1 | 459.1 | 428.7 | 411.5 | 395.7 | 403.1 | 397.1 | 320.9
1502 | 1404 | 526.3 | 458.7 | 496.1 | 459.2 | 428.8 | 411.7 | 395.9 | 403.3 | 397.2 | 321.1
1503 | 1405 | 526.3 | 458.7 | 496.1 | 459.2 | 428.9 | 411.9 | 396.1 | 403.5 | 397.2 | 321.2
1504 | 1406 | 526.3 | 458.8 | 496.1 | 459.3 | 429.1 | 412.1 | 396.3 | 403.8 | 397.3 | 321.4
1505 | 1407 | 526.3 | 458.8 | 496.2 | 459.3 | 429.2 | 412.3 | 396.5 | 403.9 | 397.3 | 321.6
1506 | 1408 | 526.3 | 458.8 | 496.2 | 459.3 | 429.4 | 412.6 | 396.7 | 404.1 | 397.4 | 321.7
1507 | 1409 | 526.4 | 458.9 | 496.2 | 459.4 | 429.5 | 412.8 | 396.9 | 404.3 | 397.5 | 321.9
1508 | 1410 | 526.4 | 458.9 | 496.2 | 459.4 | 429.6 | 413 | 397.1 | 404.4 | 397.5 | 322.1
1509 | 1411 | 526.4 | 458.9 | 496.3 | 459.5 | 429.7 | 413.2 | 397.3 | 404.6 | 397.6 | 322.3
1510 | 1412 | 526.4 | 459 | 496.3 | 459.5 | 429.9 | 413.4 | 397.5 | 404.8 | 397.6 | 322.4
1511 | 1413 | 526.3 | 459 | 496.3 | 459.6 | 430 | 413.6 | 397.7 | 404.9 | 397.7 | 322.6
1512 | 1414 | 526.4 | 459.1 | 496.3 | 459.6 | 430.1 | 413.8 | 398 | 405 | 397.7 | 322.8
1513 | 1415 | 526.3 | 459.1 | 496.3 | 459.6 | 430.2 | 414 | 398.2 | 405.2 | 397.8 | 322.9
1514 | 1416 | 526.3 | 459.2 | 496.3 | 459.7 | 430.3 | 414.2 | 398.4 | 405.4 | 397.8 | 323.1
1515 | 1417 | 526.3 | 459.2 | 496.4 | 459.7 | 430.4 | 414.4 | 398.6 | 405.6 | 397.8 | 323.2
1516 | 1418 | 526.3 | 459.2 | 496.4 | 459.7 | 430.4 | 414.6 | 398.8 | 405.7 | 397.9 | 323.4
1517 | 1419 | 526.3 | 459.3 | 496.4 | 459.8 | 430.5 | 414.8 | 399 | 405.9 | 397.9 | 323.6
1518 | 1420 | 526.3 | 459.3 | 496.4 | 459.8 | 430.6 | 415 | 399.2 | 406 | 397.9 | 323.7
1519 | 1421 | 526.3 | 459.3 | 496.5 | 459.9 | 430.7 | 415.2 | 399.4 | 406.2 | 398 | 323.9
1520 | 1422 | 526.3 | 459.4 | 496.5 | 459.9 | 430.8 | 415.4 | 399.7 | 406.3 | 398 | 324.1
1521 | 1423 | 526.3 | 459.4 | 496.5 | 459.9 | 430.9 | 415.6 | 399.9 | 406.5 | 398 | 324.2
1522 | 1424 | 526.3 | 459.5 | 496.5 | 460 | 431 | 415.7 | 400.1 | 406.6 | 398.1 | 324.4
1523 | 1425 | 526.3 | 459.5 | 496.6 | 460 | 431.1 | 415.9 | 400.3 | 406.8 | 398.1 | 324.6
1524 | 1426 | 526.3 | 459.5 | 496.6 | 460.1 | 431.2 | 416.1 | 400.5 | 406.9 | 398.1 | 324.7
1525 | 1427 | 526.3 | 459.6 | 496.6 | 460.1 | 431.2 | 416.3 | 400.7 | 407.1 | 398.1 | 324.9
1526 | 1428 | 526.3 | 459.6 | 496.6 | 460.1 | 431.4 | 416.4 | 400.9 | 407.1 | 398.1 | 325
1527 | 1429 | 526.3 | 459.7 | 496.7 | 460.2 | 431.6 | 416.6 | 401.1 | 407.3 | 398.2 | 325.2
1528 | 1430 | 526.3 | 459.7 | 496.7 | 460.2 | 431.7 | 416.8 | 401.3 | 407.4 | 398.2 | 325.4
1529 | 1431 | 526.3 | 459.7 | 496.7 | 460.2 | 431.8 | 416.9 | 401.5 | 407.6 | 398.2 | 325.5
1530 | 1432 | 526.3 | 459.8 | 496.7 | 460.3 | 431.9 | 417.1 | 401.7 | 407.7 | 398.3 | 325.7
1531 | 1433 | 526.4 | 459.8 | 496.7 | 460.3 | 432 | 417.2 | 401.9 | 407.9 | 398.3 | 325.8
1532 | 1434 | 526.4 | 459.8 | 496.8 | 460.3 | 432.1 | 417.4 | 402.1 | 408.1 | 398.3 | 326
1533 | 1435 | 526.4 | 459.9 | 496.8 | 460.4 | 432.2 | 417.6 | 402.3 | 408.2 | 398.3 | 326.2
1534 | 1436 | 526.4 | 459.9 | 496.9 | 460.4 | 432.3 | 417.8 | 402.5 | 408.3 | 398.3 | 326.3
1535 | 1437 | 526.4 | 460 | 496.9 | 460.4 | 432.4 | 418 | 402.7 | 408.5 | 398.4 | 326.5
1536 | 1438 | 526.3 | 460 | 496.9 | 460.5 | 432.5 | 418.1 | 403 | 408.7 | 398.4 | 326.7
1537 | 1439 | 526.3 | 460 | 496.9 | 460.5 | 432.6 | 418.3 | 403.1 | 408.8 | 398.4 | 326.8
1538 | 1440 | 526.3 | 460.1 | 496.9 | 460.6 | 432.7 | 418.5 | 403.3 | 409 | 398.4 | 327
1539 | 1441 | 526.2 | 460.1 | 496.9 | 460.6 | 432.9 | 418.7 | 403.5 | 409.1 | 398.4 | 327.2
1540 | 1442 | 526.2 | 460.2 | 497 | 460.6 | 432.9 | 418.8 | 403.7 | 409.2 | 398.5 | 327.3
1541 | 1443 | 526.2 | 460.2 | 497 | 460.7 | 433.1 | 419 | 403.9 | 409.4 | 398.5 | 327.5
1542 | 1444 | 526.2 | 460.2 | 497 | 460.7 | 433.1 | 419.2 | 404.1 | 409.7 | 398.5 | 327.7
1543 | 1445 | 526.2 | 460.3 | 497.1 | 460.7 | 433.2 | 419.4 | 404.3 | 409.8 | 398.5 | 327.8
1544 | 1446 | 526.2 | 460.3 | 497.1 | 460.8 | 433.2 | 419.5 | 404.5 | 409.9 | 398.6 | 328
1545 | 1447 | 526.2 | 460.4 | 497.1 | 460.8 | 433.3 | 419.7 | 404.7 | 410 | 398.6 | 328.1
1546 | 1448 | 526.2 | 460.4 | 497.1 | 460.8 | 433.4 | 419.8 | 404.9 | 410.2 | 398.6 | 328.3
1547 | 1449 | 526.2 | 460.4 | 497.1 | 460.9 | 433.5 | 420 | 405.1 | 410.3 | 398.7 | 328.5
1548 | 1450 | 526.2 | 460.5 | 497.1 | 460.9 | 433.6 | 420.2 | 405.3 | 410.6 | 398.7 | 328.6
1549 | 1451 | 526.1 | 460.5 | 497.2 | 461 | 433.6 | 420.4 | 405.5 | 410.7 | 398.7 | 328.8
1550 | 1452 | 526.1 | 460.5 | 497.2 | 461 | 433.6 | 420.5 | 405.7 | 410.9 | 398.8 | 328.9
1551 | 1453 | 526 | 460.6 | 497.2 | 461 | 433.7 | 420.7 | 405.9 | 411 | 398.8 | 329.1
1552 | 1454 | 526 | 460.6 | 497.2 | 461.1 | 433.8 | 420.9 | 406.1 | 411.2 | 398.8 | 329.3
1553 | 1455 | 526 | 460.7 | 497.2 | 461.1 | 433.8 | 421 | 406.2 | 411.3 | 398.9 | 329.4
1554 | 1456 | 526 | 460.7 | 497.2 | 461.2 | 433.9 | 421.2 | 406.4 | 411.5 | 398.9 | 329.6
1555 | 1457 | 526 | 460.7 | 497.2 | 461.2 | 433.9 | 421.4 | 406.6 | 411.7 | 399 | 329.7
1556 | 1458 | 526 | 460.8 | 497.3 | 461.2 | 434 | 421.5 | 406.8 | 411.8 | 399 | 329.8
1557 | 1459 | 526 | 460.8 | 497.3 | 461.3 | 434 | 421.7 | 407 | 412 | 399.1 | 330
1558 | 1460 | 526 | 460.9 | 497.3 | 461.3 | 434.1 | 421.8 | 407.1 | 412.2 | 399.1 | 330.2
1559 | 1461 | 526 | 460.9 | 497.3 | 461.3 | 434.1 | 422 | 407.3 | 412.3 | 399.2 | 330.3
1560 | 1462 | 526 | 460.9 | 497.3 | 461.4 | 434.2 | 422.2 | 407.6 | 412.4 | 399.2 | 330.5
1561 | 1463 | 526.1 | 461 | 497.3 | 461.4 | 434.3 | 422.3 | 407.9 | 412.5 | 399.3 | 330.6
1562 | 1464 | 526.1 | 461 | 497.4 | 461.5 | 434.4 | 422.5 | 408.2 | 412.6 | 399.3 | 330.8
1563 | 1465 | 526.1 | 461.1 | 497.4 | 461.5 | 434.5 | 422.7 | 408.4 | 412.8 | 399.4 | 330.9
1564 | 1466 | 526.2 | 461.1 | 497.4 | 461.5 | 434.5 | 422.8 | 408.7 | 413 | 399.5 | 331
1565 | 1467 | 526.2 | 461.1 | 497.4 | 461.6 | 434.5 | 423 | 408.9 | 413.1 | 399.5 | 331.2
1566 | 1468 | 526.3 | 461.2 | 497.5 | 461.6 | 434.5 | 423.2 | 409.1 | 413.3 | 399.6 | 331.4
1567 | 1469 | 526.3 | 461.2 | 497.5 | 461.6 | 434.6 | 423.3 | 409.3 | 413.5 | 399.7 | 331.5
1568 | 1470 | 526.4 | 461.3 | 497.5 | 461.7 | 434.7 | 423.5 | 409.5 | 413.6 | 399.8 | 331.7
1569 | 1471 | 526.4 | 461.3 | 497.5 | 461.7 | 434.8 | 423.7 | 409.8 | 413.8 | 399.8 | 331.8
1570 | 1472 | 526.4 | 461.3 | 497.6 | 461.8 | 434.8 | 423.8 | 410 | 414 | 399.9 | 332
1571 | 1473 | 526.4 | 461.4 | 497.6 | 461.8 | 434.8 | 424 | 410.2 | 414.2 | 400 | 332.1
1572 | 1474 | 526.5 | 461.4 | 497.6 | 461.8 | 434.9 | 424.1 | 410.4 | 414.3 | 400.1 | 332.3
1573 | 1475 | 526.5 | 461.4 | 497.6 | 461.9 | 434.9 | 424.3 | 410.6 | 414.5 | 400.1 | 332.4
1574 | 1476 | 526.6 | 461.5 | 497.7 | 461.9 | 435 | 424.4 | 410.8 | 414.7 | 400.2 | 332.6
1575 | 1477 | 526.6 | 461.5 | 497.7 | 461.9 | 435.1 | 424.6 | 411 | 414.8 | 400.3 | 332.7
1576 | 1478 | 526.6 | 461.6 | 497.7 | 462 | 435.2 | 424.8 | 411.2 | 415 | 400.4 | 332.9
1577 | 1479 | 526.6 | 461.6 | 497.8 | 462 | 435.2 | 424.9 | 411.4 | 415.1 | 400.5 | 333.1
1578 | 1480 | 526.5 | 461.6 | 497.8 | 462.1 | 435.2 | 425.1 | 411.6 | 415.3 | 400.6 | 333.2
1579 | 1481 | 526.6 | 461.7 | 497.8 | 462.1 | 435.2 | 425.2 | 411.8 | 415.4 | 400.6 | 333.4
1580 | 1482 | 526.6 | 461.7 | 497.9 | 462.1 | 435.2 | 425.4 | 412 | 415.6 | 400.7 | 333.5
1581 | 1483 | 526.5 | 461.8 | 497.9 | 462.1 | 435.3 | 425.5 | 412.2 | 415.7 | 400.8 | 333.7
1582 | 1484 | 526.5 | 461.8 | 497.9 | 462.2 | 435.3 | 425.7 | 412.3 | 415.9 | 400.9 | 333.9
1583 | 1485 | 526.5 | 461.8 | 497.9 | 462.2 | 435.3 | 425.9 | 412.5 | 416 | 401 | 334.1
1584 | 1486 | 526.5 | 461.9 | 497.9 | 462.3 | 435.4 | 426 | 412.7 | 416.2 | 401.1 | 334.2
1585 | 1487 | 526.5 | 461.9 | 497.9 | 462.3 | 435.4 | 426.2 | 412.9 | 416.3 | 401.2 | 334.4
1586 | 1488 | 526.5 | 461.9 | 498 | 462.3 | 435.4 | 426.3 | 413.1 | 416.5 | 401.3 | 334.6
1587 | 1489 | 526.4 | 462 | 498 | 462.3 | 435.5 | 426.5 | 413.3 | 416.6 | 401.4 | 334.7
1588 | 1490 | 526.4 | 462 | 498 | 462.4 | 435.5 | 426.6 | 413.5 | 416.8 | 401.5 | 334.9
1589 | 1491 | 526.4 | 462.1 | 498 | 462.4 | 435.5 | 426.8 | 413.7 | 417 | 401.6 | 335.1
1590 | 1492 | 526.4 | 462.1 | 498 | 462.5 | 435.6 | 426.9 | 413.9 | 417.1 | 401.8 | 335.2
1591 | 1493 | 526.4 | 462.1 | 498.1 | 462.5 | 435.6 | 427.1 | 414 | 417.3 | 401.9 | 335.4
1592 | 1494 | 526.4 | 462.2 | 498.1 | 462.5 | 435.7 | 427.2 | 414.2 | 417.5 | 402 | 335.6
1593 | 1495 | 526.4 | 462.2 | 498.1 | 462.6 | 435.6 | 427.4 | 414.4 | 417.6 | 402.1 | 335.7
1594 | 1496 | 526.3 | 462.3 | 498.2 | 462.6 | 435.6 | 427.5 | 414.6 | 417.8 | 402.2 | 335.9
1595 | 1497 | 526.3 | 462.3 | 498.2 | 462.6 | 435.6 | 427.7 | 414.8 | 418 | 402.3 | 336.1
1596 | 1498 | 526.3 | 462.3 | 498.1 | 462.7 | 435.7 | 427.8 | 414.9 | 418.2 | 402.4 | 336.2
1597 | 1499 | 526.2 | 462.4 | 498.1 | 462.7 | 435.7 | 427.9 | 415.1 | 418.3 | 402.5 | 336.4
1598 | 1500 | 526.2 | 462.4 | 498.2 | 462.7 | 435.7 | 428.1 | 415.2 | 418.5 | 402.6 | 336.6
1599 | 1501 | 526.1 | 462.4 | 498.2 | 462.8 | 435.7 | 428.2 | 415.4 | 418.7 | 402.8 | 336.8
1600 | 1502 | 526.1 | 462.5 | 498.2 | 462.8 | 435.7 | 428.3 | 415.5 | 418.9 | 402.9 | 336.9
1601 | 1503 | 526 | 462.5 | 498.3 | 462.9 | 435.7 | 428.5 | 415.7 | 419 | 403 | 337.1
1602 | 1504 | 526 | 462.5 | 498.3 | 462.9 | 435.7 | 428.6 | 415.9 | 419.1 | 403.1 | 337.3
1603 | 1505 | 526 | 462.6 | 498.3 | 462.9 | 435.7 | 428.7 | 416 | 419.3 | 403.2 | 337.5
1604 | 1506 | 526.1 | 462.6 | 498.3 | 463 | 435.7 | 428.9 | 416.1 | 419.4 | 403.4 | 337.6
1605 | 1507 | 526.1 | 462.7 | 498.3 | 463 | 435.8 | 429 | 416.3 | 419.5 | 403.5 | 337.8
1606 | 1508 | 526.1 | 462.7 | 498.4 | 463 | 435.8 | 429.1 | 416.5 | 419.7 | 403.6 | 338
1607 | 1509 | 526.2 | 462.7 | 498.4 | 463 | 435.8 | 429.2 | 416.6 | 419.8 | 403.7 | 338.1
1608 | 1510 | 526.2 | 462.8 | 498.4 | 463.1 | 435.8 | 429.4 | 416.7 | 419.9 | 403.8 | 338.3
1609 | 1511 | 526.2 | 462.8 | 498.4 | 463.1 | 435.9 | 429.5 | 416.9 | 420 | 404 | 338.5
1610 | 1512 | 526.2 | 462.8 | 498.4 | 463.2 | 435.9 | 429.6 | 417 | 420.1 | 404.1 | 338.7
1611 | 1513 | 526.2 | 462.9 | 498.5 | 463.2 | 435.9 | 429.7 | 417.2 | 420.3 | 404.2 | 338.8
1612 | 1514 | 526.3 | 462.9 | 498.5 | 463.2 | 436 | 429.8 | 417.3 | 420.4 | 404.3 | 339
1613 | 1515 | 526.3 | 462.9 | 498.5 | 463.3 | 436.1 | 429.8 | 417.5 | 420.5 | 404.4 | 339.2
1614 | 1516 | 526.3 | 463 | 498.5 | 463.3 | 436.2 | 429.9 | 417.6 | 420.6 | 404.5 | 339.4
1615 | 1517 | 526.3 | 463 | 498.5 | 463.3 | 436.3 | 430 | 417.8 | 420.7 | 404.6 | 339.5
1616 | 1518 | 526.3 | 463.1 | 498.5 | 463.4 | 436.3 | 430.1 | 417.9 | 420.8 | 404.7 | 339.7
1617 | 1519 | 526.3 | 463.1 | 498.6 | 463.4 | 436.4 | 430.2 | 418.1 | 420.9 | 404.8 | 339.9
1618 | 1520 | 526.3 | 463.1 | 498.6 | 463.4 | 436.4 | 430.3 | 418.2 | 421 | 404.9 | 340.1
1619 | 1521 | 526.3 | 463.2 | 498.6 | 463.5 | 436.5 | 430.3 | 418.3 | 421.1 | 405.1 | 340.2
1620 | 1522 | 526.3 | 463.2 | 498.6 | 463.5 | 436.5 | 430.4 | 418.5 | 421.2 | 405.2 | 340.4
1621 | 1523 | 526.3 | 463.2 | 498.6 | 463.5 | 436.6 | 430.5 | 418.6 | 421.3 | 405.3 | 340.6
1622 | 1524 | 526.4 | 463.3 | 498.6 | 463.5 | 436.6 | 430.5 | 418.8 | 421.4 | 405.4 | 340.8
1623 | 1525 | 526.4 | 463.3 | 498.7 | 463.6 | 436.7 | 430.6 | 418.9 | 421.5 | 405.5 | 340.9
1624 | 1526 | 526.4 | 463.4 | 498.7 | 463.6 | 436.9 | 430.6 | 419.1 | 421.6 | 405.7 | 341.1
1625 | 1527 | 526.4 | 463.4 | 498.7 | 463.7 | 437.1 | 430.7 | 419.2 | 421.7 | 405.8 | 341.3
1626 | 1528 | 526.4 | 463.4 | 498.8 | 463.7 | 437.2 | 430.8 | 419.3 | 421.7 | 405.9 | 341.5
1627 | 1529 | 526.4 | 463.5 | 498.8 | 463.7 | 437.3 | 430.9 | 419.5 | 421.8 | 406 | 341.7
1628 | 1530 | 526.4 | 463.5 | 498.8 | 463.7 | 437.5 | 431.1 | 419.6 | 421.8 | 406.1 | 341.8
1629 | 1531 | 526.4 | 463.5 | 498.8 | 463.8 | 437.5 | 431.2 | 419.7 | 421.8 | 406.2 | 342
1630 | 1532 | 526.3 | 463.6 | 498.8 | 463.8 | 437.5 | 431.3 | 419.8 | 421.9 | 406.3 | 342.2
1631 | 1533 | 526.3 | 463.6 | 498.8 | 463.8 | 437.6 | 431.4 | 420 | 421.9 | 406.5 | 342.3
1632 | 1534 | 526.3 | 463.6 | 498.8 | 463.9 | 437.7 | 431.6 | 420.1 | 422 | 406.6 | 342.5
1633 | 1535 | 526.2 | 463.7 | 498.8 | 463.9 | 437.7 | 431.7 | 420.2 | 422 | 406.7 | 342.7
1634 | 1536 | 526.2 | 463.7 | 498.8 | 463.9 | 437.8 | 431.8 | 420.3 | 422.1 | 406.8 | 342.9
1635 | 1537 | 526.2 | 463.7 | 498.9 | 463.9 | 437.9 | 431.9 | 420.5 | 422.1 | 406.9 | 343
1636 | 1538 | 526.2 | 463.8 | 498.9 | 464 | 438 | 432.1 | 420.6 | 422.2 | 407 | 343.2
1637 | 1539 | 526.2 | 463.8 | 498.9 | 464 | 438.1 | 432.2 | 420.7 | 422.3 | 407.1 | 343.3
1638 | 1540 | 526.2 | 463.9 | 498.9 | 464 | 438.2 | 432.3 | 420.8 | 422.4 | 407.2 | 343.5
1639 | 1541 | 526.2 | 463.9 | 498.9 | 464.1 | 438.3 | 432.4 | 420.9 | 422.4 | 407.3 | 343.7
1640 | 1542 | 526.2 | 463.9 | 498.9 | 464.1 | 438.3 | 432.5 | 421.1 | 422.5 | 407.5 | 343.8
1641 | 1543 | 526.2 | 464 | 498.9 | 464.1 | 438.4 | 432.6 | 421.2 | 422.5 | 407.6 | 344
1642 | 1544 | 526.2 | 464 | 498.9 | 464.1 | 438.5 | 432.8 | 421.3 | 422.5 | 407.7 | 344.2
1643 | 1545 | 526.2 | 464 | 499 | 464.2 | 438.6 | 432.9 | 421.4 | 422.6 | 407.8 | 344.3
1644 | 1546 | 526.2 | 464.1 | 499 | 464.2 | 438.6 | 433 | 421.5 | 422.6 | 407.9 | 344.5
1645 | 1547 | 526.2 | 464.1 | 499 | 464.2 | 438.6 | 433.1 | 421.6 | 422.7 | 408 | 344.7
1646 | 1548 | 526.2 | 464.1 | 499 | 464.3 | 438.7 | 433.2 | 421.8 | 422.8 | 408.1 | 344.8
1647 | 1549 | 526.2 | 464.2 | 499.1 | 464.3 | 438.8 | 433.3 | 421.9 | 422.8 | 408.2 | 345
1648 | 1550 | 526.3 | 464.2 | 499.1 | 464.3 | 438.8 | 433.3 | 422 | 422.8 | 408.3 | 345.2
1649 | 1551 | 526.3 | 464.2 | 499.1 | 464.3 | 438.9 | 433.4 | 422.1 | 422.8 | 408.4 | 345.3
1650 | 1552 | 526.3 | 464.3 | 499.1 | 464.4 | 439 | 433.6 | 422.2 | 422.8 | 408.5 | 345.5
1651 | 1553 | 526.4 | 464.3 | 499.1 | 464.4 | 439 | 433.7 | 422.3 | 422.9 | 408.6 | 345.6
1652 | 1554 | 526.3 | 464.4 | 499.1 | 464.4 | 439.1 | 433.8 | 422.4 | 422.9 | 408.7 | 345.8
1653 | 1555 | 526.3 | 464.4 | 499.1 | 464.5 | 439.1 | 433.9 | 422.5 | 422.9 | 408.8 | 346
1654 | 1556 | 526.3 | 464.4 | 499.1 | 464.5 | 439.1 | 434 | 422.6 | 423 | 408.9 | 346.1
1655 | 1557 | 526.3 | 464.5 | 499.2 | 464.5 | 439.2 | 434.1 | 422.8 | 422.9 | 409 | 346.3
1656 | 1558 | 526.3 | 464.5 | 499.2 | 464.6 | 439.3 | 434.2 | 422.9 | 422.9 | 409.1 | 346.5
1657 | 1559 | 526.4 | 464.5 | 499.3 | 464.6 | 439.3 | 434.4 | 423 | 422.9 | 409.2 | 346.6
1658 | 1560 | 526.4 | 464.6 | 499.3 | 464.6 | 439.4 | 434.5 | 423.1 | 422.9 | 409.3 | 346.8
1659 | 1561 | 526.4 | 464.6 | 499.3 | 464.6 | 439.5 | 434.6 | 423.2 | 422.9 | 409.4 | 346.9
1660 | 1562 | 526.4 | 464.6 | 499.2 | 464.7 | 439.5 | 434.7 | 423.3 | 423 | 409.5 | 347.1
1661 | 1563 | 526.4 | 464.7 | 499.2 | 464.7 | 439.6 | 434.8 | 423.4 | 423 | 409.6 | 347.3
1662 | 1564 | 526.4 | 464.7 | 499.3 | 464.7 | 439.7 | 435 | 423.5 | 422.9 | 409.7 | 347.4
1663 | 1565 | 526.4 | 464.7 | 499.3 | 464.7 | 439.8 | 435.1 | 423.6 | 422.9 | 409.7 | 347.6
1664 | 1566 | 526.4 | 464.8 | 499.3 | 464.8 | 439.9 | 435.3 | 423.7 | 423 | 409.8 | 347.7
1665 | 1567 | 526.4 | 464.8 | 499.3 | 464.8 | 440 | 435.4 | 423.8 | 423 | 409.9 | 347.9
1666 | 1568 | 526.4 | 464.8 | 499.3 | 464.8 | 440.1 | 435.6 | 423.9 | 423 | 410 | 348.1
1667 | 1569 | 526.4 | 464.9 | 499.4 | 464.8 | 440.1 | 435.8 | 424 | 423 | 410 | 348.2
1668 | 1570 | 526.4 | 464.9 | 499.4 | 464.9 | 440.2 | 435.9 | 424.1 | 423.1 | 410.1 | 348.4
1669 | 1571 | 526.4 | 464.9 | 499.4 | 464.9 | 440.2 | 436.1 | 424.2 | 423.2 | 410.2 | 348.5
1670 | 1572 | 526.4 | 464.9 | 499.4 | 464.9 | 440.3 | 436.2 | 424.2 | 423.2 | 410.3 | 348.7
1671 | 1573 | 526.4 | 465 | 499.4 | 465 | 440.4 | 436.4 | 424.3 | 423.3 | 410.4 | 348.9
1672 | 1574 | 526.4 | 465 | 499.5 | 465 | 440.4 | 436.5 | 424.4 | 423.3 | 410.5 | 349
1673 | 1575 | 526.3 | 465 | 499.5 | 465 | 440.5 | 436.6 | 424.5 | 423.3 | 410.5 | 349.2
1674 | 1576 | 526.3 | 465.1 | 499.5 | 465 | 440.6 | 436.7 | 424.6 | 423.3 | 410.6 | 349.4
1675 | 1577 | 526.3 | 465.1 | 499.5 | 465.1 | 440.7 | 436.8 | 424.7 | 423.3 | 410.7 | 349.6
1676 | 1578 | 526.2 | 465.1 | 499.5 | 465.1 | 440.8 | 437 | 424.8 | 423.4 | 410.8 | 349.7
1677 | 1579 | 526.2 | 465.2 | 499.5 | 465.1 | 440.8 | 437.1 | 424.9 | 423.5 | 410.9 | 349.9
1678 | 1580 | 526.2 | 465.2 | 499.6 | 465.1 | 441 | 437.2 | 425 | 423.6 | 410.9 | 350.1
1679 | 1581 | 526.2 | 465.2 | 499.6 | 465.2 | 441.1 | 437.4 | 425.2 | 423.6 | 411 | 350.2
1680 | 1582 | 526.3 | 465.3 | 499.6 | 465.2 | 441.3 | 437.5 | 425.3 | 423.7 | 411.1 | 350.4
1681 | 1583 | 526.3 | 465.3 | 499.5 | 465.2 | 441.4 | 437.7 | 425.4 | 423.7 | 411.2 | 350.5
1682 | 1584 | 526.3 | 465.3 | 499.5 | 465.3 | 441.6 | 437.8 | 425.5 | 423.7 | 411.2 | 350.7
1683 | 1585 | 526.3 | 465.4 | 499.6 | 465.3 | 441.7 | 437.9 | 425.6 | 423.8 | 411.3 | 350.9
1684 | 1586 | 526.3 | 465.4 | 499.6 | 465.3 | 441.8 | 438.1 | 425.7 | 423.8 | 411.4 | 351.1
1685 | 1587 | 526.3 | 465.4 | 499.6 | 465.3 | 441.9 | 438.2 | 425.9 | 423.9 | 411.5 | 351.4
1686 | 1588 | 526.3 | 465.5 | 499.7 | 465.4 | 442 | 438.3 | 426 | 423.9 | 411.6 | 351.6
1687 | 1589 | 526.3 | 465.5 | 499.7 | 465.4 | 442.1 | 438.4 | 426.1 | 423.9 | 411.6 | 351.8
1688 | 1590 | 526.3 | 465.5 | 499.7 | 465.4 | 442.2 | 438.6 | 426.3 | 424 | 411.7 | 352
1689 | 1591 | 526.3 | 465.6 | 499.7 | 465.5 | 442.3 | 438.7 | 426.4 | 424.1 | 411.8 | 352.2
1690 | 1592 | 526.3 | 465.6 | 499.7 | 465.5 | 442.4 | 438.9 | 426.5 | 424.1 | 411.9 | 352.4
1691 | 1593 | 526.3 | 465.6 | 499.7 | 465.5 | 442.5 | 439 | 426.7 | 424.2 | 412 | 352.5
1692 | 1594 | 526.3 | 465.7 | 499.8 | 465.6 | 442.6 | 439.2 | 426.8 | 424.2 | 412.1 | 352.6
1693 | 1595 | 526.3 | 465.7 | 499.8 | 465.6 | 442.7 | 439.3 | 427 | 424.3 | 412.2 | 352.8
1694 | 1596 | 526.3 | 465.7 | 499.8 | 465.6 | 442.7 | 439.5 | 427.1 | 424.4 | 412.3 | 352.9
1695 | 1597 | 526.3 | 465.8 | 499.8 | 465.6 | 442.8 | 439.6 | 427.2 | 424.5 | 412.4 | 353.1
1696 | 1598 | 526.2 | 465.8 | 499.8 | 465.6 | 442.9 | 439.8 | 427.4 | 424.6 | 412.5 | 353.2
1697 | 1599 | 526.2 | 465.8 | 499.9 | 465.7 | 443 | 440 | 427.5 | 424.6 | 412.6 | 353.4
1698 | 1600 | 526.3 | 465.8 | 499.9 | 465.7 | 443.1 | 440.2 | 427.7 | 424.6 | 412.7 | 353.5
1699 | 1601 | 526.3 | 465.9 | 499.9 | 465.7 | 443.2 | 440.3 | 427.8 | 424.7 | 412.8 | 353.6
1700 | 1602 | 526.3 | 465.9 | 499.9 | 465.8 | 443.3 | 440.4 | 428 | 424.8 | 412.9 | 353.8
1701 | 1603 | 526.4 | 465.9 | 499.9 | 465.8 | 443.4 | 440.6 | 428.1 | 424.8 | 412.9 | 353.9
1702 | 1604 | 526.3 | 466 | 499.9 | 465.8 | 443.4 | 440.8 | 428.3 | 424.8 | 413 | 354.1
1703 | 1605 | 526.3 | 466 | 499.9 | 465.9 | 443.5 | 441 | 428.4 | 424.9 | 413 | 354.2
1704 | 1606 | 526.2 | 466 | 499.9 | 465.9 | 443.6 | 441.1 | 428.6 | 424.8 | 413.1 | 354.3
1705 | 1607 | 526.2 | 466 | 499.9 | 465.9 | 443.7 | 441.3 | 428.7 | 424.9 | 413.2 | 354.5
1706 | 1608 | 526.2 | 466.1 | 499.9 | 466 | 443.8 | 441.5 | 428.9 | 425 | 413.2 | 354.6
1707 | 1609 | 526.3 | 466.1 | 499.9 | 466 | 443.9 | 441.6 | 429 | 425 | 413.3 | 354.8
1708 | 1610 | 526.2 | 466.1 | 500 | 466 | 443.9 | 441.8 | 429.2 | 425.1 | 413.4 | 354.9
1709 | 1611 | 526.2 | 466.2 | 500 | 466 | 444 | 441.9 | 429.3 | 425.2 | 413.5 | 355
1710 | 1612 | 526.2 | 466.2 | 500 | 466.1 | 444.1 | 442.1 | 429.5 | 425.3 | 413.5 | 355.2
1711 | 1613 | 526.3 | 466.2 | 500 | 466.1 | 444.2 | 442.2 | 429.7 | 425.3 | 413.6 | 355.3
1712 | 1614 | 526.3 | 466.3 | 500 | 466.1 | 444.3 | 442.4 | 429.9 | 425.4 | 413.7 | 355.4
1713 | 1615 | 526.3 | 466.3 | 499.9 | 466.1 | 444.4 | 442.6 | 430.1 | 425.4 | 413.8 | 355.6
1714 | 1616 | 526.3 | 466.3 | 500 | 466.2 | 444.5 | 442.7 | 430.2 | 425.5 | 413.9 | 355.7
1715 | 1617 | 526.2 | 466.4 | 500.1 | 466.2 | 444.6 | 442.9 | 430.4 | 425.5 | 413.9 | 355.8
1716 | 1618 | 526.2 | 466.4 | 500.1 | 466.2 | 444.7 | 443.1 | 430.5 | 425.6 | 414 | 356
1717 | 1619 | 526.2 | 466.4 | 500.1 | 466.3 | 444.8 | 443.2 | 430.7 | 425.6 | 414.1 | 356.1
1718 | 1620 | 526.2 | 466.5 | 500 | 466.3 | 444.9 | 443.3 | 430.8 | 425.6 | 414.2 | 356.2
1719 | 1621 | 526.1 | 466.5 | 500 | 466.3 | 445 | 443.5 | 431 | 425.6 | 414.2 | 356.4
1720 | 1622 | 526.1 | 466.5 | 500 | 466.3 | 445.1 | 443.6 | 431.2 | 425.7 | 414.3 | 356.5
1721 | 1623 | 526.1 | 466.5 | 500.1 | 466.4 | 445.2 | 443.7 | 431.4 | 425.7 | 414.4 | 356.6
1722 | 1624 | 526.1 | 466.6 | 500.1 | 466.4 | 445.3 | 443.9 | 431.5 | 425.8 | 414.5 | 356.7
1723 | 1625 | 526.1 | 466.6 | 500.1 | 466.4 | 445.4 | 444 | 431.8 | 425.8 | 414.6 | 356.9
1724 | 1626 | 526.1 | 466.6 | 500.2 | 466.5 | 445.5 | 444.1 | 432.1 | 425.9 | 414.7 | 357
1725 | 1627 | 526.2 | 466.7 | 500.2 | 466.5 | 445.6 | 444.3 | 432.3 | 426 | 414.8 | 357.1
1726 | 1628 | 526.2 | 466.7 | 500.2 | 466.5 | 445.7 | 444.5 | 432.6 | 426.1 | 414.9 | 357.3
1727 | 1629 | 526.2 | 466.7 | 500.2 | 466.5 | 445.8 | 444.6 | 432.8 | 426.1 | 415 | 357.4
1728 | 1630 | 526.1 | 466.7 | 500.2 | 466.6 | 445.9 | 444.7 | 433 | 426.2 | 415.1 | 357.5
1729 | 1631 | 526.1 | 466.8 | 500.2 | 466.6 | 446 | 444.9 | 433.2 | 426.3 | 415.2 | 357.6
1730 | 1632 | 526.1 | 466.8 | 500.2 | 466.6 | 446.1 | 445 | 433.4 | 426.4 | 415.3 | 357.8
1731 | 1633 | 526.1 | 466.8 | 500.3 | 466.7 | 446.2 | 445.1 | 433.5 | 426.5 | 415.4 | 357.9
1732 | 1634 | 526.1 | 466.9 | 500.3 | 466.7 | 446.3 | 445.3 | 433.8 | 426.6 | 415.5 | 358
1733 | 1635 | 526.2 | 466.9 | 500.3 | 466.7 | 446.4 | 445.5 | 434 | 426.6 | 415.5 | 358.2
1734 | 1636 | 526.2 | 466.9 | 500.3 | 466.7 | 446.6 | 445.5 | 434.2 | 426.7 | 415.6 | 358.3
1735 | 1637 | 526.2 | 466.9 | 500.4 | 466.7 | 446.7 | 445.7 | 434.4 | 426.8 | 415.8 | 358.4
1736 | 1638 | 526.2 | 467 | 500.4 | 466.8 | 446.8 | 445.8 | 434.7 | 426.9 | 415.9 | 358.5
1737 | 1639 | 526.2 | 467 | 500.4 | 466.8 | 446.9 | 445.9 | 434.9 | 427 | 416 | 358.7
1738 | 1640 | 526.3 | 467 | 500.4 | 466.9 | 447 | 446 | 435.1 | 427.1 | 416.1 | 358.8
1739 | 1641 | 526.3 | 467.1 | 500.4 | 466.9 | 447.1 | 446.2 | 435.3 | 427.2 | 416.2 | 358.9
1740 | 1642 | 526.3 | 467.1 | 500.4 | 466.9 | 447.2 | 446.3 | 435.6 | 427.2 | 416.2 | 359.1
1741 | 1643 | 526.3 | 467.1 | 500.5 | 466.9 | 447.3 | 446.5 | 435.8 | 427.2 | 416.3 | 359.2
1742 | 1644 | 526.3 | 467.1 | 500.5 | 466.9 | 447.5 | 446.6 | 436 | 427.3 | 416.4 | 359.3
1743 | 1645 | 526.3 | 467.2 | 500.5 | 467 | 447.6 | 446.7 | 436.2 | 427.5 | 416.5 | 359.5
1744 | 1646 | 526.3 | 467.2 | 500.5 | 467 | 447.7 | 446.8 | 436.4 | 427.6 | 416.6 | 359.6
1745 | 1647 | 526.3 | 467.2 | 500.5 | 467 | 447.8 | 446.9 | 436.6 | 427.8 | 416.7 | 359.7
1746 | 1648 | 526.3 | 467.2 | 500.5 | 467.1 | 447.9 | 447 | 436.8 | 427.9 | 416.8 | 359.8
1747 | 1649 | 526.3 | 467.3 | 500.5 | 467.1 | 448 | 447.2 | 437 | 427.9 | 416.9 | 360
1748 | 1650 | 526.3 | 467.3 | 500.5 | 467.1 | 448.1 | 447.3 | 437.2 | 427.9 | 417 | 360.1
1749 | 1651 | 526.3 | 467.3 | 500.6 | 467.2 | 448.2 | 447.4 | 437.3 | 428 | 417.1 | 360.2
1750 | 1652 | 526.3 | 467.4 | 500.6 | 467.2 | 448.4 | 447.6 | 437.5 | 428.1 | 417.2 | 360.4
1751 | 1653 | 526.3 | 467.4 | 500.6 | 467.2 | 448.5 | 447.7 | 437.7 | 428.1 | 417.3 | 360.5
1752 | 1654 | 526.2 | 467.4 | 500.6 | 467.2 | 448.6 | 447.8 | 437.8 | 428.2 | 417.4 | 360.6
1753 | 1655 | 526.2 | 467.4 | 500.6 | 467.2 | 448.7 | 447.9 | 438 | 428.3 | 417.4 | 360.8
1754 | 1656 | 526.2 | 467.5 | 500.6 | 467.3 | 448.8 | 448.1 | 438.2 | 428.4 | 417.5 | 360.9
1755 | 1657 | 526.1 | 467.5 | 500.6 | 467.3 | 448.9 | 448.2 | 438.4 | 428.5 | 417.6 | 361
1756 | 1658 | 526.1 | 467.5 | 500.6 | 467.3 | 449 | 448.3 | 438.5 | 428.5 | 417.7 | 361.2
1757 | 1659 | 526.1 | 467.5 | 500.7 | 467.4 | 449.1 | 448.4 | 438.7 | 428.6 | 417.7 | 361.3
1758 | 1660 | 526.1 | 467.6 | 500.7 | 467.4 | 449.2 | 448.5 | 438.8 | 428.7 | 417.8 | 361.4
1759 | 1661 | 526.1 | 467.6 | 500.7 | 467.4 | 449.3 | 448.6 | 439 | 428.8 | 417.9 | 361.6
1760 | 1662 | 526.1 | 467.6 | 500.7 | 467.4 | 449.4 | 448.7 | 439.1 | 428.9 | 418 | 361.7
1761 | 1663 | 526 | 467.7 | 500.7 | 467.5 | 449.5 | 448.8 | 439.3 | 428.9 | 418.1 | 361.8
1762 | 1664 | 526 | 467.7 | 500.7 | 467.5 | 449.6 | 448.9 | 439.4 | 429.1 | 418.1 | 362
1763 | 1665 | 526 | 467.7 | 500.7 | 467.5 | 449.7 | 449 | 439.6 | 429.1 | 418.3 | 362.1
1764 | 1666 | 526 | 467.7 | 500.8 | 467.6 | 449.8 | 449.2 | 439.7 | 429.2 | 418.3 | 362.2
1765 | 1667 | 526 | 467.8 | 500.8 | 467.6 | 449.9 | 449.3 | 439.9 | 429.4 | 418.4 | 362.4
1766 | 1668 | 526.1 | 467.8 | 500.8 | 467.6 | 450 | 449.4 | 440 | 429.6 | 418.5 | 362.5
1767 | 1669 | 526.1 | 467.8 | 500.8 | 467.6 | 450.1 | 449.5 | 440.2 | 429.7 | 418.6 | 362.6
1768 | 1670 | 526.1 | 467.8 | 500.8 | 467.7 | 450.2 | 449.6 | 440.3 | 429.8 | 418.7 | 362.8
1769 | 1671 | 526.1 | 467.8 | 500.8 | 467.7 | 450.3 | 449.7 | 440.4 | 430 | 418.8 | 362.9
1770 | 1672 | 526.1 | 467.9 | 500.9 | 467.7 | 450.4 | 449.8 | 440.6 | 430.1 | 418.9 | 363
1771 | 1673 | 526.2 | 467.9 | 500.9 | 467.7 | 450.5 | 449.9 | 440.7 | 430.2 | 419 | 363.2
1772 | 1674 | 526.2 | 467.9 | 500.9 | 467.8 | 450.6 | 450 | 440.9 | 430.4 | 419 | 363.3
1773 | 1675 | 526.2 | 467.9 | 501 | 467.8 | 450.7 | 450.1 | 441 | 430.6 | 419.1 | 363.4
1774 | 1676 | 526.1 | 468 | 500.9 | 467.8 | 450.8 | 450.2 | 441.1 | 430.7 | 419.2 | 363.5
1775 | 1677 | 526.1 | 468 | 500.9 | 467.9 | 450.9 | 450.3 | 441.3 | 430.8 | 419.3 | 363.7
1776 | 1678 | 526.1 | 468 | 501 | 467.9 | 451 | 450.4 | 441.4 | 430.9 | 419.4 | 363.8
1777 | 1679 | 526.1 | 468 | 501 | 467.9 | 451.1 | 450.5 | 441.5 | 431.1 | 419.5 | 363.9
1778 | 1680 | 526 | 468.1 | 501 | 467.9 | 451.2 | 450.6 | 441.6 | 431.3 | 419.6 | 364.1
1779 | 1681 | 526 | 468.1 | 501 | 467.9 | 451.3 | 450.7 | 441.8 | 431.4 | 419.6 | 364.2
1780 | 1682 | 526 | 468.1 | 501 | 468 | 451.4 | 450.8 | 441.9 | 431.5 | 419.7 | 364.3
1781 | 1683 | 526 | 468.2 | 501 | 468 | 451.5 | 450.9 | 442 | 431.5 | 419.8 | 364.5
1782 | 1684 | 525.9 | 468.2 | 501 | 468 | 451.6 | 451 | 442.1 | 431.7 | 419.9 | 364.6
1783 | 1685 | 526 | 468.2 | 501 | 468.1 | 451.7 | 451.1 | 442.2 | 431.8 | 420 | 364.8
1784 | 1686 | 526 | 468.2 | 501 | 468.1 | 451.7 | 451.1 | 442.3 | 432 | 420.1 | 364.9
1785 | 1687 | 526 | 468.2 | 501.1 | 468.1 | 451.8 | 451.3 | 442.4 | 432.1 | 420.1 | 365
1786 | 1688 | 526.1 | 468.3 | 501.1 | 468.1 | 451.9 | 451.3 | 442.5 | 432.2 | 420.2 | 365.2
1787 | 1689 | 526.1 | 468.3 | 501.1 | 468.2 | 452 | 451.4 | 442.6 | 432.4 | 420.3 | 365.3
1788 | 1690 | 526.1 | 468.3 | 501.1 | 468.2 | 452.1 | 451.5 | 442.6 | 432.5 | 420.4 | 365.4
1789 | 1691 | 526.1 | 468.3 | 501.1 | 468.2 | 452.2 | 451.6 | 442.7 | 432.6 | 420.4 | 365.6
1790 | 1692 | 526.1 | 468.4 | 501.1 | 468.3 | 452.3 | 451.7 | 442.8 | 432.7 | 420.5 | 365.7
1791 | 1693 | 526.1 | 468.4 | 501.1 | 468.3 | 452.4 | 451.8 | 442.9 | 432.9 | 420.6 | 365.8
1792 | 1694 | 526.1 | 468.4 | 501.1 | 468.3 | 452.5 | 451.8 | 443 | 433.1 | 420.7 | 366
1793 | 1695 | 526.1 | 468.4 | 501.1 | 468.3 | 452.6 | 451.9 | 443.1 | 433.3 | 420.7 | 366.1
1794 | 1696 | 526.1 | 468.4 | 501.1 | 468.3 | 452.6 | 452 | 443.2 | 433.4 | 420.8 | 366.3
1795 | 1697 | 526.1 | 468.5 | 501.1 | 468.4 | 452.7 | 452.1 | 443.3 | 433.4 | 420.9 | 366.4
1796 | 1698 | 526.2 | 468.5 | 501.1 | 468.4 | 452.8 | 452.2 | 443.3 | 433.5 | 421 | 366.6
1797 | 1699 | 526.2 | 468.5 | 501.2 | 468.4 | 452.9 | 452.3 | 443.4 | 433.6 | 421.1 | 366.7
1798 | 1700 | 526.3 | 468.5 | 501.2 | 468.4 | 453 | 452.3 | 443.5 | 433.7 | 421.2 | 366.8
1799 | 1701 | 526.3 | 468.6 | 501.2 | 468.5 | 453.1 | 452.4 | 443.6 | 433.8 | 421.3 | 367
1800 | 1702 | 526.3 | 468.6 | 501.2 | 468.5 | 453.2 | 452.5 | 443.6 | 433.9 | 421.4 | 367.1
1801 | 1703 | 526.3 | 468.6 | 501.2 | 468.5 | 453.2 | 452.6 | 443.7 | 434.1 | 421.5 | 367.3
1802 | 1704 | 526.4 | 468.6 | 501.2 | 468.6 | 453.3 | 452.7 | 443.8 | 434.2 | 421.6 | 367.4
1803 | 1705 | 526.3 | 468.7 | 501.2 | 468.6 | 453.4 | 452.8 | 443.9 | 434.3 | 421.7 | 367.6
1804 | 1706 | 526.3 | 468.7 | 501.3 | 468.6 | 453.5 | 452.9 | 443.9 | 434.4 | 421.8 | 367.7
1805 | 1707 | 526.3 | 468.7 | 501.3 | 468.7 | 453.6 | 452.9 | 444 | 434.6 | 421.9 | 367.9
1806 | 1708 | 526.4 | 468.7 | 501.3 | 468.7 | 453.6 | 453 | 444.1 | 434.6 | 421.9 | 368
1807 | 1709 | 526.4 | 468.8 | 501.3 | 468.7 | 453.7 | 453.1 | 444.1 | 434.7 | 422 | 368.2
1808 | 1710 | 526.4 | 468.8 | 501.3 | 468.7 | 453.8 | 453.2 | 444.2 | 434.7 | 422.1 | 368.3
1809 | 1711 | 526.3 | 468.8 | 501.3 | 468.8 | 453.9 | 453.3 | 444.2 | 434.8 | 422.2 | 368.4
1810 | 1712 | 526.3 | 468.8 | 501.3 | 468.8 | 454 | 453.3 | 444.3 | 434.8 | 422.3 | 368.6
1811 | 1713 | 526.3 | 468.9 | 501.3 | 468.8 | 454 | 453.4 | 444.4 | 434.9 | 422.4 | 368.7
1812 | 1714 | 526.3 | 468.9 | 501.3 | 468.8 | 454.1 | 453.5 | 444.4 | 435 | 422.5 | 368.9
1813 | 1715 | 526.3 | 468.9 | 501.3 | 468.8 | 454.2 | 453.6 | 444.5 | 435.1 | 422.5 | 369
1814 | 1716 | 526.3 | 468.9 | 501.3 | 468.9 | 454.3 | 453.7 | 444.6 | 435.2 | 422.6 | 369.2
1815 | 1717 | 526.3 | 468.9 | 501.4 | 468.9 | 454.3 | 453.7 | 444.7 | 435.3 | 422.6 | 369.3
1816 | 1718 | 526.3 | 469 | 501.4 | 468.9 | 454.4 | 453.8 | 444.7 | 435.4 | 422.7 | 369.4
1817 | 1719 | 526.3 | 469 | 501.4 | 469 | 454.5 | 453.9 | 444.8 | 435.6 | 422.8 | 369.6
1818 | 1720 | 526.3 | 469.1 | 501.2 | 469.1 | 454.5 | 454 | 444.9 | 435.7 | 422.8 | 369.8
1819 | 1721 | 526.3 | 469.1 | 501.3 | 469.1 | 454.6 | 454.1 | 445 | 435.8 | 423 | 369.9
1820 | 1722 | 526.3 | 469.1 | 501.4 | 469 | 454.7 | 454.1 | 445 | 435.8 | 423 | 370
1821 | 1723 | 526.4 | 469.1 | 501.4 | 469.1 | 454.7 | 454.2 | 445.1 | 435.8 | 423.1 | 370.2
1822 | 1724 | 526.4 | 469.1 | 501.4 | 469.1 | 454.8 | 454.3 | 445.2 | 435.9 | 423.3 | 370.3
1823 | 1725 | 526.4 | 469.1 | 501.5 | 469.1 | 454.9 | 454.3 | 445.3 | 435.9 | 423.4 | 370.5
1824 | 1726 | 526.4 | 469.2 | 501.5 | 469.1 | 454.9 | 454.4 | 445.3 | 436 | 423.5 | 370.6
1825 | 1727 | 526.4 | 469.2 | 501.5 | 469.2 | 455 | 454.5 | 445.4 | 436.1 | 423.6 | 370.7
1826 | 1728 | 526.4 | 469.2 | 501.5 | 469.2 | 455.1 | 454.6 | 445.5 | 436.3 | 423.7 | 370.9
1827 | 1729 | 526.4 | 469.2 | 501.5 | 469.2 | 455.1 | 454.7 | 445.6 | 436.4 | 423.8 | 371
1828 | 1730 | 526.3 | 469.3 | 501.5 | 469.3 | 455.2 | 454.8 | 445.7 | 436.6 | 423.9 | 371.2
1829 | 1731 | 526.3 | 469.4 | 501.3 | 469.4 | 455.3 | 454.9 | 445.8 | 436.8 | 424.1 | 371.3
1830 | 1732 | 526.2 | 469.5 | 501 | 469.5 | 455.4 | 455 | 445.8 | 436.9 | 424.2 | 371.5
1831 | 1733 | 526.2 | 469.3 | 501.5 | 469.3 | 455.4 | 455.1 | 445.9 | 437.1 | 424.3 | 371.6
1832 | 1734 | 526.2 | 469.4 | 501.5 | 469.4 | 455.5 | 455.1 | 446 | 437.2 | 424.4 | 371.7
1833 | 1735 | 526.2 | 469.4 | 501.5 | 469.4 | 455.6 | 455.2 | 446 | 437.2 | 424.5 | 371.8
1834 | 1736 | 526.2 | 469.4 | 501.6 | 469.4 | 455.7 | 455.3 | 446.1 | 437.3 | 424.7 | 372
1835 | 1737 | 526.2 | 469.4 | 501.6 | 469.4 | 455.8 | 455.3 | 446.2 | 437.5 | 424.8 | 372.1
1836 | 1738 | 526.3 | 469.4 | 501.6 | 469.5 | 455.8 | 455.4 | 446.3 | 437.5 | 424.9 | 372.2
1837 | 1739 | 526.3 | 469.5 | 501.5 | 469.5 | 455.9 | 455.5 | 446.3 | 437.6 | 425 | 372.4
1838 | 1740 | 526.3 | 469.7 | 501.1 | 469.7 | 456 | 455.6 | 446.4 | 437.7 | 425.2 | 372.5
1839 | 1741 | 526.3 | 469.5 | 501.6 | 469.5 | 456 | 455.7 | 446.5 | 437.9 | 425.3 | 372.6
1840 | 1742 | 526.3 | 469.5 | 501.6 | 469.6 | 456.1 | 455.7 | 446.6 | 438 | 425.5 | 372.8
1841 | 1743 | 526.3 | 469.6 | 501.6 | 469.6 | 456.2 | 455.8 | 446.6 | 438.1 | 425.6 | 372.9
1842 | 1744 | 526.3 | 469.6 | 501.6 | 469.6 | 456.3 | 455.9 | 446.7 | 438.2 | 425.8 | 373
1843 | 1745 | 526.3 | 469.7 | 501.5 | 469.7 | 456.3 | 456 | 446.8 | 438.3 | 425.9 | 373.2
1844 | 1746 | 526.4 | 469.7 | 501.5 | 469.7 | 456.4 | 456.1 | 446.9 | 438.5 | 426.1 | 373.3
1845 | 1747 | 526.4 | 469.6 | 501.6 | 469.7 | 456.5 | 456.1 | 446.9 | 438.5 | 426.2 | 373.4
1846 | 1748 | 526.4 | 469.7 | 501.5 | 469.8 | 456.6 | 456.2 | 447 | 438.6 | 426.3 | 373.6
1847 | 1749 | 526.4 | 469.8 | 501.5 | 469.8 | 456.6 | 456.2 | 447.1 | 438.8 | 426.5 | 373.7
1848 | 1750 | 526.4 | 469.8 | 501.5 | 469.8 | 456.7 | 456.3 | 447.2 | 439 | 426.6 | 373.8
1849 | 1751 | 526.4 | 469.7 | 501.6 | 469.8 | 456.7 | 456.3 | 447.2 | 439.1 | 426.7 | 373.9
1850 | 1752 | 526.4 | 469.8 | 501.6 | 469.8 | 456.8 | 456.4 | 447.3 | 439.2 | 426.9 | 374
1851 | 1753 | 526.4 | 469.8 | 501.6 | 469.9 | 456.9 | 456.5 | 447.4 | 439.2 | 427 | 374.2
1852 | 1754 | 526.4 | 469.8 | 501.6 | 469.9 | 456.9 | 456.6 | 447.5 | 439.3 | 427.2 | 374.3
1853 | 1755 | 526.4 | 469.9 | 501.6 | 469.9 | 457 | 456.6 | 447.5 | 439.4 | 427.3 | 374.4
1854 | 1756 | 526.4 | 469.9 | 501.7 | 469.9 | 457.1 | 456.7 | 447.6 | 439.5 | 427.5 | 374.6
1855 | 1757 | 526.4 | 469.9 | 501.7 | 470 | 457.1 | 456.8 | 447.7 | 439.6 | 427.6 | 374.7
1856 | 1758 | 526.4 | 469.9 | 501.7 | 470 | 457.2 | 456.8 | 447.8 | 439.7 | 427.7 | 374.8
1857 | 1759 | 526.4 | 469.9 | 501.6 | 470 | 457.3 | 456.9 | 447.8 | 439.9 | 427.9 | 375
1858 | 1760 | 526.3 | 470 | 501.7 | 470 | 457.4 | 457 | 447.9 | 439.9 | 428.1 | 375.1
1859 | 1761 | 526.2 | 470 | 501.7 | 470.1 | 457.4 | 457 | 448 | 440.1 | 428.2 | 375.2
1860 | 1762 | 526.2 | 470 | 501.7 | 470.1 | 457.5 | 457.1 | 448 | 440.3 | 428.3 | 375.4
1861 | 1763 | 526.1 | 470 | 501.7 | 470.1 | 457.6 | 457.2 | 448.1 | 440.4 | 428.4 | 375.5
1862 | 1764 | 526.1 | 470 | 501.7 | 470.2 | 457.6 | 457.2 | 448.1 | 440.6 | 428.6 | 375.6
1863 | 1765 | 526.1 | 470.2 | 501.4 | 470.3 | 457.7 | 457.3 | 448.2 | 440.7 | 428.7 | 375.8
1864 | 1766 | 526 | 470.3 | 501.2 | 470.4 | 457.8 | 457.4 | 448.3 | 440.8 | 428.9 | 375.9
1865 | 1767 | 526 | 470.4 | 501.2 | 470.4 | 457.9 | 457.4 | 448.3 | 440.9 | 429 | 376.1
1866 | 1768 | 526 | 470.4 | 501.2 | 470.5 | 458 | 457.5 | 448.4 | 441 | 429.1 | 376.2
1867 | 1769 | 526.1 | 470.4 | 501.2 | 470.5 | 458.1 | 457.6 | 448.5 | 441.1 | 429.2 | 376.3
1868 | 1770 | 526 | 470.4 | 501.2 | 470.5 | 458.1 | 457.7 | 448.5 | 441.3 | 429.3 | 376.5
1869 | 1771 | 526 | 470.4 | 501.2 | 470.5 | 458.2 | 457.7 | 448.6 | 441.4 | 429.5 | 376.6
1870 | 1772 | 526 | 470.5 | 501.2 | 470.6 | 458.3 | 457.8 | 448.7 | 441.5 | 429.6 | 376.7
1871 | 1773 | 526 | 470.5 | 501.2 | 470.6 | 458.4 | 457.9 | 448.7 | 441.7 | 429.6 | 376.8
1872 | 1774 | 525.9 | 470.5 | 501.2 | 470.6 | 458.4 | 457.9 | 448.8 | 441.8 | 429.8 | 377
1873 | 1775 | 526 | 470.5 | 501.3 | 470.6 | 458.5 | 458 | 448.9 | 442 | 429.9 | 377.1
1874 | 1776 | 526 | 470.5 | 501.3 | 470.7 | 458.6 | 458.1 | 448.9 | 442.1 | 430 | 377.2
1875 | 1777 | 526.1 | 470.5 | 501.3 | 470.7 | 458.6 | 458.1 | 449 | 442.2 | 430.2 | 377.3
1876 | 1778 | 526.1 | 470.6 | 501.3 | 470.7 | 458.7 | 458.2 | 449.1 | 442.4 | 430.3 | 377.5
1877 | 1779 | 526.1 | 470.6 | 501.3 | 470.7 | 458.8 | 458.3 | 449.1 | 442.4 | 430.3 | 377.6
1878 | 1780 | 526.2 | 470.6 | 501.3 | 470.8 | 458.9 | 458.3 | 449.2 | 442.5 | 430.5 | 377.7
1879 | 1781 | 526.2 | 470.6 | 501.3 | 470.8 | 458.9 | 458.4 | 449.3 | 442.6 | 430.6 | 377.8
1880 | 1782 | 526.2 | 470.6 | 501.3 | 470.8 | 459 | 458.5 | 449.4 | 442.7 | 430.7 | 378
1881 | 1783 | 526.2 | 470.7 | 501.4 | 470.8 | 459.1 | 458.5 | 449.4 | 442.8 | 430.8 | 378.1
1882 | 1784 | 526.2 | 470.7 | 501.4 | 470.9 | 459.1 | 458.6 | 449.5 | 443 | 431 | 378.2
1883 | 1785 | 526.2 | 470.7 | 501.4 | 470.9 | 459.2 | 458.7 | 449.6 | 443.1 | 431.1 | 378.3
1884 | 1786 | 526.2 | 470.7 | 501.5 | 470.9 | 459.3 | 458.8 | 449.6 | 443.2 | 431.3 | 378.4
1885 | 1787 | 526.2 | 470.7 | 501.4 | 471 | 459.4 | 458.8 | 449.7 | 443.3 | 431.4 | 378.6
1886 | 1788 | 526.2 | 470.8 | 501.4 | 471 | 459.4 | 458.9 | 449.8 | 443.5 | 431.5 | 378.7
1887 | 1789 | 526.2 | 470.8 | 501.5 | 471 | 459.5 | 459 | 449.8 | 443.6 | 431.6 | 378.8
1888 | 1790 | 526.3 | 470.8 | 501.5 | 471 | 459.5 | 459 | 449.9 | 443.7 | 431.7 | 378.9
1889 | 1791 | 526.3 | 470.8 | 501.5 | 471.1 | 459.6 | 459.1 | 449.9 | 443.8 | 431.8 | 379.1
1890 | 1792 | 526.3 | 470.9 | 501.4 | 471.1 | 459.6 | 459.1 | 450 | 444 | 431.9 | 379.2
1891 | 1793 | 526.3 | 470.8 | 501.5 | 471.1 | 459.7 | 459.2 | 450.1 | 444.1 | 432 | 379.3
1892 | 1794 | 526.3 | 470.9 | 501.5 | 471.1 | 459.7 | 459.3 | 450.1 | 444.3 | 432.1 | 379.4
1893 | 1795 | 526.3 | 470.9 | 501.5 | 471.1 | 459.8 | 459.3 | 450.2 | 444.3 | 432.3 | 379.6
1894 | 1796 | 526.2 | 470.9 | 501.5 | 471.2 | 459.8 | 459.4 | 450.2 | 444.4 | 432.5 | 379.7
1895 | 1797 | 526.2 | 470.9 | 501.5 | 471.2 | 459.9 | 459.5 | 450.3 | 444.5 | 432.6 | 379.9
1896 | 1798 | 526.1 | 470.9 | 501.6 | 471.2 | 460 | 459.5 | 450.4 | 444.6 | 432.7 | 380
1897 | 1799 | 526.1 | 470.9 | 501.6 | 471.2 | 460 | 459.6 | 450.4 | 444.7 | 432.8 | 380.2
1898 | 1800 | 526 | 471 | 501.6 | 471.3 | 460.1 | 459.7 | 450.5 | 444.8 | 433 | 380.3
1899 | 1801 | 526 | 471 | 501.6 | 471.3 | 460.2 | 459.8 | 450.6 | 444.9 | 433.1 | 380.5
1900 | 1802 | 526 | 471 | 501.6 | 471.3 | 460.2 | 459.8 | 450.6 | 445.1 | 433.3 | 380.7
1901 | 1803 | 526 | 471 | 501.6 | 471.3 | 460.3 | 459.9 | 450.7 | 445.3 | 433.4 | 380.8
1902 | 1804 | 526 | 471 | 501.6 | 471.4 | 460.3 | 459.9 | 450.7 | 445.4 | 433.5 | 381
1903 | 1805 | 526 | 471.1 | 501.6 | 471.4 | 460.4 | 460 | 450.8 | 445.5 | 433.5 | 381.1
1904 | 1806 | 526 | 471.1 | 501.6 | 471.4 | 460.5 | 460.1 | 450.8 | 445.6 | 433.7 | 381.3
1905 | 1807 | 526 | 471.1 | 501.6 | 471.5 | 460.5 | 460.1 | 450.9 | 445.7 | 433.8 | 381.5
1906 | 1808 | 526 | 471.1 | 501.6 | 471.5 | 460.6 | 460.2 | 451 | 445.8 | 434 | 381.7
1907 | 1809 | 526 | 471.1 | 501.6 | 471.5 | 460.7 | 460.3 | 451 | 445.9 | 434 | 381.9
1908 | 1810 | 526.1 | 471.2 | 501.7 | 471.5 | 460.8 | 460.3 | 451.1 | 445.9 | 434.1 | 382.1
1909 | 1811 | 526.1 | 471.2 | 501.7 | 471.6 | 460.8 | 460.4 | 451.2 | 446.1 | 434.2 | 382.3
1910 | 1812 | 526 | 471.2 | 501.7 | 471.6 | 460.9 | 460.4 | 451.2 | 446.2 | 434.4 | 382.4
1911 | 1813 | 526 | 471.2 | 501.7 | 471.6 | 460.9 | 460.5 | 451.3 | 446.3 | 434.5 | 382.6
1912 | 1814 | 526 | 471.2 | 501.7 | 471.6 | 461 | 460.6 | 451.3 | 446.3 | 434.5 | 382.8
1913 | 1815 | 526 | 471.2 | 501.7 | 471.7 | 461.1 | 460.6 | 451.4 | 446.4 | 434.6 | 383
1914 | 1816 | 526 | 471.3 | 501.8 | 471.7 | 461.2 | 460.7 | 451.4 | 446.5 | 434.6 | 383.1
1915 | 1817 | 526 | 471.3 | 501.8 | 471.7 | 461.2 | 460.7 | 451.5 | 446.7 | 434.7 | 383.3
1916 | 1818 | 526 | 471.3 | 501.8 | 471.7 | 461.3 | 460.8 | 451.6 | 446.8 | 434.8 | 383.5
1917 | 1819 | 526 | 471.3 | 501.8 | 471.7 | 461.4 | 460.8 | 451.6 | 447 | 434.8 | 383.6
1918 | 1820 | 526 | 471.3 | 501.8 | 471.8 | 461.4 | 460.9 | 451.7 | 447.1 | 434.9 | 383.8
1919 | 1821 | 526 | 471.3 | 501.8 | 471.8 | 461.5 | 461 | 451.8 | 447.2 | 435 | 384
1920 | 1822 | 526 | 471.3 | 501.9 | 471.8 | 461.5 | 461 | 451.8 | 447.3 | 435.1 | 384.1
1921 | 1823 | 526 | 471.4 | 501.9 | 471.8 | 461.6 | 461.1 | 451.9 | 447.4 | 435.2 | 384.3
1922 | 1824 | 526.1 | 471.4 | 501.9 | 471.9 | 461.7 | 461.1 | 451.9 | 447.4 | 435.2 | 384.5
1923 | 1825 | 526.1 | 471.4 | 501.9 | 471.9 | 461.7 | 461.2 | 452 | 447.5 | 435.2 | 384.6
1924 | 1826 | 526.1 | 471.4 | 501.9 | 471.9 | 461.8 | 461.2 | 452 | 447.6 | 435.3 | 384.8
1925 | 1827 | 526.1 | 471.4 | 501.9 | 472 | 461.9 | 461.3 | 452.1 | 447.7 | 435.4 | 384.9
1926 | 1828 | 526.1 | 471.5 | 501.8 | 472 | 462 | 461.3 | 452.1 | 447.7 | 435.4 | 385.1
1927 | 1829 | 526.1 | 471.5 | 501.9 | 472 | 462 | 461.4 | 452.2 | 447.8 | 435.5 | 385.2
1928 | 1830 | 526.1 | 471.5 | 501.9 | 472 | 462.1 | 461.4 | 452.2 | 447.9 | 435.5 | 385.4
1929 | 1831 | 526 | 471.5 | 501.9 | 472 | 462.1 | 461.5 | 452.3 | 448 | 435.6 | 385.6
1930 | 1832 | 526 | 471.5 | 501.9 | 472 | 462.2 | 461.6 | 452.3 | 448.1 | 435.6 | 385.7
1931 | 1833 | 526 | 471.5 | 501.9 | 472.1 | 462.3 | 461.6 | 452.4 | 448.1 | 435.7 | 385.9
1932 | 1834 | 526 | 471.6 | 501.9 | 472.1 | 462.3 | 461.7 | 452.4 | 448.2 | 435.7 | 386
1933 | 1835 | 526 | 471.6 | 501.9 | 472.1 | 462.4 | 461.8 | 452.5 | 448.3 | 435.7 | 386.2
1934 | 1836 | 526 | 471.6 | 501.9 | 472.2 | 462.4 | 461.9 | 452.5 | 448.5 | 435.8 | 386.3
1935 | 1837 | 526 | 471.6 | 502 | 472.2 | 462.5 | 461.9 | 452.6 | 448.6 | 435.8 | 386.5
1936 | 1838 | 526 | 471.6 | 501.9 | 472.2 | 462.6 | 462 | 452.6 | 448.6 | 435.9 | 386.6
1937 | 1839 | 526 | 471.7 | 502 | 472.2 | 462.6 | 462 | 452.7 | 448.7 | 435.9 | 386.8
1938 | 1840 | 526 | 471.7 | 502 | 472.2 | 462.7 | 462.1 | 452.8 | 448.8 | 435.9 | 386.9
1939 | 1841 | 526 | 471.7 | 502.1 | 472.3 | 462.7 | 462.2 | 452.8 | 448.8 | 436 | 387.1
1940 | 1842 | 526.1 | 471.7 | 502.1 | 472.3 | 462.8 | 462.2 | 452.9 | 448.9 | 436 | 387.2
1941 | 1843 | 526.2 | 471.7 | 502.1 | 472.3 | 462.9 | 462.3 | 452.9 | 449 | 436.1 | 387.3
1942 | 1844 | 526.2 | 471.7 | 502.1 | 472.3 | 462.9 | 462.4 | 453 | 449.1 | 436.1 | 387.5
1943 | 1845 | 526.2 | 471.7 | 502.1 | 472.4 | 463 | 462.4 | 453 | 449.2 | 436.1 | 387.6
1944 | 1846 | 526.2 | 471.8 | 501.9 | 472.4 | 463 | 462.5 | 453.1 | 449.2 | 436.2 | 387.8
1945 | 1847 | 526.2 | 471.8 | 502.1 | 472.4 | 463.1 | 462.5 | 453.2 | 449.4 | 436.3 | 387.9
1946 | 1848 | 526.2 | 471.8 | 502.1 | 472.4 | 463.2 | 462.6 | 453.2 | 449.5 | 436.3 | 388.1
1947 | 1849 | 526.2 | 471.9 | 502 | 472.5 | 463.3 | 462.7 | 453.3 | 449.6 | 436.3 | 388.3
1948 | 1850 | 526.3 | 471.8 | 502.1 | 472.5 | 463.3 | 462.7 | 453.3 | 449.7 | 436.4 | 388.4
1949 | 1851 | 526.3 | 471.8 | 502.2 | 472.5 | 463.4 | 462.8 | 453.4 | 449.8 | 436.5 | 388.5
1950 | 1852 | 526.3 | 471.8 | 502.2 | 472.5 | 463.4 | 462.9 | 453.5 | 449.9 | 436.5 | 388.7
1951 | 1853 | 526.3 | 471.9 | 502.2 | 472.5 | 463.5 | 462.9 | 453.5 | 449.9 | 436.6 | 388.8
1952 | 1854 | 526.3 | 471.9 | 502.2 | 472.5 | 463.6 | 463 | 453.6 | 450.1 | 436.6 | 389
1953 | 1855 | 526.3 | 471.9 | 502.2 | 472.6 | 463.6 | 463 | 453.7 | 450.2 | 436.7 | 389.1
1954 | 1856 | 526.3 | 471.9 | 502.2 | 472.6 | 463.7 | 463.1 | 453.7 | 450.2 | 436.7 | 389.3
1955 | 1857 | 526.2 | 471.9 | 502.2 | 472.6 | 463.8 | 463.2 | 453.8 | 450.3 | 436.8 | 389.4
1956 | 1858 | 526.2 | 472 | 502.2 | 472.7 | 463.8 | 463.2 | 453.9 | 450.4 | 436.8 | 389.6
1957 | 1859 | 526.2 | 472 | 502.2 | 472.7 | 463.9 | 463.3 | 453.9 | 450.5 | 436.9 | 389.7
1958 | 1860 | 526.1 | 472 | 502.2 | 472.7 | 463.9 | 463.3 | 454 | 450.6 | 436.9 | 389.9
1959 | 1861 | 526.1 | 472 | 502.2 | 472.7 | 464 | 463.4 | 454.1 | 450.7 | 437 | 390
1960 | 1862 | 526.1 | 472 | 502.2 | 472.7 | 464.1 | 463.5 | 454.2 | 450.8 | 437 | 390.2
1961 | 1863 | 526 | 472 | 502.3 | 472.8 | 464.1 | 463.5 | 454.2 | 450.9 | 437 | 390.3
1962 | 1864 | 526 | 472.1 | 502.3 | 472.8 | 464.2 | 463.6 | 454.3 | 451.1 | 437.1 | 390.5
1963 | 1865 | 526.1 | 472.1 | 502.3 | 472.8 | 464.3 | 463.6 | 454.4 | 451.2 | 437.1 | 390.6
1964 | 1866 | 526.1 | 472.1 | 502.3 | 472.8 | 464.3 | 463.6 | 454.4 | 451.3 | 437.1 | 390.8
1965 | 1867 | 526.1 | 472.1 | 502.3 | 472.8 | 464.4 | 463.7 | 454.5 | 451.4 | 437.2 | 390.9
1966 | 1868 | 526.1 | 472.1 | 502.3 | 472.9 | 464.4 | 463.7 | 454.6 | 451.5 | 437.3 | 391
1967 | 1869 | 526.1 | 472.1 | 502.3 | 472.9 | 464.5 | 463.8 | 454.7 | 451.6 | 437.3 | 391.2
1968 | 1870 | 526.1 | 472.1 | 502.3 | 472.9 | 464.6 | 463.9 | 454.7 | 451.7 | 437.3 | 391.3
1969 | 1871 | 526.1 | 472.2 | 502.4 | 472.9 | 464.6 | 464 | 454.8 | 451.6 | 437.4 | 391.5
1970 | 1872 | 526.1 | 472.2 | 502.4 | 473 | 464.7 | 464 | 454.9 | 451.6 | 437.4 | 391.6
1971 | 1873 | 526.1 | 472.2 | 502.4 | 473 | 464.8 | 464.1 | 455 | 451.7 | 437.5 | 391.8
1972 | 1874 | 526.1 | 472.2 | 502.4 | 473 | 464.8 | 464.1 | 455 | 451.8 | 437.5 | 391.9
1973 | 1875 | 526.1 | 472.2 | 502.4 | 473 | 464.9 | 464.2 | 455.1 | 451.9 | 437.5 | 392
1974 | 1876 | 526.1 | 472.3 | 502.4 | 473 | 464.9 | 464.2 | 455.2 | 452 | 437.5 | 392.2
1975 | 1877 | 526.1 | 472.3 | 502.4 | 473 | 465 | 464.3 | 455.3 | 452.1 | 437.6 | 392.3
1976 | 1878 | 526.1 | 472.4 | 502.3 | 473.1 | 465.1 | 464.3 | 455.3 | 452.1 | 437.6 | 392.5
1977 | 1879 | 526.1 | 472.3 | 502.5 | 473.1 | 465.1 | 464.4 | 455.4 | 452.2 | 437.6 | 392.6
1978 | 1880 | 526.1 | 472.3 | 502.5 | 473.1 | 465.2 | 464.4 | 455.5 | 452.2 | 437.6 | 392.8
1979 | 1881 | 526.1 | 472.3 | 502.5 | 473.1 | 465.2 | 464.5 | 455.6 | 452.3 | 437.7 | 392.9
1980 | 1882 | 526.1 | 472.4 | 502.5 | 473.1 | 465.3 | 464.5 | 455.6 | 452.4 | 437.7 | 393
1981 | 1883 | 526.1 | 472.4 | 502.5 | 473.2 | 465.4 | 464.6 | 455.7 | 452.5 | 437.7 | 393.1
1982 | 1884 | 526.1 | 472.4 | 502.5 | 473.2 | 465.4 | 464.6 | 455.8 | 452.6 | 437.7 | 393.3
1983 | 1885 | 526.1 | 472.4 | 502.6 | 473.2 | 465.5 | 464.7 | 455.9 | 452.7 | 437.8 | 393.4
1984 | 1886 | 526.1 | 472.4 | 502.6 | 473.2 | 465.5 | 464.7 | 456 | 452.7 | 437.8 | 393.5
1985 | 1887 | 526.1 | 472.4 | 502.5 | 473.3 | 465.6 | 464.8 | 456 | 452.8 | 437.8 | 393.7
1986 | 1888 | 526.1 | 472.4 | 502.5 | 473.3 | 465.7 | 464.9 | 456.1 | 452.9 | 437.8 | 393.8
1987 | 1889 | 526.1 | 472.5 | 502.6 | 473.3 | 465.7 | 465 | 456.2 | 453 | 437.9 | 393.9
1988 | 1890 | 526.1 | 472.5 | 502.6 | 473.3 | 465.8 | 465 | 456.2 | 453.1 | 437.9 | 394
1989 | 1891 | 526.1 | 472.5 | 502.6 | 473.3 | 465.8 | 465.1 | 456.3 | 453.2 | 437.9 | 394.1
1990 | 1892 | 526.2 | 472.5 | 502.5 | 473.3 | 465.9 | 465.1 | 456.2 | 453.2 | 437.9 | 394.3
1991 | 1893 | 526.2 | 472.5 | 502.6 | 473.4 | 466 | 465.2 | 456.3 | 453.3 | 438 | 394.4
1992 | 1894 | 526.2 | 472.5 | 502.6 | 473.4 | 466 | 465.2 | 456.4 | 453.3 | 438 | 394.5
1993 | 1895 | 526.1 | 472.5 | 502.6 | 473.4 | 466.1 | 465.3 | 456.5 | 453.4 | 438.1 | 394.6
1994 | 1896 | 526.2 | 472.6 | 502.6 | 473.5 | 466.1 | 465.4 | 456.5 | 453.5 | 438.1 | 394.8
1995 | 1897 | 526.2 | 472.6 | 502.6 | 473.5 | 466.2 | 465.4 | 456.6 | 453.6 | 438.1 | 394.9
1996 | 1898 | 526.2 | 472.6 | 502.7 | 473.5 | 466.2 | 465.5 | 456.7 | 453.5 | 438.1 | 395
1997 | 1899 | 526.2 | 472.6 | 502.7 | 473.5 | 466.3 | 465.5 | 456.8 | 453.6 | 438.2 | 395.1
1998 | 1900 | 526.1 | 472.6 | 502.7 | 473.5 | 466.4 | 465.6 | 456.9 | 453.7 | 438.2 | 395.2
1999 | 1901 | 526.1 | 472.6 | 502.7 | 473.5 | 466.4 | 465.7 | 456.9 | 453.8 | 438.3 | 395.3
2000 | 1902 | 526.1 | 472.6 | 502.8 | 473.5 | 466.5 | 465.7 | 457 | 453.8 | 438.3 | 395.4
2001 | 1903 | 526.1 | 472.6 | 502.8 | 473.6 | 466.5 | 465.8 | 457.1 | 453.9 | 438.4 | 395.5
2002 | 1904 | 526.1 | 472.6 | 502.8 | 473.6 | 466.6 | 465.8 | 457.1 | 454 | 438.5 | 395.6
2003 | 1905 | 526.1 | 472.7 | 502.8 | 473.6 | 466.6 | 465.9 | 457.2 | 454.1 | 438.5 | 395.7
2004 | 1906 | 526.1 | 472.7 | 502.8 | 473.6 | 466.7 | 466 | 457.3 | 454.2 | 438.6 | 395.9
2005 | 1907 | 526.1 | 472.7 | 502.8 | 473.6 | 466.8 | 466 | 457.3 | 454.3 | 438.7 | 396
2006 | 1908 | 526.1 | 472.7 | 502.8 | 473.7 | 466.8 | 466.1 | 457.4 | 454.3 | 438.7 | 396.1
2007 | 1909 | 526.1 | 472.7 | 502.8 | 473.7 | 466.9 | 466.1 | 457.5 | 454.4 | 438.8 | 396.2
2008 | 1910 | 526.1 | 472.7 | 502.8 | 473.7 | 466.9 | 466.2 | 457.5 | 454.4 | 438.8 | 396.3
2009 | 1911 | 526.1 | 472.7 | 502.9 | 473.7 | 467 | 466.3 | 457.6 | 454.5 | 438.9 | 396.4
2010 | 1912 | 526 | 472.8 | 502.9 | 473.8 | 467.1 | 466.4 | 457.7 | 454.5 | 439 | 396.5
2011 | 1913 | 526 | 472.8 | 502.9 | 473.8 | 467.1 | 466.4 | 457.7 | 454.6 | 439 | 396.6
2012 | 1914 | 526 | 472.8 | 502.9 | 473.8 | 467.2 | 466.5 | 457.8 | 454.7 | 439.1 | 396.7
2013 | 1915 | 526 | 472.8 | 502.9 | 473.8 | 467.2 | 466.5 | 457.8 | 454.7 | 439.2 | 396.8
2014 | 1916 | 526 | 472.8 | 502.9 | 473.9 | 467.3 | 466.6 | 457.9 | 454.8 | 439.2 | 396.9
2015 | 1917 | 526 | 472.8 | 502.9 | 473.9 | 467.3 | 466.6 | 458 | 454.9 | 439.3 | 397
2016 | 1918 | 526 | 472.8 | 502.9 | 473.9 | 467.4 | 466.7 | 458 | 454.9 | 439.4 | 397.1
2017 | 1919 | 525.9 | 472.9 | 503 | 473.9 | 467.4 | 466.8 | 458.1 | 455 | 439.5 | 397.2
2018 | 1920 | 525.9 | 472.9 | 502.9 | 474 | 467.5 | 466.8 | 458.1 | 455 | 439.5 | 397.3
2019 | 1921 | 526 | 472.9 | 502.9 | 473.9 | 467.5 | 466.9 | 458.2 | 455.1 | 439.6 | 397.4
2020 | 1922 | 526 | 472.9 | 503 | 474 | 467.6 | 466.9 | 458.3 | 455.1 | 439.6 | 397.5
2021 | 1923 | 526 | 473 | 502.9 | 474 | 467.7 | 467 | 458.3 | 455.2 | 439.7 | 397.6
2022 | 1924 | 526 | 472.9 | 503 | 474 | 467.7 | 467 | 458.4 | 455.2 | 439.8 | 397.7
2023 | 1925 | 526 | 472.9 | 503 | 474.1 | 467.8 | 467.1 | 458.4 | 455.2 | 439.9 | 397.8
2024 | 1926 | 526 | 473 | 503 | 474.1 | 467.8 | 467.2 | 458.5 | 455.3 | 439.9 | 397.9
2025 | 1927 | 526 | 473 | 503.1 | 474.1 | 467.9 | 467.2 | 458.5 | 455.3 | 439.9 | 398
2026 | 1928 | 526 | 473 | 503.1 | 474.1 | 467.9 | 467.3 | 458.6 | 455.3 | 439.9 | 398.1
2027 | 1929 | 526 | 473 | 503.1 | 474.2 | 468 | 467.3 | 458.6 | 455.4 | 440 | 398.1
2028 | 1930 | 526 | 473 | 503.1 | 474.2 | 468 | 467.4 | 458.7 | 455.5 | 440.1 | 398.2
2029 | 1931 | 526 | 473 | 503.1 | 474.2 | 468.1 | 467.4 | 458.7 | 455.5 | 440.2 | 398.3
2030 | 1932 | 526 | 473 | 503.1 | 474.2 | 468.1 | 467.5 | 458.8 | 455.6 | 440.3 | 398.4
2031 | 1933 | 525.9 | 473.1 | 503.2 | 474.2 | 468.2 | 467.5 | 458.9 | 455.6 | 440.3 | 398.5
2032 | 1934 | 525.9 | 473.1 | 503.2 | 474.3 | 468.2 | 467.6 | 458.9 | 455.6 | 440.4 | 398.5
2033 | 1935 | 525.9 | 473.1 | 503.2 | 474.3 | 468.3 | 467.6 | 459 | 455.6 | 440.6 | 398.6
2034 | 1936 | 525.9 | 473.1 | 503.2 | 474.3 | 468.4 | 467.7 | 459.1 | 455.7 | 440.7 | 398.7
2035 | 1937 | 525.9 | 473.1 | 503.2 | 474.3 | 468.4 | 467.8 | 459.1 | 455.7 | 440.8 | 398.7
2036 | 1938 | 525.9 | 473.1 | 503.2 | 474.3 | 468.5 | 467.8 | 459.1 | 455.8 | 440.9 | 398.8
2037 | 1939 | 525.9 | 473.1 | 503.2 | 474.4 | 468.5 | 467.9 | 459.2 | 455.9 | 441 | 398.9
2038 | 1940 | 525.9 | 473.2 | 503.2 | 474.4 | 468.6 | 467.9 | 459.3 | 455.9 | 441.1 | 399
2039 | 1941 | 525.9 | 473.2 | 503.2 | 474.4 | 468.6 | 468 | 459.3 | 455.9 | 441.2 | 399.1
2040 | 1942 | 525.9 | 473.2 | 503.2 | 474.4 | 468.7 | 468 | 459.4 | 455.9 | 441.2 | 399.1
2041 | 1943 | 525.9 | 473.2 | 503.3 | 474.4 | 468.7 | 468.1 | 459.4 | 455.9 | 441.3 | 399.2
2042 | 1944 | 525.9 | 473.2 | 503.3 | 474.5 | 468.8 | 468.1 | 459.5 | 455.9 | 441.3 | 399.3
2043 | 1945 | 525.9 | 473.2 | 503.3 | 474.5 | 468.9 | 468.2 | 459.5 | 456 | 441.4 | 399.4
2044 | 1946 | 525.9 | 473.3 | 503.3 | 474.5 | 468.9 | 468.2 | 459.6 | 456 | 441.4 | 399.4
2045 | 1947 | 525.9 | 473.3 | 503.3 | 474.5 | 469 | 468.3 | 459.6 | 456.1 | 441.4 | 399.5
2046 | 1948 | 525.9 | 473.3 | 503.3 | 474.6 | 469 | 468.3 | 459.7 | 456.1 | 441.5 | 399.6
2047 | 1949 | 525.8 | 473.3 | 503.3 | 474.6 | 469.1 | 468.4 | 459.7 | 456.2 | 441.5 | 399.7
2048 | 1950 | 525.9 | 473.3 | 503.4 | 474.6 | 469.1 | 468.4 | 459.8 | 456.2 | 441.6 | 399.8
2049 | 1951 | 525.9 | 473.3 | 503.4 | 474.6 | 469.2 | 468.5 | 459.9 | 456.3 | 441.6 | 399.9
2050 | 1952 | 525.9 | 473.3 | 503.4 | 474.7 | 469.2 | 468.5 | 459.9 | 456.3 | 441.7 | 399.9
2051 | 1953 | 525.9 | 473.4 | 503.4 | 474.7 | 469.3 | 468.6 | 460 | 456.5 | 441.7 | 400
2052 | 1954 | 525.9 | 473.4 | 503.4 | 474.7 | 469.3 | 468.6 | 460 | 456.6 | 441.8 | 400.1
2053 | 1955 | 525.9 | 473.4 | 503.5 | 474.7 | 469.4 | 468.7 | 460.1 | 456.6 | 441.9 | 400.2
2054 | 1956 | 525.9 | 473.4 | 503.5 | 474.7 | 469.4 | 468.7 | 460.1 | 456.6 | 442 | 400.2
2055 | 1957 | 526 | 473.4 | 503.5 | 474.8 | 469.5 | 468.8 | 460.2 | 456.7 | 442 | 400.3
2056 | 1958 | 526 | 473.4 | 503.5 | 474.8 | 469.5 | 468.8 | 460.3 | 456.8 | 442.1 | 400.4
2057 | 1959 | 526 | 473.5 | 503.5 | 474.8 | 469.6 | 468.9 | 460.3 | 456.9 | 442.2 | 400.5
2058 | 1960 | 526 | 473.5 | 503.5 | 474.8 | 469.6 | 468.9 | 460.4 | 456.9 | 442.3 | 400.5
2059 | 1961 | 526 | 473.5 | 503.5 | 474.8 | 469.7 | 469 | 460.4 | 456.9 | 442.3 | 400.6
2060 | 1962 | 526 | 473.6 | 503.4 | 474.9 | 469.7 | 469.1 | 460.5 | 457 | 442.4 | 400.7
2061 | 1963 | 526.1 | 473.5 | 503.6 | 474.9 | 469.8 | 469.1 | 460.5 | 457.1 | 442.4 | 400.8
2062 | 1964 | 526.1 | 473.5 | 503.7 | 474.9 | 470 | 469.2 | 460.6 | 457.1 | 442.3 | 400.9
2063 | 1965 | 526.1 | 473.6 | 503.6 | 474.9 | 469.9 | 469.2 | 460.6 | 457.2 | 442.5 | 400.9
2064 | 1966 | 526.1 | 474.3 | 502.1 | 475.5 | 405.4 | 404 | 391.6 | 388.3 | 365.4 | 342.8
2065 | 1967 | 526.1 | 475.3 | 500.1 | 476.3 | 242.1 | 246.1 | 229.4 | 235.5 | 162.2 | 201.2
2066 | 1968 | 526.2 | 473.5 | 503.7 | 475 | 470 | 469.2 | 460.7 | 457.3 | 442.3 | 401.1
2067 | 1969 | 524.9 | 482 | 485.8 | 482 | 294.1 | 291 | 279.8 | 278.7 | 196.4 | 244.1
2068 | 1970 | 524.7 | 483.2 | 483 | 483 | 311.8 | 306.4 | 294.8 | 292.7 | 222.6 | 257.8
2069 | 1971 | 526.3 | 473.6 | 503.8 | 475 | 470.4 | 469.4 | 460.9 | 457.7 | 442.6 | 401.4
2070 | 1972 | 526.2 | 473.6 | 503.7 | 475 | 470.3 | 469.5 | 461 | 457.9 | 442.7 | 401.4
2071 | 1973 | 526.2 | 473.6 | 503.7 | 475.1 | 470.3 | 469.5 | 461.1 | 458 | 442.7 | 401.4
2072 | 1974 | 526.3 | 473.7 | 503.7 | 475.1 | 470.3 | 469.6 | 461.1 | 458.1 | 442.7 | 401.5
2073 | 1975 | 526.2 | 473.7 | 503.7 | 475.1 | 470.4 | 469.6 | 461.2 | 458.1 | 442.7 | 401.6
2074 | 1976 | 526.2 | 473.7 | 503.7 | 475.1 | 470.4 | 469.7 | 461.2 | 458.1 | 442.8 | 401.7
2075 | 1977 | 526.2 | 473.8 | 503.6 | 475.2 | 466.6 | 457.5 | 454.8 | 446.4 | 425 | 395.9
2076 | 1978 | 525.1 | 481.5 | 487.2 | 481.6 | 202.4 | 173.2 | 181.1 | 173.7 | 127.6 | 155.8
2077 | 1979 | 526.2 | 473.7 | 503.8 | 475.2 | 469.9 | 469.1 | 460.6 | 457.4 | 442 | 401.4
2078 | 1980 | 526.2 | 473.7 | 503.8 | 475.2 | 470.6 | 469.8 | 461.4 | 458.2 | 443.1 | 401.9
2079 | 1981 | 526.2 | 473.8 | 503.8 | 475.2 | 470.6 | 469.9 | 461.5 | 458.4 | 443.1 | 402
2080 | 1982 | 526.2 | 473.8 | 503.8 | 475.3 | 470.6 | 469.9 | 461.5 | 458.5 | 443.2 | 402.1
2081 | 1983 | 526.2 | 473.8 | 503.8 | 475.3 | 470.7 | 469.9 | 461.6 | 458.6 | 443.3 | 402.1
2082 | 1984 | 526.2 | 473.8 | 503.8 | 475.3 | 470.7 | 470 | 461.6 | 458.7 | 443.4 | 402.2
2083 | 1985 | 526.2 | 473.9 | 503.8 | 475.3 | 470.7 | 470 | 461.7 | 458.7 | 443.5 | 402.3
2084 | 1986 | 526.3 | 473.9 | 503.8 | 475.4 | 470.8 | 470.1 | 461.7 | 458.7 | 443.6 | 402.4
2085 | 1987 | 526.3 | 473.9 | 503.8 | 475.4 | 470.8 | 470.1 | 461.8 | 458.7 | 443.7 | 402.4
2086 | 1988 | 526.3 | 473.9 | 503.8 | 475.4 | 470.9 | 470.2 | 461.8 | 458.8 | 443.8 | 402.5
2087 | 1989 | 526.3 | 473.9 | 503.9 | 475.4 | 470.9 | 470.2 | 461.9 | 458.9 | 443.9 | 402.6
2088 | 1990 | 526.3 | 473.9 | 503.9 | 475.4 | 471 | 470.2 | 461.9 | 458.9 | 444 | 402.7
2089 | 1991 | 526.3 | 474 | 503.9 | 475.4 | 471 | 470.3 | 462 | 458.9 | 444.1 | 402.7
2090 | 1992 | 526.3 | 474 | 503.9 | 475.5 | 471 | 470.3 | 462 | 458.9 | 444.2 | 402.8
2091 | 1993 | 526.3 | 474 | 503.9 | 475.5 | 471.1 | 470.3 | 462.1 | 458.9 | 444.3 | 402.9
2092 | 1994 | 526.3 | 474 | 504 | 475.5 | 471.1 | 470.4 | 462.1 | 459 | 444.4 | 402.9
2093 | 1995 | 526.3 | 474 | 503.9 | 475.5 | 471.1 | 470.4 | 462.2 | 459.1 | 444.5 | 403
2094 | 1996 | 526.2 | 474 | 503.9 | 475.5 | 471.2 | 470.5 | 462.2 | 459.1 | 444.6 | 403.1
2095 | 1997 | 526.2 | 474.1 | 503.9 | 475.5 | 471.2 | 470.5 | 462.3 | 459.1 | 444.8 | 403.1
2096 | 1998 | 526.2 | 474.1 | 503.9 | 475.6 | 471.3 | 470.5 | 462.3 | 459 | 444.9 | 403.2
2097 | 1999 | 526.2 | 474.1 | 504 | 475.6 | 471.3 | 470.6 | 462.4 | 459 | 445 | 403.2
2098 | 2000 | 526.2 | 474.2 | 503.7 | 475.7 | 471.4 | 470.6 | 462.4 | 459 | 445.1 | 403.4
2099 | 2001 | 526.2 | 474.1 | 504 | 475.7 | 471.4 | 470.6 | 462.4 | 458.9 | 445.2 | 403.4
2100 | 2002 | 526.2 | 474.1 | 504.1 | 475.7 | 471.4 | 470.7 | 462.5 | 458.9 | 445.3 | 403.4
2101 | 2003 | 526.2 | 474.1 | 504.1 | 475.7 | 471.5 | 470.7 | 462.5 | 459 | 445.3 | 403.5
2102 | 2004 | 526.2 | 474.2 | 504 | 475.7 | 471.5 | 470.8 | 462.6 | 459.1 | 445.4 | 403.6
2103 | 2005 | 526.1 | 474.2 | 504 | 475.7 | 471.5 | 470.8 | 462.6 | 459.1 | 445.5 | 403.6
2104 | 2006 | 526.1 | 474.2 | 504.1 | 475.7 | 471.6 | 470.8 | 462.7 | 459.2 | 445.6 | 403.7
2105 | 2007 | 526.1 | 474.2 | 504 | 475.8 | 471.6 | 470.9 | 462.7 | 459.3 | 445.7 | 403.8
2106 | 2008 | 526.1 | 474.2 | 504.1 | 475.8 | 471.6 | 470.9 | 462.8 | 459.3 | 445.8 | 403.8
2107 | 2009 | 526 | 474.3 | 504.1 | 475.8 | 471.7 | 470.9 | 462.8 | 459.3 | 445.8 | 403.9
2108 | 2010 | 526 | 474.3 | 504.1 | 475.8 | 471.7 | 471 | 462.8 | 459.4 | 445.9 | 403.9
2109 | 2011 | 526 | 474.3 | 504.1 | 475.8 | 471.7 | 471 | 462.9 | 459.5 | 446 | 404
2110 | 2012 | 526.1 | 474.3 | 504.1 | 475.9 | 471.8 | 471 | 462.9 | 459.6 | 446 | 404.1
2111 | 2013 | 526.1 | 474.3 | 504.2 | 475.9 | 471.8 | 471.1 | 463 | 459.6 | 446.1 | 404.2
2112 | 2014 | 526 | 474.3 | 504.2 | 475.9 | 471.9 | 471.1 | 463 | 459.7 | 446.2 | 404.2
2113 | 2015 | 526.1 | 474.3 | 504.2 | 475.9 | 471.9 | 471.2 | 463.1 | 459.7 | 446.2 | 404.3
2114 | 2016 | 526.1 | 474.4 | 504.2 | 475.9 | 472 | 471.2 | 463.1 | 459.8 | 446.3 | 404.4
2115 | 2017 | 526.1 | 474.4 | 504.2 | 475.9 | 472 | 471.2 | 463.2 | 459.9 | 446.4 | 404.5
2116 | 2018 | 526 | 474.4 | 504.1 | 476 | 472 | 471.3 | 463.2 | 459.9 | 446.4 | 404.5
2117 | 2019 | 526 | 474.4 | 504.2 | 476 | 472.1 | 471.3 | 463.2 | 459.9 | 446.5 | 404.6
2118 | 2020 | 526 | 474.4 | 504.2 | 476 | 472.1 | 471.4 | 463.3 | 460 | 446.5 | 404.7
2119 | 2021 | 526 | 474.4 | 504.2 | 476 | 472.2 | 471.4 | 463.3 | 460.1 | 446.6 | 404.7
2120 | 2022 | 526 | 474.5 | 504.2 | 476 | 472.2 | 471.4 | 463.4 | 460.1 | 446.7 | 404.8
2121 | 2023 | 526.1 | 474.5 | 504.2 | 476 | 472.3 | 471.5 | 463.4 | 460.2 | 446.7 | 404.8
2122 | 2024 | 526.1 | 474.5 | 504.2 | 476.1 | 472.3 | 471.5 | 463.5 | 460.2 | 446.8 | 404.9
2123 | 2025 | 526.1 | 474.5 | 504.3 | 476.1 | 472.3 | 471.5 | 463.5 | 460.3 | 446.9 | 405
2124 | 2026 | 526.1 | 474.5 | 504.3 | 476.1 | 472.4 | 471.6 | 463.6 | 460.4 | 447 | 405
2125 | 2027 | 526.1 | 474.5 | 504.3 | 476.1 | 472.4 | 471.6 | 463.6 | 460.5 | 447 | 405.1
2126 | 2028 | 526.1 | 474.5 | 504.3 | 476.1 | 472.5 | 471.6 | 463.6 | 460.5 | 447.1 | 405.1
2127 | 2029 | 526.1 | 474.6 | 504.4 | 476.1 | 472.5 | 471.7 | 463.7 | 460.6 | 447.1 | 405.2
2128 | 2030 | 526.2 | 474.6 | 504.4 | 476.2 | 472.6 | 471.7 | 463.7 | 460.7 | 447.2 | 405.2
2129 | 2031 | 526.2 | 474.6 | 504.4 | 476.2 | 472.6 | 471.8 | 463.8 | 460.7 | 447.2 | 405.3
2130 | 2032 | 526.1 | 474.6 | 504.3 | 476.2 | 472.6 | 471.8 | 463.8 | 460.7 | 447.2 | 405.4
2131 | 2033 | 526.1 | 474.6 | 504.3 | 476.2 | 472.7 | 471.8 | 463.9 | 460.8 | 447.3 | 405.4
2132 | 2034 | 526.1 | 474.6 | 504.4 | 476.2 | 472.7 | 471.9 | 463.9 | 460.8 | 447.3 | 405.5
2133 | 2035 | 526.1 | 474.7 | 504.4 | 476.3 | 472.8 | 471.9 | 464 | 460.9 | 447.4 | 405.5
2134 | 2036 | 526.1 | 474.7 | 504.4 | 476.3 | 472.8 | 471.9 | 464 | 460.9 | 447.4 | 405.6
2135 | 2037 | 526 | 474.7 | 504.4 | 476.3 | 472.8 | 472 | 464 | 460.9 | 447.5 | 405.6
2136 | 2038 | 526 | 474.7 | 504.4 | 476.3 | 472.9 | 472 | 464.1 | 460.9 | 447.5 | 405.7
2137 | 2039 | 526 | 474.7 | 504.5 | 476.3 | 472.9 | 472 | 464.1 | 461 | 447.6 | 405.8
2138 | 2040 | 526 | 474.7 | 504.5 | 476.4 | 472.9 | 472.1 | 464.2 | 461 | 447.6 | 405.8
2139 | 2041 | 526 | 474.7 | 504.5 | 476.4 | 473 | 472.1 | 464.2 | 461 | 447.7 | 405.9
2140 | 2042 | 526 | 474.8 | 504.5 | 476.4 | 473 | 472.1 | 464.2 | 461.1 | 447.7 | 405.9
2141 | 2043 | 526.1 | 474.8 | 504.5 | 476.4 | 473.1 | 472.2 | 464.3 | 461.2 | 447.8 | 406
2142 | 2044 | 526.1 | 474.8 | 504.5 | 476.4 | 473.1 | 472.2 | 464.3 | 461.3 | 447.8 | 406
2143 | 2045 | 526.1 | 474.8 | 504.5 | 476.4 | 473.1 | 472.2 | 464.4 | 461.3 | 447.9 | 406.1
2144 | 2046 | 526.1 | 474.8 | 504.5 | 476.5 | 473.2 | 472.3 | 464.4 | 461.4 | 447.9 | 406.1
2145 | 2047 | 526.1 | 474.8 | 504.5 | 476.5 | 473.2 | 472.3 | 464.5 | 461.4 | 448 | 406.2
2146 | 2048 | 526.1 | 474.8 | 504.5 | 476.5 | 473.3 | 472.4 | 464.5 | 461.4 | 448 | 406.2
2147 | 2049 | 526.1 | 474.9 | 504.5 | 476.5 | 473.3 | 472.4 | 464.5 | 461.4 | 448.1 | 406.3
2148 | 2050 | 526.1 | 474.9 | 504.6 | 476.5 | 473.4 | 472.4 | 464.6 | 461.4 | 448.2 | 406.3
2149 | 2051 | 526.1 | 474.9 | 504.6 | 476.5 | 473.4 | 472.5 | 464.6 | 461.5 | 448.2 | 406.4
2150 | 2052 | 526.1 | 474.9 | 504.6 | 476.6 | 473.4 | 472.5 | 464.7 | 461.5 | 448.3 | 406.4
2151 | 2053 | 526.1 | 474.9 | 504.6 | 476.6 | 473.5 | 472.5 | 464.7 | 461.6 | 448.4 | 406.5
2152 | 2054 | 526.1 | 474.9 | 504.7 | 476.6 | 473.5 | 472.6 | 464.8 | 461.6 | 448.4 | 406.5
2153 | 2055 | 526.2 | 474.9 | 504.7 | 476.6 | 473.6 | 472.6 | 464.8 | 461.6 | 448.5 | 406.6
2154 | 2056 | 526.2 | 475 | 504.7 | 476.6 | 473.6 | 472.7 | 464.9 | 461.7 | 448.6 | 406.6
2155 | 2057 | 526.2 | 475 | 504.6 | 476.7 | 473.7 | 472.7 | 464.9 | 461.7 | 448.6 | 406.6
2156 | 2058 | 526.2 | 475 | 504.6 | 476.7 | 473.7 | 472.7 | 464.9 | 461.7 | 448.7 | 406.7
2157 | 2059 | 526.2 | 475 | 504.7 | 476.7 | 473.7 | 472.8 | 465 | 461.8 | 448.7 | 406.7
2158 | 2060 | 526.3 | 475 | 504.7 | 476.7 | 473.8 | 472.8 | 465 | 461.8 | 448.8 | 406.8
2159 | 2061 | 526.3 | 475 | 504.7 | 476.7 | 473.8 | 472.8 | 465.1 | 461.8 | 448.9 | 406.8
2160 | 2062 | 526.3 | 475 | 504.7 | 476.7 | 473.9 | 472.9 | 465.1 | 461.9 | 448.9 | 406.9
2161 | 2063 | 526.2 | 475.1 | 504.7 | 476.8 | 473.9 | 472.9 | 465.2 | 462 | 449 | 406.9
2162 | 2064 | 526.2 | 475.1 | 504.7 | 476.8 | 473.9 | 473 | 465.2 | 462.1 | 449 | 406.9
2163 | 2065 | 526.3 | 475.1 | 504.7 | 476.8 | 474 | 473 | 465.2 | 462.2 | 449.1 | 407
2164 | 2066 | 526.3 | 475.1 | 504.8 | 476.8 | 474 | 473 | 465.3 | 462.2 | 449.1 | 407
2165 | 2067 | 526.3 | 475.1 | 504.7 | 476.8 | 474.1 | 473.1 | 465.3 | 462.3 | 449.2 | 407.1
2166 | 2068 | 526.2 | 475.1 | 504.7 | 476.9 | 474.1 | 473.1 | 465.4 | 462.3 | 449.2 | 407.1
2167 | 2069 | 526.2 | 475.2 | 504.7 | 476.9 | 474.1 | 473.1 | 465.4 | 462.4 | 449.3 | 407.2
2168 | 2070 | 526.2 | 475.2 | 504.8 | 476.9 | 474.2 | 473.2 | 465.4 | 462.5 | 449.4 | 407.2
2169 | 2071 | 526.2 | 475.2 | 504.8 | 476.9 | 474.2 | 473.2 | 465.5 | 462.6 | 449.4 | 407.2
2170 | 2072 | 526.2 | 475.2 | 504.9 | 476.9 | 474.2 | 473.2 | 465.5 | 462.7 | 449.5 | 407.3
2171 | 2073 | 526.2 | 475.2 | 504.9 | 476.9 | 474.3 | 473.3 | 465.6 | 462.7 | 449.5 | 407.3
2172 | 2074 | 526.1 | 475.2 | 504.9 | 476.9 | 474.3 | 473.3 | 465.6 | 462.8 | 449.6 | 407.4
2173 | 2075 | 526.1 | 475.2 | 504.9 | 476.9 | 474.4 | 473.3 | 465.6 | 462.8 | 449.6 | 407.5
2174 | 2076 | 526.1 | 475.2 | 504.9 | 477 | 474.4 | 473.4 | 465.7 | 462.9 | 449.7 | 407.5
2175 | 2077 | 526.1 | 475.2 | 504.9 | 477 | 474.4 | 473.4 | 465.7 | 462.9 | 449.7 | 407.5
2176 | 2078 | 526.1 | 475.3 | 504.9 | 477 | 474.5 | 473.5 | 465.8 | 462.8 | 449.8 | 407.6
2177 | 2079 | 526.1 | 475.3 | 504.9 | 477 | 474.5 | 473.5 | 465.8 | 462.8 | 449.8 | 407.6
2178 | 2080 | 526 | 475.3 | 504.9 | 477 | 474.6 | 473.6 | 465.8 | 462.8 | 449.9 | 407.7
2179 | 2081 | 526 | 475.3 | 504.9 | 477 | 474.6 | 473.6 | 465.9 | 462.9 | 449.9 | 407.7
2180 | 2082 | 526 | 475.3 | 504.9 | 477 | 474.6 | 473.6 | 465.9 | 463 | 450 | 407.8
2181 | 2083 | 526 | 475.3 | 504.9 | 477.1 | 474.7 | 473.7 | 466 | 463 | 450 | 407.8
2182 | 2084 | 526 | 475.4 | 504.9 | 477.1 | 474.7 | 473.7 | 466 | 463.1 | 450.1 | 407.9
2183 | 2085 | 526 | 475.4 | 505 | 477.1 | 474.7 | 473.7 | 466.1 | 463.1 | 450.1 | 407.9
2184 | 2086 | 526 | 475.4 | 505 | 477.1 | 474.8 | 473.8 | 466.1 | 463.2 | 450.1 | 408
2185 | 2087 | 526 | 475.4 | 505 | 477.1 | 474.8 | 473.8 | 466.1 | 463.3 | 450.2 | 408
2186 | 2088 | 526 | 475.5 | 504.8 | 477.2 | 474.9 | 473.9 | 466.1 | 463.3 | 450.2 | 408.2
2187 | 2089 | 526 | 475.4 | 504.9 | 477.2 | 474.9 | 473.9 | 466.2 | 463.4 | 450.2 | 408.2
2188 | 2090 | 526 | 475.4 | 505 | 477.2 | 474.9 | 473.9 | 466.3 | 463.5 | 450.3 | 408.2
2189 | 2091 | 526 | 475.5 | 504.9 | 477.2 | 475 | 474 | 466.3 | 463.5 | 450.3 | 408.3
2190 | 2092 | 526 | 475.5 | 505 | 477.2 | 475 | 474 | 466.4 | 463.6 | 450.4 | 408.3
2191 | 2093 | 526 | 475.5 | 505.1 | 477.2 | 475 | 474 | 466.4 | 463.6 | 450.4 | 408.4
2192 | 2094 | 526 | 475.5 | 505 | 477.2 | 475.1 | 474.1 | 466.4 | 463.6 | 450.4 | 408.4
2193 | 2095 | 526 | 475.5 | 505 | 477.2 | 475.1 | 474.1 | 466.5 | 463.7 | 450.5 | 408.5
2194 | 2096 | 526 | 475.5 | 505.1 | 477.3 | 475.2 | 474.1 | 466.5 | 463.7 | 450.5 | 408.5
2195 | 2097 | 526 | 475.5 | 505.1 | 477.3 | 475.2 | 474.2 | 466.6 | 463.8 | 450.6 | 408.6
2196 | 2098 | 526 | 475.5 | 505.1 | 477.3 | 475.2 | 474.2 | 466.6 | 463.8 | 450.6 | 408.6
2197 | 2099 | 526 | 475.6 | 505.1 | 477.3 | 475.3 | 474.3 | 466.6 | 463.9 | 450.7 | 408.7
2198 | 2100 | 526 | 475.6 | 505.1 | 477.3 | 475.3 | 474.3 | 466.7 | 463.9 | 450.7 | 408.7
2199 | 2101 | 526 | 475.6 | 505.1 | 477.3 | 475.4 | 474.3 | 466.8 | 464 | 450.7 | 408.8
2200 | 2102 | 526 | 475.6 | 505.1 | 477.4 | 475.4 | 474.4 | 466.8 | 464.1 | 450.8 | 408.8
2201 | 2103 | 526 | 475.6 | 505.1 | 477.4 | 475.4 | 474.4 | 466.9 | 464.1 | 450.8 | 408.9
2202 | 2104 | 526 | 475.6 | 505.1 | 477.4 | 475.5 | 474.5 | 466.9 | 464.1 | 450.9 | 408.9
2203 | 2105 | 526 | 475.6 | 505.1 | 477.4 | 475.5 | 474.5 | 466.9 | 464.2 | 450.9 | 409
2204 | 2106 | 526 | 475.7 | 505.1 | 477.4 | 475.5 | 474.5 | 467 | 464.2 | 450.9 | 409
2205 | 2107 | 526 | 475.7 | 505.2 | 477.4 | 475.6 | 474.6 | 467 | 464.2 | 451 | 409.1
2206 | 2108 | 526 | 475.7 | 505.2 | 477.5 | 475.6 | 474.6 | 467.1 | 464.4 | 451 | 409.2
2207 | 2109 | 526.1 | 475.7 | 505.2 | 477.5 | 475.7 | 474.6 | 467.1 | 464.5 | 451.1 | 409.2
2208 | 2110 | 526.1 | 475.7 | 505.2 | 477.5 | 475.7 | 474.7 | 467.2 | 464.5 | 451.1 | 409.3
2209 | 2111 | 526.1 | 475.7 | 505.3 | 477.5 | 475.7 | 474.7 | 467.2 | 464.5 | 451.1 | 409.4
2210 | 2112 | 526.1 | 475.7 | 505.3 | 477.5 | 475.8 | 474.8 | 467.3 | 464.5 | 451.2 | 409.4
2211 | 2113 | 526 | 476.1 | 504.6 | 477.8 | 476 | 474.9 | 467.3 | 464.6 | 451.2 | 409.7
2212 | 2114 | 526.1 | 475.8 | 505.1 | 477.6 | 475.9 | 474.9 | 467.3 | 464.7 | 451.2 | 409.6
2213 | 2115 | 526.1 | 475.8 | 505.3 | 477.6 | 475.9 | 474.9 | 467.4 | 464.7 | 451.3 | 409.6
2214 | 2116 | 526.1 | 475.8 | 505.3 | 477.6 | 476 | 474.9 | 467.4 | 464.7 | 451.3 | 409.7
2215 | 2117 | 526.1 | 475.8 | 505.3 | 477.6 | 476 | 475 | 467.5 | 464.8 | 451.4 | 409.7
2216 | 2118 | 526.1 | 475.9 | 505.3 | 477.6 | 476 | 475 | 467.5 | 464.8 | 451.4 | 409.8
2217 | 2119 | 526 | 475.9 | 505.3 | 477.6 | 476.1 | 475.1 | 467.6 | 464.9 | 451.4 | 409.9
2218 | 2120 | 526 | 475.9 | 505.3 | 477.6 | 476.1 | 475.1 | 467.6 | 464.9 | 451.5 | 409.9
2219 | 2121 | 526 | 475.9 | 505.3 | 477.7 | 476.2 | 475.2 | 467.7 | 465 | 451.5 | 410
2220 | 2122 | 526 | 475.9 | 505.4 | 477.7 | 476.2 | 475.2 | 467.7 | 465 | 451.5 | 410.1
2221 | 2123 | 526 | 475.9 | 505.3 | 477.7 | 476.2 | 475.2 | 467.8 | 465.1 | 451.6 | 410.1
2222 | 2124 | 525.9 | 475.9 | 505.3 | 477.7 | 476.3 | 475.3 | 467.8 | 465.1 | 451.6 | 410.2
2223 | 2125 | 525.9 | 475.9 | 505.4 | 477.7 | 476.3 | 475.3 | 467.9 | 465.2 | 451.7 | 410.2
2224 | 2126 | 525.9 | 476 | 505.4 | 477.7 | 476.4 | 475.4 | 467.9 | 465.2 | 451.7 | 410.3
2225 | 2127 | 525.9 | 476 | 505.4 | 477.8 | 476.4 | 475.4 | 467.9 | 465.2 | 451.7 | 410.4
2226 | 2128 | 525.9 | 476 | 505.4 | 477.8 | 476.4 | 475.5 | 468 | 465.3 | 451.8 | 410.4
2227 | 2129 | 525.9 | 476 | 505.4 | 477.8 | 476.5 | 475.5 | 468 | 465.3 | 451.8 | 410.5
2228 | 2130 | 525.9 | 476 | 505.4 | 477.8 | 476.5 | 475.5 | 468.1 | 465.3 | 451.8 | 410.5
2229 | 2131 | 525.9 | 476 | 505.4 | 477.8 | 476.6 | 475.6 | 468.1 | 465.4 | 451.9 | 410.6
2230 | 2132 | 525.8 | 476 | 505.4 | 477.9 | 476.6 | 475.6 | 468.2 | 465.5 | 451.9 | 410.7
2231 | 2133 | 525.8 | 476.1 | 505.4 | 477.9 | 476.7 | 475.7 | 468.2 | 465.6 | 451.9 | 410.8
2232 | 2134 | 525.8 | 476.1 | 505.4 | 477.9 | 476.7 | 475.7 | 468.3 | 465.6 | 452 | 410.8
2233 | 2135 | 525.8 | 476.1 | 505.5 | 477.9 | 476.8 | 475.8 | 468.3 | 465.7 | 452 | 410.9
2234 | 2136 | 525.8 | 476.1 | 505.5 | 477.9 | 476.8 | 475.8 | 468.4 | 465.7 | 452 | 411
2235 | 2137 | 525.8 | 476.1 | 505.5 | 477.9 | 476.8 | 475.8 | 468.4 | 465.8 | 452.1 | 411
2236 | 2138 | 525.8 | 476.1 | 505.5 | 477.9 | 476.9 | 475.9 | 468.5 | 465.8 | 452.1 | 411.1
2237 | 2139 | 525.9 | 476.1 | 505.5 | 478 | 476.9 | 475.9 | 468.5 | 465.9 | 452.1 | 411.1
2238 | 2140 | 525.9 | 476.1 | 505.5 | 478 | 476.9 | 476 | 468.6 | 465.8 | 452.2 | 411.2
2239 | 2141 | 525.9 | 476.1 | 505.5 | 478 | 477 | 476 | 468.6 | 465.9 | 452.2 | 411.3
2240 | 2142 | 525.9 | 476.2 | 505.5 | 478 | 477 | 476 | 468.6 | 466 | 452.2 | 411.3
2241 | 2143 | 525.9 | 476.2 | 505.5 | 478 | 477.1 | 476.1 | 468.7 | 466.2 | 452.2 | 411.4
2242 | 2144 | 525.8 | 476.2 | 505.5 | 478 | 477.1 | 476.1 | 468.7 | 466.3 | 452.3 | 411.4
2243 | 2145 | 525.8 | 476.2 | 505.5 | 478 | 477.1 | 476.2 | 468.8 | 466.4 | 452.3 | 411.5
2244 | 2146 | 525.8 | 476.2 | 505.6 | 478.1 | 477.2 | 476.2 | 468.8 | 466.4 | 452.3 | 411.6
2245 | 2147 | 525.8 | 476.2 | 505.5 | 478.1 | 477.2 | 476.2 | 468.9 | 466.3 | 452.4 | 411.6
2246 | 2148 | 525.8 | 476.2 | 505.6 | 478.1 | 477.2 | 476.3 | 468.9 | 466.4 | 452.4 | 411.7
2247 | 2149 | 525.9 | 476.3 | 505.6 | 478.1 | 477.3 | 476.3 | 469 | 466.5 | 452.4 | 411.7
2248 | 2150 | 525.9 | 476.3 | 505.6 | 478.1 | 477.3 | 476.3 | 469 | 466.5 | 452.5 | 411.8
2249 | 2151 | 525.9 | 476.3 | 505.6 | 478.1 | 477.4 | 476.4 | 469.1 | 466.6 | 452.5 | 411.8
2250 | 2152 | 525.9 | 476.3 | 505.7 | 478.2 | 477.4 | 476.4 | 469.1 | 466.7 | 452.5 | 411.9
2251 | 2153 | 525.9 | 476.3 | 505.6 | 478.2 | 477.4 | 476.5 | 469.1 | 466.7 | 452.6 | 412
2252 | 2154 | 525.9 | 476.3 | 505.7 | 478.2 | 477.5 | 476.5 | 469.2 | 466.7 | 452.6 | 412
2253 | 2155 | 525.9 | 476.4 | 505.6 | 478.2 | 477.5 | 476.5 | 469.2 | 466.8 | 452.6 | 412.1
2254 | 2156 | 525.9 | 476.4 | 505.6 | 478.2 | 477.5 | 476.6 | 469.3 | 466.8 | 452.7 | 412.1
2255 | 2157 | 525.9 | 476.4 | 505.7 | 478.2 | 477.6 | 476.6 | 469.3 | 466.9 | 452.7 | 412.2
2256 | 2158 | 525.9 | 476.4 | 505.7 | 478.2 | 477.6 | 476.7 | 469.4 | 466.8 | 452.7 | 412.3
2257 | 2159 | 525.9 | 476.4 | 505.7 | 478.3 | 477.7 | 476.7 | 469.4 | 466.9 | 452.8 | 412.3
2258 | 2160 | 525.9 | 476.4 | 505.7 | 478.3 | 477.7 | 476.7 | 469.5 | 467 | 452.8 | 412.4
2259 | 2161 | 525.9 | 476.4 | 505.7 | 478.3 | 477.7 | 476.8 | 469.5 | 467 | 452.9 | 412.4
2260 | 2162 | 525.9 | 476.4 | 505.7 | 478.3 | 477.8 | 476.8 | 469.5 | 467 | 452.9 | 412.5
2261 | 2163 | 525.9 | 476.5 | 505.7 | 478.3 | 477.8 | 476.8 | 469.6 | 467.1 | 452.9 | 412.5
2262 | 2164 | 525.9 | 476.5 | 505.8 | 478.3 | 477.8 | 476.9 | 469.6 | 467.2 | 453 | 412.6
2263 | 2165 | 525.9 | 476.5 | 505.8 | 478.3 | 477.9 | 476.9 | 469.7 | 467.3 | 453 | 412.6
2264 | 2166 | 525.9 | 476.5 | 505.8 | 478.3 | 477.9 | 477 | 469.7 | 467.3 | 453 | 412.7
2265 | 2167 | 526 | 476.5 | 505.8 | 478.4 | 478 | 477 | 469.8 | 467.3 | 453.1 | 412.8
2266 | 2168 | 526 | 476.5 | 505.8 | 478.4 | 478 | 477.1 | 469.8 | 467.4 | 453.1 | 412.8
2267 | 2169 | 526 | 476.5 | 505.8 | 478.4 | 478.1 | 477.1 | 469.9 | 467.4 | 453.2 | 412.9
2268 | 2170 | 526 | 476.6 | 505.8 | 478.4 | 478.1 | 477.2 | 469.9 | 467.4 | 453.2 | 413
2269 | 2171 | 525.9 | 476.8 | 505.3 | 478.6 | 478.3 | 477.3 | 470 | 467.3 | 453.2 | 413.1
2270 | 2172 | 526 | 476.6 | 505.9 | 478.4 | 478.2 | 477.2 | 470 | 467.4 | 453.3 | 413.1
2271 | 2173 | 526.1 | 476.6 | 505.9 | 478.4 | 478.3 | 477.3 | 470.1 | 467.4 | 453.3 | 413.2
2272 | 2174 | 526.1 | 476.6 | 505.9 | 478.4 | 478.3 | 477.3 | 470.1 | 467.5 | 453.4 | 413.2
2273 | 2175 | 526.1 | 476.6 | 505.9 | 478.5 | 478.3 | 477.3 | 470.2 | 467.5 | 453.4 | 413.3
2274 | 2176 | 526.1 | 476.6 | 505.9 | 478.5 | 478.4 | 477.4 | 470.2 | 467.6 | 453.4 | 413.4
2275 | 2177 | 526.1 | 476.6 | 505.9 | 478.5 | 478.4 | 477.4 | 470.2 | 467.7 | 453.5 | 413.4
2276 | 2178 | 526.1 | 476.6 | 506 | 478.5 | 478.4 | 477.4 | 470.3 | 467.8 | 453.5 | 413.5
2277 | 2179 | 526.1 | 476.7 | 506 | 478.5 | 478.4 | 477.5 | 470.3 | 467.8 | 453.6 | 413.5
2278 | 2180 | 526.1 | 476.7 | 506 | 478.5 | 478.5 | 477.5 | 470.4 | 467.9 | 453.6 | 413.6
2279 | 2181 | 526.2 | 476.7 | 506 | 478.5 | 478.5 | 477.6 | 470.4 | 467.9 | 453.6 | 413.7
2280 | 2182 | 526.2 | 476.7 | 506 | 478.6 | 478.5 | 477.6 | 470.5 | 468 | 453.7 | 413.7
2281 | 2183 | 526.2 | 476.7 | 506 | 478.6 | 478.6 | 477.6 | 470.5 | 468 | 453.7 | 413.8
2282 | 2184 | 526.2 | 476.7 | 506.1 | 478.6 | 478.6 | 477.7 | 470.5 | 468 | 453.8 | 413.9
2283 | 2185 | 526.3 | 476.7 | 506 | 478.6 | 478.6 | 477.7 | 470.6 | 468.1 | 453.8 | 413.9
2284 | 2186 | 526.2 | 476.7 | 506 | 478.6 | 478.7 | 477.8 | 470.6 | 468.2 | 453.9 | 414
2285 | 2187 | 526.3 | 476.8 | 506.1 | 478.6 | 478.7 | 477.8 | 470.7 | 468.3 | 453.9 | 414
2286 | 2188 | 526.3 | 476.8 | 506.1 | 478.6 | 478.8 | 477.8 | 470.7 | 468.4 | 453.9 | 414.1
2287 | 2189 | 526.3 | 476.8 | 506.1 | 478.6 | 478.8 | 477.9 | 470.8 | 468.5 | 454 | 414.2
2288 | 2190 | 526.3 | 476.8 | 506.1 | 478.6 | 478.9 | 477.9 | 470.8 | 468.5 | 454 | 414.2
2289 | 2191 | 526.2 | 476.8 | 506.1 | 478.6 | 478.9 | 477.9 | 470.9 | 468.6 | 454.1 | 414.3
2290 | 2192 | 526.2 | 476.8 | 506.1 | 478.6 | 478.9 | 478 | 470.9 | 468.6 | 454.1 | 414.4
2291 | 2193 | 526.2 | 476.8 | 506.2 | 478.7 | 479 | 478 | 471 | 468.6 | 454.1 | 414.4
2292 | 2194 | 526.2 | 476.9 | 506.1 | 478.7 | 479 | 478.1 | 471 | 468.6 | 454.2 | 414.5
2293 | 2195 | 526.2 | 476.9 | 506.1 | 478.7 | 479 | 478.1 | 471 | 468.6 | 454.2 | 414.6
2294 | 2196 | 526.3 | 476.9 | 506.1 | 478.7 | 479.1 | 478.1 | 471.1 | 468.7 | 454.2 | 414.6
2295 | 2197 | 526.3 | 476.9 | 506.1 | 478.7 | 479.1 | 478.2 | 471.1 | 468.7 | 454.3 | 414.7
2296 | 2198 | 526.2 | 476.9 | 506.2 | 478.7 | 479.2 | 478.2 | 471.2 | 468.8 | 454.3 | 414.8
2297 | 2199 | 526.2 | 476.9 | 506.2 | 478.7 | 479.2 | 478.3 | 471.2 | 468.9 | 454.3 | 414.8
2298 | 2200 | 526.2 | 476.9 | 506.2 | 478.8 | 479.2 | 478.3 | 471.3 | 469 | 454.4 | 414.9
2299 | 2201 | 526.2 | 477 | 506.3 | 478.8 | 479.3 | 478.4 | 471.3 | 469 | 454.4 | 414.9
2300 | 2202 | 526.2 | 477 | 506.3 | 478.8 | 479.3 | 478.4 | 471.4 | 469 | 454.4 | 415
2301 | 2203 | 526.2 | 477 | 506.3 | 478.8 | 479.4 | 478.4 | 471.4 | 469.1 | 454.5 | 415
2302 | 2204 | 526.1 | 477 | 506.2 | 478.8 | 479.4 | 478.5 | 471.5 | 469.2 | 454.5 | 415.1
2303 | 2205 | 526.1 | 477 | 506.2 | 478.8 | 479.4 | 478.5 | 471.5 | 469.3 | 454.5 | 415.1
2304 | 2206 | 526.1 | 477 | 506.2 | 478.8 | 479.5 | 478.5 | 471.5 | 469.3 | 454.6 | 415.1
2305 | 2207 | 526.1 | 477 | 506.2 | 478.8 | 479.5 | 478.5 | 471.6 | 469.3 | 454.6 | 415.2
2306 | 2208 | 526.1 | 477.1 | 506.2 | 478.9 | 479.5 | 478.6 | 471.6 | 469.3 | 454.6 | 415.3
2307 | 2209 | 526.2 | 477.1 | 506.3 | 478.9 | 479.6 | 478.6 | 471.7 | 469.3 | 454.7 | 415.3
2308 | 2210 | 526.2 | 477.1 | 506.3 | 478.9 | 479.6 | 478.6 | 471.7 | 469.4 | 454.7 | 415.4
2309 | 2211 | 526.2 | 477.1 | 506.3 | 478.9 | 479.7 | 478.7 | 471.8 | 469.4 | 454.7 | 415.5
2310 | 2212 | 526.2 | 477.1 | 506.3 | 478.9 | 479.7 | 478.7 | 471.8 | 469.4 | 454.8 | 415.6
2311 | 2213 | 526.2 | 477.1 | 506.3 | 478.9 | 479.7 | 478.8 | 471.9 | 469.4 | 454.8 | 415.6
2312 | 2214 | 526.2 | 477.1 | 506.3 | 478.9 | 479.8 | 478.8 | 471.9 | 469.4 | 454.9 | 415.7
2313 | 2215 | 526.2 | 477.2 | 506.4 | 479 | 479.8 | 478.8 | 471.9 | 469.5 | 454.9 | 415.7
2314 | 2216 | 526.2 | 477.2 | 506.4 | 479 | 479.8 | 478.9 | 472 | 469.6 | 454.9 | 415.7
2315 | 2217 | 526.2 | 477.2 | 506.3 | 479 | 479.9 | 478.9 | 472 | 469.7 | 455 | 415.8
2316 | 2218 | 526.3 | 477.2 | 506.4 | 479 | 479.9 | 478.9 | 472.1 | 469.7 | 455 | 415.8
2317 | 2219 | 526.3 | 477.2 | 506.4 | 479 | 479.9 | 479 | 472.1 | 469.7 | 455 | 415.9
2318 | 2220 | 526.3 | 477.2 | 506.4 | 479 | 480 | 479 | 472.2 | 469.7 | 455.1 | 415.9
2319 | 2221 | 526.3 | 477.2 | 506.4 | 479 | 480 | 479.1 | 472.2 | 469.7 | 455.1 | 416
2320 | 2222 | 526.3 | 477.2 | 506.4 | 479 | 480.1 | 479.1 | 472.2 | 469.7 | 455.2 | 416.1
2321 | 2223 | 526.3 | 477.3 | 506.5 | 479 | 480.1 | 479.1 | 472.3 | 469.6 | 455.2 | 416.1
2322 | 2224 | 526.4 | 477.3 | 506.4 | 479.1 | 480.1 | 479.2 | 472.3 | 469.6 | 455.2 | 416.2
2323 | 2225 | 526.3 | 477.3 | 506.4 | 479.1 | 480.2 | 479.2 | 472.4 | 469.7 | 455.3 | 416.3
2324 | 2226 | 526.4 | 477.3 | 506.4 | 479.1 | 480.2 | 479.3 | 472.4 | 469.7 | 455.3 | 416.3
2325 | 2227 | 526.3 | 477.3 | 506.5 | 479.1 | 480.2 | 479.3 | 472.5 | 469.8 | 455.4 | 416.3
2326 | 2228 | 526.3 | 477.3 | 506.4 | 479.1 | 480.3 | 479.3 | 472.5 | 470 | 455.4 | 416.4
2327 | 2229 | 526.3 | 477.3 | 506.5 | 479.1 | 480.3 | 479.4 | 472.5 | 470 | 455.4 | 416.4
2328 | 2230 | 526.3 | 477.4 | 506.5 | 479.1 | 480.4 | 479.4 | 472.6 | 470 | 455.5 | 416.5
2329 | 2231 | 526.3 | 477.4 | 506.5 | 479.1 | 480.4 | 479.4 | 472.6 | 470.1 | 455.5 | 416.6
2330 | 2232 | 526.3 | 477.4 | 506.5 | 479.1 | 480.4 | 479.5 | 472.7 | 470.1 | 455.5 | 416.6
2331 | 2233 | 526.3 | 477.4 | 506.5 | 479.2 | 480.4 | 479.5 | 472.7 | 470.1 | 455.6 | 416.7
2332 | 2234 | 526.3 | 477.4 | 506.6 | 479.2 | 480.5 | 479.5 | 472.8 | 470.2 | 455.6 | 416.7
2333 | 2235 | 526.3 | 477.4 | 506.6 | 479.2 | 480.5 | 479.6 | 472.8 | 470.2 | 455.6 | 416.7
2334 | 2236 | 526.3 | 477.4 | 506.6 | 479.2 | 480.5 | 479.6 | 472.9 | 470.2 | 455.7 | 416.8
2335 | 2237 | 526.3 | 477.4 | 506.6 | 479.2 | 480.6 | 479.6 | 472.9 | 470.2 | 455.7 | 416.9
2336 | 2238 | 526.3 | 477.5 | 506.6 | 479.2 | 480.6 | 479.7 | 472.9 | 470.3 | 455.8 | 416.9
2337 | 2239 | 526.2 | 477.5 | 506.7 | 479.2 | 480.6 | 479.7 | 473 | 470.4 | 455.8 | 417
2338 | 2240 | 526.2 | 477.5 | 506.7 | 479.2 | 480.7 | 479.7 | 473 | 470.4 | 455.8 | 417
2339 | 2241 | 526.2 | 477.5 | 506.7 | 479.2 | 480.7 | 479.8 | 473.1 | 470.5 | 455.9 | 417.1
2340 | 2242 | 526.2 | 477.5 | 506.7 | 479.3 | 480.8 | 479.8 | 473.1 | 470.5 | 455.9 | 417.1
2341 | 2243 | 526.2 | 477.5 | 506.7 | 479.3 | 480.8 | 479.9 | 473.2 | 470.6 | 456 | 417.1
2342 | 2244 | 526.1 | 477.5 | 506.7 | 479.3 | 480.8 | 479.9 | 473.2 | 470.7 | 456 | 417.2
2343 | 2245 | 526.1 | 477.6 | 506.7 | 479.3 | 480.9 | 479.9 | 473.2 | 470.8 | 456 | 417.2
2344 | 2246 | 526.1 | 477.6 | 506.7 | 479.3 | 480.9 | 480 | 473.3 | 470.9 | 456.1 | 417.2
2345 | 2247 | 526 | 477.6 | 506.7 | 479.3 | 480.9 | 480 | 473.3 | 470.9 | 456.1 | 417.3
2346 | 2248 | 526 | 477.6 | 506.7 | 479.3 | 481 | 480.1 | 473.4 | 471 | 456.1 | 417.3
2347 | 2249 | 526 | 477.6 | 506.7 | 479.4 | 481 | 480.1 | 473.4 | 471 | 456.2 | 417.4
2348 | 2250 | 526 | 477.6 | 506.7 | 479.3 | 481 | 480.1 | 473.4 | 471 | 456.2 | 417.4
2349 | 2251 | 525.9 | 477.6 | 506.8 | 479.4 | 481.1 | 480.2 | 473.5 | 471.1 | 456.2 | 417.5
2350 | 2252 | 525.9 | 477.7 | 506.8 | 479.4 | 481.1 | 480.2 | 473.5 | 471.1 | 456.3 | 417.5
2351 | 2253 | 525.9 | 477.7 | 506.8 | 479.4 | 481.1 | 480.2 | 473.6 | 471 | 456.3 | 417.5
2352 | 2254 | 525.9 | 477.7 | 506.8 | 479.4 | 481.2 | 480.3 | 473.6 | 471.1 | 456.3 | 417.6
2353 | 2255 | 525.9 | 477.7 | 506.8 | 479.4 | 481.2 | 480.3 | 473.7 | 471.1 | 456.4 | 417.6
2354 | 2256 | 525.9 | 477.7 | 506.8 | 479.4 | 481.2 | 480.3 | 473.7 | 471.2 | 456.4 | 417.6
2355 | 2257 | 525.9 | 477.7 | 506.8 | 479.4 | 481.3 | 480.4 | 473.7 | 471.3 | 456.5 | 417.7
2356 | 2258 | 525.9 | 477.7 | 506.8 | 479.5 | 481.3 | 480.4 | 473.8 | 471.4 | 456.5 | 417.7
2357 | 2259 | 526 | 477.7 | 506.8 | 479.5 | 481.3 | 480.5 | 473.8 | 471.5 | 456.5 | 417.7
2358 | 2260 | 526 | 477.8 | 506.8 | 479.5 | 481.4 | 480.5 | 473.9 | 471.6 | 456.6 | 417.8
2359 | 2261 | 526 | 477.8 | 506.8 | 479.5 | 481.4 | 480.5 | 473.9 | 471.7 | 456.6 | 417.9
2360 | 2262 | 526 | 477.8 | 506.8 | 479.5 | 481.5 | 480.6 | 474 | 471.7 | 456.7 | 417.9
2361 | 2263 | 526 | 477.8 | 506.8 | 479.5 | 481.5 | 480.6 | 474 | 471.7 | 456.7 | 418
2362 | 2264 | 526 | 477.8 | 506.8 | 479.5 | 481.5 | 480.6 | 474 | 471.7 | 456.7 | 418
2363 | 2265 | 526 | 477.8 | 506.8 | 479.5 | 481.6 | 480.7 | 474.1 | 471.8 | 456.8 | 418
2364 | 2266 | 526 | 477.8 | 506.8 | 479.5 | 481.6 | 480.7 | 474.1 | 471.8 | 456.8 | 418.1
2365 | 2267 | 526 | 477.8 | 506.8 | 479.6 | 481.6 | 480.7 | 474.2 | 471.8 | 456.8 | 418.1
2366 | 2268 | 525.9 | 477.8 | 506.8 | 479.6 | 481.7 | 480.8 | 474.2 | 471.9 | 456.9 | 418.1
2367 | 2269 | 526 | 477.9 | 506.9 | 479.6 | 481.7 | 480.8 | 474.3 | 471.9 | 456.9 | 418.2
2368 | 2270 | 526 | 477.9 | 506.9 | 479.6 | 481.7 | 480.8 | 474.3 | 471.9 | 456.9 | 418.2
2369 | 2271 | 526 | 477.9 | 506.9 | 479.6 | 481.7 | 480.9 | 474.3 | 472 | 457 | 418.3
2370 | 2272 | 526 | 477.9 | 506.9 | 479.6 | 481.8 | 480.9 | 474.4 | 472.1 | 457 | 418.3
2371 | 2273 | 526 | 477.9 | 507 | 479.6 | 481.8 | 480.9 | 474.4 | 472.1 | 457 | 418.3
2372 | 2274 | 526 | 477.9 | 507 | 479.6 | 481.8 | 480.9 | 474.5 | 472.1 | 457 | 418.4
2373 | 2275 | 526 | 477.9 | 507 | 479.6 | 481.9 | 481 | 474.5 | 472.2 | 457.1 | 418.5
2374 | 2276 | 526 | 477.9 | 507 | 479.7 | 481.9 | 481 | 474.6 | 472.2 | 457.1 | 418.5
2375 | 2277 | 526 | 477.9 | 507 | 479.7 | 481.9 | 481.1 | 474.6 | 472.3 | 457.1 | 418.5
2376 | 2278 | 526 | 477.9 | 507 | 479.7 | 482 | 481.1 | 474.6 | 472.4 | 457.2 | 418.6
2377 | 2279 | 525.9 | 477.9 | 507 | 479.7 | 482 | 481.1 | 474.7 | 472.4 | 457.2 | 418.6
2378 | 2280 | 525.9 | 478 | 507.1 | 479.7 | 482 | 481.2 | 474.7 | 472.4 | 457.2 | 418.7
2379 | 2281 | 525.8 | 478 | 507.1 | 479.7 | 482.1 | 481.2 | 474.8 | 472.5 | 457.3 | 418.7
2380 | 2282 | 525.8 | 478 | 507.1 | 479.7 | 482.1 | 481.3 | 474.8 | 472.5 | 457.3 | 418.7
2381 | 2283 | 525.8 | 478 | 507.1 | 479.7 | 482.2 | 481.3 | 474.8 | 472.6 | 457.3 | 418.8
2382 | 2284 | 525.8 | 478 | 507.1 | 479.7 | 482.2 | 481.3 | 474.9 | 472.6 | 457.4 | 418.9
2383 | 2285 | 525.8 | 478 | 507.1 | 479.8 | 482.2 | 481.4 | 474.9 | 472.7 | 457.4 | 418.9
2384 | 2286 | 525.8 | 478 | 507.1 | 479.8 | 482.3 | 481.4 | 475 | 472.9 | 457.4 | 419
2385 | 2287 | 525.8 | 478 | 507.1 | 479.8 | 482.3 | 481.4 | 475 | 472.9 | 457.5 | 419.1
2386 | 2288 | 525.8 | 478.1 | 507.1 | 479.8 | 482.3 | 481.4 | 475 | 472.9 | 457.5 | 419.1
2387 | 2289 | 525.8 | 478.1 | 507.2 | 479.8 | 482.4 | 481.5 | 475.1 | 472.9 | 457.5 | 419.2
2388 | 2290 | 525.7 | 478.1 | 507.2 | 479.8 | 482.4 | 481.5 | 475.1 | 472.9 | 457.5 | 419.3
2389 | 2291 | 525.7 | 478.1 | 507.2 | 479.8 | 482.4 | 481.5 | 475.2 | 473 | 457.6 | 419.3
2390 | 2292 | 525.7 | 478.1 | 507.2 | 479.8 | 482.4 | 481.6 | 475.2 | 473 | 457.6 | 419.4
2391 | 2293 | 525.7 | 478.1 | 507.2 | 479.8 | 482.5 | 481.6 | 475.2 | 472.9 | 457.6 | 419.5
2392 | 2294 | 525.7 | 478.1 | 507.2 | 479.8 | 482.5 | 481.7 | 475.3 | 472.9 | 457.7 | 419.5
2393 | 2295 | 525.6 | 478.1 | 507.2 | 479.8 | 482.6 | 481.7 | 475.3 | 472.9 | 457.7 | 419.6
2394 | 2296 | 525.6 | 478.2 | 507.2 | 479.9 | 482.6 | 481.7 | 475.4 | 473 | 457.7 | 419.6
2395 | 2297 | 525.5 | 478.2 | 507.1 | 479.9 | 482.6 | 481.8 | 475.4 | 473.1 | 457.8 | 419.6
2396 | 2298 | 525.5 | 478.2 | 507.1 | 479.9 | 482.7 | 481.8 | 475.5 | 473.1 | 457.8 | 419.7
2397 | 2299 | 525.4 | 478.2 | 507.2 | 479.9 | 482.7 | 481.8 | 475.5 | 473.2 | 457.9 | 419.8
2398 | 2300 | 525.4 | 478.2 | 507.2 | 479.9 | 482.7 | 481.9 | 475.5 | 473.3 | 457.9 | 419.8
2399 | 2301 | 525.4 | 478.2 | 507.2 | 479.9 | 482.8 | 481.9 | 475.6 | 473.4 | 457.9 | 419.9
2400 | 2302 | 525.4 | 478.2 | 507.1 | 479.9 | 482.8 | 481.9 | 475.6 | 473.5 | 458 | 420
2401 | 2303 | 525.4 | 478.3 | 507.2 | 479.9 | 482.8 | 482 | 475.7 | 473.5 | 458 | 420
2402 | 2304 | 525.4 | 478.2 | 507.2 | 479.9 | 482.8 | 482 | 475.7 | 473.6 | 458 | 420.1
2403 | 2305 | 525.4 | 478.3 | 507.2 | 479.9 | 482.9 | 482 | 475.7 | 473.7 | 458.1 | 420.2
2404 | 2306 | 525.4 | 478.3 | 507.3 | 479.9 | 482.9 | 482.1 | 475.8 | 473.7 | 458.1 | 420.2
2405 | 2307 | 525.5 | 478.3 | 507.3 | 479.9 | 483 | 482.1 | 475.8 | 473.7 | 458.1 | 420.3
2406 | 2308 | 525.5 | 478.3 | 507.3 | 479.9 | 483 | 482.1 | 475.8 | 473.8 | 458.2 | 420.3
2407 | 2309 | 525.6 | 478.3 | 507.3 | 480 | 483 | 482.2 | 475.9 | 473.9 | 458.2 | 420.3
2408 | 2310 | 525.6 | 478.3 | 507.3 | 480 | 483.1 | 482.2 | 475.9 | 473.9 | 458.2 | 420.4
2409 | 2311 | 525.7 | 478.3 | 507.3 | 480 | 483.1 | 482.2 | 476 | 474 | 458.3 | 420.5
2410 | 2312 | 525.7 | 478.4 | 507.3 | 480 | 483.1 | 482.3 | 476 | 474 | 458.3 | 420.5
2411 | 2313 | 525.7 | 478.4 | 507.3 | 480 | 483.1 | 482.3 | 476 | 474.1 | 458.3 | 420.6
2412 | 2314 | 525.8 | 478.4 | 507.3 | 480 | 483.2 | 482.3 | 476.1 | 474.1 | 458.3 | 420.7
2413 | 2315 | 525.8 | 478.4 | 507.4 | 480 | 483.2 | 482.4 | 476.1 | 474.1 | 458.4 | 420.8
2414 | 2316 | 525.8 | 478.4 | 507.4 | 480 | 483.2 | 482.4 | 476.2 | 474.2 | 458.4 | 420.9
2415 | 2317 | 525.9 | 478.4 | 507.3 | 480 | 483.3 | 482.4 | 476.2 | 474.2 | 458.4 | 421
2416 | 2318 | 525.9 | 478.4 | 507.4 | 480 | 483.3 | 482.5 | 476.2 | 474.2 | 458.5 | 421
2417 | 2319 | 525.9 | 478.5 | 507.4 | 480 | 483.4 | 482.5 | 476.3 | 474.1 | 458.5 | 421.1
2418 | 2320 | 526 | 478.5 | 507.4 | 480.1 | 483.4 | 482.6 | 476.3 | 474.2 | 458.6 | 421.2
2419 | 2321 | 526 | 478.5 | 507.4 | 480.1 | 483.4 | 482.6 | 476.4 | 474.2 | 458.6 | 421.2
2420 | 2322 | 526.1 | 478.5 | 507.5 | 480.1 | 483.5 | 482.6 | 476.4 | 474.2 | 458.6 | 421.3
2421 | 2323 | 526 | 478.5 | 507.5 | 480.1 | 483.5 | 482.7 | 476.4 | 474.2 | 458.7 | 421.4
2422 | 2324 | 526 | 478.5 | 507.5 | 480.1 | 483.5 | 482.7 | 476.5 | 474.3 | 458.7 | 421.5
2423 | 2325 | 526 | 478.5 | 507.5 | 480.1 | 483.6 | 482.7 | 476.5 | 474.3 | 458.7 | 421.5
2424 | 2326 | 526 | 478.5 | 507.5 | 480.1 | 483.6 | 482.8 | 476.6 | 474.4 | 458.8 | 421.6
2425 | 2327 | 526 | 478.5 | 507.5 | 480.1 | 483.6 | 482.8 | 476.6 | 474.5 | 458.8 | 421.7
2426 | 2328 | 526 | 478.6 | 507.5 | 480.1 | 483.7 | 482.8 | 476.6 | 474.4 | 458.8 | 421.7
2427 | 2329 | 526 | 478.6 | 507.5 | 480.1 | 483.7 | 482.9 | 476.7 | 474.5 | 458.9 | 421.8
2428 | 2330 | 526.1 | 478.6 | 507.5 | 480.1 | 483.7 | 482.9 | 476.7 | 474.5 | 458.9 | 421.9
2429 | 2331 | 526.1 | 478.6 | 507.5 | 480.1 | 483.8 | 482.9 | 476.8 | 474.5 | 458.9 | 421.9
2430 | 2332 | 526.1 | 478.6 | 507.5 | 480.2 | 483.8 | 483 | 476.8 | 474.5 | 459 | 422
2431 | 2333 | 526.1 | 478.6 | 507.5 | 480.2 | 483.8 | 483 | 476.8 | 474.6 | 459 | 422.1
2432 | 2334 | 526.1 | 478.6 | 507.6 | 480.2 | 483.9 | 483 | 476.9 | 474.6 | 459 | 422.1
2433 | 2335 | 526.1 | 478.6 | 507.6 | 480.2 | 483.9 | 483.1 | 476.9 | 474.6 | 459.1 | 422.2
2434 | 2336 | 526.1 | 478.7 | 507.6 | 480.2 | 483.9 | 483.1 | 477 | 474.6 | 459.1 | 422.3
2435 | 2337 | 526.1 | 478.7 | 507.6 | 480.2 | 484 | 483.1 | 477 | 474.6 | 459.1 | 422.3
2436 | 2338 | 526.1 | 478.7 | 507.6 | 480.2 | 484 | 483.2 | 477 | 474.6 | 459.2 | 422.4
2437 | 2339 | 526.1 | 478.7 | 507.6 | 480.2 | 484 | 483.2 | 477.1 | 474.6 | 459.2 | 422.4
2438 | 2340 | 526.1 | 478.7 | 507.6 | 480.2 | 484.1 | 483.3 | 477.1 | 474.6 | 459.3 | 422.5
2439 | 2341 | 526.1 | 478.7 | 507.6 | 480.2 | 484.1 | 483.3 | 477.2 | 474.7 | 459.3 | 422.5
2440 | 2342 | 526.1 | 478.7 | 507.6 | 480.3 | 484.1 | 483.3 | 477.2 | 474.8 | 459.3 | 422.6
2441 | 2343 | 526.1 | 478.7 | 507.6 | 480.3 | 484.2 | 483.4 | 477.2 | 474.8 | 459.4 | 422.7
2442 | 2344 | 526.1 | 478.8 | 507.7 | 480.3 | 484.2 | 483.4 | 477.3 | 474.8 | 459.4 | 422.7
2443 | 2345 | 526.1 | 478.8 | 507.7 | 480.3 | 484.2 | 483.4 | 477.3 | 474.9 | 459.4 | 422.8
2444 | 2346 | 526.1 | 478.8 | 507.7 | 480.3 | 484.3 | 483.4 | 477.4 | 475 | 459.4 | 422.8
2445 | 2347 | 526.1 | 478.8 | 507.7 | 480.3 | 484.3 | 483.5 | 477.4 | 475 | 459.5 | 422.9
2446 | 2348 | 526.1 | 478.8 | 507.7 | 480.3 | 484.3 | 483.5 | 477.4 | 475.1 | 459.5 | 422.9
2447 | 2349 | 526.1 | 478.8 | 507.7 | 480.3 | 484.4 | 483.5 | 477.5 | 475.1 | 459.5 | 423
2448 | 2350 | 526.1 | 478.8 | 507.7 | 480.3 | 484.4 | 483.6 | 477.5 | 475.2 | 459.6 | 423
2449 | 2351 | 526.1 | 478.8 | 507.7 | 480.3 | 484.4 | 483.6 | 477.6 | 475.3 | 459.6 | 423.1
2450 | 2352 | 526.1 | 478.9 | 507.8 | 480.3 | 484.4 | 483.7 | 477.6 | 475.5 | 459.6 | 423.1
2451 | 2353 | 526.1 | 478.9 | 507.8 | 480.3 | 484.5 | 483.7 | 477.7 | 475.5 | 459.7 | 423.2
2452 | 2354 | 526.1 | 478.9 | 507.8 | 480.3 | 484.5 | 483.7 | 477.7 | 475.6 | 459.7 | 423.2
2453 | 2355 | 526.1 | 478.9 | 507.8 | 480.4 | 484.6 | 483.8 | 477.7 | 475.6 | 459.8 | 423.3
2454 | 2356 | 526.1 | 478.9 | 507.8 | 480.4 | 484.6 | 483.8 | 477.8 | 475.7 | 459.8 | 423.3
2455 | 2357 | 526.1 | 478.9 | 507.7 | 480.4 | 484.7 | 483.9 | 477.8 | 475.7 | 459.8 | 423.4
2456 | 2358 | 526.1 | 478.9 | 507.8 | 480.4 | 484.7 | 483.9 | 477.8 | 475.8 | 459.9 | 423.4
2457 | 2359 | 526.1 | 478.9 | 507.8 | 480.4 | 484.7 | 483.9 | 477.9 | 475.9 | 459.9 | 423.4
2458 | 2360 | 526.1 | 478.9 | 507.8 | 480.4 | 484.8 | 484 | 477.9 | 475.9 | 459.9 | 423.5
2459 | 2361 | 526.1 | 478.9 | 507.9 | 480.4 | 484.8 | 484 | 478 | 476 | 460 | 423.5
2460 | 2362 | 526.1 | 479 | 507.8 | 480.4 | 484.8 | 484 | 478 | 476 | 460 | 423.5
2461 | 2363 | 526.1 | 479 | 507.9 | 480.4 | 484.9 | 484.1 | 478.1 | 476 | 460 | 423.6
2462 | 2364 | 526.1 | 479 | 507.9 | 480.4 | 484.9 | 484.1 | 478.1 | 476.1 | 460 | 423.6
2463 | 2365 | 526 | 479.2 | 507.3 | 480.7 | 485.1 | 484.2 | 478.1 | 476.1 | 460 | 423.9
2464 | 2366 | 526 | 479.3 | 507.3 | 480.7 | 485.2 | 484.3 | 478.2 | 476.2 | 460.1 | 424
2465 | 2367 | 526 | 479 | 507.9 | 480.5 | 485 | 484.2 | 478.2 | 476.3 | 460.2 | 423.7
2466 | 2368 | 526 | 479 | 507.9 | 480.5 | 485 | 484.2 | 478.3 | 476.4 | 460.2 | 423.8
2467 | 2369 | 526 | 479 | 507.9 | 480.5 | 485 | 484.3 | 478.3 | 476.4 | 460.2 | 423.8
2468 | 2370 | 525.9 | 479 | 507.9 | 480.5 | 485.1 | 484.3 | 478.3 | 476.5 | 460.3 | 423.9
2469 | 2371 | 525.9 | 479 | 507.9 | 480.5 | 485.1 | 484.4 | 478.4 | 476.5 | 460.3 | 423.9
2470 | 2372 | 525.9 | 479 | 507.9 | 480.5 | 485.1 | 484.4 | 478.4 | 476.5 | 460.3 | 423.9
2471 | 2373 | 525.9 | 479.1 | 508 | 480.5 | 485.2 | 484.4 | 478.5 | 476.5 | 460.4 | 423.9
2472 | 2374 | 525.9 | 479.1 | 508 | 480.5 | 485.2 | 484.5 | 478.5 | 476.6 | 460.4 | 424
2473 | 2375 | 525.9 | 479.1 | 508 | 480.6 | 485.2 | 484.5 | 478.5 | 476.6 | 460.4 | 424
2474 | 2376 | 525.9 | 479.1 | 507.9 | 480.6 | 485.3 | 484.5 | 478.6 | 476.7 | 460.5 | 424
2475 | 2377 | 525.9 | 479.1 | 508 | 480.6 | 485.3 | 484.6 | 478.6 | 476.7 | 460.5 | 424.1
2476 | 2378 | 525.9 | 479.1 | 508 | 480.6 | 485.3 | 484.6 | 478.7 | 476.7 | 460.5 | 424.1
2477 | 2379 | 525.9 | 479.1 | 507.9 | 480.6 | 485.4 | 484.6 | 478.7 | 476.8 | 460.5 | 424.2
2478 | 2380 | 525.8 | 479.2 | 507.9 | 480.6 | 485.4 | 484.7 | 478.7 | 476.7 | 460.6 | 424.2
2479 | 2381 | 525.8 | 479.2 | 508 | 480.6 | 485.4 | 484.7 | 478.8 | 476.8 | 460.6 | 424.2
2480 | 2382 | 525.8 | 479.3 | 507.7 | 480.7 | 485.6 | 484.8 | 478.8 | 476.8 | 460.6 | 424.4
2481 | 2383 | 525.8 | 479.3 | 507.8 | 480.7 | 485.6 | 484.8 | 478.9 | 477 | 460.6 | 424.4
2482 | 2384 | 525.8 | 479.2 | 508 | 480.6 | 485.5 | 484.8 | 478.9 | 477 | 460.7 | 424.3
2483 | 2385 | 525.8 | 479.5 | 507.4 | 480.9 | 485.8 | 485 | 478.9 | 477 | 460.7 | 424.6
2484 | 2386 | 525.8 | 479.3 | 507.8 | 480.7 | 485.7 | 484.9 | 479 | 477.2 | 460.7 | 424.5
2485 | 2387 | 525.9 | 479.2 | 508 | 480.7 | 485.7 | 484.9 | 479 | 477.2 | 460.8 | 424.5
2486 | 2388 | 525.8 | 479.6 | 507.1 | 481 | 486 | 485.2 | 479.1 | 477.2 | 460.8 | 424.8
2487 | 2389 | 525.9 | 479.2 | 508 | 480.7 | 485.8 | 485 | 479.1 | 477.3 | 460.9 | 424.5
2488 | 2390 | 526 | 479.3 | 507.9 | 480.7 | 485.8 | 485.1 | 479.2 | 477.3 | 460.9 | 424.6
2489 | 2391 | 526 | 479.5 | 507.7 | 480.9 | 486 | 485.2 | 479.2 | 477.4 | 460.9 | 424.8
2490 | 2392 | 526 | 479.3 | 508.1 | 480.7 | 485.9 | 485.1 | 479.2 | 477.5 | 461 | 424.6
2491 | 2393 | 526 | 479.3 | 508 | 480.8 | 485.9 | 485.2 | 479.3 | 477.5 | 461 | 424.7
2492.1 | 2394.1 | 526.1 | 479.4 | 508 | 480.8 | 486 | 485.2 | 479.3 | 477.6 | 461 | 424.8
2493.1 | 2395.1 | 526.1 | 479.3 | 508.2 | 480.7 | 486 | 485.2 | 479.4 | 477.6 | 461.1 | 424.7
2494.1 | 2396.1 | 526.1 | 479.3 | 508.1 | 480.8 | 486 | 485.2 | 479.4 | 477.7 | 461.1 | 424.8
2495.1 | 2397.1 | 526.1 | 479.3 | 508.2 | 480.8 | 486 | 485.3 | 479.4 | 477.8 | 461.1 | 424.8
2496.1 | 2398.1 | 526.1 | 479.3 | 508.2 | 480.8 | 486 | 485.3 | 479.5 | 477.9 | 461.1 | 424.8
2497.1 | 2399.1 | 526.1 | 479.6 | 507.7 | 481 | 486.2 | 485.5 | 479.5 | 477.9 | 461.1 | 425.1
2498.1 | 2400.1 | 526.2 | 479.5 | 508 | 480.9 | 486.2 | 485.4 | 479.6 | 477.9 | 461.2 | 425
2499.1 | 2401.1 | 526.2 | 479.4 | 508.2 | 480.8 | 486.1 | 485.4 | 479.6 | 477.9 | 461.2 | 424.9
2500.1 | 2402.1 | 526.2 | 479.4 | 508.3 | 480.8 | 486.2 | 485.4 | 479.6 | 477.9 | 461.3 | 425
2501.1 | 2403.1 | 526.3 | 479.4 | 508.3 | 480.8 | 486.2 | 485.5 | 479.7 | 477.9 | 461.3 | 425
2502.1 | 2404.1 | 526.3 | 479.4 | 508.3 | 480.8 | 486.2 | 485.5 | 479.7 | 477.9 | 461.3 | 425.1
2503.1 | 2405.1 | 526.3 | 479.4 | 508.2 | 480.8 | 486.3 | 485.6 | 479.8 | 477.9 | 461.4 | 425.1
2504.1 | 2406.1 | 526.3 | 479.4 | 508.2 | 480.8 | 486.3 | 485.6 | 479.8 | 478 | 461.4 | 425.1
2505.1 | 2407.1 | 526.2 | 479.5 | 508.3 | 480.8 | 486.4 | 485.6 | 479.8 | 478 | 461.4 | 425.2
2506.1 | 2408.1 | 526.2 | 479.5 | 508.3 | 480.8 | 486.4 | 485.7 | 479.9 | 478.1 | 461.5 | 425.2
2507.1 | 2409.1 | 526.2 | 479.5 | 508.3 | 480.8 | 486.4 | 485.7 | 479.9 | 478.2 | 461.5 | 425.2
2508.1 | 2410.1 | 526.2 | 479.5 | 508.3 | 480.9 | 486.5 | 485.7 | 480 | 478.3 | 461.5 | 425.3
2509.1 | 2411.1 | 526.2 | 479.5 | 508.3 | 480.9 | 486.5 | 485.8 | 480 | 478.4 | 461.6 | 425.3
2510.1 | 2412.1 | 526.2 | 479.5 | 508.3 | 480.8 | 486.6 | 485.8 | 480 | 478.4 | 461.6 | 425.4
2511.1 | 2413.1 | 526.1 | 479.5 | 508.3 | 480.9 | 486.6 | 485.9 | 480.1 | 478.5 | 461.6 | 425.4
2512.1 | 2414.1 | 526.1 | 479.5 | 508.3 | 480.9 | 486.6 | 485.9 | 480.1 | 478.6 | 461.7 | 425.4
2513.1 | 2415.1 | 526.1 | 479.5 | 508.3 | 480.9 | 486.7 | 485.9 | 480.2 | 478.7 | 461.7 | 425.5
2514.1 | 2416.1 | 526.1 | 479.5 | 508.4 | 480.9 | 486.7 | 486 | 480.2 | 478.7 | 461.8 | 425.5
2515.1 | 2417.1 | 526.1 | 479.5 | 508.4 | 480.9 | 486.7 | 486 | 480.2 | 478.7 | 461.8 | 425.5
2516.1 | 2418.1 | 526.1 | 479.6 | 508.4 | 480.9 | 486.8 | 486 | 480.3 | 478.8 | 461.8 | 425.6
2517.1 | 2419.1 | 526.1 | 479.6 | 508.4 | 480.9 | 486.8 | 486.1 | 480.3 | 478.9 | 461.9 | 425.6
2518.1 | 2420.1 | 526.1 | 479.6 | 508.4 | 480.9 | 486.8 | 486.1 | 480.4 | 479 | 461.9 | 425.6
2519.1 | 2421.1 | 526.1 | 479.6 | 508.4 | 480.9 | 486.9 | 486.1 | 480.4 | 478.9 | 461.9 | 425.7
2520.1 | 2422.1 | 526.1 | 479.6 | 508.4 | 480.9 | 486.9 | 486.2 | 480.4 | 478.9 | 461.9 | 425.7
2521.1 | 2423.1 | 526.1 | 479.6 | 508.4 | 480.9 | 486.9 | 486.2 | 480.5 | 479 | 461.9 | 425.8
2522.1 | 2424.1 | 526.1 | 479.6 | 508.4 | 480.9 | 486.9 | 486.2 | 480.5 | 479.1 | 462 | 425.8
2523.1 | 2425.1 | 526.1 | 479.6 | 508.4 | 480.9 | 487 | 486.3 | 480.6 | 479.1 | 462 | 425.8
2524.1 | 2426.1 | 526.1 | 479.6 | 508.5 | 480.9 | 487 | 486.3 | 480.6 | 479.2 | 462 | 425.9
2525.1 | 2427.1 | 526.1 | 479.7 | 508.4 | 481 | 487 | 486.3 | 480.6 | 479.2 | 462.1 | 425.9
2526.1 | 2428.1 | 526.1 | 479.7 | 508.4 | 481 | 487.1 | 486.4 | 480.7 | 479.3 | 462.1 | 425.9
2527.1 | 2429.1 | 526.1 | 479.7 | 508.4 | 481 | 487.1 | 486.4 | 480.7 | 479.3 | 462.1 | 426
2528.1 | 2430.1 | 526.2 | 479.7 | 508.5 | 481 | 487.1 | 486.5 | 480.8 | 479.4 | 462.2 | 426
2529.1 | 2431.1 | 526.2 | 479.7 | 508.5 | 481 | 487.2 | 486.5 | 480.8 | 479.4 | 462.2 | 426
2530.1 | 2432.1 | 526.2 | 479.7 | 508.5 | 481 | 487.2 | 486.5 | 480.8 | 479.5 | 462.2 | 426.1
2531.1 | 2433.1 | 526.1 | 479.7 | 508.5 | 481 | 487.2 | 486.5 | 480.9 | 479.4 | 462.2 | 426.1
2532.1 | 2434.1 | 526.1 | 479.7 | 508.5 | 481 | 487.3 | 486.6 | 480.9 | 479.4 | 462.2 | 426.2
2533.1 | 2435.1 | 526.1 | 479.7 | 508.6 | 481 | 487.3 | 486.6 | 481 | 479.4 | 462.3 | 426.2
2534.1 | 2436.1 | 526.1 | 479.7 | 508.5 | 481 | 487.3 | 486.6 | 481 | 479.4 | 462.3 | 426.2
2535.1 | 2437.1 | 526.1 | 479.7 | 508.5 | 481 | 487.4 | 486.7 | 481 | 479.5 | 462.4 | 426.3
2536.1 | 2438.1 | 526.1 | 479.8 | 508.5 | 481 | 487.4 | 486.7 | 481.1 | 479.5 | 462.4 | 426.3
2537.1 | 2439.1 | 526.1 | 479.8 | 508.6 | 481 | 487.4 | 486.8 | 481.1 | 479.5 | 462.4 | 426.3
2538.1 | 2440.1 | 526.1 | 479.8 | 508.6 | 481 | 487.5 | 486.8 | 481.1 | 479.6 | 462.5 | 426.4
2539.1 | 2441.1 | 526.1 | 479.8 | 508.6 | 481 | 487.5 | 486.8 | 481.2 | 479.7 | 462.5 | 426.4
2540.1 | 2442.1 | 526.1 | 479.8 | 508.6 | 481 | 487.5 | 486.9 | 481.2 | 479.7 | 462.5 | 426.5
2541.1 | 2443.1 | 526.1 | 479.8 | 508.6 | 481 | 487.6 | 486.9 | 481.3 | 479.7 | 462.5 | 426.5
2542.1 | 2444.1 | 526.1 | 479.8 | 508.6 | 481 | 487.6 | 486.9 | 481.3 | 479.8 | 462.6 | 426.5
2543.1 | 2445.1 | 526 | 479.8 | 508.6 | 481.1 | 487.6 | 487 | 481.3 | 479.8 | 462.6 | 426.6
2544.1 | 2446.1 | 526 | 479.8 | 508.6 | 481.1 | 487.7 | 487 | 481.4 | 479.9 | 462.6 | 426.6
2545.1 | 2447.1 | 526 | 479.8 | 508.6 | 481.1 | 487.7 | 487 | 481.4 | 479.9 | 462.7 | 426.6
2546.1 | 2448.1 | 525.9 | 479.9 | 508.7 | 481.1 | 487.7 | 487.1 | 481.5 | 479.9 | 462.7 | 426.7
2547.1 | 2449.1 | 525.9 | 479.9 | 508.7 | 481.1 | 487.8 | 487.1 | 481.5 | 479.9 | 462.7 | 426.7
2548.1 | 2450.1 | 525.9 | 479.9 | 508.7 | 481.1 | 487.8 | 487.1 | 481.5 | 480 | 462.8 | 426.8
2549.1 | 2451.1 | 525.9 | 479.9 | 508.6 | 481.1 | 487.8 | 487.2 | 481.6 | 479.9 | 462.8 | 426.8
2550.1 | 2452.1 | 525.9 | 479.9 | 508.6 | 481.1 | 487.9 | 487.2 | 481.6 | 479.9 | 462.8 | 426.8
2551.1 | 2453.1 | 525.9 | 479.9 | 508.6 | 481.1 | 487.9 | 487.3 | 481.6 | 480 | 462.9 | 426.9
2552.1 | 2454.1 | 525.9 | 479.9 | 508.6 | 481.1 | 487.9 | 487.3 | 481.7 | 480 | 462.9 | 426.9
2553.1 | 2455.1 | 525.9 | 479.9 | 508.7 | 481.1 | 488 | 487.3 | 481.7 | 480.1 | 462.9 | 426.9
2554.1 | 2456.1 | 525.9 | 480 | 508.7 | 481.1 | 488 | 487.4 | 481.8 | 480.2 | 463 | 427
2555.1 | 2457.1 | 525.9 | 480 | 508.7 | 481.1 | 488 | 487.4 | 481.8 | 480.3 | 463 | 427
2556.1 | 2458.1 | 525.9 | 480 | 508.7 | 481.2 | 488.1 | 487.4 | 481.8 | 480.3 | 463 | 427
2557.1 | 2459.1 | 525.9 | 480 | 508.7 | 481.2 | 488.1 | 487.5 | 481.9 | 480.4 | 463.1 | 427.1
2558.1 | 2460.1 | 525.9 | 480 | 508.7 | 481.2 | 488.1 | 487.5 | 481.9 | 480.4 | 463.1 | 427.1
2559.1 | 2461.1 | 525.9 | 480 | 508.7 | 481.1 | 488.2 | 487.5 | 481.9 | 480.5 | 463.1 | 427.2
2560.1 | 2462.1 | 526 | 480 | 508.7 | 481.2 | 488.2 | 487.6 | 482 | 480.5 | 463.1 | 427.2
2561.1 | 2463.1 | 526.1 | 480 | 508.7 | 481.2 | 488.2 | 487.6 | 482 | 480.6 | 463.2 | 427.2
2562.1 | 2464.1 | 526.1 | 480 | 508.7 | 481.2 | 488.3 | 487.6 | 482.1 | 480.6 | 463.2 | 427.3
2563.1 | 2465.1 | 526.1 | 480 | 508.7 | 481.2 | 488.3 | 487.7 | 482.1 | 480.7 | 463.2 | 427.3
2564.1 | 2466.1 | 526.2 | 480.1 | 508.7 | 481.2 | 488.3 | 487.7 | 482.1 | 480.7 | 463.3 | 427.3
2565.1 | 2467.1 | 526.2 | 480.1 | 508.8 | 481.2 | 488.4 | 487.7 | 482.2 | 480.9 | 463.3 | 427.4
2566.1 | 2468.1 | 526.2 | 480.1 | 508.8 | 481.2 | 488.4 | 487.8 | 482.2 | 480.9 | 463.3 | 427.4
2567.1 | 2469.1 | 526.3 | 480.1 | 508.8 | 481.2 | 488.4 | 487.8 | 482.3 | 480.9 | 463.3 | 427.4
2568.1 | 2470.1 | 526.3 | 480.1 | 508.8 | 481.2 | 488.5 | 487.8 | 482.3 | 481 | 463.4 | 427.5
2569.1 | 2471.1 | 526.3 | 480.1 | 508.8 | 481.2 | 488.5 | 487.9 | 482.3 | 481 | 463.4 | 427.5
2570.1 | 2472.1 | 526.3 | 480.1 | 508.9 | 481.2 | 488.5 | 487.9 | 482.4 | 481.1 | 463.4 | 427.5
2571.1 | 2473.1 | 526.4 | 480.1 | 508.9 | 481.2 | 488.6 | 487.9 | 482.4 | 481.1 | 463.5 | 427.6
2572.1 | 2474.1 | 526.3 | 480.1 | 508.9 | 481.2 | 488.6 | 488 | 482.4 | 481.1 | 463.5 | 427.6
2573.1 | 2475.1 | 526.3 | 480.1 | 508.9 | 481.2 | 488.6 | 488 | 482.5 | 481.1 | 463.5 | 427.6
2574.1 | 2476.1 | 526.3 | 480.2 | 508.9 | 481.2 | 488.6 | 488 | 482.5 | 481.2 | 463.6 | 427.7
2575.1 | 2477.1 | 526.3 | 480.2 | 508.9 | 481.2 | 488.7 | 488.1 | 482.6 | 481.3 | 463.6 | 427.7
2576.1 | 2478.1 | 526.3 | 480.2 | 508.9 | 481.2 | 488.7 | 488.1 | 482.6 | 481.3 | 463.6 | 427.7
2577.1 | 2479.1 | 526.3 | 480.2 | 508.9 | 481.3 | 488.7 | 488.2 | 482.6 | 481.3 | 463.7 | 427.8
2578.1 | 2480.1 | 526.3 | 480.2 | 508.9 | 481.3 | 488.8 | 488.2 | 482.7 | 481.3 | 463.7 | 427.8
2579.1 | 2481.1 | 526.3 | 480.2 | 508.9 | 481.3 | 488.8 | 488.2 | 482.7 | 481.3 | 463.7 | 427.8
2580.1 | 2482.1 | 526.3 | 480.3 | 508.9 | 481.3 | 488.9 | 488.3 | 482.7 | 481.3 | 463.8 | 427.8
2581.1 | 2483.1 | 526.2 | 480.2 | 509 | 481.2 | 488.9 | 488.3 | 482.8 | 481.5 | 463.8 | 427.9
2582.1 | 2484.1 | 526.3 | 480.2 | 509 | 481.3 | 488.9 | 488.3 | 482.8 | 481.5 | 463.8 | 427.9
2583.1 | 2485.1 | 526.3 | 480.3 | 509 | 481.3 | 489 | 488.4 | 482.9 | 481.6 | 463.9 | 427.9
2584.1 | 2486.1 | 526.3 | 480.2 | 509 | 481.3 | 489 | 488.4 | 482.9 | 481.7 | 463.9 | 427.9
2585.1 | 2487.1 | 526.3 | 480.3 | 509 | 481.3 | 489 | 488.4 | 482.9 | 481.7 | 463.9 | 428
2586.1 | 2488.1 | 526.2 | 480.3 | 509 | 481.3 | 489.1 | 488.5 | 483 | 481.8 | 464 | 428
2587.1 | 2489.1 | 526.2 | 480.3 | 509 | 481.3 | 489.1 | 488.5 | 483 | 481.8 | 464 | 428
2588.1 | 2490.1 | 526.2 | 480.3 | 509 | 481.3 | 489.1 | 488.6 | 483 | 481.8 | 464 | 428.1
2589.1 | 2491.1 | 526.2 | 480.3 | 509 | 481.4 | 489.2 | 488.6 | 483.1 | 481.9 | 464 | 428.1
2590.1 | 2492.1 | 526.1 | 480.4 | 508.8 | 481.4 | 489.3 | 488.7 | 483.1 | 481.8 | 464 | 428.2
2591.1 | 2493.1 | 526.1 | 480.5 | 508.7 | 481.5 | 489.4 | 488.7 | 483.1 | 481.9 | 464.1 | 428.3
2592.1 | 2494.1 | 526 | 480.4 | 509.1 | 481.4 | 489.3 | 488.7 | 483.2 | 482 | 464.1 | 428.2
2593.1 | 2495.1 | 526 | 480.4 | 509 | 481.3 | 489.3 | 488.7 | 483.2 | 482 | 464.2 | 428.2
2594.1 | 2496.1 | 526 | 480.4 | 509.1 | 481.3 | 489.3 | 488.8 | 483.3 | 481.9 | 464.2 | 428.2
2595.1 | 2497.1 | 526 | 480.4 | 508.9 | 481.4 | 489.4 | 488.8 | 483.3 | 481.9 | 464.2 | 428.3
2596.1 | 2498.1 | 525.9 | 480.4 | 509 | 481.4 | 489.4 | 488.8 | 483.3 | 481.9 | 464.2 | 428.3
2597.1 | 2499.1 | 525.9 | 480.4 | 509.1 | 481.4 | 489.4 | 488.8 | 483.4 | 482 | 464.2 | 428.3
2598.1 | 2500.1 | 525.9 | 480.4 | 509.1 | 481.4 | 489.5 | 488.9 | 483.4 | 482.1 | 464.3 | 428.4
2599.1 | 2501.1 | 525.9 | 480.4 | 509.2 | 481.4 | 489.5 | 488.9 | 483.5 | 482.2 | 464.3 | 428.4
2600.1 | 2502.1 | 525.9 | 480.4 | 509.2 | 481.4 | 489.5 | 489 | 483.5 | 482.3 | 464.3 | 428.4
2601.1 | 2503.1 | 525.9 | 480.4 | 509.1 | 481.4 | 489.6 | 489 | 483.5 | 482.3 | 464.3 | 428.5
2602.1 | 2504.1 | 525.9 | 480.4 | 509.1 | 481.4 | 489.6 | 489 | 483.6 | 482.3 | 464.4 | 428.5
2603.1 | 2505.1 | 525.9 | 480.4 | 509.2 | 481.4 | 489.6 | 489.1 | 483.6 | 482.3 | 464.4 | 428.5
2604.1 | 2506.1 | 525.9 | 480.5 | 509.1 | 481.4 | 489.6 | 489.1 | 483.6 | 482.3 | 464.4 | 428.5
2605.1 | 2507.1 | 525.9 | 480.5 | 509.2 | 481.4 | 489.7 | 489.1 | 483.7 | 482.3 | 464.5 | 428.6
2606.1 | 2508.1 | 525.9 | 480.5 | 509.2 | 481.4 | 489.7 | 489.2 | 483.7 | 482.2 | 464.5 | 428.6
2607.1 | 2509.1 | 525.9 | 480.5 | 509.2 | 481.4 | 489.7 | 489.2 | 483.7 | 482.2 | 464.5 | 428.6
2608.1 | 2510.1 | 525.9 | 480.5 | 509.2 | 481.4 | 489.8 | 489.2 | 483.8 | 482.3 | 464.6 | 428.7
2609.1 | 2511.1 | 525.9 | 480.5 | 509.2 | 481.4 | 489.8 | 489.3 | 483.8 | 482.4 | 464.6 | 428.7
2610.1 | 2512.1 | 525.9 | 480.5 | 509.2 | 481.5 | 489.9 | 489.3 | 483.9 | 482.4 | 464.6 | 428.7
2611.1 | 2513.1 | 525.9 | 480.6 | 509.1 | 481.5 | 489.9 | 489.3 | 483.9 | 482.4 | 464.7 | 428.7
2612.1 | 2514.1 | 526 | 480.5 | 509.2 | 481.4 | 489.9 | 489.4 | 483.9 | 482.5 | 464.7 | 428.8
2613.1 | 2515.1 | 526 | 480.6 | 509.2 | 481.5 | 489.9 | 489.4 | 484 | 482.5 | 464.7 | 428.8
2614.1 | 2516.1 | 526.1 | 480.6 | 509.2 | 481.5 | 490 | 489.4 | 484 | 482.5 | 464.7 | 428.8
2615.1 | 2517.1 | 526.1 | 480.6 | 509.3 | 481.5 | 490 | 489.5 | 484 | 482.6 | 464.7 | 428.8
2616.1 | 2518.1 | 526.1 | 480.6 | 509.3 | 481.5 | 490 | 489.5 | 484.1 | 482.6 | 464.8 | 428.9
2617.1 | 2519.1 | 526.2 | 480.6 | 509.3 | 481.5 | 490.1 | 489.5 | 484.1 | 482.6 | 464.8 | 428.9
2618.1 | 2520.1 | 526.2 | 480.6 | 509.3 | 481.5 | 490.1 | 489.6 | 484.2 | 482.7 | 464.8 | 428.9
2619.1 | 2521.1 | 526.2 | 480.6 | 509.3 | 481.5 | 490.1 | 489.6 | 484.2 | 482.8 | 464.9 | 429
2620.1 | 2522.1 | 526.2 | 480.6 | 509.4 | 481.5 | 490.2 | 489.6 | 484.2 | 482.9 | 464.9 | 429
2621.1 | 2523.1 | 526.2 | 480.6 | 509.4 | 481.5 | 490.2 | 489.7 | 484.3 | 483 | 464.9 | 429
2622.1 | 2524.1 | 526.2 | 480.6 | 509.3 | 481.5 | 490.2 | 489.7 | 484.3 | 483.1 | 465 | 429
2623.1 | 2525.1 | 526.2 | 480.6 | 509.4 | 481.5 | 490.3 | 489.8 | 484.3 | 483.1 | 465 | 429
2624.1 | 2526.1 | 526.2 | 480.6 | 509.4 | 481.5 | 490.3 | 489.8 | 484.4 | 483.2 | 465 | 429.1
2625.1 | 2527.1 | 526.2 | 480.6 | 509.4 | 481.5 | 490.3 | 489.8 | 484.4 | 483.3 | 465 | 429.1
2626.1 | 2528.1 | 526.2 | 480.6 | 509.4 | 481.5 | 490.4 | 489.9 | 484.4 | 483.3 | 465.1 | 429.1
2627.1 | 2529.1 | 526.2 | 480.7 | 509.5 | 481.5 | 490.4 | 489.9 | 484.5 | 483.3 | 465.1 | 429.1
2628.1 | 2530.1 | 526.2 | 480.7 | 509.5 | 481.5 | 490.4 | 489.9 | 484.5 | 483.3 | 465.1 | 429.2
2629.1 | 2531.1 | 526.2 | 480.7 | 509.5 | 481.5 | 490.5 | 489.9 | 484.5 | 483.4 | 465.1 | 429.2
2630.1 | 2532.1 | 526.1 | 480.7 | 509.5 | 481.6 | 490.5 | 490 | 484.6 | 483.5 | 465.2 | 429.2
2631.1 | 2533.1 | 526 | 480.7 | 509.5 | 481.6 | 490.5 | 490 | 484.6 | 483.5 | 465.2 | 429.2
2632.1 | 2534.1 | 526 | 480.7 | 509.5 | 481.6 | 490.6 | 490 | 484.7 | 483.6 | 465.2 | 429.2
2633.1 | 2535.1 | 525.9 | 480.7 | 509.5 | 481.5 | 490.6 | 490.1 | 484.7 | 483.6 | 465.2 | 429.2
2634.1 | 2536.1 | 525.9 | 480.8 | 509.5 | 481.6 | 490.6 | 490.1 | 484.7 | 483.6 | 465.3 | 429.3
2635.1 | 2537.1 | 525.9 | 480.8 | 509.5 | 481.6 | 490.7 | 490.1 | 484.8 | 483.6 | 465.3 | 429.3
2636.1 | 2538.1 | 525.9 | 480.8 | 509.5 | 481.6 | 490.7 | 490.2 | 484.8 | 483.6 | 465.3 | 429.3
2637.1 | 2539.1 | 525.9 | 480.8 | 509.5 | 481.6 | 490.7 | 490.2 | 484.8 | 483.7 | 465.4 | 429.4
2638.1 | 2540.1 | 525.9 | 480.8 | 509.6 | 481.6 | 490.8 | 490.2 | 484.9 | 483.7 | 465.4 | 429.4
2639.1 | 2541.1 | 525.9 | 480.8 | 509.6 | 481.6 | 490.8 | 490.3 | 484.9 | 483.7 | 465.4 | 429.4
2640.1 | 2542.1 | 525.9 | 480.8 | 509.5 | 481.6 | 490.8 | 490.3 | 484.9 | 483.8 | 465.4 | 429.4
2641.1 | 2543.1 | 525.9 | 480.8 | 509.5 | 481.6 | 490.8 | 490.3 | 485 | 483.8 | 465.5 | 429.4
2642.1 | 2544.1 | 525.9 | 480.8 | 509.5 | 481.6 | 490.9 | 490.4 | 485 | 483.8 | 465.5 | 429.5
2643.1 | 2545.1 | 526 | 480.8 | 509.6 | 481.6 | 490.9 | 490.4 | 485.1 | 483.8 | 465.5 | 429.5
2644.1 | 2546.1 | 526 | 480.8 | 509.6 | 481.6 | 490.9 | 490.4 | 485.1 | 483.8 | 465.5 | 429.5
2645.1 | 2547.1 | 526 | 480.9 | 509.6 | 481.6 | 491 | 490.5 | 485.1 | 483.8 | 465.6 | 429.5
2646.1 | 2548.1 | 526 | 480.9 | 509.6 | 481.6 | 491 | 490.5 | 485.2 | 483.9 | 465.6 | 429.6
2647.1 | 2549.1 | 526 | 480.9 | 509.7 | 481.6 | 491 | 490.5 | 485.2 | 483.9 | 465.6 | 429.6
2648.1 | 2550.1 | 526 | 481 | 509.5 | 481.7 | 491.2 | 490.6 | 485.2 | 483.9 | 465.6 | 429.7
2649.1 | 2551.1 | 526 | 480.9 | 509.6 | 481.7 | 491.2 | 490.6 | 485.3 | 484 | 465.7 | 429.7
2650.1 | 2552.1 | 526 | 480.9 | 509.7 | 481.6 | 491.1 | 490.6 | 485.3 | 484 | 465.7 | 429.7
2651.1 | 2553.1 | 526 | 480.9 | 509.7 | 481.6 | 491.2 | 490.7 | 485.3 | 484.1 | 465.7 | 429.7
2652.1 | 2554.1 | 526 | 480.9 | 509.7 | 481.7 | 491.2 | 490.7 | 485.4 | 484.2 | 465.8 | 429.7
2653.1 | 2555.1 | 526 | 480.9 | 509.7 | 481.7 | 491.2 | 490.7 | 485.4 | 484.2 | 465.8 | 429.7
2654.1 | 2556.1 | 526 | 481.2 | 509.1 | 481.9 | 491.6 | 491 | 485.4 | 484.1 | 465.7 | 430.2
2655.1 | 2557.1 | 526 | 481 | 509.7 | 481.7 | 491.3 | 490.8 | 485.5 | 484.1 | 465.8 | 429.8
2656.1 | 2558.1 | 526.1 | 481 | 509.7 | 481.7 | 491.3 | 490.8 | 485.5 | 484.2 | 465.9 | 429.8
2657.1 | 2559.1 | 526.1 | 481.1 | 509.4 | 481.8 | 491.6 | 491 | 485.5 | 484.2 | 465.8 | 430.1
2658.1 | 2560.1 | 526.1 | 481 | 509.8 | 481.7 | 491.4 | 490.9 | 485.6 | 484.3 | 465.9 | 429.9
2659.1 | 2561.1 | 526.1 | 481 | 509.7 | 481.7 | 491.5 | 491 | 485.6 | 484.4 | 465.9 | 430
2660.1 | 2562.1 | 526.1 | 481 | 509.7 | 481.7 | 491.5 | 491 | 485.7 | 484.4 | 466 | 429.9
2661.1 | 2563.1 | 526.1 | 481 | 509.8 | 481.7 | 491.5 | 491 | 485.7 | 484.5 | 466 | 430
2662.1 | 2564.1 | 526.1 | 481 | 509.8 | 481.7 | 491.5 | 491 | 485.7 | 484.6 | 466 | 430
2663.1 | 2565.1 | 526.1 | 481 | 509.8 | 481.7 | 491.6 | 491.1 | 485.8 | 484.6 | 466 | 430
2664.1 | 2566.1 | 526.1 | 481 | 509.8 | 481.7 | 491.6 | 491.1 | 485.8 | 484.6 | 466.1 | 430.1
2665.1 | 2567.1 | 526.1 | 481.2 | 509.6 | 481.8 | 491.8 | 491.2 | 485.8 | 484.7 | 466.1 | 430.2
2666.1 | 2568.1 | 526.1 | 481.1 | 509.8 | 481.7 | 491.7 | 491.2 | 485.9 | 484.7 | 466.1 | 430.1
2667.1 | 2569.1 | 526.1 | 481.1 | 509.8 | 481.7 | 491.7 | 491.2 | 485.9 | 484.8 | 466.1 | 430.1
2668.1 | 2570.1 | 526.1 | 481.1 | 509.8 | 481.7 | 491.7 | 491.2 | 485.9 | 484.8 | 466.2 | 430.1
2669.1 | 2571.1 | 526.1 | 481.1 | 509.8 | 481.7 | 491.8 | 491.3 | 486 | 484.9 | 466.2 | 430.1
2670.1 | 2572.1 | 526.1 | 481.1 | 509.9 | 481.7 | 491.8 | 491.3 | 486 | 485 | 466.2 | 430.2
2671.1 | 2573.1 | 526.1 | 481.1 | 509.9 | 481.7 | 491.8 | 491.3 | 486.1 | 485 | 466.2 | 430.2
2672.1 | 2574.1 | 526.1 | 481.1 | 509.9 | 481.8 | 491.9 | 491.4 | 486.1 | 485.1 | 466.2 | 430.2
2673.1 | 2575.1 | 526.1 | 481.1 | 509.9 | 481.8 | 491.9 | 491.4 | 486.1 | 485.2 | 466.3 | 430.2
2674.1 | 2576.1 | 526.1 | 481.1 | 509.9 | 481.8 | 491.9 | 491.4 | 486.2 | 485.2 | 466.3 | 430.3
2675.1 | 2577.1 | 526 | 481.1 | 509.9 | 481.8 | 492 | 491.5 | 486.2 | 485.3 | 466.3 | 430.3
2676.1 | 2578.1 | 526 | 481.1 | 509.9 | 481.8 | 492 | 491.5 | 486.2 | 485.4 | 466.3 | 430.3
2677.1 | 2579.1 | 526 | 481.2 | 509.9 | 481.8 | 492 | 491.5 | 486.3 | 485.5 | 466.4 | 430.3
2678.1 | 2580.1 | 526 | 481.2 | 510 | 481.8 | 492 | 491.6 | 486.3 | 485.4 | 466.4 | 430.3
2679.1 | 2581.1 | 526 | 481.2 | 509.9 | 481.8 | 492.1 | 491.6 | 486.3 | 485.4 | 466.4 | 430.4
2680.1 | 2582.1 | 526 | 481.2 | 509.9 | 481.8 | 492.1 | 491.6 | 486.4 | 485.4 | 466.4 | 430.4
2681.1 | 2583.1 | 526 | 481.2 | 509.9 | 481.8 | 492.1 | 491.6 | 486.4 | 485.4 | 466.4 | 430.4
2682.1 | 2584.1 | 526 | 481.2 | 510 | 481.8 | 492.2 | 491.7 | 486.4 | 485.4 | 466.5 | 430.4
2683.1 | 2585.1 | 526 | 481.2 | 510 | 481.8 | 492.2 | 491.7 | 486.5 | 485.4 | 466.5 | 430.4
2684.1 | 2586.1 | 526 | 481.2 | 510 | 481.8 | 492.2 | 491.7 | 486.5 | 485.4 | 466.5 | 430.5
2685.1 | 2587.1 | 526 | 481.2 | 510 | 481.8 | 492.3 | 491.8 | 486.6 | 485.4 | 466.6 | 430.5
2686.1 | 2588.1 | 526.1 | 481.2 | 510 | 481.8 | 492.3 | 491.8 | 486.6 | 485.4 | 466.6 | 430.5
2687.1 | 2589.1 | 526.1 | 481.2 | 510.1 | 481.8 | 492.3 | 491.8 | 486.6 | 485.4 | 466.6 | 430.5
2688.1 | 2590.1 | 526.1 | 481.2 | 510 | 481.8 | 492.4 | 491.9 | 486.7 | 485.5 | 466.6 | 430.5
2689.1 | 2591.1 | 526 | 481.2 | 510 | 481.8 | 492.4 | 491.9 | 486.7 | 485.6 | 466.6 | 430.6
2690.1 | 2592.1 | 526 | 481.3 | 509.9 | 481.9 | 492.5 | 492 | 486.7 | 485.6 | 466.6 | 430.7
2691.1 | 2593.1 | 526 | 481.3 | 510.1 | 481.8 | 492.5 | 492 | 486.8 | 485.7 | 466.7 | 430.6
2692.1 | 2594.1 | 526 | 481.3 | 510.1 | 481.8 | 492.5 | 492 | 486.8 | 485.7 | 466.7 | 430.6
2693.1 | 2595.1 | 526 | 481.3 | 510.1 | 481.9 | 492.6 | 492 | 486.8 | 485.8 | 466.7 | 430.7
2694.1 | 2596.1 | 526 | 481.3 | 510.1 | 481.8 | 492.6 | 492.1 | 486.9 | 485.8 | 466.7 | 430.7
2695.1 | 2597.1 | 526 | 481.3 | 510.1 | 481.8 | 492.6 | 492.1 | 486.9 | 485.8 | 466.8 | 430.7
2696.1 | 2598.1 | 526 | 481.3 | 510.1 | 481.9 | 492.7 | 492.1 | 486.9 | 485.9 | 466.8 | 430.7
2697.1 | 2599.1 | 526 | 481.3 | 510.1 | 481.9 | 492.7 | 492.2 | 487 | 485.9 | 466.8 | 430.8
2698.1 | 2600.1 | 526 | 481.4 | 510 | 481.9 | 492.8 | 492.2 | 487 | 485.9 | 466.8 | 430.8
2699.1 | 2601.1 | 526 | 481.4 | 510.1 | 481.9 | 492.7 | 492.2 | 487.1 | 485.9 | 466.9 | 430.8
2700.1 | 2602.1 | 526 | 481.4 | 510.2 | 481.9 | 492.8 | 492.3 | 487.1 | 485.9 | 466.9 | 430.8
2701.1 | 2603.1 | 526 | 481.4 | 510.1 | 481.9 | 492.8 | 492.3 | 487.1 | 485.9 | 466.9 | 430.8
2702.1 | 2604.1 | 526 | 481.4 | 510.2 | 481.9 | 492.8 | 492.3 | 487.2 | 486 | 466.9 | 430.8
2703.1 | 2605.1 | 526 | 481.4 | 510.2 | 481.9 | 492.9 | 492.4 | 487.2 | 486 | 466.9 | 430.9
2704.1 | 2606.1 | 526 | 481.4 | 510.2 | 481.9 | 492.9 | 492.4 | 487.2 | 486 | 467 | 430.9
2705.1 | 2607.1 | 526 | 481.4 | 510.2 | 481.9 | 492.9 | 492.4 | 487.3 | 486 | 467 | 430.9
2706.1 | 2608.1 | 526 | 481.4 | 510.2 | 481.9 | 493 | 492.5 | 487.3 | 486.1 | 467 | 431
2707.1 | 2609.1 | 526 | 481.4 | 510.2 | 481.9 | 493 | 492.5 | 487.3 | 486.2 | 467 | 430.9
2708.1 | 2610.1 | 526.1 | 481.4 | 510.2 | 481.9 | 493 | 492.5 | 487.4 | 486.2 | 467.1 | 431
2709.1 | 2611.1 | 526.1 | 481.4 | 510.2 | 481.9 | 493.1 | 492.5 | 487.4 | 486.2 | 467.1 | 431
2710.1 | 2612.1 | 526.1 | 481.4 | 510.3 | 481.9 | 493.1 | 492.6 | 487.4 | 486.2 | 467.1 | 431
2711.1 | 2613.1 | 526.1 | 481.4 | 510.3 | 481.9 | 493.1 | 492.6 | 487.5 | 486.2 | 467.1 | 431
2712.1 | 2614.1 | 526.1 | 481.5 | 510.3 | 481.9 | 493.2 | 492.6 | 487.5 | 486.3 | 467.1 | 431.1
2713.1 | 2615.1 | 526.1 | 481.5 | 510.3 | 481.9 | 493.2 | 492.7 | 487.5 | 486.3 | 467.2 | 431.1
2714.1 | 2616.1 | 526.1 | 481.5 | 510.3 | 481.9 | 493.2 | 492.7 | 487.6 | 486.4 | 467.2 | 431.1
2715.1 | 2617.1 | 526.1 | 481.5 | 510.3 | 481.9 | 493.3 | 492.7 | 487.6 | 486.5 | 467.2 | 431.1
2716.1 | 2618.1 | 526.1 | 481.5 | 510.3 | 481.9 | 493.3 | 492.8 | 487.6 | 486.7 | 467.2 | 431.1
2717.1 | 2619.1 | 526.1 | 481.5 | 510.3 | 481.9 | 493.3 | 492.8 | 487.7 | 486.7 | 467.2 | 431.2
2718.1 | 2620.1 | 526.1 | 481.5 | 510.3 | 481.9 | 493.4 | 492.8 | 487.7 | 486.7 | 467.3 | 431.2
2719.1 | 2621.1 | 526.2 | 481.5 | 510.3 | 481.9 | 493.4 | 492.9 | 487.7 | 486.7 | 467.3 | 431.2
2720.1 | 2622.1 | 526.1 | 481.6 | 510.4 | 481.9 | 493.4 | 492.9 | 487.8 | 486.8 | 467.3 | 431.2
2721.1 | 2623.1 | 526.1 | 481.6 | 510.4 | 481.9 | 493.4 | 492.9 | 487.8 | 486.8 | 467.3 | 431.3
2722.1 | 2624.1 | 526.1 | 481.6 | 510.4 | 481.9 | 493.5 | 493 | 487.9 | 486.8 | 467.3 | 431.2
2723.1 | 2625.1 | 526.1 | 481.6 | 510.4 | 481.9 | 493.5 | 493 | 487.9 | 486.8 | 467.4 | 431.3
2724.1 | 2626.1 | 526.1 | 481.6 | 510.3 | 481.9 | 493.5 | 493 | 487.9 | 486.9 | 467.4 | 431.3
2725.1 | 2627.1 | 526.2 | 481.6 | 510.3 | 481.9 | 493.6 | 493 | 488 | 487 | 467.4 | 431.3
2726.1 | 2628.1 | 526.2 | 481.6 | 510.4 | 482 | 493.6 | 493.1 | 488 | 487.1 | 467.4 | 431.3
2727.1 | 2629.1 | 526.2 | 481.6 | 510.4 | 482 | 493.6 | 493.1 | 488 | 487.1 | 467.4 | 431.4
2728.1 | 2630.1 | 526.2 | 481.6 | 510.4 | 481.9 | 493.6 | 493.1 | 488.1 | 487.1 | 467.5 | 431.4
2729.1 | 2631.1 | 526.2 | 481.6 | 510.4 | 482 | 493.7 | 493.2 | 488.1 | 487 | 467.5 | 431.4
2730.1 | 2632.1 | 526.2 | 481.6 | 510.4 | 482 | 493.7 | 493.2 | 488.1 | 487 | 467.5 | 431.4
2731.1 | 2633.1 | 526.2 | 481.6 | 510.4 | 482 | 493.7 | 493.2 | 488.2 | 487.1 | 467.5 | 431.4
2732.1 | 2634.1 | 526.2 | 481.7 | 510.4 | 482 | 493.8 | 493.3 | 488.2 | 487.1 | 467.5 | 431.5
2733.1 | 2635.1 | 526.2 | 481.7 | 510.5 | 482 | 493.8 | 493.3 | 488.2 | 487.2 | 467.6 | 431.4
2734.1 | 2636.1 | 526.2 | 481.7 | 510.5 | 481.9 | 493.8 | 493.3 | 488.3 | 487.2 | 467.6 | 431.5
2735.1 | 2637.1 | 526.2 | 481.7 | 510.4 | 482 | 493.9 | 493.4 | 488.3 | 487.2 | 467.6 | 431.5
2736.1 | 2638.1 | 526.2 | 481.7 | 510.5 | 482 | 493.9 | 493.4 | 488.3 | 487.2 | 467.6 | 431.5
2737.1 | 2639.1 | 526.2 | 481.7 | 510.5 | 482 | 493.9 | 493.4 | 488.4 | 487.2 | 467.7 | 431.5
2738.1 | 2640.1 | 526.1 | 481.7 | 510.5 | 482 | 494 | 493.4 | 488.4 | 487.3 | 467.7 | 431.5
2739.1 | 2641.1 | 526.1 | 481.7 | 510.5 | 482 | 494 | 493.5 | 488.4 | 487.3 | 467.7 | 431.6
2740.1 | 2642.1 | 526.1 | 481.7 | 510.5 | 482 | 494 | 493.5 | 488.5 | 487.3 | 467.7 | 431.6
2741.1 | 2643.1 | 526.2 | 481.7 | 510.6 | 482 | 494 | 493.5 | 488.5 | 487.3 | 467.7 | 431.6
2742.1 | 2644.1 | 526.1 | 481.8 | 510.6 | 482 | 494.1 | 493.6 | 488.5 | 487.3 | 467.8 | 431.6
2743.1 | 2645.1 | 526.2 | 481.8 | 510.6 | 482 | 494.1 | 493.6 | 488.6 | 487.4 | 467.8 | 431.6
2744.1 | 2646.1 | 526.2 | 481.8 | 510.6 | 482 | 494.1 | 493.6 | 488.6 | 487.5 | 467.8 | 431.6
2745.1 | 2647.1 | 526.2 | 481.8 | 510.6 | 482 | 494.2 | 493.6 | 488.6 | 487.6 | 467.8 | 431.6
2746.1 | 2648.1 | 526.2 | 481.8 | 510.6 | 482 | 494.2 | 493.7 | 488.7 | 487.6 | 467.8 | 431.7
2747.1 | 2649.1 | 526.2 | 481.8 | 510.6 | 482 | 494.2 | 493.7 | 488.7 | 487.7 | 467.9 | 431.7
2748.1 | 2650.1 | 526.2 | 481.8 | 510.6 | 482 | 494.3 | 493.7 | 488.7 | 487.7 | 467.9 | 431.7
2749.1 | 2651.1 | 526.2 | 481.8 | 510.7 | 482 | 494.3 | 493.8 | 488.8 | 487.8 | 467.9 | 431.7
2750.1 | 2652.1 | 526.2 | 481.8 | 510.7 | 482 | 494.3 | 493.8 | 488.8 | 487.9 | 467.9 | 431.7
2751.1 | 2653.1 | 526.1 | 481.8 | 510.7 | 482 | 494.3 | 493.8 | 488.8 | 487.9 | 467.9 | 431.8
2752.1 | 2654.1 | 526.1 | 481.8 | 510.7 | 482 | 494.4 | 493.9 | 488.9 | 488 | 468 | 431.8
2753.1 | 2655.1 | 526.1 | 481.9 | 510.7 | 482 | 494.4 | 493.9 | 488.9 | 488 | 468 | 431.8
2754.1 | 2656.1 | 526.1 | 481.9 | 510.7 | 482 | 494.4 | 493.9 | 488.9 | 488 | 468 | 431.8
2755.1 | 2657.1 | 526.1 | 481.9 | 510.7 | 482 | 494.5 | 493.9 | 489 | 488 | 468 | 431.8
2756.1 | 2658.1 | 526.1 | 481.9 | 510.7 | 482 | 494.5 | 494 | 489 | 488 | 468 | 431.8
2757.1 | 2659.1 | 526.1 | 481.9 | 510.8 | 482 | 494.5 | 494 | 489 | 488.1 | 468 | 431.8
2758.1 | 2660.1 | 526 | 481.9 | 510.8 | 482 | 494.6 | 494 | 489.1 | 488.2 | 468 | 431.9
2759.1 | 2661.1 | 526 | 481.9 | 510.7 | 482 | 494.6 | 494 | 489.1 | 488.2 | 468.1 | 431.9
2760.1 | 2662.1 | 526 | 481.9 | 510.7 | 482 | 494.6 | 494.1 | 489.1 | 488.3 | 468.1 | 431.9
2761.1 | 2663.1 | 526 | 481.9 | 510.8 | 482 | 494.6 | 494.1 | 489.1 | 488.3 | 468.1 | 431.9
2762.1 | 2664.1 | 526 | 481.9 | 510.8 | 482 | 494.6 | 494.1 | 489.2 | 488.3 | 468.1 | 431.9
2763.1 | 2665.1 | 526 | 481.9 | 510.8 | 482 | 494.7 | 494.1 | 489.2 | 488.4 | 468.1 | 431.9
2764.1 | 2666.1 | 526 | 481.9 | 510.8 | 482 | 494.7 | 494.1 | 489.2 | 488.4 | 468.1 | 431.9
2765.1 | 2667.1 | 526 | 481.9 | 510.8 | 482 | 494.7 | 494.2 | 489.3 | 488.4 | 468.1 | 431.9
2766.1 | 2668.1 | 526 | 481.9 | 510.9 | 482.1 | 494.7 | 494.2 | 489.3 | 488.4 | 468.2 | 432
2767.1 | 2669.1 | 526 | 481.9 | 510.9 | 482 | 494.8 | 494.2 | 489.3 | 488.5 | 468.2 | 432
2768.1 | 2670.1 | 526 | 481.9 | 510.9 | 482 | 494.8 | 494.2 | 489.4 | 488.5 | 468.2 | 432
2769.1 | 2671.1 | 525.9 | 482 | 510.9 | 482.1 | 494.8 | 494.3 | 489.4 | 488.5 | 468.2 | 432
2770.1 | 2672.1 | 525.9 | 482 | 510.9 | 482.1 | 494.8 | 494.3 | 489.4 | 488.6 | 468.2 | 432
2771.1 | 2673.1 | 525.9 | 482 | 510.9 | 482.1 | 494.9 | 494.3 | 489.5 | 488.6 | 468.2 | 432
2772.1 | 2674.1 | 525.9 | 482 | 510.9 | 482.1 | 494.9 | 494.4 | 489.5 | 488.6 | 468.2 | 432
2773.1 | 2675.1 | 525.9 | 482 | 510.9 | 482.1 | 494.9 | 494.4 | 489.5 | 488.6 | 468.3 | 432
2774.1 | 2676.1 | 526 | 482 | 510.9 | 482.1 | 495 | 494.4 | 489.5 | 488.6 | 468.3 | 432
2775.1 | 2677.1 | 526 | 482 | 510.9 | 482.1 | 495 | 494.5 | 489.6 | 488.6 | 468.3 | 432.1
2776.1 | 2678.1 | 526 | 482 | 510.9 | 482.1 | 495 | 494.5 | 489.6 | 488.6 | 468.3 | 432.1
2777.1 | 2679.1 | 526.1 | 482 | 510.9 | 482.1 | 495.1 | 494.5 | 489.6 | 488.6 | 468.4 | 432.1
2778.1 | 2680.1 | 526.1 | 482 | 510.9 | 482.1 | 495.1 | 494.6 | 489.7 | 488.6 | 468.4 | 432.1
2779.1 | 2681.1 | 526.1 | 482 | 510.9 | 482.1 | 495.1 | 494.6 | 489.7 | 488.6 | 468.4 | 432.1
2780.1 | 2682.1 | 526.1 | 482.1 | 510.9 | 482.1 | 495.1 | 494.6 | 489.7 | 488.8 | 468.4 | 432.1
2781.1 | 2683.1 | 526.2 | 482.1 | 510.9 | 482.1 | 495.1 | 494.6 | 489.8 | 488.8 | 468.4 | 432.2
2782.1 | 2684.1 | 526.2 | 482.1 | 511 | 482.1 | 495.2 | 494.7 | 489.8 | 488.8 | 468.4 | 432.2
2783.1 | 2685.1 | 526.2 | 482.1 | 511 | 482.1 | 495.2 | 494.7 | 489.8 | 488.9 | 468.5 | 432.2
2784.1 | 2686.1 | 526.3 | 482.1 | 511 | 482.1 | 495.2 | 494.7 | 489.9 | 488.8 | 468.5 | 432.2
2785.1 | 2687.1 | 526.3 | 482.1 | 511 | 482.1 | 495.2 | 494.8 | 489.9 | 488.8 | 468.5 | 432.2
2786.1 | 2688.1 | 526.3 | 482.1 | 511 | 482.1 | 495.3 | 494.8 | 489.9 | 488.8 | 468.5 | 432.2
2787.1 | 2689.1 | 526.3 | 482.1 | 511 | 482.1 | 495.3 | 494.8 | 490 | 488.8 | 468.5 | 432.2
2788.1 | 2690.1 | 526.3 | 482.1 | 511 | 482.1 | 495.3 | 494.8 | 490 | 488.9 | 468.6 | 432.2
2789.1 | 2691.1 | 526.3 | 482.1 | 511 | 482.1 | 495.3 | 494.9 | 490 | 489 | 468.6 | 432.3
2790.1 | 2692.1 | 526.3 | 482.1 | 511 | 482.1 | 495.4 | 494.9 | 490.1 | 489.1 | 468.6 | 432.3
2791.1 | 2693.1 | 526.3 | 482.1 | 511.1 | 482.1 | 495.4 | 494.9 | 490.1 | 489.1 | 468.6 | 432.3
2792.1 | 2694.1 | 526.3 | 482.2 | 511.1 | 482.1 | 495.4 | 494.9 | 490.1 | 489.2 | 468.6 | 432.3
2793.1 | 2695.1 | 526.3 | 482.2 | 511.1 | 482.1 | 495.4 | 495 | 490.1 | 489.2 | 468.6 | 432.3
2794.1 | 2696.1 | 526.4 | 482.2 | 511.1 | 482.1 | 495.5 | 495 | 490.2 | 489.2 | 468.7 | 432.3
2795.1 | 2697.1 | 526.4 | 482.2 | 511.1 | 482.1 | 495.5 | 495 | 490.2 | 489.2 | 468.7 | 432.3
2796.1 | 2698.1 | 526.4 | 482.2 | 511.1 | 482.1 | 495.5 | 495 | 490.2 | 489.2 | 468.7 | 432.4
2797.1 | 2699.1 | 526.4 | 482.2 | 511.1 | 482.1 | 495.6 | 495.1 | 490.3 | 489.2 | 468.7 | 432.4
2798.1 | 2700.1 | 526.4 | 482.2 | 511.2 | 482.1 | 495.6 | 495.1 | 490.3 | 489.3 | 468.7 | 432.4
2799.1 | 2701.1 | 526.4 | 482.2 | 511.2 | 482.1 | 495.6 | 495.1 | 490.3 | 489.3 | 468.7 | 432.4
2800.1 | 2702.1 | 526.4 | 482.2 | 511.1 | 482.1 | 495.6 | 495.1 | 490.4 | 489.4 | 468.8 | 432.4
2801.1 | 2703.1 | 526.4 | 482.2 | 511.2 | 482.1 | 495.7 | 495.2 | 490.4 | 489.4 | 468.8 | 432.4
2802.1 | 2704.1 | 526.4 | 482.2 | 511.2 | 482.1 | 495.7 | 495.2 | 490.4 | 489.5 | 468.8 | 432.5
2803.1 | 2705.1 | 526.3 | 482.2 | 511.2 | 482.1 | 495.7 | 495.2 | 490.5 | 489.5 | 468.8 | 432.5
2804.1 | 2706.1 | 526.3 | 482.3 | 511.2 | 482.1 | 495.7 | 495.2 | 490.5 | 489.5 | 468.8 | 432.5
2805.1 | 2707.1 | 526.3 | 482.3 | 511.1 | 482.1 | 495.7 | 495.3 | 490.5 | 489.6 | 468.8 | 432.5
2806.1 | 2708.1 | 526.2 | 482.3 | 511.1 | 482.1 | 495.8 | 495.3 | 490.5 | 489.7 | 468.8 | 432.5
2807.1 | 2709.1 | 526.2 | 482.3 | 511.2 | 482.1 | 495.8 | 495.3 | 490.6 | 489.8 | 468.8 | 432.5
2808.1 | 2710.1 | 526.2 | 482.3 | 511.2 | 482.1 | 495.8 | 495.3 | 490.6 | 489.8 | 468.9 | 432.6
2809.1 | 2711.1 | 526.2 | 482.3 | 511.2 | 482.1 | 495.8 | 495.3 | 490.6 | 489.9 | 468.9 | 432.6
2810.1 | 2712.1 | 526.2 | 482.3 | 511.2 | 482.1 | 495.9 | 495.4 | 490.7 | 490 | 468.9 | 432.6
2811.1 | 2713.1 | 526.2 | 482.3 | 511.2 | 482.1 | 495.9 | 495.4 | 490.7 | 490 | 468.9 | 432.6
2812.1 | 2714.1 | 526.2 | 482.3 | 511.2 | 482.1 | 495.9 | 495.4 | 490.7 | 490.1 | 468.9 | 432.6
2813.1 | 2715.1 | 526.2 | 482.3 | 511.2 | 482.1 | 495.9 | 495.5 | 490.7 | 490.1 | 468.9 | 432.7
2814.1 | 2716.1 | 526.2 | 482.3 | 511.2 | 482.1 | 496 | 495.5 | 490.8 | 490.1 | 469 | 432.7
2815.1 | 2717.1 | 526.1 | 482.3 | 511.2 | 482.1 | 496 | 495.5 | 490.8 | 490.2 | 469 | 432.7
2816.1 | 2718.1 | 526.1 | 482.3 | 511.2 | 482.1 | 496 | 495.5 | 490.8 | 490.2 | 469 | 432.7
2817.1 | 2719.1 | 526.1 | 482.4 | 511.2 | 482.1 | 496 | 495.6 | 490.9 | 490.3 | 469 | 432.7
2818.1 | 2720.1 | 526.1 | 482.4 | 511.3 | 482.1 | 496.1 | 495.6 | 490.9 | 490.2 | 469 | 432.8
2819.1 | 2721.1 | 526.1 | 482.4 | 511.3 | 482.1 | 496.1 | 495.6 | 490.9 | 490.2 | 469 | 432.8
2820.1 | 2722.1 | 526 | 482.4 | 511.3 | 482.1 | 496.1 | 495.6 | 491 | 490.3 | 469.1 | 432.8
2821.1 | 2723.1 | 526.1 | 482.4 | 511.3 | 482.1 | 496.1 | 495.7 | 491 | 490.3 | 469.1 | 432.8
2822.1 | 2724.1 | 526.1 | 482.4 | 511.4 | 482.1 | 496.1 | 495.7 | 491 | 490.4 | 469.1 | 432.8
2823.1 | 2725.1 | 526.1 | 482.4 | 511.4 | 482.1 | 496.2 | 495.7 | 491 | 490.4 | 469.1 | 432.9
2824.1 | 2726.1 | 526.1 | 482.4 | 511.4 | 482.1 | 496.2 | 495.7 | 491.1 | 490.4 | 469.1 | 432.9
2825.1 | 2727.1 | 526.1 | 482.4 | 511.4 | 482.1 | 496.2 | 495.8 | 491.1 | 490.5 | 469.1 | 432.9
2826.1 | 2728.1 | 526.1 | 482.4 | 511.4 | 482.1 | 496.2 | 495.8 | 491.1 | 490.5 | 469.1 | 432.9
2827.1 | 2729.1 | 526.1 | 482.4 | 511.3 | 482.1 | 496.3 | 495.8 | 491.2 | 490.6 | 469.2 | 432.9
2828.1 | 2730.1 | 526 | 482.4 | 511.3 | 482.1 | 496.3 | 495.8 | 491.2 | 490.7 | 469.2 | 432.9
2829.1 | 2731.1 | 526 | 482.4 | 511.3 | 482.1 | 496.3 | 495.9 | 491.2 | 490.7 | 469.2 | 433
2830.1 | 2732.1 | 526 | 482.5 | 511.3 | 482.1 | 496.3 | 495.9 | 491.3 | 490.7 | 469.2 | 433
2831.1 | 2733.1 | 526 | 482.5 | 511.3 | 482.1 | 451.7 | 451.1 | 446.6 | 449.5 | 427.1 | 392.4
2832.1 | 2734.1 | 526 | 482.5 | 511.4 | 482.1 | 221.6 | 223.8 | 220 | 234.6 | 207.1 | 190
2833.1 | 2735.1 | 526 | 482.5 | 511.4 | 482.1 | 496.2 | 495.8 | 491.1 | 490.5 | 471.5 | 432.8
2834.1 | 2736.1 | 525.9 | 482.5 | 511.4 | 482.1 | 496.5 | 496 | 491.4 | 490.8 | 471.3 | 433.1
2835.1 | 2737.1 | 525.9 | 482.5 | 511.4 | 482.1 | 496.6 | 496.1 | 491.4 | 490.9 | 470.8 | 433.1
2836.1 | 2738.1 | 525.9 | 482.5 | 511.4 | 482.1 | 496.6 | 496.1 | 491.4 | 490.9 | 470.5 | 433.1
2837.1 | 2739.1 | 525.9 | 482.5 | 511.5 | 482.1 | 496.6 | 496.1 | 491.5 | 490.8 | 470.3 | 433.1
2838.1 | 2740.1 | 525.9 | 482.3 | 511.8 | 482 | 496.5 | 496.1 | 491.5 | 490.8 | 470.1 | 433.1
2839.1 | 2741.1 | 525.9 | 482.2 | 512.1 | 481.9 | 496.4 | 496.1 | 491.5 | 490.9 | 470 | 433
2840.1 | 2742.1 | 525.9 | 482.2 | 512.2 | 481.8 | 496.3 | 496.1 | 491.6 | 491 | 469.9 | 432.9
2841.1 | 2743.1 | 525.7 | 482.2 | 512.2 | 481.8 | 385.7 | 387.6 | 382.6 | 397.4 | 363.5 | 331.4
2842.1 | 2744.1 | 525.4 | 482.2 | 512.2 | 481.8 | 331.6 | 335.8 | 330.3 | 353.1 | 311.1 | 283.5
2843.1 | 2745.1 | 525.1 | 482.2 | 512.2 | 481.8 | 236.9 | 243.6 | 237.1 | 276.5 | 219.4 | 193.7
2844.1 | 2746.1 | 524.6 | 482.2 | 512.1 | 481.8 | 279.9 | 281.5 | 277.9 | 293.7 | 262.6 | 241
2845.1 | 2747.1 | 524.2 | 482.2 | 512.1 | 481.8 | 368.7 | 370.3 | 366.4 | 373.9 | 349.5 | 321.8
2846.1 | 2748.1 | 523.6 | 482.1 | 512.1 | 481.8 | 496.4 | 496.2 | 491.7 | 491.1 | 472.5 | 433
2847.1 | 2749.1 | 523 | 482.1 | 512 | 481.7 | 211.6 | 213.3 | 208.8 | 226.8 | 199.3 | 178.2
2848.1 | 2750.1 | 522.5 | 482.1 | 512 | 481.7 | 446.2 | 447 | 442.5 | 445.1 | 426 | 389.3
2849.1 | 2751.1 | 521.8 | 482.1 | 511.9 | 481.7 | 492.8 | 492.4 | 488 | 487.6 | 470.5 | 429.6
2850.1 | 2752.1 | 521.1 | 482 | 511.9 | 481.6 | 152 | 154.6 | 152.3 | 173.1 | 219.4 | 131.2
2851.1 | 2753.1 | 520.5 | 482 | 511.9 | 481.6 | 492.9 | 492.9 | 488.3 | 487.9 | 473.8 | 430
2852.1 | 2754.1 | 519.8 | 482 | 511.8 | 481.6 | 426.1 | 425.8 | 422.4 | 425.6 | 440.4 | 371.8
2853.1 | 2755.1 | 519 | 482 | 511.7 | 481.6 | 195.6 | 199.3 | 198.4 | 215.2 | 291.4 | 176
2854.1 | 2756.1 | 518.3 | 481.9 | 511.6 | 481.5 | 496.7 | 496.6 | 491.8 | 491.3 | 471.7 | 433
2855.1 | 2757.1 | 517.5 | 481.9 | 511.6 | 481.5 | 497 | 496.7 | 492.1 | 491.5 | 471.9 | 433.2
2856.1 | 2758.1 | 516.8 | 481.8 | 511.5 | 481.4 | 497.1 | 496.7 | 492.1 | 491.6 | 471.5 | 433.2
2857.1 | 2759.1 | 516 | 481.8 | 511.4 | 481.4 | 497.1 | 496.7 | 492.2 | 491.6 | 471.2 | 433.2
2858.1 | 2760.1 | 515.2 | 481.8 | 511.3 | 481.3 | 497.2 | 496.7 | 492.2 | 491.6 | 471 | 433.3
2859.1 | 2761.1 | 514.4 | 481.7 | 511.2 | 481.3 | 497.2 | 496.7 | 492.2 | 491.7 | 470.8 | 433.3
2860.1 | 2762.1 | 513.6 | 481.7 | 511.2 | 481.3 | 497.2 | 496.7 | 492.3 | 491.7 | 470.7 | 433.3
2861.1 | 2763.1 | 512.8 | 481.6 | 511.1 | 481.2 | 497.2 | 496.7 | 492.3 | 491.7 | 470.5 | 433.3
2862.1 | 2764.1 | 512 | 481.6 | 511 | 481.1 | 345.6 | 346.8 | 343.8 | 351.4 | 190.1 | 303.1
2863.1 | 2765.1 | 511.1 | 481.5 | 510.9 | 481.1 | 276.6 | 280.7 | 278 | 289.7 | 380.4 | 246.1
2864.1 | 2766.1 | 510.3 | 481.5 | 510.8 | 481 | 497.2 | 496.8 | 492.3 | 491.8 | 470.5 | 433.3
2865.1 | 2767.1 | 509.6 | 481.4 | 510.7 | 481 | 260.3 | 263.5 | 261.2 | 267.7 | -67.4 | 230.9
2866.1 | 2768.1 | 508.8 | 481.3 | 510.6 | 480.9 | 359.8 | 364 | 360.5 | 365.5 | 129.4 | 318.7
2867.1 | 2769.1 | 508 | 481.3 | 510.4 | 480.8 | 497.4 | 497 | 492.4 | 492.1 | 470.1 | 433.3
2868.1 | 2770.1 | 507.2 | 481.2 | 510.3 | 480.8 | 497.5 | 497 | 492.4 | 492.2 | 470.1 | 433.4
2869.1 | 2771.1 | 506.4 | 481.1 | 510.2 | 480.7 | 497.5 | 496.9 | 492.5 | 492.2 | 470.1 | 433.4
2870.1 | 2772.1 | 505.6 | 481.1 | 510.1 | 480.6 | 497.5 | 496.9 | 492.5 | 492.1 | 470 | 433.4
2871.1 | 2773.1 | 504.8 | 481 | 510 | 480.6 | 497.5 | 496.9 | 492.5 | 492.1 | 470 | 433.4
2872.1 | 2774.1 | 504 | 480.9 | 509.8 | 480.5 | 497.5 | 496.9 | 492.5 | 492.1 | 470 | 433.4
2873.1 | 2775.1 | 503.1 | 480.9 | 509.7 | 480.4 | 424.9 | 425.7 | 422.1 | 424.5 | 313.4 | 371.7
2874.1 | 2776.1 | 502.3 | 480.8 | 509.6 | 480.3 | 184 | 195.3 | 193.1 | 204.6 | NaN | 172.4
2875.1 | 2777.1 | 501.5 | 480.7 | 509.5 | 480.3 | 497.4 | 496.9 | 492.3 | 492 | 469 | 433.2
2876.1 | 2778.1 | 500.7 | 480.6 | 509.4 | 480.2 | 497.6 | 497.1 | 492.6 | 492.3 | 469.8 | 433.5
2877.1 | 2779.1 | 500 | 480.5 | 509.2 | 480.1 | 497.7 | 497 | 492.6 | 492.3 | 469.8 | 433.5
2878.1 | 2780.1 | 499.2 | 480.5 | 509.1 | 480 | 497.7 | 497 | 492.6 | 492.4 | 469.8 | 433.5
2879.1 | 2781.1 | 498.4 | 480.4 | 509 | 479.9 | 497.7 | 497 | 492.7 | 492.4 | 469.8 | 433.5
2880.1 | 2782.1 | 497.6 | 480.3 | 508.8 | 479.8 | 497.7 | 497 | 492.7 | 492.3 | 469.8 | 433.5
2881.1 | 2783.1 | 496.8 | 480.2 | 508.7 | 479.7 | 497.7 | 496.9 | 492.7 | 492.3 | 469.8 | 433.5
2882.1 | 2784.1 | 496 | 480.1 | 508.5 | 479.6 | 497.6 | 496.9 | 492.7 | 492.3 | 469.7 | 433.5
2883.1 | 2785.1 | 495.3 | 480 | 508.3 | 479.5 | 354.2 | 355.8 | 353.2 | 364.8 | 331.9 | 311.6
2884.1 | 2786.1 | 494.5 | 479.9 | 508.2 | 479.4 | 291.6 | 295.6 | 293.3 | 310.7 | 272.2 | 259.7
2885.1 | 2787.1 | 493.7 | 479.8 | 508 | 479.3 | 159.8 | 166.3 | 165.8 | 195.8 | 146.4 | 148.3
2886.1 | 2788.1 | 492.9 | 479.7 | 507.9 | 479.2 | 259.7 | 263 | 260.7 | 275 | 24.5 | 230.5
2887.1 | 2789.1 | 492.1 | 479.6 | 507.8 | 479.1 | 358.2 | 363.2 | 359.6 | 365.5 | 119.1 | 318.1
2888.1 | 2790.1 | 491.3 | 479.5 | 507.6 | 479 | 497.6 | 497.1 | 492.7 | 492.3 | 469.5 | 433.5
2889.1 | 2791.1 | 490.6 | 479.4 | 507.3 | 478.9 | 174.6 | 178.2 | 176.2 | 188.2 | -180.2 | 157.3
2890.1 | 2792.1 | 489.8 | 479.3 | 507.3 | 478.8 | 443.1 | 444.8 | 440.5 | 443.5 | 351.6 | 388.5
2891.1 | 2793.1 | 489 | 479.2 | 507.1 | 478.7 | 493.3 | 492.8 | 488.2 | 488.3 | 459.1 | 429.4
2892.1 | 2794.1 | 488.2 | 479.1 | 506.9 | 478.6 | 123.5 | 134 | 132.5 | 147.9 | NaN | 120.2
2893.1 | 2795.1 | 487.4 | 479 | 506.7 | 478.4 | 494.3 | 494.2 | 489.6 | 489.6 | 459.3 | 430.9
2894.1 | 2796.1 | 486.6 | 478.8 | 506.6 | 478.3 | 424.9 | 424.9 | 421.1 | 424.9 | 290.2 | 370.4
2895.1 | 2797.1 | 485.8 | 478.7 | 506.5 | 478.2 | 186.8 | 199.1 | 197 | 210.9 | NaN | 176.1
2896.1 | 2798.1 | 485 | 478.6 | 506.3 | 478.1 | 497.4 | 497 | 492.5 | 492.4 | 468.5 | 433.3
2897.1 | 2799.1 | 484.2 | 478.5 | 506.1 | 478 | 497.7 | 497.1 | 492.7 | 492.6 | 469.4 | 433.5
2898.1 | 2800.1 | 483.4 | 478.3 | 505.9 | 477.8 | 497.7 | 497 | 492.7 | 492.6 | 469.4 | 433.6
2899.1 | 2801.1 | 482.7 | 478.2 | 505.7 | 477.7 | 497.7 | 496.9 | 492.7 | 492.6 | 469.4 | 433.6
2900.1 | 2802.1 | 481.9 | 478.1 | 505.5 | 477.6 | 497.8 | 496.9 | 492.7 | 492.5 | 469.3 | 433.6
2901.1 | 2803.1 | 481.2 | 478 | 505.4 | 477.4 | 497.6 | 496.8 | 492.7 | 492.6 | 469.3 | 433.6
2902.1 | 2804.1 | 480.4 | 477.8 | 505.2 | 477.3 | 497.6 | 496.8 | 492.7 | 492.6 | 469.3 | 433.6
2903.1 | 2805.1 | 479.7 | 477.7 | 505 | 477.2 | 497.6 | 496.7 | 492.7 | 492.6 | 469.2 | 433.6
2904.1 | 2806.1 | 478.9 | 477.6 | 504.7 | 477.1 | 345.2 | 344.6 | 341 | 347.6 | 232.6 | 300.9
2905.1 | 2807.1 | 478.2 | 477.5 | 504.5 | 476.9 | 279.7 | 284 | 281.3 | 289.7 | 102.3 | 250
2906.1 | 2808.1 | 477.5 | 477.3 | 504.4 | 476.8 | 497.4 | 496.7 | 492.6 | 492.6 | 469 | 433.5
2907.1 | 2809.1 | 476.8 | 477.2 | 504.2 | 476.6 | 253 | 261.2 | 259.2 | 272.7 | -149.1 | 229.7
2908.1 | 2810.1 | 476 | 477 | 504 | 476.5 | 357.2 | 363.1 | 359.8 | 368 | 128.6 | 318.4
2909.1 | 2811.1 | 475.3 | 476.9 | 503.8 | 476.4 | 497.3 | 496.7 | 492.5 | 492.5 | 468.8 | 433.5
2910.1 | 2812.1 | 474.5 | 476.8 | 503.6 | 476.2 | 497.3 | 496.6 | 492.5 | 492.6 | 468.8 | 433.5
2911.1 | 2813.1 | 473.7 | 476.6 | 503.4 | 476 | 497.3 | 496.5 | 492.5 | 492.6 | 468.8 | 433.5
2912.1 | 2814.1 | 473 | 476.4 | 503.2 | 475.9 | 497.2 | 496.4 | 492.5 | 492.7 | 468.7 | 433.5
2913.1 | 2815.1 | 472.3 | 476.3 | 503 | 475.8 | 497.2 | 496.3 | 492.5 | 492.7 | 468.7 | 433.5
2914.1 | 2816.1 | 471.5 | 476.2 | 502.8 | 475.6 | 497.1 | 496.2 | 492.4 | 492.6 | 468.6 | 433.5
2915.1 | 2817.1 | 470.8 | 476 | 502.6 | 475.5 | 421 | 420.9 | 417.8 | 421.1 | 333.2 | 368.3
2916.1 | 2818.1 | 470.1 | 475.9 | 502.4 | 475.3 | 188.4 | 200.6 | 198.8 | 213.5 | NaN | 178.2
2917.1 | 2819.1 | 469.3 | 475.8 | 502 | 475.2 | 497.7 | 496.5 | 492 | 492.4 | 467.2 | 433.7
2918.1 | 2820.1 | 468.6 | 475.6 | 501.9 | 475 | 497 | 496.2 | 492.3 | 492.6 | 468.3 | 433.4
2919.1 | 2821.1 | 467.9 | 475.4 | 501.7 | 474.8 | 496.8 | 496 | 492.3 | 492.6 | 468.3 | 433.4
2920.1 | 2822.1 | 467.2 | 475.2 | 501.6 | 474.7 | 496.7 | 495.9 | 492.2 | 492.6 | 468.3 | 433.4
2921.1 | 2823.1 | 466.5 | 475.1 | 501.4 | 474.5 | 496.7 | 495.8 | 492.2 | 492.6 | 468.2 | 433.4
2922.1 | 2824.1 | 465.8 | 474.9 | 501.1 | 474.3 | 496.6 | 495.7 | 492.2 | 492.5 | 468.1 | 433.3
2923.1 | 2825.1 | 465 | 474.8 | 500.9 | 474.2 | 496.5 | 495.7 | 492.1 | 492.4 | 468 | 433.3
2924.1 | 2826.1 | 464.3 | 474.6 | 500.7 | 474 | 496.4 | 495.6 | 492.1 | 492.3 | 468 | 433.3
2925.1 | 2827.1 | 463.6 | 474.5 | 500.5 | 473.9 | 351.4 | 352.3 | 350.7 | 363.4 | 328 | 310.2
2926.1 | 2828.1 | 462.9 | 474.3 | 500.2 | 473.7 | 287.6 | 291 | 289.8 | 308.3 | 265.1 | 257.8
2927.1 | 2829.1 | 462.2 | 474.1 | 500 | 473.5 | 156.1 | 161.6 | 162.3 | 194 | 138.5 | 147
2928.1 | 2830.1 | 461.5 | 474 | 499.9 | 473.4 | 248.9 | 255.8 | 253.9 | 264.7 | -114.7 | 225.7
2929.1 | 2831.1 | 460.8 | 473.8 | 499.7 | 473.2 | 357.8 | 363.9 | 360.8 | 368.3 | 115.1 | 319.7
2930.1 | 2832.1 | 460.1 | 473.6 | 499.5 | 473 | 495.9 | 495.4 | 491.7 | 492.1 | 467.5 | 433.1
2931.1 | 2833.1 | 459.4 | 473.5 | 499.3 | 472.9 | 163.2 | 174.8 | 173.5 | 190.5 | NaN | 155.8
2932.1 | 2834.1 | 458.7 | 473.3 | 499.1 | 472.7 | 441.5 | 443.9 | 440.3 | 444.1 | 330.5 | 388.9
2933.1 | 2835.1 | 458.1 | 473.1 | 498.8 | 472.5 | 489.5 | 489.1 | 485.5 | 486.2 | 451.4 | 427.7
2934.1 | 2836.1 | 457.4 | 473 | 498.6 | 472.3 | 121.1 | 131 | 130.1 | 154 | NaN | 118.9
2935.1 | 2837.1 | 456.7 | 472.8 | 498.4 | 472.2 | 492.1 | 492 | 488.2 | 488.9 | 458.6 | 430.3
2936.1 | 2838.1 | 456 | 472.6 | 498.1 | 472 | 421.4 | 421.2 | 418.4 | 423.4 | 304 | 369.1
2937.1 | 2839.1 | 455.3 | 472.4 | 497.9 | 471.8 | 192.6 | 199.9 | 198.7 | 218.9 | NaN | 178.3
2938.1 | 2840.1 | 454.6 | 472.2 | 497.7 | 471.6 | 495.2 | 494.8 | 491.1 | 491.8 | 466.1 | 432.7
2939.1 | 2841.1 | 453.9 | 472.1 | 497.4 | 471.4 | 495.4 | 494.7 | 491.3 | 491.9 | 466.9 | 432.9
2940.1 | 2842.1 | 453.2 | 471.9 | 497.2 | 471.2 | 495.3 | 494.6 | 491.2 | 491.8 | 466.8 | 432.9
2941.1 | 2843.1 | 452.5 | 471.7 | 497 | 471.1 | 495.2 | 494.4 | 491.2 | 491.8 | 466.7 | 432.9
2942.1 | 2844.1 | 451.8 | 471.7 | 496.4 | 471 | 496.9 | 495.1 | 491 | 491.6 | 466.1 | 433.9
2943.1 | 2845.1 | 451.2 | 471.4 | 496.4 | 470.7 | 495.4 | 494.4 | 491 | 491.8 | 466.3 | 433
2944.1 | 2846.1 | 450.6 | 471.1 | 496.2 | 470.5 | 494.9 | 494.1 | 491 | 491.8 | 466.4 | 432.8
2945.1 | 2847.1 | 449.9 | 471 | 495.9 | 470.4 | 495.3 | 494.2 | 490.9 | 491.8 | 466.1 | 433
2946.1 | 2848.1 | 449.3 | 470.8 | 495.7 | 470.2 | 336.1 | 340.2 | 337.6 | 346.9 | 84 | 298.6
2947.1 | 2849.1 | 448.6 | 470.6 | 495.5 | 469.9 | 274.1 | 282.8 | 280.9 | 295.1 | -107.9 | 250.3
2948.1 | 2850.1 | 448 | 470.4 | 495.2 | 469.8 | 494.7 | 494 | 490.6 | 491.5 | 465.7 | 432.8
2949.1 | 2851.1 | 447.3 | 470.2 | 495 | 469.6 | 253.2 | 257.2 | 256.7 | 274 | -150.2 | 227.7
2950.1 | 2852.1 | 446.7 | 470 | 494.7 | 469.4 | 361.8 | 364.1 | 361.7 | 371.1 | 144 | 320.9
2951.1 | 2853.1 | 446 | 469.8 | 494.5 | 469.2 | 494.2 | 493.6 | 490.4 | 491.2 | 465.6 | 432.5
2952.1 | 2854.1 | 445.4 | 469.6 | 494.3 | 469 | 494.1 | 493.4 | 490.4 | 491.1 | 465.6 | 432.5
2953.1 | 2855.1 | 444.8 | 469.5 | 494 | 468.8 | 494 | 493.3 | 490.3 | 491 | 465.5 | 432.4
2954.1 | 2856.1 | 444.1 | 469.3 | 493.8 | 468.6 | 494.2 | 493.2 | 490.2 | 491 | 465.3 | 432.5
2955.1 | 2857.1 | 443.5 | 469.1 | 493.5 | 468.4 | 493.8 | 493 | 490.2 | 491 | 465.3 | 432.3
2956.1 | 2858.1 | 442.9 | 468.9 | 493.3 | 468.2 | 493.6 | 492.8 | 490.1 | 490.9 | 465.2 | 432.3
2957.1 | 2859.1 | 442.3 | 468.7 | 493 | 468 | 413.9 | 415.3 | 413.2 | 418.7 | 275.2 | 365.1
2958.1 | 2860.1 | 441.6 | 468.5 | 492.8 | 467.8 | 194.9 | 202.5 | 201.7 | 221.7 | NaN | 181.4
2959.1 | 2861.1 | 441 | 468.3 | 492.5 | 467.6 | 493 | 492.5 | 489.6 | 490.5 | 464.1 | 432
2960.1 | 2862.1 | 440.4 | 468.1 | 492.3 | 467.4 | 493.1 | 492.5 | 489.7 | 490.6 | 464.7 | 432.1
2961.1 | 2863.1 | 439.8 | 467.9 | 492 | 467.2 | 493 | 492.3 | 489.6 | 490.5 | 464.7 | 432.1
2962.1 | 2864.1 | 439.1 | 467.7 | 491.8 | 467 | 492.9 | 492.2 | 489.5 | 490.4 | 464.6 | 432
2963.1 | 2865.1 | 438.5 | 467.5 | 491.6 | 466.9 | 492.8 | 492.1 | 489.5 | 490.4 | 464.5 | 432
2964.1 | 2866.1 | 437.9 | 467.3 | 491.3 | 466.7 | 492.6 | 491.9 | 489.4 | 490.3 | 464.4 | 431.9
2965.1 | 2867.1 | 437.4 | 467.1 | 491 | 466.5 | 492.5 | 491.8 | 489.3 | 490.3 | 464.3 | 431.9
2966.1 | 2868.1 | 436.7 | 466.9 | 490.8 | 466.2 | 492.4 | 491.6 | 489.2 | 490.1 | 464.2 | 431.9
2967.1 | 2869.1 | 436.1 | 466.7 | 490.5 | 466 | 347.9 | 349 | 347.8 | 361.4 | 324.6 | 308.9
2968.1 | 2870.1 | 435.5 | 466.5 | 490.2 | 465.8 | 288.7 | 292.1 | 291.2 | 310.7 | 275.7 | 260.2
2969.1 | 2871.1 | 434.9 | 466.3 | 490 | 465.6 | 160.8 | 166.7 | 167.3 | 201.8 | 143.7 | 152.5
2970.1 | 2872.1 | 434.3 | 466.1 | 489.7 | 465.4 | 249 | 251.3 | 250.5 | 267.4 | -106.5 | 223.3
2971.1 | 2873.1 | 433.7 | 465.9 | 489.5 | 465.2 | 362.2 | 364.1 | 362.2 | 371.6 | 161 | 321.8
2972.1 | 2874.1 | 433.1 | 465.7 | 489.2 | 465 | 491.5 | 491.1 | 488.5 | 489.5 | 463.4 | 431.5
2973.1 | 2875.1 | 432.5 | 465.5 | 489 | 464.8 | 168.1 | 171.2 | 170.7 | 193 | NaN | 154
2974.1 | 2876.1 | 431.9 | 465.3 | 488.7 | 464.6 | 444.6 | 445.6 | 443 | 447.2 | 355.2 | 392.4
2975.1 | 2877.1 | 431.3 | 465.1 | 488.4 | 464.4 | 483.2 | 482.7 | 480.1 | 481.9 | 446.7 | 424
2976.1 | 2878.1 | 430.6 | 464.9 | 488.1 | 464.2 | 131.5 | 135 | 134.6 | 159.8 | NaN | 123.3
2977.1 | 2879.1 | 430 | 464.7 | 487.8 | 464 | 488 | 488 | 485.4 | 486.7 | 455.7 | 429
2978.1 | 2880.1 | 429.4 | 464.5 | 487.6 | 463.7 | 414.1 | 413.9 | 411.2 | 417.8 | 310.3 | 363.6
2979.1 | 2881.1 | 428.8 | 464.2 | 487.3 | 463.5 | 201.5 | 205 | 203.9 | 224.7 | NaN | 183.6
2980.1 | 2882.1 | 428.2 | 464 | 487.1 | 463.3 | 490.3 | 490.1 | 487.5 | 488.8 | 462 | 430.9
2981.1 | 2883.1 | 427.6 | 463.8 | 486.8 | 463.1 | 490.4 | 490 | 487.6 | 488.9 | 462.4 | 431
2982.1 | 2884.1 | 427 | 463.6 | 486.6 | 462.9 | 490.3 | 489.8 | 487.5 | 488.8 | 462.3 | 430.9
2983.1 | 2885.1 | 426.4 | 463.4 | 486.3 | 462.6 | 490.1 | 489.6 | 487.4 | 488.7 | 462.2 | 430.9
2984.1 | 2886.1 | 425.8 | 463.4 | 485.6 | 462.6 | 491.8 | 490.2 | 487.2 | 488.5 | 461.5 | 432
2985.1 | 2887.1 | 425.2 | 463 | 485.7 | 462.2 | 489.9 | 489.3 | 487.2 | 488.5 | 461.9 | 430.8
2986.1 | 2888.1 | 424.7 | 462.8 | 485.4 | 462 | 489.7 | 489 | 487 | 488.5 | 461.8 | 430.7
2987.1 | 2889.1 | 424.1 | 462.7 | 484.8 | 461.9 | 490.4 | 489.3 | 486.9 | 488.3 | 461.4 | 431.3
2988.1 | 2890.1 | 423.5 | 462.3 | 484.9 | 461.6 | 333.7 | 334.4 | 332.3 | 343.9 | 103.5 | 295
2989.1 | 2891.1 | 422.9 | 462.1 | 484.6 | 461.3 | 278.1 | 281 | 279.3 | 294.1 | -29.3 | 249.7
2990.1 | 2892.1 | 422.4 | 461.9 | 484.3 | 461.1 | 489.2 | 488.7 | 486.5 | 488 | 461.1 | 430.5
2991.1 | 2893.1 | 421.8 | 461.7 | 484.1 | 460.9 | 254.3 | 255.5 | 254.7 | 271.2 | -48.2 | 227.3
2992.1 | 2894.1 | 421.2 | 461.5 | 483.8 | 460.7 | 358.8 | 360.4 | 358.6 | 368.6 | 184.4 | 319.3
2993.1 | 2895.1 | 420.6 | 461.2 | 483.6 | 460.5 | 488.6 | 488.2 | 486.1 | 487.8 | 460.8 | 430.2
2994.1 | 2896.1 | 420 | 461 | 483.2 | 460.2 | 488.5 | 488 | 486.1 | 487.7 | 460.8 | 430.2
2995.1 | 2897.1 | 419.5 | 460.8 | 483 | 460 | 488.4 | 487.8 | 485.9 | 487.6 | 460.6 | 430.1
2996.1 | 2898.1 | 418.9 | 460.6 | 482.7 | 459.8 | 488.2 | 487.6 | 485.8 | 487.4 | 460.5 | 430
2997.1 | 2899.1 | 418.3 | 460.4 | 482.4 | 459.6 | 488 | 487.5 | 485.7 | 487.2 | 460.3 | 430
2998.1 | 2900.1 | 417.8 | 460.2 | 482.2 | 459.4 | 487.9 | 487.3 | 485.5 | 487.1 | 460.2 | 429.9
2999.1 | 2901.1 | 417.2 | 460 | 481.9 | 459.1 | 415.2 | 415.3 | 413.8 | 419.8 | 300.1 | 367
3000.1 | 2902.1 | 416.7 | 459.7 | 481.7 | 458.9 | 196.6 | 201 | 199.5 | 220.1 | NaN | 180.4
3001.1 | 2903.1 | 416.1 | 459.5 | 481.3 | 458.7 | 487.5 | 487 | 484.9 | 486.5 | 458.9 | 429.7
3002.1 | 2904.1 | 415.5 | 459.3 | 481.1 | 458.4 | 487.2 | 486.8 | 485 | 486.6 | 459.6 | 429.6
3003.1 | 2905.1 | 415 | 459.1 | 480.8 | 458.2 | 487 | 486.5 | 484.9 | 486.6 | 459.5 | 429.5
3004.1 | 2906.1 | 414.4 | 458.8 | 480.6 | 458 | 486.9 | 486.3 | 484.7 | 486.6 | 459.3 | 429.5
3005.1 | 2907.1 | 413.9 | 458.6 | 480.3 | 457.8 | 486.7 | 486.2 | 484.6 | 486.4 | 459.2 | 429.4
3006.1 | 2908.1 | 413.3 | 458.4 | 480 | 457.5 | 486.5 | 486 | 484.5 | 486.4 | 459 | 429.3
3007.1 | 2909.1 | 412.8 | 458.2 | 479.7 | 457.3 | 486.3 | 485.8 | 484.3 | 486.3 | 458.9 | 429.3
3008.1 | 2910.1 | 412.3 | 458 | 479.5 | 457.1 | 486.2 | 485.6 | 484.2 | 486.2 | 458.8 | 429.2
3009.1 | 2911.1 | 411.7 | 457.7 | 479.2 | 456.8 | 344.8 | 345.8 | 344.9 | 359.4 | 321.9 | 307.8
3010.1 | 2912.1 | 411.1 | 457.5 | 478.9 | 456.6 | 284.5 | 287.6 | 286.7 | 307 | 262.1 | 257.7
3011.1 | 2913.1 | 410.6 | 457.3 | 478.6 | 456.4 | 156.1 | 161 | 160.8 | 194.6 | 138.9 | 148.1
3012.1 | 2914.1 | 410.1 | 457.1 | 478.3 | 456.2 | 250.3 | 251.9 | 251.1 | 268.1 | -90.7 | 224.9
3013.1 | 2915.1 | 409.5 | 456.8 | 478 | 456 | 354.8 | 356.4 | 355.2 | 365.5 | 174.2 | 317.1
3014.1 | 2916.1 | 409 | 456.6 | 477.8 | 455.7 | 485.1 | 484.8 | 483.3 | 485.2 | 457.8 | 428.6
3015.1 | 2917.1 | 408.5 | 456.4 | 477.5 | 455.5 | 168.7 | 171.3 | 170.8 | 193.2 | NaN | 154.7
3016.1 | 2918.1 | 407.9 | 456.2 | 477.2 | 455.2 | 432.9 | 433.9 | 432.3 | 437.7 | 340.7 | 384.6
3017.1 | 2919.1 | 407.4 | 455.9 | 476.9 | 455 | 478.7 | 478.4 | 476.9 | 479.4 | 442.4 | 423.2
3018.1 | 2920.1 | 406.9 | 455.7 | 476.6 | 454.8 | 129.2 | 132.2 | 131.7 | 156.6 | NaN | 121.6
3019.1 | 2921.1 | 406.3 | 455.5 | 476.4 | 454.6 | 481.2 | 481.3 | 479.7 | 482.1 | 449.8 | 425.8
3020.1 | 2922.1 | 405.8 | 455.2 | 476.1 | 454.3 | 408.1 | 408 | 406.8 | 413.6 | 291.6 | 361.7
3021.1 | 2923.1 | 405.3 | 455 | 475.8 | 454.1 | 196.2 | 199.4 | 198.3 | 219.2 | NaN | 179.8
3022.1 | 2924.1 | 404.8 | 454.8 | 475.5 | 453.8 | 483.6 | 483.5 | 481.9 | 484 | 456.1 | 427.8
3023.1 | 2925.1 | 404.3 | 454.6 | 475.3 | 453.6 | 483.6 | 483.4 | 482 | 484.1 | 456.6 | 427.9
3024.1 | 2926.1 | 403.7 | 454.3 | 475 | 453.4 | 483.5 | 483.1 | 481.8 | 484.1 | 456.4 | 427.9
3025.1 | 2927.1 | 403.2 | 454.1 | 474.7 | 453.1 | 483.3 | 482.9 | 481.7 | 484 | 456.3 | 427.8
3026.1 | 2928.1 | 402.7 | 453.9 | 474.4 | 452.9 | 483.1 | 482.7 | 481.5 | 483.9 | 456.1 | 427.7
3027.1 | 2929.1 | 402.2 | 453.6 | 474.1 | 452.7 | 483 | 482.5 | 481.4 | 483.8 | 456 | 427.6
3028.1 | 2930.1 | 401.7 | 453.4 | 473.9 | 452.4 | 482.8 | 482.3 | 481.2 | 483.6 | 455.8 | 427.5
3029.1 | 2931.1 | 401.2 | 453.2 | 473.6 | 452.2 | 482.6 | 482.1 | 481.1 | 483.5 | 455.7 | 427.4
3030.1 | 2932.1 | 400.6 | 453 | 473.3 | 452 | 482.4 | 481.9 | 480.9 | 483.4 | 455.5 | 427.3
3031.1 | 2933.1 | 400.1 | 452.7 | 473 | 451.7 | 482.2 | 481.7 | 480.8 | 483.3 | 455.3 | 427.3

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 61 |  |  | 2006-09-01 | 12:30
38961.5203 | 1 | 0 | 1 | TS/TP | 7-C | Conduit
38961.5208 | 1 | 0 | 1 | 525 C | 23 kW/m2 |  | Bundle
38961.5212 | 1 | 0 | 1
38961.5217 | 1 | 0 | 1
38961.5222 | 1 | 0 | 1
38961.5227 | 1 | 0 | 1
38961.5232 | 1 | 0 | 1
38961.5237 | 1 | 0 | 1
38961.5242 | 1 | 0 | 1
38961.5246 | 1 | 0 | 1
38961.5251 | 1 | 0 | 1
38961.5256 | 1 | 0 | 1
38961.5261 | 1 | 0 | 1
38961.5266 | 1 | 0 | 1
38961.5271 | 1 | 0 | 1
38961.5276 | 1 | 0 | 1
38961.528 | 1 | 0 | 1
38961.5285 | 1 | 0 | 1
38961.529 | 1 | 0 | 1
38961.5295 | 1 | 0 | 1
38961.53 | 1 | 0 | 1
38961.5305 | 1 | 0 | 1
38961.531 | 1 | 0 | 1
38961.5314 | 1 | 0 | 1
38961.5319 | 1 | 0 | 1
38961.5324 | 1 | 0 | 1
38961.5329 | 1 | 0 | 1
38961.5334 | 1 | 0 | 1
38961.5339 | 1 | 0 | 1
38961.5344 | 1 | 0 | 1
38961.5348 | 1 | 0 | 1
38961.5353 | 1 | 0 | 1
38961.5358 | 1 | 0 | 1
38961.5363 | 1 | 0 | 1
38961.5368 | 1 | 0 | 1
38961.5373 | 1 | 0 | 1
38961.5378 | 1 | 0 | 1
38961.5383 | 1 | 0 | 1
38961.5387 | 1 | 0 | 1
38961.5392 | 937 | 974 | 1
38961.5397 | 930 | 1030 | 1
38961.5402 | 1027 | 1071 | 1
38961.5407 | 1037 | 1128 | 1
38961.5412 | 1135 | 1107 | 1
38961.5417 | 937 | 916 | 1
38961.5421 | 1022 | 993 | 1
38961.5426 | 957 | 950 | 1
38961.5431 | 610 | 590 | 1
38961.5436 | 568 | 580 | 1
38961.5441 | 603 | 0 | 1
38961.5446 | 1007 | 974 | 1
38961.5451 | 1051 | 1017 | 1
38961.5455 | 1421 | 0 | 1
38961.546 | 1953 | 3 | 1
38961.5465 | 2320 | 4 | 1
38961.547 | 2392 | 2 | 1
38961.5475 | 2424 | 3 | 1
38961.548 | 2208 | 2 | 1
38961.5485 | 2326 | 2 | 1
38961.5489 | 2001 | 2 | 1
38961.5494 | 2248 | 2 | 1
38961.5499 | 2448 | 3 | 1
38961.5504 | 2275 | 3 | 1
38961.5509 | 1873 | 3 | 1
38961.5514 | 1443 | 0 | 1
38961.5519 | 1274 | 0 | 1
38961.5523 | 2359 | 1 | 1
38961.5528 | 2303 | 1 | 1
38961.5533 | 2089 | 1 | 1
38961.5538 | 2033 | 1 | 1
38961.5543 | 1389 | 0 | 1
38961.5548 | 124 | 0 | 1
38961.5592 | 1851 | 1 | 1
38961.5597 | 5 | 0 | 1
38961.5601 | 245 | 0 | 1
38961.5606 | 2 | 0 | 1
38961.5611 | 264 | 0 | 1
38961.5616 | 1154 | 0 | 1
38961.5621 | 56 | 0 | 1
38961.5626 | 524 | 0 | 1
1
38961.5203 | 1 | 0 | 2
38961.5208 | 1 | 0 | 2
38961.5213 | 1 | 0 | 2
38961.5217 | 1 | 0 | 2
38961.5222 | 1 | 0 | 2
38961.5227 | 1 | 0 | 2
38961.5232 | 1 | 0 | 2
38961.5237 | 1 | 0 | 2
38961.5242 | 1 | 0 | 2
38961.5247 | 1 | 0 | 2
38961.5252 | 1 | 0 | 2
38961.5256 | 1 | 0 | 2
38961.5261 | 1 | 0 | 2
38961.5266 | 1 | 0 | 2
38961.5271 | 1 | 0 | 2
38961.5276 | 1 | 0 | 2
38961.5281 | 2 | 0 | 2
38961.5286 | 1 | 0 | 2
38961.529 | 1 | 0 | 2
38961.5295 | 1 | 0 | 2
38961.53 | 1 | 0 | 2
38961.5305 | 1 | 0 | 2
38961.531 | 1 | 0 | 2
38961.5315 | 1 | 0 | 2
38961.532 | 1 | 0 | 2
38961.5324 | 1 | 0 | 2
38961.5329 | 1 | 0 | 2
38961.5334 | 1 | 0 | 2
38961.5339 | 1 | 0 | 2
38961.5344 | 1 | 0 | 2
38961.5349 | 1 | 0 | 2
38961.5354 | 1 | 0 | 2
38961.5358 | 1 | 0 | 2
38961.5363 | 1 | 0 | 2
38961.5368 | 1 | 0 | 2
38961.5373 | 1 | 0 | 2
38961.5378 | 1 | 0 | 2
38961.5383 | 1 | 0 | 2
38961.5388 | 1 | 0 | 2
38961.5392 | 1193 | 927 | 2
38961.5397 | 1068 | 1148 | 2
38961.5402 | 1125 | 1099 | 2
38961.5407 | 1195 | 1174 | 2
38961.5412 | 1088 | 1159 | 2
38961.5417 | 1191 | 1168 | 2
38961.5422 | 961 | 934 | 2
38961.5427 | 1075 | 1046 | 2
38961.5431 | 1186 | 1170 | 2
38961.5436 | 925 | 1024 | 2
38961.5441 | 2413 | 1 | 2
38961.5446 | 1058 | 1024 | 2
38961.5451 | 1058 | 1024 | 2
38961.5456 | 2110 | 1 | 2
38961.5461 | 2203 | 3 | 2
38961.5465 | 1988 | 2 | 2
38961.547 | 1898 | 2 | 2
38961.5475 | 2250 | 2 | 2
38961.548 | 2031 | 2 | 2
38961.5485 | 2179 | 3 | 2
38961.549 | 2084 | 0 | 2
38961.5494 | 2377 | 2 | 2
38961.5499 | 2077 | 2 | 2
38961.5504 | 2014 | 2 | 2
38961.5509 | 2237 | 2 | 2
38961.5514 | 2203 | 0 | 2
38961.5519 | 2317 | 0 | 2
38961.5524 | 1952 | 1 | 2
38961.5528 | 2368 | 1 | 2
38961.5533 | 2372 | 1 | 2
38961.5538 | 1956 | 1 | 2
38961.5543 | 2126 | 0 | 2
38961.5548 | 2303 | 0 | 2
38961.5592 | 2442 | 0 | 2
38961.5597 | 2240 | 0 | 2
38961.5602 | 2010 | 0 | 2
38961.5606 | 2083 | 0 | 2
38961.5611 | 2021 | 0 | 2
38961.5616 | 2178 | 0 | 2
38961.5621 | 2194 | 0 | 2
38961.5626 | 2189 | 0 | 2
2
38961.5203 | 1 | 0 | 3
38961.5208 | 1 | 0 | 3
38961.5213 | 1 | 0 | 3
38961.5218 | 1 | 0 | 3
38961.5222 | 1 | 0 | 3
38961.5227 | 1 | 0 | 3
38961.5232 | 1 | 0 | 3
38961.5237 | 1 | 0 | 3
38961.5242 | 1 | 0 | 3
38961.5247 | 1 | 0 | 3
38961.5252 | 1 | 0 | 3
38961.5256 | 1 | 0 | 3
38961.5261 | 1 | 0 | 3
38961.5266 | 1 | 0 | 3
38961.5271 | 1 | 0 | 3
38961.5276 | 1 | 0 | 3
38961.5281 | 1 | 0 | 3
38961.5286 | 1 | 0 | 3
38961.5291 | 1 | 0 | 3
38961.5295 | 1 | 0 | 3
38961.53 | 1 | 0 | 3
38961.5305 | 1 | 0 | 3
38961.531 | 1 | 0 | 3
38961.5315 | 1 | 0 | 3
38961.532 | 1 | 0 | 3
38961.5325 | 1 | 0 | 3
38961.5329 | 1 | 0 | 3
38961.5334 | 1 | 0 | 3
38961.5339 | 1 | 0 | 3
38961.5344 | 1 | 0 | 3
38961.5349 | 1 | 0 | 3
38961.5354 | 1 | 0 | 3
38961.5359 | 1 | 0 | 3
38961.5363 | 1 | 0 | 3
38961.5368 | 1 | 0 | 3
38961.5373 | 1 | 0 | 3
38961.5378 | 1 | 0 | 3
38961.5383 | 1 | 0 | 3
38961.5388 | 1 | 0 | 3
38961.5393 | 2 | 2 | 3
38961.5397 | 2 | 2 | 3
38961.5402 | 1 | 2 | 3
38961.5407 | 2 | 2 | 3
38961.5412 | 1 | 1 | 3
38961.5417 | 2 | 2 | 3
38961.5422 | 2 | 1 | 3
38961.5427 | 2 | 2 | 3
38961.5431 | 2 | 2 | 3
38961.5436 | 21 | 1 | 3
38961.5441 | 1152 | 0 | 3
38961.5446 | 3 | 1 | 3
38961.5451 | 2 | 2 | 3
38961.5456 | 1211 | 0 | 3
38961.5461 | 2345 | 0 | 3
38961.5466 | 2393 | 0 | 3
38961.547 | 1895 | 0 | 3
38961.5475 | 1980 | 0 | 3
38961.548 | 2039 | 0 | 3
38961.5485 | 2021 | 0 | 3
38961.549 | 2105 | 0 | 3
38961.5495 | 2259 | 0 | 3
38961.55 | 2044 | 0 | 3
38961.5504 | 2332 | 0 | 3
38961.5509 | 2054 | 0 | 3
38961.5514 | 1587 | 0 | 3
38961.5519 | 1476 | 0 | 3
38961.5524 | 2343 | 0 | 3
38961.5529 | 2209 | 0 | 3
38961.5534 | 2085 | 0 | 3
38961.5538 | 2159 | 0 | 3
38961.5543 | 775 | 0 | 3
38961.5548 | 694 | 0 | 3
38961.5592 | 1241 | 0 | 3
38961.5597 | 5 | 0 | 3
38961.5602 | 3 | 0 | 3
38961.5607 | 2 | 0 | 3
38961.5611 | 1157 | 0 | 3
38961.5616 | 187 | 0 | 3
38961.5621 | 2 | 0 | 3
38961.5626 | 2 | 0 | 3
3
38961.5203 | 1 | 0 | 4
38961.5208 | 1 | 0 | 4
38961.5213 | 1 | 0 | 4
38961.5218 | 1 | 0 | 4
38961.5223 | 1 | 0 | 4
38961.5228 | 1 | 0 | 4
38961.5232 | 1 | 0 | 4
38961.5237 | 1 | 0 | 4
38961.5242 | 1 | 0 | 4
38961.5247 | 1 | 0 | 4
38961.5252 | 1 | 0 | 4
38961.5257 | 1 | 0 | 4
38961.5262 | 1 | 0 | 4
38961.5266 | 1 | 0 | 4
38961.5271 | 1 | 0 | 4
38961.5276 | 1 | 0 | 4
38961.5281 | 1 | 0 | 4
38961.5286 | 1 | 0 | 4
38961.5291 | 1 | 0 | 4
38961.5296 | 1 | 0 | 4
38961.53 | 1 | 0 | 4
38961.5305 | 1 | 0 | 4
38961.531 | 1 | 0 | 4
38961.5315 | 1 | 0 | 4
38961.532 | 1 | 0 | 4
38961.5325 | 1 | 0 | 4
38961.533 | 1 | 0 | 4
38961.5334 | 1 | 0 | 4
38961.5339 | 1 | 0 | 4
38961.5344 | 1 | 0 | 4
38961.5349 | 1 | 0 | 4
38961.5354 | 1 | 0 | 4
38961.5359 | 1 | 0 | 4
38961.5364 | 1 | 0 | 4
38961.5368 | 1 | 0 | 4
38961.5373 | 1 | 0 | 4
38961.5378 | 1 | 0 | 4
38961.5383 | 1 | 0 | 4
38961.5388 | 1 | 0 | 4
38961.5393 | 1 | 1 | 4
38961.5398 | 1 | 1 | 4
38961.5402 | 1 | 1 | 4
38961.5407 | 1 | 1 | 4
38961.5412 | 1 | 1 | 4
38961.5417 | 2 | 1 | 4
38961.5422 | 2 | 1 | 4
38961.5427 | 2 | 0 | 4
38961.5432 | 2 | 0 | 4
38961.5436 | 2 | 1 | 4
38961.5441 | 3 | 0 | 4
38961.5446 | 2 | 1 | 4
38961.5451 | 47 | 1 | 4
38961.5456 | 2 | 0 | 4
38961.5461 | 70 | 0 | 4
38961.5466 | 2 | 0 | 4
38961.547 | 3 | 0 | 4
38961.5475 | 2 | 0 | 4
38961.548 | 2 | 0 | 4
38961.5485 | 2 | 1 | 4
38961.549 | 2045 | 0 | 4
38961.5495 | 1986 | 0 | 4
38961.55 | 1975 | 0 | 4
38961.5505 | 1418 | 0 | 4
38961.5509 | 19 | 0 | 4
38961.5514 | 54 | 0 | 4
38961.5519 | 116 | 0 | 4
38961.5524 | 1067 | 0 | 4
38961.5529 | 192 | 0 | 4
38961.5534 | 624 | 0 | 4
38961.5539 | 554 | 0 | 4
38961.5543 | 667 | 0 | 4
38961.5548 | 710 | 0 | 4
38961.5592 | 153 | 0 | 4
38961.5597 | 142 | 0 | 4
38961.5602 | 25 | 0 | 4
38961.5607 | 8 | 0 | 4
38961.5612 | 6 | 0 | 4
38961.5616 | 3 | 0 | 4
38961.5621 | 2 | 0 | 4
38961.5626 | 2 | 0 | 4
4
38961.5203 | 1 | 0 | 5
38961.5208 | 1 | 0 | 5
38961.5213 | 1 | 0 | 5
38961.5218 | 1 | 0 | 5
38961.5223 | 1 | 0 | 5
38961.5228 | 1 | 0 | 5
38961.5233 | 1 | 0 | 5
38961.5237 | 1 | 0 | 5
38961.5242 | 1 | 0 | 5
38961.5247 | 1 | 0 | 5
38961.5252 | 1 | 0 | 5
38961.5257 | 1 | 0 | 5
38961.5262 | 1 | 0 | 5
38961.5267 | 1 | 0 | 5
38961.5271 | 1 | 0 | 5
38961.5276 | 1 | 0 | 5
38961.5281 | 1 | 0 | 5
38961.5286 | 1 | 0 | 5
38961.5291 | 1 | 0 | 5
38961.5296 | 1 | 0 | 5
38961.5301 | 1 | 0 | 5
38961.5305 | 1 | 0 | 5
38961.531 | 1 | 0 | 5
38961.5315 | 1 | 0 | 5
38961.532 | 1 | 0 | 5
38961.5325 | 1 | 0 | 5
38961.533 | 1 | 0 | 5
38961.5335 | 1 | 0 | 5
38961.5339 | 1 | 0 | 5
38961.5344 | 1 | 0 | 5
38961.5349 | 1 | 0 | 5
38961.5354 | 1 | 0 | 5
38961.5359 | 1 | 0 | 5
38961.5364 | 1 | 0 | 5
38961.5369 | 1 | 0 | 5
38961.5373 | 1 | 0 | 5
38961.5378 | 1 | 0 | 5
38961.5383 | 1 | 0 | 5
38961.5388 | 1 | 0 | 5
38961.5393 | 1 | 0 | 5
38961.5398 | 1 | 0 | 5
38961.5403 | 1 | 0 | 5
38961.5408 | 1 | 0 | 5
38961.5412 | 2 | 0 | 5
38961.5417 | 2 | 0 | 5
38961.5422 | 2 | 0 | 5
38961.5427 | 2 | 0 | 5
38961.5432 | 2 | 0 | 5
38961.5437 | 2050 | 0 | 5
38961.5442 | 1897 | 0 | 5
38961.5446 | 2 | 0 | 5
38961.5451 | 2 | 0 | 5
38961.5456 | 2310 | 0 | 5
38961.5461 | 1898 | 0 | 5
38961.5466 | 2409 | 0 | 5
38961.5471 | 2178 | 0 | 5
38961.5476 | 2377 | 0 | 5
38961.548 | 1982 | 0 | 5
38961.5485 | 2445 | 1 | 5
38961.549 | 1823 | 0 | 5
38961.5495 | 1917 | 0 | 5
38961.55 | 2022 | 0 | 5
38961.5505 | 2126 | 0 | 5
38961.5514 | 1353 | 0 | 5
38961.5519 | 2159 | 0 | 5
38961.5524 | 2151 | 0 | 5
38961.5529 | 2422 | 0 | 5
38961.5534 | 2114 | 0 | 5
38961.5539 | 2169 | 0 | 5
38961.5544 | 95 | 0 | 5
38961.5548 | 820 | 0 | 5
38961.5592 | 10 | 0 | 5
38961.5597 | 3 | 0 | 5
38961.5602 | 3 | 0 | 5
38961.5607 | 1 | 0 | 5
38961.5612 | 624 | 0 | 5
38961.5617 | 152 | 0 | 5
38961.5621 | 141 | 0 | 5
38961.5626 | 24 | 0 | 5
5
38961.5203 | 1 | 0 | 6
38961.5208 | 1 | 0 | 6
38961.5213 | 1 | 0 | 6
38961.5218 | 1 | 0 | 6
38961.5223 | 1 | 0 | 6
38961.5228 | 1 | 0 | 6
38961.5233 | 1 | 0 | 6
38961.5238 | 1 | 0 | 6
38961.5242 | 1 | 0 | 6
38961.5247 | 1 | 0 | 6
38961.5252 | 1 | 0 | 6
38961.5257 | 1 | 0 | 6
38961.5262 | 1 | 0 | 6
38961.5267 | 1 | 0 | 6
38961.5272 | 1 | 0 | 6
38961.5276 | 1 | 0 | 6
38961.5281 | 1 | 0 | 6
38961.5286 | 1 | 0 | 6
38961.5291 | 1 | 0 | 6
38961.5296 | 1 | 0 | 6
38961.5301 | 1 | 0 | 6
38961.5306 | 1 | 0 | 6
38961.531 | 1 | 0 | 6
38961.5315 | 1 | 0 | 6
38961.532 | 1 | 0 | 6
38961.5325 | 1 | 0 | 6
38961.533 | 1 | 0 | 6
38961.5335 | 1 | 0 | 6
38961.534 | 1 | 0 | 6
38961.5344 | 1 | 0 | 6
38961.5349 | 1 | 0 | 6
38961.5354 | 1 | 0 | 6
38961.5359 | 1 | 0 | 6
38961.5364 | 1 | 0 | 6
38961.5369 | 1 | 0 | 6
38961.5374 | 1 | 0 | 6
38961.5378 | 1 | 0 | 6
38961.5383 | 1 | 0 | 6
38961.5388 | 1 | 0 | 6
38961.5393 | 1 | 0 | 6
38961.5398 | 1 | 0 | 6
38961.5403 | 1 | 0 | 6
38961.5408 | 1 | 0 | 6
38961.5413 | 1 | 0 | 6
38961.5417 | 1 | 0 | 6
38961.5422 | 1 | 0 | 6
38961.5427 | 2 | 0 | 6
38961.5432 | 2 | 0 | 6
38961.5437 | 2 | 0 | 6
38961.5442 | 153 | 0 | 6
38961.5447 | 5 | 0 | 6
38961.5451 | 32 | 0 | 6
38961.5456 | 2 | 0 | 6
38961.5461 | 91 | 0 | 6
38961.5466 | 2 | 0 | 6
38961.5471 | 2 | 0 | 6
38961.5476 | 2 | 0 | 6
38961.5481 | 2 | 0 | 6
38961.5485 | 3 | 0 | 6
38961.549 | 2049 | 0 | 6
38961.5495 | 1955 | 0 | 6
38961.55 | 1982 | 0 | 6
38961.5505 | 1838 | 0 | 6
38961.551 | 22 | 0 | 6
38961.5515 | 49 | 0 | 6
38961.5519 | 206 | 0 | 6
38961.5524 | 187 | 0 | 6
38961.5529 | 207 | 0 | 6
38961.5534 | 562 | 0 | 6
38961.5539 | 679 | 0 | 6
38961.5544 | 612 | 0 | 6
38961.5549 | 735 | 0 | 6
38961.5592 | 169 | 0 | 6
38961.5597 | 177 | 0 | 6
38961.5602 | 53 | 0 | 6
38961.5607 | 26 | 0 | 6
38961.5612 | 22 | 0 | 6
38961.5617 | 15 | 0 | 6
38961.5622 | 11 | 0 | 6
38961.5627 | 4 | 0 | 6
6
38961.5204 | 1 | 0 | 7
38961.5209 | 1 | 0 | 7
38961.5213 | 4 | 0 | 7
38961.5218 | 1 | 0 | 7
38961.5223 | 2 | 0 | 7
38961.5228 | 1 | 0 | 7
38961.5233 | 1 | 0 | 7
38961.5238 | 1 | 0 | 7
38961.5243 | 1 | 0 | 7
38961.5247 | 1 | 0 | 7
38961.5252 | 1 | 0 | 7
38961.5257 | 1 | 0 | 7
38961.5262 | 1 | 0 | 7
38961.5267 | 1 | 0 | 7
38961.5272 | 1 | 0 | 7
38961.5277 | 1 | 0 | 7
38961.5281 | 1 | 0 | 7
38961.5286 | 1 | 0 | 7
38961.5291 | 1 | 0 | 7
38961.5296 | 1 | 0 | 7
38961.5301 | 1 | 0 | 7
38961.5306 | 1 | 0 | 7
38961.5311 | 1 | 0 | 7
38961.5316 | 1 | 0 | 7
38961.532 | 1 | 0 | 7
38961.5325 | 1 | 0 | 7
38961.533 | 1 | 0 | 7
38961.5335 | 1 | 0 | 7
38961.534 | 1 | 0 | 7
38961.5345 | 1 | 0 | 7
38961.535 | 1 | 0 | 7
38961.5354 | 1 | 0 | 7
38961.5359 | 1 | 0 | 7
38961.5364 | 1 | 0 | 7
38961.5369 | 1 | 0 | 7
38961.5374 | 1 | 0 | 7
38961.5379 | 1 | 0 | 7
38961.5384 | 1 | 0 | 7
38961.5388 | 1 | 0 | 7
38961.5393 | 1 | 0 | 7
38961.5398 | 1 | 0 | 7
38961.5403 | 1 | 0 | 7
38961.5408 | 1 | 0 | 7
38961.5413 | 1 | 0 | 7
38961.5418 | 1 | 0 | 7
38961.5422 | 2 | 0 | 7
38961.5427 | 2 | 0 | 7
38961.5432 | 47 | 0 | 7
38961.5437 | 2345 | 26 | 7
38961.5442 | 2262 | 14 | 7
38961.5447 | 2 | 0 | 7
38961.5452 | 2 | 0 | 7
38961.5456 | 2379 | 5 | 7
38961.5461 | 2216 | 4 | 7
38961.5466 | 2172 | 3 | 7
38961.5471 | 1928 | 2 | 7
38961.5476 | 2146 | 3 | 7
38961.5481 | 1930 | 2 | 7
38961.5486 | 2024 | 2 | 7
38961.5491 | 1896 | 1 | 7
38961.5495 | 2317 | 2 | 7
38961.55 | 2059 | 3 | 7
38961.5505 | 2038 | 2 | 7
38961.551 | 1597 | 1 | 7
38961.5515 | 463 | 0 | 7
38961.552 | 2425 | 2 | 7
38961.5524 | 1971 | 2 | 7
38961.5529 | 2325 | 2 | 7
38961.5534 | 2146 | 1 | 7
38961.5539 | 1977 | 1 | 7
38961.5544 | 80 | 0 | 7
38961.5549 | 69 | 0 | 7
38961.5593 | 14 | 0 | 7
38961.5597 | 3 | 0 | 7
38961.5602 | 3 | 0 | 7
38961.5607 | 2 | 0 | 7
38961.5612 | 215 | 0 | 7
38961.5617 | 2 | 0 | 7
38961.5622 | 4 | 0 | 7
38961.5627 | 2 | 0 | 7
7
38961.5204 | 1 | 0 | 8
38961.5209 | 1 | 0 | 8
38961.5214 | 1 | 0 | 8
38961.5218 | 1 | 0 | 8
38961.5223 | 1 | 0 | 8
38961.5228 | 1 | 0 | 8
38961.5233 | 1 | 0 | 8
38961.5238 | 1 | 0 | 8
38961.5243 | 1 | 0 | 8
38961.5248 | 1 | 0 | 8
38961.5252 | 1 | 0 | 8
38961.5257 | 1 | 0 | 8
38961.5262 | 1 | 0 | 8
38961.5267 | 1 | 0 | 8
38961.5272 | 1 | 0 | 8
38961.5277 | 1 | 0 | 8
38961.5282 | 1 | 0 | 8
38961.5286 | 1 | 0 | 8
38961.5291 | 1 | 0 | 8
38961.5296 | 1 | 0 | 8
38961.5301 | 1 | 0 | 8
38961.5306 | 1 | 0 | 8
38961.5311 | 1 | 0 | 8
38961.5316 | 1 | 0 | 8
38961.532 | 1 | 0 | 8
38961.5325 | 1 | 0 | 8
38961.533 | 1 | 0 | 8
38961.5335 | 1 | 0 | 8
38961.534 | 1 | 0 | 8
38961.5345 | 1 | 0 | 8
38961.535 | 1 | 0 | 8
38961.5355 | 1 | 0 | 8
38961.5359 | 1 | 0 | 8
38961.5364 | 1 | 0 | 8
38961.5369 | 1 | 0 | 8
38961.5374 | 1 | 0 | 8
38961.5379 | 1 | 0 | 8
38961.5384 | 1 | 0 | 8
38961.5389 | 1 | 0 | 8
38961.5393 | 1 | 0 | 8
38961.5398 | 1 | 0 | 8
38961.5403 | 1 | 0 | 8
38961.5408 | 1 | 0 | 8
38961.5413 | 231 | 0 | 8
38961.5418 | 1784 | 0 | 8
38961.5423 | 2095 | 0 | 8
38961.5427 | 2170 | 0 | 8
38961.5432 | 1962 | 0 | 8
38961.5437 | 1956 | 15 | 8
38961.5442 | 2118 | 9 | 8
38961.5447 | 2323 | 0 | 8
38961.5452 | 2395 | 0 | 8
38961.5457 | 2082 | 4 | 8
38961.5461 | 2046 | 2 | 8
38961.5466 | 1953 | 2 | 8
38961.5471 | 1924 | 2 | 8
38961.5476 | 2450 | 3 | 8
38961.5481 | 1948 | 2 | 8
38961.5486 | 2035 | 1 | 8
38961.5491 | 2449 | 0 | 8
38961.5495 | 2461 | 1 | 8
38961.55 | 2201 | 2 | 8
38961.5505 | 2469 | 2 | 8
38961.551 | 2206 | 0 | 8
38961.5515 | 2063 | 0 | 8
38961.552 | 2360 | 1 | 8
38961.5525 | 2268 | 1 | 8
38961.553 | 2328 | 1 | 8
38961.5534 | 2094 | 1 | 8
38961.5539 | 2174 | 1 | 8
38961.5544 | 2466 | 0 | 8
38961.5549 | 2416 | 0 | 8
38961.5593 | 2047 | 0 | 8
38961.5598 | 1997 | 0 | 8
38961.5603 | 2021 | 0 | 8
38961.5607 | 1901 | 0 | 8
38961.5612 | 1947 | 0 | 8
38961.5617 | 2212 | 0 | 8
38961.5622 | 2431 | 0 | 8
38961.5627 | 2307 | 0 | 8
8
38961.5204 | 1 | 0 | 9
38961.5209 | 1 | 0 | 9
38961.5214 | 1 | 0 | 9
38961.5219 | 1 | 0 | 9
38961.5223 | 1 | 0 | 9
38961.5228 | 1 | 0 | 9
38961.5233 | 1 | 0 | 9
38961.5238 | 1 | 0 | 9
38961.5243 | 1 | 0 | 9
38961.5248 | 1 | 0 | 9
38961.5253 | 1 | 0 | 9
38961.5258 | 1 | 0 | 9
38961.5262 | 1 | 0 | 9
38961.5267 | 1 | 0 | 9
38961.5272 | 1 | 0 | 9
38961.5277 | 1 | 0 | 9
38961.5282 | 1 | 0 | 9
38961.5287 | 1 | 0 | 9
38961.5292 | 1 | 0 | 9
38961.5296 | 1 | 0 | 9
38961.5301 | 1 | 0 | 9
38961.5306 | 1 | 0 | 9
38961.5311 | 1 | 0 | 9
38961.5316 | 1 | 0 | 9
38961.5321 | 1 | 0 | 9
38961.5326 | 1 | 0 | 9
38961.533 | 1 | 0 | 9
38961.5335 | 1 | 0 | 9
38961.534 | 1 | 0 | 9
38961.5345 | 1 | 0 | 9
38961.535 | 1 | 0 | 9
38961.5355 | 1 | 0 | 9
38961.5359 | 1 | 0 | 9
38961.5364 | 1 | 0 | 9
38961.5369 | 1 | 0 | 9
38961.5374 | 1 | 0 | 9
38961.5379 | 1 | 0 | 9
38961.5384 | 1 | 0 | 9
38961.5389 | 1 | 0 | 9
38961.5394 | 1 | 0 | 9
38961.5398 | 1 | 0 | 9
38961.5403 | 1 | 0 | 9
38961.5408 | 1 | 0 | 9
38961.5413 | 1 | 0 | 9
38961.5418 | 2 | 0 | 9
38961.5423 | 2 | 0 | 9
38961.5428 | 2 | 0 | 9
38961.5432 | 4 | 0 | 9
38961.5437 | 2163 | 17 | 9
38961.5442 | 1888 | 9 | 9
38961.5447 | 2 | 0 | 9
38961.5452 | 2 | 0 | 9
38961.5457 | 2400 | 5 | 9
38961.5462 | 1919 | 3 | 9
38961.5466 | 2225 | 3 | 9
38961.5471 | 1997 | 2 | 9
38961.5476 | 2436 | 3 | 9
38961.5481 | 2223 | 2 | 9
38961.5486 | 2036 | 2 | 9
38961.5491 | 1917 | 1 | 9
38961.5496 | 2068 | 2 | 9
38961.55 | 2452 | 3 | 9
38961.5505 | 2063 | 2 | 9
38961.551 | 164 | 0 | 9
38961.5515 | 1989 | 1 | 9
38961.552 | 2092 | 2 | 9
38961.5525 | 1917 | 1 | 9
38961.553 | 2366 | 2 | 9
38961.5534 | 2324 | 14 | 9
38961.5539 | 2164 | 10 | 9
38961.5544 | 1143 | 0 | 9
38961.5549 | 82 | 0 | 9
38961.5593 | 175 | 0 | 9
38961.5598 | 3 | 0 | 9
38961.5603 | 3 | 0 | 9
38961.5608 | 3 | 0 | 9
38961.5612 | 57 | 0 | 9
38961.5617 | 2 | 0 | 9
38961.5622 | 2 | 0 | 9
38961.5627 | 516 | 0 | 9
9
38961.5204 | 1 | 0 | 10
38961.5209 | 1 | 0 | 10
38961.5214 | 1 | 0 | 10
38961.5219 | 1 | 0 | 10
38961.5224 | 1 | 0 | 10
38961.5228 | 1 | 0 | 10
38961.5233 | 1 | 0 | 10
38961.5238 | 1 | 0 | 10
38961.5243 | 1 | 0 | 10
38961.5248 | 1 | 0 | 10
38961.5253 | 1 | 0 | 10
38961.5258 | 1 | 0 | 10
38961.5263 | 1 | 0 | 10
38961.5267 | 1 | 0 | 10
38961.5272 | 1 | 1 | 10
38961.5277 | 1 | 0 | 10
38961.5282 | 1 | 0 | 10
38961.5287 | 1 | 0 | 10
38961.5292 | 1 | 0 | 10
38961.5297 | 1 | 0 | 10
38961.5301 | 1 | 0 | 10
38961.5306 | 1 | 0 | 10
38961.5311 | 1 | 0 | 10
38961.5316 | 1 | 0 | 10
38961.5321 | 1 | 0 | 10
38961.5326 | 1 | 0 | 10
38961.5331 | 1 | 0 | 10
38961.5335 | 1 | 0 | 10
38961.534 | 1 | 0 | 10
38961.5345 | 1 | 0 | 10
38961.535 | 1 | 0 | 10
38961.5355 | 1 | 0 | 10
38961.536 | 1 | 0 | 10
38961.5365 | 1 | 0 | 10
38961.5369 | 1 | 0 | 10
38961.5374 | 1 | 0 | 10
38961.5379 | 1 | 0 | 10
38961.5384 | 1 | 0 | 10
38961.5389 | 1 | 0 | 10
38961.5394 | 1 | 0 | 10
38961.5399 | 1 | 0 | 10
38961.5403 | 1 | 0 | 10
38961.5408 | 1 | 0 | 10
38961.5413 | 1 | 0 | 10
38961.5418 | 2165 | 0 | 10
38961.5423 | 1929 | 0 | 10
38961.5428 | 16 | 0 | 10
38961.5433 | 2038 | 7 | 10
38961.5437 | 2408 | 15 | 10
38961.5442 | 2075 | 9 | 10
38961.5447 | 2350 | 0 | 10
38961.5452 | 2206 | 0 | 10
38961.5457 | 2056 | 4 | 10
38961.5462 | 2377 | 3 | 10
38961.5467 | 2188 | 3 | 10
38961.5472 | 2228 | 3 | 10
38961.5476 | 2353 | 3 | 10
38961.5481 | 2349 | 2 | 10
38961.5486 | 1967 | 2 | 10
38961.5491 | 2135 | 0 | 10
38961.5496 | 2128 | 2 | 10
38961.5501 | 2470 | 2 | 10
38961.5506 | 1996 | 2 | 10
38961.551 | 2258 | 0 | 10
38961.5515 | 2175 | 2 | 10
38961.552 | 2192 | 1 | 10
38961.5525 | 2134 | 1 | 10
38961.553 | 2126 | 2 | 10
38961.5535 | 2036 | 6 | 10
38961.554 | 2260 | 10 | 10
38961.5544 | 2322 | 0 | 10
38961.5549 | 2435 | 0 | 10
38961.5593 | 2256 | 0 | 10
38961.5598 | 2364 | 0 | 10
38961.5603 | 2003 | 0 | 10
38961.5608 | 2330 | 0 | 10
38961.5612 | 2407 | 0 | 10
38961.5617 | 2412 | 0 | 10
38961.5622 | 2400 | 0 | 10
38961.5627 | 2239 | 0 | 10
10
38961.5204 | 1 | 0 | 11
38961.5209 | 2 | 0 | 11
38961.5214 | 1 | 0 | 11
38961.5219 | 1 | 0 | 11
38961.5224 | 1 | 0 | 11
38961.5229 | 1 | 0 | 11
38961.5233 | 1 | 0 | 11
38961.5238 | 1 | 0 | 11
38961.5243 | 1 | 0 | 11
38961.5248 | 1 | 0 | 11
38961.5253 | 1 | 0 | 11
38961.5258 | 1 | 0 | 11
38961.5263 | 1 | 0 | 11
38961.5267 | 1 | 0 | 11
38961.5272 | 1 | 0 | 11
38961.5277 | 1 | 0 | 11
38961.5282 | 1 | 0 | 11
38961.5287 | 1 | 0 | 11
38961.5292 | 1 | 0 | 11
38961.5297 | 1 | 0 | 11
38961.5302 | 1 | 0 | 11
38961.5306 | 1 | 0 | 11
38961.5311 | 1 | 0 | 11
38961.5316 | 1 | 0 | 11
38961.5321 | 1 | 0 | 11
38961.5326 | 1 | 0 | 11
38961.5331 | 1 | 0 | 11
38961.5336 | 1 | 0 | 11
38961.534 | 1 | 0 | 11
38961.5345 | 1 | 0 | 11
38961.535 | 1 | 0 | 11
38961.5355 | 1 | 0 | 11
38961.536 | 1 | 0 | 11
38961.5365 | 1 | 0 | 11
38961.537 | 1 | 0 | 11
38961.5374 | 1 | 0 | 11
38961.5379 | 1 | 0 | 11
38961.5384 | 1 | 0 | 11
38961.5389 | 1 | 0 | 11
38961.5394 | 1 | 0 | 11
38961.5399 | 1 | 0 | 11
38961.5404 | 1 | 0 | 11
38961.5408 | 1 | 0 | 11
38961.5413 | 1 | 0 | 11
38961.5418 | 2 | 0 | 11
38961.5423 | 2 | 0 | 11
38961.5428 | 2 | 0 | 11
38961.5433 | 4 | 0 | 11
38961.5438 | 2306 | 0 | 11
38961.5442 | 2267 | 0 | 11
38961.5447 | 3 | 0 | 11
38961.5452 | 2 | 0 | 11
38961.5457 | 2416 | 0 | 11
38961.5462 | 1911 | 0 | 11
38961.5467 | 2434 | 0 | 11
38961.5472 | 2177 | 0 | 11
38961.5477 | 2357 | 0 | 11
38961.5481 | 2450 | 0 | 11
38961.5486 | 2077 | 0 | 11
38961.5491 | 2190 | 0 | 11
38961.5496 | 2230 | 0 | 11
38961.5501 | 2094 | 0 | 11
38961.5506 | 2380 | 0 | 11
38961.5511 | 1968 | 0 | 11
38961.5515 | 1966 | 0 | 11
38961.552 | 1939 | 0 | 11
38961.5525 | 1935 | 0 | 11
38961.553 | 2053 | 0 | 11
38961.5535 | 1916 | 0 | 11
38961.554 | 2237 | 0 | 11
38961.5545 | 2131 | 0 | 11
38961.5549 | 2460 | 0 | 11
38961.5593 | 2019 | 0 | 11
38961.5598 | 2327 | 0 | 11
38961.5603 | 2376 | 0 | 11
38961.5608 | 2335 | 0 | 11
38961.5613 | 2188 | 0 | 11
38961.5618 | 2450 | 0 | 11
38961.5622 | 2253 | 0 | 11
38961.5627 | 2357 | 0 | 11
11
38961.5205 | 1 | 0 | 12
38961.5209 | 1 | 0 | 12
38961.5214 | 1 | 0 | 12
38961.5219 | 1 | 0 | 12
38961.5224 | 1 | 0 | 12
38961.5229 | 1 | 0 | 12
38961.5234 | 1 | 0 | 12
38961.5239 | 1 | 0 | 12
38961.5243 | 1 | 0 | 12
38961.5248 | 1 | 0 | 12
38961.5253 | 1 | 0 | 12
38961.5258 | 1 | 0 | 12
38961.5263 | 1 | 0 | 12
38961.5268 | 1 | 0 | 12
38961.5273 | 1 | 0 | 12
38961.5277 | 1 | 0 | 12
38961.5282 | 1 | 0 | 12
38961.5287 | 1 | 0 | 12
38961.5292 | 1 | 0 | 12
38961.5297 | 1 | 0 | 12
38961.5302 | 1 | 0 | 12
38961.5307 | 1 | 0 | 12
38961.5311 | 1 | 0 | 12
38961.5316 | 1 | 0 | 12
38961.5321 | 1 | 0 | 12
38961.5326 | 1 | 0 | 12
38961.5331 | 1 | 0 | 12
38961.5336 | 1 | 0 | 12
38961.5341 | 1 | 0 | 12
38961.5345 | 1 | 0 | 12
38961.535 | 1 | 0 | 12
38961.5355 | 1 | 0 | 12
38961.536 | 1 | 0 | 12
38961.5365 | 1 | 0 | 12
38961.537 | 1 | 0 | 12
38961.5375 | 1 | 0 | 12
38961.538 | 1 | 0 | 12
38961.5384 | 1 | 0 | 12
38961.5389 | 1 | 0 | 12
38961.5394 | 1 | 0 | 12
38961.5399 | 1 | 0 | 12
38961.5404 | 1 | 0 | 12
38961.5409 | 1 | 0 | 12
38961.5414 | 1 | 0 | 12
38961.5418 | 2 | 0 | 12
38961.5423 | 2 | 0 | 12
38961.5428 | 2 | 0 | 12
38961.5433 | 2 | 0 | 12
38961.5438 | 2 | 0 | 12
38961.5443 | 76 | 0 | 12
38961.5448 | 152 | 0 | 12
38961.5452 | 236 | 0 | 12
38961.5457 | 3 | 0 | 12
38961.5462 | 304 | 0 | 12
38961.5467 | 2 | 0 | 12
38961.5472 | 2 | 0 | 12
38961.5477 | 2 | 0 | 12
38961.5481 | 2 | 0 | 12
38961.5486 | 2 | 0 | 12
38961.5491 | 1963 | 0 | 12
38961.5496 | 1960 | 0 | 12
38961.5501 | 1980 | 0 | 12
38961.5506 | 1392 | 0 | 12
38961.5511 | 27 | 1 | 12
38961.5516 | 70 | 0 | 12
38961.552 | 131 | 0 | 12
38961.5525 | 219 | 0 | 12
38961.553 | 297 | 0 | 12
38961.5535 | 642 | 0 | 12
38961.554 | 641 | 0 | 12
38961.5545 | 625 | 0 | 12
38961.555 | 589 | 0 | 12
38961.5593 | 186 | 0 | 12
38961.5598 | 148 | 0 | 12
38961.5603 | 14 | 0 | 12
38961.5608 | 7 | 0 | 12
38961.5613 | 4 | 0 | 12
38961.5618 | 3 | 0 | 12
38961.5623 | 3 | 0 | 12
38961.5627 | 3 | 0 | 12
12
38961.5205 | 1 | 0 | 13
38961.5209 | 1 | 0 | 13
38961.5214 | 1 | 0 | 13
38961.5219 | 1 | 0 | 13
38961.5224 | 1 | 0 | 13
38961.5229 | 1 | 0 | 13
38961.5234 | 1 | 0 | 13
38961.5239 | 1 | 0 | 13
38961.5244 | 1 | 0 | 13
38961.5248 | 1 | 0 | 13
38961.5253 | 1 | 0 | 13
38961.5258 | 1 | 0 | 13
38961.5263 | 1 | 0 | 13
38961.5268 | 1 | 0 | 13
38961.5273 | 1 | 0 | 13
38961.5278 | 1 | 0 | 13
38961.5282 | 1 | 0 | 13
38961.5287 | 1 | 0 | 13
38961.5292 | 1 | 0 | 13
38961.5297 | 1 | 0 | 13
38961.5302 | 1 | 0 | 13
38961.5307 | 1 | 0 | 13
38961.5312 | 1 | 0 | 13
38961.5316 | 1 | 0 | 13
38961.5321 | 1 | 0 | 13
38961.5326 | 1 | 0 | 13
38961.5331 | 1 | 0 | 13
38961.5336 | 1 | 0 | 13
38961.5341 | 1 | 0 | 13
38961.5346 | 1 | 0 | 13
38961.535 | 1 | 0 | 13
38961.5355 | 1 | 0 | 13
38961.536 | 1 | 0 | 13
38961.5365 | 1 | 0 | 13
38961.537 | 1 | 0 | 13
38961.5375 | 1 | 0 | 13
38961.538 | 1 | 0 | 13
38961.5384 | 1 | 0 | 13
38961.5389 | 1 | 0 | 13
38961.5394 | 1 | 0 | 13
38961.5399 | 1 | 0 | 13
38961.5404 | 1 | 0 | 13
38961.5409 | 1 | 0 | 13
38961.5414 | 1 | 0 | 13
38961.5419 | 2 | 0 | 13
38961.5423 | 2 | 0 | 13
38961.5428 | 2 | 0 | 13
38961.5433 | 2 | 0 | 13
38961.5438 | 1899 | 0 | 13
38961.5443 | 1947 | 0 | 13
38961.5448 | 2 | 0 | 13
38961.5453 | 2 | 0 | 13
38961.5457 | 1867 | 0 | 13
38961.5462 | 2357 | 0 | 13
38961.5467 | 2182 | 0 | 13
38961.5472 | 1889 | 0 | 13
38961.5477 | 2043 | 0 | 13
38961.5482 | 2254 | 0 | 13
38961.5487 | 2170 | 1 | 13
38961.5491 | 1689 | 0 | 13
38961.5496 | 2046 | 0 | 13
38961.5501 | 2455 | 0 | 13
38961.5506 | 1909 | 0 | 13
38961.5511 | 1394 | 1 | 13
38961.5516 | 2346 | 0 | 13
38961.5521 | 2235 | 0 | 13
38961.5525 | 2321 | 0 | 13
38961.553 | 2250 | 0 | 13
38961.5535 | 2423 | 0 | 13
38961.554 | 1526 | 0 | 13
38961.5545 | 2404 | 0 | 13
38961.555 | 234 | 0 | 13
38961.5594 | 4 | 0 | 13
38961.5598 | 3 | 0 | 13
38961.5603 | 3 | 0 | 13
38961.5608 | 2 | 0 | 13
38961.5613 | 276 | 0 | 13
38961.5618 | 12 | 0 | 13
38961.5623 | 192 | 0 | 13
13
38961.5205 | 1 | 0 | 14
38961.521 | 1 | 0 | 14
38961.5215 | 1 | 0 | 14
38961.5219 | 1 | 0 | 14
38961.5224 | 1 | 0 | 14
38961.5229 | 1 | 0 | 14
38961.5234 | 1 | 0 | 14
38961.5239 | 1 | 0 | 14
38961.5244 | 1 | 0 | 14
38961.5249 | 1 | 0 | 14
38961.5253 | 1 | 0 | 14
38961.5258 | 1 | 0 | 14
38961.5263 | 1 | 0 | 14
38961.5268 | 1 | 0 | 14
38961.5273 | 1 | 0 | 14
38961.5278 | 1 | 0 | 14
38961.5283 | 1 | 0 | 14
38961.5287 | 1 | 0 | 14
38961.5292 | 1 | 0 | 14
38961.5297 | 1 | 0 | 14
38961.5302 | 1 | 0 | 14
38961.5307 | 1 | 0 | 14
38961.5312 | 1 | 0 | 14
38961.5317 | 1 | 0 | 14
38961.5322 | 1 | 0 | 14
38961.5326 | 1 | 0 | 14
38961.5331 | 1 | 0 | 14
38961.5336 | 1 | 0 | 14
38961.5341 | 1 | 0 | 14
38961.5346 | 1 | 0 | 14
38961.5351 | 1 | 0 | 14
38961.5355 | 1 | 0 | 14
38961.536 | 1 | 0 | 14
38961.5365 | 1 | 0 | 14
38961.537 | 1 | 0 | 14
38961.5375 | 1 | 0 | 14
38961.538 | 1 | 0 | 14
38961.5385 | 1 | 0 | 14
38961.5389 | 1 | 0 | 14
38961.5394 | 1 | 0 | 14
38961.5399 | 1 | 0 | 14
38961.5404 | 1 | 0 | 14
38961.5409 | 1 | 0 | 14
38961.5414 | 1 | 0 | 14
38961.5419 | 1 | 0 | 14
38961.5423 | 1 | 0 | 14
38961.5428 | 2 | 0 | 14
38961.5433 | 2 | 0 | 14
38961.5438 | 2391 | 0 | 14
38961.5443 | 1974 | 0 | 14
38961.5448 | 2 | 0 | 14
38961.5453 | 2 | 0 | 14
38961.5458 | 2234 | 0 | 14
38961.5462 | 2035 | 0 | 14
38961.5467 | 2264 | 0 | 14
38961.5472 | 2071 | 0 | 14
38961.5477 | 1960 | 0 | 14
38961.5482 | 1957 | 0 | 14
38961.5487 | 2406 | 0 | 14
38961.5492 | 2139 | 0 | 14
38961.5496 | 2473 | 0 | 14
38961.5501 | 1994 | 1 | 14
38961.5506 | 2135 | 0 | 14
38961.5511 | 2465 | 0 | 14
38961.5516 | 2299 | 0 | 14
38961.5521 | 2404 | 0 | 14
38961.5526 | 2129 | 0 | 14
38961.553 | 2215 | 0 | 14
38961.5535 | 2213 | 0 | 14
38961.554 | 2361 | 0 | 14
38961.5545 | 1963 | 0 | 14
38961.555 | 1995 | 0 | 14
38961.5594 | 2091 | 0 | 14
38961.5599 | 1993 | 0 | 14
38961.5603 | 2114 | 0 | 14
38961.5608 | 2343 | 0 | 14
38961.5613 | 1981 | 0 | 14
38961.5618 | 2310 | 0 | 14
38961.5623 | 2438 | 0 | 14
38961.5628 | 2128 | 0 | 14
14
38961.5205 | 1 | 0 | 15
38961.521 | 1 | 0 | 15
38961.5215 | 1 | 0 | 15
38961.522 | 1 | 0 | 15
38961.5224 | 1 | 0 | 15
38961.5229 | 1 | 0 | 15
38961.5234 | 1 | 0 | 15
38961.5239 | 1 | 0 | 15
38961.5244 | 1 | 0 | 15
38961.5249 | 1 | 0 | 15
38961.5254 | 1 | 0 | 15
38961.5258 | 1 | 0 | 15
38961.5263 | 1 | 0 | 15
38961.5268 | 1 | 0 | 15
38961.5273 | 1 | 0 | 15
38961.5278 | 1 | 0 | 15
38961.5283 | 1 | 0 | 15
38961.5288 | 1 | 0 | 15
38961.5292 | 1 | 0 | 15
38961.5297 | 1 | 0 | 15
38961.5302 | 1 | 0 | 15
38961.5307 | 1 | 0 | 15
38961.5312 | 1 | 0 | 15
38961.5317 | 1 | 0 | 15
38961.5322 | 1 | 0 | 15
38961.5327 | 1 | 0 | 15
38961.5331 | 1 | 0 | 15
38961.5336 | 1 | 0 | 15
38961.5341 | 1 | 0 | 15
38961.5346 | 1 | 0 | 15
38961.5351 | 1 | 0 | 15
38961.5356 | 1 | 0 | 15
38961.5361 | 1 | 0 | 15
38961.5365 | 1 | 0 | 15
38961.537 | 1 | 0 | 15
38961.5375 | 1 | 0 | 15
38961.538 | 1 | 0 | 15
38961.5385 | 1 | 0 | 15
38961.539 | 1 | 0 | 15
38961.5395 | 1 | 0 | 15
38961.5399 | 1 | 0 | 15
38961.5404 | 1 | 0 | 15
38961.5409 | 1 | 0 | 15
38961.5414 | 1 | 0 | 15
38961.5419 | 1 | 0 | 15
38961.5424 | 2 | 0 | 15
38961.5429 | 2 | 0 | 15
38961.5433 | 2 | 0 | 15
38961.5438 | 2031 | 13 | 15
38961.5443 | 2396 | 8 | 15
38961.5448 | 2 | 0 | 15
38961.5453 | 2 | 0 | 15
38961.5458 | 2251 | 5 | 15
38961.5463 | 2221 | 4 | 15
38961.5467 | 2172 | 3 | 15
38961.5472 | 2175 | 4 | 15
38961.5477 | 2200 | 2 | 15
38961.5482 | 2168 | 2 | 15
38961.5487 | 2450 | 2 | 15
38961.5492 | 2059 | 1 | 15
38961.5497 | 1991 | 1 | 15
38961.5502 | 2126 | 2 | 15
38961.5506 | 2014 | 1 | 15
38961.5511 | 2246 | 2 | 15
38961.5516 | 2031 | 3 | 15
38961.5521 | 2333 | 2 | 15
38961.5526 | 2259 | 1 | 15
38961.5531 | 2335 | 1 | 15
38961.5536 | 2460 | 1 | 15
38961.554 | 1983 | 1 | 15
38961.5545 | 2133 | 2 | 15
38961.555 | 2104 | 2 | 15
38961.5594 | 1965 | 2 | 15
38961.5599 | 2267 | 2 | 15
38961.5604 | 2033 | 1 | 15
38961.5609 | 2286 | 2 | 15
38961.5613 | 2042 | 2 | 15
38961.5618 | 2362 | 2 | 15
38961.5623 | 1977 | 1 | 15
38961.5628 | 2184 | 2 | 15
15
38961.5205 | 1 | 0 | 16
38961.521 | 1 | 0 | 16
38961.5215 | 1 | 0 | 16
38961.522 | 1 | 0 | 16
38961.5225 | 1 | 0 | 16
38961.5229 | 1 | 0 | 16
38961.5234 | 1 | 0 | 16
38961.5239 | 1 | 0 | 16
38961.5244 | 1 | 0 | 16
38961.5249 | 1 | 0 | 16
38961.5254 | 1 | 0 | 16
38961.5259 | 1 | 0 | 16
38961.5263 | 1 | 0 | 16
38961.5268 | 1 | 0 | 16
38961.5273 | 1 | 0 | 16
38961.5278 | 1 | 0 | 16
38961.5283 | 1 | 0 | 16
38961.5288 | 1 | 0 | 16
38961.5293 | 1 | 0 | 16
38961.5297 | 1 | 0 | 16
38961.5302 | 1 | 0 | 16
38961.5307 | 1 | 0 | 16
38961.5312 | 1 | 0 | 16
38961.5317 | 1 | 0 | 16
38961.5322 | 1 | 0 | 16
38961.5327 | 1 | 0 | 16
38961.5331 | 1 | 0 | 16
38961.5336 | 1 | 0 | 16
38961.5341 | 1 | 0 | 16
38961.5346 | 1 | 0 | 16
38961.5351 | 1 | 0 | 16
38961.5356 | 1 | 0 | 16
38961.5361 | 1 | 0 | 16
38961.5366 | 1 | 0 | 16
38961.537 | 1 | 0 | 16
38961.5375 | 1 | 0 | 16
38961.538 | 1 | 0 | 16
38961.5385 | 1 | 0 | 16
38961.539 | 1 | 0 | 16
38961.5395 | 1 | 0 | 16
38961.54 | 1 | 0 | 16
38961.5404 | 1 | 0 | 16
38961.5409 | 1 | 0 | 16
38961.5414 | 303 | 0 | 16
38961.5419 | 1972 | 0 | 16
38961.5424 | 2316 | 0 | 16
38961.5429 | 1974 | 0 | 16
38961.5434 | 2348 | 12 | 16
38961.5438 | 2124 | 13 | 16
38961.5443 | 2172 | 9 | 16
38961.5448 | 2271 | 0 | 16
38961.5453 | 2138 | 0 | 16
38961.5458 | 2272 | 5 | 16
38961.5463 | 2057 | 3 | 16
38961.5468 | 2362 | 3 | 16
38961.5472 | 2047 | 2 | 16
38961.5477 | 1925 | 1 | 16
38961.5482 | 2269 | 2 | 16
38961.5487 | 1970 | 1 | 16
38961.5492 | 1915 | 1 | 16
38961.5497 | 2476 | 2 | 16
38961.5502 | 1922 | 1 | 16
38961.5506 | 2181 | 2 | 16
38961.5511 | 2472 | 2 | 16
38961.5516 | 1965 | 1 | 16
38961.5521 | 2252 | 1 | 16
38961.5526 | 2184 | 1 | 16
38961.5531 | 2236 | 1 | 16
38961.5536 | 2135 | 1 | 16
38961.5541 | 2280 | 1 | 16
38961.5545 | 2482 | 1 | 16
38961.555 | 2106 | 1 | 16
38961.5594 | 2312 | 1 | 16
38961.5599 | 2295 | 2 | 16
38961.5604 | 2450 | 2 | 16
38961.5609 | 2388 | 2 | 16
38961.5614 | 2041 | 1 | 16
38961.5618 | 1912 | 2 | 16
38961.5623 | 2211 | 2 | 16
38961.5628 | 2208 | 2 | 16
16
38961.5205 | 1 | 0 | 17
38961.521 | 1 | 0 | 17
38961.5215 | 1 | 0 | 17
38961.522 | 1 | 0 | 17
38961.5225 | 1 | 0 | 17
38961.523 | 1 | 0 | 17
38961.5234 | 1 | 0 | 17
38961.5239 | 1 | 0 | 17
38961.5244 | 1 | 0 | 17
38961.5249 | 1 | 0 | 17
38961.5254 | 1 | 0 | 17
38961.5259 | 1 | 0 | 17
38961.5264 | 1 | 0 | 17
38961.5269 | 1 | 0 | 17
38961.5273 | 1 | 0 | 17
38961.5278 | 1 | 0 | 17
38961.5283 | 1 | 0 | 17
38961.5288 | 1 | 0 | 17
38961.5293 | 1 | 0 | 17
38961.5298 | 1 | 0 | 17
38961.5303 | 1 | 0 | 17
38961.5307 | 1 | 0 | 17
38961.5312 | 1 | 0 | 17
38961.5317 | 1 | 0 | 17
38961.5322 | 1 | 0 | 17
38961.5327 | 1 | 0 | 17
38961.5332 | 1 | 0 | 17
38961.5337 | 1 | 0 | 17
38961.5341 | 1 | 0 | 17
38961.5346 | 1 | 0 | 17
38961.5351 | 1 | 0 | 17
38961.5356 | 1 | 0 | 17
38961.5361 | 1 | 0 | 17
38961.5366 | 1 | 0 | 17
38961.5371 | 1 | 0 | 17
38961.5375 | 1 | 0 | 17
38961.538 | 1 | 0 | 17
38961.5385 | 1 | 0 | 17
38961.539 | 1 | 0 | 17
38961.5395 | 1 | 0 | 17
38961.54 | 1 | 0 | 17
38961.5405 | 1 | 0 | 17
38961.5409 | 1 | 0 | 17
38961.5414 | 1 | 0 | 17
38961.5419 | 2 | 0 | 17
38961.5424 | 2 | 0 | 17
38961.5429 | 2 | 0 | 17
38961.5434 | 2 | 0 | 17
38961.5439 | 1951 | 11 | 17
38961.5444 | 1987 | 7 | 17
38961.5448 | 3 | 0 | 17
38961.5453 | 9 | 0 | 17
38961.5458 | 2043 | 4 | 17
38961.5463 | 2295 | 3 | 17
38961.5468 | 2395 | 3 | 17
38961.5473 | 1935 | 2 | 17
38961.5478 | 2448 | 2 | 17
38961.5482 | 2153 | 2 | 17
38961.5487 | 2057 | 2 | 17
38961.5492 | 2051 | 2 | 17
38961.5497 | 2326 | 2 | 17
38961.5502 | 2068 | 1 | 17
38961.5507 | 2390 | 2 | 17
38961.5512 | 2106 | 0 | 17
38961.5516 | 2187 | 1 | 17
38961.5521 | 2356 | 1 | 17
38961.5526 | 1922 | 1 | 17
38961.5531 | 2350 | 1 | 17
38961.5536 | 2481 | 1 | 17
38961.5541 | 2015 | 1 | 17
38961.5545 | 2397 | 1 | 17
38961.555 | 2065 | 1 | 17
38961.5594 | 2301 | 2 | 17
38961.5599 | 1921 | 1 | 17
38961.5604 | 1958 | 1 | 17
38961.5609 | 2169 | 1 | 17
38961.5614 | 2428 | 1 | 17
38961.5619 | 2020 | 1 | 17
38961.5623 | 1921 | 1 | 17
38961.5628 | 2092 | 1 | 17
17
38961.5205 | 1 | 0 | 18
38961.521 | 1 | 0 | 18
38961.5215 | 1 | 0 | 18
38961.522 | 1 | 0 | 18
38961.5225 | 1 | 0 | 18
38961.523 | 1 | 0 | 18
38961.5235 | 1 | 0 | 18
38961.5239 | 1 | 0 | 18
38961.5244 | 1 | 0 | 18
38961.5249 | 1 | 0 | 18
38961.5254 | 1 | 0 | 18
38961.5259 | 1 | 0 | 18
38961.5264 | 1 | 0 | 18
38961.5269 | 1 | 0 | 18
38961.5273 | 1 | 0 | 18
38961.5278 | 1 | 0 | 18
38961.5283 | 1 | 0 | 18
38961.5288 | 1 | 0 | 18
38961.5293 | 1 | 0 | 18
38961.5298 | 1 | 0 | 18
38961.5303 | 1 | 0 | 18
38961.5308 | 1 | 0 | 18
38961.5312 | 1 | 0 | 18
38961.5317 | 1 | 0 | 18
38961.5322 | 1 | 0 | 18
38961.5327 | 1 | 0 | 18
38961.5332 | 1 | 0 | 18
38961.5337 | 1 | 0 | 18
38961.5342 | 1 | 0 | 18
38961.5346 | 1 | 0 | 18
38961.5351 | 1 | 0 | 18
38961.5356 | 1 | 0 | 18
38961.5361 | 1 | 0 | 18
38961.5366 | 1 | 0 | 18
38961.5371 | 1 | 0 | 18
38961.5376 | 1 | 0 | 18
38961.538 | 1 | 0 | 18
38961.5385 | 1 | 0 | 18
38961.539 | 1 | 0 | 18
38961.5395 | 1 | 0 | 18
38961.54 | 1 | 0 | 18
38961.5405 | 1 | 0 | 18
38961.541 | 1 | 0 | 18
38961.5414 | 1 | 0 | 18
38961.5419 | 2050 | 0 | 18
38961.5424 | 1972 | 0 | 18
38961.5429 | 1980 | 0 | 18
38961.5434 | 2128 | 0 | 18
38961.5439 | 2105 | 13 | 18
38961.5444 | 2283 | 2 | 18
38961.5448 | 1874 | 0 | 18
38961.5453 | 1915 | 0 | 18
38961.5458 | 2435 | 5 | 18
38961.5463 | 1896 | 3 | 18
38961.5468 | 2100 | 3 | 18
38961.5473 | 2353 | 2 | 18
38961.5478 | 2391 | 2 | 18
38961.5483 | 2364 | 2 | 18
38961.5487 | 2205 | 2 | 18
38961.5492 | 2081 | 1 | 18
38961.5497 | 2272 | 1 | 18
38961.5502 | 2019 | 1 | 18
38961.5507 | 1957 | 1 | 18
38961.5512 | 2192 | 2 | 18
38961.5517 | 2314 | 1 | 18
38961.5521 | 2068 | 1 | 18
38961.5526 | 2380 | 1 | 18
38961.5531 | 2474 | 1 | 18
38961.5536 | 1963 | 1 | 18
38961.5541 | 2130 | 1 | 18
38961.5546 | 1912 | 1 | 18
38961.5551 | 2024 | 1 | 18
38961.5594 | 2160 | 1 | 18
38961.5599 | 2146 | 1 | 18
38961.5604 | 2071 | 1 | 18
38961.5609 | 1965 | 1 | 18
38961.5614 | 2113 | 1 | 18
38961.5619 | 1869 | 1 | 18
38961.5624 | 2071 | 1 | 18
38961.5628 | 1983 | 1 | 18
18
38961.5206 | 1 | 0 | 19
38961.5211 | 1 | 0 | 19
38961.5215 | 1 | 0 | 19
38961.522 | 1 | 0 | 19
38961.5225 | 1 | 0 | 19
38961.523 | 1 | 0 | 19
38961.5235 | 1 | 0 | 19
38961.524 | 1 | 0 | 19
38961.5245 | 1 | 0 | 19
38961.5249 | 1 | 0 | 19
38961.5254 | 1 | 0 | 19
38961.5259 | 1 | 0 | 19
38961.5264 | 1 | 0 | 19
38961.5269 | 1 | 0 | 19
38961.5274 | 1 | 0 | 19
38961.5279 | 1 | 0 | 19
38961.5283 | 1 | 0 | 19
38961.5288 | 1 | 0 | 19
38961.5293 | 1 | 0 | 19
38961.5298 | 1 | 0 | 19
38961.5303 | 1 | 0 | 19
38961.5308 | 1 | 0 | 19
38961.5312 | 1 | 0 | 19
38961.5317 | 1 | 0 | 19
38961.5322 | 1 | 0 | 19
38961.5327 | 1 | 0 | 19
38961.5332 | 1 | 0 | 19
38961.5337 | 1 | 0 | 19
38961.5342 | 1 | 0 | 19
38961.5347 | 1 | 0 | 19
38961.5351 | 1 | 0 | 19
38961.5356 | 1 | 0 | 19
38961.5361 | 1 | 0 | 19
38961.5366 | 1 | 0 | 19
38961.5371 | 1 | 0 | 19
38961.5376 | 1 | 0 | 19
38961.5381 | 1 | 0 | 19
38961.5385 | 1 | 0 | 19
38961.539 | 1 | 0 | 19
38961.5395 | 1 | 0 | 19
38961.54 | 1 | 0 | 19
38961.5405 | 1 | 0 | 19
38961.541 | 1 | 0 | 19
38961.5415 | 1 | 0 | 19
38961.5419 | 2 | 0 | 19
38961.5424 | 2 | 0 | 19
38961.5429 | 2 | 0 | 19
38961.5434 | 1179 | 1189 | 19
38961.5439 | 1177 | 1138 | 19
38961.5444 | 1144 | 1102 | 19
38961.5449 | 1017 | 975 | 19
38961.5453 | 1089 | 1146 | 19
38961.5458 | 1012 | 971 | 19
38961.5463 | 472 | 472 | 19
38961.5468 | 1000 | 961 | 19
38961.5473 | 1100 | 1056 | 19
38961.5478 | 1023 | 979 | 19
38961.5483 | 1094 | 1122 | 19
38961.5488 | 629 | 619 | 19
38961.5492 | 2275 | 77 | 19
38961.5497 | 1927 | 41 | 19
38961.5502 | 1866 | 684 | 19
38961.5507 | 1203 | 1164 | 19
38961.5512 | 1239 | 1153 | 19
38961.5517 | 691 | 547 | 19
38961.5522 | 1237 | 1051 | 19
38961.5526 | 1234 | 870 | 19
38961.5531 | 1054 | 797 | 19
38961.5536 | 1392 | 903 | 19
38961.5541 | 1158 | 743 | 19
38961.5546 | 1302 | 807 | 19
38961.5551 | 1116 | 724 | 19
38961.5595 | 465 | 1 | 19
38961.5599 | 16 | 0 | 19
38961.5604 | 213 | 170 | 19
38961.5609 | 6 | 0 | 19
38961.5614 | 4 | 0 | 19
38961.5619 | 4 | 0 | 19
38961.5624 | 19 | 11 | 19
38961.5629 | 2 | 0 | 19
19
38961.5206 | 1 | 0 | 20
38961.5211 | 1 | 0 | 20
38961.5216 | 1 | 0 | 20
38961.522 | 1 | 0 | 20
38961.5225 | 1 | 0 | 20
38961.523 | 1 | 0 | 20
38961.5235 | 1 | 0 | 20
38961.524 | 1 | 0 | 20
38961.5245 | 1 | 0 | 20
38961.525 | 1 | 0 | 20
38961.5254 | 1 | 0 | 20
38961.5259 | 1 | 0 | 20
38961.5264 | 1 | 0 | 20
38961.5269 | 1 | 0 | 20
38961.5274 | 1 | 0 | 20
38961.5279 | 1 | 0 | 20
38961.5284 | 1 | 0 | 20
38961.5288 | 1 | 0 | 20
38961.5293 | 1 | 0 | 20
38961.5298 | 1 | 0 | 20
38961.5303 | 1 | 0 | 20
38961.5308 | 1 | 0 | 20
38961.5313 | 1 | 0 | 20
38961.5318 | 1 | 0 | 20
38961.5322 | 1 | 0 | 20
38961.5327 | 1 | 0 | 20
38961.5332 | 1 | 0 | 20
38961.5337 | 1 | 0 | 20
38961.5342 | 1 | 0 | 20
38961.5347 | 1 | 0 | 20
38961.5352 | 1 | 0 | 20
38961.5356 | 1 | 0 | 20
38961.5361 | 1 | 0 | 20
38961.5366 | 1 | 0 | 20
38961.5371 | 1 | 0 | 20
38961.5376 | 1 | 0 | 20
38961.5381 | 1 | 0 | 20
38961.5386 | 1 | 0 | 20
38961.5391 | 1 | 0 | 20
38961.5395 | 1 | 0 | 20
38961.54 | 1 | 0 | 20
38961.5405 | 1 | 0 | 20
38961.541 | 1 | 0 | 20
38961.5415 | 1 | 0 | 20
38961.542 | 2 | 0 | 20
38961.5425 | 2 | 0 | 20
38961.5429 | 2 | 0 | 20
38961.5434 | 1019 | 1107 | 20
38961.5439 | 1083 | 1046 | 20
38961.5444 | 1004 | 967 | 20
38961.5449 | 1206 | 1177 | 20
38961.5454 | 1198 | 1116 | 20
38961.5459 | 1004 | 915 | 20
38961.5463 | 927 | 943 | 20
38961.5468 | 1031 | 991 | 20
38961.5473 | 1183 | 1161 | 20
38961.5478 | 1107 | 1061 | 20
38961.5483 | 1171 | 1176 | 20
38961.5488 | 949 | 944 | 20
38961.5493 | 2308 | 66 | 20
38961.5497 | 2080 | 38 | 20
38961.5502 | 1607 | 737 | 20
38961.5507 | 1115 | 1063 | 20
38961.5512 | 1255 | 1147 | 20
38961.5517 | 437 | 344 | 20
38961.5522 | 1198 | 853 | 20
38961.5527 | 1329 | 912 | 20
38961.5531 | 1125 | 856 | 20
38961.5536 | 1344 | 876 | 20
38961.5541 | 1351 | 930 | 20
38961.5546 | 1139 | 719 | 20
38961.5551 | 1400 | 864 | 20
38961.5595 | 74 | 0 | 20
38961.56 | 56 | 0 | 20
38961.5604 | 138 | 55 | 20
38961.5609 | 34 | 6 | 20
38961.5614 | 15 | 0 | 20
38961.5619 | 13 | 0 | 20
38961.5624 | 8 | 0 | 20
38961.5629 | 4 | 0 | 20
20
38961.5206 | 1 | 0 | 21
38961.5211 | 1 | 0 | 21
38961.5216 | 1 | 0 | 21
38961.5221 | 1 | 0 | 21
38961.5225 | 1 | 0 | 21
38961.523 | 1 | 0 | 21
38961.5235 | 1 | 0 | 21
38961.524 | 1 | 0 | 21
38961.5245 | 1 | 0 | 21
38961.525 | 1 | 0 | 21
38961.5255 | 1 | 0 | 21
38961.5259 | 1 | 0 | 21
38961.5264 | 1 | 0 | 21
38961.5269 | 1 | 0 | 21
38961.5274 | 1 | 0 | 21
38961.5279 | 1 | 0 | 21
38961.5284 | 1 | 0 | 21
38961.5289 | 1 | 0 | 21
38961.5293 | 1 | 0 | 21
38961.5298 | 1 | 0 | 21
38961.5303 | 1 | 0 | 21
38961.5308 | 1 | 0 | 21
38961.5313 | 1 | 0 | 21
38961.5318 | 1 | 0 | 21
38961.5323 | 1 | 0 | 21
38961.5327 | 1 | 0 | 21
38961.5332 | 1 | 0 | 21
38961.5337 | 1 | 0 | 21
38961.5342 | 1 | 0 | 21
38961.5347 | 1 | 0 | 21
38961.5352 | 1 | 0 | 21
38961.5357 | 1 | 0 | 21
38961.5361 | 1 | 0 | 21
38961.5366 | 1 | 0 | 21
38961.5371 | 1 | 0 | 21
38961.5376 | 1 | 0 | 21
38961.5381 | 1 | 0 | 21
38961.5386 | 1 | 0 | 21
38961.5391 | 1 | 0 | 21
38961.5395 | 1 | 0 | 21
38961.54 | 1 | 0 | 21
38961.5405 | 1 | 0 | 21
38961.541 | 1 | 0 | 21
38961.5415 | 1 | 0 | 21
38961.542 | 1 | 0 | 21
38961.5425 | 1 | 0 | 21
38961.543 | 2 | 0 | 21
38961.5434 | 2 | 2 | 21
38961.5439 | 2 | 2 | 21
38961.5444 | 2 | 2 | 21
38961.5449 | 62 | 1 | 21
38961.5454 | 2 | 1 | 21
38961.5459 | 55 | 1 | 21
38961.5464 | 25 | 1 | 21
38961.5468 | 2 | 1 | 21
38961.5473 | 2 | 1 | 21
38961.5478 | 2 | 1 | 21
38961.5483 | 2 | 1 | 21
38961.5488 | 5 | 1 | 21
38961.5493 | 2288 | 0 | 21
38961.5498 | 1847 | 0 | 21
38961.5502 | 2006 | 1 | 21
38961.5507 | 186 | 1 | 21
38961.5512 | 31 | 1 | 21
38961.5517 | 74 | 0 | 21
38961.5522 | 145 | 1 | 21
38961.5527 | 168 | 1 | 21
38961.5532 | 403 | 1 | 21
38961.5536 | 531 | 1 | 21
38961.5541 | 580 | 1 | 21
38961.5546 | 643 | 1 | 21
38961.5551 | 758 | 1 | 21
38961.5595 | 24 | 0 | 21
38961.56 | 14 | 0 | 21
38961.5605 | 10 | 0 | 21
38961.5609 | 5 | 0 | 21
38961.5614 | 3 | 0 | 21
38961.5619 | 3 | 0 | 21
38961.5624 | 2 | 0 | 21
38961.5629 | 2 | 0 | 21
21
38961.5206 | 1 | 0 | 22
38961.5211 | 1 | 0 | 22
38961.5216 | 1 | 0 | 22
38961.5221 | 1 | 0 | 22
38961.5226 | 1 | 0 | 22
38961.523 | 1 | 0 | 22
38961.5235 | 1 | 0 | 22
38961.524 | 1 | 0 | 22
38961.5245 | 1 | 0 | 22
38961.525 | 1 | 0 | 22
38961.5255 | 1 | 0 | 22
38961.526 | 1 | 0 | 22
38961.5264 | 1 | 0 | 22
38961.5269 | 1 | 0 | 22
38961.5274 | 1 | 0 | 22
38961.5279 | 1 | 0 | 22
38961.5284 | 1 | 0 | 22
38961.5289 | 1 | 0 | 22
38961.5294 | 1 | 0 | 22
38961.5298 | 1 | 0 | 22
38961.5303 | 1 | 0 | 22
38961.5308 | 1 | 0 | 22
38961.5313 | 1 | 0 | 22
38961.5318 | 1 | 0 | 22
38961.5323 | 1 | 0 | 22
38961.5328 | 1 | 0 | 22
38961.5333 | 1 | 0 | 22
38961.5337 | 1 | 0 | 22
38961.5342 | 1 | 0 | 22
38961.5347 | 1 | 0 | 22
38961.5352 | 1 | 0 | 22
38961.5357 | 1 | 0 | 22
38961.5362 | 1 | 0 | 22
38961.5367 | 1 | 0 | 22
38961.5371 | 1 | 0 | 22
38961.5376 | 1 | 0 | 22
38961.5381 | 1 | 0 | 22
38961.5386 | 1 | 0 | 22
38961.5391 | 1 | 0 | 22
38961.5396 | 1 | 0 | 22
38961.5401 | 1 | 0 | 22
38961.541 | 1 | 0 | 22
38961.5415 | 1281 | 0 | 22
38961.542 | 1658 | 0 | 22
38961.5425 | 1862 | 0 | 22
38961.543 | 2051 | 0 | 22
38961.5435 | 1957 | 1 | 22
38961.5439 | 2216 | 1 | 22
38961.5444 | 2400 | 1 | 22
38961.5449 | 1903 | 1 | 22
38961.5459 | 1988 | 0 | 22
38961.5464 | 2155 | 1 | 22
38961.5469 | 2437 | 1 | 22
38961.5473 | 1968 | 1 | 22
38961.5478 | 2437 | 1 | 22
38961.5483 | 2436 | 1 | 22
38961.5488 | 2281 | 0 | 22
38961.5493 | 2034 | 0 | 22
38961.5498 | 1916 | 0 | 22
38961.5503 | 2001 | 0 | 22
38961.5508 | 2327 | 1 | 22
38961.5512 | 2119 | 0 | 22
38961.5517 | 2051 | 0 | 22
38961.5522 | 2404 | 0 | 22
38961.5527 | 2301 | 0 | 22
38961.5532 | 2191 | 0 | 22
38961.5537 | 2384 | 0 | 22
38961.5541 | 2270 | 0 | 22
38961.5546 | 1931 | 0 | 22
38961.5551 | 2292 | 0 | 22
38961.5595 | 2210 | 0 | 22
38961.56 | 2012 | 0 | 22
38961.5605 | 2403 | 0 | 22
38961.561 | 2280 | 0 | 22
38961.5614 | 2027 | 0 | 22
38961.5619 | 2333 | 0 | 22
38961.5624 | 2120 | 0 | 22
38961.5629 | 1942 | 0 | 22
22
38961.5206 | 1 | 0 | 23
38961.5211 | 1 | 0 | 23
38961.5216 | 1 | 0 | 23
38961.5221 | 1 | 0 | 23
38961.5226 | 1 | 0 | 23
38961.5231 | 1 | 0 | 23
38961.5235 | 1 | 0 | 23
38961.524 | 1 | 0 | 23
38961.5245 | 1 | 0 | 23
38961.525 | 1 | 0 | 23
38961.5255 | 1 | 0 | 23
38961.526 | 1 | 0 | 23
38961.5265 | 1 | 0 | 23
38961.5269 | 1 | 0 | 23
38961.5274 | 1 | 0 | 23
38961.5279 | 1 | 0 | 23
38961.5284 | 1 | 0 | 23
38961.5289 | 1 | 0 | 23
38961.5294 | 1 | 0 | 23
38961.5299 | 1 | 0 | 23
38961.5303 | 1 | 0 | 23
38961.5308 | 1 | 0 | 23
38961.5313 | 1 | 0 | 23
38961.5318 | 1 | 0 | 23
38961.5323 | 1 | 0 | 23
38961.5328 | 1 | 0 | 23
38961.5333 | 1 | 0 | 23
38961.5338 | 1 | 0 | 23
38961.5342 | 1 | 0 | 23
38961.5347 | 1 | 0 | 23
38961.5352 | 1 | 0 | 23
38961.5357 | 1 | 0 | 23
38961.5362 | 1 | 0 | 23
38961.5367 | 1 | 0 | 23
38961.5372 | 1 | 0 | 23
38961.5376 | 1 | 0 | 23
38961.5381 | 1 | 0 | 23
38961.5386 | 1 | 0 | 23
38961.5391 | 1 | 0 | 23
38961.5396 | 1 | 0 | 23
38961.5401 | 1 | 0 | 23
38961.5406 | 1 | 0 | 23
38961.541 | 1 | 0 | 23
38961.5415 | 1 | 0 | 23
38961.542 | 2 | 0 | 23
38961.5425 | 3 | 0 | 23
38961.543 | 2 | 0 | 23
38961.5435 | 2 | 0 | 23
38961.544 | 2 | 1 | 23
38961.5444 | 3 | 0 | 23
38961.5449 | 191 | 0 | 23
38961.5454 | 2 | 1 | 23
38961.5459 | 61 | 0 | 23
38961.5464 | 3 | 0 | 23
38961.5469 | 3 | 0 | 23
38961.5474 | 2 | 0 | 23
38961.5478 | 2 | 0 | 23
38961.5483 | 2 | 0 | 23
38961.5488 | 755 | 0 | 23
38961.5493 | 2123 | 0 | 23
38961.5498 | 2337 | 0 | 23
38961.5503 | 1816 | 0 | 23
38961.5508 | 39 | 0 | 23
38961.5512 | 33 | 0 | 23
38961.5517 | 100 | 0 | 23
38961.5522 | 249 | 1 | 23
38961.5527 | 995 | 0 | 23
38961.5532 | 413 | 0 | 23
38961.5537 | 654 | 0 | 23
38961.5542 | 564 | 0 | 23
38961.5547 | 674 | 0 | 23
38961.5551 | 670 | 0 | 23
38961.5595 | 165 | 0 | 23
38961.56 | 18 | 0 | 23
38961.5605 | 10 | 0 | 23
38961.561 | 6 | 0 | 23
38961.5615 | 4 | 0 | 23
38961.562 | 3 | 0 | 23
38961.5624 | 2 | 0 | 23
38961.5629 | 3 | 0 | 23
23
38961.5206 | 1 | 0 | 24
38961.5211 | 1 | 0 | 24
38961.5216 | 1 | 0 | 24
38961.5221 | 1 | 0 | 24
38961.5226 | 1 | 0 | 24
38961.5231 | 1 | 0 | 24
38961.5236 | 1 | 0 | 24
38961.5241 | 1 | 0 | 24
38961.5245 | 1 | 0 | 24
38961.525 | 1 | 0 | 24
38961.5255 | 1 | 0 | 24
38961.526 | 1 | 0 | 24
38961.5265 | 1 | 0 | 24
38961.527 | 1 | 0 | 24
38961.5275 | 1 | 0 | 24
38961.5279 | 1 | 0 | 24
38961.5284 | 1 | 0 | 24
38961.5289 | 1 | 0 | 24
38961.5294 | 1 | 0 | 24
38961.5299 | 1 | 0 | 24
38961.5304 | 1 | 0 | 24
38961.5309 | 1 | 0 | 24
38961.5313 | 1 | 0 | 24
38961.5318 | 1 | 0 | 24
38961.5323 | 1 | 0 | 24
38961.5328 | 1 | 0 | 24
38961.5333 | 1 | 0 | 24
38961.5338 | 1 | 0 | 24
38961.5342 | 1 | 0 | 24
38961.5347 | 1 | 0 | 24
38961.5352 | 1 | 0 | 24
38961.5357 | 1 | 0 | 24
38961.5362 | 1 | 0 | 24
38961.5367 | 1 | 0 | 24
38961.5372 | 1 | 0 | 24
38961.5377 | 1 | 0 | 24
38961.5381 | 1 | 0 | 24
38961.5386 | 1 | 0 | 24
38961.5391 | 1 | 0 | 24
38961.5396 | 1 | 0 | 24
38961.5401 | 1 | 0 | 24
38961.5406 | 1 | 0 | 24
38961.5411 | 1 | 0 | 24
38961.5415 | 4 | 0 | 24
38961.542 | 2089 | 0 | 24
38961.5425 | 2161 | 0 | 24
38961.543 | 2108 | 0 | 24
38961.5435 | 2305 | 0 | 24
38961.544 | 2221 | 0 | 24
38961.5445 | 2205 | 0 | 24
38961.5449 | 1982 | 0 | 24
38961.5454 | 2220 | 0 | 24
38961.5459 | 1887 | 0 | 24
38961.5464 | 2085 | 0 | 24
38961.5469 | 2049 | 0 | 24
38961.5474 | 1948 | 0 | 24
38961.5479 | 2332 | 0 | 24
38961.5483 | 2064 | 1 | 24
38961.5488 | 2277 | 0 | 24
38961.5493 | 1958 | 0 | 24
38961.5498 | 2346 | 0 | 24
38961.5503 | 2427 | 0 | 24
38961.5508 | 2026 | 0 | 24
38961.5513 | 1909 | 0 | 24
38961.5517 | 1970 | 0 | 24
38961.5522 | 2182 | 0 | 24
38961.5527 | 1917 | 0 | 24
38961.5532 | 1913 | 0 | 24
38961.5537 | 1962 | 0 | 24
38961.5542 | 2273 | 0 | 24
38961.5547 | 2036 | 0 | 24
38961.5552 | 1961 | 0 | 24
38961.5595 | 2081 | 0 | 24
38961.56 | 2383 | 0 | 24
38961.5605 | 2371 | 0 | 24
38961.561 | 2366 | 0 | 24
38961.5615 | 2001 | 0 | 24
38961.562 | 2104 | 0 | 24
38961.5625 | 2018 | 0 | 24
38961.5629 | 2396 | 0 | 24
24
38961.5207 | 1 | 0 | 25
38961.5211 | 1 | 0 | 25
38961.5216 | 1 | 0 | 25
38961.5221 | 1 | 0 | 25
38961.5226 | 1 | 0 | 25
38961.5231 | 1 | 0 | 25
38961.5236 | 1 | 0 | 25
38961.5241 | 1 | 0 | 25
38961.5245 | 1 | 0 | 25
38961.525 | 1 | 0 | 25
38961.5255 | 1 | 0 | 25
38961.526 | 1 | 0 | 25
38961.5265 | 1 | 0 | 25
38961.527 | 1 | 0 | 25
38961.5275 | 1 | 0 | 25
38961.528 | 1 | 0 | 25
38961.5284 | 1 | 0 | 25
38961.5289 | 1 | 0 | 25
38961.5294 | 1 | 0 | 25
38961.5299 | 1 | 0 | 25
38961.5304 | 1 | 0 | 25
38961.5309 | 1 | 0 | 25
38961.5314 | 1 | 0 | 25
38961.5318 | 1 | 0 | 25
38961.5323 | 1 | 0 | 25
38961.5328 | 1 | 0 | 25
38961.5333 | 1 | 0 | 25
38961.5338 | 1 | 0 | 25
38961.5343 | 1 | 0 | 25
38961.5348 | 1 | 0 | 25
38961.5352 | 1 | 0 | 25
38961.5357 | 1 | 0 | 25
38961.5362 | 1 | 0 | 25
38961.5367 | 1 | 0 | 25
38961.5372 | 1 | 0 | 25
38961.5377 | 1 | 0 | 25
38961.5382 | 1 | 0 | 25
38961.5386 | 1 | 0 | 25
38961.5391 | 1 | 0 | 25
38961.5396 | 1 | 0 | 25
38961.5401 | 1 | 0 | 25
38961.5406 | 1 | 0 | 25
38961.5411 | 1 | 0 | 25
38961.5416 | 1 | 0 | 25
38961.542 | 3 | 0 | 25
38961.5425 | 2 | 0 | 25
38961.543 | 2 | 0 | 25
38961.5435 | 2 | 0 | 25
38961.544 | 2 | 0 | 25
38961.5445 | 2 | 0 | 25
38961.545 | 3 | 0 | 25
38961.5455 | 2 | 0 | 25
38961.5459 | 656 | 0 | 25
38961.5464 | 2 | 0 | 25
38961.5469 | 2 | 0 | 25
38961.5474 | 2 | 0 | 25
38961.5479 | 2 | 0 | 25
38961.5484 | 2 | 0 | 25
38961.5489 | 1543 | 0 | 25
38961.5493 | 2150 | 0 | 25
38961.5498 | 1853 | 0 | 25
38961.5503 | 1717 | 0 | 25
38961.5508 | 261 | 0 | 25
38961.5513 | 43 | 0 | 25
38961.5518 | 103 | 0 | 25
38961.5523 | 642 | 0 | 25
38961.5527 | 264 | 0 | 25
38961.5532 | 400 | 0 | 25
38961.5537 | 541 | 0 | 25
38961.5542 | 575 | 0 | 25
38961.5547 | 669 | 0 | 25
38961.5552 | 679 | 0 | 25
38961.5595 | 153 | 0 | 25
38961.56 | 58 | 0 | 25
38961.5605 | 35 | 0 | 25
38961.561 | 25 | 0 | 25
38961.5615 | 17 | 0 | 25
38961.562 | 12 | 0 | 25
38961.5625 | 5 | 0 | 25
38961.563 | 4 | 0 | 25
25
38961.5207 | 1 | 0 | 26
38961.5212 | 1 | 0 | 26
38961.5216 | 1 | 0 | 26
38961.5221 | 1 | 0 | 26
38961.5226 | 1 | 0 | 26
38961.5231 | 1 | 0 | 26
38961.5236 | 1 | 0 | 26
38961.5241 | 1 | 0 | 26
38961.5246 | 1 | 0 | 26
38961.525 | 1 | 0 | 26
38961.5255 | 1 | 0 | 26
38961.526 | 1 | 0 | 26
38961.5265 | 1 | 0 | 26
38961.527 | 1 | 0 | 26
38961.5275 | 1 | 0 | 26
38961.528 | 1 | 0 | 26
38961.5284 | 1 | 0 | 26
38961.5289 | 1 | 0 | 26
38961.5294 | 1 | 0 | 26
38961.5299 | 1 | 0 | 26
38961.5304 | 1 | 0 | 26
38961.5309 | 1 | 0 | 26
38961.5314 | 1 | 0 | 26
38961.5319 | 1 | 0 | 26
38961.5323 | 1 | 0 | 26
38961.5328 | 1 | 0 | 26
38961.5333 | 1 | 0 | 26
38961.5338 | 1 | 0 | 26
38961.5343 | 1 | 0 | 26
38961.5348 | 1 | 0 | 26
38961.5353 | 1 | 0 | 26
38961.5357 | 1 | 0 | 26
38961.5362 | 1 | 0 | 26
38961.5367 | 1 | 0 | 26
38961.5372 | 1 | 0 | 26
38961.5377 | 1 | 0 | 26
38961.5382 | 1 | 0 | 26
38961.5387 | 1 | 0 | 26
38961.5391 | 1 | 0 | 26
38961.5396 | 1 | 0 | 26
38961.5401 | 1 | 0 | 26
38961.5406 | 1 | 0 | 26
38961.5411 | 1 | 0 | 26
38961.5416 | 1992 | 0 | 26
38961.5421 | 1701 | 0 | 26
38961.5425 | 1850 | 0 | 26
38961.543 | 1848 | 0 | 26
38961.5435 | 2148 | 0 | 26
38961.544 | 1919 | 0 | 26
38961.5445 | 1905 | 1 | 26
38961.545 | 2398 | 0 | 26
38961.5455 | 2411 | 0 | 26
38961.5459 | 2388 | 0 | 26
38961.5464 | 2135 | 0 | 26
38961.5469 | 2302 | 1 | 26
38961.5474 | 2142 | 0 | 26
38961.5479 | 2137 | 0 | 26
38961.5484 | 2078 | 0 | 26
38961.5489 | 1927 | 0 | 26
38961.5494 | 2409 | 0 | 26
38961.5498 | 2409 | 0 | 26
38961.5503 | 2079 | 0 | 26
38961.5508 | 1915 | 0 | 26
38961.5513 | 2032 | 0 | 26
38961.5518 | 2182 | 0 | 26
38961.5523 | 1962 | 0 | 26
38961.5528 | 2312 | 0 | 26
38961.5532 | 2436 | 0 | 26
38961.5537 | 1931 | 0 | 26
38961.5542 | 2293 | 0 | 26
38961.5547 | 2083 | 0 | 26
38961.5552 | 2096 | 0 | 26
38961.5596 | 2410 | 0 | 26
38961.5601 | 1973 | 0 | 26
38961.5605 | 2203 | 0 | 26
38961.561 | 2371 | 0 | 26
38961.5615 | 1940 | 0 | 26
38961.562 | 2301 | 0 | 26
38961.5625 | 2319 | 0 | 26
38961.563 | 2324 | 0 | 26
26
38961.5207 | 1 | 0 | 27
38961.5212 | 1 | 0 | 27
38961.5217 | 1 | 0 | 27
38961.5222 | 1 | 0 | 27
38961.5226 | 1 | 0 | 27
38961.5231 | 1 | 0 | 27
38961.5236 | 1 | 0 | 27
38961.5241 | 1 | 1 | 27
38961.5246 | 1 | 0 | 27
38961.5251 | 1 | 0 | 27
38961.5256 | 1 | 0 | 27
38961.526 | 1 | 0 | 27
38961.5265 | 1 | 0 | 27
38961.527 | 1 | 0 | 27
38961.5275 | 1 | 0 | 27
38961.528 | 1 | 0 | 27
38961.5285 | 1 | 0 | 27
38961.529 | 1 | 0 | 27
38961.5294 | 1 | 0 | 27
38961.5299 | 1 | 0 | 27
38961.5304 | 1 | 0 | 27
38961.5309 | 1 | 0 | 27
38961.5314 | 1 | 0 | 27
38961.5319 | 1 | 0 | 27
38961.5324 | 1 | 0 | 27
38961.5328 | 1 | 0 | 27
38961.5333 | 1 | 0 | 27
38961.5338 | 1 | 0 | 27
38961.5343 | 1 | 0 | 27
38961.5348 | 1 | 0 | 27
38961.5353 | 1 | 0 | 27
38961.5358 | 1 | 0 | 27
38961.5362 | 1 | 0 | 27
38961.5367 | 1 | 0 | 27
38961.5372 | 1 | 0 | 27
38961.5377 | 1 | 0 | 27
38961.5382 | 1 | 0 | 27
38961.5387 | 1 | 0 | 27
38961.5392 | 1 | 0 | 27
38961.5397 | 1 | 0 | 27
38961.5401 | 1 | 0 | 27
38961.5406 | 1 | 0 | 27
38961.5411 | 1 | 0 | 27
38961.5416 | 2 | 0 | 27
38961.5421 | 2 | 0 | 27
38961.5426 | 2 | 0 | 27
38961.5431 | 2 | 0 | 27
38961.5435 | 2 | 0 | 27
38961.544 | 2 | 0 | 27
38961.5445 | 3 | 0 | 27
38961.545 | 256 | 0 | 27
38961.5455 | 2 | 0 | 27
38961.546 | 4 | 0 | 27
38961.5465 | 2 | 0 | 27
38961.5469 | 2 | 0 | 27
38961.5474 | 2 | 0 | 27
38961.5479 | 2 | 0 | 27
38961.5484 | 2 | 0 | 27
38961.5489 | 2014 | 0 | 27
38961.5494 | 2378 | 0 | 27
38961.5498 | 1915 | 0 | 27
38961.5503 | 1776 | 0 | 27
38961.5508 | 509 | 0 | 27
38961.5513 | 41 | 0 | 27
38961.5518 | 105 | 0 | 27
38961.5523 | 1192 | 0 | 27
38961.5528 | 1407 | 0 | 27
38961.5533 | 558 | 0 | 27
38961.5537 | 667 | 0 | 27
38961.5542 | 714 | 0 | 27
38961.5547 | 620 | 0 | 27
38961.5552 | 623 | 0 | 27
38961.5596 | 193 | 0 | 27
38961.5601 | 65 | 0 | 27
38961.5606 | 44 | 0 | 27
38961.561 | 32 | 0 | 27
38961.5615 | 24 | 0 | 27
38961.562 | 15 | 0 | 27
38961.5625 | 6 | 0 | 27
38961.563 | 4 | 0 | 27
27
38961.5207 | 1 | 0 | 28
38961.5212 | 1 | 0 | 28
38961.5217 | 1 | 0 | 28
38961.5222 | 1 | 0 | 28
38961.5227 | 1 | 0 | 28
38961.5231 | 1 | 0 | 28
38961.5236 | 1 | 0 | 28
38961.5241 | 1 | 0 | 28
38961.5246 | 1 | 0 | 28
38961.5251 | 1 | 0 | 28
38961.5256 | 1 | 0 | 28
38961.5261 | 1 | 0 | 28
38961.5265 | 1 | 0 | 28
38961.527 | 1 | 0 | 28
38961.5275 | 1 | 0 | 28
38961.528 | 1 | 0 | 28
38961.5285 | 1 | 0 | 28
38961.529 | 1 | 0 | 28
38961.5295 | 1 | 0 | 28
38961.5299 | 1 | 0 | 28
38961.5304 | 1 | 0 | 28
38961.5309 | 1 | 0 | 28
38961.5314 | 1 | 0 | 28
38961.5319 | 1 | 0 | 28
38961.5324 | 1 | 0 | 28
38961.5329 | 1 | 0 | 28
38961.5333 | 1 | 0 | 28
38961.5338 | 1 | 0 | 28
38961.5343 | 1 | 0 | 28
38961.5348 | 1 | 0 | 28
38961.5353 | 1 | 0 | 28
38961.5358 | 1 | 0 | 28
38961.5363 | 1 | 0 | 28
38961.5367 | 1 | 0 | 28
38961.5372 | 1 | 0 | 28
38961.5377 | 1 | 0 | 28
38961.5382 | 1 | 0 | 28
38961.5387 | 1 | 0 | 28
38961.5392 | 1 | 0 | 28
38961.5397 | 1 | 0 | 28
38961.5402 | 1 | 0 | 28
38961.5406 | 1 | 0 | 28
38961.5411 | 1 | 0 | 28
38961.5416 | 1811 | 0 | 28
38961.5421 | 2162 | 0 | 28
38961.5426 | 1889 | 0 | 28
38961.5431 | 1859 | 0 | 28
38961.5436 | 2346 | 0 | 28
38961.544 | 2106 | 0 | 28
38961.5445 | 2377 | 0 | 28
38961.545 | 2068 | 0 | 28
38961.5455 | 1981 | 0 | 28
38961.546 | 1953 | 0 | 28
38961.5465 | 2034 | 0 | 28
38961.547 | 2081 | 0 | 28
38961.5474 | 2134 | 0 | 28
38961.5479 | 2438 | 0 | 28
38961.5484 | 2433 | 0 | 28
38961.5489 | 2466 | 0 | 28
38961.5494 | 1916 | 0 | 28
38961.5499 | 2455 | 0 | 28
38961.5504 | 1916 | 1 | 28
38961.5508 | 1988 | 0 | 28
38961.5513 | 2177 | 0 | 28
38961.5518 | 1946 | 0 | 28
38961.5523 | 1938 | 0 | 28
38961.5528 | 2159 | 0 | 28
38961.5533 | 2452 | 0 | 28
38961.5538 | 1878 | 0 | 28
38961.5542 | 1880 | 0 | 28
38961.5547 | 2119 | 0 | 28
38961.5552 | 1973 | 0 | 28
38961.5596 | 2209 | 0 | 28
38961.5601 | 2068 | 0 | 28
38961.5606 | 2104 | 0 | 28
38961.5611 | 2415 | 0 | 28
38961.5616 | 2014 | 0 | 28
38961.562 | 2027 | 0 | 28
38961.5625 | 2218 | 0 | 28
38961.563 | 2392 | 0 | 28
28
38961.5207 | 1 | 0 | 29
38961.5212 | 1 | 0 | 29
38961.5217 | 1 | 0 | 29
38961.5222 | 1 | 0 | 29
38961.5227 | 1 | 0 | 29
38961.5232 | 1 | 0 | 29
38961.5236 | 1 | 0 | 29
38961.5241 | 1 | 0 | 29
38961.5246 | 1 | 0 | 29
38961.5251 | 1 | 0 | 29
38961.5256 | 1 | 1 | 29
38961.5261 | 1 | 0 | 29
38961.5266 | 1 | 0 | 29
38961.527 | 1 | 0 | 29
38961.5275 | 1 | 0 | 29
38961.528 | 1 | 0 | 29
38961.5285 | 1 | 0 | 29
38961.529 | 1 | 0 | 29
38961.5295 | 1 | 0 | 29
38961.53 | 1 | 0 | 29
38961.5305 | 1 | 0 | 29
38961.5309 | 1 | 0 | 29
38961.5314 | 1 | 0 | 29
38961.5319 | 1 | 0 | 29
38961.5324 | 1 | 0 | 29
38961.5329 | 1 | 0 | 29
38961.5334 | 1 | 0 | 29
38961.5338 | 1 | 0 | 29
38961.5343 | 1 | 0 | 29
38961.5348 | 1 | 0 | 29
38961.5353 | 1 | 0 | 29
38961.5358 | 1 | 0 | 29
38961.5363 | 1 | 0 | 29
38961.5368 | 1 | 0 | 29
38961.5372 | 1 | 0 | 29
38961.5377 | 1 | 0 | 29
38961.5382 | 1 | 0 | 29
38961.5387 | 1 | 0 | 29
38961.5392 | 1 | 0 | 29
38961.5397 | 1 | 0 | 29
38961.5402 | 1 | 0 | 29
38961.5406 | 1 | 0 | 29
38961.5411 | 1 | 0 | 29
38961.5416 | 1942 | 0 | 29
38961.5421 | 1959 | 0 | 29
38961.5426 | 2048 | 25 | 29
38961.5431 | 2080 | 43 | 29
38961.5436 | 1917 | 18 | 29
38961.5441 | 2262 | 13 | 29
38961.5445 | 1912 | 7 | 29
38961.545 | 2268 | 7 | 29
38961.5455 | 2203 | 6 | 29
38961.546 | 2351 | 4 | 29
38961.5465 | 2332 | 3 | 29
38961.547 | 1984 | 3 | 29
38961.5475 | 2333 | 2 | 29
38961.5479 | 2224 | 2 | 29
38961.5484 | 2112 | 2 | 29
38961.5489 | 2196 | 3 | 29
38961.5494 | 2446 | 2 | 29
38961.5499 | 2053 | 2 | 29
38961.5504 | 1972 | 2 | 29
38961.5509 | 2292 | 2 | 29
38961.5513 | 1997 | 1 | 29
38961.5518 | 2120 | 2 | 29
38961.5523 | 2067 | 1 | 29
38961.5528 | 2117 | 1 | 29
38961.5533 | 2454 | 1 | 29
38961.5538 | 2472 | 1 | 29
38961.5543 | 2028 | 1 | 29
38961.5547 | 2014 | 1 | 29
38961.5552 | 1925 | 1 | 29
38961.5596 | 2188 | 2 | 29
38961.5601 | 2435 | 1 | 29
38961.5606 | 2220 | 1 | 29
38961.5611 | 2423 | 2 | 29
38961.5616 | 1900 | 1 | 29
38961.562 | 2230 | 1 | 29
38961.5625 | 1993 | 1 | 29
38961.563 | 2459 | 1 | 29
29
38961.5207 | 1 | 0 | 30
38961.5212 | 1 | 0 | 30
38961.5217 | 1 | 0 | 30
38961.5222 | 1 | 0 | 30
38961.5227 | 1 | 0 | 30
38961.5232 | 1 | 0 | 30
38961.5237 | 1 | 0 | 30
38961.5241 | 1 | 0 | 30
38961.5246 | 1 | 0 | 30
38961.5251 | 1 | 0 | 30
38961.5256 | 1 | 0 | 30
38961.5261 | 1 | 0 | 30
38961.5266 | 1 | 0 | 30
38961.5271 | 1 | 0 | 30
38961.5275 | 1 | 0 | 30
38961.528 | 1 | 0 | 30
38961.5285 | 1 | 0 | 30
38961.529 | 1 | 0 | 30
38961.5295 | 1 | 0 | 30
38961.53 | 1 | 0 | 30
38961.5305 | 1 | 0 | 30
38961.5309 | 1 | 0 | 30
38961.5314 | 1 | 0 | 30
38961.5319 | 1 | 0 | 30
38961.5324 | 1 | 0 | 30
38961.5329 | 1 | 0 | 30
38961.5334 | 1 | 0 | 30
38961.5339 | 1 | 0 | 30
38961.5344 | 1 | 0 | 30
38961.5348 | 1 | 0 | 30
38961.5353 | 1 | 0 | 30
38961.5358 | 1 | 0 | 30
38961.5363 | 1 | 0 | 30
38961.5368 | 1 | 0 | 30
38961.5373 | 1 | 0 | 30
38961.5378 | 1 | 0 | 30
38961.5382 | 1 | 0 | 30
38961.5387 | 1 | 0 | 30
38961.5392 | 1 | 0 | 30
38961.5397 | 1 | 0 | 30
38961.5402 | 1 | 0 | 30
38961.5407 | 1 | 0 | 30
38961.5412 | 1 | 0 | 30
38961.5416 | 1828 | 0 | 30
38961.5421 | 2085 | 0 | 30
38961.5426 | 2243 | 30 | 30
38961.5431 | 1850 | 30 | 30
38961.5436 | 2344 | 22 | 30
38961.5441 | 2323 | 12 | 30
38961.5446 | 2047 | 7 | 30
38961.545 | 2361 | 7 | 30
38961.5455 | 2380 | 6 | 30
38961.546 | 2406 | 4 | 30
38961.5465 | 2172 | 5 | 30
38961.547 | 2235 | 3 | 30
38961.5475 | 2302 | 3 | 30
38961.548 | 2279 | 3 | 30
38961.5484 | 2454 | 2 | 30
38961.5489 | 2129 | 2 | 30
38961.5494 | 2441 | 2 | 30
38961.5499 | 2149 | 3 | 30
38961.5504 | 2168 | 2 | 30
38961.5509 | 2068 | 1 | 30
38961.5514 | 2249 | 2 | 30
38961.5519 | 2026 | 1 | 30
38961.5523 | 2363 | 1 | 30
38961.5528 | 1954 | 1 | 30
38961.5533 | 2092 | 1 | 30
38961.5538 | 1899 | 1 | 30
38961.5543 | 2279 | 1 | 30
38961.5548 | 2379 | 1 | 30
38961.5553 | 2354 | 1 | 30
38961.5596 | 2099 | 1 | 30
38961.5601 | 2080 | 1 | 30
38961.5606 | 2103 | 1 | 30
38961.5611 | 2282 | 1 | 30
38961.5616 | 2415 | 1 | 30
38961.5621 | 1991 | 1 | 30
38961.5625 | 1871 | 1 | 30
38961.563 | 2405 | 2 | 30
30

## Test Facts
Last row in IRMS data sheets: | 85
Time when Penlight power was initiated: | 98