## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 68
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, mixture of PE, XLPE, XLPO, EPR, Vita-Link & TS/TP insulated control cables (Items 15, 10, 8, 2, 11 & 3). Cable specimens present: Six lengths of cable were monitored for electrical performance, 1 each of PE, XLPE, XLPO, EPR, Vita-Link & TS/TP. A seventh length of cable (Vita-Link cable Item #11) was monitored for temperature response. No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 162 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
162 | 0 | Initated Penlight Heating
1252 | 1090 | Conductors D7 & D8 short together at less than 100 ohms (30) | EPR Cable D shorts internally
1267-1269 | 1105-1107 | Conductors F11 & F12 short to ground at less than 1000 ohms (730 & 719) | TS/TP Cable F shorts to ground
1292-1294 | 1130-1132 | Conductors F11 & F12 short together at less than 100 ohms (17); conductors A1 & A2 short together at less than 100 ohms (1) | PE Cable A and TS/TP Cable F short internally
1300-1322 | 1138-1160 | Conductors A1 & A2 both short to ground at less than 1000 ohms (99 & 107) | PE Cable A shorts to ground intermittently
1437 | 1275 | Cables ignite and burn
1452-1454 | 1290-1292 | The existing ground fault on Conductors F11 & F12 decrease to less than 100 ohms (4 & 5) | TS/TP Cable F shorts to ground intermittently
1460 | 1298 | Power to Penlight is shutoff
1538 | 1376 | Conductors B3 & B4 short together at less than 100 ohms (10) | XLPE Cable B shorts internally
1586 | 1424 | Conductors C5 & C6 short together at less than 100 ohms (25) | XLPO Cable C shorts internally
1598-1603 | 1436-1441 | Conductors D7 & D8 short to ground at much less than 100 ohms (<1 & <1) | EPR Cable D shorts to ground
1720-1735 | 1558-1573 | Conductors B3 & B4 short to ground at less than 1000 ohms (143 & 165) | XLPE Cable B shorts to ground intermittently
2304-2313 | 2142-2151 | Conductors C5 & C6 short to ground at less than 100 ohms (2 & 2) | XLPO Cable C shorted to ground
Additional Observations
Observation 1 | The Vita-Link cable (E) did not fail either internally or externally.
Observation 2 | It took 1090 s (18.2 min.) from the start of Penlight heating for the first internal short to occur, 1105 s (18.4 min.) for the first short to ground, and 1275 s (21.3 min.) for the cable bundle to ignite.
Observation 3 | No cable to cable interactions took place during this test.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A = PE Cable, Item #15
B = XLPE Cable, Item #10
C = XLPO Cable, Item #8
D = EPR Cable, Item #2
E = Vita-Link Cable, Item #11
F = TS/TP Cable, Item #3
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 68 |  |  | 2006-08-23 | 15:05
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-161.5 | 211201.9994 | -158.5 | 211201.9994 | -155.5 | 211201.9994 | -153 | 211201.9994 | -150 | 211201.9994 | -130.5 | 211201.9994 | -127.5 | 211201.9994 | -125 | 211201.9994 | -122 | 211201.9994 | -102.5 | 211201.9994 | -99.5 | 211201.9994 | -97 | 211201.9994 | -94 | 251037.9994 | -91.5 | 223237.9994 | -88.5 | 211201.9994 | -85.5 | 211201.9994 | -77.5 | 211201.9994 | -74.5 | 211201.9994 | -71.5 | 240937.9994 | -69 | 239137.9994 | -66 | 211201.9994 | -63.5 | 211201.9994 | -55 | 211201.9994 | -46.5 | 211201.9994 | -43.5 | 211201.9994 | -41 | 211201.9994 | -38 | 240737.9994 | -29.5 | 211201.9994 | -27 | 211201.9994 | -24 | 227837.9994 | -21.5 | 211201.9994 | -18.5 | 242537.9994 | -15.5 | 247537.9994 | -13 | 246437.9994 | -4.5 | 236237.9994 | -1.5 | 232737.9994 | 6.5 | 211201.9994 | 9.5 | 248537.9994 | 12.5 | 218837.9994 | 15 | 215837.9994 | 18 | 211201.9994 | 20.5 | 234337.9994 | -143 | 211201.9994 | -137.5 | 211201.9994 | -87.125 | 211201.9994 | -81.5 | 223237.9994 | -75.875 | 211201.9994 | -36.625 | 211201.9994 | -31.125 | 211201.9994 | -8.625 | 232737.9994 | 13.75 | 211201.9994
23.5 | 211201.9994 | 26.5 | 211201.9994 | 29 | 211201.9994 | 32 | 211201.9994 | 34.5 | 211201.9994 | 54.5 | 211201.9994 | 57 | 211201.9994 | 60 | 211201.9994 | 62.5 | 211201.9994 | 82.5 | 211201.9994 | 85 | 211201.9994 | 88 | 211201.9994 | 90.5 | 251037.9994 | 93.5 | 223237.9994 | 96.5 | 211201.9994 | 99 | 211201.9994 | 107.5 | 211201.9994 | 110.5 | 211201.9994 | 113 | 240937.9994 | 116 | 239137.9994 | 118.5 | 211201.9994 | 121.5 | 211201.9994 | 130 | 211201.9994 | 138.5 | 211201.9994 | 141 | 211201.9994 | 143.5 | 211201.9994 | 146.5 | 240737.9994 | 155 | 211201.9994 | 158 | 211201.9994 | 160.5 | 227837.9994 | 163.5 | 211201.9994 | 166.5 | 242537.9994 | 169 | 247537.9994 | 171.5 | 246437.9994 | 180.5 | 236237.9994 | 183 | 232737.9994 | 191.5 | 211201.9994 | 194.5 | 248537.9994 | 197 | 218837.9994 | 200 | 215837.9994 | 202.5 | 211201.9994 | 205.5 | 234337.9994 | 41.75 | 211201.9994 | 47.25 | 211201.9994 | 97.75 | 211201.9994 | 103.25 | 223237.9994 | 108.875 | 211201.9994 | 148.125 | 211201.9994 | 153.5 | 211201.9994 | 176 | 232737.9994 | 198.5 | 211201.9994
208 | 211201.9994 | 211 | 211201.9994 | 214 | 211201.9994 | 216.5 | 211201.9994 | 219.5 | 211201.9994 | 239 | 211201.9994 | 242 | 211201.9994 | 244.5 | 211201.9994 | 247.5 | 211201.9994 | 267 | 211201.9994 | 269.5 | 211201.9994 | 272.5 | 211201.9994 | 275.5 | 251037.9994 | 278 | 223237.9994 | 281 | 211201.9994 | 284 | 105550.9988 | 292.5 | 211201.9994 | 295 | 211201.9994 | 297.5 | 240937.9994 | 300.5 | 239137.9994 | 303.5 | 211201.9994 | 306 | 211201.9994 | 314.5 | 211201.9994 | 323 | 211201.9994 | 326 | 211201.9994 | 328.5 | 211201.9994 | 331.5 | 240737.9994 | 339.5 | 211201.9994 | 342.5 | 211201.9994 | 345.5 | 227837.9994 | 348.5 | 211201.9994 | 351 | 242537.9994 | 353.5 | 247537.9994 | 356.5 | 246437.9994 | 365 | 236237.9994 | 367.5 | 232737.9994 | 376.5 | 211201.9994 | 379 | 248537.9994 | 382 | 218837.9994 | 384.5 | 215837.9994 | 387.5 | 211201.9994 | 390.5 | 234337.9994 | 226.5 | 211201.9994 | 232 | 211201.9994 | 282.375 | 211201.9994 | 287.875 | 223237.9994 | 293.625 | 105550.9988 | 332.75 | 211201.9994 | 338.5 | 211201.9994 | 360.625 | 232737.9994 | 383.25 | 211201.9994
393 | 211201.9994 | 396 | 211201.9994 | 398.5 | 211201.9994 | 401.5 | 211201.9994 | 404 | 211201.9994 | 424 | 211201.9994 | 426.5 | 211201.9994 | 429.5 | 105550.9988 | 432.5 | 211201.9994 | 452 | 211201.9994 | 454.5 | 211201.9994 | 457.5 | 211201.9994 | 460 | 251037.9994 | 463 | 223237.9994 | 465.5 | 211201.9994 | 468.5 | 211201.9994 | 477 | 211201.9994 | 479.5 | 211201.9994 | 482.5 | 240937.9994 | 485.5 | 239137.9994 | 488 | 211201.9994 | 491 | 211201.9994 | 499.5 | 211201.9994 | 507.5 | 211201.9994 | 510.5 | 211201.9994 | 513.5 | 211201.9994 | 516 | 240737.9994 | 524.5 | 211201.9994 | 527.5 | 211201.9994 | 530 | 227837.9994 | 533 | 211201.9994 | 535.5 | 242537.9994 | 538.5 | 247537.9994 | 541.5 | 246437.9994 | 550 | 236237.9994 | 552.5 | 232737.9994 | 561 | 211201.9994 | 564 | 248537.9994 | 566.5 | 218837.9994 | 569.5 | 215837.9994 | 572.5 | 211201.9994 | 575 | 234337.9994 | 411.25 | 211201.9994 | 416.875 | 105550.9988 | 467.125 | 211201.9994 | 472.75 | 223237.9994 | 478.25 | 211201.9994 | 517.5 | 211201.9994 | 523.125 | 211201.9994 | 545.625 | 232737.9994 | 568.125 | 211201.9994
578 | 211201.9994 | 580.5 | 211201.9994 | 583.5 | 211201.9994 | 586.5 | 211201.9994 | 589 | 211201.9994 | 608.5 | 211201.9994 | 611.5 | 211201.9994 | 614 | 211201.9994 | 617 | 211201.9994 | 636.5 | 211201.9994 | 639.5 | 211201.9994 | 642 | 211201.9994 | 645 | 251037.9994 | 647.5 | 223237.9994 | 650.5 | 211201.9994 | 653.5 | 211201.9994 | 661.5 | 211201.9994 | 664.5 | 211201.9994 | 667.5 | 240937.9994 | 670.5 | 239137.9994 | 673 | 211201.9994 | 675.5 | 211201.9994 | 684.5 | 211201.9994 | 692.5 | 211201.9994 | 695.5 | 211201.9994 | 698.5 | 211201.9994 | 701 | 240737.9994 | 709.5 | 211201.9994 | 712.5 | 211201.9994 | 715 | 227837.9994 | 718 | 211201.9994 | 720.5 | 242537.9994 | 723.5 | 247537.9994 | 726 | 246437.9994 | 734.5 | 236237.9994 | 737.5 | 232737.9994 | 746 | 211201.9994 | 748.5 | 248537.9994 | 751.5 | 218837.9994 | 754.5 | 215837.9994 | 757 | 211201.9994 | 759.5 | 234337.9994 | 596 | 211201.9994 | 601.625 | 211201.9994 | 651.875 | 211201.9994 | 657.625 | 223237.9994 | 663.125 | 211201.9994 | 702.5 | 211201.9994 | 708.125 | 211201.9994 | 730.375 | 232737.9994 | 752.875 | 211201.9994
762.5 | 211201.9994 | 765.5 | 211201.9994 | 768.5 | 211201.9994 | 771 | 211201.9994 | 773.5 | 211201.9994 | 793.5 | 211201.9994 | 796 | 211201.9994 | 799 | 211201.9994 | 801.5 | 211201.9994 | 821.5 | 211201.9994 | 824 | 211201.9994 | 827 | 211201.9994 | 829.5 | 251037.9994 | 832.5 | 223237.9994 | 835.5 | 211201.9994 | 838 | 211201.9994 | 846.5 | 211201.9994 | 849.5 | 211201.9994 | 852 | 240937.9994 | 855 | 239137.9994 | 857.5 | 211201.9994 | 860.5 | 211201.9994 | 869 | 211201.9994 | 877.5 | 211201.9994 | 880 | 211201.9994 | 883 | 211201.9994 | 886 | 240737.9994 | 894 | 211201.9994 | 897 | 211201.9994 | 899.5 | 227837.9994 | 902.5 | 211201.9994 | 905.5 | 242537.9994 | 908 | 247537.9994 | 911 | 246437.9994 | 919.5 | 236237.9994 | 922 | 232737.9994 | 930.5 | 211201.9994 | 933.5 | 248537.9994 | 936 | 218837.9994 | 939 | 215837.9994 | 941.5 | 211201.9994 | 944.5 | 234337.9994 | 780.875 | 211201.9994 | 786.25 | 211201.9994 | 836.75 | 211201.9994 | 842.25 | 223237.9994 | 847.875 | 211201.9994 | 887.125 | 211201.9994 | 892.75 | 211201.9994 | 915.125 | 232737.9994 | 937.5 | 211201.9994
947.5 | 211201.9994 | 950 | 211201.9994 | 953 | 211201.9994 | 955.5 | 211201.9994 | 958.5 | 211201.9994 | 978 | 211201.9994 | 981 | 211201.9994 | 983.5 | 211201.9994 | 986.5 | 211201.9994 | 1006 | 211201.9994 | 1009 | 211201.9994 | 1011.5 | 211201.9994 | 1014.5 | 251037.9994 | 1017.5 | 223237.9994 | 1020 | 211201.9994 | 1023 | 211201.9994 | 1031.5 | 211201.9994 | 1034 | 211201.9994 | 1037 | 240937.9994 | 1039.5 | 239137.9994 | 1042.5 | 211201.9994 | 1045.5 | 211201.9994 | 1053.5 | 211201.9994 | 1062 | 211201.9994 | 1065 | 211201.9994 | 1067.5 | 211201.9994 | 1070.5 | 240737.9994 | 1079 | 211201.9994 | 1081.5 | 211201.9994 | 1084.5 | 227837.9994 | 1087.5 | 211201.9994 | 1090 | 29.949 | 1093 | 61734.5807 | 1095.5 | 246238.0811 | 1104 | 236237.9994 | 1107 | 232737.9994 | 1115.5 | 211002.0947 | 1118 | 248537.9994 | 1121 | 218837.9994 | 1123.5 | 215837.9994 | 1126.5 | 211201.9994 | 1129.5 | 16.5119 | 965.5 | 211201.9994 | 971 | 211201.9994 | 1021.5 | 211201.9994 | 1027.125 | 223237.9994 | 1032.75 | 211201.9994 | 1071.875 | 211201.9994 | 1077.5 | 211201.9994 | 1099.875 | 61734.5807 | 1122.25 | 211201.9994
1132 | 1.2732 | 1135 | 42100.5417 | 1137.5 | 105401.071 | 1140.5 | 211001.9527 | 1143.5 | 211002.0947 | 1163 | 105550.9988 | 1165.5 | 211002.0947 | 1168.5 | 211201.9994 | 1171.5 | 211201.9994 | 1191 | 70333.9982 | 1193.5 | 105550.9988 | 1196.5 | 105550.9988 | 1199.5 | 251037.9994 | 1202 | 223237.9994 | 1205 | 211201.9994 | 1207.5 | 211201.9994 | 1216 | 70333.9982 | 1219 | 105550.9988 | 1221.5 | 120418.9988 | 1224.5 | 239137.9994 | 1227.5 | 211201.9994 | 1230 | 211201.9994 | 1238.5 | 70333.9982 | 1247 | 105550.9988 | 1249.5 | 211201.9994 | 1252.5 | 211201.9994 | 1255.5 | 80179.3315 | 1263.5 | 211201.9994 | 1266.5 | 211201.9994 | 1269.5 | 227837.9994 | 1271 | 70333.9982 | 1275 | 71.0713 | 1277.5 | 61659.5909 | 1280.5 | 245938.3245 | 1289 | 235438.5924 | 1291.5 | 231938.3436 | 1300 | 70333.9982 | 1303 | 124218.9988 | 1305.5 | 109368.9988 | 1308.5 | 71879.3315 | 1311.5 | 70333.9982 | 1314 | 2.8959 | 1150.25 | 42100.5417 | 1156 | 211001.9527 | 1206.25 | 70333.9982 | 1211.875 | 120418.9988 | 1217.5 | 211201.9994 | 1256.625 | 105550.9988 | 1262.125 | 70333.9982 | 1284.625 | 61659.5909 | 1307.125 | 70333.9982
1317 | 21.0445 | 1319.5 | 42080.5229 | 1322.5 | 105351.1183 | 1325.5 | 210802.284 | 1328 | 105550.9988 | 1347.5 | 70333.9982 | 1350.5 | 105550.9988 | 1353.5 | 105550.9988 | 1356 | 105550.9988 | 1375.5 | 9.6611 | 1378.5 | 52650.4764 | 1381.5 | 210902.142 | 1384 | 125468.9988 | 1387 | 74345.9982 | 1389.5 | 70333.9982 | 1392.5 | 105550.9988 | 1401 | 70333.9982 | 1403.5 | 105550.9988 | 1406.5 | 120418.9988 | 1409 | 79645.9982 | 1412 | 70333.9982 | 1414.5 | 105550.9988 | 1423.5 | 24.6231 | 1431.5 | 70333.9982 | 1434.5 | 105550.9988 | 1437.5 | 105550.9988 | 1440 | 80179.3315 | 1448.5 | 70333.9982 | 1451.5 | 105550.9988 | 1454 | 113868.9988 | 1457 | 70333.9982 | 1459.5 | 0.79164 | 1462.5 | 34795.7957 | 1465.5 | 23309.6011 | 1473.5 | 20711.6758 | 1476.5 | 17315.6609 | 1485 | 52725.4976 | 1487.5 | 82779.3315 | 1490.5 | 72879.3315 | 1493 | 71879.3315 | 1496 | 70333.9982 | 1499 | 68.7913 | 1335 | 42080.5229 | 1340.75 | 105550.9988 | 1391.125 | 52650.4764 | 1396.625 | 74345.9982 | 1402.125 | 70333.9982 | 1441.5 | 70333.9982 | 1447.125 | 70333.9982 | 1469.5 | 17315.6609 | 1491.75 | 70333.9982
1501.5 | 22.2229 | 1504.5 | 52650.5946 | 1507.5 | 210802.2366 | 1510 | 210502.7572 | 1513 | 105550.9988 | 1532.5 | 70333.9982 | 1535.5 | 70333.9982 | 1538 | 105550.9988 | 1541 | 105550.9988 | 1560.5 | 6.6211 | 1563.5 | 52625.5828 | 1566 | 210802.2366 | 1569 | 83612.6648 | 1571.5 | 74345.9982 | 1574.5 | 52725.4976 | 1577.5 | 70333.9982 | 1585.5 | 42160.3969 | 1588.5 | 35116.9963 | 1591.5 | 34333.9957 | 1594 | 29804.7451 | 1597 | 210102.9465 | 1599.5 | 210003.0412 | 1608 | 2.3961 | 1616.5 | 70333.9982 | 1619 | 105550.9988 | 1622 | 105550.9988 | 1625 | 80179.3315 | 1633.5 | 105550.9988 | 1636 | 70333.9982 | 1639 | 113868.9988 | 1641.5 | 70333.9982 | 1644.5 | 19.0651 | 1647.5 | 1536.1368 | 1650 | 41687.2111 | 1658.5 | 59662.1705 | 1661.5 | 50594.5037 | 1669.5 | 70333.9982 | 1672.5 | 124218.9988 | 1675 | 72879.3315 | 1678 | 71879.3315 | 1680.5 | 70333.9982 | 1683.5 | 0.71764 | 1520 | 52650.5946 | 1525.5 | 105550.9988 | 1575.875 | 35116.9963 | 1581.5 | 29804.7451 | 1587.125 | 52725.4976 | 1626.25 | 70333.9982 | 1631.875 | 70333.9982 | 1654.375 | 1536.1368 | 1676.5 | 70333.9982
1686.5 | 17.7704 | 1689.5 | 66041.9526 | 1692 | 198314.068 | 1695 | 105550.9988 | 1697.5 | 105550.9988 | 1717.5 | 70333.9982 | 1720 | 105550.9988 | 1723 | 70333.9982 | 1725.5 | 105550.9988 | 1745.5 | 18.4908 | 1748 | 49847.8763 | 1751 | 198513.9261 | 1753.5 | 21735.3712 | 1756.5 | 38332.9153 | 1759.5 | 198014.3993 | 1762 | 196415.9137 | 1770.5 | 196216.103 | 1773.5 | 193718.4693 | 1776 | 22859.5169 | 1778.5 | 68529.5156 | 1781.5 | 193218.9426 | 1784.5 | 192119.9837 | 1792.5 | 6.6098 | 1801 | 210702.3786 | 1804 | 105550.9988 | 1806.5 | 105550.9988 | 1809.5 | 80179.3315 | 1818 | 70333.9982 | 1821 | 105550.9988 | 1823.5 | 113868.9988 | 1826.5 | 105550.9988 | 1829 | 13.9824 | 1832 | 32698.3397 | 1835 | 1536.1285 | 1843 | 54768.3904 | 1846 | 38887.8304 | 1854.5 | 70333.9982 | 1857 | 82779.3315 | 1860 | 72879.3315 | 1862.5 | 71879.3315 | 1865.5 | 70333.9982 | 1868.5 | 2263.352 | 1704.75 | 66041.9526 | 1710.25 | 70333.9982 | 1760.75 | 49847.8763 | 1766.125 | 21735.3712 | 1771.875 | 192119.9837 | 1811 | 70333.9982 | 1816.5 | 80179.3315 | 1839 | 1536.1285 | 1861.25 | 70333.9982
1871.5 | 2.9146 | 1874 | 48809.6338 | 1876.5 | 193318.8006 | 1879.5 | 210702.4259 | 1882.5 | 210802.284 | 1902 | 105550.9988 | 1905 | 105550.9988 | 1907.5 | 105550.9988 | 1910.5 | 105550.9988 | 1930 | 18.1875 | 1933 | 51424.3653 | 1935.5 | 205807.0165 | 1938.5 | 6644.7289 | 1941.5 | 6001.378 | 1944 | 205007.7737 | 1947 | 204608.1523 | 1955 | 205207.5844 | 1958 | 204108.6256 | 1960.5 | 13660.9596 | 1963.5 | 80677.7629 | 1966.5 | 204208.5309 | 1969 | 203808.9095 | 1977.5 | 21.7046 | 1986 | 70333.9982 | 1989 | 105550.9988 | 1991.5 | 70333.9982 | 1994.5 | 140542.8675 | 2003 | 105550.9988 | 2005.5 | 105550.9988 | 2008.5 | 113868.9988 | 2011 | 70333.9982 | 2014 | 20.2207 | 2016.5 | 13821.236 | 2019.5 | 48079.4232 | 2028 | 49674.8642 | 2030.5 | 61958.0672 | 2039 | 70333.9982 | 2042 | 82779.3315 | 2044.5 | 109368.9988 | 2047.5 | 107868.9988 | 2050.5 | 105550.9988 | 2053 | 96.6425 | 1889.375 | 48809.6338 | 1895 | 105550.9988 | 1945.375 | 51424.3653 | 1951 | 6001.378 | 1956.625 | 203808.9095 | 1995.875 | 70333.9982 | 2001.375 | 70333.9982 | 2023.625 | 13821.236 | 2046.125 | 82779.3315
2056 | 1.4121 | 2058.5 | 51528.1857 | 2061.5 | 205906.8745 | 2064.5 | 105550.9988 | 2067 | 105550.9988 | 2086.5 | 105550.9988 | 2089.5 | 105550.9988 | 2092.5 | 105550.9988 | 2095 | 105550.9988 | 2114.5 | 16.6205 | 2117.5 | 69734.5204 | 2120.5 | 209403.6091 | 2123 | 111475.18 | 2126 | 37269.0767 | 2128.5 | 209603.4198 | 2131.5 | 209303.7037 | 2140 | 209603.4198 | 2142.5 | 209503.5144 | 2145.5 | 18843.8688 | 2148.5 | 20275.6838 | 2151 | 209403.6091 | 2154 | 209403.6091 | 2162.5 | 0.24894 | 2170.5 | 210702.3786 | 2173.5 | 105550.9988 | 2176.5 | 105550.9988 | 2179 | 120318.9988 | 2187.5 | 70333.9982 | 2190.5 | 105550.9988 | 2193 | 113868.9988 | 2196 | 105550.9988 | 2198.5 | 15.383 | 2201.5 | 27615.6787 | 2204.5 | 21212.1565 | 2212.5 | 93918.6311 | 2215.5 | 50872.369 | 2224 | 105550.9988 | 2226.5 | 124218.9988 | 2229.5 | 109368.9988 | 2232.5 | 107868.9988 | 2235 | 105550.9988 | 2238 | 77479.8452 | 2074 | 51528.1857 | 2079.75 | 105550.9988 | 2130.125 | 69734.5204 | 2135.75 | 18843.8688 | 2141.25 | 209303.7037 | 2180.5 | 70333.9982 | 2186.125 | 105550.9988 | 2208.5 | 21212.1565 | 2230.875 | 105550.9988
2240.5 | 14.4573 | 2243.5 | 70200.7928 | 2246.5 | 210702.3313 | 2249 | 210802.284 | 2252 | 105550.9988 | 2271.5 | 105550.9988 | 2274.5 | 105550.9988 | 2277 | 105550.9988 | 2280 | 105550.9988 | 2299.5 | 20.503 | 2302.5 | 52675.4527 | 2305 | 210802.284 | 2308 | 125468.9988 | 2310.5 | 74345.9982 | 2313.5 | 70333.9982 | 2316.5 | 105550.9988 | 2324.5 | 105550.9988 | 2327.5 | 105550.9988 | 2330.5 | 120418.9988 | 2333 | 79645.9982 | 2336 | 70333.9982 | 2338.5 | 105550.9988 | 2347 | 10.8719 | 2355.5 | 210702.3786 | 2358.5 | 105550.9988 | 2361 | 211201.9994 | 2364 | 240737.9994 | 2372.5 | 105550.9988 | 2375 | 105550.9988 | 2378 | 113868.9988 | 2380.5 | 211201.9994 | 2383.5 | 1.6821 | 2386.5 | 7928.3835 | 2389 | 28703.0301 | 2397.5 | 1536.0477 | 2400.5 | 1536.6789 | 2408.5 | 105550.9988 | 2411.5 | 124218.9988 | 2414.5 | 109368.9988 | 2417 | 107868.9988 | 2420 | 105550.9988 | 2422.5 | 15.5261 | 2259 | 70200.7928 | 2264.5 | 105550.9988 | 2314.875 | 52675.4527 | 2320.5 | 74345.9982 | 2326.125 | 70333.9982 | 2365.375 | 105550.9988 | 2370.875 | 113868.9988 | 2393.375 | 1536.0477 | 2415.75 | 105550.9988
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Minimum Conductor to Ground Resistances
Penlight Test 68 |  |  | 2006-08-23 | 15:05
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-155.7 | 211202 |  | -133.3 | 211202 | -105.2778 | 211202 | -89.7222 | 211202 | -75.4444 | 211202 | -66.7222 | 211202 | -42.5 | 240938 | -37 | 223238 | -24.6667 | 211202 | -21.6111 | 211202 | -4 | 211202 | -1.7 | 211202 | -155.7 | 211202 | -105.2778 | 211202 | -75.4444 | 211202 | -68.625 | 211202 | -60.3194 | 211202 | -31.4444 | 211202 | -47.1111 | 211202 | -36.9667 | 211202 | -12.9944 | 211202 | -144.5 | 211202 | -97.5 | 211202 | -71.0833 | 211202 | -39.75 | 223238 | -23.1389 | 211202 | -2.85 | 211202
29.1 | 211202 |  | 51.5 | 211202 | 79.5556 | 211202 | 95.0556 | 211202 | 109.3333 | 211202 | 118.0556 | 211202 | 142.1 | 240938 | 147.9 | 223238 | 160.1111 | 211202 | 163.1111 | 211202 | 180.8 | 211202 | 183 | 211202 | 29.1 | 211202 | 79.5556 | 211202 | 109.3333 | 211202 | 116.1528 | 211202 | 124.4583 | 211202 | 153.3056 | 211202 | 137.6528 | 211202 | 147.7972 | 211202 | 171.7556 | 211202 | 40.3 | 211202 | 87.3056 | 211202 | 113.6944 | 211202 | 145 | 223238 | 161.6111 | 211202 | 181.9 | 211202
213.8 | 211202 |  | 236.2 | 211202 | 264.1667 | 105551 | 279.7778 | 211202 | 294.0556 | 211202 | 302.7778 | 211202 | 326.8 | 240938 | 332.4 | 223238 | 344.7778 | 211202 | 347.8889 | 211202 | 365.6 | 211202 | 368 | 211202 | 213.8 | 105551 | 264.1667 | 105551 | 294.0556 | 211202 | 300.7861 | 105551 | 309.1528 | 105551 | 337.9667 | 211202 | 322.375 | 211202 | 332.6083 | 211202 | 356.5667 | 211202 | 225 | 211202 | 271.9722 | 105551 | 298.4167 | 211202 | 329.6 | 223238 | 346.3333 | 211202 | 366.8 | 211202
398.6 | 211202 |  | 421.1 | 105551 | 449 | 211202 | 464.5 | 211202 | 478.8333 | 211202 | 487.5556 | 211202 | 511.6 | 240938 | 517.3 | 223238 | 529.5 | 211202 | 532.7222 | 105551 | 550.4 | 211202 | 552.6 | 211202 | 398.6 | 105551 | 449 | 105551 | 478.8333 | 105551 | 485.6 | 211202 | 493.9306 | 105551 | 522.7806 | 105551 | 507.1528 | 105551 | 517.3472 | 211202 | 541.3056 | 105551 | 409.85 | 105551 | 456.75 | 211202 | 483.1944 | 211202 | 514.45 | 223238 | 531.1111 | 105551 | 551.5 | 211202
583.5 | 211202 |  | 605.8 | 211202 | 633.7222 | 211202 | 649.3333 | 211202 | 663.7222 | 211202 | 672.4444 | 211202 | 696.5 | 240938 | 702.1 | 223238 | 714.3889 | 211202 | 717.5556 | 211202 | 735.2 | 211202 | 737.4 | 211202 | 583.5 | 211202 | 633.7222 | 211202 | 663.7222 | 211202 | 670.4139 | 211202 | 678.75 | 211202 | 707.6361 | 211202 | 692.0278 | 211202 | 702.1917 | 211202 | 726.1361 | 211202 | 594.65 | 211202 | 641.5278 | 211202 | 668.0833 | 211202 | 699.3 | 223238 | 715.9722 | 211202 | 736.3 | 211202
768.2 | 211202 |  | 790.5 | 211202 | 818.5556 | 211202 | 834.1111 | 211202 | 848.4444 | 211202 | 857.0556 | 211202 | 881.2 | 240938 | 886.9 | 223238 | 899.1111 | 211202 | 902.1667 | 211202 | 919.9 | 211202 | 922.1 | 211202 | 768.2 | 211202 | 818.5556 | 211202 | 848.4444 | 211202 | 855.1917 | 211202 | 863.4861 | 211202 | 892.3444 | 211202 | 876.6944 | 211202 | 886.875 | 211202 | 910.8194 | 211202 | 779.35 | 211202 | 826.3333 | 211202 | 852.75 | 211202 | 884.05 | 223238 | 900.6389 | 211202 | 921 | 211202
952.9 | 211202 |  | 975.3 | 211202 | 1003.2778 | 211202 | 1018.8889 | 211202 | 1033.1111 | 211202 | 1041.8333 | 211202 | 1066 | 6457.7838 | 1071.6 | 6457.7838 | 1083.8889 | 211202 | 1087 | 211202 | 1104.6 | 730.1091 | 1107 | 718.6829 | 952.9 | 211202 | 1003.2778 | 6457.7838 | 1033.1111 | 718.6829 | 1039.9417 | 6457.7838 | 1048.2639 | 211202 | 1077.1222 | 6457.7838 | 1061.4583 | 211202 | 1071.6361 | 718.6829 | 1095.6222 | 718.6829 | 964.1 | 211202 | 1011.0833 | 211202 | 1037.4722 | 211202 | 1068.8 | 6457.7838 | 1085.4444 | 211202 | 1105.8 | 718.6829
1137.7 | 99.4391 |  | 1160.1 | 106.929 | 1188.1111 | 70334 | 1203.6111 | 70334 | 1217.9444 | 70334 | 1226.6111 | 70334 | 1250.8 | 2617.5091 | 1256.4 | 4207.9852 | 1268.6667 | 70334 | 1271.7222 | 70334 | 1289.5 | 3.9863 | 1291.5 | 4.6568 | 1137.7 | 99.4391 | 1188.1111 | 2617.5091 | 1217.9444 | 3.9863 | 1224.7306 | 2617.5091 | 1233.0278 | 70334 | 1261.8972 | 2617.5091 | 1246.2361 | 70334 | 1256.3889 | 3.9863 | 1280.3472 | 3.9863 | 1148.9 | 99.4391 | 1195.8611 | 70334 | 1222.2778 | 70334 | 1253.6 | 2617.5091 | 1270.1944 | 70334 | 1290.5 | 3.9863
1322.5 | 468.8207 |  | 1344.9 | 415.2293 | 1372.8333 | 70334 | 1388.3333 | 2674.6511 | 1402.8333 | 3199.3216 | 1411.5 | 12938.7202 | 1435.6 | 0.67967 | 1441.1 | 0.68939 | 1453.3889 | 52725.5 | 1456.5556 | 70334 | 1474.2 | 0.76435 | 1476.5 | 0.7538 | 1322.5 | 415.2293 | 1372.8333 | 0.67967 | 1402.8333 | 0.7538 | 1409.4667 | 0.67967 | 1417.7778 | 2674.6511 | 1446.6611 | 0.67967 | 1431.0694 | 3199.3216 | 1441.2583 | 0.7538 | 1465.1611 | 0.7538 | 1333.7 | 415.2293 | 1380.5833 | 2674.6511 | 1407.1667 | 3199.3216 | 1438.35 | 0.67967 | 1454.9722 | 52725.5 | 1475.35 | 0.7538
1507.3 | 1258.8477 |  | 1529.7 | 2035.3145 | 1557.7222 | 142.6181 | 1573.2778 | 164.5026 | 1587.5 | 8027 | 1596.2778 | 3482.778 | 1620.5 | 0.65651 | 1626 | 7.4261 | 1638.2778 | 70334 | 1641.2778 | 70334 | 1659 | 0.66316 | 1661.1 | 0.68478 | 1507.3 | 142.6181 | 1557.7222 | 0.65651 | 1587.5 | 0.66316 | 1594.375 | 0.65651 | 1602.6389 | 142.6181 | 1631.5139 | 0.65651 | 1615.8333 | 3482.778 | 1625.9694 | 0.66316 | 1649.9139 | 0.66316 | 1518.5 | 1258.8477 | 1565.5 | 142.6181 | 1591.8889 | 3482.778 | 1623.25 | 0.65651 | 1639.7778 | 70334 | 1660.05 | 0.66316
1692.1 | 3456.813 |  | 1714.5 | 19472.7648 | 1742.5556 | 1356.5744 | 1758 | 726.443 | 1772.2222 | 12697.3365 | 1781 | 3566.1752 | 1805.1 | 0.66912 | 1810.6 | 20.1539 | 1822.9444 | 70334 | 1826.1111 | 70334 | 1843.6 | 2.9557 | 1846 | 16.6734 | 1692.1 | 726.443 | 1742.5556 | 0.66912 | 1772.2222 | 2.9557 | 1779.0639 | 0.66912 | 1787.4028 | 726.443 | 1816.1889 | 0.66912 | 1800.5694 | 3566.1752 | 1810.7056 | 2.9557 | 1834.6639 | 2.9557 | 1703.3 | 3456.813 | 1750.2778 | 726.443 | 1776.6111 | 3566.1752 | 1807.85 | 0.66912 | 1824.5278 | 70334 | 1844.8 | 2.9557
1876.8 | 437.3504 |  | 1899.3 | 505.8426 | 1927.2778 | 1270.7976 | 1942.6667 | 1093.2343 | 1957.0556 | 3019.9987 | 1965.7778 | 14936.7796 | 1989.8 | 2.7815 | 1995.5 | 2.829 | 2007.7222 | 70334 | 2010.8333 | 70334 | 2028.5 | 38.3959 | 2030.7 | 19.5147 | 1876.8 | 437.3504 | 1927.2778 | 2.7815 | 1957.0556 | 19.5147 | 1963.8111 | 2.7815 | 1972.125 | 1093.2343 | 2000.9639 | 2.7815 | 1985.3472 | 3019.9987 | 1995.5083 | 19.5147 | 2019.4389 | 19.5147 | 1888.05 | 437.3504 | 1934.9722 | 1093.2343 | 1961.4167 | 3019.9987 | 1992.65 | 2.7815 | 2009.2778 | 70334 | 2029.6 | 19.5147
2061.5 | 165.0964 |  | 2083.9 | 172.9304 | 2111.8333 | 4591.2438 | 2127.4444 | 1289.491 | 2141.8333 | 1.9476 | 2150.5 | 2.2054 | 2174.6 | 8.5423 | 2180.2 | 9.341 | 2192.3889 | 78679.3333 | 2195.6667 | 77512.6667 | 2213.3 | 19415.6444 | 2215.5 | 1285.6835 | 2061.5 | 1.9476 | 2111.8333 | 8.5423 | 2141.8333 | 1.9476 | 2148.5194 | 8.5423 | 2156.8333 | 1289.491 | 2185.7139 | 8.5423 | 2170.0972 | 1.9476 | 2180.2833 | 1.9476 | 2204.2139 | 1285.6835 | 2072.7 | 165.0964 | 2119.6389 | 1289.491 | 2146.1667 | 1.9476 | 2177.4 | 8.5423 | 2194.0278 | 77512.6667 | 2214.4 | 1285.6835
2246.3 | 1047.0215 |  | 2268.7 | 3143.094 | 2296.7222 | 10935.6262 | 2312.2778 | 2362.28 | 2326.5556 | 258.729 | 2335.2778 | 236.6471 | 2359.5 | 3.1186 | 2365 | 0.69821 | 2377.3333 | 78679.3333 | 2380.3889 | 82079.3333 | 2398 | 16.752 | 2400.3 | 6114.7647 | 2246.3 | 236.6471 | 2296.7222 | 0.69821 | 2326.5556 | 16.752 | 2333.375 | 0.69821 | 2341.6806 | 2362.28 | 2370.5556 | 0.69821 | 2354.8889 | 236.6471 | 2365.0333 | 16.752 | 2389.0056 | 16.752 | 2257.5 | 1047.0215 | 2304.5 | 2362.28 | 2330.9167 | 236.6471 | 2362.25 | 0.69821 | 2378.8611 | 78679.3333 | 2399.15 | 16.752
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0

## F11-F12
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 143.1245 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38952.6288 | 1 | 0 | 38952.6288 | 1 | 0 |  | 20.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38952.631 | 1 | 0 | 38952.631 | 1 | 0 |  | 205.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38952.6331 | 1 | 0 | 38952.6331 | 1 | 0 |  | 390.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38952.6352 | 1 | 0 | 38952.6353 | 1 | 0 |  | 575 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38952.6374 | 1 | 0 | 38952.6374 | 1 | 0 |  | 759.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38952.6395 | 1 | 0 | 38952.6395 | 1 | 0 |  | 944.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234338 | 234338 | 234337.9994
38952.6417 | 1085 | 1060 | 38952.6417 | 1119 | 1185 |  | 1129.5 | 1291.5 | 66.2393 | 64.7131 | 68.315 | 72.3443 | 0.66239 | 0.64713 | 0.68315 | 0.72344 | 0.015263 | 0.040293 | 730.1091 | 718.6829 | 16.5119
38952.6438 | 1782 | 492 | 38952.6438 | 2227 | 399 |  | 1314 | 1476 | 108.7912 | 30.0366 | 135.9585 | 24.359 | 1.0879 | 0.30037 | 1.3596 | 0.24359 | 0.78755 | 1.116 | 17.4203 | 25.3829 | 2.8959
38952.6459 | 2053 | 59 | 38952.646 | 1971 | 30 |  | 1499 | 1661 | 125.3358 | 3.602 | 120.3297 | 1.8315 | 1.2534 | 0.03602 | 1.2033 | 0.018315 | 1.2173 | 1.185 | 16.9881 | 21.1618 | 68.7913
38952.6481 | 2328 | 0 | 38952.6481 | 1555 | 1 |  | 1683.5 | 1845.5 | 142.1245 | 0 | 94.9328 | 0.06105 | 1.4212 | 0 | 0.94933 | 0.0006105 | 1.4212 | 0.94872 | 0.70361 | 50.861 | 0.71764
38952.6502 | 2185 | 1 | 38952.6502 | 1321 | 506 |  | 1868.5 | 2030.5 | 133.3944 | 0.06105 | 80.6471 | 30.8913 | 1.3339 | 0.0006105 | 0.80647 | 0.30891 | 1.3333 | 0.49756 | 7.2776 | 16.6734 | 2263.352
38952.6523 | 808 | 781 | 38952.6524 | 10 | 8 |  | 2053 | 2215 | 49.3284 | 47.6801 | 0.6105 | 0.4884 | 0.49328 | 0.4768 | 0.006105 | 0.004884 | 0.016484 | 0.001221 | 5824.735 | 125325.4297 | 96.6425
38952.6545 | 15 | 3 | 38952.6545 | 2 | 0 |  | 2238 | 2400 | 0.91575 | 0.18315 | 0.1221 | 0 | 0.0091575 | 0.0018315 | 0.001221 | 0 | 0.007326 | 0.001221 | 19415.6444 | 117119 | 77479.8452
38952.6566 | 2008 | 0 | 38952.6566 | 3 | 0 |  | 2422.5 | 2584.5 | 122.5885 | 0 | 0.18315 | 0 | 1.2259 | 0 | 0.0018315 | 0 | 1.2259 | 0.0018315 | 16.752 | 78046 | 15.5261

## E10-F12
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38952.6288 | 1 | 0 | 38952.6288 | 1 | 0 |  | 18 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6309 | 1 | 0 | 38952.6309 | 1 | 0 |  | 202.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6331 | 1 | 0 | 38952.6331 | 1 | 0 |  | 387.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6352 | 1 | 0 | 38952.6352 | 1 | 0 |  | 572.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6373 | 1 | 0 | 38952.6374 | 1 | 0 |  | 757 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6395 | 1 | 0 | 38952.6395 | 1 | 0 |  | 941.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6416 | 1 | 0 | 38952.6416 | 1 | 0 |  | 1126.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6438 | 3 | 0 | 38952.6438 | 2019 | 0 |  | 1311.5 | 1473.5 | 0.18315 | 0 | 123.2601 | 0 | 0.0018315 | 0 | 1.2326 | 0 | 0.0018315 | 1.2326 | 70334 | 4.6568 | 70333.9982
38952.6459 | 3 | 0 | 38952.6459 | 2086 | 0 |  | 1496 | 1658 | 0.18315 | 0 | 127.3504 | 0 | 0.0018315 | 0 | 1.2735 | 0 | 0.0018315 | 1.2735 | 70334 | 1.2953 | 70333.9982
38952.648 | 3 | 0 | 38952.6481 | 1834 | 0 |  | 1680.5 | 1842.5 | 0.18315 | 0 | 111.9658 | 0 | 0.0018315 | 0 | 1.1197 | 0 | 0.0018315 | 1.1197 | 70334 | 15.2137 | 70333.9982
38952.6502 | 3 | 0 | 38952.6502 | 1627 | 0 |  | 1865.5 | 2027.5 | 0.18315 | 0 | 99.3284 | 0 | 0.0018315 | 0 | 0.99328 | 0 | 0.0018315 | 0.99328 | 70334 | 29.8722 | 70333.9982
38952.6523 | 2 | 0 | 38952.6523 | 3 | 0 |  | 2050.5 | 2212.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.6545 | 2 | 0 | 38952.6545 | 2 | 0 |  | 2235 | 2397 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6566 | 2 | 0 | 38952.6566 | 34 | 0 |  | 2420 | 2582 | 0.1221 | 0 | 2.0757 | 0 | 0.001221 | 0 | 0.020757 | 0 | 0.001221 | 0.020757 | 105551 | 6114.7647 | 105550.9988

## E10-F11
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 131.8303 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38952.6288 | 1 | 0 | 38952.6288 | 1 | 0 |  | 15 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 215838 | 215838 | 215837.9994
38952.6309 | 1 | 0 | 38952.6309 | 1 | 0 |  | 200 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 215838 | 215838 | 215837.9994
38952.633 | 1 | 0 | 38952.6331 | 1 | 0 |  | 384.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 215838 | 215838 | 215837.9994
38952.6352 | 1 | 0 | 38952.6352 | 1 | 0 |  | 569.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 215838 | 215838 | 215837.9994
38952.6373 | 1 | 0 | 38952.6373 | 1 | 0 |  | 754.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 215838 | 215838 | 215837.9994
38952.6395 | 1 | 0 | 38952.6395 | 1 | 0 |  | 939 | 1101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 215838 | 215838 | 215837.9994
38952.6416 | 1 | 0 | 38952.6416 | 1 | 0 |  | 1123.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 215838 | 215838 | 215837.9994
38952.6437 | 3 | 0 | 38952.6438 | 1638 | 0 |  | 1308.5 | 1470.5 | 0.18315 | 0 | 100 | 0 | 0.0018315 | 0 | 1 | 0 | 0.0018315 | 1 | 71879.3333 | 31.8303 | 71879.3315
38952.6459 | 3 | 0 | 38952.6459 | 2143 | 0 |  | 1493 | 1655 | 0.18315 | 0 | 130.8303 | 0 | 0.0018315 | 0 | 1.3083 | 0 | 0.0018315 | 1.3083 | 71879.3333 | 0.76435 | 71879.3315
38952.648 | 3 | 0 | 38952.648 | 2026 | 0 |  | 1678 | 1840 | 0.18315 | 0 | 123.6874 | 0 | 0.0018315 | 0 | 1.2369 | 0 | 0.0018315 | 1.2369 | 71879.3333 | 6.5834 | 71879.3315
38952.6502 | 3 | 0 | 38952.6502 | 2028 | 0 |  | 1862.5 | 2024.5 | 0.18315 | 0 | 123.8095 | 0 | 0.0018315 | 0 | 1.2381 | 0 | 0.0018315 | 1.2381 | 71879.3333 | 6.4783 | 71879.3315
38952.6523 | 2 | 0 | 38952.6523 | 2 | 0 |  | 2047.5 | 2209.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 107869 | 107869 | 107868.9988
38952.6544 | 2 | 0 | 38952.6544 | 2 | 0 |  | 2232.5 | 2394.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 107869 | 107869 | 107868.9988
38952.6566 | 2 | 0 | 38952.6566 | 2 | 0 |  | 2417 | 2579 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 107869 | 107869 | 107868.9988

## E9-F12
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 133.6618 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38952.6287 | 1 | 0 | 38952.6288 | 1 | 0 |  | 12.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218838 | 218838 | 218837.9994
38952.6309 | 1 | 0 | 38952.6309 | 1 | 0 |  | 197 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218838 | 218838 | 218837.9994
38952.633 | 1 | 0 | 38952.633 | 1 | 0 |  | 382 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218838 | 218838 | 218837.9994
38952.6352 | 1 | 0 | 38952.6352 | 1 | 0 |  | 566.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218838 | 218838 | 218837.9994
38952.6373 | 1 | 0 | 38952.6373 | 1 | 0 |  | 751.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218838 | 218838 | 218837.9994
38952.6394 | 1 | 0 | 38952.6394 | 1 | 0 |  | 936 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218838 | 218838 | 218837.9994
38952.6416 | 1 | 0 | 38952.6416 | 1 | 0 |  | 1121 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218838 | 218838 | 218837.9994
38952.6437 | 2 | 0 | 38952.6437 | 1689 | 0 |  | 1305.5 | 1467.5 | 0.1221 | 0 | 103.1136 | 0 | 0.001221 | 0 | 1.0311 | 0 | 0.001221 | 1.0311 | 109369 | 29.6258 | 109368.9988
38952.6458 | 3 | 0 | 38952.6459 | 2173 | 0 |  | 1490.5 | 1652.5 | 0.18315 | 0 | 132.6618 | 0 | 0.0018315 | 0 | 1.3266 | 0 | 0.0018315 | 1.3266 | 72879.3333 | 0.7538 | 72879.3315
38952.648 | 3 | 0 | 38952.648 | 1711 | 0 |  | 1675 | 1837 | 0.18315 | 0 | 104.4567 | 0 | 0.0018315 | 0 | 1.0446 | 0 | 0.0018315 | 1.0446 | 72879.3333 | 27.9591 | 72879.3315
38952.6501 | 3 | 0 | 38952.6501 | 768 | 0 |  | 1860 | 2022 | 0.18315 | 0 | 46.8864 | 0 | 0.0018315 | 0 | 0.46886 | 0 | 0.0018315 | 0.46886 | 72879.3333 | 185.0755 | 72879.3315
38952.6523 | 2 | 0 | 38952.6523 | 15 | 0 |  | 2044.5 | 2206.5 | 0.1221 | 0 | 0.91575 | 0 | 0.001221 | 0 | 0.0091575 | 0 | 0.001221 | 0.0091575 | 109369 | 14495.8667 | 109368.9988
38952.6544 | 2 | 0 | 38952.6544 | 158 | 0 |  | 2229.5 | 2391.5 | 0.1221 | 0 | 9.6459 | 0 | 0.001221 | 0 | 0.096459 | 0 | 0.001221 | 0.096459 | 109369 | 1285.6835 | 109368.9988
38952.6565 | 2 | 0 | 38952.6566 | 3 | 0 |  | 2414.5 | 2576.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 109369 | 72879.3333 | 109368.9988

## E9-F11
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 151.7937 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38952.6287 | 1 | 0 | 38952.6287 | 1 | 0 |  | 9.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38952.6308 | 1 | 0 | 38952.6309 | 1 | 0 |  | 194.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38952.633 | 1 | 0 | 38952.633 | 1 | 0 |  | 379 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38952.6351 | 1 | 0 | 38952.6351 | 1 | 0 |  | 564 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38952.6373 | 1 | 0 | 38952.6373 | 1 | 0 |  | 748.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38952.6394 | 1 | 0 | 38952.6394 | 1 | 0 |  | 933.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38952.6415 | 1 | 0 | 38952.6416 | 1 | 0 |  | 1118 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38952.6437 | 2 | 0 | 38952.6437 | 1259 | 0 |  | 1303 | 1465 | 0.1221 | 0 | 76.862 | 0 | 0.001221 | 0 | 0.76862 | 0 | 0.001221 | 0.76862 | 124219 | 97.4885 | 124218.9988
38952.6458 | 3 | 0 | 38952.6458 | 1848 | 0 |  | 1487.5 | 1649.5 | 0.18315 | 0 | 112.8205 | 0 | 0.0018315 | 0 | 1.1282 | 0 | 0.0018315 | 1.1282 | 82779.3333 | 34.5444 | 82779.3315
38952.648 | 2 | 0 | 38952.648 | 2470 | 0 |  | 1672.5 | 1834.5 | 0.1221 | 0 | 150.7937 | 0 | 0.001221 | 0 | 1.5079 | 0 | 0.001221 | 1.5079 | 124219 | 0.66316 | 124218.9988
38952.6501 | 3 | 0 | 38952.6501 | 2415 | 0 |  | 1857 | 2019 | 0.18315 | 0 | 147.4359 | 0 | 0.0018315 | 0 | 1.4744 | 0 | 0.0018315 | 1.4744 | 82779.3333 | 2.9557 | 82779.3315
38952.6522 | 3 | 0 | 38952.6522 | 3 | 0 |  | 2042 | 2204 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 82779.3333 | 82779.3333 | 82779.3315
38952.6544 | 2 | 0 | 38952.6544 | 2 | 0 |  | 2226.5 | 2388.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124219 | 124219 | 124218.9988
38952.6565 | 2 | 0 | 38952.6565 | 3 | 0 |  | 2411.5 | 2573.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 124219 | 82779.3333 | 124218.9988

## E9-E10
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38952.6287 | 1 | 0 | 38952.6287 | 1 | 0 |  | 6.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6308 | 1 | 0 | 38952.6308 | 1 | 0 |  | 191.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.633 | 1 | 0 | 38952.633 | 1 | 0 |  | 376.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6351 | 1 | 0 | 38952.6351 | 1 | 0 |  | 561 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6372 | 1 | 0 | 38952.6372 | 1 | 0 |  | 746 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6394 | 1 | 0 | 38952.6394 | 1 | 0 |  | 930.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6415 | 1 | 1 | 38952.6415 | 1 | 0 |  | 1115.5 | 1277.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38952.6436 | 3 | 0 | 38952.6437 | 2 | 0 |  | 1300 | 1462 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6458 | 4 | 0 | 38952.6458 | 3 | 0 |  | 1485 | 1647 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.6479 | 3 | 0 | 38952.6479 | 3 | 0 |  | 1669.5 | 1831.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.6501 | 3 | 0 | 38952.6501 | 3 | 0 |  | 1854.5 | 2016.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.6522 | 3 | 0 | 38952.6522 | 3 | 0 |  | 2039 | 2201 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.6543 | 2 | 0 | 38952.6544 | 2 | 0 |  | 2224 | 2386 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6565 | 2 | 0 | 38952.6565 | 2 | 0 |  | 2408.5 | 2570.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## D8-E10
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 142.1477 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38952.6286 | 1 | 0 | 38952.6286 | 1 | 0 |  | -1.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38952.6307 | 1 | 0 | 38952.6307 | 1 | 0 |  | 183 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38952.6328 | 1 | 0 | 38952.6329 | 1 | 0 |  | 367.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38952.635 | 1 | 0 | 38952.635 | 1 | 0 |  | 552.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38952.6371 | 1 | 0 | 38952.6371 | 1 | 0 |  | 737.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38952.6393 | 1 | 0 | 38952.6393 | 1 | 0 |  | 922 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38952.6414 | 1 | 0 | 38952.6414 | 1 | 0 |  | 1107 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38952.6435 | 7 | 1 | 38952.6436 | 1 | 0 |  | 1291.5 | 1453.5 | 0.42735 | 0.06105 | 0.06105 | 0 | 0.0042735 | 0.0006105 | 0.0006105 | 0 | 0.003663 | 0.0006105 | 38692.4375 | 232738 | 231938.3436
38952.6457 | 2154 | 1 | 38952.6457 | 3 | 0 |  | 1476.5 | 1638.5 | 131.5018 | 0.06105 | 0.18315 | 0 | 1.315 | 0.0006105 | 0.0018315 | 0 | 1.3144 | 0.0018315 | 8.0994 | 77512.6667 | 17315.6609
38952.6478 | 1821 | 1 | 38952.6478 | 2 | 0 |  | 1661.5 | 1823.5 | 111.1722 | 0.06105 | 0.1221 | 0 | 1.1117 | 0.0006105 | 0.001221 | 0 | 1.1111 | 0.001221 | 27.878 | 116319 | 50594.5037
38952.65 | 1938 | 1 | 38952.65 | 3 | 0 |  | 1846 | 2008 | 118.315 | 0.06105 | 0.18315 | 0 | 1.1832 | 0.0006105 | 0.0018315 | 0 | 1.1825 | 0.0018315 | 20.1539 | 77512.6667 | 38887.8304
38952.6521 | 1707 | 1 | 38952.6521 | 3 | 0 |  | 2030.5 | 2192.5 | 104.2125 | 0.06105 | 0.18315 | 0 | 1.0421 | 0.0006105 | 0.0018315 | 0 | 1.0415 | 0.0018315 | 36.4232 | 77512.6667 | 61958.0672
38952.6542 | 1818 | 1 | 38952.6542 | 3 | 0 |  | 2215.5 | 2377.5 | 110.989 | 0.06105 | 0.18315 | 0 | 1.1099 | 0.0006105 | 0.0018315 | 0 | 1.1093 | 0.0018315 | 28.0892 | 77512.6667 | 50872.369
38952.6564 | 2312 | 1 | 38952.6564 | 2 | 0 |  | 2400.5 | 2562.5 | 141.1477 | 0.06105 | 0.1221 | 0 | 1.4115 | 0.0006105 | 0.001221 | 0 | 1.4109 | 0.001221 | 0.70878 | 116319 | 1536.6789

## D8-E9
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 144.2845 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38952.6285 | 1 | 0 | 38952.6286 | 1 | 0 |  | -4.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38952.6307 | 1 | 0 | 38952.6307 | 1 | 0 |  | 180.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38952.6328 | 1 | 0 | 38952.6328 | 1 | 0 |  | 365 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38952.635 | 1 | 0 | 38952.635 | 1 | 0 |  | 550 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38952.6371 | 1 | 0 | 38952.6371 | 1 | 0 |  | 734.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38952.6392 | 1 | 0 | 38952.6392 | 1 | 0 |  | 919.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38952.6414 | 1 | 0 | 38952.6414 | 1 | 0 |  | 1104 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38952.6435 | 6 | 1 | 38952.6435 | 2 | 0 |  | 1289 | 1451 | 0.3663 | 0.06105 | 0.1221 | 0 | 0.003663 | 0.0006105 | 0.001221 | 0 | 0.0030525 | 0.001221 | 47155.5878 | 118069 | 235438.5924
38952.6456 | 2155 | 1 | 38952.6457 | 3 | 0 |  | 1473.5 | 1635.5 | 131.5629 | 0.06105 | 0.18315 | 0 | 1.3156 | 0.0006105 | 0.0018315 | 0 | 1.315 | 0.0018315 | 9.6741 | 78679.3333 | 20711.6758
38952.6478 | 1765 | 1 | 38952.6478 | 3 | 0 |  | 1658.5 | 1820.5 | 107.7534 | 0.06105 | 0.18315 | 0 | 1.0775 | 0.0006105 | 0.0018315 | 0 | 1.0769 | 0.0018315 | 33.9218 | 78679.3333 | 59662.1705
38952.6499 | 1814 | 1 | 38952.6499 | 3 | 0 |  | 1843 | 2005 | 110.7448 | 0.06105 | 0.18315 | 0 | 1.1074 | 0.0006105 | 0.0018315 | 0 | 1.1068 | 0.0018315 | 30.3023 | 78679.3333 | 54768.3904
38952.6521 | 1865 | 1 | 38952.6521 | 3 | 0 |  | 2028 | 2190 | 113.8584 | 0.06105 | 0.18315 | 0 | 1.1386 | 0.0006105 | 0.0018315 | 0 | 1.138 | 0.0018315 | 26.7371 | 78679.3333 | 49674.8642
38952.6542 | 1422 | 1 | 38952.6542 | 3 | 0 |  | 2212.5 | 2374.5 | 86.8132 | 0.06105 | 0.18315 | 0 | 0.86813 | 0.0006105 | 0.0018315 | 0 | 0.86752 | 0.0018315 | 66.2478 | 78679.3333 | 93918.6311
38952.6563 | 2347 | 1 | 38952.6564 | 3 | 0 |  | 2397.5 | 2559.5 | 143.2845 | 0.06105 | 0.18315 | 0 | 1.4328 | 0.0006105 | 0.0018315 | 0 | 1.4322 | 0.0018315 | 0.69821 | 78679.3333 | 1536.0477

## D7-E10
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 150.5116 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38952.6284 | 1 | 0 | 38952.6285 | 1 | 0 |  | -13 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246438 | 246438 | 246437.9994
38952.6306 | 1 | 0 | 38952.6306 | 1 | 0 |  | 171.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246438 | 246438 | 246437.9994
38952.6327 | 1 | 0 | 38952.6327 | 1 | 0 |  | 356.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246438 | 246438 | 246437.9994
38952.6349 | 1 | 0 | 38952.6349 | 1 | 0 |  | 541.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246438 | 246438 | 246437.9994
38952.637 | 1 | 0 | 38952.637 | 1 | 0 |  | 726 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246438 | 246438 | 246437.9994
38952.6391 | 1 | 0 | 38952.6392 | 1 | 0 |  | 911 | 1073 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246438 | 246438 | 246437.9994
38952.6413 | 1 | 1 | 38952.6413 | 1 | 0 |  | 1095.5 | 1257.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 607316878.44 | 246438 | 246238.0811
38952.6434 | 3 | 1 | 38952.6434 | 2 | 0 |  | 1280.5 | 1442.5 | 0.18315 | 0.06105 | 0.1221 | 0 | 0.0018315 | 0.0006105 | 0.001221 | 0 | 0.001221 | 0.001221 | 123169 | 123169 | 245938.3245
38952.6456 | 2231 | 1 | 38952.6456 | 3 | 0 |  | 1465.5 | 1627.5 | 136.2027 | 0.06105 | 0.18315 | 0 | 1.362 | 0.0006105 | 0.0018315 | 0 | 1.3614 | 0.0018315 | 10.5103 | 82079.3334 | 23309.6011
38952.6477 | 2047 | 1 | 38952.6477 | 3 | 0 |  | 1650 | 1812 | 124.9695 | 0.06105 | 0.18315 | 0 | 1.2497 | 0.0006105 | 0.0018315 | 0 | 1.2491 | 0.0018315 | 20.4487 | 82079.3334 | 41687.2111
38952.6498 | 2449 | 1 | 38952.6498 | 3 | 0 |  | 1835 | 1997 | 149.5116 | 0.06105 | 0.18315 | 0 | 1.4951 | 0.0006105 | 0.0018315 | 0 | 1.4945 | 0.0018315 | 0.66912 | 82079.3333 | 1536.1285
38952.652 | 1983 | 1 | 38952.652 | 3 | 0 |  | 2019.5 | 2181.5 | 121.0623 | 0.06105 | 0.18315 | 0 | 1.2106 | 0.0006105 | 0.0018315 | 0 | 1.21 | 0.0018315 | 24.3381 | 82079.3333 | 48079.4232
38952.6541 | 2252 | 1 | 38952.6541 | 3 | 0 |  | 2204.5 | 2366.5 | 137.4847 | 0.06105 | 0.18315 | 0 | 1.3748 | 0.0006105 | 0.0018315 | 0 | 1.3742 | 0.0018315 | 9.4793 | 82079.3334 | 21212.1565
38952.6562 | 2177 | 1 | 38952.6563 | 3 | 0 |  | 2389 | 2551 | 132.906 | 0.06105 | 0.18315 | 0 | 1.3291 | 0.0006105 | 0.0018315 | 0 | 1.3284 | 0.0018315 | 13.2528 | 82079.3333 | 28703.0301

## D7-E9
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 151.1832 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38952.6284 | 1 | 0 | 38952.6284 | 1 | 0 |  | -15.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38952.6305 | 1 | 0 | 38952.6306 | 1 | 0 |  | 169 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38952.6327 | 1 | 0 | 38952.6327 | 1 | 0 |  | 353.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38952.6348 | 1 | 0 | 38952.6348 | 1 | 0 |  | 538.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38952.637 | 1 | 0 | 38952.637 | 1 | 0 |  | 723.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38952.6391 | 1 | 0 | 38952.6391 | 1 | 0 |  | 908 | 1070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38952.6412 | 2 | 4 | 38952.6413 | 3 | 2 |  | 1093 | 1255 | 0.1221 | 0.2442 | 0.18315 | 0.1221 | 0.001221 | 0.002442 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 123818.9595 | 247738.1619 | 61734.5807
38952.6434 | 5 | 4 | 38952.6434 | 3 | 2 |  | 1277.5 | 1439.5 | 0.30525 | 0.2442 | 0.18315 | 0.1221 | 0.0030525 | 0.002442 | 0.0018315 | 0.001221 | 0.0006105 | 0.0006105 | 247538 | 247538 | 61659.5909
38952.6455 | 2127 | 1 | 38952.6455 | 3 | 0 |  | 1462.5 | 1624.5 | 129.8535 | 0.06105 | 0.18315 | 0 | 1.2985 | 0.0006105 | 0.0018315 | 0 | 1.2979 | 0.0018315 | 16.4337 | 82446 | 34795.7957
38952.6477 | 2460 | 1 | 38952.6477 | 3 | 0 |  | 1647.5 | 1809.5 | 150.1832 | 0.06105 | 0.18315 | 0 | 1.5018 | 0.0006105 | 0.0018315 | 0 | 1.5012 | 0.0018315 | 0.66612 | 82446 | 1536.1368
38952.6498 | 2148 | 1 | 38952.6498 | 3 | 0 |  | 1832 | 1994 | 131.1355 | 0.06105 | 0.18315 | 0 | 1.3114 | 0.0006105 | 0.0018315 | 0 | 1.3107 | 0.0018315 | 15.2948 | 82446 | 32698.3397
38952.6519 | 2337 | 1 | 38952.6519 | 3 | 0 |  | 2016.5 | 2178.5 | 142.674 | 0.06105 | 0.18315 | 0 | 1.4267 | 0.0006105 | 0.0018315 | 0 | 1.4261 | 0.0018315 | 5.9666 | 82446 | 13821.236
38952.6541 | 2199 | 1 | 38952.6541 | 2 | 0 |  | 2201.5 | 2363.5 | 134.2491 | 0.06105 | 0.1221 | 0 | 1.3425 | 0.0006105 | 0.001221 | 0 | 1.3419 | 0.001221 | 12.6197 | 123719 | 27615.6787
38952.6562 | 2396 | 1 | 38952.6562 | 3 | 0 |  | 2386.5 | 2548.5 | 146.2759 | 0.06105 | 0.18315 | 0 | 1.4628 | 0.0006105 | 0.0018315 | 0 | 1.4621 | 0.0018315 | 3.3562 | 82446 | 7928.3835

## D7-D8
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 148.1306 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38952.6284 | 1 | 0 | 38952.6284 | 1 | 0 |  | -18.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38952.6305 | 1 | 0 | 38952.6305 | 1 | 0 |  | 166.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38952.6327 | 1 | 0 | 38952.6327 | 1 | 0 |  | 351 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38952.6348 | 1 | 0 | 38952.6348 | 1 | 0 |  | 535.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38952.6369 | 1 | 0 | 38952.6369 | 1 | 0 |  | 720.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38952.6391 | 1 | 0 | 38952.6391 | 1 | 0 |  | 905.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242538 | 242538 | 242537.9994
38952.6412 | 1074 | 1037 | 38952.6412 | 1166 | 1129 |  | 1090 | 1252 | 65.5678 | 63.3089 | 71.1844 | 68.9255 | 0.65568 | 0.63309 | 0.71184 | 0.68926 | 0.022589 | 0.022589 | 6457.7838 | 6457.7838 | 29.949
38952.6433 | 913 | 876 | 38952.6434 | 964 | 962 |  | 1275 | 1437 | 55.7387 | 53.4799 | 58.8523 | 58.7302 | 0.55739 | 0.5348 | 0.58852 | 0.5873 | 0.022589 | 0.001221 | 2617.5091 | 4207.9852 | 71.0713
38952.6455 | 2410 | 0 | 38952.6455 | 1875 | 0 |  | 1459.5 | 1621.5 | 147.1306 | 0 | 114.4689 | 0 | 1.4713 | 0 | 1.1447 | 0 | 1.4713 | 1.1447 | 0.67967 | 29.4069 | 0.79164
38952.6476 | 2017 | 0 | 38952.6476 | 2009 | 0 |  | 1644.5 | 1806.5 | 123.138 | 0 | 122.6496 | 0 | 1.2314 | 0 | 1.2265 | 0 | 1.2314 | 1.2265 | 20.2965 | 20.7755 | 19.0651
38952.6498 | 2105 | 0 | 38952.6498 | 1664 | 0 |  | 1829 | 1991 | 128.5104 | 0 | 101.5873 | 0 | 1.2851 | 0 | 1.0159 | 0 | 1.2851 | 1.0159 | 15.2675 | 45.8161 | 13.9824
38952.6519 | 1998 | 0 | 38952.6519 | 2150 | 0 |  | 2014 | 2176 | 121.978 | 0 | 131.2576 | 0 | 1.2198 | 0 | 1.3126 | 0 | 1.2198 | 1.3126 | 21.4404 | 12.8549 | 20.2207
38952.654 | 2080 | 0 | 38952.6541 | 1387 | 0 |  | 2198.5 | 2360.5 | 126.9841 | 0 | 84.6764 | 0 | 1.2698 | 0 | 0.84676 | 0 | 1.2698 | 0.84676 | 16.6529 | 74.9373 | 15.383
38952.6562 | 2353 | 0 | 38952.6562 | 2354 | 0 |  | 2383.5 | 2545.5 | 143.6508 | 0 | 143.7118 | 0 | 1.4365 | 0 | 1.4371 | 0 | 1.4365 | 1.4371 | 3.1186 | 3.0748 | 1.6821

## C6-F12
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38952.6283 | 1 | 0 | 38952.6284 | 1 | 0 |  | -21.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6305 | 1 | 0 | 38952.6305 | 1 | 0 |  | 163.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6326 | 1 | 0 | 38952.6326 | 1 | 0 |  | 348.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6348 | 1 | 0 | 38952.6348 | 1 | 0 |  | 533 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6369 | 1 | 0 | 38952.6369 | 1 | 0 |  | 718 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.639 | 1 | 0 | 38952.6391 | 1 | 0 |  | 902.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6412 | 1 | 0 | 38952.6412 | 1 | 0 |  | 1087.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6433 | 3 | 0 |  | 1725 | 0 |  | 1271 | 1433 | 0.18315 | 0 | 105.3114 | 0 | 0.0018315 | 0 | 1.0531 | 0 | 0.0018315 | 1.0531 | 70334 | 22.4939 | 70333.9982
38952.6455 | 3 | 0 | 38952.6455 | 1466 | 0 |  | 1457 | 1619 | 0.18315 | 0 | 89.4994 | 0 | 0.0018315 | 0 | 0.89499 | 0 | 0.0018315 | 0.89499 | 70334 | 44.1351 | 70333.9982
38952.6476 | 3 | 0 | 38952.6476 | 1609 | 0 |  | 1641.5 | 1803.5 | 0.18315 | 0 | 98.2295 | 0 | 0.0018315 | 0 | 0.9823 | 0 | 0.0018315 | 0.9823 | 70334 | 31.325 | 70333.9982
38952.6497 | 2 | 0 | 38952.6497 | 1344 | 0 |  | 1826.5 | 1988.5 | 0.1221 | 0 | 82.0513 | 0 | 0.001221 | 0 | 0.82051 | 0 | 0.001221 | 0.82051 | 105551 | 57.2188 | 105550.9988
38952.6519 | 3 | 0 | 38952.6519 | 1768 | 0 |  | 2011 | 2173 | 0.18315 | 0 | 107.9365 | 0 | 0.0018315 | 0 | 1.0794 | 0 | 0.0018315 | 1.0794 | 70334 | 19.5147 | 70333.9982
38952.654 | 2 | 0 | 38952.654 | 1 | 0 |  | 2196 | 2358 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.6561 | 1 | 0 | 38952.6562 | 2 | 0 |  | 2380.5 | 2542.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994

## C6-F11
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 139.1563 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38952.6283 | 1 | 0 | 38952.6283 | 1 | 0 |  | -24 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227838 | 227838 | 227837.9994
38952.6305 | 1 | 0 | 38952.6305 | 1 | 0 |  | 160.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227838 | 227838 | 227837.9994
38952.6326 | 1 | 0 | 38952.6326 | 1 | 0 |  | 345.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227838 | 227838 | 227837.9994
38952.6347 | 1 | 0 | 38952.6347 | 1 | 0 |  | 530 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227838 | 227838 | 227837.9994
38952.6369 | 1 | 0 | 38952.6369 | 1 | 0 |  | 715 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227838 | 227838 | 227837.9994
38952.639 | 1 | 0 | 38952.639 | 1 | 0 |  | 899.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227838 | 227838 | 227837.9994
38952.6411 | 1 | 0 | 38952.6412 | 1 | 0 |  | 1084.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227838 | 227838 | 227837.9994
38952.6433 | 1 | 0 | 38952.6433 | 2192 | 0 |  | 1269.5 | 1431.5 | 0.06105 | 0 | 133.8217 | 0 | 0.0006105 | 0 | 1.3382 | 0 | 0.0006105 | 1.3382 | 227838 | 3.9863 | 227837.9994
38952.6454 | 2 | 0 | 38952.6454 | 1933 | 0 |  | 1454 | 1616 | 0.1221 | 0 | 118.0098 | 0 | 0.001221 | 0 | 1.1801 | 0 | 0.001221 | 1.1801 | 113869 | 17.9193 | 113868.9988
38952.6476 | 2 | 0 | 38952.6476 | 2263 | 0 |  | 1639 | 1801 | 0.1221 | 0 | 138.1563 | 0 | 0.001221 | 0 | 1.3816 | 0 | 0.001221 | 1.3816 | 113869 | 0.72382 | 113868.9988
38952.6497 | 2 | 0 | 38952.6497 | 2167 | 0 |  | 1823.5 | 1985.5 | 0.1221 | 0 | 132.2955 | 0 | 0.001221 | 0 | 1.323 | 0 | 0.001221 | 1.323 | 113869 | 5.186 | 113868.9988
38952.6518 | 2 | 0 | 38952.6519 | 1647 | 0 |  | 2008.5 | 2170.5 | 0.1221 | 0 | 100.5495 | 0 | 0.001221 | 0 | 1.0055 | 0 | 0.001221 | 1.0055 | 113869 | 38.3959 | 113868.9988
38952.654 | 2 | 0 | 38952.654 | 2 | 0 |  | 2193 | 2355 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113869 | 113869 | 113868.9988
38952.6561 | 2 | 0 | 38952.6561 | 2 | 0 |  | 2378 | 2540 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 113869 | 113869 | 113868.9988

## C6-E10
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38952.6283 | 1 | 0 | 38952.6283 | 1 | 0 |  | -27 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6304 | 1 | 0 | 38952.6304 | 1 | 0 |  | 158 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6326 | 1 | 0 | 38952.6326 | 1 | 0 |  | 342.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6347 | 1 | 0 | 38952.6347 | 1 | 0 |  | 527.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6368 | 1 | 0 | 38952.6369 | 1 | 0 |  | 712.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.639 | 1 | 0 | 38952.639 | 1 | 0 |  | 897 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6411 | 1 | 0 | 38952.6411 | 1 | 0 |  | 1081.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6433 | 1 | 0 | 38952.6433 | 2 | 0 |  | 1266.5 | 1428.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.6454 | 2 | 0 | 38952.6454 | 2 | 0 |  | 1451.5 | 1613.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6475 | 3 | 0 | 38952.6475 | 2 | 0 |  | 1636 | 1798 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6497 | 2 | 0 | 38952.6497 | 2 | 1 |  | 1821 | 1983 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.6518 | 2 | 0 | 38952.6518 | 2 | 0 |  | 2005.5 | 2167.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6539 | 2 | 0 | 38952.654 | 2 | 0 |  | 2190.5 | 2352.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6561 | 2 | 0 | 38952.6561 | 2 | 0 |  | 2375 | 2537 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## C6-E9
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38952.6283 | 1 | 0 | 38952.6283 | 1 | 0 |  | -29.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6304 | 1 | 0 | 38952.6304 | 1 | 0 |  | 155 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6325 | 1 | 0 | 38952.6325 | 1 | 0 |  | 339.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6347 | 1 | 0 | 38952.6347 | 1 | 0 |  | 524.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6368 | 1 | 0 | 38952.6368 | 1 | 0 |  | 709.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6389 | 1 | 0 | 38952.639 | 1 | 0 |  | 894 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6411 | 1 | 0 | 38952.6411 | 1 | 0 |  | 1079 | 1241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6432 | 1 | 0 | 38952.6432 | 2 | 0 |  | 1263.5 | 1425.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.6454 | 3 | 0 | 38952.6454 | 2 | 0 |  | 1448.5 | 1610.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6475 | 2 | 0 | 38952.6475 | 2 | 0 |  | 1633.5 | 1795.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6496 | 3 | 0 | 38952.6497 | 2 | 0 |  | 1818 | 1980 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6518 | 2 | 0 | 38952.6518 | 2 | 0 |  | 2003 | 2165 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6539 | 3 | 0 | 38952.6539 | 2 | 0 |  | 2187.5 | 2349.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6561 | 2 | 0 | 38952.6561 | 2 | 0 |  | 2372.5 | 2534.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## C5-F12
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 147.0317 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38952.6281 | 1 | 0 | 38952.6282 | 1 | 0 |  | -38 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994
38952.6303 | 1 | 0 | 38952.6303 | 1 | 0 |  | 146.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994
38952.6324 | 1 | 0 | 38952.6324 | 1 | 0 |  | 331.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994
38952.6346 | 1 | 0 | 38952.6346 | 1 | 0 |  | 516 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994
38952.6367 | 1 | 0 | 38952.6367 | 1 | 0 |  | 701 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994
38952.6388 | 1 | 0 | 38952.6389 | 1 | 0 |  | 886 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994
38952.641 | 1 | 0 | 38952.641 | 1 | 0 |  | 1070.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994
38952.6431 | 3 | 0 | 38952.6431 | 2161 | 0 |  | 1255.5 | 1417.5 | 0.18315 | 0 | 131.9292 | 0 | 0.0018315 | 0 | 1.3193 | 0 | 0.0018315 | 1.3193 | 80179.3333 | 11.4475 | 80179.3315
38952.6453 | 3 | 0 | 38952.6453 | 1736 | 0 |  | 1440 | 1602 | 0.18315 | 0 | 105.9829 | 0 | 0.0018315 | 0 | 1.0598 | 0 | 0.0018315 | 1.0598 | 80179.3333 | 38.7316 | 80179.3315
38952.6474 | 3 | 0 | 38952.6474 | 2392 | 0 |  | 1625 | 1787 | 0.18315 | 0 | 146.0317 | 0 | 0.0018315 | 0 | 1.4603 | 0 | 0.0018315 | 1.4603 | 80179.3333 | 0.68478 | 80179.3315
38952.6495 | 3 | 0 | 38952.6495 | 1716 | 0 |  | 1809.5 | 1971.5 | 0.18315 | 0 | 104.7619 | 0 | 0.0018315 | 0 | 1.0476 | 0 | 0.0018315 | 1.0476 | 80179.3333 | 40.3485 | 80179.3315
38952.6517 | 2 | 1 | 38952.6517 | 1356 | 0 |  | 1994.5 | 2156.5 | 0.1221 | 0.06105 | 82.7839 | 0 | 0.001221 | 0.0006105 | 0.82784 | 0 | 0.0006105 | 0.82784 | 834077.526 | 140.5497 | 140542.8675
38952.6538 | 2 | 0 | 38952.6538 | 2 | 0 |  | 2179 | 2341 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 120319 | 120319 | 120318.9988
38952.6559 | 1 | 0 | 38952.656 | 1 | 0 |  | 2364 | 2526 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240738 | 240738 | 240737.9994

## C5-F11
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38952.6281 | 1 | 0 | 38952.6281 | 1 | 0 |  | -41 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6303 | 1 | 0 | 38952.6303 | 1 | 0 |  | 143.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6324 | 1 | 0 | 38952.6324 | 1 | 0 |  | 328.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6345 | 1 | 0 | 38952.6345 | 1 | 0 |  | 513.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6367 | 1 | 0 | 38952.6367 | 1 | 0 |  | 698.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6388 | 1 | 0 | 38952.6388 | 1 | 0 |  | 883 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6409 | 1 | 0 | 38952.641 | 1 | 0 |  | 1067.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6431 | 1 | 0 | 38952.6431 | 1941 | 0 |  | 1252.5 | 1414.5 | 0.06105 | 0 | 118.4982 | 0 | 0.0006105 | 0 | 1.185 | 0 | 0.0006105 | 1.185 | 211202 | 8.8624 | 211201.9994
38952.6452 | 2 | 0 | 38952.6452 | 2013 | 0 |  | 1437.5 | 1599.5 | 0.1221 | 0 | 122.8938 | 0 | 0.001221 | 0 | 1.2289 | 0 | 0.001221 | 1.2289 | 105551 | 4.9687 | 105550.9988
38952.6474 | 2 | 0 | 38952.6474 | 2021 | 0 |  | 1622 | 1784 | 0.1221 | 0 | 123.3822 | 0 | 0.001221 | 0 | 1.2338 | 0 | 0.001221 | 1.2338 | 105551 | 4.5532 | 105550.9988
38952.6495 | 2 | 0 | 38952.6495 | 1984 | 0 |  | 1806.5 | 1968.5 | 0.1221 | 0 | 121.1233 | 0 | 0.001221 | 0 | 1.2112 | 0 | 0.001221 | 1.2112 | 105551 | 6.503 | 105550.9988
38952.6516 | 3 | 0 | 38952.6517 | 989 | 0 |  | 1991.5 | 2153.5 | 0.18315 | 0 | 60.3785 | 0 | 0.0018315 | 0 | 0.60379 | 0 | 0.0018315 | 0.60379 | 70334 | 113.6522 | 70333.9982
38952.6538 | 2 | 0 | 38952.6538 | 3 | 0 |  | 2176.5 | 2338.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.6559 | 1 | 0 | 38952.6559 | 1 | 0 |  | 2361 | 2523 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C5-E10
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38952.6281 | 1 | 0 | 38952.6281 | 1 | 0 |  | -43.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6302 | 1 | 0 | 38952.6302 | 1 | 0 |  | 141 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6324 | 1 | 0 | 38952.6324 | 1 | 0 |  | 326 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6345 | 1 | 0 | 38952.6345 | 2 | 0 |  | 510.5 | 672.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.6366 | 1 | 0 | 38952.6367 | 1 | 0 |  | 695.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6388 | 1 | 0 | 38952.6388 | 1 | 0 |  | 880 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6409 | 1 | 0 | 38952.6409 | 1 | 0 |  | 1065 | 1227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6431 | 1 | 0 | 38952.6431 | 1 | 0 |  | 1249.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6452 | 2 | 0 | 38952.6452 | 2 | 0 |  | 1434.5 | 1596.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6473 | 2 | 0 | 38952.6473 | 3 | 0 |  | 1619 | 1781 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.6495 | 2 | 0 | 38952.6495 | 2 | 0 |  | 1804 | 1966 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6516 | 2 | 0 | 38952.6516 | 2 | 0 |  | 1989 | 2151 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6537 | 2 | 0 | 38952.6538 | 2 | 0 |  | 2173.5 | 2335.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6559 | 2 | 0 | 38952.6559 | 2 | 0 |  | 2358.5 | 2520.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## C5-E9
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38952.6281 | 1 | 0 | 38952.6281 | 1 | 0 |  | -46.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6302 | 1 | 0 | 38952.6302 | 1 | 0 |  | 138.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6323 | 1 | 0 | 38952.6323 | 1 | 0 |  | 323 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6345 | 1 | 0 | 38952.6345 | 1 | 0 |  | 507.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6366 | 1 | 0 | 38952.6366 | 1 | 0 |  | 692.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6387 | 1 | 0 | 38952.6388 | 1 | 0 |  | 877.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6409 | 1 | 0 | 38952.6409 | 1 | 0 |  | 1062 | 1224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.643 | 2 | 0 | 38952.643 | 1 | 0 |  | 1247 | 1409 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.6452 | 3 | 0 | 38952.6452 | 2 | 0 |  | 1431.5 | 1593.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6473 | 3 | 0 | 38952.6473 | 3 | 0 |  | 1616.5 | 1778.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.6494 | 3 | 1 | 38952.6495 | 2 | 0 |  | 1801 | 1963 | 0.18315 | 0.06105 | 0.1221 | 0 | 0.0018315 | 0.0006105 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 210702.3786
38952.6516 | 3 | 0 | 38952.6516 | 2 | 0 |  | 1986 | 2148 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6537 | 3 | 1 | 38952.6537 | 2 | 0 |  | 2170.5 | 2332.5 | 0.18315 | 0.06105 | 0.1221 | 0 | 0.0018315 | 0.0006105 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 210702.3786
38952.6559 | 3 | 1 | 38952.6559 | 2 | 0 |  | 2355.5 | 2517.5 | 0.18315 | 0.06105 | 0.1221 | 0 | 0.0018315 | 0.0006105 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 210702.3786

## C5-C6
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38952.628 | 1 | 0 | 38952.628 | 1 | 0 |  | -55 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6301 | 1 | 0 | 38952.6301 | 1 | 0 |  | 130 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6322 | 1 | 0 | 38952.6322 | 1 | 0 |  | 314.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6344 | 1 | 0 | 38952.6344 | 1 | 0 |  | 499.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6365 | 1 | 0 | 38952.6365 | 1 | 0 |  | 684.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6386 | 1 | 0 | 38952.6387 | 1 | 0 |  | 869 | 1031 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6408 | 1 | 0 | 38952.6408 | 1 | 0 |  | 1053.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6429 | 3 | 0 | 38952.6429 | 2 | 0 |  | 1238.5 | 1400.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6451 | 956 | 927 | 38952.6451 | 1026 | 1069 |  | 1423.5 | 1585.5 | 58.3639 | 56.5934 | 62.6374 | 65.2625 | 0.58364 | 0.56593 | 0.62637 | 0.65263 | 0.017705 | 0.026252 | 3199.3216 | 12938.7202 | 24.6231
38952.6472 | 1085 | 1054 | 38952.6472 | 1202 | 1175 |  | 1608 | 1770 | 66.2393 | 64.3468 | 73.3822 | 71.7338 | 0.66239 | 0.64347 | 0.73382 | 0.71734 | 0.018926 | 0.016484 | 139524.5492 | 3482.778 | 2.3961
38952.6493 | 1112 | 1074 | 38952.6494 | 1089 | 1052 |  | 1792.5 | 1954.5 | 67.8877 | 65.5678 | 66.4835 | 64.2247 | 0.67888 | 0.65568 | 0.66484 | 0.64225 | 0.023199 | 0.022589 | 12697.3365 | 3566.1752 | 6.6098
38952.6515 | 1176 | 1199 | 38952.6515 | 1108 | 1079 |  | 1977.5 | 2139.5 | 71.7949 | 73.199 | 67.6435 | 65.873 | 0.71795 | 0.73199 | 0.67643 | 0.65873 | 0.014042 | 0.017705 | 3019.9987 | 14936.7796 | 21.7046
38952.6536 | 1078 | 1170 | 38952.6536 | 1005 | 979 |  | 2162.5 | 2324.5 | 65.812 | 71.4286 | 61.3553 | 59.768 | 0.65812 | 0.71429 | 0.61355 | 0.59768 | 0.056166 | 0.015873 | 1.9476 | 2.2054 | 0.24894
38952.6558 | 993 | 970 | 38952.6558 | 962 | 1084 |  | 2347 | 2509 | 60.6227 | 59.2186 | 58.7302 | 66.1783 | 0.60623 | 0.59219 | 0.5873 | 0.66178 | 0.014042 | 0.074481 | 258.729 | 236.6471 | 10.8719

## B4-E10
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38952.6279 | 1 | 0 | 38952.6279 | 1 | 0 |  | -63.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.63 | 1 | 0 | 38952.63 | 1 | 0 |  | 121.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6321 | 1 | 0 | 38952.6322 | 1 | 0 |  | 306 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6343 | 1 | 0 | 38952.6343 | 1 | 0 |  | 491 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6364 | 1 | 0 | 38952.6364 | 1 | 0 |  | 675.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6386 | 1 | 0 | 38952.6386 | 1 | 0 |  | 860.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6407 | 1 | 0 | 38952.6407 | 1 | 0 |  | 1045.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6428 | 1 | 0 | 38952.6428 | 2 | 0 |  | 1230 | 1392 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.645 | 2 | 0 | 38952.645 | 2 | 0 |  | 1414.5 | 1576.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6471 | 10 | 1 | 38952.6471 | 2 | 0 |  | 1599.5 | 1761.5 | 0.6105 | 0.06105 | 0.1221 | 0 | 0.006105 | 0.0006105 | 0.001221 | 0 | 0.0054945 | 0.001221 | 23369.3489 | 105551 | 210003.0412
38952.6492 | 189 | 1 | 38952.6493 | 2 | 0 |  | 1784.5 | 1946.5 | 11.5385 | 0.06105 | 0.1221 | 0 | 0.11538 | 0.0006105 | 0.001221 | 0 | 0.11477 | 0.001221 | 1023.4201 | 105551 | 192119.9837
38952.6514 | 72 | 1 | 38952.6514 | 2 | 0 |  | 1969 | 2131 | 4.3956 | 0.06105 | 0.1221 | 0 | 0.043956 | 0.0006105 | 0.001221 | 0 | 0.043346 | 0.001221 | 2874.7144 | 105551 | 203808.9095
38952.6535 | 16 | 1 | 38952.6535 | 2 | 0 |  | 2154 | 2316 | 0.9768 | 0.06105 | 0.1221 | 0 | 0.009768 | 0.0006105 | 0.001221 | 0 | 0.0091575 | 0.001221 | 13981.0164 | 105551 | 209403.6091
38952.6557 | 2 | 0 | 38952.6557 | 1 | 0 |  | 2338.5 | 2500.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## B4-E9
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38952.6278 | 1 | 0 | 38952.6278 | 1 | 0 |  | -66 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.63 | 1 | 0 | 38952.63 | 1 | 0 |  | 118.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6321 | 1 | 0 | 38952.6321 | 1 | 0 |  | 303.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6342 | 1 | 0 | 38952.6343 | 1 | 0 |  | 488 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6364 | 1 | 0 | 38952.6364 | 1 | 0 |  | 673 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6385 | 1 | 0 | 38952.6385 | 1 | 0 |  | 857.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6407 | 1 | 0 | 38952.6407 | 1 | 0 |  | 1042.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6428 | 1 | 0 | 38952.6428 | 1 | 0 |  | 1227.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6449 | 3 | 0 | 38952.645 | 2 | 0 |  | 1412 | 1574 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6471 | 9 | 1 | 38952.6471 | 2 | 0 |  | 1597 | 1759 | 0.54945 | 0.06105 | 0.1221 | 0 | 0.0054945 | 0.0006105 | 0.001221 | 0 | 0.004884 | 0.001221 | 26303.365 | 105551 | 210102.9465
38952.6492 | 178 | 1 | 38952.6492 | 2 | 0 |  | 1781.5 | 1943.5 | 10.8669 | 0.06105 | 0.1221 | 0 | 0.10867 | 0.0006105 | 0.001221 | 0 | 0.10806 | 0.001221 | 1093.2375 | 105551 | 193218.9426
38952.6514 | 68 | 1 | 38952.6514 | 2 | 0 |  | 1966.5 | 2128.5 | 4.1514 | 0.06105 | 0.1221 | 0 | 0.041514 | 0.0006105 | 0.001221 | 0 | 0.040904 | 0.001221 | 3052.3118 | 105551 | 204208.5309
38952.6535 | 16 | 1 | 38952.6535 | 2 | 0 |  | 2151 | 2313 | 0.9768 | 0.06105 | 0.1221 | 0 | 0.009768 | 0.0006105 | 0.001221 | 0 | 0.0091575 | 0.001221 | 13981.0164 | 105551 | 209403.6091
38952.6556 | 3 | 0 | 38952.6556 | 2 | 0 |  | 2336 | 2498 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982

## B4-D8
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 146.0549 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38952.6278 | 1 | 0 | 38952.6278 | 1 | 0 |  | -69 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6299 | 1 | 0 | 38952.63 | 1 | 0 |  | 116 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6321 | 1 | 0 | 38952.6321 | 1 | 0 |  | 300.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6342 | 1 | 0 | 38952.6342 | 1 | 0 |  | 485.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6364 | 1 | 0 | 38952.6364 | 1 | 0 |  | 670.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6385 | 1 | 0 | 38952.6385 | 1 | 0 |  | 855 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6406 | 1 | 0 | 38952.6406 | 1 | 0 |  | 1039.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6428 | 1 | 0 | 38952.6428 | 1 | 0 |  | 1224.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38952.6449 | 3 | 0 | 38952.6449 | 2376 | 0 |  | 1409 | 1571 | 0.18315 | 0 | 145.0549 | 0 | 0.0018315 | 0 | 1.4505 | 0 | 0.0018315 | 1.4505 | 79646 | 0.68939 | 79645.9982
38952.647 | 8 | 0 | 38952.6471 | 2227 | 0 |  | 1594 | 1756 | 0.4884 | 0 | 135.9585 | 0 | 0.004884 | 0 | 1.3596 | 0 | 0.004884 | 1.3596 | 29804.75 | 7.4261 | 29804.7451
38952.6492 | 174 | 1 | 38952.6492 | 1653 | 0 |  | 1778.5 | 1940.5 | 10.6227 | 0.06105 | 100.9158 | 0 | 0.10623 | 0.0006105 | 1.0092 | 0 | 0.10562 | 1.0092 | 1299.0885 | 44.7296 | 68529.5156
38952.6513 | 67 | 1 | 38952.6513 | 1562 | 0 |  | 1963.5 | 2125.5 | 4.0904 | 0.06105 | 95.3602 | 0 | 0.040904 | 0.0006105 | 0.9536 | 0 | 0.040293 | 0.9536 | 3626.6667 | 53.1613 | 80677.7629
38952.6535 | 18 | 1 | 38952.6535 | 2188 | 0 |  | 2148.5 | 2310.5 | 1.0989 | 0.06105 | 133.5775 | 0 | 0.010989 | 0.0006105 | 1.3358 | 0 | 0.010379 | 1.3358 | 37721.7935 | 9.341 | 20275.6838
38952.6556 | 3 | 0 | 38952.6556 | 1989 | 0 |  | 2333 | 2495 | 0.18315 | 0 | 121.4286 | 0 | 0.0018315 | 0 | 1.2143 | 0 | 0.0018315 | 1.2143 | 79646 | 20.2805 | 79645.9982

## B4-D7
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 147.1538 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38952.6278 | 1 | 0 | 38952.6278 | 1 | 0 |  | -71.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.6299 | 1 | 0 | 38952.6299 | 1 | 0 |  | 113 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.632 | 1 | 0 | 38952.632 | 1 | 0 |  | 297.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.6342 | 1 | 0 | 38952.6342 | 1 | 0 |  | 482.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.6363 | 1 | 0 | 38952.6363 | 1 | 0 |  | 667.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.6384 | 1 | 0 | 38952.6385 | 1 | 0 |  | 852 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.6406 | 1 | 0 | 38952.6406 | 1 | 0 |  | 1037 | 1199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.6427 | 2 | 0 | 38952.6427 | 1 | 0 |  | 1221.5 | 1383.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 120419 | 240938 | 120418.9988
38952.6449 | 2 | 0 | 38952.6449 | 2336 | 0 |  | 1406.5 | 1568.5 | 0.1221 | 0 | 142.6129 | 0 | 0.001221 | 0 | 1.4261 | 0 | 0.001221 | 1.4261 | 120419 | 3.1841 | 120418.9988
38952.647 | 7 | 0 | 38952.647 | 2153 | 0 |  | 1591.5 | 1753.5 | 0.42735 | 0 | 131.4408 | 0 | 0.0042735 | 0 | 1.3144 | 0 | 0.0042735 | 1.3144 | 34334 | 11.9545 | 34333.9957
38952.6491 | 191 | 1 | 38952.6492 | 2162 | 0 |  | 1776 | 1938 | 11.6606 | 0.06105 | 131.9902 | 0 | 0.11661 | 0.0006105 | 1.3199 | 0 | 0.116 | 1.3199 | 1224.1776 | 11.4884 | 22859.5169
38952.6513 | 66 | 1 | 38952.6513 | 2394 | 0 |  | 1960.5 | 2122.5 | 4.0293 | 0.06105 | 146.1538 | 0 | 0.040293 | 0.0006105 | 1.4615 | 0 | 0.039683 | 1.4615 | 2888.8095 | 6.1905 | 13660.9596
38952.6534 | 15 | 1 | 38952.6534 | 2271 | 0 |  | 2145.5 | 2307.5 | 0.91575 | 0.06105 | 138.6447 | 0 | 0.0091575 | 0.0006105 | 1.3864 | 0 | 0.008547 | 1.3864 | 104438.2083 | 8.5423 | 18843.8688
38952.6556 | 2 | 0 | 38952.6556 | 2153 | 0 |  | 2330.5 | 2492.5 | 0.1221 | 0 | 131.4408 | 0 | 0.001221 | 0 | 1.3144 | 0 | 0.001221 | 1.3144 | 120419 | 11.9545 | 120418.9988

## B4-C6
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38952.6277 | 1 | 0 | 38952.6277 | 1 | 0 |  | -74.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6299 | 1 | 0 | 38952.6299 | 1 | 0 |  | 110.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.632 | 1 | 0 | 38952.632 | 1 | 0 |  | 295 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6341 | 1 | 0 | 38952.6342 | 1 | 0 |  | 479.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6363 | 1 | 0 | 38952.6363 | 1 | 0 |  | 664.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6384 | 1 | 0 | 38952.6384 | 1 | 0 |  | 849.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6406 | 1 | 0 | 38952.6406 | 1 | 0 |  | 1034 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6427 | 2 | 0 | 38952.6427 | 2 | 0 |  | 1219 | 1381 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6448 | 2 | 0 | 38952.6448 | 2 | 0 |  | 1403.5 | 1565.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.647 | 6 | 0 | 38952.647 | 2 | 0 |  | 1588.5 | 1750.5 | 0.3663 | 0 | 0.1221 | 0 | 0.003663 | 0 | 0.001221 | 0 | 0.003663 | 0.001221 | 35117 | 105551 | 35116.9963
38952.6491 | 173 | 1 | 38952.6491 | 2 | 0 |  | 1773.5 | 1935.5 | 10.5617 | 0.06105 | 0.1221 | 0 | 0.10562 | 0.0006105 | 0.001221 | 0 | 0.10501 | 0.001221 | 1127.9248 | 105551 | 193718.4693
38952.6513 | 69 | 1 | 38952.6513 | 2 | 0 |  | 1958 | 2120 | 4.2125 | 0.06105 | 0.1221 | 0 | 0.042125 | 0.0006105 | 0.001221 | 0 | 0.041514 | 0.001221 | 3005.9536 | 105551 | 204108.6256
38952.6534 | 15 | 1 | 38952.6534 | 2 | 0 |  | 2142.5 | 2304.5 | 0.91575 | 0.06105 | 0.1221 | 0 | 0.0091575 | 0.0006105 | 0.001221 | 0 | 0.008547 | 0.001221 | 14986.8713 | 105551 | 209503.5144
38952.6555 | 2 | 0 | 38952.6555 | 1 | 0 |  | 2327.5 | 2489.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## B4-C5
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38952.6277 | 1 | 0 | 38952.6277 | 1 | 0 |  | -77.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6298 | 1 | 0 | 38952.6298 | 1 | 0 |  | 107.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.632 | 1 | 0 | 38952.632 | 1 | 0 |  | 292.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6341 | 1 | 0 | 38952.6341 | 1 | 0 |  | 477 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6363 | 1 | 0 | 38952.6363 | 1 | 0 |  | 661.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6384 | 1 | 0 | 38952.6384 | 1 | 0 |  | 846.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6405 | 1 | 0 | 38952.6405 | 1 | 0 |  | 1031.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6427 | 3 | 0 | 38952.6427 | 2 | 0 |  | 1216 | 1378 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6448 | 3 | 0 | 38952.6448 | 2 | 0 |  | 1401 | 1563 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6469 | 5 | 0 | 38952.647 | 2 | 0 |  | 1585.5 | 1747.5 | 0.30525 | 0 | 0.1221 | 0 | 0.0030525 | 0 | 0.001221 | 0 | 0.0030525 | 0.001221 | 42160.4 | 105551 | 42160.3969
38952.6491 | 148 | 1 | 38952.6491 | 2 | 0 |  | 1770.5 | 1932.5 | 9.0354 | 0.06105 | 0.1221 | 0 | 0.090354 | 0.0006105 | 0.001221 | 0 | 0.089744 | 0.001221 | 1336.7569 | 105551 | 196216.103
38952.6512 | 58 | 1 | 38952.6512 | 2 | 0 |  | 1955 | 2117 | 3.5409 | 0.06105 | 0.1221 | 0 | 0.035409 | 0.0006105 | 0.001221 | 0 | 0.034799 | 0.001221 | 3605.3582 | 105551 | 205207.5844
38952.6534 | 14 | 1 | 38952.6534 | 2 | 0 |  | 2140 | 2302 | 0.8547 | 0.06105 | 0.1221 | 0 | 0.008547 | 0.0006105 | 0.001221 | 0 | 0.0079365 | 0.001221 | 16147.4845 | 105551 | 209603.4198
38952.6555 | 2 | 0 | 38952.6555 | 2 | 0 |  | 2324.5 | 2486.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## B3-E10
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38952.6276 | 1 | 0 | 38952.6276 | 1 | 0 |  | -85.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6297 | 1 | 0 | 38952.6298 | 1 | 0 |  | 99 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6319 | 2 | 0 | 38952.6319 | 1 | 0 |  | 284 | 446 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.634 | 1 | 0 | 38952.634 | 1 | 0 |  | 468.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6362 | 1 | 0 | 38952.6362 | 1 | 0 |  | 653.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6383 | 1 | 0 | 38952.6383 | 1 | 0 |  | 838 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6404 | 1 | 0 | 38952.6405 | 1 | 0 |  | 1023 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6426 | 1 | 0 | 38952.6426 | 1 | 0 |  | 1207.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6447 | 2 | 0 | 38952.6447 | 2 | 0 |  | 1392.5 | 1554.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6469 | 3 | 0 | 38952.6469 | 2 | 0 |  | 1577.5 | 1739.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.649 | 146 | 1 | 38952.649 | 2 | 0 |  | 1762 | 1924 | 8.9133 | 0.06105 | 0.1221 | 0 | 0.089133 | 0.0006105 | 0.001221 | 0 | 0.088523 | 0.001221 | 1356.5744 | 105551 | 196415.9137
38952.6511 | 64 | 1 | 38952.6511 | 2 | 0 |  | 1947 | 2109 | 3.9072 | 0.06105 | 0.1221 | 0 | 0.039072 | 0.0006105 | 0.001221 | 0 | 0.038462 | 0.001221 | 3252.4616 | 105551 | 204608.1523
38952.6533 | 17 | 1 | 38952.6533 | 2 | 0 |  | 2131.5 | 2293.5 | 1.0379 | 0.06105 | 0.1221 | 0 | 0.010379 | 0.0006105 | 0.001221 | 0 | 0.009768 | 0.001221 | 13100.9007 | 105551 | 209303.7037
38952.6554 | 2 | 0 | 38952.6554 | 2 | 0 |  | 2316.5 | 2478.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## B3-E9
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38952.6276 | 1 | 0 | 38952.6276 | 1 | 0 |  | -88.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6297 | 1 | 0 | 38952.6297 | 1 | 0 |  | 96.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6318 | 1 | 0 | 38952.6319 | 1 | 0 |  | 281 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.634 | 1 | 0 | 38952.634 | 1 | 0 |  | 465.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6361 | 1 | 0 | 38952.6361 | 1 | 0 |  | 650.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6383 | 1 | 0 | 38952.6383 | 1 | 0 |  | 835.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6404 | 1 | 0 | 38952.6404 | 1 | 0 |  | 1020 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6425 | 1 | 0 | 38952.6426 | 1 | 0 |  | 1205 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6447 | 3 | 0 | 38952.6447 | 3 | 0 |  | 1389.5 | 1551.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.6468 | 4 | 0 | 38952.6468 | 3 | 0 |  | 1574.5 | 1736.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.649 | 130 | 1 | 38952.649 | 2 | 0 |  | 1759.5 | 1921.5 | 7.9365 | 0.06105 | 0.1221 | 0 | 0.079365 | 0.0006105 | 0.001221 | 0 | 0.078755 | 0.001221 | 1537.2361 | 105551 | 198014.3993
38952.6511 | 60 | 1 | 38952.6511 | 2 | 0 |  | 1944 | 2106 | 3.663 | 0.06105 | 0.1221 | 0 | 0.03663 | 0.0006105 | 0.001221 | 0 | 0.03602 | 0.001221 | 3479.7508 | 105551 | 205007.7737
38952.6532 | 14 | 1 | 38952.6532 | 2 | 0 |  | 2128.5 | 2290.5 | 0.8547 | 0.06105 | 0.1221 | 0 | 0.008547 | 0.0006105 | 0.001221 | 0 | 0.0079365 | 0.001221 | 16147.4845 | 105551 | 209603.4198
38952.6554 | 3 | 0 | 38952.6554 | 2 | 0 |  | 2313.5 | 2475.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982

## B3-D8
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 136.348 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38952.6275 | 1 | 0 | 38952.6275 | 1 | 0 |  | -91.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6297 | 1 | 0 | 38952.6297 | 1 | 0 |  | 93.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6318 | 1 | 0 | 38952.6318 | 1 | 0 |  | 278 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6339 | 1 | 0 | 38952.634 | 1 | 0 |  | 463 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6361 | 1 | 0 | 38952.6361 | 1 | 0 |  | 647.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6382 | 1 | 0 | 38952.6382 | 1 | 0 |  | 832.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6404 | 1 | 0 | 38952.6404 | 1 | 0 |  | 1017.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6425 | 1 | 0 | 38952.6425 | 1 | 0 |  | 1202 | 1364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223238 | 223238 | 223237.9994
38952.6446 | 3 | 0 | 38952.6447 | 1920 | 0 |  | 1387 | 1549 | 0.18315 | 0 | 117.2161 | 0 | 0.0018315 | 0 | 1.1722 | 0 | 0.0018315 | 1.1722 | 74346 | 16.3219 | 74345.9982
38952.6468 | 3 | 0 | 38952.6468 | 1912 | 0 |  | 1571.5 | 1733.5 | 0.18315 | 0 | 116.7277 | 0 | 0.0018315 | 0 | 1.1673 | 0 | 0.0018315 | 1.1673 | 74346 | 16.8086 | 74345.9982
38952.6489 | 136 | 1 | 38952.6489 | 1825 | 0 |  | 1756.5 | 1918.5 | 8.3028 | 0.06105 | 111.4164 | 0 | 0.083028 | 0.0006105 | 1.1142 | 0 | 0.082418 | 1.1142 | 1606.8045 | 22.377 | 38332.9153
38952.6511 | 51 | 1 | 38952.6511 | 2217 | 0 |  | 1941.5 | 2103.5 | 3.1136 | 0.06105 | 135.348 | 0 | 0.031136 | 0.0006105 | 1.3535 | 0 | 0.030525 | 1.3535 | 2557.0375 | 2.829 | 6001.378
38952.6532 | 15 | 1 | 38952.6532 | 1858 | 0 |  | 2126 | 2288 | 0.91575 | 0.06105 | 113.431 | 0 | 0.0091575 | 0.0006105 | 1.1343 | 0 | 0.008547 | 1.1343 | 24511.541 | 20.2034 | 37269.0767
38952.6553 | 3 | 0 | 38952.6553 | 1817 | 0 |  | 2310.5 | 2472.5 | 0.18315 | 0 | 110.928 | 0 | 0.0018315 | 0 | 1.1093 | 0 | 0.0018315 | 1.1093 | 74346 | 22.9158 | 74345.9982

## B3-D7
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 153.3199 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38952.6275 | 1 | 0 | 38952.6275 | 1 | 0 |  | -94 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6296 | 1 | 0 | 38952.6297 | 1 | 0 |  | 90.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6318 | 1 | 0 | 38952.6318 | 1 | 0 |  | 275.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6339 | 1 | 0 | 38952.6339 | 1 | 0 |  | 460 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6361 | 1 | 0 | 38952.6361 | 1 | 0 |  | 645 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6382 | 1 | 0 | 38952.6382 | 1 | 0 |  | 829.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6403 | 1 | 0 | 38952.6403 | 1 | 0 |  | 1014.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6425 | 1 | 0 | 38952.6425 | 1 | 0 |  | 1199.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251038 | 251038 | 251037.9994
38952.6446 | 2 | 0 | 38952.6446 | 2350 | 0 |  | 1384 | 1546 | 0.1221 | 0 | 143.4676 | 0 | 0.001221 | 0 | 1.4347 | 0 | 0.001221 | 1.4347 | 125469 | 6.8672 | 125468.9988
38952.6467 | 3 | 0 | 38952.6468 | 2495 | 0 |  | 1569 | 1731 | 0.18315 | 0 | 152.3199 | 0 | 0.0018315 | 0 | 1.5232 | 0 | 0.0018315 | 1.5232 | 83612.6667 | 0.65651 | 83612.6648
38952.6489 | 141 | 1 | 38952.6489 | 2281 | 0 |  | 1753.5 | 1915.5 | 8.6081 | 0.06105 | 139.2552 | 0 | 0.086081 | 0.0006105 | 1.3926 | 0 | 0.08547 | 1.3926 | 1821.9822 | 10.1 | 21735.3712
38952.651 | 55 | 1 | 38952.651 | 2477 | 0 |  | 1938.5 | 2100.5 | 3.3578 | 0.06105 | 151.221 | 0 | 0.033578 | 0.0006105 | 1.5122 | 0 | 0.032967 | 1.5122 | 13610.4861 | 2.7815 | 6644.7289
38952.6532 | 18 | 1 | 38952.6532 | 2437 | 0 |  | 2123 | 2285 | 1.0989 | 0.06105 | 148.779 | 0 | 0.010989 | 0.0006105 | 1.4878 | 0 | 0.010379 | 1.4878 | 15816.7401 | 80.9182 | 111475.18
38952.6553 | 2 | 0 | 38952.6553 | 2089 | 0 |  | 2308 | 2470 | 0.1221 | 0 | 127.5336 | 0 | 0.001221 | 0 | 1.2753 | 0 | 0.001221 | 1.2753 | 125469 | 20.2192 | 125468.9988

## B3-C6
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38952.6275 | 1 | 0 | 38952.6275 | 1 | 0 |  | -97 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6296 | 1 | 0 | 38952.6296 | 1 | 0 |  | 88 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6317 | 1 | 0 | 38952.6318 | 1 | 0 |  | 272.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6339 | 1 | 0 | 38952.6339 | 1 | 0 |  | 457.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.636 | 1 | 0 | 38952.636 | 1 | 0 |  | 642 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6382 | 1 | 0 | 38952.6382 | 1 | 0 |  | 827 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6403 | 1 | 0 | 38952.6403 | 1 | 0 |  | 1011.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6424 | 2 | 0 | 38952.6425 | 1 | 0 |  | 1196.5 | 1358.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.6446 | 2 | 1 | 38952.6446 | 2 | 1 |  | 1381.5 | 1543.5 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38952.6467 | 3 | 1 | 38952.6467 | 2 | 1 |  | 1566 | 1728 | 0.18315 | 0.06105 | 0.1221 | 0.06105 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 105525.9704 | 211302.2372 | 210802.2366
38952.6489 | 125 | 1 | 38952.6489 | 2 | 0 |  | 1751 | 1913 | 7.6313 | 0.06105 | 0.1221 | 0 | 0.076313 | 0.0006105 | 0.001221 | 0 | 0.075702 | 0.001221 | 1603.2542 | 105551 | 198513.9261
38952.651 | 52 | 1 | 38952.651 | 2 | 0 |  | 1935.5 | 2097.5 | 3.1746 | 0.06105 | 0.1221 | 0 | 0.031746 | 0.0006105 | 0.001221 | 0 | 0.031136 | 0.001221 | 4041.2908 | 105551 | 205807.0165
38952.6531 | 16 | 1 | 38952.6531 | 2 | 0 |  | 2120.5 | 2282.5 | 0.9768 | 0.06105 | 0.1221 | 0 | 0.009768 | 0.0006105 | 0.001221 | 0 | 0.0091575 | 0.001221 | 13981.0164 | 105551 | 209403.6091
38952.6553 | 2 | 1 | 38952.6553 | 2 | 0 |  | 2305 | 2467 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211302.1897 | 105551 | 210802.284

## B3-C5
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38952.6274 | 1 | 0 | 38952.6275 | 1 | 0 |  | -99.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6296 | 1 | 0 | 38952.6296 | 1 | 0 |  | 85 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6317 | 1 | 0 | 38952.6317 | 1 | 0 |  | 269.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6339 | 1 | 0 | 38952.6339 | 1 | 0 |  | 454.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.636 | 1 | 0 | 38952.636 | 1 | 0 |  | 639.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6381 | 1 | 0 | 38952.6381 | 1 | 0 |  | 824 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6403 | 1 | 0 | 38952.6403 | 1 | 0 |  | 1009 | 1171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6424 | 2 | 0 | 38952.6424 | 2 | 0 |  | 1193.5 | 1355.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6445 | 3 | 4 | 38952.6446 | 2 | 2 |  | 1378.5 | 1540.5 | 0.18315 | 0.2442 | 0.1221 | 0.1221 | 0.0018315 | 0.002442 | 0.001221 | 0.001221 | 0.0006105 | 0 | 211001.621 | 222714321.0475 | 52650.4764
38952.6467 | 3 | 4 | 38952.6467 | 2 | 1 |  | 1563.5 | 1725.5 | 0.18315 | 0.2442 | 0.1221 | 0.06105 | 0.0018315 | 0.002442 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211402.3797 | 211201.9052 | 52625.5828
38952.6488 | 115 | 4 | 38952.6488 | 2 | 2 |  | 1748 | 1910 | 7.0208 | 0.2442 | 0.1221 | 0.1221 | 0.070208 | 0.002442 | 0.001221 | 0.001221 | 0.067766 | 0 | 1800.0146 | 1899933.4144 | 49847.8763
38952.651 | 52 | 4 | 38952.651 | 2 | 2 |  | 1933 | 2095 | 3.1746 | 0.2442 | 0.1221 | 0.1221 | 0.031746 | 0.002442 | 0.001221 | 0.001221 | 0.029304 | 0 | 4293.7838 | 4532131.7087 | 51424.3653
38952.6531 | 17 | 3 | 38952.6531 | 2 | 1 |  | 2117.5 | 2279.5 | 1.0379 | 0.18315 | 0.1221 | 0.06105 | 0.010379 | 0.0018315 | 0.001221 | 0.0006105 | 0.008547 | 0.0006105 | 14973.0812 | 212521.3562 | 69734.5204
38952.6552 | 2 | 4 | 38952.6553 | 2 | 2 |  | 2302.5 | 2464.5 | 0.1221 | 0.2442 | 0.1221 | 0.1221 | 0.001221 | 0.002442 | 0.001221 | 0.001221 | 0.001221 | 0 | 105550.8105 | 111409936.0197 | 52675.4527

## B3-B4
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38952.6274 | 1 | 0 | 38952.6274 | 1 | 0 |  | -102.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6295 | 1 | 0 | 38952.6296 | 1 | 0 |  | 82.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6317 | 1 | 0 | 38952.6317 | 1 | 0 |  | 267 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6338 | 1 | 0 | 38952.6338 | 1 | 0 |  | 452 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.636 | 1 | 0 | 38952.636 | 1 | 0 |  | 636.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6381 | 1 | 0 | 38952.6381 | 1 | 0 |  | 821.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6402 | 1 | 0 | 38952.6403 | 1 | 0 |  | 1006 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6424 | 3 | 0 | 38952.6424 | 3 | 0 |  | 1191 | 1353 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.6445 | 1026 | 988 | 38952.6445 | 1180 | 1144 |  | 1375.5 | 1537.5 | 62.6374 | 60.3175 | 72.0391 | 69.8413 | 0.62637 | 0.60317 | 0.72039 | 0.69841 | 0.023199 | 0.021978 | 102490.8156 | 2674.6511 | 9.6611
38952.6467 | 1106 | 1127 | 38952.6467 | 1054 | 998 |  | 1560.5 | 1722.5 | 67.5214 | 68.8034 | 64.3468 | 60.928 | 0.67521 | 0.68803 | 0.64347 | 0.60928 | 0.012821 | 0.034188 | 142.6181 | 164.5026 | 6.6211
38952.6488 | 1261 | 1079 | 38952.6488 | 1277 | 1118 |  | 1745.5 | 1907.5 | 76.9841 | 65.873 | 77.9609 | 68.254 | 0.76984 | 0.65873 | 0.77961 | 0.68254 | 0.11111 | 0.09707 | 2545.7721 | 726.443 | 18.4908
38952.6509 | 1187 | 1132 | 38952.6509 | 1209 | 1141 |  | 1930 | 2092 | 72.4664 | 69.1087 | 73.8095 | 69.6581 | 0.72466 | 0.69109 | 0.7381 | 0.69658 | 0.033578 | 0.041514 | 1667.4851 | 212013.1553 | 18.1875
38952.6531 | 1020 | 927 | 38952.6531 | 1081 | 982 |  | 2114.5 | 2276.5 | 62.2711 | 56.5934 | 65.9951 | 59.9512 | 0.62271 | 0.56593 | 0.65995 | 0.59951 | 0.056777 | 0.06044 | 5177.4494 | 1289.491 | 16.6205
38952.6552 | 1208 | 1151 | 38952.6552 | 1083 | 1137 |  | 2299.5 | 2461.5 | 73.7485 | 70.2686 | 66.1172 | 69.4139 | 0.73748 | 0.70269 | 0.66117 | 0.69414 | 0.034799 | 0.032967 | 10935.6262 | 2362.28 | 20.503

## A2-C6
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38952.6272 | 1 | 0 | 38952.6272 | 1 | 0 |  | -122 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6293 | 1 | 0 | 38952.6293 | 1 | 0 |  | 62.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6315 | 1 | 0 | 38952.6315 | 1 | 0 |  | 247.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6336 | 1 | 0 | 38952.6336 | 1 | 0 |  | 432.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6357 | 1 | 0 | 38952.6358 | 1 | 0 |  | 617 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6379 | 1 | 0 | 38952.6379 | 1 | 0 |  | 801.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.64 | 1 | 0 | 38952.64 | 1 | 0 |  | 986.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6422 | 1 | 0 | 38952.6422 | 1 | 0 |  | 1171.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6443 | 2 | 0 | 38952.6443 | 2 | 0 |  | 1356 | 1518 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6464 | 2 | 0 | 38952.6464 | 2 | 0 |  | 1541 | 1703 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6486 | 2 | 0 | 38952.6486 | 2 | 0 |  | 1725.5 | 1887.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6507 | 2 | 0 | 38952.6507 | 2 | 0 |  | 1910.5 | 2072.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6528 | 2 | 0 | 38952.6529 | 2 | 0 |  | 2095 | 2257 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.655 | 2 | 0 | 38952.655 | 1 | 0 |  | 2280 | 2442 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## A2-C5
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38952.6271 | 1 | 0 | 38952.6272 | 1 | 0 |  | -125 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6293 | 1 | 0 | 38952.6293 | 1 | 0 |  | 60 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6314 | 1 | 0 | 38952.6314 | 1 | 0 |  | 244.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6336 | 2 | 0 | 38952.6336 | 1 | 0 |  | 429.5 | 591.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.6357 | 1 | 0 | 38952.6357 | 1 | 0 |  | 614 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6378 | 1 | 0 | 38952.6379 | 1 | 0 |  | 799 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.64 | 1 | 0 | 38952.64 | 1 | 0 |  | 983.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6421 | 1 | 0 | 38952.6421 | 1 | 0 |  | 1168.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6443 | 2 | 0 | 38952.6443 | 2 | 0 |  | 1353.5 | 1515.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6464 | 2 | 0 | 38952.6464 | 26 | 0 |  | 1538 | 1700 | 0.1221 | 0 | 1.5873 | 0 | 0.001221 | 0 | 0.015873 | 0 | 0.001221 | 0.015873 | 105551 | 8027 | 105550.9988
38952.6485 | 3 | 0 | 38952.6486 | 2 | 0 |  | 1723 | 1885 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6507 | 2 | 0 | 38952.6507 | 2 | 0 |  | 1907.5 | 2069.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6528 | 2 | 0 | 38952.6528 | 2 | 0 |  | 2092.5 | 2254.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6549 | 2 | 0 | 38952.655 | 2 | 0 |  | 2277 | 2439 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## A2-B4
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38952.6271 | 1 | 0 | 38952.6271 | 1 | 0 |  | -127.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6292 | 1 | 0 | 38952.6293 | 1 | 0 |  | 57 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6314 | 1 | 0 | 38952.6314 | 1 | 0 |  | 242 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6335 | 1 | 0 | 38952.6335 | 1 | 0 |  | 426.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6357 | 1 | 0 | 38952.6357 | 1 | 0 |  | 611.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6378 | 1 | 0 | 38952.6378 | 1 | 0 |  | 796 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6399 | 1 | 0 | 38952.64 | 1 | 0 |  | 981 | 1143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6421 | 1 | 1 | 38952.6421 | 1 | 0 |  | 1165.5 | 1327.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38952.6442 | 2 | 0 | 38952.6442 | 2 | 0 |  | 1350.5 | 1512.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6464 | 3 | 0 | 38952.6464 | 2 | 0 |  | 1535.5 | 1697.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6485 | 2 | 0 | 38952.6485 | 2 | 0 |  | 1720 | 1882 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6506 | 2 | 0 | 38952.6507 | 2 | 0 |  | 1905 | 2067 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6528 | 2 | 0 | 38952.6528 | 2 | 0 |  | 2089.5 | 2251.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6549 | 2 | 0 | 38952.6549 | 2 | 0 |  | 2274.5 | 2436.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## A2-B3
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38952.6271 | 1 | 0 | 38952.6271 | 1 | 0 |  | -130.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6292 | 1 | 0 | 38952.6292 | 1 | 0 |  | 54.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6314 | 1 | 0 | 38952.6314 | 2 | 0 |  | 239 | 401 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.6335 | 1 | 0 | 38952.6335 | 1 | 0 |  | 424 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6356 | 1 | 0 | 38952.6356 | 1 | 0 |  | 608.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6378 | 1 | 0 | 38952.6378 | 1 | 0 |  | 793.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6399 | 1 | 0 | 38952.6399 | 1 | 0 |  | 978 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.642 | 2 | 0 | 38952.6421 | 2 | 0 |  | 1163 | 1325 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6442 | 3 | 0 | 38952.6442 | 2 | 0 |  | 1347.5 | 1509.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.6463 | 3 | 0 | 38952.6463 | 3 | 0 |  | 1532.5 | 1694.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.6485 | 3 | 0 | 38952.6485 | 132 | 0 |  | 1717.5 | 1879.5 | 0.18315 | 0 | 8.0586 | 0 | 0.0018315 | 0 | 0.080586 | 0 | 0.0018315 | 0.080586 | 70334 | 1500.7727 | 70333.9982
38952.6506 | 2 | 0 | 38952.6506 | 145 | 0 |  | 1902 | 2064 | 0.1221 | 0 | 8.8523 | 0 | 0.001221 | 0 | 0.088523 | 0 | 0.001221 | 0.088523 | 105551 | 1357.2552 | 105550.9988
38952.6527 | 2 | 0 | 38952.6528 | 45 | 0 |  | 2086.5 | 2248.5 | 0.1221 | 0 | 2.7473 | 0 | 0.001221 | 0 | 0.027473 | 0 | 0.001221 | 0.027473 | 105551 | 4595.6 | 105550.9988
38952.6549 | 2 | 0 | 38952.6549 | 3 | 0 |  | 2271.5 | 2433.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988

## A1-C6
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38952.6269 | 1 | 0 | 38952.6269 | 1 | 0 |  | -150 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.629 | 1 | 0 | 38952.629 | 1 | 0 |  | 34.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6311 | 1 | 0 | 38952.6311 | 1 | 0 |  | 219.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6333 | 1 | 0 | 38952.6333 | 1 | 0 |  | 404 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6354 | 1 | 0 | 38952.6354 | 1 | 0 |  | 589 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6375 | 1 | 0 | 38952.6376 | 1 | 0 |  | 773.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6397 | 1 | 0 | 38952.6397 | 1 | 0 |  | 958.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6418 | 1 | 1 | 38952.6418 | 1 | 0 |  | 1143.5 | 1305.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38952.644 | 2 | 0 | 38952.644 | 2 | 0 |  | 1328 | 1490 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6461 | 2 | 0 | 38952.6461 | 13 | 0 |  | 1513 | 1675 | 0.1221 | 0 | 0.79365 | 0 | 0.001221 | 0 | 0.0079365 | 0 | 0.001221 | 0.0079365 | 105551 | 16154 | 105550.9988
38952.6482 | 2 | 0 | 38952.6483 | 3 | 0 |  | 1697.5 | 1859.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.6504 | 2 | 1 | 38952.6504 | 2 | 0 |  | 1882.5 | 2044.5 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211302.1897 | 105551 | 210802.284
38952.6525 | 2 | 0 | 38952.6525 | 2 | 0 |  | 2067 | 2229 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6547 | 2 | 0 | 38952.6547 | 2 | 0 |  | 2252 | 2414 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988

## A1-C5
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38952.6268 | 1 | 0 | 38952.6268 | 1 | 0 |  | -153 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.629 | 1 | 0 | 38952.629 | 1 | 0 |  | 32 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6311 | 1 | 0 | 38952.6311 | 1 | 0 |  | 216.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6332 | 1 | 0 | 38952.6333 | 1 | 0 |  | 401.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6354 | 1 | 0 | 38952.6354 | 1 | 0 |  | 586.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6375 | 1 | 0 | 38952.6375 | 1 | 0 |  | 771 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6397 | 1 | 0 | 38952.6397 | 1 | 0 |  | 955.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6418 | 2 | 1 | 38952.6418 | 1 | 1 |  | 1140.5 | 1302.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211101.9527 | 445851546.4873 | 211001.9527
38952.6439 | 2 | 1 | 38952.6439 | 2 | 0 |  | 1325.5 | 1487.5 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211302.1897 | 105551 | 210802.284
38952.6461 | 3 | 1 | 38952.6461 | 4 | 0 |  | 1510 | 1672 | 0.18315 | 0.06105 | 0.2442 | 0 | 0.0018315 | 0.0006105 | 0.002442 | 0 | 0.001221 | 0.002442 | 105601.1424 | 52725.5 | 210502.7572
38952.6482 | 2 | 0 | 38952.6482 | 3 | 0 |  | 1695 | 1857 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.6503 | 2 | 1 | 38952.6504 | 3 | 0 |  | 1879.5 | 2041.5 | 0.1221 | 0.06105 | 0.18315 | 0 | 0.001221 | 0.0006105 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 211402.5695 | 70334 | 210702.4259
38952.6525 | 2 | 0 | 38952.6525 | 2 | 0 |  | 2064.5 | 2226.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.6546 | 2 | 1 | 38952.6546 | 2 | 0 |  | 2249 | 2411 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211302.1897 | 105551 | 210802.284

## A1-B4
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38952.6268 | 1 | 0 | 38952.6268 | 1 | 0 |  | -155.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6289 | 1 | 0 | 38952.6289 | 1 | 0 |  | 29 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6311 | 1 | 0 | 38952.6311 | 1 | 0 |  | 214 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6332 | 1 | 0 | 38952.6332 | 1 | 0 |  | 398.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6353 | 1 | 0 | 38952.6354 | 1 | 0 |  | 583.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6375 | 1 | 0 | 38952.6375 | 1 | 0 |  | 768.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6396 | 1 | 0 | 38952.6396 | 1 | 0 |  | 953 | 1115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6418 | 2 | 2 | 38952.6418 | 2 | 1 |  | 1137.5 | 1299.5 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 222820172.02 | 211101.9053 | 105401.071
38952.6439 | 3 | 2 | 38952.6439 | 2 | 1 |  | 1322.5 | 1484.5 | 0.18315 | 0.1221 | 0.1221 | 0.06105 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 105351.1183
38952.646 | 2 | 1 | 38952.6461 | 3 | 1 |  | 1507.5 | 1669.5 | 0.1221 | 0.06105 | 0.18315 | 0.06105 | 0.001221 | 0.0006105 | 0.0018315 | 0.0006105 | 0.0006105 | 0.001221 | 211302.2372 | 105525.9704 | 210802.2366
38952.6482 | 2 | 1 | 38952.6482 | 128 | 1 |  | 1692 | 1854 | 0.1221 | 0.06105 | 7.8144 | 0.06105 | 0.001221 | 0.0006105 | 0.078144 | 0.0006105 | 0.0006105 | 0.077534 | 225531.2602 | 1563.0133 | 198314.068
38952.6503 | 2 | 1 | 38952.6503 | 178 | 1 |  | 1876.5 | 2038.5 | 0.1221 | 0.06105 | 10.8669 | 0.06105 | 0.001221 | 0.0006105 | 0.10867 | 0.0006105 | 0.0006105 | 0.10806 | 232355.9982 | 1093.2343 | 193318.8006
38952.6525 | 2 | 1 | 38952.6525 | 52 | 1 |  | 2061.5 | 2223.5 | 0.1221 | 0.06105 | 3.1746 | 0.06105 | 0.001221 | 0.0006105 | 0.031746 | 0.0006105 | 0.0006105 | 0.031136 | 216458.2164 | 4041.2523 | 205906.8745
38952.6546 | 2 | 1 | 38952.6546 | 4 | 1 |  | 2246.5 | 2408.5 | 0.1221 | 0.06105 | 0.2442 | 0.06105 | 0.001221 | 0.0006105 | 0.002442 | 0.0006105 | 0.0006105 | 0.0018315 | 211402.6648 | 70311.7532 | 210702.3313

## A1-B3
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38952.6268 | 1 | 0 | 38952.6268 | 1 | 0 |  | -158.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6289 | 1 | 0 | 38952.6289 | 1 | 0 |  | 26.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.631 | 1 | 0 | 38952.6311 | 1 | 0 |  | 211 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6332 | 1 | 0 | 38952.6332 | 1 | 0 |  | 396 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6353 | 1 | 0 | 38952.6353 | 1 | 0 |  | 580.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6375 | 1 | 0 | 38952.6375 | 1 | 0 |  | 765.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6396 | 1 | 0 | 38952.6396 | 1 | 0 |  | 950 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6417 | 2 | 5 | 38952.6417 | 2 | 3 |  | 1135 | 1297 | 0.1221 | 0.30525 | 0.1221 | 0.18315 | 0.001221 | 0.0030525 | 0.001221 | 0.0018315 | 0.0018315 | 0.0006105 | 70422.6957 | 212005.1398 | 42100.5417
38952.6439 | 3 | 5 | 38952.6439 | 2 | 3 |  | 1319.5 | 1481.5 | 0.18315 | 0.30525 | 0.1221 | 0.18315 | 0.0018315 | 0.0030525 | 0.001221 | 0.0018315 | 0.001221 | 0.0006105 | 105625.7332 | 211703.2833 | 42080.5229
38952.646 | 2 | 4 | 38952.646 | 3 | 2 |  | 1504.5 | 1666.5 | 0.1221 | 0.2442 | 0.18315 | 0.1221 | 0.001221 | 0.002442 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 105650.9526 | 211402.1898 | 52650.5946
38952.6481 | 3 | 3 | 38952.6482 | 128 | 2 |  | 1689.5 | 1851.5 | 0.18315 | 0.18315 | 7.8144 | 0.1221 | 0.0018315 | 0.0018315 | 0.078144 | 0.001221 | 0 | 0.076923 | 1108049.18 | 1575.4104 | 66041.9526
38952.6503 | 3 | 4 | 38952.6503 | 156 | 2 |  | 1874 | 2036 | 0.18315 | 0.2442 | 9.5238 | 0.1221 | 0.0018315 | 0.002442 | 0.095238 | 0.001221 | 0.0006105 | 0.094017 | 307925.5597 | 1270.7976 | 48809.6338
38952.6524 | 3 | 4 | 38952.6524 | 47 | 2 |  | 2058.5 | 2220.5 | 0.18315 | 0.2442 | 2.8694 | 0.1221 | 0.0018315 | 0.002442 | 0.028694 | 0.001221 | 0.0006105 | 0.027473 | 231139.4111 | 4591.2438 | 51528.1857
38952.6546 | 2 | 3 | 38952.6546 | 4 | 2 |  | 2243.5 | 2405.5 | 0.1221 | 0.18315 | 0.2442 | 0.1221 | 0.001221 | 0.0018315 | 0.002442 | 0.001221 | 0.0006105 | 0.001221 | 211703.9971 | 105500.8341 | 70200.7928

## A1-A2
Penlight Test 68 |  |  | 2006-08-23 | 15:05 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38952.6267 | 1 | 0 | 38952.6267 | 1 | 0 |  | -161.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6289 | 1 | 0 | 38952.6289 | 1 | 0 |  | 23.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.631 | 1 | 0 | 38952.631 | 1 | 0 |  | 208 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6331 | 1 | 0 | 38952.6332 | 1 | 0 |  | 393 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6353 | 1 | 0 | 38952.6353 | 1 | 0 |  | 578 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6374 | 1 | 0 | 38952.6374 | 1 | 0 |  | 762.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6396 | 1 | 0 | 38952.6396 | 1 | 0 |  | 947.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.6417 | 1045 | 1095 | 38952.6417 | 1044 | 1019 |  | 1132 | 1294 | 63.7973 | 66.8498 | 63.7363 | 62.21 | 0.63797 | 0.6685 | 0.63736 | 0.6221 | 0.030525 | 0.015263 | 99.4391 | 106.929 | 1.2732
38952.6438 | 949 | 923 | 38952.6439 | 952 | 1069 |  | 1317 | 1479 | 57.9365 | 56.3492 | 58.1197 | 65.2625 | 0.57937 | 0.56349 | 0.5812 | 0.65263 | 0.015873 | 0.071429 | 468.8207 | 415.2293 | 21.0445
38952.646 | 1202 | 1188 | 38952.646 | 1144 | 1191 |  | 1501.5 | 1663.5 | 73.3822 | 72.5275 | 69.8413 | 72.7106 | 0.73382 | 0.72527 | 0.69841 | 0.72711 | 0.008547 | 0.028694 | 1258.8477 | 2035.3145 | 22.2229
38952.6481 | 1175 | 1142 | 38952.6481 | 1144 | 1107 |  | 1686.5 | 1848.5 | 71.7338 | 69.7192 | 69.8413 | 67.5824 | 0.71734 | 0.69719 | 0.69841 | 0.67582 | 0.020147 | 0.022589 | 3456.813 | 19472.7648 | 17.7704
38952.6503 | 1063 | 1088 | 38952.6503 | 1121 | 1072 |  | 1871.5 | 2033.5 | 64.8962 | 66.4225 | 68.4371 | 65.4457 | 0.64896 | 0.66422 | 0.68437 | 0.65446 | 0.015263 | 0.029915 | 437.3504 | 505.8426 | 2.9146
38952.6524 | 1061 | 1076 | 38952.6524 | 1039 | 984 |  | 2056 | 2218 | 64.7741 | 65.6899 | 63.431 | 60.0733 | 0.64774 | 0.6569 | 0.63431 | 0.60073 | 0.0091575 | 0.033578 | 165.0964 | 172.9304 | 1.4121
38952.6545 | 1115 | 1173 | 38952.6545 | 1187 | 1194 |  | 2240.5 | 2402.5 | 68.0708 | 71.6117 | 72.4664 | 72.8938 | 0.68071 | 0.71612 | 0.72466 | 0.72894 | 0.035409 | 0.0042735 | 1047.0215 | 3143.094 | 14.4573

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 68 |  |  | 2006-08-23 | 15:05
38952.6267 | 1 | 0 | 1 | TS/TP Mix | 7-C | Tray
38952.6289 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38952.631 | 1 | 0 | 1
38952.6331 | 1 | 0 | 1
38952.6353 | 1 | 0 | 1
38952.6374 | 1 | 0 | 1
38952.6396 | 1 | 0 | 1
38952.6417 | 1045 | 1095 | 1
38952.6438 | 949 | 923 | 1
38952.646 | 1202 | 1188 | 1
38952.6481 | 1175 | 1142 | 1
38952.6503 | 1063 | 1088 | 1
38952.6524 | 1061 | 1076 | 1
38952.6545 | 1115 | 1173 | 1
1
38952.6267 | 1 | 0 | 2
38952.6289 | 1 | 0 | 2
38952.631 | 1 | 0 | 2
38952.6332 | 1 | 0 | 2
38952.6353 | 1 | 0 | 2
38952.6374 | 1 | 0 | 2
38952.6396 | 1 | 0 | 2
38952.6417 | 1044 | 1019 | 2
38952.6439 | 952 | 1069 | 2
38952.646 | 1144 | 1191 | 2
38952.6481 | 1144 | 1107 | 2
38952.6503 | 1121 | 1072 | 2
38952.6524 | 1039 | 984 | 2
38952.6545 | 1187 | 1194 | 2
2
38952.6268 | 1 | 0 | 3
38952.6289 | 1 | 0 | 3
38952.631 | 1 | 0 | 3
38952.6332 | 1 | 0 | 3
38952.6353 | 1 | 0 | 3
38952.6375 | 1 | 0 | 3
38952.6396 | 1 | 0 | 3
38952.6417 | 2 | 5 | 3
38952.6439 | 3 | 5 | 3
38952.646 | 2 | 4 | 3
38952.6481 | 3 | 3 | 3
38952.6503 | 3 | 4 | 3
38952.6524 | 3 | 4 | 3
38952.6546 | 2 | 3 | 3
3
38952.6268 | 1 | 0 | 4
38952.6289 | 1 | 0 | 4
38952.6311 | 1 | 0 | 4
38952.6332 | 1 | 0 | 4
38952.6353 | 1 | 0 | 4
38952.6375 | 1 | 0 | 4
38952.6396 | 1 | 0 | 4
38952.6417 | 2 | 3 | 4
38952.6439 | 2 | 3 | 4
38952.646 | 3 | 2 | 4
38952.6482 | 128 | 2 | 4
38952.6503 | 156 | 2 | 4
38952.6524 | 47 | 2 | 4
38952.6546 | 4 | 2 | 4
4
38952.6268 | 1 | 0 | 5
38952.6289 | 1 | 0 | 5
38952.6311 | 1 | 0 | 5
38952.6332 | 1 | 0 | 5
38952.6353 | 1 | 0 | 5
38952.6375 | 1 | 0 | 5
38952.6396 | 1 | 0 | 5
38952.6418 | 2 | 2 | 5
38952.6439 | 3 | 2 | 5
38952.646 | 2 | 1 | 5
38952.6482 | 2 | 1 | 5
38952.6503 | 2 | 1 | 5
38952.6525 | 2 | 1 | 5
38952.6546 | 2 | 1 | 5
5
38952.6268 | 1 | 0 | 6
38952.6289 | 1 | 0 | 6
38952.6311 | 1 | 0 | 6
38952.6332 | 1 | 0 | 6
38952.6354 | 1 | 0 | 6
38952.6375 | 1 | 0 | 6
38952.6396 | 1 | 0 | 6
38952.6418 | 2 | 1 | 6
38952.6439 | 2 | 1 | 6
38952.6461 | 3 | 1 | 6
38952.6482 | 128 | 1 | 6
38952.6503 | 178 | 1 | 6
38952.6525 | 52 | 1 | 6
38952.6546 | 4 | 1 | 6
6
38952.6268 | 1 | 0 | 7
38952.629 | 1 | 0 | 7
38952.6311 | 1 | 0 | 7
38952.6332 | 1 | 0 | 7
38952.6354 | 1 | 0 | 7
38952.6375 | 1 | 0 | 7
38952.6397 | 1 | 0 | 7
38952.6418 | 2 | 1 | 7
38952.6439 | 2 | 1 | 7
38952.6461 | 3 | 1 | 7
38952.6482 | 2 | 0 | 7
38952.6503 | 2 | 1 | 7
38952.6525 | 2 | 0 | 7
38952.6546 | 2 | 1 | 7
7
38952.6268 | 1 | 0 | 8
38952.629 | 1 | 0 | 8
38952.6311 | 1 | 0 | 8
38952.6333 | 1 | 0 | 8
38952.6354 | 1 | 0 | 8
38952.6375 | 1 | 0 | 8
38952.6397 | 1 | 0 | 8
38952.6418 | 1 | 1 | 8
38952.6439 | 2 | 0 | 8
38952.6461 | 4 | 0 | 8
38952.6482 | 3 | 0 | 8
38952.6504 | 3 | 0 | 8
38952.6525 | 2 | 0 | 8
38952.6546 | 2 | 0 | 8
8
38952.6269 | 1 | 0 | 9
38952.629 | 1 | 0 | 9
38952.6311 | 1 | 0 | 9
38952.6333 | 1 | 0 | 9
38952.6354 | 1 | 0 | 9
38952.6375 | 1 | 0 | 9
38952.6397 | 1 | 0 | 9
38952.6418 | 1 | 1 | 9
38952.644 | 2 | 0 | 9
38952.6461 | 2 | 0 | 9
38952.6482 | 2 | 0 | 9
38952.6504 | 2 | 1 | 9
38952.6525 | 2 | 0 | 9
38952.6547 | 2 | 0 | 9
9
38952.6269 | 1 | 0 | 10
38952.629 | 1 | 0 | 10
38952.6311 | 1 | 0 | 10
38952.6333 | 1 | 0 | 10
38952.6354 | 1 | 0 | 10
38952.6376 | 1 | 0 | 10
38952.6397 | 1 | 0 | 10
38952.6418 | 1 | 1 | 10
38952.644 | 2 | 0 | 10
38952.6461 | 13 | 0 | 10
38952.6483 | 3 | 0 | 10
38952.6504 | 2 | 0 | 10
38952.6525 | 2 | 0 | 10
38952.6547 | 2 | 0 | 10
10
38952.6269 | 1 | 0 | 11
38952.629 | 1 | 0 | 11
38952.6312 | 1 | 0 | 11
38952.6333 | 1 | 0 | 11
38952.6354 | 1 | 0 | 11
38952.6376 | 1 | 0 | 11
38952.6397 | 1 | 0 | 11
38952.6419 | 1 | 1 | 11
38952.644 | 2 | 0 | 11
38952.6461 | 2 | 0 | 11
38952.6483 | 2 | 0 | 11
38952.6504 | 2 | 0 | 11
38952.6525 | 2 | 0 | 11
38952.6547 | 2 | 0 | 11
11
38952.6269 | 1 | 0 | 12
38952.629 | 1 | 0 | 12
38952.6312 | 1 | 0 | 12
38952.6333 | 1 | 0 | 12
38952.6355 | 1 | 0 | 12
38952.6376 | 1 | 0 | 12
38952.6397 | 1 | 0 | 12
38952.6419 | 1 | 0 | 12
38952.644 | 313 | 0 | 12
38952.6461 | 1925 | 0 | 12
38952.6483 | 2087 | 0 | 12
38952.6504 | 2089 | 0 | 12
38952.6526 | 2522 | 0 | 12
38952.6547 | 2461 | 0 | 12
12
38952.6269 | 1 | 0 | 13
38952.6291 | 1 | 0 | 13
38952.6312 | 1 | 0 | 13
38952.6333 | 1 | 0 | 13
38952.6355 | 1 | 0 | 13
38952.6376 | 1 | 0 | 13
38952.6397 | 1 | 0 | 13
38952.6419 | 1 | 0 | 13
38952.644 | 2 | 0 | 13
38952.6462 | 3 | 0 | 13
38952.6483 | 3 | 0 | 13
38952.6504 | 3 | 0 | 13
38952.6526 | 2 | 0 | 13
38952.6547 | 3 | 0 | 13
13
38952.6269 | 1 | 0 | 14
38952.6291 | 1 | 0 | 14
38952.6312 | 1 | 0 | 14
38952.6333 | 1 | 0 | 14
38952.6355 | 1 | 0 | 14
38952.6376 | 1 | 0 | 14
38952.6398 | 1 | 0 | 14
38952.6419 | 1 | 0 | 14
38952.644 | 384 | 0 | 14
38952.6462 | 1944 | 0 | 14
38952.6483 | 1978 | 0 | 14
38952.6505 | 2214 | 0 | 14
38952.6526 | 1907 | 0 | 14
38952.6547 | 2057 | 0 | 14
14
38952.627 | 1 | 0 | 15
38952.6291 | 1 | 0 | 15
38952.6312 | 1 | 0 | 15
38952.6334 | 1 | 0 | 15
38952.6355 | 1 | 0 | 15
38952.6376 | 1 | 0 | 15
38952.6398 | 1 | 0 | 15
38952.6419 | 1 | 0 | 15
38952.6441 | 2 | 0 | 15
38952.6462 | 3 | 0 | 15
38952.6483 | 3 | 0 | 15
38952.6505 | 3 | 0 | 15
38952.6526 | 3 | 0 | 15
38952.6548 | 2 | 0 | 15
15
38952.627 | 1 | 0 | 16
38952.6291 | 1 | 0 | 16
38952.6312 | 1 | 0 | 16
38952.6334 | 1 | 0 | 16
38952.6355 | 1 | 0 | 16
38952.6377 | 1 | 0 | 16
38952.6398 | 1 | 0 | 16
38952.6419 | 1 | 0 | 16
38952.6441 | 2 | 0 | 16
38952.6462 | 2 | 0 | 16
38952.6484 | 3 | 0 | 16
38952.6505 | 2 | 0 | 16
38952.6526 | 2 | 0 | 16
38952.6548 | 2 | 0 | 16
16
38952.627 | 1 | 0 | 17
38952.6291 | 1 | 0 | 17
38952.6313 | 1 | 0 | 17
38952.6334 | 1 | 0 | 17
38952.6355 | 1 | 0 | 17
38952.6377 | 1 | 0 | 17
38952.6398 | 1 | 0 | 17
38952.642 | 1 | 0 | 17
38952.6441 | 1 | 0 | 17
38952.6462 | 3 | 0 | 17
38952.6484 | 2 | 0 | 17
38952.6505 | 3 | 0 | 17
38952.6527 | 2 | 0 | 17
38952.6548 | 2 | 0 | 17
17
38952.627 | 1 | 0 | 18
38952.6291 | 1 | 0 | 18
38952.6313 | 1 | 0 | 18
38952.6334 | 1 | 0 | 18
38952.6356 | 1 | 0 | 18
38952.6377 | 1 | 0 | 18
38952.6398 | 1 | 0 | 18
38952.642 | 1 | 0 | 18
38952.6441 | 2 | 0 | 18
38952.6462 | 3 | 0 | 18
38952.6484 | 2 | 0 | 18
38952.6505 | 2 | 0 | 18
38952.6527 | 2 | 0 | 18
38952.6548 | 2 | 0 | 18
18
38952.627 | 1 | 0 | 19
38952.6292 | 1 | 0 | 19
38952.6313 | 1 | 0 | 19
38952.6334 | 1 | 0 | 19
38952.6356 | 1 | 0 | 19
38952.6377 | 1 | 0 | 19
38952.6398 | 1 | 0 | 19
38952.642 | 1 | 0 | 19
38952.6441 | 1 | 0 | 19
38952.6463 | 2 | 0 | 19
38952.6484 | 3 | 0 | 19
38952.6505 | 2 | 0 | 19
38952.6527 | 2 | 0 | 19
38952.6548 | 2 | 0 | 19
19
38952.627 | 1 | 0 | 20
38952.6292 | 1 | 0 | 20
38952.6313 | 1 | 0 | 20
38952.6334 | 1 | 0 | 20
38952.6356 | 1 | 0 | 20
38952.6377 | 1 | 0 | 20
38952.6399 | 1 | 0 | 20
38952.642 | 1 | 0 | 20
38952.6441 | 1572 | 0 | 20
38952.6463 | 2462 | 0 | 20
38952.6484 | 2025 | 0 | 20
38952.6506 | 1592 | 0 | 20
38952.6527 | 774 | 0 | 20
38952.6548 | 2 | 0 | 20
20
38952.627 | 1 | 0 | 21
38952.6292 | 1 | 0 | 21
38952.6313 | 1 | 0 | 21
38952.6335 | 1 | 0 | 21
38952.6356 | 1 | 0 | 21
38952.6377 | 1 | 0 | 21
38952.6399 | 1 | 0 | 21
38952.642 | 1 | 0 | 21
38952.6442 | 2 | 0 | 21
38952.6463 | 3 | 0 | 21
38952.6484 | 3 | 0 | 21
38952.6506 | 3 | 0 | 21
38952.6527 | 3 | 0 | 21
38952.6548 | 2 | 0 | 21
21
38952.6271 | 1 | 0 | 22
38952.6292 | 1 | 0 | 22
38952.6313 | 1 | 0 | 22
38952.6335 | 1 | 0 | 22
38952.6356 | 1 | 0 | 22
38952.6378 | 1 | 0 | 22
38952.6399 | 1 | 0 | 22
38952.642 | 1802 | 2 | 22
38952.6442 | 2211 | 0 | 22
38952.6463 | 2193 | 0 | 22
38952.6484 | 1959 | 0 | 22
38952.6506 | 1402 | 0 | 22
38952.6527 | 981 | 0 | 22
38952.6549 | 2 | 0 | 22
22
38952.6271 | 1 | 0 | 23
38952.6292 | 1 | 0 | 23
38952.6314 | 1 | 0 | 23
38952.6335 | 1 | 0 | 23
38952.6356 | 1 | 0 | 23
38952.6378 | 1 | 0 | 23
38952.6399 | 1 | 0 | 23
38952.642 | 2 | 0 | 23
38952.6442 | 3 | 0 | 23
38952.6463 | 3 | 0 | 23
38952.6485 | 3 | 0 | 23
38952.6506 | 2 | 0 | 23
38952.6527 | 2 | 0 | 23
38952.6549 | 2 | 0 | 23
23
38952.6271 | 1 | 0 | 24
38952.6292 | 1 | 0 | 24
38952.6314 | 2 | 0 | 24
38952.6335 | 1 | 0 | 24
38952.6356 | 1 | 0 | 24
38952.6378 | 1 | 0 | 24
38952.6399 | 1 | 0 | 24
38952.6421 | 2 | 0 | 24
38952.6442 | 2 | 0 | 24
38952.6463 | 3 | 0 | 24
38952.6485 | 132 | 0 | 24
38952.6506 | 145 | 0 | 24
38952.6528 | 45 | 0 | 24
38952.6549 | 3 | 0 | 24
24
38952.6271 | 1 | 0 | 25
38952.6292 | 1 | 0 | 25
38952.6314 | 1 | 0 | 25
38952.6335 | 1 | 0 | 25
38952.6357 | 1 | 0 | 25
38952.6378 | 1 | 0 | 25
38952.6399 | 1 | 0 | 25
38952.6421 | 1 | 1 | 25
38952.6442 | 2 | 0 | 25
38952.6464 | 3 | 0 | 25
38952.6485 | 2 | 0 | 25
38952.6506 | 2 | 0 | 25
38952.6528 | 2 | 0 | 25
38952.6549 | 2 | 0 | 25
25
38952.6271 | 1 | 0 | 26
38952.6293 | 1 | 0 | 26
38952.6314 | 1 | 0 | 26
38952.6335 | 1 | 0 | 26
38952.6357 | 1 | 0 | 26
38952.6378 | 1 | 0 | 26
38952.64 | 1 | 0 | 26
38952.6421 | 1 | 0 | 26
38952.6442 | 2 | 0 | 26
38952.6464 | 2 | 0 | 26
38952.6485 | 2 | 0 | 26
38952.6507 | 2 | 0 | 26
38952.6528 | 2 | 0 | 26
38952.6549 | 2 | 0 | 26
26
38952.6271 | 1 | 0 | 27
38952.6293 | 1 | 0 | 27
38952.6314 | 1 | 0 | 27
38952.6336 | 2 | 0 | 27
38952.6357 | 1 | 0 | 27
38952.6378 | 1 | 0 | 27
38952.64 | 1 | 0 | 27
38952.6421 | 1 | 0 | 27
38952.6443 | 2 | 0 | 27
38952.6464 | 2 | 0 | 27
38952.6485 | 3 | 0 | 27
38952.6507 | 2 | 0 | 27
38952.6528 | 2 | 0 | 27
38952.6549 | 2 | 0 | 27
27
38952.6272 | 1 | 0 | 28
38952.6293 | 1 | 0 | 28
38952.6314 | 1 | 0 | 28
38952.6336 | 1 | 0 | 28
38952.6357 | 1 | 0 | 28
38952.6379 | 1 | 0 | 28
38952.64 | 1 | 0 | 28
38952.6421 | 1 | 0 | 28
38952.6443 | 2 | 0 | 28
38952.6464 | 26 | 0 | 28
38952.6486 | 2 | 0 | 28
38952.6507 | 2 | 0 | 28
38952.6528 | 2 | 0 | 28
38952.655 | 2 | 0 | 28
28
38952.6272 | 1 | 0 | 29
38952.6293 | 1 | 0 | 29
38952.6315 | 1 | 0 | 29
38952.6336 | 1 | 0 | 29
38952.6357 | 1 | 0 | 29
38952.6379 | 1 | 0 | 29
38952.64 | 1 | 0 | 29
38952.6422 | 1 | 0 | 29
38952.6443 | 2 | 0 | 29
38952.6464 | 2 | 0 | 29
38952.6486 | 2 | 0 | 29
38952.6507 | 2 | 0 | 29
38952.6528 | 2 | 0 | 29
38952.655 | 2 | 0 | 29
29
38952.6272 | 1 | 0 | 30
38952.6293 | 1 | 0 | 30
38952.6315 | 1 | 0 | 30
38952.6336 | 1 | 0 | 30
38952.6358 | 1 | 0 | 30
38952.6379 | 1 | 0 | 30
38952.64 | 1 | 0 | 30
38952.6422 | 1 | 0 | 30
38952.6443 | 2 | 0 | 30
38952.6464 | 2 | 0 | 30
38952.6486 | 2 | 0 | 30
38952.6507 | 2 | 0 | 30
38952.6529 | 2 | 0 | 30
38952.655 | 1 | 0 | 30
30
38952.6272 | 1 | 0 | 31
38952.6294 | 1 | 0 | 31
38952.6315 | 1 | 0 | 31
38952.6336 | 1 | 0 | 31
38952.6358 | 1 | 0 | 31
38952.6379 | 1 | 0 | 31
38952.64 | 1 | 0 | 31
38952.6422 | 1 | 0 | 31
38952.6443 | 1 | 0 | 31
38952.6465 | 2 | 0 | 31
38952.6486 | 3 | 1 | 31
38952.6507 | 2 | 0 | 31
38952.6529 | 2 | 0 | 31
38952.655 | 2 | 0 | 31
31
38952.6272 | 1 | 0 | 32
38952.6294 | 1 | 0 | 32
38952.6315 | 1 | 0 | 32
38952.6336 | 1 | 0 | 32
38952.6358 | 1 | 0 | 32
38952.6379 | 1 | 0 | 32
38952.6401 | 1 | 0 | 32
38952.6422 | 1 | 0 | 32
38952.6443 | 1373 | 0 | 32
38952.6465 | 2456 | 0 | 32
38952.6486 | 2255 | 0 | 32
38952.6508 | 1943 | 0 | 32
38952.6529 | 2348 | 0 | 32
38952.655 | 2107 | 0 | 32
32
38952.6272 | 1 | 0 | 33
38952.6294 | 1 | 0 | 33
38952.6315 | 1 | 0 | 33
38952.6337 | 1 | 0 | 33
38952.6358 | 1 | 0 | 33
38952.6379 | 1 | 0 | 33
38952.6401 | 1 | 0 | 33
38952.6422 | 1 | 0 | 33
38952.6444 | 2 | 0 | 33
38952.6465 | 3 | 0 | 33
38952.6486 | 3 | 0 | 33
38952.6508 | 3 | 0 | 33
38952.6529 | 3 | 0 | 33
38952.655 | 2 | 0 | 33
33
38952.6273 | 1 | 0 | 34
38952.6294 | 1 | 0 | 34
38952.6315 | 1 | 0 | 34
38952.6337 | 1 | 0 | 34
38952.6358 | 1 | 0 | 34
38952.638 | 1 | 0 | 34
38952.6401 | 1 | 0 | 34
38952.6422 | 1 | 0 | 34
38952.6444 | 2099 | 0 | 34
38952.6465 | 1844 | 0 | 34
38952.6486 | 1905 | 1 | 34
38952.6508 | 1700 | 0 | 34
38952.6529 | 2145 | 0 | 34
38952.6551 | 1967 | 0 | 34
34
38952.6273 | 1 | 0 | 35
38952.6294 | 1 | 0 | 35
38952.6316 | 1 | 0 | 35
38952.6337 | 1 | 0 | 35
38952.6358 | 1 | 0 | 35
38952.638 | 1 | 0 | 35
38952.6401 | 1 | 0 | 35
38952.6422 | 1 | 0 | 35
38952.6444 | 3 | 0 | 35
38952.6465 | 3 | 0 | 35
38952.6487 | 3 | 0 | 35
38952.6508 | 3 | 0 | 35
38952.6529 | 3 | 0 | 35
38952.6551 | 3 | 0 | 35
35
38952.6273 | 1 | 0 | 36
38952.6294 | 1 | 0 | 36
38952.6316 | 1 | 0 | 36
38952.6337 | 1 | 0 | 36
38952.6358 | 1 | 0 | 36
38952.638 | 1 | 0 | 36
38952.6401 | 1 | 0 | 36
38952.6423 | 1 | 0 | 36
38952.6444 | 2 | 0 | 36
38952.6465 | 3 | 0 | 36
38952.6487 | 3 | 0 | 36
38952.6508 | 2 | 0 | 36
38952.653 | 3 | 0 | 36
38952.6551 | 2 | 0 | 36
36
38952.6273 | 1 | 0 | 37
38952.6294 | 1 | 0 | 37
38952.6316 | 1 | 0 | 37
38952.6337 | 1 | 0 | 37
38952.6359 | 1 | 0 | 37
38952.638 | 1 | 0 | 37
38952.6401 | 1 | 0 | 37
38952.6423 | 1 | 0 | 37
38952.6444 | 2 | 0 | 37
38952.6466 | 2 | 0 | 37
38952.6487 | 2 | 0 | 37
38952.6508 | 2 | 0 | 37
38952.653 | 2 | 0 | 37
38952.6551 | 2 | 0 | 37
37
38952.6273 | 1 | 0 | 38
38952.6295 | 1 | 0 | 38
38952.6316 | 1 | 0 | 38
38952.6337 | 1 | 0 | 38
38952.6359 | 1 | 0 | 38
38952.638 | 1 | 0 | 38
38952.6402 | 1 | 0 | 38
38952.6423 | 1 | 0 | 38
38952.6444 | 2 | 0 | 38
38952.6466 | 2 | 0 | 38
38952.6487 | 3 | 0 | 38
38952.6508 | 2 | 0 | 38
38952.653 | 2 | 0 | 38
38952.6551 | 2 | 0 | 38
38
38952.6273 | 1 | 0 | 39
38952.6295 | 1 | 0 | 39
38952.6316 | 1 | 0 | 39
38952.6338 | 1 | 0 | 39
38952.6359 | 1 | 0 | 39
38952.638 | 1 | 0 | 39
38952.6402 | 1 | 0 | 39
38952.6423 | 1 | 0 | 39
38952.6444 | 2 | 0 | 39
38952.6466 | 2 | 0 | 39
38952.6487 | 2 | 0 | 39
38952.6509 | 2 | 0 | 39
38952.653 | 2 | 0 | 39
38952.6551 | 2 | 0 | 39
39
38952.6274 | 1 | 0 | 40
38952.6295 | 1 | 0 | 40
38952.6316 | 1 | 0 | 40
38952.6338 | 1 | 0 | 40
38952.6359 | 1 | 0 | 40
38952.638 | 1 | 0 | 40
38952.6402 | 1 | 0 | 40
38952.6423 | 2145 | 0 | 40
38952.6445 | 1602 | 0 | 40
38952.6466 | 2141 | 0 | 40
38952.6487 | 2118 | 0 | 40
38952.6509 | 1661 | 0 | 40
38952.653 | 2 | 0 | 40
38952.6552 | 2 | 0 | 40
40
38952.6274 | 1 | 0 | 41
38952.6295 | 1 | 0 | 41
38952.6317 | 1 | 0 | 41
38952.6338 | 1 | 0 | 41
38952.6359 | 1 | 0 | 41
38952.6381 | 1 | 0 | 41
38952.6402 | 1 | 0 | 41
38952.6423 | 3 | 0 | 41
38952.6445 | 3 | 0 | 41
38952.6466 | 3 | 0 | 41
38952.6488 | 2 | 0 | 41
38952.6509 | 2 | 0 | 41
38952.653 | 2 | 0 | 41
38952.6552 | 1 | 0 | 41
41
38952.6274 | 1 | 0 | 42
38952.6295 | 1 | 0 | 42
38952.6317 | 1 | 0 | 42
38952.6338 | 1 | 0 | 42
38952.6359 | 1 | 0 | 42
38952.6381 | 1 | 0 | 42
38952.6402 | 1 | 0 | 42
38952.6424 | 2216 | 0 | 42
38952.6445 | 1553 | 0 | 42
38952.6466 | 2258 | 0 | 42
38952.6488 | 1777 | 0 | 42
38952.6509 | 1695 | 0 | 42
38952.6531 | 1586 | 0 | 42
38952.6552 | 2 | 0 | 42
42
38952.6274 | 1 | 0 | 43
38952.6295 | 1 | 0 | 43
38952.6317 | 1 | 0 | 43
38952.6338 | 1 | 0 | 43
38952.636 | 1 | 0 | 43
38952.6381 | 1 | 0 | 43
38952.6402 | 1 | 0 | 43
38952.6424 | 3 | 0 | 43
38952.6445 | 1026 | 988 | 43
38952.6467 | 1106 | 1127 | 43
38952.6488 | 1261 | 1079 | 43
38952.6509 | 1187 | 1132 | 43
38952.6531 | 1020 | 927 | 43
38952.6552 | 1208 | 1151 | 43
43
38952.6274 | 1 | 0 | 44
38952.6296 | 1 | 0 | 44
38952.6317 | 1 | 0 | 44
38952.6338 | 1 | 0 | 44
38952.636 | 1 | 0 | 44
38952.6381 | 1 | 0 | 44
38952.6403 | 1 | 0 | 44
38952.6424 | 3 | 0 | 44
38952.6445 | 1180 | 1144 | 44
38952.6467 | 1054 | 998 | 44
38952.6488 | 1277 | 1118 | 44
38952.6509 | 1209 | 1141 | 44
38952.6531 | 1081 | 982 | 44
38952.6552 | 1083 | 1137 | 44
44
38952.6274 | 1 | 0 | 45
38952.6296 | 1 | 0 | 45
38952.6317 | 1 | 0 | 45
38952.6339 | 1 | 0 | 45
38952.636 | 1 | 0 | 45
38952.6381 | 1 | 0 | 45
38952.6403 | 1 | 0 | 45
38952.6424 | 2 | 0 | 45
38952.6445 | 3 | 4 | 45
38952.6467 | 3 | 4 | 45
38952.6488 | 115 | 4 | 45
38952.651 | 52 | 4 | 45
38952.6531 | 17 | 3 | 45
38952.6552 | 2 | 4 | 45
45
38952.6275 | 1 | 0 | 46
38952.6296 | 1 | 0 | 46
38952.6317 | 1 | 0 | 46
38952.6339 | 1 | 0 | 46
38952.636 | 1 | 0 | 46
38952.6381 | 1 | 0 | 46
38952.6403 | 1 | 0 | 46
38952.6424 | 2 | 0 | 46
38952.6446 | 2 | 2 | 46
38952.6467 | 2 | 1 | 46
38952.6488 | 2 | 2 | 46
38952.651 | 2 | 2 | 46
38952.6531 | 2 | 1 | 46
38952.6553 | 2 | 2 | 46
46
38952.6275 | 1 | 0 | 47
38952.6296 | 1 | 0 | 47
38952.6317 | 1 | 0 | 47
38952.6339 | 1 | 0 | 47
38952.636 | 1 | 0 | 47
38952.6382 | 1 | 0 | 47
38952.6403 | 1 | 0 | 47
38952.6424 | 2 | 0 | 47
38952.6446 | 2 | 1 | 47
38952.6467 | 3 | 1 | 47
38952.6489 | 125 | 1 | 47
38952.651 | 52 | 1 | 47
38952.6531 | 16 | 1 | 47
38952.6553 | 2 | 1 | 47
47
38952.6275 | 1 | 0 | 48
38952.6296 | 1 | 0 | 48
38952.6318 | 1 | 0 | 48
38952.6339 | 1 | 0 | 48
38952.636 | 1 | 0 | 48
38952.6382 | 1 | 0 | 48
38952.6403 | 1 | 0 | 48
38952.6425 | 1 | 0 | 48
38952.6446 | 2 | 1 | 48
38952.6467 | 2 | 1 | 48
38952.6489 | 2 | 0 | 48
38952.651 | 2 | 0 | 48
38952.6531 | 2 | 0 | 48
38952.6553 | 2 | 0 | 48
48
38952.6275 | 1 | 0 | 49
38952.6296 | 1 | 0 | 49
38952.6318 | 1 | 0 | 49
38952.6339 | 1 | 0 | 49
38952.6361 | 1 | 0 | 49
38952.6382 | 1 | 0 | 49
38952.6403 | 1 | 0 | 49
38952.6425 | 1 | 0 | 49
38952.6446 | 2 | 0 | 49
38952.6467 | 3 | 0 | 49
38952.6489 | 141 | 1 | 49
38952.651 | 55 | 1 | 49
38952.6532 | 18 | 0 | 49
38952.6553 | 2 | 0 | 49
49
38952.6275 | 1 | 0 | 50
38952.6297 | 1 | 0 | 50
38952.6318 | 1 | 0 | 50
38952.6339 | 1 | 0 | 50
38952.6361 | 1 | 0 | 50
38952.6382 | 1 | 0 | 50
38952.6403 | 1 | 0 | 50
38952.6425 | 1 | 0 | 50
38952.6446 | 2350 | 0 | 50
38952.6468 | 2495 | 0 | 50
38952.6489 | 2281 | 0 | 50
38952.651 | 2477 | 0 | 50
38952.6532 | 2437 | 0 | 50
38952.6553 | 2089 | 0 | 50
50
38952.6275 | 1 | 0 | 51
38952.6297 | 1 | 0 | 51
38952.6318 | 1 | 0 | 51
38952.6339 | 1 | 0 | 51
38952.6361 | 1 | 0 | 51
38952.6382 | 1 | 0 | 51
38952.6404 | 1 | 0 | 51
38952.6425 | 1 | 0 | 51
38952.6446 | 3 | 0 | 51
38952.6468 | 3 | 0 | 51
38952.6489 | 136 | 0 | 51
38952.6511 | 51 | 0 | 51
38952.6532 | 15 | 0 | 51
38952.6553 | 3 | 0 | 51
51
38952.6275 | 1 | 0 | 52
38952.6297 | 1 | 0 | 52
38952.6318 | 1 | 0 | 52
38952.634 | 1 | 0 | 52
38952.6361 | 1 | 0 | 52
38952.6382 | 1 | 0 | 52
38952.6404 | 1 | 0 | 52
38952.6425 | 1 | 0 | 52
38952.6447 | 1920 | 0 | 52
38952.6468 | 1912 | 0 | 52
38952.6489 | 1825 | 0 | 52
38952.6511 | 2217 | 0 | 52
38952.6532 | 1858 | 0 | 52
38952.6553 | 1817 | 0 | 52
52
38952.6276 | 1 | 0 | 53
38952.6297 | 1 | 0 | 53
38952.6318 | 1 | 0 | 53
38952.634 | 1 | 0 | 53
38952.6361 | 1 | 0 | 53
38952.6383 | 1 | 0 | 53
38952.6404 | 1 | 0 | 53
38952.6425 | 1 | 0 | 53
38952.6447 | 3 | 0 | 53
38952.6468 | 4 | 0 | 53
38952.649 | 130 | 0 | 53
38952.6511 | 60 | 0 | 53
38952.6532 | 14 | 0 | 53
38952.6554 | 3 | 0 | 53
53
38952.6276 | 1 | 0 | 54
38952.6297 | 1 | 0 | 54
38952.6319 | 1 | 0 | 54
38952.634 | 1 | 0 | 54
38952.6361 | 1 | 0 | 54
38952.6383 | 1 | 0 | 54
38952.6404 | 1 | 0 | 54
38952.6426 | 1 | 0 | 54
38952.6447 | 3 | 0 | 54
38952.6468 | 3 | 0 | 54
38952.649 | 2 | 0 | 54
38952.6511 | 2 | 0 | 54
38952.6532 | 2 | 0 | 54
38952.6554 | 2 | 0 | 54
54
38952.6276 | 1 | 0 | 55
38952.6297 | 1 | 0 | 55
38952.6319 | 2 | 0 | 55
38952.634 | 1 | 0 | 55
38952.6362 | 1 | 0 | 55
38952.6383 | 1 | 0 | 55
38952.6404 | 1 | 0 | 55
38952.6426 | 1 | 0 | 55
38952.6447 | 2 | 0 | 55
38952.6469 | 3 | 0 | 55
38952.649 | 146 | 0 | 55
38952.6511 | 64 | 0 | 55
38952.6533 | 17 | 0 | 55
38952.6554 | 2 | 0 | 55
55
38952.6276 | 1 | 0 | 56
38952.6298 | 1 | 0 | 56
38952.6319 | 1 | 0 | 56
38952.634 | 1 | 0 | 56
38952.6362 | 1 | 0 | 56
38952.6383 | 1 | 0 | 56
38952.6405 | 1 | 0 | 56
38952.6426 | 1 | 0 | 56
38952.6447 | 2 | 0 | 56
38952.6469 | 2 | 0 | 56
38952.649 | 2 | 0 | 56
38952.6511 | 2 | 0 | 56
38952.6533 | 2 | 0 | 56
38952.6554 | 2 | 0 | 56
56
38952.6276 | 1 | 0 | 57
38952.6298 | 1 | 0 | 57
38952.6319 | 1 | 0 | 57
38952.6341 | 1 | 0 | 57
38952.6362 | 1 | 0 | 57
38952.6383 | 1 | 0 | 57
38952.6405 | 1 | 0 | 57
38952.6426 | 1 | 0 | 57
38952.6447 | 2 | 0 | 57
38952.6469 | 4 | 0 | 57
38952.649 | 131 | 0 | 57
38952.6512 | 60 | 0 | 57
38952.6533 | 13 | 0 | 57
38952.6554 | 2 | 0 | 57
57
38952.6277 | 2 | 0 | 58
38952.6298 | 1 | 0 | 58
38952.6319 | 1 | 0 | 58
38952.6341 | 1 | 0 | 58
38952.6362 | 1 | 0 | 58
38952.6383 | 1 | 0 | 58
38952.6405 | 1 | 0 | 58
38952.6426 | 2449 | 0 | 58
38952.6448 | 2015 | 0 | 58
38952.6469 | 2188 | 0 | 58
38952.649 | 2455 | 0 | 58
38952.6512 | 1793 | 0 | 58
38952.6533 | 2 | 0 | 58
38952.6555 | 2 | 0 | 58
58
38952.6277 | 1 | 0 | 59
38952.6298 | 1 | 0 | 59
38952.6319 | 1 | 0 | 59
38952.6341 | 1 | 0 | 59
38952.6362 | 1 | 0 | 59
38952.6384 | 1 | 0 | 59
38952.6405 | 1 | 0 | 59
38952.6426 | 3 | 0 | 59
38952.6448 | 3 | 0 | 59
38952.6469 | 5 | 0 | 59
38952.6491 | 178 | 0 | 59
38952.6512 | 60 | 0 | 59
38952.6533 | 13 | 0 | 59
38952.6555 | 2 | 0 | 59
59
38952.6277 | 1 | 0 | 60
38952.6298 | 1 | 0 | 60
38952.632 | 1 | 0 | 60
38952.6341 | 1 | 0 | 60
38952.6362 | 1 | 0 | 60
38952.6384 | 1 | 0 | 60
38952.6405 | 1 | 0 | 60
38952.6427 | 2001 | 0 | 60
38952.6448 | 1818 | 0 | 60
38952.6469 | 1933 | 0 | 60
38952.6491 | 1839 | 0 | 60
38952.6512 | 1692 | 0 | 60
38952.6533 | 21 | 0 | 60
38952.6555 | 2 | 0 | 60
60
38952.6277 | 1 | 0 | 61
38952.6298 | 1 | 0 | 61
38952.632 | 1 | 0 | 61
38952.6341 | 1 | 0 | 61
38952.6363 | 1 | 0 | 61
38952.6384 | 1 | 0 | 61
38952.6405 | 1 | 0 | 61
38952.6427 | 3 | 0 | 61
38952.6448 | 3 | 0 | 61
38952.6469 | 5 | 0 | 61
38952.6491 | 148 | 0 | 61
38952.6512 | 58 | 0 | 61
38952.6534 | 14 | 0 | 61
38952.6555 | 2 | 0 | 61
61
38952.6277 | 1 | 0 | 62
38952.6298 | 1 | 0 | 62
38952.632 | 1 | 0 | 62
38952.6341 | 1 | 0 | 62
38952.6363 | 1 | 0 | 62
38952.6384 | 1 | 0 | 62
38952.6405 | 1 | 0 | 62
38952.6427 | 2 | 0 | 62
38952.6448 | 2 | 0 | 62
38952.647 | 2 | 0 | 62
38952.6491 | 2 | 0 | 62
38952.6512 | 2 | 0 | 62
38952.6534 | 2 | 0 | 62
38952.6555 | 2 | 0 | 62
62
38952.6277 | 1 | 0 | 63
38952.6299 | 1 | 0 | 63
38952.632 | 1 | 0 | 63
38952.6341 | 1 | 0 | 63
38952.6363 | 1 | 0 | 63
38952.6384 | 1 | 0 | 63
38952.6406 | 1 | 0 | 63
38952.6427 | 2 | 0 | 63
38952.6448 | 2 | 0 | 63
38952.647 | 6 | 0 | 63
38952.6491 | 173 | 0 | 63
38952.6513 | 69 | 0 | 63
38952.6534 | 15 | 0 | 63
38952.6555 | 2 | 0 | 63
63
38952.6277 | 1 | 0 | 64
38952.6299 | 1 | 0 | 64
38952.632 | 1 | 0 | 64
38952.6342 | 1 | 0 | 64
38952.6363 | 1 | 0 | 64
38952.6384 | 1 | 0 | 64
38952.6406 | 1 | 0 | 64
38952.6427 | 2 | 0 | 64
38952.6448 | 2 | 0 | 64
38952.647 | 2 | 0 | 64
38952.6491 | 2 | 0 | 64
38952.6513 | 2 | 0 | 64
38952.6534 | 2 | 0 | 64
38952.6555 | 1 | 0 | 64
64
38952.6278 | 1 | 0 | 65
38952.6299 | 1 | 0 | 65
38952.632 | 1 | 0 | 65
38952.6342 | 1 | 0 | 65
38952.6363 | 1 | 0 | 65
38952.6384 | 1 | 0 | 65
38952.6406 | 1 | 0 | 65
38952.6427 | 2 | 0 | 65
38952.6449 | 2 | 0 | 65
38952.647 | 7 | 0 | 65
38952.6491 | 191 | 0 | 65
38952.6513 | 66 | 0 | 65
38952.6534 | 15 | 0 | 65
38952.6556 | 2 | 0 | 65
65
38952.6278 | 1 | 0 | 66
38952.6299 | 1 | 0 | 66
38952.632 | 1 | 0 | 66
38952.6342 | 1 | 0 | 66
38952.6363 | 1 | 0 | 66
38952.6385 | 1 | 0 | 66
38952.6406 | 1 | 0 | 66
38952.6427 | 1 | 0 | 66
38952.6449 | 2336 | 0 | 66
38952.647 | 2153 | 0 | 66
38952.6492 | 2162 | 0 | 66
38952.6513 | 2394 | 0 | 66
38952.6534 | 2271 | 0 | 66
38952.6556 | 2153 | 0 | 66
66
38952.6278 | 1 | 0 | 67
38952.6299 | 1 | 0 | 67
38952.6321 | 1 | 0 | 67
38952.6342 | 1 | 0 | 67
38952.6364 | 1 | 0 | 67
38952.6385 | 1 | 0 | 67
38952.6406 | 1 | 0 | 67
38952.6428 | 1 | 0 | 67
38952.6449 | 3 | 0 | 67
38952.647 | 8 | 0 | 67
38952.6492 | 174 | 0 | 67
38952.6513 | 67 | 0 | 67
38952.6535 | 18 | 0 | 67
38952.6556 | 3 | 0 | 67
67
38952.6278 | 1 | 0 | 68
38952.63 | 1 | 0 | 68
38952.6321 | 1 | 0 | 68
38952.6342 | 1 | 0 | 68
38952.6364 | 1 | 0 | 68
38952.6385 | 1 | 0 | 68
38952.6406 | 1 | 0 | 68
38952.6428 | 1 | 0 | 68
38952.6449 | 2376 | 0 | 68
38952.6471 | 2227 | 0 | 68
38952.6492 | 1653 | 0 | 68
38952.6513 | 1562 | 0 | 68
38952.6535 | 2188 | 0 | 68
38952.6556 | 1989 | 0 | 68
68
38952.6278 | 1 | 0 | 69
38952.63 | 1 | 0 | 69
38952.6321 | 1 | 0 | 69
38952.6342 | 1 | 0 | 69
38952.6364 | 1 | 0 | 69
38952.6385 | 1 | 0 | 69
38952.6407 | 1 | 0 | 69
38952.6428 | 1 | 0 | 69
38952.6449 | 3 | 0 | 69
38952.6471 | 9 | 1 | 69
38952.6492 | 178 | 0 | 69
38952.6514 | 68 | 0 | 69
38952.6535 | 16 | 0 | 69
38952.6556 | 3 | 0 | 69
69
38952.6278 | 1 | 0 | 70
38952.63 | 1 | 0 | 70
38952.6321 | 1 | 0 | 70
38952.6343 | 1 | 0 | 70
38952.6364 | 1 | 0 | 70
38952.6385 | 1 | 0 | 70
38952.6407 | 1 | 0 | 70
38952.6428 | 1 | 0 | 70
38952.645 | 2 | 0 | 70
38952.6471 | 2 | 0 | 70
38952.6492 | 2 | 0 | 70
38952.6514 | 2 | 0 | 70
38952.6535 | 2 | 0 | 70
38952.6556 | 2 | 0 | 70
70
38952.6279 | 1 | 0 | 71
38952.63 | 1 | 0 | 71
38952.6321 | 1 | 0 | 71
38952.6343 | 1 | 0 | 71
38952.6364 | 1 | 0 | 71
38952.6386 | 1 | 0 | 71
38952.6407 | 1 | 0 | 71
38952.6428 | 1 | 0 | 71
38952.645 | 2 | 0 | 71
38952.6471 | 10 | 0 | 71
38952.6492 | 189 | 0 | 71
38952.6514 | 72 | 0 | 71
38952.6535 | 16 | 0 | 71
38952.6557 | 2 | 0 | 71
71
38952.6279 | 1 | 0 | 72
38952.63 | 1 | 0 | 72
38952.6322 | 1 | 0 | 72
38952.6343 | 1 | 0 | 72
38952.6364 | 1 | 0 | 72
38952.6386 | 1 | 0 | 72
38952.6407 | 1 | 0 | 72
38952.6428 | 2 | 0 | 72
38952.645 | 2 | 0 | 72
38952.6471 | 2 | 0 | 72
38952.6493 | 2 | 0 | 72
38952.6514 | 2 | 0 | 72
38952.6535 | 2 | 0 | 72
38952.6557 | 1 | 0 | 72
72
38952.6279 | 1 | 0 | 73
38952.63 | 1 | 0 | 73
38952.6322 | 1 | 0 | 73
38952.6343 | 1 | 0 | 73
38952.6364 | 1 | 0 | 73
38952.6386 | 1 | 0 | 73
38952.6407 | 1 | 0 | 73
38952.6429 | 1 | 0 | 73
38952.645 | 2 | 0 | 73
38952.6471 | 12 | 0 | 73
38952.6493 | 148 | 0 | 73
38952.6514 | 62 | 0 | 73
38952.6536 | 15 | 0 | 73
38952.6557 | 2 | 0 | 73
73
38952.6279 | 1 | 0 | 74
38952.63 | 1 | 0 | 74
38952.6322 | 1 | 0 | 74
38952.6343 | 1 | 0 | 74
38952.6365 | 1 | 0 | 74
38952.6386 | 1 | 0 | 74
38952.6407 | 1 | 0 | 74
38952.6429 | 2125 | 0 | 74
38952.645 | 1623 | 0 | 74
38952.6472 | 2363 | 0 | 74
38952.6493 | 1915 | 0 | 74
38952.6514 | 1752 | 0 | 74
38952.6536 | 2 | 0 | 74
38952.6557 | 1 | 0 | 74
74
38952.6279 | 1 | 0 | 75
38952.6301 | 1 | 0 | 75
38952.6322 | 1 | 0 | 75
38952.6343 | 1 | 0 | 75
38952.6365 | 1 | 0 | 75
38952.6386 | 1 | 0 | 75
38952.6408 | 1 | 0 | 75
38952.6429 | 2 | 0 | 75
38952.645 | 2 | 0 | 75
38952.6472 | 15 | 0 | 75
38952.6493 | 149 | 0 | 75
38952.6514 | 66 | 0 | 75
38952.6536 | 17 | 0 | 75
38952.6557 | 2 | 0 | 75
75
38952.6279 | 1 | 0 | 76
38952.6301 | 1 | 0 | 76
38952.6322 | 1 | 0 | 76
38952.6344 | 1 | 0 | 76
38952.6365 | 1 | 0 | 76
38952.6386 | 1 | 0 | 76
38952.6408 | 1 | 0 | 76
38952.6429 | 2271 | 0 | 76
38952.645 | 1649 | 0 | 76
38952.6472 | 2096 | 0 | 76
38952.6493 | 1582 | 0 | 76
38952.6515 | 594 | 0 | 76
38952.6536 | 6 | 0 | 76
38952.6557 | 2 | 0 | 76
76
38952.628 | 1 | 0 | 77
38952.6301 | 1 | 0 | 77
38952.6322 | 1 | 0 | 77
38952.6344 | 1 | 0 | 77
38952.6365 | 1 | 0 | 77
38952.6386 | 1 | 0 | 77
38952.6408 | 1 | 0 | 77
38952.6429 | 3 | 0 | 77
38952.6451 | 956 | 927 | 77
38952.6472 | 1085 | 1054 | 77
38952.6493 | 1112 | 1074 | 77
38952.6515 | 1176 | 1199 | 77
38952.6536 | 1078 | 1170 | 77
38952.6558 | 993 | 970 | 77
77
38952.628 | 1 | 0 | 78
38952.6301 | 1 | 0 | 78
38952.6322 | 1 | 0 | 78
38952.6344 | 1 | 0 | 78
38952.6365 | 1 | 0 | 78
38952.6387 | 1 | 0 | 78
38952.6408 | 1 | 0 | 78
38952.6429 | 2 | 0 | 78
38952.6451 | 1026 | 1069 | 78
38952.6472 | 1202 | 1175 | 78
38952.6494 | 1089 | 1052 | 78
38952.6515 | 1108 | 1079 | 78
38952.6536 | 1005 | 979 | 78
38952.6558 | 962 | 1084 | 78
78
38952.628 | 1 | 0 | 79
38952.6301 | 1 | 0 | 79
38952.6323 | 1 | 0 | 79
38952.6344 | 1 | 0 | 79
38952.6365 | 1 | 0 | 79
38952.6387 | 1 | 0 | 79
38952.6408 | 1 | 0 | 79
38952.643 | 2 | 0 | 79
38952.6451 | 2 | 4 | 79
38952.6472 | 3 | 4 | 79
38952.6494 | 2 | 4 | 79
38952.6515 | 2 | 4 | 79
38952.6536 | 2 | 4 | 79
38952.6558 | 2 | 4 | 79
79
38952.628 | 1 | 0 | 80
38952.6301 | 1 | 0 | 80
38952.6323 | 1 | 0 | 80
38952.6344 | 1 | 0 | 80
38952.6366 | 1 | 0 | 80
38952.6387 | 1 | 0 | 80
38952.6408 | 1 | 0 | 80
38952.643 | 2 | 0 | 80
38952.6451 | 2095 | 2 | 80
38952.6472 | 2426 | 2 | 80
38952.6494 | 2049 | 2 | 80
38952.6515 | 2446 | 2 | 80
38952.6537 | 2088 | 2 | 80
38952.6558 | 2165 | 2 | 80
80
38952.628 | 1 | 0 | 81
38952.6302 | 1 | 0 | 81
38952.6323 | 1 | 0 | 81
38952.6344 | 1 | 0 | 81
38952.6366 | 1 | 0 | 81
38952.6387 | 1 | 0 | 81
38952.6409 | 1 | 0 | 81
38952.643 | 2 | 0 | 81
38952.6451 | 3 | 1 | 81
38952.6473 | 3 | 1 | 81
38952.6494 | 3 | 1 | 81
38952.6515 | 3 | 1 | 81
38952.6537 | 3 | 1 | 81
38952.6558 | 3 | 1 | 81
81
38952.628 | 1 | 0 | 82
38952.6302 | 1 | 0 | 82
38952.6323 | 1 | 0 | 82
38952.6345 | 1 | 0 | 82
38952.6366 | 1 | 0 | 82
38952.6387 | 1 | 0 | 82
38952.6409 | 1 | 0 | 82
38952.643 | 1 | 0 | 82
38952.6452 | 1920 | 1 | 82
38952.6473 | 2009 | 1 | 82
38952.6494 | 1606 | 1 | 82
38952.6516 | 1999 | 1 | 82
38952.6537 | 1837 | 0 | 82
38952.6558 | 2222 | 1 | 82
82
38952.6281 | 1 | 0 | 83
38952.6302 | 1 | 0 | 83
38952.6323 | 1 | 0 | 83
38952.6345 | 1 | 0 | 83
38952.6366 | 1 | 0 | 83
38952.6387 | 1 | 0 | 83
38952.6409 | 1 | 0 | 83
38952.643 | 2 | 0 | 83
38952.6452 | 3 | 0 | 83
38952.6473 | 3 | 0 | 83
38952.6494 | 3 | 1 | 83
38952.6516 | 3 | 0 | 83
38952.6537 | 3 | 1 | 83
38952.6559 | 3 | 1 | 83
83
38952.6281 | 1 | 0 | 84
38952.6302 | 1 | 0 | 84
38952.6323 | 1 | 0 | 84
38952.6345 | 1 | 0 | 84
38952.6366 | 1 | 0 | 84
38952.6388 | 1 | 0 | 84
38952.6409 | 1 | 0 | 84
38952.643 | 1 | 0 | 84
38952.6452 | 2 | 0 | 84
38952.6473 | 3 | 0 | 84
38952.6495 | 2 | 0 | 84
38952.6516 | 2 | 0 | 84
38952.6537 | 2 | 0 | 84
38952.6559 | 2 | 0 | 84
84
38952.6281 | 1 | 0 | 85
38952.6302 | 1 | 0 | 85
38952.6324 | 1 | 0 | 85
38952.6345 | 1 | 0 | 85
38952.6366 | 1 | 0 | 85
38952.6388 | 1 | 0 | 85
38952.6409 | 1 | 0 | 85
38952.6431 | 1 | 0 | 85
38952.6452 | 2 | 0 | 85
38952.6473 | 2 | 0 | 85
38952.6495 | 2 | 0 | 85
38952.6516 | 2 | 0 | 85
38952.6537 | 2 | 0 | 85
38952.6559 | 2 | 0 | 85
85
38952.6281 | 1 | 0 | 86
38952.6302 | 1 | 0 | 86
38952.6324 | 1 | 0 | 86
38952.6345 | 2 | 0 | 86
38952.6367 | 1 | 0 | 86
38952.6388 | 1 | 0 | 86
38952.6409 | 1 | 0 | 86
38952.6431 | 1 | 0 | 86
38952.6452 | 2 | 0 | 86
38952.6473 | 3 | 0 | 86
38952.6495 | 2 | 0 | 86
38952.6516 | 2 | 0 | 86
38952.6538 | 2 | 0 | 86
38952.6559 | 2 | 0 | 86
86
38952.6281 | 1 | 0 | 87
38952.6303 | 1 | 0 | 87
38952.6324 | 1 | 0 | 87
38952.6345 | 1 | 0 | 87
38952.6367 | 1 | 0 | 87
38952.6388 | 1 | 0 | 87
38952.6409 | 1 | 0 | 87
38952.6431 | 1 | 0 | 87
38952.6452 | 2 | 0 | 87
38952.6474 | 2 | 0 | 87
38952.6495 | 2 | 0 | 87
38952.6516 | 3 | 0 | 87
38952.6538 | 2 | 0 | 87
38952.6559 | 1 | 0 | 87
87
38952.6281 | 1 | 0 | 88
38952.6303 | 1 | 0 | 88
38952.6324 | 1 | 0 | 88
38952.6345 | 1 | 0 | 88
38952.6367 | 1 | 0 | 88
38952.6388 | 1 | 0 | 88
38952.641 | 1 | 0 | 88
38952.6431 | 1941 | 0 | 88
38952.6452 | 2013 | 0 | 88
38952.6474 | 2021 | 0 | 88
38952.6495 | 1984 | 0 | 88
38952.6517 | 989 | 0 | 88
38952.6538 | 3 | 0 | 88
38952.6559 | 1 | 0 | 88
88
38952.6281 | 1 | 0 | 89
38952.6303 | 1 | 0 | 89
38952.6324 | 1 | 0 | 89
38952.6346 | 1 | 0 | 89
38952.6367 | 1 | 0 | 89
38952.6388 | 1 | 0 | 89
38952.641 | 1 | 0 | 89
38952.6431 | 3 | 0 | 89
38952.6453 | 3 | 0 | 89
38952.6474 | 3 | 0 | 89
38952.6495 | 3 | 0 | 89
38952.6517 | 2 | 1 | 89
38952.6538 | 2 | 0 | 89
38952.6559 | 1 | 0 | 89
89
38952.6282 | 1 | 0 | 90
38952.6303 | 1 | 0 | 90
38952.6324 | 1 | 0 | 90
38952.6346 | 1 | 0 | 90
38952.6367 | 1 | 0 | 90
38952.6389 | 1 | 0 | 90
38952.641 | 1 | 0 | 90
38952.6431 | 2161 | 0 | 90
38952.6453 | 1736 | 0 | 90
38952.6474 | 2392 | 0 | 90
38952.6495 | 1716 | 0 | 90
38952.6517 | 1356 | 0 | 90
38952.6538 | 2 | 0 | 90
38952.656 | 1 | 0 | 90
90
38952.6282 | 1 | 0 | 91
38952.6303 | 1 | 0 | 91
38952.6325 | 1 | 0 | 91
38952.6346 | 1 | 0 | 91
38952.6367 | 1 | 0 | 91
38952.6389 | 1 | 0 | 91
38952.641 | 1 | 0 | 91
38952.6431 | 3 | 0 | 91
38952.6453 | 3 | 0 | 91
38952.6474 | 3 | 0 | 91
38952.6496 | 2 | 0 | 91
38952.6517 | 3 | 0 | 91
38952.6538 | 2 | 0 | 91
38952.656 | 1 | 0 | 91
91
38952.6282 | 1 | 0 | 92
38952.6303 | 1 | 0 | 92
38952.6325 | 1 | 0 | 92
38952.6346 | 1 | 0 | 92
38952.6367 | 1 | 0 | 92
38952.6389 | 1 | 0 | 92
38952.641 | 1 | 0 | 92
38952.6432 | 3 | 0 | 92
38952.6453 | 2312 | 0 | 92
38952.6474 | 2509 | 0 | 92
38952.6496 | 2492 | 0 | 92
38952.6517 | 2423 | 0 | 92
38952.6539 | 2272 | 0 | 92
38952.656 | 2329 | 0 | 92
92
38952.6282 | 1 | 0 | 93
38952.6304 | 1 | 0 | 93
38952.6325 | 1 | 0 | 93
38952.6346 | 1 | 0 | 93
38952.6368 | 1 | 0 | 93
38952.6389 | 1 | 0 | 93
38952.641 | 1 | 0 | 93
38952.6432 | 2 | 0 | 93
38952.6453 | 3 | 0 | 93
38952.6475 | 3 | 0 | 93
38952.6496 | 2 | 0 | 93
38952.6517 | 3 | 0 | 93
38952.6539 | 3 | 0 | 93
38952.656 | 3 | 0 | 93
93
38952.6282 | 1 | 0 | 94
38952.6304 | 1 | 0 | 94
38952.6325 | 1 | 0 | 94
38952.6346 | 1 | 0 | 94
38952.6368 | 1 | 0 | 94
38952.6389 | 1 | 0 | 94
38952.6411 | 1 | 0 | 94
38952.6432 | 2 | 0 | 94
38952.6453 | 2081 | 0 | 94
38952.6475 | 2094 | 0 | 94
38952.6496 | 1708 | 0 | 94
38952.6518 | 1879 | 0 | 94
38952.6539 | 1424 | 0 | 94
38952.656 | 1831 | 0 | 94
94
38952.6283 | 1 | 0 | 95
38952.6304 | 1 | 0 | 95
38952.6325 | 1 | 0 | 95
38952.6347 | 1 | 0 | 95
38952.6368 | 1 | 0 | 95
38952.6389 | 1 | 0 | 95
38952.6411 | 1 | 0 | 95
38952.6432 | 1 | 0 | 95
38952.6454 | 3 | 0 | 95
38952.6475 | 2 | 0 | 95
38952.6496 | 3 | 0 | 95
38952.6518 | 2 | 0 | 95
38952.6539 | 3 | 0 | 95
38952.6561 | 2 | 0 | 95
95
38952.6283 | 1 | 0 | 96
38952.6304 | 1 | 0 | 96
38952.6325 | 1 | 0 | 96
38952.6347 | 1 | 0 | 96
38952.6368 | 1 | 0 | 96
38952.639 | 1 | 0 | 96
38952.6411 | 1 | 0 | 96
38952.6432 | 2 | 0 | 96
38952.6454 | 2 | 0 | 96
38952.6475 | 2 | 0 | 96
38952.6497 | 2 | 0 | 96
38952.6518 | 2 | 0 | 96
38952.6539 | 2 | 0 | 96
38952.6561 | 2 | 0 | 96
96
38952.6283 | 1 | 0 | 97
38952.6304 | 1 | 0 | 97
38952.6326 | 1 | 0 | 97
38952.6347 | 1 | 0 | 97
38952.6368 | 1 | 0 | 97
38952.639 | 1 | 0 | 97
38952.6411 | 1 | 0 | 97
38952.6433 | 1 | 0 | 97
38952.6454 | 2 | 0 | 97
38952.6475 | 3 | 0 | 97
38952.6497 | 2 | 0 | 97
38952.6518 | 2 | 0 | 97
38952.6539 | 2 | 0 | 97
38952.6561 | 2 | 0 | 97
97
38952.6283 | 1 | 0 | 98
38952.6304 | 1 | 0 | 98
38952.6326 | 1 | 0 | 98
38952.6347 | 1 | 0 | 98
38952.6369 | 1 | 0 | 98
38952.639 | 1 | 0 | 98
38952.6411 | 1 | 0 | 98
38952.6433 | 2 | 0 | 98
38952.6454 | 2 | 0 | 98
38952.6475 | 2 | 0 | 98
38952.6497 | 2 | 1 | 98
38952.6518 | 2 | 0 | 98
38952.654 | 2 | 0 | 98
38952.6561 | 2 | 0 | 98
98
38952.6283 | 1 | 0 | 99
38952.6305 | 1 | 0 | 99
38952.6326 | 1 | 0 | 99
38952.6347 | 1 | 0 | 99
38952.6369 | 1 | 0 | 99
38952.639 | 1 | 0 | 99
38952.6411 | 1 | 0 | 99
38952.6433 | 1 | 0 | 99
38952.6454 | 2 | 0 | 99
38952.6476 | 2 | 0 | 99
38952.6497 | 2 | 0 | 99
38952.6518 | 2 | 0 | 99
38952.654 | 2 | 0 | 99
38952.6561 | 2 | 0 | 99
99
38952.6283 | 1 | 0 | 100
38952.6305 | 1 | 0 | 100
38952.6326 | 1 | 0 | 100
38952.6347 | 1 | 0 | 100
38952.6369 | 1 | 0 | 100
38952.639 | 1 | 0 | 100
38952.6412 | 1 | 0 | 100
38952.6433 | 2192 | 0 | 100
38952.6454 | 1933 | 0 | 100
38952.6476 | 2263 | 0 | 100
38952.6497 | 2167 | 0 | 100
38952.6519 | 1647 | 0 | 100
38952.654 | 2 | 0 | 100
38952.6561 | 2 | 0 | 100
100
38952.6283 | 1 | 0 | 101
38952.6305 | 1 | 0 | 101
38952.6326 | 1 | 0 | 101
38952.6348 | 1 | 0 | 101
38952.6369 | 1 | 0 | 101
38952.639 | 1 | 0 | 101
38952.6412 | 1 | 0 | 101
38952.6433 | 3 | 0 | 101
38952.6455 | 3 | 0 | 101
38952.6476 | 3 | 0 | 101
38952.6497 | 2 | 0 | 101
38952.6519 | 3 | 0 | 101
38952.654 | 2 | 0 | 101
38952.6561 | 1 | 0 | 101
101
38952.6284 | 1 | 0 | 102
38952.6305 | 1 | 0 | 102
38952.6326 | 1 | 0 | 102
38952.6348 | 1 | 0 | 102
38952.6369 | 1 | 0 | 102
38952.6391 | 1 | 0 | 102
38952.6412 | 1 | 0 | 102
38952.6455 | 1466 | 0 | 102
38952.6476 | 1609 | 0 | 102
38952.6497 | 1344 | 0 | 102
38952.6519 | 1768 | 0 | 102
38952.654 | 1 | 0 | 102
38952.6562 | 2 | 0 | 102
102
38952.6284 | 1 | 0 | 103
38952.6305 | 1 | 0 | 103
38952.6327 | 1 | 0 | 103
38952.6348 | 1 | 0 | 103
38952.6369 | 1 | 0 | 103
38952.6391 | 1 | 0 | 103
38952.6412 | 1074 | 1037 | 103
38952.6433 | 913 | 876 | 103
38952.6455 | 2410 | 0 | 103
38952.6476 | 2017 | 0 | 103
38952.6498 | 2105 | 0 | 103
38952.6519 | 1998 | 0 | 103
38952.654 | 2080 | 0 | 103
38952.6562 | 2353 | 0 | 103
103
38952.6284 | 1 | 0 | 104
38952.6305 | 1 | 0 | 104
38952.6327 | 1 | 0 | 104
38952.6348 | 1 | 0 | 104
38952.6369 | 1 | 0 | 104
38952.6391 | 1 | 0 | 104
38952.6412 | 1166 | 1129 | 104
38952.6434 | 964 | 962 | 104
38952.6455 | 1875 | 0 | 104
38952.6476 | 2009 | 0 | 104
38952.6498 | 1664 | 0 | 104
38952.6519 | 2150 | 0 | 104
38952.6541 | 1387 | 0 | 104
38952.6562 | 2354 | 0 | 104
104
38952.6284 | 1 | 0 | 105
38952.6305 | 1 | 0 | 105
38952.6327 | 1 | 0 | 105
38952.6348 | 1 | 0 | 105
38952.637 | 1 | 0 | 105
38952.6391 | 1 | 0 | 105
38952.6412 | 2 | 4 | 105
38952.6434 | 5 | 4 | 105
38952.6455 | 2127 | 0 | 105
38952.6477 | 2460 | 0 | 105
38952.6498 | 2148 | 0 | 105
38952.6519 | 2337 | 0 | 105
38952.6541 | 2199 | 0 | 105
38952.6562 | 2396 | 0 | 105
105
38952.6284 | 1 | 0 | 106
38952.6306 | 1 | 0 | 106
38952.6327 | 1 | 0 | 106
38952.6348 | 1 | 0 | 106
38952.637 | 1 | 0 | 106
38952.6391 | 1 | 0 | 106
38952.6413 | 3 | 2 | 106
38952.6434 | 3 | 2 | 106
38952.6455 | 3 | 0 | 106
38952.6477 | 3 | 0 | 106
38952.6498 | 3 | 0 | 106
38952.6519 | 3 | 0 | 106
38952.6541 | 2 | 0 | 106
38952.6562 | 3 | 0 | 106
106
38952.6284 | 1 | 0 | 107
38952.6306 | 1 | 0 | 107
38952.6327 | 1 | 0 | 107
38952.6349 | 1 | 0 | 107
38952.637 | 1 | 0 | 107
38952.6391 | 1 | 0 | 107
38952.6413 | 1 | 1 | 107
38952.6434 | 3 | 1 | 107
38952.6456 | 2231 | 0 | 107
38952.6477 | 2047 | 0 | 107
38952.6498 | 2449 | 0 | 107
38952.652 | 1983 | 0 | 107
38952.6541 | 2252 | 0 | 107
38952.6562 | 2177 | 0 | 107
107
38952.6285 | 1 | 0 | 108
38952.6306 | 1 | 0 | 108
38952.6327 | 1 | 0 | 108
38952.6349 | 1 | 0 | 108
38952.637 | 1 | 0 | 108
38952.6392 | 1 | 0 | 108
38952.6413 | 1 | 1 | 108
38952.6434 | 2 | 0 | 108
38952.6456 | 3 | 0 | 108
38952.6477 | 3 | 0 | 108
38952.6498 | 3 | 0 | 108
38952.652 | 3 | 0 | 108
38952.6541 | 3 | 0 | 108
38952.6563 | 3 | 0 | 108
108
38952.6285 | 1 | 0 | 109
38952.6306 | 1 | 0 | 109
38952.6328 | 1 | 0 | 109
38952.6349 | 1 | 0 | 109
38952.637 | 1 | 0 | 109
38952.6392 | 1 | 0 | 109
38952.6413 | 1 | 0 | 109
38952.6434 | 3 | 1 | 109
38952.6456 | 2174 | 0 | 109
38952.6477 | 2514 | 0 | 109
38952.6499 | 2042 | 0 | 109
38952.652 | 2140 | 0 | 109
38952.6541 | 2263 | 0 | 109
38952.6563 | 2232 | 0 | 109
109
38952.6285 | 1 | 0 | 110
38952.6306 | 1 | 0 | 110
38952.6328 | 1 | 0 | 110
38952.6349 | 1 | 0 | 110
38952.637 | 1 | 0 | 110
38952.6392 | 1 | 0 | 110
38952.6413 | 1 | 0 | 110
38952.6435 | 2067 | 0 | 110
38952.6456 | 1257 | 0 | 110
38952.6477 | 2295 | 0 | 110
38952.6499 | 2179 | 0 | 110
38952.652 | 905 | 0 | 110
38952.6542 | 3 | 0 | 110
38952.6563 | 3 | 0 | 110
110
38952.6285 | 1 | 0 | 111
38952.6306 | 1 | 0 | 111
38952.6328 | 1 | 0 | 111
38952.6349 | 1 | 0 | 111
38952.6371 | 1 | 0 | 111
38952.6392 | 1 | 0 | 111
38952.6413 | 1 | 0 | 111
38952.6435 | 5 | 0 | 111
38952.6456 | 1962 | 0 | 111
38952.6478 | 2512 | 1 | 111
38952.6499 | 2074 | 0 | 111
38952.652 | 2377 | 0 | 111
38952.6542 | 2253 | 0 | 111
38952.6563 | 2292 | 0 | 111
111
38952.6285 | 1 | 0 | 112
38952.6307 | 1 | 0 | 112
38952.6328 | 1 | 0 | 112
38952.6349 | 1 | 0 | 112
38952.6371 | 1 | 0 | 112
38952.6392 | 1 | 0 | 112
38952.6414 | 1 | 0 | 112
38952.6435 | 1829 | 1 | 112
38952.6456 | 2061 | 0 | 112
38952.6478 | 1949 | 0 | 112
38952.6499 | 1805 | 0 | 112
38952.652 | 1677 | 0 | 112
38952.6542 | 3 | 0 | 112
38952.6563 | 3 | 0 | 112
112
38952.6285 | 1 | 0 | 113
38952.6307 | 1 | 0 | 113
38952.6328 | 1 | 0 | 113
38952.635 | 1 | 0 | 113
38952.6371 | 1 | 0 | 113
38952.6392 | 1 | 0 | 113
38952.6414 | 1 | 0 | 113
38952.6435 | 6 | 0 | 113
38952.6456 | 2155 | 0 | 113
38952.6478 | 1765 | 0 | 113
38952.6499 | 1814 | 0 | 113
38952.6521 | 1865 | 0 | 113
38952.6542 | 1422 | 0 | 113
38952.6563 | 2347 | 0 | 113
113
38952.6286 | 1 | 0 | 114
38952.6307 | 1 | 0 | 114
38952.6328 | 1 | 0 | 114
38952.635 | 1 | 0 | 114
38952.6371 | 1 | 0 | 114
38952.6392 | 1 | 0 | 114
38952.6414 | 1 | 0 | 114
38952.6435 | 2 | 0 | 114
38952.6457 | 3 | 0 | 114
38952.6478 | 3 | 0 | 114
38952.6499 | 3 | 0 | 114
38952.6521 | 3 | 0 | 114
38952.6542 | 3 | 0 | 114
38952.6564 | 3 | 0 | 114
114
38952.6286 | 1 | 0 | 115
38952.6307 | 1 | 0 | 115
38952.6328 | 1 | 0 | 115
38952.635 | 1 | 0 | 115
38952.6371 | 1 | 0 | 115
38952.6393 | 1 | 0 | 115
38952.6414 | 1 | 0 | 115
38952.6435 | 7 | 0 | 115
38952.6457 | 2154 | 0 | 115
38952.6478 | 1821 | 0 | 115
38952.65 | 1938 | 0 | 115
38952.6521 | 1707 | 0 | 115
38952.6542 | 1818 | 0 | 115
38952.6564 | 2312 | 0 | 115
115
38952.6286 | 1 | 0 | 116
38952.6307 | 1 | 0 | 116
38952.6329 | 1 | 0 | 116
38952.635 | 1 | 0 | 116
38952.6371 | 1 | 0 | 116
38952.6393 | 1 | 0 | 116
38952.6414 | 1 | 0 | 116
38952.6436 | 1 | 0 | 116
38952.6457 | 3 | 0 | 116
38952.6478 | 2 | 0 | 116
38952.65 | 3 | 0 | 116
38952.6521 | 3 | 0 | 116
38952.6542 | 3 | 0 | 116
38952.6564 | 2 | 0 | 116
116
38952.6286 | 1 | 0 | 117
38952.6307 | 1 | 0 | 117
38952.6329 | 1 | 0 | 117
38952.635 | 1 | 0 | 117
38952.6372 | 1 | 0 | 117
38952.6393 | 1 | 0 | 117
38952.6414 | 1 | 0 | 117
38952.6436 | 14 | 0 | 117
38952.6457 | 1852 | 0 | 117
38952.6478 | 1747 | 0 | 117
38952.65 | 1886 | 0 | 117
38952.6521 | 1883 | 0 | 117
38952.6543 | 1443 | 0 | 117
38952.6564 | 2179 | 0 | 117
117
38952.6286 | 1 | 0 | 118
38952.6308 | 1 | 0 | 118
38952.6329 | 1 | 0 | 118
38952.635 | 1 | 0 | 118
38952.6372 | 1 | 0 | 118
38952.6393 | 1 | 0 | 118
38952.6414 | 1 | 0 | 118
38952.6436 | 1316 | 0 | 118
38952.6457 | 2033 | 0 | 118
38952.6479 | 1997 | 0 | 118
38952.65 | 2137 | 0 | 118
38952.6521 | 17 | 0 | 118
38952.6543 | 3 | 0 | 118
38952.6564 | 319 | 0 | 118
118
38952.6286 | 1 | 0 | 119
38952.6308 | 1 | 0 | 119
38952.635 | 1 | 0 | 119
38952.6372 | 1 | 0 | 119
38952.6393 | 1 | 0 | 119
38952.6415 | 1 | 0 | 119
38952.6436 | 21 | 0 | 119
38952.6457 | 2094 | 0 | 119
38952.6479 | 1947 | 0 | 119
38952.65 | 1751 | 0 | 119
38952.6522 | 1875 | 0 | 119
38952.6543 | 1800 | 0 | 119
38952.6564 | 2215 | 0 | 119
119
38952.6287 | 1 | 0 | 120
38952.6308 | 1 | 0 | 120
38952.6329 | 1 | 0 | 120
38952.6351 | 1 | 0 | 120
38952.6372 | 1 | 0 | 120
38952.6393 | 1 | 0 | 120
38952.6415 | 1 | 0 | 120
38952.6436 | 1397 | 0 | 120
38952.6458 | 1768 | 0 | 120
38952.6479 | 1964 | 0 | 120
38952.65 | 1474 | 0 | 120
38952.6522 | 288 | 0 | 120
38952.6543 | 3 | 0 | 120
38952.6565 | 3 | 0 | 120
120
38952.6287 | 1 | 0 | 121
38952.6308 | 1 | 0 | 121
38952.633 | 1 | 0 | 121
38952.6351 | 1 | 0 | 121
38952.6372 | 1 | 0 | 121
38952.6394 | 1 | 0 | 121
38952.6415 | 1 | 1 | 121
38952.6436 | 3 | 0 | 121
38952.6458 | 4 | 0 | 121
38952.6479 | 3 | 0 | 121
38952.6501 | 3 | 0 | 121
38952.6522 | 3 | 0 | 121
38952.6543 | 2 | 0 | 121
38952.6565 | 2 | 0 | 121
121
38952.6287 | 1 | 0 | 122
38952.6308 | 1 | 0 | 122
38952.633 | 1 | 0 | 122
38952.6351 | 1 | 0 | 122
38952.6372 | 1 | 0 | 122
38952.6394 | 1 | 0 | 122
38952.6415 | 1 | 0 | 122
38952.6437 | 2 | 0 | 122
38952.6458 | 3 | 0 | 122
38952.6479 | 3 | 0 | 122
38952.6501 | 3 | 0 | 122
38952.6522 | 3 | 0 | 122
38952.6544 | 2 | 0 | 122
38952.6565 | 2 | 0 | 122
122
38952.6287 | 1 | 0 | 123
38952.6308 | 1 | 0 | 123
38952.633 | 1 | 0 | 123
38952.6351 | 1 | 0 | 123
38952.6373 | 1 | 0 | 123
38952.6394 | 1 | 0 | 123
38952.6415 | 1 | 0 | 123
38952.6437 | 2 | 0 | 123
38952.6458 | 3 | 0 | 123
38952.648 | 2 | 0 | 123
38952.6501 | 3 | 0 | 123
38952.6522 | 3 | 0 | 123
38952.6544 | 2 | 0 | 123
38952.6565 | 2 | 0 | 123
123
38952.6287 | 1 | 0 | 124
38952.6309 | 1 | 0 | 124
38952.633 | 1 | 0 | 124
38952.6351 | 1 | 0 | 124
38952.6373 | 1 | 0 | 124
38952.6394 | 1 | 0 | 124
38952.6416 | 1 | 0 | 124
38952.6437 | 1259 | 0 | 124
38952.6458 | 1848 | 0 | 124
38952.648 | 2470 | 0 | 124
38952.6501 | 2415 | 0 | 124
38952.6522 | 3 | 0 | 124
38952.6544 | 2 | 0 | 124
38952.6565 | 3 | 0 | 124
124
38952.6287 | 1 | 0 | 125
38952.6309 | 1 | 0 | 125
38952.633 | 1 | 0 | 125
38952.6352 | 1 | 0 | 125
38952.6373 | 1 | 0 | 125
38952.6394 | 1 | 0 | 125
38952.6416 | 1 | 0 | 125
38952.6437 | 2 | 0 | 125
38952.6458 | 3 | 0 | 125
38952.648 | 3 | 0 | 125
38952.6501 | 3 | 0 | 125
38952.6523 | 2 | 0 | 125
38952.6544 | 2 | 0 | 125
38952.6565 | 2 | 0 | 125
125
38952.6288 | 1 | 0 | 126
38952.6309 | 1 | 0 | 126
38952.633 | 1 | 0 | 126
38952.6352 | 1 | 0 | 126
38952.6373 | 1 | 0 | 126
38952.6394 | 1 | 0 | 126
38952.6416 | 1 | 0 | 126
38952.6437 | 1689 | 0 | 126
38952.6459 | 2173 | 0 | 126
38952.648 | 1711 | 0 | 126
38952.6501 | 768 | 0 | 126
38952.6523 | 15 | 0 | 126
38952.6544 | 158 | 0 | 126
38952.6566 | 3 | 0 | 126
126
38952.6288 | 1 | 0 | 127
38952.6309 | 1 | 0 | 127
38952.633 | 1 | 0 | 127
38952.6352 | 1 | 0 | 127
38952.6373 | 1 | 0 | 127
38952.6395 | 1 | 0 | 127
38952.6416 | 1 | 0 | 127
38952.6437 | 3 | 0 | 127
38952.6459 | 3 | 0 | 127
38952.648 | 3 | 0 | 127
38952.6502 | 3 | 0 | 127
38952.6523 | 2 | 0 | 127
38952.6544 | 2 | 0 | 127
38952.6566 | 2 | 0 | 127
127
38952.6288 | 1 | 0 | 128
38952.6309 | 1 | 0 | 128
38952.6331 | 1 | 0 | 128
38952.6352 | 1 | 0 | 128
38952.6373 | 1 | 0 | 128
38952.6395 | 1 | 0 | 128
38952.6416 | 1 | 0 | 128
38952.6438 | 1638 | 0 | 128
38952.6459 | 2143 | 0 | 128
38952.648 | 2026 | 0 | 128
38952.6502 | 2028 | 0 | 128
38952.6523 | 2 | 0 | 128
38952.6544 | 2 | 0 | 128
38952.6566 | 2 | 0 | 128
128
38952.6288 | 1 | 0 | 129
38952.6309 | 1 | 0 | 129
38952.6331 | 1 | 0 | 129
38952.6352 | 1 | 0 | 129
38952.6373 | 1 | 0 | 129
38952.6395 | 1 | 0 | 129
38952.6416 | 1 | 0 | 129
38952.6438 | 3 | 0 | 129
38952.6459 | 3 | 0 | 129
38952.648 | 3 | 0 | 129
38952.6502 | 3 | 0 | 129
38952.6523 | 2 | 0 | 129
38952.6545 | 2 | 0 | 129
38952.6566 | 2 | 0 | 129
129
38952.6288 | 1 | 0 | 130
38952.6309 | 1 | 0 | 130
38952.6331 | 1 | 0 | 130
38952.6352 | 1 | 0 | 130
38952.6374 | 1 | 0 | 130
38952.6395 | 1 | 0 | 130
38952.6416 | 1 | 0 | 130
38952.6438 | 2019 | 0 | 130
38952.6459 | 2086 | 0 | 130
38952.6481 | 1834 | 0 | 130
38952.6502 | 1627 | 0 | 130
38952.6523 | 3 | 0 | 130
38952.6545 | 2 | 0 | 130
38952.6566 | 34 | 0 | 130
130
38952.6288 | 1 | 0 | 131
38952.631 | 1 | 0 | 131
38952.6331 | 1 | 0 | 131
38952.6352 | 1 | 0 | 131
38952.6374 | 1 | 0 | 131
38952.6395 | 1 | 0 | 131
38952.6417 | 1085 | 1060 | 131
38952.6438 | 1782 | 492 | 131
38952.6459 | 2053 | 59 | 131
38952.6481 | 2328 | 0 | 131
38952.6502 | 2185 | 1 | 131
38952.6523 | 808 | 781 | 131
38952.6545 | 15 | 3 | 131
38952.6566 | 2008 | 0 | 131
131
38952.6288 | 1 | 0 | 132
38952.631 | 1 | 0 | 132
38952.6331 | 1 | 0 | 132
38952.6353 | 1 | 0 | 132
38952.6374 | 1 | 0 | 132
38952.6395 | 1 | 0 | 132
38952.6417 | 1119 | 1185 | 132
38952.6438 | 2227 | 399 | 132
38952.646 | 1971 | 30 | 132
38952.6481 | 1555 | 1 | 132
38952.6502 | 1321 | 506 | 132
38952.6524 | 10 | 8 | 132
38952.6545 | 2 | 0 | 132
38952.6566 | 3 | 0 | 132
132

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -162 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 26.9
1 | -161 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 26.9
2 | -160 | 19 | 25.8 | 22.8 | 25.8 | 27.6 | 23.8 | 23.7 | 27
3 | -159 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 26.9
4 | -158 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 26.9
5 | -157 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
6 | -156 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
7 | -155 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
8 | -154 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
9 | -153 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
10 | -152 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
11 | -151 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
12 | -150 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
13 | -149 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
14 | -148 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 27
15 | -147 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 26.9
16 | -146 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.7 | 26.9
17 | -145 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
18 | -144 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
19 | -143 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
20 | -142 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
21 | -141 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
22 | -140 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
23 | -139 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
24 | -138 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
25 | -137 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
26 | -136 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
27 | -135 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
28 | -134 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
29 | -133 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
30 | -132 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
31 | -131 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
32 | -130 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
33 | -129 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
34 | -128 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
35 | -127 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
36 | -126 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
37 | -125 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
38 | -124 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
39 | -123 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
40 | -122 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
41 | -121 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
42 | -120 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
43 | -119 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
44 | -118 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
45 | -117 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
46 | -116 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
47 | -115 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
48 | -114 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
49 | -113 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
50 | -112 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
51 | -111 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
52 | -110 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
53 | -109 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
54 | -108 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
55 | -107 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
56 | -106 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
57 | -105 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
58 | -104 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
59 | -103 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
60 | -102 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
61 | -101 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
62 | -100 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
63 | -99 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
64 | -98 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
65 | -97 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
66 | -96 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
67 | -95 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
68 | -94 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
69 | -93 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 26.9
70 | -92 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
71 | -91 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
72 | -90 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
73 | -89 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
74 | -88 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
75 | -87 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
76 | -86 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
77 | -85 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
78 | -84 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
79 | -83 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
80 | -82 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
81 | -81 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
82 | -80 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
83 | -79 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
84 | -78 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
85 | -77 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
86 | -76 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
87 | -75 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
88 | -74 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
89 | -73 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
90 | -72 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
91 | -71 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
92 | -70 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
93 | -69 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
94 | -68 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
95 | -67 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
96 | -66 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
97 | -65 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
98 | -64 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
99 | -63 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
100 | -62 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
101 | -61 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.2
102 | -60 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
103 | -59 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
104 | -58 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
105 | -57 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
106 | -56 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
107 | -55 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
108 | -54 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
109 | -53 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
110 | -52 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
111 | -51 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
112 | -50 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
113 | -49 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
114 | -48 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
115 | -47 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
116 | -46 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
117 | -45 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
118 | -44 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
119 | -43 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
120 | -42 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
121 | -41 | 19 | 25.7 | 22.9 | 25.8 | 27.3 | 23.8 | 23.8 | 27
122 | -40 | 19 | 25.8 | 22.9 | 25.8 | 27.3 | 23.8 | 23.8 | 27
123 | -39 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
124 | -38 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
125 | -37 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
126 | -36 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
127 | -35 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
128 | -34 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
129 | -33 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
130 | -32 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
131 | -31 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
132 | -30 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
133 | -29 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.2
134 | -28 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
135 | -27 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
136 | -26 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
137 | -25 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
138 | -24 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
139 | -23 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
140 | -22 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
141 | -21 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
142 | -20 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
143 | -19 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
144 | -18 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
145 | -17 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
146 | -16 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
147 | -15 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
148 | -14 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
149 | -13 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
150 | -12 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
151 | -11 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
152 | -10 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
153 | -9 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
154 | -8 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
155 | -7 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27.1
156 | -6 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
157 | -5 | 19 | 25.8 | 22.8 | 25.8 | 27.5 | 23.8 | 23.8 | 27
158 | -4 | 19 | 25.9 | 22.7 | 25.9 | 27.6 | 23.9 | 23.8 | 27
159 | -3 | 19 | 26.4 | 21.7 | 26.2 | 28.8 | 24 | 23.8 | 26.9
160 | -2 | 19 | 26.5 | 21.4 | 26.3 | 29.2 | 24 | 23.8 | 26.9
161 | -1 | 19.2 | 26.6 | 21.3 | 26.3 | 29.2 | 24 | 23.8 | 26.9
162 | 0 | 20 | 26.6 | 21.4 | 26.3 | 29.2 | 24 | 23.8 | 26.9
163 | 1 | 21.4 | 26.5 | 21.4 | 26.3 | 29.2 | 24 | 23.8 | 27
164 | 2 | 23.2 | 26.6 | 21.4 | 26.3 | 29.2 | 24 | 23.8 | 27
165 | 3 | 25.5 | 26.6 | 21.3 | 26.3 | 29.3 | 24 | 23.8 | 27
166 | 4 | 28.2 | 26.6 | 21.3 | 26.3 | 29.3 | 24 | 23.9 | 27
167 | 5 | 31.3 | 26.6 | 21.3 | 26.3 | 29.3 | 24.1 | 23.9 | 27
168 | 6 | 34.6 | 26.6 | 21.3 | 26.3 | 29.3 | 24.1 | 24 | 27.1
169 | 7 | 38.2 | 26.6 | 21.3 | 26.3 | 29.3 | 24.1 | 24 | 27.1
170 | 8 | 42 | 26.6 | 21.3 | 26.3 | 29.3 | 24.2 | 24.1 | 27.2
171 | 9 | 45.9 | 26.6 | 21.3 | 26.3 | 29.3 | 24.2 | 24.1 | 27.2
172 | 10 | 50.1 | 26.6 | 21.3 | 26.3 | 29.3 | 24.3 | 24.2 | 27.2
173 | 11 | 54.4 | 26.6 | 21.3 | 26.3 | 29.3 | 24.4 | 24.3 | 27.3
174 | 12 | 58.9 | 26.6 | 21.3 | 26.3 | 29.3 | 24.4 | 24.4 | 27.4
175 | 13 | 63.5 | 26.6 | 21.3 | 26.3 | 29.4 | 24.5 | 24.5 | 27.5
176 | 14 | 68.2 | 26.6 | 21.3 | 26.3 | 29.4 | 24.6 | 24.6 | 27.6
177 | 15 | 73.1 | 26.6 | 21.3 | 26.3 | 29.4 | 24.7 | 24.7 | 27.7
178 | 16 | 78.1 | 26.6 | 21.3 | 26.3 | 29.4 | 24.7 | 24.9 | 27.8
179 | 17 | 83.2 | 26.6 | 21.3 | 26.3 | 29.5 | 24.8 | 25 | 27.9
180 | 18 | 88.4 | 26.6 | 21.3 | 26.4 | 29.5 | 24.9 | 25.2 | 28
181 | 19 | 93.7 | 26.6 | 21.3 | 26.4 | 29.6 | 25.1 | 25.3 | 28.1
182 | 20 | 99.1 | 26.6 | 21.4 | 26.4 | 29.6 | 25.2 | 25.5 | 28.2
183 | 21 | 104.5 | 26.6 | 21.3 | 26.4 | 29.7 | 25.3 | 25.7 | 28.4
184 | 22 | 110 | 26.6 | 21.4 | 26.4 | 29.7 | 25.5 | 25.9 | 28.6
185 | 23 | 115.6 | 26.6 | 21.4 | 26.4 | 29.8 | 25.6 | 26 | 28.7
186 | 24 | 121.2 | 26.6 | 21.4 | 26.4 | 29.9 | 25.8 | 26.3 | 28.9
187 | 25 | 126.8 | 26.6 | 21.4 | 26.4 | 29.9 | 26 | 26.5 | 29.1
188 | 26 | 132.6 | 26.6 | 21.3 | 26.4 | 30 | 26.2 | 26.7 | 29.3
189 | 27 | 138.3 | 26.6 | 21.4 | 26.4 | 30.1 | 26.3 | 27 | 29.5
190 | 28 | 144.1 | 26.7 | 21.4 | 26.4 | 30.2 | 26.5 | 27.2 | 29.7
191 | 29 | 149.9 | 26.7 | 21.4 | 26.5 | 30.3 | 26.7 | 27.5 | 30
192 | 30 | 155.5 | 26.7 | 21.4 | 26.5 | 30.4 | 26.9 | 27.8 | 30.2
193 | 31 | 161 | 26.7 | 21.4 | 26.5 | 30.5 | 27.2 | 28.1 | 30.5
194 | 32 | 166.7 | 26.7 | 21.4 | 26.5 | 30.6 | 27.4 | 28.4 | 30.8
195 | 33 | 172.3 | 26.7 | 21.4 | 26.5 | 30.7 | 27.7 | 28.7 | 31.1
196 | 34 | 177.9 | 26.8 | 21.4 | 26.6 | 30.9 | 27.9 | 29 | 31.4
197 | 35 | 183.5 | 26.8 | 21.5 | 26.6 | 31 | 28.2 | 29.4 | 31.7
198 | 36 | 189.2 | 26.8 | 21.5 | 26.6 | 31.1 | 28.5 | 29.7 | 32.1
199 | 37 | 194.8 | 26.8 | 21.5 | 26.6 | 31.3 | 28.8 | 30.1 | 32.5
200 | 38 | 200.6 | 26.9 | 21.5 | 26.7 | 31.5 | 29.1 | 30.5 | 32.9
201 | 39 | 206.3 | 26.9 | 21.5 | 26.7 | 31.6 | 29.4 | 30.9 | 33.3
202 | 40 | 212 | 26.9 | 21.5 | 26.8 | 31.8 | 29.8 | 31.3 | 33.7
203 | 41 | 217.6 | 27 | 21.5 | 26.8 | 32 | 30.1 | 31.7 | 34.1
204 | 42 | 223.2 | 27 | 21.6 | 26.8 | 32.2 | 30.5 | 32.1 | 34.5
205 | 43 | 228.8 | 27 | 21.6 | 26.9 | 32.4 | 30.9 | 32.6 | 35
206 | 44 | 234.4 | 27.1 | 21.6 | 26.9 | 32.6 | 31.3 | 33.1 | 35.5
207 | 45 | 239.9 | 27.1 | 21.6 | 27 | 32.8 | 31.7 | 33.6 | 36
208 | 46 | 245.5 | 27.2 | 21.7 | 27.1 | 33.1 | 32.1 | 34.1 | 36.5
209 | 47 | 251.1 | 27.3 | 21.7 | 27.1 | 33.3 | 32.5 | 34.6 | 37.1
210 | 48 | 256.6 | 27.3 | 21.7 | 27.2 | 33.6 | 32.9 | 35.1 | 37.7
211 | 49 | 262.1 | 27.4 | 21.7 | 27.3 | 33.8 | 33.4 | 35.7 | 38.3
212 | 50 | 267.4 | 27.4 | 21.8 | 27.3 | 34.1 | 33.9 | 36.3 | 38.9
213 | 51 | 272.7 | 27.5 | 21.8 | 27.4 | 34.4 | 34.4 | 36.9 | 39.5
214 | 52 | 278.2 | 27.6 | 21.9 | 27.5 | 34.7 | 34.9 | 37.5 | 40.1
215 | 53 | 283.6 | 27.7 | 21.9 | 27.6 | 35 | 35.4 | 38.1 | 40.8
216 | 54 | 288.8 | 27.7 | 22 | 27.7 | 35.3 | 36 | 38.8 | 41.5
217 | 55 | 294.1 | 27.8 | 22 | 27.7 | 35.6 | 36.6 | 39.4 | 42.3
218 | 56 | 299.3 | 27.9 | 22.1 | 27.9 | 36 | 37.2 | 40.1 | 43
219 | 57 | 304.5 | 28 | 22.1 | 28 | 36.3 | 37.7 | 40.7 | 43.8
220 | 58 | 309.8 | 28.1 | 22.2 | 28.1 | 36.6 | 38.3 | 41.4 | 44.6
221 | 59 | 315.1 | 28.2 | 22.2 | 28.2 | 37 | 38.9 | 42.1 | 45.4
222 | 60 | 320.3 | 28.3 | 22.3 | 28.3 | 37.4 | 39.5 | 42.8 | 46.3
223 | 61 | 325.4 | 28.4 | 22.4 | 28.4 | 37.8 | 40.2 | 43.6 | 47.2
224 | 62 | 330.5 | 28.6 | 22.5 | 28.6 | 38.2 | 40.8 | 44.3 | 48.1
225 | 63 | 335.4 | 28.7 | 22.5 | 28.7 | 38.6 | 41.5 | 45.2 | 49.1
226 | 64 | 340.6 | 28.8 | 22.6 | 28.8 | 39.1 | 42.2 | 46 | 50
227 | 65 | 345.5 | 28.9 | 22.7 | 29 | 39.5 | 43 | 46.8 | 51
228 | 66 | 350.5 | 29.1 | 22.8 | 29.1 | 40 | 43.7 | 47.6 | 52.1
229 | 67 | 355.7 | 29.2 | 22.9 | 29.3 | 40.4 | 44.4 | 48.5 | 53.1
230 | 68 | 360.7 | 29.4 | 23 | 29.4 | 40.9 | 45.2 | 49.3 | 54.2
231 | 69 | 365.7 | 29.5 | 23.1 | 29.6 | 41.4 | 45.9 | 50.3 | 55.3
232 | 70 | 370.6 | 29.7 | 23.2 | 29.8 | 41.9 | 46.7 | 51.2 | 56.5
233 | 71 | 375.6 | 29.9 | 23.3 | 29.9 | 42.5 | 47.5 | 52.1 | 57.6
234 | 72 | 380.5 | 30 | 23.4 | 30.1 | 43 | 48.3 | 53.1 | 58.7
235 | 73 | 385.2 | 30.2 | 23.5 | 30.3 | 43.5 | 49.2 | 54 | 60
236 | 74 | 389.7 | 30.3 | 23.9 | 30.4 | 43.8 | 50 | 55 | 61.2
237 | 75 | 394.5 | 30.1 | 24.7 | 30.4 | 43.6 | 50.8 | 56 | 62.5
238 | 76 | 399.1 | 30.3 | 24.8 | 30.6 | 44.2 | 51.6 | 57 | 63.9
239 | 77 | 403.7 | 30.5 | 25 | 30.8 | 44.8 | 52.5 | 58 | 65.2
240 | 78 | 408.2 | 30.7 | 25.1 | 31 | 45.4 | 53.5 | 59.1 | 66.5
241 | 79 | 412.6 | 30.9 | 25.3 | 31.3 | 46.1 | 54.4 | 60.2 | 68
242 | 80 | 416.9 | 31.2 | 25.4 | 31.5 | 46.7 | 55.4 | 61.3 | 69.4
243 | 81 | 421.3 | 31.4 | 25.6 | 31.7 | 47.4 | 56.3 | 62.5 | 70.8
244 | 82 | 425.7 | 31.6 | 25.7 | 32 | 48.1 | 57.2 | 63.7 | 72.4
245 | 83 | 430.1 | 31.9 | 25.9 | 32.2 | 48.8 | 58.3 | 64.9 | 73.9
246 | 84 | 434.4 | 32.1 | 26.1 | 32.5 | 49.6 | 59.3 | 66.1 | 75.5
247 | 85 | 438.4 | 32.4 | 26.3 | 32.7 | 50.4 | 60.2 | 67.3 | 77.1
248 | 86 | 442.4 | 32.6 | 26.5 | 33 | 51.2 | 61.2 | 68.4 | 78.8
249 | 87 | 446.6 | 32.9 | 26.7 | 33.3 | 52 | 62.2 | 69.5 | 80.4
250 | 88 | 450.9 | 33.2 | 26.9 | 33.5 | 52.9 | 63.1 | 70.7 | 82.1
251 | 89 | 455.1 | 33.4 | 27.1 | 33.8 | 53.8 | 64.1 | 71.8 | 83.9
252 | 90 | 459.4 | 33.7 | 27.3 | 34.1 | 54.7 | 65.1 | 73 | 85.7
253 | 91 | 463.7 | 34 | 27.5 | 34.4 | 55.7 | 66.1 | 74.2 | 87.5
254 | 92 | 467.9 | 34.3 | 27.7 | 34.7 | 56.7 | 67.1 | 75.4 | 89.4
255 | 93 | 471.8 | 34.6 | 27.9 | 35.1 | 57.7 | 68.1 | 76.6 | 91.3
256 | 94 | 475.5 | 34.9 | 28.2 | 35.4 | 58.7 | 69.2 | 77.8 | 93.2
257 | 95 | 479.4 | 35.2 | 28.6 | 35.7 | 59.6 | 70.2 | 79.1 | 95.2
258 | 96 | 483 | 35.5 | 28.8 | 36 | 60.7 | 71.4 | 80.4 | 97.2
259 | 97 | 486.5 | 35.8 | 29 | 36.3 | 61.9 | 72.5 | 81.6 | 99.2
260 | 98 | 489.8 | 36.2 | 29.3 | 36.7 | 63 | 73.6 | 82.8 | 101.1
261 | 99 | 493 | 36.5 | 29.5 | 37 | 64.2 | 74.7 | 84.1 | 103.2
262 | 100 | 495.7 | 36.9 | 29.8 | 37.4 | 65.4 | 75.7 | 85.3 | 105.2
263 | 101 | 498.1 | 37.2 | 30.1 | 37.8 | 66.6 | 76.7 | 86.4 | 107.2
264 | 102 | 500.2 | 37.6 | 30.4 | 38.1 | 67.8 | 77.7 | 87.6 | 109.3
265 | 103 | 502.4 | 38 | 30.7 | 38.5 | 69 | 78.7 | 88.7 | 111.4
266 | 104 | 504.8 | 38.4 | 31 | 38.9 | 70.3 | 79.7 | 89.9 | 113.4
267 | 105 | 507.2 | 38.8 | 31.2 | 39.4 | 71.6 | 80.9 | 90.9 | 115.5
268 | 106 | 509.4 | 39.2 | 31.5 | 39.8 | 72.9 | 82 | 92 | 117.6
269 | 107 | 511.5 | 39.7 | 31.8 | 40.2 | 74.3 | 83 | 93.2 | 119.7
270 | 108 | 513.3 | 40.1 | 32.1 | 40.7 | 75.5 | 84.1 | 94.3 | 121.9
271 | 109 | 515.1 | 40.5 | 32.5 | 41.1 | 76.8 | 85.1 | 95.4 | 123.9
272 | 110 | 516.7 | 40.9 | 32.9 | 41.5 | 78.1 | 86.2 | 96.5 | 125.9
273 | 111 | 518.1 | 41.3 | 33.3 | 42 | 79.3 | 87.2 | 97.4 | 127.9
274 | 112 | 519.1 | 41.8 | 33.7 | 42.4 | 80.6 | 88.3 | 98.3 | 130.1
275 | 113 | 519.8 | 42.2 | 34.1 | 42.9 | 81.8 | 89.2 | 99.2 | 132.1
276 | 114 | 520.4 | 42.7 | 34.5 | 43.4 | 83.1 | 90.1 | 99.9 | 134.2
277 | 115 | 520.8 | 43.2 | 34.9 | 43.9 | 84.3 | 91.1 | 100.7 | 136.3
278 | 116 | 520.9 | 43.7 | 35.3 | 44.4 | 85.6 | 92.1 | 101.4 | 138.3
279 | 117 | 521.2 | 44.2 | 35.7 | 44.9 | 86.8 | 93 | 102.2 | 140.3
280 | 118 | 521.2 | 44.7 | 36.1 | 45.5 | 88.1 | 94 | 103 | 142.3
281 | 119 | 521.1 | 45.2 | 36.5 | 46 | 89.3 | 95 | 103.8 | 144.3
282 | 120 | 520.8 | 45.8 | 36.9 | 46.6 | 90.6 | 96 | 104.6 | 146.3
283 | 121 | 520.7 | 46.3 | 37.3 | 47.1 | 91.9 | 97 | 105.4 | 148.2
284 | 122 | 520.6 | 46.9 | 37.7 | 47.7 | 93.2 | 98 | 106.3 | 150.1
285 | 123 | 520.5 | 47.4 | 38.2 | 48.3 | 94.4 | 98.8 | 107 | 152
286 | 124 | 520.4 | 48 | 38.6 | 48.9 | 95.7 | 99.7 | 107.7 | 153.9
287 | 125 | 520.2 | 48.6 | 39.1 | 49.5 | 97 | 100.7 | 108.4 | 155.9
288 | 126 | 519.8 | 49.2 | 39.5 | 50.1 | 98.2 | 101.5 | 109.2 | 157.7
289 | 127 | 519.6 | 49.7 | 40 | 50.7 | 99.4 | 102.4 | 109.9 | 159.6
290 | 128 | 519.3 | 50.3 | 40.5 | 51.3 | 100.7 | 103.3 | 110.6 | 161.4
291 | 129 | 519 | 51 | 40.9 | 51.9 | 102 | 104.2 | 111.4 | 163.3
292 | 130 | 518.8 | 51.6 | 41.5 | 52.5 | 103.2 | 105.2 | 112.1 | 165.1
293 | 131 | 518.7 | 52.2 | 42 | 53.1 | 104.4 | 106.1 | 112.8 | 166.9
294 | 132 | 518.7 | 52.8 | 42.5 | 53.8 | 105.6 | 106.9 | 113.5 | 168.8
295 | 133 | 518.7 | 53.4 | 43 | 54.4 | 106.8 | 107.7 | 114.3 | 170.6
296 | 134 | 518.9 | 54.1 | 43.5 | 55.1 | 108 | 108.7 | 115 | 172.5
297 | 135 | 519.2 | 54.7 | 44.1 | 55.7 | 109.1 | 109.7 | 115.7 | 174.2
298 | 136 | 519.4 | 55.3 | 44.6 | 56.4 | 110.2 | 110.6 | 116.4 | 176
299 | 137 | 519.6 | 55.9 | 45.2 | 57 | 111.3 | 111.6 | 117.1 | 177.8
300 | 138 | 519.5 | 56.6 | 45.8 | 57.6 | 112.3 | 112.5 | 117.7 | 179.6
301 | 139 | 519.6 | 57.2 | 46.4 | 58.3 | 113.3 | 113.4 | 118.4 | 181.3
302 | 140 | 519.6 | 57.9 | 46.9 | 59 | 114.4 | 114.1 | 119.1 | 183.1
303 | 141 | 519.9 | 58.6 | 47.4 | 59.6 | 115.4 | 114.8 | 119.8 | 184.8
304 | 142 | 520 | 59.3 | 48 | 60.3 | 116.4 | 115.6 | 120.6 | 186.5
305 | 143 | 520.2 | 60 | 48.6 | 61 | 117.4 | 116.5 | 121.3 | 188.1
306 | 144 | 520.5 | 60.7 | 49.1 | 61.6 | 118.4 | 117.3 | 122 | 189.8
307 | 145 | 520.7 | 61.4 | 49.7 | 62.3 | 119.3 | 118 | 122.7 | 191.5
308 | 146 | 520.7 | 62.1 | 50.2 | 63 | 120.2 | 118.9 | 123.5 | 193.2
309 | 147 | 520.7 | 62.8 | 50.8 | 63.7 | 121.2 | 119.7 | 124.1 | 194.9
310 | 148 | 520.7 | 63.5 | 51.4 | 64.4 | 122.1 | 120.6 | 124.7 | 196.5
311 | 149 | 520.9 | 64.2 | 52 | 65 | 123 | 121.3 | 125.4 | 198.2
312 | 150 | 521.4 | 64.9 | 52.7 | 65.7 | 123.8 | 122.1 | 126.1 | 199.8
313 | 151 | 521.6 | 65.6 | 53.3 | 66.4 | 124.7 | 122.8 | 126.8 | 201.5
314 | 152 | 521.7 | 66.3 | 53.9 | 67.1 | 125.6 | 123.6 | 127.5 | 203.1
315 | 153 | 521.8 | 67 | 54.6 | 67.8 | 126.4 | 124.3 | 128.1 | 204.7
316 | 154 | 521.7 | 67.7 | 55.3 | 68.5 | 127.3 | 125.1 | 128.7 | 206.3
317 | 155 | 521.6 | 68.4 | 55.9 | 69.2 | 128.2 | 125.8 | 129.4 | 207.9
318 | 156 | 521.8 | 69.2 | 56.6 | 69.9 | 129.2 | 126.5 | 130 | 209.4
319 | 157 | 521.9 | 69.9 | 57.3 | 70.6 | 130.1 | 127.2 | 130.7 | 211
320 | 158 | 521.8 | 70.6 | 58 | 71.4 | 131 | 127.9 | 131.2 | 212.5
321 | 159 | 521.6 | 71.3 | 58.7 | 72.1 | 131.8 | 128.6 | 131.8 | 214.1
322 | 160 | 521.5 | 72 | 59.3 | 72.8 | 132.8 | 129.2 | 132.5 | 215.7
323 | 161 | 521.5 | 72.8 | 60 | 73.6 | 133.7 | 129.8 | 133.1 | 217.1
324 | 162 | 521.6 | 73.5 | 60.7 | 74.3 | 134.6 | 130.5 | 133.6 | 218.6
325 | 163 | 521.3 | 74.2 | 61.5 | 75 | 135.4 | 131.2 | 134.2 | 220.1
326 | 164 | 521.3 | 75 | 62.2 | 75.8 | 136.4 | 131.8 | 134.7 | 221.5
327 | 165 | 521.4 | 75.8 | 62.9 | 76.5 | 137.3 | 132.5 | 135.3 | 223
328 | 166 | 521.7 | 76.5 | 63.7 | 77.3 | 138.2 | 133.1 | 135.7 | 224.5
329 | 167 | 522 | 77.3 | 64.4 | 78 | 139.1 | 133.8 | 136.2 | 225.9
330 | 168 | 521.9 | 78 | 65.1 | 78.8 | 140 | 134.4 | 136.7 | 227.3
331 | 169 | 521.8 | 78.8 | 65.9 | 79.5 | 140.9 | 135 | 137.2 | 228.7
332 | 170 | 521.9 | 79.5 | 66.7 | 80.2 | 141.8 | 135.6 | 137.7 | 230.1
333 | 171 | 522.1 | 80.3 | 67.4 | 81 | 142.7 | 136.2 | 138.2 | 231.5
334 | 172 | 522.3 | 81.1 | 68.1 | 81.8 | 143.7 | 136.8 | 138.7 | 232.8
335 | 173 | 522.6 | 81.9 | 68.9 | 82.5 | 144.6 | 137.4 | 139.1 | 234.2
336 | 174 | 522.7 | 82.7 | 69.7 | 83.2 | 145.4 | 138.1 | 139.6 | 235.5
337 | 175 | 523 | 83.5 | 70.5 | 83.9 | 146.3 | 138.8 | 140.1 | 236.8
338 | 176 | 523 | 84.3 | 71.4 | 84.6 | 147.1 | 139.4 | 140.6 | 238.1
339 | 177 | 523 | 85.1 | 72.2 | 85.3 | 148 | 140.1 | 141.1 | 239.5
340 | 178 | 523.1 | 85.9 | 73 | 86 | 148.9 | 140.8 | 141.6 | 240.8
341 | 179 | 523.1 | 86.7 | 73.9 | 86.7 | 149.7 | 141.5 | 142 | 242.2
342 | 180 | 523.1 | 87.5 | 74.7 | 87.4 | 150.6 | 142.2 | 142.6 | 243.5
343 | 181 | 523.2 | 88.3 | 75.6 | 88.1 | 151.4 | 142.9 | 143.1 | 244.7
344 | 182 | 523 | 89.1 | 76.5 | 88.9 | 152.2 | 143.6 | 143.5 | 245.9
345 | 183 | 522.7 | 89.9 | 77.3 | 89.6 | 153.1 | 144.3 | 144 | 247.2
346 | 184 | 522.5 | 90.7 | 78.2 | 90.3 | 154 | 144.9 | 144.4 | 248.4
347 | 185 | 522.2 | 91.5 | 79 | 91.1 | 154.8 | 145.6 | 144.9 | 249.6
348 | 186 | 522 | 92.3 | 79.9 | 91.8 | 155.5 | 146.2 | 145.4 | 250.9
349 | 187 | 521.7 | 93.1 | 80.7 | 92.5 | 156.3 | 146.8 | 145.9 | 252.1
350 | 188 | 521.2 | 93.9 | 81.6 | 93.3 | 157 | 147.4 | 146.4 | 253.3
351 | 189 | 521 | 94.7 | 82.5 | 94 | 157.7 | 148 | 146.9 | 254.4
352 | 190 | 521.1 | 95.5 | 83.4 | 94.8 | 158.4 | 148.8 | 147.4 | 255.6
353 | 191 | 521.2 | 96.3 | 84.3 | 95.5 | 159.1 | 149.4 | 148 | 256.7
354 | 192 | 521 | 97.1 | 85.1 | 96.3 | 159.8 | 150.2 | 148.5 | 257.8
355 | 193 | 520.7 | 97.9 | 86 | 97 | 160.5 | 150.8 | 148.9 | 258.9
356 | 194 | 520.5 | 98.7 | 86.8 | 97.8 | 161.3 | 151.5 | 149.4 | 260
357 | 195 | 520.5 | 99.5 | 87.7 | 98.5 | 162 | 152.1 | 150 | 261.1
358 | 196 | 520.4 | 100.3 | 88.6 | 99.2 | 162.8 | 152.8 | 150.5 | 262.2
359 | 197 | 520.3 | 101.1 | 89.4 | 100 | 163.6 | 153.5 | 151 | 263.3
360 | 198 | 520.4 | 101.9 | 90.3 | 100.7 | 164.3 | 154.1 | 151.6 | 264.4
361 | 199 | 520.5 | 102.7 | 91.2 | 101.5 | 165 | 154.8 | 152.1 | 265.5
362 | 200 | 520.5 | 103.5 | 92 | 102.2 | 165.6 | 155.5 | 152.6 | 266.6
363 | 201 | 520.6 | 104.3 | 92.9 | 103 | 166.2 | 156.1 | 153.1 | 267.6
364 | 202 | 520.6 | 105.2 | 93.7 | 103.7 | 166.8 | 156.8 | 153.6 | 268.7
365 | 203 | 520.7 | 106 | 94.5 | 104.5 | 167.3 | 157.6 | 154.1 | 269.7
366 | 204 | 520.6 | 106.8 | 95.4 | 105.2 | 167.8 | 158.2 | 154.6 | 270.7
367 | 205 | 520.7 | 107.6 | 96.2 | 106 | 168.2 | 158.9 | 155.1 | 271.7
368 | 206 | 521 | 108.4 | 97.1 | 106.8 | 168.6 | 159.4 | 155.6 | 272.7
369 | 207 | 521.2 | 109.2 | 97.9 | 107.5 | 169.1 | 160 | 156.2 | 273.7
370 | 208 | 521.2 | 109.9 | 98.7 | 108.3 | 169.5 | 160.7 | 156.7 | 274.7
371 | 209 | 521.3 | 110.7 | 99.6 | 109 | 170 | 161.4 | 157.2 | 275.6
372 | 210 | 521.5 | 111.5 | 100.4 | 109.8 | 170.5 | 162.1 | 157.8 | 276.6
373 | 211 | 521.5 | 112.3 | 101.3 | 110.5 | 171 | 162.8 | 158.3 | 277.5
374 | 212 | 521.4 | 113.1 | 102.1 | 111.3 | 171.5 | 163.6 | 158.9 | 278.5
375 | 213 | 521.3 | 113.9 | 102.9 | 112 | 172 | 164.2 | 159.4 | 279.4
376 | 214 | 521 | 114.7 | 103.7 | 112.8 | 172.5 | 164.8 | 159.9 | 280.4
377 | 215 | 520.9 | 115.5 | 104.5 | 113.6 | 173 | 165.6 | 160.5 | 281.2
378 | 216 | 520.8 | 116.3 | 105.3 | 114.3 | 173.5 | 166.2 | 161.1 | 282.1
379 | 217 | 520.9 | 117.1 | 106.1 | 115.1 | 174 | 166.9 | 161.6 | 283
380 | 218 | 520.8 | 117.9 | 107 | 115.8 | 174.6 | 167.6 | 162.1 | 283.9
381 | 219 | 520.8 | 118.7 | 107.8 | 116.6 | 175.1 | 168.2 | 162.6 | 284.8
382 | 220 | 520.7 | 119.5 | 108.6 | 117.3 | 175.7 | 168.8 | 163.2 | 285.6
383 | 221 | 520.8 | 120.3 | 109.4 | 118.1 | 176.3 | 169.4 | 163.7 | 286.4
384 | 222 | 520.7 | 121 | 110.2 | 118.8 | 176.8 | 170.1 | 164.2 | 287.3
385 | 223 | 520.8 | 121.8 | 111 | 119.6 | 177.5 | 170.7 | 164.6 | 288.1
386 | 224 | 520.9 | 122.6 | 111.8 | 120.3 | 178.1 | 171.4 | 165.1 | 288.9
387 | 225 | 520.8 | 123.4 | 112.6 | 121 | 178.7 | 172.1 | 165.6 | 289.7
388 | 226 | 520.7 | 124.1 | 113.4 | 121.8 | 179.2 | 172.5 | 166 | 290.4
389 | 227 | 520.6 | 124.9 | 114.2 | 122.5 | 179.8 | 173.1 | 166.5 | 291.2
390 | 228 | 520.4 | 125.7 | 115 | 123.3 | 180.4 | 173.7 | 167.1 | 292
391 | 229 | 520.2 | 126.5 | 115.8 | 124 | 181 | 174.4 | 167.6 | 292.7
392 | 230 | 520.4 | 127.2 | 116.6 | 124.7 | 181.5 | 175.1 | 168.1 | 293.5
393 | 231 | 520.7 | 128 | 117.3 | 125.5 | 182.1 | 175.6 | 168.6 | 294.3
394 | 232 | 520.8 | 128.8 | 118.1 | 126.2 | 182.6 | 176.1 | 169.1 | 295.1
395 | 233 | 521 | 129.5 | 118.9 | 126.9 | 183.1 | 176.7 | 169.6 | 295.8
396 | 234 | 521.1 | 130.3 | 119.7 | 127.7 | 183.6 | 177.3 | 170.2 | 296.6
397 | 235 | 521.3 | 131.1 | 120.4 | 128.4 | 184.2 | 178 | 170.7 | 297.3
398 | 236 | 521.3 | 131.8 | 121.2 | 129.1 | 184.7 | 178.6 | 171.3 | 298.1
399 | 237 | 521.6 | 132.5 | 122 | 129.8 | 185.2 | 179.1 | 171.9 | 298.8
400 | 238 | 521.7 | 133.3 | 122.7 | 130.6 | 185.7 | 179.6 | 172.4 | 299.5
401 | 239 | 521.7 | 134 | 123.5 | 131.3 | 186.2 | 180.2 | 172.9 | 300.3
402 | 240 | 521.7 | 134.8 | 124.3 | 132 | 186.7 | 180.9 | 173.4 | 300.9
403 | 241 | 521.5 | 135.5 | 125 | 132.7 | 187.2 | 181.6 | 173.9 | 301.6
404 | 242 | 521.4 | 136.3 | 125.7 | 133.4 | 187.7 | 182.3 | 174.4 | 302.3
405 | 243 | 521.7 | 137 | 126.5 | 134.1 | 188.1 | 182.8 | 174.9 | 303
406 | 244 | 521.8 | 137.7 | 127.2 | 134.8 | 188.6 | 183.3 | 175.4 | 303.7
407 | 245 | 521.7 | 138.5 | 128 | 135.5 | 189.1 | 183.8 | 176 | 304.4
408 | 246 | 521.8 | 139.2 | 128.7 | 136.2 | 189.6 | 184.3 | 176.5 | 305
409 | 247 | 521.7 | 139.9 | 129.5 | 136.9 | 190 | 184.8 | 177 | 305.7
410 | 248 | 521.7 | 140.6 | 130.2 | 137.6 | 190.5 | 185.4 | 177.6 | 306.3
411 | 249 | 521.6 | 141.4 | 130.9 | 138.3 | 191 | 186.1 | 178.1 | 307
412 | 250 | 521.5 | 142.1 | 131.7 | 139 | 191.5 | 186.6 | 178.6 | 307.6
413 | 251 | 521.5 | 142.8 | 132.4 | 139.7 | 192.1 | 187.1 | 179 | 308.2
414 | 252 | 521.4 | 143.5 | 133.1 | 140.4 | 192.6 | 187.7 | 179.5 | 308.8
415 | 253 | 521.1 | 144.3 | 133.8 | 141.1 | 193.1 | 188.1 | 180 | 309.4
416 | 254 | 521 | 145 | 134.5 | 141.8 | 193.6 | 188.6 | 180.5 | 310
417 | 255 | 520.9 | 145.7 | 135.2 | 142.5 | 194.1 | 189.1 | 181 | 310.6
418 | 256 | 520.8 | 146.4 | 135.9 | 143.1 | 194.6 | 189.6 | 181.4 | 311.2
419 | 257 | 520.7 | 147.1 | 136.6 | 143.8 | 195.1 | 190 | 181.9 | 311.9
420 | 258 | 520.6 | 147.8 | 137.3 | 144.5 | 195.6 | 190.5 | 182.4 | 312.5
421 | 259 | 520.3 | 148.6 | 138.1 | 145.2 | 196.1 | 190.9 | 182.8 | 313
422 | 260 | 520.2 | 149.3 | 138.8 | 145.8 | 196.6 | 191.4 | 183.3 | 313.6
423 | 261 | 520.1 | 150 | 139.4 | 146.5 | 197.1 | 191.9 | 183.7 | 314.2
424 | 262 | 520.1 | 150.7 | 140.2 | 147.2 | 197.5 | 192.4 | 184.1 | 314.7
425 | 263 | 520.1 | 151.4 | 140.9 | 147.8 | 198 | 192.8 | 184.6 | 315.3
426 | 264 | 520.1 | 152.1 | 141.6 | 148.5 | 198.3 | 193.3 | 185 | 315.9
427 | 265 | 520.4 | 152.8 | 142.3 | 149.1 | 198.5 | 193.8 | 185.5 | 316.5
428 | 266 | 520.4 | 153.6 | 143 | 149.8 | 198.8 | 194.2 | 186 | 317
429 | 267 | 520.4 | 154.3 | 143.7 | 150.4 | 199.1 | 194.6 | 186.5 | 317.5
430 | 268 | 520.4 | 155 | 144.4 | 151.1 | 199.4 | 195.1 | 186.9 | 318
431 | 269 | 520.2 | 155.7 | 145 | 151.7 | 199.7 | 195.6 | 187.3 | 318.6
432 | 270 | 520.1 | 156.4 | 145.7 | 152.4 | 200.1 | 196 | 187.7 | 319
433 | 271 | 519.9 | 157.1 | 146.5 | 153 | 200.4 | 196.5 | 188.1 | 319.6
434 | 272 | 519.8 | 157.8 | 147.2 | 153.7 | 200.8 | 197 | 188.6 | 320.1
435 | 273 | 519.8 | 158.5 | 147.9 | 154.3 | 201.1 | 197.5 | 189 | 320.6
436 | 274 | 520.1 | 159.3 | 148.6 | 154.9 | 201.2 | 198 | 189.5 | 321.1
437 | 275 | 520.4 | 160 | 149.3 | 155.6 | 201.1 | 198.5 | 190 | 321.6
438 | 276 | 520.7 | 160.7 | 150 | 156.2 | 200.9 | 199 | 190.4 | 322.1
439 | 277 | 520.7 | 161.4 | 150.6 | 156.8 | 200.7 | 199.6 | 190.8 | 322.6
440 | 278 | 520.6 | 162.2 | 151.3 | 157.5 | 200.4 | 200.1 | 191.1 | 323.1
441 | 279 | 520.5 | 162.9 | 152 | 158.1 | 200.1 | 200.5 | 191.4 | 323.6
442 | 280 | 520.6 | 163.6 | 152.7 | 158.7 | 199.7 | 201 | 191.8 | 324.1
443 | 281 | 520.4 | 164.3 | 153.4 | 159.3 | 199.3 | 201.5 | 192.2 | 324.5
444 | 282 | 520.3 | 165 | 154.1 | 159.9 | 198.9 | 202 | 192.6 | 325
445 | 283 | 520.2 | 165.8 | 154.8 | 160.6 | 198.6 | 202.5 | 192.9 | 325.5
446 | 284 | 520.2 | 166.5 | 155.5 | 161.2 | 198.2 | 203.1 | 193.3 | 325.9
447 | 285 | 520.4 | 167.2 | 156.1 | 161.8 | 197.9 | 203.7 | 193.7 | 326.4
448 | 286 | 520.5 | 168 | 156.8 | 162.4 | 197.7 | 204.2 | 194.2 | 326.8
449 | 287 | 520.4 | 168.7 | 157.5 | 163 | 197.7 | 204.7 | 194.6 | 327.3
450 | 288 | 520.4 | 169.4 | 158.1 | 163.6 | 197.8 | 205.3 | 195 | 327.7
451 | 289 | 520.7 | 170.1 | 158.8 | 164.1 | 198 | 205.8 | 195.4 | 328.2
452 | 290 | 520.7 | 170.9 | 159.4 | 164.7 | 198.3 | 206.3 | 195.7 | 328.6
453 | 291 | 520.5 | 171.6 | 160 | 165.3 | 198.6 | 206.8 | 196.1 | 329
454 | 292 | 520.6 | 172.4 | 160.5 | 165.8 | 198.9 | 207.3 | 196.5 | 329.4
455 | 293 | 520.7 | 173.1 | 161 | 166.4 | 199.3 | 207.8 | 196.9 | 329.9
456 | 294 | 520.8 | 173.9 | 161.6 | 166.9 | 199.7 | 208.3 | 197.3 | 330.2
457 | 295 | 520.9 | 174.6 | 162.2 | 167.5 | 200.1 | 208.8 | 197.7 | 330.7
458 | 296 | 520.9 | 175.3 | 162.7 | 168.1 | 200.5 | 209.3 | 198.1 | 331.1
459 | 297 | 521 | 176.1 | 163.3 | 168.6 | 200.9 | 209.8 | 198.5 | 331.5
460 | 298 | 521 | 176.8 | 163.9 | 169.2 | 201.4 | 210.4 | 198.9 | 331.9
461 | 299 | 521 | 177.5 | 164.4 | 169.8 | 201.8 | 210.9 | 199.3 | 332.3
462 | 300 | 521 | 178.3 | 165.1 | 170.3 | 202.2 | 211.4 | 199.7 | 332.7
463 | 301 | 521 | 179 | 165.7 | 170.9 | 202.7 | 211.9 | 200.1 | 333.1
464 | 302 | 521.1 | 179.7 | 166.3 | 171.4 | 203.2 | 212.4 | 200.5 | 333.5
465 | 303 | 521.1 | 180.4 | 166.9 | 172 | 203.6 | 213 | 200.9 | 333.8
466 | 304 | 521.2 | 181.2 | 167.5 | 172.5 | 204.1 | 213.5 | 201.3 | 334.2
467 | 305 | 521.2 | 181.9 | 168.1 | 173.1 | 204.6 | 214 | 201.7 | 334.6
468 | 306 | 521.1 | 182.7 | 168.7 | 173.6 | 205.1 | 214.5 | 202 | 335
469 | 307 | 521 | 183.4 | 169.4 | 174.2 | 205.6 | 215 | 202.4 | 335.4
470 | 308 | 521.1 | 184.2 | 170 | 174.7 | 206.1 | 215.5 | 202.7 | 335.8
471 | 309 | 521.1 | 184.9 | 170.6 | 175.3 | 206.5 | 215.9 | 203.1 | 336.1
472 | 310 | 521.1 | 185.7 | 171.3 | 175.9 | 207 | 216.4 | 203.4 | 336.5
473 | 311 | 520.9 | 186.4 | 171.9 | 176.4 | 207.5 | 216.8 | 203.7 | 336.9
474 | 312 | 521 | 187.1 | 172.6 | 177 | 208 | 217.3 | 204.1 | 337.2
475 | 313 | 521 | 187.9 | 173.2 | 177.6 | 208.4 | 217.7 | 204.4 | 337.7
476 | 314 | 521 | 188.6 | 173.9 | 178.1 | 208.9 | 218.2 | 204.7 | 338
477 | 315 | 521.1 | 189.3 | 174.5 | 178.7 | 209.4 | 218.7 | 205 | 338.4
478 | 316 | 521.2 | 190 | 175.2 | 179.3 | 209.9 | 219.2 | 205.4 | 338.7
479 | 317 | 521.3 | 190.7 | 175.8 | 179.9 | 210.4 | 219.8 | 205.7 | 339.1
480 | 318 | 521.5 | 191.4 | 176.5 | 180.4 | 210.9 | 220.3 | 206 | 339.4
481 | 319 | 521.7 | 192.2 | 177.2 | 181 | 211.4 | 220.8 | 206.4 | 339.8
482 | 320 | 521.6 | 192.8 | 177.8 | 181.5 | 211.9 | 221.3 | 206.7 | 340.1
483 | 321 | 521.6 | 193.5 | 178.5 | 182.1 | 212.4 | 221.8 | 207.1 | 340.5
484 | 322 | 521.7 | 194.2 | 179.2 | 182.6 | 212.9 | 222.2 | 207.5 | 340.8
485 | 323 | 521.9 | 194.9 | 179.9 | 183.2 | 213.4 | 222.7 | 207.8 | 341.2
486 | 324 | 521.7 | 195.6 | 180.6 | 183.8 | 213.8 | 223.2 | 208.1 | 341.5
487 | 325 | 521.7 | 196.3 | 181.2 | 184.3 | 214.4 | 223.6 | 208.5 | 341.9
488 | 326 | 521.8 | 197 | 181.9 | 184.9 | 214.9 | 224 | 208.8 | 342.2
489 | 327 | 521.8 | 197.7 | 182.6 | 185.4 | 215.4 | 224.5 | 209.2 | 342.6
490 | 328 | 521.9 | 198.4 | 183.3 | 186 | 215.9 | 224.9 | 209.6 | 342.9
491 | 329 | 522.2 | 199.1 | 183.9 | 186.5 | 216.5 | 225.3 | 209.9 | 343.2
492 | 330 | 522.4 | 199.7 | 184.6 | 187.1 | 217 | 225.8 | 210.2 | 343.5
493 | 331 | 522.2 | 200.4 | 185.3 | 187.7 | 217.5 | 226.2 | 210.6 | 343.8
494 | 332 | 522 | 201.1 | 186 | 188.2 | 218.1 | 226.7 | 210.9 | 344.1
495 | 333 | 521.9 | 201.8 | 186.6 | 188.7 | 218.6 | 227.1 | 211.1 | 344.5
496 | 334 | 521.7 | 202.4 | 187.3 | 189.3 | 219.2 | 227.6 | 211.4 | 344.8
497 | 335 | 521.5 | 203.1 | 188 | 189.8 | 219.7 | 227.9 | 211.7 | 345.1
498 | 336 | 521.3 | 203.7 | 188.7 | 190.4 | 220.3 | 228.3 | 212 | 345.4
499 | 337 | 521.3 | 204.4 | 189.4 | 190.9 | 220.8 | 228.7 | 212.4 | 345.7
500 | 338 | 521.3 | 205 | 190 | 191.5 | 221.4 | 229.1 | 212.7 | 346
501 | 339 | 521.1 | 205.7 | 190.7 | 192 | 222 | 229.5 | 213 | 346.3
502 | 340 | 521.1 | 206.3 | 191.4 | 192.6 | 222.6 | 230 | 213.4 | 346.6
503 | 341 | 520.9 | 207 | 192 | 193.1 | 223.1 | 230.4 | 213.7 | 346.9
504 | 342 | 520.8 | 207.6 | 192.7 | 193.7 | 223.7 | 230.8 | 214 | 347.2
505 | 343 | 520.7 | 208.3 | 193.3 | 194.2 | 224.3 | 231.2 | 214.3 | 347.4
506 | 344 | 520.8 | 208.9 | 194 | 194.8 | 224.9 | 231.7 | 214.6 | 347.7
507 | 345 | 520.8 | 209.6 | 194.6 | 195.3 | 225.5 | 232.1 | 214.9 | 348
508 | 346 | 520.6 | 210.2 | 195.3 | 195.9 | 226.1 | 232.5 | 215.2 | 348.3
509 | 347 | 520.5 | 210.8 | 196 | 196.5 | 226.7 | 232.9 | 215.5 | 348.6
510 | 348 | 520.4 | 211.5 | 196.6 | 197 | 227.3 | 233.3 | 215.8 | 348.9
511 | 349 | 520.4 | 212.1 | 197.3 | 197.6 | 227.9 | 233.7 | 216.2 | 349.1
512 | 350 | 520.3 | 212.7 | 197.9 | 198.1 | 228.5 | 234.1 | 216.5 | 349.4
513 | 351 | 520.5 | 213.4 | 198.6 | 198.7 | 229.1 | 234.5 | 216.8 | 349.7
514 | 352 | 520.3 | 214 | 199.2 | 199.2 | 229.7 | 234.9 | 217.2 | 350
515 | 353 | 520.4 | 214.6 | 199.8 | 199.8 | 230.4 | 235.3 | 217.5 | 350.2
516 | 354 | 520.5 | 215.3 | 200.5 | 200.3 | 231 | 235.6 | 217.7 | 350.4
517 | 355 | 520.6 | 215.9 | 201.1 | 200.9 | 231.6 | 236 | 217.9 | 350.7
518 | 356 | 520.6 | 216.5 | 201.7 | 201.4 | 232.2 | 236.4 | 218.2 | 351
519 | 357 | 520.6 | 217.2 | 202.4 | 202 | 232.8 | 236.7 | 218.5 | 351.3
520 | 358 | 520.6 | 217.8 | 203 | 202.5 | 233.4 | 237 | 218.8 | 351.6
521 | 359 | 520.6 | 218.4 | 203.6 | 203.1 | 234 | 237.3 | 219.1 | 351.8
522 | 360 | 520.6 | 219 | 204.3 | 203.7 | 234.6 | 237.7 | 219.5 | 352
523 | 361 | 520.7 | 219.6 | 204.9 | 204.2 | 235.2 | 238.1 | 219.8 | 352.3
524 | 362 | 520.8 | 220.2 | 205.5 | 204.8 | 235.8 | 238.4 | 220.1 | 352.6
525 | 363 | 520.7 | 220.8 | 206.1 | 205.3 | 236.4 | 238.7 | 220.4 | 352.9
526 | 364 | 520.8 | 221.4 | 206.7 | 205.9 | 237 | 239.1 | 220.7 | 353.1
527 | 365 | 521.2 | 222 | 207.4 | 206.5 | 237.6 | 239.5 | 220.9 | 353.4
528 | 366 | 521.3 | 222.6 | 208 | 207.1 | 238.2 | 239.8 | 221.1 | 353.6
529 | 367 | 521.4 | 223.2 | 208.6 | 207.6 | 238.8 | 240.2 | 221.4 | 353.8
530 | 368 | 521.4 | 223.8 | 209.2 | 208.2 | 239.4 | 240.5 | 221.6 | 354.1
531 | 369 | 521.4 | 224.4 | 209.9 | 208.8 | 240 | 240.8 | 221.9 | 354.3
532 | 370 | 521.1 | 225 | 210.5 | 209.3 | 240.6 | 241.1 | 222.2 | 354.6
533 | 371 | 521.1 | 225.5 | 211.1 | 209.9 | 241.3 | 241.5 | 222.4 | 354.8
534 | 372 | 521 | 226.1 | 211.7 | 210.5 | 241.9 | 241.8 | 222.7 | 355.1
535 | 373 | 521 | 226.7 | 212.3 | 211 | 242.5 | 242.1 | 222.9 | 355.3
536 | 374 | 521.2 | 227.3 | 212.9 | 211.6 | 243.1 | 242.4 | 223.1 | 355.6
537 | 375 | 521.1 | 227.8 | 213.5 | 212.1 | 243.6 | 242.7 | 223.4 | 355.8
538 | 376 | 521.2 | 228.4 | 214.1 | 212.7 | 244.2 | 243 | 223.6 | 356
539 | 377 | 521.2 | 229 | 214.7 | 213.3 | 244.8 | 243.3 | 223.8 | 356.2
540 | 378 | 521 | 229.5 | 215.3 | 213.8 | 245.4 | 243.6 | 224.1 | 356.4
541 | 379 | 521 | 230.1 | 215.9 | 214.4 | 246 | 243.9 | 224.4 | 356.6
542 | 380 | 521 | 230.7 | 216.4 | 215 | 246.6 | 244.2 | 224.8 | 356.8
543 | 381 | 521.1 | 231.2 | 217 | 215.6 | 247.2 | 244.5 | 225.1 | 357.1
544 | 382 | 521.1 | 231.8 | 217.5 | 216.1 | 247.8 | 244.8 | 225.4 | 357.3
545 | 383 | 521.1 | 232.3 | 218.1 | 216.7 | 248.4 | 245 | 225.8 | 357.5
546 | 384 | 521.1 | 232.8 | 218.7 | 217.3 | 249 | 245.4 | 226.2 | 357.8
547 | 385 | 521.1 | 233.4 | 219.3 | 217.8 | 249.6 | 245.7 | 226.6 | 358
548 | 386 | 521.2 | 233.9 | 219.9 | 218.4 | 250.1 | 245.9 | 227 | 358.2
549 | 387 | 521.3 | 234.4 | 220.4 | 218.9 | 250.7 | 246.2 | 227.3 | 358.4
550 | 388 | 521.4 | 234.9 | 221 | 219.5 | 251.3 | 246.6 | 227.7 | 358.6
551 | 389 | 521.6 | 235.4 | 221.6 | 220 | 251.9 | 246.9 | 228 | 358.8
552 | 390 | 521.7 | 236 | 222.1 | 220.6 | 252.4 | 247.3 | 228.4 | 359
553 | 391 | 521.9 | 236.5 | 222.7 | 221.1 | 253 | 247.6 | 228.7 | 359.2
554 | 392 | 522 | 237 | 223.3 | 221.7 | 253.5 | 247.9 | 229.1 | 359.4
555 | 393 | 522.1 | 237.5 | 223.9 | 222.2 | 254 | 248.2 | 229.5 | 359.7
556 | 394 | 522 | 238 | 224.5 | 222.8 | 254.5 | 248.5 | 229.8 | 359.9
557 | 395 | 522.1 | 238.5 | 225.1 | 223.3 | 255.1 | 248.9 | 230.1 | 360.1
558 | 396 | 522.1 | 239 | 225.6 | 223.8 | 255.6 | 249.2 | 230.5 | 360.3
559 | 397 | 522.1 | 239.5 | 226.2 | 224.4 | 256.1 | 249.5 | 230.8 | 360.5
560 | 398 | 522.1 | 240 | 226.8 | 224.9 | 256.7 | 249.9 | 231 | 360.6
561 | 399 | 522 | 240.6 | 227.3 | 225.4 | 257.2 | 250.2 | 231.3 | 360.8
562 | 400 | 521.9 | 241.1 | 227.9 | 226 | 257.7 | 250.5 | 231.6 | 361
563 | 401 | 521.8 | 241.6 | 228.4 | 226.5 | 258.2 | 250.9 | 231.9 | 361.2
564 | 402 | 521.9 | 242.1 | 229 | 227.1 | 258.7 | 251.2 | 232.2 | 361.4
565 | 403 | 521.7 | 242.6 | 229.5 | 227.6 | 259.2 | 251.6 | 232.5 | 361.5
566 | 404 | 521.6 | 243.1 | 230.1 | 228.1 | 259.7 | 251.9 | 232.8 | 361.8
567 | 405 | 521.5 | 243.6 | 230.6 | 228.6 | 260.3 | 252.2 | 233.1 | 362
568 | 406 | 521.5 | 244.1 | 231.2 | 229.1 | 260.8 | 252.5 | 233.4 | 362.1
569 | 407 | 521.6 | 244.6 | 231.7 | 229.7 | 261.3 | 252.7 | 233.7 | 362.3
570 | 408 | 521.8 | 245.1 | 232.3 | 230.2 | 261.8 | 253 | 234 | 362.5
571 | 409 | 521.9 | 245.6 | 232.8 | 230.7 | 262.3 | 253.3 | 234.3 | 362.7
572 | 410 | 521.8 | 246.1 | 233.3 | 231.2 | 262.8 | 253.5 | 234.7 | 362.9
573 | 411 | 521.6 | 246.6 | 233.9 | 231.7 | 263.4 | 253.8 | 235 | 363
574 | 412 | 521.2 | 247.1 | 234.4 | 232.2 | 263.8 | 254.1 | 235.2 | 363.2
575 | 413 | 521.1 | 247.6 | 235 | 232.7 | 264.3 | 254.4 | 235.5 | 363.3
576 | 414 | 521 | 248.1 | 235.5 | 233.1 | 264.8 | 254.7 | 235.8 | 363.4
577 | 415 | 520.8 | 248.6 | 236.1 | 233.6 | 265.3 | 254.9 | 236.1 | 363.6
578 | 416 | 520.5 | 249.1 | 236.6 | 234.1 | 265.8 | 255.2 | 236.3 | 363.7
579 | 417 | 520.5 | 249.6 | 237.1 | 234.5 | 266.2 | 255.4 | 236.6 | 363.9
580 | 418 | 520.4 | 250.1 | 237.7 | 235 | 266.7 | 255.6 | 236.9 | 364
581 | 419 | 520.3 | 250.6 | 238.2 | 235.4 | 267.2 | 255.9 | 237.2 | 364.2
582 | 420 | 520.2 | 251 | 238.7 | 235.9 | 267.6 | 256.1 | 237.4 | 364.4
583 | 421 | 520.3 | 251.5 | 239.3 | 236.4 | 268.1 | 256.4 | 237.7 | 364.6
584 | 422 | 520.3 | 252 | 239.8 | 236.8 | 268.5 | 256.6 | 238 | 364.7
585 | 423 | 520.3 | 252.5 | 240.3 | 237.3 | 269 | 256.9 | 238.3 | 364.9
586 | 424 | 520.2 | 253 | 240.8 | 237.8 | 269.4 | 257.2 | 238.5 | 365
587 | 425 | 520.2 | 253.4 | 241.3 | 238.3 | 269.9 | 257.4 | 238.8 | 365.1
588 | 426 | 520.2 | 253.9 | 241.9 | 238.9 | 270.3 | 257.7 | 239.1 | 365.3
589 | 427 | 520.3 | 254.4 | 242.4 | 239.6 | 270.7 | 258 | 239.4 | 365.5
590 | 428 | 520.5 | 254.9 | 242.9 | 240.1 | 271.2 | 258.2 | 239.6 | 365.7
591 | 429 | 520.7 | 255.4 | 243.5 | 240.6 | 271.6 | 258.5 | 240 | 365.9
592 | 430 | 520.7 | 255.8 | 244 | 241.1 | 272 | 258.8 | 240.2 | 366.1
593 | 431 | 520.9 | 256.3 | 244.5 | 241.6 | 272.4 | 259 | 240.5 | 366.3
594 | 432 | 521 | 256.7 | 245 | 242.1 | 272.9 | 259.3 | 240.7 | 366.4
595 | 433 | 521 | 257.2 | 245.6 | 242.6 | 273.3 | 259.5 | 240.9 | 366.6
596 | 434 | 521.1 | 257.7 | 246.1 | 243.1 | 273.8 | 259.7 | 241.2 | 366.8
597 | 435 | 521.2 | 258.1 | 246.6 | 243.6 | 274.2 | 260 | 241.5 | 366.9
598 | 436 | 521.2 | 258.6 | 247.1 | 244 | 274.6 | 260.2 | 241.7 | 367.1
599 | 437 | 521.2 | 259 | 247.6 | 244.5 | 275.1 | 260.5 | 242 | 367.3
600 | 438 | 521.2 | 259.5 | 248.1 | 245 | 275.5 | 260.8 | 242.2 | 367.5
601 | 439 | 521.1 | 259.9 | 248.5 | 245.4 | 275.9 | 261 | 242.5 | 367.7
602 | 440 | 521.3 | 260.4 | 248.9 | 245.9 | 276.4 | 261.3 | 242.8 | 367.8
603 | 441 | 521.4 | 260.8 | 249.3 | 246.3 | 276.8 | 261.6 | 243 | 368
604 | 442 | 521.6 | 261.3 | 249.7 | 246.8 | 277.2 | 261.8 | 243.3 | 368.2
605 | 443 | 522 | 261.7 | 250.2 | 247.2 | 277.7 | 262.1 | 243.5 | 368.4
606 | 444 | 522.2 | 262.1 | 250.6 | 247.7 | 278.1 | 262.4 | 243.7 | 368.6
607 | 445 | 522.4 | 262.6 | 251 | 248.1 | 278.5 | 262.7 | 243.9 | 368.7
608 | 446 | 522.7 | 263 | 251.5 | 248.5 | 278.9 | 262.9 | 244.2 | 368.9
609 | 447 | 522.6 | 263.4 | 251.9 | 249 | 279.3 | 263.2 | 244.4 | 369.1
610 | 448 | 522.8 | 263.8 | 252.4 | 249.4 | 279.7 | 263.5 | 244.6 | 369.3
611 | 449 | 523.1 | 264.2 | 252.8 | 249.9 | 280.1 | 263.7 | 244.9 | 369.4
612 | 450 | 523.2 | 264.7 | 253.3 | 250.3 | 280.6 | 264 | 245.2 | 369.6
613 | 451 | 523.1 | 265 | 253.7 | 250.7 | 280.9 | 264.2 | 245.5 | 369.8
614 | 452 | 522.9 | 265.4 | 254.2 | 251.2 | 281.3 | 264.5 | 245.7 | 370
615 | 453 | 522.9 | 265.8 | 254.7 | 251.6 | 281.7 | 264.7 | 246 | 370.1
616 | 454 | 522.8 | 266.2 | 255.1 | 252 | 282.1 | 265 | 246.3 | 370.3
617 | 455 | 522.6 | 266.6 | 255.5 | 252.5 | 282.4 | 265.2 | 246.7 | 370.5
618 | 456 | 522.5 | 267 | 256 | 252.9 | 282.8 | 265.5 | 247 | 370.6
619 | 457 | 522.4 | 267.3 | 256.4 | 253.3 | 283.2 | 265.7 | 247.3 | 370.8
620 | 458 | 522.4 | 267.7 | 256.8 | 253.7 | 283.5 | 265.9 | 247.6 | 371
621 | 459 | 522.5 | 268 | 257.3 | 254.1 | 283.9 | 266.2 | 247.9 | 371.1
622 | 460 | 522.2 | 268.4 | 257.7 | 254.6 | 284.2 | 266.4 | 248.1 | 371.3
623 | 461 | 522.1 | 268.7 | 258.2 | 255 | 284.6 | 266.6 | 248.4 | 371.5
624 | 462 | 521.8 | 269.1 | 258.6 | 255.4 | 284.9 | 266.9 | 248.6 | 371.7
625 | 463 | 521.6 | 269.4 | 259 | 255.8 | 285.3 | 267.1 | 248.9 | 371.8
626 | 464 | 521.5 | 269.8 | 259.4 | 256.2 | 285.7 | 267.3 | 249.1 | 372
627 | 465 | 521.3 | 270.1 | 259.9 | 256.7 | 286.1 | 267.6 | 249.4 | 372.1
628 | 466 | 521.1 | 270.5 | 260.3 | 257.1 | 286.5 | 267.8 | 249.7 | 372.2
629 | 467 | 521.1 | 270.8 | 260.8 | 257.5 | 286.8 | 268.1 | 249.9 | 372.3
630 | 468 | 520.9 | 271.2 | 261.2 | 257.9 | 287.1 | 268.3 | 250.1 | 372.5
631 | 469 | 520.8 | 271.5 | 261.6 | 258.4 | 287.4 | 268.6 | 250.3 | 372.6
632 | 470 | 520.6 | 271.8 | 262 | 258.8 | 287.6 | 268.8 | 250.5 | 372.7
633 | 471 | 520.6 | 272.2 | 262.4 | 259.2 | 288 | 269 | 250.8 | 372.9
634 | 472 | 520.6 | 272.5 | 262.8 | 259.6 | 288.3 | 269.3 | 251 | 373
635 | 473 | 520.7 | 272.8 | 263.3 | 260 | 288.6 | 269.5 | 251.3 | 373.2
636 | 474 | 520.7 | 273.2 | 263.7 | 260.4 | 289 | 269.7 | 251.5 | 373.4
637 | 475 | 520.6 | 273.4 | 264.1 | 260.9 | 289.3 | 269.9 | 251.7 | 373.6
638 | 476 | 520.6 | 273.7 | 264.5 | 261.4 | 289.7 | 270.2 | 251.9 | 373.7
639 | 477 | 520.6 | 274 | 264.9 | 261.9 | 290.1 | 270.4 | 252.1 | 373.8
640 | 478 | 520.5 | 274.2 | 265.4 | 262.4 | 290.4 | 270.6 | 252.3 | 373.9
641 | 479 | 520.5 | 274.5 | 265.8 | 262.8 | 290.8 | 270.9 | 252.5 | 374.1
642 | 480 | 520.6 | 274.8 | 266.2 | 263.3 | 291.1 | 271.1 | 252.7 | 374.2
643 | 481 | 520.7 | 275 | 266.7 | 263.7 | 291.4 | 271.3 | 252.9 | 374.3
644 | 482 | 520.8 | 275.3 | 267.1 | 264.1 | 291.7 | 271.5 | 253.1 | 374.5
645 | 483 | 520.8 | 275.7 | 267.5 | 264.5 | 292.1 | 271.8 | 253.3 | 374.7
646 | 484 | 520.8 | 276 | 267.9 | 264.9 | 292.4 | 272 | 253.5 | 374.8
647 | 485 | 520.9 | 276.3 | 268.3 | 265.4 | 292.8 | 272.2 | 253.7 | 374.9
648 | 486 | 520.8 | 276.7 | 268.7 | 265.8 | 293.1 | 272.4 | 254 | 375.1
649 | 487 | 520.7 | 277 | 269.1 | 266.2 | 293.4 | 272.7 | 254.2 | 375.3
650 | 488 | 520.7 | 277.4 | 269.5 | 266.6 | 293.7 | 272.9 | 254.5 | 375.4
651 | 489 | 520.8 | 277.7 | 269.9 | 267 | 294 | 273.1 | 254.7 | 375.5
652 | 490 | 520.9 | 278.1 | 270.3 | 267.4 | 294.3 | 273.4 | 254.9 | 375.6
653 | 491 | 521.1 | 278.4 | 270.7 | 267.8 | 294.6 | 273.6 | 255.1 | 375.7
654 | 492 | 521.2 | 278.8 | 271.1 | 268.2 | 295 | 273.8 | 255.3 | 375.9
655 | 493 | 521.3 | 279.1 | 271.5 | 268.5 | 295.3 | 274 | 255.6 | 376
656 | 494 | 521.4 | 279.4 | 271.9 | 268.9 | 295.7 | 274.3 | 255.8 | 376.2
657 | 495 | 521.6 | 279.8 | 272.3 | 269.2 | 296 | 274.5 | 256.1 | 376.3
658 | 496 | 521.7 | 280.1 | 272.7 | 269.6 | 296.3 | 274.7 | 256.3 | 376.5
659 | 497 | 521.6 | 280.5 | 273.1 | 270 | 296.7 | 274.9 | 256.6 | 376.6
660 | 498 | 521.6 | 280.8 | 273.5 | 270.4 | 297.1 | 275.1 | 256.8 | 376.6
661 | 499 | 521.6 | 281.2 | 273.9 | 270.7 | 297.5 | 275.3 | 257.1 | 376.7
662 | 500 | 521.4 | 281.5 | 274.3 | 271.1 | 297.8 | 275.4 | 257.3 | 376.9
663 | 501 | 521.2 | 281.9 | 274.6 | 271.5 | 298.2 | 275.6 | 257.6 | 377
664 | 502 | 521.1 | 282.2 | 275 | 271.8 | 298.5 | 275.8 | 257.8 | 377.1
665 | 503 | 521 | 282.5 | 275.4 | 272.2 | 298.8 | 276.1 | 258 | 377.2
666 | 504 | 520.9 | 282.9 | 275.8 | 272.6 | 299.2 | 276.2 | 258.3 | 377.3
667 | 505 | 520.7 | 283.2 | 276.2 | 272.9 | 299.5 | 276.5 | 258.5 | 377.4
668 | 506 | 520.9 | 283.6 | 276.6 | 273.3 | 299.8 | 276.7 | 258.8 | 377.5
669 | 507 | 521 | 283.9 | 277 | 273.6 | 300.1 | 276.9 | 259 | 377.6
670 | 508 | 520.9 | 284.3 | 277.4 | 274 | 300.4 | 277.1 | 259.3 | 377.8
671 | 509 | 520.9 | 284.6 | 277.7 | 274.4 | 300.7 | 277.3 | 259.5 | 377.9
672 | 510 | 521 | 285 | 278.1 | 274.7 | 301.1 | 277.5 | 259.7 | 378.1
673 | 511 | 521.2 | 285.3 | 278.5 | 275.1 | 301.4 | 277.6 | 260 | 378.3
674 | 512 | 521.2 | 285.6 | 278.9 | 275.4 | 301.7 | 277.8 | 260.2 | 378.3
675 | 513 | 521.3 | 286 | 279.2 | 275.8 | 302 | 277.9 | 260.4 | 378.4
676 | 514 | 521.4 | 286.3 | 279.6 | 276.1 | 302.3 | 278.1 | 260.6 | 378.4
677 | 515 | 521.6 | 286.6 | 280 | 276.5 | 302.6 | 278.3 | 260.8 | 378.4
678 | 516 | 521.7 | 287 | 280.4 | 276.8 | 302.9 | 278.5 | 261 | 378.4
679 | 517 | 521.5 | 287.3 | 280.8 | 277.2 | 303.2 | 278.7 | 261.2 | 378.5
680 | 518 | 521.4 | 287.6 | 281.2 | 277.5 | 303.5 | 278.9 | 261.4 | 378.5
681 | 519 | 521.3 | 287.9 | 281.6 | 277.8 | 303.8 | 279.1 | 261.7 | 378.6
682 | 520 | 521.3 | 288.3 | 281.9 | 278.2 | 304 | 279.3 | 261.9 | 378.6
683 | 521 | 521.3 | 288.6 | 282.3 | 278.5 | 304.3 | 279.5 | 262.1 | 378.7
684 | 522 | 521.2 | 288.9 | 282.6 | 278.9 | 304.6 | 279.7 | 262.3 | 378.8
685 | 523 | 521 | 289.2 | 283 | 279.2 | 304.9 | 279.9 | 262.6 | 378.9
686 | 524 | 521.2 | 289.6 | 283.3 | 279.6 | 305.1 | 280.1 | 262.9 | 379
687 | 525 | 521.3 | 289.9 | 283.7 | 279.9 | 305.4 | 280.3 | 263.1 | 379
688 | 526 | 521.3 | 290.2 | 284 | 280.2 | 305.7 | 280.5 | 263.4 | 379.2
689 | 527 | 521.4 | 290.5 | 284.4 | 280.5 | 306 | 280.7 | 263.7 | 379.3
690 | 528 | 521.4 | 290.8 | 284.8 | 280.9 | 306.2 | 280.8 | 264 | 379.3
691 | 529 | 521.5 | 291.2 | 285.1 | 281.2 | 306.5 | 281.1 | 264.3 | 379.4
692 | 530 | 521.5 | 291.5 | 285.5 | 281.5 | 306.7 | 281.3 | 264.5 | 379.5
693 | 531 | 521.5 | 291.8 | 285.8 | 281.9 | 307 | 281.5 | 264.8 | 379.6
694 | 532 | 521.6 | 292.1 | 286.2 | 282.2 | 307.3 | 281.7 | 265 | 379.6
695 | 533 | 521.5 | 292.5 | 286.5 | 282.5 | 307.6 | 281.8 | 265.3 | 379.7
696 | 534 | 521.5 | 292.8 | 286.9 | 282.9 | 307.8 | 282 | 265.5 | 379.8
697 | 535 | 521.5 | 293.1 | 287.2 | 283.2 | 308.1 | 282.3 | 265.8 | 379.8
698 | 536 | 521.4 | 293.4 | 287.5 | 283.5 | 308.4 | 282.5 | 266 | 379.9
699 | 537 | 521.4 | 293.7 | 287.9 | 283.8 | 308.6 | 282.7 | 266.3 | 380
700 | 538 | 521.4 | 294 | 288.2 | 284.2 | 308.9 | 282.8 | 266.6 | 380
701 | 539 | 521.4 | 294.3 | 288.6 | 284.5 | 309.2 | 283.1 | 266.8 | 380.1
702 | 540 | 521.5 | 294.6 | 288.9 | 284.8 | 309.4 | 283.3 | 267.1 | 380.3
703 | 541 | 521.5 | 294.9 | 289.2 | 285.1 | 309.6 | 283.5 | 267.3 | 380.4
704 | 542 | 521.6 | 295.2 | 289.6 | 285.5 | 309.8 | 283.7 | 267.6 | 380.5
705 | 543 | 521.8 | 295.5 | 289.9 | 285.8 | 310 | 283.9 | 267.9 | 380.6
706 | 544 | 521.7 | 295.8 | 290.2 | 286.1 | 310.3 | 284.2 | 268.1 | 380.7
707 | 545 | 521.7 | 296.1 | 290.5 | 286.4 | 310.5 | 284.4 | 268.4 | 380.8
708 | 546 | 521.7 | 296.4 | 290.8 | 286.7 | 310.8 | 284.6 | 268.7 | 380.9
709 | 547 | 521.9 | 296.6 | 291.2 | 287 | 311 | 284.8 | 269 | 381
710 | 548 | 522.1 | 296.9 | 291.5 | 287.3 | 311.3 | 285.1 | 269.3 | 381.1
711 | 549 | 522.1 | 297.2 | 291.8 | 287.6 | 311.5 | 285.4 | 269.6 | 381.2
712 | 550 | 522.1 | 297.5 | 292.2 | 287.9 | 311.8 | 285.6 | 269.8 | 381.3
713 | 551 | 522.1 | 297.8 | 292.6 | 288.2 | 312 | 285.9 | 269.9 | 381.4
714 | 552 | 521.8 | 298.1 | 292.9 | 288.5 | 312.3 | 286.1 | 270.1 | 381.5
715 | 553 | 521.7 | 298.3 | 293.3 | 288.8 | 312.6 | 286.4 | 270.2 | 381.7
716 | 554 | 521.4 | 298.6 | 293.6 | 289.1 | 312.9 | 286.6 | 270.4 | 381.7
717 | 555 | 521.3 | 298.9 | 293.9 | 289.4 | 313.1 | 286.9 | 270.6 | 381.8
718 | 556 | 521.1 | 299.2 | 294.3 | 289.7 | 313.4 | 287.1 | 270.7 | 381.9
719 | 557 | 521.1 | 299.5 | 294.5 | 290.1 | 313.7 | 287.4 | 270.9 | 382
720 | 558 | 521.1 | 299.8 | 294.8 | 290.4 | 314 | 287.6 | 271.1 | 382.1
721 | 559 | 521 | 300.1 | 295.1 | 290.7 | 314.3 | 287.8 | 271.3 | 382.2
722 | 560 | 520.9 | 300.4 | 295.5 | 291 | 314.6 | 288 | 271.5 | 382.3
723 | 561 | 520.9 | 300.7 | 295.8 | 291.3 | 314.9 | 288.2 | 271.7 | 382.4
724 | 562 | 520.8 | 301 | 296.1 | 291.6 | 315.2 | 288.4 | 271.9 | 382.5
725 | 563 | 520.7 | 301.2 | 296.4 | 291.9 | 315.4 | 288.6 | 272.1 | 382.5
726 | 564 | 520.7 | 301.5 | 296.7 | 292.2 | 315.7 | 288.8 | 272.3 | 382.6
727 | 565 | 520.6 | 301.8 | 297 | 292.5 | 315.9 | 289 | 272.5 | 382.7
728 | 566 | 520.6 | 302.1 | 297.3 | 292.8 | 316.2 | 289.2 | 272.6 | 382.8
729 | 567 | 520.6 | 302.4 | 297.6 | 293.1 | 316.5 | 289.4 | 272.8 | 382.9
730 | 568 | 520.7 | 302.7 | 298 | 293.4 | 316.7 | 289.6 | 273 | 383
731 | 569 | 520.8 | 302.9 | 298.3 | 293.7 | 317 | 289.8 | 273.2 | 383
732 | 570 | 520.8 | 303.2 | 298.5 | 294 | 317.3 | 290 | 273.4 | 383.1
733 | 571 | 520.7 | 303.5 | 298.9 | 294.3 | 317.5 | 290.2 | 273.6 | 383.2
734 | 572 | 520.8 | 303.8 | 299.2 | 294.6 | 317.7 | 290.3 | 273.8 | 383.3
735 | 573 | 520.8 | 304 | 299.4 | 294.8 | 318 | 290.5 | 274 | 383.4
736 | 574 | 521 | 304.3 | 299.7 | 295.1 | 318.3 | 290.6 | 274.1 | 383.4
737 | 575 | 521.1 | 304.6 | 300 | 295.4 | 318.5 | 290.8 | 274.3 | 383.6
738 | 576 | 521.2 | 304.8 | 300.3 | 295.7 | 318.7 | 291 | 274.5 | 383.7
739 | 577 | 521.4 | 305.1 | 300.6 | 296 | 318.9 | 291.1 | 274.7 | 383.8
740 | 578 | 521.5 | 305.4 | 300.9 | 296.3 | 319.2 | 291.3 | 274.8 | 383.8
741 | 579 | 521.6 | 305.6 | 301.2 | 296.6 | 319.4 | 291.5 | 275 | 383.9
742 | 580 | 521.8 | 305.9 | 301.5 | 296.8 | 319.7 | 291.7 | 275.2 | 384
743 | 581 | 521.8 | 306.2 | 301.8 | 297.1 | 319.9 | 291.9 | 275.4 | 384.1
744 | 582 | 521.9 | 306.4 | 302.1 | 297.4 | 320.1 | 292.1 | 275.6 | 384.2
745 | 583 | 522 | 306.7 | 302.4 | 297.7 | 320.3 | 292.3 | 275.7 | 384.3
746 | 584 | 522.1 | 306.9 | 302.7 | 297.9 | 320.5 | 292.5 | 275.9 | 384.4
747 | 585 | 522.1 | 307.2 | 303 | 298.2 | 320.8 | 292.7 | 276.1 | 384.5
748 | 586 | 522.2 | 307.5 | 303.3 | 298.5 | 321 | 292.9 | 276.3 | 384.6
749 | 587 | 522.3 | 307.7 | 303.6 | 298.8 | 321.2 | 293.1 | 276.5 | 384.8
750 | 588 | 522.4 | 307.9 | 303.9 | 299 | 321.4 | 293.4 | 276.7 | 384.9
751 | 589 | 522.3 | 308.2 | 304.1 | 299.3 | 321.7 | 293.6 | 276.9 | 385.1
752 | 590 | 521.9 | 308.5 | 304.4 | 299.6 | 321.9 | 293.8 | 277.1 | 385.3
753 | 591 | 521.7 | 308.7 | 304.7 | 299.8 | 322.1 | 294 | 277.2 | 385.5
754 | 592 | 521.7 | 309 | 305 | 300.1 | 322.3 | 294.3 | 277.4 | 385.6
755 | 593 | 521.6 | 309.2 | 305.3 | 300.4 | 322.5 | 294.5 | 277.6 | 385.6
756 | 594 | 521.4 | 309.5 | 305.6 | 300.6 | 322.7 | 294.8 | 277.8 | 385.7
757 | 595 | 521.4 | 309.8 | 305.8 | 300.9 | 323 | 295 | 278 | 385.8
758 | 596 | 521.4 | 310 | 306.1 | 301.2 | 323.2 | 295.2 | 278.2 | 385.9
759 | 597 | 521.4 | 310.3 | 306.3 | 301.4 | 323.4 | 295.4 | 278.3 | 386
760 | 598 | 521.4 | 310.5 | 306.6 | 301.7 | 323.6 | 295.7 | 278.5 | 386
761 | 599 | 521.3 | 310.8 | 306.9 | 302 | 323.8 | 295.9 | 278.6 | 386.2
762 | 600 | 521.2 | 311 | 307.2 | 302.2 | 324.1 | 296.1 | 278.8 | 386.3
763 | 601 | 521.3 | 311.3 | 307.4 | 302.5 | 324.3 | 296.3 | 278.9 | 386.4
764 | 602 | 521.2 | 311.5 | 307.7 | 302.7 | 324.5 | 296.5 | 279.1 | 386.5
765 | 603 | 521.3 | 311.8 | 308 | 303 | 324.7 | 296.7 | 279.2 | 386.6
766 | 604 | 521.4 | 312 | 308.2 | 303.3 | 325 | 296.8 | 279.4 | 386.7
767 | 605 | 521.3 | 312.3 | 308.5 | 303.5 | 325.2 | 297 | 279.5 | 386.9
768 | 606 | 521.2 | 312.5 | 308.8 | 303.8 | 325.4 | 297.2 | 279.6 | 387
769 | 607 | 521 | 312.7 | 309 | 304 | 325.6 | 297.4 | 279.8 | 387.1
770 | 608 | 520.9 | 313 | 309.3 | 304.3 | 325.9 | 297.6 | 280 | 387.2
771 | 609 | 521.1 | 313.2 | 309.5 | 304.5 | 326.1 | 297.7 | 280.1 | 387.3
772 | 610 | 521.2 | 313.5 | 309.8 | 304.7 | 326.3 | 297.9 | 280.3 | 387.4
773 | 611 | 521.2 | 313.7 | 310 | 305 | 326.5 | 298.1 | 280.5 | 387.6
774 | 612 | 521.3 | 313.9 | 310.2 | 305.3 | 326.7 | 298.3 | 280.7 | 387.7
775 | 613 | 521.3 | 314.2 | 310.5 | 305.5 | 327 | 298.4 | 280.8 | 387.8
776 | 614 | 521.1 | 314.4 | 310.6 | 305.7 | 327.2 | 298.6 | 281 | 387.9
777 | 615 | 521.2 | 314.6 | 310.8 | 306 | 327.4 | 298.8 | 281.2 | 388
778 | 616 | 521.3 | 314.9 | 311 | 306.2 | 327.6 | 298.9 | 281.3 | 388
779 | 617 | 521.4 | 315.1 | 311.2 | 306.5 | 327.8 | 299.1 | 281.5 | 388.1
780 | 618 | 521.6 | 315.3 | 311.4 | 306.7 | 328 | 299.3 | 281.7 | 388.3
781 | 619 | 521.8 | 315.5 | 311.6 | 306.9 | 328.2 | 299.4 | 281.9 | 388.4
782 | 620 | 521.8 | 315.7 | 311.8 | 307.2 | 328.4 | 299.6 | 282 | 388.5
783 | 621 | 521.9 | 316 | 311.9 | 307.4 | 328.5 | 299.7 | 282.2 | 388.6
784 | 622 | 521.9 | 316.2 | 312.1 | 307.6 | 328.7 | 299.9 | 282.3 | 388.7
785 | 623 | 522 | 316.4 | 312.3 | 307.9 | 328.8 | 300.1 | 282.4 | 388.8
786 | 624 | 522.3 | 316.7 | 312.5 | 308.1 | 329 | 300.3 | 282.6 | 388.8
787 | 625 | 522.4 | 316.9 | 312.7 | 308.4 | 329.1 | 300.4 | 282.7 | 388.9
788 | 626 | 522.3 | 317.1 | 312.9 | 308.6 | 329.2 | 300.6 | 282.8 | 389
789 | 627 | 522.1 | 317.3 | 313 | 308.8 | 329.4 | 300.8 | 283 | 389.1
790 | 628 | 521.8 | 317.5 | 313.1 | 309.1 | 329.5 | 301 | 283.2 | 389.2
791 | 629 | 521.9 | 317.7 | 313.3 | 309.3 | 329.7 | 301.1 | 283.4 | 389.3
792 | 630 | 522.1 | 317.9 | 313.4 | 309.5 | 329.9 | 301.2 | 283.5 | 389.4
793 | 631 | 522.2 | 318.1 | 313.6 | 309.8 | 330 | 301.3 | 283.8 | 389.4
794 | 632 | 522.3 | 318.3 | 313.8 | 310 | 330.2 | 301.5 | 284 | 389.4
795 | 633 | 522.1 | 318.6 | 314 | 310.2 | 330.4 | 301.6 | 284.2 | 389.5
796 | 634 | 522 | 318.8 | 314.1 | 310.4 | 330.6 | 301.7 | 284.4 | 389.6
797 | 635 | 521.8 | 319 | 314.3 | 310.6 | 330.7 | 301.9 | 284.6 | 389.6
798 | 636 | 521.8 | 319.2 | 314.6 | 310.9 | 330.9 | 302.1 | 284.8 | 389.7
799 | 637 | 521.9 | 319.3 | 314.8 | 311.1 | 331 | 302.3 | 285 | 389.7
800 | 638 | 522 | 319.6 | 315 | 311.3 | 331.2 | 302.4 | 285.1 | 389.8
801 | 639 | 522.2 | 319.8 | 315.2 | 311.5 | 331.4 | 302.5 | 285.3 | 389.8
802 | 640 | 522.4 | 320 | 315.4 | 311.7 | 331.5 | 302.6 | 285.5 | 389.8
803 | 641 | 522.4 | 320.2 | 315.6 | 311.9 | 331.7 | 302.8 | 285.7 | 389.9
804 | 642 | 522.3 | 320.4 | 315.8 | 312.1 | 331.9 | 302.9 | 285.9 | 390
805 | 643 | 522.3 | 320.5 | 316 | 312.3 | 332 | 303 | 286.1 | 390
806 | 644 | 522.4 | 320.7 | 316.2 | 312.5 | 332.2 | 303.1 | 286.3 | 390
807 | 645 | 522.2 | 320.9 | 316.4 | 312.7 | 332.3 | 303.2 | 286.5 | 390.1
808 | 646 | 522.2 | 321.1 | 316.6 | 312.9 | 332.5 | 303.4 | 286.7 | 390.1
809 | 647 | 521.9 | 321.3 | 316.7 | 313.1 | 332.6 | 303.5 | 286.8 | 390.1
810 | 648 | 521.8 | 321.5 | 317 | 313.3 | 332.8 | 303.6 | 287 | 390.2
811 | 649 | 521.8 | 321.7 | 317.2 | 313.5 | 332.9 | 303.7 | 287.2 | 390.2
812 | 650 | 521.6 | 321.8 | 317.4 | 313.7 | 333 | 303.9 | 287.3 | 390.2
813 | 651 | 521.4 | 322 | 317.7 | 313.8 | 333 | 304.1 | 287.5 | 390.3
814 | 652 | 521.3 | 322.1 | 318 | 314 | 333 | 304.2 | 287.7 | 390.4
815 | 653 | 521.2 | 322.3 | 318.2 | 314.2 | 333.1 | 304.3 | 287.8 | 390.4
816 | 654 | 521.1 | 322.5 | 318.4 | 314.4 | 333.3 | 304.5 | 288 | 390.5
817 | 655 | 521.2 | 322.7 | 318.7 | 314.5 | 333.4 | 304.6 | 288.1 | 390.5
818 | 656 | 521.3 | 322.8 | 318.9 | 314.7 | 333.6 | 304.7 | 288.2 | 390.6
819 | 657 | 521.3 | 323 | 319.1 | 314.9 | 333.7 | 304.9 | 288.3 | 390.6
820 | 658 | 521.3 | 323.2 | 319.3 | 315.1 | 333.8 | 305 | 288.5 | 390.7
821 | 659 | 521.4 | 323.4 | 319.5 | 315.3 | 333.9 | 305.2 | 288.6 | 390.8
822 | 660 | 521.3 | 323.6 | 319.7 | 315.5 | 334.1 | 305.3 | 288.8 | 390.8
823 | 661 | 521.5 | 323.8 | 319.9 | 315.7 | 334.2 | 305.5 | 288.9 | 390.9
824 | 662 | 521.6 | 323.9 | 320.1 | 315.9 | 334.3 | 305.7 | 289 | 391
825 | 663 | 521.6 | 324.1 | 320.3 | 316 | 334.5 | 305.8 | 289.1 | 391.1
826 | 664 | 521.8 | 324.3 | 320.5 | 316.2 | 334.6 | 305.9 | 289.2 | 391.1
827 | 665 | 521.9 | 324.5 | 320.7 | 316.4 | 334.7 | 306.1 | 289.3 | 391.2
828 | 666 | 522 | 324.6 | 320.9 | 316.6 | 334.9 | 306.2 | 289.4 | 391.3
829 | 667 | 521.9 | 324.8 | 321.1 | 316.8 | 335 | 306.4 | 289.5 | 391.3
830 | 668 | 521.7 | 325 | 321.3 | 317 | 335.1 | 306.6 | 289.7 | 391.4
831 | 669 | 521.7 | 325.1 | 321.4 | 317.2 | 335.3 | 306.7 | 289.8 | 391.4
832 | 670 | 521.9 | 325.3 | 321.6 | 317.3 | 335.4 | 306.9 | 290 | 391.5
833 | 671 | 522.1 | 325.5 | 321.8 | 317.5 | 335.6 | 307.1 | 290.1 | 391.6
834 | 672 | 522.1 | 325.7 | 322 | 317.7 | 335.7 | 307.2 | 290.2 | 391.7
835 | 673 | 522.1 | 325.8 | 322.2 | 317.9 | 335.9 | 307.4 | 290.3 | 391.8
836 | 674 | 521.8 | 326 | 322.4 | 318.1 | 336 | 307.6 | 290.4 | 391.9
837 | 675 | 521.7 | 326.2 | 322.5 | 318.3 | 336.1 | 307.7 | 290.5 | 392
838 | 676 | 521.6 | 326.4 | 322.7 | 318.4 | 336.3 | 307.9 | 290.6 | 392.1
839 | 677 | 521.8 | 326.5 | 322.9 | 318.6 | 336.4 | 308 | 290.7 | 392.1
840 | 678 | 522.2 | 326.7 | 323 | 318.8 | 336.5 | 308.2 | 290.8 | 392.2
841 | 679 | 522.4 | 326.8 | 323.2 | 319 | 336.6 | 308.4 | 291 | 392.4
842 | 680 | 522.4 | 327 | 323.4 | 319.1 | 336.8 | 308.6 | 291.1 | 392.5
843 | 681 | 522.4 | 327.2 | 323.5 | 319.3 | 337 | 308.8 | 291.3 | 392.5
844 | 682 | 522.7 | 327.4 | 323.7 | 319.5 | 337.1 | 308.9 | 291.4 | 392.6
845 | 683 | 522.8 | 327.5 | 323.9 | 319.7 | 337.2 | 309.1 | 291.5 | 392.7
846 | 684 | 522.8 | 327.7 | 324 | 319.8 | 337.4 | 309.2 | 291.6 | 392.9
847 | 685 | 522.9 | 327.9 | 324.2 | 320 | 337.5 | 309.4 | 291.7 | 393
848 | 686 | 522.9 | 328 | 324.4 | 320.2 | 337.6 | 309.6 | 291.8 | 393.1
849 | 687 | 522.9 | 328.2 | 324.6 | 320.3 | 337.7 | 309.7 | 291.9 | 393.2
850 | 688 | 523 | 328.3 | 324.7 | 320.5 | 337.9 | 309.9 | 292 | 393.3
851 | 689 | 523.2 | 328.5 | 324.9 | 320.7 | 338 | 310.1 | 292.1 | 393.4
852 | 690 | 523.1 | 328.7 | 325.1 | 320.8 | 338.1 | 310.2 | 292.2 | 393.5
853 | 691 | 523 | 328.8 | 325.2 | 321 | 338.3 | 310.4 | 292.4 | 393.6
854 | 692 | 523 | 329 | 325.4 | 321.2 | 338.4 | 310.6 | 292.5 | 393.7
855 | 693 | 523 | 329.1 | 325.5 | 321.3 | 338.5 | 310.7 | 292.6 | 393.8
856 | 694 | 523.1 | 329.3 | 325.7 | 321.5 | 338.7 | 310.9 | 292.7 | 393.9
857 | 695 | 523 | 329.4 | 325.9 | 321.6 | 338.8 | 311.1 | 292.9 | 394
858 | 696 | 522.9 | 329.6 | 326 | 321.8 | 338.9 | 311.2 | 293 | 394
859 | 697 | 522.9 | 329.7 | 326.2 | 322 | 339 | 311.4 | 293.1 | 394.1
860 | 698 | 523 | 329.9 | 326.3 | 322.1 | 339.2 | 311.5 | 293.2 | 394.2
861 | 699 | 523 | 330 | 326.5 | 322.3 | 339.3 | 311.7 | 293.3 | 394.3
862 | 700 | 522.8 | 330.2 | 326.6 | 322.4 | 339.4 | 311.8 | 293.4 | 394.4
863 | 701 | 522.5 | 330.3 | 326.8 | 322.6 | 339.5 | 311.9 | 293.4 | 394.5
864 | 702 | 522.5 | 330.5 | 326.9 | 322.8 | 339.7 | 312.1 | 293.5 | 394.6
865 | 703 | 522.3 | 330.6 | 327.1 | 322.9 | 339.8 | 312.2 | 293.6 | 394.7
866 | 704 | 522.2 | 330.8 | 327.2 | 323.1 | 339.9 | 312.3 | 293.6 | 394.8
867 | 705 | 522.1 | 330.9 | 327.4 | 323.2 | 340 | 312.4 | 293.7 | 394.9
868 | 706 | 521.9 | 331.1 | 327.5 | 323.4 | 340.2 | 312.5 | 293.7 | 394.9
869 | 707 | 521.6 | 331.2 | 327.7 | 323.5 | 340.3 | 312.6 | 293.8 | 395.1
870 | 708 | 521.6 | 331.4 | 327.8 | 323.7 | 340.4 | 312.7 | 293.8 | 395.2
871 | 709 | 521.6 | 331.5 | 327.9 | 323.8 | 340.5 | 312.8 | 293.9 | 395.3
872 | 710 | 521.6 | 331.7 | 328.1 | 324 | 340.7 | 313 | 293.9 | 395.3
873 | 711 | 521.6 | 331.8 | 328.2 | 324.1 | 340.8 | 313.1 | 294 | 395.4
874 | 712 | 521.7 | 331.9 | 328.4 | 324.3 | 340.8 | 313.2 | 294 | 395.4
875 | 713 | 521.8 | 332.1 | 328.6 | 324.4 | 340.9 | 313.3 | 293.9 | 395.5
876 | 714 | 521.9 | 332.2 | 328.7 | 324.6 | 341.1 | 313.4 | 293.9 | 395.6
877 | 715 | 521.7 | 332.3 | 328.9 | 324.7 | 341.2 | 313.5 | 294 | 395.7
878 | 716 | 521.7 | 332.5 | 329 | 324.9 | 341.3 | 313.7 | 294 | 395.8
879 | 717 | 521.8 | 332.6 | 329.1 | 325 | 341.4 | 313.8 | 294 | 395.9
880 | 718 | 521.9 | 332.7 | 329.3 | 325.2 | 341.5 | 313.9 | 294.1 | 395.9
881 | 719 | 521.8 | 332.8 | 329.4 | 325.3 | 341.6 | 314.1 | 294.1 | 396
882 | 720 | 521.7 | 333 | 329.6 | 325.4 | 341.7 | 314.2 | 294.2 | 396.2
883 | 721 | 521.5 | 333.1 | 329.8 | 325.6 | 341.8 | 314.4 | 294.3 | 396.3
884 | 722 | 521.3 | 333.2 | 329.9 | 325.7 | 341.9 | 314.5 | 294.4 | 396.3
885 | 723 | 521.2 | 333.4 | 330 | 325.8 | 342 | 314.6 | 294.5 | 396.4
886 | 724 | 521 | 333.5 | 330.2 | 326 | 342.1 | 314.8 | 294.6 | 396.5
887 | 725 | 520.8 | 333.6 | 330.3 | 326.1 | 342.2 | 314.9 | 294.7 | 396.6
888 | 726 | 520.7 | 333.8 | 330.4 | 326.3 | 342.3 | 315.1 | 294.9 | 396.7
889 | 727 | 520.5 | 333.9 | 330.5 | 326.4 | 342.4 | 315.3 | 295 | 396.8
890 | 728 | 520.4 | 334 | 330.7 | 326.5 | 342.6 | 315.4 | 295.2 | 396.8
891 | 729 | 520.2 | 334.1 | 330.8 | 326.7 | 342.7 | 315.5 | 295.3 | 396.9
892 | 730 | 520.3 | 334.3 | 330.9 | 326.8 | 342.8 | 315.7 | 295.4 | 397
893 | 731 | 520.4 | 334.4 | 331.1 | 326.9 | 342.9 | 315.8 | 295.5 | 397.1
894 | 732 | 520.5 | 334.5 | 331.2 | 327 | 342.9 | 316 | 295.5 | 397.2
895 | 733 | 520.6 | 334.6 | 331.4 | 327.2 | 343 | 316.1 | 295.6 | 397.3
896 | 734 | 521 | 334.7 | 331.5 | 327.3 | 343.1 | 316.2 | 295.7 | 397.3
897 | 735 | 521.1 | 334.8 | 331.7 | 327.4 | 343.2 | 316.4 | 295.8 | 397.3
898 | 736 | 521.1 | 334.9 | 331.8 | 327.6 | 343.3 | 316.5 | 295.9 | 397.3
899 | 737 | 521.1 | 335 | 331.9 | 327.7 | 343.4 | 316.7 | 296 | 397.4
900 | 738 | 521.4 | 335.2 | 332 | 327.8 | 343.5 | 316.8 | 296.1 | 397.4
901 | 739 | 521.4 | 335.3 | 332.2 | 327.9 | 343.6 | 316.9 | 296.2 | 397.4
902 | 740 | 521.2 | 335.4 | 332.3 | 328.1 | 343.7 | 317.1 | 296.3 | 397.4
903 | 741 | 521.2 | 335.5 | 332.5 | 328.2 | 343.7 | 317.2 | 296.5 | 397.5
904 | 742 | 521.2 | 335.6 | 332.6 | 328.3 | 343.8 | 317.3 | 296.6 | 397.5
905 | 743 | 521.3 | 335.7 | 332.8 | 328.4 | 343.9 | 317.4 | 296.7 | 397.6
906 | 744 | 521.4 | 335.8 | 332.9 | 328.5 | 344 | 317.5 | 296.9 | 397.6
907 | 745 | 521.4 | 335.9 | 333 | 328.7 | 344.1 | 317.7 | 297 | 397.7
908 | 746 | 521.5 | 336 | 333.2 | 328.8 | 344.2 | 317.8 | 297.2 | 397.8
909 | 747 | 521.7 | 336.1 | 333.3 | 328.9 | 344.2 | 317.9 | 297.3 | 397.9
910 | 748 | 521.8 | 336.2 | 333.5 | 329 | 344.3 | 318.1 | 297.4 | 398
911 | 749 | 522.1 | 336.4 | 333.6 | 329.2 | 344.4 | 318.3 | 297.5 | 398.1
912 | 750 | 522.1 | 336.4 | 333.8 | 329.3 | 344.5 | 318.4 | 297.6 | 398.2
913 | 751 | 522 | 336.6 | 333.9 | 329.4 | 344.6 | 318.5 | 297.7 | 398.2
914 | 752 | 522.1 | 336.7 | 334.1 | 329.5 | 344.6 | 318.6 | 297.8 | 398.3
915 | 753 | 522 | 336.8 | 334.2 | 329.6 | 344.7 | 318.8 | 297.8 | 398.4
916 | 754 | 522 | 336.9 | 334.4 | 329.8 | 344.8 | 318.9 | 297.9 | 398.5
917 | 755 | 522 | 337 | 334.5 | 329.9 | 344.9 | 319 | 298 | 398.5
918 | 756 | 521.8 | 337.1 | 334.7 | 330 | 345 | 319.1 | 298.1 | 398.5
919 | 757 | 521.8 | 337.2 | 334.8 | 330.1 | 345.1 | 319.3 | 298.2 | 398.5
920 | 758 | 521.7 | 337.3 | 335 | 330.2 | 345.2 | 319.4 | 298.3 | 398.6
921 | 759 | 521.7 | 337.4 | 335.1 | 330.3 | 345.2 | 319.5 | 298.5 | 398.6
922 | 760 | 521.7 | 337.5 | 335.2 | 330.4 | 345.3 | 319.6 | 298.6 | 398.7
923 | 761 | 521.7 | 337.6 | 335.4 | 330.6 | 345.4 | 319.8 | 298.8 | 398.7
924 | 762 | 521.7 | 337.7 | 335.5 | 330.7 | 345.5 | 319.9 | 299 | 398.7
925 | 763 | 521.4 | 337.8 | 335.7 | 330.8 | 345.6 | 320.1 | 299.1 | 398.7
926 | 764 | 521 | 337.9 | 335.8 | 330.9 | 345.7 | 320.2 | 299.1 | 398.7
927 | 765 | 520.9 | 338 | 336 | 331 | 345.7 | 320.3 | 299.2 | 398.8
928 | 766 | 520.8 | 338.1 | 336.1 | 331.1 | 345.8 | 320.5 | 299.3 | 398.9
929 | 767 | 520.6 | 338.2 | 336.2 | 331.3 | 345.9 | 320.6 | 299.4 | 398.9
930 | 768 | 520.7 | 338.3 | 336.2 | 331.4 | 346 | 320.8 | 299.5 | 399
931 | 769 | 520.7 | 338.4 | 336.3 | 331.5 | 346.1 | 320.9 | 299.6 | 399.1
932 | 770 | 520.8 | 338.5 | 336.4 | 331.6 | 346.2 | 321.1 | 299.8 | 399.2
933 | 771 | 520.8 | 338.6 | 336.6 | 331.7 | 346.3 | 321.2 | 299.9 | 399.2
934 | 772 | 520.7 | 338.8 | 336.7 | 331.8 | 346.3 | 321.4 | 300 | 399.2
935 | 773 | 520.7 | 338.9 | 336.8 | 331.9 | 346.4 | 321.5 | 300.1 | 399.3
936 | 774 | 520.9 | 339 | 337 | 332 | 346.5 | 321.7 | 300.2 | 399.3
937 | 775 | 521 | 339.1 | 337.1 | 332.1 | 346.6 | 321.9 | 300.3 | 399.3
938 | 776 | 521.1 | 339.2 | 337.3 | 332.2 | 346.7 | 322.1 | 300.3 | 399.3
939 | 777 | 521.1 | 339.3 | 337.4 | 332.3 | 346.7 | 322.2 | 300.4 | 399.3
940 | 778 | 521.4 | 339.4 | 337.6 | 332.5 | 346.8 | 322.3 | 300.5 | 399.3
941 | 779 | 521.6 | 339.5 | 337.8 | 332.6 | 346.9 | 322.5 | 300.5 | 399.4
942 | 780 | 521.7 | 339.6 | 337.9 | 332.7 | 346.9 | 322.6 | 300.5 | 399.4
943 | 781 | 521.7 | 339.7 | 338.1 | 332.8 | 347 | 322.8 | 300.6 | 399.3
944 | 782 | 521.6 | 339.9 | 338.2 | 332.9 | 347.1 | 322.9 | 300.7 | 399.3
945 | 783 | 521.5 | 340 | 338.4 | 333 | 347.1 | 323.1 | 300.8 | 399.3
946 | 784 | 521.5 | 340.1 | 338.5 | 333.1 | 347.2 | 323.3 | 301 | 399.3
947 | 785 | 521.5 | 340.2 | 338.7 | 333.2 | 347.3 | 323.5 | 301.1 | 399.3
948 | 786 | 521.7 | 340.3 | 338.8 | 333.3 | 347.4 | 323.6 | 301.2 | 399.3
949 | 787 | 521.8 | 340.4 | 339 | 333.4 | 347.4 | 323.8 | 301.2 | 399.4
950 | 788 | 521.7 | 340.5 | 339.1 | 333.5 | 347.5 | 324 | 301.2 | 399.4
951 | 789 | 521.6 | 340.6 | 339.3 | 333.6 | 347.6 | 324.1 | 301.3 | 399.4
952 | 790 | 521.7 | 340.7 | 339.4 | 333.7 | 347.6 | 324.3 | 301.4 | 399.5
953 | 791 | 521.7 | 340.8 | 339.5 | 333.8 | 347.7 | 324.5 | 301.5 | 399.5
954 | 792 | 521.8 | 340.9 | 339.7 | 334 | 347.8 | 324.6 | 301.5 | 399.6
955 | 793 | 521.9 | 341 | 339.8 | 334.1 | 347.9 | 324.8 | 301.6 | 399.6
956 | 794 | 521.9 | 341.1 | 340 | 334.2 | 348 | 324.9 | 301.7 | 399.6
957 | 795 | 521.8 | 341.2 | 340.1 | 334.3 | 348 | 325 | 301.8 | 399.6
958 | 796 | 521.9 | 341.3 | 340.3 | 334.4 | 348.1 | 325.1 | 301.9 | 399.7
959 | 797 | 521.9 | 341.4 | 340.4 | 334.5 | 348.2 | 325.2 | 302 | 399.7
960 | 798 | 521.9 | 341.5 | 340.6 | 334.6 | 348.3 | 325.3 | 302.1 | 399.7
961 | 799 | 522 | 341.6 | 340.7 | 334.7 | 348.4 | 325.4 | 302.2 | 399.7
962 | 800 | 521.9 | 341.7 | 340.9 | 334.8 | 348.4 | 325.5 | 302.3 | 399.8
963 | 801 | 521.9 | 341.8 | 341 | 334.9 | 348.5 | 325.5 | 302.5 | 399.8
964 | 802 | 522 | 341.9 | 341.2 | 335 | 348.6 | 325.6 | 302.6 | 399.8
965 | 803 | 522.2 | 342 | 341.4 | 335.1 | 348.6 | 325.6 | 302.8 | 399.9
966 | 804 | 522.4 | 342.1 | 341.5 | 335.2 | 348.7 | 325.7 | 302.9 | 399.9
967 | 805 | 522.4 | 342.2 | 341.7 | 335.3 | 348.8 | 325.8 | 303 | 399.9
968 | 806 | 522.3 | 342.3 | 341.8 | 335.4 | 348.8 | 325.9 | 303.1 | 399.9
969 | 807 | 522.3 | 342.4 | 342 | 335.5 | 348.9 | 326 | 303.2 | 400
970 | 808 | 522.4 | 342.5 | 342.1 | 335.6 | 349 | 326.1 | 303.2 | 400
971 | 809 | 522.5 | 342.6 | 342.3 | 335.7 | 349.1 | 326.2 | 303.2 | 400.1
972 | 810 | 522.2 | 342.8 | 342.4 | 335.8 | 349.2 | 326.3 | 303.3 | 400.2
973 | 811 | 522 | 342.9 | 342.5 | 335.9 | 349.3 | 326.4 | 303.3 | 400.2
974 | 812 | 521.9 | 343 | 342.7 | 336 | 349.4 | 326.5 | 303.3 | 400.2
975 | 813 | 521.9 | 343.1 | 342.8 | 336.1 | 349.4 | 326.6 | 303.4 | 400.2
976 | 814 | 521.7 | 343.2 | 343 | 336.2 | 349.5 | 326.7 | 303.4 | 400.2
977 | 815 | 521.7 | 343.4 | 343.1 | 336.3 | 349.6 | 326.8 | 303.5 | 400.2
978 | 816 | 521.6 | 343.5 | 343.2 | 336.4 | 349.7 | 326.9 | 303.5 | 400.2
979 | 817 | 521.3 | 343.6 | 343.4 | 336.6 | 349.8 | 327 | 303.6 | 400.3
980 | 818 | 521.1 | 343.8 | 343.5 | 336.7 | 349.9 | 327.2 | 303.7 | 400.3
981 | 819 | 520.8 | 343.9 | 343.7 | 336.7 | 350 | 327.3 | 303.7 | 400.4
982 | 820 | 520.9 | 344 | 343.8 | 336.9 | 350.1 | 327.5 | 303.7 | 400.4
983 | 821 | 520.8 | 344.1 | 343.9 | 337 | 350.2 | 327.6 | 303.7 | 400.4
984 | 822 | 520.9 | 344.2 | 344.1 | 337.1 | 350.3 | 327.7 | 303.7 | 400.5
985 | 823 | 521 | 344.3 | 344.2 | 337.2 | 350.4 | 327.8 | 303.7 | 400.6
986 | 824 | 521 | 344.4 | 344.4 | 337.3 | 350.5 | 328 | 303.7 | 400.6
987 | 825 | 521 | 344.5 | 344.5 | 337.4 | 350.6 | 328.1 | 303.7 | 400.6
988 | 826 | 521 | 344.6 | 344.6 | 337.5 | 350.7 | 328.2 | 303.8 | 400.7
989 | 827 | 521.1 | 344.7 | 344.8 | 337.6 | 350.8 | 328.3 | 303.9 | 400.8
990 | 828 | 521.1 | 344.9 | 344.8 | 337.7 | 350.9 | 328.4 | 304 | 400.8
991 | 829 | 521.2 | 345 | 345 | 337.8 | 351 | 328.5 | 304.1 | 400.8
992 | 830 | 521.5 | 345.1 | 345.1 | 337.9 | 351.1 | 328.6 | 304.2 | 400.9
993 | 831 | 521.7 | 345.2 | 345.2 | 338 | 351.2 | 328.7 | 304.3 | 401
994 | 832 | 521.8 | 345.3 | 345.4 | 338.1 | 351.2 | 328.8 | 304.4 | 401
995 | 833 | 521.9 | 345.4 | 345.5 | 338.2 | 351.3 | 328.9 | 304.6 | 401.1
996 | 834 | 521.9 | 345.5 | 345.6 | 338.3 | 351.4 | 329 | 304.7 | 401.1
997 | 835 | 521.8 | 345.6 | 345.8 | 338.5 | 351.5 | 329.1 | 304.8 | 401.2
998 | 836 | 521.9 | 345.8 | 345.9 | 338.6 | 351.6 | 329.2 | 304.9 | 401.2
999 | 837 | 522 | 345.9 | 346 | 338.7 | 351.7 | 329.3 | 305 | 401.3
1000 | 838 | 522.2 | 346 | 346.1 | 338.8 | 351.8 | 329.4 | 305.1 | 401.4
1001 | 839 | 522.1 | 346.1 | 346.3 | 338.9 | 351.9 | 329.5 | 305.2 | 401.5
1002 | 840 | 522.1 | 346.2 | 346.4 | 339 | 352 | 329.5 | 305.3 | 401.5
1003 | 841 | 522.1 | 346.3 | 346.5 | 339.1 | 352.1 | 329.6 | 305.4 | 401.5
1004 | 842 | 522.1 | 346.5 | 346.6 | 339.2 | 352.2 | 329.7 | 305.5 | 401.6
1005 | 843 | 522.1 | 346.6 | 346.7 | 339.3 | 352.3 | 329.7 | 305.6 | 401.7
1006 | 844 | 522 | 346.7 | 346.8 | 339.4 | 352.4 | 329.8 | 305.7 | 401.8
1007 | 845 | 521.8 | 346.8 | 346.9 | 339.5 | 352.6 | 329.9 | 305.8 | 401.8
1008 | 846 | 521.7 | 346.9 | 347.1 | 339.6 | 352.7 | 329.9 | 305.9 | 401.8
1009 | 847 | 521.8 | 347 | 347.2 | 339.7 | 352.7 | 330 | 306 | 401.9
1010 | 848 | 521.8 | 347.1 | 347.3 | 339.8 | 352.9 | 330.1 | 306.1 | 401.9
1011 | 849 | 521.8 | 347.2 | 347.5 | 339.9 | 353 | 330.2 | 306.2 | 401.9
1012 | 850 | 521.7 | 347.3 | 347.6 | 340 | 353.1 | 330.3 | 306.3 | 402
1013 | 851 | 521.4 | 347.5 | 347.7 | 340.1 | 353.2 | 330.4 | 306.5 | 402
1014 | 852 | 521.2 | 347.6 | 347.8 | 340.2 | 353.3 | 330.5 | 306.6 | 402.1
1015 | 853 | 521.2 | 347.7 | 347.9 | 340.4 | 353.5 | 330.6 | 306.7 | 402.2
1016 | 854 | 521.2 | 347.8 | 348.1 | 340.5 | 353.6 | 330.7 | 306.8 | 402.2
1017 | 855 | 521.2 | 348 | 348.2 | 340.6 | 353.7 | 330.8 | 306.8 | 402.2
1018 | 856 | 521.2 | 348.1 | 348.3 | 340.7 | 353.8 | 330.8 | 306.9 | 402.2
1019 | 857 | 521.3 | 348.2 | 348.5 | 340.8 | 354 | 331 | 307 | 402.2
1020 | 858 | 521.3 | 348.3 | 348.6 | 340.9 | 354.1 | 331 | 307.1 | 402.2
1021 | 859 | 521.3 | 348.4 | 348.8 | 341 | 354.2 | 331.1 | 307.1 | 402.2
1022 | 860 | 520.9 | 348.5 | 349 | 341.1 | 354.2 | 331.3 | 307.2 | 402.2
1023 | 861 | 521 | 348.6 | 349.2 | 341.1 | 354.2 | 331.4 | 307.3 | 402.3
1024 | 862 | 521 | 348.7 | 349.4 | 341.2 | 354.3 | 331.6 | 307.4 | 402.3
1025 | 863 | 521.1 | 348.8 | 349.5 | 341.3 | 354.4 | 331.7 | 307.6 | 402.3
1026 | 864 | 521.4 | 348.9 | 349.6 | 341.4 | 354.6 | 331.8 | 307.7 | 402.3
1027 | 865 | 521.7 | 349 | 349.8 | 341.5 | 354.7 | 331.9 | 307.8 | 402.3
1028 | 866 | 522 | 349.2 | 349.9 | 341.6 | 354.9 | 332.1 | 307.9 | 402.3
1029 | 867 | 522.3 | 349.3 | 350 | 341.7 | 355 | 332.2 | 308 | 402.4
1030 | 868 | 522.4 | 349.4 | 350.2 | 341.8 | 355.1 | 332.3 | 308.2 | 402.5
1031 | 869 | 522.5 | 349.5 | 350.3 | 341.9 | 355.2 | 332.4 | 308.3 | 402.5
1032 | 870 | 522.3 | 349.6 | 350.4 | 342 | 355.4 | 332.6 | 308.4 | 402.6
1033 | 871 | 522.2 | 349.8 | 350.5 | 342.1 | 355.5 | 332.7 | 308.5 | 402.6
1034 | 872 | 522.3 | 349.9 | 350.6 | 342.2 | 355.7 | 332.8 | 308.6 | 402.7
1035 | 873 | 522.3 | 350 | 350.8 | 342.3 | 355.8 | 332.9 | 308.7 | 402.7
1036 | 874 | 522.4 | 350.2 | 350.9 | 342.4 | 356 | 333 | 308.8 | 402.7
1037 | 875 | 522.5 | 350.3 | 351 | 342.5 | 356.1 | 333.2 | 308.8 | 402.7
1038 | 876 | 522.6 | 350.4 | 351.1 | 342.6 | 356.2 | 333.3 | 308.9 | 402.8
1039 | 877 | 522.5 | 350.6 | 351.3 | 342.7 | 356.4 | 333.4 | 309 | 402.8
1040 | 878 | 522.2 | 350.7 | 351.4 | 342.8 | 356.5 | 333.5 | 309.1 | 402.8
1041 | 879 | 522.2 | 350.9 | 351.5 | 342.9 | 356.7 | 333.6 | 309.2 | 402.9
1042 | 880 | 522.3 | 351 | 351.7 | 343 | 356.8 | 333.7 | 309.2 | 402.9
1043 | 881 | 522.2 | 351.1 | 351.8 | 343.1 | 357 | 333.8 | 309.3 | 402.9
1044 | 882 | 522.2 | 351.3 | 351.9 | 343.2 | 357.2 | 333.9 | 309.4 | 402.9
1045 | 883 | 522.2 | 351.4 | 352 | 343.3 | 357.3 | 334.1 | 309.5 | 403
1046 | 884 | 521.9 | 351.5 | 352.2 | 343.4 | 357.5 | 334.2 | 309.6 | 403
1047 | 885 | 521.7 | 351.7 | 352.3 | 343.5 | 357.7 | 334.3 | 309.6 | 403
1048 | 886 | 521.8 | 351.8 | 352.4 | 343.6 | 357.9 | 334.5 | 309.7 | 403
1049 | 887 | 521.9 | 352 | 352.5 | 343.7 | 358 | 334.6 | 309.9 | 403
1050 | 888 | 522 | 352.1 | 352.7 | 343.8 | 358.2 | 334.8 | 310 | 403.1
1051 | 889 | 521.9 | 352.3 | 352.8 | 343.9 | 358.4 | 334.9 | 310 | 403.1
1052 | 890 | 521.9 | 352.4 | 352.9 | 344 | 358.6 | 335 | 310.1 | 403.1
1053 | 891 | 521.9 | 352.6 | 353.1 | 344.1 | 358.8 | 335.2 | 310.2 | 403
1054 | 892 | 521.7 | 352.7 | 353.2 | 344.1 | 359 | 335.3 | 310.3 | 403.1
1055 | 893 | 521.9 | 352.9 | 353.3 | 344.2 | 359.2 | 335.4 | 310.3 | 403.1
1056 | 894 | 521.8 | 353 | 353.5 | 344.3 | 359.3 | 335.5 | 310.4 | 403.1
1057 | 895 | 521.7 | 353.2 | 353.6 | 344.4 | 359.5 | 335.7 | 310.5 | 403.1
1058 | 896 | 521.8 | 353.3 | 353.8 | 344.5 | 359.8 | 335.8 | 310.7 | 403.2
1059 | 897 | 521.8 | 353.5 | 353.9 | 344.6 | 360 | 335.9 | 310.8 | 403.2
1060 | 898 | 521.9 | 353.6 | 354 | 344.7 | 360.1 | 336 | 310.9 | 403.3
1061 | 899 | 522 | 353.8 | 354.2 | 344.8 | 360.3 | 336.1 | 311 | 403.3
1062 | 900 | 522.1 | 353.9 | 354.3 | 344.9 | 360.6 | 336.2 | 311.1 | 403.4
1063 | 901 | 522.4 | 354.1 | 354.5 | 345 | 360.8 | 336.3 | 311.2 | 403.4
1064 | 902 | 522.4 | 354.2 | 354.6 | 345.1 | 361 | 336.3 | 311.3 | 403.4
1065 | 903 | 522.4 | 354.4 | 354.7 | 345.2 | 361.2 | 336.4 | 311.4 | 403.5
1066 | 904 | 522.5 | 354.6 | 354.9 | 345.3 | 361.4 | 336.4 | 311.4 | 403.6
1067 | 905 | 522.4 | 354.7 | 355.1 | 345.4 | 361.7 | 336.4 | 311.5 | 403.6
1068 | 906 | 522.5 | 354.9 | 355.2 | 345.4 | 361.9 | 336.4 | 311.6 | 403.6
1069 | 907 | 522.7 | 355.1 | 355.4 | 345.5 | 362.1 | 336.4 | 311.6 | 403.6
1070 | 908 | 522.6 | 355.3 | 355.5 | 345.6 | 362.3 | 336.5 | 311.6 | 403.6
1071 | 909 | 522.5 | 355.4 | 355.7 | 345.7 | 362.6 | 336.5 | 311.7 | 403.7
1072 | 910 | 522.2 | 355.6 | 355.8 | 345.8 | 362.8 | 336.6 | 311.7 | 403.7
1073 | 911 | 522.1 | 355.8 | 356 | 345.9 | 363.1 | 336.6 | 311.8 | 403.7
1074 | 912 | 522.1 | 355.9 | 356.2 | 346 | 363.3 | 336.7 | 311.9 | 403.7
1075 | 913 | 522 | 356.1 | 356.3 | 346.1 | 363.6 | 336.7 | 311.9 | 403.8
1076 | 914 | 521.9 | 356.3 | 356.5 | 346.2 | 363.9 | 336.8 | 312 | 403.8
1077 | 915 | 521.7 | 356.5 | 356.6 | 346.3 | 364.2 | 336.9 | 312.1 | 403.9
1078 | 916 | 521.7 | 356.7 | 356.8 | 346.4 | 364.4 | 337 | 312.1 | 403.9
1079 | 917 | 521.6 | 356.9 | 356.9 | 346.5 | 364.7 | 337.1 | 312.2 | 404
1080 | 918 | 521.6 | 357.1 | 357.1 | 346.6 | 365 | 337.2 | 312.3 | 404.1
1081 | 919 | 521.6 | 357.3 | 357.3 | 346.6 | 365.2 | 337.3 | 312.3 | 404.1
1082 | 920 | 521.5 | 357.5 | 357.4 | 346.7 | 365.5 | 337.3 | 312.4 | 404.1
1083 | 921 | 521.5 | 357.7 | 357.6 | 346.8 | 365.8 | 337.4 | 312.5 | 404.2
1084 | 922 | 521.4 | 357.9 | 357.7 | 346.9 | 366.1 | 337.4 | 312.5 | 404.2
1085 | 923 | 521.5 | 358.1 | 357.9 | 347 | 366.4 | 337.5 | 312.6 | 404.3
1086 | 924 | 521.6 | 358.3 | 358.1 | 347.1 | 366.6 | 337.6 | 312.7 | 404.3
1087 | 925 | 521.8 | 358.5 | 358.2 | 347.2 | 366.9 | 337.6 | 312.7 | 404.4
1088 | 926 | 521.9 | 358.7 | 358.4 | 347.3 | 367.2 | 337.7 | 312.8 | 404.5
1089 | 927 | 522.2 | 358.9 | 358.5 | 347.4 | 367.4 | 337.8 | 312.8 | 404.5
1090 | 928 | 522.2 | 359.1 | 358.7 | 347.5 | 367.7 | 337.9 | 312.9 | 404.5
1091 | 929 | 522.1 | 359.3 | 358.8 | 347.6 | 368 | 338 | 313 | 404.6
1092 | 930 | 522.2 | 359.6 | 359 | 347.7 | 368.2 | 338.1 | 313.1 | 404.6
1093 | 931 | 522.2 | 359.8 | 359.2 | 347.8 | 368.5 | 338.2 | 313.1 | 404.7
1094 | 932 | 522.1 | 360 | 359.3 | 347.9 | 368.8 | 338.3 | 313.1 | 404.8
1095 | 933 | 522.1 | 360.2 | 359.5 | 348.1 | 369 | 338.4 | 313.1 | 404.8
1096 | 934 | 522.1 | 360.5 | 359.6 | 348.2 | 369.2 | 338.5 | 313.1 | 404.9
1097 | 935 | 522.4 | 360.7 | 359.8 | 348.3 | 369.5 | 338.7 | 313.2 | 405
1098 | 936 | 522.8 | 360.9 | 360 | 348.4 | 369.7 | 338.8 | 313.3 | 405.1
1099 | 937 | 523.1 | 361.1 | 360.1 | 348.5 | 369.9 | 338.9 | 313.4 | 405.1
1100 | 938 | 523.1 | 361.4 | 360.3 | 348.6 | 370.1 | 339 | 313.5 | 405.2
1101 | 939 | 523.1 | 361.6 | 360.4 | 348.7 | 370.3 | 339 | 313.6 | 405.2
1102 | 940 | 523.2 | 361.8 | 360.6 | 348.8 | 370.5 | 339.1 | 313.7 | 405.3
1103 | 941 | 523.2 | 362.1 | 360.7 | 349 | 370.7 | 339.2 | 313.8 | 405.3
1104 | 942 | 523.1 | 362.3 | 360.9 | 349.1 | 370.9 | 339.3 | 313.9 | 405.4
1105 | 943 | 523.1 | 362.6 | 361.1 | 349.2 | 371.1 | 339.4 | 314 | 405.5
1106 | 944 | 522.9 | 362.8 | 361.2 | 349.3 | 371.3 | 339.5 | 314.1 | 405.6
1107 | 945 | 523 | 363.1 | 361.4 | 349.5 | 371.5 | 339.5 | 314.2 | 405.7
1108 | 946 | 522.7 | 363.3 | 361.5 | 349.6 | 371.7 | 339.6 | 314.2 | 405.8
1109 | 947 | 522.6 | 363.6 | 361.7 | 349.7 | 371.9 | 339.7 | 314.3 | 405.8
1110 | 948 | 522.6 | 363.8 | 361.8 | 349.8 | 372 | 339.7 | 314.4 | 405.9
1111 | 949 | 522.6 | 364 | 362 | 350 | 372.2 | 339.8 | 314.5 | 406
1112 | 950 | 522.3 | 364.3 | 362.2 | 350.1 | 372.4 | 339.9 | 314.5 | 406
1113 | 951 | 522.4 | 364.6 | 362.4 | 350.3 | 372.6 | 339.9 | 314.6 | 406.1
1114 | 952 | 522.4 | 364.8 | 362.5 | 350.4 | 372.7 | 340 | 314.7 | 406.2
1115 | 953 | 522.4 | 365.1 | 362.7 | 350.5 | 372.9 | 340.1 | 314.8 | 406.3
1116 | 954 | 522.4 | 365.3 | 362.9 | 350.7 | 373.1 | 340.2 | 314.9 | 406.4
1117 | 955 | 522.4 | 365.6 | 363.1 | 350.8 | 373.2 | 340.3 | 315 | 406.4
1118 | 956 | 522.5 | 365.9 | 363.2 | 351 | 373.4 | 340.4 | 315 | 406.5
1119 | 957 | 522.4 | 366.2 | 363.4 | 351.1 | 373.5 | 340.5 | 315.1 | 406.6
1120 | 958 | 522.4 | 366.4 | 363.6 | 351.3 | 373.7 | 340.5 | 315.1 | 406.6
1121 | 959 | 522.4 | 366.7 | 363.8 | 351.4 | 373.8 | 340.6 | 315.2 | 406.6
1122 | 960 | 522.4 | 367 | 363.9 | 351.6 | 374 | 340.7 | 315.3 | 406.6
1123 | 961 | 522.4 | 367.3 | 364.1 | 351.7 | 374.1 | 340.8 | 315.4 | 406.7
1124 | 962 | 522.3 | 367.6 | 364.2 | 351.9 | 374.2 | 340.9 | 315.4 | 406.8
1125 | 963 | 522.2 | 367.8 | 364.4 | 352 | 374.4 | 341 | 315.5 | 406.9
1126 | 964 | 522.1 | 368.1 | 364.6 | 352.2 | 374.5 | 341 | 315.5 | 406.9
1127 | 965 | 522.1 | 368.4 | 364.8 | 352.3 | 374.5 | 341 | 315.5 | 407
1128 | 966 | 522.2 | 368.7 | 364.9 | 352.5 | 374.6 | 341.1 | 315.6 | 407.2
1129 | 967 | 522 | 369 | 365.1 | 352.7 | 374.7 | 341.2 | 315.6 | 407.2
1130 | 968 | 521.6 | 369.3 | 365.3 | 352.8 | 374.9 | 341.2 | 315.7 | 407.3
1131 | 969 | 521.4 | 369.6 | 365.5 | 353 | 375 | 341.2 | 315.8 | 407.3
1132 | 970 | 521.1 | 369.8 | 365.7 | 353.1 | 375.1 | 341.2 | 315.9 | 407.4
1133 | 971 | 520.6 | 370.1 | 365.8 | 353.3 | 375.2 | 341.3 | 315.9 | 407.5
1134 | 972 | 520.6 | 370.4 | 366 | 353.5 | 375.4 | 341.3 | 316 | 407.5
1135 | 973 | 520.8 | 370.7 | 366.2 | 353.6 | 375.5 | 341.3 | 316 | 407.6
1136 | 974 | 520.9 | 371 | 366.4 | 353.8 | 375.5 | 341.3 | 316.1 | 407.8
1137 | 975 | 520.7 | 371.2 | 366.6 | 353.9 | 375.6 | 341.3 | 316.1 | 407.8
1138 | 976 | 520.7 | 371.5 | 366.8 | 354.1 | 375.7 | 341.4 | 316.2 | 407.9
1139 | 977 | 521 | 371.8 | 366.9 | 354.3 | 375.8 | 341.4 | 316.2 | 408
1140 | 978 | 521.2 | 372.1 | 367.1 | 354.4 | 375.9 | 341.4 | 316.3 | 408
1141 | 979 | 521.1 | 372.4 | 367.3 | 354.6 | 376 | 341.4 | 316.3 | 408.1
1142 | 980 | 520.8 | 372.6 | 367.5 | 354.8 | 376.1 | 341.4 | 316.3 | 408.2
1143 | 981 | 520.7 | 372.9 | 367.7 | 354.9 | 376.2 | 341.4 | 316.3 | 408.3
1144 | 982 | 520.8 | 373.2 | 367.9 | 355.1 | 376.2 | 341.5 | 316.4 | 408.3
1145 | 983 | 520.8 | 373.4 | 368 | 355.3 | 376.3 | 341.5 | 316.4 | 408.4
1146 | 984 | 520.9 | 373.7 | 368.2 | 355.4 | 376.4 | 341.5 | 316.5 | 408.4
1147 | 985 | 521.1 | 373.9 | 368.4 | 355.6 | 376.5 | 341.5 | 316.5 | 408.5
1148 | 986 | 521.2 | 374.2 | 368.6 | 355.8 | 376.5 | 341.5 | 316.6 | 408.6
1149 | 987 | 521.3 | 374.5 | 368.8 | 355.9 | 376.6 | 341.5 | 316.6 | 408.7
1150 | 988 | 521.3 | 374.7 | 369 | 356.1 | 376.7 | 341.5 | 316.6 | 408.9
1151 | 989 | 521.3 | 375 | 369.2 | 356.3 | 376.8 | 341.5 | 316.7 | 408.9
1152 | 990 | 521.4 | 375.2 | 369.3 | 356.4 | 376.9 | 341.5 | 316.7 | 409
1153 | 991 | 521.4 | 375.5 | 369.5 | 356.6 | 376.9 | 341.5 | 316.7 | 409.1
1154 | 992 | 521.6 | 375.7 | 369.7 | 356.8 | 377 | 341.6 | 316.8 | 409.2
1155 | 993 | 521.8 | 376 | 369.9 | 356.9 | 377.1 | 341.6 | 316.9 | 409.2
1156 | 994 | 521.9 | 376.2 | 370.1 | 357.1 | 377.2 | 341.7 | 317 | 409.3
1157 | 995 | 522.1 | 376.4 | 370.3 | 357.3 | 377.2 | 341.7 | 317.1 | 409.4
1158 | 996 | 522.2 | 376.7 | 370.5 | 357.5 | 377.3 | 341.7 | 317.2 | 409.5
1159 | 997 | 522.3 | 376.9 | 370.6 | 357.6 | 377.4 | 341.8 | 317.4 | 409.6
1160 | 998 | 522.3 | 377.1 | 370.8 | 357.8 | 377.5 | 341.8 | 317.5 | 409.7
1161 | 999 | 522.1 | 377.3 | 371 | 358 | 377.6 | 341.8 | 317.6 | 409.8
1162 | 1000 | 522 | 377.6 | 371.2 | 358.2 | 377.7 | 341.9 | 317.6 | 409.9
1163 | 1001 | 521.9 | 377.8 | 371.4 | 358.3 | 377.9 | 341.9 | 317.7 | 410
1164 | 1002 | 521.9 | 378 | 371.5 | 358.5 | 378 | 341.9 | 317.7 | 410.1
1165 | 1003 | 521.9 | 378.3 | 371.7 | 358.7 | 378.2 | 342 | 317.8 | 410.2
1166 | 1004 | 521.8 | 378.5 | 371.9 | 358.9 | 378.3 | 342 | 317.8 | 410.4
1167 | 1005 | 521.7 | 378.7 | 372 | 359.1 | 378.4 | 342 | 317.8 | 410.4
1168 | 1006 | 521.5 | 378.9 | 372.2 | 359.2 | 378.6 | 342.1 | 317.8 | 410.5
1169 | 1007 | 521.3 | 379.1 | 372.5 | 359.4 | 378.6 | 342.1 | 317.8 | 410.6
1170 | 1008 | 521.2 | 379.3 | 372.7 | 359.6 | 378.7 | 342.2 | 317.9 | 410.6
1171 | 1009 | 521.4 | 379.6 | 372.8 | 359.8 | 378.8 | 342.2 | 317.9 | 410.7
1172 | 1010 | 521.5 | 379.8 | 373 | 359.9 | 378.9 | 342.3 | 318 | 410.8
1173 | 1011 | 521.4 | 380 | 373.2 | 360.1 | 379.1 | 342.3 | 318.1 | 410.9
1174 | 1012 | 521.2 | 380.2 | 373.4 | 360.3 | 379.2 | 342.3 | 318.2 | 411
1175 | 1013 | 521 | 380.4 | 373.5 | 360.4 | 379.3 | 342.4 | 318.3 | 411.1
1176 | 1014 | 520.9 | 380.6 | 373.7 | 360.6 | 379.4 | 342.4 | 318.4 | 411.2
1177 | 1015 | 520.8 | 380.8 | 373.9 | 360.8 | 379.4 | 342.4 | 318.4 | 411.3
1178 | 1016 | 521.1 | 381 | 374.1 | 360.9 | 379.5 | 342.4 | 318.5 | 411.4
1179 | 1017 | 521.3 | 381.2 | 374.3 | 361.1 | 379.6 | 342.4 | 318.6 | 411.5
1180 | 1018 | 521.3 | 381.5 | 374.4 | 361.2 | 379.7 | 342.4 | 318.6 | 411.6
1181 | 1019 | 521.4 | 381.7 | 374.6 | 361.4 | 379.9 | 342.4 | 318.7 | 411.7
1182 | 1020 | 521.7 | 381.9 | 374.8 | 361.5 | 380 | 342.5 | 318.6 | 411.8
1183 | 1021 | 521.7 | 382.1 | 375 | 361.7 | 380.1 | 342.5 | 318.6 | 411.9
1184 | 1022 | 521.8 | 382.3 | 375.1 | 361.8 | 380.2 | 342.5 | 318.6 | 412
1185 | 1023 | 522.1 | 382.5 | 375.3 | 362 | 380.3 | 342.5 | 318.7 | 412.1
1186 | 1024 | 522.2 | 382.7 | 375.5 | 362.1 | 380.4 | 342.5 | 318.7 | 412.2
1187 | 1025 | 522.4 | 382.9 | 375.7 | 362.3 | 380.6 | 342.5 | 318.7 | 412.3
1188 | 1026 | 522.5 | 383.1 | 375.9 | 362.4 | 380.7 | 342.6 | 318.7 | 412.4
1189 | 1027 | 522.7 | 383.4 | 376.1 | 362.6 | 380.9 | 342.6 | 318.7 | 412.5
1190 | 1028 | 522.7 | 383.6 | 376.3 | 362.7 | 381 | 342.6 | 318.8 | 412.6
1191 | 1029 | 522.7 | 383.8 | 376.4 | 362.9 | 381.2 | 342.7 | 318.8 | 412.7
1192 | 1030 | 522.7 | 384 | 376.6 | 363 | 381.4 | 342.7 | 318.8 | 412.8
1193 | 1031 | 522.9 | 384.2 | 376.8 | 363.2 | 381.5 | 342.7 | 318.9 | 412.9
1194 | 1032 | 523 | 384.4 | 377 | 363.3 | 381.7 | 342.8 | 318.9 | 413
1195 | 1033 | 522.9 | 384.6 | 377.2 | 363.5 | 381.9 | 342.8 | 318.9 | 413.1
1196 | 1034 | 522.8 | 384.8 | 377.3 | 363.6 | 382 | 342.9 | 319 | 413.2
1197 | 1035 | 522.7 | 385 | 377.5 | 363.8 | 382.2 | 342.9 | 319 | 413.2
1198 | 1036 | 522.6 | 385.2 | 377.7 | 363.9 | 382.4 | 343 | 319.1 | 413.4
1199 | 1037 | 522.5 | 385.5 | 377.8 | 364 | 382.5 | 343 | 319.1 | 413.5
1200 | 1038 | 522.2 | 385.7 | 378 | 364.2 | 382.6 | 343 | 319.2 | 413.6
1201 | 1039 | 522 | 385.9 | 378.2 | 364.3 | 382.8 | 343.1 | 319.2 | 413.6
1202 | 1040 | 521.8 | 386.1 | 378.4 | 364.5 | 382.9 | 343.1 | 319.2 | 413.8
1203 | 1041 | 521.8 | 386.4 | 378.5 | 364.6 | 383.1 | 343.2 | 319.3 | 413.9
1204 | 1042 | 521.8 | 386.6 | 378.7 | 364.7 | 383.3 | 343.2 | 319.3 | 414
1205 | 1043 | 521.7 | 386.9 | 378.8 | 364.9 | 383.6 | 343.3 | 319.4 | 414
1206 | 1044 | 521.6 | 387.1 | 379 | 365 | 383.7 | 343.3 | 319.5 | 414
1207 | 1045 | 521.6 | 387.3 | 379.2 | 365.1 | 383.9 | 343.3 | 319.5 | 414.1
1208 | 1046 | 521.4 | 387.6 | 379.3 | 365.2 | 384.1 | 343.3 | 319.6 | 414.1
1209 | 1047 | 521.6 | 387.8 | 379.5 | 365.3 | 384.3 | 343.4 | 319.7 | 414.2
1210 | 1048 | 521.4 | 388.1 | 379.6 | 365.5 | 384.6 | 343.4 | 319.7 | 414.2
1211 | 1049 | 521.2 | 388.4 | 379.8 | 365.6 | 384.7 | 343.5 | 319.8 | 414.3
1212 | 1050 | 521.2 | 388.6 | 380 | 365.7 | 385 | 343.5 | 319.8 | 414.4
1213 | 1051 | 521.1 | 388.8 | 380.1 | 365.8 | 385.2 | 343.6 | 319.9 | 414.5
1214 | 1052 | 521.1 | 389.1 | 380.3 | 365.9 | 385.4 | 343.6 | 320 | 414.6
1215 | 1053 | 521 | 389.3 | 380.5 | 366 | 385.6 | 343.6 | 320.1 | 414.6
1216 | 1054 | 521.1 | 389.6 | 380.6 | 366.1 | 385.9 | 343.7 | 320.1 | 414.7
1217 | 1055 | 521.1 | 389.9 | 380.8 | 366.2 | 386.1 | 343.7 | 320.2 | 414.8
1218 | 1056 | 521.1 | 390.1 | 380.9 | 366.3 | 386.4 | 343.8 | 320.3 | 414.9
1219 | 1057 | 521.3 | 390.4 | 381.1 | 366.4 | 386.6 | 343.8 | 320.3 | 415
1220 | 1058 | 521.3 | 390.7 | 381.2 | 366.5 | 386.9 | 343.9 | 320.4 | 415.1
1221 | 1059 | 521.4 | 390.9 | 381.4 | 366.6 | 387.2 | 344 | 320.5 | 415.2
1222 | 1060 | 521.6 | 391.2 | 381.6 | 366.7 | 387.4 | 344.1 | 320.6 | 415.4
1223 | 1061 | 521.8 | 391.4 | 381.7 | 366.8 | 387.7 | 344.1 | 320.6 | 415.4
1224 | 1062 | 522.1 | 391.7 | 381.9 | 366.9 | 387.9 | 344.2 | 320.7 | 415.6
1225 | 1063 | 522.2 | 392 | 382.1 | 367 | 388.2 | 344.3 | 320.8 | 415.7
1226 | 1064 | 522.4 | 392.3 | 382.2 | 367.1 | 388.4 | 344.4 | 320.8 | 415.7
1227 | 1065 | 522.6 | 392.5 | 382.4 | 367.1 | 388.7 | 344.5 | 320.9 | 415.8
1228 | 1066 | 522.7 | 392.8 | 382.6 | 367.2 | 389 | 344.5 | 320.9 | 415.9
1229 | 1067 | 522.7 | 393.1 | 382.7 | 367.3 | 389.2 | 344.6 | 321 | 416
1230 | 1068 | 522.6 | 393.3 | 382.9 | 367.4 | 389.4 | 344.7 | 321 | 416
1231 | 1069 | 522.6 | 393.6 | 383.1 | 367.5 | 389.6 | 344.8 | 321.1 | 416.1
1232 | 1070 | 522.9 | 393.9 | 383.2 | 367.5 | 389.8 | 344.8 | 321.1 | 416.2
1233 | 1071 | 523.2 | 394.2 | 383.4 | 367.6 | 390 | 344.9 | 321.1 | 416.2
1234 | 1072 | 523.2 | 394.4 | 383.6 | 367.7 | 390.2 | 344.9 | 321.1 | 416.3
1235 | 1073 | 523.2 | 394.7 | 383.8 | 367.8 | 390.3 | 345 | 321.2 | 416.4
1236 | 1074 | 523.1 | 395 | 383.9 | 367.8 | 390.6 | 345 | 321.2 | 416.5
1237 | 1075 | 522.9 | 395.3 | 384.1 | 367.9 | 390.8 | 345.1 | 321.3 | 416.6
1238 | 1076 | 522.5 | 395.5 | 384.3 | 368 | 391 | 345.1 | 321.3 | 416.7
1239 | 1077 | 522 | 395.8 | 384.4 | 368.1 | 391.3 | 345.1 | 321.4 | 416.8
1240 | 1078 | 521.7 | 396.1 | 384.6 | 368.1 | 391.5 | 345.2 | 321.4 | 416.9
1241 | 1079 | 521.6 | 396.4 | 384.8 | 368.2 | 391.8 | 345.2 | 321.5 | 417
1242 | 1080 | 521.5 | 396.6 | 384.9 | 368.3 | 392 | 345.2 | 321.5 | 417.1
1243 | 1081 | 521.4 | 396.9 | 385.1 | 368.3 | 392.2 | 345.2 | 321.5 | 417.2
1244 | 1082 | 521.4 | 397.2 | 385.3 | 368.4 | 392.5 | 345.3 | 321.5 | 417.2
1245 | 1083 | 521.4 | 397.5 | 385.5 | 368.5 | 392.7 | 345.3 | 321.5 | 417.3
1246 | 1084 | 521.3 | 397.8 | 385.7 | 368.5 | 393 | 345.2 | 321.5 | 417.4
1247 | 1085 | 521.3 | 398 | 385.9 | 368.6 | 393.2 | 345.2 | 321.5 | 417.4
1248 | 1086 | 521.3 | 398.3 | 386.1 | 368.7 | 393.5 | 345.2 | 321.5 | 417.5
1249 | 1087 | 521.4 | 398.5 | 386.3 | 368.7 | 393.8 | 345.3 | 321.5 | 417.6
1250 | 1088 | 521.6 | 398.8 | 386.5 | 368.8 | 394 | 345.3 | 321.6 | 417.7
1251 | 1089 | 522 | 399.1 | 386.7 | 368.9 | 394.3 | 345.3 | 321.6 | 417.8
1252 | 1090 | 522 | 399.4 | 386.9 | 368.9 | 394.5 | 345.3 | 321.7 | 417.8
1253 | 1091 | 521.8 | 399.6 | 387.1 | 369 | 394.8 | 345.3 | 321.7 | 417.9
1254 | 1092 | 521.9 | 399.9 | 387.3 | 369.1 | 395.1 | 345.3 | 321.8 | 418
1255 | 1093 | 521.9 | 400.1 | 387.5 | 369.1 | 395.3 | 345.3 | 321.9 | 418.1
1256 | 1094 | 522 | 400.4 | 387.7 | 369.2 | 395.6 | 345.3 | 321.9 | 418.2
1257 | 1095 | 522 | 400.7 | 387.9 | 369.3 | 395.8 | 345.3 | 322 | 418.3
1258 | 1096 | 522.1 | 401 | 388.1 | 369.4 | 396.1 | 345.3 | 322 | 418.4
1259 | 1097 | 521.9 | 401.2 | 388.3 | 369.4 | 396.4 | 345.3 | 322 | 418.6
1260 | 1098 | 521.8 | 401.5 | 388.5 | 369.5 | 396.7 | 345.3 | 322 | 418.7
1261 | 1099 | 522 | 401.8 | 388.7 | 369.6 | 397 | 345.3 | 322 | 418.8
1262 | 1100 | 522 | 402.1 | 388.9 | 369.7 | 397.3 | 345.2 | 322 | 418.9
1263 | 1101 | 522.1 | 402.4 | 389.2 | 369.7 | 397.6 | 345.2 | 322.1 | 419
1264 | 1102 | 522.2 | 402.7 | 389.4 | 369.8 | 397.9 | 345.2 | 322 | 419.1
1265 | 1103 | 522.2 | 402.9 | 389.6 | 369.9 | 398.1 | 345.1 | 322 | 419.2
1266 | 1104 | 522.1 | 403.2 | 389.8 | 370 | 398.4 | 345.1 | 322.1 | 419.3
1267 | 1105 | 522 | 403.5 | 390 | 370.1 | 398.7 | 345.1 | 322.1 | 419.4
1268 | 1106 | 521.9 | 403.7 | 390.2 | 370.2 | 399 | 345 | 322.2 | 419.4
1269 | 1107 | 521.8 | 404 | 390.4 | 370.2 | 399.3 | 345 | 322.3 | 419.6
1270 | 1108 | 521.8 | 404.2 | 390.6 | 370.3 | 399.6 | 345 | 322.3 | 419.6
1271 | 1109 | 521.8 | 404.5 | 390.9 | 370.4 | 399.9 | 345 | 322.3 | 419.7
1272 | 1110 | 521.7 | 404.8 | 391.1 | 370.5 | 400.2 | 344.9 | 322.4 | 419.8
1273 | 1111 | 521.7 | 405 | 391.3 | 370.6 | 400.4 | 344.9 | 322.4 | 420
1274 | 1112 | 521.7 | 405.3 | 391.5 | 370.7 | 400.7 | 344.9 | 322.4 | 420.1
1275 | 1113 | 521.8 | 405.5 | 391.7 | 370.8 | 400.9 | 344.9 | 322.4 | 420.2
1276 | 1114 | 521.8 | 405.8 | 392 | 370.9 | 401.2 | 344.9 | 322.4 | 420.3
1277 | 1115 | 521.7 | 406.1 | 392.2 | 371 | 401.5 | 344.9 | 322.4 | 420.5
1278 | 1116 | 521.6 | 406.3 | 392.4 | 371.1 | 401.8 | 344.9 | 322.3 | 420.6
1279 | 1117 | 521.7 | 406.6 | 392.6 | 371.2 | 402.1 | 344.9 | 322.3 | 420.7
1280 | 1118 | 521.8 | 406.9 | 392.9 | 371.3 | 402.4 | 344.9 | 322.3 | 420.8
1281 | 1119 | 522.1 | 407.1 | 393.1 | 371.4 | 402.7 | 344.9 | 322.3 | 420.9
1282 | 1120 | 522.3 | 407.4 | 393.3 | 371.6 | 403.1 | 345 | 322.3 | 421
1283 | 1121 | 522.2 | 407.7 | 393.5 | 371.7 | 403.4 | 345 | 322.3 | 421
1284 | 1122 | 522 | 408 | 393.8 | 371.8 | 403.7 | 345 | 322.2 | 421.1
1285 | 1123 | 522.1 | 408.3 | 394 | 371.9 | 404 | 345.1 | 322.2 | 421.1
1286 | 1124 | 522.2 | 408.6 | 394.2 | 372 | 404.4 | 345.1 | 322.2 | 421.2
1287 | 1125 | 522.2 | 408.8 | 394.5 | 372.1 | 404.7 | 345.2 | 322.3 | 421.3
1288 | 1126 | 522.2 | 409.1 | 394.7 | 372.2 | 405.1 | 345.3 | 322.3 | 421.4
1289 | 1127 | 522.2 | 409.4 | 394.9 | 372.4 | 405.4 | 345.3 | 322.4 | 421.4
1290 | 1128 | 522.2 | 409.7 | 395.1 | 372.5 | 405.8 | 345.4 | 322.4 | 421.5
1291 | 1129 | 522.4 | 409.9 | 395.4 | 372.6 | 406.1 | 345.5 | 322.5 | 421.6
1292 | 1130 | 522.3 | 410.2 | 395.6 | 372.7 | 406.4 | 345.5 | 322.6 | 421.7
1293 | 1131 | 522.4 | 410.5 | 395.8 | 372.8 | 406.7 | 345.6 | 322.7 | 421.7
1294 | 1132 | 522.6 | 410.7 | 396.1 | 372.9 | 407 | 345.6 | 322.7 | 421.9
1295 | 1133 | 522.7 | 411 | 396.3 | 373.1 | 407.2 | 345.6 | 322.7 | 422
1296 | 1134 | 522.4 | 411.3 | 396.5 | 373.2 | 407.5 | 345.7 | 322.7 | 422
1297 | 1135 | 522.2 | 412.8 | 394 | 374.2 | 410 | 346.3 | 322.6 | 421.9
1298 | 1136 | 522.3 | 411.9 | 397 | 373.4 | 408.1 | 345.8 | 322.7 | 422.2
1299 | 1137 | 522.2 | 412.2 | 397.2 | 373.6 | 408.4 | 345.9 | 322.8 | 422.2
1300 | 1138 | 522.1 | 412.4 | 397.5 | 373.7 | 408.8 | 345.9 | 322.8 | 422.2
1301 | 1139 | 521.8 | 412.7 | 397.7 | 373.8 | 409.1 | 345.9 | 322.9 | 422.1
1302 | 1140 | 521.6 | 413 | 397.9 | 374 | 409.5 | 346 | 322.9 | 422.3
1303 | 1141 | 521.4 | 413.3 | 398.2 | 374.1 | 409.8 | 346.1 | 323 | 422.4
1304 | 1142 | 521.3 | 413.6 | 398.4 | 374.2 | 410.1 | 346.1 | 323.1 | 422.5
1305 | 1143 | 521.4 | 413.8 | 398.6 | 374.3 | 410.5 | 346.2 | 323.2 | 422.6
1306 | 1144 | 521.3 | 414.1 | 398.9 | 374.5 | 410.8 | 346.2 | 323.2 | 422.7
1307 | 1145 | 521 | 414.4 | 399.1 | 374.6 | 411.1 | 346.3 | 323.3 | 422.7
1308 | 1146 | 520.6 | 414.7 | 399.4 | 374.7 | 411.4 | 346.3 | 323.3 | 422.9
1309 | 1147 | 520.4 | 415 | 399.6 | 374.9 | 411.6 | 346.4 | 323.3 | 423
1310 | 1148 | 520.3 | 415.3 | 399.8 | 375 | 411.9 | 346.4 | 323.3 | 423.1
1311 | 1149 | 520.2 | 415.6 | 400 | 375.1 | 412.2 | 346.5 | 323.3 | 423.2
1312 | 1150 | 520.1 | 415.9 | 400.3 | 375.3 | 412.5 | 346.5 | 323.3 | 423.2
1313 | 1151 | 519.9 | 416.2 | 400.5 | 375.4 | 412.7 | 346.5 | 323.3 | 423.2
1314 | 1152 | 519.8 | 416.5 | 400.8 | 375.5 | 413 | 346.5 | 323.3 | 423.3
1315 | 1153 | 519.8 | 416.7 | 401 | 375.7 | 413.3 | 346.5 | 323.3 | 423.4
1316 | 1154 | 519.8 | 417 | 401.3 | 375.8 | 413.6 | 346.6 | 323.3 | 423.5
1317 | 1155 | 519.9 | 417.3 | 401.5 | 375.9 | 414 | 346.6 | 323.4 | 423.6
1318 | 1156 | 519.9 | 417.6 | 401.7 | 376.1 | 414.3 | 346.6 | 323.4 | 423.6
1319 | 1157 | 520 | 417.9 | 402 | 376.2 | 414.6 | 346.7 | 323.4 | 423.7
1320 | 1158 | 520.1 | 418.1 | 402.3 | 376.4 | 414.8 | 346.7 | 323.5 | 423.8
1321 | 1159 | 520.2 | 418.4 | 402.6 | 376.5 | 415.1 | 346.7 | 323.5 | 423.8
1322 | 1160 | 520.4 | 418.7 | 402.8 | 376.6 | 415.4 | 346.7 | 323.5 | 423.9
1323 | 1161 | 520.4 | 419 | 403.1 | 376.8 | 415.7 | 346.8 | 323.5 | 424
1324 | 1162 | 520.6 | 419.3 | 403.3 | 376.9 | 416 | 346.8 | 323.6 | 424.1
1325 | 1163 | 520.8 | 419.6 | 403.6 | 377.1 | 416.4 | 346.8 | 323.6 | 424.2
1326 | 1164 | 521.2 | 419.9 | 403.7 | 377.3 | 416.9 | 346.8 | 323.7 | 424.2
1327 | 1165 | 521.2 | 420.2 | 403.8 | 377.5 | 417.3 | 346.8 | 323.7 | 424.3
1328 | 1166 | 521.3 | 420.4 | 404.4 | 377.5 | 417.4 | 346.8 | 323.8 | 424.4
1329 | 1167 | 521.3 | 420.6 | 404.6 | 377.6 | 417.8 | 346.8 | 323.9 | 424.5
1330 | 1168 | 521.4 | 420.9 | 404.9 | 377.8 | 418.2 | 346.9 | 324 | 424.6
1331 | 1169 | 521.6 | 421.2 | 405.1 | 377.9 | 418.6 | 346.9 | 324 | 424.8
1332 | 1170 | 521.7 | 421.5 | 405.4 | 378.1 | 418.9 | 346.9 | 324.1 | 424.9
1333 | 1171 | 521.8 | 421.8 | 405.6 | 378.2 | 419.3 | 346.9 | 324.2 | 425
1334 | 1172 | 521.9 | 422 | 405.9 | 378.4 | 419.6 | 347 | 324.3 | 425.1
1335 | 1173 | 521.9 | 422.3 | 406.2 | 378.5 | 419.9 | 347 | 324.4 | 425.2
1336 | 1174 | 522 | 422.6 | 406.4 | 378.7 | 420.2 | 347 | 324.4 | 425.4
1337 | 1175 | 522.1 | 422.9 | 406.7 | 378.8 | 420.5 | 347 | 324.5 | 425.5
1338 | 1176 | 522.2 | 423.2 | 406.9 | 379 | 420.8 | 347.1 | 324.5 | 425.6
1339 | 1177 | 522.4 | 423.5 | 407.2 | 379.1 | 421.1 | 347.1 | 324.6 | 425.7
1340 | 1178 | 522.4 | 423.8 | 407.5 | 379.3 | 421.3 | 347.1 | 324.6 | 425.8
1341 | 1179 | 522.4 | 424 | 407.7 | 379.4 | 421.6 | 347.2 | 324.6 | 425.9
1342 | 1180 | 522.4 | 424.3 | 408 | 379.6 | 421.8 | 347.2 | 324.7 | 426
1343 | 1181 | 522.3 | 424.6 | 408.3 | 379.8 | 422.1 | 347.2 | 324.7 | 426
1344 | 1182 | 522.3 | 424.9 | 408.6 | 379.9 | 422.4 | 347.2 | 324.7 | 426.1
1345 | 1183 | 522.2 | 425.1 | 408.8 | 380.1 | 422.6 | 347.3 | 324.7 | 426.2
1346 | 1184 | 522.2 | 425.4 | 409.1 | 380.2 | 422.9 | 347.3 | 324.7 | 426.4
1347 | 1185 | 522 | 425.7 | 409.4 | 380.4 | 423.2 | 347.3 | 324.7 | 426.4
1348 | 1186 | 521.7 | 426 | 409.6 | 380.5 | 423.6 | 347.3 | 324.7 | 426.5
1349 | 1187 | 521.5 | 426.3 | 409.9 | 380.7 | 423.9 | 347.3 | 324.7 | 426.6
1350 | 1188 | 521.3 | 426.5 | 410.2 | 380.9 | 424.3 | 347.3 | 324.7 | 426.7
1351 | 1189 | 521.1 | 426.8 | 410.4 | 381 | 424.7 | 347.3 | 324.8 | 426.8
1352 | 1190 | 520.8 | 427.1 | 410.7 | 381.2 | 425 | 347.3 | 324.8 | 426.9
1353 | 1191 | 520.6 | 427.4 | 411 | 381.4 | 425.4 | 347.4 | 324.9 | 427
1354 | 1192 | 520.4 | 427.6 | 411.2 | 381.5 | 425.8 | 347.4 | 324.9 | 427.1
1355 | 1193 | 520.4 | 427.9 | 411.5 | 381.7 | 426.2 | 347.4 | 325 | 427.3
1356 | 1194 | 520.3 | 428.1 | 411.8 | 381.9 | 426.6 | 347.4 | 325 | 427.4
1357 | 1195 | 520.5 | 428.4 | 412 | 382 | 426.9 | 347.5 | 325.1 | 427.5
1358 | 1196 | 520.7 | 428.7 | 412.3 | 382.2 | 427.3 | 347.5 | 325.2 | 427.6
1359 | 1197 | 520.8 | 428.9 | 412.6 | 382.3 | 427.6 | 347.5 | 325.2 | 427.7
1360 | 1198 | 521 | 429.2 | 412.8 | 382.5 | 428 | 347.5 | 325.3 | 427.7
1361 | 1199 | 521.1 | 429.5 | 413.1 | 382.7 | 428.4 | 347.5 | 325.4 | 427.8
1362 | 1200 | 521.3 | 429.8 | 413.4 | 382.9 | 428.7 | 347.5 | 325.5 | 427.9
1363 | 1201 | 521.3 | 430 | 413.7 | 383 | 429 | 347.5 | 325.5 | 428
1364 | 1202 | 521.4 | 430.3 | 413.9 | 383.2 | 429.3 | 347.6 | 325.6 | 428
1365 | 1203 | 521.6 | 430.6 | 414.2 | 383.4 | 429.6 | 347.6 | 325.7 | 428.1
1366 | 1204 | 521.9 | 430.8 | 414.5 | 383.5 | 430 | 347.6 | 325.7 | 428.2
1367 | 1205 | 522 | 431.1 | 414.8 | 383.7 | 430.3 | 347.7 | 325.8 | 428.3
1368 | 1206 | 522.2 | 431.4 | 415.1 | 383.9 | 430.7 | 347.7 | 325.9 | 428.5
1369 | 1207 | 522.2 | 431.7 | 415.3 | 384.1 | 431 | 347.8 | 325.9 | 428.6
1370 | 1208 | 522.4 | 431.9 | 415.6 | 384.2 | 431.3 | 347.8 | 326 | 428.8
1371 | 1209 | 522.6 | 432.2 | 415.9 | 384.4 | 431.6 | 347.8 | 326 | 428.9
1372 | 1210 | 522.7 | 432.5 | 416.2 | 384.6 | 432 | 347.9 | 326.1 | 429.1
1373 | 1211 | 522.8 | 432.7 | 416.5 | 384.7 | 432.4 | 347.9 | 326.2 | 429.2
1374 | 1212 | 522.8 | 433 | 416.8 | 384.9 | 432.8 | 348 | 326.3 | 429.3
1375 | 1213 | 523 | 433.3 | 417.1 | 385.1 | 433.2 | 348 | 326.4 | 429.4
1376 | 1214 | 523 | 433.5 | 417.4 | 385.3 | 433.7 | 348 | 326.4 | 429.5
1377 | 1215 | 523 | 433.8 | 417.7 | 385.4 | 434.1 | 348.1 | 326.4 | 429.5
1378 | 1216 | 522.8 | 434.1 | 417.9 | 385.6 | 434.6 | 348.2 | 326.4 | 429.6
1379 | 1217 | 522.7 | 434.3 | 418.2 | 385.8 | 435.1 | 348.2 | 326.5 | 429.7
1380 | 1218 | 522.7 | 434.6 | 418.5 | 386 | 435.6 | 348.3 | 326.6 | 429.8
1381 | 1219 | 522.7 | 434.8 | 418.8 | 386.1 | 436.1 | 348.3 | 326.6 | 429.9
1382 | 1220 | 522.7 | 435.1 | 419.1 | 386.3 | 436.6 | 348.4 | 326.7 | 430.1
1383 | 1221 | 522.8 | 435.3 | 419.4 | 386.5 | 437.1 | 348.5 | 326.7 | 430.2
1384 | 1222 | 522.8 | 435.6 | 419.6 | 386.7 | 437.5 | 348.5 | 326.8 | 430.3
1385 | 1223 | 522.7 | 435.8 | 419.9 | 386.9 | 438 | 348.6 | 326.9 | 430.5
1386 | 1224 | 522.7 | 436.1 | 420.2 | 387 | 438.4 | 348.6 | 326.9 | 430.6
1387 | 1225 | 522.6 | 436.4 | 420.4 | 387.2 | 438.9 | 348.7 | 326.9 | 430.8
1388 | 1226 | 522.6 | 436.6 | 420.7 | 387.4 | 439.3 | 348.8 | 327 | 430.9
1389 | 1227 | 522.6 | 436.9 | 421 | 387.6 | 439.8 | 348.8 | 326.9 | 431
1390 | 1228 | 522.5 | 437.2 | 421.3 | 387.8 | 440.2 | 348.9 | 326.9 | 431.1
1391 | 1229 | 522.3 | 437.4 | 421.5 | 388 | 440.7 | 348.9 | 326.8 | 431.3
1392 | 1230 | 522 | 437.7 | 421.8 | 388.1 | 441.2 | 349 | 326.8 | 431.4
1393 | 1231 | 521.8 | 437.9 | 422.1 | 388.3 | 441.7 | 349 | 326.8 | 431.5
1394 | 1232 | 521.6 | 438.2 | 422.3 | 388.5 | 442.2 | 349.1 | 326.8 | 431.6
1395 | 1233 | 521.5 | 438.4 | 422.6 | 388.7 | 442.6 | 349.1 | 326.8 | 431.8
1396 | 1234 | 521.3 | 438.7 | 422.9 | 388.9 | 443.1 | 349.2 | 326.8 | 431.8
1397 | 1235 | 521.1 | 439 | 423.2 | 389.1 | 443.6 | 349.3 | 326.9 | 431.9
1398 | 1236 | 521.1 | 439.2 | 423.4 | 389.2 | 444.1 | 349.3 | 326.9 | 432
1399 | 1237 | 520.9 | 439.5 | 423.7 | 389.4 | 444.6 | 349.4 | 326.9 | 432.2
1400 | 1238 | 520.9 | 439.7 | 424 | 389.6 | 445.1 | 349.5 | 327 | 432.3
1401 | 1239 | 520.9 | 440 | 424.2 | 389.8 | 445.6 | 349.5 | 327 | 432.4
1402 | 1240 | 520.9 | 440.3 | 424.5 | 390 | 446.2 | 349.6 | 327 | 432.6
1403 | 1241 | 521 | 440.5 | 424.8 | 390.2 | 446.7 | 349.6 | 327.1 | 432.8
1404 | 1242 | 521.1 | 440.8 | 425 | 390.4 | 447.3 | 349.7 | 327.1 | 432.9
1405 | 1243 | 521.1 | 441 | 425.3 | 390.5 | 447.9 | 349.7 | 327.1 | 433
1406 | 1244 | 521 | 441.3 | 425.5 | 390.7 | 448.4 | 349.8 | 327.2 | 433.1
1407 | 1245 | 521 | 441.6 | 425.8 | 390.9 | 448.9 | 349.8 | 327.2 | 433.2
1408 | 1246 | 521 | 441.8 | 426.1 | 391.1 | 449.4 | 349.9 | 327.2 | 433.3
1409 | 1247 | 521.1 | 442.1 | 426.3 | 391.3 | 449.8 | 349.9 | 327.2 | 433.5
1410 | 1248 | 521.2 | 442.4 | 426.6 | 391.5 | 450.3 | 350 | 327.2 | 433.7
1411 | 1249 | 521.5 | 442.7 | 426.9 | 391.6 | 450.8 | 350.1 | 327.2 | 433.8
1412 | 1250 | 521.8 | 442.9 | 427.1 | 391.8 | 451.2 | 350.1 | 327.2 | 434
1413 | 1251 | 522 | 443.2 | 427.4 | 392 | 451.7 | 350.2 | 327.3 | 434.1
1414 | 1252 | 522.1 | 443.5 | 427.6 | 392.2 | 452.2 | 350.2 | 327.4 | 434.3
1415 | 1253 | 522.2 | 443.7 | 427.9 | 392.4 | 452.6 | 350.3 | 327.4 | 434.4
1416 | 1254 | 522.2 | 444 | 428.1 | 392.6 | 453.1 | 350.3 | 327.5 | 434.6
1417 | 1255 | 522.3 | 444.2 | 428.4 | 392.7 | 453.7 | 350.4 | 327.5 | 434.8
1418 | 1256 | 522.4 | 444.6 | 428.7 | 392.9 | 454.2 | 350.4 | 327.5 | 435
1419 | 1257 | 522.4 | 444.9 | 429 | 393.1 | 454.7 | 350.5 | 327.5 | 435.1
1420 | 1258 | 522.5 | 445.1 | 429.2 | 393.3 | 455.4 | 350.6 | 327.4 | 435.2
1421 | 1259 | 522.5 | 445.4 | 429.4 | 393.5 | 456 | 350.7 | 327.4 | 435.4
1422 | 1260 | 522.5 | 445.6 | 429.6 | 393.7 | 456.6 | 350.7 | 327.4 | 435.6
1423 | 1261 | 522.7 | 445.8 | 429.7 | 393.9 | 457.2 | 350.8 | 327.4 | 435.8
1424 | 1262 | 522.8 | 446 | 429.8 | 394.1 | 457.8 | 350.9 | 327.4 | 436
1425 | 1263 | 522.7 | 446.2 | 430 | 394.3 | 458.4 | 350.9 | 327.4 | 436.3
1426 | 1264 | 522.6 | 446.4 | 430.1 | 394.5 | 459.1 | 351 | 327.5 | 436.6
1427 | 1265 | 522.6 | 446.6 | 430.3 | 394.7 | 459.9 | 351.1 | 327.6 | 437
1428 | 1266 | 522.6 | 446.9 | 430.5 | 394.8 | 460.6 | 351.2 | 327.7 | 437.5
1429 | 1267 | 522.6 | 447.1 | 430.6 | 395 | 461.3 | 351.3 | 327.8 | 438.1
1430 | 1268 | 522.5 | 447.5 | 430.7 | 395.1 | 462 | 351.4 | 327.8 | 438.6
1431 | 1269 | 522.6 | 448 | 430.8 | 395.2 | 462.7 | 351.5 | 327.9 | 439.2
1432 | 1270 | 522.6 | 448.4 | 430.9 | 395.4 | 463.4 | 351.7 | 328 | 439.8
1433 | 1271 | 522.7 | 448.9 | 431.1 | 395.5 | 464.1 | 351.7 | 328.2 | 440.4
1434 | 1272 | 522.7 | 449.2 | 431.2 | 395.7 | 464.7 | 351.8 | 328.4 | 441
1435 | 1273 | 522.7 | 449.5 | 431.3 | 395.9 | 465.2 | 351.9 | 328.7 | 441.6
1436 | 1274 | 522.7 | 449.9 | 431.5 | 396.2 | 465.6 | 352 | 329 | 442.3
1437 | 1275 | 522.7 | 450.2 | 431.6 | 396.4 | 466 | 352.1 | 329.4 | 442.9
1438 | 1276 | 522.5 | 450.5 | 431.6 | 396.7 | 466.6 | 352.2 | 329.8 | 443.6
1439 | 1277 | 522.4 | 450.7 | 431.9 | 397 | 467.1 | 352.3 | 330.2 | 444.4
1440 | 1278 | 522.2 | 451.2 | 432 | 397.2 | 467.7 | 352.4 | 330.7 | 445.2
1441 | 1279 | 522.1 | 451.5 | 432.1 | 397.5 | 468.2 | 352.5 | 331.3 | 446
1442 | 1280 | 522 | 451.8 | 432.3 | 397.7 | 468.8 | 352.6 | 332 | 446.9
1443 | 1281 | 521.9 | 452.3 | 432.5 | 398 | 469.3 | 352.6 | 332.8 | 447.8
1444 | 1282 | 521.7 | 452.6 | 432.6 | 398.3 | 469.9 | 352.6 | 333.7 | 448.7
1445 | 1283 | 521.7 | 452.8 | 432.7 | 398.5 | 470.5 | 352.7 | 334.7 | 449.6
1446 | 1284 | 521.4 | 453.1 | 432.8 | 398.8 | 471 | 352.8 | 335.7 | 450.5
1447 | 1285 | 521.1 | 453.4 | 433 | 399 | 471.6 | 352.9 | 336.7 | 451.4
1448 | 1286 | 520.8 | 453.8 | 433.1 | 399.3 | 472.2 | 353 | 337.8 | 452.4
1449 | 1287 | 520.6 | 454.1 | 433.3 | 399.6 | 472.9 | 353.1 | 338.9 | 453.3
1450 | 1288 | 520.5 | 454.5 | 433.5 | 399.8 | 473.5 | 353.2 | 340 | 454.3
1451 | 1289 | 520.4 | 454.9 | 433.7 | 400.1 | 474.1 | 353.3 | 341.1 | 455.2
1452 | 1290 | 520.5 | 455.5 | 433.8 | 400.5 | 474.9 | 353.4 | 342.3 | 456.2
1453 | 1291 | 520.6 | 455.9 | 434 | 400.7 | 475.5 | 353.5 | 343.6 | 457.1
1454 | 1292 | 520.7 | 456.2 | 434.4 | 401 | 476 | 353.6 | 344.8 | 458
1455 | 1293 | 520.6 | 456.5 | 434.7 | 401.2 | 476.6 | 353.7 | 346 | 459.1
1456 | 1294 | 520.7 | 456.6 | 435.2 | 401.4 | 476.8 | 353.8 | 347.3 | 460.1
1457 | 1295 | 520.5 | 456.8 | 435.6 | 401.6 | 477.3 | 353.9 | 348.5 | 461.2
1458 | 1296 | 520.1 | 457.1 | 435.9 | 401.8 | 477.8 | 354 | 349.7 | 462.2
1459 | 1297 | 519.7 | 457.3 | 436.1 | 402.1 | 478.5 | 354.1 | 350.8 | 463.2
1460 | 1298 | 519 | 457.7 | 436.4 | 402.3 | 479.2 | 354.2 | 351.9 | 464.1
1461 | 1299 | 518.3 | 458.1 | 436.5 | 402.7 | 480.1 | 354.4 | 353 | 465
1462 | 1300 | 517.6 | 458.4 | 436.9 | 402.8 | 480.7 | 354.5 | 354 | 465.9
1463 | 1301 | 516.9 | 458.8 | 437.1 | 403.1 | 481.4 | 354.6 | 355 | 466.9
1464 | 1302 | 516.3 | 459.2 | 437.4 | 403.4 | 482.2 | 354.8 | 355.8 | 467.8
1465 | 1303 | 515.4 | 459.6 | 437.7 | 403.7 | 483 | 354.8 | 356.6 | 468.7
1466 | 1304 | 514.5 | 460 | 438 | 403.9 | 483.8 | 354.9 | 357.3 | 469.7
1467 | 1305 | 513.5 | 460.4 | 438.3 | 404.2 | 484.5 | 355 | 358 | 470.6
1468 | 1306 | 512.5 | 460.7 | 438.6 | 404.4 | 485.3 | 355.1 | 358.6 | 471.6
1469 | 1307 | 511.5 | 461.1 | 438.8 | 404.7 | 486.1 | 355.3 | 359.1 | 472.6
1470 | 1308 | 510.4 | 461.5 | 439.1 | 405 | 486.8 | 355.4 | 359.6 | 473.5
1471 | 1309 | 509.2 | 461.8 | 439.5 | 405.3 | 487.5 | 355.5 | 359.9 | 474.4
1472 | 1310 | 508.1 | 462.2 | 439.7 | 405.5 | 488.2 | 355.7 | 360.2 | 475.2
1473 | 1311 | 506.9 | 462.6 | 440.1 | 405.8 | 489 | 355.8 | 360.5 | 476.1
1474 | 1312 | 505.9 | 462.9 | 440.4 | 406 | 489.7 | 355.9 | 360.8 | 477
1475 | 1313 | 504.9 | 463.3 | 440.7 | 406.3 | 490.5 | 356 | 361.1 | 477.9
1476 | 1314 | 503.9 | 463.6 | 441 | 406.5 | 491.2 | 356.1 | 361.3 | 478.9
1477 | 1315 | 502.8 | 464 | 441.4 | 406.8 | 492 | 356.2 | 361.5 | 479.7
1478 | 1316 | 501.6 | 464.4 | 441.7 | 407 | 492.7 | 356.3 | 361.7 | 480.6
1479 | 1317 | 500.4 | 464.7 | 442 | 407.3 | 493.4 | 356.5 | 361.8 | 481.5
1480 | 1318 | 499.5 | 465 | 442.4 | 407.5 | 494.1 | 356.5 | 362 | 482.4
1481 | 1319 | 498.4 | 465.4 | 442.7 | 407.8 | 494.8 | 356.6 | 362.2 | 483.2
1482 | 1320 | 497.4 | 465.7 | 443.1 | 408 | 495.6 | 356.7 | 362.3 | 484.1
1483 | 1321 | 496.2 | 466 | 443.4 | 408.2 | 496.4 | 356.8 | 362.5 | 485.1
1484 | 1322 | 495 | 466.3 | 443.7 | 408.5 | 497.3 | 356.9 | 362.6 | 486.1
1485 | 1323 | 493.9 | 466.6 | 444 | 408.7 | 498.1 | 356.9 | 362.8 | 486.9
1486 | 1324 | 492.7 | 467 | 444.4 | 409 | 498.9 | 356.9 | 362.9 | 487.5
1487 | 1325 | 491.7 | 467.3 | 444.7 | 409.2 | 499.8 | 357 | 363.1 | 488
1488 | 1326 | 490.6 | 467.6 | 445.1 | 409.4 | 500.5 | 357 | 363.3 | 488.5
1489 | 1327 | 489.6 | 468 | 445.5 | 409.8 | 501.4 | 357.1 | 363.5 | 489
1490 | 1328 | 488.6 | 468.4 | 445.9 | 410 | 502.3 | 357.2 | 363.7 | 489.4
1491 | 1329 | 487.8 | 468.8 | 446.2 | 410.2 | 503.2 | 357.2 | 363.9 | 489.7
1492 | 1330 | 486.7 | 469.2 | 446.5 | 410.5 | 504 | 357.3 | 364 | 490
1493 | 1331 | 485.4 | 469.5 | 446.8 | 410.7 | 504.9 | 357.2 | 364.1 | 490.2
1494 | 1332 | 484.4 | 469.9 | 447.2 | 411 | 505.8 | 357.2 | 364.2 | 490.5
1495 | 1333 | 483.3 | 470.2 | 447.5 | 411.2 | 506.7 | 357.2 | 364.3 | 490.8
1496 | 1334 | 482.3 | 470.6 | 447.9 | 411.4 | 507.6 | 357.2 | 364.3 | 491.1
1497 | 1335 | 481.2 | 471 | 448.2 | 411.7 | 508.6 | 357.2 | 364.3 | 491.4
1498 | 1336 | 480.1 | 471.3 | 448.6 | 412 | 509.5 | 357.3 | 364.3 | 491.6
1499 | 1337 | 479.1 | 471.7 | 449 | 412.3 | 510.4 | 357.3 | 364.3 | 491.9
1500 | 1338 | 477.9 | 472.1 | 449.3 | 412.5 | 511.3 | 357.3 | 364.3 | 492.1
1501 | 1339 | 476.7 | 472.5 | 449.7 | 412.7 | 512.2 | 357.4 | 364.2 | 492.3
1502 | 1340 | 475.6 | 472.9 | 450 | 412.9 | 513.2 | 357.4 | 364.1 | 492.5
1503 | 1341 | 474.4 | 473.3 | 450.4 | 413.2 | 514.2 | 357.5 | 364 | 492.7
1504 | 1342 | 473.3 | 473.6 | 450.7 | 413.4 | 515.2 | 357.6 | 363.9 | 492.9
1505 | 1343 | 472.3 | 474 | 451 | 413.6 | 516.2 | 357.6 | 363.8 | 493.1
1506 | 1344 | 471.5 | 474.5 | 451.3 | 413.8 | 517.2 | 357.7 | 363.7 | 493.2
1507 | 1345 | 470.7 | 474.9 | 451.7 | 414.1 | 518.3 | 357.7 | 363.5 | 493.4
1508 | 1346 | 469.8 | 475.3 | 452 | 414.3 | 519.5 | 357.7 | 363.4 | 493.5
1509 | 1347 | 468.7 | 475.6 | 452.4 | 414.5 | 520.6 | 357.7 | 363.2 | 493.7
1510 | 1348 | 467.7 | 476.1 | 452.8 | 414.8 | 521.7 | 357.8 | 363.1 | 493.9
1511 | 1349 | 466.7 | 476.4 | 453.2 | 415 | 522.7 | 357.8 | 363 | 494
1512 | 1350 | 465.7 | 476.7 | 453.5 | 415.3 | 523.8 | 357.9 | 362.9 | 494.1
1513 | 1351 | 464.7 | 477.1 | 453.9 | 415.5 | 524.9 | 358 | 362.7 | 494.3
1514 | 1352 | 463.5 | 477.5 | 454.3 | 415.8 | 526 | 358.1 | 362.6 | 494.5
1515 | 1353 | 462.4 | 477.9 | 454.6 | 416 | 527.1 | 358.2 | 362.5 | 494.7
1516 | 1354 | 461.4 | 478.2 | 455 | 416.2 | 528.2 | 358.5 | 362.3 | 494.9
1517 | 1355 | 460.4 | 478.6 | 455.4 | 416.5 | 529.3 | 358.6 | 362.1 | 495.1
1518 | 1356 | 459.6 | 478.9 | 455.7 | 416.7 | 530.4 | 358.8 | 362 | 495.3
1519 | 1357 | 458.7 | 479.2 | 456.1 | 417 | 531.5 | 359.1 | 361.9 | 495.4
1520 | 1358 | 457.9 | 479.5 | 456.5 | 417.2 | 532.5 | 359.4 | 361.9 | 495.6
1521 | 1359 | 456.9 | 479.8 | 456.9 | 417.4 | 533.6 | 359.6 | 362 | 495.6
1522 | 1360 | 456 | 480.2 | 457.3 | 417.7 | 534.6 | 359.7 | 362.1 | 495.7
1523 | 1361 | 455.1 | 480.5 | 457.6 | 418 | 535.6 | 359.8 | 362.2 | 495.8
1524 | 1362 | 454.3 | 480.8 | 458.1 | 418.2 | 536.6 | 360.1 | 362.2 | 495.8
1525 | 1363 | 453.3 | 481.1 | 458.4 | 418.5 | 537.6 | 360.3 | 362.3 | 495.9
1526 | 1364 | 452.2 | 481.4 | 458.8 | 418.7 | 538.7 | 360.5 | 362.4 | 496
1527 | 1365 | 451.1 | 481.7 | 459.2 | 419 | 539.7 | 360.6 | 362.3 | 496
1528 | 1366 | 450.3 | 482 | 459.6 | 419.2 | 540.8 | 360.8 | 362.3 | 496.1
1529 | 1367 | 449.5 | 482.4 | 460 | 419.5 | 541.8 | 360.9 | 362.3 | 496.1
1530 | 1368 | 448.5 | 482.7 | 460.4 | 419.8 | 542.9 | 361 | 362.2 | 496.1
1531 | 1369 | 447.5 | 483 | 460.9 | 420 | 544 | 361.2 | 362.1 | 496.1
1532 | 1370 | 446.7 | 483.3 | 461.3 | 420.3 | 545.1 | 361.3 | 362.1 | 496.1
1533 | 1371 | 445.9 | 483.7 | 461.7 | 420.5 | 546.2 | 361.3 | 362.1 | 496.2
1534 | 1372 | 445 | 484 | 462.2 | 420.8 | 547.3 | 361.4 | 362.1 | 496.2
1535 | 1373 | 444 | 484.2 | 462.6 | 421 | 548.3 | 361.5 | 362 | 496.3
1536 | 1374 | 443.2 | 484.5 | 463 | 421.3 | 549.4 | 361.5 | 362 | 496.3
1537 | 1375 | 442.4 | 484.7 | 463.5 | 421.5 | 550.4 | 361.6 | 362 | 496.3
1538 | 1376 | 441.5 | 485 | 463.9 | 421.8 | 551.4 | 361.7 | 362 | 496.3
1539 | 1377 | 440.6 | 485.3 | 464.4 | 422.1 | 552.4 | 361.7 | 362 | 496.4
1540 | 1378 | 439.6 | 485.6 | 464.9 | 422.4 | 553.4 | 361.6 | 362 | 496.5
1541 | 1379 | 438.8 | 485.9 | 465.3 | 422.7 | 554.3 | 361.6 | 362 | 496.5
1542 | 1380 | 438.1 | 486.1 | 465.7 | 422.9 | 555.3 | 361.6 | 362 | 496.5
1543 | 1381 | 437.3 | 486.3 | 466.1 | 423.2 | 556.2 | 361.7 | 362 | 496.7
1544 | 1382 | 436.3 | 486.7 | 466.6 | 423.5 | 557.2 | 361.7 | 362 | 496.9
1545 | 1383 | 435.6 | 486.9 | 467.1 | 423.8 | 558.1 | 361.8 | 362.1 | 497
1546 | 1384 | 434.8 | 487.2 | 467.6 | 424 | 559 | 361.8 | 362.1 | 497.2
1547 | 1385 | 433.7 | 487.4 | 468 | 424.4 | 559.9 | 362 | 362.2 | 497.2
1548 | 1386 | 432.8 | 487.7 | 468.5 | 424.6 | 560.7 | 362 | 362.2 | 497.2
1549 | 1387 | 431.9 | 487.9 | 469 | 424.9 | 561.4 | 362 | 362.3 | 497.2
1550 | 1388 | 431 | 488.2 | 469.4 | 425.2 | 562.3 | 362.1 | 362.4 | 497.2
1551 | 1389 | 430.2 | 488.4 | 469.9 | 425.5 | 563 | 362.2 | 362.5 | 497.2
1552 | 1390 | 429.2 | 488.7 | 470.4 | 425.8 | 563.7 | 362.3 | 362.6 | 497.2
1553 | 1391 | 428.2 | 488.9 | 470.9 | 426.1 | 564.5 | 362.3 | 362.6 | 497.1
1554 | 1392 | 427.2 | 489.2 | 471.4 | 426.4 | 565.3 | 362.3 | 362.7 | 497.1
1555 | 1393 | 426.4 | 489.5 | 471.9 | 426.7 | 566 | 362.4 | 362.8 | 497.1
1556 | 1394 | 425.7 | 489.7 | 472.4 | 427 | 566.7 | 362.6 | 362.9 | 497.1
1557 | 1395 | 424.9 | 489.9 | 472.9 | 427.3 | 567.4 | 362.8 | 363 | 497.1
1558 | 1396 | 424.2 | 490.1 | 473.4 | 427.6 | 568 | 362.9 | 363.2 | 497
1559 | 1397 | 423.4 | 490.3 | 473.9 | 427.9 | 568.5 | 363.1 | 363.4 | 496.9
1560 | 1398 | 422.5 | 490.5 | 474.4 | 428.2 | 569.1 | 363.4 | 363.6 | 496.9
1561 | 1399 | 421.6 | 490.7 | 474.9 | 428.5 | 569.7 | 363.5 | 363.8 | 496.8
1562 | 1400 | 420.8 | 491 | 475.4 | 428.8 | 570.2 | 363.7 | 364 | 496.7
1563 | 1401 | 420.2 | 491.2 | 475.9 | 429.2 | 570.7 | 363.8 | 364.2 | 496.6
1564 | 1402 | 419.5 | 491.3 | 476.4 | 429.5 | 571.1 | 364 | 364.4 | 496.5
1565 | 1403 | 418.8 | 491.5 | 476.8 | 429.8 | 571.6 | 364.1 | 364.7 | 496.4
1566 | 1404 | 418 | 491.7 | 477.3 | 430.1 | 572 | 364.2 | 364.9 | 496.5
1567 | 1405 | 417.2 | 492 | 477.8 | 430.5 | 572.6 | 364.3 | 365.1 | 496.5
1568 | 1406 | 416.5 | 492.2 | 478.3 | 430.8 | 573.1 | 364.4 | 365.4 | 496.5
1569 | 1407 | 415.7 | 492.4 | 478.8 | 431.1 | 573.5 | 364.5 | 365.7 | 496.5
1570 | 1408 | 414.9 | 492.7 | 479.3 | 431.5 | 573.9 | 364.6 | 366 | 496.6
1571 | 1409 | 414 | 493 | 479.8 | 431.8 | 574.3 | 364.6 | 366.3 | 496.7
1572 | 1410 | 413.2 | 493.3 | 480.2 | 432.2 | 574.5 | 364.7 | 366.6 | 496.7
1573 | 1411 | 412.5 | 493.5 | 480.7 | 432.6 | 574.8 | 364.8 | 367 | 496.6
1574 | 1412 | 411.8 | 493.8 | 481.1 | 432.9 | 575.1 | 364.8 | 367.3 | 496.5
1575 | 1413 | 411 | 494 | 481.5 | 433.3 | 575.3 | 364.9 | 367.7 | 496.4
1576 | 1414 | 410.3 | 494.2 | 482 | 433.7 | 575.5 | 364.9 | 368 | 496.4
1577 | 1415 | 409.6 | 494.5 | 482.4 | 434 | 575.7 | 365 | 368.4 | 496.3
1578 | 1416 | 408.9 | 494.7 | 482.9 | 434.4 | 575.9 | 365 | 368.8 | 496.2
1579 | 1417 | 408.1 | 495 | 483.3 | 434.8 | 576.2 | 365 | 369.1 | 496
1580 | 1418 | 407.3 | 495.3 | 483.7 | 435.1 | 576.5 | 365.1 | 369.4 | 495.9
1581 | 1419 | 406.5 | 495.6 | 484.1 | 435.5 | 576.7 | 365.2 | 369.7 | 495.8
1582 | 1420 | 405.8 | 495.9 | 484.5 | 435.9 | 577 | 365.2 | 370 | 495.7
1583 | 1421 | 405 | 496.1 | 484.9 | 436.3 | 577.2 | 365.3 | 370.4 | 495.5
1584 | 1422 | 404.2 | 496.4 | 485.3 | 436.7 | 577.4 | 365.3 | 370.7 | 495.4
1585 | 1423 | 403.4 | 496.7 | 485.6 | 437 | 577.7 | 365.3 | 371 | 495.3
1586 | 1424 | 402.7 | 496.9 | 486 | 437.4 | 578 | 365.3 | 371.3 | 495.2
1587 | 1425 | 401.9 | 497.2 | 486.4 | 437.7 | 578.2 | 365.3 | 371.6 | 495.1
1588 | 1426 | 401 | 497.4 | 486.7 | 438.1 | 578.5 | 365.4 | 371.9 | 495
1589 | 1427 | 400.1 | 497.6 | 487.1 | 438.5 | 578.9 | 365.4 | 372.2 | 494.9
1590 | 1428 | 399.3 | 497.8 | 487.4 | 438.8 | 579.1 | 365.4 | 372.6 | 495
1591 | 1429 | 398.6 | 498 | 487.8 | 439.2 | 579.4 | 365.4 | 372.9 | 495
1592 | 1430 | 397.8 | 498.1 | 488.2 | 439.6 | 579.6 | 365.4 | 373.2 | 494.9
1593 | 1431 | 396.9 | 498.3 | 488.5 | 440 | 579.9 | 365.4 | 373.5 | 494.9
1594 | 1432 | 396.2 | 498.4 | 488.9 | 440.3 | 580.2 | 365.4 | 373.9 | 494.9
1595 | 1433 | 395.5 | 498.6 | 489.2 | 440.7 | 580.5 | 365.4 | 374.2 | 494.8
1596 | 1434 | 395 | 498.8 | 489.5 | 441.1 | 580.7 | 365.4 | 374.5 | 494.7
1597 | 1435 | 394.4 | 499 | 489.8 | 441.5 | 581 | 365.5 | 374.8 | 494.6
1598 | 1436 | 393.6 | 499.1 | 490.2 | 441.9 | 581.2 | 365.5 | 375.2 | 494.4
1599 | 1437 | 392.8 | 499.3 | 490.5 | 442.2 | 581.5 | 365.5 | 375.5 | 494.2
1600 | 1438 | 392.1 | 499.3 | 490.8 | 442.6 | 581.8 | 365.6 | 375.9 | 494.1
1601 | 1439 | 391.3 | 499.5 | 491.1 | 443 | 582.1 | 365.6 | 376.2 | 493.9
1602 | 1440 | 390.5 | 499.6 | 491.4 | 443.4 | 582.4 | 365.6 | 376.6 | 493.8
1603 | 1441 | 389.8 | 499.7 | 491.7 | 443.8 | 582.8 | 365.5 | 376.9 | 493.6
1604 | 1442 | 389 | 499.9 | 492 | 444.1 | 583.2 | 365.5 | 377.2 | 493.4
1605 | 1443 | 388.2 | 500 | 492.2 | 444.5 | 583.6 | 365.5 | 377.6 | 493.1
1606 | 1444 | 387.5 | 500 | 492.5 | 444.9 | 584 | 365.4 | 377.9 | 492.9
1607 | 1445 | 387 | 500.2 | 492.7 | 445.3 | 584.5 | 365.3 | 378.3 | 492.7
1608 | 1446 | 386.4 | 500.3 | 493 | 445.7 | 584.9 | 365.3 | 378.7 | 492.5
1609 | 1447 | 385.7 | 500.4 | 493.3 | 446.1 | 585.4 | 365.3 | 379.1 | 492.3
1610 | 1448 | 385.1 | 500.6 | 493.6 | 446.5 | 585.8 | 365.4 | 379.5 | 492.2
1611 | 1449 | 384.4 | 500.7 | 493.8 | 446.9 | 586.3 | 365.5 | 379.9 | 492.1
1612 | 1450 | 383.7 | 500.8 | 494.1 | 447.3 | 586.9 | 365.6 | 380.4 | 491.9
1613 | 1451 | 382.8 | 500.9 | 494.3 | 447.7 | 587.3 | 365.6 | 380.8 | 491.7
1614 | 1452 | 382 | 501.1 | 494.5 | 448.1 | 587.8 | 365.6 | 381.3 | 491.6
1615 | 1453 | 381.4 | 501.2 | 494.7 | 448.6 | 588.2 | 365.5 | 381.7 | 491.6
1616 | 1454 | 380.5 | 501.4 | 495 | 449 | 588.5 | 365.4 | 382.3 | 491.4
1617 | 1455 | 379.8 | 501.5 | 495.3 | 449.5 | 588.9 | 365.4 | 382.9 | 491.1
1618 | 1456 | 379.2 | 501.6 | 495.5 | 449.9 | 589.3 | 365.4 | 383.5 | 490.8
1619 | 1457 | 378.6 | 501.8 | 495.7 | 450.4 | 589.6 | 365.4 | 384.2 | 490.6
1620 | 1458 | 378 | 501.9 | 495.9 | 450.8 | 589.9 | 365.4 | 384.8 | 490.4
1621 | 1459 | 377.4 | 502 | 496.2 | 451.3 | 590.2 | 365.3 | 385.5 | 490.1
1622 | 1460 | 376.5 | 502.2 | 496.4 | 451.7 | 590.5 | 365.2 | 386.1 | 490.1
1623 | 1461 | 375.8 | 502.3 | 496.7 | 452.2 | 590.7 | 365.1 | 386.8 | 490.4
1624 | 1462 | 375.1 | 502.5 | 496.9 | 452.7 | 591 | 365 | 387.4 | 490.5
1625 | 1463 | 374.2 | 502.6 | 497.1 | 453.2 | 591.2 | 364.8 | 388 | 490.5
1626 | 1464 | 373.6 | 502.8 | 497.4 | 453.6 | 591.2 | 364.7 | 388.7 | 490.5
1627 | 1465 | 373 | 502.9 | 497.6 | 454.1 | 591.3 | 364.5 | 389.3 | 490.4
1628 | 1466 | 372.2 | 503.1 | 497.8 | 454.6 | 591.3 | 364.4 | 389.9 | 490.2
1629 | 1467 | 371.6 | 503.3 | 498.1 | 455.1 | 591.4 | 364.2 | 390.5 | 489.9
1630 | 1468 | 371.2 | 503.5 | 498.4 | 455.6 | 591.4 | 364.1 | 391.1 | 489.6
1631 | 1469 | 370.7 | 503.7 | 498.6 | 456.2 | 591.4 | 364.1 | 391.8 | 489.4
1632 | 1470 | 370.1 | 503.9 | 498.9 | 456.7 | 591.5 | 364.1 | 392.4 | 489.1
1633 | 1471 | 369.4 | 504.1 | 499.1 | 457.2 | 591.5 | 364.1 | 393 | 488.7
1634 | 1472 | 369 | 504.3 | 499.4 | 457.8 | 591.5 | 364 | 393.6 | 488.4
1635 | 1473 | 368.4 | 504.5 | 499.7 | 458.3 | 591.4 | 363.9 | 394.2 | 488.1
1636 | 1474 | 367.8 | 504.7 | 500 | 458.8 | 591.4 | 363.8 | 394.8 | 488
1637 | 1475 | 367.1 | 504.9 | 500.2 | 459.4 | 591.3 | 363.7 | 395.3 | 488.1
1638 | 1476 | 366.5 | 505.1 | 500.4 | 459.9 | 591.1 | 363.5 | 395.8 | 488
1639 | 1477 | 366 | 505.2 | 500.7 | 460.5 | 591.1 | 363.3 | 396.4 | 487.9
1640 | 1478 | 365.6 | 505.4 | 501 | 461 | 591 | 363.2 | 397 | 487.8
1641 | 1479 | 365 | 505.5 | 501.3 | 461.6 | 591 | 363 | 397.5 | 487.6
1642 | 1480 | 364.2 | 505.7 | 501.6 | 462.2 | 591 | 362.8 | 398.1 | 487.4
1643 | 1481 | 363.5 | 505.8 | 501.9 | 462.8 | 591 | 362.6 | 398.6 | 487.1
1644 | 1482 | 362.9 | 506 | 502.3 | 463.3 | 591 | 362.5 | 399.2 | 486.7
1645 | 1483 | 362.3 | 506.1 | 502.6 | 463.9 | 591.1 | 362.3 | 399.8 | 486.4
1646 | 1484 | 361.9 | 506.2 | 502.9 | 464.5 | 591.2 | 362.3 | 400.4 | 486
1647 | 1485 | 361.4 | 506.4 | 503.2 | 465.1 | 591.4 | 362.1 | 401 | 485.8
1648 | 1486 | 360.9 | 506.5 | 503.5 | 465.7 | 591.6 | 362 | 401.6 | 485.6
1649 | 1487 | 360.1 | 506.6 | 503.8 | 466.3 | 591.8 | 362 | 402.1 | 485.3
1650 | 1488 | 359.5 | 506.7 | 504.2 | 466.8 | 591.9 | 362 | 402.7 | 485
1651 | 1489 | 358.9 | 506.8 | 504.5 | 467.4 | 592.1 | 361.9 | 403.3 | 484.8
1652 | 1490 | 358.4 | 506.9 | 504.8 | 468 | 592.2 | 361.8 | 403.9 | 484.5
1653 | 1491 | 357.8 | 507 | 505.1 | 468.5 | 592.3 | 361.6 | 404.5 | 484.2
1654 | 1492 | 357.1 | 507.1 | 505.4 | 469.1 | 592.4 | 361.5 | 405.1 | 483.8
1655 | 1493 | 356.4 | 507.2 | 505.7 | 469.7 | 592.4 | 361.3 | 405.7 | 483.6
1656 | 1494 | 355.9 | 507.3 | 506.1 | 470.3 | 592.5 | 361.1 | 406.3 | 483.4
1657 | 1495 | 355.4 | 507.4 | 506.4 | 470.8 | 592.4 | 360.9 | 406.9 | 483.1
1658 | 1496 | 354.7 | 507.5 | 506.8 | 471.4 | 592.4 | 360.8 | 407.5 | 482.8
1659 | 1497 | 354 | 507.6 | 507.2 | 472 | 592.3 | 360.6 | 408.1 | 482.5
1660 | 1498 | 353.4 | 507.7 | 507.6 | 472.5 | 592.3 | 360.4 | 408.6 | 482.3
1661 | 1499 | 352.8 | 507.9 | 508 | 473.1 | 592.2 | 360.2 | 409.2 | 482
1662 | 1500 | 352.1 | 508 | 508.4 | 473.7 | 592.2 | 360.1 | 409.8 | 481.8
1663 | 1501 | 351.6 | 508.1 | 508.8 | 474.3 | 592.3 | 359.9 | 410.4 | 481.6
1664 | 1502 | 351 | 508.2 | 509.3 | 474.8 | 592.4 | 359.8 | 411 | 481.4
1665 | 1503 | 350.4 | 508.4 | 509.7 | 475.4 | 592.4 | 359.6 | 411.6 | 481.1
1666 | 1504 | 349.9 | 508.5 | 510.1 | 475.9 | 592.4 | 359.4 | 412.1 | 480.7
1667 | 1505 | 349.3 | 508.6 | 510.6 | 476.5 | 592.5 | 359.2 | 412.7 | 480.3
1668 | 1506 | 348.8 | 508.8 | 511 | 477.1 | 592.5 | 359.1 | 413.1 | 479.8
1669 | 1507 | 348.3 | 509 | 511.5 | 477.6 | 592.6 | 359 | 413.5 | 479.3
1670 | 1508 | 347.7 | 509.2 | 512 | 478.1 | 592.6 | 359 | 413.9 | 478.7
1671 | 1509 | 347.2 | 509.3 | 512.5 | 478.7 | 592.7 | 358.9 | 414.3 | 478.2
1672 | 1510 | 346.7 | 509.4 | 513 | 479.2 | 592.8 | 358.7 | 414.6 | 477.6
1673 | 1511 | 346 | 509.6 | 513.5 | 479.8 | 592.9 | 358.6 | 415 | 477.1
1674 | 1512 | 345.5 | 509.8 | 514 | 480.3 | 593 | 358.4 | 415.3 | 476.4
1675 | 1513 | 344.9 | 510 | 514.6 | 480.9 | 593 | 358.3 | 415.7 | 475.8
1676 | 1514 | 344.3 | 510.2 | 515.1 | 481.4 | 592.9 | 358.1 | 416.1 | 475.2
1677 | 1515 | 343.7 | 510.4 | 515.6 | 481.9 | 592.9 | 358 | 416.5 | 474.5
1678 | 1516 | 343 | 510.6 | 516.2 | 482.4 | 592.9 | 357.8 | 416.9 | 473.9
1679 | 1517 | 342.3 | 510.7 | 516.8 | 483 | 592.8 | 357.7 | 417.3 | 473.3
1680 | 1518 | 341.7 | 510.9 | 517.3 | 483.5 | 592.7 | 357.5 | 417.7 | 472.6
1681 | 1519 | 341.1 | 511.1 | 517.9 | 484 | 592.6 | 357.4 | 418.1 | 471.9
1682 | 1520 | 340.6 | 511.3 | 518.5 | 484.5 | 592.5 | 357.2 | 418.6 | 471.4
1683 | 1521 | 340 | 511.5 | 519.1 | 485.1 | 592.3 | 357.1 | 419 | 470.8
1684 | 1522 | 339.4 | 511.7 | 519.8 | 485.6 | 592.2 | 357 | 419.5 | 470.2
1685 | 1523 | 338.9 | 511.9 | 520.4 | 486.1 | 592 | 356.8 | 419.9 | 469.5
1686 | 1524 | 338.4 | 512 | 521.1 | 486.6 | 591.8 | 356.6 | 420.4 | 468.9
1687 | 1525 | 338 | 512.2 | 521.7 | 487.1 | 591.6 | 356.5 | 420.9 | 468.4
1688 | 1526 | 337.5 | 512.4 | 522.4 | 487.6 | 591.5 | 356.3 | 421.4 | 467.7
1689 | 1527 | 336.8 | 512.6 | 523.1 | 488.1 | 591.3 | 356.1 | 421.8 | 467.1
1690 | 1528 | 336.3 | 512.8 | 523.8 | 488.6 | 591.2 | 355.9 | 422.3 | 466.5
1691 | 1529 | 335.8 | 513 | 524.5 | 489.1 | 591.1 | 355.8 | 422.8 | 465.9
1692 | 1530 | 335.4 | 513.1 | 525.2 | 489.6 | 591.1 | 355.6 | 423.3 | 465.3
1693 | 1531 | 334.9 | 513.3 | 525.9 | 490 | 591 | 355.4 | 423.8 | 464.8
1694 | 1532 | 334.2 | 513.5 | 526.6 | 490.6 | 590.9 | 355.3 | 424.2 | 464.2
1695 | 1533 | 333.5 | 513.7 | 527.2 | 491 | 590.8 | 355.1 | 424.7 | 463.7
1696 | 1534 | 333 | 513.8 | 527.9 | 491.5 | 590.7 | 354.9 | 425.2 | 463.1
1697 | 1535 | 332.5 | 514 | 528.6 | 492 | 590.5 | 354.7 | 425.7 | 462.5
1698 | 1536 | 331.9 | 514.2 | 529.3 | 492.5 | 590.4 | 354.5 | 426.2 | 462
1699 | 1537 | 331.4 | 514.3 | 530 | 493 | 590.2 | 354.4 | 426.7 | 461.5
1700 | 1538 | 330.9 | 514.5 | 530.7 | 493.5 | 589.9 | 354.2 | 427.1 | 461
1701 | 1539 | 330.3 | 514.6 | 531.4 | 494 | 589.6 | 354 | 427.6 | 460.4
1702 | 1540 | 329.7 | 514.7 | 532.1 | 494.5 | 589.3 | 353.8 | 428.1 | 459.8
1703 | 1541 | 329.2 | 514.9 | 532.7 | 495 | 589 | 353.6 | 428.6 | 459.1
1704 | 1542 | 328.6 | 515 | 533.4 | 495.5 | 588.7 | 353.4 | 429.1 | 458.6
1705 | 1543 | 328.2 | 515.2 | 534.1 | 496 | 588.3 | 353.2 | 429.6 | 458.1
1706 | 1544 | 327.7 | 515.3 | 534.7 | 496.5 | 588 | 353 | 430.1 | 457.5
1707 | 1545 | 327.2 | 515.5 | 535.4 | 496.9 | 587.6 | 352.9 | 430.6 | 457
1708 | 1546 | 326.7 | 515.6 | 536.1 | 497.4 | 587.3 | 352.7 | 431.1 | 456.4
1709 | 1547 | 326.1 | 515.8 | 536.7 | 497.9 | 586.9 | 352.5 | 431.6 | 455.8
1710 | 1548 | 325.6 | 515.9 | 537.4 | 498.4 | 586.6 | 352.3 | 432.1 | 455.3
1711 | 1549 | 325 | 516.1 | 538 | 498.9 | 586.3 | 352.1 | 432.6 | 454.8
1712 | 1550 | 324.6 | 516.3 | 538.7 | 499.4 | 586 | 352 | 433.2 | 454.1
1713 | 1551 | 324.1 | 516.5 | 539.3 | 499.9 | 585.6 | 351.8 | 433.6 | 453.5
1714 | 1552 | 323.5 | 516.7 | 539.9 | 500.3 | 585.3 | 351.6 | 434.2 | 453
1715 | 1553 | 323 | 516.8 | 540.6 | 500.9 | 584.8 | 351.4 | 434.7 | 452.4
1716 | 1554 | 322.5 | 517 | 541.2 | 501.4 | 584.4 | 351.2 | 435.2 | 451.9
1717 | 1555 | 321.9 | 517.2 | 541.7 | 501.9 | 583.9 | 351 | 435.7 | 451.4
1718 | 1556 | 321.5 | 517.4 | 542.3 | 502.4 | 583.3 | 350.8 | 436.2 | 450.8
1719 | 1557 | 321.1 | 517.6 | 542.9 | 503 | 582.8 | 350.7 | 436.7 | 450.2
1720 | 1558 | 320.6 | 517.8 | 543.6 | 503.5 | 582.1 | 350.5 | 437.2 | 449.6
1721 | 1559 | 320.1 | 518.1 | 544.2 | 504 | 581.4 | 350.3 | 437.7 | 449
1722 | 1560 | 319.6 | 518.4 | 544.7 | 504.6 | 580.8 | 350.1 | 438.2 | 448.4
1723 | 1561 | 319 | 518.6 | 545.3 | 505.1 | 580.4 | 349.9 | 438.7 | 447.8
1724 | 1562 | 318.6 | 518.9 | 545.9 | 505.7 | 579.8 | 349.7 | 439.2 | 447.3
1725 | 1563 | 318.1 | 519 | 546.4 | 506.2 | 579.3 | 349.5 | 439.7 | 446.7
1726 | 1564 | 317.6 | 519.2 | 547 | 506.8 | 578.8 | 349.3 | 440.2 | 446.3
1727 | 1565 | 317 | 519.4 | 547.5 | 507.3 | 578.2 | 349.1 | 440.6 | 445.8
1728 | 1566 | 316.4 | 519.6 | 548 | 507.9 | 577.6 | 348.9 | 441.1 | 445.3
1729 | 1567 | 315.9 | 519.8 | 548.5 | 508.4 | 577.1 | 348.8 | 441.5 | 444.7
1730 | 1568 | 315.4 | 520.1 | 549.1 | 509 | 576.6 | 348.6 | 442 | 444.1
1731 | 1569 | 314.9 | 520.3 | 549.6 | 509.5 | 576.1 | 348.4 | 442.4 | 443.6
1732 | 1570 | 314.6 | 520.6 | 550.1 | 510.1 | 575.7 | 348.2 | 442.9 | 443
1733 | 1571 | 314.1 | 520.8 | 550.6 | 510.7 | 575.3 | 348 | 443.3 | 442.4
1734 | 1572 | 313.6 | 521 | 551.1 | 511.2 | 575 | 347.8 | 443.8 | 441.8
1735 | 1573 | 313.1 | 521.1 | 551.6 | 511.8 | 574.6 | 347.6 | 444.2 | 441.2
1736 | 1574 | 312.6 | 521.1 | 552.1 | 512.4 | 574.3 | 347.5 | 444.6 | 440.7
1737 | 1575 | 312.1 | 521.2 | 552.7 | 512.9 | 573.9 | 347.3 | 445 | 440.1
1738 | 1576 | 311.6 | 521.2 | 553.2 | 513.5 | 573.4 | 347.1 | 445.5 | 439.5
1739 | 1577 | 311.1 | 521.2 | 553.7 | 514.1 | 572.9 | 346.9 | 445.9 | 439
1740 | 1578 | 310.6 | 521.3 | 554.1 | 514.7 | 572.5 | 346.7 | 446.3 | 438.5
1741 | 1579 | 310.1 | 521.4 | 554.7 | 515.3 | 572 | 346.5 | 446.7 | 438
1742 | 1580 | 309.6 | 521.5 | 555.2 | 515.9 | 571.5 | 346.3 | 447 | 437.4
1743 | 1581 | 309.1 | 521.6 | 555.7 | 516.5 | 571.1 | 346.1 | 447.4 | 436.9
1744 | 1582 | 308.5 | 521.7 | 556.2 | 517.1 | 570.5 | 345.9 | 447.8 | 436.3
1745 | 1583 | 308.1 | 521.8 | 556.7 | 517.7 | 570 | 345.8 | 448.2 | 435.8
1746 | 1584 | 307.5 | 521.9 | 557.2 | 518.3 | 569.5 | 345.6 | 448.6 | 435.2
1747 | 1585 | 307 | 521.9 | 557.7 | 518.9 | 568.9 | 345.5 | 448.9 | 434.7
1748 | 1586 | 306.5 | 521.9 | 558.2 | 519.5 | 568.4 | 345.3 | 449.3 | 434.2
1749 | 1587 | 306 | 521.9 | 558.6 | 520.1 | 568 | 345.1 | 449.7 | 433.7
1750 | 1588 | 305.5 | 521.8 | 559.1 | 520.7 | 567.5 | 345 | 450.1 | 433.3
1751 | 1589 | 305 | 521.8 | 559.6 | 521.3 | 567 | 344.8 | 450.4 | 432.8
1752 | 1590 | 304.7 | 521.7 | 560 | 521.9 | 566.5 | 344.7 | 450.8 | 432.3
1753 | 1591 | 304.3 | 521.7 | 560.5 | 522.5 | 565.9 | 344.5 | 451.2 | 431.9
1754 | 1592 | 304 | 521.6 | 560.9 | 523.1 | 565.4 | 344.4 | 451.5 | 431.4
1755 | 1593 | 303.5 | 521.5 | 561.3 | 523.7 | 564.9 | 344.2 | 451.9 | 430.9
1756 | 1594 | 303 | 521.4 | 561.8 | 524.3 | 564.4 | 344 | 452.2 | 430.4
1757 | 1595 | 302.4 | 521.3 | 562.2 | 524.9 | 563.9 | 343.8 | 452.6 | 429.8
1758 | 1596 | 301.9 | 521.2 | 562.6 | 525.5 | 563.4 | 343.7 | 453 | 429.3
1759 | 1597 | 301.4 | 521.1 | 563 | 526.1 | 563 | 343.5 | 453.3 | 428.7
1760 | 1598 | 301 | 521 | 563.5 | 526.7 | 562.5 | 343.3 | 453.7 | 428.3
1761 | 1599 | 300.5 | 520.9 | 563.9 | 527.3 | 562.1 | 343.1 | 454.1 | 427.8
1762 | 1600 | 300.1 | 520.8 | 564.3 | 527.9 | 561.7 | 342.9 | 454.4 | 427.2
1763 | 1601 | 299.6 | 520.6 | 564.7 | 528.6 | 561.2 | 342.7 | 454.8 | 426.6
1764 | 1602 | 299.2 | 520.5 | 565.2 | 529.2 | 560.8 | 342.5 | 455.1 | 426.1
1765 | 1603 | 298.8 | 520.4 | 565.5 | 529.8 | 560.4 | 342.3 | 455.5 | 425.5
1766 | 1604 | 298.4 | 520.3 | 565.9 | 530.5 | 560 | 342.1 | 455.9 | 425
1767 | 1605 | 297.8 | 520.2 | 566.3 | 531.2 | 559.6 | 341.9 | 456.2 | 424.5
1768 | 1606 | 297.3 | 520.1 | 566.7 | 531.8 | 559.2 | 341.7 | 456.6 | 424
1769 | 1607 | 296.7 | 520 | 567.1 | 532.4 | 558.8 | 341.5 | 456.9 | 423.6
1770 | 1608 | 296.3 | 519.8 | 567.5 | 533.1 | 558.4 | 341.2 | 457.3 | 423.1
1771 | 1609 | 295.8 | 519.7 | 567.9 | 533.8 | 558 | 341.1 | 457.6 | 422.6
1772 | 1610 | 295.4 | 519.5 | 568.2 | 534.5 | 557.7 | 340.8 | 458 | 422.1
1773 | 1611 | 295 | 519.4 | 568.6 | 535.2 | 557.3 | 340.7 | 458.3 | 421.6
1774 | 1612 | 294.5 | 519.2 | 569 | 535.9 | 556.9 | 340.5 | 458.7 | 421.1
1775 | 1613 | 294.1 | 519 | 569.4 | 536.6 | 556.6 | 340.2 | 459 | 420.6
1776 | 1614 | 293.8 | 518.9 | 569.8 | 537.3 | 556.2 | 340 | 459.4 | 420.1
1777 | 1615 | 293.5 | 518.7 | 570.2 | 538 | 555.8 | 339.8 | 459.7 | 419.6
1778 | 1616 | 293 | 518.6 | 570.6 | 538.7 | 555.5 | 339.6 | 460.1 | 419.1
1779 | 1617 | 292.3 | 518.5 | 571 | 539.5 | 555.1 | 339.4 | 460.4 | 418.5
1780 | 1618 | 291.7 | 518.4 | 571.4 | 540.2 | 554.7 | 339.2 | 460.8 | 418
1781 | 1619 | 291.3 | 518.4 | 571.9 | 540.9 | 554.3 | 339 | 461.1 | 417.5
1782 | 1620 | 290.9 | 518.3 | 572.3 | 541.6 | 553.9 | 338.8 | 461.4 | 417
1783 | 1621 | 290.4 | 518.3 | 572.7 | 542.3 | 553.5 | 338.6 | 461.8 | 416.5
1784 | 1622 | 289.9 | 518.3 | 573.1 | 542.9 | 553.1 | 338.4 | 462.1 | 415.9
1785 | 1623 | 289.4 | 518.2 | 573.5 | 543.6 | 552.7 | 338.2 | 462.4 | 415.4
1786 | 1624 | 289 | 518.2 | 574 | 544.3 | 552.3 | 338 | 462.8 | 414.9
1787 | 1625 | 288.5 | 518.2 | 574.4 | 545 | 551.9 | 337.9 | 463.1 | 414.4
1788 | 1626 | 288.1 | 518.1 | 574.8 | 545.6 | 551.5 | 337.7 | 463.4 | 413.8
1789 | 1627 | 287.8 | 518.1 | 575.2 | 546.2 | 551.1 | 337.5 | 463.7 | 413.3
1790 | 1628 | 287.4 | 518 | 575.6 | 546.8 | 550.7 | 337.3 | 464 | 412.9
1791 | 1629 | 286.9 | 517.9 | 576.1 | 547.5 | 550.3 | 337.1 | 464.4 | 412.5
1792 | 1630 | 286.6 | 517.9 | 576.5 | 548.1 | 549.9 | 336.9 | 464.7 | 412.1
1793 | 1631 | 286.2 | 517.8 | 576.9 | 548.7 | 549.6 | 336.7 | 465 | 411.5
1794 | 1632 | 285.9 | 517.7 | 577.3 | 549.3 | 549.2 | 336.5 | 465.4 | 411
1795 | 1633 | 285.4 | 517.6 | 577.7 | 549.9 | 548.9 | 336.3 | 465.7 | 410.6
1796 | 1634 | 284.9 | 517.6 | 578.1 | 550.4 | 548.5 | 336.1 | 466 | 410.2
1797 | 1635 | 284.5 | 517.5 | 578.5 | 551 | 548.2 | 335.9 | 466.3 | 409.7
1798 | 1636 | 284.1 | 517.4 | 578.8 | 551.5 | 547.9 | 335.7 | 466.7 | 409.2
1799 | 1637 | 283.7 | 517.3 | 579.1 | 552.1 | 547.5 | 335.5 | 467 | 408.7
1800 | 1638 | 283.3 | 517.2 | 579.4 | 552.6 | 547.2 | 335.3 | 467.3 | 408.3
1801 | 1639 | 282.7 | 517.1 | 579.7 | 553.1 | 546.8 | 335.1 | 467.6 | 407.7
1802 | 1640 | 282.4 | 517.1 | 580.1 | 553.6 | 546.5 | 334.9 | 467.9 | 407.2
1803 | 1641 | 282 | 517 | 580.4 | 554.1 | 546.2 | 334.7 | 468.2 | 406.7
1804 | 1642 | 281.7 | 516.8 | 580.7 | 554.6 | 545.9 | 334.5 | 468.5 | 406.2
1805 | 1643 | 281.3 | 516.7 | 581 | 555.1 | 545.5 | 334.3 | 468.8 | 405.7
1806 | 1644 | 280.9 | 516.6 | 581.3 | 555.7 | 545.2 | 334.1 | 469.1 | 405.2
1807 | 1645 | 280.3 | 516.6 | 581.6 | 556.2 | 544.9 | 333.9 | 469.4 | 404.8
1808 | 1646 | 279.9 | 516.5 | 581.8 | 556.7 | 544.6 | 333.7 | 469.7 | 404.3
1809 | 1647 | 279.4 | 516.4 | 582.1 | 557.2 | 544.3 | 333.5 | 470 | 403.7
1810 | 1648 | 279.1 | 516.3 | 582.4 | 557.7 | 544 | 333.3 | 470.3 | 403.2
1811 | 1649 | 278.7 | 516.3 | 582.6 | 558.2 | 543.7 | 333.1 | 470.6 | 402.7
1812 | 1650 | 278.3 | 516.2 | 582.9 | 558.6 | 543.4 | 333 | 470.9 | 402.3
1813 | 1651 | 277.9 | 516.1 | 583.2 | 559.1 | 543.1 | 332.8 | 471.2 | 401.8
1814 | 1652 | 277.4 | 516.1 | 583.4 | 559.6 | 542.8 | 332.6 | 471.5 | 401.4
1815 | 1653 | 276.9 | 516 | 583.7 | 560 | 542.5 | 332.4 | 471.8 | 401
1816 | 1654 | 276.5 | 515.8 | 583.9 | 560.5 | 542.2 | 332.2 | 472.1 | 400.6
1817 | 1655 | 276.1 | 515.8 | 584.1 | 560.9 | 541.9 | 332 | 472.4 | 400.2
1818 | 1656 | 275.6 | 515.7 | 584.4 | 561.4 | 541.6 | 331.8 | 472.7 | 399.8
1819 | 1657 | 275.3 | 515.6 | 584.6 | 561.8 | 541.3 | 331.6 | 473 | 399.3
1820 | 1658 | 275 | 515.5 | 584.9 | 562.3 | 541 | 331.4 | 473.2 | 398.8
1821 | 1659 | 274.6 | 515.4 | 585.1 | 562.7 | 540.7 | 331.2 | 473.5 | 398.4
1822 | 1660 | 274.2 | 515.3 | 585.4 | 563.1 | 540.5 | 331 | 473.8 | 397.9
1823 | 1661 | 273.8 | 515.2 | 585.6 | 563.6 | 540.2 | 330.8 | 474.1 | 397.4
1824 | 1662 | 273.4 | 515.2 | 585.9 | 564 | 539.9 | 330.6 | 474.3 | 397
1825 | 1663 | 273 | 515.1 | 586.2 | 564.4 | 539.6 | 330.4 | 474.6 | 396.6
1826 | 1664 | 272.5 | 515 | 586.4 | 564.9 | 539.3 | 330.2 | 474.9 | 396.2
1827 | 1665 | 272.1 | 514.9 | 586.7 | 565.3 | 539 | 330.1 | 475.1 | 395.7
1828 | 1666 | 271.7 | 514.8 | 586.9 | 565.7 | 538.7 | 329.8 | 475.4 | 395.3
1829 | 1667 | 271.3 | 514.7 | 587.2 | 566.1 | 538.4 | 329.7 | 475.6 | 394.8
1830 | 1668 | 271 | 514.6 | 587.4 | 566.5 | 538.2 | 329.5 | 475.9 | 394.3
1831 | 1669 | 270.5 | 514.5 | 587.7 | 566.9 | 537.9 | 329.3 | 476.1 | 393.9
1832 | 1670 | 270.1 | 514.4 | 587.9 | 567.3 | 537.6 | 329.1 | 476.4 | 393.5
1833 | 1671 | 269.6 | 514.4 | 588.2 | 567.7 | 537.3 | 328.9 | 476.6 | 393
1834 | 1672 | 269.2 | 514.3 | 588.5 | 568.1 | 537 | 328.7 | 476.9 | 392.5
1835 | 1673 | 268.8 | 514.3 | 588.7 | 568.4 | 536.8 | 328.5 | 477.1 | 392.1
1836 | 1674 | 268.5 | 514.2 | 589 | 568.8 | 536.5 | 328.3 | 477.3 | 391.6
1837 | 1675 | 268.1 | 514.2 | 589.2 | 569.1 | 536.2 | 328.1 | 477.6 | 391.2
1838 | 1676 | 267.7 | 514.1 | 589.5 | 569.5 | 536 | 327.9 | 477.8 | 390.9
1839 | 1677 | 267.3 | 514.1 | 589.7 | 569.8 | 535.7 | 327.7 | 478 | 390.5
1840 | 1678 | 266.9 | 514.1 | 590 | 570.2 | 535.5 | 327.5 | 478.2 | 390.1
1841 | 1679 | 266.4 | 514 | 590.2 | 570.5 | 535.2 | 327.3 | 478.4 | 389.6
1842 | 1680 | 266.1 | 513.9 | 590.5 | 570.9 | 535 | 327.1 | 478.7 | 389.1
1843 | 1681 | 265.6 | 513.8 | 590.7 | 571.2 | 534.7 | 326.9 | 478.9 | 388.6
1844 | 1682 | 265.3 | 513.7 | 590.9 | 571.5 | 534.5 | 326.7 | 479.1 | 388.2
1845 | 1683 | 265 | 513.6 | 591.1 | 571.9 | 534.2 | 326.5 | 479.3 | 387.8
1846 | 1684 | 264.8 | 513.6 | 591.3 | 572.2 | 534 | 326.3 | 479.5 | 387.4
1847 | 1685 | 264.4 | 513.5 | 591.4 | 572.5 | 533.7 | 326.1 | 479.7 | 386.9
1848 | 1686 | 264.1 | 513.4 | 591.6 | 572.8 | 533.5 | 325.9 | 479.9 | 386.5
1849 | 1687 | 263.8 | 513.3 | 591.8 | 573.2 | 533.2 | 325.7 | 480.1 | 386.1
1850 | 1688 | 263.4 | 513.3 | 591.9 | 573.4 | 533 | 325.5 | 480.2 | 385.5
1851 | 1689 | 263 | 513.2 | 592.1 | 573.7 | 532.7 | 325.3 | 480.4 | 385.1
1852 | 1690 | 262.5 | 513.1 | 592.2 | 574 | 532.4 | 325.1 | 480.6 | 384.7
1853 | 1691 | 262 | 513 | 592.4 | 574.3 | 532.2 | 324.9 | 480.7 | 384.2
1854 | 1692 | 261.6 | 512.9 | 592.5 | 574.6 | 531.9 | 324.7 | 480.9 | 383.8
1855 | 1693 | 261.2 | 512.9 | 592.7 | 574.9 | 531.6 | 324.5 | 481 | 383.3
1856 | 1694 | 260.7 | 512.8 | 592.8 | 575.2 | 531.4 | 324.3 | 481.1 | 382.8
1857 | 1695 | 260.3 | 512.7 | 592.9 | 575.5 | 531.1 | 324.1 | 481.3 | 382.3
1858 | 1696 | 260 | 512.6 | 593.1 | 575.8 | 530.8 | 323.9 | 481.4 | 381.9
1859 | 1697 | 259.6 | 512.5 | 593.2 | 576.1 | 530.5 | 323.7 | 481.5 | 381.4
1860 | 1698 | 259.2 | 512.5 | 593.3 | 576.4 | 530.2 | 323.5 | 481.6 | 380.9
1861 | 1699 | 258.9 | 512.4 | 593.3 | 576.7 | 529.9 | 323.3 | 481.8 | 380.4
1862 | 1700 | 258.5 | 512.4 | 593.3 | 577 | 529.7 | 323.1 | 481.9 | 379.9
1863 | 1701 | 258.2 | 512.3 | 593.4 | 577.3 | 529.4 | 322.9 | 482 | 379.5
1864 | 1702 | 257.8 | 512.2 | 593.4 | 577.6 | 529.1 | 322.7 | 482.1 | 379
1865 | 1703 | 257.5 | 512.1 | 593.5 | 577.9 | 528.8 | 322.5 | 482.2 | 378.5
1866 | 1704 | 257.1 | 512 | 593.5 | 578.1 | 528.5 | 322.3 | 482.3 | 378
1867 | 1705 | 256.7 | 511.9 | 593.6 | 578.4 | 528.2 | 322.1 | 482.4 | 377.6
1868 | 1706 | 256.3 | 511.8 | 593.6 | 578.6 | 528 | 321.9 | 482.4 | 377.1
1869 | 1707 | 255.8 | 511.8 | 593.7 | 578.9 | 527.7 | 321.7 | 482.5 | 376.6
1870 | 1708 | 255.5 | 511.7 | 593.7 | 579.1 | 527.4 | 321.5 | 482.6 | 376.1
1871 | 1709 | 255.2 | 511.6 | 593.8 | 579.4 | 527.1 | 321.3 | 482.7 | 375.6
1872 | 1710 | 254.8 | 511.5 | 593.8 | 579.6 | 526.9 | 321.1 | 482.7 | 375.1
1873 | 1711 | 254.4 | 511.4 | 593.9 | 579.9 | 526.6 | 320.9 | 482.8 | 374.7
1874 | 1712 | 254 | 511.3 | 593.9 | 580.1 | 526.3 | 320.7 | 482.8 | 374.1
1875 | 1713 | 253.6 | 511.3 | 593.9 | 580.4 | 526 | 320.5 | 482.9 | 373.5
1876 | 1714 | 253.2 | 511.2 | 593.9 | 580.6 | 525.8 | 320.3 | 482.9 | 373
1877 | 1715 | 252.9 | 511.1 | 594 | 580.8 | 525.5 | 320.1 | 482.9 | 372.6
1878 | 1716 | 252.5 | 511.1 | 594 | 581 | 525.2 | 319.9 | 483 | 372.1
1879 | 1717 | 252.1 | 511 | 594 | 581.3 | 525 | 319.7 | 483 | 371.6
1880 | 1718 | 251.9 | 510.9 | 594 | 581.5 | 524.7 | 319.5 | 483 | 371
1881 | 1719 | 251.5 | 510.8 | 594 | 581.8 | 524.4 | 319.3 | 483 | 370.5
1882 | 1720 | 251.3 | 510.7 | 594 | 582 | 524.2 | 319.1 | 483.1 | 370.1
1883 | 1721 | 250.9 | 510.6 | 593.9 | 582.3 | 523.9 | 318.9 | 483.1 | 369.6
1884 | 1722 | 250.6 | 510.6 | 593.9 | 582.5 | 523.6 | 318.7 | 483.1 | 369.2
1885 | 1723 | 250.2 | 510.5 | 593.9 | 582.7 | 523.3 | 318.5 | 483.1 | 368.8
1886 | 1724 | 249.9 | 510.4 | 593.9 | 583 | 523.1 | 318.4 | 483.1 | 368.5
1887 | 1725 | 249.6 | 510.3 | 593.8 | 583.2 | 522.8 | 318.2 | 483.1 | 368
1888 | 1726 | 249.2 | 510.3 | 593.8 | 583.5 | 522.5 | 318 | 483.1 | 367.4
1889 | 1727 | 248.8 | 510.2 | 593.8 | 583.7 | 522.2 | 317.8 | 483.1 | 366.9
1890 | 1728 | 248.5 | 510.1 | 593.7 | 583.9 | 522 | 317.6 | 483.1 | 366.4
1891 | 1729 | 248 | 510 | 593.6 | 584.1 | 521.7 | 317.4 | 483 | 365.9
1892 | 1730 | 247.6 | 509.9 | 593.6 | 584.3 | 521.4 | 317.2 | 483 | 365.4
1893 | 1731 | 247.2 | 509.9 | 593.5 | 584.5 | 521.1 | 317 | 483 | 364.9
1894 | 1732 | 246.9 | 509.8 | 593.5 | 584.7 | 520.8 | 316.8 | 483 | 364.4
1895 | 1733 | 246.6 | 509.7 | 593.4 | 584.8 | 520.5 | 316.6 | 482.9 | 364
1896 | 1734 | 246.4 | 509.6 | 593.3 | 585 | 520.2 | 316.4 | 482.9 | 363.6
1897 | 1735 | 246.1 | 509.5 | 593.3 | 585.2 | 520 | 316.2 | 482.9 | 363.1
1898 | 1736 | 245.6 | 509.5 | 593.2 | 585.4 | 519.7 | 316 | 482.8 | 362.6
1899 | 1737 | 245.2 | 509.4 | 593.1 | 585.6 | 519.4 | 315.8 | 482.8 | 362.1
1900 | 1738 | 244.9 | 509.3 | 592.9 | 585.8 | 519.1 | 315.6 | 482.7 | 361.6
1901 | 1739 | 244.5 | 509.3 | 592.8 | 585.9 | 518.8 | 315.4 | 482.7 | 361
1902 | 1740 | 244.2 | 509.2 | 592.7 | 586.1 | 518.6 | 315.2 | 482.6 | 360.6
1903 | 1741 | 243.9 | 509.1 | 592.6 | 586.2 | 518.3 | 314.9 | 482.6 | 360.2
1904 | 1742 | 243.7 | 509.1 | 592.5 | 586.3 | 518 | 314.7 | 482.6 | 359.7
1905 | 1743 | 243.4 | 509 | 592.4 | 586.4 | 517.7 | 314.5 | 482.5 | 359.2
1906 | 1744 | 242.9 | 508.9 | 592.2 | 586.6 | 517.4 | 314.3 | 482.5 | 358.8
1907 | 1745 | 242.5 | 508.9 | 592 | 586.7 | 517.1 | 314.1 | 482.4 | 358.3
1908 | 1746 | 242.2 | 508.8 | 591.8 | 586.8 | 516.8 | 313.9 | 482.3 | 357.8
1909 | 1747 | 241.9 | 508.7 | 591.7 | 586.9 | 516.5 | 313.7 | 482.3 | 357.3
1910 | 1748 | 241.6 | 508.6 | 591.5 | 587 | 516.2 | 313.5 | 482.2 | 356.9
1911 | 1749 | 241.3 | 508.5 | 591.3 | 587.2 | 516 | 313.3 | 482.1 | 356.3
1912 | 1750 | 240.9 | 508.5 | 591.1 | 587.3 | 515.7 | 313.1 | 482.1 | 355.9
1913 | 1751 | 240.6 | 508.4 | 591 | 587.4 | 515.4 | 312.9 | 482 | 355.4
1914 | 1752 | 240.3 | 508.3 | 590.8 | 587.4 | 515.1 | 312.7 | 481.9 | 354.9
1915 | 1753 | 239.9 | 508.3 | 590.6 | 587.5 | 514.8 | 312.5 | 481.8 | 354.4
1916 | 1754 | 239.6 | 508.1 | 590.4 | 587.5 | 514.5 | 312.3 | 481.8 | 354
1917 | 1755 | 239.2 | 508.1 | 590.2 | 587.6 | 514.2 | 312.1 | 481.7 | 353.5
1918 | 1756 | 238.8 | 508 | 590 | 587.7 | 513.9 | 311.9 | 481.6 | 353.1
1919 | 1757 | 238.5 | 507.9 | 589.8 | 587.8 | 513.6 | 311.7 | 481.5 | 352.7
1920 | 1758 | 238.2 | 507.8 | 589.6 | 587.9 | 513.3 | 311.5 | 481.4 | 352.2
1921 | 1759 | 237.8 | 507.7 | 589.4 | 588 | 513 | 311.3 | 481.4 | 351.6
1922 | 1760 | 237.5 | 507.6 | 589.2 | 588 | 512.7 | 311.1 | 481.3 | 351.2
1923 | 1761 | 237.2 | 507.5 | 589 | 588.1 | 512.3 | 310.9 | 481.2 | 350.8
1924 | 1762 | 236.8 | 507.4 | 588.8 | 588.1 | 512 | 310.8 | 481.1 | 350.3
1925 | 1763 | 236.5 | 507.3 | 588.6 | 588.2 | 511.7 | 310.6 | 481 | 349.8
1926 | 1764 | 236.1 | 507.2 | 588.4 | 588.2 | 511.4 | 310.4 | 480.9 | 349.3
1927 | 1765 | 235.8 | 507.2 | 588.2 | 588.3 | 511.1 | 310.2 | 480.8 | 348.9
1928 | 1766 | 235.6 | 507.1 | 588 | 588.4 | 510.8 | 310 | 480.7 | 348.4
1929 | 1767 | 235.2 | 507 | 587.8 | 588.4 | 510.4 | 309.8 | 480.6 | 348
1930 | 1768 | 234.8 | 506.9 | 587.6 | 588.4 | 510.1 | 309.6 | 480.5 | 347.5
1931 | 1769 | 234.5 | 506.8 | 587.3 | 588.4 | 509.8 | 309.4 | 480.4 | 347.1
1932 | 1770 | 234.1 | 506.7 | 587.1 | 588.4 | 509.4 | 309.2 | 480.3 | 346.7
1933 | 1771 | 233.9 | 506.6 | 586.9 | 588.5 | 509.1 | 309 | 480.2 | 346.2
1934 | 1772 | 233.5 | 506.5 | 586.6 | 588.5 | 508.8 | 308.8 | 480 | 345.8
1935 | 1773 | 233.2 | 506.5 | 586.4 | 588.4 | 508.5 | 308.6 | 479.9 | 345.4
1936 | 1774 | 232.9 | 506.4 | 586.1 | 588.4 | 508.1 | 308.4 | 479.8 | 345
1937 | 1775 | 232.6 | 506.3 | 585.9 | 588.3 | 507.8 | 308.3 | 479.7 | 344.4
1938 | 1776 | 232.4 | 506.2 | 585.6 | 588.3 | 507.5 | 308.1 | 479.6 | 344
1939 | 1777 | 232.2 | 506.1 | 585.3 | 588.1 | 507.1 | 307.9 | 479.5 | 343.5
1940 | 1778 | 231.8 | 506 | 585.1 | 588 | 506.8 | 307.7 | 479.4 | 343.1
1941 | 1779 | 231.5 | 506 | 584.8 | 588 | 506.5 | 307.4 | 479.2 | 342.7
1942 | 1780 | 231.1 | 506 | 584.5 | 587.9 | 506.2 | 307.2 | 479.1 | 342.2
1943 | 1781 | 230.7 | 506 | 584.2 | 587.9 | 505.8 | 307 | 479 | 341.8
1944 | 1782 | 230.4 | 505.9 | 583.9 | 587.9 | 505.5 | 306.8 | 478.8 | 341.3
1945 | 1783 | 230.1 | 505.9 | 583.6 | 587.8 | 505.2 | 306.6 | 478.7 | 340.8
1946 | 1784 | 229.7 | 505.8 | 583.3 | 587.7 | 504.9 | 306.3 | 478.6 | 340.3
1947 | 1785 | 229.4 | 505.8 | 583 | 587.6 | 504.5 | 306.1 | 478.4 | 339.8
1948 | 1786 | 229 | 505.8 | 582.7 | 587.5 | 504.2 | 305.9 | 478.3 | 339.4
1949 | 1787 | 228.7 | 505.9 | 582.4 | 587.4 | 503.9 | 305.7 | 478.1 | 339
1950 | 1788 | 228.3 | 505.9 | 582.1 | 587.3 | 503.6 | 305.5 | 478 | 338.6
1951 | 1789 | 228 | 505.9 | 581.8 | 587.2 | 503.3 | 305.3 | 477.8 | 338.1
1952 | 1790 | 227.7 | 505.9 | 581.4 | 587.1 | 503 | 305.1 | 477.7 | 337.7
1953 | 1791 | 227.4 | 505.9 | 581.1 | 587 | 502.6 | 304.9 | 477.5 | 337.2
1954 | 1792 | 227.2 | 505.9 | 580.7 | 586.9 | 502.3 | 304.7 | 477.4 | 336.7
1955 | 1793 | 226.9 | 505.9 | 580.4 | 586.8 | 502 | 304.5 | 477.2 | 336.2
1956 | 1794 | 226.7 | 505.8 | 580 | 586.7 | 501.7 | 304.3 | 477.1 | 335.7
1957 | 1795 | 226.3 | 505.8 | 579.6 | 586.5 | 501.4 | 304.1 | 476.9 | 335.1
1958 | 1796 | 226 | 505.7 | 579.2 | 586.5 | 501.1 | 303.9 | 476.7 | 334.8
1959 | 1797 | 225.8 | 505.5 | 578.8 | 586.4 | 500.8 | 303.7 | 476.5 | 334.4
1960 | 1798 | 225.5 | 505.4 | 578.4 | 586.3 | 500.5 | 303.5 | 476.4 | 334
1961 | 1799 | 225.2 | 505.2 | 578 | 586.2 | 500.2 | 303.3 | 476.2 | 333.6
1962 | 1800 | 224.9 | 505.1 | 577.6 | 586.1 | 500 | 303.1 | 476 | 333.2
1963 | 1801 | 224.5 | 504.9 | 577.2 | 586 | 499.7 | 302.9 | 475.8 | 332.8
1964 | 1802 | 224.1 | 504.7 | 576.7 | 585.9 | 499.4 | 302.7 | 475.7 | 332.3
1965 | 1803 | 223.7 | 504.5 | 576.3 | 585.8 | 499.1 | 302.4 | 475.5 | 331.8
1966 | 1804 | 223.3 | 504.3 | 575.9 | 585.7 | 498.9 | 302.2 | 475.3 | 331.3
1967 | 1805 | 223 | 504.1 | 575.4 | 585.6 | 498.5 | 302 | 475.1 | 330.9
1968 | 1806 | 222.7 | 504 | 574.9 | 585.5 | 498.2 | 301.8 | 474.9 | 330.4
1969 | 1807 | 222.4 | 503.8 | 574.5 | 585.3 | 497.9 | 301.5 | 474.7 | 329.9
1970 | 1808 | 222.1 | 503.6 | 574 | 585.2 | 497.7 | 301.3 | 474.5 | 329.4
1971 | 1809 | 221.8 | 503.4 | 573.5 | 585 | 497.3 | 301.1 | 474.3 | 328.9
1972 | 1810 | 221.6 | 503.2 | 573.1 | 584.9 | 497.1 | 300.9 | 474.1 | 328.4
1973 | 1811 | 221.3 | 503.1 | 572.6 | 584.7 | 496.7 | 300.7 | 473.9 | 327.9
1974 | 1812 | 221 | 503 | 572 | 584.5 | 496.4 | 300.4 | 473.7 | 327.4
1975 | 1813 | 220.8 | 502.9 | 571.5 | 584.3 | 496.1 | 300.2 | 473.5 | 326.9
1976 | 1814 | 220.5 | 502.7 | 571 | 584.1 | 495.8 | 300 | 473.3 | 326.5
1977 | 1815 | 220.3 | 502.6 | 570.4 | 583.9 | 495.5 | 299.8 | 473.1 | 326.1
1978 | 1816 | 220 | 502.5 | 569.9 | 583.6 | 495.1 | 299.5 | 472.9 | 325.5
1979 | 1817 | 219.7 | 502.3 | 569.3 | 583.4 | 494.8 | 299.3 | 472.8 | 325.1
1980 | 1818 | 219.4 | 502.2 | 568.7 | 583.1 | 494.5 | 299.1 | 472.6 | 324.8
1981 | 1819 | 219 | 502.1 | 568.2 | 582.8 | 494.2 | 298.9 | 472.4 | 324.4
1982 | 1820 | 218.8 | 502 | 567.6 | 582.5 | 493.9 | 298.7 | 472.2 | 324
1983 | 1821 | 218.4 | 502 | 566.9 | 582.2 | 493.5 | 298.4 | 472 | 323.6
1984 | 1822 | 218.1 | 501.9 | 566.3 | 581.9 | 493.2 | 298.2 | 471.7 | 323.1
1985 | 1823 | 217.7 | 501.7 | 565.6 | 581.5 | 492.8 | 298 | 471.5 | 322.7
1986 | 1824 | 217.4 | 501.5 | 565 | 581.2 | 492.5 | 297.8 | 471.3 | 322.3
1987 | 1825 | 217 | 501.3 | 564.3 | 580.8 | 492.2 | 297.6 | 471.1 | 321.9
1988 | 1826 | 216.7 | 501.1 | 563.6 | 580.4 | 491.8 | 297.4 | 470.8 | 321.5
1989 | 1827 | 216.4 | 500.8 | 562.9 | 580 | 491.5 | 297.2 | 470.6 | 321.1
1990 | 1828 | 216.1 | 500.6 | 562.2 | 579.6 | 491.1 | 297 | 470.4 | 320.6
1991 | 1829 | 215.8 | 500.3 | 561.5 | 579.3 | 490.8 | 296.8 | 470.1 | 320.2
1992 | 1830 | 215.6 | 500 | 560.7 | 578.9 | 490.5 | 296.6 | 469.9 | 319.8
1993 | 1831 | 215.4 | 499.9 | 560 | 578.4 | 490.1 | 296.4 | 469.6 | 319.4
1994 | 1832 | 215.1 | 499.6 | 559.2 | 578 | 489.7 | 296.3 | 469.4 | 319.1
1995 | 1833 | 214.8 | 499.4 | 558.4 | 577.5 | 489.3 | 296.1 | 469.1 | 318.6
1996 | 1834 | 214.6 | 499 | 557.7 | 577.1 | 489 | 295.9 | 468.9 | 318.2
1997 | 1835 | 214.3 | 498.7 | 556.9 | 576.7 | 488.6 | 295.7 | 468.6 | 317.8
1998 | 1836 | 214 | 498.4 | 556.1 | 576.2 | 488.2 | 295.5 | 468.3 | 317.5
1999 | 1837 | 213.6 | 498.1 | 555.3 | 575.7 | 487.8 | 295.4 | 468.1 | 317.1
2000 | 1838 | 213.3 | 497.8 | 554.5 | 575.2 | 487.4 | 295.2 | 467.8 | 316.7
2001 | 1839 | 213 | 497.6 | 553.7 | 574.7 | 487 | 295 | 467.5 | 316.3
2002 | 1840 | 212.8 | 497.3 | 552.8 | 574.2 | 486.6 | 294.8 | 467.2 | 316
2003 | 1841 | 212.6 | 497 | 552 | 573.6 | 486.1 | 294.6 | 466.9 | 315.6
2004 | 1842 | 212.3 | 496.7 | 551.2 | 573.1 | 485.7 | 294.5 | 466.6 | 315.3
2005 | 1843 | 212 | 496.4 | 550.3 | 572.5 | 485.3 | 294.3 | 466.4 | 314.9
2006 | 1844 | 211.6 | 496.1 | 549.4 | 571.9 | 484.8 | 294.1 | 466.1 | 314.5
2007 | 1845 | 211.4 | 495.8 | 548.5 | 571.3 | 484.4 | 293.9 | 465.8 | 314.1
2008 | 1846 | 211.1 | 495.5 | 547.6 | 570.6 | 483.9 | 293.7 | 465.5 | 313.7
2009 | 1847 | 210.8 | 495.2 | 546.7 | 570 | 483.5 | 293.6 | 465.2 | 313.3
2010 | 1848 | 210.5 | 494.9 | 545.8 | 569.3 | 483 | 293.4 | 464.9 | 312.8
2011 | 1849 | 210.2 | 494.6 | 544.9 | 568.5 | 482.6 | 293.2 | 464.6 | 312.4
2012 | 1850 | 210 | 494.3 | 543.9 | 567.8 | 482.1 | 293 | 464.3 | 312
2013 | 1851 | 209.7 | 494 | 543 | 567 | 481.6 | 292.8 | 464 | 311.6
2014 | 1852 | 209.4 | 493.8 | 542 | 566.2 | 481.1 | 292.6 | 463.7 | 311.2
2015 | 1853 | 209.1 | 493.5 | 541.1 | 565.4 | 480.7 | 292.4 | 463.4 | 310.8
2016 | 1854 | 208.7 | 493.1 | 540.1 | 564.6 | 480.2 | 292.3 | 463.1 | 310.4
2017 | 1855 | 208.4 | 492.8 | 539.1 | 563.8 | 479.6 | 292.1 | 462.8 | 310
2018 | 1856 | 208.2 | 492.5 | 538.1 | 562.9 | 479.1 | 291.9 | 462.4 | 309.7
2019 | 1857 | 207.9 | 492.2 | 537.1 | 562.1 | 478.6 | 291.8 | 462.1 | 309.3
2020 | 1858 | 207.7 | 491.9 | 536.1 | 561.2 | 478.1 | 291.6 | 461.8 | 308.9
2021 | 1859 | 207.5 | 491.6 | 535.1 | 560.3 | 477.6 | 291.4 | 461.5 | 308.4
2022 | 1860 | 207.3 | 491.3 | 534 | 559.4 | 477.1 | 291.2 | 461.2 | 308
2023 | 1861 | 207.1 | 491 | 533 | 558.4 | 476.6 | 291 | 460.8 | 307.6
2024 | 1862 | 206.8 | 490.6 | 532 | 557.5 | 476 | 290.8 | 460.5 | 307.2
2025 | 1863 | 206.5 | 490.3 | 530.9 | 556.5 | 475.5 | 290.6 | 460.2 | 306.7
2026 | 1864 | 206.1 | 490 | 529.8 | 555.6 | 474.9 | 290.5 | 459.9 | 306.3
2027 | 1865 | 205.8 | 489.6 | 528.8 | 554.6 | 474.4 | 290.3 | 459.5 | 306
2028 | 1866 | 205.6 | 489.3 | 527.7 | 553.6 | 473.8 | 290.1 | 459.2 | 305.6
2029 | 1867 | 205.3 | 489 | 526.6 | 552.6 | 473.2 | 289.9 | 458.9 | 305.2
2030 | 1868 | 205.1 | 488.7 | 525.5 | 551.6 | 472.7 | 289.7 | 458.5 | 304.8
2031 | 1869 | 204.8 | 488.3 | 524.4 | 550.6 | 472.1 | 289.5 | 458.2 | 304.4
2032 | 1870 | 204.5 | 488 | 523.2 | 549.5 | 471.5 | 289.3 | 457.8 | 303.9
2033 | 1871 | 204.2 | 487.7 | 522.2 | 548.5 | 471 | 289.1 | 457.5 | 303.4
2034 | 1872 | 204 | 487.4 | 521 | 547.5 | 470.4 | 288.9 | 457.1 | 303
2035 | 1873 | 203.8 | 487 | 519.9 | 546.4 | 469.8 | 288.7 | 456.8 | 302.6
2036 | 1874 | 203.6 | 486.7 | 518.8 | 545.4 | 469.2 | 288.5 | 456.4 | 302.2
2037 | 1875 | 203.2 | 486.4 | 517.6 | 544.3 | 468.7 | 288.4 | 456.1 | 301.8
2038 | 1876 | 202.9 | 486.1 | 516.5 | 543.3 | 468.1 | 288.2 | 455.7 | 301.4
2039 | 1877 | 202.5 | 485.7 | 515.4 | 542.2 | 467.5 | 288 | 455.3 | 301
2040 | 1878 | 202.3 | 485.4 | 514.2 | 541.2 | 466.9 | 287.7 | 455 | 300.7
2041 | 1879 | 202 | 485 | 513 | 540.1 | 466.2 | 287.5 | 454.6 | 300.3
2042 | 1880 | 201.8 | 484.9 | 511.5 | 539.1 | 466 | 287.4 | 454.2 | 299.8
2043 | 1881 | 201.5 | 484.5 | 510.3 | 538.1 | 465.4 | 287.2 | 453.8 | 299.5
2044 | 1882 | 201.2 | 484.1 | 509.1 | 537 | 464.8 | 287 | 453.4 | 299.1
2045 | 1883 | 200.9 | 483.8 | 508 | 535.9 | 464.1 | 286.8 | 453 | 298.8
2046 | 1884 | 200.6 | 483.4 | 506.8 | 534.8 | 463.5 | 286.6 | 452.6 | 298.4
2047 | 1885 | 200.4 | 483 | 505.6 | 533.7 | 462.8 | 286.4 | 452.2 | 298.1
2048 | 1886 | 200.2 | 482.6 | 504.3 | 532.7 | 462.2 | 286.2 | 451.8 | 297.7
2049 | 1887 | 200 | 482.2 | 503.1 | 531.6 | 461.5 | 286.1 | 451.4 | 297.4
2050 | 1888 | 199.8 | 481.8 | 502 | 530.5 | 460.9 | 285.9 | 451 | 296.9
2051 | 1889 | 199.5 | 481.4 | 500.8 | 529.4 | 460.2 | 285.7 | 450.6 | 296.4
2052 | 1890 | 199.3 | 481 | 499.7 | 528.4 | 459.5 | 285.5 | 450.2 | 296.1
2053 | 1891 | 199.1 | 480.6 | 498.5 | 527.3 | 458.8 | 285.3 | 449.8 | 295.8
2054 | 1892 | 198.8 | 480.2 | 497.3 | 526.2 | 458.2 | 285 | 449.3 | 295.5
2055 | 1893 | 198.5 | 479.8 | 496 | 525.2 | 457.5 | 284.8 | 448.9 | 295.1
2056 | 1894 | 198.2 | 479.3 | 494.9 | 524.1 | 456.8 | 284.6 | 448.5 | 294.7
2057 | 1895 | 197.9 | 478.8 | 493.7 | 523 | 456.1 | 284.4 | 448.1 | 294.3
2058 | 1896 | 197.6 | 478.4 | 492.5 | 521.9 | 455.4 | 284.2 | 447.6 | 293.9
2059 | 1897 | 197.4 | 477.9 | 491.3 | 520.9 | 454.6 | 283.9 | 447.2 | 293.6
2060 | 1898 | 197.1 | 477.4 | 490.2 | 519.8 | 453.9 | 283.7 | 446.8 | 293.1
2061 | 1899 | 196.9 | 476.9 | 489 | 518.7 | 453.1 | 283.5 | 446.3 | 292.7
2062 | 1900 | 196.7 | 476.4 | 487.8 | 517.6 | 452.4 | 283.3 | 445.9 | 292.3
2063 | 1901 | 196.5 | 475.9 | 486.7 | 516.5 | 451.7 | 283.1 | 445.5 | 292
2064 | 1902 | 196.2 | 475.4 | 485.5 | 515.4 | 450.9 | 282.9 | 445 | 291.7
2065 | 1903 | 195.9 | 474.9 | 484.4 | 514.3 | 450.2 | 282.7 | 444.6 | 291.5
2066 | 1904 | 195.6 | 474.4 | 483.2 | 513.3 | 449.4 | 282.5 | 444.1 | 291.3
2067 | 1905 | 195.3 | 473.8 | 482.1 | 512.2 | 448.6 | 282.3 | 443.7 | 291
2068 | 1906 | 195.1 | 473.3 | 480.9 | 511.1 | 447.9 | 282.1 | 443.2 | 290.6
2069 | 1907 | 194.8 | 472.8 | 479.8 | 510 | 447.1 | 281.9 | 442.8 | 290.2
2070 | 1908 | 194.5 | 472.3 | 478.7 | 508.9 | 446.3 | 281.6 | 442.3 | 289.8
2071 | 1909 | 194.2 | 471.7 | 477.5 | 507.8 | 445.6 | 281.4 | 441.9 | 289.3
2072 | 1910 | 193.9 | 471.2 | 476.4 | 506.8 | 444.8 | 281.2 | 441.4 | 288.9
2073 | 1911 | 193.7 | 470.7 | 475.3 | 505.7 | 444 | 281 | 440.9 | 288.5
2074 | 1912 | 193.4 | 470.1 | 474.1 | 504.6 | 443.3 | 280.8 | 440.5 | 288
2075 | 1913 | 193.2 | 469.5 | 473 | 503.6 | 442.5 | 280.6 | 440 | 287.6
2076 | 1914 | 192.9 | 469 | 471.9 | 502.5 | 441.7 | 280.4 | 439.5 | 287.3
2077 | 1915 | 192.7 | 468.4 | 470.8 | 501.4 | 440.9 | 280.2 | 439.1 | 287
2078 | 1916 | 192.4 | 467.8 | 469.7 | 500.4 | 440.2 | 280 | 438.6 | 286.7
2079 | 1917 | 192.1 | 467.2 | 468.6 | 499.4 | 439.4 | 279.8 | 438.1 | 286.3
2080 | 1918 | 191.9 | 466.6 | 467.5 | 498.3 | 438.6 | 279.6 | 437.6 | 285.9
2081 | 1919 | 191.7 | 466 | 466.4 | 497.3 | 437.8 | 279.4 | 437.1 | 285.5
2082 | 1920 | 191.4 | 465.4 | 465.3 | 496.2 | 437.1 | 279.2 | 436.6 | 285.1
2083 | 1921 | 191.2 | 464.8 | 464.3 | 495.1 | 436.3 | 279 | 436.1 | 284.7
2084 | 1922 | 191 | 464.2 | 463.2 | 494 | 435.5 | 278.8 | 435.6 | 284.3
2085 | 1923 | 190.8 | 463.5 | 462.1 | 493 | 434.7 | 278.6 | 435.1 | 283.9
2086 | 1924 | 190.6 | 462.9 | 461.1 | 491.9 | 433.9 | 278.4 | 434.6 | 283.5
2087 | 1925 | 190.4 | 462.2 | 460 | 490.8 | 433.1 | 278.2 | 434.1 | 283.2
2088 | 1926 | 190.1 | 461.5 | 459 | 489.7 | 432.3 | 278 | 433.6 | 282.8
2089 | 1927 | 189.9 | 460.9 | 457.9 | 488.6 | 431.6 | 277.8 | 433.1 | 282.4
2090 | 1928 | 189.7 | 460.2 | 456.9 | 487.6 | 430.8 | 277.6 | 432.6 | 282
2091 | 1929 | 189.5 | 459.5 | 455.8 | 486.5 | 430 | 277.4 | 432 | 281.6
2092 | 1930 | 189.3 | 458.8 | 454.8 | 485.4 | 429.2 | 277.1 | 431.5 | 281.3
2093 | 1931 | 189.1 | 458.1 | 453.8 | 484.4 | 428.5 | 276.9 | 431 | 281.1
2094 | 1932 | 188.9 | 457.4 | 452.7 | 483.3 | 427.7 | 276.7 | 430.5 | 280.9
2095 | 1933 | 188.6 | 456.7 | 451.7 | 482.2 | 426.9 | 276.5 | 429.9 | 280.6
2096 | 1934 | 188.4 | 456 | 450.7 | 481.2 | 426.1 | 276.3 | 429.4 | 280.2
2097 | 1935 | 188.2 | 455.3 | 449.7 | 480.1 | 425.3 | 276.2 | 428.8 | 279.8
2098 | 1936 | 188 | 454.6 | 448.7 | 479.1 | 424.6 | 275.9 | 428.3 | 279.4
2099 | 1937 | 187.8 | 453.9 | 447.7 | 478 | 423.8 | 275.7 | 427.8 | 278.9
2100 | 1938 | 187.6 | 453.1 | 446.7 | 476.9 | 423 | 275.5 | 427.2 | 278.5
2101 | 1939 | 187.3 | 452.4 | 445.8 | 475.9 | 422.2 | 275.3 | 426.6 | 278.1
2102 | 1940 | 187 | 451.7 | 444.8 | 474.8 | 421.5 | 275.1 | 426.1 | 277.7
2103 | 1941 | 186.8 | 450.9 | 443.8 | 473.8 | 420.7 | 274.9 | 425.5 | 277.3
2104 | 1942 | 186.6 | 450.2 | 442.8 | 472.7 | 420 | 274.7 | 425 | 277
2105 | 1943 | 186.4 | 449.5 | 441.9 | 471.7 | 419.2 | 274.5 | 424.4 | 276.6
2106 | 1944 | 186.1 | 448.7 | 440.9 | 470.6 | 418.4 | 274.3 | 423.8 | 276.1
2107 | 1945 | 185.8 | 448 | 440 | 469.6 | 417.7 | 274.1 | 423.2 | 275.7
2108 | 1946 | 185.6 | 447.2 | 439 | 468.5 | 416.9 | 274 | 422.6 | 275.3
2109 | 1947 | 185.3 | 446.5 | 438.1 | 467.5 | 416.2 | 273.8 | 422 | 274.9
2110 | 1948 | 185.1 | 445.7 | 437.2 | 466.5 | 415.4 | 273.6 | 421.5 | 274.5
2111 | 1949 | 184.9 | 444.9 | 436.2 | 465.4 | 414.7 | 273.4 | 420.8 | 274.1
2112 | 1950 | 184.7 | 444.2 | 435.3 | 464.4 | 413.9 | 273.2 | 420.3 | 273.8
2113 | 1951 | 184.4 | 443.4 | 434.4 | 463.4 | 413.2 | 273 | 419.6 | 273.5
2114 | 1952 | 184.2 | 442.6 | 433.4 | 462.4 | 412.4 | 272.8 | 419 | 273.2
2115 | 1953 | 183.9 | 441.9 | 432.5 | 461.3 | 411.7 | 272.6 | 418.4 | 272.9
2116 | 1954 | 183.7 | 441.1 | 431.6 | 460.3 | 410.9 | 272.4 | 417.8 | 272.6
2117 | 1955 | 183.5 | 440.3 | 430.7 | 459.3 | 410.2 | 272.2 | 417.2 | 272.3
2118 | 1956 | 183.2 | 439.5 | 429.8 | 458.3 | 409.5 | 272 | 416.6 | 272.2
2119 | 1957 | 183 | 438.7 | 428.9 | 457.3 | 408.7 | 271.8 | 416 | 272.1
2120 | 1958 | 182.7 | 437.9 | 428.1 | 456.3 | 408 | 271.6 | 415.4 | 271.8
2121 | 1959 | 182.6 | 437.2 | 427.2 | 455.3 | 407.3 | 271.4 | 414.8 | 271.5
2122 | 1960 | 182.4 | 436.4 | 426.3 | 454.3 | 406.6 | 271.2 | 414.1 | 271.1
2123 | 1961 | 182.2 | 435.6 | 425.4 | 453.3 | 405.8 | 271 | 413.5 | 270.8
2124 | 1962 | 182 | 434.7 | 424.6 | 452.3 | 405.1 | 270.8 | 412.9 | 270.4
2125 | 1963 | 181.8 | 433.9 | 423.7 | 451.3 | 404.4 | 270.6 | 412.2 | 270
2126 | 1964 | 181.6 | 433.1 | 422.8 | 450.4 | 403.7 | 270.4 | 411.6 | 269.6
2127 | 1965 | 181.3 | 432.3 | 422 | 449.4 | 403 | 270.2 | 411 | 269.2
2128 | 1966 | 181.2 | 431.5 | 421.1 | 448.4 | 402.2 | 270 | 410.3 | 268.8
2129 | 1967 | 181.1 | 430.7 | 420.3 | 447.4 | 401.5 | 269.9 | 409.7 | 268.4
2130 | 1968 | 180.9 | 429.8 | 419.4 | 446.5 | 400.8 | 269.7 | 409.1 | 268.1
2131 | 1969 | 180.7 | 429 | 418.6 | 445.5 | 400.1 | 269.5 | 408.4 | 267.8
2132 | 1970 | 180.4 | 428.2 | 417.7 | 444.5 | 399.4 | 269.3 | 407.8 | 267.5
2133 | 1971 | 180.2 | 427.3 | 416.9 | 443.6 | 398.6 | 269.1 | 407.1 | 267.1
2134 | 1972 | 179.9 | 426.5 | 416.1 | 442.6 | 397.9 | 268.9 | 406.5 | 266.6
2135 | 1973 | 179.7 | 425.7 | 415.2 | 441.7 | 397.2 | 268.7 | 405.8 | 266.2
2136 | 1974 | 179.4 | 424.9 | 414.4 | 440.7 | 396.5 | 268.5 | 405.1 | 265.8
2137 | 1975 | 179.1 | 424 | 413.6 | 439.8 | 395.8 | 268.4 | 404.5 | 265.5
2138 | 1976 | 178.9 | 423.2 | 412.8 | 438.9 | 395.1 | 268.2 | 403.8 | 265.1
2139 | 1977 | 178.6 | 422.4 | 412 | 437.9 | 394.4 | 268 | 403.2 | 264.6
2140 | 1978 | 178.4 | 421.5 | 411.2 | 437 | 393.7 | 267.8 | 402.5 | 264.5
2141 | 1979 | 178.2 | 420.7 | 410.4 | 436 | 393 | 267.6 | 401.8 | 264.5
2142 | 1980 | 177.9 | 419.9 | 409.6 | 435.1 | 392.3 | 267.4 | 401.2 | 264.2
2143 | 1981 | 177.7 | 419.1 | 408.8 | 434.2 | 391.6 | 267.2 | 400.5 | 263.9
2144 | 1982 | 177.4 | 418.3 | 408 | 433.3 | 390.9 | 267 | 399.8 | 263.7
2145 | 1983 | 177.1 | 417.4 | 407.2 | 432.4 | 390.2 | 266.8 | 399.2 | 263.2
2146 | 1984 | 176.9 | 416.6 | 406.4 | 431.4 | 389.6 | 266.6 | 398.5 | 262.8
2147 | 1985 | 176.7 | 415.8 | 405.6 | 430.5 | 388.9 | 266.4 | 397.8 | 262.3
2148 | 1986 | 176.5 | 415 | 404.9 | 429.6 | 388.2 | 266.3 | 397.1 | 261.8
2149 | 1987 | 176.3 | 414.2 | 404.1 | 428.7 | 387.5 | 266.1 | 396.5 | 261.5
2150 | 1988 | 176.1 | 413.3 | 403.3 | 427.9 | 386.8 | 265.9 | 395.8 | 261.1
2151 | 1989 | 175.9 | 412.5 | 402.6 | 427 | 386.1 | 265.7 | 395.1 | 260.7
2152 | 1990 | 175.7 | 411.7 | 401.8 | 426.1 | 385.4 | 265.5 | 394.5 | 260.3
2153 | 1991 | 175.5 | 410.9 | 401.1 | 425.2 | 384.7 | 265.3 | 393.8 | 259.9
2154 | 1992 | 175.3 | 410 | 400.3 | 424.3 | 384 | 265.1 | 393.1 | 259.4
2155 | 1993 | 175.1 | 409.2 | 399.6 | 423.4 | 383.3 | 264.9 | 392.4 | 259
2156 | 1994 | 174.9 | 408.4 | 398.8 | 422.6 | 382.6 | 264.7 | 391.8 | 258.5
2157 | 1995 | 174.7 | 407.6 | 398.1 | 421.7 | 382 | 264.5 | 391.1 | 258.2
2158 | 1996 | 174.5 | 406.8 | 397.3 | 420.9 | 381.3 | 264.4 | 390.4 | 257.9
2159 | 1997 | 174.3 | 406 | 396.6 | 420 | 380.6 | 264.2 | 389.8 | 257.6
2160 | 1998 | 174.1 | 405.2 | 395.9 | 419.1 | 379.9 | 264 | 389.1 | 257.3
2161 | 1999 | 173.9 | 404.4 | 395.1 | 418.3 | 379.2 | 263.8 | 388.4 | 257
2162 | 2000 | 173.8 | 403.6 | 394.4 | 417.4 | 378.5 | 263.6 | 387.7 | 256.8
2163 | 2001 | 173.6 | 402.8 | 393.7 | 416.6 | 377.8 | 263.4 | 387.1 | 256.4
2164 | 2002 | 173.4 | 402 | 393 | 415.8 | 377.2 | 263.2 | 386.4 | 256
2165 | 2003 | 173.2 | 401.2 | 392.3 | 414.9 | 376.5 | 263 | 385.7 | 255.6
2166 | 2004 | 173 | 400.4 | 391.5 | 414.1 | 375.8 | 262.9 | 385.1 | 255.3
2167 | 2005 | 172.7 | 399.6 | 390.8 | 413.3 | 375.1 | 262.7 | 384.4 | 254.9
2168 | 2006 | 172.4 | 398.8 | 390.1 | 412.4 | 374.5 | 262.5 | 383.8 | 254.5
2169 | 2007 | 172.2 | 398 | 389.4 | 411.6 | 373.8 | 262.3 | 383.1 | 254.1
2170 | 2008 | 171.9 | 397.2 | 388.7 | 410.8 | 373.1 | 262.1 | 382.4 | 253.7
2171 | 2009 | 171.6 | 396.4 | 388 | 410 | 372.4 | 261.9 | 381.8 | 253.4
2172 | 2010 | 171.4 | 395.6 | 387.3 | 409.2 | 371.8 | 261.7 | 381.1 | 253
2173 | 2011 | 171.2 | 394.8 | 386.6 | 408.4 | 371.1 | 261.5 | 380.5 | 252.8
2174 | 2012 | 171.1 | 394.1 | 385.9 | 407.6 | 370.5 | 261.3 | 379.8 | 252.4
2175 | 2013 | 170.9 | 393.3 | 385.2 | 406.8 | 369.8 | 261.1 | 379.2 | 252.1
2176 | 2014 | 170.7 | 392.5 | 384.6 | 406 | 369.2 | 260.9 | 378.5 | 251.8
2177 | 2015 | 170.5 | 391.7 | 383.9 | 405.2 | 368.5 | 260.7 | 377.9 | 251.4
2178 | 2016 | 170.2 | 390.9 | 383.2 | 404.4 | 367.9 | 260.5 | 377.2 | 251
2179 | 2017 | 170 | 390.2 | 382.5 | 403.6 | 367.2 | 260.3 | 376.6 | 250.6
2180 | 2018 | 169.8 | 389.4 | 381.8 | 402.8 | 366.6 | 260.1 | 376 | 250.3
2181 | 2019 | 169.6 | 388.6 | 381.2 | 402 | 365.9 | 259.9 | 375.3 | 249.9
2182 | 2020 | 169.4 | 387.8 | 380.5 | 401.3 | 365.3 | 259.7 | 374.7 | 249.6
2183 | 2021 | 169.2 | 387.1 | 379.8 | 400.5 | 364.6 | 259.5 | 374.1 | 249.3
2184 | 2022 | 169 | 386.3 | 379.2 | 399.7 | 364 | 259.3 | 373.4 | 248.9
2185 | 2023 | 168.8 | 385.6 | 378.5 | 398.9 | 363.3 | 259.1 | 372.8 | 248.6
2186 | 2024 | 168.6 | 384.8 | 377.9 | 398.2 | 362.7 | 258.9 | 372.2 | 248.3
2187 | 2025 | 168.4 | 384.1 | 377.2 | 397.4 | 362 | 258.8 | 371.5 | 247.9
2188 | 2026 | 168.2 | 383.3 | 376.5 | 396.7 | 361.4 | 258.6 | 370.9 | 247.6
2189 | 2027 | 168 | 382.6 | 375.9 | 395.9 | 360.8 | 258.4 | 370.3 | 247.2
2190 | 2028 | 167.9 | 381.9 | 375.3 | 395.2 | 360.1 | 258.2 | 369.7 | 247
2191 | 2029 | 167.6 | 381.1 | 374.6 | 394.4 | 359.5 | 258 | 369.1 | 247
2192 | 2030 | 167.5 | 380.4 | 374 | 393.7 | 358.8 | 257.8 | 368.4 | 246.9
2193 | 2031 | 167.3 | 379.6 | 373.3 | 392.9 | 358.2 | 257.6 | 367.8 | 246.7
2194 | 2032 | 167.1 | 378.9 | 372.7 | 392.2 | 357.6 | 257.4 | 367.2 | 246.4
2195 | 2033 | 166.9 | 378.2 | 372.1 | 391.4 | 357 | 257.2 | 366.6 | 246
2196 | 2034 | 166.8 | 377.5 | 371.4 | 390.7 | 356.3 | 257 | 365.9 | 245.6
2197 | 2035 | 166.6 | 376.8 | 370.8 | 390 | 355.7 | 256.9 | 365.3 | 245.2
2198 | 2036 | 166.4 | 376.1 | 370.2 | 389.3 | 355.1 | 256.7 | 364.7 | 244.8
2199 | 2037 | 166.2 | 375.4 | 369.5 | 388.6 | 354.5 | 256.5 | 364.1 | 244.3
2200 | 2038 | 166 | 374.7 | 368.9 | 387.8 | 353.8 | 256.4 | 363.5 | 243.9
2201 | 2039 | 165.8 | 374 | 368.3 | 387.1 | 353.2 | 256.2 | 362.9 | 243.6
2202 | 2040 | 165.6 | 373.3 | 367.7 | 386.4 | 352.6 | 256 | 362.3 | 243.2
2203 | 2041 | 165.3 | 372.6 | 367.1 | 385.7 | 352 | 255.8 | 361.7 | 242.9
2204 | 2042 | 165.1 | 371.9 | 366.4 | 385 | 351.4 | 255.6 | 361.1 | 242.6
2205 | 2043 | 164.8 | 371.2 | 365.8 | 384.3 | 350.8 | 255.4 | 360.4 | 242.3
2206 | 2044 | 164.6 | 370.5 | 365.2 | 383.6 | 350.1 | 255.3 | 359.8 | 242
2207 | 2045 | 164.5 | 369.8 | 364.6 | 382.9 | 349.5 | 255.1 | 359.2 | 241.7
2208 | 2046 | 164.3 | 369.1 | 364 | 382.3 | 348.9 | 254.9 | 358.6 | 241.3
2209 | 2047 | 164 | 368.4 | 363.4 | 381.6 | 348.3 | 254.8 | 358 | 241
2210 | 2048 | 163.9 | 367.8 | 362.8 | 380.9 | 347.7 | 254.6 | 357.4 | 240.7
2211 | 2049 | 163.7 | 367.3 | 361.8 | 380.4 | 347.7 | 254.4 | 356.8 | 240.3
2212 | 2050 | 163.5 | 366.9 | 360.7 | 379.9 | 347.8 | 254.3 | 356.2 | 239.9
2213 | 2051 | 163.3 | 366.2 | 360.1 | 379.2 | 347.2 | 254.2 | 355.6 | 239.6
2214 | 2052 | 163.2 | 365.5 | 359.5 | 378.5 | 346.6 | 254 | 355 | 239.3
2215 | 2053 | 163 | 364.9 | 358.9 | 377.9 | 346 | 253.8 | 354.4 | 239
2216 | 2054 | 162.8 | 364.2 | 358.3 | 377.2 | 345.4 | 253.7 | 353.8 | 238.6
2217 | 2055 | 162.7 | 363.5 | 357.7 | 376.5 | 344.8 | 253.5 | 353.2 | 238.3
2218 | 2056 | 162.5 | 362.9 | 357.1 | 375.9 | 344.3 | 253.3 | 352.6 | 238.1
2219 | 2057 | 162.3 | 362.2 | 356.5 | 375.2 | 343.7 | 253.1 | 352 | 237.7
2220 | 2058 | 162.1 | 361.5 | 355.9 | 374.6 | 343.1 | 252.9 | 351.4 | 237.3
2221 | 2059 | 162 | 360.9 | 355.3 | 373.9 | 342.5 | 252.8 | 350.9 | 237.1
2222 | 2060 | 161.8 | 360.2 | 354.7 | 373.3 | 341.9 | 252.6 | 350.3 | 236.7
2223 | 2061 | 161.7 | 359.6 | 354.1 | 372.7 | 341.4 | 252.4 | 349.7 | 236.5
2224 | 2062 | 161.5 | 358.9 | 353.6 | 372 | 340.8 | 252.2 | 349.1 | 236.1
2225 | 2063 | 161.3 | 358.2 | 353 | 371.4 | 340.2 | 252 | 348.5 | 235.7
2226 | 2064 | 161.1 | 357.6 | 352.4 | 370.7 | 339.6 | 251.8 | 347.9 | 235.4
2227 | 2065 | 160.9 | 356.9 | 351.9 | 370.1 | 339.1 | 251.7 | 347.3 | 235.1
2228 | 2066 | 160.7 | 356.3 | 351.3 | 369.5 | 338.5 | 251.5 | 346.8 | 234.8
2229 | 2067 | 160.5 | 355.7 | 350.7 | 368.8 | 337.9 | 251.3 | 346.2 | 234.6
2230 | 2068 | 160.4 | 355 | 350.1 | 368.2 | 337.4 | 251.1 | 345.6 | 234.3
2231 | 2069 | 160.3 | 354.4 | 349.6 | 367.6 | 336.8 | 251 | 345 | 233.8
2232 | 2070 | 160.1 | 353.7 | 349 | 367 | 336.2 | 250.8 | 344.5 | 233.5
2233 | 2071 | 160 | 353.1 | 348.4 | 366.4 | 335.7 | 250.6 | 343.9 | 233.3
2234 | 2072 | 159.8 | 352.5 | 347.9 | 365.7 | 335.1 | 250.4 | 343.3 | 233
2235 | 2073 | 159.6 | 351.9 | 347.3 | 365.1 | 334.6 | 250.2 | 342.7 | 232.7
2236 | 2074 | 159.5 | 351.2 | 346.8 | 364.5 | 334 | 250.1 | 342.1 | 232.4
2237 | 2075 | 159.3 | 350.6 | 346.2 | 363.9 | 333.5 | 249.9 | 341.6 | 232.1
2238 | 2076 | 159 | 350 | 345.7 | 363.3 | 333 | 249.7 | 341 | 231.8
2239 | 2077 | 158.8 | 349.4 | 345.1 | 362.7 | 332.4 | 249.5 | 340.4 | 231.6
2240 | 2078 | 158.6 | 348.8 | 344.6 | 362.1 | 331.9 | 249.3 | 339.9 | 231.2
2241 | 2079 | 158.4 | 348.2 | 344 | 361.5 | 331.3 | 249.1 | 339.3 | 231
2242 | 2080 | 158.2 | 347.6 | 343.5 | 360.9 | 330.8 | 248.9 | 338.7 | 230.8
2243 | 2081 | 158.1 | 347 | 343 | 360.2 | 330.2 | 248.7 | 338.1 | 230.5
2244 | 2082 | 157.9 | 346.4 | 342.4 | 359.6 | 329.7 | 248.6 | 337.6 | 230.2
2245 | 2083 | 157.8 | 345.8 | 341.9 | 359.1 | 329.2 | 248.4 | 337 | 229.8
2246 | 2084 | 157.6 | 345.2 | 341.3 | 358.5 | 328.6 | 248.2 | 336.4 | 229.5
2247 | 2085 | 157.4 | 344.7 | 340.8 | 357.9 | 328.1 | 248 | 335.9 | 229.1
2248 | 2086 | 157.3 | 344.1 | 340.3 | 357.3 | 327.6 | 247.9 | 335.3 | 228.8
2249 | 2087 | 157 | 343.5 | 339.7 | 356.7 | 327.1 | 247.7 | 334.7 | 228.6
2250 | 2088 | 156.8 | 342.9 | 339.2 | 356.1 | 326.5 | 247.5 | 334.2 | 228.2
2251 | 2089 | 156.6 | 342.4 | 338.7 | 355.5 | 326 | 247.3 | 333.6 | 227.9
2252 | 2090 | 156.4 | 341.8 | 338.1 | 355 | 325.5 | 247.1 | 333.1 | 227.5
2253 | 2091 | 156.2 | 341.2 | 337.6 | 354.4 | 325 | 246.9 | 332.5 | 227.1
2254 | 2092 | 156.1 | 340.7 | 337.1 | 353.8 | 324.5 | 246.7 | 332 | 226.8
2255 | 2093 | 155.9 | 340.1 | 336.6 | 353.2 | 323.9 | 246.6 | 331.4 | 226.4
2256 | 2094 | 155.7 | 339.6 | 336.1 | 352.7 | 323.4 | 246.4 | 330.9 | 226.1
2257 | 2095 | 155.5 | 339 | 335.5 | 352.1 | 322.9 | 246.2 | 330.3 | 225.8
2258 | 2096 | 155.4 | 338.5 | 335 | 351.5 | 322.4 | 246 | 329.7 | 225.5
2259 | 2097 | 155.2 | 337.9 | 334.5 | 351 | 321.9 | 245.8 | 329.2 | 225.2
2260 | 2098 | 155 | 337.3 | 334 | 350.4 | 321.3 | 245.7 | 328.6 | 224.9
2261 | 2099 | 154.9 | 336.8 | 333.4 | 349.9 | 320.8 | 245.5 | 328.1 | 224.7
2262 | 2100 | 154.7 | 336.2 | 333 | 349.3 | 320.3 | 245.3 | 327.5 | 224.4
2263 | 2101 | 154.6 | 335.7 | 332.4 | 348.7 | 319.8 | 245.1 | 327 | 224.2
2264 | 2102 | 154.5 | 335.1 | 331.9 | 348.2 | 319.3 | 244.9 | 326.4 | 223.9
2265 | 2103 | 154.3 | 334.6 | 331.4 | 347.6 | 318.8 | 244.8 | 325.9 | 223.5
2266 | 2104 | 154.1 | 334 | 330.9 | 347.1 | 318.3 | 244.6 | 325.3 | 223.2
2267 | 2105 | 153.9 | 333.5 | 330.4 | 346.5 | 317.7 | 244.4 | 324.8 | 222.9
2268 | 2106 | 153.7 | 333 | 329.9 | 346 | 317.2 | 244.2 | 324.2 | 222.6
2269 | 2107 | 153.5 | 332.4 | 329.4 | 345.5 | 316.7 | 244 | 323.7 | 222.3
2270 | 2108 | 153.2 | 331.9 | 328.9 | 344.9 | 316.2 | 243.9 | 323.2 | 222
2271 | 2109 | 153 | 331.4 | 328.4 | 344.4 | 315.7 | 243.7 | 322.6 | 221.6
2272 | 2110 | 152.8 | 330.8 | 327.9 | 343.8 | 315.2 | 243.5 | 322.1 | 221.3
2273 | 2111 | 152.6 | 330.3 | 327.4 | 343.3 | 314.7 | 243.3 | 321.5 | 221.1
2274 | 2112 | 152.3 | 329.8 | 326.9 | 342.8 | 314.2 | 243.1 | 321 | 220.9
2275 | 2113 | 152.1 | 329.2 | 326.4 | 342.2 | 313.7 | 243 | 320.4 | 220.8
2276 | 2114 | 151.9 | 328.7 | 325.9 | 341.7 | 313.2 | 242.8 | 319.9 | 220.5
2277 | 2115 | 151.7 | 328.2 | 325.4 | 341.2 | 312.7 | 242.6 | 319.3 | 220.2
2278 | 2116 | 151.5 | 327.6 | 324.9 | 340.7 | 312.2 | 242.4 | 318.8 | 219.9
2279 | 2117 | 151.4 | 327.1 | 324.4 | 340.1 | 311.7 | 242.3 | 318.3 | 219.6
2280 | 2118 | 151.2 | 326.6 | 323.9 | 339.6 | 311.2 | 242.1 | 317.7 | 219.2
2281 | 2119 | 151.1 | 326.1 | 323.4 | 339.1 | 310.7 | 241.9 | 317.2 | 218.9
2282 | 2120 | 150.9 | 325.6 | 322.9 | 338.5 | 310.2 | 241.7 | 316.6 | 218.6
2283 | 2121 | 150.7 | 325 | 322.4 | 338 | 309.7 | 241.5 | 316.1 | 218.4
2284 | 2122 | 150.5 | 324.5 | 321.9 | 337.5 | 309.2 | 241.4 | 315.6 | 218
2285 | 2123 | 150.4 | 324 | 321.4 | 337 | 308.8 | 241.2 | 315 | 217.8
2286 | 2124 | 150.2 | 323.5 | 321 | 336.5 | 308.3 | 241 | 314.5 | 217.5
2287 | 2125 | 150 | 323 | 320.5 | 335.9 | 307.8 | 240.8 | 314 | 217.4
2288 | 2126 | 149.8 | 322.5 | 320 | 335.4 | 307.3 | 240.7 | 313.4 | 217.1
2289 | 2127 | 149.6 | 322 | 319.5 | 334.9 | 306.8 | 240.5 | 312.9 | 216.7
2290 | 2128 | 149.4 | 321.5 | 319 | 334.4 | 306.3 | 240.3 | 312.4 | 216.4
2291 | 2129 | 149.2 | 321 | 318.6 | 333.9 | 305.8 | 240.1 | 311.8 | 216.2
2292 | 2130 | 149.1 | 320.5 | 318.1 | 333.4 | 305.4 | 240 | 311.3 | 216
2293 | 2131 | 148.9 | 320 | 317.6 | 332.9 | 304.9 | 239.8 | 310.8 | 215.8
2294 | 2132 | 148.8 | 319.5 | 317.1 | 332.4 | 304.4 | 239.6 | 310.3 | 215.7
2295 | 2133 | 148.6 | 319 | 316.7 | 331.9 | 303.9 | 239.4 | 309.7 | 215.5
2296 | 2134 | 148.3 | 318.5 | 316.2 | 331.4 | 303.4 | 239.2 | 309.2 | 215.2
2297 | 2135 | 148.2 | 318 | 315.7 | 330.9 | 302.9 | 239 | 308.7 | 214.9
2298 | 2136 | 148 | 317.5 | 315.3 | 330.3 | 302.4 | 238.9 | 308.2 | 214.6
2299 | 2137 | 147.8 | 317 | 314.8 | 329.9 | 302 | 238.7 | 307.6 | 214.2
2300 | 2138 | 147.7 | 316.5 | 314.3 | 329.3 | 301.5 | 238.5 | 307.1 | 213.9
2301 | 2139 | 147.6 | 316 | 313.8 | 328.8 | 301 | 238.3 | 306.6 | 213.7
2302 | 2140 | 147.5 | 315.6 | 313.4 | 328.4 | 300.6 | 238.1 | 306.1 | 213.5
2303 | 2141 | 147.3 | 315.1 | 312.9 | 327.9 | 300.1 | 238 | 305.5 | 213.2
2304 | 2142 | 147.2 | 314.6 | 312.4 | 327.4 | 299.6 | 237.8 | 305 | 212.9
2305 | 2143 | 147 | 314.1 | 312 | 326.9 | 299.1 | 237.6 | 304.5 | 212.7
2306 | 2144 | 146.9 | 313.6 | 311.5 | 326.4 | 298.7 | 237.4 | 304 | 212.4
2307 | 2145 | 146.7 | 313.2 | 311.1 | 325.9 | 298.2 | 237.2 | 303.4 | 212.2
2308 | 2146 | 146.5 | 312.7 | 310.6 | 325.4 | 297.7 | 237 | 302.9 | 212
2309 | 2147 | 146.4 | 312.2 | 310.2 | 324.9 | 297.3 | 236.8 | 302.4 | 211.6
2310 | 2148 | 146.2 | 311.7 | 309.7 | 324.5 | 296.8 | 236.7 | 301.9 | 211.1
2311 | 2149 | 146 | 311.3 | 309.2 | 324 | 296.4 | 236.5 | 301.3 | 210.8
2312 | 2150 | 145.9 | 310.8 | 308.8 | 323.5 | 295.9 | 236.3 | 300.8 | 210.6
2313 | 2151 | 145.7 | 310.3 | 308.3 | 323 | 295.4 | 236.1 | 300.3 | 210.3
2314 | 2152 | 145.5 | 309.9 | 307.9 | 322.6 | 295 | 235.9 | 299.8 | 209.9
2315 | 2153 | 145.4 | 309.4 | 307.4 | 322.1 | 294.5 | 235.7 | 299.3 | 209.6
2316 | 2154 | 145.2 | 308.9 | 307 | 321.6 | 294.1 | 235.5 | 298.8 | 209.4
2317 | 2155 | 145.1 | 308.5 | 306.5 | 321.1 | 293.6 | 235.3 | 298.2 | 209
2318 | 2156 | 144.9 | 308 | 306.1 | 320.7 | 293.1 | 235.1 | 297.7 | 208.8
2319 | 2157 | 144.7 | 307.6 | 305.7 | 320.2 | 292.7 | 235 | 297.2 | 208.5
2320 | 2158 | 144.6 | 307.1 | 305.2 | 319.7 | 292.2 | 234.8 | 296.7 | 208.2
2321 | 2159 | 144.4 | 306.7 | 304.7 | 319.3 | 291.8 | 234.6 | 296.2 | 208
2322 | 2160 | 144.3 | 306.2 | 304.3 | 318.8 | 291.3 | 234.4 | 295.7 | 207.7
2323 | 2161 | 144.1 | 305.7 | 303.9 | 318.3 | 290.9 | 234.3 | 295.2 | 207.4
2324 | 2162 | 144 | 305.3 | 303.4 | 317.9 | 290.5 | 234.1 | 294.7 | 207.1
2325 | 2163 | 143.9 | 304.8 | 303 | 317.4 | 290 | 233.9 | 294.1 | 206.8
2326 | 2164 | 143.7 | 304.4 | 302.5 | 317 | 289.6 | 233.7 | 293.6 | 206.6
2327 | 2165 | 143.6 | 303.9 | 302.1 | 316.5 | 289.2 | 233.5 | 293.1 | 206.4
2328 | 2166 | 143.4 | 303.5 | 301.6 | 316 | 288.7 | 233.4 | 292.6 | 206.1
2329 | 2167 | 143.3 | 303 | 301.2 | 315.6 | 288.3 | 233.2 | 292.1 | 205.9
2330 | 2168 | 143.1 | 302.6 | 300.8 | 315.1 | 287.8 | 233 | 291.6 | 205.7
2331 | 2169 | 143 | 302.1 | 300.3 | 314.7 | 287.4 | 232.8 | 291.1 | 205.5
2332 | 2170 | 142.9 | 301.7 | 299.9 | 314.2 | 287 | 232.7 | 290.6 | 205.2
2333 | 2171 | 142.8 | 301.2 | 299.4 | 313.8 | 286.5 | 232.5 | 290.1 | 205
2334 | 2172 | 142.6 | 300.8 | 299 | 313.3 | 286.1 | 232.3 | 289.5 | 204.7
2335 | 2173 | 142.5 | 300.4 | 298.6 | 312.9 | 285.7 | 232.1 | 289 | 204.6
2336 | 2174 | 142.3 | 299.9 | 298.2 | 312.4 | 285.2 | 231.9 | 288.5 | 204.4
2337 | 2175 | 142.2 | 299.5 | 297.7 | 311.9 | 284.8 | 231.7 | 288 | 204.2
2338 | 2176 | 142 | 299 | 297.3 | 311.5 | 284.4 | 231.5 | 287.5 | 203.8
2339 | 2177 | 141.9 | 298.6 | 296.9 | 311.1 | 284 | 231.4 | 287 | 203.6
2340 | 2178 | 141.7 | 298.1 | 296.4 | 310.6 | 283.6 | 231.2 | 286.5 | 203.4
2341 | 2179 | 141.5 | 297.7 | 296 | 310.2 | 283.1 | 231 | 286 | 203.2
2342 | 2180 | 141.3 | 297.3 | 295.6 | 309.7 | 282.7 | 230.8 | 285.5 | 203
2343 | 2181 | 141.1 | 296.8 | 295.2 | 309.3 | 282.3 | 230.7 | 285 | 202.8
2344 | 2182 | 140.9 | 296.4 | 294.7 | 308.9 | 281.9 | 230.5 | 284.5 | 202.6
2345 | 2183 | 140.8 | 296 | 294.3 | 308.4 | 281.5 | 230.3 | 284 | 202.4
2346 | 2184 | 140.6 | 295.5 | 293.9 | 308 | 281 | 230.1 | 283.5 | 202.1
2347 | 2185 | 140.5 | 295.1 | 293.5 | 307.6 | 280.7 | 229.9 | 283 | 201.8
2348 | 2186 | 140.4 | 294.7 | 293 | 307.1 | 280.2 | 229.7 | 282.5 | 201.6
2349 | 2187 | 140.2 | 294.3 | 292.6 | 306.7 | 279.8 | 229.5 | 282 | 201.4
2350 | 2188 | 140.1 | 293.8 | 292.2 | 306.3 | 279.4 | 229.3 | 281.5 | 201.2
2351 | 2189 | 140 | 293.4 | 291.8 | 305.9 | 279 | 229.1 | 281 | 201
2352 | 2190 | 139.9 | 293 | 291.4 | 305.5 | 278.6 | 228.9 | 280.5 | 200.7
2353 | 2191 | 139.7 | 292.6 | 290.9 | 305 | 278.2 | 228.7 | 280 | 200.4
2354 | 2192 | 139.5 | 292.1 | 290.6 | 304.6 | 277.8 | 228.6 | 279.5 | 200.2
2355 | 2193 | 139.4 | 291.7 | 290.2 | 304.2 | 277.3 | 228.4 | 279 | 199.8
2356 | 2194 | 139.3 | 291.3 | 289.7 | 303.8 | 276.9 | 228.2 | 278.5 | 199.5
2357 | 2195 | 139.1 | 290.9 | 289.3 | 303.4 | 276.5 | 228 | 278 | 199.3
2358 | 2196 | 138.9 | 290.5 | 288.9 | 302.9 | 276.1 | 227.9 | 277.5 | 199
2359 | 2197 | 138.8 | 290.1 | 288.5 | 302.5 | 275.7 | 227.7 | 277 | 198.7
2360 | 2198 | 138.6 | 289.7 | 288.1 | 302.1 | 275.3 | 227.5 | 276.5 | 198.5
2361 | 2199 | 138.4 | 289.2 | 287.7 | 301.7 | 274.9 | 227.3 | 276 | 198.3
2362 | 2200 | 138.2 | 288.8 | 287.3 | 301.3 | 274.5 | 227.1 | 275.5 | 198
2363 | 2201 | 138.1 | 288.4 | 286.9 | 300.9 | 274.1 | 226.9 | 275 | 197.8
2364 | 2202 | 137.9 | 288 | 286.5 | 300.5 | 273.7 | 226.7 | 274.5 | 197.6
2365 | 2203 | 137.8 | 287.6 | 286.1 | 300.1 | 273.3 | 226.6 | 274.1 | 197.3
2366 | 2204 | 137.7 | 287.2 | 285.6 | 299.7 | 272.9 | 226.4 | 273.6 | 197.1
2367 | 2205 | 137.5 | 286.8 | 285.2 | 299.3 | 272.5 | 226.2 | 273.1 | 196.9
2368 | 2206 | 137.3 | 286.4 | 284.8 | 298.9 | 272.1 | 226 | 272.6 | 196.6
2369 | 2207 | 137.2 | 286 | 284.4 | 298.5 | 271.7 | 225.9 | 272.1 | 196.4
2370 | 2208 | 137 | 285.6 | 284 | 298.1 | 271.3 | 225.7 | 271.6 | 196.2
2371 | 2209 | 136.9 | 285.2 | 283.6 | 297.7 | 270.9 | 225.5 | 271.1 | 196
2372 | 2210 | 136.7 | 284.8 | 283.2 | 297.3 | 270.5 | 225.3 | 270.7 | 195.8
2373 | 2211 | 136.6 | 284.4 | 282.8 | 296.9 | 270.2 | 225.2 | 270.2 | 195.6
2374 | 2212 | 136.4 | 284 | 282.4 | 296.5 | 269.8 | 225 | 269.7 | 195.6
2375 | 2213 | 136.3 | 283.6 | 282 | 296.2 | 269.4 | 224.8 | 269.2 | 195.3
2376 | 2214 | 136.1 | 283.2 | 281.7 | 295.8 | 269 | 224.7 | 268.7 | 195.1
2377 | 2215 | 136 | 282.9 | 281.2 | 295.4 | 268.6 | 224.5 | 268.2 | 195
2378 | 2216 | 135.9 | 282.5 | 280.8 | 295 | 268.2 | 224.3 | 267.8 | 194.7
2379 | 2217 | 135.8 | 282.1 | 280.5 | 294.6 | 267.8 | 224.1 | 267.3 | 194.5
2380 | 2218 | 135.7 | 281.7 | 280.1 | 294.2 | 267.5 | 223.9 | 266.8 | 194.3
2381 | 2219 | 135.6 | 281.3 | 279.7 | 293.8 | 267.1 | 223.7 | 266.3 | 194
2382 | 2220 | 135.4 | 280.9 | 279.3 | 293.5 | 266.7 | 223.6 | 265.8 | 193.7
2383 | 2221 | 135.3 | 280.6 | 278.9 | 293.1 | 266.3 | 223.4 | 265.4 | 193.3
2384 | 2222 | 135.1 | 280.2 | 278.5 | 292.7 | 265.9 | 223.2 | 264.9 | 193.1
2385 | 2223 | 135 | 279.8 | 278.1 | 292.3 | 265.5 | 223 | 264.4 | 192.9
2386 | 2224 | 134.9 | 279.4 | 277.7 | 291.9 | 265.1 | 222.8 | 263.9 | 192.6
2387 | 2225 | 134.8 | 279 | 277.4 | 291.5 | 264.7 | 222.6 | 263.5 | 192.4
2388 | 2226 | 134.6 | 278.7 | 276.9 | 291.2 | 264.4 | 222.4 | 263 | 192.3
2389 | 2227 | 134.5 | 278.3 | 276.6 | 290.8 | 264 | 222.2 | 262.5 | 192.1
2390 | 2228 | 134.3 | 277.9 | 276.2 | 290.4 | 263.6 | 222.1 | 262 | 192
2391 | 2229 | 134.2 | 277.6 | 275.8 | 290 | 263.2 | 221.9 | 261.6 | 191.8
2392 | 2230 | 134 | 277.2 | 275.4 | 289.6 | 262.9 | 221.7 | 261.1 | 191.6
2393 | 2231 | 133.9 | 276.8 | 275 | 289.3 | 262.5 | 221.5 | 260.6 | 191.4
2394 | 2232 | 133.7 | 276.5 | 274.7 | 288.9 | 262.1 | 221.3 | 260.2 | 191.1
2395 | 2233 | 133.6 | 276.1 | 274.3 | 288.5 | 261.7 | 221.1 | 259.7 | 190.8
2396 | 2234 | 133.5 | 275.7 | 273.9 | 288.2 | 261.4 | 220.9 | 259.2 | 190.6
2397 | 2235 | 133.3 | 275.4 | 273.5 | 287.8 | 261 | 220.8 | 258.8 | 190.4
2398 | 2236 | 133.1 | 275 | 273.1 | 287.4 | 260.6 | 220.6 | 258.3 | 190.2
2399 | 2237 | 133 | 274.6 | 272.7 | 287.1 | 260.3 | 220.4 | 257.8 | 190
2400 | 2238 | 132.8 | 274.3 | 272.4 | 286.7 | 259.9 | 220.2 | 257.4 | 189.9
2401 | 2239 | 132.7 | 273.9 | 272 | 286.3 | 259.5 | 220 | 256.9 | 189.7
2402 | 2240 | 132.6 | 273.6 | 271.6 | 285.9 | 259.1 | 219.8 | 256.4 | 189.5
2403 | 2241 | 132.4 | 273.2 | 271.2 | 285.6 | 258.8 | 219.6 | 256 | 189.4
2404 | 2242 | 132.3 | 272.9 | 270.8 | 285.2 | 258.4 | 219.5 | 255.5 | 189.1
2405 | 2243 | 132.2 | 272.5 | 270.5 | 284.8 | 258 | 219.3 | 255.1 | 188.7
2406 | 2244 | 132.1 | 272.2 | 270.1 | 284.5 | 257.7 | 219.1 | 254.6 | 188.4
2407 | 2245 | 131.9 | 271.8 | 269.7 | 284.1 | 257.3 | 218.9 | 254.1 | 188.1
2408 | 2246 | 131.9 | 271.4 | 269.4 | 283.8 | 257 | 218.7 | 253.7 | 188
2409 | 2247 | 131.7 | 271.1 | 269 | 283.4 | 256.6 | 218.5 | 253.2 | 187.8
2410 | 2248 | 131.5 | 270.7 | 268.6 | 283 | 256.2 | 218.3 | 252.7 | 187.7
2411 | 2249 | 131.4 | 270.4 | 268.3 | 282.7 | 255.8 | 218.1 | 252.3 | 187.6
2412 | 2250 | 131.2 | 270 | 267.9 | 282.3 | 255.5 | 217.9 | 251.8 | 187.4
2413 | 2251 | 131 | 269.7 | 267.5 | 282 | 255.1 | 217.7 | 251.4 | 187.1
2414 | 2252 | 130.9 | 269.3 | 267.2 | 281.6 | 254.8 | 217.6 | 250.9 | 186.8
2415 | 2253 | 130.8 | 269 | 266.8 | 281.2 | 254.4 | 217.4 | 250.5 | 186.5
2416 | 2254 | 130.7 | 268.6 | 266.4 | 280.9 | 254 | 217.2 | 250 | 186.3
2417 | 2255 | 130.6 | 268.3 | 266 | 280.5 | 253.7 | 217 | 249.6 | 186.2
2418 | 2256 | 130.4 | 267.9 | 265.7 | 280.2 | 253.3 | 216.8 | 249.1 | 185.9
2419 | 2257 | 130.3 | 267.6 | 265.3 | 279.8 | 252.9 | 216.6 | 248.7 | 185.6
2420 | 2258 | 130.1 | 267.2 | 265 | 279.5 | 252.6 | 216.4 | 248.2 | 185.4
2421 | 2259 | 129.9 | 266.9 | 264.6 | 279.1 | 252.2 | 216.2 | 247.8 | 185.1
2422 | 2260 | 129.8 | 266.5 | 264.2 | 278.8 | 251.9 | 216 | 247.3 | 184.9
2423 | 2261 | 129.6 | 266.2 | 263.9 | 278.4 | 251.5 | 215.9 | 246.9 | 184.8
2424 | 2262 | 129.4 | 265.8 | 263.5 | 278 | 251.1 | 215.7 | 246.4 | 184.5
2425 | 2263 | 129.3 | 265.5 | 263.1 | 277.7 | 250.8 | 215.5 | 246 | 184.4
2426 | 2264 | 129.1 | 265.1 | 262.8 | 277.3 | 250.4 | 215.3 | 245.5 | 184.2
2427 | 2265 | 129 | 264.8 | 262.4 | 277 | 250 | 215.1 | 245.1 | 184
2428 | 2266 | 128.9 | 264.4 | 262.1 | 276.6 | 249.7 | 214.9 | 244.7 | 183.9
2429 | 2267 | 128.8 | 264.1 | 261.7 | 276.3 | 249.3 | 214.7 | 244.2 | 183.7
2430 | 2268 | 128.6 | 263.7 | 261.4 | 275.9 | 248.9 | 214.6 | 243.8 | 183.5
2431 | 2269 | 128.5 | 263.4 | 261 | 275.6 | 248.6 | 214.4 | 243.4 | 183.4
2432 | 2270 | 128.4 | 263 | 260.6 | 275.2 | 248.2 | 214.2 | 242.9 | 183.3
2433 | 2271 | 128.2 | 262.7 | 260.3 | 274.9 | 247.9 | 214 | 242.5 | 183.1
2434 | 2272 | 128.1 | 262.3 | 260 | 274.5 | 247.5 | 213.9 | 242.1 | 182.9
2435 | 2273 | 127.9 | 262 | 259.6 | 274.2 | 247.2 | 213.7 | 241.6 | 182.6
2436 | 2274 | 127.7 | 261.6 | 259.2 | 273.9 | 246.8 | 213.5 | 241.2 | 182.4
2437 | 2275 | 127.6 | 261.3 | 258.9 | 273.5 | 246.5 | 213.3 | 240.8 | 182.3
2438 | 2276 | 127.5 | 261 | 258.5 | 273.2 | 246.1 | 213.2 | 240.4 | 182.1
2439 | 2277 | 127.4 | 260.6 | 258.2 | 272.8 | 245.8 | 213 | 239.9 | 181.9
2440 | 2278 | 127.2 | 260.3 | 257.8 | 272.5 | 245.4 | 212.8 | 239.5 | 181.6
2441 | 2279 | 127.1 | 259.9 | 257.5 | 272.1 | 245.1 | 212.6 | 239.1 | 181.5
2442 | 2280 | 127 | 259.6 | 257.2 | 271.8 | 244.7 | 212.4 | 238.7 | 181.4
2443 | 2281 | 126.9 | 259.2 | 256.8 | 271.4 | 244.4 | 212.2 | 238.3 | 181.2
2444 | 2282 | 126.8 | 258.9 | 256.5 | 271.1 | 244 | 212 | 237.8 | 181
2445 | 2283 | 126.7 | 258.6 | 256.1 | 270.7 | 243.7 | 211.8 | 237.4 | 180.8
2446 | 2284 | 126.5 | 258.2 | 255.8 | 270.4 | 243.3 | 211.6 | 237 | 180.5
2447 | 2285 | 126.4 | 257.9 | 255.4 | 270.1 | 243 | 211.5 | 236.6 | 180.3
2448 | 2286 | 126.3 | 257.6 | 255.1 | 269.7 | 242.6 | 211.3 | 236.2 | 180.1
2449 | 2287 | 126.2 | 257.2 | 254.7 | 269.4 | 242.3 | 211.1 | 235.8 | 180
2450 | 2288 | 126 | 256.9 | 254.4 | 269.1 | 241.9 | 210.9 | 235.3 | 179.7
2451 | 2289 | 125.9 | 256.6 | 254.1 | 268.7 | 241.6 | 210.7 | 234.9 | 179.6
2452 | 2290 | 125.8 | 256.2 | 253.7 | 268.4 | 241.2 | 210.5 | 234.5 | 179.4
2453 | 2291 | 125.7 | 255.9 | 253.4 | 268 | 240.9 | 210.3 | 234.1 | 179.4
2454 | 2292 | 125.5 | 255.5 | 253.1 | 267.7 | 240.5 | 210.2 | 233.7 | 179.2
2455 | 2293 | 125.4 | 255.2 | 252.7 | 267.4 | 240.2 | 210 | 233.3 | 179.1
2456 | 2294 | 125.2 | 254.9 | 252.4 | 267 | 239.9 | 209.8 | 232.9 | 178.8
2457 | 2295 | 125.1 | 254.6 | 252 | 266.7 | 239.5 | 209.6 | 232.5 | 178.6
2458 | 2296 | 125 | 254.2 | 251.7 | 266.4 | 239.2 | 209.5 | 232.1 | 178.4
2459 | 2297 | 124.8 | 253.9 | 251.4 | 266 | 238.8 | 209.3 | 231.7 | 178.2
2460 | 2298 | 124.7 | 253.6 | 251 | 265.7 | 238.5 | 209.1 | 231.3 | 178
2461 | 2299 | 124.6 | 253.2 | 250.7 | 265.3 | 238.2 | 208.9 | 230.9 | 177.9
2462 | 2300 | 124.4 | 252.9 | 250.4 | 265 | 237.8 | 208.7 | 230.5 | 177.6
2463 | 2301 | 124.2 | 252.6 | 250 | 264.7 | 237.5 | 208.5 | 230.1 | 177.5
2464 | 2302 | 124.1 | 252.2 | 249.7 | 264.3 | 237.1 | 208.4 | 229.7 | 177.2
2465 | 2303 | 124 | 251.9 | 249.4 | 264 | 236.8 | 208.2 | 229.3 | 177.1
2466 | 2304 | 123.9 | 251.6 | 249 | 263.7 | 236.4 | 208 | 228.9 | 177.1
2467 | 2305 | 123.8 | 251.3 | 248.7 | 263.4 | 236.1 | 207.8 | 228.5 | 176.9
2468 | 2306 | 123.7 | 250.9 | 248.4 | 263 | 235.8 | 207.6 | 228.2 | 176.7
2469 | 2307 | 123.6 | 250.6 | 248.1 | 262.7 | 235.4 | 207.4 | 227.8 | 176.6
2470 | 2308 | 123.4 | 250.3 | 247.7 | 262.4 | 235.1 | 207.2 | 227.4 | 176.2
2471 | 2309 | 123.3 | 249.9 | 247.4 | 262.1 | 234.7 | 207 | 227 | 176
2472 | 2310 | 123.1 | 249.6 | 247.1 | 261.7 | 234.4 | 206.8 | 226.6 | 175.8
2473 | 2311 | 123 | 249.3 | 246.7 | 261.4 | 234.1 | 206.6 | 226.2 | 175.7
2474 | 2312 | 122.8 | 248.9 | 246.4 | 261.1 | 233.7 | 206.5 | 225.8 | 175.6
2475 | 2313 | 122.7 | 248.6 | 246.1 | 260.7 | 233.4 | 206.3 | 225.5 | 175.6
2476 | 2314 | 122.6 | 248.3 | 245.8 | 260.4 | 233 | 206.1 | 225.1 | 175.5
2477 | 2315 | 122.5 | 248 | 245.5 | 260.1 | 232.7 | 205.9 | 224.7 | 175.3
2478 | 2316 | 122.3 | 247.7 | 245.1 | 259.8 | 232.4 | 205.7 | 224.3 | 175.2
2479 | 2317 | 122.2 | 247.3 | 244.8 | 259.4 | 232 | 205.5 | 223.9 | 175.1
2480 | 2318 | 122.1 | 247 | 244.5 | 259.1 | 231.7 | 205.4 | 223.6 | 175
2481 | 2319 | 121.9 | 246.7 | 244.2 | 258.8 | 231.4 | 205.2 | 223.2 | 174.8
2482 | 2320 | 121.8 | 246.4 | 243.9 | 258.5 | 231 | 205 | 222.8 | 174.6
2483 | 2321 | 121.7 | 246 | 243.5 | 258.1 | 230.7 | 204.8 | 222.5 | 174.5
2484 | 2322 | 121.5 | 245.7 | 243.2 | 257.8 | 230.4 | 204.6 | 222.1 | 174.4
2485 | 2323 | 121.4 | 245.4 | 242.9 | 257.5 | 230 | 204.4 | 221.7 | 174.1
2486 | 2324 | 121.3 | 245.1 | 242.6 | 257.2 | 229.7 | 204.2 | 221.3 | 174
2487 | 2325 | 121.2 | 244.8 | 242.2 | 256.9 | 229.4 | 204.1 | 221 | 173.9
2488 | 2326 | 121.1 | 244.5 | 241.9 | 256.6 | 229 | 203.9 | 220.6 | 173.8
2489 | 2327 | 120.9 | 244.1 | 241.6 | 256.2 | 228.7 | 203.7 | 220.3 | 173.7
2490 | 2328 | 120.8 | 243.8 | 241.3 | 255.9 | 228.4 | 203.5 | 219.9 | 173.6
2491 | 2329 | 120.7 | 243.5 | 241 | 255.6 | 228.1 | 203.4 | 219.5 | 173.3
2492.1 | 2330.1 | 120.5 | 243.2 | 240.7 | 255.3 | 227.7 | 203.2 | 219.2 | 173
2493.1 | 2331.1 | 120.4 | 242.9 | 240.4 | 255 | 227.4 | 203 | 218.8 | 172.9
2494.1 | 2332.1 | 120.3 | 242.6 | 240.1 | 254.6 | 227 | 202.8 | 218.5 | 172.7
2495.1 | 2333.1 | 120.1 | 242.3 | 239.8 | 254.3 | 226.7 | 202.6 | 218.1 | 172.5
2496.1 | 2334.1 | 120 | 241.9 | 239.4 | 254 | 226.4 | 202.4 | 217.7 | 172.2
2497.1 | 2335.1 | 119.9 | 241.6 | 239.1 | 253.7 | 226.1 | 202.2 | 217.4 | 172.1
2498.1 | 2336.1 | 119.9 | 241.3 | 238.8 | 253.4 | 225.8 | 202.1 | 217 | 171.9
2499.1 | 2337.1 | 119.8 | 241 | 238.5 | 253.1 | 225.4 | 201.9 | 216.7 | 171.6
2500.1 | 2338.1 | 119.6 | 240.7 | 238.2 | 252.8 | 225.1 | 201.7 | 216.3 | 171.3
2501.1 | 2339.1 | 119.5 | 240.4 | 237.9 | 252.4 | 224.8 | 201.5 | 216 | 171.1
2502.1 | 2340.1 | 119.4 | 240.1 | 237.6 | 252.1 | 224.5 | 201.3 | 215.6 | 171
2503.1 | 2341.1 | 119.3 | 239.7 | 237.3 | 251.8 | 224.1 | 201.1 | 215.3 | 170.8
2504.1 | 2342.1 | 119.2 | 239.4 | 237 | 251.5 | 223.8 | 200.9 | 214.9 | 170.7
2505.1 | 2343.1 | 119 | 239.1 | 236.7 | 251.2 | 223.5 | 200.7 | 214.6 | 170.6
2506.1 | 2344.1 | 118.9 | 238.8 | 236.4 | 250.9 | 223.2 | 200.6 | 214.2 | 170.4
2507.1 | 2345.1 | 118.8 | 238.5 | 236 | 250.6 | 222.9 | 200.4 | 213.9 | 170.2
2508.1 | 2346.1 | 118.7 | 238.2 | 235.7 | 250.3 | 222.6 | 200.2 | 213.5 | 169.9
2509.1 | 2347.1 | 118.5 | 237.9 | 235.4 | 250 | 222.2 | 200 | 213.2 | 169.8
2510.1 | 2348.1 | 118.4 | 237.6 | 235.1 | 249.7 | 221.9 | 199.8 | 212.8 | 169.6
2511.1 | 2349.1 | 118.3 | 237.3 | 234.8 | 249.3 | 221.6 | 199.6 | 212.5 | 169.5
2512.1 | 2350.1 | 118.1 | 237 | 234.5 | 249 | 221.3 | 199.4 | 212.1 | 169.3
2513.1 | 2351.1 | 118 | 236.7 | 234.2 | 248.7 | 221 | 199.3 | 211.8 | 169.3
2514.1 | 2352.1 | 117.9 | 236.4 | 234 | 248.4 | 220.7 | 199.1 | 211.4 | 169.1
2515.1 | 2353.1 | 117.8 | 236.1 | 233.6 | 248.1 | 220.4 | 198.9 | 211.1 | 168.8
2516.1 | 2354.1 | 117.7 | 235.8 | 233.3 | 247.8 | 220.1 | 198.7 | 210.8 | 168.6
2517.1 | 2355.1 | 117.6 | 235.5 | 233 | 247.5 | 219.8 | 198.5 | 210.4 | 168.4
2518.1 | 2356.1 | 117.5 | 235.2 | 232.7 | 247.2 | 219.5 | 198.3 | 210.1 | 168.2
2519.1 | 2357.1 | 117.4 | 234.8 | 232.4 | 246.9 | 219.1 | 198.1 | 209.8 | 168
2520.1 | 2358.1 | 117.3 | 234.6 | 232.1 | 246.6 | 218.8 | 197.9 | 209.4 | 167.8
2521.1 | 2359.1 | 117.2 | 234.3 | 231.9 | 246.3 | 218.5 | 197.8 | 209.1 | 167.6
2522.1 | 2360.1 | 117.1 | 234 | 231.6 | 246 | 218.2 | 197.6 | 208.8 | 167.5
2523.1 | 2361.1 | 116.9 | 233.7 | 231.3 | 245.7 | 217.9 | 197.4 | 208.4 | 167.4
2524.1 | 2362.1 | 116.8 | 233.4 | 231 | 245.4 | 217.6 | 197.2 | 208.1 | 167.2
2525.1 | 2363.1 | 116.7 | 233.1 | 230.7 | 245.1 | 217.3 | 197.1 | 207.8 | 167.1
2526.1 | 2364.1 | 116.6 | 232.8 | 230.4 | 244.8 | 217 | 196.9 | 207.4 | 167
2527.1 | 2365.1 | 116.5 | 232.5 | 230.1 | 244.5 | 216.7 | 196.7 | 207.1 | 166.9
2528.1 | 2366.1 | 116.4 | 232.2 | 229.8 | 244.2 | 216.4 | 196.5 | 206.8 | 166.8
2529.1 | 2367.1 | 116.2 | 231.9 | 229.5 | 243.9 | 216.1 | 196.3 | 206.5 | 166.5
2530.1 | 2368.1 | 116.1 | 231.6 | 229.2 | 243.6 | 215.8 | 196.2 | 206.1 | 166.2
2531.1 | 2369.1 | 116 | 231.3 | 228.9 | 243.3 | 215.6 | 196 | 205.8 | 166
2532.1 | 2370.1 | 115.9 | 231 | 228.7 | 243 | 215.2 | 195.8 | 205.5 | 165.9
2533.1 | 2371.1 | 115.8 | 230.7 | 228.4 | 242.7 | 214.9 | 195.6 | 205.2 | 165.7
2534.1 | 2372.1 | 115.6 | 230.5 | 228.1 | 242.4 | 214.7 | 195.4 | 204.8 | 165.5
2535.1 | 2373.1 | 115.5 | 230.2 | 227.8 | 242.1 | 214.4 | 195.3 | 204.5 | 165.4
2536.1 | 2374.1 | 115.4 | 229.9 | 227.5 | 241.8 | 214.1 | 195.1 | 204.2 | 165.3
2537.1 | 2375.1 | 115.3 | 229.6 | 227.2 | 241.5 | 213.8 | 194.9 | 203.9 | 165.2
2538.1 | 2376.1 | 115.1 | 229.3 | 226.9 | 241.2 | 213.5 | 194.7 | 203.6 | 165.1
2539.1 | 2377.1 | 115 | 229 | 226.6 | 240.9 | 213.2 | 194.6 | 203.3 | 164.9
2540.1 | 2378.1 | 114.9 | 228.7 | 226.4 | 240.6 | 212.9 | 194.4 | 203 | 164.8
2541.1 | 2379.1 | 114.8 | 228.4 | 226.1 | 240.3 | 212.6 | 194.2 | 202.6 | 164.5
2542.1 | 2380.1 | 114.7 | 228.1 | 225.8 | 240 | 212.4 | 194.1 | 202.3 | 164.4
2543.1 | 2381.1 | 114.6 | 227.9 | 225.5 | 239.7 | 212.1 | 193.9 | 202 | 164.2
2544.1 | 2382.1 | 114.5 | 227.6 | 225.2 | 239.4 | 211.8 | 193.7 | 201.7 | 164
2545.1 | 2383.1 | 114.4 | 227.3 | 225 | 239.1 | 211.5 | 193.5 | 201.4 | 163.9
2546.1 | 2384.1 | 114.3 | 227 | 224.7 | 238.8 | 211.2 | 193.3 | 201.1 | 163.7
2547.1 | 2385.1 | 114.2 | 226.7 | 224.4 | 238.5 | 211 | 193.1 | 200.8 | 163.5
2548.1 | 2386.1 | 114 | 226.4 | 224.1 | 238.3 | 210.7 | 192.9 | 200.5 | 163.4
2549.1 | 2387.1 | 113.9 | 226.2 | 223.8 | 238 | 210.4 | 192.7 | 200.2 | 163.4
2550.1 | 2388.1 | 113.9 | 225.9 | 223.5 | 237.7 | 210.1 | 192.5 | 199.9 | 163.4
2551.1 | 2389.1 | 113.8 | 225.6 | 223.3 | 237.4 | 209.9 | 192.4 | 199.6 | 163.2
2552.1 | 2390.1 | 113.7 | 225.3 | 223 | 237.1 | 209.6 | 192.2 | 199.3 | 163
2553.1 | 2391.1 | 113.6 | 225 | 222.7 | 236.8 | 209.3 | 192 | 199 | 162.8
2554.1 | 2392.1 | 113.5 | 224.8 | 222.5 | 236.5 | 209 | 191.8 | 198.7 | 162.6
2555.1 | 2393.1 | 113.4 | 224.5 | 222.2 | 236.2 | 208.8 | 191.6 | 198.4 | 162.6
2556.1 | 2394.1 | 113.2 | 224.2 | 221.9 | 235.9 | 208.5 | 191.4 | 198.1 | 162.5
2557.1 | 2395.1 | 113.1 | 223.9 | 221.6 | 235.6 | 208.2 | 191.2 | 197.8 | 162.4
2558.1 | 2396.1 | 113 | 223.7 | 221.3 | 235.3 | 208 | 191.1 | 197.5 | 162.3
2559.1 | 2397.1 | 112.9 | 223.4 | 221.1 | 235 | 207.7 | 190.9 | 197.2 | 162.1
2560.1 | 2398.1 | 112.7 | 223.1 | 220.8 | 234.7 | 207.4 | 190.7 | 196.9 | 162
2561.1 | 2399.1 | 112.6 | 222.8 | 220.5 | 234.5 | 207.2 | 190.5 | 196.6 | 161.9
2562.1 | 2400.1 | 112.4 | 222.5 | 220.3 | 234.2 | 206.9 | 190.3 | 196.3 | 161.8
2563.1 | 2401.1 | 112.2 | 222.2 | 220 | 233.9 | 206.6 | 190.1 | 196 | 161.7
2564.1 | 2402.1 | 112.1 | 222 | 219.7 | 233.6 | 206.3 | 190 | 195.7 | 161.4
2565.1 | 2403.1 | 112 | 221.7 | 219.5 | 233.3 | 206.1 | 189.8 | 195.4 | 161.1
2566.1 | 2404.1 | 111.9 | 221.4 | 219.2 | 233 | 205.8 | 189.6 | 195.1 | 161
2567.1 | 2405.1 | 111.8 | 221.2 | 218.9 | 232.7 | 205.6 | 189.5 | 194.9 | 160.9
2568.1 | 2406.1 | 111.7 | 220.9 | 218.7 | 232.4 | 205.3 | 189.3 | 194.6 | 160.8
2569.1 | 2407.1 | 111.5 | 220.6 | 218.4 | 232.2 | 205 | 189.1 | 194.3 | 160.7
2570.1 | 2408.1 | 111.4 | 220.3 | 218.1 | 231.9 | 204.8 | 188.9 | 194 | 160.7
2571.1 | 2409.1 | 111.3 | 220.1 | 217.8 | 231.6 | 204.5 | 188.8 | 193.7 | 160.6
2572.1 | 2410.1 | 111.2 | 219.8 | 217.6 | 231.3 | 204.3 | 188.6 | 193.4 | 160.4
2573.1 | 2411.1 | 111.2 | 219.5 | 217.3 | 231 | 204 | 188.4 | 193.1 | 160.1
2574.1 | 2412.1 | 111.1 | 219.3 | 217.1 | 230.7 | 203.8 | 188.3 | 192.9 | 160
2575.1 | 2413.1 | 111 | 219 | 216.8 | 230.5 | 203.5 | 188.1 | 192.6 | 159.7

## Test Facts
Last row in IRMS data sheets: | 19
Time when Penlight power was initiated: | 162