## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 36
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, Rockbestos Firewall III, control cable. Cable specimens present: Three lengths of cable were monitored for electrical performance, a fourth length of cable monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using six channels - two for each cable (see electrical connection map), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures and six cable temperatures (see thermocouple map). Shroud power: Initiated after 118 seconds of baseline data monitoring. Special Note: Test setup included three thermocouples on the outer surface of the conduit.
DAQ Time | Penlight Time | Event | Interpretation
118 |  | Initated Penlight Heating
1622-1624 |  | Conductors C5 & C6 short to ground at less than 1000 ohms (587 & 624) | Cable C shorts to ground
1635 |  | Conductors C5 & C6 short together at less than 1000 ohms (258) | Cable C is shorted internally
1677 |  | The existing short between conductors C5 & C6 decreases to less than 100 ohms (27)
1700-1703 |  | Conductors B3 & B4 short to ground (150 & 19) | Cable B shorts to ground
1705 |  | Conductors B3 & B4 short together at less than 1000 ohms (231) | Cable B is shorted internally
1706-1708 |  | The existing shorts between conductors C5 & C6 and ground decrease to less than 100 ohms (16 & 16)
1848 |  | Conductors A1 & A2 short together at less than 100 ohms (9) | Cable A is shorted internally
1854-1863 |  | Conductors A1 & A2 both short to ground (110 & 95) | Cable A shorts to ground
2228 |  | Power to Penlight shutoff
Additional Observations
Observation 1 | Cable failures progressed as expected during this test: the two lower cables (B & C) shorted to ground well before the top cable (A)
Observation 2 | It took 1504 seconds (25.1 min.) from the start of Penlight heating for the first short to ground failure to occur, and it took 1517 s (25.3 min.) for the first internal short failure.
Observation 3 | No cable to cable interations occurred prior to one or both cable shorting to ground or internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable and conduit
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Outer surface of conduit
| TC2 | = | Conduit 2 | Outer surface of conduit at mid-point
| TC3 | = | Conduit 3 | Outer surface of conduit
| TC4 | = | Cable 1 | Within cable just below cable jacket, center position
| TC5 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC6 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC7 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC8 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC9 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
All Cables = XLPE, item #10
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 36 |  |  | 2006-08-29 | 13:45
XLPE | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | C5-C6 | Penlight Time | Minimums
-117.5 | 211201.9994 | -115 | 252337.9994 | -112 | 249737.9994 | -109.5 | 249237.9994 | -106.5 | 251337.9994 | -104 | 253737.9994 | -101 | 211201.9994 | -98.5 | 250337.9994 | -95.5 | 251937.9994 | -92.5 | 253337.9994 | -90 | 253237.9994 | -87 | 253237.9994 | -84.5 | 251737.9994 | -81.5 | 252037.9994 | -78.5 | 251937.9994 | -117.5 | #REF!
-76 | 211201.9994 | -73 | 252337.9994 | -70.5 | 249737.9994 | -67.5 | 249237.9994 | -64.5 | 251337.9994 | -61.5 | 253737.9994 | -59 | 211201.9994 | -56.5 | 250337.9994 | -53.5 | 251937.9994 | -50.5 | 253337.9994 | -47.5 | 253237.9994 | -45 | 253237.9994 | -42.5 | 251737.9994 | -39.5 | 252037.9994 | -36.5 | 251937.9994 | -76 | #REF!
-34 | 211201.9994 | -31 | 252337.9994 | -28 | 249737.9994 | -25.5 | 249237.9994 | -22.5 | 251337.9994 | -20 | 253737.9994 | -17 | 211201.9994 | -14.5 | 250337.9994 | -11.5 | 251937.9994 | -8.5 | 253337.9994 | -6 | 253237.9994 | -3 | 253237.9994 | -0.5 | 251737.9994 | 2.5 | 252037.9994 | 5.5 | 251937.9994 | -34 | #REF!
8 | 211201.9994 | 11 | 252337.9994 | 13.5 | 249737.9994 | 16.5 | 249237.9994 | 19.5 | 251337.9994 | 22 | 253737.9994 | 25 | 211201.9994 | 27.5 | 250337.9994 | 30.5 | 251937.9994 | 33.5 | 253337.9994 | 36 | 253237.9994 | 39 | 253237.9994 | 41.5 | 251737.9994 | 44.5 | 252037.9994 | 47.5 | 251937.9994 | 8 | #REF!
50 | 211201.9994 | 53 | 252337.9994 | 55.5 | 249737.9994 | 58.5 | 249237.9994 | 61.5 | 251337.9994 | 64 | 253737.9994 | 67 | 211201.9994 | 69.5 | 250337.9994 | 72.5 | 251937.9994 | 75.5 | 253337.9994 | 78 | 253237.9994 | 81 | 253237.9994 | 83.5 | 251737.9994 | 86.5 | 252037.9994 | 89.5 | 251937.9994 | 50 | #REF!
92 | 211201.9994 | 95 | 252337.9994 | 97.5 | 249737.9994 | 100.5 | 249237.9994 | 103.5 | 251337.9994 | 106 | 253737.9994 | 109 | 211201.9994 | 111.5 | 250337.9994 | 114.5 | 251937.9994 | 117.5 | 253337.9994 | 120 | 253237.9994 | 123 | 253237.9994 | 125.5 | 251737.9994 | 128.5 | 252037.9994 | 131.5 | 251937.9994 | 92 | #REF!
134 | 211201.9994 | 137 | 252337.9994 | 139.5 | 249737.9994 | 142.5 | 249237.9994 | 145.5 | 251337.9994 | 148 | 253737.9994 | 151 | 211201.9994 | 153.5 | 250337.9994 | 156.5 | 251937.9994 | 159.5 | 253337.9994 | 162 | 253237.9994 | 165 | 253237.9994 | 167.5 | 251737.9994 | 170.5 | 252037.9994 | 173.5 | 251937.9994 | 134 | #REF!
176 | 211201.9994 | 179 | 252337.9994 | 181.5 | 249737.9994 | 184.5 | 249237.9994 | 187.5 | 251337.9994 | 190 | 253737.9994 | 193 | 211201.9994 | 195.5 | 250337.9994 | 198.5 | 251937.9994 | 201.5 | 253337.9994 | 204 | 253237.9994 | 207 | 253237.9994 | 209.5 | 251737.9994 | 212.5 | 252037.9994 | 215.5 | 251937.9994 | 176 | #REF!
218 | 211201.9994 | 221 | 252337.9994 | 223.5 | 249737.9994 | 226.5 | 249237.9994 | 229.5 | 251337.9994 | 232 | 253737.9994 | 235 | 211201.9994 | 237.5 | 250337.9994 | 240.5 | 251937.9994 | 243.5 | 253337.9994 | 246 | 253237.9994 | 249 | 253237.9994 | 251.5 | 251737.9994 | 254.5 | 252037.9994 | 257.5 | 251937.9994 | 218 | #REF!
261 | 211201.9994 | 263 | 252337.9994 | 265.5 | 249737.9994 | 268.5 | 249237.9994 | 271.5 | 251337.9994 | 274 | 253737.9994 | 277 | 211201.9994 | 279.5 | 250337.9994 | 282.5 | 251937.9994 | 285.5 | 253337.9994 | 288 | 253237.9994 | 291 | 253237.9994 | 293.5 | 251737.9994 | 296.5 | 252037.9994 | 299.5 | 251937.9994 | 261 | #REF!
302 | 211201.9994 | 305 | 252337.9994 | 307.5 | 249737.9994 | 310.5 | 249237.9994 | 313.5 | 251337.9994 | 316 | 253737.9994 | 319 | 211201.9994 | 321.5 | 250337.9994 | 324.5 | 251937.9994 | 327.5 | 253337.9994 | 330 | 253237.9994 | 333 | 253237.9994 | 335.5 | 251737.9994 | 338.5 | 252037.9994 | 341.5 | 251937.9994 | 302 | #REF!
344 | 211201.9994 | 347 | 252337.9994 | 349.5 | 249737.9994 | 352.5 | 249237.9994 | 355.5 | 251337.9994 | 358 | 253737.9994 | 361 | 211201.9994 | 363.5 | 250337.9994 | 366.5 | 251937.9994 | 369.5 | 253337.9994 | 372 | 253237.9994 | 375 | 253237.9994 | 377.5 | 251737.9994 | 380.5 | 252037.9994 | 383.5 | 251937.9994 | 344 | #REF!
386 | 211201.9994 | 389 | 252337.9994 | 391.5 | 249737.9994 | 394.5 | 249237.9994 | 397.5 | 251337.9994 | 400 | 253737.9994 | 403 | 211201.9994 | 405.5 | 250337.9994 | 408.5 | 251937.9994 | 411.5 | 253337.9994 | 414 | 253237.9994 | 417 | 253237.9994 | 419.5 | 251737.9994 | 422.5 | 252037.9994 | 425.5 | 251937.9994 | 386 | #REF!
428 | 211201.9994 | 431 | 252337.9994 | 433.5 | 249737.9994 | 436.5 | 249237.9994 | 439.5 | 251337.9994 | 442 | 253737.9994 | 445 | 211201.9994 | 447.5 | 250337.9994 | 450.5 | 251937.9994 | 453.5 | 253337.9994 | 456 | 253237.9994 | 459 | 253237.9994 | 461.5 | 251737.9994 | 464.5 | 252037.9994 | 467.5 | 251937.9994 | 428 | #REF!
470 | 211201.9994 | 473 | 252337.9994 | 475.5 | 249737.9994 | 478.5 | 249237.9994 | 481.5 | 251337.9994 | 484 | 253737.9994 | 487 | 211201.9994 | 489.5 | 250337.9994 | 492.5 | 251937.9994 | 495.5 | 253337.9994 | 498 | 253237.9994 | 501 | 253237.9994 | 503.5 | 251737.9994 | 506.5 | 252037.9994 | 509.5 | 251937.9994 | 470 | #REF!
512 | 211201.9994 | 515 | 252337.9994 | 517.5 | 249737.9994 | 520.5 | 249237.9994 | 523.5 | 251337.9994 | 526 | 253737.9994 | 529 | 211201.9994 | 531.5 | 250337.9994 | 534.5 | 251937.9994 | 537 | 253337.9994 | 540 | 253237.9994 | 543 | 253237.9994 | 545.5 | 251737.9994 | 548.5 | 252037.9994 | 551.5 | 251937.9994 | 512 | #REF!
554 | 211201.9994 | 557 | 252337.9994 | 559.5 | 249737.9994 | 562.5 | 249237.9994 | 565.5 | 251337.9994 | 568 | 253737.9994 | 571 | 211201.9994 | 573.5 | 250337.9994 | 576.5 | 251937.9994 | 579.5 | 253337.9994 | 582 | 253237.9994 | 585 | 253237.9994 | 587.5 | 251737.9994 | 590.5 | 252037.9994 | 593.5 | 251937.9994 | 554 | #REF!
596 | 211201.9994 | 598.5 | 252337.9994 | 601.5 | 249737.9994 | 604.5 | 249237.9994 | 607 | 251337.9994 | 610 | 253737.9994 | 613 | 211201.9994 | 615.5 | 250337.9994 | 618.5 | 251937.9994 | 621.5 | 253337.9994 | 624 | 253237.9994 | 627 | 253237.9994 | 629.5 | 251737.9994 | 632.5 | 252037.9994 | 635.5 | 251937.9994 | 596 | #REF!
638 | 211201.9994 | 641 | 252337.9994 | 643.5 | 249737.9994 | 646.5 | 249237.9994 | 649.5 | 251337.9994 | 652 | 253737.9994 | 655 | 211201.9994 | 657.5 | 250337.9994 | 660.5 | 251937.9994 | 663.5 | 253337.9994 | 666 | 253237.9994 | 669 | 253237.9994 | 671.5 | 251737.9994 | 674.5 | 252037.9994 | 677.5 | 251937.9994 | 638 | #REF!
680 | 211201.9994 | 683 | 252337.9994 | 685.5 | 249737.9994 | 688.5 | 249237.9994 | 691.5 | 251337.9994 | 694 | 253737.9994 | 697 | 211201.9994 | 699.5 | 250337.9994 | 702.5 | 251937.9994 | 705.5 | 253337.9994 | 708 | 253237.9994 | 711 | 253237.9994 | 713.5 | 251737.9994 | 716.5 | 252037.9994 | 719 | 251937.9994 | 680 | #REF!
722 | 211201.9994 | 725 | 252337.9994 | 727.5 | 249737.9994 | 730.5 | 249237.9994 | 733.5 | 251337.9994 | 736 | 253737.9994 | 739 | 211201.9994 | 741.5 | 250337.9994 | 744.5 | 251937.9994 | 747 | 253138.0789 | 750 | 253237.9994 | 753 | 253237.9994 | 755.5 | 251737.9994 | 758.5 | 252037.9994 | 761.5 | 251937.9994 | 722 | #REF!
764 | 211201.9994 | 766.5 | 252337.9994 | 769.5 | 249737.9994 | 772.5 | 249237.9994 | 775.5 | 251337.9994 | 778 | 253737.9994 | 781 | 211201.9994 | 783.5 | 250337.9994 | 786.5 | 251937.9994 | 789.5 | 253337.9994 | 792 | 253237.9994 | 795 | 253237.9994 | 797.5 | 251737.9994 | 800.5 | 252037.9994 | 803.5 | 251937.9994 | 764 | #REF!
806 | 211201.9994 | 809 | 252337.9994 | 811.5 | 249737.9994 | 814.5 | 249237.9994 | 817 | 251337.9994 | 820 | 253737.9994 | 822.5 | 211201.9994 | 825.5 | 250337.9994 | 828.5 | 251937.9994 | 831.5 | 253337.9994 | 834 | 253237.9994 | 837 | 253237.9994 | 839.5 | 251737.9994 | 842.5 | 252037.9994 | 845.5 | 251937.9994 | 806 | #REF!
848 | 211201.9994 | 851 | 252337.9994 | 853.5 | 249737.9994 | 856.5 | 249237.9994 | 859.5 | 251337.9994 | 862 | 253737.9994 | 865 | 211201.9994 | 867.5 | 250337.9994 | 870.5 | 251937.9994 | 873 | 253337.9994 | 876 | 253237.9994 | 878.5 | 253237.9994 | 881.5 | 251737.9994 | 884.5 | 252037.9994 | 887 | 251937.9994 | 848 | #REF!
890 | 211201.9994 | 893 | 252337.9994 | 895.5 | 249737.9994 | 898.5 | 249237.9994 | 901 | 251337.9994 | 904 | 253737.9994 | 906.5 | 211201.9994 | 909.5 | 250337.9994 | 912.5 | 251937.9994 | 915.5 | 253337.9994 | 918 | 253237.9994 | 920.5 | 253237.9994 | 923.5 | 251737.9994 | 926.5 | 252037.9994 | 929 | 251937.9994 | 890 | #REF!
932 | 211201.9994 | 934.5 | 252337.9994 | 937.5 | 249737.9994 | 940.5 | 249237.9994 | 943 | 251337.9994 | 946 | 253737.9994 | 948.5 | 211201.9994 | 951.5 | 250337.9994 | 954.5 | 251937.9994 | 957 | 253337.9994 | 960 | 253237.9994 | 962.5 | 253237.9994 | 965.5 | 251737.9994 | 968.5 | 252037.9994 | 971 | 251937.9994 | 932 | #REF!
974 | 211201.9994 | 976.5 | 252337.9994 | 979.5 | 249737.9994 | 982.5 | 249237.9994 | 985.5 | 251337.9994 | 988 | 253737.9994 | 991 | 211201.9994 | 993.5 | 250337.9994 | 996.5 | 251937.9994 | 999.5 | 253337.9994 | 1002 | 253237.9994 | 1005 | 253237.9994 | 1007.5 | 251737.9994 | 1010.5 | 252037.9994 | 1013 | 251937.9994 | 974 | #REF!
1016 | 211201.9994 | 1018.5 | 252337.9994 | 1021.5 | 249737.9994 | 1024.5 | 249237.9994 | 1027 | 251337.9994 | 1030 | 253737.9994 | 1032.5 | 211201.9994 | 1035.5 | 250337.9994 | 1038.5 | 251937.9994 | 1041 | 253337.9994 | 1044 | 253237.9994 | 1046.5 | 253237.9994 | 1049.5 | 251737.9994 | 1052.5 | 252037.9994 | 1055.5 | 251937.9994 | 1016 | #REF!
1058 | 211201.9994 | 1061 | 252337.9994 | 1063.5 | 249737.9994 | 1066.5 | 249237.9994 | 1069.5 | 251337.9994 | 1072 | 253737.9994 | 1075 | 211201.9994 | 1077.5 | 250337.9994 | 1080.5 | 251937.9994 | 1083 | 253337.9994 | 1086 | 253237.9994 | 1088.5 | 253237.9994 | 1091.5 | 251737.9994 | 1094.5 | 252037.9994 | 1097 | 251937.9994 | 1058 | #REF!
1100 | 211201.9994 | 1102.5 | 252337.9994 | 1105.5 | 249737.9994 | 1108.5 | 249237.9994 | 1111 | 251337.9994 | 1114 | 253737.9994 | 1116.5 | 211201.9994 | 1119.5 | 250337.9994 | 1122.5 | 251937.9994 | 1125.5 | 253337.9994 | 1128 | 253237.9994 | 1130.5 | 253237.9994 | 1133.5 | 251737.9994 | 1136.5 | 252037.9994 | 1139 | 251937.9994 | 1100 | #REF!
1142 | 211201.9994 | 1144.5 | 252337.9994 | 1147.5 | 249737.9994 | 1150.5 | 249237.9994 | 1153 | 251337.9994 | 1156 | 253737.9994 | 1158 | 211201.9994 | 1161.5 | 250337.9994 | 1164.5 | 251937.9994 | 1167.5 | 253337.9994 | 1170 | 253237.9994 | 1172.5 | 253237.9994 | 1175.5 | 251737.9994 | 1178.5 | 252037.9994 | 1181 | 251937.9994 | 1142 | #REF!
1184 | 211201.9994 | 1186.5 | 252337.9994 | 1189.5 | 249737.9994 | 1192.5 | 249237.9994 | 1195 | 251337.9994 | 1198 | 253737.9994 | 1200.5 | 211201.9994 | 1203.5 | 250337.9994 | 1206.5 | 251937.9994 | 1209 | 253337.9994 | 1212 | 253237.9994 | 1214.5 | 253237.9994 | 1217.5 | 251737.9994 | 1220.5 | 252037.9994 | 1223.5 | 251937.9994 | 1184 | #REF!
1226 | 211201.9994 | 1228.5 | 252337.9994 | 1231.5 | 249737.9994 | 1234.5 | 249237.9994 | 1237 | 251337.9994 | 1240 | 253737.9994 | 1242.5 | 211201.9994 | 1245.5 | 250337.9994 | 1248.5 | 251937.9994 | 1251 | 253337.9994 | 1254 | 253237.9994 | 1256.5 | 253237.9994 | 1259.5 | 251737.9994 | 1262.5 | 252037.9994 | 1265 | 251937.9994 | 1226 | #REF!
1268 | 211201.9994 | 1270.5 | 252337.9994 | 1273.5 | 249737.9994 | 1276.5 | 249237.9994 | 1279.5 | 251337.9994 | 1282 | 253737.9994 | 1284.5 | 211201.9994 | 1287.5 | 250337.9994 | 1290.5 | 251937.9994 | 1293 | 253337.9994 | 1296 | 253237.9994 | 1299 | 253237.9994 | 1301.5 | 251737.9994 | 1304.5 | 252037.9994 | 1307 | 251937.9994 | 1268 | #REF!
1310 | 211201.9994 | 1312.5 | 252337.9994 | 1315.5 | 249737.9994 | 1318.5 | 249237.9994 | 1321 | 251337.9994 | 1324 | 253737.9994 | 1326.5 | 211201.9994 | 1329.5 | 250337.9994 | 1332.5 | 251937.9994 | 1335 | 253337.9994 | 1338 | 253237.9994 | 1340.5 | 253237.9994 | 1343.5 | 251737.9994 | 1346.5 | 252037.9994 | 1349 | 251937.9994 | 1310 | #REF!
1352 | 211201.9994 | 1354.5 | 252337.9994 | 1357.5 | 249737.9994 | 1360.5 | 249237.9994 | 1363 | 251337.9994 | 1366 | 253737.9994 | 1368.5 | 211201.9994 | 1371.5 | 250337.9994 | 1374.5 | 251937.9994 | 1377 | 253337.9994 | 1380 | 253237.9994 | 1382.5 | 253237.9994 | 1385.5 | 251538.0794 | 1388.5 | 252037.9994 | 1391 | 249941.5312 | 1352 | #REF!
1394 | 211201.9994 | 1396.5 | 252337.9994 | 1399.5 | 249737.9994 | 1402.5 | 249237.9994 | 1405 | 251337.9994 | 1408 | 253737.9994 | 1410.5 | 211201.9994 | 1413.5 | 250337.9994 | 1416.5 | 251937.9994 | 1419 | 253337.9994 | 1422 | 253237.9994 | 1424.5 | 253237.9994 | 1427.5 | 251737.9994 | 1430.5 | 252037.9994 | 1433 | 4095.4046 | 1394 | #REF!
1436 | 211201.9994 | 1438.5 | 252337.9994 | 1441.5 | 249737.9994 | 1444.5 | 249237.9994 | 1447 | 251337.9994 | 1450 | 253737.9994 | 1452.5 | 211201.9994 | 1455.5 | 250337.9994 | 1458.5 | 251937.9994 | 1461 | 253337.9994 | 1464 | 253237.9994 | 1466.5 | 253237.9994 | 1469.5 | 251737.9994 | 1472.5 | 252037.9994 | 1475 | 1145.9523 | 1436 | #REF!
1478 | 211201.9994 | 1480.5 | 252337.9994 | 1483.5 | 249737.9994 | 1486.5 | 249237.9994 | 1489 | 251337.9994 | 1492 | 253737.9994 | 1494.5 | 211201.9994 | 1497.5 | 250337.9994 | 1500.5 | 251937.9994 | 1503 | 126618.9988 | 1506 | 253237.9994 | 1508.5 | 253237.9994 | 1511.5 | 251737.9994 | 1514.5 | 252037.9994 | 1517 | 257.907 | 1478 | #REF!
1520 | 210902.142 | 1522.5 | 252337.9994 | 1525.5 | 249737.9994 | 1528.5 | 249237.9994 | 1531 | 251337.9994 | 1534 | 253737.9994 | 1536.5 | 211201.9994 | 1539.5 | 250337.9994 | 1542.5 | 251937.9994 | 1545 | 62362.6663 | 1548 | 253237.9994 | 1550.5 | 126568.9988 | 1553.5 | 251737.9994 | 1556.5 | 125968.9988 | 1559 | 26.5588 | 1520 | #REF!
1562 | 105351.1183 | 1564.5 | 252337.9994 | 1567.5 | 249737.9994 | 1570.5 | 249237.9994 | 1573 | 251337.9994 | 1576 | 126818.9988 | 1578 | 211201.9994 | 1581.5 | 250337.9994 | 1584.5 | 125918.9988 | 1587 | 230.7487 | 1590 | 182638.0679 | 1592.5 | 149.2212 | 1595.5 | 17.7811 | 1598.5 | 31.8975 | 1601 | 431.6538 | 1562 | #REF!
1604 | 210502.7099 | 1606.5 | 126118.9988 | 1609.5 | 124818.9988 | 1612.5 | 124568.9988 | 1615 | 125618.9988 | 1618 | 126818.9988 | 1620.5 | 70333.9982 | 1623.5 | 125118.9988 | 1626.5 | 125918.9988 | 1629 | 7555.1949 | 1632 | 18.0909 | 1634.5 | 25.576 | 1637.5 | 14.1375 | 1640.5 | 15.3027 | 1643 | 890.7348 | 1604 | #REF!
1646 | 105151.4969 | 1648.5 | 126118.9988 | 1651.5 | 124818.9988 | 1654.5 | 124568.9988 | 1657 | 125618.9988 | 1660 | 84512.6648 | 1662.5 | 105550.9988 | 1665.5 | 125118.9988 | 1668.5 | 83912.6648 | 1671 | 8611.1169 | 1674 | 3.0763 | 1676.5 | 0.72205 | 1679.5 | 24.2545 | 1682.5 | 25.9392 | 1685 | 22.5478 | 1646 | #REF!
1688 | 4378.6709 | 1690.5 | 126118.9988 | 1693.5 | 83179.3315 | 1696.5 | 124568.9988 | 1699 | 125618.9988 | 1702 | 126818.9988 | 1704.5 | 105550.9988 | 1707.5 | 125118.9988 | 1710.5 | 125918.9988 | 1713 | 1550.4243 | 1716 | 1.1846 | 1718.5 | 18.4331 | 1721.5 | 16.2083 | 1724.5 | 14.922 | 1727 | 387.6838 | 1688 | #REF!
1730 | 9.3277 | 1732.5 | 17797.7813 | 1735.5 | 83179.3315 | 1738.5 | 83012.6648 | 1741 | 83712.6648 | 1744 | 126818.9988 | 1746.5 | 70333.9982 | 1749.5 | 125118.9988 | 1752.5 | 125918.9988 | 1755 | 12.702 | 1758 | 5.5383 | 1760.5 | 9.3769 | 1763.5 | 18.4104 | 1766.5 | 23.5252 | 1769 | 23.3512 | 1730 | #REF!
1772 | 17.0788 | 1774.5 | 27735.9551 | 1777.5 | 83179.3315 | 1780.5 | 124568.9988 | 1783 | 125618.9988 | 1786 | 126818.9988 | 1788.5 | 105550.9988 | 1791.5 | 125118.9988 | 1794.5 | 125918.9988 | 1797 | 381.2934 | 1800 | 11.7298 | 1802.5 | 9.8694 | 1805.5 | 8.2838 | 1808.5 | 28.7161 | 1811 | 638.9864 | 1772 | #REF!
1814 | 6.2363 | 1816.5 | 17398.2567 | 1819.5 | 124818.9988 | 1822.5 | 124568.9988 | 1825 | 125618.9988 | 1828 | 126818.9988 | 1830.5 | 105550.9988 | 1833.5 | 125118.9988 | 1836.5 | 125918.9988 | 1839 | 24.8615 | 1842 | 20.0557 | 1844.5 | 6851.8479 | 1847.5 | 25.7232 | 1850.5 | 19.7739 | 1853 | 17.7619 | 1814 | #REF!
1856 | 9.6402 | 1858.5 | 24389.9368 | 1861.5 | 83179.3315 | 1864.5 | 83012.6648 | 1867 | 125618.9988 | 1870 | 84512.6648 | 1872.5 | 105550.9988 | 1875.5 | 125118.9988 | 1878.5 | 125918.9988 | 1881 | 13.119 | 1884 | 17.3561 | 1886.5 | 18.2048 | 1889.5 | 0.15836 | 1892.5 | 5.9971 | 1895 | 22.2415 | 1856 | #REF!
1898 | 21.2996 | 1900.5 | 1367.3333 | 1903.5 | 238324.5661 | 1906.5 | 124568.9988 | 1909 | 125618.9988 | 1912 | 84512.6648 | 1914.5 | 70333.9982 | 1917.5 | 125118.9988 | 1920.5 | 125918.9988 | 1923 | 14.0151 | 1926 | 14.5566 | 1928.5 | 0.72321 | 1931.5 | 8.7697 | 1934.5 | 26.4591 | 1937 | 21.0909 | 1898 | #REF!
1940 | 20.1343 | 1942.5 | 28762.4984 | 1945.5 | 124818.9988 | 1948.5 | 124568.9988 | 1951 | 125618.9988 | 1954 | 84512.6648 | 1956.5 | 105550.9988 | 1959.5 | 125118.9988 | 1962.5 | 125918.9988 | 1965 | 28.5763 | 1968 | 13.2309 | 1970.5 | 11.6787 | 1973.5 | 26.765 | 1976.5 | 4.7134 | 1979 | 8.033 | 1940 | #REF!
1982 | 2.1774 | 1984.5 | 93533.0304 | 1987.5 | 83179.3315 | 1990.5 | 124568.9988 | 1993 | 125618.9988 | 1996 | 126818.9988 | 1998.5 | 105550.9988 | 2001.5 | 125118.9988 | 2004.5 | 125918.9988 | 2007 | 11.3669 | 2009.5 | 16.7968 | 2012.5 | 0.18057 | 2015.5 | 1.3379 | 2018 | 4.6229 | 2021 | 213.2022 | 1982 | #REF!
2024 | 7.4212 | 2026.5 | 11754.9721 | 2029.5 | 41249.8825 | 2032.5 | 124568.9988 | 2035 | 125618.9988 | 2038 | 126818.9988 | 2040.5 | 70333.9982 | 2043.5 | 125118.9988 | 2046.5 | 125918.9988 | 2049 | 19.9863 | 2052 | 22.9399 | 2054.5 | 3.7367 | 2057.5 | 10.9586 | 2060.5 | 9.837 | 2063 | 9.5946 | 2024 | #REF!
2066 | 15.8665 | 2068.5 | 8808.4784 | 2071.5 | 124818.9988 | 2074 | 124568.9988 | 2077 | 125618.9988 | 2080 | 126818.9988 | 2082.5 | 105550.9988 | 2085.5 | 125118.9988 | 2088.5 | 125918.9988 | 2091 | 0.6787 | 2094 | 21.8427 | 2096.5 | 9.82 | 2099.5 | 7.1819 | 2102.5 | 2.2337 | 2105 | 6.0008 | 2066 | #REF!
2108 | 13.2528 | 2110.5 | 10905.9824 | 2113.5 | 124818.9988 | 2116.5 | 124568.9988 | 2119 | 125618.9988 | 2121.5 | 126818.9988 | 2124.5 | 105550.9988 | 2127.5 | 125118.9988 | 2130.5 | 125918.9988 | 2133 | 3.1175 | 2135.5 | 22.328 | 2138.5 | 18.95 | 2141.5 | 28.3595 | 2144.5 | 13.2124 | 2147 | 0.87454 | 2108 | #REF!
2150 | 11.6617 | 2152.5 | 14751.4064 | 2155.5 | 31220.5774 | 2158 | 45081.0176 | 2161 | 83712.6648 | 2164 | 1760.0476 | 2166.5 | 105550.9988 | 2169.5 | 125118.9988 | 2172.5 | 125918.9988 | 2175 | 0.39743 | 2177.5 | 1.0581 | 2180.5 | 16.2978 | 2183.5 | 1.5513 | 2186 | 2.6682 | 2189 | 6.3266 | 2150 | #REF!
2191.5 | 8.7799 | 2194.5 | 26137.8568 | 2197.5 | 124818.9988 | 2200 | 124568.9988 | 2203 | 125618.9988 | 2206 | 126818.9988 | 2208.5 | 105550.9988 | 2211.5 | 125118.9988 | 2214.5 | 125918.9988 | 2217 | 0.8882 | 2220 | 0.88586 | 2222.5 | 17.6941 | 2225.5 | 25.3369 | 2228.5 | 7.5016 | 2231 | 4.2652 | 2191.5 | #REF!
2233.5 | 20.188 | 2236.5 | 19595.6419 | 2239.5 | 33978.8098 | 2242.5 | 124568.9988 | 2245 | 125618.9988 | 2248 | 126818.9988 | 2250.5 | 105550.9988 | 2253.5 | 125118.9988 | 2256.5 | 125918.9988 | 2259 | 0.38679 | 2262 | 0.72321 | 2264.5 | 20.2321 | 2267.5 | 21.174 | 2270.5 | 26.7206 | 2273 | 184.8358 | 2233.5 | #REF!
2275.5 | 18.83 | 2278.5 | 2216.323 | 2281.5 | 78488.8958 | 2284 | 43429.6234 | 2287 | 125618.9988 | 2289.5 | 126818.9988 | 2292.5 | 105550.9988 | 2295.5 | 250337.9994 | 2298 | 125918.9988 | 2301 | 15.0871 | 2303.5 | 23.4957 | 2306.5 | 7.4957 | 2309.5 | 13.8704 | 2312 | 19.0733 | 2315 | 0.65766 | 2275.5 | #REF!
2318 | 11.3175 | 2320.5 | 2588.0089 | 2323.5 | 124818.9988 | 2326.5 | 124568.9988 | 2329 | 125618.9988 | 2331.5 | 126818.9988 | 2334.5 | 105550.9988 | 2337.5 | 125118.9988 | 2340 | 125918.9988 | 2343 | 10.9622 | 2345.5 | 12.865 | 2348.5 | 0.88586 | 2351.5 | 26.8964 | 2354 | 11.8077 | 2357 | 21.5728 | 2318 | #REF!
2360 | 21.6206 | 2362.5 | 30592.4597 | 2365.5 | 83179.3315 | 2368.5 | 124568.9988 | 2371 | 125618.9988 | 2373.5 | 126818.9988 | 2376.5 | 105550.9988 | 2379.5 | 125118.9988 | 2382 | 125918.9988 | 2385 | 1.2251 | 2387.5 | 5.8598 | 2390.5 | 18.7198 | 2393.5 | 2.4572 | 2396 | 28.245 | 2399 | 27.1959 | 2360 | #REF!
2401.5 | 4.5779 | 2404.5 | 1658.1897 | 2407.5 | 124818.9988 | 2410 | 83012.6648 | 2413 | 125618.9988 | 2416 | 126818.9988 | 2418.5 | 105550.9988 | 2421.5 | 125118.9988 | 2424 | 125918.9988 | 2427 | 3.513 | 2430 | 24.8117 | 2432.5 | 7.9721 | 2435.5 | 27.2922 | 2438 | 8.0764 | 2441 | 27.1299 | 2401.5 | #REF!
2444 | 2.7856 | 2446.5 | 215517.7065 | 2449.5 | 124818.9988 | 2452.5 | 124568.9988 | 2455 | 125618.9988 | 2457.5 | 126818.9988 | 2460.5 | 105550.9988 | 2463.5 | 125118.9988 | 2466 | 125918.9988 | 2469 | 14.3347 | 2471.5 | 27.0011 | 2474.5 | 16.4083 | 2477.5 | 0.58612 | 2481 | 5.0771 | 2483 | 12.4346 | 2444 | #REF!
2485.5 | 2.8607 | 2488.5 | 61212.3774 | 2491.5 | 124818.9988 | 2494 | 124568.9988 | 2497 | 83712.6648 | 2499.5 | 126818.9988 | 2502.5 | 105550.9988 | 2505.5 | 125118.9988 | 2508.5 | 125918.9988 | 2511 | 101.9936 | 2513.5 | 1.2269 | 2516.5 | 15.3665 | 2519.5 | 8.3807 | 2522.5 | 2.277 | 2525 | 944.472 | 2485.5 | #REF!

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 36 |  |  | 2006-08-29 | 13:45
XLPE | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | Minimums Overall
-112.1 | 211202 |  | -103.3 | 211202 | -97.7 | 252338 | -94.3 | 211202 | -92.2 | 249238 | -89.8 | 251338 | -112.1 | 211202
-70.3 | 211202 |  | -61.3 | 105551 | -55.5 | 252338 | -52.4 | 211202 | -50.1 | 249238 | -47.8 | 251338 | -70.3 | 105551
-28.2 | 211202 |  | -19.4 | 211202 | -13.7 | 252338 | -10.3 | 211202 | -8.2 | 249238 | -5.8 | 251338 | -28.2 | 211202
13.7 | 211202 |  | 22.6 | 211202 | 28.3 | 252338 | 31.6 | 211202 | 33.8 | 249238 | 36.2 | 251338 | 13.7 | 211202
55.7 | 211202 |  | 64.6 | 211202 | 70.3 | 252338 | 73.6 | 211202 | 75.8 | 249238 | 78.2 | 251338 | 55.7 | 211202
97.7 | 211202 |  | 106.6 | 211202 | 112.3 | 252338 | 115.6 | 211202 | 117.8 | 249238 | 120.2 | 251338 | 97.7 | 211202
139.7 | 211202 |  | 148.6 | 211202 | 154.3 | 252338 | 157.6 | 211202 | 159.8 | 249238 | 162.2 | 251338 | 139.7 | 211202
181.7 | 211202 |  | 190.6 | 211202 | 196.3 | 252338 | 199.6 | 211202 | 201.8 | 249238 | 204.2 | 251338 | 181.7 | 211202
223.7 | 211202 |  | 232.6 | 211202 | 238.3 | 252338 | 241.6 | 211202 | 243.8 | 249238 | 246.2 | 251338 | 223.7 | 211202
265.9 | 211202 |  | 274.8 | 211202 | 280.3 | 252338 | 283.6 | 211202 | 285.8 | 249238 | 288.2 | 251338 | 265.9 | 211202
307.7 | 211202 |  | 316.6 | 211202 | 322.3 | 252338 | 325.6 | 211202 | 327.8 | 249238 | 330.2 | 251338 | 307.7 | 211202
349.7 | 211202 |  | 358.6 | 211202 | 364.3 | 252338 | 367.6 | 211202 | 369.8 | 249238 | 372.2 | 251338 | 349.7 | 211202
391.7 | 211202 |  | 400.6 | 211202 | 406.3 | 252338 | 409.6 | 211202 | 411.8 | 249238 | 414.2 | 251338 | 391.7 | 211202
433.7 | 211202 |  | 442.6 | 211202 | 448.3 | 252338 | 451.6 | 211202 | 453.8 | 249238 | 456.2 | 251338 | 433.7 | 211202
475.7 | 211202 |  | 484.6 | 211202 | 490.3 | 252338 | 493.6 | 211202 | 495.8 | 249238 | 498.2 | 251338 | 475.7 | 211202
517.7 | 211202 |  | 526.6 | 211202 | 532.2 | 252338 | 535.5 | 211202 | 537.8 | 249238 | 540.2 | 251338 | 517.7 | 211202
559.7 | 211202 |  | 568.6 | 211202 | 574.3 | 252338 | 577.6 | 211202 | 579.8 | 249238 | 582.2 | 251338 | 559.7 | 211202
601.5 | 211202 |  | 610.6 | 211202 | 616.2 | 252338 | 619.6 | 211202 | 621.8 | 249238 | 624.1 | 251338 | 601.5 | 211202
643.7 | 211202 |  | 652.6 | 211202 | 658.3 | 252338 | 661.6 | 211202 | 663.8 | 249238 | 666.2 | 251338 | 643.7 | 211202
685.7 | 211202 |  | 694.6 | 211202 | 700.3 | 252338 | 703.6 | 211202 | 705.7 | 249238 | 708.1 | 251338 | 685.7 | 211202
727.7 | 211202 |  | 736.6 | 211202 | 742.2 | 252338 | 745.5 | 211202 | 747.8 | 249238 | 750.2 | 251338 | 727.7 | 211202
769.6 | 211202 |  | 778.6 | 211202 | 784.2 | 252338 | 787.6 | 124819 | 789.8 | 249238 | 792.2 | 251338 | 769.6 | 124819
811.6 | 211202 |  | 820.5 | 211202 | 826.3 | 252338 | 829.5 | 211202 | 831.8 | 249238 | 834.1 | 251338 | 811.6 | 211202
853.7 | 211202 |  | 862.6 | 211202 | 868.1 | 252338 | 871.5 | 211202 | 873.7 | 249238 | 876 | 251338 | 853.7 | 211202
895.6 | 211202 |  | 904.5 | 211202 | 910.2 | 252338 | 913.5 | 211202 | 915.7 | 249238 | 917.9 | 251338 | 895.6 | 211202
937.5 | 211202 |  | 946.5 | 211202 | 952 | 252338 | 955.4 | 211202 | 957.7 | 249238 | 959.9 | 251338 | 937.5 | 211202
979.6 | 211202 |  | 988.6 | 211202 | 994.2 | 252338 | 997.6 | 211202 | 999.7 | 249238 | 1002.1 | 251338 | 979.6 | 211202
1021.5 | 211202 |  | 1030.5 | 211202 | 1036 | 252338 | 1039.4 | 211202 | 1041.8 | 249238 | 1044 | 251338 | 1021.5 | 211202
1063.7 | 211202 |  | 1072.6 | 211202 | 1078.1 | 252338 | 1081.5 | 211202 | 1083.7 | 249238 | 1086 | 251338 | 1063.7 | 211202
1105.5 | 211202 |  | 1114.5 | 211202 | 1120.1 | 252338 | 1123.5 | 211202 | 1125.7 | 249238 | 1127.9 | 251338 | 1105.5 | 211202
1147.5 | 211202 |  | 1156.4 | 211202 | 1162.1 | 252338 | 1165.4 | 211202 | 1167.7 | 249238 | 1169.9 | 251338 | 1147.5 | 211202
1189.5 | 211202 |  | 1198.5 | 211202 | 1204 | 252338 | 1207.4 | 211202 | 1209.8 | 249238 | 1212 | 251338 | 1189.5 | 211202
1231.5 | 211202 |  | 1240.5 | 211202 | 1246 | 252338 | 1249.4 | 211202 | 1251.7 | 249238 | 1253.9 | 251338 | 1231.5 | 211202
1273.6 | 211202 |  | 1282.5 | 211202 | 1288.1 | 252338 | 1291.4 | 211202 | 1293.7 | 249238 | 1296.1 | 251338 | 1273.6 | 211202
1315.5 | 211202 |  | 1324.5 | 211202 | 1330 | 252338 | 1333.4 | 211202 | 1335.7 | 249238 | 1337.9 | 251338 | 1315.5 | 211202
1357.5 | 211202 |  | 1366.5 | 211202 | 1372 | 252338 | 1375.4 | 211202 | 1377.7 | 50343.8561 | 1379.9 | 17898.1108 | 1357.5 | 17898.1108
1399.5 | 211202 |  | 1408.5 | 211202 | 1414 | 252338 | 1417.4 | 211202 | 1419.7 | 4026.9367 | 1421.9 | 4250.7533 | 1399.5 | 4026.9367
1441.5 | 211202 |  | 1450.5 | 211202 | 1456 | 252338 | 1459.4 | 211202 | 1461.7 | 1507.7985 | 1463.9 | 1473.5032 | 1441.5 | 1473.5032
1483.5 | 211202 |  | 1492.5 | 211202 | 1498 | 126619 | 1501.4 | 211202 | 1503.7 | 587.0983 | 1505.9 | 624.5345 | 1483.5 | 587.0983
1525.5 | 211202 |  | 1534.5 | 211202 | 1540 | 10908.4005 | 1543.4 | 28112.3487 | 1545.7 | 274.2021 | 1547.9 | 211.6663 | 1525.5 | 211.6663
1567.5 | 211202 |  | 1576.4 | 125919 | 1582 | 149.8402 | 1585.3 | 19.0723 | 1587.7 | 16.3224 | 1589.9 | 16.2348 | 1567.5 | 16.2348
1609.5 | 70334 |  | 1618.5 | 70334 | 1624 | 16.1305 | 1627.4 | 15.4691 | 1629.7 | 4.5234 | 1631.9 | 6.5867 | 1609.5 | 4.5234
1651.5 | 70334 |  | 1660.5 | 70334 | 1666 | 2.2349 | 1669.4 | 22.3497 | 1671.7 | 7.4841 | 1673.9 | 1.2607 | 1651.5 | 1.2607
1693.5 | 70867.6774 |  | 1702.5 | 52570.4915 | 1708 | 2.6907 | 1711.4 | 4.3937 | 1713.7 | 1.3057 | 1715.9 | 14.096 | 1693.5 | 1.3057
1735.5 | 110.4862 |  | 1744.5 | 95.2581 | 1750 | 1.8203 | 1753.4 | 14.6572 | 1755.7 | 0.65836 | 1757.9 | 6.9494 | 1735.5 | 0.65836
1777.5 | 766.0583 |  | 1786.5 | 1231.9377 | 1792 | 5.7727 | 1795.4 | 1.767 | 1797.7 | 1.433 | 1799.9 | 2.4961 | 1777.5 | 1.433
1819.5 | 221.8143 |  | 1828.5 | 215.5632 | 1834 | 1.454 | 1837.4 | 21.0456 | 1839.7 | 11.4063 | 1841.9 | 8.1244 | 1819.5 | 1.454
1861.5 | 919.951 |  | 1870.5 | 1463.3615 | 1876 | 12.6167 | 1879.4 | 1.6706 | 1881.7 | 3.1883 | 1883.9 | 0.65389 | 1861.5 | 0.65389
1903.5 | 1383.4288 |  | 1912.5 | 33910.3561 | 1918 | 0.81098 | 1921.4 | 10.1654 | 1923.7 | 6.4335 | 1925.9 | 11.6518 | 1903.5 | 0.81098
1945.5 | 8650.1431 |  | 1954.5 | 5904.3565 | 1960 | 12.8763 | 1963.4 | 0.65052 | 1965.7 | 0.77551 | 1967.9 | 6.1187 | 1945.5 | 0.65052
1987.5 | 38039.8611 |  | 1996.5 | 3782.3429 | 2001.9 | 1.7013 | 2005.3 | 2.833 | 2007.6 | 0.85883 | 2009.8 | 1.0603 | 1987.5 | 0.85883
2029.5 | 4471.1695 |  | 2038.5 | 12713.0524 | 2044 | 5.2068 | 2047.4 | 0.6905 | 2049.7 | 5.7146 | 2051.9 | 2.5859 | 2029.5 | 0.6905
2071.4 | 231.9525 |  | 2080.5 | 187.2927 | 2086 | 2.1927 | 2089.4 | 0.85078 | 2091.6 | 0.65468 | 2093.9 | 3.1239 | 2071.4 | 0.65468
2113.5 | 542.4237 |  | 2122.4 | 770.5996 | 2127.8 | 4.5968 | 2131.4 | 11.4993 | 2133.6 | 0.65415 | 2135.9 | 21.0985 | 2113.5 | 0.65415
2155.4 | 379.1207 |  | 2164.5 | 367.8805 | 2169.9 | 0.69905 | 2173.3 | 3.0434 | 2175.5 | 7.7546 | 2177.8 | 5.2351 | 2155.4 | 0.69905
2197.3 | 2598.1227 |  | 2206.4 | 20995.0063 | 2212 | 0.64948 | 2215.4 | 0.65995 | 2217.6 | 0.66128 | 2219.9 | 9.6294 | 2197.3 | 0.64948
2239.4 | 2256.0608 |  | 2248.4 | 11691.8303 | 2254 | 0.81098 | 2257.4 | 9.9037 | 2259.7 | 0.70194 | 2261.9 | 1.5463 | 2239.4 | 0.70194
2281.3 | 2257.7899 |  | 2290.2 | 6303.0909 | 2295.8 | 1.7902 | 2299.3 | 2.7313 | 2301.5 | 2.1638 | 2303.7 | 0.65572 | 2281.3 | 0.65572
2323.5 | 1859.8549 |  | 2332.3 | 3397.9298 | 2337.8 | 0.65077 | 2341.3 | 4.2526 | 2343.6 | 15.5157 | 2345.7 | 1.0573 | 2323.5 | 0.65077
2365.5 | 854.3502 |  | 2374.3 | 1127.8657 | 2379.8 | 2.7313 | 2383.3 | 3.9364 | 2385.6 | 1.5383 | 2387.7 | 0.65415 | 2365.5 | 0.65415
2407.3 | 1658.8474 |  | 2416.3 | 17964.9873 | 2422 | 0.66201 | 2425.3 | 2.6896 | 2427.6 | 1.3433 | 2429.7 | 2.8797 | 2407.3 | 0.66201
2449.5 | 6503.1875 |  | 2458.3 | 6503.1875 | 2463.8 | 7.7868 | 2467.5 | 0.93707 | 2469.6 | 9.4806 | 2471.9 | 4.5782 | 2449.5 | 0.93707
2491.3 | 16926.34 |  | 2500.3 | 3774.5787 | 2505.8 | 0.96977 | 2509.4 | 0.77058 | 2511.5 | 0.69883 | 2513.9 | 2.169 | 2491.3 | 0.69883

## C5-C6
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 153.8694 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38958.5725 | 1 | 0 | 38958.5725 | 1 | 0 |  | -78.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.573 | 1 | 0 | 38958.573 | 1 | 0 |  | -36.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5735 | 1 | 0 | 38958.5735 | 1 | 0 |  | 5.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.574 | 1 | 0 | 38958.574 | 1 | 0 |  | 47.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5745 | 1 | 0 | 38958.5745 | 1 | 0 |  | 89.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.575 | 1 | 0 | 38958.575 | 1 | 0 |  | 131.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5754 | 1 | 0 | 38958.5755 | 1 | 0 |  | 173.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5759 | 1 | 0 | 38958.5759 | 1 | 0 |  | 215.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5764 | 1 | 0 | 38958.5764 | 1 | 0 |  | 257.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5769 | 1 | 0 | 38958.5769 | 1 | 0 |  | 299.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5774 | 1 | 0 | 38958.5774 | 1 | 0 |  | 341.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5779 | 1 | 0 | 38958.5779 | 1 | 0 |  | 383.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5784 | 1 | 0 | 38958.5784 | 1 | 0 |  | 425.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5788 | 1 | 0 | 38958.5789 | 1 | 0 |  | 467.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5793 | 1 | 0 | 38958.5793 | 1 | 0 |  | 509.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5798 | 1 | 0 | 38958.5798 | 1 | 0 |  | 551.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5803 | 1 | 0 | 38958.5803 | 1 | 0 |  | 593.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5808 | 1 | 0 | 38958.5808 | 1 | 0 |  | 635.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5813 | 1 | 0 | 38958.5813 | 1 | 0 |  | 677.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5817 | 1 | 0 | 38958.5818 | 1 | 0 |  | 719 | 837 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5822 | 1 | 0 | 38958.5823 | 1 | 0 |  | 761.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5827 | 1 | 0 | 38958.5827 | 1 | 0 |  | 803.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5832 | 1 | 0 | 38958.5832 | 1 | 0 |  | 845.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5837 | 1 | 0 | 38958.5837 | 1 | 0 |  | 887 | 1005 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5842 | 1 | 0 | 38958.5842 | 1 | 0 |  | 929 | 1047 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5847 | 1 | 0 | 38958.5847 | 1 | 0 |  | 971 | 1089 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5852 | 1 | 0 | 38958.5852 | 1 | 0 |  | 1013 | 1131 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5856 | 1 | 0 | 38958.5857 | 1 | 0 |  | 1055.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5861 | 1 | 0 | 38958.5861 | 1 | 0 |  | 1097 | 1215 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5866 | 1 | 0 | 38958.5866 | 1 | 0 |  | 1139 | 1257 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5871 | 1 | 0 | 38958.5871 | 1 | 0 |  | 1181 | 1299 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5876 | 1 | 0 | 38958.5876 | 1 | 0 |  | 1223.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5881 | 1 | 0 | 38958.5881 | 1 | 0 |  | 1265 | 1383 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5886 | 1 | 0 | 38958.5886 | 1 | 0 |  | 1307 | 1425 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.589 | 1 | 0 | 38958.5891 | 1 | 0 |  | 1349 | 1467 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5895 | 6 | 1 | 38958.5895 | 15 | 1 |  | 1391 | 1509 | 0.3663 | 0.06105 | 0.91575 | 0.06105 | 0.003663 | 0.0006105 | 0.0091575 | 0.0006105 | 0.0030525 | 0.008547 | 50343.8561 | 17898.1108 | 249941.5312
38958.59 | 117 | 56 | 38958.59 | 113 | 55 |  | 1433 | 1551 | 7.1429 | 3.4188 | 6.8987 | 3.3578 | 0.071429 | 0.034188 | 0.068987 | 0.033578 | 0.037241 | 0.035409 | 4026.9367 | 4250.7533 | 4095.4046
38958.5905 | 323 | 166 | 38958.5905 | 282 | 122 |  | 1475 | 1593 | 19.7192 | 10.1343 | 17.2161 | 7.4481 | 0.19719 | 0.10134 | 0.17216 | 0.074481 | 0.095849 | 0.09768 | 1507.7985 | 1473.5032 | 1145.9523
38958.591 | 793 | 441 | 38958.591 | 978 | 663 |  | 1517 | 1635 | 48.4127 | 26.9231 | 59.707 | 40.4762 | 0.48413 | 0.26923 | 0.59707 | 0.40476 | 0.2149 | 0.19231 | 587.0983 | 763.2834 | 257.907
38958.5915 | 1347 | 881 | 38958.5915 | 1366 | 891 |  | 1559 | 1677 | 82.2344 | 53.7851 | 83.3944 | 54.3956 | 0.82234 | 0.53785 | 0.83394 | 0.54396 | 0.28449 | 0.28999 | 476.7507 | 400.6735 | 26.5588
38958.592 | 1978 | 17 | 38958.592 | 2177 | 14 |  | 1601 | 1719 | 120.757 | 1.0379 | 132.906 | 0.8547 | 1.2076 | 0.010379 | 1.3291 | 0.008547 | 1.1972 | 1.3205 | 29.2185 | 16.2348 | 431.6538
38958.5924 | 2378 | 2 | 38958.5925 | 2205 | 2 |  | 1643 | 1761 | 145.177 | 0.1221 | 134.6154 | 0.1221 | 1.4518 | 0.001221 | 1.3462 | 0.001221 | 1.4505 | 1.3449 | 6.0273 | 14.5349 | 890.7348
38958.5929 | 2036 | 0 | 38958.593 | 2490 | 1 |  | 1685 | 1803 | 124.2979 | 0 | 152.0147 | 0.06105 | 1.243 | 0 | 1.5201 | 0.0006105 | 1.243 | 1.5195 | 23.7908 | 1.2607 | 22.5478
38958.5934 | 2488 | 1 | 38958.5934 | 2209 | 0 |  | 1727 | 1845 | 151.8926 | 0.06105 | 134.8596 | 0 | 1.5189 | 0.0006105 | 1.3486 | 0 | 1.5183 | 1.3486 | 1.3057 | 14.096 | 387.6838
38958.5939 | 2023 | 0 | 38958.5939 | 2297 | 1 |  | 1769 | 1887 | 123.5043 | 0 | 140.232 | 0.06105 | 1.235 | 0 | 1.4023 | 0.0006105 | 1.235 | 1.4017 | 24.5863 | 9.7726 | 23.3512
38958.5944 | 2257 | 1 | 38958.5944 | 2459 | 0 |  | 1811 | 1929 | 137.79 | 0.06105 | 150.1221 | 0 | 1.3779 | 0.0006105 | 1.5012 | 0 | 1.3773 | 1.5012 | 11.8857 | 2.4961 | 638.9864
38958.5949 | 2117 | 0 | 38958.5949 | 2139 | 0 |  | 1853 | 1971 | 129.243 | 0 | 130.5861 | 0 | 1.2924 | 0 | 1.3059 | 0 | 1.2924 | 1.3059 | 19.0543 | 17.8298 | 17.7619
38958.5954 | 2041 | 0 | 38958.5954 | 2053 | 0 |  | 1895 | 2013 | 124.6032 | 0 | 125.3358 | 0 | 1.246 | 0 | 1.2534 | 0 | 1.246 | 1.2534 | 23.4875 | 22.7657 | 22.2415
38958.5958 | 2060 | 0 | 38958.5959 | 2172 | 0 |  | 1937 | 2055 | 125.7631 | 0 | 132.6007 | 0 | 1.2576 | 0 | 1.326 | 0 | 1.2576 | 1.326 | 22.3485 | 16.0396 | 21.0909
38958.5963 | 2303 | 0 | 38958.5964 | 2163 | 0 |  | 1979 | 2097 | 140.5983 | 0 | 132.0513 | 0 | 1.406 | 0 | 1.3205 | 0 | 1.406 | 1.3205 | 9.439 | 16.5224 | 8.033
38958.5968 | 2499 | 1 | 38958.5968 | 2269 | 1 |  | 2021 | 2139 | 152.5641 | 0.06105 | 138.5226 | 0.06105 | 1.5256 | 0.0006105 | 1.3852 | 0.0006105 | 1.525 | 1.3846 | 0.85883 | 11.6836 | 213.2022
38958.5973 | 2271 | 0 | 38958.5973 | 2312 | 0 |  | 2063 | 2181 | 138.6447 | 0 | 141.1477 | 0 | 1.3864 | 0 | 1.4115 | 0 | 1.3864 | 1.4115 | 10.9811 | 9.013 | 9.5946
38958.5978 | 2346 | 0 | 38958.5978 | 1981 | 0 |  | 2105 | 2223 | 143.2234 | 0 | 120.9402 | 0 | 1.4322 | 0 | 1.2094 | 0 | 1.4322 | 1.2094 | 7.4331 | 27.2277 | 6.0008
38958.5983 | 2504 | 0 | 38958.5983 | 1960 | 0 |  | 2147 | 2265 | 152.8694 | 0 | 119.6581 | 0 | 1.5287 | 0 | 1.1966 | 0 | 1.5287 | 1.1966 | 0.65415 | 28.5908 | 0.87454
38958.5988 | 2339 | 0 | 38958.5988 | 2077 | 0 |  | 2189 | 2307 | 142.7961 | 0 | 126.801 | 0 | 1.428 | 0 | 1.268 | 0 | 1.428 | 1.268 | 7.7546 | 21.3471 | 6.3266
38958.5992 | 2384 | 0 | 38958.5993 | 2139 | 0 |  | 2231 | 2349 | 145.5433 | 0 | 130.5861 | 0 | 1.4554 | 0 | 1.3059 | 0 | 1.4554 | 1.3059 | 5.7206 | 17.8298 | 4.2652
38958.5997 | 2398 | 1 | 38958.5998 | 2482 | 0 |  | 2273 | 2391 | 146.398 | 0.06105 | 151.5263 | 0 | 1.464 | 0.0006105 | 1.5153 | 0 | 1.4634 | 1.5153 | 5.2471 | 1.5463 | 184.8358
38958.6002 | 2467 | 0 | 38958.6002 | 2179 | 0 |  | 2315 | 2433 | 150.6105 | 0 | 133.0281 | 0 | 1.5061 | 0 | 1.3303 | 0 | 1.5061 | 1.3303 | 2.1638 | 15.6668 | 0.65766
38958.6007 | 2052 | 0 | 38958.6007 | 2354 | 0 |  | 2357 | 2475 | 125.2747 | 0 | 143.7118 | 0 | 1.2527 | 0 | 1.4371 | 0 | 1.2527 | 1.4371 | 22.8255 | 7.068 | 21.5728
38958.6012 | 1963 | 0 | 38958.6012 | 2432 | 0 |  | 2399 | 2517 | 119.8413 | 0 | 148.4737 | 0 | 1.1984 | 0 | 1.4847 | 0 | 1.1984 | 1.4847 | 28.3943 | 3.634 | 27.1959
38958.6017 | 1964 | 0 | 38958.6017 | 1971 | 1 |  | 2441 | 2559 | 119.9023 | 0 | 120.3297 | 0.06105 | 1.199 | 0 | 1.2033 | 0.0006105 | 1.199 | 1.2027 | 28.3289 | 27.9381 | 27.1299
38958.6022 | 2215 | 0 | 38958.6022 | 2268 | 1 |  | 2483 | 2601 | 135.2259 | 0 | 138.4615 | 0.06105 | 1.3523 | 0 | 1.3846 | 0.0006105 | 1.3523 | 1.384 | 13.7869 | 11.1769 | 12.4346
38958.6027 | 2429 | 1 | 38958.6027 | 2257 | 0 |  | 2525 | 2643 | 148.2906 | 0.06105 | 137.79 | 0 | 1.4829 | 0.0006105 | 1.3779 | 0 | 1.4823 | 1.3779 | 3.7769 | 11.6695 | 944.472

## B4-C6
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 153.9304 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38958.5725 | 1 | 0 | 38958.5725 | 1 | 0 |  | -81.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.573 | 1 | 0 | 38958.573 | 1 | 0 |  | -39.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5735 | 1 | 0 | 38958.5735 | 1 | 0 |  | 2.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5739 | 1 | 0 | 38958.574 | 1 | 0 |  | 44.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5744 | 1 | 0 | 38958.5744 | 1 | 0 |  | 86.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5749 | 1 | 0 | 38958.5749 | 1 | 0 |  | 128.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5754 | 1 | 0 | 38958.5754 | 1 | 0 |  | 170.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5759 | 1 | 0 | 38958.5759 | 1 | 0 |  | 212.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5764 | 1 | 0 | 38958.5764 | 1 | 0 |  | 254.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5769 | 1 | 0 | 38958.5769 | 1 | 0 |  | 296.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5773 | 1 | 0 | 38958.5774 | 1 | 0 |  | 338.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5778 | 1 | 0 | 38958.5778 | 1 | 0 |  | 380.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5783 | 1 | 0 | 38958.5783 | 1 | 0 |  | 422.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5788 | 1 | 0 | 38958.5788 | 1 | 0 |  | 464.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5793 | 1 | 0 | 38958.5793 | 1 | 0 |  | 506.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5798 | 1 | 0 | 38958.5798 | 1 | 0 |  | 548.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5803 | 1 | 0 | 38958.5803 | 1 | 0 |  | 590.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5808 | 1 | 0 | 38958.5808 | 1 | 0 |  | 632.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5812 | 1 | 0 | 38958.5813 | 1 | 0 |  | 674.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5817 | 1 | 0 | 38958.5817 | 1 | 0 |  | 716.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5822 | 1 | 0 | 38958.5822 | 1 | 0 |  | 758.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5827 | 1 | 0 | 38958.5827 | 1 | 0 |  | 800.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5832 | 1 | 0 | 38958.5832 | 1 | 0 |  | 842.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5837 | 1 | 0 | 38958.5837 | 1 | 0 |  | 884.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5842 | 1 | 0 | 38958.5842 | 1 | 0 |  | 926.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5846 | 1 | 0 | 38958.5847 | 1 | 0 |  | 968.5 | 1086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5851 | 1 | 0 | 38958.5851 | 1 | 0 |  | 1010.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5856 | 1 | 0 | 38958.5856 | 1 | 0 |  | 1052.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5861 | 1 | 0 | 38958.5861 | 1 | 0 |  | 1094.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5866 | 1 | 0 | 38958.5866 | 1 | 0 |  | 1136.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5871 | 1 | 0 | 38958.5871 | 1 | 0 |  | 1178.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5876 | 1 | 0 | 38958.5876 | 1 | 0 |  | 1220.5 | 1338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.588 | 1 | 0 | 38958.5881 | 1 | 0 |  | 1262.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5885 | 1 | 0 | 38958.5885 | 1 | 0 |  | 1304.5 | 1422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.589 | 1 | 0 | 38958.589 | 1 | 0 |  | 1346.5 | 1464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.5895 | 1 | 0 | 38958.5895 | 1 | 0 |  | 1388.5 | 1506.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38958.59 | 1 | 0 | 38958.59 | 9 | 0 |  | 1430.5 | 1548.5 | 0.06105 | 0 | 0.54945 | 0 | 0.0006105 | 0 | 0.0054945 | 0 | 0.0006105 | 0.0054945 | 252038 | 27915.3333 | 252037.9994
38958.5905 | 1 | 0 | 38958.5905 | 138 | 0 |  | 1472.5 | 1590.5 | 0.06105 | 0 | 8.4249 | 0 | 0.0006105 | 0 | 0.084249 | 0 | 0.0006105 | 0.084249 | 252038 | 1727.087 | 252037.9994
38958.591 | 1 | 0 | 38958.591 | 348 | 0 |  | 1514.5 | 1632.5 | 0.06105 | 0 | 21.2454 | 0 | 0.0006105 | 0 | 0.21245 | 0 | 0.0006105 | 0.21245 | 252038 | 624.5345 | 252037.9994
38958.5914 | 2 | 0 | 38958.5915 | 809 | 0 |  | 1556.5 | 1674.5 | 0.1221 | 0 | 49.3895 | 0 | 0.001221 | 0 | 0.49389 | 0 | 0.001221 | 0.49389 | 125969 | 211.6663 | 125968.9988
38958.5919 | 1895 | 0 | 38958.5919 | 2166 | 0 |  | 1598.5 | 1716.5 | 115.6899 | 0 | 132.2344 | 0 | 1.1569 | 0 | 1.3223 | 0 | 1.1569 | 1.3223 | 33.0544 | 16.4072 | 31.8975
38958.5924 | 2162 | 0 | 38958.5924 | 2178 | 0 |  | 1640.5 | 1758.5 | 131.9902 | 0 | 132.967 | 0 | 1.3199 | 0 | 1.3297 | 0 | 1.3199 | 1.3297 | 16.6226 | 15.7658 | 15.3027
38958.5929 | 1983 | 0 | 38958.5929 | 2379 | 0 |  | 1682.5 | 1800.5 | 121.0623 | 0 | 145.2381 | 0 | 1.2106 | 0 | 1.4524 | 0 | 1.2106 | 1.4524 | 27.1498 | 5.9849 | 25.9392
38958.5934 | 2169 | 0 | 38958.5934 | 2099 | 0 |  | 1724.5 | 1842.5 | 132.4176 | 0 | 128.1441 | 0 | 1.3242 | 0 | 1.2814 | 0 | 1.3242 | 1.2814 | 16.2462 | 20.1229 | 14.922
38958.5939 | 2021 | 0 | 38958.5939 | 2282 | 0 |  | 1766.5 | 1884.5 | 123.3822 | 0 | 139.3162 | 0 | 1.2338 | 0 | 1.3932 | 0 | 1.2338 | 1.3932 | 24.759 | 10.4899 | 23.5252
38958.5944 | 1941 | 0 | 38958.5944 | 1955 | 0 |  | 1808.5 | 1926.5 | 118.4982 | 0 | 119.3529 | 0 | 1.185 | 0 | 1.1935 | 0 | 1.185 | 1.1935 | 29.9011 | 28.9708 | 28.7161
38958.5948 | 2083 | 0 | 38958.5949 | 1999 | 0 |  | 1850.5 | 1968.5 | 127.1673 | 0 | 122.0391 | 0 | 1.2717 | 0 | 1.2204 | 0 | 1.2717 | 1.2204 | 21.0456 | 26.1321 | 19.7739
38958.5953 | 2347 | 0 | 38958.5953 | 2505 | 0 |  | 1892.5 | 2010.5 | 143.2845 | 0 | 152.9304 | 0 | 1.4328 | 0 | 1.5293 | 0 | 1.4328 | 1.5293 | 7.4299 | 0.65389 | 5.9971
38958.5958 | 1975 | 0 | 38958.5958 | 2225 | 0 |  | 1934.5 | 2052.5 | 120.5739 | 0 | 135.8364 | 0 | 1.2057 | 0 | 1.3584 | 0 | 1.2057 | 1.3584 | 27.6648 | 13.3204 | 26.4591
38958.5963 | 2375 | 0 | 38958.5963 | 2376 | 0 |  | 1976.5 | 2094.5 | 144.9939 | 0 | 145.0549 | 0 | 1.4499 | 0 | 1.4505 | 0 | 1.4499 | 1.4505 | 6.1634 | 6.1187 | 4.7134
38958.5968 | 2377 | 0 | 38958.5968 | 1970 | 0 |  | 2018 | 2136 | 145.116 | 0 | 120.2686 | 0 | 1.4512 | 0 | 1.2027 | 0 | 1.4512 | 1.2027 | 6.074 | 27.9888 | 4.6229
38958.5973 | 2267 | 0 | 38958.5973 | 2427 | 0 |  | 2060.5 | 2178.5 | 138.4005 | 0 | 148.1685 | 0 | 1.384 | 0 | 1.4817 | 0 | 1.384 | 1.4817 | 11.221 | 3.8888 | 9.837
38958.5978 | 2431 | 0 | 38958.5978 | 2446 | 1 |  | 2102.5 | 2220.5 | 148.4127 | 0 | 149.3284 | 0.06105 | 1.4841 | 0 | 1.4933 | 0.0006105 | 1.4841 | 1.4927 | 3.7178 | 3.1239 | 2.2337
38958.5983 | 2201 | 0 | 38958.5983 | 2016 | 0 |  | 2144.5 | 2262.5 | 134.3712 | 0 | 123.0769 | 0 | 1.3437 | 0 | 1.2308 | 0 | 1.3437 | 1.2308 | 14.5561 | 25.0685 | 13.2124
38958.5987 | 2421 | 0 | 38958.5987 | 2249 | 0 |  | 2186 | 2304 | 147.8022 | 0 | 137.3016 | 0 | 1.478 | 0 | 1.373 | 0 | 1.478 | 1.373 | 4.1462 | 12.1112 | 2.6682
38958.5992 | 2315 | 0 | 38958.5992 | 2034 | 0 |  | 2228.5 | 2346.5 | 141.3309 | 0 | 124.1758 | 0 | 1.4133 | 0 | 1.2418 | 0 | 1.4133 | 1.2418 | 8.9149 | 23.9617 | 7.5016
38958.5997 | 1971 | 0 | 38958.5997 | 2192 | 0 |  | 2270.5 | 2388.5 | 120.3297 | 0 | 133.8217 | 0 | 1.2033 | 0 | 1.3382 | 0 | 1.2033 | 1.3382 | 27.9239 | 15.0265 | 26.7206
38958.6002 | 2095 | 0 | 38958.6002 | 2197 | 0 |  | 2312 | 2430 | 127.8999 | 0 | 134.127 | 0 | 1.279 | 0 | 1.3413 | 0 | 1.279 | 1.3413 | 20.3523 | 14.7647 | 19.0733
38958.6007 | 2228 | 0 | 38958.6007 | 2495 | 0 |  | 2354 | 2472 | 136.0195 | 0 | 152.3199 | 0 | 1.3602 | 0 | 1.5232 | 0 | 1.3602 | 1.5232 | 13.1679 | 1.0573 | 11.8077
38958.6012 | 1948 | 0 | 38958.6012 | 2288 | 0 |  | 2396 | 2514 | 118.9255 | 0 | 139.6825 | 0 | 1.1893 | 0 | 1.3968 | 0 | 1.1893 | 1.3968 | 29.4343 | 10.2002 | 28.245
38958.6016 | 2303 | 0 | 38958.6017 | 2165 | 0 |  | 2438 | 2556 | 140.5983 | 0 | 132.1734 | 0 | 1.406 | 0 | 1.3217 | 0 | 1.406 | 1.3217 | 9.4824 | 16.461 | 8.0764
| 2367 | 0 | 38958.6022 | 2411 | 0 |  | 2481 | 2599 | 144.5055 | 0 | 147.1917 | 0 | 1.4451 | 0 | 1.4719 | 0 | 1.4451 | 1.4719 | 6.5222 | 4.5782 | 5.0771
38958.6026 | 2430 | 0 | 38958.6026 | 2214 | 0 |  | 2522.5 | 2640.5 | 148.3516 | 0 | 135.1648 | 0 | 1.4835 | 0 | 1.3516 | 0 | 1.4835 | 1.3516 | 3.7605 | 13.8835 | 2.277

## B4-C5
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 153.7473 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38958.5725 | 1 | 0 | 38958.5725 | 1 | 0 |  | -84.5 | 33.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5729 | 1 | 0 | 38958.573 | 1 | 0 |  | -42.5 | 75.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5734 | 1 | 0 | 38958.5734 | 1 | 0 |  | -0.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5739 | 1 | 0 | 38958.5739 | 1 | 0 |  | 41.5 | 159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5744 | 1 | 0 | 38958.5744 | 1 | 0 |  | 83.5 | 201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5749 | 1 | 0 | 38958.5749 | 1 | 0 |  | 125.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5754 | 1 | 0 | 38958.5754 | 1 | 0 |  | 167.5 | 285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5759 | 1 | 0 | 38958.5759 | 1 | 0 |  | 209.5 | 327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5763 | 1 | 0 | 38958.5764 | 1 | 0 |  | 251.5 | 369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5768 | 1 | 0 | 38958.5768 | 1 | 0 |  | 293.5 | 411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5773 | 1 | 0 | 38958.5773 | 1 | 0 |  | 335.5 | 453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5778 | 1 | 0 | 38958.5778 | 1 | 0 |  | 377.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5783 | 1 | 0 | 38958.5783 | 1 | 0 |  | 419.5 | 537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5788 | 1 | 0 | 38958.5788 | 1 | 0 |  | 461.5 | 579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5793 | 1 | 0 | 38958.5793 | 1 | 0 |  | 503.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5797 | 1 | 0 | 38958.5798 | 1 | 0 |  | 545.5 | 663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5802 | 1 | 0 | 38958.5802 | 1 | 0 |  | 587.5 | 705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5807 | 1 | 0 | 38958.5807 | 1 | 0 |  | 629.5 | 747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5812 | 1 | 0 | 38958.5812 | 1 | 0 |  | 671.5 | 789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5817 | 1 | 0 | 38958.5817 | 1 | 0 |  | 713.5 | 831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5822 | 1 | 0 | 38958.5822 | 1 | 0 |  | 755.5 | 873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5827 | 1 | 0 | 38958.5827 | 1 | 0 |  | 797.5 | 915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5831 | 1 | 0 | 38958.5832 | 1 | 0 |  | 839.5 | 957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5836 | 1 | 0 | 38958.5836 | 1 | 0 |  | 881.5 | 999.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5841 | 1 | 0 | 38958.5841 | 1 | 0 |  | 923.5 | 1041.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5846 | 1 | 0 | 38958.5846 | 1 | 0 |  | 965.5 | 1083.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5851 | 1 | 0 | 38958.5851 | 1 | 0 |  | 1007.5 | 1125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5856 | 1 | 0 | 38958.5856 | 1 | 0 |  | 1049.5 | 1167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5861 | 1 | 0 | 38958.5861 | 1 | 0 |  | 1091.5 | 1209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5866 | 1 | 0 | 38958.5866 | 1 | 0 |  | 1133.5 | 1251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.587 | 1 | 0 | 38958.587 | 1 | 0 |  | 1175.5 | 1293.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5875 | 1 | 0 | 38958.5875 | 1 | 0 |  | 1217.5 | 1335.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.588 | 1 | 0 | 38958.588 | 1 | 0 |  | 1259.5 | 1377.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5885 | 1 | 0 | 38958.5885 | 1 | 0 |  | 1301.5 | 1419.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.589 | 1 | 0 | 38958.589 | 1 | 0 |  | 1343.5 | 1461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251738 | 251738 | 251737.9994
38958.5895 | 1 | 1 | 38958.5895 | 1 | 0 |  | 1385.5 | 1503.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 633720206.44 | 251738 | 251538.0794
38958.59 | 1 | 0 | 38958.59 | 4 | 0 |  | 1427.5 | 1545.5 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 251738 | 62859.5 | 251737.9994
38958.5904 | 1 | 0 | 38958.5905 | 102 | 0 |  | 1469.5 | 1587.5 | 0.06105 | 0 | 6.2271 | 0 | 0.0006105 | 0 | 0.062271 | 0 | 0.0006105 | 0.062271 | 251738 | 2369 | 251737.9994
38958.5909 | 1 | 0 | 38958.5909 | 293 | 0 |  | 1511.5 | 1629.5 | 0.06105 | 0 | 17.8877 | 0 | 0.0006105 | 0 | 0.17888 | 0 | 0.0006105 | 0.17888 | 251738 | 759.5154 | 251737.9994
38958.5914 | 1 | 0 | 38958.5914 | 673 | 0 |  | 1553.5 | 1671.5 | 0.06105 | 0 | 41.0867 | 0 | 0.0006105 | 0 | 0.41087 | 0 | 0.0006105 | 0.41087 | 251738 | 274.2021 | 251737.9994
38958.5919 | 2115 | 0 | 38958.5919 | 2165 | 0 |  | 1595.5 | 1713.5 | 129.1209 | 0 | 132.1734 | 0 | 1.2912 | 0 | 1.3217 | 0 | 1.2912 | 1.3217 | 19.0723 | 16.3224 | 17.7811
38958.5924 | 2181 | 0 | 38958.5924 | 1926 | 0 |  | 1637.5 | 1755.5 | 133.1502 | 0 | 117.5824 | 0 | 1.3315 | 0 | 1.1758 | 0 | 1.3315 | 1.1758 | 15.4691 | 30.757 | 14.1375
38958.5929 | 2007 | 0 | 38958.5929 | 2264 | 0 |  | 1679.5 | 1797.5 | 122.5275 | 0 | 138.2173 | 0 | 1.2253 | 0 | 1.3822 | 0 | 1.2253 | 1.3822 | 25.4798 | 11.2359 | 24.2545
38958.5934 | 2143 | 0 | 38958.5934 | 1448 | 0 |  | 1721.5 | 1839.5 | 130.8303 | 0 | 88.4005 | 0 | 1.3083 | 0 | 0.884 | 0 | 1.3083 | 0.884 | 17.5166 | 73.9213 | 16.2083
38958.5938 | 2104 | 0 | 38958.5939 | 2420 | 0 |  | 1763.5 | 1881.5 | 128.4493 | 0 | 147.7411 | 0 | 1.2845 | 0 | 1.4774 | 0 | 1.2845 | 1.4774 | 19.6949 | 4.0653 | 18.4104
38958.5943 | 2296 | 0 | 38958.5943 | 2165 | 0 |  | 1805.5 | 1923.5 | 140.1709 | 0 | 132.1734 | 0 | 1.4017 | 0 | 1.3217 | 0 | 1.4017 | 1.3217 | 9.6855 | 16.3224 | 8.2838
38958.5948 | 1984 | 0 | 38958.5948 | 2118 | 1 |  | 1847.5 | 1965.5 | 121.1233 | 0 | 129.304 | 0.06105 | 1.2112 | 0 | 1.293 | 0.0006105 | 1.2112 | 1.2924 | 26.9345 | 18.9598 | 25.7232
38958.5953 | 2477 | 0 | 38958.5953 | 1956 | 0 |  | 1889.5 | 2007.5 | 151.221 | 0 | 119.4139 | 0 | 1.5122 | 0 | 1.1941 | 0 | 1.5122 | 1.1941 | 1.6706 | 28.7515 | 0.15836
38958.5958 | 2286 | 0 | 38958.5958 | 2323 | 0 |  | 1931.5 | 2049.5 | 139.5604 | 0 | 141.8193 | 0 | 1.3956 | 0 | 1.4182 | 0 | 1.3956 | 1.4182 | 10.1654 | 8.4107 | 8.7697
38958.5963 | 1968 | 0 | 38958.5963 | 2499 | 0 |  | 1973.5 | 2091.5 | 120.1465 | 0 | 152.5641 | 0 | 1.2015 | 0 | 1.5256 | 0 | 1.2015 | 1.5256 | 27.9665 | 0.77551 | 26.765
38958.5968 | 2449 | 0 | 38958.5968 | 2075 | 0 |  | 2015.5 | 2133.5 | 149.5116 | 0 | 126.6789 | 0 | 1.4951 | 0 | 1.2668 | 0 | 1.4951 | 1.2668 | 2.833 | 21.3677 | 1.3379
38958.5972 | 2242 | 0 | 38958.5973 | 2044 | 0 |  | 2057.5 | 2175.5 | 136.8742 | 0 | 124.7863 | 0 | 1.3687 | 0 | 1.2479 | 0 | 1.3687 | 1.2479 | 12.3274 | 23.2084 | 10.9586
38958.5977 | 2319 | 0 | 38958.5977 | 2502 | 0 |  | 2099.5 | 2217.5 | 141.5751 | 0 | 152.7473 | 0 | 1.4158 | 0 | 1.5275 | 0 | 1.4158 | 1.5275 | 8.5977 | 0.65468 | 7.1819
38958.5982 | 1944 | 0 | 38958.5982 | 2124 | 0 |  | 2141.5 | 2259.5 | 118.6813 | 0 | 129.6703 | 0 | 1.1868 | 0 | 1.2967 | 0 | 1.1868 | 1.2967 | 29.5463 | 18.5678 | 28.3595
38958.5987 | 2444 | 0 | 38958.5987 | 1979 | 0 |  | 2183.5 | 2301.5 | 149.2063 | 0 | 120.8181 | 0 | 1.4921 | 0 | 1.2082 | 0 | 1.4921 | 1.2082 | 3.0434 | 27.2552 | 1.5513
38958.5992 | 1990 | 0 | 38958.5992 | 2067 | 0 |  | 2225.5 | 2343.5 | 121.4896 | 0 | 126.1905 | 0 | 1.2149 | 0 | 1.2619 | 0 | 1.2149 | 1.2619 | 26.5518 | 21.8374 | 25.3369
38958.5997 | 2057 | 0 | 38958.5997 | 2057 | 0 |  | 2267.5 | 2385.5 | 125.58 | 0 | 125.58 | 0 | 1.2558 | 0 | 1.2558 | 0 | 1.2558 | 1.2558 | 22.4298 | 22.4298 | 21.174
38958.6002 | 2186 | 0 | 38958.6002 | 2376 | 0 |  | 2309.5 | 2427.5 | 133.4554 | 0 | 145.0549 | 0 | 1.3346 | 0 | 1.4505 | 0 | 1.3346 | 1.4505 | 15.2049 | 5.9924 | 13.8704
38958.6006 | 1966 | 0 | 38958.6007 | 1956 | 0 |  | 2351.5 | 2469.5 | 120.0244 | 0 | 119.4139 | 0 | 1.2002 | 0 | 1.1941 | 0 | 1.2002 | 1.1941 | 28.0966 | 28.7515 | 26.8964
38958.6011 | 2423 | 0 | 38958.6011 | 1951 | 0 |  | 2393.5 | 2511.5 | 147.9243 | 0 | 119.1087 | 0 | 1.4792 | 0 | 1.1911 | 0 | 1.4792 | 1.1911 | 3.9364 | 29.0815 | 2.4572
38958.6016 | 1960 | 0 | 38958.6016 | 2485 | 0 |  | 2435.5 | 2553.5 | 119.6581 | 0 | 151.7094 | 0 | 1.1966 | 0 | 1.5171 | 0 | 1.1966 | 1.5171 | 28.4888 | 1.3433 | 27.2922
38958.6021 | 2495 | 0 | 38958.6021 | 2249 | 0 |  | 2477.5 | 2595.5 | 152.3199 | 0 | 137.3016 | 0 | 1.5232 | 0 | 1.373 | 0 | 1.5232 | 1.373 | 0.93707 | 11.9778 | 0.58612
38958.6026 | 2294 | 0 | 38958.6026 | 2232 | 0 |  | 2519.5 | 2637.5 | 140.0488 | 0 | 136.2637 | 0 | 1.4005 | 0 | 1.3626 | 0 | 1.4005 | 1.3626 | 9.7812 | 12.8306 | 8.3807

## B3-C6
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 154.663 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38958.5724 | 1 | 0 | 38958.5724 | 1 | 0 |  | -87 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5729 | 1 | 0 | 38958.5729 | 1 | 0 |  | -45 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5734 | 1 | 0 | 38958.5734 | 1 | 0 |  | -3 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5739 | 1 | 0 | 38958.5739 | 1 | 0 |  | 39 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5744 | 1 | 0 | 38958.5744 | 1 | 0 |  | 81 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5748 | 1 | 0 | 38958.5749 | 1 | 0 |  | 123 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5753 | 1 | 0 | 38958.5754 | 1 | 0 |  | 165 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5758 | 1 | 0 | 38958.5758 | 1 | 0 |  | 207 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5763 | 1 | 0 | 38958.5763 | 1 | 0 |  | 249 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5768 | 1 | 0 | 38958.5768 | 1 | 0 |  | 291 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5773 | 1 | 0 | 38958.5773 | 1 | 0 |  | 333 | 451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5778 | 1 | 0 | 38958.5778 | 1 | 0 |  | 375 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5783 | 1 | 0 | 38958.5783 | 1 | 0 |  | 417 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5787 | 1 | 0 | 38958.5788 | 1 | 0 |  | 459 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5792 | 1 | 0 | 38958.5792 | 1 | 0 |  | 501 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5797 | 1 | 0 | 38958.5797 | 1 | 0 |  | 543 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5802 | 1 | 0 | 38958.5802 | 1 | 0 |  | 585 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5807 | 1 | 0 | 38958.5807 | 1 | 0 |  | 627 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5812 | 1 | 0 | 38958.5812 | 1 | 0 |  | 669 | 787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5817 | 1 | 0 | 38958.5817 | 1 | 0 |  | 711 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5821 | 1 | 0 | 38958.5822 | 1 | 0 |  | 753 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5826 | 1 | 0 | 38958.5827 | 1 | 0 |  | 795 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5831 | 1 | 0 | 38958.5831 | 1 | 0 |  | 837 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5836 | 1 | 0 | 38958.5836 | 1 | 0 |  | 878.5 | 996.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5841 | 1 | 0 | 38958.5841 | 1 | 0 |  | 920.5 | 1038.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5846 | 1 | 0 | 38958.5846 | 1 | 0 |  | 962.5 | 1080.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5851 | 1 | 0 | 38958.5851 | 1 | 0 |  | 1005 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5855 | 1 | 0 | 38958.5856 | 1 | 0 |  | 1046.5 | 1164.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.586 | 1 | 0 | 38958.586 | 1 | 0 |  | 1088.5 | 1206.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5865 | 1 | 0 | 38958.5865 | 1 | 0 |  | 1130.5 | 1248.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.587 | 1 | 0 | 38958.587 | 1 | 0 |  | 1172.5 | 1290.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5875 | 1 | 0 | 38958.5875 | 1 | 0 |  | 1214.5 | 1332.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.588 | 1 | 0 | 38958.588 | 1 | 0 |  | 1256.5 | 1374.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5885 | 1 | 0 | 38958.5885 | 1 | 0 |  | 1299 | 1417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5889 | 1 | 0 | 38958.589 | 1 | 0 |  | 1340.5 | 1458.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5894 | 1 | 0 | 38958.5894 | 1 | 0 |  | 1382.5 | 1500.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5899 | 1 | 0 | 38958.5899 | 6 | 0 |  | 1424.5 | 1542.5 | 0.06105 | 0 | 0.3663 | 0 | 0.0006105 | 0 | 0.003663 | 0 | 0.0006105 | 0.003663 | 253238 | 42123 | 253237.9994
38958.5904 | 1 | 0 | 38958.5904 | 112 | 0 |  | 1466.5 | 1584.5 | 0.06105 | 0 | 6.8376 | 0 | 0.0006105 | 0 | 0.068376 | 0 | 0.0006105 | 0.068376 | 253238 | 2161.9464 | 253237.9994
38958.5909 | 1 | 0 | 38958.5909 | 268 | 0 |  | 1508.5 | 1626.5 | 0.06105 | 0 | 16.3614 | 0 | 0.0006105 | 0 | 0.16361 | 0 | 0.0006105 | 0.16361 | 253238 | 845.291 | 253237.9994
38958.5914 | 2 | 0 | 38958.5914 | 765 | 0 |  | 1550.5 | 1668.5 | 0.1221 | 0 | 46.7033 | 0 | 0.001221 | 0 | 0.46703 | 0 | 0.001221 | 0.46703 | 126569 | 231.1608 | 126568.9988
38958.5919 | 1014 | 0 | 38958.5919 | 852 | 0 |  | 1592.5 | 1710.5 | 61.9048 | 0 | 52.0147 | 0 | 0.61905 | 0 | 0.52015 | 0 | 0.61905 | 0.52015 | 149.8402 | 197.3451 | 149.2212
38958.5923 | 1998 | 0 | 38958.5924 | 2327 | 0 |  | 1634.5 | 1752.5 | 121.978 | 0 | 142.0635 | 0 | 1.2198 | 0 | 1.4206 | 0 | 1.2198 | 1.4206 | 26.7958 | 8.8689 | 25.576
38958.5928 | 2478 | 0 | 38958.5928 | 2243 | 0 |  | 1676.5 | 1794.5 | 151.2821 | 0 | 136.9353 | 0 | 1.5128 | 0 | 1.3694 | 0 | 1.5128 | 1.3694 | 2.2349 | 12.9461 | 0.72205
38958.5933 | 2116 | 0 | 38958.5933 | 1762 | 0 |  | 1718.5 | 1836.5 | 129.1819 | 0 | 107.5702 | 0 | 1.2918 | 0 | 1.0757 | 0 | 1.2918 | 1.0757 | 19.725 | 43.7787 | 18.4331
38958.5938 | 2287 | 0 | 38958.5938 | 2347 | 0 |  | 1760.5 | 1878.5 | 139.6215 | 0 | 143.2845 | 0 | 1.3962 | 0 | 1.4328 | 0 | 1.3962 | 1.4328 | 10.7731 | 7.9412 | 9.3769
38958.5943 | 2277 | 0 | 38958.5943 | 2201 | 0 |  | 1802.5 | 1920.5 | 139.011 | 0 | 134.3712 | 0 | 1.3901 | 0 | 1.3437 | 0 | 1.3901 | 1.3437 | 11.2596 | 15.1013 | 9.8694
38958.5948 | 2056 | 1 | 38958.5948 | 2169 | 0 |  | 1844.5 | 1962.5 | 125.5189 | 0.06105 | 132.4176 | 0 | 1.2552 | 0.0006105 | 1.3242 | 0 | 1.2546 | 1.3242 | 23.2977 | 16.7994 | 6851.8479
38958.5953 | 2120 | 0 | 38958.5953 | 2212 | 0 |  | 1886.5 | 2004.5 | 129.4261 | 0 | 135.0427 | 0 | 1.2943 | 0 | 1.3504 | 0 | 1.2943 | 1.3504 | 19.4991 | 14.5289 | 18.2048
38958.5958 | 2513 | 0 | 38958.5958 | 2269 | 0 |  | 1928.5 | 2046.5 | 153.4188 | 0 | 138.5226 | 0 | 1.5342 | 0 | 1.3852 | 0 | 1.5342 | 1.3852 | 0.81098 | 11.6518 | 0.72321
38958.5962 | 2241 | 0 | 38958.5963 | 2079 | 0 |  | 1970.5 | 2088.5 | 136.8132 | 0 | 126.9231 | 0 | 1.3681 | 0 | 1.2692 | 0 | 1.3681 | 1.2692 | 13.0469 | 21.8557 | 11.6787
38958.5967 | 2491 | 0 | 38958.5967 | 1980 | 0 |  | 2012.5 | 2130.5 | 152.0757 | 0 | 120.8791 | 0 | 1.5208 | 0 | 1.2088 | 0 | 1.5208 | 1.2088 | 1.7013 | 27.9485 | 0.18057
38958.5972 | 2408 | 0 | 38958.5972 | 2149 | 0 |  | 2054.5 | 2172.5 | 147.0085 | 0 | 131.1966 | 0 | 1.4701 | 0 | 1.312 | 0 | 1.4701 | 1.312 | 5.2068 | 17.8865 | 3.7367
38958.5977 | 2278 | 0 | 38958.5977 | 2150 | 0 |  | 2096.5 | 2214.5 | 139.072 | 0 | 131.2576 | 0 | 1.3907 | 0 | 1.3126 | 0 | 1.3907 | 1.3126 | 11.2107 | 17.8316 | 9.82
38958.5982 | 2107 | 0 | 38958.5982 | 2092 | 0 |  | 2138.5 | 2256.5 | 128.6325 | 0 | 127.7167 | 0 | 1.2863 | 0 | 1.2772 | 0 | 1.2863 | 1.2772 | 20.2364 | 21.0985 | 18.95
38958.5987 | 2154 | 0 | 38958.5987 | 2184 | 0 |  | 2180.5 | 2298.5 | 131.5018 | 0 | 133.3333 | 0 | 1.315 | 0 | 1.3333 | 0 | 1.315 | 1.3333 | 17.6128 | 15.9973 | 16.2978
38958.5992 | 2129 | 0 | 38958.5992 | 2130 | 0 |  | 2222.5 | 2340.5 | 129.9756 | 0 | 130.0366 | 0 | 1.2998 | 0 | 1.3004 | 0 | 1.2998 | 1.3004 | 18.9939 | 18.938 | 17.6941
38958.5996 | 2085 | 0 | 38958.5997 | 2006 | 0 |  | 2264.5 | 2382.5 | 127.2894 | 0 | 122.4664 | 0 | 1.2729 | 0 | 1.2247 | 0 | 1.2729 | 1.2247 | 21.505 | 26.2901 | 20.2321
38958.6001 | 2326 | 0 | 38958.6001 | 2068 | 0 |  | 2306.5 | 2424.5 | 142.0024 | 0 | 126.2515 | 0 | 1.42 | 0 | 1.2625 | 0 | 1.42 | 1.2625 | 8.9157 | 22.5039 | 7.4957
38958.6006 | 2517 | 0 | 38958.6006 | 2122 | 0 |  | 2348.5 | 2466.5 | 153.663 | 0 | 129.5482 | 0 | 1.5366 | 0 | 1.2955 | 0 | 1.5366 | 1.2955 | 0.65077 | 19.3864 | 0.88586
38958.6011 | 2111 | 0 | 38958.6011 | 2447 | 0 |  | 2390.5 | 2508.5 | 128.8767 | 0 | 149.3895 | 0 | 1.2888 | 0 | 1.4939 | 0 | 1.2888 | 1.4939 | 20.0085 | 3.53 | 18.7198
38958.6016 | 2316 | 0 | 38958.6016 | 2185 | 0 |  | 2432.5 | 2550.5 | 141.3919 | 0 | 133.3944 | 0 | 1.4139 | 0 | 1.3339 | 0 | 1.4139 | 1.3339 | 9.386 | 15.9442 | 7.9721
38958.6021 | 2152 | 0 | 38958.6021 | 2094 | 0 |  | 2474.5 | 2592.5 | 131.3797 | 0 | 127.8388 | 0 | 1.3138 | 0 | 1.2784 | 0 | 1.3138 | 1.2784 | 17.7221 | 20.9828 | 16.4083
38958.6026 | 2171 | 0 | 38958.6026 | 2398 | 0 |  | 2516.5 | 2634.5 | 132.5397 | 0 | 146.398 | 0 | 1.3254 | 0 | 1.464 | 0 | 1.3254 | 1.464 | 16.6918 | 5.6455 | 15.3665

## B3-C5
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 154.663 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38958.5724 | 1 | 0 | 38958.5724 | 1 | 0 |  | -90 | 28 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5729 | 1 | 0 | 38958.5729 | 1 | 0 |  | -47.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5734 | 1 | 0 | 38958.5734 | 1 | 0 |  | -6 | 112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5738 | 1 | 0 | 38958.5739 | 1 | 0 |  | 36 | 154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5743 | 1 | 0 | 38958.5744 | 1 | 0 |  | 78 | 196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5748 | 1 | 0 | 38958.5748 | 1 | 0 |  | 120 | 238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5753 | 1 | 0 | 38958.5753 | 1 | 0 |  | 162 | 280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5758 | 1 | 0 | 38958.5758 | 1 | 0 |  | 204 | 322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5763 | 1 | 0 | 38958.5763 | 1 | 0 |  | 246 | 364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5768 | 1 | 0 | 38958.5768 | 1 | 0 |  | 288 | 406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5772 | 1 | 0 | 38958.5773 | 1 | 0 |  | 330 | 448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5777 | 1 | 0 | 38958.5778 | 1 | 0 |  | 372 | 490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5782 | 1 | 0 | 38958.5782 | 1 | 0 |  | 414 | 532 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5787 | 1 | 0 | 38958.5787 | 1 | 0 |  | 456 | 574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5792 | 1 | 0 | 38958.5792 | 1 | 0 |  | 498 | 616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5797 | 1 | 0 | 38958.5797 | 1 | 0 |  | 540 | 658 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5802 | 1 | 0 | 38958.5802 | 1 | 0 |  | 582 | 700 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5806 | 1 | 0 | 38958.5807 | 1 | 0 |  | 624 | 742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5811 | 1 | 0 | 38958.5812 | 1 | 0 |  | 666 | 784 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5816 | 1 | 0 | 38958.5816 | 1 | 0 |  | 708 | 826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5821 | 1 | 0 | 38958.5821 | 1 | 0 |  | 750 | 868 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5826 | 1 | 0 | 38958.5826 | 1 | 0 |  | 792 | 910 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5831 | 1 | 0 | 38958.5831 | 1 | 0 |  | 834 | 952 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5836 | 1 | 0 | 38958.5836 | 1 | 0 |  | 876 | 994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5841 | 1 | 0 | 38958.5841 | 1 | 0 |  | 918 | 1036 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5845 | 1 | 0 | 38958.5846 | 1 | 0 |  | 960 | 1078 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.585 | 1 | 0 | 38958.585 | 1 | 0 |  | 1002 | 1120 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5855 | 1 | 0 | 38958.5855 | 1 | 0 |  | 1044 | 1162 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.586 | 1 | 0 | 38958.586 | 1 | 0 |  | 1086 | 1204 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5865 | 1 | 0 | 38958.5865 | 1 | 0 |  | 1128 | 1246 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.587 | 1 | 0 | 38958.587 | 1 | 0 |  | 1170 | 1288 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5875 | 1 | 0 | 38958.5875 | 1 | 0 |  | 1212 | 1330 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5879 | 1 | 0 | 38958.588 | 1 | 0 |  | 1254 | 1372 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5884 | 1 | 0 | 38958.5884 | 1 | 0 |  | 1296 | 1414 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5889 | 1 | 0 | 38958.5889 | 1 | 0 |  | 1338 | 1456 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5894 | 1 | 0 | 38958.5894 | 1 | 0 |  | 1380 | 1498 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38958.5899 | 1 | 0 | 38958.5899 | 2 | 0 |  | 1422 | 1540 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253238 | 126569 | 253237.9994
38958.5904 | 1 | 0 | 38958.5904 | 89 | 0 |  | 1464 | 1582 | 0.06105 | 0 | 5.4335 | 0 | 0.0006105 | 0 | 0.054335 | 0 | 0.0006105 | 0.054335 | 253238 | 2746.4944 | 253237.9994
38958.5909 | 1 | 0 | 38958.5909 | 307 | 0 |  | 1506 | 1624 | 0.06105 | 0 | 18.7424 | 0 | 0.0006105 | 0 | 0.18742 | 0 | 0.0006105 | 0.18742 | 253238 | 725.2052 | 253237.9994
38958.5913 | 1 | 0 | 38958.5914 | 635 | 0 |  | 1548 | 1666 | 0.06105 | 0 | 38.7668 | 0 | 0.0006105 | 0 | 0.38767 | 0 | 0.0006105 | 0.38767 | 253238 | 298.9575 | 253237.9994
38958.5918 | 21 | 1 | 38958.5919 | 691 | 0 |  | 1590 | 1708 | 1.2821 | 0.06105 | 42.1856 | 0 | 0.012821 | 0.0006105 | 0.42186 | 0 | 0.01221 | 0.42186 | 12801.9744 | 266.6252 | 182638.0679
38958.5923 | 2122 | 0 | 38958.5923 | 2095 | 0 |  | 1632 | 1750 | 129.5482 | 0 | 127.8999 | 0 | 1.2955 | 0 | 1.279 | 0 | 1.2955 | 1.279 | 19.3864 | 20.9251 | 18.0909
38958.5928 | 2423 | 0 | 38958.5928 | 2126 | 0 |  | 1674 | 1792 | 147.9243 | 0 | 129.7924 | 0 | 1.4792 | 0 | 1.2979 | 0 | 1.4792 | 1.2979 | 4.5555 | 19.1618 | 3.0763
38958.5933 | 2467 | 0 | 38958.5933 | 971 | 0 |  | 1716 | 1834 | 150.6105 | 0 | 59.2796 | 0 | 1.5061 | 0 | 0.5928 | 0 | 1.5061 | 0.5928 | 2.6907 | 160.9042 | 1.1846
38958.5938 | 2368 | 0 | 38958.5938 | 2445 | 0 |  | 1758 | 1876 | 144.5665 | 0 | 149.2674 | 0 | 1.4457 | 0 | 1.4927 | 0 | 1.4457 | 1.4927 | 6.984 | 3.6147 | 5.5383
38958.5943 | 2240 | 0 | 38958.5943 | 2466 | 0 |  | 1800 | 1918 | 136.7521 | 0 | 150.5495 | 0 | 1.3675 | 0 | 1.5055 | 0 | 1.3675 | 1.5055 | 13.0973 | 2.7324 | 11.7298
38958.5947 | 2088 | 0 | 38958.5948 | 2274 | 0 |  | 1842 | 1960 | 127.4725 | 0 | 138.8278 | 0 | 1.2747 | 0 | 1.3883 | 0 | 1.2747 | 1.3883 | 21.3305 | 11.4063 | 20.0557
38958.5952 | 2135 | 0 | 38958.5953 | 2062 | 0 |  | 1884 | 2002 | 130.3419 | 0 | 125.8852 | 0 | 1.3034 | 0 | 1.2589 | 0 | 1.3034 | 1.2589 | 18.6595 | 22.8603 | 17.3561
38958.5957 | 2186 | 0 | 38958.5957 | 2255 | 0 |  | 1926 | 2044 | 133.4554 | 0 | 137.6679 | 0 | 1.3346 | 0 | 1.3767 | 0 | 1.3346 | 1.3767 | 15.8911 | 12.345 | 14.5566
38958.5962 | 2211 | 0 | 38958.5962 | 2128 | 0 |  | 1968 | 2086 | 134.9817 | 0 | 129.9145 | 0 | 1.3498 | 0 | 1.2991 | 0 | 1.3498 | 1.2991 | 14.5807 | 19.0498 | 13.2309
38958.5967 | 2145 | 0 | 38958.5967 | 2233 | 1 |  | 2009.5 | 2127.5 | 130.9524 | 0 | 136.3248 | 0.06105 | 1.3095 | 0 | 1.3632 | 0.0006105 | 1.3095 | 1.3626 | 18.1063 | 13.5027 | 16.7968
38958.5972 | 2040 | 0 | 38958.5972 | 2082 | 0 |  | 2052 | 2170 | 124.5421 | 0 | 127.1062 | 0 | 1.2454 | 0 | 1.2711 | 0 | 1.2454 | 1.2711 | 24.1853 | 21.6801 | 22.9399
38958.5977 | 2058 | 0 | 38958.5977 | 2187 | 0 |  | 2094 | 2212 | 125.641 | 0 | 133.5165 | 0 | 1.2564 | 0 | 1.3352 | 0 | 1.2564 | 1.3352 | 23.0991 | 15.8381 | 21.8427
38958.5981 | 2050 | 0 | 38958.5982 | 2113 | 0 |  | 2135.5 | 2253.5 | 125.1526 | 0 | 128.9988 | 0 | 1.2515 | 0 | 1.29 | 0 | 1.2515 | 1.29 | 23.5795 | 19.8949 | 22.328
38958.5986 | 2470 | 0 | 38958.5986 | 2000 | 0 |  | 2177.5 | 2295.5 | 150.7937 | 0 | 122.1001 | 0 | 1.5079 | 0 | 1.221 | 0 | 1.5079 | 1.221 | 2.566 | 26.669 | 1.0581
38958.5991 | 2517 | 0 | 38958.5991 | 2031 | 0 |  | 2220 | 2338 | 153.663 | 0 | 123.9927 | 0 | 1.5366 | 0 | 1.2399 | 0 | 1.5366 | 1.2399 | 0.65077 | 24.7356 | 0.88586
38958.5996 | 2513 | 0 | 38958.5996 | 2267 | 0 |  | 2262 | 2380 | 153.4188 | 0 | 138.4005 | 0 | 1.5342 | 0 | 1.384 | 0 | 1.5342 | 1.384 | 0.81098 | 11.7503 | 0.72321
38958.6001 | 2031 | 0 | 38958.6001 | 2398 | 0 |  | 2303.5 | 2421.5 | 123.9927 | 0 | 146.398 | 0 | 1.2399 | 0 | 1.464 | 0 | 1.2399 | 1.464 | 24.7356 | 5.6455 | 23.4957
38958.6006 | 2218 | 0 | 38958.6006 | 2001 | 0 |  | 2345.5 | 2463.5 | 135.409 | 0 | 122.1612 | 0 | 1.3541 | 0 | 1.2216 | 0 | 1.3541 | 1.2216 | 14.2191 | 26.6057 | 12.865
38958.6011 | 2361 | 0 | 38958.6011 | 2495 | 0 |  | 2387.5 | 2505.5 | 144.1392 | 0 | 152.3199 | 0 | 1.4414 | 0 | 1.5232 | 0 | 1.4414 | 1.5232 | 7.3011 | 1.5383 | 5.8598
38958.6016 | 2010 | 0 | 38958.6016 | 2183 | 0 |  | 2430 | 2548 | 122.7106 | 0 | 133.2723 | 0 | 1.2271 | 0 | 1.3327 | 0 | 1.2271 | 1.3327 | 26.0388 | 16.0504 | 24.8117
38958.602 | 1976 | 0 | 38958.602 | 2314 | 0 |  | 2471.5 | 2589.5 | 120.6349 | 0 | 141.2698 | 0 | 1.2063 | 0 | 1.4127 | 0 | 1.2063 | 1.4127 | 28.2075 | 9.4806 | 27.0011
38958.6025 | 2466 | 0 | 38958.6025 | 2294 | 0 |  | 2513.5 | 2631.5 | 150.5495 | 0 | 140.0488 | 0 | 1.5055 | 0 | 1.4005 | 0 | 1.5055 | 1.4005 | 2.7324 | 10.435 | 1.2269

## B3-B4
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 154.7241 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38958.5724 | 1 | 0 | 38958.5724 | 1 | 0 |  | -92.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5728 | 1 | 0 | 38958.5729 | 1 | 0 |  | -50.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5733 | 1 | 0 | 38958.5733 | 1 | 0 |  | -8.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5738 | 1 | 0 | 38958.5738 | 1 | 0 |  | 33.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5743 | 1 | 0 | 38958.5743 | 1 | 0 |  | 75.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5748 | 1 | 0 | 38958.5748 | 1 | 0 |  | 117.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5753 | 1 | 0 | 38958.5753 | 1 | 0 |  | 159.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5758 | 1 | 0 | 38958.5758 | 1 | 0 |  | 201.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5762 | 1 | 0 | 38958.5763 | 1 | 0 |  | 243.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5767 | 1 | 0 | 38958.5767 | 1 | 0 |  | 285.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5772 | 1 | 0 | 38958.5772 | 1 | 0 |  | 327.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5777 | 1 | 0 | 38958.5777 | 1 | 0 |  | 369.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5782 | 1 | 0 | 38958.5782 | 1 | 0 |  | 411.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5787 | 1 | 0 | 38958.5787 | 1 | 0 |  | 453.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5792 | 1 | 0 | 38958.5792 | 1 | 0 |  | 495.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5796 | 1 | 0 | 38958.5797 | 1 | 0 |  | 537 | 655 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5801 | 1 | 0 | 38958.5802 | 1 | 0 |  | 579.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5806 | 1 | 0 | 38958.5806 | 1 | 0 |  | 621.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5811 | 1 | 0 | 38958.5811 | 1 | 0 |  | 663.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5816 | 1 | 0 | 38958.5816 | 1 | 0 |  | 705.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5821 | 1 | 1 | 38958.5821 | 1 | 0 |  | 747 | 865 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 641801422.44 | 253338 | 253138.0789
38958.5826 | 1 | 0 | 38958.5826 | 1 | 0 |  | 789.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5831 | 1 | 0 | 38958.5831 | 1 | 0 |  | 831.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5835 | 1 | 0 | 38958.5836 | 1 | 0 |  | 873 | 991 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.584 | 1 | 0 | 38958.584 | 1 | 0 |  | 915.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5845 | 1 | 0 | 38958.5845 | 1 | 0 |  | 957 | 1075 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.585 | 1 | 0 | 38958.585 | 1 | 0 |  | 999.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5855 | 1 | 0 | 38958.5855 | 1 | 0 |  | 1041 | 1159 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.586 | 1 | 0 | 38958.586 | 1 | 0 |  | 1083 | 1201 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5865 | 1 | 0 | 38958.5865 | 1 | 0 |  | 1125.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5869 | 1 | 0 | 38958.587 | 1 | 0 |  | 1167.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5874 | 1 | 0 | 38958.5874 | 1 | 0 |  | 1209 | 1327 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5879 | 1 | 0 | 38958.5879 | 1 | 0 |  | 1251 | 1369 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5884 | 1 | 0 | 38958.5884 | 1 | 0 |  | 1293 | 1411 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5889 | 1 | 0 | 38958.5889 | 1 | 0 |  | 1335 | 1453 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5894 | 1 | 0 | 38958.5894 | 1 | 0 |  | 1377 | 1495 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5898 | 1 | 0 | 38958.5899 | 1 | 0 |  | 1419 | 1537 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5903 | 1 | 0 | 38958.5904 | 1 | 0 |  | 1461 | 1579 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
38958.5908 | 2 | 0 | 38958.5908 | 1 | 0 |  | 1503 | 1621 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126619 | 253338 | 126618.9988
38958.5913 | 27 | 4 | 38958.5913 | 12 | 3 |  | 1545 | 1663 | 1.6484 | 0.2442 | 0.7326 | 0.18315 | 0.016484 | 0.002442 | 0.007326 | 0.0018315 | 0.014042 | 0.0054945 | 10908.4005 | 28112.3487 | 62362.6663
38958.5918 | 636 | 565 | 38958.5918 | 663 | 602 |  | 1587 | 1705 | 38.8278 | 34.4933 | 40.4762 | 36.7521 | 0.38828 | 0.34493 | 0.40476 | 0.36752 | 0.043346 | 0.037241 | 3264.5966 | 4397.066 | 230.7487
38958.5923 | 2183 | 1 | 38958.5923 | 1991 | 2 |  | 1629 | 1747 | 133.2723 | 0.06105 | 121.5507 | 0.1221 | 1.3327 | 0.0006105 | 1.2155 | 0.001221 | 1.3321 | 1.2143 | 16.1305 | 27.4906 | 7555.1949
38958.5928 | 2158 | 1 | 38958.5928 | 1953 | 0 |  | 1671 | 1789 | 131.746 | 0.06105 | 119.2308 | 0 | 1.3175 | 0.0006105 | 1.1923 | 0 | 1.3168 | 1.1923 | 17.4765 | 29.7686 | 8611.1169
38958.5933 | 2165 | 1 | 38958.5933 | 2428 | 1 |  | 1713 | 1831 | 132.1734 | 0.06105 | 148.2295 | 0.06105 | 1.3217 | 0.0006105 | 1.4823 | 0.0006105 | 1.3211 | 1.4817 | 17.2508 | 4.3937 | 1550.4243
38958.5937 | 2222 | 0 | 38958.5938 | 1964 | 0 |  | 1755 | 1873 | 135.6532 | 0 | 119.9023 | 0 | 1.3565 | 0 | 1.199 | 0 | 1.3565 | 1.199 | 14.0585 | 29.0418 | 12.702
38958.5942 | 2398 | 1 | 38958.5942 | 2463 | 0 |  | 1797 | 1915 | 146.398 | 0.06105 | 150.3663 | 0 | 1.464 | 0.0006105 | 1.5037 | 0 | 1.4634 | 1.5037 | 5.7727 | 2.8981 | 381.2934
38958.5947 | 2010 | 0 | 38958.5947 | 1946 | 0 |  | 1839 | 1957 | 122.7106 | 0 | 118.8034 | 0 | 1.2271 | 0 | 1.188 | 0 | 1.2271 | 1.188 | 26.0886 | 30.2354 | 24.8615
38958.5952 | 2214 | 0 | 38958.5952 | 2183 | 0 |  | 1881 | 1999 | 135.1648 | 0 | 133.2723 | 0 | 1.3516 | 0 | 1.3327 | 0 | 1.3516 | 1.3327 | 14.4706 | 16.0962 | 13.119
38958.5957 | 2197 | 0 | 38958.5957 | 2285 | 0 |  | 1923 | 2041 | 134.127 | 0 | 139.4994 | 0 | 1.3413 | 0 | 1.395 | 0 | 1.3413 | 1.395 | 15.3564 | 10.9138 | 14.0151
38958.5962 | 1953 | 0 | 38958.5962 | 2518 | 0 |  | 1965 | 2083 | 119.2308 | 0 | 153.7241 | 0 | 1.1923 | 0 | 1.5372 | 0 | 1.1923 | 1.5372 | 29.7686 | 0.65052 | 28.5763
38958.5967 | 2248 | 0 | 38958.5967 | 2410 | 0 |  | 2007 | 2125 | 137.2405 | 0 | 147.1306 | 0 | 1.3724 | 0 | 1.4713 | 0 | 1.3724 | 1.4713 | 12.7393 | 5.161 | 11.3669
38958.5971 | 2090 | 0 | 38958.5972 | 2517 | 0 |  | 2049 | 2167 | 127.5946 | 0 | 153.663 | 0 | 1.2759 | 0 | 1.5366 | 0 | 1.2759 | 1.5366 | 21.2622 | 0.6905 | 19.9863
38958.5976 | 2480 | 0 | 38958.5977 | 2513 | 0 |  | 2091 | 2209 | 151.4042 | 0 | 153.4188 | 0 | 1.514 | 0 | 1.5342 | 0 | 1.514 | 1.5342 | 2.1927 | 0.85078 | 0.6787
38958.5981 | 2423 | 0 | 38958.5981 | 2273 | 0 |  | 2133 | 2251 | 147.9243 | 0 | 138.7668 | 0 | 1.4792 | 0 | 1.3877 | 0 | 1.4792 | 1.3877 | 4.5968 | 11.4993 | 3.1175
38958.5986 | 2506 | 0 | 38958.5986 | 2358 | 0 |  | 2175 | 2293 | 152.9915 | 0 | 143.956 | 0 | 1.5299 | 0 | 1.4396 | 0 | 1.5299 | 1.4396 | 1.1325 | 7.4801 | 0.39743
38958.5991 | 2475 | 0 | 38958.5991 | 2407 | 0 |  | 2217 | 2335 | 151.0989 | 0 | 146.9475 | 0 | 1.511 | 0 | 1.4695 | 0 | 1.511 | 1.4695 | 2.3992 | 5.2921 | 0.8882
38958.5996 | 2487 | 0 | 38958.5996 | 2306 | 0 |  | 2259 | 2377 | 151.8315 | 0 | 140.7814 | 0 | 1.5183 | 0 | 1.4078 | 0 | 1.5183 | 1.4078 | 1.9051 | 9.9037 | 0.38679
38958.6001 | 2177 | 0 | 38958.6001 | 2467 | 0 |  | 2301 | 2419 | 132.906 | 0 | 150.6105 | 0 | 1.3291 | 0 | 1.5061 | 0 | 1.3291 | 1.5061 | 16.4162 | 2.7313 | 15.0871
38958.6005 | 2256 | 0 | 38958.6006 | 2431 | 0 |  | 2343 | 2461 | 137.7289 | 0 | 148.4127 | 0 | 1.3773 | 0 | 1.4841 | 0 | 1.3773 | 1.4841 | 12.3395 | 4.2526 | 10.9622
38958.601 | 2467 | 0 | 38958.6011 | 2108 | 0 |  | 2385 | 2503 | 150.6105 | 0 | 128.6935 | 0 | 1.5061 | 0 | 1.2869 | 0 | 1.5061 | 1.2869 | 2.7313 | 20.2268 | 1.2251
38958.6015 | 2414 | 0 | 38958.6015 | 2468 | 0 |  | 2427 | 2545 | 147.3748 | 0 | 150.6716 | 0 | 1.4737 | 0 | 1.5067 | 0 | 1.4737 | 1.5067 | 4.9867 | 2.6896 | 3.513
38958.602 | 2191 | 0 | 38958.602 | 2053 | 0 |  | 2469 | 2587 | 133.7607 | 0 | 125.3358 | 0 | 1.3376 | 0 | 1.2534 | 0 | 1.3376 | 1.2534 | 15.6723 | 23.4476 | 14.3347
38958.6025 | 2400 | 1 | 38958.6025 | 2515 | 0 |  | 2511 | 2629 | 146.5201 | 0.06105 | 153.5409 | 0 | 1.4652 | 0.0006105 | 1.5354 | 0 | 1.4646 | 1.5354 | 5.9218 | 0.77058 | 101.9936

## A2-C6
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 153.8694 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38958.5723 | 1 | 0 | 38958.5723 | 1 | 0 |  | -95.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5728 | 1 | 0 | 38958.5728 | 1 | 0 |  | -53.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5733 | 1 | 0 | 38958.5733 | 1 | 0 |  | -11.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5738 | 1 | 0 | 38958.5738 | 1 | 0 |  | 30.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5743 | 1 | 0 | 38958.5743 | 1 | 0 |  | 72.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5748 | 1 | 0 | 38958.5748 | 1 | 0 |  | 114.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5752 | 1 | 0 | 38958.5753 | 1 | 0 |  | 156.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5757 | 1 | 0 | 38958.5757 | 1 | 0 |  | 198.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5762 | 1 | 0 | 38958.5762 | 1 | 0 |  | 240.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5767 | 1 | 0 | 38958.5767 | 1 | 0 |  | 282.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5772 | 1 | 0 | 38958.5772 | 1 | 0 |  | 324.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5777 | 1 | 0 | 38958.5777 | 1 | 0 |  | 366.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5782 | 1 | 0 | 38958.5782 | 1 | 0 |  | 408.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5786 | 1 | 0 | 38958.5787 | 1 | 0 |  | 450.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5791 | 1 | 0 | 38958.5791 | 1 | 0 |  | 492.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5796 | 1 | 0 | 38958.5796 | 1 | 0 |  | 534.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5801 | 1 | 0 | 38958.5801 | 1 | 0 |  | 576.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5806 | 1 | 0 | 38958.5806 | 1 | 0 |  | 618.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5811 | 1 | 0 | 38958.5811 | 1 | 0 |  | 660.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5816 | 1 | 0 | 38958.5816 | 1 | 0 |  | 702.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.582 | 1 | 0 | 38958.5821 | 1 | 0 |  | 744.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5825 | 1 | 0 | 38958.5825 | 1 | 0 |  | 786.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.583 | 1 | 0 | 38958.583 | 1 | 0 |  | 828.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5835 | 1 | 0 | 38958.5835 | 1 | 0 |  | 870.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.584 | 1 | 0 | 38958.584 | 1 | 0 |  | 912.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5845 | 1 | 0 | 38958.5845 | 1 | 0 |  | 954.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.585 | 1 | 0 | 38958.585 | 1 | 0 |  | 996.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5855 | 1 | 0 | 38958.5855 | 1 | 0 |  | 1038.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5859 | 1 | 0 | 38958.5859 | 1 | 0 |  | 1080.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5864 | 1 | 0 | 38958.5864 | 1 | 0 |  | 1122.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5869 | 1 | 0 | 38958.5869 | 1 | 0 |  | 1164.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5874 | 1 | 0 | 38958.5874 | 1 | 0 |  | 1206.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5879 | 1 | 0 | 38958.5879 | 1 | 0 |  | 1248.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5884 | 1 | 0 | 38958.5884 | 1 | 0 |  | 1290.5 | 1408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5889 | 1 | 0 | 38958.5889 | 1 | 0 |  | 1332.5 | 1450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5893 | 1 | 0 | 38958.5894 | 1 | 0 |  | 1374.5 | 1492.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
38958.5898 | 1 | 0 | 38958.5898 | 3 | 0 |  | 1416.5 | 1534.5 | 0.06105 | 0 | 0.18315 | 0 | 0.0006105 | 0 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 251938 | 83912.6667 | 251937.9994
38958.5903 | 1 | 0 | 38958.5903 | 79 | 0 |  | 1458.5 | 1576.5 | 0.06105 | 0 | 4.823 | 0 | 0.0006105 | 0 | 0.04823 | 0 | 0.0006105 | 0.04823 | 251938 | 3090.3544 | 251937.9994
38958.5908 | 1 | 0 | 38958.5908 | 241 | 0 |  | 1500.5 | 1618.5 | 0.06105 | 0 | 14.7131 | 0 | 0.0006105 | 0 | 0.14713 | 0 | 0.0006105 | 0.14713 | 251938 | 945.8008 | 251937.9994
38958.5913 | 1 | 0 | 38958.5913 | 678 | 0 |  | 1542.5 | 1660.5 | 0.06105 | 0 | 41.3919 | 0 | 0.0006105 | 0 | 0.41392 | 0 | 0.0006105 | 0.41392 | 251938 | 271.7375 | 251937.9994
38958.5918 | 2 | 0 | 38958.5918 | 722 | 0 |  | 1584.5 | 1702.5 | 0.1221 | 0 | 44.0781 | 0 | 0.001221 | 0 | 0.44078 | 0 | 0.001221 | 0.44078 | 125919 | 249.0831 | 125918.9988
38958.5923 | 2 | 0 | 38958.5923 | 2101 | 0 |  | 1626.5 | 1744.5 | 0.1221 | 0 | 128.2662 | 0 | 0.001221 | 0 | 1.2827 | 0 | 0.001221 | 1.2827 | 125919 | 19.961 | 125918.9988
38958.5927 | 3 | 0 | 38958.5928 | 2026 | 0 |  | 1668.5 | 1786.5 | 0.18315 | 0 | 123.6874 | 0 | 0.0018315 | 0 | 1.2369 | 0 | 0.0018315 | 1.2369 | 83912.6667 | 24.4018 | 83912.6648
38958.5932 | 2 | 0 | 38958.5932 | 1023 | 0 |  | 1710.5 | 1828.5 | 0.1221 | 0 | 62.4542 | 0 | 0.001221 | 0 | 0.62454 | 0 | 0.001221 | 0.62454 | 125919 | 146.3715 | 125918.9988
38958.5937 | 2 | 0 | 38958.5937 | 2142 | 0 |  | 1752.5 | 1870.5 | 0.1221 | 0 | 130.7692 | 0 | 0.001221 | 0 | 1.3077 | 0 | 0.001221 | 1.3077 | 125919 | 17.6648 | 125918.9988
38958.5942 | 2 | 0 | 38958.5942 | 2139 | 0 |  | 1794.5 | 1912.5 | 0.1221 | 0 | 130.5861 | 0 | 0.001221 | 0 | 1.3059 | 0 | 0.001221 | 1.3059 | 125919 | 17.8298 | 125918.9988
38958.5947 | 2 | 0 | 38958.5947 | 2331 | 0 |  | 1836.5 | 1954.5 | 0.1221 | 0 | 142.3077 | 0 | 0.001221 | 0 | 1.4231 | 0 | 0.001221 | 1.4231 | 125919 | 8.1244 | 125918.9988
38958.5952 | 2 | 0 | 38958.5952 | 2086 | 0 |  | 1878.5 | 1996.5 | 0.1221 | 0 | 127.3504 | 0 | 0.001221 | 0 | 1.2735 | 0 | 0.001221 | 1.2735 | 125919 | 20.8236 | 125918.9988
38958.5957 | 2 | 0 | 38958.5957 | 1965 | 0 |  | 1920.5 | 2038.5 | 0.1221 | 0 | 119.9634 | 0 | 0.001221 | 0 | 1.1996 | 0 | 0.001221 | 1.1996 | 125919 | 28.2636 | 125918.9988
38958.5961 | 2 | 0 | 38958.5962 | 2010 | 1 |  | 1962.5 | 2080.5 | 0.1221 | 0 | 122.7106 | 0.06105 | 0.001221 | 0 | 1.2271 | 0.0006105 | 0.001221 | 1.2265 | 125919 | 25.4545 | 125918.9988
38958.5966 | 2 | 0 | 38958.5966 | 2396 | 0 |  | 2004.5 | 2122.5 | 0.1221 | 0 | 146.2759 | 0 | 0.001221 | 0 | 1.4628 | 0 | 0.001221 | 1.4628 | 125919 | 5.1912 | 125918.9988
38958.5971 | 2 | 0 | 38958.5971 | 2175 | 0 |  | 2046.5 | 2164.5 | 0.1221 | 0 | 132.7839 | 0 | 0.001221 | 0 | 1.3278 | 0 | 0.001221 | 1.3278 | 125919 | 15.8795 | 125918.9988
38958.5976 | 2 | 0 | 38958.5976 | 2293 | 0 |  | 2088.5 | 2206.5 | 0.1221 | 0 | 139.9878 | 0 | 0.001221 | 0 | 1.3999 | 0 | 0.001221 | 1.3999 | 125919 | 9.9163 | 125918.9988
38958.5981 | 2 | 0 | 38958.5981 | 1968 | 0 |  | 2130.5 | 2248.5 | 0.1221 | 0 | 120.1465 | 0 | 0.001221 | 0 | 1.2015 | 0 | 0.001221 | 1.2015 | 125919 | 28.0681 | 125918.9988
38958.5986 | 2 | 0 | 38958.5986 | 2395 | 0 |  | 2172.5 | 2290.5 | 0.1221 | 0 | 146.2149 | 0 | 0.001221 | 0 | 1.4621 | 0 | 0.001221 | 1.4621 | 125919 | 5.2351 | 125918.9988
38958.5991 | 2 | 0 | 38958.5991 | 2299 | 0 |  | 2214.5 | 2332.5 | 0.1221 | 0 | 140.3541 | 0 | 0.001221 | 0 | 1.4035 | 0 | 0.001221 | 1.4035 | 125919 | 9.6294 | 125918.9988
38958.5995 | 2 | 0 | 38958.5996 | 1945 | 0 |  | 2256.5 | 2374.5 | 0.1221 | 0 | 118.7424 | 0 | 0.001221 | 0 | 1.1874 | 0 | 0.001221 | 1.1874 | 125919 | 29.5825 | 125918.9988
38958.6 | 2 | 0 | 38958.6 | 2494 | 0 |  | 2298 | 2416 | 0.1221 | 0 | 152.2589 | 0 | 0.001221 | 0 | 1.5226 | 0 | 0.001221 | 1.5226 | 125919 | 1.0577 | 125918.9988
38958.6005 | 2 | 0 | 38958.6005 | 2248 | 0 |  | 2340 | 2458 | 0.1221 | 0 | 137.2405 | 0 | 0.001221 | 0 | 1.3724 | 0 | 0.001221 | 1.3724 | 125919 | 12.1165 | 125918.9988
38958.601 | 2 | 0 | 38958.601 | 2504 | 0 |  | 2382 | 2500 | 0.1221 | 0 | 152.8694 | 0 | 0.001221 | 0 | 1.5287 | 0 | 0.001221 | 1.5287 | 125919 | 0.65415 | 125918.9988
38958.6015 | 2 | 0 | 38958.6015 | 1953 | 0 |  | 2424 | 2542 | 0.1221 | 0 | 119.2308 | 0 | 0.001221 | 0 | 1.1923 | 0 | 0.001221 | 1.1923 | 125919 | 29.0517 | 125918.9988
38958.602 | 2 | 0 | 38958.602 | 2024 | 0 |  | 2466 | 2584 | 0.1221 | 0 | 123.5653 | 0 | 0.001221 | 0 | 1.2357 | 0 | 0.001221 | 1.2357 | 125919 | 24.5247 | 125918.9988
38958.6025 | 2 | 0 | 38958.6025 | 1943 | 0 |  | 2508.5 | 2626.5 | 0.1221 | 0 | 118.6203 | 0 | 0.001221 | 0 | 1.1862 | 0 | 0.001221 | 1.1862 | 125919 | 29.7159 | 125918.9988

## A2-C5
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 152.8926 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38958.5723 | 1 | 0 | 38958.5723 | 1 | 0 |  | -98.5 | 19.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5728 | 1 | 0 | 38958.5728 | 1 | 0 |  | -56.5 | 61.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5733 | 1 | 0 | 38958.5733 | 1 | 0 |  | -14.5 | 103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5738 | 1 | 0 | 38958.5738 | 1 | 0 |  | 27.5 | 145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5742 | 1 | 0 | 38958.5742 | 1 | 0 |  | 69.5 | 187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5747 | 1 | 0 | 38958.5747 | 1 | 0 |  | 111.5 | 229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5752 | 1 | 0 | 38958.5752 | 1 | 0 |  | 153.5 | 271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5757 | 1 | 0 | 38958.5757 | 1 | 0 |  | 195.5 | 313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5762 | 1 | 0 | 38958.5762 | 1 | 0 |  | 237.5 | 355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5767 | 1 | 0 | 38958.5767 | 1 | 0 |  | 279.5 | 397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5772 | 1 | 0 | 38958.5772 | 1 | 0 |  | 321.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5776 | 1 | 0 | 38958.5777 | 1 | 0 |  | 363.5 | 481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5781 | 1 | 0 | 38958.5781 | 1 | 0 |  | 405.5 | 523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5786 | 1 | 0 | 38958.5786 | 1 | 0 |  | 447.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5791 | 1 | 0 | 38958.5791 | 1 | 0 |  | 489.5 | 607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5796 | 1 | 0 | 38958.5796 | 1 | 0 |  | 531.5 | 649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5801 | 1 | 0 | 38958.5801 | 1 | 0 |  | 573.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5806 | 1 | 0 | 38958.5806 | 1 | 0 |  | 615.5 | 733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.581 | 1 | 0 | 38958.5811 | 1 | 0 |  | 657.5 | 775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5815 | 1 | 0 | 38958.5815 | 1 | 0 |  | 699.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.582 | 1 | 0 | 38958.582 | 1 | 0 |  | 741.5 | 859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5825 | 1 | 0 | 38958.5825 | 1 | 0 |  | 783.5 | 901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.583 | 1 | 0 | 38958.583 | 1 | 0 |  | 825.5 | 943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5835 | 1 | 0 | 38958.5835 | 1 | 0 |  | 867.5 | 985.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.584 | 1 | 0 | 38958.584 | 1 | 0 |  | 909.5 | 1027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5844 | 1 | 0 | 38958.5845 | 1 | 0 |  | 951.5 | 1069.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5849 | 1 | 0 | 38958.5849 | 1 | 0 |  | 993.5 | 1111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5854 | 1 | 0 | 38958.5854 | 1 | 0 |  | 1035.5 | 1153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5859 | 1 | 0 | 38958.5859 | 1 | 0 |  | 1077.5 | 1195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5864 | 1 | 0 | 38958.5864 | 1 | 0 |  | 1119.5 | 1237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5869 | 1 | 0 | 38958.5869 | 1 | 0 |  | 1161.5 | 1279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5874 | 1 | 0 | 38958.5874 | 1 | 0 |  | 1203.5 | 1321.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5878 | 1 | 0 | 38958.5879 | 1 | 0 |  | 1245.5 | 1363.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5883 | 1 | 0 | 38958.5883 | 1 | 0 |  | 1287.5 | 1405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5888 | 1 | 0 | 38958.5888 | 1 | 0 |  | 1329.5 | 1447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5893 | 1 | 0 | 38958.5893 | 1 | 0 |  | 1371.5 | 1489.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5898 | 1 | 0 | 38958.5898 | 1 | 0 |  | 1413.5 | 1531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38958.5903 | 1 | 0 | 38958.5903 | 57 | 0 |  | 1455.5 | 1573.5 | 0.06105 | 0 | 3.4799 | 0 | 0.0006105 | 0 | 0.034799 | 0 | 0.0006105 | 0.034799 | 250338 | 4293.6491 | 250337.9994
38958.5908 | 1 | 0 | 38958.5908 | 219 | 0 |  | 1497.5 | 1615.5 | 0.06105 | 0 | 13.37 | 0 | 0.0006105 | 0 | 0.1337 | 0 | 0.0006105 | 0.1337 | 250338 | 1043.5525 | 250337.9994
38958.5912 | 1 | 0 | 38958.5913 | 595 | 0 |  | 1539.5 | 1657.5 | 0.06105 | 0 | 36.3248 | 0 | 0.0006105 | 0 | 0.36325 | 0 | 0.0006105 | 0.36325 | 250338 | 320.9042 | 250337.9994
38958.5917 | 1 | 0 | 38958.5917 | 755 | 0 |  | 1581.5 | 1699.5 | 0.06105 | 0 | 46.0928 | 0 | 0.0006105 | 0 | 0.46093 | 0 | 0.0006105 | 0.46093 | 250338 | 231.706 | 250337.9994
38958.5922 | 2 | 0 | 38958.5922 | 2396 | 0 |  | 1623.5 | 1741.5 | 0.1221 | 0 | 146.2759 | 0 | 0.001221 | 0 | 1.4628 | 0 | 0.001221 | 1.4628 | 125119 | 4.5234 | 125118.9988
38958.5927 | 2 | 0 | 38958.5927 | 2330 | 0 |  | 1665.5 | 1783.5 | 0.1221 | 0 | 142.2466 | 0 | 0.001221 | 0 | 1.4225 | 0 | 0.001221 | 1.4225 | 125119 | 7.4841 | 125118.9988
38958.5932 | 2 | 0 | 38958.5932 | 2135 | 0 |  | 1707.5 | 1825.5 | 0.1221 | 0 | 130.3419 | 0 | 0.001221 | 0 | 1.3034 | 0 | 0.001221 | 1.3034 | 125119 | 17.3012 | 125118.9988
38958.5937 | 2 | 0 | 38958.5937 | 2488 | 0 |  | 1749.5 | 1867.5 | 0.1221 | 0 | 151.8926 | 0 | 0.001221 | 0 | 1.5189 | 0 | 0.001221 | 1.5189 | 125119 | 0.65836 | 125118.9988
38958.5942 | 2 | 0 | 38958.5942 | 2469 | 0 |  | 1791.5 | 1909.5 | 0.1221 | 0 | 150.7326 | 0 | 0.001221 | 0 | 1.5073 | 0 | 0.001221 | 1.5073 | 125119 | 1.433 | 125118.9988
38958.5947 | 2 | 0 | 38958.5947 | 2108 | 0 |  | 1833.5 | 1951.5 | 0.1221 | 0 | 128.6935 | 0 | 0.001221 | 0 | 1.2869 | 0 | 0.001221 | 1.2869 | 125119 | 18.8036 | 125118.9988
38958.5951 | 2 | 0 | 38958.5952 | 2427 | 0 |  | 1875.5 | 1993.5 | 0.1221 | 0 | 148.1685 | 0 | 0.001221 | 0 | 1.4817 | 0 | 0.001221 | 1.4817 | 125119 | 3.1883 | 125118.9988
38958.5956 | 2 | 0 | 38958.5956 | 2353 | 0 |  | 1917.5 | 2035.5 | 0.1221 | 0 | 143.6508 | 0 | 0.001221 | 0 | 1.4365 | 0 | 0.001221 | 1.4365 | 125119 | 6.4335 | 125118.9988
38958.5961 | 2 | 0 | 38958.5961 | 2089 | 0 |  | 1959.5 | 2077.5 | 0.1221 | 0 | 127.5336 | 0 | 0.001221 | 0 | 1.2753 | 0 | 0.001221 | 1.2753 | 125119 | 19.8842 | 125118.9988
38958.5966 | 2 | 0 | 38958.5966 | 2004 | 0 |  | 2001.5 | 2119.5 | 0.1221 | 0 | 122.3443 | 0 | 0.001221 | 0 | 1.2234 | 0 | 0.001221 | 1.2234 | 125119 | 24.9691 | 125118.9988
38958.5971 | 2 | 0 | 38958.5971 | 2369 | 0 |  | 2043.5 | 2161.5 | 0.1221 | 0 | 144.6276 | 0 | 0.001221 | 0 | 1.4463 | 0 | 0.001221 | 1.4463 | 125119 | 5.7146 | 125118.9988
38958.5976 | 2 | 0 | 38958.5976 | 2406 | 1 |  | 2085.5 | 2203.5 | 0.1221 | 0 | 146.8864 | 0.06105 | 0.001221 | 0 | 1.4689 | 0.0006105 | 0.001221 | 1.4683 | 125119 | 4.1322 | 125118.9988
38958.5981 | 2 | 0 | 38958.5981 | 2259 | 0 |  | 2127.5 | 2245.5 | 0.1221 | 0 | 137.9121 | 0 | 0.001221 | 0 | 1.3791 | 0 | 0.001221 | 1.3791 | 125119 | 10.8623 | 125118.9988
38958.5985 | 2 | 0 | 38958.5986 | 2040 | 0 |  | 2169.5 | 2287.5 | 0.1221 | 0 | 124.5421 | 0 | 0.001221 | 0 | 1.2454 | 0 | 0.001221 | 1.2454 | 125119 | 22.7637 | 125118.9988
38958.599 | 2 | 0 | 38958.599 | 1981 | 0 |  | 2211.5 | 2329.5 | 0.1221 | 0 | 120.9402 | 0 | 0.001221 | 0 | 1.2094 | 0 | 0.001221 | 1.2094 | 125119 | 26.42 | 125118.9988
38958.5995 | 2 | 0 | 38958.5995 | 2098 | 0 |  | 2253.5 | 2371.5 | 0.1221 | 0 | 128.083 | 0 | 0.001221 | 0 | 1.2808 | 0 | 0.001221 | 1.2808 | 125119 | 19.3699 | 125118.9988
38958.6 | 1 | 0 | 38958.6 | 2366 | 0 |  | 2295.5 | 2413.5 | 0.06105 | 0 | 144.4444 | 0 | 0.0006105 | 0 | 1.4444 | 0 | 0.0006105 | 1.4444 | 250338 | 5.8487 | 250337.9994
38958.6005 | 2 | 0 | 38958.6005 | 2168 | 0 |  | 2337.5 | 2455.5 | 0.1221 | 0 | 132.3565 | 0 | 0.001221 | 0 | 1.3236 | 0 | 0.001221 | 1.3236 | 125119 | 15.5157 | 125118.9988
38958.601 | 2 | 0 | 38958.601 | 1934 | 0 |  | 2379.5 | 2497.5 | 0.1221 | 0 | 118.0708 | 0 | 0.001221 | 0 | 1.1807 | 0 | 0.001221 | 1.1807 | 125119 | 29.4922 | 125118.9988
38958.6015 | 2 | 0 | 38958.6015 | 1954 | 0 |  | 2421.5 | 2539.5 | 0.1221 | 0 | 119.2918 | 0 | 0.001221 | 0 | 1.1929 | 0 | 0.001221 | 1.1929 | 125119 | 28.1668 | 125118.9988
38958.6019 | 2 | 0 | 38958.602 | 1966 | 0 |  | 2463.5 | 2581.5 | 0.1221 | 0 | 120.0244 | 0 | 0.001221 | 0 | 1.2002 | 0 | 0.001221 | 1.2002 | 125119 | 27.3845 | 125118.9988
38958.6024 | 2 | 0 | 38958.6024 | 2487 | 0 |  | 2505.5 | 2623.5 | 0.1221 | 0 | 151.8315 | 0 | 0.001221 | 0 | 1.5183 | 0 | 0.001221 | 1.5183 | 125119 | 0.69883 | 125118.9988

## A2-B4
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38958.5723 | 1 | 0 | 38958.5723 | 1 | 0 |  | -101 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5727 | 1 | 0 | 38958.5728 | 1 | 0 |  | -59 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5732 | 1 | 0 | 38958.5733 | 1 | 0 |  | -17 | 101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5737 | 1 | 0 | 38958.5737 | 1 | 0 |  | 25 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5742 | 1 | 0 | 38958.5742 | 1 | 0 |  | 67 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5747 | 1 | 0 | 38958.5747 | 1 | 0 |  | 109 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5752 | 1 | 0 | 38958.5752 | 1 | 0 |  | 151 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5757 | 1 | 0 | 38958.5757 | 1 | 0 |  | 193 | 311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5761 | 1 | 0 | 38958.5762 | 1 | 0 |  | 235 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5766 | 1 | 0 | 38958.5767 | 1 | 0 |  | 277 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5771 | 1 | 0 | 38958.5771 | 1 | 0 |  | 319 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5776 | 1 | 0 | 38958.5776 | 1 | 0 |  | 361 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5781 | 1 | 0 | 38958.5781 | 1 | 0 |  | 403 | 521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5786 | 1 | 0 | 38958.5786 | 1 | 0 |  | 445 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5791 | 1 | 0 | 38958.5791 | 1 | 0 |  | 487 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5795 | 1 | 0 | 38958.5796 | 1 | 0 |  | 529 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.58 | 1 | 0 | 38958.5801 | 1 | 0 |  | 571 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5805 | 1 | 0 | 38958.5805 | 1 | 0 |  | 613 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.581 | 1 | 0 | 38958.581 | 1 | 0 |  | 655 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5815 | 1 | 0 | 38958.5815 | 1 | 0 |  | 697 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.582 | 1 | 0 | 38958.582 | 1 | 0 |  | 739 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5825 | 1 | 0 | 38958.5825 | 1 | 0 |  | 781 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.583 | 1 | 0 | 38958.583 | 1 | 0 |  | 822.5 | 940.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5834 | 1 | 0 | 38958.5835 | 1 | 0 |  | 865 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5839 | 1 | 0 | 38958.5839 | 1 | 0 |  | 906.5 | 1024.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5844 | 1 | 0 | 38958.5844 | 1 | 0 |  | 948.5 | 1066.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5849 | 1 | 0 | 38958.5849 | 1 | 0 |  | 991 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5854 | 1 | 0 | 38958.5854 | 1 | 0 |  | 1032.5 | 1150.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5859 | 1 | 0 | 38958.5859 | 1 | 0 |  | 1075 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5864 | 1 | 0 | 38958.5864 | 1 | 0 |  | 1116.5 | 1234.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5868 | 1 | 0 |  | 1 | 0 |  | 1158 | 1276 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5873 | 1 | 0 | 38958.5873 | 1 | 0 |  | 1200.5 | 1318.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5878 | 1 | 0 | 38958.5878 | 1 | 0 |  | 1242.5 | 1360.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5883 | 1 | 0 | 38958.5883 | 1 | 0 |  | 1284.5 | 1402.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5888 | 1 | 0 | 38958.5888 | 1 | 0 |  | 1326.5 | 1444.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5893 | 1 | 0 | 38958.5893 | 1 | 0 |  | 1368.5 | 1486.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5898 | 1 | 0 | 38958.5898 | 1 | 0 |  | 1410.5 | 1528.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5902 | 1 | 0 | 38958.5903 | 1 | 0 |  | 1452.5 | 1570.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5907 | 1 | 0 | 38958.5907 | 1 | 0 |  | 1494.5 | 1612.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5912 | 1 | 0 | 38958.5912 | 1 | 0 |  | 1536.5 | 1654.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5917 | 1 | 0 |  | 1 | 0 |  | 1578 | 1696 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5922 | 3 | 0 | 38958.5922 | 2 | 0 |  | 1620.5 | 1738.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38958.5927 | 2 | 0 | 38958.5927 | 2 | 0 |  | 1662.5 | 1780.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5932 | 2 | 0 | 38958.5932 | 2 | 0 |  | 1704.5 | 1822.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5936 | 3 | 0 | 38958.5937 | 2 | 0 |  | 1746.5 | 1864.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38958.5941 | 2 | 0 | 38958.5941 | 2 | 0 |  | 1788.5 | 1906.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5946 | 2 | 0 | 38958.5946 | 2 | 0 |  | 1830.5 | 1948.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5951 | 2 | 0 | 38958.5951 | 2 | 0 |  | 1872.5 | 1990.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5956 | 3 | 0 | 38958.5956 | 2 | 0 |  | 1914.5 | 2032.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38958.5961 | 2 | 0 | 38958.5961 | 2 | 0 |  | 1956.5 | 2074.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5966 | 2 | 0 | 38958.5966 | 2 | 0 |  | 1998.5 | 2116.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.597 | 3 | 0 | 38958.5971 | 2 | 0 |  | 2040.5 | 2158.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38958.5975 | 2 | 0 | 38958.5975 | 3 | 0 |  | 2082.5 | 2200.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38958.598 | 2 | 0 | 38958.598 | 2 | 0 |  | 2124.5 | 2242.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5985 | 2 | 0 | 38958.5985 | 2 | 0 |  | 2166.5 | 2284.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.599 | 2 | 0 | 38958.599 | 2 | 0 |  | 2208.5 | 2326.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.5995 | 2 | 0 | 38958.5995 | 2 | 0 |  | 2250.5 | 2368.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.6 | 2 | 0 | 38958.6 | 2 | 0 |  | 2292.5 | 2410.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.6005 | 2 | 0 | 38958.6005 | 3 | 0 |  | 2334.5 | 2452.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38958.6009 | 2 | 0 | 38958.6009 | 2 | 0 |  | 2376.5 | 2494.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.6014 | 2 | 0 | 38958.6014 | 2 | 0 |  | 2418.5 | 2536.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.6019 | 2 | 0 | 38958.6019 | 2 | 0 |  | 2460.5 | 2578.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38958.6024 | 2 | 0 | 38958.6024 | 1 | 0 |  | 2502.5 | 2620.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988

## A2-B3
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 154.9683 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38958.5722 | 1 | 0 | 38958.5722 | 1 | 0 |  | -104 | 14 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5727 | 1 | 0 | 38958.5727 | 1 | 0 |  | -61.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5732 | 1 | 0 | 38958.5732 | 1 | 0 |  | -20 | 98 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5737 | 1 | 0 | 38958.5737 | 1 | 0 |  | 22 | 140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5742 | 1 | 0 | 38958.5742 | 1 | 0 |  | 64 | 182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5747 | 1 | 0 | 38958.5747 | 1 | 0 |  | 106 | 224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5751 | 1 | 0 | 38958.5752 | 1 | 0 |  | 148 | 266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5756 | 1 | 0 | 38958.5756 | 1 | 0 |  | 190 | 308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5761 | 1 | 0 | 38958.5761 | 1 | 0 |  | 232 | 350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5766 | 1 | 0 | 38958.5766 | 1 | 0 |  | 274 | 392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5771 | 1 | 0 | 38958.5771 | 1 | 0 |  | 316 | 434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5776 | 1 | 0 | 38958.5776 | 1 | 0 |  | 358 | 476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5781 | 1 | 0 | 38958.5781 | 1 | 0 |  | 400 | 518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5785 | 1 | 0 | 38958.5786 | 1 | 0 |  | 442 | 560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.579 | 1 | 0 | 38958.5791 | 1 | 0 |  | 484 | 602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5795 | 1 | 0 | 38958.5795 | 1 | 0 |  | 526 | 644 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.58 | 1 | 0 | 38958.58 | 1 | 0 |  | 568 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5805 | 1 | 0 | 38958.5805 | 1 | 0 |  | 610 | 728 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.581 | 1 | 0 | 38958.581 | 1 | 0 |  | 652 | 770 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5815 | 1 | 0 | 38958.5815 | 1 | 0 |  | 694 | 812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5819 | 1 | 0 | 38958.582 | 1 | 0 |  | 736 | 854 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5824 | 1 | 0 | 38958.5825 | 1 | 0 |  | 778 | 896 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5829 | 1 | 0 | 38958.5829 | 1 | 0 |  | 820 | 938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5834 | 1 | 0 | 38958.5834 | 1 | 0 |  | 862 | 980 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5839 | 1 | 0 | 38958.5839 | 1 | 0 |  | 904 | 1022 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5844 | 1 | 0 | 38958.5844 | 1 | 0 |  | 946 | 1064 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5849 | 1 | 0 | 38958.5849 | 1 | 0 |  | 988 | 1106 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5853 | 1 | 0 | 38958.5854 | 1 | 0 |  | 1030 | 1148 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5858 | 1 | 0 | 38958.5859 | 1 | 0 |  | 1072 | 1190 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5863 | 1 | 0 | 38958.5863 | 1 | 0 |  | 1114 | 1232 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5868 | 1 | 0 | 38958.5868 | 1 | 0 |  | 1156 | 1274 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5873 | 1 | 0 | 38958.5873 | 1 | 0 |  | 1198 | 1316 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5878 | 1 | 0 | 38958.5878 | 1 | 0 |  | 1240 | 1358 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5883 | 1 | 0 | 38958.5883 | 1 | 0 |  | 1282 | 1400 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5888 | 1 | 0 | 38958.5888 | 1 | 0 |  | 1324 | 1442 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5892 | 1 | 0 | 38958.5893 | 1 | 0 |  | 1366 | 1484 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5897 | 1 | 0 | 38958.5897 | 1 | 0 |  | 1408 | 1526 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5902 | 1 | 0 | 38958.5902 | 1 | 0 |  | 1450 | 1568 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5907 | 1 | 0 | 38958.5907 | 1 | 0 |  | 1492 | 1610 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5912 | 1 | 0 | 38958.5912 | 1 | 0 |  | 1534 | 1652 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38958.5917 | 2 | 0 | 38958.5917 | 2 | 0 |  | 1576 | 1694 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 126819 | 126819 | 126818.9988
38958.5922 | 2 | 0 | 38958.5922 | 1894 | 0 |  | 1618 | 1736 | 0.1221 | 0 | 115.6288 | 0 | 0.001221 | 0 | 1.1563 | 0 | 0.001221 | 1.1563 | 126819 | 34.0222 | 126818.9988
38958.5926 | 3 | 0 | 38958.5927 | 2043 | 0 |  | 1660 | 1778 | 0.18315 | 0 | 124.7253 | 0 | 0.0018315 | 0 | 1.2473 | 0 | 0.0018315 | 1.2473 | 84512.6667 | 24.2477 | 84512.6648
38958.5931 | 2 | 0 | 38958.5931 | 2345 | 0 |  | 1702 | 1820 | 0.1221 | 0 | 143.1624 | 0 | 0.001221 | 0 | 1.4316 | 0 | 0.001221 | 1.4316 | 126819 | 8.2465 | 126818.9988
38958.5936 | 2 | 0 | 38958.5936 | 2493 | 0 |  | 1744 | 1862 | 0.1221 | 0 | 152.1978 | 0 | 0.001221 | 0 | 1.522 | 0 | 0.001221 | 1.522 | 126819 | 1.8203 | 126818.9988
38958.5941 | 2 | 0 | 38958.5941 | 2172 | 0 |  | 1786 | 1904 | 0.1221 | 0 | 132.6007 | 0 | 0.001221 | 0 | 1.326 | 0 | 0.001221 | 1.326 | 126819 | 16.8683 | 126818.9988
38958.5946 | 2 | 0 | 38958.5946 | 2502 | 0 |  | 1828 | 1946 | 0.1221 | 0 | 152.7473 | 0 | 0.001221 | 0 | 1.5275 | 0 | 0.001221 | 1.5275 | 126819 | 1.454 | 126818.9988
38958.5951 | 3 | 0 | 38958.5951 | 2254 | 0 |  | 1870 | 1988 | 0.18315 | 0 | 137.6068 | 0 | 0.0018315 | 0 | 1.3761 | 0 | 0.0018315 | 1.3761 | 84512.6667 | 12.6167 | 84512.6648
38958.5956 | 3 | 0 | 38958.5956 | 2004 | 0 |  | 1912 | 2030 | 0.18315 | 0 | 122.3443 | 0 | 0.0018315 | 0 | 1.2234 | 0 | 0.0018315 | 1.2234 | 84512.6667 | 26.6657 | 84512.6648
38958.596 | 3 | 0 | 38958.5961 | 2225 | 0 |  | 1954 | 2072 | 0.18315 | 0 | 135.8364 | 0 | 0.0018315 | 0 | 1.3584 | 0 | 0.0018315 | 1.3584 | 84512.6667 | 14.0845 | 84512.6648
38958.5965 | 2 | 0 | 38958.5966 | 2476 | 0 |  | 1996 | 2114 | 0.1221 | 0 | 151.16 | 0 | 0.001221 | 0 | 1.5116 | 0 | 0.001221 | 1.5116 | 126819 | 2.5194 | 126818.9988
38958.597 | 2 | 0 | 38958.597 | 2251 | 1 |  | 2038 | 2156 | 0.1221 | 0 | 137.4237 | 0.06105 | 0.001221 | 0 | 1.3742 | 0.0006105 | 0.001221 | 1.3736 | 126819 | 12.8169 | 126818.9988
38958.5975 | 2 | 0 | 38958.5975 | 2004 | 0 |  | 2080 | 2198 | 0.1221 | 0 | 122.3443 | 0 | 0.001221 | 0 | 1.2234 | 0 | 0.001221 | 1.2234 | 126819 | 26.6657 | 126818.9988
38958.598 | 2 | 0 | 38958.598 | 2109 | 0 |  | 2121.5 | 2239.5 | 0.1221 | 0 | 128.7546 | 0 | 0.001221 | 0 | 1.2875 | 0 | 0.001221 | 1.2875 | 126819 | 20.3594 | 126818.9988
38958.5985 | 2 | 1 | 38958.5985 | 2521 | 0 |  | 2164 | 2282 | 0.1221 | 0.06105 | 153.9072 | 0 | 0.001221 | 0.0006105 | 1.5391 | 0 | 0.0006105 | 1.5391 | 1760.7418 | 0.69905 | 1760.0476
38958.599 | 2 | 0 | 38958.599 | 2522 | 0 |  | 2206 | 2324 | 0.1221 | 0 | 153.9683 | 0 | 0.001221 | 0 | 1.5397 | 0 | 0.001221 | 1.5397 | 126819 | 0.64948 | 126818.9988
38958.5994 | 2 | 0 | 38958.5995 | 2319 | 0 |  | 2248 | 2366 | 0.1221 | 0 | 141.5751 | 0 | 0.001221 | 0 | 1.4158 | 0 | 0.001221 | 1.4158 | 126819 | 9.4601 | 126818.9988
38958.5999 | 2 | 0 | 38958.5999 | 1952 | 0 |  | 2289.5 | 2407.5 | 0.1221 | 0 | 119.1697 | 0 | 0.001221 | 0 | 1.1917 | 0 | 0.001221 | 1.1917 | 126819 | 30.04 | 126818.9988
38958.6004 | 2 | 0 | 38958.6004 | 2280 | 0 |  | 2331.5 | 2449.5 | 0.1221 | 0 | 139.1941 | 0 | 0.001221 | 0 | 1.3919 | 0 | 0.001221 | 1.3919 | 126819 | 11.3325 | 126818.9988
38958.6009 | 2 | 0 | 38958.6009 | 2340 | 0 |  | 2373.5 | 2491.5 | 0.1221 | 0 | 142.8571 | 0 | 0.001221 | 0 | 1.4286 | 0 | 0.001221 | 1.4286 | 126819 | 8.4778 | 126818.9988
38958.6014 | 2 | 0 | 38958.6014 | 2342 | 0 |  | 2416 | 2534 | 0.1221 | 0 | 142.9792 | 0 | 0.001221 | 0 | 1.4298 | 0 | 0.001221 | 1.4298 | 126819 | 8.3851 | 126818.9988
38958.6019 | 2 | 0 | 38958.6019 | 2355 | 0 |  | 2457.5 | 2575.5 | 0.1221 | 0 | 143.7729 | 0 | 0.001221 | 0 | 1.4377 | 0 | 0.001221 | 1.4377 | 126819 | 7.7868 | 126818.9988
38958.6024 | 2 | 0 | 38958.6024 | 2514 | 0 |  | 2499.5 | 2617.5 | 0.1221 | 0 | 153.4799 | 0 | 0.001221 | 0 | 1.5348 | 0 | 0.001221 | 1.5348 | 126819 | 0.96977 | 126818.9988

## A1-C6
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 153.5031 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38958.5722 | 1 | 0 | 38958.5722 | 1 | 0 |  | -106.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5727 | 1 | 0 | 38958.5727 | 1 | 0 |  | -64.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5732 | 1 | 0 | 38958.5732 | 1 | 0 |  | -22.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5737 | 1 | 0 | 38958.5737 | 1 | 0 |  | 19.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5741 | 1 | 0 | 38958.5742 | 1 | 0 |  | 61.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5746 | 1 | 0 | 38958.5746 | 1 | 0 |  | 103.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5751 | 1 | 0 | 38958.5751 | 1 | 0 |  | 145.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5756 | 1 | 0 | 38958.5756 | 1 | 0 |  | 187.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5761 | 1 | 0 | 38958.5761 | 1 | 0 |  | 229.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5766 | 1 | 0 | 38958.5766 | 1 | 0 |  | 271.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5771 | 1 | 0 | 38958.5771 | 1 | 0 |  | 313.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5775 | 1 | 0 | 38958.5776 | 1 | 0 |  | 355.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.578 | 1 | 0 | 38958.578 | 1 | 0 |  | 397.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5785 | 1 | 0 | 38958.5785 | 1 | 0 |  | 439.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.579 | 1 | 0 | 38958.579 | 1 | 0 |  | 481.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5795 | 1 | 0 | 38958.5795 | 1 | 0 |  | 523.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.58 | 1 | 0 | 38958.58 | 1 | 0 |  | 565.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5805 | 1 | 0 | 38958.5805 | 1 | 0 |  | 607 | 725 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5809 | 1 | 0 | 38958.581 | 1 | 0 |  | 649.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5814 | 1 | 0 | 38958.5814 | 1 | 0 |  | 691.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5819 | 1 | 0 | 38958.5819 | 1 | 0 |  | 733.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5824 | 1 | 0 | 38958.5824 | 1 | 0 |  | 775.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5829 | 1 | 0 | 38958.5829 | 1 | 0 |  | 817 | 935 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5834 | 1 | 0 | 38958.5834 | 1 | 0 |  | 859.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5839 | 1 | 0 | 38958.5839 | 1 | 0 |  | 901 | 1019 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5843 | 1 | 0 | 38958.5844 | 1 | 0 |  | 943 | 1061 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5848 | 1 | 0 | 38958.5848 | 1 | 0 |  | 985.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5853 | 1 | 0 | 38958.5853 | 1 | 0 |  | 1027 | 1145 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5858 | 1 | 0 | 38958.5858 | 1 | 0 |  | 1069.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5863 | 1 | 0 | 38958.5863 | 1 | 0 |  | 1111 | 1229 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5868 | 1 | 0 | 38958.5868 | 1 | 0 |  | 1153 | 1271 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5873 | 1 | 0 | 38958.5873 | 1 | 0 |  | 1195 | 1313 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5877 | 1 | 0 | 38958.5878 | 1 | 0 |  | 1237 | 1355 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5882 | 1 | 0 | 38958.5883 | 1 | 0 |  | 1279.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5887 | 1 | 0 | 38958.5887 | 1 | 0 |  | 1321 | 1439 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5892 | 1 | 0 | 38958.5892 | 1 | 0 |  | 1363 | 1481 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251338 | 251338 | 251337.9994
38958.5897 | 1 | 0 | 38958.5897 | 2 | 0 |  | 1405 | 1523 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 251338 | 125619 | 251337.9994
38958.5902 | 1 | 0 | 38958.5902 | 28 | 0 |  | 1447 | 1565 | 0.06105 | 0 | 1.7094 | 0 | 0.0006105 | 0 | 0.017094 | 0 | 0.0006105 | 0.017094 | 251338 | 8879.9286 | 251337.9994
38958.5907 | 1 | 0 | 38958.5907 | 185 | 0 |  | 1489 | 1607 | 0.06105 | 0 | 11.2943 | 0 | 0.0006105 | 0 | 0.11294 | 0 | 0.0006105 | 0.11294 | 251338 | 1259.1243 | 251337.9994
38958.5911 | 1 | 0 | 38958.5912 | 548 | 0 |  | 1531 | 1649 | 0.06105 | 0 | 33.4554 | 0 | 0.0006105 | 0 | 0.33455 | 0 | 0.0006105 | 0.33455 | 251338 | 358.8285 | 251337.9994
38958.5916 | 1 | 0 | 38958.5917 | 824 | 0 |  | 1573 | 1691 | 0.06105 | 0 | 50.3053 | 0 | 0.0006105 | 0 | 0.50305 | 0 | 0.0006105 | 0.50305 | 251338 | 205.1432 | 251337.9994
38958.5921 | 2 | 0 | 38958.5921 | 2359 | 0 |  | 1615 | 1733 | 0.1221 | 0 | 144.0171 | 0 | 0.001221 | 0 | 1.4402 | 0 | 0.001221 | 1.4402 | 125619 | 6.5867 | 125618.9988
38958.5926 | 2 | 0 | 38958.5926 | 2297 | 0 |  | 1657 | 1775 | 0.1221 | 0 | 140.232 | 0 | 0.001221 | 0 | 1.4023 | 0 | 0.001221 | 1.4023 | 125619 | 9.4636 | 125618.9988
38958.5931 | 2 | 0 | 38958.5931 | 1922 | 0 |  | 1699 | 1817 | 0.1221 | 0 | 117.3382 | 0 | 0.001221 | 0 | 1.1734 | 0 | 0.001221 | 1.1734 | 125619 | 30.821 | 125618.9988
38958.5936 | 3 | 0 | 38958.5936 | 2351 | 0 |  | 1741 | 1859 | 0.18315 | 0 | 143.5287 | 0 | 0.0018315 | 0 | 1.4353 | 0 | 0.0018315 | 1.4353 | 83712.6667 | 6.9494 | 83712.6648
38958.5941 | 2 | 0 | 38958.5941 | 2248 | 0 |  | 1783 | 1901 | 0.1221 | 0 | 137.2405 | 0 | 0.001221 | 0 | 1.3724 | 0 | 0.001221 | 1.3724 | 125619 | 11.8496 | 125618.9988
38958.5945 | 2 | 0 | 38958.5946 | 1951 | 0 |  | 1825 | 1943 | 0.1221 | 0 | 119.1087 | 0 | 0.001221 | 0 | 1.1911 | 0 | 0.001221 | 1.1911 | 125619 | 28.8765 | 125618.9988
38958.595 | 2 | 0 | 38958.5951 | 2404 | 0 |  | 1867 | 1985 | 0.1221 | 0 | 146.7643 | 0 | 0.001221 | 0 | 1.4676 | 0 | 0.001221 | 1.4676 | 125619 | 4.5915 | 125618.9988
38958.5955 | 2 | 0 | 38958.5955 | 2046 | 0 |  | 1909 | 2027 | 0.1221 | 0 | 124.9084 | 0 | 0.001221 | 0 | 1.2491 | 0 | 0.001221 | 1.2491 | 125619 | 22.8925 | 125618.9988
38958.596 | 2 | 0 | 38958.596 | 2205 | 0 |  | 1951 | 2069 | 0.1221 | 0 | 134.6154 | 0 | 0.001221 | 0 | 1.3462 | 0 | 0.001221 | 1.3462 | 125619 | 14.0308 | 125618.9988
38958.5965 | 2 | 0 | 38958.5965 | 2489 | 1 |  | 1993 | 2111 | 0.1221 | 0 | 151.9536 | 0.06105 | 0.001221 | 0 | 1.5195 | 0.0006105 | 0.001221 | 1.5189 | 125619 | 1.0603 | 125618.9988
38958.597 | 2 | 0 | 38958.597 | 2451 | 0 |  | 2035 | 2153 | 0.1221 | 0 | 149.6337 | 0 | 0.001221 | 0 | 1.4963 | 0 | 0.001221 | 1.4963 | 125619 | 2.5859 | 125618.9988
38958.5975 | 2 | 0 | 38958.5975 | 2299 | 0 |  | 2077 | 2195 | 0.1221 | 0 | 140.3541 | 0 | 0.001221 | 0 | 1.4035 | 0 | 0.001221 | 1.4035 | 125619 | 9.3684 | 125618.9988
38958.598 | 2 | 0 | 38958.598 | 2007 | 0 |  | 2119 | 2237 | 0.1221 | 0 | 122.5275 | 0 | 0.001221 | 0 | 1.2253 | 0 | 0.001221 | 1.2253 | 125619 | 25.2805 | 125618.9988
38958.5984 | 3 | 0 | 38958.5985 | 2282 | 0 |  | 2161 | 2279 | 0.18315 | 0 | 139.3162 | 0 | 0.0018315 | 0 | 1.3932 | 0 | 0.0018315 | 1.3932 | 83712.6667 | 10.1832 | 83712.6648
38958.5989 | 2 | 0 | 38958.5989 | 2060 | 0 |  | 2203 | 2321 | 0.1221 | 0 | 125.7631 | 0 | 0.001221 | 0 | 1.2576 | 0 | 0.001221 | 1.2576 | 125619 | 22.0573 | 125618.9988
38958.5994 | 2 | 0 | 38958.5994 | 2184 | 0 |  | 2245 | 2363 | 0.1221 | 0 | 133.3333 | 0 | 0.001221 | 0 | 1.3333 | 0 | 0.001221 | 1.3333 | 125619 | 15.1273 | 125618.9988
38958.5999 | 2 | 0 | 38958.5999 | 2498 | 0 |  | 2287 | 2405 | 0.1221 | 0 | 152.5031 | 0 | 0.001221 | 0 | 1.525 | 0 | 0.001221 | 1.525 | 125619 | 0.65572 | 125618.9988
38958.6004 | 2 | 0 | 38958.6004 | 2342 | 0 |  | 2329 | 2447 | 0.1221 | 0 | 142.9792 | 0 | 0.001221 | 0 | 1.4298 | 0 | 0.001221 | 1.4298 | 125619 | 7.3604 | 125618.9988
38958.6009 | 2 | 0 | 38958.6009 | 1940 | 0 |  | 2371 | 2489 | 0.1221 | 0 | 118.4371 | 0 | 0.001221 | 0 | 1.1844 | 0 | 0.001221 | 1.1844 | 125619 | 29.6072 | 125618.9988
38958.6014 | 2 | 0 | 38958.6014 | 2444 | 0 |  | 2413 | 2531 | 0.1221 | 0 | 149.2063 | 0 | 0.001221 | 0 | 1.4921 | 0 | 0.001221 | 1.4921 | 125619 | 2.8797 | 125618.9988
38958.6018 | 2 | 0 | 38958.6019 | 2248 | 0 |  | 2455 | 2573 | 0.1221 | 0 | 137.2405 | 0 | 0.001221 | 0 | 1.3724 | 0 | 0.001221 | 1.3724 | 125619 | 11.8496 | 125618.9988
38958.6023 | 3 | 0 | 38958.6023 | 2461 | 0 |  | 2497 | 2615 | 0.18315 | 0 | 150.2442 | 0 | 0.0018315 | 0 | 1.5024 | 0 | 0.0018315 | 1.5024 | 83712.6667 | 2.169 | 83712.6648

## A1-C5
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 152.221 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38958.5722 | 1 | 0 | 38958.5722 | 1 | 0 |  | -109.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5727 | 1 | 0 | 38958.5727 | 1 | 0 |  | -67.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5731 | 1 | 0 | 38958.5731 | 1 | 0 |  | -25.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5736 | 1 | 0 | 38958.5736 | 1 | 0 |  | 16.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5741 | 1 | 0 | 38958.5741 | 1 | 0 |  | 58.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5746 | 1 | 0 | 38958.5746 | 1 | 0 |  | 100.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5751 | 1 | 0 | 38958.5751 | 1 | 0 |  | 142.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5756 | 1 | 0 | 38958.5756 | 1 | 0 |  | 184.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5761 | 1 | 0 | 38958.5761 | 1 | 0 |  | 226.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5765 | 1 | 0 | 38958.5766 | 1 | 0 |  | 268.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.577 | 1 | 0 | 38958.577 | 1 | 0 |  | 310.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5775 | 1 | 0 | 38958.5775 | 1 | 0 |  | 352.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.578 | 1 | 0 | 38958.578 | 1 | 0 |  | 394.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5785 | 1 | 0 | 38958.5785 | 1 | 0 |  | 436.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.579 | 1 | 0 | 38958.579 | 1 | 0 |  | 478.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5795 | 1 | 0 | 38958.5795 | 1 | 0 |  | 520.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5799 | 1 | 0 | 38958.58 | 1 | 0 |  | 562.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5804 | 1 | 0 | 38958.5804 | 1 | 0 |  | 604.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5809 | 1 | 0 | 38958.5809 | 1 | 0 |  | 646.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5814 | 1 | 0 | 38958.5814 | 1 | 0 |  | 688.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5819 | 1 | 0 | 38958.5819 | 1 | 0 |  | 730.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5824 | 1 | 0 | 38958.5824 | 1 | 0 |  | 772.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5829 | 1 | 0 | 38958.5829 | 1 | 0 |  | 814.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5833 | 1 | 0 | 38958.5834 | 1 | 0 |  | 856.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5838 | 1 | 0 | 38958.5838 | 1 | 0 |  | 898.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5843 | 1 | 0 | 38958.5843 | 1 | 0 |  | 940.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5848 | 1 | 0 | 38958.5848 | 1 | 0 |  | 982.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5853 | 1 | 0 | 38958.5853 | 1 | 0 |  | 1024.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5858 | 1 | 0 | 38958.5858 | 1 | 0 |  | 1066.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5863 | 1 | 0 | 38958.5863 | 1 | 0 |  | 1108.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5867 | 1 | 0 | 38958.5868 | 1 | 0 |  | 1150.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5872 | 1 | 0 | 38958.5872 | 1 | 0 |  | 1192.5 | 1310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5877 | 1 | 0 | 38958.5877 | 1 | 0 |  | 1234.5 | 1352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5882 | 1 | 0 | 38958.5882 | 1 | 0 |  | 1276.5 | 1394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5887 | 1 | 0 | 38958.5887 | 1 | 0 |  | 1318.5 | 1436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5892 | 1 | 0 | 38958.5892 | 1 | 0 |  | 1360.5 | 1478.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5897 | 1 | 0 | 38958.5897 | 1 | 0 |  | 1402.5 | 1520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
38958.5902 | 1 | 0 | 38958.5902 | 22 | 0 |  | 1444.5 | 1562.5 | 0.06105 | 0 | 1.3431 | 0 | 0.0006105 | 0 | 0.013431 | 0 | 0.0006105 | 0.013431 | 249238 | 11233.5455 | 249237.9994
38958.5906 | 1 | 0 | 38958.5906 | 150 | 0 |  | 1486.5 | 1604.5 | 0.06105 | 0 | 9.1575 | 0 | 0.0006105 | 0 | 0.091575 | 0 | 0.0006105 | 0.091575 | 249238 | 1562.2533 | 249237.9994
38958.5911 | 1 | 0 | 38958.5911 | 622 | 0 |  | 1528.5 | 1646.5 | 0.06105 | 0 | 37.9731 | 0 | 0.0006105 | 0 | 0.37973 | 0 | 0.0006105 | 0.37973 | 249238 | 300.865 | 249237.9994
38958.5916 | 1 | 0 | 38958.5916 | 697 | 0 |  | 1570.5 | 1688.5 | 0.06105 | 0 | 42.5519 | 0 | 0.0006105 | 0 | 0.42552 | 0 | 0.0006105 | 0.42552 | 249238 | 257.7303 | 249237.9994
38958.5921 | 2 | 0 | 38958.5921 | 1907 | 0 |  | 1612.5 | 1730.5 | 0.1221 | 0 | 116.4225 | 0 | 0.001221 | 0 | 1.1642 | 0 | 0.001221 | 1.1642 | 124569 | 30.7488 | 124568.9988
38958.5926 | 2 | 0 | 38958.5926 | 2107 | 0 |  | 1654.5 | 1772.5 | 0.1221 | 0 | 128.6325 | 0 | 0.001221 | 0 | 1.2863 | 0 | 0.001221 | 1.2863 | 124569 | 18.3379 | 124568.9988
38958.5931 | 2 | 0 | 38958.5931 | 951 | 0 |  | 1696.5 | 1814.5 | 0.1221 | 0 | 58.0586 | 0 | 0.001221 | 0 | 0.58059 | 0 | 0.001221 | 0.58059 | 124569 | 162.1851 | 124568.9988
38958.5936 | 3 | 0 | 38958.5936 | 2172 | 0 |  | 1738.5 | 1856.5 | 0.18315 | 0 | 132.6007 | 0 | 0.0018315 | 0 | 1.326 | 0 | 0.0018315 | 1.326 | 83012.6667 | 14.7965 | 83012.6648
38958.594 | 2 | 0 | 38958.5941 | 1982 | 0 |  | 1780.5 | 1898.5 | 0.1221 | 0 | 121.0012 | 0 | 0.001221 | 0 | 1.21 | 0 | 0.001221 | 1.21 | 124569 | 25.8012 | 124568.9988
38958.5945 | 2 | 0 | 38958.5945 | 2200 | 0 |  | 1822.5 | 1940.5 | 0.1221 | 0 | 134.3101 | 0 | 0.001221 | 0 | 1.3431 | 0 | 0.001221 | 1.3431 | 124569 | 13.3355 | 124568.9988
38958.595 | 3 | 0 | 38958.595 | 2088 | 0 |  | 1864.5 | 1982.5 | 0.18315 | 0 | 127.4725 | 0 | 0.0018315 | 0 | 1.2747 | 0 | 0.0018315 | 1.2747 | 83012.6667 | 19.4148 | 83012.6648
38958.5955 | 2 | 0 | 38958.5955 | 1989 | 0 |  | 1906.5 | 2024.5 | 0.1221 | 0 | 121.4286 | 0 | 0.001221 | 0 | 1.2143 | 0 | 0.001221 | 1.2143 | 124569 | 25.3585 | 124568.9988
38958.596 | 2 | 0 | 38958.596 | 2091 | 0 |  | 1948.5 | 2066.5 | 0.1221 | 0 | 127.6557 | 0 | 0.001221 | 0 | 1.2766 | 0 | 0.001221 | 1.2766 | 124569 | 19.2434 | 124568.9988
38958.5965 | 2 | 0 | 38958.5965 | 2407 | 0 |  | 1990.5 | 2108.5 | 0.1221 | 0 | 146.9475 | 0 | 0.001221 | 0 | 1.4695 | 0 | 0.001221 | 1.4695 | 124569 | 3.5887 | 124568.9988
38958.597 | 2 | 0 | 38958.597 | 2185 | 0 |  | 2032.5 | 2150.5 | 0.1221 | 0 | 133.3944 | 0 | 0.001221 | 0 | 1.3339 | 0 | 0.001221 | 1.3339 | 124569 | 14.1135 | 124568.9988
38958.5974 | 2 | 0 | 38958.5975 | 2186 | 0 |  | 2074 | 2192 | 0.1221 | 0 | 133.4554 | 0 | 0.001221 | 0 | 1.3346 | 0 | 0.001221 | 1.3346 | 124569 | 14.0613 | 124568.9988
38958.5979 | 2 | 0 | 38958.5979 | 2198 | 0 |  | 2116.5 | 2234.5 | 0.1221 | 0 | 134.188 | 0 | 0.001221 | 0 | 1.3419 | 0 | 0.001221 | 1.3419 | 124569 | 13.4386 | 124568.9988
38958.5984 | 2 | 1 | 38958.5984 | 2162 | 0 |  | 2158 | 2276 | 0.1221 | 0.06105 | 131.9902 | 0 | 0.001221 | 0.0006105 | 1.3199 | 0 | 0.0006105 | 1.3199 | 45099.1197 | 22.1032 | 45081.0176
38958.5989 | 2 | 0 | 38958.5989 | 2477 | 0 |  | 2200 | 2318 | 0.1221 | 0 | 151.221 | 0 | 0.001221 | 0 | 1.5122 | 0 | 0.001221 | 1.5122 | 124569 | 0.66128 | 124568.9988
38958.5994 | 2 | 0 | 38958.5994 | 2476 | 0 |  | 2242.5 | 2360.5 | 0.1221 | 0 | 151.16 | 0 | 0.001221 | 0 | 1.5116 | 0 | 0.001221 | 1.5116 | 124569 | 0.70194 | 124568.9988
38958.5999 | 2 | 1 | 38958.5999 | 2171 | 0 |  | 2284 | 2402 | 0.1221 | 0.06105 | 132.5397 | 0 | 0.001221 | 0.0006105 | 1.3254 | 0 | 0.0006105 | 1.3254 | 43447.0624 | 21.1225 | 43429.6234
38958.6004 | 2 | 0 | 38958.6004 | 2013 | 0 |  | 2326.5 | 2444.5 | 0.1221 | 0 | 122.8938 | 0 | 0.001221 | 0 | 1.2289 | 0 | 0.001221 | 1.2289 | 124569 | 23.8639 | 124568.9988
38958.6008 | 2 | 0 | 38958.6009 | 2005 | 0 |  | 2368.5 | 2486.5 | 0.1221 | 0 | 122.4054 | 0 | 0.001221 | 0 | 1.2241 | 0 | 0.001221 | 1.2241 | 124569 | 24.3581 | 124568.9988
38958.6013 | 3 | 0 | 38958.6013 | 1931 | 0 |  | 2410 | 2528 | 0.18315 | 0 | 117.8877 | 0 | 0.0018315 | 0 | 1.1789 | 0 | 0.0018315 | 1.1789 | 83012.6667 | 29.1238 | 83012.6648
38958.6018 | 2 | 0 | 38958.6018 | 2171 | 0 |  | 2452.5 | 2570.5 | 0.1221 | 0 | 132.5397 | 0 | 0.001221 | 0 | 1.3254 | 0 | 0.001221 | 1.3254 | 124569 | 14.8494 | 124568.9988
38958.6023 | 2 | 0 | 38958.6023 | 1957 | 0 |  | 2494 | 2612 | 0.1221 | 0 | 119.475 | 0 | 0.001221 | 0 | 1.1947 | 0 | 0.001221 | 1.1947 | 124569 | 27.4083 | 124568.9988

## A1-B4
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 152.5263 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38958.5721 | 1 | 0 | 38958.5722 | 1 | 0 |  | -112 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5726 | 1 | 0 | 38958.5726 | 1 | 0 |  | -70.5 | 47.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5731 | 1 | 0 | 38958.5731 | 1 | 0 |  | -28 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5736 | 1 | 0 | 38958.5736 | 1 | 0 |  | 13.5 | 131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5741 | 1 | 0 | 38958.5741 | 1 | 0 |  | 55.5 | 173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5746 | 1 | 0 | 38958.5746 | 1 | 0 |  | 97.5 | 215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.575 | 1 | 0 | 38958.5751 | 1 | 0 |  | 139.5 | 257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5755 | 1 | 0 | 38958.5755 | 1 | 0 |  | 181.5 | 299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.576 | 1 | 0 | 38958.576 | 1 | 0 |  | 223.5 | 341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5765 | 1 | 0 | 38958.5765 | 1 | 0 |  | 265.5 | 383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.577 | 1 | 0 | 38958.577 | 1 | 0 |  | 307.5 | 425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5775 | 1 | 0 | 38958.5775 | 1 | 0 |  | 349.5 | 467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.578 | 1 | 0 | 38958.578 | 1 | 0 |  | 391.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5784 | 1 | 0 | 38958.5785 | 1 | 0 |  | 433.5 | 551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5789 | 1 | 0 | 38958.5789 | 1 | 0 |  | 475.5 | 593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5794 | 1 | 0 | 38958.5794 | 1 | 0 |  | 517.5 | 635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5799 | 1 | 0 | 38958.5799 | 1 | 0 |  | 559.5 | 677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5804 | 1 | 0 | 38958.5804 | 1 | 0 |  | 601.5 | 719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5809 | 1 | 0 | 38958.5809 | 1 | 0 |  | 643.5 | 761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5814 | 1 | 0 | 38958.5814 | 1 | 0 |  | 685.5 | 803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5819 | 1 | 0 | 38958.5819 | 1 | 0 |  | 727.5 | 845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5823 | 1 | 0 | 38958.5823 | 2 | 0 |  | 769.5 | 887.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249738 | 124819 | 249737.9994
38958.5828 | 1 | 0 | 38958.5828 | 1 | 0 |  | 811.5 | 929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5833 | 1 | 0 | 38958.5833 | 1 | 0 |  | 853.5 | 971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5838 | 1 | 0 | 38958.5838 | 1 | 0 |  | 895.5 | 1013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5843 | 1 | 0 | 38958.5843 | 1 | 0 |  | 937.5 | 1055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5848 | 1 | 0 | 38958.5848 | 1 | 0 |  | 979.5 | 1097.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5853 | 1 | 0 | 38958.5853 | 1 | 0 |  | 1021.5 | 1139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5857 | 1 | 0 | 38958.5858 | 1 | 0 |  | 1063.5 | 1181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5862 | 1 | 0 | 38958.5862 | 1 | 0 |  | 1105.5 | 1223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5867 | 1 | 0 | 38958.5867 | 1 | 0 |  | 1147.5 | 1265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5872 | 1 | 0 | 38958.5872 | 1 | 0 |  | 1189.5 | 1307.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5877 | 1 | 0 | 38958.5877 | 1 | 0 |  | 1231.5 | 1349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5882 | 1 | 0 | 38958.5882 | 1 | 0 |  | 1273.5 | 1391.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5887 | 1 | 0 | 38958.5887 | 1 | 0 |  | 1315.5 | 1433.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5891 | 1 | 0 | 38958.5892 | 1 | 0 |  | 1357.5 | 1475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5896 | 1 | 0 | 38958.5896 | 1 | 0 |  | 1399.5 | 1517.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5901 | 1 | 0 | 38958.5901 | 1 | 0 |  | 1441.5 | 1559.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5906 | 1 | 0 | 38958.5906 | 1 | 0 |  | 1483.5 | 1601.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5911 | 1 | 0 | 38958.5911 | 1 | 0 |  | 1525.5 | 1643.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5916 | 1 | 0 | 38958.5916 | 1 | 0 |  | 1567.5 | 1685.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38958.5921 | 2 | 0 | 38958.5921 | 1857 | 0 |  | 1609.5 | 1727.5 | 0.1221 | 0 | 113.37 | 0 | 0.001221 | 0 | 1.1337 | 0 | 0.001221 | 1.1337 | 124819 | 34.5385 | 124818.9988
38958.5925 | 2 | 0 | 38958.5926 | 2042 | 0 |  | 1651.5 | 1769.5 | 0.1221 | 0 | 124.6642 | 0 | 0.001221 | 0 | 1.2466 | 0 | 0.001221 | 1.2466 | 124819 | 22.3497 | 124818.9988
38958.593 | 3 | 0 | 38958.593 | 2120 | 0 |  | 1693.5 | 1811.5 | 0.18315 | 0 | 129.4261 | 0 | 0.0018315 | 0 | 1.2943 | 0 | 0.0018315 | 1.2943 | 83179.3333 | 17.8481 | 83179.3315
38958.5935 | 3 | 0 | 38958.5935 | 2179 | 0 |  | 1735.5 | 1853.5 | 0.18315 | 0 | 133.0281 | 0 | 0.0018315 | 0 | 1.3303 | 0 | 0.0018315 | 1.3303 | 83179.3333 | 14.6572 | 83179.3315
38958.594 | 3 | 0 | 38958.594 | 2455 | 0 |  | 1777.5 | 1895.5 | 0.18315 | 0 | 149.8779 | 0 | 0.0018315 | 0 | 1.4988 | 0 | 0.0018315 | 1.4988 | 83179.3333 | 1.767 | 83179.3315
38958.5945 | 2 | 0 | 38958.5945 | 1942 | 0 |  | 1819.5 | 1937.5 | 0.1221 | 0 | 118.5592 | 0 | 0.001221 | 0 | 1.1856 | 0 | 0.001221 | 1.1856 | 124819 | 28.6498 | 124818.9988
38958.595 | 3 | 0 | 38958.595 | 1954 | 0 |  | 1861.5 | 1979.5 | 0.18315 | 0 | 119.2918 | 0 | 0.0018315 | 0 | 1.1929 | 0 | 0.0018315 | 1.1929 | 83179.3333 | 27.8598 | 83179.3315
38958.5955 | 3 | 1 | 38958.5955 | 1994 | 0 |  | 1903.5 | 2021.5 | 0.18315 | 0.06105 | 121.7338 | 0 | 0.0018315 | 0.0006105 | 1.2173 | 0 | 0.001221 | 1.2173 | 127747.53 | 2144.4728 | 238324.5661
38958.5959 | 2 | 0 | 38958.596 | 1996 | 0 |  | 1945.5 | 2063.5 | 0.1221 | 0 | 121.8559 | 0 | 0.001221 | 0 | 1.2186 | 0 | 0.001221 | 1.2186 | 124819 | 25.1693 | 124818.9988
38958.5964 | 3 | 0 | 38958.5964 | 2016 | 0 |  | 1987.5 | 2105.5 | 0.18315 | 0 | 123.0769 | 0 | 0.0018315 | 0 | 1.2308 | 0 | 0.0018315 | 1.2308 | 83179.3333 | 23.9276 | 83179.3315
38958.5969 | 2 | 1 | 38958.5969 | 2188 | 0 |  | 2029.5 | 2147.5 | 0.1221 | 0.06105 | 133.5775 | 0 | 0.001221 | 0.0006105 | 1.3358 | 0 | 0.0006105 | 1.3358 | 41266.413 | 19.8042 | 41249.8825
38958.5974 | 2 | 0 | 38958.5974 | 1995 | 0 |  | 2071.5 | 2189.5 | 0.1221 | 0 | 121.7949 | 0 | 0.001221 | 0 | 1.2179 | 0 | 0.001221 | 1.2179 | 124819 | 25.2321 | 124818.9988
38958.5979 | 2 | 0 | 38958.5979 | 1990 | 1 |  | 2113.5 | 2231.5 | 0.1221 | 0 | 121.4896 | 0.06105 | 0.001221 | 0 | 1.2149 | 0.0006105 | 0.001221 | 1.2143 | 124819 | 25.6099 | 124818.9988
38958.5984 | 3 | 1 | 38958.5984 | 2290 | 0 |  | 2155.5 | 2273.5 | 0.18315 | 0.06105 | 139.8046 | 0 | 0.0018315 | 0.0006105 | 1.398 | 0 | 0.001221 | 1.398 | 27758.7113 | 14.3071 | 31220.5774
38958.5989 | 2 | 0 | 38958.5989 | 2482 | 0 |  | 2197.5 | 2315.5 | 0.1221 | 0 | 151.5263 | 0 | 0.001221 | 0 | 1.5153 | 0 | 0.001221 | 1.5153 | 124819 | 0.65995 | 124818.9988
38958.5994 | 2 | 1 | 38958.5994 | 2231 | 0 |  | 2239.5 | 2357.5 | 0.1221 | 0.06105 | 136.2027 | 0 | 0.001221 | 0.0006105 | 1.362 | 0 | 0.0006105 | 1.362 | 33992.4265 | 15.7631 | 33978.8098
38958.5998 | 2 | 1 | 38958.5998 | 2016 | 0 |  | 2281.5 | 2399.5 | 0.1221 | 0.06105 | 123.0769 | 0 | 0.001221 | 0.0006105 | 1.2308 | 0 | 0.0006105 | 1.2308 | 78520.3495 | 45.8868 | 78488.8958
38958.6003 | 2 | 0 | 38958.6003 | 2115 | 0 |  | 2323.5 | 2441.5 | 0.1221 | 0 | 129.1209 | 0 | 0.001221 | 0 | 1.2912 | 0 | 0.001221 | 1.2912 | 124819 | 18.1267 | 124818.9988
38958.6008 | 3 | 0 | 38958.6008 | 2286 | 0 |  | 2365.5 | 2483.5 | 0.18315 | 0 | 139.5604 | 0 | 0.0018315 | 0 | 1.3956 | 0 | 0.0018315 | 1.3956 | 83179.3333 | 9.2905 | 83179.3315
38958.6013 | 2 | 0 | 38958.6013 | 2365 | 0 |  | 2407.5 | 2525.5 | 0.1221 | 0 | 144.3834 | 0 | 0.001221 | 0 | 1.4438 | 0 | 0.001221 | 1.4438 | 124819 | 5.6397 | 124818.9988
38958.6018 | 2 | 0 | 38958.6018 | 2294 | 0 |  | 2449.5 | 2567.5 | 0.1221 | 0 | 140.0488 | 0 | 0.001221 | 0 | 1.4005 | 0 | 0.001221 | 1.4005 | 124819 | 8.9093 | 124818.9988
38958.6023 | 2 | 0 | 38958.6023 | 2104 | 0 |  | 2491.5 | 2609.5 | 0.1221 | 0 | 128.4493 | 0 | 0.001221 | 0 | 1.2845 | 0 | 0.001221 | 1.2845 | 124819 | 18.7443 | 124818.9988

## A1-B3
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 154.1136 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38958.5721 | 1 | 0 | 38958.5721 | 1 | 0 |  | -115 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5726 | 1 | 0 | 38958.5726 | 1 | 0 |  | -73 | 45 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5731 | 1 | 0 | 38958.5731 | 1 | 0 |  | -31 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5736 | 1 | 0 | 38958.5736 | 1 | 0 |  | 11 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.574 | 1 | 0 | 38958.5741 | 1 | 0 |  | 53 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5745 | 1 | 0 | 38958.5745 | 1 | 0 |  | 95 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.575 | 1 | 0 | 38958.575 | 1 | 0 |  | 137 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5755 | 1 | 0 | 38958.5755 | 1 | 0 |  | 179 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.576 | 1 | 0 | 38958.576 | 1 | 0 |  | 221 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5765 | 1 | 0 | 38958.5765 | 1 | 0 |  | 263 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.577 | 1 | 0 | 38958.577 | 1 | 0 |  | 305 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5774 | 1 | 0 | 38958.5775 | 1 | 0 |  | 347 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5779 | 1 | 0 | 38958.578 | 1 | 0 |  | 389 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5784 | 1 | 0 | 38958.5784 | 1 | 0 |  | 431 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5789 | 1 | 0 | 38958.5789 | 1 | 0 |  | 473 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5794 | 1 | 0 | 38958.5794 | 1 | 0 |  | 515 | 633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5799 | 1 | 0 | 38958.5799 | 1 | 0 |  | 557 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5804 | 1 | 0 | 38958.5804 | 1 | 0 |  | 598.5 | 716.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5808 | 1 | 0 | 38958.5809 | 1 | 0 |  | 641 | 759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5813 | 1 | 0 | 38958.5814 | 1 | 0 |  | 683 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5818 | 1 | 0 | 38958.5818 | 1 | 0 |  | 725 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5823 | 1 | 0 | 38958.5823 | 1 | 0 |  | 766.5 | 884.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5828 | 1 | 0 | 38958.5828 | 1 | 0 |  | 809 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5833 | 1 | 0 | 38958.5833 | 1 | 0 |  | 851 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5838 | 1 | 0 | 38958.5838 | 1 | 0 |  | 893 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5842 | 1 | 0 | 38958.5843 | 1 | 0 |  | 934.5 | 1052.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5847 | 1 | 0 | 38958.5847 | 1 | 0 |  | 976.5 | 1094.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5852 | 1 | 0 | 38958.5852 | 1 | 0 |  | 1018.5 | 1136.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5857 | 1 | 0 | 38958.5857 | 1 | 0 |  | 1061 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5862 | 1 | 0 | 38958.5862 | 1 | 0 |  | 1102.5 | 1220.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5867 | 1 | 0 | 38958.5867 | 1 | 0 |  | 1144.5 | 1262.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5872 | 1 | 0 | 38958.5872 | 1 | 0 |  | 1186.5 | 1304.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5877 | 1 | 0 | 38958.5877 | 1 | 0 |  | 1228.5 | 1346.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5881 | 1 | 0 | 38958.5881 | 1 | 0 |  | 1270.5 | 1388.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5886 | 1 | 0 | 38958.5886 | 1 | 0 |  | 1312.5 | 1430.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5891 | 1 | 0 | 38958.5891 | 1 | 0 |  | 1354.5 | 1472.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5896 | 1 | 0 | 38958.5896 | 1 | 0 |  | 1396.5 | 1514.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5901 | 1 | 0 | 38958.5901 | 1 | 0 |  | 1438.5 | 1556.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5906 | 1 | 0 | 38958.5906 | 1 | 0 |  | 1480.5 | 1598.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5911 | 1 | 0 | 38958.5911 | 1 | 0 |  | 1522.5 | 1640.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.5915 | 1 | 0 | 38958.5916 | 1 | 0 |  | 1564.5 | 1682.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38958.592 | 2 | 0 | 38958.592 | 1888 | 0 |  | 1606.5 | 1724.5 | 0.1221 | 0 | 115.2625 | 0 | 0.001221 | 0 | 1.1526 | 0 | 0.001221 | 1.1526 | 126119 | 33.7066 | 126118.9988
38958.5925 | 2 | 0 | 38958.5925 | 2166 | 0 |  | 1648.5 | 1766.5 | 0.1221 | 0 | 132.2344 | 0 | 0.001221 | 0 | 1.3223 | 0 | 0.001221 | 1.3223 | 126119 | 16.5457 | 126118.9988
38958.593 | 2 | 0 | 38958.593 | 2079 | 0 |  | 1690.5 | 1808.5 | 0.1221 | 0 | 126.9231 | 0 | 0.001221 | 0 | 1.2692 | 0 | 0.001221 | 1.2692 | 126119 | 21.4228 | 126118.9988
38958.5935 | 2 | 2 | 38958.5935 | 2168 | 1 |  | 1732.5 | 1850.5 | 0.1221 | 0.1221 | 132.3565 | 0.06105 | 0.001221 | 0.001221 | 1.3236 | 0.0006105 | 0 | 1.323 | 20741.2041 | 16.4457 | 17797.7813
38958.594 | 2 | 2 | 38958.594 | 1969 | 1 |  | 1774.5 | 1892.5 | 0.1221 | 0.1221 | 120.2076 | 0.06105 | 0.001221 | 0.001221 | 1.2021 | 0.0006105 | 0 | 1.2015 | 35591.3975 | 28.2205 | 27735.9551
38958.5945 | 2 | 2 | 38958.5945 | 2176 | 1 |  | 1816.5 | 1934.5 | 0.1221 | 0.1221 | 132.8449 | 0.06105 | 0.001221 | 0.001221 | 1.3284 | 0.0006105 | 0 | 1.3278 | 20201.0286 | 16.0174 | 17398.2567
38958.5949 | 2 | 2 | 38958.595 | 2036 | 1 |  | 1858.5 | 1976.5 | 0.1221 | 0.1221 | 124.2979 | 0.06105 | 0.001221 | 0.001221 | 1.243 | 0.0006105 | 0 | 1.2424 | 30267.2714 | 23.999 | 24389.9368
38958.5954 | 2 | 2 | 38958.5954 | 2497 | 1 |  | 1900.5 | 2018.5 | 0.1221 | 0.1221 | 152.442 | 0.06105 | 0.001221 | 0.001221 | 1.5244 | 0.0006105 | 0 | 1.5238 | 1383.4288 | 1.0969 | 1367.3333
38958.5959 | 2 | 1 | 38958.5959 | 2290 | 1 |  | 1942.5 | 2060.5 | 0.1221 | 0.06105 | 139.8046 | 0.06105 | 0.001221 | 0.0006105 | 1.398 | 0.0006105 | 0.0006105 | 1.3974 | 28773.9059 | 12.8763 | 28762.4984
38958.5964 | 2 | 1 | 38958.5964 | 1987 | 1 |  | 1984.5 | 2102.5 | 0.1221 | 0.06105 | 121.3065 | 0.06105 | 0.001221 | 0.0006105 | 1.2131 | 0.0006105 | 0.0006105 | 1.2125 | 93570.1264 | 58.9723 | 93533.0304
38958.5969 | 2 | 2 | 38958.5969 | 2289 | 1 |  | 2026.5 | 2144.5 | 0.1221 | 0.1221 | 139.7436 | 0.06105 | 0.001221 | 0.001221 | 1.3974 | 0.0006105 | 0 | 1.3968 | 12974.5587 | 10.2876 | 11754.9721
38958.5974 | 2 | 2 | 38958.5974 | 2348 | 1 |  | 2068.5 | 2186.5 | 0.1221 | 0.1221 | 143.3455 | 0.06105 | 0.001221 | 0.001221 | 1.4335 | 0.0006105 | 0 | 1.4328 | 9477.9588 | 7.5151 | 8808.4784
38958.5979 | 2 | 2 | 38958.5979 | 2306 | 1 |  | 2110.5 | 2228.5 | 0.1221 | 0.1221 | 140.7814 | 0.06105 | 0.001221 | 0.001221 | 1.4078 | 0.0006105 | 0 | 1.4072 | 11948.706 | 9.4742 | 10905.9824
38958.5983 | 2 | 2 | 38958.5984 | 2229 | 1 |  | 2152.5 | 2270.5 | 0.1221 | 0.1221 | 136.0806 | 0.06105 | 0.001221 | 0.001221 | 1.3608 | 0.0006105 | 0 | 1.3602 | 16720.3457 | 13.2576 | 14751.4064
38958.5988 | 2 | 2 | 38958.5988 | 2001 | 1 |  | 2194.5 | 2312.5 | 0.1221 | 0.1221 | 122.1612 | 0.06105 | 0.001221 | 0.001221 | 1.2216 | 0.0006105 | 0 | 1.221 | 33004.0311 | 26.169 | 26137.8568
38958.5993 | 2 | 2 | 38958.5993 | 2132 | 1 |  | 2236.5 | 2354.5 | 0.1221 | 0.1221 | 130.1587 | 0.06105 | 0.001221 | 0.001221 | 1.3016 | 0.0006105 | 0 | 1.301 | 23222.1836 | 18.4129 | 19595.6419
38958.5998 | 2 | 2 | 38958.5998 | 2480 | 1 |  | 2278.5 | 2396.5 | 0.1221 | 0.1221 | 151.4042 | 0.06105 | 0.001221 | 0.001221 | 1.514 | 0.0006105 | 0 | 1.5134 | 2257.7899 | 1.7902 | 2216.323
38958.6003 | 2 | 1 | 38958.6003 | 2499 | 1 |  | 2320.5 | 2438.5 | 0.1221 | 0.06105 | 152.5641 | 0.06105 | 0.001221 | 0.0006105 | 1.5256 | 0.0006105 | 0.0006105 | 1.525 | 2589.0353 | 1.0371 | 2588.0089
38958.6008 | 2 | 1 | 38958.6008 | 2278 | 1 |  | 2362.5 | 2480.5 | 0.1221 | 0.06105 | 139.072 | 0.06105 | 0.001221 | 0.0006105 | 1.3907 | 0.0006105 | 0.0006105 | 1.3901 | 30604.5929 | 13.8087 | 30592.4597
38958.6013 | 2 | 1 | 38958.6013 | 2508 | 1 |  | 2404.5 | 2522.5 | 0.1221 | 0.06105 | 153.1136 | 0.06105 | 0.001221 | 0.0006105 | 1.5311 | 0.0006105 | 0.0006105 | 1.5305 | 1658.8474 | 0.66201 | 1658.1897
38958.6017 | 3 | 1 | 38958.6018 | 2002 | 1 |  | 2446.5 | 2564.5 | 0.18315 | 0.06105 | 122.2222 | 0.06105 | 0.0018315 | 0.0006105 | 1.2222 | 0.0006105 | 0.001221 | 1.2216 | 137739.2166 | 590.1314 | 215517.7065
38958.6022 | 2 | 1 | 38958.6022 | 2112 | 1 |  | 2488.5 | 2606.5 | 0.1221 | 0.06105 | 128.9377 | 0.06105 | 0.001221 | 0.0006105 | 1.2894 | 0.0006105 | 0.0006105 | 1.2888 | 61236.6547 | 32.0608 | 61212.3774

## A1-A2
Penlight Test 36 |  |  | 2006-08-29 | 13:45 |  |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38958.5721 | 1 | 0 | 38958.5721 | 1 | 0 |  | -117.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5725 | 1 | 0 | 38958.5726 | 2 | 0 |  | -76 | 42 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38958.573 | 1 | 0 | 38958.5731 | 1 | 0 |  | -34 | 84 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5735 | 1 | 0 | 38958.5735 | 1 | 0 |  | 8 | 126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.574 | 1 | 0 | 38958.574 | 1 | 0 |  | 50 | 168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5745 | 1 | 0 | 38958.5745 | 1 | 0 |  | 92 | 210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.575 | 1 | 0 | 38958.575 | 1 | 0 |  | 134 | 252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5755 | 1 | 0 | 38958.5755 | 1 | 0 |  | 176 | 294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5759 | 1 | 0 | 38958.576 | 1 | 0 |  | 218 | 336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38958.5765 | 1 | 0 |  | 261 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5769 | 1 | 0 | 38958.5769 | 1 | 0 |  | 302 | 420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5774 | 1 | 0 | 38958.5774 | 1 | 0 |  | 344 | 462 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5779 | 1 | 0 | 38958.5779 | 1 | 0 |  | 386 | 504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5784 | 1 | 0 | 38958.5784 | 1 | 0 |  | 428 | 546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5789 | 1 | 0 | 38958.5789 | 1 | 0 |  | 470 | 588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5794 | 1 | 0 | 38958.5794 | 1 | 0 |  | 512 | 630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5798 | 1 | 0 | 38958.5799 | 1 | 0 |  | 554 | 672 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5803 | 1 | 0 | 38958.5803 | 1 | 0 |  | 596 | 714 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5808 | 1 | 0 | 38958.5808 | 1 | 0 |  | 638 | 756 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5813 | 1 | 0 | 38958.5813 | 1 | 0 |  | 680 | 798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5818 | 1 | 0 | 38958.5818 | 1 | 0 |  | 722 | 840 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5823 | 1 | 0 | 38958.5823 | 1 | 0 |  | 764 | 882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5828 | 1 | 0 | 38958.5828 | 1 | 0 |  | 806 | 924 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5832 | 1 | 0 | 38958.5833 | 1 | 0 |  | 848 | 966 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5837 | 1 | 0 | 38958.5837 | 1 | 0 |  | 890 | 1008 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5842 | 1 | 0 | 38958.5842 | 1 | 0 |  | 932 | 1050 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5847 | 1 | 0 | 38958.5847 | 1 | 0 |  | 974 | 1092 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5852 | 1 | 0 | 38958.5852 | 1 | 0 |  | 1016 | 1134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5857 | 1 | 0 | 38958.5857 | 1 | 0 |  | 1058 | 1176 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5862 | 1 | 0 | 38958.5862 | 1 | 0 |  | 1100 | 1218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5866 | 1 | 0 | 38958.5867 | 1 | 0 |  | 1142 | 1260 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5871 | 1 | 0 | 38958.5872 | 1 | 0 |  | 1184 | 1302 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5876 | 1 | 0 | 38958.5876 | 1 | 0 |  | 1226 | 1344 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5881 | 1 | 0 | 38958.5881 | 1 | 0 |  | 1268 | 1386 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5886 | 1 | 0 | 38958.5886 | 1 | 0 |  | 1310 | 1428 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5891 | 1 | 0 | 38958.5891 | 1 | 0 |  | 1352 | 1470 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5896 | 1 | 0 | 38958.5896 | 1 | 0 |  | 1394 | 1512 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.59 | 1 | 0 | 38958.5901 | 1 | 0 |  | 1436 | 1554 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.5905 | 1 | 0 | 38958.5906 | 1 | 0 |  | 1478 | 1596 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38958.591 | 2 | 1 | 38958.591 | 1 | 0 |  | 1520 | 1638 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38958.5915 | 3 | 2 | 38958.5915 | 2 | 1 |  | 1562 | 1680 | 0.18315 | 0.1221 | 0.1221 | 0.06105 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 105351.1183
38958.592 | 4 | 1 | 38958.592 | 4 | 1 |  | 1604 | 1722 | 0.2442 | 0.06105 | 0.2442 | 0.06105 | 0.002442 | 0.0006105 | 0.002442 | 0.0006105 | 0.0018315 | 0.0018315 | 70334 | 70334 | 210502.7099
38958.5925 | 5 | 2 | 38958.5925 | 5 | 2 |  | 1646 | 1764 | 0.30525 | 0.1221 | 0.30525 | 0.1221 | 0.0030525 | 0.001221 | 0.0030525 | 0.001221 | 0.0018315 | 0.0018315 | 70334 | 70334 | 105151.4969
38958.593 | 49 | 46 | 38958.593 | 51 | 55 |  | 1688 | 1806 | 2.9915 | 2.8083 | 3.1136 | 3.3578 | 0.029915 | 0.028083 | 0.031136 | 0.033578 | 0.0018315 | 0.002442 | 70867.6774 | 52570.4915 | 4378.6709
38958.5934 | 979 | 952 | 38958.5935 | 1096 | 1166 |  | 1730 | 1848 | 59.768 | 58.1197 | 66.9109 | 71.1844 | 0.59768 | 0.5812 | 0.66911 | 0.71184 | 0.016484 | 0.042735 | 110.4862 | 95.2581 | 9.3277
38958.5939 | 1177 | 1148 | 38958.594 | 949 | 923 |  | 1772 | 1890 | 71.8559 | 70.0855 | 57.9365 | 56.3492 | 0.71856 | 0.70085 | 0.57937 | 0.56349 | 0.017705 | 0.015873 | 766.0583 | 1231.9377 | 17.0788
38958.5944 | 1025 | 997 | 38958.5944 | 963 | 1076 |  | 1814 | 1932 | 62.5763 | 60.8669 | 58.7912 | 65.6899 | 0.62576 | 0.60867 | 0.58791 | 0.6569 | 0.017094 | 0.068987 | 221.8143 | 215.5632 | 6.2363
38958.5949 | 1129 | 1097 | 38958.5949 | 1017 | 1057 |  | 1856 | 1974 | 68.9255 | 66.9719 | 62.0879 | 64.5299 | 0.68926 | 0.66972 | 0.62088 | 0.6453 | 0.019536 | 0.02442 | 919.951 | 1463.3615 | 9.6402
38958.5954 | 971 | 941 | 38958.5954 | 1074 | 1046 |  | 1898 | 2016 | 59.2796 | 57.4481 | 65.5678 | 63.8584 | 0.5928 | 0.57448 | 0.65568 | 0.63858 | 0.018315 | 0.017094 | 4194.7418 | 33910.3561 | 21.2996
38958.5959 | 942 | 972 | 38958.5959 | 1012 | 982 |  | 1940 | 2058 | 57.5092 | 59.3407 | 61.7827 | 59.9512 | 0.57509 | 0.59341 | 0.61783 | 0.59951 | 0.018315 | 0.018315 | 8650.1431 | 5904.3565 | 20.1343
38958.5964 | 1060 | 1030 | 38958.5964 | 962 | 996 |  | 1982 | 2100 | 64.7131 | 62.8816 | 58.7302 | 60.8059 | 0.64713 | 0.62882 | 0.5873 | 0.60806 | 0.018315 | 0.020757 | 38039.8611 | 3782.3429 | 2.1774
38958.5969 | 1035 | 1003 | 38958.5969 | 969 | 939 |  | 2024 | 2142 | 63.1868 | 61.2332 | 59.1575 | 57.326 | 0.63187 | 0.61233 | 0.59158 | 0.57326 | 0.019536 | 0.018315 | 4471.1695 | 12713.0524 | 7.4212
38958.5973 | 943 | 941 | 38958.5974 | 1155 | 1124 |  | 2066 | 2184 | 57.5702 | 57.4481 | 70.5128 | 68.6203 | 0.5757 | 0.57448 | 0.70513 | 0.6862 | 0.001221 | 0.018926 | 231.9525 | 187.2927 | 15.8665
38958.5978 | 938 | 1022 | 38958.5978 | 956 | 988 |  | 2108 | 2226 | 57.265 | 62.3932 | 58.3639 | 60.3175 | 0.57265 | 0.62393 | 0.58364 | 0.60317 | 0.051282 | 0.019536 | 542.4237 | 770.5996 | 13.2528
38958.5983 | 967 | 998 | 38958.5983 | 1050 | 944 |  | 2150 | 2268 | 59.0354 | 60.928 | 64.1026 | 57.6313 | 0.59035 | 0.60928 | 0.64103 | 0.57631 | 0.018926 | 0.064713 | 379.1207 | 367.8805 | 11.6617
38958.5988 | 1121 | 1088 | 38958.5988 | 977 | 946 |  | 2191.5 | 2309.5 | 68.4371 | 66.4225 | 59.6459 | 57.7534 | 0.68437 | 0.66422 | 0.59646 | 0.57753 | 0.020147 | 0.018926 | 2598.1227 | 20995.0063 | 8.7799
38958.5993 | 1190 | 1159 | 38958.5993 | 1137 | 1181 |  | 2233.5 | 2351.5 | 72.6496 | 70.757 | 69.4139 | 72.1001 | 0.7265 | 0.70757 | 0.69414 | 0.721 | 0.018926 | 0.026862 | 2256.0608 | 11691.8303 | 20.188
38958.5998 | 1183 | 1150 | 38958.5998 | 1028 | 995 |  | 2275.5 | 2393.5 | 72.2222 | 70.2076 | 62.7595 | 60.7448 | 0.72222 | 0.70208 | 0.62759 | 0.60745 | 0.020147 | 0.020147 | 6303.0909 | 6303.0909 | 18.83
38958.6003 | 982 | 1013 | 38958.6003 | 1110 | 1077 |  | 2318 | 2436 | 59.9512 | 61.8437 | 67.7656 | 65.7509 | 0.59951 | 0.61844 | 0.67766 | 0.65751 | 0.018926 | 0.020147 | 1859.8549 | 3397.9298 | 11.3175
38958.6007 | 1197 | 1198 | 38958.6008 | 1091 | 1133 |  | 2360 | 2478 | 73.0769 | 73.138 | 66.6056 | 69.1697 | 0.73077 | 0.73138 | 0.66606 | 0.6917 | 0.0006105 | 0.025641 | 854.3502 | 1127.8657 | 21.6206
38958.6012 | 1098 | 1064 | 38958.6012 | 956 | 924 |  | 2401.5 | 2519.5 | 67.033 | 64.9573 | 58.3639 | 56.4103 | 0.67033 | 0.64957 | 0.58364 | 0.5641 | 0.020757 | 0.019536 | 3615.0824 | 17964.9873 | 4.5779
38958.6017 | 1058 | 1026 | 38958.6017 | 986 | 954 |  | 2444 | 2562 | 64.591 | 62.6374 | 60.1954 | 58.2418 | 0.64591 | 0.62637 | 0.60195 | 0.58242 | 0.019536 | 0.019536 | 6503.1875 | 6503.1875 | 2.7856
38958.6022 | 1089 | 1055 | 38958.6022 | 1126 | 1095 |  | 2485.5 | 2603.5 | 66.4835 | 64.4078 | 68.7424 | 66.8498 | 0.66484 | 0.64408 | 0.68742 | 0.6685 | 0.020757 | 0.018926 | 16926.34 | 3774.5787 | 2.8607

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -118 | 20.8 | 30.3 | 23.1 | 30 | 33.6 | 30.1 | 28.1 | 32.3 | 26.6 | 26.1
1 | -117 | 20.8 | 30.3 | 23.1 | 30 | 33.6 | 30.1 | 28.1 | 32.3 | 26.6 | 26.1
2 | -116 | 20.8 | 30.3 | 23.1 | 30 | 33.5 | 30.1 | 28.1 | 32.3 | 26.6 | 26.1
3 | -115 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.2 | 32.3 | 26.6 | 26.1
4 | -114 | 20.8 | 30.2 | 23.2 | 30 | 33.4 | 30 | 28.2 | 32.3 | 26.6 | 26.1
5 | -113 | 20.8 | 30.2 | 23.2 | 30 | 33.4 | 30 | 28.2 | 32.3 | 26.6 | 26.1
6 | -112 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.2 | 32.3 | 26.6 | 26.1
7 | -111 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.2 | 32.4 | 26.6 | 26.1
8 | -110 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.2 | 32.4 | 26.6 | 26.1
9 | -109 | 20.8 | 30.2 | 23.2 | 30 | 33.3 | 30 | 28.2 | 32.4 | 26.6 | 26.1
10 | -108 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.1 | 32.4 | 26.6 | 26.1
11 | -107 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.2 | 32.4 | 26.6 | 26.1
12 | -106 | 20.8 | 30.2 | 23.2 | 30 | 33.4 | 30 | 28.2 | 32.4 | 26.6 | 26.1
13 | -105 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.2 | 32.4 | 26.6 | 26.1
14 | -104 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.1 | 32.4 | 26.6 | 26.1
15 | -103 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.2 | 32.4 | 26.6 | 26.1
16 | -102 | 20.7 | 30.2 | 23.1 | 30 | 33.3 | 30 | 28.2 | 32.4 | 26.6 | 26.1
17 | -101 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.1 | 32.4 | 26.6 | 26.1
18 | -100 | 20.8 | 30.2 | 23.1 | 30 | 33.4 | 30 | 28.1 | 32.4 | 26.6 | 26.1
19 | -99 | 20.8 | 29.8 | 23.8 | 29.8 | 32.5 | 29.8 | 28.2 | 32.4 | 26.6 | 26.1
20 | -98 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.3 | 32.3 | 26.6 | 26.1
21 | -97 | 20.8 | 29.7 | 24 | 29.7 | 32.5 | 29.7 | 28.3 | 32.4 | 26.6 | 26.1
22 | -96 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.3 | 32.4 | 26.6 | 26.1
23 | -95 | 20.8 | 29.7 | 24 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
24 | -94 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
25 | -93 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
26 | -92 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
27 | -91 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.3 | 32.4 | 26.6 | 26.1
28 | -90 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
29 | -89 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
30 | -88 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
31 | -87 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
32 | -86 | 20.8 | 29.7 | 24 | 29.7 | 32.5 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
33 | -85 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
34 | -84 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
35 | -83 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
36 | -82 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
37 | -81 | 20.8 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
38 | -80 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
39 | -79 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
40 | -78 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
41 | -77 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
42 | -76 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
43 | -75 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
44 | -74 | 20.7 | 29.7 | 24 | 29.7 | 32.3 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
45 | -73 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
46 | -72 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
47 | -71 | 20.8 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.6 | 26.6 | 26.1
48 | -70 | 20.7 | 29.7 | 24 | 29.7 | 32.3 | 29.7 | 28.2 | 32.6 | 26.6 | 26.1
49 | -69 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
50 | -68 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
51 | -67 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
52 | -66 | 20.8 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
53 | -65 | 20.7 | 29.7 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
54 | -64 | 20.8 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
55 | -63 | 20.8 | 29.6 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
56 | -62 | 20.8 | 29.6 | 24 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
57 | -61 | 20.8 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
58 | -60 | 20.7 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
59 | -59 | 20.8 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
60 | -58 | 20.8 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
61 | -57 | 20.7 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
62 | -56 | 20.7 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
63 | -55 | 20.7 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.6 | 26.6 | 26.1
64 | -54 | 20.8 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
65 | -53 | 20.8 | 29.6 | 24 | 29.6 | 32.3 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
66 | -52 | 20.8 | 29.6 | 24 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
67 | -51 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
68 | -50 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
69 | -49 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
70 | -48 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
71 | -47 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
72 | -46 | 20.8 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
73 | -45 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
74 | -44 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
75 | -43 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
76 | -42 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
77 | -41 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
78 | -40 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
79 | -39 | 20.7 | 29.7 | 23.8 | 29.7 | 32.3 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
80 | -38 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
81 | -37 | 20.8 | 29.7 | 23.9 | 29.6 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
82 | -36 | 20.8 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
83 | -35 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
84 | -34 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
85 | -33 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
86 | -32 | 20.7 | 29.6 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
87 | -31 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
88 | -30 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
89 | -29 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
90 | -28 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
91 | -27 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
92 | -26 | 20.7 | 29.6 | 23.9 | 29.6 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
93 | -25 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
94 | -24 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
95 | -23 | 20.7 | 29.7 | 23.9 | 29.7 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
96 | -22 | 20.7 | 29.6 | 23.9 | 29.6 | 32.4 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
97 | -21 | 20.7 | 29.6 | 23.9 | 29.6 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
98 | -20 | 20.7 | 29.6 | 23.9 | 29.6 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
99 | -19 | 20.7 | 29.6 | 23.9 | 29.6 | 32.3 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
100 | -18 | 20.7 | 29.6 | 23.9 | 29.6 | 32.2 | 29.6 | 28.2 | 32.5 | 26.6 | 26.1
101 | -17 | 20.7 | 29.6 | 23.9 | 29.6 | 32.4 | 29.7 | 28.2 | 32.5 | 26.6 | 26.1
102 | -16 | 20.7 | 29.6 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
103 | -15 | 20.7 | 29.7 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
104 | -14 | 20.7 | 29.6 | 23.9 | 29.6 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
105 | -13 | 20.7 | 29.6 | 23.9 | 29.6 | 32.2 | 29.6 | 28.2 | 32.4 | 26.6 | 26.1
106 | -12 | 20.7 | 29.6 | 23.9 | 29.6 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
107 | -11 | 20.7 | 29.7 | 23.8 | 29.7 | 32.2 | 29.6 | 28.2 | 32.4 | 26.6 | 26.1
108 | -10 | 20.7 | 29.6 | 23.9 | 29.6 | 32.4 | 29.7 | 28.2 | 32.3 | 26.6 | 26.1
109 | -9 | 20.7 | 29.7 | 23.8 | 29.7 | 32.1 | 29.6 | 28.2 | 32.4 | 26.6 | 26.1
110 | -8 | 20.7 | 29.6 | 23.9 | 29.6 | 32.2 | 29.6 | 28.2 | 32.4 | 26.6 | 26.1
111 | -7 | 20.7 | 29.6 | 23.9 | 29.6 | 32.2 | 29.6 | 28.2 | 32.4 | 26.6 | 26.1
112 | -6 | 20.7 | 29.6 | 23.9 | 29.7 | 32.3 | 29.7 | 28.2 | 32.4 | 26.6 | 26.1
113 | -5 | 20.7 | 29.6 | 23.9 | 29.6 | 32.3 | 29.6 | 28.2 | 32.4 | 26.6 | 26.1
114 | -4 | 20.7 | 29.8 | 23.6 | 29.7 | 32.5 | 29.8 | 28.1 | 32.4 | 26.6 | 26.1
115 | -3 | 20.7 | 30.7 | 21.8 | 30.3 | 34.1 | 30.4 | 28 | 32.3 | 26.5 | 26
116 | -2 | 20.7 | 31 | 21.3 | 30.5 | 34.6 | 30.6 | 27.9 | 32.3 | 26.5 | 26
117 | -1 | 20.9 | 31 | 21.3 | 30.5 | 34.6 | 30.5 | 27.9 | 32.3 | 26.5 | 26
118 | 0 | 21.6 | 31 | 21.2 | 30.5 | 34.5 | 30.5 | 27.9 | 32.3 | 26.5 | 26
119 | 1 | 22.8 | 31.1 | 21.2 | 30.5 | 34.7 | 30.6 | 27.9 | 32.3 | 26.5 | 26
120 | 2 | 24.6 | 30.9 | 21.4 | 30.5 | 34.4 | 30.5 | 27.9 | 32.4 | 26.5 | 26
121 | 3 | 26.8 | 31 | 21.3 | 30.5 | 34.6 | 30.5 | 27.9 | 32.3 | 26.4 | 26
122 | 4 | 29.5 | 31.1 | 21.3 | 30.5 | 34.6 | 30.6 | 27.9 | 32.4 | 26.5 | 26
123 | 5 | 32.5 | 31.1 | 21.3 | 30.6 | 34.7 | 30.6 | 27.9 | 32.4 | 26.5 | 26
124 | 6 | 35.9 | 31.1 | 21.3 | 30.6 | 34.6 | 30.5 | 27.9 | 32.4 | 26.5 | 26
125 | 7 | 39.5 | 31.1 | 21.4 | 30.6 | 34.6 | 30.6 | 27.9 | 32.4 | 26.5 | 26
126 | 8 | 43.3 | 31.1 | 21.4 | 30.6 | 34.7 | 30.6 | 27.9 | 32.4 | 26.5 | 26
127 | 9 | 47.4 | 31.1 | 21.5 | 30.6 | 34.6 | 30.6 | 27.9 | 32.4 | 26.5 | 26
128 | 10 | 51.6 | 31.2 | 21.6 | 30.6 | 34.6 | 30.5 | 27.9 | 32.4 | 26.5 | 26
129 | 11 | 56.1 | 31.2 | 21.6 | 30.7 | 34.6 | 30.5 | 27.9 | 32.4 | 26.5 | 26
130 | 12 | 60.7 | 31.3 | 21.7 | 30.7 | 34.7 | 30.6 | 27.9 | 32.5 | 26.5 | 26
131 | 13 | 65.5 | 31.3 | 21.8 | 30.7 | 34.5 | 30.5 | 27.9 | 32.5 | 26.5 | 26
132 | 14 | 70.4 | 31.4 | 21.8 | 30.8 | 34.6 | 30.6 | 27.9 | 32.5 | 26.5 | 26
133 | 15 | 75.4 | 31.4 | 21.9 | 30.8 | 34.6 | 30.6 | 27.9 | 32.5 | 26.5 | 26
134 | 16 | 80.6 | 31.5 | 22.1 | 30.9 | 34.7 | 30.6 | 27.9 | 32.5 | 26.5 | 26
135 | 17 | 85.9 | 31.5 | 22.3 | 30.9 | 34.5 | 30.5 | 27.9 | 32.5 | 26.5 | 26
136 | 18 | 91.3 | 31.6 | 22.4 | 31 | 34.6 | 30.6 | 27.9 | 32.5 | 26.5 | 26
137 | 19 | 96.8 | 31.6 | 22.6 | 31.1 | 34.6 | 30.6 | 27.9 | 32.6 | 26.5 | 26
138 | 20 | 102.4 | 31.7 | 22.7 | 31.2 | 34.6 | 30.5 | 27.9 | 32.5 | 26.5 | 26
139 | 21 | 108.1 | 31.8 | 22.8 | 31.2 | 34.6 | 30.5 | 27.9 | 32.6 | 26.5 | 26
140 | 22 | 113.8 | 31.9 | 23 | 31.3 | 34.6 | 30.5 | 27.9 | 32.6 | 26.5 | 26
141 | 23 | 119.6 | 32 | 23.4 | 31.4 | 34.6 | 30.6 | 27.9 | 32.6 | 26.5 | 26
142 | 24 | 125.5 | 32.2 | 23.6 | 31.5 | 34.5 | 30.5 | 27.9 | 32.6 | 26.5 | 26
143 | 25 | 131.4 | 32.3 | 23.8 | 31.6 | 34.7 | 30.6 | 27.9 | 32.6 | 26.5 | 26
144 | 26 | 137.4 | 32.3 | 24 | 31.7 | 34.6 | 30.5 | 27.9 | 32.6 | 26.5 | 26
145 | 27 | 143.4 | 32.5 | 24.3 | 31.8 | 34.6 | 30.5 | 27.9 | 32.6 | 26.5 | 26
146 | 28 | 149.4 | 32.6 | 24.5 | 31.9 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26
147 | 29 | 155.4 | 32.8 | 24.8 | 32.1 | 34.6 | 30.6 | 27.9 | 32.7 | 26.4 | 26
148 | 30 | 161.4 | 32.9 | 25 | 32.2 | 34.6 | 30.6 | 27.9 | 32.7 | 26.5 | 26
149 | 31 | 167.4 | 33.1 | 25.3 | 32.3 | 34.5 | 30.5 | 27.9 | 32.8 | 26.5 | 26
150 | 32 | 173.4 | 33.2 | 25.7 | 32.5 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26
151 | 33 | 179.5 | 33.4 | 26.1 | 32.7 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26
152 | 34 | 185.5 | 33.6 | 26.5 | 32.8 | 34.6 | 30.5 | 27.9 | 32.6 | 26.5 | 26
153 | 35 | 191.6 | 33.8 | 26.8 | 33.1 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26
154 | 36 | 197.7 | 34 | 27.2 | 33.2 | 34.6 | 30.6 | 27.9 | 32.7 | 26.4 | 26
155 | 37 | 203.9 | 34.2 | 27.5 | 33.4 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26
156 | 38 | 210 | 34.4 | 28.1 | 33.6 | 34.5 | 30.5 | 27.9 | 32.7 | 26.5 | 26
157 | 39 | 216.1 | 34.6 | 28.6 | 33.8 | 34.7 | 30.5 | 27.9 | 32.7 | 26.5 | 26
158 | 40 | 222.2 | 34.9 | 29.1 | 34 | 34.6 | 30.5 | 27.9 | 32.7 | 26.4 | 26
159 | 41 | 228.3 | 35.1 | 29.5 | 34.3 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26
160 | 42 | 234.3 | 35.3 | 30 | 34.5 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26
161 | 43 | 240.4 | 35.6 | 30.4 | 34.7 | 34.7 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
162 | 44 | 246.5 | 35.9 | 30.9 | 35 | 34.6 | 30.5 | 27.9 | 32.6 | 26.5 | 26.1
163 | 45 | 252.6 | 36.2 | 31.6 | 35.3 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
164 | 46 | 258.7 | 36.5 | 32.2 | 35.6 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
165 | 47 | 264.8 | 36.8 | 32.8 | 35.8 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
166 | 48 | 270.9 | 37.1 | 33.3 | 36.1 | 34.5 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
167 | 49 | 277 | 37.4 | 33.9 | 36.4 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
168 | 50 | 283 | 37.8 | 34.5 | 36.8 | 34.7 | 30.5 | 27.9 | 32.6 | 26.5 | 26.1
169 | 51 | 289 | 38.2 | 35.3 | 37.1 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
170 | 52 | 295 | 38.5 | 36 | 37.4 | 34.6 | 30.5 | 27.9 | 32.6 | 26.5 | 26.1
171 | 53 | 301.1 | 38.9 | 36.6 | 37.9 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.1
172 | 54 | 307.1 | 39.3 | 37.3 | 38.3 | 34.7 | 30.5 | 27.9 | 32.7 | 26.5 | 26.2
173 | 55 | 313.1 | 39.7 | 38 | 38.6 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.2
174 | 56 | 319 | 40.1 | 38.9 | 39 | 34.6 | 30.5 | 27.9 | 32.7 | 26.5 | 26.2
175 | 57 | 324.9 | 40.5 | 39.7 | 39.4 | 34.7 | 30.5 | 27.9 | 32.7 | 26.5 | 26.2
176 | 58 | 330.6 | 41 | 40.5 | 39.8 | 34.7 | 30.5 | 27.9 | 32.7 | 26.5 | 26.2
177 | 59 | 336.4 | 41.4 | 41.6 | 40.2 | 34.5 | 30.5 | 27.9 | 32.7 | 26.5 | 26.2
178 | 60 | 342.2 | 41.9 | 42.4 | 40.7 | 34.7 | 30.6 | 27.9 | 32.8 | 26.5 | 26.2
179 | 61 | 348 | 42.4 | 43.1 | 41.2 | 34.7 | 30.6 | 27.9 | 32.8 | 26.5 | 26.2
180 | 62 | 353.7 | 42.9 | 43.8 | 41.7 | 34.6 | 30.5 | 27.9 | 32.8 | 26.5 | 26.2
181 | 63 | 359.5 | 43.4 | 44.6 | 42.1 | 34.6 | 30.5 | 27.9 | 32.8 | 26.5 | 26.3
182 | 64 | 365.2 | 44 | 45.5 | 42.6 | 34.7 | 30.5 | 27.9 | 32.8 | 26.5 | 26.3
183 | 65 | 370.9 | 44.4 | 46.6 | 43.1 | 34.6 | 30.5 | 27.9 | 32.8 | 26.5 | 26.3
184 | 66 | 376.5 | 45 | 47.7 | 43.6 | 34.6 | 30.5 | 27.9 | 32.8 | 26.5 | 26.3
185 | 67 | 382.1 | 45.7 | 49 | 44.2 | 34.7 | 30.6 | 27.9 | 32.9 | 26.5 | 26.3
186 | 68 | 387.7 | 46.3 | 49.9 | 44.8 | 34.8 | 30.6 | 27.9 | 32.8 | 26.5 | 26.3
187 | 69 | 393.3 | 46.8 | 51 | 45.4 | 34.6 | 30.5 | 27.9 | 32.8 | 26.5 | 26.4
188 | 70 | 398.9 | 47.5 | 51.9 | 46 | 34.8 | 30.6 | 27.9 | 32.9 | 26.5 | 26.4
189 | 71 | 404.4 | 48.1 | 53 | 46.6 | 35 | 30.6 | 27.9 | 32.9 | 26.5 | 26.4
190 | 72 | 409.8 | 48.7 | 54 | 47.2 | 34.8 | 30.6 | 27.9 | 32.9 | 26.6 | 26.4
191 | 73 | 415.2 | 49.4 | 55.4 | 47.8 | 34.7 | 30.5 | 27.9 | 32.9 | 26.6 | 26.4
192 | 74 | 420.5 | 50.1 | 56.7 | 48.5 | 34.8 | 30.6 | 27.9 | 33 | 26.6 | 26.5
193 | 75 | 425.8 | 50.8 | 58 | 49.1 | 34.7 | 30.6 | 27.9 | 32.9 | 26.6 | 26.5
194 | 76 | 431.1 | 51.5 | 59.2 | 49.8 | 34.7 | 30.5 | 27.9 | 33 | 26.6 | 26.5
195 | 77 | 436.4 | 52.3 | 60.3 | 50.5 | 34.8 | 30.6 | 27.9 | 33 | 26.6 | 26.5
196 | 78 | 441.7 | 53.1 | 61.4 | 51.3 | 34.9 | 30.6 | 27.9 | 33 | 26.6 | 26.6
197 | 79 | 446.9 | 53.9 | 62.7 | 52.1 | 34.9 | 30.6 | 27.9 | 33.1 | 26.6 | 26.6
198 | 80 | 452.1 | 54.7 | 64 | 52.9 | 34.9 | 30.6 | 27.9 | 33.1 | 26.6 | 26.6
199 | 81 | 457.3 | 55.5 | 65.4 | 53.7 | 34.9 | 30.6 | 27.9 | 33.1 | 26.6 | 26.6
200 | 82 | 462.4 | 56.4 | 66.8 | 54.5 | 35 | 30.6 | 27.9 | 33.2 | 26.6 | 26.7
201 | 83 | 467.5 | 57.2 | 68.3 | 55.3 | 34.9 | 30.6 | 28 | 33.2 | 26.7 | 26.7
202 | 84 | 472.5 | 58.1 | 70.1 | 56.2 | 34.9 | 30.6 | 28 | 33.2 | 26.7 | 26.7
203 | 85 | 477.5 | 59 | 72 | 57.1 | 35 | 30.6 | 27.9 | 33.3 | 26.7 | 26.7
204 | 86 | 482.5 | 59.8 | 74 | 57.8 | 34.6 | 30.5 | 28 | 33.4 | 26.7 | 26.8
205 | 87 | 487.4 | 60.8 | 75.7 | 58.8 | 34.7 | 30.5 | 28 | 33.5 | 26.7 | 26.8
206 | 88 | 492.1 | 61.7 | 77.2 | 59.8 | 34.8 | 30.5 | 28 | 33.5 | 26.7 | 26.8
207 | 89 | 496.3 | 62.7 | 79 | 60.6 | 34.8 | 30.5 | 28 | 33.6 | 26.7 | 26.9
208 | 90 | 500.1 | 63.6 | 80.8 | 61.6 | 34.8 | 30.5 | 28 | 33.6 | 26.8 | 26.9
209 | 91 | 503.6 | 64.6 | 82.1 | 62.5 | 34.8 | 30.5 | 28 | 33.6 | 26.8 | 27
210 | 92 | 506.9 | 65.7 | 83.4 | 63.5 | 34.9 | 30.5 | 28 | 33.6 | 26.8 | 27
211 | 93 | 510 | 66.8 | 85.1 | 64.5 | 34.9 | 30.6 | 28.1 | 33.7 | 26.8 | 27
212 | 94 | 512.9 | 67.8 | 87 | 65.5 | 34.8 | 30.5 | 28.1 | 33.8 | 26.8 | 27.1
213 | 95 | 515.7 | 69 | 88.7 | 66.5 | 35 | 30.6 | 28.1 | 33.8 | 26.8 | 27.1
214 | 96 | 518.4 | 69.9 | 90.3 | 67.5 | 34.9 | 30.5 | 28.1 | 33.8 | 26.9 | 27.2
215 | 97 | 520.8 | 70.9 | 92.2 | 68.4 | 34.8 | 30.5 | 28.1 | 33.8 | 26.9 | 27.2
216 | 98 | 522.9 | 72 | 93.9 | 69.4 | 34.6 | 30.4 | 28.2 | 33.9 | 26.9 | 27.3
217 | 99 | 524.8 | 72.9 | 95.3 | 70.4 | 34.4 | 30.3 | 28.2 | 33.9 | 27 | 27.3
218 | 100 | 526.5 | 73.8 | 97.1 | 71.4 | 34 | 30.2 | 28.2 | 34 | 27 | 27.4
219 | 101 | 527.9 | 74.9 | 98.9 | 72.4 | 33.8 | 30.2 | 28.3 | 34 | 27 | 27.5
220 | 102 | 529.1 | 75.9 | 100.3 | 73.4 | 33.8 | 30.2 | 28.3 | 34 | 27 | 27.5
221 | 103 | 530 | 77 | 101.2 | 74.4 | 34 | 30.2 | 28.3 | 34 | 27.1 | 27.6
222 | 104 | 530.7 | 77.9 | 102.7 | 75.5 | 33.9 | 30.2 | 28.3 | 34.1 | 27.1 | 27.6
223 | 105 | 531.2 | 78.9 | 104.2 | 76.4 | 33.8 | 30.2 | 28.4 | 34.1 | 27.1 | 27.7
224 | 106 | 531.4 | 80 | 105.5 | 77.4 | 33.8 | 30.2 | 28.4 | 34.1 | 27.2 | 27.7
225 | 107 | 531.5 | 81.3 | 106.9 | 78.4 | 33.8 | 30.2 | 28.4 | 34.2 | 27.2 | 27.8
226 | 108 | 531.4 | 82.1 | 108 | 79.4 | 33.8 | 30.2 | 28.4 | 34.2 | 27.2 | 27.8
227 | 109 | 531.2 | 82.9 | 109.2 | 80.3 | 33.7 | 30.1 | 28.5 | 34.3 | 27.3 | 27.9
228 | 110 | 530.9 | 83.8 | 110.7 | 81.2 | 33.6 | 30.1 | 28.5 | 34.5 | 27.3 | 28
229 | 111 | 530.4 | 84.8 | 112.2 | 82.1 | 33.6 | 30.1 | 28.5 | 34.5 | 27.3 | 28
230 | 112 | 529.9 | 85.8 | 113.2 | 83.1 | 33.8 | 30.2 | 28.6 | 34.6 | 27.4 | 28.1
231 | 113 | 529.4 | 86.8 | 114.5 | 84.1 | 34 | 30.2 | 28.6 | 34.6 | 27.4 | 28.2
232 | 114 | 528.8 | 87.7 | 115.6 | 85 | 33.9 | 30.2 | 28.6 | 34.7 | 27.4 | 28.3
233 | 115 | 528.1 | 88.6 | 116.6 | 85.9 | 33.9 | 30.2 | 28.6 | 34.8 | 27.5 | 28.3
234 | 116 | 527.4 | 89.7 | 117.5 | 86.8 | 34 | 30.3 | 28.6 | 34.9 | 27.5 | 28.4
235 | 117 | 526.7 | 90.6 | 118.5 | 87.8 | 34.2 | 30.3 | 28.6 | 35 | 27.6 | 28.4
236 | 118 | 526 | 91.6 | 119.6 | 88.8 | 34.3 | 30.4 | 28.7 | 35 | 27.6 | 28.5
237 | 119 | 525.3 | 92.5 | 120.5 | 89.7 | 34.5 | 30.4 | 28.7 | 35.1 | 27.6 | 28.6
238 | 120 | 524.7 | 93.5 | 121.6 | 90.7 | 34.8 | 30.5 | 28.7 | 35.2 | 27.7 | 28.7
239 | 121 | 524.1 | 94.4 | 122.6 | 91.6 | 34.9 | 30.6 | 28.7 | 35.2 | 27.7 | 28.7
240 | 122 | 523.5 | 95.4 | 123.6 | 92.4 | 35 | 30.6 | 28.7 | 35.3 | 27.7 | 28.8
241 | 123 | 523 | 96.4 | 124.8 | 93.3 | 35.3 | 30.7 | 28.7 | 35.3 | 27.8 | 28.9
242 | 124 | 522.5 | 97.3 | 125.9 | 94.3 | 35.4 | 30.8 | 28.8 | 35.4 | 27.8 | 29
243 | 125 | 522.2 | 98.3 | 126.9 | 95.2 | 35.5 | 30.8 | 28.8 | 35.4 | 27.9 | 29.1
244 | 126 | 521.9 | 99.3 | 128.1 | 96.1 | 35.6 | 30.9 | 28.8 | 35.4 | 27.9 | 29.1
245 | 127 | 521.7 | 100.3 | 128.9 | 97 | 35.8 | 30.9 | 28.8 | 35.4 | 28 | 29.2
246 | 128 | 521.6 | 101.1 | 129.9 | 97.9 | 36 | 31 | 28.9 | 35.5 | 28 | 29.3
247 | 129 | 521.5 | 101.8 | 131.5 | 98.7 | 35.5 | 30.9 | 29 | 35.6 | 28.1 | 29.4
248 | 130 | 521.4 | 102.6 | 133 | 99.6 | 35.6 | 30.9 | 29 | 35.7 | 28.1 | 29.5
249 | 131 | 521.5 | 103.5 | 134.1 | 100.6 | 35.8 | 31 | 29 | 35.8 | 28.2 | 29.6
250 | 132 | 521.5 | 104.5 | 135.1 | 101.4 | 35.8 | 31 | 29.1 | 35.9 | 28.2 | 29.7
251 | 133 | 521.7 | 105.3 | 136.2 | 102.2 | 35.8 | 31 | 29.1 | 36 | 28.3 | 29.7
252 | 134 | 522 | 106.2 | 137.4 | 103.2 | 36 | 31.1 | 29.2 | 36.1 | 28.3 | 29.9
253 | 135 | 522.2 | 107.2 | 138.5 | 104 | 36.1 | 31.1 | 29.2 | 36.3 | 28.4 | 29.9
254 | 136 | 522.5 | 108 | 139.5 | 104.9 | 36 | 31.1 | 29.3 | 36.4 | 28.5 | 30
255 | 137 | 522.8 | 108.9 | 140.3 | 105.7 | 36.2 | 31.2 | 29.3 | 36.4 | 28.5 | 30.1
256 | 138 | 523.1 | 109.8 | 141.4 | 106.6 | 36.4 | 31.2 | 29.3 | 36.5 | 28.6 | 30.2
257 | 139 | 523.4 | 110.8 | 142.6 | 107.6 | 36.4 | 31.3 | 29.4 | 36.7 | 28.6 | 30.3
258 | 140 | 523.7 | 111.8 | 143.7 | 108.5 | 36.5 | 31.3 | 29.4 | 36.8 | 28.7 | 30.4
259 | 141 | 524 | 112.6 | 145.1 | 109.4 | 36.6 | 31.4 | 29.5 | 36.8 | 28.8 | 30.5
260 | 142 | 524.4 | 113.5 | 146.3 | 110.2 | 36.7 | 31.4 | 29.5 | 36.9 | 28.8 | 30.6
261 | 143 | 524.7 | 114.5 | 147.3 | 111.1 | 36.7 | 31.5 | 29.6 | 37 | 28.9 | 30.7
262 | 144 | 524.9 | 115.3 | 148.2 | 112 | 36.8 | 31.5 | 29.6 | 37 | 29 | 30.8
263 | 145 | 525.1 | 116.2 | 149.2 | 112.9 | 36.9 | 31.6 | 29.7 | 37.1 | 29 | 30.9
264 | 146 | 525.4 | 117.2 | 150.3 | 113.7 | 37 | 31.6 | 29.7 | 37.3 | 29.1 | 31
265 | 147 | 525.7 | 118.1 | 151.3 | 114.6 | 37 | 31.7 | 29.8 | 37.4 | 29.2 | 31.1
266 | 148 | 525.9 | 119.1 | 152.5 | 115.5 | 37.2 | 31.7 | 29.8 | 37.5 | 29.2 | 31.3
267 | 149 | 526.2 | 120.1 | 153.8 | 116.4 | 37.3 | 31.8 | 29.9 | 37.6 | 29.3 | 31.4
268 | 150 | 526.3 | 120.9 | 154.9 | 117.2 | 37.3 | 31.8 | 30 | 37.7 | 29.4 | 31.5
269 | 151 | 526.5 | 121.8 | 155.9 | 118.1 | 37.5 | 31.9 | 30 | 37.8 | 29.5 | 31.6
270 | 152 | 526.7 | 122.7 | 157.2 | 119 | 37.6 | 32 | 30.1 | 37.8 | 29.5 | 31.7
271 | 153 | 526.9 | 123.6 | 158.4 | 119.9 | 37.6 | 32 | 30.1 | 37.9 | 29.6 | 31.8
272 | 154 | 527 | 124.5 | 159.4 | 120.8 | 37.8 | 32.1 | 30.2 | 38 | 29.7 | 31.9
273 | 155 | 527.1 | 125.4 | 160.5 | 121.6 | 38 | 32.2 | 30.3 | 38.2 | 29.8 | 32
274 | 156 | 527.3 | 126.4 | 161.4 | 122.5 | 38.1 | 32.3 | 30.3 | 38.4 | 29.9 | 32.1
275 | 157 | 527.4 | 127.3 | 162.4 | 123.4 | 38.1 | 32.3 | 30.4 | 38.5 | 29.9 | 32.2
276 | 158 | 527.5 | 128.2 | 163.7 | 124.2 | 38.4 | 32.4 | 30.5 | 38.6 | 30 | 32.3
277 | 159 | 527.6 | 129.1 | 164.5 | 125.1 | 38.5 | 32.5 | 30.5 | 38.8 | 30.1 | 32.4
278 | 160 | 527.7 | 129.9 | 165.4 | 125.9 | 38.5 | 32.5 | 30.6 | 38.9 | 30.2 | 32.6
279 | 161 | 527.7 | 130.8 | 166.5 | 126.8 | 38.7 | 32.6 | 30.7 | 39.1 | 30.3 | 32.7
280 | 162 | 527.8 | 131.7 | 168 | 127.7 | 38.9 | 32.7 | 30.7 | 39.2 | 30.4 | 32.8
281 | 163 | 527.9 | 132.6 | 169.1 | 128.5 | 39 | 32.8 | 30.8 | 39.2 | 30.4 | 32.9
282 | 164 | 528 | 133.5 | 169.9 | 129.4 | 39 | 32.8 | 30.9 | 39.4 | 30.5 | 33.1
283 | 165 | 528.1 | 134.5 | 170.7 | 130.3 | 39.3 | 32.9 | 31 | 39.5 | 30.6 | 33.2
284 | 166 | 528.2 | 135.3 | 171.7 | 131.1 | 39.4 | 33 | 31 | 39.6 | 30.7 | 33.3
285 | 167 | 528.2 | 136.1 | 172.7 | 131.9 | 39.5 | 33.1 | 31.1 | 39.7 | 30.8 | 33.4
286 | 168 | 528.2 | 137 | 173.8 | 132.8 | 39.6 | 33.2 | 31.2 | 39.8 | 30.9 | 33.5
287 | 169 | 528.3 | 137.9 | 174.8 | 133.6 | 39.8 | 33.3 | 31.3 | 39.9 | 31 | 33.7
288 | 170 | 528.3 | 138.8 | 175.9 | 134.4 | 40 | 33.4 | 31.4 | 40 | 31.1 | 33.8
289 | 171 | 528.3 | 139.6 | 176.9 | 135.3 | 40 | 33.4 | 31.5 | 40.1 | 31.2 | 33.9
290 | 172 | 528.4 | 140.6 | 178 | 136.1 | 40.3 | 33.6 | 31.5 | 40.3 | 31.3 | 34.1
291 | 173 | 528.5 | 141.4 | 179.2 | 137 | 40.4 | 33.6 | 31.6 | 40.4 | 31.4 | 34.2
292 | 174 | 528.5 | 142.3 | 180.6 | 137.8 | 40.5 | 33.7 | 31.7 | 40.6 | 31.5 | 34.3
293 | 175 | 528.5 | 143.2 | 181.6 | 138.7 | 40.7 | 33.8 | 31.8 | 40.7 | 31.6 | 34.5
294 | 176 | 528.6 | 144.1 | 182.2 | 139.5 | 40.9 | 33.9 | 31.9 | 40.9 | 31.8 | 34.6
295 | 177 | 528.6 | 145 | 183 | 140.6 | 41 | 34 | 32 | 41 | 31.9 | 34.8
296 | 178 | 528.6 | 145.8 | 184 | 141.3 | 41.1 | 34.1 | 32.1 | 41.1 | 32 | 34.9
297 | 179 | 528.7 | 146.7 | 185 | 142.1 | 41.4 | 34.2 | 32.2 | 41.2 | 32.1 | 35
298 | 180 | 528.7 | 147.6 | 186 | 142.9 | 41.5 | 34.3 | 32.3 | 41.4 | 32.2 | 35.2
299 | 181 | 528.6 | 148.4 | 187 | 143.7 | 41.6 | 34.4 | 32.4 | 41.6 | 32.3 | 35.3
300 | 182 | 528.6 | 149.4 | 188.1 | 144.6 | 41.8 | 34.5 | 32.4 | 41.8 | 32.4 | 35.5
301 | 183 | 528.6 | 150.3 | 189.2 | 145.4 | 42.1 | 34.7 | 32.5 | 42 | 32.5 | 35.6
302 | 184 | 528.7 | 151.1 | 190.2 | 146.2 | 42.2 | 34.8 | 32.6 | 42.1 | 32.7 | 35.7
303 | 185 | 528.7 | 151.9 | 191.1 | 147 | 42.3 | 34.8 | 32.8 | 42.3 | 32.8 | 35.9
304 | 186 | 528.7 | 152.7 | 192.3 | 147.9 | 42.6 | 35 | 32.9 | 42.5 | 32.9 | 36
305 | 187 | 528.8 | 153.5 | 193.2 | 148.7 | 42.7 | 35.1 | 33 | 42.7 | 33 | 36.2
306 | 188 | 528.8 | 154.4 | 194.1 | 149.5 | 42.8 | 35.2 | 33.1 | 42.8 | 33.2 | 36.3
307 | 189 | 528.8 | 155.3 | 195.1 | 150.3 | 43 | 35.3 | 33.2 | 43 | 33.3 | 36.5
308 | 190 | 528.8 | 156.2 | 196 | 151.2 | 43.2 | 35.4 | 33.3 | 43.2 | 33.4 | 36.6
309 | 191 | 528.8 | 157.1 | 197.2 | 152 | 43.4 | 35.5 | 33.4 | 43.4 | 33.5 | 36.8
310 | 192 | 528.8 | 157.9 | 198.4 | 152.8 | 43.5 | 35.6 | 33.5 | 43.5 | 33.7 | 36.9
311 | 193 | 528.9 | 158.6 | 199.5 | 153.6 | 43.7 | 35.8 | 33.6 | 43.6 | 33.8 | 37.1
312 | 194 | 528.9 | 159.5 | 200.5 | 154.4 | 43.9 | 35.9 | 33.7 | 43.9 | 33.9 | 37.3
313 | 195 | 528.9 | 160.4 | 201.5 | 155.2 | 44.1 | 36 | 33.8 | 44.1 | 34.1 | 37.4
314 | 196 | 528.9 | 161.3 | 202.7 | 156.1 | 44.3 | 36.1 | 34 | 44.3 | 34.2 | 37.6
315 | 197 | 529 | 162.2 | 203.8 | 156.9 | 44.5 | 36.3 | 34.1 | 44.4 | 34.3 | 37.7
316 | 198 | 529 | 163 | 204.7 | 157.8 | 44.7 | 36.4 | 34.2 | 44.6 | 34.5 | 37.9
317 | 199 | 529 | 163.9 | 205.6 | 158.6 | 44.8 | 36.5 | 34.3 | 44.7 | 34.6 | 38.1
318 | 200 | 529 | 164.7 | 206.4 | 159.4 | 45.1 | 36.7 | 34.4 | 44.9 | 34.8 | 38.2
319 | 201 | 529 | 165.5 | 207.1 | 160.2 | 45.3 | 36.8 | 34.6 | 45.1 | 34.9 | 38.4
320 | 202 | 529.1 | 166.3 | 207.9 | 161 | 45.4 | 36.9 | 34.7 | 45.3 | 35.1 | 38.6
321 | 203 | 529 | 167.2 | 208.9 | 161.8 | 45.6 | 37 | 34.8 | 45.5 | 35.2 | 38.7
322 | 204 | 529 | 167.9 | 210.1 | 162.6 | 45.9 | 37.2 | 34.9 | 45.7 | 35.4 | 38.9
323 | 205 | 529 | 168.8 | 211.2 | 163.4 | 46.1 | 37.3 | 35.1 | 45.9 | 35.5 | 39.1
324 | 206 | 529 | 169.6 | 212.2 | 164.2 | 46.2 | 37.4 | 35.2 | 46.1 | 35.7 | 39.3
325 | 207 | 529 | 170.4 | 213.2 | 165 | 46.5 | 37.6 | 35.3 | 46.3 | 35.8 | 39.4
326 | 208 | 529 | 171.2 | 214.3 | 165.8 | 46.7 | 37.7 | 35.5 | 46.4 | 36 | 39.6
327 | 209 | 529 | 172.1 | 214.9 | 166.6 | 46.9 | 37.9 | 35.6 | 46.6 | 36.1 | 39.8
328 | 210 | 528.9 | 172.9 | 215.6 | 167.4 | 47.1 | 38 | 35.7 | 46.7 | 36.3 | 40
329 | 211 | 528.9 | 173.8 | 216.6 | 168.2 | 47.4 | 38.2 | 35.9 | 46.9 | 36.4 | 40.1
330 | 212 | 528.9 | 174.6 | 217.6 | 169 | 47.6 | 38.3 | 36 | 47.1 | 36.6 | 40.4
331 | 213 | 528.8 | 175.4 | 218.6 | 169.7 | 47.8 | 38.5 | 36.2 | 47.4 | 36.8 | 40.6
332 | 214 | 528.8 | 176.2 | 219.5 | 170.5 | 48.1 | 38.7 | 36.3 | 47.6 | 36.9 | 40.7
333 | 215 | 528.8 | 177.1 | 220.2 | 171.4 | 48.3 | 38.8 | 36.4 | 47.8 | 37.1 | 40.9
334 | 216 | 528.7 | 177.9 | 221.2 | 172.1 | 48.5 | 39 | 36.6 | 48 | 37.2 | 41.1
335 | 217 | 528.8 | 178.7 | 222.4 | 172.9 | 48.7 | 39.1 | 36.7 | 48.2 | 37.4 | 41.3
336 | 218 | 528.8 | 179.5 | 223.5 | 173.7 | 49 | 39.3 | 36.9 | 48.4 | 37.6 | 41.5
337 | 219 | 528.8 | 180.3 | 224.3 | 174.5 | 49.2 | 39.4 | 37 | 48.6 | 37.7 | 41.7
338 | 220 | 528.8 | 181.1 | 225 | 175.3 | 49.4 | 39.6 | 37.2 | 48.9 | 37.9 | 41.9
339 | 221 | 528.8 | 182 | 225.9 | 176 | 49.6 | 39.8 | 37.3 | 49.1 | 38.1 | 42
340 | 222 | 528.8 | 182.8 | 226.7 | 176.8 | 49.9 | 39.9 | 37.5 | 49.3 | 38.2 | 42.2
341 | 223 | 528.8 | 183.5 | 227.5 | 177.6 | 50 | 40.1 | 37.6 | 49.5 | 38.4 | 42.4
342 | 224 | 528.8 | 184.4 | 228.4 | 178.3 | 50.3 | 40.2 | 37.8 | 49.6 | 38.6 | 42.6
343 | 225 | 528.8 | 185.1 | 229.5 | 179.1 | 50.6 | 40.4 | 38 | 49.9 | 38.8 | 42.8
344 | 226 | 528.8 | 185.9 | 230.5 | 179.9 | 50.8 | 40.6 | 38.1 | 50.1 | 38.9 | 43
345 | 227 | 528.9 | 186.7 | 231.2 | 180.7 | 51 | 40.7 | 38.3 | 50.3 | 39.1 | 43.2
346 | 228 | 528.9 | 187.5 | 231.9 | 181.5 | 51.3 | 40.9 | 38.4 | 50.6 | 39.3 | 43.4
347 | 229 | 528.9 | 188.3 | 232.8 | 182.3 | 51.5 | 41.1 | 38.6 | 50.8 | 39.5 | 43.6
348 | 230 | 528.9 | 189.1 | 233.6 | 183 | 51.7 | 41.3 | 38.8 | 51.1 | 39.7 | 43.8
349 | 231 | 528.9 | 189.9 | 234.6 | 183.8 | 52 | 41.4 | 38.9 | 51.3 | 39.8 | 44
350 | 232 | 528.9 | 190.8 | 235.8 | 184.5 | 52.3 | 41.6 | 39.1 | 51.5 | 40 | 44.2
351 | 233 | 528.9 | 191.6 | 236.8 | 185.3 | 52.5 | 41.8 | 39.3 | 51.8 | 40.2 | 44.4
352 | 234 | 528.9 | 192.3 | 237.6 | 186 | 52.7 | 42 | 39.4 | 52 | 40.4 | 44.6
353 | 235 | 528.9 | 193 | 238.5 | 186.8 | 53 | 42.2 | 39.6 | 52.2 | 40.6 | 44.8
354 | 236 | 528.9 | 193.8 | 239.3 | 187.5 | 53.3 | 42.4 | 39.8 | 52.5 | 40.8 | 45.1
355 | 237 | 528.9 | 194.7 | 240.1 | 188.3 | 53.5 | 42.5 | 40 | 52.8 | 41 | 45.3
356 | 238 | 528.9 | 195.4 | 241.1 | 189 | 53.7 | 42.7 | 40.1 | 53 | 41.2 | 45.5
357 | 239 | 528.9 | 196.3 | 241.8 | 189.8 | 54 | 42.9 | 40.3 | 53.2 | 41.4 | 45.7
358 | 240 | 528.9 | 197.1 | 242.5 | 190.5 | 54.3 | 43.1 | 40.5 | 53.5 | 41.6 | 45.9
359 | 241 | 529 | 197.8 | 243.3 | 191.3 | 54.4 | 43.2 | 40.7 | 53.8 | 41.8 | 46.1
360 | 242 | 529 | 198.5 | 244.2 | 192.1 | 54.7 | 43.4 | 40.8 | 54.2 | 42 | 46.4
361 | 243 | 529 | 199.3 | 245 | 192.8 | 55 | 43.6 | 41 | 54.4 | 42.2 | 46.6
362 | 244 | 529 | 200 | 246 | 193.5 | 55.2 | 43.8 | 41.2 | 54.6 | 42.4 | 46.8
363 | 245 | 529 | 200.7 | 246.9 | 194.3 | 55.5 | 44 | 41.4 | 54.9 | 42.6 | 47
364 | 246 | 529 | 201.5 | 247.7 | 194.9 | 55.8 | 44.2 | 41.6 | 55.1 | 42.8 | 47.2
365 | 247 | 529 | 202.2 | 248.5 | 195.6 | 56.1 | 44.4 | 41.8 | 55.3 | 43 | 47.5
366 | 248 | 529 | 202.9 | 249.2 | 196.4 | 56.3 | 44.6 | 42 | 55.6 | 43.2 | 47.7
367 | 249 | 529 | 203.7 | 250.1 | 197.2 | 56.6 | 44.8 | 42.1 | 55.8 | 43.4 | 47.9
368 | 250 | 529 | 204.5 | 250.8 | 197.9 | 56.9 | 45 | 42.3 | 56.1 | 43.6 | 48.1
369 | 251 | 529.1 | 205.2 | 251.7 | 198.5 | 57.1 | 45.2 | 42.5 | 56.4 | 43.8 | 48.4
370 | 252 | 529.1 | 206 | 252.7 | 199.2 | 57.3 | 45.4 | 42.7 | 56.8 | 44 | 48.6
371 | 253 | 529.1 | 206.7 | 253.7 | 199.9 | 57.7 | 45.6 | 42.9 | 57 | 44.2 | 48.8
372 | 254 | 529.1 | 207.4 | 254.6 | 200.6 | 57.9 | 45.8 | 43.1 | 57.3 | 44.5 | 49.1
373 | 255 | 529.1 | 208.2 | 255.4 | 201.2 | 58.1 | 46 | 43.3 | 57.6 | 44.7 | 49.3
374 | 256 | 529 | 208.9 | 256.1 | 202 | 58.5 | 46.2 | 43.5 | 57.8 | 44.9 | 49.5
375 | 257 | 528.9 | 209.4 | 257.2 | 202.6 | 58.3 | 46.3 | 43.7 | 58.1 | 45.1 | 49.8
376 | 258 | 528.9 | 210.1 | 257.9 | 203.2 | 58.5 | 46.5 | 44 | 58.4 | 45.4 | 50
377 | 259 | 528.9 | 210.8 | 259 | 203.9 | 58.8 | 46.7 | 44.2 | 58.6 | 45.6 | 50.2
378 | 260 | 528.8 | 211.6 | 260 | 204.6 | 59.1 | 46.9 | 44.4 | 58.9 | 45.8 | 50.5
379 | 261 | 528.8 | 212.4 | 260.8 | 205.4 | 59.4 | 47.2 | 44.6 | 59.1 | 46 | 50.7
380 | 262 | 528.8 | 213.1 | 261.6 | 206 | 59.6 | 47.3 | 44.8 | 59.4 | 46.3 | 51
381 | 263 | 528.7 | 213.9 | 262.1 | 206.7 | 59.9 | 47.6 | 45 | 59.7 | 46.5 | 51.2
382 | 264 | 528.7 | 214.6 | 262.8 | 207.4 | 60.2 | 47.8 | 45.2 | 60 | 46.7 | 51.4
383 | 265 | 528.6 | 215.3 | 263.6 | 208.1 | 60.5 | 48 | 45.4 | 60.3 | 47 | 51.7
384 | 266 | 528.6 | 216 | 264.6 | 208.8 | 60.8 | 48.2 | 45.6 | 60.5 | 47.2 | 51.9
385 | 267 | 528.6 | 216.8 | 265.4 | 209.6 | 61.1 | 48.5 | 45.8 | 60.7 | 47.4 | 52.2
386 | 268 | 528.5 | 217.4 | 266 | 210.2 | 61.4 | 48.7 | 46 | 61 | 47.7 | 52.4
387 | 269 | 528.5 | 218.2 | 266.8 | 210.9 | 61.7 | 48.9 | 46.2 | 61.2 | 47.9 | 52.7
388 | 270 | 528.5 | 219 | 267.7 | 211.6 | 62 | 49.1 | 46.4 | 61.5 | 48.1 | 52.9
389 | 271 | 528.5 | 219.6 | 268.3 | 212.4 | 62.3 | 49.4 | 46.7 | 61.7 | 48.4 | 53.2
390 | 272 | 528.5 | 220.2 | 268.8 | 213.1 | 62.6 | 49.6 | 46.9 | 62 | 48.6 | 53.4
391 | 273 | 528.5 | 220.9 | 269.4 | 213.7 | 62.9 | 49.8 | 47.1 | 62.3 | 48.9 | 53.7
392 | 274 | 528.5 | 221.7 | 270.2 | 214.4 | 63.3 | 50 | 47.3 | 62.6 | 49.1 | 53.9
393 | 275 | 528.5 | 222.5 | 271.1 | 215.1 | 63.6 | 50.3 | 47.5 | 62.9 | 49.3 | 54.2
394 | 276 | 528.4 | 223.1 | 271.7 | 215.8 | 63.8 | 50.5 | 47.7 | 63.2 | 49.6 | 54.4
395 | 277 | 528.4 | 223.9 | 272.5 | 216.5 | 64.2 | 50.7 | 48 | 63.4 | 49.8 | 54.7
396 | 278 | 528.5 | 224.5 | 273.3 | 217.3 | 64.5 | 51 | 48.2 | 63.7 | 50.1 | 55
397 | 279 | 528.5 | 225.2 | 274.2 | 218 | 64.8 | 51.2 | 48.4 | 64.1 | 50.3 | 55.2
398 | 280 | 528.6 | 226 | 274.9 | 218.7 | 65.2 | 51.4 | 48.6 | 64.4 | 50.6 | 55.5
399 | 281 | 528.6 | 226.7 | 275.5 | 219.3 | 65.5 | 51.7 | 48.8 | 64.7 | 50.8 | 55.7
400 | 282 | 528.6 | 227.4 | 276.1 | 220 | 65.8 | 51.9 | 49.1 | 65 | 51.1 | 56
401 | 283 | 528.7 | 228 | 276.7 | 220.7 | 66.1 | 52.2 | 49.3 | 65.3 | 51.3 | 56.2
402 | 284 | 528.7 | 228.8 | 277.4 | 221.4 | 66.4 | 52.4 | 49.5 | 65.6 | 51.6 | 56.5
403 | 285 | 528.7 | 229.4 | 278.1 | 222.1 | 66.8 | 52.7 | 49.8 | 65.9 | 51.9 | 56.7
404 | 286 | 528.7 | 230.2 | 278.9 | 222.7 | 67.1 | 52.9 | 50 | 66.2 | 52.1 | 57
405 | 287 | 528.7 | 230.8 | 279.6 | 223.4 | 67.4 | 53.1 | 50.2 | 66.6 | 52.4 | 57.3
406 | 288 | 528.7 | 231.5 | 280.3 | 224.1 | 67.8 | 53.4 | 50.5 | 66.8 | 52.6 | 57.5
407 | 289 | 528.7 | 232.2 | 281.1 | 224.7 | 68.2 | 53.7 | 50.7 | 67.1 | 52.9 | 57.8
408 | 290 | 528.7 | 232.9 | 281.9 | 225.4 | 68.4 | 53.9 | 50.9 | 67.5 | 53.1 | 58.1
409 | 291 | 528.8 | 233.5 | 282.6 | 226.1 | 68.8 | 54.2 | 51.2 | 67.8 | 53.4 | 58.3
410 | 292 | 528.8 | 234.2 | 283.3 | 226.8 | 69.2 | 54.4 | 51.4 | 68.1 | 53.7 | 58.6
411 | 293 | 528.8 | 234.9 | 284.2 | 227.4 | 69.5 | 54.7 | 51.7 | 68.4 | 53.9 | 58.9
412 | 294 | 528.8 | 235.6 | 285 | 228.2 | 69.8 | 54.9 | 51.9 | 68.8 | 54.2 | 59.1
413 | 295 | 528.8 | 236.3 | 285.6 | 228.9 | 70.2 | 55.2 | 52.2 | 69.1 | 54.5 | 59.4
414 | 296 | 528.9 | 237 | 286.2 | 229.4 | 70.5 | 55.4 | 52.4 | 69.5 | 54.7 | 59.7
415 | 297 | 528.8 | 237.7 | 287.1 | 230.1 | 70.8 | 55.7 | 52.6 | 69.8 | 55 | 60
416 | 298 | 528.8 | 238.3 | 287.6 | 230.7 | 71.2 | 56 | 52.9 | 70.1 | 55.3 | 60.2
417 | 299 | 528.8 | 239 | 288.3 | 231.4 | 71.5 | 56.2 | 53.1 | 70.5 | 55.6 | 60.5
418 | 300 | 528.8 | 239.6 | 289.1 | 232.1 | 71.8 | 56.5 | 53.4 | 70.9 | 55.8 | 60.8
419 | 301 | 528.8 | 240.2 | 289.7 | 232.9 | 72.2 | 56.7 | 53.7 | 71.3 | 56.1 | 61.1
420 | 302 | 528.8 | 240.9 | 290.3 | 233.5 | 72.6 | 57 | 53.9 | 71.7 | 56.4 | 61.4
421 | 303 | 528.8 | 241.6 | 290.9 | 234.1 | 72.9 | 57.3 | 54.2 | 72 | 56.6 | 61.6
422 | 304 | 528.8 | 242.2 | 291.6 | 234.7 | 73.2 | 57.5 | 54.4 | 72.3 | 56.9 | 61.9
423 | 305 | 528.8 | 242.9 | 292.3 | 235.4 | 73.6 | 57.8 | 54.7 | 72.6 | 57.2 | 62.2
424 | 306 | 528.8 | 243.5 | 293.2 | 236 | 74 | 58.1 | 54.9 | 73 | 57.4 | 62.5
425 | 307 | 528.8 | 244.2 | 293.9 | 236.7 | 74.3 | 58.4 | 55.2 | 73.3 | 57.7 | 62.8
426 | 308 | 528.7 | 244.9 | 294.5 | 237.4 | 74.6 | 58.6 | 55.5 | 73.7 | 58 | 63
427 | 309 | 528.7 | 245.5 | 295.2 | 238 | 75.1 | 58.9 | 55.7 | 74 | 58.3 | 63.3
428 | 310 | 528.6 | 246.1 | 295.9 | 238.6 | 75.4 | 59.2 | 56 | 74.4 | 58.6 | 63.6
429 | 311 | 528.6 | 246.8 | 296.5 | 239.2 | 75.7 | 59.5 | 56.2 | 74.7 | 58.8 | 63.9
430 | 312 | 528.6 | 247.5 | 297.1 | 239.9 | 76.2 | 59.8 | 56.5 | 75 | 59.1 | 64.2
431 | 313 | 528.6 | 248.1 | 297.7 | 240.5 | 76.6 | 60.1 | 56.8 | 75.4 | 59.4 | 64.5
432 | 314 | 528.6 | 248.7 | 298.3 | 241.2 | 76.9 | 60.3 | 57 | 75.8 | 59.6 | 64.7
433 | 315 | 528.5 | 249.3 | 299 | 241.8 | 77.2 | 60.6 | 57.3 | 76.1 | 59.9 | 65
434 | 316 | 528.5 | 250 | 299.6 | 242.4 | 77.7 | 60.9 | 57.6 | 76.5 | 60.2 | 65.3
435 | 317 | 528.5 | 250.7 | 300.2 | 243.1 | 78 | 61.2 | 57.8 | 76.9 | 60.5 | 65.6
436 | 318 | 528.6 | 251.3 | 300.9 | 243.7 | 78.4 | 61.5 | 58.1 | 77.2 | 60.8 | 65.9
437 | 319 | 528.5 | 251.9 | 301.5 | 244.4 | 78.8 | 61.8 | 58.4 | 77.6 | 61 | 66.2
438 | 320 | 528.6 | 252.5 | 302.1 | 245 | 79.1 | 62.1 | 58.7 | 78 | 61.3 | 66.5
439 | 321 | 528.6 | 253.1 | 302.7 | 245.7 | 79.5 | 62.4 | 58.9 | 78.3 | 61.6 | 66.8
440 | 322 | 528.6 | 253.7 | 303.5 | 246.3 | 79.8 | 62.6 | 59.2 | 78.7 | 61.9 | 67.1
441 | 323 | 528.7 | 254.4 | 304.3 | 246.9 | 80.2 | 63 | 59.5 | 79.1 | 62.1 | 67.4
442 | 324 | 528.7 | 255 | 305 | 247.5 | 80.6 | 63.2 | 59.8 | 79.4 | 62.4 | 67.7
443 | 325 | 528.7 | 255.6 | 305.7 | 248.1 | 80.9 | 63.5 | 60.1 | 79.8 | 62.7 | 68
444 | 326 | 528.7 | 256.2 | 306.3 | 248.7 | 81.3 | 63.8 | 60.3 | 80.1 | 63 | 68.3
445 | 327 | 528.8 | 256.8 | 306.9 | 249.3 | 81.7 | 64.1 | 60.6 | 80.6 | 63.3 | 68.6
446 | 328 | 528.8 | 257.3 | 307.6 | 249.9 | 82 | 64.4 | 60.9 | 80.9 | 63.6 | 68.9
447 | 329 | 528.8 | 257.9 | 308.2 | 250.5 | 82.4 | 64.7 | 61.2 | 81.3 | 63.8 | 69.2
448 | 330 | 528.8 | 258.6 | 308.7 | 251.1 | 82.8 | 65 | 61.5 | 81.7 | 64.1 | 69.5
449 | 331 | 528.8 | 259.2 | 309.4 | 251.8 | 83.2 | 65.3 | 61.8 | 82.2 | 64.4 | 69.8
450 | 332 | 528.8 | 259.8 | 310.1 | 252.4 | 83.5 | 65.6 | 62.1 | 82.6 | 64.7 | 70.1
451 | 333 | 528.8 | 260.4 | 310.6 | 253 | 83.9 | 65.9 | 62.4 | 83 | 65 | 70.4
452 | 334 | 528.8 | 261 | 311.2 | 253.6 | 84.3 | 66.2 | 62.6 | 83.4 | 65.3 | 70.7
453 | 335 | 528.8 | 261.6 | 311.9 | 254.1 | 84.7 | 66.5 | 62.9 | 83.8 | 65.6 | 71
454 | 336 | 528.8 | 262.2 | 312.5 | 254.8 | 85 | 66.8 | 63.2 | 84.2 | 65.8 | 71.3
455 | 337 | 528.8 | 262.7 | 313 | 255.4 | 85.5 | 67.1 | 63.5 | 84.6 | 66.1 | 71.6
456 | 338 | 528.8 | 263.4 | 313.7 | 255.9 | 85.9 | 67.4 | 63.8 | 85 | 66.4 | 72
457 | 339 | 528.8 | 263.9 | 314.4 | 256.5 | 86.2 | 67.7 | 64.1 | 85.4 | 66.7 | 72.3
458 | 340 | 528.8 | 264.5 | 314.9 | 257.1 | 86.7 | 68 | 64.4 | 85.7 | 67 | 72.6
459 | 341 | 528.8 | 265.1 | 315.5 | 257.7 | 87.1 | 68.4 | 64.7 | 86.1 | 67.3 | 72.9
460 | 342 | 528.8 | 265.7 | 316.1 | 258.3 | 87.4 | 68.7 | 65 | 86.5 | 67.6 | 73.2
461 | 343 | 528.9 | 266.3 | 316.6 | 258.9 | 87.7 | 69 | 65.3 | 86.8 | 67.9 | 73.5
462 | 344 | 528.8 | 266.9 | 317.2 | 259.5 | 88.2 | 69.3 | 65.6 | 87.2 | 68.2 | 73.8
463 | 345 | 528.8 | 267.5 | 317.8 | 260 | 88.6 | 69.6 | 65.9 | 87.5 | 68.5 | 74.1
464 | 346 | 528.8 | 268 | 318.4 | 260.6 | 88.9 | 69.9 | 66.2 | 87.9 | 68.9 | 74.5
465 | 347 | 528.8 | 268.6 | 318.9 | 261.2 | 89.3 | 70.2 | 66.5 | 88.4 | 69.2 | 74.8
466 | 348 | 528.8 | 269.2 | 319.5 | 261.7 | 89.6 | 70.5 | 66.8 | 88.8 | 69.5 | 75.1
467 | 349 | 528.8 | 269.7 | 320.2 | 262.3 | 90 | 70.8 | 67.1 | 89.2 | 69.8 | 75.4
468 | 350 | 528.8 | 270.4 | 320.8 | 262.9 | 90.4 | 71.1 | 67.4 | 89.6 | 70.1 | 75.8
469 | 351 | 528.8 | 270.9 | 321.4 | 263.5 | 90.8 | 71.4 | 67.7 | 90 | 70.4 | 76.1
470 | 352 | 528.7 | 271.5 | 322 | 264 | 91.2 | 71.8 | 68 | 90.4 | 70.7 | 76.4
471 | 353 | 528.7 | 272 | 322.5 | 264.6 | 91.5 | 72.1 | 68.4 | 90.9 | 71 | 76.7
472 | 354 | 528.7 | 272.6 | 323.2 | 265.2 | 92 | 72.4 | 68.7 | 91.3 | 71.3 | 77.1
473 | 355 | 528.7 | 273.2 | 324 | 265.8 | 92.4 | 72.7 | 69 | 91.7 | 71.6 | 77.4
474 | 356 | 528.6 | 273.7 | 324.6 | 266.3 | 92.8 | 73.1 | 69.3 | 92 | 71.9 | 77.7
475 | 357 | 528.6 | 274.3 | 325 | 267 | 93.1 | 73.4 | 69.6 | 92.4 | 72.2 | 78
476 | 358 | 528.5 | 274.9 | 325.5 | 267.5 | 93.6 | 73.7 | 69.9 | 92.9 | 72.5 | 78.4
477 | 359 | 528.5 | 275.5 | 326.1 | 268 | 94 | 74 | 70.2 | 93.3 | 72.8 | 78.7
478 | 360 | 528.4 | 276 | 326.6 | 268.6 | 94.4 | 74.3 | 70.5 | 93.8 | 73.2 | 79
479 | 361 | 528.4 | 276.6 | 327.2 | 269.2 | 94.8 | 74.7 | 70.8 | 94.2 | 73.5 | 79.4
480 | 362 | 528.4 | 277.2 | 327.9 | 269.7 | 95.2 | 75 | 71.2 | 94.6 | 73.8 | 79.7
481 | 363 | 528.3 | 277.7 | 328.5 | 270.3 | 95.6 | 75.3 | 71.5 | 95.1 | 74.1 | 80
482 | 364 | 528.3 | 278.3 | 329 | 270.8 | 96 | 75.6 | 71.8 | 95.4 | 74.4 | 80.3
483 | 365 | 528.3 | 278.8 | 329.4 | 271.4 | 96.4 | 76 | 72.1 | 95.9 | 74.7 | 80.7
484 | 366 | 528.3 | 279.3 | 329.8 | 271.9 | 96.8 | 76.3 | 72.4 | 96.3 | 75 | 81
485 | 367 | 528.3 | 279.9 | 330.4 | 272.5 | 97.1 | 76.6 | 72.7 | 96.8 | 75.3 | 81.4
486 | 368 | 528.2 | 280.5 | 331 | 273.1 | 97.6 | 76.9 | 73.1 | 97.2 | 75.6 | 81.7
487 | 369 | 528.3 | 281 | 331.6 | 273.6 | 98 | 77.3 | 73.4 | 97.6 | 76 | 82
488 | 370 | 528.3 | 281.5 | 332.3 | 274.2 | 98.3 | 77.6 | 73.7 | 98.1 | 76.3 | 82.4
489 | 371 | 528.3 | 282 | 332.9 | 274.8 | 98.7 | 77.9 | 74 | 98.5 | 76.6 | 82.7
490 | 372 | 528.3 | 282.6 | 333.4 | 275.3 | 99.2 | 78.2 | 74.3 | 98.9 | 76.9 | 83.1
491 | 373 | 528.3 | 283.1 | 333.8 | 275.8 | 99.6 | 78.6 | 74.7 | 99.3 | 77.2 | 83.4
492 | 374 | 528.3 | 283.6 | 334.4 | 276.4 | 99.9 | 78.9 | 75 | 99.8 | 77.5 | 83.7
493 | 375 | 528.4 | 284.2 | 334.9 | 276.9 | 100.4 | 79.2 | 75.3 | 100.3 | 77.8 | 84.1
494 | 376 | 528.3 | 284.7 | 335.4 | 277.4 | 100.8 | 79.5 | 75.6 | 100.8 | 78.1 | 84.4
495 | 377 | 528.3 | 285.2 | 336 | 277.9 | 101.1 | 79.9 | 76 | 101.2 | 78.4 | 84.8
496 | 378 | 528.3 | 285.8 | 336.5 | 278.5 | 101.5 | 80.2 | 76.3 | 101.7 | 78.8 | 85.1
497 | 379 | 528.4 | 286.3 | 337 | 279 | 101.9 | 80.5 | 76.6 | 102.1 | 79.1 | 85.5
498 | 380 | 528.4 | 286.9 | 337.6 | 279.6 | 102.3 | 80.9 | 76.9 | 102.6 | 79.4 | 85.8
499 | 381 | 528.4 | 287.4 | 338.2 | 280.1 | 102.6 | 81.2 | 77.3 | 103 | 79.7 | 86.2
500 | 382 | 528.4 | 287.8 | 338.8 | 280.6 | 103.1 | 81.5 | 77.6 | 103.4 | 80 | 86.5
501 | 383 | 528.4 | 288.4 | 339.3 | 281.1 | 103.4 | 81.8 | 77.9 | 103.9 | 80.3 | 86.9
502 | 384 | 528.4 | 288.9 | 339.9 | 281.6 | 103.8 | 82.2 | 78.3 | 104.4 | 80.6 | 87.2
503 | 385 | 528.4 | 289.4 | 340.4 | 282.2 | 104.2 | 82.5 | 78.6 | 104.8 | 81 | 87.5
504 | 386 | 528.3 | 289.9 | 340.8 | 282.7 | 104.6 | 82.8 | 78.9 | 105.2 | 81.3 | 87.9
505 | 387 | 528.3 | 290.4 | 341.3 | 283.2 | 105 | 83.2 | 79.2 | 105.5 | 81.6 | 88.2
506 | 388 | 528.3 | 290.9 | 341.8 | 283.7 | 105.3 | 83.5 | 79.6 | 105.9 | 81.9 | 88.6
507 | 389 | 528.3 | 291.5 | 342.2 | 284.3 | 105.8 | 83.8 | 79.9 | 106.4 | 82.2 | 89
508 | 390 | 528.3 | 292 | 342.7 | 284.8 | 106.2 | 84.2 | 80.2 | 106.8 | 82.6 | 89.3
509 | 391 | 528.2 | 292.6 | 343.2 | 285.3 | 106.5 | 84.5 | 80.5 | 107.3 | 82.9 | 89.7
510 | 392 | 528.2 | 293 | 343.8 | 285.9 | 106.9 | 84.8 | 80.9 | 107.8 | 83.2 | 90
511 | 393 | 528.2 | 293.5 | 344.2 | 286.4 | 107.3 | 85.1 | 81.2 | 108.3 | 83.5 | 90.4
512 | 394 | 528.1 | 294 | 344.7 | 286.9 | 107.7 | 85.5 | 81.5 | 108.7 | 83.8 | 90.7
513 | 395 | 528.1 | 294.5 | 345.3 | 287.4 | 108 | 85.8 | 81.9 | 109.2 | 84.1 | 91.1
514 | 396 | 528.1 | 295 | 345.7 | 287.9 | 108.4 | 86.1 | 82.2 | 109.6 | 84.5 | 91.4
515 | 397 | 528 | 295.5 | 346.2 | 288.4 | 108.8 | 86.5 | 82.5 | 110.1 | 84.8 | 91.8
516 | 398 | 528 | 296 | 346.7 | 288.9 | 109.2 | 86.8 | 82.9 | 110.6 | 85.1 | 92.2
517 | 399 | 528 | 296.5 | 347.1 | 289.4 | 109.6 | 87.1 | 83.2 | 111.1 | 85.4 | 92.5
518 | 400 | 527.9 | 297 | 347.6 | 289.9 | 110 | 87.4 | 83.5 | 111.5 | 85.8 | 92.9
519 | 401 | 527.9 | 297.5 | 348.1 | 290.4 | 110.4 | 87.8 | 83.8 | 112 | 86.1 | 93.2
520 | 402 | 527.8 | 298 | 348.6 | 290.9 | 110.7 | 88.1 | 84.2 | 112.3 | 86.4 | 93.6
521 | 403 | 527.8 | 298.5 | 349.1 | 291.5 | 111.2 | 88.4 | 84.5 | 112.8 | 86.8 | 94
522 | 404 | 527.8 | 299 | 349.7 | 292 | 111.6 | 88.8 | 84.8 | 113.3 | 87.1 | 94.3
523 | 405 | 527.7 | 299.5 | 350.1 | 292.5 | 112 | 89.1 | 85.2 | 113.7 | 87.4 | 94.7
524 | 406 | 527.7 | 300 | 350.6 | 293 | 112.4 | 89.4 | 85.5 | 114 | 87.7 | 95
525 | 407 | 527.7 | 300.5 | 351.2 | 293.5 | 112.8 | 89.8 | 85.8 | 114.4 | 88.1 | 95.4
526 | 408 | 527.7 | 301 | 351.6 | 294 | 113.2 | 90.1 | 86.2 | 114.8 | 88.4 | 95.8
527 | 409 | 527.7 | 301.4 | 352.2 | 294.4 | 113.5 | 90.4 | 86.5 | 115.3 | 88.8 | 96.1
528 | 410 | 527.7 | 301.9 | 352.6 | 294.9 | 114 | 90.7 | 86.8 | 115.8 | 89.1 | 96.5
529 | 411 | 527.7 | 302.4 | 353 | 295.4 | 114.4 | 91.1 | 87.1 | 116.2 | 89.4 | 96.8
530 | 412 | 527.7 | 302.9 | 353.5 | 295.9 | 114.7 | 91.4 | 87.5 | 116.6 | 89.8 | 97.2
531 | 413 | 527.7 | 303.3 | 354.2 | 296.4 | 115.1 | 91.7 | 87.8 | 117.1 | 90.1 | 97.6
532 | 414 | 527.7 | 303.8 | 354.7 | 296.9 | 115.5 | 92.1 | 88.1 | 117.6 | 90.5 | 97.9
533 | 415 | 527.7 | 304.3 | 355.1 | 297.4 | 115.9 | 92.4 | 88.5 | 118.1 | 90.8 | 98.3
534 | 416 | 527.7 | 304.8 | 355.4 | 297.9 | 116.3 | 92.7 | 88.8 | 118.6 | 91.2 | 98.7
535 | 417 | 527.8 | 305.2 | 355.8 | 298.4 | 116.7 | 93 | 89.1 | 119.1 | 91.6 | 99
536 | 418 | 527.7 | 305.7 | 356.3 | 298.8 | 117.1 | 93.4 | 89.5 | 119.6 | 91.9 | 99.4
537 | 419 | 527.7 | 306.2 | 356.7 | 299.3 | 117.5 | 93.7 | 89.8 | 120.1 | 92.3 | 99.8
538 | 420 | 527.7 | 306.7 | 357.1 | 299.8 | 117.9 | 94 | 90.1 | 120.5 | 92.6 | 100.1
539 | 421 | 527.6 | 307.1 | 357.5 | 300.3 | 118.4 | 94.3 | 90.4 | 121 | 93 | 100.5
540 | 422 | 527.6 | 307.6 | 357.9 | 300.7 | 118.8 | 94.7 | 90.8 | 121.5 | 93.3 | 100.9
541 | 423 | 527.6 | 308.1 | 358.5 | 301.2 | 119.1 | 95 | 91.1 | 121.9 | 93.7 | 101.2
542 | 424 | 527.6 | 308.5 | 359.1 | 301.7 | 119.6 | 95.3 | 91.4 | 122.3 | 94 | 101.6
543 | 425 | 527.6 | 309 | 359.6 | 302.2 | 120 | 95.7 | 91.8 | 122.7 | 94.4 | 102
544 | 426 | 527.6 | 309.4 | 360 | 302.7 | 120.4 | 96 | 92.1 | 123.2 | 94.8 | 102.4
545 | 427 | 527.6 | 309.9 | 360.5 | 303.1 | 120.8 | 96.3 | 92.4 | 123.6 | 95.1 | 102.7
546 | 428 | 527.6 | 310.4 | 360.8 | 303.6 | 121.2 | 96.6 | 92.8 | 124 | 95.5 | 103.1
547 | 429 | 527.7 | 310.8 | 361.3 | 304.1 | 121.6 | 97 | 93.1 | 124.4 | 95.8 | 103.5
548 | 430 | 527.7 | 311.3 | 361.7 | 304.5 | 122 | 97.3 | 93.4 | 124.8 | 96.2 | 103.9
549 | 431 | 527.7 | 311.7 | 362.1 | 305 | 122.4 | 97.6 | 93.8 | 125.2 | 96.6 | 104.2
550 | 432 | 527.7 | 312.2 | 362.5 | 305.5 | 122.8 | 98 | 94.1 | 125.5 | 96.9 | 104.6
551 | 433 | 527.7 | 312.6 | 362.9 | 305.9 | 123.2 | 98.3 | 94.4 | 126 | 97.3 | 104.9
552 | 434 | 527.7 | 313.1 | 363.4 | 306.4 | 123.6 | 98.6 | 94.7 | 126.4 | 97.7 | 105.3
553 | 435 | 527.7 | 313.5 | 363.8 | 306.9 | 124.1 | 99 | 95.1 | 126.8 | 98 | 105.7
554 | 436 | 527.6 | 314 | 364.2 | 307.3 | 124.5 | 99.3 | 95.4 | 127.3 | 98.4 | 106
555 | 437 | 527.6 | 314.5 | 364.6 | 307.8 | 124.9 | 99.6 | 95.7 | 127.8 | 98.7 | 106.4
556 | 438 | 527.6 | 314.9 | 365.1 | 308.3 | 125.3 | 100 | 96.1 | 128.2 | 99.1 | 106.8
557 | 439 | 527.6 | 315.4 | 365.5 | 308.7 | 125.8 | 100.3 | 96.4 | 128.6 | 99.5 | 107.2
558 | 440 | 527.6 | 315.8 | 365.9 | 309.2 | 126.1 | 100.6 | 96.7 | 129 | 99.8 | 107.6
559 | 441 | 527.6 | 316.3 | 366.3 | 309.6 | 126.5 | 100.9 | 97.1 | 129.4 | 100.2 | 107.9
560 | 442 | 527.6 | 316.7 | 366.8 | 310.1 | 127 | 101.3 | 97.4 | 129.9 | 100.5 | 108.3
561 | 443 | 527.6 | 317.2 | 367.1 | 310.5 | 127.4 | 101.6 | 97.7 | 130.3 | 100.9 | 108.7
562 | 444 | 527.6 | 317.6 | 367.7 | 311 | 127.7 | 101.9 | 98.1 | 130.7 | 101.3 | 109
563 | 445 | 527.7 | 318 | 368.2 | 311.4 | 128.1 | 102.3 | 98.4 | 131.1 | 101.6 | 109.4
564 | 446 | 527.7 | 318.4 | 368.6 | 311.9 | 128.5 | 102.6 | 98.7 | 131.6 | 102 | 109.8
565 | 447 | 527.7 | 318.9 | 369 | 312.3 | 128.9 | 103 | 99.1 | 132 | 102.4 | 110.2
566 | 448 | 527.7 | 319.3 | 369.4 | 312.8 | 129.2 | 103.3 | 99.4 | 132.4 | 102.7 | 110.6
567 | 449 | 527.7 | 319.7 | 369.8 | 313.2 | 129.7 | 103.7 | 99.8 | 132.8 | 103.1 | 111
568 | 450 | 527.7 | 320.1 | 370.2 | 313.7 | 130.1 | 104 | 100.1 | 133.2 | 103.4 | 111.3
569 | 451 | 527.7 | 320.6 | 370.6 | 314.1 | 130.4 | 104.4 | 100.5 | 133.6 | 103.8 | 111.7
570 | 452 | 527.7 | 321.1 | 371 | 314.6 | 130.8 | 104.8 | 100.8 | 133.9 | 104.2 | 112.1
571 | 453 | 527.7 | 321.5 | 371.4 | 315 | 131.2 | 105.1 | 101.2 | 134.4 | 104.5 | 112.5
572 | 454 | 527.7 | 321.9 | 371.7 | 315.4 | 131.5 | 105.5 | 101.5 | 134.8 | 104.9 | 112.9
573 | 455 | 527.7 | 322.3 | 372.2 | 315.9 | 131.9 | 105.9 | 101.9 | 135.2 | 105.2 | 113.3
574 | 456 | 527.8 | 322.7 | 372.7 | 316.3 | 132.3 | 106.3 | 102.2 | 135.5 | 105.6 | 113.6
575 | 457 | 527.8 | 323.2 | 373 | 316.7 | 132.7 | 106.6 | 102.6 | 135.9 | 106 | 114
576 | 458 | 527.8 | 323.6 | 373.4 | 317.2 | 133 | 107 | 102.9 | 136.3 | 106.3 | 114.4
577 | 459 | 527.8 | 324 | 373.8 | 317.6 | 133.4 | 107.4 | 103.3 | 136.6 | 106.7 | 114.8
578 | 460 | 527.8 | 323.8 | 375.4 | 317.6 | 132.7 | 107.4 | 103.8 | 137.1 | 107.1 | 115.2
579 | 461 | 527.8 | 323.8 | 376.6 | 317.7 | 132.4 | 107.6 | 104.2 | 137.5 | 107.5 | 115.6
580 | 462 | 527.8 | 324.3 | 377 | 318.1 | 132.8 | 108 | 104.6 | 137.9 | 107.8 | 116
581 | 463 | 527.7 | 324.6 | 377.6 | 318.6 | 133.2 | 108.4 | 105 | 138.3 | 108.2 | 116.3
582 | 464 | 527.7 | 325.1 | 377.9 | 319 | 133.5 | 108.8 | 105.3 | 138.7 | 108.6 | 116.7
583 | 465 | 527.7 | 325.5 | 378.3 | 319.4 | 133.9 | 109.2 | 105.7 | 139.1 | 109 | 117.1
584 | 466 | 527.6 | 325.9 | 378.7 | 319.8 | 134.3 | 109.6 | 106.1 | 139.5 | 109.3 | 117.5
585 | 467 | 527.6 | 326.3 | 379.1 | 320.3 | 134.7 | 110 | 106.5 | 139.9 | 109.7 | 117.9
586 | 468 | 527.6 | 326.7 | 379.5 | 320.7 | 135.1 | 110.4 | 106.9 | 140.3 | 110.1 | 118.2
587 | 469 | 527.5 | 327.1 | 379.9 | 321.1 | 135.5 | 110.8 | 107.3 | 140.7 | 110.4 | 118.6
588 | 470 | 527.5 | 327.5 | 380.2 | 321.5 | 135.9 | 111.2 | 107.6 | 141.2 | 110.8 | 119
589 | 471 | 527.5 | 327.9 | 380.6 | 322 | 136.3 | 111.6 | 108 | 141.5 | 111.2 | 119.4
590 | 472 | 527.4 | 328.3 | 381 | 322.4 | 136.7 | 111.9 | 108.4 | 141.9 | 111.6 | 119.8
591 | 473 | 527.4 | 328.7 | 381.3 | 322.8 | 137 | 112.3 | 108.8 | 142.3 | 111.9 | 120.2
592 | 474 | 527.3 | 329.1 | 381.6 | 323.2 | 137.4 | 112.6 | 109.2 | 142.7 | 112.3 | 120.6
593 | 475 | 527.2 | 329.5 | 382 | 323.6 | 137.9 | 113 | 109.6 | 143.1 | 112.7 | 121
594 | 476 | 527.2 | 329.9 | 382.4 | 324 | 138.3 | 113.3 | 110 | 143.6 | 113.1 | 121.3
595 | 477 | 527.1 | 330.3 | 382.8 | 324.4 | 138.7 | 113.6 | 110.4 | 144 | 113.4 | 121.7
596 | 478 | 527.1 | 330.8 | 383.2 | 324.8 | 139.1 | 113.9 | 110.8 | 144.4 | 113.8 | 122.1
597 | 479 | 527.1 | 331.2 | 383.4 | 325.3 | 139.4 | 114.2 | 111.2 | 144.8 | 114.2 | 122.5
598 | 480 | 527.1 | 331.5 | 383.8 | 325.7 | 139.8 | 114.5 | 111.5 | 145.3 | 114.6 | 122.9
599 | 481 | 527.1 | 331.9 | 384.2 | 326.1 | 140.2 | 114.9 | 111.9 | 145.7 | 114.9 | 123.3
600 | 482 | 527 | 332.3 | 384.6 | 326.5 | 140.7 | 115.2 | 112.3 | 146.2 | 115.3 | 123.6
601 | 483 | 527 | 332.7 | 384.9 | 326.9 | 141.1 | 115.5 | 112.7 | 146.7 | 115.7 | 124
602 | 484 | 527 | 333.1 | 385.2 | 327.3 | 141.5 | 115.9 | 113.1 | 147.1 | 116 | 124.4
603 | 485 | 527 | 333.4 | 385.5 | 327.6 | 141.9 | 116.2 | 113.5 | 147.5 | 116.4 | 124.8
604 | 486 | 527 | 333.9 | 385.9 | 328 | 142.3 | 116.6 | 113.8 | 147.9 | 116.8 | 125.2
605 | 487 | 527 | 334.2 | 386.3 | 328.4 | 142.8 | 117 | 114.2 | 148.3 | 117.2 | 125.6
606 | 488 | 527 | 334.6 | 386.8 | 328.9 | 143.2 | 117.4 | 114.6 | 148.8 | 117.5 | 126
607 | 489 | 526.9 | 335 | 387.2 | 329.3 | 143.6 | 117.8 | 115 | 149.2 | 117.9 | 126.3
608 | 490 | 526.9 | 335.4 | 387.5 | 329.7 | 144 | 118.2 | 115.4 | 149.7 | 118.3 | 126.7
609 | 491 | 526.9 | 335.8 | 387.8 | 330.1 | 144.5 | 118.6 | 115.8 | 150.2 | 118.6 | 127.1
610 | 492 | 526.9 | 336.1 | 388.2 | 330.4 | 144.9 | 118.9 | 116.1 | 150.7 | 119 | 127.5
611 | 493 | 526.9 | 336.5 | 388.6 | 330.8 | 145.4 | 119.2 | 116.5 | 151.1 | 119.4 | 127.9
612 | 494 | 526.9 | 336.9 | 388.8 | 331.2 | 145.8 | 119.5 | 116.9 | 151.6 | 119.7 | 128.2
613 | 495 | 526.9 | 337.3 | 389.1 | 331.6 | 146.3 | 119.9 | 117.2 | 152 | 120.1 | 128.6
614 | 496 | 526.9 | 337.7 | 389.5 | 332 | 146.7 | 120.2 | 117.6 | 152.5 | 120.5 | 129
615 | 497 | 526.9 | 338 | 389.8 | 332.4 | 147.1 | 120.5 | 118 | 152.9 | 120.8 | 129.4
616 | 498 | 526.9 | 338.4 | 390.1 | 332.8 | 147.6 | 120.9 | 118.3 | 153.4 | 121.2 | 129.7
617 | 499 | 526.9 | 338.8 | 390.5 | 333.2 | 148 | 121.2 | 118.7 | 153.9 | 121.5 | 130.1
618 | 500 | 526.9 | 339.2 | 390.9 | 333.6 | 148.5 | 121.5 | 119 | 154.3 | 121.9 | 130.5
619 | 501 | 526.8 | 339.5 | 391.2 | 334 | 148.9 | 121.9 | 119.4 | 154.7 | 122.3 | 130.9
620 | 502 | 526.8 | 339.9 | 391.5 | 334.4 | 149.4 | 122.2 | 119.8 | 155.2 | 122.6 | 131.2
621 | 503 | 526.8 | 340.3 | 391.9 | 334.7 | 149.9 | 122.6 | 120.1 | 155.7 | 123 | 131.6
622 | 504 | 526.8 | 340.7 | 392.2 | 335.1 | 150.3 | 122.9 | 120.5 | 156.2 | 123.3 | 132
623 | 505 | 526.8 | 341 | 392.5 | 335.5 | 150.8 | 123.3 | 120.8 | 156.6 | 123.7 | 132.4
624 | 506 | 526.8 | 341.4 | 392.8 | 335.8 | 151.3 | 123.7 | 121.2 | 157 | 124.1 | 132.7
625 | 507 | 526.9 | 341.8 | 393.1 | 336.2 | 151.7 | 124.1 | 121.6 | 157.4 | 124.4 | 133.1
626 | 508 | 526.9 | 342.2 | 393.5 | 336.6 | 152.2 | 124.5 | 122 | 157.9 | 124.8 | 133.5
627 | 509 | 526.9 | 342.5 | 393.8 | 337 | 152.7 | 124.9 | 122.3 | 158.4 | 125.1 | 133.9
628 | 510 | 526.9 | 342.9 | 394.2 | 337.4 | 153.1 | 125.4 | 122.7 | 158.9 | 125.5 | 134.3
629 | 511 | 526.9 | 343.2 | 394.6 | 337.7 | 153.6 | 125.8 | 123.1 | 159.4 | 125.9 | 134.7
630 | 512 | 526.9 | 343.6 | 394.9 | 338.1 | 154.1 | 126.3 | 123.5 | 159.9 | 126.2 | 135.1
631 | 513 | 527 | 344 | 395.2 | 338.5 | 154.6 | 126.8 | 124 | 160.5 | 126.6 | 135.4
632 | 514 | 527 | 344.3 | 395.5 | 338.8 | 155.1 | 127.4 | 124.4 | 161 | 126.9 | 135.8
633 | 515 | 527 | 344.7 | 395.9 | 339.2 | 155.6 | 127.9 | 124.8 | 161.5 | 127.3 | 136.2
634 | 516 | 527 | 345 | 396.2 | 339.6 | 156.1 | 128.4 | 125.2 | 162 | 127.7 | 136.6
635 | 517 | 526.9 | 345.4 | 396.6 | 340 | 156.6 | 129 | 125.7 | 162.5 | 128 | 136.9
636 | 518 | 526.9 | 345.7 | 396.9 | 340.3 | 157.1 | 129.5 | 126.1 | 163.1 | 128.4 | 137.3
637 | 519 | 527 | 346.1 | 397.2 | 340.7 | 157.6 | 130.1 | 126.6 | 163.5 | 128.7 | 137.6
638 | 520 | 527 | 346.4 | 397.6 | 341.1 | 158.1 | 130.7 | 127 | 163.9 | 129.1 | 138
639 | 521 | 527 | 346.8 | 398 | 341.4 | 158.6 | 131.3 | 127.5 | 164.4 | 129.4 | 138.4
640 | 522 | 527 | 347.2 | 398.3 | 341.8 | 159.1 | 131.9 | 127.9 | 164.9 | 129.8 | 138.8
641 | 523 | 527 | 347.5 | 398.6 | 342.1 | 159.7 | 132.6 | 128.4 | 165.5 | 130.2 | 139.1
642 | 524 | 527 | 347.8 | 398.9 | 342.5 | 160.2 | 133.2 | 128.9 | 166 | 130.5 | 139.5
643 | 525 | 527 | 348.2 | 399.2 | 342.9 | 160.7 | 133.8 | 129.4 | 166.5 | 130.9 | 139.9
644 | 526 | 527 | 348.5 | 399.5 | 343.2 | 161.2 | 134.5 | 129.9 | 167 | 131.3 | 140.3
645 | 527 | 527 | 348.9 | 399.9 | 343.6 | 161.7 | 135.1 | 130.4 | 167.5 | 131.7 | 140.6
646 | 528 | 527 | 349.3 | 400.2 | 343.9 | 162.2 | 135.7 | 131 | 168.1 | 132 | 141
647 | 529 | 527 | 349.6 | 400.5 | 344.3 | 162.7 | 136.3 | 131.5 | 168.6 | 132.4 | 141.4
648 | 530 | 527.1 | 349.9 | 400.7 | 344.6 | 163.3 | 136.9 | 132 | 169.2 | 132.8 | 141.8
649 | 531 | 527.1 | 350.3 | 401.1 | 345 | 163.8 | 137.6 | 132.6 | 169.7 | 133.1 | 142.1
650 | 532 | 527.1 | 350.6 | 401.5 | 345.3 | 164.3 | 138.2 | 133.1 | 170.3 | 133.5 | 142.5
651 | 533 | 527.1 | 351 | 401.8 | 345.7 | 164.8 | 138.7 | 133.7 | 170.9 | 133.9 | 142.9
652 | 534 | 527.1 | 351.3 | 402 | 346 | 165.3 | 139.3 | 134.3 | 171.4 | 134.3 | 143.2
653 | 535 | 527.1 | 351.6 | 402.3 | 346.4 | 165.9 | 139.9 | 134.9 | 171.9 | 134.6 | 143.6
654 | 536 | 527 | 352 | 402.7 | 346.7 | 166.4 | 140.5 | 135.5 | 172.5 | 135 | 144
655 | 537 | 527 | 352.3 | 403.1 | 347.1 | 166.9 | 141.1 | 136.1 | 173 | 135.4 | 144.4
656 | 538 | 527 | 352.7 | 403.4 | 347.4 | 167.4 | 141.7 | 136.7 | 173.5 | 135.8 | 144.7
657 | 539 | 527 | 353 | 403.6 | 347.8 | 167.9 | 142.2 | 137.3 | 174 | 136.2 | 145.1
658 | 540 | 527 | 353.3 | 403.8 | 348.1 | 168.5 | 142.8 | 137.9 | 174.6 | 136.6 | 145.5
659 | 541 | 527 | 353.6 | 404.2 | 348.5 | 169 | 143.4 | 138.6 | 175.2 | 136.9 | 145.9
660 | 542 | 526.9 | 354 | 404.5 | 348.8 | 169.5 | 143.9 | 139.1 | 175.9 | 137.3 | 146.3
661 | 543 | 527 | 354.3 | 404.7 | 349.1 | 170 | 144.5 | 139.7 | 176.5 | 137.7 | 146.7
662 | 544 | 527 | 354.6 | 405 | 349.5 | 170.6 | 145 | 140.3 | 177 | 138.1 | 147
663 | 545 | 527 | 355 | 405.4 | 349.8 | 171.1 | 145.6 | 140.9 | 177.6 | 138.5 | 147.4
664 | 546 | 527 | 355.3 | 405.8 | 350.2 | 171.6 | 146.1 | 141.5 | 178.1 | 138.9 | 147.8
665 | 547 | 527 | 355.6 | 406.1 | 350.5 | 172.1 | 146.7 | 142.1 | 178.7 | 139.3 | 148.2
666 | 548 | 526.9 | 355.9 | 406.4 | 350.8 | 172.6 | 147.2 | 142.7 | 179.3 | 139.6 | 148.5
667 | 549 | 526.9 | 356.3 | 406.7 | 351.2 | 173.1 | 147.8 | 143.3 | 179.7 | 140 | 148.9
668 | 550 | 526.9 | 356.6 | 407 | 351.5 | 173.7 | 148.3 | 143.8 | 180.2 | 140.4 | 149.3
669 | 551 | 527 | 356.9 | 407.2 | 351.8 | 174.2 | 148.9 | 144.4 | 180.8 | 140.8 | 149.7
670 | 552 | 526.9 | 357.2 | 407.4 | 352.2 | 174.7 | 149.4 | 145 | 181.3 | 141.2 | 150
671 | 553 | 526.9 | 357.6 | 407.8 | 352.5 | 175.2 | 149.9 | 145.6 | 181.9 | 141.6 | 150.4
672 | 554 | 526.9 | 357.9 | 408.1 | 352.8 | 175.7 | 150.5 | 146.1 | 182.5 | 142 | 150.8
673 | 555 | 526.9 | 358.2 | 408.3 | 353.2 | 176.3 | 151 | 146.7 | 183 | 142.4 | 151.2
674 | 556 | 526.9 | 358.5 | 408.6 | 353.5 | 176.8 | 151.6 | 147.2 | 183.6 | 142.8 | 151.6
675 | 557 | 526.8 | 358.8 | 408.9 | 353.8 | 177.3 | 152.1 | 147.8 | 184.2 | 143.2 | 151.9
676 | 558 | 526.8 | 359.2 | 409.2 | 354.2 | 177.8 | 152.6 | 148.3 | 184.7 | 143.6 | 152.3
677 | 559 | 526.8 | 359.5 | 409.5 | 354.5 | 178.3 | 153.2 | 148.9 | 185.3 | 144 | 152.7
678 | 560 | 526.7 | 359.8 | 409.8 | 354.8 | 178.8 | 153.7 | 149.5 | 185.9 | 144.4 | 153.1
679 | 561 | 526.7 | 360.1 | 410 | 355.1 | 179.4 | 154.3 | 150 | 186.4 | 144.7 | 153.5
680 | 562 | 526.7 | 360.5 | 410.3 | 355.4 | 179.9 | 154.8 | 150.6 | 187 | 145.1 | 153.9
681 | 563 | 526.7 | 360.8 | 410.6 | 355.8 | 180.4 | 155.3 | 151.1 | 187.6 | 145.5 | 154.2
682 | 564 | 526.7 | 361.1 | 410.9 | 356.1 | 180.9 | 155.8 | 151.6 | 188.2 | 145.9 | 154.6
683 | 565 | 526.7 | 361.4 | 411.1 | 356.5 | 181.4 | 156.4 | 152.2 | 188.8 | 146.3 | 155
684 | 566 | 526.7 | 361.7 | 411.5 | 356.7 | 182 | 156.9 | 152.7 | 189.4 | 146.7 | 155.3
685 | 567 | 526.6 | 362 | 411.8 | 357 | 182.5 | 157.4 | 153.3 | 189.9 | 147.1 | 155.7
686 | 568 | 526.6 | 362.3 | 412 | 357.4 | 183 | 158 | 153.8 | 190.4 | 147.5 | 156.1
687 | 569 | 526.6 | 362.6 | 412.3 | 357.7 | 183.5 | 158.5 | 154.3 | 190.9 | 147.9 | 156.4
688 | 570 | 526.6 | 362.9 | 412.5 | 358 | 184 | 159 | 154.9 | 191.5 | 148.3 | 156.8
689 | 571 | 526.6 | 363.2 | 412.9 | 358.3 | 184.5 | 159.5 | 155.4 | 192.2 | 148.7 | 157.2
690 | 572 | 526.5 | 363.6 | 413.3 | 358.7 | 185 | 160.1 | 156 | 192.8 | 149.1 | 157.5
691 | 573 | 526.5 | 363.9 | 413.6 | 359 | 185.6 | 160.6 | 156.5 | 193.3 | 149.5 | 157.9
692 | 574 | 526.5 | 364.2 | 413.8 | 359.3 | 186.1 | 161.1 | 157 | 193.9 | 149.9 | 158.3
693 | 575 | 526.5 | 364.5 | 414.1 | 359.6 | 186.6 | 161.6 | 157.6 | 194.5 | 150.3 | 158.7
694 | 576 | 526.5 | 364.8 | 414.3 | 359.9 | 187.1 | 162.2 | 158.1 | 195 | 150.6 | 159.2
695 | 577 | 526.5 | 365.1 | 414.6 | 360.2 | 187.6 | 162.7 | 158.6 | 195.6 | 151 | 159.6
696 | 578 | 526.5 | 365.4 | 414.8 | 360.5 | 188.2 | 163.2 | 159.2 | 196.1 | 151.4 | 160
697 | 579 | 526.5 | 365.7 | 415.1 | 360.8 | 188.7 | 163.7 | 159.7 | 196.6 | 151.8 | 160.4
698 | 580 | 526.5 | 366 | 415.4 | 361.1 | 189.2 | 164.2 | 160.2 | 197.2 | 152.2 | 160.8
699 | 581 | 526.6 | 366.3 | 415.7 | 361.4 | 189.7 | 164.7 | 160.7 | 197.8 | 152.6 | 161.2
700 | 582 | 526.6 | 366.6 | 416 | 361.7 | 190.2 | 165.3 | 161.3 | 198.5 | 153 | 161.6
701 | 583 | 526.6 | 366.9 | 416.3 | 362 | 190.7 | 165.8 | 161.8 | 199.1 | 153.3 | 161.9
702 | 584 | 526.7 | 367.2 | 416.6 | 362.3 | 191.3 | 166.3 | 162.3 | 199.6 | 153.7 | 162.3
703 | 585 | 526.7 | 367.5 | 416.9 | 362.7 | 191.8 | 166.8 | 162.8 | 200.1 | 154.1 | 162.7
704 | 586 | 526.7 | 367.8 | 417.1 | 363 | 192.3 | 167.3 | 163.4 | 200.7 | 154.5 | 163.1
705 | 587 | 526.8 | 368.2 | 417.3 | 363.3 | 192.7 | 167.8 | 163.9 | 201.2 | 154.9 | 163.4
706 | 588 | 526.8 | 368.5 | 417.6 | 363.6 | 193.3 | 168.4 | 164.4 | 201.8 | 155.3 | 163.8
707 | 589 | 526.8 | 368.8 | 417.9 | 363.9 | 193.8 | 168.9 | 165 | 202.3 | 155.7 | 164.2
708 | 590 | 526.8 | 369.1 | 418.2 | 364.2 | 194.3 | 169.4 | 165.5 | 202.9 | 156 | 164.6
709 | 591 | 526.8 | 369.3 | 418.4 | 364.5 | 194.8 | 169.9 | 166 | 203.5 | 156.4 | 165
710 | 592 | 526.8 | 369.6 | 418.7 | 364.8 | 195.4 | 170.4 | 166.5 | 204 | 156.8 | 165.4
711 | 593 | 526.7 | 369.9 | 419 | 365.1 | 195.9 | 170.9 | 167 | 204.6 | 157.2 | 165.8
712 | 594 | 526.7 | 370.2 | 419.2 | 365.4 | 196.4 | 171.5 | 167.6 | 205.1 | 157.6 | 166.2
713 | 595 | 526.7 | 370.5 | 419.5 | 365.7 | 196.9 | 172 | 168.1 | 205.7 | 158 | 166.6
714 | 596 | 526.6 | 370.8 | 419.8 | 366 | 197.4 | 172.5 | 168.6 | 206.3 | 158.3 | 167
715 | 597 | 526.6 | 371.1 | 420.1 | 366.2 | 197.9 | 173 | 169.1 | 206.9 | 158.7 | 167.4
716 | 598 | 526.6 | 371.4 | 420.4 | 366.6 | 198.4 | 173.5 | 169.6 | 207.4 | 159.1 | 167.8
717 | 599 | 526.6 | 371.7 | 420.6 | 366.9 | 199 | 174 | 170.2 | 207.9 | 159.5 | 168.2
718 | 600 | 526.6 | 371.9 | 420.9 | 367.1 | 199.5 | 174.5 | 170.7 | 208.4 | 159.9 | 168.6
719 | 601 | 526.6 | 372.2 | 421.2 | 367.4 | 200 | 175 | 171.2 | 208.9 | 160.3 | 169
720 | 602 | 526.5 | 372.5 | 421.5 | 367.7 | 200.5 | 175.6 | 171.7 | 209.4 | 160.6 | 169.4
721 | 603 | 526.5 | 372.8 | 421.8 | 368 | 201 | 176.1 | 172.2 | 210 | 161 | 169.9
722 | 604 | 526.5 | 373.1 | 422 | 368.3 | 201.5 | 176.6 | 172.8 | 210.5 | 161.4 | 170.3
723 | 605 | 526.5 | 373.4 | 422.2 | 368.6 | 202 | 177.1 | 173.3 | 211.1 | 161.8 | 170.7
724 | 606 | 526.5 | 373.7 | 422.5 | 368.9 | 202.5 | 177.6 | 173.8 | 211.6 | 162.2 | 171.1
725 | 607 | 526.5 | 374 | 422.8 | 369.2 | 203 | 178.1 | 174.3 | 212.2 | 162.6 | 171.6
726 | 608 | 526.5 | 374.3 | 423.1 | 369.4 | 203.5 | 178.6 | 174.8 | 212.7 | 162.9 | 172
727 | 609 | 526.5 | 374.5 | 423.3 | 369.7 | 204 | 179.1 | 175.3 | 213.3 | 163.3 | 172.4
728 | 610 | 526.5 | 374.8 | 423.5 | 370 | 204.5 | 179.6 | 175.8 | 213.9 | 163.7 | 172.8
729 | 611 | 526.4 | 375.1 | 423.8 | 370.2 | 205 | 180.1 | 176.4 | 214.4 | 164.1 | 173.2
730 | 612 | 526.4 | 375.4 | 424 | 370.5 | 205.5 | 180.6 | 176.9 | 214.9 | 164.5 | 173.6
731 | 613 | 526.4 | 375.7 | 424.2 | 370.8 | 206 | 181.1 | 177.4 | 215.4 | 164.8 | 173.9
732 | 614 | 526.4 | 376 | 424.4 | 371.1 | 206.5 | 181.6 | 177.9 | 216 | 165.2 | 174.3
733 | 615 | 526.4 | 376.2 | 424.6 | 371.4 | 207 | 182.1 | 178.4 | 216.5 | 165.6 | 174.7
734 | 616 | 526.4 | 376.5 | 424.9 | 371.7 | 207.5 | 182.6 | 178.9 | 217 | 166 | 175.1
735 | 617 | 526.4 | 376.8 | 425.1 | 372 | 208 | 183.1 | 179.4 | 217.6 | 166.4 | 175.5
736 | 618 | 526.4 | 377.1 | 425.4 | 372.2 | 208.5 | 183.6 | 179.9 | 218.3 | 166.8 | 175.9
737 | 619 | 526.5 | 377.3 | 425.7 | 372.5 | 209 | 184.1 | 180.4 | 218.8 | 167.1 | 176.3
738 | 620 | 526.5 | 377.6 | 426 | 372.8 | 209.5 | 184.6 | 181 | 219.4 | 167.5 | 176.7
739 | 621 | 526.4 | 377.9 | 426.2 | 373 | 210 | 185.1 | 181.5 | 220 | 167.9 | 177.1
740 | 622 | 526.4 | 378.2 | 426.4 | 373.3 | 210.5 | 185.6 | 182 | 220.5 | 168.3 | 177.5
741 | 623 | 526.4 | 378.5 | 426.6 | 373.6 | 211.1 | 186.1 | 182.5 | 220.9 | 168.7 | 177.9
742 | 624 | 526.4 | 378.7 | 426.8 | 373.9 | 211.6 | 186.6 | 183 | 221.5 | 169.1 | 178.3
743 | 625 | 526.5 | 379 | 427.1 | 374.2 | 212.1 | 187 | 183.5 | 222 | 169.5 | 178.7
744 | 626 | 526.5 | 379.3 | 427.3 | 374.5 | 212.6 | 187.5 | 184 | 222.6 | 169.8 | 179.1
745 | 627 | 526.5 | 379.6 | 427.5 | 374.7 | 213.1 | 188 | 184.5 | 223.1 | 170.2 | 179.4
746 | 628 | 526.5 | 379.9 | 427.8 | 375 | 213.5 | 188.5 | 185 | 223.7 | 170.6 | 179.9
747 | 629 | 526.5 | 380.1 | 428 | 375.3 | 214 | 189 | 185.5 | 224.2 | 171 | 180.3
748 | 630 | 526.5 | 380.4 | 428.2 | 375.6 | 214.5 | 189.5 | 186 | 224.7 | 171.4 | 180.7
749 | 631 | 526.5 | 380.7 | 428.5 | 375.9 | 215 | 190 | 186.5 | 225.3 | 171.8 | 181.2
750 | 632 | 526.5 | 381 | 428.7 | 376.1 | 215.4 | 190.5 | 187 | 225.8 | 172.2 | 181.6
751 | 633 | 526.5 | 381.2 | 429 | 376.4 | 215.9 | 191 | 187.5 | 226.3 | 172.6 | 182.1
752 | 634 | 526.5 | 381.5 | 429.2 | 376.6 | 216.4 | 191.5 | 188 | 226.8 | 173 | 182.5
753 | 635 | 526.5 | 381.8 | 429.4 | 376.9 | 216.9 | 192 | 188.6 | 227.4 | 173.3 | 182.9
754 | 636 | 526.5 | 382.1 | 429.7 | 377.2 | 217.4 | 192.5 | 189.1 | 227.9 | 173.7 | 183.4
755 | 637 | 526.5 | 382.3 | 429.9 | 377.5 | 217.8 | 193 | 189.6 | 228.4 | 174.1 | 183.8
756 | 638 | 526.6 | 382.6 | 430.2 | 377.7 | 218.3 | 193.4 | 190.1 | 229 | 174.5 | 184.2
757 | 639 | 526.5 | 382.9 | 430.4 | 378 | 218.8 | 193.9 | 190.6 | 229.6 | 174.9 | 184.6
758 | 640 | 526.5 | 383.1 | 430.6 | 378.3 | 219.3 | 194.4 | 191.1 | 230.2 | 175.3 | 185
759 | 641 | 526.5 | 383.4 | 430.9 | 378.5 | 219.8 | 194.9 | 191.5 | 230.8 | 175.7 | 185.5
760 | 642 | 526.6 | 383.7 | 431.2 | 378.8 | 220.2 | 195.4 | 192 | 231.2 | 176.1 | 186
761 | 643 | 526.6 | 383.9 | 431.4 | 379.1 | 220.7 | 195.9 | 192.5 | 231.7 | 176.5 | 186.5
762 | 644 | 526.5 | 384.2 | 431.7 | 379.4 | 221.2 | 196.4 | 193 | 232.2 | 176.9 | 187
763 | 645 | 526.5 | 384.5 | 431.9 | 379.6 | 221.7 | 196.9 | 193.5 | 232.6 | 177.3 | 187.4
764 | 646 | 526.5 | 384.7 | 432.1 | 379.9 | 222.2 | 197.4 | 194 | 233.1 | 177.7 | 187.9
765 | 647 | 526.5 | 385 | 432.3 | 380.2 | 222.6 | 197.8 | 194.5 | 233.6 | 178.1 | 188.4
766 | 648 | 526.5 | 385.3 | 432.6 | 380.4 | 223.1 | 198.3 | 195 | 234.2 | 178.5 | 188.9
767 | 649 | 526.4 | 385.6 | 432.8 | 380.7 | 223.6 | 198.8 | 195.5 | 234.8 | 178.9 | 189.4
768 | 650 | 526.4 | 385.8 | 433 | 380.9 | 224.1 | 199.3 | 196 | 235.3 | 179.2 | 189.9
769 | 651 | 526.4 | 386.1 | 433.2 | 381.2 | 224.6 | 199.8 | 196.4 | 235.8 | 179.6 | 190.4
770 | 652 | 526.4 | 386.3 | 433.5 | 381.5 | 225.1 | 200.3 | 196.9 | 236.2 | 180 | 190.9
771 | 653 | 526.3 | 386.6 | 433.7 | 381.8 | 225.6 | 200.8 | 197.4 | 236.7 | 180.4 | 191.4
772 | 654 | 526.3 | 386.8 | 434 | 382.1 | 226.1 | 201.2 | 197.9 | 237.3 | 180.8 | 192
773 | 655 | 526.3 | 387.1 | 434.2 | 382.3 | 226.6 | 201.7 | 198.3 | 237.8 | 181.2 | 192.5
774 | 656 | 526.3 | 387.4 | 434.5 | 382.6 | 227 | 202.2 | 198.8 | 238.3 | 181.7 | 193.1
775 | 657 | 526.2 | 387.6 | 434.7 | 382.9 | 227.5 | 202.7 | 199.2 | 238.8 | 182.1 | 193.7
776 | 658 | 526.2 | 387.9 | 434.9 | 383.2 | 227.9 | 203.1 | 199.7 | 239.3 | 182.5 | 194.3
777 | 659 | 526.2 | 388.2 | 435 | 383.4 | 228.3 | 203.6 | 200.2 | 239.7 | 182.9 | 194.7
778 | 660 | 526.2 | 388.4 | 435.3 | 383.7 | 228.7 | 204.1 | 200.6 | 240.2 | 183.3 | 195.2
779 | 661 | 526.2 | 388.7 | 435.6 | 384 | 229.2 | 204.5 | 201.1 | 240.6 | 183.7 | 195.7
780 | 662 | 526.2 | 388.9 | 435.8 | 384.3 | 229.6 | 204.9 | 201.5 | 241.1 | 184.1 | 196.2
781 | 663 | 526.2 | 389.2 | 436 | 384.5 | 230 | 205.4 | 202 | 241.7 | 184.5 | 196.7
782 | 664 | 526.2 | 389.4 | 436.2 | 384.8 | 230.5 | 205.8 | 202.4 | 242.2 | 184.9 | 197.3
783 | 665 | 526.2 | 389.7 | 436.4 | 385.1 | 230.9 | 206.3 | 202.9 | 242.7 | 185.3 | 197.9
784 | 666 | 526.2 | 389.9 | 436.7 | 385.3 | 231.3 | 206.7 | 203.3 | 243.2 | 185.7 | 198.4
785 | 667 | 526.2 | 390.2 | 437 | 385.6 | 231.8 | 207.2 | 203.7 | 243.7 | 186.1 | 198.9
786 | 668 | 526.2 | 390.4 | 437.2 | 385.9 | 232.2 | 207.6 | 204.2 | 244.1 | 186.5 | 199.3
787 | 669 | 526.2 | 390.7 | 437.4 | 386.1 | 232.6 | 208.1 | 204.6 | 244.6 | 186.9 | 199.7
788 | 670 | 526.2 | 390.9 | 437.6 | 386.4 | 233.1 | 208.5 | 205.1 | 245.1 | 187.3 | 200.2
789 | 671 | 526.3 | 391.2 | 437.8 | 386.6 | 233.5 | 208.9 | 205.5 | 245.7 | 187.7 | 200.7
790 | 672 | 526.3 | 391.4 | 438 | 386.9 | 233.9 | 209.3 | 205.9 | 246.2 | 188.1 | 201.1
791 | 673 | 526.3 | 391.6 | 438.2 | 387.2 | 234.3 | 209.8 | 206.4 | 246.9 | 188.5 | 201.6
792 | 674 | 526.3 | 391.9 | 438.4 | 387.4 | 234.7 | 210.2 | 206.8 | 247.6 | 189 | 202.1
793 | 675 | 526.4 | 392.1 | 438.7 | 387.6 | 235.1 | 210.6 | 207.2 | 248.3 | 189.4 | 202.6
794 | 676 | 526.4 | 392.4 | 438.9 | 387.9 | 235.5 | 211 | 207.7 | 249 | 189.8 | 203.1
795 | 677 | 526.4 | 392.6 | 439.1 | 388.1 | 236 | 211.5 | 208.1 | 249.6 | 190.2 | 203.6
796 | 678 | 526.4 | 392.9 | 439.3 | 388.4 | 236.4 | 211.9 | 208.6 | 250.3 | 190.6 | 204.1
797 | 679 | 526.4 | 393.1 | 439.6 | 388.6 | 236.8 | 212.3 | 209 | 251 | 191.1 | 204.6
798 | 680 | 526.4 | 393.3 | 439.8 | 388.9 | 237.2 | 212.7 | 209.4 | 251.8 | 191.5 | 205.1
799 | 681 | 526.4 | 393.6 | 440 | 389.1 | 237.6 | 213.2 | 209.8 | 252.5 | 191.9 | 205.5
800 | 682 | 526.4 | 393.8 | 440.2 | 389.3 | 237.9 | 213.6 | 210.3 | 253.3 | 192.3 | 206.1
801 | 683 | 526.4 | 394 | 440.4 | 389.6 | 238.3 | 214 | 210.7 | 254.3 | 192.7 | 206.6
802 | 684 | 526.4 | 394.3 | 440.6 | 389.8 | 238.7 | 214.4 | 211.1 | 255.5 | 193.2 | 207.1
803 | 685 | 526.3 | 394.5 | 440.9 | 390.1 | 239 | 214.8 | 211.5 | 256.6 | 193.6 | 207.5
804 | 686 | 526.3 | 394.7 | 441.1 | 390.3 | 239.4 | 215.2 | 211.9 | 257.8 | 194 | 208
805 | 687 | 526.3 | 395 | 441.2 | 390.6 | 239.7 | 215.6 | 212.3 | 258.9 | 194.4 | 208.5
806 | 688 | 526.3 | 395.2 | 441.4 | 390.8 | 240.1 | 216 | 212.8 | 259.9 | 194.9 | 208.9
807 | 689 | 526.3 | 395.4 | 441.7 | 391 | 240.4 | 216.4 | 213.2 | 260.8 | 195.3 | 209.3
808 | 690 | 526.3 | 395.7 | 441.9 | 391.3 | 240.8 | 216.8 | 213.6 | 261.6 | 195.7 | 209.6
809 | 691 | 526.3 | 395.9 | 442.2 | 391.5 | 241.1 | 217.3 | 213.9 | 262.4 | 196.2 | 210
810 | 692 | 526.3 | 396.1 | 442.4 | 391.8 | 241.4 | 217.6 | 214.4 | 263 | 196.6 | 210.5
811 | 693 | 526.3 | 396.4 | 442.5 | 392 | 241.7 | 218 | 214.8 | 263.5 | 197 | 210.9
812 | 694 | 526.3 | 396.6 | 442.7 | 392.3 | 241.9 | 218.4 | 215.2 | 263.8 | 197.4 | 211.2
813 | 695 | 526.3 | 396.8 | 442.9 | 392.5 | 242.2 | 218.8 | 215.6 | 263.9 | 197.8 | 211.6
814 | 696 | 526.3 | 397.1 | 443.1 | 392.7 | 242.4 | 219.2 | 216 | 264.1 | 198.3 | 211.9
815 | 697 | 526.3 | 397.3 | 443.3 | 393 | 242.7 | 219.6 | 216.4 | 264.3 | 198.7 | 212.3
816 | 698 | 526.4 | 397.5 | 443.5 | 393.2 | 243 | 220 | 216.8 | 264.5 | 199.1 | 212.7
817 | 699 | 526.4 | 397.8 | 443.8 | 393.4 | 243.3 | 220.4 | 217.2 | 264.7 | 199.5 | 213
818 | 700 | 526.4 | 398 | 443.9 | 393.7 | 243.6 | 220.8 | 217.6 | 265 | 199.9 | 213.3
819 | 701 | 526.4 | 398.2 | 444.1 | 393.9 | 243.8 | 221.2 | 218 | 265.3 | 200.4 | 213.7
820 | 702 | 526.4 | 398.4 | 444.3 | 394.1 | 244.1 | 221.5 | 218.3 | 265.5 | 200.8 | 214.1
821 | 703 | 526.5 | 398.6 | 444.5 | 394.3 | 244.3 | 221.9 | 218.7 | 265.8 | 201.2 | 214.5
822 | 704 | 526.5 | 398.9 | 444.7 | 394.6 | 244.6 | 222.3 | 219.1 | 266.1 | 201.6 | 215
823 | 705 | 526.5 | 399.1 | 445 | 394.8 | 244.9 | 222.7 | 219.5 | 266.4 | 202 | 215.5
824 | 706 | 526.5 | 399.3 | 445.2 | 395.1 | 245.2 | 223 | 219.9 | 266.7 | 202.4 | 216
825 | 707 | 526.5 | 399.5 | 445.4 | 395.3 | 245.4 | 223.4 | 220.3 | 266.9 | 202.8 | 216.5
826 | 708 | 526.4 | 399.7 | 445.6 | 395.5 | 245.7 | 223.8 | 220.7 | 267.3 | 203.2 | 217.1
827 | 709 | 526.4 | 400 | 445.8 | 395.7 | 246 | 224.2 | 221.1 | 267.7 | 203.7 | 217.6
828 | 710 | 526.4 | 400.2 | 446 | 396 | 246.3 | 224.5 | 221.5 | 268 | 204.1 | 218.2
829 | 711 | 526.4 | 400.4 | 446.2 | 396.2 | 246.6 | 224.9 | 221.9 | 268.3 | 204.5 | 218.7
830 | 712 | 526.4 | 400.6 | 446.4 | 396.4 | 246.9 | 225.3 | 222.3 | 268.6 | 204.9 | 219.2
831 | 713 | 526.4 | 400.8 | 446.6 | 396.6 | 247.3 | 225.6 | 222.6 | 268.8 | 205.3 | 219.7
832 | 714 | 526.4 | 401 | 446.7 | 396.9 | 247.6 | 226 | 223 | 269.1 | 205.7 | 220.1
833 | 715 | 526.4 | 401.3 | 446.9 | 397.1 | 247.9 | 226.4 | 223.4 | 269.4 | 206.1 | 220.6
834 | 716 | 526.4 | 401.5 | 447.1 | 397.3 | 248.3 | 226.7 | 223.8 | 269.7 | 206.5 | 221
835 | 717 | 526.3 | 401.7 | 447.2 | 397.6 | 248.6 | 227.1 | 224.2 | 270 | 206.9 | 221.4
836 | 718 | 526.4 | 401.9 | 447.3 | 397.8 | 248.9 | 227.5 | 224.6 | 270.3 | 207.2 | 221.7
837 | 719 | 526.3 | 402.1 | 447.5 | 398 | 249.1 | 227.8 | 224.9 | 270.4 | 207.7 | 222
838 | 720 | 526.3 | 402.3 | 447.8 | 398.2 | 249.4 | 228.2 | 225.3 | 270.6 | 208.1 | 222.4
839 | 721 | 526.3 | 402.5 | 448.1 | 398.5 | 249.7 | 228.5 | 225.7 | 270.6 | 208.4 | 222.7
840 | 722 | 526.3 | 402.7 | 448.2 | 398.7 | 250.1 | 228.9 | 226 | 270.7 | 208.8 | 223
841 | 723 | 526.2 | 402.9 | 448.4 | 398.9 | 250.5 | 229.2 | 226.4 | 270.8 | 209.2 | 223.4
842 | 724 | 526.2 | 403.2 | 448.6 | 399.1 | 250.9 | 229.6 | 226.8 | 270.9 | 209.6 | 223.7
843 | 725 | 526.2 | 403.4 | 448.8 | 399.3 | 251.3 | 230 | 227.2 | 271 | 210 | 224
844 | 726 | 526.2 | 403.6 | 449 | 399.6 | 251.7 | 230.3 | 227.5 | 271.1 | 210.4 | 224.3
845 | 727 | 526.2 | 403.8 | 449.2 | 399.8 | 252 | 230.7 | 227.9 | 271.2 | 210.8 | 224.7
846 | 728 | 526.2 | 404 | 449.3 | 400 | 252.4 | 231 | 228.3 | 271.3 | 211.2 | 225.2
847 | 729 | 526.1 | 404.2 | 449.5 | 400.2 | 252.7 | 231.4 | 228.6 | 271.3 | 211.5 | 225.6
848 | 730 | 526.1 | 404.4 | 449.7 | 400.4 | 253.1 | 231.7 | 229 | 271.5 | 211.9 | 226.1
849 | 731 | 526 | 404.6 | 449.8 | 400.6 | 253.4 | 232.1 | 229.4 | 271.6 | 212.3 | 226.5
850 | 732 | 526 | 404.8 | 450 | 400.8 | 253.8 | 232.4 | 229.7 | 271.8 | 212.7 | 226.9
851 | 733 | 526 | 405 | 450.2 | 401.1 | 254.1 | 232.8 | 230.1 | 272.1 | 213 | 227.4
852 | 734 | 526 | 405.2 | 450.4 | 401.3 | 254.5 | 233.1 | 230.5 | 272.6 | 213.4 | 227.8
853 | 735 | 526 | 405.4 | 450.5 | 401.5 | 254.8 | 233.5 | 230.8 | 273.1 | 213.8 | 228.2
854 | 736 | 526 | 405.6 | 450.7 | 401.7 | 255.2 | 233.8 | 231.2 | 273.6 | 214.2 | 228.6
855 | 737 | 525.9 | 405.8 | 450.9 | 401.9 | 255.6 | 234.2 | 231.6 | 274 | 214.5 | 229
856 | 738 | 526 | 406 | 451.1 | 402.1 | 255.9 | 234.5 | 231.9 | 274.4 | 214.9 | 229.5
857 | 739 | 526 | 406.2 | 451.2 | 402.3 | 256.2 | 234.9 | 232.3 | 274.7 | 215.3 | 229.9
858 | 740 | 526 | 406.4 | 451.4 | 402.6 | 256.3 | 235.2 | 232.6 | 275 | 215.7 | 230.4
859 | 741 | 526 | 406.6 | 451.6 | 402.8 | 256.3 | 235.6 | 233 | 275.2 | 216 | 230.8
860 | 742 | 526 | 406.8 | 451.8 | 403 | 256.3 | 235.9 | 233.3 | 275.6 | 216.4 | 231.3
861 | 743 | 526.1 | 407 | 452 | 403.2 | 256.3 | 236.3 | 233.7 | 276 | 216.8 | 231.7
862 | 744 | 526.1 | 407.2 | 452.1 | 403.4 | 256.4 | 236.6 | 234 | 276.3 | 217.1 | 232.2
863 | 745 | 526.1 | 407.4 | 452.3 | 403.6 | 256.6 | 237 | 234.4 | 276.6 | 217.5 | 232.5
864 | 746 | 526.2 | 407.6 | 452.5 | 403.8 | 256.9 | 237.3 | 234.7 | 277.2 | 217.9 | 233
865 | 747 | 526.1 | 407.8 | 452.7 | 404 | 257.2 | 237.7 | 235 | 278 | 218.2 | 233.4
866 | 748 | 526.2 | 408 | 452.9 | 404.2 | 257.6 | 238 | 235.4 | 278.9 | 218.6 | 233.9
867 | 749 | 526.2 | 408.2 | 453 | 404.4 | 258 | 238.4 | 235.7 | 279.7 | 219 | 234.3
868 | 750 | 526.2 | 408.4 | 453.2 | 404.7 | 258.3 | 238.7 | 236 | 280.3 | 219.3 | 234.7
869 | 751 | 526.2 | 408.6 | 453.3 | 404.9 | 258.7 | 239 | 236.4 | 280.7 | 219.7 | 235.2
870 | 752 | 526.2 | 408.8 | 453.5 | 405.1 | 259.2 | 239.4 | 236.7 | 281.1 | 220.1 | 235.6
871 | 753 | 526.2 | 409 | 453.6 | 405.3 | 259.5 | 239.7 | 237 | 281.5 | 220.5 | 236.1
872 | 754 | 526.2 | 409.2 | 453.8 | 405.5 | 259.9 | 240 | 237.4 | 281.9 | 220.8 | 236.5
873 | 755 | 526.2 | 409.4 | 454 | 405.7 | 260.1 | 240.4 | 237.7 | 282.3 | 221.2 | 237
874 | 756 | 526.3 | 409.6 | 454.2 | 405.9 | 260.2 | 240.7 | 238 | 282.7 | 221.6 | 237.4
875 | 757 | 526.3 | 409.8 | 454.3 | 406.1 | 260.4 | 241 | 238.3 | 283.2 | 221.9 | 237.9
876 | 758 | 526.3 | 410 | 454.5 | 406.3 | 260.6 | 241.3 | 238.7 | 283.6 | 222.3 | 238.4
877 | 759 | 526.2 | 410.2 | 454.7 | 406.5 | 260.7 | 241.6 | 239 | 283.9 | 222.6 | 238.9
878 | 760 | 526.2 | 410.4 | 454.8 | 406.7 | 261 | 242 | 239.3 | 284.2 | 223 | 239.4
879 | 761 | 526.2 | 410.6 | 455 | 406.9 | 261.2 | 242.3 | 239.6 | 284.6 | 223.3 | 240.2
880 | 762 | 526.1 | 410.7 | 455.2 | 407.1 | 261.3 | 242.6 | 240 | 284.8 | 223.7 | 240.7
881 | 763 | 526.1 | 410.9 | 455.4 | 407.3 | 261.5 | 242.9 | 240.3 | 284.9 | 224.1 | 241.3
882 | 764 | 526.1 | 411.1 | 455.6 | 407.5 | 261.6 | 243.3 | 240.6 | 285 | 224.4 | 241.8
883 | 765 | 526.1 | 411.3 | 455.8 | 407.7 | 261.9 | 243.6 | 240.9 | 285.1 | 224.8 | 242.2
884 | 766 | 526.1 | 411.5 | 455.9 | 407.9 | 262.1 | 243.9 | 241.3 | 285.5 | 225.1 | 242.6
885 | 767 | 526.1 | 411.7 | 456.1 | 408.1 | 262.3 | 244.2 | 241.6 | 286.2 | 225.5 | 242.9
886 | 768 | 526 | 411.9 | 456.3 | 408.3 | 262.6 | 244.5 | 241.9 | 286.8 | 225.8 | 243.4
887 | 769 | 526 | 412.1 | 456.4 | 408.5 | 262.9 | 244.8 | 242.2 | 287.3 | 226.2 | 243.8
888 | 770 | 526 | 412.3 | 456.5 | 408.7 | 263.2 | 245.2 | 242.5 | 287.7 | 226.5 | 244.3
889 | 771 | 526 | 412.5 | 456.6 | 408.9 | 263.4 | 245.5 | 242.8 | 288.1 | 226.9 | 245
890 | 772 | 525.9 | 412.7 | 456.8 | 409 | 263.6 | 245.8 | 243.1 | 288.6 | 227.2 | 245.6
891 | 773 | 525.9 | 412.8 | 457 | 409.2 | 263.7 | 246.1 | 243.5 | 289 | 227.6 | 246.1
892 | 774 | 525.9 | 413 | 457.2 | 409.4 | 264 | 246.4 | 243.8 | 289.5 | 227.9 | 246.9
893 | 775 | 525.9 | 413.2 | 457.4 | 409.6 | 264.2 | 246.7 | 244.1 | 289.9 | 228.3 | 247.2
894 | 776 | 525.9 | 413.4 | 457.5 | 409.8 | 264.4 | 247 | 244.4 | 290.4 | 228.6 | 247.5
895 | 777 | 525.8 | 413.6 | 457.6 | 410 | 264.6 | 247.3 | 244.7 | 290.8 | 228.9 | 248
896 | 778 | 525.8 | 413.8 | 457.7 | 410.2 | 264.9 | 247.6 | 245 | 291.1 | 229.3 | 248.5
897 | 779 | 525.9 | 414 | 457.9 | 410.4 | 265.1 | 247.9 | 245.3 | 291.4 | 229.6 | 249
898 | 780 | 525.9 | 414.2 | 458 | 410.6 | 265.4 | 248.2 | 245.7 | 291.6 | 230 | 249.3
899 | 781 | 525.9 | 414.3 | 458.2 | 410.8 | 265.7 | 248.5 | 246 | 291.8 | 230.4 | 249.7
900 | 782 | 525.8 | 414.5 | 458.3 | 411 | 266 | 248.9 | 246.3 | 292 | 230.8 | 250.1
901 | 783 | 525.8 | 414.7 | 458.5 | 411.2 | 266.3 | 249.2 | 246.6 | 292.1 | 231.2 | 250.6
902 | 784 | 525.8 | 414.9 | 458.6 | 411.4 | 266.5 | 249.5 | 246.9 | 292.3 | 231.6 | 251
903 | 785 | 525.9 | 415.1 | 458.8 | 411.6 | 266.7 | 249.7 | 247.2 | 292.4 | 232 | 251.3
904 | 786 | 525.9 | 415.3 | 459 | 411.8 | 267 | 250.1 | 247.5 | 292.4 | 232.4 | 251.6
905 | 787 | 525.9 | 415.5 | 459.1 | 412 | 267.3 | 250.4 | 247.8 | 292.1 | 232.9 | 252
906 | 788 | 525.9 | 415.6 | 459.3 | 412.2 | 267.5 | 250.7 | 248.1 | 291.9 | 233.3 | 252.4
907 | 789 | 525.9 | 415.8 | 459.4 | 412.4 | 267.7 | 251 | 248.4 | 291.8 | 233.7 | 252.8
908 | 790 | 525.8 | 416 | 459.6 | 412.6 | 267.9 | 251.3 | 248.7 | 292 | 234.1 | 253.2
909 | 791 | 525.8 | 416.2 | 459.8 | 412.8 | 268.2 | 251.6 | 249 | 292.2 | 234.5 | 253.6
910 | 792 | 525.8 | 416.4 | 459.9 | 412.9 | 268.6 | 251.9 | 249.3 | 292.3 | 234.8 | 253.9
911 | 793 | 525.8 | 416.6 | 460 | 413.1 | 268.9 | 252.2 | 249.6 | 292.6 | 235.2 | 254.3
912 | 794 | 525.8 | 416.7 | 460.1 | 413.3 | 269.1 | 252.5 | 249.9 | 292.8 | 235.6 | 254.6
913 | 795 | 525.8 | 416.9 | 460.3 | 413.5 | 269.3 | 252.8 | 250.2 | 292.9 | 236 | 255
914 | 796 | 525.8 | 417.1 | 460.4 | 413.7 | 269.6 | 253.2 | 250.5 | 293.1 | 236.4 | 255.4
915 | 797 | 525.8 | 417.3 | 460.6 | 413.9 | 269.9 | 253.5 | 250.8 | 293.3 | 236.8 | 255.8
916 | 798 | 525.8 | 417.5 | 460.7 | 414.1 | 270.2 | 253.8 | 251.1 | 293.6 | 237.1 | 256.1
917 | 799 | 525.8 | 417.6 | 460.8 | 414.3 | 270.4 | 254.1 | 251.4 | 293.9 | 237.5 | 256.4
918 | 800 | 525.8 | 417.8 | 461 | 414.5 | 270.5 | 254.4 | 251.7 | 294.1 | 237.9 | 256.8
919 | 801 | 525.8 | 418 | 461.1 | 414.7 | 270.8 | 254.7 | 252 | 294.4 | 238.2 | 257.1
920 | 802 | 525.8 | 418.2 | 461.3 | 414.9 | 271 | 255 | 252.3 | 294.7 | 238.6 | 257.5
921 | 803 | 525.8 | 418.4 | 461.4 | 415.1 | 271.2 | 255.3 | 252.6 | 294.8 | 239 | 257.9
922 | 804 | 525.8 | 418.5 | 461.6 | 415.3 | 271.5 | 255.6 | 252.9 | 295.1 | 239.3 | 258.3
923 | 805 | 525.8 | 418.7 | 461.7 | 415.5 | 271.7 | 255.9 | 253.2 | 295.2 | 239.7 | 258.8
924 | 806 | 525.8 | 418.9 | 461.9 | 415.7 | 272 | 256.2 | 253.5 | 295.4 | 240.1 | 259.3
925 | 807 | 525.8 | 419.1 | 462 | 415.9 | 272.2 | 256.5 | 253.8 | 295.6 | 240.4 | 259.7
926 | 808 | 525.8 | 419.3 | 462.1 | 416.1 | 272.5 | 256.9 | 254.1 | 295.8 | 240.8 | 260
927 | 809 | 525.8 | 419.4 | 462.3 | 416.3 | 272.8 | 257.2 | 254.4 | 296 | 241.1 | 260.3
928 | 810 | 525.8 | 419.6 | 462.4 | 416.5 | 273.1 | 257.5 | 254.7 | 296.3 | 241.5 | 260.8
929 | 811 | 525.8 | 419.8 | 462.6 | 416.6 | 273.4 | 257.8 | 255 | 296.5 | 241.8 | 261.1
930 | 812 | 525.8 | 419.9 | 462.7 | 416.8 | 273.7 | 258 | 255.3 | 296.8 | 242.2 | 261.5
931 | 813 | 525.8 | 420.1 | 462.8 | 417 | 274 | 258.3 | 255.6 | 297 | 242.5 | 261.9
932 | 814 | 525.9 | 420.3 | 463 | 417.2 | 274.3 | 258.6 | 255.8 | 297.2 | 242.8 | 262.2
933 | 815 | 525.9 | 420.5 | 463.1 | 417.4 | 274.6 | 258.9 | 256.1 | 297.6 | 243.1 | 262.5
934 | 816 | 525.9 | 420.6 | 463.2 | 417.6 | 275 | 259.2 | 256.4 | 298 | 243.5 | 263
935 | 817 | 526 | 420.8 | 463.4 | 417.8 | 275.2 | 259.5 | 256.7 | 298.3 | 243.8 | 263.4
936 | 818 | 526 | 421 | 463.5 | 418 | 275.4 | 259.8 | 257 | 298.5 | 244.1 | 263.7
937 | 819 | 526 | 421.2 | 463.6 | 418.2 | 275.7 | 260.1 | 257.3 | 298.9 | 244.5 | 264.2
938 | 820 | 526 | 421.3 | 463.8 | 418.4 | 276 | 260.4 | 257.6 | 299.2 | 244.8 | 264.5
939 | 821 | 526 | 421.5 | 463.9 | 418.6 | 276.3 | 260.7 | 257.9 | 299.6 | 245.1 | 264.8
940 | 822 | 526 | 421.7 | 464 | 418.7 | 276.5 | 261 | 258.2 | 299.9 | 245.4 | 265.1
941 | 823 | 526 | 421.8 | 464.2 | 418.9 | 276.7 | 261.3 | 258.5 | 300.3 | 245.8 | 265.6
942 | 824 | 526 | 422 | 464.3 | 419.1 | 276.9 | 261.6 | 258.8 | 300.6 | 246.1 | 266
943 | 825 | 526 | 422.2 | 464.4 | 419.3 | 277.2 | 261.8 | 259.1 | 300.8 | 246.4 | 266.4
944 | 826 | 526 | 422.4 | 464.6 | 419.5 | 277.4 | 262.1 | 259.4 | 301.1 | 246.7 | 266.7
945 | 827 | 526 | 422.5 | 464.7 | 419.7 | 277.6 | 262.4 | 259.6 | 301.4 | 247 | 267.1
946 | 828 | 526 | 422.7 | 464.9 | 419.8 | 277.8 | 262.7 | 259.9 | 301.7 | 247.4 | 267.5
947 | 829 | 526 | 422.9 | 465 | 420 | 278.1 | 263 | 260.2 | 302 | 247.7 | 267.9
948 | 830 | 525.9 | 423 | 465.1 | 420.2 | 278.3 | 263.3 | 260.5 | 302.3 | 248 | 268.4
949 | 831 | 525.9 | 423.2 | 465.2 | 420.4 | 278.5 | 263.6 | 260.8 | 302.7 | 248.3 | 268.7
950 | 832 | 525.8 | 423.4 | 465.4 | 420.6 | 278.8 | 263.8 | 261.1 | 302.9 | 248.6 | 269.1
951 | 833 | 525.8 | 423.5 | 465.5 | 420.8 | 279 | 264.1 | 261.4 | 303.3 | 248.9 | 269.5
952 | 834 | 525.8 | 423.7 | 465.6 | 420.9 | 279.2 | 264.4 | 261.7 | 303.7 | 249.1 | 269.9
953 | 835 | 525.8 | 423.9 | 465.8 | 421.1 | 279.5 | 264.7 | 262 | 304 | 249.4 | 270.3
954 | 836 | 525.8 | 424 | 465.9 | 421.3 | 279.7 | 265 | 262.3 | 304.3 | 249.7 | 270.7
955 | 837 | 525.8 | 424.2 | 466 | 421.5 | 280 | 265.3 | 262.6 | 304.5 | 250 | 271.1
956 | 838 | 525.8 | 424.3 | 466.2 | 421.7 | 280.2 | 265.6 | 262.9 | 304.8 | 250.3 | 271.5
957 | 839 | 525.8 | 424.5 | 466.3 | 421.8 | 280.2 | 265.9 | 263.2 | 305.1 | 250.6 | 271.9
958 | 840 | 525.8 | 424.7 | 466.4 | 422 | 280.2 | 266.2 | 263.5 | 305.4 | 250.9 | 272.3
959 | 841 | 525.8 | 424.8 | 466.5 | 422.2 | 280.2 | 266.5 | 263.8 | 305.8 | 251.2 | 272.6
960 | 842 | 525.8 | 425 | 466.7 | 422.4 | 280.4 | 266.8 | 264.1 | 306.2 | 251.4 | 273
961 | 843 | 525.7 | 425.2 | 466.8 | 422.5 | 280.5 | 267.1 | 264.4 | 306.5 | 251.7 | 273.3
962 | 844 | 525.7 | 425.3 | 466.9 | 422.7 | 280.7 | 267.3 | 264.7 | 306.8 | 252 | 273.6
963 | 845 | 525.7 | 425.5 | 467 | 422.9 | 280.8 | 267.6 | 265.1 | 307.1 | 252.3 | 274
964 | 846 | 525.7 | 425.6 | 467.2 | 423.1 | 281 | 268 | 265.4 | 307.4 | 252.6 | 274.4
965 | 847 | 525.7 | 425.8 | 467.3 | 423.2 | 281.1 | 268.3 | 265.7 | 307.7 | 252.8 | 274.7
966 | 848 | 525.7 | 425.9 | 467.4 | 423.4 | 281.3 | 268.6 | 266 | 308.1 | 253.1 | 275.1
967 | 849 | 525.7 | 426.1 | 467.5 | 423.5 | 281.4 | 268.9 | 266.3 | 308.3 | 253.4 | 275.5
968 | 850 | 525.7 | 426.3 | 467.6 | 423.7 | 281.6 | 269.2 | 266.6 | 308.7 | 253.6 | 275.9
969 | 851 | 525.7 | 426.4 | 467.7 | 423.9 | 281.8 | 269.5 | 266.9 | 309.1 | 253.9 | 276.2
970 | 852 | 525.7 | 426.6 | 467.9 | 424.1 | 282.1 | 269.8 | 267.2 | 309.3 | 254.2 | 276.5
971 | 853 | 525.7 | 426.7 | 468 | 424.2 | 282.4 | 270.2 | 267.5 | 309.6 | 254.4 | 276.8
972 | 854 | 525.7 | 426.8 | 468.1 | 424.4 | 282.7 | 270.5 | 267.8 | 310.1 | 254.7 | 277.2
973 | 855 | 525.7 | 427 | 468.3 | 424.5 | 283 | 270.8 | 268.2 | 310.6 | 254.9 | 277.6
974 | 856 | 525.6 | 427.2 | 468.4 | 424.7 | 283.2 | 271.1 | 268.5 | 311 | 255.2 | 278
975 | 857 | 525.6 | 427.3 | 468.5 | 424.9 | 283.5 | 271.4 | 268.8 | 311.3 | 255.4 | 278.4
976 | 858 | 525.6 | 427.5 | 468.6 | 425 | 283.8 | 271.7 | 269.1 | 311.7 | 255.7 | 278.8
977 | 859 | 525.6 | 427.6 | 468.7 | 425.2 | 284 | 272 | 269.5 | 312.2 | 256 | 279.2
978 | 860 | 525.5 | 427.8 | 468.8 | 425.4 | 284.2 | 272.3 | 269.8 | 312.5 | 256.2 | 279.5
979 | 861 | 525.6 | 427.9 | 468.9 | 425.5 | 284.5 | 272.6 | 270.1 | 312.8 | 256.5 | 279.9
980 | 862 | 525.6 | 428.1 | 469 | 425.7 | 284.7 | 272.9 | 270.4 | 313.2 | 256.7 | 280.3
981 | 863 | 525.6 | 428.2 | 469.1 | 425.9 | 285 | 273.2 | 270.7 | 313.7 | 257 | 280.7
982 | 864 | 525.6 | 428.4 | 469.3 | 426 | 285.3 | 273.5 | 271 | 314.1 | 257.2 | 281.1
983 | 865 | 525.6 | 428.5 | 469.4 | 426.2 | 285.5 | 273.8 | 271.3 | 314.4 | 257.5 | 281.6
984 | 866 | 525.7 | 428.7 | 469.5 | 426.3 | 285.7 | 274.1 | 271.6 | 314.8 | 257.7 | 282
985 | 867 | 525.7 | 428.8 | 469.6 | 426.5 | 286 | 274.5 | 271.9 | 315 | 258 | 282.3
986 | 868 | 525.7 | 429 | 469.8 | 426.7 | 286.3 | 274.8 | 272.2 | 315.4 | 258.2 | 282.7
987 | 869 | 525.7 | 429.1 | 469.9 | 426.8 | 286.8 | 275.1 | 272.5 | 315.7 | 258.5 | 283.1
988 | 870 | 525.7 | 429.3 | 470 | 427 | 287 | 275.4 | 272.8 | 316 | 258.7 | 283.4
989 | 871 | 525.6 | 429.4 | 470.1 | 427.1 | 287.2 | 275.7 | 273.1 | 316.5 | 259 | 283.7
990 | 872 | 525.6 | 429.5 | 470.2 | 427.3 | 287.5 | 276 | 273.4 | 316.8 | 259.2 | 284.1
991 | 873 | 525.6 | 429.7 | 470.3 | 427.5 | 287.8 | 276.3 | 273.7 | 317.2 | 259.4 | 284.4
992 | 874 | 525.6 | 429.8 | 470.4 | 427.6 | 288 | 276.7 | 274 | 317.5 | 259.7 | 284.8
993 | 875 | 525.6 | 430 | 470.5 | 427.8 | 288.2 | 277 | 274.3 | 317.9 | 259.9 | 285.1
994 | 876 | 525.6 | 430.1 | 470.7 | 427.9 | 288.5 | 277.3 | 274.6 | 318.3 | 260.2 | 285.5
995 | 877 | 525.5 | 430.3 | 470.8 | 428.1 | 288.8 | 277.6 | 274.9 | 318.7 | 260.4 | 285.9
996 | 878 | 525.5 | 430.4 | 470.9 | 428.2 | 289.1 | 277.9 | 275.2 | 319.1 | 260.6 | 286.2
997 | 879 | 525.5 | 430.5 | 471 | 428.4 | 289.4 | 278.3 | 275.5 | 319.4 | 260.9 | 286.6
998 | 880 | 525.5 | 430.7 | 471.1 | 428.5 | 289.7 | 278.6 | 275.8 | 319.7 | 261.1 | 286.9
999 | 881 | 525.5 | 430.8 | 471.2 | 428.7 | 290 | 279 | 276.1 | 320.1 | 261.4 | 287.3
1000 | 882 | 525.5 | 431 | 471.3 | 428.8 | 290.3 | 279.3 | 276.5 | 320.5 | 261.6 | 287.6
1001 | 883 | 525.5 | 431.1 | 471.4 | 429 | 290.6 | 279.6 | 276.8 | 321 | 261.8 | 288
1002 | 884 | 525.5 | 431.2 | 471.5 | 429.1 | 290.9 | 280 | 277.1 | 321.3 | 262.1 | 288.4
1003 | 885 | 525.5 | 431.4 | 471.6 | 429.3 | 291.2 | 280.3 | 277.4 | 321.7 | 262.3 | 288.9
1004 | 886 | 525.5 | 431.5 | 471.7 | 429.4 | 291.5 | 280.7 | 277.7 | 322.2 | 262.6 | 289.3
1005 | 887 | 525.4 | 431.7 | 471.8 | 429.6 | 291.8 | 281 | 278 | 322.8 | 262.8 | 289.7
1006 | 888 | 525.4 | 431.8 | 471.9 | 429.7 | 292.1 | 281.3 | 278.4 | 323.1 | 263 | 290.1
1007 | 889 | 525.4 | 431.9 | 472 | 429.9 | 292.4 | 281.7 | 278.7 | 323.5 | 263.3 | 290.4
1008 | 890 | 525.4 | 432.1 | 472.1 | 430 | 292.7 | 282 | 279 | 323.8 | 263.5 | 290.9
1009 | 891 | 525.4 | 432.2 | 472.3 | 430.2 | 293 | 282.3 | 279.3 | 324.1 | 263.8 | 291.3
1010 | 892 | 525.4 | 432.4 | 472.4 | 430.3 | 293.3 | 282.7 | 279.6 | 324.4 | 264 | 291.7
1011 | 893 | 525.4 | 432.5 | 472.4 | 430.5 | 293.7 | 283 | 279.9 | 324.8 | 264.2 | 292.1
1012 | 894 | 525.4 | 432.6 | 472.5 | 430.6 | 294 | 283.3 | 280.2 | 325.2 | 264.5 | 292.5
1013 | 895 | 525.4 | 432.8 | 472.6 | 430.8 | 294.3 | 283.6 | 280.5 | 325.7 | 264.7 | 292.9
1014 | 896 | 525.4 | 432.9 | 472.7 | 430.9 | 294.5 | 284 | 280.8 | 326 | 265 | 293.2
1015 | 897 | 525.4 | 433 | 472.8 | 431 | 294.9 | 284.3 | 281.2 | 326.3 | 265.2 | 293.6
1016 | 898 | 525.4 | 433.2 | 472.9 | 431.2 | 295.1 | 284.7 | 281.5 | 326.7 | 265.5 | 294.1
1017 | 899 | 525.4 | 433.3 | 473.1 | 431.3 | 295.4 | 285 | 281.8 | 327.2 | 265.7 | 294.4
1018 | 900 | 525.4 | 433.4 | 473.1 | 431.5 | 295.7 | 285.3 | 282.1 | 327.5 | 265.9 | 294.8
1019 | 901 | 525.5 | 433.6 | 473.2 | 431.6 | 296 | 285.7 | 282.5 | 327.9 | 266.2 | 295.2
1020 | 902 | 525.5 | 433.7 | 473.3 | 431.8 | 296.3 | 286 | 282.8 | 328.3 | 266.4 | 295.6
1021 | 903 | 525.5 | 433.8 | 473.4 | 431.9 | 296.6 | 286.3 | 283.1 | 328.6 | 266.7 | 296
1022 | 904 | 525.5 | 434 | 473.5 | 432 | 296.9 | 286.6 | 283.4 | 328.9 | 266.9 | 296.4
1023 | 905 | 525.5 | 434.1 | 473.6 | 432.2 | 297.3 | 286.9 | 283.7 | 329.3 | 267.2 | 296.7
1024 | 906 | 525.5 | 434.2 | 473.7 | 432.3 | 297.6 | 287.3 | 284 | 329.7 | 267.4 | 297.1
1025 | 907 | 525.5 | 434.3 | 473.8 | 432.5 | 297.9 | 287.6 | 284.3 | 330 | 267.7 | 297.4
1026 | 908 | 525.5 | 434.5 | 473.9 | 432.6 | 298.2 | 287.9 | 284.7 | 330.4 | 267.9 | 297.7
1027 | 909 | 525.5 | 434.6 | 474 | 432.8 | 298.6 | 288.2 | 285 | 330.8 | 268.2 | 298.1
1028 | 910 | 525.5 | 434.7 | 474.1 | 432.9 | 298.9 | 288.5 | 285.3 | 331.1 | 268.4 | 298.5
1029 | 911 | 525.5 | 434.9 | 474.2 | 433 | 299.3 | 288.8 | 285.6 | 331.4 | 268.7 | 298.9
1030 | 912 | 525.5 | 435 | 474.3 | 433.2 | 299.6 | 289.1 | 285.9 | 331.6 | 268.9 | 299.2
1031 | 913 | 525.5 | 435.1 | 474.4 | 433.3 | 300 | 289.5 | 286.2 | 332 | 269.2 | 299.6
1032 | 914 | 525.5 | 435.2 | 474.5 | 433.5 | 300.2 | 289.8 | 286.6 | 332.3 | 269.4 | 300
1033 | 915 | 525.5 | 435.4 | 474.6 | 433.6 | 300.5 | 290.1 | 286.9 | 332.7 | 269.6 | 300.3
1034 | 916 | 525.5 | 435.5 | 474.7 | 433.7 | 300.8 | 290.4 | 287.2 | 333 | 269.9 | 300.6
1035 | 917 | 525.4 | 435.6 | 474.8 | 433.9 | 301.2 | 290.7 | 287.5 | 333.3 | 270.1 | 301
1036 | 918 | 525.4 | 435.7 | 474.9 | 434 | 301.5 | 291.1 | 287.8 | 333.7 | 270.4 | 301.3
1037 | 919 | 525.4 | 435.8 | 475 | 434.1 | 301.8 | 291.4 | 288.1 | 334 | 270.6 | 301.7
1038 | 920 | 525.4 | 436 | 475.1 | 434.3 | 302.1 | 291.7 | 288.5 | 334.4 | 270.9 | 302
1039 | 921 | 525.4 | 436.1 | 475.2 | 434.4 | 302.4 | 292.1 | 288.8 | 334.8 | 271.1 | 302.4
1040 | 922 | 525.3 | 436.2 | 475.3 | 434.6 | 302.6 | 292.4 | 289.1 | 335.2 | 271.3 | 302.7
1041 | 923 | 525.3 | 436.3 | 475.4 | 434.7 | 302.9 | 292.7 | 289.4 | 335.6 | 271.6 | 303.1
1042 | 924 | 525.3 | 436.4 | 475.4 | 434.8 | 303.1 | 293 | 289.7 | 336.1 | 271.8 | 303.4
1043 | 925 | 525.3 | 436.6 | 475.5 | 435 | 303.4 | 293.3 | 290 | 336.5 | 272.1 | 303.7
1044 | 926 | 525.3 | 436.7 | 475.6 | 435.1 | 303.7 | 293.6 | 290.3 | 336.8 | 272.3 | 304
1045 | 927 | 525.3 | 436.8 | 475.7 | 435.2 | 304 | 293.9 | 290.6 | 337.2 | 272.6 | 304.4
1046 | 928 | 525.3 | 436.9 | 475.8 | 435.4 | 304.3 | 294.2 | 291 | 337.6 | 272.8 | 304.7
1047 | 929 | 525.3 | 437.1 | 475.9 | 435.5 | 304.6 | 294.6 | 291.3 | 337.9 | 273 | 305
1048 | 930 | 525.3 | 437.2 | 476 | 435.6 | 304.9 | 294.9 | 291.6 | 338.3 | 273.3 | 305.3
1049 | 931 | 525.3 | 437.3 | 476.1 | 435.7 | 305.1 | 295.2 | 291.9 | 338.6 | 273.5 | 305.7
1050 | 932 | 525.3 | 437.4 | 476.1 | 435.9 | 305.4 | 295.5 | 292.3 | 339 | 273.8 | 306
1051 | 933 | 525.3 | 437.5 | 476.2 | 436 | 305.7 | 295.8 | 292.6 | 339.4 | 274 | 306.3
1052 | 934 | 525.3 | 437.7 | 476.3 | 436.1 | 305.9 | 296.1 | 292.9 | 339.8 | 274.2 | 306.6
1053 | 935 | 525.3 | 437.8 | 476.4 | 436.3 | 306.2 | 296.4 | 293.2 | 340.1 | 274.5 | 306.9
1054 | 936 | 525.3 | 437.9 | 476.5 | 436.4 | 306.5 | 296.7 | 293.6 | 340.4 | 274.7 | 307.2
1055 | 937 | 525.4 | 438 | 476.6 | 436.5 | 306.8 | 297 | 293.9 | 340.6 | 275 | 307.5
1056 | 938 | 525.4 | 438.1 | 476.7 | 436.6 | 307 | 297.3 | 294.2 | 340.9 | 275.2 | 307.8
1057 | 939 | 525.4 | 438.3 | 476.8 | 436.8 | 307.4 | 297.6 | 294.6 | 341.1 | 275.4 | 308.1
1058 | 940 | 525.4 | 438.4 | 476.8 | 436.9 | 307.7 | 297.9 | 294.9 | 341.4 | 275.7 | 308.4
1059 | 941 | 525.3 | 438.5 | 477 | 437 | 308.1 | 298.3 | 295.2 | 341.8 | 275.9 | 308.7
1060 | 942 | 525.3 | 438.6 | 477 | 437.2 | 308.4 | 298.6 | 295.5 | 342 | 276.2 | 309
1061 | 943 | 525.3 | 438.7 | 477.1 | 437.3 | 308.9 | 298.9 | 295.9 | 342.5 | 276.4 | 309.2
1062 | 944 | 525.3 | 438.8 | 477.3 | 437.4 | 309.3 | 299.2 | 296.2 | 342.8 | 276.7 | 309.5
1063 | 945 | 525.2 | 439 | 477.4 | 437.5 | 309.7 | 299.5 | 296.5 | 343.1 | 276.9 | 309.8
1064 | 946 | 525.2 | 439.1 | 477.5 | 437.7 | 310.1 | 299.8 | 296.8 | 343.4 | 277.2 | 310.1
1065 | 947 | 525.2 | 439.2 | 477.5 | 437.8 | 310.6 | 300.1 | 297.1 | 343.7 | 277.4 | 310.3
1066 | 948 | 525.2 | 439.3 | 477.6 | 437.9 | 311 | 300.4 | 297.4 | 344 | 277.6 | 310.6
1067 | 949 | 525.2 | 439.4 | 477.7 | 438 | 311.4 | 300.7 | 297.8 | 344.4 | 277.9 | 310.9
1068 | 950 | 525.2 | 439.5 | 477.8 | 438.2 | 311.8 | 301.1 | 298.1 | 344.8 | 278.1 | 311.2
1069 | 951 | 525.2 | 439.6 | 477.8 | 438.3 | 312.2 | 301.4 | 298.4 | 345.2 | 278.4 | 311.5
1070 | 952 | 525.1 | 439.8 | 477.9 | 438.4 | 312.6 | 301.7 | 298.7 | 345.7 | 278.6 | 311.7
1071 | 953 | 525.1 | 439.9 | 478 | 438.5 | 312.9 | 302.1 | 299 | 346 | 278.9 | 312
1072 | 954 | 525.1 | 440 | 478.1 | 438.6 | 313.3 | 302.4 | 299.3 | 346.4 | 279.1 | 312.3
1073 | 955 | 525.1 | 440.1 | 478.2 | 438.8 | 313.7 | 302.7 | 299.7 | 346.7 | 279.3 | 312.5
1074 | 956 | 525.1 | 440.2 | 478.2 | 438.9 | 313.9 | 303.1 | 300 | 347 | 279.6 | 312.8
1075 | 957 | 525.1 | 440.3 | 478.3 | 439 | 314.2 | 303.4 | 300.3 | 347.2 | 279.8 | 313
1076 | 958 | 525.1 | 440.4 | 478.4 | 439.1 | 314.6 | 303.7 | 300.6 | 347.6 | 280.1 | 313.3
1077 | 959 | 525.2 | 440.5 | 478.5 | 439.2 | 314.8 | 304 | 300.9 | 347.8 | 280.3 | 313.5
1078 | 960 | 525.2 | 440.7 | 478.6 | 439.4 | 315.1 | 304.3 | 301.2 | 347.4 | 280.6 | 313.8
1079 | 961 | 525.2 | 440.8 | 478.7 | 439.5 | 315.3 | 304.6 | 301.5 | 347.9 | 280.8 | 314.1
1080 | 962 | 525.2 | 440.9 | 478.7 | 439.6 | 315.6 | 305 | 301.9 | 348.3 | 281.1 | 314.4
1081 | 963 | 525.2 | 441 | 478.8 | 439.7 | 315.9 | 305.3 | 302.2 | 348.6 | 281.3 | 314.6
1082 | 964 | 525.2 | 441.1 | 478.9 | 439.8 | 316.2 | 305.6 | 302.5 | 349.1 | 281.6 | 314.9
1083 | 965 | 525.2 | 441.2 | 479 | 440 | 316.6 | 305.9 | 302.8 | 349.5 | 281.8 | 315.2
1084 | 966 | 525.2 | 441.3 | 479.1 | 440.1 | 316.9 | 306.2 | 303.1 | 349.9 | 282.1 | 315.5
1085 | 967 | 525.2 | 441.4 | 479.1 | 440.2 | 317.3 | 306.6 | 303.5 | 350.3 | 282.3 | 315.8
1086 | 968 | 525.2 | 441.5 | 479.2 | 440.3 | 317.7 | 306.9 | 303.8 | 350.6 | 282.6 | 316
1087 | 969 | 525.1 | 441.6 | 479.3 | 440.4 | 318.1 | 307.3 | 304.1 | 350.9 | 282.8 | 316.3
1088 | 970 | 525.1 | 441.7 | 479.4 | 440.6 | 318.5 | 307.6 | 304.4 | 351.3 | 283.1 | 316.6
1089 | 971 | 525.1 | 441.8 | 479.4 | 440.7 | 318.9 | 307.9 | 304.7 | 351.6 | 283.3 | 316.8
1090 | 972 | 525 | 441.9 | 479.5 | 440.8 | 319.3 | 308.3 | 305 | 351.9 | 283.6 | 317.1
1091 | 973 | 525 | 442 | 479.6 | 440.9 | 319.7 | 308.6 | 305.4 | 352.1 | 283.8 | 317.4
1092 | 974 | 525 | 442.1 | 479.7 | 441 | 320.1 | 308.9 | 305.7 | 352.4 | 284.1 | 317.6
1093 | 975 | 524.9 | 442.3 | 479.8 | 441.1 | 320.5 | 309.2 | 306 | 352.6 | 284.4 | 317.9
1094 | 976 | 524.9 | 442.4 | 479.9 | 441.3 | 320.9 | 309.5 | 306.3 | 352.9 | 284.6 | 318.1
1095 | 977 | 524.9 | 442.5 | 480 | 441.4 | 321.3 | 309.8 | 306.6 | 353 | 284.9 | 318.3
1096 | 978 | 524.9 | 442.6 | 480.1 | 441.5 | 321.7 | 310.1 | 306.9 | 353.3 | 285.1 | 318.6
1097 | 979 | 524.9 | 442.7 | 480.1 | 441.6 | 322.1 | 310.4 | 307.2 | 353.7 | 285.4 | 318.8
1098 | 980 | 524.9 | 442.8 | 480.2 | 441.7 | 322.6 | 310.7 | 307.5 | 354 | 285.6 | 319.1
1099 | 981 | 524.9 | 442.9 | 480.2 | 441.8 | 323 | 311 | 307.8 | 354.3 | 285.9 | 319.3
1100 | 982 | 524.9 | 443 | 480.3 | 441.9 | 323.4 | 311.3 | 308.1 | 354.7 | 286.2 | 319.5
1101 | 983 | 524.8 | 443.1 | 480.4 | 442 | 323.8 | 311.6 | 308.5 | 355.1 | 286.4 | 319.7
1102 | 984 | 524.8 | 443.2 | 480.5 | 442.1 | 324.1 | 311.9 | 308.8 | 355.4 | 286.7 | 319.9
1103 | 985 | 524.8 | 443.3 | 480.6 | 442.2 | 324.5 | 312.2 | 309.1 | 355.8 | 287 | 320.1
1104 | 986 | 524.8 | 443.4 | 480.6 | 442.4 | 324.9 | 312.5 | 309.4 | 356.1 | 287.2 | 320.4
1105 | 987 | 524.7 | 443.5 | 480.7 | 442.5 | 325.3 | 312.8 | 309.7 | 356.5 | 287.4 | 320.6
1106 | 988 | 524.7 | 443.6 | 480.8 | 442.6 | 325.8 | 313.1 | 310.1 | 356.8 | 287.7 | 320.8
1107 | 989 | 524.6 | 443.7 | 480.9 | 442.7 | 326.2 | 313.4 | 310.4 | 357.1 | 287.9 | 321
1108 | 990 | 524.6 | 443.8 | 480.9 | 442.8 | 326.5 | 313.7 | 310.7 | 357.5 | 288.2 | 321.3
1109 | 991 | 524.6 | 443.9 | 481 | 442.9 | 326.9 | 314 | 311 | 357.7 | 288.4 | 321.5
1110 | 992 | 524.7 | 444 | 481 | 443 | 327.3 | 314.3 | 311.3 | 357.9 | 288.7 | 321.7
1111 | 993 | 524.7 | 444.1 | 481.1 | 443.1 | 327.8 | 314.6 | 311.7 | 358.4 | 288.9 | 321.9
1112 | 994 | 524.7 | 444.2 | 481.2 | 443.2 | 328.3 | 314.9 | 312 | 358.8 | 289.2 | 322.2
1113 | 995 | 524.7 | 444.3 | 481.3 | 443.3 | 328.8 | 315.2 | 312.3 | 359.1 | 289.4 | 322.4
1114 | 996 | 524.7 | 444.4 | 481.4 | 443.4 | 329.3 | 315.6 | 312.6 | 359.3 | 289.6 | 322.7
1115 | 997 | 524.7 | 444.5 | 481.4 | 443.5 | 329.7 | 315.9 | 312.9 | 359.5 | 289.9 | 322.9
1116 | 998 | 524.7 | 444.6 | 481.5 | 443.6 | 330.1 | 316.2 | 313.3 | 359.9 | 290.1 | 323.2
1117 | 999 | 524.8 | 444.7 | 481.6 | 443.7 | 330.6 | 316.5 | 313.6 | 360.1 | 290.4 | 323.4
1118 | 1000 | 524.8 | 444.8 | 481.7 | 443.8 | 331.1 | 316.9 | 313.9 | 360.4 | 290.6 | 323.7
1119 | 1001 | 524.8 | 444.9 | 481.8 | 443.9 | 331.6 | 317.2 | 314.2 | 360.7 | 290.8 | 324
1120 | 1002 | 524.8 | 445 | 481.8 | 444 | 332 | 317.5 | 314.5 | 361 | 291.1 | 324.2
1121 | 1003 | 524.8 | 445.1 | 481.9 | 444.1 | 332.4 | 317.9 | 314.8 | 361.4 | 291.3 | 324.5
1122 | 1004 | 524.9 | 445.2 | 481.9 | 444.2 | 332.8 | 318.2 | 315.1 | 361.8 | 291.6 | 324.8
1123 | 1005 | 524.9 | 445.3 | 482 | 444.3 | 333.2 | 318.6 | 315.5 | 362.2 | 291.8 | 325
1124 | 1006 | 524.9 | 445.3 | 482.1 | 444.5 | 333.7 | 318.9 | 315.8 | 362.5 | 292 | 325.3
1125 | 1007 | 524.9 | 445.4 | 482.2 | 444.6 | 334.1 | 319.3 | 316.1 | 362.8 | 292.3 | 325.6
1126 | 1008 | 525 | 445.5 | 482.2 | 444.7 | 334.6 | 319.6 | 316.4 | 363 | 292.5 | 325.8
1127 | 1009 | 524.9 | 445.6 | 482.3 | 444.8 | 335.1 | 320 | 316.7 | 363.3 | 292.7 | 326.1
1128 | 1010 | 525 | 445.7 | 482.4 | 444.9 | 335.5 | 320.3 | 317 | 363.5 | 292.9 | 326.4
1129 | 1011 | 525 | 445.8 | 482.4 | 445 | 335.9 | 320.6 | 317.3 | 363.6 | 293.2 | 326.7
1130 | 1012 | 525 | 445.9 | 482.5 | 445.1 | 336.2 | 321 | 317.6 | 363.9 | 293.4 | 327
1131 | 1013 | 525 | 446 | 482.6 | 445.2 | 336.6 | 321.3 | 317.9 | 364.2 | 293.6 | 327.2
1132 | 1014 | 525 | 446.1 | 482.6 | 445.3 | 337 | 321.6 | 318.2 | 364.6 | 293.8 | 327.5
1133 | 1015 | 525 | 446.2 | 482.7 | 445.4 | 337.4 | 321.9 | 318.5 | 364.9 | 294 | 327.7
1134 | 1016 | 525 | 446.3 | 482.8 | 445.5 | 337.8 | 322.3 | 318.8 | 365.2 | 294.2 | 328
1135 | 1017 | 525 | 446.4 | 482.9 | 445.6 | 338.2 | 322.6 | 319.1 | 365.4 | 294.4 | 328.2
1136 | 1018 | 525 | 446.5 | 483 | 445.7 | 338.7 | 322.9 | 319.4 | 365.7 | 294.6 | 328.5
1137 | 1019 | 525 | 446.6 | 483 | 445.8 | 339.2 | 323.2 | 319.7 | 366.1 | 294.7 | 328.7
1138 | 1020 | 525 | 446.7 | 483.1 | 445.9 | 339.6 | 323.6 | 320 | 366.4 | 294.9 | 329
1139 | 1021 | 525 | 446.8 | 483.1 | 446 | 340 | 323.9 | 320.3 | 366.7 | 295.1 | 329.3
1140 | 1022 | 525 | 446.9 | 483.2 | 446.1 | 340.4 | 324.2 | 320.6 | 367 | 295.3 | 329.6
1141 | 1023 | 525 | 446.9 | 483.3 | 446.2 | 340.8 | 324.5 | 320.9 | 367.2 | 295.5 | 329.8
1142 | 1024 | 525.1 | 447 | 483.3 | 446.3 | 341.2 | 324.8 | 321.3 | 367.5 | 295.6 | 330.1
1143 | 1025 | 525.1 | 447.1 | 483.4 | 446.4 | 341.6 | 325.1 | 321.6 | 367.9 | 295.8 | 330.4
1144 | 1026 | 525.1 | 447.2 | 483.5 | 446.5 | 341.9 | 325.4 | 321.9 | 368.3 | 296 | 330.7
1145 | 1027 | 525.1 | 447.3 | 483.5 | 446.6 | 342.2 | 325.8 | 322.2 | 368.6 | 296.2 | 330.9
1146 | 1028 | 525.1 | 447.4 | 483.6 | 446.6 | 342.6 | 326.1 | 322.5 | 368.9 | 296.4 | 331.2
1147 | 1029 | 525.1 | 447.5 | 483.7 | 446.7 | 342.9 | 326.4 | 322.8 | 369.2 | 296.5 | 331.5
1148 | 1030 | 525.2 | 447.6 | 483.7 | 446.8 | 343.3 | 326.8 | 323.1 | 369.5 | 296.7 | 331.7
1149 | 1031 | 525.2 | 447.7 | 483.8 | 446.9 | 343.6 | 327.1 | 323.4 | 369.8 | 296.9 | 332
1150 | 1032 | 525.2 | 447.8 | 483.9 | 447 | 343.9 | 327.4 | 323.7 | 369.9 | 297 | 332.2
1151 | 1033 | 525.2 | 447.8 | 483.9 | 447.1 | 344.2 | 327.8 | 324 | 370.2 | 297.2 | 332.5
1152 | 1034 | 525.3 | 447.9 | 484 | 447.2 | 344.6 | 328.1 | 324.3 | 370.4 | 297.4 | 332.7
1153 | 1035 | 525.3 | 448 | 484.1 | 447.3 | 344.9 | 328.4 | 324.6 | 370.6 | 297.5 | 333
1154 | 1036 | 525.3 | 448.1 | 484.1 | 447.4 | 345.2 | 328.7 | 325 | 370.9 | 297.7 | 333.2
1155 | 1037 | 525.3 | 448.2 | 484.2 | 447.5 | 345.6 | 329 | 325.3 | 371 | 297.8 | 333.4
1156 | 1038 | 525.3 | 448.3 | 484.2 | 447.6 | 345.9 | 329.4 | 325.6 | 371.2 | 298 | 333.7
1157 | 1039 | 525.3 | 448.4 | 484.3 | 447.7 | 346.2 | 329.7 | 325.9 | 371.5 | 298.1 | 333.9
1158 | 1040 | 525.3 | 448.5 | 484.3 | 447.8 | 346.5 | 330 | 326.2 | 371.6 | 298.3 | 334.1
1159 | 1041 | 525.3 | 448.5 | 484.4 | 447.9 | 346.7 | 330.3 | 326.5 | 371.9 | 298.5 | 334.3
1160 | 1042 | 525.4 | 448.6 | 484.5 | 448 | 347 | 330.6 | 326.8 | 372.2 | 298.6 | 334.5
1161 | 1043 | 525.4 | 448.7 | 484.6 | 448.1 | 347.4 | 330.9 | 327.1 | 372.4 | 298.8 | 334.7
1162 | 1044 | 525.4 | 448.8 | 484.6 | 448.2 | 347.8 | 331.2 | 327.4 | 372.7 | 298.9 | 334.9
1163 | 1045 | 525.4 | 448.9 | 484.7 | 448.2 | 348.1 | 331.5 | 327.7 | 373 | 299 | 335.1
1164 | 1046 | 525.4 | 449 | 484.8 | 448.3 | 348.4 | 331.8 | 328 | 373.3 | 299.2 | 335.3
1165 | 1047 | 525.4 | 449 | 484.9 | 448.4 | 348.7 | 332.1 | 328.3 | 373.6 | 299.3 | 335.6
1166 | 1048 | 525.4 | 449.1 | 484.9 | 448.5 | 349 | 332.5 | 328.6 | 374 | 299.5 | 335.8
1167 | 1049 | 525.4 | 449.2 | 485 | 448.6 | 349.2 | 332.8 | 328.9 | 374.2 | 299.6 | 336
1168 | 1050 | 525.4 | 449.3 | 485 | 448.7 | 349.5 | 333.1 | 329.2 | 374.5 | 299.8 | 336.2
1169 | 1051 | 525.4 | 449.4 | 485.1 | 448.8 | 349.8 | 333.5 | 329.5 | 374.8 | 299.9 | 336.4
1170 | 1052 | 525.5 | 449.5 | 485.1 | 448.9 | 350.1 | 333.8 | 329.8 | 375.1 | 300.1 | 336.7
1171 | 1053 | 525.5 | 449.6 | 485.2 | 449 | 350.3 | 334.1 | 330.1 | 375.4 | 300.2 | 336.9
1172 | 1054 | 525.5 | 449.6 | 485.3 | 449.1 | 350.6 | 334.4 | 330.4 | 375.6 | 300.4 | 337.1
1173 | 1055 | 525.5 | 449.7 | 485.4 | 449.1 | 350.9 | 334.8 | 330.7 | 375.8 | 300.5 | 337.3
1174 | 1056 | 525.4 | 449.8 | 485.4 | 449.2 | 351.1 | 335.3 | 330.9 | 376.1 | 300.7 | 337.5
1175 | 1057 | 525.4 | 449.9 | 485.5 | 449.3 | 351.4 | 335.7 | 331.2 | 376.3 | 300.9 | 337.7
1176 | 1058 | 525.4 | 450 | 485.5 | 449.4 | 351.7 | 336 | 331.5 | 376.4 | 301 | 337.9
1177 | 1059 | 525.4 | 450.1 | 485.5 | 449.5 | 351.9 | 336.4 | 331.8 | 376.5 | 301.2 | 338.1
1178 | 1060 | 525.4 | 450.2 | 485.6 | 449.6 | 352.2 | 336.7 | 332.1 | 376.6 | 301.3 | 338.3
1179 | 1061 | 525.4 | 450.3 | 485.7 | 449.7 | 352.5 | 337.1 | 332.3 | 376.8 | 301.5 | 338.5
1180 | 1062 | 525.4 | 450.3 | 485.8 | 449.8 | 352.8 | 337.4 | 332.6 | 376.9 | 301.7 | 338.8
1181 | 1063 | 525.4 | 450.4 | 485.8 | 449.9 | 353 | 337.7 | 332.9 | 377.1 | 301.8 | 339
1182 | 1064 | 525.4 | 450.5 | 485.9 | 450 | 353.4 | 338 | 333.2 | 377.1 | 302 | 339.2
1183 | 1065 | 525.3 | 450.6 | 486 | 450 | 353.6 | 338.4 | 333.5 | 377 | 302.2 | 339.4
1184 | 1066 | 525.3 | 450.6 | 486 | 450.1 | 353.9 | 338.7 | 333.7 | 377.1 | 302.4 | 339.6
1185 | 1067 | 525.3 | 450.7 | 486.1 | 450.2 | 354.2 | 339 | 334 | 377.3 | 302.5 | 339.8
1186 | 1068 | 525.3 | 450.8 | 486.1 | 450.3 | 354.5 | 339.3 | 334.3 | 377.5 | 302.7 | 340
1187 | 1069 | 525.3 | 450.9 | 486.2 | 450.4 | 354.8 | 339.6 | 334.6 | 377.5 | 302.9 | 340.1
1188 | 1070 | 525.3 | 450.9 | 486.2 | 450.5 | 355.1 | 339.8 | 334.8 | 377.6 | 303.1 | 340.4
1189 | 1071 | 525.3 | 451 | 486.3 | 450.6 | 355.4 | 340.1 | 335.1 | 377.8 | 303.3 | 340.6
1190 | 1072 | 525.3 | 451.1 | 486.4 | 450.7 | 355.7 | 340.4 | 335.4 | 377.9 | 303.5 | 340.8
1191 | 1073 | 525.2 | 451.2 | 486.4 | 450.7 | 356 | 340.7 | 335.7 | 378.1 | 303.7 | 341
1192 | 1074 | 525.2 | 451.3 | 486.5 | 450.8 | 356.3 | 341 | 335.9 | 378.1 | 303.9 | 341.2
1193 | 1075 | 525.2 | 451.4 | 486.6 | 450.9 | 356.6 | 341.3 | 336.2 | 378.3 | 304.1 | 341.5
1194 | 1076 | 525.3 | 451.4 | 486.6 | 451 | 356.9 | 341.5 | 336.5 | 378.5 | 304.3 | 341.7
1195 | 1077 | 525.3 | 451.5 | 486.7 | 451.1 | 357.1 | 341.8 | 336.8 | 378.6 | 304.5 | 341.9
1196 | 1078 | 525.3 | 451.6 | 486.7 | 451.2 | 357.4 | 342.1 | 337 | 378.9 | 304.7 | 342.1
1197 | 1079 | 525.2 | 451.7 | 486.8 | 451.3 | 357.7 | 342.3 | 337.3 | 379.2 | 304.9 | 342.4
1198 | 1080 | 525.2 | 451.8 | 486.9 | 451.3 | 358 | 342.6 | 337.6 | 379.4 | 305.2 | 342.6
1199 | 1081 | 525.2 | 451.8 | 486.9 | 451.4 | 358.3 | 342.9 | 337.9 | 379.6 | 305.4 | 342.8
1200 | 1082 | 525.2 | 451.9 | 487 | 451.5 | 358.6 | 343.1 | 338.1 | 379.8 | 305.6 | 343.1
1201 | 1083 | 525.2 | 452 | 487 | 451.6 | 358.9 | 343.4 | 338.4 | 380.1 | 305.8 | 343.3
1202 | 1084 | 525.2 | 452.1 | 487.1 | 451.7 | 359.2 | 343.7 | 338.7 | 380.3 | 306 | 343.5
1203 | 1085 | 525.2 | 452.1 | 487.2 | 451.7 | 359.4 | 343.9 | 339 | 380.6 | 306.2 | 343.7
1204 | 1086 | 525.2 | 452.2 | 487.2 | 451.8 | 359.7 | 344.2 | 339.3 | 380.8 | 306.4 | 343.9
1205 | 1087 | 525.2 | 452.3 | 487.3 | 451.9 | 360 | 344.4 | 339.6 | 381.1 | 306.6 | 344.2
1206 | 1088 | 525.2 | 452.4 | 487.3 | 452 | 360.3 | 344.7 | 339.8 | 381.4 | 306.8 | 344.4
1207 | 1089 | 525.2 | 452.4 | 487.4 | 452.1 | 360.6 | 344.9 | 340.1 | 381.8 | 307 | 344.6
1208 | 1090 | 525.2 | 452.5 | 487.5 | 452.2 | 360.9 | 345.2 | 340.4 | 382 | 307.2 | 344.8
1209 | 1091 | 525.2 | 452.6 | 487.5 | 452.2 | 361.2 | 345.4 | 340.7 | 382.3 | 307.4 | 345.1
1210 | 1092 | 525.2 | 452.7 | 487.6 | 452.3 | 361.5 | 345.7 | 341 | 382.5 | 307.6 | 345.3
1211 | 1093 | 525.2 | 452.8 | 487.6 | 452.4 | 361.8 | 345.9 | 341.3 | 382.7 | 307.8 | 345.5
1212 | 1094 | 525.2 | 452.8 | 487.7 | 452.5 | 362.1 | 346.2 | 341.5 | 383.1 | 308.1 | 345.7
1213 | 1095 | 525.2 | 452.9 | 487.8 | 452.5 | 362.4 | 346.4 | 341.8 | 383.4 | 308.3 | 346
1214 | 1096 | 525.2 | 453 | 487.8 | 452.6 | 362.7 | 346.6 | 342.1 | 383.6 | 308.5 | 346.2
1215 | 1097 | 525.2 | 453 | 487.9 | 452.7 | 362.9 | 346.8 | 342.4 | 383.9 | 308.7 | 346.4
1216 | 1098 | 525.2 | 453.1 | 487.9 | 452.8 | 363.1 | 347.1 | 342.7 | 384.1 | 308.9 | 346.6
1217 | 1099 | 525.3 | 453.2 | 488 | 452.9 | 363.4 | 347.4 | 342.9 | 384.4 | 309.2 | 346.8
1218 | 1100 | 525.3 | 453.3 | 488 | 453 | 363.6 | 347.6 | 343.2 | 384.7 | 309.4 | 347.1
1219 | 1101 | 525.3 | 453.4 | 488.1 | 453 | 363.9 | 347.8 | 343.5 | 385.1 | 309.6 | 347.3
1220 | 1102 | 525.4 | 453.4 | 488.2 | 453.1 | 364.1 | 348.1 | 343.8 | 385.5 | 309.8 | 347.5
1221 | 1103 | 525.4 | 453.5 | 488.2 | 453.2 | 364.4 | 348.3 | 344.1 | 385.8 | 310 | 347.7
1222 | 1104 | 525.4 | 453.6 | 488.3 | 453.3 | 364.6 | 348.6 | 344.3 | 386.1 | 310.3 | 347.9
1223 | 1105 | 525.4 | 453.7 | 488.3 | 453.4 | 364.8 | 348.9 | 344.6 | 386.3 | 310.5 | 348.1
1224 | 1106 | 525.4 | 453.7 | 488.4 | 453.4 | 365.1 | 349.2 | 344.9 | 386.6 | 310.7 | 348.3
1225 | 1107 | 525.4 | 453.8 | 488.4 | 453.5 | 365.4 | 349.4 | 345.2 | 386.8 | 310.9 | 348.5
1226 | 1108 | 525.4 | 453.9 | 488.5 | 453.6 | 365.6 | 349.7 | 345.5 | 387.2 | 311.2 | 348.7
1227 | 1109 | 525.4 | 453.9 | 488.6 | 453.7 | 365.9 | 350 | 345.8 | 387.5 | 311.4 | 348.9
1228 | 1110 | 525.4 | 454 | 488.6 | 453.7 | 366.1 | 350.3 | 346 | 387.7 | 311.6 | 349
1229 | 1111 | 525.4 | 454.1 | 488.7 | 453.8 | 366.4 | 350.5 | 346.3 | 388 | 311.9 | 349.2
1230 | 1112 | 525.4 | 454.2 | 488.7 | 453.9 | 366.6 | 350.8 | 346.6 | 388.3 | 312.1 | 349.4
1231 | 1113 | 525.4 | 454.2 | 488.8 | 454 | 366.9 | 351.1 | 346.9 | 388.6 | 312.3 | 349.5
1232 | 1114 | 525.4 | 454.3 | 488.8 | 454.1 | 367.2 | 351.4 | 347.2 | 388.8 | 312.5 | 349.7
1233 | 1115 | 525.4 | 454.4 | 488.9 | 454.1 | 367.4 | 351.7 | 347.5 | 389 | 312.8 | 349.9
1234 | 1116 | 525.3 | 454.5 | 488.9 | 454.2 | 367.6 | 351.9 | 347.8 | 389.2 | 313 | 350
1235 | 1117 | 525.3 | 454.5 | 489 | 454.3 | 367.7 | 352.2 | 348 | 389.4 | 313.2 | 350.2
1236 | 1118 | 525.3 | 454.6 | 489.1 | 454.4 | 367.8 | 352.5 | 348.3 | 389.6 | 313.5 | 350.4
1237 | 1119 | 525.3 | 454.7 | 489.1 | 454.4 | 367.8 | 352.8 | 348.6 | 389.9 | 313.7 | 350.6
1238 | 1120 | 525.3 | 454.7 | 489.2 | 454.5 | 367.9 | 353.1 | 348.9 | 390.2 | 313.9 | 350.7
1239 | 1121 | 525.3 | 454.8 | 489.3 | 454.6 | 368 | 353.4 | 349.2 | 390.4 | 314.2 | 350.9
1240 | 1122 | 525.2 | 454.9 | 489.3 | 454.7 | 368.1 | 353.7 | 349.5 | 390.6 | 314.4 | 351.1
1241 | 1123 | 525.3 | 455 | 489.3 | 454.8 | 368.2 | 354 | 349.7 | 390.8 | 314.6 | 351.3
1242 | 1124 | 525.3 | 455 | 489.4 | 454.8 | 368.4 | 354.3 | 350 | 390.9 | 314.8 | 351.4
1243 | 1125 | 525.3 | 455.1 | 489.4 | 454.9 | 368.5 | 354.6 | 350.3 | 391.2 | 315.1 | 351.6
1244 | 1126 | 525.3 | 455.2 | 489.5 | 455 | 368.6 | 354.9 | 350.6 | 391.4 | 315.3 | 351.8
1245 | 1127 | 525.3 | 455.2 | 489.6 | 455 | 368.8 | 355.2 | 350.9 | 391.6 | 315.5 | 352
1246 | 1128 | 525.3 | 455.3 | 489.6 | 455.1 | 369 | 355.5 | 351.2 | 391.8 | 315.8 | 352.2
1247 | 1129 | 525.3 | 455.4 | 489.7 | 455.2 | 369.2 | 355.7 | 351.5 | 392 | 316 | 352.3
1248 | 1130 | 525.2 | 455.4 | 489.7 | 455.3 | 369.3 | 356 | 351.7 | 392.2 | 316.2 | 352.5
1249 | 1131 | 525.2 | 455.5 | 489.8 | 455.3 | 369.6 | 356.4 | 352 | 392.4 | 316.4 | 352.7
1250 | 1132 | 525.2 | 455.6 | 489.8 | 455.4 | 369.8 | 356.7 | 352.3 | 392.6 | 316.7 | 352.9
1251 | 1133 | 525.2 | 455.6 | 489.9 | 455.5 | 370 | 357 | 352.6 | 392.9 | 316.9 | 353.1
1252 | 1134 | 525.2 | 455.7 | 489.9 | 455.6 | 370.2 | 357.3 | 352.9 | 393.1 | 317.2 | 353.3
1253 | 1135 | 525.1 | 455.8 | 489.9 | 455.6 | 370.5 | 357.6 | 353.2 | 393.2 | 317.4 | 353.5
1254 | 1136 | 525.1 | 455.9 | 490 | 455.7 | 370.7 | 357.9 | 353.5 | 393.4 | 317.7 | 353.7
1255 | 1137 | 525.1 | 455.9 | 490.1 | 455.8 | 371 | 358.1 | 353.8 | 393.6 | 317.9 | 353.9
1256 | 1138 | 525.1 | 456 | 490.1 | 455.8 | 371.2 | 358.5 | 354 | 393.8 | 318.2 | 354.1
1257 | 1139 | 525.1 | 456 | 490.2 | 455.9 | 371.4 | 358.8 | 354.3 | 394 | 318.4 | 354.3
1258 | 1140 | 525.1 | 456.1 | 490.2 | 456 | 371.6 | 359 | 354.6 | 394.2 | 318.7 | 354.5
1259 | 1141 | 525.1 | 456.2 | 490.3 | 456.1 | 371.9 | 359.4 | 354.9 | 394.4 | 318.9 | 354.7
1260 | 1142 | 525 | 456.2 | 490.3 | 456.1 | 372.1 | 359.7 | 355.2 | 394.6 | 319.2 | 354.9
1261 | 1143 | 525 | 456.3 | 490.4 | 456.2 | 372.3 | 360 | 355.5 | 394.8 | 319.4 | 355.1
1262 | 1144 | 525 | 456.4 | 490.4 | 456.3 | 372.6 | 360.3 | 355.8 | 395 | 319.7 | 355.3
1263 | 1145 | 525 | 456.4 | 490.5 | 456.3 | 372.8 | 360.6 | 356.1 | 395.2 | 319.9 | 355.5
1264 | 1146 | 525 | 456.5 | 490.5 | 456.4 | 373 | 360.9 | 356.4 | 395.3 | 320.2 | 355.6
1265 | 1147 | 525 | 456.6 | 490.6 | 456.5 | 373.2 | 361.2 | 356.7 | 395.4 | 320.5 | 355.8
1266 | 1148 | 525 | 456.6 | 490.7 | 456.5 | 373.4 | 361.5 | 357 | 395.5 | 320.7 | 356
1267 | 1149 | 525 | 456.7 | 490.7 | 456.6 | 373.7 | 361.8 | 357.3 | 395.7 | 321 | 356.2
1268 | 1150 | 525 | 456.7 | 490.8 | 456.7 | 373.9 | 362.1 | 357.6 | 396 | 321.3 | 356.4
1269 | 1151 | 525 | 456.8 | 490.9 | 456.7 | 374.1 | 362.4 | 357.9 | 396.1 | 321.5 | 356.7
1270 | 1152 | 525 | 456.9 | 490.9 | 456.8 | 374.3 | 362.7 | 358.2 | 396.3 | 321.8 | 356.9
1271 | 1153 | 525 | 456.9 | 491 | 456.9 | 374.5 | 363 | 358.5 | 396.5 | 322 | 357.1
1272 | 1154 | 525 | 457 | 491 | 456.9 | 374.7 | 363.3 | 358.8 | 396.7 | 322.3 | 357.3
1273 | 1155 | 525.1 | 457.1 | 491 | 457 | 374.9 | 363.6 | 359.1 | 396.9 | 322.6 | 357.5
1274 | 1156 | 525.1 | 457.1 | 491.1 | 457.1 | 375.1 | 363.9 | 359.4 | 397 | 322.9 | 357.8
1275 | 1157 | 525.1 | 457.2 | 491.1 | 457.2 | 375.3 | 364.2 | 359.7 | 397.2 | 323.1 | 358
1276 | 1158 | 525.2 | 457.2 | 491.2 | 457.2 | 375.5 | 364.5 | 360 | 397.3 | 323.4 | 358.2
1277 | 1159 | 525.2 | 457.3 | 491.2 | 457.3 | 375.7 | 364.8 | 360.3 | 397.5 | 323.7 | 358.5
1278 | 1160 | 525.2 | 457.4 | 491.3 | 457.4 | 375.9 | 365.1 | 360.6 | 397.7 | 324 | 358.7
1279 | 1161 | 525.2 | 457.4 | 491.4 | 457.4 | 376.1 | 365.4 | 360.9 | 397.8 | 324.3 | 358.9
1280 | 1162 | 525.3 | 457.5 | 491.4 | 457.5 | 376.3 | 365.7 | 361.2 | 397.9 | 324.6 | 359.1
1281 | 1163 | 525.3 | 457.5 | 491.5 | 457.6 | 376.4 | 366 | 361.5 | 398.1 | 324.8 | 359.3
1282 | 1164 | 525.3 | 457.6 | 491.5 | 457.6 | 376.6 | 366.3 | 361.8 | 398.3 | 325.1 | 359.5
1283 | 1165 | 525.3 | 457.7 | 491.6 | 457.7 | 376.9 | 366.6 | 362.1 | 398.5 | 325.4 | 359.7
1284 | 1166 | 525.3 | 457.7 | 491.6 | 457.8 | 377.1 | 366.9 | 362.4 | 398.7 | 325.7 | 359.8
1285 | 1167 | 525.3 | 457.8 | 491.7 | 457.8 | 377.3 | 367.2 | 362.7 | 398.8 | 326 | 359.9
1286 | 1168 | 525.4 | 457.9 | 491.7 | 457.9 | 377.5 | 367.5 | 363 | 399 | 326.3 | 360.1
1287 | 1169 | 525.4 | 457.9 | 491.8 | 458 | 377.7 | 367.8 | 363.3 | 399.2 | 326.6 | 360.3
1288 | 1170 | 525.4 | 458 | 491.8 | 458 | 377.9 | 368.1 | 363.7 | 399.4 | 326.9 | 360.4
1289 | 1171 | 525.4 | 458 | 491.9 | 458.1 | 378.1 | 368.4 | 364 | 399.6 | 327.2 | 360.4
1290 | 1172 | 525.4 | 458.1 | 492 | 458.2 | 378.3 | 368.6 | 364.3 | 399.7 | 327.5 | 360.5
1291 | 1173 | 525.4 | 458.2 | 491.9 | 458.3 | 378.6 | 369 | 364.6 | 399.9 | 327.8 | 360.6
1292 | 1174 | 525.4 | 458.5 | 491.5 | 458.5 | 379.3 | 369.4 | 364.9 | 400 | 328.1 | 360.7
1293 | 1175 | 525.4 | 458.6 | 491.6 | 458.6 | 379.5 | 369.7 | 365.2 | 400.2 | 328.4 | 360.8
1294 | 1176 | 525.4 | 458.6 | 491.6 | 458.6 | 379.7 | 369.9 | 365.5 | 400.3 | 328.7 | 360.8
1295 | 1177 | 525.4 | 458.7 | 491.7 | 458.7 | 380 | 370.2 | 365.8 | 400.4 | 329 | 360.9
1296 | 1178 | 525.4 | 458.7 | 491.7 | 458.8 | 380.2 | 370.5 | 366.1 | 400.6 | 329.3 | 360.9
1297 | 1179 | 525.3 | 458.8 | 491.8 | 458.9 | 380.4 | 370.8 | 366.4 | 400.8 | 329.7 | 360.9
1298 | 1180 | 525.3 | 458.9 | 491.8 | 458.9 | 380.6 | 371 | 366.7 | 400.9 | 330 | 360.8
1299 | 1181 | 525.3 | 458.9 | 491.9 | 459 | 380.8 | 371.3 | 367 | 401 | 330.3 | 360.8
1300 | 1182 | 525.2 | 459 | 491.9 | 459 | 381 | 371.5 | 367.3 | 401.1 | 330.6 | 360.7
1301 | 1183 | 525.2 | 459 | 491.9 | 459.1 | 381.2 | 371.8 | 367.6 | 401.2 | 330.9 | 360.5
1302 | 1184 | 525.2 | 459.1 | 492 | 459.2 | 381.4 | 372 | 367.9 | 401.4 | 331.2 | 360.3
1303 | 1185 | 525.1 | 459.2 | 492 | 459.3 | 381.6 | 372.3 | 368.2 | 401.6 | 331.5 | 360.2
1304 | 1186 | 525.1 | 459.2 | 492.1 | 459.3 | 381.8 | 372.5 | 368.5 | 401.8 | 331.8 | 360.4
1305 | 1187 | 525.1 | 459.3 | 492.1 | 459.4 | 382 | 372.7 | 368.8 | 402 | 332.1 | 360.5
1306 | 1188 | 525 | 459.3 | 492.2 | 459.4 | 382.1 | 372.9 | 369 | 402.2 | 332.4 | 360.7
1307 | 1189 | 525 | 459.4 | 492.2 | 459.5 | 382.3 | 373.1 | 369.3 | 402.4 | 332.8 | 360.9
1308 | 1190 | 524.9 | 459.5 | 492.3 | 459.6 | 382.5 | 373.3 | 369.6 | 402.6 | 333.1 | 361.1
1309 | 1191 | 524.9 | 459.5 | 492.3 | 459.6 | 382.7 | 373.5 | 369.9 | 402.8 | 333.4 | 361.3
1310 | 1192 | 524.8 | 459.6 | 492.4 | 459.7 | 382.9 | 373.7 | 370.1 | 403 | 333.7 | 361.5
1311 | 1193 | 524.8 | 459.6 | 492.4 | 459.8 | 383.1 | 373.8 | 370.4 | 403.2 | 334 | 361.7
1312 | 1194 | 524.7 | 459.7 | 492.4 | 459.8 | 383.3 | 374 | 370.7 | 403.4 | 334.3 | 361.9
1313 | 1195 | 524.7 | 459.8 | 492.4 | 459.9 | 383.4 | 374.2 | 371 | 403.5 | 334.7 | 362.1
1314 | 1196 | 524.6 | 459.8 | 492.5 | 460 | 383.6 | 374.3 | 371.2 | 403.8 | 335 | 362.3
1315 | 1197 | 524.6 | 459.9 | 492.6 | 460 | 383.8 | 374.5 | 371.5 | 404 | 335.3 | 362.4
1316 | 1198 | 524.6 | 459.9 | 492.6 | 460.1 | 384 | 374.6 | 371.7 | 404.2 | 335.6 | 362.6
1317 | 1199 | 524.5 | 460 | 492.7 | 460.2 | 384.1 | 374.8 | 372 | 404.5 | 335.9 | 362.7
1318 | 1200 | 524.5 | 460 | 492.7 | 460.2 | 384.3 | 374.9 | 372.2 | 404.7 | 336.3 | 362.8
1319 | 1201 | 524.4 | 460.1 | 492.8 | 460.3 | 384.5 | 375 | 372.4 | 404.9 | 336.6 | 363
1320 | 1202 | 524.4 | 460.1 | 492.8 | 460.3 | 384.7 | 375.1 | 372.7 | 405.2 | 336.9 | 363.2
1321 | 1203 | 524.4 | 460.2 | 492.8 | 460.4 | 384.8 | 375.2 | 372.9 | 405.4 | 337.2 | 363.3
1322 | 1204 | 524.4 | 460.3 | 492.9 | 460.5 | 385 | 375.3 | 373.1 | 405.7 | 337.5 | 363.4
1323 | 1205 | 524.4 | 460.3 | 493 | 460.5 | 385.2 | 375.4 | 373.3 | 406 | 337.9 | 363.6
1324 | 1206 | 524.3 | 460.4 | 493 | 460.6 | 385.3 | 375.5 | 373.6 | 406.2 | 338.2 | 363.8
1325 | 1207 | 524.3 | 460.4 | 493.1 | 460.7 | 385.5 | 375.6 | 373.8 | 406.4 | 338.5 | 364
1326 | 1208 | 524.3 | 460.5 | 493.1 | 460.7 | 385.6 | 375.6 | 374 | 406.7 | 338.8 | 364.2
1327 | 1209 | 524.2 | 460.5 | 493.1 | 460.8 | 385.8 | 375.7 | 374.2 | 406.9 | 339.1 | 364.4
1328 | 1210 | 524.2 | 460.6 | 493.2 | 460.9 | 385.9 | 375.8 | 374.4 | 407.1 | 339.4 | 364.6
1329 | 1211 | 524.2 | 460.6 | 493.2 | 460.9 | 386.1 | 375.9 | 374.5 | 407.4 | 339.8 | 364.8
1330 | 1212 | 524.2 | 460.7 | 493.3 | 461 | 386.2 | 375.9 | 374.7 | 407.6 | 340.1 | 365
1331 | 1213 | 524.2 | 460.7 | 493.3 | 461.1 | 386.4 | 376 | 374.9 | 407.8 | 340.4 | 365.2
1332 | 1214 | 524.2 | 460.8 | 493.4 | 461.1 | 386.5 | 376.1 | 375.1 | 408.1 | 340.7 | 365.3
1333 | 1215 | 524.2 | 460.8 | 493.4 | 461.2 | 386.7 | 376.2 | 375.2 | 408.2 | 341 | 365.3
1334 | 1216 | 524.3 | 460.9 | 493.5 | 461.2 | 386.8 | 376.2 | 375.4 | 408.4 | 341.3 | 365.5
1335 | 1217 | 524.3 | 461 | 493.5 | 461.3 | 386.9 | 376.3 | 375.5 | 408.6 | 341.7 | 365.8
1336 | 1218 | 524.3 | 461 | 493.6 | 461.4 | 387.1 | 376.4 | 375.7 | 408.8 | 342 | 366
1337 | 1219 | 524.4 | 461.1 | 493.6 | 461.4 | 387.2 | 376.4 | 375.8 | 409 | 342.3 | 366.3
1338 | 1220 | 524.4 | 461.1 | 493.7 | 461.5 | 387.4 | 376.5 | 376 | 409.3 | 342.6 | 366.5
1339 | 1221 | 524.4 | 461.2 | 493.7 | 461.5 | 387.5 | 376.6 | 376.1 | 409.5 | 342.9 | 366.6
1340 | 1222 | 524.4 | 461.2 | 493.7 | 461.6 | 387.6 | 376.7 | 376.2 | 409.8 | 343.2 | 366.8
1341 | 1223 | 524.4 | 461.3 | 493.8 | 461.7 | 387.8 | 376.7 | 376.3 | 410 | 343.5 | 366.9
1342 | 1224 | 524.4 | 461.3 | 493.8 | 461.8 | 387.9 | 376.8 | 376.4 | 410.2 | 343.9 | 367.1
1343 | 1225 | 524.4 | 461.4 | 493.8 | 461.8 | 388 | 376.9 | 376.6 | 410.5 | 344.2 | 367.3
1344 | 1226 | 524.4 | 461.4 | 493.9 | 461.9 | 388.2 | 377 | 376.7 | 410.7 | 344.5 | 367.4
1345 | 1227 | 524.4 | 461.5 | 493.9 | 461.9 | 388.3 | 377.1 | 376.8 | 410.9 | 344.9 | 367.5
1346 | 1228 | 524.4 | 461.6 | 494 | 462 | 388.5 | 377.2 | 376.9 | 411 | 345.2 | 367.6
1347 | 1229 | 524.5 | 461.6 | 494 | 462.1 | 388.6 | 377.2 | 377 | 411.3 | 345.6 | 367.7
1348 | 1230 | 524.5 | 461.6 | 494.1 | 462.1 | 388.7 | 377.3 | 377 | 411.5 | 345.9 | 367.8
1349 | 1231 | 524.5 | 461.7 | 494.1 | 462.2 | 388.9 | 377.4 | 377.1 | 411.7 | 346.3 | 368.1
1350 | 1232 | 524.5 | 461.7 | 494.2 | 462.3 | 389 | 377.5 | 377.2 | 411.8 | 346.6 | 368.2
1351 | 1233 | 524.5 | 461.8 | 494.2 | 462.3 | 389.1 | 377.6 | 377.3 | 412 | 346.9 | 368.4
1352 | 1234 | 524.5 | 461.8 | 494.2 | 462.4 | 389.2 | 377.7 | 377.4 | 412.2 | 347.3 | 368.6
1353 | 1235 | 524.5 | 461.9 | 494.3 | 462.4 | 389.3 | 377.8 | 377.5 | 412.3 | 347.6 | 368.7
1354 | 1236 | 524.5 | 462 | 494.4 | 462.5 | 389.5 | 377.9 | 377.6 | 412.5 | 347.9 | 368.9
1355 | 1237 | 524.5 | 462 | 494.4 | 462.6 | 389.6 | 378 | 377.7 | 412.7 | 348.3 | 369.1
1356 | 1238 | 524.5 | 462.1 | 494.4 | 462.6 | 389.7 | 378.1 | 377.8 | 412.9 | 348.6 | 369.2
1357 | 1239 | 524.5 | 462.1 | 494.5 | 462.7 | 389.9 | 378.2 | 377.9 | 413 | 348.9 | 369.3
1358 | 1240 | 524.5 | 462.2 | 494.5 | 462.8 | 390 | 378.3 | 377.9 | 413.2 | 349.2 | 369.5
1359 | 1241 | 524.5 | 462.2 | 494.6 | 462.8 | 390.1 | 378.4 | 378 | 413.5 | 349.6 | 369.6
1360 | 1242 | 524.5 | 462.3 | 494.6 | 462.9 | 390.2 | 378.5 | 378.1 | 413.6 | 349.9 | 369.7
1361 | 1243 | 524.6 | 462.3 | 494.6 | 462.9 | 390.4 | 378.6 | 378.2 | 413.8 | 350.2 | 369.9
1362 | 1244 | 524.6 | 462.4 | 494.6 | 463 | 390.5 | 378.7 | 378.3 | 414.1 | 350.5 | 370
1363 | 1245 | 524.6 | 462.4 | 494.7 | 463 | 390.6 | 378.8 | 378.4 | 414.3 | 350.8 | 370.2
1364 | 1246 | 524.6 | 462.5 | 494.7 | 463.1 | 390.8 | 378.9 | 378.5 | 414.5 | 351.1 | 370.4
1365 | 1247 | 524.6 | 462.6 | 494.7 | 463.2 | 390.9 | 379 | 378.5 | 414.7 | 351.4 | 370.5
1366 | 1248 | 524.6 | 462.6 | 494.8 | 463.2 | 391 | 379.1 | 378.6 | 414.8 | 351.7 | 370.7
1367 | 1249 | 524.7 | 462.7 | 494.8 | 463.3 | 391.1 | 379.3 | 378.7 | 415 | 352 | 370.8
1368 | 1250 | 524.7 | 462.7 | 494.9 | 463.3 | 391.3 | 379.4 | 378.8 | 415.1 | 352.3 | 371
1369 | 1251 | 524.8 | 462.8 | 494.9 | 463.4 | 391.4 | 379.5 | 378.9 | 415.4 | 352.6 | 371.2
1370 | 1252 | 524.8 | 462.8 | 494.9 | 463.5 | 391.5 | 379.6 | 379 | 415.6 | 352.9 | 371.3
1371 | 1253 | 524.8 | 462.9 | 495 | 463.5 | 391.6 | 379.7 | 379.1 | 415.9 | 353.2 | 371.5
1372 | 1254 | 524.9 | 462.9 | 495 | 463.6 | 391.7 | 379.8 | 379.2 | 416.1 | 353.5 | 371.7
1373 | 1255 | 524.9 | 463 | 495.1 | 463.6 | 391.9 | 379.9 | 379.4 | 416.2 | 353.8 | 371.8
1374 | 1256 | 524.9 | 463 | 495.1 | 463.7 | 392 | 380 | 379.5 | 416.4 | 354.1 | 372.1
1375 | 1257 | 524.9 | 463.1 | 495.2 | 463.8 | 392.1 | 380.1 | 379.6 | 416.6 | 354.3 | 372.3
1376 | 1258 | 525 | 463.1 | 495.2 | 463.8 | 392.2 | 380.2 | 379.7 | 416.8 | 354.6 | 372.6
1377 | 1259 | 525 | 463.2 | 495.3 | 463.9 | 392.3 | 380.3 | 379.8 | 417 | 354.9 | 372.8
1378 | 1260 | 525.1 | 463.2 | 495.3 | 463.9 | 392.4 | 380.5 | 379.9 | 417.1 | 355.2 | 373
1379 | 1261 | 525.1 | 463.3 | 495.3 | 464 | 392.6 | 380.6 | 380.1 | 417.3 | 355.5 | 373.3
1380 | 1262 | 525.1 | 463.3 | 495.4 | 464.1 | 392.7 | 380.7 | 380.2 | 417.4 | 355.7 | 373.5
1381 | 1263 | 525.2 | 463.4 | 495.4 | 464.1 | 392.8 | 380.8 | 380.3 | 417.6 | 356 | 373.7
1382 | 1264 | 525.2 | 463.4 | 495.5 | 464.2 | 392.9 | 380.9 | 380.4 | 417.8 | 356.3 | 373.9
1383 | 1265 | 525.2 | 463.5 | 495.5 | 464.2 | 393.1 | 381 | 380.5 | 417.9 | 356.5 | 374.1
1384 | 1266 | 525.3 | 463.5 | 495.5 | 464.3 | 393.2 | 381.1 | 380.6 | 418 | 356.8 | 374.3
1385 | 1267 | 525.3 | 463.6 | 495.5 | 464.4 | 393.3 | 381.3 | 380.8 | 418.3 | 357 | 374.5
1386 | 1268 | 525.3 | 463.6 | 495.6 | 464.4 | 393.4 | 381.4 | 380.9 | 418.5 | 357.3 | 374.6
1387 | 1269 | 525.3 | 463.7 | 495.6 | 464.5 | 393.5 | 381.5 | 381 | 418.6 | 357.5 | 374.8
1388 | 1270 | 525.4 | 463.7 | 495.7 | 464.5 | 393.7 | 381.6 | 381.1 | 418.7 | 357.8 | 374.9
1389 | 1271 | 525.4 | 463.8 | 495.8 | 464.6 | 393.8 | 381.7 | 381.2 | 418.9 | 358 | 375.1
1390 | 1272 | 525.4 | 463.9 | 495.8 | 464.7 | 393.9 | 381.9 | 381.4 | 419.1 | 358.3 | 375.2
1391 | 1273 | 525.4 | 463.9 | 495.8 | 464.7 | 394.1 | 382 | 381.5 | 419.3 | 358.5 | 375.4
1392 | 1274 | 525.4 | 464 | 495.9 | 464.8 | 394.2 | 382.1 | 381.6 | 419.5 | 358.7 | 375.5
1393 | 1275 | 525.4 | 464 | 495.9 | 464.8 | 394.3 | 382.3 | 381.7 | 419.7 | 359 | 375.7
1394 | 1276 | 525.4 | 464.1 | 495.9 | 464.9 | 394.4 | 382.4 | 381.8 | 419.8 | 359.2 | 375.8
1395 | 1277 | 525.4 | 464.1 | 496 | 464.9 | 394.6 | 382.6 | 382 | 419.9 | 359.4 | 376
1396 | 1278 | 525.4 | 464.1 | 496 | 465 | 394.7 | 382.7 | 382.1 | 420.1 | 359.6 | 376.2
1397 | 1279 | 525.4 | 464.2 | 496 | 465.1 | 394.9 | 382.8 | 382.2 | 420.4 | 359.9 | 376.4
1398 | 1280 | 525.3 | 464.2 | 496.1 | 465.1 | 395 | 383 | 382.3 | 420.6 | 360.1 | 376.5
1399 | 1281 | 525.3 | 464.3 | 496.1 | 465.2 | 395.1 | 383.1 | 382.5 | 420.8 | 360.3 | 376.7
1400 | 1282 | 525.3 | 464.3 | 496.1 | 465.2 | 395.3 | 383.3 | 382.6 | 420.9 | 360.5 | 376.9
1401 | 1283 | 525.3 | 464.4 | 496.2 | 465.3 | 395.4 | 383.4 | 382.7 | 421 | 360.8 | 377.1
1402 | 1284 | 525.2 | 464.4 | 496.2 | 465.3 | 395.5 | 383.6 | 382.8 | 421.2 | 361 | 377.2
1403 | 1285 | 525.2 | 464.5 | 496.3 | 465.4 | 395.7 | 383.7 | 383 | 421.3 | 361.2 | 377.4
1404 | 1286 | 525.2 | 464.5 | 496.3 | 465.5 | 395.8 | 383.9 | 383.1 | 421.4 | 361.5 | 377.6
1405 | 1287 | 525.1 | 464.6 | 496.3 | 465.5 | 396 | 384 | 383.2 | 421.6 | 361.7 | 377.8
1406 | 1288 | 525.1 | 464.6 | 496.3 | 465.6 | 396.1 | 384.2 | 383.3 | 421.7 | 361.9 | 377.9
1407 | 1289 | 525.1 | 464.7 | 496.4 | 465.6 | 396.3 | 384.3 | 383.5 | 421.9 | 362.2 | 378.1
1408 | 1290 | 525 | 464.7 | 496.4 | 465.7 | 396.4 | 384.5 | 383.6 | 422 | 362.4 | 378.3
1409 | 1291 | 525 | 464.8 | 496.4 | 465.7 | 396.6 | 384.6 | 383.7 | 422.2 | 362.7 | 378.4
1410 | 1292 | 525 | 464.8 | 496.4 | 465.8 | 396.7 | 384.8 | 383.9 | 422.3 | 362.9 | 378.6
1411 | 1293 | 525 | 464.9 | 496.5 | 465.8 | 396.9 | 384.9 | 384 | 422.4 | 363.2 | 378.8
1412 | 1294 | 525 | 464.9 | 496.5 | 465.9 | 397 | 385.1 | 384.1 | 422.5 | 363.4 | 378.9
1413 | 1295 | 525 | 465 | 496.5 | 466 | 397.2 | 385.2 | 384.3 | 422.6 | 363.6 | 379.1
1414 | 1296 | 525 | 465 | 496.6 | 466 | 397.3 | 385.3 | 384.4 | 422.8 | 363.9 | 379.3
1415 | 1297 | 525 | 465.1 | 496.6 | 466.1 | 397.5 | 385.5 | 384.5 | 422.9 | 364.1 | 379.4
1416 | 1298 | 525 | 465.1 | 496.6 | 466.1 | 397.6 | 385.7 | 384.7 | 423 | 364.3 | 379.6
1417 | 1299 | 525 | 465.2 | 496.6 | 466.2 | 397.8 | 385.8 | 384.8 | 423.2 | 364.6 | 379.7
1418 | 1300 | 525 | 465.2 | 496.7 | 466.2 | 397.9 | 385.9 | 384.9 | 423.3 | 364.8 | 379.9
1419 | 1301 | 525 | 465.3 | 496.7 | 466.3 | 398 | 386.1 | 385.1 | 423.5 | 365 | 380.1
1420 | 1302 | 525 | 465.3 | 496.8 | 466.3 | 398.2 | 386.2 | 385.2 | 423.6 | 365.2 | 380.2
1421 | 1303 | 525 | 465.3 | 496.8 | 466.4 | 398.3 | 386.4 | 385.3 | 423.8 | 365.5 | 380.4
1422 | 1304 | 525 | 465.4 | 496.8 | 466.5 | 398.4 | 386.5 | 385.5 | 423.9 | 365.7 | 380.6
1423 | 1305 | 525 | 465.4 | 496.8 | 466.5 | 398.6 | 386.7 | 385.6 | 424 | 365.9 | 380.7
1424 | 1306 | 525 | 465.5 | 496.9 | 466.6 | 398.7 | 386.8 | 385.8 | 424.1 | 366.1 | 380.9
1425 | 1307 | 525 | 465.5 | 496.9 | 466.6 | 398.8 | 387 | 385.9 | 424.3 | 366.4 | 381
1426 | 1308 | 525 | 465.5 | 497 | 466.7 | 399 | 387.1 | 386 | 424.4 | 366.6 | 381.2
1427 | 1309 | 525 | 465.6 | 497 | 466.7 | 399.1 | 387.3 | 386.2 | 424.6 | 366.8 | 381.4
1428 | 1310 | 525 | 465.6 | 497 | 466.8 | 399.3 | 387.4 | 386.3 | 424.7 | 367 | 381.5
1429 | 1311 | 525 | 465.7 | 497.1 | 466.8 | 399.4 | 387.6 | 386.5 | 424.8 | 367.2 | 381.7
1430 | 1312 | 525 | 465.7 | 497.1 | 466.9 | 399.6 | 387.7 | 386.6 | 425 | 367.4 | 381.8
1431 | 1313 | 525 | 465.8 | 497.1 | 466.9 | 399.7 | 387.9 | 386.7 | 425 | 367.6 | 382
1432 | 1314 | 525 | 465.8 | 497.1 | 467 | 399.9 | 388.1 | 386.9 | 425.1 | 367.8 | 382.1
1433 | 1315 | 525 | 465.9 | 497.2 | 467 | 400 | 388.2 | 387 | 425.3 | 368.1 | 382.3
1434 | 1316 | 525 | 465.9 | 497.2 | 467.1 | 400.2 | 388.4 | 387.2 | 425.5 | 368.2 | 382.4
1435 | 1317 | 525 | 466 | 497.2 | 467.1 | 400.3 | 388.5 | 387.3 | 425.7 | 368.4 | 382.6
1436 | 1318 | 525 | 466 | 497.3 | 467.2 | 400.5 | 388.7 | 387.5 | 425.8 | 368.6 | 382.8
1437 | 1319 | 525 | 466.1 | 497.3 | 467.3 | 400.7 | 388.8 | 387.6 | 426 | 368.8 | 382.9
1438 | 1320 | 524.9 | 466.1 | 497.3 | 467.3 | 400.8 | 389 | 387.7 | 426.2 | 369 | 383.1
1439 | 1321 | 524.9 | 466.1 | 497.4 | 467.4 | 401 | 389.2 | 387.9 | 426.4 | 369.2 | 383.2
1440 | 1322 | 525 | 466.2 | 497.4 | 467.4 | 401.1 | 389.3 | 388 | 426.5 | 369.4 | 383.4
1441 | 1323 | 524.9 | 466.2 | 497.4 | 467.4 | 401.3 | 389.5 | 388.2 | 426.7 | 369.6 | 383.5
1442 | 1324 | 524.9 | 466.3 | 497.4 | 467.5 | 401.5 | 389.7 | 388.3 | 426.9 | 369.8 | 383.7
1443 | 1325 | 524.9 | 466.3 | 497.5 | 467.6 | 401.7 | 389.8 | 388.5 | 427 | 369.9 | 383.8
1444 | 1326 | 524.9 | 466.4 | 497.5 | 467.6 | 401.8 | 390 | 388.6 | 427.1 | 370.1 | 384
1445 | 1327 | 525 | 466.4 | 497.6 | 467.7 | 402 | 390.1 | 388.8 | 427.2 | 370.3 | 384.1
1446 | 1328 | 525 | 466.4 | 497.6 | 467.7 | 402.2 | 390.3 | 388.9 | 427.3 | 370.5 | 384.3
1447 | 1329 | 525 | 466.5 | 497.6 | 467.7 | 402.3 | 390.5 | 389.1 | 427.5 | 370.7 | 384.4
1448 | 1330 | 525 | 466.5 | 497.7 | 467.8 | 402.5 | 390.6 | 389.2 | 427.6 | 370.8 | 384.6
1449 | 1331 | 525 | 466.6 | 497.7 | 467.8 | 402.7 | 390.8 | 389.4 | 427.8 | 371 | 384.7
1450 | 1332 | 525 | 466.6 | 497.7 | 467.9 | 402.8 | 391 | 389.5 | 427.9 | 371.2 | 384.8
1451 | 1333 | 525 | 466.7 | 497.8 | 468 | 403 | 391.1 | 389.7 | 428 | 371.4 | 385
1452 | 1334 | 525 | 466.7 | 497.8 | 468 | 403.2 | 391.3 | 389.9 | 428.2 | 371.5 | 385.1
1453 | 1335 | 525 | 466.8 | 497.8 | 468 | 403.3 | 391.5 | 390 | 428.3 | 371.7 | 385.2
1454 | 1336 | 525 | 466.8 | 497.8 | 468.1 | 403.5 | 391.6 | 390.2 | 428.6 | 371.9 | 385.4
1455 | 1337 | 525 | 466.8 | 497.9 | 468.2 | 403.7 | 391.8 | 390.3 | 428.8 | 372 | 385.5
1456 | 1338 | 525 | 466.9 | 497.9 | 468.2 | 403.9 | 392 | 390.5 | 429 | 372.2 | 385.6
1457 | 1339 | 525 | 466.9 | 498 | 468.2 | 404 | 392.2 | 390.6 | 429.3 | 372.4 | 385.8
1458 | 1340 | 525 | 467 | 498 | 468.3 | 404.2 | 392.3 | 390.8 | 429.5 | 372.5 | 385.9
1459 | 1341 | 525 | 467 | 498 | 468.4 | 404.3 | 392.5 | 391 | 429.7 | 372.7 | 386
1460 | 1342 | 525 | 467.1 | 498 | 468.4 | 404.5 | 392.7 | 391.2 | 429.8 | 372.8 | 386.2
1461 | 1343 | 525 | 467.1 | 498.1 | 468.4 | 404.6 | 392.9 | 391.3 | 430.1 | 373 | 386.3
1462 | 1344 | 525 | 467.1 | 498.1 | 468.5 | 404.8 | 393.1 | 391.5 | 430.2 | 373.1 | 386.4
1463 | 1345 | 525 | 467.2 | 498.1 | 468.5 | 405 | 393.3 | 391.6 | 430.3 | 373.3 | 386.6
1464 | 1346 | 525 | 467.2 | 498.1 | 468.6 | 405.1 | 393.4 | 391.8 | 430.5 | 373.4 | 386.7
1465 | 1347 | 525 | 467.3 | 498.1 | 468.7 | 405.3 | 393.6 | 392 | 430.7 | 373.6 | 386.9
1466 | 1348 | 525 | 467.3 | 498.2 | 468.7 | 405.5 | 393.8 | 392.1 | 430.8 | 373.7 | 387
1467 | 1349 | 525 | 467.3 | 498.2 | 468.7 | 405.7 | 394 | 392.3 | 431 | 373.9 | 387.2
1468 | 1350 | 525 | 467.4 | 498.2 | 468.8 | 405.8 | 394.2 | 392.5 | 431.2 | 374 | 387.3
1469 | 1351 | 525 | 467.4 | 498.3 | 468.8 | 406 | 394.4 | 392.7 | 431.4 | 374.2 | 387.4
1470 | 1352 | 525 | 467.5 | 498.3 | 468.9 | 406.1 | 394.6 | 392.8 | 431.6 | 374.3 | 387.6
1471 | 1353 | 525 | 467.5 | 498.3 | 468.9 | 406.3 | 394.7 | 393 | 431.8 | 374.5 | 387.7
1472 | 1354 | 525 | 467.6 | 498.3 | 469 | 406.4 | 394.9 | 393.2 | 432 | 374.6 | 387.8
1473 | 1355 | 525 | 467.6 | 498.4 | 469 | 406.6 | 395.1 | 393.4 | 432.1 | 374.8 | 388
1474 | 1356 | 525 | 467.6 | 498.4 | 469.1 | 406.8 | 395.3 | 393.5 | 432.3 | 374.9 | 388.1
1475 | 1357 | 525 | 467.7 | 498.4 | 469.1 | 406.9 | 395.5 | 393.7 | 432.5 | 375.1 | 388.3
1476 | 1358 | 525 | 467.7 | 498.5 | 469.2 | 407.1 | 395.7 | 393.9 | 432.7 | 375.2 | 388.4
1477 | 1359 | 525 | 467.8 | 498.5 | 469.2 | 407.3 | 395.9 | 394.1 | 432.8 | 375.3 | 388.5
1478 | 1360 | 525.1 | 467.8 | 498.5 | 469.3 | 407.5 | 396.1 | 394.2 | 433 | 375.5 | 388.6
1479 | 1361 | 525.1 | 467.8 | 498.6 | 469.3 | 407.6 | 396.3 | 394.4 | 433.2 | 375.6 | 388.7
1480 | 1362 | 525.1 | 467.9 | 498.6 | 469.4 | 407.8 | 396.5 | 394.6 | 433.4 | 375.8 | 388.9
1481 | 1363 | 525.2 | 467.9 | 498.6 | 469.4 | 407.9 | 396.7 | 394.8 | 433.5 | 375.9 | 389
1482 | 1364 | 525.2 | 468 | 498.6 | 469.4 | 408.1 | 396.9 | 395 | 433.7 | 376 | 389.1
1483 | 1365 | 525.2 | 468 | 498.7 | 469.5 | 408.3 | 397.1 | 395.2 | 433.8 | 376.2 | 389.2
1484 | 1366 | 525.2 | 468.1 | 498.7 | 469.5 | 408.5 | 397.4 | 395.4 | 433.9 | 376.3 | 389.4
1485 | 1367 | 525.2 | 468.1 | 498.7 | 469.6 | 408.6 | 397.6 | 395.6 | 434.1 | 376.5 | 389.5
1486 | 1368 | 525.2 | 468.1 | 498.7 | 469.6 | 408.8 | 397.8 | 395.8 | 434.3 | 376.6 | 389.6
1487 | 1369 | 525.2 | 468.2 | 498.7 | 469.7 | 409 | 398 | 396 | 434.4 | 376.7 | 389.7
1488 | 1370 | 525.2 | 468.2 | 498.8 | 469.7 | 409.2 | 398.2 | 396.2 | 434.5 | 376.9 | 389.8
1489 | 1371 | 525.2 | 468.3 | 498.8 | 469.8 | 409.3 | 398.5 | 396.4 | 434.6 | 377 | 390
1490 | 1372 | 525.2 | 468.3 | 498.9 | 469.8 | 409.5 | 398.7 | 396.6 | 434.8 | 377.1 | 390.1
1491 | 1373 | 525.3 | 468.4 | 498.9 | 469.9 | 409.7 | 398.9 | 396.8 | 434.9 | 377.3 | 390.2
1492 | 1374 | 525.3 | 468.4 | 498.9 | 469.9 | 409.9 | 399.1 | 397 | 435.1 | 377.4 | 390.3
1493 | 1375 | 525.3 | 468.5 | 498.9 | 469.9 | 410 | 399.3 | 397.2 | 435.1 | 377.5 | 390.4
1494 | 1376 | 525.3 | 468.5 | 499 | 470 | 410.2 | 399.5 | 397.4 | 435.1 | 377.7 | 390.5
1495 | 1377 | 525.3 | 468.5 | 499 | 470 | 410.4 | 399.8 | 397.6 | 435.3 | 377.8 | 390.7
1496 | 1378 | 525.3 | 468.6 | 499 | 470.1 | 410.5 | 400 | 397.8 | 435.5 | 378 | 390.8
1497 | 1379 | 525.3 | 468.6 | 499.1 | 470.1 | 410.7 | 400.2 | 398 | 435.7 | 378.1 | 390.9
1498 | 1380 | 525.3 | 468.7 | 499.1 | 470.2 | 410.9 | 400.4 | 398.2 | 435.9 | 378.2 | 391
1499 | 1381 | 525.3 | 468.7 | 499.1 | 470.2 | 411 | 400.6 | 398.4 | 436 | 378.4 | 391.1
1500 | 1382 | 525.3 | 468.8 | 499.1 | 470.3 | 411.2 | 400.9 | 398.6 | 436.1 | 378.5 | 391.2
1501 | 1383 | 525.3 | 468.8 | 499.2 | 470.3 | 411.4 | 401.1 | 398.8 | 436.3 | 378.6 | 391.3
1502 | 1384 | 525.3 | 468.8 | 499.2 | 470.4 | 411.5 | 401.3 | 399 | 436.5 | 378.8 | 391.4
1503 | 1385 | 525.3 | 468.9 | 499.2 | 470.4 | 411.7 | 401.6 | 399.2 | 436.6 | 378.9 | 391.5
1504 | 1386 | 525.3 | 468.9 | 499.3 | 470.4 | 412 | 401.8 | 399.4 | 436.8 | 379 | 391.6
1505 | 1387 | 525.3 | 469 | 499.3 | 470.5 | 412.2 | 402 | 399.6 | 437 | 379.2 | 391.7
1506 | 1388 | 525.3 | 469 | 499.3 | 470.5 | 412.4 | 402.2 | 399.8 | 437.1 | 379.3 | 391.8
1507 | 1389 | 525.3 | 469 | 499.3 | 470.6 | 412.7 | 402.5 | 400 | 437.3 | 379.4 | 391.9
1508 | 1390 | 525.3 | 469.1 | 499.3 | 470.6 | 412.9 | 402.7 | 400.2 | 437.4 | 379.6 | 392
1509 | 1391 | 525.3 | 469.1 | 499.4 | 470.7 | 413.1 | 402.9 | 400.4 | 437.6 | 379.7 | 392.1
1510 | 1392 | 525.3 | 469.2 | 499.4 | 470.7 | 413.4 | 403.1 | 400.6 | 437.8 | 379.8 | 392.2
1511 | 1393 | 525.4 | 469.2 | 499.4 | 470.7 | 413.6 | 403.4 | 400.8 | 438 | 380 | 392.4
1512 | 1394 | 525.3 | 469.2 | 499.5 | 470.8 | 413.7 | 403.6 | 401.1 | 438.1 | 380.1 | 392.5
1513 | 1395 | 525.3 | 469.3 | 499.5 | 470.8 | 414 | 403.8 | 401.3 | 438.3 | 380.2 | 392.6
1514 | 1396 | 525.3 | 469.3 | 499.5 | 470.9 | 414.3 | 404 | 401.5 | 438.5 | 380.4 | 392.8
1515 | 1397 | 525.3 | 469.4 | 499.6 | 470.9 | 414.5 | 404.2 | 401.7 | 438.6 | 380.5 | 392.9
1516 | 1398 | 525.3 | 469.4 | 499.6 | 471 | 414.6 | 404.5 | 401.9 | 438.8 | 380.6 | 393
1517 | 1399 | 525.3 | 469.4 | 499.6 | 471 | 415 | 404.7 | 402.1 | 439 | 380.8 | 393.2
1518 | 1400 | 525.2 | 469.5 | 499.6 | 471.1 | 415.2 | 404.9 | 402.3 | 439.2 | 380.9 | 393.4
1519 | 1401 | 525.2 | 469.5 | 499.7 | 471.1 | 415.4 | 405.1 | 402.5 | 439.4 | 381 | 393.5
1520 | 1402 | 525.2 | 469.6 | 499.7 | 471.1 | 415.6 | 405.4 | 402.7 | 439.5 | 381.2 | 393.6
1521 | 1403 | 525.2 | 469.6 | 499.7 | 471.2 | 415.8 | 405.6 | 402.9 | 439.7 | 381.3 | 393.7
1522 | 1404 | 525.2 | 469.6 | 499.7 | 471.2 | 415.9 | 405.8 | 403.1 | 439.9 | 381.5 | 393.8
1523 | 1405 | 525.1 | 469.7 | 499.7 | 471.3 | 416.1 | 406 | 403.3 | 440 | 381.6 | 393.9
1524 | 1406 | 525.1 | 469.7 | 499.8 | 471.3 | 416.4 | 406.2 | 403.5 | 440.2 | 381.7 | 394
1525 | 1407 | 525.1 | 469.7 | 499.8 | 471.3 | 416.5 | 406.5 | 403.7 | 440.5 | 381.9 | 394.1
1526 | 1408 | 525.2 | 469.8 | 499.9 | 471.4 | 416.7 | 406.7 | 403.9 | 440.6 | 382 | 394.2
1527 | 1409 | 525.2 | 469.8 | 499.9 | 471.4 | 417 | 406.9 | 404.1 | 440.8 | 382.1 | 394.3
1528 | 1410 | 525.2 | 469.9 | 499.9 | 471.5 | 417.2 | 407.1 | 404.3 | 441 | 382.3 | 394.4
1529 | 1411 | 525.2 | 469.9 | 499.9 | 471.5 | 417.3 | 407.3 | 404.5 | 441.2 | 382.4 | 394.5
1530 | 1412 | 525.2 | 469.9 | 499.9 | 471.5 | 417.5 | 407.5 | 404.7 | 441.5 | 382.5 | 394.6
1531 | 1413 | 525.2 | 469.9 | 500 | 471.5 | 417.5 | 407.7 | 404.9 | 441.7 | 382.7 | 394.7
1532 | 1414 | 525.2 | 469.8 | 500.2 | 471.5 | 417.6 | 407.8 | 405.2 | 441.9 | 382.8 | 394.9
1533 | 1415 | 525.3 | 469.9 | 500.2 | 471.5 | 417.8 | 408 | 405.4 | 442.1 | 382.9 | 395
1534 | 1416 | 525.3 | 469.9 | 500.2 | 471.6 | 417.9 | 408.2 | 405.6 | 442.2 | 383.1 | 395.1
1535 | 1417 | 525.3 | 469.9 | 500.3 | 471.6 | 418.1 | 408.4 | 405.8 | 442.4 | 383.2 | 395.2
1536 | 1418 | 525.3 | 470 | 500.3 | 471.6 | 418.2 | 408.6 | 406 | 442.6 | 383.3 | 395.3
1537 | 1419 | 525.3 | 470 | 500.3 | 471.7 | 418.4 | 408.8 | 406.2 | 442.9 | 383.5 | 395.4
1538 | 1420 | 525.3 | 470.1 | 500.4 | 471.7 | 418.6 | 409 | 406.4 | 443.1 | 383.6 | 395.4
1539 | 1421 | 525.3 | 470.1 | 500.4 | 471.8 | 418.9 | 409.3 | 406.6 | 443.2 | 383.7 | 395.5
1540 | 1422 | 525.3 | 470.1 | 500.4 | 471.8 | 419 | 409.5 | 406.8 | 443.4 | 383.9 | 395.6
1541 | 1423 | 525.3 | 470.2 | 500.5 | 471.8 | 419.1 | 409.7 | 407 | 443.6 | 384 | 395.7
1542 | 1424 | 525.3 | 470.2 | 500.5 | 471.9 | 419.3 | 409.9 | 407.2 | 443.8 | 384.1 | 395.8
1543 | 1425 | 525.3 | 470.3 | 500.5 | 471.9 | 419.5 | 410.1 | 407.4 | 444 | 384.3 | 395.9
1544 | 1426 | 525.4 | 470.3 | 500.5 | 472 | 419.6 | 410.3 | 407.6 | 444.1 | 384.4 | 396
1545 | 1427 | 525.4 | 470.3 | 500.6 | 472 | 419.8 | 410.5 | 407.7 | 444.4 | 384.6 | 396
1546 | 1428 | 525.3 | 470.4 | 500.6 | 472 | 419.9 | 410.7 | 407.9 | 444.5 | 384.7 | 396.1
1547 | 1429 | 525.3 | 470.4 | 500.6 | 472.1 | 420.1 | 410.9 | 408.1 | 444.5 | 384.8 | 396.2
1548 | 1430 | 525.3 | 470.4 | 500.6 | 472.1 | 420.3 | 411.1 | 408.3 | 444.7 | 385 | 396.4
1549 | 1431 | 525.3 | 470.5 | 500.7 | 472.2 | 420.4 | 411.3 | 408.5 | 444.8 | 385.1 | 396.5
1550 | 1432 | 525.3 | 470.5 | 500.7 | 472.2 | 420.7 | 411.5 | 408.7 | 445 | 385.2 | 396.6
1551 | 1433 | 525.3 | 470.5 | 500.7 | 472.2 | 420.8 | 411.7 | 408.9 | 445.2 | 385.4 | 396.6
1552 | 1434 | 525.3 | 470.6 | 500.7 | 472.3 | 420.9 | 411.9 | 409.1 | 445.4 | 385.5 | 396.8
1553 | 1435 | 525.3 | 470.6 | 500.8 | 472.3 | 421 | 412.1 | 409.3 | 445.6 | 385.6 | 396.9
1554 | 1436 | 525.2 | 470.6 | 500.8 | 472.3 | 421.2 | 412.3 | 409.5 | 446 | 385.8 | 397
1555 | 1437 | 525.2 | 470.7 | 500.8 | 472.4 | 421.3 | 412.5 | 409.6 | 446.4 | 385.9 | 397.1
1556 | 1438 | 525.2 | 470.7 | 500.8 | 472.4 | 421.4 | 412.7 | 409.8 | 446.9 | 386 | 397.2
1557 | 1439 | 525.2 | 470.7 | 500.8 | 472.4 | 421.6 | 412.9 | 410 | 447.4 | 386.2 | 397.3
1558 | 1440 | 525.2 | 470.8 | 500.9 | 472.5 | 421.7 | 413.1 | 410.2 | 447.8 | 386.3 | 397.4
1559 | 1441 | 525.2 | 470.8 | 500.9 | 472.5 | 422 | 413.3 | 410.4 | 448.1 | 386.5 | 397.5
1560 | 1442 | 525.1 | 470.9 | 500.9 | 472.5 | 422.1 | 413.5 | 410.5 | 448.4 | 386.6 | 397.7
1561 | 1443 | 525.1 | 470.9 | 500.9 | 472.6 | 422.3 | 413.7 | 410.7 | 448.7 | 386.7 | 397.8
1562 | 1444 | 525.1 | 470.9 | 501 | 472.6 | 422.4 | 413.8 | 410.9 | 448.9 | 386.9 | 397.9
1563 | 1445 | 525 | 471 | 501 | 472.7 | 422.5 | 414 | 411.1 | 449.1 | 387 | 398.1
1564 | 1446 | 525 | 471 | 501 | 472.7 | 422.7 | 414.2 | 411.2 | 449.3 | 387.2 | 398.2
1565 | 1447 | 525 | 471 | 501 | 472.7 | 422.8 | 414.4 | 411.4 | 449.6 | 387.3 | 398.3
1566 | 1448 | 524.9 | 471.1 | 501 | 472.8 | 423 | 414.6 | 411.6 | 449.8 | 387.4 | 398.5
1567 | 1449 | 524.9 | 471.1 | 501.1 | 472.8 | 423.1 | 414.8 | 411.8 | 450.1 | 387.6 | 398.6
1568 | 1450 | 524.8 | 471.1 | 501.1 | 472.8 | 423.3 | 415 | 411.9 | 450.3 | 387.7 | 398.7
1569 | 1451 | 524.8 | 471.2 | 501.1 | 472.9 | 423.5 | 415.2 | 412.1 | 450.5 | 387.8 | 398.8
1570 | 1452 | 524.8 | 471.2 | 501.1 | 472.9 | 423.7 | 415.4 | 412.3 | 450.6 | 388 | 398.9
1571 | 1453 | 524.9 | 471.2 | 501.1 | 472.9 | 423.9 | 415.6 | 412.5 | 450.8 | 388.1 | 399
1572 | 1454 | 524.9 | 471.3 | 501.2 | 473 | 424 | 415.7 | 412.6 | 451 | 388.2 | 399.1
1573 | 1455 | 524.9 | 471.3 | 501.2 | 473 | 424.2 | 415.9 | 412.8 | 451.2 | 388.4 | 399.2
1574 | 1456 | 524.9 | 471.3 | 501.2 | 473.1 | 424.3 | 416.1 | 413 | 451.3 | 388.5 | 399.3
1575 | 1457 | 524.9 | 471.4 | 501.3 | 473.1 | 424.4 | 416.3 | 413.2 | 451.4 | 388.7 | 399.4
1576 | 1458 | 524.9 | 471.4 | 501.3 | 473.1 | 424.6 | 416.5 | 413.3 | 451.6 | 388.8 | 399.5
1577 | 1459 | 524.9 | 471.5 | 501.3 | 473.2 | 424.7 | 416.6 | 413.5 | 451.8 | 388.9 | 399.6
1578 | 1460 | 524.9 | 471.5 | 501.3 | 473.2 | 424.8 | 416.8 | 413.7 | 452 | 389.1 | 399.7
1579 | 1461 | 524.9 | 471.5 | 501.3 | 473.2 | 425 | 417 | 413.8 | 452 | 389.2 | 399.8
1580 | 1462 | 524.9 | 471.6 | 501.4 | 473.3 | 425.1 | 417.2 | 414 | 452.2 | 389.3 | 399.9
1581 | 1463 | 524.9 | 471.6 | 501.4 | 473.3 | 425.3 | 417.4 | 414.2 | 452.3 | 389.5 | 400
1582 | 1464 | 525 | 471.6 | 501.4 | 473.3 | 425.4 | 417.6 | 414.3 | 452.4 | 389.6 | 400.1
1583 | 1465 | 525 | 471.7 | 501.4 | 473.4 | 425.6 | 417.7 | 414.5 | 452.6 | 389.7 | 400.2
1584 | 1466 | 525 | 471.7 | 501.4 | 473.4 | 425.7 | 417.9 | 414.7 | 452.7 | 389.9 | 400.3
1585 | 1467 | 525.1 | 471.7 | 501.5 | 473.4 | 425.9 | 418.1 | 414.8 | 452.9 | 390 | 400.4
1586 | 1468 | 525.1 | 471.8 | 501.5 | 473.5 | 426 | 418.3 | 415 | 453 | 390.1 | 400.5
1587 | 1469 | 525.1 | 471.8 | 501.5 | 473.5 | 426.1 | 418.4 | 415.2 | 453.2 | 390.3 | 400.6
1588 | 1470 | 525.1 | 471.8 | 501.5 | 473.5 | 426.2 | 418.6 | 415.3 | 453.3 | 390.4 | 400.7
1589 | 1471 | 525.1 | 471.8 | 501.6 | 473.6 | 426.3 | 418.8 | 415.5 | 453.5 | 390.5 | 400.8
1590 | 1472 | 525.2 | 471.9 | 501.6 | 473.6 | 426.5 | 418.9 | 415.6 | 453.6 | 390.7 | 400.9
1591 | 1473 | 525.2 | 471.9 | 501.6 | 473.6 | 426.6 | 419.1 | 415.8 | 453.8 | 390.8 | 401
1592 | 1474 | 525.2 | 472 | 501.6 | 473.7 | 426.8 | 419.3 | 416 | 453.9 | 391 | 401.1
1593 | 1475 | 525.2 | 472 | 501.7 | 473.7 | 426.9 | 419.5 | 416.1 | 454.2 | 391.1 | 401.3
1594 | 1476 | 525.2 | 472 | 501.7 | 473.7 | 427 | 419.6 | 416.3 | 454.2 | 391.2 | 401.3
1595 | 1477 | 525.2 | 472 | 501.7 | 473.8 | 427.1 | 419.8 | 416.4 | 454.3 | 391.4 | 401.4
1596 | 1478 | 525.1 | 472.1 | 501.7 | 473.8 | 427.2 | 420 | 416.6 | 454.4 | 391.5 | 401.5
1597 | 1479 | 525.2 | 472.1 | 501.7 | 473.8 | 427.4 | 420.2 | 416.8 | 454.6 | 391.6 | 401.6
1598 | 1480 | 525.2 | 472.1 | 501.8 | 473.9 | 427.5 | 420.3 | 416.9 | 454.8 | 391.8 | 401.7
1599 | 1481 | 525.1 | 472.2 | 501.8 | 473.9 | 427.6 | 420.5 | 417.1 | 454.9 | 391.9 | 401.8
1600 | 1482 | 525.1 | 472.2 | 501.8 | 473.9 | 427.8 | 420.7 | 417.2 | 455.1 | 392 | 401.9
1601 | 1483 | 525.1 | 472.2 | 501.8 | 474 | 427.9 | 420.8 | 417.4 | 455.2 | 392.2 | 402
1602 | 1484 | 525.1 | 472.3 | 501.8 | 474 | 428 | 421 | 417.6 | 455.3 | 392.3 | 402.1
1603 | 1485 | 525.1 | 472.3 | 501.9 | 474.1 | 428.1 | 421.1 | 417.7 | 455.3 | 392.4 | 402.2
1604 | 1486 | 525.1 | 472.3 | 501.9 | 474.1 | 428.3 | 421.3 | 417.9 | 455.4 | 392.6 | 402.3
1605 | 1487 | 525.1 | 472.4 | 501.9 | 474.1 | 428.4 | 421.5 | 418 | 455.5 | 392.7 | 402.4
1606 | 1488 | 525.1 | 472.4 | 501.9 | 474.1 | 428.5 | 421.6 | 418.2 | 455.6 | 392.8 | 402.5
1607 | 1489 | 525.1 | 472.4 | 501.9 | 474.2 | 428.7 | 421.8 | 418.3 | 455.7 | 392.9 | 402.6
1608 | 1490 | 525.1 | 472.5 | 501.9 | 474.2 | 428.8 | 421.9 | 418.5 | 456 | 393.1 | 402.8
1609 | 1491 | 525.1 | 472.5 | 502 | 474.2 | 428.9 | 422.1 | 418.6 | 456 | 393.2 | 402.9
1610 | 1492 | 525.1 | 472.5 | 502 | 474.3 | 429 | 422.3 | 418.8 | 456.2 | 393.4 | 403
1611 | 1493 | 525.1 | 472.6 | 502 | 474.3 | 429.1 | 422.4 | 418.9 | 456.3 | 393.5 | 403.1
1612 | 1494 | 525.2 | 472.6 | 502.1 | 474.3 | 429.2 | 422.6 | 419.1 | 456.4 | 393.6 | 403.3
1613 | 1495 | 525.2 | 472.6 | 502.1 | 474.4 | 429.4 | 422.7 | 419.3 | 456.6 | 393.8 | 403.4
1614 | 1496 | 525.2 | 472.7 | 502.1 | 474.4 | 429.5 | 422.9 | 419.4 | 456.7 | 393.9 | 403.5
1615 | 1497 | 525.2 | 472.7 | 502.1 | 474.4 | 429.6 | 423 | 419.6 | 456.7 | 394 | 403.6
1616 | 1498 | 525.2 | 472.7 | 502.1 | 474.5 | 429.7 | 423.2 | 419.7 | 456.8 | 394.1 | 403.7
1617 | 1499 | 525.3 | 472.7 | 502.1 | 474.5 | 429.9 | 423.4 | 419.9 | 457 | 394.3 | 403.8
1618 | 1500 | 525.3 | 472.8 | 502.2 | 474.5 | 430 | 423.5 | 420 | 457.1 | 394.4 | 404
1619 | 1501 | 525.3 | 472.8 | 502.2 | 474.6 | 430.1 | 423.7 | 420.1 | 457.3 | 394.5 | 404.1
1620 | 1502 | 525.3 | 472.8 | 502.2 | 474.6 | 430.3 | 423.8 | 420.3 | 457.4 | 394.7 | 404.1
1621 | 1503 | 525.3 | 472.9 | 502.2 | 474.6 | 430.4 | 424 | 420.5 | 457.6 | 394.8 | 404.3
1622 | 1504 | 525.3 | 472.9 | 502.2 | 474.7 | 430.6 | 424.1 | 420.6 | 457.6 | 394.9 | 404.4
1623 | 1505 | 525.3 | 472.9 | 502.2 | 474.7 | 430.7 | 424.3 | 420.7 | 457.7 | 395.1 | 404.5
1624 | 1506 | 525.3 | 473 | 502.3 | 474.7 | 430.8 | 424.4 | 420.9 | 457.6 | 395.2 | 404.6
1625 | 1507 | 525.3 | 473 | 502.3 | 474.8 | 430.9 | 424.6 | 421 | 457.6 | 395.3 | 404.7
1626 | 1508 | 525.3 | 473 | 502.3 | 474.8 | 431 | 424.7 | 421.2 | 457.7 | 395.5 | 404.8
1627 | 1509 | 525.3 | 473.1 | 502.3 | 474.8 | 431.1 | 424.9 | 421.3 | 457.8 | 395.6 | 404.9
1628 | 1510 | 525.3 | 473.1 | 502.3 | 474.9 | 431.2 | 425.1 | 421.5 | 457.9 | 395.7 | 405
1629 | 1511 | 525.2 | 473.1 | 502.3 | 474.9 | 431.4 | 425.2 | 421.6 | 458 | 395.8 | 405.1
1630 | 1512 | 525.2 | 473.2 | 502.4 | 474.9 | 431.5 | 425.4 | 421.8 | 458.1 | 396 | 405.2
1631 | 1513 | 525.2 | 473.2 | 502.4 | 475 | 431.6 | 425.5 | 421.9 | 458.3 | 396.1 | 405.3
1632 | 1514 | 525.2 | 473.2 | 502.4 | 475 | 431.8 | 425.7 | 422 | 458.3 | 396.2 | 405.4
1633 | 1515 | 525.2 | 473.2 | 502.4 | 475 | 431.9 | 425.8 | 422.2 | 458.3 | 396.4 | 405.5
1634 | 1516 | 525.2 | 473.3 | 502.4 | 475.1 | 432 | 426 | 422.3 | 458.2 | 396.5 | 405.6
1635 | 1517 | 525.2 | 473.3 | 502.4 | 475.1 | 432.1 | 426.1 | 422.5 | 458.2 | 396.6 | 405.7
1636 | 1518 | 525.2 | 473.3 | 502.4 | 475.1 | 432.2 | 426.3 | 422.6 | 458.3 | 396.8 | 405.8
1637 | 1519 | 525.2 | 473.4 | 502.5 | 475.2 | 432.3 | 426.4 | 422.8 | 458.5 | 396.9 | 405.9
1638 | 1520 | 525.1 | 473.4 | 502.5 | 475.2 | 432.5 | 426.6 | 422.9 | 458.6 | 397 | 406
1639 | 1521 | 525.1 | 473.4 | 502.5 | 475.2 | 432.6 | 426.7 | 423 | 458.8 | 397.2 | 406.1
1640 | 1522 | 525.1 | 473.5 | 502.5 | 475.3 | 432.7 | 426.9 | 423.2 | 458.9 | 397.3 | 406.2
1641 | 1523 | 525.1 | 473.5 | 502.5 | 475.3 | 432.8 | 427 | 423.3 | 459.1 | 397.4 | 406.3
1642 | 1524 | 525.1 | 473.5 | 502.5 | 475.3 | 433 | 427.2 | 423.5 | 459 | 397.6 | 406.4
1643 | 1525 | 525.1 | 473.6 | 502.6 | 475.4 | 433.1 | 427.3 | 423.6 | 459.1 | 397.7 | 406.5
1644 | 1526 | 525 | 473.6 | 502.6 | 475.4 | 433.2 | 427.5 | 423.7 | 459.1 | 397.8 | 406.6
1645 | 1527 | 525 | 473.6 | 502.6 | 475.4 | 433.3 | 427.6 | 423.9 | 459 | 398 | 406.7
1646 | 1528 | 525 | 473.6 | 502.6 | 475.5 | 433.4 | 427.8 | 424 | 458.9 | 398.1 | 406.8
1647 | 1529 | 525 | 473.7 | 502.6 | 475.5 | 433.5 | 428 | 424.2 | 459 | 398.2 | 406.9
1648 | 1530 | 525 | 473.7 | 502.6 | 475.5 | 433.6 | 428.1 | 424.3 | 459.2 | 398.4 | 407
1649 | 1531 | 524.9 | 473.7 | 502.6 | 475.6 | 433.7 | 428.3 | 424.4 | 459.3 | 398.5 | 407.1
1650 | 1532 | 524.9 | 473.8 | 502.6 | 475.6 | 433.9 | 428.4 | 424.6 | 459.2 | 398.6 | 407.2
1651 | 1533 | 524.9 | 473.8 | 502.6 | 475.6 | 434 | 428.6 | 424.7 | 459.2 | 398.8 | 407.3
1652 | 1534 | 524.9 | 473.8 | 502.7 | 475.7 | 434.1 | 428.8 | 424.8 | 459.2 | 398.9 | 407.3
1653 | 1535 | 524.9 | 473.9 | 502.7 | 475.7 | 434.2 | 428.9 | 425 | 459.2 | 399 | 407.4
1654 | 1536 | 524.9 | 473.9 | 502.7 | 475.7 | 434.4 | 429.1 | 425.1 | 459.2 | 399.1 | 407.5
1655 | 1537 | 524.9 | 473.9 | 502.7 | 475.7 | 434.5 | 429.3 | 425.2 | 459.3 | 399.3 | 407.6
1656 | 1538 | 524.9 | 473.9 | 502.7 | 475.8 | 434.6 | 429.4 | 425.4 | 459.4 | 399.4 | 407.6
1657 | 1539 | 525 | 474 | 502.7 | 475.8 | 434.7 | 429.6 | 425.5 | 459.4 | 399.5 | 407.7
1658 | 1540 | 525 | 474 | 502.7 | 475.8 | 434.8 | 429.8 | 425.6 | 459.5 | 399.7 | 407.8
1659 | 1541 | 525 | 474 | 502.7 | 475.9 | 434.9 | 429.9 | 425.8 | 459.5 | 399.8 | 407.9
1660 | 1542 | 525 | 474.1 | 502.8 | 475.9 | 435 | 430.1 | 425.9 | 459.6 | 399.9 | 408
1661 | 1543 | 525 | 474.1 | 502.7 | 475.9 | 435.1 | 430.2 | 426 | 459.7 | 400 | 408.1
1662 | 1544 | 525 | 474.1 | 502.8 | 476 | 435.2 | 430.4 | 426.2 | 459.8 | 400.2 | 408.2
1663 | 1545 | 525 | 474.2 | 502.8 | 476 | 435.3 | 430.6 | 426.3 | 459.7 | 400.3 | 408.2
1664 | 1546 | 525 | 474.2 | 502.8 | 476 | 435.4 | 430.7 | 426.4 | 459.6 | 400.4 | 408.3
1665 | 1547 | 525.1 | 474.2 | 502.8 | 476.1 | 435.5 | 430.9 | 426.6 | 459.7 | 400.6 | 408.4
1666 | 1548 | 525.1 | 474.2 | 502.8 | 476.1 | 435.5 | 431 | 426.7 | 459.8 | 400.7 | 408.5
1667 | 1549 | 525.1 | 474.3 | 502.8 | 476.1 | 435.6 | 431.2 | 426.9 | 459.9 | 400.8 | 408.6
1668 | 1550 | 525.1 | 474.3 | 502.9 | 476.1 | 435.7 | 431.3 | 427 | 459.8 | 400.9 | 408.7
1669 | 1551 | 525.2 | 474.3 | 502.9 | 476.2 | 435.8 | 431.5 | 427.1 | 459.7 | 401.1 | 408.7
1670 | 1552 | 525.2 | 474.4 | 502.9 | 476.2 | 435.9 | 431.6 | 427.3 | 459.7 | 401.2 | 408.8
1671 | 1553 | 525.2 | 474.4 | 502.9 | 476.2 | 436 | 431.8 | 427.4 | 459.8 | 401.3 | 408.9
1672 | 1554 | 525.2 | 474.4 | 502.9 | 476.3 | 436.1 | 431.9 | 427.6 | 459.6 | 401.5 | 409
1673 | 1555 | 525.2 | 474.5 | 502.9 | 476.3 | 436.2 | 432.1 | 427.7 | 459.6 | 401.6 | 409.1
1674 | 1556 | 525.3 | 474.5 | 502.9 | 476.3 | 436.3 | 432.2 | 427.8 | 459.8 | 401.7 | 409.2
1675 | 1557 | 525.3 | 474.5 | 502.9 | 476.4 | 436.4 | 432.3 | 428 | 459.7 | 401.9 | 409.3
1676 | 1558 | 525.3 | 474.5 | 502.9 | 476.4 | 436.5 | 432.5 | 428.1 | 459.6 | 402 | 409.4
1677 | 1559 | 525.3 | 474.6 | 502.9 | 476.4 | 436.6 | 432.6 | 428.2 | 459.6 | 402.1 | 409.4
1678 | 1560 | 525.3 | 474.6 | 503 | 476.5 | 436.7 | 432.7 | 428.4 | 459.5 | 402.3 | 409.5
1679 | 1561 | 525.3 | 474.6 | 503 | 476.5 | 436.9 | 432.9 | 428.5 | 459.4 | 402.4 | 409.6
1680 | 1562 | 525.3 | 474.7 | 503 | 476.5 | 437 | 433 | 428.6 | 459.4 | 402.5 | 409.7
1681 | 1563 | 525.3 | 474.7 | 503 | 476.6 | 437.1 | 433.2 | 428.7 | 459.5 | 402.7 | 409.8
1682 | 1564 | 525.3 | 474.7 | 503 | 476.6 | 437.2 | 433.3 | 428.9 | 459.6 | 402.8 | 409.8
1683 | 1565 | 525.3 | 474.8 | 503 | 476.6 | 437.3 | 433.4 | 429 | 459.5 | 403 | 409.9
1684 | 1566 | 525.3 | 474.8 | 503 | 476.7 | 437.4 | 433.5 | 429.1 | 459.4 | 403.1 | 410
1685 | 1567 | 525.3 | 474.8 | 503 | 476.7 | 437.5 | 433.7 | 429.2 | 459.5 | 403.3 | 410.1
1686 | 1568 | 525.3 | 474.9 | 503 | 476.7 | 437.6 | 433.8 | 429.4 | 459.7 | 403.5 | 410.2
1687 | 1569 | 525.3 | 474.9 | 503 | 476.7 | 437.7 | 433.9 | 429.5 | 459.6 | 403.6 | 410.2
1688 | 1570 | 525.4 | 474.9 | 503 | 476.8 | 437.8 | 434 | 429.6 | 459.6 | 403.8 | 410.3
1689 | 1571 | 525.4 | 474.9 | 503 | 476.8 | 438 | 434.2 | 429.8 | 459.6 | 403.9 | 410.4
1690 | 1572 | 525.3 | 475 | 503.1 | 476.8 | 438.1 | 434.3 | 429.9 | 459.5 | 404.1 | 410.5
1691 | 1573 | 525.3 | 475 | 503.1 | 476.9 | 438.2 | 434.4 | 430.1 | 459.5 | 404.2 | 410.6
1692 | 1574 | 525.3 | 475 | 503.1 | 476.9 | 438.3 | 434.5 | 430.2 | 459.5 | 404.4 | 410.6
1693 | 1575 | 525.3 | 475.1 | 503.1 | 476.9 | 438.4 | 434.7 | 430.4 | 459.6 | 404.5 | 410.7
1694 | 1576 | 525.3 | 475.1 | 503.1 | 477 | 438.5 | 434.8 | 430.5 | 459.7 | 404.7 | 410.8
1695 | 1577 | 525.2 | 475.1 | 503.1 | 477 | 438.6 | 434.9 | 430.7 | 459.7 | 404.8 | 410.9
1696 | 1578 | 525.2 | 475.1 | 503.1 | 477 | 438.8 | 435 | 430.8 | 459.7 | 405 | 411
1697 | 1579 | 525.2 | 475.2 | 503.1 | 477.1 | 438.9 | 435.1 | 431 | 459.7 | 405.2 | 411.1
1698 | 1580 | 525.2 | 475.2 | 503.2 | 477.1 | 439 | 435.2 | 431.1 | 459.8 | 405.3 | 411.1
1699 | 1581 | 525.2 | 475.2 | 503.1 | 477.1 | 439.1 | 435.3 | 431.3 | 459.9 | 405.5 | 411.2
1700 | 1582 | 525.2 | 475.3 | 503.1 | 477.1 | 439.3 | 435.5 | 431.4 | 459.8 | 405.6 | 411.3
1701 | 1583 | 525.1 | 475.3 | 503.2 | 477.2 | 439.4 | 435.6 | 431.6 | 459.7 | 405.8 | 411.4
1702 | 1584 | 525.1 | 475.3 | 503.2 | 477.2 | 439.5 | 435.7 | 431.7 | 459.8 | 405.9 | 411.5
1703 | 1585 | 525.1 | 475.4 | 503.2 | 477.2 | 439.6 | 435.8 | 431.9 | 459.8 | 406.1 | 411.5
1704 | 1586 | 525.1 | 475.4 | 503.2 | 477.3 | 439.7 | 435.9 | 432 | 459.7 | 406.2 | 411.6
1705 | 1587 | 525.1 | 475.4 | 503.2 | 477.3 | 439.8 | 436 | 432.2 | 459.7 | 406.3 | 411.7
1706 | 1588 | 525.1 | 475.4 | 503.2 | 477.3 | 440 | 436.2 | 432.3 | 459.5 | 406.5 | 411.8
1707 | 1589 | 525.1 | 475.5 | 503.2 | 477.4 | 440.2 | 436.3 | 432.5 | 459.6 | 406.6 | 411.9
1708 | 1590 | 525.1 | 475.5 | 503.2 | 477.4 | 440.3 | 436.4 | 432.6 | 459.5 | 406.8 | 412
1709 | 1591 | 525.1 | 475.5 | 503.2 | 477.4 | 440.5 | 436.6 | 432.8 | 459.4 | 406.9 | 412.1
1710 | 1592 | 525.1 | 475.6 | 503.2 | 477.4 | 440.7 | 436.7 | 432.9 | 459.5 | 407 | 412.2
1711 | 1593 | 525.1 | 475.6 | 503.2 | 477.5 | 440.8 | 436.8 | 433 | 459.4 | 407.2 | 412.2
1712 | 1594 | 525.1 | 475.6 | 503.3 | 477.5 | 440.9 | 437 | 433.2 | 459.3 | 407.3 | 412.3
1713 | 1595 | 525.1 | 475.6 | 503.3 | 477.5 | 441.1 | 437.1 | 433.3 | 459.2 | 407.5 | 412.4
1714 | 1596 | 525.1 | 475.7 | 503.3 | 477.6 | 441.3 | 437.2 | 433.4 | 459.2 | 407.6 | 412.5
1715 | 1597 | 525.1 | 475.7 | 503.3 | 477.6 | 441.5 | 437.4 | 433.5 | 459.2 | 407.8 | 412.6
1716 | 1598 | 525.1 | 475.7 | 503.3 | 477.6 | 441.6 | 437.5 | 433.6 | 459.3 | 407.9 | 412.7
1717 | 1599 | 525.1 | 475.8 | 503.3 | 477.6 | 441.7 | 437.7 | 433.7 | 459.2 | 408.1 | 412.8
1718 | 1600 | 525.1 | 475.8 | 503.3 | 477.7 | 441.7 | 437.8 | 433.8 | 459.2 | 408.2 | 412.9
1719 | 1601 | 525.1 | 475.8 | 503.3 | 477.7 | 441.8 | 437.9 | 433.8 | 459.2 | 408.4 | 412.9
1720 | 1602 | 525.1 | 475.8 | 503.4 | 477.7 | 441.9 | 438.1 | 433.9 | 459.1 | 408.5 | 413
1721 | 1603 | 525.1 | 475.9 | 503.4 | 477.7 | 442.1 | 438.2 | 434 | 458.9 | 408.7 | 413.1
1722 | 1604 | 525.1 | 475.9 | 503.4 | 477.8 | 442.2 | 438.4 | 434.1 | 458.8 | 408.8 | 413.2
1723 | 1605 | 525.1 | 475.9 | 503.4 | 477.8 | 442.3 | 438.5 | 434.2 | 458.8 | 409 | 413.3
1724 | 1606 | 525.1 | 476 | 503.4 | 477.8 | 442.4 | 438.7 | 434.3 | 458.8 | 409.2 | 413.3
1725 | 1607 | 525 | 476 | 503.4 | 477.9 | 442.5 | 438.8 | 434.4 | 458.8 | 409.3 | 413.4
1726 | 1608 | 525 | 476 | 503.4 | 477.9 | 442.7 | 438.9 | 434.5 | 458.9 | 409.5 | 413.5
1727 | 1609 | 525 | 476 | 503.4 | 477.9 | 442.9 | 439.1 | 434.6 | 458.9 | 409.6 | 413.6
1728 | 1610 | 525 | 476.1 | 503.4 | 477.9 | 443.1 | 439.2 | 434.8 | 458.8 | 409.7 | 413.7
1729 | 1611 | 525 | 476.1 | 503.5 | 478 | 443.2 | 439.4 | 434.9 | 458.6 | 409.9 | 413.7
1730 | 1612 | 525 | 476.1 | 503.5 | 478 | 443.3 | 439.6 | 435 | 458.5 | 410 | 413.8
1731 | 1613 | 525 | 476.2 | 503.5 | 478 | 443.4 | 439.7 | 435.1 | 458.6 | 410.1 | 413.9
1732 | 1614 | 525 | 476.2 | 503.5 | 478.1 | 443.4 | 439.8 | 435.3 | 458.7 | 410.3 | 414
1733 | 1615 | 525 | 476.2 | 503.5 | 478.1 | 443.6 | 440 | 435.4 | 458.7 | 410.4 | 414.1
1734 | 1616 | 525 | 476.2 | 503.5 | 478.1 | 443.7 | 440.1 | 435.5 | 458.5 | 410.6 | 414.2
1735 | 1617 | 525 | 476.3 | 503.6 | 478.1 | 443.8 | 440.2 | 435.7 | 458.5 | 410.7 | 414.3
1736 | 1618 | 524.9 | 476.3 | 503.6 | 478.2 | 444 | 440.4 | 435.8 | 458.6 | 410.9 | 414.3
1737 | 1619 | 524.9 | 476.3 | 503.6 | 478.2 | 444.1 | 440.5 | 435.9 | 458.5 | 411 | 414.4
1738 | 1620 | 524.9 | 476.3 | 503.6 | 478.2 | 444.2 | 440.6 | 436 | 458.4 | 411.2 | 414.5
1739 | 1621 | 524.9 | 476.4 | 503.6 | 478.2 | 444.3 | 440.8 | 436.2 | 458 | 411.3 | 414.6
1740 | 1622 | 525 | 476.4 | 503.6 | 478.3 | 444.5 | 441 | 436.3 | 458 | 411.5 | 414.7
1741 | 1623 | 525 | 476.4 | 503.6 | 478.3 | 444.7 | 441.1 | 436.4 | 458 | 411.6 | 414.8
1742 | 1624 | 525 | 476.4 | 503.7 | 478.3 | 444.8 | 441.3 | 436.6 | 458.1 | 411.8 | 414.9
1743 | 1625 | 525 | 476.5 | 503.7 | 478.4 | 444.9 | 441.4 | 436.8 | 458.1 | 411.9 | 414.9
1744 | 1626 | 524.9 | 476.5 | 503.7 | 478.4 | 444.9 | 441.6 | 436.9 | 458.1 | 412 | 415
1745 | 1627 | 524.9 | 476.5 | 503.7 | 478.4 | 445.1 | 441.7 | 437 | 458.1 | 412.2 | 415.1
1746 | 1628 | 524.9 | 476.5 | 503.7 | 478.4 | 445.2 | 441.8 | 437.2 | 458.1 | 412.3 | 415.2
1747 | 1629 | 524.9 | 476.6 | 503.7 | 478.5 | 445.4 | 442 | 437.3 | 458.1 | 412.5 | 415.3
1748 | 1630 | 524.9 | 476.6 | 503.7 | 478.5 | 445.7 | 442.1 | 437.4 | 458.1 | 412.6 | 415.3
1749 | 1631 | 524.9 | 476.6 | 503.7 | 478.5 | 445.9 | 442.3 | 437.5 | 458 | 412.7 | 415.4
1750 | 1632 | 524.9 | 476.7 | 503.7 | 478.6 | 445.9 | 442.4 | 437.7 | 458 | 412.9 | 415.5
1751 | 1633 | 524.9 | 476.7 | 503.7 | 478.6 | 446 | 442.6 | 437.8 | 458.2 | 413 | 415.6
1752 | 1634 | 524.9 | 476.7 | 503.8 | 478.6 | 446.1 | 442.7 | 438 | 458.3 | 413.2 | 415.7
1753 | 1635 | 524.9 | 476.7 | 503.7 | 478.6 | 446.2 | 442.9 | 438.1 | 458.3 | 413.3 | 415.8
1754 | 1636 | 524.9 | 476.7 | 503.8 | 478.7 | 446.3 | 443 | 438.3 | 458.3 | 413.4 | 415.9
1755 | 1637 | 524.9 | 476.8 | 503.8 | 478.7 | 446.4 | 443.1 | 438.5 | 458.3 | 413.6 | 416
1756 | 1638 | 524.9 | 476.8 | 503.8 | 478.7 | 446.6 | 443.3 | 438.7 | 458.3 | 413.7 | 416
1757 | 1639 | 524.8 | 476.8 | 503.8 | 478.7 | 446.8 | 443.4 | 438.8 | 458.3 | 413.9 | 416.1
1758 | 1640 | 524.8 | 476.9 | 503.8 | 478.8 | 446.9 | 443.5 | 439 | 458.4 | 414.1 | 416.2
1759 | 1641 | 524.8 | 476.9 | 503.8 | 478.8 | 447.1 | 443.6 | 439.1 | 458.4 | 414.2 | 416.3
1760 | 1642 | 524.8 | 476.9 | 503.8 | 478.8 | 447.1 | 443.8 | 439.2 | 458.6 | 414.4 | 416.4
1761 | 1643 | 524.8 | 476.9 | 503.9 | 478.8 | 447.1 | 443.9 | 439.4 | 458.8 | 414.5 | 416.4
1762 | 1644 | 524.8 | 477 | 503.8 | 478.9 | 447.1 | 444 | 439.5 | 458.7 | 414.6 | 416.5
1763 | 1645 | 524.8 | 477 | 503.9 | 478.9 | 447.2 | 444.1 | 439.6 | 458.6 | 414.8 | 416.6
1764 | 1646 | 524.7 | 477 | 503.9 | 478.9 | 447.3 | 444.2 | 439.8 | 458.5 | 414.9 | 416.7
1765 | 1647 | 524.7 | 477 | 503.9 | 479 | 447.5 | 444.3 | 439.9 | 458.6 | 415.1 | 416.8
1766 | 1648 | 524.7 | 477.1 | 503.9 | 479 | 447.7 | 444.4 | 440.1 | 458.7 | 415.2 | 416.9
1767 | 1649 | 524.7 | 477.1 | 503.9 | 479 | 447.8 | 444.5 | 440.2 | 458.7 | 415.3 | 416.9
1768 | 1650 | 524.7 | 477.1 | 503.9 | 479 | 448 | 444.6 | 440.3 | 458.8 | 415.5 | 417
1769 | 1651 | 524.7 | 477.2 | 504 | 479.1 | 448.1 | 444.7 | 440.4 | 458.7 | 415.7 | 417.1
1770 | 1652 | 524.7 | 477.2 | 503.9 | 479.1 | 448.3 | 444.8 | 440.6 | 458.7 | 415.8 | 417.2
1771 | 1653 | 524.7 | 477.2 | 504 | 479.1 | 448.4 | 445 | 440.7 | 458.6 | 416.1 | 417.2
1772 | 1654 | 524.7 | 477.2 | 504 | 479.1 | 448.4 | 445.1 | 440.9 | 458.4 | 416.3 | 417.3
1773 | 1655 | 524.7 | 477.3 | 503.9 | 479.2 | 448.5 | 445.2 | 441 | 458.4 | 416.4 | 417.4
1774 | 1656 | 524.7 | 477.3 | 504 | 479.2 | 448.5 | 445.3 | 441.2 | 458.4 | 416.5 | 417.5
1775 | 1657 | 524.7 | 477.3 | 504 | 479.2 | 448.7 | 445.4 | 441.4 | 458.6 | 416.7 | 417.6
1776 | 1658 | 524.7 | 477.4 | 504 | 479.2 | 448.8 | 445.6 | 441.5 | 458.8 | 416.8 | 417.6
1777 | 1659 | 524.6 | 477.4 | 504 | 479.3 | 448.9 | 445.7 | 441.6 | 458.9 | 416.9 | 417.7
1778 | 1660 | 524.6 | 477.4 | 504 | 479.3 | 449 | 445.9 | 441.7 | 459 | 417.1 | 417.8
1779 | 1661 | 524.7 | 477.4 | 504 | 479.3 | 449.1 | 446 | 441.9 | 458.9 | 417.2 | 417.9
1780 | 1662 | 524.7 | 477.4 | 504.1 | 479.3 | 449.1 | 446.2 | 442 | 458.9 | 417.3 | 418
1781 | 1663 | 524.7 | 477.5 | 504.1 | 479.4 | 449.3 | 446.3 | 442.2 | 459 | 417.4 | 418.1
1782 | 1664 | 524.7 | 477.5 | 504.1 | 479.4 | 449.4 | 446.4 | 442.3 | 459.2 | 417.5 | 418.1
1783 | 1665 | 524.7 | 477.5 | 504.1 | 479.4 | 449.5 | 446.5 | 442.5 | 459.3 | 417.6 | 418.2
1784 | 1666 | 524.7 | 477.6 | 504.1 | 479.4 | 449.7 | 446.6 | 442.7 | 459.4 | 417.8 | 418.3
1785 | 1667 | 524.7 | 477.6 | 504.1 | 479.5 | 449.8 | 446.7 | 443.2 | 459.3 | 417.9 | 418.4
1786 | 1668 | 524.8 | 477.6 | 504.1 | 479.5 | 450 | 446.8 | 443.7 | 459.2 | 418.1 | 418.5
1787 | 1669 | 524.7 | 477.6 | 504.1 | 479.5 | 450.1 | 446.9 | 444.1 | 459.2 | 418.2 | 418.5
1788 | 1670 | 524.7 | 477.7 | 504.1 | 479.5 | 450.2 | 447 | 444.1 | 459.2 | 418.3 | 418.6
1789 | 1671 | 524.7 | 477.7 | 504.1 | 479.5 | 450.3 | 447.1 | 444.1 | 459 | 418.4 | 418.7
1790 | 1672 | 524.7 | 477.7 | 504.1 | 479.6 | 450.4 | 447.2 | 444 | 459 | 418.5 | 418.8
1791 | 1673 | 524.7 | 477.7 | 504.2 | 479.6 | 450.5 | 447.3 | 444 | 459 | 418.6 | 418.9
1792 | 1674 | 524.7 | 477.7 | 504.2 | 479.6 | 450.7 | 447.4 | 444 | 459 | 418.7 | 419
1793 | 1675 | 524.8 | 477.8 | 504.2 | 479.7 | 450.7 | 447.6 | 444.1 | 458.9 | 418.8 | 419.1
1794 | 1676 | 524.8 | 477.8 | 504.2 | 479.7 | 450.8 | 447.7 | 444.1 | 458.9 | 418.9 | 419.1
1795 | 1677 | 524.8 | 477.8 | 504.2 | 479.7 | 450.9 | 447.8 | 444.2 | 459 | 419.1 | 419.2
1796 | 1678 | 524.8 | 477.8 | 504.2 | 479.7 | 451 | 447.9 | 444.2 | 459 | 419.2 | 419.3
1797 | 1679 | 524.8 | 477.9 | 504.2 | 479.8 | 451.2 | 448.1 | 444.3 | 458.9 | 419.3 | 419.4
1798 | 1680 | 524.8 | 477.9 | 504.2 | 479.8 | 451.4 | 448.2 | 444.4 | 458.9 | 419.4 | 419.5
1799 | 1681 | 524.8 | 477.9 | 504.2 | 479.8 | 451.6 | 448.3 | 444.5 | 459 | 419.5 | 419.6
1800 | 1682 | 524.8 | 478 | 504.2 | 479.8 | 451.7 | 448.4 | 444.6 | 458.9 | 419.7 | 419.7
1801 | 1683 | 524.8 | 478 | 504.2 | 479.8 | 451.8 | 448.6 | 444.8 | 458.7 | 419.8 | 419.7
1802 | 1684 | 524.9 | 478 | 504.2 | 479.9 | 451.8 | 448.6 | 444.9 | 458.8 | 419.9 | 419.8
1803 | 1685 | 524.9 | 478 | 504.2 | 479.9 | 451.9 | 448.7 | 445 | 458.8 | 420 | 419.9
1804 | 1686 | 524.9 | 478.1 | 504.2 | 479.9 | 452 | 448.8 | 445.2 | 458.8 | 420.1 | 420
1805 | 1687 | 524.9 | 478.1 | 504.3 | 479.9 | 452.1 | 448.9 | 445.3 | 458.8 | 420.2 | 420.1
1806 | 1688 | 524.9 | 478.1 | 504.3 | 480 | 452.2 | 449 | 445.4 | 458.8 | 420.3 | 420.2
1807 | 1689 | 524.9 | 478.1 | 504.3 | 480 | 452.3 | 449.1 | 445.5 | 458.8 | 420.5 | 420.3
1808 | 1690 | 524.9 | 478.2 | 504.3 | 480 | 452.4 | 449.2 | 445.6 | 458.7 | 420.6 | 420.3
1809 | 1691 | 524.9 | 478.2 | 504.3 | 480 | 452.5 | 449.3 | 445.7 | 458.5 | 420.7 | 420.4
1810 | 1692 | 524.9 | 478.2 | 504.3 | 480.1 | 452.5 | 449.4 | 446 | 458.4 | 420.8 | 420.5
1811 | 1693 | 524.9 | 478.2 | 504.3 | 480.1 | 452.6 | 449.6 | 446.3 | 458.4 | 420.9 | 420.6
1812 | 1694 | 524.9 | 478.3 | 504.3 | 480.1 | 452.7 | 449.7 | 446.6 | 458.4 | 421.1 | 420.7
1813 | 1695 | 524.9 | 478.3 | 504.3 | 480.1 | 452.8 | 449.8 | 446.9 | 458.4 | 421.2 | 420.8
1814 | 1696 | 524.9 | 478.3 | 504.3 | 480.2 | 452.9 | 449.9 | 447 | 458.4 | 421.3 | 420.8
1815 | 1697 | 524.9 | 478.3 | 504.3 | 480.2 | 453 | 450 | 447.1 | 458.5 | 421.3 | 420.9
1816 | 1698 | 524.9 | 478.3 | 504.3 | 480.2 | 453.1 | 450.1 | 447.2 | 458.8 | 421.4 | 421
1817 | 1699 | 524.9 | 478.4 | 504.3 | 480.2 | 453.2 | 450.2 | 447.2 | 459.2 | 421.5 | 421.1
1818 | 1700 | 524.9 | 478.4 | 504.4 | 480.2 | 453.3 | 450.3 | 447.2 | 459.4 | 421.6 | 421.2
1819 | 1701 | 524.9 | 478.4 | 504.4 | 480.3 | 453.4 | 450.4 | 447.2 | 459.4 | 421.6 | 421.2
1820 | 1702 | 524.9 | 478.4 | 504.4 | 480.3 | 453.5 | 450.4 | 447.2 | 459.5 | 421.7 | 421.3
1821 | 1703 | 524.9 | 478.5 | 504.4 | 480.3 | 453.5 | 450.6 | 447.2 | 459.7 | 421.8 | 421.4
1822 | 1704 | 524.9 | 478.5 | 504.4 | 480.3 | 453.6 | 450.7 | 447.3 | 459.8 | 421.9 | 421.5
1823 | 1705 | 524.9 | 478.5 | 504.4 | 480.4 | 453.7 | 450.7 | 447.4 | 460 | 422 | 421.6
1824 | 1706 | 524.9 | 478.5 | 504.4 | 480.4 | 453.8 | 450.8 | 447.5 | 460 | 422.1 | 421.6
1825 | 1707 | 524.9 | 478.6 | 504.5 | 480.4 | 454 | 450.9 | 447.6 | 460 | 422.2 | 421.7
1826 | 1708 | 524.9 | 478.6 | 504.5 | 480.4 | 454 | 451 | 447.6 | 460.2 | 422.3 | 421.8
1827 | 1709 | 524.9 | 478.6 | 504.5 | 480.5 | 454.1 | 451.1 | 447.7 | 460.6 | 422.4 | 421.9
1828 | 1710 | 524.9 | 478.7 | 504.5 | 480.5 | 454.2 | 451.2 | 447.8 | 460.9 | 422.5 | 421.9
1829 | 1711 | 524.9 | 478.7 | 504.5 | 480.5 | 454.3 | 451.2 | 447.8 | 461 | 422.6 | 422
1830 | 1712 | 524.9 | 478.7 | 504.5 | 480.5 | 454.4 | 451.3 | 447.9 | 461.2 | 422.6 | 422.1
1831 | 1713 | 524.9 | 478.8 | 504.5 | 480.6 | 454.4 | 451.4 | 448 | 461.5 | 422.7 | 422.2
1832 | 1714 | 524.9 | 478.8 | 504.5 | 480.6 | 454.5 | 451.5 | 448.1 | 461.7 | 422.8 | 422.3
1833 | 1715 | 524.9 | 478.8 | 504.5 | 480.6 | 454.5 | 451.6 | 448.2 | 461.8 | 422.9 | 422.3
1834 | 1716 | 524.9 | 478.9 | 504.5 | 480.6 | 454.6 | 451.6 | 448.4 | 462 | 423 | 422.4
1835 | 1717 | 524.9 | 478.9 | 504.5 | 480.7 | 454.7 | 451.7 | 448.6 | 462.2 | 423 | 422.5
1836 | 1718 | 524.8 | 478.9 | 504.5 | 480.7 | 454.8 | 451.8 | 448.7 | 462.4 | 423.1 | 422.6
1837 | 1719 | 524.8 | 479 | 504.5 | 480.7 | 454.8 | 451.9 | 448.8 | 462.5 | 423.2 | 422.7
1838 | 1720 | 524.8 | 479 | 504.5 | 480.7 | 454.9 | 452 | 449 | 462.8 | 423.3 | 422.7
1839 | 1721 | 524.8 | 479 | 504.5 | 480.8 | 455 | 452 | 449 | 462.9 | 423.4 | 422.8
1840 | 1722 | 524.7 | 479.1 | 504.6 | 480.8 | 455.1 | 452.1 | 449.1 | 463 | 423.4 | 422.9
1841 | 1723 | 524.7 | 479.1 | 504.5 | 480.8 | 455.2 | 452.2 | 449.1 | 462.8 | 423.5 | 423
1842 | 1724 | 524.6 | 479.1 | 504.6 | 480.8 | 455.3 | 452.3 | 449.2 | 462.8 | 423.5 | 423
1843 | 1725 | 524.6 | 479.1 | 504.6 | 480.8 | 455.4 | 452.3 | 449.2 | 462.9 | 423.6 | 423.1
1844 | 1726 | 524.6 | 479.2 | 504.6 | 480.9 | 455.5 | 452.4 | 449.3 | 463.2 | 423.6 | 423.2
1845 | 1727 | 524.6 | 479.2 | 504.6 | 480.9 | 455.5 | 452.4 | 449.4 | 463.6 | 423.6 | 423.3
1846 | 1728 | 524.6 | 479.2 | 504.6 | 480.9 | 455.6 | 452.5 | 449.5 | 463.5 | 423.7 | 423.4
1847 | 1729 | 524.6 | 479.3 | 504.6 | 480.9 | 455.7 | 452.5 | 449.5 | 463.4 | 423.7 | 423.4
1848 | 1730 | 524.6 | 479.3 | 504.6 | 480.9 | 455.7 | 452.6 | 449.4 | 463.6 | 423.8 | 423.5
1849 | 1731 | 524.6 | 479.3 | 504.6 | 481 | 455.7 | 452.7 | 449.4 | 463.5 | 423.8 | 423.6
1850 | 1732 | 524.7 | 479.4 | 504.6 | 481 | 455.8 | 452.7 | 449.5 | 463.4 | 423.9 | 423.7
1851 | 1733 | 524.7 | 479.4 | 504.6 | 481 | 455.8 | 452.8 | 449.6 | 463.3 | 423.9 | 423.8
1852 | 1734 | 524.7 | 479.4 | 504.6 | 481 | 455.9 | 452.8 | 449.7 | 463.4 | 424 | 423.9
1853 | 1735 | 524.7 | 479.4 | 504.7 | 481.1 | 455.9 | 452.9 | 449.7 | 463.6 | 424.1 | 423.9
1854 | 1736 | 524.7 | 479.4 | 504.7 | 481.1 | 456 | 452.9 | 449.7 | 464.1 | 424.1 | 424
1855 | 1737 | 524.7 | 479.5 | 504.7 | 481.1 | 456.1 | 453 | 449.8 | 464.7 | 424.2 | 424.1
1856 | 1738 | 524.7 | 479.5 | 504.7 | 481.1 | 456.1 | 453.1 | 449.9 | 464.9 | 424.2 | 424.2
1857 | 1739 | 524.7 | 479.5 | 504.7 | 481.1 | 456.2 | 453.1 | 449.9 | 464.6 | 424.3 | 424.3
1858 | 1740 | 524.7 | 479.5 | 504.7 | 481.2 | 456.2 | 453.2 | 449.9 | 464.5 | 424.3 | 424.3
1859 | 1741 | 524.7 | 479.6 | 504.7 | 481.2 | 456.3 | 453.2 | 450 | 464.8 | 424.4 | 424.4
1860 | 1742 | 524.7 | 479.6 | 504.7 | 481.2 | 456.3 | 453.3 | 450 | 464.9 | 424.4 | 424.5
1861 | 1743 | 524.7 | 479.6 | 504.7 | 481.2 | 456.4 | 453.3 | 450.1 | 465.3 | 424.5 | 424.6
1862 | 1744 | 524.7 | 479.7 | 504.7 | 481.3 | 456.5 | 453.4 | 450.2 | 465.3 | 424.5 | 424.7
1863 | 1745 | 524.7 | 479.7 | 504.7 | 481.3 | 456.5 | 453.4 | 450.3 | 465.3 | 424.6 | 424.8
1864 | 1746 | 524.7 | 479.7 | 504.8 | 481.3 | 456.6 | 453.5 | 450.3 | 465.3 | 424.6 | 424.8
1865 | 1747 | 524.7 | 479.7 | 504.7 | 481.3 | 456.7 | 453.5 | 450.4 | 465.3 | 424.7 | 424.9
1866 | 1748 | 524.7 | 479.8 | 504.8 | 481.3 | 456.7 | 453.6 | 450.4 | 465.4 | 424.7 | 425
1867 | 1749 | 524.7 | 479.8 | 504.8 | 481.4 | 456.8 | 453.6 | 450.5 | 465.7 | 424.8 | 425.1
1868 | 1750 | 524.6 | 479.8 | 504.7 | 481.4 | 456.8 | 453.7 | 450.6 | 466 | 424.9 | 425.2
1869 | 1751 | 524.6 | 479.8 | 504.7 | 481.4 | 456.9 | 453.7 | 450.6 | 466.2 | 425 | 425.2
1870 | 1752 | 524.6 | 479.9 | 504.7 | 481.4 | 456.9 | 453.8 | 450.6 | 466.2 | 425.1 | 425.3
1871 | 1753 | 524.6 | 479.9 | 504.8 | 481.4 | 457 | 453.8 | 450.6 | 466.4 | 425.2 | 425.4
1872 | 1754 | 524.6 | 479.9 | 504.8 | 481.5 | 457 | 453.8 | 450.5 | 466.5 | 425.3 | 425.5
1873 | 1755 | 524.6 | 479.9 | 504.8 | 481.5 | 457 | 453.9 | 450.5 | 466.7 | 425.4 | 425.6
1874 | 1756 | 524.6 | 480 | 504.8 | 481.5 | 457.1 | 453.9 | 450.6 | 467.1 | 425.5 | 425.7
1875 | 1757 | 524.6 | 480 | 504.8 | 481.5 | 457.2 | 454 | 450.6 | 467 | 425.6 | 425.8
1876 | 1758 | 524.6 | 480 | 504.8 | 481.5 | 457.2 | 454 | 450.6 | 466.6 | 425.8 | 425.9
1877 | 1759 | 524.6 | 480 | 504.8 | 481.6 | 457.3 | 454.1 | 450.6 | 466.3 | 425.9 | 425.9
1878 | 1760 | 524.5 | 480 | 504.8 | 481.6 | 457.3 | 454.1 | 450.7 | 466.2 | 426 | 426
1879 | 1761 | 524.5 | 480.1 | 504.8 | 481.6 | 457.3 | 454.2 | 450.7 | 466.1 | 426.1 | 426.1
1880 | 1762 | 524.5 | 480.1 | 504.8 | 481.6 | 457.3 | 454.2 | 450.8 | 466.1 | 426.3 | 426.2
1881 | 1763 | 524.5 | 480.1 | 504.8 | 481.6 | 457.3 | 454.2 | 450.8 | 466.2 | 426.4 | 426.3
1882 | 1764 | 524.5 | 480.1 | 504.8 | 481.7 | 457.4 | 454.3 | 450.8 | 466.3 | 426.6 | 426.3
1883 | 1765 | 524.5 | 480.2 | 504.8 | 481.7 | 457.4 | 454.3 | 450.9 | 466.4 | 426.7 | 426.4
1884 | 1766 | 524.5 | 480.2 | 504.8 | 481.7 | 457.5 | 454.4 | 450.9 | 466.5 | 426.9 | 426.5
1885 | 1767 | 524.5 | 480.2 | 504.8 | 481.7 | 457.6 | 454.4 | 450.9 | 466.6 | 427.1 | 426.6
1886 | 1768 | 524.5 | 480.2 | 504.8 | 481.7 | 457.6 | 454.5 | 450.9 | 466.6 | 427.5 | 426.7
1887 | 1769 | 524.5 | 480.3 | 504.8 | 481.8 | 457.7 | 454.5 | 451 | 466.6 | 427.9 | 426.7
1888 | 1770 | 524.6 | 480.3 | 504.8 | 481.8 | 457.8 | 454.6 | 451 | 466.7 | 428.1 | 426.8
1889 | 1771 | 524.6 | 480.3 | 504.8 | 481.8 | 457.8 | 454.7 | 451.1 | 466.8 | 428.3 | 426.9
1890 | 1772 | 524.7 | 480.3 | 504.9 | 481.8 | 457.9 | 454.7 | 451.1 | 466.8 | 428.6 | 427
1891 | 1773 | 524.7 | 480.4 | 504.8 | 481.8 | 458 | 454.8 | 451.2 | 466.8 | 428.9 | 427
1892 | 1774 | 524.7 | 480.4 | 504.8 | 481.9 | 457.9 | 454.8 | 451.2 | 466.8 | 429.1 | 427.1
1893 | 1775 | 524.7 | 480.4 | 504.9 | 481.9 | 457.9 | 454.9 | 451.3 | 466.8 | 429.3 | 427.2
1894 | 1776 | 524.8 | 480.4 | 504.9 | 481.9 | 457.9 | 454.9 | 451.3 | 467 | 429.5 | 427.3
1895 | 1777 | 524.8 | 480.4 | 504.9 | 481.9 | 457.9 | 455 | 451.4 | 467 | 429.8 | 427.3
1896 | 1778 | 524.8 | 480.4 | 504.9 | 481.9 | 457.9 | 455 | 451.5 | 467.1 | 430 | 427.4
1897 | 1779 | 524.8 | 480.5 | 504.9 | 482 | 457.8 | 455 | 451.5 | 467.5 | 430.2 | 427.5
1898 | 1780 | 524.9 | 480.5 | 504.9 | 482 | 457.9 | 455.1 | 451.6 | 467.6 | 430.4 | 427.6
1899 | 1781 | 524.9 | 480.5 | 504.9 | 482 | 457.9 | 455.1 | 451.6 | 467.5 | 430.6 | 427.6
1900 | 1782 | 524.9 | 480.5 | 504.9 | 482 | 457.9 | 455.1 | 451.6 | 467.6 | 430.7 | 427.7
1901 | 1783 | 524.9 | 480.6 | 504.9 | 482.1 | 457.9 | 455.2 | 451.6 | 467.6 | 430.7 | 427.8
1902 | 1784 | 524.9 | 480.6 | 504.9 | 482.1 | 458 | 455.2 | 451.7 | 467.6 | 430.8 | 427.9
1903 | 1785 | 524.9 | 480.6 | 504.9 | 482.1 | 458 | 455.2 | 451.7 | 467.6 | 430.8 | 427.9
1904 | 1786 | 524.9 | 480.6 | 504.9 | 482.1 | 458.1 | 455.3 | 451.8 | 467.5 | 430.8 | 428
1905 | 1787 | 525 | 480.7 | 504.9 | 482.2 | 458.1 | 455.4 | 451.8 | 467.6 | 431 | 428.1
1906 | 1788 | 525 | 480.7 | 504.9 | 482.2 | 458.1 | 455.4 | 451.9 | 467.6 | 431.1 | 428.1
1907 | 1789 | 525 | 480.7 | 504.9 | 482.2 | 458.1 | 455.4 | 451.9 | 467.7 | 431.1 | 428.2
1908 | 1790 | 525 | 480.7 | 504.9 | 482.2 | 458.1 | 455.5 | 452 | 467.7 | 431 | 428.3
1909 | 1791 | 525 | 480.8 | 504.9 | 482.3 | 458.1 | 455.5 | 452 | 467.7 | 431.1 | 428.3
1910 | 1792 | 525 | 480.8 | 504.9 | 482.3 | 458.1 | 455.6 | 452.1 | 467.7 | 431.1 | 428.4
1911 | 1793 | 525 | 480.8 | 504.8 | 482.3 | 458.1 | 455.6 | 452.3 | 467.8 | 431.2 | 428.4
1912 | 1794 | 525 | 480.9 | 504.8 | 482.4 | 458.1 | 455.6 | 452.4 | 467.8 | 431.2 | 428.5
1913 | 1795 | 525 | 480.9 | 504.8 | 482.4 | 458.2 | 455.7 | 452.4 | 467.9 | 431.3 | 428.6
1914 | 1796 | 525 | 480.9 | 504.8 | 482.4 | 458.3 | 455.7 | 452.5 | 467.9 | 431.5 | 428.7
1915 | 1797 | 525 | 480.9 | 504.8 | 482.4 | 458.4 | 455.7 | 452.5 | 467.9 | 431.7 | 428.7
1916 | 1798 | 525 | 481 | 504.8 | 482.4 | 458.4 | 455.8 | 452.5 | 467.7 | 431.8 | 428.8
1917 | 1799 | 525.1 | 481 | 504.8 | 482.5 | 458.4 | 455.8 | 452.6 | 467.7 | 431.9 | 428.8
1918 | 1800 | 525.1 | 481 | 504.8 | 482.5 | 458.4 | 455.9 | 452.6 | 467.7 | 431.9 | 428.9
1919 | 1801 | 525.1 | 481.1 | 504.8 | 482.5 | 458.4 | 455.9 | 452.7 | 467.8 | 432 | 429
1920 | 1802 | 525.1 | 481.1 | 504.8 | 482.6 | 458.4 | 456 | 452.8 | 467.9 | 432.1 | 429
1921 | 1803 | 525.1 | 481.1 | 504.8 | 482.6 | 458.4 | 456 | 452.8 | 468.1 | 432.3 | 429.1
1922 | 1804 | 525.1 | 481.1 | 504.8 | 482.6 | 458.4 | 456 | 452.8 | 468.1 | 432.3 | 429.2
1923 | 1805 | 525.1 | 481.2 | 504.7 | 482.6 | 458.5 | 456.1 | 452.9 | 468.1 | 432.4 | 429.2
1924 | 1806 | 525.1 | 481.4 | 504.4 | 482.8 | 458.8 | 456.2 | 452.9 | 468.1 | 432.5 | 429.3
1925 | 1807 | 525.1 | 481.4 | 504.3 | 482.8 | 458.9 | 456.2 | 453 | 468.2 | 432.6 | 429.4
1926 | 1808 | 525.1 | 481.5 | 504.3 | 482.9 | 458.9 | 456.3 | 453 | 468.2 | 432.6 | 429.4
1927 | 1809 | 525.1 | 481.5 | 504.3 | 482.9 | 459 | 456.3 | 453 | 468.3 | 432.7 | 429.5
1928 | 1810 | 525 | 481.5 | 504.3 | 482.9 | 459 | 456.4 | 453 | 468.3 | 432.8 | 429.6
1929 | 1811 | 525 | 481.5 | 504.3 | 482.9 | 459 | 456.4 | 453.1 | 468.1 | 432.8 | 429.6
1930 | 1812 | 525 | 481.5 | 504.3 | 482.9 | 459 | 456.4 | 453.1 | 468 | 432.8 | 429.7
1931 | 1813 | 525 | 481.6 | 504.3 | 483 | 459 | 456.5 | 453.2 | 467.7 | 432.8 | 429.8
1932 | 1814 | 525 | 481.6 | 504.2 | 483 | 459 | 456.5 | 453.2 | 467.6 | 432.7 | 429.8
1933 | 1815 | 525 | 481.6 | 504.2 | 483 | 459 | 456.5 | 453.3 | 467.6 | 432.8 | 429.9
1934 | 1816 | 525 | 481.6 | 504.3 | 483 | 459.1 | 456.6 | 453.3 | 467.6 | 432.8 | 430
1935 | 1817 | 525 | 481.7 | 504.2 | 483.1 | 459.2 | 456.6 | 453.4 | 467.6 | 432.8 | 430
1936 | 1818 | 525 | 481.7 | 504.2 | 483.1 | 459.2 | 456.6 | 453.5 | 467.6 | 432.9 | 430.1
1937 | 1819 | 525 | 481.7 | 504.2 | 483.1 | 459.2 | 456.6 | 453.5 | 467.7 | 432.9 | 430.2
1938 | 1820 | 525 | 481.7 | 504.2 | 483.1 | 459.3 | 456.7 | 453.6 | 467.9 | 432.9 | 430.2
1939 | 1821 | 525 | 481.8 | 504.1 | 483.2 | 459.3 | 456.7 | 453.7 | 467.9 | 433 | 430.3
1940 | 1822 | 525 | 481.8 | 504.1 | 483.2 | 459.4 | 456.8 | 453.7 | 467.9 | 433.1 | 430.3
1941 | 1823 | 525 | 481.8 | 504.2 | 483.2 | 459.4 | 456.8 | 453.8 | 467.8 | 433.1 | 430.4
1942 | 1824 | 524.9 | 481.8 | 504.2 | 483.2 | 459.5 | 456.8 | 453.8 | 467.7 | 433.2 | 430.5
1943 | 1825 | 524.9 | 481.9 | 504.1 | 483.3 | 459.5 | 456.9 | 453.9 | 467.7 | 433.3 | 430.6
1944 | 1826 | 524.9 | 481.9 | 504.1 | 483.3 | 459.6 | 456.9 | 453.9 | 467.8 | 433.3 | 430.6
1945 | 1827 | 524.9 | 481.9 | 504.1 | 483.3 | 459.6 | 457 | 454 | 467.8 | 433.4 | 430.7
1946 | 1828 | 524.9 | 481.9 | 504.1 | 483.3 | 459.7 | 457 | 454 | 467.9 | 433.4 | 430.8
1947 | 1829 | 524.8 | 482 | 504.1 | 483.3 | 459.7 | 457 | 454.1 | 468.1 | 433.5 | 430.8
1948 | 1830 | 524.8 | 482 | 504.1 | 483.3 | 459.7 | 457.1 | 454.2 | 468.2 | 433.5 | 430.9
1949 | 1831 | 524.8 | 482 | 504.1 | 483.4 | 459.8 | 457.1 | 454.3 | 468.5 | 433.6 | 430.9
1950 | 1832 | 524.8 | 482 | 504.1 | 483.4 | 459.8 | 457.2 | 454.4 | 468.7 | 433.6 | 430.9
1951 | 1833 | 524.8 | 482 | 504.1 | 483.4 | 459.8 | 457.2 | 454.5 | 468.7 | 433.6 | 431
1952 | 1834 | 524.8 | 482 | 504.1 | 483.4 | 459.9 | 457.3 | 454.5 | 468.7 | 433.7 | 431
1953 | 1835 | 524.8 | 482.1 | 504.1 | 483.5 | 459.9 | 457.3 | 454.5 | 468.9 | 433.7 | 431.1
1954 | 1836 | 524.8 | 482.1 | 504.1 | 483.5 | 459.9 | 457.3 | 454.6 | 468.9 | 433.8 | 431.2
1955 | 1837 | 524.8 | 482.1 | 504.1 | 483.5 | 460 | 457.4 | 454.7 | 468.9 | 433.8 | 431.2
1956 | 1838 | 524.8 | 482.1 | 504.1 | 483.5 | 460 | 457.4 | 454.7 | 469 | 433.9 | 431.3
1957 | 1839 | 524.8 | 482.2 | 504.1 | 483.6 | 460 | 457.5 | 454.8 | 469.1 | 433.9 | 431.4
1958 | 1840 | 524.8 | 482.2 | 504.1 | 483.6 | 460.1 | 457.5 | 454.9 | 469.1 | 433.9 | 431.5
1959 | 1841 | 524.8 | 482.2 | 504.1 | 483.6 | 460.3 | 457.6 | 455 | 468.9 | 433.9 | 431.5
1960 | 1842 | 524.8 | 482.2 | 504.1 | 483.6 | 460.3 | 457.6 | 455 | 469.1 | 433.9 | 431.6
1961 | 1843 | 524.8 | 482.2 | 504 | 483.6 | 460.3 | 457.6 | 455.1 | 469.3 | 433.9 | 431.6
1962 | 1844 | 524.8 | 482.2 | 504 | 483.6 | 460.3 | 457.7 | 455.1 | 469.3 | 433.9 | 431.7
1963 | 1845 | 524.8 | 482.3 | 504 | 483.7 | 460.3 | 457.7 | 455.2 | 469.4 | 433.9 | 431.7
1964 | 1846 | 524.7 | 482.3 | 504 | 483.7 | 460.3 | 457.7 | 455.3 | 469.4 | 433.9 | 431.8
1965 | 1847 | 524.7 | 482.3 | 504 | 483.7 | 460.3 | 457.8 | 455.3 | 469.4 | 433.9 | 431.9
1966 | 1848 | 524.7 | 482.3 | 504.1 | 483.7 | 460.3 | 457.8 | 455.3 | 469.4 | 433.8 | 432
1967 | 1849 | 524.7 | 482.3 | 504.1 | 483.7 | 460.3 | 457.8 | 455.3 | 469.4 | 433.8 | 432
1968 | 1850 | 524.7 | 482.3 | 504.1 | 483.8 | 460.3 | 457.9 | 455.3 | 469.3 | 433.8 | 432
1969 | 1851 | 524.7 | 482.3 | 504.1 | 483.7 | 460.3 | 457.9 | 455.3 | 469.3 | 433.7 | 432.1
1970 | 1852 | 524.7 | 482.3 | 504.1 | 483.7 | 460.3 | 458 | 455.4 | 469.3 | 433.7 | 432.1
1971 | 1853 | 524.7 | 482.4 | 504.1 | 483.8 | 460.3 | 458 | 455.4 | 469.3 | 433.6 | 432.2
1972 | 1854 | 524.7 | 482.4 | 504.1 | 483.8 | 460.4 | 458 | 455.4 | 469.4 | 433.6 | 432.3
1973 | 1855 | 524.7 | 482.4 | 504.1 | 483.8 | 460.4 | 458.1 | 455.4 | 469.5 | 433.6 | 432.4
1974 | 1856 | 524.7 | 482.4 | 504.1 | 483.8 | 460.4 | 458.1 | 455.5 | 469.3 | 433.6 | 432.4
1975 | 1857 | 524.7 | 482.4 | 504.1 | 483.9 | 460.4 | 458.1 | 455.5 | 469.2 | 433.6 | 432.4
1976 | 1858 | 524.8 | 482.4 | 504.2 | 483.9 | 460.5 | 458.2 | 455.5 | 469.2 | 433.5 | 432.4
1977 | 1859 | 524.8 | 482.4 | 504.2 | 483.9 | 460.5 | 458.2 | 455.6 | 469.2 | 433.5 | 432.4
1978 | 1860 | 524.8 | 482.5 | 504.2 | 483.9 | 460.6 | 458.2 | 455.6 | 469.3 | 433.4 | 432.6
1979 | 1861 | 524.9 | 482.5 | 504.2 | 483.9 | 460.6 | 458.2 | 455.7 | 469.3 | 433.4 | 432.6
1980 | 1862 | 524.9 | 482.5 | 504.2 | 483.9 | 460.7 | 458.3 | 455.7 | 469.4 | 433.4 | 432.8
1981 | 1863 | 524.9 | 482.5 | 504.2 | 483.9 | 460.7 | 458.3 | 455.7 | 469.3 | 433.4 | 432.8
1982 | 1864 | 524.9 | 482.5 | 504.2 | 484 | 460.7 | 458.3 | 455.7 | 469.3 | 433.4 | 432.9
1983 | 1865 | 524.9 | 482.5 | 504.3 | 483.9 | 460.8 | 458.4 | 455.8 | 469.3 | 433.4 | 433
1984 | 1866 | 524.9 | 482.5 | 504.3 | 484 | 460.8 | 458.4 | 455.8 | 469.4 | 433.4 | 433
1985 | 1867 | 524.9 | 482.5 | 504.3 | 484 | 460.8 | 458.4 | 455.9 | 469.6 | 433.4 | 433.1
1986 | 1868 | 524.9 | 482.5 | 504.4 | 484 | 460.9 | 458.4 | 455.9 | 469.7 | 433.4 | 433.1
1987 | 1869 | 525 | 482.5 | 504.4 | 484 | 460.9 | 458.5 | 455.9 | 469.9 | 433.4 | 433.2
1988 | 1870 | 525 | 482.5 | 504.4 | 484 | 461 | 458.5 | 456 | 469.7 | 433.4 | 433.2
1989 | 1871 | 525 | 482.5 | 504.4 | 484 | 461 | 458.5 | 456 | 469.7 | 433.4 | 433.3
1990 | 1872 | 525 | 482.5 | 504.5 | 484 | 461 | 458.6 | 456.1 | 469.8 | 433.4 | 433.2
1991 | 1873 | 525 | 482.5 | 504.5 | 484 | 461 | 458.6 | 456.1 | 469.8 | 433.4 | 433.2
1992 | 1874 | 525.1 | 482.6 | 504.5 | 484 | 461 | 458.6 | 456.2 | 469.9 | 433.4 | 433.1
1993 | 1875 | 525.1 | 482.6 | 504.5 | 484.1 | 461.1 | 458.6 | 456.2 | 469.8 | 433.4 | 433.2
1994 | 1876 | 525.1 | 482.6 | 504.5 | 484.1 | 461.2 | 458.7 | 456.3 | 469.7 | 433.3 | 433.2
1995 | 1877 | 525.1 | 482.6 | 504.5 | 484.1 | 461.2 | 458.7 | 456.3 | 469.6 | 433.3 | 433.3
1996 | 1878 | 525.1 | 482.6 | 504.5 | 484.1 | 461.2 | 458.7 | 456.4 | 469.6 | 433.3 | 433.3
1997 | 1879 | 525.1 | 482.6 | 504.6 | 484.1 | 461.3 | 458.8 | 456.6 | 469.6 | 433.3 | 433.4
1998 | 1880 | 525.1 | 482.6 | 504.6 | 484.1 | 461.3 | 458.8 | 456.6 | 469.6 | 433.3 | 433.5
1999 | 1881 | 525.1 | 482.6 | 504.5 | 484.1 | 461.3 | 458.8 | 456.6 | 469.6 | 433.3 | 433.6
2000 | 1882 | 525.1 | 482.7 | 504.6 | 484.2 | 461.4 | 458.9 | 456.7 | 469.6 | 433.3 | 433.6
2001 | 1883 | 525.1 | 482.7 | 504.6 | 484.2 | 461.4 | 458.9 | 456.7 | 469.6 | 433.3 | 433.7
2002 | 1884 | 525.1 | 482.7 | 504.6 | 484.2 | 461.4 | 459 | 456.7 | 469.5 | 433.3 | 433.7
2003 | 1885 | 525.1 | 482.7 | 504.6 | 484.2 | 461.5 | 459 | 456.8 | 469.4 | 433.3 | 433.7
2004 | 1886 | 525.1 | 482.7 | 504.6 | 484.2 | 461.5 | 459 | 456.8 | 469.5 | 433.3 | 433.8
2005 | 1887 | 525.1 | 482.7 | 504.6 | 484.2 | 461.6 | 459.1 | 456.8 | 469.5 | 433.3 | 433.9
2006 | 1888 | 525.1 | 482.7 | 504.6 | 484.3 | 461.6 | 459.1 | 456.9 | 469.7 | 433.3 | 434
2007 | 1889 | 525.1 | 482.8 | 504.6 | 484.3 | 461.6 | 459.1 | 456.9 | 469.8 | 433.3 | 434
2008 | 1890 | 525.1 | 482.8 | 504.6 | 484.3 | 461.7 | 459.2 | 456.9 | 469.7 | 433.3 | 434.1
2009 | 1891 | 525.1 | 482.8 | 504.6 | 484.3 | 461.7 | 459.2 | 457 | 469.6 | 433.3 | 434.1
2010 | 1892 | 525.1 | 482.8 | 504.6 | 484.3 | 461.7 | 459.2 | 457 | 469.6 | 433.4 | 434.1
2011 | 1893 | 525.1 | 482.8 | 504.6 | 484.3 | 461.7 | 459.3 | 457.1 | 469.7 | 433.4 | 434.1
2012 | 1894 | 525.1 | 482.8 | 504.6 | 484.4 | 461.8 | 459.3 | 457.1 | 469.8 | 433.4 | 434.1
2013 | 1895 | 525.1 | 482.9 | 504.6 | 484.4 | 461.8 | 459.3 | 457.2 | 470 | 433.4 | 434.2
2014 | 1896 | 525.1 | 482.9 | 504.6 | 484.4 | 461.8 | 459.4 | 457.2 | 470.1 | 433.4 | 434.2
2015 | 1897 | 525.1 | 482.9 | 504.7 | 484.4 | 461.9 | 459.4 | 457.3 | 470.2 | 433.4 | 434.2
2016 | 1898 | 525.1 | 482.9 | 504.6 | 484.4 | 461.9 | 459.4 | 457.3 | 470.2 | 433.4 | 434.3
2017 | 1899 | 525.1 | 483 | 504.5 | 484.5 | 461.9 | 459.5 | 457.3 | 470.2 | 433.4 | 434.3
2018 | 1900 | 525.1 | 483 | 504.4 | 484.5 | 462 | 459.5 | 457.4 | 470.2 | 433.5 | 434.4
2019 | 1901 | 525.1 | 483.1 | 504.4 | 484.5 | 462 | 459.5 | 457.4 | 470.1 | 433.5 | 434.5
2020 | 1902 | 525.1 | 483.1 | 504.4 | 484.6 | 462.1 | 459.6 | 457.5 | 470.2 | 433.5 | 434.5
2021 | 1903 | 525.1 | 483.1 | 504.4 | 484.6 | 462.1 | 459.6 | 457.5 | 470.3 | 433.5 | 434.5
2022 | 1904 | 525.1 | 483.1 | 504.5 | 484.6 | 462.2 | 459.7 | 457.5 | 470.5 | 433.6 | 434.6
2023 | 1905 | 525.1 | 483.1 | 504.5 | 484.6 | 462.1 | 459.7 | 457.6 | 470.5 | 433.6 | 434.5
2024 | 1906 | 525.1 | 483.2 | 504.4 | 484.6 | 462.2 | 459.7 | 457.6 | 470.5 | 433.6 | 434.6
2025 | 1907 | 525.1 | 483.2 | 504.5 | 484.6 | 462.2 | 459.7 | 457.7 | 470.4 | 433.6 | 434.7
2026 | 1908 | 525.1 | 483.2 | 504.5 | 484.6 | 462.3 | 459.8 | 457.7 | 470.4 | 433.7 | 434.9
2027 | 1909 | 525.1 | 483.2 | 504.4 | 484.7 | 462.2 | 459.8 | 457.7 | 470.4 | 433.7 | 434.8
2028 | 1910 | 525.1 | 483.2 | 504.5 | 484.7 | 462.3 | 459.8 | 457.8 | 470.4 | 433.8 | 434.9
2029 | 1911 | 525.1 | 483.2 | 504.5 | 484.7 | 462.4 | 459.9 | 457.8 | 470.3 | 433.8 | 435
2030 | 1912 | 525.1 | 483.2 | 504.5 | 484.7 | 462.4 | 459.9 | 457.9 | 470.3 | 433.9 | 435.2
2031 | 1913 | 525.1 | 483.3 | 504.5 | 484.7 | 462.4 | 459.9 | 457.9 | 470.2 | 433.9 | 435.2
2032 | 1914 | 525.1 | 483.3 | 504.5 | 484.7 | 462.4 | 460 | 457.9 | 470.2 | 433.9 | 435.2
2033 | 1915 | 525.1 | 483.4 | 504.3 | 484.8 | 462.6 | 460.1 | 458 | 470.3 | 434 | 435.3
2034 | 1916 | 525 | 483.4 | 504.3 | 484.8 | 462.5 | 460.1 | 458 | 470.5 | 434 | 435.2
2035 | 1917 | 525 | 483.4 | 504.3 | 484.9 | 462.6 | 460.1 | 458 | 470.7 | 434.1 | 435.2
2036 | 1918 | 525 | 483.4 | 504.4 | 484.8 | 462.7 | 460.2 | 458.1 | 470.7 | 434.1 | 435.3
2037 | 1919 | 525 | 483.5 | 504.3 | 484.9 | 462.6 | 460.2 | 458.1 | 470.8 | 434.2 | 435.3
2038 | 1920 | 525 | 483.5 | 504.4 | 484.9 | 462.7 | 460.2 | 458.1 | 470.8 | 434.3 | 435.5
2039 | 1921 | 525 | 483.5 | 504.4 | 484.9 | 462.7 | 460.2 | 458.2 | 470.7 | 434.3 | 435.5
2040 | 1922 | 525 | 483.5 | 504.4 | 484.9 | 462.8 | 460.3 | 458.2 | 470.8 | 434.4 | 435.5
2041 | 1923 | 525 | 483.5 | 504.4 | 484.9 | 462.8 | 460.3 | 458.3 | 470.9 | 434.5 | 435.6
2042 | 1924 | 525 | 483.5 | 504.4 | 485 | 462.8 | 460.3 | 458.3 | 471 | 434.5 | 435.6
2043 | 1925 | 525 | 483.5 | 504.4 | 485 | 462.9 | 460.4 | 458.3 | 471 | 434.6 | 435.8
2044 | 1926 | 525 | 483.6 | 504.4 | 485 | 462.9 | 460.4 | 458.4 | 470.8 | 434.6 | 435.8
2045 | 1927 | 525.1 | 483.6 | 504.4 | 485 | 462.9 | 460.4 | 458.4 | 470.7 | 434.7 | 435.8
2046 | 1928 | 525.1 | 483.6 | 504.4 | 485 | 463 | 460.5 | 458.4 | 470.8 | 434.8 | 435.9
2047 | 1929 | 525.1 | 483.6 | 504.4 | 485 | 463 | 460.5 | 458.5 | 470.8 | 434.8 | 436
2048 | 1930 | 525.1 | 483.6 | 504.4 | 485 | 463 | 460.5 | 458.5 | 470.7 | 434.9 | 436.1
2049 | 1931 | 525.1 | 483.6 | 504.4 | 485 | 463.1 | 460.6 | 458.5 | 470.8 | 435.1 | 436.2
2050 | 1932 | 525.1 | 483.6 | 504.5 | 485 | 463.2 | 460.6 | 458.6 | 470.9 | 435.2 | 436.1
2051 | 1933 | 525.1 | 483.6 | 504.4 | 485.1 | 463.1 | 460.6 | 458.6 | 471.1 | 435.3 | 436.1
2052 | 1934 | 525.1 | 483.7 | 504.5 | 485.1 | 463.1 | 460.7 | 458.6 | 471.1 | 435.5 | 436.2
2053 | 1935 | 525.1 | 483.6 | 504.5 | 485.1 | 463.2 | 460.7 | 458.7 | 471.1 | 435.5 | 436.2
2054 | 1936 | 525.1 | 483.6 | 504.5 | 485.1 | 463.2 | 460.7 | 458.7 | 471 | 435.6 | 436.3
2055 | 1937 | 525.1 | 483.7 | 504.5 | 485.1 | 463.2 | 460.7 | 458.7 | 471 | 435.7 | 436.3
2056 | 1938 | 525.1 | 483.7 | 504.5 | 485.1 | 463.3 | 460.8 | 458.8 | 471 | 435.8 | 436.4
2057 | 1939 | 525.1 | 483.7 | 504.6 | 485.1 | 463.4 | 460.8 | 458.8 | 471.1 | 435.8 | 436.4
2058 | 1940 | 525.1 | 483.7 | 504.5 | 485.2 | 463.4 | 460.9 | 458.8 | 471.1 | 435.9 | 436.3
2059 | 1941 | 525.1 | 483.7 | 504.5 | 485.2 | 463.4 | 460.9 | 458.9 | 471.2 | 436 | 436.4
2060 | 1942 | 525.1 | 483.8 | 504.5 | 485.2 | 463.5 | 460.9 | 458.9 | 471.4 | 436 | 436.5
2061 | 1943 | 525.1 | 483.8 | 504.6 | 485.2 | 463.5 | 461 | 458.9 | 471.4 | 436.1 | 436.6
2062 | 1944 | 525.1 | 483.8 | 504.5 | 485.2 | 463.5 | 461 | 459 | 471.5 | 436.1 | 436.6
2063 | 1945 | 525.1 | 483.8 | 504.5 | 485.2 | 463.5 | 461 | 459 | 471.6 | 436.2 | 436.7
2064 | 1946 | 525.1 | 483.8 | 504.6 | 485.2 | 463.6 | 461.1 | 459 | 471.7 | 436.2 | 436.6
2065 | 1947 | 525.1 | 483.8 | 504.6 | 485.3 | 463.6 | 461.1 | 459 | 471.8 | 436.3 | 436.6
2066 | 1948 | 525.1 | 483.8 | 504.6 | 485.3 | 463.6 | 461.1 | 459.1 | 471.8 | 436.3 | 436.7
2067 | 1949 | 525.1 | 483.8 | 504.6 | 485.3 | 463.7 | 461.1 | 459.1 | 471.8 | 436.3 | 436.8
2068 | 1950 | 525.1 | 483.8 | 504.6 | 485.3 | 463.7 | 461.2 | 459.2 | 471.7 | 436.4 | 436.9
2069 | 1951 | 525.1 | 483.9 | 504.6 | 485.3 | 463.7 | 461.2 | 459.2 | 471.7 | 436.4 | 436.8
2070 | 1952 | 525.1 | 483.9 | 504.6 | 485.3 | 463.7 | 461.2 | 459.2 | 471.6 | 436.5 | 436.8
2071 | 1953 | 525.1 | 483.9 | 504.7 | 485.3 | 463.8 | 461.3 | 459.3 | 471.5 | 436.5 | 437
2072 | 1954 | 525.1 | 483.9 | 504.6 | 485.3 | 463.8 | 461.3 | 459.3 | 471.6 | 436.5 | 437
2073 | 1955 | 525.1 | 483.9 | 504.6 | 485.4 | 463.8 | 461.3 | 459.3 | 471.5 | 436.6 | 437
2074 | 1956 | 525.1 | 483.9 | 504.7 | 485.4 | 463.9 | 461.4 | 459.4 | 471.5 | 436.6 | 437
2075 | 1957 | 525.1 | 483.9 | 504.7 | 485.4 | 463.9 | 461.4 | 459.4 | 471.5 | 436.7 | 437
2076 | 1958 | 525.1 | 484 | 504.7 | 485.4 | 463.9 | 461.4 | 459.4 | 471.6 | 436.8 | 437.1
2077 | 1959 | 525.1 | 484 | 504.7 | 485.4 | 463.9 | 461.5 | 459.4 | 471.7 | 436.8 | 437.2
2078 | 1960 | 525.1 | 484 | 504.7 | 485.4 | 464.1 | 461.5 | 459.5 | 471.7 | 436.8 | 437.2
2079 | 1961 | 525.1 | 484 | 504.7 | 485.4 | 464 | 461.5 | 459.5 | 471.8 | 436.9 | 437.2
2080 | 1962 | 525.1 | 484 | 504.7 | 485.4 | 464.1 | 461.6 | 459.5 | 471.8 | 437 | 437.3
2081 | 1963 | 525.1 | 484 | 504.8 | 485.4 | 464.1 | 461.6 | 459.6 | 471.8 | 437 | 437.4
2082 | 1964 | 525.1 | 484 | 504.8 | 485.4 | 464.2 | 461.6 | 459.6 | 471.9 | 437.1 | 437.4
2083 | 1965 | 525.1 | 484.1 | 504.7 | 485.5 | 464.1 | 461.7 | 459.6 | 471.9 | 437.1 | 437.5
2084 | 1966 | 525.1 | 484.1 | 504.7 | 485.5 | 464.2 | 461.7 | 459.7 | 472 | 437.2 | 437.6
2085 | 1967 | 525.2 | 484 | 504.8 | 485.5 | 464.3 | 461.7 | 459.7 | 472 | 437.3 | 437.6
2086 | 1968 | 525.2 | 484.1 | 504.8 | 485.5 | 464.3 | 461.8 | 459.7 | 472 | 437.3 | 437.6
2087 | 1969 | 525.2 | 484.1 | 504.8 | 485.5 | 464.3 | 461.8 | 459.7 | 472.1 | 437.4 | 437.7
2088 | 1970 | 525.2 | 484.1 | 504.8 | 485.5 | 464.3 | 461.8 | 459.8 | 472.1 | 437.4 | 437.7
2089 | 1971 | 525.1 | 484.1 | 504.8 | 485.5 | 464.4 | 461.9 | 459.8 | 472.1 | 437.5 | 437.7
2090 | 1972 | 525.1 | 484.1 | 504.8 | 485.6 | 464.4 | 461.9 | 459.8 | 472.1 | 437.5 | 437.7
2091 | 1973 | 525.1 | 484.1 | 504.8 | 485.6 | 464.4 | 461.9 | 459.9 | 472.2 | 437.6 | 437.7
2092 | 1974 | 525.1 | 484.1 | 504.9 | 485.6 | 464.5 | 462 | 459.9 | 472.3 | 437.6 | 437.8
2093 | 1975 | 525.1 | 484.2 | 504.8 | 485.6 | 464.5 | 462 | 459.9 | 472.4 | 437.7 | 437.8
2094 | 1976 | 525.1 | 484.2 | 504.8 | 485.6 | 464.5 | 462 | 460 | 472.5 | 437.7 | 437.8
2095 | 1977 | 525.1 | 484.2 | 504.9 | 485.6 | 464.6 | 462 | 460 | 472.6 | 437.8 | 437.9
2096 | 1978 | 525 | 484.2 | 504.9 | 485.6 | 464.6 | 462.1 | 460 | 472.5 | 437.8 | 438
2097 | 1979 | 525 | 484.2 | 504.8 | 485.6 | 464.6 | 462.1 | 460 | 472.5 | 437.9 | 438.1
2098 | 1980 | 525 | 484.2 | 504.8 | 485.6 | 464.6 | 462.1 | 460.1 | 472.6 | 437.9 | 438.2
2099 | 1981 | 525 | 484.2 | 504.9 | 485.6 | 464.7 | 462.2 | 460.1 | 472.6 | 438 | 438.2
2100 | 1982 | 525 | 484.2 | 504.9 | 485.7 | 464.7 | 462.2 | 460.1 | 472.7 | 438 | 438.2
2101 | 1983 | 525 | 484.3 | 504.8 | 485.7 | 464.7 | 462.2 | 460.2 | 472.8 | 438.1 | 438.2
2102 | 1984 | 525 | 484.3 | 504.9 | 485.7 | 464.8 | 462.3 | 460.2 | 473 | 438.2 | 438.3
2103 | 1985 | 525 | 484.2 | 505 | 485.7 | 464.8 | 462.3 | 460.2 | 473 | 438.3 | 438.2
2104 | 1986 | 525 | 484.3 | 504.9 | 485.7 | 464.8 | 462.3 | 460.3 | 473.1 | 438.3 | 438.2
2105 | 1987 | 525 | 484.3 | 504.9 | 485.7 | 464.8 | 462.3 | 460.3 | 473 | 438.4 | 438.3
2106 | 1988 | 525 | 484.3 | 505 | 485.7 | 464.9 | 462.4 | 460.3 | 473 | 438.4 | 438.3
2107 | 1989 | 525 | 484.3 | 505 | 485.7 | 464.9 | 462.4 | 460.4 | 473 | 438.5 | 438.4
2108 | 1990 | 525 | 484.3 | 504.9 | 485.7 | 464.9 | 462.4 | 460.4 | 473 | 438.6 | 438.4
2109 | 1991 | 525 | 484.3 | 505 | 485.7 | 465 | 462.5 | 460.4 | 473.1 | 438.7 | 438.4
2110 | 1992 | 525 | 484.3 | 505 | 485.7 | 465 | 462.5 | 460.4 | 473.1 | 438.8 | 438.5
2111 | 1993 | 525 | 484.4 | 505 | 485.8 | 465 | 462.5 | 460.5 | 473.2 | 438.8 | 438.5
2112 | 1994 | 525 | 484.4 | 505 | 485.8 | 465 | 462.5 | 460.5 | 473.4 | 438.9 | 438.6
2113 | 1995 | 525.1 | 484.3 | 505.1 | 485.8 | 465.1 | 462.6 | 460.5 | 473.5 | 438.9 | 438.7
2114 | 1996 | 525.1 | 484.4 | 505 | 485.8 | 465.1 | 462.6 | 460.6 | 473.6 | 438.9 | 438.7
2115 | 1997 | 525.1 | 484.4 | 505 | 485.8 | 465.1 | 462.6 | 460.6 | 473.5 | 439 | 438.8
2116 | 1998 | 525.1 | 484.4 | 505.1 | 485.8 | 465.2 | 462.7 | 460.6 | 473.6 | 439 | 438.8
2117 | 1999 | 525.1 | 484.4 | 505.1 | 485.8 | 465.2 | 462.7 | 460.6 | 473.6 | 439.1 | 438.9
2118 | 2000 | 525.1 | 484.4 | 505.1 | 485.8 | 465.2 | 462.7 | 460.7 | 473.7 | 439.2 | 438.9
2119 | 2001 | 525.1 | 484.4 | 505.1 | 485.9 | 465.2 | 462.8 | 460.7 | 473.7 | 439.2 | 439
2120 | 2002 | 525 | 484.4 | 505.1 | 485.9 | 465.3 | 462.8 | 460.7 | 473.7 | 439.3 | 439
2121 | 2003 | 525 | 484.4 | 505.1 | 485.9 | 465.3 | 462.8 | 460.8 | 473.7 | 439.4 | 439
2122 | 2004 | 525 | 484.5 | 505.1 | 485.9 | 465.3 | 462.8 | 460.8 | 473.8 | 439.4 | 439
2123 | 2005 | 525.1 | 484.4 | 505.2 | 485.9 | 465.4 | 462.9 | 460.8 | 473.8 | 439.5 | 439
2124 | 2006 | 525.1 | 484.5 | 505.2 | 485.9 | 465.4 | 462.9 | 460.9 | 473.9 | 439.5 | 439.1
2125 | 2007 | 525.1 | 484.5 | 505.1 | 485.9 | 465.4 | 462.9 | 460.9 | 473.9 | 439.6 | 439.1
2126 | 2008 | 525.1 | 484.5 | 505.1 | 485.9 | 465.5 | 463 | 460.9 | 474 | 439.6 | 439.1
2127 | 2009 | 525.1 | 484.5 | 505.2 | 485.9 | 465.6 | 463 | 460.9 | 474 | 439.7 | 439.2
2128 | 2010 | 525.1 | 484.5 | 505.2 | 485.9 | 465.5 | 463 | 461 | 474 | 439.7 | 439.1
2129 | 2011 | 525.1 | 484.5 | 505.2 | 486 | 465.6 | 463.1 | 461 | 474 | 439.7 | 439.2
2130 | 2012 | 525.1 | 484.5 | 505.2 | 486 | 465.6 | 463.1 | 461 | 474 | 439.8 | 439.2
2131 | 2013 | 525.1 | 484.5 | 505.2 | 486 | 465.7 | 463.1 | 461.1 | 474 | 439.8 | 439.3
2132 | 2014 | 525.1 | 484.6 | 505.2 | 486 | 465.7 | 463.2 | 461.1 | 474 | 439.9 | 439.3
2133 | 2015 | 525.1 | 484.6 | 505.2 | 486 | 465.7 | 463.2 | 461.1 | 474 | 439.9 | 439.3
2134 | 2016 | 525.1 | 484.5 | 505.3 | 486 | 465.8 | 463.2 | 461.1 | 474.1 | 440 | 439.4
2135 | 2017 | 525 | 484.6 | 505.3 | 486 | 465.7 | 463.3 | 461.2 | 474.1 | 440 | 439.5
2136 | 2018 | 525 | 484.6 | 505.3 | 486 | 465.8 | 463.3 | 461.2 | 474.2 | 440.1 | 439.5
2137 | 2019 | 525 | 484.6 | 505.3 | 486 | 465.8 | 463.3 | 461.2 | 474.2 | 440.1 | 439.5
2138 | 2020 | 525 | 484.6 | 505.3 | 486 | 465.9 | 463.4 | 461.3 | 474.3 | 440.2 | 439.5
2139 | 2021 | 525 | 484.6 | 505.3 | 486.1 | 465.8 | 463.4 | 461.3 | 474.3 | 440.3 | 439.5
2140 | 2022 | 525 | 484.6 | 505.3 | 486.1 | 465.9 | 463.4 | 461.3 | 474.3 | 440.4 | 439.5
2141 | 2023 | 525 | 484.6 | 505.4 | 486.1 | 466 | 463.5 | 461.3 | 474.4 | 440.5 | 439.5
2142 | 2024 | 525 | 484.6 | 505.4 | 486.1 | 466 | 463.5 | 461.4 | 474.5 | 440.5 | 439.5
2143 | 2025 | 525 | 484.6 | 505.4 | 486.1 | 466 | 463.5 | 461.4 | 474.6 | 440.6 | 439.5
2144 | 2026 | 525 | 484.6 | 505.4 | 486.1 | 466 | 463.6 | 461.4 | 474.6 | 440.6 | 439.6
2145 | 2027 | 525 | 484.6 | 505.5 | 486.1 | 466.1 | 463.6 | 461.5 | 474.6 | 440.6 | 439.6
2146 | 2028 | 525 | 484.7 | 505.4 | 486.1 | 466.1 | 463.6 | 461.5 | 474.6 | 440.7 | 439.7
2147 | 2029 | 525 | 484.7 | 505.4 | 486.1 | 466.1 | 463.6 | 461.5 | 474.8 | 440.7 | 439.7
2148 | 2030 | 525 | 484.6 | 505.5 | 486.1 | 466.2 | 463.7 | 461.5 | 474.8 | 440.8 | 439.7
2149 | 2031 | 525 | 484.7 | 505.4 | 486.1 | 466.2 | 463.7 | 461.6 | 474.8 | 440.8 | 439.8
2150 | 2032 | 525 | 484.7 | 505.4 | 486.2 | 466.2 | 463.7 | 461.6 | 474.9 | 440.8 | 439.8
2151 | 2033 | 525 | 484.7 | 505.5 | 486.2 | 466.3 | 463.8 | 461.6 | 474.9 | 440.9 | 439.8
2152 | 2034 | 525 | 484.7 | 505.5 | 486.2 | 466.3 | 463.8 | 461.7 | 475 | 440.9 | 439.8
2153 | 2035 | 525 | 484.7 | 505.5 | 486.2 | 466.3 | 463.8 | 461.7 | 475 | 440.9 | 439.9
2154 | 2036 | 525 | 484.8 | 505.5 | 486.2 | 466.3 | 463.9 | 461.7 | 475 | 441 | 439.9
2155 | 2037 | 525 | 484.7 | 505.6 | 486.2 | 466.4 | 463.9 | 461.7 | 475.1 | 441.1 | 439.8
2156 | 2038 | 525 | 484.8 | 505.6 | 486.2 | 466.4 | 463.9 | 461.8 | 475.1 | 441.2 | 439.7
2157 | 2039 | 525 | 484.8 | 505.5 | 486.2 | 466.4 | 464 | 461.8 | 475.1 | 441.2 | 439.8
2158 | 2040 | 525 | 484.8 | 505.6 | 486.2 | 466.5 | 464 | 461.8 | 475.1 | 441.3 | 439.8
2159 | 2041 | 525 | 484.8 | 505.6 | 486.2 | 466.5 | 464.1 | 461.8 | 475.1 | 441.3 | 439.8
2160 | 2042 | 525.1 | 484.8 | 505.6 | 486.3 | 466.5 | 464.1 | 461.9 | 475.1 | 441.3 | 439.8
2161 | 2043 | 525.1 | 484.8 | 505.6 | 486.3 | 466.5 | 464.1 | 461.9 | 475.2 | 441.3 | 439.9
2162 | 2044 | 525.1 | 484.8 | 505.7 | 486.2 | 466.6 | 464.2 | 461.9 | 475.1 | 441.4 | 440.1
2163 | 2045 | 525.1 | 484.8 | 505.6 | 486.3 | 466.6 | 464.2 | 462 | 475.2 | 441.4 | 440.1
2164 | 2046 | 525.1 | 484.8 | 505.7 | 486.3 | 466.6 | 464.2 | 462 | 475.3 | 441.4 | 439.9
2165 | 2047 | 525.1 | 484.8 | 505.8 | 486.3 | 466.7 | 464.2 | 462 | 475.3 | 441.5 | 439.8
2166 | 2048 | 525.1 | 484.6 | 506.1 | 486.2 | 466.5 | 464.2 | 462.1 | 475.3 | 441.6 | 439.9
2167 | 2049 | 525.1 | 484.5 | 506.3 | 486.1 | 466.4 | 464.2 | 462.1 | 475.3 | 441.6 | 440
2168 | 2050 | 525.1 | 484.5 | 506.4 | 486.1 | 466.4 | 464.2 | 462.2 | 475.3 | 441.6 | 440.1
2169 | 2051 | 525.1 | 484.5 | 506.4 | 486.1 | 466.4 | 464.3 | 462.2 | 475.4 | 441.7 | 440.1
2170 | 2052 | 525.1 | 484.5 | 506.4 | 486.1 | 466.4 | 464.3 | 462.2 | 475.5 | 441.8 | 440.1
2171 | 2053 | 525.1 | 484.5 | 506.4 | 486.1 | 466.5 | 464.3 | 462.2 | 475.5 | 441.8 | 440.1
2172 | 2054 | 525.1 | 484.5 | 506.4 | 486.1 | 466.5 | 464.3 | 462.3 | 475.4 | 441.8 | 440.2
2173 | 2055 | 525.2 | 484.5 | 506.5 | 486.1 | 466.6 | 464.4 | 462.3 | 475.4 | 441.8 | 440.1
2174 | 2056 | 525.2 | 484.6 | 506.4 | 486.2 | 466.6 | 464.4 | 462.3 | 475.5 | 441.9 | 440.2
2175 | 2057 | 525.2 | 484.6 | 506.4 | 486.2 | 466.6 | 464.4 | 462.3 | 475.6 | 441.9 | 440.3
2176 | 2058 | 525.2 | 484.5 | 506.5 | 486.2 | 466.7 | 464.5 | 462.4 | 475.7 | 442 | 440.1
2177 | 2059 | 525.2 | 484.6 | 506.5 | 486.2 | 466.7 | 464.5 | 462.4 | 475.7 | 442 | 440.2
2178 | 2060 | 525.2 | 484.6 | 506.5 | 486.2 | 466.7 | 464.5 | 462.4 | 475.7 | 442 | 440.2
2179 | 2061 | 525.2 | 484.6 | 506.5 | 486.2 | 466.8 | 464.6 | 462.5 | 475.7 | 442.1 | 440.2
2180 | 2062 | 525.2 | 484.6 | 506.5 | 486.2 | 466.8 | 464.6 | 462.5 | 475.8 | 442.1 | 440.2
2181 | 2063 | 525.2 | 484.6 | 506.5 | 486.2 | 466.8 | 464.6 | 462.5 | 475.9 | 442.1 | 440.3
2182 | 2064 | 525.3 | 484.6 | 506.5 | 486.2 | 466.8 | 464.7 | 462.5 | 475.9 | 442.2 | 440.4
2183 | 2065 | 525.3 | 484.6 | 506.6 | 486.2 | 466.9 | 464.7 | 462.5 | 475.9 | 442.2 | 440.4
2184 | 2066 | 525.3 | 484.6 | 506.6 | 486.2 | 466.9 | 464.7 | 462.6 | 475.9 | 442.2 | 440.3
2185 | 2067 | 525.3 | 484.6 | 506.6 | 486.3 | 466.9 | 464.8 | 462.6 | 475.9 | 442.3 | 440.3
2186 | 2068 | 525.3 | 484.6 | 506.6 | 486.2 | 467 | 464.8 | 462.6 | 475.9 | 442.3 | 440.3
2187 | 2069 | 525.3 | 484.6 | 506.7 | 486.2 | 467 | 464.8 | 462.7 | 476 | 442.3 | 440.4
2188 | 2070 | 525.3 | 484.7 | 506.6 | 486.3 | 467 | 464.9 | 462.7 | 476.1 | 442.3 | 440.5
2189 | 2071 | 525.3 | 484.7 | 506.7 | 486.3 | 467.1 | 464.9 | 462.7 | 475.9 | 442.3 | 440.5
2190 | 2072 | 525.3 | 484.7 | 506.7 | 486.3 | 467.2 | 465 | 462.7 | 476 | 442.4 | 440.6
2191 | 2073 | 525.3 | 484.7 | 506.7 | 486.3 | 467.2 | 465 | 462.8 | 476.1 | 442.4 | 440.7
2192 | 2074 | 525.4 | 484.7 | 506.7 | 486.3 | 467.2 | 465 | 462.8 | 476.2 | 442.4 | 440.7
2193 | 2075 | 525.3 | 484.7 | 506.7 | 486.3 | 467.3 | 465 | 462.8 | 476.3 | 442.5 | 440.7
2194 | 2076 | 525.3 | 484.7 | 506.8 | 486.3 | 467.3 | 465.1 | 462.9 | 476.3 | 442.6 | 440.7
2195 | 2077 | 525.3 | 484.7 | 506.7 | 486.3 | 467.3 | 465.1 | 462.9 | 476.4 | 442.6 | 440.7
2196 | 2078 | 525.3 | 484.7 | 506.7 | 486.3 | 467.4 | 465.1 | 462.9 | 476.4 | 442.7 | 440.7
2197 | 2079 | 525.4 | 484.7 | 506.8 | 486.3 | 467.4 | 465.2 | 463 | 476.4 | 442.7 | 440.8
2198 | 2080 | 525.3 | 484.8 | 506.7 | 486.4 | 467.4 | 465.2 | 463 | 476.4 | 442.7 | 440.9
2199 | 2081 | 525.3 | 484.8 | 506.7 | 486.4 | 467.5 | 465.2 | 463 | 476.5 | 442.8 | 440.9
2200 | 2082 | 525.3 | 484.7 | 506.8 | 486.4 | 467.5 | 465.3 | 463.1 | 476.5 | 442.8 | 441
2201 | 2083 | 525.3 | 484.7 | 506.8 | 486.4 | 467.6 | 465.3 | 463.1 | 476.6 | 442.8 | 441
2202 | 2084 | 525.3 | 484.8 | 506.8 | 486.4 | 467.6 | 465.3 | 463.1 | 476.7 | 442.9 | 441
2203 | 2085 | 525.3 | 484.8 | 506.8 | 486.4 | 467.6 | 465.3 | 463.2 | 476.7 | 442.9 | 441
2204 | 2086 | 525.3 | 484.7 | 506.9 | 486.4 | 467.7 | 465.4 | 463.2 | 476.8 | 443 | 441
2205 | 2087 | 525.3 | 484.8 | 506.8 | 486.4 | 467.7 | 465.4 | 463.2 | 476.8 | 443 | 441.1
2206 | 2088 | 525.2 | 484.8 | 506.8 | 486.4 | 467.7 | 465.4 | 463.3 | 476.8 | 443.1 | 441.1
2207 | 2089 | 525.2 | 484.8 | 506.9 | 486.4 | 467.7 | 465.5 | 463.3 | 476.9 | 443.1 | 441.1
2208 | 2090 | 525.2 | 484.8 | 506.9 | 486.4 | 467.8 | 465.5 | 463.3 | 476.9 | 443.2 | 441.2
2209 | 2091 | 525.2 | 484.8 | 506.9 | 486.4 | 467.8 | 465.5 | 463.4 | 477 | 443.2 | 441.1
2210 | 2092 | 525.2 | 484.8 | 506.9 | 486.5 | 467.9 | 465.6 | 463.4 | 477 | 443.3 | 441.2
2211 | 2093 | 525.2 | 484.8 | 507 | 486.5 | 467.9 | 465.6 | 463.4 | 477.1 | 443.3 | 441.2
2212 | 2094 | 525.2 | 484.8 | 507 | 486.5 | 467.9 | 465.6 | 463.5 | 477.2 | 443.4 | 441.2
2213 | 2095 | 525.2 | 484.8 | 507 | 486.5 | 467.9 | 465.7 | 463.5 | 477.1 | 443.5 | 441.2
2214 | 2096 | 525.2 | 484.8 | 507 | 486.5 | 468 | 465.7 | 463.5 | 477.2 | 443.5 | 441.2
2215 | 2097 | 525.2 | 484.8 | 507 | 486.5 | 468 | 465.8 | 463.6 | 477.3 | 443.6 | 441.2
2216 | 2098 | 525.2 | 484.8 | 507 | 486.5 | 468 | 465.8 | 463.6 | 477.3 | 443.6 | 441.2
2217 | 2099 | 525.2 | 484.8 | 507 | 486.5 | 468.1 | 465.8 | 463.6 | 477.4 | 443.7 | 441.2
2218 | 2100 | 525.2 | 484.8 | 507.1 | 486.5 | 468.2 | 465.9 | 463.7 | 477.4 | 443.8 | 441.2
2219 | 2101 | 525.2 | 484.8 | 507.1 | 486.5 | 468.2 | 465.9 | 463.7 | 477.4 | 443.8 | 441.3
2220 | 2102 | 525.2 | 484.8 | 507.1 | 486.5 | 468.2 | 465.9 | 463.7 | 477.5 | 443.9 | 441.3
2221 | 2103 | 525.2 | 484.8 | 507.1 | 486.5 | 468.2 | 466 | 463.8 | 477.5 | 443.9 | 441.3
2222 | 2104 | 525.2 | 484.8 | 507.1 | 486.5 | 468.3 | 466 | 463.8 | 477.4 | 444 | 441.2
2223 | 2105 | 525.2 | 484.8 | 507.1 | 486.6 | 468.3 | 466 | 463.9 | 477.5 | 444.1 | 441.3
2224 | 2106 | 525.2 | 484.9 | 507.1 | 486.6 | 468.3 | 466.1 | 463.9 | 477.5 | 444.1 | 441.3
2225 | 2107 | 525.2 | 484.7 | 507.3 | 486.5 | 468.3 | 466.1 | 463.9 | 477.6 | 444.2 | 441.4
2226 | 2108 | 525.2 | 484.6 | 507.6 | 486.4 | 468.1 | 466 | 464 | 477.6 | 444.2 | 441.4
2227 | 2109 | 525.1 | 484.5 | 507.8 | 486.3 | 468 | 466 | 464 | 477.7 | 444.2 | 441.5
2228 | 2110 | 525 | 484.5 | 507.9 | 486.3 | 468.1 | 466.1 | 464.1 | 477.8 | 444.2 | 441.5
2229 | 2111 | 524.8 | 484.5 | 507.9 | 486.3 | 468.1 | 466.1 | 464.1 | 477.9 | 444.3 | 441.5
2230 | 2112 | 524.5 | 484.5 | 507.8 | 486.3 | 468.1 | 466.1 | 464.1 | 477.9 | 444.4 | 441.5
2231 | 2113 | 524.2 | 484.5 | 507.8 | 486.3 | 468.2 | 466.2 | 464.2 | 477.9 | 444.5 | 441.5
2232 | 2114 | 523.7 | 484.5 | 507.8 | 486.3 | 468.2 | 466.2 | 464.2 | 477.9 | 444.5 | 441.5
2233 | 2115 | 523.2 | 484.5 | 507.7 | 486.3 | 468.2 | 466.3 | 464.2 | 477.9 | 444.6 | 441.5
2234 | 2116 | 522.7 | 484.5 | 507.7 | 486.3 | 468.3 | 466.3 | 464.3 | 478 | 444.7 | 441.6
2235 | 2117 | 522.2 | 484.4 | 507.7 | 486.3 | 468.3 | 466.3 | 464.3 | 478.1 | 444.7 | 441.6
2236 | 2118 | 521.6 | 484.4 | 507.6 | 486.3 | 468.4 | 466.4 | 464.3 | 478.2 | 444.7 | 441.5
2237 | 2119 | 520.9 | 484.4 | 507.6 | 486.2 | 468.4 | 466.4 | 464.4 | 478.1 | 444.8 | 441.5
2238 | 2120 | 520.3 | 484.4 | 507.6 | 486.2 | 468.4 | 466.4 | 464.4 | 478.2 | 444.8 | 441.6
2239 | 2121 | 519.6 | 484.3 | 507.6 | 486.2 | 468.5 | 466.5 | 464.5 | 478.2 | 444.9 | 441.6
2240 | 2122 | 519 | 484.3 | 507.4 | 486.2 | 468.5 | 466.5 | 464.5 | 478.3 | 444.9 | 441.6
2241 | 2123 | 518.3 | 484.3 | 507.4 | 486.2 | 468.6 | 466.6 | 464.5 | 478.4 | 445 | 441.5
2242 | 2124 | 517.6 | 484.2 | 507.4 | 486.1 | 468.6 | 466.6 | 464.6 | 478.4 | 445 | 441.5
2243 | 2125 | 516.9 | 484.2 | 507.3 | 486.1 | 468.7 | 466.6 | 464.6 | 478.4 | 445 | 441.5
2244 | 2126 | 516.1 | 484.2 | 507.2 | 486.1 | 468.7 | 466.7 | 464.6 | 478.4 | 445.1 | 441.6
2245 | 2127 | 515.4 | 484.2 | 507.1 | 486 | 468.8 | 466.7 | 464.7 | 478.4 | 445.1 | 441.7
2246 | 2128 | 514.7 | 484.1 | 507.1 | 486 | 468.8 | 466.8 | 464.7 | 478.4 | 445.2 | 441.7
2247 | 2129 | 513.9 | 484.1 | 507 | 486 | 468.8 | 466.8 | 464.7 | 478.5 | 445.2 | 441.7
2248 | 2130 | 513.2 | 484 | 506.9 | 485.9 | 468.9 | 466.8 | 464.8 | 478.6 | 445.3 | 441.7
2249 | 2131 | 512.4 | 484 | 506.8 | 485.9 | 468.9 | 466.9 | 464.8 | 478.7 | 445.3 | 441.8
2250 | 2132 | 511.7 | 483.9 | 506.8 | 485.8 | 469 | 466.9 | 464.9 | 478.7 | 445.4 | 441.8
2251 | 2133 | 510.9 | 483.9 | 506.7 | 485.8 | 469 | 467 | 464.9 | 478.7 | 445.4 | 441.7
2252 | 2134 | 510.1 | 483.8 | 506.6 | 485.7 | 469 | 467 | 464.9 | 478.8 | 445.4 | 441.7
2253 | 2135 | 509.4 | 483.7 | 506.5 | 485.7 | 469.1 | 467 | 465 | 478.8 | 445.4 | 441.7
2254 | 2136 | 508.6 | 483.7 | 506.4 | 485.6 | 469.1 | 467.1 | 465 | 478.8 | 445.4 | 441.6
2255 | 2137 | 507.8 | 483.6 | 506.3 | 485.6 | 469.1 | 467.1 | 465 | 478.8 | 445.4 | 441.6
2256 | 2138 | 507 | 483.6 | 506.2 | 485.5 | 469.2 | 467.2 | 465.1 | 478.8 | 445.5 | 441.6
2257 | 2139 | 506.3 | 483.5 | 506.1 | 485.4 | 469.2 | 467.2 | 465.1 | 478.9 | 445.6 | 441.6
2258 | 2140 | 505.5 | 483.4 | 506 | 485.4 | 469.3 | 467.2 | 465.1 | 478.9 | 445.7 | 441.6
2259 | 2141 | 504.7 | 483.4 | 505.9 | 485.3 | 469.3 | 467.3 | 465.2 | 478.9 | 445.7 | 441.6
2260 | 2142 | 504 | 483.3 | 505.8 | 485.3 | 469.4 | 467.3 | 465.2 | 479 | 445.8 | 441.5
2261 | 2143 | 503.2 | 483.2 | 505.7 | 485.2 | 469.4 | 467.4 | 465.2 | 479 | 445.8 | 441.5
2262 | 2144 | 502.4 | 483.1 | 505.6 | 485.1 | 469.4 | 467.4 | 465.3 | 479 | 445.8 | 441.5
2263 | 2145 | 501.6 | 483.1 | 505.5 | 485 | 469.5 | 467.4 | 465.3 | 479 | 445.8 | 441.4
2264 | 2146 | 500.9 | 483 | 505.4 | 485 | 469.5 | 467.5 | 465.4 | 479 | 445.8 | 441.4
2265 | 2147 | 500.1 | 482.9 | 505.2 | 484.9 | 469.5 | 467.5 | 465.4 | 479.1 | 445.8 | 441.4
2266 | 2148 | 499.4 | 482.8 | 505.1 | 484.8 | 469.6 | 467.5 | 465.4 | 479.2 | 445.8 | 441.4
2267 | 2149 | 498.7 | 482.7 | 505 | 484.7 | 469.6 | 467.6 | 465.5 | 479.3 | 445.9 | 441.2
2268 | 2150 | 497.9 | 482.6 | 504.9 | 484.7 | 469.6 | 467.6 | 465.5 | 479.4 | 445.9 | 441.1
2269 | 2151 | 497.1 | 482.6 | 504.7 | 484.6 | 469.7 | 467.7 | 465.5 | 479.4 | 446 | 441
2270 | 2152 | 496.4 | 482.5 | 504.6 | 484.5 | 469.7 | 467.7 | 465.5 | 479.4 | 446 | 441
2271 | 2153 | 495.6 | 482.4 | 504.5 | 484.4 | 469.8 | 467.7 | 465.6 | 479.4 | 446 | 441
2272 | 2154 | 494.8 | 482.3 | 504.4 | 484.3 | 469.8 | 467.8 | 465.6 | 479.4 | 446 | 441
2273 | 2155 | 494.1 | 482.2 | 504.2 | 484.2 | 469.8 | 467.8 | 465.6 | 479.4 | 446.1 | 441
2274 | 2156 | 493.4 | 482.1 | 504.1 | 484.1 | 469.9 | 467.9 | 465.7 | 479.3 | 446.1 | 440.9
2275 | 2157 | 492.6 | 482 | 504 | 484 | 469.9 | 467.9 | 465.7 | 479.3 | 446.2 | 440.9
2276 | 2158 | 491.9 | 481.9 | 503.8 | 483.9 | 469.9 | 467.9 | 465.7 | 479.3 | 446.2 | 440.9
2277 | 2159 | 491.1 | 481.8 | 503.7 | 483.9 | 470 | 468 | 465.8 | 479.3 | 446.2 | 440.9
2278 | 2160 | 490.4 | 481.7 | 503.5 | 483.8 | 470 | 468 | 465.8 | 479.3 | 446.3 | 440.9
2279 | 2161 | 489.6 | 481.6 | 503.4 | 483.7 | 470.1 | 468 | 465.8 | 479.3 | 446.3 | 440.8
2280 | 2162 | 488.8 | 481.5 | 503.2 | 483.5 | 470.1 | 468.1 | 465.9 | 479.3 | 446.4 | 440.8
2281 | 2163 | 488.1 | 481.3 | 503.1 | 483.4 | 470.2 | 468.1 | 465.9 | 479.3 | 446.4 | 440.8
2282 | 2164 | 487.3 | 481.2 | 502.9 | 483.3 | 470.2 | 468.1 | 465.9 | 479.3 | 446.5 | 440.8
2283 | 2165 | 486.6 | 481.1 | 502.8 | 483.2 | 470.2 | 468.2 | 466 | 479.3 | 446.5 | 440.7
2284 | 2166 | 485.8 | 481 | 502.6 | 483.1 | 470.2 | 468.2 | 466 | 479.3 | 446.5 | 440.7
2285 | 2167 | 485.1 | 480.9 | 502.5 | 483 | 470.3 | 468.2 | 466 | 479.2 | 446.5 | 440.7
2286 | 2168 | 484.3 | 480.8 | 502.3 | 482.9 | 470.3 | 468.2 | 466 | 479.2 | 446.5 | 440.7
2287 | 2169 | 483.5 | 480.7 | 502.1 | 482.8 | 470.3 | 468.3 | 466.1 | 479.2 | 446.5 | 440.6
2288 | 2170 | 482.8 | 480.5 | 502 | 482.7 | 470.4 | 468.3 | 466.1 | 479.3 | 446.5 | 440.6
2289 | 2171 | 482.1 | 480.4 | 501.8 | 482.5 | 470.4 | 468.3 | 466.1 | 479.3 | 446.6 | 440.6
2290 | 2172 | 481.3 | 480.3 | 501.6 | 482.4 | 470.4 | 468.4 | 466.1 | 479.4 | 446.6 | 440.5
2291 | 2173 | 480.6 | 480.2 | 501.5 | 482.3 | 470.4 | 468.4 | 466.1 | 479.3 | 446.6 | 440.5
2292 | 2174 | 479.9 | 480 | 501.3 | 482.2 | 470.5 | 468.4 | 466.2 | 479.3 | 446.7 | 440.5
2293 | 2175 | 479.1 | 479.9 | 501.1 | 482.1 | 470.5 | 468.5 | 466.2 | 479.3 | 446.7 | 440.4
2294 | 2176 | 478.4 | 479.8 | 500.9 | 481.9 | 470.5 | 468.5 | 466.2 | 479.3 | 446.8 | 440.3
2295 | 2177 | 477.7 | 479.6 | 500.8 | 481.8 | 470.6 | 468.5 | 466.2 | 479.3 | 446.8 | 440.3
2296 | 2178 | 477 | 479.5 | 500.6 | 481.7 | 470.6 | 468.5 | 466.3 | 479.4 | 446.8 | 440.2
2297 | 2179 | 476.3 | 479.4 | 500.4 | 481.6 | 470.6 | 468.6 | 466.3 | 479.3 | 446.8 | 440.2
2298 | 2180 | 475.6 | 479.2 | 500.2 | 481.4 | 470.6 | 468.6 | 466.3 | 479.4 | 446.8 | 440.1
2299 | 2181 | 474.9 | 479.1 | 500.1 | 481.3 | 470.7 | 468.6 | 466.3 | 479.4 | 446.8 | 440.1
2300 | 2182 | 474.2 | 479 | 500 | 481.2 | 470.7 | 468.6 | 466.3 | 479.4 | 446.8 | 440.1
2301 | 2183 | 473.6 | 478.8 | 499.8 | 481 | 470.7 | 468.7 | 466.3 | 479.4 | 446.9 | 439.9
2302 | 2184 | 472.9 | 478.7 | 499.7 | 480.9 | 470.8 | 468.7 | 466.4 | 479.5 | 446.9 | 439.9
2303 | 2185 | 472.2 | 478.6 | 499.5 | 480.8 | 470.8 | 468.7 | 466.4 | 479.4 | 446.9 | 439.9
2304 | 2186 | 471.5 | 478.4 | 499.3 | 480.6 | 470.8 | 468.7 | 466.4 | 479.4 | 446.9 | 439.9
2305 | 2187 | 470.8 | 478.3 | 499.1 | 480.5 | 470.8 | 468.8 | 466.4 | 479.3 | 447 | 439.8
2306 | 2188 | 470.2 | 478.1 | 498.9 | 480.3 | 470.8 | 468.8 | 466.4 | 479.3 | 447 | 439.7
2307 | 2189 | 469.5 | 478 | 498.7 | 480.2 | 470.8 | 468.8 | 466.4 | 479.3 | 446.9 | 439.6
2308 | 2190 | 468.8 | 477.8 | 498.5 | 480.1 | 470.8 | 468.8 | 466.5 | 479.3 | 446.9 | 439.6
2309 | 2191 | 468.1 | 477.7 | 498.3 | 479.9 | 470.9 | 468.8 | 466.5 | 479.2 | 446.9 | 439.6
2310 | 2192 | 467.4 | 477.5 | 498.1 | 479.8 | 470.9 | 468.9 | 466.5 | 479.2 | 446.9 | 439.5
2311 | 2193 | 466.8 | 477.4 | 497.9 | 479.6 | 470.9 | 468.9 | 466.5 | 479.1 | 446.9 | 439.4
2312 | 2194 | 466.1 | 477.2 | 497.7 | 479.5 | 470.9 | 468.9 | 466.5 | 479 | 446.9 | 439.4
2313 | 2195 | 465.4 | 477 | 497.6 | 479.3 | 470.9 | 468.9 | 466.5 | 479 | 446.9 | 439.3
2314 | 2196 | 464.8 | 476.9 | 497.3 | 479.2 | 470.9 | 468.9 | 466.5 | 479.1 | 446.8 | 439.2
2315 | 2197 | 464.1 | 476.7 | 497.1 | 479 | 471 | 468.9 | 466.5 | 479.1 | 446.8 | 439.1
2316 | 2198 | 463.5 | 476.6 | 496.9 | 478.9 | 471 | 469 | 466.5 | 479 | 446.8 | 439.1
2317 | 2199 | 462.8 | 476.4 | 496.7 | 478.7 | 471 | 469 | 466.6 | 479 | 446.9 | 439.1
2318 | 2200 | 462.2 | 476.3 | 496.5 | 478.6 | 471 | 469 | 466.6 | 478.9 | 446.8 | 438.9
2319 | 2201 | 461.5 | 476.1 | 496.3 | 478.4 | 471 | 469 | 466.6 | 478.8 | 446.8 | 438.9
2320 | 2202 | 460.9 | 475.9 | 496.1 | 478.2 | 471 | 469 | 466.6 | 478.8 | 446.9 | 438.8
2321 | 2203 | 460.2 | 475.8 | 495.9 | 478.1 | 471 | 469 | 466.6 | 478.7 | 446.9 | 438.8
2322 | 2204 | 459.5 | 475.6 | 495.6 | 477.9 | 471.1 | 469 | 466.6 | 478.7 | 446.9 | 438.7
2323 | 2205 | 458.9 | 475.5 | 495.5 | 477.8 | 471.1 | 469.1 | 466.6 | 478.7 | 447 | 438.6
2324 | 2206 | 458.2 | 475.3 | 495.2 | 477.6 | 471.1 | 469.1 | 466.6 | 478.7 | 447 | 438.6
2325 | 2207 | 457.5 | 475.1 | 495 | 477.5 | 471.1 | 469.1 | 466.6 | 478.7 | 447 | 438.6
2326 | 2208 | 456.9 | 475 | 494.8 | 477.3 | 471.1 | 469.1 | 466.6 | 478.6 | 447.1 | 438.5
2327 | 2209 | 456.2 | 474.8 | 494.6 | 477.1 | 471.1 | 469.1 | 466.6 | 478.5 | 447.1 | 438.5
2328 | 2210 | 455.6 | 474.6 | 494.4 | 477 | 471.1 | 469.1 | 466.6 | 478.5 | 447.1 | 438.4
2329 | 2211 | 455 | 474.5 | 494.1 | 476.8 | 471.1 | 469.1 | 466.6 | 478.5 | 447 | 438.3
2330 | 2212 | 454.4 | 474.3 | 494 | 476.6 | 471.1 | 469.1 | 466.6 | 478.5 | 447.1 | 438.3
2331 | 2213 | 453.7 | 474.1 | 493.7 | 476.5 | 471.1 | 469.1 | 466.6 | 478.4 | 447.1 | 438.2
2332 | 2214 | 453.1 | 473.9 | 493.5 | 476.3 | 471.1 | 469.1 | 466.6 | 478.3 | 447.1 | 438
2333 | 2215 | 452.5 | 473.8 | 493.3 | 476.1 | 471.2 | 469.1 | 466.6 | 478.3 | 447.1 | 437.9
2334 | 2216 | 451.8 | 473.6 | 493.1 | 475.9 | 471.2 | 469.1 | 466.6 | 478.4 | 447.1 | 437.9
2335 | 2217 | 451.2 | 473.4 | 492.8 | 475.8 | 471.1 | 469.1 | 466.6 | 478.4 | 447 | 437.9
2336 | 2218 | 450.5 | 473.2 | 492.6 | 475.6 | 471.1 | 469.1 | 466.6 | 478.5 | 447.1 | 437.8
2337 | 2219 | 449.9 | 473 | 492.4 | 475.4 | 471.1 | 469.1 | 466.6 | 478.5 | 447.1 | 437.7
2338 | 2220 | 449.3 | 472.9 | 492.2 | 475.3 | 471.1 | 469.1 | 466.6 | 478.5 | 447.1 | 437.6
2339 | 2221 | 448.7 | 472.7 | 491.9 | 475.1 | 471.1 | 469.1 | 466.6 | 478.4 | 447.1 | 437.5
2340 | 2222 | 448 | 472.5 | 491.7 | 474.9 | 471.1 | 469.1 | 466.6 | 478.4 | 447.1 | 437.4
2341 | 2223 | 447.4 | 472.3 | 491.5 | 474.7 | 471.1 | 469.1 | 466.6 | 478.4 | 447.1 | 437.4
2342 | 2224 | 446.8 | 472.1 | 491.2 | 474.5 | 471.1 | 469.1 | 466.6 | 478.4 | 447.1 | 437.4
2343 | 2225 | 446.2 | 472 | 491 | 474.4 | 471.1 | 469.1 | 466.6 | 478.2 | 447.1 | 437.3
2344 | 2226 | 445.6 | 471.8 | 490.8 | 474.2 | 471.2 | 469.1 | 466.5 | 478.1 | 447.2 | 437.2
2345 | 2227 | 445 | 471.6 | 490.5 | 474 | 471.1 | 469.1 | 466.5 | 478 | 447.1 | 437.1
2346 | 2228 | 444.4 | 471.4 | 490.3 | 473.8 | 471.1 | 469.1 | 466.5 | 478 | 447.1 | 437
2347 | 2229 | 443.8 | 471.2 | 490.1 | 473.6 | 471.1 | 469.1 | 466.5 | 478.1 | 447.1 | 436.9
2348 | 2230 | 443.2 | 471 | 489.8 | 473.4 | 471.1 | 469.1 | 466.5 | 478 | 447.1 | 436.8
2349 | 2231 | 442.6 | 470.8 | 489.6 | 473.3 | 471.1 | 469.1 | 466.5 | 477.9 | 447.1 | 436.7
2350 | 2232 | 442 | 470.6 | 489.3 | 473.1 | 471.1 | 469.1 | 466.5 | 477.9 | 447 | 436.6
2351 | 2233 | 441.4 | 470.4 | 489.1 | 472.9 | 471.1 | 469.1 | 466.5 | 477.7 | 447 | 436.5
2352 | 2234 | 440.8 | 470.3 | 488.9 | 472.7 | 471.1 | 469 | 466.5 | 477.5 | 447 | 436.5
2353 | 2235 | 440.2 | 470.1 | 488.6 | 472.5 | 471 | 469 | 466.4 | 477.5 | 446.9 | 436.4
2354 | 2236 | 439.6 | 469.9 | 488.4 | 472.3 | 471 | 469 | 466.4 | 477.5 | 446.9 | 436.3
2355 | 2237 | 439 | 469.7 | 488.2 | 472.1 | 471 | 469 | 466.4 | 477.4 | 446.9 | 436.2
2356 | 2238 | 438.4 | 469.5 | 487.9 | 472 | 471 | 469 | 466.4 | 477.4 | 446.9 | 436.1
2357 | 2239 | 437.8 | 469.3 | 487.7 | 471.8 | 471 | 469 | 466.4 | 477.4 | 446.9 | 436
2358 | 2240 | 437.2 | 469.1 | 487.4 | 471.6 | 471 | 469 | 466.4 | 477.3 | 447 | 435.9
2359 | 2241 | 436.6 | 468.9 | 487.2 | 471.4 | 470.9 | 469 | 466.3 | 477.2 | 447 | 435.8
2360 | 2242 | 436 | 468.7 | 486.9 | 471.2 | 470.9 | 468.9 | 466.3 | 477.1 | 447 | 435.7
2361 | 2243 | 435.5 | 468.5 | 486.7 | 471 | 470.9 | 468.9 | 466.3 | 477.1 | 446.9 | 435.6
2362 | 2244 | 434.9 | 468.3 | 486.5 | 470.8 | 470.9 | 468.9 | 466.3 | 477 | 446.9 | 435.6
2363 | 2245 | 434.3 | 468.1 | 486.2 | 470.6 | 470.9 | 468.9 | 466.3 | 476.9 | 446.9 | 435.5
2364 | 2246 | 433.8 | 467.9 | 486 | 470.4 | 470.8 | 468.9 | 466.2 | 476.9 | 446.9 | 435.3
2365 | 2247 | 433.2 | 467.7 | 485.8 | 470.2 | 470.8 | 468.9 | 466.2 | 476.8 | 446.9 | 435.2
2366 | 2248 | 432.6 | 467.5 | 485.5 | 470 | 470.8 | 468.8 | 466.2 | 476.7 | 446.9 | 435.1
2367 | 2249 | 432 | 467.3 | 485.2 | 469.8 | 470.8 | 468.8 | 466.2 | 476.6 | 446.9 | 435
2368 | 2250 | 431.4 | 467.1 | 485 | 469.6 | 470.7 | 468.8 | 466.1 | 476.5 | 446.9 | 434.9
2369 | 2251 | 430.8 | 466.9 | 484.8 | 469.4 | 470.7 | 468.8 | 466.1 | 476.4 | 446.9 | 434.8
2370 | 2252 | 430.3 | 466.7 | 484.5 | 469.2 | 470.7 | 468.7 | 466.1 | 476.3 | 446.9 | 434.8
2371 | 2253 | 429.7 | 466.5 | 484.2 | 469 | 470.7 | 468.7 | 466.1 | 476.3 | 446.8 | 434.6
2372 | 2254 | 429.1 | 466.3 | 484 | 468.8 | 470.7 | 468.7 | 466 | 476.1 | 446.8 | 434.5
2373 | 2255 | 428.6 | 466.1 | 483.7 | 468.6 | 470.6 | 468.7 | 466 | 476 | 446.8 | 434.4
2374 | 2256 | 428 | 465.9 | 483.5 | 468.4 | 470.6 | 468.6 | 466 | 475.9 | 446.8 | 434.3
2375 | 2257 | 427.5 | 465.7 | 483.3 | 468.2 | 470.5 | 468.6 | 465.9 | 475.8 | 446.8 | 434.3
2376 | 2258 | 427 | 465.5 | 483 | 468 | 470.5 | 468.6 | 465.9 | 475.7 | 446.7 | 434.2
2377 | 2259 | 426.4 | 465.3 | 482.7 | 467.8 | 470.5 | 468.6 | 465.9 | 475.8 | 446.7 | 434.1
2378 | 2260 | 425.9 | 465.1 | 482.5 | 467.6 | 470.5 | 468.5 | 465.8 | 475.7 | 446.7 | 434
2379 | 2261 | 425.3 | 464.9 | 482.2 | 467.4 | 470.4 | 468.5 | 465.8 | 475.6 | 446.7 | 433.8
2380 | 2262 | 424.8 | 464.7 | 482 | 467.2 | 470.4 | 468.5 | 465.8 | 475.5 | 446.6 | 433.7
2381 | 2263 | 424.3 | 464.5 | 481.7 | 467 | 470.4 | 468.4 | 465.7 | 475.5 | 446.6 | 433.6
2382 | 2264 | 423.8 | 464.3 | 481.5 | 466.8 | 470.3 | 468.4 | 465.7 | 475.3 | 446.6 | 433.5
2383 | 2265 | 423.2 | 464.1 | 481.2 | 466.6 | 470.3 | 468.4 | 465.7 | 475.2 | 446.6 | 433.4
2384 | 2266 | 422.7 | 463.8 | 480.9 | 466.4 | 470.2 | 468.3 | 465.6 | 475.1 | 446.5 | 433.3
2385 | 2267 | 422.1 | 463.6 | 480.7 | 466.2 | 470.2 | 468.3 | 465.6 | 475.1 | 446.5 | 433.2
2386 | 2268 | 421.6 | 463.4 | 480.5 | 465.9 | 470.2 | 468.3 | 465.6 | 475 | 446.5 | 433.1
2387 | 2269 | 421.1 | 463.2 | 480.2 | 465.7 | 470.2 | 468.2 | 465.5 | 474.9 | 446.4 | 433
2388 | 2270 | 420.5 | 463 | 479.9 | 465.5 | 470.1 | 468.2 | 465.5 | 474.9 | 446.4 | 432.9
2389 | 2271 | 420 | 462.8 | 479.7 | 465.3 | 470.1 | 468.2 | 465.4 | 474.9 | 446.3 | 432.8
2390 | 2272 | 419.5 | 462.6 | 479.4 | 465.1 | 470.1 | 468.1 | 465.4 | 474.8 | 446.3 | 432.7
2391 | 2273 | 418.9 | 462.4 | 479.1 | 464.9 | 470 | 468.1 | 465.4 | 474.7 | 446.3 | 432.5
2392 | 2274 | 418.4 | 462.2 | 478.9 | 464.7 | 470 | 468 | 465.3 | 474.6 | 446.2 | 432.4
2393 | 2275 | 417.9 | 461.9 | 478.7 | 464.5 | 469.9 | 468 | 465.3 | 474.6 | 446.2 | 432.4
2394 | 2276 | 417.3 | 461.7 | 478.4 | 464.3 | 469.9 | 468 | 465.2 | 474.6 | 446.2 | 432.3
2395 | 2277 | 416.8 | 461.5 | 478.1 | 464.1 | 469.8 | 467.9 | 465.2 | 474.5 | 446.1 | 432.1
2396 | 2278 | 416.3 | 461.3 | 477.8 | 463.8 | 469.8 | 467.9 | 465.1 | 474.4 | 446.1 | 432
2397 | 2279 | 415.8 | 461.1 | 477.6 | 463.6 | 469.7 | 467.8 | 465.1 | 474.3 | 446.1 | 431.9
2398 | 2280 | 415.2 | 460.9 | 477.3 | 463.4 | 469.7 | 467.8 | 465 | 474.1 | 446 | 431.8
2399 | 2281 | 414.7 | 460.7 | 477 | 463.2 | 469.6 | 467.7 | 465 | 474 | 446 | 431.7
2400 | 2282 | 414.2 | 460.4 | 476.8 | 463 | 469.6 | 467.7 | 464.9 | 473.9 | 445.9 | 431.6
2401 | 2283 | 413.7 | 460.2 | 476.5 | 462.8 | 469.5 | 467.6 | 464.9 | 473.8 | 445.9 | 431.5
2402 | 2284 | 413.2 | 460 | 476.3 | 462.6 | 469.5 | 467.6 | 464.9 | 473.7 | 445.9 | 431.4
2403 | 2285 | 412.7 | 459.8 | 476 | 462.3 | 469.4 | 467.6 | 464.8 | 473.6 | 445.8 | 431.3
2404 | 2286 | 412.2 | 459.6 | 475.8 | 462.1 | 469.4 | 467.5 | 464.7 | 473.5 | 445.8 | 431.1
2405 | 2287 | 411.6 | 459.4 | 475.5 | 461.9 | 469.3 | 467.5 | 464.7 | 473.4 | 445.7 | 431
2406 | 2288 | 411.1 | 459.1 | 475.2 | 461.7 | 469.2 | 467.4 | 464.6 | 473.3 | 445.7 | 430.9
2407 | 2289 | 410.6 | 458.9 | 475 | 461.5 | 469.2 | 467.4 | 464.6 | 473.1 | 445.6 | 430.8
2408 | 2290 | 410.1 | 458.7 | 474.7 | 461.2 | 469.1 | 467.3 | 464.5 | 473 | 445.6 | 430.7
2409 | 2291 | 409.7 | 458.5 | 474.4 | 461 | 469.1 | 467.3 | 464.5 | 473 | 445.6 | 430.6
2410 | 2292 | 409.2 | 458.2 | 474.2 | 460.8 | 469 | 467.2 | 464.4 | 472.8 | 445.5 | 430.5
2411 | 2293 | 408.7 | 458 | 474 | 460.6 | 469 | 467.2 | 464.4 | 472.7 | 445.5 | 430.4
2412 | 2294 | 408.2 | 457.8 | 473.7 | 460.4 | 468.9 | 467.1 | 464.3 | 472.6 | 445.5 | 430.2
2413 | 2295 | 407.7 | 457.6 | 473.4 | 460.2 | 468.8 | 467 | 464.3 | 472.6 | 445.4 | 430.1
2414 | 2296 | 407.2 | 457.4 | 473.1 | 459.9 | 468.8 | 467 | 464.2 | 472.6 | 445.4 | 430
2415 | 2297 | 406.7 | 457.1 | 472.9 | 459.7 | 468.7 | 466.9 | 464.1 | 472.5 | 445.3 | 429.9
2416 | 2298 | 406.2 | 456.9 | 472.6 | 459.5 | 468.7 | 466.9 | 464.1 | 472.3 | 445.2 | 429.7
2417 | 2299 | 405.7 | 456.7 | 472.4 | 459.3 | 468.6 | 466.8 | 464 | 472.2 | 445.2 | 429.6
2418 | 2300 | 405.2 | 456.5 | 472.1 | 459 | 468.6 | 466.8 | 464 | 472.1 | 445.2 | 429.5
2419 | 2301 | 404.7 | 456.3 | 471.8 | 458.8 | 468.5 | 466.7 | 463.9 | 472.1 | 445.1 | 429.3
2420 | 2302 | 404.2 | 456.1 | 471.5 | 458.6 | 468.4 | 466.7 | 463.9 | 472 | 445.1 | 429.2
2421 | 2303 | 403.8 | 455.8 | 471.3 | 458.4 | 468.4 | 466.6 | 463.8 | 471.9 | 445 | 429.1
2422 | 2304 | 403.3 | 455.6 | 471 | 458.2 | 468.3 | 466.5 | 463.7 | 471.8 | 445 | 429
2423 | 2305 | 402.8 | 455.4 | 470.7 | 458 | 468.2 | 466.5 | 463.7 | 471.8 | 444.9 | 428.8
2424 | 2306 | 402.3 | 455.2 | 470.5 | 457.7 | 468.2 | 466.4 | 463.6 | 471.7 | 444.9 | 428.7
2425 | 2307 | 401.8 | 454.9 | 470.2 | 457.5 | 468.1 | 466.4 | 463.5 | 471.5 | 444.8 | 428.6
2426 | 2308 | 401.3 | 454.7 | 469.9 | 457.3 | 468 | 466.3 | 463.5 | 471.4 | 444.8 | 428.5
2427 | 2309 | 400.8 | 454.5 | 469.7 | 457.1 | 467.9 | 466.2 | 463.4 | 471.2 | 444.7 | 428.4
2428 | 2310 | 400.4 | 454.3 | 469.4 | 456.8 | 467.9 | 466.2 | 463.3 | 471.1 | 444.7 | 428.2
2429 | 2311 | 399.9 | 454.1 | 469.1 | 456.6 | 467.8 | 466.1 | 463.3 | 471 | 444.6 | 428.1
2430 | 2312 | 399.4 | 453.8 | 468.9 | 456.4 | 467.7 | 466 | 463.2 | 470.9 | 444.6 | 428
2431 | 2313 | 398.9 | 453.6 | 468.6 | 456.2 | 467.7 | 466 | 463.1 | 470.8 | 444.5 | 427.9
2432 | 2314 | 398.5 | 453.4 | 468.3 | 455.9 | 467.6 | 465.9 | 463.1 | 470.7 | 444.5 | 427.8
2433 | 2315 | 398 | 453.2 | 468 | 455.7 | 467.5 | 465.8 | 463 | 470.7 | 444.4 | 427.6
2434 | 2316 | 397.5 | 453 | 467.8 | 455.5 | 467.5 | 465.8 | 462.9 | 470.6 | 444.4 | 427.5
2435 | 2317 | 397 | 452.7 | 467.5 | 455.3 | 467.4 | 465.7 | 462.9 | 470.5 | 444.3 | 427.3
2436 | 2318 | 396.5 | 452.5 | 467.3 | 455 | 467.3 | 465.6 | 462.8 | 470.4 | 444.3 | 427.2
2437 | 2319 | 396 | 452.3 | 467 | 454.8 | 467.2 | 465.6 | 462.7 | 470.3 | 444.2 | 427
2438 | 2320 | 395.5 | 452 | 466.7 | 454.6 | 467.2 | 465.5 | 462.6 | 470.1 | 444.2 | 426.9
2439 | 2321 | 395.1 | 451.8 | 466.5 | 454.4 | 467.1 | 465.4 | 462.6 | 470.1 | 444.1 | 426.8
2440 | 2322 | 394.6 | 451.6 | 466.2 | 454.1 | 467 | 465.3 | 462.5 | 469.9 | 444.1 | 426.7
2441 | 2323 | 394.1 | 451.4 | 465.9 | 453.9 | 466.9 | 465.3 | 462.4 | 469.7 | 444 | 426.5
2442 | 2324 | 393.6 | 451.1 | 465.7 | 453.7 | 466.9 | 465.2 | 462.3 | 469.6 | 443.9 | 426.4
2443 | 2325 | 393.1 | 450.9 | 465.4 | 453.5 | 466.8 | 465.1 | 462.3 | 469.5 | 443.9 | 426.3
2444 | 2326 | 392.7 | 450.7 | 465.1 | 453.2 | 466.7 | 465.1 | 462.2 | 469.4 | 443.8 | 426.2
2445 | 2327 | 392.2 | 450.5 | 464.9 | 453 | 466.6 | 465 | 462.1 | 469.4 | 443.8 | 426
2446 | 2328 | 391.7 | 450.2 | 464.6 | 452.8 | 466.6 | 464.9 | 462 | 469.3 | 443.7 | 425.9
2447 | 2329 | 391.3 | 450 | 464.3 | 452.5 | 466.5 | 464.8 | 462 | 469.2 | 443.7 | 425.7
2448 | 2330 | 390.8 | 449.8 | 464 | 452.3 | 466.4 | 464.7 | 461.9 | 469 | 443.6 | 425.6
2449 | 2331 | 390.4 | 449.6 | 463.8 | 452.1 | 466.3 | 464.7 | 461.8 | 468.9 | 443.6 | 425.5
2450 | 2332 | 389.9 | 449.3 | 463.5 | 451.9 | 466.2 | 464.6 | 461.7 | 468.7 | 443.5 | 425.3
2451 | 2333 | 389.5 | 449.1 | 463.3 | 451.6 | 466.1 | 464.5 | 461.6 | 468.5 | 443.4 | 425.2
2452 | 2334 | 389 | 448.9 | 463 | 451.4 | 466 | 464.4 | 461.6 | 468.4 | 443.4 | 425.1
2453 | 2335 | 388.6 | 448.7 | 462.7 | 451.2 | 466 | 464.4 | 461.5 | 468.3 | 443.3 | 424.9
2454 | 2336 | 388.1 | 448.4 | 462.4 | 450.9 | 465.9 | 464.3 | 461.4 | 468.2 | 443.2 | 424.8
2455 | 2337 | 387.7 | 448.2 | 462.2 | 450.7 | 465.8 | 464.2 | 461.3 | 468.1 | 443.2 | 424.7
2456 | 2338 | 387.2 | 448 | 461.9 | 450.5 | 465.7 | 464.1 | 461.2 | 468 | 443.1 | 424.5
2457 | 2339 | 386.8 | 447.8 | 461.6 | 450.3 | 465.6 | 464 | 461.1 | 467.9 | 443 | 424.4
2458 | 2340 | 386.3 | 447.5 | 461.4 | 450 | 465.5 | 463.9 | 461.1 | 467.6 | 443 | 424.2
2459 | 2341 | 385.9 | 447.3 | 461.1 | 449.8 | 465.4 | 463.9 | 461 | 467.5 | 442.9 | 424.1
2460 | 2342 | 385.5 | 447.1 | 460.9 | 449.6 | 465.3 | 463.8 | 460.9 | 467.5 | 442.9 | 424
2461 | 2343 | 385 | 446.9 | 460.6 | 449.3 | 465.2 | 463.7 | 460.8 | 467.4 | 442.8 | 423.8
2462 | 2344 | 384.6 | 446.6 | 460.3 | 449.1 | 465.1 | 463.6 | 460.7 | 467.3 | 442.7 | 423.7
2463 | 2345 | 384.1 | 446.4 | 460.1 | 448.9 | 465 | 463.5 | 460.6 | 467.1 | 442.7 | 423.6
2464 | 2346 | 383.7 | 446.2 | 459.8 | 448.6 | 464.9 | 463.4 | 460.5 | 466.9 | 442.6 | 423.4
2465 | 2347 | 383.3 | 446 | 459.5 | 448.4 | 464.8 | 463.3 | 460.4 | 466.8 | 442.5 | 423.3
2466 | 2348 | 382.8 | 445.7 | 459.2 | 448.2 | 464.7 | 463.3 | 460.4 | 466.7 | 442.5 | 423.2
2467 | 2349 | 382.4 | 445.5 | 459 | 447.9 | 464.7 | 463.2 | 460.3 | 466.6 | 442.4 | 423
2468 | 2350 | 382 | 445.3 | 458.7 | 447.7 | 464.6 | 463.1 | 460.2 | 466.5 | 442.3 | 422.9
2469 | 2351 | 381.5 | 445.1 | 458.4 | 447.5 | 464.5 | 463 | 460.1 | 466.4 | 442.2 | 422.7
2470 | 2352 | 381.1 | 444.8 | 458.2 | 447.3 | 464.4 | 462.9 | 460 | 466.4 | 442.2 | 422.6
2471 | 2353 | 380.7 | 444.6 | 457.9 | 447 | 464.3 | 462.8 | 459.9 | 466.2 | 442.1 | 422.5
2472 | 2354 | 380.3 | 444.4 | 457.6 | 446.8 | 464.2 | 462.7 | 459.8 | 466 | 442 | 422.3
2473 | 2355 | 379.8 | 444.1 | 457.3 | 446.6 | 464.1 | 462.6 | 459.7 | 465.8 | 442 | 422.1
2474 | 2356 | 379.4 | 443.9 | 457.1 | 446.3 | 464 | 462.5 | 459.6 | 465.7 | 441.9 | 422
2475 | 2357 | 379 | 443.7 | 456.8 | 446.1 | 463.9 | 462.4 | 459.5 | 465.5 | 441.8 | 421.8
2476 | 2358 | 378.6 | 443.5 | 456.5 | 445.9 | 463.8 | 462.3 | 459.4 | 465.3 | 441.7 | 421.7
2477 | 2359 | 378.2 | 443.2 | 456.3 | 445.6 | 463.7 | 462.3 | 459.3 | 465.2 | 441.6 | 421.5
2478 | 2360 | 377.8 | 443 | 456 | 445.4 | 463.6 | 462.2 | 459.2 | 465 | 441.6 | 421.4
2479 | 2361 | 377.3 | 442.8 | 455.7 | 445.2 | 463.5 | 462.1 | 459.1 | 464.9 | 441.5 | 421.2
2480 | 2362 | 376.9 | 442.5 | 455.5 | 444.9 | 463.4 | 462 | 459.1 | 464.8 | 441.4 | 421.1
2481 | 2363 | 376.5 | 442.3 | 455.2 | 444.7 | 463.3 | 461.9 | 459 | 464.7 | 441.3 | 421
2482 | 2364 | 376.1 | 442.1 | 454.9 | 444.5 | 463.2 | 461.8 | 458.9 | 464.6 | 441.3 | 420.8
2483 | 2365 | 375.6 | 441.8 | 454.7 | 444.3 | 463.1 | 461.7 | 458.8 | 464.4 | 441.2 | 420.7
2484 | 2366 | 375.2 | 441.6 | 454.4 | 444 | 463 | 461.6 | 458.7 | 464.2 | 441.1 | 420.5
2485 | 2367 | 374.8 | 441.4 | 454.1 | 443.8 | 462.8 | 461.5 | 458.6 | 464.1 | 441.1 | 420.4
2486 | 2368 | 374.4 | 441.2 | 453.8 | 443.6 | 462.7 | 461.4 | 458.5 | 464.1 | 441 | 420.3
2487 | 2369 | 374 | 440.9 | 453.6 | 443.3 | 462.6 | 461.3 | 458.4 | 464 | 440.9 | 420.2
2488 | 2370 | 373.5 | 440.7 | 453.3 | 443.1 | 462.5 | 461.2 | 458.3 | 463.8 | 440.9 | 420
2489 | 2371 | 373.1 | 440.5 | 453 | 442.9 | 462.4 | 461.1 | 458.2 | 463.6 | 440.8 | 419.9
2490 | 2372 | 372.7 | 440.3 | 452.8 | 442.6 | 462.3 | 461 | 458.1 | 463.5 | 440.7 | 419.7
2491 | 2373 | 372.3 | 440 | 452.6 | 442.4 | 462.2 | 460.9 | 457.9 | 463.5 | 440.6 | 419.6
2492.1 | 2374.1 | 371.9 | 439.8 | 452.2 | 442.2 | 462.1 | 460.8 | 457.8 | 463.4 | 440.6 | 419.4
2493.1 | 2375.1 | 371.5 | 439.6 | 452 | 441.9 | 462 | 460.7 | 457.7 | 463.2 | 440.5 | 419.3
2494.1 | 2376.1 | 371.1 | 439.3 | 451.7 | 441.7 | 461.9 | 460.6 | 457.6 | 463 | 440.4 | 419.1
2495.1 | 2377.1 | 370.7 | 439.1 | 451.5 | 441.5 | 461.8 | 460.5 | 457.5 | 462.8 | 440.3 | 419
2496.1 | 2378.1 | 370.3 | 438.9 | 451.2 | 441.2 | 461.6 | 460.4 | 457.4 | 462.6 | 440.3 | 418.8
2497.1 | 2379.1 | 369.9 | 438.7 | 450.9 | 441 | 461.5 | 460.2 | 457.3 | 462.6 | 440.2 | 418.7
2498.1 | 2380.1 | 369.5 | 438.4 | 450.7 | 440.8 | 461.4 | 460.1 | 457.2 | 462.4 | 440.1 | 418.5
2499.1 | 2381.1 | 369.1 | 438.2 | 450.4 | 440.5 | 461.3 | 460 | 457.1 | 462.3 | 440 | 418.4
2500.1 | 2382.1 | 368.7 | 438 | 450.1 | 440.3 | 461.2 | 459.9 | 457 | 462.1 | 439.9 | 418.2
2501.1 | 2383.1 | 368.4 | 437.8 | 449.9 | 440.1 | 461.1 | 459.8 | 456.9 | 462 | 439.9 | 418
2502.1 | 2384.1 | 368 | 437.5 | 449.6 | 439.8 | 461 | 459.7 | 456.8 | 461.9 | 439.8 | 417.9
2503.1 | 2385.1 | 367.6 | 437.3 | 449.2 | 439.6 | 460.9 | 459.6 | 456.7 | 461.9 | 439.7 | 417.8
2504.1 | 2386.1 | 367.2 | 437.1 | 449 | 439.4 | 460.8 | 459.5 | 456.6 | 461.8 | 439.6 | 417.6
2505.1 | 2387.1 | 366.8 | 436.9 | 448.8 | 439.2 | 460.7 | 459.4 | 456.5 | 461.6 | 439.5 | 417.5
2506.1 | 2388.1 | 366.4 | 436.6 | 448.5 | 438.9 | 460.5 | 459.3 | 456.4 | 461.5 | 439.4 | 417.3
2507.1 | 2389.1 | 366 | 436.4 | 448.2 | 438.7 | 460.4 | 459.2 | 456.2 | 461.4 | 439.4 | 417.2
2508.1 | 2390.1 | 365.6 | 436.2 | 448 | 438.5 | 460.3 | 459.1 | 456.1 | 461.2 | 439.3 | 417
2509.1 | 2391.1 | 365.2 | 435.9 | 447.7 | 438.2 | 460.2 | 459 | 456 | 460.9 | 439.2 | 416.9
2510.1 | 2392.1 | 364.8 | 435.7 | 447.4 | 438 | 460 | 458.8 | 455.9 | 460.7 | 439.1 | 416.7
2511.1 | 2393.1 | 364.5 | 435.5 | 447.1 | 437.8 | 459.9 | 458.7 | 455.8 | 460.6 | 439 | 416.6
2512.1 | 2394.1 | 364.1 | 435.3 | 446.9 | 437.5 | 459.8 | 458.6 | 455.7 | 460.4 | 438.9 | 416.4
2513.1 | 2395.1 | 363.7 | 435 | 446.6 | 437.3 | 459.7 | 458.5 | 455.6 | 460.2 | 438.9 | 416.3
2514.1 | 2396.1 | 363.3 | 434.8 | 446.4 | 437.1 | 459.6 | 458.4 | 455.5 | 460.1 | 438.8 | 416.2
2515.1 | 2397.1 | 362.9 | 434.6 | 446.1 | 436.8 | 459.5 | 458.3 | 455.3 | 459.9 | 438.7 | 416
2516.1 | 2398.1 | 362.5 | 434.3 | 445.9 | 436.6 | 459.4 | 458.2 | 455.2 | 459.7 | 438.6 | 415.9
2517.1 | 2399.1 | 362.2 | 434.1 | 445.6 | 436.4 | 459.2 | 458.1 | 455.1 | 459.5 | 438.5 | 415.7
2518.1 | 2400.1 | 361.8 | 433.9 | 445.3 | 436.1 | 459.1 | 457.9 | 455 | 459.4 | 438.5 | 415.5
2519.1 | 2401.1 | 361.4 | 433.7 | 445.1 | 435.9 | 459 | 457.8 | 454.9 | 459.3 | 438.4 | 415.4
2520.1 | 2402.1 | 361 | 433.5 | 444.8 | 435.7 | 458.9 | 457.7 | 454.8 | 459.3 | 438.3 | 415.2
2521.1 | 2403.1 | 360.6 | 433.2 | 444.5 | 435.4 | 458.7 | 457.6 | 454.7 | 459.1 | 438.2 | 415.1
2522.1 | 2404.1 | 360.3 | 433 | 444.3 | 435.2 | 458.6 | 457.5 | 454.5 | 458.9 | 438.1 | 415
2523.1 | 2405.1 | 359.9 | 432.8 | 444 | 434.9 | 458.5 | 457.4 | 454.4 | 458.7 | 438 | 414.8
2524.1 | 2406.1 | 359.5 | 432.6 | 443.7 | 434.7 | 458.4 | 457.2 | 454.3 | 458.5 | 437.9 | 414.6
2525.1 | 2407.1 | 359.1 | 432.3 | 443.5 | 434.5 | 458.3 | 457.1 | 454.2 | 458.4 | 437.8 | 414.5
2526.1 | 2408.1 | 358.8 | 432.1 | 443.2 | 434.2 | 458.2 | 457 | 454.1 | 458.3 | 437.7 | 414.3
2527.1 | 2409.1 | 358.4 | 431.9 | 442.9 | 434 | 458 | 456.9 | 454 | 458.1 | 437.6 | 414.1
2528.1 | 2410.1 | 358 | 431.6 | 442.7 | 433.8 | 457.9 | 456.8 | 453.8 | 458 | 437.5 | 414
2529.1 | 2411.1 | 357.6 | 431.4 | 442.4 | 433.5 | 457.8 | 456.6 | 453.7 | 457.8 | 437.4 | 413.8
2530.1 | 2412.1 | 357.3 | 431.2 | 442.2 | 433.3 | 457.7 | 456.5 | 453.6 | 457.6 | 437.3 | 413.7
2531.1 | 2413.1 | 356.9 | 430.9 | 441.9 | 433.1 | 457.5 | 456.4 | 453.5 | 457.5 | 437.2 | 413.5
2532.1 | 2414.1 | 356.5 | 430.7 | 441.6 | 432.8 | 457.4 | 456.3 | 453.4 | 457.3 | 437.1 | 413.4
2533.1 | 2415.1 | 356.2 | 430.5 | 441.4 | 432.6 | 457.3 | 456.2 | 453.2 | 457.2 | 437 | 413.2
2534.1 | 2416.1 | 355.8 | 430.3 | 441.1 | 432.4 | 457.1 | 456 | 453.1 | 457.1 | 436.9 | 413.1
2535.1 | 2417.1 | 355.4 | 430 | 440.8 | 432.1 | 457 | 455.9 | 453 | 457 | 436.8 | 412.9
2536.1 | 2418.1 | 355.1 | 429.8 | 440.6 | 431.9 | 456.9 | 455.8 | 452.9 | 456.8 | 436.7 | 412.8
2537.1 | 2419.1 | 354.7 | 429.6 | 440.3 | 431.7 | 456.8 | 455.7 | 452.7 | 456.7 | 436.6 | 412.6
2538.1 | 2420.1 | 354.4 | 429.4 | 440 | 431.4 | 456.6 | 455.5 | 452.6 | 456.5 | 436.6 | 412.4
2539.1 | 2421.1 | 354 | 429.1 | 439.8 | 431.2 | 456.5 | 455.4 | 452.5 | 456.5 | 436.5 | 412.3
2540.1 | 2422.1 | 353.7 | 428.9 | 439.5 | 431 | 456.4 | 455.3 | 452.4 | 456.3 | 436.4 | 412.1
2541.1 | 2423.1 | 353.3 | 428.7 | 439.3 | 430.7 | 456.2 | 455.2 | 452.2 | 456.1 | 436.3 | 412
2542.1 | 2424.1 | 352.9 | 428.4 | 439 | 430.5 | 456.1 | 455 | 452.1 | 456 | 436.2 | 411.8
2543.1 | 2425.1 | 352.6 | 428.2 | 438.7 | 430.3 | 456 | 454.9 | 452 | 455.9 | 436.1 | 411.7
2544.1 | 2426.1 | 352.2 | 428 | 438.5 | 430 | 455.8 | 454.8 | 451.9 | 455.7 | 436 | 411.5
2545.1 | 2427.1 | 351.9 | 427.8 | 438.2 | 429.8 | 455.7 | 454.7 | 451.7 | 455.5 | 435.9 | 411.4
2546.1 | 2428.1 | 351.5 | 427.5 | 438 | 429.6 | 455.5 | 454.5 | 451.6 | 455.4 | 435.8 | 411.2
2547.1 | 2429.1 | 351.2 | 427.3 | 437.7 | 429.3 | 455.4 | 454.4 | 451.5 | 455.2 | 435.7 | 411.1
2548.1 | 2430.1 | 350.8 | 427.1 | 437.4 | 429.1 | 455.3 | 454.3 | 451.3 | 455.1 | 435.6 | 410.9
2549.1 | 2431.1 | 350.5 | 426.8 | 437.2 | 428.9 | 455.1 | 454.1 | 451.2 | 455 | 435.5 | 410.7
2550.1 | 2432.1 | 350.1 | 426.6 | 436.9 | 428.7 | 455 | 454 | 451.1 | 454.8 | 435.4 | 410.6
2551.1 | 2433.1 | 349.8 | 426.4 | 436.7 | 428.4 | 454.9 | 453.9 | 451 | 454.6 | 435.3 | 410.4
2552.1 | 2434.1 | 349.4 | 426.2 | 436.4 | 428.2 | 454.8 | 453.8 | 450.8 | 454.4 | 435.2 | 410.3
2553.1 | 2435.1 | 349 | 425.9 | 436.1 | 428 | 454.6 | 453.6 | 450.7 | 454.3 | 435.1 | 410.1
2554.1 | 2436.1 | 348.7 | 425.7 | 435.9 | 427.7 | 454.5 | 453.5 | 450.6 | 454.2 | 435 | 410
2555.1 | 2437.1 | 348.3 | 425.5 | 435.6 | 427.5 | 454.3 | 453.4 | 450.4 | 454 | 434.9 | 409.8
2556.1 | 2438.1 | 347.9 | 425.2 | 435.3 | 427.3 | 454.2 | 453.2 | 450.3 | 453.9 | 434.8 | 409.6
2557.1 | 2439.1 | 347.6 | 425 | 435.1 | 427 | 454.1 | 453.1 | 450.2 | 453.7 | 434.7 | 409.5
2558.1 | 2440.1 | 347.2 | 424.8 | 434.8 | 426.8 | 454 | 453 | 450 | 453.5 | 434.6 | 409.3
2559.1 | 2441.1 | 346.9 | 424.6 | 434.5 | 426.6 | 453.8 | 452.8 | 449.9 | 453.4 | 434.4 | 409.2
2560.1 | 2442.1 | 346.5 | 424.3 | 434.3 | 426.3 | 453.7 | 452.7 | 449.8 | 453.2 | 434.3 | 409
2561.1 | 2443.1 | 346.2 | 424.1 | 434.1 | 426.1 | 453.6 | 452.6 | 449.6 | 452.9 | 434.2 | 408.8
2562.1 | 2444.1 | 345.8 | 423.9 | 433.8 | 425.9 | 453.4 | 452.4 | 449.5 | 452.8 | 434.1 | 408.7
2563.1 | 2445.1 | 345.5 | 423.6 | 433.5 | 425.6 | 453.2 | 452.3 | 449.4 | 452.5 | 434 | 408.5
2564.1 | 2446.1 | 345.1 | 423.4 | 433.3 | 425.4 | 453.1 | 452.1 | 449.2 | 452.4 | 433.9 | 408.3
2565.1 | 2447.1 | 344.8 | 423.2 | 433 | 425.2 | 453 | 452 | 449.1 | 452.2 | 433.8 | 408.2
2566.1 | 2448.1 | 344.4 | 423 | 432.7 | 424.9 | 452.8 | 451.9 | 449 | 452 | 433.7 | 408
2567.1 | 2449.1 | 344.1 | 422.7 | 432.5 | 424.7 | 452.7 | 451.7 | 448.8 | 451.8 | 433.6 | 407.9
2568.1 | 2450.1 | 343.7 | 422.5 | 432.3 | 424.5 | 452.6 | 451.6 | 448.7 | 451.6 | 433.4 | 407.7
2569.1 | 2451.1 | 343.4 | 422.3 | 432 | 424.2 | 452.4 | 451.5 | 448.6 | 451.4 | 433.4 | 407.6
2570.1 | 2452.1 | 343 | 422 | 431.7 | 424 | 452.3 | 451.3 | 448.4 | 451.2 | 433.2 | 407.4
2571.1 | 2453.1 | 342.7 | 421.8 | 431.5 | 423.8 | 452.1 | 451.2 | 448.3 | 451 | 433.1 | 407.3
2572.1 | 2454.1 | 342.4 | 421.6 | 431.2 | 423.5 | 452 | 451 | 448.2 | 450.8 | 433 | 407.1
2573.1 | 2455.1 | 342 | 421.4 | 430.9 | 423.3 | 451.8 | 450.9 | 448 | 450.8 | 432.9 | 406.9
2574.1 | 2456.1 | 341.7 | 421.1 | 430.7 | 423.1 | 451.7 | 450.8 | 447.9 | 450.6 | 432.8 | 406.8
2575.1 | 2457.1 | 341.3 | 420.9 | 430.4 | 422.8 | 451.6 | 450.6 | 447.7 | 450.5 | 432.7 | 406.6
2576.1 | 2458.1 | 341 | 420.7 | 430.1 | 422.6 | 451.4 | 450.5 | 447.6 | 450.4 | 432.6 | 406.4
2577.1 | 2459.1 | 340.7 | 420.5 | 429.9 | 422.4 | 451.2 | 450.3 | 447.5 | 450.1 | 432.5 | 406.3
2578.1 | 2460.1 | 340.3 | 420.2 | 429.7 | 422.2 | 451.1 | 450.2 | 447.3 | 450.1 | 432.4 | 406.1
2579.1 | 2461.1 | 340 | 420 | 429.4 | 421.9 | 451 | 450.1 | 447.2 | 450 | 432.2 | 405.9
2580.1 | 2462.1 | 339.7 | 419.8 | 429.1 | 421.7 | 450.8 | 449.9 | 447 | 449.8 | 432.1 | 405.8
2581.1 | 2463.1 | 339.3 | 419.5 | 428.9 | 421.5 | 450.7 | 449.8 | 446.9 | 449.7 | 432 | 405.6
2582.1 | 2464.1 | 339 | 419.3 | 428.7 | 421.2 | 450.6 | 449.6 | 446.7 | 449.5 | 431.9 | 405.5
2583.1 | 2465.1 | 338.6 | 419.1 | 428.4 | 421 | 450.4 | 449.5 | 446.6 | 449.3 | 431.8 | 405.3
2584.1 | 2466.1 | 338.3 | 418.9 | 428.1 | 420.8 | 450.2 | 449.3 | 446.5 | 449.1 | 431.6 | 405.1
2585.1 | 2467.1 | 338 | 418.6 | 427.9 | 420.6 | 450.1 | 449.2 | 446.3 | 448.9 | 431.5 | 404.9
2586.1 | 2468.1 | 337.6 | 418.4 | 427.6 | 420.3 | 450 | 449 | 446.2 | 448.6 | 431.4 | 404.8
2587.1 | 2469.1 | 337.3 | 418.2 | 427.4 | 420.1 | 449.8 | 448.9 | 446 | 448.5 | 431.3 | 404.6
2588.1 | 2470.1 | 336.9 | 417.9 | 427.1 | 419.9 | 449.6 | 448.7 | 445.9 | 448.3 | 431.2 | 404.4
2589.1 | 2471.1 | 336.6 | 417.7 | 426.9 | 419.6 | 449.5 | 448.6 | 445.8 | 448.1 | 431.1 | 404.3
2590.1 | 2472.1 | 336.2 | 417.5 | 426.6 | 419.4 | 449.3 | 448.4 | 445.6 | 447.9 | 430.9 | 404.1
2591.1 | 2473.1 | 335.9 | 417.3 | 426.3 | 419.2 | 449.2 | 448.3 | 445.5 | 447.7 | 430.8 | 404
2592.1 | 2474.1 | 335.6 | 417 | 426.1 | 418.9 | 449 | 448.2 | 445.3 | 447.6 | 430.7 | 403.8
2593.1 | 2475.1 | 335.2 | 416.8 | 425.8 | 418.7 | 448.9 | 448 | 445.2 | 447.6 | 430.6 | 403.6
2594.1 | 2476.1 | 334.9 | 416.6 | 425.6 | 418.5 | 448.7 | 447.9 | 445 | 447.4 | 430.5 | 403.5
2595.1 | 2477.1 | 334.5 | 416.4 | 425.3 | 418.2 | 448.6 | 447.7 | 444.9 | 447.2 | 430.4 | 403.3
2596.1 | 2478.1 | 334.2 | 416.1 | 425.1 | 418 | 448.4 | 447.6 | 444.7 | 447 | 430.3 | 403.1
2597.1 | 2479.1 | 333.9 | 415.9 | 424.8 | 417.8 | 448.3 | 447.4 | 444.6 | 446.9 | 430.2 | 403
2598.1 | 2480.1 | 333.6 | 415.7 | 424.5 | 417.6 | 448.1 | 447.3 | 444.4 | 446.7 | 430 | 402.8
2599.1 | 2481.1 | 333.2 | 415.4 | 424.3 | 417.3 | 448 | 447.1 | 444.3 | 446.5 | 429.9 | 402.6
2600.1 | 2482.1 | 332.9 | 415.2 | 424.1 | 417.1 | 447.8 | 447 | 444.1 | 446.3 | 429.8 | 402.5
2601.1 | 2483.1 | 332.6 | 415 | 423.8 | 416.9 | 447.7 | 446.8 | 444 | 446.1 | 429.7 | 402.3
2602.1 | 2484.1 | 332.3 | 414.8 | 423.5 | 416.7 | 447.5 | 446.7 | 443.9 | 446 | 429.6 | 402.1
2603.1 | 2485.1 | 331.9 | 414.5 | 423.3 | 416.4 | 447.4 | 446.5 | 443.7 | 445.9 | 429.4 | 402
2604.1 | 2486.1 | 331.6 | 414.3 | 423 | 416.2 | 447.2 | 446.4 | 443.6 | 445.7 | 429.3 | 401.8
2605.1 | 2487.1 | 331.3 | 414.1 | 422.8 | 416 | 447 | 446.2 | 443.4 | 445.5 | 429.2 | 401.6
2606.1 | 2488.1 | 331 | 413.8 | 422.6 | 415.7 | 446.9 | 446.1 | 443.3 | 445.3 | 429.1 | 401.5
2607.1 | 2489.1 | 330.6 | 413.6 | 422.4 | 415.5 | 446.7 | 445.9 | 443.1 | 445.2 | 429 | 401.3
2608.1 | 2490.1 | 330.3 | 413.4 | 422.1 | 415.3 | 446.6 | 445.8 | 443 | 445.1 | 428.8 | 401.1
2609.1 | 2491.1 | 330 | 413.2 | 421.8 | 415.1 | 446.4 | 445.6 | 442.8 | 444.9 | 428.7 | 401
2610.1 | 2492.1 | 329.7 | 412.9 | 421.6 | 414.8 | 446.3 | 445.5 | 442.7 | 444.6 | 428.6 | 400.8
2611.1 | 2493.1 | 329.4 | 412.7 | 421.3 | 414.6 | 446.1 | 445.3 | 442.5 | 444.4 | 428.5 | 400.6
2612.1 | 2494.1 | 329.1 | 412.5 | 421 | 414.4 | 445.9 | 445.1 | 442.4 | 444.3 | 428.3 | 400.5
2613.1 | 2495.1 | 328.8 | 412.3 | 420.8 | 414.1 | 445.8 | 445 | 442.2 | 444.1 | 428.2 | 400.3
2614.1 | 2496.1 | 328.5 | 412 | 420.6 | 413.9 | 445.6 | 444.9 | 442.1 | 443.8 | 428.1 | 400.1
2615.1 | 2497.1 | 328.2 | 411.8 | 420.3 | 413.7 | 445.4 | 444.7 | 441.9 | 443.6 | 428 | 400
2616.1 | 2498.1 | 327.9 | 411.6 | 420 | 413.5 | 445.3 | 444.5 | 441.8 | 443.5 | 427.8 | 399.8
2617.1 | 2499.1 | 327.5 | 411.4 | 419.8 | 413.2 | 445.2 | 444.4 | 441.6 | 443.2 | 427.7 | 399.6
2618.1 | 2500.1 | 327.2 | 411.2 | 419.6 | 413 | 445 | 444.2 | 441.5 | 443 | 427.6 | 399.5
2619.1 | 2501.1 | 326.9 | 410.9 | 419.3 | 412.8 | 444.8 | 444.1 | 441.3 | 442.9 | 427.5 | 399.3
2620.1 | 2502.1 | 326.6 | 410.7 | 419.1 | 412.6 | 444.7 | 443.9 | 441.1 | 442.8 | 427.4 | 399.1
2621.1 | 2503.1 | 326.3 | 410.5 | 418.8 | 412.3 | 444.5 | 443.8 | 441 | 442.7 | 427.2 | 399
2622.1 | 2504.1 | 326 | 410.3 | 418.6 | 412.1 | 444.3 | 443.6 | 440.8 | 442.6 | 427.1 | 398.8
2623.1 | 2505.1 | 325.7 | 410 | 418.3 | 411.9 | 444.2 | 443.5 | 440.7 | 442.5 | 427 | 398.6
2624.1 | 2506.1 | 325.4 | 409.8 | 418.1 | 411.6 | 444 | 443.3 | 440.5 | 442.4 | 426.9 | 398.5
2625.1 | 2507.1 | 325 | 409.6 | 417.8 | 411.4 | 443.9 | 443.2 | 440.4 | 442.3 | 426.7 | 398.3
2626.1 | 2508.1 | 324.7 | 409.4 | 417.5 | 411.2 | 443.7 | 443 | 440.2 | 442 | 426.6 | 398.1
2627.1 | 2509.1 | 324.4 | 409.2 | 417.3 | 411 | 443.6 | 442.8 | 440.1 | 441.8 | 426.5 | 398
2628.1 | 2510.1 | 324.1 | 408.9 | 417.1 | 410.7 | 443.4 | 442.7 | 439.9 | 441.6 | 426.3 | 397.8
2629.1 | 2511.1 | 323.8 | 408.7 | 416.9 | 410.5 | 443.2 | 442.5 | 439.8 | 441.5 | 426.2 | 397.6
2630.1 | 2512.1 | 323.5 | 408.5 | 416.6 | 410.3 | 443.1 | 442.4 | 439.6 | 441.3 | 426.1 | 397.5
2631.1 | 2513.1 | 323.2 | 408.2 | 416.4 | 410.1 | 442.9 | 442.2 | 439.4 | 441.2 | 425.9 | 397.3

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 36 |  |  | 2006-08-29 | 13:45
38958.5721 | 1 | 0 | 1 | XLPE | 7-C | Conduit
38958.5725 | 1 | 0 | 1 | 525 C | 23 kW/m2 |  | Bundle
38958.573 | 1 | 0 | 1
38958.5735 | 1 | 0 | 1
38958.574 | 1 | 0 | 1
38958.5745 | 1 | 0 | 1
38958.575 | 1 | 0 | 1
38958.5755 | 1 | 0 | 1
38958.5759 | 1 | 0 | 1
38958.5769 | 1 | 0 | 1
38958.5774 | 1 | 0 | 1
38958.5779 | 1 | 0 | 1
38958.5784 | 1 | 0 | 1
38958.5789 | 1 | 0 | 1
38958.5794 | 1 | 0 | 1
38958.5798 | 1 | 0 | 1
38958.5803 | 1 | 0 | 1
38958.5808 | 1 | 0 | 1
38958.5813 | 1 | 0 | 1
38958.5818 | 1 | 0 | 1
38958.5823 | 1 | 0 | 1
38958.5828 | 1 | 0 | 1
38958.5832 | 1 | 0 | 1
38958.5837 | 1 | 0 | 1
38958.5842 | 1 | 0 | 1
38958.5847 | 1 | 0 | 1
38958.5852 | 1 | 0 | 1
38958.5857 | 1 | 0 | 1
38958.5862 | 1 | 0 | 1
38958.5866 | 1 | 0 | 1
38958.5871 | 1 | 0 | 1
38958.5876 | 1 | 0 | 1
38958.5881 | 1 | 0 | 1
38958.5886 | 1 | 0 | 1
38958.5891 | 1 | 0 | 1
38958.5896 | 1 | 0 | 1
38958.59 | 1 | 0 | 1
38958.5905 | 1 | 0 | 1
38958.591 | 2 | 1 | 1
38958.5915 | 3 | 2 | 1
38958.592 | 4 | 1 | 1
38958.5925 | 5 | 2 | 1
38958.593 | 49 | 46 | 1
38958.5934 | 979 | 952 | 1
38958.5939 | 1177 | 1148 | 1
38958.5944 | 1025 | 997 | 1
38958.5949 | 1129 | 1097 | 1
38958.5954 | 971 | 941 | 1
38958.5959 | 942 | 972 | 1
38958.5964 | 1060 | 1030 | 1
38958.5969 | 1035 | 1003 | 1
38958.5973 | 943 | 941 | 1
38958.5978 | 938 | 1022 | 1
38958.5983 | 967 | 998 | 1
38958.5988 | 1121 | 1088 | 1
38958.5993 | 1190 | 1159 | 1
38958.5998 | 1183 | 1150 | 1
38958.6003 | 982 | 1013 | 1
38958.6007 | 1197 | 1198 | 1
38958.6012 | 1098 | 1064 | 1
38958.6017 | 1058 | 1026 | 1
38958.6022 | 1089 | 1055 | 1
1
38958.5721 | 1 | 0 | 2
38958.5726 | 2 | 0 | 2
38958.5731 | 1 | 0 | 2
38958.5735 | 1 | 0 | 2
38958.574 | 1 | 0 | 2
38958.5745 | 1 | 0 | 2
38958.575 | 1 | 0 | 2
38958.5755 | 1 | 0 | 2
38958.576 | 1 | 0 | 2
38958.5765 | 1 | 0 | 2
38958.5769 | 1 | 0 | 2
38958.5774 | 1 | 0 | 2
38958.5779 | 1 | 0 | 2
38958.5784 | 1 | 0 | 2
38958.5789 | 1 | 0 | 2
38958.5794 | 1 | 0 | 2
38958.5799 | 1 | 0 | 2
38958.5803 | 1 | 0 | 2
38958.5808 | 1 | 0 | 2
38958.5813 | 1 | 0 | 2
38958.5818 | 1 | 0 | 2
38958.5823 | 1 | 0 | 2
38958.5828 | 1 | 0 | 2
38958.5833 | 1 | 0 | 2
38958.5837 | 1 | 0 | 2
38958.5842 | 1 | 0 | 2
38958.5847 | 1 | 0 | 2
38958.5852 | 1 | 0 | 2
38958.5857 | 1 | 0 | 2
38958.5862 | 1 | 0 | 2
38958.5867 | 1 | 0 | 2
38958.5872 | 1 | 0 | 2
38958.5876 | 1 | 0 | 2
38958.5881 | 1 | 0 | 2
38958.5886 | 1 | 0 | 2
38958.5891 | 1 | 0 | 2
38958.5896 | 1 | 0 | 2
38958.5901 | 1 | 0 | 2
38958.5906 | 1 | 0 | 2
38958.591 | 1 | 0 | 2
38958.5915 | 2 | 1 | 2
38958.592 | 4 | 1 | 2
38958.5925 | 5 | 2 | 2
38958.593 | 51 | 55 | 2
38958.5935 | 1096 | 1166 | 2
38958.594 | 949 | 923 | 2
38958.5944 | 963 | 1076 | 2
38958.5949 | 1017 | 1057 | 2
38958.5954 | 1074 | 1046 | 2
38958.5959 | 1012 | 982 | 2
38958.5964 | 962 | 996 | 2
38958.5969 | 969 | 939 | 2
38958.5974 | 1155 | 1124 | 2
38958.5978 | 956 | 988 | 2
38958.5983 | 1050 | 944 | 2
38958.5988 | 977 | 946 | 2
38958.5993 | 1137 | 1181 | 2
38958.5998 | 1028 | 995 | 2
38958.6003 | 1110 | 1077 | 2
38958.6008 | 1091 | 1133 | 2
38958.6012 | 956 | 924 | 2
38958.6017 | 986 | 954 | 2
38958.6022 | 1126 | 1095 | 2
2
38958.5721 | 1 | 0 | 3
38958.5726 | 1 | 0 | 3
38958.5731 | 1 | 0 | 3
38958.5736 | 1 | 0 | 3
38958.574 | 1 | 0 | 3
38958.5745 | 1 | 0 | 3
38958.575 | 1 | 0 | 3
38958.5755 | 1 | 0 | 3
38958.576 | 1 | 0 | 3
38958.5765 | 1 | 0 | 3
38958.577 | 1 | 0 | 3
38958.5774 | 1 | 0 | 3
38958.5779 | 1 | 0 | 3
38958.5784 | 1 | 0 | 3
38958.5789 | 1 | 0 | 3
38958.5794 | 1 | 0 | 3
38958.5799 | 1 | 0 | 3
38958.5804 | 1 | 0 | 3
38958.5808 | 1 | 0 | 3
38958.5813 | 1 | 0 | 3
38958.5818 | 1 | 0 | 3
38958.5823 | 1 | 0 | 3
38958.5828 | 1 | 0 | 3
38958.5833 | 1 | 0 | 3
38958.5838 | 1 | 0 | 3
38958.5842 | 1 | 0 | 3
38958.5847 | 1 | 0 | 3
38958.5852 | 1 | 0 | 3
38958.5857 | 1 | 0 | 3
38958.5862 | 1 | 0 | 3
38958.5867 | 1 | 0 | 3
38958.5872 | 1 | 0 | 3
38958.5877 | 1 | 0 | 3
38958.5881 | 1 | 0 | 3
38958.5886 | 1 | 0 | 3
38958.5891 | 1 | 0 | 3
38958.5896 | 1 | 0 | 3
38958.5901 | 1 | 0 | 3
38958.5906 | 1 | 0 | 3
38958.5911 | 1 | 0 | 3
38958.5915 | 1 | 0 | 3
38958.592 | 2 | 0 | 3
38958.5925 | 2 | 0 | 3
38958.593 | 2 | 0 | 3
38958.5935 | 2 | 2 | 3
38958.594 | 2 | 2 | 3
38958.5945 | 2 | 2 | 3
38958.5949 | 2 | 2 | 3
38958.5954 | 2 | 2 | 3
38958.5959 | 2 | 1 | 3
38958.5964 | 2 | 1 | 3
38958.5969 | 2 | 2 | 3
38958.5974 | 2 | 2 | 3
38958.5979 | 2 | 2 | 3
38958.5983 | 2 | 2 | 3
38958.5988 | 2 | 2 | 3
38958.5993 | 2 | 2 | 3
38958.5998 | 2 | 2 | 3
38958.6003 | 2 | 1 | 3
38958.6008 | 2 | 1 | 3
38958.6013 | 2 | 1 | 3
38958.6017 | 3 | 1 | 3
38958.6022 | 2 | 1 | 3
3
38958.5721 | 1 | 0 | 4
38958.5726 | 1 | 0 | 4
38958.5731 | 1 | 0 | 4
38958.5736 | 1 | 0 | 4
38958.5741 | 1 | 0 | 4
38958.5745 | 1 | 0 | 4
38958.575 | 1 | 0 | 4
38958.5755 | 1 | 0 | 4
38958.576 | 1 | 0 | 4
38958.5765 | 1 | 0 | 4
38958.577 | 1 | 0 | 4
38958.5775 | 1 | 0 | 4
38958.578 | 1 | 0 | 4
38958.5784 | 1 | 0 | 4
38958.5789 | 1 | 0 | 4
38958.5794 | 1 | 0 | 4
38958.5799 | 1 | 0 | 4
38958.5804 | 1 | 0 | 4
38958.5809 | 1 | 0 | 4
38958.5814 | 1 | 0 | 4
38958.5818 | 1 | 0 | 4
38958.5823 | 1 | 0 | 4
38958.5828 | 1 | 0 | 4
38958.5833 | 1 | 0 | 4
38958.5838 | 1 | 0 | 4
38958.5843 | 1 | 0 | 4
38958.5847 | 1 | 0 | 4
38958.5852 | 1 | 0 | 4
38958.5857 | 1 | 0 | 4
38958.5862 | 1 | 0 | 4
38958.5867 | 1 | 0 | 4
38958.5872 | 1 | 0 | 4
38958.5877 | 1 | 0 | 4
38958.5881 | 1 | 0 | 4
38958.5886 | 1 | 0 | 4
38958.5891 | 1 | 0 | 4
38958.5896 | 1 | 0 | 4
38958.5901 | 1 | 0 | 4
38958.5906 | 1 | 0 | 4
38958.5911 | 1 | 0 | 4
38958.5916 | 1 | 0 | 4
38958.592 | 1888 | 0 | 4
38958.5925 | 2166 | 0 | 4
38958.593 | 2079 | 0 | 4
38958.5935 | 2168 | 1 | 4
38958.594 | 1969 | 1 | 4
38958.5945 | 2176 | 1 | 4
38958.595 | 2036 | 1 | 4
38958.5954 | 2497 | 1 | 4
38958.5959 | 2290 | 1 | 4
38958.5964 | 1987 | 1 | 4
38958.5969 | 2289 | 1 | 4
38958.5974 | 2348 | 1 | 4
38958.5979 | 2306 | 1 | 4
38958.5984 | 2229 | 1 | 4
38958.5988 | 2001 | 1 | 4
38958.5993 | 2132 | 1 | 4
38958.5998 | 2480 | 1 | 4
38958.6003 | 2499 | 1 | 4
38958.6008 | 2278 | 1 | 4
38958.6013 | 2508 | 1 | 4
38958.6018 | 2002 | 1 | 4
38958.6022 | 2112 | 1 | 4
4
38958.5721 | 1 | 0 | 5
38958.5726 | 1 | 0 | 5
38958.5731 | 1 | 0 | 5
38958.5736 | 1 | 0 | 5
38958.5741 | 1 | 0 | 5
38958.5746 | 1 | 0 | 5
38958.575 | 1 | 0 | 5
38958.5755 | 1 | 0 | 5
38958.576 | 1 | 0 | 5
38958.5765 | 1 | 0 | 5
38958.577 | 1 | 0 | 5
38958.5775 | 1 | 0 | 5
38958.578 | 1 | 0 | 5
38958.5784 | 1 | 0 | 5
38958.5789 | 1 | 0 | 5
38958.5794 | 1 | 0 | 5
38958.5799 | 1 | 0 | 5
38958.5804 | 1 | 0 | 5
38958.5809 | 1 | 0 | 5
38958.5814 | 1 | 0 | 5
38958.5819 | 1 | 0 | 5
38958.5823 | 1 | 0 | 5
38958.5828 | 1 | 0 | 5
38958.5833 | 1 | 0 | 5
38958.5838 | 1 | 0 | 5
38958.5843 | 1 | 0 | 5
38958.5848 | 1 | 0 | 5
38958.5853 | 1 | 0 | 5
38958.5857 | 1 | 0 | 5
38958.5862 | 1 | 0 | 5
38958.5867 | 1 | 0 | 5
38958.5872 | 1 | 0 | 5
38958.5877 | 1 | 0 | 5
38958.5882 | 1 | 0 | 5
38958.5887 | 1 | 0 | 5
38958.5891 | 1 | 0 | 5
38958.5896 | 1 | 0 | 5
38958.5901 | 1 | 0 | 5
38958.5906 | 1 | 0 | 5
38958.5911 | 1 | 0 | 5
38958.5916 | 1 | 0 | 5
38958.5921 | 2 | 0 | 5
38958.5925 | 2 | 0 | 5
38958.593 | 3 | 0 | 5
38958.5935 | 3 | 0 | 5
38958.594 | 3 | 0 | 5
38958.5945 | 2 | 0 | 5
38958.595 | 3 | 0 | 5
38958.5955 | 3 | 1 | 5
38958.5959 | 2 | 0 | 5
38958.5964 | 3 | 0 | 5
38958.5969 | 2 | 1 | 5
38958.5974 | 2 | 0 | 5
38958.5979 | 2 | 0 | 5
38958.5984 | 3 | 1 | 5
38958.5989 | 2 | 0 | 5
38958.5994 | 2 | 1 | 5
38958.5998 | 2 | 1 | 5
38958.6003 | 2 | 0 | 5
38958.6008 | 3 | 0 | 5
38958.6013 | 2 | 0 | 5
38958.6018 | 2 | 0 | 5
38958.6023 | 2 | 0 | 5
5
38958.5722 | 1 | 0 | 6
38958.5726 | 1 | 0 | 6
38958.5731 | 1 | 0 | 6
38958.5736 | 1 | 0 | 6
38958.5741 | 1 | 0 | 6
38958.5746 | 1 | 0 | 6
38958.5751 | 1 | 0 | 6
38958.5755 | 1 | 0 | 6
38958.576 | 1 | 0 | 6
38958.5765 | 1 | 0 | 6
38958.577 | 1 | 0 | 6
38958.5775 | 1 | 0 | 6
38958.578 | 1 | 0 | 6
38958.5785 | 1 | 0 | 6
38958.5789 | 1 | 0 | 6
38958.5794 | 1 | 0 | 6
38958.5799 | 1 | 0 | 6
38958.5804 | 1 | 0 | 6
38958.5809 | 1 | 0 | 6
38958.5814 | 1 | 0 | 6
38958.5819 | 1 | 0 | 6
38958.5823 | 2 | 0 | 6
38958.5828 | 1 | 0 | 6
38958.5833 | 1 | 0 | 6
38958.5838 | 1 | 0 | 6
38958.5843 | 1 | 0 | 6
38958.5848 | 1 | 0 | 6
38958.5853 | 1 | 0 | 6
38958.5858 | 1 | 0 | 6
38958.5862 | 1 | 0 | 6
38958.5867 | 1 | 0 | 6
38958.5872 | 1 | 0 | 6
38958.5877 | 1 | 0 | 6
38958.5882 | 1 | 0 | 6
38958.5887 | 1 | 0 | 6
38958.5892 | 1 | 0 | 6
38958.5896 | 1 | 0 | 6
38958.5901 | 1 | 0 | 6
38958.5906 | 1 | 0 | 6
38958.5911 | 1 | 0 | 6
38958.5916 | 1 | 0 | 6
38958.5921 | 1857 | 0 | 6
38958.5926 | 2042 | 0 | 6
38958.593 | 2120 | 0 | 6
38958.5935 | 2179 | 0 | 6
38958.594 | 2455 | 0 | 6
38958.5945 | 1942 | 0 | 6
38958.595 | 1954 | 0 | 6
38958.5955 | 1994 | 0 | 6
38958.596 | 1996 | 0 | 6
38958.5964 | 2016 | 0 | 6
38958.5969 | 2188 | 0 | 6
38958.5974 | 1995 | 0 | 6
38958.5979 | 1990 | 1 | 6
38958.5984 | 2290 | 0 | 6
38958.5989 | 2482 | 0 | 6
38958.5994 | 2231 | 0 | 6
38958.5998 | 2016 | 0 | 6
38958.6003 | 2115 | 0 | 6
38958.6008 | 2286 | 0 | 6
38958.6013 | 2365 | 0 | 6
38958.6018 | 2294 | 0 | 6
38958.6023 | 2104 | 0 | 6
6
38958.5722 | 1 | 0 | 7
38958.5727 | 1 | 0 | 7
38958.5731 | 1 | 0 | 7
38958.5736 | 1 | 0 | 7
38958.5741 | 1 | 0 | 7
38958.5746 | 1 | 0 | 7
38958.5751 | 1 | 0 | 7
38958.5756 | 1 | 0 | 7
38958.5761 | 1 | 0 | 7
38958.5765 | 1 | 0 | 7
38958.577 | 1 | 0 | 7
38958.5775 | 1 | 0 | 7
38958.578 | 1 | 0 | 7
38958.5785 | 1 | 0 | 7
38958.579 | 1 | 0 | 7
38958.5795 | 1 | 0 | 7
38958.5799 | 1 | 0 | 7
38958.5804 | 1 | 0 | 7
38958.5809 | 1 | 0 | 7
38958.5814 | 1 | 0 | 7
38958.5819 | 1 | 0 | 7
38958.5824 | 1 | 0 | 7
38958.5829 | 1 | 0 | 7
38958.5833 | 1 | 0 | 7
38958.5838 | 1 | 0 | 7
38958.5843 | 1 | 0 | 7
38958.5848 | 1 | 0 | 7
38958.5853 | 1 | 0 | 7
38958.5858 | 1 | 0 | 7
38958.5863 | 1 | 0 | 7
38958.5867 | 1 | 0 | 7
38958.5872 | 1 | 0 | 7
38958.5877 | 1 | 0 | 7
38958.5882 | 1 | 0 | 7
38958.5887 | 1 | 0 | 7
38958.5892 | 1 | 0 | 7
38958.5897 | 1 | 0 | 7
38958.5902 | 1 | 0 | 7
38958.5906 | 1 | 0 | 7
38958.5911 | 1 | 0 | 7
38958.5916 | 1 | 0 | 7
38958.5921 | 2 | 0 | 7
38958.5926 | 2 | 0 | 7
38958.5931 | 2 | 0 | 7
38958.5936 | 3 | 0 | 7
38958.594 | 2 | 0 | 7
38958.5945 | 2 | 0 | 7
38958.595 | 3 | 0 | 7
38958.5955 | 2 | 0 | 7
38958.596 | 2 | 0 | 7
38958.5965 | 2 | 0 | 7
38958.597 | 2 | 0 | 7
38958.5974 | 2 | 0 | 7
38958.5979 | 2 | 0 | 7
38958.5984 | 2 | 1 | 7
38958.5989 | 2 | 0 | 7
38958.5994 | 2 | 0 | 7
38958.5999 | 2 | 1 | 7
38958.6004 | 2 | 0 | 7
38958.6008 | 2 | 0 | 7
38958.6013 | 3 | 0 | 7
38958.6018 | 2 | 0 | 7
38958.6023 | 2 | 0 | 7
7
38958.5722 | 1 | 0 | 8
38958.5727 | 1 | 0 | 8
38958.5731 | 1 | 0 | 8
38958.5736 | 1 | 0 | 8
38958.5741 | 1 | 0 | 8
38958.5746 | 1 | 0 | 8
38958.5751 | 1 | 0 | 8
38958.5756 | 1 | 0 | 8
38958.5761 | 1 | 0 | 8
38958.5766 | 1 | 0 | 8
38958.577 | 1 | 0 | 8
38958.5775 | 1 | 0 | 8
38958.578 | 1 | 0 | 8
38958.5785 | 1 | 0 | 8
38958.579 | 1 | 0 | 8
38958.5795 | 1 | 0 | 8
38958.58 | 1 | 0 | 8
38958.5804 | 1 | 0 | 8
38958.5809 | 1 | 0 | 8
38958.5814 | 1 | 0 | 8
38958.5819 | 1 | 0 | 8
38958.5824 | 1 | 0 | 8
38958.5829 | 1 | 0 | 8
38958.5834 | 1 | 0 | 8
38958.5838 | 1 | 0 | 8
38958.5843 | 1 | 0 | 8
38958.5848 | 1 | 0 | 8
38958.5853 | 1 | 0 | 8
38958.5858 | 1 | 0 | 8
38958.5863 | 1 | 0 | 8
38958.5868 | 1 | 0 | 8
38958.5872 | 1 | 0 | 8
38958.5877 | 1 | 0 | 8
38958.5882 | 1 | 0 | 8
38958.5887 | 1 | 0 | 8
38958.5892 | 1 | 0 | 8
38958.5897 | 1 | 0 | 8
38958.5902 | 22 | 0 | 8
38958.5906 | 150 | 0 | 8
38958.5911 | 622 | 0 | 8
38958.5916 | 697 | 0 | 8
38958.5921 | 1907 | 0 | 8
38958.5926 | 2107 | 0 | 8
38958.5931 | 951 | 0 | 8
38958.5936 | 2172 | 0 | 8
38958.5941 | 1982 | 0 | 8
38958.5945 | 2200 | 0 | 8
38958.595 | 2088 | 0 | 8
38958.5955 | 1989 | 0 | 8
38958.596 | 2091 | 0 | 8
38958.5965 | 2407 | 0 | 8
38958.597 | 2185 | 0 | 8
38958.5975 | 2186 | 0 | 8
38958.5979 | 2198 | 0 | 8
38958.5984 | 2162 | 0 | 8
38958.5989 | 2477 | 0 | 8
38958.5994 | 2476 | 0 | 8
38958.5999 | 2171 | 0 | 8
38958.6004 | 2013 | 0 | 8
38958.6009 | 2005 | 0 | 8
38958.6013 | 1931 | 0 | 8
38958.6018 | 2171 | 0 | 8
38958.6023 | 1957 | 0 | 8
8
38958.5722 | 1 | 0 | 9
38958.5727 | 1 | 0 | 9
38958.5732 | 1 | 0 | 9
38958.5737 | 1 | 0 | 9
38958.5741 | 1 | 0 | 9
38958.5746 | 1 | 0 | 9
38958.5751 | 1 | 0 | 9
38958.5756 | 1 | 0 | 9
38958.5761 | 1 | 0 | 9
38958.5766 | 1 | 0 | 9
38958.5771 | 1 | 0 | 9
38958.5775 | 1 | 0 | 9
38958.578 | 1 | 0 | 9
38958.5785 | 1 | 0 | 9
38958.579 | 1 | 0 | 9
38958.5795 | 1 | 0 | 9
38958.58 | 1 | 0 | 9
38958.5805 | 1 | 0 | 9
38958.5809 | 1 | 0 | 9
38958.5814 | 1 | 0 | 9
38958.5819 | 1 | 0 | 9
38958.5824 | 1 | 0 | 9
38958.5829 | 1 | 0 | 9
38958.5834 | 1 | 0 | 9
38958.5839 | 1 | 0 | 9
38958.5843 | 1 | 0 | 9
38958.5848 | 1 | 0 | 9
38958.5853 | 1 | 0 | 9
38958.5858 | 1 | 0 | 9
38958.5863 | 1 | 0 | 9
38958.5868 | 1 | 0 | 9
38958.5873 | 1 | 0 | 9
38958.5877 | 1 | 0 | 9
38958.5882 | 1 | 0 | 9
38958.5887 | 1 | 0 | 9
38958.5892 | 1 | 0 | 9
38958.5897 | 1 | 0 | 9
38958.5902 | 1 | 0 | 9
38958.5907 | 1 | 0 | 9
38958.5911 | 1 | 0 | 9
38958.5916 | 1 | 0 | 9
38958.5921 | 2 | 0 | 9
38958.5926 | 2 | 0 | 9
38958.5931 | 2 | 0 | 9
38958.5936 | 3 | 0 | 9
38958.5941 | 2 | 0 | 9
38958.5945 | 2 | 0 | 9
38958.595 | 2 | 0 | 9
38958.5955 | 2 | 0 | 9
38958.596 | 2 | 0 | 9
38958.5965 | 2 | 0 | 9
38958.597 | 2 | 0 | 9
38958.5975 | 2 | 0 | 9
38958.598 | 2 | 0 | 9
38958.5984 | 3 | 0 | 9
38958.5989 | 2 | 0 | 9
38958.5994 | 2 | 0 | 9
38958.5999 | 2 | 0 | 9
38958.6004 | 2 | 0 | 9
38958.6009 | 2 | 0 | 9
38958.6014 | 2 | 0 | 9
38958.6018 | 2 | 0 | 9
38958.6023 | 3 | 0 | 9
9
38958.5722 | 1 | 0 | 10
38958.5727 | 1 | 0 | 10
38958.5732 | 1 | 0 | 10
38958.5737 | 1 | 0 | 10
38958.5742 | 1 | 0 | 10
38958.5746 | 1 | 0 | 10
38958.5751 | 1 | 0 | 10
38958.5756 | 1 | 0 | 10
38958.5761 | 1 | 0 | 10
38958.5766 | 1 | 0 | 10
38958.5771 | 1 | 0 | 10
38958.5776 | 1 | 0 | 10
38958.578 | 1 | 0 | 10
38958.5785 | 1 | 0 | 10
38958.579 | 1 | 0 | 10
38958.5795 | 1 | 0 | 10
38958.58 | 1 | 0 | 10
38958.5805 | 1 | 0 | 10
38958.581 | 1 | 0 | 10
38958.5814 | 1 | 0 | 10
38958.5819 | 1 | 0 | 10
38958.5824 | 1 | 0 | 10
38958.5829 | 1 | 0 | 10
38958.5834 | 1 | 0 | 10
38958.5839 | 1 | 0 | 10
38958.5844 | 1 | 0 | 10
38958.5848 | 1 | 0 | 10
38958.5853 | 1 | 0 | 10
38958.5858 | 1 | 0 | 10
38958.5863 | 1 | 0 | 10
38958.5868 | 1 | 0 | 10
38958.5873 | 1 | 0 | 10
38958.5878 | 1 | 0 | 10
38958.5883 | 1 | 0 | 10
38958.5887 | 1 | 0 | 10
38958.5892 | 1 | 0 | 10
38958.5897 | 2 | 0 | 10
38958.5902 | 28 | 0 | 10
38958.5907 | 185 | 0 | 10
38958.5912 | 548 | 0 | 10
38958.5917 | 824 | 0 | 10
38958.5921 | 2359 | 0 | 10
38958.5926 | 2297 | 0 | 10
38958.5931 | 1922 | 0 | 10
38958.5936 | 2351 | 0 | 10
38958.5941 | 2248 | 0 | 10
38958.5946 | 1951 | 0 | 10
38958.5951 | 2404 | 0 | 10
38958.5955 | 2046 | 0 | 10
38958.596 | 2205 | 0 | 10
38958.5965 | 2489 | 1 | 10
38958.597 | 2451 | 0 | 10
38958.5975 | 2299 | 0 | 10
38958.598 | 2007 | 0 | 10
38958.5985 | 2282 | 0 | 10
38958.5989 | 2060 | 0 | 10
38958.5994 | 2184 | 0 | 10
38958.5999 | 2498 | 0 | 10
38958.6004 | 2342 | 0 | 10
38958.6009 | 1940 | 0 | 10
38958.6014 | 2444 | 0 | 10
38958.6019 | 2248 | 0 | 10
38958.6023 | 2461 | 0 | 10
10
38958.5722 | 1 | 0 | 11
38958.5727 | 1 | 0 | 11
38958.5732 | 1 | 0 | 11
38958.5737 | 1 | 0 | 11
38958.5742 | 1 | 0 | 11
38958.5747 | 1 | 0 | 11
38958.5751 | 1 | 0 | 11
38958.5756 | 1 | 0 | 11
38958.5761 | 1 | 0 | 11
38958.5766 | 1 | 0 | 11
38958.5771 | 1 | 0 | 11
38958.5776 | 1 | 0 | 11
38958.5781 | 1 | 0 | 11
38958.5785 | 1 | 0 | 11
38958.579 | 1 | 0 | 11
38958.5795 | 1 | 0 | 11
38958.58 | 1 | 0 | 11
38958.5805 | 1 | 0 | 11
38958.581 | 1 | 0 | 11
38958.5815 | 1 | 0 | 11
38958.5819 | 1 | 0 | 11
38958.5824 | 1 | 0 | 11
38958.5829 | 1 | 0 | 11
38958.5834 | 1 | 0 | 11
38958.5839 | 1 | 0 | 11
38958.5844 | 1 | 0 | 11
38958.5849 | 1 | 0 | 11
38958.5853 | 1 | 0 | 11
38958.5858 | 1 | 0 | 11
38958.5863 | 1 | 0 | 11
38958.5868 | 1 | 0 | 11
38958.5873 | 1 | 0 | 11
38958.5878 | 1 | 0 | 11
38958.5883 | 1 | 0 | 11
38958.5888 | 1 | 0 | 11
38958.5892 | 1 | 0 | 11
38958.5897 | 1 | 0 | 11
38958.5902 | 1 | 0 | 11
38958.5907 | 1 | 0 | 11
38958.5912 | 1 | 0 | 11
38958.5917 | 2 | 0 | 11
38958.5922 | 2 | 0 | 11
38958.5926 | 3 | 0 | 11
38958.5931 | 2 | 0 | 11
38958.5936 | 2 | 0 | 11
38958.5941 | 2 | 0 | 11
38958.5946 | 2 | 0 | 11
38958.5951 | 3 | 0 | 11
38958.5956 | 3 | 0 | 11
38958.596 | 3 | 0 | 11
38958.5965 | 2 | 0 | 11
38958.597 | 2 | 0 | 11
38958.5975 | 2 | 0 | 11
38958.598 | 2 | 0 | 11
38958.5985 | 2 | 1 | 11
38958.599 | 2 | 0 | 11
38958.5994 | 2 | 0 | 11
38958.5999 | 2 | 0 | 11
38958.6004 | 2 | 0 | 11
38958.6009 | 2 | 0 | 11
38958.6014 | 2 | 0 | 11
38958.6019 | 2 | 0 | 11
38958.6024 | 2 | 0 | 11
11
38958.5722 | 1 | 0 | 12
38958.5727 | 1 | 0 | 12
38958.5732 | 1 | 0 | 12
38958.5737 | 1 | 0 | 12
38958.5742 | 1 | 0 | 12
38958.5747 | 1 | 0 | 12
38958.5752 | 1 | 0 | 12
38958.5756 | 1 | 0 | 12
38958.5761 | 1 | 0 | 12
38958.5766 | 1 | 0 | 12
38958.5771 | 1 | 0 | 12
38958.5776 | 1 | 0 | 12
38958.5781 | 1 | 0 | 12
38958.5786 | 1 | 0 | 12
38958.5791 | 1 | 0 | 12
38958.5795 | 1 | 0 | 12
38958.58 | 1 | 0 | 12
38958.5805 | 1 | 0 | 12
38958.581 | 1 | 0 | 12
38958.5815 | 1 | 0 | 12
38958.582 | 1 | 0 | 12
38958.5825 | 1 | 0 | 12
38958.5829 | 1 | 0 | 12
38958.5834 | 1 | 0 | 12
38958.5839 | 1 | 0 | 12
38958.5844 | 1 | 0 | 12
38958.5849 | 1 | 0 | 12
38958.5854 | 1 | 0 | 12
38958.5859 | 1 | 0 | 12
38958.5863 | 1 | 0 | 12
38958.5868 | 1 | 0 | 12
38958.5873 | 1 | 0 | 12
38958.5878 | 1 | 0 | 12
38958.5883 | 1 | 0 | 12
38958.5888 | 1 | 0 | 12
38958.5893 | 1 | 0 | 12
38958.5897 | 1 | 0 | 12
38958.5902 | 1 | 0 | 12
38958.5907 | 1 | 0 | 12
38958.5912 | 1 | 0 | 12
38958.5917 | 2 | 0 | 12
38958.5922 | 1894 | 0 | 12
38958.5927 | 2043 | 0 | 12
38958.5931 | 2345 | 0 | 12
38958.5936 | 2493 | 0 | 12
38958.5941 | 2172 | 0 | 12
38958.5946 | 2502 | 0 | 12
38958.5951 | 2254 | 0 | 12
38958.5956 | 2004 | 0 | 12
38958.5961 | 2225 | 0 | 12
38958.5966 | 2476 | 0 | 12
38958.597 | 2251 | 1 | 12
38958.5975 | 2004 | 0 | 12
38958.598 | 2109 | 0 | 12
38958.5985 | 2521 | 0 | 12
38958.599 | 2522 | 0 | 12
38958.5995 | 2319 | 0 | 12
38958.5999 | 1952 | 0 | 12
38958.6004 | 2280 | 0 | 12
38958.6009 | 2340 | 0 | 12
38958.6014 | 2342 | 0 | 12
38958.6019 | 2355 | 0 | 12
38958.6024 | 2514 | 0 | 12
12
38958.5723 | 1 | 0 | 13
38958.5727 | 1 | 0 | 13
38958.5732 | 1 | 0 | 13
38958.5737 | 1 | 0 | 13
38958.5742 | 1 | 0 | 13
38958.5747 | 1 | 0 | 13
38958.5752 | 1 | 0 | 13
38958.5757 | 1 | 0 | 13
38958.5761 | 1 | 0 | 13
38958.5766 | 1 | 0 | 13
38958.5771 | 1 | 0 | 13
38958.5776 | 1 | 0 | 13
38958.5781 | 1 | 0 | 13
38958.5786 | 1 | 0 | 13
38958.5791 | 1 | 0 | 13
38958.5795 | 1 | 0 | 13
38958.58 | 1 | 0 | 13
38958.5805 | 1 | 0 | 13
38958.581 | 1 | 0 | 13
38958.5815 | 1 | 0 | 13
38958.582 | 1 | 0 | 13
38958.5825 | 1 | 0 | 13
38958.583 | 1 | 0 | 13
38958.5834 | 1 | 0 | 13
38958.5839 | 1 | 0 | 13
38958.5844 | 1 | 0 | 13
38958.5849 | 1 | 0 | 13
38958.5854 | 1 | 0 | 13
38958.5859 | 1 | 0 | 13
38958.5864 | 1 | 0 | 13
38958.5868 | 1 | 0 | 13
38958.5873 | 1 | 0 | 13
38958.5878 | 1 | 0 | 13
38958.5883 | 1 | 0 | 13
38958.5888 | 1 | 0 | 13
38958.5893 | 1 | 0 | 13
38958.5898 | 1 | 0 | 13
38958.5902 | 1 | 0 | 13
38958.5907 | 1 | 0 | 13
38958.5912 | 1 | 0 | 13
38958.5917 | 1 | 0 | 13
38958.5922 | 3 | 0 | 13
38958.5927 | 2 | 0 | 13
38958.5932 | 2 | 0 | 13
38958.5936 | 3 | 0 | 13
38958.5941 | 2 | 0 | 13
38958.5946 | 2 | 0 | 13
38958.5951 | 2 | 0 | 13
38958.5956 | 3 | 0 | 13
38958.5961 | 2 | 0 | 13
38958.5966 | 2 | 0 | 13
38958.597 | 3 | 0 | 13
38958.5975 | 2 | 0 | 13
38958.598 | 2 | 0 | 13
38958.5985 | 2 | 0 | 13
38958.599 | 2 | 0 | 13
38958.5995 | 2 | 0 | 13
38958.6 | 2 | 0 | 13
38958.6005 | 2 | 0 | 13
38958.6009 | 2 | 0 | 13
38958.6014 | 2 | 0 | 13
38958.6019 | 2 | 0 | 13
38958.6024 | 2 | 0 | 13
13
38958.5723 | 1 | 0 | 14
38958.5728 | 1 | 0 | 14
38958.5733 | 1 | 0 | 14
38958.5737 | 1 | 0 | 14
38958.5742 | 1 | 0 | 14
38958.5747 | 1 | 0 | 14
38958.5752 | 1 | 0 | 14
38958.5757 | 1 | 0 | 14
38958.5762 | 1 | 0 | 14
38958.5767 | 1 | 0 | 14
38958.5771 | 1 | 0 | 14
38958.5776 | 1 | 0 | 14
38958.5781 | 1 | 0 | 14
38958.5786 | 1 | 0 | 14
38958.5791 | 1 | 0 | 14
38958.5796 | 1 | 0 | 14
38958.5801 | 1 | 0 | 14
38958.5805 | 1 | 0 | 14
38958.581 | 1 | 0 | 14
38958.5815 | 1 | 0 | 14
38958.582 | 1 | 0 | 14
38958.5825 | 1 | 0 | 14
38958.583 | 1 | 0 | 14
38958.5835 | 1 | 0 | 14
38958.5839 | 1 | 0 | 14
38958.5844 | 1 | 0 | 14
38958.5849 | 1 | 0 | 14
38958.5854 | 1 | 0 | 14
38958.5859 | 1 | 0 | 14
38958.5864 | 1 | 0 | 14
38958.5873 | 1 | 0 | 14
38958.5878 | 1 | 0 | 14
38958.5883 | 1 | 0 | 14
38958.5888 | 1 | 0 | 14
38958.5893 | 1 | 0 | 14
38958.5898 | 1 | 0 | 14
38958.5903 | 1 | 0 | 14
38958.5907 | 1 | 0 | 14
38958.5912 | 1 | 0 | 14
38958.5922 | 2 | 0 | 14
38958.5927 | 2 | 0 | 14
38958.5932 | 2 | 0 | 14
38958.5937 | 2 | 0 | 14
38958.5941 | 2 | 0 | 14
38958.5946 | 2 | 0 | 14
38958.5951 | 2 | 0 | 14
38958.5956 | 2 | 0 | 14
38958.5961 | 2 | 0 | 14
38958.5966 | 2 | 0 | 14
38958.5971 | 2 | 0 | 14
38958.5975 | 3 | 0 | 14
38958.598 | 2 | 0 | 14
38958.5985 | 2 | 0 | 14
38958.599 | 2 | 0 | 14
38958.5995 | 2 | 0 | 14
38958.6 | 2 | 0 | 14
38958.6005 | 3 | 0 | 14
38958.6009 | 2 | 0 | 14
38958.6014 | 2 | 0 | 14
38958.6019 | 2 | 0 | 14
38958.6024 | 1 | 0 | 14
14
38958.5723 | 1 | 0 | 15
38958.5728 | 1 | 0 | 15
38958.5733 | 1 | 0 | 15
38958.5738 | 1 | 0 | 15
38958.5742 | 1 | 0 | 15
38958.5747 | 1 | 0 | 15
38958.5752 | 1 | 0 | 15
38958.5757 | 1 | 0 | 15
38958.5762 | 1 | 0 | 15
38958.5767 | 1 | 0 | 15
38958.5772 | 1 | 0 | 15
38958.5776 | 1 | 0 | 15
38958.5781 | 1 | 0 | 15
38958.5786 | 1 | 0 | 15
38958.5791 | 1 | 0 | 15
38958.5796 | 1 | 0 | 15
38958.5801 | 1 | 0 | 15
38958.5806 | 1 | 0 | 15
38958.581 | 1 | 0 | 15
38958.5815 | 1 | 0 | 15
38958.582 | 1 | 0 | 15
38958.5825 | 1 | 0 | 15
38958.583 | 1 | 0 | 15
38958.5835 | 1 | 0 | 15
38958.584 | 1 | 0 | 15
38958.5844 | 1 | 0 | 15
38958.5849 | 1 | 0 | 15
38958.5854 | 1 | 0 | 15
38958.5859 | 1 | 0 | 15
38958.5864 | 1 | 0 | 15
38958.5869 | 1 | 0 | 15
38958.5874 | 1 | 0 | 15
38958.5878 | 1 | 0 | 15
38958.5883 | 1 | 0 | 15
38958.5888 | 1 | 0 | 15
38958.5893 | 1 | 0 | 15
38958.5898 | 1 | 0 | 15
38958.5903 | 1 | 0 | 15
38958.5908 | 1 | 0 | 15
38958.5912 | 1 | 0 | 15
38958.5917 | 1 | 0 | 15
38958.5922 | 2 | 0 | 15
38958.5927 | 2 | 0 | 15
38958.5932 | 2 | 0 | 15
38958.5937 | 2 | 0 | 15
38958.5942 | 2 | 0 | 15
38958.5947 | 2 | 0 | 15
38958.5951 | 2 | 0 | 15
38958.5956 | 2 | 0 | 15
38958.5961 | 2 | 0 | 15
38958.5966 | 2 | 0 | 15
38958.5971 | 2 | 0 | 15
38958.5976 | 2 | 0 | 15
38958.5981 | 2 | 0 | 15
38958.5985 | 2 | 0 | 15
38958.599 | 2 | 0 | 15
38958.5995 | 2 | 0 | 15
38958.6 | 1 | 0 | 15
38958.6005 | 2 | 0 | 15
38958.601 | 2 | 0 | 15
38958.6015 | 2 | 0 | 15
38958.6019 | 2 | 0 | 15
38958.6024 | 2 | 0 | 15
15
38958.5723 | 1 | 0 | 16
38958.5728 | 1 | 0 | 16
38958.5733 | 1 | 0 | 16
38958.5738 | 1 | 0 | 16
38958.5742 | 1 | 0 | 16
38958.5747 | 1 | 0 | 16
38958.5752 | 1 | 0 | 16
38958.5757 | 1 | 0 | 16
38958.5762 | 1 | 0 | 16
38958.5767 | 1 | 0 | 16
38958.5772 | 1 | 0 | 16
38958.5777 | 1 | 0 | 16
38958.5781 | 1 | 0 | 16
38958.5786 | 1 | 0 | 16
38958.5791 | 1 | 0 | 16
38958.5796 | 1 | 0 | 16
38958.5801 | 1 | 0 | 16
38958.5806 | 1 | 0 | 16
38958.5811 | 1 | 0 | 16
38958.5815 | 1 | 0 | 16
38958.582 | 1 | 0 | 16
38958.5825 | 1 | 0 | 16
38958.583 | 1 | 0 | 16
38958.5835 | 1 | 0 | 16
38958.584 | 1 | 0 | 16
38958.5845 | 1 | 0 | 16
38958.5849 | 1 | 0 | 16
38958.5854 | 1 | 0 | 16
38958.5859 | 1 | 0 | 16
38958.5864 | 1 | 0 | 16
38958.5869 | 1 | 0 | 16
38958.5874 | 1 | 0 | 16
38958.5879 | 1 | 0 | 16
38958.5883 | 1 | 0 | 16
38958.5888 | 1 | 0 | 16
38958.5893 | 1 | 0 | 16
38958.5898 | 1 | 0 | 16
38958.5903 | 57 | 0 | 16
38958.5908 | 219 | 0 | 16
38958.5913 | 595 | 0 | 16
38958.5917 | 755 | 0 | 16
38958.5922 | 2396 | 0 | 16
38958.5927 | 2330 | 0 | 16
38958.5932 | 2135 | 0 | 16
38958.5937 | 2488 | 0 | 16
38958.5942 | 2469 | 0 | 16
38958.5947 | 2108 | 0 | 16
38958.5952 | 2427 | 0 | 16
38958.5956 | 2353 | 0 | 16
38958.5961 | 2089 | 0 | 16
38958.5966 | 2004 | 0 | 16
38958.5971 | 2369 | 0 | 16
38958.5976 | 2406 | 1 | 16
38958.5981 | 2259 | 0 | 16
38958.5986 | 2040 | 0 | 16
38958.599 | 1981 | 0 | 16
38958.5995 | 2098 | 0 | 16
38958.6 | 2366 | 0 | 16
38958.6005 | 2168 | 0 | 16
38958.601 | 1934 | 0 | 16
38958.6015 | 1954 | 0 | 16
38958.602 | 1966 | 0 | 16
38958.6024 | 2487 | 0 | 16
16
38958.5723 | 1 | 0 | 17
38958.5728 | 1 | 0 | 17
38958.5733 | 1 | 0 | 17
38958.5738 | 1 | 0 | 17
38958.5743 | 1 | 0 | 17
38958.5748 | 1 | 0 | 17
38958.5752 | 1 | 0 | 17
38958.5757 | 1 | 0 | 17
38958.5762 | 1 | 0 | 17
38958.5767 | 1 | 0 | 17
38958.5772 | 1 | 0 | 17
38958.5777 | 1 | 0 | 17
38958.5782 | 1 | 0 | 17
38958.5786 | 1 | 0 | 17
38958.5791 | 1 | 0 | 17
38958.5796 | 1 | 0 | 17
38958.5801 | 1 | 0 | 17
38958.5806 | 1 | 0 | 17
38958.5811 | 1 | 0 | 17
38958.5816 | 1 | 0 | 17
38958.582 | 1 | 0 | 17
38958.5825 | 1 | 0 | 17
38958.583 | 1 | 0 | 17
38958.5835 | 1 | 0 | 17
38958.584 | 1 | 0 | 17
38958.5845 | 1 | 0 | 17
38958.585 | 1 | 0 | 17
38958.5855 | 1 | 0 | 17
38958.5859 | 1 | 0 | 17
38958.5864 | 1 | 0 | 17
38958.5869 | 1 | 0 | 17
38958.5874 | 1 | 0 | 17
38958.5879 | 1 | 0 | 17
38958.5884 | 1 | 0 | 17
38958.5889 | 1 | 0 | 17
38958.5893 | 1 | 0 | 17
38958.5898 | 1 | 0 | 17
38958.5903 | 1 | 0 | 17
38958.5908 | 1 | 0 | 17
38958.5913 | 1 | 0 | 17
38958.5918 | 2 | 0 | 17
38958.5923 | 2 | 0 | 17
38958.5927 | 3 | 0 | 17
38958.5932 | 2 | 0 | 17
38958.5937 | 2 | 0 | 17
38958.5942 | 2 | 0 | 17
38958.5947 | 2 | 0 | 17
38958.5952 | 2 | 0 | 17
38958.5957 | 2 | 0 | 17
38958.5961 | 2 | 0 | 17
38958.5966 | 2 | 0 | 17
38958.5971 | 2 | 0 | 17
38958.5976 | 2 | 0 | 17
38958.5981 | 2 | 0 | 17
38958.5986 | 2 | 0 | 17
38958.5991 | 2 | 0 | 17
38958.5995 | 2 | 0 | 17
38958.6 | 2 | 0 | 17
38958.6005 | 2 | 0 | 17
38958.601 | 2 | 0 | 17
38958.6015 | 2 | 0 | 17
38958.602 | 2 | 0 | 17
38958.6025 | 2 | 0 | 17
17
38958.5723 | 1 | 0 | 18
38958.5728 | 1 | 0 | 18
38958.5733 | 1 | 0 | 18
38958.5738 | 1 | 0 | 18
38958.5743 | 1 | 0 | 18
38958.5748 | 1 | 0 | 18
38958.5753 | 1 | 0 | 18
38958.5757 | 1 | 0 | 18
38958.5762 | 1 | 0 | 18
38958.5767 | 1 | 0 | 18
38958.5772 | 1 | 0 | 18
38958.5777 | 1 | 0 | 18
38958.5782 | 1 | 0 | 18
38958.5787 | 1 | 0 | 18
38958.5791 | 1 | 0 | 18
38958.5796 | 1 | 0 | 18
38958.5801 | 1 | 0 | 18
38958.5806 | 1 | 0 | 18
38958.5811 | 1 | 0 | 18
38958.5816 | 1 | 0 | 18
38958.5821 | 1 | 0 | 18
38958.5825 | 1 | 0 | 18
38958.583 | 1 | 0 | 18
38958.5835 | 1 | 0 | 18
38958.584 | 1 | 0 | 18
38958.5845 | 1 | 0 | 18
38958.585 | 1 | 0 | 18
38958.5855 | 1 | 0 | 18
38958.5859 | 1 | 0 | 18
38958.5864 | 1 | 0 | 18
38958.5869 | 1 | 0 | 18
38958.5874 | 1 | 0 | 18
38958.5879 | 1 | 0 | 18
38958.5884 | 1 | 0 | 18
38958.5889 | 1 | 0 | 18
38958.5894 | 1 | 1 | 18
38958.5898 | 3 | 0 | 18
38958.5903 | 79 | 0 | 18
38958.5908 | 241 | 0 | 18
38958.5913 | 678 | 0 | 18
38958.5918 | 722 | 0 | 18
38958.5923 | 2101 | 0 | 18
38958.5928 | 2026 | 0 | 18
38958.5932 | 1023 | 0 | 18
38958.5937 | 2142 | 0 | 18
38958.5942 | 2139 | 0 | 18
38958.5947 | 2331 | 0 | 18
38958.5952 | 2086 | 0 | 18
38958.5957 | 1965 | 0 | 18
38958.5962 | 2010 | 1 | 18
38958.5966 | 2396 | 0 | 18
38958.5971 | 2175 | 0 | 18
38958.5976 | 2293 | 0 | 18
38958.5981 | 1968 | 0 | 18
38958.5986 | 2395 | 0 | 18
38958.5991 | 2299 | 0 | 18
38958.5996 | 1945 | 0 | 18
38958.6 | 2494 | 0 | 18
38958.6005 | 2248 | 0 | 18
38958.601 | 2504 | 0 | 18
38958.6015 | 1953 | 0 | 18
38958.602 | 2024 | 0 | 18
38958.6025 | 1943 | 0 | 18
18
38958.5724 | 1 | 0 | 19
38958.5728 | 1 | 0 | 19
38958.5733 | 1 | 0 | 19
38958.5738 | 1 | 0 | 19
38958.5743 | 1 | 0 | 19
38958.5748 | 1 | 0 | 19
38958.5753 | 1 | 0 | 19
38958.5758 | 1 | 0 | 19
38958.5762 | 1 | 0 | 19
38958.5767 | 1 | 0 | 19
38958.5772 | 1 | 0 | 19
38958.5777 | 1 | 0 | 19
38958.5782 | 1 | 0 | 19
38958.5787 | 1 | 0 | 19
38958.5792 | 1 | 0 | 19
38958.5796 | 1 | 0 | 19
38958.5801 | 1 | 0 | 19
38958.5806 | 1 | 0 | 19
38958.5811 | 1 | 0 | 19
38958.5816 | 1 | 0 | 19
38958.5821 | 1 | 1 | 19
38958.5826 | 1 | 0 | 19
38958.5831 | 1 | 0 | 19
38958.5835 | 1 | 0 | 19
38958.584 | 1 | 0 | 19
38958.5845 | 1 | 0 | 19
38958.585 | 1 | 0 | 19
38958.5855 | 1 | 0 | 19
38958.586 | 1 | 0 | 19
38958.5865 | 1 | 0 | 19
38958.5869 | 1 | 0 | 19
38958.5874 | 1 | 0 | 19
38958.5879 | 1 | 0 | 19
38958.5884 | 1 | 0 | 19
38958.5889 | 1 | 0 | 19
38958.5894 | 1 | 0 | 19
38958.5898 | 1 | 0 | 19
38958.5903 | 1 | 0 | 19
38958.5908 | 2 | 0 | 19
38958.5913 | 27 | 4 | 19
38958.5918 | 636 | 565 | 19
38958.5923 | 2183 | 1 | 19
38958.5928 | 2158 | 1 | 19
38958.5933 | 2165 | 1 | 19
38958.5937 | 2222 | 0 | 19
38958.5942 | 2398 | 1 | 19
38958.5947 | 2010 | 0 | 19
38958.5952 | 2214 | 0 | 19
38958.5957 | 2197 | 0 | 19
38958.5962 | 1953 | 0 | 19
38958.5967 | 2248 | 0 | 19
38958.5971 | 2090 | 0 | 19
38958.5976 | 2480 | 0 | 19
38958.5981 | 2423 | 0 | 19
38958.5986 | 2506 | 0 | 19
38958.5991 | 2475 | 0 | 19
38958.5996 | 2487 | 0 | 19
38958.6001 | 2177 | 0 | 19
38958.6005 | 2256 | 0 | 19
38958.601 | 2467 | 0 | 19
38958.6015 | 2414 | 0 | 19
38958.602 | 2191 | 0 | 19
38958.6025 | 2400 | 1 | 19
19
38958.5724 | 1 | 0 | 20
38958.5729 | 1 | 0 | 20
38958.5733 | 1 | 0 | 20
38958.5738 | 1 | 0 | 20
38958.5743 | 1 | 0 | 20
38958.5748 | 1 | 0 | 20
38958.5753 | 1 | 0 | 20
38958.5758 | 1 | 0 | 20
38958.5763 | 1 | 0 | 20
38958.5767 | 1 | 0 | 20
38958.5772 | 1 | 0 | 20
38958.5777 | 1 | 0 | 20
38958.5782 | 1 | 0 | 20
38958.5787 | 1 | 0 | 20
38958.5792 | 1 | 0 | 20
38958.5797 | 1 | 0 | 20
38958.5802 | 1 | 0 | 20
38958.5806 | 1 | 0 | 20
38958.5811 | 1 | 0 | 20
38958.5816 | 1 | 0 | 20
38958.5821 | 1 | 0 | 20
38958.5826 | 1 | 0 | 20
38958.5831 | 1 | 0 | 20
38958.5836 | 1 | 0 | 20
38958.584 | 1 | 0 | 20
38958.5845 | 1 | 0 | 20
38958.585 | 1 | 0 | 20
38958.5855 | 1 | 0 | 20
38958.586 | 1 | 0 | 20
38958.5865 | 1 | 0 | 20
38958.587 | 1 | 0 | 20
38958.5874 | 1 | 0 | 20
38958.5879 | 1 | 0 | 20
38958.5884 | 1 | 0 | 20
38958.5889 | 1 | 0 | 20
38958.5894 | 1 | 0 | 20
38958.5899 | 1 | 0 | 20
38958.5904 | 1 | 0 | 20
38958.5908 | 1 | 0 | 20
38958.5913 | 12 | 3 | 20
38958.5918 | 663 | 602 | 20
38958.5923 | 1991 | 2 | 20
38958.5928 | 1953 | 0 | 20
38958.5933 | 2428 | 1 | 20
38958.5938 | 1964 | 0 | 20
38958.5942 | 2463 | 0 | 20
38958.5947 | 1946 | 0 | 20
38958.5952 | 2183 | 0 | 20
38958.5957 | 2285 | 0 | 20
38958.5962 | 2518 | 0 | 20
38958.5967 | 2410 | 0 | 20
38958.5972 | 2517 | 0 | 20
38958.5977 | 2513 | 0 | 20
38958.5981 | 2273 | 0 | 20
38958.5986 | 2358 | 0 | 20
38958.5991 | 2407 | 0 | 20
38958.5996 | 2306 | 0 | 20
38958.6001 | 2467 | 0 | 20
38958.6006 | 2431 | 0 | 20
38958.6011 | 2108 | 0 | 20
38958.6015 | 2468 | 0 | 20
38958.602 | 2053 | 0 | 20
38958.6025 | 2515 | 0 | 20
20
38958.5724 | 1 | 0 | 21
38958.5729 | 1 | 0 | 21
38958.5734 | 1 | 0 | 21
38958.5738 | 1 | 0 | 21
38958.5743 | 1 | 0 | 21
38958.5748 | 1 | 0 | 21
38958.5753 | 1 | 0 | 21
38958.5758 | 1 | 0 | 21
38958.5763 | 1 | 0 | 21
38958.5768 | 1 | 0 | 21
38958.5772 | 1 | 0 | 21
38958.5777 | 1 | 0 | 21
38958.5782 | 1 | 0 | 21
38958.5787 | 1 | 0 | 21
38958.5792 | 1 | 0 | 21
38958.5797 | 1 | 0 | 21
38958.5802 | 1 | 0 | 21
38958.5806 | 1 | 0 | 21
38958.5811 | 1 | 0 | 21
38958.5816 | 1 | 0 | 21
38958.5821 | 1 | 0 | 21
38958.5826 | 1 | 0 | 21
38958.5831 | 1 | 0 | 21
38958.5836 | 1 | 0 | 21
38958.5841 | 1 | 0 | 21
38958.5845 | 1 | 0 | 21
38958.585 | 1 | 0 | 21
38958.5855 | 1 | 0 | 21
38958.586 | 1 | 0 | 21
38958.5865 | 1 | 0 | 21
38958.587 | 1 | 0 | 21
38958.5875 | 1 | 0 | 21
38958.5879 | 1 | 0 | 21
38958.5884 | 1 | 0 | 21
38958.5889 | 1 | 0 | 21
38958.5894 | 1 | 0 | 21
38958.5899 | 1 | 0 | 21
38958.5904 | 1 | 0 | 21
38958.5909 | 1 | 0 | 21
38958.5913 | 1 | 0 | 21
38958.5918 | 21 | 1 | 21
38958.5923 | 2122 | 0 | 21
38958.5928 | 2423 | 0 | 21
38958.5933 | 2467 | 0 | 21
38958.5938 | 2368 | 0 | 21
38958.5943 | 2240 | 0 | 21
38958.5947 | 2088 | 0 | 21
38958.5952 | 2135 | 0 | 21
38958.5957 | 2186 | 0 | 21
38958.5962 | 2211 | 0 | 21
38958.5967 | 2145 | 0 | 21
38958.5972 | 2040 | 0 | 21
38958.5977 | 2058 | 0 | 21
38958.5981 | 2050 | 0 | 21
38958.5986 | 2470 | 0 | 21
38958.5991 | 2517 | 0 | 21
38958.5996 | 2513 | 0 | 21
38958.6001 | 2031 | 0 | 21
38958.6006 | 2218 | 0 | 21
38958.6011 | 2361 | 0 | 21
38958.6016 | 2010 | 0 | 21
38958.602 | 1976 | 0 | 21
38958.6025 | 2466 | 0 | 21
21
38958.5724 | 1 | 0 | 22
38958.5729 | 1 | 0 | 22
38958.5734 | 1 | 0 | 22
38958.5739 | 1 | 0 | 22
38958.5744 | 1 | 0 | 22
38958.5748 | 1 | 0 | 22
38958.5753 | 1 | 0 | 22
38958.5758 | 1 | 0 | 22
38958.5763 | 1 | 0 | 22
38958.5768 | 1 | 0 | 22
38958.5773 | 1 | 0 | 22
38958.5778 | 1 | 0 | 22
38958.5782 | 1 | 0 | 22
38958.5787 | 1 | 0 | 22
38958.5792 | 1 | 0 | 22
38958.5797 | 1 | 0 | 22
38958.5802 | 1 | 0 | 22
38958.5807 | 1 | 0 | 22
38958.5812 | 1 | 0 | 22
38958.5816 | 1 | 0 | 22
38958.5821 | 1 | 0 | 22
38958.5826 | 1 | 0 | 22
38958.5831 | 1 | 0 | 22
38958.5836 | 1 | 0 | 22
38958.5841 | 1 | 0 | 22
38958.5846 | 1 | 0 | 22
38958.585 | 1 | 0 | 22
38958.5855 | 1 | 0 | 22
38958.586 | 1 | 0 | 22
38958.5865 | 1 | 0 | 22
38958.587 | 1 | 0 | 22
38958.5875 | 1 | 0 | 22
38958.588 | 1 | 0 | 22
38958.5884 | 1 | 0 | 22
38958.5889 | 1 | 0 | 22
38958.5894 | 1 | 0 | 22
38958.5899 | 2 | 0 | 22
38958.5904 | 89 | 0 | 22
38958.5909 | 307 | 0 | 22
38958.5914 | 635 | 0 | 22
38958.5919 | 691 | 0 | 22
38958.5923 | 2095 | 0 | 22
38958.5928 | 2126 | 0 | 22
38958.5933 | 971 | 0 | 22
38958.5938 | 2445 | 0 | 22
38958.5943 | 2466 | 0 | 22
38958.5948 | 2274 | 0 | 22
38958.5953 | 2062 | 0 | 22
38958.5957 | 2255 | 0 | 22
38958.5962 | 2128 | 0 | 22
38958.5967 | 2233 | 1 | 22
38958.5972 | 2082 | 0 | 22
38958.5977 | 2187 | 0 | 22
38958.5982 | 2113 | 0 | 22
38958.5986 | 2000 | 0 | 22
38958.5991 | 2031 | 0 | 22
38958.5996 | 2267 | 0 | 22
38958.6001 | 2398 | 0 | 22
38958.6006 | 2001 | 0 | 22
38958.6011 | 2495 | 0 | 22
38958.6016 | 2183 | 0 | 22
38958.602 | 2314 | 0 | 22
38958.6025 | 2294 | 0 | 22
22
38958.5724 | 1 | 0 | 23
38958.5729 | 1 | 0 | 23
38958.5734 | 1 | 0 | 23
38958.5739 | 1 | 0 | 23
38958.5744 | 1 | 0 | 23
38958.5748 | 1 | 0 | 23
38958.5753 | 1 | 0 | 23
38958.5758 | 1 | 0 | 23
38958.5763 | 1 | 0 | 23
38958.5768 | 1 | 0 | 23
38958.5773 | 1 | 0 | 23
38958.5778 | 1 | 0 | 23
38958.5783 | 1 | 0 | 23
38958.5787 | 1 | 0 | 23
38958.5792 | 1 | 0 | 23
38958.5797 | 1 | 0 | 23
38958.5802 | 1 | 0 | 23
38958.5807 | 1 | 0 | 23
38958.5812 | 1 | 0 | 23
38958.5817 | 1 | 0 | 23
38958.5821 | 1 | 0 | 23
38958.5826 | 1 | 0 | 23
38958.5831 | 1 | 0 | 23
38958.5836 | 1 | 0 | 23
38958.5841 | 1 | 0 | 23
38958.5846 | 1 | 0 | 23
38958.5851 | 1 | 0 | 23
38958.5855 | 1 | 0 | 23
38958.586 | 1 | 0 | 23
38958.5865 | 1 | 0 | 23
38958.587 | 1 | 0 | 23
38958.5875 | 1 | 0 | 23
38958.588 | 1 | 0 | 23
38958.5885 | 1 | 0 | 23
38958.5889 | 1 | 0 | 23
38958.5894 | 1 | 0 | 23
38958.5899 | 1 | 0 | 23
38958.5904 | 1 | 0 | 23
38958.5909 | 1 | 0 | 23
38958.5914 | 2 | 0 | 23
38958.5919 | 1014 | 0 | 23
38958.5923 | 1998 | 0 | 23
38958.5928 | 2478 | 0 | 23
38958.5933 | 2116 | 0 | 23
38958.5938 | 2287 | 0 | 23
38958.5943 | 2277 | 0 | 23
38958.5948 | 2056 | 1 | 23
38958.5953 | 2120 | 0 | 23
38958.5958 | 2513 | 0 | 23
38958.5962 | 2241 | 0 | 23
38958.5967 | 2491 | 0 | 23
38958.5972 | 2408 | 0 | 23
38958.5977 | 2278 | 0 | 23
38958.5982 | 2107 | 0 | 23
38958.5987 | 2154 | 0 | 23
38958.5992 | 2129 | 0 | 23
38958.5996 | 2085 | 0 | 23
38958.6001 | 2326 | 0 | 23
38958.6006 | 2517 | 0 | 23
38958.6011 | 2111 | 0 | 23
38958.6016 | 2316 | 0 | 23
38958.6021 | 2152 | 0 | 23
38958.6026 | 2171 | 0 | 23
23
38958.5724 | 1 | 0 | 24
38958.5729 | 1 | 0 | 24
38958.5734 | 1 | 0 | 24
38958.5739 | 1 | 0 | 24
38958.5744 | 1 | 0 | 24
38958.5749 | 1 | 0 | 24
38958.5754 | 1 | 0 | 24
38958.5758 | 1 | 0 | 24
38958.5763 | 1 | 0 | 24
38958.5768 | 1 | 0 | 24
38958.5773 | 1 | 0 | 24
38958.5778 | 1 | 0 | 24
38958.5783 | 1 | 0 | 24
38958.5788 | 1 | 0 | 24
38958.5792 | 1 | 0 | 24
38958.5797 | 1 | 0 | 24
38958.5802 | 1 | 0 | 24
38958.5807 | 1 | 0 | 24
38958.5812 | 1 | 0 | 24
38958.5817 | 1 | 0 | 24
38958.5822 | 1 | 0 | 24
38958.5827 | 1 | 0 | 24
38958.5831 | 1 | 0 | 24
38958.5836 | 1 | 0 | 24
38958.5841 | 1 | 0 | 24
38958.5846 | 1 | 0 | 24
38958.5851 | 1 | 0 | 24
38958.5856 | 1 | 0 | 24
38958.586 | 1 | 0 | 24
38958.5865 | 1 | 0 | 24
38958.587 | 1 | 0 | 24
38958.5875 | 1 | 0 | 24
38958.588 | 1 | 0 | 24
38958.5885 | 1 | 0 | 24
38958.589 | 1 | 0 | 24
38958.5894 | 1 | 0 | 24
38958.5899 | 6 | 0 | 24
38958.5904 | 112 | 0 | 24
38958.5909 | 268 | 0 | 24
38958.5914 | 765 | 0 | 24
38958.5919 | 852 | 0 | 24
38958.5924 | 2327 | 0 | 24
38958.5928 | 2243 | 0 | 24
38958.5933 | 1762 | 0 | 24
38958.5938 | 2347 | 0 | 24
38958.5943 | 2201 | 0 | 24
38958.5948 | 2169 | 0 | 24
38958.5953 | 2212 | 0 | 24
38958.5958 | 2269 | 0 | 24
38958.5963 | 2079 | 0 | 24
38958.5967 | 1980 | 0 | 24
38958.5972 | 2149 | 0 | 24
38958.5977 | 2150 | 0 | 24
38958.5982 | 2092 | 0 | 24
38958.5987 | 2184 | 0 | 24
38958.5992 | 2130 | 0 | 24
38958.5997 | 2006 | 0 | 24
38958.6001 | 2068 | 0 | 24
38958.6006 | 2122 | 0 | 24
38958.6011 | 2447 | 0 | 24
38958.6016 | 2185 | 0 | 24
38958.6021 | 2094 | 0 | 24
38958.6026 | 2398 | 0 | 24
24
38958.5725 | 1 | 0 | 25
38958.5729 | 1 | 0 | 25
38958.5734 | 1 | 0 | 25
38958.5739 | 1 | 0 | 25
38958.5744 | 1 | 0 | 25
38958.5749 | 1 | 0 | 25
38958.5754 | 1 | 0 | 25
38958.5759 | 1 | 0 | 25
38958.5763 | 1 | 0 | 25
38958.5768 | 1 | 0 | 25
38958.5773 | 1 | 0 | 25
38958.5778 | 1 | 0 | 25
38958.5783 | 1 | 0 | 25
38958.5788 | 1 | 0 | 25
38958.5793 | 1 | 0 | 25
38958.5797 | 1 | 0 | 25
38958.5802 | 1 | 0 | 25
38958.5807 | 1 | 0 | 25
38958.5812 | 1 | 0 | 25
38958.5817 | 1 | 0 | 25
38958.5822 | 1 | 0 | 25
38958.5827 | 1 | 0 | 25
38958.5831 | 1 | 0 | 25
38958.5836 | 1 | 0 | 25
38958.5841 | 1 | 0 | 25
38958.5846 | 1 | 0 | 25
38958.5851 | 1 | 0 | 25
38958.5856 | 1 | 0 | 25
38958.5861 | 1 | 0 | 25
38958.5866 | 1 | 0 | 25
38958.587 | 1 | 0 | 25
38958.5875 | 1 | 0 | 25
38958.588 | 1 | 0 | 25
38958.5885 | 1 | 0 | 25
38958.589 | 1 | 0 | 25
38958.5895 | 1 | 1 | 25
38958.59 | 1 | 0 | 25
38958.5904 | 1 | 0 | 25
38958.5909 | 1 | 0 | 25
38958.5914 | 1 | 0 | 25
38958.5919 | 2115 | 0 | 25
38958.5924 | 2181 | 0 | 25
38958.5929 | 2007 | 0 | 25
38958.5934 | 2143 | 0 | 25
38958.5938 | 2104 | 0 | 25
38958.5943 | 2296 | 0 | 25
38958.5948 | 1984 | 0 | 25
38958.5953 | 2477 | 0 | 25
38958.5958 | 2286 | 0 | 25
38958.5963 | 1968 | 0 | 25
38958.5968 | 2449 | 0 | 25
38958.5972 | 2242 | 0 | 25
38958.5977 | 2319 | 0 | 25
38958.5982 | 1944 | 0 | 25
38958.5987 | 2444 | 0 | 25
38958.5992 | 1990 | 0 | 25
38958.5997 | 2057 | 0 | 25
38958.6002 | 2186 | 0 | 25
38958.6006 | 1966 | 0 | 25
38958.6011 | 2423 | 0 | 25
38958.6016 | 1960 | 0 | 25
38958.6021 | 2495 | 0 | 25
38958.6026 | 2294 | 0 | 25
25
38958.5725 | 1 | 0 | 26
38958.573 | 1 | 0 | 26
38958.5734 | 1 | 0 | 26
38958.5739 | 1 | 0 | 26
38958.5744 | 1 | 0 | 26
38958.5749 | 1 | 0 | 26
38958.5754 | 1 | 0 | 26
38958.5759 | 1 | 0 | 26
38958.5764 | 1 | 0 | 26
38958.5768 | 1 | 0 | 26
38958.5773 | 1 | 0 | 26
38958.5778 | 1 | 0 | 26
38958.5783 | 1 | 0 | 26
38958.5788 | 1 | 0 | 26
38958.5793 | 1 | 0 | 26
38958.5798 | 1 | 0 | 26
38958.5802 | 1 | 0 | 26
38958.5807 | 1 | 0 | 26
38958.5812 | 1 | 0 | 26
38958.5817 | 1 | 0 | 26
38958.5822 | 1 | 0 | 26
38958.5827 | 1 | 0 | 26
38958.5832 | 1 | 0 | 26
38958.5836 | 1 | 0 | 26
38958.5841 | 1 | 0 | 26
38958.5846 | 1 | 0 | 26
38958.5851 | 1 | 0 | 26
38958.5856 | 1 | 0 | 26
38958.5861 | 1 | 0 | 26
38958.5866 | 1 | 0 | 26
38958.587 | 1 | 0 | 26
38958.5875 | 1 | 0 | 26
38958.588 | 1 | 0 | 26
38958.5885 | 1 | 0 | 26
38958.589 | 1 | 0 | 26
38958.5895 | 1 | 0 | 26
38958.59 | 4 | 0 | 26
38958.5905 | 102 | 0 | 26
38958.5909 | 293 | 0 | 26
38958.5914 | 673 | 0 | 26
38958.5919 | 2165 | 0 | 26
38958.5924 | 1926 | 0 | 26
38958.5929 | 2264 | 0 | 26
38958.5934 | 1448 | 0 | 26
38958.5939 | 2420 | 0 | 26
38958.5943 | 2165 | 0 | 26
38958.5948 | 2118 | 1 | 26
38958.5953 | 1956 | 0 | 26
38958.5958 | 2323 | 0 | 26
38958.5963 | 2499 | 0 | 26
38958.5968 | 2075 | 0 | 26
38958.5973 | 2044 | 0 | 26
38958.5977 | 2502 | 0 | 26
38958.5982 | 2124 | 0 | 26
38958.5987 | 1979 | 0 | 26
38958.5992 | 2067 | 0 | 26
38958.5997 | 2057 | 0 | 26
38958.6002 | 2376 | 0 | 26
38958.6007 | 1956 | 0 | 26
38958.6011 | 1951 | 0 | 26
38958.6016 | 2485 | 0 | 26
38958.6021 | 2249 | 0 | 26
38958.6026 | 2232 | 0 | 26
26
38958.5725 | 1 | 0 | 27
38958.573 | 1 | 0 | 27
38958.5735 | 1 | 0 | 27
38958.5739 | 1 | 0 | 27
38958.5744 | 1 | 0 | 27
38958.5749 | 1 | 0 | 27
38958.5754 | 1 | 0 | 27
38958.5759 | 1 | 0 | 27
38958.5764 | 1 | 0 | 27
38958.5769 | 1 | 0 | 27
38958.5773 | 1 | 0 | 27
38958.5778 | 1 | 0 | 27
38958.5783 | 1 | 0 | 27
38958.5788 | 1 | 0 | 27
38958.5793 | 1 | 0 | 27
38958.5798 | 1 | 0 | 27
38958.5803 | 1 | 0 | 27
38958.5808 | 1 | 0 | 27
38958.5812 | 1 | 0 | 27
38958.5817 | 1 | 0 | 27
38958.5822 | 1 | 0 | 27
38958.5827 | 1 | 0 | 27
38958.5832 | 1 | 0 | 27
38958.5837 | 1 | 0 | 27
38958.5842 | 1 | 0 | 27
38958.5846 | 1 | 0 | 27
38958.5851 | 1 | 0 | 27
38958.5856 | 1 | 0 | 27
38958.5861 | 1 | 0 | 27
38958.5866 | 1 | 0 | 27
38958.5871 | 1 | 0 | 27
38958.5876 | 1 | 0 | 27
38958.588 | 1 | 0 | 27
38958.5885 | 1 | 0 | 27
38958.589 | 1 | 0 | 27
38958.5895 | 1 | 0 | 27
38958.59 | 1 | 0 | 27
38958.5905 | 1 | 0 | 27
38958.591 | 1 | 0 | 27
38958.5914 | 2 | 0 | 27
38958.5919 | 1895 | 0 | 27
38958.5924 | 2162 | 0 | 27
38958.5929 | 1983 | 0 | 27
38958.5934 | 2169 | 0 | 27
38958.5939 | 2021 | 0 | 27
38958.5944 | 1941 | 0 | 27
38958.5948 | 2083 | 0 | 27
38958.5953 | 2347 | 0 | 27
38958.5958 | 1975 | 0 | 27
38958.5963 | 2375 | 0 | 27
38958.5968 | 2377 | 0 | 27
38958.5973 | 2267 | 0 | 27
38958.5978 | 2431 | 0 | 27
38958.5983 | 2201 | 0 | 27
38958.5987 | 2421 | 0 | 27
38958.5992 | 2315 | 0 | 27
38958.5997 | 1971 | 0 | 27
38958.6002 | 2095 | 0 | 27
38958.6007 | 2228 | 0 | 27
38958.6012 | 1948 | 0 | 27
38958.6016 | 2303 | 0 | 27
38958.6026 | 2430 | 0 | 27
27
38958.5725 | 1 | 0 | 28
38958.573 | 1 | 0 | 28
38958.5735 | 1 | 0 | 28
38958.574 | 1 | 0 | 28
38958.5744 | 1 | 0 | 28
38958.5749 | 1 | 0 | 28
38958.5754 | 1 | 0 | 28
38958.5759 | 1 | 0 | 28
38958.5764 | 1 | 0 | 28
38958.5769 | 1 | 0 | 28
38958.5774 | 1 | 0 | 28
38958.5778 | 1 | 0 | 28
38958.5783 | 1 | 0 | 28
38958.5788 | 1 | 0 | 28
38958.5793 | 1 | 0 | 28
38958.5798 | 1 | 0 | 28
38958.5803 | 1 | 0 | 28
38958.5808 | 1 | 0 | 28
38958.5813 | 1 | 0 | 28
38958.5817 | 1 | 0 | 28
38958.5822 | 1 | 0 | 28
38958.5827 | 1 | 0 | 28
38958.5832 | 1 | 0 | 28
38958.5837 | 1 | 0 | 28
38958.5842 | 1 | 0 | 28
38958.5847 | 1 | 0 | 28
38958.5851 | 1 | 0 | 28
38958.5856 | 1 | 0 | 28
38958.5861 | 1 | 0 | 28
38958.5866 | 1 | 0 | 28
38958.5871 | 1 | 0 | 28
38958.5876 | 1 | 0 | 28
38958.5881 | 1 | 0 | 28
38958.5885 | 1 | 0 | 28
38958.589 | 1 | 0 | 28
38958.5895 | 1 | 0 | 28
38958.59 | 9 | 0 | 28
38958.5905 | 138 | 0 | 28
38958.591 | 348 | 0 | 28
38958.5915 | 809 | 0 | 28
38958.5919 | 2166 | 0 | 28
38958.5924 | 2178 | 0 | 28
38958.5929 | 2379 | 0 | 28
38958.5934 | 2099 | 0 | 28
38958.5939 | 2282 | 0 | 28
38958.5944 | 1955 | 0 | 28
38958.5949 | 1999 | 0 | 28
38958.5953 | 2505 | 0 | 28
38958.5958 | 2225 | 0 | 28
38958.5963 | 2376 | 0 | 28
38958.5968 | 1970 | 0 | 28
38958.5973 | 2427 | 0 | 28
38958.5978 | 2446 | 1 | 28
38958.5983 | 2016 | 0 | 28
38958.5987 | 2249 | 0 | 28
38958.5992 | 2034 | 0 | 28
38958.5997 | 2192 | 0 | 28
38958.6002 | 2197 | 0 | 28
38958.6007 | 2495 | 0 | 28
38958.6012 | 2288 | 0 | 28
38958.6017 | 2165 | 0 | 28
38958.6022 | 2411 | 0 | 28
38958.6026 | 2214 | 0 | 28
28
38958.5725 | 1 | 0 | 29
38958.573 | 1 | 0 | 29
38958.5735 | 1 | 0 | 29
38958.574 | 1 | 0 | 29
38958.5745 | 1 | 0 | 29
38958.575 | 1 | 0 | 29
38958.5754 | 1 | 0 | 29
38958.5759 | 1 | 0 | 29
38958.5764 | 1 | 0 | 29
38958.5769 | 1 | 0 | 29
38958.5774 | 1 | 0 | 29
38958.5779 | 1 | 0 | 29
38958.5784 | 1 | 0 | 29
38958.5788 | 1 | 0 | 29
38958.5793 | 1 | 0 | 29
38958.5798 | 1 | 0 | 29
38958.5803 | 1 | 0 | 29
38958.5808 | 1 | 0 | 29
38958.5813 | 1 | 0 | 29
38958.5817 | 1 | 0 | 29
38958.5822 | 1 | 0 | 29
38958.5827 | 1 | 0 | 29
38958.5832 | 1 | 0 | 29
38958.5837 | 1 | 0 | 29
38958.5842 | 1 | 0 | 29
38958.5847 | 1 | 0 | 29
38958.5852 | 1 | 0 | 29
38958.5856 | 1 | 0 | 29
38958.5861 | 1 | 0 | 29
38958.5866 | 1 | 0 | 29
38958.5871 | 1 | 0 | 29
38958.5876 | 1 | 0 | 29
38958.5881 | 1 | 0 | 29
38958.5886 | 1 | 0 | 29
38958.589 | 1 | 0 | 29
38958.5895 | 6 | 1 | 29
38958.59 | 117 | 56 | 29
38958.5905 | 323 | 166 | 29
38958.591 | 793 | 441 | 29
38958.5915 | 1347 | 881 | 29
38958.592 | 1978 | 17 | 29
38958.5924 | 2378 | 2 | 29
38958.5929 | 2036 | 0 | 29
38958.5934 | 2488 | 1 | 29
38958.5939 | 2023 | 0 | 29
38958.5944 | 2257 | 1 | 29
38958.5949 | 2117 | 0 | 29
38958.5954 | 2041 | 0 | 29
38958.5958 | 2060 | 0 | 29
38958.5963 | 2303 | 0 | 29
38958.5968 | 2499 | 1 | 29
38958.5973 | 2271 | 0 | 29
38958.5978 | 2346 | 0 | 29
38958.5983 | 2504 | 0 | 29
38958.5988 | 2339 | 0 | 29
38958.5992 | 2384 | 0 | 29
38958.5997 | 2398 | 1 | 29
38958.6002 | 2467 | 0 | 29
38958.6007 | 2052 | 0 | 29
38958.6012 | 1963 | 0 | 29
38958.6017 | 1964 | 0 | 29
38958.6022 | 2215 | 0 | 29
38958.6027 | 2429 | 1 | 29
29
38958.5725 | 1 | 0 | 30
38958.573 | 1 | 0 | 30
38958.5735 | 1 | 0 | 30
38958.574 | 1 | 0 | 30
38958.5745 | 1 | 0 | 30
38958.575 | 1 | 0 | 30
38958.5755 | 1 | 0 | 30
38958.5759 | 1 | 0 | 30
38958.5764 | 1 | 0 | 30
38958.5769 | 1 | 0 | 30
38958.5774 | 1 | 0 | 30
38958.5779 | 1 | 0 | 30
38958.5784 | 1 | 0 | 30
38958.5789 | 1 | 0 | 30
38958.5793 | 1 | 0 | 30
38958.5798 | 1 | 0 | 30
38958.5803 | 1 | 0 | 30
38958.5808 | 1 | 0 | 30
38958.5813 | 1 | 0 | 30
38958.5818 | 1 | 0 | 30
38958.5823 | 1 | 0 | 30
38958.5827 | 1 | 0 | 30
38958.5832 | 1 | 0 | 30
38958.5837 | 1 | 0 | 30
38958.5842 | 1 | 0 | 30
38958.5847 | 1 | 0 | 30
38958.5852 | 1 | 0 | 30
38958.5857 | 1 | 0 | 30
38958.5861 | 1 | 0 | 30
38958.5866 | 1 | 0 | 30
38958.5871 | 1 | 0 | 30
38958.5876 | 1 | 0 | 30
38958.5881 | 1 | 0 | 30
38958.5886 | 1 | 0 | 30
38958.5891 | 1 | 0 | 30
38958.5895 | 15 | 1 | 30
38958.59 | 113 | 55 | 30
38958.5905 | 282 | 122 | 30
38958.591 | 978 | 663 | 30
38958.5915 | 1366 | 891 | 30
38958.592 | 2177 | 14 | 30
38958.5925 | 2205 | 2 | 30
38958.593 | 2490 | 1 | 30
38958.5934 | 2209 | 0 | 30
38958.5939 | 2297 | 1 | 30
38958.5944 | 2459 | 0 | 30
38958.5949 | 2139 | 0 | 30
38958.5954 | 2053 | 0 | 30
38958.5959 | 2172 | 0 | 30
38958.5964 | 2163 | 0 | 30
38958.5968 | 2269 | 1 | 30
38958.5973 | 2312 | 0 | 30
38958.5978 | 1981 | 0 | 30
38958.5983 | 1960 | 0 | 30
38958.5988 | 2077 | 0 | 30
38958.5993 | 2139 | 0 | 30
38958.5998 | 2482 | 0 | 30
38958.6002 | 2179 | 0 | 30
38958.6007 | 2354 | 0 | 30
38958.6012 | 2432 | 0 | 30
38958.6017 | 1971 | 1 | 30
38958.6022 | 2268 | 1 | 30
38958.6027 | 2257 | 0 | 30
30

## Test Facts
Last row in IRMS data sheets: | 68
Time when Penlight power was initiated: | 118